## Test Conditions
DESIREE-FIRE Test Number 39 - Circuit Simulator Data Only
Test Date: | 2009-09-24
DCSim DAQ Start Time | 14:24
DCSim Time for Synchronization | 14:56
Heat Source Synchronization | 0:43 | minutes:seconds
Heat Source DAQ Start Time | 14:56
Heat Source Start Time | 14:58
DCSim Offset | 0:34 | minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 2010 | seconds
Heat Source Offset | 0:02 | minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 103 | seconds
Heat Source Stop Time | 16:11
Test Duration | 1:13 | minutes:seconds
| 4400 | seconds
CT500 Turns | 2 |  | This is the number of times the lead conductor within the DCSim Panels were wrapped around the Hall Effect Device of the current transducer.
CT35 Turns | 5
Pre-Test Baseline: | Gathered
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit Number | Cable Type |  | Cable TC Channel | Air TC Channel
SWGR Close | PE/PVC, 7c, 12AWG |  | Channel 3 and Channel 4 represent the side and top of the thermocouple cable, respectively. | TC11 in the Temperature Data File
SWGR Trip | PE/PVC, 7c, 12AWG |  | Channel 3 and Channel 4 represent the side and top of the thermocouple cable, respectively. | TC11 in the Temperature Data File
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds. Two different current transducers were for each circuit. One current transducer (Ohio Semitronics, model number CTL-51/35) was used to detect lower (0 - 35A) amperage transient behavior through a paired and calibrated signal conditioner (CTA201RX5). The other transducer (Ohio Semitronics, model number CTL-601/500) was set to detect transient current increases from 0 - 500A. These were also paired and calibrated with a signal conditioner (CTA2-1X5).
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | SWGR_CT500 | SWGR-a_CT35_1_PC | SWGR-a_CT35_2_N1 | SWGR-b_CT35_1_PT | SWGR-b_CT35_2_G | SWGR-b_CT35_3_R | SWGR-b_CT35_4_N2 | SWGR-a_VT7_1_C1 | SWGR-a_VTU_1_PC | SWGR-a_VTU_2_N1 | SWGR-b_VT7_1_G | SWGR-b_VT7_2_R | SWGR-b_VT7_3_T | SWGR-b_VT7_4_SP | SWGR-b_VT7_5_SP | SWGR-b_VTU_1_PT | SWGR-b_VTU_2_N2 | {SWGR-C} V(N1) - V(Batt -) | {SWGR-C} V(PC) - V(Batt +) | {SWGR-C} V(C1) - V(Batt +) | {SWGR-T} V(G) - V(Batt -) | {SWGR-T} V(R) - V(Batt +) | {SWGR-T} V(N2) - V(Batt -) | {SWGR-T} V(PT) - V(Batt +) | {SWGR-C} V(C1) - V(N1) | {SWGR-T} V(SP1) - V(Batt -) | {SWGR-T} V(SP2) - V(Batt -) | {SWGR-T} V(R) - V(Batt -) | {SWGR-T} V(PC) - V(Batt -) | {SWGR-T} V(C1) - V(Batt -) | {SWGR-T} V(PT) - V(Batt -) | {SWGR-T} V(T) - V(Batt -) | {SWGR-T} V(N2) - V(Batt -) | {SWGR-C} V(PC) - V(Batt -) | {SWGR-C} V(C1) - V(Batt -) | {SWGR-T} V(T) - V(Batt -) | {SWGR-T} V(R) - V(Batt -) | {SWGR-T} V(PT) - V(Batt -) | {SWGR-C} V(N1) - V(Batt +) | {SWGR-T} V(N2) - V(Batt +)
-0.03125 | 122.8958 | -60.6949 | 61.8439 | 0.21011 | 0.0025892 | 0.0062314 | -0.0020807 | 0.066806 | -0.00071986 | 0.069848 | -60.7681 | 61.7798 | -60.9787 | -60.8826 | 61.5967 | 0.054932 | -0.18768 | 0.16022 | 61.7661 | -60.965 | -0.28381 | -0.064087 | -0.073242 | -0.18768 | -0.24719 | -0.27008 | -0.07782 | 0.21057 | 60.5072 | 60.8551 | 122.2916 | 122.4747 | -0.073242 | 122.4609 | 60.7498 | -0.27008 | 122.4747 | -0.073242 | 60.7498 | 122.2916 | 122.4609 | -122.8226 | -122.8088
0.90625 | 122.8775 | -60.6857 | 61.821 | 0.26352 | 0.0038708 | 0.0079404 | 0.0026191 | 0.061893 | -0.0011471 | 0.066003 | -60.7956 | 61.8393 | -60.9695 | -60.8322 | 61.5234 | -0.10986 | -0.17853 | 0.17395 | 61.7889 | -61.0016 | -0.28381 | 0.01831 | -0.10986 | -0.14648 | -0.29755 | -0.31586 | -0.032044 | 0.17395 | 60.5072 | 60.8597 | 122.2092 | 122.525 | -0.10986 | 122.4747 | 60.5759 | -0.31586 | 122.525 | -0.10986 | 60.5759 | 122.2092 | 122.4747 | -122.7905 | -122.8226
1.9688 | 122.7859 | -60.7269 | 61.853 | 0.19485 | 0.0070752 | 0.0096494 | 0.0030463 | 0.065952 | 0.0033389 | 0.069848 | -60.8276 | 61.8347 | -61.0291 | -60.9512 | 61.5234 | -0.018311 | -0.07782 | 0.054932 | 61.8256 | -61.0107 | -0.30212 | -0.01831 | -0.10071 | -0.2243 | -0.32959 | -0.28381 | -0.027465 | 0.20142 | 60.6491 | 60.7819 | 122.2504 | 122.5616 | -0.10071 | 122.5525 | 60.7086 | -0.28381 | 122.5616 | -0.10071 | 60.7086 | 122.2504 | 122.5525 | -122.8821 | -122.8638
2.9219 | 122.7814 | -60.704 | 61.9125 | -0.3392 | 0.0051526 | 0.0045224 | -0.0003717 | 0.064884 | -0.0030697 | 0.069635 | -60.8368 | 61.8713 | -60.9787 | -60.9329 | 61.5509 | 0.045776 | 0.14648 | 0.18768 | 61.8896 | -61.0016 | -0.27466 | -0.041199 | -0.13275 | -0.22888 | -0.36163 | -0.29755 | -0.022889 | 0.14191 | 60.8505 | 60.8917 | 122.2549 | 122.5754 | -0.13275 | 122.5937 | 60.7498 | -0.29755 | 122.5754 | -0.13275 | 60.7498 | 122.2549 | 122.5937 | -122.8912 | -122.9141
3.9688 | 122.7905 | -60.7407 | 61.8805 | 0.17197 | 0.0068616 | 0.0087948 | 0.0030463 | 0.066379 | -0.00050626 | 0.067926 | -60.8505 | 61.8622 | -60.9924 | -60.9787 | 61.5143 | -0.059509 | -0.041199 | 0.027466 | 61.8164 | -61.0016 | -0.25177 | -0.01831 | -0.10986 | -0.23804 | -0.36621 | -0.26093 | -0.064087 | 0.14191 | 60.6995 | 60.7681 | 122.2549 | 122.6028 | -0.10986 | 122.5571 | 60.6812 | -0.26093 | 122.6028 | -0.10986 | 60.6812 | 122.2549 | 122.5571 | -122.8729 | -122.8821
4.9062 | 122.8821 | -60.6995 | 61.8256 | 0.22537 | 0.0028028 | 0.0079404 | -0.0012261 | 0.068302 | -0.0017881 | 0.068567 | -60.7773 | 61.7661 | -60.9558 | -60.8688 | 61.6013 | 0.054932 | -0.18768 | 0.15564 | 61.7935 | -60.9879 | -0.25635 | -0.05951 | -0.07782 | -0.16937 | -0.22431 | -0.28839 | -0.032044 | 0.17853 | 60.5118 | 60.8551 | 122.3007 | 122.4655 | -0.07782 | 122.493 | 60.7544 | -0.28839 | 122.4655 | -0.07782 | 60.7544 | 122.3007 | 122.493 | -122.7814 | -122.8134
5.9531 | 122.7997 | -60.7269 | 61.8805 | -0.21713 | 0.0030164 | 0.0085812 | 0.0017645 | 0.065952 | -0.0028561 | 0.068994 | -60.8826 | 61.8484 | -60.9787 | -60.8414 | 61.615 | 0.091553 | 0.068665 | 0.21973 | 61.8622 | -60.997 | -0.25177 | -0.032043 | -0.15564 | -0.11444 | -0.2655 | -0.27008 | -0.01831 | 0.096131 | 60.7956 | 60.9467 | 122.3419 | 122.5754 | -0.15564 | 122.5891 | 60.8185 | -0.27008 | 122.5754 | -0.15564 | 60.8185 | 122.3419 | 122.5891 | -122.8592 | -122.8775
6.9062 | 122.8729 | -60.6857 | 61.8439 | 0.19485 | 0.0051526 | 0.012854 | 0.0009101 | 0.065952 | -0.0024289 | 0.066644 | -60.7544 | 61.7844 | -60.9421 | -60.8826 | 61.6058 | 0.041199 | -0.19684 | 0.16022 | 61.7935 | -60.9604 | -0.25635 | -0.059509 | -0.068665 | -0.19684 | -0.23804 | -0.27466 | -0.050354 | 0.18768 | 60.4889 | 60.8459 | 122.2916 | 122.4701 | -0.068665 | 122.4792 | 60.7269 | -0.27466 | 122.4701 | -0.068665 | 60.7269 | 122.2916 | 122.4792 | -122.7859 | -122.8043
7.9688 | 122.8867 | -60.6857 | 61.8484 | -0.079803 | 0.004939 | 0.0017454 | -0.0061395 | 0.062107 | 0.00034814 | 0.06643 | -60.7819 | 61.7706 | -60.9375 | -60.8643 | 61.6241 | 0.10529 | -0.082397 | 0.22888 | 61.7844 | -60.9695 | -0.25177 | -0.07782 | -0.09613 | -0.17853 | -0.2243 | -0.28381 | -0.064087 | 0.15564 | 60.6033 | 60.9146 | 122.3099 | 122.4564 | -0.09613 | 122.4701 | 60.791 | -0.28381 | 122.4564 | -0.09613 | 60.791 | 122.3099 | 122.4701 | -122.7859 | -122.818
8.9062 | 122.8912 | -60.6949 | 61.8301 | 0.21774 | 0.0055798 | 0.0072996 | 0.0021917 | 0.064884 | -0.0017881 | 0.070916 | -60.7681 | 61.7798 | -60.9558 | -60.878 | 61.5875 | 0.041199 | -0.20599 | 0.16937 | 61.7615 | -61.0016 | -0.26093 | -0.050354 | -0.073242 | -0.18311 | -0.24262 | -0.3067 | -0.068664 | 0.18768 | 60.4889 | 60.8643 | 122.2824 | 122.4747 | -0.073242 | 122.4564 | 60.7361 | -0.3067 | 122.4747 | -0.073242 | 60.7361 | 122.2824 | 122.4564 | -122.7859 | -122.8317
9.9531 | 122.818 | -60.7269 | 61.8942 | 0.072784 | 0.0055798 | 0.010504 | 0.0060369 | 0.065311 | -0.0045651 | 0.069635 | -60.8139 | 61.8393 | -60.9879 | -60.9238 | 61.5097 | -0.013733 | 0.022888 | 0.091553 | 61.8484 | -60.9879 | -0.26093 | -0.054932 | -0.086975 | -0.19684 | -0.38452 | -0.26093 | -0.045776 | 0.17395 | 60.7498 | 60.8185 | 122.2366 | 122.5662 | -0.086975 | 122.5754 | 60.7132 | -0.26093 | 122.5662 | -0.086975 | 60.7132 | 122.2366 | 122.5754 | -122.8821 | -122.8821
10.9062 | 122.8867 | -60.6766 | 61.821 | 0.24826 | 0.0042982 | 0.0092222 | 0.0024053 | 0.066165 | 0.00013454 | 0.068994 | -60.7407 | 61.7935 | -60.9467 | -60.8734 | 61.6058 | 0.050354 | -0.19226 | 0.15106 | 61.7981 | -60.9833 | -0.27008 | -0.027466 | -0.064087 | -0.19684 | -0.21515 | -0.3067 | -0.022888 | 0.20599 | 60.4843 | 60.8276 | 122.2824 | 122.4701 | -0.064087 | 122.4747 | 60.7269 | -0.3067 | 122.4701 | -0.064087 | 60.7269 | 122.2824 | 122.4747 | -122.7676 | -122.8043
11.9531 | 122.8134 | -60.7224 | 61.8851 | -0.049286 | 0.0040846 | 0.010077 | 0.0056097 | 0.066593 | -0.0022153 | 0.067712 | -60.7819 | 61.8576 | -60.9833 | -60.8826 | 61.5784 | 0.045776 | 0.013733 | 0.16937 | 61.8393 | -61.0062 | -0.26092 | -0.027466 | -0.059509 | -0.16022 | -0.3067 | -0.28381 | -0.045777 | 0.20142 | 60.7361 | 60.8917 | 122.3007 | 122.58 | -0.059509 | 122.5616 | 60.7681 | -0.28381 | 122.58 | -0.059509 | 60.7681 | 122.3007 | 122.5616 | -122.8683 | -122.8912
12.9219 | 122.7722 | -60.7269 | 61.9308 | -0.21713 | 0.0045118 | 0.0068722 | 0.0013373 | 0.065525 | -0.0013609 | 0.067285 | -60.8459 | 61.8805 | -60.9833 | -60.9192 | 61.5417 | 0.050354 | 0.14191 | 0.17853 | 61.8988 | -61.0199 | -0.25635 | -0.050354 | -0.11902 | -0.19226 | -0.3891 | -0.29297 | -0.032043 | 0.13733 | 60.8688 | 60.9055 | 122.2687 | 122.6074 | -0.11902 | 122.6257 | 60.7773 | -0.29297 | 122.6074 | -0.11902 | 60.7773 | 122.2687 | 122.6257 | -122.9141 | -122.9507
13.9531 | 122.8638 | -60.7086 | 61.8484 | 0.15671 | 0.0030164 | 0.006445 | -0.0020807 | 0.066593 | -0.00050626 | 0.068353 | -60.7819 | 61.7889 | -60.9787 | -60.8917 | 61.6013 | 0.041199 | -0.16937 | 0.15564 | 61.8164 | -60.9833 | -0.27008 | -0.05951 | -0.073242 | -0.18311 | -0.24719 | -0.27466 | -0.032044 | 0.19684 | 60.5392 | 60.8643 | 122.3099 | 122.4976 | -0.073242 | 122.525 | 60.7498 | -0.27466 | 122.4976 | -0.073242 | 60.7498 | 122.3099 | 122.525 | -122.8271 | -122.8317
14.9062 | 122.85 | -60.704 | 61.853 | 0.14908 | 0.0023756 | 0.0075132 | 0.0004827 | 0.065097 | -0.00093346 | 0.068567 | -60.7773 | 61.7981 | -60.9924 | -60.878 | 61.5784 | 0.036621 | -0.19226 | 0.16479 | 61.7844 | -60.9924 | -0.28839 | -0.054931 | -0.073242 | -0.17395 | -0.27466 | -0.28839 | -0.068664 | 0.21515 | 60.5118 | 60.8688 | 122.2824 | 122.5021 | -0.073242 | 122.4884 | 60.7407 | -0.28839 | 122.5021 | -0.073242 | 60.7407 | 122.2824 | 122.4884 | -122.8455 | -122.8455
15.9531 | 122.7676 | -60.7132 | 61.8576 | 0.14145 | 0.0070752 | 0.0092222 | 0.0068915 | 0.065738 | 0.00034814 | 0.067071 | -60.8459 | 61.8668 | -60.9879 | -60.9833 | 61.4777 | -0.041199 | -0.004578 | 0.032043 | 61.8347 | -61.0291 | -0.27466 | 0.009155 | -0.13275 | -0.27008 | -0.37994 | -0.31586 | -0.022888 | 0.14191 | 60.7086 | 60.7452 | 122.1909 | 122.58 | -0.13275 | 122.5479 | 60.672 | -0.31586 | 122.58 | -0.13275 | 60.672 | 122.1909 | 122.5479 | -122.8455 | -122.8867
16.9062 | 122.8729 | -60.704 | 61.8347 | 0.1796 | 0.0072888 | 0.009863 | 0.0036871 | 0.065097 | -0.00050626 | 0.067712 | -60.8139 | 61.8256 | -60.9695 | -60.9192 | 61.5967 | 0.07782 | -0.14648 | -0.013733 | 61.8027 | -60.9924 | -0.2655 | -0.009155 | -0.10986 | -0.21515 | -0.23804 | -0.28839 | -0.032044 | 0.15564 | 60.5576 | 60.6903 | 122.3007 | 122.5296 | -0.10986 | 122.5067 | 60.7819 | -0.28839 | 122.5296 | -0.10986 | 60.7819 | 122.3007 | 122.5067 | -122.8043 | -122.8271
17.9688 | 122.8409 | -60.672 | 61.8851 | -0.18662 | 0.004939 | 0.0062314 | -0.0035761 | 0.065738 | -0.0017881 | 0.070062 | -60.7544 | 61.8393 | -60.9375 | -60.8688 | 61.6333 | 0.13275 | 0.027466 | 0.27466 | 61.8256 | -60.9833 | -0.2655 | -0.045777 | -0.082398 | -0.19684 | -0.25177 | -0.31128 | -0.059509 | 0.1831 | 60.6995 | 60.9467 | 122.3053 | 122.5113 | -0.082398 | 122.4976 | 60.8047 | -0.31128 | 122.5113 | -0.082398 | 60.8047 | 122.3053 | 122.4976 | -122.8226 | -122.8683
18.9062 | 122.8729 | -60.7178 | 61.8439 | 0.21011 | 0.00323 | 0.0083676 | -0.0029351 | 0.065952 | -0.00050626 | 0.067712 | -60.791 | 61.821 | -60.9604 | -60.9055 | 61.5601 | 0.16022 | -0.14191 | 0.045776 | 61.7935 | -60.9695 | -0.24262 | -0.022888 | -0.073243 | -0.18768 | -0.28381 | -0.25177 | -0.050354 | 0.16937 | 60.5759 | 60.7635 | 122.2778 | 122.5388 | -0.073243 | 122.5113 | 60.878 | -0.25177 | 122.5388 | -0.073243 | 60.878 | 122.2778 | 122.5113 | -122.8043 | -122.8134
19.9531 | 122.8134 | -60.7452 | 61.8439 | 0.21774 | 0.0075024 | 0.0083676 | 0.0047553 | 0.064884 | -0.0013609 | 0.068994 | -60.8322 | 61.8439 | -61.0153 | -60.9375 | 61.5234 | -0.041199 | -0.091553 | 0.054932 | 61.8073 | -61.0199 | -0.27008 | 0 | -0.086975 | -0.19226 | -0.32043 | -0.27466 | -0.036621 | 0.18311 | 60.6537 | 60.8002 | 122.2687 | 122.5891 | -0.086975 | 122.5525 | 60.704 | -0.27466 | 122.5891 | -0.086975 | 60.704 | 122.2687 | 122.5525 | -122.8592 | -122.8638
20.9062 | 122.8775 | -60.7178 | 61.8118 | 0.22537 | 0.0055798 | 0.0060178 | 0.0036871 | 0.065738 | 0.0012027 | 0.068994 | -60.7773 | 61.7935 | -60.9467 | -60.8826 | 61.6058 | 0.050354 | -0.19226 | 0.17395 | 61.7798 | -61.0016 | -0.22888 | -0.018311 | -0.05951 | -0.16479 | -0.20599 | -0.28381 | -0.032044 | 0.16937 | 60.5255 | 60.8917 | 122.3236 | 122.5113 | -0.05951 | 122.4976 | 60.7681 | -0.28381 | 122.5113 | -0.05951 | 60.7681 | 122.3236 | 122.4976 | -122.7585 | -122.8134
21.9531 | 122.7814 | -60.759 | 61.8393 | 0.1796 | 0.0047254 | 0.0049496 | 0.0062507 | 0.065525 | -0.0015745 | 0.070062 | -60.8688 | 61.8576 | -60.9924 | -60.9558 | 61.4868 | -0.073242 | -0.022888 | 0.022888 | 61.8256 | -61.0428 | -0.23346 | 0.018311 | -0.10986 | -0.19684 | -0.35248 | -0.28381 | -0.013732 | 0.1236 | 60.7361 | 60.7819 | 122.2458 | 122.6166 | -0.10986 | 122.5845 | 60.6857 | -0.28381 | 122.6166 | -0.10986 | 60.6857 | 122.2458 | 122.5845 | -122.8317 | -122.8821
22.9062 | 122.8638 | -60.704 | 61.8439 | 0.17197 | 0.0060072 | 0.0092222 | -0.0018671 | 0.066379 | 0.0012027 | 0.067926 | -60.7864 | 61.7981 | -60.9604 | -60.8826 | 61.6013 | 0.045776 | -0.17395 | 0.16479 | 61.7889 | -61.0016 | -0.25635 | -0.045776 | -0.082397 | -0.17853 | -0.24262 | -0.29755 | -0.054932 | 0.17395 | 60.5301 | 60.8688 | 122.3053 | 122.5021 | -0.082397 | 122.493 | 60.7498 | -0.29755 | 122.5021 | -0.082397 | 60.7498 | 122.3053 | 122.493 | -122.8043 | -122.8455
23.9531 | 122.7768 | -60.7315 | 61.8805 | 0.15671 | 0.004939 | 0.0083676 | 0.0047553 | 0.070438 | -0.0017881 | 0.06643 | -60.8688 | 61.8484 | -61.0153 | -60.9741 | 61.5005 | -0.064087 | -0.004578 | 0.032043 | 61.853 | -61.0107 | -0.28381 | -0.032043 | -0.13733 | -0.24261 | -0.37994 | -0.27924 | -0.027466 | 0.14649 | 60.7269 | 60.7635 | 122.2321 | 122.58 | -0.13733 | 122.5845 | 60.6674 | -0.27924 | 122.58 | -0.13733 | 60.6674 | 122.2321 | 122.5845 | -122.8958 | -122.8912
24.9062 | 122.9004 | -60.6857 | 61.8622 | -0.026398 | 0.0028028 | 0.0051632 | -0.0050715 | 0.066165 | -0.0015745 | 0.069421 | -60.8047 | 61.7889 | -60.9695 | -60.8826 | 61.6104 | 0.091553 | -0.082397 | 0.23804 | 61.8073 | -60.9512 | -0.28381 | -0.073243 | -0.11902 | -0.19684 | -0.25177 | -0.2655 | -0.054932 | 0.16479 | 60.6033 | 60.9238 | 122.2961 | 122.4747 | -0.11902 | 122.493 | 60.7773 | -0.2655 | 122.4747 | -0.11902 | 60.7773 | 122.2961 | 122.493 | -122.8317 | -122.8134
25.9688 | 122.7448 | -60.7315 | 61.8805 | 0.1796 | 0.0060072 | 0.0077268 | 0.0043281 | 0.065097 | 0.00056194 | 0.069207 | -60.8368 | 61.8713 | -60.9833 | -60.9787 | 61.4868 | -0.068665 | -0.009155 | 0.027466 | 61.8118 | -61.0291 | -0.25177 | -0.009155 | -0.10529 | -0.24719 | -0.39368 | -0.29755 | -0.068664 | 0.14648 | 60.7224 | 60.759 | 122.2183 | 122.6028 | -0.10529 | 122.5433 | 60.6628 | -0.29755 | 122.6028 | -0.10529 | 60.6628 | 122.2183 | 122.5433 | -122.8638 | -122.9095
26.9062 | 122.8271 | -60.7178 | 61.8393 | -0.14847 | 0.0028028 | 0.010717 | -0.0035761 | 0.064029 | -0.0020017 | 0.069207 | -60.8551 | 61.7661 | -60.9879 | -60.9055 | 61.5646 | 0.027466 | -0.091553 | 0.13275 | 61.7981 | -60.9741 | -0.27008 | -0.073242 | -0.13733 | -0.18768 | -0.27466 | -0.25635 | -0.041198 | 0.13275 | 60.6262 | 60.8505 | 122.2824 | 122.4838 | -0.13733 | 122.5159 | 60.7452 | -0.25635 | 122.4838 | -0.13733 | 60.7452 | 122.2824 | 122.5159 | -122.8271 | -122.8134
27.9688 | 122.7448 | -60.759 | 61.8805 | 0.0041197 | 0.0060072 | 0.010077 | 0.0062507 | 0.066379 | -0.0024289 | 0.068353 | -60.8276 | 61.8622 | -60.9879 | -60.9512 | 61.5051 | -0.032043 | 0.036621 | 0.059509 | 61.8301 | -60.997 | -0.22888 | -0.01831 | -0.068665 | -0.19226 | -0.37537 | -0.23804 | -0.050354 | 0.16022 | 60.7956 | 60.8185 | 122.2641 | 122.6212 | -0.068665 | 122.5891 | 60.7269 | -0.23804 | 122.6212 | -0.068665 | 60.7269 | 122.2641 | 122.5891 | -122.8683 | -122.8775
28.9062 | 122.8912 | -60.6995 | 61.8576 | 0.233 | 0.0034436 | 0.0079404 | 0.0009101 | 0.064243 | 0.0018435 | 0.070703 | -60.7681 | 61.8118 | -60.9558 | -60.8688 | 61.6104 | 0.050354 | -0.21057 | 0.15564 | 61.7432 | -60.997 | -0.25635 | -0.045776 | -0.068664 | -0.16937 | -0.24719 | -0.29755 | -0.11444 | 0.18768 | 60.4889 | 60.8551 | 122.3099 | 122.5113 | -0.068664 | 122.4426 | 60.7498 | -0.29755 | 122.5113 | -0.068664 | 60.7498 | 122.3099 | 122.4426 | -122.8134 | -122.8546
29.9531 | 122.8455 | -60.7132 | 61.8118 | 0.14908 | 0.0023756 | 0.005377 | -0.0014399 | 0.064884 | 0.0012027 | 0.067498 | -60.8047 | 61.7752 | -60.9833 | -60.8871 | 61.6058 | 0.041199 | -0.15564 | 0.16022 | 61.7706 | -60.9695 | -0.27008 | -0.036621 | -0.091553 | -0.17395 | -0.20599 | -0.25635 | -0.041199 | 0.17853 | 60.5576 | 60.8734 | 122.319 | 122.4884 | -0.091553 | 122.4838 | 60.7544 | -0.25635 | 122.4884 | -0.091553 | 60.7544 | 122.319 | 122.4838 | -122.7951 | -122.7814
30.9062 | 122.8821 | -60.6995 | 61.8347 | 0.21011 | 0.002162 | 0.0034544 | 0.0026191 | 0.065952 | -0.0022153 | 0.066217 | -60.7544 | 61.7844 | -60.9467 | -60.8734 | 61.6104 | 0.054932 | -0.20142 | 0.16937 | 61.7798 | -60.9833 | -0.24719 | -0.050354 | -0.054932 | -0.17395 | -0.2243 | -0.28381 | -0.054932 | 0.19226 | 60.498 | 60.8688 | 122.3099 | 122.4838 | -0.054932 | 122.4792 | 60.7544 | -0.28381 | 122.4838 | -0.054932 | 60.7544 | 122.3099 | 122.4792 | -122.7814 | -122.818
31.9531 | 122.8821 | -60.7132 | 61.8118 | 0.19485 | 0.0038708 | 0.006445 | 0.0036871 | 0.063816 | -0.00050626 | 0.066003 | -60.7727 | 61.7386 | -60.965 | -60.8688 | 61.6013 | 0.054932 | -0.21057 | 0.16022 | 61.7706 | -60.9879 | -0.25177 | -0.073243 | -0.059509 | -0.15564 | -0.21057 | -0.27466 | -0.041199 | 0.19226 | 60.5026 | 60.8734 | 122.3145 | 122.4518 | -0.059509 | 122.4838 | 60.7681 | -0.27466 | 122.4518 | -0.059509 | 60.7681 | 122.3145 | 122.4838 | -122.7768 | -122.7997
32.9062 | 122.8592 | -60.7132 | 61.8439 | 0.042267 | 0.002162 | 0.0070858 | -0.0033625 | 0.062107 | -0.0015745 | 0.067712 | -60.8368 | 61.7615 | -60.9604 | -60.9055 | 61.5921 | 0.045776 | -0.068665 | 0.16937 | 61.7844 | -60.9833 | -0.24719 | -0.082397 | -0.1236 | -0.19226 | -0.25177 | -0.27008 | -0.059509 | 0.1236 | 60.6445 | 60.8826 | 122.3053 | 122.4747 | -0.1236 | 122.4976 | 60.759 | -0.27008 | 122.4747 | -0.1236 | 60.759 | 122.3053 | 122.4976 | -122.8043 | -122.8271
33.9531 | 122.85 | -60.672 | 61.8622 | 0.11093 | 0.0019482 | 0.006445 | -0.0029351 | 0.061679 | -0.0022153 | 0.068994 | -60.8322 | 61.7889 | -60.9741 | -60.9055 | 61.5738 | 0.027466 | -0.086975 | 0.14648 | 61.8118 | -60.9467 | -0.30212 | -0.073243 | -0.16022 | -0.23346 | -0.28839 | -0.27466 | -0.050354 | 0.14191 | 60.585 | 60.8185 | 122.2458 | 122.4609 | -0.16022 | 122.4838 | 60.6995 | -0.27466 | 122.4609 | -0.16022 | 60.6995 | 122.2458 | 122.4838 | -122.8363 | -122.8088
34.9062 | 122.9187 | -60.6628 | 61.8668 | -0.17136 | 0.0030164 | 0.0038816 | -0.0014399 | 0.06232 | -0.0024289 | 0.067926 | -60.7407 | 61.7844 | -60.9467 | -60.8139 | 61.6425 | 0.14648 | -0.064087 | 0.3067 | 61.7889 | -60.9604 | -0.28381 | -0.082397 | -0.07782 | -0.15106 | -0.2243 | -0.29755 | -0.07782 | 0.20599 | 60.5988 | 60.9695 | 122.3053 | 122.4472 | -0.07782 | 122.4518 | 60.8093 | -0.29755 | 122.4472 | -0.07782 | 60.8093 | 122.3053 | 122.4518 | -122.8134 | -122.8271
35.9688 | 122.7631 | -60.7773 | 61.8851 | 0.095673 | 0.0057934 | 0.010931 | 0.0068915 | 0.063816 | -0.0034971 | 0.068994 | -60.8551 | 61.8439 | -60.997 | -60.9787 | 61.4868 | -0.054932 | 0.022888 | 0.022888 | 61.821 | -60.997 | -0.21973 | -0.041199 | -0.07782 | -0.20142 | -0.39826 | -0.21973 | -0.064087 | 0.14191 | 60.8002 | 60.8002 | 122.2641 | 122.6212 | -0.07782 | 122.5983 | 60.7224 | -0.21973 | 122.6212 | -0.07782 | 60.7224 | 122.2641 | 122.5983 | -122.8821 | -122.8821
36.9062 | 122.8592 | -60.6857 | 61.8668 | 0.011749 | 0.0017346 | 0.0079404 | -0.0044305 | 0.063388 | 0.00056194 | 0.068353 | -60.8231 | 61.7661 | -60.9467 | -60.8871 | 61.5921 | 0.068665 | -0.07782 | 0.18768 | 61.7706 | -60.9695 | -0.26093 | -0.10071 | -0.13733 | -0.20142 | -0.27466 | -0.28381 | -0.09613 | 0.1236 | 60.6079 | 60.8734 | 122.2778 | 122.4518 | -0.13733 | 122.4564 | 60.7544 | -0.28381 | 122.4518 | -0.13733 | 60.7544 | 122.2778 | 122.4564 | -122.8134 | -122.8363
37.9531 | 122.8363 | -60.6812 | 61.8622 | 0.011749 | 0.0013074 | 0.0072996 | 5.5496e-05 | 0.062534 | -0.0013609 | 0.070276 | -60.6491 | 61.7523 | -60.9329 | -60.8871 | 61.5875 | 0.027466 | -0.16479 | 0.15106 | 61.7661 | -60.9787 | -0.25177 | -0.10986 | 0.032043 | -0.20599 | -0.27466 | -0.29755 | -0.096131 | 0.28381 | 60.5164 | 60.8322 | 122.2687 | 122.4335 | 0.032043 | 122.4472 | 60.7086 | -0.29755 | 122.4335 | 0.032043 | 60.7086 | 122.2687 | 122.4472 | -122.7951 | -122.8409
38.9062 | 122.8455 | -60.6903 | 61.8484 | -2.7348 | 0.0045118 | 0.0092222 | 0.0004827 | 0.063816 | -0.0020017 | 0.068139 | -61.1023 | 61.7569 | -60.9787 | -60.8643 | 61.5692 | 0.027466 | -0.13733 | 0.13733 | 61.7798 | -60.9558 | -0.28839 | -0.091553 | -0.41199 | -0.17395 | -0.27924 | -0.2655 | -0.068665 | -0.1236 | 60.553 | 60.8276 | 122.2595 | 122.4472 | -0.41199 | 122.4701 | 60.7178 | -0.2655 | 122.4472 | -0.41199 | 60.7178 | 122.2595 | 122.4701 | -122.8271 | -122.8043
39.9688 | 122.7264 | -60.6812 | 61.908 | -0.2095 | 0.0079298 | 0.0075132 | 0.0049689 | 0.062534 | -0.00029266 | 0.066003 | -60.7956 | 61.9125 | -60.9787 | -60.8917 | 61.7615 | -0.004578 | -0.15106 | 0.3891 | 61.8256 | -61.0199 | -0.29755 | 0.004578 | -0.11444 | -0.21057 | -0.14648 | -0.33875 | -0.082397 | 0.18311 | 60.5301 | 61.0703 | 122.4426 | 122.5937 | -0.11444 | 122.5067 | 60.6766 | -0.33875 | 122.5937 | -0.11444 | 60.6766 | 122.4426 | 122.5067 | -122.8867 | -122.9279
40.9062 | 122.8912 | -60.6674 | 61.8713 | -0.17899 | 0.0010938 | 0.0045224 | -0.0025079 | 0.063816 | -0.0013609 | 0.067071 | -60.7361 | 61.7706 | -60.9512 | -60.8093 | 61.6562 | 0.15564 | -0.068665 | 0.30212 | 61.8118 | -60.9055 | -0.28381 | -0.10071 | -0.068665 | -0.14191 | -0.21515 | -0.23804 | -0.059509 | 0.21515 | 60.5988 | 60.9695 | 122.3236 | 122.438 | -0.068665 | 122.4792 | 60.8231 | -0.23804 | 122.438 | -0.068665 | 60.8231 | 122.3236 | 122.4792 | -122.8226 | -122.7768
41.9531 | 122.8592 | -60.6903 | 61.8805 | 0.0041197 | 0.0019482 | 0.0058042 | -0.0014399 | 0.061679 | 0.00056194 | 0.067498 | -60.8414 | 61.7752 | -60.9879 | -60.8917 | 61.5921 | 0.059509 | -0.07782 | 0.18768 | 61.8073 | -60.9695 | -0.29755 | -0.10529 | -0.15106 | -0.20142 | -0.28839 | -0.27923 | -0.073242 | 0.14648 | 60.6125 | 60.878 | 122.2824 | 122.4655 | -0.15106 | 122.4976 | 60.7498 | -0.27923 | 122.4655 | -0.15106 | 60.7498 | 122.2824 | 122.4976 | -122.8683 | -122.85
42.9062 | 122.8592 | -60.7224 | 61.8713 | -0.026398 | 0.0017346 | 0.003668 | -0.0010125 | 0.062961 | -7.9062e-05 | 0.069635 | -60.8368 | 61.7981 | -60.9695 | -60.8963 | 61.5784 | 0.054932 | -0.073242 | 0.17853 | 61.7889 | -60.9467 | -0.24719 | -0.073242 | -0.11444 | -0.17395 | -0.29297 | -0.2243 | -0.082398 | 0.13275 | 60.6491 | 60.9009 | 122.3007 | 122.5204 | -0.11444 | 122.5113 | 60.7773 | -0.2243 | 122.5204 | -0.11444 | 60.7773 | 122.3007 | 122.5113 | -122.8409 | -122.818
43.9531 | 122.8958 | -60.7132 | 61.8027 | 0.19485 | 0.002162 | 0.0075132 | -0.0010125 | 0.06232 | -0.0015745 | 0.069207 | -60.791 | 61.7661 | -60.965 | -60.8826 | 61.9125 | 0.36163 | -0.56305 | -0.086975 | 61.7523 | -60.965 | -0.25177 | -0.036621 | -0.07782 | -0.16937 | 0.10986 | -0.25177 | -0.050354 | 0.17395 | 60.1501 | 60.6262 | 122.6257 | 122.4792 | -0.07782 | 122.4655 | 61.0748 | -0.25177 | 122.4792 | -0.07782 | 61.0748 | 122.6257 | 122.4655 | -122.7676 | -122.7676
44.9062 | 122.7951 | -60.7224 | 61.8896 | -0.17136 | 0.0055798 | 0.010931 | 0.0075323 | 0.064456 | -0.00050626 | 0.066644 | -60.759 | 61.8668 | -60.9512 | -60.8505 | 61.5738 | 0.059509 | 0.032043 | 0.19684 | 61.8347 | -61.0153 | -0.22888 | -0.022888 | -0.036621 | -0.12817 | -0.31586 | -0.29297 | -0.054931 | 0.19226 | 60.7544 | 60.9192 | 122.2961 | 122.5891 | -0.036621 | 122.5571 | 60.7819 | -0.29297 | 122.5891 | -0.036621 | 60.7819 | 122.2961 | 122.5571 | -122.8409 | -122.905
45.9062 | 122.8409 | -60.704 | 61.8759 | 0.019379 | -0.00061524 | 0.0066586 | -0.0016535 | 0.063175 | 0.00077554 | 0.069207 | -60.8231 | 61.7844 | -60.9924 | -60.9146 | 61.5967 | 0.032043 | -0.073242 | 0.14648 | 61.7981 | -60.9604 | -0.28839 | -0.091553 | -0.11902 | -0.21057 | -0.27924 | -0.25635 | -0.07782 | 0.16937 | 60.6308 | 60.8505 | 122.3007 | 122.4884 | -0.11902 | 122.5021 | 60.7361 | -0.25635 | 122.4884 | -0.11902 | 60.7361 | 122.3007 | 122.5021 | -122.8683 | -122.8363
46.9062 | 122.8821 | -60.6949 | 61.8713 | 0.11856 | 0.0025892 | 0.0045224 | -0.0025079 | 0.05997 | 0.0014163 | 0.069635 | -60.7773 | 61.7889 | -60.9467 | -60.8459 | 61.6425 | 0.1236 | -0.10986 | 0.26093 | 61.8164 | -60.9329 | -0.25177 | -0.082398 | -0.082398 | -0.15106 | -0.22888 | -0.23804 | -0.054932 | 0.16937 | 60.585 | 60.9558 | 122.3373 | 122.4838 | -0.082398 | 122.5113 | 60.8185 | -0.23804 | 122.4838 | -0.082398 | 60.8185 | 122.3373 | 122.5113 | -122.818 | -122.8043
47.9688 | 122.8775 | -60.7132 | 61.8484 | 0.21774 | 0.0019482 | 0.0051632 | 0.0009101 | 0.062534 | -0.0017881 | 0.069635 | -60.759 | 61.7386 | -60.965 | -60.8505 | 61.5967 | 0.059509 | -0.18768 | 0.15106 | 61.7523 | -60.9695 | -0.25177 | -0.10986 | -0.045776 | -0.13733 | -0.25177 | -0.25635 | -0.096131 | 0.20599 | 60.5255 | 60.8643 | 122.3099 | 122.4518 | -0.045776 | 122.4655 | 60.7727 | -0.25635 | 122.4518 | -0.045776 | 60.7727 | 122.3099 | 122.4655 | -122.8134 | -122.818
48.9062 | 122.8638 | -60.6857 | 61.8759 | 0.049896 | 0.00323 | 0.0049496 | -0.0035761 | 0.060398 | 0.0012027 | 0.066858 | -60.8276 | 61.7935 | -60.965 | -60.8826 | 61.5921 | 0.073242 | -0.082397 | 0.18768 | 61.7844 | -60.9467 | -0.27924 | -0.082398 | -0.14191 | -0.19684 | -0.28381 | -0.26093 | -0.091553 | 0.13733 | 60.6033 | 60.8734 | 122.2778 | 122.4792 | -0.14191 | 122.4701 | 60.759 | -0.26093 | 122.4792 | -0.14191 | 60.759 | 122.2778 | 122.4701 | -122.8409 | -122.8226
49.9688 | 122.7905 | -60.7224 | 61.908 | -0.1561 | 0.0068616 | 0.0062314 | 0.0002691 | 0.061038 | -0.0011471 | 0.068567 | -60.8093 | 61.8988 | -60.9421 | -60.91 | 61.5326 | 0.050354 | 0.13733 | 0.17853 | 61.8576 | -61.0062 | -0.21973 | -0.009155 | -0.086975 | -0.18768 | -0.37537 | -0.28381 | -0.050354 | 0.13275 | 60.8597 | 60.9009 | 122.2549 | 122.6212 | -0.086975 | 122.58 | 60.7727 | -0.28381 | 122.6212 | -0.086975 | 60.7727 | 122.2549 | 122.58 | -122.85 | -122.9141
50.9062 | 122.8958 | -60.6995 | 61.853 | -0.034027 | 0.002162 | 0.0055906 | -0.0014399 | 0.06232 | -0.00093346 | 0.070062 | -60.7956 | 61.7752 | -60.965 | -60.8643 | 61.6241 | 0.086975 | -0.073242 | 0.2243 | 61.8073 | -60.9375 | -0.2655 | -0.077819 | -0.09613 | -0.16479 | -0.22888 | -0.23804 | -0.045776 | 0.16937 | 60.6262 | 60.9238 | 122.3236 | 122.4747 | -0.09613 | 122.5067 | 60.7864 | -0.23804 | 122.4747 | -0.09613 | 60.7864 | 122.3236 | 122.5067 | -122.818 | -122.7905
51.9062 | 122.8317 | -60.7269 | 61.8576 | -0.087433 | 0.001521 | 0.0075132 | -0.0037897 | 0.062107 | -0.0013609 | 0.06878 | -60.8597 | 61.7615 | -60.9695 | -60.9192 | 61.5784 | 0.045776 | -0.064087 | 0.15106 | 61.7798 | -60.9512 | -0.24261 | -0.09613 | -0.13275 | -0.19226 | -0.27924 | -0.2243 | -0.07782 | 0.10986 | 60.6628 | 60.878 | 122.3053 | 122.4884 | -0.13275 | 122.5067 | 60.7727 | -0.2243 | 122.4884 | -0.13275 | 60.7727 | 122.3053 | 122.5067 | -122.8271 | -122.8088
52.9531 | 122.8409 | -60.7178 | 61.8713 | 0.13382 | 0.0023756 | 0.0051632 | -0.0012261 | 0.060611 | -0.00093346 | 0.068994 | -60.8002 | 61.7523 | -60.9787 | -60.8826 | 61.5784 | 0.045776 | -0.15564 | 0.13275 | 61.7569 | -60.9787 | -0.26093 | -0.11902 | -0.082398 | -0.16479 | -0.29297 | -0.26093 | -0.11444 | 0.17853 | 60.5621 | 60.8505 | 122.2961 | 122.4701 | -0.082398 | 122.4747 | 60.7635 | -0.26093 | 122.4701 | -0.082398 | 60.7635 | 122.2961 | 122.4747 | -122.85 | -122.85
53.9062 | 122.8729 | -60.6949 | 61.8668 | -0.064545 | 0.0042982 | 0.0085812 | -0.0029351 | 0.060398 | 0.00034814 | 0.067712 | -60.8047 | 61.7661 | -60.9604 | -60.8368 | 61.6333 | 0.10529 | -0.073242 | 0.24719 | 61.7798 | -60.9558 | -0.2655 | -0.10071 | -0.10986 | -0.14191 | -0.23346 | -0.26093 | -0.086975 | 0.15564 | 60.6216 | 60.9421 | 122.3282 | 122.4609 | -0.10986 | 122.4747 | 60.8002 | -0.26093 | 122.4609 | -0.10986 | 60.8002 | 122.3282 | 122.4747 | -122.8271 | -122.8226
54.9844 | 122.7676 | -60.7132 | 61.8896 | 0.88913 | 0.0034436 | 0.0085812 | 0.0039007 | 0.064029 | -0.0032835 | 0.067071 | -60.6995 | 61.8347 | -60.9879 | -60.8459 | 61.5875 | 0.07782 | 0.009155 | 0.18768 | 61.7935 | -60.9787 | -0.27466 | -0.054931 | 0.013733 | -0.13275 | -0.30212 | -0.2655 | -0.09613 | 0.28839 | 60.7224 | 60.9009 | 122.3007 | 122.5479 | 0.013733 | 122.5067 | 60.791 | -0.2655 | 122.5479 | 0.013733 | 60.791 | 122.3007 | 122.5067 | -122.8775 | -122.8683
55.9062 | 122.85 | -60.6949 | 61.8484 | 0.088043 | 0.0019482 | 0.0028134 | -0.0031489 | 0.06467 | 0.0024845 | 0.067712 | -60.8322 | 61.7661 | -60.9741 | -60.9055 | 61.5921 | 0.15564 | -0.027466 | 0.09613 | 61.8164 | -60.9192 | -0.27924 | -0.082398 | -0.13733 | -0.21057 | -0.25635 | -0.2243 | -0.032044 | 0.14191 | 60.6674 | 60.791 | 122.287 | 122.4609 | -0.13733 | 122.5113 | 60.8505 | -0.2243 | 122.4609 | -0.13733 | 60.8505 | 122.287 | 122.5113 | -122.8226 | -122.7676
56.9531 | 122.8729 | -60.6949 | 61.8576 | 0.019379 | 0.0045118 | 0.0051632 | -0.0029351 | 0.064243 | -0.0022153 | 0.069635 | -60.8368 | 61.7661 | -60.9879 | -60.8826 | 61.6013 | 0.050354 | -0.07782 | 0.17853 | 61.7981 | -60.9421 | -0.29297 | -0.091553 | -0.14191 | -0.18768 | -0.25635 | -0.24719 | -0.059509 | 0.15106 | 60.6171 | 60.8734 | 122.2961 | 122.4609 | -0.14191 | 122.493 | 60.7452 | -0.24719 | 122.4609 | -0.14191 | 60.7452 | 122.2961 | 122.493 | -122.8455 | -122.7997
57.9062 | 122.8409 | -60.704 | 61.8759 | 0.11093 | 0.0038708 | 0.0060178 | 5.5496e-05 | 0.061893 | 0.00077554 | 0.069207 | -60.8231 | 61.7706 | -60.9695 | -60.9192 | 61.5738 | 0.022888 | -0.11444 | 0.14648 | 61.7569 | -60.965 | -0.2655 | -0.10529 | -0.11902 | -0.21515 | -0.30212 | -0.26093 | -0.11902 | 0.14648 | 60.5896 | 60.8505 | 122.2778 | 122.4747 | -0.11902 | 122.4609 | 60.7269 | -0.26093 | 122.4747 | -0.11902 | 60.7269 | 122.2778 | 122.4609 | -122.8455 | -122.8409
58.9688 | 122.7585 | -60.7498 | 61.8988 | 0.034637 | 0.0053662 | 0.0077268 | 0.0051825 | 0.064884 | -0.00071986 | 0.067926 | -60.8185 | 61.821 | -60.997 | -60.9192 | 61.5372 | 0 | 0.009155 | 0.091553 | 61.8118 | -60.9924 | -0.24719 | -0.07782 | -0.068664 | -0.16937 | -0.36163 | -0.24262 | -0.086975 | 0.17853 | 60.759 | 60.8414 | 122.287 | 122.5708 | -0.068664 | 122.5616 | 60.7498 | -0.24262 | 122.5708 | -0.068664 | 60.7498 | 122.287 | 122.5616 | -122.8958 | -122.8912
59.9062 | 122.9141 | -60.6903 | 61.8759 | -0.2858 | 0.0045118 | 0.0066586 | -0.0020807 | 0.064243 | -7.9062e-05 | 0.068567 | -60.7544 | 61.8073 | -60.9283 | -60.8276 | 61.6516 | 0.13733 | -0.027466 | 0.28381 | 61.821 | -60.9146 | -0.23804 | -0.068665 | -0.064087 | -0.13733 | -0.2243 | -0.2243 | -0.054932 | 0.17395 | 60.6628 | 60.9741 | 122.3419 | 122.4976 | -0.064087 | 122.5113 | 60.8276 | -0.2243 | 122.4976 | -0.064087 | 60.8276 | 122.3419 | 122.5113 | -122.8043 | -122.7905
60.9688 | 122.9095 | -60.6903 | 61.8439 | 0.12619 | 0.0036572 | 0.0038816 | 0.0043281 | 0.065738 | -0.0024289 | 0.069207 | -60.8002 | 61.7661 | -60.9879 | -60.8826 | 61.5875 | 0.036621 | -0.16937 | 0.1236 | 61.7935 | -60.9421 | -0.29755 | -0.07782 | -0.10986 | -0.19226 | -0.25635 | -0.25177 | -0.050354 | 0.18768 | 60.5209 | 60.8139 | 122.2778 | 122.4564 | -0.10986 | 122.4838 | 60.7269 | -0.25177 | 122.4564 | -0.10986 | 60.7269 | 122.2778 | 122.4838 | -122.8317 | -122.7859
61.9062 | 122.9599 | -60.6995 | 61.8668 | 0.034637 | 0.0019482 | 0.0070858 | -0.0042169 | 0.062534 | -0.00093346 | 0.067498 | -60.8276 | 61.7752 | -60.9558 | -60.9055 | 61.6013 | 0.027466 | -0.068665 | 0.15564 | 61.8118 | -60.9512 | -0.25635 | -0.091552 | -0.12817 | -0.20599 | -0.2655 | -0.25177 | -0.054931 | 0.12817 | 60.6308 | 60.8551 | 122.3007 | 122.4747 | -0.12817 | 122.5113 | 60.7269 | -0.25177 | 122.4747 | -0.12817 | 60.7269 | 122.3007 | 122.5113 | -122.8226 | -122.818
62.9062 | 122.8592 | -60.7132 | 61.8301 | 0.20248 | 0.002162 | 0.0092222 | 0.0013373 | 0.06232 | -7.9062e-05 | 0.068567 | -60.7727 | 61.7844 | -60.965 | -60.8734 | 61.5921 | 0.050354 | -0.16022 | 0.14648 | 61.7386 | -60.9924 | -0.25177 | -0.045776 | -0.059509 | -0.16022 | -0.23804 | -0.27924 | -0.091553 | 0.19226 | 60.553 | 60.8597 | 122.3053 | 122.4976 | -0.059509 | 122.4518 | 60.7636 | -0.27924 | 122.4976 | -0.059509 | 60.7636 | 122.3053 | 122.4518 | -122.7951 | -122.8226
63.9531 | 122.9141 | -60.672 | 61.8393 | 0.21011 | 0.0028028 | 0.0087948 | 0.0009101 | 0.06467 | 0.0029117 | 0.066644 | -60.759 | 61.7798 | -60.9467 | -60.9421 | 61.6837 | 0.1831 | -0.16479 | 0.1236 | 61.7615 | -60.9558 | -0.27466 | -0.059509 | -0.086975 | -0.27008 | -0.15564 | -0.28381 | -0.077819 | 0.18768 | 60.5072 | 60.7956 | 122.3557 | 122.4518 | -0.086975 | 122.4335 | 60.8551 | -0.28381 | 122.4518 | -0.086975 | 60.8551 | 122.3557 | 122.4335 | -122.7859 | -122.7951
64.9062 | 122.8683 | -60.6949 | 61.8484 | 0.080414 | 0.0034436 | 0.010077 | -0.0012261 | 0.063175 | 0.00034814 | 0.068994 | -60.8047 | 61.7935 | -60.9741 | -60.9192 | 61.5692 | 0.027466 | -0.11902 | 0.12817 | 61.7706 | -60.9879 | -0.27924 | -0.054932 | -0.10986 | -0.2243 | -0.27924 | -0.29297 | -0.07782 | 0.16937 | 60.5759 | 60.8231 | 122.2641 | 122.4884 | -0.10986 | 122.4655 | 60.7224 | -0.29297 | 122.4884 | -0.10986 | 60.7224 | 122.2641 | 122.4655 | -122.8226 | -122.8363
65.9531 | 122.9004 | -60.7132 | 61.8164 | 0.1796 | 0.0042982 | 0.0072996 | 0.0068915 | 0.063602 | -0.00071986 | 0.067712 | -60.7727 | 61.7935 | -60.9558 | -60.8505 | 61.5967 | 0.041199 | -0.19684 | 0.15564 | 61.7477 | -60.9833 | -0.24261 | -0.022888 | -0.059509 | -0.13733 | -0.21973 | -0.27008 | -0.068664 | 0.18311 | 60.5164 | 60.8688 | 122.3099 | 122.5067 | -0.059509 | 122.4609 | 60.7544 | -0.27008 | 122.5067 | -0.059509 | 60.7544 | 122.3099 | 122.4609 | -122.7722 | -122.7997
66.9062 | 122.8638 | -60.7086 | 61.8256 | 0.22537 | 0.0047254 | 0.0083676 | 0.0039007 | 0.062961 | -0.0026425 | 0.068353 | -60.7681 | 61.8073 | -60.9604 | -60.8643 | 61.5829 | 0.045776 | -0.17395 | 0.13275 | 61.7615 | -60.9924 | -0.25177 | -0.018311 | -0.059509 | -0.15564 | -0.24262 | -0.28381 | -0.064087 | 0.19226 | 60.5347 | 60.8414 | 122.2916 | 122.5159 | -0.059509 | 122.4701 | 60.7544 | -0.28381 | 122.5159 | -0.059509 | 60.7544 | 122.2916 | 122.4701 | -122.7859 | -122.818
67.9688 | 122.8775 | -60.6949 | 61.8393 | -0.018768 | 0.0036572 | 0.0087948 | 0.0053961 | 0.06467 | -0.00029266 | 0.066003 | -60.8185 | 61.7981 | -60.9879 | -60.8688 | 61.5967 | 0.050354 | -0.19226 | 0.14191 | 61.7569 | -60.9741 | -0.29297 | -0.041198 | -0.1236 | -0.17395 | -0.24261 | -0.27924 | -0.082397 | 0.16937 | 60.5026 | 60.8368 | 122.2916 | 122.493 | -0.1236 | 122.4518 | 60.7452 | -0.27924 | 122.493 | -0.1236 | 60.7452 | 122.2916 | 122.4518 | -122.8271 | -122.8134
68.9062 | 122.8546 | -60.7086 | 61.8484 | 0.12619 | 0.004939 | 0.0070858 | -0.0018671 | 0.063175 | -0.00050626 | 0.068353 | -60.8185 | 61.7889 | -60.9512 | -60.91 | 61.5692 | 0.022888 | -0.13733 | 0.13733 | 61.7798 | -60.9604 | -0.24262 | -0.05951 | -0.10986 | -0.20142 | -0.27924 | -0.25177 | -0.068665 | 0.13275 | 60.5713 | 60.8459 | 122.2778 | 122.4976 | -0.10986 | 122.4884 | 60.7315 | -0.25177 | 122.4976 | -0.10986 | 60.7315 | 122.2778 | 122.4884 | -122.7997 | -122.8088
69.9688 | 122.8271 | -60.7086 | 61.8576 | 0.24063 | 0.0055798 | 0.013067 | 0.0036871 | 0.06467 | -0.0017881 | 0.069207 | -60.8231 | 61.8301 | -60.9879 | -60.8871 | 61.5738 | 0 | -0.16022 | 0.1236 | 61.7615 | -60.9695 | -0.27924 | -0.027466 | -0.11444 | -0.17853 | -0.28381 | -0.26093 | -0.09613 | 0.16479 | 60.5484 | 60.8322 | 122.2824 | 122.5388 | -0.11444 | 122.4701 | 60.7086 | -0.26093 | 122.5388 | -0.11444 | 60.7086 | 122.2824 | 122.4701 | -122.8455 | -122.8271
70.9062 | 122.8775 | -60.6812 | 61.821 | 0.21774 | 0.0060072 | 0.0060178 | 0.0013373 | 0.062961 | -0.0026425 | 0.068567 | -60.759 | 61.7798 | -60.9924 | -60.8597 | 61.6287 | 0.068665 | -0.19226 | 0.16479 | 61.7798 | -60.9695 | -0.31128 | -0.041199 | -0.07782 | -0.17853 | -0.19226 | -0.28839 | -0.041199 | 0.23346 | 60.4889 | 60.8459 | 122.3099 | 122.4609 | -0.07782 | 122.4609 | 60.7498 | -0.28839 | 122.4609 | -0.07782 | 60.7498 | 122.3099 | 122.4609 | -122.8134 | -122.7905
71.9688 | 122.7905 | -60.7224 | 61.8576 | -0.011139 | 0.0060072 | 0.0060178 | 0.0062507 | 0.064884 | -0.00071986 | 0.067712 | -60.7864 | 61.8439 | -61.0016 | -60.9009 | 61.5372 | 0.022888 | 0.013733 | 0.1236 | 61.8484 | -60.9879 | -0.27924 | -0.013733 | -0.064087 | -0.17853 | -0.32043 | -0.2655 | -0.009155 | 0.21515 | 60.7361 | 60.8459 | 122.2595 | 122.5662 | -0.064087 | 122.5708 | 60.7452 | -0.2655 | 122.5662 | -0.064087 | 60.7452 | 122.2595 | 122.5708 | -122.8592 | -122.8455
72.9062 | 122.8638 | -60.7224 | 61.8439 | 0.21774 | 0.0060072 | 0.0079404 | 0.0030463 | 0.066593 | -0.0013609 | 0.070703 | -60.8185 | 61.8439 | -60.9833 | -60.8963 | 61.5646 | 0.018311 | -0.15106 | 0.10986 | 61.7889 | -60.9604 | -0.26092 | 0 | -0.09613 | -0.17395 | -0.27924 | -0.23804 | -0.054932 | 0.16479 | 60.5713 | 60.8322 | 122.287 | 122.5662 | -0.09613 | 122.5113 | 60.7407 | -0.23804 | 122.5662 | -0.09613 | 60.7407 | 122.287 | 122.5113 | -122.8271 | -122.8043
73.9531 | 122.7997 | -60.6949 | 61.8896 | -0.14847 | 0.0070752 | 0.0085812 | 0.0032599 | 0.066593 | -0.0028561 | 0.066858 | -60.7636 | 61.8713 | -60.9604 | -60.8688 | 61.5967 | 0.10071 | 0.054932 | 0.17853 | 61.8576 | -60.9787 | -0.2655 | -0.01831 | -0.068665 | -0.17395 | -0.29297 | -0.28381 | -0.032043 | 0.19684 | 60.7498 | 60.8734 | 122.2916 | 122.5662 | -0.068665 | 122.5525 | 60.7956 | -0.28381 | 122.5662 | -0.068665 | 60.7956 | 122.2916 | 122.5525 | -122.85 | -122.8683
74.9062 | 122.8592 | -60.6812 | 61.8713 | 0.065155 | 0.0019482 | 0.0017454 | -0.0048577 | 0.065738 | -0.0026425 | 0.069421 | -60.8322 | 61.7752 | -60.9787 | -60.8917 | 61.6104 | 0.07782 | -0.064087 | 0.1831 | 61.8027 | -60.9375 | -0.29755 | -0.09613 | -0.15106 | -0.21057 | -0.26093 | -0.25635 | -0.068665 | 0.14648 | 60.6171 | 60.8643 | 122.2916 | 122.4564 | -0.15106 | 122.4838 | 60.759 | -0.25635 | 122.4564 | -0.15106 | 60.759 | 122.2916 | 122.4838 | -122.85 | -122.8088
75.9688 | 122.818 | -60.6903 | 61.908 | -0.21713 | 0.0055798 | 0.0072996 | 0.0058233 | 0.064884 | -0.0024289 | 0.068567 | -60.7773 | 61.8622 | -60.9695 | -60.8871 | 61.5692 | 0.082397 | 0.073242 | 0.19684 | 61.853 | -60.9879 | -0.27923 | -0.045776 | -0.086975 | -0.19684 | -0.33874 | -0.29755 | -0.054932 | 0.19226 | 60.7636 | 60.8871 | 122.2595 | 122.5525 | -0.086975 | 122.5433 | 60.7727 | -0.29755 | 122.5525 | -0.086975 | 60.7727 | 122.2595 | 122.5433 | -122.8775 | -122.8958
76.9062 | 122.8638 | -60.6995 | 61.8439 | 0.22537 | 0.0042982 | 0.0094358 | 0.0013373 | 0.067447 | -0.00093346 | 0.069421 | -60.9421 | 61.7661 | -60.9695 | -60.8322 | 61.6196 | 0.068665 | -0.19684 | 0.16479 | 61.7798 | -60.9879 | -0.27008 | -0.07782 | -0.24262 | -0.13275 | -0.2243 | -0.28839 | -0.064087 | 0.027465 | 60.5026 | 60.8643 | 122.319 | 122.4655 | -0.24262 | 122.4792 | 60.7681 | -0.28839 | 122.4655 | -0.24262 | 60.7681 | 122.319 | 122.4792 | -122.8134 | -122.8317
77.9688 | 122.7676 | -60.7407 | 61.8576 | 0.034637 | 0.0051526 | 0.0062314 | 0.0060369 | 0.065738 | -0.00093346 | 0.069635 | -60.8093 | 61.8576 | -60.9695 | -60.9375 | 61.5234 | -0.004578 | 0.036621 | 0.07782 | 61.8301 | -60.9924 | -0.22888 | 0 | -0.068664 | -0.19684 | -0.33417 | -0.25177 | -0.027466 | 0.16022 | 60.7773 | 60.8185 | 122.2641 | 122.5983 | -0.068664 | 122.5708 | 60.7361 | -0.25177 | 122.5983 | -0.068664 | 60.7361 | 122.2641 | 122.5708 | -122.8271 | -122.85
78.9062 | 122.8683 | -60.6995 | 61.8393 | 0.30167 | 0.0055798 | 0.011358 | 0.0011237 | 0.06702 | -0.0013609 | 0.070703 | -60.7773 | 61.7981 | -60.9741 | -60.8734 | 61.6104 | 0.045776 | -0.17853 | 0.15564 | 61.7981 | -60.9833 | -0.27466 | -0.041198 | -0.07782 | -0.17395 | -0.22888 | -0.28381 | -0.041198 | 0.19684 | 60.5209 | 60.8551 | 122.3099 | 122.4976 | -0.07782 | 122.4976 | 60.7452 | -0.28381 | 122.4976 | -0.07782 | 60.7452 | 122.3099 | 122.4976 | -122.8134 | -122.8226
79.9531 | 122.8546 | -60.6995 | 61.8393 | 0.21774 | 0.0038708 | 0.0094358 | -0.0025079 | 0.065738 | 0.00013454 | 0.069421 | -60.7773 | 61.7844 | -60.9741 | -60.8917 | 61.5875 | 0.027466 | -0.16479 | 0.16479 | 61.7889 | -60.9924 | -0.27466 | -0.054931 | -0.07782 | -0.19226 | -0.25177 | -0.29297 | -0.050354 | 0.19684 | 60.5347 | 60.8643 | 122.287 | 122.4838 | -0.07782 | 122.4884 | 60.7269 | -0.29297 | 122.4838 | -0.07782 | 60.7269 | 122.287 | 122.4884 | -122.8134 | -122.8317
80.9062 | 122.7997 | -60.759 | 61.8713 | 0.16434 | 0.0060072 | 0.0090086 | 0.0053961 | 0.066165 | -0.0026425 | 0.06878 | -60.8414 | 61.8713 | -60.997 | -60.9604 | 61.5189 | -0.036621 | -0.036621 | 0.045776 | 61.8576 | -61.0291 | -0.23804 | 0 | -0.082398 | -0.20142 | -0.35248 | -0.27008 | -0.013733 | 0.15564 | 60.7224 | 60.8047 | 122.2778 | 122.6303 | -0.082398 | 122.6166 | 60.7224 | -0.27008 | 122.6303 | -0.082398 | 60.7224 | 122.2778 | 122.6166 | -122.8683 | -122.9004
81.9531 | 122.7722 | -60.7132 | 61.8713 | -0.056915 | 0.0057934 | 0.01264 | 0.0060369 | 0.06702 | -0.0037107 | 0.069421 | -60.7681 | 61.8713 | -60.9879 | -60.8963 | 61.5555 | 0.068665 | 0.027466 | 0.17853 | 61.8393 | -60.9741 | -0.27466 | 0 | -0.054931 | -0.1831 | -0.31586 | -0.26092 | -0.032044 | 0.21973 | 60.7407 | 60.8917 | 122.2687 | 122.5845 | -0.054931 | 122.5525 | 60.7819 | -0.26092 | 122.5845 | -0.054931 | 60.7819 | 122.2687 | 122.5525 | -122.8592 | -122.8455
82.9062 | 122.8638 | -60.7407 | 61.8301 | 0.20248 | 0.0030164 | 0.0094358 | -0.0012261 | 0.065738 | -0.0015745 | 0.070276 | -60.7773 | 61.8027 | -60.9558 | -60.878 | 61.6013 | 0.064087 | -0.17395 | 0.16022 | 61.8073 | -60.9787 | -0.21515 | -0.027466 | -0.036621 | -0.13733 | -0.22888 | -0.23804 | -0.022888 | 0.17853 | 60.5667 | 60.9009 | 122.3419 | 122.5433 | -0.036621 | 122.5479 | 60.8047 | -0.23804 | 122.5433 | -0.036621 | 60.8047 | 122.3419 | 122.5479 | -122.7859 | -122.8088
83.9688 | 122.7585 | -60.7224 | 61.8713 | 0.0041197 | 0.0053662 | 0.0083676 | 0.0060369 | 0.065952 | -0.00029266 | 0.068139 | -60.8139 | 61.8622 | -61.0016 | -60.9238 | 61.5234 | -0.004578 | 0.032043 | 0.10071 | 61.8301 | -61.0153 | -0.27924 | -0.009155 | -0.091553 | -0.20142 | -0.3479 | -0.29297 | -0.041199 | 0.18768 | 60.7544 | 60.8231 | 122.2458 | 122.5845 | -0.091553 | 122.5525 | 60.7178 | -0.29297 | 122.5845 | -0.091553 | 60.7178 | 122.2458 | 122.5525 | -122.8729 | -122.8867
84.9062 | 122.8134 | -60.6949 | 61.8896 | -0.25528 | 0.002162 | 0.003668 | -0.0020807 | 0.06467 | -0.00029266 | 0.068353 | -60.7727 | 61.7798 | -60.9879 | -60.8688 | 61.6058 | 0.10986 | 0.073242 | 0.25177 | 61.8484 | -60.9558 | -0.29297 | -0.10986 | -0.07782 | -0.17395 | -0.28381 | -0.26093 | -0.041198 | 0.21515 | 60.7681 | 60.9467 | 122.3007 | 122.4747 | -0.07782 | 122.5433 | 60.8047 | -0.26093 | 122.4747 | -0.07782 | 60.8047 | 122.3007 | 122.5433 | -122.8775 | -122.8455
85.9531 | 122.7905 | -60.7315 | 61.8805 | -0.018768 | 0.0038708 | 0.0079404 | 0.0036871 | 0.065311 | -0.0032835 | 0.069421 | -60.7773 | 61.8851 | -60.9695 | -60.91 | 61.5509 | 0.018311 | 0.013733 | 0.13275 | 61.8347 | -61.0107 | -0.23804 | 0.004578 | -0.045777 | -0.17853 | -0.32959 | -0.27924 | -0.045776 | 0.19226 | 60.7452 | 60.8643 | 122.2824 | 122.6166 | -0.045777 | 122.5662 | 60.7498 | -0.27924 | 122.6166 | -0.045777 | 60.7498 | 122.2824 | 122.5662 | -122.85 | -122.8912
86.9062 | 122.8134 | -60.7407 | 61.8622 | 0.1796 | 0.004939 | 0.0090086 | 0.0036871 | 0.065952 | 0.00034814 | 0.067285 | -60.8459 | 61.8668 | -61.0153 | -60.965 | 61.5143 | -0.022888 | -0.036621 | 0.041199 | 61.853 | -61.0153 | -0.27466 | 0.004577 | -0.10529 | -0.2243 | -0.3479 | -0.27466 | -0.009156 | 0.16937 | 60.704 | 60.7819 | 122.2549 | 122.6074 | -0.10529 | 122.5937 | 60.7178 | -0.27466 | 122.6074 | -0.10529 | 60.7178 | 122.2549 | 122.5937 | -122.8775 | -122.8775
87.9531 | 122.8043 | -60.6995 | 61.8942 | -0.17899 | 0.004939 | 0.0049496 | 0.0011237 | 0.066806 | -0.0032835 | 0.067071 | -60.8047 | 61.9125 | -60.9604 | -60.8917 | 61.5692 | 0.068665 | 0.09613 | 0.18768 | 61.8851 | -61.0245 | -0.26093 | 0.018311 | -0.10529 | -0.19226 | -0.32501 | -0.32501 | -0.009155 | 0.15564 | 60.7956 | 60.8871 | 122.2687 | 122.612 | -0.10529 | 122.5845 | 60.7681 | -0.32501 | 122.612 | -0.10529 | 60.7681 | 122.2687 | 122.5845 | -122.8546 | -122.9187
88.9062 | 122.8592 | -60.6903 | 61.8576 | 0.14145 | 0.0057934 | 0.0068722 | -0.0040033 | 0.065311 | -0.0013609 | 0.069848 | -60.8276 | 61.8027 | -60.9375 | -60.9421 | 61.5784 | 0.022888 | -0.10071 | 0.14191 | 61.8027 | -60.9695 | -0.24719 | -0.054932 | -0.13733 | -0.25177 | -0.27924 | -0.27923 | -0.054932 | 0.10986 | 60.5896 | 60.8322 | 122.2687 | 122.493 | -0.13733 | 122.493 | 60.7132 | -0.27923 | 122.493 | -0.13733 | 60.7132 | 122.2687 | 122.493 | -122.7951 | -122.8271
89.9688 | 122.7585 | -60.7544 | 61.8759 | 0.042267 | 0.0038708 | 0.0083676 | 0.0043281 | 0.066379 | -0.0022153 | 0.068139 | -60.8276 | 61.853 | -60.9879 | -60.9558 | 61.5097 | -0.022888 | 0.018311 | 0.054932 | 61.8347 | -61.0107 | -0.23346 | -0.022889 | -0.073242 | -0.20142 | -0.36621 | -0.25635 | -0.041199 | 0.16022 | 60.7727 | 60.8093 | 122.2641 | 122.6074 | -0.073242 | 122.5891 | 60.7315 | -0.25635 | 122.6074 | -0.073242 | 60.7315 | 122.2641 | 122.5891 | -122.8638 | -122.8867
90.9062 | 122.8912 | -60.7132 | 61.8164 | 0.17197 | 0.004939 | 0.0072996 | -0.0010125 | 0.065952 | -0.0013609 | 0.069635 | -60.7681 | 61.7844 | -60.9558 | -60.8734 | 61.6013 | 0.041199 | -0.1831 | 0.16937 | 61.8073 | -60.9741 | -0.24261 | -0.032043 | -0.054931 | -0.16022 | -0.21515 | -0.26092 | -0.009155 | 0.18768 | 60.5301 | 60.8826 | 122.3145 | 122.4976 | -0.054931 | 122.5204 | 60.7544 | -0.26092 | 122.4976 | -0.054931 | 60.7544 | 122.3145 | 122.5204 | -122.7722 | -122.7905
91.9531 | 122.8317 | -60.7178 | 61.8759 | -0.087433 | 0.0060072 | 0.0068722 | 0.0028327 | 0.065525 | -0.0015745 | 0.068994 | -60.7544 | 61.8851 | -60.9558 | -60.8917 | 61.5875 | 0.068665 | 0.050354 | 0.20599 | 61.8484 | -60.9879 | -0.23804 | 0.009155 | -0.036622 | -0.17395 | -0.28839 | -0.27008 | -0.027466 | 0.20142 | 60.7681 | 60.9238 | 122.3053 | 122.6028 | -0.036622 | 122.5662 | 60.7864 | -0.27008 | 122.6028 | -0.036622 | 60.7864 | 122.3053 | 122.5662 | -122.8317 | -122.8638
92.9062 | 122.8958 | -60.6903 | 61.8256 | 0.18723 | 0.0053662 | 0.0051632 | 0.0032599 | 0.068943 | -0.0028561 | 0.068353 | -60.7544 | 61.7935 | -60.965 | -60.6949 | 61.6791 | 0.045776 | -0.19226 | 0.19226 | 61.8027 | -60.9558 | -0.27466 | -0.032044 | -0.064087 | -0.004577 | -0.14648 | -0.2655 | -0.022889 | 0.21057 | 60.498 | 60.8826 | 122.3694 | 122.4838 | -0.064087 | 122.493 | 60.7361 | -0.2655 | 122.4838 | -0.064087 | 60.7361 | 122.3694 | 122.493 | -122.7905 | -122.7814
93.9531 | 122.8088 | -60.6995 | 61.9125 | -0.18662 | 0.0038708 | 0.0060178 | 0.0034735 | 0.065738 | -0.00050626 | 0.068139 | -60.8185 | 61.8942 | -60.9558 | -60.9192 | 61.5555 | 0.059509 | 0.13275 | 0.17853 | 61.8759 | -60.9924 | -0.25635 | -0.018311 | -0.11902 | -0.21973 | -0.35706 | -0.29297 | -0.036621 | 0.13733 | 60.8322 | 60.878 | 122.2549 | 122.5937 | -0.11902 | 122.5754 | 60.759 | -0.29297 | 122.5937 | -0.11902 | 60.759 | 122.2549 | 122.5754 | -122.8683 | -122.905
94.9062 | 122.9004 | -60.6949 | 61.8164 | 0.22537 | 0.0038708 | 0.006445 | 5.5496e-05 | 0.065097 | -0.0011471 | 0.070276 | -60.7727 | 61.7661 | -60.9604 | -60.8734 | 61.6058 | 0.045776 | -0.19226 | 0.17853 | 61.8027 | -60.965 | -0.2655 | -0.050354 | -0.07782 | -0.17853 | -0.21057 | -0.27008 | -0.013733 | 0.18768 | 60.5026 | 60.8734 | 122.3007 | 122.4609 | -0.07782 | 122.4976 | 60.7407 | -0.27008 | 122.4609 | -0.07782 | 60.7407 | 122.3007 | 122.4976 | -122.7768 | -122.7814
95.9688 | 122.8317 | -60.7132 | 61.8484 | 0.233 | 0.0036572 | 0.0090086 | 0.0043281 | 0.064456 | -0.0011471 | 0.069635 | -60.8139 | 61.8256 | -60.997 | -60.9238 | 61.5555 | 0.013733 | -0.14191 | 0.10986 | 61.7798 | -61.0062 | -0.28381 | -0.022888 | -0.10071 | -0.21057 | -0.29297 | -0.29297 | -0.068665 | 0.1831 | 60.5713 | 60.8231 | 122.2687 | 122.5388 | -0.10071 | 122.493 | 60.7269 | -0.29297 | 122.5388 | -0.10071 | 60.7269 | 122.2687 | 122.493 | -122.8455 | -122.8546
96.9062 | 122.9004 | -60.704 | 61.821 | 0.12619 | 0.0057934 | 0.0072996 | -0.0020807 | 0.064029 | 0.00056194 | 0.068353 | -60.7636 | 61.7752 | -60.9741 | -60.878 | 61.6104 | 0.050354 | -0.1831 | 0.17395 | 61.8073 | -61.0062 | -0.27008 | -0.045776 | -0.059509 | -0.17395 | -0.21057 | -0.30212 | -0.013733 | 0.21057 | 60.5209 | 60.878 | 122.3145 | 122.4792 | -0.059509 | 122.5113 | 60.7544 | -0.30212 | 122.4792 | -0.059509 | 60.7544 | 122.3145 | 122.5113 | -122.7951 | -122.8271
97.9531 | 122.7905 | -60.7361 | 61.8393 | 0.20248 | 0.0045118 | 0.010717 | 0.0026191 | 0.066379 | -0.00093346 | 0.067926 | -60.8414 | 61.8256 | -61.0107 | -60.9329 | 61.5143 | -0.045776 | -0.068665 | 0.045776 | 61.8118 | -61.0428 | -0.27466 | -0.013732 | -0.10529 | -0.19684 | -0.32501 | -0.3067 | -0.027465 | 0.16937 | 60.6674 | 60.7819 | 122.2504 | 122.5616 | -0.10529 | 122.5479 | 60.6903 | -0.3067 | 122.5616 | -0.10529 | 60.6903 | 122.2504 | 122.5479 | -122.85 | -122.8821
98.9062 | 122.7173 | -60.6812 | 61.9354 | -0.25528 | 0.0062208 | 0.0043088 | -0.0025079 | 0.064243 | -0.0030697 | 0.066858 | -60.8414 | 61.8576 | -60.9787 | -60.9283 | 61.5509 | 0.054932 | 0.16022 | 0.19226 | 61.8668 | -60.9695 | -0.29755 | -0.07782 | -0.16022 | -0.24719 | -0.38452 | -0.28839 | -0.068665 | 0.13733 | 60.8414 | 60.8734 | 122.2321 | 122.5388 | -0.16022 | 122.5479 | 60.7361 | -0.28839 | 122.5388 | -0.16022 | 60.7361 | 122.2321 | 122.5479 | -122.9141 | -122.905
99.9531 | 122.7539 | -60.7498 | 61.8851 | 0.1796 | 0.0042982 | 0.0049496 | 0.0019781 | 0.064029 | -0.0011471 | 0.068353 | -60.8826 | 61.8256 | -61.0153 | -61.0382 | 61.5051 | 0.018311 | 0 | 0.027466 | 61.8576 | -60.9924 | -0.2655 | -0.059509 | -0.13275 | -0.28839 | -0.37994 | -0.24262 | -0.027466 | 0.13275 | 60.7498 | 60.7773 | 122.2549 | 122.5754 | -0.13275 | 122.6074 | 60.7681 | -0.24262 | 122.5754 | -0.13275 | 60.7681 | 122.2549 | 122.6074 | -122.9004 | -122.8775
100.9062 | 122.8683 | -60.6995 | 61.8347 | 0.1796 | 0.0062208 | 0.0094358 | 0.0032599 | 0.066165 | -0.0013609 | 0.069421 | -60.8047 | 61.8393 | -60.9695 | -60.9055 | 61.5646 | 0.032043 | -0.14648 | 0.11444 | 61.8118 | -60.997 | -0.27008 | 0.004577 | -0.10529 | -0.20599 | -0.27008 | -0.29755 | -0.022888 | 0.16479 | 60.553 | 60.8139 | 122.2641 | 122.5388 | -0.10529 | 122.5113 | 60.7315 | -0.29755 | 122.5388 | -0.10529 | 60.7315 | 122.2641 | 122.5113 | -122.8043 | -122.8317
101.9531 | 122.7768 | -60.7361 | 61.8622 | 0.17197 | 0.0055798 | 0.0096494 | 0.0039007 | 0.065952 | -7.9062e-05 | 0.068994 | -60.8551 | 61.8256 | -61.0062 | -60.9558 | 61.4914 | -0.045776 | -0.032043 | 0.045776 | 61.853 | -60.9879 | -0.27008 | -0.036621 | -0.11902 | -0.21973 | -0.37079 | -0.25177 | -0.009156 | 0.15106 | 60.704 | 60.7819 | 122.2275 | 122.5616 | -0.11902 | 122.5891 | 60.6903 | -0.25177 | 122.5616 | -0.11902 | 60.6903 | 122.2275 | 122.5891 | -122.8683 | -122.85
102.9062 | 122.8455 | -60.672 | 61.8301 | 0.0041197 | 0.0010938 | 0.0077268 | -0.0044305 | 0.066165 | -0.0013609 | 0.067071 | -60.64 | 61.8439 | -60.9604 | -60.8917 | 61.5875 | 0.022888 | -0.073242 | 0.13733 | 61.7844 | -60.997 | -0.28839 | 0.013733 | 0.032043 | -0.21973 | -0.24262 | -0.32501 | -0.045776 | 0.32043 | 60.5988 | 60.8093 | 122.2595 | 122.5159 | 0.032043 | 122.4564 | 60.6949 | -0.32501 | 122.5159 | 0.032043 | 60.6949 | 122.2595 | 122.4564 | -122.7905 | -122.8271
103.9688 | 122.8683 | -60.6857 | 61.8347 | -0.11032 | 0.00323 | 0.010504 | -0.0037897 | 0.063602 | -0.00050626 | 0.066644 | -60.7681 | 61.8118 | -60.9512 | -60.8185 | 61.6653 | 0.15106 | -0.091553 | 0.27466 | 61.8301 | -60.9695 | -0.2655 | -0.022888 | -0.082397 | -0.13275 | -0.16937 | -0.28381 | -0.004578 | 0.18311 | 60.5942 | 60.9604 | 122.3511 | 122.4976 | -0.082397 | 122.5159 | 60.8368 | -0.28381 | 122.4976 | -0.082397 | 60.8368 | 122.3511 | 122.5159 | -122.7859 | -122.8043
104.9062 | 122.8821 | -60.6949 | 61.8759 | 0.034637 | 0.0025892 | 0.0028134 | -0.0010125 | 0.062961 | 0.00056194 | 0.068994 | -60.8093 | 61.7844 | -60.9695 | -60.8917 | 61.5967 | 0.054932 | -0.073242 | 0.18768 | 61.7981 | -60.965 | -0.27466 | -0.091553 | -0.11444 | -0.19684 | -0.27924 | -0.27008 | -0.07782 | 0.16022 | 60.6216 | 60.8826 | 122.2916 | 122.4792 | -0.11444 | 122.493 | 60.7498 | -0.27008 | 122.4792 | -0.11444 | 60.7498 | 122.2916 | 122.493 | -122.8455 | -122.8409
105.9531 | 122.7493 | -60.759 | 61.9034 | 0.042267 | 0.0042982 | 0.011999 | 0.0066779 | 0.06232 | -0.0024289 | 0.067285 | -60.8231 | 61.8622 | -61.0153 | -60.9558 | 61.4685 | -0.050354 | 0.032043 | 0.050354 | 61.8164 | -61.0245 | -0.25635 | -0.041198 | -0.064087 | -0.19684 | -0.43488 | -0.2655 | -0.086975 | 0.19226 | 60.791 | 60.8093 | 122.2275 | 122.6212 | -0.064087 | 122.5754 | 60.7086 | -0.2655 | 122.6212 | -0.064087 | 60.7086 | 122.2275 | 122.5754 | -122.9187 | -122.9279
106.9062 | 122.8867 | -60.7132 | 61.8347 | 0.41611 | 0.0019482 | 0.0090086 | 0.0024053 | 0.064884 | -0.0034971 | 0.065362 | -60.7727 | 61.7844 | -60.965 | -60.8734 | 61.5921 | 0.059509 | -0.18768 | 0.14648 | 61.821 | -60.9833 | -0.25177 | -0.050354 | -0.059509 | -0.16022 | -0.24262 | -0.27008 | -0.013733 | 0.19226 | 60.5255 | 60.8597 | 122.3053 | 122.4976 | -0.059509 | 122.5342 | 60.7727 | -0.27008 | 122.4976 | -0.059509 | 60.7727 | 122.3053 | 122.5342 | -122.7997 | -122.818
107.9688 | 122.7539 | -60.7452 | 61.8622 | 0.0041197 | 0.0060072 | 0.010717 | 0.0060369 | 0.064884 | -0.0028561 | 0.066217 | -60.8047 | 61.8347 | -60.997 | -60.9375 | 61.5143 | -0.004578 | 0.027466 | 0.11902 | 61.8484 | -60.9924 | -0.25177 | -0.027466 | -0.05951 | -0.19226 | -0.3479 | -0.24719 | -0.013733 | 0.19226 | 60.7727 | 60.8643 | 122.2595 | 122.58 | -0.05951 | 122.5937 | 60.7407 | -0.24719 | 122.58 | -0.05951 | 60.7407 | 122.2595 | 122.5937 | -122.8592 | -122.8546
108.9062 | 122.937 | -60.6949 | 61.8484 | -0.14084 | 0.0047254 | 0.0049496 | -0.0033625 | 0.06467 | -7.9062e-05 | 0.068353 | -60.7407 | 61.821 | -60.9558 | -60.8368 | 61.9812 | 0.44861 | -0.32501 | 0.032043 | 61.8439 | -60.9558 | -0.26093 | -0.027466 | -0.045777 | -0.14191 | 0.13275 | -0.26093 | -0.004578 | 0.21515 | 60.3699 | 60.7269 | 122.6761 | 122.5159 | -0.045777 | 122.5388 | 61.1435 | -0.26093 | 122.5159 | -0.045777 | 61.1435 | 122.6761 | 122.5388 | -122.8043 | -122.8043
109.9688 | 122.8912 | -60.7178 | 61.853 | 0.233 | 0.0045118 | 0.010504 | -0.0012261 | 0.067234 | 0.0012027 | 0.068353 | -60.7681 | 61.7889 | -60.9604 | -60.8597 | 61.5875 | 0.045776 | -0.17853 | 0.16937 | 61.7706 | -60.9833 | -0.24262 | -0.064087 | -0.050354 | -0.14191 | -0.2655 | -0.2655 | -0.082397 | 0.19226 | 60.5392 | 60.8871 | 122.3053 | 122.5067 | -0.050354 | 122.4884 | 60.7635 | -0.2655 | 122.5067 | -0.050354 | 60.7635 | 122.3053 | 122.4884 | -122.8134 | -122.8363
110.9062 | 122.8455 | -60.7132 | 61.8164 | 0.18723 | 0.0036572 | 0.0070858 | 0.0002691 | 0.065311 | -7.9062e-05 | 0.068994 | -60.7773 | 61.7935 | -60.9512 | -60.878 | 61.5738 | 0.036621 | -0.17853 | 0.14648 | 61.7844 | -60.9787 | -0.23804 | -0.022888 | -0.064087 | -0.16479 | -0.24261 | -0.2655 | -0.032043 | 0.17395 | 60.5347 | 60.8597 | 122.287 | 122.5067 | -0.064087 | 122.4976 | 60.7498 | -0.2655 | 122.5067 | -0.064087 | 60.7498 | 122.287 | 122.4976 | -122.7676 | -122.7951
111.9688 | 122.7768 | -60.7498 | 61.8805 | 0.019379 | 0.0057934 | 0.0087948 | 0.0056097 | 0.064456 | -0.00093346 | 0.068994 | -60.7956 | 61.8393 | -60.9833 | -60.9009 | 61.5463 | 0.018311 | 0.004578 | 0.11444 | 61.8164 | -61.0336 | -0.23346 | -0.041199 | -0.045776 | -0.15106 | -0.33417 | -0.28381 | -0.064087 | 0.18768 | 60.7544 | 60.8643 | 122.2961 | 122.5891 | -0.045776 | 122.5662 | 60.7681 | -0.28381 | 122.5891 | -0.045776 | 60.7681 | 122.2961 | 122.5662 | -122.8638 | -122.9141
112.9062 | 122.8546 | -60.6949 | 61.821 | 0.14145 | 0.001521 | 0.0077268 | 0.0002691 | 0.064243 | -0.00029266 | 0.06878 | -60.7819 | 61.7615 | -60.9741 | -60.8871 | 61.5875 | 0.045776 | -0.17853 | 0.15564 | 61.7981 | -60.9787 | -0.27924 | -0.059509 | -0.086975 | -0.19226 | -0.23346 | -0.28381 | -0.022888 | 0.19226 | 60.5164 | 60.8505 | 122.2824 | 122.4564 | -0.086975 | 122.493 | 60.7407 | -0.28381 | 122.4564 | -0.086975 | 60.7407 | 122.2824 | 122.493 | -122.7951 | -122.7997
113.9688 | 122.8821 | -60.6857 | 61.8622 | 0.027008 | 0.0034436 | 0.0023862 | -0.0012261 | 0.063816 | -0.0013609 | 0.067498 | -60.7224 | 61.7981 | -60.9512 | -60.8139 | 61.6425 | 0.14648 | -0.036621 | 0.28839 | 61.821 | -60.9467 | -0.2655 | -0.064087 | -0.036621 | -0.12817 | -0.21973 | -0.26093 | -0.041199 | 0.22888 | 60.6491 | 60.9741 | 122.3282 | 122.4838 | -0.036621 | 122.5067 | 60.8322 | -0.26093 | 122.4838 | -0.036621 | 60.8322 | 122.3282 | 122.5067 | -122.8134 | -122.8088
114.9062 | 122.9187 | -60.6537 | 61.8576 | -0.087433 | 0.0030164 | 0.0060178 | -0.0020807 | 0.063816 | -0.0041379 | 0.067071 | -60.7864 | 61.7752 | -60.9375 | -60.8185 | 61.6837 | 0.16022 | -0.09613 | 0.28839 | 61.8073 | -60.965 | -0.28381 | -0.082397 | -0.13275 | -0.16479 | -0.17395 | -0.31128 | -0.050354 | 0.15106 | 60.5576 | 60.9421 | 122.3373 | 122.4289 | -0.13275 | 122.4609 | 60.8139 | -0.31128 | 122.4289 | -0.13275 | 60.8139 | 122.3373 | 122.4609 | -122.7951 | -122.8226
115.9531 | 122.8638 | -60.704 | 61.8484 | 0.18723 | 0.0034436 | 0.0032406 | 0.0013373 | 0.062961 | -0.0013609 | 0.067071 | -60.7727 | 61.7706 | -60.9879 | -60.8597 | 61.5875 | 0.050354 | -0.20142 | 0.16479 | 61.7981 | -60.9604 | -0.28381 | -0.07782 | -0.068664 | -0.15564 | -0.26093 | -0.25635 | -0.050354 | 0.21515 | 60.5026 | 60.8688 | 122.2916 | 122.4747 | -0.068664 | 122.5021 | 60.7544 | -0.25635 | 122.4747 | -0.068664 | 60.7544 | 122.2916 | 122.5021 | -122.8363 | -122.8088
116.9062 | 122.8455 | -60.7086 | 61.8393 | 0.15671 | 0.0040846 | 0.008154 | 0.0006965 | 0.062747 | 0.00034814 | 0.067285 | -60.8093 | 61.7432 | -60.9741 | -60.8963 | 61.5738 | 0.022888 | -0.12817 | 0.13275 | 61.7798 | -60.9695 | -0.2655 | -0.09613 | -0.10071 | -0.18768 | -0.2655 | -0.26093 | -0.059509 | 0.16479 | 60.5804 | 60.8414 | 122.2824 | 122.4518 | -0.10071 | 122.4884 | 60.7315 | -0.26093 | 122.4518 | -0.10071 | 60.7315 | 122.2824 | 122.4884 | -122.8134 | -122.8088
117.9531 | 122.8592 | -60.6949 | 61.8851 | 0.11093 | 0.0028028 | 0.003027 | -0.0001581 | 0.063816 | 0.0016299 | 0.070489 | -60.8047 | 61.7477 | -60.965 | -60.8917 | 61.5692 | 0.018311 | -0.13275 | 0.14648 | 61.7661 | -60.965 | -0.27008 | -0.13733 | -0.10986 | -0.19684 | -0.31586 | -0.27008 | -0.11902 | 0.16022 | 60.5621 | 60.8414 | 122.2641 | 122.4426 | -0.10986 | 122.4609 | 60.7132 | -0.27008 | 122.4426 | -0.10986 | 60.7132 | 122.2641 | 122.4609 | -122.85 | -122.85
118.9062 | 122.8592 | -60.7086 | 61.8622 | 0.15671 | 0.004939 | 0.0055906 | 0.0009101 | 0.063602 | 0.00077554 | 0.070062 | -60.7864 | 61.7615 | -60.9558 | -60.8871 | 61.5738 | 0.018311 | -0.15106 | 0.14648 | 61.7798 | -60.9833 | -0.24719 | -0.10071 | -0.07782 | -0.17853 | -0.28839 | -0.27466 | -0.082398 | 0.16937 | 60.5576 | 60.8551 | 122.2824 | 122.4701 | -0.07782 | 122.4884 | 60.7269 | -0.27466 | 122.4701 | -0.07782 | 60.7269 | 122.2824 | 122.4884 | -122.818 | -122.8455
119.9688 | 122.8226 | -60.7132 | 61.8347 | 0.21011 | 0.0047254 | 0.006445 | 0.0045417 | 0.06467 | -0.0024289 | 0.068353 | -60.8276 | 61.7935 | -60.997 | -60.91 | 61.5189 | -0.004578 | -0.13275 | 0.10529 | 61.821 | -60.965 | -0.28381 | -0.041199 | -0.11444 | -0.19684 | -0.31586 | -0.25177 | -0.013733 | 0.16937 | 60.5804 | 60.8185 | 122.2321 | 122.5067 | -0.11444 | 122.5342 | 60.7086 | -0.25177 | 122.5067 | -0.11444 | 60.7086 | 122.2321 | 122.5342 | -122.8317 | -122.7997
120.9062 | 122.8775 | -60.672 | 61.8256 | 0.14908 | 0.0045118 | 0.0070858 | 0.0026191 | 0.064456 | -0.00071986 | 0.06878 | -60.7544 | 61.7752 | -60.9604 | -60.8505 | 61.615 | 0.059509 | -0.21057 | 0.15564 | 61.8073 | -60.9558 | -0.28839 | -0.050354 | -0.082398 | -0.17853 | -0.21057 | -0.28381 | -0.018311 | 0.20599 | 60.4614 | 60.8276 | 122.287 | 122.4472 | -0.082398 | 122.4792 | 60.7315 | -0.28381 | 122.4472 | -0.082398 | 60.7315 | 122.287 | 122.4792 | -122.7859 | -122.7814
121.9531 | 122.937 | -60.7132 | 61.8805 | 0.11093 | 0.0045118 | 0.003668 | -0.0029351 | 0.062107 | -0.00093346 | 0.06878 | -60.8093 | 61.7615 | -60.9695 | -60.91 | 61.5692 | 0.036621 | -0.091553 | 0.14191 | 61.7981 | -60.9512 | -0.25635 | -0.11902 | -0.09613 | -0.19684 | -0.31128 | -0.23804 | -0.082397 | 0.16022 | 60.6216 | 60.8551 | 122.2824 | 122.4747 | -0.09613 | 122.5113 | 60.7498 | -0.23804 | 122.4747 | -0.09613 | 60.7498 | 122.2824 | 122.5113 | -122.85 | -122.8317
122.9062 | 122.8546 | -60.6995 | 61.8759 | 0.011749 | 0.00045296 | 0.0092222 | 0.0004827 | 0.060825 | 0.0020571 | 0.068353 | -60.8322 | 61.7844 | -60.9741 | -60.8871 | 61.5967 | 0.064087 | -0.082397 | 0.17853 | 61.821 | -60.9558 | -0.27466 | -0.091553 | -0.13275 | -0.18768 | -0.27924 | -0.25635 | -0.054932 | 0.14191 | 60.6171 | 60.878 | 122.2961 | 122.4838 | -0.13275 | 122.5204 | 60.7636 | -0.25635 | 122.4838 | -0.13275 | 60.7636 | 122.2961 | 122.5204 | -122.85 | -122.8317
123.9688 | 122.818 | -60.704 | 61.8576 | 0.233 | 0.0045118 | 0.0058042 | 0.0071051 | 0.063388 | 0.00056194 | 0.069207 | -60.8231 | 61.7981 | -60.997 | -60.9055 | 61.528 | -0.013733 | -0.10529 | 0.086975 | 61.7889 | -60.9879 | -0.29297 | -0.059509 | -0.11902 | -0.20142 | -0.32959 | -0.28381 | -0.068665 | 0.17395 | 60.5988 | 60.791 | 122.2321 | 122.5021 | -0.11902 | 122.493 | 60.6903 | -0.28381 | 122.5021 | -0.11902 | 60.6903 | 122.2321 | 122.493 | -122.8546 | -122.8455
124.9062 | 122.7859 | -60.6949 | 61.908 | -0.22476 | 0.0013074 | 0.0062314 | -0.0010125 | 0.061252 | 0.00056194 | 0.068567 | -60.791 | 61.8439 | -60.9695 | -60.8871 | 61.5692 | 0.064087 | 0.1236 | 0.20142 | 61.8301 | -60.9924 | -0.27466 | -0.064087 | -0.096131 | -0.19226 | -0.33874 | -0.29755 | -0.07782 | 0.17853 | 60.8185 | 60.8963 | 122.2641 | 122.5388 | -0.096131 | 122.525 | 60.759 | -0.29755 | 122.5388 | -0.096131 | 60.759 | 122.2641 | 122.525 | -122.8775 | -122.9004
125.9531 | 122.8912 | -60.7224 | 61.8713 | 0.1796 | 0.002162 | 0.0040952 | 0.0002691 | 0.064243 | -0.00071986 | 0.06878 | -60.7819 | 61.7569 | -60.9558 | -60.8688 | 61.6013 | 0.050354 | -0.19684 | 0.18768 | 61.7889 | -60.9512 | -0.23346 | -0.11444 | -0.059509 | -0.14648 | -0.27008 | -0.22888 | -0.082398 | 0.17395 | 60.5255 | 60.91 | 122.3236 | 122.4792 | -0.059509 | 122.5113 | 60.7727 | -0.22888 | 122.4792 | -0.059509 | 60.7727 | 122.3236 | 122.5113 | -122.8271 | -122.8226
126.9062 | 122.8455 | -60.7178 | 61.821 | 0.080414 | 0.0040846 | -0.0012454 | -0.0012261 | 0.066165 | 0.00034814 | 0.066217 | -60.8368 | 61.7661 | -60.9558 | -60.8963 | 61.5829 | 0.022888 | -0.059509 | 0.15564 | 61.8027 | -60.9741 | -0.23804 | -0.054932 | -0.11902 | -0.17853 | -0.23804 | -0.25635 | -0.018311 | 0.11902 | 60.6583 | 60.8734 | 122.3007 | 122.4838 | -0.11902 | 122.5204 | 60.7407 | -0.25635 | 122.4838 | -0.11902 | 60.7407 | 122.3007 | 122.5204 | -122.7768 | -122.7951
127.9688 | 122.7905 | -60.7224 | 61.8439 | 0.20248 | 0.0057934 | 0.0094358 | 0.0045417 | 0.063816 | -0.00050626 | 0.06878 | -60.8322 | 61.8073 | -61.0062 | -60.9421 | 61.528 | -0.050354 | -0.064087 | 0.041199 | 61.7981 | -61.0016 | -0.28381 | -0.036621 | -0.10986 | -0.21973 | -0.31586 | -0.27924 | -0.045776 | 0.17395 | 60.6583 | 60.7636 | 122.2504 | 122.5296 | -0.10986 | 122.5204 | 60.672 | -0.27924 | 122.5296 | -0.10986 | 60.672 | 122.2504 | 122.5204 | -122.85 | -122.8455
128.9062 | 122.8638 | -60.6995 | 61.8576 | 0.080414 | 0.00066656 | 0.0021726 | -0.0031489 | 0.063175 | -0.0024289 | 0.066858 | -60.8185 | 61.7615 | -60.9467 | -60.9192 | 61.5463 | 0.013733 | -0.091553 | 0.14191 | 61.7935 | -60.9558 | -0.24719 | -0.09613 | -0.11902 | -0.21973 | -0.31128 | -0.25635 | -0.064087 | 0.12817 | 60.6079 | 60.8414 | 122.2458 | 122.4609 | -0.11902 | 122.493 | 60.7132 | -0.25635 | 122.4609 | -0.11902 | 60.7132 | 122.2458 | 122.493 | -122.8043 | -122.8134
129.9688 | 122.8317 | -60.6949 | 61.8347 | 0.019379 | -0.00040164 | 0.0032406 | -0.0031489 | 0.061252 | -0.0017881 | 0.067498 | -60.8276 | 61.7569 | -60.9512 | -60.9009 | 61.5692 | 0.027466 | -0.082397 | 0.2243 | 61.8439 | -60.9375 | -0.25635 | -0.07782 | -0.13275 | -0.20599 | -0.2655 | -0.24262 | 0.009155 | 0.1236 | 60.6125 | 60.9192 | 122.2641 | 122.4518 | -0.13275 | 122.5388 | 60.7224 | -0.24262 | 122.4518 | -0.13275 | 60.7224 | 122.2641 | 122.5388 | -122.7859 | -122.7722
130.9062 | 122.8729 | -60.672 | 61.8805 | -0.079803 | 0.0023756 | 0.0034544 | -0.0031489 | 0.062107 | -0.00093346 | 0.068567 | -60.7864 | 61.7661 | -60.9192 | -60.8414 | 61.6379 | 0.10986 | -0.07782 | 0.23346 | 61.7935 | -60.9421 | -0.24719 | -0.11444 | -0.11444 | -0.16937 | -0.24262 | -0.27008 | -0.086975 | 0.13275 | 60.5942 | 60.9055 | 122.3099 | 122.438 | -0.11444 | 122.4655 | 60.7819 | -0.27008 | 122.438 | -0.11444 | 60.7819 | 122.3099 | 122.4655 | -122.7997 | -122.8226
131.9531 | 122.8546 | -60.6949 | 61.8851 | 0.12619 | 0.0023756 | 0.0049496 | 0.0004827 | 0.061038 | -0.00071986 | 0.068139 | -60.8139 | 61.7477 | -60.9695 | -60.8826 | 61.5921 | 0.032043 | -0.10071 | 0.15106 | 61.7706 | -60.9512 | -0.27466 | -0.13733 | -0.11902 | -0.18768 | -0.29297 | -0.25635 | -0.11444 | 0.15564 | 60.5942 | 60.8459 | 122.287 | 122.4426 | -0.11902 | 122.4655 | 60.7269 | -0.25635 | 122.4426 | -0.11902 | 60.7269 | 122.287 | 122.4655 | -122.8546 | -122.8363
132.9062 | 122.8821 | -60.6674 | 61.8713 | -0.041657 | 0.00045296 | 0.0051632 | -0.0014399 | 0.061893 | 0.00056194 | 0.06878 | -60.7819 | 61.7935 | -60.9604 | -60.8414 | 61.6333 | 0.12817 | -0.091553 | 0.25635 | 61.7935 | -60.9467 | -0.29297 | -0.07782 | -0.11444 | -0.17395 | -0.23804 | -0.27924 | -0.07782 | 0.17853 | 60.5759 | 60.9238 | 122.3007 | 122.4609 | -0.11444 | 122.4609 | 60.7956 | -0.27924 | 122.4609 | -0.11444 | 60.7956 | 122.3007 | 122.4609 | -122.8317 | -122.818
133.9531 | 122.8958 | -60.6674 | 61.8759 | -0.072174 | 0.0019482 | 0.0058042 | -0.0016535 | 0.05997 | -0.0026425 | 0.067071 | -60.791 | 61.7798 | -60.9467 | -60.8276 | 61.6333 | 0.11902 | -0.086975 | 0.2655 | 61.7935 | -60.9192 | -0.27924 | -0.096131 | -0.1236 | -0.16022 | -0.24261 | -0.25177 | -0.082398 | 0.15564 | 60.5804 | 60.9329 | 122.3007 | 122.4472 | -0.1236 | 122.4609 | 60.7864 | -0.25177 | 122.4472 | -0.1236 | 60.7864 | 122.3007 | 122.4609 | -122.8226 | -122.7951
134.9062 | 122.8455 | -60.6903 | 61.8576 | -0.011139 | 0.0019482 | 0.0077268 | -0.0031489 | 0.061893 | -0.00050626 | 0.067285 | -60.8047 | 61.7661 | -61.0016 | -60.8688 | 61.5967 | 0.068665 | -0.068665 | 0.18768 | 61.8118 | -60.9329 | -0.31128 | -0.091553 | -0.11444 | -0.17853 | -0.26093 | -0.24261 | -0.045776 | 0.19684 | 60.6216 | 60.878 | 122.287 | 122.4564 | -0.11444 | 122.5021 | 60.759 | -0.24261 | 122.4564 | -0.11444 | 60.759 | 122.287 | 122.5021 | -122.8592 | -122.7905
135.9531 | 122.8363 | -60.7086 | 61.853 | 0.18723 | 0.0017346 | 0.0055906 | -0.0003717 | 0.062961 | 0.00013454 | 0.06878 | -60.8139 | 61.7111 | -60.9833 | -60.8871 | 61.5692 | 0.022888 | -0.12817 | 0.12817 | 61.7798 | -60.9604 | -0.27466 | -0.14191 | -0.10529 | -0.17853 | -0.28381 | -0.25177 | -0.073242 | 0.16937 | 60.5804 | 60.8368 | 122.2778 | 122.4197 | -0.10529 | 122.4884 | 60.7315 | -0.25177 | 122.4197 | -0.10529 | 60.7315 | 122.2778 | 122.4884 | -122.8363 | -122.8134
136.9062 | 122.8409 | -60.6857 | 61.8622 | -0.16373 | 0.0028028 | 0.0092222 | 0.0006965 | 0.064243 | 0.00034814 | 0.06643 | -60.7544 | 61.7706 | -60.9467 | -60.8139 | 61.615 | 0.13275 | -0.004578 | 0.28839 | 61.7935 | -60.9421 | -0.26093 | -0.091553 | -0.068665 | -0.12817 | -0.24719 | -0.25635 | -0.068665 | 0.19226 | 60.6812 | 60.9741 | 122.3007 | 122.4564 | -0.068665 | 122.4792 | 60.8185 | -0.25635 | 122.4564 | -0.068665 | 60.8185 | 122.3007 | 122.4792 | -122.8088 | -122.8043
137.9688 | 122.8409 | -60.7086 | 61.8576 | 0.095673 | 0.002162 | 0.006445 | -0.0016535 | 0.06232 | -0.0017881 | 0.067712 | -60.8185 | 61.7569 | -60.9512 | -60.8963 | 61.5646 | 0.013733 | -0.11444 | 0.14191 | 61.7706 | -60.9283 | -0.24262 | -0.10071 | -0.10986 | -0.18768 | -0.29297 | -0.21973 | -0.086975 | 0.13275 | 60.5942 | 60.8505 | 122.2733 | 122.4655 | -0.10986 | 122.4792 | 60.7224 | -0.21973 | 122.4655 | -0.10986 | 60.7224 | 122.2733 | 122.4792 | -122.8088 | -122.7859
138.9062 | 122.8912 | -60.6857 | 61.8713 | -0.19424 | 0.004939 | 0.0092222 | 0.0017645 | 0.061893 | -0.00093346 | 0.066003 | -61.0016 | 61.7569 | -60.9787 | -60.8231 | 61.6333 | 0.14191 | -0.032043 | 0.30212 | 61.7615 | -60.9329 | -0.29297 | -0.11444 | -0.31586 | -0.13733 | -0.23804 | -0.24719 | -0.10986 | -0.022888 | 60.6537 | 60.9879 | 122.319 | 122.4426 | -0.31586 | 122.4472 | 60.8276 | -0.24719 | 122.4426 | -0.31586 | 60.8276 | 122.319 | 122.4472 | -122.85 | -122.8043
139.9531 | 122.9187 | -60.672 | 61.8347 | -0.064545 | 0.001521 | 0.0021726 | -0.0022943 | 0.061252 | -0.0024289 | 0.069207 | -60.7727 | 61.7844 | -60.9512 | -60.8231 | 61.6287 | 0.12817 | -0.086975 | 0.27466 | 61.7752 | -60.9192 | -0.27924 | -0.050354 | -0.10071 | -0.15106 | -0.20599 | -0.24719 | -0.059509 | 0.17853 | 60.585 | 60.9467 | 122.3007 | 122.4564 | -0.10071 | 122.4472 | 60.8002 | -0.24719 | 122.4564 | -0.10071 | 60.8002 | 122.3007 | 122.4472 | -122.7859 | -122.7539
140.9062 | 122.8867 | -60.6537 | 61.8759 | 2.6591 | 0.0017346 | -0.0012454 | -0.0012261 | 0.062961 | -0.0017881 | 0.067712 | -60.8093 | 61.7432 | -60.965 | -60.8047 | 61.6608 | 0.1831 | -0.059509 | 0.27466 | 61.8027 | -60.9238 | -0.31128 | -0.13275 | -0.15564 | -0.15106 | -0.21515 | -0.27008 | -0.073243 | 0.15564 | 60.5942 | 60.9283 | 122.3145 | 122.3969 | -0.15564 | 122.4564 | 60.8368 | -0.27008 | 122.3969 | -0.15564 | 60.8368 | 122.3145 | 122.4564 | -122.8409 | -122.7997
141.9688 | 122.8683 | -60.704 | 61.8713 | -0.011139 | 0.00323 | 0.0034544 | -0.0033625 | 0.060611 | 0.00034814 | 0.067285 | -60.791 | 61.8118 | -60.9558 | -60.8505 | 61.6196 | 0.10071 | -0.082397 | 0.2243 | 61.7889 | -60.9421 | -0.25177 | -0.059509 | -0.086975 | -0.14648 | -0.25177 | -0.23804 | -0.082398 | 0.16479 | 60.6216 | 60.9283 | 122.3236 | 122.5159 | -0.086975 | 122.493 | 60.8047 | -0.23804 | 122.5159 | -0.086975 | 60.8047 | 122.3236 | 122.493 | -122.8271 | -122.8134
142.9062 | 122.9141 | -60.6903 | 61.8805 | -0.97244 | 0.0017346 | 0.0092222 | -0.0012261 | 0.061038 | -0.00093346 | 0.067712 | -60.7636 | 61.7661 | -60.9467 | -60.7819 | 61.6653 | 0.14648 | -0.054932 | 0.3067 | 61.7935 | -60.9238 | -0.25635 | -0.11444 | -0.073242 | -0.091552 | -0.21515 | -0.23346 | -0.086975 | 0.1831 | 60.6354 | 60.997 | 122.3557 | 122.4564 | -0.073242 | 122.4838 | 60.8368 | -0.23346 | 122.4564 | -0.073242 | 60.8368 | 122.3557 | 122.4838 | -122.8271 | -122.8043
143.9688 | 122.8317 | -60.7269 | 61.8713 | 0.19485 | 0.002162 | 0.003027 | -0.0020807 | 0.060825 | -0.00050626 | 0.068353 | -60.8231 | 61.7935 | -60.965 | -60.8688 | 61.5784 | 0.032043 | -0.068665 | 0.16479 | 61.7935 | -60.9604 | -0.23804 | -0.07782 | -0.09613 | -0.14191 | -0.29297 | -0.23346 | -0.07782 | 0.14191 | 60.6583 | 60.8917 | 122.3053 | 122.5204 | -0.09613 | 122.5204 | 60.759 | -0.23346 | 122.5204 | -0.09613 | 60.759 | 122.3053 | 122.5204 | -122.8363 | -122.8317
144.9062 | 122.7859 | -60.7086 | 61.908 | -0.25528 | 0.0040846 | 0.0040952 | 0.0002691 | 0.063388 | -0.0013609 | 0.067285 | -60.8185 | 61.8393 | -60.9787 | -60.8963 | 61.5555 | 0.045776 | 0.10529 | 0.16937 | 61.8301 | -60.9695 | -0.27008 | -0.068665 | -0.10986 | -0.18768 | -0.35248 | -0.26093 | -0.07782 | 0.16022 | 60.8139 | 60.878 | 122.2641 | 122.5479 | -0.10986 | 122.5388 | 60.7544 | -0.26093 | 122.5479 | -0.10986 | 60.7544 | 122.2641 | 122.5388 | -122.8867 | -122.8775
145.9531 | 122.9187 | -60.6812 | 61.8484 | -0.049286 | 0.0040846 | 0.0051632 | -0.0010125 | 0.06232 | -0.0015745 | 0.069207 | -60.7727 | 61.7798 | -60.9558 | -60.8093 | 61.6608 | 0.14191 | -0.09613 | 0.27924 | 61.7752 | -60.9283 | -0.27466 | -0.068665 | -0.091553 | -0.12817 | -0.18768 | -0.24719 | -0.073242 | 0.18311 | 60.585 | 60.9604 | 122.3419 | 122.4609 | -0.091553 | 122.4564 | 60.8231 | -0.24719 | 122.4609 | -0.091553 | 60.8231 | 122.3419 | 122.4564 | -122.8043 | -122.7768
146.9062 | 122.8363 | -60.6812 | 61.8896 | -0.19424 | 0.002162 | 0.003668 | 0.0015509 | 0.06232 | -0.00093346 | 0.067071 | -60.759 | 61.8118 | -60.9604 | -60.8368 | 61.6241 | 0.11902 | 0.041199 | 0.25177 | 61.8301 | -60.9467 | -0.27924 | -0.077819 | -0.07782 | -0.15564 | -0.2655 | -0.2655 | -0.059509 | 0.20142 | 60.7224 | 60.9329 | 122.3053 | 122.493 | -0.07782 | 122.5113 | 60.8002 | -0.2655 | 122.493 | -0.07782 | 60.8002 | 122.3053 | 122.5113 | -122.85 | -122.8363
147.9688 | 122.9691 | -60.6903 | 61.8759 | 0.13382 | 0.001521 | 0.0060178 | 0.0011237 | 0.062961 | -0.00071986 | 0.068139 | -60.8231 | 61.7752 | -60.9512 | -60.8917 | 61.5738 | 0.027466 | -0.091553 | 0.15106 | 61.7706 | -60.9512 | -0.26093 | -0.10071 | -0.13275 | -0.20142 | -0.30212 | -0.26093 | -0.10529 | 0.12817 | 60.5988 | 60.8414 | 122.2641 | 122.4655 | -0.13275 | 122.4609 | 60.7178 | -0.26093 | 122.4655 | -0.13275 | 60.7178 | 122.2641 | 122.4609 | -122.8271 | -122.8271
148.9062 | 122.8226 | -60.7178 | 61.8988 | -0.24765 | 0.002162 | 0.003027 | 5.5496e-05 | 0.062961 | -0.0022153 | 0.06643 | -60.759 | 61.8256 | -60.9467 | -60.8414 | 61.6287 | 0.10986 | 0.050354 | 0.25177 | 61.7935 | -60.9558 | -0.22888 | -0.073242 | -0.041199 | -0.1236 | -0.27008 | -0.23804 | -0.10529 | 0.18768 | 60.7681 | 60.9695 | 122.3465 | 122.5433 | -0.041199 | 122.5113 | 60.8276 | -0.23804 | 122.5433 | -0.041199 | 60.8276 | 122.3465 | 122.5113 | -122.8455 | -122.8546
149.9688 | 122.8683 | -60.6812 | 61.8713 | -0.2095 | 0.0034436 | 0.0062314 | 0.0004827 | 0.063175 | 0.00034814 | 0.068994 | -60.7498 | 61.8256 | -60.9558 | -60.8276 | 61.6425 | 0.15106 | -0.022888 | 0.27008 | 61.7981 | -60.9467 | -0.27466 | -0.045776 | -0.068665 | -0.14649 | -0.22888 | -0.2655 | -0.073242 | 0.20599 | 60.6583 | 60.9512 | 122.3236 | 122.5067 | -0.068665 | 122.4792 | 60.8322 | -0.2655 | 122.5067 | -0.068665 | 60.8322 | 122.3236 | 122.4792 | -122.8271 | -122.818
150.9062 | 122.7676 | -60.7132 | 61.9263 | -0.23239 | 0.004939 | 0.0055906 | 0.0039007 | 0.064456 | -0.0034971 | 0.069207 | -60.9009 | 61.8576 | -60.9467 | -60.8963 | 61.5234 | 0.018311 | 0.16479 | 0.17395 | 61.8301 | -60.9741 | -0.23346 | -0.068665 | -0.18768 | -0.1831 | -0.40283 | -0.26092 | -0.096131 | 0.045776 | 60.878 | 60.8871 | 122.2366 | 122.5708 | -0.18768 | 122.5433 | 60.7315 | -0.26092 | 122.5708 | -0.18768 | 60.7315 | 122.2366 | 122.5433 | -122.8729 | -122.9004
151.9531 | 122.8912 | -60.7086 | 61.8576 | 0.080414 | 0.0036572 | 0.0077268 | -0.0001581 | 0.065952 | -0.00029266 | 0.066858 | -60.8139 | 61.8118 | -60.9741 | -60.8963 | 61.5875 | 0.032043 | -0.091553 | 0.14648 | 61.7798 | -60.9467 | -0.2655 | -0.045776 | -0.10529 | -0.18768 | -0.27008 | -0.23804 | -0.07782 | 0.16022 | 60.6171 | 60.8551 | 122.2961 | 122.5204 | -0.10529 | 122.4884 | 60.7407 | -0.23804 | 122.5204 | -0.10529 | 60.7407 | 122.2961 | 122.4884 | -122.8317 | -122.8043
152.9062 | 122.7676 | -60.7452 | 61.8942 | 1.1028 | 0.0040846 | 0.0060178 | 0.0045417 | 0.063388 | -0.0013609 | 0.068567 | -60.9055 | 61.8576 | -61.0016 | -60.9238 | 61.5417 | 0.064087 | 0.15564 | 0.16479 | 61.8347 | -60.9558 | -0.25635 | -0.036621 | -0.16022 | -0.17853 | -0.35248 | -0.21057 | -0.059509 | 0.09613 | 60.9009 | 60.91 | 122.287 | 122.6028 | -0.16022 | 122.58 | 60.8093 | -0.21057 | 122.6028 | -0.16022 | 60.8093 | 122.287 | 122.58 | -122.8958 | -122.85
153.9688 | 122.8867 | -60.6903 | 61.8622 | 0.14908 | 0.0025892 | 0.0062314 | 0.0011237 | 0.062747 | -0.0039243 | 0.068353 | -60.6949 | 61.8256 | -60.9421 | -60.8093 | 61.6699 | 0.15564 | -0.041199 | 0.28839 | 61.7798 | -60.9375 | -0.25177 | -0.036621 | -0.004577 | -0.11902 | -0.19226 | -0.24719 | -0.082398 | 0.24719 | 60.6491 | 60.9787 | 122.3602 | 122.5159 | -0.004577 | 122.4701 | 60.8459 | -0.24719 | 122.5159 | -0.004577 | 60.8459 | 122.3602 | 122.4701 | -122.8043 | -122.7997
154.9062 | 122.7036 | -60.7407 | 61.8805 | 0.095673 | 0.0062208 | 0.0072996 | 0.0088141 | 0.064243 | -7.9062e-05 | 0.069207 | -60.8505 | 61.8622 | -61.0382 | -60.9695 | 61.4777 | -0.29297 | -0.18768 | 0.33417 | 61.7798 | -61.0199 | -0.29755 | -0.01831 | -0.10986 | -0.22888 | -0.40283 | -0.27923 | -0.10071 | 0.18768 | 60.553 | 61.0748 | 122.2183 | 122.6028 | -0.10986 | 122.5204 | 60.4477 | -0.27923 | 122.6028 | -0.10986 | 60.4477 | 122.2183 | 122.5204 | -122.9187 | -122.9004
155.9531 | 122.8729 | -60.7086 | 61.8393 | 0.94254 | 0.0013074 | 0.0045224 | -0.0007989 | 0.064029 | 0.00034814 | 0.066858 | -60.6766 | 61.7981 | -60.9329 | -60.8231 | 61.702 | 0.18768 | -0.059509 | 0.30212 | 61.8073 | -60.9192 | -0.2243 | -0.041198 | 0.032043 | -0.11444 | -0.13733 | -0.21057 | -0.032043 | 0.25635 | 60.6491 | 61.0107 | 122.4106 | 122.5067 | 0.032043 | 122.5159 | 60.8963 | -0.21057 | 122.5067 | 0.032043 | 60.8963 | 122.4106 | 122.5159 | -122.7722 | -122.7585
156.9062 | 122.7448 | -60.7315 | 61.9171 | -0.27054 | 0.0040846 | 0.0066586 | 0.0045417 | 0.064243 | -0.0011471 | 0.065362 | -60.8185 | 61.9034 | -60.9695 | -60.91 | 61.5555 | 0.054932 | 0.13275 | 0.17853 | 61.8576 | -60.9467 | -0.23804 | -0.013733 | -0.086975 | -0.17853 | -0.36163 | -0.21515 | -0.059509 | 0.15106 | 60.8643 | 60.91 | 122.287 | 122.6349 | -0.086975 | 122.5891 | 60.7864 | -0.21515 | 122.6349 | -0.086975 | 60.7864 | 122.287 | 122.5891 | -122.8867 | -122.8638
157.9531 | 122.8226 | -60.6949 | 61.9308 | -0.24002 | 0.0025892 | 0.0028134 | -0.0020807 | 0.064029 | -0.0011471 | 0.068567 | -60.759 | 61.8576 | -60.9375 | -60.8414 | 61.6287 | 0.13275 | 0.045776 | 0.26093 | 61.8301 | -60.9741 | -0.24262 | -0.073242 | -0.064087 | -0.14648 | -0.30212 | -0.27924 | -0.10071 | 0.17853 | 60.7407 | 60.9558 | 122.3236 | 122.5525 | -0.064087 | 122.525 | 60.8276 | -0.27924 | 122.5525 | -0.064087 | 60.8276 | 122.3236 | 122.525 | -122.8683 | -122.905
158.9062 | 122.8134 | -60.7361 | 61.8668 | -0.018768 | 0.0064344 | 0.0079404 | 0.0045417 | 0.065097 | -0.0020017 | 0.069848 | -60.7681 | 61.8851 | -60.9833 | -60.8963 | 61.5509 | 0.018311 | 0.027466 | 0.12817 | 61.8301 | -60.997 | -0.24719 | 0.018311 | -0.032043 | -0.16022 | -0.31586 | -0.26093 | -0.036621 | 0.21515 | 60.7635 | 60.8643 | 122.287 | 122.6212 | -0.032043 | 122.5662 | 60.7544 | -0.26093 | 122.6212 | -0.032043 | 60.7544 | 122.287 | 122.5662 | -122.85 | -122.8638
159.9688 | 122.7951 | -60.6995 | 61.8896 | -0.11795 | 0.0040846 | 0.0090086 | 0.0045417 | 0.067234 | -0.0013609 | 0.069635 | -60.7773 | 61.8759 | -60.9879 | -60.8734 | 61.5829 | 0.091553 | 0.054932 | 0.18768 | 61.8668 | -60.9695 | -0.28839 | -0.013732 | -0.07782 | -0.17395 | -0.3067 | -0.27008 | -0.022888 | 0.21057 | 60.7544 | 60.8871 | 122.2824 | 122.5754 | -0.07782 | 122.5662 | 60.791 | -0.27008 | 122.5754 | -0.07782 | 60.791 | 122.2824 | 122.5662 | -122.8775 | -122.8592
160.9062 | 122.7585 | -60.759 | 61.908 | -0.23239 | 0.0053662 | 0.0055906 | 0.0019781 | 0.065952 | -0.0015745 | 0.06878 | -60.8139 | 61.8988 | -60.9833 | -60.9192 | 61.5509 | 0.064087 | 0.13733 | 0.17395 | 61.8805 | -60.9787 | -0.2243 | -0.009155 | -0.054932 | -0.16022 | -0.35706 | -0.21973 | -0.027466 | 0.16937 | 60.8963 | 60.9329 | 122.3099 | 122.6578 | -0.054932 | 122.6395 | 60.8231 | -0.21973 | 122.6578 | -0.054932 | 60.8231 | 122.3099 | 122.6395 | -122.8912 | -122.8867
161.9688 | 122.7493 | -60.7315 | 61.9034 | -0.2858 | 0.0055798 | 0.0083676 | 0.0019781 | 0.066165 | 0.00098914 | 0.067926 | -60.8597 | 61.9034 | -60.9512 | -60.9283 | 61.5372 | 0.045776 | 0.13733 | 0.16022 | 61.8668 | -60.9833 | -0.21973 | 0 | -0.12817 | -0.19684 | -0.36621 | -0.25177 | -0.036621 | 0.091553 | 60.8688 | 60.8917 | 122.2687 | 122.6349 | -0.12817 | 122.5983 | 60.7773 | -0.25177 | 122.6349 | -0.12817 | 60.7773 | 122.2687 | 122.5983 | -122.8546 | -122.8867
162.9062 | 122.818 | -60.7269 | 61.9034 | -0.2095 | 0.0075024 | 0.0066586 | 0.0051825 | 0.065311 | -0.0013609 | 0.067498 | -60.7773 | 61.9125 | -60.9924 | -60.8734 | 61.5692 | 0.064087 | 0.018311 | 0.16937 | 61.8347 | -60.9924 | -0.2655 | 0.009156 | -0.050354 | -0.14648 | -0.33417 | -0.2655 | -0.068664 | 0.21515 | 60.7452 | 60.8963 | 122.2961 | 122.6395 | -0.050354 | 122.5616 | 60.791 | -0.2655 | 122.6395 | -0.050354 | 60.791 | 122.2961 | 122.5616 | -122.8958 | -122.8958
163.9688 | 122.8409 | -60.7132 | 61.8805 | -0.22476 | 0.0042982 | 0.0072996 | -0.0031489 | 0.066379 | -0.0013609 | 0.067071 | -60.7498 | 61.8668 | -60.9421 | -60.8551 | 61.6379 | 0.13733 | 0.059509 | 0.26093 | 61.8439 | -60.9512 | -0.22888 | -0.013733 | -0.036621 | -0.14191 | -0.24262 | -0.23804 | -0.036621 | 0.19226 | 60.7727 | 60.9741 | 122.3511 | 122.58 | -0.036621 | 122.5571 | 60.8505 | -0.23804 | 122.58 | -0.036621 | 60.8505 | 122.3511 | 122.5571 | -122.8226 | -122.8317
164.9062 | 122.8775 | -60.7315 | 61.8393 | 0.233 | 0.0036572 | 0.010077 | 0.0021917 | 0.064029 | -0.00071986 | 0.068353 | -60.8185 | 61.8301 | -60.9879 | -60.9192 | 61.5875 | 0.032043 | -0.14191 | 0.12817 | 61.7798 | -60.9833 | -0.25635 | -0.009155 | -0.086975 | -0.18768 | -0.25177 | -0.25177 | -0.059509 | 0.16937 | 60.5896 | 60.8597 | 122.319 | 122.5616 | -0.086975 | 122.5113 | 60.7635 | -0.25177 | 122.5616 | -0.086975 | 60.7635 | 122.319 | 122.5113 | -122.8271 | -122.8226
165.9531 | 122.7448 | -60.7315 | 61.9171 | -0.1561 | 0.0072888 | 0.0075132 | 0.0026191 | 0.064456 | -0.0015745 | 0.067071 | -60.8185 | 61.9171 | -60.9741 | -60.9283 | 61.5555 | 0.059509 | 0.14191 | 0.17395 | 61.8484 | -61.0016 | -0.24261 | 0 | -0.086975 | -0.19684 | -0.36163 | -0.27008 | -0.068664 | 0.15564 | 60.8734 | 60.9055 | 122.287 | 122.6486 | -0.086975 | 122.58 | 60.791 | -0.27008 | 122.6486 | -0.086975 | 60.791 | 122.287 | 122.58 | -122.8912 | -122.9187
166.9062 | 122.8088 | -60.7269 | 61.8942 | -0.0035098 | 0.0034436 | 0.005377 | 0.0034735 | 0.066165 | 0.00034814 | 0.068567 | -60.7819 | 61.908 | -60.9879 | -60.9146 | 61.5555 | 0.041199 | 0.009155 | 0.13275 | 61.8439 | -61.0153 | -0.26093 | 0.013733 | -0.054931 | -0.18768 | -0.33875 | -0.28839 | -0.050354 | 0.20599 | 60.7361 | 60.8597 | 122.2824 | 122.6349 | -0.054931 | 122.5708 | 60.7681 | -0.28839 | 122.6349 | -0.054931 | 60.7681 | 122.2824 | 122.5708 | -122.8821 | -122.9095
167.9688 | 122.7997 | -60.7178 | 61.8988 | -0.14847 | 0.0047254 | 0.0085812 | 0.0026191 | 0.067447 | -0.00050626 | 0.06878 | -60.8047 | 61.9492 | -60.9741 | -60.9192 | 61.5601 | 0.07782 | 0.1236 | 0.18768 | 61.8988 | -61.0153 | -0.25635 | 0.050354 | -0.086976 | -0.20142 | -0.33874 | -0.29755 | 0 | 0.16937 | 60.8414 | 60.9055 | 122.2778 | 122.6669 | -0.086976 | 122.6166 | 60.7956 | -0.29755 | 122.6669 | -0.086976 | 60.7956 | 122.2778 | 122.6166 | -122.8729 | -122.9141
168.9062 | 122.7768 | -60.7269 | 61.9125 | 0.011749 | 0.0070752 | 0.011358 | 0.0024053 | 0.068943 | -0.0024289 | 0.069421 | -60.7864 | 61.8851 | -60.9879 | -60.9238 | 61.528 | 0.018311 | 0.022888 | 0.10529 | 61.8668 | -61.0062 | -0.26093 | -0.027466 | -0.059509 | -0.19684 | -0.38452 | -0.27924 | -0.045777 | 0.20142 | 60.7498 | 60.8322 | 122.2549 | 122.612 | -0.059509 | 122.5937 | 60.7452 | -0.27924 | 122.612 | -0.059509 | 60.7452 | 122.2549 | 122.5937 | -122.9004 | -122.9187
169.9688 | 122.7859 | -60.7086 | 61.8988 | -0.20187 | 0.004939 | 0.0058042 | 0.0002691 | 0.066806 | -0.00093346 | 0.070916 | -60.8322 | 61.8942 | -61.0016 | -60.9329 | 61.5601 | 0.054932 | 0.15106 | 0.17853 | 61.8805 | -60.997 | -0.29297 | -0.004578 | -0.1236 | -0.2243 | -0.33874 | -0.28839 | -0.018311 | 0.16937 | 60.8597 | 60.8871 | 122.2687 | 122.6028 | -0.1236 | 122.5891 | 60.7636 | -0.28839 | 122.6028 | -0.1236 | 60.7636 | 122.2687 | 122.5891 | -122.9004 | -122.8958
170.9062 | 122.7768 | -60.7269 | 61.9034 | -0.056915 | 0.0057934 | 0.0068722 | 0.0056097 | 0.068088 | -0.0020017 | 0.069848 | -60.7407 | 61.9171 | -60.9787 | -60.9146 | 61.5646 | 0.054932 | 0.022888 | 0.16022 | 61.8576 | -61.0199 | -0.25177 | 0.013733 | -0.013733 | -0.18768 | -0.33875 | -0.29297 | -0.045776 | 0.23804 | 60.7498 | 60.8871 | 122.2916 | 122.644 | -0.013733 | 122.5845 | 60.7819 | -0.29297 | 122.644 | -0.013733 | 60.7819 | 122.2916 | 122.5845 | -122.8821 | -122.9233
171.9531 | 122.7631 | -60.7452 | 61.8713 | 0.14145 | 0.0064344 | 0.005377 | 0.0013373 | 0.069156 | 0.00077554 | 0.068567 | -60.8276 | 61.8942 | -60.9879 | -60.9833 | 61.5051 | -0.050354 | -0.018311 | 0.059509 | 61.853 | -61.0336 | -0.24262 | 0.022888 | -0.082398 | -0.23804 | -0.36621 | -0.28839 | -0.018311 | 0.16022 | 60.7269 | 60.8047 | 122.2504 | 122.6395 | -0.082398 | 122.5983 | 60.6949 | -0.28839 | 122.6395 | -0.082398 | 60.6949 | 122.2504 | 122.5983 | -122.8592 | -122.905
172.9062 | 122.731 | -60.7224 | 61.8668 | 0.17197 | 0.0081434 | 0.011999 | 0.0009101 | 0.07471 | -0.0011471 | 0.067498 | -60.8505 | 61.9034 | -61.0016 | -60.8459 | 61.7752 | 0.15106 | -0.09613 | 0.068665 | 61.8576 | -61.0428 | -0.27924 | 0.036621 | -0.12817 | -0.1236 | -0.091552 | -0.32043 | -0.009155 | 0.15106 | 60.6262 | 60.791 | 122.4976 | 122.6257 | -0.12817 | 122.58 | 60.8734 | -0.32043 | 122.6257 | -0.12817 | 60.8734 | 122.4976 | 122.58 | -122.8683 | -122.9095
173.9062 | 122.7768 | -60.7315 | 61.8759 | 0.20248 | 0.004939 | 0.010717 | 0.0021917 | 0.068943 | 0.00056194 | 0.066858 | -60.8505 | 61.9034 | -61.0107 | -60.9741 | 61.5143 | -0.041199 | -0.032043 | 0.041199 | 61.8393 | -61.0153 | -0.27924 | 0.027465 | -0.11902 | -0.24261 | -0.36163 | -0.28381 | -0.036622 | 0.16022 | 60.6995 | 60.7727 | 122.2458 | 122.6349 | -0.11902 | 122.5708 | 60.6903 | -0.28381 | 122.6349 | -0.11902 | 60.6903 | 122.2458 | 122.5708 | -122.8867 | -122.8912
174.9688 | 122.7448 | -60.7407 | 61.8576 | -0.034027 | 0.0057934 | 0.010931 | 0.0032599 | 0.068729 | 0.00056194 | 0.068139 | -60.8002 | 61.8713 | -61.0199 | -60.9787 | 61.5005 | -0.054932 | -0.004578 | 0.036621 | 61.8622 | -61.0016 | -0.27923 | 0.013733 | -0.059509 | -0.23804 | -0.35706 | -0.26093 | 0.004578 | 0.21973 | 60.7361 | 60.7773 | 122.2412 | 122.612 | -0.059509 | 122.6028 | 60.6857 | -0.26093 | 122.612 | -0.059509 | 60.6857 | 122.2412 | 122.6028 | -122.8775 | -122.8592
175.9062 | 122.7997 | -60.7498 | 61.8393 | 0.11856 | 0.0053662 | 0.0072996 | 0.0015509 | 0.066165 | 0.00098914 | 0.068567 | -60.8414 | 61.9125 | -61.0062 | -60.9558 | 61.5051 | -0.036621 | -0.054932 | 0.064087 | 61.8256 | -61.0336 | -0.25635 | 0.073243 | -0.091553 | -0.20599 | -0.33417 | -0.28381 | -0.013732 | 0.1648 | 60.6949 | 60.8139 | 122.2549 | 122.6624 | -0.091553 | 122.5754 | 60.7132 | -0.28381 | 122.6624 | -0.091553 | 60.7132 | 122.2549 | 122.5754 | -122.8455 | -122.8729
176.9531 | 122.7448 | -60.7361 | 61.8576 | 0.034637 | 0.0070752 | 0.01029 | 0.0034735 | 0.06702 | -0.0011471 | 0.067285 | -60.8002 | 61.8988 | -60.9695 | -60.9558 | 61.5051 | -0.013733 | 0.027466 | 0.068665 | 61.8576 | -61.0474 | -0.23346 | 0.041199 | -0.064087 | -0.21973 | -0.35248 | -0.31128 | 0 | 0.16937 | 60.7635 | 60.8047 | 122.2412 | 122.6349 | -0.064087 | 122.5937 | 60.7224 | -0.31128 | 122.6349 | -0.064087 | 60.7224 | 122.2412 | 122.5937 | -122.8271 | -122.905
177.9062 | 122.7768 | -60.7544 | 61.8896 | 0.15671 | 0.0068616 | 0.0075132 | 0.0058233 | 0.068943 | -0.0013609 | 0.064935 | -60.8505 | 61.9125 | -61.0016 | -60.8551 | 61.4456 | -0.13275 | 0.10529 | 0.068665 | 61.8942 | -61.0611 | -0.24719 | 0.022889 | -0.09613 | -0.10071 | -0.44403 | -0.3067 | 0.004578 | 0.15106 | 60.8597 | 60.8231 | 122.2 | 122.6669 | -0.09613 | 122.6486 | 60.6216 | -0.3067 | 122.6669 | -0.09613 | 60.6216 | 122.2 | 122.6486 | -122.8912 | -122.9507
178.9531 | 122.8546 | -60.7224 | 61.8164 | 0.17197 | 0.0064344 | 0.011999 | 0.0002691 | 0.066165 | -0.00093346 | 0.070703 | -60.7819 | 61.8164 | -60.965 | -60.9146 | 61.5875 | 0.050354 | -0.17853 | 0.14648 | 61.8118 | -61.0016 | -0.24261 | 0 | -0.059509 | -0.19226 | -0.22888 | -0.27924 | -0.004577 | 0.18311 | 60.5438 | 60.8688 | 122.3099 | 122.5388 | -0.059509 | 122.5342 | 60.7727 | -0.27924 | 122.5388 | -0.059509 | 60.7727 | 122.3099 | 122.5342 | -122.7814 | -122.818
179.9062 | 122.8638 | -60.7086 | 61.8668 | 0.12619 | 0.0042982 | 0.0040952 | -0.0061395 | 0.065097 | -0.00093346 | 0.067712 | -60.8459 | 61.7706 | -60.997 | -60.9146 | 61.5738 | 0.054932 | -0.07782 | 0.18768 | 61.8439 | -60.9695 | -0.28839 | -0.09613 | -0.13733 | -0.20599 | -0.29297 | -0.26093 | -0.022888 | 0.15106 | 60.6308 | 60.8963 | 122.2824 | 122.4792 | -0.13733 | 122.5525 | 60.7636 | -0.26093 | 122.4792 | -0.13733 | 60.7636 | 122.2824 | 122.5525 | -122.8638 | -122.8363
180.9531 | 122.7905 | -60.7132 | 61.8439 | -0.026398 | 0.0062208 | 0.0087948 | 0.0026191 | 0.065311 | -0.0013609 | 0.066858 | -60.759 | 61.8759 | -60.9695 | -60.8917 | 61.5738 | 0 | -0.050354 | 0.19226 | 61.8393 | -61.0336 | -0.25635 | 0.032044 | -0.045776 | -0.17853 | -0.27008 | -0.32043 | -0.004578 | 0.21057 | 60.6628 | 60.9055 | 122.287 | 122.5891 | -0.045776 | 122.5525 | 60.7132 | -0.32043 | 122.5891 | -0.045776 | 60.7132 | 122.287 | 122.5525 | -122.8134 | -122.8775
181.9062 | 122.7814 | -60.7361 | 61.8484 | 0.18723 | 0.004939 | 0.0058042 | 0.0017645 | 0.068729 | 0.0020571 | 0.067071 | -60.8322 | 61.8988 | -60.997 | -60.9558 | 61.5005 | -0.050354 | -0.054932 | 0.064087 | 61.8393 | -61.0199 | -0.26093 | 0.050354 | -0.09613 | -0.21973 | -0.3479 | -0.28381 | -0.009156 | 0.16479 | 60.6812 | 60.8002 | 122.2366 | 122.6349 | -0.09613 | 122.5754 | 60.6857 | -0.28381 | 122.6349 | -0.09613 | 60.6857 | 122.2366 | 122.5754 | -122.8455 | -122.8683
182.9531 | 122.8088 | -60.7452 | 61.8622 | 0.15671 | 0.0062208 | 0.0083676 | 0.0041143 | 0.067234 | 0.0024845 | 0.069635 | -60.8231 | 61.8805 | -61.0291 | -60.9833 | 61.5005 | -0.045776 | -0.068665 | 0.064087 | 61.8668 | -61.0428 | -0.28381 | 0.01831 | -0.07782 | -0.23804 | -0.36163 | -0.29755 | 0.004577 | 0.20599 | 60.6766 | 60.8093 | 122.2458 | 122.6257 | -0.07782 | 122.612 | 60.6995 | -0.29755 | 122.6257 | -0.07782 | 60.6995 | 122.2458 | 122.612 | -122.8912 | -122.905
183.9062 | 122.7814 | -60.7452 | 61.853 | 0.14908 | 0.0077162 | 0.0077268 | 0.0019781 | 0.067874 | -0.0011471 | 0.069635 | -60.8322 | 61.8668 | -60.9879 | -60.9558 | 61.5051 | -0.041199 | -0.050354 | 0.054932 | 61.8393 | -61.0336 | -0.24262 | 0.013733 | -0.086975 | -0.21057 | -0.3479 | -0.28839 | -0.013733 | 0.15564 | 60.6949 | 60.8002 | 122.2504 | 122.612 | -0.086975 | 122.5845 | 60.704 | -0.28839 | 122.612 | -0.086975 | 60.704 | 122.2504 | 122.5845 | -122.8409 | -122.8867
184.9688 | 122.7493 | -60.7315 | 61.8622 | 0.011749 | 0.0057934 | 0.0068722 | 0.0028327 | 0.066806 | -0.0024289 | 0.067712 | -60.878 | 61.853 | -61.0016 | -60.9833 | 61.4731 | -0.059509 | -0.013733 | 0.045776 | 61.8668 | -61.0062 | -0.27008 | -0.009156 | -0.14648 | -0.25177 | -0.3891 | -0.27466 | 0.004577 | 0.1236 | 60.7178 | 60.7773 | 122.2046 | 122.5845 | -0.14648 | 122.5983 | 60.672 | -0.27466 | 122.5845 | -0.14648 | 60.672 | 122.2046 | 122.5983 | -122.8638 | -122.8683
185.9062 | 122.8592 | -60.6812 | 61.8301 | 0.1033 | 0.00323 | 0.0058042 | -0.0033625 | 0.067234 | 0.0035525 | 0.068567 | -60.7773 | 61.8164 | -60.9695 | -60.8963 | 61.5875 | 0.032043 | -0.16479 | 0.16022 | 61.8118 | -61.0016 | -0.28839 | -0.013733 | -0.096131 | -0.21515 | -0.24262 | -0.32044 | -0.01831 | 0.19226 | 60.5164 | 60.8414 | 122.2687 | 122.4976 | -0.096131 | 122.493 | 60.7132 | -0.32044 | 122.4976 | -0.096131 | 60.7132 | 122.2687 | 122.493 | -122.7997 | -122.8317
186.9531 | 122.7722 | -60.7315 | 61.8805 | 0.042267 | 0.0045118 | 0.0072996 | 0.0049689 | 0.064456 | 0.00056194 | 0.069635 | -60.8185 | 61.8668 | -60.9924 | -60.9512 | 61.4777 | -0.036621 | 0.032043 | 0.073242 | 61.8668 | -61.0428 | -0.26093 | -0.013733 | -0.086975 | -0.21973 | -0.40283 | -0.31128 | -0.013733 | 0.17395 | 60.7635 | 60.8047 | 122.2092 | 122.5983 | -0.086975 | 122.5983 | 60.6949 | -0.31128 | 122.5983 | -0.086975 | 60.6949 | 122.2092 | 122.5983 | -122.8729 | -122.9233
187.9062 | 122.8638 | -60.704 | 61.8164 | 0.26352 | 0.0042982 | 0.009863 | 0.0026191 | 0.068729 | -0.00093346 | 0.068139 | -60.7864 | 61.8393 | -60.9787 | -60.8871 | 61.5921 | 0.027466 | -0.18768 | 0.13733 | 61.8118 | -61.0336 | -0.27466 | 0.022888 | -0.082397 | -0.18311 | -0.2243 | -0.32959 | -0.004577 | 0.19226 | 60.5164 | 60.8414 | 122.2961 | 122.5433 | -0.082397 | 122.5159 | 60.7315 | -0.32959 | 122.5433 | -0.082397 | 60.7315 | 122.2961 | 122.5159 | -122.7951 | -122.85
188.9531 | 122.7768 | -60.7361 | 61.8576 | 0.065155 | 0.0047254 | 0.010077 | 0.0021917 | 0.06702 | 0.00013454 | 0.067926 | -60.8093 | 61.8896 | -61.0107 | -60.9467 | 61.5005 | -0.036621 | 0.027466 | 0.068665 | 61.8668 | -61.0107 | -0.27466 | 0.032043 | -0.073242 | -0.21057 | -0.35706 | -0.27466 | 0.009155 | 0.20142 | 60.7635 | 60.8047 | 122.2366 | 122.6257 | -0.073242 | 122.6028 | 60.6995 | -0.27466 | 122.6257 | -0.073242 | 60.6995 | 122.2366 | 122.6028 | -122.8683 | -122.8683
189.9062 | 122.8271 | -60.6903 | 61.8393 | 0.14145 | 0.0040846 | 0.0045224 | -0.0020807 | 0.064884 | -0.00093346 | 0.066858 | -60.7956 | 61.7844 | -60.9879 | -60.91 | 61.5646 | 0.032043 | -0.16937 | 0.15106 | 61.7981 | -60.9924 | -0.29755 | -0.054931 | -0.10528 | -0.21973 | -0.27466 | -0.30212 | -0.041198 | 0.19226 | 60.5209 | 60.8414 | 122.2549 | 122.4747 | -0.10528 | 122.4884 | 60.7224 | -0.30212 | 122.4747 | -0.10528 | 60.7224 | 122.2549 | 122.4884 | -122.8271 | -122.8317
190.9531 | 122.7631 | -60.7361 | 61.8713 | -0.011139 | 0.0055798 | 0.0090086 | 0.0058233 | 0.064456 | -0.00071986 | 0.068139 | -60.7773 | 61.8713 | -60.9879 | -60.8963 | 61.5326 | 0.022888 | 0.018311 | 0.12817 | 61.8393 | -61.0107 | -0.25177 | 0 | -0.041199 | -0.16022 | -0.33875 | -0.27466 | -0.032044 | 0.21057 | 60.7544 | 60.8643 | 122.2687 | 122.6074 | -0.041199 | 122.5754 | 60.759 | -0.27466 | 122.6074 | -0.041199 | 60.759 | 122.2687 | 122.5754 | -122.8592 | -122.8821
191.9062 | 122.7768 | -60.6857 | 61.8347 | 0.049896 | 0.0042982 | 0.0068722 | -0.0082757 | 0.065097 | 0.00098914 | 0.069421 | -60.8185 | 61.8073 | -60.9741 | -60.9329 | 61.5692 | 0.027466 | -0.086975 | 0.36163 | 61.8713 | -60.9467 | -0.28839 | -0.027466 | -0.13275 | -0.24719 | -0.2655 | -0.26093 | 0.036621 | 0.15564 | 60.5988 | 61.0474 | 122.2549 | 122.493 | -0.13275 | 122.5571 | 60.7132 | -0.26093 | 122.493 | -0.13275 | 60.7132 | 122.2549 | 122.5571 | -122.8088 | -122.7814
192.9531 | 122.8683 | -60.6995 | 61.8347 | 0.25589 | 0.0045118 | 0.010931 | -0.0007989 | 0.066806 | -0.00093346 | 0.06878 | -60.759 | 61.7706 | -60.9741 | -60.8917 | 61.5875 | 0.041199 | -0.20142 | 0.16479 | 61.7706 | -61.0062 | -0.27466 | -0.064087 | -0.059509 | -0.19226 | -0.24719 | -0.3067 | -0.064087 | 0.21515 | 60.498 | 60.8643 | 122.287 | 122.4701 | -0.059509 | 122.4701 | 60.7407 | -0.3067 | 122.4701 | -0.059509 | 60.7407 | 122.287 | 122.4701 | -122.8088 | -122.8409
193.9062 | 122.8821 | -60.6903 | 61.8256 | 0.19485 | 0.0051526 | 0.0055906 | 5.5496e-05 | 0.063602 | -0.0017881 | 0.070276 | -60.759 | 61.7844 | -60.9741 | -60.8688 | 61.6058 | 0.045776 | -0.19684 | 0.16937 | 61.8073 | -60.9833 | -0.28381 | -0.041199 | -0.068664 | -0.17853 | -0.21973 | -0.29297 | -0.018311 | 0.21515 | 60.4935 | 60.8597 | 122.2961 | 122.4747 | -0.068664 | 122.4976 | 60.7361 | -0.29297 | 122.4747 | -0.068664 | 60.7361 | 122.2961 | 122.4976 | -122.7997 | -122.8088
194.9844 | 122.8455 | -60.6857 | 61.8713 | -0.011139 | 0.0028028 | 0.0045224 | -0.0016535 | 0.063816 | 0.0018435 | 0.06878 | -60.8139 | 61.7386 | -60.9833 | -60.9009 | 61.6196 | 0.068665 | -0.082397 | 0.23346 | 61.821 | -60.9695 | -0.29755 | -0.13275 | -0.12817 | -0.21515 | -0.25177 | -0.28381 | -0.050354 | 0.16937 | 60.6033 | 60.9192 | 122.3053 | 122.4243 | -0.12817 | 122.5067 | 60.7544 | -0.28381 | 122.4243 | -0.12817 | 60.7544 | 122.3053 | 122.5067 | -122.8546 | -122.8409
195.9062 | 122.8821 | -60.6949 | 61.8256 | 0.14908 | 0.004939 | 0.0051632 | 0.0019781 | 0.063602 | -0.0015745 | 0.067071 | -60.7544 | 61.7798 | -60.9604 | -60.8734 | 61.5875 | 0.036621 | -0.18768 | 0.15564 | 61.7615 | -61.0062 | -0.2655 | -0.045777 | -0.05951 | -0.17853 | -0.23804 | -0.31128 | -0.064087 | 0.20599 | 60.5072 | 60.8505 | 122.2824 | 122.4747 | -0.05951 | 122.4564 | 60.7315 | -0.31128 | 122.4747 | -0.05951 | 60.7315 | 122.2824 | 122.4564 | -122.7859 | -122.8317
196.9531 | 122.8088 | -60.6995 | 61.8576 | 0.20248 | 0.0051526 | 0.0079404 | 0.0047553 | 0.065952 | 0.0018435 | 0.069848 | -60.8185 | 61.8256 | -61.0016 | -60.9329 | 61.5051 | -0.027466 | -0.086975 | 0.073242 | 61.8256 | -61.0245 | -0.30212 | -0.032043 | -0.11902 | -0.23346 | -0.35248 | -0.32501 | -0.032043 | 0.18311 | 60.6125 | 60.7727 | 122.2046 | 122.525 | -0.11902 | 122.525 | 60.672 | -0.32501 | 122.525 | -0.11902 | 60.672 | 122.2046 | 122.525 | -122.8592 | -122.8821
197.9062 | 122.8775 | -60.6857 | 61.8301 | 0.25589 | 0.004939 | 0.0079404 | -0.0007989 | 0.066165 | -0.00071986 | 0.066858 | -60.7727 | 61.7477 | -60.9924 | -60.8505 | 61.5875 | 0.022888 | -0.18768 | 0.15564 | 61.8164 | -60.9924 | -0.3067 | -0.082397 | -0.086975 | -0.16479 | -0.24262 | -0.3067 | -0.013733 | 0.21973 | 60.498 | 60.8414 | 122.2733 | 122.4335 | -0.086975 | 122.5021 | 60.7086 | -0.3067 | 122.4335 | -0.086975 | 60.7086 | 122.2733 | 122.5021 | -122.8226 | -122.8226
198.9531 | 122.818 | -60.7224 | 61.853 | 0.22537 | 0.0036572 | 0.0085812 | 0.0045417 | 0.06702 | -0.0017881 | 0.067712 | -60.8368 | 61.821 | -61.0016 | -60.9375 | 61.5097 | -0.050354 | -0.086975 | 0.064087 | 61.8118 | -61.0062 | -0.27924 | -0.032043 | -0.11444 | -0.21515 | -0.34332 | -0.28381 | -0.041198 | 0.16479 | 60.6354 | 60.7864 | 122.2321 | 122.5433 | -0.11444 | 122.5342 | 60.672 | -0.28381 | 122.5433 | -0.11444 | 60.672 | 122.2321 | 122.5342 | -122.8546 | -122.8592
199.9219 | 122.7859 | -60.7361 | 61.8713 | -0.018768 | 0.0079298 | 0.012213 | 0.0077459 | 0.066593 | -0.0015745 | 0.066003 | -60.7681 | 61.8942 | -60.9833 | -60.9146 | 61.5326 | -0.004578 | 0.013733 | 0.11444 | 61.8439 | -61.0291 | -0.24719 | 0.022888 | -0.032043 | -0.17853 | -0.33875 | -0.29297 | -0.027466 | 0.21515 | 60.7498 | 60.8505 | 122.2687 | 122.6303 | -0.032043 | 122.58 | 60.7315 | -0.29297 | 122.6303 | -0.032043 | 60.7315 | 122.2687 | 122.58 | -122.8546 | -122.9004
200.9531 | 122.7951 | -60.7361 | 61.8393 | 0.17197 | 0.0051526 | 0.0085812 | 0.0028327 | 0.067874 | -0.0030697 | 0.068353 | -60.8414 | 61.8439 | -61.0291 | -60.9329 | 61.5097 | -0.036621 | -0.086975 | 0.054932 | 61.8484 | -61.0107 | -0.29297 | 0.004578 | -0.10529 | -0.19684 | -0.32959 | -0.27466 | 0.009156 | 0.18768 | 60.6491 | 60.791 | 122.2458 | 122.58 | -0.10529 | 122.5845 | 60.6995 | -0.27466 | 122.58 | -0.10529 | 60.6995 | 122.2458 | 122.5845 | -122.8683 | -122.85
201.9062 | 122.8409 | -60.7086 | 61.8301 | 0.16434 | 0.0045118 | 0.0062314 | -0.0031489 | 0.066379 | -0.00093346 | 0.068567 | -60.7819 | 61.7477 | -60.9924 | -60.8963 | 61.6013 | 0.041199 | -0.17395 | 0.14191 | 61.8027 | -60.997 | -0.28381 | -0.082397 | -0.073242 | -0.18768 | -0.22888 | -0.28839 | -0.027466 | 0.21057 | 60.5347 | 60.8505 | 122.3099 | 122.4564 | -0.073242 | 122.5113 | 60.7498 | -0.28839 | 122.4564 | -0.073242 | 60.7498 | 122.3099 | 122.5113 | -122.8226 | -122.8271
202.9531 | 122.8683 | -60.6995 | 61.8347 | 0.24826 | 0.00323 | 0.0060178 | 0.0032599 | 0.06467 | -0.00093346 | 0.069848 | -60.8093 | 61.8027 | -60.9879 | -60.8688 | 61.6058 | 0.022888 | -0.2243 | 0.12817 | 61.7889 | -61.0153 | -0.28839 | -0.032044 | -0.10986 | -0.16937 | -0.22888 | -0.31586 | -0.045777 | 0.17853 | 60.4752 | 60.8276 | 122.3053 | 122.5021 | -0.10986 | 122.4884 | 60.7224 | -0.31586 | 122.5021 | -0.10986 | 60.7224 | 122.3053 | 122.4884 | -122.8226 | -122.85
203.9062 | 122.8821 | -60.7269 | 61.8164 | 0.19485 | 0.0045118 | 0.0075132 | -0.0003717 | 0.065311 | 0.00056194 | 0.069207 | -60.7178 | 61.7798 | -61.0245 | -60.8597 | 61.6562 | 0.068665 | -0.20142 | 0.16937 | 61.7889 | -60.9879 | -0.29755 | -0.036621 | 0.009156 | -0.13275 | -0.16022 | -0.26093 | -0.027466 | 0.3067 | 60.5255 | 60.8963 | 122.3831 | 122.5067 | 0.009156 | 122.5159 | 60.7956 | -0.26093 | 122.5067 | 0.009156 | 60.7956 | 122.3831 | 122.5159 | -122.8409 | -122.8043
204.9688 | 122.8821 | -60.6583 | 61.853 | -0.072174 | 0.0047254 | 0.0075132 | -0.0033625 | 0.065525 | -0.0015745 | 0.066644 | -60.7361 | 61.8164 | -60.9283 | -60.8185 | 61.6653 | 0.16479 | -0.09613 | 0.3067 | 61.8164 | -60.9558 | -0.27008 | -0.036621 | -0.07782 | -0.16022 | -0.18768 | -0.29755 | -0.036621 | 0.19226 | 60.5621 | 60.965 | 122.3236 | 122.4747 | -0.07782 | 122.4747 | 60.8231 | -0.29755 | 122.4747 | -0.07782 | 60.8231 | 122.3236 | 122.4747 | -122.7814 | -122.8088
205.9062 | 122.8455 | -60.7178 | 61.8622 | 0.19485 | 0.0030164 | 0.0025998 | -0.0037897 | 0.063816 | 0.00077554 | 0.069421 | -60.8002 | 61.7661 | -60.9833 | -60.91 | 61.5601 | 0.004578 | -0.1236 | 0.11902 | 61.7752 | -60.9833 | -0.2655 | -0.096131 | -0.082398 | -0.19226 | -0.30212 | -0.2655 | -0.086975 | 0.1831 | 60.5942 | 60.8368 | 122.2778 | 122.4838 | -0.082398 | 122.493 | 60.7224 | -0.2655 | 122.4838 | -0.082398 | 60.7224 | 122.2778 | 122.493 | -122.8455 | -122.8455
206.9688 | 122.7722 | -60.7269 | 61.9034 | 0.042267 | 0.0053662 | 0.005377 | 0.0073187 | 0.064456 | -0.0030697 | 0.065789 | -60.8047 | 61.8347 | -61.0016 | -60.9238 | 61.5143 | -0.027466 | 0.013733 | 0.091553 | 61.8301 | -61.0199 | -0.27466 | -0.068664 | -0.07782 | -0.19684 | -0.3891 | -0.29297 | -0.073242 | 0.19684 | 60.7407 | 60.8185 | 122.2412 | 122.5616 | -0.07782 | 122.5571 | 60.6995 | -0.29297 | 122.5616 | -0.07782 | 60.6995 | 122.2412 | 122.5571 | -122.905 | -122.9233
207.9062 | 122.8134 | -60.7132 | 61.853 | 0.019379 | 0.00023916 | 0.0066586 | -0.0020807 | 0.063602 | -0.0020017 | 0.067071 | -60.8322 | 61.7798 | -60.965 | -60.7681 | 61.6928 | -0.018311 | -0.14648 | 0.17853 | 61.8256 | -60.9512 | -0.25177 | -0.073242 | -0.11902 | -0.054931 | -0.16022 | -0.23804 | -0.027465 | 0.13275 | 60.5667 | 60.8917 | 122.406 | 122.493 | -0.11902 | 122.5388 | 60.6949 | -0.23804 | 122.493 | -0.11902 | 60.6949 | 122.406 | 122.5388 | -122.818 | -122.8043
208.9531 | 122.8226 | -60.7361 | 61.8713 | 0.26352 | 0.0034436 | 0.0075132 | 0.0034735 | 0.065311 | -0.00071986 | 0.069421 | -60.8322 | 61.8393 | -61.0016 | -60.9146 | 61.5189 | -0.036621 | -0.09613 | 0.073242 | 61.8073 | -61.0016 | -0.2655 | -0.032044 | -0.09613 | -0.17853 | -0.35248 | -0.2655 | -0.064087 | 0.16937 | 60.64 | 60.8093 | 122.2549 | 122.5754 | -0.09613 | 122.5433 | 60.6995 | -0.2655 | 122.5754 | -0.09613 | 60.6995 | 122.2549 | 122.5433 | -122.8729 | -122.8729
209.9219 | 122.7951 | -60.704 | 61.8759 | -0.087433 | 0.0051526 | 0.0040952 | 0.0039007 | 0.066593 | -0.0043515 | 0.068139 | -60.7636 | 61.8393 | -60.9787 | -60.8643 | 61.5784 | 0.073242 | 0.041199 | 0.19226 | 61.8393 | -60.9741 | -0.27466 | -0.036622 | -0.059509 | -0.16022 | -0.29755 | -0.27008 | -0.036622 | 0.21515 | 60.7452 | 60.8963 | 122.2824 | 122.5433 | -0.059509 | 122.5433 | 60.7773 | -0.27008 | 122.5433 | -0.059509 | 60.7773 | 122.2824 | 122.5433 | -122.8546 | -122.85
210.9531 | 122.8271 | -60.7315 | 61.8622 | 0.12619 | 0.0017346 | 0.0040952 | -0.0025079 | 0.065311 | -0.00029266 | 0.069207 | -60.8185 | 61.7661 | -60.9787 | -60.9146 | 61.5601 | 0.045776 | -0.091553 | 0.13733 | 61.8164 | -60.9924 | -0.24719 | -0.096131 | -0.086975 | -0.18311 | -0.30212 | -0.26093 | -0.045777 | 0.16022 | 60.64 | 60.8688 | 122.2916 | 122.4976 | -0.086975 | 122.5479 | 60.7773 | -0.26093 | 122.4976 | -0.086975 | 60.7773 | 122.2916 | 122.5479 | -122.8409 | -122.8546
211.9062 | 122.8775 | -60.6995 | 61.8347 | 1.1256 | 0.0036572 | 0.0025998 | 0.0015509 | 0.064243 | 0.0020571 | 0.067285 | -60.6262 | 61.7752 | -60.9695 | -60.8643 | 61.615 | 0.054932 | -0.2243 | 0.15106 | 61.7798 | -60.997 | -0.27008 | -0.059509 | 0.073242 | -0.16479 | -0.21973 | -0.29755 | -0.054932 | 0.34332 | 60.4752 | 60.8505 | 122.3145 | 122.4747 | 0.073242 | 122.4792 | 60.7544 | -0.29755 | 122.4747 | 0.073242 | 60.7544 | 122.3145 | 122.4792 | -122.8043 | -122.8317
212.9531 | 122.7722 | -60.7132 | 61.8668 | 0.18723 | 0.002162 | 0.0021726 | 0.0045417 | 0.06467 | -0.0022153 | 0.069421 | -60.8505 | 61.8118 | -61.0107 | -60.9558 | 61.5005 | -0.041199 | -0.036621 | 0.041199 | 61.8393 | -60.997 | -0.29755 | -0.054931 | -0.13733 | -0.24261 | -0.36621 | -0.28381 | -0.027466 | 0.16022 | 60.6766 | 60.7544 | 122.2137 | 122.525 | -0.13733 | 122.5525 | 60.672 | -0.28381 | 122.525 | -0.13733 | 60.672 | 122.2137 | 122.5525 | -122.8775 | -122.8638
213.9062 | 122.8592 | -60.7132 | 61.8484 | 0.15671 | 0.0047254 | 0.0060178 | -0.0020807 | 0.063602 | -0.0017881 | 0.068353 | -60.8139 | 61.7889 | -60.9741 | -60.9055 | 61.5646 | 0.018311 | -0.10071 | 0.11902 | 61.7798 | -60.965 | -0.26092 | -0.05951 | -0.10071 | -0.19226 | -0.28381 | -0.25177 | -0.068665 | 0.16022 | 60.6125 | 60.8322 | 122.2778 | 122.5021 | -0.10071 | 122.493 | 60.7315 | -0.25177 | 122.5021 | -0.10071 | 60.7315 | 122.2778 | 122.493 | -122.8226 | -122.8134
214.9688 | 122.7631 | -60.7224 | 61.9308 | 0.20248 | 0.0047254 | 0.0055906 | 0.0011237 | 0.063602 | -0.00093346 | 0.06878 | -60.8276 | 61.8439 | -60.9924 | -60.9238 | 61.5372 | 0.045776 | 0.14191 | 0.16937 | 61.8622 | -60.9879 | -0.27008 | -0.086975 | -0.10529 | -0.20142 | -0.39368 | -0.2655 | -0.068664 | 0.16479 | 60.8643 | 60.8917 | 122.2595 | 122.5662 | -0.10529 | 122.5845 | 60.7681 | -0.2655 | 122.5662 | -0.10529 | 60.7681 | 122.2595 | 122.5845 | -122.9233 | -122.9187
215.9062 | 122.8271 | -60.7178 | 61.8622 | 0.042267 | 0.0028028 | 0.0068722 | -0.0029351 | 0.063816 | 0.0012027 | 0.069207 | -60.8185 | 61.7615 | -60.9467 | -60.9009 | 61.5921 | 0.032043 | 0.15106 | 0.27466 | 61.8393 | -60.9421 | -0.22888 | -0.10071 | -0.10071 | -0.18311 | -0.27008 | -0.22431 | -0.022889 | 0.12817 | 60.8688 | 60.9924 | 122.3099 | 122.4792 | -0.10071 | 122.5571 | 60.7498 | -0.22431 | 122.4792 | -0.10071 | 60.7498 | 122.3099 | 122.5571 | -122.8088 | -122.8043
216.9531 | 122.7905 | -60.7132 | 61.8393 | 0.17197 | 0.0045118 | 0.0085812 | 0.0066779 | 0.065525 | -0.0024289 | 0.067712 | -60.8231 | 61.8439 | -60.9924 | -60.9329 | 61.5143 | -0.045776 | -0.064087 | 0.064087 | 61.821 | -60.9879 | -0.27924 | 0.004578 | -0.10986 | -0.21973 | -0.32501 | -0.27466 | -0.01831 | 0.16937 | 60.6491 | 60.7773 | 122.2275 | 122.5571 | -0.10986 | 122.5342 | 60.6674 | -0.27466 | 122.5571 | -0.10986 | 60.6674 | 122.2275 | 122.5342 | -122.8317 | -122.8271
217.9062 | 122.8683 | -60.6857 | 61.8393 | -0.14847 | 0.0019482 | 0.0096494 | 0.0024053 | 0.065525 | -0.0024289 | 0.067926 | -60.7498 | 61.7706 | -60.9421 | -60.8414 | 61.5967 | 0.050354 | -0.19226 | 0.17853 | 61.7889 | -60.9558 | -0.25635 | -0.068664 | -0.064087 | -0.15564 | -0.24261 | -0.27008 | -0.050354 | 0.19226 | 60.4935 | 60.8643 | 122.2824 | 122.4564 | -0.064087 | 122.4747 | 60.7361 | -0.27008 | 122.4564 | -0.064087 | 60.7361 | 122.2824 | 122.4747 | -122.7814 | -122.7951
218.9531 | 122.7722 | -60.7132 | 61.8622 | 0.14908 | 0.0051526 | 0.0079404 | 0.0053961 | 0.064243 | -0.0047787 | 0.070062 | -60.8368 | 61.8393 | -61.0107 | -60.9604 | 61.5005 | -0.041199 | -0.064087 | 0.036621 | 61.7844 | -61.0062 | -0.29755 | -0.022889 | -0.1236 | -0.24719 | -0.36163 | -0.29297 | -0.07782 | 0.17395 | 60.6491 | 60.7498 | 122.2137 | 122.5525 | -0.1236 | 122.4976 | 60.672 | -0.29297 | 122.5525 | -0.1236 | 60.672 | 122.2137 | 122.4976 | -122.8729 | -122.8683
219.9062 | 122.9095 | -60.6628 | 61.8851 | -0.14084 | 0.0010938 | 0.0066586 | -0.0042169 | 0.067234 | -0.0020017 | 0.066644 | -60.7498 | 61.7661 | -60.9375 | -60.8139 | 61.6745 | 0.17395 | -0.086975 | 0.31586 | 61.8073 | -60.9512 | -0.27466 | -0.11902 | -0.086975 | -0.15106 | -0.21057 | -0.28839 | -0.07782 | 0.18768 | 60.5759 | 60.9787 | 122.3373 | 122.4289 | -0.086975 | 122.4701 | 60.8368 | -0.28839 | 122.4289 | -0.086975 | 60.8368 | 122.3373 | 122.4701 | -122.8226 | -122.8363
220.9688 | 122.8683 | -60.7086 | 61.8164 | 0.35507 | 0.0030164 | 0.008154 | 0.0026191 | 0.066379 | -0.0011471 | 0.068353 | -60.759 | 61.7523 | -60.9604 | -60.8414 | 61.6241 | 0.059509 | -0.19684 | 0.16022 | 61.8027 | -60.9512 | -0.25177 | -0.064087 | -0.050354 | -0.13275 | -0.19226 | -0.24262 | -0.013733 | 0.20142 | 60.5118 | 60.8688 | 122.3328 | 122.4609 | -0.050354 | 122.5113 | 60.7681 | -0.24262 | 122.4609 | -0.050354 | 60.7681 | 122.3328 | 122.5113 | -122.7768 | -122.7676
221.9062 | 122.85 | -60.6949 | 61.8301 | -0.37735 | 0.002162 | 0.0072996 | -0.0031489 | 0.063602 | -0.0011471 | 0.068353 | -60.8459 | 61.7798 | -60.9741 | -60.9192 | 61.5692 | 0.032043 | -0.050354 | 0.16022 | 61.8073 | -60.9741 | -0.27924 | -0.050354 | -0.15106 | -0.2243 | -0.26093 | -0.27924 | -0.022888 | 0.12817 | 60.6445 | 60.8551 | 122.2641 | 122.4747 | -0.15106 | 122.5021 | 60.7269 | -0.27924 | 122.4747 | -0.15106 | 60.7269 | 122.2641 | 122.5021 | -122.8043 | -122.8043
222.9688 | 122.7539 | -60.7544 | 61.8484 | 1.8657 | 0.0072888 | 0.0045224 | 0.0051825 | 0.061466 | 0.00013454 | 0.067926 | -60.6445 | 61.8118 | -60.997 | -61.0016 | 61.4822 | -0.045776 | -0.013733 | 0.027466 | 61.8301 | -61.0107 | -0.24261 | -0.036621 | 0.10986 | -0.24719 | -0.36621 | -0.25635 | -0.018311 | 0.35248 | 60.7407 | 60.7819 | 122.2366 | 122.5662 | 0.10986 | 122.5845 | 60.7086 | -0.25635 | 122.5662 | 0.10986 | 60.7086 | 122.2366 | 122.5845 | -122.8455 | -122.8592
223.9062 | 122.8409 | -60.6903 | 61.8668 | -0.43076 | 0.0023756 | 0.0066586 | -0.0033625 | 0.062534 | -0.0026425 | 0.067712 | -60.8551 | 61.7706 | -60.9558 | -60.91 | 61.5738 | 0.032043 | -0.073242 | 0.17853 | 61.7889 | -60.9512 | -0.2655 | -0.09613 | -0.16479 | -0.21973 | -0.29297 | -0.26093 | -0.07782 | 0.10071 | 60.6171 | 60.8688 | 122.2641 | 122.4609 | -0.16479 | 122.4792 | 60.7224 | -0.26093 | 122.4609 | -0.16479 | 60.7224 | 122.2641 | 122.4792 | -122.8226 | -122.818
224.9688 | 122.8317 | -60.6903 | 61.8576 | 0.1033 | 0.0025892 | 0.0032406 | -0.0005853 | 0.063388 | -0.00029266 | 0.068567 | -60.8185 | 61.7798 | -60.9741 | -60.8871 | 61.5829 | 0.041199 | -0.082397 | 0.15564 | 61.7844 | -60.9558 | -0.28381 | -0.07782 | -0.12817 | -0.19684 | -0.27466 | -0.2655 | -0.073242 | 0.15564 | 60.6079 | 60.8459 | 122.2733 | 122.4701 | -0.12817 | 122.4747 | 60.7315 | -0.2655 | 122.4701 | -0.12817 | 60.7315 | 122.2733 | 122.4747 | -122.8317 | -122.8134
225.9062 | 122.8546 | -60.6812 | 61.8576 | 0.1796 | 0.0036572 | 0.0066586 | -0.0007989 | 0.062534 | -0.00029266 | 0.067285 | -60.8002 | 61.7569 | -60.9467 | -60.9009 | 61.5692 | 0.041199 | -0.064087 | 0.17395 | 61.8164 | -60.9512 | -0.2655 | -0.10071 | -0.11902 | -0.21973 | -0.28839 | -0.27008 | -0.041199 | 0.14648 | 60.6171 | 60.8551 | 122.2504 | 122.438 | -0.11902 | 122.4976 | 60.7224 | -0.27008 | 122.438 | -0.11902 | 60.7224 | 122.2504 | 122.4976 | -122.8043 | -122.8088
226.9531 | 122.8592 | -60.6949 | 61.821 | 1.6597 | 0.0040846 | 0.0077268 | 0.0019781 | 0.063602 | -0.0026425 | 0.067712 | -60.8093 | 61.7203 | -60.9924 | -60.8368 | 61.5875 | 0.041199 | -0.19684 | 0.14648 | 61.7706 | -60.9741 | -0.29755 | -0.10071 | -0.11444 | -0.14191 | -0.23346 | -0.27924 | -0.050354 | 0.18311 | 60.498 | 60.8414 | 122.2824 | 122.4152 | -0.11444 | 122.4655 | 60.7361 | -0.27924 | 122.4152 | -0.11444 | 60.7361 | 122.2824 | 122.4655 | -122.8134 | -122.7951
227.9062 | 122.8363 | -60.6949 | 61.8576 | -0.041657 | 0.001521 | 0.0058042 | -0.0048577 | 0.062534 | -0.00071986 | 0.06878 | -60.8368 | 61.7661 | -60.9787 | -60.8917 | 61.5738 | 0.045776 | -0.059509 | 0.17853 | 61.8027 | -60.9604 | -0.28381 | -0.091553 | -0.14191 | -0.19684 | -0.28381 | -0.2655 | -0.054932 | 0.14191 | 60.6354 | 60.8734 | 122.2687 | 122.4609 | -0.14191 | 122.4976 | 60.7407 | -0.2655 | 122.4609 | -0.14191 | 60.7407 | 122.2687 | 122.4976 | -122.8363 | -122.818
228.9688 | 122.8134 | -60.7315 | 61.853 | 0.1796 | 0.004939 | 0.011572 | 0.0047553 | 0.063175 | -0.0026425 | 0.068139 | -60.8368 | 61.8164 | -61.0153 | -60.9283 | 61.5143 | -0.036621 | -0.091553 | 0.059509 | 61.7981 | -60.9833 | -0.28381 | -0.036621 | -0.10529 | -0.19684 | -0.33874 | -0.25177 | -0.054931 | 0.17853 | 60.64 | 60.791 | 122.2458 | 122.5479 | -0.10529 | 122.5296 | 60.6949 | -0.25177 | 122.5479 | -0.10529 | 60.6949 | 122.2458 | 122.5296 | -122.8683 | -122.8363
229.9062 | 122.7631 | -60.7498 | 61.8851 | -0.24002 | 0.0023756 | 0.0058042 | 0.0017645 | 0.064456 | -0.0028561 | 0.067926 | -60.8322 | 61.8759 | -60.9741 | -60.9558 | 61.6882 | 0.22888 | 0.022888 | 0.018311 | 61.8805 | -60.9741 | -0.2243 | -0.009155 | -0.082397 | -0.20599 | -0.19684 | -0.2243 | -0.004578 | 0.14191 | 60.7727 | 60.7681 | 122.438 | 122.6257 | -0.082397 | 122.6303 | 60.9787 | -0.2243 | 122.6257 | -0.082397 | 60.9787 | 122.438 | 122.6303 | -122.8592 | -122.8592
230.9531 | 122.8592 | -60.6995 | 61.8256 | 0.76706 | 0.00066656 | 0.004736 | 0.0011237 | 0.06467 | -0.00093346 | 0.06878 | -60.6171 | 61.7569 | -60.9787 | -60.8505 | 61.5967 | 0.054932 | -0.21515 | 0.14191 | 61.7569 | -60.9238 | -0.27924 | -0.068665 | 0.082398 | -0.15106 | -0.22888 | -0.2243 | -0.068665 | 0.36163 | 60.4843 | 60.8414 | 122.2961 | 122.4564 | 0.082398 | 122.4564 | 60.7544 | -0.2243 | 122.4564 | 0.082398 | 60.7544 | 122.2961 | 122.4564 | -122.8043 | -122.7493
231.9062 | 122.8958 | -60.672 | 61.8393 | -0.026398 | 0.0010938 | 0.004736 | -0.0025079 | 0.061038 | -0.00029266 | 0.06643 | -60.791 | 61.7889 | -60.9558 | -60.8505 | 61.6287 | 0.11444 | -0.073242 | 0.25177 | 61.8073 | -60.9283 | -0.28381 | -0.050354 | -0.11902 | -0.17853 | -0.21057 | -0.25635 | -0.032043 | 0.16479 | 60.5988 | 60.9238 | 122.3007 | 122.4609 | -0.11902 | 122.4792 | 60.7864 | -0.25635 | 122.4609 | -0.11902 | 60.7864 | 122.3007 | 122.4792 | -122.7951 | -122.7676
232.9531 | 122.8821 | -60.6812 | 61.8347 | 0.15671 | 0.00323 | 0.0072996 | 0.0026191 | 0.063816 | -0.0024289 | 0.068139 | -60.7864 | 61.7752 | -60.9879 | -60.8917 | 61.5829 | 0.036621 | -0.17395 | 0.13733 | 61.7706 | -60.9695 | -0.3067 | -0.059509 | -0.10529 | -0.21057 | -0.25177 | -0.28839 | -0.064087 | 0.20142 | 60.5072 | 60.8185 | 122.2641 | 122.4564 | -0.10529 | 122.4518 | 60.7178 | -0.28839 | 122.4564 | -0.10529 | 60.7178 | 122.2641 | 122.4518 | -122.8226 | -122.8043
233.9062 | 122.8088 | -60.6491 | 61.8347 | -0.11795 | 0.0017346 | 0.0085812 | -0.0010125 | 0.061893 | -0.00050626 | 0.068994 | -60.7407 | 61.7615 | -60.9375 | -60.7956 | 61.6837 | 0.16022 | -0.059509 | 0.42572 | 61.8118 | -60.9283 | -0.28839 | -0.073242 | -0.091553 | -0.14648 | -0.15106 | -0.27924 | -0.022888 | 0.19684 | 60.5896 | 61.0748 | 122.3328 | 122.4106 | -0.091553 | 122.4609 | 60.8093 | -0.27924 | 122.4106 | -0.091553 | 60.8093 | 122.3328 | 122.4609 | -122.7722 | -122.7631
234.9531 | 122.8317 | -60.7086 | 61.8576 | 0.065155 | 0.0013074 | 0.0045224 | -0.0037897 | 0.060611 | -7.9062e-05 | 0.069421 | -60.8185 | 61.7386 | -60.9375 | -60.8871 | 61.5967 | 0.054932 | -0.073242 | 0.16479 | 61.8073 | -60.9604 | -0.22888 | -0.11902 | -0.10986 | -0.17853 | -0.26093 | -0.25177 | -0.050354 | 0.11902 | 60.6354 | 60.8734 | 122.3053 | 122.4472 | -0.10986 | 122.5159 | 60.7636 | -0.25177 | 122.4472 | -0.10986 | 60.7636 | 122.3053 | 122.5159 | -122.7951 | -122.818
235.9062 | 122.8729 | -60.6903 | 61.8622 | -0.11795 | 0.0013074 | 0.0058042 | 5.5496e-05 | 0.06232 | -0.00071986 | 0.062371 | -60.7224 | 61.7615 | -60.9375 | -60.5942 | 61.9904 | 0.41657 | -0.41657 | 0.17853 | 61.7981 | -60.9192 | -0.24719 | -0.10071 | -0.032043 | 0.096131 | 0.12817 | -0.22888 | -0.064087 | 0.21515 | 60.2737 | 60.8688 | 122.6807 | 122.4518 | -0.032043 | 122.4884 | 61.1069 | -0.22888 | 122.4518 | -0.032043 | 61.1069 | 122.6807 | 122.4884 | -122.7997 | -122.7814
236.9531 | 122.8775 | -60.6537 | 61.8759 | -0.041657 | 0.0010938 | 0.0032406 | -0.0016535 | 0.061679 | -0.0032835 | 0.06878 | -60.7727 | 61.7523 | -60.9512 | -60.8185 | 61.6196 | 0.11902 | -0.091553 | 0.25635 | 61.7981 | -60.9421 | -0.29755 | -0.1236 | -0.11902 | -0.16479 | -0.25635 | -0.28839 | -0.07782 | 0.17853 | 60.5621 | 60.91 | 122.2733 | 122.406 | -0.11902 | 122.4518 | 60.7727 | -0.28839 | 122.406 | -0.11902 | 60.7727 | 122.2733 | 122.4518 | -122.8271 | -122.818
237.9062 | 122.8638 | -60.6766 | 61.8668 | -0.064545 | 0.0019482 | 0.0040952 | -0.0012261 | 0.063175 | -0.0017881 | 0.066858 | -60.7773 | 61.7844 | -60.9604 | -60.8322 | 61.6379 | 0.1236 | -0.091553 | 0.25635 | 61.7889 | -60.9421 | -0.28381 | -0.082397 | -0.10071 | -0.15564 | -0.22888 | -0.2655 | -0.07782 | 0.18311 | 60.585 | 60.9329 | 122.3145 | 122.4609 | -0.10071 | 122.4655 | 60.8002 | -0.2655 | 122.4609 | -0.10071 | 60.8002 | 122.3145 | 122.4655 | -122.8271 | -122.8088
238.9688 | 122.8271 | -60.7361 | 61.8484 | 0.24826 | 0.0034436 | 0.0096494 | 0.0028327 | 0.061466 | -0.0026425 | 0.067498 | -60.8139 | 61.7844 | -60.9879 | -60.9009 | 61.5372 | -0.004578 | -0.15106 | 0.10071 | 61.7935 | -60.9879 | -0.25177 | -0.064087 | -0.07782 | -0.1648 | -0.31128 | -0.25177 | -0.054932 | 0.17395 | 60.585 | 60.8368 | 122.2733 | 122.5204 | -0.07782 | 122.5296 | 60.7315 | -0.25177 | 122.5204 | -0.07782 | 60.7315 | 122.2733 | 122.5296 | -122.8363 | -122.8363
239.9062 | 122.7631 | -60.7269 | 61.8851 | 1.1256 | 0.0036572 | 0.0060178 | 0.0017645 | 0.061466 | -0.00050626 | 0.065789 | -60.8093 | 61.8805 | -60.9695 | -60.9238 | 61.5509 | 0.059509 | 0.14191 | 0.16479 | 61.8713 | -60.9879 | -0.24261 | -0.004578 | -0.082397 | -0.19684 | -0.33417 | -0.26093 | -0.013733 | 0.16022 | 60.8688 | 60.8917 | 122.2778 | 122.6074 | -0.082397 | 122.5983 | 60.7864 | -0.26093 | 122.6074 | -0.082397 | 60.7864 | 122.2778 | 122.5983 | -122.8546 | -122.8729
240.9688 | 122.8409 | -60.7086 | 61.853 | -0.51468 | 0.002162 | 0.005377 | -0.0027215 | 0.065525 | -0.0013609 | 0.068994 | -60.7544 | 61.7844 | -60.9421 | -60.91 | 61.5738 | 0.013733 | -0.07782 | 0.13733 | 61.7981 | -60.9421 | -0.23346 | -0.068664 | -0.045777 | -0.20142 | -0.27923 | -0.23346 | -0.054931 | 0.18768 | 60.6308 | 60.8459 | 122.2824 | 122.493 | -0.045777 | 122.5067 | 60.7224 | -0.23346 | 122.493 | -0.045777 | 60.7224 | 122.2824 | 122.5067 | -122.7951 | -122.7951
241.9062 | 122.8409 | -60.6766 | 61.8622 | -0.21713 | 0.00323 | 0.0070858 | -0.0003717 | 0.062107 | -0.0015745 | 0.068994 | -60.7498 | 61.7981 | -60.9467 | -60.8322 | 61.6516 | 0.14191 | -0.013733 | 0.29297 | 61.8118 | -60.9421 | -0.27008 | -0.064087 | -0.073242 | -0.15564 | -0.21057 | -0.2655 | -0.050354 | 0.19684 | 60.6628 | 60.9695 | 122.3282 | 122.4747 | -0.073242 | 122.4884 | 60.8185 | -0.2655 | 122.4747 | -0.073242 | 60.8185 | 122.3282 | 122.4884 | -122.8088 | -122.8043
242.9531 | 122.8867 | -60.6903 | 61.8393 | 0.35507 | 0.0034436 | 0.0066586 | 0.0021917 | 0.063816 | 0.00034814 | 0.067285 | -60.7773 | 61.7706 | -60.9879 | -60.8459 | 61.5784 | 0.059509 | -0.18768 | 0.15564 | 61.7798 | -60.9604 | -0.29755 | -0.068664 | -0.086975 | -0.15564 | -0.26093 | -0.27008 | -0.059509 | 0.21057 | 60.5026 | 60.8459 | 122.2687 | 122.4609 | -0.086975 | 122.4701 | 60.7498 | -0.27008 | 122.4609 | -0.086975 | 60.7498 | 122.2687 | 122.4701 | -122.8271 | -122.7997
243.9062 | 122.8912 | -60.6674 | 61.8668 | -0.17136 | 0.0034436 | 0.0070858 | 0.0034735 | 0.064456 | -0.0030697 | 0.068353 | -60.8917 | 61.7889 | -60.9192 | -60.7544 | 61.6058 | 0.07782 | -0.027466 | 0.29297 | 61.7844 | -60.9238 | -0.25177 | -0.07782 | -0.22431 | -0.086976 | -0.26093 | -0.25635 | -0.082397 | 0.027465 | 60.64 | 60.9604 | 122.2733 | 122.4564 | -0.22431 | 122.4518 | 60.7452 | -0.25635 | 122.4564 | -0.22431 | 60.7452 | 122.2733 | 122.4518 | -122.7859 | -122.7905
244.9688 | 122.9095 | -60.6766 | 61.8713 | -0.12558 | 0.0042982 | 0.0068722 | -0.0016535 | 0.061893 | -7.9062e-05 | 0.06643 | -60.7361 | 61.8027 | -60.9283 | -60.8002 | 61.6699 | 0.14648 | -0.082397 | 0.28839 | 61.7935 | -60.9512 | -0.25177 | -0.068665 | -0.059509 | -0.1236 | -0.20142 | -0.27466 | -0.07782 | 0.19226 | 60.5942 | 60.965 | 122.3465 | 122.4792 | -0.059509 | 122.4701 | 60.8231 | -0.27466 | 122.4792 | -0.059509 | 60.8231 | 122.3465 | 122.4701 | -122.7997 | -122.8226
245.9062 | 122.8546 | -60.6857 | 61.8942 | -0.21713 | 0.0019482 | 0.003668 | 0.0006965 | 0.063388 | -0.0020017 | 0.064508 | -60.7407 | 61.7752 | -60.9512 | -60.8322 | 61.647 | 0.14191 | 0.009155 | 0.29297 | 61.8027 | -60.9467 | -0.2655 | -0.11902 | -0.054932 | -0.14648 | -0.24719 | -0.26093 | -0.091553 | 0.21057 | 60.6949 | 60.9787 | 122.3328 | 122.4609 | -0.054932 | 122.4884 | 60.8276 | -0.26093 | 122.4609 | -0.054932 | 60.8276 | 122.3328 | 122.4884 | -122.8455 | -122.8409
246.9531 | 122.8958 | -60.6674 | 61.8439 | 0.17197 | 0.002162 | 0.0070858 | 0.0017645 | 0.06232 | -0.0024289 | 0.069421 | -60.7727 | 61.7844 | -60.9741 | -60.8414 | 61.6104 | 0.050354 | -0.19226 | 0.16479 | 61.7569 | -60.9467 | -0.3067 | -0.059509 | -0.10529 | -0.17395 | -0.23346 | -0.27924 | -0.086975 | 0.20142 | 60.4752 | 60.8322 | 122.2778 | 122.4518 | -0.10529 | 122.4243 | 60.7178 | -0.27924 | 122.4518 | -0.10529 | 60.7178 | 122.2778 | 122.4243 | -122.818 | -122.7905
247.9062 | 122.7814 | -60.7086 | 61.8988 | -0.19424 | 0.00323 | 0.0072996 | 0.0026191 | 0.063175 | -0.0030697 | 0.06878 | -60.8139 | 61.8484 | -60.9833 | -60.9055 | 61.5509 | 0.045776 | 0.13275 | 0.17853 | 61.8301 | -60.965 | -0.27466 | -0.050354 | -0.10529 | -0.19684 | -0.3479 | -0.25635 | -0.068665 | 0.16937 | 60.8414 | 60.8871 | 122.2595 | 122.5571 | -0.10529 | 122.5388 | 60.7544 | -0.25635 | 122.5571 | -0.10529 | 60.7544 | 122.2595 | 122.5388 | -122.8821 | -122.8638
248.9688 | 122.8729 | -60.6903 | 61.8851 | -0.018768 | 0.00066656 | 0.0032406 | -0.0029351 | 0.063816 | -0.0013609 | 0.06878 | -60.8093 | 61.7935 | -60.9741 | -60.8551 | 61.6241 | 0.086975 | -0.082397 | 0.22888 | 61.7935 | -60.9329 | -0.28381 | -0.091553 | -0.11902 | -0.16479 | -0.26093 | -0.24261 | -0.091553 | 0.16479 | 60.6079 | 60.9192 | 122.3145 | 122.4838 | -0.11902 | 122.4838 | 60.7773 | -0.24261 | 122.4838 | -0.11902 | 60.7773 | 122.3145 | 122.4838 | -122.8592 | -122.818
249.9062 | 122.7768 | -60.7224 | 61.8942 | -0.0035098 | 0.0057934 | 0.0062314 | 0.0081733 | 0.064243 | -0.0020017 | 0.06643 | -60.7498 | 61.8622 | -60.9558 | -60.8597 | 61.5372 | 0.041199 | 0.009155 | 0.15564 | 61.821 | -61.0016 | -0.23346 | -0.032043 | -0.027466 | -0.13733 | -0.35706 | -0.27924 | -0.073242 | 0.20599 | 60.7315 | 60.878 | 122.2595 | 122.5845 | -0.027466 | 122.5433 | 60.7636 | -0.27924 | 122.5845 | -0.027466 | 60.7636 | 122.2595 | 122.5433 | -122.85 | -122.8958
250.9688 | 122.8958 | -60.6857 | 61.8576 | -0.041657 | 0.00023916 | 0.0066586 | -0.0040033 | 0.062534 | -0.0011471 | 0.067498 | -60.7864 | 61.821 | -60.9558 | -60.8459 | 61.6287 | 0.10986 | -0.068665 | 0.23804 | 61.821 | -60.9604 | -0.27008 | -0.036621 | -0.10071 | -0.16022 | -0.22888 | -0.27466 | -0.036621 | 0.16937 | 60.6171 | 60.9238 | 122.3145 | 122.5067 | -0.10071 | 122.5067 | 60.7956 | -0.27466 | 122.5067 | -0.10071 | 60.7956 | 122.3145 | 122.5067 | -122.8134 | -122.818
251.9062 | 122.8226 | -60.6903 | 61.8942 | -0.2095 | 0.0034436 | 0.0085812 | -0.0003717 | 0.060825 | -0.0015745 | 0.066003 | -60.759 | 61.8347 | -60.9467 | -60.8459 | 61.6379 | 0.11444 | 0.045776 | 0.2655 | 61.821 | -60.9329 | -0.25635 | -0.059509 | -0.068664 | -0.15564 | -0.25635 | -0.24261 | -0.073242 | 0.18768 | 60.7361 | 60.9558 | 122.3282 | 122.525 | -0.068664 | 122.5113 | 60.8047 | -0.24261 | 122.525 | -0.068664 | 60.8047 | 122.3282 | 122.5113 | -122.8409 | -122.8271
252.9531 | 122.8683 | -60.6628 | 61.8393 | -0.026398 | 0.0038708 | 0.0083676 | -0.0001581 | 0.061466 | -0.0028561 | 0.067712 | -60.8093 | 61.7889 | -60.9695 | -60.8597 | 61.6104 | 0.091553 | -0.059509 | 0.23346 | 61.7981 | -60.9467 | -0.3067 | -0.050354 | -0.14648 | -0.19684 | -0.22888 | -0.28381 | -0.041198 | 0.16022 | 60.6033 | 60.8963 | 122.2733 | 122.4518 | -0.14648 | 122.4609 | 60.7544 | -0.28381 | 122.4518 | -0.14648 | 60.7544 | 122.2733 | 122.4609 | -122.8088 | -122.7859
253.9062 | 122.7722 | -60.7224 | 61.94 | -0.27054 | 0.0040846 | 0.0055906 | 0.0026191 | 0.063388 | -0.0024289 | 0.065576 | -60.8185 | 61.8576 | -60.965 | -60.91 | 61.5463 | 0.050354 | 0.13733 | 0.20142 | 61.8347 | -60.9833 | -0.24261 | -0.082397 | -0.09613 | -0.18768 | -0.39368 | -0.26092 | -0.10529 | 0.14648 | 60.8597 | 60.9238 | 122.2687 | 122.58 | -0.09613 | 122.5571 | 60.7727 | -0.26092 | 122.58 | -0.09613 | 60.7727 | 122.2687 | 122.5571 | -122.905 | -122.9233
254.9062 | 122.7585 | -60.7178 | 61.9308 | -0.22476 | 0.0057934 | 0.0011044 | -0.0003717 | 0.062961 | 0.00056194 | 0.068353 | -60.8093 | 61.908 | -60.9924 | -60.9009 | 61.5555 | 0.050354 | 0.13275 | 0.17853 | 61.8576 | -60.9879 | -0.27466 | -0.022888 | -0.091553 | -0.18311 | -0.37537 | -0.27008 | -0.073242 | 0.18311 | 60.8505 | 60.8963 | 122.2733 | 122.6257 | -0.091553 | 122.5754 | 60.7681 | -0.27008 | 122.6257 | -0.091553 | 60.7681 | 122.2733 | 122.5754 | -122.9233 | -122.9187
255.9531 | 122.8912 | -60.6812 | 61.8759 | -0.018768 | 0.001521 | 0.0079404 | -0.0018671 | 0.066806 | 0.00098914 | 0.067712 | -60.7315 | 61.821 | -60.9421 | -60.8093 | 61.6516 | 0.13733 | -0.050354 | 0.30212 | 61.8073 | -60.9558 | -0.26093 | -0.054932 | -0.050354 | -0.12817 | -0.2243 | -0.27466 | -0.068665 | 0.21057 | 60.6308 | 60.9833 | 122.3328 | 122.5021 | -0.050354 | 122.4884 | 60.8185 | -0.27466 | 122.5021 | -0.050354 | 60.8185 | 122.3328 | 122.4884 | -122.818 | -122.8317
256.9062 | 122.7905 | -60.6812 | 61.9583 | -0.087433 | 0.0036572 | 0.0096494 | 0.0017645 | 0.064029 | 0.00013454 | 0.068139 | -60.8185 | 61.8713 | -60.9695 | -60.9055 | 61.5555 | 0.050354 | 0.13733 | 0.18768 | 61.8622 | -60.9695 | -0.28839 | -0.086975 | -0.13733 | -0.22431 | -0.40283 | -0.28839 | -0.09613 | 0.15106 | 60.8185 | 60.8688 | 122.2366 | 122.5525 | -0.13733 | 122.5433 | 60.7315 | -0.28839 | 122.5525 | -0.13733 | 60.7315 | 122.2366 | 122.5433 | -122.9279 | -122.9279
257.9531 | 122.8912 | -60.6628 | 61.8622 | -0.072174 | 0.0019482 | 0.0049496 | -0.0012261 | 0.062961 | -0.00093346 | 0.066217 | -60.7178 | 61.8256 | -60.9421 | -60.8093 | 61.6837 | 0.15106 | -0.054932 | 0.28381 | 61.8027 | -60.9421 | -0.27924 | -0.036621 | -0.054931 | -0.14648 | -0.17853 | -0.27924 | -0.05951 | 0.22431 | 60.6079 | 60.9467 | 122.3465 | 122.4884 | -0.054931 | 122.4655 | 60.8139 | -0.27924 | 122.4884 | -0.054931 | 60.8139 | 122.3465 | 122.4655 | -122.8043 | -122.8043
258.9062 | 122.7676 | -60.6995 | 61.94 | -0.17136 | 0.0051526 | 0.0058042 | 0.0062507 | 0.064029 | -0.00093346 | 0.067926 | -60.8368 | 61.8713 | -60.9833 | -60.9009 | 61.5372 | 0.064087 | 0.13733 | 0.16937 | 61.8759 | -60.9787 | -0.28381 | -0.068664 | -0.13733 | -0.20142 | -0.40283 | -0.27924 | -0.064086 | 0.14648 | 60.8368 | 60.8688 | 122.2366 | 122.5708 | -0.13733 | 122.5754 | 60.7636 | -0.27924 | 122.5708 | -0.13733 | 60.7636 | 122.2366 | 122.5754 | -122.9233 | -122.9187
259.9531 | 122.7493 | -60.7269 | 61.9263 | -0.24765 | 0.0055798 | 0.0051632 | 0.0013373 | 0.060825 | -0.00093346 | 0.069421 | -60.8185 | 61.8713 | -60.9741 | -60.9009 | 61.5509 | 0.064087 | 0.14648 | 0.1831 | 61.8713 | -60.9695 | -0.24719 | -0.054932 | -0.091552 | -0.17395 | -0.37537 | -0.24261 | -0.054932 | 0.15564 | 60.8734 | 60.91 | 122.2778 | 122.5983 | -0.091552 | 122.5983 | 60.791 | -0.24261 | 122.5983 | -0.091552 | 60.791 | 122.2778 | 122.5983 | -122.9004 | -122.8958
260.9062 | 122.8271 | -60.6995 | 61.972 | -0.22476 | 0.0030164 | 0.0015316 | 0.0002691 | 0.063602 | -0.0022153 | 0.067712 | -60.8276 | 61.8622 | -60.9924 | -60.91 | 61.5463 | 0.054932 | 0.13275 | 0.19226 | 61.8713 | -61.0016 | -0.29297 | -0.10986 | -0.12817 | -0.21057 | -0.42572 | -0.30212 | -0.10071 | 0.16479 | 60.8322 | 60.8917 | 122.2458 | 122.5616 | -0.12817 | 122.5708 | 60.7544 | -0.30212 | 122.5616 | -0.12817 | 60.7544 | 122.2458 | 122.5708 | -122.9645 | -122.9736
261.9531 | 122.8271 | -60.6995 | 61.8805 | 0.15671 | 0.0025892 | 0.0028134 | -0.0010125 | 0.065097 | -0.0013609 | 0.067285 | -60.8185 | 61.8073 | -60.965 | -60.9146 | 61.5646 | 0.022888 | -0.10529 | 0.12817 | 61.7844 | -60.9833 | -0.2655 | -0.073242 | -0.11902 | -0.21515 | -0.31586 | -0.28381 | -0.09613 | 0.14648 | 60.5942 | 60.8276 | 122.2641 | 122.5067 | -0.11902 | 122.4838 | 60.7224 | -0.28381 | 122.5067 | -0.11902 | 60.7224 | 122.2641 | 122.4838 | -122.8455 | -122.8638
262.9062 | 122.7631 | -60.7315 | 61.9125 | -0.20187 | 0.0055798 | 0.011786 | 0.0039007 | 0.062534 | 0.00013454 | 0.067498 | -60.8139 | 61.908 | -60.9924 | -60.9238 | 61.5417 | 0.041199 | 0.1236 | 0.17395 | 61.8484 | -61.0153 | -0.26093 | -0.004578 | -0.082398 | -0.19226 | -0.37079 | -0.28381 | -0.064087 | 0.17853 | 60.8551 | 60.9055 | 122.2733 | 122.6395 | -0.082398 | 122.58 | 60.7727 | -0.28381 | 122.6395 | -0.082398 | 60.7727 | 122.2733 | 122.58 | -122.905 | -122.9279
263.9688 | 122.8592 | -60.6812 | 61.8484 | -0.17136 | 0.0025892 | 0.0094358 | -0.0007989 | 0.063816 | 0.00034814 | 0.067498 | -60.7269 | 61.8118 | -60.9467 | -60.5255 | 61.9125 | 0.20142 | -0.35706 | 0.27008 | 61.7844 | -60.9604 | -0.2655 | -0.036621 | -0.045777 | 0.15564 | 0.064087 | -0.27924 | -0.064087 | 0.21973 | 60.3241 | 60.9512 | 122.5937 | 122.493 | -0.045777 | 122.4655 | 60.8826 | -0.27924 | 122.493 | -0.045777 | 60.8826 | 122.5937 | 122.4655 | -122.7951 | -122.8088
264.9062 | 122.7356 | -60.7681 | 61.8713 | 0.86624 | 0.0062208 | 0.0068722 | 0.0064643 | 0.063602 | -0.0011471 | 0.06878 | -60.8597 | 61.8713 | -61.0016 | -60.9879 | 61.4685 | -0.059509 | -0.004578 | 0.013733 | 61.821 | -61.0062 | -0.23346 | 0 | -0.091553 | -0.21973 | -0.40283 | -0.23804 | -0.050354 | 0.14191 | 60.7635 | 60.7819 | 122.2366 | 122.6395 | -0.091553 | 122.5891 | 60.7086 | -0.23804 | 122.6395 | -0.091553 | 60.7086 | 122.2366 | 122.5891 | -122.8729 | -122.8775
265.9062 | 122.7722 | -60.6903 | 61.9034 | -0.16373 | 0.0064344 | 0.0068722 | 0.0041143 | 0.064456 | -0.0028561 | 0.069207 | -60.8047 | 61.9171 | -60.997 | -60.91 | 61.5601 | 0.054932 | 0.1236 | 0.17853 | 61.8484 | -60.997 | -0.3067 | 0.013733 | -0.11444 | -0.21973 | -0.34332 | -0.3067 | -0.054931 | 0.19226 | 60.8139 | 60.8688 | 122.2504 | 122.6074 | -0.11444 | 122.5388 | 60.7452 | -0.3067 | 122.6074 | -0.11444 | 60.7452 | 122.2504 | 122.5388 | -122.9004 | -122.9004
266.9531 | 122.7676 | -60.7086 | 61.8896 | -0.26291 | 0.0038708 | 0.004736 | -0.0001581 | 0.065525 | 0.0012027 | 0.067926 | -60.791 | 61.8759 | -60.9512 | -60.8871 | 61.5784 | 0.073242 | 0.11444 | 0.21057 | 61.8759 | -60.9375 | -0.24262 | -0.013732 | -0.082398 | -0.17853 | -0.31128 | -0.22888 | -0.013732 | 0.16022 | 60.8231 | 60.9192 | 122.287 | 122.5845 | -0.082398 | 122.5845 | 60.7819 | -0.22888 | 122.5845 | -0.082398 | 60.7819 | 122.287 | 122.5845 | -122.8409 | -122.8271
267.9062 | 122.7814 | -60.7132 | 61.8668 | -0.11032 | 0.0038708 | 0.004736 | 0.0043281 | 0.066379 | -0.0037107 | 0.068353 | -60.7498 | 61.908 | -60.9879 | -60.878 | 61.5875 | 0.086975 | 0.022888 | 0.18768 | 61.8484 | -60.9879 | -0.27466 | 0.041199 | -0.036621 | -0.16479 | -0.27924 | -0.27466 | -0.01831 | 0.23804 | 60.7361 | 60.9009 | 122.3007 | 122.6212 | -0.036621 | 122.5616 | 60.8002 | -0.27466 | 122.6212 | -0.036621 | 60.8002 | 122.3007 | 122.5616 | -122.8546 | -122.8546
268.9531 | 122.7539 | -60.7269 | 61.9034 | -0.20187 | 0.0030164 | 0.008154 | 0.0026191 | 0.066379 | -0.0013609 | 0.06643 | -60.6995 | 61.9263 | -60.9467 | -60.9375 | 61.5555 | 0.054932 | 0.12817 | 0.18768 | 61.8668 | -60.9924 | -0.21973 | 0.022889 | 0.027466 | -0.21057 | -0.3479 | -0.2655 | -0.036621 | 0.24719 | 60.8551 | 60.9146 | 122.2824 | 122.6532 | 0.027466 | 122.5937 | 60.7819 | -0.2655 | 122.6532 | 0.027466 | 60.7819 | 122.2824 | 122.5937 | -122.85 | -122.8958
269.9062 | 122.7676 | -60.7361 | 61.8622 | 0.14145 | 0.0036572 | 0.011145 | 0.0047553 | 0.067234 | 0.00013454 | 0.066858 | -60.8459 | 61.8988 | -61.0062 | -60.965 | 61.5005 | -0.041199 | -0.027466 | 0.054932 | 61.8347 | -61.0245 | -0.27008 | 0.036621 | -0.10986 | -0.22888 | -0.36163 | -0.28839 | -0.027466 | 0.16022 | 60.7086 | 60.791 | 122.2366 | 122.6349 | -0.10986 | 122.5708 | 60.6949 | -0.28839 | 122.6349 | -0.10986 | 60.6949 | 122.2366 | 122.5708 | -122.8683 | -122.8867
270.9688 | 122.8409 | -60.6949 | 61.908 | -0.22476 | 0.0038708 | 0.0077268 | -0.0020807 | 0.064456 | 0.00098914 | 0.066858 | -60.7498 | 61.8484 | -60.9558 | -60.8688 | 61.6104 | 0.13275 | 0.068665 | 0.25177 | 61.8256 | -60.9833 | -0.26093 | -0.059509 | -0.054932 | -0.17395 | -0.29755 | -0.28839 | -0.082397 | 0.20599 | 60.7636 | 60.9467 | 122.3053 | 122.5433 | -0.054932 | 122.5204 | 60.8276 | -0.28839 | 122.5433 | -0.054932 | 60.8276 | 122.3053 | 122.5204 | -122.8638 | -122.8912
271.9062 | 122.7905 | -60.704 | 61.8851 | 0.049896 | 0.0068616 | 0.0079404 | 0.0071051 | 0.067874 | -0.0039243 | 0.067071 | -60.7544 | 61.908 | -60.9558 | -60.878 | 61.5555 | 0.041199 | 0.027466 | 0.16479 | 61.8347 | -61.0062 | -0.25177 | 0.022888 | -0.050354 | -0.17395 | -0.32959 | -0.30212 | -0.050354 | 0.20142 | 60.7315 | 60.8688 | 122.2595 | 122.612 | -0.050354 | 122.5388 | 60.7452 | -0.30212 | 122.612 | -0.050354 | 60.7452 | 122.2595 | 122.5388 | -122.8409 | -122.8912
272.9688 | 122.7768 | -60.7086 | 61.9263 | -0.16373 | 0.0047254 | 0.0049496 | 0.0024053 | 0.06702 | -0.00093346 | 0.067712 | -60.8276 | 61.908 | -60.9924 | -60.9238 | 61.5372 | 0.064087 | 0.13275 | 0.17395 | 61.8851 | -60.997 | -0.28381 | -0.018311 | -0.11902 | -0.21515 | -0.3891 | -0.28839 | -0.041199 | 0.16479 | 60.8414 | 60.8826 | 122.2458 | 122.6166 | -0.11902 | 122.5937 | 60.7727 | -0.28839 | 122.6166 | -0.11902 | 60.7727 | 122.2458 | 122.5937 | -122.9187 | -122.9233
273.9062 | 122.7951 | -60.7132 | 61.9034 | -0.056915 | 0.0060072 | 0.0072996 | 0.0041143 | 0.066593 | -0.0024289 | 0.069848 | -60.759 | 61.9034 | -60.965 | -60.9009 | 61.5646 | 0.050354 | 0.041199 | 0.15564 | 61.8668 | -60.9879 | -0.25177 | 0 | -0.045776 | -0.18768 | -0.33875 | -0.27466 | -0.036621 | 0.20599 | 60.7544 | 60.8688 | 122.2778 | 122.6166 | -0.045776 | 122.58 | 60.7636 | -0.27466 | 122.6166 | -0.045776 | 60.7636 | 122.2778 | 122.58 | -122.8683 | -122.8912
274.9688 | 122.7631 | -60.7315 | 61.8942 | -0.14084 | 0.0030164 | 0.0087948 | -0.0012261 | 0.066165 | -0.0017881 | 0.067712 | -60.8185 | 61.908 | -60.997 | -60.9192 | 61.5601 | 0.059509 | 0.12817 | 0.1831 | 61.9034 | -61.0016 | -0.2655 | 0.013733 | -0.086975 | -0.18768 | -0.33417 | -0.27008 | 0.009155 | 0.17853 | 60.8597 | 60.9146 | 122.2916 | 122.6395 | -0.086975 | 122.6349 | 60.791 | -0.27008 | 122.6395 | -0.086975 | 60.791 | 122.2916 | 122.6349 | -122.8912 | -122.8958
275.9062 | 122.7814 | -60.7086 | 61.908 | -0.079803 | 0.0062208 | 0.0058042 | 5.5496e-05 | 0.066806 | -0.0011471 | 0.067285 | -60.7544 | 61.8851 | -60.9695 | -60.8917 | 61.5601 | 0.041199 | 0.018311 | 0.15564 | 61.8576 | -61.0199 | -0.26093 | -0.022888 | -0.045777 | -0.18311 | -0.3479 | -0.31128 | -0.050354 | 0.21515 | 60.7269 | 60.8643 | 122.2687 | 122.5937 | -0.045777 | 122.5662 | 60.7498 | -0.31128 | 122.5937 | -0.045777 | 60.7498 | 122.2687 | 122.5662 | -122.8775 | -122.9279
276.9531 | 122.8958 | -60.6857 | 61.8484 | -0.16373 | 0.006648 | 0.0072996 | -0.0042169 | 0.063388 | -0.0013609 | 0.070062 | -60.7224 | 61.8668 | -60.9467 | -61.0748 | 61.409 | 0.09613 | 0.022888 | 0.21973 | 61.8347 | -60.9695 | -0.26093 | 0.01831 | -0.036621 | -0.3891 | -0.43945 | -0.28381 | -0.013733 | 0.2243 | 60.7086 | 60.9055 | 122.0947 | 122.5525 | -0.036621 | 122.5204 | 60.7819 | -0.28381 | 122.5525 | -0.036621 | 60.7819 | 122.0947 | 122.5204 | -122.7951 | -122.818
277.9062 | 122.8088 | -60.7132 | 61.8439 | -0.18662 | 0.0053662 | 0.0068722 | 0.0028327 | 0.06702 | -0.0024289 | 0.067926 | -60.7498 | 61.8988 | -60.9787 | -60.8871 | 61.5692 | 0.073242 | 0.018311 | 0.16479 | 61.8347 | -61.0199 | -0.2655 | 0.054932 | -0.036621 | -0.17395 | -0.27466 | -0.3067 | -0.009155 | 0.22888 | 60.7315 | 60.878 | 122.2824 | 122.612 | -0.036621 | 122.5479 | 60.7864 | -0.3067 | 122.612 | -0.036621 | 60.7864 | 122.2824 | 122.5479 | -122.8226 | -122.8638
278.9531 | 122.7585 | -60.7498 | 61.908 | -0.17899 | 0.0047254 | 0.0083676 | -0.0037897 | 0.065311 | 0.00077554 | 0.069207 | -60.8231 | 61.9171 | -60.9558 | -61.0931 | 61.5234 | 0.073242 | 0.14191 | 0.13275 | 61.8759 | -60.997 | -0.20599 | 0.009155 | -0.073242 | -0.34332 | -0.38452 | -0.24719 | -0.032043 | 0.13275 | 60.8917 | 60.8826 | 122.2733 | 122.6669 | -0.073242 | 122.6257 | 60.8231 | -0.24719 | 122.6669 | -0.073242 | 60.8231 | 122.2733 | 122.6257 | -122.8638 | -122.905
279.9062 | 122.8409 | -60.7086 | 61.8713 | 0.1796 | 0.004939 | 0.0077268 | -0.0050715 | 0.066593 | -7.9062e-05 | 0.070489 | -60.8276 | 61.7844 | -60.9833 | -60.91 | 61.5829 | 0.032043 | -0.09613 | 0.15106 | 61.821 | -60.9879 | -0.27466 | -0.086975 | -0.11902 | -0.20142 | -0.28839 | -0.27924 | -0.050354 | 0.15564 | 60.6125 | 60.8597 | 122.2916 | 122.493 | -0.11902 | 122.5296 | 60.7407 | -0.27924 | 122.493 | -0.11902 | 60.7407 | 122.2916 | 122.5296 | -122.8546 | -122.8592
280.9531 | 122.7264 | -60.7132 | 61.9171 | -0.13321 | 0.0036572 | 0.014349 | 0.0013373 | 0.063602 | -0.00093346 | 0.067712 | -60.8093 | 61.908 | -60.9695 | -60.9375 | 61.5372 | 0.045776 | 0.13733 | 0.18768 | 61.8942 | -61.0291 | -0.25635 | -0.009155 | -0.09613 | -0.2243 | -0.37994 | -0.31586 | -0.022888 | 0.16022 | 60.8505 | 60.9009 | 122.2504 | 122.6212 | -0.09613 | 122.6074 | 60.759 | -0.31586 | 122.6212 | -0.09613 | 60.759 | 122.2504 | 122.6074 | -122.8867 | -122.9462
281.9062 | 122.8455 | -60.7132 | 61.9125 | -0.087433 | 0.0042982 | 0.0090086 | 0.0051825 | 0.065097 | 0.00098914 | 0.069421 | -60.759 | 61.8988 | -60.9512 | -60.8643 | 61.5601 | 0.059509 | -0.11444 | -0.013733 | 61.8347 | -61.0336 | -0.23804 | -0.013733 | -0.045776 | -0.15106 | -0.35248 | -0.32043 | -0.07782 | 0.19226 | 60.5988 | 60.6995 | 122.2733 | 122.612 | -0.045776 | 122.5479 | 60.7727 | -0.32043 | 122.612 | -0.045776 | 60.7727 | 122.2733 | 122.5479 | -122.8638 | -122.9462
282.9688 | 122.8088 | -60.6903 | 61.9583 | -0.22476 | 0.0017346 | 0.0038816 | 0.0006965 | 0.065311 | -0.0013609 | 0.068139 | -60.8276 | 61.9125 | -60.9512 | -60.9192 | 61.5555 | 0.045776 | 0.13275 | 0.19684 | 61.8668 | -61.0016 | -0.26093 | -0.045776 | -0.13733 | -0.22888 | -0.40283 | -0.31128 | -0.091553 | 0.1236 | 60.8231 | 60.8871 | 122.2458 | 122.6028 | -0.13733 | 122.5571 | 60.7361 | -0.31128 | 122.6028 | -0.13733 | 60.7361 | 122.2458 | 122.5571 | -122.9095 | -122.9599
283.9062 | 122.7814 | -60.7224 | 61.8805 | -0.14084 | 0.00323 | 0.0094358 | 0.0030463 | 0.06467 | -0.00071986 | 0.068139 | -60.7315 | 61.9263 | -60.9604 | -60.878 | 61.5417 | 0.059509 | 0.027466 | 0.17395 | 61.853 | -60.997 | -0.23804 | 0.045777 | -0.009155 | -0.15564 | -0.33875 | -0.27466 | -0.027466 | 0.22888 | 60.7498 | 60.8963 | 122.2641 | 122.6486 | -0.009155 | 122.5754 | 60.7819 | -0.27466 | 122.6486 | -0.009155 | 60.7819 | 122.2641 | 122.5754 | -122.8409 | -122.8775
284.9531 | 122.7814 | -60.7269 | 61.9217 | -0.2095 | 0.0034436 | 0.01264 | 0.0045417 | 0.065525 | -0.0020017 | 0.067712 | -60.7727 | 61.9217 | -60.9924 | -60.8917 | 61.5921 | 0.073242 | 0.073242 | 0.19226 | 61.8896 | -61.0245 | -0.2655 | 0 | -0.045776 | -0.1648 | -0.32959 | -0.29755 | -0.032044 | 0.21973 | 60.8002 | 60.9192 | 122.319 | 122.6486 | -0.045776 | 122.6166 | 60.8002 | -0.29755 | 122.6486 | -0.045776 | 60.8002 | 122.319 | 122.6166 | -122.9141 | -122.9462
285.9219 | 122.8455 | -60.704 | 61.8668 | 0.011749 | 0.0028028 | 0.003027 | -0.0063531 | 0.064243 | -0.0020017 | 0.067712 | -60.8322 | 61.7798 | -60.9833 | -60.91 | 61.5921 | 0.050354 | -0.068665 | 0.17395 | 61.8347 | -60.965 | -0.27923 | -0.086975 | -0.12817 | -0.20599 | -0.27466 | -0.26093 | -0.032043 | 0.15106 | 60.6354 | 60.878 | 122.2961 | 122.4838 | -0.12817 | 122.5388 | 60.7544 | -0.26093 | 122.4838 | -0.12817 | 60.7544 | 122.2961 | 122.5388 | -122.85 | -122.8317
286.9688 | 122.731 | -60.7361 | 61.8988 | -0.18662 | 0.006648 | 0.010504 | 5.5496e-05 | 0.065952 | -0.0032835 | 0.066003 | -60.8322 | 61.9171 | -60.9741 | -60.7452 | 61.5051 | -0.022888 | -0.004578 | 0.21973 | 61.8301 | -61.0474 | -0.23804 | 0.01831 | -0.09613 | -0.009155 | -0.39368 | -0.31128 | -0.068665 | 0.14191 | 60.7315 | 60.9558 | 122.2412 | 122.6532 | -0.09613 | 122.5662 | 60.7132 | -0.31128 | 122.6532 | -0.09613 | 60.7132 | 122.2412 | 122.5662 | -122.8729 | -122.9462
287.9062 | 122.7448 | -60.7407 | 61.8942 | 0.019379 | 0.0034436 | 0.011145 | 0.0053961 | 0.067234 | -0.0013609 | 0.067712 | -60.7544 | 61.8942 | -60.9741 | -60.878 | 61.5509 | 0.050354 | 0.032043 | 0.16937 | 61.8393 | -61.0382 | -0.23346 | 0 | -0.013733 | -0.13733 | -0.34332 | -0.29755 | -0.054932 | 0.21973 | 60.7727 | 60.91 | 122.2916 | 122.6349 | -0.013733 | 122.58 | 60.791 | -0.29755 | 122.6349 | -0.013733 | 60.791 | 122.2916 | 122.58 | -122.8683 | -122.9324
288.9531 | 122.7585 | -60.7178 | 61.9171 | 0.16434 | 0.0055798 | 0.0079404 | -0.0001581 | 0.064243 | 0.00077554 | 0.067712 | -60.9924 | 61.9308 | -61.0062 | -60.9375 | 61.528 | 0.054932 | 0.15564 | 0.16479 | 61.8942 | -61.0199 | -0.28839 | 0.013733 | -0.27466 | -0.21973 | -0.3891 | -0.30212 | -0.022888 | 0.013733 | 60.8734 | 60.8826 | 122.2458 | 122.6486 | -0.27466 | 122.612 | 60.7727 | -0.30212 | 122.6486 | -0.27466 | 60.7727 | 122.2458 | 122.612 | -122.9233 | -122.937
289.9062 | 122.8088 | -60.7132 | 61.853 | 0.24826 | 0.006648 | 0.0066586 | 0.0017645 | 0.067661 | -0.00050626 | 0.066217 | -60.8322 | 61.853 | -61.0107 | -60.9283 | 61.5189 | -0.032043 | -0.10071 | 0.068665 | 61.8393 | -61.0199 | -0.29755 | 0 | -0.11902 | -0.21515 | -0.33417 | -0.3067 | -0.013733 | 0.17853 | 60.6125 | 60.7819 | 122.2321 | 122.5662 | -0.11902 | 122.5525 | 60.6812 | -0.3067 | 122.5662 | -0.11902 | 60.6812 | 122.2321 | 122.5525 | -122.8638 | -122.8729
290.9688 | 122.7951 | -60.7178 | 61.8896 | -0.27054 | 0.0053662 | 0.0066586 | 0.0047553 | 0.067447 | -0.0024289 | 0.067926 | -60.7773 | 61.8484 | -60.997 | -60.8688 | 61.5601 | 0.064087 | -0.004578 | 0.16022 | 61.8759 | -60.997 | -0.27924 | -0.041198 | -0.05951 | -0.15106 | -0.32959 | -0.27924 | -0.013732 | 0.21973 | 60.7132 | 60.878 | 122.2778 | 122.5662 | -0.05951 | 122.5937 | 60.7819 | -0.27924 | 122.5662 | -0.05951 | 60.7819 | 122.2778 | 122.5937 | -122.8867 | -122.8867
291.9062 | 122.7951 | -60.6995 | 61.8713 | -0.14084 | 0.0060072 | 0.0017454 | 0.0017645 | 0.065952 | -0.0013609 | 0.067285 | -60.7727 | 61.8942 | -61.0016 | -60.8917 | 61.5875 | 0.068665 | 0.086975 | 0.21515 | 61.8759 | -61.0107 | -0.30212 | 0.022888 | -0.073242 | -0.19226 | -0.28381 | -0.31128 | 0.004578 | 0.22888 | 60.7864 | 60.9146 | 122.287 | 122.5937 | -0.073242 | 122.5754 | 60.7681 | -0.31128 | 122.5937 | -0.073242 | 60.7681 | 122.287 | 122.5754 | -122.8729 | -122.8821
292.9531 | 122.7722 | -60.7086 | 61.8759 | -0.16373 | 0.0057934 | 0.0079404 | 0.0009101 | 0.066593 | -0.0017881 | 0.069207 | -60.791 | 61.9171 | -60.9787 | -60.8963 | 61.5784 | 0.064087 | 0.10071 | 0.19684 | 61.8988 | -60.9879 | -0.27008 | 0.041198 | -0.082398 | -0.18768 | -0.29755 | -0.27924 | 0.022888 | 0.18768 | 60.8093 | 60.9055 | 122.287 | 122.6257 | -0.082398 | 122.6074 | 60.7727 | -0.27924 | 122.6257 | -0.082398 | 60.7727 | 122.287 | 122.6074 | -122.8546 | -122.8638
293.9062 | 122.7905 | -60.7132 | 61.9034 | -0.17899 | 0.0064344 | 0.004736 | 0.0013373 | 0.06702 | -0.0024289 | 0.067926 | -60.8093 | 61.9034 | -60.9741 | -60.9055 | 61.5692 | 0.054932 | 0.1236 | 0.17853 | 61.8851 | -61.0016 | -0.26092 | 0 | -0.09613 | -0.19226 | -0.33417 | -0.28839 | -0.01831 | 0.16479 | 60.8368 | 60.8917 | 122.2824 | 122.6166 | -0.09613 | 122.5983 | 60.7681 | -0.28839 | 122.6166 | -0.09613 | 60.7681 | 122.2824 | 122.5983 | -122.8775 | -122.905
294.9688 | 122.8638 | -60.672 | 61.8942 | 0.057526 | 0.0023756 | 0.0040952 | -0.0048577 | 0.065952 | -0.00050626 | 0.067926 | -60.7407 | 61.8484 | -60.9055 | -60.8139 | 61.6653 | 0.15106 | -0.050354 | 0.30212 | 61.821 | -60.9558 | -0.23346 | -0.045776 | -0.068665 | -0.14191 | -0.22888 | -0.28381 | -0.073242 | 0.16479 | 60.6216 | 60.9741 | 122.3373 | 122.5204 | -0.068665 | 122.493 | 60.8231 | -0.28381 | 122.5204 | -0.068665 | 60.8231 | 122.3373 | 122.493 | -122.7997 | -122.85
295.9219 | 122.8043 | -60.7086 | 61.8439 | 0.11856 | 0.0028028 | 0.0075132 | -0.0022943 | 0.066806 | -0.0030697 | 0.068994 | -60.8185 | 61.7615 | -60.997 | -60.9283 | 61.5555 | 0.013733 | -0.10071 | 0.15106 | 61.8347 | -60.9604 | -0.28839 | -0.082397 | -0.10986 | -0.21973 | -0.28839 | -0.25177 | -0.009155 | 0.17853 | 60.6079 | 60.8597 | 122.2641 | 122.4701 | -0.10986 | 122.5433 | 60.7224 | -0.25177 | 122.4701 | -0.10986 | 60.7224 | 122.2641 | 122.5433 | -122.8409 | -122.8043
296.9688 | 122.8729 | -60.6812 | 61.853 | 1.0646 | 0.0051526 | 0.0038816 | -0.0020807 | 0.064884 | 0.0020571 | 0.066858 | -60.6308 | 61.8484 | -60.9467 | -60.8322 | 61.6699 | 0.16937 | -0.073242 | 0.3067 | 61.7935 | -60.9879 | -0.2655 | -0.004577 | 0.050354 | -0.15106 | -0.1831 | -0.3067 | -0.059509 | 0.31586 | 60.6079 | 60.9879 | 122.3511 | 122.5296 | 0.050354 | 122.4747 | 60.8505 | -0.3067 | 122.5296 | 0.050354 | 60.8505 | 122.3511 | 122.4747 | -122.7997 | -122.8409
297.9062 | 122.7814 | -60.7224 | 61.8896 | 0.14908 | 0.0060072 | 0.0060178 | 0.0073187 | 0.064243 | -0.00050626 | 0.067712 | -60.7224 | 61.8668 | -60.997 | -60.8688 | 61.5417 | 0.064087 | 0.004578 | 0.16937 | 61.8484 | -61.0062 | -0.27466 | -0.022888 | 0 | -0.14648 | -0.3479 | -0.28381 | -0.041198 | 0.27466 | 60.7269 | 60.8917 | 122.2641 | 122.5891 | 0 | 122.5708 | 60.7864 | -0.28381 | 122.5891 | 0 | 60.7864 | 122.2641 | 122.5708 | -122.8867 | -122.8958
298.9688 | 122.7356 | -60.7086 | 61.9125 | -0.33157 | 0.0051526 | 0.0087948 | 5.5496e-05 | 0.063388 | -0.00071986 | 0.066217 | -60.8047 | 61.8896 | -60.965 | -60.9192 | 61.5234 | 0.041199 | 0.13733 | 0.20142 | 61.8988 | -60.997 | -0.25635 | -0.022889 | -0.096131 | -0.21057 | -0.3891 | -0.28839 | -0.013733 | 0.16022 | 60.8459 | 60.91 | 122.2321 | 122.5983 | -0.096131 | 122.6074 | 60.7498 | -0.28839 | 122.5983 | -0.096131 | 60.7498 | 122.2321 | 122.6074 | -122.8775 | -122.9095
299.9062 | 122.7585 | -60.7544 | 61.8759 | -0.47653 | 0.0051526 | 0.0090086 | 0.0036871 | 0.067234 | -0.0011471 | 0.068353 | -60.8917 | 61.8988 | -61.0062 | -60.9695 | 61.4594 | -0.054932 | 0.009155 | 0.054932 | 61.8713 | -61.0291 | -0.25177 | 0.022888 | -0.13733 | -0.21515 | -0.41656 | -0.27466 | -0.004578 | 0.11444 | 60.7636 | 60.8093 | 122.2137 | 122.6532 | -0.13733 | 122.6257 | 60.6995 | -0.27466 | 122.6532 | -0.13733 | 60.6995 | 122.2137 | 122.6257 | -122.8821 | -122.905
300.9688 | 122.85 | -60.704 | 61.8347 | 0.24826 | 0.004939 | 0.008154 | -0.0007989 | 0.066593 | 0.0026981 | 0.066644 | -60.7407 | 61.8118 | -60.9467 | -60.8643 | 61.6058 | 0.041199 | -0.18768 | 0.16022 | 61.7661 | -61.0062 | -0.24261 | -0.022888 | -0.036621 | -0.16022 | -0.22888 | -0.30212 | -0.068665 | 0.20599 | 60.5164 | 60.8643 | 122.3099 | 122.5159 | -0.036621 | 122.4701 | 60.7452 | -0.30212 | 122.5159 | -0.036621 | 60.7452 | 122.3099 | 122.4701 | -122.7814 | -122.8409
301.9062 | 122.7951 | -60.7086 | 61.8668 | -0.22476 | 0.0062208 | 0.0083676 | 0.0045417 | 0.064456 | -0.0020017 | 0.067071 | -60.7544 | 61.908 | -60.965 | -60.8597 | 61.5692 | 0.073242 | 0.064087 | 0.19684 | 61.8576 | -61.0107 | -0.25635 | 0.041199 | -0.045777 | -0.15106 | -0.29755 | -0.30212 | -0.009155 | 0.21057 | 60.7727 | 60.9055 | 122.2778 | 122.6166 | -0.045777 | 122.5662 | 60.7819 | -0.30212 | 122.6166 | -0.045777 | 60.7819 | 122.2778 | 122.5662 | -122.8317 | -122.8775
302.9062 | 122.7631 | -60.7361 | 61.908 | 0.080414 | 0.0057934 | 0.0077268 | 0.0030463 | 0.066165 | -0.00071986 | 0.068567 | -60.8093 | 61.9034 | -60.9924 | -60.9604 | 61.5051 | -0.041199 | 0.027466 | 0.073242 | 61.8439 | -61.0336 | -0.25635 | -0.004578 | -0.073242 | -0.2243 | -0.40283 | -0.29755 | -0.064087 | 0.18311 | 60.7635 | 60.8093 | 122.2412 | 122.6395 | -0.073242 | 122.58 | 60.6949 | -0.29755 | 122.6395 | -0.073242 | 60.6949 | 122.2412 | 122.58 | -122.9004 | -122.9416
303.9688 | 122.7814 | -60.7132 | 61.908 | -0.21713 | 0.0051526 | 0.0092222 | 0.0004827 | 0.067234 | -0.0028561 | 0.069635 | -60.8093 | 61.9171 | -60.9924 | -60.9146 | 61.5417 | 0.050354 | 0.11902 | 0.17395 | 61.8896 | -61.0107 | -0.27924 | 0.009155 | -0.09613 | -0.20142 | -0.36621 | -0.29755 | -0.018311 | 0.18311 | 60.8322 | 60.8871 | 122.2549 | 122.6303 | -0.09613 | 122.6028 | 60.7636 | -0.29755 | 122.6303 | -0.09613 | 60.7636 | 122.2549 | 122.6028 | -122.9004 | -122.9187
304.9062 | 122.7539 | -60.7315 | 61.8713 | 0.16434 | 0.0042982 | 0.0075132 | 0.0077459 | 0.070011 | -0.0017881 | 0.067712 | -60.8597 | 61.8805 | -60.9879 | -60.7407 | 61.5601 | -0.12817 | 0.036621 | 0.11902 | 61.8668 | -61.0062 | -0.25635 | 0.009155 | -0.12817 | -0.009156 | -0.31128 | -0.27466 | -0.004578 | 0.12817 | 60.7681 | 60.8505 | 122.2916 | 122.612 | -0.12817 | 122.5983 | 60.6033 | -0.27466 | 122.612 | -0.12817 | 60.6033 | 122.2916 | 122.5983 | -122.8592 | -122.8775
305.9688 | 122.8729 | -60.6766 | 61.8576 | -0.018768 | 0.0038708 | 0.0055906 | -0.0087031 | 0.065525 | 0.00077554 | 0.068567 | -60.7864 | 61.8576 | -60.965 | -60.8643 | 61.6058 | 0.10071 | -0.073242 | 0.22888 | 61.8118 | -60.9787 | -0.28839 | 0 | -0.10986 | -0.18768 | -0.25177 | -0.30212 | -0.045776 | 0.17853 | 60.6033 | 60.9055 | 122.2824 | 122.5342 | -0.10986 | 122.4884 | 60.7773 | -0.30212 | 122.5342 | -0.10986 | 60.7773 | 122.2824 | 122.4884 | -122.8226 | -122.8363
306.9062 | 122.7905 | -60.7178 | 61.8851 | 0.034637 | 0.004939 | 0.0075132 | 0.0034735 | 0.064884 | 0.0014163 | 0.067712 | -60.7544 | 61.8942 | -60.9833 | -60.8871 | 61.5326 | 0.064087 | 0.018311 | 0.16022 | 61.8622 | -61.0153 | -0.2655 | 0.009155 | -0.036622 | -0.16937 | -0.35248 | -0.29755 | -0.022888 | 0.22888 | 60.7361 | 60.878 | 122.2504 | 122.612 | -0.036622 | 122.58 | 60.7819 | -0.29755 | 122.612 | -0.036622 | 60.7819 | 122.2504 | 122.58 | -122.8683 | -122.9004
307.9531 | 122.7997 | -60.7224 | 61.908 | -0.2095 | 0.0045118 | 0.0058042 | 0.0026191 | 0.068302 | -0.0013609 | 0.068353 | -60.759 | 61.908 | -60.9787 | -60.8826 | 61.5692 | 0.064087 | 0.045776 | 0.19684 | 61.8759 | -60.9833 | -0.25635 | 0 | -0.036621 | -0.16022 | -0.33874 | -0.26092 | -0.032043 | 0.21973 | 60.7681 | 60.9192 | 122.2916 | 122.6303 | -0.036621 | 122.5983 | 60.7864 | -0.26092 | 122.6303 | -0.036621 | 60.7864 | 122.2916 | 122.5983 | -122.8867 | -122.8912
308.9062 | 122.7814 | -60.7178 | 61.8942 | -0.12558 | 0.0060072 | 0.0075132 | 0.0036871 | 0.067874 | -0.0017881 | 0.070703 | -60.7452 | 61.9492 | -60.9695 | -60.8688 | 61.5784 | 0.086975 | 0.050354 | 0.19226 | 61.8713 | -61.0291 | -0.25177 | 0.054932 | -0.027466 | -0.15106 | -0.31586 | -0.31128 | -0.022888 | 0.2243 | 60.7681 | 60.91 | 122.2961 | 122.6669 | -0.027466 | 122.5891 | 60.8047 | -0.31128 | 122.6669 | -0.027466 | 60.8047 | 122.2961 | 122.5891 | -122.8638 | -122.9233
309.9688 | 122.7585 | -60.6995 | 61.8759 | 0.011749 | 0.004939 | 0.0062314 | 0.0034735 | 0.067447 | -0.0011471 | 0.068994 | -60.7773 | 61.8576 | -60.9879 | -60.8917 | 61.5509 | 0.050354 | 0.027466 | 0.15564 | 61.8576 | -61.0062 | -0.28839 | -0.018311 | -0.07782 | -0.19226 | -0.32501 | -0.3067 | -0.018311 | 0.21057 | 60.7269 | 60.8551 | 122.2504 | 122.5571 | -0.07782 | 122.5571 | 60.7498 | -0.3067 | 122.5571 | -0.07782 | 60.7498 | 122.2504 | 122.5571 | -122.8638 | -122.8821
310.9062 | 122.8226 | -60.7132 | 61.8713 | -0.38498 | 0.0057934 | 0.005377 | 0.0021917 | 0.067234 | -0.00071986 | 0.067285 | -60.7544 | 61.9171 | -60.9833 | -60.8826 | 61.5692 | 0.091553 | 0 | 0.15564 | 61.8759 | -61.0107 | -0.27008 | 0.045776 | -0.041199 | -0.16937 | -0.30212 | -0.29755 | 0.004578 | 0.22888 | 60.7132 | 60.8688 | 122.2824 | 122.6303 | -0.041199 | 122.5891 | 60.8047 | -0.29755 | 122.6303 | -0.041199 | 60.8047 | 122.2824 | 122.5891 | -122.8546 | -122.8821
311.9688 | 122.7722 | -60.7452 | 61.8713 | -0.25528 | 0.0055798 | 0.0094358 | -0.0037897 | 0.065311 | -0.0015745 | 0.070062 | -60.7819 | 61.9034 | -60.9604 | -60.9192 | 61.5372 | 0.045776 | 0.14191 | 0.19684 | 61.8942 | -61.0016 | -0.21515 | 0.032043 | -0.036621 | -0.17395 | -0.33417 | -0.25635 | 0.022888 | 0.17853 | 60.8871 | 60.9421 | 122.2824 | 122.6486 | -0.036621 | 122.6395 | 60.791 | -0.25635 | 122.6486 | -0.036621 | 60.791 | 122.2824 | 122.6395 | -122.8317 | -122.8729
312.9062 | 122.7722 | -60.7224 | 61.8713 | 0.034637 | 0.0060072 | 0.010504 | 0.0032599 | 0.068302 | 0.00077554 | 0.069207 | -60.7727 | 61.9034 | -60.9924 | -60.91 | 61.5417 | 0.018311 | 0.009155 | 0.11444 | 61.8393 | -61.0428 | -0.27008 | 0.032043 | -0.050354 | -0.18768 | -0.32959 | -0.32043 | -0.032044 | 0.21973 | 60.7315 | 60.8368 | 122.2641 | 122.6257 | -0.050354 | 122.5616 | 60.7407 | -0.32043 | 122.6257 | -0.050354 | 60.7407 | 122.2641 | 122.5616 | -122.8638 | -122.9141
313.9531 | 122.7356 | -60.7269 | 61.8851 | -0.20187 | 0.0030164 | 0.0083676 | -0.0018671 | 0.063388 | 0.00077554 | 0.068353 | -60.8093 | 61.8942 | -60.9695 | -60.9146 | 61.441 | -0.10986 | 0.13733 | 0.20599 | 61.8805 | -61.0199 | -0.24261 | 0.009155 | -0.082397 | -0.18768 | -0.44403 | -0.29297 | -0.004578 | 0.16022 | 60.8643 | 60.9329 | 122.168 | 122.6212 | -0.082397 | 122.6074 | 60.6171 | -0.29297 | 122.6212 | -0.082397 | 60.6171 | 122.168 | 122.6074 | -122.8546 | -122.905
314.9062 | 122.8638 | -60.6949 | 61.8301 | 0.26352 | 0.0034436 | 0.009863 | -0.0037897 | 0.066165 | -0.0013609 | 0.066858 | -60.7819 | 61.7981 | -60.9833 | -60.878 | 61.5967 | 0.054932 | -0.20142 | 0.17395 | 61.8027 | -60.9924 | -0.28839 | -0.032043 | -0.086975 | -0.18311 | -0.23346 | -0.29755 | -0.027466 | 0.20142 | 60.4935 | 60.8688 | 122.2916 | 122.493 | -0.086975 | 122.4976 | 60.7498 | -0.29755 | 122.493 | -0.086975 | 60.7498 | 122.2916 | 122.4976 | -122.8134 | -122.8226
315.9531 | 122.7814 | -60.7224 | 61.8851 | -0.19424 | 0.0047254 | 0.0096494 | 0.0011237 | 0.067234 | -0.0011471 | 0.067285 | -60.7727 | 61.9354 | -60.9741 | -60.8917 | 61.5829 | 0.086975 | 0.073242 | 0.21057 | 61.8713 | -61.0428 | -0.25177 | 0.050354 | -0.050354 | -0.16937 | -0.30212 | -0.32043 | -0.013733 | 0.20142 | 60.7956 | 60.9329 | 122.3053 | 122.6578 | -0.050354 | 122.5937 | 60.8093 | -0.32043 | 122.6578 | -0.050354 | 60.8093 | 122.3053 | 122.5937 | -122.8592 | -122.9279
316.9062 | 122.7493 | -60.759 | 61.8713 | 0.17197 | 0.0079298 | 0.010077 | 0.0045417 | 0.066593 | -0.0013609 | 0.070489 | -61.1252 | 61.8301 | -61.0428 | -60.965 | 61.4548 | -0.064087 | 0.032043 | 0.027466 | 61.821 | -61.0519 | -0.28381 | -0.041199 | -0.36621 | -0.20599 | -0.41656 | -0.29297 | -0.050354 | -0.082397 | 60.791 | 60.7864 | 122.2137 | 122.5891 | -0.36621 | 122.58 | 60.6949 | -0.29297 | 122.5891 | -0.36621 | 60.6949 | 122.2137 | 122.58 | -122.9141 | -122.9233
317.9688 | 122.7859 | -60.7224 | 61.8759 | 0.019379 | 0.006648 | 0.0092222 | 0.0060369 | 0.067447 | 0.0014163 | 0.070062 | -60.7819 | 61.9034 | -60.9924 | -60.9192 | 61.5326 | 0 | 0.013733 | 0.11902 | 61.8622 | -61.0245 | -0.27008 | 0.027465 | -0.059509 | -0.19684 | -0.34332 | -0.30212 | -0.013733 | 0.21057 | 60.7361 | 60.8414 | 122.2549 | 122.6257 | -0.059509 | 122.5845 | 60.7224 | -0.30212 | 122.6257 | -0.059509 | 60.7224 | 122.2549 | 122.5845 | -122.8683 | -122.9004
318.9062 | 122.7402 | -60.7407 | 61.8851 | 0.057526 | 0.0051526 | 0.0090086 | 0.0026191 | 0.068088 | 0.00056194 | 0.068353 | -60.7956 | 61.9263 | -60.9879 | -60.9512 | 61.5051 | -0.022888 | 0.027466 | 0.086975 | 61.8668 | -61.0291 | -0.24719 | 0.041199 | -0.054931 | -0.21057 | -0.37994 | -0.28839 | -0.018311 | 0.19226 | 60.7681 | 60.8276 | 122.2458 | 122.6669 | -0.054931 | 122.6074 | 60.7178 | -0.28839 | 122.6669 | -0.054931 | 60.7178 | 122.2458 | 122.6074 | -122.8729 | -122.9141
319.9531 | 122.7402 | -60.7498 | 61.8851 | 0.049896 | 0.0070752 | 0.0087948 | 0.0030463 | 0.069797 | -0.0020017 | 0.068139 | -60.791 | 61.9171 | -60.9833 | -60.9512 | 61.5051 | -0.013733 | 0.018311 | 0.07782 | 61.8896 | -61.0291 | -0.23346 | 0.032043 | -0.041199 | -0.20142 | -0.37994 | -0.27924 | 0.004577 | 0.19226 | 60.7681 | 60.8276 | 122.2549 | 122.6669 | -0.041199 | 122.6395 | 60.7361 | -0.27924 | 122.6669 | -0.041199 | 60.7361 | 122.2549 | 122.6395 | -122.8683 | -122.9141
320.9062 | 122.7448 | -60.7407 | 61.8851 | 0.049896 | 0.0072888 | 0.0066586 | 0.0013373 | 0.069797 | -0.00071986 | 0.068567 | -60.8002 | 61.908 | -60.9695 | -60.9421 | 61.5234 | 0 | 0.022888 | 0.082397 | 61.8668 | -61.0199 | -0.22888 | 0.022888 | -0.059509 | -0.20142 | -0.36163 | -0.27923 | -0.018311 | 0.16937 | 60.7636 | 60.8231 | 122.2641 | 122.6486 | -0.059509 | 122.6074 | 60.7407 | -0.27923 | 122.6486 | -0.059509 | 60.7407 | 122.2641 | 122.6074 | -122.8546 | -122.905
321.9531 | 122.7768 | -60.7498 | 61.853 | 0.080414 | 0.0079298 | 0.0070858 | 5.5496e-05 | 0.065952 | 0.00098914 | 0.06878 | -60.8505 | 61.8942 | -60.9833 | -60.9787 | 61.4914 | -0.036621 | -0.004578 | 0.041199 | 61.8576 | -61.0519 | -0.23346 | 0.041199 | -0.10071 | -0.22888 | -0.36163 | -0.30212 | 0.004578 | 0.13275 | 60.7452 | 60.791 | 122.2412 | 122.644 | -0.10071 | 122.6074 | 60.7132 | -0.30212 | 122.644 | -0.10071 | 60.7132 | 122.2412 | 122.6074 | -122.8363 | -122.905
322.9062 | 122.7402 | -60.7269 | 61.8759 | 0.042267 | 0.0062208 | 0.0077268 | 0.0024053 | 0.066379 | -0.0026425 | 0.068353 | -60.791 | 61.908 | -61.0062 | -60.9375 | 61.5097 | -0.013733 | 0.027466 | 0.10071 | 61.8439 | -61.0657 | -0.27924 | 0.032043 | -0.064087 | -0.21057 | -0.36621 | -0.33875 | -0.032044 | 0.21515 | 60.7544 | 60.8276 | 122.2366 | 122.6349 | -0.064087 | 122.5708 | 60.7132 | -0.33875 | 122.6349 | -0.064087 | 60.7132 | 122.2366 | 122.5708 | -122.8821 | -122.9416
323.9531 | 122.8043 | -60.7086 | 61.8668 | -0.041657 | 0.0036572 | 0.0096494 | -0.0003717 | 0.068088 | -0.00093346 | 0.069848 | -60.7178 | 61.8942 | -61.0016 | -60.878 | 61.5692 | 0.050354 | 0.022888 | 0.17395 | 61.8851 | -61.0199 | -0.29297 | 0.027466 | -0.009155 | -0.16937 | -0.29755 | -0.31128 | 0.018311 | 0.28381 | 60.7315 | 60.8826 | 122.2778 | 122.6028 | -0.009155 | 122.5937 | 60.759 | -0.31128 | 122.6028 | -0.009155 | 60.759 | 122.2778 | 122.5937 | -122.8683 | -122.8867
324.9062 | 122.7173 | -60.7544 | 61.8805 | 0.049896 | 0.004939 | 0.0085812 | 0.0019781 | 0.066379 | -0.0032835 | 0.067712 | -60.8231 | 61.8988 | -60.9879 | -60.9787 | 61.4822 | -0.07782 | 0.041199 | 0.045776 | 61.8668 | -61.0291 | -0.23346 | 0.018311 | -0.068664 | -0.2243 | -0.39825 | -0.27466 | -0.013733 | 0.16479 | 60.7956 | 60.8002 | 122.2366 | 122.6532 | -0.068664 | 122.6212 | 60.6766 | -0.27466 | 122.6532 | -0.068664 | 60.6766 | 122.2366 | 122.6212 | -122.8683 | -122.9095
325.9531 | 122.7356 | -60.7498 | 61.8668 | 0.15671 | 0.0075024 | 0.011999 | 0.0024053 | 0.070224 | -0.0011471 | 0.066003 | -60.8322 | 61.8851 | -61.0016 | -60.997 | 61.4822 | -0.054932 | 0.036621 | 0.059509 | 61.8805 | -61.0336 | -0.25177 | 0.018311 | -0.082397 | -0.24719 | -0.38452 | -0.28381 | 0.013733 | 0.16937 | 60.7864 | 60.8093 | 122.2321 | 122.6349 | -0.082397 | 122.6303 | 60.6949 | -0.28381 | 122.6349 | -0.082397 | 60.6949 | 122.2321 | 122.6303 | -122.8683 | -122.9004
326.9062 | 122.7219 | -60.759 | 61.8668 | 0.080414 | 0.006648 | 0.0068722 | 0.0004827 | 0.067661 | 0.00077554 | 0.069635 | -60.8459 | 61.9217 | -61.0016 | -60.9879 | 61.4777 | -0.045776 | 0.050354 | 0.050354 | 61.8759 | -61.0519 | -0.24262 | 0.054932 | -0.086975 | -0.22888 | -0.3891 | -0.29297 | 0.009156 | 0.15564 | 60.8093 | 60.8093 | 122.2366 | 122.6807 | -0.086975 | 122.6349 | 60.7132 | -0.29297 | 122.6807 | -0.086975 | 60.7132 | 122.2366 | 122.6349 | -122.8683 | -122.9187
327.9688 | 122.7676 | -60.7086 | 61.8713 | 0.042267 | 0.0051526 | 0.0072996 | 0.0019781 | 0.068088 | -0.0011471 | 0.070276 | -60.8047 | 61.9034 | -60.997 | -60.9238 | 61.5143 | 0.009155 | 0.032043 | 0.09613 | 61.8622 | -61.0199 | -0.28839 | 0.032043 | -0.096131 | -0.21515 | -0.35706 | -0.31128 | -0.009155 | 0.19226 | 60.7407 | 60.8047 | 122.2229 | 122.612 | -0.096131 | 122.5708 | 60.7178 | -0.31128 | 122.612 | -0.096131 | 60.7178 | 122.2229 | 122.5708 | -122.8683 | -122.8912
328.9062 | 122.7402 | -60.759 | 61.8851 | 0.080414 | 0.0053662 | 0.0055906 | 0.0011237 | 0.070224 | 0.00013454 | 0.068994 | -60.8322 | 61.908 | -61.0153 | -60.9695 | 61.4914 | -0.041199 | 0.064087 | 0.045776 | 61.9034 | -61.0565 | -0.25635 | 0.022888 | -0.073242 | -0.21057 | -0.39368 | -0.29755 | 0.01831 | 0.18311 | 60.8231 | 60.8047 | 122.2504 | 122.6669 | -0.073242 | 122.6624 | 60.7178 | -0.29755 | 122.6669 | -0.073242 | 60.7178 | 122.2504 | 122.6624 | -122.9004 | -122.9416
329.9688 | 122.8729 | -60.7086 | 61.821 | 0.27115 | 0.0010938 | 0.011999 | -0.0029351 | 0.067447 | 0.00013454 | 0.068994 | -60.7773 | 61.7889 | -60.9879 | -60.9055 | 61.5875 | 0.041199 | -0.1831 | 0.17853 | 61.7889 | -60.9695 | -0.27924 | -0.032044 | -0.068665 | -0.19684 | -0.23346 | -0.26093 | -0.032044 | 0.21057 | 60.5255 | 60.8871 | 122.2961 | 122.4976 | -0.068665 | 122.4976 | 60.7498 | -0.26093 | 122.4976 | -0.068665 | 60.7498 | 122.2961 | 122.4976 | -122.8088 | -122.7905
330.9062 | 122.7402 | -60.7361 | 61.8713 | -0.40024 | 0.0057934 | 0.006445 | 0.0024053 | 0.066806 | 0.00034814 | 0.069207 | -60.8826 | 61.8988 | -60.9924 | -60.9833 | 61.4685 | -0.07782 | 0.004578 | 0.054932 | 61.853 | -61.0794 | -0.25635 | 0.027466 | -0.14648 | -0.24719 | -0.40283 | -0.34332 | -0.018311 | 0.10986 | 60.7407 | 60.791 | 122.2046 | 122.6349 | -0.14648 | 122.5891 | 60.6583 | -0.34332 | 122.6349 | -0.14648 | 60.6583 | 122.2046 | 122.5891 | -122.8638 | -122.9507
331.9531 | 122.7859 | -60.7132 | 61.908 | -0.19424 | 0.0040846 | 0.0068722 | 0.0006965 | 0.066165 | 0.0024845 | 0.068567 | -60.8047 | 61.9263 | -60.9741 | -60.9238 | 61.5417 | 0.045776 | 0.1236 | 0.19684 | 61.8896 | -61.0291 | -0.26092 | 0.018311 | -0.091553 | -0.21057 | -0.36621 | -0.31586 | -0.018311 | 0.16937 | 60.8368 | 60.91 | 122.2549 | 122.6395 | -0.091553 | 122.6028 | 60.759 | -0.31586 | 122.6395 | -0.091553 | 60.759 | 122.2549 | 122.6028 | -122.8821 | -122.937
332.9062 | 122.8088 | -60.7086 | 61.8759 | 0.17197 | 0.004939 | 0.0058042 | -0.0001581 | 0.06702 | -7.9062e-05 | 0.067071 | -60.8276 | 61.8851 | -60.997 | -60.9375 | 61.5051 | -0.004578 | -0.10529 | 0.10529 | 61.853 | -61.0153 | -0.28839 | 0.009155 | -0.11902 | -0.22888 | -0.37079 | -0.3067 | -0.022889 | 0.16937 | 60.6033 | 60.8139 | 122.2137 | 122.5937 | -0.11902 | 122.5616 | 60.704 | -0.3067 | 122.5937 | -0.11902 | 60.704 | 122.2137 | 122.5616 | -122.8729 | -122.8912
333.9531 | 122.7631 | -60.7269 | 61.8988 | -0.11795 | 0.0038708 | 0.0032406 | 0.0006965 | 0.065525 | 0.00013454 | 0.067926 | -60.7956 | 61.8988 | -60.9604 | -60.9055 | 61.5372 | 0.054932 | 0.13733 | 0.18768 | 61.9034 | -61.0199 | -0.23346 | 0 | -0.068664 | -0.17853 | -0.36163 | -0.29297 | 0.004577 | 0.1648 | 60.8643 | 60.9146 | 122.2641 | 122.6257 | -0.068664 | 122.6303 | 60.7819 | -0.29297 | 122.6257 | -0.068664 | 60.7819 | 122.2641 | 122.6303 | -122.8592 | -122.9187
334.9062 | 122.8546 | -60.6857 | 61.8713 | 0.16434 | 0.0023756 | 0.010077 | -0.0054987 | 0.064029 | -0.0015745 | 0.068994 | -60.8185 | 61.7981 | -60.997 | -60.9192 | 61.5555 | 0.009155 | -0.10529 | 0.13733 | 61.8256 | -60.9833 | -0.31128 | -0.073242 | -0.13275 | -0.23346 | -0.31586 | -0.29755 | -0.045776 | 0.17853 | 60.5804 | 60.8231 | 122.2412 | 122.4838 | -0.13275 | 122.5113 | 60.6949 | -0.29755 | 122.4838 | -0.13275 | 60.6949 | 122.2412 | 122.5113 | -122.8683 | -122.8546
335.9688 | 122.7722 | -60.704 | 61.8805 | -0.049286 | 0.0072888 | 0.0090086 | 0.0053961 | 0.064456 | -0.0020017 | 0.067712 | -60.7681 | 61.8896 | -60.9879 | -60.8963 | 61.528 | 0.013733 | 0.013733 | 0.15564 | 61.8439 | -61.0474 | -0.28381 | 0.009155 | -0.064086 | -0.19226 | -0.35248 | -0.34332 | -0.036621 | 0.21973 | 60.7178 | 60.8597 | 122.2321 | 122.5937 | -0.064086 | 122.5479 | 60.7178 | -0.34332 | 122.5937 | -0.064086 | 60.7178 | 122.2321 | 122.5479 | -122.8683 | -122.9279
336.9062 | 122.7814 | -60.7498 | 61.8576 | 0.17197 | 0.0062208 | 0.011358 | 0.0019781 | 0.06702 | 0.00034814 | 0.070276 | -60.8322 | 61.8759 | -60.9833 | -60.9695 | 61.4868 | -0.059509 | -0.036621 | 0.050354 | 61.8668 | -61.0428 | -0.23346 | 0.018311 | -0.082397 | -0.21973 | -0.37079 | -0.29297 | 0.009155 | 0.15106 | 60.7132 | 60.8002 | 122.2366 | 122.6257 | -0.082397 | 122.6166 | 60.6903 | -0.29297 | 122.6257 | -0.082397 | 60.6903 | 122.2366 | 122.6166 | -122.8409 | -122.9004
337.9688 | 122.7997 | -60.704 | 61.8484 | 0.13382 | 0.004939 | 0.0077268 | 0.0011237 | 0.066165 | -0.0011471 | 0.067498 | -60.8322 | 61.8805 | -61.0153 | -60.9604 | 61.4914 | -0.036621 | -0.064087 | 0.054932 | 61.853 | -61.0245 | -0.31128 | 0.032043 | -0.12817 | -0.25635 | -0.35706 | -0.32043 | 0.004577 | 0.18311 | 60.64 | 60.759 | 122.1954 | 122.5845 | -0.12817 | 122.5571 | 60.6674 | -0.32043 | 122.5845 | -0.12817 | 60.6674 | 122.1954 | 122.5571 | -122.8638 | -122.8729
338.9062 | 122.85 | -60.6903 | 61.8347 | 0.1796 | 0.0045118 | 0.011145 | -0.0031489 | 0.06467 | 0.00077554 | 0.069635 | -60.7819 | 61.7706 | -60.9879 | -60.8826 | 61.5921 | 0.032043 | -0.18768 | 0.16479 | 61.8118 | -60.9833 | -0.29755 | -0.064087 | -0.091552 | -0.19226 | -0.24262 | -0.29297 | -0.022888 | 0.20599 | 60.5026 | 60.8551 | 122.2824 | 122.4609 | -0.091552 | 122.5021 | 60.7224 | -0.29297 | 122.4609 | -0.091552 | 60.7224 | 122.2824 | 122.5021 | -122.8226 | -122.818
339.9531 | 122.7356 | -60.7407 | 61.8622 | 0.16434 | 0.006648 | 0.0060178 | 0.0013373 | 0.066165 | 0.00034814 | 0.068353 | -60.8551 | 61.8484 | -61.0199 | -60.9467 | 61.4868 | -0.050354 | -0.041199 | 0.045776 | 61.821 | -61.0291 | -0.27923 | -0.013733 | -0.11444 | -0.20599 | -0.37537 | -0.28839 | -0.041199 | 0.16479 | 60.6995 | 60.7864 | 122.2275 | 122.5891 | -0.11444 | 122.5616 | 60.6903 | -0.28839 | 122.5891 | -0.11444 | 60.6903 | 122.2275 | 122.5616 | -122.8821 | -122.8912
340.9062 | 122.8638 | -60.7132 | 61.8347 | 0.24063 | 0.0070752 | 0.0083676 | 0.0009101 | 0.066806 | 0.0018435 | 0.067712 | -60.7956 | 61.8484 | -60.9879 | -60.9146 | 61.5326 | -0.009155 | -0.15106 | 0.10529 | 61.821 | -61.0153 | -0.27466 | 0.013733 | -0.082397 | -0.20142 | -0.30212 | -0.30212 | -0.013733 | 0.19226 | 60.5621 | 60.8185 | 122.2458 | 122.5616 | -0.082397 | 122.5342 | 60.704 | -0.30212 | 122.5616 | -0.082397 | 60.704 | 122.2458 | 122.5342 | -122.8226 | -122.85
341.9531 | 122.7539 | -60.7407 | 61.8896 | 0.019379 | 0.0055798 | 0.0087948 | 0.0047553 | 0.068302 | -7.9062e-05 | 0.06643 | -60.7819 | 61.908 | -60.9924 | -60.9329 | 61.5189 | -0.027466 | 0.032043 | 0.10529 | 61.8622 | -61.0199 | -0.25177 | 0.018311 | -0.041198 | -0.19226 | -0.37079 | -0.27923 | -0.027465 | 0.21057 | 60.7727 | 60.8459 | 122.2595 | 122.6486 | -0.041198 | 122.6028 | 60.7132 | -0.27923 | 122.6486 | -0.041198 | 60.7132 | 122.2595 | 122.6028 | -122.8821 | -122.9095
342.9062 | 122.7539 | -60.7315 | 61.853 | 0.20248 | 0.0057934 | 0.010931 | 0.0043281 | 0.066593 | 0.00034814 | 0.067926 | -60.8322 | 61.853 | -61.0062 | -60.9558 | 61.4777 | -0.050354 | -0.009155 | 0.036621 | 61.8805 | -61.0336 | -0.27466 | 0 | -0.10071 | -0.2243 | -0.37537 | -0.30212 | 0.027466 | 0.17395 | 60.7224 | 60.7681 | 122.2092 | 122.5845 | -0.10071 | 122.612 | 60.6812 | -0.30212 | 122.5845 | -0.10071 | 60.6812 | 122.2092 | 122.612 | -122.8592 | -122.8867
343.9688 | 122.731 | -60.7132 | 61.8622 | 0.15671 | 0.0045118 | 0.011786 | 0.0086005 | 0.06702 | -0.0034971 | 0.066858 | -60.8368 | 61.853 | -61.0016 | -60.7498 | 61.4914 | -0.13733 | 0.082397 | 0.11444 | 61.8759 | -61.0245 | -0.28839 | -0.009156 | -0.1236 | -0.036621 | -0.37079 | -0.31128 | 0.013733 | 0.16479 | 60.7956 | 60.8276 | 122.2046 | 122.5662 | -0.1236 | 122.5891 | 60.5759 | -0.31128 | 122.5662 | -0.1236 | 60.5759 | 122.2046 | 122.5891 | -122.8638 | -122.8867
344.9219 | 122.9004 | -60.6674 | 61.8484 | 0.52292 | 0.002162 | 0.0072996 | -0.0076349 | 0.066379 | 0.0012027 | 0.071344 | -60.6491 | 61.7935 | -60.9558 | -60.8231 | 61.6653 | 0.16937 | -0.054932 | 0.31128 | 61.853 | -60.965 | -0.28839 | -0.054932 | 0.01831 | -0.15564 | -0.18311 | -0.29755 | 0.004577 | 0.3067 | 60.6125 | 60.9787 | 122.3328 | 122.4609 | 0.01831 | 122.5204 | 60.8368 | -0.29755 | 122.4609 | 0.01831 | 60.8368 | 122.3328 | 122.5204 | -122.8043 | -122.8134
345.9531 | 122.7264 | -60.7361 | 61.8668 | 0.20248 | 0.0051526 | 0.011358 | 0.0051825 | 0.065525 | -0.00071986 | 0.068139 | -60.8459 | 61.8713 | -60.997 | -60.9833 | 61.4639 | -0.064087 | 0.032043 | 0.036621 | 61.8347 | -61.0336 | -0.26093 | 0.004578 | -0.10986 | -0.24719 | -0.40283 | -0.29755 | -0.032043 | 0.15106 | 60.7681 | 60.7727 | 122.2 | 122.6074 | -0.10986 | 122.5708 | 60.672 | -0.29755 | 122.6074 | -0.10986 | 60.672 | 122.2 | 122.5708 | -122.8638 | -122.9004
346.9062 | 122.8775 | -60.6857 | 61.8347 | 0.21011 | 0.00323 | 0.0068722 | -0.0018671 | 0.066593 | 0.0014163 | 0.067498 | -60.7544 | 61.8027 | -60.9604 | -60.8688 | 61.6058 | 0.045776 | -0.17853 | 0.16022 | 61.8118 | -60.997 | -0.27466 | -0.032044 | -0.068665 | -0.1831 | -0.22888 | -0.31128 | -0.022888 | 0.20599 | 60.5072 | 60.8459 | 122.2916 | 122.4884 | -0.068665 | 122.4976 | 60.7315 | -0.31128 | 122.4884 | -0.068665 | 60.7315 | 122.2916 | 122.4976 | -122.7951 | -122.8317
347.9531 | 122.7814 | -60.704 | 61.8713 | -0.9343 | 0.0038708 | 0.0087948 | 0.0068915 | 0.06467 | 0.00077554 | 0.066858 | -60.704 | 61.8851 | -60.9741 | -60.8597 | 61.5555 | 0.045776 | 0.009155 | 0.17395 | 61.853 | -60.9924 | -0.27008 | 0.013733 | 0 | -0.15564 | -0.31586 | -0.28839 | -0.018311 | 0.27008 | 60.7132 | 60.878 | 122.2595 | 122.5891 | 0 | 122.5571 | 60.7498 | -0.28839 | 122.5891 | 0 | 60.7498 | 122.2595 | 122.5571 | -122.8455 | -122.8638
348.9062 | 122.8638 | -60.6949 | 61.8118 | 0.095673 | 0.0045118 | 0.0096494 | -0.0003717 | 0.066165 | -0.00093346 | 0.06878 | -60.7498 | 61.7935 | -60.9604 | -60.8597 | 61.5967 | 0.045776 | -0.18768 | 0.15564 | 61.8301 | -60.997 | -0.2655 | -0.018311 | -0.054932 | -0.16479 | -0.21515 | -0.30212 | 0.01831 | 0.21057 | 60.5072 | 60.8505 | 122.2916 | 122.4884 | -0.054932 | 122.525 | 60.7407 | -0.30212 | 122.4884 | -0.054932 | 60.7407 | 122.2916 | 122.525 | -122.7722 | -122.8088
349.9688 | 122.8317 | -60.7178 | 61.8393 | 0.233 | 0.0060072 | 0.010717 | 0.0004827 | 0.065952 | -0.0024289 | 0.067712 | -60.8185 | 61.8027 | -61.0291 | -60.91 | 61.5463 | -0.013733 | -0.1236 | 0.10071 | 61.821 | -60.9879 | -0.31128 | -0.036621 | -0.10071 | -0.19226 | -0.29297 | -0.27008 | -0.01831 | 0.21057 | 60.5942 | 60.8185 | 122.2641 | 122.5204 | -0.10071 | 122.5388 | 60.704 | -0.27008 | 122.5204 | -0.10071 | 60.704 | 122.2641 | 122.5388 | -122.8683 | -122.8271
350.9062 | 122.8729 | -60.6949 | 61.8073 | 0.011749 | 0.0051526 | 0.0072996 | -0.0010125 | 0.065311 | -0.0013609 | 0.069421 | -60.7773 | 61.7981 | -60.9924 | -60.878 | 61.5784 | 0.041199 | -0.17395 | 0.15106 | 61.7981 | -60.9879 | -0.29755 | -0.009155 | -0.082398 | -0.18311 | -0.22888 | -0.29297 | -0.009155 | 0.21515 | 60.5209 | 60.8459 | 122.2733 | 122.493 | -0.082398 | 122.493 | 60.7361 | -0.29297 | 122.493 | -0.082398 | 60.7361 | 122.2733 | 122.493 | -122.7997 | -122.7951
351.9688 | 122.7585 | -60.7407 | 61.8759 | -0.072174 | 0.0042982 | 0.008154 | 0.0039007 | 0.065952 | -7.9062e-05 | 0.069207 | -60.8414 | 61.8622 | -61.0107 | -60.9604 | 61.496 | -0.050354 | -0.032043 | 0.054932 | 61.8484 | -61.0107 | -0.27008 | -0.013733 | -0.10071 | -0.21973 | -0.37994 | -0.27008 | -0.027466 | 0.16937 | 60.7086 | 60.7956 | 122.2366 | 122.6028 | -0.10071 | 122.5891 | 60.6903 | -0.27008 | 122.6028 | -0.10071 | 60.6903 | 122.2366 | 122.5891 | -122.8867 | -122.8867
352.9062 | 122.8363 | -60.6628 | 61.8164 | 0.20248 | 0.00088016 | 0.0045224 | -0.0018671 | 0.064029 | 0.00056194 | 0.067926 | -60.7819 | 61.7844 | -60.9879 | -60.8963 | 61.5875 | 0.041199 | -0.17395 | 0.15564 | 61.8027 | -60.9741 | -0.32501 | -0.032043 | -0.11902 | -0.23346 | -0.22888 | -0.31128 | -0.013733 | 0.20599 | 60.4889 | 60.8185 | 122.2504 | 122.4472 | -0.11902 | 122.4655 | 60.704 | -0.31128 | 122.4472 | -0.11902 | 60.704 | 122.2504 | 122.4655 | -122.8043 | -122.7905
353.9688 | 122.8134 | -60.7086 | 61.8301 | 0.13382 | 0.0072888 | 0.0075132 | 0.0017645 | 0.065738 | -0.00029266 | 0.068353 | -60.8322 | 61.8347 | -60.997 | -60.9421 | 61.5234 | -0.041199 | -0.09613 | 0.073242 | 61.8256 | -61.0428 | -0.28839 | 0.004578 | -0.1236 | -0.23346 | -0.3067 | -0.33417 | -0.004577 | 0.16479 | 60.6125 | 60.7819 | 122.2321 | 122.5433 | -0.1236 | 122.5342 | 60.6674 | -0.33417 | 122.5433 | -0.1236 | 60.6674 | 122.2321 | 122.5342 | -122.8271 | -122.8729
354.9062 | 122.8775 | -60.6903 | 61.8439 | -0.026398 | 0.0053662 | 0.003027 | -0.0067803 | 0.063602 | 0.0016299 | 0.068139 | -60.8139 | 61.7798 | -60.9833 | -60.878 | 61.6196 | 0.091553 | -0.07782 | 0.23804 | 61.8393 | -60.9741 | -0.29297 | -0.064087 | -0.1236 | -0.18768 | -0.2243 | -0.28381 | -0.004578 | 0.16937 | 60.6125 | 60.9283 | 122.3099 | 122.4701 | -0.1236 | 122.5296 | 60.7819 | -0.28381 | 122.4701 | -0.1236 | 60.7819 | 122.3099 | 122.5296 | -122.8271 | -122.818
355.9688 | 122.7997 | -60.7132 | 61.8668 | 0.17197 | 0.0040846 | 0.0051632 | 0.0047553 | 0.065738 | -0.0013609 | 0.068139 | -60.8368 | 61.8484 | -61.0199 | -60.9512 | 61.496 | -0.054932 | -0.073242 | 0.059509 | 61.8256 | -60.997 | -0.3067 | -0.01831 | -0.1236 | -0.23804 | -0.37079 | -0.28381 | -0.041198 | 0.1831 | 60.64 | 60.7727 | 122.2092 | 122.5616 | -0.1236 | 122.5388 | 60.6583 | -0.28381 | 122.5616 | -0.1236 | 60.6583 | 122.2092 | 122.5388 | -122.8867 | -122.8638
356.9062 | 122.8363 | -60.6903 | 61.8576 | 0.20248 | 0.0051526 | 0.0070858 | 0.0021917 | 0.066165 | -0.0013609 | 0.066644 | -60.8139 | 61.8484 | -60.9924 | -60.9146 | 61.5326 | -0.022888 | -0.11444 | 0.086975 | 61.8164 | -61.0336 | -0.30212 | -0.009155 | -0.1236 | -0.2243 | -0.32501 | -0.34332 | -0.041199 | 0.17853 | 60.5759 | 60.7773 | 122.2229 | 122.5388 | -0.1236 | 122.5067 | 60.6674 | -0.34332 | 122.5388 | -0.1236 | 60.6674 | 122.2229 | 122.5067 | -122.85 | -122.8912
357.9531 | 122.7585 | -60.7132 | 61.8942 | 0.59158 | 0.0060072 | 0.004736 | 0.0051825 | 0.066165 | -0.00071986 | 0.068353 | -60.8643 | 61.8484 | -60.9924 | -60.9741 | 61.4822 | -0.059509 | -0.004578 | 0.027466 | 61.8668 | -61.0062 | -0.27924 | -0.045776 | -0.15106 | -0.26092 | -0.41199 | -0.29297 | -0.027466 | 0.12817 | 60.7086 | 60.7407 | 122.1954 | 122.5616 | -0.15106 | 122.58 | 60.6537 | -0.29297 | 122.5616 | -0.15106 | 60.6537 | 122.1954 | 122.58 | -122.8867 | -122.9004
358.9062 | 122.8455 | -60.6766 | 61.8347 | 0.16434 | 0.0034436 | 0.009863 | -0.0027215 | 0.065952 | -0.0028561 | 0.069207 | -60.7773 | 61.7798 | -60.9741 | -60.9009 | 61.5784 | 0.036621 | -0.15564 | 0.15564 | 61.8118 | -60.9787 | -0.29755 | -0.054932 | -0.10071 | -0.2243 | -0.25635 | -0.30212 | -0.022888 | 0.19684 | 60.5209 | 60.8322 | 122.2549 | 122.4564 | -0.10071 | 122.4884 | 60.7132 | -0.30212 | 122.4564 | -0.10071 | 60.7132 | 122.2549 | 122.4884 | -122.8088 | -122.8134
359.9688 | 122.8592 | -60.672 | 61.8439 | -0.049286 | 2.5564e-05 | 0.0068722 | -0.0048577 | 0.061893 | -7.9062e-05 | 0.068994 | -60.7819 | 61.7935 | -60.9558 | -60.8551 | 61.6425 | 0.10529 | -0.07782 | 0.23346 | 61.821 | -60.9558 | -0.28381 | -0.050354 | -0.10986 | -0.18311 | -0.20142 | -0.28381 | -0.022888 | 0.17395 | 60.5942 | 60.9055 | 122.3145 | 122.4655 | -0.10986 | 122.493 | 60.7773 | -0.28381 | 122.4655 | -0.10986 | 60.7773 | 122.3145 | 122.493 | -122.7997 | -122.7997
360.9062 | 122.8729 | -60.6766 | 61.8668 | 0.26352 | 0.0055798 | 0.0079404 | 0.0051825 | 0.06467 | -0.00071986 | 0.066644 | -60.7544 | 61.8027 | -60.9467 | -60.6857 | 61.6241 | 0.032043 | -0.1831 | 0.20599 | 61.7706 | -60.9787 | -0.27008 | -0.064087 | -0.07782 | -0.009155 | -0.24261 | -0.30212 | -0.09613 | 0.19226 | 60.4935 | 60.8826 | 122.3007 | 122.4792 | -0.07782 | 122.4472 | 60.7086 | -0.30212 | 122.4792 | -0.07782 | 60.7086 | 122.3007 | 122.4472 | -122.8134 | -122.8455
361.9531 | 122.7676 | -60.7086 | 61.8805 | 0.042267 | 0.0064344 | 0.010717 | 0.0077459 | 0.065525 | -0.0024289 | 0.066644 | -60.7819 | 61.8576 | -60.997 | -60.91 | 61.5143 | -0.013733 | 0 | 0.10529 | 61.853 | -61.0245 | -0.28839 | -0.022888 | -0.073242 | -0.20142 | -0.36621 | -0.31586 | -0.027466 | 0.21515 | 60.7086 | 60.8139 | 122.2229 | 122.5662 | -0.073242 | 122.5616 | 60.6949 | -0.31586 | 122.5662 | -0.073242 | 60.6949 | 122.2229 | 122.5616 | -122.8775 | -122.905
362.9062 | 122.8821 | -60.6537 | 61.8439 | -0.087433 | 0.00023916 | 0.0077268 | -0.0040033 | 0.063816 | -0.0022153 | 0.068567 | -60.7681 | 61.7798 | -60.9467 | -60.8231 | 61.6287 | 0.13275 | -0.07782 | 0.28381 | 61.8301 | -60.9329 | -0.29297 | -0.064087 | -0.11444 | -0.16937 | -0.21515 | -0.27923 | -0.013733 | 0.17853 | 60.5759 | 60.9375 | 122.2824 | 122.4335 | -0.11444 | 122.4838 | 60.7864 | -0.27923 | 122.4335 | -0.11444 | 60.7864 | 122.2824 | 122.4838 | -122.7905 | -122.7768
363.9531 | 122.7676 | -60.7178 | 61.8988 | 0.0041197 | 0.0051526 | 0.0096494 | 0.0079595 | 0.063175 | -0.0020017 | 0.067071 | -60.7681 | 61.8805 | -60.9741 | -60.8871 | 61.5234 | 0.018311 | 0.009155 | 0.11902 | 61.8393 | -61.0107 | -0.25635 | -0.018311 | -0.050354 | -0.16937 | -0.37537 | -0.29297 | -0.05951 | 0.20599 | 60.7269 | 60.8368 | 122.2412 | 122.5983 | -0.050354 | 122.5571 | 60.7361 | -0.29297 | 122.5983 | -0.050354 | 60.7361 | 122.2412 | 122.5571 | -122.8729 | -122.9095
364.9219 | 122.9828 | -60.6491 | 61.9308 | -0.10269 | 0.002162 | 0.010077 | -0.0037897 | 0.062534 | -0.0030697 | 0.066858 | -60.7224 | 61.7798 | -60.9467 | -60.7864 | 61.6791 | 0.14191 | -0.064087 | 0.30212 | 61.8393 | -60.9467 | -0.29755 | -0.15106 | -0.073242 | -0.13733 | -0.25177 | -0.29755 | -0.091553 | 0.2243 | 60.585 | 60.9512 | 122.3282 | 122.4289 | -0.073242 | 122.4884 | 60.791 | -0.29755 | 122.4289 | -0.073242 | 60.791 | 122.3282 | 122.4884 | -122.8775 | -122.8775
365.9688 | 122.7448 | -60.7269 | 61.8942 | 0.11856 | 0.0060072 | 0.0070858 | 0.0062507 | 0.065952 | -0.0024289 | 0.068353 | -60.8185 | 61.8759 | -61.0016 | -60.9741 | 61.4777 | -0.054932 | 0.041199 | 0.068665 | 61.8759 | -61.0199 | -0.27466 | -0.01831 | -0.091552 | -0.24719 | -0.41657 | -0.29297 | -0.01831 | 0.18311 | 60.7681 | 60.7956 | 122.2046 | 122.6028 | -0.091552 | 122.6028 | 60.672 | -0.29297 | 122.6028 | -0.091552 | 60.672 | 122.2046 | 122.6028 | -122.8958 | -122.9141
366.9062 | 122.8867 | -60.6903 | 61.8713 | 0.29404 | 0.0051526 | 0.0049496 | 0.0021917 | 0.068088 | -0.0026425 | 0.070276 | -60.7452 | 61.8073 | -60.9558 | -60.9375 | 61.377 | -0.036621 | -0.036621 | 0.2655 | 61.8027 | -60.9741 | -0.2655 | -0.064087 | -0.054931 | -0.24719 | -0.49439 | -0.28381 | -0.068665 | 0.21057 | 60.6537 | 60.9558 | 122.0673 | 122.4976 | -0.054931 | 122.493 | 60.6537 | -0.28381 | 122.4976 | -0.054931 | 60.6537 | 122.0673 | 122.493 | -122.8271 | -122.8455
367.9219 | 122.8363 | -60.6766 | 61.8713 | -0.17136 | 0.0023756 | 0.004736 | -0.0027215 | 0.060611 | -0.00029266 | 0.071344 | -60.7544 | 61.8027 | -60.9467 | -60.8322 | 61.6104 | 0.14648 | 0.022888 | 0.2655 | 61.8484 | -60.9604 | -0.27008 | -0.068665 | -0.07782 | -0.15564 | -0.26093 | -0.28381 | -0.022888 | 0.19226 | 60.6995 | 60.9421 | 122.287 | 122.4792 | -0.07782 | 122.525 | 60.8231 | -0.28381 | 122.4792 | -0.07782 | 60.8231 | 122.287 | 122.525 | -122.818 | -122.8317
368.9062 | 122.8821 | -60.6995 | 61.8347 | 0.15671 | 0.0038708 | 0.0070858 | 0.0047553 | 0.066593 | -0.0011471 | 0.066858 | -60.7636 | 61.7935 | -60.9741 | -60.8551 | 61.5875 | 0.050354 | -0.19226 | 0.16022 | 61.7935 | -61.0062 | -0.27466 | -0.041199 | -0.064087 | -0.15564 | -0.24719 | -0.3067 | -0.041199 | 0.21057 | 60.5072 | 60.8597 | 122.287 | 122.493 | -0.064087 | 122.493 | 60.7498 | -0.3067 | 122.493 | -0.064087 | 60.7498 | 122.287 | 122.493 | -122.8088 | -122.8409
369.9062 | 122.85 | -60.7086 | 61.8439 | 0.24826 | 0.0038708 | 0.0090086 | -0.0010125 | 0.063175 | 0.00013454 | 0.070062 | -60.7727 | 61.7981 | -60.9879 | -60.8826 | 61.5921 | 0.022888 | -0.16022 | 0.13733 | 61.7935 | -60.9604 | -0.27924 | -0.045776 | -0.064087 | -0.17395 | -0.25177 | -0.25177 | -0.050354 | 0.21515 | 60.5484 | 60.8459 | 122.3007 | 122.5067 | -0.064087 | 122.5021 | 60.7315 | -0.25177 | 122.5067 | -0.064087 | 60.7315 | 122.3007 | 122.5021 | -122.8317 | -122.8043
370.9062 | 122.818 | -60.7224 | 61.8668 | 0.16434 | 0.0062208 | 0.009863 | 0.0060369 | 0.06467 | -0.00071986 | 0.070489 | -60.8185 | 61.853 | -60.9924 | -60.9421 | 61.4868 | -0.045776 | -0.068665 | 0.050354 | 61.821 | -61.0382 | -0.27008 | -0.013733 | -0.09613 | -0.21973 | -0.37994 | -0.31586 | -0.045776 | 0.17395 | 60.6537 | 60.7727 | 122.2092 | 122.5754 | -0.09613 | 122.5433 | 60.6766 | -0.31586 | 122.5754 | -0.09613 | 60.6766 | 122.2092 | 122.5433 | -122.8592 | -122.905
371.9062 | 122.85 | -60.7086 | 61.821 | 0.233 | 0.0057934 | 0.0062314 | 0.0036871 | 0.066379 | 0.0012027 | 0.067498 | -60.7773 | 61.8393 | -60.9879 | -60.8734 | 61.5875 | 0.022888 | -0.14648 | 0.12817 | 61.7798 | -60.9787 | -0.27924 | 0.01831 | -0.068665 | -0.16479 | -0.23346 | -0.27008 | -0.041199 | 0.21057 | 60.5621 | 60.8368 | 122.2961 | 122.5479 | -0.068665 | 122.4884 | 60.7315 | -0.27008 | 122.5479 | -0.068665 | 60.7315 | 122.2961 | 122.4884 | -122.8088 | -122.7997
372.9219 | 122.8317 | -60.6857 | 61.8713 | -0.21713 | 0.0019482 | 0.0028134 | -0.0003717 | 0.063602 | -0.0020017 | 0.067285 | -60.7544 | 61.821 | -60.9512 | -60.8597 | 61.6058 | 0.12817 | 0.036621 | 0.27466 | 61.821 | -60.9695 | -0.2655 | -0.050354 | -0.068665 | -0.17395 | -0.2655 | -0.28381 | -0.050354 | 0.19684 | 60.7224 | 60.9604 | 122.2916 | 122.5067 | -0.068665 | 122.5067 | 60.8139 | -0.28381 | 122.5067 | -0.068665 | 60.8139 | 122.2916 | 122.5067 | -122.8226 | -122.8409
373.9688 | 122.7905 | -60.704 | 61.8942 | -0.17899 | 0.0070752 | 0.0094358 | 0.0043281 | 0.06467 | -0.00050626 | 0.069207 | -60.7864 | 61.8851 | -60.9741 | -60.8734 | 61.5692 | 0.054932 | 0.11444 | 0.19684 | 61.8622 | -61.0062 | -0.27008 | -0.009155 | -0.082397 | -0.16937 | -0.32501 | -0.30212 | -0.032043 | 0.18768 | 60.8185 | 60.9009 | 122.2733 | 122.5891 | -0.082397 | 122.5662 | 60.759 | -0.30212 | 122.5891 | -0.082397 | 60.759 | 122.2733 | 122.5662 | -122.8683 | -122.9004
374.9062 | 122.8317 | -60.6857 | 61.821 | 0.21011 | 0.004939 | 0.0062314 | -0.0025079 | 0.063602 | -0.0011471 | 0.069207 | -60.791 | 61.7661 | -60.9695 | -60.9055 | 61.5829 | 0.041199 | -0.13275 | 0.14191 | 61.7981 | -60.965 | -0.28381 | -0.054932 | -0.10529 | -0.21973 | -0.23804 | -0.27924 | -0.022888 | 0.17853 | 60.553 | 60.8276 | 122.2687 | 122.4518 | -0.10529 | 122.4838 | 60.7269 | -0.27924 | 122.4518 | -0.10529 | 60.7269 | 122.2687 | 122.4838 | -122.7905 | -122.7859
375.9062 | 122.8683 | -60.704 | 61.8347 | 0.27115 | 0.0047254 | 0.0072996 | 0.0047553 | 0.064884 | -0.00093346 | 0.070489 | -60.7681 | 61.8301 | -60.9695 | -60.8688 | 61.5875 | 0.041199 | -0.17853 | 0.13275 | 61.7706 | -60.9924 | -0.2655 | -0.004578 | -0.064086 | -0.16479 | -0.24719 | -0.28839 | -0.064087 | 0.20142 | 60.5255 | 60.8368 | 122.2916 | 122.5342 | -0.064086 | 122.4747 | 60.7452 | -0.28839 | 122.5342 | -0.064086 | 60.7452 | 122.2916 | 122.4747 | -122.8043 | -122.8271
376.9688 | 122.7722 | -60.7086 | 61.8896 | -0.026398 | 0.004939 | 0.009863 | 0.0047553 | 0.064884 | -0.0026425 | 0.067498 | -60.7819 | 61.8942 | -60.9833 | -60.8826 | 61.528 | 0.022888 | 0.018311 | 0.14648 | 61.8484 | -61.0062 | -0.27466 | 0.004578 | -0.073242 | -0.17395 | -0.36163 | -0.29755 | -0.041198 | 0.20142 | 60.7269 | 60.8551 | 122.2366 | 122.6028 | -0.073242 | 122.5571 | 60.7315 | -0.29755 | 122.6028 | -0.073242 | 60.7315 | 122.2366 | 122.5571 | -122.8729 | -122.8958
377.9219 | 122.7402 | -60.7361 | 61.8988 | 0.034637 | 0.0055798 | 0.0087948 | 0.0047553 | 0.066806 | -0.00093346 | 0.067498 | -60.8047 | 61.8942 | -61.0107 | -60.9238 | 61.4868 | -0.022888 | 0.027466 | 0.09613 | 61.8576 | -61.0016 | -0.27466 | -0.004578 | -0.068665 | -0.18768 | -0.41199 | -0.2655 | -0.041199 | 0.20599 | 60.7635 | 60.8322 | 122.2229 | 122.6303 | -0.068665 | 122.5937 | 60.7132 | -0.2655 | 122.6303 | -0.068665 | 60.7132 | 122.2229 | 122.5937 | -122.9095 | -122.9004
378.9531 | 122.7631 | -60.7269 | 61.8805 | 0.011749 | 0.0042982 | 0.0083676 | 0.0028327 | 0.067874 | -0.0011471 | 0.068353 | -60.8597 | 61.8622 | -60.9924 | -60.9512 | 61.5005 | -0.059509 | -0.009155 | 0.032043 | 61.8393 | -61.0016 | -0.2655 | -0.01831 | -0.13275 | -0.2243 | -0.37994 | -0.27466 | -0.041199 | 0.13275 | 60.7178 | 60.759 | 122.2275 | 122.5891 | -0.13275 | 122.5662 | 60.6674 | -0.27466 | 122.5891 | -0.13275 | 60.6674 | 122.2275 | 122.5662 | -122.8729 | -122.8821
379.9062 | 122.8683 | -60.672 | 61.8668 | -0.041657 | 0.0017346 | 0.0017454 | -0.0061395 | 0.06467 | -0.0011471 | 0.071557 | -60.8002 | 61.821 | -60.9833 | -60.8505 | 61.6333 | 0.11902 | -0.07782 | 0.2655 | 61.8256 | -60.9375 | -0.31128 | -0.045776 | -0.12817 | -0.17853 | -0.23346 | -0.2655 | -0.041198 | 0.1831 | 60.5942 | 60.9375 | 122.3053 | 122.493 | -0.12817 | 122.4976 | 60.791 | -0.2655 | 122.493 | -0.12817 | 60.791 | 122.3053 | 122.4976 | -122.85 | -122.8043
380.9531 | 122.7768 | -60.7178 | 61.8576 | 0.14145 | 0.0045118 | 0.004736 | 0.0028327 | 0.066165 | 0.00056194 | 0.067498 | -60.8231 | 61.853 | -60.997 | -60.9329 | 61.5005 | -0.041199 | -0.068665 | 0.068665 | 61.8118 | -61.0199 | -0.27924 | -0.004578 | -0.10529 | -0.21515 | -0.35706 | -0.30212 | -0.045776 | 0.17395 | 60.6491 | 60.7864 | 122.2183 | 122.5708 | -0.10529 | 122.5296 | 60.6766 | -0.30212 | 122.5708 | -0.10529 | 60.6766 | 122.2183 | 122.5296 | -122.8546 | -122.8775
381.9062 | 122.8317 | -60.6857 | 61.8439 | 0.13382 | 0.0042982 | 0.004736 | -0.0029351 | 0.065525 | 0.00034814 | 0.066644 | -60.8093 | 61.8073 | -60.965 | -60.9283 | 61.5555 | 0.018311 | -0.09613 | 0.16022 | 61.8347 | -60.9695 | -0.27924 | -0.036621 | -0.1236 | -0.24262 | -0.28839 | -0.28381 | -0.009155 | 0.15564 | 60.5896 | 60.8459 | 122.2412 | 122.493 | -0.1236 | 122.5204 | 60.704 | -0.28381 | 122.493 | -0.1236 | 60.704 | 122.2412 | 122.5204 | -122.8088 | -122.8134
382.9844 | 122.8088 | -60.704 | 61.8896 | -0.10269 | 0.0064344 | 0.004736 | 0.0032599 | 0.064884 | 0.00034814 | 0.067926 | -60.7636 | 61.8942 | -60.9512 | -60.8734 | 61.5784 | 0.086975 | 0.073242 | 0.20142 | 61.8439 | -60.9879 | -0.24719 | 0.004578 | -0.059509 | -0.16937 | -0.31128 | -0.28381 | -0.045776 | 0.18768 | 60.7773 | 60.9055 | 122.2824 | 122.5983 | -0.059509 | 122.5479 | 60.791 | -0.28381 | 122.5983 | -0.059509 | 60.791 | 122.2824 | 122.5479 | -122.8409 | -122.8775
383.9062 | 122.8729 | -60.6903 | 61.8256 | 0.18723 | 0.004939 | 0.0068722 | 0.0006965 | 0.064456 | -0.0020017 | 0.068567 | -60.7636 | 61.8027 | -60.9787 | -60.8688 | 61.5784 | 0.054932 | -0.18768 | 0.16479 | 61.7981 | -60.965 | -0.28839 | -0.022889 | -0.073242 | -0.17853 | -0.24719 | -0.27466 | -0.027466 | 0.21515 | 60.5026 | 60.8551 | 122.2687 | 122.493 | -0.073242 | 122.4884 | 60.7452 | -0.27466 | 122.493 | -0.073242 | 60.7452 | 122.2687 | 122.4884 | -122.8043 | -122.7905
384.9688 | 122.8317 | -60.7132 | 61.8576 | -0.041657 | 0.002162 | 0.0058042 | -0.0046441 | 0.064243 | -7.9062e-05 | 0.067071 | -60.8047 | 61.7981 | -60.9741 | -60.8917 | 61.5829 | 0.07782 | -0.07782 | 0.19684 | 61.8073 | -60.9833 | -0.26092 | -0.059509 | -0.091553 | -0.17853 | -0.27466 | -0.27008 | -0.050354 | 0.16937 | 60.6354 | 60.91 | 122.2961 | 122.5113 | -0.091553 | 122.5204 | 60.791 | -0.27008 | 122.5113 | -0.091553 | 60.791 | 122.2961 | 122.5204 | -122.8317 | -122.8409
385.9062 | 122.9141 | -60.6995 | 61.7798 | 0.15671 | 0.0075024 | 0.0090086 | 0.0030463 | 0.063602 | -0.00093346 | 0.067712 | -60.791 | 61.7844 | -60.9833 | -60.8688 | 61.5692 | 0.041199 | -0.18768 | 0.15106 | 61.7706 | -60.9833 | -0.28381 | 0.004578 | -0.091553 | -0.16937 | -0.21057 | -0.28381 | -0.009155 | 0.19226 | 60.5118 | 60.8505 | 122.2687 | 122.4838 | -0.091553 | 122.4701 | 60.7407 | -0.28381 | 122.4838 | -0.091553 | 60.7407 | 122.2687 | 122.4701 | -122.7631 | -122.7631
386.9688 | 122.8867 | -60.704 | 61.8347 | -0.072174 | 0.0051526 | 0.005377 | -0.0010125 | 0.056766 | -0.0043515 | 0.067498 | -60.7178 | 61.8256 | -60.9421 | -60.7956 | 61.3358 | -0.1236 | 0.013733 | 0.32044 | 61.7798 | -60.9879 | -0.23804 | -0.009155 | -0.013732 | -0.091552 | -0.49896 | -0.28381 | -0.054932 | 0.22431 | 60.7178 | 61.0245 | 122.0398 | 122.5296 | -0.013732 | 122.4838 | 60.5804 | -0.28381 | 122.5296 | -0.013732 | 60.5804 | 122.0398 | 122.4838 | -122.7768 | -122.8226
387.9219 | 122.8638 | -60.6857 | 61.8484 | 0.24826 | 0.0038708 | 0.0032406 | -0.0001581 | 0.063602 | -0.0022153 | 0.066217 | -60.7681 | 61.7661 | -60.9924 | -60.8688 | 61.6058 | 0.059509 | -0.1831 | 0.1831 | 61.7615 | -60.9741 | -0.3067 | -0.082398 | -0.082397 | -0.1831 | -0.24262 | -0.28839 | -0.086975 | 0.22431 | 60.5026 | 60.8688 | 122.2916 | 122.4518 | -0.082397 | 122.4472 | 60.7452 | -0.28839 | 122.4518 | -0.082397 | 60.7452 | 122.2916 | 122.4472 | -122.8409 | -122.8226
388.9688 | 122.7859 | -60.6766 | 61.8759 | -0.026398 | 0.006648 | 0.0068722 | 0.0073187 | 0.064456 | -0.0020017 | 0.068567 | -60.9146 | 61.7981 | -61.0199 | -60.8826 | 61.5417 | 0.064087 | 0.027466 | 0.21515 | 61.853 | -60.9879 | -0.34332 | -0.07782 | -0.23804 | -0.20599 | -0.33417 | -0.31128 | -0.022889 | 0.10529 | 60.704 | 60.8917 | 122.2183 | 122.4747 | -0.23804 | 122.5296 | 60.7407 | -0.31128 | 122.4747 | -0.23804 | 60.7407 | 122.2183 | 122.5296 | -122.8958 | -122.8638
389.9219 | 122.8088 | -60.6857 | 61.908 | -0.24765 | 0.00088016 | 0.006445 | -0.0001581 | 0.063816 | -0.0015745 | 0.067926 | -60.7636 | 61.8164 | -60.9467 | -60.8459 | 61.5829 | 0.11902 | 0.059509 | 0.25177 | 61.8576 | -60.9283 | -0.26093 | -0.091553 | -0.07782 | -0.16022 | -0.32501 | -0.24262 | -0.050354 | 0.1831 | 60.7452 | 60.9375 | 122.2687 | 122.5021 | -0.07782 | 122.5433 | 60.8047 | -0.24262 | 122.5021 | -0.07782 | 60.8047 | 122.2687 | 122.5433 | -122.8546 | -122.8363
390.9688 | 122.7402 | -60.7315 | 61.8942 | 0.17197 | 0.0085706 | 0.0090086 | 0.0064643 | 0.066806 | -0.00071986 | 0.067071 | -61.1618 | 61.7889 | -61.0016 | -60.9329 | 61.4502 | -0.073242 | 0.036621 | 0.050354 | 61.8576 | -61.0199 | -0.27008 | -0.10529 | -0.4303 | -0.20142 | -0.44403 | -0.28839 | -0.036621 | -0.16022 | 60.7681 | 60.7819 | 122.1817 | 122.5204 | -0.4303 | 122.5891 | 60.6583 | -0.28839 | 122.5204 | -0.4303 | 60.6583 | 122.1817 | 122.5891 | -122.8958 | -122.9141
391.9219 | 122.85 | -60.6674 | 61.8622 | 0.28641 | 0.0019482 | 0.0058042 | -0.0035761 | 0.06467 | -0.0028561 | 0.067071 | -60.704 | 61.7935 | -60.9512 | -60.8139 | 61.6516 | 0.16022 | -0.054932 | 0.30212 | 61.821 | -60.9146 | -0.28381 | -0.068665 | -0.036622 | -0.14648 | -0.21057 | -0.24719 | -0.041199 | 0.24719 | 60.6125 | 60.9695 | 122.319 | 122.4609 | -0.036622 | 122.4884 | 60.8276 | -0.24719 | 122.4609 | -0.036622 | 60.8276 | 122.319 | 122.4884 | -122.8134 | -122.7768
392.9844 | 122.8912 | -60.6766 | 61.8668 | -0.19424 | 0.0036572 | 0.0043088 | -0.0016535 | 0.060398 | 0.00077554 | 0.067712 | -60.7407 | 61.7706 | -60.9512 | -60.8093 | 61.6516 | 0.15564 | -0.086975 | 0.32044 | 61.8256 | -60.9558 | -0.27466 | -0.09613 | -0.064087 | -0.13275 | -0.21515 | -0.27924 | -0.041198 | 0.21057 | 60.5896 | 60.997 | 122.3282 | 122.4472 | -0.064087 | 122.5021 | 60.8322 | -0.27924 | 122.4472 | -0.064087 | 60.8322 | 122.3282 | 122.5021 | -122.818 | -122.8226
393.9062 | 122.7951 | -60.6995 | 61.8713 | 0.042267 | 0.0019482 | 0.0087948 | -0.0012261 | 0.061038 | -7.9062e-05 | 0.069635 | -60.8231 | 61.7844 | -60.9787 | -60.9695 | 61.5555 | 0.059509 | -0.1236 | 0.15106 | 61.8073 | -60.9604 | -0.27924 | -0.086975 | -0.1236 | -0.27008 | -0.31586 | -0.26093 | -0.064087 | 0.15564 | 60.5759 | 60.8505 | 122.2549 | 122.4838 | -0.1236 | 122.5067 | 60.759 | -0.26093 | 122.4838 | -0.1236 | 60.759 | 122.2549 | 122.5067 | -122.85 | -122.8317
394.9688 | 122.7448 | -60.7132 | 61.8942 | 0.15671 | 0.0062208 | 0.0092222 | 0.0068915 | 0.062747 | -0.00093346 | 0.069207 | -60.8505 | 61.8301 | -61.0199 | -60.9512 | 61.4777 | -0.041199 | -0.027466 | 0.050354 | 61.8256 | -61.0336 | -0.3067 | -0.064087 | -0.13733 | -0.23804 | -0.41657 | -0.32043 | -0.068664 | 0.16937 | 60.6857 | 60.7636 | 122.1909 | 122.5433 | -0.13733 | 122.5388 | 60.672 | -0.32043 | 122.5433 | -0.13733 | 60.672 | 122.1909 | 122.5388 | -122.9141 | -122.9279
395.9062 | 122.8958 | -60.704 | 61.8576 | 0.27878 | 0.0034436 | 0.0051632 | -0.0018671 | 0.064456 | 0.00056194 | 0.068353 | -60.7407 | 61.7935 | -60.9421 | -60.8688 | 61.5967 | 0.059509 | -0.20142 | 0.16022 | 61.7981 | -60.9833 | -0.23804 | -0.064087 | -0.036621 | -0.16479 | -0.26093 | -0.27923 | -0.059509 | 0.20142 | 60.5026 | 60.8643 | 122.3007 | 122.4976 | -0.036621 | 122.5021 | 60.7635 | -0.27923 | 122.4976 | -0.036621 | 60.7635 | 122.3007 | 122.5021 | -122.7997 | -122.8409
396.9844 | 122.8592 | -60.6674 | 61.8256 | 0.034637 | 0.0019482 | 0.0051632 | -0.0044305 | 0.061466 | -0.0013609 | 0.067712 | -60.8322 | 61.7844 | -60.9924 | -60.878 | 61.5875 | 0.073242 | -0.07782 | 0.19226 | 61.7889 | -60.9879 | -0.32501 | -0.041199 | -0.16479 | -0.21057 | -0.23804 | -0.32043 | -0.036622 | 0.16022 | 60.5896 | 60.8597 | 122.2549 | 122.4518 | -0.16479 | 122.4564 | 60.7407 | -0.32043 | 122.4518 | -0.16479 | 60.7407 | 122.2549 | 122.4564 | -122.818 | -122.8134
397.9219 | 122.7951 | -60.7178 | 61.8439 | 0.1796 | 0.0051526 | 0.0051632 | 0.0047553 | 0.064243 | -0.0015745 | 0.070916 | -60.8002 | 61.8622 | -60.965 | -60.9238 | 61.5097 | -0.041199 | -0.11444 | 0.082397 | 61.7935 | -61.0245 | -0.24719 | 0.018311 | -0.082398 | -0.20599 | -0.33417 | -0.3067 | -0.050354 | 0.16479 | 60.6033 | 60.8002 | 122.2275 | 122.58 | -0.082398 | 122.5113 | 60.6766 | -0.3067 | 122.58 | -0.082398 | 60.6766 | 122.2275 | 122.5113 | -122.8088 | -122.8683
398.9531 | 122.7264 | -60.7224 | 61.8576 | 0.011749 | 0.006648 | 0.0072996 | 0.0056097 | 0.063388 | -0.00071986 | 0.067285 | -60.7864 | 61.8759 | -60.9695 | -60.9283 | 61.5143 | -0.032043 | 0.013733 | 0.091553 | 61.8576 | -61.0245 | -0.24719 | 0.018311 | -0.064087 | -0.20599 | -0.34332 | -0.30212 | 0 | 0.18311 | 60.7361 | 60.8139 | 122.2366 | 122.5983 | -0.064087 | 122.58 | 60.6903 | -0.30212 | 122.5983 | -0.064087 | 60.6903 | 122.2366 | 122.58 | -122.8271 | -122.8821
399.9062 | 122.8088 | -60.7086 | 61.8439 | 0.19485 | 0.00323 | 0.0096494 | -0.0044305 | 0.063816 | -0.00093346 | 0.068994 | -60.8414 | 61.8027 | -60.9787 | -60.9055 | 61.5646 | 0.045776 | -0.064087 | 0.16937 | 61.8027 | -60.965 | -0.27008 | -0.041199 | -0.13275 | -0.19684 | -0.27924 | -0.25635 | -0.041199 | 0.13733 | 60.6445 | 60.878 | 122.2733 | 122.5113 | -0.13275 | 122.5113 | 60.7544 | -0.25635 | 122.5113 | -0.13275 | 60.7544 | 122.2733 | 122.5113 | -122.8226 | -122.8088
400.9688 | 122.8546 | -60.6766 | 61.8439 | 0.20248 | 0.0040846 | 0.0062314 | 0.0024053 | 0.063816 | -0.0022153 | 0.067285 | -60.7864 | 61.8027 | -60.9833 | -60.8826 | 61.5601 | 0.036621 | -0.16937 | 0.15106 | 61.7615 | -60.9741 | -0.3067 | -0.041199 | -0.10986 | -0.20599 | -0.28381 | -0.29755 | -0.082397 | 0.19684 | 60.5072 | 60.8276 | 122.2366 | 122.4792 | -0.10986 | 122.4381 | 60.7132 | -0.29755 | 122.4792 | -0.10986 | 60.7132 | 122.2366 | 122.4381 | -122.8271 | -122.818
401.9219 | 122.7631 | -60.7086 | 61.8988 | -0.12558 | 0.0038708 | 0.0068722 | 0.0015509 | 0.064456 | -0.0020017 | 0.067498 | -60.7864 | 61.853 | -60.997 | -60.9192 | 61.5463 | 0.045776 | 0.1236 | 0.20142 | 61.8439 | -61.0062 | -0.28839 | -0.045777 | -0.07782 | -0.21057 | -0.35248 | -0.29755 | -0.054932 | 0.21057 | 60.8322 | 60.91 | 122.2549 | 122.5616 | -0.07782 | 122.5525 | 60.7544 | -0.29755 | 122.5616 | -0.07782 | 60.7544 | 122.2549 | 122.5525 | -122.8958 | -122.905
402.9688 | 122.7722 | -60.7269 | 61.8942 | 0.042267 | 0.0057934 | 0.010077 | 0.0075323 | 0.065525 | -0.00071986 | 0.067285 | -60.8093 | 61.8347 | -60.9787 | -60.9192 | 61.5234 | -0.022888 | 0 | 0.09613 | 61.853 | -60.9833 | -0.25177 | -0.059509 | -0.082397 | -0.19226 | -0.37079 | -0.25635 | -0.041199 | 0.16937 | 60.7269 | 60.8231 | 122.2504 | 122.5616 | -0.082397 | 122.58 | 60.704 | -0.25635 | 122.5616 | -0.082397 | 60.704 | 122.2504 | 122.58 | -122.8729 | -122.8775
403.9062 | 122.8638 | -60.6857 | 61.8027 | 0.15671 | 0.00323 | 0.011572 | 0.0019781 | 0.068088 | -0.0024289 | 0.067712 | -60.7681 | 61.8118 | -60.9558 | -60.878 | 61.5875 | 0.036621 | -0.17853 | 0.15564 | 61.7844 | -60.9741 | -0.27008 | 0.009156 | -0.082397 | -0.19226 | -0.21515 | -0.28839 | -0.01831 | 0.18768 | 60.5072 | 60.8414 | 122.2733 | 122.4976 | -0.082397 | 122.4701 | 60.7224 | -0.28839 | 122.4976 | -0.082397 | 60.7224 | 122.2733 | 122.4701 | -122.7585 | -122.7768
404.9688 | 122.7997 | -60.7361 | 61.8439 | 0.24826 | 0.0057934 | 0.0060178 | 0.0024053 | 0.066806 | -0.0034971 | 0.069635 | -60.8276 | 61.8256 | -61.0107 | -60.91 | 61.528 | -0.027466 | -0.09613 | 0.082397 | 61.8073 | -61.0153 | -0.27466 | -0.01831 | -0.091553 | -0.17395 | -0.31586 | -0.27924 | -0.036621 | 0.1831 | 60.64 | 60.8185 | 122.2641 | 122.5616 | -0.091553 | 122.5433 | 60.7086 | -0.27924 | 122.5616 | -0.091553 | 60.7086 | 122.2641 | 122.5433 | -122.8546 | -122.8592
405.9062 | 122.85 | -60.6949 | 61.853 | 0.24063 | 0.0034436 | 0.013708 | -0.0025079 | 0.063388 | -0.0017881 | 0.069848 | -60.9467 | 61.7661 | -60.9833 | -60.8276 | 61.6196 | 0.045776 | -0.21057 | 0.17853 | 61.7981 | -60.9741 | -0.28839 | -0.086975 | -0.25177 | -0.13275 | -0.23346 | -0.27924 | -0.054931 | 0.036621 | 60.4843 | 60.8734 | 122.3145 | 122.4609 | -0.25177 | 122.493 | 60.7407 | -0.27924 | 122.4609 | -0.25177 | 60.7407 | 122.3145 | 122.493 | -122.8363 | -122.8271
406.9844 | 122.7859 | -60.672 | 61.9034 | -0.25528 | 0.0025892 | 0.0045224 | -0.0003717 | 0.062961 | -0.0030697 | 0.069635 | -60.7819 | 61.8118 | -60.9787 | -60.878 | 61.5875 | 0.11444 | 0.086975 | 0.23804 | 61.8713 | -60.965 | -0.3067 | -0.091552 | -0.10986 | -0.20599 | -0.31586 | -0.29297 | -0.032043 | 0.19684 | 60.759 | 60.91 | 122.2595 | 122.4838 | -0.10986 | 122.5433 | 60.7864 | -0.29297 | 122.4838 | -0.10986 | 60.7864 | 122.2595 | 122.5433 | -122.8821 | -122.8683
407.9219 | 122.8455 | -60.6537 | 61.8851 | -1.6209 | 0.00023916 | 0.006445 | -0.0016535 | 0.063816 | -0.00093346 | 0.067071 | -60.6216 | 61.8439 | -60.9238 | -60.8002 | 61.6791 | 0.14191 | -0.068665 | 0.31586 | 61.8164 | -60.9467 | -0.27008 | -0.041199 | 0.032044 | -0.14648 | -0.20599 | -0.29297 | -0.068665 | 0.30212 | 60.585 | 60.9695 | 122.3328 | 122.4976 | 0.032044 | 122.4701 | 60.7956 | -0.29297 | 122.4976 | 0.032044 | 60.7956 | 122.3328 | 122.4701 | -122.8088 | -122.8317
408.9531 | 122.7448 | -60.7361 | 61.908 | 0.080414 | 0.0036572 | 0.0060178 | 0.0071051 | 0.063175 | -0.00093346 | 0.067926 | -60.8276 | 61.8759 | -60.9741 | -60.9421 | 61.4914 | -0.041199 | 0.022888 | 0.054932 | 61.8576 | -61.0428 | -0.23804 | -0.032043 | -0.091553 | -0.20599 | -0.41656 | -0.3067 | -0.050354 | 0.14648 | 60.759 | 60.791 | 122.2275 | 122.612 | -0.091553 | 122.5937 | 60.6949 | -0.3067 | 122.612 | -0.091553 | 60.6949 | 122.2275 | 122.5937 | -122.8821 | -122.9507
409.9062 | 122.8409 | -60.704 | 61.8393 | -0.018768 | 0.0038708 | 0.0062314 | 0.0013373 | 0.064884 | -0.0032835 | 0.067285 | -60.7361 | 61.7706 | -60.9421 | -60.8505 | 61.6104 | 0.050354 | -0.20142 | 0.19226 | 61.8027 | -60.9604 | -0.23804 | -0.068664 | -0.032043 | -0.14648 | -0.22888 | -0.25635 | -0.036621 | 0.20599 | 60.5026 | 60.8963 | 122.3145 | 122.4747 | -0.032043 | 122.5067 | 60.7544 | -0.25635 | 122.4747 | -0.032043 | 60.7544 | 122.3145 | 122.5067 | -122.7814 | -122.7997
410.9688 | 122.7264 | -60.7407 | 61.8851 | 0.080414 | 0.0057934 | 0.0038816 | 0.0056097 | 0.065525 | -0.0020017 | 0.067285 | -60.8231 | 61.8347 | -61.0199 | -60.9421 | 61.4731 | -0.050354 | 0.054932 | 0.082397 | 61.8439 | -60.9924 | -0.27923 | -0.050354 | -0.082397 | -0.20142 | -0.41199 | -0.25177 | -0.041199 | 0.19684 | 60.7956 | 60.8231 | 122.2137 | 122.5754 | -0.082397 | 122.5845 | 60.6903 | -0.25177 | 122.5754 | -0.082397 | 60.6903 | 122.2137 | 122.5845 | -122.905 | -122.8775
411.9062 | 122.7814 | -60.7224 | 61.8439 | 0.22537 | 0.0072888 | 0.0060178 | 0.0026191 | 0.065311 | -0.0032835 | 0.070703 | -60.8231 | 61.8622 | -60.9879 | -60.9604 | 61.4822 | -0.064087 | -0.032043 | 0.054932 | 61.8439 | -61.0336 | -0.2655 | 0.018311 | -0.10071 | -0.23804 | -0.36163 | -0.31128 | 0 | 0.16479 | 60.6903 | 60.7773 | 122.2046 | 122.5845 | -0.10071 | 122.5662 | 60.6583 | -0.31128 | 122.5845 | -0.10071 | 60.6583 | 122.2046 | 122.5662 | -122.8317 | -122.8775
412.9531 | 122.7676 | -60.7086 | 61.8759 | 0.19485 | 0.0045118 | 0.0068722 | 0.0051825 | 0.065525 | 0.00013454 | 0.068139 | -60.7269 | 61.9171 | -60.9924 | -60.8734 | 61.5692 | 0.059509 | 0 | 0.16937 | 61.8301 | -61.0291 | -0.28381 | 0.041198 | -0.018311 | -0.16479 | -0.3067 | -0.32043 | -0.045777 | 0.2655 | 60.7086 | 60.878 | 122.2778 | 122.6257 | -0.018311 | 122.5388 | 60.7681 | -0.32043 | 122.6257 | -0.018311 | 60.7681 | 122.2778 | 122.5388 | -122.8683 | -122.905
413.9062 | 122.8088 | -60.6903 | 61.8347 | 0.1796 | 0.0036572 | 0.004736 | -0.0040033 | 0.065097 | -0.00029266 | 0.067926 | -60.8002 | 61.8027 | -60.9924 | -60.9055 | 61.5784 | 0.027466 | -0.13275 | 0.14648 | 61.8118 | -60.9558 | -0.30212 | -0.032044 | -0.10986 | -0.21515 | -0.25635 | -0.2655 | -0.022888 | 0.19226 | 60.5576 | 60.8368 | 122.2687 | 122.493 | -0.10986 | 122.5021 | 60.7178 | -0.2655 | 122.493 | -0.10986 | 60.7178 | 122.2687 | 122.5021 | -122.8271 | -122.7905
414.9531 | 122.8729 | -60.6766 | 61.8301 | 0.18723 | 0.0045118 | 0.0068722 | 0.0034735 | 0.065952 | -0.00093346 | 0.068994 | -60.7773 | 61.8073 | -60.9924 | -60.8734 | 61.5738 | 0.036621 | -0.17395 | 0.14191 | 61.7935 | -60.9787 | -0.31586 | -0.022888 | -0.10071 | -0.19684 | -0.25635 | -0.30212 | -0.036621 | 0.21515 | 60.5026 | 60.8185 | 122.2504 | 122.4838 | -0.10071 | 122.4701 | 60.7132 | -0.30212 | 122.4838 | -0.10071 | 60.7132 | 122.2504 | 122.4701 | -122.8226 | -122.8088
415.9062 | 122.8775 | -60.6949 | 61.8164 | 0.22537 | 0.0042982 | 0.010077 | 0.0021917 | 0.065311 | -0.0028561 | 0.069207 | -60.7681 | 61.8713 | -60.9833 | -60.9009 | 61.5692 | 0.032043 | -0.1831 | 0.11444 | 61.8118 | -61.0016 | -0.28839 | 0.054932 | -0.073242 | -0.20599 | -0.24719 | -0.3067 | -0.004577 | 0.21515 | 60.5118 | 60.8093 | 122.2641 | 122.5662 | -0.073242 | 122.5067 | 60.7269 | -0.3067 | 122.5662 | -0.073242 | 60.7269 | 122.2641 | 122.5067 | -122.7997 | -122.818
416.9688 | 122.8683 | -60.6674 | 61.821 | 0.17197 | 0.0053662 | 0.0043088 | 0.0004827 | 0.066165 | -0.0015745 | 0.068994 | -60.7956 | 61.7889 | -60.9924 | -60.8871 | 61.5646 | 0.064087 | -0.1831 | 0.12817 | 61.8027 | -60.9787 | -0.32501 | -0.032044 | -0.12817 | -0.21973 | -0.25635 | -0.31128 | -0.018311 | 0.19684 | 60.4843 | 60.7956 | 122.2321 | 122.4564 | -0.12817 | 122.4701 | 60.7315 | -0.31128 | 122.4564 | -0.12817 | 60.7315 | 122.2321 | 122.4701 | -122.8134 | -122.7997
417.9062 | 122.8592 | -60.6995 | 61.8576 | 0.18723 | 0.0042982 | 0.0060178 | -0.0007989 | 0.066379 | -0.0015745 | 0.069848 | -60.7452 | 61.7889 | -60.9558 | -60.878 | 61.6699 | -0.009155 | -0.39825 | 0.33417 | 61.7203 | -61.0016 | -0.25635 | -0.068665 | -0.045776 | -0.17853 | -0.18768 | -0.30212 | -0.13733 | 0.21057 | 60.3012 | 61.0336 | 122.3694 | 122.4884 | -0.045776 | 122.4197 | 60.6903 | -0.30212 | 122.4884 | -0.045776 | 60.6903 | 122.3694 | 122.4197 | -122.8134 | -122.8592
418.9531 | 122.7631 | -60.7452 | 61.8805 | 0.46951 | 0.0068616 | 0.0066586 | 0.0049689 | 0.065097 | -0.0011471 | 0.067071 | -60.8093 | 61.8942 | -60.965 | -60.9695 | 61.4777 | -0.068665 | -0.004578 | 0.045776 | 61.8256 | -61.0199 | -0.21973 | 0.013733 | -0.064087 | -0.2243 | -0.40283 | -0.27466 | -0.054931 | 0.15564 | 60.7407 | 60.791 | 122.2229 | 122.6395 | -0.064087 | 122.5708 | 60.6766 | -0.27466 | 122.6395 | -0.064087 | 60.6766 | 122.2229 | 122.5708 | -122.8455 | -122.9004
419.9062 | 122.7951 | -60.6583 | 61.8439 | 0.049896 | 0.0028028 | 0.010717 | -0.0040033 | 0.066379 | -0.00093346 | 0.069421 | -60.8185 | 61.7752 | -60.9833 | -60.9192 | 61.5646 | -0.041199 | 0.17853 | 0.27924 | 61.8576 | -60.9329 | -0.32501 | -0.068664 | -0.16022 | -0.26093 | -0.27924 | -0.27466 | 0.013733 | 0.16479 | 60.8368 | 60.9375 | 122.2229 | 122.4335 | -0.16022 | 122.5159 | 60.6171 | -0.27466 | 122.4335 | -0.16022 | 60.6171 | 122.2229 | 122.5159 | -122.8271 | -122.7768
420.9531 | 122.7493 | -60.7178 | 61.8759 | 0.66788 | 0.0053662 | 0.0087948 | 0.0075323 | 0.064884 | 0.00034814 | 0.068139 | -60.8551 | 61.8805 | -61.0016 | -60.9833 | 61.4594 | -0.064087 | -0.018311 | 0.022888 | 61.8393 | -61.0199 | -0.28381 | 0.004577 | -0.13733 | -0.2655 | -0.41656 | -0.30212 | -0.036622 | 0.14648 | 60.6995 | 60.7407 | 122.1771 | 122.5983 | -0.13733 | 122.5571 | 60.6537 | -0.30212 | 122.5983 | -0.13733 | 60.6537 | 122.1771 | 122.5571 | -122.8775 | -122.8958
421.9062 | 122.8546 | -60.704 | 61.8347 | 0.25589 | 0.0070752 | 0.0090086 | 0.0026191 | 0.065525 | -7.9062e-05 | 0.068994 | -60.7315 | 61.8347 | -60.9695 | -60.878 | 61.5921 | 0.045776 | -0.17853 | 0.16022 | 61.7935 | -60.9879 | -0.2655 | 0 | -0.027465 | -0.17395 | -0.24262 | -0.28381 | -0.041199 | 0.23804 | 60.5255 | 60.8643 | 122.2961 | 122.5388 | -0.027465 | 122.4976 | 60.7498 | -0.28381 | 122.5388 | -0.027465 | 60.7498 | 122.2961 | 122.4976 | -122.8043 | -122.8226
422.9688 | 122.7448 | -60.7498 | 61.8576 | 0.16434 | 0.0053662 | 0.0066586 | 0.0026191 | 0.066379 | -0.0026425 | 0.069635 | -60.8459 | 61.8484 | -61.0107 | -60.9787 | 61.4594 | -0.07782 | 0.018311 | 0.036621 | 61.8439 | -61.0382 | -0.26093 | -0.009155 | -0.09613 | -0.22888 | -0.39825 | -0.28839 | -0.013733 | 0.16479 | 60.7681 | 60.7864 | 122.2092 | 122.5983 | -0.09613 | 122.5937 | 60.672 | -0.28839 | 122.5983 | -0.09613 | 60.672 | 122.2092 | 122.5937 | -122.8683 | -122.8958
423.9062 | 122.85 | -60.6995 | 61.8027 | 0.32455 | 0.0047254 | 0.0079404 | -0.0022943 | 0.065952 | -0.0034971 | 0.069207 | -60.7498 | 61.8073 | -60.9741 | -60.8643 | 61.6104 | 0.050354 | -0.18768 | 0.17395 | 61.8256 | -61.0016 | -0.27466 | 0.004578 | -0.050354 | -0.16479 | -0.19226 | -0.30212 | 0.022889 | 0.2243 | 60.5118 | 60.8734 | 122.3099 | 122.5067 | -0.050354 | 122.525 | 60.7498 | -0.30212 | 122.5067 | -0.050354 | 60.7498 | 122.3099 | 122.525 | -122.7768 | -122.8043
424.9531 | 122.7768 | -60.7315 | 61.8622 | 0.16434 | 0.0087842 | 0.0066586 | 0.0024053 | 0.064884 | -0.0011471 | 0.067926 | -60.8185 | 61.8713 | -60.997 | -60.9375 | 61.5051 | -0.027466 | -0.07782 | 0.073242 | 61.8073 | -61.0291 | -0.2655 | 0.009155 | -0.086975 | -0.20599 | -0.35706 | -0.29755 | -0.054932 | 0.17853 | 60.6537 | 60.8047 | 122.2366 | 122.6028 | -0.086975 | 122.5388 | 60.704 | -0.29755 | 122.6028 | -0.086975 | 60.704 | 122.2366 | 122.5388 | -122.8592 | -122.8912
425.9062 | 122.8638 | -60.6857 | 61.8393 | -0.0035098 | 0.0028028 | 0.0090086 | -0.0050715 | 0.065311 | -0.00071986 | 0.066003 | -60.8185 | 61.8164 | -60.9787 | -60.8917 | 61.5967 | 0.064087 | -0.073242 | 0.20142 | 61.8484 | -60.9787 | -0.29297 | -0.022888 | -0.13275 | -0.20599 | -0.24261 | -0.29297 | 0.009156 | 0.16022 | 60.6125 | 60.8871 | 122.2824 | 122.5021 | -0.13275 | 122.5342 | 60.7498 | -0.29297 | 122.5021 | -0.13275 | 60.7498 | 122.2824 | 122.5342 | -122.818 | -122.818
426.9688 | 122.7539 | -60.7132 | 61.8805 | -0.31631 | 0.0055798 | 0.012213 | 0.0041143 | 0.065097 | -0.0030697 | 0.066858 | -60.7407 | 61.8668 | -60.9695 | -60.8734 | 61.5463 | 0.054932 | 0.009155 | 0.17853 | 61.821 | -60.997 | -0.25635 | -0.013733 | -0.027466 | -0.16022 | -0.33417 | -0.28381 | -0.059509 | 0.22888 | 60.7224 | 60.8917 | 122.2595 | 122.58 | -0.027466 | 122.5342 | 60.7681 | -0.28381 | 122.58 | -0.027466 | 60.7681 | 122.2595 | 122.5342 | -122.85 | -122.8775
427.9062 | 122.8638 | -60.6903 | 61.8759 | 0.095673 | 0.0036572 | 0.003668 | -0.0046441 | 0.065097 | -0.0022153 | 0.068994 | -60.8139 | 61.7844 | -60.9879 | -60.9055 | 61.5372 | 0.045776 | -0.086975 | 0.15106 | 61.8484 | -60.9467 | -0.29755 | -0.091553 | -0.1236 | -0.21515 | -0.33875 | -0.25635 | -0.027466 | 0.17395 | 60.6033 | 60.8414 | 122.2275 | 122.4747 | -0.1236 | 122.5388 | 60.7361 | -0.25635 | 122.4747 | -0.1236 | 60.7361 | 122.2275 | 122.5388 | -122.8638 | -122.8226
428.9688 | 122.9004 | -60.6995 | 61.853 | -0.1561 | 0.00088016 | -0.00017722 | -0.0014399 | 0.061252 | -0.0020017 | 0.068567 | -60.7224 | 61.7981 | -60.9558 | -60.8963 | 61.9949 | 0.44861 | -0.32501 | 0.050354 | 61.8073 | -60.9421 | -0.25635 | -0.054931 | -0.022888 | -0.19684 | 0.14191 | -0.24262 | -0.045776 | 0.23346 | 60.3745 | 60.7498 | 122.6944 | 122.4976 | -0.022888 | 122.5067 | 61.1481 | -0.24262 | 122.4976 | -0.022888 | 61.1481 | 122.6944 | 122.5067 | -122.8088 | -122.7951
429.9062 | 122.8363 | -60.6995 | 61.8393 | 0.12619 | 0.002162 | 0.0077268 | 5.5496e-05 | 0.062747 | -0.0013609 | 0.069848 | -60.7773 | 61.7844 | -60.9695 | -60.9055 | 61.5555 | 0.036621 | -0.15564 | 0.16479 | 61.7981 | -61.0016 | -0.27008 | -0.054931 | -0.07782 | -0.20599 | -0.28381 | -0.30212 | -0.041198 | 0.19226 | 60.5438 | 60.8643 | 122.2549 | 122.4838 | -0.07782 | 122.4976 | 60.7361 | -0.30212 | 122.4838 | -0.07782 | 60.7361 | 122.2549 | 122.4976 | -122.8088 | -122.8409
430.9531 | 122.8729 | -60.6766 | 61.8393 | -0.072174 | 0.0053662 | 0.0034544 | 0.0034735 | 0.064029 | -0.0020017 | 0.068139 | -60.7407 | 61.8164 | -60.9512 | -60.8414 | 61.6013 | 0.064087 | -0.18768 | 0.16937 | 61.7935 | -60.9924 | -0.27466 | -0.022888 | -0.064087 | -0.16479 | -0.23804 | -0.31586 | -0.045776 | 0.21057 | 60.4889 | 60.8459 | 122.2778 | 122.493 | -0.064087 | 122.4701 | 60.7407 | -0.31586 | 122.493 | -0.064087 | 60.7407 | 122.2778 | 122.4701 | -122.7905 | -122.8317
431.9062 | 122.8638 | -60.6857 | 61.8301 | -0.12558 | 0.0023756 | 0.006445 | 0.0002691 | 0.061893 | -0.0013609 | 0.069635 | -60.7269 | 61.7752 | -60.9604 | -60.8002 | 61.6791 | -0.004578 | 0.43945 | 0.4715 | 61.8942 | -60.9238 | -0.27466 | -0.054931 | -0.041199 | -0.11444 | -0.15106 | -0.23804 | 0.064087 | 0.23346 | 61.1252 | 61.1572 | 122.3648 | 122.4609 | -0.041199 | 122.58 | 60.6812 | -0.23804 | 122.4609 | -0.041199 | 60.6812 | 122.3648 | 122.58 | -122.7905 | -122.7539
432.9688 | 122.7814 | -60.704 | 61.8668 | 0.25589 | 0.0028028 | 0.0062314 | 0.0047553 | 0.064884 | -0.00093346 | 0.068994 | -60.8093 | 61.8439 | -61.0153 | -60.9055 | 61.5051 | -0.032043 | -0.11444 | 0.073242 | 61.7935 | -61.0016 | -0.31128 | -0.022888 | -0.10529 | -0.20142 | -0.36163 | -0.29755 | -0.073242 | 0.20599 | 60.5896 | 60.7773 | 122.2092 | 122.5479 | -0.10529 | 122.4976 | 60.672 | -0.29755 | 122.5479 | -0.10529 | 60.672 | 122.2092 | 122.4976 | -122.8821 | -122.8683
433.9062 | 122.818 | -60.672 | 61.8439 | 0.049896 | 0.0017346 | 0.0032406 | -0.0022943 | 0.061679 | -0.00093346 | 0.070062 | -60.8047 | 61.7981 | -60.9695 | -60.8963 | 61.5646 | 0.032043 | -0.1236 | 0.16022 | 61.8118 | -60.9741 | -0.29755 | -0.045776 | -0.13275 | -0.2243 | -0.27924 | -0.30212 | -0.032043 | 0.16479 | 60.5484 | 60.8322 | 122.2366 | 122.4701 | -0.13275 | 122.4838 | 60.704 | -0.30212 | 122.4701 | -0.13275 | 60.704 | 122.2366 | 122.4838 | -122.8134 | -122.818
434.9688 | 122.8683 | -60.672 | 61.8484 | -0.064545 | 0.00323 | 0.0043088 | -0.0003717 | 0.061466 | 0.00034814 | 0.069848 | -60.8002 | 61.7798 | -60.9787 | -60.8505 | 61.6013 | 0.082397 | -0.07782 | 0.24261 | 61.7935 | -61.0016 | -0.3067 | -0.068665 | -0.12817 | -0.17853 | -0.24719 | -0.32959 | -0.054932 | 0.17853 | 60.5942 | 60.9146 | 122.2733 | 122.4518 | -0.12817 | 122.4655 | 60.7544 | -0.32959 | 122.4518 | -0.12817 | 60.7544 | 122.2733 | 122.4655 | -122.8271 | -122.85
435.9062 | 122.8638 | -60.6949 | 61.853 | -0.041657 | 0.0010938 | 0.00089078 | 0.0002691 | 0.061679 | 0.00077554 | 0.06643 | -60.7864 | 61.7798 | -60.9741 | -60.8597 | 61.6013 | 0.091553 | -0.086975 | 0.2243 | 61.7889 | -60.9787 | -0.27924 | -0.073242 | -0.091553 | -0.16479 | -0.25177 | -0.28381 | -0.064087 | 0.18768 | 60.6079 | 60.9192 | 122.2961 | 122.4747 | -0.091553 | 122.4838 | 60.7864 | -0.28381 | 122.4747 | -0.091553 | 60.7864 | 122.2961 | 122.4838 | -122.8271 | -122.8317
436.9688 | 122.7493 | -60.7086 | 61.8622 | 0.065155 | 0.0055798 | 0.011572 | 0.0053961 | 0.064243 | -0.0015745 | 0.066644 | -60.7956 | 61.8439 | -61.0016 | -60.9238 | 61.4822 | -0.041199 | 0.013733 | 0.082397 | 61.8347 | -61.0199 | -0.29297 | -0.018311 | -0.086975 | -0.21515 | -0.37994 | -0.31128 | -0.027466 | 0.20599 | 60.7224 | 60.791 | 122.1909 | 122.5525 | -0.086975 | 122.5433 | 60.6674 | -0.31128 | 122.5525 | -0.086975 | 60.6674 | 122.1909 | 122.5433 | -122.8638 | -122.8821
437.9062 | 122.8546 | -60.672 | 61.8484 | -0.056915 | 0.0036572 | 0.0043088 | -0.0037897 | 0.062534 | -0.00071986 | 0.069848 | -60.7681 | 61.7752 | -60.9467 | -60.8093 | 61.6562 | 0.14191 | -0.10529 | 0.27924 | 61.7981 | -60.9604 | -0.27466 | -0.073242 | -0.09613 | -0.13733 | -0.19226 | -0.28839 | -0.050354 | 0.17853 | 60.5667 | 60.9512 | 122.3282 | 122.4472 | -0.09613 | 122.4701 | 60.8139 | -0.28839 | 122.4472 | -0.09613 | 60.8139 | 122.3282 | 122.4701 | -122.7951 | -122.8088
438.9688 | 122.7814 | -60.6903 | 61.9034 | -0.034027 | 0.0025892 | 0.011145 | 0.0053961 | 0.063388 | -0.0030697 | 0.069421 | -60.759 | 61.8759 | -60.9924 | -60.8597 | 61.5738 | 0.064087 | 0.032043 | 0.19226 | 61.8393 | -61.0016 | -0.30212 | -0.027465 | -0.068664 | -0.16937 | -0.32959 | -0.31128 | -0.064087 | 0.23346 | 60.7224 | 60.8826 | 122.2641 | 122.5662 | -0.068664 | 122.5296 | 60.7544 | -0.31128 | 122.5662 | -0.068664 | 60.7544 | 122.2641 | 122.5296 | -122.8958 | -122.905
439.9062 | 122.8592 | -60.7132 | 61.8301 | 0.11093 | 0.0017346 | 0.0034544 | 0.0024053 | 0.065311 | -0.00050626 | 0.069207 | -60.7407 | 61.8073 | -60.9604 | -60.8688 | 61.5921 | 0.027466 | -0.21515 | 0.16022 | 61.8073 | -60.9924 | -0.24719 | -0.022888 | -0.027466 | -0.15564 | -0.23804 | -0.27924 | -0.022888 | 0.21973 | 60.498 | 60.8734 | 122.3053 | 122.5204 | -0.027466 | 122.5204 | 60.7407 | -0.27924 | 122.5204 | -0.027466 | 60.7407 | 122.3053 | 122.5204 | -122.7905 | -122.8226
440.9688 | 122.8729 | -60.6766 | 61.8439 | -0.049286 | 0.001521 | 0.0049496 | -0.0035761 | 0.064456 | -0.00050626 | 0.069635 | -60.7498 | 61.821 | -60.9329 | -60.8231 | 61.6196 | 0.11444 | -0.091553 | 0.25177 | 61.8027 | -60.9558 | -0.25635 | -0.022888 | -0.073242 | -0.14648 | -0.2243 | -0.27924 | -0.041199 | 0.1831 | 60.585 | 60.9283 | 122.2961 | 122.4976 | -0.073242 | 122.4792 | 60.791 | -0.27924 | 122.4976 | -0.073242 | 60.791 | 122.2961 | 122.4792 | -122.7768 | -122.7997
441.9062 | 122.8226 | -60.6903 | 61.8576 | -0.041657 | 0.0036572 | 0.0034544 | -0.0016535 | 0.061252 | -0.0013609 | 0.068567 | -60.8505 | 61.7889 | -61.0062 | -60.8826 | 61.5784 | 0.054932 | -0.068665 | 0.1831 | 61.8027 | -60.9467 | -0.31586 | -0.068665 | -0.16022 | -0.19226 | -0.27924 | -0.25635 | -0.054932 | 0.15564 | 60.6216 | 60.8734 | 122.2687 | 122.4792 | -0.16022 | 122.493 | 60.7452 | -0.25635 | 122.4792 | -0.16022 | 60.7452 | 122.2687 | 122.493 | -122.8638 | -122.8043
442.9688 | 122.7219 | -60.6995 | 61.9125 | -0.7283 | 0.0060072 | 0.0062314 | 0.0071051 | 0.062747 | -0.0022153 | 0.067926 | -60.9375 | 61.8347 | -61.0245 | -60.9558 | 61.4594 | -0.073242 | -0.004578 | 0.045776 | 61.8393 | -61.0107 | -0.32501 | -0.07782 | -0.23804 | -0.25635 | -0.45319 | -0.31128 | -0.073243 | 0.086975 | 60.6949 | 60.7452 | 122.1588 | 122.5342 | -0.23804 | 122.5388 | 60.6262 | -0.31128 | 122.5342 | -0.23804 | 60.6262 | 122.1588 | 122.5388 | -122.937 | -122.9233
443.9219 | 122.8134 | -60.6949 | 61.9217 | -0.18662 | 0.0036572 | 0.008154 | 0.0006965 | 0.064243 | -0.0024289 | 0.067285 | -60.8139 | 61.8805 | -60.9695 | -60.91 | 61.5372 | 0.054932 | 0.13733 | 0.1831 | 61.8713 | -60.9787 | -0.27466 | -0.041199 | -0.11902 | -0.21515 | -0.38452 | -0.28381 | -0.050354 | 0.15564 | 60.8322 | 60.878 | 122.2321 | 122.5754 | -0.11902 | 122.5662 | 60.7498 | -0.28381 | 122.5754 | -0.11902 | 60.7498 | 122.2321 | 122.5662 | -122.8912 | -122.9004
444.9531 | 122.8363 | -60.7132 | 61.8256 | 0.20248 | 0.0047254 | 0.0072996 | 0.0036871 | 0.065525 | -0.0013609 | 0.068567 | -60.8185 | 61.8301 | -60.9924 | -60.91 | 61.528 | -0.018311 | -0.1236 | 0.09613 | 61.8164 | -60.9879 | -0.27924 | 0.004577 | -0.10528 | -0.19684 | -0.29755 | -0.27466 | -0.009156 | 0.17395 | 60.5896 | 60.8093 | 122.2412 | 122.5433 | -0.10528 | 122.5296 | 60.6949 | -0.27466 | 122.5433 | -0.10528 | 60.6949 | 122.2412 | 122.5296 | -122.818 | -122.8134
445.9062 | 122.8455 | -60.6995 | 61.8256 | 0.080414 | 0.0017346 | 0.0092222 | -0.0046441 | 0.064456 | -0.0026425 | 0.068567 | -60.8231 | 61.7889 | -60.9512 | -60.9009 | 61.6104 | 0.19226 | -0.07782 | 0.068665 | 61.8301 | -60.9329 | -0.25177 | -0.036622 | -0.1236 | -0.20142 | -0.21515 | -0.23346 | 0.004577 | 0.12817 | 60.6216 | 60.7681 | 122.3099 | 122.4884 | -0.1236 | 122.5296 | 60.8917 | -0.23346 | 122.4884 | -0.1236 | 60.8917 | 122.3099 | 122.5296 | -122.7768 | -122.7585
446.9688 | 122.7859 | -60.7269 | 61.8393 | 0.24063 | 0.0047254 | 0.004736 | 0.0021917 | 0.064884 | -0.0017881 | 0.067285 | -60.8139 | 61.8759 | -60.9879 | -60.9009 | 61.5326 | -0.027466 | -0.09613 | 0.086975 | 61.7981 | -61.0336 | -0.26093 | 0.036622 | -0.086975 | -0.17395 | -0.3067 | -0.3067 | -0.041198 | 0.17395 | 60.6308 | 60.8139 | 122.2595 | 122.6028 | -0.086975 | 122.525 | 60.6995 | -0.3067 | 122.6028 | -0.086975 | 60.6995 | 122.2595 | 122.525 | -122.8271 | -122.8729
447.9062 | 122.8592 | -60.6949 | 61.8256 | 1.6826 | 0.0042982 | 0.0077268 | 0.0011237 | 0.064456 | -0.0022153 | 0.066858 | -60.7727 | 61.7386 | -60.9879 | -60.8414 | 61.5921 | 0.036621 | -0.19226 | 0.15106 | 61.7889 | -60.997 | -0.29297 | -0.086976 | -0.07782 | -0.14648 | -0.23346 | -0.30212 | -0.036622 | 0.21515 | 60.5026 | 60.8459 | 122.287 | 122.4335 | -0.07782 | 122.4838 | 60.7315 | -0.30212 | 122.4335 | -0.07782 | 60.7315 | 122.287 | 122.4838 | -122.8134 | -122.8226
448.9531 | 122.7585 | -60.7086 | 61.8347 | 0.1796 | 0.0062208 | 0.0079404 | 0.0039007 | 0.063816 | -0.0024289 | 0.066644 | -60.8551 | 61.8439 | -60.9879 | -60.9512 | 61.5005 | -0.064087 | -0.009155 | 0.027466 | 61.8301 | -61.0153 | -0.27924 | 0.009155 | -0.14648 | -0.24262 | -0.33417 | -0.3067 | -0.004578 | 0.13275 | 60.6995 | 60.7361 | 122.2092 | 122.5525 | -0.14648 | 122.5388 | 60.6445 | -0.3067 | 122.5525 | -0.14648 | 60.6445 | 122.2092 | 122.5388 | -122.8226 | -122.85
449.9219 | 122.8271 | -60.6903 | 61.8759 | -0.20187 | 0.0019482 | 0.006445 | -0.0022943 | 0.064243 | -0.0028561 | 0.066858 | -60.7544 | 61.7981 | -60.9695 | -60.8276 | 61.6425 | 0.14191 | 0.009155 | 0.28381 | 61.8347 | -60.965 | -0.27923 | -0.07782 | -0.064087 | -0.13733 | -0.23346 | -0.27466 | -0.041199 | 0.21515 | 60.6995 | 60.9741 | 122.3328 | 122.4884 | -0.064087 | 122.525 | 60.8322 | -0.27466 | 122.4884 | -0.064087 | 60.8322 | 122.3328 | 122.525 | -122.8455 | -122.8409
450.9688 | 122.8226 | -60.6995 | 61.8027 | 0.33981 | 0.0042982 | 0.0096494 | 0.0013373 | 0.065952 | -0.0039243 | 0.067498 | -60.7727 | 61.7752 | -60.9879 | -60.8551 | 61.5875 | 0.064087 | -0.19684 | 0.15564 | 61.7798 | -60.965 | -0.28839 | -0.027465 | -0.073242 | -0.15564 | -0.21515 | -0.2655 | -0.022888 | 0.21515 | 60.5026 | 60.8551 | 122.287 | 122.4747 | -0.073242 | 122.4792 | 60.7636 | -0.2655 | 122.4747 | -0.073242 | 60.7636 | 122.287 | 122.4792 | -122.7905 | -122.7676
451.9219 | 122.8134 | -60.6628 | 61.9034 | -0.25528 | 0.00023916 | 0.0032406 | -0.0016535 | 0.065097 | -0.00050626 | 0.068139 | -60.7544 | 61.821 | -60.9604 | -60.8643 | 61.6104 | 0.11902 | 0.059509 | 0.24719 | 61.8256 | -60.9604 | -0.29755 | -0.082397 | -0.091553 | -0.20142 | -0.29297 | -0.29755 | -0.077819 | 0.20599 | 60.7224 | 60.91 | 122.2733 | 122.4838 | -0.091553 | 122.4884 | 60.7819 | -0.29755 | 122.4838 | -0.091553 | 60.7819 | 122.2733 | 122.4884 | -122.8638 | -122.8638
452.9688 | 122.7951 | -60.704 | 61.8759 | -0.087433 | 0.0040846 | 0.0032406 | 0.0053961 | 0.065525 | -0.0017881 | 0.067071 | -60.7498 | 61.8713 | -60.965 | -60.8643 | 61.5646 | 0.068665 | 0.022888 | 0.19684 | 61.8576 | -60.9787 | -0.26093 | -0.004578 | -0.045776 | -0.16022 | -0.31128 | -0.27466 | -0.018311 | 0.21515 | 60.7269 | 60.9009 | 122.2687 | 122.5754 | -0.045776 | 122.5616 | 60.7727 | -0.27466 | 122.5754 | -0.045776 | 60.7727 | 122.2687 | 122.5616 | -122.8409 | -122.8546
453.9062 | 122.8775 | -60.6857 | 61.821 | 0.34744 | 0.0034436 | 0.0087948 | -0.0010125 | 0.064029 | -0.0020017 | 0.067926 | -60.7498 | 61.7752 | -60.9787 | -60.8505 | 61.6013 | 0.068665 | -0.18768 | 0.17395 | 61.8073 | -60.9604 | -0.29297 | -0.045776 | -0.064087 | -0.16479 | -0.21973 | -0.27466 | -0.013733 | 0.22888 | 60.498 | 60.8597 | 122.287 | 122.4609 | -0.064087 | 122.493 | 60.7544 | -0.27466 | 122.4609 | -0.064087 | 60.7544 | 122.287 | 122.493 | -122.7997 | -122.7814
454.9531 | 122.8592 | -60.6857 | 61.8301 | 0.233 | 0.0047254 | 0.0055906 | 0.0032599 | 0.063816 | -0.0034971 | 0.067285 | -60.7864 | 61.7981 | -60.9833 | -60.8734 | 61.6013 | 0.013733 | -0.19226 | 0.13275 | 61.7889 | -60.9924 | -0.29755 | -0.032043 | -0.10071 | -0.18768 | -0.22888 | -0.3067 | -0.041199 | 0.19684 | 60.4935 | 60.8185 | 122.287 | 122.4838 | -0.10071 | 122.4747 | 60.6995 | -0.3067 | 122.4838 | -0.10071 | 60.6995 | 122.287 | 122.4747 | -122.8134 | -122.8226
455.9062 | 122.8409 | -60.6812 | 61.8301 | 0.21774 | 0.00323 | 0.0092222 | 0.0017645 | 0.066806 | -0.0011471 | 0.067498 | -60.7361 | 61.8073 | -60.965 | -60.8231 | 61.5234 | -0.14191 | -0.1236 | 0.32959 | 61.7706 | -60.9741 | -0.28381 | -0.022888 | -0.054932 | -0.14191 | -0.3067 | -0.29297 | -0.059509 | 0.22888 | 60.5576 | 61.0107 | 122.2046 | 122.4884 | -0.054932 | 122.4518 | 60.5392 | -0.29297 | 122.4884 | -0.054932 | 60.5392 | 122.2046 | 122.4518 | -122.7951 | -122.8043
456.9688 | 122.8912 | -60.6812 | 61.8484 | -0.14847 | 0.0023756 | 0.0090086 | -0.0048577 | 0.063175 | -0.0026425 | 0.068994 | -60.7224 | 61.7889 | -60.9421 | -60.9695 | 61.3541 | -0.032043 | 0.045776 | 0.27924 | 61.8027 | -60.965 | -0.26093 | -0.05951 | -0.041199 | -0.28839 | -0.49439 | -0.28381 | -0.045777 | 0.21973 | 60.7269 | 60.9604 | 122.0352 | 122.4701 | -0.041199 | 122.4838 | 60.6491 | -0.28381 | 122.4701 | -0.041199 | 60.6491 | 122.0352 | 122.4838 | -122.7905 | -122.8134
457.9062 | 122.8592 | -60.7086 | 61.8484 | -1.1555 | 0.0019482 | 0.0051632 | 0.0026191 | 0.064456 | -0.00071986 | 0.069848 | -60.7269 | 61.8118 | -60.9375 | -60.8414 | 61.5784 | 0.045776 | -0.18768 | 0.16937 | 61.7798 | -60.9833 | -0.22888 | -0.036621 | -0.018311 | -0.13275 | -0.27008 | -0.27466 | -0.068665 | 0.21057 | 60.5209 | 60.878 | 122.287 | 122.5204 | -0.018311 | 122.4884 | 60.7544 | -0.27466 | 122.5204 | -0.018311 | 60.7544 | 122.287 | 122.4884 | -122.7859 | -122.8317
458.9688 | 122.7997 | -60.7315 | 61.8622 | 0.16434 | 0.0057934 | 0.0032406 | 0.0049689 | 0.061466 | -0.0015745 | 0.067712 | -60.8276 | 61.8439 | -61.0016 | -60.9467 | 61.496 | -0.036621 | -0.068665 | 0.068665 | 61.8164 | -61.0153 | -0.27008 | -0.018311 | -0.096131 | -0.21515 | -0.36621 | -0.28381 | -0.045777 | 0.17395 | 60.6628 | 60.8002 | 122.2275 | 122.5754 | -0.096131 | 122.5479 | 60.6949 | -0.28381 | 122.5754 | -0.096131 | 60.6949 | 122.2275 | 122.5479 | -122.8638 | -122.8775
459.9062 | 122.8043 | -60.7224 | 61.8301 | 0.21011 | 0.004939 | 0.011358 | 0.0045417 | 0.065097 | -0.0024289 | 0.067926 | -60.8002 | 61.8759 | -61.0153 | -60.9192 | 61.5189 | -0.018311 | -0.13275 | 0.09613 | 61.8027 | -61.0153 | -0.29297 | 0.045777 | -0.07782 | -0.19684 | -0.31128 | -0.29297 | -0.027466 | 0.21515 | 60.5896 | 60.8185 | 122.2412 | 122.5983 | -0.07782 | 122.525 | 60.704 | -0.29297 | 122.5983 | -0.07782 | 60.704 | 122.2412 | 122.525 | -122.8455 | -122.8455
460.9531 | 122.7448 | -60.7315 | 61.8851 | 0.065155 | 0.006648 | 0.011145 | 0.0045417 | 0.067661 | -0.0022153 | 0.070489 | -60.8139 | 61.9125 | -61.0062 | -60.9512 | 61.4822 | -0.041199 | 0.041199 | 0.059509 | 61.8622 | -61.0153 | -0.27466 | 0.027466 | -0.082398 | -0.21973 | -0.40283 | -0.28381 | -0.022888 | 0.19226 | 60.7727 | 60.791 | 122.2137 | 122.644 | -0.082398 | 122.5937 | 60.6903 | -0.28381 | 122.644 | -0.082398 | 60.6903 | 122.2137 | 122.5937 | -122.8912 | -122.9004
461.9062 | 122.8226 | -60.6949 | 61.8439 | 0.19485 | 0.0030164 | 0.0038816 | -0.0022943 | 0.065525 | -0.0013609 | 0.070276 | -60.7773 | 61.7752 | -61.0016 | -60.8826 | 61.5829 | 0.045776 | -0.17853 | 0.16022 | 61.7798 | -60.9604 | -0.3067 | -0.068664 | -0.082398 | -0.18768 | -0.26093 | -0.2655 | -0.064087 | 0.2243 | 60.5164 | 60.8551 | 122.2778 | 122.4701 | -0.082398 | 122.4747 | 60.7407 | -0.2655 | 122.4701 | -0.082398 | 60.7407 | 122.2778 | 122.4747 | -122.8455 | -122.8043
462.9531 | 122.8317 | -60.6995 | 61.8439 | 0.24063 | 0.0038708 | 0.0083676 | 0.0043281 | 0.065311 | -0.0017881 | 0.066644 | -60.8093 | 61.821 | -61.0016 | -60.8871 | 61.5555 | 0.022888 | -0.16937 | 0.14648 | 61.7706 | -61.0016 | -0.30212 | -0.022888 | -0.10986 | -0.18768 | -0.28839 | -0.30212 | -0.073242 | 0.19226 | 60.5301 | 60.8459 | 122.2549 | 122.5204 | -0.10986 | 122.4701 | 60.7224 | -0.30212 | 122.5204 | -0.10986 | 60.7224 | 122.2549 | 122.4701 | -122.8455 | -122.8455
463.9062 | 122.8317 | -60.7315 | 61.8027 | 0.21011 | 0.0030164 | 0.011358 | 0.0004827 | 0.065525 | -0.00093346 | 0.06878 | -60.7361 | 61.8073 | -60.9512 | -60.8459 | 61.5967 | 0.054932 | -0.20599 | 0.16937 | 61.8073 | -60.9924 | -0.21973 | 0.004578 | -0.004578 | -0.11444 | -0.20599 | -0.26093 | 0.004578 | 0.21515 | 60.5255 | 60.9009 | 122.3282 | 122.5388 | -0.004578 | 122.5388 | 60.7864 | -0.26093 | 122.5388 | -0.004578 | 60.7864 | 122.3282 | 122.5388 | -122.7539 | -122.7951
464.9688 | 122.7219 | -60.7086 | 61.8896 | 0.11093 | 0.0051526 | 0.0062314 | 0.0032599 | 0.065097 | -0.0028561 | 0.069635 | -60.8368 | 61.8347 | -61.0474 | -60.9604 | 61.4685 | -0.073242 | 0.022888 | 0.032043 | 61.821 | -61.0153 | -0.33874 | -0.054931 | -0.12817 | -0.25177 | -0.42114 | -0.3067 | -0.068664 | 0.21057 | 60.7315 | 60.7407 | 122.1771 | 122.5433 | -0.12817 | 122.5296 | 60.6354 | -0.3067 | 122.5433 | -0.12817 | 60.6354 | 122.1771 | 122.5296 | -122.937 | -122.905
465.9062 | 122.8455 | -60.6766 | 61.8576 | 0.19485 | 0.0034436 | 0.011999 | 0.0017645 | 0.065525 | -0.0015745 | 0.067926 | -60.7681 | 61.8118 | -60.9695 | -60.8826 | 61.5646 | 0.018311 | -0.16479 | 0.15106 | 61.8027 | -60.9879 | -0.29297 | -0.045776 | -0.091552 | -0.20599 | -0.29297 | -0.31128 | -0.054932 | 0.20142 | 60.5118 | 60.8276 | 122.2412 | 122.4884 | -0.091552 | 122.4792 | 60.6949 | -0.31128 | 122.4884 | -0.091552 | 60.6949 | 122.2412 | 122.4792 | -122.8271 | -122.8455
466.9688 | 122.7585 | -60.6995 | 61.8805 | -0.049286 | 0.0047254 | 0.0085812 | 0.0039007 | 0.065952 | -0.0017881 | 0.067712 | -60.7727 | 61.8484 | -61.0016 | -60.8917 | 61.5463 | 0.041199 | 0.004578 | 0.16479 | 61.8668 | -60.9833 | -0.30212 | -0.032043 | -0.073242 | -0.19226 | -0.33417 | -0.28381 | -0.013733 | 0.22888 | 60.704 | 60.8643 | 122.2458 | 122.5479 | -0.073242 | 122.5662 | 60.7407 | -0.28381 | 122.5479 | -0.073242 | 60.7407 | 122.2458 | 122.5662 | -122.8821 | -122.8638
467.9062 | 122.7081 | -60.7407 | 61.8576 | 0.15671 | 0.0055798 | 0.010504 | 0.0039007 | 0.068088 | -0.0026425 | 0.067926 | -60.8231 | 61.9217 | -60.9604 | -60.9695 | 61.4685 | -0.054932 | 0.041199 | 0.036621 | 61.8851 | -61.0428 | -0.21973 | 0.064087 | -0.082397 | -0.22888 | -0.3891 | -0.30212 | 0.027466 | 0.13733 | 60.7819 | 60.7773 | 122.2092 | 122.6624 | -0.082397 | 122.6257 | 60.6857 | -0.30212 | 122.6624 | -0.082397 | 60.6857 | 122.2092 | 122.6257 | -122.818 | -122.9004
468.9062 | 122.7402 | -60.7315 | 61.8713 | -2.4831 | 0.004939 | 0.008154 | 0.0030463 | 0.066806 | -0.0034971 | 0.069207 | -60.8047 | 61.9217 | -60.965 | -60.9604 | 61.4822 | -0.073242 | 0.004578 | 0.068665 | 61.8805 | -61.0245 | -0.23346 | 0.050354 | -0.073243 | -0.22888 | -0.3891 | -0.29297 | 0.009155 | 0.16022 | 60.7361 | 60.8002 | 122.2137 | 122.6532 | -0.073243 | 122.612 | 60.6583 | -0.29297 | 122.6532 | -0.073243 | 60.6583 | 122.2137 | 122.612 | -122.8363 | -122.8958
469.9688 | 122.8088 | -60.7224 | 61.853 | 0.18723 | 0.0057934 | 0.0066586 | 0.0006965 | 0.068088 | -0.00071986 | 0.06878 | -60.8368 | 61.8301 | -61.0474 | -60.9375 | 61.5143 | -0.018311 | -0.091553 | 0.07782 | 61.8347 | -60.9924 | -0.32501 | -0.022888 | -0.11444 | -0.21515 | -0.33874 | -0.27008 | -0.01831 | 0.21057 | 60.6308 | 60.8002 | 122.2366 | 122.5525 | -0.11444 | 122.5571 | 60.704 | -0.27008 | 122.5525 | -0.11444 | 60.704 | 122.2366 | 122.5571 | -122.9004 | -122.8455
470.9062 | 122.8363 | -60.759 | 61.8942 | 0.080414 | 0.0064344 | 0.010077 | 0.0041143 | 0.068302 | -0.0024289 | 0.068567 | -60.8505 | 61.908 | -60.997 | -60.9787 | 61.4594 | -0.059509 | 0.013733 | -0.33875 | 61.8164 | -61.0794 | -0.23804 | 0.013733 | -0.091553 | -0.21973 | -0.43488 | -0.32044 | -0.07782 | 0.14648 | 60.7727 | 60.4202 | 122.2183 | 122.6669 | -0.091553 | 122.5754 | 60.6995 | -0.32044 | 122.6669 | -0.091553 | 60.6995 | 122.2183 | 122.5754 | -122.8912 | -122.9736
471.9688 | 122.7036 | -60.7178 | 61.8851 | 0.12619 | 0.0062208 | 0.0085812 | 0.0021917 | 0.06702 | -0.00050626 | 0.070703 | -60.8551 | 61.8942 | -61.0245 | -60.9787 | 61.3586 | -0.29755 | 0.050354 | 0.33875 | 61.8484 | -60.997 | -0.3067 | 0.009155 | -0.13733 | -0.26093 | -0.52643 | -0.27924 | -0.036621 | 0.16937 | 60.7681 | 61.0565 | 122.0764 | 122.612 | -0.13733 | 122.5662 | 60.4202 | -0.27924 | 122.612 | -0.13733 | 60.4202 | 122.0764 | 122.5662 | -122.9095 | -122.8821
472.9062 | 122.7905 | -60.7178 | 61.8439 | 0.17197 | 0.0047254 | 0.0062314 | 0.0011237 | 0.066593 | -0.00093346 | 0.068994 | -60.8139 | 61.8668 | -61.0016 | -60.9329 | 61.5234 | -0.009155 | -0.086975 | 0.07782 | 61.8256 | -61.0107 | -0.28381 | 0.022888 | -0.096131 | -0.21515 | -0.32043 | -0.29297 | -0.01831 | 0.18768 | 60.6308 | 60.7956 | 122.2412 | 122.5845 | -0.096131 | 122.5433 | 60.7086 | -0.29297 | 122.5845 | -0.096131 | 60.7086 | 122.2412 | 122.5433 | -122.8455 | -122.8546
473.9688 | 122.7997 | -60.7224 | 61.8393 | 0.24063 | 0.0077162 | 0.0087948 | 0.0004827 | 0.066806 | 0.0014163 | 0.067071 | -60.8185 | 61.8393 | -60.9924 | -60.9375 | 61.5143 | -0.018311 | -0.10071 | 0.073242 | 61.8164 | -61.0016 | -0.27008 | 0 | -0.09613 | -0.21515 | -0.32501 | -0.27924 | -0.022888 | 0.17395 | 60.6216 | 60.7956 | 122.2366 | 122.5616 | -0.09613 | 122.5388 | 60.704 | -0.27924 | 122.5616 | -0.09613 | 60.704 | 122.2366 | 122.5388 | -122.8317 | -122.8409
474.9062 | 122.8271 | -60.7178 | 61.8439 | 0.095673 | 0.0023756 | 0.008154 | -0.0048577 | 0.065525 | -0.00029266 | 0.068994 | -60.8185 | 61.7752 | -60.9741 | -60.9238 | 61.5601 | 0.022888 | -0.091553 | 0.15106 | 61.821 | -60.9741 | -0.25635 | -0.068664 | -0.10071 | -0.20599 | -0.28381 | -0.25635 | -0.022888 | 0.15564 | 60.6262 | 60.8688 | 122.2778 | 122.493 | -0.10071 | 122.5388 | 60.7407 | -0.25635 | 122.493 | -0.10071 | 60.7407 | 122.2778 | 122.5388 | -122.818 | -122.818
475.9688 | 122.7493 | -60.7086 | 61.8942 | -0.16373 | 0.0057934 | 0.0049496 | 0.0013373 | 0.065097 | -0.0028561 | 0.06878 | -60.8047 | 61.9217 | -60.9924 | -60.9283 | 61.5143 | 0.022888 | 0.15564 | 0.17395 | 61.8942 | -61.0336 | -0.28381 | 0.027466 | -0.096131 | -0.21973 | -0.37994 | -0.32501 | 0 | 0.18768 | 60.8643 | 60.8826 | 122.2229 | 122.6303 | -0.096131 | 122.6028 | 60.7315 | -0.32501 | 122.6303 | -0.096131 | 60.7315 | 122.2229 | 122.6028 | -122.8867 | -122.9279
476.9219 | 122.8409 | -60.6857 | 61.8668 | 0.034637 | 0.0051526 | 0.0060178 | -0.0063531 | 0.062534 | -0.0013609 | 0.068567 | -60.8139 | 61.8027 | -60.9879 | -60.8917 | 61.5692 | 0.059509 | -0.068665 | 0.21515 | 61.8118 | -60.9741 | -0.30212 | -0.064087 | -0.12817 | -0.20599 | -0.29755 | -0.28839 | -0.054931 | 0.17395 | 60.6171 | 60.9009 | 122.2549 | 122.4884 | -0.12817 | 122.4976 | 60.7452 | -0.28839 | 122.4884 | -0.12817 | 60.7452 | 122.2549 | 122.4976 | -122.8546 | -122.8409
477.9688 | 122.8226 | -60.6949 | 61.8851 | 0.065155 | 0.0038708 | 0.0090086 | -0.0033625 | 0.06232 | -0.00029266 | 0.067498 | -60.7864 | 61.8164 | -60.9467 | -60.91 | 61.5555 | 0.036621 | -0.086975 | 0.15106 | 61.7981 | -61.0336 | -0.25177 | -0.068665 | -0.091553 | -0.21515 | -0.32959 | -0.33875 | -0.086975 | 0.16022 | 60.6079 | 60.8459 | 122.2504 | 122.5113 | -0.091553 | 122.493 | 60.7315 | -0.33875 | 122.5113 | -0.091553 | 60.7315 | 122.2504 | 122.493 | -122.8317 | -122.9187
478.9062 | 122.7539 | -60.7361 | 61.8668 | 0.14145 | 0.008357 | 0.0058042 | 0.0051825 | 0.063602 | -0.00071986 | 0.067285 | -60.8414 | 61.8851 | -60.9879 | -60.9512 | 61.4868 | -0.050354 | -0.041199 | 0.045776 | 61.8347 | -61.0382 | -0.25177 | 0.018311 | -0.10529 | -0.21515 | -0.37994 | -0.30212 | -0.032043 | 0.14648 | 60.6949 | 60.7819 | 122.2229 | 122.6212 | -0.10529 | 122.5708 | 60.6857 | -0.30212 | 122.6212 | -0.10529 | 60.6857 | 122.2229 | 122.5708 | -122.8546 | -122.905
479.9688 | 122.7722 | -60.7086 | 61.8851 | 0.072784 | 0.0034436 | 0.008154 | 0.0049689 | 0.064884 | -0.0026425 | 0.065362 | -60.8002 | 61.8668 | -60.997 | -60.9375 | 61.4777 | -0.022888 | 0.013733 | 0.073242 | 61.8713 | -61.0153 | -0.28839 | -0.018311 | -0.091553 | -0.22888 | -0.40741 | -0.3067 | -0.013733 | 0.19684 | 60.7224 | 60.7819 | 122.1863 | 122.5754 | -0.091553 | 122.58 | 60.6857 | -0.3067 | 122.5754 | -0.091553 | 60.6857 | 122.1863 | 122.58 | -122.8821 | -122.9004
480.9062 | 122.7859 | -60.7132 | 61.8622 | 0.011749 | 0.0068616 | 0.010077 | 0.0049689 | 0.064456 | -0.00029266 | 0.06643 | -60.7819 | 61.9034 | -60.997 | -60.91 | 61.4914 | -0.009155 | 0.032043 | 0.12817 | 61.8713 | -61.0199 | -0.28381 | 0.041198 | -0.068664 | -0.19684 | -0.37079 | -0.3067 | 0.009155 | 0.21515 | 60.7452 | 60.8414 | 122.2046 | 122.6166 | -0.068664 | 122.5845 | 60.704 | -0.3067 | 122.6166 | -0.068664 | 60.704 | 122.2046 | 122.5845 | -122.8592 | -122.8821
481.9688 | 122.7676 | -60.7086 | 61.8622 | -0.041657 | 0.0079298 | 0.011572 | 0.0039007 | 0.065738 | -0.0011471 | 0.068353 | -60.7727 | 61.9034 | -61.0016 | -60.9283 | 61.5097 | 0.004578 | 0.018311 | 0.13275 | 61.853 | -61.0199 | -0.29297 | 0.041198 | -0.064087 | -0.21973 | -0.35248 | -0.31128 | -0.009156 | 0.22888 | 60.7269 | 60.8414 | 122.2183 | 122.612 | -0.064087 | 122.5616 | 60.7132 | -0.31128 | 122.612 | -0.064087 | 60.7132 | 122.2183 | 122.5616 | -122.8638 | -122.8821
482.9219 | 122.818 | -60.6949 | 61.853 | -0.11795 | 0.00323 | 0.0038816 | -0.0050715 | 0.065952 | -0.00093346 | 0.069635 | -60.8322 | 61.7935 | -61.0062 | -60.9146 | 61.5601 | 0.050354 | -0.07782 | 0.18768 | 61.853 | -60.9467 | -0.31128 | -0.059509 | -0.13733 | -0.21973 | -0.29297 | -0.25177 | 0 | 0.17395 | 60.6171 | 60.8826 | 122.2549 | 122.4884 | -0.13733 | 122.5479 | 60.7452 | -0.25177 | 122.4884 | -0.13733 | 60.7452 | 122.2549 | 122.5479 | -122.8592 | -122.7997
483.9688 | 122.7814 | -60.6995 | 61.8851 | -0.049286 | 0.0051526 | 0.013922 | 0.0053961 | 0.06467 | -0.0011471 | 0.068567 | -60.7544 | 61.8622 | -60.9833 | -60.8871 | 61.5417 | 0.050354 | 0.018311 | 0.14191 | 61.8439 | -61.0428 | -0.28381 | -0.022888 | -0.054932 | -0.18768 | -0.34332 | -0.34332 | -0.041199 | 0.22888 | 60.7178 | 60.8414 | 122.2412 | 122.5616 | -0.054932 | 122.5433 | 60.7498 | -0.34332 | 122.5616 | -0.054932 | 60.7498 | 122.2412 | 122.5433 | -122.8683 | -122.9279
484.9062 | 122.8546 | -60.6857 | 61.8393 | 0.28641 | 0.00323 | 0.0075132 | -0.0010125 | 0.065311 | -0.0026425 | 0.067498 | -60.7452 | 61.8027 | -60.9695 | -60.8688 | 61.5967 | 0.036621 | -0.18768 | 0.1831 | 61.8118 | -60.997 | -0.28381 | -0.036621 | -0.059509 | -0.1831 | -0.24261 | -0.31128 | -0.027465 | 0.2243 | 60.498 | 60.8688 | 122.2824 | 122.4884 | -0.059509 | 122.4976 | 60.7224 | -0.31128 | 122.4884 | -0.059509 | 60.7224 | 122.2824 | 122.4976 | -122.8088 | -122.8363
485.9531 | 122.731 | -60.7224 | 61.8622 | 0.095673 | 0.0070752 | 0.0032406 | 0.0049689 | 0.066379 | -0.00029266 | 0.068994 | -60.7819 | 61.8759 | -61.0062 | -60.9467 | 61.5005 | -0.027466 | 0.027466 | 0.082397 | 61.853 | -61.0565 | -0.28381 | 0.013733 | -0.059509 | -0.2243 | -0.36163 | -0.33417 | -0.009156 | 0.22431 | 60.7498 | 60.8047 | 122.2229 | 122.5983 | -0.059509 | 122.5754 | 60.6949 | -0.33417 | 122.5983 | -0.059509 | 60.6949 | 122.2229 | 122.5754 | -122.8683 | -122.9187
486.9062 | 122.8729 | -60.6903 | 61.8118 | 0.21011 | 0.0036572 | 0.0060178 | 0.0045417 | 0.069156 | -0.00029266 | 0.065789 | -60.7544 | 61.8301 | -60.9833 | -60.7086 | 61.7294 | 0.054932 | -0.21973 | 0.21973 | 61.8439 | -60.9879 | -0.29297 | 0.01831 | -0.064087 | -0.01831 | -0.082398 | -0.29755 | 0.032043 | 0.22888 | 60.4706 | 60.91 | 122.4197 | 122.5204 | -0.064087 | 122.5342 | 60.7452 | -0.29755 | 122.5204 | -0.064087 | 60.7452 | 122.4197 | 122.5342 | -122.7951 | -122.7997
487.9688 | 122.8043 | -60.7407 | 61.8805 | 0.088043 | 0.0040846 | 0.003668 | 0.0039007 | 0.066593 | 0.00013454 | 0.070489 | -60.8597 | 61.8759 | -61.0336 | -60.9695 | 61.4639 | -0.073242 | -0.14191 | -0.33875 | 61.7844 | -61.0474 | -0.29297 | -0.004577 | -0.11902 | -0.22888 | -0.41656 | -0.3067 | -0.09613 | 0.17395 | 60.5988 | 60.4019 | 122.2046 | 122.6166 | -0.11902 | 122.525 | 60.6674 | -0.3067 | 122.6166 | -0.11902 | 60.6674 | 122.2046 | 122.525 | -122.9141 | -122.9279
488.9062 | 122.7036 | -60.7498 | 61.8759 | 0.072784 | 0.006648 | 0.0060178 | 0.0041143 | 0.067661 | -0.0011471 | 0.06878 | -60.7864 | 61.908 | -60.9787 | -60.9467 | 61.5097 | -0.027466 | 0.041199 | 0.054932 | 61.8393 | -61.0336 | -0.22888 | 0.032043 | -0.036621 | -0.19684 | -0.36621 | -0.28381 | -0.036622 | 0.19226 | 60.791 | 60.8047 | 122.2595 | 122.6578 | -0.036621 | 122.5891 | 60.7224 | -0.28381 | 122.6578 | -0.036621 | 60.7224 | 122.2595 | 122.5891 | -122.8546 | -122.9095
489.9688 | 122.7859 | -60.6949 | 61.8942 | -0.17899 | 0.0045118 | 0.0083676 | 0.0030463 | 0.068088 | -0.0022153 | 0.067926 | -60.7864 | 61.8988 | -60.9741 | -60.8963 | 61.5646 | 0.073242 | 0.09613 | 0.21057 | 61.9125 | -60.9741 | -0.27924 | 0.004578 | -0.091553 | -0.20142 | -0.32959 | -0.27924 | 0.018311 | 0.18768 | 60.791 | 60.9055 | 122.2595 | 122.5937 | -0.091553 | 122.6074 | 60.7681 | -0.27924 | 122.5937 | -0.091553 | 60.7681 | 122.2595 | 122.6074 | -122.8683 | -122.8683
490.9062 | 122.7676 | -60.7178 | 61.8393 | 0.233 | 0.0045118 | 0.0068722 | 0.0030463 | 0.067661 | -0.0017881 | 0.068567 | -60.8322 | 61.908 | -60.9879 | -60.9604 | 61.4777 | -0.054932 | -0.004578 | 0.054932 | 61.8668 | -61.0611 | -0.27008 | 0.068665 | -0.11444 | -0.24262 | -0.36163 | -0.34332 | 0.027466 | 0.15564 | 60.7132 | 60.7727 | 122.1954 | 122.6257 | -0.11444 | 122.5845 | 60.6628 | -0.34332 | 122.6257 | -0.11444 | 60.6628 | 122.1954 | 122.5845 | -122.8271 | -122.9004
491.9688 | 122.7448 | -60.6857 | 61.8851 | 0.034637 | 0.0051526 | 0.010504 | 0.0011237 | 0.067661 | -0.0017881 | 0.068139 | -60.7773 | 61.8713 | -61.0016 | -60.9238 | 61.5097 | -0.004578 | 0.027466 | 0.14191 | 61.8759 | -61.0153 | -0.31586 | -0.013733 | -0.091553 | -0.23804 | -0.37537 | -0.32959 | -0.009155 | 0.2243 | 60.7132 | 60.8276 | 122.1954 | 122.5571 | -0.091553 | 122.5616 | 60.6812 | -0.32959 | 122.5571 | -0.091553 | 60.6812 | 122.1954 | 122.5616 | -122.8867 | -122.9004
492.9062 | 122.8455 | -60.6674 | 61.8256 | -0.52231 | 0.0013074 | 0.0062314 | -0.0022943 | 0.066379 | -0.00050626 | 0.06878 | -60.6171 | 61.8439 | -60.9512 | -60.8688 | 61.5829 | 0.050354 | -0.20599 | 0.1831 | 61.7889 | -61.0062 | -0.28381 | 0.01831 | 0.050354 | -0.20142 | -0.24262 | -0.33875 | -0.036622 | 0.33417 | 60.4614 | 60.8505 | 122.2504 | 122.5113 | 0.050354 | 122.4564 | 60.7178 | -0.33875 | 122.5113 | 0.050354 | 60.7178 | 122.2504 | 122.4564 | -122.7768 | -122.8317
493.9531 | 122.7493 | -60.7178 | 61.8988 | 0.72128 | 0.0057934 | 0.0058042 | 0.0015509 | 0.064884 | -0.0011471 | 0.067071 | -60.8093 | 61.9171 | -61.0153 | -60.9192 | 61.5417 | 0.068665 | 0.13733 | 0.17853 | 61.8851 | -61.0016 | -0.29755 | 0.01831 | -0.091553 | -0.20142 | -0.35706 | -0.28381 | -0.013733 | 0.20599 | 60.8551 | 60.8963 | 122.2595 | 122.6349 | -0.091553 | 122.6028 | 60.7864 | -0.28381 | 122.6349 | -0.091553 | 60.7864 | 122.2595 | 122.6028 | -122.9141 | -122.9004
494.9062 | 122.7219 | -60.7544 | 61.8805 | 0.080414 | 0.0064344 | 0.0092222 | 0.0036871 | 0.063175 | -0.0020017 | 0.068353 | -60.8139 | 61.9034 | -60.965 | -60.9879 | 61.4731 | -0.045776 | 0.041199 | 0.059509 | 61.853 | -61.0336 | -0.21057 | 0.022888 | -0.059509 | -0.23346 | -0.40741 | -0.27923 | -0.027466 | 0.15106 | 60.7956 | 60.8139 | 122.2275 | 122.6578 | -0.059509 | 122.6074 | 60.7086 | -0.27923 | 122.6578 | -0.059509 | 60.7086 | 122.2275 | 122.6074 | -122.8455 | -122.9141
495.9531 | 122.7814 | -60.704 | 61.8896 | -0.22476 | 0.0034436 | 0.004736 | 0.0032599 | 0.067447 | -0.00029266 | 0.066858 | -60.7773 | 61.9354 | -60.9787 | -60.9009 | 61.5601 | 0.073242 | 0.082397 | 0.20599 | 61.8805 | -61.0062 | -0.27466 | 0.045777 | -0.073242 | -0.19684 | -0.32959 | -0.30212 | -0.009155 | 0.20142 | 60.7864 | 60.91 | 122.2641 | 122.6395 | -0.073242 | 122.5845 | 60.7773 | -0.30212 | 122.6395 | -0.073242 | 60.7773 | 122.2641 | 122.5845 | -122.8683 | -122.8958
496.9062 | 122.7402 | -60.7315 | 61.8759 | 0.049896 | 0.0057934 | 0.0087948 | 0.0047553 | 0.067447 | -0.0015745 | 0.067498 | -60.8002 | 61.9034 | -60.9833 | -60.9283 | 61.5189 | -0.013733 | 0.022888 | 0.091553 | 61.8851 | -61.0245 | -0.25177 | 0.027465 | -0.068665 | -0.19684 | -0.35706 | -0.29297 | 0.009155 | 0.1831 | 60.7544 | 60.8231 | 122.2504 | 122.6349 | -0.068665 | 122.6166 | 60.7178 | -0.29297 | 122.6349 | -0.068665 | 60.7178 | 122.2504 | 122.6166 | -122.8592 | -122.9004
497.9688 | 122.8363 | -60.7269 | 61.821 | 0.15671 | 0.0034436 | 0.0058042 | -0.0012261 | 0.068088 | -0.0011471 | 0.070276 | -60.7498 | 61.8256 | -60.9512 | -60.878 | 61.5921 | 0.054932 | -0.17853 | 0.16479 | 61.8256 | -60.9924 | -0.2243 | 0.004578 | -0.022888 | -0.15106 | -0.22888 | -0.2655 | 0.004578 | 0.20142 | 60.5484 | 60.8917 | 122.319 | 122.5525 | -0.022888 | 122.5525 | 60.7819 | -0.2655 | 122.5525 | -0.022888 | 60.7819 | 122.319 | 122.5525 | -122.7722 | -122.8134
498.9062 | 122.7631 | -60.7452 | 61.8668 | -0.0035098 | 0.0075024 | 0.010717 | 0.0032599 | 0.067874 | 0.00013454 | 0.06878 | -60.7544 | 61.8988 | -60.9787 | -60.9009 | 61.528 | 0.027466 | 0.018311 | 0.13275 | 61.8851 | -61.0336 | -0.23346 | 0.032044 | -0.009156 | -0.15564 | -0.33874 | -0.28839 | 0.018311 | 0.2243 | 60.7635 | 60.878 | 122.2733 | 122.644 | -0.009156 | 122.6303 | 60.7727 | -0.28839 | 122.644 | -0.009156 | 60.7727 | 122.2733 | 122.6303 | -122.8455 | -122.9004
499.9688 | 122.731 | -60.7361 | 61.8896 | -0.20187 | 0.0042982 | 0.004736 | -0.0014399 | 0.065738 | 0.0012027 | 0.068139 | -60.8002 | 61.9308 | -60.9741 | -60.965 | 61.4182 | -0.1236 | 0.18768 | 0.19226 | 61.8988 | -61.0107 | -0.23804 | 0.041199 | -0.064087 | -0.22888 | -0.4715 | -0.27466 | 0.009156 | 0.17395 | 60.9238 | 60.9283 | 122.1542 | 122.6669 | -0.064087 | 122.6349 | 60.6125 | -0.27466 | 122.6669 | -0.064087 | 60.6125 | 122.1542 | 122.6349 | -122.8638 | -122.9004
500.9062 | 122.7951 | -60.7224 | 61.8713 | -0.018768 | 0.0060072 | 0.0068722 | 0.0039007 | 0.067234 | -0.0011471 | 0.068139 | -60.7361 | 61.9125 | -60.9787 | -60.9009 | 61.5463 | 0.054932 | 0.013733 | 0.16937 | 61.8622 | -61.0016 | -0.25635 | 0.041199 | -0.013733 | -0.17853 | -0.32501 | -0.27924 | -0.009155 | 0.24262 | 60.7361 | 60.8917 | 122.2687 | 122.6349 | -0.013733 | 122.5845 | 60.7773 | -0.27924 | 122.6349 | -0.013733 | 60.7773 | 122.2687 | 122.5845 | -122.85 | -122.8729
501.9688 | 122.731 | -60.7086 | 61.9217 | -0.23239 | 0.006648 | 0.008154 | -0.0029351 | 0.064243 | -0.0032835 | 0.070062 | -60.8047 | 61.9034 | -60.9787 | -60.9329 | 61.5234 | 0.068665 | 0.12817 | 0.18768 | 61.9171 | -61.0291 | -0.27008 | -0.018311 | -0.096131 | -0.2243 | -0.39825 | -0.32043 | -0.004578 | 0.17395 | 60.8368 | 60.8963 | 122.2321 | 122.612 | -0.096131 | 122.6257 | 60.7773 | -0.32043 | 122.612 | -0.096131 | 60.7773 | 122.2321 | 122.6257 | -122.9004 | -122.9507
502.9062 | 122.7722 | -60.704 | 61.8759 | 0.034637 | 0.0040846 | 0.011145 | 0.0041143 | 0.068729 | 0.00056194 | 0.071344 | -60.7681 | 61.8942 | -60.9924 | -60.9192 | 61.5189 | 0.027466 | 0 | 0.13733 | 61.8805 | -61.0107 | -0.28839 | 0.01831 | -0.064086 | -0.21515 | -0.35706 | -0.3067 | 0.004577 | 0.22431 | 60.704 | 60.8414 | 122.2229 | 122.5983 | -0.064086 | 122.5845 | 60.7315 | -0.3067 | 122.5983 | -0.064086 | 60.7315 | 122.2229 | 122.5845 | -122.8683 | -122.8867
503.9688 | 122.7997 | -60.7269 | 61.8622 | -0.17899 | 0.0045118 | 0.008154 | 0.0021917 | 0.066593 | 0.00056194 | 0.069848 | -60.7544 | 61.9354 | -60.9833 | -60.8505 | 61.5692 | 0.064087 | 0.073242 | 0.21057 | 61.8759 | -61.0474 | -0.25635 | 0.073242 | -0.027466 | -0.1236 | -0.29297 | -0.32043 | 0.013733 | 0.22888 | 60.8002 | 60.9375 | 122.2961 | 122.6624 | -0.027466 | 122.6028 | 60.791 | -0.32043 | 122.6624 | -0.027466 | 60.791 | 122.2961 | 122.6028 | -122.8455 | -122.9095
504.9062 | 122.7127 | -60.7361 | 61.8851 | 0.15671 | 0.0072888 | 0.0066586 | 0.0058233 | 0.070438 | -7.9062e-05 | 0.067071 | -60.8597 | 61.9125 | -61.0199 | -60.7544 | 61.5921 | -0.086975 | 0.059509 | 0.10986 | 61.8759 | -61.0245 | -0.28381 | 0.027466 | -0.1236 | -0.018311 | -0.29297 | -0.28839 | -0.009155 | 0.16022 | 60.7956 | 60.8459 | 122.3282 | 122.6486 | -0.1236 | 122.612 | 60.6491 | -0.28839 | 122.6486 | -0.1236 | 60.6491 | 122.3282 | 122.612 | -122.905 | -122.9095
505.9531 | 122.8043 | -60.704 | 61.8805 | -0.14847 | 0.0036572 | 0.009863 | 0.0006965 | 0.066379 | -0.00050626 | 0.068567 | -60.8047 | 61.9034 | -60.9741 | -60.9055 | 61.5646 | 0.068665 | 0.11444 | 0.18768 | 61.8988 | -61.0062 | -0.27008 | 0.022888 | -0.10071 | -0.20142 | -0.31586 | -0.30212 | 0.018311 | 0.16937 | 60.8185 | 60.8917 | 122.2687 | 122.6074 | -0.10071 | 122.6028 | 60.7727 | -0.30212 | 122.6074 | -0.10071 | 60.7727 | 122.2687 | 122.6028 | -122.8546 | -122.8867
506.9062 | 122.7493 | -60.7132 | 61.8576 | 0.19485 | 0.0062208 | 0.0077268 | 0.0011237 | 0.065952 | -0.0015745 | 0.069848 | -60.8322 | 61.8896 | -61.0062 | -60.9741 | 61.4868 | -0.050354 | -0.027466 | 0.041199 | 61.8759 | -61.0336 | -0.29297 | 0.032043 | -0.11902 | -0.26092 | -0.37079 | -0.32043 | 0.018311 | 0.17395 | 60.6857 | 60.7544 | 122.2 | 122.6028 | -0.11902 | 122.5891 | 60.6628 | -0.32043 | 122.6028 | -0.11902 | 60.6628 | 122.2 | 122.5891 | -122.8638 | -122.8912
507.9531 | 122.7676 | -60.7086 | 61.8942 | -0.24765 | 0.0038708 | 0.0068722 | -0.0037897 | 0.065311 | -0.0013609 | 0.06878 | -60.7498 | 61.8805 | -60.9787 | -60.9009 | 61.5875 | 0.082397 | 0.10986 | 0.22888 | 61.8851 | -60.9833 | -0.27008 | -0.013733 | -0.041199 | -0.19226 | -0.3067 | -0.27466 | -0.009155 | 0.22888 | 60.8185 | 60.9375 | 122.2961 | 122.5891 | -0.041199 | 122.5937 | 60.791 | -0.27466 | 122.5891 | -0.041199 | 60.791 | 122.2961 | 122.5937 | -122.8729 | -122.8775
508.9062 | 122.731 | -60.7544 | 61.8851 | 0.080414 | 0.0040846 | 0.0094358 | 0.0015509 | 0.066165 | -0.0020017 | 0.069848 | -60.8185 | 61.8805 | -61.0062 | -60.9558 | 61.4777 | -0.054932 | 0.032043 | 0.050354 | 61.8576 | -61.0428 | -0.25177 | -0.004578 | -0.064086 | -0.20142 | -0.40741 | -0.28839 | -0.027466 | 0.18768 | 60.7864 | 60.8047 | 122.2321 | 122.6349 | -0.064086 | 122.612 | 60.6995 | -0.28839 | 122.6349 | -0.064086 | 60.6995 | 122.2321 | 122.612 | -122.8912 | -122.9279
509.9688 | 122.7493 | -60.6995 | 61.8896 | -0.1561 | 0.006648 | 0.0023862 | 0.0006965 | 0.065311 | -0.0022153 | 0.067926 | -60.8002 | 61.908 | -60.9924 | -60.9192 | 61.5372 | 0.064087 | 0.13275 | 0.16022 | 61.8805 | -60.9879 | -0.29297 | 0.018311 | -0.10071 | -0.21973 | -0.35248 | -0.28839 | -0.009155 | 0.19226 | 60.8322 | 60.8597 | 122.2366 | 122.6074 | -0.10071 | 122.58 | 60.7636 | -0.28839 | 122.6074 | -0.10071 | 60.7636 | 122.2366 | 122.58 | -122.8821 | -122.8775
510.9062 | 122.7127 | -60.7544 | 61.8851 | 0.080414 | 0.0051526 | 0.010504 | 0.0047553 | 0.065738 | 0.0012027 | 0.066858 | -60.8047 | 61.9125 | -60.9833 | -60.9558 | 61.496 | -0.036621 | 0.032043 | 0.091553 | 61.8713 | -61.0107 | -0.22888 | 0.027466 | -0.050354 | -0.20142 | -0.3891 | -0.25635 | -0.013733 | 0.17853 | 60.7864 | 60.8459 | 122.2504 | 122.6669 | -0.050354 | 122.6257 | 60.7178 | -0.25635 | 122.6669 | -0.050354 | 60.7178 | 122.2504 | 122.6257 | -122.8683 | -122.8958
511.9531 | 122.7997 | -60.7086 | 61.8713 | -0.14084 | 0.0051526 | 0.0085812 | 0.0002691 | 0.06702 | 0.0016299 | 0.068567 | -60.759 | 61.8942 | -60.9833 | -60.8826 | 61.5646 | 0.045776 | 0.041199 | 0.20142 | 61.908 | -61.0291 | -0.27466 | 0.022888 | -0.050354 | -0.17395 | -0.3067 | -0.32043 | 0.036621 | 0.2243 | 60.7498 | 60.91 | 122.2733 | 122.6028 | -0.050354 | 122.6166 | 60.7544 | -0.32043 | 122.6028 | -0.050354 | 60.7544 | 122.2733 | 122.6166 | -122.8546 | -122.9004
512.9062 | 122.8043 | -60.6949 | 61.8759 | -0.19424 | 0.0055798 | 0.010931 | 0.0032599 | 0.065097 | -0.0017881 | 0.068139 | -60.7452 | 61.8805 | -61.0016 | -60.878 | 61.5601 | 0.07782 | 0.041199 | 0.19684 | 61.8851 | -60.9879 | -0.3067 | 0.004577 | -0.050354 | -0.18311 | -0.31586 | -0.29297 | 0.009155 | 0.25635 | 60.7361 | 60.8917 | 122.2549 | 122.5754 | -0.050354 | 122.58 | 60.7727 | -0.29297 | 122.5754 | -0.050354 | 60.7727 | 122.2549 | 122.58 | -122.8775 | -122.8638
513.9688 | 122.7631 | -60.7224 | 61.9217 | -0.25528 | 0.0055798 | 0.0055906 | -0.0010125 | 0.066806 | 0.00056194 | 0.069207 | -60.7864 | 61.8942 | -60.9833 | -60.9192 | 61.5646 | 0.068665 | 0.1236 | 0.21057 | 61.8805 | -61.0428 | -0.26092 | -0.027466 | -0.064087 | -0.19684 | -0.35706 | -0.32043 | -0.041199 | 0.19684 | 60.8459 | 60.9329 | 122.287 | 122.6166 | -0.064087 | 122.6028 | 60.791 | -0.32043 | 122.6166 | -0.064087 | 60.791 | 122.287 | 122.6028 | -122.905 | -122.9645
514.9062 | 122.7264 | -60.7452 | 61.8805 | 2.6668 | 0.0051526 | 0.011572 | 0.0011237 | 0.064884 | 0.00098914 | 0.06878 | -60.6766 | 61.8896 | -61.0062 | -60.9924 | 61.5051 | -0.050354 | -0.009155 | 0.036621 | 61.853 | -61.0474 | -0.26093 | 0.009155 | 0.068664 | -0.24719 | -0.37537 | -0.30212 | -0.027466 | 0.32959 | 60.7361 | 60.7819 | 122.2504 | 122.6349 | 0.068664 | 122.5983 | 60.6949 | -0.30212 | 122.6349 | 0.068664 | 60.6949 | 122.2504 | 122.5983 | -122.8867 | -122.9279
515.9688 | 122.7631 | -60.7086 | 61.8851 | -0.24765 | 0.0028028 | 0.0049496 | -0.0025079 | 0.062961 | -0.0011471 | 0.067498 | -60.8231 | 61.8851 | -60.9833 | -60.9283 | 61.4548 | 0.10529 | 0.33875 | 0.045776 | 61.9217 | -60.997 | -0.27466 | 0 | -0.11444 | -0.21973 | -0.4303 | -0.28839 | 0.036621 | 0.16022 | 61.0474 | 60.7544 | 122.1634 | 122.5937 | -0.11444 | 122.6303 | 60.8139 | -0.28839 | 122.5937 | -0.11444 | 60.8139 | 122.1634 | 122.6303 | -122.8683 | -122.8821
516.9062 | 122.7814 | -60.7224 | 61.8622 | -0.034027 | 0.008357 | 0.0083676 | 0.0032599 | 0.066379 | -0.00093346 | 0.068994 | -60.7315 | 61.9217 | -60.9879 | -60.8963 | 61.5372 | 0.041199 | 0.032043 | 0.17853 | 61.853 | -61.0153 | -0.2655 | 0.059509 | -0.009155 | -0.17395 | -0.32501 | -0.29297 | -0.009156 | 0.25635 | 60.7544 | 60.9009 | 122.2595 | 122.644 | -0.009155 | 122.5754 | 60.7636 | -0.29297 | 122.644 | -0.009155 | 60.7636 | 122.2595 | 122.5754 | -122.85 | -122.8775
517.9688 | 122.7448 | -60.7224 | 61.9034 | 0.042267 | 0.0030164 | 0.0077268 | -0.0005853 | 0.067447 | -0.0017881 | 0.070489 | -60.8185 | 61.9354 | -61.0153 | -60.9375 | 61.5326 | 0.045776 | 0.15106 | 0.17395 | 61.8942 | -61.0062 | -0.29297 | 0.032044 | -0.09613 | -0.21515 | -0.37079 | -0.28381 | -0.009155 | 0.19684 | 60.8734 | 60.8963 | 122.2549 | 122.6578 | -0.09613 | 122.6166 | 60.7681 | -0.28381 | 122.6578 | -0.09613 | 60.7681 | 122.2549 | 122.6166 | -122.9187 | -122.9095
518.9062 | 122.7905 | -60.7407 | 61.8896 | -0.24002 | 0.00323 | 0.0083676 | 0.0004827 | 0.066806 | -0.00029266 | 0.06643 | -60.7727 | 61.908 | -60.9879 | -60.878 | 61.5738 | 0.07782 | 0.073242 | 0.21515 | 61.8759 | -60.997 | -0.24719 | 0.018311 | -0.032043 | -0.13733 | -0.31586 | -0.25635 | -0.013732 | 0.21515 | 60.8139 | 60.9558 | 122.3145 | 122.6486 | -0.032043 | 122.6166 | 60.8185 | -0.25635 | 122.6486 | -0.032043 | 60.8185 | 122.3145 | 122.6166 | -122.8775 | -122.8867
519.9531 | 122.731 | -60.7132 | 61.908 | -0.087433 | 0.0038708 | 0.0079404 | -0.0018671 | 0.065097 | -7.9062e-05 | 0.067926 | -60.8231 | 61.9171 | -60.9787 | -60.9283 | 61.5417 | 0.054932 | 0.14191 | 0.17853 | 61.9217 | -61.0153 | -0.2655 | 0.009155 | -0.10986 | -0.21515 | -0.36621 | -0.30212 | 0.013733 | 0.15564 | 60.8551 | 60.8917 | 122.2549 | 122.6303 | -0.10986 | 122.6349 | 60.7681 | -0.30212 | 122.6303 | -0.10986 | 60.7681 | 122.2549 | 122.6349 | -122.8867 | -122.9233
520.9062 | 122.7997 | -60.7132 | 61.8896 | -0.1561 | 0.0047254 | 0.0075132 | 0.0030463 | 0.066165 | -0.00029266 | 0.067926 | -60.7544 | 61.908 | -60.9833 | -60.878 | 61.5555 | 0.082397 | 0.032043 | 0.18768 | 61.8759 | -61.0199 | -0.27008 | 0.018311 | -0.041199 | -0.16479 | -0.33417 | -0.3067 | -0.013732 | 0.22888 | 60.7452 | 60.9009 | 122.2687 | 122.6212 | -0.041199 | 122.5891 | 60.7956 | -0.3067 | 122.6212 | -0.041199 | 60.7956 | 122.2687 | 122.5891 | -122.8729 | -122.9095
521.9531 | 122.7219 | -60.704 | 61.9217 | -0.2095 | 0.0047254 | 0.0051632 | -0.0014399 | 0.066379 | -0.0017881 | 0.067071 | -60.8093 | 61.9217 | -60.997 | -60.91 | 61.5372 | 0.041199 | 0.13733 | 0.17853 | 61.908 | -61.0153 | -0.29297 | 0 | -0.10529 | -0.20599 | -0.38452 | -0.31128 | -0.013733 | 0.18768 | 60.8414 | 60.8826 | 122.2412 | 122.6257 | -0.10529 | 122.612 | 60.7452 | -0.31128 | 122.6257 | -0.10529 | 60.7452 | 122.2412 | 122.612 | -122.9187 | -122.937
522.9062 | 122.7173 | -60.7315 | 61.9034 | -0.17899 | 0.0042982 | 0.003027 | -0.0033625 | 0.064243 | -0.00029266 | 0.067071 | -60.8185 | 61.8942 | -60.9924 | -60.9192 | 61.5417 | 0.013733 | 0.42572 | 0.09613 | 61.9537 | -60.9833 | -0.26093 | -0.009155 | -0.086975 | -0.18768 | -0.36163 | -0.25177 | 0.050354 | 0.17395 | 61.1572 | 60.8276 | 122.2733 | 122.6257 | -0.086975 | 122.6852 | 60.7452 | -0.25177 | 122.6257 | -0.086975 | 60.7452 | 122.2733 | 122.6852 | -122.8958 | -122.8867
523.9531 | 122.7768 | -60.7132 | 61.8851 | -0.19424 | 0.0040846 | 0.0058042 | 0.0026191 | 0.066379 | -0.0011471 | 0.067071 | -60.7956 | 61.9308 | -60.9741 | -60.8963 | 61.5509 | 0.07782 | 0.10071 | 0.20599 | 61.8851 | -61.0062 | -0.26092 | 0.045776 | -0.082397 | -0.1831 | -0.33417 | -0.29297 | 0 | 0.17853 | 60.8139 | 60.9192 | 122.2641 | 122.644 | -0.082397 | 122.5983 | 60.791 | -0.29297 | 122.644 | -0.082397 | 60.791 | 122.2641 | 122.5983 | -122.8592 | -122.8912
524.9062 | 122.7951 | -60.7132 | 61.8713 | -0.049286 | 0.0030164 | 0.0068722 | 0.0011237 | 0.067234 | -0.0026425 | 0.068994 | -60.7498 | 61.8942 | -60.9924 | -60.8826 | 61.5463 | 0.073242 | 0.041199 | 0.20599 | 61.9034 | -61.0107 | -0.27924 | 0.022888 | -0.036621 | -0.16937 | -0.32501 | -0.29755 | 0.032043 | 0.24262 | 60.7544 | 60.9192 | 122.2595 | 122.6074 | -0.036621 | 122.6166 | 60.7864 | -0.29755 | 122.6074 | -0.036621 | 60.7864 | 122.2595 | 122.6166 | -122.8638 | -122.8821
525.9688 | 122.9004 | -60.6857 | 61.8851 | -1.7049 | 0.001521 | 0.0055906 | -0.0054987 | 0.066593 | 0.00034814 | 0.067285 | -60.5209 | 61.9034 | -60.9283 | -60.8276 | 61.6379 | 0.14648 | -0.045776 | 0.31586 | 61.8439 | -60.9787 | -0.24262 | 0.01831 | 0.16479 | -0.14191 | -0.24719 | -0.29297 | -0.041199 | 0.40741 | 60.64 | 61.0016 | 122.3236 | 122.5891 | 0.16479 | 122.5296 | 60.8322 | -0.29297 | 122.5891 | 0.16479 | 60.8322 | 122.3236 | 122.5296 | -122.8134 | -122.8638
526.9062 | 122.7448 | -60.7315 | 61.8713 | -0.40787 | 0.0057934 | 0.0068722 | 0.0036871 | 0.065952 | -0.00029266 | 0.067712 | -60.8963 | 61.8805 | -61.0199 | -60.9741 | 61.4548 | -0.064087 | -0.004578 | 0.041199 | 61.8439 | -61.0291 | -0.28839 | 0.009155 | -0.16479 | -0.24261 | -0.41656 | -0.29755 | -0.027466 | 0.1236 | 60.7269 | 60.7727 | 122.1863 | 122.612 | -0.16479 | 122.5754 | 60.6674 | -0.29755 | 122.612 | -0.16479 | 60.6674 | 122.1863 | 122.5754 | -122.8912 | -122.9004
527.9531 | 122.7631 | -60.7086 | 61.9263 | -0.17136 | 0.0051526 | 0.0023862 | 0.0002691 | 0.063388 | -7.9062e-05 | 0.067926 | -60.8047 | 61.8988 | -61.0062 | -60.9192 | 61.5189 | 0.045776 | 0.13733 | 0.1831 | 61.9034 | -61.0016 | -0.29755 | -0.027466 | -0.096131 | -0.21057 | -0.40741 | -0.29297 | -0.022889 | 0.20142 | 60.8459 | 60.8917 | 122.2275 | 122.6074 | -0.096131 | 122.612 | 60.7544 | -0.29297 | 122.6074 | -0.096131 | 60.7544 | 122.2275 | 122.612 | -122.9324 | -122.9279
528.9062 | 122.7768 | -60.7361 | 61.8805 | -0.1561 | 0.0036572 | 0.0087948 | 0.0011237 | 0.065525 | -0.0011471 | 0.066644 | -60.7864 | 61.9308 | -60.9741 | -60.878 | 61.5601 | 0.059509 | 0.10529 | 0.21973 | 61.908 | -60.9833 | -0.23804 | 0.050354 | -0.050354 | -0.14191 | -0.32043 | -0.24719 | 0.027466 | 0.18768 | 60.8414 | 60.9558 | 122.2961 | 122.6669 | -0.050354 | 122.644 | 60.7956 | -0.24719 | 122.6669 | -0.050354 | 60.7956 | 122.2961 | 122.644 | -122.8546 | -122.8638
529.9688 | 122.7905 | -60.7224 | 61.8988 | -0.18662 | 0.0040846 | 0.0096494 | 0.0013373 | 0.066165 | -0.0024289 | 0.069421 | -60.7819 | 61.9034 | -60.9879 | -60.8917 | 61.5509 | 0.068665 | 0.10529 | 0.19684 | 61.9034 | -60.9833 | -0.2655 | 0.004577 | -0.059509 | -0.16937 | -0.3479 | -0.26092 | 0.004577 | 0.20599 | 60.8276 | 60.9192 | 122.2733 | 122.6257 | -0.059509 | 122.6257 | 60.791 | -0.26092 | 122.6257 | -0.059509 | 60.791 | 122.2733 | 122.6257 | -122.8867 | -122.8821
530.9062 | 122.7859 | -60.704 | 61.9263 | -0.17136 | 0.0034436 | 0.0085812 | -0.0007989 | 0.067661 | -0.00071986 | 0.069207 | -60.8093 | 61.908 | -61.0062 | -60.9283 | 61.5417 | 0.059509 | 0.10529 | 0.17853 | 61.8896 | -61.0062 | -0.30212 | -0.018311 | -0.10529 | -0.2243 | -0.38452 | -0.30212 | -0.036622 | 0.19684 | 60.8093 | 60.8826 | 122.2458 | 122.612 | -0.10529 | 122.5937 | 60.7635 | -0.30212 | 122.612 | -0.10529 | 60.7635 | 122.2458 | 122.5937 | -122.9324 | -122.9324
531.9688 | 122.7402 | -60.704 | 61.8942 | -0.011139 | 0.0057934 | 0.012426 | 0.0053961 | 0.068515 | -0.0015745 | 0.067071 | -60.7727 | 61.8851 | -61.0062 | -60.9192 | 61.528 | 0.004578 | 0.009155 | 0.11902 | 61.8759 | -61.0016 | -0.30212 | -0.009155 | -0.068664 | -0.21515 | -0.36621 | -0.29755 | -0.01831 | 0.23346 | 60.7132 | 60.8231 | 122.2321 | 122.5891 | -0.068664 | 122.58 | 60.7086 | -0.29755 | 122.5891 | -0.068664 | 60.7086 | 122.2321 | 122.58 | -122.9004 | -122.8958
532.9062 | 122.7539 | -60.6949 | 61.9171 | -0.17899 | 0.0070752 | 0.0049496 | 0.0006965 | 0.065525 | 0.00034814 | 0.066858 | -60.8047 | 61.8805 | -60.997 | -60.9238 | 61.5234 | 0.032043 | 0.13275 | 0.1831 | 61.9308 | -60.9879 | -0.30212 | -0.036621 | -0.10986 | -0.22888 | -0.39368 | -0.29297 | 0.013733 | 0.19226 | 60.8276 | 60.878 | 122.2183 | 122.5754 | -0.10986 | 122.6257 | 60.7269 | -0.29297 | 122.5754 | -0.10986 | 60.7269 | 122.2183 | 122.6257 | -122.9141 | -122.905
533.9688 | 122.7859 | -60.6857 | 61.9034 | -0.2095 | 0.0047254 | 0.006445 | -0.0035761 | 0.065952 | -0.0020017 | 0.066644 | -60.7681 | 61.8759 | -60.9467 | -60.8826 | 61.5829 | 0.10986 | 0.10986 | 0.24261 | 61.8713 | -61.0062 | -0.26093 | -0.027465 | -0.082397 | -0.19684 | -0.32043 | -0.32044 | -0.032043 | 0.17853 | 60.7956 | 60.9283 | 122.2687 | 122.5616 | -0.082397 | 122.5571 | 60.7956 | -0.32044 | 122.5616 | -0.082397 | 60.7956 | 122.2687 | 122.5571 | -122.85 | -122.9095
534.9062 | 122.7905 | -60.7086 | 61.9217 | -0.17899 | 0.0047254 | 0.0060178 | 0.0034735 | 0.066379 | -0.0011471 | 0.067926 | -60.7864 | 61.8988 | -60.9741 | -60.8871 | 61.5417 | 0.07782 | 0.086975 | 0.21057 | 61.853 | -60.997 | -0.2655 | -0.022888 | -0.07782 | -0.17853 | -0.37994 | -0.28839 | -0.068665 | 0.18768 | 60.7956 | 60.9192 | 122.2504 | 122.6074 | -0.07782 | 122.5616 | 60.7864 | -0.28839 | 122.6074 | -0.07782 | 60.7864 | 122.2504 | 122.5616 | -122.8958 | -122.9187
535.9688 | 122.8088 | -60.7132 | 61.8942 | -0.26291 | 0.0013074 | 0.0021726 | -0.0044305 | 0.066165 | -0.0034971 | 0.067712 | -60.7498 | 61.8439 | -60.9558 | -60.8688 | 61.6058 | 0.12817 | 0.068665 | 0.2655 | 61.8668 | -60.9604 | -0.24261 | -0.050354 | -0.036621 | -0.15564 | -0.28839 | -0.24719 | -0.027466 | 0.20599 | 60.7819 | 60.9787 | 122.319 | 122.5571 | -0.036621 | 122.58 | 60.8414 | -0.24719 | 122.5571 | -0.036621 | 60.8414 | 122.319 | 122.58 | -122.85 | -122.8546
536.9062 | 122.7859 | -60.7224 | 61.8942 | -0.17136 | 0.0051526 | 0.0045224 | 0.0030463 | 0.065738 | 0.00077554 | 0.068994 | -60.7544 | 61.8851 | -61.0016 | -60.8917 | 61.528 | 0.054932 | 0.013733 | 0.17395 | 61.8622 | -60.997 | -0.27924 | -0.009155 | -0.032044 | -0.16937 | -0.36621 | -0.27466 | -0.032043 | 0.24719 | 60.7361 | 60.8963 | 122.2504 | 122.6074 | -0.032044 | 122.5845 | 60.7773 | -0.27466 | 122.6074 | -0.032044 | 60.7773 | 122.2504 | 122.5845 | -122.8958 | -122.8912
537.9531 | 122.7676 | -60.704 | 61.9034 | -0.25528 | 0.0051526 | 0.0062314 | -0.0016535 | 0.065525 | 0.00056194 | 0.068353 | -60.7636 | 61.8896 | -60.9604 | -60.8963 | 61.5692 | 0.07782 | 0.1236 | 0.21515 | 61.9171 | -61.0153 | -0.25635 | -0.013733 | -0.059509 | -0.19226 | -0.33417 | -0.31128 | 0.013733 | 0.19684 | 60.8276 | 60.9192 | 122.2733 | 122.5937 | -0.059509 | 122.6212 | 60.7819 | -0.31128 | 122.5937 | -0.059509 | 60.7819 | 122.2733 | 122.6212 | -122.8638 | -122.9187
538.9062 | 122.8088 | -60.704 | 61.8896 | -0.034027 | 0.0045118 | 0.0096494 | 0.0075323 | 0.068729 | -0.0024289 | 0.067712 | -60.7498 | 61.9034 | -60.9833 | -60.8139 | 61.5875 | 0.064087 | 0.027466 | 0.20142 | 61.8576 | -61.0107 | -0.27923 | 0.013733 | -0.045776 | -0.10986 | -0.30212 | -0.3067 | -0.032043 | 0.23346 | 60.7315 | 60.9055 | 122.2916 | 122.6074 | -0.045776 | 122.5616 | 60.7681 | -0.3067 | 122.6074 | -0.045776 | 60.7681 | 122.2916 | 122.5616 | -122.8729 | -122.9004
539.9688 | 122.7036 | -60.7452 | 61.8805 | 0.072784 | 0.0057934 | 0.0058042 | 0.0049689 | 0.067874 | -0.0022153 | 0.066644 | -60.7956 | 61.8805 | -61.0107 | -60.9512 | 61.5051 | -0.027466 | 0.022888 | 0.068665 | 61.8713 | -61.0428 | -0.2655 | 0 | -0.050354 | -0.20599 | -0.37537 | -0.29755 | -0.009155 | 0.21515 | 60.7681 | 60.8139 | 122.2504 | 122.6257 | -0.050354 | 122.6166 | 60.7178 | -0.29755 | 122.6257 | -0.050354 | 60.7178 | 122.2504 | 122.6166 | -122.8912 | -122.9233
540.9062 | 122.731 | -60.7269 | 61.9034 | -0.18662 | 0.0042982 | 0.0079404 | 0.0011237 | 0.065097 | -7.9062e-05 | 0.068567 | -60.8139 | 61.8851 | -61.0016 | -60.9283 | 61.5234 | 0.050354 | 0.14648 | 0.18768 | 61.8896 | -60.997 | -0.27466 | -0.01831 | -0.086975 | -0.20142 | -0.37994 | -0.27008 | -0.013733 | 0.18768 | 60.8734 | 60.9146 | 122.2504 | 122.612 | -0.086975 | 122.6166 | 60.7773 | -0.27008 | 122.612 | -0.086975 | 60.7773 | 122.2504 | 122.6166 | -122.905 | -122.9004
541.9688 | 122.7356 | -60.7224 | 61.8759 | 0.14145 | 0.0057934 | 0.0083676 | 0.0006965 | 0.065952 | 0.00098914 | 0.068353 | -60.8322 | 61.8805 | -60.9924 | -60.9695 | 61.496 | -0.050354 | -0.022888 | 0.045776 | 61.8576 | -61.0291 | -0.27008 | 0.004577 | -0.10986 | -0.24719 | -0.37994 | -0.3067 | -0.018311 | 0.16022 | 60.6995 | 60.7681 | 122.2183 | 122.6028 | -0.10986 | 122.58 | 60.672 | -0.3067 | 122.6028 | -0.10986 | 60.672 | 122.2183 | 122.58 | -122.8683 | -122.905
542.9062 | 122.7814 | -60.6857 | 61.8851 | -0.14084 | 0.006648 | 0.006445 | 0.0021917 | 0.066806 | -0.00093346 | 0.066644 | -60.7681 | 61.908 | -60.9741 | -60.878 | 61.5555 | 0.068665 | 0.045776 | 0.20142 | 61.8851 | -61.0199 | -0.28839 | 0.022888 | -0.082397 | -0.19226 | -0.32959 | -0.33417 | 0 | 0.20599 | 60.7315 | 60.8871 | 122.2412 | 122.5937 | -0.082397 | 122.5708 | 60.7544 | -0.33417 | 122.5937 | -0.082397 | 60.7544 | 122.2412 | 122.5708 | -122.8592 | -122.905
543.9688 | 122.7951 | -60.6903 | 61.8439 | 0.088043 | 0.0025892 | 0.0079404 | -0.0042169 | 0.065525 | 0.0018435 | 0.069848 | -60.8047 | 61.821 | -60.9695 | -60.9192 | 61.5692 | 0.041199 | -0.073242 | 0.37994 | 61.8576 | -60.9558 | -0.27923 | -0.022888 | -0.11444 | -0.22888 | -0.27466 | -0.2655 | 0.013733 | 0.16479 | 60.6171 | 61.0703 | 122.2595 | 122.5113 | -0.11444 | 122.5479 | 60.7315 | -0.2655 | 122.5113 | -0.11444 | 60.7315 | 122.2595 | 122.5479 | -122.8134 | -122.7997
544.9219 | 122.7676 | -60.7178 | 61.8484 | 0.1796 | 0.0038708 | 0.0049496 | 0.0032599 | 0.066379 | 0.00098914 | 0.068353 | -60.8185 | 61.8576 | -60.997 | -60.9512 | 61.496 | -0.050354 | -0.068665 | 0.059509 | 61.8256 | -61.0336 | -0.27924 | 0.009155 | -0.10071 | -0.23346 | -0.35248 | -0.31586 | -0.022888 | 0.17853 | 60.6491 | 60.7773 | 122.2137 | 122.5754 | -0.10071 | 122.5433 | 60.6674 | -0.31586 | 122.5754 | -0.10071 | 60.6674 | 122.2137 | 122.5433 | -122.8455 | -122.8821
545.9531 | 122.8775 | -60.6949 | 61.8393 | -0.049286 | 0.0040846 | 0.0062314 | -0.0050715 | 0.063175 | -0.0020017 | 0.067498 | -60.7544 | 61.8484 | -60.9512 | -60.8093 | 61.6653 | 0.14648 | -0.10071 | 0.30212 | 61.8164 | -60.9924 | -0.25635 | 0.009156 | -0.05951 | -0.11444 | -0.17395 | -0.29755 | -0.022888 | 0.19684 | 60.5942 | 60.997 | 122.3602 | 122.5433 | -0.05951 | 122.5113 | 60.8414 | -0.29755 | 122.5433 | -0.05951 | 60.8414 | 122.3602 | 122.5113 | -122.7905 | -122.8317
546.9219 | 122.8638 | -60.7086 | 61.853 | 0.15671 | 0.0045118 | 0.0070858 | 0.0015509 | 0.062534 | 0.0020571 | 0.068353 | -60.7407 | 61.7889 | -60.965 | -60.878 | 61.5555 | 0.054932 | -0.16937 | 0.16022 | 61.8027 | -60.9879 | -0.25635 | -0.064087 | -0.032044 | -0.16937 | -0.29755 | -0.27924 | -0.050354 | 0.2243 | 60.5392 | 60.8688 | 122.2641 | 122.4976 | -0.032044 | 122.5113 | 60.7636 | -0.27924 | 122.4976 | -0.032044 | 60.7636 | 122.2641 | 122.5113 | -122.818 | -122.8409
547.9688 | 122.7402 | -60.7315 | 61.9034 | -0.25528 | 0.0028028 | 0.011145 | -0.0003717 | 0.062534 | -0.0026425 | 0.067926 | -60.8322 | 61.8668 | -60.9604 | -60.9146 | 61.528 | 0.050354 | 0.12817 | 0.19684 | 61.8851 | -61.0291 | -0.22888 | -0.036621 | -0.10071 | -0.18311 | -0.37537 | -0.29755 | -0.01831 | 0.12817 | 60.8597 | 60.9283 | 122.2595 | 122.5983 | -0.10071 | 122.6166 | 60.7819 | -0.29755 | 122.5983 | -0.10071 | 60.7819 | 122.2595 | 122.6166 | -122.8638 | -122.9324
548.9062 | 122.7493 | -60.7361 | 61.8988 | -0.17899 | 0.00323 | 0.0034544 | -0.0029351 | 0.064884 | -0.00050626 | 0.067285 | -60.8231 | 61.8759 | -60.9741 | -61.0474 | 61.5234 | 0.045776 | 0.12817 | 0.15564 | 61.8805 | -61.0016 | -0.23804 | -0.022888 | -0.086975 | -0.31128 | -0.37537 | -0.2655 | -0.018311 | 0.15106 | 60.8643 | 60.8917 | 122.2595 | 122.612 | -0.086975 | 122.6166 | 60.7819 | -0.2655 | 122.612 | -0.086975 | 60.7819 | 122.2595 | 122.6166 | -122.8729 | -122.9004
549.9688 | 122.9233 | -60.6812 | 61.8805 | 0.17197 | 0.0034436 | 0.003027 | -0.0033625 | 0.064029 | -0.0017881 | 0.067712 | -60.8185 | 61.8073 | -60.965 | -60.9055 | 61.5463 | 0.018311 | -0.091553 | 0.16479 | 61.8393 | -60.9467 | -0.28381 | -0.073242 | -0.13733 | -0.22431 | -0.33417 | -0.2655 | -0.041199 | 0.14648 | 60.5896 | 60.8459 | 122.2275 | 122.4884 | -0.13733 | 122.5204 | 60.6995 | -0.2655 | 122.4884 | -0.13733 | 60.6995 | 122.2275 | 122.5204 | -122.8455 | -122.8271
550.9062 | 122.7676 | -60.7315 | 61.8896 | -0.19424 | 0.0047254 | 0.0092222 | 0.0024053 | 0.062747 | -0.00050626 | 0.066858 | -60.7956 | 61.8942 | -60.9787 | -60.9283 | 61.5234 | 0.027466 | 0.13733 | 0.17395 | 61.8759 | -61.0245 | -0.24719 | 0.004578 | -0.064087 | -0.19684 | -0.36621 | -0.29297 | -0.013732 | 0.18311 | 60.8688 | 60.9055 | 122.2549 | 122.6257 | -0.064087 | 122.6074 | 60.759 | -0.29297 | 122.6257 | -0.064087 | 60.759 | 122.2549 | 122.6074 | -122.8683 | -122.9141
551.9688 | 122.818 | -60.7178 | 61.8393 | 0.18723 | 0.0030164 | 0.0066586 | 0.0056097 | 0.065097 | -0.00050626 | 0.068567 | -60.7956 | 61.8851 | -61.0016 | -60.8963 | 61.5463 | -0.009155 | -0.16479 | 0.13275 | 61.821 | -60.997 | -0.28381 | 0.045777 | -0.07782 | -0.17853 | -0.29297 | -0.27924 | -0.01831 | 0.20599 | 60.553 | 60.8505 | 122.2641 | 122.6028 | -0.07782 | 122.5388 | 60.7086 | -0.27924 | 122.6028 | -0.07782 | 60.7086 | 122.2641 | 122.5388 | -122.8409 | -122.8363
552.9062 | 122.7402 | -60.7224 | 61.8896 | -0.16373 | 0.0055798 | 0.0051632 | 0.0041143 | 0.065525 | -0.0013609 | 0.066858 | -60.9924 | 61.8759 | -61.0245 | -60.9329 | 61.528 | 0.050354 | 0.16022 | 0.17853 | 61.8851 | -61.0107 | -0.30212 | -0.013732 | -0.27008 | -0.21057 | -0.36163 | -0.28839 | -0.004577 | 0.032043 | 60.8826 | 60.9009 | 122.2504 | 122.5983 | -0.27008 | 122.6074 | 60.7727 | -0.28839 | 122.5983 | -0.27008 | 60.7727 | 122.2504 | 122.6074 | -122.9141 | -122.9004
553.9688 | 122.8592 | -60.6857 | 61.8576 | -0.064545 | 0.0051526 | 0.0017454 | -0.0031489 | 0.06467 | -0.0013609 | 0.067926 | -60.7773 | 61.8118 | -60.9558 | -60.8459 | 61.6104 | 0.1236 | -0.086975 | 0.2655 | 61.8301 | -60.9787 | -0.27008 | -0.045776 | -0.091553 | -0.16022 | -0.24719 | -0.29297 | -0.027466 | 0.17853 | 60.5988 | 60.9512 | 122.2961 | 122.4976 | -0.091553 | 122.5159 | 60.8093 | -0.29297 | 122.4976 | -0.091553 | 60.8093 | 122.2961 | 122.5159 | -122.8134 | -122.8363
554.9219 | 122.7448 | -60.7498 | 61.8622 | 0.0041197 | 0.0055798 | 0.010931 | 0.0058233 | 0.064884 | -0.0017881 | 0.06878 | -60.6079 | 61.8942 | -60.9604 | -60.9467 | 61.4822 | -0.068665 | -0.013733 | 0.036621 | 61.8439 | -61.0703 | -0.21057 | 0.032043 | 0.14191 | -0.19684 | -0.37994 | -0.32043 | -0.018311 | 0.35248 | 60.7361 | 60.7864 | 122.2321 | 122.644 | 0.14191 | 122.5937 | 60.6812 | -0.32043 | 122.644 | 0.14191 | 60.6812 | 122.2321 | 122.5937 | -122.8226 | -122.9324
555.9844 | 122.7997 | -60.6995 | 61.853 | -0.018768 | 0.0051526 | 0.0023862 | -0.0037897 | 0.064029 | 0.0014163 | 0.06878 | -60.8093 | 61.853 | -60.9741 | -60.8871 | 61.5829 | 0.027466 | -0.064087 | 0.18768 | 61.8393 | -60.997 | -0.27466 | 0 | -0.10986 | -0.18768 | -0.27008 | -0.29755 | -0.013733 | 0.16479 | 60.6354 | 60.8871 | 122.2824 | 122.5525 | -0.10986 | 122.5388 | 60.7269 | -0.29755 | 122.5525 | -0.10986 | 60.7269 | 122.2824 | 122.5388 | -122.8271 | -122.85
556.9062 | 122.7814 | -60.704 | 61.8805 | -0.095062 | 0.0028028 | 0.008154 | 0.0049689 | 0.063175 | -0.0032835 | 0.068567 | -60.7452 | 61.8576 | -60.9695 | -60.8597 | 61.5417 | 0.07782 | 0.032043 | 0.21973 | 61.8576 | -60.997 | -0.2655 | -0.022888 | -0.041198 | -0.15564 | -0.33875 | -0.29297 | -0.022888 | 0.2243 | 60.7361 | 60.9238 | 122.2458 | 122.5616 | -0.041198 | 122.5616 | 60.7819 | -0.29297 | 122.5616 | -0.041198 | 60.7819 | 122.2458 | 122.5616 | -122.85 | -122.8775
557.9062 | 122.7585 | -60.6857 | 61.9034 | -0.24002 | 0.002162 | 0.0049496 | -0.0029351 | 0.063602 | -0.0024289 | 0.067285 | -60.7681 | 61.853 | -60.9741 | -60.8871 | 61.5646 | 0.073242 | 0.10071 | 0.23346 | 61.8896 | -60.9924 | -0.28839 | -0.050354 | -0.082397 | -0.20142 | -0.33875 | -0.3067 | -0.013733 | 0.20599 | 60.7864 | 60.9192 | 122.2504 | 122.5388 | -0.082397 | 122.5754 | 60.759 | -0.3067 | 122.5388 | -0.082397 | 60.759 | 122.2504 | 122.5754 | -122.8775 | -122.8958
558.9062 | 122.7585 | -60.7132 | 61.908 | -0.22476 | 0.0047254 | 0.0032406 | 0.0011237 | 0.062107 | -0.0022153 | 0.065576 | -60.7864 | 61.908 | -60.9879 | -60.9192 | 61.5509 | 0.045776 | 0.11444 | 0.18768 | 61.8622 | -60.997 | -0.27466 | 0 | -0.073242 | -0.20599 | -0.35706 | -0.28381 | -0.045776 | 0.20142 | 60.8276 | 60.9009 | 122.2641 | 122.6212 | -0.073242 | 122.5754 | 60.759 | -0.28381 | 122.6212 | -0.073242 | 60.759 | 122.2641 | 122.5754 | -122.8958 | -122.905
559.9062 | 122.7356 | -60.6995 | 61.8988 | -0.21713 | 0.0045118 | 0.0040952 | 0.0004827 | 0.065311 | -0.0011471 | 0.068994 | -60.8185 | 61.8851 | -60.9924 | -60.91 | 61.5326 | 0.032043 | 0.11902 | 0.17853 | 61.9171 | -60.9924 | -0.29297 | -0.013733 | -0.11902 | -0.21057 | -0.36621 | -0.29297 | 0.01831 | 0.17395 | 60.8185 | 60.878 | 122.2321 | 122.5845 | -0.11902 | 122.6166 | 60.7315 | -0.29297 | 122.5845 | -0.11902 | 60.7315 | 122.2321 | 122.6166 | -122.8912 | -122.8912
560.9531 | 122.8271 | -60.7224 | 61.8484 | 0.1796 | 0.0013074 | 0.0066586 | -0.0022943 | 0.065738 | -0.0013609 | 0.067712 | -60.8139 | 61.7981 | -60.9879 | -60.8963 | 61.5509 | 0.022888 | -0.13733 | 0.13275 | 61.8073 | -60.9695 | -0.2655 | -0.050354 | -0.091553 | -0.17395 | -0.29755 | -0.24719 | -0.041199 | 0.17395 | 60.585 | 60.8551 | 122.2733 | 122.5204 | -0.091553 | 122.5296 | 60.7452 | -0.24719 | 122.5204 | -0.091553 | 60.7452 | 122.2733 | 122.5296 | -122.8363 | -122.818
561.9062 | 122.8455 | -60.7086 | 61.8301 | 0.18723 | 0.00323 | 0.005377 | 0.0034735 | 0.063816 | 0.00013454 | 0.06878 | -60.7544 | 61.7935 | -60.9695 | -60.8551 | 61.5829 | 0.050354 | -0.19226 | 0.15106 | 61.7935 | -60.9741 | -0.26093 | -0.036621 | -0.045777 | -0.14648 | -0.24719 | -0.2655 | -0.036621 | 0.21515 | 60.5164 | 60.8597 | 122.2916 | 122.5021 | -0.045777 | 122.5021 | 60.759 | -0.2655 | 122.5021 | -0.045777 | 60.759 | 122.2916 | 122.5021 | -122.7997 | -122.8043
562.9688 | 122.8683 | -60.6537 | 61.8393 | -0.16373 | -0.00018804 | 0.0023862 | -0.0031489 | 0.062961 | -0.00050626 | 0.06878 | -60.4523 | 61.8576 | -60.9375 | -60.8414 | 61.6425 | 0.15106 | -0.082397 | 0.32044 | 61.8027 | -60.9512 | -0.28381 | 0.018311 | 0.20142 | -0.18768 | -0.19684 | -0.29755 | -0.036621 | 0.48523 | 60.5713 | 60.9741 | 122.2961 | 122.5113 | 0.20142 | 122.4564 | 60.8047 | -0.29755 | 122.5113 | 0.20142 | 60.8047 | 122.2961 | 122.4564 | -122.7768 | -122.7905
563.9062 | 122.7631 | -60.7315 | 61.8805 | -0.20187 | 0.0042982 | 0.0038816 | 0.0013373 | 0.063175 | -0.0030697 | 0.067712 | -60.8185 | 61.8713 | -60.9833 | -60.9146 | 61.4227 | 0.16022 | 0.30212 | 0.032043 | 61.8942 | -60.9604 | -0.25177 | -0.009155 | -0.086975 | -0.18311 | -0.45776 | -0.22888 | 0.013733 | 0.16479 | 61.0336 | 60.7635 | 122.1542 | 122.6028 | -0.086975 | 122.6257 | 60.8917 | -0.22888 | 122.6028 | -0.086975 | 60.8917 | 122.1542 | 122.6257 | -122.8638 | -122.8409
564.9531 | 122.7905 | -60.704 | 61.9308 | -0.12558 | 0.0045118 | 0.0049496 | 0.0056097 | 0.063602 | -0.0024289 | 0.067926 | -60.7864 | 61.8713 | -60.9879 | -60.8734 | 61.5692 | 0.073242 | 0.086975 | 0.19684 | 61.8805 | -60.9879 | -0.28381 | -0.059509 | -0.082397 | -0.16937 | -0.36163 | -0.28381 | -0.050354 | 0.20142 | 60.791 | 60.9009 | 122.2733 | 122.5754 | -0.082397 | 122.5845 | 60.7773 | -0.28381 | 122.5754 | -0.082397 | 60.7773 | 122.2733 | 122.5845 | -122.9187 | -122.9187
565.9062 | 122.7493 | -60.7224 | 61.908 | -0.43076 | 0.0075024 | 0.001959 | 0.0013373 | 0.067447 | -0.0013609 | 0.067071 | -60.8047 | 61.8622 | -61.0062 | -60.8963 | 61.5372 | 0.045776 | 0.12817 | 0.17853 | 61.8805 | -60.9741 | -0.28381 | -0.045776 | -0.082398 | -0.17395 | -0.37079 | -0.25177 | -0.027466 | 0.20142 | 60.8505 | 60.9009 | 122.2595 | 122.5845 | -0.082398 | 122.6028 | 60.7681 | -0.25177 | 122.5845 | -0.082398 | 60.7681 | 122.2595 | 122.6028 | -122.9141 | -122.8821
566.9688 | 122.7356 | -60.7361 | 61.8668 | 0.019379 | 0.0047254 | 0.008154 | 0.0066779 | 0.064243 | -0.0026425 | 0.069635 | -60.7819 | 61.8393 | -60.9741 | -60.9055 | 61.5189 | 0 | 0.009155 | 0.11444 | 61.853 | -61.0107 | -0.23804 | -0.027466 | -0.045776 | -0.16937 | -0.3479 | -0.27466 | -0.013733 | 0.19226 | 60.7452 | 60.8505 | 122.2549 | 122.5754 | -0.045776 | 122.5891 | 60.7361 | -0.27466 | 122.5754 | -0.045776 | 60.7361 | 122.2549 | 122.5891 | -122.8409 | -122.8775
567.9062 | 122.7722 | -60.6903 | 61.8988 | -0.20187 | 0.0034436 | 0.0040952 | -0.0033625 | 0.064456 | -0.0013609 | 0.068139 | -60.7681 | 61.8301 | -60.9787 | -60.8551 | 61.5875 | 0.11444 | 0.082397 | 0.25177 | 61.8576 | -60.9604 | -0.28839 | -0.068665 | -0.077819 | -0.16479 | -0.31128 | -0.27008 | -0.041199 | 0.21057 | 60.7727 | 60.9421 | 122.2778 | 122.5204 | -0.077819 | 122.5479 | 60.8047 | -0.27008 | 122.5204 | -0.077819 | 60.8047 | 122.2778 | 122.5479 | -122.8775 | -122.8592
568.9688 | 122.8592 | -60.6766 | 61.8668 | -0.27054 | 0.0023756 | -0.00060462 | -0.0031489 | 0.063175 | -0.0015745 | 0.068353 | -60.7361 | 61.7981 | -60.9375 | -60.8231 | 61.6241 | 0.15564 | -0.032043 | 0.29297 | 61.8393 | -60.9375 | -0.26093 | -0.068664 | -0.059509 | -0.14648 | -0.24261 | -0.26093 | -0.027466 | 0.20142 | 60.6445 | 60.9695 | 122.3007 | 122.4747 | -0.059509 | 122.5159 | 60.8322 | -0.26093 | 122.4747 | -0.059509 | 60.8322 | 122.3007 | 122.5159 | -122.8043 | -122.8043
569.9062 | 122.7539 | -60.7086 | 61.9125 | -0.27054 | 0.0030164 | 0.0066586 | -0.0010125 | 0.062747 | -0.0028561 | 0.069207 | -60.7956 | 61.8439 | -60.9604 | -60.878 | 61.5417 | 0.050354 | 0.10529 | 0.21973 | 61.8759 | -60.9787 | -0.25177 | -0.068665 | -0.086975 | -0.16937 | -0.37079 | -0.27008 | -0.036621 | 0.1648 | 60.8139 | 60.9283 | 122.2504 | 122.5525 | -0.086975 | 122.5845 | 60.759 | -0.27008 | 122.5525 | -0.086975 | 60.759 | 122.2504 | 122.5845 | -122.8729 | -122.8912
570.9688 | 122.9095 | -60.6903 | 61.853 | -0.14084 | 0.0017346 | -0.0018862 | -0.0005853 | 0.056552 | -0.0034971 | 0.06878 | -60.7315 | 61.7844 | -60.9512 | -60.9283 | 61.3815 | -0.022888 | -0.004578 | 0.27466 | 61.821 | -60.9192 | -0.26093 | -0.068664 | -0.041198 | -0.23804 | -0.4715 | -0.22888 | -0.032043 | 0.21973 | 60.6857 | 60.965 | 122.0718 | 122.4747 | -0.041198 | 122.5113 | 60.6674 | -0.22888 | 122.4747 | -0.041198 | 60.6674 | 122.0718 | 122.5113 | -122.8043 | -122.7722
571.9062 | 122.7676 | -60.7178 | 61.9171 | -0.24002 | 0.0047254 | 0.0066586 | 0.0045417 | 0.062747 | -0.0017881 | 0.068139 | -60.8185 | 61.8622 | -60.9787 | -60.91 | 61.5326 | 0.050354 | 0.13275 | 0.16937 | 61.8622 | -60.9787 | -0.26093 | -0.054931 | -0.10071 | -0.19226 | -0.38452 | -0.26093 | -0.054931 | 0.16022 | 60.8505 | 60.8871 | 122.2504 | 122.58 | -0.10071 | 122.58 | 60.7681 | -0.26093 | 122.58 | -0.10071 | 60.7681 | 122.2504 | 122.58 | -122.8958 | -122.8958
572.9688 | 122.7493 | -60.6995 | 61.9034 | -0.14847 | 0.0034436 | 0.0040952 | 0.0071051 | 0.063175 | -0.0026425 | 0.065789 | -60.759 | 61.8347 | -61.0016 | -60.8688 | 61.5417 | 0.068665 | 0.032043 | 0.19226 | 61.853 | -60.9879 | -0.30212 | -0.068664 | -0.059509 | -0.16937 | -0.36163 | -0.28839 | -0.050354 | 0.24262 | 60.7315 | 60.8917 | 122.2412 | 122.5342 | -0.059509 | 122.5525 | 60.7681 | -0.28839 | 122.5342 | -0.059509 | 60.7681 | 122.2412 | 122.5525 | -122.905 | -122.8912
573.9062 | 122.7768 | -60.704 | 61.9034 | -0.24765 | 0.0030164 | 0.0062314 | -0.0014399 | 0.063388 | -0.0011471 | 0.066858 | -60.7727 | 61.8301 | -60.9512 | -60.8871 | 61.5692 | 0.064087 | 0.082397 | 0.21515 | 61.8896 | -60.9787 | -0.24719 | -0.073242 | -0.068664 | -0.18311 | -0.33417 | -0.27466 | -0.013733 | 0.17853 | 60.7864 | 60.9192 | 122.2733 | 122.5342 | -0.068664 | 122.5937 | 60.7681 | -0.27466 | 122.5342 | -0.068664 | 60.7681 | 122.2733 | 122.5937 | -122.8546 | -122.8821
574.9688 | 122.731 | -60.7224 | 61.9034 | -0.24002 | 0.004939 | 0.0079404 | 0.0024053 | 0.06702 | -0.0041379 | 0.066644 | -60.7956 | 61.8988 | -60.9604 | -60.9192 | 61.5463 | 0.050354 | 0.1236 | 0.1831 | 61.8942 | -61.0016 | -0.23804 | -0.004577 | -0.073242 | -0.19684 | -0.35706 | -0.27924 | -0.009155 | 0.1648 | 60.8459 | 60.9055 | 122.2687 | 122.6212 | -0.073242 | 122.6166 | 60.7727 | -0.27924 | 122.6212 | -0.073242 | 60.7727 | 122.2687 | 122.6166 | -122.8638 | -122.905
575.9062 | 122.7448 | -60.7132 | 61.9354 | -0.55283 | 0.0030164 | 0.0085812 | 0.0017645 | 0.061893 | -0.0026425 | 0.067926 | -60.8185 | 61.821 | -61.0153 | -60.9055 | 61.5417 | 0.054932 | 0.13275 | 0.17395 | 61.8851 | -60.9741 | -0.30212 | -0.11444 | -0.10528 | -0.19226 | -0.39368 | -0.26092 | -0.050354 | 0.19684 | 60.8459 | 60.8871 | 122.2549 | 122.5342 | -0.10528 | 122.5983 | 60.7681 | -0.26092 | 122.5342 | -0.10528 | 60.7681 | 122.2549 | 122.5983 | -122.9507 | -122.9095
576.9688 | 122.85 | -60.6674 | 61.8805 | -0.095062 | 0.0010938 | 0.0043088 | -0.0042169 | 0.06232 | -0.00050626 | 0.068994 | -60.7636 | 61.7935 | -60.9741 | -60.8139 | 61.6516 | 0.15106 | -0.091553 | 0.27924 | 61.8164 | -60.8963 | -0.3067 | -0.086975 | -0.096131 | -0.14648 | -0.22888 | -0.22888 | -0.064087 | 0.21057 | 60.5759 | 60.9467 | 122.319 | 122.4609 | -0.096131 | 122.4838 | 60.8185 | -0.22888 | 122.4609 | -0.096131 | 60.8185 | 122.319 | 122.4838 | -122.8546 | -122.7768
577.9062 | 122.8638 | -60.6583 | 61.8805 | -0.14084 | 0.002162 | 0.010717 | -0.0007989 | 0.060611 | -0.0020017 | 0.068567 | -60.759 | 61.7752 | -60.9421 | -60.8231 | 61.6241 | 0.16022 | -0.045776 | 0.29755 | 61.821 | -60.9283 | -0.28381 | -0.10529 | -0.10071 | -0.16479 | -0.25635 | -0.27008 | -0.059509 | 0.18311 | 60.6125 | 60.9558 | 122.2824 | 122.4335 | -0.10071 | 122.4792 | 60.8185 | -0.27008 | 122.4335 | -0.10071 | 60.8185 | 122.2824 | 122.4792 | -122.8226 | -122.8088
578.9219 | 122.7585 | -60.7132 | 61.8484 | 0.14908 | 0.0047254 | 0.0066586 | 0.0062507 | 0.063816 | -0.0026425 | 0.068353 | -60.8002 | 61.8851 | -60.997 | -60.9375 | 61.5005 | -0.050354 | -0.041199 | 0.059509 | 61.8393 | -61.0382 | -0.28381 | 0.036621 | -0.086975 | -0.2243 | -0.3479 | -0.32501 | -0.009156 | 0.19684 | 60.672 | 60.7727 | 122.2137 | 122.5983 | -0.086975 | 122.5525 | 60.6628 | -0.32501 | 122.5983 | -0.086975 | 60.6628 | 122.2137 | 122.5525 | -122.8455 | -122.8867
579.9688 | 122.7676 | -60.6995 | 61.8759 | -0.14084 | 0.0040846 | 0.005377 | 0.0051825 | 0.063602 | -0.00050626 | 0.06878 | -60.7452 | 61.8668 | -60.9833 | -60.8643 | 61.5555 | 0.059509 | 0.004578 | 0.17395 | 61.8484 | -60.9833 | -0.28381 | -0.009156 | -0.045776 | -0.16479 | -0.32043 | -0.28381 | -0.027466 | 0.23804 | 60.704 | 60.8734 | 122.2549 | 122.5662 | -0.045776 | 122.5479 | 60.759 | -0.28381 | 122.5662 | -0.045776 | 60.759 | 122.2549 | 122.5479 | -122.8592 | -122.8592
580.9062 | 122.8592 | -60.6583 | 61.8576 | -0.13321 | 0.001521 | 0.0034544 | -0.0031489 | 0.062961 | -0.0026425 | 0.067071 | -60.7361 | 61.7706 | -60.9787 | -60.8047 | 61.6379 | 0.15564 | -0.036621 | 0.3067 | 61.8393 | -60.9329 | -0.32043 | -0.086975 | -0.07782 | -0.14648 | -0.21973 | -0.27466 | -0.018311 | 0.24262 | 60.6216 | 60.965 | 122.2961 | 122.4289 | -0.07782 | 122.4976 | 60.8139 | -0.27466 | 122.4289 | -0.07782 | 60.8139 | 122.2961 | 122.4976 | -122.8363 | -122.7905
581.9688 | 122.7539 | -60.7086 | 61.9034 | 0.042267 | 0.0045118 | 0.0068722 | 0.0019781 | 0.064456 | -0.0030697 | 0.06878 | -60.8231 | 61.8301 | -61.0016 | -60.9146 | 61.5234 | 0.027466 | 0.14191 | 0.17395 | 61.8759 | -60.997 | -0.29297 | -0.073242 | -0.11444 | -0.20599 | -0.37994 | -0.28839 | -0.027465 | 0.17853 | 60.8505 | 60.8826 | 122.2321 | 122.5388 | -0.11444 | 122.5845 | 60.7361 | -0.28839 | 122.5388 | -0.11444 | 60.7361 | 122.2321 | 122.5845 | -122.905 | -122.9004
582.9062 | 122.8226 | -60.6491 | 61.8759 | -0.18662 | -0.00061524 | 0.0051632 | -0.0027215 | 0.063175 | -0.0028561 | 0.068139 | -60.7636 | 61.8027 | -60.9467 | -60.8139 | 61.6241 | 0.14648 | -0.013733 | 0.29297 | 61.8301 | -60.9421 | -0.29755 | -0.073243 | -0.11444 | -0.16479 | -0.25177 | -0.29297 | -0.045777 | 0.1831 | 60.6354 | 60.9421 | 122.2733 | 122.4518 | -0.11444 | 122.4792 | 60.7956 | -0.29297 | 122.4518 | -0.11444 | 60.7956 | 122.2733 | 122.4792 | -122.8226 | -122.818
583.9844 | 122.7631 | -60.704 | 61.9263 | -0.1561 | 0.0055798 | 0.0058042 | 0.0026191 | 0.065097 | -0.00050626 | 0.068139 | -60.7956 | 61.908 | -60.9741 | -60.9055 | 61.5372 | 0.050354 | 0.11902 | 0.17395 | 61.8759 | -60.9924 | -0.27008 | -0.018311 | -0.091552 | -0.20142 | -0.3891 | -0.28839 | -0.050354 | 0.17853 | 60.8231 | 60.878 | 122.2412 | 122.612 | -0.091552 | 122.58 | 60.7544 | -0.28839 | 122.612 | -0.091552 | 60.7544 | 122.2412 | 122.58 | -122.9004 | -122.9187
584.9062 | 122.7448 | -60.7269 | 61.9263 | -0.087433 | 0.002162 | 0.0051632 | -0.0025079 | 0.062747 | -0.0030697 | 0.068139 | -60.8139 | 61.8484 | -60.9879 | -60.9192 | 61.5417 | 0.059509 | 0.11444 | 0.19684 | 61.8713 | -60.9512 | -0.26093 | -0.07782 | -0.086975 | -0.19226 | -0.38452 | -0.2243 | -0.054932 | 0.17395 | 60.8414 | 60.9238 | 122.2687 | 122.5754 | -0.086975 | 122.5983 | 60.7864 | -0.2243 | 122.5754 | -0.086975 | 60.7864 | 122.2687 | 122.5983 | -122.9141 | -122.8775
585.9531 | 122.8363 | -60.6766 | 61.853 | -0.087433 | 0.00045296 | 0.0040952 | -0.0037897 | 0.064456 | -0.00093346 | 0.069421 | -60.7864 | 61.7752 | -60.9741 | -60.8551 | 61.615 | 0.11902 | -0.086975 | 0.24719 | 61.8118 | -60.9375 | -0.29755 | -0.077819 | -0.10986 | -0.17853 | -0.23804 | -0.26093 | -0.041198 | 0.18768 | 60.5896 | 60.9238 | 122.2916 | 122.4518 | -0.10986 | 122.4884 | 60.7956 | -0.26093 | 122.4518 | -0.10986 | 60.7956 | 122.2916 | 122.4884 | -122.8271 | -122.7905
586.9062 | 122.7814 | -60.672 | 61.908 | -0.22476 | 0.001521 | 0.0028134 | 0.0002691 | 0.06232 | -0.0015745 | 0.068353 | -60.7636 | 61.7935 | -60.965 | -60.8505 | 61.5784 | 0.11902 | 0.059509 | 0.2655 | 61.8301 | -60.9604 | -0.29297 | -0.11444 | -0.091553 | -0.17853 | -0.32959 | -0.28839 | -0.07782 | 0.20142 | 60.7315 | 60.9375 | 122.2504 | 122.4655 | -0.091553 | 122.5021 | 60.791 | -0.28839 | 122.4655 | -0.091553 | 60.791 | 122.2504 | 122.5021 | -122.8729 | -122.8683
587.9688 | 122.7951 | -60.6812 | 61.853 | 0.1796 | 0.0017346 | 0.006445 | -0.0018671 | 0.062961 | -0.00093346 | 0.068567 | -60.8093 | 61.7752 | -60.9924 | -60.8963 | 61.5509 | 0.032043 | -0.10986 | 0.15106 | 61.821 | -60.9512 | -0.31128 | -0.077819 | -0.12817 | -0.21515 | -0.30212 | -0.27008 | -0.032043 | 0.18311 | 60.5713 | 60.8322 | 122.2321 | 122.4564 | -0.12817 | 122.5021 | 60.7132 | -0.27008 | 122.4564 | -0.12817 | 60.7132 | 122.2321 | 122.5021 | -122.8455 | -122.8043
588.9219 | 122.7905 | -60.7086 | 61.8942 | -0.1561 | 0.0047254 | 0.0040952 | 0.0056097 | 0.063175 | -0.00029266 | 0.067712 | -60.7452 | 61.8713 | -60.9833 | -60.8597 | 61.5601 | 0.064087 | 0.050354 | 0.20599 | 61.8439 | -60.9833 | -0.27466 | -0.022888 | -0.036621 | -0.15106 | -0.33417 | -0.27466 | -0.050354 | 0.23804 | 60.759 | 60.9146 | 122.2687 | 122.58 | -0.036621 | 122.5525 | 60.7727 | -0.27466 | 122.58 | -0.036621 | 60.7727 | 122.2687 | 122.5525 | -122.8775 | -122.8775
589.9531 | 122.8775 | -60.6995 | 61.8851 | -0.0035098 | 0.0034436 | 0.0025998 | -0.0027215 | 0.062107 | -0.00029266 | 0.068567 | -60.8002 | 61.7752 | -60.9741 | -60.8597 | 61.6058 | 0.09613 | -0.09613 | 0.24261 | 61.8256 | -60.9512 | -0.27466 | -0.10986 | -0.10071 | -0.16022 | -0.27924 | -0.25177 | -0.059509 | 0.17395 | 60.6033 | 60.9421 | 122.3053 | 122.4747 | -0.10071 | 122.525 | 60.7956 | -0.25177 | 122.4747 | -0.10071 | 60.7956 | 122.3053 | 122.525 | -122.8592 | -122.8363
590.9062 | 122.8134 | -60.704 | 61.853 | 0.11856 | 0.0019482 | 0.005377 | -0.0020807 | 0.064456 | -0.0039243 | 0.068567 | -60.8322 | 61.7844 | -60.965 | -60.8917 | 61.5417 | 0.022888 | -0.073242 | 0.16937 | 61.8347 | -60.9558 | -0.26093 | -0.068664 | -0.12817 | -0.18768 | -0.31128 | -0.25177 | -0.01831 | 0.13275 | 60.6308 | 60.8734 | 122.2458 | 122.4884 | -0.12817 | 122.5388 | 60.7269 | -0.25177 | 122.4884 | -0.12817 | 60.7269 | 122.2458 | 122.5388 | -122.818 | -122.8088
591.9844 | 122.8821 | -60.6857 | 61.8668 | -0.072174 | 0.0045118 | 0.0058042 | -0.0016535 | 0.061038 | -0.0020017 | 0.067926 | -60.7498 | 61.7798 | -60.9558 | -60.8185 | 61.6379 | 0.16022 | -0.091553 | 0.27924 | 61.7981 | -60.9512 | -0.27008 | -0.086975 | -0.064087 | -0.13275 | -0.22888 | -0.2655 | -0.068664 | 0.20599 | 60.5942 | 60.965 | 122.3236 | 122.4655 | -0.064087 | 122.4838 | 60.8459 | -0.2655 | 122.4655 | -0.064087 | 60.8459 | 122.3236 | 122.4838 | -122.8226 | -122.818
592.9062 | 122.818 | -60.6995 | 61.8393 | 0.11093 | 0.0023756 | 0.001959 | -0.0010125 | 0.062747 | -0.0020017 | 0.066217 | -60.8047 | 61.7569 | -60.9695 | -60.9055 | 61.5463 | 0.004578 | -0.09613 | 0.15564 | 61.7935 | -60.9512 | -0.27008 | -0.082397 | -0.10529 | -0.20599 | -0.29297 | -0.25177 | -0.045776 | 0.16479 | 60.6033 | 60.8551 | 122.2458 | 122.4564 | -0.10529 | 122.493 | 60.704 | -0.25177 | 122.4564 | -0.10529 | 60.704 | 122.2458 | 122.493 | -122.8088 | -122.7905
593.9844 | 122.7219 | -60.7452 | 61.8851 | 0.072784 | 0.0038708 | 0.0062314 | 0.0049689 | 0.063602 | -0.0013609 | 0.067071 | -60.8047 | 61.8301 | -61.0107 | -60.9329 | 61.4594 | -0.041199 | 0.045776 | 0.068665 | 61.8393 | -60.9879 | -0.2655 | -0.054932 | -0.05951 | -0.18768 | -0.42572 | -0.24262 | -0.045777 | 0.20599 | 60.791 | 60.8139 | 122.2046 | 122.5754 | -0.05951 | 122.5845 | 60.704 | -0.24262 | 122.5754 | -0.05951 | 60.704 | 122.2046 | 122.5845 | -122.8958 | -122.8729
594.9062 | 122.8409 | -60.6354 | 61.8805 | -0.16373 | 0.002162 | 0.0011044 | -0.0029351 | 0.061893 | -0.00071986 | 0.067712 | -60.7498 | 61.7981 | -60.9467 | -60.8185 | 61.6241 | 0.1236 | -0.004578 | 0.30212 | 61.8393 | -60.9467 | -0.31128 | -0.082397 | -0.11444 | -0.1831 | -0.25635 | -0.31128 | -0.041199 | 0.19684 | 60.6308 | 60.9375 | 122.2595 | 122.4335 | -0.11444 | 122.4747 | 60.759 | -0.31128 | 122.4335 | -0.11444 | 60.759 | 122.2595 | 122.4747 | -122.8271 | -122.8271
595.9688 | 122.7905 | -60.7269 | 61.8484 | 0.21011 | 0.0034436 | 0.0085812 | 0.0028327 | 0.06467 | -0.0043515 | 0.069207 | -60.8231 | 61.8073 | -61.0016 | -60.9375 | 61.5143 | -0.045776 | -0.09613 | 0.068665 | 61.8393 | -60.9787 | -0.27466 | -0.041199 | -0.09613 | -0.21057 | -0.33417 | -0.25177 | -0.009156 | 0.17853 | 60.6308 | 60.7956 | 122.2412 | 122.5342 | -0.09613 | 122.5662 | 60.6812 | -0.25177 | 122.5342 | -0.09613 | 60.6812 | 122.2412 | 122.5662 | -122.85 | -122.8271
596.9062 | 122.818 | -60.6903 | 61.8484 | 0.21011 | 0.0036572 | 0.0092222 | -0.0014399 | 0.062534 | -0.00071986 | 0.067285 | -60.7956 | 61.7889 | -60.9741 | -60.8917 | 61.5829 | 0.022888 | -0.13275 | 0.14648 | 61.8118 | -60.9604 | -0.28381 | -0.05951 | -0.10528 | -0.20142 | -0.2655 | -0.27008 | -0.036621 | 0.17853 | 60.5576 | 60.8368 | 122.2733 | 122.4792 | -0.10528 | 122.5021 | 60.7132 | -0.27008 | 122.4792 | -0.10528 | 60.7132 | 122.2733 | 122.5021 | -122.8226 | -122.8088
597.9531 | 122.7951 | -60.7086 | 61.853 | 0.1796 | 0.0051526 | 0.009863 | 0.0036871 | 0.065311 | -0.0024289 | 0.066858 | -60.8276 | 61.8256 | -61.0062 | -60.9283 | 61.5051 | -0.027466 | -0.091553 | 0.068665 | 61.821 | -61.0107 | -0.29755 | -0.027465 | -0.11902 | -0.21973 | -0.3479 | -0.30212 | -0.032043 | 0.17853 | 60.6171 | 60.7773 | 122.2137 | 122.5342 | -0.11902 | 122.5296 | 60.6812 | -0.30212 | 122.5342 | -0.11902 | 60.6812 | 122.2137 | 122.5296 | -122.8592 | -122.8638
598.9062 | 122.9004 | -60.672 | 61.8393 | 1.6521 | 0.0038708 | 0.0045224 | 0.0009101 | 0.064456 | -0.0011471 | 0.068139 | -60.704 | 61.7661 | -60.965 | -60.8322 | 61.6058 | 0.041199 | -0.22888 | 0.15564 | 61.7844 | -60.9879 | -0.29297 | -0.073242 | -0.032044 | -0.16022 | -0.23346 | -0.31586 | -0.054931 | 0.26093 | 60.4431 | 60.8276 | 122.2778 | 122.438 | -0.032044 | 122.4564 | 60.7132 | -0.31586 | 122.438 | -0.032044 | 60.7132 | 122.2778 | 122.4564 | -122.8043 | -122.8271
599.9688 | 122.85 | -60.6812 | 61.8256 | 0.14908 | 0.0045118 | 0.006445 | 0.0024053 | 0.063602 | -0.0022153 | 0.068567 | -60.7727 | 61.7523 | -60.965 | -60.8688 | 61.5784 | 0.041199 | -0.16479 | 0.16022 | 61.7752 | -60.9467 | -0.28381 | -0.073243 | -0.091553 | -0.18768 | -0.24719 | -0.2655 | -0.050354 | 0.19226 | 60.5164 | 60.8414 | 122.2595 | 122.4335 | -0.091553 | 122.4564 | 60.7224 | -0.2655 | 122.4335 | -0.091553 | 60.7224 | 122.2595 | 122.4564 | -122.7905 | -122.7722
600.9062 | 122.8088 | -60.6995 | 61.8393 | 0.18723 | 0.0038708 | 0.0060178 | 0.0017645 | 0.063816 | -0.00093346 | 0.067712 | -60.7727 | 61.7889 | -60.965 | -60.8826 | 61.5692 | 0.032043 | -0.14648 | 0.15564 | 61.7935 | -60.9879 | -0.2655 | -0.050354 | -0.073242 | -0.1831 | -0.27008 | -0.28839 | -0.045776 | 0.19226 | 60.553 | 60.8551 | 122.2687 | 122.4884 | -0.073242 | 122.493 | 60.7315 | -0.28839 | 122.4884 | -0.073242 | 60.7315 | 122.2687 | 122.493 | -122.8043 | -122.8271
601.9688 | 122.7951 | -60.672 | 61.8668 | 0.0041197 | 0.0023756 | 0.0075132 | -0.0012261 | 0.061466 | -0.0015745 | 0.067926 | -60.8047 | 61.8073 | -60.9833 | -60.9055 | 61.5738 | 0.041199 | -0.032043 | 0.38452 | 61.8118 | -60.9467 | -0.31128 | -0.059509 | -0.13275 | -0.23346 | -0.29297 | -0.27466 | -0.054931 | 0.17853 | 60.64 | 61.0565 | 122.2458 | 122.4792 | -0.13275 | 122.4838 | 60.7132 | -0.27466 | 122.4792 | -0.13275 | 60.7132 | 122.2458 | 122.4838 | -122.85 | -122.8134
602.9062 | 122.8088 | -60.6995 | 61.853 | 0.027008 | 0.0055798 | 0.0043088 | -0.0022943 | 0.062107 | -0.0022153 | 0.068139 | -60.7452 | 61.8393 | -60.9467 | -60.8917 | 61.5784 | 0.050354 | -0.082397 | 0.16022 | 61.7844 | -61.0107 | -0.24719 | -0.013733 | -0.045776 | -0.19226 | -0.27466 | -0.31128 | -0.068664 | 0.20142 | 60.6171 | 60.8597 | 122.2778 | 122.5388 | -0.045776 | 122.4838 | 60.7498 | -0.31128 | 122.5388 | -0.045776 | 60.7498 | 122.2778 | 122.4838 | -122.7997 | -122.8638
603.9531 | 122.818 | -60.6949 | 61.8393 | 0.15671 | 0.00088016 | 0.0051632 | 0.0011237 | 0.062961 | -0.00050626 | 0.067071 | -60.791 | 61.7798 | -60.9741 | -60.8597 | 61.5463 | 0.032043 | -0.15564 | 0.15564 | 61.7889 | -60.9741 | -0.27924 | -0.059509 | -0.096131 | -0.16479 | -0.29297 | -0.27924 | -0.050354 | 0.1831 | 60.5392 | 60.8505 | 122.2412 | 122.4747 | -0.096131 | 122.4838 | 60.7269 | -0.27924 | 122.4747 | -0.096131 | 60.7269 | 122.2412 | 122.4838 | -122.8134 | -122.8134
604.9062 | 122.8546 | -60.6903 | 61.853 | -0.064545 | 0.0047254 | 0.00089078 | 5.5496e-05 | 0.061252 | -7.9062e-05 | 0.068567 | -60.7819 | 61.7981 | -60.9787 | -60.8459 | 61.6104 | 0.11902 | -0.059509 | 0.23346 | 61.8256 | -60.9512 | -0.28839 | -0.054931 | -0.091552 | -0.15564 | -0.24261 | -0.26093 | -0.027465 | 0.19684 | 60.6308 | 60.9238 | 122.3007 | 122.4884 | -0.091552 | 122.5159 | 60.8093 | -0.26093 | 122.4884 | -0.091552 | 60.8093 | 122.3007 | 122.5159 | -122.8317 | -122.8043
605.9531 | 122.7631 | -60.7178 | 61.8668 | 0.15671 | 0.0053662 | 0.0094358 | 0.0075323 | 0.063816 | -0.00029266 | 0.066644 | -60.8414 | 61.8393 | -60.9879 | -60.9421 | 61.4868 | -0.064087 | -0.036621 | 0.054932 | 61.8164 | -61.0107 | -0.27008 | -0.027466 | -0.1236 | -0.22431 | -0.37994 | -0.29297 | -0.050354 | 0.14648 | 60.6812 | 60.7727 | 122.2046 | 122.5571 | -0.1236 | 122.5342 | 60.6537 | -0.29297 | 122.5571 | -0.1236 | 60.6537 | 122.2046 | 122.5342 | -122.8546 | -122.8775
606.9062 | 122.8683 | -60.6766 | 61.821 | 0.3093 | 0.0040846 | 0.0051632 | 0.0019781 | 0.066593 | -0.00050626 | 0.06878 | -60.7727 | 61.8073 | -60.9879 | -60.8505 | 61.5875 | 0.036621 | -0.20142 | 0.15564 | 61.8027 | -60.9695 | -0.31128 | -0.013733 | -0.09613 | -0.17395 | -0.23346 | -0.29297 | -0.018311 | 0.21515 | 60.4752 | 60.8322 | 122.2641 | 122.4838 | -0.09613 | 122.4792 | 60.7132 | -0.29297 | 122.4838 | -0.09613 | 60.7132 | 122.2641 | 122.4792 | -122.8088 | -122.7905
607.9531 | 122.7127 | -60.7269 | 61.8759 | 0.042267 | 0.0070752 | 0.0077268 | 0.0064643 | 0.065525 | -0.0034971 | 0.068353 | -60.8002 | 61.8713 | -61.0062 | -60.9146 | 61.5005 | -0.027466 | 0.022888 | 0.091553 | 61.8668 | -60.9924 | -0.27924 | -0.004578 | -0.073242 | -0.18768 | -0.37537 | -0.2655 | -0.009156 | 0.20599 | 60.7498 | 60.8185 | 122.2275 | 122.5983 | -0.073242 | 122.5937 | 60.6995 | -0.2655 | 122.5983 | -0.073242 | 60.6995 | 122.2275 | 122.5937 | -122.8821 | -122.8683
608.9062 | 122.8775 | -60.6674 | 61.8164 | 0.14908 | 0.0036572 | 0.003668 | -0.0012261 | 0.066379 | -0.0024289 | 0.069635 | -60.7452 | 61.8164 | -60.9879 | -60.8597 | 61.6013 | 0.041199 | -0.1831 | 0.16937 | 61.7981 | -60.9787 | -0.32043 | 0 | -0.07782 | -0.19226 | -0.21515 | -0.31128 | -0.01831 | 0.24262 | 60.4843 | 60.8368 | 122.2687 | 122.4838 | -0.07782 | 122.4655 | 60.7086 | -0.31128 | 122.4838 | -0.07782 | 60.7086 | 122.2687 | 122.4655 | -122.8043 | -122.7951
609.9688 | 122.7539 | -60.7132 | 61.8896 | -0.018768 | 0.0057934 | 0.0075132 | 0.0068915 | 0.066806 | -0.0011471 | 0.067498 | -60.8093 | 61.8759 | -61.0062 | -60.9146 | 61.528 | 0.004578 | 0.018311 | 0.11444 | 61.8622 | -61.0062 | -0.29297 | -0.013732 | -0.09613 | -0.20142 | -0.36163 | -0.29297 | -0.027465 | 0.19684 | 60.7315 | 60.8276 | 122.2412 | 122.5891 | -0.09613 | 122.5754 | 60.7178 | -0.29297 | 122.5891 | -0.09613 | 60.7178 | 122.2412 | 122.5754 | -122.8958 | -122.8958
610.9062 | 122.8821 | -60.6812 | 61.8301 | 0.22537 | 0.0042982 | 0.0085812 | -0.0014399 | 0.065952 | -0.00050626 | 0.067285 | -60.6674 | 61.8118 | -60.9879 | -60.8459 | 61.6287 | 0.07782 | -0.20142 | 0.16479 | 61.7981 | -60.965 | -0.3067 | -0.01831 | 0.013733 | -0.1648 | -0.20142 | -0.28381 | -0.032043 | 0.32043 | 60.4797 | 60.8459 | 122.3099 | 122.493 | 0.013733 | 122.4792 | 60.759 | -0.28381 | 122.493 | 0.013733 | 60.759 | 122.3099 | 122.4792 | -122.818 | -122.7951
611.9531 | 122.7173 | -60.7407 | 61.8805 | 0.11093 | 0.0068616 | 0.00089078 | 0.0051825 | 0.066379 | -7.9062e-05 | 0.06643 | -60.8322 | 61.8942 | -61.0016 | -60.9558 | 61.4731 | -0.073242 | 0.041199 | 0.036621 | 61.8347 | -61.0336 | -0.26093 | 0.013733 | -0.091552 | -0.21515 | -0.40741 | -0.29297 | -0.045776 | 0.16937 | 60.7819 | 60.7773 | 122.2137 | 122.6349 | -0.091552 | 122.5754 | 60.6674 | -0.29297 | 122.6349 | -0.091552 | 60.6674 | 122.2137 | 122.5754 | -122.8821 | -122.9141
612.9062 | 122.7356 | -60.7224 | 61.8713 | -0.4155 | 0.004939 | 0.0038816 | 0.0045417 | 0.06702 | -0.00050626 | 0.067071 | -60.6354 | 61.8988 | -60.9833 | -60.9558 | 61.4914 | -0.054932 | -0.018311 | 0.050354 | 61.8027 | -61.0382 | -0.26092 | 0.027466 | 0.086975 | -0.23346 | -0.37994 | -0.31586 | -0.068665 | 0.3479 | 60.704 | 60.7727 | 122.2137 | 122.6212 | 0.086975 | 122.525 | 60.6674 | -0.31586 | 122.6212 | 0.086975 | 60.6674 | 122.2137 | 122.525 | -122.8546 | -122.9095
613.9531 | 122.8271 | -60.6995 | 61.8347 | 0.17197 | 0.001521 | 0.0090086 | -0.0031489 | 0.065097 | -0.0020017 | 0.066003 | -60.7636 | 61.7889 | -60.9787 | -60.8734 | 61.5829 | 0.059509 | -0.18768 | 0.16479 | 61.8073 | -60.9879 | -0.27924 | -0.045777 | -0.064087 | -0.17395 | -0.25177 | -0.28839 | -0.027466 | 0.21515 | 60.5118 | 60.8643 | 122.2824 | 122.4884 | -0.064087 | 122.5067 | 60.759 | -0.28839 | 122.4884 | -0.064087 | 60.759 | 122.2824 | 122.5067 | -122.8134 | -122.8226
614.9062 | 122.7997 | -60.6949 | 61.8393 | 0.095673 | 0.0028028 | 0.0058042 | -0.0012261 | 0.065097 | -0.00050626 | 0.068567 | -60.8139 | 61.8347 | -60.9604 | -60.9146 | 61.5601 | 0.032043 | -0.1236 | 0.14648 | 61.8027 | -60.9833 | -0.2655 | -0.004577 | -0.11902 | -0.21973 | -0.27923 | -0.28839 | -0.036621 | 0.14648 | 60.5713 | 60.8414 | 122.2549 | 122.5296 | -0.11902 | 122.4976 | 60.7269 | -0.28839 | 122.5296 | -0.11902 | 60.7269 | 122.2549 | 122.4976 | -122.7997 | -122.8226
615.9688 | 122.818 | -60.7132 | 61.8576 | 0.20248 | 0.0051526 | 0.0040952 | -0.0001581 | 0.062961 | -0.00050626 | 0.069635 | -60.7636 | 61.8164 | -60.9604 | -60.9055 | 61.5555 | 0.032043 | -0.16937 | 0.14191 | 61.7752 | -60.9924 | -0.24719 | -0.041199 | -0.050354 | -0.19226 | -0.30212 | -0.27924 | -0.082397 | 0.19684 | 60.5438 | 60.8551 | 122.2687 | 122.5296 | -0.050354 | 122.4884 | 60.7452 | -0.27924 | 122.5296 | -0.050354 | 60.7452 | 122.2687 | 122.4884 | -122.818 | -122.85
616.9062 | 122.7631 | -60.7361 | 61.8668 | 0.18723 | 0.0062208 | 0.0087948 | 0.0053961 | 0.063388 | -0.00029266 | 0.06878 | -60.8276 | 61.8942 | -61.0016 | -60.9421 | 61.4868 | -0.036621 | -0.032043 | 0.045776 | 61.8027 | -61.0107 | -0.2655 | 0.027466 | -0.091553 | -0.20599 | -0.37994 | -0.27466 | -0.064087 | 0.17395 | 60.704 | 60.7819 | 122.2229 | 122.6303 | -0.091553 | 122.5388 | 60.6995 | -0.27466 | 122.6303 | -0.091553 | 60.6995 | 122.2229 | 122.5388 | -122.8683 | -122.8775
617.9531 | 122.7493 | -60.7224 | 61.853 | 0.26352 | 0.0079298 | 0.0077268 | 0.0043281 | 0.065738 | 0.00034814 | 0.067285 | -60.8002 | 61.8851 | -61.0245 | -60.9329 | 61.4822 | -0.050354 | -0.018311 | 0.050354 | 61.8301 | -61.0245 | -0.30212 | 0.032044 | -0.07782 | -0.21057 | -0.37079 | -0.30212 | -0.022888 | 0.2243 | 60.704 | 60.7727 | 122.2046 | 122.6074 | -0.07782 | 122.5525 | 60.672 | -0.30212 | 122.6074 | -0.07782 | 60.672 | 122.2046 | 122.5525 | -122.8775 | -122.8775
618.9062 | 122.7448 | -60.7407 | 61.8668 | 0.15671 | 0.0070752 | 0.01029 | 0.0030463 | 0.06702 | 0.0018435 | 0.068567 | -60.8643 | 61.9263 | -61.0291 | -60.9879 | 61.4731 | -0.064087 | 0 | 0.045776 | 61.8347 | -61.0336 | -0.28839 | 0.05951 | -0.1236 | -0.24719 | -0.39368 | -0.29297 | -0.032043 | 0.16479 | 60.7407 | 60.7864 | 122.2137 | 122.6669 | -0.1236 | 122.5754 | 60.6766 | -0.29297 | 122.6669 | -0.1236 | 60.6766 | 122.2137 | 122.5754 | -122.8958 | -122.9004
619.9531 | 122.7448 | -60.7132 | 61.8713 | 0.1796 | 0.0051526 | 0.0055906 | 0.0039007 | 0.066806 | -0.0026425 | 0.069635 | -60.8322 | 61.8347 | -61.0382 | -60.965 | 61.4914 | -0.041199 | -0.036621 | 0.050354 | 61.8576 | -61.0016 | -0.32501 | -0.036621 | -0.11902 | -0.25177 | -0.37994 | -0.28839 | -0.013733 | 0.20599 | 60.6766 | 60.7636 | 122.2046 | 122.5479 | -0.11902 | 122.5708 | 60.672 | -0.28839 | 122.5479 | -0.11902 | 60.672 | 122.2046 | 122.5708 | -122.9095 | -122.8729
620.9062 | 122.7356 | -60.7498 | 61.8576 | 0.11856 | 0.0055798 | 0.008154 | 0.0041143 | 0.065311 | -0.0020017 | 0.068567 | -60.8231 | 61.908 | -60.9741 | -60.965 | 61.4502 | -0.059509 | 0.027466 | 0.050354 | 61.8484 | -61.0382 | -0.2243 | 0.050354 | -0.073242 | -0.21515 | -0.40741 | -0.28839 | -0.009155 | 0.15106 | 60.7773 | 60.8002 | 122.2 | 122.6578 | -0.073242 | 122.5983 | 60.6903 | -0.28839 | 122.6578 | -0.073242 | 60.6903 | 122.2 | 122.5983 | -122.8317 | -122.8958
621.9531 | 122.8683 | -60.7086 | 61.7981 | 0.40085 | 0.0040846 | 0.0077268 | 0.0024053 | 0.065097 | -0.0011471 | 0.067498 | -60.7681 | 61.8484 | -60.965 | -60.8597 | 61.5875 | 0.054932 | -0.18768 | 0.16022 | 61.821 | -61.0062 | -0.25635 | 0.050354 | -0.059509 | -0.15106 | -0.21057 | -0.29755 | 0.022888 | 0.19684 | 60.5209 | 60.8688 | 122.2961 | 122.5571 | -0.059509 | 122.5296 | 60.7636 | -0.29755 | 122.5571 | -0.059509 | 60.7636 | 122.2961 | 122.5296 | -122.7631 | -122.8043
622.9062 | 122.7402 | -60.7178 | 61.8851 | 0.13382 | 0.0045118 | 0.0060178 | 0.0086005 | 0.067661 | -0.0022153 | 0.066858 | -60.8551 | 61.9125 | -61.0062 | -60.7681 | 61.5051 | -0.12817 | 0.073242 | 0.10529 | 61.8622 | -61.0245 | -0.28839 | 0.027466 | -0.13733 | -0.050354 | -0.37994 | -0.3067 | -0.022888 | 0.15106 | 60.791 | 60.8231 | 122.2229 | 122.6303 | -0.13733 | 122.58 | 60.5896 | -0.3067 | 122.6303 | -0.13733 | 60.5896 | 122.2229 | 122.58 | -122.8912 | -122.9095
623.9531 | 122.7219 | -60.7178 | 61.8896 | 0.21774 | 0.0042982 | 0.011145 | 0.0030463 | 0.068088 | 0.0018435 | 0.066858 | -60.8322 | 61.8896 | -60.9924 | -60.9604 | 61.4868 | -0.059509 | -0.013733 | 0.054932 | 61.8393 | -61.0245 | -0.27466 | 0 | -0.11444 | -0.24262 | -0.40283 | -0.3067 | -0.050354 | 0.16022 | 60.704 | 60.7727 | 122.2046 | 122.6074 | -0.11444 | 122.5571 | 60.6583 | -0.3067 | 122.6074 | -0.11444 | 60.6583 | 122.2046 | 122.5571 | -122.8821 | -122.9141
624.9062 | 122.8683 | -60.6949 | 61.8576 | -0.056915 | 0.0013074 | 0.0028134 | -0.0059259 | 0.06467 | -0.0022153 | 0.067071 | -60.7727 | 61.7935 | -60.9695 | -60.8551 | 61.6379 | 0.1236 | -0.082397 | 0.25177 | 61.8301 | -60.9833 | -0.27466 | -0.064087 | -0.07782 | -0.16022 | -0.21973 | -0.28839 | -0.027466 | 0.19684 | 60.6125 | 60.9467 | 122.3328 | 122.4884 | -0.07782 | 122.525 | 60.8185 | -0.28839 | 122.4884 | -0.07782 | 60.8185 | 122.3328 | 122.525 | -122.8271 | -122.8409
625.9688 | 122.7585 | -60.6537 | 61.8896 | 1.1867 | 0.00323 | 0.009863 | 0.0049689 | 0.065952 | -0.0039243 | 0.066003 | -60.6537 | 61.8988 | -60.9695 | -60.8688 | 61.5738 | 0.10071 | 0.004578 | 0.19226 | 61.8484 | -61.0107 | -0.31586 | 0.009156 | 0 | -0.21515 | -0.31586 | -0.35706 | -0.041198 | 0.31586 | 60.6583 | 60.8459 | 122.2275 | 122.5525 | 0 | 122.5021 | 60.7544 | -0.35706 | 122.5525 | 0 | 60.7544 | 122.2275 | 122.5021 | -122.8592 | -122.9004
626.9062 | 122.7814 | -60.6995 | 61.8576 | 0.019379 | 0.0068616 | 0.0051632 | 0.0062507 | 0.066165 | 0.0012027 | 0.066217 | -60.7407 | 61.9217 | -60.9695 | -60.8826 | 61.5326 | 0.036621 | 0.036621 | 0.17395 | 61.8713 | -61.0199 | -0.27008 | 0.064087 | -0.041199 | -0.1831 | -0.32501 | -0.32043 | 0.013733 | 0.22888 | 60.7361 | 60.8734 | 122.2321 | 122.6212 | -0.041199 | 122.5708 | 60.7361 | -0.32043 | 122.6212 | -0.041199 | 60.7361 | 122.2321 | 122.5708 | -122.8271 | -122.8775
627.9688 | 122.5845 | -60.7544 | 61.7889 | 0.12619 | 0.0070752 | 0.006445 | 0.0034735 | 0.066806 | -0.0015745 | 0.068139 | -60.8276 | 61.908 | -60.9924 | -60.9879 | 61.4548 | -0.059509 | 0.027466 | 0.041199 | 61.8805 | -61.0565 | -0.23804 | 0.11902 | -0.073242 | -0.23346 | -0.33417 | -0.30212 | 0.091553 | 0.16479 | 60.7819 | 60.7956 | 122.2092 | 122.6624 | -0.073242 | 122.6349 | 60.6949 | -0.30212 | 122.6624 | -0.073242 | 60.6949 | 122.2092 | 122.6349 | -122.7814 | -122.8455
628.9062 | 122.731 | -60.7269 | 61.8622 | 0.049896 | 0.0042982 | 0.0090086 | 0.0032599 | 0.068515 | -0.00029266 | 0.067926 | -60.8047 | 61.9125 | -60.9787 | -60.9467 | 61.4685 | -0.032043 | 0.041199 | 0.073242 | 61.8484 | -61.0428 | -0.25177 | 0.050354 | -0.07782 | -0.21973 | -0.39368 | -0.31586 | -0.013733 | 0.17395 | 60.7681 | 60.8002 | 122.1954 | 122.6395 | -0.07782 | 122.5754 | 60.6949 | -0.31586 | 122.6395 | -0.07782 | 60.6949 | 122.1954 | 122.5754 | -122.8409 | -122.905
629.9688 | 122.8775 | -60.672 | 61.8393 | 0.21011 | 0.0040846 | 0.01029 | -0.0003717 | 0.065738 | -0.0011471 | 0.067498 | -60.7452 | 61.7935 | -60.9924 | -60.8826 | 61.5921 | 0.17853 | -0.49896 | 0.17853 | 61.7569 | -61.0107 | -0.32044 | -0.045776 | -0.073242 | -0.21057 | -0.24719 | -0.33875 | -0.082397 | 0.24719 | 60.173 | 60.8505 | 122.2641 | 122.4655 | -0.073242 | 122.4289 | 60.8505 | -0.33875 | 122.4655 | -0.073242 | 60.8505 | 122.2641 | 122.4289 | -122.8317 | -122.85
630.9062 | 122.7493 | -60.7178 | 61.8851 | -0.034027 | 0.0060072 | 0.003027 | 0.0053961 | 0.06702 | -0.0015745 | 0.067712 | -60.759 | 61.8942 | -60.965 | -60.9055 | 61.5143 | 0.013733 | 0.027466 | 0.14648 | 61.8759 | -61.0245 | -0.24719 | 0.009155 | -0.041199 | -0.18768 | -0.37079 | -0.3067 | -0.009155 | 0.20599 | 60.7452 | 60.8643 | 122.2321 | 122.612 | -0.041199 | 122.5937 | 60.7315 | -0.3067 | 122.612 | -0.041199 | 60.7315 | 122.2321 | 122.5937 | -122.85 | -122.9095
631.9531 | 122.7631 | -60.7224 | 61.853 | 0.15671 | 0.0051526 | 0.011786 | 0.0002691 | 0.067874 | -0.0015745 | 0.069207 | -60.8231 | 61.908 | -61.0062 | -60.965 | 61.4731 | -0.036621 | -0.045776 | 0.064087 | 61.8622 | -61.0245 | -0.28381 | 0.054932 | -0.10071 | -0.24261 | -0.37994 | -0.30212 | 0.009156 | 0.18311 | 60.6766 | 60.7864 | 122.1954 | 122.6303 | -0.10071 | 122.5845 | 60.6857 | -0.30212 | 122.6303 | -0.10071 | 60.6857 | 122.1954 | 122.5845 | -122.8592 | -122.8775
632.9062 | 122.7814 | -60.7132 | 61.8713 | 0.1033 | 0.0079298 | 0.0077268 | 0.0045417 | 0.064456 | -0.00029266 | 0.066217 | -60.6949 | 61.9034 | -60.997 | -60.8688 | 61.5555 | 0.082397 | 0.022888 | 0.1831 | 61.8484 | -61.0107 | -0.28381 | 0.032043 | 0.018311 | -0.15564 | -0.31586 | -0.29755 | -0.022888 | 0.30212 | 60.7361 | 60.8963 | 122.2687 | 122.6166 | 0.018311 | 122.5616 | 60.7956 | -0.29755 | 122.6166 | 0.018311 | 60.7956 | 122.2687 | 122.5616 | -122.8683 | -122.8821
633.9531 | 122.7356 | -60.7269 | 61.8576 | 0.080414 | 0.0042982 | 0.010077 | 0.0028327 | 0.066593 | -0.0022153 | 0.068994 | -60.8047 | 61.908 | -60.9833 | -60.9512 | 61.5051 | -0.018311 | 0.045776 | 0.086975 | 61.9034 | -61.0382 | -0.25635 | 0.050354 | -0.07782 | -0.2243 | -0.35248 | -0.31128 | 0.045776 | 0.17853 | 60.7727 | 60.8139 | 122.2321 | 122.6349 | -0.07782 | 122.6303 | 60.7086 | -0.31128 | 122.6349 | -0.07782 | 60.7086 | 122.2321 | 122.6303 | -122.8409 | -122.8958
634.9062 | 122.7951 | -60.704 | 61.8713 | -0.14084 | 0.0062208 | 0.0085812 | 0.0024053 | 0.067447 | -0.00071986 | 0.068567 | -60.7544 | 61.9034 | -60.9787 | -60.8963 | 61.5463 | 0.054932 | 0.009155 | 0.16937 | 61.8576 | -61.0153 | -0.27466 | 0.032043 | -0.050354 | -0.19226 | -0.32501 | -0.31128 | -0.013733 | 0.2243 | 60.7132 | 60.8734 | 122.2504 | 122.6074 | -0.050354 | 122.5616 | 60.759 | -0.31128 | 122.6074 | -0.050354 | 60.759 | 122.2504 | 122.5616 | -122.85 | -122.8867
635.9688 | 122.7402 | -60.7224 | 61.8896 | -0.26291 | 0.004939 | 0.0043088 | -0.0022943 | 0.06702 | 0.00034814 | 0.067926 | -60.8093 | 61.94 | -60.9924 | -60.9512 | 61.5326 | 0.073242 | 0.12817 | 0.19226 | 61.9171 | -61.0199 | -0.27008 | 0.050354 | -0.086975 | -0.22888 | -0.35706 | -0.29755 | 0.027466 | 0.18311 | 60.8505 | 60.9146 | 122.2549 | 122.6624 | -0.086975 | 122.6395 | 60.7956 | -0.29755 | 122.6624 | -0.086975 | 60.7956 | 122.2549 | 122.6395 | -122.8821 | -122.9095
636.9062 | 122.7814 | -60.6995 | 61.8988 | -0.072174 | 0.0047254 | 0.0077268 | 0.0009101 | 0.068088 | 0.00034814 | 0.068567 | -60.7498 | 61.8988 | -60.9833 | -60.8871 | 61.5509 | 0.073242 | 0.032043 | 0.20599 | 61.8622 | -60.9787 | -0.28381 | 0 | -0.050354 | -0.18768 | -0.3479 | -0.27924 | -0.036621 | 0.23346 | 60.7315 | 60.9055 | 122.2504 | 122.5983 | -0.050354 | 122.5616 | 60.7727 | -0.27924 | 122.5983 | -0.050354 | 60.7727 | 122.2504 | 122.5616 | -122.8821 | -122.8775
637.9531 | 122.7493 | -60.704 | 61.9034 | -0.20187 | 0.00323 | 0.013067 | 0.0006965 | 0.06702 | -0.00029266 | 0.065789 | -60.8047 | 61.9125 | -61.0016 | -60.9192 | 61.5234 | 0.059509 | 0.15106 | 0.18768 | 61.8805 | -61.0016 | -0.29755 | 0.009156 | -0.10071 | -0.21515 | -0.37994 | -0.29755 | -0.022888 | 0.19684 | 60.8551 | 60.8917 | 122.2275 | 122.6166 | -0.10071 | 122.5845 | 60.7635 | -0.29755 | 122.6166 | -0.10071 | 60.7635 | 122.2275 | 122.5845 | -122.905 | -122.905
638.9062 | 122.7585 | -60.7086 | 61.9125 | -0.13321 | 0.0040846 | 0.0060178 | 0.0021917 | 0.065952 | -0.0017881 | 0.067712 | -60.7773 | 61.908 | -60.9787 | -60.8963 | 61.5509 | 0.091553 | 0.082397 | 0.21973 | 61.8668 | -61.0016 | -0.27008 | -0.004578 | -0.068665 | -0.18768 | -0.36163 | -0.29297 | -0.045777 | 0.20142 | 60.791 | 60.9283 | 122.2595 | 122.6166 | -0.068665 | 122.5754 | 60.8002 | -0.29297 | 122.6166 | -0.068665 | 60.8002 | 122.2595 | 122.5754 | -122.8912 | -122.9141
639.9688 | 122.7493 | -60.7361 | 61.8668 | 0.21011 | 0.0072888 | 0.0077268 | 0.0019781 | 0.06702 | -7.9062e-05 | 0.070276 | -60.8276 | 61.8851 | -60.9833 | -60.9833 | 61.4868 | -0.054932 | -0.022888 | 0.054932 | 61.8896 | -61.0199 | -0.24719 | 0.018311 | -0.091553 | -0.24719 | -0.37994 | -0.28381 | 0.022888 | 0.15564 | 60.7132 | 60.791 | 122.2229 | 122.6212 | -0.091553 | 122.6257 | 60.6812 | -0.28381 | 122.6212 | -0.091553 | 60.6812 | 122.2229 | 122.6257 | -122.85 | -122.8867
640.9062 | 122.7493 | -60.7269 | 61.908 | -0.17899 | 0.0028028 | 0.0077268 | -0.0005853 | 0.064884 | -0.00093346 | 0.066858 | -60.8139 | 61.8713 | -60.965 | -60.9192 | 61.5372 | 0.045776 | 0.14648 | 0.18768 | 61.9125 | -60.997 | -0.23804 | -0.036621 | -0.086975 | -0.19226 | -0.37079 | -0.27008 | 0.004578 | 0.15106 | 60.8734 | 60.9146 | 122.2641 | 122.5983 | -0.086975 | 122.6395 | 60.7727 | -0.27008 | 122.5983 | -0.086975 | 60.7727 | 122.2641 | 122.6395 | -122.8729 | -122.905
641.9688 | 122.7859 | -60.6995 | 61.8851 | -0.12558 | 0.002162 | 0.0055906 | 0.0026191 | 0.067661 | -0.00050626 | 0.068567 | -60.7498 | 61.9217 | -60.9879 | -60.8734 | 61.5784 | 0.09613 | 0.050354 | 0.21973 | 61.908 | -61.0153 | -0.28839 | 0.036621 | -0.050354 | -0.17395 | -0.3067 | -0.31586 | 0.022888 | 0.23804 | 60.7498 | 60.9192 | 122.2778 | 122.6212 | -0.050354 | 122.6074 | 60.7956 | -0.31586 | 122.6212 | -0.050354 | 60.7956 | 122.2778 | 122.6074 | -122.8729 | -122.9004
642.9062 | 122.7631 | -60.7315 | 61.8851 | -0.43839 | 0.0013074 | 0.0083676 | -0.0020807 | 0.06467 | -0.00029266 | 0.068139 | -60.8322 | 61.8622 | -61.0199 | -60.9375 | 61.528 | 0.041199 | 0.14191 | 0.17853 | 61.9034 | -60.9833 | -0.28839 | -0.022888 | -0.10071 | -0.20599 | -0.35706 | -0.25177 | 0.01831 | 0.18768 | 60.8734 | 60.91 | 122.2595 | 122.5937 | -0.10071 | 122.6349 | 60.7727 | -0.25177 | 122.5937 | -0.10071 | 60.7727 | 122.2595 | 122.6349 | -122.905 | -122.8683
643.9688 | 122.7493 | -60.6903 | 61.908 | -0.48416 | 0.0025892 | 0.0051632 | 0.0009101 | 0.066379 | -0.0022153 | 0.069848 | -60.8368 | 61.8851 | -60.9787 | -60.9238 | 61.5097 | 0.045776 | 0.14191 | 0.19226 | 61.9217 | -60.997 | -0.28839 | -0.022888 | -0.14648 | -0.23346 | -0.39825 | -0.3067 | 0.013733 | 0.14191 | 60.8322 | 60.8826 | 122.2 | 122.5754 | -0.14648 | 122.612 | 60.7361 | -0.3067 | 122.5754 | -0.14648 | 60.7361 | 122.2 | 122.612 | -122.8867 | -122.905
644.9062 | 122.7402 | -60.7498 | 61.9034 | 0.072784 | 0.0042982 | 0.0094358 | 0.0024053 | 0.065952 | -0.00071986 | 0.068353 | -60.8093 | 61.9125 | -60.997 | -60.9467 | 61.4685 | -0.032043 | 0.036621 | 0.068665 | 61.8668 | -61.0245 | -0.24719 | 0.009156 | -0.059509 | -0.19684 | -0.43488 | -0.27466 | -0.036621 | 0.18768 | 60.7864 | 60.8185 | 122.2183 | 122.6624 | -0.059509 | 122.6166 | 60.7178 | -0.27466 | 122.6624 | -0.059509 | 60.7178 | 122.2183 | 122.6166 | -122.9004 | -122.9279
645.9531 | 122.7676 | -60.7132 | 61.9034 | -0.16373 | 0.0028028 | 0.0072996 | 0.0011237 | 0.067447 | -0.0017881 | 0.067071 | -60.7819 | 61.8896 | -60.997 | -60.9055 | 61.5417 | 0.050354 | 0.091553 | 0.20142 | 61.9034 | -60.9924 | -0.28381 | -0.013733 | -0.068664 | -0.19226 | -0.36163 | -0.27924 | 0 | 0.21515 | 60.8047 | 60.9146 | 122.2549 | 122.6028 | -0.068664 | 122.6166 | 60.7636 | -0.27924 | 122.6028 | -0.068664 | 60.7636 | 122.2549 | 122.6166 | -122.9004 | -122.8958
646.9062 | 122.7631 | -60.7178 | 61.908 | 0.32455 | 0.0023756 | 0.0058042 | 0.0006965 | 0.064243 | -0.0015745 | 0.066644 | -60.9741 | 61.8668 | -60.9879 | -60.9421 | 61.528 | 0.073242 | 0.14191 | 0.16937 | 61.9308 | -60.9879 | -0.27008 | -0.041199 | -0.25635 | -0.22431 | -0.37994 | -0.27008 | 0.022888 | 0.013733 | 60.8597 | 60.8871 | 122.2458 | 122.5845 | -0.25635 | 122.6486 | 60.791 | -0.27008 | 122.5845 | -0.25635 | 60.791 | 122.2458 | 122.6486 | -122.8958 | -122.8958
647.9531 | 123.0057 | -60.6583 | 61.9308 | -0.10269 | 0.0060072 | 0.0040952 | -0.0035761 | 0.065311 | -0.0022153 | 0.069848 | -60.7269 | 61.7935 | -60.9512 | -60.8231 | 61.6516 | 0.16022 | -0.054932 | 0.3067 | 61.853 | -60.9512 | -0.29297 | -0.13733 | -0.068665 | -0.16479 | -0.27924 | -0.29297 | -0.07782 | 0.2243 | 60.6033 | 60.965 | 122.3099 | 122.4518 | -0.068665 | 122.5113 | 60.8185 | -0.29297 | 122.4518 | -0.068665 | 60.8185 | 122.3099 | 122.5113 | -122.8821 | -122.8821
648.9062 | 122.7676 | -60.7132 | 61.94 | -0.27054 | 0.0042982 | 0.0038816 | 0.0013373 | 0.063602 | -0.00093346 | 0.068139 | -60.8139 | 61.8668 | -60.9833 | -60.9146 | 61.5143 | 0.032043 | 0.14191 | 0.1831 | 61.8942 | -60.9924 | -0.27008 | -0.073242 | -0.10071 | -0.20142 | -0.42572 | -0.27924 | -0.045776 | 0.16937 | 60.8551 | 60.8963 | 122.2275 | 122.58 | -0.10071 | 122.6074 | 60.7452 | -0.27924 | 122.58 | -0.10071 | 60.7452 | 122.2275 | 122.6074 | -122.9233 | -122.9324
649.9531 | 122.7951 | -60.6995 | 61.8851 | -0.087433 | 0.0045118 | 0.006445 | 0.0045417 | 0.065525 | -0.0024289 | 0.06643 | -60.7452 | 61.8896 | -61.0016 | -60.8688 | 61.5463 | 0.068665 | 0.022888 | 0.17853 | 61.8668 | -60.9833 | -0.30212 | 0.004577 | -0.045776 | -0.16937 | -0.33875 | -0.28381 | -0.018311 | 0.25635 | 60.7224 | 60.878 | 122.2458 | 122.5891 | -0.045776 | 122.5662 | 60.7681 | -0.28381 | 122.5891 | -0.045776 | 60.7681 | 122.2458 | 122.5662 | -122.8867 | -122.8683
650.9062 | 122.7264 | -60.7086 | 61.8988 | -0.25528 | 0.0025892 | 0.0017454 | 0.0004827 | 0.064456 | -0.0020017 | 0.067926 | -60.6125 | 61.908 | -60.9741 | -60.9695 | 61.528 | 0.050354 | 0.14648 | 0.1831 | 61.8988 | -61.0016 | -0.2655 | 0.009155 | 0.09613 | -0.26093 | -0.37079 | -0.29297 | 0 | 0.36163 | 60.8551 | 60.8917 | 122.2366 | 122.6166 | 0.09613 | 122.6074 | 60.759 | -0.29297 | 122.6166 | 0.09613 | 60.759 | 122.2366 | 122.6074 | -122.8729 | -122.9004
651.9688 | 122.7539 | -60.7178 | 61.9034 | -0.24765 | 0.00323 | 0.0038816 | -0.0020807 | 0.063602 | -0.0011471 | 0.068567 | -60.7727 | 61.8576 | -60.9879 | -60.9146 | 61.5555 | 0.073242 | 0.1236 | 0.20599 | 61.8896 | -60.9741 | -0.27008 | -0.045776 | -0.054932 | -0.19684 | -0.3479 | -0.25635 | -0.013733 | 0.21515 | 60.8414 | 60.9238 | 122.2733 | 122.5754 | -0.054932 | 122.6074 | 60.791 | -0.25635 | 122.5754 | -0.054932 | 60.791 | 122.2733 | 122.6074 | -122.8912 | -122.8775
652.9062 | 122.7905 | -60.6766 | 61.8805 | -0.20187 | 0.0013074 | 0.0072996 | -0.0022943 | 0.064243 | -0.00093346 | 0.067712 | -60.7636 | 61.8256 | -60.9558 | -60.8414 | 61.6013 | 0.1236 | 0.032043 | 0.2655 | 61.8668 | -60.965 | -0.27924 | -0.054931 | -0.086975 | -0.16479 | -0.27924 | -0.28839 | -0.013733 | 0.19226 | 60.7086 | 60.9421 | 122.2778 | 122.5021 | -0.086975 | 122.5433 | 60.8002 | -0.28839 | 122.5021 | -0.086975 | 60.8002 | 122.2778 | 122.5433 | -122.8363 | -122.8455
653.9531 | 122.8455 | -60.6766 | 61.8347 | -0.17136 | 0.0010938 | 0.0070858 | -0.0014399 | 0.064029 | 0.00034814 | 0.067712 | -60.7132 | 61.7889 | -60.9375 | -60.7681 | 61.6562 | 0.12817 | -0.091553 | 0.33417 | 61.8301 | -60.9421 | -0.26093 | -0.045777 | -0.036621 | -0.091552 | -0.17853 | -0.2655 | -0.004578 | 0.2243 | 60.585 | 61.0107 | 122.3328 | 122.4655 | -0.036621 | 122.5067 | 60.8047 | -0.2655 | 122.4655 | -0.036621 | 60.8047 | 122.3328 | 122.5067 | -122.7722 | -122.7768
654.9062 | 122.7814 | -60.6903 | 61.8759 | -0.4155 | 0.0064344 | 0.0094358 | 0.0045417 | 0.065097 | -0.0015745 | 0.066003 | -60.7269 | 61.8988 | -61.0016 | -60.8688 | 61.5417 | 0.045776 | 0.013733 | 0.17395 | 61.8805 | -61.0107 | -0.31128 | 0.022888 | -0.036621 | -0.17853 | -0.33417 | -0.32043 | 0.004577 | 0.27466 | 60.704 | 60.8643 | 122.2321 | 122.5891 | -0.036621 | 122.5708 | 60.7361 | -0.32043 | 122.5891 | -0.036621 | 60.7361 | 122.2321 | 122.5708 | -122.8775 | -122.8867
655.9688 | 122.8546 | -60.6674 | 61.8347 | -0.19424 | 0.0028028 | 0.0085812 | -0.0027215 | 0.063816 | -0.00029266 | 0.06643 | -60.7086 | 61.7889 | -60.9375 | -60.5392 | 61.7661 | 0.009155 | -0.23804 | 0.32044 | 61.8073 | -60.9604 | -0.27008 | -0.045777 | -0.041199 | 0.12817 | -0.068665 | -0.29297 | -0.027466 | 0.22888 | 60.4294 | 60.9879 | 122.4335 | 122.4564 | -0.041199 | 122.4747 | 60.6766 | -0.29297 | 122.4564 | -0.041199 | 60.6766 | 122.4335 | 122.4747 | -122.7722 | -122.7951
656.9062 | 122.7493 | -60.7132 | 61.9034 | -0.24765 | 0.0030164 | 0.0062314 | 0.0036871 | 0.064243 | -0.0013609 | 0.067926 | -60.8276 | 61.8896 | -60.965 | -60.9238 | 61.5234 | 0.036621 | 0.12817 | 0.17395 | 61.8851 | -61.0016 | -0.25177 | -0.013733 | -0.11444 | -0.21057 | -0.37994 | -0.28839 | -0.01831 | 0.13733 | 60.8414 | 60.8871 | 122.2366 | 122.6028 | -0.11444 | 122.5983 | 60.7498 | -0.28839 | 122.6028 | -0.11444 | 60.7498 | 122.2366 | 122.5983 | -122.8683 | -122.905
657.9531 | 122.8226 | -60.6857 | 61.8805 | -0.17899 | 0.001521 | 0.0038816 | -0.0040033 | 0.064029 | 0.0012027 | 0.065362 | -60.7361 | 61.8073 | -60.9558 | -60.8185 | 61.6013 | 0.11902 | 0.009155 | 0.28381 | 61.8668 | -60.9558 | -0.27008 | -0.073242 | -0.050354 | -0.13275 | -0.27924 | -0.27008 | -0.013733 | 0.21973 | 60.6949 | 60.9695 | 122.287 | 122.493 | -0.050354 | 122.5525 | 60.8047 | -0.27008 | 122.493 | -0.050354 | 60.8047 | 122.287 | 122.5525 | -122.8363 | -122.8363
658.9062 | 122.7585 | -60.6995 | 61.9034 | -0.24765 | 0.0019482 | 0.00067718 | -0.0001581 | 0.063175 | -0.0020017 | 0.067926 | -60.7681 | 61.8347 | -60.9558 | -60.91 | 61.5509 | 0.064087 | 0.10071 | 0.20599 | 61.8622 | -61.0016 | -0.25635 | -0.068664 | -0.068664 | -0.21057 | -0.35248 | -0.30212 | -0.041198 | 0.18768 | 60.8002 | 60.9055 | 122.2504 | 122.5342 | -0.068664 | 122.5616 | 60.7636 | -0.30212 | 122.5342 | -0.068664 | 60.7636 | 122.2504 | 122.5616 | -122.8592 | -122.905
659.9688 | 122.8363 | -60.6903 | 61.8668 | -0.018768 | 0.0025892 | 0.005377 | -0.0016535 | 0.061893 | -0.00093346 | 0.067285 | -60.7727 | 61.8484 | -60.9512 | -60.8917 | 61.5784 | 0.064087 | -0.07782 | 0.21515 | 61.8347 | -60.9787 | -0.26093 | -0.01831 | -0.082397 | -0.20142 | -0.28839 | -0.28839 | -0.032043 | 0.17853 | 60.6125 | 60.9055 | 122.2687 | 122.5388 | -0.082397 | 122.525 | 60.7544 | -0.28839 | 122.5388 | -0.082397 | 60.7544 | 122.2687 | 122.525 | -122.818 | -122.8455
660.9062 | 122.6898 | -60.7315 | 61.908 | -0.24765 | 0.0040846 | 0.003668 | 0.0011237 | 0.062534 | -0.0011471 | 0.067926 | -60.8139 | 61.8668 | -61.0062 | -60.9055 | 61.528 | -0.022888 | 0.42572 | 0.28839 | 61.9034 | -60.9467 | -0.27466 | -0.041199 | -0.082398 | -0.17395 | -0.37994 | -0.21515 | -0.004578 | 0.19226 | 61.1572 | 61.0199 | 122.2595 | 122.5983 | -0.082398 | 122.6349 | 60.7086 | -0.21515 | 122.5983 | -0.082398 | 60.7086 | 122.2595 | 122.6349 | -122.9141 | -122.8546
661.9531 | 122.8683 | -60.6628 | 61.8713 | -0.049286 | 0.0023756 | 0.0060178 | -0.0040033 | 0.064029 | -7.9062e-05 | 0.068139 | -60.7407 | 61.8027 | -60.9558 | -60.8185 | 61.6196 | 0.12817 | -0.091553 | 0.3067 | 61.821 | -60.9558 | -0.29297 | -0.068665 | -0.07782 | -0.15564 | -0.25177 | -0.29297 | -0.050354 | 0.21515 | 60.5713 | 60.9695 | 122.2824 | 122.4655 | -0.07782 | 122.4838 | 60.791 | -0.29297 | 122.4655 | -0.07782 | 60.791 | 122.2824 | 122.4838 | -122.8271 | -122.8271
662.9062 | 122.731 | -60.7132 | 61.9125 | -0.14847 | 0.0040846 | 0.0075132 | 0.0017645 | 0.062961 | -0.0020017 | 0.067498 | -60.7819 | 61.8622 | -61.0016 | -60.8963 | 61.5326 | 0.054932 | 0.11444 | 0.20599 | 61.8988 | -60.9787 | -0.28839 | -0.050354 | -0.068664 | -0.1831 | -0.37994 | -0.2655 | -0.013733 | 0.21973 | 60.8276 | 60.9192 | 122.2458 | 122.5754 | -0.068664 | 122.612 | 60.7681 | -0.2655 | 122.5754 | -0.068664 | 60.7681 | 122.2458 | 122.612 | -122.9141 | -122.8912
663.9531 | 122.85 | -60.672 | 61.8713 | -0.14847 | 0.00045296 | 0.0043088 | 0.0019781 | 0.065952 | -0.0030697 | 0.067071 | -60.7132 | 61.8027 | -60.9375 | -60.7498 | 61.6104 | 0.091553 | -0.054932 | 0.30212 | 61.8301 | -60.9421 | -0.2655 | -0.068665 | -0.041199 | -0.07782 | -0.26093 | -0.27008 | -0.041199 | 0.2243 | 60.6171 | 60.9741 | 122.2824 | 122.4747 | -0.041199 | 122.5021 | 60.7635 | -0.27008 | 122.4747 | -0.041199 | 60.7635 | 122.2824 | 122.5021 | -122.8088 | -122.8134
664.9219 | 122.7264 | -60.7544 | 61.9034 | 0.034637 | 0.006648 | 0.0070858 | 0.0066779 | 0.063175 | -0.0022153 | 0.069635 | -60.8185 | 61.8805 | -61.0153 | -60.9512 | 61.4548 | -0.064087 | 0.022888 | 0.036621 | 61.8622 | -61.0519 | -0.26093 | -0.022888 | -0.064086 | -0.19684 | -0.44861 | -0.29755 | -0.041198 | 0.19684 | 60.7773 | 60.791 | 122.2092 | 122.6349 | -0.064086 | 122.6166 | 60.6903 | -0.29755 | 122.6349 | -0.064086 | 60.6903 | 122.2092 | 122.6166 | -122.9187 | -122.9553
665.9531 | 122.85 | -60.6812 | 61.8668 | -0.23239 | 0.0013074 | 0.0034544 | -0.0016535 | 0.062961 | -0.00029266 | 0.066217 | -60.7452 | 61.7981 | -60.9695 | -60.8093 | 61.6287 | 0.15564 | -0.036621 | 0.30212 | 61.8484 | -60.9512 | -0.28839 | -0.068664 | -0.064087 | -0.12817 | -0.23804 | -0.27008 | -0.01831 | 0.2243 | 60.6445 | 60.9833 | 122.3099 | 122.4792 | -0.064087 | 122.5296 | 60.8368 | -0.27008 | 122.4792 | -0.064087 | 60.8368 | 122.3099 | 122.5296 | -122.8363 | -122.818
666.9062 | 122.7905 | -60.6766 | 61.908 | -0.18662 | 0.0025892 | 0.0032406 | -0.0001581 | 0.063816 | -0.0024289 | 0.068994 | -60.7773 | 61.8118 | -60.9695 | -60.8368 | 61.5875 | 0.10986 | 0.073242 | 0.24719 | 61.8484 | -60.9833 | -0.29297 | -0.09613 | -0.10071 | -0.16022 | -0.32043 | -0.3067 | -0.059509 | 0.19226 | 60.7498 | 60.9238 | 122.2641 | 122.4884 | -0.10071 | 122.525 | 60.7864 | -0.3067 | 122.4884 | -0.10071 | 60.7864 | 122.2641 | 122.525 | -122.8775 | -122.8912
667.9531 | 122.8546 | -60.6949 | 61.8713 | -0.026398 | 0.0019482 | 0.0058042 | -0.0050715 | 0.063816 | -0.0017881 | 0.067498 | -60.7956 | 61.7935 | -60.9741 | -60.8551 | 61.6013 | 0.10071 | -0.09613 | 0.22888 | 61.8347 | -60.9421 | -0.27924 | -0.07782 | -0.10071 | -0.16022 | -0.27008 | -0.24719 | -0.036621 | 0.17853 | 60.5988 | 60.9238 | 122.2961 | 122.4884 | -0.10071 | 122.5296 | 60.7956 | -0.24719 | 122.4884 | -0.10071 | 60.7956 | 122.2961 | 122.5296 | -122.8455 | -122.8134
668.9062 | 122.8271 | -60.6812 | 61.8851 | -0.23239 | 0.0053662 | 0.005377 | 0.0013373 | 0.062747 | -0.00093346 | 0.06643 | -60.7452 | 61.8347 | -60.9558 | -60.8414 | 61.6013 | 0.1236 | 0.032043 | 0.26093 | 61.8301 | -60.9604 | -0.27466 | -0.050354 | -0.064087 | -0.16022 | -0.28381 | -0.27924 | -0.054932 | 0.21057 | 60.7132 | 60.9421 | 122.2824 | 122.5159 | -0.064087 | 122.5113 | 60.8047 | -0.27924 | 122.5159 | -0.064087 | 60.8047 | 122.2824 | 122.5113 | -122.8409 | -122.8455
669.9844 | 122.7539 | -60.7361 | 61.8576 | -0.026398 | 0.0055798 | 0.0085812 | 0.0073187 | 0.064884 | -0.0026425 | 0.067285 | -60.7681 | 61.853 | -61.0016 | -60.8963 | 61.5326 | 0.013733 | -0.009155 | 0.13275 | 61.8164 | -60.997 | -0.2655 | -0.004578 | -0.032043 | -0.16022 | -0.32501 | -0.26093 | -0.041199 | 0.23346 | 60.7269 | 60.8688 | 122.2687 | 122.5891 | -0.032043 | 122.5525 | 60.7498 | -0.26093 | 122.5891 | -0.032043 | 60.7498 | 122.2687 | 122.5525 | -122.8592 | -122.8546
670.9062 | 122.7493 | -60.6903 | 61.8896 | -0.14847 | 0.0045118 | 0.003027 | 0.0013373 | 0.064243 | -0.0030697 | 0.066858 | -60.7681 | 61.853 | -60.9833 | -60.878 | 61.5829 | 0.091553 | 0.086975 | 0.19684 | 61.8942 | -60.9467 | -0.29297 | -0.036621 | -0.077819 | -0.18768 | -0.3067 | -0.25635 | 0.004578 | 0.21515 | 60.7773 | 60.8871 | 122.2733 | 122.5433 | -0.077819 | 122.5845 | 60.7819 | -0.25635 | 122.5433 | -0.077819 | 60.7819 | 122.2733 | 122.5845 | -122.8729 | -122.8363
671.9062 | 122.7127 | -60.6857 | 61.8896 | -0.24002 | 0.0023756 | 0.0045224 | 0.0006965 | 0.063175 | -0.0034971 | 0.067285 | -60.7864 | 61.8439 | -60.9604 | -60.8871 | 61.5555 | 0.068665 | 0.11902 | 0.2243 | 61.8713 | -60.9512 | -0.27466 | -0.045776 | -0.10071 | -0.20142 | -0.33417 | -0.2655 | -0.01831 | 0.17395 | 60.8047 | 60.91 | 122.2412 | 122.5296 | -0.10071 | 122.5571 | 60.7544 | -0.2655 | 122.5296 | -0.10071 | 60.7544 | 122.2412 | 122.5571 | -122.85 | -122.8409
672.9531 | 122.8088 | -60.6857 | 61.8301 | 0.15671 | 0.0034436 | 0.003668 | 5.5496e-05 | 0.064243 | 0.00056194 | 0.067498 | -60.7681 | 61.7432 | -60.9924 | -60.8688 | 61.5692 | 0.059509 | -0.16937 | 0.16937 | 61.8027 | -60.9421 | -0.3067 | -0.086975 | -0.082397 | -0.1831 | -0.26093 | -0.25635 | -0.027466 | 0.22431 | 60.5164 | 60.8551 | 122.2549 | 122.4289 | -0.082397 | 122.4884 | 60.7452 | -0.25635 | 122.4289 | -0.082397 | 60.7452 | 122.2549 | 122.4884 | -122.8226 | -122.7722
673.9062 | 122.7264 | -60.704 | 61.908 | -0.27054 | 0.0053662 | 0.0023862 | 0.0024053 | 0.063388 | -0.0047787 | 0.06878 | -60.8185 | 61.8393 | -60.9924 | -60.704 | 61.5967 | 0.045776 | -0.022888 | 0.15106 | 61.8484 | -61.0016 | -0.28839 | -0.068665 | -0.11444 | 0 | -0.31128 | -0.29755 | -0.059509 | 0.17395 | 60.6812 | 60.8551 | 122.3007 | 122.5433 | -0.11444 | 122.5525 | 60.7498 | -0.29755 | 122.5433 | -0.11444 | 60.7498 | 122.3007 | 122.5525 | -122.9004 | -122.9095
674.9688 | 122.7768 | -60.704 | 61.9125 | -0.24002 | 0.0034436 | 0.0077268 | -0.0012261 | 0.062534 | -0.0017881 | 0.067712 | -60.7544 | 61.8484 | -60.9467 | -60.8643 | 61.5555 | 0.068665 | 0.086975 | 0.19226 | 61.853 | -60.9787 | -0.24261 | -0.064087 | -0.050354 | -0.16022 | -0.35706 | -0.27466 | -0.05951 | 0.19226 | 60.791 | 60.8963 | 122.2595 | 122.5525 | -0.050354 | 122.5571 | 60.7727 | -0.27466 | 122.5525 | -0.050354 | 60.7727 | 122.2595 | 122.5571 | -122.8592 | -122.8912
675.9062 | 122.85 | -60.6995 | 61.8668 | 0.33981 | 0.002162 | 0.0058042 | -0.0014399 | 0.063175 | -0.0022153 | 0.067712 | -60.7132 | 61.7981 | -60.9604 | -60.8139 | 61.6699 | 0.16479 | -0.050354 | 0.31128 | 61.8027 | -60.9329 | -0.26093 | -0.068664 | -0.013733 | -0.11444 | -0.19684 | -0.23346 | -0.064087 | 0.24719 | 60.6491 | 61.0107 | 122.3694 | 122.4976 | -0.013733 | 122.5021 | 60.8643 | -0.23346 | 122.4976 | -0.013733 | 60.8643 | 122.3694 | 122.5021 | -122.8271 | -122.7997
676.9688 | 122.8821 | -60.6674 | 61.8668 | -0.056915 | -0.00082884 | 0.0043088 | -0.0010125 | 0.063602 | 0.00013454 | 0.068994 | -60.7086 | 61.7981 | -60.9421 | -60.7956 | 61.6653 | 0.17395 | -0.10986 | 0.3067 | 61.8164 | -60.9512 | -0.27466 | -0.068664 | -0.041199 | -0.12817 | -0.20142 | -0.28381 | -0.050354 | 0.23346 | 60.5576 | 60.9741 | 122.3328 | 122.4655 | -0.041199 | 122.4838 | 60.8414 | -0.28381 | 122.4655 | -0.041199 | 60.8414 | 122.3328 | 122.4838 | -122.8088 | -122.818
677.9062 | 122.7539 | -60.7315 | 61.9034 | -0.18662 | 0.004939 | 0.008154 | 0.0039007 | 0.061893 | -0.0015745 | 0.068567 | -60.8002 | 61.8576 | -61.0016 | -60.8826 | 61.528 | 0.041199 | 0.11444 | 0.17853 | 61.8988 | -60.997 | -0.27008 | -0.045776 | -0.068665 | -0.15106 | -0.37537 | -0.2655 | -0.004577 | 0.20142 | 60.8459 | 60.91 | 122.2595 | 122.5891 | -0.068665 | 122.6303 | 60.7727 | -0.2655 | 122.5891 | -0.068665 | 60.7727 | 122.2595 | 122.6303 | -122.905 | -122.9004
678.9688 | 122.8775 | -60.704 | 61.853 | -0.041657 | 0.0034436 | 0.0058042 | -0.0016535 | 0.064884 | 0.00077554 | 0.067285 | -60.7636 | 61.7935 | -60.9512 | -60.8185 | 61.6379 | 0.13733 | -0.091553 | 0.28839 | 61.7981 | -60.9421 | -0.24719 | -0.059509 | -0.059509 | -0.11444 | -0.21515 | -0.23804 | -0.054931 | 0.18768 | 60.6125 | 60.9924 | 122.3419 | 122.4976 | -0.059509 | 122.5021 | 60.8414 | -0.23804 | 122.4976 | -0.059509 | 60.8414 | 122.3419 | 122.5021 | -122.8043 | -122.7951
679.9219 | 122.85 | -60.6903 | 61.8484 | 0.30167 | 0.0047254 | 0.0058042 | 0.0045417 | 0.06467 | -0.00093346 | 0.068139 | -60.7361 | 61.8118 | -60.9512 | -60.8505 | 61.5692 | 0.050354 | -0.20142 | 0.15564 | 61.7661 | -61.0016 | -0.26093 | -0.036621 | -0.045776 | -0.16022 | -0.27924 | -0.31128 | -0.082398 | 0.21515 | 60.4889 | 60.8459 | 122.2595 | 122.5021 | -0.045776 | 122.4564 | 60.7407 | -0.31128 | 122.5021 | -0.045776 | 60.7407 | 122.2595 | 122.4564 | -122.7997 | -122.85
680.9688 | 122.9507 | -60.6583 | 61.9034 | -0.17136 | 0.0017346 | 0.00089078 | -0.0020807 | 0.062747 | -0.00071986 | 0.067712 | -60.759 | 61.7752 | -60.9421 | -60.791 | 61.6562 | 0.16022 | -0.059509 | 0.31586 | 61.8118 | -60.9512 | -0.28381 | -0.12817 | -0.10071 | -0.13275 | -0.24719 | -0.29297 | -0.091552 | 0.18311 | 60.5988 | 60.9741 | 122.3145 | 122.4335 | -0.10071 | 122.4701 | 60.8185 | -0.29297 | 122.4335 | -0.10071 | 60.8185 | 122.3145 | 122.4701 | -122.8455 | -122.8546
681.9062 | 122.8455 | -60.6583 | 61.8851 | -3.0553 | 0.0013074 | 0.0077268 | 0.0011237 | 0.063175 | -0.0032835 | 0.066644 | -60.7452 | 61.8439 | -60.9283 | -60.7956 | 61.6425 | 0.13275 | -0.07782 | 0.32501 | 61.821 | -60.9329 | -0.27008 | -0.041199 | -0.086975 | -0.13733 | -0.24262 | -0.27466 | -0.064087 | 0.18311 | 60.5804 | 60.9833 | 122.3007 | 122.5021 | -0.086975 | 122.4792 | 60.791 | -0.27466 | 122.5021 | -0.086975 | 60.791 | 122.3007 | 122.4792 | -122.8134 | -122.818
682.9531 | 122.85 | -60.6766 | 61.853 | -0.056915 | 0.00088016 | 0.0032406 | -0.0001581 | 0.061893 | -0.0011471 | 0.067285 | -60.7636 | 61.7981 | -60.9558 | -60.8093 | 61.615 | 0.10529 | -0.07782 | 0.26093 | 61.8256 | -60.9695 | -0.27924 | -0.054931 | -0.086975 | -0.13275 | -0.23804 | -0.29297 | -0.027465 | 0.19226 | 60.5988 | 60.9375 | 122.2916 | 122.4747 | -0.086975 | 122.5021 | 60.7819 | -0.29297 | 122.4747 | -0.086975 | 60.7819 | 122.2916 | 122.5021 | -122.8088 | -122.8226
683.9062 | 122.7173 | -60.6812 | 61.908 | -0.24002 | 0.001521 | 0.0049496 | 0.0017645 | 0.061679 | -0.0013609 | 0.067926 | -60.759 | 61.8347 | -60.9741 | -60.8551 | 61.5646 | 0.10071 | 0.09613 | 0.23346 | 61.8622 | -60.965 | -0.29297 | -0.073242 | -0.07782 | -0.17395 | -0.34332 | -0.28381 | -0.045776 | 0.21515 | 60.7773 | 60.9146 | 122.2458 | 122.5159 | -0.07782 | 122.5433 | 60.7819 | -0.28381 | 122.5159 | -0.07782 | 60.7819 | 122.2458 | 122.5433 | -122.8821 | -122.8729
684.9688 | 122.7905 | -60.7178 | 61.8896 | -0.049286 | 0.0025892 | 0.009863 | 0.0075323 | 0.065738 | -0.00093346 | 0.070062 | -60.7269 | 61.853 | -60.9879 | -60.9558 | 61.5555 | 0.10529 | 0.022888 | 0.18768 | 61.8301 | -61.0153 | -0.27008 | -0.036621 | -0.009156 | -0.23804 | -0.33417 | -0.29755 | -0.059509 | 0.26093 | 60.7407 | 60.9055 | 122.2733 | 122.5708 | -0.009156 | 122.5479 | 60.8231 | -0.29755 | 122.5708 | -0.009156 | 60.8231 | 122.2733 | 122.5479 | -122.8775 | -122.905
685.9062 | 122.8226 | -60.6857 | 61.8988 | -0.19424 | 0.00045296 | 0.0040952 | -0.0001581 | 0.06467 | -0.0028561 | 0.066644 | -60.7315 | 61.8118 | -60.9879 | -60.8276 | 61.6287 | 0.11902 | 0.041199 | 0.27466 | 61.8439 | -60.9467 | -0.30212 | -0.086975 | -0.045776 | -0.14191 | -0.27008 | -0.26093 | -0.054932 | 0.25635 | 60.7269 | 60.9604 | 122.3145 | 122.4976 | -0.045776 | 122.5296 | 60.8047 | -0.26093 | 122.4976 | -0.045776 | 60.8047 | 122.3145 | 122.5296 | -122.8867 | -122.8455
686.9531 | 122.85 | -60.6903 | 61.8668 | 0.0041197 | 0.00088016 | 0.0049496 | -0.0029351 | 0.062747 | -0.0022153 | 0.068139 | -60.8047 | 61.7935 | -60.9604 | -60.8734 | 61.5921 | 0.073242 | -0.07782 | 0.21515 | 61.7798 | -60.965 | -0.27008 | -0.073242 | -0.11444 | -0.1831 | -0.27466 | -0.27466 | -0.086975 | 0.15564 | 60.6125 | 60.9055 | 122.2824 | 122.4838 | -0.11444 | 122.4701 | 60.7636 | -0.27466 | 122.4838 | -0.11444 | 60.7636 | 122.2824 | 122.4701 | -122.8271 | -122.8317
687.9062 | 122.8363 | -60.7086 | 61.8805 | -0.13321 | 0.002162 | 0.006445 | 0.0015509 | 0.062961 | -0.00093346 | 0.066858 | -60.7452 | 61.7981 | -60.9467 | -60.8139 | 61.615 | 0.14648 | -0.004578 | 0.31128 | 61.821 | -60.9421 | -0.23804 | -0.082397 | -0.036621 | -0.10529 | -0.2655 | -0.23346 | -0.059509 | 0.20142 | 60.704 | 61.0199 | 122.3236 | 122.5067 | -0.036621 | 122.5296 | 60.8551 | -0.23346 | 122.5067 | -0.036621 | 60.8551 | 122.3236 | 122.5296 | -122.8271 | -122.8226
688.9688 | 122.818 | -60.6766 | 61.8484 | 0.011749 | 0.0010938 | 0.0032406 | -0.0001581 | 0.063602 | -0.00093346 | 0.068567 | -60.8093 | 61.7889 | -60.9833 | -60.8871 | 61.7111 | 0.19226 | -0.13733 | 0.082397 | 61.8164 | -60.9604 | -0.3067 | -0.05951 | -0.13275 | -0.21057 | -0.13733 | -0.28381 | -0.032044 | 0.17395 | 60.5392 | 60.759 | 122.3877 | 122.4655 | -0.13275 | 122.493 | 60.8688 | -0.28381 | 122.4655 | -0.13275 | 60.8688 | 122.3877 | 122.493 | -122.8317 | -122.8088
689.9062 | 122.7493 | -60.7178 | 61.9125 | -0.20187 | 0.0051526 | 0.0058042 | 0.0058233 | 0.062747 | 0.00056194 | 0.06643 | -60.7819 | 61.8942 | -60.997 | -60.8871 | 61.5234 | 0.032043 | 0.10986 | 0.17395 | 61.8393 | -60.997 | -0.27924 | -0.018311 | -0.064087 | -0.16937 | -0.3891 | -0.27924 | -0.073243 | 0.21515 | 60.8276 | 60.8917 | 122.2412 | 122.612 | -0.064087 | 122.5571 | 60.7498 | -0.27924 | 122.612 | -0.064087 | 60.7498 | 122.2412 | 122.5571 | -122.9095 | -122.9095
690.9531 | 122.8455 | -60.6628 | 61.8576 | -0.087433 | 0.0028028 | 0.0040952 | -0.0027215 | 0.062107 | -0.00050626 | 0.06878 | -60.7315 | 61.8027 | -60.9512 | -60.7864 | 61.6379 | 0.16937 | -0.045776 | 0.32044 | 61.8027 | -60.9238 | -0.28839 | -0.054932 | -0.068664 | -0.1236 | -0.21973 | -0.26093 | -0.054932 | 0.21973 | 60.6171 | 60.9833 | 122.3007 | 122.4655 | -0.068664 | 122.4655 | 60.8322 | -0.26093 | 122.4655 | -0.068664 | 60.8322 | 122.3007 | 122.4655 | -122.8088 | -122.7814
691.9062 | 122.7448 | -60.704 | 61.9034 | -0.36972 | 0.0030164 | 0.0045224 | 0.0032599 | 0.063175 | -0.0017881 | 0.066644 | -60.8002 | 61.8668 | -61.0062 | -60.8963 | 61.5463 | 0.045776 | 0.1236 | 0.19226 | 61.8484 | -60.997 | -0.30212 | -0.036621 | -0.09613 | -0.19226 | -0.35706 | -0.29297 | -0.054931 | 0.20599 | 60.8276 | 60.8963 | 122.2504 | 122.5708 | -0.09613 | 122.5525 | 60.7498 | -0.29297 | 122.5708 | -0.09613 | 60.7498 | 122.2504 | 122.5525 | -122.9095 | -122.9004
692.9531 | 122.8592 | -60.6537 | 61.8805 | -0.16373 | 0.0036572 | 0.00024998 | 5.5496e-05 | 0.060184 | -0.0024289 | 0.066644 | -60.4477 | 61.8622 | -60.9192 | -60.8505 | 61.6104 | 0.15106 | -0.086975 | 0.29297 | 61.8073 | -60.9375 | -0.2655 | -0.01831 | 0.20599 | -0.19684 | -0.27008 | -0.28381 | -0.073242 | 0.4715 | 60.5667 | 60.9467 | 122.2641 | 122.5159 | 0.20599 | 122.4609 | 60.8047 | -0.28381 | 122.5159 | 0.20599 | 60.8047 | 122.2641 | 122.4609 | -122.7997 | -122.818
693.9062 | 122.8363 | -60.6583 | 61.8896 | -0.17899 | 0.0013074 | 0.0045224 | 0.0006965 | 0.061679 | -0.0015745 | 0.068353 | -60.7407 | 61.7889 | -60.9833 | -60.8093 | 61.615 | 0.14191 | -0.004578 | 0.29755 | 61.8027 | -60.9375 | -0.32501 | -0.10071 | -0.082398 | -0.15106 | -0.27466 | -0.27924 | -0.086975 | 0.24261 | 60.6537 | 60.9558 | 122.2733 | 122.4472 | -0.082398 | 122.4609 | 60.8002 | -0.27924 | 122.4472 | -0.082398 | 60.8002 | 122.2733 | 122.4609 | -122.8729 | -122.8271
694.9531 | 122.8592 | -60.6766 | 61.8759 | -0.049286 | 0.0042982 | 0.0021726 | -0.0018671 | 0.061466 | -0.0013609 | 0.069848 | -60.7819 | 61.7889 | -60.9695 | -60.8231 | 61.615 | 0.10986 | -0.086975 | 0.25177 | 61.7844 | -60.9604 | -0.29297 | -0.086976 | -0.10529 | -0.14648 | -0.26093 | -0.28381 | -0.091553 | 0.18768 | 60.5896 | 60.9283 | 122.2916 | 122.4655 | -0.10529 | 122.4609 | 60.7864 | -0.28381 | 122.4655 | -0.10529 | 60.7864 | 122.2916 | 122.4609 | -122.8455 | -122.8363
695.9062 | 122.8638 | -60.6491 | 61.8668 | -0.095062 | 0.0023756 | 0.0023862 | -0.0003717 | 0.06467 | -0.0034971 | 0.06878 | -60.7269 | 61.7889 | -60.9787 | -60.7819 | 61.6287 | 0.14648 | -0.091553 | 0.31128 | 61.8256 | -60.91 | -0.32959 | -0.07782 | -0.07782 | -0.13275 | -0.23804 | -0.26093 | -0.041198 | 0.25177 | 60.5576 | 60.9604 | 122.2778 | 122.438 | -0.07782 | 122.4747 | 60.7956 | -0.26093 | 122.438 | -0.07782 | 60.7956 | 122.2778 | 122.4747 | -122.8455 | -122.7768
696.9688 | 122.8043 | -60.6857 | 61.8439 | 0.11093 | 0.0013074 | 0.0049496 | -0.0007989 | 0.061679 | -0.0011471 | 0.068567 | -60.8047 | 61.7523 | -60.9695 | -60.8917 | 61.5326 | 0.018311 | -0.11444 | 0.15564 | 61.8073 | -60.9604 | -0.28381 | -0.091553 | -0.11902 | -0.20599 | -0.31128 | -0.27466 | -0.036621 | 0.16479 | 60.5713 | 60.8414 | 122.2183 | 122.438 | -0.11902 | 122.493 | 60.704 | -0.27466 | 122.438 | -0.11902 | 60.704 | 122.2183 | 122.493 | -122.8134 | -122.8043
697.9062 | 122.7539 | -60.7315 | 61.9034 | 1.0799 | 0.0019482 | 0.005377 | 0.0028327 | 0.061252 | -0.0011471 | 0.067926 | -60.8414 | 61.8256 | -61.0153 | -60.91 | 61.5417 | 0.068665 | 0.14648 | 0.17395 | 61.8896 | -60.9833 | -0.28381 | -0.077819 | -0.10986 | -0.17853 | -0.36163 | -0.25177 | -0.013733 | 0.17395 | 60.878 | 60.9055 | 122.2733 | 122.5571 | -0.10986 | 122.6212 | 60.8002 | -0.25177 | 122.5571 | -0.10986 | 60.8002 | 122.2733 | 122.6212 | -122.9187 | -122.8867
698.9531 | 122.8134 | -60.6857 | 61.853 | -0.026398 | 0.00023916 | 0.0040952 | -0.0040033 | 0.063816 | -0.0026425 | 0.066217 | -60.7681 | 61.7981 | -60.9833 | -60.8459 | 61.6104 | 0.11902 | -0.073242 | 0.25177 | 61.8256 | -60.9421 | -0.29755 | -0.054931 | -0.082397 | -0.16022 | -0.24261 | -0.25635 | -0.027465 | 0.21515 | 60.6125 | 60.9375 | 122.2961 | 122.4838 | -0.082397 | 122.5113 | 60.8047 | -0.25635 | 122.4838 | -0.082397 | 60.8047 | 122.2961 | 122.5113 | -122.8363 | -122.7951
699.9062 | 122.8409 | -60.6903 | 61.8713 | -0.36972 | 0.0019482 | 0.0066586 | -0.0001581 | 0.063175 | 0.00056194 | 0.065576 | -60.7315 | 61.7798 | -60.9375 | -60.7727 | 61.6287 | 0.14648 | -0.045776 | 0.32959 | 61.8118 | -60.9329 | -0.24719 | -0.091553 | -0.041198 | -0.082397 | -0.24262 | -0.24261 | -0.059509 | 0.20599 | 60.6445 | 61.0199 | 122.319 | 122.4701 | -0.041198 | 122.5021 | 60.8368 | -0.24261 | 122.4701 | -0.041198 | 60.8368 | 122.319 | 122.5021 | -122.8088 | -122.8043
700.9688 | 122.8043 | -60.7086 | 61.8393 | 0.14908 | 0.0019482 | 0.0034544 | -0.0016535 | 0.061466 | -0.0013609 | 0.067285 | -60.7956 | 61.7844 | -60.9924 | -60.8826 | 61.5326 | 0.013733 | -0.13275 | 0.14648 | 61.7844 | -60.9741 | -0.28381 | -0.054931 | -0.086975 | -0.17395 | -0.3067 | -0.2655 | -0.054931 | 0.19684 | 60.5759 | 60.8551 | 122.2412 | 122.493 | -0.086975 | 122.493 | 60.7224 | -0.2655 | 122.493 | -0.086975 | 60.7224 | 122.2412 | 122.493 | -122.8317 | -122.8134
701.9062 | 122.8409 | -60.672 | 61.8439 | -0.20187 | 0.0017346 | 0.0043088 | -0.0020807 | 0.062961 | -0.00093346 | 0.068994 | -60.7178 | 61.7844 | -60.9604 | -60.7819 | 62.0041 | 0.43488 | -0.35706 | 0.10529 | 61.7661 | -60.965 | -0.28839 | -0.059509 | -0.045776 | -0.10986 | 0.16022 | -0.29297 | -0.07782 | 0.24262 | 60.3149 | 60.7773 | 122.6761 | 122.4564 | -0.045776 | 122.438 | 61.1069 | -0.29297 | 122.4564 | -0.045776 | 61.1069 | 122.6761 | 122.438 | -122.8043 | -122.8088
702.9688 | 122.8592 | -60.7132 | 61.8484 | 0.019379 | 0.00066656 | 0.003668 | -0.0020807 | 0.061893 | -0.0011471 | 0.066217 | -60.8047 | 61.7844 | -60.9924 | -60.8826 | 61.5646 | 0.059509 | -0.07782 | 0.1831 | 61.8118 | -60.9421 | -0.27924 | -0.064087 | -0.091553 | -0.16937 | -0.28381 | -0.22888 | -0.036621 | 0.18768 | 60.6354 | 60.8963 | 122.2778 | 122.4976 | -0.091553 | 122.525 | 60.7727 | -0.22888 | 122.4976 | -0.091553 | 60.7727 | 122.2778 | 122.525 | -122.8409 | -122.7905
703.9062 | 122.8775 | -60.672 | 61.8851 | -0.064545 | 0.0030164 | 0.0072996 | -0.0001581 | 0.060184 | 0.00056194 | 0.068353 | -60.7452 | 61.7889 | -60.965 | -60.7956 | 61.6333 | 0.14648 | -0.091553 | 0.31586 | 61.7844 | -60.9329 | -0.29297 | -0.096131 | -0.073242 | -0.1236 | -0.25177 | -0.26093 | -0.10071 | 0.21973 | 60.5804 | 60.9879 | 122.3053 | 122.4609 | -0.073242 | 122.4564 | 60.8185 | -0.26093 | 122.4609 | -0.073242 | 60.8185 | 122.3053 | 122.4564 | -122.85 | -122.818
704.9688 | 122.8271 | -60.6766 | 61.8301 | -1.6896 | 0.0019482 | 0.0051632 | -0.0003717 | 0.062534 | -0.0017881 | 0.066644 | -60.8047 | 61.7935 | -60.9604 | -60.8871 | 61.5372 | 0.018311 | -0.07782 | 0.17395 | 61.7844 | -60.9512 | -0.28381 | -0.036621 | -0.12817 | -0.21057 | -0.29297 | -0.27466 | -0.045776 | 0.15564 | 60.5988 | 60.8505 | 122.2137 | 122.4701 | -0.12817 | 122.4609 | 60.6949 | -0.27466 | 122.4701 | -0.12817 | 60.6949 | 122.2137 | 122.4609 | -122.7905 | -122.7814
705.9062 | 122.7493 | -60.6812 | 61.9125 | -0.18662 | 0.0019482 | 0.001959 | 0.0019781 | 0.062747 | -0.0028561 | 0.06878 | -60.7681 | 61.8073 | -60.9787 | -60.8734 | 61.5692 | 0.059509 | 0.082397 | 0.21973 | 61.8347 | -60.9375 | -0.29755 | -0.10529 | -0.086975 | -0.19226 | -0.34332 | -0.25635 | -0.07782 | 0.21057 | 60.7635 | 60.9009 | 122.2504 | 122.4884 | -0.086975 | 122.5159 | 60.7407 | -0.25635 | 122.4884 | -0.086975 | 60.7407 | 122.2504 | 122.5159 | -122.8912 | -122.85
706.9531 | 122.7493 | -60.6995 | 61.8713 | 0.19485 | 0.0040846 | 0.0079404 | 0.0060369 | 0.063816 | -0.0022153 | 0.066217 | -60.8322 | 61.8118 | -61.0199 | -60.9283 | 61.4868 | -0.054932 | -0.054932 | 0.054932 | 61.8256 | -60.997 | -0.32043 | -0.059509 | -0.13275 | -0.22888 | -0.38452 | -0.29755 | -0.045776 | 0.18768 | 60.6445 | 60.7544 | 122.1863 | 122.5113 | -0.13275 | 122.525 | 60.6445 | -0.29755 | 122.5113 | -0.13275 | 60.6445 | 122.1863 | 122.525 | -122.8912 | -122.8683
707.9062 | 122.8775 | -60.6583 | 61.8164 | -0.049286 | 0.002162 | 0.004736 | -0.0029351 | 0.062107 | -0.0028561 | 0.066003 | -60.7727 | 61.7706 | -60.9558 | -60.7864 | 61.6379 | 0.12817 | -0.1236 | 0.28839 | 61.7981 | -60.9421 | -0.29755 | -0.045776 | -0.11444 | -0.12817 | -0.17853 | -0.28381 | -0.01831 | 0.18311 | 60.5347 | 60.9467 | 122.2961 | 122.4289 | -0.11444 | 122.4564 | 60.7864 | -0.28381 | 122.4289 | -0.11444 | 60.7864 | 122.2961 | 122.4564 | -122.7722 | -122.7585
708.9688 | 122.7997 | -60.6812 | 61.8347 | 0.14908 | 0.0010938 | 0.005377 | -0.0005853 | 0.064243 | -0.0026425 | 0.067712 | -60.7956 | 61.7523 | -60.9604 | -60.8734 | 61.5555 | 0.022888 | -0.1236 | 0.13733 | 61.8027 | -60.9467 | -0.27924 | -0.082398 | -0.11444 | -0.19226 | -0.27924 | -0.2655 | -0.032044 | 0.1648 | 60.5576 | 60.8185 | 122.2366 | 122.4335 | -0.11444 | 122.4838 | 60.704 | -0.2655 | 122.4335 | -0.11444 | 60.704 | 122.2366 | 122.4838 | -122.7951 | -122.7814
709.9062 | 122.85 | -60.6674 | 61.8484 | -0.23239 | 0.002162 | 0.0060178 | -0.0005853 | 0.061679 | -0.0034971 | 0.068139 | -60.7224 | 61.8027 | -60.9512 | -60.7956 | 61.6241 | 0.13733 | -0.045776 | 0.30212 | 61.8118 | -60.9512 | -0.28381 | -0.045777 | -0.054932 | -0.12817 | -0.2243 | -0.28381 | -0.036621 | 0.22888 | 60.6216 | 60.9695 | 122.2916 | 122.4701 | -0.054932 | 122.4792 | 60.8047 | -0.28381 | 122.4701 | -0.054932 | 60.8047 | 122.2916 | 122.4792 | -122.7997 | -122.7997
710.9688 | 122.8043 | -60.704 | 61.8576 | 0.088043 | 0.00088016 | 0.0060178 | -0.0016535 | 0.062961 | -0.0028561 | 0.067071 | -60.8276 | 61.7569 | -60.9924 | -60.8826 | 61.5646 | 0.027466 | -0.086975 | 0.15564 | 61.7935 | -60.9833 | -0.28839 | -0.10071 | -0.1236 | -0.17853 | -0.29297 | -0.27923 | -0.064087 | 0.16479 | 60.6171 | 60.8597 | 122.2687 | 122.4609 | -0.1236 | 122.4976 | 60.7315 | -0.27923 | 122.4609 | -0.1236 | 60.7315 | 122.2687 | 122.4976 | -122.85 | -122.8409
711.9062 | 122.818 | -60.6766 | 61.8942 | -0.20187 | -0.0010424 | 0.001318 | -0.0014399 | 0.060398 | -0.0028561 | 0.066858 | -60.759 | 61.7798 | -60.9512 | -60.8093 | 61.6058 | 0.14191 | 0.027466 | 0.27008 | 61.821 | -60.9512 | -0.27466 | -0.11444 | -0.082397 | -0.13275 | -0.28839 | -0.27466 | -0.073242 | 0.19226 | 60.704 | 60.9467 | 122.2824 | 122.4564 | -0.082397 | 122.4976 | 60.8185 | -0.27466 | 122.4564 | -0.082397 | 60.8185 | 122.2824 | 122.4976 | -122.8455 | -122.8455
712.9688 | 122.8043 | -60.7086 | 61.8484 | -0.0035098 | 0.0013074 | 0.0034544 | 0.0002691 | 0.063816 | -0.0011471 | 0.067712 | -60.8597 | 61.7981 | -60.9558 | -60.9055 | 61.5784 | 0.036621 | -0.10529 | 0.15106 | 61.8164 | -60.9558 | -0.24719 | -0.050354 | -0.15106 | -0.19684 | -0.27008 | -0.24719 | -0.032044 | 0.096131 | 60.6033 | 60.8597 | 122.287 | 122.5067 | -0.15106 | 122.525 | 60.7452 | -0.24719 | 122.5067 | -0.15106 | 60.7452 | 122.287 | 122.525 | -122.8043 | -122.8043
713.9062 | 122.8638 | -60.6674 | 61.8668 | -0.064545 | 0.0010938 | 0.0032406 | -0.0018671 | 0.060611 | -0.0022153 | 0.067926 | -60.759 | 61.7706 | -60.9558 | -60.8231 | 61.6241 | 0.10071 | -0.07782 | 0.24261 | 61.7935 | -60.9558 | -0.28839 | -0.09613 | -0.091553 | -0.15564 | -0.24261 | -0.28839 | -0.073242 | 0.19684 | 60.5896 | 60.91 | 122.2916 | 122.438 | -0.091553 | 122.4609 | 60.7681 | -0.28839 | 122.438 | -0.091553 | 60.7681 | 122.2916 | 122.4609 | -122.8226 | -122.8226
714.9688 | 122.7585 | -60.6903 | 61.9766 | -0.20187 | 0.0030164 | 0.0068722 | 0.0026191 | 0.062107 | -0.00029266 | 0.066858 | -60.8047 | 61.8713 | -60.9787 | -60.8963 | 61.5555 | 0.032043 | 0.10986 | 0.18768 | 61.8393 | -60.9741 | -0.28839 | -0.10529 | -0.11444 | -0.20599 | -0.42114 | -0.28381 | -0.13733 | 0.17395 | 60.8002 | 60.878 | 122.2458 | 122.5616 | -0.11444 | 122.5296 | 60.7224 | -0.28381 | 122.5616 | -0.11444 | 60.7224 | 122.2458 | 122.5296 | -122.9553 | -122.9507
715.9062 | 122.8546 | -60.6949 | 61.853 | 0.0041197 | 0.0038708 | 0.0038816 | -0.0007989 | 0.063388 | 0.00013454 | 0.068139 | -60.8093 | 61.7798 | -60.965 | -60.8688 | 61.5829 | 0.073242 | -0.07782 | 0.21973 | 61.8027 | -60.9375 | -0.27008 | -0.073242 | -0.11444 | -0.17395 | -0.27008 | -0.24262 | -0.050354 | 0.15564 | 60.6171 | 60.9146 | 122.2778 | 122.4747 | -0.11444 | 122.4976 | 60.7681 | -0.24262 | 122.4747 | -0.11444 | 60.7681 | 122.2778 | 122.4976 | -122.818 | -122.7905
716.9531 | 122.8409 | -60.6812 | 61.8347 | 0.18723 | 0.0019482 | 0.0062314 | 0.0036871 | 0.063388 | -0.0034971 | 0.068353 | -60.7773 | 61.7615 | -60.997 | -60.8368 | 61.5875 | 0.054932 | -0.19226 | 0.17395 | 61.7752 | -60.9421 | -0.31586 | -0.073242 | -0.096131 | -0.15564 | -0.24719 | -0.26093 | -0.059509 | 0.21973 | 60.4889 | 60.8551 | 122.2687 | 122.4426 | -0.096131 | 122.4564 | 60.7361 | -0.26093 | 122.4426 | -0.096131 | 60.7361 | 122.2687 | 122.4564 | -122.8317 | -122.7768
717.9062 | 122.85 | -60.6995 | 61.8622 | 0.11093 | -0.001256 | 0.0025998 | -0.0037897 | 0.062534 | 0.00098914 | 0.067712 | -60.8322 | 61.7981 | -60.9879 | -60.878 | 61.5692 | 0.050354 | -0.07782 | 0.17395 | 61.7752 | -60.9604 | -0.28839 | -0.064087 | -0.13275 | -0.17853 | -0.29297 | -0.26093 | -0.086975 | 0.15564 | 60.6216 | 60.8734 | 122.2687 | 122.4976 | -0.13275 | 122.4747 | 60.7498 | -0.26093 | 122.4976 | -0.13275 | 60.7498 | 122.2687 | 122.4747 | -122.85 | -122.8226
718.9688 | 122.7905 | -60.6995 | 61.8484 | 0.011749 | 0.001521 | 0.0028134 | -0.0025079 | 0.059543 | -0.00050626 | 0.067926 | -60.8139 | 61.7844 | -60.965 | -60.8826 | 61.5601 | 0.022888 | -0.10529 | 0.16937 | 61.7889 | -60.9512 | -0.2655 | -0.064087 | -0.11444 | -0.1831 | -0.28839 | -0.25177 | -0.05951 | 0.15106 | 60.5942 | 60.8688 | 122.2595 | 122.4838 | -0.11444 | 122.4884 | 60.7224 | -0.25177 | 122.4838 | -0.11444 | 60.7224 | 122.2595 | 122.4884 | -122.8134 | -122.7997
719.9062 | 122.8775 | -60.6583 | 61.8668 | -0.11032 | 0.002162 | 0.003668 | 0.0026191 | 0.065097 | -0.0011471 | 0.066858 | -60.7224 | 61.7981 | -60.9283 | -60.7681 | 61.6241 | 0.11902 | -0.073242 | 0.31128 | 61.7798 | -60.9421 | -0.27008 | -0.068664 | -0.064087 | -0.10986 | -0.24261 | -0.28381 | -0.086975 | 0.20599 | 60.585 | 60.9695 | 122.2824 | 122.4564 | -0.064087 | 122.438 | 60.7773 | -0.28381 | 122.4564 | -0.064087 | 60.7773 | 122.2824 | 122.438 | -122.7951 | -122.8088
720.9688 | 122.8409 | -60.6995 | 61.8484 | 0.19485 | 0.0028028 | 0.0070858 | 0.0006965 | 0.062534 | -0.0013609 | 0.067712 | -60.7544 | 61.7477 | -60.9879 | -60.8505 | 61.5921 | 0.054932 | -0.19226 | 0.17395 | 61.7615 | -60.9741 | -0.28839 | -0.10071 | -0.054932 | -0.15106 | -0.25635 | -0.27466 | -0.086975 | 0.23346 | 60.5072 | 60.8734 | 122.2916 | 122.4472 | -0.054932 | 122.4609 | 60.7544 | -0.27466 | 122.4472 | -0.054932 | 60.7544 | 122.2916 | 122.4609 | -122.8363 | -122.8226
721.9062 | 122.7997 | -60.6903 | 61.8301 | -0.87326 | 0.0034436 | 0.0072996 | -0.0025079 | 0.061252 | 0.00034814 | 0.068353 | -60.8826 | 61.8027 | -60.9512 | -60.9009 | 61.5417 | 0.032043 | -0.082397 | 0.16937 | 61.7844 | -60.9467 | -0.26093 | -0.027466 | -0.19226 | -0.21057 | -0.28839 | -0.25635 | -0.045776 | 0.068665 | 60.6079 | 60.8597 | 122.2321 | 122.493 | -0.19226 | 122.4747 | 60.7224 | -0.25635 | 122.493 | -0.19226 | 60.7224 | 122.2321 | 122.4747 | -122.7814 | -122.7768
722.9688 | 122.8455 | -60.6857 | 61.853 | 0.21011 | 0.0023756 | 0.0062314 | 0.0060369 | 0.062747 | 0.0024845 | 0.067071 | -60.8139 | 61.8027 | -61.0199 | -60.8734 | 61.5417 | 0 | -0.16479 | 0.1236 | 61.7706 | -60.965 | -0.33417 | -0.050354 | -0.12817 | -0.18768 | -0.31128 | -0.27924 | -0.082397 | 0.20599 | 60.5209 | 60.8093 | 122.2275 | 122.4884 | -0.12817 | 122.4564 | 60.6857 | -0.27924 | 122.4884 | -0.12817 | 60.6857 | 122.2275 | 122.4564 | -122.8729 | -122.818
723.9062 | 122.8134 | -60.6766 | 61.8576 | 0.088043 | 0.0013074 | 0.004736 | -0.0014399 | 0.061893 | 0.00013454 | 0.065576 | -60.8139 | 61.7661 | -60.9787 | -60.8826 | 61.5463 | 0.032043 | -0.082397 | 0.15106 | 61.7935 | -60.965 | -0.30212 | -0.091553 | -0.13733 | -0.20599 | -0.31128 | -0.28839 | -0.064087 | 0.16479 | 60.5942 | 60.8276 | 122.2229 | 122.4426 | -0.13733 | 122.4701 | 60.7086 | -0.28839 | 122.4426 | -0.13733 | 60.7086 | 122.2229 | 122.4701 | -122.8363 | -122.8226
724.9688 | 122.7631 | -60.6949 | 61.8896 | -0.17899 | 0.00066656 | 0.005377 | 0.0017645 | 0.061252 | -0.0011471 | 0.065362 | -60.7452 | 61.8256 | -60.9604 | -60.8231 | 61.6058 | 0.11444 | 0.045776 | 0.27924 | 61.8256 | -60.9192 | -0.2655 | -0.064086 | -0.050354 | -0.12817 | -0.28381 | -0.2243 | -0.064086 | 0.21515 | 60.7407 | 60.9741 | 122.3007 | 122.5204 | -0.050354 | 122.5204 | 60.8093 | -0.2243 | 122.5204 | -0.050354 | 60.8093 | 122.3007 | 122.5204 | -122.85 | -122.8088
725.9062 | 122.818 | -60.6766 | 61.8713 | 0.034637 | 0.00088016 | 0.001959 | -0.0027215 | 0.06232 | -0.0013609 | 0.067926 | -60.8185 | 61.7615 | -60.9833 | -60.878 | 61.5417 | 0.10071 | -0.004578 | 0.15106 | 61.8256 | -60.9192 | -0.3067 | -0.10986 | -0.14191 | -0.20142 | -0.32959 | -0.24261 | -0.045776 | 0.16479 | 60.672 | 60.8276 | 122.2183 | 122.4381 | -0.14191 | 122.5021 | 60.7773 | -0.24261 | 122.4381 | -0.14191 | 60.7773 | 122.2183 | 122.5021 | -122.8546 | -122.7905
726.9688 | 122.8592 | -60.6766 | 61.8484 | 0.18723 | 0.00066656 | 0.0066586 | 0.0024053 | 0.062961 | -7.9062e-05 | 0.068139 | -60.7361 | 61.7661 | -60.9787 | -60.8505 | 61.5784 | 0.050354 | -0.20599 | 0.18768 | 61.7661 | -60.965 | -0.30212 | -0.082398 | -0.059509 | -0.17395 | -0.27008 | -0.28839 | -0.082398 | 0.24262 | 60.4706 | 60.8643 | 122.2549 | 122.4426 | -0.059509 | 122.4426 | 60.7269 | -0.28839 | 122.4426 | -0.059509 | 60.7269 | 122.2549 | 122.4426 | -122.8271 | -122.8134
727.9062 | 122.818 | -60.7086 | 61.853 | 0.080414 | 0.0034436 | 0.0049496 | -0.0016535 | 0.063175 | -0.00071986 | 0.067926 | -60.8047 | 61.7569 | -61.0153 | -60.8963 | 61.5143 | 0.022888 | -0.10071 | 0.15106 | 61.7844 | -60.9741 | -0.3067 | -0.09613 | -0.096131 | -0.18768 | -0.33874 | -0.2655 | -0.068664 | 0.21057 | 60.6079 | 60.8597 | 122.2229 | 122.4655 | -0.096131 | 122.493 | 60.7315 | -0.2655 | 122.4655 | -0.096131 | 60.7315 | 122.2229 | 122.493 | -122.8683 | -122.8271
728.9688 | 122.7448 | -60.7269 | 61.8576 | 0.24063 | 0.0047254 | 0.0087948 | 0.0039007 | 0.063388 | -0.0041379 | 0.067071 | -60.8276 | 61.8301 | -61.0016 | -60.9283 | 61.4914 | -0.050354 | -0.018311 | 0.059509 | 61.821 | -60.997 | -0.27466 | -0.027466 | -0.10071 | -0.20142 | -0.36621 | -0.27008 | -0.036621 | 0.17395 | 60.7086 | 60.7864 | 122.2183 | 122.5571 | -0.10071 | 122.5479 | 60.6766 | -0.27008 | 122.5571 | -0.10071 | 60.6766 | 122.2183 | 122.5479 | -122.8592 | -122.8546
729.9062 | 122.8088 | -60.6766 | 61.8347 | 0.019379 | 0.0042982 | 0.0034544 | -0.0007989 | 0.06232 | -0.0022153 | 0.067285 | -60.8185 | 61.7752 | -60.9787 | -60.8917 | 61.5555 | 0.027466 | -0.10529 | 0.16022 | 61.7935 | -60.9604 | -0.30212 | -0.059509 | -0.14191 | -0.21515 | -0.27924 | -0.28381 | -0.041199 | 0.16022 | 60.5713 | 60.8368 | 122.2321 | 122.4518 | -0.14191 | 122.4701 | 60.704 | -0.28381 | 122.4518 | -0.14191 | 60.704 | 122.2321 | 122.4701 | -122.8134 | -122.7951
730.9531 | 122.8271 | -60.7132 | 61.8668 | 0.11856 | 0.00323 | 0.0077268 | -0.0014399 | 0.061679 | -0.0011471 | 0.067498 | -60.8139 | 61.7889 | -60.9833 | -60.878 | 61.5601 | 0.018311 | -0.10986 | 0.16022 | 61.7935 | -60.9604 | -0.27008 | -0.07782 | -0.10071 | -0.16479 | -0.3067 | -0.24719 | -0.073242 | 0.16937 | 60.6033 | 60.8734 | 122.2733 | 122.5021 | -0.10071 | 122.5067 | 60.7315 | -0.24719 | 122.5021 | -0.10071 | 60.7315 | 122.2733 | 122.5067 | -122.85 | -122.8271
731.9062 | 122.85 | -60.704 | 61.8347 | 0.20248 | 0.0017346 | 0.005377 | 0.0017645 | 0.06232 | -0.0047787 | 0.067712 | -60.759 | 61.7569 | -60.9604 | -60.8368 | 61.5967 | 0.041199 | -0.19226 | 0.19226 | 61.7432 | -60.9604 | -0.25635 | -0.07782 | -0.054931 | -0.13275 | -0.23804 | -0.25635 | -0.091553 | 0.20142 | 60.5118 | 60.8963 | 122.3007 | 122.4609 | -0.054931 | 122.4472 | 60.7452 | -0.25635 | 122.4609 | -0.054931 | 60.7452 | 122.3007 | 122.4472 | -122.7951 | -122.7951
732.9688 | 122.7402 | -60.704 | 61.8668 | 0.24826 | 0.0051526 | 0.0072996 | 0.0062507 | 0.064029 | -0.0024289 | 0.065789 | -60.8322 | 61.8393 | -61.0291 | -60.9375 | 61.4822 | -0.050354 | -0.022888 | 0.041199 | 61.8073 | -61.0382 | -0.32501 | -0.027466 | -0.12817 | -0.23346 | -0.38452 | -0.33417 | -0.059509 | 0.19684 | 60.6812 | 60.7452 | 122.1863 | 122.5433 | -0.12817 | 122.5113 | 60.6537 | -0.33417 | 122.5433 | -0.12817 | 60.6537 | 122.1863 | 122.5113 | -122.8958 | -122.905
733.9062 | 122.8134 | -60.6857 | 61.8576 | 0.027008 | 0.0047254 | 0.0066586 | -0.0007989 | 0.064029 | 0.00034814 | 0.067498 | -60.8139 | 61.8073 | -60.9787 | -60.8871 | 61.5601 | 0.022888 | -0.10529 | 0.16022 | 61.7935 | -60.9741 | -0.29297 | -0.050354 | -0.12817 | -0.20142 | -0.29755 | -0.28839 | -0.064087 | 0.16479 | 60.5804 | 60.8459 | 122.2458 | 122.493 | -0.12817 | 122.4792 | 60.7086 | -0.28839 | 122.493 | -0.12817 | 60.7086 | 122.2458 | 122.4792 | -122.8363 | -122.8317
734.9688 | 122.8638 | -60.672 | 61.8164 | 0.20248 | 0.0036572 | 0.003668 | 0.0036871 | 0.061893 | -0.0032835 | 0.068139 | -60.9146 | 61.7294 | -60.9833 | -60.8185 | 61.5875 | 0.059509 | -0.19226 | 0.16937 | 61.7523 | -60.9695 | -0.31128 | -0.086975 | -0.24262 | -0.14648 | -0.22888 | -0.29755 | -0.064087 | 0.068664 | 60.4797 | 60.8414 | 122.2595 | 122.4014 | -0.24262 | 122.4243 | 60.7315 | -0.29755 | 122.4014 | -0.24262 | 60.7315 | 122.2595 | 122.4243 | -122.7997 | -122.7859
735.9062 | 122.8455 | -60.672 | 61.8347 | 0.15671 | 0.0036572 | 0.004736 | 0.0009101 | 0.064456 | -0.0024289 | 0.067285 | -60.7544 | 61.7706 | -60.965 | -60.8505 | 61.5921 | 0.045776 | -0.18768 | 0.16937 | 61.7706 | -60.965 | -0.29297 | -0.064087 | -0.082398 | -0.17853 | -0.24262 | -0.29297 | -0.064087 | 0.21057 | 60.4843 | 60.8414 | 122.2641 | 122.4426 | -0.082398 | 122.4426 | 60.7178 | -0.29297 | 122.4426 | -0.082398 | 60.7178 | 122.2641 | 122.4426 | -122.7997 | -122.7997
736.9531 | 122.7448 | -60.7269 | 61.8713 | 0.13382 | 0.0068616 | 0.006445 | 0.0073187 | 0.062534 | -0.0011471 | 0.076471 | -60.8551 | 61.8805 | -60.997 | -61.2076 | 61.203 | -0.13275 | 0.27466 | 0.10071 | 61.8576 | -61.0016 | -0.27008 | 0.009155 | -0.12817 | -0.48065 | -0.66833 | -0.27466 | -0.013733 | 0.14191 | 61.0016 | 60.8276 | 121.9299 | 122.6074 | -0.12817 | 122.5845 | 60.5942 | -0.27466 | 122.6074 | -0.12817 | 60.5942 | 121.9299 | 122.5845 | -122.8683 | -122.8729
737.9062 | 122.7951 | -60.704 | 61.8301 | 0.24063 | 0.0055798 | 0.0077268 | 0.0036871 | 0.066593 | -0.0013609 | 0.068353 | -60.8047 | 61.8439 | -61.0107 | -60.8871 | 61.5326 | -0.004578 | -0.11902 | 0.09613 | 61.8118 | -60.9879 | -0.3067 | 0.013733 | -0.10071 | -0.18311 | -0.29755 | -0.28381 | -0.01831 | 0.20599 | 60.585 | 60.8002 | 122.2366 | 122.5479 | -0.10071 | 122.5159 | 60.6995 | -0.28381 | 122.5479 | -0.10071 | 60.6995 | 122.2366 | 122.5159 | -122.8409 | -122.818
738.9688 | 122.7722 | -60.6903 | 61.8805 | 0.439 | 0.0036572 | 0.0040952 | 0.0043281 | 0.064243 | -0.0039243 | 0.067285 | -60.704 | 61.853 | -60.9879 | -60.8597 | 61.5692 | 0.082397 | 0.022888 | 0.19226 | 61.8439 | -60.9741 | -0.29755 | -0.027466 | -0.013733 | -0.16937 | -0.31128 | -0.28381 | -0.036621 | 0.28381 | 60.7132 | 60.8826 | 122.2595 | 122.5433 | -0.013733 | 122.5342 | 60.7727 | -0.28381 | 122.5433 | -0.013733 | 60.7727 | 122.2595 | 122.5342 | -122.8683 | -122.8546
739.9062 | 122.7997 | -60.6903 | 61.8256 | 0.072784 | 0.0010938 | 0.003027 | -0.0040033 | 0.065738 | -0.0013609 | 0.067712 | -60.6949 | 61.8301 | -60.965 | -60.8734 | 61.5601 | 0.036621 | -0.054932 | 0.16022 | 61.8073 | -60.9512 | -0.27466 | 0.004577 | -0.004577 | -0.1831 | -0.2655 | -0.26093 | -0.018311 | 0.27008 | 60.6354 | 60.8505 | 122.2504 | 122.5204 | -0.004577 | 122.4976 | 60.7269 | -0.26093 | 122.5204 | -0.004577 | 60.7269 | 122.2504 | 122.4976 | -122.7905 | -122.7768
740.9531 | 122.7448 | -60.7315 | 61.8713 | 3.5213 | 0.0062208 | 0.010717 | 0.0066779 | 0.063816 | -0.0030697 | 0.068353 | -60.7452 | 61.8256 | -61.0107 | -60.9421 | 61.496 | -0.032043 | -0.009155 | 0.027466 | 61.8347 | -61.0107 | -0.27924 | -0.045776 | -0.013733 | -0.21057 | -0.37537 | -0.27924 | -0.036621 | 0.2655 | 60.7224 | 60.759 | 122.2275 | 122.5571 | -0.013733 | 122.5662 | 60.6995 | -0.27924 | 122.5571 | -0.013733 | 60.6995 | 122.2275 | 122.5662 | -122.8821 | -122.8821
741.9062 | 122.8729 | -60.6857 | 61.8256 | 0.17197 | 0.0042982 | 0.0092222 | 0.0009101 | 0.065738 | -0.00029266 | 0.068994 | -60.7269 | 61.8027 | -60.9741 | -60.9833 | 61.6425 | 0.13733 | -0.10986 | 0.14648 | 61.7798 | -60.9924 | -0.28839 | -0.022889 | -0.041199 | -0.29755 | -0.18311 | -0.3067 | -0.045777 | 0.24719 | 60.5759 | 60.8322 | 122.3282 | 122.4884 | -0.041199 | 122.4655 | 60.8231 | -0.3067 | 122.4884 | -0.041199 | 60.8231 | 122.3282 | 122.4655 | -122.7997 | -122.818
742.9531 | 122.7951 | -60.7086 | 61.8484 | 0.16434 | 0.0051526 | 0.0077268 | 0.0036871 | 0.065097 | -0.00050626 | 0.067712 | -60.8276 | 61.8622 | -61.0153 | -60.9283 | 61.5051 | -0.032043 | -0.082397 | 0.064087 | 61.8118 | -61.0199 | -0.3067 | 0.013733 | -0.11902 | -0.21973 | -0.34332 | -0.31128 | -0.036621 | 0.18768 | 60.6262 | 60.7727 | 122.2137 | 122.5708 | -0.11902 | 122.5204 | 60.6766 | -0.31128 | 122.5708 | -0.11902 | 60.6766 | 122.2137 | 122.5204 | -122.8638 | -122.8683
743.9062 | 122.7448 | -60.704 | 61.8439 | 0.22537 | 0.0057934 | 0.0060178 | 0.0068915 | 0.066165 | -0.00093346 | 0.070062 | -60.8231 | 61.8759 | -61.0199 | -60.9512 | 61.496 | -0.045776 | -0.032043 | 0.050354 | 61.8393 | -61.0291 | -0.31586 | 0.032044 | -0.11902 | -0.24719 | -0.3479 | -0.32501 | -0.004578 | 0.19684 | 60.672 | 60.7544 | 122.2 | 122.58 | -0.11902 | 122.5433 | 60.6583 | -0.32501 | 122.58 | -0.11902 | 60.6583 | 122.2 | 122.5433 | -122.8638 | -122.8729
744.9688 | 122.7493 | -60.6949 | 61.8805 | 0.011749 | 0.0064344 | 0.0077268 | 0.0047553 | 0.065952 | -0.0043515 | 0.068994 | -60.791 | 61.8713 | -60.9924 | -60.9009 | 61.5189 | 0.013733 | 0.022888 | 0.11444 | 61.8484 | -61.0153 | -0.29755 | -0.009155 | -0.096131 | -0.20599 | -0.36163 | -0.32044 | -0.032043 | 0.20142 | 60.7178 | 60.8093 | 122.2137 | 122.5662 | -0.096131 | 122.5433 | 60.7086 | -0.32044 | 122.5662 | -0.096131 | 60.7086 | 122.2137 | 122.5433 | -122.8729 | -122.8958
745.9062 | 122.7127 | -60.7315 | 61.8759 | 0.12619 | 0.0060072 | 0.0083676 | 0.0053961 | 0.067661 | -0.0017881 | 0.067498 | -60.8185 | 61.8988 | -60.9787 | -60.965 | 61.4777 | -0.045776 | 0.022888 | 0.041199 | 61.8301 | -61.0428 | -0.24719 | 0.022888 | -0.086975 | -0.23346 | -0.39825 | -0.31128 | -0.045777 | 0.16022 | 60.7544 | 60.7727 | 122.2092 | 122.6303 | -0.086975 | 122.5616 | 60.6857 | -0.31128 | 122.6303 | -0.086975 | 60.6857 | 122.2092 | 122.5616 | -122.8546 | -122.9187
746.9688 | 122.7722 | -60.6949 | 61.8896 | -0.2095 | 0.0064344 | 0.0043088 | 0.0028327 | 0.068088 | -0.00071986 | 0.067712 | -60.7864 | 61.9308 | -60.9924 | -60.8871 | 61.5646 | 0.086975 | 0.068665 | 0.21515 | 61.8759 | -61.0153 | -0.29755 | 0.041199 | -0.091553 | -0.19226 | -0.32501 | -0.32044 | -0.013732 | 0.20599 | 60.7636 | 60.91 | 122.2595 | 122.6257 | -0.091553 | 122.5708 | 60.7819 | -0.32044 | 122.6257 | -0.091553 | 60.7819 | 122.2595 | 122.5708 | -122.8821 | -122.905
747.9062 | 122.7402 | -60.7132 | 61.8713 | 0.049896 | 0.0055798 | 0.0070858 | 0.0024053 | 0.068515 | -0.0017881 | 0.068567 | -60.8002 | 61.9125 | -61.0016 | -60.9558 | 61.4914 | -0.032043 | 0.032043 | 0.068665 | 61.8713 | -61.0291 | -0.28839 | 0.041199 | -0.086975 | -0.24261 | -0.37994 | -0.31586 | 0 | 0.20142 | 60.7452 | 60.7819 | 122.2046 | 122.6257 | -0.086975 | 122.5845 | 60.6812 | -0.31586 | 122.6257 | -0.086975 | 60.6812 | 122.2046 | 122.5845 | -122.8729 | -122.9004
748.9531 | 122.7631 | -60.7086 | 61.8668 | 0.034637 | 0.0051526 | 0.012426 | 0.0045417 | 0.067447 | -0.0024289 | 0.068139 | -60.7269 | 61.9125 | -60.9924 | -60.8963 | 61.5417 | 0.059509 | 0.013733 | 0.17395 | 61.853 | -61.0199 | -0.28381 | 0.045777 | -0.018311 | -0.18768 | -0.32501 | -0.31128 | -0.013733 | 0.2655 | 60.7224 | 60.8826 | 122.2504 | 122.6212 | -0.018311 | 122.5616 | 60.7681 | -0.31128 | 122.6212 | -0.018311 | 60.7681 | 122.2504 | 122.5616 | -122.8592 | -122.8867
749.9062 | 122.7585 | -60.704 | 61.8713 | -0.011139 | 0.006648 | 0.0055906 | 0.0049689 | 0.06702 | -0.0017881 | 0.070062 | -60.759 | 61.9263 | -60.997 | -60.8963 | 61.5234 | 0.045776 | 0.041199 | 0.14191 | 61.8713 | -61.0382 | -0.29297 | 0.054932 | -0.054931 | -0.19226 | -0.3479 | -0.33417 | 0 | 0.23804 | 60.7452 | 60.8459 | 122.2275 | 122.6303 | -0.054931 | 122.5754 | 60.7498 | -0.33417 | 122.6303 | -0.054931 | 60.7498 | 122.2275 | 122.5754 | -122.8683 | -122.9095
750.9688 | 122.8546 | -60.672 | 61.8576 | -0.16373 | 0.0010938 | 0.005377 | -0.0057123 | 0.06467 | -0.00050626 | 0.067071 | -60.4523 | 61.9354 | -60.9009 | -60.8459 | 61.6333 | 0.16937 | -0.068665 | 0.3067 | 61.853 | -60.9695 | -0.22888 | 0.07782 | 0.21973 | -0.17395 | -0.2243 | -0.29755 | -0.004578 | 0.44861 | 60.6033 | 60.9787 | 122.3053 | 122.6074 | 0.21973 | 122.525 | 60.8414 | -0.29755 | 122.6074 | 0.21973 | 60.8414 | 122.3053 | 122.525 | -122.7585 | -122.8271
751.9062 | 122.7768 | -60.6949 | 61.8896 | -0.14847 | 0.0057934 | 0.0058042 | 0.0030463 | 0.064243 | -0.00029266 | 0.068353 | -60.7773 | 61.9446 | -60.9879 | -60.878 | 61.5692 | 0.064087 | 0.10986 | 0.20599 | 61.8668 | -61.0245 | -0.29297 | 0.054932 | -0.082398 | -0.18311 | -0.32043 | -0.32959 | -0.022888 | 0.21057 | 60.8047 | 60.9009 | 122.2641 | 122.6395 | -0.082398 | 122.5616 | 60.759 | -0.32959 | 122.6395 | -0.082398 | 60.759 | 122.2641 | 122.5616 | -122.8775 | -122.9141
752.9688 | 122.7631 | -60.7224 | 61.8851 | -0.45364 | 0.0040846 | 0.0077268 | -0.0001581 | 0.064884 | -0.00050626 | 0.069635 | -60.791 | 61.9171 | -60.9741 | -60.9192 | 61.528 | 0.050354 | 0.14191 | 0.19226 | 61.9034 | -61.0153 | -0.25177 | 0.032043 | -0.068665 | -0.19684 | -0.35706 | -0.29297 | 0.01831 | 0.1831 | 60.8643 | 60.9146 | 122.2504 | 122.6395 | -0.068665 | 122.6257 | 60.7727 | -0.29297 | 122.6395 | -0.068665 | 60.7727 | 122.2504 | 122.6257 | -122.8592 | -122.9004
753.9062 | 122.7631 | -60.7269 | 61.8942 | -0.026398 | 0.0045118 | 0.0083676 | 0.0043281 | 0.067234 | -0.0013609 | 0.069207 | -60.7452 | 61.8713 | -60.9833 | -60.9009 | 61.5326 | 0.045776 | 0.018311 | 0.16022 | 61.8805 | -61.0153 | -0.25635 | -0.022888 | -0.01831 | -0.17395 | -0.36163 | -0.28839 | -0.013733 | 0.23804 | 60.7452 | 60.8871 | 122.2595 | 122.5983 | -0.01831 | 122.6074 | 60.7727 | -0.28839 | 122.5983 | -0.01831 | 60.7727 | 122.2595 | 122.6074 | -122.8775 | -122.9095
754.9688 | 122.8683 | -60.6445 | 61.8759 | -0.17136 | 0.00023916 | 0.0083676 | -0.0061395 | 0.066806 | 0.00077554 | 0.06643 | -60.4523 | 61.8988 | -60.9512 | -60.8322 | 61.6562 | 0.16022 | -0.064087 | 0.32044 | 61.8256 | -60.9604 | -0.3067 | 0.022888 | 0.19226 | -0.18768 | -0.21973 | -0.31586 | -0.050354 | 0.49896 | 60.5804 | 60.965 | 122.3007 | 122.5433 | 0.19226 | 122.4701 | 60.8047 | -0.31586 | 122.5433 | 0.19226 | 60.8047 | 122.3007 | 122.4701 | -122.8271 | -122.8363
755.9219 | 122.8317 | -60.6628 | 61.8256 | 0.25589 | 0.0047254 | 0.008154 | 0.0011237 | 0.06702 | 0.00013454 | 0.069635 | -60.7681 | 61.8073 | -61.0062 | -60.8871 | 61.5555 | 0.041199 | -0.15106 | 0.14648 | 61.8347 | -60.997 | -0.34332 | -0.018311 | -0.10529 | -0.2243 | -0.27008 | -0.33417 | 0.009155 | 0.23804 | 60.5118 | 60.8093 | 122.2183 | 122.4701 | -0.10529 | 122.4976 | 60.704 | -0.33417 | 122.4701 | -0.10529 | 60.704 | 122.2183 | 122.4976 | -122.8317 | -122.8226
756.9531 | 122.8729 | -60.6903 | 61.8439 | 0.095673 | 0.0034436 | 0.0051632 | -0.0052851 | 0.065311 | -0.00093346 | 0.068994 | -60.791 | 61.8256 | -60.9787 | -60.8871 | 61.5463 | 0.032043 | -0.07782 | 0.17395 | 61.8164 | -60.9787 | -0.28839 | -0.01831 | -0.10071 | -0.19684 | -0.29755 | -0.28839 | -0.027466 | 0.18768 | 60.6125 | 60.8643 | 122.2366 | 122.5159 | -0.10071 | 122.5067 | 60.7224 | -0.28839 | 122.5159 | -0.10071 | 60.7224 | 122.2366 | 122.5067 | -122.8226 | -122.8226
757.9062 | 122.7997 | -60.7086 | 61.9034 | -0.18662 | 0.0062208 | 0.0062314 | 0.0045417 | 0.064029 | -0.0039243 | 0.066644 | -60.7819 | 61.8942 | -60.9924 | -60.8643 | 61.5555 | 0.082397 | 0.073242 | 0.2243 | 61.8805 | -61.0153 | -0.28381 | -0.009155 | -0.073242 | -0.15564 | -0.3479 | -0.3067 | -0.022888 | 0.21057 | 60.7819 | 60.9329 | 122.2641 | 122.6028 | -0.073242 | 122.5891 | 60.791 | -0.3067 | 122.6028 | -0.073242 | 60.791 | 122.2641 | 122.5891 | -122.8958 | -122.9187
758.9688 | 122.7951 | -60.6949 | 61.8805 | -0.22476 | 0.0028028 | 0.0060178 | -0.0027215 | 0.064456 | -0.0017881 | 0.06878 | -60.7407 | 61.853 | -60.9283 | -60.8505 | 61.5921 | 0.11444 | 0.041199 | 0.28839 | 61.8713 | -60.9741 | -0.23346 | -0.027466 | -0.045777 | -0.15564 | -0.28839 | -0.27924 | -0.009155 | 0.18768 | 60.7361 | 60.9833 | 122.287 | 122.5479 | -0.045777 | 122.5662 | 60.8093 | -0.27924 | 122.5479 | -0.045777 | 60.8093 | 122.287 | 122.5662 | -122.8088 | -122.8546
759.9062 | 122.7951 | -60.7224 | 61.9034 | -0.13321 | 0.0047254 | 0.006445 | 0.0041143 | 0.066379 | -0.0026425 | 0.067285 | -60.7498 | 61.9125 | -61.0016 | -60.8871 | 61.5463 | 0.073242 | 0.004578 | 0.21057 | 61.8713 | -61.0062 | -0.27924 | 0.009156 | -0.027466 | -0.16479 | -0.35706 | -0.28381 | -0.032043 | 0.25177 | 60.7269 | 60.9329 | 122.2687 | 122.6349 | -0.027466 | 122.5937 | 60.7956 | -0.28381 | 122.6349 | -0.027466 | 60.7956 | 122.2687 | 122.5937 | -122.905 | -122.9095
760.9688 | 122.7356 | -60.7452 | 61.8668 | 0.13382 | 0.0077162 | 0.0072996 | 0.0034735 | 0.066806 | -0.0024289 | 0.068353 | -60.8368 | 61.853 | -60.997 | -60.9512 | 61.4639 | -0.045776 | -0.022888 | 0.064087 | 61.8576 | -61.0107 | -0.25177 | -0.013733 | -0.091553 | -0.20599 | -0.40283 | -0.2655 | -0.009155 | 0.16022 | 60.7224 | 60.8093 | 122.2092 | 122.5983 | -0.091553 | 122.6028 | 60.6995 | -0.2655 | 122.5983 | -0.091553 | 60.6995 | 122.2092 | 122.6028 | -122.8638 | -122.8775
761.9062 | 122.7631 | -60.704 | 61.8942 | -0.18662 | 0.0019482 | 0.0075132 | 5.5496e-05 | 0.066806 | -0.0017881 | 0.067712 | -60.8139 | 61.8988 | -61.0107 | -60.9009 | 61.528 | 0.054932 | 0.1236 | 0.19226 | 61.9217 | -60.9924 | -0.3067 | 0.004578 | -0.10986 | -0.19684 | -0.36621 | -0.28839 | 0.027466 | 0.19684 | 60.8276 | 60.8963 | 122.2321 | 122.6028 | -0.10986 | 122.6257 | 60.759 | -0.28839 | 122.6028 | -0.10986 | 60.759 | 122.2321 | 122.6257 | -122.905 | -122.8867
762.9688 | 122.8729 | -60.7132 | 61.8484 | -0.072174 | 0.001521 | 0.00089078 | -0.0048577 | 0.064029 | -0.0015745 | 0.066858 | -60.7727 | 61.7889 | -60.9512 | -60.8643 | 61.5967 | 0.09613 | -0.07782 | 0.24719 | 61.8393 | -60.9695 | -0.23804 | -0.05951 | -0.059509 | -0.15106 | -0.25177 | -0.25635 | -0.009156 | 0.17853 | 60.6354 | 60.9604 | 122.3099 | 122.5021 | -0.059509 | 122.5525 | 60.8093 | -0.25635 | 122.5021 | -0.059509 | 60.8093 | 122.3099 | 122.5525 | -122.7997 | -122.818
763.9062 | 122.731 | -60.6903 | 61.9171 | -0.21713 | 0.0034436 | 0.0040952 | -0.0005853 | 0.063175 | -0.0024289 | 0.06878 | -60.7956 | 61.8484 | -60.9604 | -60.8963 | 61.5326 | 0.073242 | 0.12817 | 0.23346 | 61.8668 | -60.9924 | -0.27008 | -0.068664 | -0.10528 | -0.20599 | -0.38452 | -0.30212 | -0.050354 | 0.1648 | 60.8185 | 60.9238 | 122.2229 | 122.5388 | -0.10528 | 122.5571 | 60.7636 | -0.30212 | 122.5388 | -0.10528 | 60.7636 | 122.2229 | 122.5571 | -122.8775 | -122.9095
764.9531 | 122.7402 | -60.7132 | 61.9354 | -0.19424 | 0.0053662 | 0.0051632 | 0.0032599 | 0.063175 | -0.0039243 | 0.069421 | -60.8139 | 61.9171 | -60.965 | -60.9146 | 61.5234 | 0.041199 | 0.11902 | 0.17853 | 61.8942 | -61.0062 | -0.25177 | -0.018311 | -0.10071 | -0.20142 | -0.41199 | -0.29297 | -0.041199 | 0.15106 | 60.8322 | 60.8917 | 122.2366 | 122.6303 | -0.10071 | 122.6074 | 60.7544 | -0.29297 | 122.6303 | -0.10071 | 60.7544 | 122.2366 | 122.6074 | -122.9004 | -122.9416
765.9219 | 122.7631 | -60.7636 | 61.8713 | 0.15671 | 0.0038708 | 0.0058042 | 0.0045417 | 0.065738 | -0.00050626 | 0.066858 | -60.8276 | 61.8484 | -61.0062 | -60.9604 | 61.4822 | -0.059509 | -0.022888 | 0.054932 | 61.8759 | -61.0291 | -0.24262 | -0.022888 | -0.064087 | -0.19684 | -0.3891 | -0.2655 | 0.004578 | 0.17853 | 60.7407 | 60.8185 | 122.2458 | 122.612 | -0.064087 | 122.6395 | 60.704 | -0.2655 | 122.612 | -0.064087 | 60.704 | 122.2458 | 122.6395 | -122.8775 | -122.9004
766.9688 | 122.818 | -60.704 | 61.8301 | -0.0035098 | 0.0045118 | 0.0077268 | -0.0016535 | 0.064243 | -0.0015745 | 0.066003 | -60.8093 | 61.7752 | -60.9787 | -60.8871 | 61.5829 | 0.059509 | -0.086975 | 0.21515 | 61.8393 | -60.965 | -0.27466 | -0.054931 | -0.10529 | -0.18311 | -0.24719 | -0.26093 | 0.009155 | 0.16937 | 60.6171 | 60.9192 | 122.287 | 122.4792 | -0.10529 | 122.5433 | 60.7635 | -0.26093 | 122.4792 | -0.10529 | 60.7635 | 122.287 | 122.5433 | -122.8088 | -122.7951
767.9062 | 122.7539 | -60.7315 | 61.908 | -0.1561 | 0.0036572 | 0.0060178 | 0.0032599 | 0.064884 | 0.00077554 | 0.068567 | -60.7956 | 61.8622 | -60.997 | -60.9009 | 61.5189 | 0.041199 | 0.14191 | 0.18768 | 61.8851 | -60.9879 | -0.2655 | -0.045776 | -0.064087 | -0.16937 | -0.3891 | -0.25635 | -0.022888 | 0.20142 | 60.8734 | 60.9192 | 122.2504 | 122.5937 | -0.064087 | 122.6166 | 60.7727 | -0.25635 | 122.5937 | -0.064087 | 60.7727 | 122.2504 | 122.6166 | -122.905 | -122.8958
768.9688 | 122.8226 | -60.704 | 61.8301 | 0.24826 | 0.0038708 | 0.0025998 | 0.0019781 | 0.06467 | 0.00034814 | 0.068994 | -60.8047 | 61.8073 | -61.0199 | -60.8917 | 61.5326 | -0.009155 | -0.13275 | 0.10529 | 61.853 | -60.9879 | -0.31586 | -0.022888 | -0.10071 | -0.18768 | -0.29755 | -0.28381 | 0.022888 | 0.21515 | 60.5713 | 60.8093 | 122.2366 | 122.5113 | -0.10071 | 122.5571 | 60.6949 | -0.28381 | 122.5113 | -0.10071 | 60.6949 | 122.2366 | 122.5571 | -122.85 | -122.818
769.9219 | 122.731 | -60.6949 | 61.8896 | 0.027008 | 0.0072888 | 0.0085812 | 0.0058233 | 0.067661 | -7.9062e-05 | 0.064721 | -60.7452 | 61.8759 | -60.9604 | -60.9055 | 61.5189 | 0 | 0.009155 | 0.1236 | 61.8484 | -61.0291 | -0.2655 | -0.013732 | -0.050354 | -0.21057 | -0.37079 | -0.33417 | -0.041198 | 0.21515 | 60.704 | 60.8185 | 122.2137 | 122.5708 | -0.050354 | 122.5433 | 60.6949 | -0.33417 | 122.5708 | -0.050354 | 60.6949 | 122.2137 | 122.5433 | -122.85 | -122.9187
770.9688 | 122.6669 | -60.7086 | 61.8439 | -0.11795 | 0.0079298 | 0.006445 | 0.0049689 | 0.066379 | -0.0032835 | 0.067071 | -60.7498 | 61.8668 | -60.9741 | -60.8688 | 61.5555 | 0.073242 | 0.018311 | 0.20142 | 61.8713 | -61.0291 | -0.2655 | 0.022888 | -0.041199 | -0.16022 | -0.28839 | -0.32043 | 0.027466 | 0.2243 | 60.7269 | 60.91 | 122.2641 | 122.5754 | -0.041199 | 122.58 | 60.7819 | -0.32043 | 122.5754 | -0.041199 | 60.7819 | 122.2641 | 122.58 | -122.818 | -122.8729
771.9062 | 122.8317 | -60.6903 | 61.8301 | -0.1561 | 0.001521 | 0.0045224 | -0.0065667 | 0.060398 | -0.0026425 | 0.069421 | -60.7269 | 61.8027 | -60.9787 | -60.8276 | 61.3403 | -0.086975 | 0.004578 | 0.32044 | 61.8164 | -60.9283 | -0.28839 | -0.027466 | -0.036621 | -0.13733 | -0.48981 | -0.23804 | -0.013733 | 0.25177 | 60.6949 | 61.0107 | 122.0306 | 122.493 | -0.036621 | 122.5067 | 60.6033 | -0.23804 | 122.493 | -0.036621 | 60.6033 | 122.0306 | 122.5067 | -122.8088 | -122.7585
772.9531 | 122.818 | -60.704 | 61.8393 | 0.034637 | 0.0030164 | 0.0049496 | -0.0061395 | 0.062961 | -0.00071986 | 0.068353 | -60.8185 | 61.7889 | -60.9924 | -60.8871 | 61.5784 | 0.054932 | -0.073242 | 0.18768 | 61.8347 | -60.9558 | -0.28839 | -0.050354 | -0.11444 | -0.18311 | -0.26093 | -0.25177 | -0.004577 | 0.17395 | 60.6308 | 60.8917 | 122.2824 | 122.493 | -0.11444 | 122.5388 | 60.759 | -0.25177 | 122.493 | -0.11444 | 60.759 | 122.2824 | 122.5388 | -122.8317 | -122.7951
773.9062 | 122.7768 | -60.7086 | 61.8896 | -0.24002 | 0.001521 | 0.005377 | 0.0004827 | 0.061893 | -0.0034971 | 0.068994 | -60.7544 | 61.821 | -60.9512 | -60.8459 | 61.5829 | 0.1236 | 0.050354 | 0.27008 | 61.8713 | -60.965 | -0.24262 | -0.068664 | -0.045777 | -0.13733 | -0.3067 | -0.25635 | -0.01831 | 0.19684 | 60.759 | 60.9787 | 122.2916 | 122.5296 | -0.045777 | 122.58 | 60.8322 | -0.25635 | 122.5296 | -0.045777 | 60.8322 | 122.2916 | 122.58 | -122.8409 | -122.8546
774.9688 | 122.8729 | -60.6537 | 61.8668 | -0.16373 | 0.00066656 | 0.001959 | -0.0005853 | 0.062747 | -0.00093346 | 0.068567 | -60.7269 | 61.7889 | -60.9558 | -60.7956 | 61.6653 | 0.15106 | -0.086975 | 0.31586 | 61.8439 | -60.9329 | -0.30212 | -0.07782 | -0.073242 | -0.14191 | -0.20142 | -0.27923 | -0.022888 | 0.22888 | 60.5667 | 60.9695 | 122.319 | 122.4426 | -0.073242 | 122.4976 | 60.8047 | -0.27923 | 122.4426 | -0.073242 | 60.8047 | 122.319 | 122.4976 | -122.8226 | -122.7997
775.9062 | 122.8546 | -60.6812 | 61.8759 | -0.018768 | 0.0038708 | 0.0045224 | -0.0010125 | 0.061466 | -0.0028561 | 0.067498 | -60.7636 | 61.7615 | -60.9833 | -60.8322 | 61.6104 | 0.12817 | -0.09613 | 0.2655 | 61.8027 | -60.9558 | -0.30212 | -0.11444 | -0.082398 | -0.15106 | -0.2655 | -0.27466 | -0.073243 | 0.21973 | 60.585 | 60.9467 | 122.2916 | 122.4426 | -0.082398 | 122.4838 | 60.8093 | -0.27466 | 122.4426 | -0.082398 | 60.8093 | 122.2916 | 122.4838 | -122.8592 | -122.8317
776.9688 | 122.7859 | -60.704 | 61.853 | 0.21011 | 0.0038708 | 0.0090086 | 0.0058233 | 0.06232 | -0.0030697 | 0.066644 | -60.8139 | 61.7981 | -61.0107 | -60.9055 | 61.5005 | -0.022888 | -0.10529 | 0.086975 | 61.8393 | -60.9375 | -0.3067 | -0.054931 | -0.10986 | -0.20142 | -0.35248 | -0.23346 | -0.013733 | 0.19684 | 60.5988 | 60.791 | 122.2046 | 122.5021 | -0.10986 | 122.5433 | 60.6812 | -0.23346 | 122.5021 | -0.10986 | 60.6812 | 122.2046 | 122.5433 | -122.8638 | -122.7905
777.9062 | 122.8683 | -60.6674 | 61.8484 | -0.13321 | 0.0030164 | 0.00024998 | -0.0027215 | 0.061893 | -0.0017881 | 0.068994 | -60.7407 | 61.7889 | -60.9558 | -60.7956 | 61.6333 | 0.15564 | -0.10529 | 0.32044 | 61.821 | -60.9558 | -0.28839 | -0.05951 | -0.073243 | -0.12817 | -0.21515 | -0.28839 | -0.027466 | 0.21515 | 60.5621 | 60.9879 | 122.3007 | 122.4564 | -0.073243 | 122.4884 | 60.8231 | -0.28839 | 122.4564 | -0.073243 | 60.8231 | 122.3007 | 122.4884 | -122.8043 | -122.8043
778.9531 | 122.7905 | -60.6903 | 61.8439 | 0.042267 | 0.0028028 | 0.0021726 | -0.0052851 | 0.061252 | -7.9062e-05 | 0.068353 | -60.8002 | 61.7752 | -60.9741 | -60.9558 | 61.5234 | 0.022888 | -0.07782 | 0.13733 | 61.8027 | -60.9604 | -0.28381 | -0.068664 | -0.10986 | -0.2655 | -0.32043 | -0.27008 | -0.041199 | 0.17395 | 60.6125 | 60.8276 | 122.2137 | 122.4655 | -0.10986 | 122.493 | 60.7132 | -0.27008 | 122.4655 | -0.10986 | 60.7132 | 122.2137 | 122.493 | -122.818 | -122.8043
779.9062 | 122.8592 | -60.6491 | 61.8484 | -0.14847 | 0.0036572 | 0.0045224 | -0.0048577 | 0.06232 | 0.0033389 | 0.070276 | -60.7178 | 61.7889 | -60.9467 | -60.9512 | 61.6791 | 0.25177 | -0.16022 | 0.27008 | 61.8118 | -60.9604 | -0.29755 | -0.05951 | -0.068664 | -0.30212 | -0.16937 | -0.31128 | -0.036621 | 0.22888 | 60.4889 | 60.9192 | 122.3282 | 122.438 | -0.068664 | 122.4609 | 60.9009 | -0.31128 | 122.438 | -0.068664 | 60.9009 | 122.3282 | 122.4609 | -122.7951 | -122.8088
780.9688 | 122.8088 | -60.704 | 61.8484 | 0.057526 | 0.00045296 | 0.0049496 | -0.0018671 | 0.061252 | 0.00034814 | 0.066644 | -60.8047 | 61.7615 | -60.9924 | -60.7956 | 61.4365 | -0.009155 | -0.059509 | 0.16937 | 61.8347 | -60.9467 | -0.28839 | -0.086975 | -0.10071 | -0.091552 | -0.41199 | -0.24261 | -0.013733 | 0.18768 | 60.6445 | 60.8734 | 122.1405 | 122.4655 | -0.10071 | 122.5388 | 60.6949 | -0.24261 | 122.4655 | -0.10071 | 60.6949 | 122.1405 | 122.5388 | -122.8409 | -122.7951
781.9062 | 123.0103 | -60.6354 | 61.9263 | -0.10269 | 0.0013074 | 0.0045224 | 0.0002691 | 0.062107 | -0.0034971 | 0.064935 | -60.7178 | 61.7523 | -60.9604 | -60.7727 | 61.6562 | 0.14191 | -0.082397 | 0.31128 | 61.8622 | -60.9238 | -0.32501 | -0.17395 | -0.082397 | -0.13733 | -0.27008 | -0.28839 | -0.064087 | 0.24262 | 60.553 | 60.9467 | 122.2916 | 122.3877 | -0.082397 | 122.4976 | 60.7773 | -0.28839 | 122.3877 | -0.082397 | 60.7773 | 122.2916 | 122.4976 | -122.8867 | -122.85
782.9062 | 122.9004 | -60.672 | 61.8576 | -0.18662 | 0.00045296 | 0.0062314 | -0.0033625 | 0.062961 | 0.00013454 | 0.067498 | -60.7361 | 61.7889 | -60.9787 | -60.7773 | 61.647 | 0.15564 | -0.086975 | 0.32501 | 61.8622 | -60.9055 | -0.3067 | -0.068665 | -0.064087 | -0.10529 | -0.21057 | -0.23346 | 0.004578 | 0.24262 | 60.585 | 60.997 | 122.319 | 122.4609 | -0.064087 | 122.5342 | 60.8276 | -0.23346 | 122.4609 | -0.064087 | 60.8276 | 122.319 | 122.5342 | -122.8363 | -122.7631
783.9531 | 122.8363 | -60.6674 | 61.8668 | -0.026398 | 0.0017346 | 0.0015316 | -0.0025079 | 0.061679 | -0.0013609 | 0.068139 | -60.7956 | 61.7752 | -60.9787 | -60.8459 | 61.5875 | 0.082397 | -0.086975 | 0.23346 | 61.8073 | -60.9695 | -0.31128 | -0.091552 | -0.12817 | -0.17853 | -0.27924 | -0.30212 | -0.059509 | 0.18311 | 60.5804 | 60.9009 | 122.2549 | 122.4426 | -0.12817 | 122.4747 | 60.7498 | -0.30212 | 122.4426 | -0.12817 | 60.7498 | 122.2549 | 122.4747 | -122.8455 | -122.8363
784.9062 | 122.7356 | -60.704 | 61.8988 | -0.16373 | 0.0034436 | 0.0043088 | 0.0073187 | 0.062107 | -0.0011471 | 0.068139 | -60.7864 | 61.8668 | -60.9558 | -60.8505 | 61.5417 | 0.054932 | 0.091553 | 0.1831 | 61.853 | -61.0153 | -0.25177 | -0.032044 | -0.082397 | -0.14648 | -0.35706 | -0.31128 | -0.045777 | 0.16937 | 60.7956 | 60.8871 | 122.2458 | 122.5708 | -0.082397 | 122.5571 | 60.759 | -0.31128 | 122.5708 | -0.082397 | 60.759 | 122.2458 | 122.5571 | -122.8546 | -122.9141
785.9688 | 122.8363 | -60.7086 | 61.8668 | 0.14908 | 0.0013074 | 0.0045224 | -0.0003717 | 0.063175 | -0.0020017 | 0.068994 | -60.7956 | 61.7706 | -60.9787 | -60.8963 | 61.5509 | 0.004578 | -0.11902 | 0.14191 | 61.8164 | -60.965 | -0.27008 | -0.09613 | -0.086975 | -0.18768 | -0.31586 | -0.25635 | -0.050354 | 0.18311 | 60.5896 | 60.8505 | 122.2595 | 122.4792 | -0.086975 | 122.525 | 60.7132 | -0.25635 | 122.4792 | -0.086975 | 60.7132 | 122.2595 | 122.525 | -122.8455 | -122.8317
786.9062 | 122.8363 | -60.6628 | 61.8484 | -0.056915 | 0.00045296 | 0.0075132 | -0.0042169 | 0.063175 | -0.0022153 | 0.068139 | -60.7773 | 61.7752 | -60.9695 | -60.8231 | 61.615 | 0.10986 | -0.086975 | 0.2655 | 61.8439 | -60.91 | -0.3067 | -0.073242 | -0.11444 | -0.16022 | -0.23346 | -0.24719 | -0.004578 | 0.19226 | 60.5759 | 60.9283 | 122.2778 | 122.4381 | -0.11444 | 122.5067 | 60.7727 | -0.24719 | 122.4381 | -0.11444 | 60.7727 | 122.2778 | 122.5067 | -122.818 | -122.7585
787.9531 | 122.8683 | -60.6766 | 61.8851 | -0.23239 | 0.002162 | 0.0051632 | 0.0009101 | 0.061252 | -0.0032835 | 0.067712 | -60.704 | 61.8073 | -60.965 | -60.791 | 61.6425 | 0.12817 | -0.036621 | 0.28839 | 61.8347 | -60.9421 | -0.28839 | -0.07782 | -0.027466 | -0.11444 | -0.24262 | -0.2655 | -0.050354 | 0.26093 | 60.64 | 60.965 | 122.319 | 122.4838 | -0.027466 | 122.5113 | 60.8047 | -0.2655 | 122.4838 | -0.027466 | 60.8047 | 122.319 | 122.5113 | -122.85 | -122.8271
788.9062 | 122.8775 | -60.6766 | 61.8896 | -0.056915 | 0.0025892 | 0.001959 | -0.0007989 | 0.061252 | -0.0022153 | 0.06643 | -60.7361 | 61.7844 | -60.965 | -60.7864 | 61.6562 | 0.13733 | -0.10529 | 0.3067 | 61.8027 | -60.9283 | -0.28839 | -0.10529 | -0.059509 | -0.10986 | -0.23346 | -0.25177 | -0.086975 | 0.22888 | 60.5713 | 60.9833 | 122.3328 | 122.4609 | -0.059509 | 122.4792 | 60.8139 | -0.25177 | 122.4609 | -0.059509 | 60.8139 | 122.3328 | 122.4792 | -122.8546 | -122.818
789.9688 | 122.7219 | -60.7132 | 61.9125 | -0.26291 | 0.0051526 | 0.0049496 | 0.0071051 | 0.061893 | -0.00029266 | 0.067498 | -60.791 | 61.9125 | -60.9512 | -60.8917 | 61.5143 | 0.045776 | 0.14191 | 0.17853 | 61.8759 | -60.9787 | -0.23804 | 0 | -0.07782 | -0.17853 | -0.39825 | -0.2655 | -0.036621 | 0.16022 | 60.8551 | 60.8917 | 122.2275 | 122.6257 | -0.07782 | 122.5891 | 60.759 | -0.2655 | 122.6257 | -0.07782 | 60.759 | 122.2275 | 122.5891 | -122.8638 | -122.8912
790.9062 | 122.8592 | -60.6491 | 61.8347 | -0.11795 | 0.0038708 | 0.0051632 | -0.0016535 | 0.063602 | -0.0022153 | 0.069207 | -60.7544 | 61.7798 | -60.9604 | -60.8093 | 61.6333 | 0.14191 | -0.082397 | 0.28381 | 61.8256 | -60.9375 | -0.31128 | -0.054932 | -0.10529 | -0.16022 | -0.20142 | -0.28839 | -0.009155 | 0.20599 | 60.5667 | 60.9329 | 122.2824 | 122.4289 | -0.10529 | 122.4747 | 60.791 | -0.28839 | 122.4289 | -0.10529 | 60.791 | 122.2824 | 122.4747 | -122.7951 | -122.7722
791.9531 | 122.8592 | -60.6903 | 61.8347 | 0.13382 | 0.0019482 | 0.003027 | 0.0009101 | 0.06467 | -0.0032835 | 0.067712 | -60.759 | 61.7661 | -60.9879 | -60.8322 | 61.5875 | 0.054932 | -0.20599 | 0.18768 | 61.7798 | -60.9512 | -0.29755 | -0.068665 | -0.068664 | -0.14191 | -0.24719 | -0.26093 | -0.054932 | 0.22888 | 60.4843 | 60.878 | 122.2778 | 122.4564 | -0.068664 | 122.4701 | 60.7452 | -0.26093 | 122.4564 | -0.068664 | 60.7452 | 122.2778 | 122.4701 | -122.8226 | -122.7859
792.9062 | 122.8592 | -60.6537 | 61.8713 | -0.072174 | 0.00045296 | 0.006445 | -0.0052851 | 0.061466 | -0.0011471 | 0.067071 | -60.759 | 61.7935 | -60.9604 | -60.8231 | 61.6196 | 0.11902 | -0.09613 | 0.26093 | 61.8118 | -60.9421 | -0.3067 | -0.07782 | -0.10529 | -0.16937 | -0.25177 | -0.28839 | -0.059509 | 0.20142 | 60.5576 | 60.9146 | 122.2733 | 122.4472 | -0.10529 | 122.4655 | 60.7727 | -0.28839 | 122.4472 | -0.10529 | 60.7727 | 122.2733 | 122.4655 | -122.8317 | -122.8134
793.9688 | 122.8363 | -60.6903 | 61.8713 | 0.042267 | 0.0036572 | 0.0034544 | -0.0005853 | 0.061679 | -0.0015745 | 0.067926 | -60.7956 | 61.7752 | -60.9833 | -60.8505 | 61.5646 | 0.068665 | -0.10071 | 0.20142 | 61.8256 | -60.9421 | -0.29297 | -0.09613 | -0.10528 | -0.16022 | -0.3067 | -0.25177 | -0.045776 | 0.18768 | 60.5896 | 60.8917 | 122.2549 | 122.4655 | -0.10528 | 122.5159 | 60.759 | -0.25177 | 122.4655 | -0.10528 | 60.759 | 122.2549 | 122.5159 | -122.8546 | -122.8134
794.9062 | 122.7402 | -60.7269 | 61.9034 | -0.19424 | 0.0023756 | 0.0025998 | 0.0041143 | 0.06232 | -0.0013609 | 0.066003 | -60.7864 | 61.8668 | -60.997 | -60.8688 | 61.8027 | 0.16479 | -0.036621 | 0.050354 | 61.8393 | -60.997 | -0.27008 | -0.036621 | -0.059509 | -0.14191 | -0.10071 | -0.27008 | -0.064087 | 0.21057 | 60.6903 | 60.7773 | 122.5296 | 122.5937 | -0.059509 | 122.5662 | 60.8917 | -0.27008 | 122.5937 | -0.059509 | 60.8917 | 122.5296 | 122.5662 | -122.9004 | -122.9004
795.9531 | 122.8226 | -60.704 | 61.8622 | 0.13382 | -0.00040164 | 0.0023862 | -0.0012261 | 0.061893 | -0.00093346 | 0.068567 | -60.8047 | 61.7706 | -60.9924 | -60.8826 | 61.5326 | 0.004578 | -0.091553 | 0.15564 | 61.8027 | -60.9512 | -0.28839 | -0.091553 | -0.10071 | -0.17853 | -0.32959 | -0.24719 | -0.05951 | 0.18768 | 60.6125 | 60.8597 | 122.2366 | 122.4747 | -0.10071 | 122.5067 | 60.7086 | -0.24719 | 122.4747 | -0.10071 | 60.7086 | 122.2366 | 122.5067 | -122.8546 | -122.8134
796.9062 | 122.8729 | -60.6674 | 61.8439 | -0.072174 | 0.00066656 | 0.003668 | -0.0022943 | 0.060398 | 0.00013454 | 0.067285 | -60.7636 | 61.7889 | -60.9512 | -60.8093 | 61.6196 | 0.13733 | -0.073242 | 0.29297 | 61.7981 | -60.9329 | -0.28381 | -0.054932 | -0.096131 | -0.14191 | -0.2243 | -0.2655 | -0.045776 | 0.18768 | 60.5942 | 60.9604 | 122.287 | 122.4564 | -0.096131 | 122.4655 | 60.8047 | -0.2655 | 122.4564 | -0.096131 | 60.8047 | 122.287 | 122.4655 | -122.7951 | -122.7768
797.9531 | 122.818 | -60.6903 | 61.8439 | 0.11856 | 0.0017346 | 0.0049496 | -0.0044305 | 0.061679 | -0.00071986 | 0.069848 | -60.7773 | 61.7569 | -60.9558 | -60.8688 | 61.5509 | 0.018311 | -0.14648 | 0.15106 | 61.7935 | -60.9558 | -0.2655 | -0.086975 | -0.086975 | -0.17853 | -0.29297 | -0.2655 | -0.050354 | 0.17853 | 60.5438 | 60.8414 | 122.2412 | 122.4472 | -0.086975 | 122.4838 | 60.7086 | -0.2655 | 122.4472 | -0.086975 | 60.7086 | 122.2412 | 122.4838 | -122.7997 | -122.7997
798.9062 | 122.85 | -60.6491 | 61.8484 | -0.095062 | -0.00040164 | 0.0015316 | -0.0007989 | 0.061679 | -7.9062e-05 | 0.066644 | -60.7636 | 61.7798 | -60.9695 | -60.8139 | 61.6196 | 0.11902 | -0.082397 | 0.26093 | 61.7752 | -60.9558 | -0.32043 | -0.068665 | -0.11444 | -0.16479 | -0.22888 | -0.3067 | -0.073242 | 0.20599 | 60.5667 | 60.91 | 122.2687 | 122.4289 | -0.11444 | 122.4243 | 60.7681 | -0.3067 | 122.4289 | -0.11444 | 60.7681 | 122.2687 | 122.4243 | -122.818 | -122.8043
799.9531 | 122.8546 | -60.672 | 61.8759 | -0.0035098 | 0.0025892 | 0.0060178 | -0.0040033 | 0.060825 | 0.0016299 | 0.069207 | -60.759 | 61.8118 | -60.9421 | -60.8368 | 61.6058 | 0.10529 | -0.07782 | 0.26093 | 61.7889 | -60.9375 | -0.27008 | -0.064087 | -0.086975 | -0.1648 | -0.27008 | -0.2655 | -0.086976 | 0.18311 | 60.5942 | 60.9329 | 122.2778 | 122.4838 | -0.086975 | 122.4609 | 60.7773 | -0.2655 | 122.4838 | -0.086975 | 60.7773 | 122.2778 | 122.4609 | -122.818 | -122.8134
800.9062 | 122.8409 | -60.6857 | 61.8622 | -0.064545 | 0.001521 | 0.003027 | -0.0014399 | 0.061252 | -0.00050626 | 0.067498 | -60.7819 | 61.8027 | -60.9467 | -60.8505 | 61.615 | 0.10529 | -0.086975 | 0.24261 | 61.8027 | -60.9467 | -0.26093 | -0.05951 | -0.09613 | -0.16479 | -0.24719 | -0.26093 | -0.05951 | 0.16479 | 60.5988 | 60.9283 | 122.3007 | 122.4884 | -0.09613 | 122.4884 | 60.791 | -0.26093 | 122.4884 | -0.09613 | 60.791 | 122.3007 | 122.4884 | -122.8088 | -122.8088
801.9531 | 122.8317 | -60.6857 | 61.8668 | 0.0041197 | 0.001521 | 0.0015316 | -0.0031489 | 0.061466 | -0.0013609 | 0.066003 | -60.7864 | 61.7844 | -60.9695 | -60.8459 | 61.5875 | 0.064087 | -0.064087 | 0.21515 | 61.7615 | -60.9329 | -0.28381 | -0.082397 | -0.10071 | -0.16022 | -0.27924 | -0.24719 | -0.10529 | 0.18311 | 60.6216 | 60.9009 | 122.2733 | 122.4701 | -0.10071 | 122.4472 | 60.7498 | -0.24719 | 122.4701 | -0.10071 | 60.7498 | 122.2733 | 122.4472 | -122.8363 | -122.7997
802.9062 | 122.8409 | -60.6812 | 61.853 | -0.041657 | 0.0030164 | 0.0045224 | -0.0025079 | 0.060825 | 0.00013454 | 0.067285 | -60.7544 | 61.7889 | -60.997 | -60.8139 | 61.6104 | 0.1236 | -0.10071 | 0.27466 | 61.7569 | -60.9375 | -0.31586 | -0.064087 | -0.073243 | -0.13275 | -0.24261 | -0.25635 | -0.09613 | 0.24261 | 60.5804 | 60.9558 | 122.2916 | 122.4701 | -0.073243 | 122.438 | 60.8047 | -0.25635 | 122.4701 | -0.073243 | 60.8047 | 122.2916 | 122.438 | -122.85 | -122.7905
803.9688 | 122.8455 | -60.6995 | 61.8439 | 0.30167 | 0.00323 | 0.0051632 | 0.0049689 | 0.064456 | -0.00071986 | 0.067926 | -60.759 | 61.7569 | -60.9741 | -60.8185 | 61.5646 | 0.045776 | -0.20142 | 0.14191 | 61.7661 | -60.9467 | -0.27466 | -0.086975 | -0.059509 | -0.11902 | -0.27924 | -0.24719 | -0.07782 | 0.21515 | 60.498 | 60.8414 | 122.2641 | 122.4564 | -0.059509 | 122.4655 | 60.7452 | -0.24719 | 122.4564 | -0.059509 | 60.7452 | 122.2641 | 122.4655 | -122.818 | -122.7905
804.9062 | 122.818 | -60.6949 | 61.8896 | -0.27054 | 0.00323 | 0.006445 | -0.0007989 | 0.060611 | -0.0032835 | 0.067926 | -60.7544 | 61.8347 | -60.9604 | -60.8276 | 61.6058 | 0.13275 | 0.013733 | 0.27466 | 61.8347 | -60.9558 | -0.2655 | -0.054931 | -0.05951 | -0.13275 | -0.28381 | -0.26093 | -0.054931 | 0.20599 | 60.7086 | 60.9695 | 122.3007 | 122.5296 | -0.05951 | 122.5296 | 60.8276 | -0.26093 | 122.5296 | -0.05951 | 60.8276 | 122.3007 | 122.5296 | -122.85 | -122.8455
805.9531 | 122.8638 | -60.6445 | 61.8256 | 0.24826 | 0.0030164 | 0.0075132 | 0.0019781 | 0.062747 | -0.0015745 | 0.06878 | -60.759 | 61.7615 | -60.9741 | -60.8322 | 61.5784 | 0.054932 | -0.20599 | 0.15564 | 61.7661 | -60.9558 | -0.32959 | -0.064087 | -0.11444 | -0.18768 | -0.24719 | -0.31128 | -0.05951 | 0.21515 | 60.4385 | 60.8002 | 122.2229 | 122.406 | -0.11444 | 122.4106 | 60.6995 | -0.31128 | 122.406 | -0.11444 | 60.6995 | 122.2229 | 122.4106 | -122.7997 | -122.7814
806.9062 | 122.8134 | -60.6903 | 61.8576 | 0.1033 | 0.00323 | 0.00067718 | -0.0042169 | 0.062534 | 0.00098914 | 0.068139 | -60.8322 | 61.7661 | -60.9924 | -60.8688 | 61.5692 | 0.045776 | -0.082397 | 0.18768 | 61.7935 | -60.9283 | -0.30212 | -0.091553 | -0.14191 | -0.17853 | -0.28839 | -0.23804 | -0.064087 | 0.16022 | 60.6079 | 60.878 | 122.2595 | 122.4564 | -0.14191 | 122.4838 | 60.7361 | -0.23804 | 122.4564 | -0.14191 | 60.7361 | 122.2595 | 122.4838 | -122.85 | -122.7859
807.9531 | 122.85 | -60.672 | 61.8301 | 0.19485 | 0.0028028 | 0.005377 | 0.0013373 | 0.063175 | -0.0020017 | 0.067071 | -60.7636 | 61.7523 | -60.9833 | -60.8505 | 61.5921 | 0.050354 | -0.17395 | 0.19226 | 61.7615 | -60.9512 | -0.31128 | -0.07782 | -0.091553 | -0.17853 | -0.23804 | -0.27924 | -0.068664 | 0.21973 | 60.498 | 60.8643 | 122.2641 | 122.4243 | -0.091553 | 122.4335 | 60.7224 | -0.27924 | 122.4243 | -0.091553 | 60.7224 | 122.2641 | 122.4335 | -122.8134 | -122.7814
808.9062 | 122.8683 | -60.6857 | 61.8805 | -0.095062 | 0.001521 | 0.0066586 | -0.0029351 | 0.061252 | -0.0011471 | 0.067926 | -60.7544 | 61.7981 | -60.9787 | -60.8002 | 61.6287 | 0.13275 | -0.086975 | 0.27924 | 61.7935 | -60.9467 | -0.29297 | -0.082397 | -0.068665 | -0.11444 | -0.25177 | -0.26093 | -0.086975 | 0.2243 | 60.5988 | 60.965 | 122.3145 | 122.4838 | -0.068665 | 122.4792 | 60.8185 | -0.26093 | 122.4838 | -0.068665 | 60.8185 | 122.3145 | 122.4792 | -122.8592 | -122.8271
809.9688 | 122.8455 | -60.6674 | 61.853 | 0.027008 | 0.001521 | 0.004736 | 0.0002691 | 0.05997 | -0.00093346 | 0.066858 | -60.8047 | 61.7798 | -60.965 | -60.8871 | 61.5784 | 0.022888 | -0.091553 | 0.16022 | 61.7706 | -60.9558 | -0.29755 | -0.073242 | -0.13733 | -0.21973 | -0.27466 | -0.28839 | -0.082397 | 0.16022 | 60.5759 | 60.8276 | 122.2458 | 122.4472 | -0.13733 | 122.438 | 60.6903 | -0.28839 | 122.4472 | -0.13733 | 60.6903 | 122.2458 | 122.438 | -122.818 | -122.8088
810.9062 | 122.8088 | -60.6766 | 61.8439 | 0.088043 | 0.0030164 | 0.004736 | -0.0010125 | 0.063602 | -0.0022153 | 0.067498 | -60.8139 | 61.7798 | -60.9558 | -60.8459 | 61.5601 | 0.036621 | -0.073242 | 0.16937 | 61.7981 | -60.9512 | -0.27924 | -0.064087 | -0.13733 | -0.16937 | -0.28381 | -0.27466 | -0.045776 | 0.14191 | 60.6033 | 60.8459 | 122.2366 | 122.4564 | -0.13733 | 122.4747 | 60.7132 | -0.27466 | 122.4564 | -0.13733 | 60.7132 | 122.2366 | 122.4747 | -122.7997 | -122.7951
811.9531 | 122.8683 | -60.6674 | 61.8347 | 0.33981 | 0.0025892 | 0.005377 | 0.0017645 | 0.061466 | -0.00071986 | 0.068353 | -60.7361 | 61.7661 | -60.9924 | -60.8322 | 61.5875 | 0.050354 | -0.20142 | 0.17395 | 61.7706 | -60.965 | -0.32501 | -0.068665 | -0.068665 | -0.16479 | -0.24719 | -0.29755 | -0.064087 | 0.25635 | 60.466 | 60.8414 | 122.2549 | 122.4335 | -0.068665 | 122.438 | 60.7178 | -0.29755 | 122.4335 | -0.068665 | 60.7178 | 122.2549 | 122.438 | -122.8271 | -122.7997
812.9062 | 122.8134 | -60.6812 | 61.8576 | 0.17197 | 0.0038708 | 0.0068722 | 0.0009101 | 0.064456 | -0.0022153 | 0.068353 | -60.7544 | 61.7798 | -60.965 | -60.8551 | 61.5692 | 0.041199 | -0.18768 | 0.16937 | 61.7798 | -60.9558 | -0.28381 | -0.07782 | -0.073243 | -0.17395 | -0.28839 | -0.27466 | -0.07782 | 0.21057 | 60.4935 | 60.8505 | 122.2504 | 122.4609 | -0.073243 | 122.4609 | 60.7224 | -0.27466 | 122.4609 | -0.073243 | 60.7224 | 122.2504 | 122.4609 | -122.8226 | -122.8134
813.9688 | 122.8271 | -60.7178 | 61.9171 | 0.14908 | 0.0051526 | 0.0066586 | 0.0051825 | 0.063388 | -0.0020017 | 0.068353 | -60.8414 | 61.8668 | -61.0336 | -60.9421 | 61.4502 | -0.054932 | -0.16479 | -0.29755 | 61.7706 | -61.0062 | -0.31586 | -0.050354 | -0.1236 | -0.22431 | -0.46692 | -0.28839 | -0.14648 | 0.19226 | 60.553 | 60.4202 | 122.168 | 122.5845 | -0.1236 | 122.4884 | 60.6628 | -0.28839 | 122.5845 | -0.1236 | 60.6628 | 122.168 | 122.4884 | -122.9507 | -122.9233
814.9062 | 122.818 | -60.6949 | 61.8576 | 0.088043 | 0.0010938 | 0.0011044 | -0.0061395 | 0.063175 | -0.0022153 | 0.067285 | -60.8276 | 61.7615 | -60.965 | -60.8551 | 61.5875 | 0.041199 | -0.082397 | 0.18768 | 61.8393 | -60.9375 | -0.27008 | -0.09613 | -0.13275 | -0.16022 | -0.27008 | -0.24262 | -0.018311 | 0.13733 | 60.6125 | 60.8826 | 122.2824 | 122.4564 | -0.13275 | 122.5342 | 60.7361 | -0.24262 | 122.4564 | -0.13275 | 60.7361 | 122.2824 | 122.5342 | -122.8226 | -122.7951
815.9062 | 122.8043 | -60.6903 | 61.8484 | 0.057526 | 0.0038708 | 0.0051632 | -0.0020807 | 0.062961 | -0.00029266 | 0.069635 | -60.8093 | 61.7752 | -60.9695 | -60.8871 | 61.5875 | 0.054932 | -0.09613 | 0.17853 | 61.8118 | -60.9421 | -0.27923 | -0.073242 | -0.11902 | -0.19684 | -0.26093 | -0.25177 | -0.036621 | 0.16022 | 60.5942 | 60.8688 | 122.2778 | 122.4655 | -0.11902 | 122.5021 | 60.7452 | -0.25177 | 122.4655 | -0.11902 | 60.7452 | 122.2778 | 122.5021 | -122.818 | -122.7905
816.9531 | 122.7356 | -60.7178 | 61.908 | 0.049896 | 0.0064344 | 0.0079404 | 0.0058233 | 0.064029 | -0.0039243 | 0.067712 | -60.8093 | 61.8668 | -61.0016 | -60.9192 | 61.4685 | -0.032043 | 0.032043 | 0.064087 | 61.8439 | -61.0062 | -0.28381 | -0.041199 | -0.091553 | -0.20142 | -0.43945 | -0.28839 | -0.064087 | 0.19226 | 60.7498 | 60.7819 | 122.1863 | 122.5845 | -0.091553 | 122.5616 | 60.6857 | -0.28839 | 122.5845 | -0.091553 | 60.6857 | 122.1863 | 122.5616 | -122.9095 | -122.9141
817.9062 | 122.8363 | -60.6674 | 61.8164 | 0.21011 | 0.0023756 | 0.0055906 | 5.5496e-05 | 0.063816 | -0.0030697 | 0.06643 | -60.7636 | 61.7798 | -60.9924 | -60.8688 | 61.5875 | 0.059509 | -0.1831 | 0.16022 | 61.7889 | -60.9833 | -0.32501 | -0.036621 | -0.096131 | -0.20142 | -0.22888 | -0.31586 | -0.027466 | 0.22888 | 60.4843 | 60.8276 | 122.2549 | 122.4472 | -0.096131 | 122.4564 | 60.7269 | -0.31586 | 122.4472 | -0.096131 | 60.7269 | 122.2549 | 122.4564 | -122.8088 | -122.7997
818.9531 | 122.731 | -60.7315 | 61.8668 | 0.042267 | 0.0051526 | 0.0090086 | 0.0045417 | 0.064884 | -0.0045651 | 0.067712 | -60.8276 | 61.8668 | -60.9833 | -60.9329 | 61.4822 | -0.041199 | 0.018311 | 0.050354 | 61.8393 | -61.0016 | -0.25177 | 0 | -0.096131 | -0.20142 | -0.38452 | -0.27008 | -0.027466 | 0.15564 | 60.7498 | 60.7819 | 122.2137 | 122.5983 | -0.096131 | 122.5708 | 60.6903 | -0.27008 | 122.5983 | -0.096131 | 60.6903 | 122.2137 | 122.5708 | -122.85 | -122.8683
819.9062 | 122.8363 | -60.6674 | 61.8347 | 0.11093 | 0.0028028 | 0.0085812 | -0.0035761 | 0.064243 | -0.0030697 | 0.06878 | -60.8093 | 61.7981 | -60.9787 | -60.8871 | 61.5601 | 0.022888 | -0.10071 | 0.14191 | 61.8073 | -60.9558 | -0.31128 | -0.036621 | -0.14191 | -0.21973 | -0.27466 | -0.28839 | -0.027466 | 0.16937 | 60.5667 | 60.8093 | 122.2275 | 122.4655 | -0.14191 | 122.4747 | 60.6903 | -0.28839 | 122.4655 | -0.14191 | 60.6903 | 122.2275 | 122.4747 | -122.8134 | -122.7905
820.9531 | 122.85 | -60.704 | 61.7844 | 0.14908 | 0.00323 | 0.0049496 | 0.0030463 | 0.066165 | -0.0015745 | 0.067926 | -60.7407 | 61.7889 | -60.9467 | -60.8459 | 61.5829 | 0.054932 | -0.19684 | 0.17853 | 61.7706 | -60.9741 | -0.24261 | 0.004577 | -0.036621 | -0.14191 | -0.20142 | -0.27008 | -0.013733 | 0.20599 | 60.5072 | 60.8826 | 122.287 | 122.493 | -0.036621 | 122.4747 | 60.759 | -0.27008 | 122.493 | -0.036621 | 60.759 | 122.287 | 122.4747 | -122.731 | -122.7585
821.9062 | 122.8455 | -60.6812 | 61.8439 | 0.35507 | 0.0047254 | 0.0066586 | 0.0015509 | 0.06467 | -0.0020017 | 0.067498 | -60.7086 | 61.7981 | -60.9512 | -60.8505 | 61.6287 | 0.059509 | -0.20599 | 0.1831 | 61.7935 | -60.9879 | -0.27008 | -0.045776 | -0.027466 | -0.16937 | -0.21515 | -0.3067 | -0.050354 | 0.24262 | 60.4752 | 60.8643 | 122.3099 | 122.4792 | -0.027466 | 122.4747 | 60.7407 | -0.3067 | 122.4792 | -0.027466 | 60.7407 | 122.3099 | 122.4747 | -122.7951 | -122.8317
822.9688 | 122.7814 | -60.6995 | 61.8896 | -0.17136 | 0.004939 | 0.01029 | 0.0056097 | 0.064029 | -0.0037107 | 0.068567 | -60.759 | 61.8988 | -60.9787 | -60.8688 | 61.5738 | 0.086975 | 0.091553 | 0.21515 | 61.8668 | -60.9695 | -0.27924 | 0.009156 | -0.059509 | -0.16937 | -0.31586 | -0.27008 | -0.022888 | 0.21973 | 60.791 | 60.9146 | 122.2733 | 122.5983 | -0.059509 | 122.5662 | 60.7864 | -0.27008 | 122.5983 | -0.059509 | 60.7864 | 122.2733 | 122.5662 | -122.8683 | -122.8592
823.9062 | 122.8546 | -60.6766 | 61.8256 | 0.21011 | 0.0034436 | 0.012213 | 0.0026191 | 0.064243 | -0.00093346 | 0.068567 | -60.759 | 61.8118 | -60.965 | -60.8414 | 61.5967 | 0.059509 | -0.16937 | 0.15106 | 61.8073 | -60.9604 | -0.28839 | -0.013733 | -0.082397 | -0.16479 | -0.22888 | -0.28381 | -0.018311 | 0.20599 | 60.5072 | 60.8276 | 122.2733 | 122.4884 | -0.082397 | 122.4838 | 60.7361 | -0.28381 | 122.4884 | -0.082397 | 60.7361 | 122.2733 | 122.4838 | -122.7905 | -122.7859
824.9688 | 122.8638 | -60.6995 | 61.8301 | 0.21774 | 0.0062208 | 0.0058042 | 0.0034735 | 0.065738 | -0.00050626 | 0.067712 | -60.759 | 61.7844 | -61.0062 | -60.8414 | 61.5829 | 0.041199 | -0.17853 | 0.14648 | 61.7752 | -60.9833 | -0.3067 | -0.045776 | -0.059509 | -0.14191 | -0.24719 | -0.28381 | -0.054931 | 0.24719 | 60.5209 | 60.8459 | 122.2824 | 122.4838 | -0.059509 | 122.4747 | 60.7407 | -0.28381 | 122.4838 | -0.059509 | 60.7407 | 122.2824 | 122.4747 | -122.8363 | -122.8134
825.9062 | 122.7585 | -60.7361 | 61.8576 | 0.93491 | 0.0060072 | 0.0060178 | 0.0045417 | 0.066379 | 0.00013454 | 0.067926 | -60.7819 | 61.9125 | -60.9833 | -60.965 | 61.4868 | -0.032043 | -0.004578 | 0.050354 | 61.821 | -61.0107 | -0.24719 | 0.054932 | -0.045776 | -0.22888 | -0.37079 | -0.27466 | -0.036621 | 0.20142 | 60.7315 | 60.7864 | 122.2229 | 122.6486 | -0.045776 | 122.5571 | 60.704 | -0.27466 | 122.6486 | -0.045776 | 60.704 | 122.2229 | 122.5571 | -122.8409 | -122.8683
826.9531 | 122.7493 | -60.7361 | 61.8668 | 0.080414 | 0.0060072 | 0.011145 | 0.0064643 | 0.065738 | -0.0026425 | 0.067712 | -60.7773 | 61.8988 | -60.9741 | -60.9238 | 61.5097 | -0.009155 | 0.018311 | 0.09613 | 61.8668 | -61.0062 | -0.23804 | 0.032044 | -0.041199 | -0.18768 | -0.35706 | -0.27008 | 0 | 0.19684 | 60.7544 | 60.8322 | 122.2458 | 122.6349 | -0.041199 | 122.6028 | 60.7269 | -0.27008 | 122.6349 | -0.041199 | 60.7269 | 122.2458 | 122.6028 | -122.8409 | -122.8729
827.9062 | 122.7905 | -60.6949 | 61.8439 | 0.27115 | 0.0057934 | 0.0070858 | 0.0036871 | 0.066379 | -0.0024289 | 0.068567 | -60.8047 | 61.8622 | -60.997 | -60.9146 | 61.5234 | -0.009155 | -0.10529 | 0.091553 | 61.8393 | -61.0016 | -0.30212 | 0.018311 | -0.10986 | -0.21973 | -0.32043 | -0.3067 | -0.004578 | 0.19226 | 60.5896 | 60.7864 | 122.2183 | 122.5571 | -0.10986 | 122.5342 | 60.6857 | -0.3067 | 122.5571 | -0.10986 | 60.6857 | 122.2183 | 122.5342 | -122.8409 | -122.8455
828.9688 | 122.7173 | -60.704 | 61.8942 | 0.065155 | 0.0062208 | 0.0092222 | 0.0041143 | 0.068088 | -0.0020017 | 0.068994 | -60.8002 | 61.8988 | -61.0107 | -60.9421 | 61.4777 | -0.027466 | 0.022888 | 0.054932 | 61.8851 | -61.0245 | -0.3067 | 0.004578 | -0.09613 | -0.23804 | -0.41657 | -0.32043 | -0.009155 | 0.21057 | 60.7269 | 60.759 | 122.1817 | 122.6028 | -0.09613 | 122.5891 | 60.6766 | -0.32043 | 122.6028 | -0.09613 | 60.6766 | 122.1817 | 122.5891 | -122.905 | -122.9187
829.9062 | 122.818 | -60.6857 | 61.8301 | 0.19485 | 0.0023756 | 0.012213 | -0.0035761 | 0.065097 | -0.00093346 | 0.070276 | -60.8047 | 61.7798 | -61.0016 | -60.9009 | 61.5738 | 0.027466 | -0.11902 | 0.15564 | 61.8164 | -60.9695 | -0.31586 | -0.050354 | -0.11902 | -0.21515 | -0.25635 | -0.28381 | -0.013733 | 0.19684 | 60.5667 | 60.8414 | 122.2595 | 122.4655 | -0.11902 | 122.5021 | 60.7132 | -0.28381 | 122.4655 | -0.11902 | 60.7132 | 122.2595 | 122.5021 | -122.8317 | -122.7997
830.9531 | 122.731 | -60.6995 | 61.8713 | 0.042267 | 0.0042982 | 0.0079404 | 0.0062507 | 0.068729 | -0.0020017 | 0.070062 | -60.8002 | 61.9171 | -60.9695 | -60.9421 | 61.4914 | -0.032043 | 0.045776 | 0.082397 | 61.853 | -61.0153 | -0.27008 | 0.045776 | -0.10071 | -0.24262 | -0.37994 | -0.31586 | -0.018311 | 0.16937 | 60.7452 | 60.7819 | 122.1909 | 122.6166 | -0.10071 | 122.5525 | 60.6674 | -0.31586 | 122.6166 | -0.10071 | 60.6674 | 122.1909 | 122.5525 | -122.8409 | -122.8867
831.9062 | 122.612 | -60.7544 | 61.8164 | 0.095673 | 0.0075024 | 0.0062314 | 0.0043281 | 0.069583 | -0.0017881 | 0.068567 | -60.8093 | 61.9034 | -61.0016 | -60.9787 | 61.4639 | -0.041199 | 0.013733 | 0.036621 | 61.8851 | -61.0062 | -0.24719 | 0.086975 | -0.054931 | -0.2243 | -0.35248 | -0.25177 | 0.068665 | 0.19226 | 60.7681 | 60.791 | 122.2183 | 122.6578 | -0.054931 | 122.6395 | 60.7132 | -0.25177 | 122.6578 | -0.054931 | 60.7132 | 122.2183 | 122.6395 | -122.818 | -122.8226
832.9688 | 122.7585 | -60.6949 | 61.8851 | -0.27054 | 0.0068616 | 0.0079404 | -0.0001581 | 0.063388 | -0.00071986 | 0.068353 | -60.6262 | 61.972 | -60.9604 | -60.9558 | 61.528 | 0.064087 | 0.14191 | 0.17853 | 61.908 | -60.9924 | -0.2655 | 0.086975 | 0.068664 | -0.26093 | -0.35706 | -0.29755 | 0.022888 | 0.33417 | 60.8368 | 60.8734 | 122.2229 | 122.6669 | 0.068664 | 122.6028 | 60.759 | -0.29755 | 122.6669 | 0.068664 | 60.759 | 122.2229 | 122.6028 | -122.8455 | -122.8775
833.9062 | 122.7539 | -60.7269 | 61.8805 | 0.042267 | 0.0051526 | 0.003027 | 0.0047553 | 0.06937 | -0.0013609 | 0.06878 | -60.7819 | 61.9171 | -60.9741 | -60.9238 | 61.5051 | -0.013733 | 0.032043 | 0.09613 | 61.853 | -61.0016 | -0.24719 | 0.036621 | -0.054931 | -0.19684 | -0.37537 | -0.27466 | -0.027466 | 0.19226 | 60.759 | 60.8231 | 122.2321 | 122.644 | -0.054931 | 122.58 | 60.7132 | -0.27466 | 122.644 | -0.054931 | 60.7132 | 122.2321 | 122.58 | -122.8546 | -122.8821
834.9531 | 122.7081 | -60.7269 | 61.8713 | 0.065155 | 0.0047254 | 0.0058042 | 0.0039007 | 0.067661 | -0.0015745 | 0.069848 | -60.8368 | 61.8988 | -61.0291 | -60.9558 | 61.4639 | -0.059509 | 0.036621 | 0.045776 | 61.8759 | -61.0245 | -0.30212 | 0.027466 | -0.10986 | -0.22888 | -0.40741 | -0.29755 | 0.004578 | 0.19226 | 60.7635 | 60.7727 | 122.1909 | 122.6257 | -0.10986 | 122.6028 | 60.6674 | -0.29755 | 122.6257 | -0.10986 | 60.6674 | 122.1909 | 122.6028 | -122.9004 | -122.8958
835.9062 | 122.7448 | -60.6857 | 61.8576 | 0.057526 | 0.0055798 | 0.01029 | 0.0041143 | 0.067234 | -0.00071986 | 0.068139 | -60.759 | 61.9125 | -61.0016 | -60.8917 | 61.5463 | 0.041199 | 0.018311 | 0.14648 | 61.8668 | -60.9833 | -0.31586 | 0.054932 | -0.073242 | -0.20599 | -0.31128 | -0.29755 | 0.009155 | 0.24262 | 60.704 | 60.8322 | 122.2321 | 122.5983 | -0.073242 | 122.5525 | 60.7269 | -0.29755 | 122.5983 | -0.073242 | 60.7269 | 122.2321 | 122.5525 | -122.8592 | -122.8409
836.9688 | 122.7859 | -60.6766 | 61.8942 | -0.16373 | 0.0040846 | 0.0058042 | 0.0004827 | 0.06702 | 0.00013454 | 0.067285 | -60.7864 | 61.9217 | -60.9787 | -60.9009 | 61.5646 | 0.064087 | 0.10071 | 0.21973 | 61.8988 | -60.997 | -0.30212 | 0.027466 | -0.10986 | -0.2243 | -0.32959 | -0.32043 | 0.004578 | 0.19226 | 60.7773 | 60.8963 | 122.2412 | 122.5983 | -0.10986 | 122.5754 | 60.7407 | -0.32043 | 122.5983 | -0.10986 | 60.7407 | 122.2412 | 122.5754 | -122.8729 | -122.8912
837.9062 | 122.7539 | -60.7132 | 61.8622 | -0.056915 | 0.0051526 | 0.0083676 | 0.0032599 | 0.067234 | -0.0013609 | 0.071344 | -60.7636 | 61.8896 | -60.997 | -60.8917 | 61.5143 | 0.032043 | 0 | 0.13275 | 61.8668 | -60.997 | -0.28381 | 0.027465 | -0.050354 | -0.17853 | -0.3479 | -0.28381 | 0.004577 | 0.23346 | 60.7132 | 60.8459 | 122.2275 | 122.6028 | -0.050354 | 122.58 | 60.7452 | -0.28381 | 122.6028 | -0.050354 | 60.7452 | 122.2275 | 122.58 | -122.8592 | -122.8592
838.9688 | 122.8683 | -60.6491 | 61.8576 | -0.11032 | 0.001521 | 0.0040952 | -0.0054987 | 0.067234 | 0.0016299 | 0.069207 | -60.7315 | 61.8439 | -60.9421 | -60.8231 | 61.6425 | 0.16022 | -0.07782 | 0.31128 | 61.8393 | -60.9833 | -0.29297 | -0.013733 | -0.082397 | -0.17395 | -0.21515 | -0.33417 | -0.018311 | 0.21057 | 60.5713 | 60.9604 | 122.2916 | 122.493 | -0.082397 | 122.4884 | 60.8093 | -0.33417 | 122.493 | -0.082397 | 60.8093 | 122.2916 | 122.4884 | -122.7997 | -122.8409
839.9062 | 122.7676 | -60.7132 | 61.8484 | 0.1796 | 0.004939 | 0.0079404 | 0.0043281 | 0.065952 | -0.0015745 | 0.068567 | -60.8139 | 61.8576 | -61.0016 | -60.9467 | 61.5005 | -0.022888 | -0.086975 | 0.082397 | 61.8439 | -61.0199 | -0.28839 | 0.009155 | -0.10071 | -0.23346 | -0.3479 | -0.3067 | -0.004578 | 0.18768 | 60.6262 | 60.7956 | 122.2137 | 122.5708 | -0.10071 | 122.5571 | 60.6903 | -0.3067 | 122.5708 | -0.10071 | 60.6903 | 122.2137 | 122.5571 | -122.85 | -122.8683
840.9688 | 122.8134 | -60.6674 | 61.853 | -0.19424 | 0.0017346 | 0.0072996 | -0.0016535 | 0.062961 | -0.0011471 | 0.06878 | -60.7315 | 61.8805 | -60.9604 | -60.8414 | 61.5875 | 0.1236 | 0.050354 | 0.25635 | 61.8759 | -60.9924 | -0.29297 | 0.027466 | -0.064087 | -0.17395 | -0.2655 | -0.32501 | 0.022889 | 0.22888 | 60.7178 | 60.9238 | 122.2549 | 122.5479 | -0.064087 | 122.5433 | 60.791 | -0.32501 | 122.5479 | -0.064087 | 60.791 | 122.2549 | 122.5433 | -122.8134 | -122.8455
841.9062 | 122.7722 | -60.6857 | 61.8805 | -0.17136 | 0.0047254 | 0.0070858 | 0.0043281 | 0.065097 | -0.0020017 | 0.068994 | -60.7452 | 61.9171 | -60.9695 | -60.878 | 61.5692 | 0.09613 | 0.068665 | 0.21515 | 61.8896 | -61.0199 | -0.28381 | 0.036621 | -0.059509 | -0.19226 | -0.31128 | -0.33417 | 0.009155 | 0.2243 | 60.7544 | 60.9009 | 122.2549 | 122.6028 | -0.059509 | 122.5754 | 60.7819 | -0.33417 | 122.6028 | -0.059509 | 60.7819 | 122.2549 | 122.5754 | -122.85 | -122.9004
842.9688 | 122.7905 | -60.6903 | 61.853 | 0.080414 | 0.0036572 | 0.0083676 | -0.0029351 | 0.066379 | -0.00093346 | 0.066644 | -60.8002 | 61.8576 | -60.9741 | -60.8917 | 61.5692 | 0.045776 | -0.068665 | 0.17853 | 61.8484 | -60.9879 | -0.28381 | 0.004578 | -0.10986 | -0.20142 | -0.28381 | -0.29755 | -0.004577 | 0.17395 | 60.6216 | 60.8688 | 122.2595 | 122.5479 | -0.10986 | 122.5388 | 60.7361 | -0.29755 | 122.5479 | -0.10986 | 60.7361 | 122.2595 | 122.5388 | -122.8271 | -122.8409
843.9062 | 122.7722 | -60.704 | 61.8896 | -0.14847 | 0.0057934 | 0.0040952 | 0.0060369 | 0.065525 | -0.0028561 | 0.068994 | -60.7544 | 61.9217 | -60.9924 | -60.8734 | 61.5555 | 0.068665 | 0.073242 | 0.2243 | 61.8851 | -61.0199 | -0.28839 | 0.032044 | -0.050354 | -0.16937 | -0.33417 | -0.31586 | -0.004577 | 0.23804 | 60.7773 | 60.9283 | 122.2595 | 122.6257 | -0.050354 | 122.5891 | 60.7727 | -0.31586 | 122.6257 | -0.050354 | 60.7727 | 122.2595 | 122.5891 | -122.8821 | -122.9095
844.9688 | 122.8958 | -60.6445 | 61.8622 | 0.41611 | 0.0030164 | 0.0083676 | -0.0035761 | 0.065311 | -0.0011471 | 0.067712 | -60.6308 | 61.853 | -60.9512 | -60.8047 | 61.647 | 0.16937 | -0.064087 | 0.32501 | 61.853 | -60.965 | -0.3067 | -0.009156 | 0.013733 | -0.16022 | -0.21515 | -0.32043 | -0.009156 | 0.32044 | 60.5804 | 60.9695 | 122.2916 | 122.4976 | 0.013733 | 122.4976 | 60.8139 | -0.32043 | 122.4976 | 0.013733 | 60.8139 | 122.2916 | 122.4976 | -122.8134 | -122.8271
845.9062 | 122.7493 | -60.6949 | 61.9217 | -0.27054 | 0.0040846 | 0.0058042 | 0.0045417 | 0.063602 | -0.0030697 | 0.067071 | -60.8185 | 61.8896 | -61.0062 | -60.9146 | 61.528 | 0.045776 | 0.12817 | 0.1831 | 61.8851 | -60.9833 | -0.31128 | -0.032044 | -0.1236 | -0.21973 | -0.39368 | -0.28839 | -0.036621 | 0.18768 | 60.8231 | 60.878 | 122.2229 | 122.5845 | -0.1236 | 122.58 | 60.7407 | -0.28839 | 122.5845 | -0.1236 | 60.7407 | 122.2229 | 122.58 | -122.9279 | -122.905
846.9688 | 122.7905 | -60.672 | 61.8622 | -0.21713 | 0.0017346 | 0.0058042 | -0.0005853 | 0.064029 | -0.0017881 | 0.066217 | -60.759 | 61.8393 | -60.9604 | -60.8368 | 61.6196 | 0.1236 | 0.022888 | 0.27466 | 61.8484 | -60.9741 | -0.28839 | -0.022889 | -0.086975 | -0.1648 | -0.24262 | -0.30212 | -0.013733 | 0.20142 | 60.6949 | 60.9467 | 122.2916 | 122.5113 | -0.086975 | 122.5204 | 60.7956 | -0.30212 | 122.5113 | -0.086975 | 60.7956 | 122.2916 | 122.5204 | -122.8226 | -122.8363
847.9062 | 122.8043 | -60.6949 | 61.9629 | -0.17899 | 0.0025892 | -0.00017722 | 0.0002691 | 0.065311 | -0.0013609 | 0.069207 | -60.8047 | 61.8713 | -60.9879 | -60.91 | 61.5234 | 0.054932 | 0.1236 | 0.19226 | 61.908 | -60.9924 | -0.29297 | -0.091553 | -0.10986 | -0.21515 | -0.43945 | -0.29755 | -0.054932 | 0.1831 | 60.8185 | 60.8871 | 122.2183 | 122.5662 | -0.10986 | 122.6028 | 60.7498 | -0.29755 | 122.5662 | -0.10986 | 60.7498 | 122.2183 | 122.6028 | -122.9507 | -122.9553
848.9531 | 122.8455 | -60.6949 | 61.8576 | -0.20187 | 0.00323 | 0.0023862 | -0.0001581 | 0.065311 | -0.0024289 | 0.068567 | -60.7224 | 61.8576 | -60.9604 | -60.8322 | 61.6196 | 0.14648 | -0.004578 | 0.28381 | 61.8622 | -60.9695 | -0.2655 | 0 | -0.027466 | -0.13733 | -0.23804 | -0.27466 | 0.004578 | 0.23804 | 60.6903 | 60.9787 | 122.3145 | 122.5525 | -0.027466 | 122.5571 | 60.8414 | -0.27466 | 122.5525 | -0.027466 | 60.8414 | 122.3145 | 122.5571 | -122.818 | -122.8271
849.9062 | 122.731 | -60.7132 | 61.9125 | -0.19424 | 0.0034436 | 0.0015316 | 0.0017645 | 0.064243 | -0.00050626 | 0.069421 | -60.8047 | 61.8805 | -60.9879 | -60.9055 | 61.5326 | 0.045776 | 0.12817 | 0.1831 | 61.8805 | -60.9924 | -0.27466 | -0.032044 | -0.091553 | -0.19226 | -0.37994 | -0.27924 | -0.032044 | 0.1831 | 60.8414 | 60.8963 | 122.2458 | 122.5937 | -0.091553 | 122.5937 | 60.759 | -0.27924 | 122.5937 | -0.091553 | 60.759 | 122.2458 | 122.5937 | -122.9004 | -122.905
850.9531 | 122.8912 | -60.6674 | 61.853 | -0.19424 | 0.00023916 | 0.0055906 | -0.0089167 | 0.05997 | -0.0011471 | 0.06878 | -60.7132 | 61.8027 | -60.965 | -61.0748 | 61.4456 | 0.16022 | -0.054932 | 0.21057 | 61.8256 | -60.9375 | -0.29755 | -0.050354 | -0.045777 | -0.40741 | -0.40741 | -0.27008 | -0.027465 | 0.25177 | 60.6125 | 60.878 | 122.113 | 122.4701 | -0.045777 | 122.493 | 60.8276 | -0.27008 | 122.4701 | -0.045777 | 60.8276 | 122.113 | 122.493 | -122.818 | -122.7905
851.9219 | 122.731 | -60.7269 | 61.8896 | 0.057526 | 0.0047254 | 0.0060178 | 0.0081733 | 0.064884 | -0.0013609 | 0.067926 | -60.7681 | 61.9125 | -61.0016 | -60.9238 | 61.4731 | -0.054932 | 0.032043 | 0.082397 | 61.8851 | -61.0336 | -0.27466 | 0.022889 | -0.041198 | -0.19684 | -0.41656 | -0.3067 | -0.004577 | 0.23346 | 60.759 | 60.8093 | 122.2 | 122.6395 | -0.041198 | 122.612 | 60.672 | -0.3067 | 122.6395 | -0.041198 | 60.672 | 122.2 | 122.612 | -122.8912 | -122.9233
852.9531 | 122.85 | -60.6491 | 61.8576 | -0.2095 | 0.00045296 | 0.0032406 | -0.0031489 | 0.062961 | -0.0028561 | 0.06878 | -60.7407 | 61.8164 | -60.9741 | -60.8139 | 61.6241 | 0.14648 | -0.018311 | 0.29755 | 61.8713 | -60.9421 | -0.32501 | -0.041199 | -0.091553 | -0.16479 | -0.23346 | -0.29297 | 0.013733 | 0.23346 | 60.6308 | 60.9467 | 122.2733 | 122.4655 | -0.091553 | 122.5204 | 60.7956 | -0.29297 | 122.4655 | -0.091553 | 60.7956 | 122.2733 | 122.5204 | -122.8317 | -122.7997
853.9062 | 122.8821 | -60.6308 | 61.8805 | -0.049286 | 0.0017346 | 0.006445 | -0.0018671 | 0.064029 | -0.0026425 | 0.066858 | -60.7269 | 61.7981 | -60.9421 | -60.8093 | 61.6241 | 0.12817 | -0.054932 | 0.31128 | 61.8713 | -60.9421 | -0.31128 | -0.082397 | -0.096131 | -0.17853 | -0.25635 | -0.31128 | -0.009155 | 0.21515 | 60.5759 | 60.9421 | 122.2549 | 122.4289 | -0.096131 | 122.5021 | 60.759 | -0.31128 | 122.4289 | -0.096131 | 60.759 | 122.2549 | 122.5021 | -122.8226 | -122.8226
854.9688 | 122.8775 | -60.672 | 61.8622 | -0.087433 | 0.001521 | 0.003027 | 0.0006965 | 0.061252 | -7.9062e-05 | 0.067285 | -60.7361 | 61.821 | -60.9421 | -60.8231 | 61.6333 | 0.14191 | -0.086975 | 0.30212 | 61.8027 | -60.965 | -0.27008 | -0.041199 | -0.064087 | -0.15106 | -0.22888 | -0.29297 | -0.05951 | 0.20599 | 60.585 | 60.9741 | 122.3053 | 122.493 | -0.064087 | 122.4747 | 60.8139 | -0.29297 | 122.493 | -0.064087 | 60.8139 | 122.3053 | 122.4747 | -122.8043 | -122.8271
855.9062 | 122.8729 | -60.6583 | 61.8439 | -0.087433 | -0.00018804 | -0.0044498 | -0.0025079 | 0.061679 | -0.0011471 | 0.068994 | -60.7498 | 61.7889 | -60.9695 | -60.8093 | 61.6196 | 0.13733 | -0.09613 | 0.29297 | 61.8118 | -60.9329 | -0.31128 | -0.054932 | -0.091553 | -0.15106 | -0.2243 | -0.27466 | -0.032043 | 0.21973 | 60.5621 | 60.9512 | 122.2778 | 122.4472 | -0.091553 | 122.4701 | 60.7956 | -0.27466 | 122.4472 | -0.091553 | 60.7956 | 122.2778 | 122.4701 | -122.8134 | -122.7768
856.9688 | 122.7493 | -60.6903 | 61.8759 | -0.22476 | 0.0051526 | 0.0058042 | 0.0075323 | 0.062747 | -0.0015745 | 0.066003 | -60.7452 | 61.9125 | -60.9558 | -60.8459 | 61.5234 | 0.050354 | 0.013733 | 0.17395 | 61.8484 | -61.0062 | -0.2655 | 0.036621 | -0.054931 | -0.15564 | -0.35248 | -0.31586 | -0.027466 | 0.21057 | 60.704 | 60.8643 | 122.2137 | 122.6028 | -0.054931 | 122.5388 | 60.7407 | -0.31586 | 122.6028 | -0.054931 | 60.7407 | 122.2137 | 122.5388 | -122.8317 | -122.8821
857.9062 | 122.8775 | -60.6583 | 61.8484 | -0.10269 | 0.0036572 | 0.0045224 | -0.0016535 | 0.062534 | -0.0020017 | 0.070062 | -60.7315 | 61.7889 | -60.9741 | -60.8002 | 61.6333 | 0.15106 | -0.09613 | 0.31586 | 61.8301 | -60.9329 | -0.31586 | -0.05951 | -0.073242 | -0.14191 | -0.21515 | -0.27466 | -0.018311 | 0.24261 | 60.5621 | 60.9741 | 122.2916 | 122.4472 | -0.073242 | 122.4884 | 60.8093 | -0.27466 | 122.4472 | -0.073242 | 60.8093 | 122.2916 | 122.4884 | -122.8226 | -122.7814
858.9688 | 122.6852 | -60.7315 | 61.853 | 0.11093 | 0.0019482 | 0.006445 | 0.0041143 | 0.063602 | -0.0022153 | 0.068994 | -60.8505 | 61.8301 | -61.0199 | -60.9558 | 61.4639 | -0.073242 | 0.004578 | 0.050354 | 61.8484 | -60.997 | -0.28839 | -0.022888 | -0.11902 | -0.2243 | -0.3891 | -0.2655 | -0.004577 | 0.16937 | 60.7361 | 60.7819 | 122.1954 | 122.5616 | -0.11902 | 122.58 | 60.6583 | -0.2655 | 122.5616 | -0.11902 | 60.6583 | 122.1954 | 122.58 | -122.8729 | -122.85
859.9062 | 122.7173 | -60.7315 | 61.8851 | -0.19424 | 0.0051526 | 0.0011044 | 0.0039007 | 0.063602 | -0.0020017 | 0.068994 | -60.7956 | 61.8851 | -60.9833 | -60.9009 | 61.5417 | 0.027466 | 0.11902 | 0.1831 | 61.8851 | -60.9879 | -0.25177 | 0 | -0.064087 | -0.16937 | -0.34332 | -0.25635 | 0 | 0.18768 | 60.8505 | 60.9146 | 122.2733 | 122.6166 | -0.064087 | 122.6166 | 60.759 | -0.25635 | 122.6166 | -0.064087 | 60.759 | 122.2733 | 122.6166 | -122.8683 | -122.8729
860.9531 | 122.8363 | -60.704 | 61.7798 | 0.1796 | 0.0017346 | 0.0049496 | 0.0032599 | 0.065738 | -0.0015745 | 0.068567 | -60.7452 | 61.7889 | -60.9787 | -60.8459 | 61.5875 | 0.054932 | -0.20599 | 0.17395 | 61.8073 | -60.9375 | -0.27466 | 0.009155 | -0.041198 | -0.14191 | -0.19226 | -0.23346 | 0.027466 | 0.23346 | 60.498 | 60.878 | 122.2916 | 122.493 | -0.041198 | 122.5113 | 60.759 | -0.23346 | 122.493 | -0.041198 | 60.759 | 122.2916 | 122.5113 | -122.7585 | -122.7173
861.9219 | 122.7768 | -60.6949 | 61.8896 | 0.83572 | 0.0038708 | 0.0051632 | 0.0030463 | 0.065952 | 0.00077554 | 0.067498 | -60.6583 | 61.8759 | -60.9787 | -60.8505 | 61.5875 | 0.073242 | -0.004578 | 0.17853 | 61.8668 | -61.0107 | -0.28381 | -0.013732 | 0.036621 | -0.15564 | -0.30212 | -0.31586 | -0.022888 | 0.32043 | 60.6903 | 60.8734 | 122.2824 | 122.5708 | 0.036621 | 122.5616 | 60.7681 | -0.31586 | 122.5708 | 0.036621 | 60.7681 | 122.2824 | 122.5616 | -122.8683 | -122.9004
862.9531 | 122.8043 | -60.672 | 61.8484 | 0.17197 | 0.00045296 | 0.0051632 | -0.0018671 | 0.063816 | -0.0017881 | 0.069848 | -60.8047 | 61.7752 | -60.9787 | -60.9009 | 61.5463 | 0.004578 | -0.10986 | 0.15106 | 61.8301 | -60.9833 | -0.3067 | -0.073242 | -0.13275 | -0.22888 | -0.30212 | -0.31128 | -0.018311 | 0.17395 | 60.5621 | 60.8231 | 122.2183 | 122.4472 | -0.13275 | 122.5021 | 60.6766 | -0.31128 | 122.4472 | -0.13275 | 60.6766 | 122.2183 | 122.5021 | -122.8271 | -122.8317
863.9062 | 122.8271 | -60.6903 | 61.8576 | -0.011139 | 0.0013074 | 0.0028134 | -0.0040033 | 0.061679 | -0.00050626 | 0.067498 | -60.8047 | 61.7844 | -60.997 | -60.8688 | 61.5784 | 0.073242 | -0.073242 | 0.19684 | 61.8073 | -60.965 | -0.3067 | -0.073242 | -0.11444 | -0.17853 | -0.27924 | -0.27466 | -0.050354 | 0.19226 | 60.6171 | 60.8871 | 122.2687 | 122.4747 | -0.11444 | 122.4976 | 60.7636 | -0.27466 | 122.4747 | -0.11444 | 60.7636 | 122.2687 | 122.4976 | -122.8546 | -122.8226
864.9531 | 122.8043 | -60.6766 | 61.8668 | 0.17197 | 0.00323 | 0.0060178 | 0.0009101 | 0.061252 | -7.9062e-05 | 0.066858 | -60.7544 | 61.7523 | -60.965 | -60.8688 | 61.5738 | 0.032043 | -0.16937 | 0.1831 | 61.7798 | -60.9558 | -0.28839 | -0.11444 | -0.07782 | -0.19226 | -0.29297 | -0.27924 | -0.086975 | 0.21057 | 60.5072 | 60.8597 | 122.2504 | 122.4289 | -0.07782 | 122.4564 | 60.7086 | -0.27924 | 122.4289 | -0.07782 | 60.7086 | 122.2504 | 122.4564 | -122.8317 | -122.8226
865.9062 | 122.8134 | -60.6995 | 61.8484 | -0.011139 | 0.00323 | 0.003027 | 0.0002691 | 0.062534 | -0.0017881 | 0.067712 | -60.8688 | 61.7935 | -60.9467 | -60.8917 | 61.5234 | 0.045776 | -0.091553 | 0.15564 | 61.8118 | -60.965 | -0.24719 | -0.054932 | -0.16937 | -0.19226 | -0.32501 | -0.2655 | -0.036621 | 0.07782 | 60.6079 | 60.8551 | 122.2229 | 122.493 | -0.16937 | 122.5113 | 60.7452 | -0.2655 | 122.493 | -0.16937 | 60.7452 | 122.2229 | 122.5113 | -122.7951 | -122.8134
866.9688 | 122.7676 | -60.6949 | 61.8896 | -0.16373 | 0.0017346 | 0.0070858 | 0.0051825 | 0.059543 | -0.0030697 | 0.068567 | -60.7956 | 61.8439 | -61.0016 | -60.8643 | 61.5417 | 0.050354 | 0.09613 | 0.20142 | 61.8805 | -60.9833 | -0.3067 | -0.045776 | -0.10071 | -0.16937 | -0.3479 | -0.28839 | -0.009155 | 0.20599 | 60.791 | 60.8963 | 122.2366 | 122.5388 | -0.10071 | 122.5754 | 60.7452 | -0.28839 | 122.5388 | -0.10071 | 60.7452 | 122.2366 | 122.5754 | -122.8912 | -122.8729
867.9062 | 122.8043 | -60.6949 | 61.853 | 0.042267 | 0.0019482 | 0.0032406 | -0.0027215 | 0.062961 | -7.9062e-05 | 0.070276 | -60.8093 | 61.7798 | -60.9741 | -60.8963 | 61.5646 | 0.032043 | -0.10071 | 0.16937 | 61.8301 | -60.9604 | -0.27924 | -0.073242 | -0.11444 | -0.20142 | -0.28839 | -0.2655 | -0.022888 | 0.16479 | 60.5942 | 60.8643 | 122.2595 | 122.4747 | -0.11444 | 122.525 | 60.7269 | -0.2655 | 122.4747 | -0.11444 | 60.7269 | 122.2595 | 122.525 | -122.8271 | -122.8134
868.9531 | 122.8317 | -60.6812 | 61.8484 | 0.13382 | 0.001521 | 0.0094358 | -0.0033625 | 0.061679 | -0.0028561 | 0.06643 | -60.8093 | 61.7752 | -60.9833 | -60.8734 | 61.5417 | 0.013733 | -0.10071 | 0.15564 | 61.8073 | -60.9695 | -0.30212 | -0.073242 | -0.12817 | -0.19226 | -0.3067 | -0.28839 | -0.041199 | 0.17395 | 60.5804 | 60.8368 | 122.2229 | 122.4564 | -0.12817 | 122.4884 | 60.6949 | -0.28839 | 122.4564 | -0.12817 | 60.6949 | 122.2229 | 122.4884 | -122.8317 | -122.818
869.9062 | 122.8043 | -60.6903 | 61.853 | 0.042267 | 0.0013074 | 0.0060178 | 0.0015509 | 0.062747 | 0.0018435 | 0.066644 | -60.8047 | 61.8073 | -60.9467 | -60.8551 | 61.5509 | 0.013733 | -0.07782 | 0.16022 | 61.8164 | -60.9512 | -0.25635 | -0.045776 | -0.11444 | -0.16479 | -0.30212 | -0.26093 | -0.036621 | 0.14191 | 60.6125 | 60.8505 | 122.2412 | 122.4976 | -0.11444 | 122.5067 | 60.704 | -0.26093 | 122.4976 | -0.11444 | 60.704 | 122.2412 | 122.5067 | -122.7997 | -122.8043
870.9688 | 122.7402 | -60.6949 | 61.8576 | 0.26352 | 0.0064344 | 0.0066586 | 0.0047553 | 0.06467 | -0.0017881 | 0.067712 | -60.8185 | 61.8301 | -61.0107 | -60.9329 | 61.4777 | -0.064087 | -0.036621 | 0.050354 | 61.8484 | -61.0107 | -0.31586 | -0.027466 | -0.1236 | -0.23804 | -0.37994 | -0.31586 | -0.009155 | 0.19226 | 60.6583 | 60.7452 | 122.1725 | 122.525 | -0.1236 | 122.5433 | 60.6308 | -0.31586 | 122.525 | -0.1236 | 60.6308 | 122.1725 | 122.5433 | -122.8683 | -122.8683
871.9062 | 122.8226 | -60.672 | 61.8713 | -0.018768 | 0.0010938 | 0.0028134 | -0.0029351 | 0.062534 | -0.00093346 | 0.065576 | -60.791 | 61.7889 | -60.9787 | -60.8505 | 61.5692 | 0.050354 | -0.068665 | 0.18768 | 61.8256 | -60.9695 | -0.3067 | -0.082398 | -0.11902 | -0.17853 | -0.30212 | -0.29755 | -0.045776 | 0.18768 | 60.6033 | 60.8597 | 122.2412 | 122.4609 | -0.11902 | 122.4976 | 60.7224 | -0.29755 | 122.4609 | -0.11902 | 60.7224 | 122.2412 | 122.4976 | -122.85 | -122.8409
872.9688 | 122.7631 | -60.7086 | 61.8484 | 0.21774 | 0.0042982 | 0.006445 | 0.0041143 | 0.062747 | -0.0024289 | 0.067285 | -60.8002 | 61.7935 | -61.0062 | -60.8917 | 61.5326 | -0.018311 | -0.10071 | 0.07782 | 61.8393 | -60.9695 | -0.29755 | -0.054932 | -0.091553 | -0.18311 | -0.31586 | -0.26093 | -0.009156 | 0.20599 | 60.6079 | 60.7864 | 122.2412 | 122.5021 | -0.091553 | 122.5479 | 60.6903 | -0.26093 | 122.5021 | -0.091553 | 60.6903 | 122.2412 | 122.5479 | -122.8546 | -122.818
873.9062 | 122.8226 | -60.672 | 61.8668 | 0.034637 | 0.002162 | 0.005377 | -0.0027215 | 0.063175 | -0.0020017 | 0.069635 | -60.8002 | 61.7889 | -60.9741 | -60.878 | 61.5372 | 0.009155 | -0.091553 | 0.13733 | 61.8256 | -60.9512 | -0.30212 | -0.07782 | -0.12817 | -0.20599 | -0.32959 | -0.27924 | -0.041198 | 0.17395 | 60.5804 | 60.8093 | 122.2092 | 122.4609 | -0.12817 | 122.4976 | 60.6812 | -0.27924 | 122.4609 | -0.12817 | 60.6812 | 122.2092 | 122.4976 | -122.8409 | -122.818
874.9219 | 122.7448 | -60.6903 | 61.908 | -0.36209 | 0.0038708 | 0.005377 | 0.0034735 | 0.063816 | -0.00093346 | 0.064508 | -60.7864 | 61.8988 | -60.9741 | -60.8917 | 61.5372 | 0.036621 | 0.13275 | 0.17395 | 61.8622 | -60.9924 | -0.28381 | -0.009155 | -0.09613 | -0.20142 | -0.37079 | -0.30212 | -0.045776 | 0.18768 | 60.8231 | 60.8643 | 122.2275 | 122.5891 | -0.09613 | 122.5525 | 60.7269 | -0.30212 | 122.5891 | -0.09613 | 60.7269 | 122.2275 | 122.5525 | -122.8821 | -122.9004
875.9531 | 122.7402 | -60.6949 | 61.8896 | -0.041657 | 0.0036572 | 0.0075132 | 0.0053961 | 0.062534 | -0.0017881 | 0.066217 | -60.7636 | 61.8713 | -60.9924 | -60.8734 | 61.5143 | -0.009155 | 0.013733 | 0.10986 | 61.8484 | -60.9833 | -0.29755 | -0.01831 | -0.068665 | -0.17853 | -0.37537 | -0.28839 | -0.041198 | 0.22888 | 60.7086 | 60.8047 | 122.2092 | 122.5662 | -0.068665 | 122.5433 | 60.6857 | -0.28839 | 122.5662 | -0.068665 | 60.6857 | 122.2092 | 122.5433 | -122.8821 | -122.8729
876.9062 | 122.7997 | -60.6857 | 61.853 | 0.15671 | 0.0040846 | 0.0062314 | -0.0022943 | 0.066806 | -0.0017881 | 0.067498 | -60.7727 | 61.7981 | -60.9695 | -60.8688 | 61.5829 | 0.032043 | -0.16479 | 0.14191 | 61.8073 | -60.9512 | -0.28381 | -0.054931 | -0.086975 | -0.1831 | -0.27008 | -0.2655 | -0.045776 | 0.19684 | 60.5209 | 60.8276 | 122.2687 | 122.4838 | -0.086975 | 122.493 | 60.7178 | -0.2655 | 122.4838 | -0.086975 | 60.7178 | 122.2687 | 122.493 | -122.8226 | -122.8043
877.9531 | 122.7219 | -60.6812 | 61.8942 | 0.080414 | 0.0062208 | 0.0075132 | 0.0068915 | 0.06467 | -0.0030697 | 0.069421 | -60.7864 | 61.8484 | -61.0153 | -60.8963 | 61.4868 | -0.004578 | -0.013733 | 0.091553 | 61.8668 | -61.0016 | -0.33417 | -0.045776 | -0.10529 | -0.21515 | -0.40741 | -0.32044 | -0.027466 | 0.22888 | 60.6674 | 60.7727 | 122.168 | 122.5296 | -0.10529 | 122.5479 | 60.6766 | -0.32044 | 122.5296 | -0.10529 | 60.6766 | 122.168 | 122.5479 | -122.9095 | -122.8958
878.9062 | 122.8226 | -60.6949 | 61.8439 | 0.19485 | 0.0013074 | 0.0072996 | -0.0033625 | 0.062747 | -0.0028561 | 0.06643 | -60.7773 | 61.7981 | -60.9512 | -60.8826 | 61.5601 | 0.022888 | -0.1236 | 0.1236 | 61.8164 | -60.9741 | -0.25635 | -0.045776 | -0.082398 | -0.18768 | -0.28381 | -0.27924 | -0.027466 | 0.17395 | 60.5713 | 60.8185 | 122.2549 | 122.493 | -0.082398 | 122.5113 | 60.7178 | -0.27924 | 122.493 | -0.082398 | 60.7178 | 122.2549 | 122.5113 | -122.7951 | -122.818
879.9688 | 122.7356 | -60.7361 | 61.8439 | 0.14908 | 0.0062208 | 0.0062314 | 0.0049689 | 0.064243 | -0.0026425 | 0.068353 | -60.8139 | 61.8668 | -61.0016 | -60.9421 | 61.4914 | -0.054932 | -0.022888 | 0.045776 | 61.8393 | -61.0062 | -0.2655 | 0.022888 | -0.07782 | -0.20599 | -0.35248 | -0.27008 | -0.004578 | 0.18768 | 60.7132 | 60.7819 | 122.2275 | 122.6028 | -0.07782 | 122.5754 | 60.6812 | -0.27008 | 122.6028 | -0.07782 | 60.6812 | 122.2275 | 122.5754 | -122.8455 | -122.85
880.9062 | 122.8088 | -60.6812 | 61.8759 | 0.11093 | 0.0042982 | 0.0021726 | -0.0018671 | 0.061893 | -0.0022153 | 0.067498 | -60.7819 | 61.7935 | -60.9512 | -60.9055 | 61.5692 | 0.022888 | -0.091553 | 0.15564 | 61.8439 | -60.9558 | -0.27008 | -0.082398 | -0.10071 | -0.22431 | -0.3067 | -0.27466 | -0.032044 | 0.16937 | 60.5896 | 60.8368 | 122.2504 | 122.4747 | -0.10071 | 122.525 | 60.704 | -0.27466 | 122.4747 | -0.10071 | 60.704 | 122.2504 | 122.525 | -122.8271 | -122.8317
881.9688 | 122.8546 | -60.6949 | 61.8439 | 0.1796 | 0.0060072 | 0.00089078 | 0.0039007 | 0.064243 | -0.0028561 | 0.068353 | -60.7727 | 61.8118 | -60.9787 | -60.8597 | 61.5692 | 0.032043 | -0.1831 | 0.13275 | 61.8164 | -60.9512 | -0.28381 | -0.032043 | -0.07782 | -0.16479 | -0.27466 | -0.25635 | -0.027466 | 0.20599 | 60.5118 | 60.8276 | 122.2641 | 122.5067 | -0.07782 | 122.5113 | 60.7269 | -0.25635 | 122.5067 | -0.07782 | 60.7269 | 122.2641 | 122.5113 | -122.8226 | -122.7951
882.9062 | 122.8592 | -60.672 | 61.8393 | 0.27878 | 0.0042982 | 0.0068722 | 0.0041143 | 0.063175 | -0.0030697 | 0.068567 | -60.7727 | 61.8256 | -60.9879 | -60.8368 | 61.5784 | 0.050354 | -0.17853 | 0.16022 | 61.7889 | -60.965 | -0.31586 | -0.013732 | -0.10071 | -0.1648 | -0.26093 | -0.29297 | -0.050354 | 0.21515 | 60.4935 | 60.8322 | 122.2504 | 122.4976 | -0.10071 | 122.4609 | 60.7224 | -0.29297 | 122.4976 | -0.10071 | 60.7224 | 122.2504 | 122.4609 | -122.8271 | -122.8043
883.9688 | 122.7722 | -60.7132 | 61.8439 | 0.17197 | 0.0057934 | 0.0077268 | 0.0034735 | 0.065738 | -0.0024289 | 0.06878 | -60.8185 | 61.8576 | -61.0062 | -60.9375 | 61.5143 | -0.036621 | -0.086975 | 0.068665 | 61.8347 | -60.997 | -0.29297 | 0.013733 | -0.10528 | -0.2243 | -0.32959 | -0.28381 | -0.009155 | 0.18768 | 60.6262 | 60.7819 | 122.2275 | 122.5708 | -0.10528 | 122.5479 | 60.6766 | -0.28381 | 122.5708 | -0.10528 | 60.6766 | 122.2275 | 122.5479 | -122.85 | -122.8409
884.9062 | 122.8363 | -60.6812 | 61.8622 | 0.049896 | 0.002162 | 0.0034544 | -0.0025079 | 0.062747 | -0.0017881 | 0.067071 | -60.7864 | 61.7935 | -60.9512 | -60.8688 | 61.5967 | 0.073242 | -0.07782 | 0.2243 | 61.8256 | -60.9421 | -0.27008 | -0.068665 | -0.10529 | -0.18768 | -0.2655 | -0.26093 | -0.036621 | 0.1648 | 60.6033 | 60.9055 | 122.2778 | 122.4747 | -0.10529 | 122.5067 | 60.7544 | -0.26093 | 122.4747 | -0.10529 | 60.7544 | 122.2778 | 122.5067 | -122.8134 | -122.8043
885.9531 | 122.7081 | -60.704 | 61.908 | 0.14908 | 0.0040846 | 0.0077268 | 0.0077459 | 0.065738 | -0.0032835 | 0.066858 | -60.8185 | 61.8713 | -60.997 | -60.6949 | 61.6562 | -0.054932 | -0.018311 | 0.11444 | 61.8576 | -61.0199 | -0.29297 | -0.036621 | -0.11444 | 0.009156 | -0.25177 | -0.31586 | -0.050354 | 0.17853 | 60.6857 | 60.8185 | 122.3602 | 122.5754 | -0.11444 | 122.5616 | 60.6491 | -0.31586 | 122.5754 | -0.11444 | 60.6491 | 122.3602 | 122.5616 | -122.905 | -122.9279
886.9062 | 122.8683 | -60.6674 | 61.8576 | 0.233 | 0.0042982 | 0.006445 | 0.0032599 | 0.064243 | -0.0026425 | 0.068994 | -60.7224 | 61.7981 | -60.9604 | -61.0245 | 61.4685 | 0.032043 | -0.022888 | 0.17395 | 61.821 | -60.9558 | -0.29297 | -0.059509 | -0.054932 | -0.35706 | -0.3891 | -0.28839 | -0.036621 | 0.23804 | 60.6445 | 60.8414 | 122.1359 | 122.4655 | -0.054932 | 122.4884 | 60.6995 | -0.28839 | 122.4655 | -0.054932 | 60.6995 | 122.1359 | 122.4884 | -122.818 | -122.8134
887.9531 | 122.7127 | -60.7224 | 61.8713 | 0.11093 | 0.0038708 | 0.0043088 | 0.0068915 | 0.066165 | -0.0030697 | 0.066217 | -60.7956 | 61.9125 | -60.9741 | -60.9238 | 61.4731 | -0.054932 | 0.013733 | 0.041199 | 61.8576 | -61.0245 | -0.25177 | 0.041199 | -0.073242 | -0.20142 | -0.39825 | -0.30212 | -0.013733 | 0.17853 | 60.7361 | 60.7636 | 122.1954 | 122.6349 | -0.073242 | 122.58 | 60.6674 | -0.30212 | 122.6349 | -0.073242 | 60.6674 | 122.1954 | 122.58 | -122.8455 | -122.8958
888.9062 | 122.8317 | -60.6537 | 61.8256 | 0.27115 | 0.0051526 | 0.0075132 | 0.0011237 | 0.066806 | 0.00056194 | 0.066644 | -60.759 | 61.8301 | -60.9787 | -60.8688 | 61.5692 | 0.045776 | -0.16022 | 0.14191 | 61.8027 | -60.9695 | -0.32501 | 0.004577 | -0.10529 | -0.21515 | -0.25635 | -0.31586 | -0.022889 | 0.21973 | 60.4935 | 60.7956 | 122.2229 | 122.4838 | -0.10529 | 122.4564 | 60.6995 | -0.31586 | 122.4838 | -0.10529 | 60.6995 | 122.2229 | 122.4564 | -122.8043 | -122.7951
889.9688 | 122.7539 | -60.6995 | 61.8713 | 0.13382 | 0.006648 | 0.0090086 | 0.0034735 | 0.065738 | -0.0024289 | 0.069207 | -60.8093 | 61.8301 | -61.0016 | -60.9283 | 61.496 | -0.041199 | -0.050354 | 0.064087 | 61.8484 | -60.9741 | -0.30212 | -0.041199 | -0.10986 | -0.22888 | -0.37537 | -0.27466 | -0.022888 | 0.19226 | 60.6491 | 60.7636 | 122.1954 | 122.5296 | -0.10986 | 122.5479 | 60.6583 | -0.27466 | 122.5296 | -0.10986 | 60.6583 | 122.1954 | 122.5479 | -122.8729 | -122.8455
890.9062 | 122.7768 | -60.6903 | 61.8256 | 0.1796 | 0.0072888 | 0.0060178 | 0.0026191 | 0.068302 | 0.00013454 | 0.067926 | -60.8093 | 61.8759 | -60.9741 | -60.9055 | 61.5097 | -0.027466 | -0.091553 | 0.073242 | 61.8622 | -60.9879 | -0.28381 | 0.050354 | -0.11902 | -0.21515 | -0.31586 | -0.29755 | 0.036621 | 0.16479 | 60.5988 | 60.7636 | 122.2 | 122.5662 | -0.11902 | 122.5525 | 60.6628 | -0.29755 | 122.5662 | -0.11902 | 60.6628 | 122.2 | 122.5525 | -122.7997 | -122.8134
891.9531 | 122.8226 | -60.6949 | 61.8118 | 0.25589 | 0.0047254 | 0.0090086 | 0.0028327 | 0.067447 | -0.00071986 | 0.068994 | -60.7636 | 61.8896 | -60.9695 | -60.8597 | 61.5646 | 0.036621 | -0.13275 | 0.11902 | 61.8256 | -60.9787 | -0.27466 | 0.077819 | -0.068665 | -0.16479 | -0.24719 | -0.28381 | 0.013733 | 0.20599 | 60.5621 | 60.8139 | 122.2595 | 122.5845 | -0.068665 | 122.5204 | 60.7315 | -0.28381 | 122.5845 | -0.068665 | 60.7315 | 122.2595 | 122.5204 | -122.7814 | -122.7905
892.9062 | 122.8043 | -60.7086 | 61.8393 | 0.24063 | 0.0057934 | 0.008154 | 0.0026191 | 0.06467 | 0.00098914 | 0.069207 | -60.7864 | 61.8622 | -60.9787 | -60.9055 | 61.528 | -0.022888 | -0.10529 | 0.091553 | 61.8576 | -60.9833 | -0.27008 | 0.022889 | -0.07782 | -0.19684 | -0.31128 | -0.27466 | 0.018311 | 0.19226 | 60.6033 | 60.8002 | 122.2366 | 122.5708 | -0.07782 | 122.5662 | 60.6857 | -0.27466 | 122.5708 | -0.07782 | 60.6857 | 122.2366 | 122.5662 | -122.818 | -122.8226
893.9688 | 122.7676 | -60.672 | 61.908 | -0.056915 | 0.0036572 | 0.0058042 | 0.0041143 | 0.063602 | -0.00050626 | 0.067498 | -60.8505 | 61.8896 | -60.9879 | -60.8505 | 61.5463 | 0.064087 | 0.027466 | 0.19226 | 61.8805 | -60.9833 | -0.31586 | -0.018311 | -0.17853 | -0.17853 | -0.36163 | -0.31128 | -0.027466 | 0.13733 | 60.6995 | 60.8643 | 122.2183 | 122.5616 | -0.17853 | 122.5525 | 60.7361 | -0.31128 | 122.5616 | -0.17853 | 60.7361 | 122.2183 | 122.5525 | -122.8958 | -122.8912
894.9062 | 122.818 | -60.64 | 61.8256 | 0.19485 | 0.0030164 | 0.0058042 | -0.0005853 | 0.06702 | -0.00093346 | 0.069635 | -60.7086 | 61.8393 | -60.9604 | -60.8459 | 61.5143 | -0.14648 | -0.14191 | 0.31586 | 61.8256 | -60.9421 | -0.32043 | 0.013732 | -0.068664 | -0.20599 | -0.31128 | -0.30212 | 0 | 0.25177 | 60.498 | 60.9558 | 122.1542 | 122.4792 | -0.068664 | 122.4655 | 60.4935 | -0.30212 | 122.4792 | -0.068664 | 60.4935 | 122.1542 | 122.4655 | -122.7859 | -122.7676
895.9531 | 122.6944 | -60.6949 | 61.8896 | 0.065155 | 0.0055798 | 0.005377 | 0.0056097 | 0.065952 | -0.00050626 | 0.067285 | -60.7819 | 61.9217 | -60.9924 | -60.9375 | 61.4914 | -0.022888 | 0.022888 | 0.045776 | 61.8988 | -61.0519 | -0.29755 | 0.032044 | -0.086975 | -0.24262 | -0.39825 | -0.35706 | 0.009156 | 0.21057 | 60.7178 | 60.7407 | 122.1863 | 122.6166 | -0.086975 | 122.5937 | 60.672 | -0.35706 | 122.6166 | -0.086975 | 60.672 | 122.1863 | 122.5937 | -122.8821 | -122.9416
896.9062 | 122.7539 | -60.6949 | 61.8713 | 0.16434 | 0.0053662 | 0.0072996 | 0.0036871 | 0.068515 | -0.0026425 | 0.066858 | -60.7864 | 61.9171 | -61.0062 | -60.9238 | 61.5005 | -0.041199 | -0.045776 | 0.059509 | 61.8942 | -61.0153 | -0.31128 | 0.045776 | -0.091553 | -0.22888 | -0.37079 | -0.32044 | 0.022888 | 0.21973 | 60.6491 | 60.7544 | 122.1954 | 122.612 | -0.091553 | 122.5891 | 60.6537 | -0.32044 | 122.612 | -0.091553 | 60.6537 | 122.1954 | 122.5891 | -122.8775 | -122.8867
897.9531 | 122.7264 | -60.6812 | 61.908 | -0.19424 | 0.0047254 | 0.0058042 | -0.0022943 | 0.067661 | -0.0017881 | 0.068353 | -60.7819 | 61.94 | -60.9283 | -60.9283 | 61.4456 | -0.12817 | 0.17853 | 0.19684 | 61.9034 | -61.0062 | -0.24719 | 0.032043 | -0.10071 | -0.24719 | -0.46234 | -0.32501 | -0.004578 | 0.14648 | 60.8597 | 60.878 | 122.1268 | 122.6212 | -0.10071 | 122.5845 | 60.553 | -0.32501 | 122.6212 | -0.10071 | 60.553 | 122.1268 | 122.5845 | -122.8363 | -122.9141
898.9062 | 122.6898 | -60.7269 | 61.8988 | 0.15671 | 0.0070752 | 0.005377 | 0.0071051 | 0.070438 | -0.0015745 | 0.065576 | -60.8368 | 61.9217 | -60.9924 | -60.6903 | 61.6699 | -0.045776 | -0.013733 | 0.12817 | 61.8988 | -61.0245 | -0.2655 | 0.022888 | -0.10986 | 0.036621 | -0.22888 | -0.29755 | 0 | 0.15564 | 60.7132 | 60.8551 | 122.3969 | 122.6486 | -0.10986 | 122.6257 | 60.6812 | -0.29755 | 122.6486 | -0.10986 | 60.6812 | 122.3969 | 122.6257 | -122.8912 | -122.9233
899.9531 | 122.7631 | -60.6812 | 61.8759 | -0.12558 | 0.0051526 | 0.008154 | 0.0039007 | 0.066379 | -0.00050626 | 0.069635 | -60.7086 | 61.9217 | -60.9833 | -60.8597 | 61.5784 | 0.068665 | 0.036621 | 0.20142 | 61.9034 | -60.997 | -0.30212 | 0.045776 | -0.027466 | -0.17853 | -0.29755 | -0.31586 | 0.027465 | 0.27466 | 60.7178 | 60.8826 | 122.2595 | 122.6028 | -0.027466 | 122.5845 | 60.7498 | -0.31586 | 122.6028 | -0.027466 | 60.7498 | 122.2595 | 122.5845 | -122.8592 | -122.8729
900.9062 | 122.7127 | -60.6903 | 61.8988 | -0.011139 | 0.0057934 | 0.010717 | 0.0049689 | 0.067234 | -0.0041379 | 0.06878 | -60.7864 | 61.94 | -60.9604 | -60.9329 | 61.4639 | -0.041199 | 0.032043 | 0.050354 | 61.8988 | -61.0107 | -0.27008 | 0.041198 | -0.09613 | -0.24261 | -0.43488 | -0.32043 | 0 | 0.17395 | 60.7224 | 60.7407 | 122.1542 | 122.6303 | -0.09613 | 122.5891 | 60.6491 | -0.32043 | 122.6303 | -0.09613 | 60.6491 | 122.1542 | 122.5891 | -122.8592 | -122.9095
901.9531 | 122.731 | -60.6903 | 61.9217 | 0.049896 | 0.0051526 | 0.009863 | 0.0017645 | 0.068729 | -0.0011471 | 0.069207 | -60.704 | 61.9446 | -60.9375 | -60.8597 | 61.5555 | 0.045776 | 0.018311 | 0.15106 | 61.9034 | -60.9833 | -0.24719 | 0.022888 | -0.013733 | -0.16937 | -0.36621 | -0.29297 | -0.018311 | 0.23346 | 60.7086 | 60.8414 | 122.2458 | 122.6349 | -0.013733 | 122.5937 | 60.7361 | -0.29297 | 122.6349 | -0.013733 | 60.7361 | 122.2458 | 122.5937 | -122.8592 | -122.905
902.9062 | 122.7173 | -60.6857 | 61.8942 | 0.027008 | 0.0047254 | 0.0051632 | 0.0036871 | 0.06937 | -0.0026425 | 0.06643 | -60.7498 | 61.9217 | -60.9741 | -60.8963 | 61.528 | -0.018311 | 0.032043 | 0.11444 | 61.8988 | -61.0016 | -0.28839 | 0.027466 | -0.064087 | -0.21057 | -0.36621 | -0.31586 | 0.004578 | 0.2243 | 60.7178 | 60.8002 | 122.2137 | 122.6074 | -0.064087 | 122.5845 | 60.6674 | -0.31586 | 122.6074 | -0.064087 | 60.6674 | 122.2137 | 122.5845 | -122.8683 | -122.8958
903.9688 | 122.7585 | -60.6857 | 61.9034 | -0.064545 | 0.0064344 | 0.01029 | 0.0017645 | 0.070011 | 0.00034814 | 0.06878 | -60.6903 | 61.9446 | -60.9787 | -60.8505 | 61.5784 | 0.036621 | 0.013733 | 0.19226 | 61.9217 | -60.965 | -0.29297 | 0.041199 | -0.004578 | -0.16479 | -0.32501 | -0.27924 | 0.018311 | 0.28839 | 60.6995 | 60.878 | 122.2641 | 122.6303 | -0.004578 | 122.6074 | 60.7224 | -0.27924 | 122.6303 | -0.004578 | 60.7224 | 122.2641 | 122.6074 | -122.8821 | -122.8683
904.9062 | 122.7631 | -60.704 | 61.8622 | 0.15671 | 0.0053662 | 0.0032406 | 0.0032599 | 0.067661 | -0.0013609 | 0.06878 | -60.8139 | 61.94 | -60.9924 | -60.9375 | 61.5051 | -0.059509 | -0.022888 | 0.059509 | 61.908 | -61.0153 | -0.28839 | 0.077819 | -0.10986 | -0.23346 | -0.35706 | -0.31128 | 0.045776 | 0.17853 | 60.6812 | 60.7635 | 122.2092 | 122.644 | -0.10986 | 122.612 | 60.6445 | -0.31128 | 122.644 | -0.10986 | 60.6445 | 122.2092 | 122.612 | -122.8546 | -122.8775
905.9688 | 122.8226 | -60.6079 | 61.9171 | -0.2095 | 0.0057934 | 0.0092222 | -0.0057123 | 0.065311 | 0.00013454 | 0.068139 | -60.6903 | 61.9034 | -60.9009 | -60.8185 | 61.647 | 0.13733 | -0.009155 | 0.28381 | 61.9034 | -60.9604 | -0.29297 | -0.013733 | -0.082398 | -0.21057 | -0.27008 | -0.35248 | -0.013733 | 0.21057 | 60.5988 | 60.8917 | 122.2549 | 122.5113 | -0.082398 | 122.5113 | 60.7452 | -0.35248 | 122.5113 | -0.082398 | 60.7452 | 122.2549 | 122.5113 | -122.818 | -122.8775
906.9062 | 122.7356 | -60.6903 | 61.908 | 0.034637 | 0.0038708 | 0.008154 | 0.0060369 | 0.065525 | -0.00029266 | 0.067498 | -60.7819 | 61.9537 | -60.9833 | -60.9192 | 61.5097 | -0.018311 | 0.032043 | 0.082397 | 61.8759 | -61.0199 | -0.29297 | 0.045776 | -0.091552 | -0.22888 | -0.39825 | -0.32959 | -0.032043 | 0.20142 | 60.7224 | 60.7727 | 122.2 | 122.644 | -0.091552 | 122.5662 | 60.672 | -0.32959 | 122.644 | -0.091552 | 60.672 | 122.2 | 122.5662 | -122.8912 | -122.9279
907.9688 | 122.7631 | -60.6628 | 61.9263 | -0.34683 | 0.0034436 | 0.0079404 | -0.0033625 | 0.066379 | -0.0011471 | 0.066858 | -60.7727 | 61.9492 | -60.9467 | -60.8963 | 61.5601 | 0.059509 | 0.1236 | 0.19684 | 61.9217 | -60.9879 | -0.28381 | 0.022888 | -0.10986 | -0.23346 | -0.36621 | -0.32501 | -0.004578 | 0.17395 | 60.7864 | 60.8597 | 122.2229 | 122.612 | -0.10986 | 122.5845 | 60.7224 | -0.32501 | 122.612 | -0.10986 | 60.7224 | 122.2229 | 122.5845 | -122.8729 | -122.9141
908.9062 | 122.7814 | -60.6766 | 61.9308 | -0.095062 | 0.0051526 | 0.009863 | 0.0047553 | 0.06702 | -0.0017881 | 0.067498 | -60.7086 | 61.94 | -60.9558 | -60.8185 | 61.5372 | 0.036621 | 0.064087 | 0.16479 | 61.9171 | -61.0062 | -0.27924 | 0.009155 | -0.032043 | -0.14191 | -0.39368 | -0.32959 | -0.013733 | 0.24719 | 60.7407 | 60.8414 | 122.2137 | 122.6166 | -0.032043 | 122.5937 | 60.7132 | -0.32959 | 122.6166 | -0.032043 | 60.7132 | 122.2137 | 122.5937 | -122.8867 | -122.937
909.9688 | 122.7631 | -60.6537 | 61.9217 | -0.2095 | 0.0051526 | 0.0060178 | 0.0013373 | 0.064456 | -0.0013609 | 0.065789 | -60.7224 | 61.9171 | -60.9512 | -60.8597 | 61.5692 | 0.064087 | 0.07782 | 0.21515 | 61.9217 | -60.9741 | -0.29755 | -0.004578 | -0.068664 | -0.20599 | -0.35248 | -0.32043 | 0 | 0.22888 | 60.7315 | 60.8688 | 122.2229 | 122.5708 | -0.068664 | 122.5754 | 60.7178 | -0.32043 | 122.5708 | -0.068664 | 60.7178 | 122.2229 | 122.5754 | -122.8729 | -122.8958
910.9062 | 122.7264 | -60.6903 | 61.9125 | 0.0041197 | 0.0064344 | 0.0079404 | 0.0028327 | 0.066806 | -0.00050626 | 0.068567 | -60.7315 | 61.9583 | -60.9787 | -60.8871 | 61.528 | 0.004578 | 0.018311 | 0.10986 | 61.9263 | -61.0062 | -0.28839 | 0.045776 | -0.041198 | -0.19684 | -0.38452 | -0.31586 | 0.013733 | 0.24719 | 60.7086 | 60.8002 | 122.2183 | 122.6486 | -0.041198 | 122.6166 | 60.6949 | -0.31586 | 122.6486 | -0.041198 | 60.6949 | 122.2183 | 122.6166 | -122.8912 | -122.9187
911.9688 | 122.731 | -60.672 | 61.9125 | -0.21713 | 0.0040846 | 0.003668 | -0.0016535 | 0.067234 | -0.00050626 | 0.067712 | -60.7727 | 61.9217 | -60.9558 | -60.7956 | 61.4822 | -0.091553 | 0.10071 | 0.21515 | 61.94 | -60.9833 | -0.28381 | 0.009155 | -0.10071 | -0.1236 | -0.4303 | -0.31128 | 0.027465 | 0.18311 | 60.7727 | 60.8871 | 122.1542 | 122.5937 | -0.10071 | 122.612 | 60.5804 | -0.31128 | 122.5937 | -0.10071 | 60.5804 | 122.1542 | 122.612 | -122.8683 | -122.8958
912.9062 | 122.7768 | -60.6903 | 61.9034 | -0.16373 | 0.0034436 | 0.0049496 | 0.0026191 | 0.065097 | -0.00050626 | 0.069421 | -60.7269 | 61.94 | -60.9558 | -60.8414 | 61.5921 | 0.050354 | 0.054932 | 0.1831 | 61.908 | -60.9787 | -0.2655 | 0.036621 | -0.036621 | -0.15106 | -0.31128 | -0.28839 | 0.004578 | 0.22888 | 60.7452 | 60.8734 | 122.2824 | 122.6303 | -0.036621 | 122.5983 | 60.7407 | -0.28839 | 122.6303 | -0.036621 | 60.7407 | 122.2824 | 122.5983 | -122.8592 | -122.8821
913.9531 | 122.7722 | -60.6537 | 61.9171 | -0.10269 | 0.0045118 | 0.008154 | 0.0066779 | 0.067447 | -0.0024289 | 0.06643 | -60.7224 | 61.94 | -60.9741 | -60.8093 | 61.5463 | 0.041199 | 0.059509 | 0.17853 | 61.9171 | -60.9833 | -0.32043 | 0.022888 | -0.068664 | -0.15564 | -0.37079 | -0.32959 | 0 | 0.25177 | 60.7132 | 60.8322 | 122.2 | 122.5937 | -0.068664 | 122.5708 | 60.6949 | -0.32959 | 122.5937 | -0.068664 | 60.6949 | 122.2 | 122.5708 | -122.8912 | -122.9004
914.9062 | 122.7539 | -60.6857 | 61.9354 | 0.11093 | 0.0057934 | 0.0083676 | 0.0019781 | 0.070438 | -0.0024289 | 0.067071 | -60.7956 | 61.9537 | -60.9604 | -60.9558 | 61.4731 | 0.013733 | -0.50354 | -0.16479 | 61.8256 | -61.0107 | -0.27466 | 0.01831 | -0.10986 | -0.27008 | -0.46234 | -0.32501 | -0.10986 | 0.1648 | 60.1822 | 60.5209 | 122.1588 | 122.6395 | -0.10986 | 122.5113 | 60.6995 | -0.32501 | 122.6395 | -0.10986 | 60.6995 | 122.1588 | 122.5113 | -122.8958 | -122.9462
915.9688 | 122.8363 | -60.6354 | 61.9217 | 0.042267 | 0.0034436 | 0.0077268 | -0.0054987 | 0.064456 | -0.0013609 | 0.068353 | -60.7681 | 61.8805 | -60.9329 | -60.8643 | 61.5875 | 0.050354 | -0.064087 | 0.18768 | 61.8942 | -60.9512 | -0.29755 | -0.041199 | -0.13275 | -0.22888 | -0.33417 | -0.31586 | -0.027466 | 0.16479 | 60.5713 | 60.8231 | 122.2229 | 122.5159 | -0.13275 | 122.5296 | 60.6857 | -0.31586 | 122.5159 | -0.13275 | 60.6857 | 122.2229 | 122.5296 | -122.8546 | -122.8729
916.9062 | 122.7493 | -60.6262 | 61.9858 | -0.14084 | 0.0062208 | 0.0090086 | 0.0041143 | 0.06232 | -0.0013609 | 0.067498 | -60.7224 | 61.9812 | -60.9238 | -60.8093 | 61.6104 | 0.050354 | 0.082397 | 0.1831 | 61.9537 | -60.91 | -0.29755 | -0.004578 | -0.09613 | -0.1831 | -0.37537 | -0.28381 | -0.032044 | 0.20142 | 60.7086 | 60.8093 | 122.2366 | 122.6074 | -0.09613 | 122.58 | 60.6766 | -0.28381 | 122.6074 | -0.09613 | 60.6766 | 122.2366 | 122.58 | -122.9095 | -122.8958
917.9531 | 122.7264 | -60.6583 | 61.9537 | -0.27817 | 0.0028028 | 0.0055906 | 0.0009101 | 0.065311 | -0.0017881 | 0.06878 | -60.5759 | 61.9766 | -60.9055 | -60.9009 | 61.5555 | 0.027466 | 0.11902 | 0.15564 | 61.9766 | -60.9421 | -0.24719 | 0.022889 | 0.082397 | -0.24262 | -0.39825 | -0.28381 | 0.022889 | 0.32959 | 60.7773 | 60.8139 | 122.2137 | 122.6349 | 0.082397 | 122.6349 | 60.6857 | -0.28381 | 122.6349 | 0.082397 | 60.6857 | 122.2137 | 122.6349 | -122.8592 | -122.8958
918.9062 | 122.6395 | -60.6125 | 61.9904 | -0.2095 | 0.0045118 | 0.0068722 | -0.0005853 | 0.063175 | -0.0015745 | 0.067926 | -60.7361 | 61.9812 | -60.9055 | -60.8414 | 61.5829 | 0.013733 | 0.13275 | 0.35706 | 61.9949 | -60.8917 | -0.29297 | -0.009155 | -0.1236 | -0.22888 | -0.40741 | -0.27924 | 0.004578 | 0.16937 | 60.7452 | 60.9695 | 122.1954 | 122.5937 | -0.1236 | 122.6074 | 60.6262 | -0.27924 | 122.5937 | -0.1236 | 60.6262 | 122.1954 | 122.6074 | -122.8958 | -122.8821
919.9688 | 122.7448 | -60.6171 | 61.9675 | 0.034637 | 0.0055798 | 0.0066586 | 0.0043281 | 0.067447 | -0.00050626 | 0.068139 | -60.6903 | 61.9766 | -60.8963 | -60.8276 | 61.5692 | -0.041199 | 0.018311 | 0.086975 | 61.9812 | -60.9329 | -0.27924 | 0.009156 | -0.073243 | -0.21057 | -0.39825 | -0.31586 | 0.013733 | 0.20599 | 60.6354 | 60.704 | 122.1863 | 122.5937 | -0.073243 | 122.5983 | 60.5759 | -0.31586 | 122.5937 | -0.073243 | 60.5759 | 122.1863 | 122.5983 | -122.8638 | -122.9004
920.9062 | 122.7173 | -60.6125 | 62.0132 | -0.17899 | 0.00323 | 0.0066586 | -0.0035761 | 0.064884 | 0.00077554 | 0.067712 | -60.7178 | 61.9949 | -60.8871 | -60.8688 | 61.6425 | 0.050354 | 0.082397 | 0.15564 | 61.9995 | -60.9009 | -0.27466 | -0.018311 | -0.10529 | -0.25635 | -0.37079 | -0.28839 | -0.013733 | 0.16937 | 60.6949 | 60.7681 | 122.2549 | 122.6074 | -0.10529 | 122.612 | 60.6628 | -0.28839 | 122.6074 | -0.10529 | 60.6628 | 122.2549 | 122.612 | -122.9004 | -122.9141
921.9688 | 122.8363 | -60.6308 | 61.8896 | 0.16434 | 0.0028028 | 0.0049496 | -0.0020807 | 0.064456 | 0.00098914 | 0.067285 | -60.7224 | 61.8393 | -60.9421 | -60.8368 | 61.5875 | 0.013733 | -0.17853 | 0.14191 | 61.8942 | -60.9192 | -0.31128 | -0.050354 | -0.091553 | -0.20599 | -0.30212 | -0.28839 | 0.004578 | 0.21973 | 60.4523 | 60.7727 | 122.2183 | 122.4701 | -0.091553 | 122.525 | 60.6445 | -0.28839 | 122.4701 | -0.091553 | 60.6445 | 122.2183 | 122.525 | -122.8317 | -122.8088
922.9062 | 122.731 | -60.6445 | 61.9812 | -0.27817 | 0.0047254 | 0.0011044 | 0.0002691 | 0.061893 | 0.00034814 | 0.066858 | -60.7452 | 61.9171 | -60.9375 | -60.8643 | 61.5692 | 0.045776 | 0.11444 | 0.17395 | 61.94 | -60.9512 | -0.29297 | -0.064087 | -0.10071 | -0.21973 | -0.41199 | -0.3067 | -0.041199 | 0.19226 | 60.759 | 60.8185 | 122.2137 | 122.5616 | -0.10071 | 122.5845 | 60.6903 | -0.3067 | 122.5616 | -0.10071 | 60.6903 | 122.2137 | 122.5845 | -122.9187 | -122.9324
923.9688 | 122.8271 | -60.6125 | 61.9125 | 0.12619 | 0.00023916 | 0.0062314 | -0.0025079 | 0.061466 | -0.0017881 | 0.069848 | -60.7132 | 61.8576 | -60.9009 | -60.8231 | 61.6013 | 0 | -0.14191 | 0.12817 | 61.8805 | -60.91 | -0.28839 | -0.054932 | -0.10071 | -0.21057 | -0.31128 | -0.29755 | -0.032044 | 0.18768 | 60.4706 | 60.7407 | 122.2137 | 122.4701 | -0.10071 | 122.493 | 60.6125 | -0.29755 | 122.4701 | -0.10071 | 60.6125 | 122.2137 | 122.493 | -122.8134 | -122.8226
924.9062 | 122.7539 | -60.6445 | 61.9537 | 0.13382 | 0.0040846 | 0.0043088 | 0.0060369 | 0.06467 | -0.0013609 | 0.069207 | -60.7224 | 61.9629 | -60.91 | -60.8368 | 61.5555 | -0.091553 | -0.045776 | 0.036621 | 61.94 | -60.9512 | -0.2655 | 0.009156 | -0.07782 | -0.19226 | -0.39825 | -0.3067 | -0.013733 | 0.18768 | 60.5988 | 60.6812 | 122.2 | 122.6074 | -0.07782 | 122.5845 | 60.553 | -0.3067 | 122.6074 | -0.07782 | 60.553 | 122.2 | 122.5845 | -122.8638 | -122.905
925.9531 | 122.818 | -60.64 | 61.8805 | 0.20248 | 0.00323 | 0.0077268 | -0.0031489 | 0.064029 | -0.0017881 | 0.067712 | -60.7407 | 61.8622 | -60.9146 | -60.8414 | 61.6196 | -0.009155 | -0.14191 | 0.13733 | 61.8713 | -60.9146 | -0.27466 | -0.01831 | -0.10071 | -0.20142 | -0.26093 | -0.27466 | -0.009155 | 0.17395 | 60.498 | 60.7773 | 122.2595 | 122.5021 | -0.10071 | 122.5113 | 60.6308 | -0.27466 | 122.5021 | -0.10071 | 60.6308 | 122.2595 | 122.5113 | -122.7951 | -122.7951
926.9062 | 122.7448 | -60.6216 | 61.9263 | -0.16373 | 0.0042982 | 0.00089078 | -0.0012261 | 0.061466 | -0.00050626 | 0.066644 | -60.7224 | 61.908 | -60.91 | -60.8414 | 61.5829 | 0.050354 | 0.1236 | 0.17853 | 61.9446 | -60.9467 | -0.28839 | -0.018311 | -0.10071 | -0.21973 | -0.34332 | -0.32501 | 0.01831 | 0.18768 | 60.7452 | 60.8002 | 122.2046 | 122.5296 | -0.10071 | 122.5662 | 60.672 | -0.32501 | 122.5296 | -0.10071 | 60.672 | 122.2046 | 122.5662 | -122.8363 | -122.8729
927.9531 | 122.8134 | -60.6445 | 61.908 | 0.11856 | 0.0047254 | -0.00039102 | -0.0020807 | 0.061038 | -0.00029266 | 0.068353 | -60.7315 | 61.8439 | -60.9375 | -60.8276 | 61.5829 | 0.018311 | -0.10986 | 0.13733 | 61.8942 | -60.9238 | -0.29297 | -0.064087 | -0.086975 | -0.18311 | -0.32501 | -0.27924 | -0.013733 | 0.20599 | 60.5347 | 60.7819 | 122.2275 | 122.4884 | -0.086975 | 122.5388 | 60.6628 | -0.27924 | 122.4884 | -0.086975 | 60.6628 | 122.2275 | 122.5388 | -122.8455 | -122.8317
928.9062 | 122.7951 | -60.5988 | 61.9766 | -0.25528 | 0.002162 | 0.006445 | 0.0017645 | 0.062107 | -0.0013609 | 0.06643 | -60.6857 | 61.9125 | -60.9055 | -60.7773 | 61.6333 | 0.068665 | 0.032043 | 0.23804 | 61.9217 | -60.9238 | -0.3067 | -0.064087 | -0.086975 | -0.17853 | -0.34332 | -0.32501 | -0.054932 | 0.21973 | 60.6308 | 60.8368 | 122.2321 | 122.5113 | -0.086975 | 122.5204 | 60.6674 | -0.32501 | 122.5113 | -0.086975 | 60.6674 | 122.2321 | 122.5204 | -122.8821 | -122.9004
929.9688 | 122.7264 | -60.6491 | 61.972 | -0.10269 | 0.00323 | 0.0096494 | 0.0060369 | 0.063816 | -0.0020017 | 0.067498 | -60.6583 | 61.94 | -60.8871 | -60.7727 | 61.6058 | 0.032043 | -0.004578 | 0.16937 | 61.9492 | -60.9421 | -0.23804 | -0.032044 | -0.009155 | -0.1236 | -0.36621 | -0.29297 | -0.022888 | 0.22888 | 60.6445 | 60.8185 | 122.2549 | 122.5891 | -0.009155 | 122.5983 | 60.6812 | -0.29297 | 122.5891 | -0.009155 | 60.6812 | 122.2549 | 122.5983 | -122.8592 | -122.9141
930.9062 | 122.8226 | -60.6033 | 61.9583 | -0.17899 | 0.0034436 | 0.0017454 | -0.0010125 | 0.064456 | -0.0028561 | 0.067498 | -60.6857 | 61.8988 | -60.8917 | -60.7498 | 61.6608 | 0.10071 | -0.004578 | 0.25177 | 61.9217 | -60.8688 | -0.28839 | -0.059509 | -0.082397 | -0.14648 | -0.29755 | -0.2655 | -0.036621 | 0.20599 | 60.5988 | 60.8551 | 122.2641 | 122.5021 | -0.082397 | 122.525 | 60.704 | -0.2655 | 122.5021 | -0.082397 | 60.704 | 122.2641 | 122.525 | -122.85 | -122.8271
931.9688 | 122.7951 | -60.6491 | 61.8896 | 0.25589 | 0.0030164 | 0.0085812 | 0.0045417 | 0.063388 | -0.0034971 | 0.068567 | -60.7224 | 61.9034 | -60.9421 | -60.8231 | 61.5829 | -0.027466 | -0.16022 | 0.082397 | 61.8805 | -60.9283 | -0.29297 | 0.013733 | -0.073242 | -0.17395 | -0.3067 | -0.27924 | -0.009155 | 0.21973 | 60.4889 | 60.7315 | 122.2321 | 122.5525 | -0.073242 | 122.5296 | 60.6216 | -0.27924 | 122.5525 | -0.073242 | 60.6216 | 122.2321 | 122.5296 | -122.8317 | -122.818
932.9062 | 122.7631 | -60.6491 | 61.9858 | -0.2095 | 0.0017346 | 0.0051632 | -0.0003717 | 0.064456 | -0.0011471 | 0.068994 | -60.6949 | 61.94 | -60.9009 | -60.7956 | 61.615 | 0.050354 | 0.073242 | 0.18768 | 61.9583 | -60.8963 | -0.25177 | -0.045777 | -0.045776 | -0.14648 | -0.37079 | -0.24719 | -0.027466 | 0.20599 | 60.7224 | 60.8368 | 122.2641 | 122.5891 | -0.045776 | 122.6074 | 60.6995 | -0.24719 | 122.5891 | -0.045776 | 60.6995 | 122.2641 | 122.6074 | -122.8867 | -122.8821
933.9531 | 122.7768 | -60.6079 | 61.9675 | -0.24765 | 0.0028028 | 0.0075132 | -0.0005853 | 0.063175 | -0.0020017 | 0.065362 | -60.6995 | 61.9034 | -60.9055 | -60.7681 | 61.6379 | 0.073242 | 0.050354 | 0.21515 | 61.9446 | -60.878 | -0.29755 | -0.064087 | -0.091553 | -0.16022 | -0.32959 | -0.27008 | -0.022888 | 0.20599 | 60.6583 | 60.8231 | 122.2458 | 122.5113 | -0.091553 | 122.5525 | 60.6812 | -0.27008 | 122.5113 | -0.091553 | 60.6812 | 122.2458 | 122.5525 | -122.8729 | -122.8455
934.9062 | 122.6852 | -60.64 | 61.9766 | -0.21713 | 0.0028028 | 0.0038816 | 0.0013373 | 0.061893 | -0.00029266 | 0.067712 | -60.7315 | 61.9629 | -60.91 | -60.8368 | 61.5738 | -0.004578 | 0.11902 | 0.15564 | 61.9446 | -60.8917 | -0.27008 | -0.013733 | -0.091552 | -0.19684 | -0.40283 | -0.25177 | -0.032044 | 0.17853 | 60.759 | 60.7956 | 122.2137 | 122.6028 | -0.091552 | 122.5845 | 60.6354 | -0.25177 | 122.6028 | -0.091552 | 60.6354 | 122.2137 | 122.5845 | -122.8867 | -122.8683
935.9531 | 122.8638 | -60.5804 | 61.9675 | -0.087433 | 0.0036572 | 0.00046358 | -0.0020807 | 0.062534 | 0.00077554 | 0.067712 | -60.6537 | 61.8851 | -60.8597 | -60.7315 | 61.7065 | 0.086975 | -0.10071 | 0.28381 | 61.9217 | -60.8368 | -0.27924 | -0.082397 | -0.073243 | -0.15106 | -0.26092 | -0.25635 | -0.045776 | 0.20599 | 60.4797 | 60.8643 | 122.287 | 122.4655 | -0.073243 | 122.5021 | 60.6674 | -0.25635 | 122.4655 | -0.073243 | 60.6674 | 122.287 | 122.5021 | -122.8271 | -122.8043
936.9062 | 122.7402 | -60.5942 | 62.0087 | -0.22476 | 0.0030164 | 0.0045224 | 0.0028327 | 0.061252 | -0.0024289 | 0.066644 | -60.6674 | 61.94 | -60.8826 | -60.7956 | 61.6013 | -0.013733 | 0.091553 | 0.1831 | 61.9629 | -60.8734 | -0.28839 | -0.068665 | -0.073242 | -0.20142 | -0.40741 | -0.27924 | -0.045776 | 0.21515 | 60.6857 | 60.7773 | 122.1954 | 122.5342 | -0.073242 | 122.5571 | 60.5804 | -0.27924 | 122.5342 | -0.073242 | 60.5804 | 122.1954 | 122.5571 | -122.8912 | -122.8821
937.9688 | 122.731 | -60.6033 | 61.9675 | 0.019379 | 0.0042982 | 0.0068722 | 0.0066779 | 0.064884 | -0.0039243 | 0.067285 | -60.6628 | 61.9629 | -60.8871 | -60.8002 | 61.5829 | -0.050354 | 0.004578 | 0.09613 | 61.9766 | -60.9192 | -0.28381 | -0.004577 | -0.059509 | -0.19684 | -0.38452 | -0.31586 | 0.009156 | 0.2243 | 60.6079 | 60.6995 | 122.1863 | 122.5662 | -0.059509 | 122.58 | 60.553 | -0.31586 | 122.5662 | -0.059509 | 60.553 | 122.1863 | 122.58 | -122.8546 | -122.8867
938.9062 | 122.8455 | -60.5759 | 61.94 | -0.27054 | 0.0025892 | 0.0028134 | -0.0016535 | 0.061252 | -0.0024289 | 0.067498 | -60.6445 | 61.9125 | -60.8643 | -60.7361 | 61.6974 | 0.10529 | -0.064087 | 0.27466 | 61.9446 | -60.8459 | -0.28839 | -0.027465 | -0.068664 | -0.16022 | -0.24261 | -0.27008 | 0.004578 | 0.21973 | 60.5118 | 60.8505 | 122.2733 | 122.4884 | -0.068664 | 122.5204 | 60.6812 | -0.27008 | 122.4884 | -0.068664 | 60.6812 | 122.2733 | 122.5204 | -122.8043 | -122.7859
939.9688 | 122.9324 | -60.585 | 62.0087 | -0.12558 | 0.001521 | 0.0043088 | -0.0018671 | 0.063602 | -0.0015745 | 0.068567 | -60.6491 | 61.8576 | -60.878 | -60.7315 | 61.702 | 0.1236 | -0.073242 | 0.27466 | 61.8942 | -60.8917 | -0.29297 | -0.15106 | -0.064087 | -0.14648 | -0.3067 | -0.3067 | -0.11444 | 0.22888 | 60.5118 | 60.8597 | 122.287 | 122.4426 | -0.064087 | 122.4792 | 60.7086 | -0.3067 | 122.4426 | -0.064087 | 60.7086 | 122.287 | 122.4792 | -122.8867 | -122.9004
940.9062 | 122.7997 | -60.6125 | 61.9675 | -0.17136 | 0.0034436 | 0.0032406 | 0.0017645 | 0.062534 | -0.00093346 | 0.066003 | -60.672 | 61.8759 | -60.8871 | -60.759 | 61.6379 | 0.091553 | 0.022888 | 0.24261 | 61.9217 | -60.8917 | -0.27466 | -0.091552 | -0.059509 | -0.14648 | -0.32959 | -0.27924 | -0.045776 | 0.21515 | 60.6354 | 60.8551 | 122.2504 | 122.4884 | -0.059509 | 122.5342 | 60.704 | -0.27924 | 122.4884 | -0.059509 | 60.704 | 122.2504 | 122.5342 | -122.8546 | -122.8592
941.9688 | 122.8592 | -60.5942 | 61.908 | -0.095062 | 0.0013074 | 0.003027 | -0.0016535 | 0.061252 | -0.0011471 | 0.06878 | -60.6812 | 61.8301 | -60.9146 | -60.7407 | 61.6791 | 0.10986 | -0.1236 | 0.25635 | 61.8622 | -60.8963 | -0.32043 | -0.07782 | -0.086975 | -0.14648 | -0.22888 | -0.30212 | -0.045776 | 0.23346 | 60.4706 | 60.8505 | 122.2733 | 122.4243 | -0.086975 | 122.4564 | 60.704 | -0.30212 | 122.4243 | -0.086975 | 60.704 | 122.2733 | 122.4564 | -122.8226 | -122.8043
942.9219 | 122.7905 | -60.6583 | 61.9171 | 0.22537 | 0.0036572 | 0.0075132 | 0.0064643 | 0.063175 | -0.0017881 | 0.067926 | -60.7361 | 61.9125 | -60.9375 | -60.8322 | 61.5509 | -0.068665 | -0.13733 | 0.059509 | 61.8484 | -60.9375 | -0.27924 | -0.004577 | -0.07782 | -0.17395 | -0.36621 | -0.27924 | -0.068664 | 0.20142 | 60.5209 | 60.7178 | 122.2092 | 122.5708 | -0.07782 | 122.5067 | 60.5896 | -0.27924 | 122.5708 | -0.07782 | 60.5896 | 122.2092 | 122.5067 | -122.8546 | -122.8546
943.9531 | 122.8363 | -60.5988 | 61.94 | -0.011139 | 0.00023916 | 0.0077268 | -0.0037897 | 0.063175 | -0.00071986 | 0.067926 | -60.6949 | 61.8668 | -60.8826 | -60.759 | 61.6699 | 0.050354 | -0.09613 | 0.19226 | 61.9171 | -60.8734 | -0.28381 | -0.073242 | -0.09613 | -0.16022 | -0.27008 | -0.27466 | -0.022888 | 0.18768 | 60.5026 | 60.791 | 122.2687 | 122.4655 | -0.09613 | 122.5159 | 60.6491 | -0.27466 | 122.4655 | -0.09613 | 60.6491 | 122.2687 | 122.5159 | -122.8226 | -122.8134
944.9062 | 122.8775 | -60.5942 | 61.9308 | -0.10269 | 0.0028028 | 0.0055906 | -0.0027215 | 0.060611 | 0.0016299 | 0.067498 | -60.6766 | 61.8805 | -60.8917 | -60.7132 | 61.702 | 0.10071 | -0.11902 | 0.27008 | 61.8713 | -60.878 | -0.29755 | -0.050354 | -0.082398 | -0.11902 | -0.22888 | -0.28381 | -0.059509 | 0.21515 | 60.4752 | 60.8643 | 122.2961 | 122.4747 | -0.082398 | 122.4655 | 60.6949 | -0.28381 | 122.4747 | -0.082398 | 60.6949 | 122.2961 | 122.4655 | -122.8226 | -122.8088
945.9531 | 122.85 | -60.6079 | 61.94 | 2.621 | 0.0030164 | 0.004736 | 0.0009101 | 0.062107 | -0.00071986 | 0.067071 | -60.759 | 61.8393 | -60.9055 | -60.759 | 61.6653 | 0.11902 | -0.086975 | 0.25177 | 61.8805 | -60.8871 | -0.29755 | -0.10071 | -0.15106 | -0.15106 | -0.27466 | -0.27924 | -0.059509 | 0.14648 | 60.5209 | 60.8597 | 122.2733 | 122.4472 | -0.15106 | 122.4884 | 60.7269 | -0.27924 | 122.4472 | -0.15106 | 60.7269 | 122.2733 | 122.4884 | -122.8455 | -122.8271
946.9062 | 122.8592 | -60.585 | 61.94 | -0.14847 | 0.00088016 | 0.00089078 | -0.0067803 | 0.061252 | 0.00077554 | 0.067926 | -60.6445 | 61.8942 | -60.8597 | -60.8734 | 61.734 | 0.20142 | -0.20142 | 0.22888 | 61.8622 | -60.8597 | -0.27466 | -0.045776 | -0.059509 | -0.28839 | -0.20599 | -0.27466 | -0.077819 | 0.21515 | 60.3836 | 60.8139 | 122.319 | 122.4792 | -0.059509 | 122.4472 | 60.7864 | -0.27466 | 122.4792 | -0.059509 | 60.7864 | 122.319 | 122.4472 | -122.7997 | -122.7997
947.9688 | 122.7539 | -60.6308 | 61.9995 | -0.14084 | 0.0060072 | 0.0049496 | 0.0032599 | 0.061252 | -0.0028561 | 0.065576 | -60.7178 | 61.9766 | -60.91 | -60.7956 | 61.5784 | 0.009155 | 0.091553 | 0.12817 | 61.9446 | -60.9238 | -0.27924 | -0.022888 | -0.086975 | -0.16479 | -0.42114 | -0.29297 | -0.054932 | 0.19226 | 60.7224 | 60.759 | 122.2092 | 122.6074 | -0.086975 | 122.5754 | 60.64 | -0.29297 | 122.6074 | -0.086975 | 60.64 | 122.2092 | 122.5754 | -122.9095 | -122.9233
948.9062 | 122.7722 | -60.5896 | 61.9766 | -0.24765 | 0.00323 | 0.0034544 | 0.0017645 | 0.061252 | -0.0013609 | 0.06643 | -60.6766 | 61.8896 | -60.91 | -60.759 | 61.6425 | 0.054932 | 0.027466 | 0.20599 | 61.9308 | -60.8643 | -0.32043 | -0.086976 | -0.086975 | -0.16937 | -0.33417 | -0.27466 | -0.045777 | 0.23346 | 60.6171 | 60.7956 | 122.2321 | 122.4792 | -0.086975 | 122.5204 | 60.6445 | -0.27466 | 122.4792 | -0.086975 | 60.6445 | 122.2321 | 122.5204 | -122.8867 | -122.8409
949.9688 | 122.8134 | -60.6079 | 61.94 | 0.1796 | -0.0010424 | 0.0051632 | -0.0016535 | 0.063816 | -7.9062e-05 | 0.069207 | -60.7498 | 61.8576 | -60.91 | -60.8231 | 61.5921 | -0.013733 | -0.12817 | 0.11444 | 61.8805 | -60.8917 | -0.30212 | -0.082397 | -0.14191 | -0.21515 | -0.3479 | -0.28381 | -0.059509 | 0.16022 | 60.4797 | 60.7224 | 122.2 | 122.4655 | -0.14191 | 122.4884 | 60.5942 | -0.28381 | 122.4655 | -0.14191 | 60.5942 | 122.2 | 122.4884 | -122.85 | -122.8317
950.9062 | 122.8683 | -60.5988 | 61.9354 | -0.35446 | 0.0025892 | 0.0062314 | -0.0010125 | 0.061038 | -0.00093346 | 0.06878 | -60.9283 | 61.8347 | -60.9238 | -60.7452 | 61.6379 | 0.10529 | -0.050354 | 0.24719 | 61.8759 | -60.9009 | -0.32501 | -0.10071 | -0.32959 | -0.14648 | -0.29755 | -0.30212 | -0.059509 | -0.004578 | 60.5484 | 60.8459 | 122.2366 | 122.4335 | -0.32959 | 122.4747 | 60.704 | -0.30212 | 122.4335 | -0.32959 | 60.704 | 122.2366 | 122.4747 | -122.8592 | -122.8363
951.9531 | 122.8729 | -60.6033 | 61.908 | -0.072174 | 0.0017346 | 0.0021726 | -0.0014399 | 0.061466 | -0.0013609 | 0.069207 | -60.7086 | 61.8347 | -60.91 | -60.7544 | 61.6425 | 0.082397 | -0.11444 | 0.21973 | 61.8668 | -60.8917 | -0.3067 | -0.073242 | -0.10529 | -0.15106 | -0.2655 | -0.28839 | -0.041199 | 0.20142 | 60.4889 | 60.8231 | 122.2458 | 122.4381 | -0.10529 | 122.4701 | 60.6857 | -0.28839 | 122.4381 | -0.10529 | 60.6857 | 122.2458 | 122.4701 | -122.818 | -122.7997
952.9062 | 122.8958 | -60.6354 | 61.908 | -0.2095 | 0.0042982 | 0.0049496 | -0.0010125 | 0.060184 | -0.0015745 | 0.067498 | -60.6445 | 61.853 | -60.91 | -60.7544 | 61.9125 | 0.35706 | -0.32501 | -0.022888 | 61.8759 | -60.9009 | -0.27466 | -0.054932 | -0.009155 | -0.11902 | 0.004578 | -0.2655 | -0.032043 | 0.2655 | 60.3104 | 60.6125 | 122.5479 | 122.4884 | -0.009155 | 122.5113 | 60.9924 | -0.2655 | 122.4884 | -0.009155 | 60.9924 | 122.5479 | 122.5113 | -122.818 | -122.8088
953.9688 | 122.818 | -60.6354 | 61.8805 | 0.011749 | 0.0013074 | 0.0021726 | -0.0025079 | 0.06232 | -0.0020017 | 0.068567 | -60.7269 | 61.821 | -60.9467 | -60.8047 | 61.5921 | 0.027466 | -0.09613 | 0.16022 | 61.8576 | -60.8871 | -0.31128 | -0.059509 | -0.091553 | -0.16937 | -0.28839 | -0.25177 | -0.022888 | 0.21973 | 60.5392 | 60.7956 | 122.2275 | 122.4564 | -0.091553 | 122.493 | 60.6628 | -0.25177 | 122.4564 | -0.091553 | 60.6628 | 122.2275 | 122.493 | -122.8271 | -122.7676
954.9062 | 122.8043 | -60.64 | 61.9492 | -0.10269 | 0.0047254 | 0.0058042 | 0.0064643 | 0.064456 | -0.0017881 | 0.066858 | -60.6995 | 61.8942 | -60.9467 | -60.7819 | 61.5692 | 0.054932 | 0.032043 | 0.15106 | 61.908 | -60.9329 | -0.3067 | -0.054932 | -0.059509 | -0.14191 | -0.37994 | -0.29297 | -0.041199 | 0.24719 | 60.672 | 60.791 | 122.2092 | 122.5342 | -0.059509 | 122.5479 | 60.6949 | -0.29297 | 122.5342 | -0.059509 | 60.6949 | 122.2092 | 122.5479 | -122.8958 | -122.8821
955.9688 | 122.8043 | -60.6583 | 61.8896 | 0.19485 | 0.00066656 | 0.0066586 | 0.0019781 | 0.063175 | -0.0022153 | 0.069207 | -60.704 | 61.8256 | -60.9558 | -60.8002 | 61.5875 | 0.018311 | -0.20599 | 0.11444 | 61.8439 | -60.878 | -0.29755 | -0.064086 | -0.045777 | -0.14191 | -0.30212 | -0.21973 | -0.045776 | 0.25177 | 60.4523 | 60.7727 | 122.2458 | 122.4838 | -0.045777 | 122.5021 | 60.6766 | -0.21973 | 122.4838 | -0.045777 | 60.6766 | 122.2458 | 122.5021 | -122.8455 | -122.7676
956.9062 | 122.8134 | -60.6216 | 61.9263 | -0.20187 | 0.0010938 | 0.0023862 | -0.0001581 | 0.06232 | -0.0011471 | 0.066644 | -60.704 | 61.853 | -60.9238 | -60.7407 | 61.6333 | 0.091553 | -0.032043 | 0.24719 | 61.8805 | -60.8688 | -0.30212 | -0.073243 | -0.082398 | -0.11902 | -0.29297 | -0.24719 | -0.045777 | 0.21973 | 60.5896 | 60.8688 | 122.2549 | 122.4747 | -0.082398 | 122.5021 | 60.7132 | -0.24719 | 122.4747 | -0.082398 | 60.7132 | 122.2549 | 122.5021 | -122.85 | -122.7951
957.9531 | 122.8226 | -60.64 | 61.9034 | -0.026398 | 0.0025892 | 0.0066586 | -0.0005853 | 0.06232 | -0.0017881 | 0.068567 | -60.7727 | 61.8393 | -60.9604 | -60.8276 | 61.5829 | 0 | -0.086975 | 0.14191 | 61.8484 | -60.91 | -0.32043 | -0.064087 | -0.13275 | -0.18768 | -0.32043 | -0.27008 | -0.054931 | 0.18768 | 60.553 | 60.7819 | 122.2229 | 122.4792 | -0.13275 | 122.4884 | 60.64 | -0.27008 | 122.4792 | -0.13275 | 60.64 | 122.2229 | 122.4884 | -122.8638 | -122.8134
958.9062 | 122.8363 | -60.6354 | 61.9171 | -0.056915 | 0.001521 | 0.0043088 | -0.0003717 | 0.064243 | -0.0028561 | 0.068994 | -60.7407 | 61.8073 | -60.9787 | -60.8002 | 61.6287 | 0.059509 | -0.11444 | 0.16937 | 61.8713 | -60.9055 | -0.34332 | -0.10986 | -0.10529 | -0.16479 | -0.28839 | -0.27008 | -0.045776 | 0.23804 | 60.5209 | 60.8047 | 122.2641 | 122.4426 | -0.10529 | 122.5067 | 60.6949 | -0.27008 | 122.4426 | -0.10529 | 60.6949 | 122.2641 | 122.5067 | -122.8958 | -122.8226
959.9688 | 122.7631 | -60.6491 | 61.9446 | -0.22476 | 0.0055798 | 0.005377 | 0.0071051 | 0.061893 | -0.0026425 | 0.067712 | -60.6903 | 61.9354 | -60.9283 | -60.7819 | 61.5829 | -0.004578 | 0.009155 | 0.15106 | 61.9171 | -60.9512 | -0.27924 | -0.009155 | -0.041199 | -0.13275 | -0.36163 | -0.30212 | -0.027466 | 0.23804 | 60.6583 | 60.8002 | 122.2321 | 122.5845 | -0.041199 | 122.5662 | 60.6445 | -0.30212 | 122.5845 | -0.041199 | 60.6445 | 122.2321 | 122.5662 | -122.8729 | -122.8958
960.9062 | 122.8271 | -60.6262 | 61.9308 | -0.13321 | 0.0036572 | 0.0049496 | -0.0031489 | 0.062961 | -0.00093346 | 0.064935 | -60.6766 | 61.8301 | -60.91 | -60.7681 | 61.6333 | 0.064087 | -0.054932 | 0.25635 | 61.8805 | -60.8688 | -0.28381 | -0.10071 | -0.050354 | -0.14191 | -0.29755 | -0.24261 | -0.050354 | 0.23346 | 60.5713 | 60.8826 | 122.2595 | 122.4564 | -0.050354 | 122.5067 | 60.6903 | -0.24261 | 122.4564 | -0.050354 | 60.6903 | 122.2595 | 122.5067 | -122.8409 | -122.7997
961.9688 | 122.818 | -60.64 | 61.9034 | 0.095673 | 0.0010938 | 0.0017454 | -0.0020807 | 0.063388 | -0.0015745 | 0.068567 | -60.7727 | 61.8073 | -60.9467 | -60.8597 | 61.5417 | -0.041199 | -0.10071 | 0.13733 | 61.8393 | -60.9192 | -0.3067 | -0.09613 | -0.13275 | -0.21973 | -0.36163 | -0.27923 | -0.064087 | 0.17395 | 60.5392 | 60.7773 | 122.1817 | 122.4472 | -0.13275 | 122.4792 | 60.5988 | -0.27923 | 122.4472 | -0.13275 | 60.5988 | 122.1817 | 122.4792 | -122.85 | -122.8226
962.9062 | 122.8409 | -60.6171 | 61.8805 | -0.056915 | 0.0030164 | -0.00039102 | -0.0027215 | 0.061038 | 0.00034814 | 0.067498 | -60.7132 | 61.8027 | -60.9192 | -60.7544 | 61.6241 | 0.064087 | -0.1236 | 0.2655 | 61.821 | -60.9238 | -0.30212 | -0.07782 | -0.096131 | -0.13733 | -0.25635 | -0.3067 | -0.059509 | 0.20599 | 60.4935 | 60.8826 | 122.2412 | 122.4197 | -0.096131 | 122.438 | 60.6812 | -0.3067 | 122.4197 | -0.096131 | 60.6812 | 122.2412 | 122.438 | -122.7997 | -122.8043
963.9531 | 122.7631 | -60.6537 | 61.8622 | 0.088043 | 0.0025892 | 0.0045224 | -0.0020807 | 0.063388 | -0.0017881 | 0.065362 | -60.7727 | 61.8027 | -60.965 | -60.8597 | 61.528 | -0.036621 | -0.07782 | 0.3479 | 61.8805 | -60.91 | -0.31128 | -0.05951 | -0.11902 | -0.20599 | -0.33417 | -0.25635 | 0.01831 | 0.19226 | 60.5759 | 61.0016 | 122.1817 | 122.4564 | -0.11902 | 122.5342 | 60.6171 | -0.25635 | 122.4564 | -0.11902 | 60.6171 | 122.1817 | 122.5342 | -122.8271 | -122.7722
964.9062 | 122.7264 | -60.6812 | 61.9308 | -0.21713 | 0.0038708 | 0.0032406 | 0.0009101 | 0.063175 | -0.0037107 | 0.066858 | -60.7361 | 61.853 | -60.9604 | -60.8414 | 61.5463 | 0.004578 | 0.064087 | 0.20142 | 61.8713 | -60.9283 | -0.27924 | -0.07782 | -0.054932 | -0.16022 | -0.38452 | -0.24719 | -0.059509 | 0.2243 | 60.7452 | 60.8826 | 122.2275 | 122.5342 | -0.054932 | 122.5525 | 60.6857 | -0.24719 | 122.5342 | -0.054932 | 60.6857 | 122.2275 | 122.5525 | -122.8912 | -122.8592
965.9688 | 122.7997 | -60.6949 | 61.8393 | 0.21011 | 0.001521 | 0.0079404 | -0.0007989 | 0.062961 | -0.00071986 | 0.068353 | -60.7315 | 61.7935 | -60.9695 | -60.8414 | 61.5417 | -0.013733 | -0.17853 | 0.14648 | 61.7935 | -60.9329 | -0.27466 | -0.045776 | -0.036621 | -0.14648 | -0.29755 | -0.23804 | -0.045776 | 0.23804 | 60.5164 | 60.8414 | 122.2366 | 122.4884 | -0.036621 | 122.4884 | 60.6812 | -0.23804 | 122.4884 | -0.036621 | 60.6812 | 122.2366 | 122.4884 | -122.8088 | -122.7722
966.9062 | 122.8134 | -60.6812 | 61.8896 | 0.019379 | 0.0038708 | -0.00060462 | -0.0010125 | 0.060611 | -0.00071986 | 0.070489 | -60.791 | 61.8164 | -60.9604 | -60.8368 | 61.5509 | 0.004578 | -0.10071 | 0.20142 | 61.8073 | -60.9146 | -0.27924 | -0.073242 | -0.10986 | -0.15564 | -0.33875 | -0.23346 | -0.082397 | 0.16937 | 60.5804 | 60.8826 | 122.2321 | 122.4976 | -0.10986 | 122.4884 | 60.6857 | -0.23346 | 122.4976 | -0.10986 | 60.6857 | 122.2321 | 122.4884 | -122.85 | -122.8043
967.9531 | 122.8409 | -60.6812 | 61.8484 | -0.0035098 | 0.0017346 | 0.0066586 | 0.0019781 | 0.06232 | -0.0037107 | 0.067071 | -60.7407 | 61.7935 | -60.9421 | -60.8139 | 61.5463 | -0.013733 | -0.21515 | 0.15564 | 61.7889 | -60.9375 | -0.26093 | -0.054932 | -0.05951 | -0.13275 | -0.30212 | -0.25635 | -0.05951 | 0.20142 | 60.466 | 60.8368 | 122.2275 | 122.4747 | -0.05951 | 122.4701 | 60.6674 | -0.25635 | 122.4747 | -0.05951 | 60.6674 | 122.2275 | 122.4701 | -122.7905 | -122.7859
968.9062 | 122.85 | -60.6491 | 61.8896 | -0.011139 | 0.0023756 | 0.0032406 | -0.0014399 | 0.060184 | -0.0015745 | 0.068567 | -60.7636 | 61.7844 | -60.9467 | -60.8276 | 61.5692 | 0.018311 | -0.11902 | 0.23346 | 61.821 | -60.9329 | -0.29755 | -0.10529 | -0.11444 | -0.17853 | -0.32043 | -0.28381 | -0.068664 | 0.1831 | 60.5301 | 60.8826 | 122.2183 | 122.4335 | -0.11444 | 122.4701 | 60.6674 | -0.28381 | 122.4335 | -0.11444 | 60.6674 | 122.2183 | 122.4701 | -122.8363 | -122.8226
969.9688 | 122.7997 | -60.6812 | 61.8668 | 0.11093 | 0.0025892 | 0.0058042 | 0.0006965 | 0.061038 | -7.9062e-05 | 0.065362 | -60.7819 | 61.8027 | -60.9558 | -60.8643 | 61.5234 | -0.009155 | -0.1236 | 0.12817 | 61.8027 | -60.9512 | -0.27466 | -0.064087 | -0.10071 | -0.18311 | -0.34332 | -0.27008 | -0.064087 | 0.17395 | 60.5576 | 60.8093 | 122.2046 | 122.4838 | -0.10071 | 122.4838 | 60.672 | -0.27008 | 122.4838 | -0.10071 | 60.672 | 122.2046 | 122.4838 | -122.8226 | -122.818
970.9062 | 122.818 | -60.6445 | 61.8851 | 0.011749 | 0.0036572 | 0.001318 | -0.0012261 | 0.061466 | -0.00093346 | 0.067071 | -60.7819 | 61.8073 | -60.9695 | -60.8322 | 61.5463 | -0.004578 | -0.091553 | 0.17395 | 61.8256 | -60.9421 | -0.32501 | -0.07782 | -0.13733 | -0.18768 | -0.33875 | -0.29755 | -0.059509 | 0.18768 | 60.553 | 60.8185 | 122.1909 | 122.4518 | -0.13733 | 122.4701 | 60.64 | -0.29755 | 122.4518 | -0.13733 | 60.64 | 122.1909 | 122.4701 | -122.8546 | -122.8271
971.9688 | 122.8546 | -60.6628 | 61.8576 | 0.31693 | 0.0019482 | 0.0072996 | -0.0001581 | 0.062747 | -0.00071986 | 0.066644 | -60.7224 | 61.7889 | -60.9695 | -60.8047 | 61.5601 | -0.004578 | -0.23804 | 0.15106 | 61.8073 | -60.9329 | -0.3067 | -0.068665 | -0.059509 | -0.14191 | -0.29755 | -0.27008 | -0.050354 | 0.24719 | 60.4248 | 60.8139 | 122.2229 | 122.4518 | -0.059509 | 122.4701 | 60.6583 | -0.27008 | 122.4518 | -0.059509 | 60.6583 | 122.2229 | 122.4701 | -122.8271 | -122.7905
972.9062 | 122.8226 | -60.6857 | 61.8713 | 0.11093 | 0.0025892 | 0.0028134 | -0.0035761 | 0.061893 | -0.0013609 | 0.06878 | -60.7773 | 61.7523 | -60.9512 | -60.8734 | 61.5143 | -0.027466 | -0.16022 | 0.13275 | 61.8073 | -60.9558 | -0.2655 | -0.11902 | -0.091553 | -0.18768 | -0.35706 | -0.27008 | -0.064087 | 0.17395 | 60.5255 | 60.8185 | 122.2 | 122.438 | -0.091553 | 122.493 | 60.6583 | -0.27008 | 122.438 | -0.091553 | 60.6583 | 122.2 | 122.493 | -122.8226 | -122.8271
973.9688 | 122.8409 | -60.6674 | 61.8484 | 0.17197 | 0.00323 | 0.0079404 | 0.0017645 | 0.062961 | -0.0030697 | 0.067712 | -60.7407 | 61.7615 | -60.9467 | -60.8322 | 61.5326 | -0.013733 | -0.20599 | 0.15106 | 61.7798 | -60.9558 | -0.27924 | -0.086975 | -0.073243 | -0.16479 | -0.31586 | -0.28839 | -0.068665 | 0.20599 | 60.4614 | 60.8185 | 122.2 | 122.4289 | -0.073243 | 122.4472 | 60.6537 | -0.28839 | 122.4289 | -0.073243 | 60.6537 | 122.2 | 122.4472 | -122.7951 | -122.8043
974.9062 | 122.8363 | -60.6491 | 61.8347 | -0.018768 | 0.0023756 | 0.0051632 | -0.0035761 | 0.060611 | 0.00056194 | 0.068994 | -60.7727 | 61.7981 | -60.9604 | -60.8231 | 61.5601 | 0.032043 | -0.09613 | 0.22888 | 61.7981 | -60.9421 | -0.31128 | -0.036621 | -0.1236 | -0.17395 | -0.27466 | -0.29297 | -0.036621 | 0.18768 | 60.553 | 60.878 | 122.2092 | 122.4472 | -0.1236 | 122.4472 | 60.6812 | -0.29297 | 122.4472 | -0.1236 | 60.6812 | 122.2092 | 122.4472 | -122.7951 | -122.7768
975.9688 | 122.7402 | -60.7224 | 61.8759 | 0.21011 | 0.0042982 | 0.0049496 | 0.0043281 | 0.062107 | -0.00071986 | 0.066644 | -60.8047 | 61.8301 | -61.0291 | -60.9146 | 61.4319 | -0.1236 | -0.045776 | 0.050354 | 61.821 | -60.9924 | -0.3067 | -0.045777 | -0.082398 | -0.19226 | -0.44403 | -0.27008 | -0.054932 | 0.2243 | 60.6766 | 60.7727 | 122.1542 | 122.5525 | -0.082398 | 122.5433 | 60.5988 | -0.27008 | 122.5525 | -0.082398 | 60.5988 | 122.1542 | 122.5433 | -122.905 | -122.8683
976.9062 | 122.7951 | -60.6628 | 61.853 | 0.11093 | 0.004939 | 0.0011044 | -0.0018671 | 0.061252 | -0.0015745 | 0.06878 | -60.8002 | 61.8164 | -60.965 | -60.8871 | 61.5372 | -0.054932 | -0.1236 | 0.14648 | 61.8301 | -60.9604 | -0.30212 | -0.036621 | -0.13733 | -0.2243 | -0.31586 | -0.29755 | -0.022888 | 0.16479 | 60.5392 | 60.8093 | 122.2 | 122.4792 | -0.13733 | 122.493 | 60.6079 | -0.29755 | 122.4792 | -0.13733 | 60.6079 | 122.2 | 122.493 | -122.818 | -122.8134
977.9531 | 122.7814 | -60.6949 | 61.8484 | 0.233 | 0.0036572 | 0.0038816 | 0.0053961 | 0.065525 | -0.00071986 | 0.067498 | -60.7864 | 61.8301 | -60.997 | -60.8643 | 61.4914 | -0.068665 | -0.1831 | 0.09613 | 61.8164 | -60.9467 | -0.30212 | -0.018311 | -0.091553 | -0.16937 | -0.35706 | -0.25177 | -0.032044 | 0.21057 | 60.5118 | 60.791 | 122.1863 | 122.525 | -0.091553 | 122.5113 | 60.6262 | -0.25177 | 122.525 | -0.091553 | 60.6262 | 122.1863 | 122.5113 | -122.8455 | -122.7951
978.9062 | 122.818 | -60.6537 | 61.8668 | 0.21011 | 0.0040846 | 0.0051632 | -0.0022943 | 0.063175 | -0.0017881 | 0.067926 | -60.7452 | 61.7981 | -60.9695 | -60.8505 | 61.5417 | -0.036621 | -0.16479 | 0.13733 | 61.821 | -60.9558 | -0.31586 | -0.068664 | -0.091552 | -0.19684 | -0.32501 | -0.30212 | -0.045776 | 0.2243 | 60.4889 | 60.791 | 122.1954 | 122.4518 | -0.091552 | 122.4747 | 60.6171 | -0.30212 | 122.4518 | -0.091552 | 60.6171 | 122.1954 | 122.4747 | -122.8363 | -122.8226
979.9688 | 122.7997 | -60.6766 | 61.853 | 0.17197 | 0.0025892 | 0.0015316 | 0.0009101 | 0.062534 | -0.00071986 | 0.067285 | -60.7361 | 61.8118 | -60.9375 | -60.8322 | 61.5463 | -0.032043 | -0.1831 | 0.12817 | 61.8073 | -60.9604 | -0.26093 | -0.041198 | -0.059509 | -0.15564 | -0.3067 | -0.28381 | -0.045776 | 0.20142 | 60.4935 | 60.8047 | 122.2229 | 122.4884 | -0.059509 | 122.4838 | 60.6445 | -0.28381 | 122.4884 | -0.059509 | 60.6445 | 122.2229 | 122.4838 | -122.7905 | -122.8134
980.9062 | 122.8409 | -60.64 | 61.8347 | 0.15671 | 0.0040846 | 0.0049496 | 0.0021917 | 0.065311 | -0.0017881 | 0.065576 | -60.7132 | 61.8347 | -60.9467 | -60.8002 | 61.5692 | -0.022888 | -0.21973 | 0.12817 | 61.8073 | -60.9421 | -0.3067 | 0 | -0.073242 | -0.16022 | -0.2655 | -0.30212 | -0.027466 | 0.23346 | 60.4202 | 60.7681 | 122.2092 | 122.4747 | -0.073242 | 122.4472 | 60.6171 | -0.30212 | 122.4747 | -0.073242 | 60.6171 | 122.2092 | 122.4472 | -122.7814 | -122.7768
981.9531 | 122.731 | -60.6857 | 61.8851 | 0.233 | 0.0030164 | 0.0043088 | 0.0049689 | 0.065097 | -0.00029266 | 0.067712 | -60.791 | 61.8668 | -60.9924 | -60.9055 | 61.4456 | -0.11444 | -0.086975 | 0.032043 | 61.8576 | -60.9741 | -0.3067 | -0.018311 | -0.10529 | -0.21973 | -0.43945 | -0.28839 | -0.027466 | 0.20142 | 60.5988 | 60.7178 | 122.1313 | 122.5525 | -0.10529 | 122.5433 | 60.5713 | -0.28839 | 122.5525 | -0.10529 | 60.5713 | 122.1313 | 122.5433 | -122.8775 | -122.8592
982.9062 | 122.8363 | -60.6674 | 61.821 | 0.16434 | 0.0017346 | 0.0096494 | 0.0004827 | 0.063175 | -0.00071986 | 0.065362 | -60.7498 | 61.7661 | -60.9421 | -60.8414 | 61.5417 | 0.041199 | -0.21057 | 0.15106 | 61.7981 | -60.9833 | -0.27466 | -0.054932 | -0.082398 | -0.17395 | -0.27924 | -0.31586 | -0.022888 | 0.19226 | 60.4568 | 60.8185 | 122.2092 | 122.4335 | -0.082398 | 122.4655 | 60.7086 | -0.31586 | 122.4335 | -0.082398 | 60.7086 | 122.2092 | 122.4655 | -122.7631 | -122.8043
983.9688 | 122.731 | -60.6949 | 61.8988 | -0.12558 | 0.0047254 | 0.0049496 | 0.0039007 | 0.064029 | -0.0015745 | 0.067498 | -60.7773 | 61.8942 | -60.9924 | -60.8917 | 61.496 | 0.009155 | 0.082397 | 0.15564 | 61.8484 | -61.0016 | -0.29755 | -0.004578 | -0.082398 | -0.19684 | -0.40283 | -0.3067 | -0.050354 | 0.21515 | 60.7773 | 60.8505 | 122.1909 | 122.5891 | -0.082398 | 122.5433 | 60.704 | -0.3067 | 122.5891 | -0.082398 | 60.704 | 122.1909 | 122.5433 | -122.8912 | -122.9004
984.9062 | 122.8134 | -60.6857 | 61.8393 | -0.018768 | 0.00023916 | 0.0025998 | -0.0037897 | 0.064243 | -0.0022153 | 0.067712 | -60.7864 | 61.7615 | -60.9924 | -60.8368 | 61.5326 | 0.091553 | -0.11444 | 0.21057 | 61.8118 | -60.9375 | -0.3067 | -0.077819 | -0.10071 | -0.15106 | -0.3067 | -0.25177 | -0.027465 | 0.20599 | 60.5713 | 60.8963 | 122.2183 | 122.4472 | -0.10071 | 122.4976 | 60.7773 | -0.25177 | 122.4472 | -0.10071 | 60.7773 | 122.2183 | 122.4976 | -122.8317 | -122.7768
985.9062 | 122.8683 | -60.6903 | 61.853 | 0.15671 | 0.0060072 | 0.004736 | -0.0001581 | 0.063175 | -0.0015745 | 0.06878 | -60.7269 | 61.7889 | -60.9879 | -60.8459 | 61.5143 | 0.032043 | -0.2243 | 0.15106 | 61.7752 | -60.9879 | -0.29755 | -0.064087 | -0.036621 | -0.15564 | -0.33874 | -0.29755 | -0.077819 | 0.26093 | 60.466 | 60.8414 | 122.2046 | 122.4792 | -0.036621 | 122.4655 | 60.7224 | -0.29755 | 122.4792 | -0.036621 | 60.7224 | 122.2046 | 122.4655 | -122.8409 | -122.8409
986.9531 | 122.7493 | -60.6857 | 61.8988 | -0.11795 | 0.004939 | 0.0072996 | 0.0062507 | 0.062747 | -0.0032835 | 0.065789 | -60.7269 | 61.8851 | -60.9879 | -60.8505 | 61.496 | -0.027466 | -0.10071 | 0.17395 | 61.8347 | -61.0153 | -0.30212 | -0.013733 | -0.041199 | -0.16479 | -0.40283 | -0.32959 | -0.064087 | 0.26093 | 60.585 | 60.8597 | 122.1817 | 122.5708 | -0.041199 | 122.5204 | 60.6583 | -0.32959 | 122.5708 | -0.041199 | 60.6583 | 122.1817 | 122.5204 | -122.8867 | -122.9141
987.9062 | 122.8546 | -60.672 | 61.853 | 0.21011 | 0.0025892 | 0.005377 | 0.0021917 | 0.064456 | 0.00056194 | 0.066217 | -60.7407 | 61.7935 | -60.9695 | -60.8459 | 61.6379 | 0.20599 | -0.25635 | 0.10986 | 61.7889 | -60.9375 | -0.29755 | -0.059509 | -0.068665 | -0.17395 | -0.21515 | -0.2655 | -0.064087 | 0.22888 | 60.4156 | 60.7819 | 122.3099 | 122.4655 | -0.068665 | 122.4609 | 60.878 | -0.2655 | 122.4655 | -0.068665 | 60.878 | 122.3099 | 122.4609 | -122.8226 | -122.7905
988.9531 | 122.7676 | -60.6995 | 61.8896 | -0.079803 | 0.004939 | 0.0062314 | 0.0064643 | 0.06467 | -0.0032835 | 0.067285 | -60.6903 | 61.8713 | -60.9879 | -60.8185 | 61.5143 | 0.036621 | -0.027466 | 0.13733 | 61.8576 | -60.9695 | -0.28839 | -0.01831 | 0.009155 | -0.11902 | -0.37537 | -0.27008 | -0.032043 | 0.29755 | 60.672 | 60.8368 | 122.2137 | 122.5708 | 0.009155 | 122.5571 | 60.7361 | -0.27008 | 122.5708 | 0.009155 | 60.7361 | 122.2137 | 122.5571 | -122.8775 | -122.8592
989.9062 | 122.8592 | -60.6766 | 61.853 | -0.041657 | 0.0017346 | 0.0025998 | -0.0037897 | 0.064243 | -0.0011471 | 0.067926 | -60.7681 | 61.7935 | -60.9512 | -60.8322 | 61.5601 | 0.09613 | -0.11902 | 0.23346 | 61.821 | -60.9192 | -0.27466 | -0.059509 | -0.091552 | -0.15564 | -0.29297 | -0.24261 | -0.032043 | 0.18311 | 60.5576 | 60.91 | 122.2366 | 122.4701 | -0.091552 | 122.4976 | 60.7727 | -0.24261 | 122.4701 | -0.091552 | 60.7727 | 122.2366 | 122.4976 | -122.8043 | -122.7722
990.9531 | 122.8592 | -60.672 | 61.8347 | 0.20248 | 0.004939 | 0.004736 | 0.0034735 | 0.065097 | -0.0022153 | 0.067285 | -60.9009 | 61.8027 | -60.9787 | -60.8002 | 61.5372 | 0.036621 | -0.23804 | 0.15564 | 61.7752 | -61.0062 | -0.3067 | -0.032044 | -0.22888 | -0.12817 | -0.29755 | -0.33417 | -0.059509 | 0.07782 | 60.434 | 60.8276 | 122.2092 | 122.4747 | -0.22888 | 122.4472 | 60.7086 | -0.33417 | 122.4747 | -0.22888 | 60.7086 | 122.2092 | 122.4472 | -122.8134 | -122.8409
991.9062 | 122.7997 | -60.7086 | 61.8439 | 0.27115 | 0.0040846 | 0.0083676 | 0.0030463 | 0.066165 | -0.00050626 | 0.066644 | -60.7773 | 61.8668 | -60.997 | -60.8734 | 61.4868 | -0.004578 | -0.19226 | 0.091553 | 61.8118 | -60.9787 | -0.28839 | 0.022888 | -0.068665 | -0.16479 | -0.35706 | -0.27008 | -0.032043 | 0.21973 | 60.5164 | 60.8002 | 122.1954 | 122.5754 | -0.068665 | 122.5204 | 60.704 | -0.27008 | 122.5754 | -0.068665 | 60.704 | 122.1954 | 122.5204 | -122.8409 | -122.8226
992.9531 | 122.7631 | -60.6857 | 61.8439 | 0.18723 | 0.0062208 | 0.0083676 | 0.0045417 | 0.064884 | -0.0011471 | 0.068994 | -60.791 | 61.8805 | -61.0016 | -60.9192 | 61.4456 | -0.041199 | -0.15106 | 0.064087 | 61.8301 | -60.9924 | -0.31586 | 0.036621 | -0.10529 | -0.23346 | -0.39825 | -0.3067 | -0.013733 | 0.21057 | 60.5347 | 60.7498 | 122.1313 | 122.5662 | -0.10529 | 122.5159 | 60.6445 | -0.3067 | 122.5662 | -0.10529 | 60.6445 | 122.1313 | 122.5159 | -122.8455 | -122.8363
993.9062 | 122.8409 | -60.672 | 61.7889 | 0.29404 | 0.0034436 | 0.0068722 | 0.0039007 | 0.065738 | -0.0011471 | 0.068567 | -60.7361 | 61.8439 | -60.9787 | -60.8505 | 61.496 | 0.018311 | -0.21057 | 0.14191 | 61.7935 | -60.9833 | -0.3067 | 0.054932 | -0.064087 | -0.17853 | -0.29297 | -0.31128 | 0.004578 | 0.24262 | 60.4614 | 60.8139 | 122.168 | 122.5159 | -0.064087 | 122.4655 | 60.6903 | -0.31128 | 122.5159 | -0.064087 | 60.6903 | 122.168 | 122.4655 | -122.7676 | -122.7722
994.9531 | 122.7264 | -60.6949 | 61.8942 | 0.14908 | 0.0070752 | 0.004736 | 0.0026191 | 0.066165 | -0.0026425 | 0.067498 | -60.8047 | 61.8851 | -61.0016 | -60.9238 | 61.4365 | -0.045776 | -0.086975 | 0.004578 | 61.8713 | -60.9879 | -0.3067 | -0.009155 | -0.10986 | -0.22888 | -0.45776 | -0.29297 | -0.022888 | 0.19684 | 60.6079 | 60.6995 | 122.1313 | 122.58 | -0.10986 | 122.5662 | 60.6491 | -0.29297 | 122.58 | -0.10986 | 60.6491 | 122.1313 | 122.5662 | -122.8958 | -122.8821
995.9062 | 122.8043 | -60.6537 | 61.8484 | 0.18723 | 0.0040846 | 0.0058042 | 0.0006965 | 0.065738 | -0.0015745 | 0.069848 | -60.704 | 61.8622 | -60.9467 | -60.759 | 61.4227 | -0.13733 | -0.14191 | 0.29755 | 61.8301 | -60.9604 | -0.29297 | 0.013733 | -0.050354 | -0.10529 | -0.42572 | -0.3067 | -0.018311 | 0.24261 | 60.5118 | 60.9512 | 122.0764 | 122.5159 | -0.050354 | 122.4838 | 60.5164 | -0.3067 | 122.5159 | -0.050354 | 60.5164 | 122.0764 | 122.4838 | -122.7951 | -122.8088
996.9688 | 122.6898 | -60.6857 | 61.8484 | 0.095673 | 0.0062208 | 0.012854 | 0.0049689 | 0.065952 | -0.00050626 | 0.067285 | -60.8047 | 61.9034 | -61.0016 | -60.9329 | 61.4227 | -0.091553 | -0.013733 | -0.013733 | 61.8759 | -61.0062 | -0.31586 | 0.054931 | -0.11902 | -0.24719 | -0.42572 | -0.32044 | 0.027466 | 0.19684 | 60.672 | 60.672 | 122.1085 | 122.5891 | -0.11902 | 122.5616 | 60.5942 | -0.32044 | 122.5891 | -0.11902 | 60.5942 | 122.1085 | 122.5616 | -122.85 | -122.8546
997.9062 | 122.7219 | -60.7178 | 61.8713 | 0.17197 | 0.0040846 | 0.011145 | 0.0039007 | 0.067661 | -0.0022153 | 0.069848 | -60.7773 | 61.9171 | -61.0016 | -60.9146 | 61.4319 | -0.054932 | -0.09613 | 0.022888 | 61.8851 | -60.9879 | -0.28381 | 0.045776 | -0.05951 | -0.19684 | -0.43945 | -0.27008 | 0.013733 | 0.2243 | 60.6216 | 60.7407 | 122.1497 | 122.6349 | -0.05951 | 122.6028 | 60.6628 | -0.27008 | 122.6349 | -0.05951 | 60.6628 | 122.1497 | 122.6028 | -122.8729 | -122.8592
998.9688 | 122.7631 | -60.6857 | 61.9125 | -0.17136 | 0.0057934 | 0.011145 | 0.0024053 | 0.065952 | -0.0024289 | 0.06643 | -60.7269 | 61.9537 | -60.9695 | -60.8597 | 61.5097 | 0.050354 | 0.022888 | 0.13733 | 61.9217 | -60.9604 | -0.28381 | 0.041198 | -0.041199 | -0.17395 | -0.40283 | -0.27466 | 0.009155 | 0.24261 | 60.7086 | 60.8231 | 122.1954 | 122.6395 | -0.041199 | 122.6074 | 60.7361 | -0.27466 | 122.6395 | -0.041199 | 60.7361 | 122.1954 | 122.6074 | -122.8821 | -122.8729
999.9062 | 122.8592 | -60.6216 | 61.8713 | 0.24063 | 0.0030164 | 0.0040952 | -0.0020807 | 0.064884 | -0.00071986 | 0.067926 | -60.7132 | 61.8301 | -60.9283 | -60.8231 | 61.5646 | 0.050354 | -0.24719 | 0.13733 | 61.8393 | -60.9512 | -0.3067 | -0.041199 | -0.091553 | -0.20142 | -0.3067 | -0.32959 | -0.032044 | 0.21515 | 60.3745 | 60.759 | 122.1863 | 122.4518 | -0.091553 | 122.4609 | 60.672 | -0.32959 | 122.4518 | -0.091553 | 60.672 | 122.1863 | 122.4609 | -122.7997 | -122.8226
1000.9531 | 122.7585 | -60.6491 | 61.9263 | -0.12558 | 0.0060072 | 0.0083676 | 0.0053961 | 0.064456 | -0.0020017 | 0.068994 | -60.6857 | 61.9263 | -60.91 | -60.8231 | 61.528 | 0.027466 | -0.036621 | 0.10986 | 61.8988 | -60.965 | -0.26093 | 0 | -0.036621 | -0.17395 | -0.39825 | -0.31586 | -0.027466 | 0.2243 | 60.6125 | 60.759 | 122.1771 | 122.5754 | -0.036621 | 122.5479 | 60.6766 | -0.31586 | 122.5754 | -0.036621 | 60.6766 | 122.1771 | 122.5479 | -122.8363 | -122.8912
1001.9062 | 122.8271 | -60.6583 | 61.8851 | 0.20248 | 0.0079298 | 0.0068722 | 0.0006965 | 0.066806 | -0.0015745 | 0.06878 | -60.7224 | 61.9034 | -60.9421 | -60.8368 | 61.5051 | 0.004578 | -0.19684 | 0.068665 | 61.9034 | -60.9604 | -0.28381 | 0.01831 | -0.064087 | -0.17853 | -0.37994 | -0.30212 | 0.01831 | 0.21973 | 60.4614 | 60.7269 | 122.1634 | 122.5616 | -0.064087 | 122.5616 | 60.6628 | -0.30212 | 122.5616 | -0.064087 | 60.6628 | 122.1634 | 122.5616 | -122.8271 | -122.8455
1002.9531 | 122.7173 | -60.6812 | 61.9034 | 0.027008 | 0.0062208 | 0.0092222 | 0.0021917 | 0.066593 | -0.0011471 | 0.068567 | -60.7681 | 61.9629 | -60.9329 | -60.8871 | 61.4365 | -0.091553 | -0.032043 | 0.018311 | 61.9125 | -60.9741 | -0.25177 | 0.05951 | -0.086975 | -0.20599 | -0.46692 | -0.29297 | 0.009156 | 0.16479 | 60.6491 | 60.6995 | 122.1176 | 122.644 | -0.086975 | 122.5937 | 60.5896 | -0.29297 | 122.644 | -0.086975 | 60.5896 | 122.1176 | 122.5937 | -122.8363 | -122.8775
1003.9062 | 122.7585 | -60.6354 | 61.9354 | 0.1796 | 0.0042982 | 0.0043088 | 0.0094549 | 0.064456 | -0.0045651 | 0.068567 | -60.7636 | 61.9949 | -60.9695 | -60.8139 | 61.3907 | -0.15564 | 0.045776 | 0.013733 | 61.9675 | -60.965 | -0.33417 | 0.059509 | -0.12817 | -0.17853 | -0.54474 | -0.32959 | 0.032043 | 0.20599 | 60.6812 | 60.6491 | 122.0261 | 122.6303 | -0.12817 | 122.6028 | 60.4797 | -0.32959 | 122.6303 | -0.12817 | 60.4797 | 122.0261 | 122.6028 | -122.905 | -122.9004
1004.9531 | 122.6166 | -60.6537 | 61.8896 | 0.11856 | 0.0081434 | 0.0058042 | 0.0030463 | 0.066593 | -0.0026425 | 0.068567 | -60.7498 | 61.9949 | -60.8963 | -60.8963 | 61.4777 | -0.11444 | -0.086975 | -0.004578 | 61.9949 | -60.9421 | -0.24261 | 0.10529 | -0.09613 | -0.24261 | -0.41199 | -0.28839 | 0.10529 | 0.14648 | 60.5667 | 60.6491 | 122.1313 | 122.6486 | -0.09613 | 122.6486 | 60.5392 | -0.28839 | 122.6486 | -0.09613 | 60.5392 | 122.1313 | 122.6486 | -122.7859 | -122.8317
1005.9062 | 122.7264 | -60.6491 | 61.9583 | 0.080414 | 0.0064344 | 0.0096494 | 0.0053961 | 0.067234 | -0.0032835 | 0.068353 | -60.7315 | 62.0041 | -60.9238 | -60.878 | 61.4731 | -0.18768 | -0.050354 | -0.013733 | 61.9583 | -60.9467 | -0.27466 | 0.045776 | -0.082397 | -0.22888 | -0.48523 | -0.29755 | 0 | 0.19226 | 60.5988 | 60.6354 | 122.1222 | 122.6532 | -0.082397 | 122.6074 | 60.4614 | -0.29755 | 122.6532 | -0.082397 | 60.4614 | 122.1222 | 122.6074 | -122.8821 | -122.905
1006.9688 | 122.8226 | -60.585 | 61.9034 | -0.20187 | 0.0034436 | 0.0079404 | -0.0035761 | 0.066806 | 0.0014163 | 0.067926 | -60.6308 | 61.9308 | -60.8826 | -60.7361 | 61.6379 | -0.1236 | 0.35248 | 0.41657 | 61.9904 | -60.8597 | -0.29755 | 0.027466 | -0.045776 | -0.15106 | -0.2655 | -0.27466 | 0.086975 | 0.25177 | 60.9375 | 61.0016 | 122.2229 | 122.5159 | -0.045776 | 122.5754 | 60.4614 | -0.27466 | 122.5159 | -0.045776 | 60.4614 | 122.2229 | 122.5754 | -122.7859 | -122.7631
1007.9062 | 122.7539 | -60.6445 | 61.9492 | 0.18723 | 0.0055798 | 0.0058042 | 0.0034735 | 0.065097 | -0.00093346 | 0.065149 | -60.7361 | 62.0041 | -60.9283 | -60.8688 | 61.4914 | -0.19226 | -0.13733 | 0.013733 | 61.9034 | -60.9695 | -0.28381 | 0.054931 | -0.091553 | -0.2243 | -0.45776 | -0.32501 | -0.045777 | 0.19226 | 60.5072 | 60.6583 | 122.1359 | 122.6486 | -0.091553 | 122.5479 | 60.4523 | -0.32501 | 122.6486 | -0.091553 | 60.4523 | 122.1359 | 122.5479 | -122.8775 | -122.9187
1008.9531 | 122.7493 | -60.6308 | 61.9537 | -0.17899 | 0.0036572 | 0.006445 | 0.0047553 | 0.067234 | -0.0017881 | 0.067712 | -60.672 | 61.9766 | -60.9329 | -60.8093 | 61.5234 | -0.09613 | -0.032043 | 0.14648 | 61.94 | -60.9467 | -0.30212 | 0.022889 | -0.041199 | -0.17853 | -0.4303 | -0.31586 | -0.013733 | 0.26093 | 60.5988 | 60.7773 | 122.1542 | 122.6074 | -0.041199 | 122.5708 | 60.5347 | -0.31586 | 122.6074 | -0.041199 | 60.5347 | 122.1542 | 122.5708 | -122.8867 | -122.9004
1009.9062 | 122.8317 | -60.6445 | 61.8668 | 0.11856 | 0.0023756 | 0.0062314 | -0.0018671 | 0.066593 | -0.00029266 | 0.068353 | -60.7132 | 61.853 | -60.9558 | -60.8368 | 61.5555 | -0.091553 | -0.23804 | 0.14191 | 61.8805 | -60.9421 | -0.31128 | -0.013733 | -0.068665 | -0.19226 | -0.31128 | -0.29755 | 0.013733 | 0.24261 | 60.4065 | 60.7864 | 122.2 | 122.4976 | -0.068665 | 122.525 | 60.553 | -0.29755 | 122.4976 | -0.068665 | 60.553 | 122.2 | 122.525 | -122.8226 | -122.8088
1010.9531 | 122.7631 | -60.6674 | 61.9125 | -0.17899 | 0.0047254 | 0.006445 | 0.0039007 | 0.064243 | -0.0013609 | 0.066858 | -60.6903 | 62.0041 | -60.91 | -60.8139 | 61.5189 | -0.10071 | -0.022888 | 0.15106 | 61.9446 | -60.9833 | -0.24262 | 0.091552 | -0.022889 | -0.14648 | -0.39368 | -0.31586 | 0.032043 | 0.21973 | 60.6445 | 60.8185 | 122.1863 | 122.6715 | -0.022889 | 122.612 | 60.5667 | -0.31586 | 122.6715 | -0.022889 | 60.5667 | 122.1863 | 122.612 | -122.8226 | -122.8958
1011.9062 | 122.7264 | -60.6491 | 61.9308 | 0.065155 | 0.0064344 | 0.0068722 | 0.0032599 | 0.066165 | -0.0028561 | 0.069421 | -60.7224 | 61.9858 | -60.9192 | -60.878 | 61.4456 | -0.2243 | -0.054932 | 0.013733 | 61.9263 | -60.9741 | -0.27008 | 0.054932 | -0.073242 | -0.22888 | -0.48523 | -0.32501 | -0.004577 | 0.19684 | 60.5942 | 60.6628 | 122.0947 | 122.6349 | -0.073242 | 122.5754 | 60.4248 | -0.32501 | 122.6349 | -0.073242 | 60.4248 | 122.0947 | 122.5754 | -122.85 | -122.905
1012.9531 | 122.7676 | -60.6628 | 61.9354 | -0.23239 | 0.0034436 | 0.0072996 | 0.0026191 | 0.067234 | -0.00093346 | 0.067498 | -60.7315 | 61.9858 | -60.9604 | -60.8505 | 61.5005 | -0.18768 | -0.013733 | 0.15106 | 61.9492 | -60.9695 | -0.29755 | 0.050354 | -0.068664 | -0.18768 | -0.43488 | -0.3067 | 0.013733 | 0.22888 | 60.6491 | 60.8139 | 122.1634 | 122.6486 | -0.068664 | 122.612 | 60.4752 | -0.3067 | 122.6486 | -0.068664 | 60.4752 | 122.1634 | 122.612 | -122.8958 | -122.905
1013.9062 | 122.7631 | -60.64 | 61.9446 | 0.027008 | 0.0062208 | 0.0079404 | 0.0021917 | 0.067661 | -0.00071986 | 0.069848 | -60.6949 | 61.9675 | -60.9283 | -60.8459 | 61.4777 | -0.32044 | -0.054932 | 0.064087 | 61.9675 | -60.9695 | -0.28839 | 0.022888 | -0.054931 | -0.20599 | -0.46692 | -0.32959 | 0.022888 | 0.23346 | 60.585 | 60.704 | 122.1176 | 122.6074 | -0.054931 | 122.6074 | 60.3195 | -0.32959 | 122.6074 | -0.054931 | 60.3195 | 122.1176 | 122.6074 | -122.8729 | -122.9141
1014.9531 | 122.7814 | -60.64 | 61.972 | -0.16373 | 0.0045118 | 0.0060178 | 0.0015509 | 0.068729 | -0.0011471 | 0.069207 | -60.64 | 61.9858 | -60.9055 | -60.791 | 61.5372 | -0.3067 | -0.064087 | 0.16022 | 61.972 | -60.9192 | -0.2655 | 0.013733 | 0 | -0.15106 | -0.43488 | -0.27923 | 0 | 0.2655 | 60.5759 | 60.8002 | 122.1771 | 122.6257 | 0 | 122.612 | 60.3333 | -0.27923 | 122.6257 | 0 | 60.3333 | 122.1771 | 122.612 | -122.8775 | -122.8912
1015.9062 | 122.7264 | -60.6766 | 61.9492 | -1.7812 | 0.0055798 | 0.0096494 | 0.0026191 | 0.066806 | -7.9062e-05 | 0.067926 | -60.7498 | 62.0041 | -60.9009 | -60.8734 | 61.4548 | -0.49439 | -0.064087 | 0.013733 | 61.9949 | -60.9512 | -0.2243 | 0.054931 | -0.073242 | -0.19684 | -0.49438 | -0.27466 | 0.045776 | 0.15106 | 60.6125 | 60.6903 | 122.1313 | 122.6807 | -0.073242 | 122.6715 | 60.1822 | -0.27466 | 122.6807 | -0.073242 | 60.1822 | 122.1313 | 122.6715 | -122.85 | -122.9004
1016.9688 | 122.7493 | -60.5988 | 61.9675 | 1.0493 | 0.0070752 | 0.0077268 | 0.0032599 | 0.066165 | -0.0032835 | 0.069421 | -60.585 | 61.9858 | -60.91 | -60.7819 | 61.5784 | -0.39825 | -0.091553 | 0.14648 | 61.9949 | -60.9055 | -0.31128 | 0.018311 | 0.013733 | -0.18311 | -0.3891 | -0.3067 | 0.027466 | 0.32501 | 60.5072 | 60.7452 | 122.1771 | 122.5845 | 0.013733 | 122.5937 | 60.2005 | -0.3067 | 122.5845 | 0.013733 | 60.2005 | 122.1771 | 122.5937 | -122.8775 | -122.8729
1017.9062 | 122.7127 | -60.6308 | 61.94 | 0.1033 | 0.004939 | 0.006445 | 0.0034735 | 0.066593 | -0.0022153 | 0.068567 | -60.6995 | 61.9766 | -60.91 | -60.878 | 61.4685 | -0.52643 | -0.086975 | 0.036621 | 61.9492 | -60.9741 | -0.27924 | 0.036622 | -0.068665 | -0.24719 | -0.4715 | -0.34332 | 0.009156 | 0.21057 | 60.5438 | 60.6674 | 122.0993 | 122.6074 | -0.068665 | 122.58 | 60.1044 | -0.34332 | 122.6074 | -0.068665 | 60.1044 | 122.0993 | 122.58 | -122.85 | -122.9141
1018.9688 | 122.7493 | -60.6079 | 61.9812 | -0.11032 | 0.0040846 | 0.01029 | 0.0021917 | 0.068088 | -0.0024289 | 0.065362 | -60.6537 | 62.0407 | -60.9055 | -60.7956 | 61.5555 | -0.46234 | -0.027466 | 0.14191 | 61.9949 | -60.9283 | -0.29755 | 0.059509 | -0.045777 | -0.18768 | -0.42572 | -0.32044 | 0.013733 | 0.25177 | 60.5804 | 60.7498 | 122.1634 | 122.6486 | -0.045777 | 122.6028 | 60.1456 | -0.32044 | 122.6486 | -0.045777 | 60.1456 | 122.1634 | 122.6028 | -122.8867 | -122.9095
1019.9062 | 122.8226 | -60.5896 | 61.9217 | 0.24063 | 0.002162 | 0.0055906 | -0.0025079 | 0.066593 | -0.0013609 | 0.066644 | -60.6583 | 61.9125 | -60.9055 | -60.791 | 61.5646 | -0.49439 | -0.27008 | 0.14191 | 61.9217 | -60.8643 | -0.31586 | -0.009155 | -0.068664 | -0.20142 | -0.35706 | -0.27466 | 0 | 0.24719 | 60.3195 | 60.7315 | 122.1542 | 122.5021 | -0.068664 | 122.5113 | 60.0952 | -0.27466 | 122.5021 | -0.068664 | 60.0952 | 122.1542 | 122.5113 | -122.8271 | -122.7859
1020.9531 | 122.7631 | -60.6125 | 62.0087 | -0.16373 | 0.0070752 | 0.004736 | 0.0013373 | 0.067661 | 0.00098914 | 0.067071 | -60.6812 | 62.0361 | -60.8871 | -60.8002 | 61.5372 | -0.53558 | 0.013733 | 0.14191 | 62.0178 | -60.9329 | -0.27466 | 0.027466 | -0.068664 | -0.18768 | -0.4715 | -0.32043 | 0.009155 | 0.20599 | 60.6262 | 60.7544 | 122.1497 | 122.6486 | -0.068664 | 122.6303 | 60.0769 | -0.32043 | 122.6486 | -0.068664 | 60.0769 | 122.1497 | 122.6303 | -122.8958 | -122.9416
1021.9062 | 122.731 | -60.6125 | 61.9583 | -2.6814 | 0.0053662 | 0.011358 | 0.0030463 | 0.068088 | -0.00093346 | 0.069848 | -60.6583 | 62.0224 | -60.9238 | -60.8597 | 61.4639 | -0.75989 | -0.086975 | 0.027466 | 61.9629 | -60.9375 | -0.31128 | 0.064087 | -0.045776 | -0.24719 | -0.49438 | -0.32501 | 0.004578 | 0.2655 | 60.5255 | 60.64 | 122.0764 | 122.6349 | -0.045776 | 122.5754 | 59.8526 | -0.32501 | 122.6349 | -0.045776 | 59.8526 | 122.0764 | 122.5754 | -122.8821 | -122.8958
1022.9688 | 122.7722 | -60.585 | 61.9766 | -0.1561 | 0.00323 | 0.0060178 | 0.0026191 | 0.066379 | -0.00029266 | 0.067285 | -60.6216 | 62.0087 | -60.8826 | -60.7681 | 61.5646 | -0.75989 | -0.022888 | 0.15564 | 62.0087 | -60.878 | -0.29755 | 0.032043 | -0.036621 | -0.1831 | -0.41199 | -0.29297 | 0.032043 | 0.26093 | 60.5621 | 60.7407 | 122.1497 | 122.5937 | -0.036621 | 122.5937 | 59.8251 | -0.29297 | 122.5937 | -0.036621 | 59.8251 | 122.1497 | 122.5937 | -122.8592 | -122.8546
1023.9062 | 122.731 | -60.6216 | 61.9904 | -0.011139 | 0.0064344 | 0.0058042 | 0.0039007 | 0.066165 | -0.0024289 | 0.070062 | -60.6674 | 62.0361 | -60.9192 | -60.8322 | 61.4822 | -0.91553 | -0.07782 | 0.045776 | 61.9949 | -60.9283 | -0.29755 | 0.045777 | -0.045776 | -0.21057 | -0.50812 | -0.3067 | 0.004578 | 0.25177 | 60.5438 | 60.6674 | 122.1039 | 122.6578 | -0.045776 | 122.6166 | 59.7061 | -0.3067 | 122.6578 | -0.045776 | 59.7061 | 122.1039 | 122.6166 | -122.9095 | -122.9187
1024.9531 | 122.7264 | -60.585 | 62.0041 | 0.049896 | 0.0068616 | 0.0055906 | 0.0045417 | 0.065952 | -0.0015745 | 0.066217 | -60.6491 | 62.0178 | -60.91 | -60.8002 | 61.5234 | -0.93384 | -0.086975 | 0.045776 | 62.0178 | -60.9192 | -0.32501 | 0.013733 | -0.064087 | -0.21515 | -0.48065 | -0.33417 | 0.013733 | 0.26093 | 60.498 | 60.6308 | 122.1085 | 122.6028 | -0.064087 | 122.6028 | 59.6512 | -0.33417 | 122.6028 | -0.064087 | 59.6512 | 122.1085 | 122.6028 | -122.9141 | -122.9233
1025.9062 | 122.731 | -60.5804 | 61.9812 | 0.049896 | 0.0042982 | 0.009863 | 0.0013373 | 0.066165 | -0.0013609 | 0.067712 | -60.6125 | 62.0453 | -60.8505 | -60.7956 | 61.528 | -0.83771 | -0.054932 | 0.068665 | 62.0224 | -60.8826 | -0.27008 | 0.064087 | -0.032044 | -0.21515 | -0.45319 | -0.30212 | 0.041199 | 0.23804 | 60.5255 | 60.6491 | 122.1085 | 122.6257 | -0.032044 | 122.6028 | 59.7427 | -0.30212 | 122.6257 | -0.032044 | 59.7427 | 122.1085 | 122.6028 | -122.8317 | -122.8638
1026.9531 | 122.7722 | -60.5896 | 61.9904 | -0.17136 | 0.0036572 | 0.0092222 | 0.0034735 | 0.068943 | -0.0022153 | 0.068353 | -60.6354 | 62.0407 | -60.878 | -60.7956 | 61.5417 | -0.65918 | -0.027466 | 0.15564 | 62.0041 | -60.9192 | -0.28839 | 0.050354 | -0.045776 | -0.20599 | -0.44861 | -0.32959 | 0.013733 | 0.24262 | 60.5621 | 60.7452 | 122.1313 | 122.6303 | -0.045776 | 122.5937 | 59.9304 | -0.32959 | 122.6303 | -0.045776 | 59.9304 | 122.1313 | 122.5937 | -122.8683 | -122.9095
1027.9062 | 122.7081 | -60.6171 | 61.9766 | 0.042267 | 0.0030164 | 0.011786 | 0.0013373 | 0.06702 | -0.0020017 | 0.067071 | -60.6903 | 62.0224 | -60.8963 | -60.8368 | 61.4822 | -0.72784 | -0.059509 | 0.013733 | 61.9904 | -60.91 | -0.27924 | 0.045776 | -0.073243 | -0.21973 | -0.49439 | -0.29297 | 0.013732 | 0.20599 | 60.5576 | 60.6308 | 122.0993 | 122.6395 | -0.073243 | 122.6074 | 59.8892 | -0.29297 | 122.6395 | -0.073243 | 59.8892 | 122.0993 | 122.6074 | -122.8729 | -122.8867
1028.9688 | 122.8455 | -60.5713 | 61.94 | 0.19485 | 0.00323 | 0.005377 | 0.0034735 | 0.067874 | -0.00050626 | 0.068994 | -60.6216 | 61.9034 | -60.878 | -60.5942 | 61.647 | -0.64087 | -0.2655 | 0.16022 | 61.9446 | -60.8643 | -0.3067 | -0.036621 | -0.050354 | -0.022888 | -0.29297 | -0.29297 | 0.004578 | 0.25635 | 60.3058 | 60.7315 | 122.2183 | 122.4747 | -0.050354 | 122.5159 | 59.9304 | -0.29297 | 122.4747 | -0.050354 | 59.9304 | 122.2183 | 122.5159 | -122.818 | -122.8043
1029.9219 | 122.7722 | -60.5804 | 61.9537 | 0.042267 | 0.0010938 | 0.0038816 | -0.0080621 | 0.064243 | -0.00029266 | 0.068567 | -60.6949 | 61.9171 | -60.8963 | -60.8276 | 61.5875 | -0.58136 | -0.17395 | 0.1236 | 61.9629 | -60.8505 | -0.31586 | -0.036621 | -0.11444 | -0.24719 | -0.36621 | -0.27008 | 0.009156 | 0.20142 | 60.4065 | 60.704 | 122.168 | 122.4976 | -0.11444 | 122.5433 | 59.9991 | -0.27008 | 122.4976 | -0.11444 | 59.9991 | 122.168 | 122.5433 | -122.85 | -122.8043
1030.9531 | 122.7448 | -60.6125 | 62.0316 | -0.25528 | 0.006648 | 0.0087948 | 0.0011237 | 0.063175 | -7.9062e-05 | 0.068353 | -60.6628 | 62.0041 | -60.8551 | -60.8139 | 61.5601 | -0.36621 | 0.068665 | -0.059509 | 62.0453 | -60.9238 | -0.24262 | -0.027466 | -0.050354 | -0.20142 | -0.4715 | -0.31128 | 0.013733 | 0.19226 | 60.6812 | 60.553 | 122.1725 | 122.6166 | -0.050354 | 122.6578 | 60.2463 | -0.31128 | 122.6166 | -0.050354 | 60.2463 | 122.1725 | 122.6578 | -122.8867 | -122.9553
1031.9062 | 122.7448 | -60.6079 | 61.9949 | -0.026398 | 0.0057934 | 0.006445 | 0.0073187 | 0.065952 | 0.00034814 | 0.067071 | -60.6171 | 62.027 | -60.878 | -60.7864 | 61.5189 | -0.70496 | -0.091553 | 0.091553 | 61.9766 | -60.9329 | -0.27008 | 0.032044 | -0.009155 | -0.17853 | -0.47607 | -0.32501 | -0.01831 | 0.26093 | 60.5164 | 60.6995 | 122.1268 | 122.6349 | -0.009155 | 122.5845 | 59.903 | -0.32501 | 122.6349 | -0.009155 | 59.903 | 122.1268 | 122.5845 | -122.8729 | -122.9279
1032.9531 | 122.7264 | -60.585 | 62.0087 | -0.36209 | 0.0075024 | 0.0058042 | 0.0026191 | 0.06467 | 0.0012027 | 0.067926 | -60.704 | 62.0453 | -60.8826 | -60.8047 | 61.4777 | -0.78735 | 0.032043 | 0.10986 | 62.0224 | -60.9146 | -0.29755 | 0.036621 | -0.11902 | -0.21973 | -0.53101 | -0.32959 | 0.013733 | 0.17853 | 60.6171 | 60.6949 | 122.0627 | 122.6303 | -0.11902 | 122.6074 | 59.7977 | -0.32959 | 122.6303 | -0.11902 | 59.7977 | 122.0627 | 122.6074 | -122.8912 | -122.9233
1033.9219 | 122.8226 | -60.585 | 61.9537 | -0.011139 | 0.0013074 | 0.0017454 | -0.0063531 | 0.063602 | 0.00056194 | 0.067712 | -60.704 | 61.9034 | -60.8917 | -60.7956 | 61.5417 | -0.71869 | -0.16479 | 0.14648 | 61.9446 | -60.8734 | -0.3067 | -0.050354 | -0.11902 | -0.21057 | -0.41199 | -0.28839 | -0.009155 | 0.18768 | 60.4202 | 60.7315 | 122.1268 | 122.4884 | -0.11902 | 122.5296 | 59.8663 | -0.28839 | 122.4884 | -0.11902 | 59.8663 | 122.1268 | 122.5296 | -122.8455 | -122.8271
1034.9688 | 122.7722 | -60.5988 | 61.972 | 0.019379 | 0.0045118 | 0.0094358 | 0.0056097 | 0.064243 | -0.0017881 | 0.070276 | -60.6308 | 61.9766 | -60.8826 | -60.791 | 61.5005 | -0.80109 | -0.082397 | 0.086975 | 61.9583 | -60.9512 | -0.28381 | 0.004578 | -0.032043 | -0.19226 | -0.4715 | -0.35248 | -0.013733 | 0.25177 | 60.5164 | 60.6857 | 122.0993 | 122.5754 | -0.032043 | 122.5571 | 59.7977 | -0.35248 | 122.5754 | -0.032043 | 59.7977 | 122.0993 | 122.5571 | -122.8546 | -122.9233
1035.9062 | 122.7859 | -60.6171 | 61.972 | -0.22476 | 0.0045118 | 0.0070858 | 0.0015509 | 0.06467 | -0.00071986 | 0.065576 | -60.6628 | 61.9949 | -60.8963 | -60.7819 | 61.4822 | -0.67291 | -0.009155 | 0.13275 | 61.972 | -60.9329 | -0.27924 | 0.022888 | -0.045777 | -0.1648 | -0.48981 | -0.31586 | 0 | 0.23346 | 60.6079 | 60.7498 | 122.0993 | 122.612 | -0.045777 | 122.5891 | 59.9442 | -0.31586 | 122.612 | -0.045777 | 59.9442 | 122.0993 | 122.5891 | -122.8683 | -122.905
1036.9531 | 122.7448 | -60.672 | 61.9217 | -0.24002 | 0.004939 | 0.006445 | 0.0013373 | 0.064029 | -0.00071986 | 0.066858 | -60.7452 | 61.972 | -60.9283 | -60.878 | 61.3953 | -0.63171 | 0.050354 | 0.09613 | 61.9583 | -60.965 | -0.25635 | 0.050354 | -0.073242 | -0.20599 | -0.52643 | -0.29297 | 0.036621 | 0.18311 | 60.7224 | 60.7681 | 122.0673 | 122.644 | -0.073242 | 122.6303 | 60.0403 | -0.29297 | 122.644 | -0.073242 | 60.0403 | 122.0673 | 122.6303 | -122.85 | -122.8867
1037.9062 | 122.7173 | -60.704 | 61.908 | -0.034027 | 0.0045118 | 0.0045224 | 0.0043281 | 0.066593 | -0.0015745 | 0.06878 | -60.7544 | 61.9308 | -60.997 | -60.9283 | 61.3449 | -0.62256 | -0.064087 | 0.032043 | 61.908 | -61.0199 | -0.29297 | 0.022888 | -0.050354 | -0.2243 | -0.56305 | -0.31586 | 0 | 0.24261 | 60.64 | 60.7361 | 122.049 | 122.6349 | -0.050354 | 122.612 | 60.0815 | -0.31586 | 122.6349 | -0.050354 | 60.0815 | 122.049 | 122.612 | -122.905 | -122.9279
1038.9688 | 122.7539 | -60.6583 | 61.908 | -0.064545 | 0.006648 | 0.0051632 | 0.0043281 | 0.06937 | -0.0017881 | 0.066217 | -60.7132 | 61.9034 | -60.9695 | -60.8459 | 61.3907 | -0.68665 | -0.064087 | 0.07782 | 61.9217 | -60.9558 | -0.31128 | -0.004578 | -0.054932 | -0.18768 | -0.51727 | -0.29755 | 0.013733 | 0.25635 | 60.5942 | 60.7361 | 122.049 | 122.5616 | -0.054932 | 122.58 | 59.9716 | -0.29755 | 122.5616 | -0.054932 | 59.9716 | 122.049 | 122.58 | -122.8775 | -122.8638
1039.9062 | 122.8088 | -60.6857 | 61.8713 | 0.20248 | 0.0060072 | 0.006445 | 0.0004827 | 0.067447 | 0.0016299 | 0.068139 | -60.7819 | 61.8942 | -60.9833 | -60.9055 | 61.3449 | -0.74158 | -0.19226 | 0.036621 | 61.8851 | -61.0062 | -0.29755 | 0.022888 | -0.09613 | -0.21973 | -0.52643 | -0.32044 | 0.013733 | 0.20142 | 60.4935 | 60.7224 | 122.0306 | 122.58 | -0.09613 | 122.5708 | 59.9442 | -0.32044 | 122.58 | -0.09613 | 59.9442 | 122.0306 | 122.5708 | -122.8546 | -122.8775
1040.9688 | 122.7768 | -60.6491 | 61.9446 | -0.14847 | 0.0055798 | 0.0085812 | 0.0019781 | 0.064884 | -0.0015745 | 0.067712 | -60.7315 | 61.9629 | -60.9329 | -60.8414 | 61.4044 | -0.73242 | 0.032043 | 0.09613 | 61.9446 | -60.9695 | -0.28381 | 0.018311 | -0.082397 | -0.19226 | -0.54016 | -0.32043 | 0 | 0.20142 | 60.6812 | 60.7452 | 122.0535 | 122.612 | -0.082397 | 122.5937 | 59.9167 | -0.32043 | 122.612 | -0.082397 | 59.9167 | 122.0535 | 122.5937 | -122.8775 | -122.9141
1041.9062 | 122.7631 | -60.6766 | 61.9263 | -0.056915 | 0.0034436 | 0.0066586 | 0.0041143 | 0.067234 | -0.00050626 | 0.069421 | -60.6995 | 61.972 | -60.9512 | -60.8505 | 61.3678 | -0.76904 | -0.050354 | 0.045776 | 61.94 | -60.965 | -0.27466 | 0.045776 | -0.022888 | -0.17395 | -0.55847 | -0.28839 | 0.013732 | 0.25177 | 60.6262 | 60.7224 | 122.0444 | 122.6486 | -0.022888 | 122.6166 | 59.9075 | -0.28839 | 122.6486 | -0.022888 | 59.9075 | 122.0444 | 122.6166 | -122.8775 | -122.8912
1042.9688 | 122.8363 | -60.6171 | 61.94 | -0.1561 | 0.0040846 | 0.006445 | -0.0044305 | 0.067234 | 0.00013454 | 0.068353 | -60.6628 | 61.9034 | -60.9009 | -60.7819 | 61.4777 | -0.60425 | -0.12817 | 0.20599 | 61.9308 | -60.9283 | -0.28381 | -0.036621 | -0.045777 | -0.1648 | -0.46234 | -0.31128 | -0.009155 | 0.23804 | 60.4889 | 60.8231 | 122.0947 | 122.5204 | -0.045777 | 122.5479 | 60.0128 | -0.31128 | 122.5204 | -0.045777 | 60.0128 | 122.0947 | 122.5479 | -122.8409 | -122.8683
1043.9062 | 122.85 | -60.6262 | 61.94 | -0.59097 | 0.0042982 | 0.0090086 | -0.0031489 | 0.063175 | 0.00034814 | 0.066003 | -60.7178 | 61.9034 | -60.8826 | -60.7636 | 61.4914 | -0.5127 | -0.1236 | 0.23346 | 61.9217 | -60.9375 | -0.25635 | -0.036621 | -0.091552 | -0.13733 | -0.44861 | -0.31128 | -0.01831 | 0.16479 | 60.5026 | 60.8597 | 122.1176 | 122.5296 | -0.091552 | 122.5479 | 60.1135 | -0.31128 | 122.5296 | -0.091552 | 60.1135 | 122.1176 | 122.5479 | -122.8226 | -122.8775
1044.9688 | 122.8455 | -60.6354 | 61.8393 | 0.20248 | 0.0034436 | 0.0072996 | 0.0002691 | 0.061679 | 0.00013454 | 0.069207 | -60.6812 | 61.8896 | -60.9558 | -60.8322 | 61.3861 | -0.58594 | -0.27008 | 0.091553 | 61.8347 | -60.9421 | -0.32043 | 0.050354 | -0.045776 | -0.19684 | -0.45319 | -0.3067 | -0.004577 | 0.27466 | 60.3653 | 60.7269 | 122.0215 | 122.525 | -0.045776 | 122.4701 | 60.0494 | -0.3067 | 122.525 | -0.045776 | 60.0494 | 122.0215 | 122.4701 | -122.7951 | -122.7814
1045.9062 | 122.7631 | -60.672 | 61.908 | -0.17136 | 0.0060072 | 0.0051632 | 0.0064643 | 0.065525 | -0.0013609 | 0.066644 | -60.6857 | 61.9537 | -60.9283 | -60.8505 | 61.3861 | -0.62256 | -0.07782 | 0.068665 | 61.8988 | -61.0062 | -0.25635 | 0.045776 | -0.013733 | -0.17853 | -0.52185 | -0.33417 | -0.009155 | 0.24262 | 60.5942 | 60.7407 | 122.0581 | 122.6257 | -0.013733 | 122.5708 | 60.0494 | -0.33417 | 122.6257 | -0.013733 | 60.0494 | 122.0581 | 122.5708 | -122.8363 | -122.9141
1046.9688 | 122.8226 | -60.6308 | 61.9446 | -0.22476 | 0.00323 | 0.0038816 | -0.0031489 | 0.065097 | -0.0020017 | 0.067285 | -60.6583 | 61.9263 | -60.9146 | -60.7864 | 61.4502 | -0.5722 | -0.073242 | 0.17853 | 61.9125 | -60.9329 | -0.28381 | -0.01831 | -0.027466 | -0.15564 | -0.49439 | -0.30212 | -0.032043 | 0.25635 | 60.5576 | 60.8093 | 122.081 | 122.5571 | -0.027466 | 122.5433 | 60.0586 | -0.30212 | 122.5571 | -0.027466 | 60.0586 | 122.081 | 122.5433 | -122.8592 | -122.8775
1047.9062 | 122.7448 | -60.6537 | 61.9492 | 0.049896 | 0.0034436 | 0.008154 | 0.0075323 | 0.065952 | -0.0015745 | 0.068353 | -60.6949 | 61.9766 | -60.91 | -60.8459 | 61.3495 | -0.70038 | -0.091553 | 0.036621 | 61.9537 | -60.9741 | -0.25635 | 0.027466 | -0.041198 | -0.19226 | -0.59967 | -0.32043 | 0.004577 | 0.21515 | 60.5621 | 60.6903 | 122.0032 | 122.6303 | -0.041198 | 122.6074 | 59.9533 | -0.32043 | 122.6303 | -0.041198 | 59.9533 | 122.0032 | 122.6074 | -122.8592 | -122.9233
1048.9688 | 122.8546 | -60.6491 | 61.8851 | 0.12619 | 0.0047254 | 0.0077268 | -0.0005853 | 0.065952 | -0.0030697 | 0.068353 | -60.6812 | 61.8988 | -60.8963 | -60.791 | 61.441 | -0.64545 | -0.27466 | 0.09613 | 61.8896 | -60.9375 | -0.24719 | 0.013733 | -0.032043 | -0.14191 | -0.44403 | -0.28839 | 0.004577 | 0.21515 | 60.3745 | 60.7452 | 122.0901 | 122.5479 | -0.032043 | 122.5388 | 60.0037 | -0.28839 | 122.5479 | -0.032043 | 60.0037 | 122.0901 | 122.5388 | -122.7814 | -122.8226
1049.9062 | 122.8592 | -60.6491 | 61.8896 | 0.15671 | 0.0051526 | 0.0045224 | 0.0036871 | 0.067447 | -0.0013609 | 0.068567 | -60.6812 | 61.8851 | -60.9329 | -60.8093 | 61.4182 | -0.6546 | -0.27466 | 0.091553 | 61.8851 | -60.9329 | -0.28381 | -0.004577 | -0.032043 | -0.16022 | -0.4715 | -0.28381 | -0.004577 | 0.25177 | 60.3745 | 60.7407 | 122.0673 | 122.5342 | -0.032043 | 122.5342 | 59.9945 | -0.28381 | 122.5342 | -0.032043 | 59.9945 | 122.0673 | 122.5342 | -122.8226 | -122.8226
1050.9688 | 122.7173 | -60.6354 | 61.9583 | -0.27054 | 0.0047254 | 0.0062314 | 0.0009101 | 0.061893 | -7.9062e-05 | 0.068139 | -60.7361 | 61.9858 | -60.9329 | -60.8185 | 61.6287 | -0.54016 | -0.15106 | -0.059509 | 61.9354 | -60.9879 | -0.29755 | 0.027466 | -0.10071 | -0.1831 | -0.32959 | -0.35248 | -0.022888 | 0.19684 | 60.4843 | 60.5759 | 122.2641 | 122.6212 | -0.10071 | 122.5708 | 60.0952 | -0.35248 | 122.6212 | -0.10071 | 60.0952 | 122.2641 | 122.5708 | -122.8912 | -122.9462
1051.9062 | 122.7081 | -60.6583 | 61.9308 | 0.034637 | 0.0060072 | 0.0055906 | 0.0047553 | 0.065525 | -0.0017881 | 0.068353 | -60.6949 | 61.9354 | -60.9375 | -60.8597 | 61.3358 | -0.6958 | -0.068665 | -0.013733 | 61.9308 | -60.9879 | -0.27924 | 0.004578 | -0.036621 | -0.20142 | -0.59509 | -0.32959 | 0 | 0.24262 | 60.5896 | 60.6445 | 121.994 | 122.5937 | -0.036621 | 122.5891 | 59.9625 | -0.32959 | 122.5937 | -0.036621 | 59.9625 | 121.994 | 122.5891 | -122.8683 | -122.9187
1052.9531 | 122.7402 | -60.6537 | 61.9629 | 0.84335 | 0.0047254 | 0.0062314 | -0.0007989 | 0.068729 | -0.00093346 | 0.068353 | -60.7224 | 61.9812 | -60.9421 | -60.8368 | 61.377 | -0.6546 | 0.018311 | 0.045776 | 61.9583 | -60.9512 | -0.28839 | 0.01831 | -0.068664 | -0.18311 | -0.58594 | -0.29755 | -0.004578 | 0.21973 | 60.672 | 60.6995 | 122.0306 | 122.6349 | -0.068664 | 122.612 | 59.9991 | -0.29755 | 122.6349 | -0.068664 | 59.9991 | 122.0306 | 122.612 | -122.905 | -122.9141
1053.9062 | 122.7631 | -60.6079 | 61.9629 | 0.19485 | 0.004939 | 0.0077268 | 0.0043281 | 0.065952 | -0.0026425 | 0.069635 | -60.6125 | 62.0316 | -60.9009 | -60.7864 | 61.4227 | -0.64545 | -0.09613 | 0.050354 | 61.9904 | -60.9055 | -0.29297 | 0.068664 | -0.004578 | -0.17853 | -0.54016 | -0.29755 | 0.027465 | 0.28839 | 60.5118 | 60.6583 | 122.0306 | 122.6395 | -0.004578 | 122.5983 | 59.9625 | -0.29755 | 122.6395 | -0.004578 | 59.9625 | 122.0306 | 122.5983 | -122.8638 | -122.8683
1054.9531 | 122.7676 | -60.585 | 61.9949 | -0.22476 | 0.002162 | 0.0049496 | 0.0004827 | 0.064884 | -0.0011471 | 0.066003 | -60.6583 | 62.0041 | -60.8688 | -60.7773 | 61.4319 | -0.68207 | -0.041199 | 0.073242 | 61.9904 | -60.9192 | -0.28381 | 0.009155 | -0.073242 | -0.19226 | -0.56305 | -0.33417 | -0.004578 | 0.21057 | 60.5438 | 60.6583 | 122.0169 | 122.5891 | -0.073242 | 122.5754 | 59.903 | -0.33417 | 122.5891 | -0.073242 | 59.903 | 122.0169 | 122.5754 | -122.8638 | -122.9141
1055.9062 | 122.7127 | -60.6491 | 61.972 | 0.088043 | 0.0072888 | 0.0096494 | 0.0043281 | 0.067661 | -7.9062e-05 | 0.067498 | -60.704 | 62.0224 | -60.9146 | -60.8734 | 61.3312 | -0.81482 | -0.091553 | -0.07782 | 61.9766 | -60.9558 | -0.2655 | 0.050354 | -0.054932 | -0.2243 | -0.64087 | -0.3067 | 0.004578 | 0.21057 | 60.5576 | 60.5713 | 121.9803 | 122.6715 | -0.054932 | 122.6257 | 59.8343 | -0.3067 | 122.6715 | -0.054932 | 59.8343 | 121.9803 | 122.6257 | -122.8867 | -122.9279
1056.9531 | 122.7539 | -60.64 | 61.9812 | -0.2095 | 0.0036572 | 0.0058042 | 0.0013373 | 0.065311 | -0.0015745 | 0.066858 | -60.7224 | 61.9812 | -60.9238 | -60.8185 | 61.3586 | -0.81482 | -0.013733 | 0.018311 | 61.9904 | -60.91 | -0.28381 | 0 | -0.082397 | -0.17853 | -0.62256 | -0.27008 | 0.009155 | 0.20142 | 60.6262 | 60.6583 | 121.9986 | 122.6212 | -0.082397 | 122.6303 | 59.8251 | -0.27008 | 122.6212 | -0.082397 | 59.8251 | 121.9986 | 122.6303 | -122.905 | -122.8912
1057.9062 | 122.7127 | -60.6537 | 61.9492 | 0.080414 | 0.0060072 | 0.005377 | 0.0051825 | 0.066165 | -0.0022153 | 0.06878 | -60.704 | 61.9812 | -60.9192 | -60.8643 | 61.3083 | -0.82398 | -0.07782 | -0.064087 | 61.9537 | -60.965 | -0.2655 | 0.032043 | -0.050354 | -0.21057 | -0.64087 | -0.31128 | 0.004577 | 0.21515 | 60.5759 | 60.5896 | 121.962 | 122.6349 | -0.050354 | 122.6074 | 59.8297 | -0.31128 | 122.6349 | -0.050354 | 59.8297 | 121.962 | 122.6074 | -122.8683 | -122.9141
1058.9531 | 122.7859 | -60.6079 | 61.9446 | -0.20187 | 0.00323 | 0.0070858 | -0.0029351 | 0.066593 | -7.9062e-05 | 0.067285 | -60.6583 | 61.9583 | -60.8688 | -60.7727 | 61.3998 | -0.66834 | -0.10529 | 0.091553 | 61.9537 | -60.9283 | -0.26093 | 0.013733 | -0.050354 | -0.1648 | -0.54474 | -0.32044 | 0.009155 | 0.21057 | 60.5026 | 60.6995 | 122.0078 | 122.5662 | -0.050354 | 122.5616 | 59.9396 | -0.32044 | 122.5662 | -0.050354 | 59.9396 | 122.0078 | 122.5616 | -122.8134 | -122.8729
1059.9062 | 122.8638 | -60.64 | 61.8576 | 0.21774 | 0.0028028 | 0.009863 | 5.5496e-05 | 0.065097 | -0.00071986 | 0.067498 | -60.6674 | 61.8393 | -60.9283 | -60.8505 | 61.322 | -0.66376 | -0.28839 | 0.018311 | 61.8942 | -60.9238 | -0.28839 | -0.018311 | -0.027465 | -0.21057 | -0.53558 | -0.28381 | 0.036621 | 0.26093 | 60.3516 | 60.6583 | 121.962 | 122.4792 | -0.027465 | 122.5342 | 59.9762 | -0.28381 | 122.4792 | -0.027465 | 59.9762 | 121.962 | 122.5342 | -122.7859 | -122.7814
1060.9688 | 122.7219 | -60.6125 | 61.94 | -0.16373 | 0.0057934 | 0.0077268 | 0.0015509 | 0.064456 | -0.00071986 | 0.065362 | -60.7178 | 61.9537 | -60.9192 | -60.8414 | 61.322 | -0.76904 | 0 | -0.004578 | 61.9629 | -60.9512 | -0.3067 | 0.013733 | -0.10529 | -0.22888 | -0.61798 | -0.33875 | 0.022889 | 0.20142 | 60.6125 | 60.6079 | 121.9345 | 122.5662 | -0.10529 | 122.5754 | 59.8434 | -0.33875 | 122.5662 | -0.10529 | 59.8434 | 121.9345 | 122.5754 | -122.8592 | -122.8912
1061.9062 | 122.7356 | -60.6445 | 61.9858 | 0.057526 | 0.0055798 | 0.0060178 | 0.0075323 | 0.066165 | -0.0013609 | 0.067712 | -60.6491 | 61.9995 | -60.8963 | -60.8047 | 61.322 | -0.79193 | -0.11444 | -0.050354 | 61.972 | -60.9192 | -0.25177 | 0.013733 | -0.004578 | -0.16022 | -0.66376 | -0.27466 | -0.013733 | 0.24719 | 60.5301 | 60.5942 | 121.9666 | 122.644 | -0.004578 | 122.6166 | 59.8526 | -0.27466 | 122.644 | -0.004578 | 59.8526 | 121.9666 | 122.6166 | -122.8821 | -122.905
1062.9688 | 122.7631 | -60.6308 | 61.9537 | -0.21713 | 0.0034436 | 0.0062314 | 0.0024053 | 0.064029 | -0.00093346 | 0.067071 | -60.704 | 61.9949 | -60.9283 | -60.8231 | 61.3312 | -0.61798 | -0.027466 | 0.004578 | 61.9766 | -60.9512 | -0.29755 | 0.041199 | -0.073243 | -0.19226 | -0.62256 | -0.32044 | 0.022889 | 0.2243 | 60.6033 | 60.6354 | 121.962 | 122.6257 | -0.073243 | 122.6074 | 60.0128 | -0.32044 | 122.6257 | -0.073243 | 60.0128 | 121.962 | 122.6074 | -122.8821 | -122.905
1063.9062 | 122.6898 | -60.6628 | 61.9583 | 0.12619 | 0.0081434 | 0.0096494 | 0.0028327 | 0.066165 | -7.9062e-05 | 0.067712 | -60.7361 | 61.972 | -60.9238 | -60.8826 | 61.2442 | -0.65918 | -0.082397 | -0.12817 | 61.9354 | -60.965 | -0.26093 | 0.013733 | -0.073242 | -0.21973 | -0.71411 | -0.30212 | -0.022888 | 0.18768 | 60.5804 | 60.5347 | 121.907 | 122.6349 | -0.073242 | 122.5983 | 60.0037 | -0.30212 | 122.6349 | -0.073242 | 60.0037 | 121.907 | 122.5983 | -122.8821 | -122.9233
1064.9688 | 122.7585 | -60.6491 | 61.9217 | -0.049286 | 0.0051526 | 0.0070858 | 0.0021917 | 0.067234 | -0.0022153 | 0.067285 | -60.672 | 61.9492 | -60.9421 | -60.8414 | 61.2808 | -0.5722 | -0.11444 | -0.022888 | 61.9217 | -60.965 | -0.29297 | 0.027466 | -0.022888 | -0.19226 | -0.64087 | -0.31586 | 0 | 0.27008 | 60.5347 | 60.6262 | 121.9299 | 122.5983 | -0.022888 | 122.5708 | 60.0769 | -0.31586 | 122.5983 | -0.022888 | 60.0769 | 121.9299 | 122.5708 | -122.8638 | -122.8867
1065.9062 | 122.7356 | -60.6674 | 61.9125 | 0.057526 | 0.0036572 | 0.003027 | 0.0026191 | 0.067661 | -0.0043515 | 0.067498 | -60.7315 | 61.9858 | -60.9467 | -60.8963 | 61.2534 | -0.29755 | -0.086975 | -0.13733 | 61.9537 | -61.0016 | -0.27924 | 0.073242 | -0.064087 | -0.22888 | -0.65918 | -0.33417 | 0.041198 | 0.21515 | 60.5804 | 60.5301 | 121.9208 | 122.6532 | -0.064087 | 122.6212 | 60.3699 | -0.33417 | 122.6532 | -0.064087 | 60.3699 | 121.9208 | 122.6212 | -122.8592 | -122.9141
1066.9062 | 122.7219 | -60.6628 | 61.9263 | 0.027008 | 0.0042982 | 0.0083676 | 0.0024053 | 0.06702 | -0.00071986 | 0.068353 | -60.6766 | 61.9858 | -60.9421 | -60.8505 | 61.322 | -0.16022 | -0.11444 | -0.073242 | 61.9217 | -60.9421 | -0.27924 | 0.059509 | -0.013733 | -0.18768 | -0.60425 | -0.27924 | -0.004578 | 0.2655 | 60.5484 | 60.5896 | 121.9849 | 122.6486 | -0.013733 | 122.5845 | 60.5026 | -0.27924 | 122.6486 | -0.013733 | 60.5026 | 121.9849 | 122.5845 | -122.8683 | -122.8683
1067.9688 | 122.7036 | -60.64 | 61.972 | -0.19424 | 0.0036572 | 0.0055906 | -0.0025079 | 0.067661 | -0.00071986 | 0.065789 | -60.7269 | 61.9995 | -60.9283 | -60.8276 | 61.3449 | -0.091553 | -0.032043 | -0.027466 | 61.9904 | -60.965 | -0.28839 | 0.027466 | -0.086975 | -0.18768 | -0.62714 | -0.32501 | 0.01831 | 0.20142 | 60.6079 | 60.6125 | 121.9849 | 122.6395 | -0.086975 | 122.6303 | 60.5484 | -0.32501 | 122.6395 | -0.086975 | 60.5484 | 121.9849 | 122.6303 | -122.9004 | -122.937
1068.9062 | 122.7402 | -60.6766 | 61.9171 | -0.049286 | 0.0062208 | 0.0077268 | 0.0028327 | 0.067447 | -0.0030697 | 0.067071 | -60.7224 | 61.94 | -60.9467 | -60.878 | 61.2762 | -0.12817 | -0.12817 | -0.064087 | 61.9217 | -61.0016 | -0.27008 | 0.022888 | -0.045776 | -0.20142 | -0.64087 | -0.32501 | 0.004578 | 0.2243 | 60.5484 | 60.6125 | 121.9528 | 122.6166 | -0.045776 | 122.5983 | 60.5484 | -0.32501 | 122.6166 | -0.045776 | 60.5484 | 121.9528 | 122.5983 | -122.8638 | -122.9187
1069.9688 | 122.731 | -60.6491 | 61.9217 | 0.0041197 | 0.0023756 | 0.012213 | 0.0028327 | 0.067661 | -0.0017881 | 0.066858 | -60.6857 | 61.9492 | -60.9512 | -60.8597 | 61.2991 | -0.1831 | -0.13275 | -0.10529 | 61.94 | -61.0107 | -0.30212 | 0.027466 | -0.036621 | -0.21057 | -0.62256 | -0.36163 | 0.01831 | 0.2655 | 60.5164 | 60.5438 | 121.9482 | 122.5983 | -0.036621 | 122.5891 | 60.466 | -0.36163 | 122.5983 | -0.036621 | 60.466 | 121.9482 | 122.5891 | -122.8729 | -122.9324
1070.9062 | 122.7493 | -60.6491 | 61.9217 | -0.11795 | 0.0047254 | 0.006445 | 0.0004827 | 0.066593 | -0.0024289 | 0.06878 | -60.6903 | 61.9583 | -60.9329 | -60.8231 | 61.3266 | -0.27924 | -0.10986 | -0.050354 | 61.9171 | -60.9512 | -0.28381 | 0.036621 | -0.041199 | -0.17395 | -0.59509 | -0.30212 | -0.004578 | 0.24261 | 60.5392 | 60.5988 | 121.9757 | 122.6074 | -0.041199 | 122.5662 | 60.3699 | -0.30212 | 122.6074 | -0.041199 | 60.3699 | 121.9757 | 122.5662 | -122.8546 | -122.8729
1071.9062 | 122.7402 | -60.6354 | 61.9308 | 0.1796 | 0.0064344 | 0.0092222 | 0.0041143 | 0.067447 | -0.0011471 | 0.067071 | -60.759 | 61.9629 | -60.9375 | -60.9055 | 61.2946 | -0.5127 | -0.13733 | -0.15106 | 61.9354 | -60.9787 | -0.30212 | 0.032044 | -0.1236 | -0.27008 | -0.63629 | -0.34332 | 0.004578 | 0.17853 | 60.498 | 60.4843 | 121.9299 | 122.5983 | -0.1236 | 122.5708 | 60.1227 | -0.34332 | 122.5983 | -0.1236 | 60.1227 | 121.9299 | 122.5708 | -122.8683 | -122.9095
1072.9531 | 122.7493 | -60.6125 | 61.9812 | -0.17899 | 0.0064344 | 0.006445 | 0.0021917 | 0.067874 | -0.0034971 | 0.066644 | -60.6766 | 62.0407 | -60.8826 | -60.8231 | 61.3815 | -0.45319 | -0.032043 | -0.07782 | 62.0361 | -60.91 | -0.27008 | 0.059509 | -0.064087 | -0.21057 | -0.59967 | -0.29755 | 0.054932 | 0.20599 | 60.5804 | 60.5347 | 121.994 | 122.6532 | -0.064087 | 122.6486 | 60.1593 | -0.29755 | 122.6532 | -0.064087 | 60.1593 | 121.994 | 122.6486 | -122.8638 | -122.8912
1073.9062 | 122.7356 | -60.6766 | 61.9217 | 0.019379 | 0.0075024 | 0.0096494 | 0.0041143 | 0.06937 | 0.00056194 | 0.070062 | -60.6766 | 61.9629 | -60.9283 | -60.8688 | 61.2991 | -0.46234 | -0.050354 | -0.13733 | 61.94 | -61.0016 | -0.25177 | 0.041199 | 0 | -0.19226 | -0.62256 | -0.32501 | 0.01831 | 0.25177 | 60.6262 | 60.5392 | 121.9757 | 122.6395 | 0 | 122.6166 | 60.2142 | -0.32501 | 122.6395 | 0 | 60.2142 | 121.9757 | 122.6166 | -122.85 | -122.9233
1074.9688 | 122.7539 | -60.6216 | 61.9125 | -0.12558 | 0.0062208 | 0.005377 | -0.0007989 | 0.068088 | -0.0020017 | 0.068139 | -60.6628 | 61.9263 | -60.9512 | -60.8185 | 61.3586 | -0.35706 | -0.009155 | -0.068665 | 61.9629 | -60.9421 | -0.32959 | 0.013733 | -0.041199 | -0.19684 | -0.55389 | -0.32044 | 0.050354 | 0.28839 | 60.6125 | 60.553 | 121.9803 | 122.5479 | -0.041199 | 122.5845 | 60.2646 | -0.32044 | 122.5479 | -0.041199 | 60.2646 | 121.9803 | 122.5845 | -122.8638 | -122.8546
1075.9062 | 122.7585 | -60.6995 | 61.8988 | 0.019379 | 0.0081434 | 0.0070858 | 0.0019781 | 0.068302 | -0.0017881 | 0.068139 | -60.7132 | 61.94 | -60.9787 | -60.8871 | 61.2625 | -0.3479 | 0.032043 | -0.11902 | 61.908 | -60.997 | -0.27924 | 0.041198 | -0.013733 | -0.18768 | -0.63629 | -0.29755 | 0.009155 | 0.2655 | 60.7315 | 60.5804 | 121.962 | 122.6395 | -0.013733 | 122.6074 | 60.3516 | -0.29755 | 122.6395 | -0.013733 | 60.3516 | 121.962 | 122.6074 | -122.8775 | -122.8958
1076.9062 | 122.7493 | -60.704 | 61.8942 | -0.018768 | 0.006648 | 0.0092222 | 0.0013373 | 0.068088 | -0.0015745 | 0.066644 | -60.7315 | 61.9308 | -60.9695 | -60.9055 | 61.2534 | -0.50354 | 0.018311 | -0.21973 | 61.8942 | -61.0336 | -0.2655 | 0.036621 | -0.027465 | -0.20142 | -0.64087 | -0.32959 | 0 | 0.23804 | 60.7224 | 60.4843 | 121.9574 | 122.6349 | -0.027465 | 122.5983 | 60.2005 | -0.32959 | 122.6349 | -0.027465 | 60.2005 | 121.9574 | 122.5983 | -122.8638 | -122.9279
1077.9688 | 122.7905 | -60.6857 | 61.9034 | -0.27054 | 0.0057934 | 0.0058042 | 5.5496e-05 | 0.065952 | 0.00077554 | 0.067285 | -60.8139 | 61.8988 | -60.9787 | -60.9329 | 61.2076 | -0.53558 | 0.13275 | -0.24719 | 61.8988 | -61.0199 | -0.29297 | -0.004577 | -0.12817 | -0.24719 | -0.6958 | -0.33417 | -0.004577 | 0.16479 | 60.8185 | 60.4385 | 121.8933 | 122.5845 | -0.12817 | 122.5845 | 60.1501 | -0.33417 | 122.5845 | -0.12817 | 60.1501 | 121.8933 | 122.5845 | -122.8821 | -122.9233
1078.9062 | 122.7448 | -60.6812 | 61.8896 | 0.019379 | 0.0055798 | 0.0060178 | 0.0034735 | 0.066806 | -0.0022153 | 0.066858 | -60.7452 | 61.9171 | -60.997 | -60.9192 | 61.2122 | -0.60425 | 0.032043 | -0.33417 | 61.8988 | -61.0245 | -0.31586 | 0.027466 | -0.064087 | -0.23804 | -0.67749 | -0.34332 | 0.009156 | 0.25177 | 60.7132 | 60.347 | 121.8933 | 122.5983 | -0.064087 | 122.58 | 60.0769 | -0.34332 | 122.5983 | -0.064087 | 60.0769 | 121.8933 | 122.58 | -122.8867 | -122.9141
1079.9531 | 122.6898 | -60.6857 | 61.8668 | 0.233 | 0.0042982 | 0.0058042 | 0.0034735 | 0.067874 | 0.0024845 | 0.068353 | -60.7636 | 61.9446 | -60.9741 | -60.9512 | 61.2076 | -0.71869 | 0.07782 | -0.4303 | 61.9217 | -61.0291 | -0.28839 | 0.07782 | -0.07782 | -0.2655 | -0.65918 | -0.34332 | 0.054932 | 0.21057 | 60.7636 | 60.2554 | 121.8933 | 122.6303 | -0.07782 | 122.6074 | 59.967 | -0.34332 | 122.6303 | -0.07782 | 59.967 | 121.8933 | 122.6074 | -122.8409 | -122.8958
1080.9062 | 122.7493 | -60.672 | 61.9034 | 0.011749 | 0.0040846 | 0.0058042 | 0.0045417 | 0.067874 | -0.00071986 | 0.068353 | -60.6857 | 61.9812 | -60.9238 | -60.8597 | 61.2991 | -0.69122 | 0.036621 | -0.3891 | 61.9308 | -60.9924 | -0.25177 | 0.07782 | -0.013733 | -0.18768 | -0.60425 | -0.32044 | 0.027466 | 0.23804 | 60.7086 | 60.2829 | 121.9711 | 122.6532 | -0.013733 | 122.6028 | 59.9808 | -0.32044 | 122.6532 | -0.013733 | 59.9808 | 121.9711 | 122.6028 | -122.8271 | -122.8958
1081.9688 | 122.731 | -60.7269 | 61.8668 | -0.25528 | 0.002162 | 0.0066586 | -0.0042169 | 0.065525 | -0.00050626 | 0.069848 | -60.7773 | 61.8713 | -60.965 | -60.9283 | 61.2122 | -0.68207 | 0.086975 | -0.33417 | 61.8805 | -61.0245 | -0.23804 | 0.004578 | -0.050354 | -0.20142 | -0.6546 | -0.29755 | 0.013733 | 0.18768 | 60.8139 | 60.3928 | 121.9391 | 122.5983 | -0.050354 | 122.6074 | 60.0449 | -0.29755 | 122.5983 | -0.050354 | 60.0449 | 121.9391 | 122.6074 | -122.8317 | -122.8912
1082.9062 | 122.7081 | -60.7224 | 61.8759 | 0.042267 | 0.0051526 | 0.0094358 | 0.0051825 | 0.06702 | -0.0030697 | 0.067712 | -60.759 | 61.9125 | -61.0016 | -60.9329 | 61.1801 | -0.84228 | 0.045776 | -0.44861 | 61.8851 | -61.0657 | -0.27924 | 0.036621 | -0.036621 | -0.21057 | -0.6958 | -0.34332 | 0.009155 | 0.24262 | 60.7681 | 60.2737 | 121.9025 | 122.6349 | -0.036621 | 122.6074 | 59.8801 | -0.34332 | 122.6349 | -0.036621 | 59.8801 | 121.9025 | 122.6074 | -122.8775 | -122.9416
1083.9531 | 122.7768 | -60.6766 | 61.9125 | -0.17136 | 0.0057934 | 0.0072996 | 0.0024053 | 0.065952 | 0.00013454 | 0.065576 | -60.6949 | 61.9583 | -60.9695 | -60.8551 | 61.2488 | -0.68207 | 0.032043 | -0.36621 | 61.9308 | -61.0062 | -0.29297 | 0.045776 | -0.01831 | -0.17853 | -0.66376 | -0.32959 | 0.01831 | 0.27466 | 60.7086 | 60.3104 | 121.9254 | 122.6349 | -0.01831 | 122.6074 | 59.9945 | -0.32959 | 122.6349 | -0.01831 | 59.9945 | 121.9254 | 122.6074 | -122.8821 | -122.9187
1084.9062 | 122.731 | -60.6674 | 61.908 | 0.0041197 | 0.004939 | 0.0092222 | 0.0045417 | 0.067447 | -0.00093346 | 0.067071 | -60.7178 | 61.94 | -60.965 | -60.878 | 61.2167 | -0.72327 | 0.027466 | -0.45776 | 61.9263 | -61.0016 | -0.29755 | 0.032043 | -0.050354 | -0.21057 | -0.69122 | -0.33417 | 0.018311 | 0.24719 | 60.6949 | 60.2097 | 121.8842 | 122.6074 | -0.050354 | 122.5937 | 59.9442 | -0.33417 | 122.6074 | -0.050354 | 59.9442 | 121.8842 | 122.5937 | -122.8729 | -122.9095
1085.9688 | 122.7722 | -60.64 | 61.9217 | -0.12558 | 0.0055798 | 0.003668 | 0.0041143 | 0.065952 | -0.0028561 | 0.067285 | -60.6857 | 61.9629 | -60.9741 | -60.8551 | 61.2579 | -0.59967 | 0.032043 | -0.41657 | 61.9537 | -61.0016 | -0.33417 | 0.041199 | -0.045776 | -0.21515 | -0.66376 | -0.36163 | 0.032043 | 0.28839 | 60.672 | 60.2234 | 121.8979 | 122.6028 | -0.045776 | 122.5937 | 60.0403 | -0.36163 | 122.6028 | -0.045776 | 60.0403 | 121.8979 | 122.5937 | -122.8958 | -122.9233
1086.9062 | 122.7264 | -60.6583 | 61.9583 | -0.041657 | 0.0068616 | 0.0068722 | 0.0026191 | 0.066806 | -0.0017881 | 0.067926 | -60.6674 | 61.9675 | -60.9283 | -60.8459 | 61.2625 | -0.62714 | 0.032043 | -0.46692 | 61.9446 | -60.965 | -0.27008 | 0.009155 | -0.009155 | -0.18768 | -0.6958 | -0.3067 | -0.013733 | 0.26093 | 60.6903 | 60.1913 | 121.9208 | 122.6257 | -0.009155 | 122.6028 | 60.0311 | -0.3067 | 122.6257 | -0.009155 | 60.0311 | 121.9208 | 122.6028 | -122.8867 | -122.9233
1087.9531 | 122.7448 | -60.6674 | 61.9629 | 1.0265 | 0.0042982 | 0.0075132 | -0.0018671 | 0.06702 | -0.0030697 | 0.06878 | -60.6949 | 61.9904 | -60.9192 | -60.8597 | 61.29 | -0.57678 | 0.10071 | -0.50354 | 61.9904 | -60.9375 | -0.25177 | 0.027465 | -0.027466 | -0.19226 | -0.67291 | -0.27008 | 0.027465 | 0.2243 | 60.7681 | 60.1639 | 121.9574 | 122.6578 | -0.027466 | 122.6578 | 60.0906 | -0.27008 | 122.6578 | -0.027466 | 60.0906 | 121.9574 | 122.6578 | -122.8821 | -122.9004
1088.9062 | 122.7539 | -60.6583 | 61.9446 | -1.3921 | 0.0055798 | 0.0077268 | 0.0045417 | 0.065952 | -0.0024289 | 0.067071 | -60.6903 | 61.9629 | -60.9467 | -60.8093 | 61.2534 | -0.56305 | 0.009155 | -0.49439 | 61.9263 | -60.9558 | -0.28839 | 0.018311 | -0.032044 | -0.15106 | -0.69122 | -0.29755 | -0.01831 | 0.25635 | 60.6674 | 60.1639 | 121.9116 | 122.6212 | -0.032044 | 122.5845 | 60.0952 | -0.29755 | 122.6212 | -0.032044 | 60.0952 | 121.9116 | 122.5845 | -122.8912 | -122.9004
1089.9688 | 122.8226 | -60.6262 | 61.8576 | 0.28641 | 0.0057934 | 0.005377 | -0.0027215 | 0.068515 | -0.0022153 | 0.06878 | -60.6583 | 61.8851 | -60.9604 | -60.8185 | 61.2808 | -0.54932 | -0.1236 | -0.5127 | 61.9034 | -60.91 | -0.33417 | 0.027466 | -0.032043 | -0.19226 | -0.57678 | -0.28381 | 0.045776 | 0.30212 | 60.5026 | 60.1135 | 121.907 | 122.5113 | -0.032043 | 122.5296 | 60.0769 | -0.28381 | 122.5113 | -0.032043 | 60.0769 | 121.907 | 122.5296 | -122.818 | -122.7676
1090.9062 | 122.6944 | -60.64 | 61.9446 | -0.079803 | 0.0062208 | 0.009863 | 0.0036871 | 0.066379 | -0.0022153 | 0.066217 | -60.6445 | 61.9675 | -60.9283 | -60.8093 | 61.2488 | -0.64087 | 0.018311 | -0.53558 | 61.94 | -60.9695 | -0.28839 | 0.022888 | -0.004577 | -0.16937 | -0.6958 | -0.32959 | -0.004578 | 0.28381 | 60.6583 | 60.1044 | 121.8887 | 122.6074 | -0.004577 | 122.58 | 59.9991 | -0.32959 | 122.6074 | -0.004577 | 59.9991 | 121.8887 | 122.58 | -122.8729 | -122.9141
1091.9688 | 122.8409 | -60.553 | 61.9583 | -1.0182 | 0.0040846 | 0.0096494 | -0.0054987 | 0.066165 | -0.00093346 | 0.066858 | -60.64 | 61.9446 | -60.8551 | -60.7132 | 61.3815 | -0.57678 | -0.059509 | -0.39368 | 61.972 | -60.8963 | -0.30212 | -0.013733 | -0.086975 | -0.16022 | -0.57678 | -0.34332 | 0.013733 | 0.21515 | 60.4935 | 60.1593 | 121.9345 | 122.4976 | -0.086975 | 122.525 | 59.9762 | -0.34332 | 122.4976 | -0.086975 | 59.9762 | 121.9345 | 122.525 | -122.8134 | -122.8546
1092.9062 | 122.7814 | -60.585 | 62.0041 | 1.3011 | 0.004939 | 0.013281 | 0.0068915 | 0.066379 | -0.0020017 | 0.06878 | -60.7407 | 62.0407 | -60.8871 | -60.759 | 61.3266 | -0.63629 | 0.013733 | -0.57678 | 62.0041 | -60.9009 | -0.30212 | 0.036621 | -0.15564 | -0.17395 | -0.67749 | -0.31586 | 0 | 0.14648 | 60.5988 | 60.0082 | 121.9116 | 122.6257 | -0.15564 | 122.5891 | 59.9487 | -0.31586 | 122.6257 | -0.15564 | 59.9487 | 121.9116 | 122.5891 | -122.8912 | -122.905
1093.9531 | 122.7448 | -60.6308 | 61.9904 | -0.1561 | 0.00323 | 0.0090086 | 0.0002691 | 0.063602 | -0.00050626 | 0.067926 | -60.704 | 61.9766 | -60.8917 | -60.8459 | 61.2396 | -0.67749 | 0.10529 | -0.59052 | 61.9766 | -60.9375 | -0.26093 | -0.013732 | -0.073243 | -0.21515 | -0.75073 | -0.3067 | -0.013732 | 0.18768 | 60.7361 | 60.0403 | 121.8704 | 122.6074 | -0.073243 | 122.6074 | 59.9533 | -0.3067 | 122.6074 | -0.073243 | 59.9533 | 121.8704 | 122.6074 | -122.8821 | -122.9279
1094.9062 | 122.7539 | -60.6674 | 61.9263 | -0.11795 | 0.0055798 | 0.0066586 | 0.0039007 | 0.065311 | -0.00050626 | 0.067285 | -60.6583 | 61.9583 | -60.9467 | -60.8459 | 61.2259 | -0.74158 | 0.013733 | -0.58136 | 61.9263 | -60.9604 | -0.27924 | 0.032043 | 0.009155 | -0.17853 | -0.70038 | -0.29297 | 0 | 0.28839 | 60.6812 | 60.0861 | 121.8933 | 122.6257 | 0.009155 | 122.5937 | 59.9258 | -0.29297 | 122.6257 | 0.009155 | 59.9258 | 121.8933 | 122.5937 | -122.8729 | -122.8867
1095.9531 | 122.7768 | -60.6628 | 61.9354 | -0.24002 | 0.0017346 | 0.0045224 | -0.0010125 | 0.066379 | -0.00071986 | 0.067712 | -60.7224 | 61.9354 | -60.9146 | -60.8276 | 61.2259 | -0.66376 | 0.050354 | -0.5722 | 61.9583 | -60.9467 | -0.25177 | 0 | -0.059509 | -0.1648 | -0.70953 | -0.28381 | 0.022888 | 0.19226 | 60.7132 | 60.0906 | 121.8887 | 122.5983 | -0.059509 | 122.6212 | 59.9991 | -0.28381 | 122.5983 | -0.059509 | 59.9991 | 121.8887 | 122.6212 | -122.85 | -122.8821
1096.9062 | 122.7402 | -60.6995 | 61.8942 | -0.018768 | 0.002162 | 0.0062314 | 0.0019781 | 0.065952 | 0.00013454 | 0.067285 | -60.6628 | 61.8942 | -60.997 | -60.8688 | 61.203 | -0.64087 | 0.004578 | -0.50812 | 61.8713 | -61.0291 | -0.29755 | 0 | 0.036621 | -0.16937 | -0.69122 | -0.32959 | -0.022888 | 0.33417 | 60.704 | 60.1913 | 121.9025 | 122.5937 | 0.036621 | 122.5708 | 60.0586 | -0.32959 | 122.5937 | 0.036621 | 60.0586 | 121.9025 | 122.5708 | -122.8912 | -122.9233
1097.9688 | 122.7036 | -60.704 | 61.9308 | -0.24765 | 0.0038708 | 0.0060178 | -0.0022943 | 0.063816 | 0.0014163 | 0.066003 | -60.7681 | 61.9492 | -60.9741 | -60.6766 | 61.2305 | -0.68665 | -0.054932 | -0.55847 | 61.9171 | -61.0291 | -0.27008 | 0.018311 | -0.064086 | 0.027466 | -0.70038 | -0.32501 | -0.013733 | 0.20599 | 60.6491 | 60.1456 | 121.9345 | 122.6532 | -0.064086 | 122.6212 | 60.0174 | -0.32501 | 122.6532 | -0.064086 | 60.0174 | 121.9345 | 122.6212 | -122.905 | -122.9599
1098.9062 | 122.7493 | -60.6857 | 61.9217 | -0.041657 | 0.0062208 | 0.0092222 | 0.0056097 | 0.066593 | 0.00034814 | 0.068353 | -60.6812 | 61.9492 | -60.9375 | -60.8459 | 61.1801 | -0.67749 | 0.009155 | -0.56763 | 61.9125 | -60.9879 | -0.25177 | 0.027466 | 0.004578 | -0.16022 | -0.74158 | -0.30212 | -0.009155 | 0.25635 | 60.6949 | 60.1181 | 121.8658 | 122.6349 | 0.004578 | 122.5983 | 60.0082 | -0.30212 | 122.6349 | 0.004578 | 60.0082 | 121.8658 | 122.5983 | -122.8592 | -122.9095
1099.9688 | 122.7402 | -60.6766 | 61.9354 | -0.36209 | 0.0057934 | 0.004736 | -0.0003717 | 0.065738 | -0.0013609 | 0.065362 | -60.7864 | 61.9263 | -60.9924 | -60.9055 | 61.1481 | -0.74158 | 0.086975 | -0.58136 | 61.9217 | -60.997 | -0.31586 | -0.009155 | -0.10986 | -0.22888 | -0.78735 | -0.32043 | -0.013733 | 0.20599 | 60.7636 | 60.0952 | 121.8246 | 122.6028 | -0.10986 | 122.5983 | 59.935 | -0.32043 | 122.6028 | -0.10986 | 59.935 | 121.8246 | 122.5983 | -122.9279 | -122.9324
1100.9062 | 122.7539 | -60.7315 | 61.8576 | 1.7436 | 0.0038708 | 0.0049496 | 0.0041143 | 0.06467 | -0.0032835 | 0.066858 | -60.7132 | 61.8576 | -61.0474 | -60.8963 | 61.1435 | -0.65918 | -0.013733 | -0.56305 | 61.8439 | -61.0565 | -0.31586 | 0 | 0.01831 | -0.16479 | -0.71411 | -0.32501 | -0.013733 | 0.33417 | 60.7178 | 60.1685 | 121.875 | 122.5891 | 0.01831 | 122.5754 | 60.0723 | -0.32501 | 122.5891 | 0.01831 | 60.0723 | 121.875 | 122.5754 | -122.905 | -122.9141
1101.9531 | 122.7493 | -60.7498 | 61.8576 | -0.13321 | 0.0030164 | 0.001959 | 0.0041143 | 0.068515 | -0.0013609 | 0.06878 | -60.7727 | 61.8988 | -61.0336 | -60.91 | 61.1343 | -0.72327 | 0 | -0.55847 | 61.8988 | -61.0382 | -0.28381 | 0.041199 | -0.022888 | -0.16022 | -0.72327 | -0.28839 | 0.041199 | 0.26093 | 60.7498 | 60.1913 | 121.8842 | 122.6486 | -0.022888 | 122.6486 | 60.0266 | -0.28839 | 122.6486 | -0.022888 | 60.0266 | 121.8842 | 122.6486 | -122.8912 | -122.8958
1102.9062 | 122.7951 | -60.7452 | 61.8393 | -0.22476 | 0.0053662 | 0.0043088 | 0.0011237 | 0.067234 | -0.0026425 | 0.067285 | -60.7864 | 61.8759 | -61.0336 | -60.9238 | 61.116 | -0.75989 | 0.018311 | -0.54016 | 61.8759 | -61.0565 | -0.28839 | 0.036622 | -0.041199 | -0.17853 | -0.72327 | -0.31128 | 0.036622 | 0.24719 | 60.7635 | 60.2051 | 121.8613 | 122.6212 | -0.041199 | 122.6212 | 59.9854 | -0.31128 | 122.6212 | -0.041199 | 59.9854 | 121.8613 | 122.6212 | -122.8729 | -122.8958
1103.9688 | 122.6944 | -60.7086 | 61.8622 | -0.17136 | 0.0042982 | 0.0096494 | -0.0022943 | 0.065952 | -0.0011471 | 0.068353 | -60.8047 | 61.8942 | -61.0291 | -60.9512 | 61.1023 | -0.74616 | 0.041199 | -0.46234 | 61.9034 | -61.0107 | -0.32043 | 0.032043 | -0.096131 | -0.24262 | -0.75989 | -0.30212 | 0.041198 | 0.2243 | 60.7498 | 60.2463 | 121.8109 | 122.6028 | -0.096131 | 122.612 | 59.9625 | -0.30212 | 122.6028 | -0.096131 | 59.9625 | 121.8109 | 122.612 | -122.8912 | -122.8729
1104.9062 | 122.7219 | -60.7498 | 61.8393 | 0.065155 | 0.0051526 | 0.0034544 | 0.0043281 | 0.065311 | -7.9062e-05 | 0.066217 | -60.7956 | 61.8713 | -61.0382 | -60.9604 | 61.0474 | -0.75989 | -0.16022 | -0.65002 | 61.8668 | -61.0703 | -0.28839 | 0.032044 | -0.045776 | -0.21057 | -0.79193 | -0.32043 | 0.027466 | 0.24262 | 60.5896 | 60.0998 | 121.7972 | 122.6212 | -0.045776 | 122.6166 | 59.9899 | -0.32043 | 122.6212 | -0.045776 | 59.9899 | 121.7972 | 122.6166 | -122.8775 | -122.9095
1105.9688 | 122.7951 | -60.7407 | 61.8073 | -0.16373 | 0.0047254 | 0.004736 | -0.0035761 | 0.064884 | 0.00013454 | 0.066858 | -60.791 | 61.8027 | -61.0245 | -60.8963 | 61.1114 | -0.54016 | -0.19684 | -0.50354 | 61.8301 | -61.0565 | -0.28381 | -0.004578 | -0.050354 | -0.15564 | -0.6958 | -0.31586 | 0.022888 | 0.23346 | 60.5438 | 60.2371 | 121.8521 | 122.5433 | -0.050354 | 122.5708 | 60.2005 | -0.31586 | 122.5433 | -0.050354 | 60.2005 | 121.8521 | 122.5708 | -122.8317 | -122.8638
1106.9062 | 122.7631 | -60.7269 | 61.821 | -0.17899 | 0.00323 | 0.0062314 | 0.0021917 | 0.066165 | 0.00013454 | 0.067498 | -60.791 | 61.8713 | -61.0199 | -60.91 | 61.0657 | -0.6134 | -0.17395 | -0.56305 | 61.8576 | -61.0703 | -0.29297 | 0.050354 | -0.064087 | -0.18311 | -0.75531 | -0.34332 | 0.036621 | 0.22888 | 60.553 | 60.1639 | 121.7926 | 122.5983 | -0.064087 | 122.5845 | 60.1135 | -0.34332 | 122.5983 | -0.064087 | 60.1135 | 121.7926 | 122.5845 | -122.8409 | -122.8912
1107.9531 | 122.7951 | -60.8047 | 61.7615 | -0.23239 | 0.0040846 | 0.006445 | -0.0012261 | 0.065525 | 0.00013454 | 0.067071 | -60.8276 | 61.7661 | -61.0611 | -60.9558 | 61.0382 | -0.63629 | -0.26093 | -0.50354 | 61.7798 | -61.0931 | -0.25635 | 0.004577 | -0.022888 | -0.15106 | -0.72327 | -0.28839 | 0.01831 | 0.23346 | 60.5438 | 60.3012 | 121.843 | 122.5708 | -0.022888 | 122.5845 | 60.1685 | -0.28839 | 122.5708 | -0.022888 | 60.1685 | 121.843 | 122.5845 | -122.8226 | -122.8546
1108.9062 | 122.7493 | -60.704 | 61.8668 | -0.27054 | 0.0042982 | 0.0049496 | 0.0015509 | 0.064884 | -7.9062e-05 | 0.064721 | -60.7773 | 61.9125 | -61.0153 | -60.8871 | 61.0703 | -0.66376 | -0.2243 | -0.61798 | 61.9034 | -61.0245 | -0.31128 | 0.045777 | -0.073242 | -0.18311 | -0.79651 | -0.32043 | 0.036621 | 0.23804 | 60.4797 | 60.0861 | 121.7743 | 122.6166 | -0.073242 | 122.6074 | 60.0403 | -0.32043 | 122.6166 | -0.073242 | 60.0403 | 121.7743 | 122.6074 | -122.8821 | -122.8912
1109.9688 | 122.7448 | -60.6857 | 61.9217 | -0.3392 | 0.004939 | 0.0051632 | 0.0015509 | 0.062747 | 0.0012027 | 0.067071 | -60.7773 | 61.9125 | -60.997 | -60.91 | 61.0931 | -0.737 | -0.1831 | -0.64087 | 61.9217 | -61.0291 | -0.31128 | -0.009155 | -0.091553 | -0.2243 | -0.82855 | -0.34332 | 0 | 0.21973 | 60.5026 | 60.0449 | 121.7789 | 122.5983 | -0.091553 | 122.6074 | 59.9487 | -0.34332 | 122.5983 | -0.091553 | 59.9487 | 121.7789 | 122.6074 | -122.9187 | -122.9507
1110.9062 | 122.7768 | -60.7269 | 61.8851 | -0.18662 | 0.0047254 | 0.0085812 | 0.0039007 | 0.064884 | -0.00071986 | 0.068567 | -60.7315 | 61.8759 | -61.0153 | -60.8871 | 61.116 | -0.71869 | -0.25177 | -0.60883 | 61.8759 | -61.0199 | -0.28839 | -0.009155 | -0.004577 | -0.16022 | -0.76904 | -0.29297 | -0.009155 | 0.28381 | 60.4752 | 60.1181 | 121.843 | 122.6028 | -0.004577 | 122.6028 | 60.0082 | -0.29297 | 122.6028 | -0.004577 | 60.0082 | 121.843 | 122.6028 | -122.9004 | -122.905
1111.9531 | 122.7219 | -60.759 | 61.8576 | -0.24765 | 0.0042982 | 0.0038816 | 0.0004827 | 0.066593 | -0.00050626 | 0.06878 | -60.8368 | 61.8805 | -61.0153 | -60.9467 | 61.0611 | -0.6958 | -0.18768 | -0.63629 | 61.8713 | -61.0703 | -0.25635 | 0.022888 | -0.07782 | -0.18768 | -0.79651 | -0.31128 | 0.013733 | 0.17853 | 60.5713 | 60.1227 | 121.8201 | 122.6395 | -0.07782 | 122.6303 | 60.0632 | -0.31128 | 122.6395 | -0.07782 | 60.0632 | 121.8201 | 122.6303 | -122.8729 | -122.9279
1112.9062 | 122.7127 | -60.7681 | 61.853 | -0.38498 | 0.0045118 | 0.0038816 | -0.0020807 | 0.065952 | -0.00050626 | 0.066644 | -60.8734 | 61.8393 | -61.0611 | -60.9787 | 61.0107 | -0.71869 | -0.20599 | -0.62714 | 61.8576 | -61.0748 | -0.29297 | -0.013733 | -0.10529 | -0.21057 | -0.84228 | -0.3067 | 0.004578 | 0.18768 | 60.5621 | 60.141 | 121.7789 | 122.6074 | -0.10529 | 122.6257 | 60.0494 | -0.3067 | 122.6074 | -0.10529 | 60.0494 | 121.7789 | 122.6257 | -122.9141 | -122.9279
1113.9688 | 122.7951 | -60.7452 | 61.8347 | -0.17136 | 0.002162 | 0.0021726 | -0.0029351 | 0.062961 | 0.00013454 | 0.067285 | -60.759 | 61.7981 | -60.997 | -60.8826 | 61.1435 | -0.59052 | -0.33875 | -0.55389 | 61.8164 | -61.0336 | -0.25177 | -0.036621 | -0.013733 | -0.13733 | -0.69122 | -0.28839 | -0.018311 | 0.23804 | 60.4065 | 60.1913 | 121.8887 | 122.5433 | -0.013733 | 122.5616 | 60.1547 | -0.28839 | 122.5433 | -0.013733 | 60.1547 | 121.8887 | 122.5616 | -122.8317 | -122.8683
1114.9062 | 122.7402 | -60.7178 | 61.8805 | -0.011139 | 0.0070752 | 0.004736 | 0.0060369 | 0.06467 | 0.00056194 | 0.064935 | -60.7224 | 61.9034 | -61.0016 | -60.8963 | 61.1023 | -0.68207 | -0.31586 | -0.68207 | 61.8805 | -61.0107 | -0.28381 | 0.022888 | -0.004578 | -0.17853 | -0.7782 | -0.29297 | 0 | 0.27924 | 60.4019 | 60.0357 | 121.8201 | 122.6212 | -0.004578 | 122.5983 | 60.0357 | -0.29297 | 122.6212 | -0.004578 | 60.0357 | 121.8201 | 122.5983 | -122.8821 | -122.8912
1115.9688 | 122.8729 | -60.6949 | 61.8439 | -0.064545 | 0.0019482 | 0.0060178 | -0.0040033 | 0.063388 | -0.00071986 | 0.067071 | -60.7269 | 61.7889 | -60.9879 | -60.8139 | 61.235 | -0.64087 | -0.4303 | -0.52643 | 61.8347 | -60.9879 | -0.29297 | -0.054932 | -0.032044 | -0.11902 | -0.60883 | -0.29297 | -0.009155 | 0.26093 | 60.2646 | 60.1685 | 121.9299 | 122.4838 | -0.032044 | 122.5296 | 60.054 | -0.29297 | 122.4838 | -0.032044 | 60.054 | 121.9299 | 122.5296 | -122.8317 | -122.8317
1116.9062 | 122.7402 | -60.7956 | 61.8301 | -0.17899 | 0.001521 | 0.006445 | 0.0051825 | 0.061466 | -0.0028561 | 0.066003 | -60.8597 | 61.8027 | -61.0611 | -60.9924 | 60.997 | -0.93384 | -0.23346 | -0.62714 | 61.8073 | -61.084 | -0.2655 | -0.027466 | -0.064087 | -0.19684 | -0.83313 | -0.28839 | -0.022888 | 0.20142 | 60.5621 | 60.1685 | 121.7926 | 122.5983 | -0.064087 | 122.6028 | 59.8618 | -0.28839 | 122.5983 | -0.064087 | 59.8618 | 121.7926 | 122.6028 | -122.8912 | -122.9141
1117.9531 | 122.7219 | -60.8414 | 61.7981 | -0.24765 | 0.0034436 | 0.00024998 | 0.0017645 | 0.064456 | -0.0013609 | 0.063653 | -60.8963 | 61.7889 | -61.1114 | -60.9329 | 61.1664 | -0.89722 | -0.38452 | -0.6546 | 61.7661 | -61.1389 | -0.27008 | -0.009156 | -0.054931 | -0.091552 | -0.63171 | -0.29755 | -0.032044 | 0.21515 | 60.4568 | 60.1868 | 122.0078 | 122.6303 | -0.054931 | 122.6074 | 59.9442 | -0.29755 | 122.6303 | -0.054931 | 59.9442 | 122.0078 | 122.6074 | -122.9095 | -122.937
1118.9062 | 122.7173 | -60.8368 | 61.7706 | -0.23239 | 0.0053662 | 0.0043088 | 0.0021917 | 0.063816 | -0.00071986 | 0.067498 | -60.9283 | 61.7569 | -61.1343 | -61.0519 | 60.9146 | -0.93842 | -0.21057 | -0.64545 | 61.7706 | -61.1206 | -0.29755 | -0.013733 | -0.091553 | -0.21515 | -0.85602 | -0.28381 | 0 | 0.20599 | 60.6262 | 60.1913 | 121.7514 | 122.5937 | -0.091553 | 122.6074 | 59.8984 | -0.28381 | 122.5937 | -0.091553 | 59.8984 | 121.7514 | 122.6074 | -122.905 | -122.8912
1119.9844 | 122.7448 | -60.8917 | 61.7111 | -0.018768 | 0.0036572 | 0.0058042 | 0.0028327 | 0.065097 | -0.00071986 | 0.067498 | -60.9192 | 61.6516 | -61.2076 | -61.0794 | 60.8688 | -1.0803 | -0.33875 | -0.54932 | 61.6882 | -61.171 | -0.31586 | -0.05951 | -0.027465 | -0.18768 | -0.84229 | -0.27923 | -0.022889 | 0.28839 | 60.553 | 60.3424 | 121.7606 | 122.5433 | -0.027465 | 122.58 | 59.8114 | -0.27923 | 122.5433 | -0.027465 | 59.8114 | 121.7606 | 122.58 | -122.9187 | -122.8821
1120.9062 | 122.7585 | -60.8368 | 61.7294 | -0.18662 | 0.0019482 | 0.0068722 | 0.0032599 | 0.066165 | -0.0045651 | 0.067712 | -60.8688 | 61.7477 | -61.1252 | -61.0107 | 60.9283 | -1.2177 | -0.28839 | -0.5722 | 61.7706 | -61.1389 | -0.28839 | 0.018311 | -0.032043 | -0.17395 | -0.80109 | -0.30212 | 0.041199 | 0.25635 | 60.5484 | 60.2646 | 121.7651 | 122.5845 | -0.032043 | 122.6074 | 59.6191 | -0.30212 | 122.5845 | -0.032043 | 59.6191 | 121.7651 | 122.6074 | -122.8546 | -122.8683
1121.9531 | 122.7951 | -60.9238 | 61.5829 | 0.16434 | 0.0025892 | 0.003668 | -0.0033625 | 0.064029 | -0.00093346 | 0.068353 | -60.965 | 61.5738 | -61.2213 | -61.1114 | 60.8368 | -1.2268 | -0.50354 | -0.51727 | 61.6104 | -61.2167 | -0.29755 | -0.009155 | -0.041199 | -0.18768 | -0.74615 | -0.29297 | 0.027466 | 0.25635 | 60.4202 | 60.4065 | 121.7606 | 122.4976 | -0.041199 | 122.5342 | 59.697 | -0.29297 | 122.4976 | -0.041199 | 59.697 | 121.7606 | 122.5342 | -122.8043 | -122.7997
1122.9062 | 122.7036 | -60.8826 | 61.7569 | -0.19424 | 0.0017346 | 0.00089078 | -0.0001581 | 0.06467 | -0.00071986 | 0.066217 | -60.9375 | 61.7157 | -61.1389 | -61.0703 | 60.8826 | -1.4374 | -0.22888 | -0.4715 | 61.7386 | -61.1572 | -0.25635 | -0.041199 | -0.054932 | -0.18768 | -0.87433 | -0.27466 | -0.018311 | 0.20142 | 60.6537 | 60.4111 | 121.7651 | 122.5983 | -0.054932 | 122.6212 | 59.4452 | -0.27466 | 122.5983 | -0.054932 | 59.4452 | 121.7651 | 122.6212 | -122.8958 | -122.9141
1123.9531 | 122.8912 | -60.8917 | 61.6425 | -0.13321 | 0.0013074 | 0.0058042 | -0.0025079 | 0.064456 | -0.0013609 | 0.067071 | -60.9192 | 61.5921 | -61.1664 | -61.0153 | 61.0062 | -1.181 | -0.37079 | -0.70953 | 61.6516 | -61.1618 | -0.27466 | -0.050354 | -0.027465 | -0.1236 | -0.63629 | -0.27008 | 0.009155 | 0.24719 | 60.5209 | 60.1822 | 121.8979 | 122.4838 | -0.027465 | 122.5433 | 59.7107 | -0.27008 | 122.4838 | -0.027465 | 59.7107 | 121.8979 | 122.5433 | -122.8088 | -122.8043
1124.9219 | 122.7356 | -60.8688 | 61.647 | 0.11093 | 0.0023756 | 0.0043088 | -0.0037897 | 0.063602 | -0.0017881 | 0.06643 | -60.9879 | 61.6104 | -61.1984 | -61.084 | 60.878 | -1.5472 | -0.4303 | -0.48523 | 61.6287 | -61.1755 | -0.32959 | -0.036621 | -0.11902 | -0.21515 | -0.76904 | -0.3067 | -0.018311 | 0.21057 | 60.4385 | 60.3836 | 121.7468 | 122.4792 | -0.11902 | 122.4976 | 59.3216 | -0.3067 | 122.4792 | -0.11902 | 59.3216 | 121.7468 | 122.4976 | -122.8455 | -122.8226
1125.9531 | 122.7448 | -60.9146 | 61.6974 | -0.4155 | 0.0030164 | 0.0058042 | 0.0021917 | 0.060611 | -0.0013609 | 0.068353 | -61.0107 | 61.6562 | -61.1755 | -61.0977 | 60.8047 | -1.5839 | -0.25635 | -0.44861 | 61.6608 | -61.2076 | -0.26093 | -0.041199 | -0.09613 | -0.18311 | -0.89264 | -0.29297 | -0.036621 | 0.16479 | 60.6583 | 60.466 | 121.7194 | 122.5708 | -0.09613 | 122.5754 | 59.3307 | -0.29297 | 122.5708 | -0.09613 | 59.3307 | 121.7194 | 122.5754 | -122.8729 | -122.905
1126.9062 | 122.8088 | -60.8826 | 61.6425 | -0.17136 | 0.00088016 | 0.00067718 | -0.0003717 | 0.062534 | -0.0026425 | 0.06878 | -60.9421 | 61.5829 | -61.171 | -61.0428 | 60.8551 | -1.5106 | -0.39825 | -0.32501 | 61.6241 | -61.1801 | -0.28839 | -0.059509 | -0.05951 | -0.16022 | -0.78735 | -0.29755 | -0.01831 | 0.22888 | 60.4843 | 60.5576 | 121.7377 | 122.4655 | -0.05951 | 122.5067 | 59.3719 | -0.29755 | 122.4655 | -0.05951 | 59.3719 | 121.7377 | 122.5067 | -122.8134 | -122.8226
1127.9688 | 122.7859 | -60.791 | 61.7477 | 0.11093 | 0.001521 | 0.0032406 | -0.0001581 | 0.063388 | 0.00077554 | 0.067285 | -60.8551 | 61.6928 | -61.0931 | -60.9604 | 61.0016 | -1.4923 | -0.54016 | -0.43488 | 61.7294 | -61.1069 | -0.30212 | -0.054932 | -0.064087 | -0.16937 | -0.74616 | -0.31586 | -0.018311 | 0.23804 | 60.2509 | 60.3561 | 121.7926 | 122.4838 | -0.064087 | 122.5204 | 59.2987 | -0.31586 | 122.4838 | -0.064087 | 59.2987 | 121.7926 | 122.5204 | -122.8409 | -122.8546
1128.9062 | 122.7173 | -60.8871 | 61.7386 | -0.30869 | 0.0030164 | 0.0060178 | 0.0015509 | 0.061252 | -0.0015745 | 0.066644 | -60.965 | 61.6791 | -61.1801 | -61.0931 | 60.8368 | -1.1993 | -0.3067 | -0.46234 | 61.6928 | -61.171 | -0.29297 | -0.059509 | -0.07782 | -0.20599 | -0.90179 | -0.28381 | -0.045776 | 0.21515 | 60.5804 | 60.4248 | 121.7239 | 122.5662 | -0.07782 | 122.58 | 59.6878 | -0.28381 | 122.5662 | -0.07782 | 59.6878 | 121.7239 | 122.58 | -122.9187 | -122.9095
1129.9688 | 122.7676 | -60.965 | 61.6196 | -0.24765 | 0.0047254 | 0.0075132 | 0.0053961 | 0.06467 | -0.0028561 | 0.067071 | -60.9924 | 61.615 | -61.2442 | -61.1252 | 60.7361 | -1.3641 | -0.39825 | -0.48065 | 61.5784 | -61.2808 | -0.27924 | -0.004578 | -0.027466 | -0.16022 | -0.88348 | -0.31586 | -0.041199 | 0.25177 | 60.5667 | 60.4843 | 121.701 | 122.58 | -0.027466 | 122.5433 | 59.6008 | -0.31586 | 122.58 | -0.027466 | 59.6008 | 121.701 | 122.5433 | -122.8638 | -122.9004
1130.9062 | 122.8409 | -60.9192 | 61.5967 | -0.14084 | 0.0013074 | 0.0032406 | -0.0020807 | 0.063175 | -0.0015745 | 0.067285 | -60.9558 | 61.5601 | -61.2122 | -61.0657 | 60.8368 | -1.2863 | -0.46692 | -0.40741 | 61.5921 | -61.2259 | -0.29297 | -0.036621 | -0.036622 | -0.14648 | -0.75989 | -0.3067 | -0.004578 | 0.25635 | 60.4523 | 60.5118 | 121.756 | 122.4792 | -0.036622 | 122.5113 | 59.6329 | -0.3067 | 122.4792 | -0.036622 | 59.6329 | 121.756 | 122.5113 | -122.8088 | -122.8226
1131.9531 | 122.8317 | -60.9055 | 61.6104 | -0.049286 | 0.00023916 | 0.0060178 | -0.0033625 | 0.061893 | -0.0015745 | 0.067498 | -61.0016 | 61.5417 | -61.1984 | -61.0657 | 60.8414 | -1.5335 | -0.50354 | -0.43488 | 61.5967 | -61.1893 | -0.29297 | -0.068665 | -0.09613 | -0.16022 | -0.76904 | -0.28381 | -0.013733 | 0.19684 | 60.4019 | 60.4706 | 121.7468 | 122.4472 | -0.09613 | 122.5021 | 59.3719 | -0.28381 | 122.4472 | -0.09613 | 59.3719 | 121.7468 | 122.5021 | -122.8088 | -122.7997
1132.9062 | 122.7264 | -60.9512 | 61.6562 | -0.27817 | 0.0030164 | 0.00046358 | 0.0006965 | 0.061679 | -0.00093346 | 0.067926 | -61.0245 | 61.6058 | -61.235 | -61.1343 | 60.7727 | -1.2131 | -0.33875 | -0.54474 | 61.615 | -61.2396 | -0.28381 | -0.050354 | -0.073242 | -0.1831 | -0.88348 | -0.28839 | -0.041199 | 0.21057 | 60.6125 | 60.4065 | 121.7239 | 122.5571 | -0.073242 | 122.5662 | 59.7382 | -0.28839 | 122.5571 | -0.073242 | 59.7382 | 121.7239 | 122.5662 | -122.8912 | -122.8958
1133.9688 | 122.8592 | -61.0245 | 61.4868 | -0.095062 | 0.001521 | 0.00024998 | -0.0003717 | 0.061466 | -0.0020017 | 0.067712 | -61.0703 | 61.4594 | -61.2991 | -61.1526 | 60.7086 | -1.1124 | -0.56763 | -0.35248 | 61.4548 | -61.2991 | -0.27466 | -0.027465 | -0.045776 | -0.12817 | -0.7782 | -0.27466 | -0.032043 | 0.22888 | 60.4568 | 60.672 | 121.7331 | 122.4838 | -0.045776 | 122.4792 | 59.9121 | -0.27466 | 122.4838 | -0.045776 | 59.9121 | 121.7331 | 122.4792 | -122.7859 | -122.7859
1134.9062 | 122.8455 | -60.9695 | 61.5692 | -0.14847 | 0.00045296 | 0.001959 | 0.0004827 | 0.061893 | -0.0034971 | 0.066644 | -61.0016 | 61.496 | -61.2534 | -61.084 | 60.8047 | -1.3824 | -0.53558 | -0.39368 | 61.528 | -61.2534 | -0.28381 | -0.073242 | -0.032044 | -0.11444 | -0.76447 | -0.28381 | -0.041199 | 0.25177 | 60.434 | 60.5759 | 121.7743 | 122.4655 | -0.032044 | 122.4976 | 59.5871 | -0.28381 | 122.4655 | -0.032044 | 59.5871 | 121.7743 | 122.4976 | -122.8226 | -122.8226
1135.9531 | 122.8134 | -61.0931 | 61.4685 | 0.057526 | -0.001256 | 0.0045224 | -0.0029351 | 0.06232 | -0.00093346 | 0.068994 | -60.9924 | 61.4319 | -61.3449 | -61.2396 | 60.6216 | -1.2726 | -0.5722 | -0.46234 | 61.4594 | -61.3495 | -0.25177 | -0.036621 | 0.10071 | -0.14648 | -0.84686 | -0.25635 | -0.009155 | 0.35248 | 60.5209 | 60.6308 | 121.7148 | 122.525 | 0.10071 | 122.5525 | 59.8206 | -0.25635 | 122.525 | 0.10071 | 59.8206 | 121.7148 | 122.5525 | -122.8134 | -122.818
1136.9062 | 122.8683 | -61.1618 | 61.3541 | -0.20187 | 0.0019482 | 0.003668 | 0.0041143 | 0.063175 | -0.00050626 | 0.066003 | -61.3266 | 61.29 | -61.4502 | -61.3037 | 60.3882 | -1.6891 | -0.55389 | -0.35248 | 61.3129 | -61.4731 | -0.28839 | -0.064087 | -0.1648 | -0.14191 | -0.96588 | -0.31128 | -0.041199 | 0.1236 | 60.6079 | 60.8093 | 121.55 | 122.4518 | -0.1648 | 122.4747 | 59.4727 | -0.31128 | 122.4518 | -0.1648 | 59.4727 | 121.55 | 122.4747 | -122.8043 | -122.8271
1137.9531 | 122.8271 | -61.1481 | 61.377 | -0.079803 | 0.00045296 | 0.0058042 | -0.0001581 | 0.061252 | -0.00093346 | 0.067712 | -61.3174 | 61.2579 | -61.5189 | -61.3861 | 60.4477 | -1.8448 | -0.56763 | -0.41199 | 61.322 | -61.4227 | -0.37079 | -0.11902 | -0.16937 | -0.23804 | -0.92926 | -0.27466 | -0.054932 | 0.20142 | 60.5804 | 60.7361 | 121.5958 | 122.406 | -0.16937 | 122.4701 | 59.3033 | -0.27466 | 122.406 | -0.16937 | 59.3033 | 121.5958 | 122.4701 | -122.8958 | -122.7997
1138.9062 | 122.8363 | -61.0153 | 61.5097 | -0.47653 | 0.0013074 | 0.003027 | -0.0007989 | 0.061038 | -0.00029266 | 0.068567 | -61.0748 | 61.4273 | -61.3495 | -61.1343 | 60.6857 | -1.9043 | -0.59967 | -0.32501 | 61.4594 | -61.3083 | -0.33417 | -0.082398 | -0.059509 | -0.11902 | -0.82397 | -0.29297 | -0.050354 | 0.27466 | 60.4156 | 60.6903 | 121.7011 | 122.4426 | -0.059509 | 122.4747 | 59.111 | -0.29297 | 122.4426 | -0.059509 | 59.111 | 121.7011 | 122.4747 | -122.8592 | -122.818
1139.9688 | 122.7127 | -61.1618 | 61.4456 | -0.69016 | 0.0019482 | 0.0032406 | 0.0060369 | 0.061252 | -0.00093346 | 0.066858 | -61.2442 | 61.4365 | -61.441 | -61.3403 | 60.4385 | -2.092 | -0.43945 | -0.44861 | 61.4044 | -61.4685 | -0.27924 | -0.009156 | -0.082398 | -0.17853 | -1.0071 | -0.3067 | -0.041199 | 0.19684 | 60.7224 | 60.7132 | 121.6003 | 122.5983 | -0.082398 | 122.5662 | 59.0698 | -0.3067 | 122.5983 | -0.082398 | 59.0698 | 121.6003 | 122.5662 | -122.8867 | -122.9141
1140.9062 | 122.8317 | -61.116 | 61.3998 | -0.16373 | 0.00066656 | 0.0072996 | -0.0001581 | 0.063602 | -0.00071986 | 0.068353 | -61.1664 | 61.3174 | -61.4273 | -61.2534 | 60.553 | -2.092 | -0.61798 | -0.36621 | 61.3861 | -61.3815 | -0.31128 | -0.082397 | -0.050354 | -0.13733 | -0.84686 | -0.2655 | -0.013733 | 0.26093 | 60.498 | 60.7498 | 121.669 | 122.4335 | -0.050354 | 122.5021 | 59.024 | -0.2655 | 122.4335 | -0.050354 | 59.024 | 121.669 | 122.5021 | -122.8271 | -122.7814
1141.9531 | 122.7859 | -61.2305 | 61.2717 | 0.11856 | 0.002162 | 0.0066586 | 0.0011237 | 0.061893 | 0.00034814 | 0.069421 | -61.3495 | 61.203 | -61.5646 | -61.4456 | 60.3195 | -2.2339 | -0.68665 | -0.38452 | 61.2579 | -61.5326 | -0.33417 | -0.068664 | -0.11902 | -0.21515 | -0.95215 | -0.30212 | -0.013732 | 0.21515 | 60.5438 | 60.8459 | 121.55 | 122.4335 | -0.11902 | 122.4884 | 58.9966 | -0.30212 | 122.4335 | -0.11902 | 58.9966 | 121.55 | 122.4884 | -122.8363 | -122.8043
1142.9062 | 122.8455 | -61.1114 | 61.3815 | -0.12558 | 2.5564e-05 | 0.0015316 | -0.0031489 | 0.05997 | -0.0011471 | 0.068994 | -61.2991 | 61.2122 | -61.5372 | -61.2534 | 60.5438 | -2.0325 | -0.62714 | -0.22888 | 61.3541 | -61.3907 | -0.42572 | -0.16937 | -0.18768 | -0.14191 | -0.83771 | -0.27924 | -0.027466 | 0.23804 | 60.4843 | 60.8826 | 121.6553 | 122.3236 | -0.18768 | 122.4655 | 59.079 | -0.27924 | 122.3236 | -0.18768 | 59.079 | 121.6553 | 122.4655 | -122.9187 | -122.7722
1143.9531 | 122.7997 | -61.235 | 61.2534 | 0.14908 | 0.001521 | 0.0034544 | -0.0016535 | 0.061893 | 0.00034814 | 0.066644 | -61.3037 | 61.1984 | -61.5463 | -61.409 | 60.347 | -2.0096 | -0.74616 | -0.39825 | 61.2213 | -61.5234 | -0.31128 | -0.054932 | -0.068665 | -0.17395 | -0.90637 | -0.28839 | -0.032044 | 0.24262 | 60.4889 | 60.8368 | 121.582 | 122.4335 | -0.068665 | 122.4564 | 59.2255 | -0.28839 | 122.4335 | -0.068665 | 59.2255 | 121.582 | 122.4564 | -122.7997 | -122.7768
1144.9219 | 122.7402 | -61.4365 | 61.1755 | -0.011139 | 0.0064344 | 0.005377 | 0.0075323 | 0.064884 | -0.0022153 | 0.06643 | -61.4548 | 61.1664 | -61.7203 | -61.5646 | 60.0494 | -1.9638 | -0.68665 | -0.37994 | 61.1023 | -61.7523 | -0.28381 | -0.009155 | -0.018311 | -0.12817 | -1.1261 | -0.31586 | -0.073242 | 0.2655 | 60.7498 | 61.0565 | 121.4859 | 122.6028 | -0.018311 | 122.5388 | 59.4727 | -0.31586 | 122.6028 | -0.018311 | 59.4727 | 121.4859 | 122.5388 | -122.8958 | -122.9279
1145.9688 | 122.8088 | -61.2946 | 61.2442 | 0.057526 | 0.00023916 | 0.0043088 | -0.0022943 | 0.061038 | -0.00071986 | 0.069635 | -61.29 | 61.1938 | -61.5921 | -61.5051 | 60.2966 | -1.7761 | -0.71411 | -0.45319 | 61.1984 | -61.5829 | -0.29755 | -0.050354 | 0.004578 | -0.21057 | -0.94757 | -0.28839 | -0.045777 | 0.30212 | 60.5804 | 60.8414 | 121.5912 | 122.4884 | 0.004578 | 122.493 | 59.5184 | -0.28839 | 122.4884 | 0.004578 | 59.5184 | 121.5912 | 122.493 | -122.8363 | -122.8271
1146.9062 | 122.8043 | -61.5555 | 60.9924 | 0.095673 | 0.00066656 | 0.001959 | -0.0033625 | 0.061679 | -0.0011471 | 0.067926 | -61.6928 | 60.8963 | -61.8942 | -61.7477 | 59.8618 | -1.6754 | -0.70496 | -0.40283 | 60.9421 | -61.8393 | -0.33875 | -0.096131 | -0.13733 | -0.19226 | -1.1307 | -0.28381 | -0.050354 | 0.20142 | 60.8505 | 61.1526 | 121.4172 | 122.4518 | -0.13733 | 122.4976 | 59.8801 | -0.28381 | 122.4518 | -0.13733 | 59.8801 | 121.4172 | 122.4976 | -122.8867 | -122.8317
1147.9688 | 122.7127 | -61.5967 | 61.0107 | 0.21774 | 0.0034436 | 0.0068722 | 0.0071051 | 0.06232 | -0.0047787 | 0.069207 | -61.6882 | 60.9787 | -61.8942 | -61.7157 | 59.6878 | -1.8585 | -0.53101 | -0.45319 | 60.9695 | -61.8576 | -0.29755 | -0.032043 | -0.091552 | -0.11902 | -1.3229 | -0.26093 | -0.041199 | 0.20599 | 61.0657 | 61.1435 | 121.2845 | 122.5754 | -0.091552 | 122.5662 | 59.7382 | -0.26093 | 122.5754 | -0.091552 | 59.7382 | 121.2845 | 122.5662 | -122.905 | -122.8683
1148.9062 | 122.8729 | -61.5738 | 60.9558 | -0.17899 | 0.0013074 | 0.0060178 | 0.0004827 | 0.065097 | -0.00050626 | 0.067926 | -61.6241 | 60.8551 | -61.8805 | -61.5829 | 59.903 | -1.7395 | -0.74158 | -0.24261 | 60.9055 | -61.8301 | -0.3067 | -0.10071 | -0.050354 | -0.009155 | -1.0529 | -0.25635 | -0.050354 | 0.25635 | 60.8322 | 61.3312 | 121.4767 | 122.4289 | -0.050354 | 122.4792 | 59.8343 | -0.25635 | 122.4289 | -0.050354 | 59.8343 | 121.4767 | 122.4792 | -122.8363 | -122.7859
1149.9688 | 122.8638 | -61.496 | 61.0107 | 0.16434 | 0.0023756 | 0.0060178 | 0.0032599 | 0.063602 | -0.0034971 | 0.06643 | -61.5372 | 60.9787 | -61.7798 | -61.6516 | 59.9625 | -1.8814 | -0.82398 | -0.33875 | 60.9833 | -61.7706 | -0.28381 | -0.032043 | -0.041198 | -0.15564 | -1.0483 | -0.27466 | -0.027466 | 0.24261 | 60.672 | 61.1572 | 121.4584 | 122.4747 | -0.041198 | 122.4792 | 59.6146 | -0.27466 | 122.4747 | -0.041198 | 59.6146 | 121.4584 | 122.4792 | -122.7905 | -122.7814
1150.9062 | 122.8043 | -61.528 | 61.0107 | 0.12619 | 0.0030164 | 0.0070858 | -0.0005853 | 0.061893 | -0.0011471 | 0.068139 | -61.6241 | 60.9467 | -61.8256 | -61.734 | 59.8892 | -1.7807 | -0.74616 | -0.3891 | 60.9558 | -61.8073 | -0.29755 | -0.064087 | -0.096131 | -0.20599 | -1.1215 | -0.27924 | -0.054931 | 0.20142 | 60.7819 | 61.1389 | 121.4172 | 122.4747 | -0.096131 | 122.4838 | 59.7473 | -0.27924 | 122.4747 | -0.096131 | 59.7473 | 121.4172 | 122.4838 | -122.8363 | -122.818
1151.9531 | 122.818 | -61.6287 | 60.91 | -0.041657 | 0.0019482 | -0.0010318 | -0.0020807 | 0.061466 | -0.00029266 | 0.067712 | -61.7661 | 60.8139 | -61.9537 | -61.8393 | 59.7336 | -1.5244 | -0.737 | -0.28839 | 60.8368 | -61.9217 | -0.32501 | -0.09613 | -0.13733 | -0.21057 | -1.1765 | -0.29297 | -0.073242 | 0.18768 | 60.8917 | 61.3403 | 121.3623 | 122.4426 | -0.13733 | 122.4655 | 60.1044 | -0.29297 | 122.4426 | -0.13733 | 60.1044 | 121.3623 | 122.4655 | -122.8638 | -122.8317
1152.9062 | 122.7768 | -61.5143 | 60.9833 | 0.11856 | 0.00023916 | 0.0023862 | -0.0020807 | 0.05997 | -0.00029266 | 0.067071 | -61.6562 | 60.9055 | -61.8668 | -61.7477 | 59.8755 | -1.4053 | -0.58594 | -0.31128 | 60.9512 | -61.8164 | -0.35248 | -0.077819 | -0.14191 | -0.23346 | -1.1078 | -0.30212 | -0.032043 | 0.21057 | 60.9283 | 61.203 | 121.3898 | 122.4197 | -0.14191 | 122.4655 | 60.1089 | -0.30212 | 122.4197 | -0.14191 | 60.1089 | 121.3898 | 122.4655 | -122.85 | -122.7997
1153.9531 | 122.85 | -61.5189 | 60.997 | -0.58334 | 0.0034436 | 0.005377 | 0.0011237 | 0.062961 | -0.0020017 | 0.066644 | -61.5875 | 60.9192 | -61.8393 | -61.6882 | 59.9075 | -1.2543 | -0.83313 | -0.3067 | 60.9558 | -61.8027 | -0.32043 | -0.07782 | -0.068664 | -0.16937 | -1.0895 | -0.28381 | -0.041198 | 0.25177 | 60.6857 | 61.2122 | 121.4264 | 122.438 | -0.068664 | 122.4747 | 60.2646 | -0.28381 | 122.438 | -0.068664 | 60.2646 | 121.4264 | 122.4747 | -122.8363 | -122.7997
1154.9219 | 122.7768 | -61.6562 | 60.965 | -0.21713 | 0.0040846 | 0.0055906 | 0.0009101 | 0.063388 | -0.0028561 | 0.067498 | -61.7661 | 60.9009 | -61.9812 | -61.8851 | 59.6695 | -1.4145 | -0.56305 | -0.29297 | 60.8871 | -61.9629 | -0.32501 | -0.064087 | -0.10986 | -0.22888 | -1.2955 | -0.3067 | -0.07782 | 0.21515 | 61.0931 | 61.3632 | 121.3257 | 122.5571 | -0.10986 | 122.5433 | 60.2417 | -0.3067 | 122.5571 | -0.10986 | 60.2417 | 121.3257 | 122.5433 | -122.9462 | -122.9279
1155.9688 | 122.8363 | -61.7752 | 60.7315 | 0.20248 | 0.0051526 | 0.0043088 | 0.0019781 | 0.064456 | 0.00034814 | 0.067071 | -61.8301 | 60.6995 | -62.0956 | -61.9308 | 59.5139 | -1.3092 | -0.84686 | -0.23804 | 60.6995 | -62.0361 | -0.32043 | -0.032043 | -0.054931 | -0.15564 | -1.2177 | -0.26093 | -0.032043 | 0.2655 | 60.9283 | 61.5372 | 121.2891 | 122.4747 | -0.054931 | 122.4747 | 60.466 | -0.26093 | 122.4747 | -0.054931 | 60.466 | 121.2891 | 122.4747 | -122.8271 | -122.7676
1156.9062 | 122.7814 | -61.94 | 60.5621 | -0.034027 | 0.0042982 | 0.0034544 | -0.0022943 | 0.06232 | -0.0013609 | 0.065149 | -62.0544 | 60.5255 | -62.2559 | -62.1414 | 59.3079 | -1.2314 | -0.58594 | -0.16022 | 60.5667 | -62.2009 | -0.31586 | -0.036621 | -0.11444 | -0.20142 | -1.2543 | -0.26093 | 0.004577 | 0.20142 | 61.3541 | 61.7798 | 121.2479 | 122.4655 | -0.11444 | 122.5067 | 60.7086 | -0.26093 | 122.4655 | -0.11444 | 60.7086 | 121.2479 | 122.5067 | -122.818 | -122.7631
1157.9531 | 122.7127 | -61.6516 | 60.9009 | 0.1796 | 0.0042982 | 0.010077 | 0.0030463 | 0.064456 | -0.00093346 | 0.066858 | -61.7111 | 60.8505 | -61.9766 | -61.8713 | 59.7427 | -1.2863 | -0.68665 | -0.36621 | 60.8917 | -61.9492 | -0.32501 | -0.050354 | -0.05951 | -0.21973 | -1.1581 | -0.29755 | -0.009155 | 0.2655 | 60.965 | 61.2854 | 121.3943 | 122.5021 | -0.05951 | 122.5433 | 60.3653 | -0.29755 | 122.5021 | -0.05951 | 60.3653 | 121.3943 | 122.5433 | -122.8775 | -122.85
1158.9062 | 122.7951 | -61.821 | 60.7132 | 1.2325 | 2.5564e-05 | 0.0040952 | -0.0044305 | 0.062107 | -0.0017881 | 0.069207 | -61.9217 | 60.6308 | -62.114 | -62.027 | 59.4864 | -1.1993 | -0.737 | -0.32044 | 60.672 | -62.0911 | -0.29297 | -0.082398 | -0.10071 | -0.20599 | -1.2268 | -0.27008 | -0.041199 | 0.19226 | 61.084 | 61.5005 | 121.3074 | 122.4518 | -0.10071 | 122.493 | 60.6216 | -0.27008 | 122.4518 | -0.10071 | 60.6216 | 121.3074 | 122.493 | -122.8271 | -122.8043
1159.9688 | 122.8088 | -61.8484 | 60.7132 | -0.018768 | 0.0030164 | 0.005377 | -0.0014399 | 0.062107 | -0.00093346 | 0.06878 | -61.9263 | 60.6674 | -62.1368 | -62.027 | 59.4543 | -1.0986 | -0.75531 | -0.29755 | 60.6491 | -62.1323 | -0.28839 | -0.045777 | -0.07782 | -0.17853 | -1.2589 | -0.28381 | -0.064087 | 0.21057 | 61.0931 | 61.5509 | 121.3028 | 122.5159 | -0.07782 | 122.4976 | 60.7498 | -0.28381 | 122.5159 | -0.07782 | 60.7498 | 121.3028 | 122.4976 | -122.85 | -122.8455
1160.9062 | 122.8455 | -61.7294 | 60.7498 | 0.27115 | 0.0030164 | 0.0032406 | 0.0036871 | 0.063602 | -0.00029266 | 0.069635 | -61.7935 | 60.6766 | -62.0636 | -61.9217 | 59.5871 | -1.1993 | -0.88806 | -0.37994 | 60.7086 | -62.0499 | -0.33417 | -0.073242 | -0.064087 | -0.19226 | -1.1627 | -0.32044 | -0.041199 | 0.27008 | 60.8414 | 61.3495 | 121.3165 | 122.406 | -0.064087 | 122.438 | 60.5301 | -0.32044 | 122.406 | -0.064087 | 60.5301 | 121.3165 | 122.438 | -122.8134 | -122.7997
1161.9688 | 122.8363 | -62.0407 | 60.4568 | 0.057526 | 0.0030164 | 0.0083676 | 0.0049689 | 0.062534 | -0.0013609 | 0.066217 | -62.0865 | 60.4202 | -62.3611 | -62.1964 | 59.1797 | -1.2131 | -0.90637 | -0.41199 | 60.4019 | -62.3566 | -0.32044 | -0.036621 | -0.045777 | -0.15564 | -1.2772 | -0.31586 | -0.054931 | 0.27466 | 61.1343 | 61.6287 | 121.2204 | 122.4609 | -0.045777 | 122.4426 | 60.8276 | -0.31586 | 122.4609 | -0.045777 | 60.8276 | 121.2204 | 122.4426 | -122.818 | -122.8134
1162.9062 | 122.7997 | -62.1506 | 60.3882 | 0.18723 | 0.0055798 | 0.00024998 | -0.0018671 | 0.062534 | -0.0013609 | 0.069848 | -62.2147 | 60.3195 | -62.4344 | -62.3383 | 59.0149 | -1.1307 | -0.83771 | -0.37079 | 60.3699 | -62.4207 | -0.28381 | -0.068665 | -0.064087 | -0.18768 | -1.3733 | -0.27008 | -0.018311 | 0.21973 | 61.3129 | 61.7798 | 121.1655 | 122.4701 | -0.064087 | 122.5204 | 61.0199 | -0.27008 | 122.4701 | -0.064087 | 61.0199 | 121.1655 | 122.5204 | -122.8226 | -122.8088
1163.9688 | 122.7219 | -62.1094 | 60.4843 | 0.11093 | 0.0042982 | 0.0092222 | 0.0051825 | 0.06467 | -0.00093346 | 0.067712 | -62.1964 | 60.4523 | -62.4115 | -62.3062 | 59.0561 | -1.181 | -0.77362 | -0.54932 | 60.4477 | -62.3932 | -0.30212 | -0.032043 | -0.086975 | -0.19684 | -1.4282 | -0.28381 | -0.036621 | 0.21515 | 61.3358 | 61.5601 | 121.1655 | 122.5616 | -0.086975 | 122.5571 | 60.9283 | -0.28381 | 122.5616 | -0.086975 | 60.9283 | 121.1655 | 122.5571 | -122.8958 | -122.8775
1164.9062 | 122.8455 | -62.0865 | 60.4385 | -0.18662 | 0.002162 | 0.0077268 | -0.0014399 | 0.062534 | -0.00093346 | 0.067926 | -62.0956 | 60.4156 | -62.3566 | -62.2238 | 59.1202 | -0.71869 | -0.77362 | -0.22888 | 60.4019 | -62.352 | -0.27008 | -0.022889 | -0.009155 | -0.13733 | -1.3184 | -0.2655 | -0.036621 | 0.26093 | 61.3129 | 61.8576 | 121.2067 | 122.5021 | -0.009155 | 122.4884 | 61.3678 | -0.2655 | 122.5021 | -0.009155 | 61.3678 | 121.2067 | 122.4884 | -122.7951 | -122.7905
1165.9688 | 122.8317 | -62.1414 | 60.347 | 0.27115 | 0.0019482 | 0.0043088 | 0.0039007 | 0.063816 | -0.0028561 | 0.067712 | -62.1918 | 60.3378 | -62.471 | -62.3245 | 59.0012 | -0.37537 | -0.89722 | -0.33417 | 60.3333 | -62.439 | -0.32959 | -0.009155 | -0.050354 | -0.18311 | -1.3458 | -0.29755 | -0.013733 | 0.27924 | 61.2442 | 61.8073 | 121.1426 | 122.4792 | -0.050354 | 122.4747 | 61.7661 | -0.29755 | 122.4792 | -0.050354 | 61.7661 | 121.1426 | 122.4747 | -122.818 | -122.7859
1166.9062 | 122.8546 | -62.1918 | 60.3195 | 0.24826 | 0.0030164 | 0.0090086 | -0.0022943 | 0.064029 | -0.0017881 | 0.067071 | -62.2101 | 60.2829 | -62.4573 | -62.3199 | 58.9325 | -0.24719 | -0.91095 | -0.27008 | 60.2692 | -62.471 | -0.2655 | -0.036621 | -0.018311 | -0.12817 | -1.387 | -0.27924 | -0.050354 | 0.24719 | 61.2808 | 61.9217 | 121.1243 | 122.4747 | -0.018311 | 122.4609 | 61.9446 | -0.27924 | 122.4747 | -0.018311 | 61.9446 | 121.1243 | 122.4609 | -122.7768 | -122.7905
1167.9688 | 122.7905 | -62.2009 | 60.3058 | 0.24063 | 0.0036572 | 0.0068722 | 0.0034735 | 0.064029 | -0.0017881 | 0.069207 | -62.1872 | 60.2966 | -62.471 | -62.3428 | 58.9371 | 0.12817 | -0.86517 | -0.39825 | 60.2829 | -62.4664 | -0.27008 | -0.009155 | 0.013733 | -0.14191 | -1.3687 | -0.2655 | -0.022888 | 0.28381 | 61.3358 | 61.8027 | 121.138 | 122.4976 | 0.013733 | 122.4838 | 62.3291 | -0.2655 | 122.4976 | 0.013733 | 62.3291 | 121.138 | 122.4838 | -122.7768 | -122.7722
1168.9062 | 122.7951 | -62.1826 | 60.3653 | 0.16434 | 0.004939 | 0.0062314 | -0.0027215 | 0.062534 | -0.0011471 | 0.06878 | -62.2284 | 60.3699 | -62.4573 | -62.3474 | 58.9279 | 0.17853 | -0.75073 | -0.45319 | 60.3378 | -62.471 | -0.27466 | 0.004578 | -0.045777 | -0.16479 | -1.4374 | -0.28839 | -0.027465 | 0.22888 | 61.4319 | 61.7294 | 121.1105 | 122.5525 | -0.045777 | 122.5204 | 62.3611 | -0.28839 | 122.5525 | -0.045777 | 62.3611 | 121.1105 | 122.5204 | -122.8226 | -122.8363
1169.9688 | 122.7036 | -62.2604 | 60.2966 | 0.072784 | 0.0025892 | 0.0045224 | 0.0060369 | 0.063602 | -0.0039243 | 0.069421 | -62.3245 | 60.2966 | -62.5671 | -62.4481 | 58.7402 | 0.55847 | -0.67749 | -0.67749 | 60.2829 | -62.558 | -0.3067 | 0 | -0.064087 | -0.18768 | -1.5564 | -0.29755 | -0.013733 | 0.24262 | 61.5829 | 61.5829 | 121.0007 | 122.5571 | -0.064087 | 122.5433 | 62.8189 | -0.29755 | 122.5571 | -0.064087 | 62.8189 | 121.0007 | 122.5433 | -122.8638 | -122.8546
1170.9062 | 117.0547 | -59.6741 | 57.0099 | 0.15671 | 0.0025892 | 0.0068722 | 6.9253 | 0.0033602 | -0.012683 | 7.0079 | -59.7198 | 57.0236 | -59.935 | 20.8466 | 40.86 | 1.2497 | -0.49439 | -0.009155 | 39.6194 | -42.7551 | -0.26093 | 0.013733 | -0.045777 | 80.5206 | -16.1499 | 16.9189 | -17.3904 | 0.21515 | 59.1797 | 59.6649 | 100.5341 | 116.6977 | -0.045777 | 99.2935 | 60.9238 | 16.9189 | 116.6977 | -0.045777 | 60.9238 | 100.5341 | 99.2935 | -116.9449 | -99.765
1171.9531 | 122.4426 | -63.0524 | 59.0195 | 0.21011 | 0.0030164 | 0.0049496 | -0.0067803 | -0.001553 | 0.00034814 | -0.0053469 | -63.0066 | 58.9966 | -63.382 | 59.1934 | 57.7469 | 2.5497 | -1.7303 | -0.90637 | 59.0103 | -63.3453 | -0.32959 | -0.022888 | 0.045776 | 122.2458 | -1.2726 | -0.29297 | -0.009155 | 0.37537 | 61.322 | 62.146 | 120.7993 | 122.0489 | 0.045776 | 122.0627 | 65.6021 | -0.29297 | 122.0489 | 0.045776 | 65.6021 | 120.7993 | 122.0627 | -122.4014 | -122.3648
1172.9062 | 122.5754 | -65.6754 | 56.4926 | 0.18723 | 0.00323 | 0.0028134 | -0.0005853 | -0.0024076 | -0.00029266 | -0.0034243 | -65.6891 | 56.5109 | -65.9866 | 56.6986 | 55.1239 | 1.9043 | -1.6342 | -1.2817 | 56.4377 | -66.0141 | -0.31128 | 0.01831 | -0.013733 | 122.374 | -1.3687 | -0.33875 | -0.054932 | 0.29755 | 64.0411 | 64.3936 | 120.7993 | 122.1863 | -0.013733 | 122.113 | 67.5797 | -0.33875 | 122.1863 | -0.013733 | 67.5797 | 120.7993 | 122.113 | -122.4792 | -122.5067
1173.9531 | 122.58 | -66.1148 | 56.0898 | 0.40085 | 0.0045118 | 0.0045224 | -0.0003717 | -0.003903 | -0.00071986 | -0.0023563 | -66.1606 | 56.044 | -66.4627 | 56.2958 | 54.6707 | 1.8448 | -1.2634 | -1.0712 | 56.0532 | -66.4352 | -0.3479 | -0.045777 | -0.045776 | 122.4106 | -1.4191 | -0.32044 | -0.036621 | 0.30213 | 64.8514 | 65.0436 | 120.7855 | 122.1588 | -0.045776 | 122.168 | 67.9596 | -0.32044 | 122.1588 | -0.045776 | 67.9596 | 120.7855 | 122.168 | -122.5525 | -122.525
1174.9062 | 122.5937 | -66.0599 | 56.1905 | -0.011139 | -0.00061524 | 0.0040952 | -0.0065667 | -0.0028348 | -7.9062e-05 | -0.0027835 | -66.1102 | 56.1813 | -66.3528 | 56.4011 | 54.7714 | 2.1378 | -1.0574 | -1.0941 | 56.1768 | -66.3391 | -0.29297 | -0.009156 | -0.050354 | 122.4609 | -1.4191 | -0.27924 | -0.013733 | 0.24262 | 65.0024 | 64.9658 | 120.8313 | 122.2412 | -0.050354 | 122.2366 | 68.1976 | -0.27924 | 122.2412 | -0.050354 | 68.1976 | 120.8313 | 122.2366 | -122.5433 | -122.5296
1175.9688 | 122.5204 | -65.863 | 56.4285 | 0.21011 | 0.004939 | 0.010717 | 0.0036871 | -0.0026212 | 0.0020571 | -0.0027835 | -65.9409 | 56.4514 | -66.1926 | 56.5201 | 54.8447 | 2.3071 | -1.0757 | -1.2726 | 56.4148 | -66.2109 | -0.32959 | 0.022888 | -0.07782 | 122.3831 | -1.5839 | -0.3479 | -0.013733 | 0.25177 | 64.7873 | 64.5905 | 120.7077 | 122.3145 | -0.07782 | 122.2778 | 68.1702 | -0.3479 | 122.3145 | -0.07782 | 68.1702 | 120.7077 | 122.2778 | -122.6212 | -122.6395
1176.9062 | 122.6761 | -65.5518 | 56.7032 | 0.29404 | 0.0051526 | 0.0043088 | 0.0011237 | -0.0011258 | -0.00071986 | -0.0047061 | -65.5609 | 56.6803 | -65.8356 | 56.9366 | 55.3253 | 2.7191 | -1.181 | -1.1948 | 56.7032 | -65.8859 | -0.28381 | -0.022888 | -0.009155 | 122.4884 | -1.3779 | -0.33417 | 0 | 0.27466 | 64.3707 | 64.357 | 120.8771 | 122.2321 | -0.009155 | 122.2549 | 68.2709 | -0.33417 | 122.2321 | -0.009155 | 68.2709 | 120.8771 | 122.2549 | -122.5388 | -122.5891
1177.9688 | 122.5433 | -65.5243 | 56.8085 | -1.1784 | 0.0040846 | 0.0043088 | 0.0039007 | -0.003262 | -0.0013609 | -0.00064734 | -65.5472 | 56.8451 | -65.8447 | 56.9778 | 55.2795 | 2.9663 | -1.0803 | -1.3321 | 56.8176 | -65.8585 | -0.32044 | 0.036621 | -0.022888 | 122.5021 | -1.5289 | -0.33417 | 0.009155 | 0.29755 | 64.444 | 64.1922 | 120.8038 | 122.3694 | -0.022888 | 122.3419 | 68.4906 | -0.33417 | 122.3694 | -0.022888 | 68.4906 | 120.8038 | 122.3419 | -122.6532 | -122.6669
1178.9062 | 122.6303 | -65.3412 | 56.9687 | 0.21011 | 0.0045118 | 0.0058042 | 0.0004827 | -0.00069859 | -0.0017881 | -0.0034243 | -65.4007 | 56.9916 | -65.6342 | 57.1609 | 55.5038 | 2.9251 | -1.2863 | -1.3184 | 56.9733 | -65.6525 | -0.29297 | 0.022888 | -0.059509 | 122.5021 | -1.4648 | -0.31128 | 0.004578 | 0.23346 | 64.0549 | 64.0228 | 120.845 | 122.3328 | -0.059509 | 122.3145 | 68.2663 | -0.31128 | 122.3328 | -0.059509 | 68.2663 | 120.845 | 122.3145 | -122.6028 | -122.6212
1179.9688 | 122.6303 | -65.181 | 57.1426 | 0.065155 | 0.00023916 | 0.0021726 | -0.0037897 | -0.003903 | -0.0017881 | -0.0025699 | -65.2725 | 57.1335 | -65.4694 | 57.3074 | 55.6641 | 2.9297 | -1.2497 | -1.4191 | 57.1381 | -65.4877 | -0.28839 | -0.009155 | -0.091553 | 122.4884 | -1.4786 | -0.3067 | -0.004577 | 0.19684 | 63.9313 | 63.7619 | 120.845 | 122.3145 | -0.091553 | 122.319 | 68.1107 | -0.3067 | 122.3145 | -0.091553 | 68.1107 | 120.845 | 122.319 | -122.612 | -122.6303
1180.9062 | 122.6166 | -65.4282 | 56.9778 | 0.21011 | 0.0055798 | 0.0055906 | 0.0036871 | -0.002194 | -0.00029266 | -0.0021427 | -65.4694 | 56.9778 | -65.712 | 57.0831 | 55.3574 | 3.1448 | -1.2451 | -1.5106 | 56.9595 | -65.744 | -0.28381 | 0 | -0.041198 | 122.5113 | -1.6205 | -0.31586 | -0.01831 | 0.24262 | 64.183 | 63.9175 | 120.7855 | 122.406 | -0.041198 | 122.3877 | 68.573 | -0.31586 | 122.406 | -0.041198 | 68.573 | 120.7855 | 122.3877 | -122.6898 | -122.7219
1181.9531 | 122.5754 | -65.3641 | 57.019 | -0.018768 | 0.0051526 | 0.0096494 | 0.0032599 | -0.002194 | -0.0020017 | -0.0015017 | -65.3641 | 57.0511 | -65.6662 | 57.1655 | 55.4581 | 3.273 | -1.9455 | -1.593 | 57.0374 | -65.6845 | -0.30212 | 0.032043 | 0 | 122.5296 | -1.561 | -0.32043 | 0.018311 | 0.30212 | 63.4186 | 63.7711 | 120.8221 | 122.4152 | 0 | 122.4014 | 68.6371 | -0.32043 | 122.4152 | 0 | 68.6371 | 120.8221 | 122.4014 | -122.6852 | -122.7036
1182.9062 | 122.6807 | -65.5884 | 56.7719 | 0.12619 | 0.0036572 | 0.0038816 | -0.0025079 | -0.0041166 | -0.0015745 | -0.0036379 | -65.6204 | 56.7535 | -65.8905 | 56.9641 | 55.2521 | 3.1677 | -1.0757 | -1.6113 | 56.749 | -65.9042 | -0.30212 | -0.018311 | -0.032043 | 122.5525 | -1.5198 | -0.31586 | -0.022889 | 0.27008 | 64.5126 | 63.9771 | 120.8405 | 122.3419 | -0.032043 | 122.3373 | 68.7561 | -0.31586 | 122.3419 | -0.032043 | 68.7561 | 120.8405 | 122.3373 | -122.6624 | -122.6761
1183.9688 | 122.5708 | -65.8356 | 56.6025 | -0.21713 | 0.0045118 | 0.0096494 | 0.0015509 | -0.0043302 | -0.00093346 | -0.0017153 | -65.8676 | 56.5933 | -66.1789 | 56.6895 | 54.9225 | 3.3829 | -0.83313 | -1.6434 | 56.6254 | -66.1606 | -0.34332 | -0.009155 | -0.032044 | 122.525 | -1.68 | -0.32501 | 0.022888 | 0.31128 | 65.0024 | 64.1922 | 120.7581 | 122.4289 | -0.032044 | 122.4609 | 69.2184 | -0.32501 | 122.4289 | -0.032044 | 69.2184 | 120.7581 | 122.4609 | -122.7814 | -122.7631
1184.9062 | 122.6715 | -65.831 | 56.6071 | -0.011139 | 0.00045296 | 0.001959 | -0.0044305 | -0.0036892 | -0.0020017 | -0.0023563 | -65.8813 | 56.5018 | -66.124 | 56.7535 | 55.0507 | 3.4744 | -0.92926 | -1.4648 | 56.5613 | -66.0736 | -0.29297 | -0.10529 | -0.050354 | 122.5845 | -1.5564 | -0.24261 | -0.045777 | 0.24261 | 64.9017 | 64.3662 | 120.8817 | 122.3328 | -0.050354 | 122.3923 | 69.3054 | -0.24261 | 122.3328 | -0.050354 | 69.3054 | 120.8817 | 122.3923 | -122.731 | -122.6807
1185.9688 | 122.6028 | -66.0782 | 56.3736 | 0.027008 | 0.0040846 | 0.0051632 | 0.0064643 | -0.0028348 | 0.0012027 | -0.0049197 | -66.0919 | 56.3736 | -66.3574 | 56.4331 | 54.7028 | 3.4058 | -0.74158 | -1.3733 | 56.3278 | -66.4352 | -0.27924 | 0 | -0.013733 | 122.5113 | -1.6708 | -0.35706 | -0.045776 | 0.2655 | 65.3366 | 64.7049 | 120.7809 | 122.4518 | -0.013733 | 122.406 | 69.4839 | -0.35706 | 122.4518 | -0.013733 | 69.4839 | 120.7809 | 122.406 | -122.731 | -122.8088
1186.9062 | 122.6532 | -66.4032 | 55.9982 | 0.24826 | 0.0028028 | 0.0066586 | 5.5496e-05 | -0.0013394 | -0.00050626 | -0.0034243 | -66.3986 | 55.9662 | -66.7145 | 56.1996 | 54.4922 | 3.6804 | -0.97504 | -1.387 | 55.9753 | -66.7007 | -0.31128 | -0.032043 | 0.004577 | 122.6028 | -1.506 | -0.29755 | -0.022888 | 0.31586 | 65.4282 | 65.0162 | 120.8954 | 122.3694 | 0.004577 | 122.3785 | 70.0836 | -0.29755 | 122.3694 | 0.004577 | 70.0836 | 120.8954 | 122.3785 | -122.7127 | -122.699
1187.9062 | 122.6578 | -66.7694 | 55.6549 | 0.1796 | 0.004939 | 0.0051632 | 0.0009101 | -0.0013394 | 0.0018435 | -0.00086094 | -66.7923 | 55.6778 | -67.0624 | 55.7785 | 54.0573 | 3.6621 | -0.91095 | -1.5427 | 55.6458 | -67.099 | -0.29297 | 0.022888 | -0.022888 | 122.5479 | -1.5976 | -0.32959 | -0.009155 | 0.27008 | 65.8585 | 65.2267 | 120.8267 | 122.4472 | -0.022888 | 122.4152 | 70.4315 | -0.32959 | 122.4472 | -0.022888 | 70.4315 | 120.8267 | 122.4152 | -122.7173 | -122.7539
1188.9688 | 122.5983 | -66.9388 | 55.5267 | 0.049896 | 0.0053662 | 0.0043088 | 0.0062507 | -0.001553 | -0.0011471 | -0.0019289 | -66.9708 | 55.5176 | -67.2546 | 55.5908 | 53.8971 | 3.7857 | -0.77362 | -1.6251 | 55.4993 | -67.2638 | -0.31586 | -0.009155 | -0.032043 | 122.5296 | -1.6296 | -0.32501 | -0.027465 | 0.28381 | 66.1652 | 65.3137 | 120.8359 | 122.4564 | -0.032043 | 122.4381 | 70.7245 | -0.32501 | 122.4564 | -0.032043 | 70.7245 | 120.8359 | 122.4381 | -122.7814 | -122.7905
1189.9062 | 122.7081 | -66.9342 | 55.4901 | -0.049286 | 0.0013074 | 0.0038816 | -0.0065667 | -0.002194 | -7.9062e-05 | -0.0015017 | -67.0166 | 55.4581 | -67.2592 | 55.6366 | 53.9703 | 4.0192 | -0.89722 | -1.5106 | 55.4993 | -67.2089 | -0.32501 | -0.032043 | -0.082398 | 122.5708 | -1.5198 | -0.27466 | 0.009156 | 0.24261 | 66.037 | 65.4236 | 120.9045 | 122.3923 | -0.082398 | 122.4335 | 70.9534 | -0.27466 | 122.3923 | -0.082398 | 70.9534 | 120.9045 | 122.4335 | -122.7493 | -122.699
1190.9531 | 122.6624 | -67.3462 | 55.1056 | 0.18723 | 0.0047254 | 0.0049496 | 0.0041143 | -0.003903 | 0.00034814 | -0.0021427 | -67.4103 | 55.0827 | -67.6575 | 55.1834 | 53.4897 | 3.9688 | -0.87433 | -1.6388 | 55.0781 | -67.6895 | -0.31128 | -0.022888 | -0.064087 | 122.5296 | -1.6159 | -0.34332 | -0.027466 | 0.24719 | 66.4719 | 65.7074 | 120.8359 | 122.4289 | -0.064087 | 122.4243 | 71.315 | -0.34332 | 122.4289 | -0.064087 | 71.315 | 120.8359 | 122.4243 | -122.7631 | -122.7951
1191.9062 | 122.7219 | -67.6117 | 54.7623 | 0.072784 | 0.0038708 | 0.004736 | 5.5496e-05 | -0.0024076 | -0.0028561 | -0.0023563 | -67.662 | 54.744 | -67.9276 | 54.9545 | 53.2196 | 4.0741 | -1.0025 | -1.5656 | 54.7897 | -67.9276 | -0.31586 | -0.01831 | -0.050354 | 122.5662 | -1.5427 | -0.31586 | 0.027466 | 0.2655 | 66.6092 | 66.0461 | 120.8313 | 122.3557 | -0.050354 | 122.4014 | 71.6858 | -0.31586 | 122.3557 | -0.050354 | 71.6858 | 120.8313 | 122.4014 | -122.6898 | -122.6898
1192.9531 | 122.6395 | -67.7216 | 54.776 | 0.15671 | 0.0030164 | 0.006445 | 0.0045417 | -0.0041166 | -0.0013609 | -0.0025699 | -67.7261 | 54.808 | -67.9733 | 54.863 | 53.1235 | 3.9093 | -0.87891 | -1.7715 | 54.744 | -68.0511 | -0.25177 | 0.032043 | -0.004577 | 122.5845 | -1.6525 | -0.32959 | -0.032043 | 0.24719 | 66.8427 | 65.95 | 120.845 | 122.5296 | -0.004577 | 122.4655 | 71.6309 | -0.32959 | 122.5296 | -0.004577 | 71.6309 | 120.845 | 122.4655 | -122.7493 | -122.8271
1193.9062 | 122.7539 | -67.5476 | 54.8401 | 0.17197 | 0.00323 | 0.0062314 | 0.0017645 | -0.0045438 | -0.00093346 | -0.0015017 | -67.5339 | 54.8355 | -67.8497 | 55.0232 | 53.3386 | 3.978 | -0.93384 | -1.6388 | 54.8218 | -67.8726 | -0.30212 | -0.004578 | 0.013732 | 122.5708 | -1.5015 | -0.32501 | -0.018311 | 0.31586 | 66.6138 | 65.9088 | 120.8862 | 122.3831 | 0.013732 | 122.3694 | 71.5256 | -0.32501 | 122.3831 | 0.013732 | 71.5256 | 120.8862 | 122.3694 | -122.6898 | -122.7127
1194.9688 | 122.7448 | -68.2068 | 54.2038 | -0.034027 | 0.0019482 | 0.0051632 | -0.0046441 | -0.0034756 | 0.0016299 | -0.0025699 | -68.2571 | 54.1397 | -68.541 | 54.4098 | 52.739 | 3.8956 | -0.94299 | -1.6434 | 54.1992 | -68.4952 | -0.33417 | -0.064087 | -0.050354 | 122.6166 | -1.4648 | -0.28839 | -0.004577 | 0.28381 | 67.2638 | 66.5634 | 120.9457 | 122.3465 | -0.050354 | 122.406 | 72.1024 | -0.28839 | 122.3465 | -0.050354 | 72.1024 | 120.9457 | 122.406 | -122.7448 | -122.699
1195.9062 | 122.7493 | -68.0328 | 54.3686 | 0.13382 | 0.00323 | 0.00067718 | 0.0019781 | -0.0051846 | -0.0020017 | -0.0044925 | -68.0054 | 54.3777 | -68.3075 | 54.5425 | 52.8442 | 3.8177 | -1.0941 | -1.8173 | 54.3457 | -68.3762 | -0.27466 | 0.009156 | 0.027466 | 122.5754 | -1.5244 | -0.34332 | -0.022888 | 0.30212 | 66.9388 | 66.2155 | 120.8771 | 122.4106 | 0.027466 | 122.3785 | 71.8506 | -0.34332 | 122.4106 | 0.027466 | 71.8506 | 120.8771 | 122.3785 | -122.6761 | -122.7448
1196.9688 | 122.6395 | -68.5593 | 53.9108 | 0.27115 | 0.0030164 | 0.0045224 | 0.0068915 | -0.0036892 | -0.0013609 | -0.0019289 | -68.6508 | 53.8651 | -68.9255 | 53.9383 | 52.1851 | 3.6667 | -1.03 | -2.0508 | 53.8422 | -68.9117 | -0.36621 | -0.045777 | -0.091553 | 122.4976 | -1.7258 | -0.35248 | -0.068665 | 0.27466 | 67.5293 | 66.5085 | 120.7443 | 122.4243 | -0.091553 | 122.4014 | 72.226 | -0.35248 | 122.4243 | -0.091553 | 72.226 | 120.7443 | 122.4014 | -122.8363 | -122.8226
1197.9062 | 122.7585 | -69.1635 | 53.2379 | 0.14145 | 0.0034436 | 0.0058042 | 0.0015509 | -0.0024076 | -0.00029266 | -0.0023563 | -69.1635 | 53.2196 | -69.4885 | 53.4485 | 51.7639 | 3.6758 | -1.1536 | -1.9867 | 53.2471 | -69.4748 | -0.32501 | -0.018311 | 0 | 122.612 | -1.474 | -0.31128 | 0.009155 | 0.32501 | 68.0099 | 67.1768 | 120.9274 | 122.3831 | 0 | 122.4106 | 72.8394 | -0.31128 | 122.3831 | 0 | 72.8394 | 120.9274 | 122.4106 | -122.7264 | -122.7127
1198.9531 | 122.7036 | -69.4199 | 53.0731 | -0.18662 | 0.006648 | 0.0070858 | 0.0041143 | -0.0028348 | -0.00029266 | -0.0038515 | -69.3832 | 53.1052 | -69.7083 | 53.2288 | 51.4801 | 3.4973 | -0.93842 | -2.037 | 53.1097 | -69.7266 | -0.28839 | 0.032044 | 0.036621 | 122.6486 | -1.593 | -0.3067 | 0.036621 | 0.32501 | 68.4814 | 67.3828 | 120.9 | 122.525 | 0.036621 | 122.5296 | 72.9172 | -0.3067 | 122.525 | 0.036621 | 72.9172 | 120.9 | 122.5296 | -122.7814 | -122.7997
1199.9062 | 122.7264 | -69.6671 | 52.7618 | -0.3392 | 0.00323 | 0.005377 | -0.0027215 | -0.0043302 | -0.0011471 | -0.0015017 | -69.7449 | 52.7344 | -69.9509 | 52.9221 | 51.2604 | 3.5706 | -1.0849 | -2.1149 | 52.7802 | -69.9692 | -0.28381 | -0.027466 | -0.07782 | 122.5891 | -1.5015 | -0.30212 | 0.01831 | 0.20599 | 68.5822 | 67.5522 | 120.9274 | 122.4014 | -0.07782 | 122.4472 | 73.2376 | -0.30212 | 122.4014 | -0.07782 | 73.2376 | 120.9274 | 122.4472 | -122.7127 | -122.731
1200.9531 | 122.6761 | -70.1752 | 52.3453 | -0.17136 | 0.00323 | 0.0062314 | 0.0026191 | -0.0051846 | 0.00056194 | -0.0023563 | -70.2164 | 52.2903 | -70.5185 | 52.4048 | 50.7385 | 3.6072 | -0.88806 | -1.9409 | 52.3178 | -70.5002 | -0.34332 | -0.054932 | -0.041199 | 122.58 | -1.6068 | -0.32501 | -0.027466 | 0.30212 | 69.2871 | 68.2343 | 120.9137 | 122.4655 | -0.041199 | 122.493 | 73.7823 | -0.32501 | 122.4655 | -0.041199 | 73.7823 | 120.9137 | 122.493 | -122.8638 | -122.8455
1201.9062 | 122.7219 | -70.61 | 51.86 | 0.21011 | 0.0038708 | 0.0079404 | 0.0041143 | -0.0028348 | 0.0016299 | -0.00064734 | -70.61 | 51.8555 | -70.8893 | 52.0157 | 50.3403 | 3.5339 | -1.1078 | -1.9363 | 51.86 | -70.9122 | -0.27924 | -0.004577 | 0 | 122.6257 | -1.5198 | -0.30212 | 0 | 0.27924 | 69.5023 | 68.6737 | 120.9503 | 122.4655 | 0 | 122.4701 | 74.144 | -0.30212 | 122.4655 | 0 | 74.144 | 120.9503 | 122.4701 | -122.7493 | -122.7722
1202.9688 | 122.6624 | -70.9808 | 51.5213 | 0.14145 | 0.0030164 | 0.0058042 | 0.0024053 | -0.0017666 | -0.0028561 | -0.00021994 | -70.99 | 51.5305 | -71.2646 | 51.5945 | 49.8642 | 3.0899 | -1.149 | -2.1378 | 51.5488 | -71.3013 | -0.28381 | 0.009156 | -0.009155 | 122.5754 | -1.6571 | -0.32044 | 0.027466 | 0.27466 | 69.8318 | 68.8431 | 120.845 | 122.5113 | -0.009155 | 122.5296 | 74.0707 | -0.32044 | 122.5113 | -0.009155 | 74.0707 | 120.845 | 122.5296 | -122.7859 | -122.8226
1203.9062 | 122.7036 | -71.2143 | 51.178 | 0.1796 | 0.0023756 | 0.0087948 | -0.0012261 | -0.00069859 | -0.00029266 | -0.0019289 | -71.2509 | 51.1459 | -71.5713 | 51.4389 | 49.6262 | 3.5522 | -1.2817 | -2.0645 | 51.2329 | -71.5164 | -0.35706 | -0.032044 | -0.036622 | 122.6532 | -1.5518 | -0.30212 | 0.054931 | 0.32043 | 69.9326 | 69.1498 | 120.8405 | 122.3602 | -0.036622 | 122.4472 | 74.7665 | -0.30212 | 122.3602 | -0.036622 | 74.7665 | 120.8405 | 122.4472 | -122.7493 | -122.6944
1204.9688 | 122.6715 | -71.4661 | 50.9995 | 0.15671 | 0.0034436 | 0.0060178 | 0.0056097 | -0.0028348 | -0.00093346 | -0.0034243 | -71.5439 | 51.0132 | -71.7911 | 51.1963 | 49.4293 | 3.5202 | -0.9613 | -2.211 | 51.1185 | -71.7636 | -0.32501 | 0.013733 | -0.07782 | 122.6624 | -1.5701 | -0.29755 | 0.11902 | 0.24719 | 70.5048 | 69.2551 | 120.8954 | 122.4792 | -0.07782 | 122.5845 | 74.9863 | -0.29755 | 122.4792 | -0.07782 | 74.9863 | 120.8954 | 122.5845 | -122.7905 | -122.7631
1205.9219 | 122.7219 | -72.4182 | 50.0656 | -0.18662 | 2.5564e-05 | 0.0040952 | 5.5496e-05 | -0.003262 | 0.00013454 | -0.0019289 | -72.4182 | 49.9649 | -72.7615 | 50.2167 | 48.5413 | 3.6209 | -0.98419 | -1.8265 | 50.0336 | -72.7524 | -0.34332 | -0.10071 | 0 | 122.6349 | -1.5244 | -0.33417 | -0.032044 | 0.34332 | 71.434 | 70.5917 | 120.9595 | 122.3831 | 0 | 122.4518 | 76.0391 | -0.33417 | 122.3831 | 0 | 76.0391 | 120.9595 | 122.4518 | -122.8271 | -122.818
1206.9531 | 122.6257 | -72.5739 | 49.9374 | 0.042267 | 0.0045118 | 0.0075132 | 0.0066779 | -0.0017666 | -7.9062e-05 | -0.0049197 | -72.5601 | 49.9558 | -72.8302 | 50.0153 | 48.2254 | 3.0487 | -0.97961 | -2.124 | 49.9649 | -72.9309 | -0.25635 | 0.018311 | 0.013733 | 122.5891 | -1.712 | -0.35706 | 0.027466 | 0.27008 | 71.5942 | 70.4498 | 120.7993 | 122.5296 | 0.013733 | 122.5388 | 75.6226 | -0.35706 | 122.5296 | 0.013733 | 75.6226 | 120.7993 | 122.5388 | -122.7676 | -122.8683
1207.9062 | 122.7493 | -73.1873 | 49.2416 | 0.22537 | 0.0017346 | 0.0070858 | -0.0003717 | -0.0030484 | 0.00056194 | -0.0023563 | -73.1552 | 49.2004 | -73.494 | 49.4659 | 47.7081 | 3.0945 | -1.2817 | -2.3117 | 49.2508 | -73.5031 | -0.3067 | -0.041199 | 0.032044 | 122.6532 | -1.5335 | -0.31586 | 0.009155 | 0.33875 | 71.9055 | 70.8755 | 120.8954 | 122.3877 | 0.032044 | 122.438 | 76.2817 | -0.31586 | 122.3877 | 0.032044 | 76.2817 | 120.8954 | 122.438 | -122.7356 | -122.7448
1208.9688 | 122.7081 | -73.2239 | 49.2966 | 0.20248 | 0.0051526 | 0.0055906 | 0.0053961 | -0.001553 | 0.00056194 | -0.0032107 | -73.2834 | 49.2737 | -73.5672 | 49.2645 | 47.4197 | 3.154 | -1.6663 | -2.7924 | 49.1913 | -73.6404 | -0.34332 | -0.022888 | -0.059509 | 122.4884 | -1.8768 | -0.41656 | -0.10529 | 0.28381 | 71.5576 | 70.4315 | 120.6436 | 122.4976 | -0.059509 | 122.4152 | 76.3779 | -0.41656 | 122.4976 | -0.059509 | 76.3779 | 120.6436 | 122.4152 | -122.8638 | -122.937
1209.9062 | 122.7676 | -73.5489 | 48.8937 | 0.034637 | 2.5564e-05 | 0.0021726 | -0.0025079 | -0.0024076 | -0.00093346 | -0.0036379 | -73.6267 | 48.7885 | -73.8831 | 49.0265 | 47.2321 | 3.1586 | -1.3184 | -2.3392 | 48.88 | -73.8693 | -0.33417 | -0.10529 | -0.07782 | 122.5754 | -1.6617 | -0.32044 | -0.013733 | 0.25635 | 72.2305 | 71.2097 | 120.7809 | 122.3373 | -0.07782 | 122.4289 | 76.7075 | -0.32044 | 122.3373 | -0.07782 | 76.7075 | 120.7809 | 122.4289 | -122.7768 | -122.7631
1210.9688 | 122.7402 | -73.6816 | 48.8113 | 0.24063 | 0.0038708 | 0.0023862 | 0.0066779 | -0.003262 | 0.00013454 | -0.0012881 | -73.7778 | 48.7061 | -74.0433 | 48.88 | 47.0856 | 3.2639 | -1.4053 | -2.2797 | 48.761 | -74.0067 | -0.36163 | -0.10529 | -0.09613 | 122.5616 | -1.7258 | -0.32501 | -0.050354 | 0.2655 | 72.2763 | 71.402 | 120.7672 | 122.3877 | -0.09613 | 122.4426 | 76.9455 | -0.32501 | 122.3877 | -0.09613 | 76.9455 | 120.7672 | 122.4426 | -122.8546 | -122.818
1211.9062 | 122.7768 | -73.8281 | 48.6008 | -0.14847 | 0.0013074 | 0.004736 | 0.0026191 | -0.0019802 | 0.00013454 | -0.0038515 | -73.8464 | 48.5367 | -74.1852 | 48.7701 | 47.0627 | 3.4058 | -1.5427 | -2.211 | 48.5687 | -74.1714 | -0.35706 | -0.064087 | -0.018311 | 122.5983 | -1.5381 | -0.34332 | -0.032043 | 0.33875 | 72.2855 | 71.6171 | 120.8908 | 122.3648 | -0.018311 | 122.3969 | 77.2339 | -0.34332 | 122.3648 | -0.018311 | 77.2339 | 120.8908 | 122.3969 | -122.7859 | -122.7722
1212.9531 | 122.7402 | -74.1211 | 48.317 | 0.15671 | 0.001521 | 0.0040952 | 0.0011237 | -0.0047574 | -0.00050626 | -0.0049197 | -74.1302 | 48.262 | -74.4324 | 48.4817 | 46.7514 | 3.3051 | -1.6342 | -2.179 | 48.3032 | -74.4461 | -0.31128 | -0.054932 | -0.009155 | 122.6028 | -1.5656 | -0.32501 | -0.013733 | 0.30212 | 72.4869 | 71.9421 | 120.8725 | 122.3831 | -0.009155 | 122.4243 | 77.4261 | -0.32501 | 122.3831 | -0.009155 | 77.4261 | 120.8725 | 122.4243 | -122.7493 | -122.7631
1213.9062 | 122.7676 | -74.9634 | 47.4884 | 0.24826 | 0.0047254 | 0.0062314 | 0.0034735 | -0.003903 | -0.0011471 | -0.0029971 | -75.0504 | 47.4838 | -75.2289 | 47.7722 | 45.9412 | 3.2227 | -1.7761 | -2.3987 | 47.493 | -75.2838 | -0.2655 | -0.004577 | -0.086975 | 122.7356 | -1.5472 | -0.32043 | 0.004578 | 0.17853 | 73.1873 | 72.5647 | 120.9045 | 122.4472 | -0.086975 | 122.4564 | 78.186 | -0.32043 | 122.4472 | -0.086975 | 78.186 | 120.9045 | 122.4564 | -122.7173 | -122.7722
1214.9531 | 122.7493 | -75.2289 | 47.2366 | 0.22537 | 0.0025892 | 0.005377 | 0.0064643 | -0.0024076 | -0.0015745 | -0.0023563 | -75.2518 | 47.1909 | -75.5814 | 47.4106 | 45.6253 | 3.1219 | -1.68 | -2.4948 | 47.2229 | -75.5356 | -0.35248 | -0.045776 | -0.022888 | 122.6395 | -1.6113 | -0.3067 | -0.013733 | 0.32959 | 73.5489 | 72.7341 | 120.8542 | 122.4197 | -0.022888 | 122.4518 | 78.3508 | -0.3067 | 122.4197 | -0.022888 | 78.3508 | 120.8542 | 122.4518 | -122.818 | -122.7722
1215.9219 | 122.6532 | -75.6042 | 46.9666 | -0.10269 | 0.0034436 | -0.00017722 | 0.0019781 | -0.0047574 | -0.00050626 | -0.0021427 | -75.6912 | 46.8155 | -75.9521 | 47.0261 | 45.3003 | 2.861 | -1.5106 | -2.3346 | 46.962 | -75.9018 | -0.3479 | -0.15106 | -0.086975 | 122.6303 | -1.6663 | -0.29755 | -0.004578 | 0.26093 | 74.0936 | 73.2697 | 120.9045 | 122.4197 | -0.086975 | 122.5662 | 78.4653 | -0.29755 | 122.4197 | -0.086975 | 78.4653 | 120.9045 | 122.5662 | -122.9187 | -122.8683
1216.9688 | 122.7493 | -76.0254 | 46.4355 | 0.24826 | 0.0051526 | 0.0043088 | 0.0062507 | -0.0017666 | -0.0013609 | -0.0012881 | -75.9705 | 46.4951 | -76.2955 | 46.6187 | 44.8975 | 2.742 | -1.8494 | -2.6001 | 46.4722 | -76.3275 | -0.27008 | 0.059509 | 0.054932 | 122.644 | -1.5381 | -0.30212 | 0.036621 | 0.32501 | 74.176 | 73.4253 | 120.9229 | 122.5204 | 0.054932 | 122.4976 | 78.7674 | -0.30212 | 122.5204 | 0.054932 | 78.7674 | 120.9229 | 122.4976 | -122.731 | -122.7631
1217.9062 | 122.7859 | -76.68 | 45.7718 | 0.60684 | 0.00323 | 0.0066586 | 0.0006965 | -0.003262 | -0.0022153 | -0.0040653 | -76.593 | 45.7581 | -76.9684 | 45.9732 | 44.2703 | 2.7466 | -2.0325 | -2.6047 | 45.7901 | -76.9501 | -0.28839 | -0.013733 | 0.086975 | 122.6532 | -1.5015 | -0.27008 | 0.01831 | 0.37537 | 74.6475 | 74.0753 | 120.9503 | 122.4381 | 0.086975 | 122.4701 | 79.4266 | -0.27008 | 122.4381 | 0.086975 | 79.4266 | 120.9503 | 122.4701 | -122.7402 | -122.7219
1218.9688 | 122.6486 | -75.9521 | 46.5637 | 0.072784 | 0.0051526 | 0.0083676 | 0.0073187 | -0.001553 | -0.0017881 | -0.0034243 | -76.0254 | 46.4996 | -76.3367 | 46.5912 | 44.8105 | 2.774 | -1.7075 | -2.6779 | 46.55 | -76.3184 | -0.38452 | -0.064087 | -0.073243 | 122.5433 | -1.7532 | -0.36621 | -0.013733 | 0.31128 | 74.2447 | 73.2742 | 120.7626 | 122.4518 | -0.073243 | 122.5021 | 78.7262 | -0.36621 | 122.4518 | -0.073243 | 78.7262 | 120.7626 | 122.5021 | -122.9004 | -122.8821
1219.9062 | 122.8317 | -75.9247 | 46.5546 | -0.14847 | 0.0017346 | 0.0028134 | -0.0040033 | -0.0043302 | -0.0011471 | -0.0015017 | -75.856 | 46.5271 | -76.181 | 46.7377 | 44.8883 | 2.4307 | -1.9043 | -2.4445 | 46.5454 | -76.2085 | -0.25635 | -0.027465 | 0.068665 | 122.6624 | -1.6663 | -0.28381 | -0.009155 | 0.32501 | 74.0204 | 73.4802 | 120.813 | 122.4518 | 0.068665 | 122.4701 | 78.3554 | -0.28381 | 122.4518 | 0.068665 | 78.3554 | 120.813 | 122.4701 | -122.7356 | -122.7631
1220.9688 | 122.7859 | -76.1719 | 46.3165 | 0.22537 | 0.0040846 | 0.0060178 | 0.0039007 | -0.003903 | -0.0013609 | -0.0029971 | -76.1719 | 46.257 | -76.4923 | 46.4905 | 44.7098 | 2.0645 | -1.9409 | -2.5085 | 46.3165 | -76.474 | -0.32044 | -0.059509 | 0 | 122.6624 | -1.6067 | -0.30212 | 0 | 0.32044 | 74.231 | 73.6633 | 120.8817 | 122.4289 | 0 | 122.4884 | 78.2364 | -0.30212 | 122.4289 | 0 | 78.2364 | 120.8817 | 122.4884 | -122.8088 | -122.7905
1221.9062 | 122.7997 | -76.8997 | 45.5383 | -0.24002 | 0.001521 | 0.0087948 | 0.0036871 | -0.004971 | -0.00050626 | -0.0019289 | -76.8127 | 45.5658 | -77.1469 | 45.7809 | 43.9911 | 2.0599 | -2.124 | -2.7466 | 45.5475 | -77.2156 | -0.24719 | 0.027466 | 0.086975 | 122.6807 | -1.5472 | -0.31586 | 0.009155 | 0.33417 | 74.7757 | 74.1531 | 120.8908 | 122.4655 | 0.086975 | 122.4472 | 78.9597 | -0.31586 | 122.4655 | 0.086975 | 78.9597 | 120.8908 | 122.4472 | -122.6852 | -122.7539
1222.9531 | 122.6944 | -76.8906 | 45.6482 | 0.1796 | 0.0036572 | 0.0040952 | 0.0064643 | -0.0026212 | 0.00098914 | -0.0027835 | -76.9547 | 45.6024 | -77.2202 | 45.6573 | 43.8629 | 2.3621 | -1.9089 | -2.774 | 45.5978 | -77.2568 | -0.32959 | -0.045776 | -0.064087 | 122.5479 | -1.7853 | -0.36621 | -0.050354 | 0.2655 | 74.9817 | 74.1165 | 120.7535 | 122.493 | -0.064087 | 122.4884 | 79.2526 | -0.36621 | 122.493 | -0.064087 | 79.2526 | 120.7535 | 122.4884 | -122.8683 | -122.905
1223.9062 | 122.7859 | -76.973 | 45.5109 | 0.233 | 0.004939 | 0.0049496 | 0.0034735 | -0.0019802 | 0.0026981 | -0.0021427 | -76.9455 | 45.5154 | -77.2476 | 45.7214 | 43.9041 | 2.5818 | -1.8585 | -2.6688 | 45.5246 | -77.2659 | -0.27466 | 0.004578 | 0.027465 | 122.6944 | -1.6067 | -0.29297 | 0.013733 | 0.30212 | 75.1144 | 74.3042 | 120.8771 | 122.4884 | 0.027465 | 122.4976 | 79.5547 | -0.29297 | 122.4884 | 0.027465 | 79.5547 | 120.8771 | 122.4976 | -122.7585 | -122.7768
1224.9531 | 122.8455 | -77.0462 | 45.4147 | 0.21774 | 0.004939 | 0.010077 | 0.0051825 | -0.0024076 | 0.00034814 | -0.00086094 | -76.9775 | 45.4376 | -77.298 | 45.6528 | 43.8217 | 2.829 | -1.8768 | -2.829 | 45.4102 | -77.3804 | -0.25177 | 0.022888 | 0.068665 | 122.699 | -1.593 | -0.33417 | -0.004578 | 0.32044 | 75.1694 | 74.2172 | 120.8679 | 122.4838 | 0.068665 | 122.4564 | 79.8752 | -0.33417 | 122.4838 | 0.068665 | 79.8752 | 120.8679 | 122.4564 | -122.7127 | -122.7951
1225.9062 | 122.8317 | -76.4511 | 46.0236 | -0.087433 | 0.0019482 | 0.0055906 | -0.0029351 | -0.00668 | 0.00013454 | -0.0017153 | -76.4191 | 46.0373 | -76.7166 | 46.2296 | 44.5038 | 3.186 | -1.7303 | -2.5681 | 45.9961 | -76.7899 | -0.2655 | 0.013732 | 0.032044 | 122.6807 | -1.5198 | -0.33875 | -0.027466 | 0.29755 | 74.7208 | 73.8831 | 120.9549 | 122.4884 | 0.032044 | 122.4472 | 79.6371 | -0.33875 | 122.4884 | 0.032044 | 79.6371 | 120.9549 | 122.4472 | -122.7402 | -122.8134
1226.9531 | 122.7814 | -78.0167 | 44.4489 | 0.29404 | 0.0042982 | 0.005377 | 0.0073187 | -0.002194 | -7.9062e-05 | -0.0021427 | -77.9068 | 44.5038 | -78.2318 | 44.6823 | 42.9245 | 2.6184 | -2.0508 | -2.7512 | 44.458 | -78.3142 | -0.21515 | 0.054931 | 0.10986 | 122.699 | -1.5244 | -0.29755 | 0.009155 | 0.32501 | 75.9659 | 75.2655 | 120.9412 | 122.5204 | 0.10986 | 122.4747 | 80.6351 | -0.29755 | 122.5204 | 0.10986 | 80.6351 | 120.9412 | 122.4747 | -122.6807 | -122.7631
1227.9062 | 122.8043 | -78.1082 | 44.3573 | 0.20248 | 0.0034436 | 0.0077268 | 0.0066779 | -0.0041166 | -0.0011471 | -0.0025699 | -78.0762 | 44.3298 | -78.4287 | 44.4901 | 42.8009 | 2.4307 | -2.0737 | -2.7008 | 44.339 | -78.447 | -0.32044 | -0.027466 | 0.032043 | 122.5983 | -1.5564 | -0.33875 | -0.018311 | 0.35248 | 76.0345 | 75.4074 | 120.9091 | 122.438 | 0.032043 | 122.4472 | 80.5389 | -0.33875 | 122.438 | 0.032043 | 80.5389 | 120.9091 | 122.4472 | -122.786 | -122.8043
1228.9688 | 122.6761 | -78.4973 | 44.0186 | 0.057526 | 0.004939 | 0.009863 | 0.0066779 | -0.002194 | -0.00071986 | -0.0025699 | -78.4698 | 44.0552 | -78.8132 | 44.0918 | 42.3569 | 2.0966 | -2.0416 | -3.0808 | 44.0552 | -78.8315 | -0.31586 | 0.036621 | 0.027465 | 122.5891 | -1.6617 | -0.33417 | 0.036621 | 0.34332 | 76.4557 | 75.4166 | 120.8542 | 122.5525 | 0.027465 | 122.5525 | 80.5939 | -0.33417 | 122.5525 | 0.027465 | 80.5939 | 120.8542 | 122.5525 | -122.8317 | -122.85
1229.9062 | 122.8088 | -78.0853 | 44.4122 | -0.018768 | 0.00066656 | 0.0040952 | -0.0035761 | -0.0041166 | -0.00093346 | -0.0029971 | -78.0487 | 44.3802 | -78.3737 | 44.5724 | 42.7368 | 1.9318 | -2.2018 | -2.8656 | 44.4077 | -78.3875 | -0.28839 | -0.032043 | 0.036621 | 122.6578 | -1.6754 | -0.30212 | -0.004577 | 0.32501 | 75.8835 | 75.2197 | 120.8221 | 122.4655 | 0.036621 | 122.493 | 80.0171 | -0.30212 | 122.4655 | 0.036621 | 80.0171 | 120.8221 | 122.493 | -122.7859 | -122.7997
1230.9531 | 122.7264 | -77.6184 | 44.9295 | -0.14084 | 0.0064344 | 0.003668 | 0.0053961 | -0.003262 | -0.0020017 | -0.0040653 | -77.5772 | 44.8883 | -77.9572 | 45.0211 | 43.1808 | 2.1286 | -1.9592 | -2.8656 | 44.8883 | -77.9846 | -0.33875 | -0.041198 | 0.041199 | 122.6395 | -1.7487 | -0.36621 | -0.041198 | 0.37994 | 75.6592 | 74.7528 | 120.7993 | 122.5067 | 0.041199 | 122.5067 | 79.747 | -0.36621 | 122.5067 | 0.041199 | 79.747 | 120.7993 | 122.5067 | -122.8867 | -122.9141
1231.9062 | 122.8226 | -77.6184 | 44.8334 | 0.24063 | 0.0038708 | 0.0096494 | 0.0045417 | -0.0026212 | -0.00050626 | -0.0034243 | -77.6688 | 44.6869 | -78.0533 | 44.9799 | 43.1671 | 1.9043 | -2.0874 | -2.8061 | 44.8151 | -77.98 | -0.43488 | -0.14648 | -0.050354 | 122.5983 | -1.6663 | -0.36163 | -0.018311 | 0.38452 | 75.531 | 74.8123 | 120.7855 | 122.3053 | -0.050354 | 122.4335 | 79.5227 | -0.36163 | 122.3053 | -0.050354 | 79.5227 | 120.7855 | 122.4335 | -122.8867 | -122.8134
1232.9531 | 122.7264 | -78.1723 | 44.3985 | 0.15671 | 0.0042982 | 0.0045224 | 0.0053961 | -0.0034756 | -0.00050626 | 0.0049069 | -78.2227 | 44.3253 | -78.5294 | 44.1513 | 42.3019 | 1.8768 | -1.5152 | -2.3758 | 44.3619 | -78.5385 | -0.35706 | -0.073243 | -0.050354 | 122.3236 | -2.0966 | -0.36621 | -0.036622 | 0.3067 | 76.6571 | 75.7965 | 120.4742 | 122.4976 | -0.050354 | 122.5342 | 80.0491 | -0.36621 | 122.4976 | -0.050354 | 80.0491 | 120.4742 | 122.5342 | -122.9279 | -122.937
1233.9062 | 122.8088 | -78.4241 | 44.0826 | 0.24826 | 0.0028028 | 0.0049496 | 0.0036871 | -0.0030484 | 0.00013454 | -0.0036379 | -78.4195 | 44.0735 | -78.7262 | 44.1788 | 42.3431 | 1.387 | -2.1194 | -3.0075 | 44.0872 | -78.7537 | -0.30212 | -0.009156 | 0.004577 | 122.6028 | -1.7395 | -0.32959 | 0.004577 | 0.3067 | 76.3046 | 75.4166 | 120.7672 | 122.4976 | 0.004577 | 122.5113 | 79.8111 | -0.32959 | 122.4976 | 0.004577 | 79.8111 | 120.7672 | 122.5113 | -122.8088 | -122.8363
1234.9688 | 122.7631 | -78.6987 | 43.8858 | 0.13382 | 0.0064344 | 0.0094358 | 0.0075323 | -0.00027139 | -0.00050626 | -0.00064734 | -78.7582 | 43.8034 | -79.0283 | 43.8538 | 42.0776 | 1.4511 | -1.7853 | -3.0258 | 43.8126 | -79.0558 | -0.32959 | -0.082397 | -0.05951 | 122.5525 | -1.8082 | -0.35706 | -0.073242 | 0.27008 | 76.9135 | 75.6729 | 120.7764 | 122.5021 | -0.05951 | 122.5113 | 80.1498 | -0.35706 | 122.5021 | -0.05951 | 80.1498 | 120.7764 | 122.5113 | -122.9141 | -122.9416
1235.9062 | 122.8088 | -79.0283 | 43.4235 | 0.21011 | 0.0017346 | 0.0034544 | -0.0003717 | -0.0019802 | 0.00098914 | -0.0010745 | -78.9917 | 43.4097 | -79.335 | 43.6111 | 41.8533 | 1.4603 | -2.179 | -3.1082 | 43.4418 | -79.3488 | -0.3067 | -0.013733 | 0.036621 | 122.6395 | -1.5701 | -0.32044 | 0.01831 | 0.34332 | 76.8494 | 75.9201 | 120.8817 | 122.438 | 0.036621 | 122.4701 | 80.4886 | -0.32044 | 122.438 | 0.036621 | 80.4886 | 120.8817 | 122.4701 | -122.7585 | -122.7722
1236.9531 | 122.7081 | -79.1107 | 43.4738 | 0.18723 | 0.0042982 | 0.0075132 | 0.0075323 | -0.0051846 | -0.0028561 | -0.0034243 | -79.1061 | 43.4784 | -79.4128 | 43.4372 | 41.6656 | 1.5884 | -2.1515 | -3.2593 | 43.4555 | -79.422 | -0.30212 | 0.004578 | 0.004578 | 122.5479 | -1.8082 | -0.31128 | -0.018311 | 0.3067 | 76.9592 | 75.8514 | 120.7764 | 122.5891 | 0.004578 | 122.5662 | 80.6992 | -0.31128 | 122.5891 | 0.004578 | 80.6992 | 120.7764 | 122.5662 | -122.8867 | -122.8958
1237.9062 | 122.7859 | -78.4149 | 44.0918 | 0.1796 | 0.0010938 | 0.0028134 | 0.0045417 | -0.0019802 | 0.00098914 | -0.0021427 | -78.3966 | 44.101 | -78.7262 | 44.1696 | 42.4301 | 1.4511 | -2.3575 | -3.3142 | 44.0277 | -78.7903 | -0.31128 | 0.009155 | 0.018311 | 122.5845 | -1.6617 | -0.37537 | -0.064087 | 0.32959 | 76.0574 | 75.1007 | 120.845 | 122.5159 | 0.018311 | 122.4426 | 79.866 | -0.37537 | 122.5159 | 0.018311 | 79.866 | 120.845 | 122.4426 | -122.818 | -122.8821
1238.9531 | 122.7264 | -78.8635 | 43.7073 | 0.034637 | 0.0042982 | 0.0066586 | 0.0062507 | -0.0019802 | -0.0015745 | -0.0036379 | -78.8361 | 43.6981 | -79.1473 | 43.7531 | 41.9495 | 1.0757 | -2.3071 | -3.5797 | 43.6798 | -79.216 | -0.28381 | -0.009155 | 0.027465 | 122.6166 | -1.7578 | -0.35248 | -0.027465 | 0.31128 | 76.5564 | 75.2838 | 120.813 | 122.5616 | 0.027465 | 122.5433 | 79.9393 | -0.35248 | 122.5616 | 0.027465 | 79.9393 | 120.813 | 122.5433 | -122.8546 | -122.9233
1239.9062 | 122.7814 | -79.0329 | 43.4418 | -0.0035098 | -0.00061524 | 0.0043088 | -0.0054987 | -0.0036892 | 0.00056194 | 0.0019163 | -79.0146 | 43.4555 | -79.303 | 43.483 | 41.89 | 0.96588 | -2.5314 | -3.5065 | 43.4418 | -79.3671 | -0.27008 | 0.013733 | 0.018311 | 122.5159 | -1.5518 | -0.33417 | 0 | 0.28839 | 76.5015 | 75.5264 | 120.9229 | 122.4884 | 0.018311 | 122.4747 | 79.9988 | -0.33417 | 122.4884 | 0.018311 | 79.9988 | 120.9229 | 122.4747 | -122.7448 | -122.8088
1240.9531 | 122.8271 | -78.6209 | 43.8721 | 0.1796 | 0.0038708 | 0.0072996 | 0.0036871 | -0.0041166 | 0.00034814 | -0.0025699 | -78.5385 | 43.8583 | -78.9139 | 44.0414 | 42.366 | 1.0254 | -2.5314 | -3.1998 | 43.8309 | -78.9597 | -0.29297 | -0.013733 | 0.082398 | 122.6624 | -1.506 | -0.33874 | -0.041198 | 0.37537 | 76.0895 | 75.4211 | 120.9869 | 122.4792 | 0.082398 | 122.4518 | 79.6463 | -0.33874 | 122.4792 | 0.082398 | 79.6463 | 120.9869 | 122.4518 | -122.7859 | -122.8317
1241.9062 | 122.7768 | -79.422 | 43.1168 | 0.15671 | 0.0030164 | 0.0038816 | 0.0049689 | -0.003262 | -7.9062e-05 | -0.00064734 | -79.4586 | 43.0801 | -79.7699 | 43.1763 | 41.3818 | 0.48981 | -2.2842 | -2.7969 | 43.1122 | -79.7516 | -0.3479 | -0.036621 | -0.036621 | 122.5983 | -1.7349 | -0.32959 | -0.004577 | 0.31128 | 77.1378 | 76.6251 | 120.8038 | 122.5021 | -0.036621 | 122.5342 | 79.9118 | -0.32959 | 122.5021 | -0.036621 | 79.9118 | 120.8038 | 122.5342 | -122.8867 | -122.8683
1242.9531 | 122.7127 | -79.1519 | 43.4464 | 0.14908 | 0.006648 | 0.0090086 | 0.0081733 | -0.0013394 | -0.0026425 | -0.0023563 | -79.3442 | 43.4235 | -79.4357 | 43.5013 | 41.748 | 0.79193 | -2.3117 | -2.8061 | 43.4464 | -79.4678 | -0.28381 | -0.022888 | -0.19226 | 122.6532 | -1.6983 | -0.31586 | 0 | 0.091553 | 76.8402 | 76.3458 | 120.9 | 122.5754 | -0.19226 | 122.5983 | 79.9438 | -0.31586 | 122.5754 | -0.19226 | 79.9438 | 120.9 | 122.5983 | -122.8821 | -122.9141
1243.9062 | 122.7356 | -78.7994 | 43.7073 | 0.18723 | 0.0042982 | 0.0060178 | 0.0056097 | -0.0019802 | -0.0011471 | -0.0036379 | -78.7949 | 43.7805 | -79.0833 | 43.8354 | 42.1738 | 1.0071 | -2.4628 | -3.1677 | 43.7714 | -79.1199 | -0.28381 | 0.073243 | 0.004577 | 122.6349 | -1.5335 | -0.32044 | 0.064087 | 0.28839 | 76.3367 | 75.6317 | 120.9732 | 122.58 | 0.004577 | 122.5708 | 79.8065 | -0.32044 | 122.58 | 0.004577 | 79.8065 | 120.9732 | 122.5708 | -122.7905 | -122.8271
1244.9688 | 122.7676 | -80.3513 | 42.1829 | 0.16434 | 0.0025892 | 0.0072996 | -0.0044305 | -0.001553 | -0.0015745 | -0.0021427 | -80.3329 | 42.1051 | -80.6305 | 42.3203 | 40.6036 | 0.32959 | -2.7191 | -3.4378 | 42.1875 | -80.6351 | -0.27924 | -0.077819 | 0.01831 | 122.6715 | -1.5793 | -0.28381 | 0.004578 | 0.29755 | 77.6321 | 76.9135 | 120.9549 | 122.4564 | 0.01831 | 122.5388 | 80.6808 | -0.28381 | 122.4564 | 0.01831 | 80.6808 | 120.9549 | 122.5388 | -122.8134 | -122.818
1245.9062 | 122.7951 | -79.7836 | 42.7368 | 0.21774 | 0.0034436 | 0.0032406 | 0.0064643 | -0.0036892 | -0.00029266 | -0.0038515 | -79.7653 | 42.7094 | -80.0629 | 42.8238 | 41.1209 | 0.41199 | -2.4536 | -3.1082 | 42.7185 | -80.1361 | -0.27924 | -0.027465 | 0.01831 | 122.6074 | -1.6159 | -0.35248 | -0.01831 | 0.29755 | 77.33 | 76.6754 | 120.9045 | 122.493 | 0.01831 | 122.5021 | 80.1956 | -0.35248 | 122.493 | 0.01831 | 80.1956 | 120.9045 | 122.5021 | -122.7997 | -122.8729
1246.9531 | 122.7722 | -80.191 | 42.334 | 0.22537 | 0.0060072 | 0.0045224 | 0.0047553 | -0.003903 | -0.00093346 | -0.0021427 | -80.1178 | 42.3798 | -80.4565 | 42.4438 | 40.7089 | 0.086975 | -2.4353 | -3.1128 | 42.3569 | -80.5252 | -0.2655 | 0.045777 | 0.073242 | 122.6349 | -1.6251 | -0.33417 | 0.022889 | 0.33875 | 77.7557 | 77.0782 | 120.9 | 122.5708 | 0.073242 | 122.5479 | 80.278 | -0.33417 | 122.5708 | 0.073242 | 80.278 | 120.9 | 122.5479 | -122.7905 | -122.8592
1247.9062 | 122.7402 | -80.278 | 42.2424 | 0.22537 | 0.0053662 | 0.0045224 | 0.0053961 | -0.00048499 | 0.00098914 | -0.0040653 | -80.2322 | 42.2928 | -80.5618 | 42.3431 | 40.6357 | 0.15106 | -2.4399 | -3.1631 | 42.247 | -80.6351 | -0.28381 | 0.050354 | 0.045776 | 122.6212 | -1.6068 | -0.35706 | 0.004577 | 0.32959 | 77.8381 | 77.1149 | 120.9137 | 122.5708 | 0.045776 | 122.525 | 80.4291 | -0.35706 | 122.5708 | 0.045776 | 80.4291 | 120.9137 | 122.525 | -122.8043 | -122.8775
1248.9688 | 122.7493 | -79.4998 | 43.0389 | -1.1632 | 0.00323 | 0.0051632 | 0.0060369 | -5.7592e-05 | -0.0030697 | -0.0032107 | -79.3854 | 43.0573 | -79.8019 | 43.1854 | 41.4505 | 0.38452 | -2.2018 | -3.0853 | 43.0801 | -79.8569 | -0.30212 | 0.018311 | 0.11444 | 122.6852 | -1.5884 | -0.35706 | 0.041199 | 0.41657 | 77.298 | 76.4145 | 120.9503 | 122.5571 | 0.11444 | 122.58 | 79.8843 | -0.35706 | 122.5571 | 0.11444 | 79.8843 | 120.9503 | 122.58 | -122.8409 | -122.8958
1249.9062 | 122.8363 | -79.8294 | 42.6819 | 1.942 | 0.0028028 | 0.0040952 | 0.0011237 | -0.0028348 | -0.0013609 | -0.0027835 | -79.6829 | 42.6682 | -80.072 | 42.865 | 41.1987 | 0.37537 | -2.5818 | -3.5934 | 42.6819 | -80.0949 | -0.24261 | -0.013733 | 0.14648 | 122.6944 | -1.4832 | -0.2655 | 0 | 0.3891 | 77.2476 | 76.236 | 121.0281 | 122.4976 | 0.14648 | 122.5113 | 80.2048 | -0.2655 | 122.4976 | 0.14648 | 80.2048 | 121.0281 | 122.5113 | -122.7539 | -122.7768
1250.9688 | 122.7036 | -81.0425 | 41.5237 | 0.088043 | 0.0053662 | 0.0045224 | 0.0064643 | -0.002194 | -7.9062e-05 | -0.0019289 | -80.9784 | 41.5192 | -81.3263 | 41.5741 | 39.9124 | -0.11444 | -2.4307 | -4.0237 | 41.5558 | -81.395 | -0.28381 | -0.004578 | 0.064086 | 122.6166 | -1.6113 | -0.35248 | 0.032043 | 0.3479 | 78.6118 | 77.0187 | 120.9549 | 122.5616 | 0.064086 | 122.5983 | 80.928 | -0.35248 | 122.5616 | 0.064086 | 80.928 | 120.9549 | 122.5983 | -122.85 | -122.9187
1251.9062 | 122.8226 | -80.3467 | 42.1509 | 0.1796 | 0.00323 | 0.010717 | 0.0015509 | -0.00091219 | 0.0014163 | -0.0032107 | -80.4199 | 41.9815 | -80.7587 | 42.2836 | 40.7272 | 0.004578 | -2.3895 | -3.4515 | 42.16 | -80.658 | -0.41199 | -0.16937 | -0.073242 | 122.6303 | -1.4236 | -0.31128 | 0.009155 | 0.33875 | 77.9572 | 76.8951 | 121.0739 | 122.3282 | -0.073242 | 122.5067 | 80.3513 | -0.31128 | 122.3282 | -0.073242 | 80.3513 | 121.0739 | 122.5067 | -122.9095 | -122.8088
1252.9688 | 122.7264 | -80.3787 | 42.2012 | 0.065155 | 0.006648 | 0.006445 | 0.0081733 | -0.0024076 | -7.9062e-05 | -0.0042789 | -80.3467 | 42.1509 | -80.6992 | 42.2974 | 40.7227 | 0.45319 | -1.9455 | -3.1815 | 42.2195 | -80.7312 | -0.32044 | -0.050354 | 0.032043 | 122.6761 | -1.4786 | -0.35248 | 0.01831 | 0.35248 | 78.4332 | 77.1973 | 121.1014 | 122.5296 | 0.032043 | 122.5983 | 80.8319 | -0.35248 | 122.5296 | 0.032043 | 80.8319 | 121.1014 | 122.5983 | -122.9004 | -122.9324
1253.9062 | 122.7493 | -80.1361 | 42.3889 | 0.15671 | 0.004939 | 0.008154 | 0.0047553 | -0.00048499 | -0.0020017 | -0.0019289 | -80.1178 | 42.4072 | -80.4474 | 42.485 | 40.8554 | 0.40283 | -2.0737 | -3.0945 | 42.4484 | -80.4703 | -0.31128 | 0.018311 | 0.01831 | 122.6212 | -1.5335 | -0.33417 | 0.059509 | 0.32959 | 78.0624 | 77.0416 | 120.9915 | 122.5433 | 0.01831 | 122.5845 | 80.5389 | -0.33417 | 122.5433 | 0.01831 | 80.5389 | 120.9915 | 122.5845 | -122.8363 | -122.8592
1254.9688 | 122.7173 | -80.8411 | 41.7206 | 0.74417 | -0.0010424 | 0.003668 | 0.0034735 | -0.0028348 | 0.00013454 | -0.0021427 | -80.5618 | 41.7801 | -81.0928 | 41.7801 | 40.1596 | 0.3479 | -2.2064 | -2.8381 | 41.7755 | -81.1478 | -0.25177 | 0.059509 | 0.27923 | 122.6212 | -1.561 | -0.3067 | 0.054932 | 0.531 | 78.6346 | 78.0029 | 121.0007 | 122.6212 | 0.27923 | 122.6166 | 81.189 | -0.3067 | 122.6212 | 0.27923 | 81.189 | 121.0007 | 122.6166 | -122.8134 | -122.8683
1255.9062 | 122.7081 | -80.7632 | 41.7938 | 0.13382 | 0.0040846 | 0.0092222 | 0.0043281 | -0.0011258 | -0.0013609 | -0.0027835 | -80.7999 | 41.7526 | -81.0791 | 41.7938 | 40.0681 | 0.50812 | -2.2385 | -2.9343 | 41.7984 | -81.1295 | -0.31586 | -0.041198 | -0.036621 | 122.5571 | -1.7258 | -0.36621 | 0.004578 | 0.27924 | 78.5248 | 77.829 | 120.8313 | 122.5159 | -0.036621 | 122.5616 | 81.2714 | -0.36621 | 122.5159 | -0.036621 | 81.2714 | 120.8313 | 122.5616 | -122.8729 | -122.9233
1256.9531 | 122.7127 | -81.1707 | 41.4093 | 0.019379 | 0.0051526 | 0.0087948 | 0.0062507 | -0.00048499 | 0.00056194 | -0.0034243 | -81.0287 | 41.4642 | -81.4087 | 41.4459 | 39.8804 | -0.1236 | -2.4445 | -3.3051 | 41.4368 | -81.4911 | -0.23804 | 0.054931 | 0.14191 | 122.6166 | -1.5289 | -0.32044 | 0.027466 | 0.37994 | 78.7262 | 77.8656 | 121.051 | 122.6349 | 0.14191 | 122.6074 | 81.0471 | -0.32044 | 122.6349 | 0.14191 | 81.0471 | 121.051 | 122.6074 | -122.818 | -122.9004
1257.9062 | 122.6669 | -80.2689 | 42.3294 | 0.095673 | 0.0034436 | 0.0062314 | 0.0081733 | -0.00069859 | -0.00029266 | -0.0049197 | -80.1819 | 42.3752 | -80.5344 | 42.3111 | 40.654 | 0.018311 | -2.3666 | -3.2043 | 42.3157 | -80.6122 | -0.2655 | 0.045776 | 0.086975 | 122.58 | -1.6754 | -0.34332 | -0.013733 | 0.35248 | 77.9022 | 77.0645 | 120.9229 | 122.644 | 0.086975 | 122.5845 | 80.2872 | -0.34332 | 122.644 | 0.086975 | 80.2872 | 120.9229 | 122.5845 | -122.8638 | -122.9416
1258.9531 | 122.7356 | -80.5756 | 41.9952 | 0.14145 | 0.0042982 | 0.0079404 | 0.0068915 | -0.0017666 | -0.0024289 | -0.00086094 | -80.5252 | 42.0868 | -80.8228 | 42.041 | 40.2786 | -0.082397 | -2.4216 | -3.1403 | 42.041 | -80.8914 | -0.24719 | 0.091553 | 0.050354 | 122.6166 | -1.7166 | -0.31586 | 0.045777 | 0.29755 | 78.154 | 77.4353 | 120.8542 | 122.6624 | 0.050354 | 122.6166 | 80.4932 | -0.31586 | 122.6624 | 0.050354 | 80.4932 | 120.8542 | 122.6166 | -122.818 | -122.8867
1259.9062 | 122.8455 | -80.3558 | 42.1326 | 0.21774 | 0.002162 | 0.0075132 | 0.0030463 | -0.00069859 | -0.0015745 | -0.0021427 | -80.4153 | 41.9907 | -80.777 | 42.2836 | 40.6219 | -0.027466 | -2.4811 | -2.8152 | 42.1555 | -80.69 | -0.42114 | -0.14191 | -0.059509 | 122.6395 | -1.5106 | -0.33417 | 0.022889 | 0.36163 | 77.8748 | 77.5406 | 120.9778 | 122.3465 | -0.059509 | 122.5113 | 80.3284 | -0.33417 | 122.3465 | -0.059509 | 80.3284 | 120.9778 | 122.5113 | -122.9095 | -122.8226
1260.9531 | 122.7402 | -81.4316 | 41.1713 | -0.23239 | 0.0038708 | 0.0085812 | 0.0034735 | -0.002194 | 0.0016299 | -0.0017153 | -81.3904 | 41.1575 | -81.6834 | 41.2308 | 39.6561 | -0.5127 | -2.4628 | -3.1952 | 41.1713 | -81.7703 | -0.25177 | -0.013733 | 0.041199 | 122.6624 | -1.5152 | -0.33875 | 0 | 0.29297 | 78.9688 | 78.2364 | 121.0876 | 122.5891 | 0.041199 | 122.6028 | 80.9189 | -0.33875 | 122.5891 | 0.041199 | 80.9189 | 121.0876 | 122.6028 | -122.8546 | -122.9416
1261.9062 | 122.7036 | -81.4224 | 41.1942 | 0.042267 | 0.0045118 | 0.0070858 | 0.0053961 | -0.0013394 | -0.00050626 | -0.0032107 | -81.514 | 40.9973 | -81.8802 | 41.1713 | 39.6011 | -0.76904 | -2.2797 | -3.1311 | 41.1438 | -81.8344 | -0.45776 | -0.19684 | -0.091553 | 122.5937 | -1.593 | -0.41199 | -0.050354 | 0.36621 | 79.1428 | 78.2913 | 121.0236 | 122.4197 | -0.091553 | 122.5662 | 80.6534 | -0.41199 | 122.4197 | -0.091553 | 80.6534 | 121.0236 | 122.5662 | -123.0743 | -123.0286
1262.9531 | 122.731 | -81.2393 | 41.3269 | 0.027008 | 0.004939 | 0.0058042 | 0.0071051 | 0.00015601 | -0.00050626 | -0.0032107 | -81.1386 | 41.3452 | -81.5552 | 41.4093 | 39.7293 | -0.86517 | -2.3758 | -3.0029 | 41.3269 | -81.5781 | -0.31586 | 0.018311 | 0.10071 | 122.6486 | -1.5976 | -0.33875 | 0 | 0.41657 | 78.8635 | 78.2364 | 120.9686 | 122.5845 | 0.10071 | 122.5662 | 80.3741 | -0.33875 | 122.5845 | 0.10071 | 80.3741 | 120.9686 | 122.5662 | -122.8821 | -122.905
1263.9062 | 122.6898 | -80.777 | 41.7801 | 0.057526 | 0.0055798 | 0.0055906 | 0.0064643 | 0.00058321 | -0.0020017 | -0.0021427 | -80.7495 | 41.803 | -81.0928 | 41.8396 | 40.2328 | -0.65002 | -2.3117 | -3.0899 | 41.8076 | -81.1615 | -0.31586 | 0.022889 | 0.027466 | 122.6166 | -1.5472 | -0.38452 | 0.027466 | 0.34332 | 78.4653 | 77.6871 | 121.0098 | 122.58 | 0.027466 | 122.5845 | 80.127 | -0.38452 | 122.58 | 0.027466 | 80.127 | 121.0098 | 122.5845 | -122.8729 | -122.9416
1264.9688 | 122.8088 | -81.6605 | 40.8371 | 0.11856 | 0.00066656 | 0.0043088 | -0.0010125 | -0.0011258 | -0.0020017 | -0.0023563 | -81.7291 | 40.6265 | -82.1045 | 40.9561 | 39.4958 | -0.67749 | -3.0212 | -2.9846 | 40.8508 | -81.9809 | -0.44403 | -0.21057 | -0.068665 | 122.6166 | -1.3412 | -0.32044 | 0.013733 | 0.37537 | 78.6392 | 78.6758 | 121.1563 | 122.287 | -0.068665 | 122.5113 | 80.983 | -0.32044 | 122.287 | -0.068665 | 80.983 | 121.1563 | 122.5113 | -122.9416 | -122.818
1265.9062 | 122.7997 | -82.4387 | 40.1184 | 0.24063 | 0.0064344 | 0.0066586 | 0.0060369 | -0.0017666 | -0.0011471 | -0.0025699 | -82.4158 | 40.0726 | -82.7591 | 40.2328 | 38.7634 | -1.062 | -3.0899 | -3.4012 | 40.123 | -82.7728 | -0.32043 | -0.045776 | 0.022889 | 122.6715 | -1.355 | -0.33417 | 0.004578 | 0.34332 | 79.3488 | 79.0375 | 121.2021 | 122.5113 | 0.022889 | 122.5616 | 81.3766 | -0.33417 | 122.5113 | 0.022889 | 81.3766 | 121.2021 | 122.5616 | -122.8775 | -122.8912
1266.9531 | 122.7219 | -82.5119 | 40.0864 | 0.1033 | 0.0038708 | 0.0040952 | 0.0075323 | -0.00048499 | -0.00093346 | -0.0027835 | -82.4249 | 40.1276 | -82.7637 | 40.0772 | 38.4888 | -1.4511 | -2.9892 | -3.5522 | 40.0909 | -82.9056 | -0.25177 | 0.041198 | 0.086975 | 122.5891 | -1.5976 | -0.39368 | 0.004577 | 0.33875 | 79.5227 | 78.9597 | 121.0007 | 122.6395 | 0.086975 | 122.6028 | 81.0608 | -0.39368 | 122.6395 | 0.086975 | 81.0608 | 121.0007 | 122.6028 | -122.85 | -122.9919
1267.9062 | 122.7173 | -80.9509 | 41.6245 | 0.088043 | 0.0051526 | 0.004736 | 0.0062507 | 0.00058321 | -0.00050626 | -0.0023563 | -80.983 | 41.5695 | -81.2988 | 41.6611 | 40.1001 | -1.0803 | -2.7466 | -3.1036 | 41.684 | -81.2805 | -0.3479 | -0.054932 | -0.032043 | 122.612 | -1.5244 | -0.32959 | 0.059509 | 0.31586 | 78.2043 | 77.8473 | 121.051 | 122.5204 | -0.032043 | 122.6349 | 79.8706 | -0.32959 | 122.5204 | -0.032043 | 79.8706 | 121.051 | 122.6349 | -122.9233 | -122.905
1268.9531 | 122.7631 | -80.2048 | 42.366 | 0.042267 | 0.0055798 | 0.0079404 | 0.0073187 | 0.0016512 | -0.0017881 | -0.0021427 | -80.1086 | 42.4164 | -80.4932 | 42.4438 | 40.7822 | -1.0483 | -3.0808 | -3.2776 | 42.3706 | -80.571 | -0.28839 | 0.050354 | 0.09613 | 122.6486 | -1.5839 | -0.36621 | 0.004577 | 0.38452 | 77.124 | 76.9272 | 120.9869 | 122.6212 | 0.09613 | 122.5754 | 79.1565 | -0.36621 | 122.6212 | 0.09613 | 79.1565 | 120.9869 | 122.5754 | -122.8592 | -122.937
1269.9062 | 122.7951 | -80.8594 | 41.6428 | 0.13382 | 0.002162 | 0.0087948 | -0.0018671 | -0.0028348 | -0.00093346 | -0.0021427 | -80.7632 | 41.6885 | -81.0928 | 41.8076 | 40.2328 | -1.1673 | -3.241 | -3.0167 | 41.7023 | -81.1249 | -0.23346 | 0.045777 | 0.09613 | 122.6669 | -1.4099 | -0.2655 | 0.05951 | 0.32959 | 77.6184 | 77.8427 | 121.0922 | 122.5479 | 0.09613 | 122.5616 | 79.6921 | -0.2655 | 122.5479 | 0.09613 | 79.6921 | 121.0922 | 122.5616 | -122.7356 | -122.7676
1270.9531 | 122.7631 | -81.2622 | 41.2903 | -0.011139 | 0.0036572 | 0.0079404 | 0.0081733 | -0.0030484 | 0.00077554 | -0.0029971 | -81.2347 | 41.2674 | -81.6238 | 41.4093 | 39.743 | -1.0986 | -3.2501 | -3.0716 | 41.2994 | -81.6467 | -0.36163 | -0.022888 | 0.027466 | 122.6715 | -1.5472 | -0.38452 | 0.009155 | 0.3891 | 78.0121 | 78.1906 | 121.0052 | 122.5296 | 0.027466 | 122.5616 | 80.1636 | -0.38452 | 122.5296 | 0.027466 | 80.1636 | 121.0052 | 122.5616 | -122.9141 | -122.937
1271.9062 | 122.7493 | -80.9967 | 41.5787 | -0.011139 | 0.0042982 | 0.0070858 | 0.0075323 | -0.00048499 | -7.9062e-05 | -0.0012881 | -81.0059 | 41.51 | -81.3629 | 41.5924 | 40.0772 | -0.98877 | -3.3234 | -3.1311 | 41.5649 | -81.3309 | -0.36621 | -0.068664 | -0.009155 | 122.5891 | -1.5015 | -0.33417 | -0.013733 | 0.35706 | 77.6733 | 77.8656 | 121.0739 | 122.5067 | -0.009155 | 122.5616 | 80.0079 | -0.33417 | 122.5067 | -0.009155 | 80.0079 | 121.0739 | 122.5616 | -122.9416 | -122.9095
1272.9531 | 122.7631 | -82.1915 | 40.3885 | -0.072174 | 0.0057934 | 0.0085812 | 0.0083869 | -0.003262 | -0.0017881 | -0.0038515 | -81.9443 | 40.5624 | -82.3059 | 40.5029 | 38.9053 | -1.2634 | -3.3829 | -3.5065 | 40.4663 | -82.5302 | -0.11444 | 0.17395 | 0.24719 | 122.6944 | -1.4832 | -0.33875 | 0.07782 | 0.36163 | 78.8086 | 78.685 | 121.0968 | 122.7539 | 0.24719 | 122.6578 | 80.928 | -0.33875 | 122.7539 | 0.24719 | 80.928 | 121.0968 | 122.6578 | -122.6944 | -122.9187
1273.9062 | 122.7402 | -81.134 | 41.4688 | 0.042267 | 0.0047254 | 0.0034544 | 0.0079595 | 0.00036961 | -0.00071986 | -0.0012881 | -81.1249 | 41.4322 | -81.5048 | 41.4413 | 39.8758 | -1.2497 | -3.1265 | -3.0762 | 41.4505 | -81.5048 | -0.37079 | -0.036621 | 0.009155 | 122.5754 | -1.593 | -0.37079 | -0.018311 | 0.37994 | 78.0075 | 78.0579 | 121.0098 | 122.5662 | 0.009155 | 122.5845 | 79.8843 | -0.37079 | 122.5662 | 0.009155 | 79.8843 | 121.0098 | 122.5845 | -122.9736 | -122.9736
1274.9531 | 122.731 | -82.0496 | 40.5441 | -0.064545 | 0.004939 | 0.0087948 | 0.0066779 | -5.7592e-05 | -0.0011471 | -0.0010745 | -81.9351 | 40.567 | -82.3471 | 40.567 | 38.9923 | -1.4786 | -3.3691 | -3.1311 | 40.5075 | -82.4112 | -0.29755 | 0.022889 | 0.11444 | 122.6166 | -1.5518 | -0.36163 | -0.036621 | 0.41199 | 78.6804 | 78.9185 | 121.0419 | 122.6166 | 0.11444 | 122.5571 | 80.571 | -0.36163 | 122.6166 | 0.11444 | 80.571 | 121.0419 | 122.5571 | -122.8912 | -122.9553
1275.9062 | 122.7264 | -81.3583 | 41.2216 | 0.088043 | 0.002162 | 0.0083676 | 0.0049689 | 0.00058321 | -0.0013609 | -0.0015017 | -81.2668 | 41.2582 | -81.6376 | 41.2216 | 39.6881 | -1.6983 | -3.5797 | -3.5431 | 41.2262 | -81.7337 | -0.27924 | 0.036621 | 0.091552 | 122.58 | -1.5335 | -0.37537 | 0.004577 | 0.37079 | 77.7786 | 77.8152 | 121.0464 | 122.6166 | 0.091552 | 122.5845 | 79.66 | -0.37537 | 122.6166 | 0.091552 | 79.66 | 121.0464 | 122.5845 | -122.8592 | -122.9553
1276.9531 | 122.7539 | -81.4362 | 41.1621 | -0.14847 | 0.0040846 | 0.0021726 | 0.0043281 | 0.001224 | 0.00056194 | -0.0040653 | -81.4133 | 41.1209 | -81.752 | 41.2079 | 39.6378 | -1.1902 | -2.742 | -3.0945 | 41.185 | -81.7795 | -0.31586 | -0.041198 | 0.022888 | 122.644 | -1.5244 | -0.34332 | 0.022889 | 0.33875 | 78.6942 | 78.3417 | 121.0739 | 122.5571 | 0.022888 | 122.6212 | 80.246 | -0.34332 | 122.5571 | 0.022888 | 80.246 | 121.0739 | 122.6212 | -122.9141 | -122.9416
1277.9062 | 122.7493 | -80.8273 | 41.7572 | 0.0041197 | 0.0040846 | 0.0045224 | 0.0073187 | 0.0010104 | -0.0017881 | -0.0015017 | -80.7587 | 41.7847 | -81.1203 | 41.835 | 40.242 | -0.9613 | -2.3712 | -2.9068 | 41.8121 | -81.1569 | -0.29297 | 0.027466 | 0.068665 | 122.6624 | -1.5152 | -0.32959 | 0.054932 | 0.36163 | 78.4561 | 77.9205 | 121.0693 | 122.612 | 0.068665 | 122.6395 | 79.866 | -0.32959 | 122.612 | 0.068665 | 79.866 | 121.0693 | 122.6395 | -122.8775 | -122.9141
1278.9688 | 122.8271 | -81.134 | 41.3635 | -0.30106 | 0.0028028 | 0.0049496 | -0.0025079 | -0.003903 | -0.00029266 | -0.0032107 | -81.102 | 41.3361 | -81.514 | 41.4917 | 40.0131 | -1.0574 | -3.2272 | -3.0167 | 41.3635 | -81.514 | -0.37994 | -0.027465 | 0.032043 | 122.6257 | -1.3504 | -0.37994 | 0 | 0.41199 | 77.9068 | 78.1174 | 121.1472 | 122.4701 | 0.032043 | 122.4976 | 80.0766 | -0.37994 | 122.4701 | 0.032043 | 80.0766 | 121.1472 | 122.4976 | -122.8775 | -122.8775
1279.9062 | 122.8317 | -81.2164 | 41.3086 | 0.18723 | 0.0025892 | 0.0045224 | 0.0032599 | -0.0019802 | 0.00077554 | -0.0032107 | -81.0837 | 41.3132 | -81.4865 | 41.5375 | 40.1276 | -1.4603 | -4.0421 | -3.2867 | 41.3361 | -81.4911 | -0.27008 | 0.004577 | 0.13275 | 122.7539 | -1.181 | -0.27466 | 0.027466 | 0.40283 | 77.1744 | 77.9297 | 121.344 | 122.5296 | 0.13275 | 122.5525 | 79.7562 | -0.27466 | 122.5296 | 0.13275 | 79.7562 | 121.344 | 122.5525 | -122.7951 | -122.7997
1280.9062 | 122.7631 | -81.2393 | 41.3315 | -0.041657 | 0.004939 | 0.009863 | 0.0060369 | -0.0026212 | 0.00077554 | -0.0038515 | -81.2073 | 41.3498 | -81.546 | 41.3864 | 39.798 | -1.7303 | -3.7354 | -3.5431 | 41.3086 | -81.6376 | -0.3067 | 0.01831 | 0.032044 | 122.6257 | -1.5335 | -0.39825 | -0.022888 | 0.33875 | 77.504 | 77.6962 | 121.0373 | 122.5891 | 0.032044 | 122.5479 | 79.509 | -0.39825 | 122.5891 | 0.032044 | 79.509 | 121.0373 | 122.5479 | -122.8775 | -122.9691
1281.9531 | 122.7768 | -82.0404 | 40.5258 | -0.13321 | 0.0060072 | 0.0075132 | 0.0058233 | -0.00091219 | -0.0026425 | -0.0042789 | -82.0312 | 40.4892 | -82.3791 | 40.6631 | 39.0976 | -1.8311 | -3.6987 | -3.5568 | 40.6128 | -82.3791 | -0.33874 | -0.036621 | 0.009155 | 122.7036 | -1.4282 | -0.33874 | 0.086975 | 0.3479 | 78.3417 | 78.4836 | 121.138 | 122.5296 | 0.009155 | 122.6532 | 80.2094 | -0.33874 | 122.5296 | 0.009155 | 80.2094 | 121.138 | 122.6532 | -122.905 | -122.905
1282.9062 | 122.6898 | -81.0974 | 41.4688 | -0.079803 | 0.0051526 | 0.0058042 | 0.0058233 | -5.7592e-05 | -0.00093346 | -0.0021427 | -81.0013 | 41.5649 | -81.3812 | 41.5787 | 40.0085 | -1.7944 | -3.5568 | -3.5522 | 41.5237 | -81.4774 | -0.28381 | 0.09613 | 0.09613 | 122.6761 | -1.4603 | -0.37994 | 0.054932 | 0.37994 | 77.5406 | 77.5452 | 121.106 | 122.6624 | 0.09613 | 122.6212 | 79.303 | -0.37994 | 122.6624 | 0.09613 | 79.303 | 121.106 | 122.6212 | -122.85 | -122.9462
1283.9531 | 122.7402 | -81.6147 | 41.0156 | -1.888 | 0.0038708 | 0.0077268 | 0.0004827 | 0.00036961 | 0.00056194 | -0.0038515 | -81.6055 | 41.0248 | -81.9214 | 41.0385 | 39.5554 | -1.7624 | -3.4058 | -3.3417 | 41.0706 | -81.9443 | -0.3067 | 0.009155 | 0.009155 | 122.6532 | -1.4603 | -0.32959 | 0.054932 | 0.31586 | 78.2089 | 78.273 | 121.17 | 122.6395 | 0.009155 | 122.6852 | 79.8523 | -0.32959 | 122.6395 | 0.009155 | 79.8523 | 121.17 | 122.6852 | -122.937 | -122.9599
1284.9062 | 122.7356 | -81.9489 | 40.6311 | -0.56046 | 0.0060072 | 0.0075132 | 0.0060369 | -0.0017666 | -0.00071986 | -0.00021994 | -81.8848 | 40.7181 | -82.2052 | 40.6631 | 39.1342 | -2.1515 | -3.7033 | -3.685 | 40.6631 | -82.2922 | -0.25635 | 0.086975 | 0.064087 | 122.612 | -1.4969 | -0.34332 | 0.032043 | 0.32043 | 78.2455 | 78.2639 | 121.0831 | 122.6669 | 0.064087 | 122.612 | 79.7974 | -0.34332 | 122.6669 | 0.064087 | 79.7974 | 121.0831 | 122.612 | -122.8363 | -122.9233
1285.9688 | 122.85 | -81.1615 | 41.3956 | -0.12558 | 0.0034436 | 0.0043088 | -0.0025079 | -0.00069859 | -7.9062e-05 | -0.0027835 | -81.0333 | 41.4185 | -81.4133 | 41.5833 | 40.0635 | -2.0966 | -3.5202 | -3.5019 | 41.4642 | -81.4865 | -0.25177 | 0.022888 | 0.12817 | 122.7448 | -1.3321 | -0.32501 | 0.068664 | 0.37994 | 77.6413 | 77.6596 | 121.225 | 122.58 | 0.12817 | 122.6257 | 79.0649 | -0.32501 | 122.58 | 0.12817 | 79.0649 | 121.225 | 122.6257 | -122.8088 | -122.8821
1286.9062 | 122.7356 | -82.3883 | 40.2145 | -0.0035098 | 0.0038708 | 0.0070858 | 0.0096685 | -0.00048499 | -0.00093346 | -0.0066287 | -82.283 | 40.242 | -82.6492 | 40.2786 | 38.7772 | -2.1881 | -4.1153 | -3.8315 | 40.2283 | -82.7454 | -0.26093 | 0.027465 | 0.10529 | 122.6669 | -1.4374 | -0.35706 | 0.013732 | 0.36621 | 78.273 | 78.5568 | 121.1655 | 122.6303 | 0.10529 | 122.6166 | 80.2002 | -0.35706 | 122.6303 | 0.10529 | 80.2002 | 121.1655 | 122.6166 | -122.8638 | -122.9599
1287.9688 | 122.7631 | -82.0999 | 40.5029 | -0.10269 | 0.0057934 | 0.005377 | 0.0045417 | -0.0024076 | 0.00034814 | -0.0034243 | -82.1503 | 40.3473 | -82.5119 | 40.4984 | 39.1296 | -2.4307 | -4.5319 | -4.2847 | 40.4846 | -82.489 | -0.41199 | -0.15564 | -0.050354 | 122.5983 | -1.3733 | -0.3891 | -0.018311 | 0.36163 | 77.5681 | 77.8152 | 121.2296 | 122.4472 | -0.050354 | 122.5845 | 79.6692 | -0.3891 | 122.4472 | -0.050354 | 79.6692 | 121.2296 | 122.5845 | -123.0148 | -122.9919
1288.9062 | 122.7814 | -82.0358 | 40.5762 | -0.14847 | 0.0045118 | 0.006445 | 0.0066779 | -0.00048499 | -0.00071986 | -0.0012881 | -81.8985 | 40.6357 | -82.2784 | 40.6586 | 39.1388 | -2.7054 | -4.866 | -4.4632 | 40.5762 | -82.3608 | -0.24261 | 0.059509 | 0.13733 | 122.6944 | -1.4374 | -0.32501 | 0 | 0.37994 | 77.1698 | 77.5726 | 121.1746 | 122.6715 | 0.13733 | 122.612 | 79.3304 | -0.32501 | 122.6715 | 0.13733 | 79.3304 | 121.1746 | 122.612 | -122.8546 | -122.937
1289.9688 | 122.7493 | -82.2327 | 40.3336 | 0.17197 | 0.0042982 | 0.0060178 | 0.0028327 | 0.00015601 | 0.00034814 | -0.0025699 | -82.2006 | 40.3381 | -82.5714 | 40.361 | 38.9282 | -2.6505 | -4.8843 | -4.1611 | 40.3748 | -82.5668 | -0.33875 | 0.004578 | 0.032043 | 122.5937 | -1.4053 | -0.33417 | 0.041199 | 0.37079 | 77.3483 | 78.0716 | 121.1609 | 122.5708 | 0.032043 | 122.6074 | 79.5822 | -0.33417 | 122.5708 | 0.032043 | 79.5822 | 121.1609 | 122.6074 | -122.905 | -122.9004
1290.9062 | 122.7859 | -80.9326 | 41.6336 | -0.072174 | 0.00323 | 0.004736 | 0.0064643 | -0.0013394 | -0.00071986 | -0.0025699 | -80.8594 | 41.6199 | -81.2622 | 41.7572 | 40.3748 | -2.8244 | -5.2917 | -4.454 | 41.716 | -81.2668 | -0.32959 | -0.013733 | 0.073242 | 122.6898 | -1.2589 | -0.33417 | 0.082397 | 0.40283 | 75.6409 | 76.4786 | 121.3074 | 122.5525 | 0.073242 | 122.6486 | 78.1082 | -0.33417 | 122.5525 | 0.073242 | 78.1082 | 121.3074 | 122.6486 | -122.8958 | -122.9004
1291.9531 | 122.7356 | -81.8253 | 40.741 | 0.027008 | 0.0055798 | 0.005377 | 0.0064643 | -0.00091219 | -0.0015745 | -0.0034243 | -81.7429 | 40.7776 | -82.1136 | 40.8188 | 39.4592 | -3.2959 | -5.452 | -4.6875 | 40.8188 | -82.164 | -0.28839 | 0.036621 | 0.082397 | 122.644 | -1.2817 | -0.33875 | 0.07782 | 0.37079 | 76.3733 | 77.1378 | 121.2845 | 122.6028 | 0.082397 | 122.644 | 78.5294 | -0.33875 | 122.6028 | 0.082397 | 78.5294 | 121.2845 | 122.644 | -122.8546 | -122.905
1292.9062 | 122.7585 | -80.928 | 41.6931 | -0.14084 | 0.0036572 | 0.0094358 | 0.0045417 | -0.0011258 | 0.00013454 | -0.0040653 | -80.9143 | 41.6016 | -81.308 | 41.7526 | 40.3381 | -3.0396 | -5.2597 | -4.4128 | 41.6931 | -81.2485 | -0.37994 | -0.091553 | 0.013733 | 122.6807 | -1.355 | -0.32043 | 0 | 0.39368 | 75.6683 | 76.5152 | 121.2662 | 122.5296 | 0.013733 | 122.6212 | 77.8885 | -0.32043 | 122.5296 | 0.013733 | 77.8885 | 121.2662 | 122.6212 | -123.0011 | -122.9416
1293.9688 | 122.7539 | -82.4295 | 40.1733 | -0.17136 | 0.0030164 | 0.001959 | 0.0026191 | 0.00015601 | -7.9062e-05 | -0.0019289 | -82.3059 | 40.2832 | -82.663 | 40.2695 | 38.887 | -3.4561 | -5.3741 | -4.4037 | 40.1962 | -82.7774 | -0.23346 | 0.10986 | 0.1236 | 122.699 | -1.2863 | -0.3479 | 0.022888 | 0.35706 | 77.0554 | 78.0258 | 121.3165 | 122.7127 | 0.1236 | 122.6257 | 78.9734 | -0.3479 | 122.7127 | 0.1236 | 78.9734 | 121.3165 | 122.6257 | -122.8363 | -122.9507
1294.9062 | 122.7951 | -81.4865 | 41.1255 | -0.079803 | 0.0036572 | 0.0068722 | 0.0064643 | -0.0017666 | -0.0017881 | -0.0027835 | -81.3995 | 41.1209 | -81.7841 | 41.217 | 39.9445 | -3.2181 | -5.9509 | -4.2892 | 41.1758 | -81.7795 | -0.29755 | -0.004577 | 0.086975 | 122.7036 | -1.181 | -0.29297 | 0.050354 | 0.38452 | 75.5356 | 77.1973 | 121.431 | 122.6074 | 0.086975 | 122.6624 | 78.2684 | -0.29297 | 122.6074 | 0.086975 | 78.2684 | 121.431 | 122.6624 | -122.9095 | -122.905
1295.9531 | 122.8455 | -82.4387 | 40.155 | -0.034027 | 0.0025892 | 0.0075132 | -0.0040033 | -0.003262 | 0.00034814 | -0.0023563 | -82.3975 | 40.1001 | -82.7271 | 40.274 | 38.9832 | -3.3279 | -6.2073 | -4.6005 | 40.1688 | -82.7499 | -0.28839 | -0.054931 | 0.041199 | 122.7127 | -1.1719 | -0.31128 | 0.013733 | 0.32959 | 76.2314 | 77.8381 | 121.4218 | 122.5388 | 0.041199 | 122.6074 | 79.1107 | -0.31128 | 122.5388 | 0.041199 | 79.1107 | 121.4218 | 122.6074 | -122.8821 | -122.905
1296.9219 | 122.8134 | -82.9056 | 39.6606 | 0.19485 | 0.0013074 | 0.0028134 | 0.0004827 | -0.0036892 | -0.0017881 | -0.0012881 | -82.9376 | 39.505 | -83.2947 | 39.7614 | 38.4064 | -3.5477 | -6.2759 | -4.6097 | 39.6194 | -83.226 | -0.3891 | -0.15564 | -0.032043 | 122.6669 | -1.2543 | -0.32043 | -0.041199 | 0.35706 | 76.6296 | 78.2959 | 121.312 | 122.4106 | -0.032043 | 122.525 | 79.3579 | -0.32043 | 122.4106 | -0.032043 | 79.3579 | 121.312 | 122.525 | -122.9553 | -122.8867
1297.9688 | 122.7631 | -82.2556 | 40.3427 | -0.17136 | 0.00088016 | 0.0058042 | 0.0021917 | -0.0051846 | 0.00034814 | -0.0023563 | -82.2372 | 40.242 | -82.5897 | 40.4343 | 39.1525 | -3.0304 | -5.7449 | -4.0695 | 40.3473 | -82.5943 | -0.33417 | -0.10071 | 0.01831 | 122.6898 | -1.1902 | -0.33875 | 0.004578 | 0.35248 | 76.5106 | 78.186 | 121.4081 | 122.4976 | 0.01831 | 122.6028 | 79.2252 | -0.33875 | 122.4976 | 0.01831 | 79.2252 | 121.4081 | 122.6028 | -122.9324 | -122.937
1298.9062 | 122.7768 | -83.0429 | 39.5645 | -0.19424 | 0.004939 | 0.0087948 | 0.0060369 | -0.0053982 | -0.0013609 | -0.0023563 | -82.9651 | 39.6057 | -83.2947 | 39.6652 | 38.3102 | -3.1952 | -5.7587 | -3.978 | 39.5966 | -83.3633 | -0.25177 | 0.041199 | 0.07782 | 122.7081 | -1.2543 | -0.32043 | 0.032044 | 0.32959 | 77.2842 | 79.0649 | 121.3531 | 122.6486 | 0.07782 | 122.6395 | 79.8477 | -0.32043 | 122.6486 | 0.07782 | 79.8477 | 121.3531 | 122.6395 | -122.8592 | -122.9279
1299.9688 | 122.7081 | -82.9651 | 39.6561 | 0.22537 | 0.0057934 | 0.0079404 | 0.010523 | -0.0017666 | 0.0014163 | -0.0025699 | -82.9239 | 39.6149 | -83.2993 | 39.7156 | 38.4109 | -3.3096 | -5.8044 | -3.9688 | 39.6744 | -83.2993 | -0.33417 | -0.041199 | 0.041199 | 122.6807 | -1.2451 | -0.33417 | 0.01831 | 0.37537 | 77.1606 | 78.9963 | 121.376 | 122.58 | 0.041199 | 122.6395 | 79.6555 | -0.33417 | 122.58 | 0.041199 | 79.6555 | 121.376 | 122.6395 | -122.9553 | -122.9553
1300.9062 | 122.7997 | -83.1665 | 39.3906 | -0.041657 | 0.0030164 | 0.010717 | 0.0086005 | -0.002194 | -0.0024289 | -0.0019289 | -83.2077 | 39.299 | -83.5876 | 39.5325 | 38.1546 | -3.1036 | -6.0791 | -3.8315 | 39.4409 | -83.5464 | -0.42114 | -0.091553 | -0.041199 | 122.699 | -1.236 | -0.37994 | 0.050354 | 0.37994 | 77.0874 | 79.335 | 121.3211 | 122.4655 | -0.041199 | 122.6074 | 80.0629 | -0.37994 | 122.4655 | -0.041199 | 80.0629 | 121.3211 | 122.6074 | -122.9782 | -122.937
1301.9688 | 122.7127 | -82.6172 | 39.9719 | 0.019379 | 0.006648 | 0.0051632 | 0.0071051 | -0.00048499 | -0.00071986 | -0.00086094 | -82.5256 | 40.0543 | -82.8918 | 40.0223 | 38.6765 | -2.5864 | -5.5252 | -3.6255 | 39.9902 | -82.9971 | -0.27466 | 0.082397 | 0.091552 | 122.6395 | -1.2955 | -0.37994 | 0.01831 | 0.36621 | 77.092 | 78.9917 | 121.2936 | 122.6715 | 0.091552 | 122.6074 | 80.0308 | -0.37994 | 122.6715 | 0.091552 | 80.0308 | 121.2936 | 122.6074 | -122.8638 | -122.9691
1302.9062 | 122.7768 | -81.6513 | 40.9653 | -0.24002 | 0.0030164 | 0.0090086 | 0.0021917 | -0.00048499 | 0.0014163 | -0.0040653 | -81.6834 | 40.892 | -82.0221 | 40.9653 | 39.6332 | -2.1927 | -5.2231 | -3.3005 | 40.9241 | -82.0312 | -0.37079 | -0.073242 | -0.032044 | 122.6166 | -1.3321 | -0.37994 | -0.041199 | 0.33874 | 76.4282 | 78.3508 | 121.2845 | 122.5433 | -0.032044 | 122.5754 | 79.4586 | -0.37994 | 122.5433 | -0.032044 | 79.4586 | 121.2845 | 122.5754 | -122.9874 | -122.9965
1303.9531 | 122.85 | -81.9809 | 40.5853 | 0.034637 | 0.0025892 | 0.0017454 | -0.0046441 | -0.0028348 | 0.0033389 | -0.0021427 | -81.8939 | 40.6128 | -82.2372 | 40.7364 | 39.4226 | -2.0508 | -5.1086 | -2.9984 | 40.6174 | -82.2784 | -0.25635 | 0.027466 | 0.086975 | 122.7173 | -1.1627 | -0.29755 | 0.032044 | 0.34332 | 76.8723 | 78.9825 | 121.4035 | 122.5937 | 0.086975 | 122.5983 | 79.9301 | -0.29755 | 122.5937 | 0.086975 | 79.9301 | 121.4035 | 122.5983 | -122.8226 | -122.8638
1304.9062 | 122.7585 | -82.8003 | 39.8071 | 0.1033 | 0.0036572 | 0.006445 | 0.0066779 | -0.003262 | -0.00029266 | -0.0017153 | -82.7225 | 39.8758 | -83.0612 | 39.8529 | 38.4201 | -2.2797 | -5.4611 | -3.479 | 39.8209 | -83.1482 | -0.26093 | 0.068664 | 0.07782 | 122.6532 | -1.387 | -0.3479 | 0.013733 | 0.33875 | 77.3392 | 79.3213 | 121.2204 | 122.6761 | 0.07782 | 122.6212 | 80.5206 | -0.3479 | 122.6761 | 0.07782 | 80.5206 | 121.2204 | 122.6212 | -122.8683 | -122.9553
1305.9531 | 122.7402 | -82.2052 | 40.4068 | -0.24002 | 0.00045296 | -0.00039102 | 0.0026191 | -0.002194 | -0.00050626 | -0.0034243 | -82.0999 | 40.3793 | -82.457 | 40.5258 | 39.2029 | -1.918 | -4.7516 | -3.0487 | 40.4388 | -82.5394 | -0.25177 | -0.027466 | 0.10529 | 122.731 | -1.2039 | -0.33417 | 0.032044 | 0.35706 | 77.4536 | 79.1565 | 121.4081 | 122.5845 | 0.10529 | 122.644 | 80.2872 | -0.33417 | 122.5845 | 0.10529 | 80.2872 | 121.4081 | 122.644 | -122.8638 | -122.9462
1306.9219 | 122.8592 | -81.4819 | 41.0248 | 0.19485 | 0.0028028 | 0.010504 | 0.0051825 | -0.0030484 | -7.9062e-05 | -0.0032107 | -81.34 | 41.0751 | -81.7429 | 41.2537 | 39.8163 | -1.9547 | -5.1498 | -3.2501 | 41.0751 | -81.7841 | -0.26093 | 0.050354 | 0.14191 | 122.7356 | -1.2085 | -0.30212 | 0.050354 | 0.40283 | 76.3321 | 78.2318 | 121.2982 | 122.5571 | 0.14191 | 122.5571 | 79.5273 | -0.30212 | 122.5571 | 0.14191 | 79.5273 | 121.2982 | 122.5571 | -122.7676 | -122.8088
1307.9688 | 122.8271 | -81.9077 | 40.686 | -0.18662 | 0.0042982 | 0.0072996 | 0.0011237 | -0.0051846 | -0.00050626 | -0.0040653 | -81.7749 | 40.6952 | -82.1457 | 40.7867 | 39.4363 | -2.0691 | -5.072 | -3.2181 | 40.6403 | -82.2693 | -0.23804 | 0.009155 | 0.13275 | 122.6944 | -1.2497 | -0.36163 | -0.045776 | 0.37079 | 76.8356 | 78.6896 | 121.344 | 122.6028 | 0.13275 | 122.5479 | 79.8386 | -0.36163 | 122.6028 | 0.13275 | 79.8386 | 121.344 | 122.5479 | -122.8317 | -122.9553
1308.9062 | 122.7814 | -81.6193 | 40.979 | -0.064545 | 0.0053662 | 0.0072996 | 0.0081733 | -0.0041166 | -0.0020017 | -0.0062015 | -81.5048 | 40.9882 | -81.9168 | 41.1072 | 39.6057 | -1.973 | -5.1315 | -3.3051 | 40.9927 | -81.9855 | -0.29755 | 0.009155 | 0.11444 | 122.7264 | -1.3733 | -0.36621 | 0.013733 | 0.41199 | 76.4877 | 78.3142 | 121.225 | 122.6074 | 0.11444 | 122.612 | 79.6463 | -0.36621 | 122.6074 | 0.11444 | 79.6463 | 121.225 | 122.612 | -122.8958 | -122.9645
1309.9688 | 122.7768 | -81.5826 | 41.0294 | -0.27817 | 0.0038708 | 0.0028134 | 0.0011237 | -0.0060392 | 0.00056194 | -0.0023563 | -81.5598 | 41.0339 | -81.8848 | 40.9927 | 39.5233 | -2.179 | -5.0034 | -3.3096 | 41.0477 | -81.9122 | -0.30212 | 0.004578 | 0.022889 | 122.5754 | -1.506 | -0.32959 | 0.01831 | 0.32501 | 76.5793 | 78.273 | 121.106 | 122.6166 | 0.022889 | 122.6303 | 79.4037 | -0.32959 | 122.6166 | 0.022889 | 79.4037 | 121.106 | 122.6303 | -122.9141 | -122.9416
1310.9062 | 122.7905 | -82.077 | 40.535 | -0.21713 | 0.0036572 | 0.003027 | 0.0077459 | -0.00091219 | -0.00029266 | -0.0021427 | -81.9855 | 40.5533 | -82.3517 | 40.6494 | 39.2532 | -2.0599 | -5.3329 | -3.4927 | 40.5762 | -82.3975 | -0.27466 | 0.018311 | 0.091552 | 122.7264 | -1.2817 | -0.32044 | 0.041199 | 0.36621 | 76.7441 | 78.5843 | 121.3303 | 122.6303 | 0.091552 | 122.6532 | 80.0171 | -0.32044 | 122.6303 | 0.091552 | 80.0171 | 121.3303 | 122.6532 | -122.8867 | -122.9324
1311.9688 | 122.8317 | -81.5414 | 41.0797 | 0.13382 | 0.0045118 | 0.0058042 | 0.0064643 | -0.0019802 | -0.0013609 | -0.00043374 | -81.4865 | 41.0751 | -81.8298 | 41.0797 | 39.8117 | -2.2522 | -4.9072 | -3.7765 | 41.0751 | -81.8756 | -0.28839 | -0.004578 | 0.054932 | 122.6212 | -1.268 | -0.33417 | -0.004578 | 0.34332 | 76.6342 | 77.7649 | 121.3531 | 122.6166 | 0.054932 | 122.6166 | 79.2892 | -0.33417 | 122.6166 | 0.054932 | 79.2892 | 121.3531 | 122.6166 | -122.9095 | -122.9553
1312.9062 | 122.7814 | -82.045 | 40.5579 | -0.23239 | 0.0025892 | 0.004736 | 0.0032599 | -0.00069859 | -0.00050626 | -0.0027835 | -82.0404 | 40.5304 | -82.3883 | 40.5808 | 39.3265 | -2.2842 | -4.7516 | -3.1952 | 40.5853 | -82.4158 | -0.34332 | -0.027465 | 0.004578 | 122.6257 | -1.2314 | -0.37079 | 0.027466 | 0.3479 | 77.2934 | 78.8498 | 121.3715 | 122.5754 | 0.004578 | 122.6303 | 79.7607 | -0.37079 | 122.5754 | 0.004578 | 79.7607 | 121.3715 | 122.6303 | -122.9462 | -122.9736
1313.9688 | 122.7539 | -82.0129 | 40.6265 | -0.20187 | 0.001521 | 0.0051632 | 0.0013373 | -0.0024076 | 0.00077554 | -0.0015017 | -81.8985 | 40.6311 | -82.2281 | 40.6677 | 39.4318 | -2.3392 | -5.1178 | -3.241 | 40.6586 | -82.3196 | -0.21515 | 0.004578 | 0.11444 | 122.6807 | -1.1948 | -0.3067 | 0.032043 | 0.32959 | 76.8951 | 78.772 | 121.4447 | 122.644 | 0.11444 | 122.6715 | 79.6738 | -0.3067 | 122.644 | 0.11444 | 79.6738 | 121.4447 | 122.6715 | -122.8546 | -122.9462
1314.9062 | 122.7722 | -81.8253 | 40.8005 | -0.0035098 | 0.0047254 | 0.0087948 | 0.0075323 | -0.00048499 | -0.00050626 | -0.0027835 | -81.7062 | 40.8096 | -82.1045 | 40.8279 | 39.5599 | -2.4536 | -5.2139 | -3.2135 | 40.7822 | -82.164 | -0.27924 | 0.009155 | 0.11902 | 122.6532 | -1.2405 | -0.33875 | -0.01831 | 0.39825 | 76.6113 | 78.6118 | 121.3852 | 122.6349 | 0.11902 | 122.6074 | 79.3716 | -0.33875 | 122.6349 | 0.11902 | 79.3716 | 121.3852 | 122.6074 | -122.905 | -122.9645
1315.9531 | 122.8134 | -81.9672 | 40.5945 | 0.080414 | 0.0023756 | 0.0015316 | -0.0007989 | -0.0041166 | -0.0034971 | -0.0021427 | -81.8939 | 40.5853 | -82.2693 | 40.7135 | 39.4501 | -2.4628 | -5.3833 | -3.3096 | 40.6174 | -82.2739 | -0.30212 | -0.009155 | 0.073242 | 122.6807 | -1.1444 | -0.3067 | 0.022889 | 0.37537 | 76.5839 | 78.6575 | 121.4172 | 122.5525 | 0.073242 | 122.5845 | 79.5044 | -0.3067 | 122.5525 | 0.073242 | 79.5044 | 121.4172 | 122.5845 | -122.8638 | -122.8683
1316.9062 | 122.7631 | -81.871 | 40.741 | -0.16373 | 0.0030164 | 0.0038816 | 0.0053961 | -0.0036892 | -0.00093346 | -0.0021427 | -81.8207 | 40.7593 | -82.1823 | 40.8554 | 39.5599 | -2.0645 | -4.8111 | -3.1357 | 40.773 | -82.2235 | -0.31128 | 0.01831 | 0.050354 | 122.7264 | -1.181 | -0.35248 | 0.032043 | 0.36163 | 77.0599 | 78.7354 | 121.431 | 122.6303 | 0.050354 | 122.644 | 79.8065 | -0.35248 | 122.6303 | 0.050354 | 79.8065 | 121.431 | 122.644 | -122.9233 | -122.9645
1317.9688 | 122.7539 | -82.2876 | 40.3336 | -0.29343 | 0.0038708 | 0.0021726 | 0.0009101 | -0.003903 | 0.0014163 | -0.0019289 | -82.2235 | 40.3748 | -82.5577 | 40.3793 | 39.0427 | -2.6642 | -5.7587 | -3.7262 | 40.329 | -82.6447 | -0.27008 | 0.041199 | 0.064087 | 122.6669 | -1.2909 | -0.35706 | -0.004578 | 0.33417 | 76.5289 | 78.5614 | 121.3303 | 122.6624 | 0.064087 | 122.6166 | 79.6234 | -0.35706 | 122.6624 | 0.064087 | 79.6234 | 121.3303 | 122.6166 | -122.8912 | -122.9782
1318.9062 | 122.7722 | -82.1594 | 40.4434 | -0.11795 | 0.0045118 | 0.0077268 | 0.0064643 | -0.0034756 | -0.0011471 | -0.0023563 | -81.8985 | 40.5808 | -82.3471 | 40.6036 | 39.2029 | -2.6047 | -5.6808 | -3.7399 | 40.5167 | -82.4478 | -0.18768 | 0.13733 | 0.26093 | 122.7631 | -1.2405 | -0.28839 | 0.073243 | 0.44861 | 76.4786 | 78.4195 | 121.3623 | 122.7402 | 0.26093 | 122.6761 | 79.5547 | -0.28839 | 122.7402 | 0.26093 | 79.5547 | 121.3623 | 122.6761 | -122.7905 | -122.8912
1319.9531 | 122.7905 | -81.5964 | 41.0385 | -0.17136 | 0.006648 | 0.003668 | 0.0079595 | -0.0026212 | -0.00071986 | -0.0025699 | -81.546 | 40.9973 | -81.9305 | 41.0568 | 39.8575 | -2.5589 | -5.6808 | -3.7994 | 40.9973 | -81.958 | -0.33417 | -0.041199 | 0.050354 | 122.6532 | -1.181 | -0.36163 | -0.041199 | 0.38452 | 75.9155 | 77.7969 | 121.4539 | 122.5937 | 0.050354 | 122.5937 | 79.0375 | -0.36163 | 122.5937 | 0.050354 | 79.0375 | 121.4539 | 122.5937 | -122.9691 | -122.9965
1320.9062 | 122.7905 | -80.2643 | 42.3523 | -0.064545 | 0.0042982 | 0.0049496 | 0.0090277 | -5.7592e-05 | -0.0022153 | -0.0021427 | -80.1956 | 42.2974 | -80.603 | 42.4759 | 41.0751 | -2.4536 | -5.452 | -3.7079 | 42.3477 | -80.5984 | -0.33875 | -0.054932 | 0.068664 | 122.7402 | -1.2772 | -0.33417 | -0.004578 | 0.40741 | 74.8123 | 76.5564 | 121.3394 | 122.5616 | 0.068664 | 122.612 | 77.8107 | -0.33417 | 122.5616 | 0.068664 | 77.8107 | 121.3394 | 122.612 | -122.9553 | -122.9507
1321.9688 | 122.7585 | -80.6213 | 42.0136 | -0.20187 | 0.0057934 | 0.0055906 | 0.0049689 | -0.0011258 | 0.00056194 | -0.0015017 | -80.5984 | 41.9632 | -80.9463 | 41.9998 | 40.7089 | -2.4628 | -5.3558 | -3.6758 | 42.0044 | -80.9509 | -0.32501 | -0.050354 | 0.022888 | 122.6212 | -1.3046 | -0.32959 | -0.009155 | 0.3479 | 75.2655 | 76.9455 | 121.3303 | 122.5845 | 0.022888 | 122.6257 | 78.1586 | -0.32959 | 122.5845 | 0.022888 | 78.1586 | 121.3303 | 122.6257 | -122.9599 | -122.9645
1322.9062 | 122.7676 | -79.8615 | 42.7505 | -0.17136 | 0.0036572 | 0.0025998 | 0.0051825 | -0.001553 | -0.0011471 | -0.0027835 | -79.8843 | 42.6865 | -80.2322 | 42.8101 | 41.5375 | -2.1835 | -5.2048 | -3.6026 | 42.7505 | -80.191 | -0.37079 | -0.064087 | -0.022888 | 122.6715 | -1.2131 | -0.32959 | 0 | 0.3479 | 74.6567 | 76.2589 | 121.3989 | 122.5479 | -0.022888 | 122.612 | 77.6779 | -0.32959 | 122.5479 | -0.022888 | 77.6779 | 121.3989 | 122.612 | -122.9828 | -122.9416
1323.9531 | 122.8867 | -81.6605 | 40.9012 | -0.16373 | 0.0051526 | 0.001959 | -0.0025079 | 0.00036961 | 0.0018435 | -0.0023563 | -81.5781 | 40.8417 | -81.9626 | 41.0889 | 39.8941 | -2.5909 | -5.6625 | -3.5477 | 40.9103 | -81.9534 | -0.30212 | -0.059509 | 0.082397 | 122.7493 | -1.0071 | -0.29297 | 0.009155 | 0.38452 | 75.9979 | 78.1128 | 121.5546 | 122.5021 | 0.082397 | 122.5708 | 79.0695 | -0.29297 | 122.5021 | 0.082397 | 79.0695 | 121.5546 | 122.5708 | -122.8638 | -122.8546
1324.9062 | 122.7631 | -80.4108 | 42.2195 | 0.049896 | 0.0047254 | 0.0038816 | 0.0064643 | -0.0024076 | 0.0016299 | -0.0034243 | -80.3879 | 42.215 | -80.7358 | 42.2699 | 40.9882 | -2.4353 | -4.9988 | -3.566 | 42.2424 | -80.7266 | -0.32501 | -0.004577 | 0.022889 | 122.6807 | -1.2314 | -0.31586 | 0.022889 | 0.3479 | 75.412 | 76.8448 | 121.3989 | 122.6257 | 0.022889 | 122.6532 | 77.9755 | -0.31586 | 122.6257 | 0.022889 | 77.9755 | 121.3989 | 122.6532 | -122.9553 | -122.9462
1325.9688 | 122.8409 | -80.0308 | 42.5171 | -0.018768 | 0.0028028 | 0.0049496 | -0.0025079 | -0.0051846 | 0.0016299 | -0.0032107 | -80.0217 | 42.5079 | -80.3375 | 42.6819 | 41.391 | -2.1011 | -5.4199 | -3.3554 | 42.5446 | -80.3879 | -0.3067 | -0.009155 | 0.009156 | 122.7127 | -1.1261 | -0.35706 | 0.027466 | 0.31586 | 74.6109 | 76.6754 | 121.4218 | 122.5388 | 0.009156 | 122.5754 | 77.9297 | -0.35706 | 122.5388 | 0.009156 | 77.9297 | 121.4218 | 122.5754 | -122.8546 | -122.905
1326.9062 | 122.7402 | -80.1361 | 42.4896 | -0.17899 | 0.0042982 | 0.004736 | 0.0051825 | -0.004971 | 0.00098914 | -0.0021427 | -80.2185 | 42.3981 | -80.5527 | 42.4988 | 41.2079 | -2.0462 | -5.0262 | -3.3325 | 42.4576 | -80.5023 | -0.41657 | -0.091553 | -0.082398 | 122.6349 | -1.2817 | -0.36621 | -0.032043 | 0.33417 | 75.1099 | 76.8036 | 121.344 | 122.5342 | -0.082398 | 122.5937 | 78.0899 | -0.36621 | 122.5342 | -0.082398 | 78.0899 | 121.344 | 122.5937 | -123.0423 | -122.9919
1327.9062 | 122.7905 | -81.4682 | 41.1301 | -0.21713 | 0.0038708 | 0.0068722 | 0.0060369 | -0.0026212 | -0.00050626 | -0.0025699 | -81.3171 | 41.2445 | -81.6925 | 41.304 | 39.9719 | -2.2842 | -4.8569 | -3.4698 | 41.1804 | -81.7886 | -0.2243 | 0.11444 | 0.15106 | 122.7722 | -1.1581 | -0.32043 | 0.050354 | 0.37537 | 76.6113 | 77.9984 | 121.4401 | 122.7127 | 0.15106 | 122.6486 | 79.184 | -0.32043 | 122.7127 | 0.15106 | 79.184 | 121.4401 | 122.6486 | -122.8226 | -122.9187
1328.9062 | 122.7631 | -81.5323 | 41.0843 | -0.026398 | 0.0025892 | 0.0070858 | 0.0073187 | -0.00091219 | 0.0020571 | -0.0027835 | -81.3538 | 41.1209 | -81.7657 | 41.1942 | 39.8987 | -2.5406 | -5.5801 | -3.6026 | 41.1163 | -81.8481 | -0.23346 | 0.036621 | 0.17853 | 122.7264 | -1.1856 | -0.31586 | 0.032043 | 0.41199 | 75.9521 | 77.9297 | 121.431 | 122.6532 | 0.17853 | 122.6486 | 78.9917 | -0.31586 | 122.6532 | 0.17853 | 78.9917 | 121.431 | 122.6486 | -122.85 | -122.9324
1329.9688 | 122.8134 | -80.7632 | 41.8167 | -0.14847 | 0.0010938 | 0.0038816 | 0.0017645 | -0.002194 | -0.00029266 | -0.0015017 | -80.6671 | 41.803 | -81.0562 | 41.9495 | 40.7547 | -2.3849 | -5.4153 | -3.3371 | 41.8259 | -81.0883 | -0.29297 | -0.013732 | 0.096131 | 122.7127 | -1.062 | -0.32501 | 0.009156 | 0.3891 | 75.3479 | 77.4261 | 121.5179 | 122.5662 | 0.096131 | 122.5891 | 78.3783 | -0.32501 | 122.5662 | 0.096131 | 78.3783 | 121.5179 | 122.5891 | -122.8729 | -122.905
1330.9062 | 122.7448 | -80.6305 | 42.009 | -0.19424 | 0.0038708 | 0.0066586 | 0.0051825 | -0.0041166 | -0.00071986 | -0.0040653 | -80.5389 | 41.9998 | -80.8868 | 42.041 | 40.7181 | -2.5177 | -5.5023 | -3.3463 | 42.009 | -80.9418 | -0.25635 | -0.009155 | 0.091553 | 122.6715 | -1.2909 | -0.31128 | 0 | 0.3479 | 75.1282 | 77.2842 | 121.3486 | 122.6303 | 0.091553 | 122.6395 | 78.1128 | -0.31128 | 122.6303 | 0.091553 | 78.1128 | 121.3486 | 122.6395 | -122.8958 | -122.9507
1331.9688 | 122.8409 | -81.134 | 41.4597 | -0.2858 | 0.0040846 | 0.0040952 | 0.0002691 | -0.0030484 | -0.00071986 | -0.0023563 | -81.0928 | 41.3681 | -81.4682 | 41.5649 | 40.2191 | -2.7283 | -5.6305 | -3.2135 | 41.4139 | -81.4682 | -0.33417 | -0.091553 | 0.041199 | 122.699 | -1.2405 | -0.33417 | -0.045777 | 0.37537 | 75.5035 | 77.9205 | 121.3531 | 122.5021 | 0.041199 | 122.5479 | 78.4058 | -0.33417 | 122.5021 | 0.041199 | 78.4058 | 121.3531 | 122.5479 | -122.9279 | -122.9279
1332.9062 | 122.7631 | -81.2027 | 41.4413 | 0.66788 | 0.0040846 | 0.0032406 | 0.0015509 | -0.0034756 | 0.00013454 | -0.0051333 | -81.0379 | 41.4825 | -81.4224 | 41.4825 | 40.21 | -3.0258 | -5.3055 | -3.4515 | 41.4734 | -81.5094 | -0.21973 | 0.041199 | 0.16479 | 122.6852 | -1.2314 | -0.3067 | 0.032044 | 0.38452 | 75.8972 | 77.7512 | 121.4127 | 122.6852 | 0.16479 | 122.6761 | 78.1769 | -0.3067 | 122.6852 | 0.16479 | 78.1769 | 121.4127 | 122.6761 | -122.8638 | -122.9507
1333.9531 | 122.7631 | -81.0974 | 41.5283 | -0.24765 | 0.0042982 | 0.00067718 | 0.0030463 | -0.0043302 | -0.0011471 | -0.0032107 | -81.0333 | 41.4825 | -81.3721 | 41.6153 | 40.2512 | -3.0853 | -5.8868 | -3.8727 | 41.5054 | -81.395 | -0.27466 | -0.045776 | 0.064087 | 122.7127 | -1.2772 | -0.29755 | -0.022888 | 0.33874 | 75.2106 | 77.2247 | 121.3486 | 122.58 | 0.064087 | 122.6028 | 78.0121 | -0.29755 | 122.58 | 0.064087 | 78.0121 | 121.3486 | 122.6028 | -122.9004 | -122.9233
1334.9062 | 122.7722 | -80.7953 | 41.8533 | -0.17136 | 0.0047254 | 0.0077268 | 0.0062507 | -0.0026212 | -0.00071986 | -0.0027835 | -80.6808 | 41.9037 | -81.0287 | 41.9083 | 40.5441 | -2.3804 | -5.5481 | -3.717 | 41.8854 | -81.0791 | -0.23346 | 0.050354 | 0.11444 | 122.7036 | -1.3092 | -0.28381 | 0.032043 | 0.3479 | 75.2472 | 77.0782 | 121.3394 | 122.699 | 0.11444 | 122.6807 | 78.4149 | -0.28381 | 122.699 | 0.11444 | 78.4149 | 121.3394 | 122.6807 | -122.8821 | -122.9324
1335.9688 | 122.7585 | -81.4407 | 41.2308 | -0.25528 | 0.0013074 | 0.0045224 | 0.0043281 | -0.0030484 | -0.0013609 | -0.0034243 | -81.4911 | 41.0431 | -81.8298 | 41.217 | 39.8849 | -2.1835 | -5.2643 | -3.4653 | 41.1026 | -81.7841 | -0.3891 | -0.18768 | -0.050354 | 122.6578 | -1.3458 | -0.34332 | -0.12817 | 0.33875 | 76.1765 | 77.9755 | 121.3257 | 122.4838 | -0.050354 | 122.5433 | 79.2572 | -0.34332 | 122.4838 | -0.050354 | 79.2572 | 121.3257 | 122.5433 | -123.0606 | -123.0148
1336.9062 | 122.7768 | -81.5735 | 41.0522 | 0.0041197 | 0.0036572 | 0.0049496 | 0.0045417 | -0.0026212 | -0.00071986 | -0.0040653 | -81.4911 | 41.1209 | -81.7978 | 41.1301 | 39.7842 | -2.5589 | -5.5252 | -3.7125 | 41.0706 | -81.8985 | -0.22431 | 0.068665 | 0.082397 | 122.7036 | -1.268 | -0.32501 | 0.018311 | 0.3067 | 76.0483 | 77.861 | 121.3577 | 122.6944 | 0.082397 | 122.644 | 79.0146 | -0.32501 | 122.6944 | 0.082397 | 79.0146 | 121.3577 | 122.644 | -122.85 | -122.9507
1337.9688 | 122.8363 | -81.7383 | 40.8508 | 0.1796 | 0.0023756 | 0.0043088 | -0.0003717 | -0.0047574 | -0.00050626 | -0.0023563 | -81.7612 | 40.8142 | -82.0175 | 40.8875 | 39.6149 | -2.655 | -6.015 | -3.7308 | 40.8142 | -82.0221 | -0.27924 | -0.036621 | -0.022888 | 122.6257 | -1.236 | -0.28381 | -0.036621 | 0.25635 | 75.7233 | 78.0075 | 121.3531 | 122.5525 | -0.022888 | 122.5525 | 79.0833 | -0.28381 | 122.5525 | -0.022888 | 79.0833 | 121.3531 | 122.5525 | -122.8683 | -122.8729
1338.9062 | 122.7676 | -81.0837 | 41.5375 | -0.17136 | 0.0025892 | 0.0015316 | 0.0075323 | -0.0028348 | 0.0012027 | -0.0032107 | -80.9738 | 41.6473 | -81.2943 | 41.6748 | 40.3976 | -3.2913 | -6.8573 | -4.3945 | 41.5878 | -81.3995 | -0.21057 | 0.10986 | 0.10986 | 122.7585 | -1.1398 | -0.31586 | 0.050354 | 0.32043 | 74.2264 | 76.6891 | 121.4813 | 122.731 | 0.10986 | 122.6715 | 77.7924 | -0.31586 | 122.731 | 0.10986 | 77.7924 | 121.4813 | 122.6715 | -122.8317 | -122.937
1339.9531 | 122.7814 | -81.5735 | 41.1072 | -0.25528 | 0.00323 | 0.001959 | 0.0041143 | -0.0047574 | -0.00029266 | -0.0042789 | -81.5277 | 41.0797 | -81.7886 | 41.1392 | 39.7339 | -3.6896 | -7.1594 | -4.4403 | 41.0843 | -81.9031 | -0.21515 | -0.027466 | 0.045776 | 122.7127 | -1.3733 | -0.32959 | -0.022888 | 0.26093 | 74.4141 | 77.1332 | 121.3074 | 122.6532 | 0.045776 | 122.6578 | 77.8839 | -0.32959 | 122.6532 | 0.045776 | 77.8839 | 121.3074 | 122.6578 | -122.8958 | -123.0103
1340.9062 | 122.7539 | -81.6788 | 40.9607 | -0.11032 | 0.0025892 | 0.0028134 | 0.0017645 | -0.003903 | -0.0013609 | -0.0042789 | -81.6422 | 40.9103 | -81.9946 | 41.0294 | 39.6561 | -4.0146 | -7.2372 | -4.454 | 40.9744 | -81.9901 | -0.31586 | -0.050354 | 0.036621 | 122.7081 | -1.3046 | -0.31128 | 0.013733 | 0.35248 | 74.4415 | 77.2247 | 121.3348 | 122.5891 | 0.036621 | 122.6532 | 77.6642 | -0.31128 | 122.5891 | 0.036621 | 77.6642 | 121.3348 | 122.6532 | -122.9553 | -122.9507
1341.9688 | 122.8821 | -80.0766 | 42.5034 | 0.1796 | 2.5564e-05 | 0.0032406 | -0.0001581 | -0.0041166 | -0.0017881 | -0.0034243 | -80.0674 | 42.3706 | -80.4245 | 42.6361 | 41.2491 | -3.4607 | -6.9855 | -3.9597 | 42.453 | -80.365 | -0.3479 | -0.13275 | 0.009155 | 122.7127 | -1.2543 | -0.28839 | -0.050354 | 0.35706 | 73.0911 | 76.1169 | 121.3257 | 122.4472 | 0.009155 | 122.5296 | 76.6159 | -0.28839 | 122.4472 | 0.009155 | 76.6159 | 121.3257 | 122.5296 | -122.9279 | -122.8683
1342.9062 | 122.7997 | -80.3467 | 42.2653 | -0.11032 | 0.0053662 | 0.0032406 | 0.0081733 | -0.0026212 | -0.0015745 | -0.0034243 | -80.3238 | 42.2012 | -80.6946 | 42.3569 | 40.9882 | -3.7949 | -7.3013 | -4.2526 | 42.2424 | -80.7129 | -0.3479 | -0.064087 | 0.022888 | 122.7036 | -1.2772 | -0.36621 | -0.022888 | 0.37079 | 73.0453 | 76.0941 | 121.3348 | 122.5479 | 0.022888 | 122.5891 | 76.5518 | -0.36621 | 122.5479 | 0.022888 | 76.5518 | 121.3348 | 122.5891 | -122.9599 | -122.9782
1343.9531 | 122.8775 | -80.5298 | 42.0547 | -0.13321 | 0.001521 | 0.003668 | 5.5496e-05 | -0.003262 | -0.0013609 | -0.0023563 | -80.452 | 41.9815 | -80.8228 | 42.1509 | 40.86 | -3.6621 | -7.3059 | -4.1016 | 42.0227 | -80.8411 | -0.29297 | -0.073243 | 0.07782 | 122.6807 | -1.1948 | -0.31128 | -0.032044 | 0.37079 | 73.2239 | 76.4282 | 121.3898 | 122.5113 | 0.07782 | 122.5525 | 76.8677 | -0.31128 | 122.5113 | 0.07782 | 76.8677 | 121.3898 | 122.5525 | -122.8775 | -122.8958
1344.9062 | 122.7585 | -80.4428 | 42.1646 | -0.19424 | 0.0023756 | 0.0011044 | 0.0071051 | -0.0030484 | -0.0030697 | -0.0027835 | -80.3146 | 42.2791 | -80.6168 | 42.2928 | 40.9653 | -4.3304 | -7.4936 | -4.4998 | 42.2195 | -80.7724 | -0.17395 | 0.11444 | 0.12817 | 122.7356 | -1.1993 | -0.32959 | 0.054931 | 0.30212 | 72.9492 | 75.943 | 121.4081 | 122.7219 | 0.12817 | 122.6624 | 76.1124 | -0.32959 | 122.7219 | 0.12817 | 76.1124 | 121.4081 | 122.6624 | -122.7814 | -122.937
1345.9688 | 122.8409 | -80.4886 | 42.1143 | 0.12619 | 0.0028028 | 0.004736 | 0.0002691 | -0.0060392 | 0.00013454 | -0.0027835 | -80.4794 | 42.0593 | -80.7907 | 42.2516 | 40.947 | -3.5522 | -7.0267 | -3.9825 | 42.1234 | -80.7907 | -0.30212 | -0.054932 | 0.009155 | 122.7402 | -1.1673 | -0.30212 | 0.009155 | 0.31128 | 73.4619 | 76.506 | 121.4355 | 122.5479 | 0.009155 | 122.612 | 76.9363 | -0.30212 | 122.5479 | 0.009155 | 76.9363 | 121.4355 | 122.612 | -122.905 | -122.905
1346.9062 | 122.7631 | -80.1636 | 42.5079 | -0.11795 | 0.0028028 | 0.004736 | 0.0034735 | -0.0056118 | -0.00029266 | -0.0064151 | -80.0903 | 42.4622 | -80.4062 | 42.5766 | 41.2445 | -3.6346 | -6.7154 | -3.8956 | 42.5079 | -80.4794 | -0.24262 | -0.045777 | 0.073242 | 122.7402 | -1.2634 | -0.31586 | 0 | 0.31586 | 73.4482 | 76.268 | 121.4081 | 122.6257 | 0.073242 | 122.6715 | 76.5289 | -0.31586 | 122.6257 | 0.073242 | 76.5289 | 121.4081 | 122.6715 | -122.9141 | -122.9874
1347.9688 | 122.8226 | -81.1386 | 41.4734 | -0.25528 | 0.001521 | 0.0023862 | 0.0021917 | -0.0060392 | -0.00093346 | -0.0021427 | -81.0242 | 41.4551 | -81.395 | 41.6061 | 40.329 | -3.9871 | -7.1136 | -4.0329 | 41.4688 | -81.4728 | -0.25635 | -0.018311 | 0.11444 | 122.7448 | -1.1444 | -0.33417 | -0.004578 | 0.37079 | 74.025 | 77.1057 | 121.4676 | 122.5937 | 0.11444 | 122.6074 | 77.1515 | -0.33417 | 122.5937 | 0.11444 | 77.1515 | 121.4676 | 122.6074 | -122.8683 | -122.9462
1348.9062 | 122.818 | -81.4224 | 41.2033 | -0.11795 | 0.0023756 | 0.0025998 | 0.010523 | -0.0017666 | -0.0032835 | -0.0044925 | -81.3721 | 41.1575 | -81.7383 | 41.3315 | 40.0497 | -4.2526 | -6.9534 | -4.2206 | 41.2033 | -81.7566 | -0.31586 | -0.045776 | 0.050354 | 122.7539 | -1.1536 | -0.33417 | 0 | 0.36621 | 74.469 | 77.2018 | 121.4722 | 122.58 | 0.050354 | 122.6257 | 77.1698 | -0.33417 | 122.58 | 0.050354 | 77.1698 | 121.4722 | 122.6257 | -122.9416 | -122.9599
1349.9688 | 122.85 | -81.2256 | 41.3773 | 0.019379 | 0.001521 | 0.0040952 | -0.0003717 | -0.0034756 | -0.00093346 | -0.0034243 | -81.1798 | 41.3315 | -81.514 | 41.5283 | 40.2237 | -4.129 | -7.0862 | -4.3076 | 41.3635 | -81.5414 | -0.28839 | -0.045776 | 0.045776 | 122.7539 | -1.1536 | -0.31586 | -0.013733 | 0.33417 | 74.1394 | 76.918 | 121.4493 | 122.5571 | 0.045776 | 122.5891 | 77.0966 | -0.31586 | 122.5571 | 0.045776 | 77.0966 | 121.4493 | 122.5891 | -122.8912 | -122.9187
1350.9062 | 122.8088 | -81.1844 | 41.4047 | -0.26291 | 0.002162 | 0.0025998 | 0.0043281 | -0.0056118 | -0.0024289 | -0.0042789 | -81.1752 | 41.3406 | -81.514 | 41.5604 | 40.3564 | -4.1382 | -6.8665 | -4.1016 | 41.4093 | -81.514 | -0.32959 | -0.064087 | 0.009155 | 122.7448 | -1.0483 | -0.32959 | 0.004578 | 0.33875 | 74.3179 | 77.0828 | 121.5408 | 122.525 | 0.009155 | 122.5937 | 77.0462 | -0.32959 | 122.525 | 0.009155 | 77.0462 | 121.5408 | 122.5937 | -122.9187 | -122.9187
1351.9531 | 122.7585 | -81.9305 | 40.7272 | -0.44601 | 0.00088016 | -0.001459 | 0.0056097 | -0.0043302 | 0.00056194 | -0.0036379 | -81.9122 | 40.7043 | -82.1915 | 40.7776 | 39.5233 | -4.39 | -6.8161 | -4.3716 | 40.6952 | -82.2372 | -0.26093 | -0.022888 | 0.018311 | 122.7081 | -1.2039 | -0.3067 | -0.032044 | 0.27924 | 75.1144 | 77.5589 | 121.4539 | 122.6349 | 0.018311 | 122.6257 | 77.5406 | -0.3067 | 122.6349 | 0.018311 | 77.5406 | 121.4539 | 122.6257 | -122.9187 | -122.9645
1352.9062 | 122.7631 | -82.0587 | 40.5808 | 0.034637 | 0.0030164 | 0.0028134 | 0.0092413 | -0.0036892 | -0.0015745 | -0.0029971 | -82.0267 | 40.5304 | -82.3929 | 40.6586 | 39.3768 | -4.422 | -7.1869 | -4.7012 | 40.5808 | -82.4158 | -0.33417 | -0.050354 | 0.032044 | 122.7173 | -1.2039 | -0.35706 | 0 | 0.36621 | 74.8718 | 77.3575 | 121.4355 | 122.5891 | 0.032044 | 122.6395 | 77.6367 | -0.35706 | 122.5891 | 0.032044 | 77.6367 | 121.4355 | 122.6395 | -122.9736 | -122.9965
1353.9688 | 122.8546 | -81.6147 | 41.0065 | -0.21713 | 0.0019482 | 0.003668 | 0.0006965 | -0.0030484 | -0.0011471 | -0.0036379 | -81.5781 | 40.9561 | -81.9077 | 41.1118 | 39.8117 | -4.2252 | -6.7795 | -4.4998 | 40.9973 | -81.9214 | -0.29297 | -0.050354 | 0.036621 | 122.7264 | -1.1948 | -0.3067 | -0.009156 | 0.32959 | 74.8352 | 77.1149 | 121.4264 | 122.5708 | 0.036621 | 122.612 | 77.3895 | -0.3067 | 122.5708 | 0.036621 | 77.3895 | 121.4264 | 122.612 | -122.9141 | -122.9279
1354.9062 | 122.7814 | -82.5119 | 40.1047 | 0.011749 | 0.0030164 | 0.0072996 | 0.0092413 | -0.0024076 | -0.00071986 | -0.0021427 | -82.4661 | 40.0818 | -82.8369 | 40.1825 | 38.8596 | -4.2526 | -6.7291 | -4.7562 | 40.1047 | -82.8644 | -0.32501 | -0.022888 | 0.045777 | 122.6944 | -1.2451 | -0.35248 | 0 | 0.37079 | 75.7828 | 77.7557 | 121.3715 | 122.5937 | 0.045777 | 122.6166 | 78.2593 | -0.35248 | 122.5937 | 0.045777 | 78.2593 | 121.3715 | 122.6166 | -122.9416 | -122.9691
1355.9688 | 122.8958 | -82.2281 | 40.3519 | 0.11093 | 0.0028028 | 0.0040952 | 0.0051825 | -0.00048499 | -0.00050626 | 0.00042086 | -82.1915 | 40.3244 | -82.5439 | 40.5212 | 39.2075 | -3.9871 | -6.8481 | -4.6326 | 40.3564 | -82.4844 | -0.31586 | -0.027466 | 0.036621 | 122.7493 | -1.1444 | -0.25635 | 0.004577 | 0.35248 | 75.3799 | 77.5955 | 121.4355 | 122.5525 | 0.036621 | 122.5845 | 78.241 | -0.25635 | 122.5525 | 0.036621 | 78.241 | 121.4355 | 122.5845 | -122.8958 | -122.8363
1356.9062 | 122.6944 | -81.5094 | 41.1255 | -0.17136 | 0.0030164 | 0.00046358 | 0.0009101 | -0.0062528 | 0.00034814 | -0.0047061 | -81.5277 | 41.066 | -81.8481 | 41.153 | 39.8483 | -3.8681 | -6.5369 | -4.4083 | 41.1072 | -81.8115 | -0.33875 | -0.059509 | -0.018311 | 122.6624 | -1.2772 | -0.30212 | -0.01831 | 0.32044 | 74.9725 | 77.1011 | 121.3577 | 122.5754 | -0.018311 | 122.6166 | 77.6413 | -0.30212 | 122.5754 | -0.018311 | 77.6413 | 121.3577 | 122.6166 | -122.9736 | -122.937
1357.9688 | 122.7997 | -81.6284 | 40.9836 | 0.011749 | 0.0034436 | 0.0038816 | 0.0098823 | -0.0030484 | -0.0028561 | -0.0021427 | -81.5872 | 40.947 | -81.9351 | 41.0477 | 39.7797 | -4.0329 | -7.1457 | -4.9484 | 40.9698 | -81.9946 | -0.3067 | -0.036622 | 0.041199 | 122.6761 | -1.2039 | -0.36621 | -0.013733 | 0.3479 | 74.4827 | 76.68 | 121.4081 | 122.5754 | 0.041199 | 122.5983 | 77.5955 | -0.36621 | 122.5754 | 0.041199 | 77.5955 | 121.4081 | 122.5983 | -122.9187 | -122.9782
1358.9062 | 122.7585 | -81.4407 | 41.1942 | -0.049286 | 0.004939 | 0.0017454 | 0.0004827 | -0.0034756 | -0.00029266 | -0.0025699 | -81.5872 | 41.0202 | -81.9031 | 41.1621 | 39.9673 | -3.8132 | -6.3171 | -4.4724 | 41.1667 | -81.7703 | -0.46234 | -0.17395 | -0.14648 | 122.6028 | -1.2268 | -0.32959 | -0.027466 | 0.31586 | 75.1236 | 76.9684 | 121.4081 | 122.4609 | -0.14648 | 122.6074 | 77.6276 | -0.32959 | 122.4609 | -0.14648 | 77.6276 | 121.4081 | 122.6074 | -123.0972 | -122.9645
1359.9688 | 122.8226 | -81.6559 | 40.9195 | -0.11795 | 0.0042982 | 0.0066586 | 0.0092413 | -0.0017666 | -0.0011471 | -0.0042789 | -81.5964 | 40.947 | -81.9626 | 41.0019 | 39.7614 | -3.9871 | -6.4499 | -4.715 | 40.9744 | -82.0038 | -0.3067 | 0.027465 | 0.059509 | 122.6578 | -1.1581 | -0.3479 | 0.054931 | 0.36621 | 75.206 | 76.9409 | 121.4172 | 122.6028 | 0.059509 | 122.6303 | 77.6688 | -0.3479 | 122.6028 | 0.059509 | 77.6688 | 121.4172 | 122.6303 | -122.8821 | -122.9233
1360.9062 | 122.7997 | -81.665 | 40.9836 | -0.2095 | 0.0019482 | 0.00089078 | 0.0011237 | -0.0034756 | -0.00093346 | -0.0036379 | -81.6788 | 40.8508 | -82.0084 | 40.9836 | 39.6927 | -3.9963 | -6.8893 | -4.8203 | 40.9424 | -81.9855 | -0.34332 | -0.13275 | -0.013733 | 122.6486 | -1.2909 | -0.32044 | -0.041199 | 0.32959 | 74.7757 | 76.8448 | 121.3577 | 122.5159 | -0.013733 | 122.6074 | 77.6688 | -0.32044 | 122.5159 | -0.013733 | 77.6688 | 121.3577 | 122.6074 | -122.9919 | -122.9691
1361.9688 | 122.8821 | -82.1228 | 40.4297 | -0.064545 | 0.001521 | 0.0032406 | -0.0012261 | -0.0034756 | -0.00029266 | -0.0019289 | -82.2189 | 40.274 | -82.5714 | 40.4709 | 39.1891 | -4.1061 | -7.0221 | -4.715 | 40.3564 | -82.4936 | -0.44861 | -0.15564 | -0.09613 | 122.5937 | -1.2405 | -0.37079 | -0.073242 | 0.35248 | 75.1007 | 77.4078 | 121.312 | 122.3969 | -0.09613 | 122.4792 | 78.0167 | -0.37079 | 122.3969 | -0.09613 | 78.0167 | 121.312 | 122.4792 | -123.0011 | -122.9233
1362.9219 | 122.8683 | -81.9901 | 40.6219 | 0.0041197 | 0.0028028 | 0.0015316 | -0.0001581 | -0.0068936 | 0.00013454 | -0.0019289 | -82.0084 | 40.48 | -82.3242 | 40.6677 | 39.3539 | -4.2068 | -7.0816 | -5.0308 | 40.5624 | -82.2922 | -0.33417 | -0.14191 | -0.018311 | 122.6578 | -1.268 | -0.30212 | -0.059509 | 0.31586 | 74.9084 | 76.9592 | 121.344 | 122.4701 | -0.018311 | 122.5525 | 77.7832 | -0.30212 | 122.4701 | -0.018311 | 77.7832 | 121.344 | 122.5525 | -122.9462 | -122.9141
1363.9531 | 122.8867 | -82.2693 | 40.3107 | 0.0041197 | 0.0010938 | 0.00024998 | 0.0032599 | -0.0053982 | -0.0013609 | -0.0012881 | -82.3242 | 40.1138 | -82.6675 | 40.448 | 39.1846 | -4.2023 | -6.8069 | -4.8157 | 40.2557 | -82.6035 | -0.39825 | -0.19684 | -0.054932 | 122.7173 | -1.1261 | -0.33417 | -0.054932 | 0.34332 | 75.4623 | 77.4536 | 121.4539 | 122.3831 | -0.054932 | 122.525 | 78.067 | -0.33417 | 122.3831 | -0.054932 | 78.067 | 121.4539 | 122.525 | -122.9782 | -122.9141
1364.9062 | 122.8455 | -81.8161 | 40.8096 | -0.064545 | 0.0038708 | 0.0075132 | 0.0098823 | -0.0041166 | -0.00093346 | -0.0023563 | -81.8619 | 40.6311 | -82.2876 | 40.8188 | 39.5279 | -4.1794 | -7.0953 | -4.8843 | 40.741 | -82.196 | -0.4715 | -0.17853 | -0.045776 | 122.6349 | -1.2817 | -0.37994 | -0.068664 | 0.42572 | 74.7208 | 76.9318 | 121.344 | 122.4472 | -0.045776 | 122.5571 | 77.6367 | -0.37994 | 122.4472 | -0.045776 | 77.6367 | 121.344 | 122.5571 | -123.0972 | -123.0057
1365.9531 | 122.8912 | -81.7062 | 40.8325 | -3.658 | -0.001256 | 0.0011044 | 0.0009101 | -0.0030484 | -0.0020017 | -0.0034243 | -81.7245 | 40.8279 | -82.0312 | 41.0843 | 39.7659 | -4.1977 | -7.0816 | -4.7836 | 40.86 | -82.045 | -0.32501 | -0.004578 | -0.01831 | 122.7905 | -1.0666 | -0.33875 | 0.027465 | 0.3067 | 74.6246 | 76.9226 | 121.4722 | 122.5342 | -0.01831 | 122.5662 | 77.5085 | -0.33875 | 122.5342 | -0.01831 | 77.5085 | 121.4722 | 122.5662 | -122.8638 | -122.8775
1366.9062 | 122.7585 | -82.1457 | 40.4938 | 1.2096 | 0.0030164 | 0.0045224 | 0.0058233 | -0.00668 | -0.00050626 | -0.0038515 | -82.2189 | 40.3839 | -82.5394 | 40.4755 | 39.2441 | -4.3671 | -7.3059 | -5.0766 | 40.4526 | -82.489 | -0.39368 | -0.10986 | -0.073242 | 122.6212 | -1.2497 | -0.34332 | -0.041198 | 0.32043 | 74.8398 | 77.0691 | 121.3898 | 122.5296 | -0.073242 | 122.5983 | 77.7786 | -0.34332 | 122.5296 | -0.073242 | 77.7786 | 121.3898 | 122.5983 | -123.0331 | -122.9828
1367.9844 | 122.7264 | -82.1274 | 40.5487 | 0.12619 | 0.0045118 | 0.0034544 | 0.0066779 | -0.0028348 | -0.0022153 | -0.0038515 | -82.0862 | 40.5167 | -82.4203 | 40.5716 | 39.0427 | -4.6234 | -6.9214 | -4.4449 | 40.5258 | -82.457 | -0.29297 | -0.032043 | 0.041198 | 122.699 | -1.506 | -0.32959 | -0.022888 | 0.33417 | 75.206 | 77.6825 | 121.17 | 122.644 | 0.041198 | 122.6532 | 77.504 | -0.32959 | 122.644 | 0.041198 | 77.504 | 121.17 | 122.6532 | -122.9691 | -123.0057
1368.9062 | 122.8088 | -81.546 | 41.0843 | -0.18662 | 0.0028028 | 0.0079404 | 0.0081733 | -0.0019802 | -0.0015745 | -0.0049197 | -81.4362 | 41.1118 | -81.8436 | 41.3086 | 39.9536 | -4.1656 | -6.5277 | -4.4174 | 41.1942 | -81.8024 | -0.29755 | 0.027465 | 0.10986 | 122.8546 | -1.1307 | -0.25635 | 0.10986 | 0.40741 | 75.0183 | 77.1286 | 121.4996 | 122.6578 | 0.10986 | 122.7402 | 77.3804 | -0.25635 | 122.6578 | 0.10986 | 77.3804 | 121.4996 | 122.7402 | -122.9279 | -122.8867
1369.9688 | 122.7631 | -81.2943 | 41.3589 | -0.24002 | 0.0025892 | 0.003668 | 0.0011237 | -0.0026212 | 0.0026981 | -0.0051333 | -81.221 | 41.3773 | -81.5506 | 41.3452 | 40.2054 | -3.7262 | -6.3309 | -4.3076 | 41.3818 | -81.6193 | -0.25635 | 0.01831 | 0.073242 | 122.6395 | -1.1536 | -0.32501 | 0.022888 | 0.32959 | 74.9634 | 76.9867 | 121.4996 | 122.6715 | 0.073242 | 122.6761 | 77.5681 | -0.32501 | 122.6715 | 0.073242 | 77.5681 | 121.4996 | 122.6761 | -122.9095 | -122.9782
1370.9062 | 122.7814 | -82.1503 | 40.4938 | 0.034637 | 0.0028028 | 0.0092222 | 0.0071051 | 0.0010104 | -0.0028561 | -0.0034243 | -82.0679 | 40.5075 | -82.4158 | 40.5441 | 39.2944 | -4.0466 | -6.6788 | -4.628 | 40.4846 | -82.4936 | -0.2655 | 0.013733 | 0.082398 | 122.6944 | -1.1993 | -0.34332 | -0.009155 | 0.3479 | 75.4715 | 77.5223 | 121.4447 | 122.6578 | 0.082398 | 122.6349 | 78.1036 | -0.34332 | 122.6578 | 0.082398 | 78.1036 | 121.4447 | 122.6349 | -122.9095 | -122.9874
1371.9688 | 122.8638 | -81.5048 | 41.1163 | 0.0041197 | 0.002162 | 0.00089078 | -0.0012261 | -0.0034756 | -7.9062e-05 | -0.0027835 | -81.4728 | 41.0568 | -81.7886 | 41.185 | 39.9628 | -3.7994 | -7.2281 | -4.6875 | 41.066 | -81.8436 | -0.28381 | -0.059509 | 0.032044 | 122.6898 | -1.1536 | -0.33874 | -0.050354 | 0.31586 | 74.2767 | 76.8173 | 121.4676 | 122.5616 | 0.032044 | 122.5708 | 77.7054 | -0.33874 | 122.5616 | 0.032044 | 77.7054 | 121.4676 | 122.5708 | -122.905 | -122.9599
1372.9219 | 122.7905 | -80.4062 | 42.247 | -0.17899 | 0.0042982 | 0.009863 | 0.0075323 | -0.003903 | 0.0012027 | -0.0027835 | -80.2872 | 42.2012 | -80.7312 | 42.3614 | 41.0339 | -3.6209 | -6.5964 | -4.6783 | 42.2287 | -80.7541 | -0.32501 | -0.045776 | 0.11902 | 122.7676 | -1.2131 | -0.3479 | -0.01831 | 0.44403 | 73.8098 | 75.7278 | 121.4401 | 122.6074 | 0.11902 | 122.6349 | 76.7853 | -0.3479 | 122.6074 | 0.11902 | 76.7853 | 121.4401 | 122.6349 | -122.9782 | -123.0011
1373.9531 | 122.6944 | -81.0471 | 41.597 | -0.23239 | 0.0038708 | 0.00024998 | 0.0030463 | -0.0041166 | -0.0017881 | -0.0025699 | -81.0654 | 41.5649 | -81.3629 | 41.5924 | 40.2924 | -3.7537 | -6.7612 | -4.8752 | 41.6061 | -81.34 | -0.31586 | -0.032044 | -0.018311 | 122.6395 | -1.3046 | -0.29297 | 0.009155 | 0.29755 | 74.2859 | 76.1719 | 121.3394 | 122.612 | -0.018311 | 122.6532 | 77.2934 | -0.29297 | 122.612 | -0.018311 | 77.2934 | 121.3394 | 122.6532 | -122.9599 | -122.937
1374.9062 | 122.7448 | -81.9214 | 40.7272 | -0.087433 | 0.0030164 | 0.004736 | 0.0024053 | -0.0019802 | 0.00034814 | -0.0042789 | -81.8756 | 40.7547 | -82.164 | 40.7959 | 39.505 | -3.8956 | -7.0816 | -5.1453 | 40.7547 | -82.2189 | -0.24261 | 0.027466 | 0.045777 | 122.7173 | -1.2222 | -0.29755 | 0.027466 | 0.28839 | 74.8398 | 76.7761 | 121.4264 | 122.6761 | 0.045777 | 122.6761 | 78.0258 | -0.29755 | 122.6761 | 0.045777 | 78.0258 | 121.4264 | 122.6761 | -122.8912 | -122.9462
1375.9844 | 122.7997 | -81.4774 | 41.1575 | 0.15671 | 0.0034436 | 0.001318 | 0.0071051 | -0.0013394 | -0.0011471 | -0.00021994 | -81.4957 | 41.0889 | -81.8253 | 41.1987 | 39.9811 | -3.8132 | -6.8939 | -5.4749 | 41.1392 | -81.8069 | -0.3479 | -0.068665 | -0.018311 | 122.6761 | -1.1765 | -0.32959 | -0.018311 | 0.32959 | 74.5834 | 76.0025 | 121.4584 | 122.5662 | -0.018311 | 122.6166 | 77.6642 | -0.32959 | 122.5662 | -0.018311 | 77.6642 | 121.4584 | 122.6166 | -122.9828 | -122.9645
1376.9062 | 122.7722 | -81.134 | 41.5283 | -0.1561 | 0.004939 | 0.0023862 | 0.0056097 | -0.0030484 | -0.0024289 | -0.0053469 | -81.0562 | 41.5604 | -81.3766 | 41.5878 | 40.3702 | -3.8864 | -6.5506 | -5.0446 | 41.5375 | -81.4133 | -0.24262 | 0.032044 | 0.07782 | 122.7219 | -1.1581 | -0.27924 | 0.009156 | 0.32044 | 74.5834 | 76.0895 | 121.5042 | 122.6944 | 0.07782 | 122.6715 | 77.2476 | -0.27924 | 122.6944 | 0.07782 | 77.2476 | 121.5042 | 122.6715 | -122.905 | -122.9416
1377.9844 | 122.8592 | -81.7062 | 40.8691 | 0.027008 | 2.5564e-05 | 0.0070858 | -0.0012261 | -0.0030484 | -0.00093346 | -0.0021427 | -81.6696 | 40.8279 | -82.0129 | 40.9882 | 39.7339 | -4.0558 | -7.7087 | -5.8182 | 40.8691 | -82.0267 | -0.3067 | -0.041199 | 0.036621 | 122.6944 | -1.1353 | -0.32043 | 0 | 0.34332 | 73.9975 | 75.8881 | 121.4401 | 122.5342 | 0.036621 | 122.5754 | 77.6505 | -0.32043 | 122.5342 | 0.036621 | 77.6505 | 121.4401 | 122.5754 | -122.8821 | -122.8958
1378.9062 | 122.8455 | -81.958 | 40.6906 | -0.026398 | 0.004939 | 0.008154 | 0.0086005 | -0.0034756 | -0.0013609 | -0.0023563 | -81.8573 | 40.7455 | -82.1823 | 40.86 | 39.6423 | -4.1016 | -7.9239 | -6.0287 | 40.7181 | -82.3105 | -0.2243 | 0.054931 | 0.10071 | 122.818 | -1.0483 | -0.35248 | 0.027466 | 0.32501 | 74.0341 | 75.9293 | 121.6003 | 122.7036 | 0.10071 | 122.6761 | 77.8564 | -0.35248 | 122.7036 | 0.10071 | 77.8564 | 121.6003 | 122.6761 | -122.8729 | -123.0011
1379.9688 | 122.8088 | -81.189 | 41.4505 | -0.095062 | 0.0028028 | 0.0049496 | 0.0056097 | -0.002194 | -0.0020017 | -0.0036379 | -81.0928 | 41.5329 | -81.4087 | 41.5741 | 40.2924 | -3.9276 | -7.3471 | -5.5756 | 41.4688 | -81.5094 | -0.21973 | 0.082398 | 0.096131 | 122.7631 | -1.1581 | -0.32043 | 0.018311 | 0.31586 | 73.8419 | 75.6134 | 121.4813 | 122.7219 | 0.096131 | 122.6578 | 77.2614 | -0.32043 | 122.7219 | 0.096131 | 77.2614 | 121.4813 | 122.6578 | -122.8592 | -122.9599
1380.9062 | 122.7997 | -81.926 | 40.741 | -0.18662 | 0.0025892 | 0.0055906 | 0.0002691 | -0.0030484 | 0.00034814 | -0.0029971 | -81.8893 | 40.7364 | -82.2144 | 40.7776 | 39.624 | -3.8498 | -7.1045 | -5.5481 | 40.7776 | -82.2052 | -0.28839 | -0.004578 | 0.036621 | 122.7036 | -1.1169 | -0.27924 | 0.036621 | 0.32501 | 74.8215 | 76.3779 | 121.55 | 122.6624 | 0.036621 | 122.7036 | 78.0762 | -0.27924 | 122.6624 | 0.036621 | 78.0762 | 121.55 | 122.7036 | -122.9553 | -122.9462
1381.9531 | 122.9004 | -80.9875 | 41.6245 | 0.019379 | 0.00045296 | 0.003027 | -0.0018671 | -0.0024076 | -7.9062e-05 | -0.00086094 | -80.9647 | 41.5833 | -81.2485 | 41.7435 | 40.5075 | -3.8864 | -6.5918 | -5.0674 | 41.6016 | -81.2943 | -0.26093 | -0.041199 | 0.022888 | 122.731 | -1.1169 | -0.3067 | -0.022889 | 0.28381 | 74.3958 | 75.9201 | 121.4951 | 122.5708 | 0.022888 | 122.5891 | 77.1011 | -0.3067 | 122.5708 | 0.022888 | 77.1011 | 121.4951 | 122.5891 | -122.8729 | -122.9187
1382.9219 | 122.7493 | -80.6396 | 42.0456 | -0.22476 | 0.002162 | 0.0038816 | 0.0041143 | -0.0053982 | -0.0039243 | -0.0027835 | -80.6259 | 41.9403 | -80.9463 | 42.0547 | 40.7593 | -4.0237 | -6.2393 | -4.9622 | 42.0136 | -80.9463 | -0.3067 | -0.10528 | 0.013732 | 122.6944 | -1.2863 | -0.3067 | -0.032043 | 0.32043 | 74.4003 | 75.6775 | 121.3989 | 122.58 | 0.013732 | 122.6532 | 76.6159 | -0.3067 | 122.58 | 0.013732 | 76.6159 | 121.3989 | 122.6532 | -122.9919 | -122.9919
1383.9688 | 122.8546 | -80.6992 | 41.8991 | 0.11856 | 0.0010938 | 0.0034544 | 0.0009101 | -0.003903 | -0.00050626 | -0.0032107 | -80.6763 | 41.7938 | -81.0104 | 42.0136 | 40.7776 | -3.9276 | -6.5918 | -4.8706 | 41.9037 | -80.9692 | -0.31128 | -0.10529 | 0.022888 | 122.7127 | -1.1215 | -0.27008 | 0.004578 | 0.33417 | 74.1074 | 75.8286 | 121.4767 | 122.493 | 0.022888 | 122.6028 | 76.7715 | -0.27008 | 122.493 | 0.022888 | 76.7715 | 121.4767 | 122.6028 | -122.9095 | -122.8683
1384.9219 | 122.8043 | -81.2027 | 41.4459 | -0.049286 | 0.0051526 | 0.0068722 | 0.0086005 | -0.0041166 | -0.00050626 | -0.0036379 | -80.9647 | 41.5924 | -81.3492 | 41.5604 | 40.2878 | -4.0009 | -6.3858 | -4.4357 | 41.4551 | -81.5323 | -0.14648 | 0.14648 | 0.23804 | 122.7631 | -1.1581 | -0.32959 | 0.009155 | 0.38452 | 74.8169 | 76.767 | 121.4905 | 122.7951 | 0.23804 | 122.6578 | 77.2018 | -0.32959 | 122.7951 | 0.23804 | 77.2018 | 121.4905 | 122.6578 | -122.7951 | -122.9782
1385.9688 | 122.8821 | -80.6671 | 41.8945 | 0.18723 | 0.002162 | 0.0043088 | 0.0030463 | -0.0034756 | -0.00071986 | -0.0015017 | -80.5344 | 41.9083 | -80.9235 | 42.0227 | 40.7455 | -3.7582 | -6.5369 | -4.0512 | 41.8854 | -80.9738 | -0.25635 | 0.013733 | 0.13275 | 122.6898 | -1.149 | -0.3067 | -0.009155 | 0.3891 | 74.1302 | 76.6159 | 121.4127 | 122.5754 | 0.13275 | 122.5525 | 76.9089 | -0.3067 | 122.5754 | 0.13275 | 76.9089 | 121.4127 | 122.5525 | -122.818 | -122.8683
1386.9062 | 122.7814 | -80.6168 | 42.0227 | 0.072784 | 0.0079298 | 0.0079404 | 0.0086005 | -0.0030484 | -0.0015745 | -0.0017153 | -80.5573 | 41.9998 | -80.9143 | 42.1234 | 40.7867 | -3.923 | -6.102 | -4.5227 | 42.041 | -80.9555 | -0.29755 | -0.022888 | 0.059509 | 122.7402 | -1.236 | -0.33875 | 0.018311 | 0.35706 | 74.5148 | 76.0941 | 121.4035 | 122.6166 | 0.059509 | 122.6578 | 76.6937 | -0.33875 | 122.6166 | 0.059509 | 76.6937 | 121.4035 | 122.6578 | -122.937 | -122.9782
1387.9844 | 122.9141 | -80.5161 | 42.0547 | 0.20248 | 0.0028028 | 0.008154 | 0.0047553 | -0.0013394 | -0.00050626 | -0.0040653 | -80.4382 | 42.0181 | -80.8182 | 42.1738 | 40.8829 | -3.8589 | -6.2073 | -4.2023 | 42.0456 | -80.8502 | -0.30212 | -0.036622 | 0.07782 | 122.6898 | -1.1719 | -0.33417 | -0.009156 | 0.37994 | 74.3088 | 76.3138 | 121.3989 | 122.5342 | 0.07782 | 122.5616 | 76.6571 | -0.33417 | 122.5342 | 0.07782 | 76.6571 | 121.3989 | 122.5616 | -122.8729 | -122.905
1388.9062 | 122.9233 | -80.8273 | 41.7435 | -0.12558 | -0.00061524 | 0.003027 | -0.0010125 | -0.00668 | -0.0013609 | -0.0038515 | -80.7495 | 41.7068 | -81.1386 | 41.9037 | 40.6815 | -3.9505 | -6.3492 | -4.1748 | 41.7389 | -81.1478 | -0.31128 | -0.036621 | 0.07782 | 122.731 | -1.062 | -0.32043 | -0.004577 | 0.3891 | 74.4781 | 76.6525 | 121.5088 | 122.5342 | 0.07782 | 122.5662 | 76.8768 | -0.32043 | 122.5342 | 0.07782 | 76.8768 | 121.5088 | 122.5662 | -122.8821 | -122.8912
1389.9688 | 122.8638 | -80.7495 | 41.8488 | -0.049286 | 0.002162 | 0.0015316 | -0.0012261 | -0.0064664 | -0.00050626 | -0.0023563 | -80.7999 | 41.716 | -81.1203 | 42.0227 | 40.7959 | -3.9551 | -6.8893 | -4.5639 | 41.8579 | -81.0196 | -0.37079 | -0.13275 | -0.050354 | 122.7722 | -1.0529 | -0.27008 | 0.009155 | 0.32043 | 73.8602 | 76.1856 | 121.5454 | 122.4655 | -0.050354 | 122.6074 | 76.7944 | -0.27008 | 122.4655 | -0.050354 | 76.7944 | 121.5454 | 122.6074 | -122.9691 | -122.8683
1390.9062 | 122.8043 | -81.7703 | 40.8829 | -0.22476 | 0.00045296 | 0.0023862 | 0.0062507 | -0.0058256 | -0.0011471 | -0.0051333 | -81.7657 | 40.7501 | -82.1182 | 40.9653 | 39.7385 | -4.3396 | -7.3517 | -5.159 | 40.8463 | -82.1045 | -0.3479 | -0.13275 | 0.004578 | 122.7356 | -1.1444 | -0.33417 | -0.036622 | 0.35248 | 74.4186 | 76.6113 | 121.5088 | 122.5204 | 0.004578 | 122.6166 | 77.4307 | -0.33417 | 122.5204 | 0.004578 | 77.4307 | 121.5088 | 122.6166 | -123.0011 | -122.9874
1391.9062 | 122.8912 | -81.6925 | 40.8737 | 0.4924 | 0.0023756 | 0.0028134 | 0.0021917 | -0.0053982 | -0.0028561 | -0.0023563 | -81.6605 | 40.7684 | -82.045 | 41.0568 | 39.9857 | -4.2023 | -7.3196 | -5.2917 | 40.8646 | -82.0038 | -0.35248 | -0.10528 | 0.032044 | 122.7493 | -0.88806 | -0.31128 | -0.009155 | 0.38452 | 74.3729 | 76.4008 | 121.6782 | 122.4609 | 0.032044 | 122.5571 | 77.4902 | -0.31128 | 122.4609 | 0.032044 | 77.4902 | 121.6782 | 122.5571 | -122.9187 | -122.8775
1392.9531 | 122.8317 | -81.0333 | 41.5466 | 0.027008 | 0.0019482 | 0.0017454 | 0.0009101 | -0.0077482 | -0.00093346 | -0.0040653 | -81.1066 | 41.4139 | -81.4087 | 41.6748 | 40.5121 | -4.2801 | -7.0496 | -5.0354 | 41.5466 | -81.3309 | -0.37537 | -0.13275 | -0.073242 | 122.7081 | -1.0345 | -0.29755 | 0 | 0.30212 | 73.9838 | 75.9979 | 121.5454 | 122.4472 | -0.073242 | 122.58 | 76.7532 | -0.29755 | 122.4472 | -0.073242 | 76.7532 | 121.5454 | 122.58 | -122.9553 | -122.8775
1393.9062 | 122.8958 | -81.9489 | 40.6219 | -0.041657 | 0.0034436 | 0.0021726 | 0.0006965 | -0.0062528 | -0.00071986 | -0.0040653 | -81.9717 | 40.4663 | -82.3425 | 40.8234 | 39.6103 | -4.3854 | -7.5211 | -5.3101 | 40.6174 | -82.2601 | -0.39368 | -0.15564 | -0.022888 | 122.7722 | -1.0117 | -0.31128 | -0.004577 | 0.37079 | 74.4278 | 76.6388 | 121.5591 | 122.4152 | -0.022888 | 122.5662 | 77.5635 | -0.31128 | 122.4152 | -0.022888 | 77.5635 | 121.5591 | 122.5662 | -122.9645 | -122.8821
1394.9688 | 122.905 | -81.0471 | 41.5604 | -0.041657 | 0.00045296 | 0.0025998 | 0.0028327 | -0.0064664 | -0.0020017 | -0.0049197 | -81.0059 | 41.4688 | -81.3492 | 41.6931 | 40.5075 | -4.2984 | -7.3013 | -5.1407 | 41.5192 | -81.3492 | -0.30212 | -0.091553 | 0.041199 | 122.7402 | -1.0529 | -0.30212 | -0.041199 | 0.34332 | 73.7457 | 75.9064 | 121.5546 | 122.5159 | 0.041199 | 122.5662 | 76.7487 | -0.30212 | 122.5159 | 0.041199 | 76.7487 | 121.5546 | 122.5662 | -122.9095 | -122.9095
1395.9062 | 122.8592 | -81.0013 | 41.5924 | -0.17899 | 0.0013074 | 0.003027 | 0.0053961 | -0.0068936 | -0.00050626 | -0.0034243 | -80.8731 | 41.5558 | -81.2576 | 41.8121 | 40.6036 | -4.2938 | -7.5348 | -5.2231 | 41.5833 | -81.3034 | -0.25635 | -0.036621 | 0.12817 | 122.8134 | -0.98877 | -0.30212 | -0.009155 | 0.38452 | 73.4665 | 75.7782 | 121.6049 | 122.5571 | 0.12817 | 122.5845 | 76.7075 | -0.30212 | 122.5571 | 0.12817 | 76.7075 | 121.6049 | 122.5845 | -122.85 | -122.8958
1396.9531 | 122.8912 | -81.0379 | 41.5054 | -0.049286 | 2.5564e-05 | 0.00046358 | 0.0013373 | -0.0086026 | 0.00034814 | -0.0036379 | -81.189 | 41.2811 | -81.5002 | 41.6931 | 40.4846 | -4.3533 | -7.6126 | -5.1407 | 41.478 | -81.4087 | -0.46234 | -0.2243 | -0.15106 | 122.731 | -1.0208 | -0.37079 | -0.027466 | 0.31128 | 73.4253 | 75.8972 | 121.5225 | 122.319 | -0.15106 | 122.5159 | 76.6846 | -0.37079 | 122.319 | -0.15106 | 76.6846 | 121.5225 | 122.5159 | -123.0057 | -122.9141
1397.9219 | 122.8043 | -80.278 | 42.3752 | -0.2095 | 0.0036572 | 0.0032406 | 0.0086005 | -0.0041166 | -0.0011471 | -0.0038515 | -80.2094 | 42.4255 | -80.5344 | 42.4576 | 41.2216 | -4.2023 | -6.665 | -4.9942 | 42.3706 | -80.5984 | -0.25635 | 0.050354 | 0.068664 | 122.7356 | -1.1536 | -0.32044 | -0.004578 | 0.32501 | 73.613 | 75.2838 | 121.4996 | 122.7036 | 0.068664 | 122.6486 | 76.0757 | -0.32044 | 122.7036 | 0.068664 | 76.0757 | 121.4996 | 122.6486 | -122.9095 | -122.9736
1398.9688 | 122.8043 | -80.1178 | 42.4942 | -0.072174 | 0.0051526 | 0.0068722 | 0.010737 | -0.0034756 | 0.00098914 | -0.0038515 | -80.0537 | 42.5034 | -80.4291 | 42.6178 | 41.3864 | -4.1885 | -7.0999 | -5.1041 | 42.4805 | -80.4703 | -0.31128 | 0.009155 | 0.064087 | 122.7356 | -1.1078 | -0.35248 | -0.013733 | 0.37537 | 73.0179 | 75.0137 | 121.5042 | 122.6212 | 0.064087 | 122.5983 | 75.9293 | -0.35248 | 122.6212 | 0.064087 | 75.9293 | 121.5042 | 122.5983 | -122.9233 | -122.9645
1399.9062 | 122.9187 | -80.1132 | 42.453 | -0.072174 | 0.00045296 | 0.0023862 | -0.0005853 | -0.003903 | -0.00071986 | -0.0040653 | -80.0949 | 42.3706 | -80.4565 | 42.6407 | 41.4185 | -4.0054 | -7.0496 | -4.8065 | 42.4301 | -80.4337 | -0.34332 | -0.082398 | 0.01831 | 122.7539 | -1.0345 | -0.32044 | -0.022888 | 0.36163 | 73.0637 | 75.3067 | 121.5317 | 122.4838 | 0.01831 | 122.5433 | 76.1078 | -0.32044 | 122.4838 | 0.01831 | 76.1078 | 121.5317 | 122.5433 | -122.9095 | -122.8867
1400.9688 | 122.8912 | -81.3263 | 41.217 | 0.18723 | 0.0040846 | 0.0049496 | 0.0039007 | -0.0047574 | 0.00098914 | -0.0034243 | -81.1752 | 41.2399 | -81.5826 | 41.4413 | 40.2191 | -4.1931 | -7.132 | -4.9118 | 41.2308 | -81.6376 | -0.25635 | 0.022888 | 0.15106 | 122.7676 | -0.99793 | -0.31128 | 0.013733 | 0.40741 | 74.1943 | 76.4145 | 121.5454 | 122.5662 | 0.15106 | 122.5571 | 77.1332 | -0.31128 | 122.5662 | 0.15106 | 77.1332 | 121.5454 | 122.5571 | -122.7997 | -122.8546
1401.9219 | 122.7905 | -80.3467 | 42.3157 | -0.21713 | 0.0045118 | 0.0028134 | 0.0066779 | -0.0060392 | -0.00050626 | -0.0023563 | -80.3329 | 42.2653 | -80.6442 | 42.3981 | 41.1346 | -3.9917 | -6.7245 | -4.9667 | 42.2791 | -80.6717 | -0.29755 | -0.050354 | 0.013733 | 122.7448 | -1.181 | -0.32501 | -0.036621 | 0.31128 | 73.6221 | 75.3799 | 121.4813 | 122.612 | 0.013733 | 122.6257 | 76.355 | -0.32501 | 122.612 | 0.013733 | 76.355 | 121.4813 | 122.6257 | -122.9599 | -122.9874
1402.9688 | 122.8546 | -80.5939 | 42.009 | -0.1561 | 0.001521 | 0.0038816 | 0.0034735 | -0.0047574 | -0.00071986 | -0.0059879 | -80.5115 | 41.9312 | -80.8823 | 42.215 | 40.9424 | -3.7308 | -7.0633 | -4.8889 | 42.0227 | -80.8914 | -0.28839 | -0.07782 | 0.082397 | 122.8088 | -1.0666 | -0.29755 | 0.013733 | 0.37079 | 73.5306 | 75.705 | 121.5363 | 122.525 | 0.082397 | 122.6166 | 76.8631 | -0.29755 | 122.525 | 0.082397 | 76.8631 | 121.5363 | 122.6166 | -122.8912 | -122.9004
1403.9062 | 122.8683 | -80.452 | 42.1463 | -0.018768 | 0.0013074 | -0.00081822 | 0.0017645 | -0.0056118 | -0.0011471 | -0.0034243 | -80.4611 | 42.0639 | -80.7449 | 42.2974 | 41.0522 | -3.978 | -6.9901 | -4.8706 | 42.1326 | -80.7404 | -0.29297 | -0.082397 | -0.009156 | 122.7493 | -1.0941 | -0.28839 | -0.013733 | 0.28381 | 73.4619 | 75.5814 | 121.5042 | 122.5159 | -0.009156 | 122.5845 | 76.474 | -0.28839 | 122.5159 | -0.009156 | 76.474 | 121.5042 | 122.5845 | -122.8912 | -122.8867
1404.9688 | 122.7997 | -81.2943 | 41.3818 | -0.19424 | 0.00088016 | 0.003027 | 0.0051825 | -0.0068936 | -0.0015745 | -0.0040653 | -81.2485 | 41.2537 | -81.6147 | 41.4597 | 40.274 | -4.0466 | -7.196 | -4.985 | 41.3315 | -81.5826 | -0.32043 | -0.12817 | 0.045776 | 122.7539 | -1.1078 | -0.28839 | -0.050354 | 0.36621 | 74.0982 | 76.3092 | 121.5683 | 122.5479 | 0.045776 | 122.6257 | 77.2476 | -0.28839 | 122.5479 | 0.045776 | 77.2476 | 121.5683 | 122.6257 | -122.9965 | -122.9645
1405.9062 | 122.8546 | -81.6238 | 40.9744 | 0.13382 | 0.0017346 | 0.0017454 | 0.0034735 | -0.0041166 | -0.0015745 | -0.0019289 | -81.6101 | 40.9012 | -81.9168 | 41.0797 | 39.8895 | -4.0558 | -7.37 | -5.2231 | 40.9149 | -81.9305 | -0.29297 | -0.073242 | 0.013733 | 122.7036 | -1.0849 | -0.3067 | -0.059509 | 0.3067 | 74.2538 | 76.4008 | 121.5134 | 122.525 | 0.013733 | 122.5388 | 77.5681 | -0.3067 | 122.525 | 0.013733 | 77.5681 | 121.5134 | 122.5388 | -122.8912 | -122.905
1406.9688 | 122.9004 | -80.7312 | 41.8259 | 0.18723 | 0.0025892 | 0.003668 | 0.0068915 | -0.0045438 | -0.0017881 | -0.0023563 | -80.7312 | 41.6885 | -81.102 | 42.0731 | 40.9286 | -3.7628 | -7.3059 | -5.1224 | 41.7709 | -81.0287 | -0.37079 | -0.13733 | 0 | 122.8043 | -0.89722 | -0.29755 | -0.054932 | 0.37079 | 73.4253 | 75.6088 | 121.6599 | 122.4197 | 0 | 122.5021 | 76.9684 | -0.29755 | 122.4197 | 0 | 76.9684 | 121.6599 | 122.5021 | -122.9279 | -122.8546
1407.9219 | 122.8088 | -80.6534 | 42.0181 | 0.034637 | 0.0064344 | 0.0079404 | 0.010523 | -0.003262 | -7.9062e-05 | -0.0019289 | -80.5389 | 42.0456 | -80.9006 | 42.0776 | 40.8051 | -3.9825 | -7.0267 | -5.2094 | 41.9907 | -80.9692 | -0.24719 | 0.027466 | 0.11444 | 122.731 | -1.2131 | -0.31586 | -0.027465 | 0.36163 | 73.6267 | 75.444 | 121.4584 | 122.699 | 0.11444 | 122.644 | 76.6708 | -0.31586 | 122.699 | 0.11444 | 76.6708 | 121.4584 | 122.644 | -122.9187 | -122.9874
1408.9688 | 122.9233 | -80.5115 | 42.0639 | -0.20187 | 0.0013074 | -0.00017722 | 0.0002691 | -0.0026212 | -0.0015745 | -0.0051333 | -80.4016 | 42.0456 | -80.7953 | 42.2882 | 41.0614 | -3.9047 | -7.132 | -4.985 | 42.0547 | -80.809 | -0.28381 | -0.018311 | 0.10986 | 122.7997 | -1.0025 | -0.29755 | -0.009155 | 0.39368 | 73.3795 | 75.5264 | 121.5729 | 122.5571 | 0.10986 | 122.5662 | 76.6068 | -0.29755 | 122.5571 | 0.10986 | 76.6068 | 121.5729 | 122.5662 | -122.8592 | -122.8729
1409.9062 | 122.8592 | -80.4016 | 42.1829 | -0.034027 | 0.0019482 | 0.0043088 | 0.0013373 | -0.0077482 | -0.0020017 | -0.0025699 | -80.3604 | 42.1738 | -80.69 | 42.3523 | 41.1392 | -4.01 | -7.5394 | -5.2643 | 42.2104 | -80.6717 | -0.28839 | -0.009155 | 0.041198 | 122.7539 | -1.0437 | -0.27008 | 0.027466 | 0.32959 | 72.8622 | 75.1373 | 121.5408 | 122.5754 | 0.041198 | 122.612 | 76.3916 | -0.27008 | 122.5754 | 0.041198 | 76.3916 | 121.5408 | 122.612 | -122.8729 | -122.8546
1410.9688 | 122.8821 | -79.5456 | 43.0573 | -0.1561 | 0.0030164 | 0.0032406 | -0.0010125 | -0.0081754 | 0.0029117 | -0.0023563 | -79.3808 | 43.1259 | -79.7287 | 43.1305 | 42.0822 | -3.9597 | -7.2052 | -5.1086 | 43.0344 | -79.8431 | -0.18311 | 0.068665 | 0.16479 | 122.6761 | -0.97504 | -0.29755 | -0.022888 | 0.3479 | 72.3404 | 74.4369 | 121.6278 | 122.6715 | 0.16479 | 122.58 | 75.5859 | -0.29755 | 122.6715 | 0.16479 | 75.5859 | 121.6278 | 122.58 | -122.786 | -122.9004
1411.9062 | 122.8775 | -79.8203 | 42.8009 | 0.065155 | 0.0034436 | 0.00024998 | 0.0019781 | -0.0043302 | 0.00034814 | -0.0029971 | -79.7836 | 42.7368 | -80.0903 | 42.9382 | 41.6473 | -4.1794 | -7.4478 | -5.3879 | 42.7597 | -80.127 | -0.27008 | -0.064087 | 0.036621 | 122.7585 | -1.1536 | -0.3067 | -0.041198 | 0.3067 | 72.3724 | 74.4324 | 121.4676 | 122.5571 | 0.036621 | 122.58 | 75.6409 | -0.3067 | 122.5571 | 0.036621 | 75.6409 | 121.4676 | 122.58 | -122.8912 | -122.9279
1412.9844 | 122.8912 | -78.8864 | 43.6935 | -0.19424 | -0.00061524 | 0.0011044 | 0.0017645 | -0.0068936 | -0.0017881 | -0.0015017 | -78.7582 | 43.634 | -79.1885 | 44.0872 | 42.7231 | -3.7399 | -7.4753 | -5.0262 | 43.6295 | -79.2297 | -0.30212 | -0.059509 | 0.12817 | 122.9736 | -0.97046 | -0.34332 | -0.064086 | 0.4303 | 71.4111 | 73.8602 | 121.6095 | 122.5204 | 0.12817 | 122.5159 | 75.1465 | -0.34332 | 122.5204 | 0.12817 | 75.1465 | 121.6095 | 122.5159 | -122.8821 | -122.9233
1413.9062 | 122.8455 | -78.8132 | 43.8034 | 0.088043 | -0.002965 | 0.0011044 | -0.0005853 | -0.0071072 | -0.00071986 | -0.0036379 | -78.7628 | 43.6707 | -79.1565 | 43.9407 | 42.6407 | -3.7216 | -7.1594 | -5.3467 | 43.7485 | -79.1061 | -0.34332 | -0.13275 | 0.050354 | 122.7539 | -1.1627 | -0.29297 | -0.054932 | 0.39368 | 71.6537 | 73.4665 | 121.4539 | 122.4838 | 0.050354 | 122.5616 | 75.0916 | -0.29297 | 122.4838 | 0.050354 | 75.0916 | 121.4539 | 122.5616 | -122.9599 | -122.9095
1414.9688 | 122.8683 | -79.3854 | 43.1763 | 0.15671 | 0.0010938 | 0.0066586 | 0.0028327 | -0.0079618 | -0.0017881 | -0.0053469 | -79.3991 | 43.0389 | -79.7791 | 43.3456 | 42.0868 | -3.3783 | -7.1045 | -5.4199 | 43.1305 | -79.7195 | -0.39368 | -0.13733 | -0.013733 | 122.731 | -1.0895 | -0.33417 | -0.045777 | 0.37994 | 72.2809 | 73.9655 | 121.4722 | 122.4243 | -0.013733 | 122.5159 | 76.0071 | -0.33417 | 122.4243 | -0.013733 | 76.0071 | 121.4722 | 122.5159 | -122.9553 | -122.8958
1415.9062 | 122.9095 | -79.5135 | 43.0481 | 0.049896 | 0.001521 | 0.003668 | 0.0013373 | -0.0064664 | 0.00013454 | -0.0040653 | -79.4861 | 43.0161 | -79.8248 | 43.2129 | 41.9907 | -3.511 | -7.4112 | -5.9555 | 43.0527 | -79.8065 | -0.31128 | -0.032044 | 0.027466 | 122.7264 | -1.0574 | -0.29297 | 0.004577 | 0.33874 | 72.1024 | 73.558 | 121.5042 | 122.5296 | 0.027466 | 122.5662 | 76.0025 | -0.29297 | 122.5296 | 0.027466 | 76.0025 | 121.5042 | 122.5662 | -122.8729 | -122.8546
1416.9844 | 122.905 | -79.3488 | 43.2175 | -0.034027 | 0.001521 | 0.0023862 | 0.0024053 | -0.0058256 | 0.00013454 | -0.0040653 | -79.2664 | 43.2266 | -79.6143 | 43.4509 | 42.1646 | -3.5019 | -7.3242 | -5.896 | 43.2129 | -79.6783 | -0.2655 | 0.009156 | 0.082398 | 122.7997 | -1.0529 | -0.32959 | -0.004577 | 0.3479 | 72.0245 | 73.4528 | 121.5134 | 122.5754 | 0.082398 | 122.5616 | 75.8469 | -0.32959 | 122.5754 | 0.082398 | 75.8469 | 121.5134 | 122.5616 | -122.8317 | -122.8958
1417.9062 | 122.8683 | -79.4815 | 43.071 | 0.16434 | 0.002162 | 0.0015316 | 0.0041143 | -0.003903 | -0.00071986 | -0.0010745 | -79.4128 | 43.0481 | -79.7424 | 43.2999 | 42.0547 | -3.7033 | -7.6172 | -6.1157 | 43.0573 | -79.8248 | -0.26093 | -0.022888 | 0.068664 | 122.7814 | -1.0162 | -0.34332 | -0.013733 | 0.32959 | 71.8643 | 73.3658 | 121.5363 | 122.5296 | 0.068664 | 122.5388 | 75.7782 | -0.34332 | 122.5296 | 0.068664 | 75.7782 | 121.5363 | 122.5388 | -122.8134 | -122.8958
1418.9688 | 122.7722 | -79.2389 | 43.396 | 0.019379 | 0.0036572 | 0.0072996 | 0.0092413 | -0.00668 | -0.0026425 | -0.0038515 | -79.2618 | 43.2816 | -79.628 | 43.4738 | 42.2333 | -3.6026 | -7.0312 | -5.4886 | 43.396 | -79.5273 | -0.3891 | -0.11444 | -0.022888 | 122.7127 | -1.1627 | -0.28839 | 0 | 0.36621 | 72.2076 | 73.7503 | 121.4722 | 122.5204 | -0.022888 | 122.6349 | 75.6363 | -0.28839 | 122.5204 | -0.022888 | 75.6363 | 121.4722 | 122.6349 | -123.024 | -122.9233
1419.9219 | 122.7814 | -79.7791 | 42.8604 | -0.27817 | 0.0017346 | 0.004736 | 0.0036871 | -0.0030484 | 0.00034814 | -0.0036379 | -79.715 | 42.8146 | -80.072 | 42.9611 | 41.6336 | -3.7125 | -7.2968 | -5.5939 | 42.8696 | -80.0903 | -0.29297 | -0.045777 | 0.064087 | 122.7402 | -1.2268 | -0.31128 | 0.009155 | 0.35706 | 72.4823 | 74.1852 | 121.4127 | 122.5937 | 0.064087 | 122.6486 | 76.0666 | -0.31128 | 122.5937 | 0.064087 | 76.0666 | 121.4127 | 122.6486 | -122.9324 | -122.9507
1420.9531 | 122.8043 | -80.3284 | 42.3248 | 0.13382 | 0.0025892 | 0.0055906 | 0.0071051 | -0.0017666 | -0.0022153 | -0.0036379 | -80.3421 | 42.2287 | -80.6488 | 42.3431 | 41.1758 | -3.9505 | -7.9193 | -6.3675 | 42.2836 | -80.6442 | -0.32044 | -0.09613 | -0.013733 | 122.6715 | -1.149 | -0.31586 | -0.041199 | 0.3067 | 72.4091 | 73.9609 | 121.5042 | 122.5571 | -0.013733 | 122.612 | 76.3779 | -0.31586 | 122.5571 | -0.013733 | 76.3779 | 121.5042 | 122.612 | -122.9736 | -122.9691
1421.9062 | 122.8912 | -80.0629 | 42.5262 | 0.16434 | 0.0010938 | 0.0034544 | -0.0003717 | -0.0030484 | -0.0022153 | -0.0034243 | -80.0446 | 42.4667 | -80.3741 | 42.6086 | 41.4551 | -3.653 | -7.4844 | -6.0196 | 42.4942 | -80.3879 | -0.31128 | -0.059509 | 0.01831 | 122.6715 | -1.0712 | -0.32501 | -0.032043 | 0.32959 | 72.5784 | 74.0433 | 121.5179 | 122.5296 | 0.01831 | 122.5571 | 76.4099 | -0.32501 | 122.5296 | 0.01831 | 76.4099 | 121.5179 | 122.5571 | -122.9004 | -122.9141
1422.9688 | 122.8821 | -80.3787 | 42.2516 | 0.011749 | 0.00323 | 0.003668 | 0.0009101 | -0.0062528 | 0.0014163 | -0.0032107 | -80.3329 | 42.1921 | -80.6808 | 42.366 | 41.2308 | -3.3005 | -7.3288 | -5.6396 | 42.1692 | -80.7083 | -0.30212 | -0.059509 | 0.045776 | 122.7448 | -1.0208 | -0.32959 | -0.082398 | 0.3479 | 73.0499 | 74.7391 | 121.6095 | 122.5708 | 0.045776 | 122.5479 | 77.0782 | -0.32959 | 122.5708 | 0.045776 | 77.0782 | 121.6095 | 122.5479 | -122.9324 | -122.9599
1423.9062 | 122.9095 | -80.3513 | 42.215 | 0.32455 | 0.00023916 | 0.0060178 | 0.0068915 | -0.0056118 | -0.0024289 | -0.0040653 | -80.2872 | 42.1371 | -80.6625 | 42.3843 | 41.2079 | -3.5156 | -7.4158 | -5.7816 | 42.2058 | -80.6168 | -0.31128 | -0.07782 | 0.064087 | 122.7356 | -1.0071 | -0.2655 | -0.009155 | 0.37537 | 72.9355 | 74.5697 | 121.5591 | 122.4884 | 0.064087 | 122.5571 | 76.8356 | -0.2655 | 122.4884 | 0.064087 | 76.8356 | 121.5591 | 122.5571 | -122.8775 | -122.8317
1424.9688 | 122.8088 | -79.8386 | 42.7917 | 0.16434 | 0.0025892 | 0.003027 | 0.0077459 | -0.00668 | -0.0017881 | -0.0027835 | -80.0629 | 42.4667 | -80.4108 | 42.8604 | 41.5512 | -3.7216 | -7.2739 | -5.6671 | 42.6819 | -80.1956 | -0.57221 | -0.32501 | -0.2243 | 122.699 | -1.2405 | -0.35706 | -0.10986 | 0.3479 | 72.5647 | 74.1714 | 121.3898 | 122.3053 | -0.2243 | 122.5204 | 76.1169 | -0.35706 | 122.3053 | -0.2243 | 76.1169 | 121.3898 | 122.5204 | -123.2025 | -122.9874
1425.9062 | 122.8775 | -79.5135 | 43.0252 | 0.21011 | 0.002162 | 0.0045224 | 0.0039007 | -0.0026212 | -0.0015745 | -0.0023563 | -79.5227 | 42.9337 | -79.8477 | 43.2495 | 41.9998 | -3.5568 | -7.37 | -5.4977 | 43.0252 | -79.8294 | -0.33417 | -0.091553 | -0.009155 | 122.7631 | -1.0254 | -0.31586 | 0 | 0.32501 | 72.1436 | 74.0158 | 121.5134 | 122.4472 | -0.009155 | 122.5388 | 75.9567 | -0.31586 | 122.4472 | -0.009155 | 75.9567 | 121.5134 | 122.5388 | -122.8729 | -122.8546
1426.9688 | 122.8271 | -80.6992 | 41.9083 | -0.14084 | 0.0028028 | 0.004736 | 0.0088141 | -0.003903 | -0.0041379 | -0.0021427 | -80.6168 | 41.8579 | -80.9967 | 42.0914 | 40.8005 | -3.8361 | -7.869 | -6.1249 | 41.9266 | -81.0379 | -0.29755 | -0.050354 | 0.082398 | 122.7905 | -1.1078 | -0.33875 | 0.018311 | 0.37994 | 72.8302 | 74.5743 | 121.4996 | 122.5571 | 0.082398 | 122.6257 | 76.8631 | -0.33875 | 122.5571 | 0.082398 | 76.8631 | 121.4996 | 122.6257 | -122.905 | -122.9462
1427.9062 | 122.8546 | -80.2643 | 42.3294 | 0.15671 | 0.0034436 | 0.0066586 | 0.0024053 | -0.0024076 | -0.0013609 | -0.0017153 | -80.2094 | 42.2333 | -80.571 | 42.4759 | 41.217 | -3.7354 | -7.8232 | -6.1707 | 42.2974 | -80.5756 | -0.3067 | -0.096131 | 0.054931 | 122.7402 | -1.1124 | -0.31128 | -0.032044 | 0.36163 | 72.4411 | 74.0936 | 121.4813 | 122.4976 | 0.054931 | 122.5616 | 76.5289 | -0.31128 | 122.4976 | 0.054931 | 76.5289 | 121.4813 | 122.5616 | -122.9004 | -122.905
1428.9688 | 122.8546 | -80.9692 | 41.6656 | -0.17899 | 0.00066656 | 0.003668 | 0.0030463 | -0.0053982 | -0.0020017 | -0.0036379 | -80.8182 | 41.6794 | -81.1707 | 41.8716 | 40.6219 | -4.0558 | -8.2031 | -6.6422 | 41.7023 | -81.2302 | -0.20142 | 0.013733 | 0.15106 | 122.8409 | -1.0437 | -0.26093 | 0.036622 | 0.35248 | 72.7661 | 74.3271 | 121.5912 | 122.6486 | 0.15106 | 122.6715 | 76.9135 | -0.26093 | 122.6486 | 0.15106 | 76.9135 | 121.5912 | 122.6715 | -122.8363 | -122.8958
1429.9062 | 122.8409 | -81.2256 | 41.4322 | 0.18723 | 0.0045118 | 0.009863 | 0.0081733 | -0.0017666 | -0.00050626 | -0.0015017 | -81.1386 | 41.4413 | -81.4819 | 41.5054 | 40.2283 | -4.097 | -8.3908 | -6.9214 | 41.4001 | -81.5552 | -0.25635 | 0.009155 | 0.086975 | 122.731 | -1.2039 | -0.32959 | -0.032044 | 0.34332 | 72.8348 | 74.3042 | 121.4539 | 122.6669 | 0.086975 | 122.6257 | 77.1286 | -0.32959 | 122.6669 | 0.086975 | 77.1286 | 121.4539 | 122.6257 | -122.9141 | -122.9874
1430.9688 | 122.8043 | -80.2505 | 42.3798 | -0.018768 | 0.0040846 | 0.0090086 | 0.0079595 | -0.002194 | -0.0011471 | -0.0034243 | -80.2094 | 42.3065 | -80.5893 | 42.485 | 41.2445 | -3.8773 | -7.7454 | -6.4453 | 42.4164 | -80.5389 | -0.33874 | -0.073242 | 0.041198 | 122.7356 | -1.1353 | -0.28839 | 0.036621 | 0.37994 | 72.5052 | 73.8052 | 121.4951 | 122.5571 | 0.041198 | 122.6669 | 76.3733 | -0.28839 | 122.5571 | 0.041198 | 76.3733 | 121.4951 | 122.6669 | -122.9691 | -122.9187
1431.9219 | 122.9095 | -79.6738 | 42.9016 | -0.17136 | 0.001521 | 0.0045224 | -0.0018671 | 0.0014376 | -0.0015745 | -0.0012881 | -79.7745 | 42.6956 | -80.1498 | 43.1625 | 42.0364 | -3.8132 | -7.782 | -6.221 | 42.9474 | -79.9484 | -0.47607 | -0.20599 | -0.10071 | 122.8363 | -0.86517 | -0.27466 | 0.045777 | 0.37537 | 71.8918 | 73.4528 | 121.7102 | 122.3694 | -0.10071 | 122.6212 | 75.8606 | -0.27466 | 122.3694 | -0.10071 | 75.8606 | 121.7102 | 122.6212 | -123.0515 | -122.85
1432.9688 | 122.8592 | -79.184 | 43.4647 | 0.19485 | 0.0060072 | 0.001318 | 0.0077459 | -0.003262 | -0.0020017 | -0.0025699 | -79.1885 | 43.3365 | -79.5364 | 43.5471 | 42.3431 | -3.9322 | -7.8232 | -6.8298 | 43.4418 | -79.4907 | -0.35248 | -0.12817 | -0.004578 | 122.731 | -1.1215 | -0.3067 | -0.022889 | 0.3479 | 71.3608 | 72.3541 | 121.5271 | 122.5204 | -0.004578 | 122.6257 | 75.2518 | -0.3067 | 122.5204 | -0.004578 | 75.2518 | 121.5271 | 122.6257 | -123.0011 | -122.9553
1433.9062 | 122.8775 | -78.9688 | 43.602 | 0.233 | 0.0028028 | 0.003668 | 0.0064643 | -0.002194 | -7.9062e-05 | -0.0036379 | -78.9459 | 43.634 | -79.2664 | 43.7119 | 42.4896 | -3.6072 | -7.5531 | -6.5598 | 43.5654 | -79.3213 | -0.29755 | 0.032043 | 0.022888 | 122.6807 | -1.1124 | -0.35248 | -0.036621 | 0.32043 | 71.4157 | 72.4091 | 121.4584 | 122.6028 | 0.022888 | 122.5342 | 75.3616 | -0.35248 | 122.6028 | 0.022888 | 75.3616 | 121.4584 | 122.5342 | -122.8683 | -122.9233
1434.9688 | 122.7722 | -79.7562 | 42.9108 | 0.0041197 | 0.0028028 | 0.0083676 | 0.0068915 | -0.0013394 | -0.0052061 | -0.0040653 | -79.6921 | 42.9062 | -80.04 | 42.9703 | 41.7023 | -3.7811 | -7.5897 | -6.4178 | 42.8696 | -80.0583 | -0.28381 | -0.004578 | 0.064087 | 122.7264 | -1.2085 | -0.30212 | -0.041199 | 0.3479 | 72.1664 | 73.3383 | 121.4584 | 122.6624 | 0.064087 | 122.6257 | 75.975 | -0.30212 | 122.6624 | 0.064087 | 75.975 | 121.4584 | 122.6257 | -122.9507 | -122.9691
1435.9219 | 122.8912 | -79.8798 | 42.7185 | -0.30106 | 0.00088016 | 0.0043088 | -0.0007989 | -0.0043302 | -0.0020017 | -0.00086094 | -79.8431 | 42.627 | -80.2094 | 42.8833 | 41.6153 | -3.717 | -8.1619 | -6.6055 | 42.7139 | -80.1956 | -0.32959 | -0.091553 | 0.036621 | 122.7631 | -1.1032 | -0.31586 | -0.004578 | 0.36621 | 71.7178 | 73.2742 | 121.4951 | 122.5067 | 0.036621 | 122.5937 | 76.1627 | -0.31586 | 122.5067 | 0.036621 | 76.1627 | 121.4951 | 122.5937 | -122.9279 | -122.9141
1436.9688 | 122.7676 | -79.0695 | 43.5791 | 0.072784 | 0.0055798 | 0.0028134 | 0.0096685 | -0.0024076 | -0.00093346 | -0.0049197 | -79.0237 | 43.5059 | -79.4083 | 43.6203 | 42.2791 | -3.6484 | -7.7866 | -6.6513 | 43.5608 | -79.3991 | -0.33875 | -0.073243 | 0.045776 | 122.6898 | -1.3 | -0.32959 | -0.018311 | 0.38452 | 71.283 | 72.4182 | 121.3486 | 122.5754 | 0.045776 | 122.6303 | 75.4211 | -0.32959 | 122.5754 | 0.045776 | 75.4211 | 121.3486 | 122.6303 | -122.9874 | -122.9782
1437.9062 | 122.8912 | -79.7974 | 42.7826 | 0.14145 | 0.00323 | 0.0058042 | 0.0043281 | -0.00069859 | -0.0020017 | -0.0036379 | -79.7699 | 42.6956 | -80.1498 | 42.9153 | 41.6931 | -3.9642 | -8.4549 | -6.9901 | 42.7322 | -80.1361 | -0.35248 | -0.086975 | 0.027466 | 122.7127 | -1.0895 | -0.33874 | -0.050354 | 0.37994 | 71.3425 | 72.8073 | 121.4905 | 122.493 | 0.027466 | 122.5296 | 75.8331 | -0.33874 | 122.493 | 0.027466 | 75.8331 | 121.4905 | 122.5296 | -122.9324 | -122.9187
1438.9688 | 122.7722 | -80.6717 | 42.0227 | -0.2095 | 0.0025892 | 0.0040952 | 0.0051825 | -0.0041166 | -0.00071986 | -0.0047061 | -80.6763 | 41.922 | -81.0333 | 42.009 | 40.7822 | -3.9688 | -8.4961 | -7.3608 | 41.9495 | -81.0333 | -0.36163 | -0.10071 | -0.004578 | 122.6807 | -1.2405 | -0.36163 | -0.073242 | 0.35706 | 72.1756 | 73.3109 | 121.4539 | 122.5937 | -0.004578 | 122.6212 | 76.7029 | -0.36163 | 122.5937 | -0.004578 | 76.7029 | 121.4539 | 122.6212 | -123.056 | -123.056
1439.9062 | 122.7905 | -79.7287 | 42.897 | 0.37033 | 0.00323 | 0.006445 | 0.0090277 | -0.0030484 | -0.0022153 | -0.0029971 | -79.6555 | 42.9611 | -80.0079 | 42.9611 | 41.748 | -4.0924 | -8.7158 | -7.2235 | 42.9016 | -80.1086 | -0.27924 | 0.064087 | 0.073242 | 122.6898 | -1.149 | -0.37994 | 0.004577 | 0.35248 | 71.0129 | 72.5052 | 121.4767 | 122.6898 | 0.073242 | 122.6303 | 75.6363 | -0.37994 | 122.6898 | 0.073242 | 75.6363 | 121.4767 | 122.6303 | -122.905 | -123.0057
1440.9688 | 122.8088 | -79.7699 | 42.8467 | 0.027008 | 0.0053662 | 0.0060178 | 0.0077459 | -0.001553 | -0.00050626 | -0.0040653 | -79.5776 | 42.8558 | -80.072 | 42.9703 | 41.7709 | -4.0466 | -8.6243 | -7.1136 | 42.9108 | -80.1041 | -0.30212 | 0.009155 | 0.19226 | 122.7402 | -1.0757 | -0.33417 | 0.064087 | 0.49438 | 71.1456 | 72.6562 | 121.5408 | 122.6257 | 0.19226 | 122.6807 | 75.7233 | -0.33417 | 122.6257 | 0.19226 | 75.7233 | 121.5408 | 122.6807 | -122.9187 | -122.9507
1441.9062 | 122.7997 | -79.4174 | 43.2266 | 0.088043 | 0.0042982 | 0.0068722 | 0.0051825 | -0.001553 | -0.00071986 | -0.0040653 | -79.4128 | 43.1808 | -79.8019 | 43.3136 | 42.1371 | -4.0833 | -8.725 | -7.3196 | 43.2449 | -79.7424 | -0.38452 | -0.045777 | 0.004577 | 122.731 | -1.0895 | -0.32501 | 0.01831 | 0.3891 | 70.6924 | 72.0978 | 121.5546 | 122.5983 | 0.004577 | 122.6624 | 75.3342 | -0.32501 | 122.5983 | 0.004577 | 75.3342 | 121.5546 | 122.6624 | -123.0286 | -122.9691
1442.9688 | 122.9233 | -78.7399 | 43.8309 | 0.28641 | 0.0019482 | 0.0083676 | -0.0012261 | 0.00015601 | -0.0026425 | -0.0038515 | -78.6896 | 43.7531 | -79.0787 | 44.0689 | 42.9428 | -3.9688 | -8.6609 | -7.164 | 43.8812 | -79.01 | -0.33875 | -0.07782 | 0.050354 | 122.8088 | -0.88806 | -0.27008 | 0.050354 | 0.3891 | 70.079 | 71.5759 | 121.6827 | 122.493 | 0.050354 | 122.6212 | 74.7711 | -0.27008 | 122.493 | 0.050354 | 74.7711 | 121.6827 | 122.6212 | -122.9095 | -122.8409
1443.9062 | 122.8226 | -79.097 | 43.5699 | -0.026398 | 0.0042982 | 0.0070858 | 0.0073187 | -0.00048499 | -0.0022153 | -0.0027835 | -79.0146 | 43.5287 | -79.4083 | 43.6935 | 42.5491 | -4.1107 | -8.313 | -7.1503 | 43.5883 | -79.4128 | -0.31128 | -0.041198 | 0.082398 | 122.7905 | -1.0208 | -0.31586 | 0.018311 | 0.39368 | 70.784 | 71.9467 | 121.6461 | 122.6257 | 0.082398 | 122.6852 | 74.9863 | -0.31586 | 122.6257 | 0.082398 | 74.9863 | 121.6461 | 122.6852 | -122.9782 | -122.9828
1444.9688 | 122.7951 | -79.4174 | 43.2358 | -0.17136 | 0.00323 | 0.0049496 | 0.0009101 | -0.0028348 | -0.0013609 | -0.0025699 | -79.3533 | 43.2175 | -79.715 | 43.3136 | 42.1509 | -4.3076 | -8.194 | -7.1274 | 43.2632 | -79.7607 | -0.29755 | -0.018311 | 0.064086 | 122.731 | -1.0849 | -0.34332 | 0.027466 | 0.36163 | 71.2234 | 72.29 | 121.5683 | 122.6349 | 0.064086 | 122.6807 | 75.1099 | -0.34332 | 122.6349 | 0.064086 | 75.1099 | 121.5683 | 122.6807 | -122.9507 | -122.9965
1445.9062 | 122.7951 | -79.4128 | 43.1946 | -0.034027 | 0.0036572 | 0.0068722 | 0.0079595 | -0.0011258 | -0.0022153 | -0.0029971 | -79.39 | 43.19 | -79.7836 | 43.2724 | 42.0731 | -3.9917 | -7.6401 | -6.8253 | 43.2495 | -79.7745 | -0.37079 | -0.004578 | 0.022888 | 122.6852 | -1.1215 | -0.36163 | 0.054932 | 0.39368 | 71.7728 | 72.5876 | 121.4859 | 122.6028 | 0.022888 | 122.6624 | 75.4211 | -0.36163 | 122.6028 | 0.022888 | 75.4211 | 121.4859 | 122.6624 | -122.9782 | -122.9691
1446.9688 | 122.7951 | -79.7791 | 42.8513 | 0.011749 | 0.0064344 | 0.0058042 | 0.0073187 | -0.00091219 | 0.00077554 | -0.0034243 | -79.6875 | 42.8833 | -80.0674 | 42.9886 | 41.7297 | -4.216 | -7.933 | -7.077 | 42.865 | -80.1361 | -0.28839 | 0.032044 | 0.091553 | 122.7676 | -1.1215 | -0.35705 | 0.013733 | 0.37994 | 71.846 | 72.702 | 121.5088 | 122.6624 | 0.091553 | 122.644 | 75.5631 | -0.35705 | 122.6624 | 0.091553 | 75.5631 | 121.5088 | 122.644 | -122.9187 | -122.9874
1447.9062 | 122.9233 | -78.8315 | 43.7439 | 0.24063 | 0.0047254 | 0.0045224 | 0.0024053 | 0.0014376 | -0.0011471 | -0.0021427 | -78.6942 | 43.7439 | -79.0833 | 43.8995 | 42.421 | -3.978 | -7.4936 | -6.8848 | 43.7714 | -79.1428 | -0.25177 | 0 | 0.13733 | 122.731 | -1.3229 | -0.31128 | 0.027466 | 0.3891 | 71.3379 | 71.9467 | 121.2524 | 122.5754 | 0.13733 | 122.6028 | 74.8535 | -0.31128 | 122.5754 | 0.13733 | 74.8535 | 121.2524 | 122.6028 | -122.8271 | -122.8867
1448.9531 | 122.7951 | -79.1702 | 43.4647 | 0.019379 | 0.0064344 | 0.010077 | 0.0053961 | -0.00091219 | -0.0026425 | -0.0027835 | -79.1656 | 43.3685 | -79.5502 | 43.5013 | 42.2333 | -4.1611 | -7.6904 | -7.1274 | 43.4647 | -79.5364 | -0.37994 | -0.096131 | 0.004578 | 122.6715 | -1.2314 | -0.36621 | 0 | 0.38452 | 71.4798 | 72.0428 | 121.4035 | 122.5388 | 0.004578 | 122.6349 | 75.0092 | -0.36621 | 122.5388 | 0.004578 | 75.0092 | 121.4035 | 122.6349 | -123.0148 | -123.0011
1449.9062 | 122.7768 | -79.9484 | 42.7185 | 0.14908 | 0.0047254 | 0.0040952 | 0.0041143 | -0.002194 | 0.0014163 | -0.0040653 | -79.66 | 42.7551 | -80.2277 | 42.7139 | 41.6656 | -4.3396 | -8.7112 | -8.0887 | 42.7322 | -80.2597 | -0.27924 | 0.036621 | 0.28839 | 122.6624 | -1.0529 | -0.31128 | 0.013733 | 0.56763 | 71.2372 | 71.8597 | 121.6141 | 122.7036 | 0.28839 | 122.6807 | 75.6088 | -0.31128 | 122.7036 | 0.28839 | 75.6088 | 121.6141 | 122.6807 | -122.9462 | -122.9782
1450.9688 | 122.8821 | -79.3442 | 43.2541 | 0.24826 | 0.0034436 | 0.008154 | 0.0030463 | -0.0028348 | -0.00093346 | -0.00086094 | -79.2252 | 43.277 | -79.6097 | 43.4326 | 42.1738 | -4.0558 | -8.6517 | -7.7866 | 43.277 | -79.6326 | -0.2655 | 0.022889 | 0.11902 | 122.7768 | -1.0803 | -0.28839 | 0.022889 | 0.38452 | 70.6924 | 71.5576 | 121.5179 | 122.6212 | 0.11902 | 122.6212 | 75.2884 | -0.28839 | 122.6212 | 0.11902 | 75.2884 | 121.5179 | 122.6212 | -122.8638 | -122.8867
1451.9062 | 122.8134 | -79.866 | 42.7826 | -0.11032 | 0.0034436 | 0.0055906 | 0.0066779 | -0.002194 | -0.0015745 | -0.0023563 | -79.7653 | 42.8101 | -80.1682 | 42.8741 | 41.6153 | -4.1107 | -8.3954 | -8.0338 | 42.8101 | -80.1865 | -0.30212 | 0.027466 | 0.10071 | 122.7402 | -1.1673 | -0.32043 | 0.027466 | 0.40283 | 71.4706 | 71.8323 | 121.4813 | 122.6761 | 0.10071 | 122.6761 | 75.7553 | -0.32043 | 122.6761 | 0.10071 | 75.7553 | 121.4813 | 122.6761 | -122.9507 | -122.9691
1452.9688 | 122.7859 | -79.2343 | 43.4326 | 0.32455 | 0.00088016 | 0.005377 | 0.0028327 | 0.0010104 | -0.00071986 | -0.0010745 | -78.9597 | 43.4418 | -79.5364 | 43.4555 | 42.3019 | -4.1016 | -8.6609 | -8.1757 | 43.4372 | -79.5227 | -0.30212 | 0.009155 | 0.27466 | 122.6898 | -1.1307 | -0.28839 | 0.004578 | 0.57678 | 70.5734 | 71.0587 | 121.5363 | 122.6761 | 0.27466 | 122.6715 | 75.1328 | -0.28839 | 122.6761 | 0.27466 | 75.1328 | 121.5363 | 122.6715 | -122.9691 | -122.9553
1453.9062 | 122.8043 | -80.0583 | 42.5949 | -0.026398 | 0.0055798 | 0.0060178 | 0.0071051 | 0.00015601 | -0.0028561 | -0.0034243 | -79.8935 | 42.6224 | -80.3101 | 42.627 | 41.5054 | -4.5914 | -9.1461 | -8.551 | 42.5812 | -80.4382 | -0.25177 | 0.027465 | 0.16479 | 122.6852 | -1.0895 | -0.37994 | -0.013733 | 0.41656 | 70.9122 | 71.5073 | 121.5637 | 122.6807 | 0.16479 | 122.6395 | 75.4669 | -0.37994 | 122.6807 | 0.16479 | 75.4669 | 121.5637 | 122.6395 | -122.905 | -123.0331
1454.9531 | 122.8409 | -79.7241 | 42.9199 | -0.19424 | 0.0053662 | 0.001959 | 0.0041143 | -0.00027139 | -0.0015745 | -0.0023563 | -79.6967 | 42.7872 | -80.1315 | 43.0023 | 41.8762 | -4.4174 | -9.082 | -8.5831 | 42.9382 | -80.0674 | -0.40741 | -0.13275 | 0.027466 | 122.7264 | -1.0437 | -0.34332 | 0.01831 | 0.43488 | 70.6421 | 71.1411 | 121.6003 | 122.5113 | 0.027466 | 122.6624 | 75.3067 | -0.34332 | 122.5113 | 0.027466 | 75.3067 | 121.6003 | 122.6624 | -123.0515 | -122.9874
1455.9062 | 122.8638 | -79.5593 | 43.0344 | 0.18723 | 0.0047254 | 0.008154 | 0.0036871 | -0.00048499 | -0.0022153 | -0.0042789 | -79.4449 | 43.0984 | -79.834 | 43.2129 | 42.1005 | -4.3716 | -8.9493 | -8.4457 | 43.1168 | -79.8523 | -0.27466 | 0.064087 | 0.11444 | 122.7722 | -0.93384 | -0.29297 | 0.082397 | 0.3891 | 70.61 | 71.1136 | 121.6599 | 122.6578 | 0.11444 | 122.6761 | 75.1877 | -0.29297 | 122.6578 | 0.11444 | 75.1877 | 121.6599 | 122.6761 | -122.8683 | -122.8867
1456.9688 | 122.7814 | -79.6738 | 42.9611 | -1.9948 | 0.0038708 | 0.0094358 | 0.0013373 | -0.0024076 | 0.0018435 | -0.0025699 | -79.6234 | 43.0664 | -79.9118 | 43.0847 | 41.9449 | -4.6555 | -8.8898 | -8.6929 | 43.0206 | -80.0217 | -0.23804 | 0.10529 | 0.050354 | 122.7585 | -1.0162 | -0.3479 | 0.059509 | 0.28839 | 70.784 | 70.9808 | 121.6187 | 122.7402 | 0.050354 | 122.6944 | 75.0183 | -0.3479 | 122.7402 | 0.050354 | 75.0183 | 121.6187 | 122.6944 | -122.8729 | -122.9828
1457.9062 | 122.8683 | -78.9322 | 43.6386 | 0.1796 | 0.0042982 | 0.001959 | -0.0010125 | -0.0013394 | -0.00071986 | -0.0023563 | -78.8406 | 43.5837 | -79.248 | 43.84 | 42.8055 | -4.0787 | -8.4183 | -8.075 | 43.6569 | -79.2526 | -0.31586 | -0.054932 | 0.091553 | 122.7722 | -0.83313 | -0.32043 | 0.01831 | 0.40741 | 70.5139 | 70.8572 | 121.7377 | 122.5159 | 0.091553 | 122.5891 | 74.8535 | -0.32043 | 122.5159 | 0.091553 | 74.8535 | 121.7377 | 122.5891 | -122.8867 | -122.8912
1458.9531 | 122.7905 | -79.5181 | 43.1763 | -0.1561 | 0.0030164 | 0.0051632 | 0.0021917 | -0.0045438 | -0.00093346 | -0.0032107 | -79.4403 | 43.1763 | -79.8065 | 43.2358 | 42.1463 | -4.921 | -8.3084 | -8.4274 | 43.1808 | -79.866 | -0.28839 | 0 | 0.077819 | 122.7539 | -1.03 | -0.3479 | 0.004577 | 0.36621 | 71.2097 | 71.0907 | 121.6644 | 122.6944 | 0.077819 | 122.699 | 74.5972 | -0.3479 | 122.6944 | 0.077819 | 74.5972 | 121.6644 | 122.699 | -122.9828 | -123.0423
1459.9062 | 122.8271 | -80.191 | 42.453 | -0.10269 | 0.0034436 | 0.0083676 | 0.0053961 | -0.0034756 | -0.0024289 | -0.0047061 | -80.1315 | 42.4118 | -80.5573 | 42.5354 | 41.423 | -4.9805 | -9.5444 | -9.0958 | 42.4393 | -80.5435 | -0.36621 | -0.041199 | 0.059509 | 122.7264 | -1.03 | -0.35248 | -0.013733 | 0.42572 | 70.6467 | 71.0953 | 121.6141 | 122.6028 | 0.059509 | 122.6303 | 75.2106 | -0.35248 | 122.6028 | 0.059509 | 75.2106 | 121.6141 | 122.6303 | -123.0103 | -122.9965
1460.9688 | 122.7676 | -80.6305 | 42.0685 | -0.16373 | 0.0030164 | 0.0058042 | 0.0006965 | -0.0045438 | -0.0017881 | -0.0034243 | -80.571 | 41.9815 | -80.9692 | 42.0959 | 41.0294 | -5.1315 | -9.7321 | -9.3155 | 42.0273 | -80.9692 | -0.33875 | -0.086975 | 0.059509 | 122.7264 | -1.0391 | -0.33875 | -0.041198 | 0.39825 | 70.8984 | 71.315 | 121.6599 | 122.612 | 0.059509 | 122.6578 | 75.499 | -0.33875 | 122.612 | 0.059509 | 75.499 | 121.6599 | 122.6578 | -123.0377 | -123.0377
1461.9062 | 122.8638 | -80.6534 | 41.9998 | -0.22476 | 0.0025892 | 0.0070858 | 0.0049689 | -0.0019802 | -0.00050626 | -0.0034243 | -80.5801 | 41.9861 | -80.9875 | 42.0868 | 40.9241 | -5.0812 | -9.9014 | -9.1644 | 41.9952 | -81.0059 | -0.33417 | -0.013733 | 0.073242 | 122.7402 | -1.0757 | -0.35248 | -0.004578 | 0.40741 | 70.752 | 71.489 | 121.5775 | 122.6395 | 0.073242 | 122.6486 | 75.5722 | -0.35248 | 122.6395 | 0.073242 | 75.5722 | 121.5775 | 122.6486 | -122.9874 | -123.0057
1462.9531 | 122.8409 | -80.6671 | 41.9815 | -0.14847 | 0.0017346 | 0.0038816 | 0.0053961 | -0.0026212 | -0.0024289 | -0.0027835 | -80.4062 | 42.1692 | -80.8182 | 42.1417 | 40.9607 | -5.2277 | -9.7183 | -8.9859 | 42.0593 | -80.9921 | -0.15106 | 0.18768 | 0.26093 | 122.8088 | -1.0208 | -0.32501 | 0.07782 | 0.41199 | 70.9488 | 71.6812 | 121.6278 | 122.8363 | 0.26093 | 122.7264 | 75.4395 | -0.32501 | 122.8363 | 0.26093 | 75.4395 | 121.6278 | 122.7264 | -122.7997 | -122.9736
1463.9062 | 122.7997 | -80.3925 | 42.2379 | -0.026398 | 0.0047254 | 0.0075132 | 0.0060369 | -0.0017666 | -0.0024289 | -0.0036379 | -80.3101 | 42.2424 | -80.722 | 42.3111 | 41.2125 | -4.4586 | -9.5398 | -8.4091 | 42.2379 | -80.7541 | -0.32959 | 0.004578 | 0.082397 | 122.7036 | -1.0254 | -0.36163 | 0 | 0.41199 | 70.8527 | 71.9833 | 121.6049 | 122.6349 | 0.082397 | 122.6303 | 75.9338 | -0.36163 | 122.6349 | 0.082397 | 75.9338 | 121.6049 | 122.6303 | -122.9599 | -122.9919
1464.9688 | 122.8729 | -80.9052 | 41.716 | -0.20187 | 0.0023756 | 0.0049496 | -0.0010125 | -0.003262 | -7.9062e-05 | -0.00086094 | -80.809 | 41.6702 | -81.1981 | 41.8991 | 40.86 | -4.7653 | -9.3842 | -8.8211 | 41.7389 | -81.2622 | -0.29297 | -0.045776 | 0.09613 | 122.8043 | -0.85602 | -0.35706 | 0.022889 | 0.3891 | 71.521 | 72.084 | 121.7651 | 122.5754 | 0.09613 | 122.644 | 76.1398 | -0.35706 | 122.5754 | 0.09613 | 76.1398 | 121.7651 | 122.644 | -122.9141 | -122.9782
1465.9062 | 122.8363 | -80.365 | 42.2928 | -0.056915 | 0.0055798 | 0.0066586 | 0.0068915 | -0.0028348 | -0.00093346 | -0.0044925 | -80.127 | 42.3203 | -80.6305 | 42.453 | 41.2766 | -4.9118 | -9.6909 | -9.2331 | 42.3386 | -80.6854 | -0.2655 | 0.027465 | 0.23804 | 122.818 | -1.0162 | -0.32043 | 0.045776 | 0.50354 | 70.6741 | 71.1319 | 121.6415 | 122.6852 | 0.23804 | 122.7036 | 75.4532 | -0.32043 | 122.6852 | 0.23804 | 75.4532 | 121.6415 | 122.7036 | -122.9233 | -122.9782
1466.9688 | 122.7997 | -80.0217 | 42.6361 | -0.25528 | 0.0028028 | 0.0040952 | 0.0024053 | -0.0011258 | -0.00071986 | -0.0042789 | -79.9713 | 42.5674 | -80.3925 | 42.6819 | 41.6702 | -5.1407 | -9.4254 | -8.931 | 42.6498 | -80.3604 | -0.37079 | -0.068664 | 0.050354 | 122.7036 | -0.96588 | -0.33875 | 0.013733 | 0.42114 | 70.5963 | 71.0907 | 121.6919 | 122.5891 | 0.050354 | 122.6715 | 74.881 | -0.33875 | 122.5891 | 0.050354 | 74.881 | 121.6919 | 122.6715 | -123.0286 | -122.9965
1467.9062 | 122.8088 | -79.5135 | 43.1625 | 0.034637 | 0.0030164 | 0.004736 | 0.0066779 | -0.0013394 | -0.0024289 | -0.0042789 | -79.3533 | 43.2541 | -79.7333 | 43.2495 | 42.1509 | -5.0354 | -8.5052 | -7.8552 | 43.1854 | -79.8386 | -0.21973 | 0.091552 | 0.16022 | 122.7631 | -1.0117 | -0.32501 | 0.022888 | 0.37994 | 71.0083 | 71.6583 | 121.6644 | 122.7676 | 0.16022 | 122.699 | 74.4781 | -0.32501 | 122.7676 | 0.16022 | 74.4781 | 121.6644 | 122.699 | -122.8958 | -123.0011
1468.9688 | 122.9141 | -78.2272 | 44.371 | 0.27115 | 0.0030164 | 0.0015316 | -0.0016535 | -0.0024076 | 0.00013454 | -0.0036379 | -78.0716 | 44.426 | -78.4744 | 44.5587 | 43.4647 | -4.4174 | -8.6609 | -8.0338 | 44.3848 | -78.566 | -0.24719 | 0.054931 | 0.15564 | 122.7859 | -0.90637 | -0.33875 | 0.013733 | 0.40283 | 69.5663 | 70.1935 | 121.6919 | 122.6532 | 0.15564 | 122.612 | 73.8098 | -0.33875 | 122.6532 | 0.15564 | 73.8098 | 121.6919 | 122.612 | -122.8455 | -122.937
1469.9062 | 122.8043 | -78.6896 | 44.0094 | -0.13321 | 0.002162 | 0.0068722 | 0.0051825 | -0.00091219 | -0.0015745 | -0.0042789 | -78.5614 | 43.9453 | -79.0009 | 44.0689 | 42.9932 | -4.2114 | -8.075 | -7.576 | 43.9911 | -79.0649 | -0.31128 | -0.064087 | 0.12817 | 122.7585 | -1.0162 | -0.37537 | -0.01831 | 0.43945 | 70.6146 | 71.1136 | 121.6827 | 122.6349 | 0.12817 | 122.6807 | 74.4781 | -0.37537 | 122.6349 | 0.12817 | 74.4781 | 121.6827 | 122.6807 | -123.0103 | -123.0743
1470.9688 | 122.7951 | -79.1885 | 43.4875 | -0.25528 | 0.0038708 | 0.010717 | 0.0041143 | -0.0019802 | -0.00050626 | -0.0038515 | -79.3442 | 43.4692 | -79.5227 | 43.5333 | 42.4713 | -3.9093 | -8.4045 | -7.8598 | 43.4921 | -79.5364 | -0.33417 | -0.018311 | -0.15564 | 122.7219 | -1.0162 | -0.3479 | 0.004577 | 0.17853 | 70.784 | 71.3287 | 121.6599 | 122.6578 | -0.15564 | 122.6807 | 75.2792 | -0.3479 | 122.6578 | -0.15564 | 75.2792 | 121.6599 | 122.6807 | -123.0103 | -123.024
1471.9062 | 122.8043 | -79.8523 | 42.8329 | -0.18662 | 0.0047254 | 0.0034544 | 0.0049689 | -0.00091219 | -7.9062e-05 | -0.0015017 | -79.7836 | 42.7597 | -80.1636 | 42.8604 | 41.8121 | -4.4815 | -8.4503 | -7.7683 | 42.8467 | -80.2094 | -0.31128 | -0.073242 | 0.068665 | 122.7127 | -1.0208 | -0.35706 | 0.013733 | 0.37994 | 71.402 | 72.084 | 121.6644 | 122.612 | 0.068665 | 122.699 | 75.3708 | -0.35706 | 122.612 | 0.068665 | 75.3708 | 121.6644 | 122.699 | -122.9965 | -123.0423
1472.9062 | 122.7859 | -79.3442 | 43.3228 | 0.080414 | 0.001521 | 0.0090086 | 0.0079595 | -0.00091219 | -0.0020017 | -0.0027835 | -79.184 | 43.3594 | -79.628 | 43.4006 | 42.3431 | -3.6392 | -8.4183 | -8.0566 | 43.396 | -79.6875 | -0.28381 | 0.036621 | 0.16022 | 122.7448 | -0.97961 | -0.34332 | 0.073242 | 0.44403 | 70.9259 | 71.2875 | 121.6873 | 122.7036 | 0.16022 | 122.7402 | 75.705 | -0.34332 | 122.7036 | 0.16022 | 75.705 | 121.6873 | 122.7402 | -122.9507 | -123.0103
1473.9688 | 122.8546 | -79.3762 | 43.2953 | -0.17899 | 0.004939 | 3.6382e-05 | 0.0064643 | -0.00069859 | -0.0024289 | -0.0027835 | -79.2343 | 43.309 | -79.6371 | 43.4418 | 42.2653 | -3.479 | -8.2764 | -8.226 | 43.3502 | -79.715 | -0.26093 | 0.013733 | 0.14191 | 122.818 | -1.03 | -0.33875 | 0.054932 | 0.40283 | 71.0999 | 71.1502 | 121.6415 | 122.6852 | 0.14191 | 122.7264 | 75.8972 | -0.33875 | 122.6852 | 0.14191 | 75.8972 | 121.6415 | 122.7264 | -122.9324 | -123.0103
1474.9062 | 122.8317 | -78.154 | 44.5175 | -0.064545 | 0.0036572 | 0.0066586 | 0.0071051 | -0.0017666 | 0.00013454 | -0.0025699 | -77.9846 | 44.577 | -78.4149 | 44.6411 | 43.4647 | -3.511 | -8.1619 | -7.9468 | 44.5404 | -78.4607 | -0.26093 | 0.059509 | 0.16937 | 122.7951 | -1.0529 | -0.3067 | 0.022888 | 0.4303 | 69.9921 | 70.2072 | 121.6187 | 122.731 | 0.16937 | 122.6944 | 74.6429 | -0.3067 | 122.731 | 0.16937 | 74.6429 | 121.6187 | 122.6944 | -122.9324 | -122.9782
1475.9688 | 122.8043 | -79.0283 | 43.6478 | -0.62149 | 0.0040846 | 0.004736 | 0.0017645 | -0.0017666 | 0.00013454 | -0.0049197 | -78.891 | 43.7027 | -79.2389 | 43.7485 | 42.6315 | -3.8589 | -8.4641 | -7.782 | 43.6981 | -79.3259 | -0.21057 | 0.054932 | 0.13733 | 122.7768 | -1.0162 | -0.29755 | 0.050354 | 0.3479 | 70.5643 | 71.2463 | 121.6599 | 122.731 | 0.13733 | 122.7264 | 75.1694 | -0.29755 | 122.731 | 0.13733 | 75.1694 | 121.6599 | 122.7264 | -122.8867 | -122.9736
1476.9062 | 122.8455 | -79.0009 | 43.6798 | -0.24765 | 0.0013074 | 0.0055906 | 0.0041143 | -0.0030484 | -0.00029266 | -0.0034243 | -78.8818 | 43.7164 | -79.2847 | 43.8217 | 42.6865 | -3.8589 | -8.5831 | -7.6309 | 43.7027 | -79.2892 | -0.28381 | 0.036621 | 0.11902 | 122.8226 | -0.99335 | -0.28839 | 0.022888 | 0.40283 | 70.4178 | 71.3699 | 121.6873 | 122.7173 | 0.11902 | 122.7036 | 75.1419 | -0.28839 | 122.7173 | 0.11902 | 75.1419 | 121.6873 | 122.7036 | -122.9645 | -122.9691
1477.9531 | 122.8134 | -79.1656 | 43.4784 | -0.22476 | 0.0025892 | 0.0060178 | 0.0041143 | -5.7592e-05 | 0.00077554 | -0.0023563 | -79.1382 | 43.4647 | -79.5044 | 43.5287 | 42.5034 | -3.9597 | -8.6243 | -7.7774 | 43.515 | -79.5364 | -0.33875 | -0.013733 | 0.027465 | 122.6944 | -0.97504 | -0.37079 | 0.036621 | 0.36621 | 70.5414 | 71.3882 | 121.669 | 122.6303 | 0.027465 | 122.6807 | 75.206 | -0.37079 | 122.6303 | 0.027465 | 75.206 | 121.669 | 122.6807 | -122.9828 | -123.0148
1478.9062 | 122.7814 | -78.9551 | 43.7576 | -0.24765 | 0.0034436 | 0.005377 | 0.0017645 | -0.0030484 | -0.00093346 | -0.0047061 | -78.8956 | 43.7119 | -79.2755 | 43.7759 | 42.7185 | -3.7628 | -8.1757 | -7.7637 | 43.7576 | -79.2664 | -0.32044 | -0.045776 | 0.059509 | 122.731 | -1.0391 | -0.31128 | 0 | 0.37994 | 70.7794 | 71.1914 | 121.6736 | 122.6669 | 0.059509 | 122.7127 | 75.1923 | -0.31128 | 122.6669 | 0.059509 | 75.1923 | 121.6736 | 122.7127 | -123.0331 | -123.024
1479.9531 | 122.8958 | -78.4332 | 44.1879 | -2.3763 | 0.0013074 | 0.0068722 | -0.0022943 | -0.0019802 | -0.00071986 | -0.0015017 | -78.511 | 44.1193 | -78.7674 | 44.4168 | 43.277 | -3.5797 | -8.0063 | -7.7499 | 44.2108 | -78.7445 | -0.33417 | -0.068664 | -0.077819 | 122.85 | -0.91095 | -0.31128 | 0.022888 | 0.25635 | 70.4269 | 70.6833 | 121.7102 | 122.5525 | -0.077819 | 122.644 | 74.8535 | -0.31128 | 122.5525 | -0.077819 | 74.8535 | 121.7102 | 122.644 | -122.9553 | -122.9324
1480.9062 | 122.8409 | -79.1656 | 43.5562 | 0.18723 | 0.0070752 | 0.0079404 | 0.0068915 | -0.0019802 | -7.9062e-05 | -0.00043374 | -79.0466 | 43.5883 | -79.4174 | 43.5196 | 42.4347 | -3.7537 | -8.2855 | -7.9788 | 43.4921 | -79.4952 | -0.25177 | 0.032044 | 0.11902 | 122.6852 | -1.1215 | -0.32959 | -0.064087 | 0.37079 | 70.8801 | 71.1868 | 121.6003 | 122.7539 | 0.11902 | 122.6578 | 75.412 | -0.32959 | 122.7539 | 0.11902 | 75.412 | 121.6003 | 122.6578 | -122.9736 | -123.0515
1481.9688 | 122.8271 | -78.8635 | 43.7851 | -0.1561 | 0.0028028 | 0.0049496 | 0.0041143 | -0.00027139 | -0.00093346 | -0.0017153 | -78.7537 | 43.808 | -79.184 | 43.9453 | 42.8284 | -3.479 | -8.1665 | -7.5027 | 43.8263 | -79.2206 | -0.32044 | 0.022888 | 0.10986 | 122.8088 | -0.95673 | -0.35706 | 0.041199 | 0.4303 | 70.697 | 71.3608 | 121.6919 | 122.6715 | 0.10986 | 122.6898 | 75.3845 | -0.35706 | 122.6715 | 0.10986 | 75.3845 | 121.6919 | 122.6898 | -122.9691 | -123.0057
1482.9062 | 122.7722 | -77.9388 | 44.7784 | 0.095673 | 0.0045118 | 0.0083676 | 0.0073187 | 0.0010104 | -0.00029266 | -0.0025699 | -77.8519 | 44.7281 | -78.2364 | 44.6915 | 43.5791 | -3.6758 | -8.194 | -7.814 | 44.7144 | -78.2684 | -0.29755 | -0.050354 | 0.086975 | 122.6303 | -1.1993 | -0.32959 | -0.064087 | 0.38452 | 69.7449 | 70.1248 | 121.5179 | 122.6669 | 0.086975 | 122.6532 | 74.263 | -0.32959 | 122.6669 | 0.086975 | 74.263 | 121.5179 | 122.6532 | -123.0148 | -123.0469
1483.9062 | 122.7722 | -78.0304 | 44.6091 | 0.095673 | 0.0053662 | 0.0040952 | 0.0062507 | -0.0011258 | -0.0013609 | -0.0032107 | -78.0258 | 44.6045 | -78.3691 | 44.6503 | 43.5333 | -3.6118 | -8.3359 | -7.8964 | 44.6548 | -78.3737 | -0.33875 | -0.004578 | 0.004578 | 122.6807 | -1.0757 | -0.34332 | 0.045776 | 0.34332 | 69.6945 | 70.134 | 121.5637 | 122.6349 | 0.004578 | 122.6852 | 74.4186 | -0.34332 | 122.6349 | 0.004578 | 74.4186 | 121.5637 | 122.6852 | -122.9782 | -122.9828
1484.9688 | 122.8134 | -77.8931 | 44.7647 | -0.1561 | 0.0045118 | 0.0060178 | 0.0083869 | -0.0043302 | 0.0012027 | -0.0040653 | -77.8519 | 44.7418 | -78.2318 | 44.8334 | 43.7531 | -3.4012 | -8.0795 | -7.7454 | 44.7739 | -78.2227 | -0.33875 | -0.022888 | 0.041198 | 122.7264 | -1.0117 | -0.32959 | 0.009156 | 0.37994 | 69.8135 | 70.1477 | 121.6461 | 122.6349 | 0.041198 | 122.6669 | 74.4919 | -0.32959 | 122.6349 | 0.041198 | 74.4919 | 121.6461 | 122.6669 | -122.9965 | -122.9874
1485.9219 | 122.9462 | -79.0237 | 43.5699 | 0.15671 | 0.0030164 | 0.0060178 | 0.0015509 | -0.00091219 | -0.00050626 | -0.00064734 | -79.0329 | 43.4647 | -79.4495 | 43.6249 | 42.6361 | -3.3829 | -8.638 | -7.8049 | 43.5104 | -79.3854 | -0.42572 | -0.10529 | -0.009155 | 122.6486 | -0.93384 | -0.36163 | -0.059509 | 0.41656 | 70.3857 | 71.2189 | 121.6599 | 122.4884 | -0.009155 | 122.5342 | 75.6409 | -0.36163 | 122.4884 | -0.009155 | 75.6409 | 121.6599 | 122.5342 | -123.0194 | -122.9553
1486.9688 | 122.818 | -78.1128 | 44.5541 | -0.17136 | 0.0025892 | 0.0077268 | 0.0026191 | -0.0041166 | -0.0015745 | -0.0017153 | -78.0121 | 44.5679 | -78.4058 | 44.6228 | 43.6066 | -3.1586 | -8.0292 | -7.5027 | 44.577 | -78.4058 | -0.29297 | 0.013733 | 0.10071 | 122.7356 | -0.94757 | -0.29297 | 0.022888 | 0.39368 | 70.0836 | 70.61 | 121.7194 | 122.6807 | 0.10071 | 122.6898 | 74.9542 | -0.29297 | 122.6807 | 0.10071 | 74.9542 | 121.7194 | 122.6898 | -122.9599 | -122.9599
1487.9062 | 122.7859 | -77.742 | 44.9524 | 0.042267 | 0.0034436 | 0.0062314 | 0.0068915 | -0.002194 | -7.9062e-05 | -0.0040653 | -77.6916 | 44.9387 | -78.0579 | 44.9432 | 43.8675 | -3.186 | -7.9834 | -7.4844 | 44.9203 | -78.0762 | -0.31586 | -0.013733 | 0.050354 | 122.6852 | -1.0849 | -0.33417 | -0.032044 | 0.36621 | 69.7586 | 70.2576 | 121.6095 | 122.6807 | 0.050354 | 122.6624 | 74.556 | -0.33417 | 122.6807 | 0.050354 | 74.556 | 121.6095 | 122.6624 | -123.0103 | -123.0286
1488.9844 | 122.8226 | -76.2588 | 46.3715 | 0.17197 | 0.0055798 | 0.0062314 | 0.0053961 | -0.00027139 | -0.00093346 | -0.0019289 | -76.2451 | 46.3165 | -76.6068 | 46.463 | 45.3735 | -3.1586 | -8.3313 | -7.3334 | 46.3989 | -76.5472 | -0.3479 | -0.054932 | 0.013733 | 122.7219 | -0.99793 | -0.28839 | 0.027466 | 0.36163 | 67.9276 | 68.9255 | 121.6324 | 122.5754 | 0.013733 | 122.6578 | 73.1003 | -0.28839 | 122.5754 | 0.013733 | 73.1003 | 121.6324 | 122.6578 | -122.9782 | -122.9187
1489.9062 | 122.8271 | -76.2817 | 46.3669 | 0.042267 | 0.0062208 | 0.0058042 | 0.0075323 | 0.0010104 | -0.00093346 | -0.0029971 | -76.1398 | 46.3852 | -76.5564 | 46.4859 | 45.3735 | -2.8748 | -8.1161 | -7.1457 | 46.3715 | -76.6342 | -0.27466 | 0.018311 | 0.14191 | 122.7676 | -0.99335 | -0.35248 | 0.004578 | 0.41656 | 68.1656 | 69.136 | 121.6553 | 122.6669 | 0.14191 | 122.6532 | 73.407 | -0.35248 | 122.6669 | 0.14191 | 73.407 | 121.6553 | 122.6532 | -122.9233 | -123.0011
1490.9688 | 122.7814 | -76.5701 | 46.1105 | -0.14084 | 0.00323 | 0.0045224 | -0.0018671 | -0.0024076 | -0.00029266 | -0.0023563 | -76.5747 | 46.0419 | -76.9363 | 46.1334 | 45.0531 | -2.6962 | -8.0292 | -6.9626 | 46.1105 | -76.8951 | -0.36621 | -0.068665 | -0.004578 | 122.7036 | -1.0574 | -0.32501 | 0 | 0.36163 | 68.541 | 69.6075 | 121.6232 | 122.612 | -0.004578 | 122.6807 | 73.8739 | -0.32501 | 122.612 | -0.004578 | 73.8739 | 121.6232 | 122.6807 | -123.0469 | -123.0057
1491.9062 | 122.8363 | -76.7258 | 45.9503 | 0.40085 | 0.0038708 | 0.0068722 | 0.0049689 | -0.0026212 | -0.0013609 | -0.0040653 | -76.6068 | 45.932 | -77.0325 | 46.0602 | 44.9295 | -2.7328 | -8.3817 | -6.7703 | 45.9549 | -77.0508 | -0.3067 | -0.01831 | 0.11902 | 122.7859 | -1.0208 | -0.32501 | 0.004578 | 0.42572 | 68.3441 | 69.9554 | 121.6553 | 122.6578 | 0.11902 | 122.6807 | 73.9929 | -0.32501 | 122.6578 | 0.11902 | 73.9929 | 121.6553 | 122.6807 | -122.9828 | -123.0011
1492.9688 | 122.7859 | -77.5131 | 45.1767 | -0.23239 | 0.0047254 | 0.005377 | 0.0006965 | -0.0028348 | -0.0011471 | -0.0025699 | -77.4399 | 45.1035 | -77.8244 | 45.2271 | 44.133 | -2.8976 | -8.2718 | -6.7017 | 45.2133 | -77.8656 | -0.31128 | -0.073242 | 0.073243 | 122.7402 | -1.0437 | -0.35248 | 0.036621 | 0.38452 | 69.2413 | 70.8115 | 121.6461 | 122.6166 | 0.073243 | 122.7264 | 74.6155 | -0.35248 | 122.6166 | 0.073243 | 74.6155 | 121.6461 | 122.7264 | -123.0011 | -123.0423
1493.9219 | 122.905 | -77.2018 | 45.3873 | 0.34744 | 0.0010938 | 0.005377 | 0.0009101 | -0.0030484 | -0.0022153 | -0.00043374 | -77.092 | 45.3598 | -77.5131 | 45.5658 | 44.4626 | -2.8061 | -8.5739 | -6.8527 | 45.3827 | -77.504 | -0.31128 | -0.027466 | 0.10986 | 122.7676 | -0.92468 | -0.30212 | -0.004578 | 0.42114 | 68.6279 | 70.3491 | 121.6644 | 122.5616 | 0.10986 | 122.5845 | 74.3958 | -0.30212 | 122.5616 | 0.10986 | 74.3958 | 121.6644 | 122.5845 | -122.9004 | -122.8912
1494.9531 | 122.8134 | -76.9043 | 45.7718 | -0.20187 | 0.00323 | 0.0032406 | 0.0004827 | -0.00668 | 0.00056194 | -0.0010745 | -76.8311 | 45.7443 | -77.1927 | 45.7947 | 44.6777 | -2.7008 | -8.2809 | -6.8665 | 45.7581 | -77.2659 | -0.28839 | -0.027466 | 0.073242 | 122.699 | -1.0941 | -0.36163 | -0.013733 | 0.36163 | 68.6234 | 70.0378 | 121.582 | 122.6486 | 0.073242 | 122.6624 | 74.2035 | -0.36163 | 122.6486 | 0.073242 | 74.2035 | 121.582 | 122.6624 | -122.9645 | -123.0377
1495.9219 | 122.905 | -76.9089 | 45.6757 | -0.018768 | 0.0010938 | 0.0040952 | -0.0003717 | -0.0045438 | -0.00050626 | -0.0025699 | -76.9043 | 45.5795 | -77.2842 | 45.8542 | 44.7052 | -2.6321 | -8.4915 | -6.6742 | 45.7169 | -77.2202 | -0.37537 | -0.09613 | 0.004578 | 122.7631 | -0.97046 | -0.31128 | 0.041199 | 0.37994 | 68.4174 | 70.2347 | 121.6141 | 122.4884 | 0.004578 | 122.6257 | 74.2767 | -0.31128 | 122.4884 | 0.004578 | 74.2767 | 121.6141 | 122.6257 | -122.9599 | -122.8958
1496.9688 | 122.8638 | -75.8743 | 46.7606 | -0.19424 | 0.0019482 | 0.0038816 | 0.0039007 | -0.0028348 | -0.0011471 | -0.0040653 | -75.7919 | 46.7102 | -76.1536 | 46.9162 | 45.7214 | -2.2888 | -7.8461 | -6.0471 | 46.7606 | -76.2497 | -0.27923 | -0.050354 | 0.082398 | 122.7905 | -1.0391 | -0.37537 | 0 | 0.36163 | 68.0283 | 69.8273 | 121.5958 | 122.5845 | 0.082398 | 122.6349 | 73.5855 | -0.37537 | 122.5845 | 0.082398 | 73.5855 | 121.5958 | 122.6349 | -122.9141 | -123.0103
1497.9062 | 122.7768 | -76.6846 | 45.9824 | 0.034637 | 0.004939 | 0.006445 | 0.0088141 | -0.0036892 | -0.0030697 | -0.0038515 | -76.6068 | 45.9778 | -77.0142 | 46.0556 | 44.8837 | -2.504 | -7.9834 | -5.809 | 45.9641 | -77.0599 | -0.32959 | -0.004578 | 0.07782 | 122.7402 | -1.0986 | -0.37537 | -0.018311 | 0.40741 | 68.7012 | 70.8755 | 121.5683 | 122.6624 | 0.07782 | 122.6486 | 74.1806 | -0.37537 | 122.6624 | 0.07782 | 74.1806 | 121.5683 | 122.6486 | -122.9965 | -123.0423
1498.9844 | 122.8775 | -77.0187 | 45.5933 | 0.20248 | 0.0045118 | 0.0058042 | 0.0034735 | -0.0011258 | -0.00093346 | -0.0023563 | -76.9821 | 45.5475 | -77.3666 | 45.7352 | 44.5953 | -2.623 | -8.4824 | -5.928 | 45.6024 | -77.3483 | -0.3479 | -0.045777 | 0.036621 | 122.7539 | -0.99793 | -0.32959 | 0.009155 | 0.38452 | 68.5364 | 71.0907 | 121.6141 | 122.5662 | 0.036621 | 122.6212 | 74.3958 | -0.32959 | 122.5662 | 0.036621 | 74.3958 | 121.6141 | 122.6212 | -122.9599 | -122.9416
1499.9062 | 122.8088 | -77.1606 | 45.5292 | -0.17136 | 0.00323 | 0.003668 | 0.0041143 | -0.0024076 | 0.00098914 | -0.0032107 | -77.0782 | 45.5063 | -77.449 | 45.5704 | 44.4489 | -2.655 | -8.1619 | -5.9372 | 45.5521 | -77.4811 | -0.28839 | -0.022888 | 0.082398 | 122.731 | -1.0803 | -0.32043 | 0.022888 | 0.37079 | 68.9987 | 71.2234 | 121.6095 | 122.6669 | 0.082398 | 122.7127 | 74.5056 | -0.32043 | 122.6669 | 0.082398 | 74.5056 | 121.6095 | 122.7127 | -122.9782 | -123.0103
1500.9688 | 122.7448 | -77.2156 | 45.5017 | 0.17197 | 0.0045118 | 0.0068722 | 0.0066779 | -0.002194 | -0.0017881 | -0.0023563 | -77.0599 | 45.5658 | -77.4353 | 45.5338 | 44.545 | -3.5477 | -8.6655 | -5.8273 | 45.4971 | -77.504 | -0.21973 | 0.064087 | 0.15564 | 122.7493 | -0.95673 | -0.28839 | -0.004578 | 0.37537 | 68.5501 | 71.3882 | 121.7606 | 122.7814 | 0.15564 | 122.7127 | 73.6679 | -0.28839 | 122.7814 | 0.15564 | 73.6679 | 121.7606 | 122.7127 | -122.937 | -123.0057
1501.9062 | 122.818 | -77.1469 | 45.4971 | 0.042267 | 0.00323 | 0.004736 | 0.0068915 | 0.00079681 | -0.0017881 | -0.0015017 | -77.037 | 45.52 | -77.4719 | 45.5612 | 44.3481 | -3.5751 | -8.4961 | -5.9692 | 45.5109 | -77.4994 | -0.32501 | 0.022889 | 0.10986 | 122.7081 | -1.149 | -0.35248 | 0.013733 | 0.43488 | 68.6508 | 71.1777 | 121.4951 | 122.6669 | 0.10986 | 122.6578 | 73.5718 | -0.35248 | 122.6669 | 0.10986 | 73.5718 | 121.4951 | 122.6578 | -122.9691 | -122.9965
1502.9688 | 122.7951 | -77.0645 | 45.5887 | -0.0035098 | 0.0034436 | 0.0075132 | 0.0066779 | -0.00027139 | 0.00013454 | -0.0027835 | -76.8585 | 45.6894 | -77.2842 | 45.7214 | 44.5129 | -3.598 | -8.6105 | -5.9784 | 45.6345 | -77.3895 | -0.21973 | 0.10071 | 0.20599 | 122.7859 | -1.0757 | -0.32501 | 0.045776 | 0.42572 | 68.454 | 71.0861 | 121.5775 | 122.7539 | 0.20599 | 122.699 | 73.4665 | -0.32501 | 122.7539 | 0.20599 | 73.4665 | 121.5775 | 122.699 | -122.8729 | -122.9782
1503.9062 | 122.8363 | -77.2842 | 45.3781 | -0.1561 | 0.0034436 | 0.0051632 | 0.0041143 | -0.00069859 | 0.00034814 | -0.0027835 | -77.2156 | 45.3415 | -77.6367 | 45.4697 | 44.339 | -3.4698 | -8.519 | -5.9143 | 45.4193 | -77.5955 | -0.35248 | -0.036621 | 0.068665 | 122.7539 | -1.0391 | -0.31128 | 0.041199 | 0.42114 | 68.7653 | 71.3699 | 121.6232 | 122.6257 | 0.068665 | 122.7036 | 73.8144 | -0.31128 | 122.6257 | 0.068665 | 73.8144 | 121.6232 | 122.7036 | -123.0148 | -122.9736
1504.9531 | 122.8226 | -76.9684 | 45.6894 | -0.24002 | 0.004939 | 0.0060178 | -0.0025079 | -0.0024076 | 0.0012027 | -0.0025699 | -76.8997 | 45.694 | -77.2385 | 45.7672 | 44.6732 | -3.4836 | -8.6838 | -5.7861 | 45.7535 | -77.2751 | -0.27008 | 0.004578 | 0.068665 | 122.7356 | -1.0162 | -0.3067 | 0.064087 | 0.33874 | 68.2846 | 71.1823 | 121.6415 | 122.6624 | 0.068665 | 122.7219 | 73.4848 | -0.3067 | 122.6624 | 0.068665 | 73.4848 | 121.6415 | 122.7219 | -122.9279 | -122.9645
1505.9062 | 122.8821 | -77.4078 | 45.1721 | 0.28641 | 0.0030164 | 0.0060178 | 0.0049689 | -0.0028348 | -0.00050626 | -0.0010745 | -77.2568 | 45.2591 | -77.6642 | 45.3873 | 44.2108 | -3.5019 | -8.7936 | -5.4062 | 45.2225 | -77.7283 | -0.25635 | 0.086975 | 0.15106 | 122.7951 | -0.9613 | -0.32043 | 0.050354 | 0.40741 | 68.6142 | 72.0016 | 121.6187 | 122.6669 | 0.15106 | 122.6303 | 73.9059 | -0.32043 | 122.6669 | 0.15106 | 73.9059 | 121.6187 | 122.6303 | -122.8363 | -122.9004
1506.9688 | 122.8043 | -77.5864 | 45.0485 | -0.24765 | 0.0051526 | 0.0070858 | 0.0028327 | -0.0028348 | -7.9062e-05 | -0.0012881 | -77.4948 | 45.1218 | -77.8702 | 45.1263 | 43.9499 | -3.5339 | -8.3908 | -5.8319 | 45.1218 | -77.9251 | -0.28381 | 0.073242 | 0.091553 | 122.7127 | -1.0986 | -0.33875 | 0.073242 | 0.37537 | 69.1956 | 71.7545 | 121.5363 | 122.7081 | 0.091553 | 122.7081 | 74.0524 | -0.33875 | 122.7081 | 0.091553 | 74.0524 | 121.5363 | 122.7081 | -122.9187 | -122.9736
1507.9062 | 122.7905 | -77.7283 | 44.8975 | 0.065155 | 0.0036572 | 0.006445 | 0.0071051 | -0.0011258 | -0.0015745 | -0.0027835 | -77.3438 | 45.2499 | -77.7466 | 44.9982 | 43.8675 | -3.7033 | -8.6288 | -5.9372 | 44.9661 | -78.0396 | -0.018311 | 0.35248 | 0.38452 | 122.7264 | -1.03 | -0.31128 | 0.068664 | 0.40283 | 69.0994 | 71.7911 | 121.5958 | 122.9782 | 0.38452 | 122.6944 | 74.025 | -0.31128 | 122.9782 | 0.38452 | 74.025 | 121.5958 | 122.6944 | -122.644 | -122.937
1508.9688 | 122.7768 | -77.092 | 45.6116 | 1.2553 | 0.0038708 | -0.0018862 | 0.0011237 | -0.003903 | -7.9062e-05 | -0.0032107 | -77.1194 | 45.5292 | -77.4261 | 45.6345 | 44.4717 | -3.5202 | -8.4915 | -5.8044 | 45.6024 | -77.4124 | -0.33417 | -0.082397 | -0.027466 | 122.7264 | -1.1398 | -0.32043 | -0.009155 | 0.3067 | 68.6005 | 71.2875 | 121.5637 | 122.6212 | -0.027466 | 122.6944 | 73.5718 | -0.32043 | 122.6212 | -0.027466 | 73.5718 | 121.5637 | 122.6944 | -123.0377 | -123.024
1509.9062 | 122.8592 | -77.2064 | 45.4742 | -0.19424 | 0.0055798 | 0.0040952 | 0.0039007 | -0.00048499 | -0.0017881 | -0.0032107 | -77.1378 | 45.433 | -77.5726 | 45.5933 | 44.4397 | -3.4241 | -8.6151 | -5.7312 | 45.4926 | -77.5131 | -0.36621 | -0.041199 | 0.068665 | 122.7997 | -1.0345 | -0.3067 | 0.018311 | 0.43488 | 68.5913 | 71.4752 | 121.6461 | 122.6395 | 0.068665 | 122.699 | 73.7823 | -0.3067 | 122.6395 | 0.068665 | 73.7823 | 121.6461 | 122.699 | -123.0469 | -122.9874
1510.9688 | 122.7997 | -77.7649 | 44.9112 | 0.11856 | 0.0051526 | 0.0068722 | 0.0032599 | 0.00015601 | -0.00050626 | -0.0027835 | -77.8656 | 44.7189 | -78.241 | 44.838 | 43.7851 | -3.6118 | -8.6884 | -5.1041 | 44.8654 | -78.1265 | -0.47607 | -0.19226 | -0.10071 | 122.6028 | -1.1261 | -0.36163 | -0.045777 | 0.37537 | 69.0765 | 72.6608 | 121.55 | 122.4838 | -0.10071 | 122.6303 | 74.1531 | -0.36163 | 122.4838 | -0.10071 | 74.1531 | 121.55 | 122.6303 | -123.1522 | -123.0377
1511.9062 | 122.8134 | -77.2385 | 45.4239 | -0.2095 | 0.0019482 | 0.0043088 | 0.0006965 | -0.0028348 | -0.00071986 | -0.0027835 | -77.2293 | 45.3918 | -77.5223 | 45.4514 | 44.2657 | -3.4698 | -8.226 | -4.9026 | 45.4559 | -77.5864 | -0.28381 | -0.032043 | 0.009155 | 122.6898 | -1.1581 | -0.3479 | 0.032044 | 0.29297 | 69.0125 | 72.3358 | 121.5042 | 122.6303 | 0.009155 | 122.6944 | 73.7686 | -0.3479 | 122.6303 | 0.009155 | 73.7686 | 121.5042 | 122.6944 | -122.9462 | -123.0103
1512.9688 | 122.8271 | -77.4445 | 45.2454 | -0.2858 | 0.0038708 | 0.0068722 | -0.0003717 | -0.003903 | 0.00013454 | -0.0023563 | -77.3621 | 45.1813 | -77.7191 | 45.3278 | 44.1879 | -3.5339 | -8.4915 | -5.2689 | 45.2774 | -77.7695 | -0.27466 | -0.064087 | 0.082397 | 122.7722 | -1.0574 | -0.32501 | 0.032044 | 0.35706 | 68.9529 | 72.1756 | 121.6324 | 122.6257 | 0.082397 | 122.7219 | 73.9105 | -0.32501 | 122.6257 | 0.082397 | 73.9105 | 121.6324 | 122.7219 | -122.9645 | -123.0148
1513.9062 | 122.7768 | -77.0782 | 45.607 | -0.23239 | 0.0030164 | -0.001459 | 0.0026191 | -0.004971 | -0.0024289 | -0.0027835 | -77.0874 | 45.5109 | -77.449 | 45.6253 | 44.4717 | -3.3554 | -8.3221 | -5.3055 | 45.575 | -77.4216 | -0.37079 | -0.096131 | -0.009155 | 122.7036 | -1.1353 | -0.34332 | -0.032044 | 0.36163 | 68.7561 | 71.7728 | 121.55 | 122.5891 | -0.009155 | 122.6532 | 73.7228 | -0.34332 | 122.5891 | -0.009155 | 73.7228 | 121.55 | 122.6532 | -123.056 | -123.0286
1514.9688 | 122.8271 | -61.5967 | 61.0977 | 0.072784 | 0.0042982 | 0.0045224 | 0.0092413 | -0.0034756 | -0.0020017 | 0.0031979 | -61.4731 | 61.1389 | -61.821 | 61.2213 | 59.7382 | -0.64545 | -5.3879 | -2.9572 | 61.116 | -61.8851 | -0.2243 | 0.041199 | 0.1236 | 122.818 | -1.3596 | -0.28839 | 0.018311 | 0.3479 | 56.2088 | 58.6395 | 121.3348 | 122.7356 | 0.1236 | 122.7127 | 60.9512 | -0.28839 | 122.7356 | 0.1236 | 60.9512 | 121.3348 | 122.7127 | -122.9187 | -122.9828
1515.9062 | 122.85 | -55.1239 | 67.5476 | 0.027008 | 0.0045118 | 0.0028134 | 0.0075323 | -0.0011258 | -0.0011471 | 0.0027707 | -55.1651 | 67.5476 | -55.4123 | 67.6575 | 66.0919 | 0.46692 | -3.6209 | -1.5427 | 67.5522 | -55.4306 | -0.28839 | 0 | -0.041199 | 122.7814 | -1.4557 | -0.3067 | 0.004578 | 0.24719 | 51.503 | 53.5812 | 121.2158 | 122.6715 | -0.041199 | 122.6761 | 55.5908 | -0.3067 | 122.6715 | -0.041199 | 55.5908 | 121.2158 | 122.6761 | -122.9599 | -122.9782
1516.9688 | 122.8775 | -74.9405 | 47.6624 | 0.13382 | 0.0019482 | 0.0040952 | -0.0027215 | -0.002194 | 0.00056194 | -0.0032107 | -75.0412 | 47.4976 | -75.4074 | 47.8043 | 46.6278 | -2.7374 | -7.8461 | -4.9484 | 47.6624 | -75.2655 | -0.46692 | -0.16479 | -0.10071 | 122.7448 | -1.0345 | -0.32501 | 0 | 0.36621 | 67.0944 | 69.9921 | 121.5683 | 122.4381 | -0.10071 | 122.6028 | 72.2031 | -0.32501 | 122.4381 | -0.10071 | 72.2031 | 121.5683 | 122.6028 | -123.0698 | -122.9279
1517.9062 | 122.8317 | -55.4489 | 67.2592 | -0.17899 | 0.0042982 | 0.0034544 | 0.0066779 | -0.0030484 | -0.0013609 | 0.0010617 | -55.4718 | 67.218 | -55.7465 | 67.3691 | 65.7806 | 0.54474 | -3.2776 | -1.268 | 67.2501 | -55.7419 | -0.29755 | -0.041198 | -0.022888 | 122.818 | -1.4786 | -0.29297 | -0.009155 | 0.27466 | 52.1713 | 54.1809 | 121.2296 | 122.6669 | -0.022888 | 122.699 | 55.9937 | -0.29297 | 122.6669 | -0.022888 | 55.9937 | 121.2296 | 122.699 | -123.0057 | -123.0011
1518.9688 | 122.9324 | -53.2791 | 69.3695 | -0.20187 | 2.5564e-05 | -0.00039102 | 0.0032599 | -0.0024076 | -0.0022153 | 0.0042661 | -53.3936 | 69.3558 | -53.5446 | 69.5709 | 67.8589 | 1.0483 | -2.7374 | -0.53558 | 69.342 | -53.5858 | -0.2655 | -0.013733 | -0.11444 | 122.85 | -1.5106 | -0.3067 | -0.027466 | 0.15106 | 50.5417 | 52.7435 | 121.138 | 122.6349 | -0.11444 | 122.6212 | 54.3274 | -0.3067 | 122.6349 | -0.11444 | 54.3274 | 121.138 | 122.6212 | -122.9141 | -122.9553
1519.9062 | 122.8363 | -51.709 | 70.9625 | -0.14847 | 0.0042982 | 0.0055906 | 0.0066779 | -0.0041166 | -0.0024289 | 0.0021299 | -51.7319 | 70.9305 | -52.0477 | 71.077 | 69.4107 | 1.2909 | -2.4673 | -0.39368 | 70.9442 | -52.0432 | -0.33874 | -0.032043 | -0.022889 | 122.7859 | -1.5518 | -0.33417 | -0.01831 | 0.31586 | 49.2416 | 51.3153 | 121.1197 | 122.6395 | -0.022889 | 122.6532 | 52.9999 | -0.33417 | 122.6395 | -0.022889 | 52.9999 | 121.1197 | 122.6532 | -123.0103 | -123.0057
1520.9688 | 122.7356 | -51.4069 | 71.228 | 0.17197 | 0.0055798 | 0.0075132 | 0.0071051 | -0.00027139 | -7.9062e-05 | 0.0044797 | -51.5442 | 71.2234 | -51.7822 | 71.3104 | 69.516 | 0.87891 | -2.5681 | -0.10986 | 71.2738 | -51.741 | -0.37537 | -0.004577 | -0.13733 | 122.7173 | -1.712 | -0.33417 | 0.045777 | 0.23804 | 48.8388 | 51.297 | 120.9229 | 122.6303 | -0.13733 | 122.6807 | 52.2858 | -0.33417 | 122.6303 | -0.13733 | 52.2858 | 120.9229 | 122.6807 | -123.0103 | -122.9691
1521.9062 | 122.7997 | -50.7523 | 71.8918 | -0.29343 | 0.0023756 | 0.005377 | 0.0002691 | -0.0013394 | 0.00034814 | 0.0034115 | -50.798 | 71.8872 | -51.0452 | 72.0245 | 70.3766 | 1.4877 | -2.4948 | -0.40283 | 71.9193 | -51.0498 | -0.29297 | -0.004578 | -0.045777 | 122.7768 | -1.5152 | -0.29755 | 0.027465 | 0.24719 | 48.2574 | 50.3494 | 121.1288 | 122.6395 | -0.045777 | 122.6715 | 52.24 | -0.29755 | 122.6395 | -0.045777 | 52.24 | 121.1288 | 122.6715 | -122.937 | -122.9416
1522.9688 | 122.8363 | -50.5554 | 72.1024 | -0.10269 | 0.0038708 | 0.0043088 | 0.0077459 | -0.0034756 | -0.0017881 | 0.0019163 | -50.6332 | 72.0795 | -50.9308 | 72.2488 | 70.4956 | 1.7578 | -2.2797 | -0.30212 | 72.0886 | -50.9079 | -0.37537 | -0.022888 | -0.07782 | 122.8043 | -1.6068 | -0.35248 | -0.013733 | 0.29755 | 48.2758 | 50.2533 | 121.051 | 122.6349 | -0.07782 | 122.644 | 52.3132 | -0.35248 | 122.6349 | -0.07782 | 52.3132 | 121.051 | 122.644 | -123.0331 | -123.0103
1523.9062 | 122.9324 | -50.061 | 72.5739 | 2.2701 | 0.002162 | 0.00046358 | -0.0031489 | -0.0047574 | -0.00071986 | 0.0051205 | -50.1801 | 72.4731 | -50.3769 | 72.7661 | 71.1044 | 1.7349 | -2.3529 | -0.027466 | 72.5647 | -50.3448 | -0.31586 | -0.10071 | -0.11902 | 122.8271 | -1.4694 | -0.28381 | -0.009156 | 0.19684 | 47.7081 | 50.0336 | 121.1655 | 122.5342 | -0.11902 | 122.6257 | 51.796 | -0.28381 | 122.5342 | -0.11902 | 51.796 | 121.1655 | 122.6257 | -122.9507 | -122.9187
1524.9688 | 122.8729 | -50.9033 | 71.7178 | -0.034027 | 0.0010938 | 0.0045224 | -0.0054987 | -0.003262 | 0.0026981 | 0.0036253 | -50.9537 | 71.7087 | -51.1826 | 71.8826 | 70.253 | 1.4603 | -2.6459 | -0.36621 | 71.727 | -51.1917 | -0.27924 | -0.009155 | -0.050354 | 122.7859 | -1.4648 | -0.28839 | 0.009156 | 0.22888 | 48.2574 | 50.5371 | 121.1563 | 122.612 | -0.050354 | 122.6303 | 52.3636 | -0.28839 | 122.612 | -0.050354 | 52.3636 | 121.1563 | 122.6303 | -122.9004 | -122.9095
1525.9062 | 122.9141 | -50.7248 | 71.8781 | -0.34683 | 2.5564e-05 | 0.00046358 | 0.0017645 | -0.0071072 | -0.00050626 | 0.0046933 | -50.7614 | 71.8277 | -51.0452 | 72.084 | 70.3629 | 1.4969 | -2.7237 | -0.11902 | 71.8506 | -51.0452 | -0.32043 | -0.050354 | -0.036622 | 122.8088 | -1.5152 | -0.32043 | -0.027466 | 0.28381 | 48.0011 | 50.6058 | 121.0876 | 122.5525 | -0.036622 | 122.5754 | 52.2217 | -0.32043 | 122.5525 | -0.036622 | 52.2217 | 121.0876 | 122.5754 | -122.9233 | -122.9233
1526.9688 | 122.8912 | -50.2853 | 72.3267 | -0.3392 | 0.00045296 | 0.006445 | -0.0001581 | -0.0056118 | -0.00029266 | 0.0027707 | -50.4181 | 72.2717 | -50.6104 | 72.4915 | 70.7794 | 1.4465 | -2.6962 | -0.045776 | 72.3175 | -50.5966 | -0.32501 | -0.054931 | -0.13275 | 122.7768 | -1.5472 | -0.31128 | -0.009155 | 0.19226 | 47.5891 | 50.2396 | 121.0648 | 122.5571 | -0.13275 | 122.6028 | 51.7319 | -0.31128 | 122.5571 | -0.13275 | 51.7319 | 121.0648 | 122.6028 | -122.937 | -122.9233
1527.9062 | 122.8088 | -50.7294 | 71.9604 | -0.27817 | 0.0023756 | 0.0038816 | 0.0077459 | -0.0051846 | -0.00071986 | 0.0038389 | -50.9125 | 71.9055 | -51.0406 | 72.0337 | 70.2301 | 1.4328 | -2.2247 | -0.23804 | 71.9238 | -51.0086 | -0.31128 | -0.054931 | -0.18311 | 122.7631 | -1.7303 | -0.27924 | -0.036621 | 0.12817 | 48.5046 | 50.4913 | 120.9595 | 122.6349 | -0.18311 | 122.6532 | 52.1622 | -0.27924 | 122.6349 | -0.18311 | 52.1622 | 120.9595 | 122.6532 | -123.0011 | -122.9691
1528.9688 | 122.905 | -50.7477 | 71.9101 | -0.026398 | 0.002162 | 0.0021726 | 0.0011237 | -0.0053982 | -0.0017881 | 0.0046933 | -50.798 | 71.8552 | -51.0178 | 72.084 | 70.3308 | 1.4008 | -2.5635 | -0.20142 | 71.8918 | -51.0269 | -0.27008 | -0.054931 | -0.050354 | 122.8317 | -1.5793 | -0.27924 | -0.01831 | 0.21973 | 48.1842 | 50.5463 | 121.0785 | 122.6028 | -0.050354 | 122.6395 | 52.1484 | -0.27924 | 122.6028 | -0.050354 | 52.1484 | 121.0785 | 122.6395 | -122.9279 | -122.937
1529.9062 | 122.818 | -50.766 | 71.9147 | -0.24002 | 0.0025892 | -0.0012454 | 0.0043281 | -0.0053982 | -0.0017881 | 0.0038389 | -50.8163 | 71.8643 | -51.0727 | 72.0245 | 70.253 | 1.2955 | -2.7374 | -0.28381 | 71.9009 | -51.0361 | -0.3067 | -0.050354 | -0.050354 | 122.7905 | -1.6617 | -0.27008 | -0.013733 | 0.25635 | 48.0286 | 50.4822 | 121.019 | 122.6303 | -0.050354 | 122.6669 | 52.0615 | -0.27008 | 122.6303 | -0.050354 | 52.0615 | 121.019 | 122.6669 | -122.9874 | -122.9507
1530.9688 | 122.7905 | -50.3906 | 72.2717 | -0.18662 | 0.0034436 | 0.003027 | 0.0058233 | -0.0051846 | -0.0017881 | 0.0036253 | -50.473 | 72.2488 | -50.6927 | 72.4777 | 70.903 | 1.6251 | -2.7008 | -0.48981 | 72.2946 | -50.679 | -0.30212 | -0.022889 | -0.082397 | 122.8683 | -1.3687 | -0.28839 | 0.022888 | 0.21973 | 47.6898 | 49.9008 | 121.2936 | 122.6395 | -0.082397 | 122.6852 | 52.0157 | -0.28839 | 122.6395 | -0.082397 | 52.0157 | 121.2936 | 122.6852 | -122.9645 | -122.9507
1531.9062 | 122.905 | -50.0473 | 72.6013 | 0.019379 | 0.0028028 | -0.00017722 | 0.0009101 | -0.0062528 | -0.00093346 | 0.0042661 | -50.1205 | 72.496 | -50.3769 | 72.7753 | 71.022 | 1.6251 | -2.2659 | 0.082397 | 72.5876 | -50.3311 | -0.32959 | -0.10529 | -0.073242 | 122.8226 | -1.5793 | -0.28381 | -0.013733 | 0.25635 | 47.7814 | 50.1297 | 121.0693 | 122.5433 | -0.073242 | 122.6349 | 51.6724 | -0.28381 | 122.5433 | -0.073242 | 51.6724 | 121.0693 | 122.6349 | -122.9782 | -122.9324
1532.9844 | 122.8088 | -49.7406 | 72.9538 | 0.072784 | 0.004939 | 0.0072996 | 0.010096 | -0.0045438 | -0.00071986 | 0.0057615 | -49.7681 | 72.9584 | -50.0107 | 73.0453 | 71.2601 | 1.3687 | -2.3575 | 0.041199 | 72.9218 | -50.061 | -0.27008 | 0.004578 | -0.027465 | 122.7859 | -1.6937 | -0.32043 | -0.032043 | 0.24262 | 47.3831 | 49.7818 | 121.0007 | 122.699 | -0.027465 | 122.6624 | 51.1093 | -0.32043 | 122.699 | -0.027465 | 51.1093 | 121.0007 | 122.6624 | -122.9645 | -123.0148
1533.9062 | 122.9187 | -50.3265 | 72.2946 | -0.049286 | 0.0010938 | 0.004736 | -0.0018671 | -0.0045438 | 0.00077554 | 0.0046933 | -50.3998 | 72.2443 | -50.6561 | 72.5143 | 70.7565 | 1.3458 | -2.6642 | -0.15564 | 72.2855 | -50.5875 | -0.32959 | -0.050354 | -0.073242 | 122.8409 | -1.5381 | -0.26093 | -0.009156 | 0.25635 | 47.6624 | 50.1709 | 121.0831 | 122.5708 | -0.073242 | 122.612 | 51.6724 | -0.26093 | 122.5708 | -0.073242 | 51.6724 | 121.0831 | 122.612 | -122.9507 | -122.8821
1534.9531 | 99.5773 | -71.7682 | 50.7889 | 0.11856 | 0.00088016 | 0.003027 | 0.0004827 | -0.0068936 | 0.00098914 | -0.0019289 | -71.7728 | 50.7385 | -72.1161 | 50.9903 | 49.6033 | -2.1881 | -7.3563 | -3.7903 | 50.7935 | -72.1207 | -0.3479 | -0.050354 | -0.004578 | 122.7585 | -1.1856 | -0.35248 | 0.004578 | 0.34332 | 64.4119 | 67.9779 | 121.3715 | 122.5067 | -0.004578 | 122.5616 | 69.5801 | -0.35248 | 122.5067 | -0.004578 | 69.5801 | 121.3715 | 122.5616 | -122.905 | -122.9095
1535.9062 | 122.9507 | -49.9924 | 72.6471 | -0.24002 | 0.0034436 | 0.0023862 | 0.0032599 | -0.0079618 | -0.00071986 | 0.0049069 | -49.9878 | 72.5967 | -50.267 | 72.9034 | 71.1136 | 1.712 | -2.4628 | 0.16479 | 72.6013 | -50.2899 | -0.27466 | -0.050354 | 0.004578 | 122.8958 | -1.5335 | -0.29755 | -0.045777 | 0.27924 | 47.5296 | 50.1572 | 121.106 | 122.5891 | 0.004578 | 122.5937 | 51.7044 | -0.29755 | 122.5891 | 0.004578 | 51.7044 | 121.106 | 122.5937 | -122.9141 | -122.937
1536.9531 | 122.8729 | -50.061 | 72.551 | 0.11093 | 0.0013074 | 0.0017454 | 0.0019781 | -0.0062528 | -0.00029266 | 0.0040525 | -50.1572 | 72.4731 | -50.3998 | 72.7661 | 70.9625 | 1.7441 | -2.623 | -0.10529 | 72.5235 | -50.3815 | -0.33875 | -0.077819 | -0.096131 | 122.8271 | -1.5884 | -0.32044 | -0.027465 | 0.24261 | 47.438 | 49.9557 | 121.0236 | 122.5342 | -0.096131 | 122.5845 | 51.8051 | -0.32044 | 122.5342 | -0.096131 | 51.8051 | 121.0236 | 122.5845 | -122.9507 | -122.9324
1537.9062 | 122.8363 | -71.8185 | 50.7614 | -0.064545 | 0.0040846 | 0.0025998 | 0.0066779 | -0.0068936 | -0.0037107 | -0.0042789 | -71.7957 | 50.7294 | -72.2351 | 50.9171 | 49.585 | -2.1057 | -7.1732 | -3.7811 | 50.7751 | -72.1756 | -0.41657 | -0.032044 | 0.022888 | 122.7356 | -1.1765 | -0.35706 | 0.013732 | 0.43945 | 64.6454 | 68.0374 | 121.4035 | 122.5479 | 0.022888 | 122.5937 | 69.7128 | -0.35706 | 122.5479 | 0.022888 | 69.7128 | 121.4035 | 122.5937 | -122.9965 | -122.937
1538.9531 | 122.8821 | -72.8531 | 49.7406 | 0.1033 | 0.001521 | 0.0023862 | -0.0001581 | -0.0028348 | -0.0015745 | -0.0038515 | -72.8439 | 49.6582 | -73.1873 | 49.9283 | 48.5962 | -2.0508 | -7.6721 | -4.0695 | 49.7589 | -73.114 | -0.33417 | -0.082398 | 0.009155 | 122.7814 | -1.1444 | -0.26093 | 0.01831 | 0.34332 | 65.181 | 68.7836 | 121.4493 | 122.5113 | 0.009155 | 122.612 | 70.8023 | -0.26093 | 122.5113 | 0.009155 | 70.8023 | 121.4493 | 122.612 | -122.9279 | -122.8546
1539.9062 | 122.8821 | -73.7732 | 48.8525 | -0.041657 | 0.00066656 | 0.0045224 | 0.0006965 | -0.0062528 | -7.9062e-05 | -0.0036379 | -73.7183 | 48.7473 | -74.0845 | 49.0082 | 47.7219 | -2.4261 | -7.9697 | -4.1245 | 48.7793 | -74.0753 | -0.31128 | -0.10529 | 0.054931 | 122.7814 | -1.1307 | -0.30212 | -0.073242 | 0.36621 | 65.8035 | 69.6487 | 121.4951 | 122.5204 | 0.054931 | 122.5525 | 71.347 | -0.30212 | 122.5204 | 0.054931 | 71.347 | 121.4951 | 122.5525 | -122.937 | -122.9279
1540.9688 | 122.9004 | -74.7391 | 47.8409 | 0.21774 | 0.0030164 | 0.003027 | 0.0011237 | -0.0060392 | -0.00029266 | -0.0038515 | -74.6338 | 47.8363 | -75.0229 | 48.0331 | 46.7606 | -2.5269 | -8.2626 | -4.5044 | 47.8683 | -75.032 | -0.28381 | -0.004577 | 0.10529 | 122.7722 | -1.0803 | -0.29297 | 0.027466 | 0.3891 | 66.4764 | 70.2347 | 121.4996 | 122.5754 | 0.10529 | 122.6074 | 72.2122 | -0.29297 | 122.5754 | 0.10529 | 72.2122 | 121.4996 | 122.6074 | -122.8638 | -122.8729
1541.9062 | 122.8912 | -75.6226 | 46.9849 | 0.17197 | 0.00088016 | 0.0045224 | 0.0021917 | -0.0068936 | 0.00013454 | -0.0040653 | -75.5493 | 46.9162 | -75.9476 | 47.1405 | 45.8633 | -2.298 | -8.4229 | -4.715 | 46.9711 | -75.9338 | -0.32501 | -0.068664 | 0.073243 | 122.7631 | -1.1215 | -0.31128 | -0.013733 | 0.39825 | 67.1997 | 70.9076 | 121.4859 | 122.5388 | 0.073243 | 122.5937 | 73.3246 | -0.31128 | 122.5388 | 0.073243 | 73.3246 | 121.4859 | 122.5937 | -122.9324 | -122.9187
1542.9688 | 122.9279 | -76.8265 | 45.7626 | -0.095062 | 0.001521 | -0.0010318 | 0.0004827 | -0.0079618 | -0.0032835 | -0.0034243 | -76.7303 | 45.7031 | -77.1378 | 45.9641 | 44.7372 | -2.2568 | -8.9447 | -5.0125 | 45.7443 | -77.1515 | -0.31128 | -0.059509 | 0.09613 | 122.7905 | -1.0254 | -0.32501 | -0.01831 | 0.40741 | 67.8818 | 71.814 | 121.5637 | 122.5296 | 0.09613 | 122.5708 | 74.5697 | -0.32501 | 122.5296 | 0.09613 | 74.5697 | 121.5637 | 122.5708 | -122.9004 | -122.9141
1543.9062 | 122.9095 | -76.8311 | 45.7718 | 0.18723 | 0.001521 | 0.0060178 | 0.0009101 | -0.0047574 | -0.0013609 | -0.0025699 | -76.8997 | 45.5246 | -77.3163 | 45.9778 | 44.7327 | -2.1698 | -8.9996 | -5.04 | 45.7718 | -77.1057 | -0.48523 | -0.24719 | -0.068664 | 122.8088 | -1.0391 | -0.27466 | 0 | 0.41656 | 67.8314 | 71.7911 | 121.5637 | 122.3557 | -0.068664 | 122.6028 | 74.6613 | -0.27466 | 122.3557 | -0.068664 | 74.6613 | 121.5637 | 122.6028 | -123.0881 | -122.8775
1544.9531 | 122.8867 | -77.0691 | 45.5658 | 0.18723 | 0.0047254 | 0.0058042 | 0.0068915 | -0.004971 | -0.0017881 | -0.0027835 | -77.0416 | 45.488 | -77.4445 | 45.6894 | 44.4168 | -2.1194 | -8.6609 | -5.04 | 45.5521 | -77.3849 | -0.37537 | -0.07782 | 0.027466 | 122.7585 | -1.149 | -0.31586 | -0.013733 | 0.40283 | 68.4082 | 72.0291 | 121.4859 | 122.5571 | 0.027466 | 122.6212 | 74.9496 | -0.31586 | 122.5571 | 0.027466 | 74.9496 | 121.4859 | 122.6212 | -123.0103 | -122.9507
1545.9062 | 122.818 | -78.0258 | 44.5679 | 0.11856 | 0.001521 | 0.0017454 | 0.0009101 | -0.0051846 | -0.0022153 | -0.0029971 | -77.9617 | 44.5404 | -78.3142 | 44.751 | 43.5287 | -2.2568 | -9.0134 | -5.3192 | 44.5633 | -78.3417 | -0.28839 | -0.027466 | 0.064087 | 122.7768 | -1.0391 | -0.31586 | -0.004578 | 0.35248 | 69.0125 | 72.7066 | 121.5546 | 122.5662 | 0.064087 | 122.5891 | 75.769 | -0.31586 | 122.5662 | 0.064087 | 75.769 | 121.5546 | 122.5891 | -122.8821 | -122.9095
1546.9688 | 122.8088 | -78.1815 | 44.4534 | 0.072784 | 0.0028028 | 0.0051632 | 0.011164 | -0.003903 | -0.0013609 | -0.0025699 | -78.1036 | 44.4351 | -78.5202 | 44.5358 | 43.309 | -2.8839 | -9.1507 | -5.3696 | 44.4351 | -78.5385 | -0.33874 | -0.01831 | 0.07782 | 122.7173 | -1.1444 | -0.35705 | -0.01831 | 0.41656 | 69.0308 | 72.8119 | 121.4905 | 122.6166 | 0.07782 | 122.6166 | 75.2975 | -0.35705 | 122.6166 | 0.07782 | 75.2975 | 121.4905 | 122.6166 | -122.9736 | -122.9919
1547.9062 | 122.8043 | -77.6596 | 44.989 | -0.22476 | 0.0036572 | -0.00017722 | 0.0032599 | -0.003262 | -0.0026425 | -0.0027835 | -77.4765 | 44.9844 | -77.9617 | 45.0348 | 43.8492 | -2.4399 | -8.7158 | -5.2643 | 45.0256 | -77.9572 | -0.30212 | -0.004578 | 0.18311 | 122.6944 | -1.1398 | -0.29755 | 0.036621 | 0.48523 | 68.9438 | 72.3953 | 121.5088 | 122.644 | 0.18311 | 122.6852 | 75.2197 | -0.29755 | 122.644 | 0.18311 | 75.2197 | 121.5088 | 122.6852 | -122.9507 | -122.9462
1548.9688 | 122.9233 | -77.98 | 44.6091 | 0.21774 | 0.0030164 | 0.0068722 | 0.0021917 | -0.0013394 | -0.00029266 | -0.0036379 | -77.8885 | 44.5084 | -78.3279 | 44.7922 | 43.5654 | -2.0325 | -9.0958 | -5.4291 | 44.577 | -78.2776 | -0.3479 | -0.10071 | 0.091553 | 122.7722 | -1.0437 | -0.29755 | -0.032044 | 0.43945 | 68.8843 | 72.551 | 121.5454 | 122.4884 | 0.091553 | 122.5571 | 75.9476 | -0.29755 | 122.4884 | 0.091553 | 75.9476 | 121.5454 | 122.5571 | -122.937 | -122.8867
1549.9062 | 122.9004 | -78.1265 | 44.4534 | -0.24002 | 0.002162 | 0.0015316 | -0.0003717 | -0.0060392 | -0.0026425 | -0.0051333 | -78.1769 | 44.3436 | -78.5294 | 44.577 | 43.3914 | -2.0508 | -9.1415 | -5.9006 | 44.4077 | -78.4561 | -0.40283 | -0.10986 | -0.050354 | 122.7036 | -1.062 | -0.32959 | -0.045776 | 0.35248 | 68.985 | 72.226 | 121.5179 | 122.4701 | -0.050354 | 122.5342 | 76.0757 | -0.32959 | 122.4701 | -0.050354 | 76.0757 | 121.5179 | 122.5342 | -122.9828 | -122.9095
1550.9688 | 122.8271 | -78.4149 | 44.2612 | -0.21713 | 0.0025892 | 0.0066586 | 0.0032599 | -0.0043302 | 0.00013454 | -0.0019289 | -78.3646 | 44.2062 | -78.7262 | 44.3573 | 43.1625 | -2.1835 | -9.1644 | -6.1249 | 44.2474 | -78.7216 | -0.31128 | -0.054931 | 0.050354 | 122.7722 | -1.0986 | -0.3067 | -0.013732 | 0.36163 | 69.2505 | 72.29 | 121.5775 | 122.6212 | 0.050354 | 122.6624 | 76.2314 | -0.3067 | 122.6212 | 0.050354 | 76.2314 | 121.5775 | 122.6624 | -122.9874 | -122.9828
1551.9062 | 122.9187 | -79.3854 | 43.2037 | 0.034637 | 0.0047254 | 0.006445 | 0.0068915 | -0.0034756 | -0.0013609 | -0.0015017 | -79.335 | 43.1076 | -79.7699 | 43.4143 | 42.2104 | -2.3346 | -9.4025 | -6.7703 | 43.222 | -79.7058 | -0.38452 | -0.09613 | 0.050354 | 122.7997 | -0.99335 | -0.32044 | 0.018311 | 0.43488 | 69.9829 | 72.6151 | 121.5958 | 122.493 | 0.050354 | 122.6074 | 77.0508 | -0.32044 | 122.493 | 0.050354 | 77.0508 | 121.5958 | 122.6074 | -122.9736 | -122.9095
1552.9688 | 122.9324 | -79.2847 | 43.309 | -0.0035098 | 0.00023916 | 0.0051632 | 0.0015509 | -0.0060392 | -0.0026425 | -0.0047061 | -79.2114 | 43.222 | -79.6143 | 43.4601 | 42.2653 | -1.9089 | -9.2926 | -6.0242 | 43.2541 | -79.66 | -0.32959 | -0.086975 | 0.073242 | 122.7448 | -1.0437 | -0.37537 | -0.054932 | 0.40283 | 69.9921 | 73.2605 | 121.55 | 122.5067 | 0.073242 | 122.5388 | 77.3758 | -0.37537 | 122.5067 | 0.073242 | 77.3758 | 121.55 | 122.5388 | -122.9233 | -122.9691
1553.9062 | 122.8958 | -79.1794 | 43.4097 | 0.049896 | 0.002162 | 0.003027 | 0.0009101 | -0.0019802 | -7.9062e-05 | -0.0015017 | -79.1611 | 43.3411 | -79.5319 | 43.5287 | 42.2379 | -2.2568 | -9.0408 | -6.5872 | 43.3868 | -79.5135 | -0.35248 | -0.068665 | 0.01831 | 122.7081 | -1.1719 | -0.33417 | -0.022888 | 0.37079 | 70.1385 | 72.5922 | 121.4172 | 122.5204 | 0.01831 | 122.5662 | 76.9226 | -0.33417 | 122.5204 | 0.01831 | 76.9226 | 121.4172 | 122.5662 | -122.9416 | -122.9233
1554.9688 | 122.8958 | -79.5319 | 43.1076 | 0.065155 | -0.00082884 | 0.0023862 | 0.0002691 | -0.008389 | -0.00029266 | -0.0029971 | -79.509 | 43.0206 | -79.8752 | 43.2083 | 41.9815 | -2.1973 | -8.963 | -6.5826 | 43.0573 | -79.8706 | -0.34332 | -0.086975 | 0.022888 | 122.7402 | -1.1261 | -0.33875 | -0.050354 | 0.36621 | 70.5688 | 72.9492 | 121.5134 | 122.5525 | 0.022888 | 122.5891 | 77.3346 | -0.33875 | 122.5525 | 0.022888 | 77.3346 | 121.5134 | 122.5891 | -122.9828 | -122.9782
1555.9062 | 122.8729 | -80.2734 | 42.3523 | -0.19424 | 0.001521 | 0.0055906 | 0.0036871 | -0.0056118 | 0.00013454 | -0.0036379 | -80.1773 | 42.2974 | -80.5756 | 42.4942 | 41.2354 | -1.7624 | -9.1599 | -6.7062 | 42.3065 | -80.6213 | -0.30213 | -0.054932 | 0.09613 | 122.7676 | -1.1169 | -0.3479 | -0.045776 | 0.39826 | 71.1136 | 73.5672 | 121.5088 | 122.5708 | 0.09613 | 122.58 | 78.511 | -0.3479 | 122.5708 | 0.09613 | 78.511 | 121.5088 | 122.58 | -122.9279 | -122.9736
1556.9688 | 122.8867 | -79.3762 | 43.2678 | -0.026398 | 2.5564e-05 | 0.0028134 | 0.0019781 | -0.0047574 | 0.00013454 | -0.0064151 | -79.3488 | 43.1717 | -79.7104 | 43.515 | 42.2333 | -1.6754 | -9.1507 | -6.5964 | 43.2083 | -79.7012 | -0.33417 | -0.09613 | 0.027466 | 122.8912 | -1.0345 | -0.32501 | -0.059509 | 0.36163 | 70.2255 | 72.7798 | 121.6095 | 122.5479 | 0.027466 | 122.5845 | 77.7008 | -0.32501 | 122.5479 | 0.027466 | 77.7008 | 121.6095 | 122.5845 | -122.9782 | -122.9691
1557.9062 | 122.9095 | -78.36 | 44.2795 | -0.0035098 | 0.0025892 | 0.0043088 | 0.0024053 | -0.0047574 | 0.00034814 | -0.0012881 | -78.2639 | 44.2749 | -78.6255 | 44.4809 | 43.2037 | -1.4969 | -8.0704 | -6.2027 | 44.2703 | -78.6667 | -0.2655 | -0.004578 | 0.09613 | 122.8409 | -1.0757 | -0.3067 | -0.009155 | 0.36163 | 70.2896 | 72.1573 | 121.5637 | 122.6349 | 0.09613 | 122.6303 | 76.8631 | -0.3067 | 122.6349 | 0.09613 | 76.8631 | 121.5637 | 122.6303 | -122.905 | -122.9462
1558.9688 | 122.8638 | -79.4586 | 43.1854 | 0.19485 | 0.0047254 | 0.0096494 | 0.010737 | -0.0043302 | -0.0013609 | -0.0027835 | -79.4266 | 43.1534 | -79.8386 | 43.2587 | 41.9861 | -1.9318 | -9.2056 | -5.5206 | 43.1305 | -79.8248 | -0.37994 | -0.032044 | 0.032043 | 122.7173 | -1.1993 | -0.36621 | -0.054932 | 0.41199 | 70.253 | 73.938 | 121.4447 | 122.612 | 0.032043 | 122.5891 | 77.5269 | -0.36621 | 122.612 | 0.032043 | 77.5269 | 121.4447 | 122.5891 | -123.024 | -123.0103
1559.9062 | 122.8043 | -78.9093 | 43.7531 | 0.22537 | 0.0047254 | 0.0079404 | 0.0079595 | -0.0019802 | -0.0013609 | -0.0027835 | -78.7949 | 43.8034 | -79.1977 | 43.8492 | 42.5995 | -2.1332 | -9.1599 | -5.8868 | 43.7576 | -79.2526 | -0.28839 | 0.050354 | 0.11444 | 122.7585 | -1.1536 | -0.34332 | 0.004577 | 0.40283 | 69.7495 | 73.0225 | 121.5088 | 122.7127 | 0.11444 | 122.6669 | 76.7761 | -0.34332 | 122.7127 | 0.11444 | 76.7761 | 121.5088 | 122.6669 | -122.9507 | -123.0057
1560.9688 | 122.9462 | -79.6555 | 42.8833 | 0.18723 | 0.0038708 | 0.0094358 | 0.0034735 | -0.0030484 | 0.0024845 | -0.0042789 | -79.6646 | 42.7734 | -80.0995 | 43.2037 | 41.9632 | -2.2156 | -9.4894 | -5.7541 | 42.984 | -79.9667 | -0.44403 | -0.10986 | -0.009155 | 122.8592 | -0.9201 | -0.31128 | 0.10071 | 0.43487 | 70.166 | 73.9014 | 121.6187 | 122.4289 | -0.009155 | 122.6395 | 77.4399 | -0.31128 | 122.4289 | -0.009155 | 77.4399 | 121.6187 | 122.6395 | -122.9828 | -122.85
1561.9062 | 122.8546 | -60.7681 | 61.9125 | 0.13382 | 0.0057934 | 0.004736 | 0.0094549 | -0.00069859 | -0.0015745 | 0.0081113 | -60.8093 | 61.9217 | -61.0886 | 61.8118 | 60.3149 | 0.41199 | -4.9622 | -3.3325 | 61.9354 | -61.0794 | -0.32044 | 0.009155 | -0.041199 | 122.58 | -1.5976 | -0.31128 | 0.022888 | 0.27924 | 55.806 | 57.4356 | 121.0831 | 122.6898 | -0.041199 | 122.7036 | 61.1801 | -0.31128 | 122.6898 | -0.041199 | 61.1801 | 121.0831 | 122.7036 | -123.0011 | -122.9919
1562.9688 | 122.9416 | -55.481 | 67.1585 | -0.056915 | 0.0028028 | 0.003668 | -0.0001581 | -0.0043302 | -0.00029266 | 0.0044797 | -55.4672 | 67.1585 | -55.7831 | 67.3462 | 65.6891 | 1.3 | -4.0283 | -1.68 | 67.0853 | -55.8014 | -0.30212 | 0 | 0.013733 | 122.8271 | -1.4694 | -0.32044 | -0.073242 | 0.31586 | 51.4526 | 53.801 | 121.17 | 122.6395 | 0.013733 | 122.5662 | 56.781 | -0.32044 | 122.6395 | 0.013733 | 56.781 | 121.17 | 122.5662 | -122.9416 | -122.9599
1563.9062 | 122.9507 | -54.1946 | 68.4219 | 0.14908 | 0.004939 | 0.0025998 | 0.0086005 | -0.0011258 | -0.00029266 | 0.0055479 | -54.213 | 68.3899 | -54.5334 | 68.6096 | 66.9067 | 1.2497 | -3.7216 | -1.593 | 68.3533 | -54.5334 | -0.33875 | -0.032043 | -0.018311 | 122.8043 | -1.5152 | -0.33875 | -0.068665 | 0.32043 | 50.473 | 52.6016 | 121.1014 | 122.5845 | -0.018311 | 122.5479 | 55.4443 | -0.33875 | 122.5845 | -0.018311 | 55.4443 | 121.1014 | 122.5479 | -122.9553 | -122.9553
1564.9688 | 122.8271 | -53.3295 | 69.3604 | -0.13321 | 0.0055798 | 0.0077268 | 0.0075323 | -0.0028348 | -0.0013609 | 0.0040525 | -53.4027 | 69.3787 | -53.6682 | 69.4382 | 67.6895 | 1.1124 | -3.4653 | -1.474 | 69.3604 | -53.6545 | -0.33875 | 0.01831 | -0.073242 | 122.7676 | -1.6708 | -0.32501 | 0 | 0.2655 | 49.8642 | 51.8555 | 121.019 | 122.7081 | -0.073242 | 122.6898 | 54.4418 | -0.32501 | 122.7081 | -0.073242 | 54.4418 | 121.019 | 122.6898 | -123.0286 | -123.0148
1565.9062 | 122.8867 | -53.3386 | 69.278 | 0.14145 | 0.0038708 | -0.00039102 | -0.0010125 | -0.0024076 | 0.00013454 | 0.0051205 | -53.3615 | 69.2551 | -53.6545 | 69.4611 | 67.7261 | 1.1307 | -3.36 | -1.062 | 69.278 | -53.6499 | -0.31586 | -0.022888 | -0.022888 | 122.7997 | -1.5518 | -0.31128 | 0 | 0.29297 | 49.9786 | 52.2766 | 121.0648 | 122.5937 | -0.022888 | 122.6166 | 54.4693 | -0.31128 | 122.5937 | -0.022888 | 54.4693 | 121.0648 | 122.6166 | -122.9324 | -122.9279
1566.9531 | 122.8271 | -52.9816 | 69.6762 | 0.21011 | 0.0042982 | 0.0021726 | 0.0077459 | -0.0043302 | 0.00013454 | 0.0036253 | -53.0319 | 69.7174 | -53.3157 | 69.7586 | 68.0145 | 1.1307 | -3.3325 | -1.2543 | 69.6167 | -53.3478 | -0.33417 | 0.041199 | -0.050354 | 122.7402 | -1.6617 | -0.36621 | -0.059509 | 0.28381 | 49.649 | 51.7273 | 120.9961 | 122.699 | -0.050354 | 122.5983 | 54.1122 | -0.36621 | 122.699 | -0.050354 | 54.1122 | 120.9961 | 122.5983 | -122.9919 | -123.024
1567.9062 | 122.9233 | -52.0935 | 70.4498 | 0.16434 | 0.004939 | 0.008154 | 0.0053961 | -0.0011258 | -0.00050626 | 0.0034115 | -52.066 | 70.5139 | -52.3911 | 70.7428 | 68.9896 | 1.1902 | -3.2639 | -1.0895 | 70.4819 | -52.4002 | -0.29755 | 0.064087 | 0.027466 | 122.8363 | -1.4603 | -0.3067 | 0.032044 | 0.32501 | 48.8297 | 51.004 | 121.0831 | 122.6074 | 0.027466 | 122.5754 | 53.2837 | -0.3067 | 122.6074 | 0.027466 | 53.2837 | 121.0831 | 122.5754 | -122.8409 | -122.85
1568.9688 | 122.9279 | -51.9333 | 70.6192 | 0.14908 | 0.0028028 | 0.0040952 | 0.0026191 | -0.0028348 | 0.0020571 | 0.0046933 | -51.9699 | 70.6558 | -52.2812 | 70.8664 | 69.0811 | 1.0345 | -3.0716 | -0.84686 | 70.6146 | -52.2949 | -0.3479 | 0.036621 | -0.036621 | 122.7997 | -1.5381 | -0.36163 | -0.004578 | 0.31128 | 48.8617 | 51.0864 | 121.0144 | 122.5891 | -0.036621 | 122.5479 | 52.9678 | -0.36163 | 122.5891 | -0.036621 | 52.9678 | 121.0144 | 122.5479 | -122.9004 | -122.9141
1569.9062 | 122.8088 | -52.2995 | 70.372 | 0.12619 | 0.0055798 | 0.01029 | 0.0088141 | -0.002194 | 0.0014163 | 0.0031979 | -52.5146 | 70.3629 | -52.6291 | 70.5139 | 68.6646 | 0.98877 | -3.0808 | -1.062 | 70.3857 | -52.6566 | -0.32959 | -0.009155 | -0.21515 | 122.8134 | -1.7075 | -0.35705 | 0.013733 | 0.11444 | 49.2188 | 51.2375 | 120.9641 | 122.6624 | -0.21515 | 122.6852 | 53.2883 | -0.35705 | 122.6624 | -0.21515 | 53.2883 | 120.9641 | 122.6852 | -123.0011 | -123.0286
1570.9688 | 122.8546 | -52.0065 | 70.6375 | 0.77469 | 0.0030164 | 0.004736 | 0.0066779 | -0.0030484 | -0.0017881 | 0.0042661 | -52.0386 | 70.6696 | -52.3361 | 70.7336 | 68.985 | 0.63629 | -3.0258 | -0.98877 | 70.6604 | -52.327 | -0.32959 | 0.032044 | -0.032043 | 122.7402 | -1.6525 | -0.32043 | 0.022888 | 0.29755 | 48.9807 | 51.0178 | 120.9915 | 122.6761 | -0.032043 | 122.6669 | 52.6428 | -0.32043 | 122.6761 | -0.032043 | 52.6428 | 120.9915 | 122.6669 | -122.9736 | -122.9645
1571.9062 | 122.8271 | -51.9379 | 70.7291 | 0.14908 | 0.0045118 | 0.009863 | 0.0062507 | -0.0024076 | -0.0017881 | 0.0044797 | -51.9104 | 70.8344 | -52.1667 | 70.8344 | 69.0582 | 1.2543 | -2.7328 | -0.96588 | 70.7382 | -52.2308 | -0.22888 | 0.10529 | 0.027466 | 122.7722 | -1.6708 | -0.29297 | 0.009155 | 0.25635 | 49.205 | 50.972 | 120.9961 | 122.7722 | 0.027466 | 122.6761 | 53.1921 | -0.29297 | 122.7722 | 0.027466 | 53.1921 | 120.9961 | 122.6761 | -122.8958 | -122.9599
1572.9688 | 122.9095 | -51.9241 | 70.697 | 1.057 | 0.00066656 | 0.0038816 | -0.0001581 | -0.0043302 | -0.00050626 | 0.0057615 | -52.0111 | 70.6879 | -52.24 | 70.871 | 69.0948 | 1.0437 | -2.5452 | -0.72327 | 70.6879 | -52.2491 | -0.31586 | -0.009155 | -0.086975 | 122.7951 | -1.6022 | -0.32501 | -0.009155 | 0.22888 | 49.379 | 51.2009 | 121.019 | 122.612 | -0.086975 | 122.612 | 52.9678 | -0.32501 | 122.612 | -0.086975 | 52.9678 | 121.019 | 122.612 | -122.937 | -122.9462
1573.9062 | 122.8409 | -52.0752 | 70.6009 | 0.26352 | 0.004939 | 0.0079404 | 0.0062507 | -0.002194 | 0.00034814 | 0.0040525 | -52.1118 | 70.665 | -52.3499 | 70.6696 | 68.9072 | 1.0757 | -2.5223 | -0.59967 | 70.6009 | -52.3911 | -0.27466 | 0.064087 | -0.036621 | 122.7448 | -1.6937 | -0.31586 | 0 | 0.23804 | 49.5529 | 51.4755 | 120.9824 | 122.7402 | -0.036621 | 122.6761 | 53.1509 | -0.31586 | 122.7402 | -0.036621 | 53.1509 | 120.9824 | 122.6761 | -122.9507 | -122.9919
1574.9844 | 122.8912 | -51.6449 | 70.9717 | 0.14145 | 0.0053662 | 0.0023862 | 0.0002691 | -0.0034756 | 0.0012027 | 0.0023435 | -51.6861 | 70.9946 | -51.9424 | 71.1548 | 69.3878 | 1.1398 | -2.8381 | -0.81024 | 70.9671 | -51.9699 | -0.29755 | 0.022888 | -0.041199 | 122.7997 | -1.5839 | -0.32501 | -0.004578 | 0.25635 | 48.8068 | 50.8347 | 121.0327 | 122.6395 | -0.041199 | 122.612 | 52.7847 | -0.32501 | 122.6395 | -0.041199 | 52.7847 | 121.0327 | 122.612 | -122.9141 | -122.9416
1575.9062 | 122.905 | -51.2878 | 71.3425 | 0.1796 | 0.0053662 | 0.0058042 | 0.0075323 | -0.0017666 | -0.0015745 | 0.0053343 | -51.2924 | 71.402 | -51.59 | 71.5393 | 69.7495 | 1.355 | -2.6825 | -0.32044 | 71.3287 | -51.6174 | -0.30212 | 0.05951 | -0.004577 | 122.8271 | -1.593 | -0.32959 | -0.013733 | 0.29755 | 48.6053 | 50.9674 | 121.0373 | 122.6898 | -0.004577 | 122.6166 | 52.6428 | -0.32959 | 122.6898 | -0.004577 | 52.6428 | 121.0373 | 122.6166 | -122.9324 | -122.9599
1576.9531 | 122.8958 | -51.1551 | 71.4523 | 0.233 | 0.0064344 | 0.0051632 | 0.0049689 | -0.0028348 | -0.0013609 | 0.0031979 | -51.1459 | 71.4615 | -51.4801 | 71.6858 | 69.9097 | 1.2314 | -2.5909 | -0.17853 | 71.4615 | -51.4572 | -0.32501 | 0.009155 | 0.009155 | 122.8409 | -1.5427 | -0.30212 | 0.009155 | 0.33417 | 48.5641 | 50.9766 | 121.0648 | 122.6166 | 0.009155 | 122.6166 | 52.3865 | -0.30212 | 122.6166 | 0.009155 | 52.3865 | 121.0648 | 122.6166 | -122.9324 | -122.9095
1577.9062 | 122.818 | -51.6861 | 70.9534 | 0.50003 | 0.0042982 | 0.0094358 | 0.0071051 | -0.002194 | -0.0015745 | 0.0040525 | -51.7685 | 70.9717 | -52.0569 | 71.0587 | 69.3008 | 1.181 | -2.8107 | -0.62256 | 70.99 | -52.0523 | -0.37079 | 0.018311 | -0.082398 | 122.7448 | -1.6525 | -0.36621 | 0.036621 | 0.28839 | 48.8754 | 51.0635 | 120.9869 | 122.6578 | -0.082398 | 122.6761 | 52.8671 | -0.36621 | 122.6578 | -0.082398 | 52.8671 | 120.9869 | 122.6761 | -123.0103 | -123.0057
1578.9688 | 122.8683 | -51.8738 | 70.7474 | 0.17197 | 0.0025892 | 0.0083676 | 0.0024053 | -0.0026212 | 0.0026981 | 0.0057615 | -51.8784 | 70.7657 | -52.1347 | 70.9305 | 69.2047 | 1.4877 | -3.1998 | -0.44403 | 70.7336 | -52.1759 | -0.26093 | 0.018311 | -0.004578 | 122.8043 | -1.5427 | -0.30212 | -0.013732 | 0.25635 | 48.674 | 51.4297 | 121.0785 | 122.6395 | -0.004578 | 122.6074 | 53.3615 | -0.30212 | 122.6395 | -0.004578 | 53.3615 | 121.0785 | 122.6074 | -122.8821 | -122.9233
1579.9219 | 122.9279 | -51.5808 | 71.0037 | -0.034027 | 0.002162 | 0.0021726 | -0.0012261 | -0.0047574 | -0.0011471 | 0.0055479 | -51.5991 | 71.0083 | -51.8921 | 71.2463 | 69.5251 | 1.7441 | -3.1357 | -0.45776 | 71.0175 | -51.8875 | -0.31128 | 0.004578 | -0.01831 | 122.8271 | -1.4786 | -0.3067 | 0.013733 | 0.29297 | 48.4451 | 51.123 | 121.106 | 122.5891 | -0.01831 | 122.5983 | 53.3249 | -0.3067 | 122.5891 | -0.01831 | 53.3249 | 121.106 | 122.5983 | -122.8958 | -122.8912
1580.9844 | 122.9324 | -51.329 | 71.283 | -0.38498 | 0.0013074 | 3.6382e-05 | -0.0001581 | -0.0058256 | -0.00050626 | 0.0038389 | -51.4206 | 71.2051 | -51.6449 | 71.5347 | 69.7678 | 1.7944 | -2.7283 | -0.27466 | 71.2463 | -51.6449 | -0.31586 | -0.07782 | -0.091552 | 122.8638 | -1.5152 | -0.31586 | -0.036621 | 0.2243 | 48.6008 | 51.0544 | 121.0968 | 122.5342 | -0.091552 | 122.5754 | 53.1235 | -0.31586 | 122.5342 | -0.091552 | 53.1235 | 121.0968 | 122.5754 | -122.9279 | -122.9279
1581.9062 | 122.9004 | -51.2878 | 71.3333 | 0.44662 | 0.0025892 | 0.0075132 | 0.0073187 | -0.0030484 | -0.0013609 | 0.0017027 | -51.2878 | 71.3287 | -51.5854 | 71.5485 | 69.7678 | 1.9043 | -2.8519 | -0.054932 | 71.2738 | -51.5945 | -0.29755 | -0.004578 | 0 | 122.8363 | -1.5656 | -0.3067 | -0.059509 | 0.29755 | 48.436 | 51.2329 | 121.0556 | 122.6166 | 0 | 122.5616 | 53.1921 | -0.3067 | 122.6166 | 0 | 53.1921 | 121.0556 | 122.5616 | -122.9187 | -122.9279
1582.9062 | 122.8592 | -51.59 | 71.0678 | 0.21774 | 0.0053662 | 0.01029 | 0.0047553 | -0.00069859 | -0.00050626 | 0.0034115 | -51.6357 | 71.1044 | -51.9196 | 71.2006 | 69.4107 | 1.8448 | -2.6367 | 0.14191 | 71.0312 | -51.9104 | -0.32959 | 0.036621 | -0.045776 | 122.7905 | -1.6571 | -0.32043 | -0.036621 | 0.28381 | 48.9532 | 51.7319 | 121.0007 | 122.6944 | -0.045776 | 122.6212 | 53.4348 | -0.32043 | 122.6944 | -0.045776 | 53.4348 | 121.0007 | 122.6212 | -122.9874 | -122.9782
1583.9062 | 122.8729 | -51.8234 | 70.7886 | 0.21011 | 0.0045118 | 0.0062314 | 0.0075323 | -0.0043302 | 0.00056194 | 0.0040525 | -51.9424 | 70.8023 | -52.2034 | 70.9351 | 69.1681 | 1.8951 | -2.3529 | 0.14191 | 70.8298 | -52.1896 | -0.37994 | 0.013733 | -0.11902 | 122.7585 | -1.6205 | -0.36621 | 0.041199 | 0.26093 | 49.4705 | 51.9653 | 120.9915 | 122.6257 | -0.11902 | 122.6532 | 53.7186 | -0.36621 | 122.6257 | -0.11902 | 53.7186 | 120.9915 | 122.6532 | -122.9919 | -122.9782
1584.9219 | 122.9233 | -51.8417 | 70.7611 | -0.17899 | 0.0028028 | 0.006445 | -0.0012261 | -0.004971 | 0.00098914 | 0.0059751 | -51.9012 | 70.697 | -52.1988 | 71.1502 | 69.4611 | 2.1698 | -2.8427 | 0.20142 | 70.7108 | -52.1805 | -0.35706 | -0.064087 | -0.059509 | 122.9919 | -1.3 | -0.33875 | -0.050354 | 0.29755 | 48.999 | 52.0432 | 121.3028 | 122.5388 | -0.059509 | 122.5525 | 54.0115 | -0.33875 | 122.5388 | -0.059509 | 54.0115 | 121.3028 | 122.5525 | -122.9599 | -122.9416
1585.9688 | 122.7997 | -51.8555 | 70.8069 | 0.080414 | 0.0055798 | 0.008154 | 0.0083869 | -0.003262 | -0.00050626 | 0.0029843 | -51.86 | 70.8572 | -52.1576 | 70.903 | 69.1269 | 1.7578 | -2.4811 | -0.16022 | 70.7886 | -52.1851 | -0.30212 | 0.050354 | -0.004577 | 122.7585 | -1.68 | -0.32959 | -0.018311 | 0.29755 | 49.3744 | 51.6953 | 120.9824 | 122.7127 | -0.004577 | 122.644 | 53.6133 | -0.32959 | 122.7127 | -0.004577 | 53.6133 | 120.9824 | 122.644 | -122.9645 | -122.9919
1586.9062 | 122.8546 | -51.8875 | 70.7565 | 0.19485 | 0.00323 | 0.008154 | 0.0062507 | -0.0019802 | -0.0011471 | 0.0070431 | -51.9424 | 70.8115 | -52.2079 | 70.8893 | 69.136 | 1.8173 | -2.4948 | -0.09613 | 70.7932 | -52.2171 | -0.32043 | 0.054931 | -0.054932 | 122.7768 | -1.6205 | -0.32959 | 0.036621 | 0.2655 | 49.3927 | 51.7914 | 121.0236 | 122.699 | -0.054932 | 122.6807 | 53.7048 | -0.32959 | 122.699 | -0.054932 | 53.7048 | 121.0236 | 122.6807 | -122.9645 | -122.9736
1587.9531 | 122.9095 | -52.0615 | 70.5505 | 0.15671 | 0.0028028 | 0.0068722 | 0.0009101 | -0.0017666 | 0.0024845 | 0.0055479 | -52.0798 | 70.5505 | -52.3499 | 70.7336 | 68.9667 | 1.8127 | -2.5543 | 0.19226 | 70.5368 | -52.3865 | -0.28839 | 0 | -0.018311 | 122.7951 | -1.5839 | -0.32501 | -0.013733 | 0.27008 | 49.5071 | 52.2537 | 121.0281 | 122.612 | -0.018311 | 122.5983 | 53.8742 | -0.32501 | 122.612 | -0.018311 | 53.8742 | 121.0281 | 122.5983 | -122.9004 | -122.937
1588.9062 | 122.9004 | -51.7731 | 70.8435 | 0.21011 | 0.0034436 | 0.004736 | 0.0053961 | -0.0011258 | -0.0024289 | 0.0042661 | -51.8188 | 70.871 | -52.0706 | 71.0632 | 69.2596 | 1.8906 | -2.3941 | 0.36163 | 70.8618 | -52.0798 | -0.29755 | 0.027466 | -0.045777 | 122.8363 | -1.5839 | -0.3067 | 0.01831 | 0.25177 | 49.379 | 52.1347 | 121.0327 | 122.644 | -0.045777 | 122.6349 | 53.6636 | -0.3067 | 122.644 | -0.045777 | 53.6636 | 121.0327 | 122.6349 | -122.9141 | -122.9233
1589.9844 | 122.9095 | -51.7319 | 70.8755 | -0.12558 | 0.0010938 | 0.003668 | -0.0005853 | -0.004971 | -0.0013609 | 0.00020726 | -51.7456 | 70.8755 | -52.0203 | 71.1548 | 69.4016 | 1.8997 | -2.2842 | 0.46234 | 70.8847 | -52.0798 | -0.28839 | 0 | -0.013732 | 122.8867 | -1.474 | -0.3479 | 0.009156 | 0.27466 | 49.4476 | 52.1942 | 121.1334 | 122.6074 | -0.013732 | 122.6166 | 53.6316 | -0.3479 | 122.6074 | -0.013732 | 53.6316 | 121.1334 | 122.6166 | -122.8958 | -122.9553
1590.9219 | 122.9324 | -51.8143 | 70.7794 | 0.019379 | 0.0017346 | -0.00039102 | -0.0007989 | -0.0034756 | -0.0020017 | 0.0049069 | -51.915 | 70.7336 | -52.1942 | 70.9717 | 69.223 | 1.8127 | -2.3849 | 0.37537 | 70.7703 | -52.1164 | -0.37994 | -0.045776 | -0.10071 | 122.786 | -1.5564 | -0.30212 | -0.009155 | 0.27924 | 49.4293 | 52.1896 | 121.0373 | 122.5479 | -0.10071 | 122.5845 | 53.627 | -0.30212 | 122.5479 | -0.10071 | 53.627 | 121.0373 | 122.5845 | -122.9736 | -122.8958
1591.9688 | 122.8088 | -52.4734 | 70.2347 | 0.088043 | 0.0047254 | 0.0017454 | 0.011377 | -0.0051846 | -0.00093346 | 0.0040525 | -52.4963 | 70.2209 | -52.771 | 70.3217 | 68.6096 | 1.5976 | -2.5681 | -0.068665 | 70.2301 | -52.803 | -0.29755 | -0.013733 | -0.022888 | 122.7951 | -1.6251 | -0.32959 | -0.004577 | 0.27466 | 49.9054 | 52.4048 | 121.0831 | 122.6944 | -0.022888 | 122.7036 | 54.071 | -0.32959 | 122.6944 | -0.022888 | 54.071 | 121.0831 | 122.7036 | -123.0057 | -123.0377
1592.9062 | 122.8638 | -52.4002 | 70.2484 | 0.21011 | 0.0038708 | 0.004736 | 0.0071051 | -0.0036892 | -0.0015745 | 0.0036253 | -52.4185 | 70.2988 | -52.7023 | 70.3995 | 68.66 | 1.5976 | -2.3666 | -0.07782 | 70.2759 | -52.7298 | -0.30212 | 0.050354 | -0.01831 | 122.7997 | -1.5884 | -0.32959 | 0.027466 | 0.28381 | 50.0336 | 52.3224 | 121.0602 | 122.699 | -0.01831 | 122.6761 | 53.9978 | -0.32959 | 122.699 | -0.01831 | 53.9978 | 121.0602 | 122.6761 | -122.9507 | -122.9782
1593.9062 | 122.8271 | -52.8214 | 69.7998 | 0.19485 | 0.0038708 | 0.0094358 | 0.0077459 | -0.001553 | -0.0013609 | 0.0042661 | -52.8717 | 69.873 | -53.1372 | 69.9554 | 68.1702 | 1.6342 | -2.5131 | -0.16479 | 69.8181 | -53.1601 | -0.31586 | 0.073242 | -0.050354 | 122.7768 | -1.6296 | -0.33874 | 0.01831 | 0.2655 | 50.3082 | 52.6566 | 120.9915 | 122.6944 | -0.050354 | 122.6395 | 54.4556 | -0.33874 | 122.6944 | -0.050354 | 54.4556 | 120.9915 | 122.6395 | -122.937 | -122.9599
1594.9844 | 122.8821 | -52.7802 | 69.8227 | 0.21774 | 0.0038708 | 0.00024998 | -0.0005853 | -0.0030484 | 0.00013454 | 0.0038389 | -52.8122 | 69.841 | -53.064 | 70.0104 | 68.2755 | 1.6983 | -2.5681 | -0.054932 | 69.8364 | -53.1143 | -0.28381 | 0.01831 | -0.032044 | 122.7905 | -1.5472 | -0.33417 | 0.013733 | 0.25177 | 50.2121 | 52.7252 | 121.0556 | 122.6212 | -0.032044 | 122.6166 | 54.4785 | -0.33417 | 122.6212 | -0.032044 | 54.4785 | 121.0556 | 122.6166 | -122.8867 | -122.937
1595.9219 | 122.9507 | -52.5055 | 70.1019 | -0.079803 | 2.5564e-05 | 0.001959 | 0.0015509 | -0.0047574 | -0.0013609 | 0.0051205 | -52.6062 | 69.9875 | -52.8671 | 70.2896 | 68.5684 | 1.767 | -2.2751 | -0.18768 | 70.0607 | -52.8534 | -0.36163 | -0.11444 | -0.10071 | 122.7951 | -1.5335 | -0.3479 | -0.041199 | 0.26093 | 50.2304 | 52.3178 | 121.0739 | 122.493 | -0.10071 | 122.5662 | 54.2725 | -0.3479 | 122.493 | -0.10071 | 54.2725 | 121.0739 | 122.5662 | -122.9691 | -122.9553
1596.9531 | 122.9324 | -52.2125 | 70.4224 | 0.233 | 0.0025892 | 0.0062314 | 0.0060369 | -0.0043302 | 0.0018435 | 0.0040525 | -52.1484 | 70.4453 | -52.4963 | 70.6741 | 68.9346 | 1.8631 | -2.2064 | -0.022888 | 70.4041 | -52.5101 | -0.28381 | 0.022888 | 0.064087 | 122.8867 | -1.4877 | -0.29755 | -0.01831 | 0.3479 | 50.0061 | 52.1896 | 121.1472 | 122.6578 | 0.064087 | 122.6166 | 54.0756 | -0.29755 | 122.6578 | 0.064087 | 54.0756 | 121.1472 | 122.6166 | -122.9187 | -122.9324
1597.9062 | 122.8821 | -52.4689 | 70.166 | 0.21011 | 0.0045118 | 0.0058042 | 0.0088141 | -0.0051846 | 0.00056194 | 0.0057615 | -52.5375 | 70.1981 | -52.7985 | 70.2942 | 68.5455 | 1.6754 | -2.2568 | 0.21515 | 70.1385 | -52.8076 | -0.32959 | 0.032043 | -0.068665 | 122.7631 | -1.6205 | -0.33875 | -0.027466 | 0.26093 | 50.2121 | 52.684 | 121.0144 | 122.6669 | -0.068665 | 122.6074 | 54.1443 | -0.33875 | 122.6669 | -0.068665 | 54.1443 | 121.0144 | 122.6074 | -122.9645 | -122.9736
1598.9688 | 122.8683 | -52.6062 | 70.0195 | 0.18723 | 0.0060072 | 0.0049496 | 0.0071051 | -0.003262 | 0.0012027 | 0.0051205 | -52.6474 | 70.0378 | -52.9266 | 70.1797 | 68.4128 | 1.7212 | -2.1423 | 0.3067 | 70.0287 | -52.9541 | -0.32044 | 0.018311 | -0.041199 | 122.7859 | -1.6068 | -0.3479 | 0.009156 | 0.27924 | 50.4639 | 52.9129 | 121.019 | 122.644 | -0.041199 | 122.6349 | 54.3274 | -0.3479 | 122.644 | -0.041199 | 54.3274 | 121.019 | 122.6349 | -122.9462 | -122.9736
1599.9062 | 122.8455 | -52.8214 | 69.8593 | 0.13382 | 0.0053662 | 0.0075132 | 0.0068915 | -0.0017666 | -0.0030697 | 0.0055479 | -52.8854 | 69.8776 | -53.1555 | 69.9417 | 68.1244 | 1.7944 | -2.1378 | 0.3067 | 69.8273 | -53.1418 | -0.33417 | 0.018311 | -0.064087 | 122.7631 | -1.7349 | -0.32043 | -0.032043 | 0.27008 | 50.6836 | 53.1281 | 120.9457 | 122.699 | -0.064087 | 122.6486 | 54.6158 | -0.32043 | 122.699 | -0.064087 | 54.6158 | 120.9457 | 122.6486 | -123.0148 | -123.0011
1600.9688 | 122.7905 | -52.7481 | 69.9783 | 0.057526 | 0.0057934 | 0.0060178 | 0.0086005 | -0.001553 | 0.00056194 | 0.0046933 | -52.7481 | 69.9921 | -52.9953 | 70.047 | 68.1793 | 1.7853 | -1.7578 | 0.36163 | 69.96 | -53.0411 | -0.24719 | 0.013732 | 0 | 122.7951 | -1.799 | -0.29297 | -0.018311 | 0.24719 | 50.9903 | 53.1097 | 120.9274 | 122.7402 | 0 | 122.7081 | 54.5334 | -0.29297 | 122.7402 | 0 | 54.5334 | 120.9274 | 122.7081 | -122.9736 | -123.0194
1601.9062 | 122.9691 | -52.5421 | 70.0882 | 0.24826 | 0.0040846 | 0.0062314 | 0.0043281 | -0.0036892 | 0.00013454 | 0.0051205 | -52.5284 | 70.1157 | -52.8442 | 70.3125 | 68.4311 | 2.0416 | -2.005 | 0.68665 | 70.0836 | -52.8442 | -0.30212 | 0.027466 | 0.013733 | 122.8546 | -1.6571 | -0.30212 | -0.004578 | 0.31586 | 50.5371 | 53.2288 | 120.9732 | 122.6578 | 0.013733 | 122.6257 | 54.5837 | -0.30212 | 122.6578 | 0.013733 | 54.5837 | 120.9732 | 122.6257 | -122.9324 | -122.9324
1602.9688 | 122.9095 | -52.7115 | 69.9234 | 0.20248 | 0.0042982 | 0.0034544 | 0.0049689 | -0.003903 | -0.0015745 | 0.0049069 | -52.7618 | 69.9326 | -53.0502 | 70.079 | 68.2388 | 1.9409 | -2.2064 | 0.6134 | 69.8959 | -53.064 | -0.33875 | 0.009155 | -0.050354 | 122.7905 | -1.6846 | -0.35248 | -0.027466 | 0.28839 | 50.5051 | 53.3249 | 120.9503 | 122.644 | -0.050354 | 122.6074 | 54.6524 | -0.35248 | 122.644 | -0.050354 | 54.6524 | 120.9503 | 122.6074 | -122.9736 | -122.9874
1603.9062 | 122.8043 | -52.8534 | 69.8273 | 0.17197 | 0.0053662 | 0.0043088 | 0.0056097 | -0.0030484 | -0.00071986 | 0.0031979 | -52.8946 | 69.8776 | -53.1647 | 69.8959 | 68.1198 | 1.6937 | -1.886 | 0.40741 | 69.841 | -53.1921 | -0.31128 | 0.050354 | -0.041198 | 122.7493 | -1.7075 | -0.33874 | 0.013732 | 0.27008 | 50.9674 | 53.2608 | 120.9732 | 122.731 | -0.041198 | 122.6944 | 54.5471 | -0.33874 | 122.731 | -0.041198 | 54.5471 | 120.9732 | 122.6944 | -122.9919 | -123.0194
1604.9688 | 122.8912 | -52.977 | 69.6808 | 0.18723 | 0.004939 | 0.0045224 | 0.0030463 | -0.00069859 | -0.0011471 | 0.0044797 | -53.0502 | 69.6945 | -53.3112 | 69.8135 | 68.042 | 2.0325 | -2.1011 | 0.30212 | 69.7037 | -53.2837 | -0.33417 | 0.013733 | -0.073242 | 122.7905 | -1.6388 | -0.3067 | 0.022888 | 0.26093 | 50.8759 | 53.2791 | 121.019 | 122.6715 | -0.073242 | 122.6807 | 55.0095 | -0.3067 | 122.6715 | -0.073242 | 55.0095 | 121.019 | 122.6807 | -122.9919 | -122.9645
1605.9062 | 122.9095 | -52.7206 | 69.9234 | 0.16434 | 0.0030164 | 0.0049496 | 0.0013373 | -0.0036892 | 0.00013454 | 0.0036253 | -52.7161 | 69.9371 | -53.009 | 70.0882 | 68.3258 | 1.9958 | -2.2751 | 0.39368 | 69.8502 | -53.0319 | -0.28839 | 0.013733 | 0.004578 | 122.8088 | -1.5976 | -0.31128 | -0.073242 | 0.29297 | 50.4456 | 53.1143 | 121.0464 | 122.6578 | 0.004578 | 122.5708 | 54.7165 | -0.31128 | 122.6578 | 0.004578 | 54.7165 | 121.0464 | 122.5708 | -122.9324 | -122.9553
1606.9531 | 122.8546 | -52.7802 | 69.8914 | -0.32394 | 0.0045118 | 0.006445 | 0.0066779 | -0.00069859 | -0.0011471 | 0.0029843 | -52.7893 | 69.9509 | -53.0548 | 70.015 | 68.248 | 1.8906 | -1.8585 | 0.42114 | 69.8547 | -53.1326 | -0.27466 | 0.05951 | -0.009156 | 122.7951 | -1.6434 | -0.35248 | -0.036621 | 0.2655 | 50.9216 | 53.2013 | 121.0281 | 122.731 | -0.009156 | 122.6349 | 54.6707 | -0.35248 | 122.731 | -0.009156 | 54.6707 | 121.0281 | 122.6349 | -122.9462 | -123.024
1607.9062 | 122.818 | -52.8397 | 69.8593 | 0.91965 | 0.0055798 | 0.0025998 | 0.0058233 | -0.0019802 | -0.0017881 | 0.0051205 | -52.9312 | 69.8868 | -53.1738 | 69.9234 | 68.1656 | 2.0599 | -1.3229 | 0.13733 | 69.8502 | -53.1601 | -0.33417 | 0.027466 | -0.091552 | 122.7631 | -1.6937 | -0.32043 | -0.009155 | 0.24262 | 51.5167 | 52.977 | 121.0052 | 122.7264 | -0.091552 | 122.6898 | 54.8996 | -0.32043 | 122.7264 | -0.091552 | 54.8996 | 121.0052 | 122.6898 | -123.0331 | -123.0194
1608.9688 | 122.7997 | -52.8351 | 69.841 | -0.026398 | 0.0055798 | 0.008154 | 0.0062507 | -0.002194 | -0.0013609 | 0.0055479 | -52.8854 | 69.8273 | -53.1967 | 69.9509 | 68.1747 | 2.0325 | -1.6342 | 0.32501 | 69.8456 | -53.1555 | -0.36163 | -0.013732 | -0.050354 | 122.7859 | -1.6663 | -0.32044 | 0.004578 | 0.31128 | 51.2009 | 53.1601 | 121.0098 | 122.6624 | -0.050354 | 122.6807 | 54.8676 | -0.32044 | 122.6624 | -0.050354 | 54.8676 | 121.0098 | 122.6807 | -123.0377 | -122.9965
1609.9062 | 122.7859 | -53.1143 | 69.5572 | 0.13382 | 0.0057934 | 0.0075132 | 0.0058233 | -0.0013394 | -0.00029266 | 0.0040525 | -53.2288 | 69.5618 | -53.476 | 69.5755 | 68.0328 | 1.6708 | -2.211 | 0.37537 | 69.5435 | -53.4622 | -0.36163 | 0.004578 | -0.11444 | 122.6898 | -1.5244 | -0.3479 | -0.013733 | 0.24719 | 50.9033 | 53.4897 | 121.1472 | 122.6761 | -0.11444 | 122.6578 | 54.7852 | -0.3479 | 122.6761 | -0.11444 | 54.7852 | 121.1472 | 122.6578 | -123.0331 | -123.0194
1610.9688 | 122.8271 | -52.771 | 69.8639 | -0.018768 | 0.0057934 | 0.0060178 | 0.0068915 | -0.0024076 | -0.0013609 | 0.0025571 | -52.8214 | 69.8959 | -53.1372 | 69.9921 | 68.2251 | 2.0325 | -1.7166 | -0.032043 | 69.8639 | -53.1143 | -0.36621 | 0.032043 | -0.050354 | 122.7631 | -1.6388 | -0.34332 | 0 | 0.31586 | 51.0544 | 52.739 | 120.9961 | 122.6669 | -0.050354 | 122.6349 | 54.8035 | -0.34332 | 122.6669 | -0.050354 | 54.8035 | 120.9961 | 122.6349 | -123.0011 | -122.9782
1611.9062 | 122.8409 | -53.1921 | 69.4839 | -0.39261 | 0.0036572 | 0.004736 | 0.0047553 | -0.0011258 | -0.00071986 | 0.0038389 | -53.2333 | 69.5206 | -53.4851 | 69.5572 | 67.7811 | 1.8311 | -1.4877 | 0.24719 | 69.5023 | -53.5309 | -0.29297 | 0.036621 | -0.041198 | 122.7493 | -1.7029 | -0.33875 | 0.01831 | 0.25177 | 51.7044 | 53.4393 | 120.9732 | 122.7127 | -0.041198 | 122.6944 | 55.0232 | -0.33875 | 122.7127 | -0.041198 | 55.0232 | 120.9732 | 122.6944 | -122.9691 | -123.0148
1612.9531 | 122.9279 | -53.3478 | 69.2688 | 0.25589 | 0.0030164 | 0.006445 | 0.0028327 | 0.00036961 | 0.00034814 | 0.0049069 | -53.3752 | 69.2917 | -53.6636 | 69.4885 | 67.7032 | 1.9226 | -1.9363 | 0.14191 | 69.2963 | -53.6774 | -0.31586 | 0.022888 | -0.027466 | 122.8363 | -1.5656 | -0.32959 | 0.027466 | 0.28839 | 51.4114 | 53.4897 | 121.051 | 122.6395 | -0.027466 | 122.644 | 55.2704 | -0.32959 | 122.6395 | -0.027466 | 55.2704 | 121.051 | 122.644 | -122.9324 | -122.9462
1613.9062 | 122.8317 | -53.5172 | 69.1269 | 0.17197 | 0.0081434 | 0.003027 | 0.0041143 | -0.003903 | 0.00034814 | 0.0051205 | -53.5858 | 69.2322 | -53.8147 | 69.2505 | 67.4744 | 1.6754 | -1.6022 | -0.036621 | 69.1544 | -53.8467 | -0.29755 | 0.10529 | -0.068664 | 122.7676 | -1.6525 | -0.32959 | 0.027466 | 0.22888 | 51.915 | 53.4805 | 120.9915 | 122.7493 | -0.068664 | 122.6715 | 55.1926 | -0.32959 | 122.7493 | -0.068664 | 55.1926 | 120.9915 | 122.6715 | -122.9416 | -122.9736
1614.9688 | 122.8134 | -53.1738 | 69.5114 | -0.31631 | 0.0038708 | 0.001959 | 0.0028327 | -0.002194 | 0.0022707 | 0.0038389 | -53.2791 | 69.5435 | -53.508 | 69.5892 | 67.7536 | 1.8265 | -1.3229 | 0.1831 | 69.5023 | -53.5034 | -0.33417 | 0.032043 | -0.10529 | 122.7631 | -1.7578 | -0.32959 | -0.009156 | 0.22888 | 51.8509 | 53.3569 | 120.9274 | 122.7173 | -0.10529 | 122.6761 | 55.0003 | -0.32959 | 122.7173 | -0.10529 | 55.0003 | 120.9274 | 122.6761 | -123.0194 | -123.0148
1615.9062 | 122.9141 | -53.4348 | 69.1681 | 0.15671 | 0.0030164 | 0.0045224 | 0.0013373 | -0.00027139 | -0.0013609 | 0.0057615 | -53.508 | 69.1177 | -53.7918 | 69.3604 | 67.5568 | 1.767 | -1.3962 | 0.31128 | 69.1452 | -53.7872 | -0.35706 | -0.050354 | -0.073243 | 122.7951 | -1.6113 | -0.35248 | -0.022888 | 0.28381 | 52.0386 | 53.746 | 120.9915 | 122.5525 | -0.073243 | 122.58 | 55.2017 | -0.35248 | 122.5525 | -0.073243 | 55.2017 | 120.9915 | 122.58 | -122.9599 | -122.9553
1616.9688 | 122.8592 | -53.4256 | 69.2184 | -0.079803 | 0.0047254 | 0.011358 | 0.0062507 | -0.0026212 | -0.00029266 | 0.0040525 | -53.4897 | 69.2505 | -53.746 | 69.3741 | 67.4789 | 1.1765 | -0.98877 | 0.45319 | 69.2276 | -53.7827 | -0.32043 | 0.032043 | -0.064087 | 122.7997 | -1.7395 | -0.35706 | 0.009155 | 0.25635 | 52.4368 | 53.8788 | 120.9045 | 122.6761 | -0.064087 | 122.6532 | 54.6021 | -0.35706 | 122.6761 | -0.064087 | 54.6021 | 120.9045 | 122.6532 | -122.9645 | -123.0011
1617.9062 | 122.8134 | -53.5904 | 69.1086 | 0.034637 | 0.0055798 | 0.0083676 | 0.0062507 | -0.002194 | 0.0016299 | 0.0036253 | -53.595 | 69.1727 | -53.8513 | 69.1956 | 67.3462 | 1.4786 | -1.149 | 0.082397 | 69.1315 | -53.9291 | -0.26093 | 0.064086 | -0.004578 | 122.7859 | -1.7624 | -0.33875 | 0.022888 | 0.25635 | 52.4414 | 53.6728 | 120.9366 | 122.7631 | -0.004578 | 122.7219 | 55.069 | -0.33875 | 122.7631 | -0.004578 | 55.069 | 120.9366 | 122.7219 | -122.9599 | -123.0377
1618.9531 | 122.7814 | -53.3157 | 69.3924 | 0.080414 | 0.0070752 | 0.0092222 | 0.0058233 | -0.00091219 | 0.00013454 | 0.0044797 | -53.3981 | 69.3695 | -53.6774 | 69.4107 | 67.5888 | 1.3596 | -1.3733 | -0.013733 | 69.4016 | -53.6636 | -0.36163 | -0.022888 | -0.082397 | 122.7264 | -1.8036 | -0.3479 | 0.009155 | 0.27924 | 51.9424 | 53.302 | 120.9045 | 122.6852 | -0.082397 | 122.7173 | 54.6753 | -0.3479 | 122.6852 | -0.082397 | 54.6753 | 120.9045 | 122.7173 | -123.0698 | -123.056
1619.9062 | 122.8088 | -53.8284 | 68.8934 | 0.065155 | 0.0068616 | 0.0077268 | 0.0053961 | 0.0022922 | 0.00013454 | 0.0036253 | -53.8742 | 68.9117 | -54.1306 | 68.9529 | 67.1722 | 1.4603 | -1.3687 | 0.30212 | 68.9026 | -54.1763 | -0.30212 | 0.01831 | -0.045777 | 122.7814 | -1.7212 | -0.3479 | 0.009155 | 0.25635 | 52.4597 | 54.1306 | 121.0007 | 122.7402 | -0.045777 | 122.731 | 55.2887 | -0.3479 | 122.7402 | -0.045777 | 55.2887 | 121.0007 | 122.731 | -123.024 | -123.0698
1620.9688 | 122.8226 | -53.8788 | 68.7973 | -0.011139 | 0.002162 | 0.006445 | 0.0058233 | 0.00079681 | -0.0034971 | 0.0049069 | -53.9017 | 68.8019 | -54.2175 | 68.9209 | 67.1219 | 1.5564 | -1.4099 | 0.059509 | 68.8431 | -54.1809 | -0.33874 | 0.004578 | -0.022888 | 122.7997 | -1.6754 | -0.30212 | 0.045777 | 0.31586 | 52.4689 | 53.9383 | 121.0007 | 122.6807 | -0.022888 | 122.7219 | 55.4352 | -0.30212 | 122.6807 | -0.022888 | 55.4352 | 121.0007 | 122.7219 | -123.0148 | -122.9782
1621.9062 | 122.7631 | -53.8788 | 68.8431 | 0.16434 | 0.0025892 | 0.008154 | 0.0053961 | 0.00036961 | 0.00034814 | 0.0044797 | -53.9383 | 68.8889 | -54.1763 | 68.9117 | 66.8701 | 1.3046 | -0.63629 | 0.09613 | 68.866 | -54.1763 | -0.29755 | 0.045776 | -0.059509 | 122.7905 | -1.973 | -0.29755 | 0.022888 | 0.23804 | 53.2425 | 53.9749 | 120.7489 | 122.7676 | -0.059509 | 122.7448 | 55.1834 | -0.29755 | 122.7676 | -0.059509 | 55.1834 | 120.7489 | 122.7448 | -123.0194 | -123.0194
1622.9688 | 122.8821 | -53.9383 | 68.7103 | -0.11795 | 0.0064344 | 0.005377 | 0.0058233 | -0.0013394 | -0.00071986 | 0.0023435 | -53.9795 | 68.7195 | -54.2862 | 68.811 | 67.1082 | 1.1444 | -1.3275 | -0.32959 | 68.692 | -54.3091 | -0.3479 | 0.009155 | -0.041199 | 122.7493 | -1.6022 | -0.37079 | -0.01831 | 0.3067 | 52.6108 | 53.6087 | 121.0464 | 122.6578 | -0.041199 | 122.6303 | 55.0827 | -0.37079 | 122.6578 | -0.041199 | 55.0827 | 121.0464 | 122.6303 | -122.9965 | -123.0194
1623.9062 | 122.8363 | -54.0298 | 68.6508 | 0.019379 | 0.0051526 | 0.01029 | 0.0047553 | 0.00015601 | -0.00093346 | 0.0034115 | -54.0665 | 68.6646 | -54.3457 | 68.7424 | 66.9571 | 1.1719 | -1.3412 | -0.19684 | 68.6554 | -54.364 | -0.31586 | 0.013733 | -0.036621 | 122.7722 | -1.6937 | -0.33417 | 0.004578 | 0.27924 | 52.6886 | 53.833 | 120.9869 | 122.6944 | -0.036621 | 122.6852 | 55.2017 | -0.33417 | 122.6944 | -0.036621 | 55.2017 | 120.9869 | 122.6852 | -122.9965 | -123.0148
1624.9688 | 122.8317 | -54.0482 | 68.6417 | -0.20187 | 0.0062208 | 0.0055906 | 0.0060369 | -0.0017666 | 0.00034814 | 0.0040525 | -54.0894 | 68.6462 | -54.4006 | 68.7332 | 66.9113 | 1.1765 | -1.4603 | 0.041199 | 68.6188 | -54.3823 | -0.35248 | 0.004577 | -0.041198 | 122.7814 | -1.7303 | -0.33417 | -0.022889 | 0.31128 | 52.5879 | 54.0894 | 120.9595 | 122.6944 | -0.041198 | 122.6669 | 55.2246 | -0.33417 | 122.6944 | -0.041198 | 55.2246 | 120.9595 | 122.6669 | -123.0423 | -123.024
1625.9062 | 122.7859 | -53.7689 | 68.9209 | 0.13382 | 0.0034436 | 0.0023862 | 0.0049689 | 0.0016512 | 0.0029117 | 0.0040525 | -53.8513 | 68.9575 | -54.0756 | 69.1177 | 67.4561 | 1.0712 | -1.5701 | -0.018311 | 68.9804 | -54.0848 | -0.3067 | 0.036622 | -0.082397 | 122.8867 | -1.4648 | -0.31586 | 0.05951 | 0.22431 | 52.1988 | 53.7506 | 121.225 | 122.7264 | -0.082397 | 122.7493 | 54.8401 | -0.31586 | 122.7264 | -0.082397 | 54.8401 | 121.225 | 122.7493 | -122.9965 | -123.0057
1626.9531 | 122.8226 | -53.9978 | 68.7149 | -0.16373 | 0.0085706 | 0.01029 | 5.5496e-05 | -5.7592e-05 | 0.00013454 | 0.0051205 | -54.039 | 68.7241 | -54.3091 | 68.8248 | 67.0074 | 1.0666 | -0.93384 | 0.2243 | 68.7469 | -54.3228 | -0.31128 | 0.009155 | -0.041198 | 122.8226 | -1.7075 | -0.32501 | 0.032043 | 0.27008 | 53.064 | 54.2221 | 121.0052 | 122.7219 | -0.041198 | 122.7448 | 55.0644 | -0.32501 | 122.7219 | -0.041198 | 55.0644 | 121.0052 | 122.7448 | -123.024 | -123.0377
1627.9062 | 122.7859 | -54.6341 | 68.0557 | 0.25589 | 0.0034436 | 0.003668 | 0.0068915 | 0.00058321 | 0.00056194 | 0.0044797 | -54.6844 | 68.1198 | -54.9316 | 68.1107 | 66.3071 | 1.0757 | -0.85144 | 0.16022 | 68.0832 | -54.9637 | -0.29755 | 0.064087 | -0.050354 | 122.7448 | -1.7487 | -0.32959 | 0.027466 | 0.24719 | 53.7827 | 54.7943 | 120.9412 | 122.7539 | -0.050354 | 122.7173 | 55.7098 | -0.32959 | 122.7539 | -0.050354 | 55.7098 | 120.9412 | 122.7173 | -122.9874 | -123.0194
1628.9531 | 122.8363 | -54.8401 | 67.8635 | -0.13321 | 0.006648 | 0.0058042 | 0.0036871 | -0.0011258 | -0.0011471 | 0.0027707 | -54.8584 | 67.9138 | -55.1147 | 67.955 | 66.188 | 1.0483 | -1.3916 | 0.41199 | 67.8589 | -55.2017 | -0.27466 | 0.050354 | -0.01831 | 122.7951 | -1.6754 | -0.36163 | -0.004577 | 0.25635 | 53.4485 | 55.2521 | 121.0281 | 122.7539 | -0.01831 | 122.699 | 55.8884 | -0.36163 | 122.7539 | -0.01831 | 55.8884 | 121.0281 | 122.699 | -122.9782 | -123.0652
1629.9062 | 122.8317 | -54.9088 | 67.7902 | 0.057526 | 0.004939 | 0.0066586 | 0.0066779 | 0.00058321 | -0.00093346 | 0.0044797 | -54.9362 | 67.8177 | -55.1926 | 67.8543 | 66.0416 | 1.2405 | -1.1948 | 0.036621 | 67.8223 | -55.22 | -0.28381 | 0.027466 | -0.027466 | 122.7631 | -1.7487 | -0.31128 | 0.032044 | 0.25635 | 53.714 | 54.9454 | 120.9503 | 122.7264 | -0.027466 | 122.731 | 56.1493 | -0.31128 | 122.7264 | -0.027466 | 56.1493 | 120.9503 | 122.731 | -122.9828 | -123.0103
1630.9688 | 122.7997 | -55.0781 | 67.6163 | 0.042267 | 0.00323 | 0.0060178 | 0.0053961 | 0.00036961 | -0.0011471 | 0.0061887 | -55.1422 | 67.6071 | -55.4077 | 67.6529 | 65.9546 | 1.0849 | -1.1398 | 0.19684 | 67.6254 | -55.4123 | -0.32959 | -0.009155 | -0.064087 | 122.731 | -1.6617 | -0.33417 | 0.009155 | 0.2655 | 53.9383 | 55.275 | 121.0327 | 122.6852 | -0.064087 | 122.7036 | 56.163 | -0.33417 | 122.6852 | -0.064087 | 56.163 | 121.0327 | 122.7036 | -123.024 | -123.0286
1631.9062 | 122.8088 | -55.0278 | 67.6392 | 0.080414 | 0.0053662 | 0.0079404 | 0.0051825 | -0.00027139 | -7.9062e-05 | 0.0044797 | -55.0369 | 67.7307 | -55.2979 | 67.7261 | 66.037 | 1.0529 | -1.0437 | 0.1236 | 67.6987 | -55.3848 | -0.27008 | 0.091553 | -0.009155 | 122.7539 | -1.6022 | -0.35706 | 0.059509 | 0.26093 | 53.9841 | 55.1514 | 121.0648 | 122.7585 | -0.009155 | 122.7264 | 56.0806 | -0.35706 | 122.7585 | -0.009155 | 56.0806 | 121.0648 | 122.7264 | -122.937 | -123.024
1632.9531 | 122.818 | -55.0095 | 67.6758 | 0.18723 | 0.0045118 | 0.0023862 | 0.0036871 | -0.0017666 | -0.0026425 | 0.0040525 | -55.0644 | 67.7353 | -55.307 | 67.7719 | 65.8447 | 0.88348 | -0.9613 | -0.013733 | 67.717 | -55.3619 | -0.29755 | 0.05951 | -0.054932 | 122.7814 | -1.8311 | -0.35248 | 0.041199 | 0.24262 | 54.0482 | 54.9957 | 120.8542 | 122.7448 | -0.054932 | 122.7264 | 55.8929 | -0.35248 | 122.7448 | -0.054932 | 55.8929 | 120.8542 | 122.7264 | -122.9828 | -123.0377
1633.9062 | 122.8546 | -55.0232 | 67.662 | -0.0035098 | 0.0040846 | 0.0051632 | 0.0058233 | 0.001224 | -0.00029266 | 0.0021299 | -55.0049 | 67.7078 | -55.3207 | 67.7994 | 66.0278 | 1.1307 | -1.0986 | 0.004578 | 67.7124 | -55.3345 | -0.29755 | 0.045777 | 0.01831 | 122.8226 | -1.6342 | -0.31128 | 0.050354 | 0.31586 | 53.9246 | 55.0278 | 121.051 | 122.731 | 0.01831 | 122.7356 | 56.1539 | -0.31128 | 122.731 | 0.01831 | 56.1539 | 121.051 | 122.7356 | -122.9828 | -122.9965
1634.9688 | 122.818 | -55.5634 | 67.1356 | -0.18662 | 0.0023756 | 0.0021726 | 0.0002691 | -0.0041166 | 0.0026981 | 0.0055479 | -55.6366 | 67.1539 | -55.8701 | 67.1722 | 65.451 | 0.87891 | -1.03 | -0.004578 | 67.1356 | -55.9021 | -0.3067 | 0.018311 | -0.073243 | 122.7356 | -1.6846 | -0.33875 | 0 | 0.23346 | 54.5334 | 55.5588 | 121.0144 | 122.7173 | -0.073243 | 122.699 | 56.4423 | -0.33875 | 122.7173 | -0.073243 | 56.4423 | 121.0144 | 122.699 | -123.0057 | -123.0377
1635.9062 | 122.8134 | -55.4672 | 67.2592 | 0.057526 | 0.0057934 | 0.0062314 | 0.0071051 | -0.001553 | -7.9062e-05 | 0.0046933 | -55.4947 | 67.2867 | -55.7419 | 67.2958 | 65.5106 | 0.68665 | -0.97046 | -0.15564 | 67.2501 | -55.7922 | -0.27466 | 0.027466 | -0.027466 | 122.7631 | -1.7487 | -0.32501 | -0.009155 | 0.24719 | 54.4968 | 55.3116 | 120.9778 | 122.7539 | -0.027466 | 122.7173 | 56.1539 | -0.32501 | 122.7539 | -0.027466 | 56.1539 | 120.9778 | 122.7173 | -123.0011 | -123.0515
1636.9531 | 122.8363 | -55.0873 | 67.6483 | -0.12558 | 0.0034436 | 0.0025998 | 0.0015509 | -0.0013394 | -0.0013609 | 0.0036253 | -55.1697 | 67.6804 | -55.3802 | 67.6804 | 65.9409 | 1.0117 | -0.38452 | 0.43488 | 67.6712 | -55.4169 | -0.29297 | 0.032044 | -0.082398 | 122.7676 | -1.7075 | -0.32959 | 0.022889 | 0.21057 | 54.7028 | 55.5222 | 121.0281 | 122.7676 | -0.082398 | 122.7585 | 56.0989 | -0.32959 | 122.7676 | -0.082398 | 56.0989 | 121.0281 | 122.7585 | -123.0286 | -123.0652
1637.9062 | 122.8409 | -55.3436 | 67.3325 | -0.20187 | 0.0040846 | 0.004736 | 0.0086005 | -5.7592e-05 | 0.00013454 | 0.0044797 | -55.3802 | 67.3553 | -55.6686 | 67.4561 | 65.6662 | 0.93384 | -0.95673 | 0.3479 | 67.3599 | -55.6778 | -0.32501 | 0.022889 | -0.036621 | 122.7997 | -1.6663 | -0.33417 | 0.027466 | 0.28839 | 54.3869 | 55.6915 | 121.0098 | 122.699 | -0.036621 | 122.7036 | 56.2775 | -0.33417 | 122.699 | -0.036621 | 56.2775 | 121.0098 | 122.7036 | -123.0011 | -123.0103
1638.9531 | 122.8317 | -55.4169 | 67.2913 | -0.1561 | 0.0038708 | 0.0077268 | 0.0041143 | -0.00048499 | -0.0022153 | 0.0038389 | -55.4535 | 67.3096 | -55.7327 | 67.392 | 65.6708 | 1.1902 | -1.062 | 0.5127 | 67.3279 | -55.7327 | -0.31586 | 0.01831 | -0.036621 | 122.8088 | -1.6205 | -0.31586 | 0.036621 | 0.27924 | 54.3549 | 55.9296 | 121.0876 | 122.7264 | -0.036621 | 122.7448 | 56.6071 | -0.31586 | 122.7264 | -0.036621 | 56.6071 | 121.0876 | 122.7448 | -123.024 | -123.024
1639.9062 | 122.8271 | -55.5542 | 67.1173 | 0.095673 | 0.0053662 | 0.006445 | 0.0079595 | 0.00079681 | -0.00029266 | 0.0044797 | -55.6229 | 67.1722 | -55.8517 | 67.1814 | 65.4556 | 1.149 | -0.90637 | 0.60883 | 67.1585 | -55.8975 | -0.29755 | 0.054931 | -0.068665 | 122.7356 | -1.6617 | -0.34332 | 0.041198 | 0.22888 | 54.6478 | 56.163 | 121.0098 | 122.7264 | -0.068665 | 122.7127 | 56.7032 | -0.34332 | 122.7264 | -0.068665 | 56.7032 | 121.0098 | 122.7127 | -122.9691 | -123.0148
1640.9688 | 122.9233 | -55.6732 | 66.9434 | -0.0035098 | 0.0028028 | 0.0038816 | -0.0031489 | -0.002194 | 0.00098914 | 0.0038389 | -55.7053 | 66.9891 | -55.9753 | 67.1448 | 65.4419 | 1.3367 | -0.99792 | 0.71411 | 66.9891 | -56.012 | -0.30212 | 0.045777 | -0.032043 | 122.818 | -1.5015 | -0.33875 | 0.045777 | 0.27008 | 54.6753 | 56.3873 | 121.1151 | 122.6624 | -0.032043 | 122.6624 | 57.0099 | -0.33875 | 122.6624 | -0.032043 | 57.0099 | 121.1151 | 122.6624 | -122.9187 | -122.9553
1641.9062 | 122.8592 | -55.3848 | 67.2958 | 0.019379 | 0.0045118 | 0.008154 | 0.0083869 | -0.0013394 | 0.00056194 | 0.0049069 | -55.3986 | 67.3416 | -55.6778 | 67.4194 | 65.7852 | 1.3641 | -0.98877 | 0.73242 | 67.2913 | -55.6686 | -0.29297 | 0.045777 | -0.013733 | 122.8043 | -1.5106 | -0.28381 | -0.004577 | 0.27923 | 54.3961 | 56.1172 | 121.17 | 122.7264 | -0.013733 | 122.6761 | 56.749 | -0.28381 | 122.7264 | -0.013733 | 56.749 | 121.17 | 122.6761 | -122.9736 | -122.9645
1642.9531 | 122.8317 | -55.2521 | 67.4377 | -0.11795 | 0.0040846 | 0.003668 | 0.0060369 | -0.0017666 | 0.00013454 | 0.0061887 | -55.2933 | 67.5018 | -55.5405 | 67.4973 | 65.7898 | 1.236 | -1.2222 | 0.48981 | 67.4789 | -55.5771 | -0.28839 | 0.064087 | -0.041199 | 122.7493 | -1.6479 | -0.32501 | 0.041199 | 0.24719 | 54.0298 | 55.7419 | 121.0419 | 122.7539 | -0.041199 | 122.731 | 56.488 | -0.32501 | 122.7539 | -0.041199 | 56.488 | 121.0419 | 122.731 | -122.9782 | -123.0148
1643.9062 | 122.8912 | -55.4626 | 67.2134 | -0.072174 | 0.0068616 | 0.0032406 | 0.0079595 | 0.00079681 | -0.00029266 | 0.00020726 | -55.4672 | 67.2638 | -55.7465 | 67.4377 | 65.6708 | 0.35248 | -1.4694 | 0.34332 | 67.2272 | -55.7877 | -0.28381 | 0.050354 | -0.004578 | 122.9004 | -1.5427 | -0.32501 | 0.013733 | 0.27924 | 53.9932 | 55.806 | 121.1334 | 122.7264 | -0.004578 | 122.6898 | 55.8151 | -0.32501 | 122.7264 | -0.004578 | 55.8151 | 121.1334 | 122.6898 | -122.9599 | -123.0011
1644.9531 | 122.8775 | -55.7922 | 66.8518 | -0.18662 | 0.0023756 | 0.0060178 | -0.0005853 | -0.0030484 | -0.0011471 | 0.0036253 | -55.8105 | 66.8701 | -56.0852 | 67.0395 | 65.387 | 1.2497 | -1.5427 | 0.50354 | 66.893 | -56.0852 | -0.29297 | 0.01831 | -0.018311 | 122.8317 | -1.4648 | -0.29297 | 0.041198 | 0.27466 | 54.2496 | 56.2958 | 121.1792 | 122.6624 | -0.018311 | 122.6852 | 57.0419 | -0.29297 | 122.6624 | -0.018311 | 57.0419 | 121.1792 | 122.6852 | -122.937 | -122.937
1645.9062 | 122.8317 | -55.5588 | 67.1539 | 0.011749 | 0.004939 | 0.0085812 | 0.0066779 | -0.001553 | -0.0020017 | 0.0027707 | -55.6366 | 67.131 | -55.9204 | 67.2089 | 65.5518 | 1.3092 | -1.0071 | 0.50812 | 67.1448 | -55.9067 | -0.36163 | -0.022889 | -0.07782 | 122.7676 | -1.6022 | -0.3479 | -0.009156 | 0.28381 | 54.5517 | 56.0669 | 121.1105 | 122.6898 | -0.07782 | 122.7036 | 56.868 | -0.3479 | 122.6898 | -0.07782 | 56.868 | 121.1105 | 122.7036 | -123.0743 | -123.0606
1646.9531 | 122.8775 | -55.7602 | 66.893 | -0.14847 | 0.00323 | 0.0045224 | 0.0060369 | -0.0019802 | -0.0011471 | 0.0053343 | -55.751 | 66.9525 | -56.0623 | 67.0624 | 65.332 | 1.1902 | -1.5198 | 0.31128 | 66.9205 | -56.0989 | -0.30212 | 0.05951 | 0.009155 | 122.8226 | -1.561 | -0.33874 | 0.027466 | 0.31128 | 54.2404 | 56.0715 | 121.0922 | 122.7127 | 0.009155 | 122.6807 | 56.9504 | -0.33874 | 122.7127 | 0.009155 | 56.9504 | 121.0922 | 122.6807 | -122.9553 | -122.9919
1647.9062 | 122.8546 | -55.6686 | 66.9983 | -0.23239 | 0.0025892 | 0.0092222 | 0.0043281 | 0.00015601 | 0.00034814 | 0.0019163 | -55.719 | 67.0349 | -56.0074 | 67.1127 | 65.419 | 1.1856 | -1.4557 | 0.22888 | 67.0441 | -55.9799 | -0.33874 | 0.036621 | -0.050354 | 122.7814 | -1.5793 | -0.31128 | 0.045776 | 0.28839 | 54.213 | 55.8975 | 121.0876 | 122.7036 | -0.050354 | 122.7127 | 56.8542 | -0.31128 | 122.7036 | -0.050354 | 56.8542 | 121.0876 | 122.7127 | -123.0057 | -122.9782
1648.9531 | 122.818 | -55.7007 | 67.0029 | -0.16373 | 0.0038708 | 0.00024998 | 0.0013373 | -0.0017666 | -0.0037107 | 0.0057615 | -55.7465 | 67.0578 | -55.9753 | 67.0807 | 65.3961 | 1.1307 | -1.0849 | 0.31128 | 67.0486 | -56.0028 | -0.27466 | 0.054931 | -0.045776 | 122.7814 | -1.6068 | -0.30212 | 0.045776 | 0.22888 | 54.6158 | 56.012 | 121.0968 | 122.7585 | -0.045776 | 122.7493 | 56.8314 | -0.30212 | 122.7585 | -0.045776 | 56.8314 | 121.0968 | 122.7493 | -122.9782 | -123.0057
1649.9062 | 122.85 | -55.6824 | 67.0074 | -0.16373 | 0.0060072 | 0.0025998 | 0.0045417 | 0.00058321 | -0.00071986 | 0.0051205 | -55.687 | 67.012 | -55.9982 | 67.1356 | 65.4465 | 1.1169 | -1.1398 | 0.32501 | 67.0486 | -56.0165 | -0.31586 | 0.004578 | -0.004578 | 122.818 | -1.561 | -0.33417 | 0.041199 | 0.31128 | 54.5425 | 56.0074 | 121.1288 | 122.6944 | -0.004578 | 122.731 | 56.7993 | -0.33417 | 122.6944 | -0.004578 | 56.7993 | 121.1288 | 122.731 | -123.0057 | -123.024
1650.9688 | 122.8134 | -55.4077 | 67.3141 | -0.24765 | 0.0034436 | 0.0060178 | -0.0005853 | -0.0034756 | -7.9062e-05 | 0.0017027 | -55.4855 | 67.2409 | -55.7465 | 67.3828 | 65.7532 | 1.0895 | -1.0437 | 0.25635 | 67.3141 | -55.7281 | -0.33874 | -0.073242 | -0.07782 | 122.7905 | -1.561 | -0.32043 | 0 | 0.26093 | 54.364 | 55.6641 | 121.1609 | 122.6486 | -0.07782 | 122.7219 | 56.4972 | -0.32043 | 122.6486 | -0.07782 | 56.4972 | 121.1609 | 122.7219 | -123.0606 | -123.0423
1651.9062 | 122.8409 | -56.0486 | 66.6824 | -0.17136 | 0.0042982 | 0.0023862 | 0.0056097 | -0.0030484 | -0.0015745 | 0.0025571 | -56.1081 | 66.6595 | -56.337 | 66.7374 | 65.062 | 0.87433 | -1.2589 | 0.32959 | 66.6687 | -56.3782 | -0.28839 | -0.022888 | -0.059509 | 122.7859 | -1.6205 | -0.32959 | -0.013733 | 0.22888 | 54.7897 | 56.3782 | 121.1105 | 122.7081 | -0.059509 | 122.7173 | 56.9229 | -0.32959 | 122.7081 | -0.059509 | 56.9229 | 121.1105 | 122.7173 | -123.0194 | -123.0606
1652.9531 | 122.8226 | -56.2088 | 66.5222 | -0.1561 | 0.0040846 | 0.0060178 | 0.0034735 | -0.00048499 | -0.0020017 | 0.0055479 | -56.2225 | 66.5405 | -56.4743 | 66.6 | 64.9017 | 0.82855 | -0.8606 | 0.31128 | 66.5085 | -56.5109 | -0.2655 | 0.01831 | -0.013733 | 122.8088 | -1.6205 | -0.30212 | -0.013733 | 0.25177 | 55.3482 | 56.5201 | 121.1105 | 122.7493 | -0.013733 | 122.7173 | 57.0374 | -0.30212 | 122.7493 | -0.013733 | 57.0374 | 121.1105 | 122.7173 | -122.9965 | -123.0331
1653.9062 | 122.8867 | -56.3736 | 66.3345 | -0.19424 | 0.0036572 | 0.0075132 | 0.0047553 | -0.0030484 | -7.9062e-05 | 0.0017027 | -56.4011 | 66.3391 | -56.6711 | 66.4536 | 64.7919 | 0.83313 | -1.4511 | 0.21057 | 66.3895 | -56.6666 | -0.29755 | 0.004577 | -0.027466 | 122.8271 | -1.5427 | -0.29297 | 0.054931 | 0.27008 | 54.9225 | 56.5842 | 121.1655 | 122.7127 | -0.027466 | 122.7631 | 57.2067 | -0.29297 | 122.7127 | -0.027466 | 57.2067 | 121.1655 | 122.7631 | -123.0057 | -123.0011
1654.9688 | 122.9416 | -56.7032 | 65.9225 | 1.8123 | 0.0030164 | 0.0021726 | -0.0010125 | -0.0030484 | 0.00056194 | 0.0049069 | -56.6757 | 65.8905 | -57.0282 | 66.1331 | 64.5218 | 0.74158 | -1.8082 | 0.46234 | 65.9592 | -57.0007 | -0.32501 | -0.032043 | 0.027466 | 122.8363 | -1.4008 | -0.29755 | 0.036621 | 0.35248 | 54.895 | 57.1655 | 121.225 | 122.5937 | 0.027466 | 122.6624 | 57.4448 | -0.29755 | 122.5937 | 0.027466 | 57.4448 | 121.225 | 122.6624 | -122.9507 | -122.9233
1655.9062 | 122.7997 | -56.868 | 65.8585 | 0.11093 | 0.0042982 | 0.0072996 | 0.0083869 | -0.0036892 | -7.9062e-05 | 0.0034115 | -56.8863 | 65.8905 | -57.1335 | 65.8859 | 64.2151 | 0.62256 | -1.7624 | 0.2655 | 65.8356 | -57.2067 | -0.2655 | 0.032044 | -0.018311 | 122.7539 | -1.6434 | -0.33875 | -0.022888 | 0.24719 | 55.1056 | 57.1335 | 121.0831 | 122.7585 | -0.018311 | 122.7036 | 57.4905 | -0.33875 | 122.7585 | -0.018311 | 57.4905 | 121.0831 | 122.7036 | -122.9919 | -123.0652
1656.9688 | 122.8271 | -57.0145 | 65.6845 | -0.056915 | 0.0042982 | 0.0051632 | 0.0036871 | -0.0036892 | 0.0012027 | 0.0038389 | -57.193 | 65.7532 | -57.2983 | 65.799 | 64.119 | 0.58594 | -0.92926 | 0.15564 | 65.7349 | -57.3303 | -0.28381 | 0.068665 | -0.17853 | 122.8134 | -1.5656 | -0.31586 | 0.050354 | 0.10529 | 56.0852 | 57.1701 | 121.1334 | 122.7676 | -0.17853 | 122.7493 | 57.6004 | -0.31586 | 122.7676 | -0.17853 | 57.6004 | 121.1334 | 122.7493 | -122.9828 | -123.0148
1657.9062 | 122.8683 | -57.4402 | 65.2176 | -0.056915 | 0.0051526 | -0.00060462 | 0.0081733 | 0.0014376 | -0.0017881 | 0.0027707 | -57.4997 | 65.1993 | -57.7789 | 65.3915 | 63.7527 | 0.59052 | -1.5564 | 0.022888 | 65.2313 | -57.756 | -0.33875 | -0.01831 | -0.059509 | 122.8317 | -1.4648 | -0.31586 | 0.013733 | 0.27924 | 55.8838 | 57.4631 | 121.1929 | 122.6395 | -0.059509 | 122.6715 | 58.0307 | -0.31586 | 122.6395 | -0.059509 | 58.0307 | 121.1929 | 122.6715 | -122.9965 | -122.9736
1658.9688 | 122.85 | -58.5297 | 64.1556 | -0.19424 | 0.0040846 | 0.0077268 | 0.0006965 | -0.0011258 | 0.00077554 | 0.0027707 | -58.5342 | 64.1281 | -58.7952 | 64.2792 | 62.6541 | 0.60425 | -1.3824 | -0.23346 | 64.1647 | -58.8272 | -0.2655 | -0.027466 | -0.004578 | 122.8088 | -1.5015 | -0.29755 | 0.009155 | 0.26093 | 57.1472 | 58.2962 | 121.1838 | 122.6578 | -0.004578 | 122.6944 | 59.1339 | -0.29755 | 122.6578 | -0.004578 | 59.1339 | 121.1838 | 122.6944 | -122.9507 | -122.9828
1659.9062 | 122.8638 | -59.079 | 63.6017 | -0.064545 | 0.0055798 | 0.0015316 | 0.0062507 | -0.00069859 | -0.0022153 | 0.0025571 | -59.0744 | 63.6337 | -59.4086 | 63.739 | 62.1414 | 0.47607 | -1.9592 | -0.37537 | 63.6292 | -59.3948 | -0.32959 | 0.032043 | 0.004577 | 122.818 | -1.4603 | -0.31586 | 0.027465 | 0.33417 | 57.1197 | 58.7036 | 121.2204 | 122.7127 | 0.004577 | 122.7081 | 59.5551 | -0.31586 | 122.7127 | 0.004577 | 59.5551 | 121.2204 | 122.7081 | -123.0103 | -122.9965
1660.9531 | 122.8271 | -58.667 | 64.0228 | -0.25528 | 0.001521 | 0.0043088 | -0.0014399 | -0.003903 | -0.00050626 | 0.0027707 | -58.6624 | 64.0274 | -58.9325 | 64.1052 | 62.5351 | 0.47607 | -1.4648 | -0.26093 | 64.064 | -58.9737 | -0.2655 | 0.004578 | 0.004577 | 122.7722 | -1.4877 | -0.3067 | 0.041199 | 0.27008 | 57.2021 | 58.4061 | 121.2021 | 122.6944 | 0.004577 | 122.731 | 59.1431 | -0.3067 | 122.6944 | 0.004577 | 59.1431 | 121.2021 | 122.731 | -122.9553 | -122.9965
1661.9062 | 122.8729 | -58.1451 | 64.5081 | 1.4613 | 0.0057934 | 0.003668 | 0.0062507 | -0.0017666 | -0.0034971 | 0.0023435 | -58.0948 | 64.5447 | -58.4747 | 64.6408 | 63.0203 | 0.5722 | -1.6067 | -0.3067 | 64.5035 | -58.4747 | -0.32959 | 0.036621 | 0.050354 | 122.786 | -1.4877 | -0.32959 | -0.004578 | 0.37994 | 56.5384 | 57.8384 | 121.1655 | 122.6898 | 0.050354 | 122.6486 | 58.7173 | -0.32959 | 122.6898 | 0.050354 | 58.7173 | 121.1655 | 122.6486 | -122.9828 | -122.9828
1662.9688 | 122.9141 | -58.7311 | 63.8901 | 0.19485 | 0.0047254 | 0.0043088 | -0.0018671 | -0.002194 | -7.9062e-05 | 0.0042661 | -58.754 | 63.8763 | -59.0103 | 64.0686 | 62.4756 | 0.65918 | -1.7258 | -0.2243 | 63.9267 | -59.024 | -0.27924 | -0.013733 | -0.022888 | 122.7997 | -1.4145 | -0.29297 | 0.036621 | 0.25635 | 57.0053 | 58.5068 | 121.2067 | 122.6074 | -0.022888 | 122.6578 | 59.3903 | -0.29297 | 122.6074 | -0.022888 | 59.3903 | 121.2067 | 122.6578 | -122.9004 | -122.9141
1663.9062 | 122.8821 | -59.0149 | 63.6703 | -0.12558 | 0.004939 | 0.004736 | 0.0064643 | -0.0043302 | -0.00093346 | 0.0010617 | -59.0378 | 63.6795 | -59.3216 | 63.7894 | 62.2238 | 0.4303 | -1.1398 | -0.28381 | 63.6703 | -59.3536 | -0.3067 | 0.009155 | -0.022888 | 122.8043 | -1.4465 | -0.33874 | 0 | 0.28381 | 57.8751 | 58.7311 | 121.2387 | 122.6944 | -0.022888 | 122.6852 | 59.4452 | -0.33874 | 122.6944 | -0.022888 | 59.4452 | 121.2387 | 122.6852 | -122.9919 | -123.024
1664.9531 | 122.8088 | -59.3079 | 63.4186 | -0.2858 | 0.0047254 | 0.0032406 | 0.0051825 | -0.0047574 | -0.00071986 | 0.0017027 | -59.4681 | 63.4689 | -59.5871 | 63.4827 | 61.9034 | 0.20142 | -1.1719 | -0.55847 | 63.4369 | -59.6283 | -0.27924 | 0.050354 | -0.16022 | 122.7905 | -1.5152 | -0.32043 | 0.018311 | 0.11902 | 58.136 | 58.7494 | 121.2112 | 122.7768 | -0.16022 | 122.7448 | 59.5093 | -0.32043 | 122.7768 | -0.16022 | 59.5093 | 121.2112 | 122.7448 | -123.0057 | -123.0469
1665.9219 | 122.9324 | -59.024 | 63.588 | 0.1796 | 0.0028028 | 0.004736 | 0.0053961 | -0.0019802 | -0.0026425 | 0.0017027 | -59.024 | 63.5696 | -59.3353 | 63.8031 | 62.2147 | 0.42114 | -1.3367 | -0.54932 | 63.6017 | -59.3445 | -0.31128 | -0.018311 | 0 | 122.8271 | -1.3733 | -0.32043 | 0.013733 | 0.31128 | 57.6874 | 58.4747 | 121.2387 | 122.5937 | 0 | 122.6257 | 59.4452 | -0.32043 | 122.5937 | 0 | 59.4452 | 121.2387 | 122.6257 | -122.9233 | -122.9324
1666.9688 | 122.9416 | -59.2072 | 63.4277 | -0.079803 | 0.002162 | 0.003027 | 5.5496e-05 | -0.003903 | 0.00013454 | 0.0025571 | -59.2346 | 63.3865 | -59.5139 | 63.62 | 62.1094 | 0.68207 | -1.0666 | -0.43488 | 63.4277 | -59.5322 | -0.3067 | -0.041198 | -0.027466 | 122.8271 | -1.3184 | -0.32501 | 0 | 0.27924 | 58.1406 | 58.7723 | 121.3165 | 122.5937 | -0.027466 | 122.6349 | 59.8892 | -0.32501 | 122.5937 | -0.027466 | 59.8892 | 121.3165 | 122.6349 | -122.9416 | -122.9599
1667.9062 | 122.8729 | -59.3491 | 63.3682 | -0.17899 | 0.0030164 | 0.0075132 | 0.0081733 | -0.0036892 | -0.00050626 | 0.0010617 | -59.3491 | 63.382 | -59.6512 | 63.4735 | 61.9171 | 0.53558 | -1.1124 | -0.68207 | 63.3408 | -59.6603 | -0.30212 | 0.013733 | 0 | 122.8226 | -1.4511 | -0.31128 | -0.027466 | 0.30212 | 58.2367 | 58.667 | 121.2662 | 122.731 | 0 | 122.6898 | 59.8846 | -0.31128 | 122.731 | 0 | 59.8846 | 121.2662 | 122.6898 | -123.0194 | -123.0286
1668.9531 | 122.9507 | -59.3216 | 63.2858 | 0.065155 | 0.00066656 | 0.003027 | -0.0005853 | -0.0041166 | -0.0049923 | 0.0046933 | -59.3445 | 63.3179 | -59.61 | 63.4827 | 61.9263 | 0.55847 | -1.0208 | -0.7782 | 63.327 | -59.5871 | -0.28839 | 0.032043 | -0.022888 | 122.8043 | -1.3596 | -0.2655 | 0.041198 | 0.2655 | 58.3008 | 58.5434 | 121.2479 | 122.6395 | -0.022888 | 122.6486 | 59.8801 | -0.2655 | 122.6395 | -0.022888 | 59.8801 | 121.2479 | 122.6486 | -122.8958 | -122.8729
1669.9062 | 122.8271 | -59.2575 | 63.4094 | -0.21713 | 0.0028028 | 0.005377 | 0.0056097 | -0.0056118 | -0.0020017 | 0.0027707 | -59.3765 | 63.3728 | -59.61 | 63.4964 | 61.972 | 0.25177 | -0.60425 | -0.82855 | 63.4369 | -59.5688 | -0.35248 | -0.036621 | -0.11902 | 122.7539 | -1.4374 | -0.31128 | 0.027466 | 0.23346 | 58.6533 | 58.429 | 121.2296 | 122.6303 | -0.11902 | 122.6944 | 59.5093 | -0.31128 | 122.6303 | -0.11902 | 59.5093 | 121.2296 | 122.6944 | -123.0194 | -122.9782
1670.9688 | 122.8592 | -59.5963 | 63.1119 | -0.24765 | 0.0023756 | 0.0032406 | 0.0028327 | -0.0045438 | 0.00056194 | 0.0014889 | -59.6558 | 63.089 | -59.903 | 63.1393 | 61.7615 | 0.2243 | -0.64087 | -0.91553 | 63.1256 | -59.8846 | -0.3067 | -0.022888 | -0.05951 | 122.7356 | -1.3504 | -0.28839 | 0.013733 | 0.24719 | 58.9554 | 58.6807 | 121.3577 | 122.6852 | -0.05951 | 122.7219 | 59.8206 | -0.28839 | 122.6852 | -0.05951 | 59.8206 | 121.3577 | 122.7219 | -123.0148 | -122.9965
1671.9062 | 122.8363 | -60.3104 | 62.4023 | 0.84335 | 0.0023756 | 0.0032406 | 0.0045417 | -0.0047574 | -0.0017881 | 0.00020726 | -60.3333 | 62.384 | -60.6354 | 62.4664 | 60.9329 | 0.082397 | -0.81024 | -0.78735 | 62.3978 | -60.6262 | -0.32501 | -0.018311 | -0.022888 | 122.7768 | -1.4694 | -0.31586 | -0.004578 | 0.30212 | 59.5001 | 59.523 | 121.2433 | 122.6944 | -0.022888 | 122.7081 | 60.3928 | -0.31586 | 122.6944 | -0.022888 | 60.3928 | 121.2433 | 122.7081 | -123.0377 | -123.0286
1672.9531 | 122.8271 | -60.4706 | 62.1643 | -0.20187 | 0.0010938 | 0.0028134 | 0.0026191 | -0.0028348 | -0.00071986 | 0.0044797 | -60.5118 | 62.1368 | -60.8093 | 62.2971 | 60.7498 | 0.55847 | -0.9201 | -0.66834 | 62.1689 | -60.8047 | -0.33874 | -0.027466 | -0.041199 | 122.7676 | -1.4145 | -0.33417 | 0.004577 | 0.29755 | 59.5505 | 59.8022 | 121.2204 | 122.6074 | -0.041199 | 122.6395 | 61.0291 | -0.33417 | 122.6074 | -0.041199 | 61.0291 | 121.2204 | 122.6395 | -122.9736 | -122.9691
1673.9062 | 122.8867 | -61.0474 | 61.6287 | -0.21713 | 0.00088016 | 0.003668 | 0.0043281 | -0.0056118 | -0.0015745 | 0.0042661 | -61.0565 | 61.5601 | -61.3632 | 61.7661 | 60.228 | 0.36163 | -0.96588 | -0.737 | 61.6013 | -61.3449 | -0.31586 | -0.068664 | -0.009156 | 122.8134 | -1.4008 | -0.29755 | -0.027466 | 0.3067 | 60.0815 | 60.3104 | 121.2753 | 122.6074 | -0.009156 | 122.6486 | 61.409 | -0.29755 | 122.6074 | -0.009156 | 61.409 | 121.2753 | 122.6486 | -122.9919 | -122.9736
1674.9531 | 122.9507 | -61.8256 | 60.8002 | -0.17899 | -0.00061524 | -0.00017722 | 0.0081733 | -0.0026212 | -0.00093346 | 0.0027707 | -61.8713 | 60.7636 | -62.1048 | 61.1069 | 59.5093 | 0.14191 | -1.0437 | -0.91095 | 60.8093 | -62.114 | -0.27923 | -0.036621 | -0.045776 | 122.9324 | -1.2909 | -0.28839 | 0.009155 | 0.23346 | 60.7819 | 60.9146 | 121.3348 | 122.5891 | -0.045776 | 122.6349 | 61.9675 | -0.28839 | 122.5891 | -0.045776 | 61.9675 | 121.3348 | 122.6349 | -122.905 | -122.9141
1675.9219 | 122.9874 | -62.5717 | 60.0128 | 0.29404 | 0.0025892 | 0.0058042 | 0.0094549 | -0.0041166 | -0.0037107 | 0.0025571 | -62.5168 | 60.0494 | -62.8418 | 60.2875 | 58.7494 | -0.068665 | -1.4557 | -1.1948 | 60.0403 | -62.8738 | -0.27008 | 0.036621 | 0.054931 | 122.8592 | -1.2634 | -0.30212 | 0.027466 | 0.32501 | 61.116 | 61.377 | 121.3211 | 122.6212 | 0.054931 | 122.612 | 62.5031 | -0.30212 | 122.6212 | 0.054931 | 62.5031 | 121.3211 | 122.612 | -122.8546 | -122.8867
1676.9688 | 122.8729 | -61.9537 | 60.6995 | 0.14145 | 0.001521 | 0.0038816 | 0.0024053 | -0.0053982 | -7.9062e-05 | 0.0044797 | -61.9675 | 60.6674 | -62.233 | 60.8368 | 59.3628 | 0.16022 | -0.9613 | -1.0574 | 60.6903 | -62.2421 | -0.27924 | -0.032044 | -0.013733 | 122.7905 | -1.3367 | -0.28839 | -0.009155 | 0.2655 | 60.9924 | 60.8963 | 121.3165 | 122.6212 | -0.013733 | 122.644 | 62.114 | -0.28839 | 122.6212 | -0.013733 | 62.114 | 121.3165 | 122.644 | -122.9324 | -122.9416
1677.9062 | 122.8271 | -107.341 | 15.3763 | -0.11795 | 0.0010938 | 0.0043088 | 0.030604 | -0.0062528 | 0.0016299 | 0.016229 | -107.1991 | 15.3168 | -107.6431 | 15.3259 | 14.7263 | -6.3858 | -9.3475 | -10.4553 | 15.4083 | -107.6889 | -0.30212 | -0.05951 | 0.14191 | 122.6669 | -0.65002 | -0.3479 | 0.032043 | 0.44403 | 97.9935 | 96.8857 | 122.0673 | 122.6578 | 0.14191 | 122.7493 | 100.9552 | -0.3479 | 122.6578 | 0.14191 | 100.9552 | 122.0673 | 122.7493 | -123.0194 | -123.0652
1678.9531 | 122.9507 | -109.0713 | 13.5864 | -0.10269 | 0.00066656 | 0.0023862 | 0.042353 | -0.0053982 | 0.00013454 | 0.031823 | -108.9432 | 13.5315 | -109.3964 | 13.6459 | 13.0966 | -7.3517 | -9.5032 | -10.7254 | 13.6139 | -109.3872 | -0.32501 | -0.054932 | 0.12817 | 122.7173 | -0.48981 | -0.31586 | 0.027466 | 0.45319 | 99.5682 | 98.3459 | 122.168 | 122.6028 | 0.12817 | 122.6852 | 101.7197 | -0.31586 | 122.6028 | 0.12817 | 101.7197 | 122.168 | 122.6852 | -122.9828 | -122.9736
1679.9062 | 122.7448 | -109.6344 | 13.1378 | -0.17136 | 0.0030164 | 0.006445 | 0.065638 | -0.0079618 | -0.0017881 | 0.048272 | -109.5566 | 13.0234 | -109.9823 | 12.9684 | 12.4832 | -7.8918 | -9.5215 | -10.4095 | 13.1332 | -109.9411 | -0.3479 | -0.11444 | 0.077819 | 122.6028 | -0.6546 | -0.3067 | -0.004577 | 0.42572 | 100.1129 | 99.2249 | 122.1176 | 122.6578 | 0.077819 | 122.7676 | 101.7426 | -0.3067 | 122.6578 | 0.077819 | 101.7426 | 122.1176 | 122.7676 | -123.1201 | -123.0789
1680.9688 | 122.9141 | -110.3897 | 12.3322 | 0.1796 | 0.0034436 | 0.0017454 | 0.089563 | -0.002194 | -0.0017881 | 0.075616 | -110.1791 | 12.2635 | -110.6506 | 12.3093 | 11.8286 | -7.8918 | -10.2997 | -10.6293 | 12.3367 | -110.6735 | -0.26093 | -0.068664 | 0.21057 | 122.699 | -0.50354 | -0.28381 | 0.004578 | 0.4715 | 100.09 | 99.7604 | 122.2183 | 122.6532 | 0.21057 | 122.7264 | 102.4979 | -0.28381 | 122.6532 | 0.21057 | 102.4979 | 122.2183 | 122.7264 | -122.9828 | -123.0057
1681.9062 | 122.9004 | -110.9253 | 11.7966 | -0.21713 | 2.5564e-05 | 0.005377 | 0.10644 | -0.0053982 | -0.0011471 | 0.093347 | -110.7056 | 11.7233 | -111.2183 | 11.8011 | 11.2839 | -7.6538 | -10.0937 | -10.6018 | 11.8149 | -111.1908 | -0.29297 | -0.073242 | 0.21973 | 122.7264 | -0.51269 | -0.2655 | 0.01831 | 0.5127 | 100.8316 | 100.3235 | 122.2092 | 122.6486 | 0.21973 | 122.7402 | 103.2715 | -0.2655 | 122.6486 | 0.21973 | 103.2715 | 122.2092 | 122.7402 | -123.0148 | -122.9874
1682.9531 | 122.937 | -111.7172 | 10.9314 | 0.20248 | 0.002162 | -0.00060462 | 0.13507 | -0.0053982 | 0.00034814 | 0.12026 | -111.6211 | 10.8261 | -112.0789 | 10.8994 | 10.4782 | -7.9468 | -10.2081 | -10.5606 | 10.9543 | -112.0285 | -0.36163 | -0.10529 | 0.09613 | 122.6166 | -0.45319 | -0.31128 | 0.022889 | 0.45776 | 101.5091 | 101.1566 | 122.1954 | 122.5433 | 0.09613 | 122.6715 | 103.7704 | -0.31128 | 122.5433 | 0.09613 | 103.7704 | 122.1954 | 122.6715 | -123.0103 | -122.9599
1683.9062 | 122.8729 | -112.2208 | 10.5194 | -0.26291 | 0.00023916 | 0.003668 | 0.1622 | -0.0043302 | -0.00071986 | 0.14739 | -112.0193 | 10.4233 | -112.4817 | 10.4233 | 9.9792 | -8.2214 | -10.4095 | -10.5331 | 10.5148 | -112.5046 | -0.26093 | -0.09613 | 0.20142 | 122.644 | -0.54016 | -0.28381 | -0.004577 | 0.46234 | 101.8112 | 101.6876 | 122.2 | 122.644 | 0.20142 | 122.7356 | 103.9993 | -0.28381 | 122.644 | 0.20142 | 103.9993 | 122.2 | 122.7356 | -123.0011 | -123.024
1684.9688 | 122.8638 | -112.7289 | 9.938 | 0.24063 | 2.5564e-05 | 0.0028134 | 0.20834 | -0.004971 | 0.00013454 | 0.19824 | -112.6144 | 9.8602 | -113.0035 | 9.8877 | 9.4528 | -8.3313 | -9.787 | -10.849 | 9.9701 | -113.0264 | -0.27466 | -0.07782 | 0.11444 | 122.6166 | -0.48523 | -0.29755 | 0.032044 | 0.3891 | 102.9419 | 101.8799 | 122.1817 | 122.5891 | 0.11444 | 122.699 | 104.3976 | -0.29755 | 122.5891 | 0.11444 | 104.3976 | 122.1817 | 122.699 | -122.9416 | -122.9645
1685.9062 | 122.7585 | -113.9053 | 8.8348 | 0.14908 | 0.0038708 | 0.008154 | 0.32861 | -0.0030484 | 0.00077554 | 0.31146 | -113.7085 | 8.7799 | -114.1525 | 8.6105 | 8.2169 | -8.6151 | -10.0845 | -11.1557 | 8.8165 | -114.2349 | -0.24719 | -0.054932 | 0.19684 | 122.5159 | -0.61798 | -0.32959 | -0.018311 | 0.44403 | 103.8208 | 102.7496 | 122.1222 | 122.6852 | 0.19684 | 122.7219 | 105.2902 | -0.32959 | 122.6852 | 0.19684 | 105.2902 | 122.1222 | 122.7219 | -122.9874 | -123.0698
1686.9062 | 122.7631 | -86.0779 | 36.4563 | -0.13321 | -0.00040164 | 0.003027 | 2.1158 | -0.00668 | 0.0012027 | 2.1179 | -85.7803 | 36.5845 | -86.1053 | 36.6806 | 35.8978 | -3.479 | -4.9805 | -5.6854 | 36.3052 | -86.1832 | -0.027466 | 0.12817 | 0.29755 | 122.7585 | -0.55847 | -0.10529 | -0.15106 | 0.32501 | 81.0974 | 80.3925 | 121.9757 | 122.6624 | 0.29755 | 122.3831 | 82.5989 | -0.10529 | 122.6624 | 0.29755 | 82.5989 | 121.9757 | 122.3831 | -122.5616 | -122.6395
1687.9531 | 101.5228 | -119.4489 | 3.1631 | -0.056915 | -0.00040164 | 0.0023862 | 0.016932 | -0.0064664 | -7.9062e-05 | 0.0036253 | -119.3069 | 3.067 | -119.7876 | 3.0487 | 2.7603 | -9.1919 | -10.6201 | -10.231 | 3.1815 | -119.7876 | -0.33875 | -0.09613 | 0.14191 | 122.4976 | -0.40283 | -0.33875 | 0.018311 | 0.48065 | 108.8287 | 109.2178 | 122.2092 | 122.5159 | 0.14191 | 122.6303 | 110.257 | -0.33875 | 122.5159 | 0.14191 | 110.257 | 122.2092 | 122.6303 | -122.9507 | -122.9507
1688.9062 | 122.7997 | -119.5862 | 3.1219 | -0.23239 | -0.0010424 | 0.00046358 | 0.018641 | -0.0053982 | -0.0015745 | 0.0029843 | -119.3481 | 3.035 | -119.8517 | 2.9755 | 2.6825 | -9.5306 | -10.1166 | -10.524 | 3.1448 | -119.8837 | -0.2655 | -0.086975 | 0.23804 | 122.5616 | -0.43945 | -0.29755 | 0.022888 | 0.50354 | 109.4696 | 109.0622 | 122.2687 | 122.6212 | 0.23804 | 122.731 | 110.0555 | -0.29755 | 122.6212 | 0.23804 | 110.0555 | 122.2687 | 122.731 | -122.9736 | -123.0057
1689.9688 | 122.8867 | -120.4285 | 2.2385 | 0.59158 | -0.00040164 | 0.0055906 | 0.022913 | -0.0030484 | -0.0026425 | 0.0044797 | -120.2087 | 2.1149 | -120.7352 | 2.1561 | 1.8585 | -9.8923 | -8.3679 | -10.7346 | 2.2659 | -120.7214 | -0.3067 | -0.1236 | 0.21973 | 122.5845 | -0.37994 | -0.29297 | 0.027466 | 0.52643 | 112.0605 | 109.6939 | 122.287 | 122.5433 | 0.21973 | 122.6944 | 110.5362 | -0.29297 | 122.5433 | 0.21973 | 110.5362 | 122.287 | 122.6944 | -122.9736 | -122.9599
1690.9062 | 122.7859 | -120.3735 | 2.3987 | -0.25528 | 0.0028028 | 0.0045224 | 0.022059 | -0.0064664 | -0.0026425 | 0.0046933 | -120.195 | 2.3849 | -120.6345 | 2.2293 | 1.9226 | -9.9701 | -9.2377 | -10.9497 | 2.4353 | -120.6619 | -0.26093 | -0.013733 | 0.17853 | 122.6028 | -0.47608 | -0.28839 | 0.036621 | 0.43945 | 111.1359 | 109.4238 | 122.2961 | 122.7585 | 0.17853 | 122.8088 | 110.4034 | -0.28839 | 122.7585 | 0.17853 | 110.4034 | 122.2961 | 122.8088 | -123.0331 | -123.0606
1691.9688 | 122.8455 | -120.2408 | 2.4673 | 0.27115 | 0.00045296 | 0.0043088 | 0.015436 | -0.0064664 | -0.00093346 | 0.0036253 | -119.9753 | 2.3621 | -120.5292 | 2.3392 | 2.0554 | -10.0342 | -9.2239 | -10.5927 | 2.5177 | -120.5383 | -0.28839 | -0.10528 | 0.2655 | 122.58 | -0.41199 | -0.29755 | 0.050354 | 0.55389 | 111.0168 | 109.6481 | 122.2961 | 122.6028 | 0.2655 | 122.7585 | 110.2066 | -0.29755 | 122.6028 | 0.2655 | 110.2066 | 122.2961 | 122.7585 | -122.9965 | -123.0057
1692.9062 | 122.8821 | -120.2499 | 2.449 | -0.19424 | 0.00066656 | 0.0028134 | 0.02035 | -0.0064664 | -0.00050626 | 0.0044797 | -120.0439 | 2.3621 | -120.5383 | 2.33 | 2.0462 | -9.8602 | -8.8806 | -10.2402 | 2.4628 | -120.5658 | -0.28839 | -0.086975 | 0.20599 | 122.58 | -0.40283 | -0.31586 | 0.013733 | 0.49439 | 111.3693 | 110.0098 | 122.2961 | 122.612 | 0.20599 | 122.7127 | 110.3897 | -0.31586 | 122.612 | 0.20599 | 110.3897 | 122.2961 | 122.7127 | -122.9874 | -123.0148
1693.9688 | 122.9187 | -120.0668 | 2.6138 | -0.072174 | -0.0010424 | 0.0032406 | 0.018427 | -0.0056118 | -0.0022153 | 0.0029843 | -119.87 | 2.5406 | -120.3461 | 2.5452 | 2.2568 | -9.137 | -7.8827 | -10.0204 | 2.6321 | -120.3598 | -0.27924 | -0.073243 | 0.19684 | 122.612 | -0.35706 | -0.29297 | 0.01831 | 0.47607 | 112.1841 | 110.0464 | 122.3236 | 122.6074 | 0.19684 | 122.699 | 110.9299 | -0.29297 | 122.6074 | 0.19684 | 110.9299 | 122.3236 | 122.699 | -122.9599 | -122.9736
1694.9062 | 122.7997 | -120.2454 | 2.5131 | -0.22476 | 0.0030164 | 0.0051632 | 0.020991 | -0.0058256 | -0.0037107 | 0.0036253 | -120.076 | 2.4078 | -120.5109 | 2.3209 | 2.0187 | -9.7137 | -8.2443 | -10.2264 | 2.5497 | -120.575 | -0.2655 | -0.10529 | 0.16937 | 122.5662 | -0.49439 | -0.32959 | 0.036621 | 0.43487 | 112.001 | 110.0189 | 122.2641 | 122.6532 | 0.16937 | 122.7951 | 110.5316 | -0.32959 | 122.6532 | 0.16937 | 110.5316 | 122.2641 | 122.7951 | -123.024 | -123.0881
1695.9688 | 122.905 | -120.1813 | 2.5452 | -0.10269 | 0.00066656 | 0.00067718 | 0.017573 | -0.0075344 | -7.9062e-05 | 0.0040525 | -119.9615 | 2.4536 | -120.4422 | 2.5314 | 2.211 | -9.7275 | -9.0546 | -10.611 | 2.5772 | -120.4605 | -0.26093 | -0.091553 | 0.21973 | 122.7127 | -0.33417 | -0.27924 | 0.032043 | 0.48065 | 111.1267 | 109.5703 | 122.3923 | 122.6349 | 0.21973 | 122.7585 | 110.4538 | -0.27924 | 122.6349 | 0.21973 | 110.4538 | 122.3923 | 122.7585 | -122.9874 | -123.0057
1696.9062 | 122.8958 | -120.2545 | 2.4124 | -0.22476 | -0.00040164 | 0.0045224 | 0.018427 | -0.0045438 | -0.0030697 | 0.0029843 | -120.0714 | 2.3346 | -120.5887 | 2.3438 | 2.0508 | -9.8785 | -8.9722 | -10.5286 | 2.4399 | -120.5658 | -0.33417 | -0.07782 | 0.18311 | 122.5983 | -0.36163 | -0.31128 | 0.027465 | 0.51727 | 111.2823 | 109.726 | 122.3053 | 122.5891 | 0.18311 | 122.6944 | 110.376 | -0.31128 | 122.5891 | 0.18311 | 110.376 | 122.3053 | 122.6944 | -123.0011 | -122.9782
1697.9688 | 122.905 | -120.3003 | 2.4124 | -0.072174 | 0.002162 | 0.00067718 | 0.017145 | -0.0060392 | -0.0026425 | 0.0044797 | -120.076 | 2.3392 | -120.5566 | 2.3163 | 2.0325 | -9.6771 | -8.6746 | -10.5698 | 2.4445 | -120.5933 | -0.25635 | -0.073243 | 0.2243 | 122.6166 | -0.37994 | -0.29297 | 0.032043 | 0.48065 | 111.6257 | 109.7305 | 122.3328 | 122.6395 | 0.2243 | 122.7448 | 110.6232 | -0.29297 | 122.6395 | 0.2243 | 110.6232 | 122.3328 | 122.7448 | -122.9691 | -123.0057
1698.9062 | 122.9187 | -120.2774 | 2.4353 | -0.27054 | -0.001256 | 0.00089078 | 0.019709 | -0.0056118 | -0.0030697 | 0.0023435 | -120.0851 | 2.3392 | -120.5704 | 2.3575 | 2.0691 | -9.8007 | -8.4961 | -10.6064 | 2.4536 | -120.5887 | -0.29297 | -0.096131 | 0.19226 | 122.6349 | -0.36621 | -0.31128 | 0.01831 | 0.48523 | 111.7813 | 109.671 | 122.3465 | 122.6166 | 0.19226 | 122.731 | 110.4767 | -0.31128 | 122.6166 | 0.19226 | 110.4767 | 122.3465 | 122.731 | -123.0057 | -123.024
1699.9688 | 122.85 | -120.1721 | 2.5177 | 0.1796 | 0.0019482 | 0.0023862 | 0.018854 | -0.0051846 | -0.00029266 | 0.0025571 | -119.9982 | 2.4261 | -120.4514 | 2.417 | 2.1057 | -10.1715 | -8.0658 | -10.7849 | 2.5269 | -120.4834 | -0.27924 | -0.091553 | 0.17395 | 122.5891 | -0.41199 | -0.31128 | 0.009155 | 0.45319 | 112.1063 | 109.3872 | 122.2778 | 122.5983 | 0.17395 | 122.699 | 110.0006 | -0.31128 | 122.5983 | 0.17395 | 110.0006 | 122.2778 | 122.699 | -122.9691 | -123.0011
1700.9219 | 122.7631 | -120.1263 | 2.655 | 0.14145 | 0.006648 | 0.0068722 | 0.022699 | -0.0073208 | -0.0015745 | 0.0040525 | -119.8334 | 2.5406 | -120.3918 | 2.3438 | 2.1057 | -10.5469 | -8.6243 | -11.174 | 2.6505 | -120.4605 | -0.2655 | -0.11444 | 0.29297 | 122.4701 | -0.54932 | -0.33417 | -0.004577 | 0.55847 | 111.5021 | 108.9523 | 122.2321 | 122.6669 | 0.29297 | 122.7768 | 109.5795 | -0.33417 | 122.6669 | 0.29297 | 109.5795 | 122.2321 | 122.7768 | -123.0469 | -123.1155
1701.9531 | 122.8775 | -120.5246 | 2.1561 | 0.095673 | -0.0014696 | 0.0032406 | 0.016504 | -0.0047574 | -0.00050626 | 0.0038389 | -120.4468 | 2.0828 | -120.9457 | 2.0279 | 1.7075 | -10.3546 | -9.0134 | -11.0916 | 2.179 | -120.8359 | -0.42114 | -0.073242 | 0.07782 | 122.5525 | -0.44861 | -0.31128 | 0.022888 | 0.49896 | 111.5112 | 109.433 | 122.2321 | 122.6074 | 0.07782 | 122.7036 | 110.17 | -0.31128 | 122.6074 | 0.07782 | 110.17 | 122.2321 | 122.7036 | -123.1018 | -122.9919
1702.9062 | 122.8912 | -120.5658 | 2.1652 | -0.18662 | 0.00088016 | 0.0023862 | 0.019709 | -0.0064664 | -0.0011471 | 0.0053343 | -120.3415 | 2.0737 | -120.8405 | 2.0462 | 1.7853 | -10.1715 | -9.1141 | -11.1374 | 2.1881 | -120.8725 | -0.27466 | -0.091553 | 0.2243 | 122.612 | -0.37994 | -0.3067 | 0.022888 | 0.49896 | 111.4517 | 109.4284 | 122.3511 | 122.6395 | 0.2243 | 122.7539 | 110.3943 | -0.3067 | 122.6395 | 0.2243 | 110.3943 | 122.3511 | 122.7539 | -123.0057 | -123.0377
1703.9531 | 122.8775 | -120.5933 | 2.1103 | -0.2095 | 0.0010938 | 0.0040952 | 0.019922 | -0.0053982 | -0.0028561 | 0.0034115 | -120.4193 | 2.0187 | -120.8862 | 1.9821 | 1.7303 | -9.8969 | -8.9218 | -11.2152 | 2.1057 | -120.8679 | -0.29297 | -0.091553 | 0.17395 | 122.5754 | -0.37994 | -0.27466 | -0.004578 | 0.46692 | 111.6714 | 109.3781 | 122.3236 | 122.612 | 0.17395 | 122.699 | 110.6964 | -0.27466 | 122.612 | 0.17395 | 110.6964 | 122.3236 | 122.699 | -122.9965 | -122.9782
1704.9062 | 122.8821 | -120.7077 | 2.0325 | -0.17136 | -0.0023242 | 0.0025998 | 0.018427 | -0.0064664 | -0.0017881 | 0.0049069 | -120.4605 | 1.918 | -120.9824 | 1.9318 | 1.6891 | -9.6909 | -9.1278 | -11.2747 | 2.0554 | -120.9732 | -0.27466 | -0.11444 | 0.24719 | 122.6395 | -0.34332 | -0.2655 | 0.022888 | 0.52185 | 111.5799 | 109.433 | 122.3969 | 122.6257 | 0.24719 | 122.7631 | 111.0168 | -0.2655 | 122.6257 | 0.24719 | 111.0168 | 122.3969 | 122.7631 | -123.0148 | -123.0057
1705.9531 | 122.8592 | -120.4376 | 2.2659 | -0.12558 | 0.0017346 | -0.00017722 | 0.017786 | -0.0053982 | -0.0013609 | 0.0027707 | -120.1996 | 2.1927 | -120.7031 | 2.1973 | 1.918 | -9.9014 | -8.4778 | -11.1694 | 2.298 | -120.7397 | -0.2655 | -0.073242 | 0.23804 | 122.6349 | -0.3479 | -0.30212 | 0.032044 | 0.50354 | 111.9598 | 109.2682 | 122.3557 | 122.6303 | 0.23804 | 122.7356 | 110.5362 | -0.30212 | 122.6303 | 0.23804 | 110.5362 | 122.3557 | 122.7356 | -122.9691 | -123.0057
1706.9062 | 122.9095 | -120.7306 | 1.9638 | -0.087433 | 2.5564e-05 | 0.0045224 | 0.021418 | -0.004971 | -0.00029266 | 0.0031979 | -120.52 | 1.8768 | -121.0464 | 1.8906 | 1.6067 | -9.8465 | -9.2239 | -11.4441 | 2.0187 | -121.0327 | -0.31586 | -0.086975 | 0.21057 | 122.6212 | -0.35706 | -0.30212 | 0.054932 | 0.52643 | 111.5067 | 109.2865 | 122.3373 | 122.6074 | 0.21057 | 122.7493 | 110.8841 | -0.30212 | 122.6074 | 0.21057 | 110.8841 | 122.3373 | 122.7493 | -123.0103 | -122.9965
1707.9688 | 122.9004 | -120.9 | 1.8036 | -0.072174 | -0.0025378 | 0.003027 | 0.018 | -0.0051846 | -0.0028561 | 0.0040525 | -120.7169 | 1.6983 | -121.2112 | 1.712 | 1.4191 | -10.0708 | -9.082 | -11.5036 | 1.8219 | -121.2204 | -0.31128 | -0.10529 | 0.1831 | 122.612 | -0.38452 | -0.32044 | 0.01831 | 0.49438 | 111.8179 | 109.3964 | 122.319 | 122.5983 | 0.1831 | 122.7219 | 110.8292 | -0.32044 | 122.5983 | 0.1831 | 110.8292 | 122.319 | 122.7219 | -123.0148 | -123.024
1708.9062 | 122.7951 | -120.9686 | 1.8127 | -0.36209 | 0.00088016 | 0.00089078 | 0.021204 | -0.0051846 | -0.0020017 | 0.0019163 | -120.8038 | 1.7303 | -121.257 | 1.5884 | 1.3229 | -9.8557 | -9.2148 | -11.5036 | 1.8539 | -121.2616 | -0.28839 | -0.082397 | 0.16479 | 122.5571 | -0.48981 | -0.29297 | 0.041199 | 0.45319 | 111.7538 | 109.465 | 122.2916 | 122.699 | 0.16479 | 122.8226 | 111.113 | -0.29297 | 122.699 | 0.16479 | 111.113 | 122.2916 | 122.8226 | -123.0698 | -123.0743
1709.9531 | 122.9462 | -120.9457 | 1.7487 | -0.11032 | 0.00088016 | 0.0049496 | 0.017786 | -0.0056118 | -0.0015745 | 0.0040525 | -120.7489 | 1.68 | -121.2708 | 1.6846 | 1.4008 | -9.9564 | -8.8898 | -11.2839 | 1.7899 | -121.2387 | -0.32501 | -0.068664 | 0.19684 | 122.6303 | -0.3479 | -0.29297 | 0.041199 | 0.52185 | 112.056 | 109.6619 | 122.3465 | 122.6257 | 0.19684 | 122.7356 | 110.9894 | -0.29297 | 122.6257 | 0.19684 | 110.9894 | 122.3465 | 122.7356 | -123.0194 | -122.9874
1710.9062 | 122.905 | -121.0098 | 1.7029 | -0.12558 | -0.001256 | 0.0011044 | 0.016504 | -0.0064664 | -0.00093346 | 0.0019163 | -120.7855 | 1.6296 | -121.2982 | 1.6388 | 1.3687 | -9.7458 | -8.5007 | -11.087 | 1.7441 | -121.3348 | -0.28839 | -0.073242 | 0.22431 | 122.6486 | -0.33417 | -0.32501 | 0.041199 | 0.5127 | 112.5092 | 109.9228 | 122.3785 | 122.6395 | 0.22431 | 122.7539 | 111.264 | -0.32501 | 122.6395 | 0.22431 | 111.264 | 122.3785 | 122.7539 | -123.0011 | -123.0377
1711.9531 | 122.9004 | -121.0556 | 1.6663 | 0.049896 | -0.001256 | 0.006445 | 0.017359 | -0.0060392 | -0.0022153 | 0.0034115 | -120.8908 | 1.5747 | -121.3623 | 1.5472 | 1.2817 | -9.8328 | -9.1141 | -11.0092 | 1.7075 | -121.3211 | -0.3067 | -0.091553 | 0.16479 | 122.6028 | -0.38452 | -0.2655 | 0.041198 | 0.4715 | 111.9415 | 110.0464 | 122.3373 | 122.6303 | 0.16479 | 122.7631 | 111.2228 | -0.2655 | 122.6303 | 0.16479 | 111.2228 | 122.3373 | 122.7631 | -123.0286 | -122.9874
1712.9062 | 122.8271 | -121.2158 | 1.5472 | -0.21713 | 0.0023756 | 0.001318 | 0.022699 | -0.0075344 | -0.0020017 | 0.0034115 | -121.0876 | 1.442 | -121.5637 | 1.3046 | 1.03 | -9.3292 | -9.0775 | -10.7666 | 1.5701 | -121.5363 | -0.3479 | -0.10529 | 0.12817 | 122.5204 | -0.51727 | -0.32044 | 0.022888 | 0.47607 | 112.1384 | 110.4492 | 122.2458 | 122.6578 | 0.12817 | 122.7859 | 111.8866 | -0.32044 | 122.6578 | 0.12817 | 111.8866 | 122.2458 | 122.7859 | -123.111 | -123.0835
1713.9531 | 122.9324 | -121.225 | 1.4786 | -0.10269 | 0.00045296 | 0.00046358 | 0.015864 | -0.0043302 | -0.00029266 | 0.0027707 | -121.0373 | 1.4191 | -121.5179 | 1.4053 | 1.149 | -9.4391 | -9.5856 | -10.6613 | 1.506 | -121.5317 | -0.29297 | -0.05951 | 0.18768 | 122.6303 | -0.32959 | -0.3067 | 0.027465 | 0.48065 | 111.6394 | 110.5637 | 122.374 | 122.644 | 0.18768 | 122.731 | 111.7859 | -0.3067 | 122.644 | 0.18768 | 111.7859 | 122.374 | 122.731 | -122.9965 | -123.0103
1714.9062 | 122.8729 | -121.1563 | 1.5884 | -0.17899 | 0.0023756 | 0.00089078 | 0.019495 | -0.004971 | 0.00034814 | 0.0051205 | -120.9366 | 1.4877 | -121.431 | 1.4648 | 1.2222 | -9.0866 | -9.6542 | -10.8948 | 1.5839 | -121.4493 | -0.27466 | -0.10071 | 0.21973 | 122.6212 | -0.36621 | -0.29297 | -0.004578 | 0.49439 | 111.5021 | 110.2615 | 122.3785 | 122.644 | 0.21973 | 122.7402 | 112.0697 | -0.29297 | 122.644 | 0.21973 | 112.0697 | 122.3785 | 122.7402 | -123.0194 | -123.0377
1715.9688 | 122.9187 | -121.2341 | 1.4877 | -2.9027 | -0.00061524 | 0.0068722 | 0.019922 | -0.0043302 | -0.0024289 | 0.0023435 | -121.0922 | 1.4008 | -121.5134 | 1.4328 | 1.181 | -7.5073 | -10.0571 | -10.4874 | 1.5244 | -121.5454 | -0.27924 | -0.086975 | 0.14191 | 122.6669 | -0.3067 | -0.31128 | 0.036621 | 0.42114 | 111.1771 | 110.7468 | 122.4152 | 122.6349 | 0.14191 | 122.7585 | 113.7268 | -0.31128 | 122.6349 | 0.14191 | 113.7268 | 122.4152 | 122.7585 | -123.0011 | -123.0331
1716.9062 | 122.9233 | -121.257 | 1.4877 | -0.12558 | -0.00040164 | 0.00046358 | 0.017786 | -0.00668 | -0.0032835 | 0.0025571 | -121.0373 | 1.3916 | -121.55 | 1.387 | 1.1261 | -8.2443 | -9.9106 | -10.4187 | 1.4923 | -121.5179 | -0.29297 | -0.09613 | 0.21973 | 122.644 | -0.36163 | -0.26093 | 0.004578 | 0.5127 | 111.3464 | 110.8383 | 122.3831 | 122.6486 | 0.21973 | 122.7493 | 113.0127 | -0.26093 | 122.6486 | 0.21973 | 113.0127 | 122.3831 | 122.7493 | -123.0377 | -123.0057
1717.9688 | 122.9004 | -121.3394 | 1.4191 | -0.034027 | 0.0010938 | 0.0043088 | 0.016504 | -0.0053982 | -0.0030697 | 0.0059751 | -121.1563 | 1.2909 | -121.6278 | 1.268 | 1.0529 | -8.4961 | -9.9976 | -10.8719 | 1.4328 | -121.6141 | -0.28839 | -0.12817 | 0.18311 | 122.6074 | -0.36621 | -0.27466 | 0.013733 | 0.4715 | 111.3419 | 110.4675 | 122.3923 | 122.6303 | 0.18311 | 122.7722 | 112.8433 | -0.27466 | 122.6303 | 0.18311 | 112.8433 | 122.3923 | 122.7722 | -123.0469 | -123.0331
1718.9062 | 122.9004 | -121.3257 | 1.4053 | -0.19424 | 2.5564e-05 | 0.00024998 | 0.017145 | -0.0058256 | -0.00050626 | 0.0031979 | -121.1197 | 1.3184 | -121.6461 | 1.2909 | 1.0345 | -7.9605 | -9.9426 | -11.3251 | 1.442 | -121.6095 | -0.32043 | -0.086975 | 0.20599 | 122.6166 | -0.37079 | -0.28381 | 0.036622 | 0.52643 | 111.3831 | 110.0006 | 122.3602 | 122.644 | 0.20599 | 122.7676 | 113.3652 | -0.28381 | 122.644 | 0.20599 | 113.3652 | 122.3602 | 122.7676 | -123.0515 | -123.0148
1719.9688 | 122.8683 | -121.6507 | 1.0803 | 0.042267 | 0.0017346 | 0.001318 | 0.019922 | -0.0051846 | -0.0011471 | 0.0038389 | -121.5729 | 1.0208 | -122.0078 | 0.94757 | 0.67749 | -7.4432 | -10.1852 | -11.4395 | 1.0849 | -121.9254 | -0.35706 | -0.059509 | 0.07782 | 122.5983 | -0.40283 | -0.27466 | 0.004578 | 0.43488 | 111.4655 | 110.2112 | 122.3282 | 122.6715 | 0.07782 | 122.7356 | 114.2075 | -0.27466 | 122.6715 | 0.07782 | 114.2075 | 122.3282 | 122.7356 | -123.0881 | -123.0057
1720.9062 | 122.8134 | -121.6324 | 1.1902 | -0.16373 | 0.0042982 | 0.0011044 | 0.023768 | -0.004971 | -0.00029266 | 0.0031979 | -121.431 | 1.1078 | -121.9116 | 0.96588 | 0.70496 | -7.6859 | -10.0204 | -11.6638 | 1.1993 | -121.962 | -0.27924 | -0.082398 | 0.20142 | 122.5983 | -0.48523 | -0.32959 | 0.009155 | 0.48065 | 111.6119 | 109.9686 | 122.3373 | 122.7402 | 0.20142 | 122.8317 | 113.9465 | -0.32959 | 122.7402 | 0.20142 | 113.9465 | 122.3373 | 122.8317 | -123.1018 | -123.1522
1721.9531 | 122.8867 | -121.4951 | 1.2131 | 1.0493 | 0.0013074 | 0.001318 | 0.019068 | -0.0062528 | -0.00071986 | 0.0025571 | -121.3852 | 1.1215 | -121.8384 | 1.0208 | 0.79193 | -8.0429 | -10.0891 | -11.9614 | 1.181 | -121.8475 | -0.34332 | -0.091553 | 0.10986 | 122.5159 | -0.42114 | -0.35248 | -0.032044 | 0.45319 | 111.4059 | 109.5337 | 122.287 | 122.6166 | 0.10986 | 122.6761 | 113.4521 | -0.35248 | 122.6166 | 0.10986 | 113.4521 | 122.287 | 122.6761 | -123.0515 | -123.0606
1722.9062 | 122.8088 | -121.6187 | 1.149 | -0.12558 | 0.00045296 | -0.00039102 | 0.021418 | -0.0047574 | -0.0011471 | 0.0042661 | -121.4447 | 1.0803 | -121.9162 | 0.94757 | 0.67291 | -8.3267 | -9.5078 | -12.2223 | 1.1856 | -121.9299 | -0.29755 | -0.068665 | 0.17395 | 122.5662 | -0.47607 | -0.31128 | 0.036621 | 0.4715 | 112.1109 | 109.3964 | 122.2916 | 122.699 | 0.17395 | 122.8043 | 113.2919 | -0.31128 | 122.699 | 0.17395 | 113.2919 | 122.2916 | 122.8043 | -123.0652 | -123.0789
1723.9531 | 122.9233 | -121.5271 | 1.1856 | -0.072174 | -0.00018804 | 0.0032406 | 0.018213 | -0.0060392 | -0.0028561 | 0.0042661 | -121.3348 | 1.1032 | -121.8521 | 1.0803 | 0.84686 | -8.4503 | -10.1166 | -11.7142 | 1.2131 | -121.8246 | -0.32501 | -0.082398 | 0.19226 | 122.6074 | -0.33874 | -0.29755 | 0.027466 | 0.51727 | 111.4105 | 109.8129 | 122.374 | 122.6303 | 0.19226 | 122.7402 | 113.0768 | -0.29755 | 122.6303 | 0.19226 | 113.0768 | 122.374 | 122.7402 | -123.0377 | -123.0103
1724.9062 | 122.8958 | -121.5454 | 1.1581 | -0.087433 | 0.001521 | 0.0072996 | 0.018427 | -0.0073208 | -0.0030697 | 0.0038389 | -121.3348 | 1.062 | -121.843 | 1.0712 | 0.81482 | -8.8394 | -9.7549 | -11.8011 | 1.1856 | -121.8704 | -0.29755 | -0.09613 | 0.21057 | 122.6166 | -0.34332 | -0.32501 | 0.027466 | 0.50812 | 111.7905 | 109.7443 | 122.3602 | 122.6074 | 0.21057 | 122.731 | 112.706 | -0.32501 | 122.6074 | 0.21057 | 112.706 | 122.3602 | 122.731 | -123.0011 | -123.0286
1725.9688 | 122.8409 | -121.6141 | 1.1627 | -0.24765 | 0.0025892 | 0.0051632 | 0.025049 | -0.0045438 | -0.0011471 | 0.0031979 | -121.3852 | 1.1032 | -121.8704 | 0.99335 | 0.72327 | -9.082 | -9.8465 | -11.6867 | 1.1948 | -121.9254 | -0.25635 | -0.05951 | 0.22888 | 122.6074 | -0.43945 | -0.31128 | 0.032043 | 0.48523 | 111.7676 | 109.9274 | 122.3373 | 122.7173 | 0.22888 | 122.8088 | 112.532 | -0.31128 | 122.7173 | 0.22888 | 112.532 | 122.3373 | 122.8088 | -123.0331 | -123.0881
1726.9062 | 122.8867 | -121.6095 | 1.1261 | -0.17136 | 0.00088016 | 0.0028134 | 0.017145 | -0.0036892 | -0.0013609 | 0.0027707 | -121.3898 | 1.0483 | -121.8887 | 1.03 | 0.77362 | -9.3613 | -9.7778 | -11.9064 | 1.149 | -121.8796 | -0.27924 | -0.07782 | 0.21973 | 122.6395 | -0.35248 | -0.27008 | 0.022888 | 0.49896 | 111.8317 | 109.7031 | 122.3831 | 122.6578 | 0.21973 | 122.7585 | 112.2482 | -0.27008 | 122.6578 | 0.21973 | 112.2482 | 122.3831 | 122.7585 | -123.0148 | -123.0057
1727.9688 | 122.8683 | -121.5775 | 1.1765 | 0.20248 | 0.0023756 | 0.0023862 | 0.024408 | -0.0028348 | -0.0024289 | 0.0027707 | -121.4035 | 1.0986 | -121.9162 | 0.99335 | 0.72327 | -9.1461 | -9.8923 | -12.4649 | 1.2039 | -121.8567 | -0.33875 | -0.07782 | 0.17395 | 122.5708 | -0.45319 | -0.27923 | 0.027465 | 0.5127 | 111.6852 | 109.1125 | 122.3007 | 122.6761 | 0.17395 | 122.7814 | 112.4313 | -0.27923 | 122.6761 | 0.17395 | 112.4313 | 122.3007 | 122.7814 | -123.0927 | -123.0331
1728.9062 | 122.9691 | -121.5134 | 1.1719 | -0.10269 | -0.0010424 | 0.0021726 | 0.017359 | -0.0056118 | -0.0022153 | 0.0031979 | -121.2433 | 1.0849 | -121.8292 | 1.1169 | 0.86517 | -8.9905 | -9.5078 | -12.3184 | 1.2085 | -121.8109 | -0.31586 | -0.086975 | 0.27008 | 122.6303 | -0.3067 | -0.29755 | 0.036621 | 0.58594 | 112.0056 | 109.1949 | 122.3785 | 122.5983 | 0.27008 | 122.7219 | 112.5229 | -0.29755 | 122.5983 | 0.27008 | 112.5229 | 122.3785 | 122.7219 | -123.0011 | -122.9828
1729.9531 | 122.9004 | -121.5546 | 1.1536 | -0.018768 | -0.0014696 | 0.001959 | 0.017786 | -0.0036892 | -0.0017881 | 0.0059751 | -121.3806 | 1.0666 | -121.8933 | 1.0345 | 0.80566 | -9.4574 | -9.9197 | -12.4649 | 1.1765 | -121.8613 | -0.33875 | -0.086975 | 0.17395 | 122.5891 | -0.3479 | -0.3067 | 0.022889 | 0.5127 | 111.6348 | 109.0897 | 122.3602 | 122.6212 | 0.17395 | 122.731 | 112.0972 | -0.3067 | 122.6212 | 0.17395 | 112.0972 | 122.3602 | 122.731 | -123.0469 | -123.0148
1730.9062 | 122.8271 | -121.7194 | 1.1032 | -0.17136 | 0.0053662 | 0.0049496 | 0.023768 | -0.0062528 | -0.0022153 | 0.0029843 | -121.5179 | 1.0345 | -121.9711 | 0.88806 | 0.60883 | -10.0754 | -10.3912 | -12.6663 | 1.1078 | -122.0306 | -0.25177 | -0.068664 | 0.20142 | 122.6074 | -0.49438 | -0.31128 | 0.004578 | 0.45319 | 111.3281 | 109.053 | 122.3282 | 122.7539 | 0.20142 | 122.8271 | 111.644 | -0.31128 | 122.7539 | 0.20142 | 111.644 | 122.3282 | 122.8271 | -123.0743 | -123.1339
1731.9688 | 122.9141 | -121.669 | 1.0529 | 0.16434 | 0.001521 | 0.0060178 | 0.016718 | -0.0041166 | -0.0030697 | 0.0055479 | -121.4813 | 0.96588 | -121.9894 | 0.93384 | 0.69122 | -10.025 | -11.2885 | -13.0417 | 1.0712 | -121.9482 | -0.32044 | -0.086975 | 0.18768 | 122.6028 | -0.36163 | -0.27924 | 0.018311 | 0.50812 | 110.3806 | 108.6273 | 122.3602 | 122.6349 | 0.18768 | 122.7402 | 111.644 | -0.27924 | 122.6349 | 0.18768 | 111.644 | 122.3602 | 122.7402 | -123.0423 | -123.0011
1732.9062 | 122.9233 | -121.6919 | 1.0162 | -0.072174 | 0.0017346 | -0.00039102 | 0.017573 | -0.0081754 | -0.0013609 | 0.0040525 | -121.5088 | 0.95215 | -121.9757 | 0.95215 | 0.70953 | -9.5856 | -10.8902 | -12.7808 | 1.0391 | -121.9894 | -0.28381 | -0.064087 | 0.18311 | 122.644 | -0.3067 | -0.29755 | 0.022889 | 0.46692 | 110.8017 | 108.9111 | 122.4014 | 122.644 | 0.18311 | 122.731 | 112.1063 | -0.29755 | 122.644 | 0.18311 | 112.1063 | 122.4014 | 122.731 | -122.9919 | -123.0057
1733.9688 | 122.8958 | -121.788 | 0.95673 | 0.057526 | -0.0033922 | 0.0043088 | 0.018213 | -0.0051846 | -0.00093346 | 0.0053343 | -121.5363 | 0.94299 | -122.0078 | 0.86975 | 0.63629 | -10.0342 | -10.8856 | -12.9501 | 1.0117 | -122.0398 | -0.21973 | -0.013733 | 0.25177 | 122.6578 | -0.32043 | -0.25177 | 0.054932 | 0.4715 | 110.9024 | 108.8379 | 122.4243 | 122.731 | 0.25177 | 122.7997 | 111.7538 | -0.25177 | 122.731 | 0.25177 | 111.7538 | 122.4243 | 122.7997 | -122.9645 | -122.9965
1734.9062 | 122.9324 | -121.7331 | 0.97504 | 0.034637 | -0.00061524 | 0.0040952 | 0.016504 | -0.0036892 | -0.00093346 | 0.0051205 | -121.5637 | 0.89264 | -122.081 | 0.86975 | 0.61798 | -9.8877 | -10.7758 | -12.9822 | 1.0071 | -122.0627 | -0.3479 | -0.082398 | 0.16937 | 122.6028 | -0.35706 | -0.32959 | 0.032043 | 0.51727 | 110.9573 | 108.7509 | 122.3511 | 122.6257 | 0.16937 | 122.7402 | 111.8454 | -0.32959 | 122.6257 | 0.16937 | 111.8454 | 122.3511 | 122.7402 | -123.056 | -123.0377
1735.9688 | 122.8226 | -121.7972 | 0.97504 | 0.042267 | 0.0019482 | 0.006445 | 0.02569 | -0.0056118 | -0.0011471 | 0.0049069 | -121.6324 | 0.92926 | -122.1222 | 0.7782 | 0.49439 | -9.9335 | -11.1191 | -13.1149 | 1.0208 | -122.1085 | -0.32501 | -0.045777 | 0.16479 | 122.5754 | -0.48065 | -0.31128 | 0.045776 | 0.48981 | 110.6781 | 108.6823 | 122.2916 | 122.7264 | 0.16479 | 122.818 | 111.8637 | -0.31128 | 122.7264 | 0.16479 | 111.8637 | 122.2916 | 122.818 | -123.0972 | -123.0835
1736.9062 | 122.8912 | -121.7743 | 0.97504 | 0.11093 | 0.00045296 | 0.003027 | 0.018213 | -0.0071072 | -7.9062e-05 | 0.0019163 | -121.6141 | 0.89264 | -122.0718 | 0.81024 | 0.56763 | -9.7778 | -10.8948 | -12.9456 | 0.98419 | -122.081 | -0.29755 | -0.082398 | 0.16022 | 122.5845 | -0.40741 | -0.3067 | 0.009155 | 0.45776 | 110.8795 | 108.8287 | 122.3419 | 122.6669 | 0.16022 | 122.7585 | 111.9965 | -0.3067 | 122.6669 | 0.16022 | 111.9965 | 122.3419 | 122.7585 | -123.0469 | -123.056
1737.9531 | 122.7768 | -121.7834 | 0.98877 | 0.065155 | 0.0040846 | 0.0038816 | 0.02569 | -0.0053982 | -0.00071986 | 0.0042661 | -121.637 | 0.89722 | -122.1176 | 0.75073 | 0.48981 | -10.199 | -10.6247 | -13.0508 | 1.0208 | -122.1085 | -0.33417 | -0.091553 | 0.14648 | 122.5342 | -0.49896 | -0.32501 | 0.032043 | 0.48065 | 111.1588 | 108.7326 | 122.2733 | 122.6807 | 0.14648 | 122.8043 | 111.5845 | -0.32501 | 122.6807 | 0.14648 | 111.5845 | 122.2733 | 122.8043 | -123.1064 | -123.0972
1738.9062 | 122.8958 | -121.756 | 0.97046 | 0.1033 | 0.0030164 | 0.008154 | 0.017359 | -0.0062528 | -0.0015745 | 0.0059751 | -121.6324 | 0.86975 | -122.0673 | 0.82398 | 0.5722 | -10.0525 | -10.8032 | -12.8448 | 0.99792 | -122.0856 | -0.31128 | -0.10071 | 0.1236 | 122.58 | -0.39825 | -0.32959 | 0.027466 | 0.43488 | 110.9528 | 108.9111 | 122.3282 | 122.6257 | 0.1236 | 122.7539 | 111.7035 | -0.32959 | 122.6257 | 0.1236 | 111.7035 | 122.3282 | 122.7539 | -123.0377 | -123.056
1739.9531 | 122.937 | -121.7789 | 0.92926 | 0.16434 | 0.00023916 | 0.0062314 | 0.017573 | -0.004971 | -0.0024289 | 0.0025571 | -121.6049 | 0.82855 | -122.1039 | 0.81024 | 0.56763 | -9.8236 | -9.7778 | -12.1902 | 0.94299 | -122.113 | -0.32501 | -0.10071 | 0.17395 | 122.5891 | -0.36163 | -0.33417 | 0.013733 | 0.49896 | 112.001 | 109.5886 | 122.3465 | 122.6074 | 0.17395 | 122.7219 | 111.9553 | -0.33417 | 122.6074 | 0.17395 | 111.9553 | 122.3465 | 122.7219 | -123.0331 | -123.0423
1740.9062 | 122.8821 | -121.8246 | 0.89264 | 0.13382 | 0.00066656 | 0.005377 | 0.020136 | -0.0060392 | 0.00034814 | 0.0046933 | -121.6782 | 0.79651 | -122.1359 | 0.74158 | 0.47607 | -9.7504 | -10.6705 | -12.9181 | 0.92468 | -122.1588 | -0.31128 | -0.09613 | 0.14648 | 122.5662 | -0.41656 | -0.33417 | 0.032044 | 0.45776 | 111.1542 | 108.9066 | 122.3007 | 122.6212 | 0.14648 | 122.7493 | 112.0743 | -0.33417 | 122.6212 | 0.14648 | 112.0743 | 122.3007 | 122.7493 | -123.0286 | -123.0515
1741.9531 | 122.9416 | -121.8292 | 0.87433 | 0.088043 | 0.0019482 | 0.0043088 | 0.021418 | -0.0026212 | -0.00071986 | 0.0049069 | -121.6599 | 0.76446 | -122.1542 | 0.77362 | 0.50354 | -10.4645 | -10.1852 | -12.5977 | 0.87891 | -122.1817 | -0.32501 | -0.10986 | 0.16937 | 122.6028 | -0.37079 | -0.35248 | 0.004577 | 0.49438 | 111.644 | 109.2316 | 122.3328 | 122.5937 | 0.16937 | 122.7081 | 111.3647 | -0.35248 | 122.5937 | 0.16937 | 111.3647 | 122.3328 | 122.7081 | -123.0286 | -123.056
1742.9062 | 122.937 | -121.8384 | 0.83313 | 0.19485 | 0.0010938 | 0.0060178 | 0.024195 | -0.0045438 | -0.0020017 | 0.0017027 | -121.6141 | 0.78278 | -122.1451 | 0.56305 | 0.4303 | -10.1166 | -10.7895 | -12.6984 | 0.84686 | -122.2046 | -0.3067 | -0.050354 | 0.2243 | 122.4014 | -0.40283 | -0.36621 | 0.013733 | 0.53101 | 111.0489 | 109.14 | 122.2687 | 122.6212 | 0.2243 | 122.6852 | 111.7218 | -0.36621 | 122.6212 | 0.2243 | 111.7218 | 122.2687 | 122.6852 | -122.9782 | -123.0377
1743.9688 | 122.7905 | -121.9025 | 0.86517 | 0.11093 | 0.0038708 | 0.0028134 | 0.025263 | -0.0041166 | -0.0032835 | 0.0027707 | -121.7834 | 0.7782 | -122.2366 | 0.63629 | 0.36621 | -10.4553 | -10.817 | -13.3026 | 0.88806 | -122.2733 | -0.33417 | -0.086975 | 0.11902 | 122.5388 | -0.49896 | -0.37079 | 0.022889 | 0.45319 | 111.0855 | 108.5999 | 122.2687 | 122.6807 | 0.11902 | 122.7905 | 111.4471 | -0.37079 | 122.6807 | 0.11902 | 111.4471 | 122.2687 | 122.7905 | -123.1018 | -123.1384
1744.9062 | 122.9095 | -121.875 | 0.83771 | 0.20248 | 0.0023756 | 0.0049496 | 0.018427 | -0.003262 | 0.00013454 | 0.0042661 | -121.6736 | 0.75073 | -122.1771 | 0.737 | 0.48065 | -10.881 | -10.8353 | -13.2706 | 0.8606 | -122.2092 | -0.30212 | -0.086976 | 0.20142 | 122.612 | -0.35706 | -0.33417 | 0.022888 | 0.50354 | 111.0397 | 108.6044 | 122.3557 | 122.6257 | 0.20142 | 122.7356 | 110.994 | -0.33417 | 122.6257 | 0.20142 | 110.994 | 122.3557 | 122.7356 | -123.0148 | -123.0469
1745.9688 | 122.7997 | -121.9437 | 0.84686 | 0.057526 | 0.0023756 | 0.0058042 | 0.025477 | -0.0034756 | -0.0026425 | 0.0053343 | -121.8109 | 0.77362 | -122.2961 | 0.63171 | 0.34332 | -11.2701 | -10.3043 | -13.2889 | 0.89264 | -122.2733 | -0.35248 | -0.073242 | 0.13275 | 122.5754 | -0.50354 | -0.32959 | 0.045776 | 0.48523 | 111.6394 | 108.6548 | 122.287 | 122.7173 | 0.13275 | 122.8363 | 110.6735 | -0.32959 | 122.7173 | 0.13275 | 110.6735 | 122.287 | 122.8363 | -123.143 | -123.1201
1746.9062 | 122.9141 | -121.8658 | 0.81482 | 0.16434 | 0.0025892 | 0.008154 | 0.019495 | -0.0019802 | -0.0020017 | 0.0053343 | -121.669 | 0.74616 | -122.2137 | 0.72327 | 0.4715 | -8.5373 | -10.8124 | -12.3276 | 0.84228 | -122.2092 | -0.3479 | -0.068664 | 0.19684 | 122.5891 | -0.34332 | -0.34332 | 0.027466 | 0.54474 | 111.0535 | 109.5383 | 122.3373 | 122.612 | 0.19684 | 122.7081 | 113.3286 | -0.34332 | 122.612 | 0.19684 | 113.3286 | 122.3373 | 122.7081 | -123.0286 | -123.024
1747.9531 | 122.9279 | -121.9482 | 0.86975 | 0.080414 | 0.0036572 | 0.0055906 | 0.025049 | -0.0013394 | -0.00071986 | 0.0055479 | -121.7743 | 0.77362 | -122.2229 | 0.59967 | 0.34332 | -9.6497 | -10.7025 | -13.5864 | 0.88348 | -122.2458 | -0.27466 | -0.09613 | 0.17395 | 122.5479 | -0.52643 | -0.29755 | 0.013733 | 0.44861 | 111.2457 | 108.3618 | 122.2916 | 122.7219 | 0.17395 | 122.8317 | 112.2986 | -0.29755 | 122.7219 | 0.17395 | 112.2986 | 122.2916 | 122.8317 | -123.0927 | -123.1155
1748.9062 | 122.8043 | -121.9528 | 0.83313 | 0.76706 | 0.0036572 | 0.0038816 | 0.023554 | -0.001553 | -0.0013609 | 0.0031979 | -121.6187 | 0.79193 | -122.2458 | 0.58594 | 0.35706 | -9.7961 | -9.8785 | -13.3575 | 0.88806 | -122.319 | -0.29297 | -0.041199 | 0.33417 | 122.5388 | -0.47607 | -0.36621 | 0.054932 | 0.62714 | 112.0743 | 108.5953 | 122.3099 | 122.7448 | 0.33417 | 122.8409 | 112.1567 | -0.36621 | 122.7448 | 0.33417 | 112.1567 | 122.3099 | 122.8409 | -123.0789 | -123.1522
1749.9688 | 122.8821 | -122.0444 | 0.72327 | -0.12558 | 0.0040846 | 0.0092222 | 0.02334 | -0.0017666 | -0.0020017 | 0.0049069 | -121.8658 | 0.6958 | -122.3557 | 0.54016 | 0.29755 | -9.4208 | -10.231 | -13.1241 | 0.76904 | -122.4335 | -0.31128 | -0.027466 | 0.17853 | 122.5845 | -0.42572 | -0.3891 | 0.045776 | 0.48981 | 111.8134 | 108.9203 | 122.3419 | 122.7402 | 0.17853 | 122.8134 | 112.6236 | -0.3891 | 122.7402 | 0.17853 | 112.6236 | 122.3419 | 122.8134 | -123.0789 | -123.1567
1750.9062 | 122.9507 | -122.0078 | 0.71411 | 0.21774 | 0.0030164 | 0.004736 | 0.018427 | -0.0013394 | -0.0039243 | 0.0053343 | -121.8521 | 0.6134 | -122.3648 | 0.59967 | 0.35706 | -9.2789 | -10.7574 | -13.3255 | 0.72327 | -122.3328 | -0.35706 | -0.10071 | 0.15564 | 122.6074 | -0.35706 | -0.32501 | 0.009156 | 0.51269 | 111.2503 | 108.6823 | 122.3648 | 122.6212 | 0.15564 | 122.731 | 112.7289 | -0.32501 | 122.6212 | 0.15564 | 112.7289 | 122.3648 | 122.731 | -123.0789 | -123.0469
1751.9531 | 122.8271 | -122.0581 | 0.73242 | -0.17136 | 0.0028028 | 0.0043088 | 0.021845 | -0.0041166 | 0.0012027 | 0.0036253 | -121.7789 | 0.68665 | -122.3648 | 0.56305 | 0.29755 | -9.2926 | -10.6979 | -13.4399 | 0.77362 | -122.4014 | -0.3067 | -0.045776 | 0.27923 | 122.6212 | -0.43488 | -0.34332 | 0.041199 | 0.58594 | 111.3602 | 108.6182 | 122.3557 | 122.7448 | 0.27923 | 122.8317 | 112.7655 | -0.34332 | 122.7448 | 0.27923 | 112.7655 | 122.3557 | 122.8317 | -123.0972 | -123.1338
1752.9062 | 122.7859 | -122.1268 | 0.72327 | 0.080414 | 0.0070752 | 0.0058042 | 0.024836 | -0.0019802 | -0.0026425 | 0.0027707 | -121.843 | 0.68207 | -122.3785 | 0.49439 | 0.23346 | -9.7458 | -10.5606 | -13.4903 | 0.76446 | -122.4243 | -0.25177 | -0.041199 | 0.28381 | 122.6212 | -0.48981 | -0.29755 | 0.041198 | 0.53558 | 111.5662 | 108.6365 | 122.3602 | 122.8088 | 0.28381 | 122.8912 | 112.381 | -0.29755 | 122.8088 | 0.28381 | 112.381 | 122.3602 | 122.8912 | -123.1018 | -123.1476
1753.9688 | 122.8592 | -122.0306 | 0.71411 | -0.17899 | 0.0036572 | 0.0045224 | 0.014368 | -0.0026212 | -0.0032835 | 0.0051205 | -121.8246 | 0.65002 | -122.3099 | 0.6134 | 0.36163 | -8.7433 | -10.8353 | -13.2385 | 0.74158 | -122.374 | -0.27923 | -0.064087 | 0.20599 | 122.644 | -0.35248 | -0.34332 | 0.027466 | 0.48523 | 111.1954 | 108.7921 | 122.3923 | 122.6807 | 0.20599 | 122.7722 | 113.2874 | -0.34332 | 122.6807 | 0.20599 | 113.2874 | 122.3923 | 122.7722 | -123.024 | -123.0881
1754.9062 | 122.7905 | -122.049 | 0.71869 | 0.065155 | 0.002162 | 0.0075132 | 0.025263 | -0.001553 | -0.0015745 | 0.0046933 | -121.8613 | 0.66376 | -122.3557 | 0.49439 | 0.25177 | -8.4229 | -10.3775 | -13.6871 | 0.76446 | -122.4152 | -0.3067 | -0.054932 | 0.18768 | 122.5433 | -0.46692 | -0.36621 | 0.045776 | 0.49439 | 111.6714 | 108.3618 | 122.3007 | 122.7127 | 0.18768 | 122.8134 | 113.6261 | -0.36621 | 122.7127 | 0.18768 | 113.6261 | 122.3007 | 122.8134 | -123.0743 | -123.1338
1755.9531 | 122.85 | -122.0535 | 0.737 | -0.14084 | 0.002162 | 0.0075132 | 0.022059 | -0.0047574 | -0.0017881 | 0.0049069 | -121.8475 | 0.66834 | -122.3648 | 0.55847 | 0.31128 | -8.5556 | -10.9085 | -13.4903 | 0.75073 | -122.3923 | -0.31128 | -0.068665 | 0.20599 | 122.612 | -0.42572 | -0.33875 | 0.013732 | 0.51727 | 111.145 | 108.5632 | 122.3648 | 122.7219 | 0.20599 | 122.8043 | 113.4979 | -0.33875 | 122.7219 | 0.20599 | 113.4979 | 122.3648 | 122.8043 | -123.1018 | -123.1293
1756.9219 | 122.9187 | -122.0169 | 0.70038 | -0.66727 | 0.002162 | 0.0083676 | 0.019068 | -0.0045438 | -0.0032835 | 0.0040525 | -121.7697 | 0.59509 | -122.3465 | 0.60425 | 0.37079 | -8.6792 | -10.0342 | -13.8199 | 0.71411 | -122.319 | -0.32959 | -0.10528 | 0.24719 | 122.6212 | -0.32959 | -0.30212 | 0.013733 | 0.57678 | 111.9827 | 108.197 | 122.3877 | 122.612 | 0.24719 | 122.731 | 113.3377 | -0.30212 | 122.612 | 0.24719 | 113.3377 | 122.3877 | 122.731 | -123.0469 | -123.0194
1757.9531 | 122.8409 | -122.0398 | 0.70953 | -0.056915 | 0.0038708 | 0.0068722 | 0.023554 | -0.0028348 | -0.00093346 | 0.0042661 | -121.7834 | 0.71869 | -122.319 | 0.55847 | 0.27466 | -7.9742 | -10.4507 | -14.1769 | 0.76904 | -122.406 | -0.27924 | 0.009155 | 0.25635 | 122.5983 | -0.43488 | -0.36621 | 0.059509 | 0.53558 | 111.5891 | 107.8629 | 122.3145 | 122.7585 | 0.25635 | 122.8088 | 114.0656 | -0.36621 | 122.7585 | 0.25635 | 114.0656 | 122.3145 | 122.8088 | -123.0286 | -123.1155
1758.9062 | 122.8363 | -122.0169 | 0.78735 | -0.064545 | 0.0045118 | 0.003027 | 0.02334 | -0.0011258 | -0.0020017 | 0.0051205 | -121.8063 | 0.68207 | -122.3602 | 0.55847 | 0.31128 | -8.1436 | -10.5103 | -14.1495 | 0.78735 | -122.3465 | -0.34332 | -0.10529 | 0.21057 | 122.5754 | -0.47608 | -0.32959 | 0 | 0.55389 | 111.5067 | 107.8674 | 122.3282 | 122.699 | 0.21057 | 122.8043 | 113.8733 | -0.32959 | 122.699 | 0.21057 | 113.8733 | 122.3282 | 122.8043 | -123.1476 | -123.1339
1759.9688 | 122.8134 | -122.0856 | 0.74158 | -0.33157 | 0.002162 | 0.011999 | 0.016932 | -0.0017666 | -0.0022153 | 0.0051205 | -121.875 | 0.66376 | -122.374 | 0.48981 | 0.2655 | -8.4869 | -10.762 | -13.9389 | 0.7782 | -122.3923 | -0.28839 | -0.07782 | 0.21057 | 122.5754 | -0.47607 | -0.3067 | 0.036621 | 0.49896 | 111.3235 | 108.1467 | 122.3511 | 122.7493 | 0.21057 | 122.8638 | 113.5986 | -0.3067 | 122.7493 | 0.21057 | 113.5986 | 122.3511 | 122.8638 | -123.1155 | -123.1339
1760.9062 | 122.8363 | -122.0581 | 0.6958 | 0.21011 | 0.0057934 | 0.0049496 | 0.022913 | -0.0011258 | -0.0024289 | 0.0017027 | -121.8796 | 0.6546 | -122.3877 | 0.50812 | 0.27008 | -8.5831 | -10.9085 | -14.3555 | 0.72327 | -122.4152 | -0.32959 | -0.041199 | 0.17853 | 122.5662 | -0.42572 | -0.35706 | 0.027466 | 0.50812 | 111.1496 | 107.7026 | 122.3282 | 122.7127 | 0.17853 | 122.7814 | 113.475 | -0.35706 | 122.7127 | 0.17853 | 113.475 | 122.3282 | 122.7814 | -123.0835 | -123.111
1761.9688 | 122.8638 | -122.0398 | 0.75531 | -0.0035098 | 0.0030164 | 0.0043088 | 0.02334 | -0.00048499 | -0.0017881 | 0.0051205 | -121.8338 | 0.66376 | -122.3969 | 0.58594 | 0.34332 | -8.8852 | -10.8582 | -14.09 | 0.80566 | -122.3923 | -0.35706 | -0.091553 | 0.20599 | 122.6257 | -0.41199 | -0.35248 | 0.050354 | 0.56305 | 111.1816 | 107.9498 | 122.3831 | 122.7036 | 0.20599 | 122.8455 | 113.1546 | -0.35248 | 122.7036 | 0.20599 | 113.1546 | 122.3831 | 122.8455 | -123.1522 | -123.1476
1762.9062 | 122.8546 | -122.0947 | 0.6958 | -0.19424 | 0.004939 | 0.0045224 | 0.017359 | -0.0024076 | -0.00093346 | 0.0057615 | -121.8796 | 0.66834 | -122.3785 | 0.48981 | 0.24719 | -9.1461 | -11.3571 | -13.9984 | 0.75073 | -122.4243 | -0.28381 | -0.027466 | 0.21515 | 122.5845 | -0.44861 | -0.32959 | 0.054931 | 0.49896 | 110.7376 | 108.0963 | 122.3419 | 122.7631 | 0.21515 | 122.8455 | 112.9486 | -0.32959 | 122.7631 | 0.21515 | 112.9486 | 122.3419 | 122.8455 | -123.0743 | -123.1201
1763.9531 | 122.8271 | -122.0764 | 0.76446 | -0.25528 | 0.0030164 | 0.0075132 | 0.017786 | -0.0019802 | -0.00050626 | 0.0072569 | -121.907 | 0.65918 | -122.374 | 0.48981 | 0.14648 | -8.2031 | -10.3958 | -14.1861 | 0.79651 | -122.374 | -0.29755 | -0.10528 | 0.16937 | 122.5662 | -0.61798 | -0.29755 | 0.032044 | 0.46692 | 111.6806 | 107.8903 | 122.2229 | 122.7356 | 0.16937 | 122.8729 | 113.8733 | -0.29755 | 122.7356 | 0.16937 | 113.8733 | 122.2229 | 122.8729 | -123.1384 | -123.1384
1764.9062 | 122.8729 | -122.0947 | 0.70496 | -0.16373 | 0.0045118 | 0.0038816 | 0.023127 | -0.003262 | -0.0043515 | 0.0044797 | -121.8887 | 0.63171 | -122.3969 | 0.5127 | 0.27466 | -8.4229 | -10.9955 | -14.447 | 0.74616 | -122.4152 | -0.30212 | -0.073242 | 0.20599 | 122.6074 | -0.4303 | -0.32043 | 0.041199 | 0.50812 | 111.0992 | 107.6477 | 122.3694 | 122.7264 | 0.20599 | 122.8409 | 113.6719 | -0.32043 | 122.7264 | 0.20599 | 113.6719 | 122.3694 | 122.8409 | -123.1018 | -123.1201
1765.9688 | 122.8683 | -122.0261 | 0.75531 | -0.23239 | 0.0030164 | 0.003668 | 0.018641 | -0.003262 | -0.00071986 | 0.0046933 | -121.9162 | 0.6546 | -122.4106 | 0.4715 | 0.21973 | -8.3679 | -11.1786 | -14.5798 | 0.76446 | -122.4152 | -0.38452 | -0.10071 | 0.10986 | 122.4976 | -0.53558 | -0.3891 | 0.009155 | 0.49438 | 110.8475 | 107.4463 | 122.2458 | 122.6807 | 0.10986 | 122.7905 | 113.6581 | -0.3891 | 122.6807 | 0.10986 | 113.6581 | 122.2458 | 122.7905 | -123.1659 | -123.1705
1766.9219 | 122.937 | -122.0306 | 0.67291 | 0.1796 | 2.5564e-05 | 0.0070858 | 0.015864 | -0.0013394 | -0.0028561 | 0.0072569 | -121.8338 | 0.60425 | -122.3602 | 0.56763 | 0.32501 | -9.0088 | -11.5219 | -14.3875 | 0.70038 | -122.3602 | -0.32959 | -0.068665 | 0.19684 | 122.5983 | -0.3479 | -0.32959 | 0.027465 | 0.52643 | 110.5087 | 107.6431 | 122.3557 | 122.6349 | 0.19684 | 122.731 | 113.0219 | -0.32959 | 122.6349 | 0.19684 | 113.0219 | 122.3557 | 122.731 | -123.0331 | -123.0331
1767.9688 | 122.9553 | -122.0581 | 0.66834 | -0.17899 | -0.00040164 | 0.005377 | 0.016932 | -0.0030484 | -7.9062e-05 | 0.0046933 | -121.8109 | 0.59967 | -122.3602 | 0.59967 | 0.41199 | -8.7524 | -11.3342 | -14.2227 | 0.70038 | -122.406 | -0.30212 | -0.068665 | 0.24719 | 122.6578 | -0.25635 | -0.3479 | 0.032043 | 0.54932 | 110.7239 | 107.8354 | 122.4701 | 122.6578 | 0.24719 | 122.7585 | 113.3057 | -0.3479 | 122.6578 | 0.24719 | 113.3057 | 122.4701 | 122.7585 | -123.0286 | -123.0743
1768.9062 | 122.8638 | -122.0993 | 0.6958 | -0.14084 | 0.0028028 | 0.005377 | 0.023768 | -0.0041166 | -0.0017881 | 0.0023435 | -121.8933 | 0.64087 | -122.406 | 0.53101 | 0.26093 | -8.7662 | -11.3388 | -14.4516 | 0.74158 | -122.4106 | -0.3067 | -0.054932 | 0.20599 | 122.6303 | -0.43488 | -0.31128 | 0.045776 | 0.5127 | 110.7605 | 107.6477 | 122.3602 | 122.7402 | 0.20599 | 122.8409 | 113.3331 | -0.31128 | 122.7402 | 0.20599 | 113.3331 | 122.3602 | 122.8409 | -123.1018 | -123.1064
1769.9062 | 122.8409 | -122.0947 | 0.6958 | -0.14084 | 0.004939 | 0.0034544 | 0.025477 | -0.003262 | -0.0015745 | 0.0044797 | -121.8887 | 0.63629 | -122.4014 | 0.52185 | 0.23804 | -7.6584 | -10.8994 | -14.6347 | 0.72327 | -122.4564 | -0.3067 | -0.059509 | 0.20599 | 122.6166 | -0.45776 | -0.36163 | 0.027466 | 0.51269 | 111.1954 | 107.46 | 122.3328 | 122.731 | 0.20599 | 122.818 | 114.4363 | -0.36163 | 122.731 | 0.20599 | 114.4363 | 122.3328 | 122.818 | -123.0972 | -123.1522
1770.9062 | 122.8546 | -122.1085 | 0.67291 | -0.011139 | 0.0040846 | 0.0058042 | 0.021631 | -0.00048499 | 0.00013454 | 0.0025571 | -121.8384 | 0.65918 | -122.3877 | 0.52185 | 0.25177 | -7.7637 | -11.0687 | -14.6484 | 0.72327 | -122.4335 | -0.27924 | -0.013733 | 0.27008 | 122.6303 | -0.42114 | -0.32501 | 0.050354 | 0.54932 | 111.0397 | 107.46 | 122.3602 | 122.7676 | 0.27008 | 122.8317 | 114.3448 | -0.32501 | 122.7676 | 0.27008 | 114.3448 | 122.3602 | 122.8317 | -123.0606 | -123.1064
1771.9062 | 122.937 | -122.0444 | 0.66834 | -0.23239 | 0.0034436 | 0.0023862 | 0.017573 | -0.0024076 | -0.00050626 | 0.0059751 | -121.8521 | 0.56305 | -122.3694 | 0.5722 | 0.27466 | -8.4869 | -11.2106 | -14.2776 | 0.6958 | -122.4014 | -0.32501 | -0.10529 | 0.19226 | 122.6166 | -0.39368 | -0.35706 | 0.027466 | 0.51727 | 110.8337 | 107.7667 | 122.319 | 122.6074 | 0.19226 | 122.7402 | 113.5574 | -0.35706 | 122.6074 | 0.19226 | 113.5574 | 122.319 | 122.7402 | -123.0377 | -123.0698
1772.9688 | 122.9004 | -122.0535 | 0.67749 | -0.17136 | 0.00066656 | 0.0040952 | 0.013514 | -0.0036892 | -0.0039243 | 0.00042086 | -121.8796 | 0.60425 | -122.3694 | 0.70038 | 0.33875 | -8.4229 | -11.9385 | -14.7125 | 0.6958 | -122.406 | -0.31586 | -0.073242 | 0.17395 | 122.7539 | -0.33875 | -0.35248 | 0.018311 | 0.48981 | 110.1151 | 107.341 | 122.3923 | 122.6578 | 0.17395 | 122.7493 | 113.6307 | -0.35248 | 122.6578 | 0.17395 | 113.6307 | 122.3923 | 122.7493 | -123.0469 | -123.0835
1773.9062 | 122.85 | -122.1085 | 0.70038 | -0.26291 | 0.001521 | 0.0028134 | 0.021204 | -0.0036892 | -0.0030697 | 0.0027707 | -121.9345 | 0.64545 | -122.4014 | 0.49439 | 0.1831 | -8.5236 | -12.0758 | -14.7812 | 0.72784 | -122.4289 | -0.29297 | -0.054931 | 0.17395 | 122.6028 | -0.51727 | -0.32044 | 0.027466 | 0.46692 | 110.0327 | 107.3273 | 122.2916 | 122.7539 | 0.17395 | 122.8363 | 113.5849 | -0.32044 | 122.7539 | 0.17395 | 113.5849 | 122.2916 | 122.8363 | -123.1018 | -123.1293
1774.9688 | 122.8821 | -122.0398 | 0.74616 | -0.22476 | 0.001521 | 0.0045224 | 0.019495 | -0.0053982 | -0.0015745 | 0.0036253 | -121.9345 | 0.63171 | -122.4426 | 0.4715 | 0.18768 | -9.1049 | -11.3068 | -14.6393 | 0.74158 | -122.4609 | -0.40283 | -0.11444 | 0.10529 | 122.5113 | -0.55847 | -0.42114 | -0.004578 | 0.50812 | 110.733 | 107.4005 | 122.2275 | 122.6715 | 0.10529 | 122.7814 | 112.9349 | -0.42114 | 122.6715 | 0.10529 | 112.9349 | 122.2275 | 122.7814 | -123.1888 | -123.2071
1775.9062 | 122.8409 | -122.1222 | 0.68665 | -0.1561 | 0.0042982 | 0.0051632 | 0.020991 | -0.002194 | -0.0011471 | 0.0038389 | -121.9025 | 0.62714 | -122.4426 | 0.47607 | 0.19684 | -9.0042 | -11.3892 | -14.8361 | 0.72784 | -122.4472 | -0.32044 | -0.05951 | 0.21973 | 122.5983 | -0.48981 | -0.32501 | 0.041198 | 0.54016 | 110.733 | 107.2861 | 122.319 | 122.7493 | 0.21973 | 122.85 | 113.118 | -0.32501 | 122.7493 | 0.21973 | 113.118 | 122.319 | 122.85 | -123.1293 | -123.1339
1776.9688 | 122.8363 | -122.1451 | 0.65918 | 0.027008 | 0.002162 | 0.003027 | 0.022913 | -0.00069859 | -0.0039243 | 0.0038389 | -121.8842 | 0.6134 | -122.4243 | 0.4715 | 0.17853 | -9.6771 | -11.6592 | -14.9368 | 0.72784 | -122.4426 | -0.27923 | -0.045777 | 0.26093 | 122.6166 | -0.48065 | -0.29755 | 0.068664 | 0.54016 | 110.4858 | 107.2083 | 122.3236 | 122.7585 | 0.26093 | 122.8729 | 112.468 | -0.29755 | 122.7585 | 0.26093 | 112.468 | 122.3236 | 122.8729 | -123.0835 | -123.1018
1777.9062 | 122.8226 | -122.1268 | 0.67749 | -0.19424 | 0.0034436 | 0.0072996 | 0.019922 | -0.0024076 | -0.0017881 | 0.0070431 | -121.9391 | 0.63629 | -122.4243 | 0.46692 | 0.17395 | -9.9014 | -11.3159 | -15.1932 | 0.72327 | -122.4701 | -0.29755 | -0.041198 | 0.18768 | 122.5937 | -0.50354 | -0.34332 | 0.045777 | 0.48523 | 110.8109 | 106.9336 | 122.3007 | 122.7631 | 0.18768 | 122.85 | 112.2253 | -0.34332 | 122.7631 | 0.18768 | 112.2253 | 122.3007 | 122.85 | -123.1018 | -123.1476
1778.9531 | 122.8867 | -122.0947 | 0.68665 | -0.22476 | 0.00088016 | 0.0077268 | 0.015009 | -0.0028348 | -0.0011471 | 0.0038389 | -121.875 | 0.59509 | -122.3877 | 0.54474 | 0.26093 | -7.7179 | -11.4304 | -15.0146 | 0.70496 | -122.4106 | -0.29297 | -0.091553 | 0.21973 | 122.6395 | -0.42572 | -0.31586 | 0.01831 | 0.51269 | 110.6644 | 107.0801 | 122.3557 | 122.6898 | 0.21973 | 122.7997 | 114.3768 | -0.31586 | 122.6898 | 0.21973 | 114.3768 | 122.3557 | 122.7997 | -123.0743 | -123.0972
1779.9062 | 122.8409 | -122.1359 | 0.66834 | -0.1561 | 0.0036572 | 0.0055906 | 0.021418 | -0.0034756 | -0.0024289 | 0.0036253 | -121.9437 | 0.6134 | -122.4335 | 0.48065 | 0.19226 | -7.7133 | -11.9522 | -14.9872 | 0.74158 | -122.4655 | -0.29755 | -0.054932 | 0.19226 | 122.6166 | -0.47607 | -0.32959 | 0.073242 | 0.48981 | 110.1837 | 107.1487 | 122.3282 | 122.7493 | 0.19226 | 122.8775 | 114.4226 | -0.32959 | 122.7493 | 0.19226 | 114.4226 | 122.3282 | 122.8775 | -123.1018 | -123.1338
1780.9688 | 122.8226 | -122.0947 | 0.67749 | -0.018768 | 0.0038708 | 0.0045224 | 0.025263 | -0.0024076 | -0.0028561 | 0.0040525 | -121.9299 | 0.59052 | -122.3877 | 0.48065 | 0.20142 | -7.988 | -13.028 | -15.2847 | 0.70953 | -122.4564 | -0.29297 | -0.086975 | 0.1648 | 122.5754 | -0.47607 | -0.36163 | 0.032044 | 0.45776 | 109.0668 | 106.81 | 122.2961 | 122.6852 | 0.1648 | 122.8043 | 114.1068 | -0.36163 | 122.6852 | 0.1648 | 114.1068 | 122.2961 | 122.8043 | -123.0652 | -123.1339
1781.9062 | 122.8088 | -122.0856 | 0.69122 | -0.14847 | 0.0025892 | 0.003668 | 0.019922 | -0.0024076 | -0.0020017 | 0.0036253 | -122.0306 | 0.64087 | -122.4289 | 0.46692 | 0.17395 | -7.8506 | -12.4832 | -15.2435 | 0.75073 | -122.4609 | -0.34332 | -0.050354 | 0.054931 | 122.5525 | -0.51727 | -0.37537 | 0.059509 | 0.39825 | 109.6024 | 106.842 | 122.2595 | 122.7264 | 0.054931 | 122.8363 | 114.2349 | -0.37537 | 122.7264 | 0.054931 | 114.2349 | 122.2595 | 122.8363 | -123.1201 | -123.1522
1782.9531 | 122.9141 | -122.0718 | 0.66834 | -0.018768 | -0.00082884 | -0.00039102 | 0.014582 | -0.0041166 | -0.0026425 | 0.0036253 | -121.9162 | 0.59052 | -122.3969 | 0.51727 | 0.23804 | -7.8827 | -12.3184 | -14.9414 | 0.6958 | -122.4014 | -0.32501 | -0.07782 | 0.15564 | 122.5891 | -0.4303 | -0.32959 | 0.027466 | 0.48065 | 109.7534 | 107.1304 | 122.3099 | 122.6624 | 0.15564 | 122.7676 | 114.1891 | -0.32959 | 122.6624 | 0.15564 | 114.1891 | 122.3099 | 122.7676 | -123.0652 | -123.0698
1783.9062 | 122.8317 | -122.1268 | 0.737 | -0.21713 | 0.0025892 | 0.0043088 | 0.019922 | -0.0028348 | -0.00071986 | 0.0027707 | -122.0581 | 0.6134 | -122.438 | 0.5127 | 0.42572 | -7.7454 | -11.8835 | -15.5869 | 0.76446 | -122.4106 | -0.31128 | -0.1236 | 0.068665 | 122.6395 | -0.31128 | -0.28381 | 0.027465 | 0.37994 | 110.2432 | 106.5399 | 122.5525 | 122.7402 | 0.068665 | 122.8912 | 114.3814 | -0.28381 | 122.7402 | 0.068665 | 114.3814 | 122.5525 | 122.8912 | -123.175 | -123.1476
1784.9688 | 122.9736 | -122.0901 | 0.6546 | -0.13321 | 0.0019482 | 0.0055906 | 0.013727 | -0.0047574 | -0.00029266 | 0.0061887 | -121.9116 | 0.57678 | -122.3923 | 0.58594 | 0.3067 | -7.7408 | -12.4237 | -14.6439 | 0.6958 | -122.3877 | -0.30212 | -0.07782 | 0.17853 | 122.6761 | -0.3479 | -0.29755 | 0.041199 | 0.48065 | 109.6664 | 107.4463 | 122.3969 | 122.6669 | 0.17853 | 122.7859 | 114.3494 | -0.29755 | 122.6669 | 0.17853 | 114.3494 | 122.3969 | 122.7859 | -123.0469 | -123.0423
1785.9219 | 122.8043 | -122.1405 | 0.67291 | 0.088043 | 0.0047254 | 0.0051632 | 0.026331 | -0.0043302 | -0.0024289 | 0.0044797 | -121.9437 | 0.6134 | -122.4426 | 0.4303 | 0.12817 | -7.8003 | -12.0026 | -14.6667 | 0.6958 | -122.4747 | -0.30212 | -0.05951 | 0.19684 | 122.5708 | -0.54474 | -0.33417 | 0.022888 | 0.49896 | 110.1379 | 107.4738 | 122.2687 | 122.7539 | 0.19684 | 122.8363 | 114.3402 | -0.33417 | 122.7539 | 0.19684 | 114.3402 | 122.2687 | 122.8363 | -123.1155 | -123.1476
1786.9688 | 122.8592 | -122.1176 | 0.66834 | 0.1796 | 0.0019482 | 0.0017454 | 0.021631 | -0.0024076 | -0.0015745 | 0.0044797 | -121.843 | 0.6134 | -122.4426 | 0.46692 | 0.17395 | -7.6538 | -12.1307 | -15.4312 | 0.70038 | -122.4426 | -0.32501 | -0.054932 | 0.27466 | 122.5845 | -0.49439 | -0.32501 | 0.032043 | 0.59967 | 109.9869 | 106.6864 | 122.2916 | 122.731 | 0.27466 | 122.818 | 114.4638 | -0.32501 | 122.731 | 0.27466 | 114.4638 | 122.2916 | 122.818 | -123.111 | -123.111
1787.9062 | 122.8958 | -122.0718 | 0.67291 | -0.2095 | 2.5564e-05 | 0.005377 | 0.019068 | -0.004971 | -0.00071986 | 0.0059751 | -121.9116 | 0.59509 | -122.3831 | 0.54932 | 0.25635 | -7.7499 | -12.236 | -14.6347 | 0.70496 | -122.4106 | -0.31128 | -0.07782 | 0.16022 | 122.6212 | -0.41656 | -0.33875 | 0.032043 | 0.4715 | 109.8358 | 107.4371 | 122.3282 | 122.6669 | 0.16022 | 122.7768 | 114.3219 | -0.33875 | 122.6669 | 0.16022 | 114.3219 | 122.3282 | 122.7768 | -123.056 | -123.0835
1788.9688 | 122.905 | -122.0901 | 0.66834 | -0.2095 | 0.00023916 | 0.00089078 | 0.016077 | -0.003903 | -7.9062e-05 | 0.0038389 | -121.6873 | 0.56763 | -122.406 | 0.5722 | 0.31128 | -7.8323 | -12.4695 | -14.5477 | 0.69122 | -122.3969 | -0.31586 | -0.10071 | 0.40283 | 122.6624 | -0.35706 | -0.3067 | 0.022888 | 0.71869 | 109.6207 | 107.5424 | 122.4014 | 122.6578 | 0.40283 | 122.7814 | 114.2578 | -0.3067 | 122.6578 | 0.40283 | 114.2578 | 122.4014 | 122.7814 | -123.0743 | -123.0652
1789.9062 | 122.9279 | -122.081 | 0.65918 | -0.018768 | 0.002162 | 0.0066586 | 0.018854 | -0.0058256 | -0.0032835 | 0.0021299 | -121.875 | 0.56305 | -122.374 | 0.59052 | 0.28381 | -8.1024 | -12.4786 | -14.5523 | 0.70038 | -122.3923 | -0.29297 | -0.096131 | 0.20599 | 122.6715 | -0.37537 | -0.31128 | 0.041198 | 0.49896 | 109.6024 | 107.5287 | 122.3648 | 122.644 | 0.20599 | 122.7814 | 113.9786 | -0.31128 | 122.644 | 0.20599 | 113.9786 | 122.3648 | 122.7814 | -123.0331 | -123.0515
1790.9531 | 122.9187 | -122.0673 | 0.69122 | -0.14847 | 0.0013074 | 0.0058042 | 0.020136 | -0.0060392 | -0.0017881 | 0.0031979 | -121.875 | 0.61798 | -122.3877 | 0.5722 | 0.27008 | -7.8094 | -12.3734 | -14.5111 | 0.72784 | -122.4243 | -0.32043 | -0.073242 | 0.19226 | 122.6395 | -0.42114 | -0.35706 | 0.036621 | 0.51269 | 109.6939 | 107.5562 | 122.3373 | 122.6852 | 0.19226 | 122.7951 | 114.2578 | -0.35706 | 122.6852 | 0.19226 | 114.2578 | 122.3373 | 122.7951 | -123.0789 | -123.1155
1791.9062 | 122.937 | -122.0535 | 0.68207 | -0.14084 | -0.00040164 | 0.0040952 | 0.018 | -0.0064664 | -0.00071986 | 0.0012753 | -121.9162 | 0.58136 | -122.3785 | 0.56763 | 0.29297 | -7.988 | -12.2131 | -14.4379 | 0.70496 | -122.3923 | -0.32501 | -0.10071 | 0.13733 | 122.6212 | -0.3891 | -0.33875 | 0.022888 | 0.46234 | 109.8404 | 107.6157 | 122.3465 | 122.6349 | 0.13733 | 122.7585 | 114.0656 | -0.33875 | 122.6349 | 0.13733 | 114.0656 | 122.3465 | 122.7585 | -123.0606 | -123.0743
1792.9688 | 122.9141 | -122.0856 | 0.66834 | 0.0041197 | 0.00066656 | 0.00046358 | 0.017573 | -0.0068936 | -0.0022153 | 0.0051205 | -121.9986 | 0.57678 | -122.4197 | 0.52185 | 0.27466 | -7.8369 | -12.3962 | -14.5203 | 0.70496 | -122.4106 | -0.33417 | -0.091553 | 0.086975 | 122.6074 | -0.39368 | -0.32501 | 0.036621 | 0.42114 | 109.6893 | 107.5653 | 122.3602 | 122.6624 | 0.086975 | 122.7905 | 114.2487 | -0.32501 | 122.6624 | 0.086975 | 114.2487 | 122.3602 | 122.7905 | -123.0881 | -123.0789
1793.9062 | 122.9599 | -122.0764 | 0.64087 | -0.17136 | 0.00023916 | 0.001959 | 0.018641 | -0.0081754 | -0.0011471 | 0.0038389 | -121.8475 | 0.59509 | -122.3831 | 0.59509 | 0.32501 | -7.2739 | -11.5448 | -13.9435 | 0.67749 | -122.3923 | -0.3067 | -0.045776 | 0.22888 | 122.6715 | -0.31586 | -0.31586 | 0.036621 | 0.53558 | 110.5316 | 108.1329 | 122.4014 | 122.6715 | 0.22888 | 122.7539 | 114.8026 | -0.31586 | 122.6715 | 0.22888 | 114.8026 | 122.4014 | 122.7539 | -123.024 | -123.0331
1794.9688 | 122.8958 | -122.113 | 0.65002 | 0.065155 | 0.0013074 | 0.0068722 | 0.017359 | -0.0068936 | -0.00071986 | 0.0029843 | -122.1588 | 0.55847 | -122.5067 | 0.48065 | 0.21515 | -7.3883 | -11.9019 | -14.3463 | 0.64545 | -122.4243 | -0.39368 | -0.091552 | -0.045776 | 122.5937 | -0.43488 | -0.31128 | -0.004577 | 0.3479 | 110.2112 | 107.7667 | 122.3282 | 122.6715 | -0.045776 | 122.7585 | 114.7247 | -0.31128 | 122.6715 | -0.045776 | 114.7247 | 122.3282 | 122.7585 | -123.1567 | -123.0743
1795.9062 | 122.85 | -122.1222 | 0.6546 | -0.20187 | 0.0019482 | 0.005377 | 0.026545 | -0.0043302 | -0.0026425 | 0.0025571 | -121.8796 | 0.60425 | -122.4289 | 0.52185 | 0.22888 | -7.283 | -11.8561 | -14.36 | 0.70038 | -122.4838 | -0.3067 | -0.050354 | 0.24261 | 122.644 | -0.42572 | -0.36163 | 0.045776 | 0.54932 | 110.2661 | 107.7621 | 122.3511 | 122.7264 | 0.24261 | 122.8226 | 114.8392 | -0.36163 | 122.7264 | 0.24261 | 114.8392 | 122.3511 | 122.8226 | -123.0835 | -123.1384
1796.9062 | 122.9874 | -122.0901 | 0.67291 | -0.1561 | 0.00066656 | 0.0021726 | 0.015009 | -0.0060392 | -0.0015745 | 0.0031979 | -121.8109 | 0.5722 | -122.4014 | 0.59509 | 0.31586 | -7.1777 | -11.3892 | -14.1815 | 0.66834 | -122.374 | -0.31128 | -0.10071 | 0.27924 | 122.6852 | -0.35706 | -0.28381 | -0.004578 | 0.59051 | 110.701 | 107.9086 | 122.406 | 122.6624 | 0.27924 | 122.7585 | 114.9124 | -0.28381 | 122.6624 | 0.27924 | 114.9124 | 122.406 | 122.7585 | -123.0743 | -123.0469
1797.9688 | 122.9095 | -122.1085 | 0.65918 | 0.13382 | 0.0017346 | -0.00017722 | 0.016718 | -0.0058256 | -0.0022153 | 0.0064023 | -121.9391 | 0.55389 | -122.4152 | 0.50812 | 0.2243 | -7.5027 | -11.554 | -14.5157 | 0.66376 | -122.4243 | -0.3067 | -0.10529 | 0.16937 | 122.6166 | -0.43488 | -0.31586 | 0.004577 | 0.47607 | 110.5545 | 107.5928 | 122.3328 | 122.6624 | 0.16937 | 122.7722 | 114.6057 | -0.31586 | 122.6624 | 0.16937 | 114.6057 | 122.3328 | 122.7722 | -123.0743 | -123.0835
1798.9062 | 122.9324 | -122.081 | 0.65918 | -0.18662 | 2.5564e-05 | 0.0060178 | 0.018854 | -0.0071072 | -0.0032835 | 0.0029843 | -121.8979 | 0.56763 | -122.4152 | 0.56305 | 0.28381 | -7.3883 | -11.6592 | -14.6759 | 0.67291 | -122.4335 | -0.33417 | -0.091553 | 0.18311 | 122.644 | -0.37537 | -0.35248 | 0.013733 | 0.51727 | 110.4218 | 107.4051 | 122.3648 | 122.6486 | 0.18311 | 122.7539 | 114.6927 | -0.35248 | 122.6486 | 0.18311 | 114.6927 | 122.3648 | 122.7539 | -123.0743 | -123.0927
1799.9531 | 122.9141 | -122.0993 | 0.6546 | 0.15671 | 0.00023916 | 0.00089078 | 0.019495 | -0.0077482 | 0.00013454 | 0.0049069 | -121.9574 | 0.53101 | -122.438 | 0.5127 | 0.24719 | -7.5623 | -11.8835 | -14.3326 | 0.67291 | -122.4197 | -0.33875 | -0.1236 | 0.14191 | 122.612 | -0.40741 | -0.32044 | 0.018311 | 0.48065 | 110.2158 | 107.7667 | 122.3465 | 122.6303 | 0.14191 | 122.7722 | 114.537 | -0.32044 | 122.6303 | 0.14191 | 114.537 | 122.3465 | 122.7722 | -123.0927 | -123.0743
1800.9062 | 122.7676 | -122.1039 | 0.69122 | -0.27054 | 0.0028028 | 0.0034544 | 0.022272 | -0.0056118 | -0.0037107 | 0.0038389 | -121.9803 | 0.58594 | -122.4472 | 0.46692 | 0.16479 | -7.5989 | -11.7554 | -13.8794 | 0.70038 | -122.4518 | -0.34332 | -0.10529 | 0.1236 | 122.5708 | -0.52643 | -0.3479 | 0.009155 | 0.46692 | 110.3485 | 108.2245 | 122.2687 | 122.6898 | 0.1236 | 122.8043 | 114.505 | -0.3479 | 122.6898 | 0.1236 | 114.505 | 122.2687 | 122.8043 | -123.1384 | -123.143
1801.9688 | 122.9187 | -122.081 | 0.63629 | 0.13382 | 0.0013074 | 0.00046358 | 0.019282 | -0.0051846 | -0.0026425 | 0.0038389 | -121.8887 | 0.54016 | -122.4014 | 0.54932 | 0.27008 | -7.2189 | -11.7508 | -14.3463 | 0.65918 | -122.406 | -0.32043 | -0.096131 | 0.19226 | 122.6303 | -0.36621 | -0.32501 | 0.022888 | 0.51269 | 110.3302 | 107.7347 | 122.3511 | 122.6212 | 0.19226 | 122.7402 | 114.8621 | -0.32501 | 122.6212 | 0.19226 | 114.8621 | 122.3511 | 122.7402 | -123.0377 | -123.0423
1802.9062 | 122.9233 | -122.0947 | 0.60883 | -0.1561 | 0.00066656 | 0.00067718 | 0.017359 | -0.0071072 | 0.00077554 | 0.0017027 | -121.8704 | 0.54932 | -122.4014 | 0.68665 | 0.39825 | -7.3105 | -12.1033 | -14.4653 | 0.6546 | -122.4289 | -0.3067 | -0.05951 | 0.22431 | 122.7814 | -0.21057 | -0.33417 | 0.045776 | 0.53101 | 109.9915 | 107.6294 | 122.493 | 122.644 | 0.22431 | 122.7493 | 114.7842 | -0.33417 | 122.644 | 0.22431 | 114.7842 | 122.493 | 122.7493 | -123.0103 | -123.0377
1803.9688 | 122.8867 | -122.113 | 0.67291 | 0.0041197 | -0.001256 | 0.0011044 | 0.018427 | -0.0071072 | -0.0020017 | 0.0042661 | -121.9711 | 0.57678 | -122.4243 | 0.51727 | 0.24261 | -7.5531 | -11.7188 | -14.6851 | 0.68665 | -122.4243 | -0.31128 | -0.096131 | 0.14191 | 122.6303 | -0.4303 | -0.31128 | 0.013733 | 0.45319 | 110.3943 | 107.428 | 122.3557 | 122.6898 | 0.14191 | 122.7997 | 114.5599 | -0.31128 | 122.6898 | 0.14191 | 114.5599 | 122.3557 | 122.7997 | -123.0972 | -123.0972
1804.9062 | 122.9324 | -122.0901 | 0.64087 | 0.14908 | -0.00040164 | 0.003668 | 0.017145 | -0.00668 | -0.00093346 | 0.0014889 | -121.8613 | 0.53101 | -122.4106 | 0.57678 | 0.29755 | -7.6309 | -11.3388 | -14.3692 | 0.6546 | -122.406 | -0.32043 | -0.10986 | 0.22888 | 122.6669 | -0.34332 | -0.31586 | 0.013733 | 0.54932 | 110.7513 | 107.7209 | 122.3877 | 122.6212 | 0.22888 | 122.7448 | 114.4592 | -0.31586 | 122.6212 | 0.22888 | 114.4592 | 122.3877 | 122.7448 | -123.0515 | -123.0469
1805.9688 | 122.8226 | -122.1268 | 0.65918 | -0.2858 | 0.0047254 | 0.00089078 | 0.023554 | -0.0041166 | 0.00013454 | 0.0019163 | -121.9894 | 0.62256 | -122.4426 | 0.45319 | 0.18768 | -7.8964 | -11.0596 | -14.4745 | 0.70038 | -122.493 | -0.31586 | -0.036621 | 0.13733 | 122.58 | -0.4715 | -0.36621 | 0.041198 | 0.45319 | 111.0672 | 107.6523 | 122.3145 | 122.7493 | 0.13733 | 122.8271 | 114.2303 | -0.36621 | 122.7493 | 0.13733 | 114.2303 | 122.3145 | 122.8271 | -123.1018 | -123.1522
1806.9062 | 122.9141 | -122.0901 | 0.65918 | -0.14084 | -0.0021106 | 0.0060178 | 0.018641 | -0.0068936 | -0.0034971 | 0.0029843 | -121.8704 | 0.54016 | -122.4243 | 0.55389 | 0.28839 | -7.9742 | -11.0687 | -14.2685 | 0.66834 | -122.406 | -0.33417 | -0.11902 | 0.21973 | 122.644 | -0.37079 | -0.31586 | 0.009155 | 0.55389 | 111.0214 | 107.8217 | 122.3785 | 122.6303 | 0.21973 | 122.7585 | 114.1159 | -0.31586 | 122.6303 | 0.21973 | 114.1159 | 122.3785 | 122.7585 | -123.0835 | -123.0652
1807.9531 | 122.9004 | -122.1085 | 0.62714 | 0.15671 | -0.0016834 | 0.0040952 | 0.017573 | -0.0047574 | -0.0017881 | 0.0059751 | -121.9299 | 0.52643 | -122.4243 | 0.49896 | 0.24261 | -8.1024 | -11.1191 | -14.1129 | 0.64545 | -122.4243 | -0.31586 | -0.10071 | 0.17853 | 122.6074 | -0.38452 | -0.31586 | 0.018311 | 0.49438 | 110.9894 | 107.9956 | 122.3511 | 122.6349 | 0.17853 | 122.7539 | 114.006 | -0.31586 | 122.6349 | 0.17853 | 114.006 | 122.3511 | 122.7539 | -123.0515 | -123.0515
1808.9062 | 122.9553 | -122.1085 | 0.6134 | -0.018768 | -0.00082884 | 0.00046358 | 0.017145 | -0.0056118 | -0.0022153 | 0.0046933 | -122.6807 | 0.54474 | -122.4335 | 0.5722 | 0.32044 | -8.313 | -11.5356 | -13.9069 | 0.63629 | -122.4014 | -0.32501 | -0.068664 | -0.5722 | 122.6807 | -0.29297 | -0.29297 | 0.022889 | -0.24719 | 110.5728 | 108.2016 | 122.4289 | 122.6532 | -0.5722 | 122.7448 | 113.7955 | -0.29297 | 122.6532 | -0.5722 | 113.7955 | 122.4289 | 122.7448 | -123.0469 | -123.0148
1809.9688 | 122.8455 | -122.1542 | 0.64087 | 0.17197 | 0.0019482 | 0.0058042 | 0.023554 | -0.0045438 | -0.0017881 | 0.0036253 | -121.9757 | 0.56763 | -122.4564 | 0.42572 | 0.16479 | -8.2581 | -11.2244 | -14.3967 | 0.6546 | -122.4609 | -0.30212 | -0.073242 | 0.17853 | 122.58 | -0.47607 | -0.3067 | 0.013733 | 0.48065 | 110.9299 | 107.7576 | 122.319 | 122.7219 | 0.17853 | 122.8088 | 113.8962 | -0.3067 | 122.7219 | 0.17853 | 113.8962 | 122.319 | 122.8088 | -123.0972 | -123.1018
1810.9219 | 122.8683 | -122.1359 | 0.64545 | -0.14847 | 0.0062208 | 0.0070858 | 0.024622 | -0.003903 | -0.0039243 | 0.0027707 | -121.8796 | 0.58136 | -122.4472 | 0.49439 | 0.22888 | -8.4732 | -11.3709 | -14.6347 | 0.66376 | -122.4747 | -0.31128 | -0.064087 | 0.25635 | 122.6303 | -0.41656 | -0.33875 | 0.01831 | 0.56763 | 110.7651 | 107.5012 | 122.3648 | 122.7173 | 0.25635 | 122.7997 | 113.6627 | -0.33875 | 122.7173 | 0.25635 | 113.6627 | 122.3648 | 122.7997 | -123.0927 | -123.1201
1811.9688 | 122.937 | -122.2458 | 0.57678 | 0.027008 | 2.5564e-05 | 0.0017454 | 0.014795 | -0.0041166 | -0.0011471 | 0.0038389 | -121.9391 | 0.52643 | -122.4701 | 0.48065 | 0.24719 | -8.9355 | -10.9817 | -14.6576 | 0.64545 | -122.4472 | -0.2243 | -0.050354 | 0.3067 | 122.7264 | -0.32959 | -0.20142 | 0.068665 | 0.53101 | 111.264 | 107.5882 | 122.493 | 122.7722 | 0.3067 | 122.8912 | 113.3102 | -0.20142 | 122.7722 | 0.3067 | 113.3102 | 122.493 | 122.8912 | -123.0469 | -123.024
1812.9062 | 122.9187 | -122.1222 | 0.62714 | 0.0041197 | 0.0017346 | 0.0070858 | 0.019495 | -0.0068936 | -0.00071986 | 0.0049069 | -122.0673 | 0.54474 | -122.4197 | 0.51727 | 0.27008 | -10.2448 | -10.9863 | -14.9872 | 0.64545 | -122.4197 | -0.29755 | -0.082397 | 0.054931 | 122.6395 | -0.35706 | -0.29755 | 0.018311 | 0.35248 | 111.1359 | 107.135 | 122.3923 | 122.6669 | 0.054931 | 122.7676 | 111.8774 | -0.29755 | 122.6669 | 0.054931 | 111.8774 | 122.3923 | 122.7676 | -123.0469 | -123.0469
1813.9688 | 122.8638 | -122.1268 | 0.66376 | 0.1033 | 0.0030164 | 0.0045224 | 0.025049 | -0.0036892 | -0.0037107 | 0.0059751 | -122.0398 | 0.56305 | -122.4838 | 0.42114 | 0.14191 | -10.8673 | -11.6455 | -15.033 | 0.68665 | -122.438 | -0.35706 | -0.10071 | 0.086975 | 122.5479 | -0.52185 | -0.31128 | 0.022889 | 0.44403 | 110.4813 | 107.0938 | 122.2687 | 122.6898 | 0.086975 | 122.8134 | 111.2595 | -0.31128 | 122.6898 | 0.086975 | 111.2595 | 122.2687 | 122.8134 | -123.1476 | -123.1018
1814.9062 | 122.9141 | -122.1405 | 0.61798 | 0.0041197 | 0.0019482 | 0.003027 | 0.01565 | -0.0062528 | -0.0030697 | 0.0031979 | -121.8063 | 0.53101 | -122.4289 | 0.48065 | 0.24261 | -9.6405 | -10.9772 | -14.9414 | 0.65002 | -122.4289 | -0.28839 | -0.086975 | 0.33417 | 122.6212 | -0.37537 | -0.28839 | 0.032043 | 0.62256 | 111.1633 | 107.1991 | 122.3831 | 122.6715 | 0.33417 | 122.7905 | 112.5 | -0.28839 | 122.6715 | 0.33417 | 112.5 | 122.3831 | 122.7905 | -123.0469 | -123.0469
1815.9688 | 122.905 | -122.1039 | 0.63171 | 0.15671 | -0.0010424 | 0.0034544 | 0.020563 | -0.0058256 | -0.00029266 | 0.0057615 | -121.9986 | 0.58136 | -122.4243 | 0.5127 | 0.26093 | -10.8994 | -11.348 | -14.8911 | 0.64087 | -122.4243 | -0.32043 | -0.050354 | 0.10529 | 122.6166 | -0.37079 | -0.32043 | 0.009155 | 0.42572 | 110.7559 | 107.2128 | 122.3648 | 122.6852 | 0.10529 | 122.7448 | 111.2045 | -0.32043 | 122.6852 | 0.10529 | 111.2045 | 122.3648 | 122.7448 | -123.056 | -123.056
1816.9062 | 122.9599 | -122.113 | 0.59052 | -0.095062 | -0.00082884 | 0.0043088 | 0.017573 | -0.0071072 | -0.0020017 | 0.0027707 | -121.9345 | 0.52643 | -122.4518 | 0.54474 | 0.27924 | -9.6451 | -11.0504 | -14.5889 | 0.61798 | -122.438 | -0.33874 | -0.064087 | 0.17853 | 122.6578 | -0.31128 | -0.32501 | 0.027466 | 0.51727 | 111.0626 | 107.5241 | 122.3923 | 122.6395 | 0.17853 | 122.731 | 112.468 | -0.32501 | 122.6395 | 0.17853 | 112.468 | 122.3923 | 122.731 | -123.0423 | -123.0286
1817.9688 | 122.9645 | -122.168 | 0.55847 | 0.1796 | 0.001521 | 0.0066586 | 0.022913 | -0.0056118 | -0.0011471 | 0.0029843 | -121.994 | 0.5127 | -122.4609 | 0.3479 | 0.20142 | -9.993 | -10.7529 | -15.0146 | 0.58594 | -122.4609 | -0.29297 | -0.045777 | 0.17395 | 122.5159 | -0.35706 | -0.29297 | 0.027465 | 0.46692 | 111.4151 | 107.1533 | 122.3694 | 122.6807 | 0.17395 | 122.7539 | 112.175 | -0.29297 | 122.6807 | 0.17395 | 112.175 | 122.3694 | 122.7539 | -123.0194 | -123.0194
1818.9062 | 122.9187 | -122.1313 | 0.6134 | 0.080414 | 0.00045296 | 0.00046358 | 0.016932 | -0.0064664 | -0.00071986 | 0.0019163 | -121.9894 | 0.52643 | -122.4472 | 0.4715 | 0.20142 | -12.0346 | -10.08 | -14.772 | 0.60883 | -122.438 | -0.31586 | -0.086975 | 0.14191 | 122.6028 | -0.41199 | -0.3067 | -0.004577 | 0.45776 | 112.0514 | 107.3593 | 122.3328 | 122.6578 | 0.14191 | 122.7402 | 110.0967 | -0.3067 | 122.6578 | 0.14191 | 110.0967 | 122.3328 | 122.7402 | -123.0606 | -123.0515
1819.9688 | 122.9279 | -122.1359 | 0.6134 | 0.15671 | 0.00066656 | 0.0021726 | 0.018427 | -0.0064664 | -0.0020017 | 0.0038389 | -121.7514 | 0.5127 | -122.4564 | 0.49896 | 0.2243 | -11.6684 | -10.35 | -14.7217 | 0.62714 | -122.4609 | -0.32044 | -0.10071 | 0.38452 | 122.6349 | -0.3891 | -0.32501 | 0.013733 | 0.70496 | 111.7859 | 107.4142 | 122.3602 | 122.6486 | 0.38452 | 122.7631 | 110.4675 | -0.32501 | 122.6486 | 0.38452 | 110.4675 | 122.3602 | 122.7631 | -123.0698 | -123.0743
1820.9219 | 122.8455 | -122.1771 | 0.62714 | -0.095062 | 0.0025892 | 0.009863 | 0.024622 | -0.0060392 | -0.0022153 | 0.0042661 | -121.8246 | 0.56763 | -122.4747 | 0.48981 | 0.17853 | -11.174 | -10.0159 | -14.1861 | 0.64087 | -122.5525 | -0.29755 | -0.059509 | 0.35248 | 122.6669 | -0.44861 | -0.37537 | 0.013733 | 0.65002 | 112.1613 | 107.991 | 122.3557 | 122.7448 | 0.35248 | 122.818 | 111.0031 | -0.37537 | 122.7448 | 0.35248 | 111.0031 | 122.3557 | 122.818 | -123.1018 | -123.1796
1821.9531 | 122.9279 | -122.1313 | 0.59967 | -0.0035098 | -0.00061524 | 0.005377 | 0.014368 | -0.003262 | -7.9062e-05 | 0.0021299 | -121.9986 | 0.51727 | -122.4792 | 0.46234 | 0.23804 | -10.73 | -10.144 | -14.0854 | 0.63171 | -122.4609 | -0.3479 | -0.082397 | 0.13275 | 122.5937 | -0.36163 | -0.32959 | 0.032044 | 0.48065 | 111.9873 | 108.046 | 122.3694 | 122.6486 | 0.13275 | 122.7631 | 111.4014 | -0.32959 | 122.6486 | 0.13275 | 111.4014 | 122.3694 | 122.7631 | -123.0789 | -123.0606
1822.9062 | 122.9279 | -122.1313 | 0.59967 | 0.1033 | -0.0010424 | 0.0017454 | 0.017145 | -0.0060392 | -0.0015745 | 0.0034115 | -122.0398 | 0.48523 | -122.5021 | 0.46692 | 0.2243 | -10.5789 | -10.1028 | -14.0671 | 0.63629 | -122.4518 | -0.37079 | -0.11444 | 0.091553 | 122.5983 | -0.37537 | -0.32043 | 0.036622 | 0.46234 | 112.0285 | 108.0643 | 122.3557 | 122.6166 | 0.091553 | 122.7676 | 111.5524 | -0.32043 | 122.6166 | 0.091553 | 111.5524 | 122.3557 | 122.7676 | -123.1018 | -123.0515
1823.9688 | 122.8592 | -122.1863 | 0.59967 | 0.17197 | 0.0023756 | 0.0049496 | 0.023768 | -0.0043302 | -0.0020017 | 0.0034115 | -121.9894 | 0.54932 | -122.5021 | 0.41199 | 0.16022 | -9.7458 | -9.9289 | -13.8519 | 0.63629 | -122.4884 | -0.31586 | -0.050354 | 0.19684 | 122.5983 | -0.43945 | -0.30212 | 0.036622 | 0.51269 | 112.2574 | 108.3344 | 122.3465 | 122.7356 | 0.19684 | 122.8226 | 112.4405 | -0.30212 | 122.7356 | 0.19684 | 112.4405 | 122.3465 | 122.8226 | -123.1018 | -123.0881
1824.9062 | 122.6395 | -73.3704 | 49.1089 | 0.21011 | 0.002162 | 0.001959 | 1.4971 | -0.0058256 | 0.00034814 | 1.5013 | -74.0753 | 48.9578 | -74.0845 | 47.9782 | 46.8567 | -0.13733 | 2.6276 | -3.36 | 48.8022 | -73.4985 | -0.71411 | -0.15106 | -0.70496 | 121.3486 | -2.2522 | -0.12817 | -0.3067 | 0.009156 | 75.9979 | 70.0104 | 120.2271 | 122.3282 | -0.70496 | 122.1725 | 73.233 | -0.12817 | 122.3282 | -0.70496 | 73.233 | 120.2271 | 122.1725 | -123.1934 | -122.6074
1825.9688 | 105.2536 | -14.3188 | 84.1003 | 0.11093 | 0.0025892 | 0.005377 | 0.0071051 | -0.0053982 | -0.0032835 | 0.017938 | -10.5103 | 112.0743 | -10.9726 | 112.2482 | 99.4904 | -7.3059 | 4.4586 | 12.0712 | 106.8878 | -15.8661 | 3.3463 | 27.9739 | 3.8086 | 126.5671 | 15.39 | -1.5472 | 22.7875 | 0.46234 | 18.7775 | 26.3901 | 113.8092 | 126.3931 | 3.8086 | 121.2067 | 7.0129 | -1.5472 | 126.3931 | 3.8086 | 7.0129 | 113.8092 | 121.2067 | -95.0729 | -99.9664
1826.9062 | 122.6212 | -5.4428 | 116.4734 | 0.14908 | 0.0034436 | 0.003668 | 0.0049689 | -0.0064664 | 0.00034814 | 0.025415 | -5.484 | 117.215 | -5.809 | 117.4347 | 115.0085 | 9.874 | 7.7545 | 9.6451 | 117.2791 | -5.6946 | -0.36621 | 0.74158 | -0.041199 | 122.8775 | -1.4648 | -0.25177 | 0.80566 | 0.32501 | 13.1973 | 15.0879 | 120.4514 | 122.6578 | -0.041199 | 122.7219 | 15.3168 | -0.25177 | 122.6578 | -0.041199 | 15.3168 | 120.4514 | 122.7219 | -122.2824 | -122.168
1827.9688 | 122.8592 | -79.8386 | 41.4139 | 0.51529 | 0.0025892 | 0.0066586 | 0.0098823 | -0.0047574 | -0.0037107 | 0.0031979 | -70.6512 | 57.8751 | -62.677 | 49.0173 | 46.582 | -5.0858 | -5.159 | -5.8502 | 47.7081 | -77.1698 | 17.1616 | 16.4612 | 9.1873 | 128.8559 | 5.1682 | 2.6688 | 6.2943 | -7.9742 | 74.6796 | 73.9883 | 126.4206 | 137.7136 | 9.1873 | 127.5467 | 74.7528 | 2.6688 | 137.7136 | 9.1873 | 74.7528 | 126.4206 | 127.5467 | -104.0909 | -118.5837
1828.9062 | 122.8638 | -70.0104 | 52.5604 | 0.13382 | 0.0023756 | 0.0068722 | 0.0021917 | -0.0062528 | -0.0022153 | 0.00063446 | -74.4598 | 49.5575 | -73.6908 | 53.3478 | 51.7639 | -1.0117 | -1.2039 | -1.9821 | 52.652 | -70.2896 | -3.6804 | -3.0029 | -4.4495 | 123.3582 | -0.79651 | -0.27924 | 0.091553 | -0.76904 | 68.8065 | 68.0283 | 121.7743 | 119.5679 | -4.4495 | 122.6624 | 68.9987 | -0.27924 | 119.5679 | -4.4495 | 68.9987 | 121.7743 | 122.6624 | -126.2512 | -122.85
1829.9688 | 122.9416 | -112.6968 | 9.8785 | 0.19485 | 0.0030164 | 0.004736 | 0.019282 | -0.0060392 | -0.0015745 | 0.0038389 | -112.4817 | 9.8694 | -113.0951 | 9.9792 | 9.494 | -7.6492 | -7.9971 | -10.8444 | 9.9426 | -113.0722 | -0.39826 | -0.009155 | 0.21515 | 122.6761 | -0.38452 | -0.37537 | 0.064087 | 0.6134 | 104.6997 | 101.8524 | 122.1909 | 122.5662 | 0.21515 | 122.6395 | 105.0476 | -0.37537 | 122.5662 | 0.21515 | 105.0476 | 122.1909 | 122.6395 | -122.9736 | -122.9507
1830.9062 | 122.8958 | -115.9836 | 6.72 | 0.14145 | -0.00040164 | 0.0021726 | 0.017145 | -0.00668 | -0.00093346 | 0.0034115 | -115.8234 | 6.6238 | -116.3452 | 6.6513 | 6.2897 | -8.1436 | -8.5281 | -11.618 | 6.752 | -116.2628 | -0.36163 | -0.096131 | 0.16022 | 122.6349 | -0.4303 | -0.27923 | 0.032043 | 0.52185 | 107.4554 | 104.3655 | 122.2733 | 122.6074 | 0.16022 | 122.7356 | 107.84 | -0.27923 | 122.6074 | 0.16022 | 107.84 | 122.2733 | 122.7356 | -123.0652 | -122.9828
1831.9531 | 122.9233 | -116.716 | 5.9967 | 0.20248 | -0.00040164 | 0.0075132 | 0.017359 | -0.0060392 | -0.00093346 | 0.0040525 | -116.478 | 5.9052 | -117.0273 | 5.9601 | 5.5664 | -10.3683 | -8.7112 | -11.8835 | 6.0196 | -116.9861 | -0.31128 | -0.091553 | 0.23804 | 122.6761 | -0.4303 | -0.27008 | 0.022888 | 0.54932 | 108.0048 | 104.8325 | 122.2824 | 122.6212 | 0.23804 | 122.7356 | 106.3477 | -0.27008 | 122.6212 | 0.23804 | 106.3477 | 122.2824 | 122.7356 | -123.024 | -122.9828
1832.9062 | 122.9553 | -116.4917 | 6.189 | 0.14908 | 0.00088016 | 0.0025998 | 0.018 | -0.0045438 | -0.0017881 | 0.0036253 | -116.2857 | 6.1111 | -116.8121 | 6.1844 | 5.7587 | -10.0204 | -8.3313 | -11.6501 | 6.2073 | -116.8259 | -0.32044 | -0.07782 | 0.20599 | 122.6761 | -0.4303 | -0.33417 | 0.01831 | 0.52643 | 108.1604 | 104.8416 | 122.2504 | 122.6028 | 0.20599 | 122.699 | 106.4713 | -0.33417 | 122.6028 | 0.20599 | 106.4713 | 122.2504 | 122.699 | -123.0011 | -123.0148
1833.9688 | 122.905 | -116.6794 | 6.0196 | 0.14145 | 0.0025892 | 0.0094358 | 0.021845 | -0.00668 | -0.0039243 | 0.0040525 | -116.3727 | 5.9738 | -116.9357 | 6.0287 | 5.6488 | -10.318 | -8.7021 | -11.9431 | 6.0791 | -116.9174 | -0.25635 | -0.045776 | 0.3067 | 122.7081 | -0.37079 | -0.23804 | 0.05951 | 0.56305 | 107.9773 | 104.7363 | 122.3282 | 122.6532 | 0.3067 | 122.7585 | 106.3614 | -0.23804 | 122.6532 | 0.3067 | 106.3614 | 122.3282 | 122.7585 | -122.9553 | -122.937
1834.9062 | 122.8912 | -116.7435 | 5.9692 | 0.69839 | 0.00045296 | 0.0034544 | 0.015009 | -0.0045438 | -0.00029266 | 0.0036253 | -116.6016 | 5.8228 | -117.0593 | 5.8456 | 5.4977 | -10.4599 | -8.1436 | -12.0712 | 5.9647 | -117.0914 | -0.31586 | -0.14648 | 0.14191 | 122.5891 | -0.4715 | -0.3479 | -0.004577 | 0.45776 | 108.5999 | 104.6722 | 122.2412 | 122.5662 | 0.14191 | 122.7081 | 106.2836 | -0.3479 | 122.5662 | 0.14191 | 106.2836 | 122.2412 | 122.7081 | -123.0286 | -123.0606
1835.9688 | 122.9691 | -114.4043 | 8.2306 | -0.11032 | -0.00018804 | -0.00081822 | 0.014582 | -0.0081754 | -0.0034971 | 0.0049069 | -114.212 | 8.1711 | -114.7522 | 8.2764 | 7.8186 | -7.0496 | -7.9834 | -11.5265 | 8.2581 | -114.743 | -0.3479 | -0.059509 | 0.19226 | 122.6807 | -0.41199 | -0.33875 | 0.027466 | 0.54016 | 106.4209 | 102.8778 | 122.2229 | 122.5754 | 0.19226 | 122.6624 | 107.3547 | -0.33875 | 122.5754 | 0.19226 | 107.3547 | 122.2229 | 122.6624 | -122.9828 | -122.9736
1836.9062 | 122.9141 | -116.4917 | 6.1844 | 0.25589 | 0.0034436 | 0.0028134 | 0.02035 | -0.00668 | -0.00071986 | 0.0034115 | -116.3132 | 6.0745 | -116.8076 | 6.1386 | 5.7404 | -8.5648 | -8.5876 | -11.9934 | 6.1798 | -116.835 | -0.31586 | -0.10986 | 0.17853 | 122.6303 | -0.44403 | -0.34332 | -0.004577 | 0.49439 | 107.9041 | 104.4983 | 122.2321 | 122.5662 | 0.17853 | 122.6715 | 107.9269 | -0.34332 | 122.5662 | 0.17853 | 107.9269 | 122.2321 | 122.6715 | -122.9919 | -123.0194
1837.9531 | 122.8134 | -117.3706 | 5.4291 | 0.16434 | 0.00323 | 0.0090086 | 0.022272 | -0.0028348 | -0.0037107 | 0.0049069 | -117.1371 | 5.3558 | -117.6636 | 5.2689 | 4.8752 | -8.4641 | -8.5098 | -12.3184 | 5.4291 | -117.6453 | -0.29297 | -0.073242 | 0.23346 | 122.6395 | -0.55389 | -0.27466 | 0 | 0.52643 | 108.8608 | 105.0522 | 122.2458 | 122.7264 | 0.23346 | 122.7997 | 108.9066 | -0.27466 | 122.7264 | 0.23346 | 108.9066 | 122.2458 | 122.7997 | -123.0927 | -123.0743
1838.9062 | 122.9874 | -117.1188 | 5.603 | 0.1796 | 0.00088016 | 0.0077268 | 0.019922 | -0.0030484 | -0.0030697 | 0.0042661 | -116.8121 | 5.5664 | -117.3523 | 5.6259 | 5.2368 | -7.3151 | -8.8257 | -12.3734 | 5.658 | -117.3981 | -0.23346 | -0.036621 | 0.3067 | 122.7448 | -0.36621 | -0.27924 | 0.054932 | 0.54016 | 108.2932 | 104.7455 | 122.3557 | 122.6852 | 0.3067 | 122.7768 | 109.8038 | -0.27924 | 122.6852 | 0.3067 | 109.8038 | 122.3557 | 122.7768 | -122.9553 | -123.0011
1839.9062 | 122.9416 | -116.2354 | 6.3675 | 0.26352 | 0.0030164 | 0.0072996 | 0.02035 | -0.0043302 | -0.0032835 | 0.0053343 | -116.2994 | 6.1203 | -116.803 | 6.1752 | 5.7816 | -7.1869 | -8.6105 | -11.8103 | 6.2256 | -116.6977 | -0.56763 | -0.24719 | -0.064086 | 122.4106 | -0.58594 | -0.46234 | -0.14191 | 0.50354 | 107.6248 | 104.425 | 122.0169 | 122.3557 | -0.064086 | 122.4609 | 109.0485 | -0.46234 | 122.3557 | -0.064086 | 109.0485 | 122.0169 | 122.4609 | -123.1705 | -123.0652
1840.9062 | 122.937 | -117.1143 | 5.5939 | -0.087433 | -0.00018804 | 0.0032406 | 0.016504 | -0.0077482 | 0.00077554 | 0.0034115 | -116.9403 | 5.4749 | -117.4667 | 5.5298 | 5.159 | -6.3583 | -8.606 | -11.998 | 5.5847 | -117.4255 | -0.35248 | -0.11902 | 0.17395 | 122.644 | -0.43487 | -0.31128 | -0.009155 | 0.52643 | 108.5083 | 105.1163 | 122.2733 | 122.5891 | 0.17395 | 122.699 | 110.7559 | -0.31128 | 122.5891 | 0.17395 | 110.7559 | 122.2733 | 122.699 | -123.0606 | -123.0194
1841.9531 | 122.8683 | -117.4988 | 5.246 | -0.11795 | 0.0034436 | 0.006445 | 0.024408 | -0.0056118 | -0.0034971 | 0.0044797 | -117.2699 | 5.1407 | -117.8238 | 5.1361 | 4.7607 | -6.7383 | -8.3267 | -12.0621 | 5.246 | -117.8604 | -0.32501 | -0.10529 | 0.22888 | 122.6349 | -0.48523 | -0.36163 | 0 | 0.55389 | 109.1721 | 105.4367 | 122.2595 | 122.6395 | 0.22888 | 122.7448 | 110.7605 | -0.36163 | 122.6395 | 0.22888 | 110.7605 | 122.2595 | 122.7448 | -123.0698 | -123.1064
1842.9219 | 122.905 | -117.366 | 5.4016 | -0.12558 | 0.00023916 | 0.0021726 | 0.017359 | -0.0051846 | -0.0032835 | 0.0046933 | -117.1097 | 5.3009 | -117.6544 | 5.3375 | 4.985 | -6.3858 | -8.8394 | -12.1262 | 5.4108 | -117.6224 | -0.28839 | -0.10071 | 0.25635 | 122.7036 | -0.41657 | -0.25635 | 0.009156 | 0.54474 | 108.5266 | 105.2399 | 122.3511 | 122.6669 | 0.25635 | 122.7768 | 110.9802 | -0.25635 | 122.6669 | 0.25635 | 110.9802 | 122.3511 | 122.7768 | -123.056 | -123.024
1843.9688 | 122.8317 | -117.2928 | 5.4245 | -1.6209 | 0.0042982 | 0.0079404 | 0.024836 | -0.0036892 | -0.0024289 | 0.0049069 | -117.1783 | 5.3925 | -117.6544 | 5.2734 | 4.866 | -6.8344 | -8.844 | -12.3367 | 5.4657 | -117.6407 | -0.36163 | -0.032044 | 0.11444 | 122.5662 | -0.55847 | -0.3479 | 0.041198 | 0.47607 | 108.4488 | 104.9561 | 122.1588 | 122.6852 | 0.11444 | 122.7585 | 110.4584 | -0.3479 | 122.6852 | 0.11444 | 110.4584 | 122.1588 | 122.7585 | -123.0789 | -123.0652
1844.9062 | 122.937 | -116.4551 | 6.2027 | 0.22537 | 0.0017346 | 0.0072996 | 0.016504 | -0.0036892 | -0.00029266 | 0.0055479 | -116.2949 | 6.1386 | -116.7755 | 6.1752 | 5.7953 | -6.3995 | -8.5968 | -11.7645 | 6.2256 | -116.8304 | -0.32044 | -0.064087 | 0.16022 | 122.6303 | -0.40741 | -0.37537 | 0.022888 | 0.48065 | 107.8583 | 104.6906 | 122.2504 | 122.5937 | 0.16022 | 122.6807 | 110.0555 | -0.37537 | 122.5937 | 0.16022 | 110.0555 | 122.2504 | 122.6807 | -122.9782 | -123.0331
1845.9688 | 122.937 | -116.9037 | 5.7907 | 0.19485 | 0.00088016 | 0.0034544 | 0.020777 | -0.003903 | -0.0034971 | 0.0044797 | -116.6428 | 5.7358 | -117.1921 | 5.8044 | 5.3101 | -6.8573 | -8.8165 | -11.5402 | 5.7953 | -117.2104 | -0.28839 | -0.054931 | 0.26093 | 122.7081 | -0.48065 | -0.3067 | 0.004578 | 0.54932 | 108.0872 | 105.3635 | 122.2137 | 122.6395 | 0.26093 | 122.699 | 110.0464 | -0.3067 | 122.6395 | 0.26093 | 110.0464 | 122.2137 | 122.699 | -122.9828 | -123.0011
1846.9062 | 122.8592 | -117.0181 | 5.7678 | 0.1796 | 0.00323 | 0.0055906 | 0.02334 | -0.0024076 | -0.0017881 | 0.0046933 | -116.7892 | 5.7083 | -117.2882 | 5.5984 | 5.2368 | -6.6055 | -8.606 | -12.0941 | 5.7632 | -117.3294 | -0.27008 | -0.059509 | 0.22888 | 122.6166 | -0.53101 | -0.31128 | -0.004577 | 0.49896 | 108.4122 | 104.924 | 122.2549 | 122.7264 | 0.22888 | 122.7814 | 110.4126 | -0.31128 | 122.7264 | 0.22888 | 110.4126 | 122.2549 | 122.7814 | -123.056 | -123.0972
1847.9688 | 122.8317 | -116.8945 | 5.7861 | 0.14908 | 0.0042982 | 0.0070858 | 0.021204 | -0.0030484 | -0.0013609 | 0.0049069 | -116.7572 | 5.7129 | -117.2928 | 5.6717 | 5.3284 | -6.546 | -8.7616 | -12.0392 | 5.8548 | -117.2836 | -0.39826 | -0.073242 | 0.13733 | 122.5662 | -0.45776 | -0.3891 | 0.068664 | 0.53558 | 108.1329 | 104.8553 | 122.2229 | 122.6074 | 0.13733 | 122.7493 | 110.3485 | -0.3891 | 122.6074 | 0.13733 | 110.3485 | 122.2229 | 122.7493 | -123.0789 | -123.0698
1848.9062 | 122.8729 | -117.0273 | 5.7175 | 0.20248 | 0.00323 | 0.0028134 | 0.019922 | -0.0036892 | -0.0013609 | 0.0049069 | -116.8121 | 5.69 | -117.2974 | 5.6076 | 5.2414 | -6.4911 | -8.876 | -11.7554 | 5.7404 | -117.3477 | -0.27008 | -0.027466 | 0.21515 | 122.6349 | -0.47607 | -0.32043 | 0.022888 | 0.48523 | 108.1512 | 105.2719 | 122.2687 | 122.7173 | 0.21515 | 122.7676 | 110.5362 | -0.32043 | 122.7173 | 0.21515 | 110.5362 | 122.2687 | 122.7676 | -123.0148 | -123.0652
1849.9531 | 122.9507 | -116.8991 | 5.809 | 0.14908 | 0.0045118 | 0.0096494 | 0.019495 | -0.00027139 | -0.0024289 | 0.0038389 | -116.6336 | 5.7907 | -117.1646 | 5.7541 | 5.3467 | -6.3766 | -8.4778 | -11.5402 | 5.8182 | -117.2195 | -0.2655 | -0.018311 | 0.2655 | 122.6532 | -0.46234 | -0.32043 | 0.009155 | 0.53101 | 108.4213 | 105.3589 | 122.2458 | 122.6898 | 0.2655 | 122.7173 | 110.5225 | -0.32043 | 122.6898 | 0.2655 | 110.5225 | 122.2458 | 122.7173 | -122.9736 | -123.0286
1850.9062 | 122.905 | -116.9037 | 5.8273 | 0.19485 | 0.0019482 | 0.0025998 | 0.013727 | -0.0036892 | -0.00071986 | 0.0068295 | -116.7252 | 5.7587 | -117.2058 | 5.7266 | 5.3604 | -6.5506 | -8.4137 | -11.5173 | 5.8365 | -117.1967 | -0.30212 | -0.068665 | 0.17853 | 122.6303 | -0.46692 | -0.29297 | 0.009155 | 0.48065 | 108.49 | 105.3864 | 122.2641 | 122.6624 | 0.17853 | 122.7402 | 110.3531 | -0.29297 | 122.6624 | 0.17853 | 110.3531 | 122.2641 | 122.7402 | -123.0331 | -123.024
1851.9531 | 122.8409 | -117.247 | 5.4428 | 0.019379 | 0.0030164 | 0.0034544 | 0.024836 | -0.0058256 | -0.0030697 | 0.0034115 | -117.0639 | 5.3925 | -117.5903 | 5.3238 | 4.9347 | -6.8115 | -8.3084 | -11.5723 | 5.484 | -117.6544 | -0.34332 | -0.050354 | 0.18311 | 122.5708 | -0.50812 | -0.40741 | 0.041199 | 0.52643 | 108.9386 | 105.6747 | 122.1817 | 122.6395 | 0.18311 | 122.731 | 110.4355 | -0.40741 | 122.6395 | 0.18311 | 110.4355 | 122.1817 | 122.731 | -123.0331 | -123.0972
1852.9219 | 122.9874 | -117.0273 | 5.658 | -0.14084 | 0.0010938 | 0.003027 | 0.013727 | -0.003903 | -0.0015745 | 0.0027707 | -116.7755 | 5.7999 | -117.2562 | 5.658 | 5.2917 | -7.3654 | -8.5648 | -11.412 | 5.6717 | -117.3386 | -0.22888 | 0.14191 | 0.25177 | 122.6852 | -0.36621 | -0.31128 | 0.013733 | 0.48065 | 108.4625 | 105.6152 | 122.319 | 122.8271 | 0.25177 | 122.699 | 109.6619 | -0.31128 | 122.8271 | 0.25177 | 109.6619 | 122.319 | 122.699 | -122.9141 | -122.9965
1853.9688 | 122.8317 | -111.5387 | 11.0458 | -0.026398 | 0.0064344 | 0.006445 | 0.022699 | -0.0036892 | -0.0028561 | 0.0040525 | -111.4243 | 11.055 | -111.9186 | 11.0184 | 10.4919 | -6.1523 | -7.608 | -10.7483 | 11.0825 | -111.9919 | -0.37994 | 0.009156 | 0.11444 | 122.5571 | -0.55389 | -0.45319 | 0.036621 | 0.49438 | 103.9307 | 100.7904 | 122.0306 | 122.5937 | 0.11444 | 122.6212 | 105.3864 | -0.45319 | 122.5937 | 0.11444 | 105.3864 | 122.0306 | 122.6212 | -122.9645 | -123.0377
1854.9062 | 122.8134 | -115.9882 | 6.6376 | 0.48477 | 0.0030164 | 0.00067718 | 0.021631 | -0.0013394 | -0.00071986 | 0.0055479 | -115.8508 | 6.6971 | -116.3727 | 6.5094 | 6.102 | -7.3196 | -8.6288 | -11.9888 | 6.6925 | -116.4276 | -0.38452 | 0.05951 | 0.13733 | 122.4976 | -0.53558 | -0.43945 | 0.054932 | 0.52185 | 107.3593 | 103.9993 | 122.0901 | 122.6852 | 0.13733 | 122.6807 | 108.6685 | -0.43945 | 122.6852 | 0.13733 | 108.6685 | 122.0901 | 122.6807 | -123.0103 | -123.0652
1855.9688 | 122.8638 | -116.0614 | 6.6147 | -0.12558 | 0.0034436 | 0.0043088 | 0.021845 | -0.0028348 | -0.0013609 | 0.0027707 | -115.8783 | 6.5414 | -116.478 | 6.5414 | 6.1066 | -7.2372 | -8.4686 | -12.1445 | 6.6513 | -116.423 | -0.41656 | -0.073242 | 0.1831 | 122.6028 | -0.50812 | -0.36163 | 0.036621 | 0.59967 | 107.5928 | 103.9169 | 122.168 | 122.6028 | 0.1831 | 122.7127 | 108.8242 | -0.36163 | 122.6028 | 0.1831 | 108.8242 | 122.168 | 122.7127 | -123.0927 | -123.0377
1856.9062 | 122.8271 | -108.8562 | 13.6826 | 0.12619 | 0.0038708 | 0.0070858 | 0.021204 | -0.0013394 | -0.0015745 | 0.0089657 | -107.7164 | 14.9002 | -108.1879 | 13.6368 | 12.8632 | -6.9031 | -7.7225 | -10.9039 | 13.9343 | -109.2728 | 0.66833 | 1.2177 | 1.1398 | 122.493 | -0.8194 | -0.41657 | 0.25177 | 0.4715 | 101.1337 | 97.9523 | 121.7194 | 123.7564 | 1.1398 | 122.7905 | 101.9531 | -0.41657 | 123.7564 | 1.1398 | 101.9531 | 121.7194 | 122.7905 | -121.8704 | -122.9553
1857.9688 | 122.818 | -112.1246 | 10.524 | 0.1033 | 0.0023756 | 0.0040952 | 0.017573 | -0.0013394 | -0.0030697 | 0.0055479 | -111.5021 | 11.174 | -111.9919 | 10.5698 | 10.0616 | -6.514 | -8.7067 | -11.412 | 10.6567 | -112.4725 | 0.13275 | 0.65002 | 0.62256 | 122.6944 | -0.46234 | -0.3479 | 0.13275 | 0.48981 | 103.418 | 100.7126 | 122.1863 | 123.2986 | 0.62256 | 122.7814 | 105.6107 | -0.3479 | 123.2986 | 0.62256 | 105.6107 | 122.1863 | 122.7814 | -122.5159 | -122.9965
1858.9062 | 122.8271 | -112.088 | 10.4874 | -0.61386 | 0.0040846 | 0.0085812 | 0.018 | 0.00079681 | -0.0017881 | 0.0036253 | -111.9919 | 10.5515 | -112.4496 | 10.4095 | 9.938 | -6.3354 | -8.5007 | -11.3159 | 10.5698 | -112.5504 | -0.36163 | 0.064087 | 0.096131 | 122.4976 | -0.54932 | -0.46234 | 0.082397 | 0.45776 | 103.5873 | 100.7721 | 122.0261 | 122.6395 | 0.096131 | 122.6578 | 105.7526 | -0.46234 | 122.6395 | 0.096131 | 105.7526 | 122.0261 | 122.6578 | -122.937 | -123.0377
1859.9688 | 122.8317 | -113.6627 | 8.9539 | -0.24765 | 0.0040846 | 0.0032406 | 0.013727 | -0.0036892 | -0.00071986 | 0.0027707 | -113.2919 | 9.2468 | -113.7405 | 8.963 | 8.5281 | -8.3267 | -8.7067 | -11.7416 | 9.0958 | -114.1113 | -0.07782 | 0.29297 | 0.37079 | 122.6257 | -0.42572 | -0.44861 | 0.14191 | 0.44861 | 104.9561 | 101.9211 | 122.1909 | 122.9095 | 0.37079 | 122.7585 | 105.336 | -0.44861 | 122.9095 | 0.37079 | 105.336 | 122.1909 | 122.7585 | -122.6944 | -123.0652
1860.9219 | 122.7768 | -112.0377 | 10.5652 | 0.11093 | 0.0028028 | 0.0011044 | 0.010096 | -0.002194 | -0.0020017 | 0.0044797 | -111.7355 | 10.6567 | -112.1704 | 10.5103 | 10.0204 | -7.8873 | -8.5693 | -11.7142 | 10.4874 | -112.7197 | -0.13275 | 0.091552 | 0.30212 | 122.5479 | -0.54474 | -0.68207 | -0.07782 | 0.43488 | 103.4683 | 100.3235 | 122.0581 | 122.6944 | 0.30212 | 122.525 | 104.1504 | -0.68207 | 122.6944 | 0.30212 | 104.1504 | 122.0581 | 122.525 | -122.7356 | -123.2849
1861.9688 | 122.85 | -110.2615 | 12.2406 | -0.095062 | 0.0051526 | 0.0062314 | 0.026117 | -0.0045438 | -0.0020017 | 0.0034115 | -108.4488 | 14.1953 | -109.0027 | 12.9044 | 11.7737 | -9.6542 | -8.0658 | -11.0275 | 12.6663 | -110.4904 | 1.2589 | 1.9547 | 1.8127 | 123.1659 | -0.46692 | -0.22888 | 0.42572 | 0.55389 | 102.1957 | 99.234 | 122.0352 | 124.4568 | 1.8127 | 122.9279 | 100.6073 | -0.22888 | 124.4568 | 1.8127 | 100.6073 | 122.0352 | 122.9279 | -121.2433 | -122.731
1862.9062 | 122.9233 | -119.838 | 2.9572 | 0.14908 | 0.0034436 | 0.009863 | 0.022486 | -0.0019802 | -0.0017881 | 0.0044797 | -119.664 | 2.8839 | -120.1675 | 2.7237 | 2.4261 | -10.8215 | -9.3567 | -13.2935 | 2.98 | -120.1813 | -0.32959 | -0.073242 | 0.17395 | 122.5616 | -0.53101 | -0.34332 | 0.022889 | 0.50354 | 110.4813 | 106.5445 | 122.2641 | 122.7219 | 0.17395 | 122.818 | 109.0164 | -0.34332 | 122.7219 | 0.17395 | 109.0164 | 122.2641 | 122.818 | -123.1247 | -123.1384
1863.9531 | 122.6303 | -119.7784 | 3.0075 | 0.057526 | 0.0036572 | 0.010077 | 0.022486 | -0.0024076 | -0.0022153 | 0.0061887 | -119.5221 | 2.9938 | -120.0897 | 2.8381 | 2.5635 | -9.256 | -9.0866 | -12.6617 | 3.0396 | -120.1263 | -0.31128 | -0.013733 | 0.25635 | 122.6166 | -0.44403 | -0.3479 | 0.032044 | 0.56763 | 110.6918 | 107.1167 | 122.3419 | 122.7722 | 0.25635 | 122.818 | 110.5225 | -0.3479 | 122.7722 | 0.25635 | 110.5225 | 122.3419 | 122.818 | -123.0972 | -123.1339
1864.9062 | 122.8409 | -119.8837 | 2.8839 | 0.24063 | 0.0047254 | 0.010077 | 0.020777 | -0.0019802 | -0.0011471 | 0.0038389 | -119.6594 | 2.8519 | -120.1859 | 2.7283 | 2.4445 | -8.8989 | -9.1782 | -12.5931 | 2.9068 | -120.2179 | -0.30212 | -0.032043 | 0.2243 | 122.612 | -0.43945 | -0.33417 | 0.022888 | 0.52643 | 110.7056 | 107.2906 | 122.3282 | 122.7356 | 0.2243 | 122.7905 | 110.9848 | -0.33417 | 122.7356 | 0.2243 | 110.9848 | 122.3282 | 122.7905 | -123.0698 | -123.1018
1865.9688 | 122.905 | -120.0211 | 2.7603 | 0.1796 | 0.0042982 | 0.0055906 | 0.011805 | -0.002194 | -0.0013609 | 0.0051205 | -119.8105 | 2.6688 | -120.3186 | 2.6093 | 2.3438 | -10.6888 | -9.375 | -12.7808 | 2.7832 | -120.3278 | -0.29755 | -0.091553 | 0.21057 | 122.6303 | -0.41656 | -0.3067 | 0.022888 | 0.50812 | 110.6461 | 107.2403 | 122.3648 | 122.6898 | 0.21057 | 122.8043 | 109.3323 | -0.3067 | 122.6898 | 0.21057 | 109.3323 | 122.3648 | 122.8043 | -123.0789 | -123.0881
1866.9062 | 122.0444 | -119.6915 | 2.6642 | 0.011749 | 0.0045118 | 0.0045224 | 0.022059 | -0.002194 | -0.0022153 | 0.0064023 | -119.9295 | 2.5864 | -120.4514 | 2.4353 | 2.1286 | -10.6567 | -9.3704 | -12.9135 | 2.6917 | -120.5109 | -0.75989 | -0.07782 | -0.23804 | 122.1268 | -0.53558 | -0.8194 | 0.027465 | 0.52185 | 110.321 | 106.778 | 121.8201 | 122.2778 | -0.23804 | 122.3831 | 109.0347 | -0.8194 | 122.2778 | -0.23804 | 109.0347 | 121.8201 | 122.3831 | -123.1155 | -123.175
1867.9531 | 122.7448 | -120.5978 | 2.0691 | 0.13382 | 0.0040846 | 0.006445 | 0.018854 | -0.0043302 | -0.0020017 | 0.0042661 | -120.5429 | 2.0233 | -120.9915 | 1.7853 | 1.561 | -10.437 | -9.4757 | -13.1195 | 2.1149 | -121.0831 | -0.39368 | -0.045777 | 0.054931 | 122.3831 | -0.50812 | -0.48523 | 0.045776 | 0.44861 | 111.1221 | 107.4783 | 122.1588 | 122.6212 | 0.054931 | 122.7127 | 110.1608 | -0.48523 | 122.6212 | 0.054931 | 110.1608 | 122.1588 | 122.7127 | -123.0606 | -123.1522
1868.9062 | 122.4106 | -120.7993 | 1.8448 | 0.13382 | 0.00323 | 0.0045224 | 0.02334 | -0.0034756 | -0.00071986 | 0.0055479 | -120.8084 | 1.7532 | -121.2708 | 1.474 | 1.2222 | -10.1852 | -9.7641 | -13.092 | 1.886 | -121.3348 | -0.4715 | -0.091553 | -0.009156 | 122.2733 | -0.62256 | -0.53558 | 0.041198 | 0.46234 | 111.0352 | 107.7072 | 122.0215 | 122.5525 | -0.009156 | 122.6852 | 110.614 | -0.53558 | 122.5525 | -0.009156 | 110.614 | 122.0215 | 122.6852 | -123.1155 | -123.1796
1869.9688 | 122.8638 | -120.6619 | 1.7807 | -0.041657 | 0.0047254 | 0.010077 | 0.021418 | -0.0013394 | -0.0013609 | 0.0034115 | -120.813 | 1.6434 | -121.3989 | 1.5335 | 1.2772 | -16.4062 | -10.2951 | -12.886 | 1.7624 | -121.3806 | -0.737 | -0.13733 | -0.15106 | 122.1954 | -0.50354 | -0.71869 | -0.018311 | 0.58594 | 110.3668 | 107.7759 | 121.9391 | 122.3053 | -0.15106 | 122.4243 | 104.2557 | -0.71869 | 122.3053 | -0.15106 | 104.2557 | 121.9391 | 122.4243 | -123.1796 | -123.1613
1870.9062 | 122.7219 | -121.1334 | 1.6983 | 0.26352 | 0.0045118 | 0.0021726 | 0.022272 | -0.00069859 | -0.00093346 | 0.0042661 | -120.9045 | 1.6388 | -121.431 | 1.4465 | 1.1902 | -14.2776 | -10.2539 | -12.8448 | 1.7303 | -121.4584 | -0.29755 | -0.059509 | 0.22888 | 122.58 | -0.50812 | -0.32501 | 0.032044 | 0.52643 | 110.8795 | 108.2886 | 122.3236 | 122.7722 | 0.22888 | 122.8638 | 106.8558 | -0.32501 | 122.7722 | 0.22888 | 106.8558 | 122.3236 | 122.8638 | -123.1293 | -123.1567
1871.9531 | 122.5113 | -120.9091 | 1.6846 | -0.11032 | 0.00323 | 0.0070858 | 0.02334 | -0.0028348 | -0.0024289 | 0.0034115 | -120.8908 | 1.593 | -121.4539 | 1.5289 | 1.2405 | -13.266 | -10.1898 | -12.7853 | 1.7487 | -121.463 | -0.54474 | -0.091552 | 0.018311 | 122.4381 | -0.44403 | -0.55389 | 0.064087 | 0.56305 | 110.7193 | 108.1238 | 122.1497 | 122.5021 | 0.018311 | 122.6578 | 107.6431 | -0.55389 | 122.5021 | 0.018311 | 107.6431 | 122.1497 | 122.6578 | -123.1384 | -123.1476
1872.9062 | 122.7676 | -121.1426 | 1.6754 | 0.14145 | 0.00323 | 0.0049496 | 0.020136 | 0.0010104 | 0.0018435 | 0.0027707 | -120.9641 | 1.593 | -121.463 | 1.5472 | 1.3733 | -15.8661 | -10.3271 | -12.8036 | 1.7075 | -121.5042 | -0.32044 | -0.082397 | 0.17853 | 122.6898 | -0.30212 | -0.36163 | 0.032043 | 0.49896 | 110.8154 | 108.3389 | 122.5159 | 122.7356 | 0.17853 | 122.85 | 105.2765 | -0.36163 | 122.7356 | 0.17853 | 105.2765 | 122.5159 | 122.85 | -123.1384 | -123.1796
1873.9688 | 122.9187 | -120.9229 | 1.6983 | -0.1561 | 0.0034436 | 0.008154 | 0.021631 | -0.002194 | -0.00093346 | 0.0034115 | -120.9045 | 1.5701 | -121.4813 | 1.4557 | 1.2085 | -16.5573 | -10.3821 | -12.7808 | 1.68 | -121.4264 | -0.55847 | -0.12817 | 0.018311 | 122.3785 | -0.48981 | -0.50354 | -0.01831 | 0.57678 | 110.5408 | 108.1421 | 122.1313 | 122.493 | 0.018311 | 122.6028 | 104.3655 | -0.50354 | 122.493 | 0.018311 | 104.3655 | 122.1313 | 122.6028 | -123.1796 | -123.1247
1874.9062 | 122.8409 | -121.1472 | 1.6571 | -0.064545 | 0.0040846 | 0.0032406 | 0.017573 | -0.00091219 | 0.00013454 | 0.0046933 | -120.9091 | 1.6022 | -121.4401 | 1.4191 | 1.1856 | -16.3834 | -10.2264 | -13.1287 | 1.7166 | -121.4951 | -0.29297 | -0.054931 | 0.23804 | 122.5662 | -0.4715 | -0.3479 | 0.05951 | 0.53101 | 110.9207 | 108.0185 | 122.3328 | 122.7493 | 0.23804 | 122.8638 | 104.7638 | -0.3479 | 122.7493 | 0.23804 | 104.7638 | 122.3328 | 122.8638 | -123.0972 | -123.1522
1875.9531 | 122.8271 | -121.2021 | 1.6159 | 0.065155 | 0.0036572 | 0.01029 | 0.019709 | -0.0030484 | -0.0017881 | 0.0049069 | -120.9778 | 1.5518 | -121.4813 | 1.3596 | 1.1124 | -15.2344 | -10.1944 | -13.0417 | 1.6434 | -121.5683 | -0.27924 | -0.064087 | 0.2243 | 122.5616 | -0.50354 | -0.36621 | 0.027466 | 0.50354 | 111.0077 | 108.1604 | 122.3145 | 122.7539 | 0.2243 | 122.8455 | 105.9677 | -0.36621 | 122.7539 | 0.2243 | 105.9677 | 122.3145 | 122.8455 | -123.0972 | -123.1842
1876.9062 | 122.8134 | -121.2204 | 1.6067 | 0.011749 | 0.0055798 | 0.0049496 | 0.022913 | 0.00015601 | -0.0034971 | 0.0040525 | -120.9457 | 1.5472 | -121.4951 | 1.3824 | 1.1215 | -15.7104 | -10.3729 | -13.3347 | 1.6434 | -121.5408 | -0.27466 | -0.059509 | 0.27466 | 122.6028 | -0.48523 | -0.32044 | 0.036622 | 0.54932 | 110.8475 | 107.8857 | 122.3419 | 122.7676 | 0.27466 | 122.8638 | 105.5099 | -0.32044 | 122.7676 | 0.27466 | 105.5099 | 122.3419 | 122.8638 | -123.1018 | -123.1476
1877.9531 | 122.8775 | -121.1334 | 1.6708 | -0.14847 | 0.0075024 | 0.0087948 | 0.020136 | -0.00048499 | -0.0030697 | 0.0034115 | -120.8862 | 1.5884 | -121.4584 | 1.4969 | 1.2314 | -14.9139 | -10.1303 | -13.3667 | 1.7029 | -121.5134 | -0.32501 | -0.082397 | 0.24719 | 122.6303 | -0.43945 | -0.37994 | 0.032044 | 0.5722 | 111.0031 | 107.7667 | 122.3648 | 122.7219 | 0.24719 | 122.8363 | 106.2195 | -0.37994 | 122.7219 | 0.24719 | 106.2195 | 122.3648 | 122.8363 | -123.1293 | -123.1842
1878.9062 | 122.8088 | -116.9907 | 5.7632 | 0.049896 | 0.0045118 | 0.0072996 | 0.018641 | -0.00027139 | 0.00056194 | 0.0038389 | -116.8808 | 5.6625 | -117.3889 | 5.5618 | 5.1819 | -13.0234 | -9.7 | -12.3642 | 5.777 | -117.3889 | -0.39825 | -0.10071 | 0.10986 | 122.5525 | -0.58136 | -0.39825 | 0.013733 | 0.50812 | 107.2906 | 104.6265 | 122.1725 | 122.6532 | 0.10986 | 122.7676 | 103.9673 | -0.39825 | 122.6532 | 0.10986 | 103.9673 | 122.1725 | 122.7676 | -123.1522 | -123.1522
1879.9531 | 122.8729 | -116.6153 | 6.1615 | -0.18662 | 0.0045118 | 0.0055906 | 0.02035 | -0.0013394 | -0.0013609 | 0.0059751 | -116.2399 | 6.34 | -116.7389 | 6.0059 | 5.658 | -12.529 | -9.6176 | -12.0941 | 6.2119 | -116.954 | -0.1236 | 0.17853 | 0.37537 | 122.6212 | -0.50354 | -0.33875 | 0.050354 | 0.49896 | 106.9977 | 104.5212 | 122.2733 | 122.9553 | 0.37537 | 122.8271 | 104.0863 | -0.33875 | 122.9553 | 0.37537 | 104.0863 | 122.2733 | 122.8271 | -122.9004 | -123.1155
1880.9062 | 122.9828 | -119.3527 | 3.3691 | 0.18723 | 0.001521 | 0.003027 | 0.018427 | -0.00091219 | -0.0028561 | 0.0053343 | -119.0323 | 3.3096 | -119.632 | 3.3325 | 3.0533 | -13.3942 | -10.2219 | -12.7716 | 3.447 | -119.6777 | -0.27924 | -0.05951 | 0.32043 | 122.6852 | -0.31586 | -0.32501 | 0.077819 | 0.59967 | 109.1309 | 106.5811 | 122.406 | 122.6624 | 0.32043 | 122.7997 | 105.9586 | -0.32501 | 122.6624 | 0.32043 | 105.9586 | 122.406 | 122.7997 | -123.0011 | -123.0469
1881.9531 | 122.9095 | -119.4946 | 3.3142 | -0.18662 | 0.0047254 | 0.0058042 | 0.021845 | -0.0036892 | -0.0015745 | 0.0057615 | -119.2291 | 3.2776 | -119.7556 | 3.1723 | 2.8885 | -14.2044 | -9.9792 | -12.7029 | 3.3691 | -119.8288 | -0.26093 | -0.036621 | 0.2655 | 122.6669 | -0.42572 | -0.33417 | 0.054932 | 0.52643 | 109.5154 | 106.7917 | 122.3831 | 122.7722 | 0.2655 | 122.8638 | 105.2902 | -0.33417 | 122.7722 | 0.2655 | 105.2902 | 122.3831 | 122.8638 | -123.0698 | -123.143
1882.9062 | 122.8592 | -119.4122 | 3.392 | -0.026398 | 0.0036572 | 0.0060178 | 0.021418 | 0.0016512 | -0.0011471 | 0.0042661 | -119.133 | 3.3188 | -119.7098 | 3.2043 | 2.9068 | -14.621 | -9.7916 | -12.4191 | 3.4103 | -119.7418 | -0.29755 | -0.073242 | 0.27923 | 122.6166 | -0.48523 | -0.32959 | 0.01831 | 0.57678 | 109.6207 | 106.9931 | 122.319 | 122.731 | 0.27923 | 122.8226 | 104.7913 | -0.32959 | 122.731 | 0.27923 | 104.7913 | 122.319 | 122.8226 | -123.1018 | -123.1338
1883.9531 | 122.8546 | -119.4443 | 3.3051 | -0.026398 | 0.0036572 | 0.0070858 | 0.021631 | 0.00036961 | -0.0015745 | 0.0036253 | -119.1925 | 3.2593 | -119.7784 | 3.1357 | 2.8427 | -14.4287 | -9.8923 | -12.1811 | 3.3417 | -119.8334 | -0.33417 | -0.045777 | 0.25177 | 122.58 | -0.46234 | -0.3891 | 0.036621 | 0.58594 | 109.552 | 107.2632 | 122.287 | 122.7036 | 0.25177 | 122.7859 | 105.0156 | -0.3891 | 122.7036 | 0.25177 | 105.0156 | 122.287 | 122.7859 | -123.0835 | -123.1384
1884.9062 | 122.8317 | -119.3802 | 3.4378 | -0.011139 | 0.0051526 | 0.004736 | 0.023127 | -0.0011258 | -0.0026425 | 0.0044797 | -119.1101 | 3.3783 | -119.6274 | 3.2272 | 2.9205 | -14.1266 | -9.8785 | -12.2635 | 3.4653 | -119.6915 | -0.24719 | -0.059509 | 0.27008 | 122.6074 | -0.51727 | -0.31128 | 0.027466 | 0.51727 | 109.5016 | 107.1167 | 122.3007 | 122.7585 | 0.27008 | 122.8455 | 105.2536 | -0.31128 | 122.7585 | 0.27008 | 105.2536 | 122.3007 | 122.8455 | -123.0652 | -123.1293
1885.9688 | 122.8912 | -119.632 | 3.1631 | -0.17136 | 0.00323 | 0.004736 | 0.019282 | 0.0014376 | -0.00029266 | 0.0038389 | -119.3893 | 3.0899 | -119.9753 | 2.9938 | 2.71 | -14.1037 | -9.6588 | -12.5427 | 3.1769 | -119.9661 | -0.34332 | -0.073242 | 0.24262 | 122.6257 | -0.45319 | -0.33417 | 0.013733 | 0.58594 | 109.9731 | 107.0892 | 122.3419 | 122.7219 | 0.24262 | 122.8088 | 105.5283 | -0.33417 | 122.7219 | 0.24262 | 105.5283 | 122.3419 | 122.8088 | -123.1384 | -123.1293
1886.9062 | 122.8638 | -119.1238 | 3.6026 | -0.12558 | 0.0036572 | 0.0090086 | 0.020777 | -0.00091219 | -0.0015745 | 0.0040525 | -118.9682 | 3.5202 | -119.5358 | 3.4103 | 3.1128 | -14.8819 | -9.6222 | -12.5336 | 3.6072 | -119.5587 | -0.41199 | -0.082397 | 0.15564 | 122.5342 | -0.48981 | -0.43488 | 0.004578 | 0.56763 | 109.5016 | 106.5903 | 122.2366 | 122.644 | 0.15564 | 122.731 | 104.2419 | -0.43488 | 122.644 | 0.15564 | 104.2419 | 122.2366 | 122.731 | -123.1384 | -123.1613
1887.9688 | 122.8409 | -119.4534 | 3.3417 | -0.34683 | 0.0019482 | 0.0028134 | 0.017359 | 0.001224 | -0.0015745 | 0.0038389 | -119.3115 | 3.3234 | -119.7876 | 3.1494 | 2.861 | -13.9114 | -9.4482 | -12.4741 | 3.4012 | -119.8151 | -0.33417 | -0.018311 | 0.14191 | 122.6028 | -0.48065 | -0.36163 | 0.059509 | 0.47608 | 110.0052 | 106.9794 | 122.3145 | 122.7768 | 0.14191 | 122.8546 | 105.542 | -0.36163 | 122.7768 | 0.14191 | 105.542 | 122.3145 | 122.8546 | -123.1293 | -123.1567
1888.9062 | 122.8912 | -119.3756 | 3.4241 | -0.11032 | 0.0038708 | 0.0085812 | 0.022059 | -0.00048499 | -0.0032835 | 0.0042661 | -119.1422 | 3.3417 | -119.7144 | 3.2593 | 2.9114 | -13.797 | -9.4986 | -12.4512 | 3.4836 | -119.7235 | -0.33875 | -0.082397 | 0.23346 | 122.6349 | -0.51269 | -0.3479 | 0.05951 | 0.5722 | 109.877 | 106.9244 | 122.287 | 122.7173 | 0.23346 | 122.8592 | 105.5786 | -0.3479 | 122.7173 | 0.23346 | 105.5786 | 122.287 | 122.8592 | -123.1384 | -123.1476
1889.9062 | 122.818 | -118.9636 | 3.7582 | -0.20187 | 0.0051526 | 0.0055906 | 0.019922 | -0.00069859 | -0.0024289 | 0.0053343 | -118.8126 | 3.6438 | -119.371 | 3.5477 | 3.2547 | -13.1241 | -9.3063 | -12.323 | 3.7445 | -119.3665 | -0.40741 | -0.11444 | 0.15106 | 122.5113 | -0.50354 | -0.40283 | -0.013733 | 0.55847 | 109.6573 | 106.6406 | 122.2183 | 122.6074 | 0.15106 | 122.7081 | 105.8395 | -0.40283 | 122.6074 | 0.15106 | 105.8395 | 122.2183 | 122.7081 | -123.1293 | -123.1247
1890.9531 | 122.8226 | -119.2566 | 3.5568 | -0.22476 | 0.0038708 | 0.0058042 | 0.015436 | -0.002194 | -0.00071986 | 0.0051205 | -118.927 | 3.5431 | -119.5267 | 3.3325 | 3.0716 | -6.9305 | -9.3155 | -12.1033 | 3.6072 | -119.5908 | -0.27008 | -0.013733 | 0.32959 | 122.5891 | -0.48523 | -0.33417 | 0.050354 | 0.59967 | 109.9411 | 107.1533 | 122.3282 | 122.7997 | 0.32959 | 122.8638 | 112.326 | -0.33417 | 122.7997 | 0.32959 | 112.326 | 122.3282 | 122.8638 | -123.0835 | -123.1476
1891.9062 | 122.8958 | -119.2703 | 3.5477 | -0.10269 | 0.0038708 | 0.0066586 | 0.017573 | -0.0011258 | -0.00071986 | 0.0017027 | -119.0002 | 3.4607 | -119.5084 | 3.3691 | 3.0945 | -6.7612 | -9.3063 | -12.0712 | 3.6026 | -119.5908 | -0.23804 | -0.086975 | 0.27008 | 122.6395 | -0.45319 | -0.32043 | 0.054932 | 0.50812 | 109.964 | 107.1991 | 122.3648 | 122.731 | 0.27008 | 122.8729 | 112.5092 | -0.32043 | 122.731 | 0.27008 | 112.5092 | 122.3648 | 122.8729 | -123.056 | -123.1384
1892.9688 | 122.8821 | -119.1971 | 3.5889 | -0.14847 | 0.0042982 | 0.0072996 | 0.016932 | -0.00091219 | -0.0030697 | 0.0046933 | -119.0277 | 3.5248 | -119.5175 | 3.4378 | 3.1403 | -6.5369 | -9.3384 | -12.0804 | 3.6438 | -119.5358 | -0.32043 | -0.064087 | 0.16937 | 122.6349 | -0.44861 | -0.33874 | 0.054932 | 0.48981 | 109.8587 | 107.1167 | 122.3373 | 122.7219 | 0.16937 | 122.8409 | 112.6602 | -0.33874 | 122.7219 | 0.16937 | 112.6602 | 122.3373 | 122.8409 | -123.1064 | -123.1247
1893.9062 | 122.8683 | -119.3115 | 3.4973 | -0.20187 | 0.0017346 | 0.0072996 | 0.018427 | -0.0017666 | 0.00034814 | 0.0051205 | -119.1101 | 3.4332 | -119.6548 | 3.2959 | 3.0121 | -6.5231 | -9.1278 | -12.1628 | 3.5431 | -119.6777 | -0.34332 | -0.064086 | 0.20142 | 122.6074 | -0.48523 | -0.36621 | 0.045777 | 0.54474 | 110.1837 | 107.1487 | 122.3236 | 122.7448 | 0.20142 | 122.8546 | 112.7884 | -0.36621 | 122.7448 | 0.20142 | 112.7884 | 122.3236 | 122.8546 | -123.1522 | -123.175
1894.9688 | 122.8546 | -119.6686 | 3.154 | -0.20187 | 0.0034436 | 0.0062314 | 0.015436 | -0.0028348 | 0.00056194 | 0.0017027 | -119.458 | 3.067 | -119.9615 | 2.9343 | 2.6459 | -6.4545 | -9.1873 | -12.149 | 3.1723 | -120.0165 | -0.29297 | -0.086975 | 0.21057 | 122.6028 | -0.50812 | -0.3479 | 0.01831 | 0.50354 | 110.4813 | 107.5195 | 122.3145 | 122.7356 | 0.21057 | 122.8409 | 113.2141 | -0.3479 | 122.7356 | 0.21057 | 113.2141 | 122.3145 | 122.8409 | -123.1155 | -123.1705
1895.9219 | 122.8546 | -119.8013 | 2.9984 | 0.17197 | 0.0042982 | 0.006445 | 0.019282 | 0.0010104 | -0.00029266 | 0.0049069 | -119.5816 | 2.9205 | -120.1355 | 2.7786 | 2.4994 | -6.601 | -8.9493 | -12.3367 | 3.0304 | -120.1538 | -0.33417 | -0.07782 | 0.21973 | 122.58 | -0.49896 | -0.35248 | 0.032044 | 0.55389 | 110.8521 | 107.4646 | 122.3007 | 122.7219 | 0.21973 | 122.8317 | 113.2004 | -0.35248 | 122.7219 | 0.21973 | 113.2004 | 122.3007 | 122.8317 | -123.1338 | -123.1522
1896.9688 | 122.8409 | -119.7418 | 3.0899 | -0.2858 | 0.00088016 | 0.0015316 | 0.015436 | -0.0034756 | -0.00050626 | 0.0044797 | -119.5496 | 2.9984 | -120.0302 | 2.8519 | 2.5772 | -6.6101 | -9.0591 | -12.2772 | 3.1036 | -120.0714 | -0.28839 | -0.091553 | 0.19226 | 122.5937 | -0.5127 | -0.32959 | 0.013733 | 0.48065 | 110.6827 | 107.4646 | 122.319 | 122.7402 | 0.19226 | 122.8455 | 113.1317 | -0.32959 | 122.7402 | 0.19226 | 113.1317 | 122.319 | 122.8455 | -123.1201 | -123.1613
1897.9062 | 122.8592 | -119.8975 | 2.9114 | -0.14084 | 0.0042982 | 0.0040952 | 0.021418 | -0.0024076 | 0.00077554 | 0.0027707 | -119.6823 | 2.8381 | -120.2133 | 2.7191 | 2.4307 | -6.6467 | -9.1461 | -12.4374 | 2.9572 | -120.2316 | -0.31586 | -0.073242 | 0.21515 | 122.6166 | -0.48065 | -0.33417 | 0.045776 | 0.53101 | 110.7513 | 107.46 | 122.3282 | 122.7356 | 0.21515 | 122.8546 | 113.2507 | -0.33417 | 122.7356 | 0.21515 | 113.2507 | 122.3282 | 122.8546 | -123.1247 | -123.143
1898.9688 | 122.9416 | -119.7327 | 3.0441 | -0.19424 | 2.5564e-05 | 0.0066586 | 0.012232 | -0.004971 | -7.9062e-05 | 0.0036253 | -119.4717 | 2.9663 | -120.0256 | 2.9343 | 2.6596 | -6.6101 | -9.613 | -12.0666 | 3.0716 | -120.0577 | -0.29297 | -0.077819 | 0.26093 | 122.6669 | -0.38452 | -0.32501 | 0.027466 | 0.55389 | 110.1196 | 107.666 | 122.3923 | 122.699 | 0.26093 | 122.8043 | 113.1226 | -0.32501 | 122.699 | 0.26093 | 113.1226 | 122.3923 | 122.8043 | -123.0698 | -123.1018
1899.9062 | 122.8867 | -119.7189 | 3.0808 | -0.16373 | 0.0034436 | 0.004736 | 0.022059 | -0.0047574 | -0.0015745 | 0.0023435 | -119.4946 | 3.0167 | -120.0623 | 2.916 | 2.6093 | -6.7657 | -9.1095 | -11.9705 | 3.1128 | -120.0531 | -0.34332 | -0.064087 | 0.2243 | 122.6349 | -0.4715 | -0.33417 | 0.032043 | 0.56763 | 110.6094 | 107.7484 | 122.3282 | 122.7356 | 0.2243 | 122.8317 | 112.9532 | -0.33417 | 122.7356 | 0.2243 | 112.9532 | 122.3282 | 122.8317 | -123.143 | -123.1339
1900.9688 | 122.8638 | -119.902 | 2.8793 | 0.17197 | 0.0028028 | 0.0083676 | 0.021204 | -5.7592e-05 | -0.0024289 | 0.0027707 | -119.6823 | 2.8152 | -120.2179 | 2.6733 | 2.3895 | -6.72 | -9.2697 | -11.9614 | 2.9251 | -120.2728 | -0.31586 | -0.064086 | 0.21973 | 122.5754 | -0.48981 | -0.37079 | 0.045777 | 0.53558 | 110.6323 | 107.9407 | 122.2916 | 122.7173 | 0.21973 | 122.8271 | 113.1821 | -0.37079 | 122.7173 | 0.21973 | 113.1821 | 122.2916 | 122.8271 | -123.0972 | -123.1522
1901.9062 | 122.85 | -120.1996 | 2.6184 | -0.22476 | 0.0023756 | 0.0023862 | 0.017786 | -0.0026212 | -0.0011471 | 0.0038389 | -119.7968 | 2.5681 | -120.4697 | 2.3758 | 2.1561 | -6.6742 | -9.4437 | -12.0666 | 2.6733 | -120.5429 | -0.27008 | -0.050354 | 0.40283 | 122.5754 | -0.46234 | -0.34332 | 0.054932 | 0.67291 | 110.7559 | 108.1329 | 122.3557 | 122.7676 | 0.40283 | 122.8729 | 113.5254 | -0.34332 | 122.7676 | 0.40283 | 113.5254 | 122.3557 | 122.8729 | -123.0881 | -123.1613
1902.9688 | 122.9691 | -119.9936 | 2.7649 | -0.087433 | 0.00066656 | 0.0085812 | 0.013086 | -0.0043302 | -7.9062e-05 | 0.0019163 | -119.7647 | 2.6642 | -120.2866 | 2.6779 | 2.4078 | -6.514 | -9.613 | -11.8515 | 2.7695 | -120.3094 | -0.29297 | -0.10071 | 0.22888 | 122.6715 | -0.35706 | -0.31586 | 0.004577 | 0.52185 | 110.3806 | 108.1421 | 122.4014 | 122.6578 | 0.22888 | 122.7631 | 113.4796 | -0.31586 | 122.6578 | 0.22888 | 113.4796 | 122.4014 | 122.7631 | -123.0515 | -123.0743
1903.9062 | 122.8271 | -120.0439 | 2.7786 | -0.13321 | 0.0030164 | 0.003668 | 0.018213 | -0.0034756 | -0.00050626 | 0.0027707 | -119.8288 | 2.7008 | -120.3644 | 2.5589 | 2.2797 | -6.7383 | -9.5123 | -12.0804 | 2.8152 | -120.3964 | -0.32044 | -0.077819 | 0.21515 | 122.6028 | -0.49896 | -0.35248 | 0.036622 | 0.53558 | 110.5316 | 107.9636 | 122.3236 | 122.7448 | 0.21515 | 122.8592 | 113.3057 | -0.35248 | 122.7448 | 0.21515 | 113.3057 | 122.3236 | 122.8592 | -123.143 | -123.175
1904.9531 | 122.9462 | -120.1035 | 2.6642 | -3.1773 | -0.0014696 | 0.0094358 | 0.014155 | -0.0028348 | -0.0011471 | 0.0044797 | -119.9432 | 2.5635 | -120.401 | 2.6138 | 2.3392 | -6.633 | -9.288 | -12.0712 | 2.6688 | -120.4285 | -0.29755 | -0.10071 | 0.16022 | 122.7173 | -0.32501 | -0.32501 | 0.004577 | 0.45776 | 110.8154 | 108.0322 | 122.4426 | 122.6669 | 0.16022 | 122.7722 | 113.4705 | -0.32501 | 122.6669 | 0.16022 | 113.4705 | 122.4426 | 122.7722 | -123.0652 | -123.0927
1905.9062 | 122.8088 | -120.0531 | 2.774 | 0.027008 | 0.00323 | 0.0068722 | 0.02334 | -0.0028348 | -0.00029266 | 0.0038389 | -119.8334 | 2.71 | -120.3735 | 2.5406 | 2.243 | -6.8344 | -9.0775 | -12.4832 | 2.8015 | -120.4056 | -0.32043 | -0.064087 | 0.21973 | 122.5937 | -0.53101 | -0.35248 | 0.027466 | 0.54016 | 110.9756 | 107.5699 | 122.2961 | 122.7631 | 0.21973 | 122.8546 | 113.2187 | -0.35248 | 122.7631 | 0.21973 | 113.2187 | 122.2961 | 122.8546 | -123.1476 | -123.1796
1906.9531 | 122.8546 | -119.7739 | 3.0762 | -0.27054 | 0.00323 | 0.003668 | 0.016077 | -0.0043302 | -0.00071986 | 0.0040525 | -119.5724 | 2.9755 | -120.0851 | 2.861 | 2.7969 | -6.3858 | -9.5123 | -12.5519 | 3.1219 | -120.0989 | -0.31128 | -0.10071 | 0.20142 | 122.6349 | -0.27924 | -0.32501 | 0.045776 | 0.51269 | 110.2615 | 107.222 | 122.5708 | 122.7493 | 0.20142 | 122.8958 | 113.3881 | -0.32501 | 122.7493 | 0.20142 | 113.3881 | 122.5708 | 122.8958 | -123.1613 | -123.175
1907.9062 | 122.8546 | -119.8196 | 2.9846 | -0.11032 | 0.0040846 | 0.0045224 | 0.019495 | -0.003903 | -0.00071986 | 0.0027707 | -119.6274 | 2.9114 | -120.1584 | 2.7832 | 2.5177 | -6.5186 | -9.6634 | -12.6251 | 3.035 | -120.1767 | -0.33874 | -0.073242 | 0.19226 | 122.6028 | -0.46692 | -0.35706 | 0.050354 | 0.53101 | 110.1562 | 107.1945 | 122.3373 | 122.731 | 0.19226 | 122.8546 | 113.3011 | -0.35706 | 122.731 | 0.19226 | 113.3011 | 122.3373 | 122.8546 | -123.143 | -123.1613
1908.9531 | 122.8455 | -119.8105 | 3.035 | -0.26291 | 0.0013074 | 3.6382e-05 | 0.017786 | -0.003262 | -0.0011471 | 0.0053343 | -119.5908 | 2.9205 | -120.1218 | 2.8152 | 2.5177 | -6.4087 | -9.8419 | -12.0941 | 3.0441 | -120.1035 | -0.31128 | -0.11444 | 0.21973 | 122.6257 | -0.51727 | -0.29297 | 0.009155 | 0.53101 | 109.9686 | 107.7164 | 122.3282 | 122.731 | 0.21973 | 122.8546 | 113.4018 | -0.29297 | 122.731 | 0.21973 | 113.4018 | 122.3282 | 122.8546 | -123.1567 | -123.1384
1909.9062 | 121.0007 | -68.7012 | 53.714 | -0.19424 | 0.0017346 | 0.0034544 | 0.0056097 | -0.003262 | -0.00071986 | 0.0029843 | -67.4973 | 55.3848 | -67.8818 | 55.2155 | 53.27 | 1.1856 | -2.2568 | -3.0533 | 54.071 | -69.0582 | 0.8194 | 1.6708 | 1.2039 | 123.9166 | -0.44403 | -0.35706 | 0.35706 | 0.38452 | 66.4444 | 65.6479 | 121.9711 | 124.086 | 1.2039 | 122.7722 | 69.8868 | -0.35706 | 124.086 | 1.2039 | 69.8868 | 121.9711 | 122.7722 | -121.5958 | -122.7722
1910.9531 | 122.8821 | -119.1742 | 3.566 | -0.24002 | 0.0010938 | 0.004736 | 0.016932 | -0.003903 | 0.00013454 | 0.0031979 | -118.9865 | 3.4653 | -119.5312 | 3.4195 | 3.1494 | -6.1249 | -9.4528 | -11.5402 | 3.598 | -119.5312 | -0.35706 | -0.10071 | 0.18768 | 122.5937 | -0.41656 | -0.35706 | 0.032043 | 0.54474 | 109.7214 | 107.634 | 122.3236 | 122.6395 | 0.18768 | 122.7722 | 113.0493 | -0.35706 | 122.6395 | 0.18768 | 113.0493 | 122.3236 | 122.7722 | -123.0972 | -123.0972
1911.9062 | 122.8363 | -119.8471 | 2.9709 | -0.20187 | 0.0019482 | 0.0055906 | 0.018854 | -0.00668 | -0.0030697 | 0.0036253 | -119.632 | 2.9022 | -120.163 | 2.7557 | 2.4994 | -6.3171 | -8.9951 | -11.7142 | 2.9984 | -120.1584 | -0.31586 | -0.068664 | 0.21515 | 122.6028 | -0.4715 | -0.31128 | 0.027466 | 0.53101 | 110.8521 | 108.1329 | 122.3465 | 122.7493 | 0.21515 | 122.8455 | 113.53 | -0.31128 | 122.7493 | 0.21515 | 113.53 | 122.3465 | 122.8455 | -123.1338 | -123.1293
1912.9531 | 123.0194 | -119.9753 | 2.7557 | -0.14847 | 0.00045296 | 0.0034544 | 0.013514 | -0.0051846 | -0.0015745 | 0.0038389 | -119.7189 | 2.7008 | -120.2591 | 2.7191 | 2.4673 | -6.1615 | -9.0408 | -11.9385 | 2.8015 | -120.2957 | -0.28381 | -0.054931 | 0.25635 | 122.6944 | -0.28839 | -0.32043 | 0.045777 | 0.54016 | 110.9344 | 108.0368 | 122.4426 | 122.6761 | 0.25635 | 122.7768 | 113.8138 | -0.32043 | 122.6761 | 0.25635 | 113.8138 | 122.4426 | 122.7768 | -123.0148 | -123.0515
1913.9062 | 122.7722 | -120.3186 | 2.504 | -0.22476 | 0.0010938 | 0.0058042 | 0.018854 | -0.0062528 | -0.00029266 | 0.0046933 | -120.1675 | 2.4033 | -120.6482 | 2.2568 | 2.0142 | -6.2302 | -9.4482 | -11.4761 | 2.5131 | -120.6299 | -0.32959 | -0.10071 | 0.15106 | 122.5754 | -0.48981 | -0.31128 | 0.009156 | 0.48065 | 110.8704 | 108.8425 | 122.3328 | 122.7219 | 0.15106 | 122.8317 | 114.0884 | -0.31128 | 122.7219 | 0.15106 | 114.0884 | 122.3328 | 122.8317 | -123.1522 | -123.1339
1914.9531 | 122.9828 | -120.314 | 2.417 | -0.072174 | 0.00088016 | 0.00046358 | 0.0133 | -0.0060392 | -0.0011471 | 0.0034115 | -120.0668 | 2.3438 | -120.6299 | 2.3621 | 2.1332 | -5.8136 | -9.8282 | -11.142 | 2.4399 | -120.6299 | -0.31586 | -0.073242 | 0.24719 | 122.6761 | -0.28381 | -0.31586 | 0.022888 | 0.56305 | 110.4858 | 109.1721 | 122.4472 | 122.6578 | 0.24719 | 122.7539 | 114.5004 | -0.31586 | 122.6578 | 0.24719 | 114.5004 | 122.4472 | 122.7539 | -123.0469 | -123.0469
1915.9219 | 122.8409 | -120.4651 | 2.3941 | 0.011749 | 0.0045118 | 0.0055906 | 0.026331 | -0.003903 | -0.0013609 | 0.0046933 | -120.1813 | 2.3117 | -120.7352 | 2.211 | 1.9272 | -5.7404 | -9.9792 | -11.5906 | 2.3941 | -120.7764 | -0.27008 | -0.082397 | 0.28381 | 122.6761 | -0.46692 | -0.31128 | 0 | 0.55389 | 110.4858 | 108.8745 | 122.3923 | 122.7768 | 0.28381 | 122.8592 | 114.7247 | -0.31128 | 122.7768 | 0.28381 | 114.7247 | 122.3923 | 122.8592 | -123.1293 | -123.1705
1916.9531 | 122.9965 | -120.4285 | 2.298 | -0.13321 | -0.00040164 | 0.0038816 | 0.014155 | -0.004971 | 0.00034814 | 0.0034115 | -120.1859 | 2.2156 | -120.7581 | 2.2568 | 2.0233 | -5.8365 | -9.9197 | -11.5128 | 2.33 | -120.7169 | -0.32959 | -0.082398 | 0.24262 | 122.6852 | -0.27466 | -0.28839 | 0.032043 | 0.5722 | 110.5087 | 108.9157 | 122.4518 | 122.644 | 0.24262 | 122.7585 | 114.592 | -0.28839 | 122.644 | 0.24262 | 114.592 | 122.4518 | 122.7585 | -123.056 | -123.0148
1917.9062 | 122.8592 | -120.5658 | 2.2659 | -0.16373 | 0.00323 | -0.0020998 | 0.019922 | -0.0058256 | -0.0022153 | 0.0023435 | -120.3735 | 2.1698 | -120.8862 | 2.037 | 1.7944 | -6.1615 | -10.0342 | -11.8927 | 2.2797 | -120.9091 | -0.32043 | -0.09613 | 0.19226 | 122.6028 | -0.4715 | -0.34332 | 0.013733 | 0.51269 | 110.5316 | 108.6731 | 122.3602 | 122.7356 | 0.19226 | 122.8455 | 114.4043 | -0.34332 | 122.7356 | 0.19226 | 114.4043 | 122.3602 | 122.8455 | -123.1522 | -123.175
1918.9531 | 122.9416 | -120.5704 | 2.2018 | 0.034637 | -0.00018804 | -0.0012454 | 0.018 | -0.0058256 | -0.0017881 | 0.0040525 | -120.3827 | 2.1149 | -120.8862 | 2.092 | 1.8311 | -6.1707 | -10.0937 | -11.9156 | 2.2202 | -120.8725 | -0.31586 | -0.086975 | 0.18768 | 122.6624 | -0.37079 | -0.30212 | 0.018311 | 0.50354 | 110.4767 | 108.6548 | 122.4014 | 122.6852 | 0.18768 | 122.7905 | 114.3997 | -0.30212 | 122.6852 | 0.18768 | 114.3997 | 122.4014 | 122.7905 | -123.0881 | -123.0743
1919.9062 | 122.8592 | -120.4926 | 2.3254 | -0.24765 | 0.002162 | 0.0011044 | 0.017573 | -0.0086026 | -0.00050626 | 0.0025571 | -120.2682 | 2.1927 | -120.7718 | 2.1378 | 1.8768 | -6.2897 | -9.4894 | -11.824 | 2.3163 | -120.8176 | -0.27924 | -0.13275 | 0.2243 | 122.6303 | -0.44861 | -0.32501 | -0.009155 | 0.50354 | 111.0031 | 108.6685 | 122.3694 | 122.6852 | 0.2243 | 122.8088 | 114.2029 | -0.32501 | 122.6852 | 0.2243 | 114.2029 | 122.3694 | 122.8088 | -123.0972 | -123.143
1920.9688 | 122.8775 | -120.488 | 2.3209 | -0.14084 | 0.0019482 | 0.0038816 | 0.022486 | -0.0051846 | -0.00093346 | 0.0036253 | -120.2225 | 2.2522 | -120.7855 | 2.1606 | 1.9089 | -6.3034 | -9.7046 | -12.0621 | 2.33 | -120.8176 | -0.29755 | -0.068665 | 0.2655 | 122.6486 | -0.41199 | -0.32959 | 0.009155 | 0.56305 | 110.7834 | 108.4259 | 122.3969 | 122.7402 | 0.2655 | 122.818 | 114.1846 | -0.32959 | 122.7402 | 0.2655 | 114.1846 | 122.3969 | 122.818 | -123.1064 | -123.1384
1921.9062 | 122.9462 | -120.488 | 2.2522 | 1.0951 | 0.0030164 | 0.003027 | 0.01565 | -0.0056118 | -0.0026425 | 0.0023435 | -120.3644 | 2.1194 | -120.813 | 2.1652 | 1.9135 | -6.1478 | -9.6085 | -11.7004 | 2.2476 | -120.8084 | -0.32501 | -0.13275 | 0.1236 | 122.6532 | -0.33874 | -0.32044 | -0.004577 | 0.44861 | 110.8795 | 108.7875 | 122.4014 | 122.6074 | 0.1236 | 122.7356 | 114.3402 | -0.32044 | 122.6074 | 0.1236 | 114.3402 | 122.4014 | 122.7356 | -123.0652 | -123.0606
1922.9062 | 122.9736 | -120.5063 | 2.2202 | -0.18662 | 0.0028028 | 0.004736 | 0.015223 | -0.010525 | -0.0032835 | 0.0029843 | -120.2637 | 2.1378 | -120.8176 | 1.9913 | 1.7258 | -6.1615 | -9.7458 | -11.8973 | 2.2247 | -120.8313 | -0.31128 | -0.082398 | 0.24262 | 122.4976 | -0.49438 | -0.32501 | 0.004577 | 0.55389 | 110.7605 | 108.609 | 122.2321 | 122.644 | 0.24262 | 122.731 | 114.3448 | -0.32501 | 122.644 | 0.24262 | 114.3448 | 122.2321 | 122.731 | -123.0377 | -123.0515
1923.9531 | 122.9507 | -120.3552 | 2.4399 | -0.30869 | -0.00040164 | 0.0015316 | 0.018213 | -0.0062528 | -0.0011471 | 0.0038389 | -120.1126 | 2.3254 | -120.6573 | 2.3392 | 2.0874 | -6.134 | -9.9014 | -11.9797 | 2.4078 | -120.6573 | -0.30212 | -0.11444 | 0.24262 | 122.6944 | -0.35248 | -0.30212 | -0.032043 | 0.54474 | 110.4538 | 108.3756 | 122.4426 | 122.6807 | 0.24262 | 122.7631 | 114.2212 | -0.30212 | 122.6807 | 0.24262 | 114.2212 | 122.4426 | 122.7631 | -123.0972 | -123.0972
1924.9062 | 122.9416 | -120.6573 | 2.0645 | 0.065155 | -0.00061524 | 0.0028134 | 0.018854 | -0.008389 | -0.0026425 | 0.0027707 | -120.4742 | 1.9638 | -121.0052 | 1.9913 | 1.7578 | -6.4407 | -10.0388 | -12.0346 | 2.0737 | -120.9961 | -0.3479 | -0.10071 | 0.18311 | 122.6486 | -0.3067 | -0.33875 | 0.009155 | 0.53101 | 110.6186 | 108.6227 | 122.4152 | 122.6212 | 0.18311 | 122.731 | 114.2166 | -0.33875 | 122.6212 | 0.18311 | 114.2166 | 122.4152 | 122.731 | -123.0698 | -123.0606
1925.9688 | 122.9553 | -120.6848 | 2.092 | 0.095673 | 0.0013074 | 0.0058042 | 0.015009 | -0.0053982 | 0.00013454 | 0.0040525 | -120.4697 | 1.973 | -120.9915 | 1.9592 | 1.7441 | -6.3354 | -9.581 | -12.03 | 2.1103 | -121.0144 | -0.3067 | -0.11902 | 0.21515 | 122.644 | -0.3479 | -0.32959 | 0.018311 | 0.52185 | 111.1038 | 108.6548 | 122.4289 | 122.6578 | 0.21515 | 122.7951 | 114.3494 | -0.32959 | 122.6578 | 0.21515 | 114.3494 | 122.4289 | 122.7951 | -123.0835 | -123.1064
1926.9062 | 122.8546 | -120.7352 | 2.092 | -0.21713 | 0.0028028 | 0.004736 | 0.020563 | -0.0064664 | -0.0020017 | 0.0036253 | -120.5109 | 2.0004 | -121.0464 | 1.8814 | 1.6571 | -6.2393 | -9.7 | -11.8423 | 2.1149 | -121.051 | -0.31128 | -0.091553 | 0.2243 | 122.6166 | -0.43488 | -0.31586 | 0.022888 | 0.53558 | 111.0352 | 108.8928 | 122.3923 | 122.7356 | 0.2243 | 122.85 | 114.4958 | -0.31586 | 122.7356 | 0.2243 | 114.4958 | 122.3923 | 122.85 | -123.1384 | -123.143
1927.9688 | 122.9279 | -120.726 | 2.0187 | 0.13382 | 0.00023916 | 0.0060178 | 0.016077 | -0.0060392 | -0.0011471 | 0.0064023 | -120.5063 | 1.9867 | -121.0098 | 1.8082 | 1.6571 | -6.1478 | -9.7549 | -11.8149 | 2.0325 | -121.0556 | -0.28381 | -0.032044 | 0.21973 | 122.5342 | -0.36163 | -0.32959 | 0.013733 | 0.50354 | 110.9711 | 108.9111 | 122.3831 | 122.7127 | 0.21973 | 122.7585 | 114.5782 | -0.32959 | 122.7127 | 0.21973 | 114.5782 | 122.3831 | 122.7585 | -123.0286 | -123.0743
1928.9062 | 122.9919 | -120.6757 | 2.0645 | -0.1561 | 0.00066656 | 0.0015316 | 0.01565 | -0.0077482 | -0.0030697 | 0.0025571 | -120.433 | 1.9547 | -120.9961 | 2.0233 | 1.7761 | -6.2073 | -9.2011 | -11.9293 | 2.0782 | -120.9824 | -0.32044 | -0.10986 | 0.24262 | 122.699 | -0.28839 | -0.3067 | 0.013733 | 0.56305 | 111.4746 | 108.7463 | 122.4518 | 122.6303 | 0.24262 | 122.7539 | 114.4684 | -0.3067 | 122.6303 | 0.24262 | 114.4684 | 122.4518 | 122.7539 | -123.0606 | -123.0469
1929.9531 | 122.9599 | -120.6757 | 2.0599 | 0.47714 | -0.00040164 | 0.0028134 | 0.015864 | -0.0073208 | -0.0022153 | 0.0031979 | -120.4056 | 1.9638 | -121.0281 | 1.9821 | 1.7715 | -6.1707 | -9.4574 | -11.7645 | 2.0645 | -121.0144 | -0.35248 | -0.096131 | 0.27008 | 122.6578 | -0.28839 | -0.33875 | 0.004577 | 0.62256 | 111.2183 | 108.9111 | 122.4472 | 122.6395 | 0.27008 | 122.7402 | 114.505 | -0.33875 | 122.6395 | 0.27008 | 114.505 | 122.4472 | 122.7402 | -123.0881 | -123.0743
1930.9062 | 122.8317 | -120.7626 | 2.0874 | -0.16373 | 0.001521 | 0.0051632 | 0.021845 | -0.0077482 | -0.00093346 | 0.0029843 | -120.5292 | 1.9867 | -121.0602 | 1.8677 | 1.6388 | -6.3309 | -9.7458 | -11.9934 | 2.0874 | -121.0556 | -0.29755 | -0.10071 | 0.23346 | 122.6303 | -0.44861 | -0.29297 | 0 | 0.53101 | 111.0168 | 108.7692 | 122.4014 | 122.7493 | 0.23346 | 122.85 | 114.4318 | -0.29297 | 122.7493 | 0.23346 | 114.4318 | 122.4014 | 122.85 | -123.1476 | -123.143
1931.9688 | 123.0148 | -120.7718 | 1.9684 | 0.1796 | 0.00323 | 0.0038816 | 0.021845 | -0.0036892 | -0.0022153 | 0.0049069 | -120.4788 | 1.9043 | -121.051 | 1.9455 | 1.6937 | -6.2759 | -10.1395 | -12.3184 | 1.9913 | -121.0419 | -0.27923 | -0.064087 | 0.29297 | 122.7173 | -0.27466 | -0.27008 | 0.022888 | 0.5722 | 110.6323 | 108.4534 | 122.4655 | 122.6761 | 0.29297 | 122.7631 | 114.4958 | -0.27008 | 122.6761 | 0.29297 | 114.4958 | 122.4655 | 122.7631 | -123.0194 | -123.0103
1932.9062 | 122.8638 | -120.7031 | 2.1103 | -0.23239 | 0.00066656 | 0.005377 | 0.016077 | -0.0073208 | -0.00071986 | 0.0038389 | -120.4697 | 1.9913 | -120.9915 | 1.9501 | 1.7166 | -6.3171 | -9.938 | -11.9019 | 2.1057 | -120.9915 | -0.28839 | -0.11902 | 0.23346 | 122.6532 | -0.39368 | -0.28839 | -0.004578 | 0.52185 | 110.7651 | 108.8013 | 122.4197 | 122.6944 | 0.23346 | 122.8088 | 114.386 | -0.28839 | 122.6944 | 0.23346 | 114.386 | 122.4197 | 122.8088 | -123.1018 | -123.1018
1933.9688 | 122.9599 | -119.252 | 3.4515 | -0.041657 | 0.00066656 | 0.003027 | 0.01565 | -0.0062528 | -0.00093346 | 0.0036253 | -119.0964 | 3.3646 | -119.632 | 3.3691 | 3.1036 | -6.0516 | -9.8785 | -11.8652 | 3.4653 | -119.5999 | -0.37994 | -0.086975 | 0.15564 | 122.6212 | -0.3479 | -0.3479 | 0.013733 | 0.53558 | 109.3735 | 107.3868 | 122.3557 | 122.6166 | 0.15564 | 122.7173 | 113.2004 | -0.3479 | 122.6166 | 0.15564 | 113.2004 | 122.3557 | 122.7173 | -123.0835 | -123.0515
1934.9062 | 122.9645 | -119.0872 | 3.653 | -0.86563 | 0.0017346 | 0.0060178 | 0.016718 | -0.0062528 | -0.0037107 | 0.0023435 | -119.0369 | 3.5156 | -119.4305 | 3.598 | 3.3051 | -6.0104 | -9.5581 | -11.673 | 3.6438 | -119.3939 | -0.34332 | -0.13733 | 0.050354 | 122.6852 | -0.3479 | -0.3067 | -0.009155 | 0.39368 | 109.5291 | 107.4142 | 122.3923 | 122.6028 | 0.050354 | 122.731 | 113.0768 | -0.3067 | 122.6028 | 0.050354 | 113.0768 | 122.3923 | 122.731 | -123.0835 | -123.0469
1935.9688 | 122.9691 | -119.0918 | 3.6484 | -0.11032 | 2.5564e-05 | -0.00081822 | 0.017145 | -0.0062528 | -0.00093346 | 0.0021299 | -118.8034 | 3.6072 | -119.339 | 3.6392 | 3.3463 | -5.9418 | -9.5993 | -11.5814 | 3.7033 | -119.371 | -0.24719 | -0.041198 | 0.28839 | 122.731 | -0.30212 | -0.27924 | 0.054932 | 0.53558 | 109.4925 | 107.5104 | 122.438 | 122.699 | 0.28839 | 122.7951 | 113.15 | -0.27924 | 122.699 | 0.28839 | 113.15 | 122.438 | 122.7951 | -122.9874 | -123.0194
1936.9062 | 122.9416 | -118.721 | 3.978 | -0.11795 | -0.00061524 | 0.004736 | 0.018 | -0.0041166 | -0.0011471 | 0.0036253 | -118.5425 | 3.8727 | -119.0781 | 3.923 | 3.6346 | -5.9418 | -9.3475 | -11.6547 | 3.9917 | -119.0689 | -0.35706 | -0.10528 | 0.17853 | 122.644 | -0.34332 | -0.3479 | 0.013733 | 0.53558 | 109.3735 | 107.0663 | 122.3557 | 122.5937 | 0.17853 | 122.7127 | 112.7792 | -0.3479 | 122.5937 | 0.17853 | 112.7792 | 122.3557 | 122.7127 | -123.056 | -123.0469
1937.9531 | 122.9141 | -118.6478 | 4.1061 | -0.11032 | 0.001521 | 0.0028134 | 0.014582 | -0.0071072 | -0.0032835 | 0.0019163 | -118.4006 | 4.0054 | -118.959 | 4.097 | 3.7857 | -5.8731 | -9.137 | -11.3892 | 4.097 | -118.927 | -0.31128 | -0.10071 | 0.24719 | 122.7448 | -0.32043 | -0.27924 | -0.009155 | 0.55847 | 109.5108 | 107.2586 | 122.4335 | 122.6532 | 0.24719 | 122.7448 | 112.7747 | -0.27924 | 122.6532 | 0.24719 | 112.7747 | 122.4335 | 122.7448 | -123.0652 | -123.0331
1938.9219 | 122.8363 | -118.6295 | 4.216 | 0.027008 | 0.0047254 | 0.0015316 | 0.026117 | -0.003903 | -0.00071986 | 0.0044797 | -118.3548 | 4.1428 | -118.8721 | 4.0604 | 3.7354 | -6.0837 | -9.1461 | -11.6867 | 4.2023 | -118.9407 | -0.24261 | -0.073242 | 0.27466 | 122.6898 | -0.48065 | -0.31128 | -0.013732 | 0.51727 | 109.4833 | 106.9427 | 122.3648 | 122.7722 | 0.27466 | 122.8317 | 112.5458 | -0.31128 | 122.7722 | 0.27466 | 112.5458 | 122.3648 | 122.8317 | -123.0881 | -123.1567
1939.9688 | 122.8958 | -118.5104 | 4.2847 | 0.15671 | 0.0047254 | 0.0085812 | 0.023554 | -0.0024076 | -0.0017881 | 0.0038389 | -118.3319 | 4.1748 | -118.8446 | 4.1107 | 3.804 | -6.0745 | -9.2926 | -11.586 | 4.2892 | -118.8034 | -0.33417 | -0.10986 | 0.17853 | 122.6212 | -0.48065 | -0.29297 | 0.004578 | 0.5127 | 109.2178 | 106.9244 | 122.3145 | 122.6852 | 0.17853 | 122.7997 | 112.4359 | -0.29297 | 122.6852 | 0.17853 | 112.4359 | 122.3145 | 122.7997 | -123.1293 | -123.0881
1940.9062 | 122.8775 | -119.2017 | 3.5614 | -0.17136 | 0.0040846 | 0.008154 | 0.020136 | -0.0030484 | -0.0024289 | 0.0025571 | -119.0552 | 3.479 | -119.5724 | 3.4149 | 3.1265 | -5.9921 | -9.3292 | -11.5952 | 3.5889 | -119.545 | -0.37079 | -0.082397 | 0.14648 | 122.6166 | -0.43487 | -0.34332 | 0.027466 | 0.51727 | 109.8724 | 107.6065 | 122.3282 | 122.6807 | 0.14648 | 122.7905 | 113.2095 | -0.34332 | 122.6807 | 0.14648 | 113.2095 | 122.3282 | 122.7905 | -123.1339 | -123.1064
1941.9688 | 122.9324 | -118.6615 | 4.0375 | 0.53055 | 0.0028028 | 0.003668 | 0.012659 | -0.003903 | -0.00029266 | 0.0042661 | -118.6707 | 3.891 | -119.0643 | 3.9139 | 3.6758 | -5.6671 | -9.2697 | -11.1649 | 4.0512 | -118.9911 | -0.40283 | -0.14648 | -0.009155 | 122.5754 | -0.36163 | -0.32959 | 0.013732 | 0.39368 | 109.3918 | 107.4966 | 122.3373 | 122.5525 | -0.009155 | 122.7127 | 112.9944 | -0.32959 | 122.5525 | -0.009155 | 112.9944 | 122.3373 | 122.7127 | -123.1018 | -123.0286
1942.9062 | 122.9416 | -118.927 | 3.8269 | -0.24002 | -0.00082884 | 0.00046358 | 0.014582 | -0.0062528 | -0.0013609 | 0.0034115 | -118.721 | 3.7399 | -119.2383 | 3.7811 | 3.4882 | -5.6122 | -9.2789 | -11.293 | 3.8544 | -119.1971 | -0.31128 | -0.086975 | 0.20599 | 122.7081 | -0.33874 | -0.27008 | 0.027466 | 0.51727 | 109.6481 | 107.634 | 122.4152 | 122.6669 | 0.20599 | 122.7814 | 113.3148 | -0.27008 | 122.6669 | 0.20599 | 113.3148 | 122.4152 | 122.7814 | -123.0652 | -123.024
1943.9688 | 122.9965 | -118.8721 | 3.8681 | -0.19424 | 0.002162 | 0.0017454 | 0.018427 | -0.0064664 | -7.9062e-05 | 0.0046933 | -118.6157 | 3.7994 | -119.2154 | 3.7903 | 3.5156 | -5.6396 | -9.375 | -11.4441 | 3.8773 | -119.1925 | -0.34332 | -0.068665 | 0.25635 | 122.6624 | -0.35248 | -0.32044 | 0.009155 | 0.59967 | 109.4971 | 107.428 | 122.3877 | 122.6715 | 0.25635 | 122.7493 | 113.2324 | -0.32044 | 122.6715 | 0.25635 | 113.2324 | 122.3877 | 122.7493 | -123.0835 | -123.0606
1944.9062 | 122.9736 | -119.0552 | 3.7125 | -0.018768 | -0.00018804 | 0.0023862 | 0.015009 | -0.0053982 | -0.0015745 | 0.0044797 | -118.8995 | 3.6118 | -119.371 | 3.6209 | 3.3508 | -5.6213 | -9.3338 | -11.5082 | 3.7079 | -119.3298 | -0.31586 | -0.10071 | 0.15564 | 122.6761 | -0.36163 | -0.27466 | -0.004577 | 0.4715 | 109.7214 | 107.547 | 122.406 | 122.6669 | 0.15564 | 122.7631 | 113.4338 | -0.27466 | 122.6669 | 0.15564 | 113.4338 | 122.406 | 122.7631 | -123.0835 | -123.0423
1945.9688 | 122.8683 | -119.101 | 3.7216 | -0.14847 | 0.0019482 | 0.004736 | 0.020991 | -0.0064664 | -0.0015745 | 0.0029843 | -118.9453 | 3.6438 | -119.4168 | 3.5385 | 3.2455 | -5.6625 | -9.4803 | -11.6592 | 3.7354 | -119.4305 | -0.31586 | -0.07782 | 0.15564 | 122.6395 | -0.47607 | -0.32959 | 0.013733 | 0.4715 | 109.6207 | 107.4417 | 122.3465 | 122.7448 | 0.15564 | 122.8363 | 113.4384 | -0.32959 | 122.7448 | 0.15564 | 113.4384 | 122.3465 | 122.8363 | -123.1384 | -123.1522
1946.9062 | 122.9645 | -119.1238 | 3.6209 | 0.7518 | -0.0014696 | 0.0015316 | 0.015009 | -0.0060392 | -0.0041379 | 0.0027707 | -118.8309 | 3.5202 | -119.4534 | 3.566 | 3.3188 | -5.603 | -9.6313 | -11.7966 | 3.6392 | -119.3939 | -0.32959 | -0.10071 | 0.29297 | 122.6898 | -0.30212 | -0.27008 | 0.01831 | 0.62256 | 109.4925 | 107.3273 | 122.4426 | 122.644 | 0.29297 | 122.7631 | 113.5208 | -0.27008 | 122.644 | 0.29297 | 113.5208 | 122.4426 | 122.7631 | -123.0743 | -123.0148
1947.9531 | 122.9553 | -118.1946 | 4.4403 | -0.20187 | 0.0013074 | 0.0028134 | 0.016504 | -0.0034756 | -0.0024289 | 0.0017027 | -118.071 | 4.3762 | -118.5928 | 4.4724 | 4.1931 | -5.3879 | -9.5489 | -11.4807 | 4.4495 | -118.5928 | -0.39825 | -0.064087 | 0.1236 | 122.6669 | -0.24719 | -0.39825 | 0.009155 | 0.52185 | 108.6456 | 106.7139 | 122.3877 | 122.5708 | 0.1236 | 122.644 | 112.8067 | -0.39825 | 122.5708 | 0.1236 | 112.8067 | 122.3877 | 122.644 | -123.0331 | -123.0331
1948.9062 | 122.85 | -118.6295 | 4.1565 | 0.019379 | 0.0055798 | 0.0045224 | 0.024622 | -0.0043302 | -0.00050626 | 0.0042661 | -118.4097 | 4.0924 | -118.927 | 4.0192 | 3.7079 | -5.5939 | -9.5123 | -11.6501 | 4.1473 | -118.9636 | -0.29755 | -0.064087 | 0.21973 | 122.6486 | -0.44861 | -0.33417 | -0.009155 | 0.51727 | 109.1171 | 106.9794 | 122.3373 | 122.7219 | 0.21973 | 122.7768 | 113.0356 | -0.33417 | 122.7219 | 0.21973 | 113.0356 | 122.3373 | 122.7768 | -123.0835 | -123.1201
1949.9688 | 122.9233 | -119.3481 | 3.3188 | 0.14908 | 0.002162 | 0.003668 | 0.014368 | -0.0034756 | 0.00056194 | 0.0029843 | -119.2886 | 3.186 | -119.8105 | 3.1815 | 2.9343 | -5.7266 | -9.2834 | -11.8149 | 3.2913 | -119.7098 | -0.46234 | -0.13275 | 0.05951 | 122.5296 | -0.38452 | -0.36163 | -0.027466 | 0.52185 | 110.0647 | 107.5333 | 122.2824 | 122.5342 | 0.05951 | 122.6395 | 113.6215 | -0.36163 | 122.5342 | 0.05951 | 113.6215 | 122.2824 | 122.6395 | -123.1293 | -123.0286
1950.9062 | 120.9091 | -117.7963 | 4.8019 | -0.24765 | 0.0010938 | 0.001959 | 0.01565 | -0.0045438 | -0.0047787 | 0.0042661 | -117.778 | 4.7058 | -118.2587 | 4.7287 | 4.4174 | -5.5847 | -9.1187 | -11.3937 | 4.8294 | -118.2632 | -0.46234 | -0.09613 | 0.018311 | 122.525 | -0.38452 | -0.46692 | 0.027466 | 0.48065 | 108.6777 | 106.4026 | 122.2137 | 122.5021 | 0.018311 | 122.6257 | 112.2116 | -0.46692 | 122.5021 | 0.018311 | 112.2116 | 122.2137 | 122.6257 | -123.0606 | -123.0652
1951.9688 | 122.9095 | -119.9753 | 2.7878 | 0.095673 | -0.00018804 | 0.00046358 | 0.017359 | -0.004971 | -0.0013609 | 0.0046933 | -119.8654 | 2.7008 | -120.2682 | 2.655 | 2.4216 | -5.9052 | -9.4208 | -11.4944 | 2.8061 | -120.2454 | -0.29297 | -0.086975 | 0.10986 | 122.6303 | -0.36621 | -0.27008 | 0.01831 | 0.40283 | 110.5545 | 108.4808 | 122.3969 | 122.6761 | 0.10986 | 122.7814 | 114.0701 | -0.27008 | 122.6761 | 0.10986 | 114.0701 | 122.3969 | 122.7814 | -123.056 | -123.0331
1952.9062 | 122.9965 | -118.7851 | 3.8864 | -0.1561 | -0.0021106 | 0.0038816 | 0.015864 | -0.0060392 | -0.0015745 | 0.0061887 | -118.5745 | 3.8361 | -119.0918 | 3.8589 | 3.6072 | -5.4657 | -9.4299 | -11.6501 | 3.9093 | -119.1055 | -0.3067 | -0.050354 | 0.21057 | 122.644 | -0.27924 | -0.32044 | 0.022888 | 0.51727 | 109.3552 | 107.135 | 122.3923 | 122.6212 | 0.21057 | 122.6944 | 113.3194 | -0.32044 | 122.6212 | 0.21057 | 113.3194 | 122.3923 | 122.6944 | -122.9782 | -122.9919
1953.9688 | 122.9507 | -118.4692 | 4.2252 | -0.095062 | 0.0017346 | 0.0021726 | 0.015864 | -0.0064664 | -0.00093346 | 0.0029843 | -118.3136 | 4.1199 | -118.8217 | 4.1702 | 3.8818 | -5.4794 | -9.288 | -11.3846 | 4.2343 | -118.8629 | -0.35248 | -0.10529 | 0.15564 | 122.6395 | -0.34332 | -0.39368 | 0.009155 | 0.50812 | 109.1812 | 107.0847 | 122.3511 | 122.5891 | 0.15564 | 122.7036 | 112.9898 | -0.39368 | 122.5891 | 0.15564 | 112.9898 | 122.3511 | 122.7036 | -123.0469 | -123.0881
1954.9062 | 122.9782 | -118.4509 | 4.2801 | -0.10269 | 0.00045296 | 0.0045224 | 0.015009 | -0.0077482 | -0.0020017 | 0.0029843 | -118.2541 | 4.1794 | -118.8171 | 4.248 | 3.9368 | -5.4932 | -9.4849 | -11.4441 | 4.2709 | -118.7622 | -0.36621 | -0.10071 | 0.19684 | 122.699 | -0.34332 | -0.31128 | -0.009155 | 0.56305 | 108.9661 | 107.0068 | 122.3877 | 122.6303 | 0.19684 | 122.7219 | 112.9578 | -0.31128 | 122.6303 | 0.19684 | 112.9578 | 122.3877 | 122.7219 | -123.0972 | -123.0423
1955.9688 | 122.9645 | -120.3186 | 2.4811 | 0.027008 | -0.0021106 | 0.0045224 | 0.015223 | -0.0068936 | -0.0020017 | 0.0042661 | -120.1263 | 2.3712 | -120.639 | 2.3666 | 2.124 | -5.6763 | -9.7916 | -10.6613 | 2.4811 | -120.5841 | -0.32043 | -0.10986 | 0.19226 | 122.6852 | -0.35706 | -0.2655 | 0 | 0.51269 | 110.527 | 109.6573 | 122.4426 | 122.6898 | 0.19226 | 122.7997 | 114.6423 | -0.2655 | 122.6898 | 0.19226 | 114.6423 | 122.4426 | 122.7997 | -123.1201 | -123.0652
1956.9062 | 122.9416 | -71.7499 | 50.8026 | -0.087433 | 2.5564e-05 | 0.0023862 | 0.0036871 | -0.0090298 | -0.0017881 | -6.342e-06 | -70.1431 | 52.0935 | -70.7108 | 52.153 | 50.3082 | 0.67749 | -2.7054 | -3.8498 | 51.1688 | -72.0291 | 1.0391 | 1.2909 | 1.6068 | 123.9029 | -0.49438 | -0.27924 | 0.36621 | 0.56763 | 69.0445 | 67.9001 | 122.0581 | 123.8434 | 1.6068 | 122.9187 | 72.4274 | -0.27924 | 123.8434 | 1.6068 | 72.4274 | 122.0581 | 122.9187 | -121.5134 | -122.8317
1957.9531 | 122.9095 | -118.5104 | 4.1885 | 0.15671 | 2.5564e-05 | 0.004736 | 0.019922 | -0.0056118 | -0.0011471 | 0.0049069 | -118.396 | 4.0924 | -118.9041 | 4.129 | 3.8269 | -5.4382 | -9.4803 | -10.643 | 4.184 | -118.8492 | -0.39368 | -0.096131 | 0.11444 | 122.6395 | -0.36163 | -0.33875 | -0.004578 | 0.50812 | 109.0302 | 107.8674 | 122.3373 | 122.6028 | 0.11444 | 122.6944 | 113.0722 | -0.33875 | 122.6028 | 0.11444 | 113.0722 | 122.3373 | 122.6944 | -123.0927 | -123.0377
1958.9062 | 122.9279 | -118.5608 | 4.216 | -0.011139 | -0.00040164 | 0.0023862 | 0.014368 | -0.0075344 | -0.0034971 | 0.0051205 | -118.4463 | 4.1245 | -118.9087 | 4.1336 | 3.8406 | -5.4474 | -9.3887 | -10.6796 | 4.1977 | -118.8354 | -0.3479 | -0.091552 | 0.11444 | 122.6944 | -0.37537 | -0.27466 | -0.01831 | 0.46234 | 109.1721 | 107.8812 | 122.4014 | 122.6852 | 0.11444 | 122.7585 | 113.1134 | -0.27466 | 122.6852 | 0.11444 | 113.1134 | 122.4014 | 122.7585 | -123.1247 | -123.0515
1959.9688 | 122.85 | -118.9728 | 3.8452 | 0.034637 | 0.001521 | 0.0045224 | 0.023981 | -0.002194 | -0.0020017 | 0.0019163 | -118.7668 | 3.7491 | -119.3069 | 3.6621 | 3.3691 | -5.6168 | -9.4528 | -10.6155 | 3.8589 | -119.2474 | -0.33417 | -0.096131 | 0.20599 | 122.6349 | -0.47607 | -0.27466 | 0.013733 | 0.54016 | 109.52 | 108.3572 | 122.3419 | 122.7219 | 0.20599 | 122.8317 | 113.356 | -0.27466 | 122.7219 | 0.20599 | 113.356 | 122.3419 | 122.8317 | -123.1522 | -123.0927
1960.9219 | 122.8729 | -118.8812 | 3.9322 | -0.19424 | 0.0036572 | 0.003668 | 0.020563 | -0.0051846 | -0.0020017 | 0.0029843 | -118.7347 | 3.8681 | -119.1834 | 3.772 | 3.4698 | -5.4016 | -9.5718 | -10.6979 | 3.9368 | -119.1925 | -0.30212 | -0.064087 | 0.14648 | 122.6532 | -0.46234 | -0.31128 | 0.004578 | 0.44861 | 109.3094 | 108.1833 | 122.3511 | 122.7493 | 0.14648 | 122.818 | 113.4796 | -0.31128 | 122.7493 | 0.14648 | 113.4796 | 122.3511 | 122.818 | -123.1155 | -123.1247
1961.9688 | 122.9324 | -119.4489 | 3.2639 | 0.18723 | 0.0017346 | 0.0066586 | 0.015009 | -0.0034756 | -0.0028561 | 0.0049069 | -119.3253 | 3.154 | -119.8334 | 3.1586 | 2.9114 | -5.6351 | -9.9243 | -11.0138 | 3.2547 | -119.7647 | -0.38452 | -0.10986 | 0.1236 | 122.6074 | -0.35248 | -0.31586 | -0.009155 | 0.50812 | 109.5245 | 108.4351 | 122.3602 | 122.6028 | 0.1236 | 122.7036 | 113.8138 | -0.31586 | 122.6028 | 0.1236 | 113.8138 | 122.3602 | 122.7036 | -123.0972 | -123.0286
1962.9062 | 122.9919 | -119.7052 | 3.0441 | -0.079803 | -0.00061524 | 0.001959 | 0.014582 | -0.0073208 | -0.0024289 | 0.0040525 | -119.4809 | 2.9709 | -119.9982 | 3.0029 | 2.7557 | -5.7083 | -9.9014 | -11.0092 | 3.0716 | -119.9661 | -0.29297 | -0.073242 | 0.2243 | 122.7081 | -0.28839 | -0.26093 | 0.027466 | 0.51727 | 109.8038 | 108.696 | 122.4609 | 122.6761 | 0.2243 | 122.7768 | 113.9969 | -0.26093 | 122.6761 | 0.2243 | 113.9969 | 122.4609 | 122.7768 | -123.0423 | -123.0103
1963.9531 | 122.9416 | -110.4401 | 12.2864 | -0.064545 | 0.0010938 | 0.0049496 | 0.012873 | -0.0062528 | -0.0020017 | 0.0036253 | -110.1791 | 12.3642 | -110.6003 | 12.2818 | 11.8423 | -4.6051 | -8.7753 | -9.4162 | 12.291 | -110.7193 | -0.16022 | 0.07782 | 0.26093 | 122.7219 | -0.44403 | -0.27924 | 0.004578 | 0.42114 | 101.6647 | 101.0239 | 122.2824 | 122.8043 | 0.26093 | 122.731 | 105.835 | -0.27924 | 122.8043 | 0.26093 | 105.835 | 122.2824 | 122.731 | -122.8867 | -123.0057
1964.9062 | 122.9187 | -118.8354 | 3.9642 | -0.079803 | 0.00045296 | -0.003168 | 0.013514 | -0.0051846 | -0.0026425 | 0.0034115 | -118.6066 | 3.891 | -119.1101 | 3.8818 | 3.6118 | -5.6671 | -10.5698 | -10.8215 | 3.9871 | -119.0598 | -0.27466 | -0.073242 | 0.22888 | 122.7173 | -0.35248 | -0.2243 | 0.022889 | 0.50354 | 108.2657 | 108.0139 | 122.4472 | 122.7264 | 0.22888 | 122.8226 | 113.1683 | -0.2243 | 122.7264 | 0.22888 | 113.1683 | 122.4472 | 122.8226 | -123.0743 | -123.024
1965.9688 | 122.8683 | -117.8192 | 4.834 | 0.21774 | 0.0030164 | 0.0043088 | 0.022059 | -0.004971 | -0.0013609 | 0.0031979 | -117.7414 | 4.7607 | -118.2404 | 4.6967 | 4.3716 | -5.6671 | -10.5743 | -10.7712 | 4.8477 | -118.2312 | -0.42114 | -0.073242 | 0.07782 | 122.5159 | -0.46234 | -0.41199 | 0.013733 | 0.49896 | 107.2449 | 107.048 | 122.1909 | 122.58 | 0.07782 | 122.6669 | 112.1521 | -0.41199 | 122.58 | 0.07782 | 112.1521 | 122.1909 | 122.6669 | -123.0743 | -123.0652
1966.9062 | 122.937 | -117.952 | 4.6509 | 0.088043 | 2.5564e-05 | 0.0034544 | 0.013514 | -0.0047574 | 0.00056194 | 0.0029843 | -117.8879 | 4.6234 | -118.364 | 4.5868 | 4.3076 | -5.69 | -10.7025 | -10.8444 | 4.6555 | -118.3548 | -0.41199 | -0.027466 | 0.064087 | 122.5388 | -0.34332 | -0.40283 | 0.004578 | 0.47607 | 107.2494 | 107.1075 | 122.2595 | 122.5754 | 0.064087 | 122.6074 | 112.262 | -0.40283 | 122.5754 | 0.064087 | 112.262 | 122.2595 | 122.6074 | -123.0148 | -123.0057
1967.9688 | 122.8775 | -118.3319 | 4.4769 | 0.27115 | 0.0023756 | 0.001959 | 0.021845 | -0.0041166 | -0.0013609 | 0.0021299 | -118.158 | 4.39 | -118.6432 | 4.2847 | 3.9917 | -5.8731 | -10.7803 | -10.9406 | 4.4815 | -118.6249 | -0.31128 | -0.086975 | 0.17395 | 122.6166 | -0.48523 | -0.29297 | 0.004577 | 0.48523 | 107.5516 | 107.3914 | 122.3236 | 122.7219 | 0.17395 | 122.8134 | 112.4588 | -0.29297 | 122.7219 | 0.17395 | 112.4588 | 122.3236 | 122.8134 | -123.1201 | -123.1018
1968.9062 | 122.9462 | -117.9611 | 4.8065 | -0.018768 | 0.001521 | 0.0040952 | 0.012873 | -0.0047574 | -0.00093346 | 0.0036253 | -117.7917 | 4.715 | -118.2632 | 4.7104 | 4.4083 | -5.777 | -10.9817 | -10.7666 | 4.8203 | -118.2175 | -0.30212 | -0.091553 | 0.16937 | 122.6715 | -0.39825 | -0.25635 | 0.013732 | 0.4715 | 106.9794 | 107.1945 | 122.3694 | 122.6761 | 0.16937 | 122.7814 | 112.1841 | -0.25635 | 122.6761 | 0.16937 | 112.1841 | 122.3694 | 122.7814 | -123.0698 | -123.024
1969.9688 | 122.9004 | -117.0044 | 5.5847 | 0.21011 | 0.00088016 | -0.0010318 | 0.019709 | -0.0030484 | -0.0017881 | 0.0025571 | -116.8854 | 5.571 | -117.3798 | 5.5344 | 5.2277 | -5.6442 | -10.6979 | -10.7208 | 5.6305 | -117.3889 | -0.37537 | -0.013733 | 0.11902 | 122.5388 | -0.35706 | -0.38452 | 0.045776 | 0.49439 | 106.3065 | 106.2836 | 122.2321 | 122.5754 | 0.11902 | 122.6349 | 111.3602 | -0.38452 | 122.5754 | 0.11902 | 111.3602 | 122.2321 | 122.6349 | -122.9645 | -122.9736
1970.9062 | 122.9324 | -117.7094 | 4.985 | 0.065155 | -0.0010424 | 0.0025998 | 0.016291 | -0.0058256 | -0.0022153 | 0.0046933 | -117.8192 | 4.8889 | -118.1717 | 4.8706 | 4.5502 | -5.9647 | -10.7437 | -10.8765 | 4.9667 | -118.0618 | -0.46234 | -0.09613 | -0.10986 | 122.58 | -0.43487 | -0.35248 | -0.01831 | 0.35248 | 106.9656 | 106.8329 | 122.2595 | 122.5983 | -0.10986 | 122.6761 | 111.7447 | -0.35248 | 122.5983 | -0.10986 | 111.7447 | 122.2595 | 122.6761 | -123.1567 | -123.0469
1971.9531 | 122.9233 | -115.6906 | 7.0358 | 0.1033 | 0.00066656 | 0.005377 | 0.01565 | -0.0058256 | -0.0034971 | 0.0027707 | -115.5212 | 6.926 | -115.9973 | 6.9672 | 6.6055 | -5.7083 | -10.2264 | -10.5194 | 7.0129 | -116.0156 | -0.3067 | -0.10986 | 0.16937 | 122.6578 | -0.4303 | -0.32501 | -0.022889 | 0.47607 | 105.4642 | 105.1712 | 122.2961 | 122.6166 | 0.16937 | 122.7036 | 109.9823 | -0.32501 | 122.6166 | 0.16937 | 109.9823 | 122.2961 | 122.7036 | -123.0331 | -123.0515
1972.9062 | 122.937 | -114.8575 | 7.7499 | 0.20248 | 0.0019482 | 0.0025998 | 0.014582 | -0.004971 | -0.00029266 | 0.0031979 | -114.7888 | 7.6767 | -115.2878 | 7.7087 | 7.3242 | -5.6488 | -9.8511 | -10.3271 | 7.7683 | -115.2832 | -0.4303 | -0.073242 | 0.068665 | 122.5662 | -0.42572 | -0.42572 | 0.018311 | 0.49896 | 105.0064 | 104.5303 | 122.1817 | 122.5342 | 0.068665 | 122.6257 | 109.2087 | -0.42572 | 122.5342 | 0.068665 | 109.2087 | 122.1817 | 122.6257 | -123.0377 | -123.0331
1973.9688 | 122.9691 | -116.4871 | 6.1661 | 0.13382 | 0.0019482 | 0.003027 | 0.020991 | -0.0028348 | -0.0020017 | 0.0021299 | -116.3544 | 6.0745 | -116.8945 | 6.1432 | 5.8182 | -5.8456 | -10.5194 | -10.5286 | 6.1569 | -116.8442 | -0.40741 | -0.091553 | 0.13275 | 122.6303 | -0.3479 | -0.35706 | -0.009156 | 0.54016 | 105.9677 | 105.9586 | 122.3053 | 122.5616 | 0.13275 | 122.644 | 110.6415 | -0.35706 | 122.5616 | 0.13275 | 110.6415 | 122.3053 | 122.644 | -123.0606 | -123.0103
1974.9062 | 122.9324 | -118.6157 | 4.1611 | 0.034637 | 0.00323 | 0.0021726 | 0.016291 | -0.0064664 | -0.0020017 | 0.0053343 | -118.4006 | 4.0283 | -119.0002 | 4.0146 | 3.7079 | -6.2622 | -10.4462 | -10.5972 | 4.1061 | -118.9316 | -0.38452 | -0.13275 | 0.21515 | 122.6303 | -0.45319 | -0.31586 | -0.054932 | 0.59967 | 108.1696 | 108.0185 | 122.3236 | 122.644 | 0.21515 | 122.7219 | 112.3535 | -0.31586 | 122.644 | 0.21515 | 112.3535 | 122.3236 | 122.7219 | -123.1613 | -123.0927
1975.9688 | 122.9141 | -116.8259 | 5.777 | 0.18723 | 0.0019482 | 0.003668 | 0.016291 | -0.0064664 | -7.9062e-05 | 0.0034115 | -116.7801 | 5.69 | -117.2562 | 5.7312 | 5.3833 | -6.3354 | -10.0388 | -10.4599 | 5.7999 | -117.2562 | -0.4303 | -0.086976 | 0.045777 | 122.5571 | -0.39368 | -0.4303 | 0.022888 | 0.47607 | 106.7871 | 106.366 | 122.2092 | 122.5159 | 0.045777 | 122.6257 | 110.4904 | -0.4303 | 122.5159 | 0.045777 | 110.4904 | 122.2092 | 122.6257 | -123.0331 | -123.0331
1976.9062 | 122.937 | -117.0914 | 5.6122 | 0.21011 | 2.5564e-05 | 0.001959 | 0.017145 | -0.0062528 | -0.00071986 | 0.0036253 | -116.9724 | 5.5023 | -117.4438 | 5.5618 | 5.2368 | -6.0287 | -10.1303 | -10.4507 | 5.6259 | -117.4164 | -0.35248 | -0.10986 | 0.11902 | 122.6532 | -0.37537 | -0.32501 | 0.013733 | 0.4715 | 106.9611 | 106.6406 | 122.3282 | 122.5937 | 0.11902 | 122.7173 | 111.0626 | -0.32501 | 122.5937 | 0.11902 | 111.0626 | 122.3282 | 122.7173 | -123.056 | -123.0286
1977.9688 | 122.8271 | -118.2816 | 4.5136 | 0.065155 | 0.0038708 | 0.0045224 | 0.025263 | -0.0013394 | -0.00071986 | 0.0038389 | -118.1351 | 4.422 | -118.6432 | 4.3304 | 4.0009 | -6.3034 | -10.6567 | -10.9268 | 4.509 | -118.5974 | -0.36163 | -0.091553 | 0.14648 | 122.612 | -0.5127 | -0.31586 | -0.004578 | 0.50812 | 107.6248 | 107.3547 | 122.2824 | 122.7036 | 0.14648 | 122.7905 | 111.9781 | -0.31586 | 122.7036 | 0.14648 | 111.9781 | 122.2824 | 122.7905 | -123.1567 | -123.111
1978.9062 | 122.9233 | -118.5104 | 4.2435 | 0.12619 | 2.5564e-05 | 0.003668 | 0.014582 | -0.0056118 | -0.0028561 | 0.0040525 | -118.3228 | 4.1199 | -118.8034 | 4.1336 | 3.8681 | -6.3309 | -10.3775 | -10.5286 | 4.2572 | -118.7714 | -0.29297 | -0.1236 | 0.18768 | 122.644 | -0.37537 | -0.26093 | 0.013733 | 0.48065 | 108.1329 | 107.9819 | 122.3785 | 122.6303 | 0.18768 | 122.7676 | 112.1796 | -0.26093 | 122.6303 | 0.18768 | 112.1796 | 122.3785 | 122.7676 | -123.0469 | -123.0148
1979.9688 | 122.937 | -118.7576 | 4.0192 | 0.21011 | 0.0019482 | 0.003668 | 0.023127 | -0.0041166 | -0.0022153 | 0.0042661 | -118.6157 | 3.9322 | -119.0826 | 3.9001 | 3.6209 | -6.4774 | -10.5927 | -10.7162 | 4.0054 | -119.0323 | -0.32501 | -0.086975 | 0.14191 | 122.6578 | -0.39825 | -0.27466 | -0.013733 | 0.46692 | 108.165 | 108.0414 | 122.3785 | 122.6898 | 0.14191 | 122.7631 | 112.2803 | -0.27466 | 122.6898 | 0.14191 | 112.2803 | 122.3785 | 122.7631 | -123.1018 | -123.0515
1980.9062 | 122.8958 | -110.7513 | 11.5585 | -0.087433 | 0.00023916 | 0.0017454 | 0.013941 | -0.0062528 | -0.00050626 | 0.0036253 | -107.2906 | 17.1661 | -106.4484 | 12.5839 | 12.2681 | -7.3425 | -10.1761 | -11.0046 | 13.0417 | -110.6735 | 4.303 | 5.6076 | 3.4607 | 123.3353 | 0.70953 | 0.07782 | 1.4832 | -0.84229 | 100.5753 | 99.7467 | 123.0194 | 127.9175 | 3.4607 | 123.793 | 103.4088 | 0.07782 | 127.9175 | 3.4607 | 103.4088 | 123.0194 | 123.793 | -118.0069 | -122.2321
1981.9531 | 122.9187 | -117.4393 | 5.3146 | 0.22537 | 0.0030164 | 0.0045224 | 0.021845 | -0.002194 | -0.0034971 | 0.0044797 | -117.2241 | 5.2551 | -117.7505 | 5.246 | 4.9576 | -6.1203 | -10.2814 | -10.7208 | 5.3284 | -117.7048 | -0.31128 | -0.059509 | 0.21515 | 122.6852 | -0.35705 | -0.2655 | 0.013733 | 0.52643 | 107.1579 | 106.7184 | 122.3969 | 122.6944 | 0.21515 | 122.7676 | 111.319 | -0.2655 | 122.6944 | 0.21515 | 111.319 | 122.3969 | 122.7676 | -123.0652 | -123.0194
1982.9062 | 122.9324 | -118.4235 | 4.3442 | 0.12619 | 0.0017346 | 0.0034544 | 0.014795 | -0.0053982 | -0.0020017 | 0.0049069 | -118.222 | 4.2709 | -118.7164 | 4.2297 | 3.9688 | -6.8619 | -10.0571 | -10.9909 | 4.3579 | -118.7027 | -0.29297 | -0.073242 | 0.20142 | 122.6532 | -0.37537 | -0.27924 | 0.013733 | 0.49438 | 108.3664 | 107.4326 | 122.3923 | 122.6944 | 0.20142 | 122.7814 | 111.5616 | -0.27924 | 122.6944 | 0.20142 | 111.5616 | 122.3923 | 122.7814 | -123.0606 | -123.0469
1983.9688 | 122.9507 | -116.1392 | 6.4819 | 0.21774 | 0.0023756 | 0.004736 | 0.019068 | -0.0053982 | -0.0032835 | 0.0010617 | -116.0797 | 6.3812 | -116.5695 | 6.3995 | 6.0654 | -6.7886 | -9.7046 | -10.5011 | 6.4682 | -116.5924 | -0.4303 | -0.10071 | 0.059509 | 122.5388 | -0.41657 | -0.45319 | -0.013733 | 0.48981 | 106.4346 | 105.6381 | 122.2046 | 122.5204 | 0.059509 | 122.6074 | 109.3506 | -0.45319 | 122.5204 | 0.059509 | 109.3506 | 122.2046 | 122.6074 | -123.0515 | -123.0743
1984.9062 | 122.9691 | -116.5237 | 6.1478 | -0.16373 | -0.00040164 | 0.0043088 | 0.018427 | -0.0036892 | -0.0034971 | 0.0055479 | -116.3773 | 6.0608 | -116.8945 | 6.1432 | 5.809 | -5.9006 | -10.1852 | -10.6934 | 6.1661 | -116.8533 | -0.37079 | -0.086975 | 0.14648 | 122.6669 | -0.33874 | -0.32959 | 0.018311 | 0.51727 | 106.3385 | 105.8304 | 122.3328 | 122.5845 | 0.14648 | 122.6898 | 110.6232 | -0.32959 | 122.5845 | 0.14648 | 110.6232 | 122.3328 | 122.6898 | -123.0423 | -123.0011
1985.9688 | 122.9691 | -117.7094 | 4.9805 | 0.12619 | -0.00018804 | 0.0043088 | 0.021631 | -0.003262 | -0.0011471 | 0.0044797 | -117.4942 | 4.9118 | -118.0389 | 4.9713 | 4.6417 | -6.0745 | -10.231 | -10.9177 | 5.0125 | -118.0206 | -0.32959 | -0.068665 | 0.21515 | 122.6807 | -0.33875 | -0.31128 | 0.032043 | 0.54474 | 107.4783 | 106.7917 | 122.3511 | 122.6212 | 0.21515 | 122.7219 | 111.6348 | -0.31128 | 122.6212 | 0.21515 | 111.6348 | 122.3511 | 122.7219 | -123.0194 | -123.0011
1987.1562 | 122.9782 | -117.485 | 5.2734 | 0.1796 | 0.0013074 | 0.0049496 | 0.023554 | -0.002194 | -0.0026425 | 0.0031979 | -117.2058 | 5.1956 | -117.7551 | 5.3101 | 4.921 | -6.2714 | -10.4782 | -10.9634 | 5.2689 | -117.7643 | -0.27008 | -0.077819 | 0.27923 | 122.7951 | -0.35248 | -0.27924 | -0.004577 | 0.54932 | 107.0068 | 106.5216 | 122.406 | 122.6807 | 0.27923 | 122.7539 | 111.2137 | -0.27924 | 122.6807 | 0.27923 | 111.2137 | 122.406 | 122.7539 | -123.0286 | -123.0377
1988.4062 | 122.9233 | -118.309 | 4.4586 | -0.2095 | 0.0010938 | 0.0045224 | 0.019495 | -0.004971 | -0.00093346 | 0.0051205 | -118.1168 | 4.3533 | -118.6203 | 4.3625 | 4.0833 | -6.3171 | -9.9838 | -11.1008 | 4.4357 | -118.6523 | -0.31128 | -0.10529 | 0.19226 | 122.6715 | -0.37537 | -0.34332 | -0.022888 | 0.50354 | 108.3252 | 107.2083 | 122.3923 | 122.6624 | 0.19226 | 122.7448 | 111.9919 | -0.34332 | 122.6624 | 0.19226 | 111.9919 | 122.3923 | 122.7448 | -123.0789 | -123.111
1989.3281 | 122.8638 | -118.4052 | 4.3396 | -0.0035098 | 0.0025892 | 0.0043088 | 0.024195 | -0.0034756 | -0.0052061 | 0.0044797 | -118.2587 | 4.2755 | -118.7805 | 4.2068 | 3.9093 | -7.8781 | -10.3409 | -10.9589 | 4.3533 | -118.7119 | -0.37537 | -0.064087 | 0.14648 | 122.612 | -0.4303 | -0.3067 | 0.013733 | 0.52185 | 108.0643 | 107.4463 | 122.3145 | 122.6807 | 0.14648 | 122.7585 | 110.527 | -0.3067 | 122.6807 | 0.14648 | 110.527 | 122.3145 | 122.7585 | -123.1201 | -123.0515
1990.375 | 122.9507 | -118.9453 | 3.8315 | 0.0041197 | 0.0013074 | 0.0040952 | 0.013727 | -0.0081754 | -0.0017881 | 0.0064023 | -118.7943 | 3.7308 | -119.2703 | 3.7445 | 3.5065 | -9.7412 | -10.9039 | -10.9863 | 3.8452 | -119.2291 | -0.32501 | -0.10071 | 0.15106 | 122.6898 | -0.32501 | -0.28381 | 0.013733 | 0.47607 | 108.0414 | 107.959 | 122.4518 | 122.6761 | 0.15106 | 122.7905 | 109.2041 | -0.28381 | 122.6761 | 0.15106 | 109.2041 | 122.4518 | 122.7905 | -123.1018 | -123.0606
1991.1875 | 122.9279 | -118.9728 | 3.7994 | 0.057526 | -0.0010424 | 0.0038816 | 0.014368 | -0.0047574 | -0.0032835 | 0.0044797 | -118.8538 | 3.6484 | -119.3115 | 3.653 | 3.3875 | -12.3779 | -10.8536 | -11.2198 | 3.7994 | -119.2749 | -0.33874 | -0.15106 | 0.11902 | 122.6257 | -0.41199 | -0.30212 | 0 | 0.45776 | 108.1192 | 107.753 | 122.3602 | 122.6212 | 0.11902 | 122.7722 | 106.5948 | -0.30212 | 122.6212 | 0.11902 | 106.5948 | 122.3602 | 122.7722 | -123.111 | -123.0743
1993.1562 | 122.8958 | -118.5974 | 4.1199 | -0.14847 | 0.0017346 | 0.0068722 | 0.024622 | -0.0056118 | -0.0034971 | 0.0012753 | -118.4692 | 4.0237 | -119.0048 | 4.0009 | 3.7033 | -10.9589 | -10.936 | -11.2473 | 4.1107 | -119.0048 | -0.40741 | -0.09613 | 0.12817 | 122.5983 | -0.41657 | -0.40741 | -0.009155 | 0.53558 | 107.6614 | 107.3502 | 122.3007 | 122.6212 | 0.12817 | 122.7081 | 107.6386 | -0.40741 | 122.6212 | 0.12817 | 107.6386 | 122.3007 | 122.7081 | -123.1247 | -123.1247
1994.1562 | 122.8912 | -118.9041 | 3.8864 | -0.20187 | 0.0025892 | -0.0012454 | 0.021845 | -0.0045438 | -0.0028561 | 0.0031979 | -118.7439 | 3.8406 | -119.2017 | 3.7262 | 3.4561 | -8.7616 | -10.8307 | -11.2198 | 3.9001 | -119.2337 | -0.29755 | -0.045777 | 0.16022 | 122.6303 | -0.4303 | -0.32959 | 0.013732 | 0.45776 | 108.0734 | 107.6843 | 122.3602 | 122.7448 | 0.16022 | 122.8043 | 110.1425 | -0.32959 | 122.7448 | 0.16022 | 110.1425 | 122.3602 | 122.8043 | -123.0881 | -123.1201
1994.7344 | 122.8821 | -118.7576 | 4.0283 | -0.18662 | 0.00045296 | 0.0025998 | 0.01565 | -0.004971 | -0.0030697 | 0.0031979 | -118.5516 | 3.9551 | -119.0369 | 3.9322 | 3.6621 | -10.3226 | -11.0413 | -11.3297 | 4.0604 | -119.0277 | -0.27924 | -0.073242 | 0.20599 | 122.6898 | -0.36621 | -0.27008 | 0.032044 | 0.48523 | 107.7164 | 107.428 | 122.4197 | 122.7127 | 0.20599 | 122.818 | 108.4351 | -0.27008 | 122.7127 | 0.20599 | 108.4351 | 122.4197 | 122.818 | -123.0652 | -123.056
1995.5781 | 122.9691 | -117.0776 | 5.5389 | -0.026398 | 0.0042982 | 0.004736 | 0.016718 | -0.0030484 | -0.00050626 | 0.0027707 | -117.0135 | 5.4657 | -117.4942 | 5.4794 | 5.191 | -8.7662 | -10.6796 | -11.1923 | 5.5573 | -117.5354 | -0.41657 | -0.073242 | 0.064087 | 122.5571 | -0.3479 | -0.45776 | 0.018311 | 0.48065 | 106.398 | 105.8853 | 122.2687 | 122.5433 | 0.064087 | 122.6349 | 108.3115 | -0.45776 | 122.5433 | 0.064087 | 108.3115 | 122.2687 | 122.6349 | -123.0331 | -123.0743
2000 | 122.9828 | -117.2791 | 5.3741 | -0.10269 | 0.00088016 | 0.001959 | 0.016291 | -0.0051846 | -0.0020017 | 0.0040525 | -117.1738 | 5.278 | -117.6636 | 5.3467 | 5.0446 | -8.2626 | -10.4782 | -10.8719 | 5.3696 | -117.691 | -0.38452 | -0.096131 | 0.10529 | 122.6257 | -0.32959 | -0.41199 | -0.004578 | 0.48981 | 106.8008 | 106.4072 | 122.3236 | 122.5571 | 0.10529 | 122.6486 | 109.0164 | -0.41199 | 122.5571 | 0.10529 | 109.0164 | 122.3236 | 122.6486 | -123.0377 | -123.0652
2000.4375 | 122.9416 | -117.6819 | 5.0537 | 0.15671 | 0.0013074 | 0.0011044 | 0.016932 | -0.0068936 | -0.00029266 | 0.0036253 | -117.5446 | 4.9713 | -118.0298 | 4.9301 | 4.6555 | -8.7891 | -10.8353 | -10.8856 | 5.0766 | -117.984 | -0.3479 | -0.082398 | 0.13733 | 122.612 | -0.39825 | -0.30212 | 0.022888 | 0.48523 | 106.8466 | 106.7963 | 122.3373 | 122.6532 | 0.13733 | 122.7585 | 108.8928 | -0.30212 | 122.6532 | 0.13733 | 108.8928 | 122.3373 | 122.7585 | -123.0835 | -123.0377
2000.9062 | 122.9691 | -116.478 | 6.1523 | 0.21011 | 0.00323 | 0.0034544 | 0.017786 | -0.004971 | -0.0015745 | 0.0046933 | -116.4047 | 6.0654 | -116.9083 | 6.1111 | 5.8044 | -8.9264 | -10.8261 | -10.5881 | 6.1707 | -116.8716 | -0.4303 | -0.086975 | 0.073242 | 122.5891 | -0.3479 | -0.39368 | 0.01831 | 0.50354 | 105.6519 | 105.8899 | 122.2824 | 122.5433 | 0.073242 | 122.6486 | 107.5516 | -0.39368 | 122.5433 | 0.073242 | 107.5516 | 122.2824 | 122.6486 | -123.0606 | -123.024
2001.9062 | 122.9736 | -117.1875 | 5.5435 | -0.064545 | 0.002162 | 0.00067718 | 0.016504 | -0.0077482 | -0.0045651 | 0.0042661 | -117.0044 | 5.4245 | -117.5217 | 5.4977 | 5.1865 | -6.2302 | -10.9634 | -10.5331 | 5.5573 | -117.5217 | -0.33417 | -0.11902 | 0.1831 | 122.6852 | -0.35706 | -0.33417 | 0.013733 | 0.51727 | 106.2241 | 106.6544 | 122.374 | 122.612 | 0.1831 | 122.7448 | 110.9573 | -0.33417 | 122.612 | 0.1831 | 110.9573 | 122.374 | 122.7448 | -123.0652 | -123.0652
2002.9688 | 122.9324 | -118.2541 | 4.4449 | 0.233 | 0.0025892 | 0.0034544 | 0.021845 | -0.0047574 | -0.0041379 | 0.0059751 | -118.19 | 4.3213 | -118.6935 | 4.3213 | 4.0558 | -6.5369 | -11.2289 | -10.9039 | 4.4128 | -118.6478 | -0.43945 | -0.1236 | 0.064087 | 122.5754 | -0.3891 | -0.39368 | -0.032043 | 0.50354 | 107.0251 | 107.3502 | 122.3099 | 122.5754 | 0.064087 | 122.6669 | 111.7172 | -0.39368 | 122.5754 | 0.064087 | 111.7172 | 122.3099 | 122.6669 | -123.1384 | -123.0927
2003.9062 | 122.3419 | -67.9688 | 54.6661 | 0.088043 | 0.0030164 | 0.0011044 | 0.0004827 | -0.0077482 | -0.00071986 | 0.0040525 | -68.0374 | 54.4327 | -68.6234 | 54.2999 | 52.6154 | -0.42114 | -2.9251 | -2.6367 | 54.0848 | -68.5135 | -0.6546 | -0.23346 | -0.068665 | 122.2687 | -2.0508 | -0.54474 | -0.58136 | 0.58594 | 65.0436 | 65.332 | 120.5841 | 122.4014 | -0.068665 | 122.0535 | 67.5476 | -0.54474 | 122.4014 | -0.068665 | 67.5476 | 120.5841 | 122.0535 | -123.2895 | -123.1796
2004.9219 | 122.8592 | -118.3868 | 4.3488 | -0.74356 | 0.0019482 | 0.0060178 | 0.023554 | -0.0073208 | -0.00071986 | 0.0017027 | -118.4006 | 4.3579 | -118.7714 | 4.1931 | 3.8727 | -10.3226 | -11.2152 | -11.2564 | 4.3671 | -118.7668 | -0.38452 | 0.009155 | -0.013733 | 122.58 | -0.47607 | -0.37994 | 0.01831 | 0.37079 | 107.1716 | 107.1304 | 122.2595 | 122.7448 | -0.013733 | 122.7539 | 108.0643 | -0.37994 | 122.7448 | -0.013733 | 108.0643 | 122.2595 | 122.7539 | -123.1201 | -123.1155
2005.9531 | 122.9736 | -118.0893 | 4.6188 | 0.15671 | 0.0025892 | 0.0023862 | 0.021204 | -0.004971 | -0.0039243 | 0.0034115 | -117.897 | 4.5456 | -118.4326 | 4.6051 | 4.2892 | -8.1024 | -11.6318 | -11.0229 | 4.6417 | -118.4143 | -0.34332 | -0.073242 | 0.19226 | 122.6944 | -0.32959 | -0.32501 | 0.022889 | 0.53558 | 106.4575 | 107.0663 | 122.3785 | 122.6349 | 0.19226 | 122.731 | 109.9869 | -0.32501 | 122.6349 | 0.19226 | 109.9869 | 122.3785 | 122.731 | -123.0515 | -123.0331
2006.9062 | 122.9416 | -118.4463 | 4.2664 | 0.11093 | 0.0013074 | 0.0075132 | 0.017359 | -0.00668 | -0.00093346 | 0.0023435 | -118.2587 | 4.2526 | -118.7073 | 4.2297 | 3.7949 | -8.0933 | -11.3846 | -11.0733 | 4.2984 | -118.7576 | -0.26093 | -0.013732 | 0.18768 | 122.6761 | -0.4715 | -0.31128 | 0.032044 | 0.44861 | 107.0618 | 107.373 | 122.2412 | 122.699 | 0.18768 | 122.7448 | 110.3531 | -0.31128 | 122.699 | 0.18768 | 110.3531 | 122.2412 | 122.7448 | -122.9736 | -123.024
2007.9531 | 122.9095 | -118.6066 | 4.097 | 0.24826 | 0.0019482 | 0.0011044 | 0.024195 | -0.0041166 | -0.00050626 | 0.0025571 | -118.4647 | 4.0375 | -119.0002 | 3.9688 | 3.6987 | -9.1965 | -11.2564 | -11.1557 | 4.1153 | -118.9728 | -0.39368 | -0.059509 | 0.14191 | 122.5754 | -0.39826 | -0.36621 | 0.01831 | 0.53558 | 107.3502 | 107.4509 | 122.3053 | 122.644 | 0.14191 | 122.7219 | 109.4101 | -0.36621 | 122.644 | 0.14191 | 109.4101 | 122.3053 | 122.7219 | -123.0972 | -123.0698
2008.9062 | 122.9782 | -117.9108 | 4.8386 | -1.8498 | -0.00082884 | 0.0015316 | 0.014155 | -0.0043302 | -0.0011471 | 0.0019163 | -117.659 | 4.7195 | -118.2266 | 4.8294 | 4.5547 | -6.9214 | -10.9451 | -10.8902 | 4.8294 | -118.1992 | -0.31586 | -0.11902 | 0.25177 | 122.7402 | -0.28381 | -0.28839 | -0.009155 | 0.56763 | 106.9656 | 107.0206 | 122.4655 | 122.6303 | 0.25177 | 122.7402 | 110.9894 | -0.28839 | 122.6303 | 0.25177 | 110.9894 | 122.4655 | 122.7402 | -123.0652 | -123.0377
2009.9688 | 122.85 | -118.3273 | 4.5227 | -0.18662 | 2.5564e-05 | 0.003027 | 0.018854 | -0.00668 | -0.0015745 | 0.0046933 | -118.0984 | 4.4495 | -118.5883 | 4.3396 | 4.0741 | -7.5943 | -10.6155 | -11.087 | 4.5593 | -118.6295 | -0.26093 | -0.073242 | 0.22888 | 122.6669 | -0.44861 | -0.30212 | 0.036621 | 0.48981 | 107.7118 | 107.2403 | 122.4014 | 122.7768 | 0.22888 | 122.8867 | 110.733 | -0.30212 | 122.7768 | 0.22888 | 110.733 | 122.4014 | 122.8867 | -123.111 | -123.1522
2010.9062 | 122.9507 | -117.5583 | 5.159 | 0.0041197 | -0.00082884 | 0.0025998 | 0.014155 | -0.0056118 | -0.00050626 | 0.0044797 | -117.453 | 5.0491 | -117.9474 | 5.0812 | 4.7836 | -7.7454 | -10.3134 | -10.9177 | 5.1636 | -117.9153 | -0.3891 | -0.10986 | 0.10529 | 122.6395 | -0.37537 | -0.35706 | 0.004577 | 0.49439 | 107.2449 | 106.6406 | 122.3419 | 122.6074 | 0.10529 | 122.7219 | 109.8129 | -0.35706 | 122.6074 | 0.10529 | 109.8129 | 122.3419 | 122.7219 | -123.1064 | -123.0743
2011.9062 | 122.9874 | -116.2766 | 6.34 | -0.072174 | 0.00045296 | 0.0017454 | 0.015436 | -0.0068936 | -0.0020017 | 0.0038389 | -116.1484 | 6.2622 | -116.6611 | 6.3629 | 6.0425 | -7.9559 | -10.112 | -10.6567 | 6.3812 | -116.6611 | -0.38452 | -0.07782 | 0.12817 | 122.6395 | -0.29755 | -0.38452 | 0.041199 | 0.5127 | 106.1646 | 105.6198 | 122.319 | 122.5388 | 0.12817 | 122.6578 | 108.3206 | -0.38452 | 122.5388 | 0.12817 | 108.3206 | 122.319 | 122.6578 | -123.0011 | -123.0011
2012.9062 | 122.9416 | -117.8513 | 4.747 | 0.072784 | -0.0010424 | 0.006445 | 0.016504 | -0.0068936 | 0.00013454 | 0.0049069 | -117.7734 | 4.7241 | -118.2678 | 4.7104 | 4.303 | -6.6422 | -10.231 | -10.8078 | 4.7562 | -118.2953 | -0.41656 | -0.022888 | 0.07782 | 122.5616 | -0.44403 | -0.44403 | 0.009156 | 0.49438 | 107.6202 | 107.0435 | 122.1542 | 122.5754 | 0.07782 | 122.6074 | 111.2091 | -0.44403 | 122.5754 | 0.07782 | 111.2091 | 122.1542 | 122.6074 | -123.0148 | -123.0423
2013.9062 | 122.9691 | -118.2907 | 4.4312 | 0.0041197 | 0.00066656 | 0.0025998 | 0.015436 | -0.0064664 | -0.0015745 | 0.0055479 | -118.1992 | 4.3304 | -118.6523 | 4.3396 | 4.0833 | -6.3538 | -10.0067 | -10.7941 | 4.4357 | -118.6386 | -0.36163 | -0.10071 | 0.091552 | 122.6303 | -0.3479 | -0.3479 | 0.004578 | 0.45319 | 108.284 | 107.4966 | 122.374 | 122.6212 | 0.091552 | 122.7264 | 111.937 | -0.3479 | 122.6212 | 0.091552 | 111.937 | 122.374 | 122.7264 | -123.0835 | -123.0698
2014.9062 | 122.85 | -113.5849 | 9.1232 | -0.3392 | 0.0013074 | 0.001318 | 0.019282 | -0.0079618 | -0.00093346 | 0.0042661 | -113.3652 | 9.137 | -113.8367 | 8.9447 | 8.6288 | -5.4428 | -9.3567 | -10.199 | 9.1599 | -113.9465 | -0.25177 | 0.013733 | 0.21973 | 122.5296 | -0.49438 | -0.36163 | 0.036621 | 0.4715 | 104.2282 | 103.3859 | 122.2137 | 122.7219 | 0.21973 | 122.7448 | 108.1421 | -0.36163 | 122.7219 | 0.21973 | 108.1421 | 122.2137 | 122.7448 | -122.9599 | -123.0698
2015.9219 | 122.905 | -117.0319 | 5.6763 | -0.16373 | 0.0019482 | 0.0062314 | 0.023768 | -0.0051846 | -0.0024289 | 0.0027707 | -116.8716 | 5.6168 | -117.4072 | 5.5893 | 5.2597 | -6.9077 | -10.0708 | -10.968 | 5.69 | -117.4622 | -0.37537 | -0.05951 | 0.16022 | 122.6212 | -0.41656 | -0.4303 | 0.013732 | 0.53558 | 106.9611 | 106.0638 | 122.2916 | 122.6486 | 0.16022 | 122.7219 | 110.1242 | -0.4303 | 122.6486 | 0.16022 | 110.1242 | 122.2916 | 122.7219 | -123.0835 | -123.1384
2016.9062 | 122.9782 | -117.6773 | 5.0446 | -0.78934 | 0.0028028 | 0.0087948 | 0.018641 | -0.0036892 | -0.0039243 | 0.0042661 | -117.6819 | 4.9667 | -118.0206 | 5.0171 | 4.747 | -6.7703 | -10.675 | -10.9451 | 5.0537 | -117.9794 | -0.34332 | -0.07782 | -0.004578 | 122.6944 | -0.29755 | -0.30212 | 0.009155 | 0.33875 | 107.0023 | 106.7322 | 122.4243 | 122.644 | -0.004578 | 122.731 | 110.907 | -0.30212 | 122.644 | -0.004578 | 110.907 | 122.4243 | 122.731 | -123.0652 | -123.024
2017.9531 | 122.9645 | -116.6199 | 6.0516 | -0.011139 | -0.00040164 | 0.001318 | 0.013941 | -0.0047574 | -0.00093346 | 0.0057615 | -116.5192 | 5.9647 | -117.0044 | 6.0059 | 5.7129 | -6.1569 | -10.5469 | -10.881 | 6.0745 | -116.9724 | -0.38452 | -0.086975 | 0.10071 | 122.6257 | -0.33875 | -0.35248 | 0.022888 | 0.48523 | 106.073 | 105.7388 | 122.3328 | 122.5845 | 0.10071 | 122.6944 | 110.463 | -0.35248 | 122.5845 | 0.10071 | 110.463 | 122.3328 | 122.6944 | -123.056 | -123.024
2018.9062 | 122.9507 | -116.6702 | 6.0974 | -0.034027 | -0.0014696 | 0.0043088 | 0.015864 | -0.00668 | -0.0043515 | 0.0040525 | -116.51 | 6.0059 | -116.9861 | 6.0425 | 5.722 | -6.0974 | -10.4874 | -10.8994 | 6.0974 | -116.9449 | -0.31586 | -0.091553 | 0.16022 | 122.7127 | -0.37537 | -0.27466 | 0 | 0.47607 | 106.1829 | 105.7709 | 122.3923 | 122.6761 | 0.16022 | 122.7676 | 110.5728 | -0.27466 | 122.6761 | 0.16022 | 110.5728 | 122.3923 | 122.7676 | -123.0835 | -123.0423
2019.9688 | 122.9324 | -118.2953 | 4.4357 | 0.065155 | 0.0025892 | 0.0058042 | 0.017786 | -0.0073208 | -0.00050626 | 0.0059751 | -118.1442 | 4.3533 | -118.6111 | 4.3488 | 4.0649 | -6.1935 | -10.8719 | -11.1694 | 4.4495 | -118.6249 | -0.31586 | -0.082397 | 0.15106 | 122.644 | -0.37079 | -0.32959 | 0.013733 | 0.46692 | 107.4234 | 107.1259 | 122.3602 | 122.6486 | 0.15106 | 122.7448 | 112.1017 | -0.32959 | 122.6486 | 0.15106 | 112.1017 | 122.3602 | 122.7448 | -123.0469 | -123.0606
2020.9062 | 122.8821 | -117.6865 | 5.1086 | -0.19424 | 0.0025892 | 0.0066586 | 0.022913 | -0.0030484 | -0.00093346 | 0.0034115 | -117.5171 | 5.0217 | -118.0206 | 4.9393 | 4.628 | -5.9326 | -10.8261 | -11.3251 | 5.1361 | -118.0252 | -0.33417 | -0.086976 | 0.16937 | 122.6257 | -0.48065 | -0.33875 | 0.027465 | 0.50354 | 106.8604 | 106.3614 | 122.3145 | 122.7081 | 0.16937 | 122.8226 | 111.7538 | -0.33875 | 122.7081 | 0.16937 | 111.7538 | 122.3145 | 122.8226 | -123.1293 | -123.1339
2021.9688 | 122.9874 | -117.1783 | 5.5618 | 0.11856 | 0.0010938 | 0.004736 | 0.017786 | -0.0036892 | -0.00093346 | 0.0023435 | -116.9998 | 5.4428 | -117.5354 | 5.5252 | 5.2002 | -5.6168 | -10.9222 | -11.0184 | 5.5573 | -117.4301 | -0.35706 | -0.11902 | 0.17853 | 122.7036 | -0.36163 | -0.25177 | -0.004578 | 0.53558 | 106.2561 | 106.16 | 122.3785 | 122.6212 | 0.17853 | 122.7356 | 111.5616 | -0.25177 | 122.6212 | 0.17853 | 111.5616 | 122.3785 | 122.7356 | -123.0972 | -122.9919
2022.9062 | 122.9828 | -117.8421 | 4.8477 | -0.2858 | -0.0014696 | 0.001959 | 0.015864 | -0.0075344 | -0.0049923 | 0.0027707 | -117.6682 | 4.7607 | -118.222 | 4.8203 | 4.5364 | -5.5756 | -10.9634 | -11.2656 | 4.8706 | -118.1946 | -0.37994 | -0.086975 | 0.17395 | 122.6624 | -0.31128 | -0.35248 | 0.022888 | 0.55389 | 106.8787 | 106.5765 | 122.3785 | 122.6028 | 0.17395 | 122.7127 | 112.2665 | -0.35248 | 122.6028 | 0.17395 | 112.2665 | 122.3785 | 122.7127 | -123.0698 | -123.0423
2023.9688 | 122.9874 | -118.5471 | 4.1611 | -0.079803 | -0.00018804 | 0.0034544 | 0.014795 | -0.0068936 | -0.00093346 | 0.0034115 | -118.4006 | 4.097 | -118.8583 | 4.1061 | 3.8544 | -5.7587 | -10.968 | -11.3159 | 4.1794 | -118.8858 | -0.31128 | -0.064087 | 0.14648 | 122.6532 | -0.3067 | -0.33874 | 0.01831 | 0.45776 | 107.579 | 107.2311 | 122.4014 | 122.644 | 0.14648 | 122.7264 | 112.7884 | -0.33874 | 122.644 | 0.14648 | 112.7884 | 122.4014 | 122.7264 | -123.0194 | -123.0469
2024.9062 | 122.8821 | -118.5013 | 4.2801 | -0.14847 | 0.0047254 | 0.0066586 | 0.026545 | -0.0043302 | -0.0041379 | 0.0023435 | -118.2678 | 4.2664 | -118.808 | 4.184 | 3.891 | -5.9647 | -10.9817 | -11.6913 | 4.2938 | -118.8492 | -0.3067 | -0.013733 | 0.23346 | 122.6852 | -0.3891 | -0.3479 | 0.013733 | 0.54016 | 107.5195 | 106.81 | 122.3923 | 122.7676 | 0.23346 | 122.7951 | 112.5366 | -0.3479 | 122.7676 | 0.23346 | 112.5366 | 122.3923 | 122.7951 | -123.0881 | -123.1293
2025.9844 | 123.5184 | -13.4354 | 82.933 | 0.072784 | 0.0055798 | 0.0017454 | 0.015223 | -0.003262 | -0.0011471 | 0.024987 | -12.8448 | 109.996 | -13.0417 | 110.3027 | 107.872 | 7.5485 | 5.9372 | 5.7175 | 109.6756 | -13.2797 | 0.39368 | 27.063 | 0.59051 | 123.7381 | 24.939 | 0.15564 | 26.7426 | 0.19684 | 19.3726 | 19.1528 | 121.3074 | 123.4314 | 0.59051 | 123.111 | 20.9839 | 0.15564 | 123.4314 | 0.59051 | 20.9839 | 121.3074 | 123.111 | -95.9747 | -96.2128
2026.9062 | 122.8592 | -117.9108 | 4.8706 | -0.25528 | 2.5564e-05 | 0.0051632 | 0.018 | -0.0030484 | -0.00050626 | 0.0049069 | -117.7322 | 4.7791 | -118.2678 | 4.7333 | 4.454 | -5.658 | -10.8353 | -11.4441 | 4.8981 | -118.2266 | -0.35705 | -0.091552 | 0.17853 | 122.644 | -0.41656 | -0.31586 | 0.027466 | 0.53558 | 107.0755 | 106.4667 | 122.3648 | 122.6898 | 0.17853 | 122.8088 | 112.2528 | -0.31586 | 122.6898 | 0.17853 | 112.2528 | 122.3648 | 122.8088 | -123.1384 | -123.0972
2027.9531 | 122.9324 | -117.4484 | 5.2597 | -0.049286 | -0.00082884 | 0.003668 | 0.014795 | -0.0041166 | -0.0017881 | 0.0057615 | -117.3523 | 5.1498 | -117.8513 | 5.1727 | 4.8935 | -5.571 | -11.2564 | -11.4944 | 5.2643 | -117.7872 | -0.40283 | -0.10986 | 0.09613 | 122.6212 | -0.36621 | -0.33875 | 0.004577 | 0.49896 | 106.192 | 105.954 | 122.3419 | 122.5983 | 0.09613 | 122.7127 | 111.8774 | -0.33875 | 122.5983 | 0.09613 | 111.8774 | 122.3419 | 122.7127 | -123.111 | -123.0469
2028.9062 | 122.9416 | -118.3868 | 4.39 | -0.14847 | 0.0013074 | 0.0023862 | 0.017573 | -0.0064664 | -0.0022153 | 0.0044797 | -118.158 | 4.303 | -118.6935 | 4.3442 | 4.0787 | -5.484 | -11.3937 | -11.4441 | 4.39 | -118.6707 | -0.3067 | -0.086975 | 0.22888 | 122.731 | -0.31128 | -0.28381 | 0 | 0.53558 | 106.9931 | 106.9427 | 122.4655 | 122.6898 | 0.22888 | 122.7768 | 112.9028 | -0.28381 | 122.6898 | 0.22888 | 112.9028 | 122.4655 | 122.7768 | -123.0835 | -123.0606
2029.9531 | 122.9691 | -118.1168 | 4.6555 | -0.087433 | -0.0010424 | 0.001959 | 0.014582 | -0.0064664 | -0.00071986 | 0.0023435 | -117.9062 | 4.5593 | -118.4189 | 4.5959 | 4.3533 | -5.3925 | -11.1832 | -11.3434 | 4.6555 | -118.4006 | -0.30212 | -0.096131 | 0.21057 | 122.7127 | -0.30212 | -0.28381 | 0 | 0.5127 | 106.9336 | 106.7734 | 122.4701 | 122.6761 | 0.21057 | 122.7722 | 112.7243 | -0.28381 | 122.6761 | 0.21057 | 112.7243 | 122.4701 | 122.7722 | -123.0743 | -123.056
2030.9062 | 122.8363 | -118.5242 | 4.2801 | 3.2161 | 0.0036572 | 0.0096494 | 0.02569 | -0.0051846 | -0.0032835 | 0.0044797 | -118.2678 | 4.2206 | -118.8583 | 4.0741 | 3.8223 | -5.6168 | -10.9314 | -11.7096 | 4.3213 | -118.8629 | -0.33417 | -0.059509 | 0.25635 | 122.5983 | -0.45776 | -0.33875 | 0.041199 | 0.59052 | 107.5928 | 106.8146 | 122.3465 | 122.7448 | 0.25635 | 122.8455 | 112.9074 | -0.33875 | 122.7448 | 0.25635 | 112.9074 | 122.3465 | 122.8455 | -123.1384 | -123.143
2031.9688 | 122.9736 | -117.7734 | 4.9438 | -3.5359 | 0.00023916 | 0.0034544 | 0.014368 | -0.003262 | 0.00034814 | 0.0040525 | -117.572 | 4.8477 | -118.1168 | 4.9072 | 4.6463 | -5.3467 | -10.8261 | -11.3663 | 4.9484 | -118.103 | -0.34332 | -0.096131 | 0.20142 | 122.6807 | -0.29755 | -0.32959 | 0.004577 | 0.54474 | 106.9473 | 106.4072 | 122.4197 | 122.6212 | 0.20142 | 122.7219 | 112.4268 | -0.32959 | 122.6212 | 0.20142 | 112.4268 | 122.4197 | 122.7219 | -123.0606 | -123.0469
2032.9062 | 122.9507 | -118.3319 | 4.4266 | -0.1561 | 0.00066656 | 0.0015316 | 0.015009 | -0.0043302 | 0.00013454 | 0.0044797 | -118.1213 | 4.3076 | -118.6478 | 4.3625 | 4.1061 | -5.3925 | -11.0367 | -11.3434 | 4.4174 | -118.6707 | -0.31586 | -0.11902 | 0.21057 | 122.6944 | -0.32043 | -0.33875 | -0.009156 | 0.52643 | 107.2952 | 106.9885 | 122.438 | 122.6395 | 0.21057 | 122.7493 | 112.9395 | -0.33875 | 122.6395 | 0.21057 | 112.9395 | 122.438 | 122.7493 | -123.0743 | -123.0972
2033.9688 | 122.9553 | -117.3798 | 5.2826 | -0.087433 | 0.002162 | 0.001959 | 0.014582 | -0.0077482 | 0.0018435 | 0.0019163 | -117.247 | 5.2139 | -117.746 | 5.2734 | 4.9805 | -5.1727 | -11.1832 | -10.9817 | 5.2917 | -117.746 | -0.36621 | -0.068665 | 0.13275 | 122.6532 | -0.30212 | -0.36621 | 0.009155 | 0.49896 | 106.1966 | 106.398 | 122.3602 | 122.5937 | 0.13275 | 122.6715 | 112.207 | -0.36621 | 122.5937 | 0.13275 | 112.207 | 122.3602 | 122.6715 | -123.0286 | -123.0286
2034.9062 | 122.85 | -115.4114 | 7.3563 | -0.26291 | 0.0017346 | 0.003668 | 0.019282 | -0.0051846 | -0.00093346 | 0.0025571 | -115.3061 | 7.2647 | -115.8051 | 7.3425 | 7.1182 | -4.8386 | -10.7025 | -10.9085 | 7.3929 | -115.773 | -0.39368 | -0.091553 | 0.10529 | 122.7539 | -0.23804 | -0.36163 | 0.036621 | 0.49896 | 104.7089 | 104.5029 | 122.5296 | 122.6761 | 0.10529 | 122.8043 | 110.5728 | -0.36163 | 122.6761 | 0.10529 | 110.5728 | 122.5296 | 122.8043 | -123.1613 | -123.1293
2035.9531 | 122.8592 | -115.9744 | 6.8298 | -0.16373 | 2.5564e-05 | 0.0025998 | 0.021845 | -0.003903 | -0.0015745 | 0.0027707 | -115.8234 | 6.7474 | -116.3177 | 6.6971 | 6.3538 | -5.0125 | -10.5515 | -10.9406 | 6.8481 | -116.2903 | -0.34332 | -0.082397 | 0.15106 | 122.6715 | -0.47607 | -0.31586 | 0.018311 | 0.49439 | 105.423 | 105.0339 | 122.3282 | 122.7219 | 0.15106 | 122.8226 | 110.9619 | -0.31586 | 122.7219 | 0.15106 | 110.9619 | 122.3282 | 122.8226 | -123.1476 | -123.1201
2036.9062 | 122.905 | -116.7435 | 6.0974 | -0.21713 | 0.0019482 | 0.0028134 | 0.01565 | -0.0024076 | -0.0030697 | 0.0040525 | -116.6199 | 5.9509 | -117.0868 | 5.8685 | 5.5664 | -4.9805 | -10.7117 | -11.1694 | 6.0608 | -117.0914 | -0.34332 | -0.14648 | 0.1236 | 122.612 | -0.53101 | -0.3479 | -0.036621 | 0.46692 | 106.0318 | 105.574 | 122.3099 | 122.6944 | 0.1236 | 122.8043 | 111.763 | -0.3479 | 122.6944 | 0.1236 | 111.763 | 122.3099 | 122.8043 | -123.1842 | -123.1888
2037.9531 | 122.8638 | -115.8737 | 6.9626 | -0.29343 | 0.00088016 | 0.0021726 | 0.016504 | -0.0047574 | -0.0013609 | 0.0051205 | -115.7089 | 6.8344 | -116.1896 | 6.7886 | 6.4545 | -4.8203 | -10.6384 | -10.8856 | 6.9763 | -116.1575 | -0.31586 | -0.12817 | 0.16479 | 122.6624 | -0.50812 | -0.28381 | 0.013733 | 0.48065 | 105.2353 | 104.9881 | 122.3282 | 122.7081 | 0.16479 | 122.85 | 111.0535 | -0.28381 | 122.7081 | 0.16479 | 111.0535 | 122.3282 | 122.85 | -123.1522 | -123.1201
2038.9062 | 122.8546 | -116.6656 | 6.1432 | -0.17899 | -0.00040164 | 0.0038816 | 0.018854 | -0.0051846 | -0.0039243 | 0.0017027 | -116.5237 | 6.0425 | -116.9998 | 5.9647 | 5.6534 | -5.0903 | -10.7574 | -11.3342 | 6.134 | -116.9952 | -0.33417 | -0.10071 | 0.14191 | 122.6303 | -0.48981 | -0.32959 | -0.009155 | 0.47607 | 105.9082 | 105.3314 | 122.319 | 122.7081 | 0.14191 | 122.7997 | 111.5753 | -0.32959 | 122.7081 | 0.14191 | 111.5753 | 122.319 | 122.7997 | -123.143 | -123.1384
2039.9531 | 122.8271 | -117.7551 | 4.9896 | -0.16373 | 0.0030164 | 0.0075132 | 0.016504 | -0.0056118 | -0.0026425 | 0.0036253 | -117.6407 | 4.9072 | -118.1442 | 4.8019 | 4.5456 | -5.3329 | -10.8444 | -11.4716 | 4.9942 | -118.1625 | -0.3891 | -0.082397 | 0.11444 | 122.5571 | -0.44403 | -0.40741 | 0.004578 | 0.50354 | 106.9107 | 106.2836 | 122.3007 | 122.6624 | 0.11444 | 122.7493 | 112.4222 | -0.40741 | 122.6624 | 0.11444 | 112.4222 | 122.3007 | 122.7493 | -123.1339 | -123.1522
2040.9062 | 122.8729 | -117.8146 | 4.9164 | -0.20187 | 0.0013074 | 0.005377 | 0.017145 | -0.0073208 | -0.00093346 | 0.0017027 | -117.7231 | 4.8614 | -118.1671 | 4.7379 | 4.4769 | -5.4153 | -10.8215 | -11.5356 | 4.9622 | -118.19 | -0.35248 | -0.054932 | 0.091553 | 122.5525 | -0.43945 | -0.37537 | 0.045776 | 0.44403 | 106.9931 | 106.279 | 122.2916 | 122.6761 | 0.091553 | 122.7768 | 112.3993 | -0.37537 | 122.6761 | 0.091553 | 112.3993 | 122.2916 | 122.7768 | -123.0835 | -123.1064
2041.9531 | 123.0057 | -118.6935 | 4.0329 | -0.1561 | -0.0014696 | 0.0055906 | 0.016077 | -0.0081754 | -0.0045651 | 0.0042661 | -118.4463 | 3.978 | -119.0186 | 3.8635 | 3.5477 | -5.3421 | -11.0825 | -11.6776 | 4.0787 | -119.0048 | -0.32501 | -0.054932 | 0.24719 | 122.5571 | -0.48523 | -0.31128 | 0.045776 | 0.57221 | 107.6111 | 107.016 | 122.2412 | 122.6715 | 0.24719 | 122.7722 | 113.3514 | -0.31128 | 122.6715 | 0.24719 | 113.3514 | 122.2412 | 122.7722 | -123.0515 | -123.0377
2042.9062 | 122.8455 | -114.5416 | 8.1711 | -0.21713 | 0.002162 | 0.003668 | 0.02035 | -0.00668 | -0.0015745 | 0.0014889 | -114.1159 | 8.3405 | -114.7156 | 8.0292 | 7.6309 | -4.9896 | -10.4141 | -11.0275 | 8.2031 | -114.9353 | -0.17395 | 0.16937 | 0.42572 | 122.5708 | -0.54016 | -0.39368 | 0.032043 | 0.59967 | 104.1275 | 103.5141 | 122.1725 | 122.8821 | 0.42572 | 122.7448 | 109.552 | -0.39368 | 122.8821 | 0.42572 | 109.552 | 122.1725 | 122.7448 | -122.8867 | -123.1064
2043.9531 | 122.8455 | -119.0048 | 3.8269 | -0.21713 | 0.0034436 | 0.0017454 | 0.018854 | -0.003262 | -0.0022153 | 0.0064023 | -118.8583 | 3.7079 | -119.3069 | 3.6667 | 3.4058 | -5.2734 | -11.3571 | -11.879 | 3.8498 | -119.3253 | -0.30212 | -0.11902 | 0.14648 | 122.6715 | -0.42114 | -0.32043 | 0.022888 | 0.44861 | 107.6477 | 107.1259 | 122.4106 | 122.7127 | 0.14648 | 122.8546 | 113.7314 | -0.32043 | 122.7127 | 0.14648 | 113.7314 | 122.4106 | 122.8546 | -123.1338 | -123.1522
2044.9062 | 122.8729 | -119.0689 | 3.7811 | -0.26291 | 0.0030164 | 0.0043088 | 0.019922 | -0.0075344 | -0.0022153 | 0.0040525 | -118.8812 | 3.6896 | -119.3665 | 3.4515 | 3.1952 | -5.1498 | -11.6501 | -12.0712 | 3.8132 | -119.3527 | -0.29755 | -0.091553 | 0.18768 | 122.5204 | -0.58594 | -0.28381 | 0.032043 | 0.48523 | 107.4188 | 106.9977 | 122.2641 | 122.7585 | 0.18768 | 122.8821 | 113.9191 | -0.28381 | 122.7585 | 0.18768 | 113.9191 | 122.2641 | 122.8821 | -123.1476 | -123.1338
2045.9062 | 122.8683 | -117.4438 | 5.3833 | -0.17136 | 0.0028028 | 0.004736 | 0.021204 | -0.0043302 | -0.0011471 | 0.0038389 | -117.2424 | 5.3009 | -117.7643 | 5.2231 | 4.9347 | -5.0446 | -11.6226 | -11.8378 | 5.397 | -117.746 | -0.32043 | -0.082398 | 0.20142 | 122.6669 | -0.44861 | -0.30212 | 0.013733 | 0.52185 | 105.8212 | 105.6061 | 122.3785 | 122.7448 | 0.20142 | 122.8409 | 112.3993 | -0.30212 | 122.7448 | 0.20142 | 112.3993 | 122.3785 | 122.8409 | -123.1476 | -123.1293
2046.9062 | 122.8775 | -119.2657 | 3.5339 | -0.30106 | 0.00323 | 0.0072996 | 0.01565 | -0.0030484 | -0.00093346 | 0.0051205 | -119.0872 | 3.4332 | -119.5953 | 3.3829 | 3.154 | -5.3925 | -12.085 | -12.1719 | 3.5431 | -119.5999 | -0.32959 | -0.10071 | 0.17853 | 122.6486 | -0.37994 | -0.33417 | 0.009155 | 0.50812 | 107.1808 | 107.0938 | 122.4197 | 122.699 | 0.17853 | 122.8088 | 113.8733 | -0.33417 | 122.699 | 0.17853 | 113.8733 | 122.4197 | 122.8088 | -123.1293 | -123.1339
2047.9062 | 122.8683 | -117.7872 | 5.0629 | -0.20187 | 0.0023756 | 0.0011044 | 0.018641 | -0.0053982 | -0.0020017 | 0.0031979 | -117.6727 | 4.9301 | -118.158 | 4.8386 | 4.5364 | -5.658 | -11.087 | -12.0575 | 5.0766 | -118.0939 | -0.37079 | -0.13275 | 0.11444 | 122.6257 | -0.52643 | -0.3067 | 0.013733 | 0.48523 | 106.7001 | 105.7297 | 122.3236 | 122.7173 | 0.11444 | 122.8638 | 112.1292 | -0.3067 | 122.7173 | 0.11444 | 112.1292 | 122.3236 | 122.8638 | -123.2208 | -123.1567
2048.9062 | 122.8729 | -116.9083 | 5.8594 | -0.19424 | 0.0019482 | 0.00067718 | 0.017573 | -0.0034756 | -0.0030697 | 0.0017027 | -116.7801 | 5.7632 | -117.2928 | 5.6808 | 5.3879 | -5.8594 | -11.4624 | -11.8286 | 5.896 | -117.2287 | -0.38452 | -0.09613 | 0.12817 | 122.5891 | -0.4715 | -0.32044 | 0.036621 | 0.5127 | 105.4459 | 105.0797 | 122.2961 | 122.6715 | 0.12817 | 122.8043 | 111.0489 | -0.32044 | 122.6715 | 0.12817 | 111.0489 | 122.2961 | 122.8043 | -123.1522 | -123.0881
2049.9688 | 122.8409 | -117.9245 | 4.9118 | -0.27817 | 0.0036572 | 0.003027 | 0.016291 | -0.0047574 | 0.00013454 | 0.0038389 | -117.746 | 4.8111 | -118.2312 | 4.715 | 4.4952 | -5.1956 | -11.705 | -11.8286 | 4.9347 | -118.2404 | -0.3067 | -0.10071 | 0.17853 | 122.6395 | -0.41657 | -0.31586 | 0.022888 | 0.48523 | 106.2195 | 106.0959 | 122.4197 | 122.7356 | 0.17853 | 122.8592 | 112.7289 | -0.31586 | 122.7356 | 0.17853 | 112.7289 | 122.4197 | 122.8592 | -123.143 | -123.1522
2050.9062 | 122.8775 | -117.2928 | 5.5298 | -0.24002 | 0.0028028 | 0.0023862 | 0.019922 | -0.0026212 | -0.0024289 | 0.0027707 | -117.1234 | 5.452 | -117.6224 | 5.3467 | 5.0583 | -5.1498 | -11.5677 | -12.0346 | 5.5481 | -117.6086 | -0.32959 | -0.07782 | 0.16937 | 122.6395 | -0.4715 | -0.31586 | 0.018311 | 0.49896 | 105.7251 | 105.2582 | 122.3511 | 122.7448 | 0.16937 | 122.8409 | 112.1429 | -0.31586 | 122.7448 | 0.16937 | 112.1429 | 122.3511 | 122.8409 | -123.1522 | -123.1384
2051.9688 | 122.8546 | -117.215 | 5.6534 | -0.24765 | 0.0013074 | 0.0021726 | 0.016718 | -0.0056118 | -0.0026425 | 0.0038389 | -117.0502 | 5.5344 | -117.54 | 5.4199 | 5.0446 | -5.1224 | -11.1694 | -12.0804 | 5.6854 | -117.4805 | -0.32501 | -0.11902 | 0.16479 | 122.6349 | -0.60883 | -0.2655 | 0.032044 | 0.48981 | 106.0455 | 105.1346 | 122.2595 | 122.7493 | 0.16479 | 122.9004 | 112.0926 | -0.2655 | 122.7493 | 0.16479 | 112.0926 | 122.2595 | 122.9004 | -123.1934 | -123.1338
2052.9062 | 122.85 | -115.7318 | 6.9992 | 0.21774 | 0.0010938 | 0.0075132 | 0.018854 | -0.0045438 | -0.00093346 | 0.0036253 | -115.654 | 6.958 | -116.1072 | 6.8481 | 6.514 | -4.9667 | -11.1694 | -11.705 | 7.0175 | -116.1392 | -0.37537 | -0.041199 | 0.07782 | 122.58 | -0.48523 | -0.40741 | 0.01831 | 0.45319 | 104.5624 | 104.0268 | 122.2458 | 122.6898 | 0.07782 | 122.7493 | 110.7651 | -0.40741 | 122.6898 | 0.07782 | 110.7651 | 122.2458 | 122.7493 | -123.1064 | -123.1384
2053.9531 | 122.9599 | -109.1309 | 13.3301 | -0.17136 | 0.0023756 | 0.003027 | 0.0086005 | -0.0058256 | 0.0041933 | 0.0051205 | -112.8433 | 9.6817 | -109.5657 | 22.5357 | 15.2344 | -5.2185 | -12.3734 | -11.9751 | 16.1362 | -108.8196 | -0.43488 | -3.6484 | -3.7125 | 131.6666 | 1.9043 | 0.31128 | 2.8061 | -3.2776 | 96.7575 | 97.1558 | 124.3652 | 118.8126 | -3.7125 | 125.267 | 103.9124 | 0.31128 | 118.8126 | -3.7125 | 103.9124 | 124.3652 | 125.267 | -122.8958 | -122.1497
2054.9062 | 123.1796 | -102.1362 | 20.8054 | 0.034637 | 0.0047254 | 0.0023862 | 0.016718 | -0.0047574 | -0.0013609 | 0.0042661 | -96.4966 | 25.4654 | -97.7554 | 25.1312 | 24.147 | -2.9388 | -8.0841 | -8.3405 | 24.9481 | -98.3093 | 4.3808 | 4.66 | 5.6396 | 127.2675 | 3.3417 | 3.8269 | 4.1428 | 1.2588 | 94.0521 | 93.7958 | 126.2833 | 127.6016 | 5.6396 | 127.0844 | 99.1974 | 3.8269 | 127.6016 | 5.6396 | 99.1974 | 126.2833 | 127.0844 | -118.5608 | -119.1147
2055.9688 | 121.5042 | -110.17 | 13.5361 | -0.064545 | -0.0010424 | 0.0025998 | 0.013941 | -0.0028348 | -0.0017881 | 0.0040525 | -112.5 | 9.9976 | -112.9669 | 9.4711 | 9.1049 | -5.1086 | -10.7529 | -10.849 | 9.581 | -113.5941 | -2.7969 | -3.5385 | -2.33 | 119.6411 | -4.4312 | -3.4241 | -3.9551 | 0.46692 | 99.4171 | 99.321 | 119.2749 | 120.1675 | -2.33 | 119.751 | 105.0613 | -3.4241 | 120.1675 | -2.33 | 105.0613 | 119.2749 | 119.751 | -126.503 | -127.1301
2056.9062 | 122.8729 | -109.5932 | 12.973 | -0.2095 | -0.0014696 | 0.00046358 | 0.016932 | -0.0034756 | -0.0022153 | 0.0021299 | -108.8562 | 13.9664 | -109.2407 | 13.2019 | 12.6755 | -5.2963 | -10.3271 | -10.3867 | 13.2065 | -109.9823 | 0.35248 | 0.99335 | 0.737 | 122.7951 | -0.29755 | -0.3891 | 0.23346 | 0.38452 | 99.2661 | 99.2065 | 122.2687 | 123.5596 | 0.737 | 122.7997 | 104.2969 | -0.3891 | 123.5596 | 0.737 | 104.2969 | 122.2687 | 122.7997 | -122.2137 | -122.9553
2057.9688 | 122.9782 | -109.5108 | 13.06 | -0.079803 | -0.00018804 | 0.0025998 | 0.011164 | -0.0047574 | -0.0028561 | 0.0038389 | -108.9706 | 13.5452 | -109.4467 | 13.3347 | 12.886 | -6.546 | -10.3546 | -10.2219 | 13.2614 | -109.845 | 0.064087 | 0.48523 | 0.54016 | 122.8455 | -0.17395 | -0.33417 | 0.20142 | 0.47607 | 99.1562 | 99.2889 | 122.3969 | 123.056 | 0.54016 | 122.7722 | 102.9648 | -0.33417 | 123.056 | 0.54016 | 102.9648 | 122.3969 | 122.7722 | -122.5067 | -122.905
2058.9062 | 122.905 | -103.4454 | 19.1574 | -0.14847 | 0.0028028 | 0.0040952 | 0.018213 | -0.0043302 | -0.0037107 | 0.0059751 | -103.2669 | 19.3863 | -103.7521 | 19.0567 | 18.3792 | -5.5573 | -8.9584 | -9.1003 | 19.0475 | -103.9673 | -0.3067 | 0.22888 | 0.17853 | 122.5021 | -0.7782 | -0.52185 | -0.10986 | 0.48523 | 94.487 | 94.3451 | 121.8246 | 122.8317 | 0.17853 | 122.493 | 97.8882 | -0.52185 | 122.8317 | 0.17853 | 97.8882 | 121.8246 | 122.493 | -122.9095 | -123.1247
2059.9688 | 122.8546 | -104.8141 | 17.775 | 0.049896 | 0.0055798 | 0.006445 | 0.019709 | -0.003262 | -0.0022153 | 0.0044797 | -104.9469 | 17.5781 | -105.4184 | 17.4957 | 16.9006 | -5.1682 | -9.407 | -8.551 | 17.7155 | -104.0909 | -0.60425 | -0.19684 | -0.13275 | 122.3099 | -0.87433 | 0.72327 | -0.059509 | 0.4715 | 95.4071 | 96.2631 | 121.7148 | 122.3923 | -0.13275 | 122.5296 | 99.646 | 0.72327 | 122.3923 | -0.13275 | 99.646 | 121.7148 | 122.5296 | -123.1934 | -121.8658
2060.9062 | 122.8683 | -111.3373 | 11.2564 | -0.17899 | -0.00082884 | 0.0038816 | 0.0133 | -0.0045438 | -0.0017881 | 0.0031979 | -110.5316 | 12.4786 | -110.8749 | 11.38 | 10.9039 | -7.9468 | -10.5469 | -10.6705 | 11.3709 | -111.6898 | 0.46234 | 1.2222 | 0.80566 | 122.7173 | -0.35248 | -0.35248 | 0.11444 | 0.34332 | 100.7904 | 100.6668 | 122.2412 | 123.8159 | 0.80566 | 122.7081 | 103.3905 | -0.35248 | 123.8159 | 0.80566 | 103.3905 | 122.2412 | 122.7081 | -122.1313 | -122.9462
2061.9531 | 122.9599 | -112.793 | 9.8373 | -0.52231 | -0.00061524 | 0.0015316 | 0.013941 | -0.0051846 | -0.0015745 | 0.0044797 | -112.4954 | 9.9564 | -112.9944 | 9.8648 | 9.4757 | -7.6035 | -11.0779 | -10.7941 | 9.8602 | -113.1821 | -0.20142 | 0.11902 | 0.29755 | 122.6578 | -0.36163 | -0.3891 | 0.022888 | 0.49896 | 101.7151 | 101.9989 | 122.2687 | 122.7493 | 0.29755 | 122.6532 | 105.1895 | -0.3891 | 122.7493 | 0.29755 | 105.1895 | 122.2687 | 122.6532 | -122.8317 | -123.0194
2062.9062 | 122.8638 | -115.3152 | 7.37 | -0.22476 | 0.0030164 | 0.0075132 | 0.019495 | -0.0043302 | -0.0022153 | 0.0017027 | -115.2374 | 7.3288 | -115.7272 | 7.2327 | 6.9031 | -7.7133 | -11.0092 | -11.2656 | 7.4158 | -115.7272 | -0.41199 | -0.041199 | 0.07782 | 122.5479 | -0.46692 | -0.41199 | 0.045776 | 0.48981 | 104.306 | 104.0497 | 122.2183 | 122.644 | 0.07782 | 122.731 | 107.6019 | -0.41199 | 122.644 | 0.07782 | 107.6019 | 122.2183 | 122.731 | -123.0972 | -123.0972
2063.9531 | 122.8546 | -116.4551 | 6.3126 | -0.19424 | 0.002162 | 0.0021726 | 0.016718 | -0.004971 | -0.0020017 | 0.0053343 | -116.3406 | 6.1981 | -116.8304 | 6.221 | 5.9189 | -8.3176 | -11.3617 | -11.0916 | 6.3629 | -116.7892 | -0.37537 | -0.11444 | 0.11444 | 122.6761 | -0.39368 | -0.33417 | 0.050354 | 0.48981 | 105.0934 | 105.3635 | 122.374 | 122.6532 | 0.11444 | 122.818 | 108.1375 | -0.33417 | 122.6532 | 0.11444 | 108.1375 | 122.374 | 122.818 | -123.143 | -123.1018
2064.9062 | 122.8912 | -113.8641 | 8.7662 | -0.034027 | 0.0034436 | 0.0070858 | 0.024836 | -0.0017666 | -0.0022153 | 0.0034115 | -113.6536 | 8.7936 | -114.1983 | 8.7936 | 8.3679 | -14.7537 | -11.2198 | -10.7574 | 8.8531 | -114.3036 | -0.33417 | 0.027466 | 0.21057 | 122.6578 | -0.39825 | -0.43945 | 0.086975 | 0.54474 | 102.6443 | 103.1067 | 122.2321 | 122.6578 | 0.21057 | 122.7173 | 99.1104 | -0.43945 | 122.6578 | 0.21057 | 99.1104 | 122.2321 | 122.7173 | -122.9645 | -123.0698
2065.9688 | 105.0934 | -113.1638 | 9.4757 | -0.11032 | 0.0013074 | 0.001959 | 0.012018 | -0.0053982 | -0.00071986 | 0.0051205 | -112.9715 | 9.4345 | -113.5117 | 9.5032 | 9.1278 | -8.8806 | -11.1557 | -10.5835 | 9.4986 | -113.5895 | -0.3479 | -0.041199 | 0.19226 | 122.6669 | -0.3479 | -0.42572 | 0.022888 | 0.54016 | 102.0081 | 102.5803 | 122.2916 | 122.5983 | 0.19226 | 122.6624 | 104.2831 | -0.42572 | 122.5983 | 0.19226 | 104.2831 | 122.2916 | 122.6624 | -122.9874 | -123.0652
2066.9219 | 122.9965 | -71.4569 | 50.4776 | 0.095673 | 0.004939 | 0.003027 | 0.011377 | -0.0036892 | -0.0011471 | 0.0042661 | -71.3882 | 51.1093 | -71.814 | 51.6312 | 50.2533 | -1.0391 | -3.3875 | -2.623 | 51.8829 | -71.1914 | -0.35706 | 0.63171 | 0.068664 | 123.0881 | -0.2243 | 0.2655 | 1.4053 | 0.42572 | 68.0695 | 68.8339 | 121.7102 | 122.5662 | 0.068664 | 123.3398 | 70.4178 | 0.2655 | 122.5662 | 0.068664 | 70.4178 | 121.7102 | 123.3398 | -122.2916 | -121.669
2067.9531 | 122.8775 | -112.0056 | 10.6018 | 0.019379 | 0.0034436 | 0.004736 | 0.012446 | -0.0045438 | -0.00029266 | 0.0053343 | -111.9644 | 10.5469 | -112.4359 | 10.5972 | 10.1578 | -7.3837 | -11.0092 | -10.318 | 10.6476 | -112.4405 | -0.4303 | -0.054932 | 0.041198 | 122.6028 | -0.44403 | -0.43488 | 0.045776 | 0.4715 | 100.9964 | 101.6876 | 122.1634 | 122.5525 | 0.041198 | 122.6532 | 104.6219 | -0.43488 | 122.5525 | 0.041198 | 104.6219 | 122.1634 | 122.6532 | -123.0377 | -123.0423
2068.9062 | 122.8867 | -112.825 | 9.8419 | -0.2095 | 0.0010938 | 0.001318 | 0.01565 | -0.0060392 | -0.0024289 | 0.0046933 | -112.6465 | 9.8648 | -113.1683 | 9.8053 | 9.407 | -7.1365 | -11.1832 | -10.6705 | 9.8831 | -113.2233 | -0.34332 | 0.022888 | 0.17853 | 122.6303 | -0.43488 | -0.39826 | 0.041199 | 0.52185 | 101.6418 | 102.1545 | 122.2321 | 122.6898 | 0.17853 | 122.7081 | 105.6885 | -0.39826 | 122.6898 | 0.17853 | 105.6885 | 122.2321 | 122.7081 | -123.0103 | -123.0652
2069.9531 | 122.9828 | -112.5916 | 10.0433 | -0.079803 | 0.00023916 | 0.00046358 | 0.010309 | -0.0062528 | -0.0020017 | 0.0019163 | -112.532 | 9.9701 | -112.9761 | 10.1303 | 9.7549 | -6.0013 | -11.348 | -10.5972 | 10.0754 | -112.9944 | -0.38452 | -0.073242 | 0.05951 | 122.7219 | -0.28839 | -0.40283 | 0.032043 | 0.44403 | 101.2436 | 101.9943 | 122.3465 | 122.5616 | 0.05951 | 122.6669 | 106.5903 | -0.40283 | 122.5616 | 0.05951 | 106.5903 | 122.3465 | 122.6669 | -123.0194 | -123.0377
2070.9062 | 122.8455 | -115.4572 | 7.3288 | -0.20187 | 0.0036572 | 0.001318 | 0.021845 | -0.0058256 | -0.00093346 | 0.0031979 | -115.2283 | 7.3151 | -115.7501 | 7.2052 | 6.8985 | -6.427 | -11.3617 | -11.3022 | 7.37 | -115.7822 | -0.29297 | -0.013733 | 0.22888 | 122.6624 | -0.4303 | -0.32501 | 0.041199 | 0.52185 | 104.0955 | 104.155 | 122.3557 | 122.7722 | 0.22888 | 122.8271 | 109.0302 | -0.32501 | 122.7722 | 0.22888 | 109.0302 | 122.3557 | 122.8271 | -123.0789 | -123.111
2071.9531 | 122.9691 | -112.8021 | 9.7824 | -0.25528 | -0.0023242 | 0.0055906 | 0.016077 | -0.0058256 | -0.0026425 | 0.0031979 | -112.6511 | 9.8557 | -113.1226 | 9.8831 | 9.494 | -6.2622 | -10.9726 | -10.4233 | 9.8694 | -113.1775 | -0.32043 | 0.073242 | 0.15106 | 122.6852 | -0.28839 | -0.37537 | 0.086975 | 0.4715 | 101.8295 | 102.3788 | 122.2961 | 122.6578 | 0.15106 | 122.6715 | 106.5399 | -0.37537 | 122.6578 | 0.15106 | 106.5399 | 122.2961 | 122.6715 | -122.905 | -122.9599
2072.9062 | 122.818 | -67.9642 | 53.7598 | -0.23239 | 0.00023916 | 0.001959 | 0.0015509 | -0.00668 | -0.0011471 | -6.342e-06 | -65.9912 | 56.488 | -67.0212 | 53.3798 | 53.6545 | -0.64545 | -3.1311 | -2.4216 | 54.2816 | -68.5501 | 0.94299 | 2.7283 | 1.973 | 121.344 | -0.10529 | -0.58594 | 0.52185 | 1.03 | 64.8331 | 65.5426 | 121.6187 | 124.4522 | 1.973 | 122.2458 | 67.3187 | -0.58594 | 124.4522 | 1.973 | 67.3187 | 121.6187 | 122.2458 | -120.7809 | -122.3099
2073.9531 | 122.8455 | -106.2378 | 16.246 | 0.027008 | 0.0010938 | 0.001318 | 0.024408 | -0.0056118 | -0.00050626 | 0.0040525 | -109.2361 | 14.1312 | -108.4442 | 16.9327 | 16.8045 | -4.4449 | -10.0891 | -9.6268 | 17.4912 | -106.7276 | -2.2064 | -2.1149 | -2.9984 | 123.1705 | 0.55847 | -0.48981 | 1.2451 | -0.79193 | 96.1487 | 96.611 | 123.0423 | 120.369 | -2.9984 | 123.7289 | 101.7929 | -0.48981 | 120.369 | -2.9984 | 101.7929 | 123.0423 | 123.7289 | -124.6902 | -122.9736
2074.9219 | 122.5891 | -66.7511 | 44.902 | -0.18662 | 0.002162 | 0.0025998 | 0.0092413 | -0.0030484 | -0.00093346 | 0.00042086 | -66.9113 | 55.8472 | -67.2363 | 55.5679 | 54.3137 | -0.54932 | -3.5568 | -2.9022 | 55.5222 | -67.5339 | -0.48523 | 10.9451 | -0.16022 | 122.319 | 9.4116 | -0.78278 | 10.6201 | 0.32501 | 63.1943 | 63.8489 | 121.0648 | 122.5983 | -0.16022 | 122.2733 | 66.2018 | -0.78278 | 122.5983 | -0.16022 | 66.2018 | 121.0648 | 122.2733 | -112.1384 | -112.4359
2075.9531 | 122.9233 | -70.2942 | 51.8784 | -0.21713 | -0.001256 | 0.0049496 | 0.0053961 | -0.0053982 | -0.0013609 | 0.0025571 | -71.8048 | 51.1826 | -71.9376 | 52.0157 | 49.6124 | -1.6571 | -3.4103 | -2.2797 | 51.9287 | -70.7291 | -1.6434 | -0.6958 | -1.5106 | 122.3099 | -2.2659 | -0.43488 | 0.050354 | 0.13275 | 66.8839 | 68.0145 | 119.9066 | 121.4767 | -1.5106 | 122.2229 | 68.6371 | -0.43488 | 121.4767 | -1.5106 | 68.6371 | 119.9066 | 122.2229 | -123.8159 | -122.6074
2076.9062 | 122.937 | -66.8884 | 55.6778 | -0.17899 | 0.0028028 | 0.0023862 | 0.0039007 | -0.003262 | -0.0024289 | 0.0014889 | -67.1494 | 55.481 | -67.4423 | 55.7922 | 54.3594 | -1.9272 | -3.3051 | -2.7283 | 55.5222 | -67.4332 | -0.55389 | -0.19684 | -0.26093 | 122.6807 | -1.3184 | -0.54474 | -0.15564 | 0.29297 | 63.5834 | 64.1602 | 121.2479 | 122.3694 | -0.26093 | 122.4106 | 64.9612 | -0.54474 | 122.3694 | -0.26093 | 64.9612 | 121.2479 | 122.4106 | -123.1201 | -123.111
2077.9688 | 122.1954 | -18.8232 | 104.7272 | 0.11856 | 0.00066656 | -0.00060462 | 0.0013373 | -0.0058256 | 0.00013454 | 0.015161 | -24.1745 | 100.9369 | -20.7321 | 106.5674 | 103.8025 | 5.8319 | 5.3238 | -3.3096 | 102.4155 | -19.5648 | -1.9089 | -3.7903 | -5.3513 | 125.3906 | -0.92468 | -0.74158 | -2.3117 | -3.4424 | 24.147 | 15.5136 | 122.6257 | 119.7601 | -5.3513 | 121.2387 | 24.6552 | -0.74158 | 119.7601 | -5.3513 | 24.6552 | 122.6257 | 121.2387 | -125.4593 | -124.292
2078.9062 | 122.7173 | -11.8011 | 98.6069 | -0.20187 | 0.00023916 | 0.003668 | 0.0024053 | -0.00668 | -0.0030697 | 0.015374 | -12.1216 | 110.6049 | -12.41 | 110.8887 | 108.4213 | 6.3309 | 5.7953 | 6.5735 | 110.6552 | -12.3734 | -0.60883 | 11.998 | -0.32043 | 122.6898 | 9.8145 | -0.57221 | 12.0483 | 0.28839 | 17.5964 | 18.3746 | 120.2225 | 122.406 | -0.32043 | 122.4564 | 18.132 | -0.57221 | 122.406 | -0.32043 | 18.132 | 120.2225 | 122.4564 | -111.0168 | -110.9802
2079.9688 | 122.7448 | -10.0159 | 112.1338 | -0.026398 | 0.001521 | 0.0011044 | 0.0032599 | -0.0064664 | -0.0026425 | 0.019433 | -9.3338 | 113.3377 | -9.7 | 112.7518 | 110.4263 | 6.6055 | 5.8411 | 6.871 | 112.8387 | -10.2036 | 0.31586 | 1.2039 | 0.68207 | 122.7676 | -1.7075 | -0.18768 | 0.70496 | 0.36621 | 15.8569 | 16.8869 | 120.4422 | 123.3536 | 0.68207 | 122.8546 | 16.6214 | -0.18768 | 123.3536 | 0.68207 | 16.6214 | 120.4422 | 122.8546 | -121.8338 | -122.3373
2080.9062 | 122.4472 | -7.3654 | 114.624 | -0.041657 | -0.00061524 | -0.00017722 | 0.0002691 | -0.00668 | 0.0020571 | 0.018579 | -7.4203 | 115.3198 | -7.663 | 115.6815 | 113.1454 | 7.1457 | 6.1569 | 7.3105 | 115.3564 | -7.6447 | -0.29755 | 0.6958 | -0.054932 | 123.0469 | -1.4786 | -0.27924 | 0.73242 | 0.24261 | 13.5223 | 14.6759 | 120.5109 | 122.6852 | -0.054932 | 122.7219 | 14.5111 | -0.27924 | 122.6852 | -0.054932 | 14.5111 | 120.5109 | 122.7219 | -122.287 | -122.2687
2081.9062 | 122.5067 | -6.3721 | 115.5533 | -0.041657 | 0.00088016 | -0.0016726 | 0.0032599 | -0.0077482 | 0.0016299 | 0.018579 | -6.3492 | 116.3727 | -6.633 | 116.7847 | 114.1113 | 7.2372 | 6.0333 | 7.3471 | 116.2766 | -6.6284 | -0.26093 | 0.8194 | 0.022888 | 123.1567 | -1.442 | -0.25635 | 0.72327 | 0.28381 | 12.4054 | 13.7192 | 120.4834 | 122.7448 | 0.022888 | 122.6486 | 13.6093 | -0.25635 | 122.7448 | 0.022888 | 13.6093 | 120.4834 | 122.6486 | -122.1863 | -122.1817
2082.9531 | 123.0011 | -14.4287 | 107.1854 | 0.24826 | 0.0047254 | -0.00017722 | 0.011377 | -0.0058256 | -0.0013609 | 0.018365 | -14.5065 | 108.2703 | -14.7766 | 108.2565 | 105.162 | 5.7495 | 4.4266 | 6.7383 | 108.2199 | -14.7995 | -0.3479 | 1.0849 | -0.07782 | 122.6852 | -2.0233 | -0.37079 | 1.0345 | 0.27008 | 18.8553 | 21.167 | 119.5908 | 122.699 | -0.07782 | 122.6486 | 20.1782 | -0.37079 | 122.699 | -0.07782 | 20.1782 | 119.5908 | 122.6486 | -121.962 | -121.9849
2083.9062 | 122.6349 | -7.4936 | 114.7476 | -0.10269 | -0.0010424 | -0.00017722 | 0.0028327 | -0.0077482 | 0.0014163 | 0.01922 | -7.1915 | 115.4572 | -7.576 | 115.448 | 112.9257 | 7.1503 | 5.5618 | 7.2052 | 115.2374 | -7.7591 | -0.082398 | 0.70953 | 0.30212 | 122.9416 | -1.8219 | -0.2655 | 0.48981 | 0.38452 | 13.0554 | 14.6988 | 120.4193 | 122.9507 | 0.30212 | 122.731 | 14.6439 | -0.2655 | 122.9507 | 0.30212 | 14.6439 | 120.4193 | 122.731 | -122.3236 | -122.5067
2084.9688 | 122.525 | -6.7108 | 115.5167 | -0.041657 | 0.0023756 | -0.0010318 | 0.0009101 | -0.0060392 | 0.0012027 | 0.017083 | -6.665 | 115.9882 | -7.0358 | 116.3132 | 113.7085 | 7.0724 | 5.4703 | 7.2281 | 116.0019 | -6.9717 | -0.32501 | 0.4715 | 0.045776 | 123.024 | -1.8082 | -0.26093 | 0.48523 | 0.37079 | 12.1811 | 13.9389 | 120.4193 | 122.699 | 0.045776 | 122.7127 | 13.7833 | -0.26093 | 122.699 | 0.045776 | 13.7833 | 120.4193 | 122.7127 | -122.5525 | -122.4884
2085.9062 | 122.6257 | -8.5327 | 113.4842 | -0.57571 | 0.0038708 | 0.0015316 | 0.0049689 | -0.0086026 | 0.00013454 | 0.01922 | -8.432 | 114.2441 | -8.812 | 114.2303 | 111.9049 | 6.5781 | 5.2963 | 7.1732 | 114.0839 | -8.8943 | -0.27924 | 0.75989 | 0.10071 | 122.7631 | -1.5793 | -0.36163 | 0.59967 | 0.37994 | 13.829 | 15.7059 | 120.4376 | 122.7768 | 0.10071 | 122.6166 | 15.1108 | -0.36163 | 122.7768 | 0.10071 | 15.1108 | 120.4376 | 122.6166 | -122.2961 | -122.3785
2086.9531 | 122.4518 | -6.8665 | 115.2374 | 0.027008 | 0.0023756 | -0.0012454 | 0.0060369 | -0.0073208 | -0.00029266 | 0.020288 | -6.8802 | 115.8142 | -7.2006 | 115.9332 | 113.7177 | 6.926 | 5.6671 | 7.338 | 115.8966 | -7.164 | -0.33417 | 0.57678 | -0.013733 | 122.7997 | -1.5198 | -0.29755 | 0.65918 | 0.32043 | 12.5336 | 14.2044 | 120.5841 | 122.6807 | -0.013733 | 122.7631 | 13.7924 | -0.29755 | 122.6807 | -0.013733 | 13.7924 | 120.5841 | 122.7631 | -122.4381 | -122.4014
2087.9062 | 122.4976 | -6.34 | 115.6906 | -0.018768 | 0.00088016 | 0.0038816 | 0.0019781 | -0.0075344 | -0.00093346 | 0.018365 | -6.3583 | 116.2079 | -6.871 | 116.6336 | 113.9877 | 6.9168 | 5.5206 | 7.3563 | 116.3544 | -6.6193 | -0.53101 | 0.51727 | -0.01831 | 122.9736 | -1.7029 | -0.27924 | 0.66376 | 0.5127 | 11.8607 | 13.6963 | 120.3278 | 122.5479 | -0.01831 | 122.6944 | 13.2568 | -0.27924 | 122.5479 | -0.01831 | 13.2568 | 120.3278 | 122.6944 | -122.5616 | -122.3099
2088.9531 | 122.3328 | -6.4087 | 115.8325 | 0.14145 | 0.0013074 | -0.0012454 | 0.0041143 | -0.0047574 | 0.00056194 | 0.021356 | -6.2302 | 116.391 | -6.6788 | 116.2857 | 113.6169 | 6.9946 | 4.953 | 7.3883 | 116.272 | -6.7429 | -0.27008 | 0.55847 | 0.17853 | 122.6944 | -2.2156 | -0.33417 | 0.43945 | 0.44861 | 11.3617 | 13.797 | 120.0256 | 122.7997 | 0.17853 | 122.6807 | 13.4033 | -0.33417 | 122.7997 | 0.17853 | 13.4033 | 120.0256 | 122.6807 | -122.5113 | -122.5754
2089.9062 | 122.3785 | -6.2759 | 116.304 | -0.10269 | 0.0019482 | 0.004736 | 0.0032599 | -0.0060392 | 0.00034814 | 0.018579 | -6.1707 | 116.4505 | -6.5506 | 116.7664 | 114.2944 | 7.0129 | 5.1407 | 7.5943 | 116.4368 | -6.5369 | -0.27466 | 0.14648 | 0.10529 | 123.0423 | -2.0096 | -0.26092 | 0.13275 | 0.37994 | 11.4166 | 13.8702 | 120.5704 | 122.7264 | 0.10529 | 122.7127 | 13.2889 | -0.26092 | 122.7264 | 0.10529 | 13.2889 | 120.5704 | 122.7127 | -122.8546 | -122.8409
2090.9688 | 122.4289 | -5.8548 | 116.2994 | 0.20248 | 0.0010938 | 0.00067718 | 0.0030463 | -0.004971 | -0.00029266 | 0.018365 | -5.7678 | 116.8716 | -6.1661 | 117.1417 | 114.5416 | 6.4911 | 5.1956 | 7.4387 | 116.8533 | -6.1157 | -0.31128 | 0.57221 | 0.086975 | 122.9965 | -1.7578 | -0.26093 | 0.5539 | 0.39825 | 11.0504 | 13.2935 | 120.3964 | 122.7264 | 0.086975 | 122.7081 | 12.3459 | -0.26093 | 122.7264 | 0.086975 | 12.3459 | 120.3964 | 122.7081 | -122.4655 | -122.4152
2091.9062 | 95.0684 | -9.4482 | 113.2004 | -0.087433 | 0.0010938 | -0.0040226 | 0.0013373 | -0.0073208 | 0.00013454 | 0.020074 | -9.6085 | 112.5916 | -10.7391 | 113.8733 | 111.2137 | 6.5231 | 4.6051 | 6.8253 | 113.1088 | -9.6725 | -1.2909 | -0.60882 | -0.16022 | 123.3215 | -1.9867 | -0.2243 | -0.091552 | 1.1307 | 14.0533 | 16.2735 | 120.6619 | 122.0398 | -0.16022 | 122.5571 | 15.9714 | -0.2243 | 122.0398 | -0.16022 | 15.9714 | 120.6619 | 122.5571 | -123.9395 | -122.8729
2092.9062 | 122.6944 | -6.7108 | 115.3336 | -0.056915 | 0.001521 | 0.00089078 | 0.0030463 | -0.0068936 | 0.0020571 | 0.01986 | -6.5781 | 116.1346 | -6.9031 | 116.3132 | 113.6353 | 6.4682 | 4.8889 | 7.5577 | 115.9424 | -6.9992 | -0.19226 | 0.80109 | 0.13275 | 123.024 | -1.6983 | -0.28839 | 0.60883 | 0.32501 | 11.5997 | 14.2685 | 120.3461 | 122.8455 | 0.13275 | 122.6532 | 13.179 | -0.28839 | 122.8455 | 0.13275 | 13.179 | 120.3461 | 122.6532 | -122.2366 | -122.3328
2093.9844 | 122.1771 | -9.0683 | 110.733 | -0.13321 | 0.0055798 | 0.004736 | 0.0092413 | -0.0056118 | 0.00077554 | 0.018151 | -8.0338 | 114.7522 | -8.3771 | 114.798 | 112.2528 | 6.4316 | 4.9622 | 5.8136 | 113.7497 | -9.2331 | 0.69122 | 4.0192 | 1.0345 | 123.8663 | 1.5198 | -0.16479 | 3.0167 | 0.34332 | 14.0305 | 14.8819 | 121.3211 | 123.8205 | 1.0345 | 122.818 | 15.4999 | -0.16479 | 123.8205 | 1.0345 | 15.4999 | 121.3211 | 122.818 | -119.1101 | -119.9661
2094.9062 | 122.5159 | -6.9122 | 115.5533 | 0.072784 | 0.00066656 | 0.00046358 | 0.0009101 | -0.0060392 | 0.00013454 | 0.017938 | -6.8802 | 115.8691 | -7.196 | 116.1026 | 113.4659 | 6.102 | 4.9301 | 7.338 | 115.8463 | -7.1594 | -0.28381 | 0.31586 | 0.032043 | 123.0148 | -2.0874 | -0.24719 | 0.29297 | 0.31586 | 11.8423 | 14.2502 | 120.3781 | 122.7814 | 0.032043 | 122.7585 | 13.0142 | -0.24719 | 122.7814 | 0.032043 | 13.0142 | 120.3781 | 122.7585 | -122.7493 | -122.7127
2095.9062 | 122.4838 | -6.1844 | 116.0294 | 0.12619 | 0.002162 | -0.0010318 | 0.0028327 | -0.004971 | -0.0015745 | 0.018151 | -6.2576 | 116.4825 | -6.5552 | 116.6473 | 114.1617 | 6.1935 | 5.0217 | 7.6355 | 116.5146 | -6.5094 | -0.37079 | 0.45319 | -0.073242 | 122.8317 | -1.8677 | -0.32501 | 0.48523 | 0.29755 | 11.2061 | 13.8199 | 120.3461 | 122.6669 | -0.073242 | 122.699 | 12.3779 | -0.32501 | 122.6669 | -0.073242 | 12.3779 | 120.3461 | 122.699 | -122.5845 | -122.5388
2096.9062 | 122.7859 | -7.6859 | 114.3219 | -0.056915 | -0.00082884 | 0.00067718 | 0.0013373 | -0.0060392 | 0.00098914 | 0.01922 | -7.3883 | 115.3015 | -7.7316 | 115.3061 | 112.8525 | 5.7953 | 4.5547 | 7.2464 | 115.1367 | -7.8735 | -0.045776 | 0.97961 | 0.29755 | 122.9919 | -1.4694 | -0.18768 | 0.81482 | 0.34332 | 12.2406 | 14.9323 | 120.5383 | 122.9874 | 0.29755 | 122.8226 | 13.4811 | -0.18768 | 122.9874 | 0.29755 | 13.4811 | 120.5383 | 122.8226 | -122.0535 | -122.1954
2097.9688 | 122.3831 | -7.695 | 114.4272 | 0.14908 | 0.001521 | 0.0045224 | 0.0021917 | -0.0060392 | 0.0016299 | 0.018151 | -7.8278 | 114.8392 | -8.1894 | 115.329 | 112.7747 | 5.9692 | 4.6234 | 7.3334 | 115.0177 | -7.9605 | -0.49438 | 0.41199 | -0.13275 | 123.024 | -1.6525 | -0.2655 | 0.59052 | 0.36163 | 12.3184 | 15.0284 | 120.4697 | 122.5342 | -0.13275 | 122.7127 | 13.6642 | -0.2655 | 122.5342 | -0.13275 | 13.6642 | 120.4697 | 122.7127 | -122.6166 | -122.3877
2098.9062 | 122.4518 | -6.6513 | 115.4617 | -0.087433 | 0.001521 | 0.005377 | 0.0021917 | -0.0075344 | 0.0022707 | 0.017083 | -6.5689 | 116.0843 | -6.9397 | 116.4276 | 113.8275 | 6.1066 | 4.6371 | 7.1274 | 116.0019 | -6.9443 | -0.28839 | 0.62256 | 0.082397 | 123.0789 | -1.6342 | -0.29297 | 0.54016 | 0.37079 | 11.2885 | 13.7787 | 120.4788 | 122.7356 | 0.082397 | 122.6532 | 12.7579 | -0.29297 | 122.7356 | 0.082397 | 12.7579 | 120.4788 | 122.6532 | -122.4014 | -122.406
2099.9688 | 122.7448 | -7.3654 | 114.8163 | -0.0035098 | 0.00066656 | 0.0034544 | 0.0051825 | -0.0060392 | 0.0039797 | 0.020501 | -7.0908 | 115.6265 | -7.4844 | 115.8554 | 113.2095 | 5.9418 | 4.5273 | 7.0496 | 115.535 | -7.4799 | -0.11902 | 0.81024 | 0.27466 | 123.2208 | -1.6067 | -0.11444 | 0.71869 | 0.39368 | 11.8927 | 14.415 | 120.575 | 122.9919 | 0.27466 | 122.9004 | 13.3072 | -0.11444 | 122.9919 | 0.27466 | 13.3072 | 120.575 | 122.9004 | -122.3007 | -122.2961
2100.9062 | 122.3877 | -6.9809 | 115.1047 | -0.026398 | -0.00082884 | 3.6382e-05 | 0.0068915 | -0.0096708 | -0.00050626 | 0.020929 | -7.1274 | 115.5533 | -7.5073 | 116.066 | 113.5712 | 5.9555 | 4.216 | 7.283 | 115.6036 | -7.3654 | -0.52643 | 0.44861 | -0.14648 | 123.0469 | -1.5335 | -0.38452 | 0.49896 | 0.37994 | 11.1969 | 14.2639 | 120.5521 | 122.5342 | -0.14648 | 122.5845 | 12.9364 | -0.38452 | 122.5342 | -0.14648 | 12.9364 | 120.5521 | 122.5845 | -122.612 | -122.4701
2101.9688 | 122.6166 | -7.0312 | 115.7867 | 0.049896 | 2.5564e-05 | -0.0012454 | 0.0015509 | -0.0068936 | 0.00056194 | 0.020288 | -6.9122 | 115.8783 | -7.1823 | 115.8005 | 113.3469 | 5.7678 | 4.5639 | 7.045 | 115.6998 | -7.3242 | -0.15106 | 0.091553 | 0.11902 | 122.8317 | -2.4399 | -0.29297 | -0.086975 | 0.27008 | 11.5952 | 14.0762 | 120.3781 | 122.9095 | 0.11902 | 122.731 | 12.7991 | -0.29297 | 122.9095 | 0.11902 | 12.7991 | 120.3781 | 122.731 | -122.9691 | -123.111
2102.9062 | 122.5983 | -6.5094 | 115.9058 | -0.018768 | 0.0028028 | 0.003668 | -0.0001581 | -0.0062528 | 0.00056194 | 0.019433 | -6.2759 | 116.4093 | -6.6147 | 116.4001 | 113.736 | 5.6946 | 4.6783 | 7.3105 | 116.217 | -6.7657 | -0.10529 | 0.50354 | 0.23346 | 122.9095 | -2.1698 | -0.25635 | 0.31128 | 0.33874 | 11.1877 | 13.8199 | 120.2454 | 122.9187 | 0.23346 | 122.7264 | 12.204 | -0.25635 | 122.9187 | 0.23346 | 12.204 | 120.2454 | 122.7264 | -122.5204 | -122.6715
2103.9531 | 117.5858 | -6.8756 | 115.5716 | 0.16434 | 0.0038708 | 0.0043088 | 0.0090277 | -0.0062528 | -0.0022153 | 0.017511 | -6.9077 | 115.9012 | -7.2601 | 116.1896 | 113.5849 | 5.4657 | 4.4998 | 7.1045 | 115.9927 | -7.077 | -0.38452 | 0.32959 | -0.032044 | 123.0652 | -1.9867 | -0.20142 | 0.42114 | 0.35248 | 11.3754 | 13.9801 | 120.4605 | 122.7768 | -0.032044 | 122.8683 | 12.3413 | -0.20142 | 122.7768 | -0.032044 | 12.3413 | 120.4605 | 122.8683 | -122.8317 | -122.6486
2104.9062 | 102.5528 | -6.4636 | 91.5894 | -0.25528 | 0.0047254 | 0.0028134 | 0.0096685 | -0.003903 | 0.00013454 | 0.021783 | -6.0104 | 116.7847 | -6.3675 | 116.4734 | 114.1663 | 5.4474 | 4.7791 | 7.4936 | 116.6656 | -6.5369 | 0.09613 | 25.1953 | 0.45319 | 122.937 | 22.5769 | -0.073242 | 25.0763 | 0.35706 | 11.2427 | 13.9572 | 120.6299 | 123.2483 | 0.45319 | 123.1293 | 11.911 | -0.073242 | 123.2483 | 0.45319 | 11.911 | 120.6299 | 123.1293 | -97.9568 | -98.1262
2105.9688 | 122.6715 | -6.4133 | 115.9836 | 0.19485 | 0.00023916 | 0.0023862 | 0.0017645 | -0.0034756 | 0.00034814 | 0.021569 | -6.546 | 116.1346 | -6.926 | 116.2628 | 113.9374 | 5.7129 | 4.335 | 7.5165 | 116.3223 | -6.7062 | -0.51269 | 0.15106 | -0.13275 | 122.6761 | -2.0462 | -0.29297 | 0.33875 | 0.37994 | 10.7483 | 13.9297 | 120.3506 | 122.5479 | -0.13275 | 122.7356 | 12.1262 | -0.29297 | 122.5479 | -0.13275 | 12.1262 | 120.3506 | 122.7356 | -122.9095 | -122.6898
2106.9062 | 106.3889 | -6.5552 | 112.9257 | 0.049896 | 0.0045118 | 0.0072996 | 0.012873 | -0.0024076 | 0.00077554 | 0.020074 | -6.2942 | 116.4413 | -6.7703 | 116.5512 | 113.8046 | 5.4016 | 4.6692 | 7.4478 | 116.3635 | -6.6971 | -0.21515 | 3.5156 | 0.26093 | 123.1064 | 0.87891 | -0.14191 | 3.4378 | 0.47607 | 11.2244 | 14.003 | 120.3598 | 122.9965 | 0.26093 | 122.9187 | 11.9568 | -0.14191 | 122.9965 | 0.26093 | 11.9568 | 120.3598 | 122.9187 | -119.696 | -119.6228
2107.9062 | 122.0856 | -6.9946 | 111.3144 | 0.011749 | 0.00088016 | 0.00089078 | 0.0019781 | -0.0045438 | 0.0014163 | 0.01922 | -7.0587 | 115.6403 | -7.3425 | 115.7227 | 113.1775 | 5.5023 | 4.3854 | 7.6126 | 115.5899 | -7.4387 | -0.3479 | 4.3259 | -0.064087 | 122.7173 | 1.8631 | -0.44403 | 4.2755 | 0.28381 | 11.38 | 14.6072 | 120.1721 | 122.6349 | -0.064087 | 122.5845 | 12.4969 | -0.44403 | 122.6349 | -0.064087 | 12.4969 | 120.1721 | 122.5845 | -118.6569 | -118.7531
2108.9062 | 122.525 | -7.7591 | 114.8071 | -0.11795 | 0.00088016 | -0.00039102 | 0.0013373 | -0.0051846 | -0.0017881 | 0.021783 | -7.7728 | 114.8804 | -8.1528 | 115.1642 | 112.619 | 5.4199 | 4.2892 | 7.4982 | 114.9445 | -8.0383 | -0.39368 | 0.073242 | -0.013733 | 122.9233 | -2.1881 | -0.27924 | 0.13733 | 0.37994 | 12.0483 | 15.2573 | 120.3781 | 122.6395 | -0.013733 | 122.7036 | 13.179 | -0.27924 | 122.6395 | -0.013733 | 13.179 | 120.3781 | 122.7036 | -122.9599 | -122.8455
2109.9531 | 122.937 | -111.731 | 10.9177 | 0.26352 | -0.0014696 | 0.0034544 | 0.017573 | -0.0062528 | -0.0030697 | 0.0025571 | -111.6074 | 10.8398 | -112.1887 | 10.9726 | 10.5835 | -3.6209 | -11.2381 | -10.2539 | 10.9039 | -112.1338 | -0.45776 | -0.07782 | 0.1236 | 122.7036 | -0.33417 | -0.40283 | -0.013733 | 0.58136 | 100.4929 | 101.4771 | 122.3145 | 122.5708 | 0.1236 | 122.6349 | 108.11 | -0.40283 | 122.5708 | 0.1236 | 108.11 | 122.3145 | 122.6349 | -123.1064 | -123.0515
2110.9062 | 122.9736 | -113.6307 | 9.0271 | 0.31693 | 0.0010938 | -0.00081822 | 0.017145 | -0.0047574 | -0.0028561 | 0.0040525 | -113.4796 | 9.0088 | -113.9832 | 9.1507 | 8.7662 | -3.7628 | -11.8057 | -10.6659 | 9.0866 | -113.9145 | -0.35248 | -0.018311 | 0.15106 | 122.7814 | -0.26093 | -0.28381 | 0.059509 | 0.50354 | 101.825 | 102.9648 | 122.3969 | 122.6395 | 0.15106 | 122.7173 | 109.8679 | -0.28381 | 122.6395 | 0.15106 | 109.8679 | 122.3969 | 122.7173 | -123.0103 | -122.9416
2111.9688 | 122.8226 | -98.3963 | 24.4492 | -0.2095 | 0.0013074 | 0.003027 | 0.019282 | -0.004971 | 0.0022707 | 0.0074705 | -104.4617 | 18.4753 | -104.4571 | 26.8158 | 22.0688 | -0.93384 | -7.7179 | -6.7245 | 24.0967 | -98.2635 | -6.0608 | -5.9738 | -6.0654 | 125.2121 | -2.3804 | 0.13275 | -0.35248 | -0.004578 | 90.6784 | 91.6718 | 120.4651 | 116.8716 | -6.0654 | 122.493 | 97.4625 | 0.13275 | 116.8716 | -6.0654 | 97.4625 | 120.4651 | 122.493 | -128.9062 | -122.7127
2112.9062 | 122.9233 | -113.768 | 8.8852 | -0.18662 | -0.0016834 | 0.0017454 | 0.014795 | -0.0036892 | -0.0024289 | 0.0051205 | -113.6307 | 8.844 | -114.1434 | 8.9355 | 8.5876 | -3.9825 | -12.1902 | -11.2885 | 8.9447 | -114.1434 | -0.37537 | -0.041199 | 0.13733 | 122.7036 | -0.29755 | -0.37537 | 0.059509 | 0.5127 | 101.5778 | 102.4796 | 122.3557 | 122.612 | 0.13733 | 122.7127 | 109.7855 | -0.37537 | 122.612 | 0.13733 | 109.7855 | 122.3557 | 122.7127 | -123.0286 | -123.0286
2113.9531 | 122.9691 | -114.8392 | 7.8049 | -1.7812 | -0.00018804 | 0.006445 | 0.016932 | -0.0047574 | -0.0011471 | 0.0038389 | -114.8849 | 7.7408 | -115.2512 | 7.869 | 7.5119 | -4.0924 | -12.7167 | -11.3709 | 7.8278 | -115.2145 | -0.41199 | -0.064087 | -0.045777 | 122.7081 | -0.29297 | -0.37537 | 0.022888 | 0.36621 | 102.1225 | 103.4683 | 122.3511 | 122.58 | -0.045777 | 122.6669 | 110.7468 | -0.37537 | 122.58 | -0.045777 | 110.7468 | 122.3511 | 122.6669 | -123.056 | -123.0194
2114.9062 | 122.8363 | -112.4725 | 10.2036 | 0.080414 | 0.0025892 | 0.0070858 | 0.023127 | -0.003262 | -0.00093346 | 0.0027707 | -112.4359 | 10.144 | -112.8983 | 10.0433 | 9.6909 | -3.9871 | -12.2543 | -11.3251 | 10.2036 | -112.9303 | -0.42572 | -0.059509 | 0.036621 | 122.5159 | -0.5127 | -0.45776 | 0 | 0.46234 | 100.2182 | 101.1475 | 122.1634 | 122.6166 | 0.036621 | 122.6761 | 108.4854 | -0.45776 | 122.6166 | 0.036621 | 108.4854 | 122.1634 | 122.6761 | -123.1018 | -123.1338
2115.9531 | 123.024 | -114.6286 | 7.9926 | -0.095062 | -0.00082884 | 0.003027 | 0.015009 | -0.003903 | 0.00034814 | 0.0036253 | -114.6881 | 7.8232 | -115.1688 | 7.8827 | 7.6263 | -3.9139 | -12.6389 | -11.3663 | 7.9376 | -115.036 | -0.54016 | -0.16937 | -0.059509 | 122.5113 | -0.36621 | -0.40741 | -0.054932 | 0.48065 | 101.9897 | 103.2623 | 122.2549 | 122.4518 | -0.059509 | 122.5662 | 110.7147 | -0.40741 | 122.4518 | -0.059509 | 110.7147 | 122.2549 | 122.5662 | -123.1613 | -123.0286
2116.9219 | 122.937 | -116.1575 | 6.5964 | 0.11093 | 0.002162 | 0.0070858 | 0.024622 | -0.0041166 | -0.00093346 | 0.0046933 | -116.0614 | 6.5552 | -116.5054 | 6.4178 | 6.1432 | -4.2114 | -12.5107 | -12.3505 | 6.6101 | -116.5054 | -0.3479 | -0.041199 | 0.096131 | 122.5754 | -0.45319 | -0.3479 | 0.013732 | 0.44403 | 103.6469 | 103.8071 | 122.3007 | 122.7127 | 0.096131 | 122.7676 | 111.9461 | -0.3479 | 122.7127 | 0.096131 | 111.9461 | 122.3007 | 122.7676 | -123.1018 | -123.1018
2117.9531 | 122.9782 | -114.4272 | 8.1345 | 0.17197 | 0.00088016 | 0.0066586 | 0.019282 | -0.0013394 | -0.0017881 | 0.0049069 | -114.3448 | 8.1894 | -114.8438 | 8.1711 | 7.8598 | -4.0237 | -12.4786 | -11.9797 | 8.1665 | -114.8483 | -0.41657 | 0.054932 | 0.082397 | 122.5983 | -0.27466 | -0.42114 | 0.032044 | 0.49896 | 101.9485 | 102.4475 | 122.287 | 122.6166 | 0.082397 | 122.5937 | 110.4034 | -0.42114 | 122.6166 | 0.082397 | 110.4034 | 122.287 | 122.5937 | -122.9782 | -122.9828
2118.9062 | 122.9462 | -118.19 | 4.5914 | -0.17899 | 0.001521 | 0.0032406 | 0.015864 | -0.0051846 | -0.0015745 | 0.0025571 | -117.9932 | 4.509 | -118.5059 | 4.5319 | 4.3076 | -4.335 | -12.8723 | -12.2223 | 4.6097 | -118.4647 | -0.31586 | -0.082398 | 0.19684 | 122.7219 | -0.28381 | -0.27466 | 0.01831 | 0.5127 | 105.3177 | 105.9677 | 122.4976 | 122.699 | 0.19684 | 122.7997 | 113.855 | -0.27466 | 122.699 | 0.19684 | 113.855 | 122.4976 | 122.7997 | -123.0972 | -123.056
2119.9688 | 89.502 | -99.5453 | 22.7737 | -0.19424 | 0.0010938 | 0.00089078 | 0.010309 | -0.0062528 | -0.0026425 | 0.0036253 | -95.8511 | 28.8437 | -94.7617 | 24.6689 | 23.4924 | -4.4083 | -10.7117 | -10.2173 | 24.2065 | -99.3164 | 4.7836 | 6.0699 | 3.6942 | 124.2142 | 0.71869 | 0.22888 | 1.4328 | -1.0895 | 88.8336 | 89.328 | 123.0377 | 128.389 | 3.6942 | 123.7518 | 95.137 | 0.22888 | 128.389 | 3.6942 | 95.137 | 123.0377 | 123.7518 | -117.5354 | -122.0901
2120.9062 | 122.8821 | -114.4592 | 8.2947 | -0.22476 | 0.00088016 | 0.0034544 | 0.017359 | -0.0064664 | -0.0030697 | 0.0040525 | -114.3494 | 8.2169 | -114.8071 | 8.1802 | 7.8964 | -4.0695 | -11.9934 | -11.9797 | 8.3267 | -114.7934 | -0.3479 | -0.07782 | 0.10986 | 122.6395 | -0.39825 | -0.33417 | 0.032043 | 0.45776 | 102.4658 | 102.4796 | 122.3557 | 122.6761 | 0.10986 | 122.7859 | 110.3897 | -0.33417 | 122.6761 | 0.10986 | 110.3897 | 122.3557 | 122.7859 | -123.1018 | -123.0881
2121.9688 | 122.9645 | -115.6677 | 6.9901 | 0.14908 | 2.5564e-05 | 0.003668 | 0.020136 | -0.0024076 | 0.00056194 | 0.0053343 | -115.5029 | 6.9626 | -116.0202 | 7.0175 | 6.7291 | -4.2526 | -12.854 | -12.4741 | 7.0496 | -115.9927 | -0.35248 | -0.027466 | 0.16479 | 122.6852 | -0.26093 | -0.32501 | 0.05951 | 0.51727 | 102.8137 | 103.1937 | 122.3969 | 122.6303 | 0.16479 | 122.7173 | 111.4151 | -0.32501 | 122.6303 | 0.16479 | 111.4151 | 122.3969 | 122.7173 | -123.0103 | -122.9828
2122.9062 | 122.9691 | -114.7339 | 7.933 | -0.24002 | 0.00066656 | 0.00046358 | 0.014795 | -0.0047574 | -7.9062e-05 | 0.0025571 | -114.6103 | 7.8873 | -115.1184 | 7.9239 | 7.6263 | -4.1382 | -12.4466 | -12.2589 | 7.9468 | -115.123 | -0.38452 | -0.045776 | 0.1236 | 122.6578 | -0.3067 | -0.3891 | 0.013733 | 0.50812 | 102.2873 | 102.475 | 122.3602 | 122.6212 | 0.1236 | 122.6807 | 110.5957 | -0.3891 | 122.6212 | 0.1236 | 110.5957 | 122.3602 | 122.6807 | -123.0515 | -123.056
2123.9688 | 122.9507 | -115.1093 | 7.6675 | 0.19485 | 0.0013074 | 0.0058042 | 0.016932 | -0.0036892 | -0.0020017 | 0.0046933 | -114.9353 | 7.5851 | -115.3931 | 7.608 | 7.3288 | -4.2389 | -12.4237 | -12.5153 | 7.6767 | -115.3656 | -0.28381 | -0.082398 | 0.17395 | 122.7173 | -0.33875 | -0.25635 | 0.009155 | 0.45776 | 102.6855 | 102.594 | 122.438 | 122.6944 | 0.17395 | 122.7859 | 110.8704 | -0.25635 | 122.6944 | 0.17395 | 110.8704 | 122.438 | 122.7859 | -123.0606 | -123.0331
2124.9062 | 122.8821 | -115.2191 | 7.4936 | -0.018768 | 0.0038708 | 0.004736 | 0.026758 | -0.0041166 | -0.0028561 | 0.0051205 | -115.1047 | 7.4432 | -115.6265 | 7.4066 | 7.0908 | -4.2343 | -12.2772 | -12.4741 | 7.5165 | -115.6723 | -0.40741 | -0.050354 | 0.11444 | 122.6257 | -0.40283 | -0.45319 | 0.022888 | 0.52185 | 102.9419 | 102.7451 | 122.3099 | 122.6624 | 0.11444 | 122.7356 | 110.9848 | -0.45319 | 122.6624 | 0.11444 | 110.9848 | 122.3099 | 122.7356 | -123.1201 | -123.1659
2125.9688 | 122.9553 | -113.7131 | 9.0042 | 0.0041197 | 0.0017346 | 3.6382e-05 | 0.013941 | -0.0045438 | -0.0032835 | 0.0027707 | -113.6215 | 8.9447 | -114.0701 | 8.9493 | 8.6655 | -4.303 | -12.561 | -12.5061 | 9.0271 | -114.0381 | -0.35705 | -0.059509 | 0.091553 | 122.6624 | -0.33874 | -0.32501 | 0.022889 | 0.44861 | 101.152 | 101.207 | 122.3785 | 122.6578 | 0.091553 | 122.7402 | 109.4101 | -0.32501 | 122.6578 | 0.091553 | 109.4101 | 122.3785 | 122.7402 | -123.0743 | -123.0423
2126.9062 | 122.85 | -115.1321 | 7.5943 | -0.14084 | 0.0030164 | 0.004736 | 0.020136 | -0.0051846 | -0.0039243 | 0.0021299 | -115.0589 | 7.5211 | -115.5441 | 7.4753 | 7.1548 | -4.6417 | -12.5153 | -13.1012 | 7.6035 | -115.5441 | -0.41199 | -0.073242 | 0.073242 | 122.6074 | -0.43945 | -0.41199 | 0.009156 | 0.48523 | 102.6169 | 102.0309 | 122.287 | 122.6532 | 0.073242 | 122.7356 | 110.4904 | -0.41199 | 122.6532 | 0.073242 | 110.4904 | 122.287 | 122.7356 | -123.1384 | -123.1384
2127.9531 | 123.0194 | -114.4363 | 8.3496 | -0.11032 | -0.00018804 | 0.0023862 | 0.014582 | -0.00668 | -0.00093346 | 0.0029843 | -114.1937 | 8.2993 | -114.6469 | 8.4 | 8.1024 | -4.2068 | -12.4924 | -12.5565 | 8.3817 | -114.6698 | -0.21057 | -0.050354 | 0.24261 | 122.8363 | -0.24719 | -0.23346 | 0.032044 | 0.45319 | 101.944 | 101.8799 | 122.5388 | 122.7356 | 0.24261 | 122.818 | 110.2295 | -0.23346 | 122.7356 | 0.24261 | 110.2295 | 122.5388 | 122.818 | -122.9965 | -123.0194
2128.9062 | 122.9141 | -115.329 | 7.4936 | -0.2095 | 0.0010938 | 0.0040952 | 0.022272 | -0.0068936 | -0.0039243 | 0.00042086 | -115.1413 | 7.4249 | -115.6082 | 7.3883 | 7.0862 | -4.2068 | -12.291 | -12.4969 | 7.5165 | -115.5991 | -0.27924 | -0.068664 | 0.18768 | 122.7173 | -0.40741 | -0.27008 | 0.022888 | 0.46692 | 103.038 | 102.832 | 122.4152 | 122.7539 | 0.18768 | 122.8455 | 111.1221 | -0.27008 | 122.7539 | 0.18768 | 111.1221 | 122.4152 | 122.8455 | -123.1018 | -123.0927
2129.9688 | 122.8592 | -113.1775 | 9.4666 | -0.11032 | 0.0057934 | 0.0094358 | 0.02569 | -0.002194 | -0.0024289 | 0.0053343 | -113.4888 | 9.8099 | -113.6856 | 8.8028 | 8.6975 | -4.1153 | -12.5244 | -12.2864 | 9.0408 | -113.8321 | -0.50812 | 0.34332 | -0.31128 | 121.9803 | -0.76904 | -0.6546 | -0.42572 | 0.19684 | 100.6531 | 100.8911 | 121.875 | 122.9874 | -0.31128 | 122.2183 | 109.0622 | -0.6546 | 122.9874 | -0.31128 | 109.0622 | 121.875 | 122.2183 | -123.1522 | -123.2986
2130.9062 | 122.8729 | -115.5853 | 7.2144 | -0.072174 | -0.0010424 | 0.001959 | 0.015436 | -0.0047574 | -0.0037107 | 0.0010617 | -115.4114 | 7.1594 | -115.8829 | 7.0404 | 6.8024 | -3.9047 | -12.8952 | -12.9227 | 7.2281 | -115.9012 | -0.29755 | -0.054931 | 0.17395 | 122.6257 | -0.41199 | -0.31586 | 0.013733 | 0.4715 | 102.6901 | 102.6627 | 122.3877 | 122.7448 | 0.17395 | 122.8134 | 111.6806 | -0.31586 | 122.7448 | 0.17395 | 111.6806 | 122.3877 | 122.8134 | -123.0972 | -123.1155
2131.9531 | 122.8546 | -115.0955 | 7.5806 | -0.56808 | 0.0025892 | 0.0045224 | 0.017786 | -0.0051846 | -0.00071986 | 0.0036253 | -115.036 | 7.5943 | -115.3473 | 7.4341 | 7.1457 | -4.1382 | -12.6801 | -12.822 | 7.6447 | -115.5258 | -0.25177 | 0.013733 | 0.059509 | 122.5296 | -0.43487 | -0.4303 | 0.064087 | 0.31128 | 102.4155 | 102.2736 | 122.2412 | 122.6898 | 0.059509 | 122.7402 | 110.9573 | -0.4303 | 122.6898 | 0.059509 | 110.9573 | 122.2412 | 122.7402 | -122.9279 | -123.1064
2132.9062 | 122.8592 | -111.3144 | 10.5286 | -0.26291 | 0.00066656 | 0.00067718 | 0.016718 | -0.0053982 | -0.0011471 | 0.0031979 | -102.4384 | 20.0546 | -102.594 | 11.4716 | 11.0046 | -7.4158 | -13.7421 | -13.4674 | 11.9476 | -111.3693 | 8.7204 | 9.5261 | 8.876 | 122.7859 | 0.47607 | -0.054932 | 1.4191 | 0.15564 | 97.5723 | 97.847 | 122.319 | 131.369 | 8.876 | 123.262 | 103.8986 | -0.054932 | 131.369 | 8.876 | 103.8986 | 122.319 | 123.262 | -113.1226 | -121.8979
2133.9688 | 122.9874 | -116.2354 | 6.4362 | -0.1561 | 0.0025892 | -0.0010318 | 0.013086 | -0.0060392 | 0.00077554 | 0.0034115 | -116.0477 | 6.4545 | -116.5054 | 6.4133 | 6.1661 | -4.0421 | -13.2339 | -12.8998 | 6.4682 | -116.6245 | -0.27008 | 0.018311 | 0.18768 | 122.6486 | -0.27008 | -0.3891 | 0.032044 | 0.45776 | 103.0014 | 103.3356 | 122.4014 | 122.6898 | 0.18768 | 122.7036 | 112.1933 | -0.3891 | 122.6898 | 0.18768 | 112.1933 | 122.4014 | 122.7036 | -122.9416 | -123.0606
2134.9062 | 122.9233 | -116.2857 | 6.4316 | 0.17197 | 0.0025892 | 0.003027 | 0.023981 | -0.0028348 | -0.0011471 | 0.0042661 | -116.2216 | 6.3583 | -116.6885 | 6.2897 | 6.0471 | -4.1794 | -13.1149 | -13.2523 | 6.4362 | -116.6885 | -0.40283 | -0.073243 | 0.064087 | 122.5754 | -0.38452 | -0.40283 | 0.004577 | 0.46692 | 103.1708 | 103.0334 | 122.3328 | 122.644 | 0.064087 | 122.7219 | 112.1063 | -0.40283 | 122.644 | 0.064087 | 112.1063 | 122.3328 | 122.7219 | -123.1201 | -123.1201
2135.9688 | 122.9782 | -113.9374 | 8.6975 | -0.17136 | 0.0013074 | 0.00024998 | 0.020777 | -0.004971 | -0.0024289 | 0.0042661 | -113.0127 | 8.8303 | -113.9969 | 8.7936 | 8.2397 | -3.8635 | -12.4741 | -12.3093 | 8.6746 | -114.2807 | -0.059509 | 0.13275 | 0.92468 | 122.731 | -0.45776 | -0.34332 | -0.022888 | 0.98419 | 101.4633 | 101.6281 | 122.1771 | 122.7676 | 0.92468 | 122.612 | 110.0739 | -0.34332 | 122.7676 | 0.92468 | 110.0739 | 122.1771 | 122.612 | -122.6944 | -122.9782
2136.9062 | 122.9233 | -115.6082 | 7.1274 | -0.25528 | 0.00088016 | 0.0040952 | 0.016932 | -0.00668 | -0.0017881 | 0.0034115 | -115.5762 | 7.0129 | -116.0477 | 6.958 | 6.6696 | -3.7903 | -12.7213 | -12.7945 | 7.077 | -115.9836 | -0.43945 | -0.11444 | 0.032043 | 122.5662 | -0.45776 | -0.37537 | -0.050354 | 0.4715 | 102.887 | 102.8137 | 122.2778 | 122.6212 | 0.032043 | 122.6852 | 111.8179 | -0.37537 | 122.6212 | 0.032043 | 111.8179 | 122.2778 | 122.6852 | -123.175 | -123.111
2137.9688 | 122.8867 | -115.4114 | 7.338 | -0.30106 | 0.00066656 | 0.003668 | 0.017786 | -0.0053982 | -0.0028561 | 0.00084806 | -115.1596 | 7.3654 | -115.6494 | 7.3517 | 7.0633 | -3.7903 | -12.7762 | -12.6617 | 7.4478 | -115.7501 | -0.23804 | 0.027465 | 0.25177 | 122.7631 | -0.27466 | -0.33875 | 0.10986 | 0.48981 | 102.6352 | 102.7496 | 122.4747 | 122.7768 | 0.25177 | 122.8592 | 111.6211 | -0.33875 | 122.7768 | 0.25177 | 111.6211 | 122.4747 | 122.8592 | -122.9874 | -123.0881
2138.9062 | 122.8592 | -115.9332 | 6.8573 | -0.079803 | 0.002162 | 0.001959 | 0.019495 | -0.0051846 | -0.0041379 | 0.0034115 | -115.8508 | 6.7612 | -116.2537 | 6.6788 | 6.4041 | -4.1656 | -12.941 | -12.8815 | 6.871 | -116.2811 | -0.32043 | -0.096131 | 0.082398 | 122.612 | -0.45319 | -0.3479 | 0.013733 | 0.40283 | 102.9922 | 103.0518 | 122.3373 | 122.6944 | 0.082398 | 122.8043 | 111.7676 | -0.3479 | 122.6944 | 0.082398 | 111.7676 | 122.3373 | 122.8043 | -123.111 | -123.1384
2139.9688 | 122.8775 | -115.4251 | 7.2601 | -0.011139 | 0.0051526 | 0.0077268 | 0.023981 | -0.0043302 | -0.0013609 | 0.0025571 | -115.3061 | 7.2372 | -115.8371 | 7.1777 | 6.871 | -4.0649 | -13.0508 | -12.8632 | 7.2876 | -115.8463 | -0.41199 | -0.022888 | 0.11902 | 122.6028 | -0.3891 | -0.42114 | 0.027466 | 0.53101 | 102.3743 | 102.562 | 122.2961 | 122.6624 | 0.11902 | 122.7127 | 111.3602 | -0.42114 | 122.6624 | 0.11902 | 111.3602 | 122.2961 | 122.7127 | -123.0972 | -123.1064
2140.9062 | 122.8821 | -116.835 | 5.9418 | -0.14084 | 0.00088016 | 0.0038816 | 0.021204 | -0.0024076 | -0.0045651 | 0.0017027 | -116.7435 | 5.8548 | -117.215 | 5.7587 | 5.4932 | -4.3076 | -13.1012 | -13.0966 | 5.9418 | -117.16 | -0.37994 | -0.086975 | 0.091553 | 122.5937 | -0.44861 | -0.32501 | 0 | 0.4715 | 103.7338 | 103.7384 | 122.3282 | 122.6898 | 0.091553 | 122.7768 | 112.5275 | -0.32501 | 122.6898 | 0.091553 | 112.5275 | 122.3282 | 122.7768 | -123.1567 | -123.1018
2141.9688 | 122.9645 | -115.8417 | 6.8848 | -1.7278 | 0.0017346 | 0.005377 | 0.014582 | -0.0013394 | -0.0022153 | 0.0027707 | -115.8783 | 6.7657 | -116.2308 | 6.8619 | 6.5872 | -4.1382 | -12.886 | -13.1012 | 6.8802 | -116.2125 | -0.3891 | -0.11902 | -0.036621 | 122.7036 | -0.29755 | -0.37079 | -0.004578 | 0.35248 | 102.9556 | 102.7405 | 122.4289 | 122.6074 | -0.036621 | 122.7219 | 111.7035 | -0.37079 | 122.6074 | -0.036621 | 111.7035 | 122.4289 | 122.7219 | -123.1155 | -123.0972
2142.9062 | 122.9004 | -116.153 | 6.6101 | -0.2095 | 0.0034436 | 0.0051632 | 0.022059 | -0.0013394 | -0.0047787 | 0.0029843 | -116.011 | 6.5826 | -116.51 | 6.4819 | 6.2073 | -4.3213 | -12.7396 | -13.4079 | 6.6422 | -116.4871 | -0.35706 | -0.027465 | 0.14191 | 122.6349 | -0.40283 | -0.33417 | 0.032044 | 0.49896 | 103.4134 | 102.7451 | 122.3602 | 122.7356 | 0.14191 | 122.7951 | 111.8317 | -0.33417 | 122.7356 | 0.14191 | 111.8317 | 122.3602 | 122.7951 | -123.1201 | -123.0972
2143.9531 | 122.9782 | -116.9266 | 5.8594 | 0.011749 | 0.00088016 | 0.0055906 | 0.012232 | -0.004971 | -0.0011471 | 0.0046933 | -116.716 | 5.7266 | -117.247 | 5.7816 | 5.5481 | -4.216 | -12.8082 | -13.2706 | 5.8502 | -117.2104 | -0.32043 | -0.13275 | 0.21057 | 122.7081 | -0.31128 | -0.28381 | -0.009155 | 0.53101 | 104.1183 | 103.656 | 122.4747 | 122.6532 | 0.21057 | 122.7768 | 112.7106 | -0.28381 | 122.6532 | 0.21057 | 112.7106 | 122.4747 | 122.7768 | -123.1064 | -123.0698
2144.9062 | 122.9141 | -115.4251 | 7.37 | -0.11032 | 0.001521 | 0.008154 | 0.020991 | -0.0043302 | -0.0039243 | 0.0021299 | -115.2878 | 7.2464 | -115.7867 | 7.2144 | 6.926 | -4.0466 | -12.6663 | -12.9913 | 7.3563 | -115.7501 | -0.36163 | -0.1236 | 0.13733 | 122.6395 | -0.44403 | -0.32501 | -0.013733 | 0.49896 | 102.7588 | 102.4338 | 122.3511 | 122.6715 | 0.13733 | 122.7814 | 111.3785 | -0.32501 | 122.6715 | 0.13733 | 111.3785 | 122.3511 | 122.7814 | -123.1567 | -123.1201
2145.9531 | 122.9233 | -116.1255 | 6.6238 | 0.011749 | -0.00061524 | 0.00024998 | 0.012232 | -0.0056118 | -0.0013609 | 0.0057615 | -115.9882 | 6.5826 | -116.4322 | 6.4407 | 6.2256 | -4.2526 | -12.5793 | -13.3987 | 6.5964 | -116.4276 | -0.3067 | -0.041198 | 0.13733 | 122.5662 | -0.39825 | -0.30212 | -0.027465 | 0.44403 | 103.5461 | 102.7267 | 122.3511 | 122.7081 | 0.13733 | 122.7219 | 111.8729 | -0.30212 | 122.7081 | 0.13733 | 111.8729 | 122.3511 | 122.7219 | -123.056 | -123.0515
2146.9062 | 122.8775 | -116.3681 | 6.4224 | 0.89676 | 0.0051526 | 0.003027 | 0.019709 | -0.0043302 | 0.00056194 | 0.0027707 | -116.2216 | 6.3721 | -116.716 | 6.2531 | 5.983 | -4.3762 | -12.973 | -13.7695 | 6.4362 | -116.7252 | -0.3479 | -0.050354 | 0.14648 | 122.6212 | -0.43945 | -0.35706 | 0.013733 | 0.49438 | 103.3951 | 102.5986 | 122.3511 | 122.7402 | 0.14648 | 122.8043 | 111.9919 | -0.35706 | 122.7402 | 0.14648 | 111.9919 | 122.3511 | 122.8043 | -123.1384 | -123.1476
2147.9531 | 122.8546 | -115.1276 | 7.5851 | -0.16373 | 0.00045296 | 0.0034544 | 0.017573 | -0.0045438 | -0.0017881 | 0.0038389 | -114.9948 | 7.5348 | -115.4709 | 7.4844 | 7.2006 | -4.0833 | -12.8494 | -13.4583 | 7.6355 | -115.5167 | -0.34332 | -0.050354 | 0.13275 | 122.612 | -0.38452 | -0.3891 | 0.050354 | 0.47607 | 102.2781 | 101.6693 | 122.3282 | 122.6624 | 0.13275 | 122.7631 | 111.0443 | -0.3891 | 122.6624 | 0.13275 | 111.0443 | 122.3282 | 122.7631 | -123.056 | -123.1018
2148.9062 | 122.8271 | -114.9445 | 7.7591 | -0.17899 | 2.5564e-05 | 0.0017454 | 0.016077 | -0.0041166 | -0.0020017 | 0.0023435 | -114.9033 | 7.7042 | -115.3519 | 7.8415 | 7.4112 | -4.2068 | -13.1699 | -13.6459 | 7.7957 | -115.3519 | -0.40741 | -0.054931 | 0.041199 | 122.7859 | -0.3479 | -0.40741 | 0.036621 | 0.44861 | 101.7746 | 101.2985 | 122.3557 | 122.6486 | 0.041199 | 122.7402 | 110.7376 | -0.40741 | 122.6486 | 0.041199 | 110.7376 | 122.3557 | 122.7402 | -123.111 | -123.111
2149.9688 | 122.9874 | -115.4434 | 7.2327 | -0.041657 | 0.0010938 | 0.0058042 | 0.015436 | -0.0058256 | -0.0022153 | 0.0021299 | -115.3107 | 7.2372 | -115.7959 | 7.1869 | 6.926 | -4.1382 | -13.0463 | -13.6871 | 7.2327 | -115.8554 | -0.35248 | 0.004578 | 0.13275 | 122.6303 | -0.3067 | -0.41199 | 0 | 0.48523 | 102.3972 | 101.7563 | 122.3694 | 122.6807 | 0.13275 | 122.6761 | 111.3052 | -0.41199 | 122.6807 | 0.13275 | 111.3052 | 122.3694 | 122.6761 | -123.0286 | -123.0881
2150.9062 | 122.8729 | -113.9191 | 8.7753 | -0.36972 | 0.00323 | 0.0021726 | 0.017573 | -0.0064664 | -0.0015745 | 0.0023435 | -113.8733 | 8.7341 | -114.3173 | 8.6563 | 8.3359 | -4.216 | -12.3825 | -13.3347 | 8.8165 | -114.3677 | -0.39826 | -0.041199 | 0.045776 | 122.5754 | -0.43945 | -0.44861 | 0.041198 | 0.44403 | 101.5366 | 100.5844 | 122.2549 | 122.6532 | 0.045776 | 122.7356 | 109.7031 | -0.44861 | 122.6532 | 0.045776 | 109.7031 | 122.2549 | 122.7356 | -123.0927 | -123.143
2151.9531 | 122.9828 | -115.6952 | 6.9901 | 0.0041197 | 2.5564e-05 | 0.0011044 | 0.014795 | -0.0043302 | 0.00056194 | 0.0038389 | -115.6586 | 6.8756 | -116.1346 | 6.8848 | 6.6238 | -4.0009 | -13.1882 | -13.504 | 6.9626 | -116.1072 | -0.43945 | -0.11444 | 0.036621 | 122.58 | -0.36621 | -0.41199 | -0.027466 | 0.47607 | 102.507 | 102.1912 | 122.319 | 122.5708 | 0.036621 | 122.6578 | 111.6943 | -0.41199 | 122.5708 | 0.036621 | 111.6943 | 122.319 | 122.6578 | -123.1247 | -123.0972
2152.9062 | 122.8683 | -116.4185 | 6.3766 | -0.4689 | 0.00088016 | 0.0055906 | 0.017573 | -0.0062528 | -0.0015745 | 0.0012753 | -116.2445 | 6.34 | -116.7526 | 6.2119 | 5.9463 | -4.4861 | -13.2431 | -13.9297 | 6.3812 | -116.7526 | -0.33417 | -0.036621 | 0.17395 | 122.6303 | -0.4303 | -0.33417 | 0.004578 | 0.50812 | 103.1754 | 102.4887 | 122.3648 | 122.7585 | 0.17395 | 122.7997 | 111.9324 | -0.33417 | 122.7585 | 0.17395 | 111.9324 | 122.3648 | 122.7997 | -123.1293 | -123.1293
2153.9531 | 122.9645 | -115.686 | 6.8939 | -0.13321 | 0.0023756 | 0.003668 | 0.014582 | -0.0045438 | -0.0011471 | -6.342e-06 | -115.448 | 6.9534 | -116.0202 | 7.1503 | 6.839 | -4.4403 | -12.9135 | -13.9664 | 6.9946 | -116.1163 | -0.33417 | 0.059509 | 0.23804 | 122.8363 | -0.054932 | -0.4303 | 0.10071 | 0.5722 | 102.7725 | 101.7197 | 122.525 | 122.6395 | 0.23804 | 122.6807 | 111.2457 | -0.4303 | 122.6395 | 0.23804 | 111.2457 | 122.525 | 122.6807 | -122.9141 | -123.0103
2154.9062 | 122.8912 | -114.4226 | 8.2581 | -0.20187 | 0.0028028 | 0.0068722 | 0.022059 | -0.0045438 | -0.0017881 | 0.0031979 | -114.3082 | 8.2581 | -114.7934 | 8.139 | 7.8094 | -4.3991 | -12.7533 | -13.9572 | 8.2764 | -114.8941 | -0.37079 | 0 | 0.11444 | 122.5616 | -0.44861 | -0.4715 | 0.01831 | 0.48523 | 101.6693 | 100.4654 | 122.2321 | 122.6807 | 0.11444 | 122.699 | 110.0235 | -0.4715 | 122.6807 | 0.11444 | 110.0235 | 122.2321 | 122.699 | -123.0515 | -123.1522
2155.9531 | 104.3655 | -115.741 | 6.871 | -0.087433 | 2.5564e-05 | 0.0049496 | 0.014582 | -0.0053982 | -0.0034971 | 0.0025571 | -115.6906 | 6.8069 | -116.1987 | 6.9077 | 6.6055 | -4.3579 | -13.2385 | -14.0945 | 6.8848 | -116.1758 | -0.45776 | -0.064087 | 0.050354 | 122.6486 | -0.2655 | -0.43488 | 0.013733 | 0.50812 | 102.5024 | 101.6464 | 122.3465 | 122.5479 | 0.050354 | 122.6257 | 111.3831 | -0.43488 | 122.5479 | 0.050354 | 111.3831 | 122.3465 | 122.6257 | -123.0698 | -123.0469
2156.9062 | 122.9279 | -115.9058 | 6.7566 | -0.23239 | -0.00040164 | 0.003668 | 0.018641 | -0.0064664 | -0.0032835 | 0.0046933 | -115.7547 | 6.7017 | -116.185 | 6.7291 | 6.5002 | -4.5227 | -12.9776 | -14.241 | 6.8161 | -116.3315 | -0.27924 | -0.054932 | 0.15106 | 122.6349 | -0.25635 | -0.42572 | 0.059509 | 0.4303 | 102.9282 | 101.6647 | 122.406 | 122.6074 | 0.15106 | 122.7219 | 111.3831 | -0.42572 | 122.6074 | 0.15106 | 111.3831 | 122.406 | 122.7219 | -122.9416 | -123.0881
2157.9531 | 123.0011 | -117.0456 | 5.6168 | -0.079803 | -0.00040164 | 0.0077268 | 0.015223 | -0.0062528 | 0.00056194 | 0.0029843 | -116.8945 | 5.5847 | -117.4026 | 5.6122 | 5.3513 | -4.5364 | -13.1378 | -14.296 | 5.6534 | -117.4026 | -0.35706 | -0.032043 | 0.15106 | 122.6578 | -0.2655 | -0.35706 | 0.036621 | 0.50812 | 103.9078 | 102.7496 | 122.3969 | 122.6303 | 0.15106 | 122.699 | 112.5092 | -0.35706 | 122.6303 | 0.15106 | 112.5092 | 122.3969 | 122.699 | -123.0194 | -123.0194
2158.9062 | 122.8592 | -117.0364 | 5.722 | -0.29343 | 0.00045296 | -0.00081822 | 0.017786 | -0.0062528 | -0.0013609 | 0.0042661 | -116.9083 | 5.6671 | -117.3935 | 5.5756 | 5.3375 | -4.5319 | -12.8311 | -14.1541 | 5.7541 | -117.3752 | -0.35706 | -0.054932 | 0.12817 | 122.612 | -0.38452 | -0.33875 | 0.032043 | 0.48523 | 104.2053 | 102.8824 | 122.374 | 122.7036 | 0.12817 | 122.7905 | 112.5046 | -0.33875 | 122.7036 | 0.12817 | 112.5046 | 122.374 | 122.7905 | -123.1155 | -123.0972
2159.9688 | 123.5641 | -84.4574 | 37.294 | 0.16434 | 0.00088016 | 0.0011044 | 0.019495 | -0.0026212 | 0.00077554 | 0.0042661 | -86.9431 | 32.4921 | -90.0375 | 30.7663 | 26.3947 | -3.0304 | -0.17853 | -8.8852 | 34.1629 | -87.0758 | -5.5801 | -4.8019 | -2.4857 | 115.2237 | -10.8994 | -2.6184 | -3.1311 | 3.0945 | 84.2789 | 75.5722 | 110.8521 | 116.9495 | -2.4857 | 118.6203 | 81.427 | -2.6184 | 116.9495 | -2.4857 | 81.427 | 110.8521 | 118.6203 | -127.3315 | -124.3698
2160.9062 | 122.8226 | -114.5737 | 8.1665 | -0.2858 | 0.00066656 | 0.0058042 | 0.021418 | -0.004971 | -0.0024289 | 0.0025571 | -114.4547 | 8.0292 | -114.8529 | 8.0154 | 7.7408 | -4.8752 | -12.9318 | -14.209 | 8.1802 | -114.9673 | -0.27924 | -0.13733 | 0.11902 | 122.5891 | -0.42572 | -0.39368 | 0.013733 | 0.39825 | 101.6418 | 100.3647 | 122.3145 | 122.6028 | 0.11902 | 122.7539 | 109.6985 | -0.39368 | 122.6028 | 0.11902 | 109.6985 | 122.3145 | 122.7539 | -123.0194 | -123.1339
2161.9531 | 123.0148 | -108.9066 | 13.678 | -0.095062 | 0.0013074 | 0.003668 | 0.014795 | -0.0058256 | 0.00077554 | 0.0031979 | -108.5632 | 13.9893 | -109.0805 | 13.7833 | 13.3347 | -4.0375 | -11.9751 | -12.9501 | 13.7421 | -109.1949 | -0.17395 | 0.31128 | 0.34332 | 122.6898 | -0.34332 | -0.28839 | 0.064086 | 0.51727 | 96.9315 | 95.9564 | 122.2412 | 122.8958 | 0.34332 | 122.6486 | 104.8691 | -0.28839 | 122.8958 | 0.34332 | 104.8691 | 122.2412 | 122.6486 | -122.7585 | -122.8729
2162.9062 | 122.8592 | -115.6403 | 7.0496 | -0.2858 | 0.0038708 | 0.0034544 | 0.022272 | -0.0051846 | -0.0013609 | 0.0029843 | -115.7455 | 7.0221 | -116.1072 | 6.9397 | 6.9305 | -4.6051 | -12.8174 | -14.0854 | 7.132 | -116.066 | -0.46692 | -0.027466 | -0.10528 | 122.58 | -0.11902 | -0.42572 | 0.082397 | 0.36163 | 102.8229 | 101.5549 | 122.5708 | 122.6624 | -0.10528 | 122.7722 | 111.0352 | -0.42572 | 122.6624 | -0.10528 | 111.0352 | 122.5708 | 122.7722 | -123.1567 | -123.1155
2163.9531 | 122.9553 | -117.247 | 5.3787 | -0.25528 | 0.00045296 | 0.0023862 | 0.017573 | -0.0060392 | -0.0015745 | 0.0019163 | -117.1646 | 5.3375 | -117.6865 | 5.3284 | 5.0995 | -4.8981 | -13.3072 | -14.9185 | 5.3925 | -117.6819 | -0.43945 | -0.041199 | 0.082397 | 122.5754 | -0.27924 | -0.43488 | 0.013733 | 0.52185 | 103.9398 | 102.3285 | 122.3465 | 122.5845 | 0.082397 | 122.6395 | 112.3489 | -0.43488 | 122.5845 | 0.082397 | 112.3489 | 122.3465 | 122.6395 | -123.0652 | -123.0606
2164.9062 | 122.9095 | -114.8941 | 7.7316 | -0.23239 | 0.00323 | 0.008154 | 0.022913 | -0.0079618 | -0.0015745 | -0.00021994 | -114.8346 | 7.7042 | -115.3564 | 7.663 | 7.3563 | -4.6783 | -12.5748 | -14.6393 | 7.7591 | -115.3748 | -0.46234 | -0.027465 | 0.059509 | 122.5571 | -0.37537 | -0.48065 | 0.027466 | 0.52185 | 102.3193 | 100.2548 | 122.2504 | 122.5983 | 0.059509 | 122.6532 | 110.2158 | -0.48065 | 122.5983 | 0.059509 | 110.2158 | 122.2504 | 122.6532 | -123.0881 | -123.1064
2165.9688 | 122.9736 | -116.5558 | 6.1203 | 0.19485 | 0.001521 | 0.0068722 | 0.017145 | -0.0019802 | -0.0015745 | 0.0049069 | -116.4276 | 6.0333 | -116.9312 | 6.0699 | 5.8273 | -4.6234 | -13.0554 | -14.5889 | 6.1432 | -116.9266 | -0.37537 | -0.086975 | 0.12817 | 122.6257 | -0.29297 | -0.37079 | 0.022888 | 0.50354 | 103.5004 | 101.9669 | 122.3831 | 122.5891 | 0.12817 | 122.699 | 111.9324 | -0.37079 | 122.5891 | 0.12817 | 111.9324 | 122.3831 | 122.699 | -123.0515 | -123.0469
2166.9062 | 122.8912 | -117.0319 | 5.7541 | -0.26291 | 0.0017346 | 0.0043088 | 0.016718 | -0.0053982 | -0.0024289 | 0.0029843 | -116.89 | 5.6534 | -117.4072 | 5.6168 | 5.3879 | -4.7195 | -13.0508 | -14.74 | 5.777 | -117.3569 | -0.37537 | -0.10071 | 0.14191 | 122.6486 | -0.36621 | -0.32501 | 0.022889 | 0.51727 | 103.981 | 102.2919 | 122.4197 | 122.6852 | 0.14191 | 122.8088 | 112.3123 | -0.32501 | 122.6852 | 0.14191 | 112.3123 | 122.4197 | 122.8088 | -123.1613 | -123.111
2167.9688 | 122.9507 | -115.036 | 7.6263 | 0.11856 | -0.00061524 | 0.0011044 | 0.013727 | -0.00668 | -0.0030697 | 0.0044797 | -114.9216 | 7.608 | -115.3702 | 7.6263 | 7.2784 | -4.4724 | -12.8632 | -14.4928 | 7.6309 | -115.416 | -0.33417 | -0.018311 | 0.11444 | 122.6624 | -0.3479 | -0.37994 | 0.004577 | 0.44861 | 102.1729 | 100.5432 | 122.3145 | 122.644 | 0.11444 | 122.6669 | 110.5637 | -0.37994 | 122.644 | 0.11444 | 110.5637 | 122.3145 | 122.6669 | -122.9965 | -123.0423
2168.9062 | 122.9233 | -116.6153 | 6.0699 | -0.2858 | 0.00023916 | 0.0032406 | 0.016504 | -0.00668 | -0.0020017 | 0.0036253 | -116.5466 | 5.9463 | -117.0547 | 5.9555 | 5.6946 | -4.5181 | -13.0875 | -14.8224 | 6.0699 | -117.0547 | -0.43945 | -0.1236 | 0.068664 | 122.5708 | -0.37537 | -0.43945 | 0 | 0.50812 | 103.5278 | 101.7929 | 122.3099 | 122.5616 | 0.068664 | 122.6852 | 112.0972 | -0.43945 | 122.5616 | 0.068664 | 112.0972 | 122.3099 | 122.6852 | -123.1247 | -123.1247
2169.9688 | 122.905 | -116.2903 | 6.4819 | -0.22476 | 0.0038708 | 0.0062314 | 0.020136 | -0.0098844 | -7.9062e-05 | 0.0029843 | -116.0843 | 6.3858 | -116.6199 | 6.3904 | 6.1111 | -4.3716 | -12.3047 | -14.946 | 6.5048 | -116.6611 | -0.32959 | -0.096131 | 0.20599 | 122.6807 | -0.37079 | -0.37079 | 0.022888 | 0.53558 | 103.9856 | 101.3443 | 122.4014 | 122.6761 | 0.20599 | 122.7951 | 111.9186 | -0.37079 | 122.6761 | 0.20599 | 111.9186 | 122.4014 | 122.7951 | -123.1018 | -123.143
2170.9062 | 123.0286 | -114.4592 | 8.1619 | -0.087433 | -0.00040164 | 0.0043088 | 0.014368 | -0.0060392 | -0.0020017 | 0.0038389 | -114.3448 | 8.1345 | -114.8575 | 8.194 | 7.8735 | -4.1656 | -12.7808 | -14.6988 | 8.194 | -114.8392 | -0.39825 | -0.027466 | 0.11444 | 122.6532 | -0.28839 | -0.37994 | 0.032044 | 0.5127 | 101.6785 | 99.7604 | 122.3328 | 122.5937 | 0.11444 | 122.6532 | 110.2936 | -0.37994 | 122.5937 | 0.11444 | 110.2936 | 122.3328 | 122.6532 | -123.0194 | -123.0011
2171.9688 | 122.9965 | -114.9124 | 7.7866 | -0.041657 | 0.00066656 | 0.0015316 | 0.016077 | -0.0062528 | -0.00093346 | 0.0057615 | -114.8392 | 7.6355 | -115.3427 | 7.7774 | 7.5073 | -4.1016 | -12.3138 | -14.6713 | 7.7911 | -115.2328 | -0.4303 | -0.15106 | 0.073243 | 122.6898 | -0.27924 | -0.32043 | 0.004578 | 0.50354 | 102.5986 | 100.2411 | 122.4197 | 122.5479 | 0.073243 | 122.7036 | 110.8109 | -0.32043 | 122.5479 | 0.073243 | 110.8109 | 122.4197 | 122.7036 | -123.1293 | -123.0194
2172.9062 | 122.8821 | -115.3976 | 7.3242 | -0.24765 | -0.001256 | 0.0051632 | 0.017573 | -0.0060392 | -0.0011471 | 0.0023435 | -115.2191 | 7.2372 | -115.7318 | 7.2556 | 6.9901 | -4.4083 | -12.4786 | -15.2023 | 7.338 | -115.7501 | -0.33417 | -0.086975 | 0.17853 | 122.6532 | -0.33417 | -0.35248 | 0.013733 | 0.5127 | 102.919 | 100.1953 | 122.3877 | 122.6349 | 0.17853 | 122.7356 | 110.9894 | -0.35248 | 122.6349 | 0.17853 | 110.9894 | 122.3877 | 122.7356 | -123.056 | -123.0743
2173.9688 | 122.937 | -114.7934 | 7.7866 | 0.027008 | 2.5564e-05 | 0.003668 | 0.015436 | -0.0045438 | 0.00013454 | 0.0023435 | -114.6011 | 7.8461 | -115.0864 | 7.7087 | 7.4387 | -4.541 | -12.4008 | -15.4175 | 7.8598 | -115.2237 | -0.29297 | 0.059509 | 0.19226 | 122.5021 | -0.3479 | -0.4303 | 0.073242 | 0.48523 | 102.3926 | 99.3759 | 122.2321 | 122.6395 | 0.19226 | 122.6532 | 110.2524 | -0.4303 | 122.6395 | 0.19226 | 110.2524 | 122.2321 | 122.6532 | -122.8729 | -123.0103
2174.9062 | 122.8958 | -113.9099 | 8.8577 | -0.095062 | 0.0025892 | 0.011572 | 0.026331 | -0.0047574 | -0.0017881 | 0.0078977 | -113.324 | 8.8348 | -114.1113 | 9.5993 | 9.2239 | -3.7216 | -12.0758 | -15.9439 | 9.3658 | -114.2395 | -0.20142 | -0.022888 | 0.58594 | 123.5092 | 0.36621 | -0.32959 | 0.50812 | 0.78735 | 101.8341 | 97.966 | 123.1339 | 122.7448 | 0.58594 | 123.2758 | 110.1883 | -0.32959 | 122.7448 | 0.58594 | 110.1883 | 123.1339 | 123.2758 | -122.9691 | -123.0972
2175.9531 | 122.9965 | -114.093 | 8.5922 | 0.057526 | -0.00061524 | 0.0032406 | 0.016932 | -0.0045438 | -0.0013609 | 0.0096067 | -114.4913 | 7.9147 | -115.0177 | 8.5693 | 8.3862 | -4.1931 | -12.2223 | -14.2593 | 8.5922 | -114.4363 | -0.92468 | -0.67749 | -0.39825 | 122.6624 | -0.20599 | -0.34332 | 0 | 0.52643 | 101.8707 | 99.8337 | 122.4792 | 122.0078 | -0.39825 | 122.6852 | 109.8999 | -0.34332 | 122.0078 | -0.39825 | 109.8999 | 122.4792 | 122.6852 | -123.6099 | -123.0286
2176.9062 | 95.0546 | -111.6257 | 11.0001 | -0.026398 | 0.00066656 | 0.00067718 | 0.016291 | -0.0068936 | -0.0028561 | 0.0021299 | -111.5982 | 10.9039 | -111.8546 | 11.0229 | 11.0001 | -4.1748 | -11.6501 | -14.1083 | 11.0733 | -112.001 | -0.22888 | -0.09613 | 0.027465 | 122.6486 | 0 | -0.37537 | 0.073242 | 0.25635 | 99.9756 | 97.5174 | 122.6257 | 122.5296 | 0.027465 | 122.699 | 107.4509 | -0.37537 | 122.5296 | 0.027465 | 107.4509 | 122.6257 | 122.699 | -122.8546 | -123.0011
2177.9688 | 123.0011 | -116.597 | 5.9509 | -0.17899 | 0.0013074 | 0.0034544 | 0.019282 | -0.00668 | -0.0026425 | 0.0049069 | -116.5237 | 5.7495 | -117.0502 | 6.2256 | 5.4977 | -4.8019 | -13.0051 | -15.1337 | 6.1615 | -117.0914 | -0.45319 | -0.20142 | 0.073242 | 122.8226 | -0.45319 | -0.49438 | 0.21057 | 0.52643 | 103.5919 | 101.4633 | 122.0947 | 122.3465 | 0.073242 | 122.7585 | 111.795 | -0.49438 | 122.3465 | 0.073242 | 111.795 | 122.0947 | 122.7585 | -123.0011 | -123.0423
2178.9062 | 123.0011 | -115.0177 | 7.6538 | -0.14847 | -0.00040164 | 0.00046358 | 0.015009 | -0.012661 | -0.0024289 | 0.0053343 | -114.8392 | 7.608 | -115.3793 | 7.5027 | 7.2281 | -4.3259 | -12.2223 | -14.8499 | 7.6721 | -115.3519 | -0.36163 | -0.045777 | 0.17853 | 122.5204 | -0.42572 | -0.33417 | 0.01831 | 0.54016 | 102.7954 | 100.1678 | 122.2458 | 122.6257 | 0.17853 | 122.6898 | 110.6918 | -0.33417 | 122.6257 | 0.17853 | 110.6918 | 122.2458 | 122.6898 | -123.0331 | -123.0057
2179.9688 | 122.9782 | -114.9353 | 7.7179 | 0.027008 | 0.0036572 | 0.003027 | 0.022272 | -0.0060392 | -0.0015745 | 0.0093931 | -114.949 | 7.5577 | -115.4205 | 7.6263 | 7.3334 | -4.4083 | -12.6389 | -14.8224 | 7.6996 | -115.3244 | -0.48523 | -0.16022 | -0.013733 | 122.5616 | -0.38452 | -0.3891 | -0.018311 | 0.4715 | 102.2964 | 100.1129 | 122.2687 | 122.493 | -0.013733 | 122.6349 | 110.527 | -0.3891 | 122.493 | -0.013733 | 110.527 | 122.2687 | 122.6349 | -123.1384 | -123.0423
2180.9062 | 103.2303 | -14.3738 | 93.8965 | -0.087433 | 0.0038708 | 0.00089078 | 0.0043281 | -0.0071072 | -0.0011471 | 0.022424 | -14.9368 | 107.5195 | -15.5411 | 108.0917 | 105.7892 | 5.3467 | 5.4337 | 6.2393 | 108.0872 | -14.8407 | -1.1673 | 13.623 | -0.56305 | 122.4655 | 11.8927 | -0.46692 | 14.1907 | 0.60425 | 19.8074 | 20.6131 | 120.163 | 121.8933 | -0.56305 | 122.4609 | 19.7205 | -0.46692 | 121.8933 | -0.56305 | 19.7205 | 120.163 | 122.4609 | -109.4376 | -108.7372
2181.9531 | 123.0194 | -11.1053 | 110.9024 | 0.049896 | 0.0025892 | 0.001318 | -0.0005853 | -0.0088162 | 0.0016299 | 0.016229 | -10.8078 | 111.9919 | -10.9863 | 111.8774 | 109.0851 | 4.9118 | 5.3696 | 6.9168 | 111.6165 | -11.4075 | 0.11902 | 1.0895 | 0.29755 | 122.9828 | -1.8173 | -0.30212 | 0.71411 | 0.17853 | 16.4749 | 18.0222 | 120.1904 | 123.0972 | 0.29755 | 122.7219 | 16.0172 | -0.30212 | 123.0972 | 0.29755 | 16.0172 | 120.1904 | 122.7219 | -121.8887 | -122.3099
2182.9062 | 115.1367 | -10.1074 | 97.7005 | -0.2095 | 0.0013074 | -0.0018862 | 0.0030463 | -0.0071072 | -0.00050626 | 0.018579 | -9.7687 | 112.8754 | -10.2219 | 113.1546 | 110.4446 | 5.0995 | 5.1407 | 7.1136 | 112.5732 | -10.3867 | -0.11444 | 15.1749 | 0.33874 | 123.262 | 12.7441 | -0.27924 | 14.8727 | 0.45319 | 15.2481 | 17.2211 | 120.5521 | 122.9828 | 0.33874 | 122.6807 | 15.2069 | -0.27924 | 122.9828 | 0.33874 | 15.2069 | 120.5521 | 122.6807 | -107.9224 | -108.0872
2183.9688 | 122.4564 | -4.5547 | 117.6041 | 0.21011 | 0.001521 | 0.0021726 | 0.0026191 | -0.0051846 | 0.00034814 | 0.016442 | -4.7745 | 118.0206 | -5.0354 | 118.4097 | 115.7364 | 5.6442 | 5.9692 | 8.1802 | 118.1625 | -4.8614 | -0.48065 | 0.41656 | -0.21973 | 122.9645 | -1.8677 | -0.3067 | 0.55847 | 0.26093 | 10.524 | 12.735 | 120.2911 | 122.5754 | -0.21973 | 122.7173 | 10.199 | -0.3067 | 122.5754 | -0.21973 | 10.199 | 120.2911 | 122.7173 | -122.6395 | -122.4655
2184.9062 | 98.7122 | 0.24719 | 87.3505 | 0.049896 | 0.0038708 | 0.0058042 | 0.0075323 | -0.0053982 | -0.00050626 | 0.01922 | -5.5344 | 117.2424 | -5.928 | 117.3889 | 114.7293 | 5.365 | 5.4108 | 8.0292 | 117.1875 | -5.928 | -6.1752 | 29.892 | -5.7816 | 117.1417 | 27.3788 | -6.1752 | 29.837 | 0.39368 | 5.1636 | 7.782 | 114.4821 | 116.9952 | -5.7816 | 116.9403 | 5.1178 | -6.1752 | 116.9952 | -5.7816 | 5.1178 | 114.4821 | 116.9403 | -93.2785 | -93.2785
2185.9531 | 122.2733 | -5.3238 | 117.0456 | 0.21011 | 0.002162 | 0.006445 | 0.0009101 | -0.0034756 | -7.9062e-05 | 0.020288 | -5.2643 | 117.3981 | -5.6808 | 117.6636 | 114.9628 | 5.3375 | 5.3421 | 8.5373 | 117.4255 | -5.5939 | -0.35705 | 0.35248 | 0.05951 | 122.9874 | -2.0828 | -0.27008 | 0.37994 | 0.41657 | 10.6659 | 13.8611 | 120.2866 | 122.7219 | 0.05951 | 122.7493 | 10.6613 | -0.27008 | 122.7219 | 0.05951 | 10.6613 | 120.2866 | 122.7493 | -122.7264 | -122.6395
2186.9062 | 122.5342 | -5.7266 | 116.8076 | -0.079803 | 0.0017346 | 0.0015316 | 0.0015509 | -0.0056118 | -0.00093346 | 0.019647 | -5.5481 | 117.0868 | -5.9784 | 117.5858 | 114.8026 | 5.2872 | 5.2689 | 8.4 | 116.9815 | -5.9601 | -0.25177 | 0.27924 | 0.17853 | 123.3124 | -2.005 | -0.23346 | 0.17395 | 0.4303 | 10.9955 | 14.1266 | 120.5292 | 122.8134 | 0.17853 | 122.7081 | 11.0138 | -0.23346 | 122.8134 | 0.17853 | 11.0138 | 120.5292 | 122.7081 | -122.7859 | -122.7676
2187.9531 | 122.3694 | -7.1869 | 115.2557 | 0.15671 | 0.0023756 | 0.00046358 | 0.0039007 | -0.0079618 | 0.0020571 | 0.020074 | -7.1594 | 115.5579 | -7.4844 | 115.6311 | 113.118 | 5.0262 | 4.9576 | 8.226 | 115.4984 | -7.5302 | -0.29755 | 0.30212 | 0.027466 | 122.818 | -2.1378 | -0.34332 | 0.24262 | 0.32501 | 12.1445 | 15.4129 | 120.3049 | 122.7448 | 0.027466 | 122.6852 | 12.2131 | -0.34332 | 122.7448 | 0.027466 | 12.2131 | 120.3049 | 122.6852 | -122.7402 | -122.7859
2188.9062 | 122.2366 | -7.7133 | 108.2108 | -0.14084 | 0.0034436 | 0.0023862 | 0.0041143 | -0.004971 | -0.00029266 | 0.017938 | -8.1253 | 114.8071 | -8.2306 | 114.8483 | 112.5 | 5.0446 | 4.8111 | 8.1894 | 114.83 | -8.226 | -0.51727 | 6.5964 | -0.41199 | 122.5616 | 4.2892 | -0.51269 | 6.6193 | 0.10529 | 12.5244 | 15.9027 | 120.2133 | 122.5204 | -0.41199 | 122.5433 | 12.7579 | -0.51269 | 122.5204 | -0.41199 | 12.7579 | 120.2133 | 122.5433 | -116.4413 | -116.4368
2189.9688 | 122.1542 | -8.638 | 113.7955 | 0.25589 | 0.0017346 | 0.0011044 | 0.0058233 | -0.0043302 | 0.0018435 | 0.025415 | -11.5814 | 112.3947 | -10.2219 | 113.4842 | 112.2482 | 5.69 | 4.5959 | 8.139 | 113.9191 | -9.1782 | -1.5839 | -1.4008 | -2.9434 | 122.1222 | -1.5472 | -0.54016 | 0.1236 | -1.3596 | 13.2339 | 16.777 | 120.8862 | 121.0327 | -2.9434 | 122.5571 | 14.328 | -0.54016 | 121.0327 | -2.9434 | 14.328 | 120.8862 | 122.5571 | -124.0173 | -122.9736
2190.9062 | 122.5113 | -7.9376 | 114.6561 | -0.079803 | 0.0019482 | -0.00017722 | 0.0049689 | -0.0077482 | -0.00071986 | 0.01687 | -7.7545 | 114.8941 | -8.1665 | 115.1459 | 112.5824 | 4.8248 | 4.4266 | 7.457 | 114.7842 | -8.1665 | -0.22888 | 0.23804 | 0.18311 | 123.0835 | -2.0737 | -0.22888 | 0.12817 | 0.41199 | 12.3642 | 15.3946 | 120.52 | 122.8317 | 0.18311 | 122.7219 | 12.7625 | -0.22888 | 122.8317 | 0.18311 | 12.7625 | 120.52 | 122.7219 | -122.8226 | -122.8226
2191.9688 | 122.905 | -115.1184 | 7.5851 | 0.12619 | -0.00061524 | 0.00067718 | 0.019709 | -0.0062528 | 0.00056194 | 0.0059751 | -114.9033 | 7.4799 | -115.4617 | 7.5302 | 7.2876 | -3.9047 | -11.8469 | -13.829 | 7.6309 | -115.4572 | -0.34332 | -0.10529 | 0.21515 | 122.6486 | -0.29755 | -0.33875 | 0.045776 | 0.55847 | 103.2715 | 101.2894 | 122.406 | 122.5983 | 0.21515 | 122.7493 | 111.2137 | -0.33875 | 122.5983 | 0.21515 | 111.2137 | 122.406 | 122.7493 | -123.0469 | -123.0423
2192.9062 | 123.1293 | -66.7282 | 54.2953 | -1.5141 | 0.0028028 | 0.001959 | 0.0094549 | -0.0051846 | -0.0013609 | 0.0034115 | -65.2817 | 56.543 | -67.392 | 66.2796 | 61.1114 | 7.0129 | 0.75989 | -3.0441 | 60.0906 | -63.4781 | -0.66376 | 2.2476 | 1.4465 | 133.0078 | 6.8161 | 3.2501 | 5.7953 | 2.1103 | 67.4881 | 63.6841 | 127.8397 | 123.2712 | 1.4465 | 126.8188 | 73.7411 | 3.2501 | 123.2712 | 1.4465 | 73.7411 | 127.8397 | 126.8188 | -121.6873 | -117.7734
2193.9531 | 122.7676 | -102.0905 | 20.311 | 0.14145 | 0.0028028 | 0.004736 | 0.026545 | -0.0045438 | -0.0024289 | 0.016442 | -102.8961 | 20.0867 | -103.0151 | 20.7047 | 19.7708 | -4.6463 | -10.6018 | -12.085 | 20.755 | -102.4017 | -0.92468 | -0.2243 | -0.80566 | 122.7951 | -0.54016 | -0.31128 | 0.44403 | 0.11902 | 91.4886 | 90.0055 | 121.8613 | 122.1771 | -0.80566 | 122.8455 | 97.4442 | -0.31128 | 122.1771 | -0.80566 | 97.4442 | 121.8613 | 122.8455 | -123.3261 | -122.7127
2194.9062 | 122.8775 | -107.4234 | 15.1428 | -0.064545 | 0.0030164 | 0.0011044 | 0.015436 | -0.0045438 | -0.0020017 | 0.0034115 | -93.7363 | 16.2048 | -103.5507 | 15.6326 | 15.0375 | -3.7903 | -11.1649 | -13.1699 | 15.6235 | -107.5836 | 3.8727 | 1.062 | 13.6871 | 123.056 | -0.10529 | -0.16022 | 0.48065 | 9.8145 | 96.2585 | 94.2535 | 122.4609 | 123.6282 | 13.6871 | 123.0469 | 103.6331 | -0.16022 | 123.6282 | 13.6871 | 103.6331 | 122.4609 | 123.0469 | -118.6935 | -122.7264
2195.9688 | 122.8317 | -113.5345 | 9.2011 | 0.25589 | 0.0034436 | 0.0015316 | 0.023981 | -0.0011258 | -0.0015745 | 0.0087521 | -112.5366 | 10.0021 | -113.0539 | 9.1507 | 8.7982 | -4.6143 | -12.2131 | -13.9252 | 9.6863 | -113.53 | 0.48065 | 0.80109 | 0.99793 | 122.6852 | -0.40283 | 0.004578 | 0.48523 | 0.51727 | 101.3214 | 99.6094 | 122.3328 | 123.5367 | 0.99793 | 123.2208 | 108.9203 | 0.004578 | 123.5367 | 0.99793 | 108.9203 | 122.3328 | 123.2208 | -122.2549 | -122.731
2196.9062 | 122.1863 | -8.139 | 112.8433 | -0.17136 | -0.00018804 | 0.003668 | -0.0001581 | -0.0043302 | -0.0013609 | 0.019006 | -8.2626 | 114.3906 | -8.6105 | 114.8758 | 112.1567 | 4.8935 | 5.7129 | 7.3425 | 114.4959 | -8.5098 | -0.4715 | 1.5472 | -0.1236 | 123.0148 | -0.68665 | -0.37079 | 1.6525 | 0.3479 | 13.8519 | 15.4816 | 120.2957 | 122.5296 | -0.1236 | 122.6349 | 13.0325 | -0.37079 | 122.5296 | -0.1236 | 13.0325 | 120.2957 | 122.6349 | -121.4539 | -121.3531
2197.9688 | 123.1064 | -21.46 | 100.4791 | -0.2095 | 0.002162 | 0.0017454 | 0.0013373 | -0.0075344 | -0.0011471 | 0.014734 | -23.3917 | 99.6094 | -23.204 | 101.7471 | 101.2482 | 5.1727 | 3.8956 | 5.4245 | 101.6098 | -21.4233 | -1.7441 | -0.86975 | -1.9318 | 123.2071 | 0.76904 | 0.036621 | 1.1307 | -0.18768 | 25.3555 | 26.8845 | 122.7081 | 121.0693 | -1.9318 | 123.0698 | 26.6327 | 0.036621 | 121.0693 | -1.9318 | 26.6327 | 122.7081 | 123.0698 | -123.6832 | -121.9025
2198.9062 | 122.4747 | -11.7783 | 110.5499 | -0.026398 | 0.0010938 | -0.0029544 | -0.0014399 | -0.0056118 | -0.00071986 | 0.018792 | -11.2701 | 111.5158 | -11.4807 | 111.0855 | 108.696 | 3.9551 | 3.9413 | 6.5781 | 111.0168 | -12.0209 | 0.29755 | 0.96588 | 0.50812 | 122.8638 | -1.8539 | -0.24261 | 0.46692 | 0.21057 | 15.7196 | 18.3563 | 120.4742 | 123.2941 | 0.50812 | 122.7951 | 15.7333 | -0.24261 | 123.2941 | 0.50812 | 15.7333 | 120.4742 | 122.7951 | -122.0306 | -122.5708
2199.9688 | 98.5107 | -19.2352 | 103.0838 | -0.079803 | 0.00023916 | -0.0025272 | 0.0088141 | -0.00668 | 0.00034814 | 0.018579 | -19.519 | 103.3264 | -19.5648 | 103.1204 | 100.0534 | 3.9413 | 3.5751 | 6.0516 | 103.5461 | -19.519 | -0.32959 | 0.24262 | -0.28381 | 122.3557 | -3.0304 | -0.28381 | 0.46234 | 0.045776 | 22.8104 | 25.2869 | 119.2886 | 122.5616 | -0.28381 | 122.7814 | 23.1766 | -0.28381 | 122.5616 | -0.28381 | 23.1766 | 119.2886 | 122.7814 | -122.6486 | -122.6028
2200.9062 | 122.5433 | -9.2194 | 112.6785 | 0.049896 | 0.0017346 | -0.00017722 | -0.0003717 | -0.0062528 | 0.00034814 | 0.018365 | -9.1599 | 113.6444 | -9.4208 | 113.9603 | 111.264 | 4.303 | 4.3213 | 7.489 | 113.5254 | -9.4391 | -0.20142 | 0.96588 | 0.059509 | 123.1796 | -1.4145 | -0.21973 | 0.84686 | 0.26093 | 13.5406 | 16.7084 | 120.4834 | 122.8638 | 0.059509 | 122.7448 | 13.5223 | -0.21973 | 122.8638 | 0.059509 | 13.5223 | 120.4834 | 122.7448 | -122.0993 | -122.1176
2201.9531 | 122.5296 | -7.9102 | 114.3677 | -0.056915 | 0.00066656 | -0.00017722 | 0.0017645 | -0.0077482 | 0.00056194 | 0.018151 | -7.6447 | 115.1321 | -7.9468 | 115.2649 | 112.7151 | 4.5639 | 4.0283 | 7.5577 | 114.6469 | -8.2077 | -0.036621 | 0.76447 | 0.2655 | 123.175 | -1.6525 | -0.29755 | 0.27924 | 0.30212 | 11.9385 | 15.4678 | 120.6253 | 123.0423 | 0.2655 | 122.5571 | 12.4741 | -0.29755 | 123.0423 | 0.2655 | 12.4741 | 120.6253 | 122.5571 | -122.3145 | -122.5754
2202.9219 | 96.8307 | -0.009155 | 85.0204 | -0.11795 | 0.0023756 | 0.0017454 | 0.010309 | -0.0051846 | -7.9062e-05 | 0.016656 | -8.3176 | 114.4775 | -8.6975 | 114.8621 | 112.3306 | 4.3716 | 4.5547 | 7.7911 | 114.5142 | -8.4824 | -8.6884 | 29.4571 | -8.3084 | 114.8712 | 27.3102 | -8.4732 | 29.4937 | 0.37994 | 4.5639 | 7.8003 | 112.3398 | 114.4867 | -8.3084 | 114.5233 | 4.3808 | -8.4732 | 114.4867 | -8.3084 | 4.3808 | 112.3398 | 114.5233 | -93.718 | -93.5028
2203.9062 | 122.9324 | -9.2331 | 112.674 | -0.041657 | 2.5564e-05 | 0.0028134 | 0.0013373 | -0.0062528 | -0.0015745 | 0.01687 | -9.2834 | 113.4888 | -9.5489 | 113.9832 | 111.4471 | 4.1885 | 3.9642 | 7.7408 | 113.4842 | -9.4803 | -0.31586 | 0.81482 | -0.050354 | 123.2162 | -1.2268 | -0.24719 | 0.81024 | 0.2655 | 13.1973 | 16.9739 | 120.6802 | 122.7219 | -0.050354 | 122.7173 | 13.4216 | -0.24719 | 122.7219 | -0.050354 | 13.4216 | 120.6802 | 122.7173 | -122.2229 | -122.1542
2204.9688 | 122.4747 | -7.0724 | 115.1871 | -0.011139 | 0.002162 | -0.00081822 | 0.0006965 | -0.0079618 | 0.0018435 | 0.01922 | -7.164 | 115.5121 | -7.5577 | 115.9744 | 113.3469 | 4.4678 | 4.422 | 8.3267 | 115.6448 | -7.3654 | -0.48523 | 0.32501 | -0.091552 | 123.0469 | -1.8402 | -0.29297 | 0.45776 | 0.39368 | 11.4944 | 15.3992 | 120.4193 | 122.5845 | -0.091552 | 122.7173 | 11.5402 | -0.29297 | 122.5845 | -0.091552 | 11.5402 | 120.4193 | 122.7173 | -122.7448 | -122.5525
2205.9062 | 122.5525 | -8.7753 | 113.5483 | 0.019379 | -0.00040164 | -0.0020998 | 0.0036871 | -0.00668 | -0.00071986 | 0.019433 | -8.3038 | 114.3036 | -8.725 | 114.0976 | 111.7447 | 4.1016 | 3.9322 | 7.5943 | 113.7543 | -9.1415 | 0.050354 | 0.75531 | 0.4715 | 122.8729 | -1.8036 | -0.36621 | 0.20599 | 0.42114 | 12.7075 | 16.3696 | 120.52 | 123.0789 | 0.4715 | 122.5296 | 12.8769 | -0.36621 | 123.0789 | 0.4715 | 12.8769 | 120.52 | 122.5296 | -122.2733 | -122.6898
2206.9531 | 122.4472 | -6.7291 | 115.4022 | 0.11856 | -0.0010424 | 0.00089078 | 0.0045417 | -0.0058256 | -0.00093346 | 0.017297 | -6.72 | 116.0294 | -7.0221 | 116.272 | 113.6444 | 4.3259 | 4.454 | 7.9147 | 116.011 | -6.9992 | -0.29297 | 0.62714 | 0.009155 | 123.0011 | -1.7578 | -0.27008 | 0.60883 | 0.30212 | 11.1832 | 14.6439 | 120.3735 | 122.7585 | 0.009155 | 122.7402 | 11.055 | -0.27008 | 122.7585 | 0.009155 | 11.055 | 120.3735 | 122.7402 | -122.4243 | -122.4014
2207.9219 | 96.2814 | 0.19226 | 86.9522 | -0.026398 | 0.0062208 | 0.0038816 | 0.011591 | -0.0045438 | 0.0012027 | 0.020501 | -6.4133 | 116.4459 | -6.6879 | 116.597 | 114.0564 | 4.2892 | 4.6326 | 8.1253 | 116.4734 | -6.5964 | -6.8802 | 29.4937 | -6.6055 | 116.4047 | 27.1042 | -6.7886 | 29.5212 | 0.27466 | 4.4403 | 7.933 | 113.8641 | 116.2537 | -6.6055 | 116.2811 | 4.097 | -6.7886 | 116.2537 | -6.6055 | 4.097 | 113.8641 | 116.2811 | -93.6401 | -93.5486
2208.9531 | 122.2504 | -10.4965 | 105.0613 | 0.18723 | 0.0023756 | 0.0023862 | 0.0051825 | -0.003903 | -0.00029266 | 0.021142 | -10.6384 | 112.207 | -10.7895 | 112.7106 | 110.1654 | 4.2023 | 3.7628 | 7.0038 | 112.0514 | -10.9085 | -0.29297 | 7.1457 | -0.14191 | 123.2071 | 5.1041 | -0.41199 | 6.9901 | 0.15106 | 14.2593 | 17.5003 | 120.6619 | 122.7036 | -0.14191 | 122.5479 | 14.6988 | -0.41199 | 122.7036 | -0.14191 | 14.6988 | 120.6619 | 122.5479 | -115.8508 | -115.9698
2209.9062 | 99.1241 | -8.0383 | 95.7092 | -0.43839 | 0.0025892 | 0.001318 | 0.0047553 | -0.0062528 | -0.0013609 | 0.019433 | -8.139 | 114.798 | -8.345 | 114.9948 | 112.2894 | 4.3671 | 4.66 | 7.6813 | 114.8895 | -8.226 | -0.3067 | 19.0887 | -0.10071 | 123.0331 | 16.5802 | -0.18768 | 19.1803 | 0.20599 | 12.6984 | 15.7196 | 120.3278 | 122.8363 | -0.10071 | 122.9279 | 12.4054 | -0.18768 | 122.8363 | -0.10071 | 12.4054 | 120.3278 | 122.9279 | -104.0543 | -103.9352
2210.9531 | 122.6349 | -7.4844 | 114.4592 | 0.0041197 | 0.0013074 | -0.00039102 | 0.0015509 | -0.0053982 | -0.0020017 | 0.020288 | -7.4661 | 115.1367 | -7.9193 | 115.4892 | 112.8571 | 4.335 | 4.541 | 8.1894 | 115.2695 | -7.7545 | -0.43488 | 0.67749 | 0.018311 | 122.9736 | -1.6022 | -0.27008 | 0.81024 | 0.45319 | 12.0255 | 15.6738 | 120.3415 | 122.6212 | 0.018311 | 122.7539 | 11.8195 | -0.27008 | 122.6212 | 0.018311 | 11.8195 | 120.3415 | 122.7539 | -122.3785 | -122.2137
2211.9062 | 122.1954 | -5.0308 | 113.2782 | 0.88913 | -0.00040164 | 0.00067718 | 0.0039007 | -0.0062528 | -0.00029266 | 0.022424 | -5.0766 | 117.485 | -5.5984 | 117.6498 | 115.2649 | 4.7379 | 4.747 | 8.7799 | 117.572 | -5.4932 | -0.56763 | 4.2068 | -0.045776 | 122.6807 | 1.9867 | -0.46234 | 4.2938 | 0.52185 | 9.7778 | 13.8107 | 120.2957 | 122.5159 | -0.045776 | 122.6028 | 9.7687 | -0.46234 | 122.5159 | -0.045776 | 9.7687 | 120.2957 | 122.6028 | -118.8766 | -118.7714
2212.9688 | 114.3082 | -9.4254 | 95.6726 | -0.48416 | 0.0028028 | -0.00060462 | 0.0041143 | -0.0064664 | -0.0020017 | 0.018792 | -9.4208 | 113.4064 | -9.7092 | 113.4705 | 110.9299 | 4.0833 | 4.1199 | 7.695 | 113.3469 | -9.7183 | -0.28381 | 17.7338 | 0.004578 | 122.8958 | 15.2573 | -0.29297 | 17.6743 | 0.28839 | 13.5452 | 17.1204 | 120.3552 | 122.8317 | 0.004578 | 122.7722 | 13.5086 | -0.29297 | 122.8317 | 0.004578 | 13.5086 | 120.3552 | 122.7722 | -105.3818 | -105.3909
2213.9062 | 122.5662 | -11.4441 | 110.6461 | 0.034637 | -0.0010424 | 0.004736 | 0.0047553 | -0.0047574 | -0.0011471 | 0.020074 | -12.0209 | 110.7559 | -12.2177 | 111.4975 | 109.0164 | 4.0421 | 3.9139 | 7.6218 | 111.1679 | -11.7645 | -0.77362 | 0.10986 | -0.57678 | 122.9416 | -1.6296 | -0.32043 | 0.52185 | 0.19684 | 15.358 | 19.0659 | 120.4605 | 122.2 | -0.57678 | 122.612 | 15.4861 | -0.32043 | 122.2 | -0.57678 | 15.4861 | 120.4605 | 122.612 | -122.8638 | -122.4106
2214.9688 | 109.2682 | -7.7225 | 92.1478 | -0.16373 | 0.0053662 | 0.0049496 | 0.010523 | -0.0053982 | 0.0014163 | 0.021569 | -7.4753 | 115.4434 | -7.7042 | 115.3152 | 112.7151 | 4.1153 | 4.4632 | 7.988 | 115.3931 | -7.7042 | 0.01831 | 23.2956 | 0.24719 | 123.0377 | 20.5673 | 0.01831 | 23.2452 | 0.22888 | 12.1857 | 15.7104 | 120.4376 | 123.1659 | 0.24719 | 123.1155 | 11.8378 | 0.01831 | 123.1659 | 0.24719 | 11.8378 | 120.4376 | 123.1155 | -99.852 | -99.852
2215.9062 | 122.4518 | -6.7154 | 105.0064 | -0.24765 | 0.0028028 | 0.001318 | 0.0062507 | -0.0056118 | 0.00077554 | 0.020715 | -6.8253 | 115.8966 | -7.1365 | 116.5146 | 113.8641 | 4.4586 | 4.2435 | 7.7866 | 115.9744 | -6.9534 | -0.42114 | 10.8902 | -0.10986 | 123.23 | 8.8577 | -0.23804 | 10.968 | 0.31128 | 10.9589 | 14.502 | 120.5795 | 122.612 | -0.10986 | 122.6898 | 11.174 | -0.23804 | 122.612 | -0.10986 | 11.174 | 120.5795 | 122.6898 | -112.1429 | -111.9598
2216.9688 | 122.2321 | -11.824 | 110.3806 | -0.049286 | 2.5564e-05 | 0.00046358 | 0.0049689 | -0.0068936 | -0.00093346 | 0.023278 | -11.38 | 111.3235 | -11.6959 | 110.9985 | 108.7097 | 3.5065 | 3.4149 | 6.5323 | 110.8246 | -12.117 | 0.12817 | 0.94299 | 0.44403 | 122.8226 | -1.6708 | -0.29297 | 0.44403 | 0.31586 | 15.239 | 18.3563 | 120.5338 | 123.1476 | 0.44403 | 122.6486 | 15.3305 | -0.29297 | 123.1476 | 0.44403 | 15.3305 | 120.5338 | 122.6486 | -122.0764 | -122.4976
2217.9062 | 122.1451 | -6.6193 | 103.7888 | -0.20187 | 0.0025892 | 0.0043088 | 0.0056097 | -0.0079618 | 0.0016299 | 0.020929 | -6.4957 | 116.1896 | -6.8756 | 115.7822 | 113.6536 | 4.3808 | 4.4083 | 7.8003 | 116.0934 | -6.9443 | -0.25635 | 12.4008 | 0.1236 | 122.4014 | 9.8648 | -0.32501 | 12.3047 | 0.37994 | 11.0275 | 14.4196 | 120.2728 | 122.8088 | 0.1236 | 122.7127 | 11.0001 | -0.32501 | 122.8088 | 0.1236 | 11.0001 | 120.2728 | 122.7127 | -110.6644 | -110.733
2218.9688 | 122.1588 | -4.8431 | 112.0056 | 0.60684 | 0.0055798 | 0.00067718 | 0.029749 | -0.00668 | -0.00050626 | 0.022638 | -4.9072 | 117.7689 | -5.2322 | 118.0161 | 115.3427 | 4.5364 | 4.8294 | 8.4 | 117.8604 | -5.2734 | -0.3891 | 5.7632 | -0.064087 | 122.8592 | 3.3371 | -0.4303 | 5.8548 | 0.32501 | 9.6725 | 13.2431 | 120.1859 | 122.612 | -0.064087 | 122.7036 | 9.3796 | -0.4303 | 122.612 | -0.064087 | 9.3796 | 120.1859 | 122.7036 | -117.2379 | -117.2791
2219.9062 | 117.0319 | -7.37 | 97.1558 | -0.16373 | 0.001521 | 0.001318 | 0.0090277 | -0.0064664 | -7.9062e-05 | 0.020288 | -7.7271 | 115.4022 | -7.6401 | 115.4068 | 113.0951 | 4.3945 | 4.6005 | 7.5027 | 115.4205 | -7.6767 | -0.27008 | 18.2465 | -0.35706 | 122.7768 | 15.9393 | -0.3067 | 18.2648 | -0.086975 | 11.9705 | 14.8727 | 120.4651 | 122.7722 | -0.35706 | 122.7905 | 11.7645 | -0.3067 | 122.7722 | -0.35706 | 11.7645 | 120.4651 | 122.7905 | -104.7958 | -104.8325
2220.9531 | 122.818 | -16.4154 | 105.8166 | -3.4062 | -0.00018804 | 0.001959 | 0.020136 | -0.0047574 | -0.00029266 | 0.021356 | -14.3372 | 108.3069 | -14.6896 | 104.9835 | 104.8691 | 2.417 | 1.9913 | 7.1823 | 106.2973 | -16.9601 | 1.7258 | 2.4902 | 2.0782 | 121.3989 | -0.94757 | -0.54474 | 0.48065 | 0.35248 | 18.4067 | 23.5977 | 121.2845 | 124.7223 | 2.0782 | 122.7127 | 18.8324 | -0.54474 | 124.7223 | 2.0782 | 18.8324 | 121.2845 | 122.7127 | -120.5063 | -122.7768
2221.9062 | 122.9919 | -108.3527 | 14.1861 | -0.095062 | 0.0010938 | 0.0025998 | 0.034876 | -0.0068936 | -0.0015745 | 0.025842 | -108.3389 | 14.3005 | -108.7326 | 15.2985 | 15.1566 | -3.3783 | -11.4761 | -14.4974 | 14.7491 | -108.8196 | -0.37994 | 0.11444 | 0.013733 | 123.6511 | 0.97046 | -0.46692 | 0.56305 | 0.39368 | 96.8765 | 93.8553 | 123.5092 | 122.6532 | 0.013733 | 123.1018 | 104.9744 | -0.46692 | 122.6532 | 0.013733 | 104.9744 | 123.5092 | 123.1018 | -122.9187 | -123.0057
2222.9688 | 106.8649 | -9.6497 | 103.0792 | 0.233 | 0.00023916 | -0.00017722 | 0.0071051 | -0.0058256 | 0.00098914 | 0.01986 | -10.5606 | 112.0972 | -10.9726 | 112.0239 | 109.5932 | 4.2572 | 4.4083 | 7.9651 | 112.4542 | -10.6064 | -1.3229 | 9.0179 | -0.91095 | 121.6736 | 6.514 | -0.95673 | 9.375 | 0.41199 | 14.0579 | 17.6147 | 119.2429 | 121.7468 | -0.91095 | 122.1039 | 13.9069 | -0.95673 | 121.7468 | -0.91095 | 13.9069 | 119.2429 | 122.1039 | -114.0518 | -113.6856
2223.9062 | 122.5159 | -11.0092 | 107.1075 | -0.18662 | 0.0010938 | 0.001959 | 0.0047553 | -0.0060392 | -0.0028561 | 0.01986 | -11.7737 | 111.1542 | -11.8561 | 111.9049 | 109.2865 | 3.9963 | 3.8635 | 7.2052 | 111.5067 | -11.4349 | -0.84686 | 4.0466 | -0.76447 | 122.9141 | 2.179 | -0.42572 | 4.3991 | 0.082397 | 14.8727 | 18.2144 | 120.2957 | 122.1634 | -0.76447 | 122.5159 | 15.0055 | -0.42572 | 122.1634 | -0.76447 | 15.0055 | 120.2957 | 122.5159 | -118.9636 | -118.5425
2224.9062 | 116.9037 | -12.3962 | 95.929 | -0.2858 | 0.00066656 | -0.00039102 | 0.0062507 | -0.0062528 | 0.00077554 | 0.01986 | -12.3459 | 110.4584 | -12.529 | 110.5957 | 108.5587 | 4.3854 | 4.0649 | 7.1274 | 110.2615 | -12.9364 | -0.13275 | 14.5294 | 0.050354 | 122.9919 | 12.6297 | -0.54016 | 14.3326 | 0.18311 | 16.4612 | 19.5236 | 120.9549 | 122.8546 | 0.050354 | 122.6578 | 16.7816 | -0.54016 | 122.8546 | 0.050354 | 16.7816 | 120.9549 | 122.6578 | -108.4579 | -108.8654
2225.9688 | 122.2504 | -10.4095 | 112.1613 | 0.21011 | 0.00023916 | 0.00046358 | 0.0075323 | -0.004971 | -0.00029266 | 0.017724 | -10.3409 | 112.3489 | -10.6796 | 112.4313 | 109.8541 | 3.8773 | 3.6346 | 7.2098 | 112.1613 | -10.8307 | -0.27008 | 0.18768 | 0.068665 | 122.8409 | -2.3071 | -0.42114 | 0 | 0.33875 | 14.0442 | 17.6193 | 120.2637 | 122.7585 | 0.068665 | 122.5708 | 14.2868 | -0.42114 | 122.7585 | 0.068665 | 14.2868 | 120.2637 | 122.5708 | -122.8409 | -122.9919
2226.9062 | 122.3282 | -10.1715 | 113.0035 | -0.13321 | 2.5564e-05 | 0.00024998 | 0.0028327 | -0.0064664 | 0.00013454 | 0.020288 | -10.1532 | 112.587 | -10.4324 | 111.2412 | 110.2203 | 4.1885 | 4.0604 | 7.8506 | 112.2528 | -10.8582 | -0.26093 | -0.41657 | 0.018311 | 121.4127 | -2.7832 | -0.68665 | -0.75073 | 0.27924 | 14.2319 | 18.0222 | 120.3918 | 122.7585 | 0.018311 | 122.4243 | 14.36 | -0.68665 | 122.7585 | 0.018311 | 14.36 | 120.3918 | 122.4243 | -123.436 | -123.8617
2227.9531 | 122.3145 | -5.9875 | 104.0405 | -0.16373 | -0.0014696 | 0.00046358 | 0.0051825 | -0.0071072 | -0.00050626 | 0.01922 | -8.7753 | 114.0289 | -8.9951 | 116.5604 | 113.9053 | 5.0491 | 5.2185 | 8.9081 | 116.4093 | -6.7429 | -3.0075 | 9.9884 | -2.7878 | 122.5479 | 9.8648 | -0.75531 | 12.3688 | 0.21973 | 11.2061 | 14.8956 | 119.8929 | 120.0165 | -2.7878 | 122.3969 | 11.0367 | -0.75531 | 120.0165 | -2.7878 | 11.0367 | 119.8929 | 122.3969 | -113.0356 | -110.7834
2228.9062 | 122.4747 | -6.2668 | 109.8679 | -0.43076 | 0.00045296 | 0.003027 | 0.0056097 | -0.0051846 | -0.0020017 | 0.020715 | -6.3629 | 116.3223 | -6.7017 | 116.391 | 113.9786 | 4.2068 | 4.4312 | 8.5556 | 116.4001 | -6.7062 | -0.43488 | 6.4545 | -0.09613 | 122.6578 | 4.1107 | -0.43945 | 6.5323 | 0.33875 | 10.6979 | 14.8224 | 120.2454 | 122.5891 | -0.09613 | 122.6669 | 10.4736 | -0.43945 | 122.5891 | -0.09613 | 10.4736 | 120.2454 | 122.6669 | -116.5695 | -116.5741
2229.9531 | 122.9599 | -10.2814 | 111.5341 | -0.011139 | 0.00023916 | -0.0027408 | 0.0047553 | -0.0064664 | -0.0011471 | 0.018365 | -10.4965 | 112.175 | -10.9268 | 112.7792 | 110.2936 | 3.5751 | 3.6438 | 7.6767 | 112.3581 | -10.5286 | -0.64545 | 0.64087 | -0.21515 | 123.0606 | -1.2405 | -0.24719 | 0.82397 | 0.4303 | 13.9252 | 17.9581 | 120.575 | 122.4564 | -0.21515 | 122.6395 | 13.8565 | -0.24719 | 122.4564 | -0.21515 | 13.8565 | 120.575 | 122.6395 | -122.4609 | -122.0627
2230.9062 | 122.6212 | -6.4957 | 103.6377 | -0.24002 | 0.00023916 | -0.0016726 | 0.0066779 | -0.0068936 | -0.0015745 | 0.018365 | -6.871 | 115.8783 | -7.251 | 116.3498 | 113.5986 | 4.1245 | 4.5959 | 8.6517 | 116.0431 | -7.0267 | -0.75531 | 12.2406 | -0.37537 | 122.8455 | 9.9609 | -0.531 | 12.4054 | 0.37994 | 11.0916 | 15.1474 | 120.0943 | 122.374 | -0.37537 | 122.5388 | 10.6201 | -0.531 | 122.374 | -0.37537 | 10.6201 | 120.0943 | 122.5388 | -110.8887 | -110.6644
2231.9688 | 122.4426 | -5.809 | 116.7297 | -0.034027 | -0.00061524 | -0.00039102 | 0.0039007 | -0.0060392 | -0.0028561 | 0.02221 | -5.8868 | 116.7664 | -6.2714 | 116.9449 | 114.6652 | 4.3304 | 4.6875 | 8.7845 | 116.89 | -6.1157 | -0.46234 | 0.036621 | -0.07782 | 122.7539 | -2.0645 | -0.3067 | 0.16022 | 0.38452 | 10.4965 | 14.5935 | 120.4742 | 122.5754 | -0.07782 | 122.699 | 10.1395 | -0.3067 | 122.5754 | -0.07782 | 10.1395 | 120.4742 | 122.699 | -123.0011 | -122.8455
2232.9062 | 122.9599 | -11.9888 | 110.3989 | -0.12558 | -0.00018804 | 0.00067718 | 0.0094549 | -0.0071072 | -7.9062e-05 | 0.023065 | -11.3846 | 111.3281 | -11.6959 | 111.2595 | 108.7784 | 3.5797 | 3.5568 | 6.9626 | 110.7193 | -12.236 | 0.29297 | 0.92926 | 0.60425 | 123.2483 | -1.6205 | -0.24719 | 0.32043 | 0.31128 | 15.5457 | 18.9514 | 120.7672 | 123.317 | 0.60425 | 122.7081 | 15.5685 | -0.24719 | 123.317 | 0.60425 | 15.5685 | 120.7672 | 122.7081 | -122.0947 | -122.6349
2233.9688 | 85.5835 | -103.656 | 17.5552 | -0.056915 | 0.001521 | 0.0011044 | 0.011377 | -0.0053982 | 0.00098914 | 0.0025571 | -96.7758 | 21.3226 | -95.4758 | 20.0363 | 20.3568 | -5.3787 | -12.149 | -13.9069 | 20.9839 | -102.5482 | 8.1802 | 3.7674 | 6.8802 | 123.6923 | 2.8015 | 1.1078 | 3.4286 | -1.3 | 91.507 | 89.7491 | 124.0128 | 124.9786 | 6.8802 | 124.6399 | 98.2773 | 1.1078 | 124.9786 | 6.8802 | 98.2773 | 124.0128 | 124.6399 | -113.031 | -120.1035
2234.9062 | 97.4945 | -2.6138 | 86.7554 | -0.21713 | 0.004939 | 0.0023862 | 0.0073187 | -0.0086026 | 0.0018435 | 0.01986 | -6.752 | 116.0065 | -7.3013 | 116.2949 | 113.6581 | 4.1565 | 4.7379 | 8.5052 | 116.2354 | -6.8298 | -4.6875 | 29.2511 | -4.1382 | 118.9087 | 26.9028 | -4.216 | 29.48 | 0.54932 | 7.3517 | 11.1191 | 116.272 | 118.6203 | -4.1382 | 118.8492 | 6.7703 | -4.216 | 118.6203 | -4.1382 | 6.7703 | 116.272 | 118.8492 | -94.0567 | -93.5852
2235.9531 | 122.4472 | -13.3026 | 109.4788 | 0.019379 | 0.00088016 | 0.00024998 | 0.0028327 | -0.0056118 | -7.9062e-05 | 0.018792 | -13.7146 | 109.2453 | -13.4537 | 109.9594 | 107.2906 | 3.5156 | 3.4653 | 6.926 | 109.5566 | -13.4262 | -0.15106 | -0.23346 | -0.41199 | 123.262 | -2.1881 | -0.1236 | 0.07782 | -0.26093 | 16.7679 | 20.2286 | 120.5933 | 122.5479 | -0.41199 | 122.8592 | 16.8182 | -0.1236 | 122.5479 | -0.41199 | 16.8182 | 120.5933 | 122.8592 | -122.9324 | -122.905
2236.9062 | 120.6619 | -5.8548 | 99.5728 | -0.1561 | 0.00023916 | -0.0018862 | 0.0090277 | -0.0051846 | 0.00013454 | 0.01922 | -5.8411 | 116.9128 | -6.2439 | 117.1967 | 114.5096 | 3.8727 | 4.4312 | 8.3313 | 116.9861 | -6.1111 | -0.3891 | 17.3401 | 0.013733 | 123.0515 | 14.9368 | -0.25635 | 17.4133 | 0.40283 | 10.2859 | 14.1861 | 120.3644 | 122.7676 | 0.013733 | 122.8409 | 9.7275 | -0.25635 | 122.7676 | 0.013733 | 9.7275 | 120.3644 | 122.8409 | -105.8167 | -105.6839
2237.9531 | 122.6486 | -4.0924 | 118.2587 | -0.11032 | 0.0017346 | 0.0043088 | 0.0043281 | -0.0073208 | 0.00034814 | 0.021569 | -4.7791 | 118.1351 | -4.8065 | 119.1696 | 116.272 | 3.978 | 4.4495 | 9.0225 | 118.6661 | -4.3533 | -0.71411 | -0.1236 | -0.68665 | 123.262 | -1.9867 | -0.26093 | 0.40741 | 0.027466 | 8.5419 | 13.1149 | 120.3644 | 122.2275 | -0.68665 | 122.7585 | 8.0704 | -0.26093 | 122.2275 | -0.68665 | 8.0704 | 120.3644 | 122.7585 | -123.0652 | -122.612
2238.9062 | 122.1359 | -4.7104 | 109.552 | -0.24765 | 0.0025892 | -0.00017722 | 0.0045417 | -0.0073208 | -0.00029266 | 0.021569 | -4.6967 | 117.9749 | -5.072 | 118.0298 | 115.5167 | 3.9597 | 4.3854 | 8.9081 | 117.9611 | -5.0903 | -0.36163 | 8.4229 | 0.013733 | 122.7402 | 5.9647 | -0.37994 | 8.4091 | 0.37537 | 9.0958 | 13.6185 | 120.2271 | 122.6852 | 0.013733 | 122.6715 | 8.67 | -0.37994 | 122.6852 | 0.013733 | 8.67 | 120.2271 | 122.6715 | -114.624 | -114.6423
2239.9531 | 122.4426 | -5.3696 | 113.1454 | 0.057526 | 0.0010938 | 0.0017454 | 0.0068915 | -0.0060392 | 0.00098914 | 0.019006 | -5.7358 | 116.9815 | -6.102 | 117.453 | 114.9582 | 3.9505 | 4.5136 | 8.8074 | 117.3203 | -5.722 | -0.73242 | 3.8361 | -0.36621 | 122.8226 | 1.8127 | -0.35248 | 4.1748 | 0.36621 | 9.8831 | 14.1769 | 120.3278 | 122.3511 | -0.36621 | 122.6898 | 9.3201 | -0.35248 | 122.3511 | -0.36621 | 9.3201 | 120.3278 | 122.6898 | -119.2474 | -118.8675
2240.9062 | 122.4426 | -5.278 | 103.7796 | -0.24765 | -0.00040164 | 0.00046358 | 0.0036871 | -0.0051846 | 0.00013454 | 0.018792 | -5.5161 | 117.2333 | -5.864 | 117.7597 | 114.9719 | 3.9322 | 4.422 | 8.7387 | 117.3431 | -5.6442 | -0.58594 | 13.4537 | -0.23804 | 123.0377 | 11.1923 | -0.36621 | 13.5635 | 0.3479 | 9.7 | 14.0167 | 120.2499 | 122.5113 | -0.23804 | 122.6212 | 9.2102 | -0.36621 | 122.5113 | -0.23804 | 9.2102 | 120.2499 | 122.6212 | -109.6436 | -109.4238
2241.9688 | 122.5937 | -8.2214 | 114.1113 | -0.011139 | -0.00040164 | 0.0032406 | 0.018641 | -0.0062528 | 0.0012027 | 0.022851 | -7.6492 | 115.0177 | -8.0246 | 114.0656 | 112.294 | 3.9551 | 4.2984 | 8.4641 | 114.6423 | -8.4366 | 0.19684 | 0.90637 | 0.57221 | 122.287 | -1.8173 | -0.21515 | 0.53101 | 0.37537 | 12.5198 | 16.6855 | 120.5154 | 123.2391 | 0.57221 | 122.8638 | 12.1765 | -0.21515 | 123.2391 | 0.57221 | 12.1765 | 120.5154 | 122.8638 | -122.1359 | -122.5479
2242.9062 | 122.2366 | -8.1848 | 106.3065 | -0.14847 | 0.0023756 | -0.001459 | 0.0133 | -0.0068936 | 0.0012027 | 0.021997 | -8.1207 | 114.4409 | -8.6151 | 114.7247 | 111.4334 | 3.4882 | 3.6621 | 8.0795 | 114.2441 | -8.6838 | -0.4303 | 8.1345 | 0.064086 | 122.9095 | 5.127 | -0.49896 | 7.9376 | 0.49438 | 11.8469 | 16.2643 | 119.6182 | 122.6257 | 0.064086 | 122.4289 | 11.673 | -0.49896 | 122.6257 | 0.064086 | 11.673 | 119.6182 | 122.4289 | -114.9216 | -114.9902
2243.9531 | 122.8683 | -101.9943 | 20.5307 | 0.17197 | -0.0010424 | -0.00081822 | 0.013086 | -0.0051846 | -0.00093346 | 0.0042661 | -100.6943 | 22.7051 | -100.6027 | 21.3226 | 20.5765 | -3.2867 | -10.2356 | -11.6226 | 21.0114 | -102.095 | 1.3916 | 2.1744 | 1.3 | 123.317 | 0.045776 | -0.10071 | 0.48065 | -0.091553 | 91.7587 | 90.3717 | 122.5708 | 124.6994 | 1.3 | 123.0057 | 98.7076 | -0.10071 | 124.6994 | 1.3 | 98.7076 | 122.5708 | 123.0057 | -121.1334 | -122.6257
2244.9062 | 122.1909 | -6.3446 | 102.6993 | -0.22476 | 0.0019482 | 0.0032406 | 0.0056097 | -0.0077482 | -0.00071986 | 0.020288 | -6.4545 | 116.423 | -6.6696 | 116.6656 | 113.9008 | 3.9047 | 4.4724 | 8.8257 | 116.1484 | -6.7841 | -0.32501 | 13.7238 | -0.10986 | 123.0103 | 11.2015 | -0.43945 | 13.4491 | 0.21515 | 10.817 | 15.1703 | 120.2454 | 122.7676 | -0.10986 | 122.493 | 10.2493 | -0.43945 | 122.7676 | -0.10986 | 10.2493 | 120.2454 | 122.493 | -109.3689 | -109.4833
2245.9531 | 122.5479 | -6.3309 | 115.8783 | -0.018768 | -0.0010424 | -0.0012454 | 0.0064643 | -0.0058256 | -0.0024289 | 0.026269 | -6.308 | 116.4185 | -6.6376 | 116.4688 | 113.9969 | 3.8727 | 4.39 | 8.7616 | 116.4001 | -6.5918 | -0.3067 | 0.54016 | 0.022889 | 122.7997 | -1.8814 | -0.26092 | 0.52185 | 0.32959 | 10.7208 | 15.0925 | 120.3278 | 122.7493 | 0.022889 | 122.731 | 10.2036 | -0.26092 | 122.7493 | 0.022889 | 10.2036 | 120.3278 | 122.731 | -122.5159 | -122.4701
2246.9062 | 122.4976 | -6.3309 | 116.3315 | -0.041657 | 0.002162 | 0.00067718 | 0.0062507 | -0.0060392 | 0.0029117 | 0.021997 | -6.9489 | 115.4343 | -7.5943 | 116.8259 | 114.1846 | 4.3167 | 4.3396 | 8.8303 | 116.3773 | -6.5598 | -1.2634 | -0.89722 | -0.61798 | 123.1567 | -2.1469 | -0.22888 | 0.045776 | 0.64545 | 10.6705 | 15.1611 | 120.5154 | 121.7651 | -0.61798 | 122.7081 | 10.6476 | -0.22888 | 121.7651 | -0.61798 | 10.6476 | 120.5154 | 122.7081 | -123.9258 | -122.8912
2247.9531 | 122.525 | -5.2414 | 117.0593 | 0.18723 | -0.00018804 | -0.0010318 | 0.0058233 | -0.0079618 | 0.00098914 | 0.021997 | -5.0537 | 117.6544 | -5.4382 | 117.9337 | 115.3931 | 3.9505 | 4.248 | 8.5602 | 117.4805 | -5.4382 | -0.19684 | 0.59509 | 0.18768 | 123.175 | -1.6663 | -0.19684 | 0.42114 | 0.38452 | 9.4894 | 13.8016 | 120.6345 | 122.8958 | 0.18768 | 122.7219 | 9.1919 | -0.19684 | 122.8958 | 0.18768 | 9.1919 | 120.6345 | 122.7219 | -122.4976 | -122.4976
2248.9062 | 122.9736 | -4.5685 | 101.8524 | -0.22476 | 0.00088016 | 0.00046358 | 0.0068915 | -0.0062528 | 0.00098914 | 0.02221 | -4.6646 | 118.0298 | -5.1178 | 118.2587 | 115.5441 | 3.9688 | 4.5731 | 8.9951 | 118.0481 | -4.985 | -0.54932 | 16.1774 | -0.096131 | 122.8271 | 13.6917 | -0.41656 | 16.1957 | 0.45319 | 9.1415 | 13.5635 | 120.1126 | 122.5983 | -0.096131 | 122.6166 | 8.5373 | -0.41656 | 122.5983 | -0.096131 | 8.5373 | 120.1126 | 122.6166 | -106.9702 | -106.8375
2249.9688 | 122.9233 | -113.5986 | 9.2514 | 0.042267 | -0.00040164 | 0.003027 | 0.016932 | -0.0064664 | 0.0018435 | 0.0070431 | -113.324 | 9.288 | -113.9191 | 8.9264 | 8.6014 | -3.566 | -10.9589 | -14.7171 | 9.4574 | -113.6948 | -0.32043 | 0.036621 | 0.27466 | 122.525 | -0.65003 | -0.09613 | 0.20599 | 0.59509 | 102.6398 | 98.8815 | 122.2 | 122.8867 | 0.27466 | 123.056 | 110.0327 | -0.09613 | 122.8867 | 0.27466 | 110.0327 | 122.2 | 123.056 | -123.1705 | -122.9462
2250.9062 | 122.9507 | -112.9852 | 9.7137 | -0.20187 | 0.00045296 | 0.0051632 | 0.016932 | -0.0068936 | -0.0032835 | 0.0019163 | -112.8433 | 9.6405 | -113.4064 | 9.7412 | 9.4116 | -3.5248 | -12.1536 | -15.1382 | 9.7321 | -113.3286 | -0.42114 | -0.073242 | 0.14191 | 122.7264 | -0.30212 | -0.34332 | 0.018311 | 0.56305 | 100.8316 | 97.847 | 122.3969 | 122.6257 | 0.14191 | 122.7173 | 109.4604 | -0.34332 | 122.6257 | 0.14191 | 109.4604 | 122.3969 | 122.7173 | -123.1201 | -123.0423
2251.9688 | 122.9965 | -114.4638 | 8.2535 | 0.20248 | 0.00088016 | -0.003168 | 0.017786 | -0.0056118 | 0.00077554 | 0.0036253 | -114.2624 | 8.1894 | -114.8026 | 8.2214 | 7.901 | -3.7125 | -12.8952 | -15.8295 | 8.2535 | -114.7659 | -0.33874 | -0.064087 | 0.20142 | 122.6852 | -0.35248 | -0.30212 | 0 | 0.54016 | 101.5686 | 98.6343 | 122.3648 | 122.6532 | 0.20142 | 122.7173 | 110.7513 | -0.30212 | 122.6532 | 0.20142 | 110.7513 | 122.3648 | 122.7173 | -123.056 | -123.0194
2252.9062 | 123.0011 | -112.8754 | 9.375 | -0.13321 | 0.0017346 | 0.003668 | 0.01565 | -0.0064664 | -0.0030697 | 0.0055479 | -104.9606 | 13.5315 | -108.2291 | 9.4666 | 9.2651 | -4.216 | -13.0463 | -15.4312 | 9.7641 | -113.0539 | 4.6463 | 4.1565 | 7.9147 | 122.3419 | -0.10986 | -0.17853 | 0.3891 | 3.2684 | 99.8291 | 97.4442 | 122.1405 | 126.4069 | 7.9147 | 122.6395 | 108.6594 | -0.17853 | 126.4069 | 7.9147 | 108.6594 | 122.1405 | 122.6395 | -117.6041 | -122.4289
2253.9531 | 122.9691 | -112.4954 | 10.1212 | 0.1033 | -0.001256 | 0.005377 | 0.016504 | -0.0062528 | -0.0017881 | 0.0049069 | -112.9395 | 9.581 | -113.3102 | 9.7183 | 9.5718 | -3.3966 | -12.7808 | -15.6555 | 9.9243 | -112.9623 | -0.81482 | -0.54016 | -0.44403 | 122.2137 | -0.54932 | -0.46692 | -0.19684 | 0.37079 | 99.7147 | 96.8399 | 122.0673 | 122.0764 | -0.44403 | 122.4197 | 109.0988 | -0.46692 | 122.0764 | -0.44403 | 109.0988 | 122.0673 | 122.4197 | -123.4314 | -123.0835
2254.9219 | 122.8638 | -106.636 | 15.9943 | -0.095062 | 0.0036572 | 0.0049496 | 0.019709 | -0.0053982 | -0.00093346 | 0.0025571 | -106.0776 | 16.4658 | -106.5674 | 16.3559 | 15.683 | -3.3783 | -11.7371 | -14.5981 | 16.1499 | -107.1396 | 0.068664 | 0.4715 | 0.55847 | 122.9919 | -0.31128 | -0.50354 | 0.15564 | 0.48981 | 94.899 | 92.038 | 122.319 | 123.1018 | 0.55847 | 122.7859 | 103.2578 | -0.50354 | 123.1018 | 0.55847 | 103.2578 | 122.319 | 122.7859 | -122.5616 | -123.1339
2255.9531 | 123.024 | -110.1929 | 12.3962 | -0.16373 | -0.0014696 | 0.0028134 | 0.012018 | -0.0060392 | -0.0013609 | 0.0023435 | -110.701 | 11.9705 | -111.0535 | 12.7533 | 12.4466 | -3.1723 | -12.5061 | -14.6622 | 12.4374 | -110.6781 | -0.8606 | -0.42572 | -0.50812 | 122.9462 | 0.050354 | -0.48523 | 0.041199 | 0.35248 | 97.6868 | 95.5307 | 122.6395 | 122.1634 | -0.50812 | 122.6303 | 107.0206 | -0.48523 | 122.1634 | -0.50812 | 107.0206 | 122.6395 | 122.6303 | -123.4497 | -123.0743
2256.9062 | 122.9965 | -114.5142 | 8.139 | -0.026398 | -0.00082884 | 0.001959 | 0.013727 | -0.0045438 | -0.0011471 | 0.0034115 | -114.4272 | 8.0612 | -114.9124 | 8.1207 | 7.8186 | -3.8452 | -13.1332 | -15.9256 | 8.1619 | -114.8849 | -0.39825 | -0.07782 | 0.086975 | 122.6349 | -0.32043 | -0.37079 | 0.022888 | 0.48523 | 101.3809 | 98.5886 | 122.3328 | 122.5754 | 0.086975 | 122.6761 | 110.6689 | -0.37079 | 122.5754 | 0.086975 | 110.6689 | 122.3328 | 122.6761 | -123.0515 | -123.024
2257.9688 | 123.0743 | -109.5932 | 12.9089 | 0.27878 | 0.001521 | 0.0021726 | 0.018854 | -0.0062528 | -0.0024289 | 0.0066159 | -109.6848 | 12.822 | -110.0601 | 13.1241 | 12.7441 | -3.5202 | -12.1857 | -14.653 | 12.9959 | -110.0647 | -0.46692 | -0.086976 | -0.091552 | 122.7173 | -0.16479 | -0.4715 | 0.086975 | 0.37537 | 97.4075 | 94.9402 | 122.3373 | 122.4152 | -0.091552 | 122.5891 | 106.073 | -0.4715 | 122.4152 | -0.091552 | 106.073 | 122.3373 | 122.5891 | -122.9691 | -122.9736
2258.9062 | 86.1465 | -101.5228 | 20.9152 | -0.049286 | -0.0027514 | 0.0060178 | 0.012873 | -0.0051846 | -0.00071986 | 0.0087521 | -98.2956 | 24.4171 | -98.5977 | 22.3206 | 21.0938 | -4.0146 | -11.0367 | -12.9456 | 21.6614 | -101.4908 | 2.9251 | 3.5019 | 3.2272 | 123.8434 | 0.17853 | 0.032043 | 0.74616 | 0.30212 | 90.4861 | 88.5773 | 122.6166 | 125.9399 | 3.2272 | 123.1842 | 97.5082 | 0.032043 | 125.9399 | 3.2272 | 97.5082 | 122.6166 | 123.1842 | -119.5129 | -122.406
2259.9688 | 121.2112 | -108.7967 | 13.765 | 0.14145 | 0.0010938 | 0.00046358 | 0.013514 | -0.0060392 | 0.00098914 | 0.0027707 | -108.0276 | 14.502 | -108.4579 | 13.9847 | 13.591 | -3.1998 | -11.8057 | -14.0213 | 14.0213 | -109.0851 | 0.33874 | 0.737 | 0.76904 | 122.7814 | -0.17395 | -0.28839 | 0.25635 | 0.4303 | 96.991 | 94.7754 | 122.3877 | 123.2986 | 0.76904 | 122.818 | 105.5969 | -0.28839 | 123.2986 | 0.76904 | 105.5969 | 122.3877 | 122.818 | -122.2229 | -122.85
2260.9062 | 122.9416 | -113.9191 | 8.7936 | 0.1033 | -0.00018804 | 0.003668 | 0.013514 | -0.0081754 | -0.0020017 | 0.0025571 | -113.8 | 8.7067 | -114.2715 | 8.7753 | 8.4137 | -3.3371 | -12.7213 | -15.0925 | 8.7982 | -114.2578 | -0.35248 | -0.086975 | 0.11902 | 122.6944 | -0.37994 | -0.33875 | 0.004578 | 0.4715 | 101.1978 | 98.8266 | 122.3328 | 122.6257 | 0.11902 | 122.7173 | 110.582 | -0.33875 | 122.6257 | 0.11902 | 110.582 | 122.3328 | 122.7173 | -123.0652 | -123.0515
2261.9531 | 123.0148 | -108.4579 | 14.0167 | -0.11032 | -0.00082884 | 0.0043088 | 0.018 | -0.00668 | 0.0012027 | 0.0074705 | -107.6889 | 15.0375 | -107.5195 | 13.829 | 13.8245 | -3.1998 | -11.7279 | -14.1312 | 14.0396 | -109.1537 | 0.93842 | 1.0208 | 0.76904 | 122.287 | -0.19226 | -0.6958 | 0.022888 | -0.16937 | 96.73 | 94.3268 | 122.2824 | 123.4955 | 0.76904 | 122.4976 | 105.2582 | -0.6958 | 123.4955 | 0.76904 | 105.2582 | 122.2824 | 122.4976 | -121.5363 | -123.1705
2262.9062 | 122.9645 | -116.0568 | 6.8848 | 0.042267 | -0.001256 | 0.0034544 | 0.014795 | -0.0077482 | -0.00071986 | 0.0044797 | -116.4139 | 6.1523 | -116.7709 | 6.1569 | 5.8868 | -3.566 | -12.1948 | -14.566 | 6.7154 | -115.8737 | -0.71411 | -0.73242 | -0.35705 | 122.2137 | -0.99792 | 0.18311 | -0.16937 | 0.35706 | 103.862 | 101.4908 | 121.9437 | 122.2092 | -0.35705 | 122.7722 | 112.4908 | 0.18311 | 122.2092 | -0.35705 | 112.4908 | 121.9437 | 122.7722 | -123.6557 | -122.7585
2263.9688 | 122.9874 | -111.6989 | 10.9039 | 0.24826 | 0.0023756 | 0.0045224 | 0.02035 | -0.0053982 | -0.0037107 | 0.0042661 | -111.232 | 11.2564 | -111.7722 | 11.1145 | 10.7208 | -3.4927 | -12.2681 | -14.7858 | 11.0458 | -112.0148 | -0.073242 | 0.35248 | 0.46692 | 122.8134 | -0.18311 | -0.31586 | 0.14191 | 0.54016 | 99.4308 | 96.9131 | 122.4197 | 122.9553 | 0.46692 | 122.7448 | 108.2062 | -0.31586 | 122.9553 | 0.46692 | 108.2062 | 122.4197 | 122.7448 | -122.6761 | -122.9187
2264.9062 | 121.2296 | -97.4396 | 25.8499 | -3.4749 | 0.0010938 | 0.0015316 | 0.018 | -0.0060392 | -0.00093346 | 0.0012753 | -102.1042 | 29.5074 | -93.0267 | 29.5349 | 20.9885 | -11.4532 | -16.0263 | -7.8827 | 25.3601 | -97.6685 | 4.4128 | 3.6575 | -4.6646 | 126.9745 | -4.8615 | -0.22888 | -0.48981 | -9.0775 | 81.4133 | 89.5569 | 118.428 | 126.947 | -4.6646 | 122.7997 | 85.9863 | -0.22888 | 126.947 | -4.6646 | 85.9863 | 118.428 | 122.7997 | -118.8766 | -123.5184
2265.9688 | 122.9782 | -113.3331 | 9.2606 | 0.21011 | -0.00018804 | 0.0066586 | 0.021418 | -0.0079618 | -0.0011471 | 0.0042661 | -112.8937 | 9.3063 | -113.5757 | 9.2834 | 8.9035 | -3.6301 | -12.8998 | -15.6052 | 9.3292 | -113.7268 | -0.24262 | 0.045776 | 0.43945 | 122.6166 | -0.35706 | -0.39368 | 0.068665 | 0.68207 | 100.4333 | 97.728 | 122.2366 | 122.6395 | 0.43945 | 122.6624 | 109.7031 | -0.39368 | 122.6395 | 0.43945 | 109.7031 | 122.2366 | 122.6624 | -122.8363 | -122.9874
2266.9062 | 123.0286 | -113.9465 | 8.7341 | -0.14847 | -0.0016834 | -0.00017722 | 0.015009 | -0.0081754 | -7.9062e-05 | 0.0038389 | -113.7955 | 8.8394 | -114.1891 | 8.7708 | 8.3817 | -3.6758 | -13.3118 | -15.5594 | 8.7158 | -114.3311 | -0.24262 | 0.10529 | 0.15106 | 122.7173 | -0.35248 | -0.38452 | -0.018311 | 0.39368 | 100.6348 | 98.3871 | 122.3282 | 122.7859 | 0.15106 | 122.6624 | 110.2707 | -0.38452 | 122.7859 | 0.15106 | 110.2707 | 122.3282 | 122.6624 | -122.9233 | -123.0652
2267.9688 | 122.9919 | -110.1013 | 12.5565 | 0.13382 | 0.0013074 | 0.0058042 | 0.017145 | -0.0041166 | -0.0017881 | 0.0034115 | -110.0006 | 12.4832 | -110.495 | 12.4969 | 12.0941 | -3.3142 | -11.9431 | -13.9435 | 12.5931 | -110.3989 | -0.39368 | -0.073243 | 0.10071 | 122.5983 | -0.46234 | -0.29755 | 0.036621 | 0.49439 | 98.1583 | 96.1578 | 122.1954 | 122.5845 | 0.10071 | 122.6944 | 106.7871 | -0.29755 | 122.5845 | 0.10071 | 106.7871 | 122.1954 | 122.6944 | -123.0515 | -122.9553
2268.9062 | 122.9736 | -109.8404 | 12.854 | 0.0041197 | -0.00061524 | 0.00067718 | 0.012446 | -0.0068936 | -0.0024289 | 0.0029843 | -109.7397 | 12.8265 | -110.202 | 12.9822 | 12.4695 | -3.6346 | -11.7371 | -13.6414 | 13.0005 | -110.0235 | -0.36163 | -0.027466 | 0.10071 | 122.8226 | -0.38452 | -0.18311 | 0.14648 | 0.46234 | 98.1033 | 96.199 | 122.3099 | 122.6669 | 0.10071 | 122.8409 | 106.2057 | -0.18311 | 122.6669 | 0.10071 | 106.2057 | 122.3099 | 122.8409 | -123.056 | -122.8775
2269.9531 | 122.8729 | -110.0143 | 12.6984 | -0.13321 | 0.0030164 | 0.0028134 | 0.022059 | -0.003903 | -0.0032835 | 0.0068295 | -109.7351 | 12.8128 | -110.2432 | 12.5473 | 12.1674 | -3.6072 | -11.8332 | -13.9938 | 12.7121 | -110.3394 | -0.22888 | 0.11444 | 0.27924 | 122.5616 | -0.53101 | -0.32501 | 0.013733 | 0.50812 | 98.1812 | 96.0205 | 122.1817 | 122.8271 | 0.27924 | 122.7264 | 106.4072 | -0.32501 | 122.8271 | 0.27924 | 106.4072 | 122.1817 | 122.7264 | -122.9416 | -123.0377
2270.9062 | 123.0057 | -108.5724 | 13.9755 | -0.079803 | 0.0025892 | 0.0028134 | 0.011805 | -0.0058256 | -0.00071986 | 0.0021299 | -109.9136 | 12.529 | -110.2203 | 15.1245 | 14.4836 | -3.4195 | -11.6318 | -13.916 | 15.3076 | -108.4076 | -1.6479 | -1.4465 | -1.3412 | 123.6969 | 0.50812 | 0.16479 | 1.3321 | 0.3067 | 96.9406 | 94.6564 | 123.056 | 121.1014 | -1.3412 | 123.88 | 105.1529 | 0.16479 | 121.1014 | -1.3412 | 105.1529 | 123.056 | 123.88 | -124.1959 | -122.3831
2271.9062 | 122.9599 | -114.2532 | 8.3817 | 0.065155 | 0.002162 | -0.00039102 | 0.014155 | -0.0043302 | 0.00077554 | 0.0031979 | -114.2807 | 8.3084 | -114.6881 | 8.2443 | 7.9376 | -3.8498 | -12.3413 | -14.6347 | 8.3542 | -114.6698 | -0.43487 | -0.073242 | -0.027466 | 122.4976 | -0.44403 | -0.41656 | -0.027466 | 0.40741 | 101.9119 | 99.6185 | 122.1909 | 122.5616 | -0.027466 | 122.6074 | 110.4034 | -0.41656 | 122.5616 | -0.027466 | 110.4034 | 122.1909 | 122.6074 | -123.0698 | -123.0515
2272.9062 | 122.4518 | -5.5389 | 116.8213 | 0.057526 | 0.0017346 | 0.0034544 | 0.0086005 | -0.0056118 | -7.9062e-05 | 0.029901 | -6.0883 | 116.5466 | -6.4819 | 117.215 | 114.7522 | 4.6051 | 5.4199 | 8.9539 | 117.16 | -5.8685 | -0.94299 | -0.27466 | -0.54932 | 122.7539 | -2.0691 | -0.32959 | 0.33875 | 0.39368 | 10.9589 | 14.4928 | 120.2911 | 122.0856 | -0.54932 | 122.699 | 10.144 | -0.32959 | 122.0856 | -0.54932 | 10.144 | 120.2911 | 122.699 | -123.3032 | -122.6898
2273.9062 | 122.5113 | -4.4037 | 117.6361 | -0.026398 | 0.0034436 | 0.003668 | 0.0034735 | -0.0092434 | 0.0018435 | 0.021356 | -4.3808 | 118.364 | -4.6417 | 118.7256 | 116.0019 | 4.2114 | 5.2094 | 9.2422 | 118.4006 | -4.5685 | -0.23804 | 0.72785 | 0.022889 | 123.1293 | -1.6342 | -0.16479 | 0.76447 | 0.26093 | 9.613 | 13.6459 | 120.4056 | 122.7676 | 0.022889 | 122.8043 | 8.6151 | -0.16479 | 122.7676 | 0.022889 | 8.6151 | 120.4056 | 122.8043 | -122.2778 | -122.2046
2274.9062 | 105.8304 | -4.7012 | 94.3314 | -0.13321 | 0.004939 | 0.003027 | 0.0041143 | -0.0086026 | -0.00050626 | 0.025842 | -4.3533 | 118.483 | -4.7516 | 118.4692 | 115.9103 | 4.2892 | 5.2734 | 9.3521 | 118.4052 | -4.6921 | -0.050354 | 24.1516 | 0.3479 | 123.1705 | 21.579 | 0.009155 | 24.0738 | 0.39825 | 9.9747 | 14.0533 | 120.6116 | 123.1842 | 0.3479 | 123.1064 | 8.9905 | 0.009155 | 123.1842 | 0.3479 | 8.9905 | 120.6116 | 123.1064 | -99.0829 | -99.0234
2275.9062 | 123.0057 | -11.5814 | 110.9665 | 0.095673 | 0.0019482 | 0.00089078 | 0.0041143 | -0.0053982 | 0.00013454 | 0.022424 | -10.1944 | 116.2628 | -6.3217 | 112.0651 | 109.4513 | 2.4216 | 3.4332 | 7.1548 | 111.6119 | -11.7371 | 5.2597 | 5.2963 | 1.387 | 123.6465 | -1.5152 | -0.15564 | 0.64545 | -3.8727 | 15.0146 | 18.7363 | 121.0327 | 127.8442 | 1.387 | 123.1934 | 14.003 | -0.15564 | 127.8442 | 1.387 | 14.003 | 121.0327 | 123.1934 | -117.2882 | -122.7036
2276.9531 | 116.9174 | -11.5723 | 87.6205 | -0.50705 | 0.00323 | 0.0028134 | 0.01095 | -0.0047574 | -0.0024289 | 0.01922 | -11.3892 | 111.5753 | -11.4578 | 111.8958 | 109.5795 | 3.8773 | 4.2206 | 7.5348 | 111.6806 | -11.3892 | 0.11444 | 23.9548 | 0.18311 | 123.468 | 21.9589 | 0.18311 | 24.0601 | 0.068665 | 15.7928 | 19.1071 | 121.1517 | 123.1476 | 0.18311 | 123.2529 | 15.4495 | 0.18311 | 123.1476 | 0.18311 | 15.4495 | 121.1517 | 123.2529 | -99.0784 | -99.0097
2277.9062 | 122.5388 | -4.1016 | 118.0389 | 0.21774 | 0.0023756 | 0.0025998 | 0.0004827 | -0.0041166 | 0.0014163 | 0.01986 | -3.9505 | 118.7439 | -4.3625 | 119.0231 | 116.217 | 4.0878 | 4.6738 | 9.2514 | 118.634 | -4.3762 | -0.26093 | 0.70496 | 0.15106 | 123.1247 | -1.8219 | -0.27466 | 0.59509 | 0.41199 | 8.7753 | 13.353 | 120.3186 | 122.8455 | 0.15106 | 122.7356 | 8.1894 | -0.27466 | 122.8455 | 0.15106 | 8.1894 | 120.3186 | 122.7356 | -122.4014 | -122.4152
2278.9688 | 113.4979 | -4.7974 | 93.8416 | 0.1796 | 0.0028028 | 0.0066586 | 0.011805 | -0.0060392 | -0.0013609 | 0.019006 | -4.4037 | 118.4326 | -4.7836 | 118.5974 | 115.6677 | 3.8773 | 4.9622 | 8.7799 | 118.2953 | -4.7516 | 0.013733 | 24.5911 | 0.39368 | 123.3948 | 21.8262 | 0.045776 | 24.4537 | 0.37994 | 9.7595 | 13.5773 | 120.4651 | 123.23 | 0.39368 | 123.0927 | 8.6746 | 0.045776 | 123.23 | 0.39368 | 8.6746 | 120.4651 | 123.0927 | -98.6252 | -98.5931
2279.9062 | 122.9507 | -7.283 | 113.2599 | 0.14908 | -0.00061524 | 0.0032406 | 0.0079595 | -0.002194 | -0.0011471 | 0.02221 | -4.4907 | 118.3228 | -4.6829 | 118.9911 | 116.1575 | 4.1885 | 3.6392 | 5.0674 | 116.2537 | -6.0562 | 2.6001 | 5.0629 | 2.7924 | 126.2741 | 2.8976 | 1.2268 | 2.9938 | 0.19226 | 10.9222 | 12.3505 | 123.4406 | 125.6058 | 2.7924 | 123.5367 | 11.4716 | 1.2268 | 125.6058 | 2.7924 | 11.4716 | 123.4406 | 123.5367 | -117.9428 | -119.3161
2280.9688 | 122.8317 | -4.129 | 105.9998 | 0.22537 | 0.002162 | 0.0023862 | 0.0090277 | -0.0030484 | -0.0015745 | 0.01986 | -4.0375 | 118.7439 | -4.3716 | 118.7164 | 115.8829 | 3.9047 | 4.454 | 9.2514 | 118.4326 | -4.5822 | -0.24261 | 12.7441 | 0.091552 | 122.8455 | 9.8831 | -0.45319 | 12.4329 | 0.33417 | 8.5831 | 13.3804 | 120.0119 | 122.8729 | 0.091552 | 122.5616 | 8.0338 | -0.45319 | 122.8729 | 0.091552 | 8.0338 | 120.0119 | 122.5616 | -110.3714 | -110.582
2281.9062 | 122.3831 | -11.0596 | 111.2366 | 0.095673 | 0.0030164 | 0.0017454 | -0.0001581 | -0.0056118 | -0.00029266 | 0.01922 | -11.2701 | 111.4609 | -11.6547 | 112.0926 | 109.3506 | 3.566 | 3.4836 | 7.7774 | 111.6348 | -11.3297 | -0.59509 | 0.2243 | -0.21057 | 123.1522 | -1.886 | -0.27008 | 0.39826 | 0.38452 | 14.5432 | 18.837 | 120.4102 | 122.5204 | -0.21057 | 122.6944 | 14.6255 | -0.27008 | 122.5204 | -0.21057 | 14.6255 | 120.4102 | 122.6944 | -122.8912 | -122.5662
2282.9531 | 123.5184 | -6.4133 | 99.1058 | 0.24063 | 0.0036572 | 0.0040952 | 0.0092413 | -0.0051846 | 0.00013454 | 0.019006 | -9.6725 | 112.9395 | -10.2127 | 114.473 | 112.4725 | 5.7724 | 5.9921 | 9.8694 | 115.8875 | -7.5302 | -3.7994 | 13.8336 | -3.2593 | 120.8862 | 13.3667 | -1.1169 | 16.7816 | 0.54016 | 12.4054 | 16.2827 | 118.8858 | 119.3527 | -3.2593 | 122.3007 | 12.1857 | -1.1169 | 119.3527 | -3.2593 | 12.1857 | 118.8858 | 122.3007 | -109.3185 | -106.636
2283.9062 | 119.8242 | -6.6422 | 115.2145 | 0.11093 | 0.0019482 | 0.0028134 | 0.0068915 | -0.003903 | -0.0013609 | 0.02691 | -6.5414 | 116.1484 | -6.9855 | 115.8829 | 113.5071 | 3.8635 | 4.3854 | 8.9035 | 115.979 | -7.1503 | -0.34332 | 0.93384 | 0.10071 | 122.525 | -1.7075 | -0.50812 | 0.76447 | 0.44403 | 11.0275 | 15.5457 | 120.1492 | 122.7905 | 0.10071 | 122.6212 | 10.5057 | -0.50812 | 122.7905 | 0.10071 | 10.5057 | 120.1492 | 122.6212 | -122.2 | -122.3648
2284.9062 | 122.2549 | -6.926 | 115.6494 | -0.079803 | 0.0028028 | 0.0011044 | 0.0066779 | -0.00668 | -0.00029266 | 0.02691 | -6.3354 | 116.4276 | -6.5414 | 113.9648 | 112.5595 | 4.509 | 5.1224 | 9.1003 | 115.8875 | -7.489 | 0.38452 | 0.7782 | 0.59051 | 120.8908 | -3.0899 | -0.56305 | 0.23804 | 0.20599 | 12.0483 | 16.0263 | 119.4855 | 123.3536 | 0.59051 | 122.8134 | 11.4349 | -0.56305 | 123.3536 | 0.59051 | 11.4349 | 119.4855 | 122.8134 | -122.1909 | -123.1384
2285.9688 | 92.5323 | -6.2393 | 90.271 | -0.018768 | 0.00323 | 0.001318 | 0.011164 | -0.0028348 | -0.0013609 | 0.020501 | -5.9738 | 116.7755 | -6.4316 | 116.8854 | 114.267 | 3.6667 | 4.1061 | 8.8623 | 116.5833 | -6.4407 | -0.19226 | 26.5045 | 0.2655 | 123.1247 | 23.996 | -0.20142 | 26.3123 | 0.45776 | 10.3455 | 15.1016 | 120.5063 | 123.0148 | 0.2655 | 122.8226 | 9.906 | -0.20142 | 123.0148 | 0.2655 | 9.906 | 120.5063 | 122.8226 | -96.7026 | -96.7117
2286.9062 | 92.9718 | -6.4728 | 110.701 | 0.080414 | 0.0025892 | 0.005377 | 0.0043281 | -0.0041166 | 0.00013454 | 0.020074 | -7.164 | 113.6673 | -10.1028 | 115.123 | 112.6831 | 5.5389 | 4.6783 | 9.1873 | 115.1596 | -6.1707 | -3.6301 | 2.9663 | -0.69122 | 121.5958 | 1.9821 | 0.30212 | 4.4586 | 2.9388 | 11.1511 | 15.6601 | 119.1559 | 120.1401 | -0.69122 | 121.6324 | 12.0117 | 0.30212 | 120.1401 | -0.69122 | 12.0117 | 119.1559 | 121.6324 | -120.8038 | -116.8716
2287.9531 | 114.8071 | -6.308 | 97.3389 | 0.14145 | 0.0040846 | 0.00046358 | 0.011377 | -0.0013394 | -0.0032835 | 0.02456 | -5.9738 | 116.8396 | -6.308 | 116.6611 | 114.0427 | 3.7216 | 4.2572 | 8.6746 | 116.5878 | -6.4865 | 0 | 19.5007 | 0.33417 | 122.9691 | 16.7038 | -0.17853 | 19.249 | 0.33417 | 10.5652 | 14.9826 | 120.3506 | 123.1476 | 0.33417 | 122.8958 | 10.0296 | -0.17853 | 123.1476 | 0.33417 | 10.0296 | 120.3506 | 122.8958 | -103.6469 | -103.8254
2288.9219 | 120.3278 | -6.1478 | 95.8374 | -0.30869 | 0.0040846 | 0.005377 | 0.0090277 | -0.0036892 | -0.00050626 | 0.01986 | -5.9692 | 116.9678 | -6.2119 | 117.1646 | 114.2029 | 3.6026 | 4.3762 | 8.5236 | 116.6656 | -6.4362 | -0.064087 | 21.1304 | 0.17853 | 123.3124 | 18.3655 | -0.28839 | 20.8282 | 0.24261 | 10.524 | 14.6713 | 120.3506 | 123.1155 | 0.17853 | 122.8134 | 9.7504 | -0.28839 | 123.1155 | 0.17853 | 9.7504 | 120.3506 | 122.8134 | -102.0493 | -102.2736
2289.9688 | 122.5937 | -4.8843 | 117.2745 | -0.034027 | 0.00045296 | -0.00060462 | 0.0015509 | -0.003903 | -0.00050626 | 0.022638 | -4.8111 | 118.1168 | -4.9255 | 118.4006 | 115.4068 | 3.7994 | 4.3213 | 9.0179 | 117.8741 | -5.2368 | -0.041199 | 0.84229 | 0.073242 | 123.2849 | -1.8677 | -0.35248 | 0.59967 | 0.11444 | 9.2056 | 13.9023 | 120.2911 | 123.0011 | 0.073242 | 122.7585 | 8.6838 | -0.35248 | 123.0011 | 0.073242 | 8.6838 | 120.2911 | 122.7585 | -122.2 | -122.5113
2290.9062 | 122.9828 | -112.294 | 10.0662 | 0.057526 | 0.004939 | 0.0032406 | 0.025263 | -0.003262 | -0.0015745 | 0.0096067 | -111.8179 | 11.1237 | -112.1841 | 9.8923 | 9.5947 | -3.6392 | -11.8103 | -13.5223 | 10.0113 | -113.0768 | 0.10986 | 1.0574 | 0.47607 | 122.1863 | -0.4715 | -0.78278 | -0.054931 | 0.36621 | 100.4837 | 98.7717 | 121.8887 | 123.4177 | 0.47607 | 122.3053 | 108.6548 | -0.78278 | 123.4177 | 0.47607 | 108.6548 | 121.8887 | 122.3053 | -122.2504 | -123.143
2291.9531 | 122.4014 | -24.8795 | 69.6259 | -0.17899 | 0.0040846 | 0.004736 | 0.01565 | -0.0024076 | -0.0017881 | 0.022638 | -23.8266 | 99.6277 | -23.5611 | 98.4558 | 95.1782 | 2.124 | 2.33 | 5.6351 | 98.1171 | -24.8566 | 1.3184 | 30.0018 | 1.0529 | 123.3353 | 25.5524 | 0.022889 | 28.4912 | -0.2655 | 27.2095 | 30.5145 | 120.0577 | 124.5071 | 1.0529 | 122.9965 | 27.0035 | 0.022889 | 124.5071 | 1.0529 | 27.0035 | 120.0577 | 122.9965 | -93.1869 | -94.4824
2292.9062 | 122.1588 | -6.2622 | 106.2332 | 0.17197 | 0.0057934 | 0.001959 | 0.014795 | -5.7592e-05 | -0.00071986 | 0.024133 | -6.8527 | 115.9882 | -7.0587 | 116.2354 | 113.7726 | 4.2709 | 4.4266 | 9.2331 | 116.2445 | -6.8985 | -0.79651 | 9.7549 | -0.59051 | 122.4976 | 7.5394 | -0.63629 | 10.0113 | 0.20599 | 10.6888 | 15.4953 | 120.0348 | 122.2504 | -0.59051 | 122.5067 | 10.5331 | -0.63629 | 122.2504 | -0.59051 | 10.5331 | 120.0348 | 122.5067 | -113.2919 | -113.1317
2293.9688 | 122.937 | -104.0451 | 18.6539 | 0.14145 | 0.0013074 | 0.0017454 | 0.019495 | -0.0019802 | -0.0015745 | 0.0036253 | -105.2948 | 18.1686 | -105.4642 | 19.8715 | 19.0109 | -2.1194 | -10.4736 | -11.9888 | 19.0018 | -104.2465 | -1.4191 | -0.48523 | -1.2497 | 123.9166 | 0.35705 | -0.20142 | 0.3479 | 0.16937 | 93.5715 | 92.0563 | 123.056 | 122.2137 | -1.2497 | 123.0469 | 101.9257 | -0.20142 | 122.2137 | -1.2497 | 101.9257 | 123.056 | 123.0469 | -124.118 | -122.9004
2294.9062 | 123.7793 | -92.4866 | 30.2124 | 0.019379 | 0.0010938 | 0.0025998 | 0.0098823 | -0.0011258 | 0.00098914 | 0.0068295 | -102.8732 | 21.6568 | -102.3926 | 22.6822 | 21.4416 | -2.6459 | -8.9767 | -10.7803 | 22.6089 | -98.5199 | -9.906 | -8.5556 | -10.3867 | 115.1688 | -8.7708 | -6.0333 | -7.6035 | -0.48065 | 83.5098 | 81.7062 | 113.9282 | 114.1434 | -10.3867 | 115.0955 | 89.8407 | -6.0333 | 114.1434 | -10.3867 | 89.8407 | 113.9282 | 115.0955 | -132.605 | -128.7323
2295.9062 | 123.0194 | -108.4396 | 14.003 | 0.11093 | 0.0034436 | 0.0038816 | 0.027186 | -0.0028348 | -0.0011471 | 0.032037 | -109.2224 | 15.0925 | -108.9935 | 23.3871 | 17.363 | -6.7886 | -14.8453 | -15.1611 | 16.8503 | -107.7576 | -0.55389 | 1.0895 | -0.78278 | 131.8268 | 3.36 | 0.68207 | 2.8473 | -0.22888 | 93.5944 | 93.2785 | 125.8026 | 123.5321 | -0.78278 | 125.2899 | 101.651 | 0.68207 | 123.5321 | -0.78278 | 101.651 | 125.8026 | 125.2899 | -122.9965 | -121.7606
2296.9531 | 122.9279 | -113.4933 | 9.2056 | -0.2095 | 0.002162 | 0.0055906 | 0.018 | -0.0028348 | -0.0034971 | 0.0019163 | -113.1409 | 9.7412 | -113.562 | 9.256 | 8.9127 | -3.6163 | -12.5702 | -15.2023 | 9.3063 | -113.8458 | -0.068665 | 0.53558 | 0.35248 | 122.7493 | -0.29297 | -0.35248 | 0.10071 | 0.42114 | 100.9232 | 98.291 | 122.406 | 123.2346 | 0.35248 | 122.7997 | 109.877 | -0.35248 | 123.2346 | 0.35248 | 109.877 | 122.406 | 122.7997 | -122.7676 | -123.0515
2297.9062 | 123.0148 | -110.5728 | 12.0575 | 0.233 | 0.0068616 | 0.005377 | 0.023127 | -0.002194 | -0.0020017 | 0.0059751 | -110.6232 | 11.9202 | -110.9024 | 10.0662 | 9.8007 | -3.7674 | -12.6434 | -15.3717 | 10.7849 | -111.7081 | -0.32959 | -0.13733 | -0.050354 | 120.639 | -2.2568 | -1.1353 | -1.2726 | 0.27924 | 97.9294 | 95.2011 | 120.3735 | 122.493 | -0.050354 | 121.3577 | 106.8054 | -1.1353 | 122.493 | -0.050354 | 106.8054 | 120.3735 | 121.3577 | -122.9599 | -123.7656
2298.9688 | 124.3607 | -8.5968 | 101.3626 | 0.17197 | 0.0034436 | 0.0017454 | 0.012018 | -0.0026212 | -0.0037107 | 0.026056 | -9.1782 | 113.9236 | -9.0775 | 115.123 | 112.0422 | 4.0558 | 4.4357 | 7.9056 | 114.2487 | -8.6746 | -0.48065 | 12.561 | -0.58136 | 123.7198 | 10.6796 | -0.07782 | 12.886 | -0.10071 | 13.0325 | 16.5024 | 120.639 | 122.5204 | -0.58136 | 122.8455 | 12.6526 | -0.07782 | 122.5204 | -0.58136 | 12.6526 | 120.639 | 122.8455 | -110.4401 | -110.0372
2299.9219 | 96.8719 | -6.8665 | 111.0992 | -0.11795 | 0.0025892 | 0.0011044 | -0.0010125 | -0.0051846 | 0.0012027 | 0.020929 | -7.2464 | 115.6448 | -7.3563 | 116.5375 | 113.7909 | 4.5685 | 4.9393 | 8.7662 | 115.9836 | -7.0038 | -0.48981 | 4.5456 | -0.37994 | 123.4039 | 2.6917 | -0.13733 | 4.8843 | 0.10986 | 11.8057 | 15.6326 | 120.6573 | 122.5113 | -0.37994 | 122.85 | 11.4349 | -0.13733 | 122.5113 | -0.37994 | 11.4349 | 120.6573 | 122.85 | -118.4555 | -118.103
2300.9688 | 92.2348 | 0.20142 | 85.2402 | 0.080414 | 0.004939 | 0.0066586 | 0.014582 | -0.0024076 | -0.0020017 | 0.022424 | -7.3837 | 115.6311 | -7.4524 | 115.5029 | 113.1042 | 4.4357 | 4.9026 | 8.876 | 115.6448 | -8.2123 | -7.6538 | 30.3909 | -7.5851 | 115.3015 | 27.8641 | -8.4137 | 30.4047 | 0.068665 | 4.7012 | 8.6746 | 112.9028 | 115.4297 | -7.5851 | 115.4434 | 4.2343 | -8.4137 | 115.4297 | -7.5851 | 4.2343 | 112.9028 | 115.4434 | -92.6926 | -93.4525
2301.9062 | 122.731 | -7.695 | 101.8982 | 0.20248 | 0.0042982 | 0.001959 | 0.010096 | -5.7592e-05 | -7.9062e-05 | 0.023492 | -7.9147 | 115.3244 | -7.7454 | 116.304 | 113.6627 | 1.6205 | 1.0483 | 7.0541 | 113.7726 | -8.606 | -0.050354 | 13.4262 | -0.21973 | 123.999 | 11.7645 | -0.91095 | 11.8744 | -0.16937 | 8.7433 | 14.7491 | 121.3577 | 123.0194 | -0.21973 | 121.4676 | 9.3155 | -0.91095 | 123.0194 | -0.21973 | 9.3155 | 121.3577 | 121.4676 | -109.6436 | -110.5042
2302.9688 | 99.2615 | -5.7358 | 87.6068 | 0.057526 | 0.0040846 | 0.0034544 | 0.0098823 | -0.00091219 | -0.00029266 | 0.021142 | -6.9031 | 116.1346 | -7.0175 | 116.1072 | 113.3286 | 3.8818 | 4.5181 | 8.7845 | 116.1575 | -6.9717 | -1.2817 | 28.5278 | -1.1673 | 121.843 | 25.7217 | -1.236 | 28.5507 | 0.11444 | 10.2539 | 14.5203 | 119.0643 | 121.8704 | -1.1673 | 121.8933 | 9.6176 | -1.236 | 121.8704 | -1.1673 | 9.6176 | 119.0643 | 121.8933 | -94.6243 | -94.5786
2303.9219 | 122.7997 | -8.3359 | 98.3093 | -0.21713 | 0.004939 | 0.0068722 | 0.010523 | -0.0026212 | -0.00093346 | 0.027124 | -8.1573 | 114.7156 | -8.4549 | 114.9902 | 111.9095 | 4.1016 | 4.2892 | 8.5327 | 114.4592 | -8.7433 | -0.11902 | 16.4062 | 0.17853 | 123.3261 | 13.6002 | -0.40741 | 16.1499 | 0.29755 | 12.6251 | 16.8686 | 120.2454 | 123.0515 | 0.17853 | 122.7951 | 12.4374 | -0.40741 | 123.0515 | 0.17853 | 12.4374 | 120.2454 | 122.7951 | -106.7642 | -107.0526
2304.9688 | 103.1067 | -4.7012 | 86.348 | 0.065155 | 0.004939 | 0.0045224 | 0.014368 | -0.001553 | -0.0015745 | 0.024774 | -7.1732 | 115.416 | -7.7911 | 115.5258 | 112.9211 | 3.8544 | 3.7903 | 8.5739 | 115.2191 | -7.7545 | -3.0899 | 29.068 | -2.4719 | 120.2271 | 26.5732 | -3.0533 | 28.8712 | 0.61798 | 8.4915 | 13.2751 | 117.6224 | 120.1172 | -2.4719 | 119.9203 | 8.5556 | -3.0533 | 120.1172 | -2.4719 | 8.5556 | 117.6224 | 119.9203 | -94.1391 | -94.1025
2305.9062 | 122.2046 | -7.3334 | 103.9719 | 0.3093 | 0.0040846 | 0.0023862 | 0.011805 | 0.00015601 | -0.0030697 | 0.025415 | -7.9468 | 114.7156 | -8.4869 | 115.4068 | 112.7335 | 4.4678 | 4.0604 | 8.6014 | 114.9948 | -7.9651 | -1.1536 | 10.7437 | -0.6134 | 122.7402 | 8.7616 | -0.63171 | 11.0229 | 0.54016 | 11.3937 | 15.9348 | 120.0668 | 122.049 | -0.6134 | 122.3282 | 11.8011 | -0.63171 | 122.049 | -0.6134 | 11.8011 | 120.0668 | 122.3282 | -112.4588 | -111.937
2306.9531 | 101.9394 | 0.23346 | 86.2473 | -0.1561 | 0.0040846 | 0.0028134 | 0.011164 | -0.0017666 | -0.0011471 | 0.021783 | -7.164 | 115.6219 | -7.5165 | 115.9653 | 113.3652 | 3.8589 | 4.097 | 8.7982 | 115.7913 | -7.2098 | -7.7499 | 29.3747 | -7.3975 | 115.7318 | 27.1179 | -7.4432 | 29.5441 | 0.35248 | 3.8635 | 8.5648 | 113.1317 | 115.3885 | -7.3975 | 115.5579 | 3.6255 | -7.4432 | 115.3885 | -7.3975 | 3.6255 | 113.1317 | 115.5579 | -93.7637 | -93.457
2307.9062 | 122.6624 | -7.5211 | 102.887 | 0.26352 | 0.004939 | -0.0025272 | 0.011805 | -0.0011258 | -7.9062e-05 | 0.024133 | -7.3654 | 115.3381 | -7.869 | 115.5899 | 112.793 | 3.5843 | 3.7399 | 8.0475 | 115.0726 | -7.9376 | -0.3479 | 12.4512 | 0.15564 | 123.111 | 9.906 | -0.41657 | 12.1857 | 0.50354 | 11.261 | 15.5685 | 120.314 | 122.8592 | 0.15564 | 122.5937 | 11.1053 | -0.41657 | 122.8592 | 0.15564 | 11.1053 | 120.314 | 122.5937 | -110.7559 | -110.8246
2308.9688 | 122.4518 | -7.4615 | 114.83 | 0.034637 | 0.0017346 | 0.00089078 | 0.0021917 | -0.003903 | 0.0020571 | 0.026696 | -7.1915 | 115.4114 | -7.7179 | 113.9923 | 112.1201 | 3.8361 | 4.3167 | 9.1003 | 115.1688 | -7.8552 | -0.25635 | 0.58136 | 0.27008 | 121.4539 | -2.71 | -0.39368 | 0.33875 | 0.52643 | 11.7783 | 16.5619 | 119.5816 | 122.8729 | 0.27008 | 122.6303 | 11.2976 | -0.39368 | 122.8729 | 0.27008 | 11.2976 | 119.5816 | 122.6303 | -122.5479 | -122.6852
2309.9219 | 122.9691 | -7.9651 | 114.1937 | -0.095062 | 0.0010938 | 0.0025998 | 0.0088141 | -0.0081754 | 0.0020571 | 0.027124 | -8.0933 | 114.7293 | -8.1985 | 115.123 | 112.4359 | 3.5751 | 3.7537 | 8.8806 | 114.8529 | -8.194 | -0.23346 | 0.53558 | -0.12817 | 123.0881 | -1.7578 | -0.22888 | 0.65918 | 0.10529 | 11.7188 | 16.8457 | 120.401 | 122.6944 | -0.12817 | 122.818 | 11.5402 | -0.22888 | 122.6944 | -0.12817 | 11.5402 | 120.401 | 122.818 | -122.3923 | -122.3877
2310.9531 | 98.1216 | -1.7532 | 85.7895 | -0.018768 | 0.0028028 | -0.00081822 | 0.018641 | -0.0045438 | -0.0013609 | 0.027124 | -7.7499 | 115.242 | -8.0612 | 114.8849 | 112.2253 | 3.6758 | 3.804 | 8.5693 | 114.8071 | -8.2077 | -6.308 | 29.4525 | -5.9967 | 116.6382 | 26.4359 | -6.4545 | 29.0176 | 0.31128 | 5.5573 | 10.3226 | 113.9786 | 116.9952 | -5.9967 | 116.5604 | 5.4291 | -6.4545 | 116.9952 | -5.9967 | 5.4291 | 113.9786 | 116.5604 | -93.8507 | -93.9972
2311.9062 | 122.6349 | -8.9676 | 104.9103 | 0.22537 | 0.0030164 | 0.001318 | 0.015864 | -0.0036892 | -0.00029266 | 0.031823 | -7.2418 | 115.4205 | -7.8094 | 114.3448 | 111.9141 | 3.3279 | 3.1403 | 7.4661 | 113.6948 | -9.2331 | 1.1581 | 10.5103 | 1.7258 | 123.3124 | 7.0038 | -0.2655 | 8.7845 | 0.56763 | 12.1078 | 16.4337 | 120.8817 | 124.3881 | 1.7258 | 122.6624 | 12.2955 | -0.2655 | 124.3881 | 1.7258 | 12.2955 | 120.8817 | 122.6624 | -112.7197 | -114.1434
2312.9688 | 91.4383 | 0.23346 | 82.9147 | 0.042267 | 0.0064344 | 0.0034544 | 0.015864 | -0.003262 | -0.00093346 | 0.023919 | -16.1728 | 110.3348 | -11.0184 | 115.8646 | 113.6261 | 5.0583 | 4.8614 | 9.462 | 115.9698 | -6.8436 | -11.2518 | 27.42 | -16.4062 | 115.6311 | 30.7114 | -7.077 | 33.0551 | -5.1544 | 4.628 | 9.2285 | 113.3926 | 110.1013 | -16.4062 | 115.7364 | 4.8248 | -7.077 | 110.1013 | -16.4062 | 4.8248 | 113.3926 | 115.7364 | -93.9331 | -89.7583
2313.9062 | 122.2641 | -7.2968 | 107.7255 | 0.21011 | 0.00088016 | 0.0072996 | 0.0062507 | -0.002194 | -0.0020017 | 0.025628 | -6.9901 | 115.7501 | -7.4249 | 115.4434 | 112.8479 | 4.0421 | 3.7125 | 8.7067 | 115.3793 | -7.6813 | -0.12817 | 8.0246 | 0.3067 | 122.7402 | 5.1224 | -0.38452 | 7.6538 | 0.43488 | 11.0092 | 16.0034 | 120.1447 | 123.0469 | 0.3067 | 122.6761 | 11.3388 | -0.38452 | 123.0469 | 0.3067 | 11.3388 | 120.1447 | 122.6761 | -115.1505 | -115.4068
2314.9531 | 119.2474 | -6.0928 | 103.2852 | 0.22537 | 0.0045118 | 0.0015316 | 0.0073187 | -0.003262 | 0.00013454 | 0.021142 | -6.2942 | 116.7068 | -6.4453 | 116.954 | 114.2029 | 4.1611 | 4.0833 | 9.2194 | 116.6702 | -6.3812 | -0.35248 | 13.4216 | -0.20142 | 123.0469 | 10.9177 | -0.28839 | 13.385 | 0.15106 | 10.1761 | 15.3122 | 120.2957 | 122.7997 | -0.20142 | 122.7631 | 10.2539 | -0.28839 | 122.7997 | -0.20142 | 10.2539 | 120.2957 | 122.7631 | -109.7305 | -109.6664
2315.9062 | 122.4609 | -7.5623 | 100.5295 | 0.25589 | 0.0047254 | 0.0021726 | 0.0133 | -0.0034756 | 0.00013454 | 0.025842 | -7.5165 | 115.0452 | -8.1161 | 115.4755 | 112.7747 | 4.1107 | 3.7445 | 8.6517 | 115.0177 | -7.9468 | -0.55389 | 14.5157 | 0.045777 | 123.0377 | 12.2452 | -0.38452 | 14.4882 | 0.59967 | 11.3068 | 16.214 | 120.3369 | 122.6074 | 0.045777 | 122.58 | 11.673 | -0.38452 | 122.6074 | 0.045777 | 11.673 | 120.3369 | 122.58 | -108.6456 | -108.4763
2316.9688 | 107.4921 | -6.5918 | 87.5793 | 0.11093 | 0.0051526 | 0.0025998 | 0.011805 | -0.0024076 | -0.0011471 | 0.021356 | -5.7678 | 117.0273 | -6.1935 | 116.7938 | 113.8733 | 3.5843 | 3.9139 | 8.8623 | 116.5649 | -6.5369 | 0.39825 | 29.4479 | 0.82397 | 123.3856 | 26.2939 | 0.054932 | 28.9856 | 0.42572 | 10.5057 | 15.4541 | 120.4651 | 123.6191 | 0.82397 | 123.1567 | 10.1761 | 0.054932 | 123.6191 | 0.82397 | 10.1761 | 120.4651 | 123.1567 | -93.7729 | -94.1162
2317.9062 | 122.2412 | -6.1295 | 112.4084 | 0.28641 | 0.0045118 | 0.0038816 | 0.011591 | -0.0034756 | 0.00034814 | 0.021356 | -5.8502 | 116.6428 | -6.6055 | 116.9266 | 113.5666 | 4.3945 | 4.1519 | 9.4757 | 116.6473 | -6.4682 | -0.47607 | 4.2343 | 0.27924 | 123.056 | 1.1581 | -0.33874 | 4.2389 | 0.75531 | 10.2814 | 15.6052 | 119.696 | 122.7722 | 0.27924 | 122.7768 | 10.524 | -0.33874 | 122.7722 | 0.27924 | 10.524 | 119.696 | 122.7768 | -119.014 | -118.8766
2318.9531 | 106.4026 | -7.1503 | 91.7084 | 0.15671 | 0.0047254 | 0.0040952 | 0.014155 | -0.003262 | -0.00071986 | 0.024987 | -6.5369 | 116.3864 | -6.8848 | 116.1987 | 112.3489 | 3.7125 | 4.0695 | 8.9676 | 116.098 | -7.0404 | 0.2655 | 24.678 | 0.6134 | 123.349 | 20.6406 | 0.10986 | 24.3896 | 0.3479 | 11.2198 | 16.1179 | 119.4992 | 123.5367 | 0.6134 | 123.2483 | 10.8627 | 0.10986 | 123.5367 | 0.6134 | 10.8627 | 119.4992 | 123.2483 | -98.5931 | -98.7488
2319.9062 | 122.4014 | -6.3171 | 109.6207 | 1.4995 | 0.0038708 | 0.00046358 | 0.0096685 | -0.003262 | -0.0011471 | 0.030114 | -6.8344 | 115.8371 | -7.1503 | 116.1118 | 113.3972 | 4.5273 | 3.8223 | 9.3796 | 116.2857 | -6.8161 | -0.83313 | 6.2164 | -0.51727 | 122.4289 | 3.7766 | -0.49896 | 6.665 | 0.31586 | 10.1395 | 15.6967 | 119.7144 | 122.1542 | -0.51727 | 122.6028 | 10.8444 | -0.49896 | 122.1542 | -0.51727 | 10.8444 | 119.7144 | 122.6028 | -116.7709 | -116.4368
2320.9531 | 112.8845 | -7.9651 | 90.2206 | 0.11856 | 0.004939 | 0.0058042 | 0.02334 | -0.0030484 | 0.0059023 | 0.03396 | -7.5851 | 115.2374 | -8.02 | 115.2054 | 112.4725 | 4.4357 | 3.7949 | 8.5419 | 115.1413 | -7.9971 | -0.054932 | 25.0168 | 0.37994 | 123.1705 | 22.2519 | -0.032043 | 24.9207 | 0.43488 | 11.7599 | 16.507 | 120.4376 | 123.2025 | 0.37994 | 123.1064 | 12.4008 | -0.032043 | 123.2025 | 0.37994 | 12.4008 | 120.4376 | 123.1064 | -98.2407 | -98.2178
2321.9062 | 108.6548 | -6.6742 | 114.6194 | 0.26352 | 0.0025892 | 0.0025998 | 0.0081733 | -0.0026212 | -0.0020017 | 0.028192 | -6.2851 | 116.5558 | -6.4865 | 116.4093 | 112.7747 | 3.6484 | 3.6026 | 8.7845 | 116.011 | -7.0221 | 0.18768 | 1.9363 | 0.3891 | 123.0835 | -1.8448 | -0.3479 | 1.3916 | 0.20142 | 10.2768 | 15.4587 | 119.4489 | 123.23 | 0.3891 | 122.6852 | 10.3226 | -0.3479 | 123.23 | 0.3891 | 10.3226 | 119.4489 | 122.6852 | -121.106 | -121.6415
2322.9688 | 102.8595 | -6.5552 | 86.7142 | 0.080414 | 0.0028028 | 0.0032406 | 0.015436 | -0.0030484 | -0.00071986 | 0.025628 | -6.2164 | 116.6656 | -6.4774 | 116.8213 | 113.562 | 3.9413 | 3.8681 | 8.4457 | 116.3406 | -6.7108 | 0.07782 | 29.9515 | 0.33875 | 123.3765 | 26.8478 | -0.15564 | 29.6265 | 0.26093 | 10.4233 | 15.0009 | 120.1172 | 123.2208 | 0.33875 | 122.8958 | 10.4965 | -0.15564 | 123.2208 | 0.33875 | 10.4965 | 120.1172 | 122.8958 | -93.1915 | -93.425
2323.9062 | 109.4559 | -5.7907 | 102.7222 | 0.20248 | 0.0053662 | 0.0043088 | 0.011805 | -0.002194 | -7.9062e-05 | 0.026056 | -5.4657 | 117.4393 | -5.7037 | 116.8854 | 113.9282 | 4.0192 | 4.2068 | 9.1736 | 117.0685 | -6.0928 | 0.086975 | 14.7171 | 0.32501 | 122.6761 | 11.2061 | -0.30212 | 14.3463 | 0.23804 | 9.9976 | 14.9643 | 119.7189 | 123.23 | 0.32501 | 122.8592 | 9.8099 | -0.30212 | 123.23 | 0.32501 | 9.8099 | 119.7189 | 122.8592 | -108.4259 | -108.815
2324.9688 | 122.5479 | -5.4749 | 105.986 | 0.233 | 0.0025892 | 0.003668 | 0.010096 | -0.0017666 | -0.0028561 | 0.023919 | -5.3879 | 117.1921 | -5.9189 | 117.3935 | 114.537 | 4.422 | 4.1107 | 9.2239 | 117.1555 | -5.9235 | -0.44403 | 11.2061 | 0.086976 | 122.8683 | 8.551 | -0.44861 | 11.1694 | 0.53101 | 9.5856 | 14.6988 | 120.0119 | 122.6669 | 0.086976 | 122.6303 | 9.8969 | -0.44861 | 122.6669 | 0.086976 | 9.8969 | 120.0119 | 122.6303 | -111.9049 | -111.9095
2325.9062 | 122.5662 | -5.5801 | 106.8375 | 0.233 | -0.00018804 | 0.004736 | 0.011805 | 0.00058321 | 0.00098914 | 0.024774 | -5.9555 | 116.6153 | -6.601 | 117.3615 | 114.3539 | 4.0558 | 3.6392 | 9.993 | 116.8991 | -6.0745 | -1.0208 | 9.7778 | -0.37537 | 122.9416 | 7.5165 | -0.49439 | 10.0616 | 0.64545 | 9.2194 | 15.5731 | 119.9341 | 122.1954 | -0.37537 | 122.4792 | 9.6359 | -0.49439 | 122.1954 | -0.37537 | 9.6359 | 119.9341 | 122.4792 | -113.4384 | -112.912
2326.9531 | 122.9691 | -14.0717 | 106.9794 | 0.1796 | 0.0034436 | 0.0043088 | 0.022699 | -0.0030484 | -0.00093346 | 0.050836 | -8.4366 | 114.3585 | -8.5281 | 111.1633 | 106.4987 | 0.75989 | 0.87891 | 6.3904 | 109.6939 | -13.353 | 5.5435 | 7.3792 | 5.6351 | 125.235 | -0.48065 | 0.71869 | 2.7145 | 0.091553 | 14.9506 | 20.462 | 120.5704 | 128.4302 | 5.6351 | 123.7656 | 14.8315 | 0.71869 | 128.4302 | 5.6351 | 14.8315 | 120.5704 | 123.7656 | -115.5075 | -120.3323
2327.9062 | 122.9507 | -7.4936 | 114.1617 | 0.27878 | 0.0025892 | 0.0025998 | 0.017359 | -0.0034756 | 0.00034814 | 0.030114 | -8.0017 | 115.0681 | -7.8186 | 115.9836 | 112.8891 | 3.8406 | 3.9963 | 9.3109 | 115.7181 | -7.4295 | -0.32501 | 0.90637 | -0.50812 | 123.4772 | -1.2726 | 0.064087 | 1.5564 | -0.18311 | 11.4899 | 16.8045 | 120.3827 | 122.5616 | -0.50812 | 123.2117 | 11.3342 | 0.064087 | 122.5616 | -0.50812 | 11.3342 | 120.3827 | 123.2117 | -121.9803 | -121.5912
2328.9688 | 99.3851 | 0.25635 | 87.4924 | -0.095062 | 0.0040846 | 0.0017454 | 0.015436 | -0.0024076 | -7.9062e-05 | 0.028192 | -5.864 | 116.716 | -6.4636 | 116.9083 | 114.0106 | 4.0741 | 4.2892 | 9.4528 | 117.0273 | -7.3929 | -6.72 | 29.2236 | -6.1203 | 116.6519 | 26.5182 | -7.6492 | 29.5349 | 0.59967 | 4.0329 | 9.1965 | 113.7543 | 116.4597 | -6.1203 | 116.7709 | 3.8177 | -7.6492 | 116.4597 | -6.1203 | 3.8177 | 113.7543 | 116.7709 | -93.956 | -94.8853
2329.9062 | 122.6303 | -4.6234 | 117.4347 | -0.034027 | 0.0030164 | -0.0023136 | 0.010096 | -0.0071072 | -0.0015745 | 0.029901 | -5.0034 | 117.5125 | -5.5069 | 118.2632 | 115.361 | 4.2801 | 4.184 | 9.3796 | 118.1671 | -4.7836 | -0.88348 | 0.07782 | -0.37994 | 122.8867 | -2.0737 | -0.16022 | 0.73242 | 0.50354 | 8.8074 | 14.003 | 119.9844 | 122.1359 | -0.37994 | 122.7905 | 8.9035 | -0.16022 | 122.1359 | -0.37994 | 8.9035 | 119.9844 | 122.7905 | -122.9416 | -122.2183
2330.9531 | 116.6977 | -15.8615 | 88.0783 | 0.21774 | 0.0064344 | 0.0032406 | 0.020563 | -0.0045438 | -0.0022153 | 0.032464 | -15.184 | 107.8766 | -15.3442 | 104.0359 | 103.45 | 4.4312 | 4.0054 | 5.7266 | 106.2378 | -16.9693 | 0.51727 | 19.7983 | 0.67749 | 119.8975 | 15.3717 | -1.1078 | 18.1595 | 0.16022 | 19.8669 | 21.5881 | 119.3115 | 123.7381 | 0.67749 | 122.0993 | 20.2927 | -1.1078 | 123.7381 | 0.67749 | 20.2927 | 119.3115 | 122.0993 | -103.4225 | -105.0476
2331.9062 | 122.6257 | -11.3251 | 111.4105 | 0.22537 | 0.001521 | 0.0043088 | 0.015864 | -0.0045438 | 0.00056194 | 0.033532 | -11.6776 | 111.1862 | -11.7371 | 110.733 | 108.6502 | 4.0146 | 3.3234 | 7.5668 | 111.3327 | -11.7188 | -0.41199 | -0.2243 | -0.35248 | 122.0581 | -2.7603 | -0.39368 | -0.077819 | 0.05951 | 14.6484 | 18.8919 | 119.9753 | 122.5113 | -0.35248 | 122.6578 | 15.3397 | -0.39368 | 122.5113 | -0.35248 | 15.3397 | 119.9753 | 122.6578 | -123.1476 | -123.1293
2332.9688 | 102.6123 | -60.5209 | 27.0721 | 2.0869 | 0.00323 | 0.00067718 | 0.021631 | -0.0064664 | -0.0017881 | 0.0044797 | -109.1766 | 13.3713 | -109.5978 | 13.4308 | 33.8791 | 30.5191 | 16.4291 | 11.1877 | 43.6157 | -84.2697 | -49.0768 | -13.7009 | -48.6557 | 73.9517 | 6.8069 | -23.7488 | 16.5436 | 0.42114 | 76.9501 | 71.7087 | 94.4 | 73.8922 | -48.6557 | 104.1367 | 91.04 | -23.7488 | 73.8922 | -48.6557 | 91.04 | 94.4 | 104.1367 | -136.6699 | -111.3419
2333.9062 | 122.8363 | -117.0044 | 5.6854 | 0.11093 | 0.00023916 | 0.0034544 | 0.014582 | -0.004971 | -0.00071986 | 0.0055479 | -116.9128 | 5.5801 | -117.4301 | 5.5435 | 5.3284 | -3.9413 | -13.0234 | -15.4358 | 5.6992 | -117.3935 | -0.42572 | -0.10529 | 0.091553 | 122.5479 | -0.35706 | -0.3891 | 0.013733 | 0.51727 | 103.981 | 101.5686 | 122.3328 | 122.5845 | 0.091553 | 122.7036 | 113.0631 | -0.3891 | 122.5845 | 0.091553 | 113.0631 | 122.3328 | 122.7036 | -123.1155 | -123.0789
2334.9688 | 122.9462 | -113.7817 | 8.8715 | 0.20248 | 0.002162 | 0.006445 | 0.016932 | -0.0024076 | -0.0026425 | 0.0036253 | -113.6353 | 8.8623 | -114.1846 | 8.8943 | 8.6838 | -3.6942 | -13.1699 | -14.6484 | 8.8715 | -114.212 | -0.40283 | -0.009155 | 0.14648 | 122.6761 | -0.18768 | -0.4303 | 0 | 0.54932 | 100.6119 | 99.1333 | 122.4655 | 122.644 | 0.14648 | 122.6532 | 110.0876 | -0.4303 | 122.644 | 0.14648 | 110.0876 | 122.4655 | 122.6532 | -123.056 | -123.0835
2335.9062 | 122.9645 | -114.1251 | 8.5739 | 0.20248 | -0.00040164 | 0.0038816 | 0.01565 | -0.0019802 | 0.0031253 | 0.0057615 | -113.8687 | 8.6655 | -114.3677 | 8.7021 | 8.2306 | -3.7491 | -13.1607 | -15.1611 | 8.6609 | -114.4547 | -0.24262 | 0.091552 | 0.25635 | 122.8271 | -0.34332 | -0.32959 | 0.086975 | 0.49896 | 100.9644 | 98.9639 | 122.3557 | 122.7905 | 0.25635 | 122.7859 | 110.376 | -0.32959 | 122.7905 | 0.25635 | 110.376 | 122.3557 | 122.7859 | -122.9416 | -123.0286
2336.9688 | 122.9141 | -113.7268 | 8.9218 | 0.18723 | 0.0030164 | 0.0038816 | 0.020777 | -0.0036892 | -0.00029266 | 0.0049069 | -113.5391 | 9.0271 | -114.0381 | 8.9127 | 8.4778 | -3.653 | -12.7258 | -15.3717 | 9.0042 | -114.1434 | -0.31128 | 0.10529 | 0.18768 | 122.6395 | -0.44403 | -0.41657 | 0.082397 | 0.49896 | 101.001 | 98.3551 | 122.2046 | 122.7539 | 0.18768 | 122.731 | 110.0739 | -0.41657 | 122.7539 | 0.18768 | 110.0739 | 122.2046 | 122.731 | -122.9599 | -123.0652
2337.9062 | 122.9416 | -113.5437 | 9.0683 | 0.12619 | 0.00066656 | 0.0015316 | 0.015436 | -0.0034756 | -0.0022153 | 0.0051205 | -113.0768 | 9.7 | -113.4979 | 8.9905 | 8.5648 | -3.8361 | -12.6251 | -15.7745 | 9.0454 | -113.9511 | 0.045776 | 0.63171 | 0.46692 | 122.5342 | -0.50354 | -0.40741 | -0.022888 | 0.42114 | 100.9186 | 97.7692 | 122.1085 | 123.2437 | 0.46692 | 122.5891 | 109.7076 | -0.40741 | 123.2437 | 0.46692 | 109.7076 | 122.1085 | 122.5891 | -122.5662 | -123.0194
2338.9531 | 122.1268 | -14.5111 | 102.8915 | 0.18723 | 0.0047254 | 0.0038816 | 0.0066779 | -0.0019802 | -0.0022153 | 0.02221 | -15.0375 | 107.7713 | -15.3168 | 108.5083 | 106.1691 | 3.6209 | 2.9205 | 7.1686 | 107.8171 | -14.9826 | -0.80566 | 4.8798 | -0.52643 | 123.0194 | 3.2776 | -0.4715 | 4.9255 | 0.27923 | 17.4316 | 21.6797 | 120.6802 | 122.2824 | -0.52643 | 122.3282 | 18.132 | -0.4715 | 122.2824 | -0.52643 | 18.132 | 120.6802 | 122.3282 | -118.2083 | -117.8741
2339.9062 | 122.5204 | -15.8295 | 106.2424 | -0.018768 | 0.0019482 | 0.0025998 | 0.0073187 | -0.0062528 | -0.00050626 | 0.022424 | -17.9535 | 105.7434 | -17.2073 | 107.9681 | 105.336 | 3.1036 | 2.8931 | 7.9056 | 107.2037 | -15.8066 | -1.3779 | -0.49896 | -2.124 | 123.7976 | -0.90637 | 0.022888 | 0.9613 | -0.74615 | 18.7225 | 23.735 | 121.1655 | 121.5729 | -2.124 | 123.0331 | 18.9331 | 0.022888 | 121.5729 | -2.124 | 18.9331 | 121.1655 | 123.0331 | -123.4497 | -122.049
2340.9688 | 122.2412 | -16.571 | 103.2852 | 0.042267 | 0.0068616 | -0.00081822 | 0.016932 | -0.0064664 | 0.00077554 | 0.025628 | -15.271 | 107.6294 | -15.4724 | 106.5399 | 104.3518 | 2.8931 | 2.4628 | 7.6401 | 106.4575 | -16.6351 | 1.0986 | 4.3442 | 1.3 | 123.111 | 1.0666 | -0.064087 | 3.1723 | 0.20142 | 19.0338 | 24.2111 | 120.9229 | 124.2004 | 1.3 | 123.0286 | 19.4641 | -0.064087 | 124.2004 | 1.3 | 19.4641 | 120.9229 | 123.0286 | -118.7576 | -119.9203
2341.9062 | 123.1064 | -64.9704 | 56.282 | 0.21011 | 0.004939 | 0.0038816 | 0.043421 | -0.0026212 | 0.00034814 | 0.039941 | -86.1877 | 39.5874 | -85.0616 | 46.2433 | 44.0231 | 12.5519 | 8.8211 | 5.127 | 55.3391 | -65.9729 | -20.0912 | -16.6946 | -21.2173 | 111.2137 | -12.2589 | -1.0025 | -0.94299 | -1.1261 | 73.7915 | 70.0974 | 108.9935 | 104.5578 | -21.2173 | 120.3094 | 77.5223 | -1.0025 | 104.5578 | -21.2173 | 77.5223 | 108.9935 | 120.3094 | -141.3437 | -122.2549
2342.9688 | 122.9324 | -112.3352 | 10.318 | 0.20248 | 0.001521 | 0.0043088 | 0.022699 | -0.00091219 | -0.0020017 | 0.0053343 | -111.7493 | 10.611 | -112.3123 | 11.1374 | 10.0525 | -3.804 | -12.3734 | -14.1541 | 10.762 | -112.6831 | 0.022888 | 0.29297 | 0.58594 | 123.4726 | -0.2655 | -0.3479 | 0.44403 | 0.56305 | 99.9619 | 98.1812 | 122.3877 | 122.9462 | 0.58594 | 123.0972 | 108.5312 | -0.3479 | 122.9462 | 0.58594 | 108.5312 | 122.3877 | 123.0972 | -122.6303 | -123.0011
2343.9062 | 122.9645 | -112.8204 | 9.7321 | 0.14145 | 0.0042982 | 0.0017454 | 0.016291 | -0.0019802 | -0.0011471 | 0.0027707 | -113.0768 | 9.3109 | -113.6627 | 9.3658 | 8.963 | -3.1082 | -12.4146 | -14.2456 | 9.5123 | -113.475 | -0.84228 | -0.42114 | -0.25635 | 122.1863 | -0.76904 | -0.6546 | -0.21973 | 0.58594 | 100.4059 | 98.5748 | 121.7834 | 122.1313 | -0.25635 | 122.3328 | 109.7122 | -0.6546 | 122.1313 | -0.25635 | 109.7122 | 121.7834 | 122.3328 | -123.3948 | -123.2071
2344.9688 | 122.905 | -115.329 | 7.3013 | 0.14145 | 0.0028028 | 0.0049496 | 0.023768 | -0.0024076 | -0.0013609 | 0.0055479 | -115.1001 | 7.4524 | -115.567 | 6.9809 | 6.6925 | -3.8544 | -13.6459 | -15.9256 | 7.3929 | -115.8417 | -0.23804 | 0.15106 | 0.22888 | 122.3099 | -0.60883 | -0.5127 | 0.091552 | 0.46692 | 101.683 | 99.4034 | 122.0215 | 122.7814 | 0.22888 | 122.7219 | 111.4746 | -0.5127 | 122.7814 | 0.22888 | 111.4746 | 122.0215 | 122.7219 | -122.8683 | -123.143
2345.9062 | 122.9828 | -108.4396 | 14.1541 | -0.20187 | 0.001521 | 0.0025998 | 0.017573 | -0.0043302 | -0.00093346 | 0.0074705 | -109.7855 | 12.7945 | -110.1242 | 12.6709 | 11.9156 | -2.8793 | -11.2656 | -13.6505 | 13.2339 | -109.4559 | -1.6846 | -1.3596 | -1.3458 | 121.1105 | -2.2385 | -1.0162 | -0.9201 | 0.33875 | 97.1741 | 94.7891 | 120.3552 | 121.2341 | -1.3458 | 121.6736 | 105.5603 | -1.0162 | 121.2341 | -1.3458 | 105.5603 | 120.3552 | 121.6736 | -124.2783 | -123.6099
2346.9688 | 122.8409 | -112.3993 | 9.8831 | -0.079803 | 0.0047254 | 0.006445 | 0.022913 | -0.0036892 | 0.0031253 | 0.0066159 | -112.2803 | 11.5997 | -112.3444 | 10.0342 | 10.08 | -3.7445 | -12.973 | -15.6784 | 10.0204 | -113.0035 | 0.054932 | 1.7166 | 0.11902 | 122.4335 | 0.19684 | -0.60425 | 0.13733 | 0.064087 | 99.4263 | 96.7209 | 122.4792 | 123.999 | 0.11902 | 122.4197 | 108.6548 | -0.60425 | 123.999 | 0.11902 | 108.6548 | 122.4792 | 122.4197 | -122.2275 | -122.8867
2347.9219 | 122.9919 | -113.4064 | 9.3246 | 0.027008 | 0.00045296 | 0.0023862 | 0.012018 | -0.0030484 | -0.0020017 | 0.0064023 | -114.0335 | 8.638 | -114.4867 | 8.9676 | 8.551 | -3.3508 | -12.4603 | -14.74 | 9.0637 | -113.8 | -1.0803 | -0.68665 | -0.62714 | 122.374 | -0.77362 | -0.39368 | -0.26093 | 0.45319 | 100.946 | 98.6664 | 121.9574 | 122.0444 | -0.62714 | 122.4701 | 110.0555 | -0.39368 | 122.0444 | -0.62714 | 110.0555 | 121.9574 | 122.4701 | -123.8113 | -123.1247
2348.9688 | 122.8592 | -102.5803 | 19.5648 | -0.36209 | 0.0036572 | 0.0066586 | 0.019068 | -0.0043302 | 0.00013454 | 0.0072569 | -96.2769 | 22.9935 | -96.9086 | 20.4575 | 19.1574 | -3.2913 | -11.6501 | -13.0463 | 20.43 | -102.7908 | 5.6717 | 3.4287 | 6.3034 | 123.0377 | -0.40741 | -0.21057 | 0.86517 | 0.63171 | 90.9302 | 89.534 | 121.7377 | 125.5737 | 6.3034 | 123.0103 | 99.2889 | -0.21057 | 125.5737 | 6.3034 | 99.2889 | 121.7377 | 123.0103 | -116.4734 | -122.3557
2349.9219 | 122.8592 | -115.9973 | 6.6101 | 0.049896 | 0.0030164 | 0.0096494 | 0.022272 | -0.0013394 | -0.0032835 | 0.0042661 | -115.8829 | 6.6971 | -116.3773 | 6.4911 | 6.2027 | -4.1153 | -13.472 | -16.7587 | 6.7795 | -116.3956 | -0.37994 | 0.086976 | 0.11444 | 122.4884 | -0.40741 | -0.39825 | 0.16937 | 0.49438 | 102.5253 | 99.2386 | 122.2 | 122.6944 | 0.11444 | 122.7768 | 111.882 | -0.39825 | 122.6944 | 0.11444 | 111.882 | 122.2 | 122.7768 | -122.9874 | -123.0057
2350.9688 | 122.9187 | -109.8724 | 12.6846 | 0.057526 | 0.0028028 | 0.0017454 | 0.021204 | 0.00058321 | -0.0013609 | 0.0051205 | -109.5795 | 13.0875 | -110.0647 | 12.7533 | 12.1307 | -3.8773 | -12.5198 | -14.7858 | 12.8494 | -110.3394 | -0.19226 | 0.40283 | 0.29297 | 122.6257 | -0.55389 | -0.46692 | 0.16479 | 0.48523 | 97.3526 | 95.0867 | 122.0032 | 122.9599 | 0.29297 | 122.7219 | 105.9952 | -0.46692 | 122.9599 | 0.29297 | 105.9952 | 122.0032 | 122.7219 | -122.7493 | -123.024
2351.9062 | 122.8958 | -110.6964 | 11.7828 | 0.057526 | 0.0036572 | 0.0068722 | 0.024195 | 0.001865 | -0.0030697 | 0.0087521 | -110.3622 | 11.9797 | -110.9619 | 10.9863 | 11.1145 | -3.3463 | -12.4283 | -14.6713 | 11.7279 | -111.1404 | -0.2655 | 0.19684 | 0.33417 | 121.6827 | -0.66834 | -0.44403 | -0.054932 | 0.59967 | 98.2681 | 96.0251 | 121.8109 | 122.6761 | 0.33417 | 122.4243 | 107.3502 | -0.44403 | 122.6761 | 0.33417 | 107.3502 | 121.8109 | 122.4243 | -122.7448 | -122.9233
2352.9219 | 122.9141 | -113.7817 | 8.9218 | -0.21713 | 0.0017346 | 3.6382e-05 | 0.018 | -0.0017666 | -0.0028561 | 0.0070431 | -113.4796 | 8.9859 | -114.006 | 8.5968 | 8.1436 | -3.5706 | -13.1287 | -15.8752 | 8.9035 | -114.1663 | -0.2243 | 0.064087 | 0.30212 | 122.3785 | -0.7782 | -0.38452 | -0.018311 | 0.52643 | 100.6531 | 97.9065 | 121.9254 | 122.7676 | 0.30212 | 122.6852 | 110.2112 | -0.38452 | 122.7676 | 0.30212 | 110.2112 | 121.9254 | 122.6852 | -122.9279 | -123.0881
2353.9531 | 122.8729 | -107.8354 | 14.7034 | 0.1033 | 0.0040846 | 0.005377 | 0.018854 | -0.002194 | -0.00050626 | 0.0057615 | -106.8512 | 16.0355 | -107.1854 | 14.8865 | 14.5294 | -3.7491 | -12.3459 | -14.3829 | 15.1199 | -108.2062 | 0.65002 | 1.3321 | 0.98419 | 122.7219 | -0.17395 | -0.37079 | 0.41657 | 0.33417 | 95.4895 | 93.4525 | 122.3648 | 123.8708 | 0.98419 | 122.9553 | 104.0863 | -0.37079 | 123.8708 | 0.98419 | 104.0863 | 122.3648 | 122.9553 | -121.8887 | -122.9095
2354.9062 | 122.9965 | -109.3506 | 13.4171 | 0.21011 | 0.00023916 | 0.0038816 | 0.0133 | -0.0043302 | -0.0022153 | 0.010034 | -109.1949 | 14.0488 | -109.7809 | 14.5294 | 13.9069 | -2.3254 | -11.705 | -14.2456 | 13.8519 | -109.4238 | -0.4303 | 0.63171 | 0.15564 | 123.88 | 0.48981 | -0.073242 | 0.43488 | 0.58594 | 97.6456 | 95.105 | 123.2574 | 123.3994 | 0.15564 | 123.2025 | 107.0251 | -0.073242 | 123.3994 | 0.15564 | 107.0251 | 123.2574 | 123.2025 | -123.1979 | -122.8409
2355.9531 | 122.8088 | -61.9675 | 0.004578 | 0.011749 | 0.0055798 | 0.0058042 | 0.023127 | -0.001553 | -0.0015745 | 0.0070431 | -107.5333 | 15.152 | -107.9727 | 15.683 | 14.566 | -4.216 | -11.6547 | -13.2568 | 15.4816 | -107.7393 | -46.0052 | 15.1474 | -45.5658 | 77.6505 | 14.5615 | -45.7718 | 15.477 | 0.43945 | 50.3128 | 48.7106 | 76.5335 | 77.1194 | -45.5658 | 77.449 | 57.7515 | -45.7718 | 77.1194 | -45.5658 | 57.7515 | 76.5335 | 77.449 | -107.9773 | -107.7438
2356.9062 | 105.7663 | -24.8703 | 71.6629 | 0.53055 | 0.0036572 | 0.0058042 | 0.033167 | -0.00069859 | -0.00071986 | 0.034387 | -28.4958 | 93.2098 | -29.8599 | 98.6206 | 97.7142 | 5.1407 | 2.4033 | 7.1915 | 97.7829 | -24.8886 | -4.9896 | 21.5469 | -3.6255 | 123.4909 | 26.0513 | -0.018311 | 26.12 | 1.3641 | 27.2736 | 32.0618 | 122.5845 | 118.0801 | -3.6255 | 122.6532 | 30.011 | -0.018311 | 118.0801 | -3.6255 | 30.011 | 122.5845 | 122.6532 | -101.5228 | -96.5515
2357.9844 | 123.0331 | -111.47 | 11.1053 | -0.11795 | -0.00018804 | 0.0034544 | 0.013514 | -0.0036892 | -0.0015745 | 0.0051205 | -111.3419 | 11.0229 | -112.0377 | 10.8765 | 10.4507 | -3.7399 | -13.3301 | -15.8569 | 10.8719 | -112.0651 | -0.56763 | -0.082398 | 0.12817 | 122.3465 | -0.6546 | -0.59509 | -0.23346 | 0.6958 | 98.14 | 95.6131 | 121.9208 | 122.493 | 0.12817 | 122.3419 | 107.7301 | -0.59509 | 122.493 | 0.12817 | 107.7301 | 121.9208 | 122.3419 | -123.143 | -123.1705
2358.9062 | 122.8455 | -114.8575 | 7.9285 | 0.065155 | 0.0051526 | 0.0023862 | 0.02569 | -0.0024076 | 0.00034814 | 0.0068295 | -115.1093 | 7.4158 | -115.6265 | 7.5165 | 7.4615 | -3.7582 | -13.559 | -16.5024 | 7.8644 | -115.3107 | -0.76904 | -0.5127 | -0.25177 | 122.374 | -0.46692 | -0.45319 | -0.064087 | 0.51727 | 101.2985 | 98.3551 | 122.319 | 122.2733 | -0.25177 | 122.7219 | 111.0992 | -0.45319 | 122.2733 | -0.25177 | 111.0992 | 122.319 | 122.7219 | -123.555 | -123.2391
2359.9688 | 122.905 | -114.8987 | 7.8369 | -0.011139 | 0.0025892 | 0.0051632 | 0.020563 | -0.0013394 | -0.0020017 | 0.0040525 | -114.7476 | 7.7911 | -115.2832 | 7.7408 | 7.3883 | -4.0375 | -13.6688 | -15.6372 | 7.901 | -115.2603 | -0.38452 | -0.045776 | 0.15106 | 122.6395 | -0.44861 | -0.36163 | 0.064087 | 0.53558 | 101.2299 | 99.2615 | 122.287 | 122.6898 | 0.15106 | 122.7997 | 110.8612 | -0.36163 | 122.6898 | 0.15106 | 110.8612 | 122.287 | 122.7997 | -123.1201 | -123.0972
2360.9062 | 123.0331 | -112.2025 | 10.2859 | 0.17197 | 0.002162 | 0.0075132 | 0.018 | -0.0026212 | -0.00050626 | 0.0053343 | -112.1841 | 10.3821 | -112.6877 | 10.1669 | 9.8328 | -3.7354 | -13.8794 | -15.0925 | 10.1349 | -112.8387 | -0.48523 | 0.09613 | 0.018311 | 122.3694 | -0.45319 | -0.63629 | -0.15106 | 0.50354 | 98.3231 | 97.11 | 122.0352 | 122.5845 | 0.018311 | 122.3373 | 108.4671 | -0.63629 | 122.5845 | 0.018311 | 108.4671 | 122.0352 | 122.3373 | -122.9736 | -123.1247
2361.9062 | 122.85 | -116.0385 | 6.8207 | 0.080414 | 0.00323 | 0.0072996 | 0.022699 | -0.0024076 | -0.0015745 | 0.0059751 | -115.8783 | 6.6422 | -116.3773 | 6.6055 | 6.3675 | -3.8681 | -13.8107 | -16.0355 | 6.9077 | -116.3406 | -0.33875 | -0.17853 | 0.16022 | 122.644 | -0.45319 | -0.30212 | 0.086975 | 0.49896 | 102.2278 | 100.0031 | 122.406 | 122.6807 | 0.16022 | 122.9462 | 112.1704 | -0.30212 | 122.6807 | 0.16022 | 112.1704 | 122.406 | 122.9462 | -123.1979 | -123.1613
2362.9844 | 122.8821 | -112.8433 | 9.9426 | -0.24002 | 0.00023916 | 0.0021726 | 0.014155 | -0.003903 | -0.0020017 | 0.0068295 | -112.7197 | 9.8831 | -113.1821 | 9.7824 | 9.3933 | -3.8589 | -13.2339 | -15.39 | 9.9518 | -113.1775 | -0.33875 | -0.059509 | 0.1236 | 122.6257 | -0.54932 | -0.33417 | 0.009155 | 0.46234 | 99.6094 | 97.4533 | 122.2366 | 122.7264 | 0.1236 | 122.7951 | 108.9844 | -0.33417 | 122.7264 | 0.1236 | 108.9844 | 122.2366 | 122.7951 | -123.1247 | -123.1201
2363.9062 | 122.8821 | -112.2116 | 10.4599 | 0.30167 | 0.0042982 | 0.001959 | 0.019495 | -0.0017666 | -0.0020017 | 0.0040525 | -112.0468 | 10.3912 | -112.6099 | 10.2722 | 9.8236 | -3.891 | -13.4445 | -15.834 | 10.4324 | -112.6831 | -0.39825 | -0.068665 | 0.16479 | 122.4838 | -0.63629 | -0.4715 | -0.027466 | 0.56305 | 98.7671 | 96.3776 | 122.0352 | 122.6028 | 0.16479 | 122.644 | 108.3206 | -0.4715 | 122.6028 | 0.16479 | 108.3206 | 122.0352 | 122.644 | -123.0698 | -123.143
2364.9688 | 122.9462 | -112.7106 | 9.9243 | 0.17197 | 0.0025892 | 0.0021726 | 0.014582 | -0.0019802 | -0.00093346 | 0.0072569 | -112.6923 | 9.7961 | -113.15 | 9.8007 | 9.5169 | -3.8269 | -13.6871 | -16.1316 | 9.9701 | -113.1363 | -0.43945 | -0.12817 | 0.01831 | 122.5113 | -0.40741 | -0.42572 | 0.045777 | 0.45776 | 99.0234 | 96.579 | 122.2275 | 122.5067 | 0.01831 | 122.6807 | 108.8837 | -0.42572 | 122.5067 | 0.01831 | 108.8837 | 122.2275 | 122.6807 | -123.0743 | -123.0606
2365.9062 | 122.9141 | -112.3764 | 10.1212 | -0.011139 | 0.00323 | 0.0087948 | 0.022913 | -0.002194 | -0.00071986 | 0.0051205 | -112.2711 | 10.2127 | -112.8296 | 10.2219 | 9.819 | -3.9001 | -13.7787 | -16.6168 | 10.2905 | -112.8845 | -0.45319 | 0.091553 | 0.10529 | 122.5983 | -0.30212 | -0.50812 | 0.16937 | 0.55847 | 98.5977 | 95.7596 | 122.1954 | 122.5891 | 0.10529 | 122.6669 | 108.4763 | -0.50812 | 122.5891 | 0.10529 | 108.4763 | 122.1954 | 122.6669 | -122.9507 | -123.0057
2366.9688 | 122.9279 | -117.2333 | 5.6168 | -0.22476 | 0.0040846 | 0.0079404 | 0.020777 | -0.00048499 | -0.0034971 | 0.0057615 | -117.0319 | 5.5481 | -117.5308 | 5.5573 | 5.2231 | -4.4174 | -14.5386 | -17.7063 | 5.7358 | -117.5217 | -0.29755 | -0.068664 | 0.20142 | 122.7905 | -0.39368 | -0.28839 | 0.11902 | 0.49896 | 102.6947 | 99.527 | 122.4564 | 122.7814 | 0.20142 | 122.9691 | 112.8159 | -0.28839 | 122.7814 | 0.20142 | 112.8159 | 122.4564 | 122.9691 | -123.1476 | -123.1384
2367.9219 | 122.85 | -112.2437 | 10.405 | 0.11093 | 0.00323 | 0.003027 | 0.02334 | -0.0011258 | -0.0030697 | 0.0053343 | -112.1429 | 10.5148 | -112.6099 | 10.2127 | 9.8328 | -4.0512 | -13.504 | -16.127 | 10.4141 | -112.7563 | -0.36621 | 0.10986 | 0.10071 | 122.4564 | -0.5722 | -0.5127 | 0.009156 | 0.46692 | 98.7396 | 96.1166 | 122.0764 | 122.7585 | 0.10071 | 122.6578 | 108.1924 | -0.5127 | 122.7585 | 0.10071 | 108.1924 | 122.0764 | 122.6578 | -123.0148 | -123.1613
2368.9688 | 122.8958 | -112.8571 | 9.7687 | -0.18662 | 0.0028028 | 0.0028134 | 0.017786 | -0.0030484 | -7.9062e-05 | 0.0046933 | -112.468 | 9.9243 | -112.9852 | 9.7412 | 9.1324 | -4.4449 | -13.9343 | -16.0995 | 9.9426 | -113.4109 | -0.12817 | 0.15564 | 0.3891 | 122.5983 | -0.63629 | -0.55389 | 0.17395 | 0.51727 | 98.9227 | 96.7575 | 121.9894 | 122.7814 | 0.3891 | 122.7997 | 108.4122 | -0.55389 | 122.7814 | 0.3891 | 108.4122 | 121.9894 | 122.7997 | -122.7539 | -123.1796
2369.9062 | 122.9507 | -112.1017 | 10.4965 | 0.233 | 0.0010938 | 0.0038816 | 0.021631 | -0.003903 | 0.00034814 | 0.0076841 | -111.4929 | 10.9589 | -111.9781 | 10.7162 | 10.0983 | -4.3076 | -14.1724 | -15.7562 | 10.7758 | -112.4908 | 0.1236 | 0.46234 | 0.60883 | 122.818 | -0.39825 | -0.3891 | 0.27924 | 0.48523 | 97.9294 | 96.3455 | 122.2 | 123.0606 | 0.60883 | 122.8775 | 107.7942 | -0.3891 | 123.0606 | 0.60883 | 107.7942 | 122.2 | 122.8775 | -122.4747 | -122.9874
2370.9688 | 122.8638 | -118.1168 | 4.6326 | -0.25528 | 0.0025892 | 0.0051632 | 0.018641 | -0.0019802 | 0.00013454 | 0.0061887 | -117.8513 | 4.66 | -118.3685 | 4.4678 | 4.2114 | -4.5914 | -14.74 | -17.07 | 4.6738 | -118.5608 | -0.25177 | 0.027466 | 0.2655 | 122.5845 | -0.42114 | -0.44403 | 0.041199 | 0.51727 | 103.3768 | 101.0468 | 122.3282 | 122.7768 | 0.2655 | 122.7905 | 113.5254 | -0.44403 | 122.7768 | 0.2655 | 113.5254 | 122.3282 | 122.7905 | -123.0011 | -123.1934
2371.9062 | 122.9095 | -116.1026 | 6.6879 | -0.034027 | 0.0034436 | 0.0066586 | 0.024836 | -0.0024076 | -0.00071986 | 0.0087521 | -115.8554 | 6.5643 | -116.4459 | 6.6925 | 6.3263 | -4.3671 | -14.0076 | -16.1224 | 6.7703 | -116.4734 | -0.34332 | -0.1236 | 0.24719 | 122.7951 | -0.36163 | -0.37079 | 0.082398 | 0.59051 | 102.095 | 99.9802 | 122.4289 | 122.6669 | 0.24719 | 122.8729 | 111.7355 | -0.37079 | 122.6669 | 0.24719 | 111.7355 | 122.4289 | 122.8729 | -123.1338 | -123.1613
2372.9844 | 122.9645 | -112.6373 | 10.0021 | 0.24826 | 0.0010938 | 0.0032406 | 0.012446 | -0.002194 | 0.0012027 | 0.0087521 | -112.4405 | 10.025 | -112.9395 | 9.9792 | 9.6313 | -3.8544 | -13.6917 | -15.1703 | 10.0616 | -113.0676 | -0.30212 | 0.022888 | 0.19684 | 122.6166 | -0.37079 | -0.4303 | 0.05951 | 0.49896 | 98.9456 | 97.467 | 122.2687 | 122.6624 | 0.19684 | 122.699 | 108.783 | -0.4303 | 122.6624 | 0.19684 | 108.783 | 122.2687 | 122.699 | -122.9416 | -123.0698
2373.9062 | 122.8958 | -115.6494 | 6.8939 | -0.17136 | 0.0042982 | 0.0043088 | 0.026758 | -0.0043302 | -0.00093346 | 0.0089657 | -115.242 | 7.6218 | -115.7318 | 7.164 | 6.7932 | -4.1473 | -14.122 | -16.4429 | 7.1686 | -116.1392 | -0.082398 | 0.72784 | 0.40741 | 122.8134 | -0.10071 | -0.48981 | 0.27466 | 0.48981 | 101.5274 | 99.2065 | 122.4426 | 123.2712 | 0.40741 | 122.818 | 111.5021 | -0.48981 | 123.2712 | 0.40741 | 111.5021 | 122.4426 | 122.818 | -122.6257 | -123.0331
2374.9844 | 122.8729 | -108.4259 | 14.3051 | 0.065155 | 0.0040846 | 0.003027 | 0.020777 | -0.0028348 | -0.0039243 | 0.0059751 | -108.1329 | 14.7949 | -108.9111 | 13.5452 | 13.2935 | -3.2822 | -12.5336 | -13.8474 | 13.7787 | -108.902 | -0.48523 | 0.48981 | 0.29297 | 121.9711 | -1.0117 | -0.47607 | -0.52643 | 0.7782 | 95.8923 | 94.5786 | 121.7194 | 123.2208 | 0.29297 | 122.2046 | 105.1437 | -0.47607 | 123.2208 | 0.29297 | 105.1437 | 121.7194 | 122.2046 | -123.2162 | -123.2071
2375.9062 | 122.9141 | -109.227 | 13.4079 | 0.027008 | 0.0040846 | 0.001318 | 0.022486 | -0.002194 | -0.0022153 | 0.0046933 | -109.1675 | 13.2248 | -109.7305 | 13.3667 | 12.9913 | -3.1128 | -12.9501 | -13.6414 | 13.4583 | -109.6573 | -0.50354 | -0.18311 | 0.05951 | 122.5937 | -0.41657 | -0.4303 | 0.050354 | 0.56305 | 96.2769 | 95.5856 | 122.2183 | 122.4518 | 0.05951 | 122.6852 | 106.1142 | -0.4303 | 122.4518 | 0.05951 | 106.1142 | 122.2183 | 122.6852 | -123.1384 | -123.0652
2376.9688 | 122.8821 | -113.0539 | 9.5535 | -0.13321 | 0.00323 | 0.004736 | 0.018 | -0.00027139 | -7.9062e-05 | 0.0036253 | -112.8662 | 9.5489 | -113.3926 | 9.5169 | 9.1965 | -3.8818 | -13.5727 | -14.0305 | 9.6954 | -113.4705 | -0.33875 | -0.004578 | 0.18768 | 122.5708 | -0.35706 | -0.41657 | 0.14191 | 0.52643 | 99.4812 | 99.0234 | 122.2504 | 122.6028 | 0.18768 | 122.7493 | 109.1721 | -0.41657 | 122.6028 | 0.18768 | 109.1721 | 122.2504 | 122.7493 | -122.9462 | -123.024
2377.9062 | 122.9782 | -113.4613 | 9.2331 | 0.24826 | 0.0038708 | 0.006445 | 0.018213 | -5.7592e-05 | -0.0030697 | 0.0064023 | -113.4521 | 9.1507 | -113.8596 | 9.2148 | 8.812 | -4.0237 | -13.9893 | -14.6347 | 9.256 | -113.8275 | -0.39825 | -0.082397 | 0.009156 | 122.6761 | -0.42114 | -0.36621 | 0.022888 | 0.40741 | 99.472 | 98.8266 | 122.2733 | 122.612 | 0.009156 | 122.7173 | 109.4376 | -0.36621 | 122.612 | 0.009156 | 109.4376 | 122.2733 | 122.7173 | -123.0927 | -123.0606
2378.9531 | 122.9691 | -115.9882 | 6.72 | 0.011749 | 0.0019482 | 0.001318 | 0.012232 | -0.0047574 | 0.00013454 | 0.0055479 | -115.7776 | 6.6833 | -116.1987 | 6.6971 | 6.3492 | -4.0512 | -14.1815 | -14.8636 | 6.7612 | -116.3864 | -0.21057 | -0.036621 | 0.21057 | 122.6852 | -0.37079 | -0.39826 | 0.041198 | 0.42114 | 101.8066 | 101.1246 | 122.3373 | 122.6715 | 0.21057 | 122.7493 | 111.937 | -0.39826 | 122.6715 | 0.21057 | 111.937 | 122.3373 | 122.7493 | -122.9187 | -123.1064
2379.9219 | 122.9736 | -117.1555 | 5.6168 | -1.2624 | 0.0017346 | 0.0028134 | 0.014795 | -0.0034756 | -0.0022153 | 0.0068295 | -117.1692 | 5.3558 | -117.6086 | 5.4153 | 5.1636 | -3.923 | -14.4516 | -15.8661 | 5.5801 | -117.4622 | -0.45319 | -0.26093 | -0.013732 | 122.5708 | -0.45319 | -0.3067 | -0.036621 | 0.43945 | 102.7039 | 101.2894 | 122.319 | 122.5113 | -0.013732 | 122.7356 | 113.2324 | -0.3067 | 122.5113 | -0.013732 | 113.2324 | 122.319 | 122.7356 | -123.2254 | -123.0789
2380.9688 | 122.9599 | -103.3813 | 19.4138 | -0.3392 | 0.0028028 | 0.00089078 | 0.028681 | -0.0071072 | -7.9062e-05 | 0.021783 | -103.8712 | 18.2327 | -104.3793 | 18.1412 | 17.1295 | -3.479 | -10.5789 | -10.9543 | 18.4525 | -104.0588 | -0.99792 | -1.181 | -0.48981 | 121.5225 | -2.2842 | -0.67749 | -0.9613 | 0.50812 | 92.8024 | 92.4271 | 120.5109 | 121.6141 | -0.48981 | 121.8338 | 99.9023 | -0.67749 | 121.6141 | -0.48981 | 99.9023 | 120.5109 | 121.8338 | -123.793 | -123.4726
2381.9062 | 122.9324 | -112.7884 | 9.9289 | -0.14847 | 0.0036572 | 0.0043088 | 0.025263 | -0.004971 | -0.0024289 | 0.0055479 | -112.8571 | 9.8007 | -113.2187 | 9.819 | 9.4254 | -3.6163 | -13.3392 | -13.8382 | 10.0159 | -113.1226 | -0.4303 | -0.12817 | -0.068665 | 122.6074 | -0.50354 | -0.33417 | 0.086975 | 0.36163 | 99.4492 | 98.9502 | 122.2137 | 122.5891 | -0.068665 | 122.8043 | 109.1721 | -0.33417 | 122.5891 | -0.068665 | 109.1721 | 122.2137 | 122.8043 | -123.1476 | -123.0515
2382.9688 | 123.0881 | -98.941 | 23.2224 | -0.27054 | 0.0019482 | 0.0058042 | 0.021418 | -0.0036892 | -0.00050626 | 0.0055479 | -110.7834 | 11.7416 | -111.3556 | 39.6378 | 36.351 | 1.3687 | -12.5381 | -11.2152 | 25.1221 | -98.3322 | -12.4146 | -11.4807 | -11.8423 | 138.5788 | 13.1287 | 0.60883 | 1.8997 | 0.57221 | 86.4029 | 87.7258 | 135.2921 | 110.6827 | -11.8423 | 124.0631 | 100.3098 | 0.60883 | 110.6827 | -11.8423 | 100.3098 | 135.2921 | 124.0631 | -134.5779 | -121.5546
2383.9062 | 122.8271 | -112.0651 | 10.3043 | -0.2095 | 0.0013074 | 0.0051632 | 0.025477 | -0.0034756 | 0.00056194 | 0.0085385 | -112.2482 | 10.1257 | -112.8113 | 10.5148 | 10.08 | -3.9688 | -13.5132 | -13.7924 | 10.3729 | -112.6328 | -0.74615 | -0.17853 | -0.18311 | 122.58 | -0.2243 | -0.56763 | 0.068665 | 0.56305 | 98.5519 | 98.2727 | 122.1451 | 122.1909 | -0.18311 | 122.438 | 108.0963 | -0.56763 | 122.1909 | -0.18311 | 108.0963 | 122.1451 | 122.438 | -123.1155 | -122.937
2384.9688 | 122.8683 | -113.4613 | 9.3109 | -0.32394 | 0.0036572 | 0.0051632 | 0.023554 | -0.00048499 | -0.0024289 | 0.0066159 | -113.4201 | 9.2834 | -113.7817 | 9.1461 | 8.638 | -4.0558 | -13.7192 | -13.7924 | 9.3567 | -113.7314 | -0.32043 | -0.027466 | 0.041199 | 122.6074 | -0.67291 | -0.27008 | 0.045776 | 0.36163 | 99.7421 | 99.6689 | 122.0993 | 122.7448 | 0.041199 | 122.818 | 109.4055 | -0.27008 | 122.7448 | 0.041199 | 109.4055 | 122.0993 | 122.818 | -123.0927 | -123.0423
2385.9219 | 122.9141 | -113.6902 | 9.0317 | 0.14145 | 0.0025892 | 0.0034544 | 0.022272 | 0.00036961 | -0.00093346 | 0.0078977 | -113.475 | 9.2148 | -113.9511 | 9.05 | 8.8257 | -3.923 | -14.0396 | -14.5157 | 9.2377 | -114.0106 | -0.26093 | 0.18311 | 0.21515 | 122.7402 | -0.20599 | -0.32043 | 0.20599 | 0.47607 | 99.6506 | 99.1745 | 122.5159 | 122.905 | 0.21515 | 122.9279 | 109.7672 | -0.32043 | 122.905 | 0.21515 | 109.7672 | 122.5159 | 122.9279 | -122.9828 | -123.0423
2386.9688 | 123.024 | -114.798 | 7.9285 | -0.27054 | 0.0025892 | -0.00017722 | 0.016718 | -0.0028348 | -0.0034971 | 0.0055479 | -114.6744 | 7.7225 | -115.2145 | 7.8461 | 7.5714 | -3.7033 | -13.9572 | -13.4857 | 7.9697 | -115.0772 | -0.41657 | -0.20599 | 0.1236 | 122.644 | -0.35706 | -0.27923 | 0.041199 | 0.54016 | 100.8408 | 101.3123 | 122.3694 | 122.5204 | 0.1236 | 122.7676 | 111.0947 | -0.27923 | 122.5204 | 0.1236 | 111.0947 | 122.3694 | 122.7676 | -123.143 | -123.0057
2387.9062 | 122.9141 | -114.6286 | 8.0933 | -0.21713 | 0.001521 | 0.004736 | 0.022913 | -0.0024076 | -0.00093346 | 0.0087521 | -114.5645 | 8.2809 | -114.9628 | 8.4045 | 7.7087 | -4.39 | -14.328 | -15.2756 | 8.2809 | -114.9994 | -0.33417 | 0.18768 | 0.064087 | 123.0331 | -0.38452 | -0.37079 | 0.18768 | 0.39825 | 100.3006 | 99.353 | 122.3373 | 122.9095 | 0.064087 | 122.9095 | 110.2386 | -0.37079 | 122.9095 | 0.064087 | 110.2386 | 122.3373 | 122.9095 | -123.056 | -123.0927
2388.9688 | 122.8409 | -115.3473 | 7.3746 | 0.095673 | 0.00323 | 0.0079404 | 0.022059 | -0.0017666 | -0.0013609 | 0.0076841 | -115.3152 | 7.3654 | -115.7547 | 7.1915 | 6.8069 | -4.2984 | -14.3646 | -15.2664 | 7.3837 | -115.7913 | -0.40741 | -0.009156 | 0.032043 | 122.5388 | -0.56763 | -0.44403 | 0.009155 | 0.43945 | 100.9827 | 100.0809 | 122.1542 | 122.7127 | 0.032043 | 122.731 | 111.0489 | -0.44403 | 122.7127 | 0.032043 | 111.0489 | 122.1542 | 122.731 | -123.1293 | -123.1659
2389.9062 | 122.8134 | -115.1047 | 7.4478 | -0.095062 | 0.0038708 | 0.0058042 | 0.026972 | 0.0010104 | -0.0015745 | 0.0070431 | -114.9078 | 7.6263 | -115.3931 | 7.489 | 7.3196 | -4.2206 | -14.4562 | -15.1566 | 7.7728 | -115.5121 | -0.28839 | 0.17853 | 0.19684 | 122.5937 | -0.12817 | -0.40741 | 0.32501 | 0.48523 | 100.6485 | 99.9481 | 122.4243 | 122.731 | 0.19684 | 122.8775 | 110.8841 | -0.40741 | 122.731 | 0.19684 | 110.8841 | 122.4243 | 122.8775 | -122.8409 | -122.9599
2390.9688 | 123.0194 | -115.2557 | 7.3746 | -0.11032 | 0.00045296 | 0.00089078 | 0.01095 | -0.0028348 | -0.0011471 | 0.0053343 | -115.2832 | 7.3105 | -115.773 | 7.2144 | 6.871 | -4.1016 | -14.502 | -15.2618 | 7.2922 | -115.5945 | -0.51727 | -0.064087 | -0.027466 | 122.4701 | -0.50354 | -0.33875 | -0.082398 | 0.48981 | 100.7538 | 99.9939 | 122.1268 | 122.5662 | -0.027466 | 122.5479 | 111.1542 | -0.33875 | 122.5662 | -0.027466 | 111.1542 | 122.1268 | 122.5479 | -123.1476 | -122.9691
2391.9062 | 122.9965 | -89.7263 | 33.0963 | 0.12619 | 0.0036572 | 0.0055906 | 0.029749 | -0.002194 | -0.0017881 | 0.016229 | -103.3035 | 18.5898 | -103.3127 | 30.7846 | 28.4866 | -2.6321 | -10.4141 | -7.6721 | 30.3085 | -91.5573 | -13.5864 | -14.5065 | -13.5773 | 120.5109 | -4.6097 | -1.8311 | -2.7878 | 0.009155 | 79.3121 | 82.0541 | 118.2129 | 108.316 | -13.5773 | 120.0348 | 87.0941 | -1.8311 | 108.316 | -13.5773 | 87.0941 | 118.2129 | 120.0348 | -136.409 | -124.6536
2392.9688 | 112.7151 | -111.2228 | 11.3571 | 0.16434 | 0.0019482 | 0.0040952 | 0.013727 | -0.0024076 | -0.00071986 | 0.0096067 | -110.2386 | 12.0071 | -110.6552 | 11.5997 | 10.9177 | -4.2892 | -13.5498 | -14.0762 | 11.4441 | -111.5982 | 0.56763 | 0.65002 | 0.98419 | 122.8226 | -0.43945 | -0.37537 | 0.086975 | 0.41657 | 97.673 | 97.1466 | 122.1405 | 123.23 | 0.98419 | 122.6669 | 106.9336 | -0.37537 | 123.23 | 0.98419 | 106.9336 | 122.1405 | 122.6669 | -122.0123 | -122.9553
2393.9062 | 122.8867 | -116.153 | 6.4362 | -0.20187 | 0.0030164 | 0.0045224 | 0.02035 | -0.004971 | -0.0017881 | 0.0055479 | -116.0248 | 6.6055 | -116.5466 | 6.4316 | 6.1707 | -4.2709 | -14.7903 | -15.6372 | 6.6513 | -116.5787 | -0.39368 | 0.16937 | 0.12817 | 122.5845 | -0.2655 | -0.42572 | 0.21515 | 0.52185 | 101.3626 | 100.5157 | 122.3236 | 122.7585 | 0.12817 | 122.8043 | 111.882 | -0.42572 | 122.7585 | 0.12817 | 111.882 | 122.3236 | 122.8043 | -122.9828 | -123.0148
2394.9688 | 122.9507 | -115.2695 | 7.4295 | 0.14145 | 0.0028028 | 0.0060178 | 0.019495 | -0.0036892 | -0.0024289 | 0.0064023 | -114.9353 | 7.4387 | -115.5212 | 7.5348 | 7.3288 | -3.9001 | -14.9231 | -15.6052 | 7.695 | -115.6128 | -0.25177 | 0.009156 | 0.33417 | 122.8043 | -0.10071 | -0.34332 | 0.2655 | 0.58594 | 100.3464 | 99.6643 | 122.5983 | 122.7081 | 0.33417 | 122.9645 | 111.3693 | -0.34332 | 122.7081 | 0.33417 | 111.3693 | 122.5983 | 122.9645 | -122.9507 | -123.0423
2395.9062 | 122.7356 | -114.6469 | 7.8735 | -0.018768 | 0.0030164 | 0.0028134 | 0.020563 | -0.0060392 | -0.0013609 | 0.0053343 | -113.6856 | 8.432 | -114.5325 | 8.2581 | 7.2968 | -4.8248 | -15.1932 | -15.0787 | 7.9147 | -115.3381 | 0.11444 | 0.55847 | 0.9613 | 122.905 | -0.57678 | -0.69122 | 0.041199 | 0.84686 | 99.4537 | 99.5682 | 121.9437 | 123.0789 | 0.9613 | 122.5616 | 109.8221 | -0.69122 | 123.0789 | 0.9613 | 109.8221 | 121.9437 | 122.5616 | -122.406 | -123.2117
2396.9844 | 122.8043 | -111.0077 | 11.7096 | 0.0041197 | 0.002162 | 0.0028134 | 0.020136 | -0.004971 | -0.0022153 | 0.0061887 | -111.4792 | 10.9955 | -111.969 | 11.7508 | 11.7783 | -3.3783 | -13.7604 | -14.3509 | 11.8057 | -111.4517 | -0.9613 | -0.71411 | -0.4715 | 122.7585 | 0.068664 | -0.44403 | 0.09613 | 0.48981 | 97.2473 | 96.6568 | 122.7859 | 122.0032 | -0.4715 | 122.8134 | 107.6294 | -0.44403 | 122.0032 | -0.4715 | 107.6294 | 122.7859 | 122.8134 | -123.6786 | -123.1613
2397.9219 | 122.9736 | -114.1296 | 8.4686 | 0.1033 | 0.00045296 | 0.0034544 | 0.020136 | -0.0013394 | -0.0020017 | 0.0083249 | -113.7955 | 8.5648 | -114.4135 | 8.4412 | 7.9559 | -4.2526 | -14.9414 | -14.0854 | 8.4366 | -114.5325 | -0.28381 | 0.09613 | 0.33417 | 122.5708 | -0.5127 | -0.40283 | -0.032044 | 0.61798 | 99.1882 | 100.0443 | 122.0856 | 122.6944 | 0.33417 | 122.5662 | 109.877 | -0.40283 | 122.6944 | 0.33417 | 109.877 | 122.0856 | 122.5662 | -122.8821 | -123.0011
2398.9688 | 122.1634 | -9.3521 | 101.4633 | -0.30106 | 0.0017346 | -0.001459 | 0.0066779 | -0.0058256 | -0.00071986 | 0.031396 | -9.8099 | 112.8479 | -10.3043 | 112.7151 | 108.9661 | 3.7857 | 5.0491 | 13.9435 | 113.0356 | -10.0891 | -0.95215 | 11.3846 | -0.45776 | 122.0673 | 7.5027 | -0.737 | 11.5723 | 0.49438 | 14.4012 | 23.2956 | 118.3182 | 122.2 | -0.45776 | 122.3877 | 13.1378 | -0.737 | 122.2 | -0.45776 | 13.1378 | 118.3182 | 122.3877 | -111.7676 | -111.5524
2399.9062 | 122.8546 | -117.0181 | 5.6625 | 0.53055 | 0.0025892 | 0.0055906 | 0.02334 | -0.0041166 | -0.00093346 | 0.0089657 | -117.0731 | 5.6534 | -117.4896 | 5.5618 | 5.2277 | -4.3671 | -15.2847 | -15.2252 | 5.69 | -117.485 | -0.4715 | -0.009156 | -0.054932 | 122.58 | -0.43488 | -0.46692 | 0.027465 | 0.41657 | 101.7334 | 101.7929 | 122.2458 | 122.6715 | -0.054932 | 122.7081 | 112.6511 | -0.46692 | 122.6715 | -0.054932 | 112.6511 | 122.2458 | 122.7081 | -123.1522 | -123.1476
2400.9688 | 123.0881 | -0.13733 | 73.2239 | -0.095062 | 0.0038708 | 0.0051632 | 0.028681 | -0.0030484 | -0.0026425 | 0.039514 | -17.72 | 104.7775 | -18.1824 | 104.8096 | 102.1271 | 4.1428 | 2.4582 | 8.2397 | 103.3813 | -19.6609 | -18.045 | 31.5537 | -17.5827 | 104.9469 | 28.9032 | -19.5236 | 30.1575 | 0.46234 | 2.5955 | 8.3771 | 102.2644 | 104.9149 | -17.5827 | 103.5187 | 4.2801 | -19.5236 | 104.9149 | -17.5827 | 4.2801 | 102.2644 | 103.5187 | -91.4062 | -92.8848
2401.9062 | 122.5845 | -14.1312 | 103.5324 | -0.24765 | 0.0023756 | -0.0018862 | 0.010096 | -0.004971 | -0.00093346 | 0.022851 | -13.5773 | 108.522 | -14.5386 | 109.1721 | 106.3339 | 5.0354 | 4.7058 | 12.7716 | 109.0988 | -14.09 | -0.40741 | 4.9896 | 0.55389 | 123.3032 | 2.8015 | 0.041199 | 5.5664 | 0.9613 | 18.837 | 26.9028 | 120.4651 | 122.6532 | 0.55389 | 123.23 | 19.1666 | 0.041199 | 122.6532 | 0.55389 | 19.1666 | 120.4651 | 123.23 | -118.071 | -117.6224
2402.9531 | 122.7631 | -11.7599 | 110.9482 | -0.018768 | 0.001521 | 0.00024998 | 0.0056097 | -0.0060392 | -0.0041379 | 0.025628 | -9.9289 | 112.7655 | -10.2905 | 109.7031 | 107.8217 | 5.2322 | 4.7928 | 14.1815 | 110.7376 | -12.4558 | 1.4694 | 1.8173 | 1.8311 | 121.463 | -3.1265 | -0.6958 | -0.21057 | 0.36163 | 16.5527 | 25.9415 | 119.5816 | 124.5255 | 1.8311 | 122.4976 | 16.9922 | -0.6958 | 124.5255 | 1.8311 | 16.9922 | 119.5816 | 122.4976 | -121.2387 | -123.4039
2403.9062 | 106.4713 | -5.9601 | 86.0092 | -0.19424 | 0.0040846 | 0.001318 | 0.022913 | -0.004971 | -0.0013609 | 0.023919 | -8.7982 | 114.0198 | -9.0637 | 115.2969 | 112.0972 | 5.4977 | 5.4382 | 15.9897 | 114.6423 | -8.4412 | -3.1036 | 28.0106 | -2.8381 | 121.257 | 26.088 | -2.4811 | 28.6331 | 0.2655 | 11.3983 | 21.9498 | 118.0573 | 119.9799 | -2.8381 | 120.6024 | 11.4578 | -2.4811 | 119.9799 | -2.8381 | 11.4578 | 118.0573 | 120.6024 | -95.0729 | -94.4504
2404.9688 | 122.9919 | -10.7895 | 111.4014 | -0.056915 | 0.0013074 | 0.0028134 | 0.0056097 | -0.0068936 | -7.9062e-05 | 0.024987 | -8.0704 | 114.5233 | -8.2581 | 113.0264 | 111.0626 | 6.5186 | 5.8456 | 15.1978 | 112.0697 | -11.554 | 2.5314 | 3.1219 | 2.7191 | 123.8159 | -0.33874 | -0.76446 | 0.66834 | 0.18768 | 16.6351 | 25.9872 | 121.8521 | 125.3128 | 2.7191 | 122.8592 | 17.308 | -0.76446 | 125.3128 | 2.7191 | 17.308 | 121.8521 | 122.8592 | -119.6594 | -122.9553
2405.9062 | 123.024 | -116.2216 | 6.9351 | -0.1561 | 0.00066656 | 0.001318 | 0.022913 | -0.003262 | -0.0024289 | 0.0040525 | -114.3082 | 7.5577 | -114.5874 | 6.6376 | 6.4362 | -4.3762 | -14.4196 | -12.9044 | 7.0312 | -116.2766 | 1.6342 | 0.62256 | 1.9135 | 122.8592 | -0.49896 | -0.054931 | 0.09613 | 0.27923 | 101.8021 | 103.3173 | 122.6578 | 123.7793 | 1.9135 | 123.2529 | 111.8454 | -0.054931 | 123.7793 | 1.9135 | 111.8454 | 122.6578 | 123.2529 | -121.5225 | -123.2117
2406.9062 | 122.9462 | -114.9261 | 7.7316 | -0.18662 | 0.0023756 | 0.0023862 | 0.025904 | -0.0024076 | -0.0037107 | 0.0076841 | -114.7476 | 7.901 | -115.3519 | 7.7637 | 7.3242 | -4.1428 | -14.8453 | -13.4674 | 7.7911 | -115.3748 | -0.42572 | 0.16937 | 0.17853 | 122.6898 | -0.40741 | -0.44861 | 0.05951 | 0.60425 | 100.0809 | 101.4587 | 122.2504 | 122.8271 | 0.17853 | 122.7173 | 110.7834 | -0.44861 | 122.8271 | 0.17853 | 110.7834 | 122.2504 | 122.7173 | -123.0835 | -123.1064
2407.9688 | 122.9416 | -117.2287 | 5.4108 | 0.080414 | 0.002162 | 0.0075132 | 0.025049 | -0.0011258 | -0.0030697 | 0.0089657 | -116.8259 | 5.5573 | -117.3706 | 5.4016 | 5.159 | -4.4449 | -15.8066 | -14.3829 | 5.5435 | -117.6086 | -0.14191 | 0.14648 | 0.40283 | 122.6303 | -0.25177 | -0.37994 | 0.13275 | 0.54474 | 101.4221 | 102.8458 | 122.3877 | 122.7859 | 0.40283 | 122.7722 | 112.7838 | -0.37994 | 122.7859 | 0.40283 | 112.7838 | 122.3877 | 122.7722 | -122.7814 | -123.0194
2408.9062 | 119.1971 | -115.6128 | 7.0175 | -0.16373 | 0.00088016 | 0.0028134 | 0.015223 | -0.0034756 | -0.0013609 | 0.0061887 | -115.48 | 7.1274 | -116.0019 | 7.0129 | 6.6193 | -5.0125 | -15.2618 | -13.4445 | 6.9855 | -116.0339 | -0.3891 | 0.10986 | 0.13275 | 122.6257 | -0.39825 | -0.42114 | -0.032043 | 0.52185 | 100.351 | 102.1683 | 122.2321 | 122.7402 | 0.13275 | 122.5983 | 110.6003 | -0.42114 | 122.7402 | 0.13275 | 110.6003 | 122.2321 | 122.5983 | -123.0194 | -123.0515
2409.9688 | 122.8409 | -113.1866 | 9.5215 | -0.34683 | 0.0030164 | 0.0090086 | 0.026331 | -0.0041166 | -0.00029266 | 0.0061887 | -113.2736 | 9.3338 | -113.6124 | 9.3384 | 8.8531 | -4.8111 | -15.1749 | -13.2477 | 9.5535 | -113.7955 | -0.42572 | -0.18768 | -0.086975 | 122.525 | -0.66833 | -0.60883 | 0.032044 | 0.33874 | 98.0118 | 99.939 | 122.0398 | 122.5204 | -0.086975 | 122.7402 | 108.3755 | -0.60883 | 122.5204 | -0.086975 | 108.3755 | 122.0398 | 122.7402 | -123.1338 | -123.317
2410.9062 | 123.0194 | -109.2819 | 13.2065 | -0.0035098 | 0.00023916 | 0.00089078 | 0.013727 | -0.0036892 | -0.0022153 | 0.0070431 | -107.4371 | 15.5182 | -108.0139 | 14.8865 | 13.6276 | -5.3925 | -14.5844 | -11.9431 | 14.0579 | -109.5886 | 1.268 | 2.3117 | 1.8448 | 124.1684 | 0.42114 | -0.3067 | 0.85144 | 0.57678 | 94.6976 | 97.3389 | 122.9095 | 124.8001 | 1.8448 | 123.3398 | 103.8895 | -0.3067 | 124.8001 | 1.8448 | 103.8895 | 122.9095 | 123.3398 | -121.2204 | -122.7951
2411.9531 | 100.0717 | -7.7042 | 94.6198 | -0.17899 | -0.00040164 | -0.0018862 | 0.0030463 | -0.0056118 | 0.00034814 | 0.022424 | -7.5989 | 115.1642 | -7.9605 | 115.329 | 112.7838 | 5.864 | 5.928 | 15.1108 | 115.2374 | -7.8049 | -0.25635 | 20.5444 | 0.10529 | 123.0331 | 18.1641 | -0.10071 | 20.6177 | 0.36163 | 13.6322 | 22.8149 | 120.488 | 122.8683 | 0.10529 | 122.9416 | 13.5681 | -0.10071 | 122.8683 | 0.10529 | 13.5681 | 120.488 | 122.9416 | -102.5803 | -102.4246
2412.9062 | 103.3401 | -4.3442 | 89.4058 | -0.1561 | 0.0038708 | 0.0043088 | 0.012659 | -0.0056118 | -0.00029266 | 0.025842 | -3.5156 | 119.0414 | -4.2206 | 118.9362 | 115.8783 | 6.0699 | 6.546 | 17.45 | 118.8446 | -4.2572 | 0.1236 | 29.6356 | 0.82855 | 123.2803 | 26.4725 | 0.086975 | 29.4388 | 0.70496 | 10.8902 | 21.7941 | 120.2225 | 123.3856 | 0.82855 | 123.1888 | 10.4141 | 0.086975 | 123.3856 | 0.82855 | 10.4141 | 120.2225 | 123.1888 | -93.6264 | -93.663
2413.9531 | 122.5159 | -3.5614 | 118.8858 | -0.14847 | 0.00045296 | 0.001318 | 0.0045417 | -0.0051846 | 0.00013454 | 0.027978 | -3.5202 | 119.2703 | -3.7491 | 119.3573 | 116.4001 | 6.0379 | 6.7566 | 18.7134 | 119.2841 | -3.8544 | -0.18768 | 0.38452 | 0.041198 | 122.9187 | -2.4857 | -0.29297 | 0.39826 | 0.22888 | 10.318 | 22.2748 | 119.9615 | 122.8317 | 0.041198 | 122.8455 | 9.5993 | -0.29297 | 122.8317 | 0.041198 | 9.5993 | 119.9615 | 122.8455 | -122.6349 | -122.7402
2414.9062 | 123.2986 | -69.9005 | 52.0935 | -0.079803 | -0.00018804 | 0.0034544 | 0.015864 | -0.0073208 | -0.0026425 | 0.013452 | -82.3929 | 63.7253 | -74.4415 | 49.5712 | 52.0844 | -7.4753 | -11.2518 | -3.8452 | 40.2603 | -74.1898 | -4.541 | 11.6318 | -12.4924 | 119.4717 | -0.009155 | -4.2892 | -11.8332 | -7.9514 | 58.6487 | 66.0553 | 121.9849 | 133.6258 | -12.4924 | 110.1608 | 62.4252 | -4.2892 | 133.6258 | -12.4924 | 62.4252 | 121.9849 | 110.1608 | -126.535 | -126.2833
2415.9531 | 122.905 | -7.9056 | 114.2349 | -0.095062 | 2.5564e-05 | -0.0040226 | 0.012018 | -0.0077482 | 0.00056194 | 0.032251 | -6.7795 | 115.8508 | -7.3151 | 115.6036 | 112.6053 | 5.4337 | 5.2139 | 16.951 | 115.0131 | -7.869 | 0.59052 | 1.6159 | 1.1261 | 123.5092 | -1.6296 | 0.036621 | 0.7782 | 0.53558 | 13.1195 | 24.8566 | 120.5109 | 123.7564 | 1.1261 | 122.9187 | 13.3392 | 0.036621 | 123.7564 | 1.1261 | 13.3392 | 120.5109 | 122.9187 | -121.55 | -122.1039
2416.9062 | 94.9036 | -11.055 | 91.5115 | -0.22476 | 0.00323 | 0.00089078 | 0.010309 | -0.0073208 | -0.0011471 | 0.048059 | -5.2185 | 117.4164 | -5.7999 | 112.6511 | 109.4925 | 3.6667 | 4.7012 | 14.7812 | 111.8271 | -11.4212 | 5.2551 | 25.9048 | 5.8365 | 123.7061 | 17.981 | -0.36621 | 20.3156 | 0.58136 | 15.7562 | 25.8362 | 120.5475 | 128.4714 | 5.8365 | 122.8821 | 14.7217 | -0.36621 | 128.4714 | 5.8365 | 14.7217 | 120.5475 | 122.8821 | -97.3114 | -102.9327
2417.9688 | 122.2092 | -24.7101 | 97.8882 | 0.97305 | 0.0023756 | 0.0062314 | 0.013727 | -0.0047574 | -0.00071986 | 0.016015 | -31.0684 | 90.2206 | -32.1487 | 96.73 | 94.812 | 5.7907 | 3.4607 | 7.5394 | 97.3206 | -25.383 | -7.4387 | -7.6675 | -6.3583 | 121.4401 | -3.0762 | -0.67291 | -0.56763 | 1.0803 | 28.1708 | 32.2495 | 119.5221 | 114.9307 | -6.3583 | 122.0306 | 30.5008 | -0.67291 | 114.9307 | -6.3583 | 30.5008 | 119.5221 | 122.0306 | -130.0369 | -123.2712
2418.9219 | 122.8317 | -98.5245 | 23.5794 | 0.072784 | 0.0030164 | 0.0079404 | 0.038935 | -0.0034756 | -7.9062e-05 | 0.02691 | -99.733 | 21.8079 | -101.2848 | 37.9898 | 28.5278 | -0.70038 | -11.586 | -12.1719 | 29.7729 | -96.199 | -2.7603 | -1.7715 | -1.2085 | 136.5143 | 4.9484 | 2.3254 | 6.1935 | 1.5518 | 86.9385 | 86.3525 | 127.0523 | 120.3323 | -1.2085 | 128.2974 | 97.8241 | 2.3254 | 120.3323 | -1.2085 | 97.8241 | 127.0523 | 128.2974 | -124.8642 | -119.7784
2419.9688 | 122.6807 | -14.9872 | 107.0023 | -0.026398 | 0.00323 | -0.0023136 | 0.0077459 | -0.003903 | 0.00034814 | 0.017511 | -16.3971 | 106.6406 | -16.1545 | 108.6731 | 105.0293 | 3.4515 | 4.3121 | 10.6339 | 107.4188 | -15.5731 | -1.1673 | -0.36163 | -1.4099 | 123.6603 | -1.973 | -0.58594 | 0.41657 | -0.24262 | 19.2993 | 25.621 | 120.0165 | 121.6278 | -1.4099 | 122.406 | 18.4387 | -0.58594 | 121.6278 | -1.4099 | 18.4387 | 120.0165 | 122.406 | -123.1567 | -122.5754
2420.9062 | 117.0868 | -15.4404 | 107.1167 | -0.13321 | 0.0025892 | -0.00081822 | 0.0013373 | -0.0075344 | 0.00077554 | 0.01986 | -15.8478 | 107.3456 | -15.6281 | 107.8491 | 105.4092 | 4.985 | 3.4287 | 9.6222 | 107.2678 | -15.6921 | -0.18768 | 0.22888 | -0.40741 | 123.2895 | -1.7075 | -0.25177 | 0.15106 | -0.21973 | 18.869 | 25.0626 | 120.8496 | 122.7859 | -0.40741 | 122.7081 | 20.4254 | -0.25177 | 122.7859 | -0.40741 | 20.4254 | 120.8496 | 122.7081 | -122.7448 | -122.8088
2421.9688 | 122.5388 | -9.0271 | 113.1454 | 0.14908 | 0.0017346 | 0.001318 | 0.0047553 | -0.0071072 | -0.00071986 | 0.020288 | -9.0729 | 113.8229 | -9.3338 | 113.9053 | 110.7788 | 5.2597 | 5.2139 | 16.3559 | 113.6765 | -9.3384 | -0.3067 | 0.67749 | -0.045776 | 122.9324 | -2.3666 | -0.31128 | 0.53101 | 0.26092 | 14.241 | 25.383 | 119.8059 | 122.85 | -0.045776 | 122.7036 | 14.2868 | -0.31128 | 122.85 | -0.045776 | 14.2868 | 119.8059 | 122.7036 | -122.4792 | -122.4838
2422.9062 | 123.0972 | -25.209 | 96.9818 | -0.026398 | -0.00040164 | 0.0043088 | 0.060511 | -0.0058256 | -0.00071986 | 0.073907 | -24.8245 | 98.0301 | -25.0305 | 96.7209 | 94.3039 | 3.4973 | 2.3254 | 10.3134 | 96.9543 | -25.882 | 0.17853 | 1.0483 | 0.38452 | 121.9299 | -2.6779 | -0.67291 | -0.027466 | 0.20599 | 27.5345 | 35.5225 | 119.5129 | 123.2391 | 0.38452 | 122.1634 | 28.7064 | -0.67291 | 123.2391 | 0.38452 | 28.7064 | 119.5129 | 122.1634 | -122.0123 | -122.8638
2423.9531 | 122.168 | -16.2552 | 105.9448 | 0.042267 | 2.5564e-05 | -0.0016726 | 0.0026191 | -0.00668 | -0.00029266 | 0.016015 | -17.3264 | 105.6885 | -17.395 | 106.4209 | 103.4637 | 4.6738 | 3.7033 | 11.5128 | 106.1554 | -16.7725 | -1.1398 | -0.25635 | -1.0712 | 122.6761 | -2.4811 | -0.51727 | 0.21057 | 0.068665 | 19.9585 | 27.7679 | 119.7189 | 121.9437 | -1.0712 | 122.4106 | 20.929 | -0.51727 | 121.9437 | -1.0712 | 20.929 | 119.7189 | 122.4106 | -123.3398 | -122.7173
2424.9062 | 122.2687 | -7.6035 | 108.5907 | -0.14847 | 0.002162 | -0.0018862 | 0.0045417 | -0.0071072 | -0.00050626 | 0.01922 | -7.663 | 115.0497 | -7.9742 | 115.2145 | 112.3169 | 5.5344 | 5.0812 | 10.1028 | 114.9445 | -8.0933 | -0.37079 | 6.459 | -0.059509 | 122.818 | 3.7262 | -0.48981 | 6.3538 | 0.31128 | 12.6846 | 17.7063 | 119.9203 | 122.6532 | -0.059509 | 122.5479 | 13.1378 | -0.48981 | 122.6532 | -0.059509 | 13.1378 | 119.9203 | 122.5479 | -116.5649 | -116.684
2425.9531 | 122.4976 | -10.3683 | 111.6486 | 0.080414 | -0.0010424 | 0.001959 | 0.0017645 | -0.0051846 | 0.0014163 | 0.018579 | -10.0204 | 112.6099 | -10.4736 | 112.3352 | 109.996 | 5.6168 | 4.9026 | 11.087 | 112.5092 | -10.5927 | -0.10529 | 0.9613 | 0.3479 | 122.7036 | -1.6525 | -0.2243 | 0.8606 | 0.45319 | 15.271 | 21.4554 | 120.3644 | 122.9782 | 0.3479 | 122.8775 | 15.9851 | -0.2243 | 122.9782 | 0.3479 | 15.9851 | 120.3644 | 122.8775 | -122.1222 | -122.2412
2426.9062 | 122.4243 | -10.8856 | 111.2137 | 0.034637 | 0.0019482 | -0.0027408 | -0.0025079 | -0.0081754 | 0.00077554 | 0.017938 | -11.0001 | 111.7447 | -11.2564 | 112.088 | 109.14 | 5.1727 | 4.7745 | 14.6255 | 111.8317 | -11.1465 | -0.37079 | 0.53101 | -0.11444 | 122.9736 | -2.0737 | -0.26093 | 0.61798 | 0.25635 | 15.6601 | 25.5112 | 120.0256 | 122.6303 | -0.11444 | 122.7173 | 16.0583 | -0.26093 | 122.6303 | -0.11444 | 16.0583 | 120.0256 | 122.7173 | -122.4701 | -122.3602
2427.9688 | 101.7746 | -6.514 | 89.2868 | -0.19424 | 0.0030164 | -0.0023136 | 0.0062507 | -0.0068936 | -0.00071986 | 0.01687 | -6.0471 | 116.6748 | -6.5872 | 116.8854 | 113.7405 | 5.4016 | 5.6946 | 15.1978 | 116.6199 | -6.4499 | -0.073242 | 27.388 | 0.46692 | 123.3994 | 24.4537 | 0.064087 | 27.3331 | 0.54016 | 12.2086 | 21.7117 | 120.2545 | 123.1888 | 0.46692 | 123.1338 | 11.9156 | 0.064087 | 123.1888 | 0.46692 | 11.9156 | 120.2545 | 123.1338 | -95.874 | -95.7367
2428.9062 | 122.1542 | -6.7337 | 114.9261 | -0.10269 | 0.00066656 | 0.00089078 | 0.0004827 | -0.0062528 | -7.9062e-05 | 0.020501 | -6.7429 | 115.8875 | -7.1777 | 116.098 | 113.1454 | 5.7724 | 5.4977 | 15.4953 | 115.8966 | -7.132 | -0.44403 | 0.9613 | -0.009155 | 122.8317 | -1.7807 | -0.39825 | 0.97046 | 0.43487 | 12.2314 | 22.229 | 119.8792 | 122.6212 | -0.009155 | 122.6303 | 12.5061 | -0.39825 | 122.6212 | -0.009155 | 12.5061 | 119.8792 | 122.6303 | -122.1039 | -122.0581
2429.9688 | 119.9936 | -5.7907 | 113.8367 | 0.20248 | 0.00323 | 0.0049496 | 0.0053961 | -0.004971 | 0.00077554 | 0.019647 | -5.6442 | 117.1509 | -6.0104 | 117.3294 | 114.2395 | 5.6717 | 5.4977 | 17.2211 | 117.1188 | -5.9738 | -0.21973 | 3.3142 | 0.14648 | 123.1201 | 0.40283 | -0.18311 | 3.2822 | 0.36621 | 11.2885 | 23.0118 | 120.0302 | 122.9416 | 0.14648 | 122.9095 | 11.4624 | -0.18311 | 122.9416 | 0.14648 | 11.4624 | 120.0302 | 122.9095 | -119.8471 | -119.8105
2430.9062 | 122.4609 | -5.4565 | 117.1463 | -0.041657 | 0.0034436 | 0.0021726 | -0.0018671 | -0.0047574 | -0.00050626 | 0.016442 | -5.3467 | 117.3111 | -5.7587 | 117.5949 | 114.5599 | 5.9555 | 5.571 | 18.3334 | 117.3203 | -5.7312 | -0.30212 | 0.1648 | 0.10986 | 123.0515 | -2.5864 | -0.27466 | 0.17395 | 0.41199 | 11.0275 | 23.79 | 120.0165 | 122.7676 | 0.10986 | 122.7768 | 11.412 | -0.27466 | 122.7676 | 0.10986 | 11.412 | 120.0165 | 122.7768 | -122.905 | -122.8775
2431.9688 | 122.3419 | -10.1624 | 111.8317 | 0.18723 | 0.00023916 | 0.005377 | 0.0015509 | -0.004971 | 0.0014163 | 0.015161 | -10.1669 | 112.5824 | -10.5011 | 112.8021 | 109.9091 | 5.452 | 5.0308 | 16.8961 | 112.4817 | -10.4691 | -0.33874 | 0.75073 | -0.004577 | 122.9645 | -1.9226 | -0.3067 | 0.65002 | 0.33417 | 15.1932 | 27.0584 | 120.0714 | 122.7448 | -0.004577 | 122.644 | 15.6143 | -0.3067 | 122.7448 | -0.004577 | 15.6143 | 120.0714 | 122.644 | -122.3328 | -122.3007
2432.9062 | 122.4701 | -9.2285 | 113.562 | -0.12558 | 0.0023756 | 0.00046358 | -0.0001581 | -0.0079618 | -0.0011471 | 0.015802 | -9.3613 | 113.4064 | -9.6497 | 113.7085 | 111.1359 | 5.8594 | 4.8019 | 16.5482 | 113.3972 | -9.5627 | -0.42114 | -0.15564 | -0.13275 | 122.937 | -2.4261 | -0.33417 | -0.16479 | 0.28839 | 14.0305 | 25.7767 | 120.3644 | 122.6349 | -0.13275 | 122.6257 | 15.0879 | -0.33417 | 122.6349 | -0.13275 | 15.0879 | 120.3644 | 122.6257 | -123.2117 | -123.1247
2433.9688 | 122.5067 | -9.0546 | 113.3102 | 0.042267 | 0.0023756 | -0.003168 | 5.5496e-05 | -0.0081754 | 0.0024845 | 0.017511 | -8.9859 | 113.7955 | -9.2697 | 114.0106 | 111.058 | 5.4886 | 5.3375 | 16.9464 | 113.6902 | -9.3018 | -0.21515 | 0.48523 | 0.068664 | 123.0652 | -2.2522 | -0.24719 | 0.37994 | 0.28381 | 14.3921 | 26.001 | 120.1126 | 122.85 | 0.068664 | 122.7448 | 14.5432 | -0.24719 | 122.85 | 0.068664 | 14.5432 | 120.1126 | 122.7448 | -122.58 | -122.612
2434.9219 | 114.505 | -8.6334 | 111.232 | -0.19424 | 0.0030164 | 0.0017454 | 0.0036871 | -0.0086026 | -7.9062e-05 | 0.01687 | -8.7616 | 114.1891 | -8.9951 | 114.3585 | 111.4563 | 5.4611 | 5.6396 | 15.9073 | 114.1983 | -8.8852 | -0.36163 | 2.9572 | -0.12817 | 122.9919 | 0.2243 | -0.25177 | 2.9663 | 0.23346 | 14.2731 | 24.5407 | 120.0897 | 122.8226 | -0.12817 | 122.8317 | 14.0945 | -0.25177 | 122.8226 | -0.12817 | 14.0945 | 120.0897 | 122.8317 | -120.2271 | -120.1172
2435.9531 | 122.4289 | -9.2743 | 112.8662 | 0.21011 | 0.0010938 | 0.0011044 | 0.0019781 | -0.0043302 | -0.00050626 | 0.017511 | -9.2743 | 113.4338 | -9.6405 | 113.6444 | 110.788 | 5.5756 | 5.2368 | 16.42 | 113.3698 | -9.6268 | -0.36621 | 0.56763 | 0 | 122.9187 | -2.0782 | -0.35248 | 0.50354 | 0.36621 | 14.5111 | 25.6943 | 120.0623 | 122.7081 | 0 | 122.644 | 14.8499 | -0.35248 | 122.7081 | 0 | 14.8499 | 120.0623 | 122.644 | -122.5067 | -122.493
2436.9062 | 122.9691 | -16.1362 | 106.0501 | -0.079803 | 0.0017346 | -0.003168 | 0.0002691 | -0.0051846 | 0.00056194 | 0.014734 | -16.1362 | 106.6727 | -16.3559 | 106.9244 | 104.187 | 4.9393 | 4.0604 | 14.5157 | 106.5582 | -16.4154 | -0.21973 | 0.62256 | 0 | 123.0606 | -1.8631 | -0.27924 | 0.50812 | 0.21973 | 20.1965 | 30.6519 | 120.3232 | 122.8088 | 0 | 122.6944 | 21.0754 | -0.27924 | 122.8088 | 0 | 21.0754 | 120.3232 | 122.6944 | -122.406 | -122.4655
2437.9688 | 122.2916 | -12.4466 | 109.5154 | 0.16434 | 0.002162 | 0.0040952 | 0.0051825 | -0.0056118 | -0.00071986 | 0.015588 | -12.529 | 110.257 | -12.8357 | 110.4263 | 107.4738 | 5.2094 | 4.4815 | 14.1678 | 110.0143 | -12.941 | -0.3891 | 0.74158 | -0.082398 | 122.8729 | -2.0416 | -0.49439 | 0.49896 | 0.3067 | 16.9281 | 26.6144 | 119.9203 | 122.7036 | -0.082398 | 122.4609 | 17.6559 | -0.49439 | 122.7036 | -0.082398 | 17.6559 | 119.9203 | 122.4609 | -122.3511 | -122.4564
2438.9062 | 122.6166 | -11.0596 | 110.8795 | 0.15671 | 2.5564e-05 | -0.0018862 | 5.5496e-05 | -0.0064664 | 0.0018435 | 0.016442 | -11.0596 | 111.7722 | -11.2747 | 111.8958 | 109.0942 | 5.4337 | 4.6875 | 15.4312 | 111.6577 | -11.3205 | -0.21515 | 0.89264 | 0 | 122.9553 | -1.7853 | -0.26093 | 0.7782 | 0.21515 | 15.7471 | 26.4908 | 120.1538 | 122.8317 | 0 | 122.7173 | 16.4932 | -0.26093 | 122.8317 | 0 | 16.4932 | 120.1538 | 122.7173 | -122.1542 | -122.2
2439.9688 | 122.3648 | -8.725 | 113.3194 | 0.32455 | 0.00045296 | 0.00067718 | 0.0036871 | -0.0056118 | 0.00056194 | 0.019647 | -8.7753 | 113.942 | -9.0912 | 114.1891 | 111.2778 | 5.5756 | 4.9988 | 15.9073 | 113.8641 | -9.1095 | -0.36621 | 0.62256 | -0.050354 | 122.9141 | -2.0416 | -0.38452 | 0.54474 | 0.31586 | 13.7238 | 24.6323 | 120.0027 | 122.6669 | -0.050354 | 122.5891 | 14.3005 | -0.38452 | 122.6669 | -0.050354 | 14.3005 | 120.0027 | 122.5891 | -122.4106 | -122.4289
2440.9062 | 122.4609 | -5.8823 | 116.629 | -0.10269 | 0.001521 | 0.0032406 | 0.0006965 | -0.0071072 | -0.0015745 | 0.018365 | -5.7816 | 116.8808 | -6.2027 | 117.1921 | 114.1937 | 5.8823 | 5.6396 | 16.7038 | 116.8442 | -6.1615 | -0.32043 | 0.25177 | 0.10071 | 123.0743 | -2.4353 | -0.27924 | 0.21515 | 0.42114 | 11.5219 | 22.5861 | 120.076 | 122.7631 | 0.10071 | 122.7264 | 11.7645 | -0.27924 | 122.7631 | 0.10071 | 11.7645 | 120.076 | 122.7264 | -122.8317 | -122.7905
2441.9531 | 98.7854 | -2.0691 | 105.0339 | 0.042267 | 0.004939 | 0.0040952 | 0.0045417 | -0.003262 | -0.00093346 | 0.017511 | -5.4565 | 117.3523 | -5.8365 | 117.4484 | 114.3997 | 5.722 | 6.0104 | 16.5939 | 117.2699 | -5.8044 | -3.7674 | 12.3184 | -3.3875 | 119.5175 | 9.3658 | -3.7354 | 12.236 | 0.37994 | 8.0795 | 18.663 | 116.4688 | 119.4214 | -3.3875 | 119.339 | 7.7911 | -3.7354 | 119.4214 | -3.3875 | 7.7911 | 116.4688 | 119.339 | -110.8704 | -110.8383
2442.9062 | 122.6212 | -5.7495 | 116.2582 | -0.018768 | 0.0030164 | -0.0050906 | -0.0012261 | -0.0034756 | -0.0013609 | 0.01986 | -5.7449 | 117.0044 | -6.1386 | 117.3203 | 114.2761 | 5.7266 | 5.8044 | 16.7908 | 117.0502 | -5.9692 | -0.3891 | 0.74616 | 0.004578 | 123.0698 | -1.9821 | -0.21973 | 0.79193 | 0.39368 | 11.554 | 22.5403 | 120.0256 | 122.7539 | 0.004578 | 122.7997 | 11.4761 | -0.21973 | 122.7539 | 0.004578 | 11.4761 | 120.0256 | 122.7997 | -122.3969 | -122.2275
2443.9688 | 122.3328 | -5.5298 | 116.5512 | 0.18723 | 2.5564e-05 | -0.0018862 | 0.0034735 | -0.0047574 | 0.00077554 | 0.01922 | -5.4657 | 117.1967 | -5.8823 | 117.453 | 114.4363 | 6.0104 | 5.8273 | 15.6876 | 117.1326 | -5.864 | -0.35248 | 0.64545 | 0.064087 | 122.9828 | -2.1149 | -0.33417 | 0.58136 | 0.41657 | 11.3571 | 21.2173 | 119.9661 | 122.7264 | 0.064087 | 122.6624 | 11.5402 | -0.33417 | 122.7264 | 0.064087 | 11.5402 | 119.9661 | 122.6624 | -122.4335 | -122.4152
2444.9219 | 98.7946 | -6.7703 | 89.4836 | -0.072174 | 0.002162 | 0.001318 | 0.011164 | -0.0051846 | -7.9062e-05 | 0.018365 | -6.2576 | 116.5741 | -6.6696 | 116.6702 | 113.6581 | 6.0242 | 5.8502 | 14.2044 | 116.4597 | -6.6193 | 0.10071 | 27.0905 | 0.5127 | 123.4406 | 24.1745 | 0.15106 | 26.976 | 0.41199 | 12.6205 | 20.9747 | 120.4285 | 123.3444 | 0.5127 | 123.23 | 12.7945 | 0.15106 | 123.3444 | 0.5127 | 12.7945 | 120.4285 | 123.23 | -96.1533 | -96.1029
2445.9531 | 122.58 | -5.983 | 116.3864 | 0.065155 | 0.0028028 | -0.0027408 | 0.0006965 | -0.0043302 | 0.00034814 | 0.016442 | -6.0562 | 116.684 | -6.4041 | 117.0547 | 114.0839 | 5.928 | 5.8044 | 15.7883 | 116.7801 | -6.2393 | -0.42114 | 0.29755 | -0.073242 | 123.0377 | -2.3026 | -0.25635 | 0.39368 | 0.3479 | 11.7874 | 21.7712 | 120.0668 | 122.6669 | -0.073242 | 122.7631 | 11.911 | -0.25635 | 122.6669 | -0.073242 | 11.911 | 120.0668 | 122.7631 | -122.7905 | -122.6257
2446.9062 | 122.5571 | -11.8698 | 110.4675 | 0.088043 | 0.00066656 | 0.003027 | 0.0021917 | -0.0058256 | 0.00077554 | 0.014947 | -11.8332 | 110.9756 | -12.1033 | 111.058 | 108.2703 | 5.4749 | 4.8614 | 14.3188 | 110.8383 | -12.1262 | -0.23346 | 0.50812 | 0.036621 | 122.9279 | -2.1973 | -0.25635 | 0.37079 | 0.27008 | 16.7313 | 26.1887 | 120.1401 | 122.8455 | 0.036621 | 122.7081 | 17.3447 | -0.25635 | 122.8455 | 0.036621 | 17.3447 | 120.1401 | 122.7081 | -122.5708 | -122.5937
2447.9688 | 122.9919 | -22.7692 | 99.8566 | 0.0041197 | 2.5564e-05 | 0.001959 | 0.0017645 | -0.0071072 | -0.0015745 | 0.012597 | -24.3118 | 98.8586 | -24.0967 | 99.5911 | 97.1512 | 4.8203 | 3.2913 | 12.2955 | 99.6689 | -23.2498 | -1.3275 | -0.99792 | -1.5427 | 122.3602 | -2.7054 | -0.48065 | -0.18768 | -0.21515 | 26.0605 | 35.0647 | 119.9203 | 121.6278 | -1.5427 | 122.438 | 27.5894 | -0.48065 | 121.6278 | -1.5427 | 27.5894 | 119.9203 | 122.438 | -123.9532 | -123.1064
2448.9062 | 121.8933 | -23.1491 | 99.6323 | -0.19424 | 0.0019482 | -0.001459 | 0.0004827 | -0.0077482 | -0.0011471 | 0.033746 | -30.3864 | 97.1924 | -26.4267 | 86.3022 | 89.5889 | 6.5689 | 7.4158 | 15.6464 | 101.0696 | -22.2519 | -3.2776 | -2.4399 | -7.2372 | 109.4513 | -10.0433 | 0.89722 | 1.4374 | -3.9597 | 30.5649 | 38.7955 | 112.738 | 120.3415 | -7.2372 | 124.2188 | 29.718 | 0.89722 | 120.3415 | -7.2372 | 29.718 | 112.738 | 124.2188 | -126.059 | -121.8842
2449.9688 | 122.4701 | -8.9127 | 113.1363 | 0.1033 | 0.00023916 | 0.00067718 | 5.5496e-05 | -0.0045438 | 0.00013454 | 0.017083 | -9.462 | 113.4567 | -9.613 | 114.1205 | 111.1862 | 5.7816 | 4.985 | 14.6851 | 113.7863 | -9.1873 | -0.70038 | 0.32043 | -0.54932 | 123.0331 | -1.9501 | -0.27466 | 0.65002 | 0.15106 | 13.8977 | 23.5977 | 120.0989 | 122.3694 | -0.54932 | 122.699 | 14.6942 | -0.27466 | 122.3694 | -0.54932 | 14.6942 | 120.0989 | 122.699 | -122.7493 | -122.3236
2450.9062 | 122.5342 | -9.1782 | 112.9349 | -0.018768 | -0.00040164 | -0.0020998 | -0.0018671 | -0.00668 | 0.00077554 | 0.014306 | -9.1507 | 113.6078 | -9.4711 | 113.8504 | 110.9711 | 5.6854 | 4.985 | 15.0833 | 113.5757 | -9.4254 | -0.29297 | 0.67291 | 0.027466 | 123.0286 | -1.9638 | -0.24719 | 0.64087 | 0.32043 | 14.1632 | 24.2615 | 120.1492 | 122.7859 | 0.027466 | 122.7539 | 14.8636 | -0.24719 | 122.7859 | 0.027466 | 14.8636 | 120.1492 | 122.7539 | -122.406 | -122.3602
2451.9688 | 122.438 | -8.6929 | 113.5071 | 0.15671 | -0.00061524 | -0.0018862 | 0.0041143 | -0.0068936 | 0.0018435 | 0.015802 | -8.6334 | 114.0839 | -8.963 | 114.3585 | 111.4105 | 5.8136 | 5.2185 | 14.8773 | 114.0335 | -8.9493 | -0.27008 | 0.57678 | 0.059509 | 123.0515 | -2.0966 | -0.25635 | 0.52643 | 0.32959 | 13.9114 | 23.5703 | 120.1035 | 122.7768 | 0.059509 | 122.7264 | 14.5065 | -0.25635 | 122.7768 | 0.059509 | 14.5065 | 120.1035 | 122.7264 | -122.4701 | -122.4564
2452.9219 | 98.2635 | -8.3679 | 88.623 | -0.24765 | 0.0053662 | 3.6382e-05 | 0.0068915 | -0.0060392 | 0.00034814 | 0.015802 | -15.9119 | 110.7742 | -13.3987 | 114.8254 | 111.8317 | 6.9168 | 6.2393 | 15.4999 | 114.3814 | -8.3908 | -5.0308 | 22.1512 | -7.5439 | 123.1934 | 23.2086 | -0.022888 | 25.7584 | -2.5131 | 14.6072 | 23.8678 | 120.1996 | 119.1422 | -7.5439 | 122.7493 | 15.2847 | -0.022888 | 119.1422 | -7.5439 | 15.2847 | 120.1996 | 122.7493 | -102.0218 | -97.0139
2453.9688 | 122.3328 | -6.7291 | 115.4846 | 0.16434 | 0.0010938 | 0.0034544 | 0.0021917 | -0.0051846 | -0.0017881 | 0.016656 | -6.4178 | 116.3315 | -6.8069 | 116.4505 | 113.4888 | 6.0516 | 5.2551 | 15.0742 | 115.9882 | -6.9809 | -0.07782 | 0.84686 | 0.31128 | 123.1796 | -1.9958 | -0.25177 | 0.50354 | 0.3891 | 11.9843 | 21.8033 | 120.2179 | 123.0606 | 0.31128 | 122.7173 | 12.7808 | -0.25177 | 123.0606 | 0.31128 | 12.7808 | 120.2179 | 122.7173 | -122.2916 | -122.4655
2454.9062 | 98.4512 | -4.2435 | 87.03 | -0.13321 | 0.00323 | 0.0017454 | 0.0071051 | -0.003903 | 0.00077554 | 0.017297 | -6.4178 | 116.4001 | -6.8253 | 116.4825 | 113.4842 | 5.9463 | 5.6488 | 15.5273 | 116.2445 | -6.8253 | -2.5818 | 29.3701 | -2.1744 | 120.726 | 26.4542 | -2.5818 | 29.2145 | 0.40741 | 9.8923 | 19.7708 | 117.7277 | 120.6436 | -2.1744 | 120.488 | 10.1898 | -2.5818 | 120.6436 | -2.1744 | 10.1898 | 117.7277 | 120.488 | -93.8553 | -93.8553
2455.9531 | 107.8629 | -6.7108 | 100.882 | 0.16434 | 0.0040846 | 0.0045224 | 0.0083869 | -0.0043302 | -0.0017881 | 0.016229 | -6.3492 | 116.4597 | -6.7657 | 116.6245 | 113.5117 | 5.6854 | 6.134 | 15.2664 | 116.4734 | -6.6284 | -0.054932 | 15.5777 | 0.36163 | 123.3353 | 12.6297 | 0.082397 | 15.5914 | 0.41657 | 12.8448 | 21.9772 | 120.2225 | 123.1705 | 0.36163 | 123.1842 | 12.3962 | 0.082397 | 123.1705 | 0.36163 | 12.3962 | 120.2225 | 123.1842 | -107.6477 | -107.5104
2456.9219 | 94.162 | 0.33875 | 85.318 | -0.22476 | 0.0040846 | 0.0051632 | 0.0086005 | -0.0013394 | -0.0017881 | 0.015802 | -8.107 | 114.7705 | -8.4595 | 114.8117 | 111.8591 | 5.7632 | 5.7404 | 15.5045 | 114.6194 | -8.4549 | -8.7982 | 29.4525 | -8.4457 | 114.473 | 26.5411 | -8.7936 | 29.3015 | 0.35248 | 5.4016 | 15.1657 | 111.5204 | 114.4318 | -8.4457 | 114.2807 | 5.4245 | -8.7936 | 114.4318 | -8.4457 | 5.4245 | 111.5204 | 114.2807 | -93.7775 | -93.7729
2457.9688 | 110.3348 | -9.375 | 93.8416 | -0.22476 | 0.0038708 | -0.0033816 | -0.0001581 | -0.0019802 | -7.9062e-05 | 0.014734 | -9.3658 | 113.5666 | -9.6634 | 113.5986 | 110.6873 | 5.7861 | 5.7083 | 15.358 | 113.5025 | -9.6405 | -0.28839 | 19.725 | 0.009155 | 122.9736 | 16.8457 | -0.2655 | 19.6609 | 0.29755 | 15.0833 | 24.733 | 120.0623 | 122.9416 | 0.009155 | 122.8775 | 15.1611 | -0.2655 | 122.9416 | 0.009155 | 15.1611 | 120.0623 | 122.8775 | -103.5049 | -103.4821
2458.9062 | 122.4655 | -14.5386 | 107.4875 | 0.027008 | -0.00018804 | 0.0028134 | -0.0022943 | -0.004971 | -0.0017881 | 0.017511 | -14.6667 | 108.197 | -14.8682 | 108.403 | 105.6519 | 5.4016 | 4.4037 | 14.1174 | 108.2062 | -14.8224 | -0.32959 | 0.70953 | -0.12817 | 122.9416 | -1.8356 | -0.28381 | 0.71869 | 0.20142 | 18.9423 | 28.656 | 120.1904 | 122.7356 | -0.12817 | 122.7448 | 19.9402 | -0.28381 | 122.7356 | -0.12817 | 19.9402 | 120.1904 | 122.7448 | -122.3557 | -122.3099
2459.9688 | 122.4701 | -8.2626 | 113.8779 | 0.18723 | 0.0028028 | -0.00017722 | 0.0019781 | -0.0041166 | -0.00093346 | 0.018579 | -8.3862 | 114.3768 | -8.6792 | 114.6835 | 111.8042 | 6.015 | 5.4291 | 15.0833 | 114.4867 | -8.5327 | -0.41657 | 0.49896 | -0.1236 | 122.9462 | -2.0737 | -0.27008 | 0.60882 | 0.29297 | 13.6917 | 23.3459 | 120.0668 | 122.6395 | -0.1236 | 122.7493 | 14.2776 | -0.27008 | 122.6395 | -0.1236 | 14.2776 | 120.0668 | 122.7493 | -122.5571 | -122.4106
2460.9219 | 122.7402 | -20.4071 | 102.0905 | 0.065155 | 0.0060072 | 0.0049496 | 0.0081733 | -0.0030484 | -7.9062e-05 | 0.014093 | -20.0317 | 103.4683 | -19.5831 | 103.6194 | 100.9644 | 4.7974 | 3.6209 | 12.0255 | 103.6743 | -19.8761 | 0.82397 | 1.3779 | 0.37537 | 124.0265 | -1.1261 | 0.53101 | 1.5839 | -0.44861 | 24.028 | 32.4326 | 121.3715 | 123.8754 | 0.37537 | 124.0814 | 25.2045 | 0.53101 | 123.8754 | 0.37537 | 25.2045 | 121.3715 | 124.0814 | -121.6736 | -121.9666
2461.9688 | 122.3785 | -10.0113 | 112.1658 | -0.0035098 | 0.00023916 | 0.0025998 | -0.0020807 | -0.00668 | 0.00056194 | 0.017083 | -10.0296 | 112.7655 | -10.35 | 112.8937 | 110.0739 | 5.658 | 5.04 | 14.1037 | 112.7106 | -10.2768 | -0.33875 | 0.59967 | -0.01831 | 122.905 | -2.092 | -0.2655 | 0.54474 | 0.32043 | 15.0513 | 24.115 | 120.0851 | 122.7768 | -0.01831 | 122.7219 | 15.6693 | -0.2655 | 122.7768 | -0.01831 | 15.6693 | 120.0851 | 122.7219 | -122.5159 | -122.4426
2462.9062 | 122.9416 | -9.3018 | 100.7858 | -0.2095 | 0.0010938 | 0.0028134 | 0.0024053 | -0.0047574 | 0.0014163 | 0.017938 | -9.343 | 113.4201 | -9.7641 | 113.4384 | 110.5957 | 5.4611 | 5.3238 | 14.4516 | 113.2782 | -9.8053 | -0.46234 | 12.6343 | -0.041199 | 122.7402 | 9.8099 | -0.50354 | 12.4924 | 0.42114 | 14.6256 | 23.7534 | 119.8975 | 122.7219 | -0.041199 | 122.58 | 14.7629 | -0.50354 | 122.7219 | -0.041199 | 14.7629 | 119.8975 | 122.58 | -110.5499 | -110.5911
2463.9531 | 123.0331 | -26.4359 | 96.2219 | 0.18723 | 0.0010938 | 0.0040952 | 0.0028327 | -0.0045438 | -0.0015745 | 0.011956 | -27.2598 | 95.1553 | -27.7725 | 95.842 | 93.4021 | 4.6967 | 2.5864 | 10.2219 | 95.7916 | -27.0905 | -1.3367 | -1.0666 | -0.82398 | 122.2778 | -2.8198 | -0.6546 | -0.4303 | 0.51269 | 29.0222 | 36.6577 | 119.838 | 121.5912 | -0.82398 | 122.2275 | 31.1325 | -0.6546 | 121.5912 | -0.82398 | 31.1325 | 119.838 | 122.2275 | -123.9944 | -123.3124
2464.9062 | 122.2824 | -8.963 | 110.8566 | 0.52292 | 0.0017346 | -0.0012454 | 0.0021917 | -0.0056118 | -0.0011471 | 0.017938 | -8.8531 | 113.7955 | -9.2377 | 113.9008 | 110.994 | 5.9372 | 5.7358 | 14.3875 | 113.6581 | -9.407 | -0.27466 | 2.9388 | 0.10986 | 122.8638 | 0.13733 | -0.44403 | 2.8015 | 0.38452 | 14.6988 | 23.3505 | 119.957 | 122.7585 | 0.10986 | 122.6212 | 14.9002 | -0.44403 | 122.7585 | 0.10986 | 14.9002 | 119.957 | 122.6212 | -120.0943 | -120.2637
2465.9688 | 122.2504 | -10.1669 | 111.3052 | 0.1796 | 0.0055798 | 0.0077268 | 0.0062507 | -0.0028348 | 0.0024845 | 0.017297 | -10.4462 | 112.4817 | -10.5972 | 112.738 | 109.7763 | 5.9235 | 5.0262 | 13.9572 | 112.4039 | -10.6018 | -0.4303 | 1.1765 | -0.27924 | 122.905 | -1.5289 | -0.43488 | 1.0986 | 0.15106 | 15.1932 | 24.1241 | 119.9432 | 122.6486 | -0.27924 | 122.5708 | 16.0904 | -0.43488 | 122.6486 | -0.27924 | 16.0904 | 119.9432 | 122.5708 | -121.9025 | -121.907
2466.9062 | 122.4655 | -8.0383 | 114.1434 | 0.011749 | -0.0010424 | -0.0010318 | 0.0019781 | -0.0056118 | -7.9062e-05 | 0.019433 | -7.8781 | 114.8941 | -8.1619 | 114.6561 | 111.9095 | 6.2073 | 5.9052 | 14.8041 | 114.7202 | -8.3405 | -0.1236 | 0.75073 | 0.16022 | 122.6944 | -2.2339 | -0.30212 | 0.57678 | 0.28381 | 13.9435 | 22.8424 | 119.9478 | 122.9324 | 0.16022 | 122.7585 | 14.2456 | -0.30212 | 122.9324 | 0.16022 | 14.2456 | 119.9478 | 122.7585 | -122.3053 | -122.4838
2467.9688 | 122.2137 | -7.4387 | 111.9873 | 0.20248 | 0.0025892 | 0.0021726 | 0.0047553 | -0.0043302 | -0.0011471 | 0.018792 | -7.4158 | 115.329 | -7.7499 | 115.5121 | 112.4496 | 6.0928 | 5.7953 | 15.2664 | 115.1779 | -7.8003 | -0.31128 | 3.3417 | 0.022889 | 122.9507 | 0.46234 | -0.36163 | 3.1906 | 0.33417 | 13.2339 | 22.7051 | 119.8883 | 122.7676 | 0.022889 | 122.6166 | 13.5315 | -0.36163 | 122.7676 | 0.022889 | 13.5315 | 119.8883 | 122.6166 | -119.7372 | -119.7876
2468.9062 | 122.4701 | -9.0042 | 113.5483 | 0.019379 | 0.00023916 | -0.00060462 | 0.0043281 | -0.0068936 | 0.0016299 | 0.017724 | -9.0042 | 113.8184 | -9.2148 | 114.1068 | 111.1404 | 6.0059 | 5.5756 | 14.4104 | 113.7588 | -9.2468 | -0.21057 | 0.27008 | 0 | 123.111 | -2.4078 | -0.24262 | 0.21057 | 0.21057 | 14.5798 | 23.4146 | 120.1447 | 122.8226 | 0 | 122.7631 | 15.0101 | -0.24262 | 122.8226 | 0 | 15.0101 | 120.1447 | 122.7631 | -122.7631 | -122.7951
2469.9531 | 122.9599 | -11.7325 | 110.733 | 0.095673 | -0.001256 | 0.00024998 | 0.0006965 | -0.0071072 | 0.00077554 | 0.017083 | -11.8378 | 111.0443 | -12.03 | 111.1816 | 108.403 | 5.6396 | 5.6168 | 13.8886 | 111.0077 | -12.0346 | -0.29755 | 0.31128 | -0.10529 | 122.9141 | -2.33 | -0.30212 | 0.27466 | 0.19226 | 17.3492 | 25.621 | 120.1355 | 122.7768 | -0.10529 | 122.7402 | 17.3721 | -0.30212 | 122.7768 | -0.10529 | 17.3721 | 120.1355 | 122.7402 | -122.7631 | -122.7676
2470.9062 | 109.2407 | -8.0521 | 106.6498 | -0.23239 | 0.002162 | 3.6382e-05 | 0.0041143 | -0.0075344 | -0.0011471 | 0.018792 | -8.0887 | 114.7156 | -8.4457 | 115.004 | 112.056 | 5.9967 | 6.3858 | 14.8682 | 114.8254 | -8.2764 | -0.39368 | 8.0658 | -0.036621 | 123.056 | 5.4062 | -0.2243 | 8.1757 | 0.35706 | 14.4379 | 22.9202 | 120.108 | 122.7676 | -0.036621 | 122.8775 | 14.0488 | -0.2243 | 122.7676 | -0.036621 | 14.0488 | 120.108 | 122.8775 | -115.0955 | -114.9261
2471.9688 | 122.8729 | -17.4637 | 104.8325 | 0.13382 | 0.0030164 | 0.001959 | 0.0028327 | -0.0051846 | -7.9062e-05 | 0.017724 | -16.0309 | 106.0593 | -17.2897 | 107.1213 | 104.1138 | 5.7083 | 3.1311 | 12.149 | 105.3268 | -17.5186 | 0.17395 | 1.2268 | 1.4328 | 124.585 | -0.71869 | -0.054932 | 0.49438 | 1.2588 | 20.5948 | 29.6127 | 121.5775 | 123.5229 | 1.4328 | 122.7905 | 23.172 | -0.054932 | 123.5229 | 1.4328 | 23.172 | 121.5775 | 122.7905 | -122.1222 | -122.3511
2472.9062 | 112.6785 | -9.8053 | 104.512 | -0.22476 | 0.0017346 | 0.0025998 | 0.0043281 | -0.0068936 | -0.0017881 | 0.01687 | -9.8877 | 112.9944 | -10.1486 | 113.0951 | 110.1334 | 6.0516 | 6.3126 | 14.3738 | 113.0264 | -10.0708 | -0.34332 | 8.4824 | -0.082397 | 122.9004 | 5.6213 | -0.2655 | 8.5144 | 0.26093 | 16.1179 | 24.1791 | 119.9387 | 122.7997 | -0.082397 | 122.8317 | 15.8569 | -0.2655 | 122.7997 | -0.082397 | 15.8569 | 119.9387 | 122.8317 | -114.6606 | -114.5828
2473.9531 | 122.4243 | -8.9081 | 113.1683 | 0.072784 | 0.001521 | -0.00017722 | 0.0006965 | -0.0045438 | 0.0014163 | 0.016229 | -8.9035 | 113.8641 | -9.2468 | 114.0747 | 111.1267 | 6.1707 | 6.1157 | 14.4928 | 113.8138 | -9.1736 | -0.33875 | 0.6958 | 0.004578 | 122.9828 | -2.0416 | -0.2655 | 0.64545 | 0.34332 | 15.0238 | 23.4009 | 120.0348 | 122.7722 | 0.004578 | 122.7219 | 15.0787 | -0.2655 | 122.7722 | 0.004578 | 15.0787 | 120.0348 | 122.7219 | -122.4152 | -122.3419
2474.9062 | 99.0875 | -7.4478 | 86.1557 | -0.18662 | 0.0025892 | -0.0023136 | 0.011805 | -0.004971 | 0.00056194 | 0.017297 | -9.4803 | 113.4796 | -9.7137 | 112.8067 | 109.9045 | 5.5573 | 5.7816 | 14.3509 | 112.8204 | -10.2997 | -2.2659 | 27.3239 | -2.0325 | 120.2545 | 23.7488 | -2.8519 | 26.6647 | 0.23346 | 13.2294 | 21.7987 | 117.3523 | 120.9274 | -2.0325 | 120.2683 | 13.0051 | -2.8519 | 120.9274 | -2.0325 | 13.0051 | 117.3523 | 120.2683 | -95.8694 | -96.4554
2475.9531 | 122.3648 | -9.9518 | 112.7335 | 0.14145 | -0.00061524 | 0.003027 | 0.0024053 | -0.0053982 | -0.0028561 | 0.017083 | -10.1074 | 112.6877 | -10.3912 | 112.944 | 110.0006 | 6.1981 | 5.6625 | 14.0762 | 112.8159 | -10.2264 | -0.43945 | -0.045776 | -0.15564 | 122.8958 | -2.7328 | -0.27466 | 0.082398 | 0.28381 | 15.6143 | 24.028 | 119.9524 | 122.6395 | -0.15564 | 122.7676 | 16.1499 | -0.27466 | 122.6395 | -0.15564 | 16.1499 | 119.9524 | 122.7676 | -123.1247 | -122.9599
2476.9062 | 122.5296 | -10.2722 | 111.731 | 0.027008 | 0.00088016 | 0.00067718 | 0.0019781 | -0.0077482 | 0.00056194 | 0.017297 | -10.524 | 112.3352 | -10.73 | 112.5824 | 109.9045 | 6.1752 | 5.5023 | 13.7924 | 112.4588 | -10.556 | -0.45776 | 0.60425 | -0.25177 | 122.8546 | -1.8265 | -0.28381 | 0.72784 | 0.20599 | 15.7745 | 24.0646 | 120.1767 | 122.6074 | -0.25177 | 122.731 | 16.4474 | -0.28381 | 122.6074 | -0.25177 | 16.4474 | 120.1767 | 122.731 | -122.4609 | -122.287
2477.9531 | 122.5067 | -9.4849 | 112.6144 | 0.12619 | 0.0025892 | -0.00081822 | 0.0011237 | -0.0064664 | -0.0011471 | 0.017083 | -9.5261 | 113.3057 | -9.7733 | 113.5117 | 110.5957 | 6.0745 | 5.6396 | 13.8428 | 113.269 | -9.7366 | -0.28839 | 0.69122 | -0.041199 | 122.9965 | -2.0187 | -0.25177 | 0.6546 | 0.24719 | 15.1245 | 23.3276 | 120.0806 | 122.7905 | -0.041199 | 122.7539 | 15.5594 | -0.25177 | 122.7905 | -0.041199 | 15.5594 | 120.0806 | 122.7539 | -122.3877 | -122.3511
2478.9062 | 122.4289 | -9.1141 | 113.4659 | -0.049286 | 0.00045296 | -0.00039102 | -0.0007989 | -0.0073208 | -0.00050626 | 0.016442 | -9.2606 | 113.5254 | -9.5078 | 113.887 | 110.9848 | 6.0471 | 5.7175 | 13.9389 | 113.5986 | -9.3658 | -0.39368 | 0.05951 | -0.14648 | 123.0011 | -2.4811 | -0.25177 | 0.13275 | 0.24719 | 14.8315 | 23.053 | 120.0989 | 122.6395 | -0.14648 | 122.7127 | 15.1611 | -0.25177 | 122.6395 | -0.14648 | 15.1611 | 120.0989 | 122.7127 | -122.9736 | -122.8317
2479.9688 | 122.3602 | -11.2381 | 110.9024 | 0.21774 | 0.002162 | -0.00039102 | 0.0036871 | -0.0045438 | -0.00029266 | 0.015161 | -10.9268 | 111.7767 | -11.293 | 111.9278 | 108.9844 | 5.6534 | 5.365 | 13.4399 | 111.4883 | -11.4944 | -0.054932 | 0.87433 | 0.31128 | 123.1659 | -1.918 | -0.25635 | 0.58594 | 0.36621 | 16.6031 | 24.678 | 120.2225 | 123.0148 | 0.31128 | 122.7264 | 16.8915 | -0.25635 | 123.0148 | 0.31128 | 16.8915 | 120.2225 | 122.7264 | -122.1954 | -122.3969
2480.9062 | 122.5067 | -8.7341 | 113.2095 | 0.17197 | -0.0014696 | 0.003668 | 0.0013373 | -0.0079618 | 0.0024845 | 0.015588 | -10.2814 | 112.7014 | -10.2722 | 114.2166 | 111.2732 | 6.0059 | 5.9006 | 11.0001 | 113.9877 | -8.9539 | -1.5381 | -0.50812 | -1.5472 | 122.9507 | -1.9363 | -0.21973 | 0.7782 | -0.009155 | 14.6347 | 19.7342 | 120.0073 | 121.4355 | -1.5472 | 122.7219 | 14.74 | -0.21973 | 121.4355 | -1.5472 | 14.74 | 120.0073 | 122.7219 | -123.4818 | -122.1634
2481.9688 | 122.3923 | -7.7591 | 114.1846 | 0.20248 | 0.0017346 | 0.00024998 | 0.0030463 | -0.0058256 | 0.00077554 | 0.018151 | -7.6813 | 115.0269 | -8.0978 | 115.1733 | 112.1521 | 6.2119 | 6.0745 | 13.2339 | 114.917 | -8.0795 | -0.33875 | 0.84229 | 0.07782 | 122.9324 | -2.0325 | -0.32044 | 0.73242 | 0.41657 | 13.8336 | 20.993 | 119.9112 | 122.7859 | 0.07782 | 122.6761 | 13.9709 | -0.32044 | 122.7859 | 0.07782 | 13.9709 | 119.9112 | 122.6761 | -122.2824 | -122.2641
2482.9062 | 118.7347 | -7.7316 | 99.1241 | -0.32394 | 0.0025892 | 0.0060178 | 0.0047553 | -0.0053982 | -7.9062e-05 | 0.016015 | -7.7179 | 115.1642 | -8.0246 | 115.2145 | 112.3077 | 6.189 | 6.2531 | 13.0875 | 115.0909 | -8.0017 | -0.29297 | 16.04 | 0.013732 | 122.9462 | 13.1836 | -0.27008 | 15.9668 | 0.3067 | 13.9847 | 20.8191 | 120.0394 | 122.8958 | 0.013732 | 122.8226 | 13.9206 | -0.27008 | 122.8958 | 0.013732 | 13.9206 | 120.0394 | 122.8226 | -107.1487 | -107.1259
2483.9688 | 98.1262 | -2.0508 | 102.626 | -0.095062 | 0.0030164 | 0.0055906 | 0.0077459 | -0.0045438 | -0.0047787 | 0.016229 | -7.4936 | 115.3061 | -7.8827 | 115.448 | 112.4496 | 6.2439 | 6.2302 | 13.9343 | 115.3061 | -7.8186 | -5.8319 | 12.6801 | -5.4428 | 117.4988 | 9.8236 | -5.7678 | 12.6801 | 0.3891 | 8.2809 | 15.9851 | 114.5004 | 117.3569 | -5.4428 | 117.3569 | 8.2947 | -5.7678 | 117.3569 | -5.4428 | 8.2947 | 114.5004 | 117.3569 | -110.5087 | -110.4446
2484.9062 | 122.5204 | -7.6447 | 114.624 | 0.072784 | 0.001521 | 0.00046358 | -0.0020807 | -0.0036892 | -0.00029266 | 0.017938 | -7.5439 | 115.2328 | -7.8506 | 115.416 | 112.4359 | 6.3126 | 5.8823 | 13.5681 | 115.1459 | -7.901 | -0.20599 | 0.60883 | 0.10071 | 123.0606 | -2.1881 | -0.25635 | 0.52185 | 0.3067 | 13.5269 | 21.2128 | 120.0806 | 122.8775 | 0.10071 | 122.7905 | 13.9572 | -0.25635 | 122.8775 | 0.10071 | 13.9572 | 120.0806 | 122.7905 | -122.4747 | -122.525
2485.9688 | 96.4874 | -1.5244 | 84.8602 | -0.095062 | 0.0045118 | 0.0060178 | 0.0066779 | -0.0045438 | -0.00093346 | 0.017297 | -8.4503 | 114.3585 | -8.8028 | 114.5096 | 111.5067 | 6.134 | 5.7724 | 13.5635 | 114.2761 | -8.8165 | -7.2784 | 29.4983 | -6.926 | 116.0339 | 26.6464 | -7.2922 | 29.4159 | 0.35248 | 7.2968 | 15.0879 | 113.031 | 115.8829 | -6.926 | 115.8005 | 7.6584 | -7.2922 | 115.8829 | -6.926 | 7.6584 | 113.031 | 115.8005 | -93.663 | -93.6768
2486.9062 | 122.4106 | -9.0225 | 113.0264 | 0.072784 | 0.00088016 | 0.0017454 | 0.0006965 | -0.0043302 | -0.00093346 | 0.019006 | -8.8898 | 113.649 | -9.2972 | 114.4638 | 111.1633 | 6.2531 | 5.7404 | 13.1882 | 113.8412 | -9.1644 | -0.27466 | 0.62256 | 0.13275 | 123.4863 | -1.8631 | -0.14191 | 0.81482 | 0.40741 | 14.7629 | 22.2107 | 120.1859 | 122.6715 | 0.13275 | 122.8638 | 15.2756 | -0.14191 | 122.6715 | 0.13275 | 15.2756 | 120.1859 | 122.8638 | -122.3236 | -122.1909
2487.9062 | 122.7219 | -12.7121 | 103.688 | -0.034027 | 0.0017346 | -0.003168 | 0.0041143 | -0.0071072 | 0.0014163 | 0.017297 | -13.1516 | 109.0347 | -13.8474 | 109.9274 | 107.3914 | 5.9738 | 5.4886 | 12.9547 | 109.9274 | -13.2156 | -1.1353 | 5.3467 | -0.43945 | 122.6395 | 3.7033 | -0.50354 | 6.2393 | 0.6958 | 18.2007 | 25.6668 | 120.1035 | 121.7468 | -0.43945 | 122.6395 | 18.6859 | -0.50354 | 121.7468 | -0.43945 | 18.6859 | 120.1035 | 122.6395 | -117.5354 | -116.9037
2488.9688 | 122.6715 | -11.5585 | 111.2457 | 0.19485 | 0.00023916 | 0.0032406 | 0.0058233 | -0.0047574 | -0.0024289 | 0.017297 | -11.5311 | 111.1862 | -11.7096 | 111.6669 | 108.5358 | 5.8319 | 5.6717 | 12.8128 | 111.1588 | -11.8011 | -0.15106 | -0.05951 | 0.027466 | 123.2254 | -2.71 | -0.24261 | -0.086976 | 0.17853 | 17.2302 | 24.3713 | 120.0943 | 122.7448 | 0.027466 | 122.7173 | 17.3904 | -0.24261 | 122.7448 | 0.027466 | 17.3904 | 120.0943 | 122.7173 | -122.9553 | -123.0469
2489.9062 | 122.4609 | -4.4083 | 117.9977 | 0.1796 | 0.002162 | -0.0029544 | 0.0028327 | -0.0056118 | -0.00071986 | 0.017297 | -4.3121 | 118.4097 | -4.7104 | 118.6066 | 115.6036 | 6.4957 | 7.5485 | 13.7924 | 118.3823 | -4.66 | -0.30212 | 0.41199 | 0.09613 | 123.0148 | -2.3941 | -0.25177 | 0.38452 | 0.39825 | 11.9568 | 18.2007 | 120.0119 | 122.818 | 0.09613 | 122.7905 | 10.9039 | -0.25177 | 122.818 | 0.09613 | 10.9039 | 120.0119 | 122.7905 | -122.7081 | -122.6578
2490.9531 | 109.6436 | -5.69 | 95.4666 | 0.68314 | 0.0025892 | 0.0028134 | 0.010523 | -0.004971 | -0.0017881 | 0.018792 | -5.4199 | 117.2241 | -6.0242 | 117.5629 | 114.5142 | 6.7383 | 7.5668 | 13.8474 | 117.3798 | -5.7587 | -0.33417 | 21.7575 | 0.27008 | 123.2529 | 19.0475 | -0.068665 | 21.9131 | 0.60425 | 13.2568 | 19.5374 | 120.2042 | 122.9141 | 0.27008 | 123.0698 | 12.4283 | -0.068665 | 122.9141 | 0.27008 | 12.4283 | 120.2042 | 123.0698 | -101.4908 | -101.2253
2491.9062 | 122.6761 | -5.191 | 116.4047 | 0.28641 | 0.0038708 | 0.0043088 | 0.0062507 | -0.0043302 | 0.0018435 | 0.018365 | -5.3741 | 117.4347 | -5.7449 | 117.6544 | 114.624 | 6.8161 | 6.8985 | 13.4811 | 117.334 | -5.6717 | -0.55389 | 1.03 | -0.18311 | 122.8455 | -1.7807 | -0.48065 | 0.92926 | 0.37079 | 12.0895 | 18.6722 | 119.8151 | 122.6257 | -0.18311 | 122.525 | 12.0071 | -0.48065 | 122.6257 | -0.18311 | 12.0071 | 119.8151 | 122.525 | -122.1497 | -122.0764
2492.9219 | 122.4152 | -5.5344 | 117.2791 | -0.064545 | 0.0028028 | 0.0011044 | -0.0012261 | -0.0056118 | 0.00056194 | 0.017938 | -5.8594 | 116.8625 | -6.2851 | 117.5034 | 114.505 | 6.9122 | 6.5048 | 12.6801 | 117.1875 | -5.809 | -0.75073 | -0.41657 | -0.32501 | 123.0377 | -2.774 | -0.27466 | -0.091553 | 0.42572 | 12.0392 | 18.2144 | 120.0394 | 122.3969 | -0.32501 | 122.7219 | 12.4466 | -0.27466 | 122.3969 | -0.32501 | 12.4466 | 120.0394 | 122.7219 | -123.5641 | -123.0881
2493.9688 | 106.3751 | -7.2327 | 91.5298 | 0.095673 | 0.0023756 | 0.0025998 | 0.010737 | -0.0041166 | -0.00093346 | 0.017938 | -6.4957 | 116.3864 | -6.7886 | 116.4322 | 113.2874 | 6.5964 | 6.5369 | 12.8128 | 116.1621 | -6.9168 | 0.44403 | 24.8566 | 0.737 | 123.6649 | 21.7575 | 0.31586 | 24.6323 | 0.29297 | 13.7695 | 20.0455 | 120.52 | 123.6191 | 0.737 | 123.3948 | 13.829 | 0.31586 | 123.6191 | 0.737 | 13.829 | 120.52 | 123.3948 | -98.3185 | -98.4467
2494.9062 | 122.4426 | -5.5893 | 117.2607 | 0.18723 | 0.00088016 | 0.0034544 | 5.5496e-05 | -0.0041166 | -7.9062e-05 | 0.017938 | -5.5389 | 117.2195 | -5.9235 | 117.421 | 114.3906 | 6.9809 | 6.8481 | 13.385 | 117.1921 | -5.8548 | -0.33417 | -0.041199 | 0.050354 | 123.0103 | -2.8702 | -0.2655 | -0.068664 | 0.38452 | 12.4374 | 18.9743 | 119.9799 | 122.8088 | 0.050354 | 122.7814 | 12.5702 | -0.2655 | 122.8088 | 0.050354 | 12.5702 | 119.9799 | 122.7814 | -123.1842 | -123.1155
2495.9688 | 111.9873 | -6.0471 | 95.2011 | -0.1561 | 0.0053662 | -0.0016726 | 0.0081733 | -0.0060392 | 0.00077554 | 0.017083 | -5.7816 | 117.128 | -6.134 | 117.1783 | 114.1342 | 6.7978 | 7.0358 | 13.1149 | 116.9724 | -6.1523 | -0.086975 | 21.9269 | 0.2655 | 123.2254 | 18.9331 | -0.10529 | 21.7712 | 0.35248 | 13.0829 | 19.162 | 120.1813 | 123.175 | 0.2655 | 123.0194 | 12.8448 | -0.10529 | 123.175 | 0.2655 | 12.8448 | 120.1813 | 123.0194 | -101.3351 | -101.3535
2496.9062 | 122.2641 | -5.0583 | 117.7597 | 0.11856 | 0.00323 | 0.0045224 | 0.0053961 | -0.0028348 | -0.0017881 | 0.017938 | -5.0125 | 117.6773 | -5.452 | 117.9108 | 114.8575 | 6.9077 | 6.8802 | 12.7945 | 117.6041 | -5.4245 | -0.39368 | -0.082398 | 0.045777 | 122.9691 | -2.9022 | -0.36621 | -0.15564 | 0.43945 | 11.9385 | 17.8528 | 119.9158 | 122.7356 | 0.045777 | 122.6624 | 11.9659 | -0.36621 | 122.7356 | 0.045777 | 11.9659 | 119.9158 | 122.6624 | -123.2117 | -123.1842
2497.9219 | 122.5433 | -5.1727 | 116.9586 | 0.18723 | 0.001521 | 0.00024998 | 0.0021917 | -0.0053982 | -0.00050626 | 0.019006 | -5.0949 | 117.6727 | -5.452 | 117.7826 | 114.8666 | 6.9855 | 7.0862 | 13.2889 | 117.6086 | -5.452 | -0.27924 | 0.71411 | 0.077819 | 122.9553 | -2.092 | -0.27924 | 0.65002 | 0.35706 | 12.2589 | 18.4616 | 120.0394 | 122.8455 | 0.077819 | 122.7814 | 12.1582 | -0.27924 | 122.8455 | 0.077819 | 12.1582 | 120.0394 | 122.7814 | -122.4106 | -122.4106
2498.9688 | 107.6981 | -5.5527 | 94.7845 | 0.1796 | 0.0040846 | 0.0038816 | 0.0092413 | -0.0068936 | 0.0029117 | 0.018151 | -5.1636 | 117.7139 | -5.5206 | 117.8467 | 114.9628 | 7.0175 | 6.752 | 12.9456 | 117.6132 | -5.5023 | 0.032043 | 22.9294 | 0.3891 | 123.3994 | 20.1782 | 0.050354 | 22.8287 | 0.35706 | 12.3047 | 18.4982 | 120.5154 | 123.2666 | 0.3891 | 123.1659 | 12.5702 | 0.050354 | 123.2666 | 0.3891 | 12.5702 | 120.5154 | 123.1659 | -100.3052 | -100.2869
2499.9062 | 122.4792 | -5.0583 | 117.247 | 0.14145 | 0.0023756 | 0.0060178 | 0.0009101 | -0.0028348 | -0.00050626 | 0.01986 | -4.9393 | 117.7689 | -5.3375 | 117.9428 | 114.9216 | 6.7978 | 6.871 | 13.2523 | 117.6956 | -5.3375 | -0.27923 | 0.52185 | 0.11902 | 123.0011 | -2.3254 | -0.27923 | 0.44861 | 0.39825 | 11.9293 | 18.3105 | 119.9799 | 122.8271 | 0.11902 | 122.7539 | 11.8561 | -0.27923 | 122.8271 | 0.11902 | 11.8561 | 119.9799 | 122.7539 | -122.5845 | -122.5845
2500.9531 | 122.905 | -21.6751 | 100.5524 | -0.14084 | 0.0036572 | 0.0051632 | 0.0090277 | -0.0024076 | -0.00071986 | 0.014734 | -21.8536 | 100.1953 | -22.7554 | 101.0788 | 98.3551 | 5.1086 | 3.6804 | 10.3409 | 100.9598 | -22.0917 | -1.0803 | -0.35706 | -0.17853 | 122.7539 | -2.1973 | -0.41656 | 0.40741 | 0.90179 | 25.3555 | 32.016 | 120.0302 | 121.8704 | -0.17853 | 122.6349 | 26.7838 | -0.41656 | 121.8704 | -0.17853 | 26.7838 | 120.0302 | 122.6349 | -123.3078 | -122.644
2501.9062 | 122.5479 | -6.958 | 114.8804 | 0.22537 | 0.0025892 | 0.0040952 | 0.0036871 | -0.0019802 | -0.00029266 | 0.018579 | -7.1228 | 115.6448 | -7.5302 | 115.9149 | 112.9715 | 6.72 | 6.4453 | 13.1012 | 115.6906 | -7.3792 | -0.5722 | 0.76447 | -0.16479 | 122.8729 | -1.9089 | -0.42114 | 0.81024 | 0.40741 | 13.4033 | 20.0592 | 119.9295 | 122.6028 | -0.16479 | 122.6486 | 13.678 | -0.42114 | 122.6028 | -0.16479 | 13.678 | 119.9295 | 122.6486 | -122.4106 | -122.2595
2502.9688 | 122.5296 | -6.926 | 115.1596 | 0.14145 | 0.0038708 | 0.0023862 | -0.0018671 | -0.004971 | 0.0012027 | 0.017938 | -6.8573 | 115.9195 | -7.2052 | 116.0614 | 113.1271 | 6.6696 | 6.6422 | 13.4995 | 115.8554 | -7.1823 | -0.27924 | 0.75989 | 0.068664 | 122.9874 | -2.0325 | -0.25635 | 0.6958 | 0.3479 | 13.5681 | 20.4254 | 120.0531 | 122.8455 | 0.068664 | 122.7814 | 13.5956 | -0.25635 | 122.8455 | 0.068664 | 13.5956 | 120.0531 | 122.7814 | -122.3648 | -122.3419
2503.9062 | 114.5325 | -6.6513 | 104.6173 | -1.331 | 0.001521 | 0.0038816 | 0.0081733 | -0.0024076 | 0.0012027 | 0.018792 | -6.601 | 116.3956 | -6.8665 | 116.4001 | 113.3743 | 6.633 | 6.5414 | 13.2111 | 116.2537 | -6.8893 | -0.21515 | 11.7783 | 0.050354 | 123.0515 | 8.757 | -0.23804 | 11.6364 | 0.2655 | 13.1927 | 19.8624 | 120.0256 | 123.0469 | 0.050354 | 122.905 | 13.2843 | -0.23804 | 123.0469 | 0.050354 | 13.2843 | 120.0256 | 122.905 | -111.4838 | -111.5067
2504.9531 | 109.9365 | -6.7108 | 103.3447 | -0.29343 | 0.002162 | 0.0015316 | 0.0058233 | -0.003262 | -0.0013609 | 0.017297 | -6.752 | 116.1621 | -7.0999 | 116.2399 | 113.2553 | 6.8893 | 6.6238 | 13.0325 | 116.1713 | -6.9534 | -0.3891 | 12.8174 | -0.041199 | 122.9507 | 9.9106 | -0.24261 | 12.8265 | 0.3479 | 13.3347 | 19.7433 | 119.9661 | 122.8729 | -0.041199 | 122.8821 | 13.6002 | -0.24261 | 122.8729 | -0.041199 | 13.6002 | 119.9661 | 122.8821 | -110.4446 | -110.2982
2505.9062 | 122.2641 | -6.871 | 115.1184 | 0.22537 | 0.00323 | 0.003668 | 0.0064643 | -0.0028348 | 0.00013454 | 0.018579 | -6.8069 | 116.0339 | -7.1548 | 115.979 | 113.0219 | 6.7017 | 6.2622 | 12.8174 | 115.8279 | -7.2601 | -0.28381 | 0.91553 | 0.064087 | 122.85 | -2.0966 | -0.3891 | 0.70953 | 0.3479 | 13.1332 | 19.6884 | 119.8929 | 122.905 | 0.064087 | 122.699 | 13.5727 | -0.3891 | 122.905 | 0.064087 | 13.5727 | 119.8929 | 122.699 | -122.2733 | -122.3785
2506.9688 | 95.5353 | -4.628 | 87.117 | -0.026398 | 0.0064344 | 0.0062314 | 0.0066779 | -0.0013394 | -0.0022153 | 0.017083 | -6.5918 | 116.2491 | -6.9992 | 116.3269 | 113.3698 | 6.6879 | 6.5048 | 12.7258 | 116.1713 | -6.9305 | -2.3712 | 29.1321 | -1.9638 | 120.9549 | 26.2527 | -2.3026 | 29.0543 | 0.40741 | 11.1328 | 17.3538 | 117.9977 | 120.8771 | -1.9638 | 120.7993 | 11.3159 | -2.3026 | 120.8771 | -1.9638 | 11.3159 | 117.9977 | 120.7993 | -94.1162 | -94.0475
2507.9062 | 123.1201 | -6.4362 | 115.7455 | 0.18723 | 0.0038708 | 0.0049496 | 0.0056097 | -0.0030484 | 0.00034814 | 0.017724 | -6.5002 | 116.4001 | -6.8619 | 116.4001 | 113.443 | 6.8207 | 6.102 | 12.6801 | 116.2674 | -6.839 | -0.42572 | 0.6546 | -0.064087 | 122.8363 | -2.3026 | -0.40283 | 0.52185 | 0.36163 | 12.5381 | 19.1162 | 119.8791 | 122.8363 | -0.064087 | 122.7036 | 13.2568 | -0.40283 | 122.8363 | -0.064087 | 13.2568 | 119.8791 | 122.7036 | -122.6074 | -122.5845
2508.9688 | 96.9406 | -1.3596 | 87.0712 | -0.0035098 | 0.0060072 | 0.0060178 | 0.0086005 | -0.0011258 | -0.00093346 | 0.019006 | -6.459 | 116.3956 | -6.8527 | 116.4413 | 113.443 | 6.9809 | 6.2393 | 12.4512 | 116.3361 | -6.8298 | -5.4932 | 29.3243 | -5.0995 | 117.8009 | 26.3718 | -5.4703 | 29.2648 | 0.39368 | 7.5989 | 13.8107 | 114.8026 | 117.7551 | -5.0995 | 117.6956 | 8.3405 | -5.4703 | 117.7551 | -5.0995 | 8.3405 | 114.8026 | 117.6956 | -93.924 | -93.9011
2509.9062 | 122.4014 | -6.2393 | 115.9058 | 0.17197 | 0.0028028 | 0.0023862 | 0.0013373 | -0.00048499 | -0.0020017 | 0.018365 | -6.2027 | 116.5649 | -6.5735 | 116.6885 | 113.7131 | 7.1182 | 6.1523 | 11.7371 | 116.5192 | -6.5506 | -0.33417 | 0.65918 | 0.036621 | 122.9279 | -2.1927 | -0.31128 | 0.6134 | 0.37079 | 12.3917 | 17.9764 | 119.9524 | 122.8043 | 0.036621 | 122.7585 | 13.3575 | -0.31128 | 122.8043 | 0.036621 | 13.3575 | 119.9524 | 122.7585 | -122.4792 | -122.4564
2510.9531 | 98.1674 | -0.3479 | 88.6642 | -0.16373 | 0.0055798 | 0.0028134 | 0.0088141 | -0.0036892 | -0.0017881 | 0.017297 | -4.7424 | 118.1213 | -5.1682 | 118.103 | 115.0452 | 7.1503 | 6.6101 | 12.0117 | 117.9749 | -5.1636 | -4.8203 | 29.4571 | -4.3945 | 118.4509 | 26.3809 | -4.8157 | 29.3106 | 0.42572 | 6.958 | 12.3596 | 115.3931 | 118.4692 | -4.3945 | 118.3228 | 7.4982 | -4.8157 | 118.4692 | -4.3945 | 7.4982 | 115.3931 | 118.3228 | -93.8324 | -93.8278
2511.9062 | 123.0515 | -3.9871 | 118.0298 | 0.25589 | 0.0034436 | 0.0025998 | 0.0041143 | 0.00058321 | -0.00029266 | 0.017724 | -4.0604 | 118.7943 | -4.4907 | 118.7759 | 115.7822 | 7.1365 | 6.5735 | 12.3413 | 118.6707 | -4.4815 | -0.50354 | 0.76447 | -0.073242 | 122.7631 | -2.2476 | -0.49438 | 0.64087 | 0.4303 | 10.5606 | 16.3284 | 119.7693 | 122.7814 | -0.073242 | 122.6578 | 11.1237 | -0.49438 | 122.7814 | -0.073242 | 11.1237 | 119.7693 | 122.6578 | -122.5204 | -122.5113
2512.9688 | 122.3373 | -7.9102 | 114.2441 | 0.13382 | 0.00066656 | 0.004736 | -0.0003717 | 0.00036961 | 0.00034814 | 0.01922 | -7.9193 | 114.8117 | -8.2901 | 115.0772 | 112.1429 | 6.7978 | 5.5984 | 11.4075 | 114.8392 | -8.1757 | -0.37994 | 0.56763 | -0.009156 | 122.9874 | -2.1011 | -0.2655 | 0.59509 | 0.37079 | 13.5086 | 19.3176 | 120.0531 | 122.7219 | -0.009156 | 122.7493 | 14.7079 | -0.2655 | 122.7219 | -0.009156 | 14.7079 | 120.0531 | 122.7493 | -122.5342 | -122.4197
2513.9062 | 122.2733 | -7.4799 | 112.1887 | 0.30167 | 0.0047254 | 0.0015316 | 0.0045417 | -0.0026212 | -0.0022153 | 0.017724 | -7.7316 | 115.1413 | -8.0338 | 115.5029 | 112.5504 | 6.6101 | 5.5252 | 11.9522 | 115.1642 | -7.869 | -0.55389 | 2.9526 | -0.25177 | 122.9828 | 0.36163 | -0.3891 | 2.9755 | 0.30212 | 13.0051 | 19.4321 | 120.0302 | 122.6212 | -0.25177 | 122.644 | 14.09 | -0.3891 | 122.6212 | -0.25177 | 14.09 | 120.0302 | 122.644 | -120.2225 | -120.0577
2514.9688 | 122.2275 | -7.0587 | 113.4384 | 0.21774 | 0.0013074 | 0.001959 | 0.0043281 | -0.0034756 | -0.0020017 | 0.018579 | -7.0999 | 115.6631 | -7.4799 | 115.7639 | 112.8021 | 6.9809 | 5.7999 | 11.8149 | 115.5579 | -7.5027 | -0.42114 | 2.2247 | -0.041199 | 122.8226 | -0.63629 | -0.44403 | 2.1194 | 0.37994 | 12.8586 | 18.8736 | 119.8608 | 122.7219 | -0.041199 | 122.6166 | 14.0396 | -0.44403 | 122.7219 | -0.041199 | 14.0396 | 119.8608 | 122.6166 | -120.9183 | -120.9412
2515.9062 | 114.6194 | -7.2693 | 103.624 | 0.33218 | 0.0045118 | 0.0079404 | 0.0077459 | -0.0026212 | 0.0014163 | 0.01687 | -7.1915 | 115.7593 | -7.5302 | 115.7318 | 112.7518 | 6.6101 | 6.2942 | 12.3047 | 115.6265 | -7.4936 | -0.26092 | 12.1353 | 0.07782 | 123.0011 | 9.1278 | -0.2243 | 12.0026 | 0.33874 | 13.5635 | 19.574 | 120.0211 | 123.0286 | 0.07782 | 122.8958 | 13.8794 | -0.2243 | 123.0286 | 0.07782 | 13.8794 | 120.0211 | 122.8958 | -111.1542 | -111.1176
2516.9688 | 122.6257 | -7.3792 | 114.6011 | 0.1033 | -0.00018804 | 0.004736 | -0.0010125 | -0.0056118 | -0.00071986 | 0.019006 | -7.2922 | 115.5258 | -7.5897 | 115.6586 | 112.7197 | 6.8939 | 6.2622 | 12.1765 | 115.5029 | -7.5897 | -0.21057 | 0.92468 | 0.086975 | 123.0377 | -1.8814 | -0.21057 | 0.9018 | 0.29755 | 13.6414 | 19.5557 | 120.0989 | 122.905 | 0.086975 | 122.8821 | 14.2731 | -0.21057 | 122.905 | 0.086975 | 14.2731 | 120.0989 | 122.8821 | -122.1909 | -122.1909
2517.9062 | 122.2549 | -7.0496 | 115.6311 | 0.14145 | 0.0045118 | 0.0038816 | 0.0049689 | -0.004971 | -0.0013609 | 0.016442 | -7.1365 | 115.6998 | -7.4936 | 115.7959 | 112.8296 | 6.8893 | 6.0562 | 12.0209 | 115.5853 | -7.4844 | -0.44403 | 0.068664 | -0.086975 | 122.8455 | -2.8015 | -0.43487 | -0.045777 | 0.35705 | 13.1058 | 19.0704 | 119.8792 | 122.7493 | -0.086975 | 122.6349 | 13.9389 | -0.43487 | 122.7493 | -0.086975 | 13.9389 | 119.8792 | 122.6349 | -123.1247 | -123.1155
2518.9688 | 122.287 | -7.1091 | 115.686 | 1.5224 | -0.00018804 | 0.0043088 | 0.0015509 | -0.0034756 | 0.00077554 | 0.016656 | -7.1091 | 115.6311 | -7.5439 | 115.8142 | 112.8616 | 6.9168 | 6.2897 | 12.41 | 115.567 | -7.489 | -0.43487 | -0.054931 | 0 | 122.9233 | -2.8244 | -0.37994 | -0.11902 | 0.43487 | 13.3987 | 19.519 | 119.9707 | 122.7402 | 0 | 122.6761 | 14.0259 | -0.37994 | 122.7402 | 0 | 14.0259 | 119.9707 | 122.6761 | -123.23 | -123.175
2519.9062 | 123.3582 | -8.0017 | 114.0198 | 0.24063 | 0.0034436 | 0.0011044 | 0.0083869 | -0.0047574 | 0.0016299 | 0.014306 | -8.1757 | 114.7202 | -8.5098 | 114.7934 | 111.8225 | 6.9809 | 5.9235 | 11.5494 | 114.6286 | -8.4595 | -0.50812 | 0.70038 | -0.17395 | 122.7951 | -2.1973 | -0.45776 | 0.60883 | 0.33417 | 13.9252 | 19.5511 | 119.8242 | 122.7219 | -0.17395 | 122.6303 | 14.9826 | -0.45776 | 122.7219 | -0.17395 | 14.9826 | 119.8242 | 122.6303 | -122.5296 | -122.4792
2520.9688 | 101.4725 | -7.9605 | 94.0704 | -0.24002 | 0.0034436 | 0.0021726 | 0.0056097 | -0.0045438 | 0.00013454 | 0.016442 | -7.4341 | 115.5075 | -7.7728 | 115.4892 | 112.5092 | 7.1045 | 6.0379 | 11.7142 | 115.3656 | -7.7683 | 0.18768 | 21.4371 | 0.52643 | 123.4497 | 18.4387 | 0.19226 | 21.2952 | 0.33875 | 13.9984 | 19.6747 | 120.4697 | 123.468 | 0.52643 | 123.3261 | 15.065 | 0.19226 | 123.468 | 0.52643 | 15.065 | 120.4697 | 123.3261 | -101.8433 | -101.8387
2521.9062 | 110.2982 | -7.869 | 114.9445 | 0.14908 | 0.0053662 | 0.0017454 | 0.0079595 | -0.0017666 | -0.0024289 | 0.015802 | -7.489 | 115.4434 | -7.8278 | 115.329 | 112.2437 | 6.8802 | 6.2393 | 11.7874 | 115.2054 | -7.933 | 0.041199 | 0.49896 | 0.37994 | 123.1979 | -2.7008 | -0.064086 | 0.26093 | 0.33875 | 14.1083 | 19.6564 | 120.1126 | 123.3124 | 0.37994 | 123.0743 | 14.7491 | -0.064086 | 123.3124 | 0.37994 | 14.7491 | 120.1126 | 123.0743 | -122.7722 | -122.8775
2522.9688 | 122.2641 | -8.3359 | 114.0244 | 0.32455 | 0.0053662 | 0.0040952 | 0.0034735 | -0.002194 | -0.0013609 | 0.018792 | -8.6151 | 114.2212 | -8.8669 | 114.5096 | 111.5753 | 7.2418 | 5.9006 | 11.3754 | 114.299 | -8.7708 | -0.53101 | 0.19684 | -0.27924 | 122.8455 | -2.449 | -0.43488 | 0.27466 | 0.25177 | 14.2365 | 19.7113 | 119.9112 | 122.5571 | -0.27924 | 122.6349 | 15.5777 | -0.43488 | 122.5571 | -0.27924 | 15.5777 | 119.9112 | 122.6349 | -122.8912 | -122.7951
2523.9062 | 109.4284 | -7.9468 | 99.4125 | 0.13382 | 0.0038708 | 0.003027 | 0.0064643 | -0.003903 | -0.00050626 | 0.019433 | -7.869 | 115.1093 | -8.194 | 114.8895 | 111.9736 | 7.3151 | 6.1615 | 11.4166 | 114.9673 | -8.1894 | -0.24719 | 15.6967 | 0.077819 | 122.8363 | 12.561 | -0.24261 | 15.5548 | 0.32501 | 14.1083 | 19.3634 | 119.9203 | 123.056 | 0.077819 | 122.9141 | 15.2618 | -0.24261 | 123.056 | 0.077819 | 15.2618 | 119.9203 | 122.9141 | -107.6065 | -107.6019
2524.9688 | 122.4884 | -7.8278 | 114.4043 | -0.072174 | 0.002162 | 0.0051632 | -0.0035761 | -0.002194 | 0.0016299 | 0.017297 | -7.7408 | 115.0635 | -8.0841 | 115.1688 | 112.2894 | 7.6035 | 5.7953 | 12.1216 | 114.9765 | -8.1024 | -0.25635 | 0.65918 | 0.086975 | 122.9965 | -2.1149 | -0.27466 | 0.5722 | 0.34332 | 13.623 | 19.9493 | 120.1172 | 122.8912 | 0.086975 | 122.8043 | 15.4312 | -0.27466 | 122.8912 | 0.086975 | 15.4312 | 120.1172 | 122.8043 | -122.4884 | -122.5067
2525.9062 | 99.8566 | -8.3771 | 110.8154 | -0.011139 | 0.0040846 | 0.0021726 | 0.0083869 | -0.0047574 | -0.0024289 | 0.017083 | -8.0063 | 114.917 | -8.3496 | 114.9628 | 111.9598 | 7.3608 | 5.8914 | 11.4212 | 114.8438 | -8.2947 | 0.027466 | 4.1016 | 0.37079 | 123.3398 | 1.1444 | 0.082397 | 4.0283 | 0.34332 | 14.2685 | 19.7983 | 120.3369 | 123.2941 | 0.37079 | 123.2208 | 15.7379 | 0.082397 | 123.2941 | 0.37079 | 15.7379 | 120.3369 | 123.2208 | -119.165 | -119.1101
2526.9688 | 101.1749 | -5.8228 | 99.3988 | -0.18662 | 0.0045118 | 0.0032406 | 0.0079595 | -0.003262 | 0.00034814 | 0.019647 | -7.2327 | 115.6311 | -7.5851 | 115.7181 | 112.6877 | 7.5531 | 6.2759 | 11.8195 | 115.535 | -7.6355 | -1.7624 | 16.2323 | -1.4099 | 121.5408 | 13.2889 | -1.8127 | 16.1362 | 0.35248 | 12.0987 | 17.6422 | 118.5104 | 121.4539 | -1.4099 | 121.3577 | 13.3759 | -1.8127 | 121.4539 | -1.4099 | 13.3759 | 118.5104 | 121.3577 | -106.9839 | -107.0343
2527.9062 | 122.58 | -6.7703 | 115.0681 | 0.24063 | 0.0025892 | 0.0043088 | 0.0047553 | -0.0013394 | -0.00029266 | 0.01687 | -6.8939 | 115.9378 | -7.2876 | 116.0477 | 113.0402 | 7.8918 | 6.395 | 12.0804 | 115.86 | -7.2372 | -0.51727 | 0.86975 | -0.1236 | 122.818 | -2.0279 | -0.46692 | 0.79193 | 0.39368 | 13.1653 | 18.8507 | 119.8105 | 122.7081 | -0.1236 | 122.6303 | 14.6622 | -0.46692 | 122.7081 | -0.1236 | 14.6622 | 119.8105 | 122.6303 | -122.3557 | -122.3053
2528.9688 | 108.4122 | -8.6655 | 89.3005 | -0.11032 | 0.0028028 | 0.0049496 | 0.0079595 | -0.00069859 | -0.00093346 | 0.016229 | -7.7133 | 115.1276 | -8.1711 | 115.1871 | 112.1979 | 7.8873 | 6.3034 | 11.792 | 115.0864 | -8.0978 | 0.49438 | 25.827 | 0.95215 | 123.8525 | 22.8973 | 0.56763 | 25.7858 | 0.45776 | 14.9689 | 20.4575 | 120.8633 | 123.793 | 0.95215 | 123.7518 | 16.5527 | 0.56763 | 123.793 | 0.95215 | 16.5527 | 120.8633 | 123.7518 | -97.4716 | -97.3984
2529.9062 | 122.4289 | -6.7566 | 115.5579 | 0.13382 | 0.0042982 | 0.003027 | 0.0006965 | -0.0011258 | 0.0024845 | 0.018151 | -6.5872 | 116.2079 | -6.9946 | 116.2674 | 113.2965 | 7.9239 | 6.5872 | 11.9476 | 116.1072 | -6.9946 | -0.23804 | 0.65002 | 0.16937 | 123.024 | -2.2614 | -0.23804 | 0.54932 | 0.40741 | 13.3438 | 18.7042 | 120.0531 | 122.9645 | 0.16937 | 122.8638 | 14.6805 | -0.23804 | 122.9645 | 0.16937 | 14.6805 | 120.0531 | 122.8638 | -122.5525 | -122.5525
2530.9688 | 101.7426 | -2.6779 | 89.9643 | -0.087433 | 0.0057934 | 0.001318 | 0.0075323 | -0.003262 | -0.00029266 | 0.017724 | -5.2689 | 117.5949 | -5.6396 | 117.7643 | 114.6835 | 8.1711 | 7.1045 | 11.9522 | 117.54 | -5.5893 | -2.9617 | 27.6306 | -2.5909 | 120.4422 | 24.7192 | -2.9114 | 27.5757 | 0.37079 | 9.7824 | 14.6301 | 117.3614 | 120.2728 | -2.5909 | 120.2179 | 10.849 | -2.9114 | 120.2728 | -2.5909 | 10.849 | 117.3614 | 120.2179 | -95.6039 | -95.5536
2531.9062 | 94.1483 | -5.5252 | 106.5445 | 0.0041197 | 0.0040846 | 0.003027 | 0.0088141 | -0.0019802 | 0.00056194 | 0.01986 | -5.0858 | 117.7277 | -5.5435 | 117.8925 | 114.9307 | 8.2169 | 6.7154 | 11.824 | 117.6224 | -5.5069 | -0.01831 | 11.1832 | 0.43945 | 123.4177 | 8.3862 | 0.018311 | 11.0779 | 0.45776 | 12.2406 | 17.3492 | 120.4559 | 123.2529 | 0.43945 | 123.1476 | 13.7421 | 0.018311 | 123.2529 | 0.43945 | 13.7421 | 120.4559 | 123.1476 | -112.088 | -112.0514
2532.9688 | 106.9611 | -5.6213 | 112.7838 | 0.4924 | 0.0023756 | 0.0028134 | 0.0073187 | -0.00069859 | 0.00077554 | 0.018579 | -4.9988 | 117.8238 | -5.4291 | 117.8009 | 114.798 | 8.3084 | 7.283 | 12.2223 | 117.6727 | -5.4657 | 0.19226 | 5.04 | 0.62256 | 123.4222 | 2.0142 | 0.15564 | 4.8889 | 0.4303 | 12.9044 | 17.8436 | 120.4193 | 123.4451 | 0.62256 | 123.2941 | 13.9297 | 0.15564 | 123.4451 | 0.62256 | 13.9297 | 120.4193 | 123.2941 | -118.2129 | -118.2495
2533.9062 | 97.6913 | -5.3558 | 115.8005 | 0.019379 | 0.0030164 | 0.0060178 | 0.0075323 | -0.00091219 | -0.0011471 | 0.018365 | -5.0308 | 117.8375 | -5.4565 | 117.7689 | 114.743 | 8.5785 | 7.37 | 12.3962 | 117.6819 | -5.5023 | -0.10071 | 2.037 | 0.32501 | 123.1247 | -1.0574 | -0.14648 | 1.8814 | 0.42572 | 12.7258 | 17.7521 | 120.0989 | 123.1934 | 0.32501 | 123.0377 | 13.9343 | -0.14648 | 123.1934 | 0.32501 | 13.9343 | 120.0989 | 123.0377 | -121.257 | -121.3028
2534.9688 | 122.6807 | -5.2139 | 117.4072 | 0.088043 | 0.0019482 | 0.003027 | -0.0042169 | -0.00091219 | 0.0012027 | 0.019006 | -5.1224 | 117.7322 | -5.452 | 117.7917 | 114.798 | 8.345 | 7.283 | 12.5015 | 117.6544 | -5.5069 | -0.23804 | 0.32501 | 0.091553 | 123.0057 | -2.6093 | -0.29297 | 0.24719 | 0.32959 | 12.4969 | 17.7155 | 120.0119 | 122.9462 | 0.091553 | 122.8683 | 13.559 | -0.29297 | 122.9462 | 0.091553 | 13.559 | 120.0119 | 122.8683 | -122.8592 | -122.9141
2535.9062 | 104.4067 | -5.246 | 117.3706 | 0.13382 | 0.0045118 | 0.00089078 | 0.0058233 | -0.0011258 | -0.00029266 | 0.016015 | -5.0812 | 117.8009 | -5.484 | 117.7734 | 114.7385 | 8.0933 | 7.608 | 12.1445 | 117.7139 | -5.4703 | -0.23804 | 0.4303 | 0.16479 | 123.0194 | -2.6321 | -0.2243 | 0.34332 | 0.40283 | 12.854 | 17.3904 | 119.9844 | 123.0469 | 0.16479 | 122.9599 | 13.3392 | -0.2243 | 123.0469 | 0.16479 | 13.3392 | 119.9844 | 122.9599 | -122.8546 | -122.8409
2536.9688 | 104.9469 | -6.5094 | 116.6336 | -0.14847 | 0.0047254 | 0.0015316 | 0.0062507 | -0.001553 | -0.0015745 | 0.018792 | -6.221 | 116.6565 | -6.6284 | 116.6656 | 113.6444 | 8.3038 | 7.0358 | 11.8973 | 116.5466 | -6.6193 | -0.11902 | 0.022888 | 0.28839 | 123.175 | -2.9892 | -0.10986 | -0.086975 | 0.40741 | 13.5452 | 18.4067 | 120.1538 | 123.1659 | 0.28839 | 123.056 | 14.8132 | -0.10986 | 123.1659 | 0.28839 | 14.8132 | 120.1538 | 123.056 | -123.262 | -123.2529
2537.9062 | 122.8638 | -6.1798 | 116.1942 | 0.14145 | 0.0057934 | 0.0023862 | 0.0058233 | 0.0010104 | 0.00056194 | 0.017724 | -6.0928 | 116.7984 | -6.4545 | 116.5329 | 113.5437 | 8.0338 | 6.9809 | 12.0483 | 116.5695 | -6.5781 | -0.27466 | 0.60425 | 0.086976 | 122.7127 | -2.6505 | -0.39825 | 0.37537 | 0.36163 | 13.1607 | 18.2281 | 119.7235 | 122.9782 | 0.086976 | 122.7493 | 14.2136 | -0.39825 | 122.9782 | 0.086976 | 14.2136 | 119.7235 | 122.7493 | -122.6486 | -122.7722
2538.9531 | 110.9116 | -6.1157 | 103.5599 | -0.034027 | 0.0040846 | -0.0012454 | 0.0073187 | 0.0014376 | -0.0013609 | 0.017724 | -5.6717 | 117.1875 | -6.0608 | 117.0181 | 113.736 | 7.5943 | 6.8207 | 12.0163 | 116.8854 | -6.2942 | 0.054932 | 13.6276 | 0.44403 | 123.1339 | 10.1761 | -0.17853 | 13.3255 | 0.3891 | 12.9364 | 18.132 | 119.8517 | 123.3032 | 0.44403 | 123.0011 | 13.71 | -0.17853 | 123.3032 | 0.44403 | 13.71 | 119.8517 | 123.0011 | -109.6207 | -109.8541
2539.9062 | 122.5113 | -5.6488 | 116.6336 | 0.25589 | 0.0023756 | 0.0066586 | 0.0011237 | -0.0011258 | 0.0024845 | 0.017724 | -5.571 | 117.2287 | -5.9418 | 117.3889 | 114.3768 | 7.9651 | 6.8756 | 12.4374 | 117.1646 | -5.928 | -0.29297 | 0.59509 | 0.07782 | 123.0377 | -2.2568 | -0.27924 | 0.53101 | 0.37079 | 12.5244 | 18.0862 | 120.0256 | 122.8775 | 0.07782 | 122.8134 | 13.6139 | -0.27924 | 122.8775 | 0.07782 | 13.6139 | 120.0256 | 122.8134 | -122.5754 | -122.5616
2540.9688 | 115.5121 | -5.6625 | 103.2394 | 0.057526 | 0.0053662 | 0.003027 | 0.0086005 | -0.0013394 | -0.0017881 | 0.015588 | -5.4932 | 117.4072 | -5.8777 | 117.366 | 114.3951 | 7.8506 | 7.3288 | 11.8149 | 117.2882 | -5.8731 | -0.21515 | 14.1678 | 0.16937 | 123.0286 | 11.1557 | -0.21057 | 14.0488 | 0.38452 | 12.9913 | 17.4774 | 120.0577 | 123.0698 | 0.16937 | 122.9507 | 13.5132 | -0.21057 | 123.0698 | 0.16937 | 13.5132 | 120.0577 | 122.9507 | -109.1171 | -109.1125
2541.9219 | 122.8088 | -5.5435 | 116.8579 | 0.12619 | 0.00066656 | 0.00067718 | -0.0016535 | -0.0017666 | 0.0012027 | 0.018579 | -5.4565 | 117.3019 | -5.8136 | 117.4622 | 114.4684 | 7.8873 | 7.1777 | 11.6409 | 117.3019 | -5.7953 | -0.27008 | 0.44403 | 0.086975 | 123.0057 | -2.3895 | -0.25177 | 0.44403 | 0.35706 | 12.7213 | 17.1844 | 120.0119 | 122.8455 | 0.086975 | 122.8455 | 13.4308 | -0.25177 | 122.8455 | 0.086975 | 13.4308 | 120.0119 | 122.8455 | -122.6715 | -122.6532
2542.9688 | 122.7081 | -5.3284 | 116.7709 | 0.11856 | 0.00066656 | 0.00046358 | 0.0039007 | -0.0058256 | -0.00071986 | 0.01986 | -5.452 | 117.334 | -5.7907 | 117.6682 | 114.6835 | 8.2397 | 7.2418 | 12.204 | 117.4393 | -5.6534 | -0.46234 | 0.56305 | -0.1236 | 122.9965 | -2.0874 | -0.32501 | 0.66833 | 0.33874 | 12.5702 | 17.5323 | 120.0119 | 122.6624 | -0.1236 | 122.7676 | 13.5681 | -0.32501 | 122.6624 | -0.1236 | 13.5681 | 120.0119 | 122.7676 | -122.5616 | -122.4243
2543.9062 | 122.5067 | -4.8523 | 118.0527 | 0.26352 | 0.0079298 | 0.0021726 | 0.0062507 | -0.0036892 | 0.0016299 | 0.018151 | -4.8614 | 118.0573 | -5.2139 | 118.0801 | 115.0406 | 8.194 | 7.1732 | 11.9476 | 117.9749 | -5.191 | -0.36163 | 0.004578 | -0.009155 | 122.9324 | -3.0121 | -0.33875 | -0.077819 | 0.35248 | 12.0255 | 16.7999 | 119.8929 | 122.9095 | -0.009155 | 122.8271 | 13.0463 | -0.33875 | 122.9095 | -0.009155 | 13.0463 | 119.8929 | 122.8271 | -123.2666 | -123.2437
2544.9688 | 122.8958 | -5.3238 | 117.0135 | 0.20248 | 0.0030164 | 0.0025998 | 0.0021917 | -0.0041166 | 0.00077554 | 0.017297 | -5.2689 | 117.5491 | -5.5847 | 117.7597 | 114.7705 | 8.4091 | 7.2144 | 11.7508 | 117.5217 | -5.5573 | -0.26093 | 0.53558 | 0.054932 | 123.0835 | -2.243 | -0.23346 | 0.50812 | 0.31586 | 12.5381 | 17.0746 | 120.0943 | 122.8729 | 0.054932 | 122.8455 | 13.7329 | -0.23346 | 122.8729 | 0.054932 | 13.7329 | 120.0943 | 122.8455 | -122.5983 | -122.5708
2545.9062 | 122.1451 | -5.1132 | 117.6361 | 0.20248 | 0.0030164 | 0.001318 | 0.0094549 | -0.002194 | -0.00029266 | 0.018365 | -4.7653 | 118.1396 | -5.159 | 117.8787 | 114.8758 | 8.2306 | 7.4707 | 12.0163 | 117.8009 | -5.3513 | -0.045777 | 0.50354 | 0.3479 | 122.9919 | -2.7603 | -0.23804 | 0.1648 | 0.39368 | 12.5839 | 17.1295 | 119.989 | 123.2529 | 0.3479 | 122.9141 | 13.3438 | -0.23804 | 123.2529 | 0.3479 | 13.3438 | 119.989 | 122.9141 | -122.7951 | -122.9874
2546.9688 | 122.4289 | -5.0079 | 117.3798 | 0.72128 | 0.002162 | 0.0021726 | -0.0007989 | -0.004971 | -0.0011471 | 0.021142 | -4.8386 | 117.8146 | -5.3055 | 118.0435 | 115.0314 | 8.3908 | 7.283 | 12.5244 | 117.8329 | -5.3009 | -0.29755 | 0.43487 | 0.16937 | 123.0515 | -2.3483 | -0.29297 | 0.45319 | 0.46692 | 12.291 | 17.5323 | 120.0394 | 122.8226 | 0.16937 | 122.8409 | 13.3987 | -0.29297 | 122.8226 | 0.16937 | 13.3987 | 120.0394 | 122.8409 | -122.6852 | -122.6807
2547.9062 | 122.9279 | -4.8798 | 117.9703 | 0.11856 | 0.00323 | 0.0028134 | 0.0002691 | -0.0034756 | 0.00034814 | 0.017511 | -4.7562 | 118.0069 | -5.1544 | 118.1213 | 115.1321 | 8.3862 | 6.8939 | 11.5631 | 117.952 | -5.1178 | -0.27466 | 0.036621 | 0.1236 | 123.0011 | -2.8381 | -0.23804 | -0.018311 | 0.39825 | 11.7737 | 16.4429 | 120.0119 | 122.8867 | 0.1236 | 122.8317 | 13.266 | -0.23804 | 122.8867 | 0.1236 | 13.266 | 120.0119 | 122.8317 | -123.1247 | -123.0881
2548.9688 | 122.9691 | -5.0949 | 117.6727 | 0.088043 | 0.0019482 | 0.0023862 | 0.0009101 | -0.00668 | 0.00077554 | 0.018151 | -5.0858 | 117.7689 | -5.3925 | 117.9016 | 114.9124 | 8.3588 | 6.9946 | 11.7233 | 117.7094 | -5.3741 | -0.29755 | 0.096131 | 0.009156 | 122.9965 | -2.7603 | -0.27924 | 0.036622 | 0.3067 | 12.0895 | 16.8182 | 120.0073 | 122.8638 | 0.009156 | 122.8043 | 13.4537 | -0.27924 | 122.8638 | 0.009156 | 13.4537 | 120.0073 | 122.8043 | -123.0652 | -123.0469
2549.9062 | 122.8958 | -4.9988 | 117.778 | 0.18723 | 0.0040846 | 0.006445 | 0.0021917 | -0.0071072 | 0.00077554 | 0.01922 | -4.8706 | 117.9153 | -5.2597 | 117.9977 | 114.9948 | 8.4137 | 6.8024 | 11.792 | 117.8192 | -5.2597 | -0.26093 | 0.13733 | 0.12817 | 122.9965 | -2.7832 | -0.26093 | 0.041199 | 0.3891 | 11.8011 | 16.7908 | 119.9936 | 122.9141 | 0.12817 | 122.818 | 13.4125 | -0.26093 | 122.9141 | 0.12817 | 13.4125 | 119.9936 | 122.818 | -123.0377 | -123.0377
2550.9688 | 122.9416 | -5.2139 | 117.572 | 0.21011 | 0.001521 | 0.0040952 | 0.0034735 | -0.0071072 | 0.00034814 | 0.018365 | -4.9301 | 117.8604 | -5.3101 | 117.8101 | 114.7751 | 8.3771 | 6.7932 | 11.6455 | 117.6178 | -5.484 | -0.096131 | 0.28839 | 0.28381 | 123.024 | -2.7969 | -0.27008 | 0.045777 | 0.37994 | 12.0071 | 16.8594 | 119.989 | 123.0743 | 0.28381 | 122.8317 | 13.591 | -0.27008 | 123.0743 | 0.28381 | 13.591 | 119.989 | 122.8317 | -122.8821 | -123.056
2551.9219 | 122.9233 | -4.7699 | 117.7094 | -0.81223 | -0.0016834 | 0.0025998 | 0.0024053 | -0.0064664 | -0.0011471 | 0.017297 | -4.6463 | 118.0893 | -5.04 | 118.3228 | 115.274 | 8.2718 | 7.0312 | 11.673 | 118.0344 | -5.0171 | -0.27008 | 0.37994 | 0.1236 | 123.0927 | -2.4353 | -0.24719 | 0.32501 | 0.39368 | 11.8011 | 16.4429 | 120.0439 | 122.8592 | 0.1236 | 122.8043 | 13.0417 | -0.24719 | 122.8592 | 0.1236 | 13.0417 | 120.0439 | 122.8043 | -122.7493 | -122.7264
2552.9531 | 122.3007 | -5.072 | 117.7689 | 0.057526 | 0.0038708 | 0.0025998 | 0.011591 | -0.003903 | 0.0012027 | 0.018579 | -4.7424 | 118.1763 | -5.1086 | 117.9657 | 114.8987 | 7.9605 | 7.0358 | 11.4624 | 117.8329 | -5.3101 | -0.036622 | 0.40741 | 0.32959 | 123.0377 | -2.8702 | -0.23804 | 0.064087 | 0.36621 | 12.1078 | 16.5344 | 119.9707 | 123.2483 | 0.32959 | 122.905 | 13.0325 | -0.23804 | 123.2483 | 0.32959 | 13.0325 | 119.9707 | 122.905 | -122.8775 | -123.0789
2553.9062 | 122.8638 | -4.7745 | 117.8787 | 0.21774 | 0.00323 | 0.0058042 | 0.0045417 | -0.0030484 | -0.00029266 | 0.017938 | -4.5136 | 118.222 | -4.9255 | 118.2816 | 115.0406 | 8.0887 | 7.3425 | 11.9293 | 118.0435 | -5.0354 | -0.15106 | 0.34332 | 0.26092 | 123.056 | -2.8381 | -0.26093 | 0.1648 | 0.41199 | 12.117 | 16.7038 | 119.8151 | 122.9965 | 0.26092 | 122.818 | 12.8632 | -0.26093 | 122.9965 | 0.26092 | 12.8632 | 119.8151 | 122.818 | -122.8043 | -122.9141
2554.9688 | 122.9416 | -4.5959 | 117.6407 | -0.18662 | 0.002162 | 0.0051632 | 0.0011237 | -0.0047574 | 0.00034814 | 0.017083 | -4.5502 | 118.2358 | -4.9164 | 118.4784 | 115.4617 | 8.7021 | 7.6309 | 12.0621 | 118.2724 | -4.8569 | -0.32043 | 0.59509 | 0.045776 | 123.0743 | -2.179 | -0.26093 | 0.63171 | 0.36621 | 12.2269 | 16.658 | 120.0577 | 122.8317 | 0.045776 | 122.8683 | 13.298 | -0.26093 | 122.8317 | 0.045776 | 13.298 | 120.0577 | 122.8683 | -122.5571 | -122.4976
2555.9062 | 122.5616 | -4.7195 | 117.7414 | 0.21011 | 0.0053662 | -0.0012454 | 0.0058233 | -0.003262 | 0.00098914 | 0.017083 | -4.5364 | 118.3044 | -4.9393 | 118.3319 | 115.2695 | 8.6563 | 7.338 | 12.1078 | 118.1488 | -4.9576 | -0.21973 | 0.56305 | 0.1831 | 123.0515 | -2.4719 | -0.23804 | 0.40741 | 0.40283 | 12.0575 | 16.8274 | 119.989 | 123.024 | 0.1831 | 122.8683 | 13.3759 | -0.23804 | 123.024 | 0.1831 | 13.3759 | 119.989 | 122.8683 | -122.6807 | -122.699
2557.0156 | 123.0423 | -4.5868 | 117.6636 | 0.21011 | 0.0045118 | 0.00067718 | 0.0049689 | -0.003262 | -0.00071986 | 0.018792 | -4.4037 | 118.3319 | -4.8248 | 118.5287 | 115.4984 | 8.8715 | 7.0038 | 11.6959 | 118.2129 | -4.8294 | -0.23804 | 0.66833 | 0.18311 | 123.1155 | -2.1652 | -0.24261 | 0.54932 | 0.42114 | 11.5906 | 16.2827 | 120.0851 | 122.9187 | 0.18311 | 122.7997 | 13.4583 | -0.24261 | 122.9187 | 0.18311 | 13.4583 | 120.0851 | 122.7997 | -122.4884 | -122.493
2558.75 | 122.9141 | -4.5639 | 117.865 | -0.14847 | 0.004939 | 0.0021726 | 0.0015509 | -0.0041166 | -0.0011471 | 0.01687 | -4.4357 | 118.3548 | -4.8569 | 118.4509 | 115.4297 | 8.4869 | 7.2739 | 12.1582 | 118.222 | -4.8706 | -0.29297 | 0.48981 | 0.12817 | 123.0148 | -2.4353 | -0.3067 | 0.35706 | 0.42114 | 11.8378 | 16.7221 | 119.9936 | 122.9187 | 0.12817 | 122.7859 | 13.0508 | -0.3067 | 122.9187 | 0.12817 | 13.0508 | 119.9936 | 122.7859 | -122.7219 | -122.7356
2559.8281 | 122.6074 | -4.4403 | 118.4052 | -0.064545 | -0.00061524 | 0.003027 | -0.0010125 | -0.0056118 | -0.00029266 | 0.018151 | -4.3671 | 118.4143 | -4.7379 | 118.6478 | 115.6082 | 8.3862 | 7.7499 | 11.5402 | 118.3914 | -4.6921 | -0.29755 | 0.009156 | 0.073243 | 123.0881 | -2.7969 | -0.25177 | -0.013733 | 0.37079 | 12.1902 | 15.9805 | 120.0485 | 122.8546 | 0.073243 | 122.8317 | 12.8265 | -0.25177 | 122.8546 | 0.073243 | 12.8265 | 120.0485 | 122.8317 | -123.143 | -123.0972
2560.7344 | 122.7722 | -4.5959 | 118.2495 | 0.14908 | 0.0013074 | 0.0055906 | 0.0011237 | -0.0028348 | -0.00071986 | 0.017511 | -4.2755 | 118.4189 | -4.6875 | 118.4692 | 115.448 | 8.3267 | 7.6813 | 11.6318 | 118.2175 | -4.8065 | -0.091553 | 0.16937 | 0.32043 | 123.0652 | -2.8015 | -0.21057 | -0.032044 | 0.41199 | 12.2772 | 16.2277 | 120.0439 | 123.0148 | 0.32043 | 122.8134 | 12.9227 | -0.21057 | 123.0148 | 0.32043 | 12.9227 | 120.0439 | 122.8134 | -122.937 | -123.056
2561.6719 | 115.4022 | -4.8248 | 118.0984 | -0.095062 | 0.0025892 | 0.0025998 | 0.0096685 | -0.0034756 | -0.0015745 | 0.019006 | -4.5136 | 118.2587 | -4.9713 | 118.3365 | 115.3152 | 8.3725 | 7.9651 | 11.6226 | 118.1717 | -4.9576 | -0.14648 | 0.16022 | 0.31128 | 123.1613 | -2.7832 | -0.13275 | 0.073242 | 0.45776 | 12.7899 | 16.4474 | 120.1401 | 123.0835 | 0.31128 | 122.9965 | 13.1973 | -0.13275 | 123.0835 | 0.31128 | 13.1973 | 120.1401 | 122.9965 | -123.0698 | -123.056
2562.4531 | 122.3465 | -4.4861 | 118.0939 | -0.23239 | 0.0019482 | 0.0025998 | 0.0006965 | -0.0062528 | 0.00013454 | 0.019006 | -4.3808 | 118.4509 | -4.7791 | 118.5608 | 115.5396 | 8.4274 | 8.1116 | 11.6959 | 118.4143 | -4.7195 | -0.29297 | 0.35706 | 0.10529 | 123.0469 | -2.5543 | -0.23346 | 0.32043 | 0.39825 | 12.5977 | 16.1819 | 120.0256 | 122.937 | 0.10529 | 122.9004 | 12.9135 | -0.23346 | 122.937 | 0.10529 | 12.9135 | 120.0256 | 122.9004 | -122.8729 | -122.8134
2562.9062 | 122.2321 | -4.6097 | 118.1168 | 0.24063 | 0.0051526 | -0.0012454 | 0.0062507 | -0.003903 | -0.00071986 | 0.019647 | -4.4769 | 118.4052 | -4.8019 | 118.19 | 115.1779 | 8.313 | 7.814 | 11.3251 | 118.222 | -4.921 | -0.19226 | 0.28839 | 0.13275 | 122.7997 | -2.9388 | -0.31128 | 0.10529 | 0.32501 | 12.4237 | 15.9348 | 119.7876 | 123.0148 | 0.13275 | 122.8317 | 12.9227 | -0.31128 | 123.0148 | 0.13275 | 12.9227 | 119.7876 | 122.8317 | -122.9187 | -123.0377
2563.9219 | 122.8134 | -40.0726 | 82.6538 | 0.27115 | 0.0040846 | 0.0040952 | 0.013727 | -0.0013394 | 0.00077554 | 0.015588 | -46.138 | 77.4307 | -46.4355 | 83.5373 | 78.9963 | 4.6234 | 0.09613 | 5.5069 | 81.0242 | -40.9882 | -6.3629 | -5.2231 | -6.0654 | 123.6099 | -3.6575 | -0.91553 | -1.6296 | 0.29755 | 40.1688 | 45.5795 | 119.0689 | 117.5034 | -6.0654 | 121.0968 | 44.696 | -0.91553 | 117.5034 | -6.0654 | 44.696 | 119.0689 | 121.0968 | -129.0894 | -123.642
2564.9062 | 122.1634 | -7.5394 | 110.3485 | 0.12619 | 0.0036572 | 0.0021726 | 0.0043281 | -0.0011258 | 0.00034814 | 0.018151 | -7.8232 | 114.9719 | -8.1345 | 115.329 | 112.4039 | 8.2581 | 7.2327 | 11.174 | 115.0772 | -7.9697 | -0.59509 | 4.6234 | -0.28381 | 122.8683 | 2.0554 | -0.4303 | 4.7287 | 0.31128 | 14.772 | 18.7134 | 119.9432 | 122.5113 | -0.28381 | 122.6166 | 15.7974 | -0.4303 | 122.5113 | -0.28381 | 15.7974 | 119.9432 | 122.6166 | -118.483 | -118.3182
2565.9062 | 122.9965 | -44.2154 | 78.2639 | 0.33218 | 0.0042982 | 0.0040952 | 0.0079595 | -0.0036892 | -0.00093346 | 0.01217 | -37.8754 | 83.2489 | -37.7518 | 84.7504 | 83.8257 | 3.7628 | -2.6505 | -0.737 | 81.6422 | -43.2129 | 6.4636 | 4.985 | 6.34 | 128.9658 | 5.5618 | 1.0025 | 3.3783 | -0.1236 | 41.5649 | 43.4784 | 128.0411 | 127.4643 | 6.34 | 125.8575 | 47.9782 | 1.0025 | 127.4643 | 6.34 | 47.9782 | 128.0411 | 125.8575 | -116.0156 | -121.4767
2566.9062 | 123.0469 | -112.8708 | 9.819 | 0.1796 | 0.0038708 | 0.006445 | 0.021418 | -0.003262 | -0.00071986 | 0.0051205 | -112.3123 | 10.025 | -112.9623 | 9.8648 | 9.407 | -6.0699 | -17.5095 | -10.3821 | 9.9472 | -113.2233 | -0.091552 | 0.20599 | 0.55847 | 122.7356 | -0.41199 | -0.35248 | 0.12817 | 0.65002 | 95.3613 | 102.4887 | 122.2778 | 122.8958 | 0.55847 | 122.818 | 106.8008 | -0.35248 | 122.8958 | 0.55847 | 106.8008 | 122.2778 | 122.818 | -122.7814 | -123.0423
2567.9062 | 122.4106 | -9.7961 | 106.6818 | 0.42374 | 0.0040846 | 0.0062314 | 0.0064643 | -0.0011258 | 0.00034814 | 0.021569 | -9.5261 | 113.3652 | -9.6634 | 113.5529 | 110.3622 | 7.9971 | 5.6946 | 10.9268 | 112.7563 | -10.2219 | 0.13275 | 6.6833 | 0.27008 | 123.349 | 3.6804 | -0.42572 | 6.0745 | 0.13733 | 15.4907 | 20.723 | 120.1584 | 123.1613 | 0.27008 | 122.5525 | 17.7933 | -0.42572 | 123.1613 | 0.27008 | 17.7933 | 120.1584 | 122.5525 | -116.3452 | -116.9037
2568.9844 | 118.0161 | -9.3796 | 94.2947 | 0.14908 | 0.0030164 | 0.0034544 | 0.0081733 | -0.0017666 | 0.0018435 | 0.020074 | -9.2422 | 113.7634 | -9.407 | 113.6307 | 110.788 | 8.1757 | 6.0699 | 10.6155 | 113.6261 | -9.5398 | -0.027465 | 19.4687 | 0.13733 | 123.0103 | 16.4932 | -0.16022 | 19.3314 | 0.16479 | 15.4495 | 19.9951 | 120.1675 | 123.143 | 0.13733 | 123.0057 | 17.5552 | -0.16022 | 123.143 | 0.13733 | 17.5552 | 120.1675 | 123.0057 | -103.7018 | -103.8345
2569.9062 | 123.6191 | -101.8707 | 22.3984 | 0.25589 | 0.004939 | 0.0049496 | 0.022486 | -0.001553 | 0.00034814 | 0.0066159 | -112.619 | 9.6863 | -113.1821 | 28.6377 | 27.0309 | 0.53101 | -12.5244 | -4.454 | 25.9735 | -96.6568 | -11.3113 | -12.7121 | -10.7483 | 130.5084 | 4.6326 | 5.2139 | 3.5751 | 0.56305 | 89.3463 | 97.4167 | 128.9017 | 111.557 | -10.7483 | 127.8442 | 102.4017 | 5.2139 | 111.557 | -10.7483 | 102.4017 | 128.9017 | 127.8442 | -135.5804 | -119.0552
2570.9062 | 122.7585 | -58.9279 | 63.0157 | 0.20248 | 0.0028028 | 0.0060178 | -0.0005853 | -0.0030484 | -7.9062e-05 | 0.0053343 | -59.4086 | 62.7914 | -59.9396 | 59.8434 | 60.9512 | 1.7349 | -5.2551 | 1.1169 | 62.6083 | -60.0174 | -1.0117 | -0.2243 | -0.48065 | 118.7714 | -2.0645 | -1.0895 | -0.40741 | 0.53101 | 53.6728 | 60.0449 | 119.8792 | 121.7194 | -0.48065 | 121.5363 | 60.6628 | -1.0895 | 121.7194 | -0.48065 | 60.6628 | 119.8792 | 121.5363 | -122.9553 | -123.0331
2571.9062 | 122.9965 | -116.9037 | 5.7587 | 0.25589 | 0.0028028 | 0.00089078 | 0.021631 | 0.001865 | -0.0015745 | 0.0042661 | -116.6061 | 5.8365 | -117.215 | 5.8594 | 5.5527 | -6.6513 | -19.5877 | -12.2452 | 5.809 | -117.2745 | -0.31128 | 0.07782 | 0.29755 | 122.7631 | -0.20599 | -0.37079 | 0.050354 | 0.60883 | 97.316 | 104.6585 | 122.4564 | 122.7402 | 0.29755 | 122.7127 | 110.2524 | -0.37079 | 122.7402 | 0.29755 | 110.2524 | 122.4564 | 122.7127 | -122.9736 | -123.0331
2572.9062 | 122.9736 | -116.0751 | 6.6467 | 0.21774 | 0.00323 | 0.0049496 | 0.018854 | -0.0024076 | -7.9062e-05 | 0.0046933 | -115.6815 | 6.7337 | -116.2811 | 6.6284 | 6.1523 | -6.7474 | -19.3588 | -12.3871 | 6.7337 | -116.4322 | -0.20599 | 0.086975 | 0.39368 | 122.7036 | -0.49438 | -0.35706 | 0.086975 | 0.59967 | 96.7163 | 103.688 | 122.2275 | 122.8088 | 0.39368 | 122.8088 | 109.3277 | -0.35706 | 122.8088 | 0.39368 | 109.3277 | 122.2275 | 122.8088 | -122.9279 | -123.0789
2573.9062 | 122.9782 | -116.5604 | 6.1157 | 0.21011 | 0.0023756 | 0.0085812 | 0.02035 | -0.0043302 | 0.00013454 | 0.0029843 | -116.2766 | 6.2576 | -116.8167 | 6.1981 | 5.7129 | -6.8848 | -19.7113 | -12.3459 | 6.1798 | -116.9495 | -0.25635 | 0.14191 | 0.28381 | 122.7585 | -0.40283 | -0.3891 | 0.064087 | 0.54016 | 96.8491 | 104.2145 | 122.2733 | 122.818 | 0.28381 | 122.7402 | 109.6756 | -0.3891 | 122.818 | 0.28381 | 109.6756 | 122.2733 | 122.7402 | -122.9324 | -123.0652
2574.9062 | 123.0789 | -115.2008 | 7.4158 | 0.20248 | 0.00323 | 0.0043088 | 0.019709 | -0.0028348 | -0.00093346 | 0.0059751 | -115.0177 | 7.4478 | -115.5716 | 7.4112 | 7.0129 | -6.4407 | -19.4641 | -12.2818 | 7.489 | -115.654 | -0.37079 | 0.032044 | 0.18311 | 122.612 | -0.40283 | -0.45319 | 0.073243 | 0.55389 | 95.7367 | 102.919 | 122.2137 | 122.6486 | 0.18311 | 122.6898 | 108.7601 | -0.45319 | 122.6486 | 0.18311 | 108.7601 | 122.2137 | 122.6898 | -122.9874 | -123.0698
2575.9062 | 122.9507 | -115.6265 | 7.1045 | 0.22537 | 0.001521 | 0.0017454 | 0.014155 | -0.0051846 | -0.00050626 | 0.0070431 | -115.5487 | 6.9672 | -116.0568 | 6.8985 | 6.5277 | -6.6559 | -19.2764 | -12.0209 | 7.0633 | -115.9836 | -0.4303 | -0.13733 | 0.07782 | 122.525 | -0.57678 | -0.35706 | -0.041199 | 0.50812 | 96.3501 | 103.6057 | 122.1542 | 122.5937 | 0.07782 | 122.6898 | 108.9706 | -0.35706 | 122.5937 | 0.07782 | 108.9706 | 122.1542 | 122.6898 | -123.1613 | -123.0881
2576.9062 | 122.9919 | -64.9887 | 57.2159 | -0.011139 | 0.00045296 | 0.0015316 | -0.0022943 | -0.0051846 | 0.0018435 | 0.0042661 | -64.92 | 57.6599 | -65.1535 | 57.9941 | 56.6666 | 1.4832 | -6.5598 | -1.8585 | 57.9803 | -65.094 | -0.16479 | 0.44403 | 0.068664 | 122.9828 | -0.54932 | -0.10529 | 0.76447 | 0.23346 | 58.429 | 63.1302 | 121.6553 | 122.6486 | 0.068664 | 122.9691 | 66.4719 | -0.10529 | 122.6486 | 0.068664 | 66.4719 | 121.6553 | 122.9691 | -122.3694 | -122.3099
2577.9062 | 122.8455 | -61.8942 | 59.761 | 0.12619 | 0.0025892 | 0.0023862 | 0.0019781 | -0.0062528 | -0.0022153 | 0.0051205 | -61.3129 | 61.6333 | -61.1938 | 63.8077 | 60.9055 | 0.045776 | -6.9855 | -1.3504 | 61.9263 | -61.3449 | 0.70038 | 1.8723 | 0.58136 | 125.7019 | 1.1444 | 0.54932 | 2.1652 | -0.11902 | 54.9088 | 60.5438 | 122.7997 | 123.5275 | 0.58136 | 123.8205 | 61.94 | 0.54932 | 123.5275 | 0.58136 | 61.94 | 122.7997 | 123.8205 | -120.9549 | -121.106
2578.9219 | 111.5158 | -115.9195 | 6.7291 | -0.11795 | 2.5564e-05 | -0.00060462 | 0.017573 | -0.0053982 | -0.0017881 | 0.0031979 | -115.7043 | 6.8115 | -116.2491 | 6.7474 | 6.3217 | -6.5186 | -19.0887 | -12.1628 | 6.7795 | -116.3956 | -0.32959 | 0.082397 | 0.21515 | 122.6669 | -0.40741 | -0.47607 | 0.050354 | 0.54474 | 96.8307 | 103.7567 | 122.2412 | 122.731 | 0.21515 | 122.699 | 109.4009 | -0.47607 | 122.731 | 0.21515 | 109.4009 | 122.2412 | 122.699 | -122.9782 | -123.1247
2579.9062 | 122.9691 | -114.7385 | 7.9605 | 0.20248 | -0.00018804 | -0.0016726 | 0.018213 | -0.0056118 | 0.00034814 | 0.0078977 | -114.6149 | 7.8827 | -115.1321 | 7.9559 | 7.4478 | -6.3263 | -19.3726 | -11.7371 | 8.0154 | -115.0223 | -0.39368 | -0.07782 | 0.1236 | 122.6944 | -0.51269 | -0.28381 | 0.054932 | 0.51727 | 95.3659 | 103.0014 | 122.1863 | 122.6212 | 0.1236 | 122.7539 | 108.4122 | -0.28381 | 122.6212 | 0.1236 | 108.4122 | 122.1863 | 122.7539 | -123.0927 | -122.9828
2580.9062 | 122.9782 | -117.1234 | 5.658 | 0.19485 | 0.00066656 | -0.00060462 | 0.016932 | -0.0060392 | -7.9062e-05 | 0.0072569 | -116.9174 | 5.5481 | -117.4576 | 5.6076 | 5.2551 | -6.546 | -19.8212 | -12.3596 | 5.69 | -117.4713 | -0.33417 | -0.10986 | 0.20599 | 122.731 | -0.40283 | -0.3479 | 0.032043 | 0.54016 | 97.3022 | 104.7638 | 122.3785 | 122.6715 | 0.20599 | 122.8134 | 110.5774 | -0.3479 | 122.6715 | 0.20599 | 110.5774 | 122.3785 | 122.8134 | -123.1155 | -123.1293
2581.9062 | 123.0423 | -58.9233 | 63.5651 | 0.7518 | 0.0010938 | -0.00017722 | 0.0026191 | -0.0056118 | -0.0017881 | 0.0044797 | -57.5546 | 64.6774 | -58.223 | 64.563 | 62.439 | 1.5427 | -5.9143 | -1.1993 | 63.7207 | -59.2575 | 0.70038 | 1.1124 | 1.3687 | 123.4863 | -1.1261 | -0.33417 | 0.15564 | 0.66833 | 53.009 | 57.724 | 121.3623 | 123.6008 | 1.3687 | 122.644 | 60.466 | -0.33417 | 123.6008 | 1.3687 | 60.466 | 121.3623 | 122.644 | -121.788 | -122.8226
2582.9062 | 122.9874 | -58.1818 | 64.5126 | 0.14145 | 0.0013074 | 0.0051632 | 0.0019781 | -0.0077482 | -0.00050626 | 0.0025571 | -58.2779 | 64.3066 | -58.6395 | 64.6088 | 62.6999 | 2.3529 | -4.5685 | -0.6546 | 64.3753 | -58.5434 | -0.45776 | -0.20599 | -0.09613 | 122.7905 | -1.8127 | -0.36163 | -0.13733 | 0.36163 | 53.6133 | 57.5272 | 120.8817 | 122.4884 | -0.09613 | 122.5571 | 60.5347 | -0.36163 | 122.4884 | -0.09613 | 60.5347 | 120.8817 | 122.5571 | -123.1522 | -123.056
2583.9062 | 122.5159 | -13.6322 | 108.9157 | 0.13382 | -0.00018804 | -0.0023136 | 0.0039007 | -0.0064664 | -0.00050626 | 0.015161 | -13.6368 | 109.2087 | -13.8611 | 109.2636 | 106.3843 | 8.7616 | 6.2531 | 8.1345 | 109.0485 | -13.9755 | -0.22888 | 0.29297 | -0.004578 | 122.8958 | -2.5314 | -0.34332 | 0.13275 | 0.2243 | 19.8853 | 21.7667 | 120.0165 | 122.8409 | -0.004578 | 122.6807 | 22.3938 | -0.34332 | 122.8409 | -0.004578 | 22.3938 | 120.0165 | 122.6807 | -122.7768 | -122.8912
2584.9688 | 122.8821 | -45.0439 | 70.1981 | 0.15671 | 0.0057934 | 0.006445 | 0.0064643 | -0.0045438 | 0.0065433 | 0.0042661 | -10.936 | 111.3876 | -11.2335 | 64.1006 | 69.6533 | -7.6035 | -6.2393 | -2.8061 | 80.9509 | -44.426 | 33.8104 | 41.1896 | 34.108 | 109.1446 | -0.54474 | 0.61798 | 10.7529 | 0.29755 | 38.8046 | 42.2379 | 114.6973 | 156.4316 | 34.108 | 125.9949 | 37.4405 | 0.61798 | 156.4316 | 34.108 | 37.4405 | 114.6973 | 125.9949 | -81.4316 | -114.624
2585.9062 | 122.3694 | -7.6172 | 115.0406 | 0.16434 | 0.00066656 | 0.0023862 | 0.0017645 | -0.0056118 | -0.00029266 | 0.017083 | -7.6218 | 115.1688 | -7.988 | 115.3198 | 112.294 | 9.6039 | 7.4753 | 9.4345 | 115.0726 | -7.988 | -0.37079 | 0.12817 | -0.004578 | 122.937 | -2.7466 | -0.37079 | 0.032044 | 0.36621 | 15.0925 | 17.0517 | 119.9112 | 122.7859 | -0.004578 | 122.6898 | 17.2211 | -0.37079 | 122.7859 | -0.004578 | 17.2211 | 119.9112 | 122.6898 | -123.0286 | -123.0286
2586.9062 | 122.1817 | -6.6101 | 111.2549 | 0.22537 | 0.0023756 | 0.00089078 | 0.0062507 | -0.0047574 | -0.00071986 | 0.017724 | -6.6147 | 116.1346 | -6.9626 | 116.1987 | 113.2233 | 9.6771 | 7.8003 | 9.7687 | 116.0019 | -7.0221 | -0.35248 | 4.8798 | -0.004578 | 122.8088 | 1.9684 | -0.41199 | 4.747 | 0.3479 | 14.4104 | 16.3788 | 119.8334 | 122.7448 | -0.004578 | 122.612 | 16.2872 | -0.41199 | 122.7448 | -0.004578 | 16.2872 | 119.8334 | 122.612 | -118.2175 | -118.277
2587.9062 | 122.3694 | -7.37 | 115.4297 | 0.12619 | 0.0017346 | 0.001959 | 0.0030463 | -0.004971 | 0.00098914 | 0.018792 | -7.4158 | 115.3198 | -7.7957 | 115.5533 | 112.5183 | 9.4208 | 7.2601 | 9.0591 | 115.2969 | -7.7545 | -0.42572 | -0.10986 | -0.045776 | 122.9233 | -2.9114 | -0.38452 | -0.13275 | 0.37994 | 14.6301 | 16.4291 | 119.8883 | 122.6898 | -0.045776 | 122.6669 | 16.7908 | -0.38452 | 122.6898 | -0.045776 | 16.7908 | 119.8883 | 122.6669 | -123.2254 | -123.1842
2588.9062 | 122.5342 | -8.2077 | 113.8962 | -0.018768 | 0.0010938 | -0.0040226 | 0.0015509 | -0.0060392 | 0.00098914 | 0.019006 | -8.1757 | 114.6469 | -8.4915 | 114.83 | 111.8408 | 9.2468 | 7.1594 | 8.9035 | 114.5691 | -8.4549 | -0.28381 | 0.75073 | 0.032044 | 123.0377 | -2.0554 | -0.24719 | 0.67291 | 0.31586 | 15.3671 | 17.1112 | 120.0485 | 122.8546 | 0.032044 | 122.7768 | 17.4545 | -0.24719 | 122.8546 | 0.032044 | 17.4545 | 120.0485 | 122.7768 | -122.3877 | -122.3511
2589.9062 | 122.4289 | -8.9951 | 113.4613 | 0.15671 | 0.0034436 | -0.00017722 | 0.0021917 | -0.0051846 | 0.00056194 | 0.018365 | -8.9951 | 113.7863 | -9.3109 | 113.9969 | 110.9619 | 8.9401 | 5.896 | 8.432 | 113.7588 | -9.288 | -0.31586 | 0.32501 | 0 | 122.9919 | -2.4994 | -0.29297 | 0.29755 | 0.31586 | 14.8911 | 17.4271 | 119.957 | 122.7814 | 0 | 122.7539 | 17.9352 | -0.29297 | 122.7814 | 0 | 17.9352 | 119.957 | 122.7539 | -122.7722 | -122.7493
2590.9062 | 122.406 | -7.2647 | 115.2008 | 0.11856 | 0.0030164 | -0.00039102 | 0.0019781 | -0.0056118 | -0.00071986 | 0.017297 | -7.2006 | 115.5716 | -7.5394 | 115.7547 | 112.7335 | 9.1965 | 6.4545 | 8.4824 | 115.4617 | -7.5439 | -0.27466 | 0.37079 | 0.064086 | 123.0194 | -2.4673 | -0.27924 | 0.26093 | 0.33874 | 13.7192 | 15.7471 | 119.9982 | 122.8363 | 0.064086 | 122.7264 | 16.4612 | -0.27924 | 122.8363 | 0.064086 | 16.4612 | 119.9982 | 122.7264 | -122.7402 | -122.7448
2591.9062 | 122.4884 | -8.5968 | 113.7863 | 0.20248 | 0.00088016 | -0.0012454 | 0.0009101 | -0.0034756 | -0.00029266 | 0.018579 | -8.3908 | 114.3631 | -8.7296 | 114.473 | 111.4151 | 9.0408 | 6.0562 | 8.1161 | 114.1434 | -8.8806 | -0.13275 | 0.57678 | 0.20599 | 123.0698 | -2.3712 | -0.28381 | 0.35706 | 0.33874 | 14.653 | 16.713 | 120.0119 | 122.9599 | 0.20599 | 122.7402 | 17.6376 | -0.28381 | 122.9599 | 0.20599 | 17.6376 | 120.0119 | 122.7402 | -122.5159 | -122.6669
2592.9062 | 122.2046 | -9.9884 | 112.0605 | 0.3627 | 0.0028028 | 0.0055906 | 0.0039007 | -0.0075344 | 0.00034814 | 0.017724 | -10.0662 | 112.7151 | -10.3867 | 113.0585 | 110.0739 | 9.0271 | 5.8914 | 7.7683 | 112.7335 | -10.2585 | -0.39826 | 0.6546 | -0.07782 | 123.0469 | -1.9867 | -0.27008 | 0.67291 | 0.32043 | 15.8798 | 17.7567 | 120.0623 | 122.7036 | -0.07782 | 122.7219 | 19.0155 | -0.27008 | 122.7036 | -0.07782 | 19.0155 | 120.0623 | 122.7219 | -122.4472 | -122.319
2593.9062 | 122.5662 | -6.0471 | 116.1896 | -0.087433 | 0.00088016 | 0.00067718 | -0.0007989 | -0.0079618 | 0.0016299 | 0.018151 | -5.9235 | 116.8533 | -6.2531 | 117.1005 | 114.0335 | 9.3338 | 6.2576 | 8.1711 | 116.7664 | -6.2805 | -0.20599 | 0.66376 | 0.1236 | 123.1476 | -2.1561 | -0.23346 | 0.57678 | 0.32959 | 12.3047 | 14.2181 | 120.0806 | 122.9004 | 0.1236 | 122.8134 | 15.3809 | -0.23346 | 122.9004 | 0.1236 | 15.3809 | 120.0806 | 122.8134 | -122.4426 | -122.4701
2594.9062 | 122.4014 | -5.9784 | 116.0797 | 0.15671 | 0.00088016 | 0.0038816 | 0.0039007 | -0.00668 | 0.0016299 | 0.017083 | -5.896 | 116.8167 | -6.2942 | 117.0135 | 113.9832 | 9.3521 | 6.3583 | 8.551 | 116.7297 | -6.3034 | -0.31586 | 0.737 | 0.082398 | 122.9919 | -2.0966 | -0.32501 | 0.65002 | 0.39825 | 12.3367 | 14.5294 | 119.9615 | 122.7951 | 0.082398 | 122.7081 | 15.3305 | -0.32501 | 122.7951 | 0.082398 | 15.3305 | 119.9615 | 122.7081 | -122.374 | -122.3831
2595.9062 | 122.525 | -5.6351 | 116.3773 | 0.1796 | -0.00018804 | -0.00039102 | 0.0011237 | -0.0075344 | 0.00013454 | 0.015802 | -5.5161 | 117.2379 | -5.896 | 117.4347 | 114.3906 | 9.1507 | 6.6467 | 8.2764 | 117.1188 | -5.8777 | -0.26093 | 0.8606 | 0.11902 | 123.0698 | -1.9867 | -0.24261 | 0.74158 | 0.37994 | 12.2818 | 13.9114 | 120.0256 | 122.8729 | 0.11902 | 122.7539 | 14.7858 | -0.24261 | 122.8729 | 0.11902 | 14.7858 | 120.0256 | 122.7539 | -122.2733 | -122.2549
2596.9062 | 122.9324 | -57.9208 | 64.9109 | 0.18723 | 0.00045296 | 0.003668 | 0.0043281 | -0.0051846 | 0.00077554 | 0.0066159 | -59.6603 | 62.4252 | -60.1913 | 64.4531 | 62.9562 | 2.7649 | -4.6371 | -0.64087 | 64.5538 | -58.3923 | -2.2705 | -2.4857 | -1.7395 | 122.374 | -1.9547 | -0.4715 | -0.35706 | 0.53101 | 53.2837 | 57.28 | 120.8771 | 120.3461 | -1.7395 | 122.4747 | 60.6857 | -0.4715 | 120.3461 | -1.7395 | 60.6857 | 120.8771 | 122.4747 | -125.1022 | -123.3032
2597.9219 | 122.9919 | -58.0719 | 64.7049 | -0.16373 | -0.0016834 | 0.00089078 | 0.0017645 | -0.0068936 | 0.00034814 | 0.0042661 | -59.2667 | 63.9038 | -59.2987 | 64.3936 | 63.1805 | 2.2156 | -5.3513 | -0.59509 | 64.3021 | -58.5205 | -1.2268 | -0.80109 | -1.1948 | 122.4655 | -1.5244 | -0.44861 | -0.40283 | 0.032043 | 52.7206 | 57.4768 | 121.2524 | 121.9757 | -1.1948 | 122.374 | 60.2875 | -0.44861 | 121.9757 | -1.1948 | 60.2875 | 121.2524 | 122.374 | -124.0036 | -123.2254
2598.9062 | 123.0148 | -58.0627 | 64.5996 | -0.18662 | 0.0010938 | -0.0012454 | -0.0014399 | -0.0064664 | 0.00077554 | 0.0040525 | -57.9117 | 64.7415 | -58.2367 | 64.888 | 63.1851 | 1.9363 | -5.5252 | -1.0391 | 64.6591 | -58.3145 | -0.17395 | 0.14191 | 0.15106 | 122.9507 | -1.4145 | -0.25177 | 0.05951 | 0.32501 | 52.5375 | 57.0236 | 121.2479 | 122.8043 | 0.15106 | 122.7219 | 59.9991 | -0.25177 | 122.8043 | 0.15106 | 59.9991 | 121.2479 | 122.7219 | -122.8363 | -122.9141
2599.9062 | 123.2117 | -83.8257 | 39.4867 | -0.14847 | 0.0013074 | 0.006445 | 0.032953 | -0.0045438 | -0.0028561 | 0.0070431 | -75.856 | 43.3182 | -79.1245 | 41.5054 | 33.1009 | -4.1245 | -9.4986 | -6.514 | 38.4521 | -84.0408 | 4.7012 | 3.8315 | 7.9697 | 125.3311 | -6.3858 | -0.21515 | -1.0345 | 3.2684 | 74.3271 | 77.3117 | 116.9266 | 127.1439 | 7.9697 | 122.2778 | 79.7012 | -0.21515 | 127.1439 | 7.9697 | 79.7012 | 116.9266 | 122.2778 | -118.6111 | -123.5275
2600.9062 | 123.0057 | -58.7814 | 63.858 | 0.19485 | 0.0019482 | 0.003027 | 0.0041143 | -0.0041166 | 0.00077554 | 0.0034115 | -58.0215 | 64.7324 | -58.3282 | 63.5834 | 62.1414 | 1.8082 | -5.4291 | -1.3 | 63.7802 | -59.1568 | 0.45319 | 0.87433 | 0.75989 | 122.3648 | -1.7166 | -0.37537 | -0.07782 | 0.3067 | 53.3524 | 57.4814 | 120.9229 | 123.5138 | 0.75989 | 122.5616 | 60.5896 | -0.37537 | 123.5138 | 0.75989 | 60.5896 | 120.9229 | 122.5616 | -122.1863 | -123.0148
2601.9062 | 122.9507 | -58.1039 | 64.4852 | 0.12619 | 0.0028028 | -0.00060462 | 0.0045417 | -0.00668 | 0.0014163 | 0.0025571 | -58.493 | 64.0778 | -58.8547 | 65.2359 | 63.3133 | 2.0233 | -5.1544 | -0.97504 | 64.7369 | -58.223 | -0.75073 | -0.40741 | -0.3891 | 123.3398 | -1.1719 | -0.11902 | 0.25177 | 0.36163 | 52.9495 | 57.1289 | 121.4172 | 122.1817 | -0.3891 | 122.8409 | 60.1273 | -0.11902 | 122.1817 | -0.3891 | 60.1273 | 121.4172 | 122.8409 | -123.3398 | -122.7081
2602.9219 | 122.3145 | -45.6665 | 64.5721 | -0.049286 | 0.002162 | 0.0045224 | 0.0021917 | -0.0062528 | 0.00098914 | 0.0081113 | -48.5962 | 73.8647 | -49.8047 | 76.8265 | 75.2014 | 5.0125 | -1.9043 | 1.387 | 76.5518 | -46.6003 | -4.1382 | 9.2926 | -2.9297 | 122.493 | 10.6293 | -0.93384 | 11.9797 | 1.2085 | 43.7622 | 47.0535 | 120.8679 | 119.5312 | -2.9297 | 122.2183 | 50.679 | -0.93384 | 119.5312 | -2.9297 | 50.679 | 120.8679 | 122.2183 | -114.3768 | -111.1725
2603.9062 | 122.7585 | -61.7615 | 60.4431 | 0.095673 | 0.0013074 | 0.0023862 | 0.0011237 | -0.0071072 | -7.9062e-05 | 0.0038389 | -62.4435 | 60.2188 | -62.796 | 61.0931 | 59.491 | 1.5793 | -6.0333 | -1.5518 | 60.9055 | -62.0407 | -1.0345 | -0.2243 | -0.68207 | 122.8546 | -0.95215 | -0.27923 | 0.46234 | 0.35248 | 55.7281 | 60.2097 | 121.2524 | 121.9803 | -0.68207 | 122.6669 | 63.3408 | -0.27923 | 121.9803 | -0.68207 | 63.3408 | 121.2524 | 122.6669 | -123.2391 | -122.4838
2604.9062 | 122.9828 | -61.4777 | 60.7132 | 0.17197 | -0.00082884 | -0.00081822 | 0.0024053 | -0.004971 | -0.00050626 | 0.0034115 | -61.409 | 61.2717 | -61.6974 | 61.6928 | 59.8801 | 1.6983 | -5.928 | -1.6891 | 61.3815 | -61.6196 | -0.21973 | 0.55847 | 0.068664 | 123.1705 | -0.83313 | -0.14191 | 0.66833 | 0.28839 | 55.5496 | 59.7885 | 121.3577 | 122.7493 | 0.068664 | 122.8592 | 63.176 | -0.14191 | 122.7493 | 0.068664 | 63.176 | 121.3577 | 122.8592 | -122.4106 | -122.3328
2605.9062 | 122.9599 | -57.9346 | 64.0686 | 0.13382 | -0.001256 | 0.0023862 | 0.0009101 | -0.0075344 | -0.0017881 | 0.0064023 | -56.1584 | 66.2567 | -56.5842 | 66.6367 | 64.3158 | 1.4694 | -5.8456 | -1.6296 | 65.2771 | -57.9208 | 1.3504 | 2.1881 | 1.7761 | 124.5712 | 0.24719 | 0.013733 | 1.2085 | 0.42572 | 52.0889 | 56.3049 | 122.2504 | 124.1913 | 1.7761 | 123.2117 | 59.404 | 0.013733 | 124.1913 | 1.7761 | 59.404 | 122.2504 | 123.2117 | -120.6528 | -121.9894
2606.9062 | 122.9553 | -57.5089 | 64.4623 | 0.15671 | 0.0030164 | 0.0021726 | 0.0011237 | -0.0043302 | -0.0030697 | 0.0042661 | -58.1543 | 64.4806 | -58.4427 | 65.4785 | 63.6108 | 2.2751 | -4.9896 | -0.78278 | 65.1672 | -57.7927 | -0.93384 | 0.018311 | -0.64545 | 122.9874 | -0.85144 | -0.28381 | 0.70496 | 0.28839 | 52.5192 | 56.7261 | 121.1197 | 121.9894 | -0.64545 | 122.6761 | 59.7839 | -0.28381 | 121.9894 | -0.64545 | 59.7839 | 121.1197 | 122.6761 | -122.905 | -122.2549
2607.9219 | 122.5525 | -6.8756 | 102.3056 | -0.19424 | 0.0023756 | 0.0034544 | 0.0021917 | -0.00668 | -0.0011471 | 0.017938 | -6.9855 | 115.8463 | -7.2968 | 115.9103 | 112.9623 | 9.8923 | 6.9855 | 8.2809 | 115.7501 | -7.3563 | -0.42114 | 13.5406 | -0.10986 | 122.7859 | 10.6567 | -0.48065 | 13.4445 | 0.31128 | 13.8611 | 15.1566 | 119.838 | 122.7219 | -0.10986 | 122.6257 | 16.7679 | -0.48065 | 122.7219 | -0.10986 | 16.7679 | 119.838 | 122.6257 | -109.6024 | -109.6619
2608.9062 | 122.5204 | -4.5685 | 118.2449 | -0.087433 | 0.00088016 | -0.001459 | 0.0004827 | -0.0056118 | -0.00029266 | 0.018579 | -4.3945 | 118.2495 | -4.8843 | 118.6157 | 115.5029 | 9.8419 | 7.2235 | 8.3542 | 118.2083 | -4.8157 | -0.31586 | 0.004578 | 0.17395 | 123.1842 | -2.742 | -0.24719 | -0.036621 | 0.48981 | 11.792 | 12.9227 | 120.0714 | 122.818 | 0.17395 | 122.7768 | 14.4104 | -0.24719 | 122.818 | 0.17395 | 14.4104 | 120.0714 | 122.7768 | -123.1293 | -123.0606
2609.9062 | 122.5296 | -6.8436 | 115.3015 | 0.095673 | 0.0036572 | 0.00024998 | -0.0027215 | -0.00668 | -0.0034971 | 0.014734 | -6.8619 | 115.947 | -7.1411 | 116.1438 | 113.2095 | 9.5032 | 6.8985 | 7.6767 | 115.9653 | -7.1228 | -0.29755 | 0.64545 | -0.01831 | 122.9874 | -2.092 | -0.27924 | 0.66376 | 0.27924 | 13.7421 | 14.5203 | 120.0531 | 122.7905 | -0.01831 | 122.8088 | 16.3467 | -0.27924 | 122.7905 | -0.01831 | 16.3467 | 120.0531 | 122.8088 | -122.4426 | -122.4243
2610.9062 | 122.5113 | -5.9555 | 116.1942 | 0.080414 | 0.0034436 | 0.00024998 | 0.0006965 | -0.004971 | 0.0014163 | 0.017724 | -5.8273 | 116.9769 | -6.1569 | 117.1555 | 114.1388 | 9.6359 | 7.5989 | 7.8506 | 116.8671 | -6.1752 | -0.20142 | 0.78278 | 0.12817 | 123.111 | -2.0554 | -0.21973 | 0.67291 | 0.32959 | 13.5544 | 13.8062 | 120.0943 | 122.9324 | 0.12817 | 122.8226 | 15.5914 | -0.21973 | 122.9324 | 0.12817 | 15.5914 | 120.0943 | 122.8226 | -122.3511 | -122.3694
2611.9062 | 122.8363 | -8.139 | 113.8687 | 0.1033 | 0.00023916 | 0.0011044 | -0.0001581 | -0.0060392 | 0.0022707 | 0.016442 | -8.3771 | 114.5096 | -8.5648 | 114.83 | 111.9507 | 9.1736 | 6.6376 | 7.6996 | 114.6103 | -8.4 | -0.42572 | 0.64087 | -0.23804 | 122.9691 | -1.918 | -0.26093 | 0.74158 | 0.18768 | 14.7766 | 15.8386 | 120.0897 | 122.6486 | -0.23804 | 122.7493 | 17.3126 | -0.26093 | 122.6486 | -0.23804 | 17.3126 | 120.0897 | 122.7493 | -122.4335 | -122.2687
2612.9219 | 97.4258 | -1.7487 | 87.2498 | -0.14084 | 0.0040846 | 0.0025998 | 0.0081733 | -0.0058256 | -0.0028561 | 0.018579 | -6.134 | 116.7023 | -6.546 | 116.8121 | 113.8046 | 9.4162 | 7.1228 | 7.6721 | 116.5787 | -6.5186 | -4.7974 | 29.4525 | -4.3854 | 118.5608 | 26.5549 | -4.7699 | 29.3289 | 0.41199 | 8.8715 | 9.4208 | 115.5533 | 118.4509 | -4.3854 | 118.3273 | 11.1649 | -4.7699 | 118.4509 | -4.3854 | 11.1649 | 115.5533 | 118.3273 | -93.7958 | -93.7683
2613.9062 | 122.3282 | -6.633 | 115.8646 | 0.18723 | 0.0010938 | 0.00046358 | 0.0006965 | -0.0047574 | 0.00034814 | 0.017083 | -6.5872 | 116.1209 | -7.0175 | 116.3452 | 113.4613 | 9.5489 | 6.2805 | 7.7087 | 116.0294 | -6.9626 | -0.38452 | 0.25635 | 0.045777 | 122.9782 | -2.4033 | -0.32959 | 0.16479 | 0.4303 | 12.9135 | 14.3417 | 120.0943 | 122.7539 | 0.045777 | 122.6624 | 16.1819 | -0.32959 | 122.7539 | 0.045777 | 16.1819 | 120.0943 | 122.6624 | -122.8821 | -122.8271
2614.9062 | 122.7219 | -16.0904 | 106.2561 | 0.27878 | 0.0013074 | 0.0025998 | 0.0064643 | -0.0068936 | 0.00056194 | 0.015802 | -18.1137 | 104.7958 | -18.1229 | 106.778 | 103.8712 | 8.0658 | 4.2526 | 6.1935 | 106.4072 | -16.4932 | -2.0325 | -1.4603 | -2.0233 | 122.8683 | -2.3849 | -0.40283 | 0.15106 | 0.009156 | 20.343 | 22.2839 | 119.9615 | 120.8862 | -2.0233 | 122.4976 | 24.1562 | -0.40283 | 120.8862 | -2.0233 | 24.1562 | 119.9615 | 122.4976 | -124.379 | -122.7493
2615.9062 | 122.525 | -15.2115 | 107.2769 | 0.18723 | 0.0023756 | 0.0015316 | 0.0013373 | -0.0058256 | 0.0012027 | 0.018579 | -15.2756 | 107.1945 | -16.1041 | 104.0634 | 105.574 | 9.9655 | 5.4611 | 6.5369 | 107.2723 | -15.2023 | -0.89264 | -0.082398 | -0.064087 | 119.2749 | -1.7029 | 0.009155 | -0.004578 | 0.82855 | 20.6726 | 21.7484 | 120.7855 | 122.406 | -0.064087 | 122.4838 | 25.177 | 0.009155 | 122.406 | -0.064087 | 25.177 | 120.7855 | 122.4838 | -123.381 | -122.4792
2616.9062 | 122.9874 | -62.5351 | 59.6878 | 0.088043 | -0.00040164 | -0.00017722 | 0.0021917 | -0.0028348 | -0.00093346 | 0.0046933 | -62.709 | 59.903 | -63.1851 | 59.816 | 58.4198 | 1.7395 | -6.0928 | -1.6113 | 60.054 | -62.8326 | -0.65002 | 0.21515 | -0.17395 | 122.3511 | -1.268 | -0.29755 | 0.36621 | 0.47607 | 56.4423 | 60.9238 | 120.9549 | 122.438 | -0.17395 | 122.5891 | 64.2746 | -0.29755 | 122.438 | -0.17395 | 64.2746 | 120.9549 | 122.5891 | -122.8729 | -122.5204
2617.9062 | 122.8821 | -58.3557 | 63.7665 | 0.14145 | -0.0014696 | 0.0043088 | 0.0017645 | -0.0053982 | 0.0022707 | 0.0055479 | -57.6599 | 64.9429 | -57.9666 | 65.1855 | 63.0478 | 1.593 | -6.0059 | -1.387 | 64.4577 | -58.5434 | 0.3891 | 1.1765 | 0.6958 | 123.5413 | -0.71869 | -0.18768 | 0.69122 | 0.3067 | 52.3499 | 56.9687 | 121.4035 | 123.2986 | 0.6958 | 122.8134 | 59.9487 | -0.18768 | 123.2986 | 0.6958 | 59.9487 | 121.4035 | 122.8134 | -121.7331 | -122.3099
2618.9062 | 105.1117 | -57.6828 | 64.7461 | -2.1855 | -0.00018804 | 0.0070858 | 0.0053961 | -0.0086026 | -0.00050626 | 0.0017027 | -57.7377 | 65.0757 | -57.9941 | 65.2908 | 63.501 | 2.0645 | -5.0812 | -0.98419 | 65.1855 | -57.8247 | -0.31128 | 0.32959 | -0.054932 | 122.9736 | -1.2451 | -0.14191 | 0.43945 | 0.25635 | 52.6016 | 56.6986 | 121.1838 | 122.7585 | -0.054932 | 122.8683 | 59.7473 | -0.14191 | 122.7585 | -0.054932 | 59.7473 | 121.1838 | 122.8683 | -122.7402 | -122.5708
2619.9062 | 122.8821 | -58.1635 | 64.4806 | 0.1796 | 0.00023916 | 0.0015316 | 0.0030463 | -0.0056118 | 0.00034814 | 0.0057615 | -57.7698 | 64.8788 | -58.0078 | 65.6937 | 63.8351 | 2.3438 | -5.8319 | -1.3824 | 64.9612 | -58.1863 | 0.15564 | 0.39825 | 0.39368 | 123.8571 | -0.64545 | -0.022888 | 0.48065 | 0.23804 | 52.3315 | 56.781 | 121.9986 | 123.0423 | 0.39368 | 123.1247 | 60.5072 | -0.022888 | 123.0423 | 0.39368 | 60.5072 | 121.9986 | 123.1247 | -122.4884 | -122.6669
2620.9062 | 122.9965 | -57.4173 | 64.8926 | 0.027008 | -0.00018804 | 0.0062314 | 0.0030463 | -0.0056118 | -0.0020017 | 0.0049069 | -57.4356 | 65.0757 | -57.8247 | 65.9088 | 64.032 | 2.4307 | -5.6168 | -1.3458 | 65.2679 | -57.7652 | -0.40741 | 0.18311 | -0.018311 | 123.3261 | -0.8606 | -0.3479 | 0.37537 | 0.3891 | 51.8005 | 56.0715 | 121.4493 | 122.493 | -0.018311 | 122.6852 | 59.848 | -0.3479 | 122.493 | -0.018311 | 59.848 | 121.4493 | 122.6852 | -122.7173 | -122.6578
2621.9062 | 123.0103 | -58.4656 | 63.6566 | -0.85037 | -0.00061524 | 0.003027 | 0.0053961 | -0.003903 | 0.00034814 | 0.0019163 | -58.5114 | 64.032 | -58.9096 | 64.4165 | 62.4939 | 2.2247 | -5.7678 | -1.4969 | 64.1144 | -58.8272 | -0.44403 | 0.37537 | -0.045777 | 122.8821 | -1.1627 | -0.36163 | 0.45776 | 0.39825 | 52.6978 | 56.9687 | 120.9595 | 122.4976 | -0.045777 | 122.58 | 60.6903 | -0.36163 | 122.4976 | -0.045777 | 60.6903 | 120.9595 | 122.58 | -122.5662 | -122.4838
2622.9062 | 122.9965 | -58.0948 | 64.0457 | 0.16434 | 0.0028028 | 0.0051632 | 0.0017645 | -0.0053982 | 0.00013454 | 0.0046933 | -57.8613 | 65.094 | -58.0261 | 64.7827 | 63.0661 | 2.1469 | -5.5252 | -1.593 | 64.5721 | -58.3374 | 0.068665 | 1.0483 | 0.23346 | 122.8775 | -0.97961 | -0.24261 | 0.52643 | 0.16479 | 52.5696 | 56.5018 | 121.1609 | 123.1888 | 0.23346 | 122.6669 | 60.2417 | -0.24261 | 123.1888 | 0.23346 | 60.2417 | 121.1609 | 122.6669 | -122.0718 | -122.3831
2623.9219 | 122.4152 | -57.9849 | 64.7644 | -0.18662 | -0.0021106 | 0.0017454 | 0.0030463 | -0.0041166 | -0.0041379 | 0.0031979 | -58.4564 | 64.3799 | -58.6533 | 64.9292 | 63.1943 | 2.504 | -5.4062 | -1.4923 | 64.7049 | -58.3054 | -0.66833 | -0.38452 | -0.4715 | 122.9141 | -1.5701 | -0.32044 | -0.059509 | 0.19684 | 52.5787 | 56.4926 | 121.1792 | 122.3648 | -0.4715 | 122.6898 | 60.4889 | -0.32044 | 122.3648 | -0.4715 | 60.4889 | 121.1792 | 122.6898 | -123.4177 | -123.0698
2624.9062 | 122.9553 | -59.4223 | 63.1439 | 0.22537 | -0.0010424 | 0.0043088 | 0.0011237 | -0.0045438 | -0.0015745 | 0.0036253 | -58.9417 | 63.4369 | -59.404 | 63.8351 | 61.8988 | 1.8951 | -5.9372 | -1.5472 | 63.6475 | -59.4223 | 0.01831 | 0.29297 | 0.48065 | 123.2574 | -1.2451 | 0 | 0.50354 | 0.46234 | 53.4851 | 57.8751 | 121.3211 | 122.8592 | 0.48065 | 123.0698 | 61.3174 | 0 | 122.8592 | 0.48065 | 61.3174 | 121.3211 | 123.0698 | -122.5479 | -122.5662
2625.9062 | 122.9828 | -58.0353 | 64.7003 | 0.1796 | -0.001256 | -0.00017722 | 0.0034735 | -0.00668 | -7.9062e-05 | 0.0055479 | -58.0444 | 64.2517 | -58.5846 | 64.7736 | 63.0066 | 2.2202 | -5.5161 | -1.442 | 64.6271 | -58.3191 | -0.54932 | -0.44861 | -0.009156 | 122.8088 | -1.6937 | -0.28381 | -0.073242 | 0.54016 | 52.5192 | 56.5933 | 121.0419 | 122.287 | -0.009156 | 122.6624 | 60.2554 | -0.28381 | 122.287 | -0.009156 | 60.2554 | 121.0419 | 122.6624 | -123.2849 | -123.0194
2626.9062 | 122.9279 | -57.1381 | 65.4556 | 0.20248 | 0.001521 | 0.0015316 | 0.0009101 | -0.004971 | -7.9062e-05 | 0.0046933 | -57.2205 | 65.3687 | -57.5409 | 65.7074 | 63.7802 | 1.9592 | -5.5939 | -1.3184 | 65.4877 | -57.4402 | -0.40283 | -0.086975 | -0.082397 | 122.8455 | -1.6754 | -0.30212 | 0.032044 | 0.32044 | 51.5442 | 55.8197 | 120.9183 | 122.5067 | -0.082397 | 122.6257 | 59.0973 | -0.30212 | 122.5067 | -0.082397 | 59.0973 | 120.9183 | 122.6257 | -122.9965 | -122.8958
2627.9062 | 122.9919 | -59.4452 | 62.8052 | 0.98831 | 0.0025892 | 0.00089078 | 0.0032599 | -0.0058256 | -0.00071986 | 0.0031979 | -58.9828 | 63.3774 | -59.491 | 63.3911 | 61.496 | 1.7487 | -6.1661 | -1.6479 | 63.1302 | -59.7977 | -0.045777 | 0.5722 | 0.46234 | 122.8363 | -1.3092 | -0.35248 | 0.32501 | 0.50812 | 53.2791 | 57.7972 | 120.9412 | 122.8226 | 0.46234 | 122.5754 | 61.1938 | -0.35248 | 122.8226 | 0.46234 | 61.1938 | 120.9412 | 122.5754 | -122.2961 | -122.6028
2628.9062 | 122.9965 | -60.7773 | 61.6241 | -0.087433 | 0.00023916 | 0.003668 | -0.0001581 | -0.0071072 | -0.0030697 | 0.0034115 | -60.466 | 62.0087 | -60.9055 | 62.0956 | 60.2692 | 1.5747 | -6.1844 | -1.7303 | 61.8118 | -61.1206 | -0.12817 | 0.38452 | 0.31128 | 122.8729 | -1.355 | -0.34332 | 0.18768 | 0.43945 | 54.5929 | 59.0469 | 121.0464 | 122.7859 | 0.31128 | 122.5891 | 62.352 | -0.34332 | 122.7859 | 0.31128 | 62.352 | 121.0464 | 122.5891 | -122.5296 | -122.7448
2629.9062 | 122.9919 | -58.5022 | 64.0091 | 0.18723 | 0.0038708 | 0.0021726 | 0.0041143 | -0.0056118 | 0.00013454 | 0.0034115 | -58.5709 | 64.0823 | -58.9188 | 64.1647 | 62.3978 | 1.8723 | -5.571 | -1.3229 | 64.032 | -58.8547 | -0.41656 | 0.073242 | -0.068665 | 122.6669 | -1.6113 | -0.35248 | 0.022888 | 0.3479 | 52.9312 | 57.1793 | 120.9 | 122.5845 | -0.068665 | 122.5342 | 60.3745 | -0.35248 | 122.5845 | -0.068665 | 60.3745 | 120.9 | 122.5342 | -122.9279 | -122.8638
2630.9062 | 122.9965 | -59.2346 | 63.2858 | 0.15671 | 0.00088016 | 0.0043088 | 0.0021917 | -0.0047574 | -0.00050626 | 0.0059751 | -59.3948 | 63.5056 | -59.5413 | 63.2034 | 61.409 | 1.7761 | -5.5618 | -1.5839 | 63.3636 | -59.5413 | -0.3067 | 0.21973 | -0.16022 | 122.438 | -1.8768 | -0.3067 | 0.077819 | 0.14649 | 53.6728 | 57.6508 | 120.6436 | 122.7402 | -0.16022 | 122.5983 | 61.0107 | -0.3067 | 122.7402 | -0.16022 | 61.0107 | 120.6436 | 122.5983 | -122.8271 | -122.8271
2631.9062 | 122.9828 | -58.4885 | 64.1556 | 0.19485 | 0.00023916 | 0.0043088 | 0.0019781 | -0.004971 | 0.00056194 | 0.0059751 | -57.9803 | 64.7781 | -58.2962 | 64.2654 | 62.5717 | 1.8906 | -5.4153 | -1.6891 | 64.2059 | -58.7677 | 0.19226 | 0.62256 | 0.50812 | 122.7539 | -1.5839 | -0.27924 | 0.050354 | 0.31586 | 53.0731 | 56.7993 | 121.0602 | 123.2666 | 0.50812 | 122.6944 | 60.379 | -0.27924 | 123.2666 | 0.50812 | 60.379 | 121.0602 | 122.6944 | -122.4518 | -122.9233
2632.9062 | 122.9828 | -58.0765 | 64.6683 | 0.21774 | 0.0010938 | 0.005377 | 0.0017645 | -0.0077482 | -0.00050626 | 0.0064023 | -58.4885 | 64.2288 | -58.8089 | 64.7507 | 63.0341 | 2.1698 | -5.4749 | -1.6342 | 64.4531 | -58.4564 | -0.73242 | -0.43945 | -0.41199 | 122.8271 | -1.6342 | -0.37994 | -0.21515 | 0.32043 | 52.6016 | 56.4423 | 121.1105 | 122.3053 | -0.41199 | 122.5296 | 60.2463 | -0.37994 | 122.3053 | -0.41199 | 60.2463 | 121.1105 | 122.5296 | -123.4772 | -123.1247
2633.9062 | 122.8821 | -55.7785 | 65.8035 | -0.24002 | 2.5564e-05 | 0.0062314 | 0.0036871 | -0.0071072 | -0.0013609 | 0.0049069 | -56.4239 | 66.3666 | -56.7261 | 67.0486 | 65.6799 | 2.3895 | -4.9713 | -1.6708 | 66.8289 | -56.3553 | -0.94757 | 0.56305 | -0.64545 | 122.8271 | -0.1236 | -0.57678 | 1.0254 | 0.30212 | 50.8072 | 54.1077 | 121.4584 | 122.1451 | -0.64545 | 122.6074 | 58.168 | -0.57678 | 122.1451 | -0.64545 | 58.168 | 121.4584 | 122.6074 | -122.5296 | -122.1588
2634.9062 | 123.0148 | -56.2866 | 66.2613 | -0.0035098 | 2.5564e-05 | 0.0040952 | 0.0047553 | -0.0047574 | -0.0024289 | 0.0034115 | -56.1996 | 66.362 | -56.543 | 66.8427 | 64.8376 | 1.9409 | -5.8273 | -1.5793 | 66.3162 | -56.6299 | -0.25635 | 0.10071 | 0.086975 | 123.1293 | -1.4236 | -0.34332 | 0.054931 | 0.34332 | 50.4593 | 54.7073 | 121.1243 | 122.6486 | 0.086975 | 122.6028 | 58.2275 | -0.34332 | 122.6486 | 0.086975 | 58.2275 | 121.1243 | 122.6028 | -122.8043 | -122.8912
2635.9062 | 122.9874 | -55.6 | 66.9342 | 0.13382 | 0.0013074 | 0.00024998 | -0.0001581 | -0.0062528 | -0.0039243 | 0.0046933 | -55.4214 | 67.186 | -55.7739 | 67.2501 | 65.3595 | 2.243 | -5.2094 | -1.0849 | 67.0258 | -55.8792 | -0.17395 | 0.25177 | 0.17853 | 122.85 | -1.5747 | -0.27923 | 0.091553 | 0.35248 | 50.3906 | 54.5151 | 120.9595 | 122.7859 | 0.17853 | 122.6257 | 57.843 | -0.27923 | 122.7859 | 0.17853 | 57.843 | 120.9595 | 122.6257 | -122.7081 | -122.8134
2636.9062 | 123.1338 | -58.5617 | 63.3133 | -0.12558 | 0.0013074 | 0.0021726 | 0.0006965 | -0.00668 | 0.00056194 | 0.0042661 | -58.0078 | 63.5193 | -58.9188 | 64.6088 | 63.3408 | 2.6825 | -5.1086 | -0.82855 | 64.5767 | -58.3282 | -0.35706 | 0.20599 | 0.55389 | 123.1705 | 0.027466 | 0.23346 | 1.2634 | 0.91095 | 53.4531 | 57.7332 | 121.9025 | 122.081 | 0.55389 | 123.1384 | 61.2442 | 0.23346 | 122.081 | 0.55389 | 61.2442 | 121.9025 | 123.1384 | -122.2321 | -121.6415
2637.9062 | 122.9645 | -57.6096 | 65.0803 | 0.1033 | 0.0013074 | 0.0034544 | 0.0002691 | -0.004971 | -0.0015745 | 0.0049069 | -57.2937 | 65.3595 | -57.5592 | 65.2542 | 63.5513 | 1.9638 | -5.9509 | -1.5884 | 65.1947 | -57.8156 | 0.050354 | 0.27924 | 0.31586 | 122.8638 | -1.5289 | -0.20599 | 0.11444 | 0.2655 | 51.6586 | 56.0211 | 121.1609 | 122.9691 | 0.31586 | 122.8043 | 59.5734 | -0.20599 | 122.9691 | 0.31586 | 59.5734 | 121.1609 | 122.8043 | -122.6395 | -122.8958
2638.9062 | 122.9004 | -57.3761 | 66.1789 | -0.034027 | 0.0010938 | 3.6382e-05 | 0.0024053 | -0.0073208 | 0.0014163 | 0.0049069 | -58.429 | 64.2197 | -58.7494 | 65.0391 | 63.0661 | 2.3392 | -5.7632 | -1.4511 | 64.5126 | -58.4839 | -1.3733 | -1.9592 | -1.0529 | 122.4152 | -3.1128 | -1.1078 | -1.6663 | 0.32043 | 51.6129 | 55.925 | 120.4422 | 121.5958 | -1.0529 | 121.8887 | 59.7153 | -1.1078 | 121.5958 | -1.0529 | 59.7153 | 120.4422 | 121.8887 | -124.9283 | -124.6628
2639.9062 | 122.9874 | -58.5159 | 64.2014 | 0.16434 | -0.0010424 | 0.003668 | 0.0006965 | -0.0062528 | 0.0012027 | 0.0042661 | -58.5526 | 64.1235 | -58.8409 | 64.2517 | 62.4481 | 2.3163 | -5.8502 | -1.6525 | 64.0182 | -58.9188 | -0.32501 | -0.07782 | -0.036621 | 122.7676 | -1.7532 | -0.40283 | -0.18311 | 0.28839 | 52.6657 | 56.8634 | 120.9641 | 122.6395 | -0.036621 | 122.5342 | 60.8322 | -0.40283 | 122.6395 | -0.036621 | 60.8322 | 120.9641 | 122.5342 | -123.0423 | -123.1201
2640.9062 | 122.9507 | -58.1039 | 64.769 | 0.14908 | 0.0023756 | 0.0038816 | 5.5496e-05 | -0.0073208 | 0.0020571 | 0.0014889 | -58.4747 | 64.1235 | -58.7997 | 64.6545 | 62.7411 | 2.3529 | -5.9647 | -1.9958 | 64.2014 | -58.7128 | -0.6958 | -0.64545 | -0.37079 | 122.7585 | -2.0279 | -0.60883 | -0.56763 | 0.32501 | 52.1393 | 56.1081 | 120.845 | 122.2275 | -0.37079 | 122.3053 | 60.4568 | -0.60883 | 122.2275 | -0.37079 | 60.4568 | 120.845 | 122.3053 | -123.5687 | -123.4818
2641.9062 | 122.9874 | -57.5867 | 65.0986 | 0.19485 | 0.0019482 | 0.0021726 | 0.0026191 | -0.00668 | -0.0020017 | 0.0051205 | -57.3578 | 65.2725 | -57.6691 | 65.4648 | 63.6017 | 2.5955 | -5.3146 | -1.4328 | 65.213 | -57.7972 | -0.082397 | 0.17395 | 0.22888 | 123.0515 | -1.4969 | -0.21057 | 0.11444 | 0.31128 | 52.272 | 56.1539 | 121.1884 | 122.8592 | 0.22888 | 122.7997 | 60.1822 | -0.21057 | 122.8592 | 0.22888 | 60.1822 | 121.1884 | 122.7997 | -122.7676 | -122.8958
2642.9062 | 123.0011 | -57.9758 | 64.6133 | 0.21774 | 0.0019482 | 0.0051632 | 0.0041143 | -0.004971 | -0.0011471 | 0.0051205 | -57.9987 | 64.5721 | -58.3923 | 64.8514 | 63.2675 | 2.6276 | -5.4337 | -1.6159 | 64.8056 | -58.1451 | -0.41656 | -0.041198 | -0.022888 | 122.8271 | -1.3458 | -0.16937 | 0.19226 | 0.39368 | 52.5421 | 56.3599 | 121.2433 | 122.5479 | -0.022888 | 122.7814 | 60.6033 | -0.16937 | 122.5479 | -0.022888 | 60.6033 | 121.2433 | 122.7814 | -123.0057 | -122.7585
2643.9062 | 122.9416 | -58.3191 | 64.3478 | 0.0041197 | -0.0021106 | 0.0015316 | 0.0004827 | -0.0071072 | -0.0022153 | 0.0034115 | -57.7606 | 64.9933 | -58.0536 | 64.9658 | 63.0661 | 2.0325 | -5.5161 | -1.7807 | 64.5218 | -58.5342 | 0.2655 | 0.64545 | 0.55847 | 123.2849 | -1.2817 | -0.21515 | 0.17395 | 0.29297 | 52.803 | 56.5384 | 121.3852 | 123.3124 | 0.55847 | 122.8409 | 60.3516 | -0.21515 | 123.3124 | 0.55847 | 60.3516 | 121.3852 | 122.8409 | -122.4014 | -122.8821
2644.9062 | 122.9919 | -57.7515 | 64.92 | 0.21774 | -0.0023242 | -0.00017722 | 0.0006965 | -0.0068936 | 0.00098914 | 0.0046933 | -57.6141 | 64.9704 | -58.017 | 65.0986 | 63.4094 | 2.6642 | -5.3238 | -1.6067 | 65.0024 | -57.9666 | -0.2655 | 0.050354 | 0.13733 | 122.85 | -1.5106 | -0.21515 | 0.082397 | 0.40283 | 52.4277 | 56.1447 | 121.1609 | 122.7219 | 0.13733 | 122.7539 | 60.4156 | -0.21515 | 122.7219 | 0.13733 | 60.4156 | 121.1609 | 122.7539 | -122.937 | -122.8867
2645.9062 | 122.9828 | -59.0836 | 63.652 | 0.13382 | 0.00088016 | -0.0027408 | 0.0004827 | -0.0064664 | 0.00034814 | 0.0046933 | -58.905 | 63.6429 | -59.2667 | 63.6337 | 61.7569 | 2.2705 | -5.7312 | -1.7258 | 63.5193 | -59.436 | -0.18311 | -0.009156 | 0.17853 | 122.7173 | -1.8951 | -0.35248 | -0.13275 | 0.36163 | 53.3524 | 57.3578 | 120.8405 | 122.7264 | 0.17853 | 122.6028 | 61.3541 | -0.35248 | 122.7264 | 0.17853 | 61.3541 | 120.8405 | 122.6028 | -122.9187 | -123.0881
2646.9062 | 122.9416 | -60.3012 | 62.3566 | 0.14908 | 0.0010938 | 0.0034544 | 0.0009101 | -0.0056118 | -0.00050626 | 0.0027707 | -60.4431 | 62.178 | -60.7773 | 62.7823 | 60.9741 | 2.3849 | -6.2439 | -2.1149 | 62.4756 | -60.4843 | -0.47607 | -0.17853 | -0.14191 | 123.0835 | -1.3824 | -0.18311 | 0.11902 | 0.33417 | 54.0573 | 58.1863 | 121.2753 | 122.4792 | -0.14191 | 122.7768 | 62.6862 | -0.18311 | 122.4792 | -0.14191 | 62.6862 | 121.2753 | 122.7768 | -123.1338 | -122.8409
2647.9062 | 122.9874 | -56.1447 | 66.7007 | 0.12619 | 0.00088016 | 0.00046358 | -0.0003717 | -0.0062528 | -0.0013609 | 0.0061887 | -58.1085 | 64.5309 | -58.3786 | 66.362 | 64.2929 | 3.1174 | -4.9805 | -1.0803 | 66.2018 | -56.6437 | -2.2339 | -2.1698 | -1.9638 | 122.5067 | -2.4078 | -0.49896 | -0.49896 | 0.27008 | 51.1642 | 55.0644 | 120.4376 | 120.6757 | -1.9638 | 122.3465 | 59.2621 | -0.49896 | 120.6757 | -1.9638 | 59.2621 | 120.4376 | 122.3465 | -125.0793 | -123.3444
2648.9062 | 122.9736 | -56.5842 | 66.1057 | 0.11856 | 0.0019482 | 0.00024998 | -0.0020807 | -0.0071072 | -0.0024289 | 0.0040525 | -56.5018 | 66.2018 | -56.8588 | 66.2064 | 64.5859 | 2.9114 | -5.2643 | -1.7349 | 66.1423 | -56.9046 | -0.27466 | 0.09613 | 0.082397 | 122.7905 | -1.5198 | -0.32043 | 0.036621 | 0.35706 | 51.3199 | 54.8492 | 121.17 | 122.7859 | 0.082397 | 122.7264 | 59.4955 | -0.32043 | 122.7859 | 0.082397 | 59.4955 | 121.17 | 122.7264 | -122.9645 | -123.0103
2649.9062 | 123.0011 | -58.2687 | 64.389 | 0.15671 | 0.0017346 | 0.00067718 | 0.0053961 | -0.0056118 | -0.0017881 | 0.0053343 | -57.8751 | 64.7461 | -58.2458 | 64.8972 | 62.8372 | 2.4582 | -6.0745 | -2.0599 | 64.389 | -58.5434 | 0.022888 | 0.35706 | 0.39368 | 123.1659 | -1.5518 | -0.27466 | 0 | 0.37079 | 52.1942 | 56.2088 | 121.106 | 123.0148 | 0.39368 | 122.6578 | 60.7269 | -0.27466 | 123.0148 | 0.39368 | 60.7269 | 121.106 | 122.6578 | -122.6349 | -122.9324
2650.9062 | 122.9919 | -58.1543 | 64.5264 | 0.14145 | 0.0025892 | 0.0023862 | -0.0003717 | -0.0041166 | 0.0024845 | 0.0034115 | -57.9117 | 64.6317 | -58.3008 | 64.8285 | 62.5763 | 2.1469 | -6.1523 | -2.0279 | 64.3478 | -58.5434 | -0.14648 | 0.10529 | 0.24262 | 122.9828 | -1.9501 | -0.3891 | -0.17853 | 0.3891 | 52.002 | 56.1264 | 120.7306 | 122.7859 | 0.24262 | 122.5021 | 60.3012 | -0.3891 | 122.7859 | 0.24262 | 60.3012 | 120.7306 | 122.5021 | -122.8271 | -123.0698
2651.9062 | 122.9507 | -57.8522 | 64.9109 | 0.12619 | 0.0025892 | -0.001459 | -0.0001581 | -0.0062528 | -0.00093346 | 0.0061887 | -58.493 | 64.2471 | -58.7906 | 64.7919 | 63.0295 | 2.8244 | -5.8868 | -1.8631 | 64.6454 | -58.2413 | -0.93841 | -0.66376 | -0.64087 | 122.644 | -1.8814 | -0.3891 | -0.2655 | 0.29755 | 51.9653 | 55.9891 | 120.8817 | 122.0993 | -0.64087 | 122.4976 | 60.6766 | -0.3891 | 122.0993 | -0.64087 | 60.6766 | 120.8817 | 122.4976 | -123.7015 | -123.1522
2652.9062 | 122.9736 | -57.8888 | 64.8331 | 0.1033 | -0.0010424 | 0.0058042 | -0.0005853 | -0.0094572 | -7.9062e-05 | 0.0034115 | -58.0582 | 64.5584 | -58.3878 | 64.9338 | 62.9517 | 2.655 | -5.8182 | -1.6434 | 64.6729 | -58.2413 | -0.49896 | -0.27466 | -0.16937 | 122.8226 | -1.8814 | -0.35248 | -0.16022 | 0.32959 | 52.0706 | 56.2454 | 120.8405 | 122.4472 | -0.16937 | 122.5616 | 60.5438 | -0.35248 | 122.4472 | -0.16937 | 60.5438 | 120.8405 | 122.5616 | -123.2208 | -123.0743
2653.9062 | 123.024 | -58.7219 | 63.9954 | -0.14847 | 0.001521 | 0.0045224 | 0.0004827 | -0.0030484 | 0.0020571 | 0.0044797 | -58.7311 | 63.8901 | -59.0973 | 64.183 | 62.4023 | 2.8931 | -6.0837 | -1.973 | 63.8763 | -59.0424 | -0.37537 | -0.10529 | -0.009155 | 122.905 | -1.593 | -0.32043 | -0.11902 | 0.36621 | 52.6382 | 56.749 | 121.1243 | 122.612 | -0.009155 | 122.5983 | 61.615 | -0.32043 | 122.612 | -0.009155 | 61.615 | 121.1243 | 122.5983 | -123.0927 | -123.0377
2654.9062 | 122.9645 | -58.6029 | 63.8626 | 0.233 | 0.00088016 | 0.0017454 | 0.0034735 | -0.00668 | -7.9062e-05 | 0.0055479 | -58.6258 | 63.8123 | -58.992 | 67.1677 | 64.6317 | 2.6779 | -6.5735 | -2.8427 | 64.9109 | -58.4198 | -0.3891 | -0.050354 | -0.022888 | 125.7706 | 0.76904 | 0.1831 | 1.0483 | 0.36621 | 52.0294 | 55.7602 | 123.2346 | 122.4152 | -0.022888 | 123.5138 | 61.2808 | 0.1831 | 122.4152 | -0.022888 | 61.2808 | 123.2346 | 123.5138 | -122.8546 | -122.2824
2655.9062 | 123.0698 | -55.8975 | 66.6916 | 0.22537 | 0.0036572 | 0.0040952 | 0.0043281 | -0.0081754 | -0.0030697 | 0.0057615 | -55.6641 | 66.7831 | -56.0944 | 65.9958 | 64.2105 | 2.9251 | -5.3375 | -1.6251 | 66.3528 | -56.4377 | -0.19684 | 0.091553 | 0.23346 | 121.8933 | -2.4811 | -0.54016 | -0.33874 | 0.4303 | 50.56 | 54.2725 | 120.108 | 122.6807 | 0.23346 | 122.2504 | 58.8226 | -0.54016 | 122.6807 | 0.23346 | 58.8226 | 120.108 | 122.2504 | -122.7859 | -123.1293
2656.9062 | 123.0972 | -57.6965 | 65.0116 | 0.21774 | 0.001521 | 0.00067718 | 0.0039007 | -0.0056118 | -0.00071986 | 0.0061887 | -57.5455 | 64.9658 | -58.2504 | 65.0986 | 63.2629 | 2.8336 | -5.603 | -2.0782 | 64.8102 | -58.0811 | -0.55389 | -0.045777 | 0.15106 | 122.7951 | -1.7487 | -0.38452 | -0.20142 | 0.70496 | 52.0935 | 55.6183 | 120.9595 | 122.6624 | 0.15106 | 122.5067 | 60.5301 | -0.38452 | 122.6624 | 0.15106 | 60.5301 | 120.9595 | 122.5067 | -123.262 | -123.0927
2657.9062 | 123.0148 | -55.9662 | 66.7145 | 0.20248 | 0.00066656 | 0.0049496 | 0.0034735 | -0.003903 | 0.0014163 | 0.0059751 | -55.6824 | 67.0166 | -55.9937 | 67.1036 | 65.2176 | 2.8702 | -5.4474 | -1.7441 | 66.7053 | -56.2454 | -0.027465 | 0.30212 | 0.28381 | 123.0698 | -1.4969 | -0.27923 | -0.009156 | 0.31128 | 50.5188 | 54.2221 | 121.1838 | 122.9828 | 0.28381 | 122.6715 | 58.8364 | -0.27923 | 122.9828 | 0.28381 | 58.8364 | 121.1838 | 122.6715 | -122.7081 | -122.9599
2658.9062 | 122.9599 | -56.5109 | 66.0873 | 0.13382 | 0.0023756 | 0.0023862 | 0.0034735 | -0.0062528 | -0.0011471 | 0.0072569 | -56.7581 | 65.9409 | -57.0602 | 66.4078 | 64.5996 | 2.8839 | -5.4977 | -1.9043 | 66.243 | -56.7169 | -0.54932 | -0.14648 | -0.24719 | 122.9187 | -1.4877 | -0.20599 | 0.15564 | 0.30212 | 51.0132 | 54.6066 | 121.1105 | 122.4518 | -0.24719 | 122.7539 | 59.3948 | -0.20599 | 122.4518 | -0.24719 | 59.3948 | 121.1105 | 122.7539 | -123.1476 | -122.8043
2659.9062 | 122.9874 | -57.1976 | 65.419 | 0.1796 | 0.0010938 | 0.0021726 | 0.0030463 | -0.0056118 | -0.00093346 | 0.0046933 | -57.312 | 65.4922 | -57.5684 | 65.6525 | 64.0274 | 2.8107 | -5.5252 | -1.9318 | 65.538 | -57.4356 | -0.37079 | 0.073243 | -0.11444 | 122.85 | -1.3916 | -0.23804 | 0.11902 | 0.25635 | 51.6724 | 55.2658 | 121.225 | 122.6898 | -0.11444 | 122.7356 | 60.0082 | -0.23804 | 122.6898 | -0.11444 | 60.0082 | 121.225 | 122.7356 | -122.9874 | -122.8546
2660.9062 | 122.9736 | -55.7236 | 66.9067 | 0.18723 | 0.0019482 | 0.0038816 | 0.0030463 | -0.0034756 | -0.00050626 | 0.0049069 | -55.8151 | 66.8381 | -56.131 | 67.3828 | 65.5518 | 2.9617 | -5.3558 | -1.8814 | 67.0303 | -55.9525 | -0.40741 | -0.068664 | -0.091553 | 123.1064 | -1.355 | -0.22888 | 0.1236 | 0.31586 | 50.3677 | 53.8422 | 121.2753 | 122.5616 | -0.091553 | 122.7539 | 58.6853 | -0.22888 | 122.5616 | -0.091553 | 58.6853 | 121.2753 | 122.7539 | -123.0377 | -122.8592
2661.9062 | 122.9919 | -56.4331 | 66.3254 | 0.20248 | 0.0019482 | 0.004736 | 0.0045417 | -0.0053982 | 0.00056194 | 0.0042661 | -56.9366 | 66.2659 | -56.8451 | 65.8264 | 64.1556 | 2.8839 | -5.3329 | -1.7715 | 66.0187 | -56.8817 | -0.41199 | -0.059509 | -0.50354 | 122.2595 | -2.1698 | -0.44861 | -0.3067 | -0.091553 | 51.1002 | 54.6616 | 120.5887 | 122.699 | -0.50354 | 122.4518 | 59.317 | -0.44861 | 122.699 | -0.50354 | 59.317 | 120.5887 | 122.4518 | -123.1705 | -123.2071
2662.9062 | 123.0286 | -55.806 | 66.8838 | 0.26352 | 0.0023756 | 0.0060178 | 0.0045417 | -0.0053982 | -0.00050626 | 0.0053343 | -55.7465 | 66.7831 | -56.1905 | 67.131 | 65.3183 | 2.9892 | -5.2185 | -1.6617 | 66.9067 | -56.0669 | -0.38452 | -0.10071 | 0.059509 | 122.937 | -1.5656 | -0.26093 | 0.022888 | 0.44403 | 50.5875 | 54.1443 | 121.1243 | 122.5891 | 0.059509 | 122.7127 | 58.7952 | -0.26093 | 122.5891 | 0.059509 | 58.7952 | 121.1243 | 122.7127 | -123.0743 | -122.9507
2663.9062 | 122.9919 | -53.9337 | 68.8293 | 0.11093 | 0.0010938 | 3.6382e-05 | 0.0002691 | -0.0062528 | -0.0013609 | 0.0070431 | -54.0253 | 68.541 | -54.4189 | 68.5455 | 66.8381 | 3.3463 | -4.5685 | -1.1948 | 68.6096 | -54.3274 | -0.48523 | -0.28839 | -0.091553 | 122.4792 | -1.9913 | -0.39368 | -0.21973 | 0.39368 | 49.3652 | 52.739 | 120.7718 | 122.4747 | -0.091553 | 122.5433 | 57.28 | -0.39368 | 122.4747 | -0.091553 | 57.28 | 120.7718 | 122.5433 | -123.2483 | -123.1567
2664.9062 | 123.0057 | -55.2475 | 67.4561 | 0.21774 | 0.0017346 | 0.008154 | 0.0041143 | -0.0051846 | 0.0012027 | 0.0042661 | -55.2383 | 67.4652 | -55.5313 | 67.6804 | 65.7852 | 2.8473 | -4.8843 | -1.5381 | 67.424 | -55.5084 | -0.28381 | 0.009155 | 0.009156 | 122.9279 | -1.6708 | -0.26093 | -0.032044 | 0.29297 | 50.3632 | 53.7094 | 121.0327 | 122.7127 | 0.009156 | 122.6715 | 58.0948 | -0.26093 | 122.7127 | 0.009156 | 58.0948 | 121.0327 | 122.6715 | -122.9874 | -122.9645
2665.9062 | 122.9874 | -54.4693 | 68.1839 | 0.14908 | 0.00088016 | 0.0015316 | 0.0030463 | -0.0060392 | -0.00071986 | 0.0068295 | -54.3777 | 68.2343 | -54.7256 | 68.7149 | 66.8518 | 3.0899 | -4.953 | -1.4694 | 68.3121 | -54.689 | -0.25635 | 0.050354 | 0.091552 | 123.1842 | -1.3321 | -0.21973 | 0.12817 | 0.3479 | 49.5163 | 52.9999 | 121.3211 | 122.7036 | 0.091552 | 122.7814 | 57.5592 | -0.21973 | 122.7036 | 0.091552 | 57.5592 | 121.3211 | 122.7814 | -122.9095 | -122.8729
2666.9062 | 123.0148 | -54.2816 | 68.3899 | 0.17197 | 0.0017346 | 0.003668 | 0.0049689 | -0.0043302 | -7.9062e-05 | 0.0038389 | -54.1214 | 68.3853 | -54.6021 | 68.573 | 66.5405 | 3.1815 | -4.8019 | -1.3458 | 68.2709 | -54.6982 | -0.32044 | -0.004578 | 0.16022 | 122.8546 | -1.8494 | -0.41656 | -0.11902 | 0.48065 | 49.4797 | 52.9358 | 120.8221 | 122.6669 | 0.16022 | 122.5525 | 57.4631 | -0.41656 | 122.6669 | 0.16022 | 57.4631 | 120.8221 | 122.5525 | -122.9919 | -123.0881
2667.9062 | 123.0148 | -54.4373 | 68.2755 | 0.13382 | 0.0042982 | 0.0032406 | 0.0043281 | -0.003903 | -0.00050626 | 0.0068295 | -54.3457 | 68.2755 | -54.6524 | 68.335 | 66.5314 | 3.0991 | -4.9072 | -1.5106 | 68.2251 | -54.744 | -0.21515 | 0 | 0.091553 | 122.7722 | -1.7441 | -0.3067 | -0.050354 | 0.3067 | 49.53 | 52.9266 | 120.9686 | 122.7127 | 0.091553 | 122.6624 | 57.5363 | -0.3067 | 122.7127 | 0.091553 | 57.5363 | 120.9686 | 122.6624 | -122.9279 | -123.0194
2668.9062 | 123.0743 | -59.5505 | 62.8372 | -0.018768 | -0.00018804 | -0.0010318 | -0.0001581 | -0.00668 | -0.0017881 | 0.0027707 | -58.8776 | 63.7115 | -59.3033 | 63.6887 | 62.0361 | 2.4902 | -6.0883 | -2.4124 | 63.4323 | -59.6008 | 0.24719 | 0.87433 | 0.67291 | 123.2391 | -0.80109 | -0.050354 | 0.59509 | 0.42572 | 53.4622 | 57.1381 | 121.5866 | 123.262 | 0.67291 | 122.9828 | 62.0407 | -0.050354 | 123.262 | 0.67291 | 62.0407 | 121.5866 | 122.9828 | -122.1405 | -122.438
2669.9062 | 123.024 | -58.1406 | 64.595 | 0.21011 | 0.0030164 | 0.001318 | 0.0051825 | -0.001553 | -0.0022153 | 0.0051205 | -57.9895 | 64.65 | -58.3237 | 64.5264 | 62.8235 | 2.33 | -6.1066 | -2.2202 | 64.3524 | -58.5205 | -0.18311 | 0.054931 | 0.15106 | 122.6669 | -1.7715 | -0.37994 | -0.24262 | 0.33417 | 52.034 | 55.9204 | 120.9641 | 122.7905 | 0.15106 | 122.493 | 60.4706 | -0.37994 | 122.7905 | 0.15106 | 60.4706 | 120.9641 | 122.493 | -122.9187 | -123.1155
2670.9062 | 122.9507 | -57.2845 | 65.4694 | 0.17197 | 0.0042982 | 0.0045224 | 0.0064643 | -0.0024076 | 0.00056194 | 0.0036253 | -57.5821 | 65.3137 | -57.756 | 65.3137 | 63.533 | 2.6413 | -5.8456 | -2.0462 | 65.181 | -57.7332 | -0.4715 | -0.15564 | -0.29755 | 122.5983 | -1.9363 | -0.44861 | -0.28839 | 0.17395 | 51.4389 | 55.2383 | 120.8176 | 122.5983 | -0.29755 | 122.4655 | 59.9258 | -0.44861 | 122.5983 | -0.29755 | 59.9258 | 120.8176 | 122.4655 | -123.2254 | -123.2025
2671.9062 | 123.056 | -53.6591 | 68.9163 | 0.019379 | 0.00066656 | 0.0034544 | 0.0021917 | -0.003262 | -0.00029266 | 0.0070431 | -55.5588 | 67.1127 | -55.8105 | 69.0262 | 67.2775 | 3.5019 | -4.6646 | -1.1124 | 68.9026 | -54.007 | -2.1515 | -1.8036 | -1.8997 | 122.6852 | -1.6388 | -0.3479 | -0.013733 | 0.25177 | 48.9944 | 52.5467 | 120.9366 | 120.7718 | -1.8997 | 122.5616 | 57.1609 | -0.3479 | 120.7718 | -1.8997 | 57.1609 | 120.9366 | 122.5616 | -124.7269 | -122.9233
2672.9062 | 123.024 | -55.7922 | 66.9159 | 0.21011 | 0.0017346 | 0.0085812 | 0.0049689 | -0.0047574 | 0.00034814 | 0.0038389 | -56.0532 | 66.8015 | -56.2363 | 67.3004 | 65.5884 | 3.0487 | -5.3238 | -2.0645 | 66.9342 | -56.0989 | -0.44403 | -0.11444 | -0.26093 | 123.0927 | -1.3275 | -0.3067 | 0.01831 | 0.1831 | 50.4684 | 53.7277 | 121.3806 | 122.5937 | -0.26093 | 122.7264 | 58.8409 | -0.3067 | 122.5937 | -0.26093 | 58.8409 | 121.3806 | 122.7264 | -123.1522 | -123.0148
2673.9062 | 122.9874 | -56.7719 | 65.9317 | 0.19485 | 0.0028028 | 0.0040952 | -0.0001581 | -0.0058256 | 0.00034814 | 0.0040525 | -56.5521 | 65.9225 | -56.9733 | 65.8813 | 64.0274 | 2.6047 | -5.5161 | -2.0645 | 65.6891 | -57.2159 | -0.20142 | -0.009156 | 0.21973 | 122.6532 | -1.9043 | -0.44403 | -0.24262 | 0.42114 | 51.2558 | 54.7073 | 120.7993 | 122.6944 | 0.21973 | 122.4609 | 59.3765 | -0.44403 | 122.6944 | 0.21973 | 59.3765 | 120.7993 | 122.4609 | -122.905 | -123.1476
2674.9062 | 123.0148 | -58.3694 | 64.3341 | 0.24826 | 0.0036572 | 0.0066586 | 0.0064643 | -0.003903 | -0.00093346 | 0.0044797 | -58.4152 | 64.183 | -58.8318 | 64.4897 | 62.7045 | 2.2842 | -6.2302 | -2.2888 | 64.2151 | -58.7631 | -0.46234 | -0.15106 | -0.045776 | 122.8592 | -1.6296 | -0.39368 | -0.11902 | 0.41656 | 52.1393 | 56.0806 | 121.0739 | 122.5525 | -0.045776 | 122.5845 | 60.6537 | -0.39368 | 122.5525 | -0.045776 | 60.6537 | 121.0739 | 122.5845 | -123.1659 | -123.0972
2675.9062 | 122.9919 | -58.905 | 63.7527 | -1.1098 | 0.0019482 | 0.0028134 | 0.0071051 | -0.0041166 | -0.00029266 | 0.0053343 | -58.0902 | 64.4302 | -58.5388 | 64.2334 | 62.2421 | 1.9958 | -6.3858 | -2.3941 | 63.8397 | -59.1751 | 0.36621 | 0.67749 | 0.81482 | 123.1384 | -1.5106 | -0.27008 | 0.086975 | 0.44861 | 52.5192 | 56.5109 | 121.1472 | 123.3353 | 0.81482 | 122.7448 | 60.9009 | -0.27008 | 123.3353 | 0.81482 | 60.9009 | 121.1472 | 122.7448 | -122.2916 | -122.9279
2676.9062 | 122.9462 | -56.2912 | 66.2064 | 0.16434 | 0.0053662 | 0.0043088 | 0.0081733 | -0.0030484 | -0.00093346 | 0.0040525 | -55.3757 | 67.6117 | -55.5267 | 68.042 | 66.0324 | 2.4536 | -5.69 | -2.2293 | 67.3874 | -55.9799 | 0.76447 | 1.4053 | 0.91553 | 124.3332 | -0.17395 | 0.31128 | 1.181 | 0.15106 | 50.6012 | 54.0619 | 122.3236 | 123.9029 | 0.91553 | 123.6786 | 58.7448 | 0.31128 | 123.9029 | 0.91553 | 58.7448 | 122.3236 | 123.6786 | -121.7331 | -122.1863
2677.9062 | 122.9462 | -55.4352 | 67.2775 | 0.21011 | 0.0040846 | 0.0034544 | 0.0071051 | -0.0047574 | -0.0017881 | 0.0057615 | -55.5862 | 67.2272 | -55.8884 | 67.4149 | 65.5151 | 2.6459 | -5.1865 | -1.6708 | 67.2501 | -55.7602 | -0.45319 | -0.050354 | -0.15106 | 122.85 | -1.7624 | -0.32501 | -0.027466 | 0.30212 | 50.2487 | 53.7643 | 120.9503 | 122.6624 | -0.15106 | 122.6852 | 58.0811 | -0.32501 | 122.6624 | -0.15106 | 58.0811 | 120.9503 | 122.6852 | -123.1659 | -123.0377
2678.9219 | 122.9187 | -57.0786 | 65.6891 | -0.21713 | 0.0040846 | 0.0049496 | 0.0039007 | -0.0034756 | -0.0020017 | 0.0040525 | -56.9687 | 65.799 | -57.2937 | 66.037 | 64.1235 | 2.6505 | -4.5364 | -2.211 | 65.7303 | -57.3898 | -0.21515 | 0.10986 | 0.10986 | 123.1155 | -1.5656 | -0.31128 | 0.041199 | 0.32501 | 52.5421 | 54.8676 | 121.2021 | 122.8775 | 0.10986 | 122.8088 | 59.729 | -0.31128 | 122.8775 | 0.10986 | 59.729 | 121.2021 | 122.8088 | -122.9828 | -123.0789
2679.9062 | 122.9782 | -56.0165 | 66.7191 | 0.26352 | 0.002162 | 0.003027 | 0.0045417 | -0.001553 | -0.0017881 | 0.0055479 | -55.806 | 66.8518 | -56.218 | 66.8747 | 64.9017 | 2.6321 | -5.0308 | -1.9135 | 66.6779 | -56.3232 | -0.20142 | 0.13275 | 0.21057 | 122.8912 | -1.8173 | -0.3067 | -0.041199 | 0.41199 | 50.9857 | 54.1031 | 120.9183 | 122.8683 | 0.21057 | 122.6944 | 58.6487 | -0.3067 | 122.8683 | 0.21057 | 58.6487 | 120.9183 | 122.6944 | -122.937 | -123.0423
2680.9062 | 122.9691 | -55.2429 | 67.4606 | 0.24063 | 0.0040846 | 0.0045224 | 0.0058233 | -0.0013394 | -0.0026425 | 0.0046933 | -55.5862 | 67.2455 | -55.8975 | 67.6712 | 65.8905 | 3.2913 | -5.127 | -1.6891 | 67.543 | -55.4901 | -0.6546 | -0.21515 | -0.34332 | 122.9141 | -1.5701 | -0.24719 | 0.082398 | 0.31128 | 50.116 | 53.5538 | 121.1334 | 122.4884 | -0.34332 | 122.7859 | 58.5342 | -0.24719 | 122.4884 | -0.34332 | 58.5342 | 121.1334 | 122.7859 | -123.3582 | -122.9507
2681.9062 | 122.9462 | -55.3528 | 67.3416 | 0.15671 | 0.0062208 | 0.0032406 | 0.0060369 | -0.002194 | 0.00013454 | 0.0042661 | -55.3482 | 67.4652 | -55.6641 | 67.4286 | 65.4922 | 2.98 | -4.8431 | -1.7166 | 67.3187 | -55.7281 | -0.31128 | 0.1236 | 0.004577 | 122.7814 | -1.8494 | -0.37537 | -0.022888 | 0.31586 | 50.5096 | 53.6362 | 120.845 | 122.818 | 0.004577 | 122.6715 | 58.3328 | -0.37537 | 122.818 | 0.004577 | 58.3328 | 120.845 | 122.6715 | -123.0057 | -123.0698
2682.9062 | 123.0011 | -55.1468 | 67.5613 | 0.26352 | 0.0023756 | 0.0011044 | 0.0036871 | -0.0028348 | 0.0014163 | 0.0059751 | -54.8264 | 67.8772 | -55.1697 | 67.7628 | 65.9363 | 2.7237 | -5.1361 | -1.6251 | 67.6117 | -55.4352 | -0.022888 | 0.31586 | 0.32044 | 122.9095 | -1.6251 | -0.28839 | 0.050354 | 0.34332 | 50.0107 | 53.5217 | 121.0831 | 123.024 | 0.32044 | 122.7585 | 57.8705 | -0.28839 | 123.024 | 0.32044 | 57.8705 | 121.0831 | 122.7585 | -122.731 | -122.9965
2683.9219 | 122.9965 | -55.3391 | 67.3782 | -0.19424 | -0.004674 | -0.0010318 | -0.0031489 | -0.0051846 | -0.0022153 | 0.0055479 | -55.1971 | 67.3233 | -55.7419 | 67.4561 | 65.712 | 2.6184 | -4.985 | -1.6113 | 67.3233 | -55.6778 | -0.40283 | -0.054932 | 0.14191 | 122.7951 | -1.6663 | -0.33875 | -0.054932 | 0.54474 | 50.354 | 53.7277 | 121.051 | 122.6624 | 0.14191 | 122.6624 | 57.9575 | -0.33875 | 122.6624 | 0.14191 | 57.9575 | 121.051 | 122.6624 | -123.1201 | -123.056
2684.9062 | 122.9095 | -57.8018 | 64.9612 | 0.16434 | 0.0040846 | 0.0072996 | 0.0073187 | -0.0043302 | 0.00056194 | 0.0053343 | -58.0078 | 65.0299 | -58.0948 | 65.0848 | 63.3408 | 2.0096 | -5.4657 | -1.9043 | 64.9933 | -58.1131 | -0.29297 | 0.068664 | -0.20599 | 122.8867 | -1.6205 | -0.31128 | 0.032043 | 0.086976 | 52.3361 | 55.8975 | 121.1426 | 122.8317 | -0.20599 | 122.7951 | 59.8114 | -0.31128 | 122.8317 | -0.20599 | 59.8114 | 121.1426 | 122.7951 | -123.056 | -123.0743
2685.9062 | 122.9874 | -57.4402 | 65.3549 | 0.16434 | 0.0047254 | 0.0066586 | 0.0062507 | -0.002194 | 0.00013454 | 0.0051205 | -57.2388 | 65.5518 | -57.5272 | 65.4282 | 63.5696 | 2.9205 | -5.5069 | -2.3163 | 65.3961 | -57.7377 | -0.086975 | 0.19684 | 0.20142 | 122.8683 | -1.7853 | -0.29755 | 0.041199 | 0.28839 | 51.9333 | 55.1239 | 121.0098 | 122.9919 | 0.20142 | 122.8363 | 60.3607 | -0.29755 | 122.9919 | 0.20142 | 60.3607 | 121.0098 | 122.8363 | -122.8821 | -123.0927
2686.9062 | 122.905 | -58.0307 | 64.6912 | -0.43076 | 0.0047254 | 0.0049496 | 0.0077459 | -0.0024076 | 0.00013454 | 0.0053343 | -57.7972 | 64.9796 | -58.1177 | 64.6591 | 62.883 | 2.9114 | -6.102 | -2.3071 | 64.7049 | -58.3466 | -0.086975 | 0.28839 | 0.23346 | 122.6898 | -1.8082 | -0.31586 | 0.013733 | 0.32044 | 51.9287 | 55.7236 | 120.9137 | 123.0103 | 0.23346 | 122.7356 | 60.9421 | -0.31586 | 123.0103 | 0.23346 | 60.9421 | 120.9137 | 122.7356 | -122.8088 | -123.0377
2687.9062 | 122.9187 | -56.694 | 65.8676 | 0.15671 | 0.0038708 | 0.0045224 | 0.0083869 | 0.0027194 | -0.0041379 | 0.0057615 | -56.5659 | 65.9821 | -56.9733 | 67.2134 | 64.8972 | 2.9297 | -5.0766 | -1.9867 | 66.6321 | -56.6116 | -0.27924 | 0.11444 | 0.12817 | 123.9075 | -0.97046 | 0.082398 | 0.76447 | 0.40741 | 51.6174 | 54.7073 | 121.5912 | 122.6761 | 0.12817 | 123.3261 | 59.6237 | 0.082398 | 122.6761 | 0.12817 | 59.6237 | 121.5912 | 123.3261 | -122.8409 | -122.4792
2688.9219 | 123.0011 | -56.5384 | 66.243 | -0.049286 | -0.0010424 | 0.00089078 | -0.0031489 | -0.0041166 | -0.0020017 | 0.0046933 | -56.813 | 66.0645 | -57.0328 | 66.3803 | 64.4165 | 3.0853 | -5.3558 | -1.6067 | 66.0919 | -56.8909 | -0.49439 | -0.17853 | -0.27466 | 122.9187 | -1.8265 | -0.35248 | -0.15106 | 0.21973 | 51.1826 | 54.9316 | 120.9549 | 122.6028 | -0.27466 | 122.6303 | 59.6237 | -0.35248 | 122.6028 | -0.27466 | 59.6237 | 120.9549 | 122.6303 | -123.2758 | -123.1338
2689.9062 | 122.8958 | -55.8289 | 66.9205 | 0.011749 | 0.0047254 | 0.0066586 | 0.0079595 | -0.00091219 | -0.0030697 | 0.0044797 | -55.5862 | 67.2272 | -55.8746 | 67.0303 | 65.0345 | 3.0167 | -4.4403 | -1.5793 | 66.9571 | -56.1356 | -0.045777 | 0.3067 | 0.24261 | 122.8592 | -1.886 | -0.3067 | 0.036621 | 0.28839 | 51.3885 | 54.2496 | 120.8633 | 123.056 | 0.24261 | 122.7859 | 58.8455 | -0.3067 | 123.056 | 0.24261 | 58.8455 | 120.8633 | 122.7859 | -122.7951 | -123.056
2690.9062 | 122.9416 | -55.0735 | 67.7032 | -0.011139 | 0.0045118 | 0.003668 | 0.0066779 | -0.0013394 | -0.00029266 | 0.0053343 | -54.8721 | 67.9596 | -55.2063 | 67.9276 | 66.0599 | 3.1403 | -5.2917 | -1.7899 | 67.7307 | -55.3299 | -0.13275 | 0.25635 | 0.20142 | 123.0011 | -1.6434 | -0.25635 | 0.027466 | 0.33417 | 49.7818 | 53.2837 | 121.1334 | 123.0331 | 0.20142 | 122.8043 | 58.2138 | -0.25635 | 123.0331 | 0.20142 | 58.2138 | 121.1334 | 122.8043 | -122.9095 | -123.0331
2691.9062 | 122.9004 | -54.8492 | 68.0008 | 0.049896 | 0.0042982 | 0.0049496 | 0.0088141 | -0.00069859 | -0.00093346 | 0.0057615 | -54.9362 | 67.8223 | -55.3024 | 67.9001 | 66.0416 | 3.1677 | -5.1086 | -1.8265 | 67.8177 | -55.2933 | -0.45319 | -0.17853 | -0.086975 | 122.7493 | -1.9592 | -0.44403 | -0.1831 | 0.36621 | 49.7406 | 53.0228 | 120.8908 | 122.6715 | -0.086975 | 122.6669 | 58.017 | -0.44403 | 122.6715 | -0.086975 | 58.017 | 120.8908 | 122.6669 | -123.3032 | -123.2941
2692.9062 | 122.9095 | -54.8813 | 67.923 | -0.026398 | 0.0042982 | 0.006445 | 0.0051825 | -5.7592e-05 | -0.0043515 | 0.0046933 | -54.4556 | 68.3029 | -54.8721 | 67.6758 | 65.9317 | 2.6871 | -5.0858 | -1.6479 | 67.7307 | -55.2979 | 0.009156 | 0.37994 | 0.42572 | 122.5571 | -1.9913 | -0.41656 | -0.19226 | 0.41657 | 49.7955 | 53.2333 | 120.813 | 123.1842 | 0.42572 | 122.612 | 57.5684 | -0.41656 | 123.1842 | 0.42572 | 57.5684 | 120.813 | 122.612 | -122.7951 | -123.2208
2693.9062 | 123.0057 | -55.5954 | 67.0029 | 0.21774 | 0.0023756 | 0.0083676 | 0.0021917 | -0.00027139 | -0.0015745 | 0.0064023 | -55.188 | 67.5888 | -55.5084 | 67.3325 | 65.4877 | 2.71 | -5.4062 | -1.6754 | 67.1677 | -55.8746 | 0.086975 | 0.58594 | 0.40741 | 122.9279 | -1.5152 | -0.27924 | 0.16479 | 0.32044 | 50.1892 | 53.92 | 121.0831 | 123.1842 | 0.40741 | 122.7631 | 58.3054 | -0.27924 | 123.1842 | 0.40741 | 58.3054 | 121.0831 | 122.7631 | -122.5113 | -122.8775
2694.9062 | 122.9004 | -56.5704 | 66.1926 | -0.018768 | 0.0040846 | 0.0060178 | 0.0068915 | 0.00036961 | -0.0011471 | 0.0044797 | -55.7968 | 67.1036 | -56.1127 | 66.3025 | 64.4852 | 2.2614 | -5.6488 | -1.9958 | 66.2338 | -56.8771 | 0.45776 | 0.91095 | 0.77362 | 122.8729 | -1.7075 | -0.3067 | 0.041199 | 0.31586 | 50.9216 | 54.5746 | 121.0556 | 123.674 | 0.77362 | 122.8043 | 58.8318 | -0.3067 | 123.674 | 0.77362 | 58.8318 | 121.0556 | 122.8043 | -122.3053 | -123.0698
2695.9062 | 122.9004 | -57.0511 | 65.6845 | -0.0035098 | 0.0055798 | 0.003027 | 0.0047553 | 0.00036961 | -0.0015745 | 0.0031979 | -56.8405 | 65.8905 | -57.2479 | 66.0233 | 64.1876 | 2.623 | -5.7541 | -1.9958 | 65.799 | -57.3486 | -0.19684 | 0.20599 | 0.21057 | 123.0743 | -1.4969 | -0.29755 | 0.11444 | 0.40741 | 51.297 | 55.0552 | 121.2387 | 122.9416 | 0.21057 | 122.85 | 59.6741 | -0.29755 | 122.9416 | 0.21057 | 59.6741 | 121.2387 | 122.85 | -122.9324 | -123.0331
2696.9062 | 122.9874 | -57.9803 | 64.6408 | 0.095673 | -0.00040164 | 0.0017454 | -0.0037897 | -0.002194 | 0.00056194 | 0.0036253 | -57.6508 | 65.0528 | -57.9483 | 64.8788 | 62.9929 | 2.33 | -6.1203 | -2.1744 | 64.8651 | -58.255 | 0.032044 | 0.41199 | 0.32959 | 122.8592 | -1.6479 | -0.27466 | 0.2243 | 0.29755 | 51.86 | 55.806 | 120.9732 | 123.0331 | 0.32959 | 122.8455 | 60.3104 | -0.27466 | 123.0331 | 0.32959 | 60.3104 | 120.9732 | 122.8455 | -122.5891 | -122.8958
2697.9062 | 122.9507 | -56.5887 | 66.3025 | -0.11032 | 0.0045118 | 0.003027 | 0.0051825 | -0.0036892 | -0.00029266 | 0.0059751 | -56.7902 | 66.1102 | -57.1152 | 65.9637 | 64.1144 | 2.5314 | -5.6396 | -1.8402 | 65.8997 | -57.1609 | -0.52643 | -0.19226 | -0.20142 | 122.5525 | -2.1881 | -0.5722 | -0.40283 | 0.32501 | 50.9491 | 54.7485 | 120.7031 | 122.699 | -0.20142 | 122.4884 | 59.1202 | -0.5722 | 122.699 | -0.20142 | 59.1202 | 120.7031 | 122.4884 | -123.4177 | -123.4634
2698.9062 | 122.9187 | -54.6204 | 68.1656 | 0.14145 | 0.0028028 | 0.0058042 | 0.011377 | -0.001553 | -0.0032835 | 0.0027707 | -54.7302 | 68.0969 | -55.0278 | 68.2846 | 66.2018 | 2.7695 | -5.0125 | -1.7212 | 67.9733 | -55.0781 | -0.40741 | -0.068664 | -0.10986 | 122.905 | -1.9638 | -0.45776 | -0.19226 | 0.29755 | 49.6078 | 52.8992 | 120.8221 | 122.7173 | -0.10986 | 122.5937 | 57.3898 | -0.45776 | 122.7173 | -0.10986 | 57.3898 | 120.8221 | 122.5937 | -123.1934 | -123.2437
2699.9062 | 122.9462 | -54.0619 | 68.7149 | -0.10269 | 0.00323 | 0.0070858 | 0.0053961 | -0.0036892 | -0.0032835 | 0.0042661 | -53.8605 | 68.7332 | -54.4144 | 68.8431 | 66.9388 | 3.1403 | -4.7333 | -1.4191 | 68.7286 | -54.3915 | -0.35248 | 0.01831 | 0.20142 | 122.905 | -1.7761 | -0.32959 | 0.013733 | 0.55389 | 49.3286 | 52.6428 | 121.0007 | 122.7951 | 0.20142 | 122.7905 | 57.2021 | -0.32959 | 122.7951 | 0.20142 | 57.2021 | 121.0007 | 122.7905 | -123.1293 | -123.1064
2700.9062 | 122.9233 | -54.451 | 68.335 | -0.064545 | 0.0040846 | 0.004736 | 0.0062507 | -0.003262 | -0.0026425 | 0.0055479 | -54.5151 | 68.0969 | -55.0003 | 68.4082 | 66.5359 | 3.1128 | -5.4199 | -1.5472 | 68.28 | -54.8172 | -0.54932 | -0.23804 | -0.064087 | 122.8592 | -1.799 | -0.36621 | -0.054932 | 0.48523 | 49.0311 | 52.9037 | 120.9869 | 122.5479 | -0.064087 | 122.731 | 57.5638 | -0.36621 | 122.5479 | -0.064087 | 57.5638 | 120.9869 | 122.731 | -123.3353 | -123.1522
2701.9062 | 122.9462 | -56.0944 | 66.655 | -0.13321 | 0.00323 | 0.0060178 | 0.0039007 | -0.0019802 | -0.0017881 | 0.0023435 | -55.5908 | 67.2043 | -55.9982 | 66.4352 | 64.8148 | 2.7512 | -5.7678 | -1.8997 | 66.5863 | -56.4697 | 0.09613 | 0.54932 | 0.50354 | 122.5296 | -1.8402 | -0.37537 | -0.068664 | 0.40741 | 50.3265 | 54.1946 | 120.9091 | 123.2986 | 0.50354 | 122.6807 | 58.8455 | -0.37537 | 123.2986 | 0.50354 | 58.8455 | 120.9091 | 122.6807 | -122.6532 | -123.1247
2702.9062 | 122.9691 | -54.2725 | 68.4677 | -0.26291 | 0.0040846 | 0.0028134 | 0.0049689 | 0.00036961 | -7.9062e-05 | 0.0055479 | -54.213 | 68.5913 | -54.5517 | 68.8019 | 66.8198 | 3.1219 | -5.3741 | -1.6983 | 68.5272 | -54.5563 | -0.27924 | 0.1236 | 0.059509 | 123.0743 | -1.6479 | -0.28381 | 0.05951 | 0.33874 | 48.8983 | 52.5742 | 121.0922 | 122.8638 | 0.059509 | 122.7997 | 57.3944 | -0.28381 | 122.8638 | 0.059509 | 57.3944 | 121.0922 | 122.7997 | -123.0194 | -123.024
2703.9062 | 122.9187 | -52.1988 | 70.3995 | -0.19424 | 0.0028028 | 0.0025998 | 0.0030463 | -0.0024076 | 0.0012027 | 0.0061887 | -51.0315 | 71.4478 | -51.5625 | 70.7108 | 68.4357 | 2.8336 | -4.7699 | -1.3504 | 70.665 | -52.4368 | 0.63629 | 1.0483 | 1.1673 | 122.9095 | -1.9638 | -0.23804 | 0.2655 | 0.53101 | 47.4289 | 50.8484 | 120.6345 | 123.6465 | 1.1673 | 122.8638 | 55.0323 | -0.23804 | 123.6465 | 1.1673 | 55.0323 | 120.6345 | 122.8638 | -121.962 | -122.8363
2704.9062 | 122.9095 | -53.9566 | 68.8156 | -0.20187 | 0.0036572 | 0.003668 | 0.0017645 | -0.0028348 | 0.00034814 | 0.0040525 | -54.0436 | 68.8248 | -54.3182 | 68.866 | 67.0395 | 3.0945 | -5.4977 | -2.124 | 68.7515 | -54.2908 | -0.36163 | 0.009155 | -0.086975 | 122.8226 | -1.7761 | -0.33417 | -0.064087 | 0.27466 | 48.4589 | 51.8326 | 120.9961 | 122.7814 | -0.086975 | 122.7081 | 57.0511 | -0.33417 | 122.7814 | -0.086975 | 57.0511 | 120.9961 | 122.7081 | -123.1338 | -123.1064
2705.9062 | 122.9324 | -54.7989 | 68.0237 | -0.23239 | 0.0019482 | 0.0011044 | 0.0047553 | -0.0026212 | -0.0041379 | 0.0044797 | -55.7053 | 67.1631 | -56.0211 | 67.2775 | 65.6754 | 3.6667 | -5.1498 | -1.7349 | 67.7719 | -55.2429 | -1.2222 | -0.8606 | -0.90637 | 122.0764 | -2.3483 | -0.44403 | -0.25177 | 0.31586 | 49.649 | 53.064 | 120.4742 | 121.962 | -0.90637 | 122.5708 | 58.4656 | -0.44403 | 121.962 | -0.90637 | 58.4656 | 120.4742 | 122.5708 | -124.0448 | -123.2666
2706.9062 | 122.9324 | -55.3574 | 67.4194 | -0.095062 | 0.0034436 | 0.001959 | 0.0043281 | -0.001553 | -7.9062e-05 | 0.0053343 | -55.3574 | 67.3599 | -55.7648 | 67.5293 | 65.657 | 3.035 | -5.6808 | -1.9684 | 67.4377 | -55.6641 | -0.40741 | -0.05951 | 0 | 122.8867 | -1.7624 | -0.3067 | 0.01831 | 0.40741 | 49.6765 | 53.389 | 121.0144 | 122.7173 | 0 | 122.7951 | 58.3923 | -0.3067 | 122.7173 | 0 | 58.3923 | 121.0144 | 122.7951 | -123.1842 | -123.0835
2707.9062 | 122.9599 | -53.0914 | 69.5023 | -0.14084 | 0.0045118 | 0.001959 | 0.0039007 | -0.00091219 | -0.00050626 | 0.0066159 | -53.1052 | 69.4839 | -53.5904 | 69.9966 | 67.8268 | 3.2593 | -4.9438 | -1.5335 | 69.6899 | -53.3707 | -0.49896 | -0.01831 | -0.013733 | 123.0881 | -1.6754 | -0.27924 | 0.18768 | 0.48523 | 48.1476 | 51.5579 | 120.9183 | 122.5754 | -0.013733 | 122.7814 | 56.3507 | -0.27924 | 122.5754 | -0.013733 | 56.3507 | 120.9183 | 122.7814 | -123.0927 | -122.8729
2708.9219 | 123.0377 | -53.7277 | 68.9804 | 0.1796 | 0.0030164 | 0.0015316 | -0.0003717 | -5.7592e-05 | 0.0012027 | 0.0064023 | -53.6865 | 69.0125 | -54.039 | 69.1544 | 67.2821 | 3.4241 | -5.2322 | -1.799 | 68.9941 | -54.0024 | -0.31128 | 0.032043 | 0.041199 | 122.8821 | -1.6983 | -0.27466 | 0.013733 | 0.35248 | 48.4955 | 51.9287 | 121.0098 | 122.7402 | 0.041199 | 122.7219 | 57.1518 | -0.27466 | 122.7402 | 0.041199 | 57.1518 | 121.0098 | 122.7219 | -123.0194 | -122.9828
2709.9062 | 122.9691 | -54.0527 | 68.8293 | -0.21713 | 0.0053662 | 0.001318 | 0.0056097 | -0.003903 | 0.00077554 | 0.0055479 | -54.0939 | 68.6874 | -54.4327 | 68.8934 | 66.9937 | 3.3737 | -5.1453 | -1.8494 | 68.7012 | -54.4189 | -0.37994 | -0.14191 | -0.041199 | 122.9462 | -1.8356 | -0.36621 | -0.12817 | 0.33875 | 48.9075 | 52.2034 | 121.0464 | 122.7402 | -0.041199 | 122.7539 | 57.4265 | -0.36621 | 122.7402 | -0.041199 | 57.4265 | 121.0464 | 122.7539 | -123.262 | -123.2483
2710.9062 | 107.8262 | -6.2531 | 116.6702 | -0.14847 | 0.0036572 | 0.001318 | 0.0026191 | -0.0024076 | 0.00098914 | 0.017083 | -6.1478 | 116.7526 | -6.5598 | 116.7389 | 113.736 | 11.3434 | 7.3883 | 6.4316 | 116.7297 | -6.5277 | -0.3067 | 0.082398 | 0.10529 | 122.9919 | -2.9343 | -0.27466 | 0.059509 | 0.41199 | 13.6414 | 12.6846 | 119.989 | 123.0057 | 0.10529 | 122.9828 | 17.5964 | -0.27466 | 123.0057 | 0.10529 | 17.5964 | 119.989 | 122.9828 | -123.23 | -123.1979
2711.9062 | 122.8821 | -53.5217 | 69.1315 | 0.40085 | 0.0028028 | 0.00046358 | 0.0030463 | -0.0026212 | 0.0012027 | 0.0046933 | -53.54 | 69.4656 | -53.7552 | 69.754 | 67.9871 | 3.6118 | -4.8477 | -2.0416 | 69.4519 | -53.7735 | -0.23346 | 0.33417 | -0.01831 | 123.2758 | -1.1444 | -0.25177 | 0.32043 | 0.21515 | 48.674 | 51.4801 | 121.5088 | 122.9874 | -0.01831 | 122.9736 | 57.1335 | -0.25177 | 122.9874 | -0.01831 | 57.1335 | 121.5088 | 122.9736 | -122.8867 | -122.905
2712.9062 | 122.9279 | -53.3798 | 69.3512 | -0.1561 | 0.002162 | 0.0025998 | 0.0043281 | -0.003903 | -0.0015745 | 0.0042661 | -53.2654 | 69.5938 | -53.4805 | 69.7861 | 67.9688 | 3.7354 | -4.6371 | -1.9592 | 69.6442 | -53.5309 | -0.10071 | 0.24262 | 0.11444 | 123.1659 | -1.3824 | -0.15106 | 0.29297 | 0.21515 | 48.7427 | 51.4206 | 121.3486 | 122.9736 | 0.11444 | 123.024 | 57.1152 | -0.15106 | 122.9736 | 0.11444 | 57.1152 | 121.3486 | 123.024 | -122.8317 | -122.8821
2713.9062 | 122.9553 | -55.4626 | 67.1951 | -0.079803 | 0.0045118 | 0.001959 | 0.0056097 | 0.00079681 | 0.00013454 | 0.0068295 | -55.0735 | 67.6209 | -55.481 | 67.4698 | 65.5838 | 3.2959 | -5.3375 | -2.2156 | 67.5339 | -55.6824 | -0.018311 | 0.42572 | 0.3891 | 122.9324 | -1.6113 | -0.21973 | 0.33875 | 0.40741 | 50.1251 | 53.2471 | 121.0464 | 123.0835 | 0.3891 | 122.9965 | 58.7585 | -0.21973 | 123.0835 | 0.3891 | 58.7585 | 121.0464 | 122.9965 | -122.6761 | -122.8775
2714.9062 | 122.9141 | -56.694 | 66.0141 | -0.11795 | 0.0038708 | 0.0068722 | 0.0064643 | -0.00048499 | -0.00071986 | 0.0036253 | -55.1834 | 67.6254 | -55.5222 | 67.5064 | 64.9246 | 2.5269 | -6.1203 | -2.9663 | 66.5222 | -56.7902 | 1.1719 | 1.6113 | 1.5106 | 124.2004 | -1.0895 | -0.09613 | 0.50812 | 0.33875 | 50.5737 | 53.7277 | 121.6187 | 124.3195 | 1.5106 | 123.2162 | 59.2209 | -0.09613 | 124.3195 | 1.5106 | 59.2209 | 121.6187 | 123.2162 | -121.5363 | -122.8043
2715.9062 | 122.9416 | -54.57 | 68.1931 | -0.18662 | 0.0051526 | 0.0032406 | 0.0036871 | -0.0024076 | -0.0013609 | 0.0038389 | -54.3503 | 68.5867 | -54.5609 | 68.6188 | 66.6687 | 3.3875 | -4.9484 | -1.8723 | 68.4036 | -54.7623 | 0.009155 | 0.39368 | 0.21973 | 123.1888 | -1.5244 | -0.19226 | 0.21057 | 0.21057 | 49.6216 | 52.6978 | 121.2387 | 123.1567 | 0.21973 | 122.9736 | 57.9575 | -0.19226 | 123.1567 | 0.21973 | 57.9575 | 121.2387 | 122.9736 | -122.7539 | -122.9553
2716.9062 | 122.905 | -54.039 | 68.7195 | -0.19424 | 0.0040846 | 0.0038816 | 0.0026191 | -0.0041166 | -0.00050626 | 0.0049069 | -54.071 | 68.7744 | -54.3503 | 68.8065 | 66.9159 | 3.2547 | -4.7287 | -1.6205 | 68.7881 | -54.3274 | -0.31128 | 0.054932 | -0.032044 | 122.8455 | -1.8036 | -0.28839 | 0.068665 | 0.27924 | 49.3103 | 52.4185 | 120.9549 | 122.8134 | -0.032044 | 122.8271 | 57.2937 | -0.28839 | 122.8134 | -0.032044 | 57.2937 | 120.9549 | 122.8271 | -123.0698 | -123.0469
2717.9062 | 122.9233 | -51.8005 | 71.0724 | -0.072174 | -0.00018804 | 0.003027 | 0.0004827 | -0.003903 | -0.00093346 | 0.0040525 | -51.6266 | 70.8206 | -52.0981 | 70.7245 | 68.9941 | 3.6987 | -3.9963 | -1.0574 | 70.9671 | -52.1393 | -0.29755 | -0.25177 | 0.17395 | 122.525 | -2.0782 | -0.33875 | -0.10529 | 0.4715 | 47.8043 | 50.7431 | 120.7947 | 122.6212 | 0.17395 | 122.7676 | 55.4993 | -0.33875 | 122.6212 | 0.17395 | 55.4993 | 120.7947 | 122.7676 | -123.1705 | -123.2117
2718.9062 | 122.9279 | -53.3203 | 69.6899 | -0.095062 | 0.0045118 | 0.001959 | 0.0066779 | -0.0026212 | -0.00071986 | 0.0040525 | -52.7618 | 69.5297 | -53.3936 | 69.278 | 67.0166 | 3.0304 | -5.0858 | -1.7715 | 69.1498 | -53.9291 | -0.073243 | -0.16022 | 0.55847 | 122.5983 | -2.6733 | -0.60883 | -0.54016 | 0.63171 | 48.2346 | 51.5488 | 120.3369 | 122.85 | 0.55847 | 122.4701 | 56.3507 | -0.60883 | 122.85 | 0.55847 | 56.3507 | 120.3369 | 122.4701 | -123.0835 | -123.6191
2719.9062 | 122.905 | -55.4306 | 67.2501 | -0.26291 | 0.0013074 | 0.00067718 | 0.0019781 | -0.0036892 | -0.00050626 | 0.0046933 | -54.5425 | 68.0603 | -54.9545 | 67.3645 | 65.5014 | 2.774 | -5.2368 | -2.1011 | 67.511 | -55.6824 | 0.47607 | 0.81024 | 0.88806 | 122.7951 | -1.7487 | -0.25177 | 0.26093 | 0.41199 | 50.1938 | 53.3295 | 120.932 | 123.4909 | 0.88806 | 122.9416 | 58.2047 | -0.25177 | 123.4909 | 0.88806 | 58.2047 | 120.932 | 122.9416 | -122.2046 | -122.9324
2720.9062 | 122.9324 | -54.7119 | 67.8085 | 1.0036 | 0.0030164 | 0.0021726 | 0.0021917 | -0.0043302 | -0.0015745 | 0.0044797 | -53.9474 | 68.9255 | -54.2175 | 69.9875 | 67.9276 | 3.4882 | -5.3238 | -2.6871 | 68.8934 | -54.5105 | 0.49439 | 1.1169 | 0.76447 | 124.6994 | 0.11902 | 0.20142 | 1.0849 | 0.27008 | 49.3881 | 52.0248 | 122.6395 | 123.6374 | 0.76447 | 123.6053 | 58.2001 | 0.20142 | 123.6374 | 0.76447 | 58.2001 | 122.6395 | 123.6053 | -122.0261 | -122.319
2721.9062 | 122.9187 | -55.1559 | 67.5797 | -0.25528 | 0.0040846 | -0.0027408 | 0.0009101 | -0.0058256 | -0.0032835 | 0.0055479 | -55.1834 | 67.6025 | -55.5038 | 67.8177 | 66.1377 | 3.9185 | -4.9301 | -2.0828 | 67.7582 | -55.3894 | -0.3479 | 0.022888 | -0.027466 | 122.9736 | -1.442 | -0.23346 | 0.17853 | 0.32043 | 50.2258 | 53.0731 | 121.2936 | 122.7585 | -0.027466 | 122.9141 | 59.0744 | -0.23346 | 122.7585 | -0.027466 | 59.0744 | 121.2936 | 122.9141 | -123.0835 | -122.9691
2722.9062 | 122.9233 | -54.4556 | 68.3212 | -0.13321 | 0.0023756 | 0.00046358 | 0.0034735 | -0.0045438 | 0.00013454 | 0.0023435 | -54.4968 | 68.2343 | -54.8355 | 68.3304 | 66.4719 | 3.4195 | -4.422 | -1.7212 | 68.3441 | -54.7852 | -0.37994 | -0.086975 | -0.041199 | 122.7859 | -1.8494 | -0.32959 | 0.022888 | 0.33874 | 50.0336 | 52.7344 | 120.9274 | 122.6898 | -0.041199 | 122.7997 | 57.8751 | -0.32959 | 122.6898 | -0.041199 | 57.8751 | 120.9274 | 122.7997 | -123.1567 | -123.1064
2723.9062 | 122.9187 | -54.8355 | 67.9733 | 0.16434 | 0.004939 | 0.010077 | 0.0043281 | -0.0013394 | -0.00093346 | 0.0027707 | -54.9545 | 67.9916 | -55.1056 | 68.0054 | 66.0919 | 3.2913 | -4.9164 | -1.9455 | 67.8955 | -55.1376 | -0.27008 | 0.01831 | -0.11902 | 122.8409 | -1.8814 | -0.30212 | -0.07782 | 0.15106 | 49.9191 | 52.89 | 120.9274 | 122.8271 | -0.11902 | 122.731 | 58.1268 | -0.30212 | 122.8271 | -0.11902 | 58.1268 | 120.9274 | 122.731 | -123.0789 | -123.111
2724.9062 | 123.024 | -54.7485 | 67.9916 | -0.011139 | 0.00023916 | 0.001318 | -0.0016535 | -0.0030484 | 0.00013454 | 0.0051205 | -54.9683 | 67.7399 | -55.2338 | 68.161 | 66.2704 | 3.891 | -4.9347 | -1.9043 | 67.9184 | -55.0827 | -0.48523 | -0.25177 | -0.21973 | 122.9095 | -1.7212 | -0.33417 | -0.073242 | 0.2655 | 49.8138 | 52.8442 | 121.019 | 122.4884 | -0.21973 | 122.6669 | 58.6395 | -0.33417 | 122.4884 | -0.21973 | 58.6395 | 121.019 | 122.6669 | -123.2254 | -123.0743
2725.9062 | 123.056 | -54.4464 | 68.161 | -0.20187 | 0.00066656 | 0.00024998 | -0.0010125 | -0.00668 | -0.0037107 | 0.0038389 | -54.5288 | 68.0145 | -54.9408 | 68.5135 | 66.3025 | 3.7033 | -4.9255 | -1.8173 | 68.2892 | -54.689 | -0.49439 | -0.14648 | -0.082398 | 122.9599 | -1.8585 | -0.24262 | 0.12817 | 0.41199 | 49.5209 | 52.6291 | 120.7489 | 122.4609 | -0.082398 | 122.7356 | 58.1497 | -0.24262 | 122.4609 | -0.082398 | 58.1497 | 120.7489 | 122.7356 | -123.1018 | -122.85
2726.9062 | 122.9782 | -4.5959 | 118.2678 | -0.095062 | 0.002162 | -0.0018862 | 5.5496e-05 | -0.0068936 | -0.0026425 | 0.016015 | -4.4312 | 118.2495 | -4.9118 | 118.4738 | 115.4388 | 11.911 | 7.9422 | 6.7749 | 118.2495 | -4.8569 | -0.31586 | -0.01831 | 0.16479 | 123.0698 | -2.829 | -0.26093 | -0.01831 | 0.48065 | 12.5381 | 11.3708 | 120.0348 | 122.8455 | 0.16479 | 122.8455 | 16.507 | -0.26093 | 122.8455 | 0.16479 | 16.507 | 120.0348 | 122.8455 | -123.1796 | -123.1247
2727.9062 | 122.9736 | -5.2139 | 117.6682 | -0.18662 | 0.0025892 | 0.00089078 | -0.0003717 | -0.00668 | 0.00056194 | 0.018151 | -5.072 | 117.6315 | -5.5115 | 117.8146 | 114.7888 | 11.5128 | 7.8049 | 6.839 | 117.6086 | -5.5023 | -0.29755 | -0.036621 | 0.14191 | 123.0286 | -2.8793 | -0.28839 | -0.059509 | 0.43945 | 13.0188 | 12.0529 | 120.0027 | 122.8455 | 0.14191 | 122.8226 | 16.7267 | -0.28839 | 122.8455 | 0.14191 | 16.7267 | 120.0027 | 122.8226 | -123.1796 | -123.1705
2728.9062 | 123.0011 | -54.0756 | 68.5226 | -0.17136 | -0.00061524 | 3.6382e-05 | 0.0039007 | -0.0051846 | -0.00029266 | 0.0057615 | -53.9749 | 68.5638 | -54.4327 | 68.9621 | 67.0029 | 3.4927 | -4.866 | -1.5793 | 68.6096 | -54.3869 | -0.35706 | 0.041199 | 0.10071 | 123.0377 | -1.5198 | -0.31128 | 0.086975 | 0.45776 | 49.2096 | 52.4963 | 121.0785 | 122.6395 | 0.10071 | 122.6852 | 57.5684 | -0.31128 | 122.6395 | 0.10071 | 57.5684 | 121.0785 | 122.6852 | -122.9553 | -122.9095
2729.9062 | 123.0286 | -54.0436 | 68.7149 | -0.30106 | -0.001256 | 0.0066586 | 0.0013373 | -0.0051846 | -0.00071986 | 0.0023435 | -54.2404 | 68.4906 | -54.5334 | 68.692 | 66.8289 | 3.8864 | -4.715 | -1.4648 | 68.5867 | -54.3686 | -0.48981 | -0.2243 | -0.19684 | 122.7356 | -1.886 | -0.32501 | -0.12817 | 0.29297 | 49.3286 | 52.5787 | 120.8725 | 122.5342 | -0.19684 | 122.6303 | 57.93 | -0.32501 | 122.5342 | -0.19684 | 57.93 | 120.8725 | 122.6303 | -123.2483 | -123.0835
2730.9062 | 123.0103 | -53.8513 | 68.9346 | -0.16373 | 0.0010938 | -0.0029544 | 0.0053961 | -0.0041166 | -0.0013609 | 0.0023435 | -53.6041 | 69.0628 | -53.9795 | 68.811 | 66.7877 | 4.1931 | -4.8294 | -1.4374 | 68.7332 | -54.2221 | -0.12817 | 0.12817 | 0.24719 | 122.6624 | -2.1469 | -0.37079 | -0.20142 | 0.37537 | 49.0219 | 52.4139 | 120.639 | 122.9141 | 0.24719 | 122.5845 | 58.0444 | -0.37079 | 122.9141 | 0.24719 | 58.0444 | 120.639 | 122.5845 | -122.9141 | -123.1567
2731.9062 | 123.0286 | -53.2654 | 69.4565 | -0.079803 | -0.001897 | -0.0016726 | 0.0004827 | -0.0047574 | -0.00050626 | 0.0057615 | -53.3569 | 69.2871 | -53.6682 | 69.6762 | 67.7628 | 4.1061 | -4.6921 | -1.6205 | 69.4473 | -53.5492 | -0.40283 | -0.16937 | -0.091553 | 122.9416 | -1.6937 | -0.28381 | -0.009155 | 0.31128 | 48.5733 | 51.6449 | 121.0281 | 122.5525 | -0.091553 | 122.7127 | 57.3715 | -0.28381 | 122.5525 | -0.091553 | 57.3715 | 121.0281 | 122.7127 | -123.1247 | -123.0057
2732.9062 | 123.0057 | -54.0985 | 68.6188 | 0.011749 | 0.00088016 | 3.6382e-05 | 0.0006965 | -0.0064664 | -0.0013609 | 0.0042661 | -54.1809 | 68.4814 | -54.5059 | 68.866 | 66.9388 | 3.7903 | -4.9896 | -1.9272 | 68.5135 | -54.4373 | -0.40741 | -0.13733 | -0.082397 | 122.9645 | -1.68 | -0.33874 | -0.10528 | 0.32501 | 49.1089 | 52.1713 | 121.0373 | 122.58 | -0.082397 | 122.612 | 57.8888 | -0.33874 | 122.58 | -0.082397 | 57.8888 | 121.0373 | 122.612 | -123.1247 | -123.056
2733.9062 | 122.8867 | -54.8172 | 68.0008 | -0.17899 | 0.0030164 | -0.0016726 | 0.0062507 | -0.0068936 | 0.00034814 | 0.0036253 | -54.5517 | 68.1747 | -54.9408 | 67.955 | 65.9821 | 3.511 | -4.7058 | -1.7303 | 67.9092 | -55.1468 | -0.1236 | 0.17395 | 0.2655 | 122.7722 | -2.0187 | -0.32959 | -0.091552 | 0.3891 | 50.1114 | 53.0869 | 120.7993 | 122.9919 | 0.2655 | 122.7264 | 58.3282 | -0.32959 | 122.9919 | 0.2655 | 58.3282 | 120.7993 | 122.7264 | -122.9416 | -123.1476
2734.9062 | 123.0698 | -53.8696 | 68.8751 | -0.14084 | -0.001256 | 0.0017454 | -0.0018671 | -0.0056118 | -0.0032835 | 0.0064023 | -53.6911 | 68.898 | -54.071 | 69.3329 | 67.4606 | 3.8589 | -5.0308 | -2.1332 | 68.8614 | -54.1626 | -0.20142 | 0.022888 | 0.17853 | 123.2025 | -1.4145 | -0.29297 | -0.013733 | 0.37994 | 48.8388 | 51.7365 | 121.3303 | 122.7676 | 0.17853 | 122.731 | 57.7286 | -0.29297 | 122.7676 | 0.17853 | 57.7286 | 121.3303 | 122.731 | -122.9462 | -123.0377
2735.9062 | 123.0377 | -53.8742 | 68.8522 | -0.079803 | 0.0017346 | 0.0011044 | -0.0020807 | -0.0086026 | -7.9062e-05 | 0.0031979 | -53.4897 | 69.1772 | -53.8239 | 69.072 | 67.0624 | 3.6987 | -5.127 | -2.1881 | 68.811 | -54.1718 | 0.050354 | 0.32501 | 0.38452 | 122.9462 | -1.7899 | -0.29755 | -0.041199 | 0.33417 | 48.7473 | 51.6861 | 120.9366 | 123.0515 | 0.38452 | 122.6852 | 57.5729 | -0.29755 | 123.0515 | 0.38452 | 57.5729 | 120.9366 | 122.6852 | -122.6761 | -123.024
2736.9062 | 123.024 | -54.0527 | 68.6508 | -0.034027 | 2.5564e-05 | -0.001459 | 0.0006965 | -0.0062528 | -0.00050626 | 0.0034115 | -54.0527 | 68.6737 | -54.3457 | 68.9484 | 66.98 | 3.5431 | -4.9942 | -2.037 | 68.6966 | -54.2999 | -0.29297 | 0.022888 | 0 | 123.0011 | -1.6708 | -0.24719 | 0.045776 | 0.29297 | 49.0585 | 52.0157 | 121.0327 | 122.7264 | 0 | 122.7493 | 57.5958 | -0.24719 | 122.7264 | 0 | 57.5958 | 121.0327 | 122.7493 | -122.9965 | -122.9507
2737.9062 | 123.0103 | -54.2862 | 68.3716 | -0.011139 | 0.00066656 | 0.0023862 | 0.0002691 | -0.0060392 | 0.00077554 | 0.0038389 | -54.3549 | 68.3899 | -54.6387 | 68.7286 | 66.7191 | 3.5294 | -5.3055 | -2.2339 | 68.4036 | -54.5654 | -0.35248 | 0.018311 | -0.068664 | 123.0148 | -1.6525 | -0.27924 | 0.032043 | 0.28381 | 48.9807 | 52.0523 | 121.0052 | 122.6761 | -0.068664 | 122.6898 | 57.8156 | -0.27924 | 122.6761 | -0.068664 | 57.8156 | 121.0052 | 122.6898 | -123.0103 | -122.937
2738.9219 | 122.9324 | -54.5517 | 68.161 | -0.17899 | 0.0023756 | 0.0017454 | 0.0077459 | -0.00668 | -0.00093346 | 0.0046933 | -54.2908 | 68.4036 | -54.689 | 68.3533 | 66.4169 | 3.5843 | -4.9164 | -1.9867 | 68.4174 | -54.6616 | -0.13733 | 0.24261 | 0.26093 | 122.905 | -1.7441 | -0.10986 | 0.25635 | 0.39825 | 49.6353 | 52.565 | 120.9686 | 122.9553 | 0.26093 | 122.9691 | 58.136 | -0.10986 | 122.9553 | 0.26093 | 58.136 | 120.9686 | 122.9691 | -122.85 | -122.8226
2739.9062 | 122.9691 | -53.3478 | 69.2917 | 0.11093 | 0.0017346 | 0.00067718 | -0.0005853 | -0.0062528 | -0.0013609 | 0.0053343 | -53.5583 | 69.072 | -53.9062 | 69.2368 | 67.3141 | 4.0924 | -4.7836 | -1.9135 | 69.3329 | -53.6499 | -0.55847 | -0.21973 | -0.21057 | 122.5845 | -1.9775 | -0.30212 | 0.041199 | 0.3479 | 48.5641 | 51.4343 | 120.6619 | 122.4197 | -0.21057 | 122.6807 | 57.4402 | -0.30212 | 122.4197 | -0.21057 | 57.4402 | 120.6619 | 122.6807 | -123.1979 | -122.9416
2740.9062 | 123.0057 | -54.158 | 68.5455 | 0.088043 | 0.0017346 | -0.00060462 | 0.0015509 | -0.00668 | -0.0034971 | 0.0029843 | -54.3091 | 68.4128 | -54.6021 | 68.9026 | 66.9479 | 3.685 | -4.9759 | -2.1332 | 68.6371 | -54.3961 | -0.44403 | -0.13275 | -0.15106 | 123.0606 | -1.5976 | -0.23804 | 0.091553 | 0.29297 | 49.1821 | 52.0248 | 121.106 | 122.5708 | -0.15106 | 122.7951 | 57.843 | -0.23804 | 122.5708 | -0.15106 | 57.843 | 121.106 | 122.7951 | -123.1476 | -122.9416
2741.9062 | 122.9691 | -53.5904 | 69.0903 | 0.042267 | 0.0010938 | 3.6382e-05 | 0.0002691 | -0.0073208 | -0.00050626 | 0.0038389 | -53.2013 | 69.6213 | -53.508 | 69.1772 | 67.4332 | 3.923 | -4.6463 | -1.8173 | 69.1635 | -53.7964 | 0.082397 | 0.53101 | 0.3891 | 122.7676 | -1.6571 | -0.20599 | 0.073242 | 0.3067 | 48.9441 | 51.7731 | 121.0236 | 123.2117 | 0.3891 | 122.7539 | 57.5134 | -0.20599 | 123.2117 | 0.3891 | 57.5134 | 121.0236 | 122.7539 | -122.5983 | -122.8867
2742.9062 | 123.0057 | -52.3453 | 70.3766 | 0.29404 | -0.0010424 | 3.6382e-05 | 0.0009101 | -0.0068936 | 0.00098914 | 0.0025571 | -52.4643 | 70.2072 | -52.7985 | 70.4132 | 68.5364 | 4.2709 | -4.335 | -1.5518 | 70.285 | -52.652 | -0.45319 | -0.16937 | -0.11902 | 122.7585 | -1.8402 | -0.3067 | -0.091553 | 0.33417 | 48.0103 | 50.7935 | 120.8817 | 122.5525 | -0.11902 | 122.6303 | 56.6162 | -0.3067 | 122.5525 | -0.11902 | 56.6162 | 120.8817 | 122.6303 | -123.175 | -123.0286
2743.9062 | 122.9324 | -54.3732 | 68.3487 | -0.14847 | 0.0013074 | 0.0049496 | 0.0047553 | -0.0053982 | -0.0030697 | 0.0023435 | -54.7165 | 68.1107 | -55.0049 | 68.3716 | 66.5955 | 3.9642 | -4.6417 | -1.8997 | 68.3762 | -54.6478 | -0.63171 | -0.23804 | -0.34332 | 122.7448 | -1.7532 | -0.27466 | 0.027466 | 0.28839 | 49.7314 | 52.4734 | 120.9686 | 122.4838 | -0.34332 | 122.7493 | 58.3374 | -0.27466 | 122.4838 | -0.34332 | 58.3374 | 120.9686 | 122.7493 | -123.3536 | -122.9965
2744.9062 | 123.0057 | -54.6478 | 68.0237 | 0.072784 | 0.00045296 | 0.0028134 | 5.5496e-05 | -0.0058256 | 0.00034814 | 0.0053343 | -54.538 | 68.129 | -54.8492 | 68.367 | 66.5176 | 3.8269 | -4.953 | -2.1927 | 68.0557 | -54.9179 | -0.20142 | 0.10529 | 0.10986 | 123.0148 | -1.506 | -0.27008 | 0.032043 | 0.31128 | 49.6948 | 52.4551 | 121.1655 | 122.7768 | 0.10986 | 122.7036 | 58.4747 | -0.27008 | 122.7768 | 0.10986 | 58.4747 | 121.1655 | 122.7036 | -122.8729 | -122.9416
2745.9062 | 123.0103 | -55.4626 | 67.218 | 0.17197 | 0.00045296 | 0.00067718 | 0.0019781 | -0.0056118 | 0.00098914 | 0.0044797 | -55.4123 | 67.2043 | -55.7693 | 67.4652 | 65.5838 | 3.4698 | -5.2505 | -2.3849 | 67.1677 | -55.7693 | -0.3067 | -0.013733 | 0.050354 | 122.9279 | -1.6342 | -0.3067 | -0.050354 | 0.35706 | 50.2121 | 53.0777 | 121.0464 | 122.6669 | 0.050354 | 122.6303 | 58.9325 | -0.3067 | 122.6669 | 0.050354 | 58.9325 | 121.0464 | 122.6303 | -122.9874 | -122.9874
2746.9062 | 122.9599 | -54.1946 | 68.5684 | 0.15671 | 0.00045296 | 0.0032406 | 0.0019781 | -0.0075344 | -0.00071986 | 0.0027707 | -54.1397 | 68.5822 | -54.4693 | 68.7149 | 66.8198 | 3.6942 | -4.6051 | -2.1286 | 68.4677 | -54.5242 | -0.27466 | 0.013733 | 0.054932 | 122.9095 | -1.7487 | -0.32959 | -0.10071 | 0.32959 | 49.5895 | 52.066 | 121.0144 | 122.7768 | 0.054932 | 122.6624 | 57.8888 | -0.32959 | 122.7768 | 0.054932 | 57.8888 | 121.0144 | 122.6624 | -123.0377 | -123.0927
2747.9062 | 123.0286 | -53.7552 | 68.9941 | 0.12619 | 0.0010938 | 0.0011044 | 0.0004827 | -0.0056118 | 0.00056194 | 0.0042661 | -54.277 | 68.2114 | -54.6844 | 68.9987 | 66.9891 | 3.6118 | -4.9896 | -2.1103 | 68.7057 | -54.1351 | -0.92926 | -0.78278 | -0.52185 | 122.7539 | -2.005 | -0.37994 | -0.28839 | 0.40741 | 48.7656 | 51.6449 | 120.7443 | 121.9666 | -0.52185 | 122.4609 | 57.3669 | -0.37994 | 121.9666 | -0.52185 | 57.3669 | 120.7443 | 122.4609 | -123.6786 | -123.1293
2748.9219 | 122.9416 | -53.2608 | 69.4565 | -0.26291 | 0.00088016 | 0.0028134 | 0.0043281 | -0.0081754 | -0.0013609 | 0.0049069 | -52.9724 | 69.635 | -53.3707 | 69.7495 | 67.6895 | 3.6163 | -4.4403 | -2.092 | 69.5023 | -53.54 | -0.10986 | 0.17853 | 0.28839 | 123.0103 | -1.767 | -0.27924 | 0.045776 | 0.39825 | 48.8205 | 51.1688 | 120.9503 | 122.8958 | 0.28839 | 122.7631 | 56.8771 | -0.27924 | 122.8958 | 0.28839 | 56.8771 | 120.9503 | 122.7631 | -122.8271 | -122.9965
2749.9062 | 123.0057 | -54.4922 | 68.2892 | 0.11093 | 0.00088016 | 0.00046358 | 0.0015509 | -0.0060392 | -0.00071986 | 0.0085385 | -54.3274 | 68.3807 | -54.6249 | 68.3533 | 66.4169 | 3.5019 | -5.0995 | -2.4445 | 68.0008 | -54.9088 | -0.13275 | 0.091552 | 0.16479 | 122.8455 | -1.8723 | -0.41656 | -0.28839 | 0.29755 | 49.3927 | 52.0477 | 120.9091 | 122.8729 | 0.16479 | 122.493 | 57.9941 | -0.41656 | 122.8729 | 0.16479 | 57.9941 | 120.9091 | 122.493 | -122.9141 | -123.1979
2750.9062 | 123.0148 | -53.4027 | 69.3054 | 0.19485 | 0.0013074 | 0.0028134 | 0.0002691 | -0.0051846 | -0.0030697 | 0.0042661 | -54.3686 | 68.5684 | -54.4647 | 69.1727 | 67.2867 | 4.1428 | -4.1199 | -1.6067 | 69.1132 | -53.7964 | -1.062 | -0.737 | -0.96588 | 122.5754 | -2.0187 | -0.39368 | -0.19226 | 0.096131 | 49.2828 | 51.796 | 120.6894 | 121.9711 | -0.96588 | 122.5159 | 57.5455 | -0.39368 | 121.9711 | -0.96588 | 57.5455 | 120.6894 | 122.5159 | -123.7701 | -123.1018
2751.9062 | 122.9645 | -52.7802 | 70.0333 | 0.16434 | 0.0028028 | 0.0032406 | 0.0024053 | -0.0075344 | -0.0011471 | 0.0046933 | -53.7048 | 68.7057 | -54.1168 | 69.722 | 67.8497 | 4.2801 | -4.5044 | -1.5701 | 69.4885 | -53.3615 | -1.3367 | -1.3275 | -0.92468 | 122.5021 | -2.1835 | -0.58136 | -0.54474 | 0.41199 | 48.2758 | 51.21 | 120.6299 | 121.4859 | -0.92468 | 122.2687 | 57.0602 | -0.58136 | 121.4859 | -0.92468 | 57.0602 | 120.6299 | 122.2687 | -124.1501 | -123.3948
2752.9062 | 123.0377 | -53.0319 | 69.6625 | 0.17197 | 0.0017346 | -0.00039102 | 0.0041143 | -0.0053982 | -0.00050626 | 0.0051205 | -52.7161 | 69.6533 | -53.2654 | 70.0104 | 68.1335 | 4.0054 | -4.8294 | -2.0233 | 69.7037 | -53.2928 | -0.23346 | -0.009156 | 0.31586 | 123.0423 | -1.5289 | -0.26093 | 0.041198 | 0.54932 | 48.2025 | 51.0086 | 121.1655 | 122.6852 | 0.31586 | 122.7356 | 57.0374 | -0.26093 | 122.6852 | 0.31586 | 57.0374 | 121.1655 | 122.7356 | -122.9279 | -122.9553
2753.9062 | 123.0194 | -54.2084 | 68.5043 | 0.19485 | 0.00088016 | 0.00067718 | 0.0047553 | -0.0064664 | 0.00013454 | 0.0081113 | -53.4027 | 69.2734 | -53.7323 | 68.7332 | 66.6595 | 3.6621 | -5.072 | -2.2202 | 68.5272 | -54.4693 | 0.47607 | 0.76904 | 0.80566 | 122.9416 | -1.8448 | -0.26093 | 0.022889 | 0.32959 | 49.1364 | 51.9882 | 120.8679 | 123.4818 | 0.80566 | 122.7356 | 57.8705 | -0.26093 | 123.4818 | 0.80566 | 57.8705 | 120.8679 | 122.7356 | -122.2366 | -122.9736
2754.9062 | 123.0515 | -53.6636 | 69.0399 | 0.41611 | 0.0017346 | 0.0015316 | 0.0036871 | -0.0053982 | -0.0011471 | 0.0055479 | -53.3981 | 69.4016 | -53.6682 | 69.1132 | 67.1494 | 3.9322 | -4.6738 | -1.9455 | 68.9804 | -53.9886 | -0.004578 | 0.36163 | 0.2655 | 122.7768 | -1.8906 | -0.32501 | -0.059509 | 0.27008 | 48.9899 | 51.7181 | 120.813 | 123.0652 | 0.2655 | 122.644 | 57.5958 | -0.32501 | 123.0652 | 0.2655 | 57.5958 | 120.813 | 122.644 | -122.7081 | -123.0286
2755.9062 | 122.9919 | -54.4693 | 68.2617 | 0.1796 | 0.002162 | 0.0038816 | 0.0045417 | -0.0056118 | 0.00034814 | 0.0044797 | -54.4144 | 68.2251 | -54.7668 | 68.3304 | 66.5909 | 3.9459 | -4.9255 | -2.298 | 68.161 | -54.776 | -0.29755 | -0.036621 | 0.054931 | 122.7997 | -1.6708 | -0.3067 | -0.10071 | 0.35248 | 49.5438 | 52.1713 | 121.0602 | 122.6944 | 0.054931 | 122.6303 | 58.4152 | -0.3067 | 122.6944 | 0.054931 | 58.4152 | 121.0602 | 122.6303 | -123.0286 | -123.0377
2756.9062 | 123.0057 | -53.833 | 68.8568 | 0.042267 | -0.001897 | -0.0023136 | -0.0003717 | -0.0068936 | -0.00093346 | 0.0057615 | -53.8147 | 68.8522 | -54.1946 | 69.104 | 67.186 | 3.8223 | -4.8889 | -2.0737 | 68.898 | -54.1168 | -0.36163 | -0.004578 | 0.018311 | 122.937 | -1.6708 | -0.28381 | 0.041198 | 0.37994 | 48.9441 | 51.7593 | 121.019 | 122.6852 | 0.018311 | 122.731 | 57.6553 | -0.28381 | 122.6852 | 0.018311 | 57.6553 | 121.019 | 122.731 | -123.0515 | -122.9736
2757.9062 | 123.0148 | -53.5172 | 69.2093 | -0.14084 | 0.0013074 | 0.001318 | 0.0051825 | -0.00668 | -0.00093346 | 0.0061887 | -53.5858 | 68.9896 | -53.9886 | 69.4199 | 67.4515 | 3.7491 | -4.5502 | -2.2018 | 69.1727 | -53.7735 | -0.4715 | -0.21973 | -0.068664 | 122.937 | -1.7578 | -0.25635 | -0.036622 | 0.40283 | 48.967 | 51.3153 | 120.9686 | 122.5067 | -0.068664 | 122.6898 | 57.2662 | -0.25635 | 122.5067 | -0.068664 | 57.2662 | 120.9686 | 122.6898 | -123.1979 | -122.9828
2758.9062 | 122.9782 | -53.7231 | 69.0445 | -0.17136 | 2.5564e-05 | 0.001318 | 0.0030463 | -0.0056118 | -0.00071986 | 0.0038389 | -53.8513 | 68.8293 | -54.1763 | 69.136 | 67.1814 | 3.6621 | -4.9347 | -2.2156 | 68.8705 | -54.0665 | -0.45319 | -0.21515 | -0.12817 | 122.8592 | -1.8631 | -0.34332 | -0.17395 | 0.32501 | 48.7885 | 51.5076 | 120.9045 | 122.5525 | -0.12817 | 122.5937 | 57.3853 | -0.34332 | 122.5525 | -0.12817 | 57.3853 | 120.9045 | 122.5937 | -123.2208 | -123.111
2759.9219 | 122.8775 | -53.3798 | 69.2413 | -0.14084 | 0.002162 | 0.00024998 | 0.0045417 | -0.0062528 | -0.0011471 | 0.0074705 | -51.9287 | 71.2646 | -51.9379 | 69.1406 | 67.0029 | 3.0258 | -4.6371 | -2.2385 | 69.1864 | -53.7277 | 1.442 | 2.0233 | 1.4511 | 122.5204 | -2.2385 | -0.3479 | -0.054932 | 0.009155 | 48.7427 | 51.1414 | 120.3827 | 124.6445 | 1.4511 | 122.5662 | 56.4056 | -0.3479 | 124.6445 | 1.4511 | 56.4056 | 120.3827 | 122.5662 | -121.1792 | -122.9691
2760.9062 | 123.0057 | -53.0502 | 69.5023 | 0.080414 | 0.0023756 | 0.0072996 | 0.0053961 | -0.0036892 | -0.00029266 | 0.0064023 | -52.7802 | 69.9371 | -53.1464 | 69.8318 | 67.923 | 4.0375 | -4.4174 | -2.1103 | 69.8181 | -53.183 | -0.09613 | 0.43488 | 0.27008 | 122.8821 | -1.5793 | -0.13275 | 0.31586 | 0.36621 | 48.6328 | 50.9399 | 120.9732 | 122.9874 | 0.27008 | 122.8683 | 57.0877 | -0.13275 | 122.9874 | 0.27008 | 57.0877 | 120.9732 | 122.8683 | -122.6486 | -122.6852
2761.9062 | 116.2949 | -32.6981 | 83.2901 | 0.24063 | 0.0010938 | 0.0062314 | 6.9253 | -0.00069859 | -0.0073423 | 7.0079 | -32.7393 | 83.2718 | -33.1009 | 53.4988 | 65.8951 | 40.3748 | 46.3623 | 12.5793 | 65.2725 | -15.0467 | -0.40283 | -0.01831 | -0.041199 | 86.1969 | -17.395 | 17.6514 | -18.0176 | 0.36163 | 79.0604 | 45.2774 | 98.5931 | 115.9698 | -0.041199 | 97.9706 | 73.0728 | 17.6514 | 115.9698 | -0.041199 | 73.0728 | 98.5931 | 97.9706 | -116.391 | -98.3368
2762.9062 | 122.1039 | -4.6371 | 117.1326 | 0.24063 | 0.0038708 | 0.0023862 | 0.031672 | -0.001553 | 0.00077554 | 0.046991 | -4.5593 | 117.572 | -4.9942 | 117.7368 | 113.1409 | 14.8224 | 116.4551 | 17.07 | 117.3935 | -5.0125 | -0.35706 | 0.43945 | 0.07782 | 122.374 | -3.9917 | -0.37537 | 0.26093 | 0.43488 | 121.0922 | 21.7072 | 117.778 | 122.2092 | 0.07782 | 122.0306 | 19.4595 | -0.37537 | 122.2092 | 0.07782 | 19.4595 | 117.778 | 122.0306 | -122.1268 | -122.1451
2763.9062 | 122.4426 | -4.2343 | 117.9657 | 0.21011 | 0.0013074 | -0.0033816 | 0.0062507 | -0.0043302 | 0.050336 | 0.070916 | -4.1016 | 118.0893 | -4.5547 | 118.2449 | 24.6872 | 9.3979 | 117.4576 | 18.0176 | 117.9932 | -4.5181 | -0.32043 | 0.1236 | 0.13275 | 122.4792 | -93.2785 | -0.28381 | 0.027466 | 0.45319 | 121.6919 | 22.2519 | 28.9215 | 122.3236 | 0.13275 | 122.2275 | 13.6322 | -0.28381 | 122.3236 | 0.13275 | 13.6322 | 28.9215 | 122.2275 | -122.5204 | -122.4838
2764.9219 | 121.9849 | -8.6655 | 113.7222 | -0.24002 | 0.0028028 | -0.00039102 | 0.027826 | -0.0075344 | 0.054609 | 0.088006 | -8.4824 | 113.8641 | -8.8257 | 113.8733 | 9.6725 | -2.7512 | 113.1775 | 15.1199 | 113.6856 | -8.9264 | -0.16022 | 0.14191 | 0.18311 | 122.5388 | -104.0497 | -0.26093 | -0.036621 | 0.34332 | 121.843 | 23.7854 | 18.338 | 122.5296 | 0.18311 | 122.3511 | 5.9143 | -0.26093 | 122.5296 | 0.18311 | 5.9143 | 18.338 | 122.3511 | -122.5479 | -122.6486
2765.9062 | 122.5159 | -6.514 | 115.9332 | 0.28641 | 0.0055798 | 0.0038816 | 0.012018 | -0.0043302 | 0.056318 | 0.078393 | -6.4499 | 115.8279 | -6.958 | 116.011 | 9.7504 | -2.3941 | 115.0864 | 18.1046 | 115.8554 | -6.7932 | -0.44403 | -0.10529 | 0.064087 | 122.525 | -106.1829 | -0.27924 | -0.07782 | 0.50812 | 121.6003 | 24.6185 | 16.2643 | 122.3419 | 0.064087 | 122.3694 | 4.1199 | -0.27924 | 122.3419 | 0.064087 | 4.1199 | 16.2643 | 122.3694 | -122.8912 | -122.7264
2766.9062 | 122.5067 | -4.509 | 118.0206 | 0.034637 | 0.0042982 | 0.001318 | 0.010096 | -0.0026212 | -0.00071986 | 0.019647 | -4.3442 | 118.1351 | -4.7653 | 118.0847 | 116.0431 | 116.2033 | 117.3065 | 22.2931 | 118.0069 | -4.7653 | -0.25635 | 0.11444 | 0.16479 | 122.5937 | -1.9775 | -0.25635 | -0.013733 | 0.42114 | 121.8155 | 26.8021 | 120.5521 | 122.644 | 0.16479 | 122.5159 | 120.7123 | -0.25635 | 122.644 | 0.16479 | 120.7123 | 120.5521 | 122.5159 | -122.7859 | -122.7859
2767.9062 | 122.5616 | -4.0695 | 118.4235 | 0.17197 | 0.006648 | 0.0077268 | 0.011805 | -0.0041166 | -0.0024289 | 0.021569 | -3.9185 | 118.5242 | -4.3396 | 118.5745 | 116.9174 | 117.1051 | 117.7689 | 22.261 | 118.4189 | -4.335 | -0.27008 | 0.10071 | 0.15106 | 122.644 | -1.506 | -0.2655 | -0.004578 | 0.42114 | 121.8384 | 26.3306 | 120.9869 | 122.5937 | 0.15106 | 122.4884 | 121.1746 | -0.2655 | 122.5937 | 0.15106 | 121.1746 | 120.9869 | 122.4884 | -122.7631 | -122.7585
2768.9062 | 122.6212 | -3.7674 | 118.6752 | 0.019379 | 0.001521 | -0.0029544 | 0.0049689 | -0.0045438 | -0.00093346 | 0.021783 | -3.6575 | 118.7393 | -4.0878 | 118.8766 | 116.2308 | 117.4255 | 117.9428 | 58.9966 | 118.6798 | -4.0054 | -0.32044 | 0.064087 | 0.10986 | 122.644 | -2.4445 | -0.23804 | 0.004578 | 0.4303 | 121.7102 | 62.764 | 119.9982 | 122.5067 | 0.10986 | 122.4472 | 121.1929 | -0.23804 | 122.5067 | 0.10986 | 121.1929 | 119.9982 | 122.4472 | -122.7631 | -122.6807
2769.9219 | 122.6578 | -4.6921 | 117.7917 | -0.026398 | -0.00061524 | -0.00081822 | 0.0032599 | -0.0045438 | -0.0020017 | 0.019647 | -4.6005 | 117.7963 | -5.0079 | 117.9977 | 116.5558 | 116.7572 | 117.0227 | 23.584 | 117.7505 | -4.9759 | -0.31586 | 0.004578 | 0.091553 | 122.6898 | -1.236 | -0.28381 | -0.041199 | 0.40741 | 121.7148 | 28.2761 | 121.2479 | 122.4884 | 0.091553 | 122.4426 | 121.4493 | -0.28381 | 122.4884 | 0.091553 | 121.4493 | 121.2479 | 122.4426 | -122.7997 | -122.7676
2770.9062 | 122.644 | -5.9235 | 116.5787 | 0.22537 | 0.0064344 | 0.004736 | 0.013086 | -0.0056118 | -0.0028561 | 0.01922 | -5.7861 | 116.6519 | -6.2393 | 116.7755 | 115.5807 | 115.8325 | 115.8325 | 23.3917 | 116.5558 | -6.2027 | -0.31586 | 0.073243 | 0.13733 | 122.699 | -0.99792 | -0.27924 | -0.022888 | 0.45319 | 121.756 | 29.3152 | 121.5042 | 122.5754 | 0.13733 | 122.4792 | 121.756 | -0.27924 | 122.5754 | 0.13733 | 121.756 | 121.5042 | 122.4792 | -122.818 | -122.7814
2771.9062 | 122.6212 | -7.251 | 115.3336 | 0.1796 | 0.0040846 | 0.005377 | 0.0079595 | -0.0043302 | -0.0013609 | 0.020501 | -7.0221 | 115.4938 | -7.4387 | 115.4434 | 114.2075 | 114.7888 | 114.5874 | 23.2452 | 115.2832 | -7.4844 | -0.18768 | 0.16022 | 0.22888 | 122.6944 | -1.1261 | -0.23346 | -0.050354 | 0.41656 | 121.8384 | 30.4962 | 121.4584 | 122.7448 | 0.22888 | 122.5342 | 122.0398 | -0.23346 | 122.7448 | 0.22888 | 122.0398 | 121.4584 | 122.5342 | -122.7722 | -122.818
2772.9062 | 121.8521 | -4.3442 | 118.2724 | 0.13382 | 0.0051526 | 0.006445 | 0.011591 | -0.0026212 | 0.0016299 | 0.024774 | -4.1794 | 118.3548 | -4.6326 | 118.2907 | 115.3107 | 117.7505 | 117.4805 | 30.3818 | 118.2449 | -4.5776 | -0.28839 | 0.082397 | 0.16479 | 122.6349 | -2.9617 | -0.23346 | -0.027466 | 0.45319 | 121.8246 | 34.726 | 119.6548 | 122.699 | 0.16479 | 122.5891 | 122.0947 | -0.23346 | 122.699 | 0.16479 | 122.0947 | 119.6548 | 122.5891 | -122.905 | -122.85
2773.9062 | 122.6944 | -5.5939 | 116.8945 | 0.18723 | 0.0013074 | 0.0043088 | 0.0045417 | -0.0026212 | 0.00034814 | 0.021356 | -5.4932 | 116.922 | -5.896 | 117.1143 | 113.9923 | 116.4551 | 116.1758 | 26.5366 | 116.8762 | -5.8777 | -0.30212 | 0.027466 | 0.10071 | 122.7081 | -2.9022 | -0.28381 | -0.01831 | 0.40283 | 121.7697 | 32.1304 | 119.5862 | 122.5159 | 0.10071 | 122.4701 | 122.049 | -0.28381 | 122.5159 | 0.10071 | 122.049 | 119.5862 | 122.4701 | -122.7905 | -122.7722
2774.9062 | 122.5479 | -5.0949 | 117.3752 | -0.36972 | 0.0072888 | 0.003027 | 0.012232 | -0.0041166 | 0.00034814 | 0.020074 | -4.9805 | 117.6407 | -5.365 | 117.5995 | 114.4135 | 116.8442 | 116.8945 | 21.8994 | 117.4942 | -5.3741 | -0.27008 | 0.2655 | 0.11444 | 122.6944 | -2.9617 | -0.27924 | 0.11902 | 0.38452 | 121.9894 | 26.9943 | 119.5084 | 122.7356 | 0.11444 | 122.5891 | 121.9391 | -0.27924 | 122.7356 | 0.11444 | 121.9391 | 119.5084 | 122.5891 | -122.7402 | -122.7493
2775.9062 | 122.6669 | -72.7524 | 49.4431 | 0.15671 | 0.0028028 | 0.0045224 | 0.010737 | -0.0013394 | -0.00050626 | 0.0017027 | -72.908 | 49.617 | -73.4344 | 49.6582 | 48.6053 | 49.8367 | 48.8846 | -2.9938 | 49.8138 | -72.963 | -0.68207 | 0.17395 | -0.15564 | 122.4106 | -0.83771 | -0.21057 | 0.37079 | 0.52643 | 121.637 | 69.7586 | 121.3577 | 122.3694 | -0.15564 | 122.5662 | 122.5891 | -0.21057 | 122.3694 | -0.15564 | 122.5891 | 121.3577 | 122.5662 | -122.8775 | -122.406
2776.9062 | 101.9531 | -97.1283 | 25.2777 | 0.1796 | 0.0034436 | 0.0051632 | 0.018854 | -0.0024076 | -0.0030697 | 0.0029843 | -97.6822 | 24.5773 | -98.2681 | 24.4446 | 24.147 | 24.5178 | 23.6343 | -9.5398 | 25.5295 | -96.8628 | -1.1398 | -0.70038 | -0.55389 | 121.5729 | -1.1307 | 0.2655 | 0.25177 | 0.58594 | 120.7626 | 87.5885 | 121.2753 | 121.7056 | -0.55389 | 122.6578 | 121.6461 | 0.2655 | 121.7056 | -0.55389 | 121.6461 | 121.2753 | 122.6578 | -123.5458 | -122.1405
2777.9062 | 122.6303 | -98.671 | 23.703 | -0.50705 | 0.00323 | 0.0021726 | 0.019922 | -0.0011258 | -0.0013609 | 0.0076841 | -98.6572 | 23.5062 | -99.2661 | 23.5199 | 22.6685 | 23.4741 | 22.2153 | -15.6235 | 23.7671 | -99.0326 | -0.59509 | -0.19684 | 0.013732 | 122.1909 | -1.0345 | -0.36163 | 0.064087 | 0.60882 | 120.8862 | 83.0475 | 121.3394 | 122.1771 | 0.013732 | 122.438 | 122.1451 | -0.36163 | 122.1771 | 0.013732 | 122.1451 | 121.3394 | 122.438 | -122.9691 | -122.7356
2778.9062 | 122.7539 | -61.322 | 60.4523 | 0.15671 | 0.00088016 | 0.003027 | 0.0002691 | -0.0019802 | -0.0017881 | 0.0042661 | -61.9492 | 60.347 | -62.3978 | 61.4273 | 59.4131 | 60.1822 | 59.903 | 0.80566 | 60.6628 | -61.8164 | -1.0757 | -0.10529 | -0.62714 | 122.7493 | -1.0391 | -0.49439 | 0.21057 | 0.44861 | 121.225 | 62.1277 | 120.7352 | 121.669 | -0.62714 | 121.9849 | 121.5042 | -0.49439 | 121.669 | -0.62714 | 121.5042 | 120.7352 | 121.9849 | -122.85 | -122.2687
2779.9062 | 122.6349 | -63.7161 | 57.811 | 0.027008 | 0.0079298 | 0.010077 | 0.0090277 | -0.002194 | 0.00056194 | 0.0057615 | -62.8693 | 59.1156 | -63.5056 | 59.3216 | 57.4677 | 58.4564 | 58.4335 | -1.7441 | 58.8501 | -64.0594 | 0.21057 | 1.3046 | 0.84686 | 123.0377 | -0.34332 | -0.34332 | 1.0391 | 0.63629 | 122.1497 | 61.972 | 121.1838 | 122.8317 | 0.84686 | 122.5662 | 122.1725 | -0.34332 | 122.8317 | 0.84686 | 122.1725 | 121.1838 | 122.5662 | -121.3165 | -121.8704
2780.9062 | 122.644 | -61.4914 | 60.965 | -0.14084 | 0.0060072 | 0.0060178 | 0.0079595 | -0.0030484 | -0.00050626 | 0.0044797 | -61.3129 | 61.1206 | -61.8851 | 60.4294 | 59.2667 | 60.7224 | 60.4614 | 1.149 | 60.6857 | -62.1552 | -0.39368 | 0.15564 | 0.17853 | 121.9208 | -1.6983 | -0.66376 | -0.27924 | 0.57221 | 121.9528 | 62.6404 | 120.7581 | 122.612 | 0.17853 | 122.1771 | 122.2137 | -0.66376 | 122.612 | 0.17853 | 122.2137 | 120.7581 | 122.1771 | -122.85 | -123.1201
2781.9062 | 122.6349 | -58.7357 | 63.7207 | 0.12619 | 0.0055798 | 0.004736 | 0.0058233 | 0.00058321 | -0.0011471 | 0.0029843 | -58.8226 | 63.7985 | -59.166 | 63.858 | 61.9858 | 63.4048 | 63.3499 | 2.4948 | 63.7253 | -59.1064 | -0.4303 | 0.07782 | -0.086975 | 122.5937 | -1.7349 | -0.37079 | 0.004578 | 0.34332 | 122.0856 | 61.2305 | 120.7214 | 122.5342 | -0.086975 | 122.4609 | 122.1405 | -0.37079 | 122.5342 | -0.086975 | 122.1405 | 120.7214 | 122.4609 | -122.8867 | -122.8271
2782.9062 | 122.7402 | -56.488 | 66.0324 | 0.088043 | 0.0064344 | 0.0062314 | 0.0066779 | -0.0019802 | -0.0030697 | 0.0031979 | -57.1198 | 65.1627 | -57.6874 | 65.126 | 63.1897 | 64.6271 | 64.5538 | 3.1174 | 65.1672 | -57.4951 | -1.1993 | -0.86975 | -0.63171 | 121.6141 | -2.8427 | -1.0071 | -0.86517 | 0.56763 | 121.0419 | 59.6054 | 119.6777 | 121.6507 | -0.63171 | 121.6553 | 121.1151 | -1.0071 | 121.6507 | -0.63171 | 121.1151 | 119.6777 | 121.6553 | -123.7198 | -123.5275
2783.9062 | 122.6166 | -61.6196 | 60.5347 | 0.11856 | 0.0055798 | 0.0055906 | 0.0053961 | -0.00069859 | -7.9062e-05 | 0.0027707 | -60.8917 | 61.2488 | -61.3083 | 60.6125 | 58.8913 | 60.5713 | 60.759 | 2.5085 | 61.0519 | -61.7706 | 0.31128 | 0.71411 | 0.72784 | 122.2321 | -1.6434 | -0.15106 | 0.51727 | 0.41656 | 122.3785 | 64.1281 | 120.5109 | 122.8683 | 0.72784 | 122.6715 | 122.1909 | -0.15106 | 122.8683 | 0.72784 | 122.1909 | 120.5109 | 122.6715 | -121.843 | -122.3053
2784.9062 | 122.6486 | -58.6853 | 63.7894 | 0.088043 | 0.0040846 | 0.0055906 | 0.0066779 | -0.00048499 | -7.9062e-05 | 0.0034115 | -58.3603 | 64.0182 | -58.8867 | 64.1144 | 62.3062 | 63.4872 | 63.4644 | 2.9709 | 63.8809 | -59.0149 | -0.20142 | 0.22888 | 0.32501 | 122.7997 | -1.4832 | -0.32959 | 0.091552 | 0.52643 | 122.1497 | 61.6562 | 120.9915 | 122.7036 | 0.32501 | 122.5662 | 122.1725 | -0.32959 | 122.7036 | 0.32501 | 122.1725 | 120.9915 | 122.5662 | -122.6761 | -122.8043
2785.9062 | 122.6303 | -64.4028 | 58.1726 | 0.11856 | 0.0045118 | 0.0072996 | 0.0064643 | -0.001553 | -0.00029266 | 0.0049069 | -63.4415 | 59.0469 | -63.826 | 58.8776 | 56.7764 | 57.7927 | 57.6004 | 2.0828 | 58.1772 | -64.769 | 0.57678 | 0.87433 | 0.9613 | 123.2803 | -1.3962 | -0.36621 | 0.004578 | 0.38452 | 122.0032 | 66.4856 | 121.1792 | 123.4497 | 0.9613 | 122.58 | 122.1954 | -0.36621 | 123.4497 | 0.9613 | 122.1954 | 121.1792 | 122.58 | -121.9986 | -122.9416
2786.9062 | 122.6349 | -64.8926 | 57.6553 | -0.095062 | 0.0042982 | 0.008154 | 0.0058233 | -0.001553 | -0.0024289 | 0.0029843 | -64.9841 | 57.4265 | -65.5334 | 57.5272 | 56.0486 | 57.1884 | 57.225 | 1.9089 | 57.5317 | -65.2954 | -0.64087 | -0.22888 | -0.091553 | 122.4197 | -1.6068 | -0.40283 | -0.1236 | 0.54932 | 122.1176 | 66.8015 | 120.9412 | 122.319 | -0.091553 | 122.4243 | 122.081 | -0.40283 | 122.319 | -0.091553 | 122.081 | 120.9412 | 122.4243 | -123.1888 | -122.9507
2787.9062 | 122.6944 | -62.7777 | 59.1476 | 0.019379 | 0.0045118 | 0.0032406 | 0.0071051 | 0.00058321 | -0.00093346 | 0.0036253 | -60.2829 | 62.2513 | -60.6445 | 62.384 | 60.5759 | 61.8713 | 61.7065 | 2.1057 | 61.6699 | -61.9537 | 2.1332 | 3.1036 | 2.4948 | 125.1617 | 1.4282 | 0.82397 | 2.5223 | 0.36163 | 124.4843 | 64.8834 | 123.3536 | 125.029 | 2.4948 | 124.4476 | 124.649 | 0.82397 | 125.029 | 2.4948 | 124.649 | 123.3536 | 124.4476 | -119.7922 | -121.1014
2788.9219 | 122.7814 | -60.1913 | 62.1826 | 0.41611 | -0.00040164 | 0.001318 | 0.0011237 | -0.001553 | -0.0015745 | 0.0038389 | -60.2005 | 62.0544 | -60.7544 | 62.3108 | 60.5667 | 61.8942 | 61.6058 | 4.9255 | 62.1185 | -60.6216 | -0.56305 | -0.12817 | -0.009155 | 122.5021 | -1.6159 | -0.4303 | -0.064087 | 0.5539 | 121.7972 | 65.1169 | 120.7581 | 122.2458 | -0.009155 | 122.3099 | 122.0856 | -0.4303 | 122.2458 | -0.009155 | 122.0856 | 120.7581 | 122.3099 | -122.937 | -122.8043
2789.9062 | 122.6715 | -63.1805 | 58.9554 | 0.019379 | 0.0045118 | 0.0060178 | 0.0068915 | -0.00091219 | 0.00056194 | 0.0025571 | -62.8876 | 59.7794 | -63.2355 | 60.3836 | 58.9691 | 59.9167 | 59.2712 | 4.3121 | 59.7656 | -63.3728 | -0.054932 | 0.82398 | 0.29297 | 123.5641 | 0.013733 | -0.19226 | 0.81024 | 0.3479 | 122.4518 | 67.4927 | 122.1497 | 122.9599 | 0.29297 | 122.9462 | 123.0972 | -0.19226 | 122.9599 | 0.29297 | 123.0972 | 122.1497 | 122.9462 | -122.1909 | -122.3282
2790.9062 | 122.7173 | -59.491 | 62.2513 | 0.011749 | 0.0077162 | 0.0045224 | 0.0081733 | -0.002194 | -0.0011471 | 0.0044797 | -57.7652 | 64.5996 | -58.287 | 64.6317 | 62.7319 | 63.9313 | 63.5422 | 4.9576 | 64.2471 | -58.8272 | 1.2039 | 2.3483 | 1.7258 | 124.1226 | 0.48065 | 0.66376 | 1.9958 | 0.52185 | 123.0331 | 64.4485 | 122.2229 | 124.0906 | 1.7258 | 123.7381 | 123.4222 | 0.66376 | 124.0906 | 1.7258 | 123.4222 | 122.2229 | 123.7381 | -120.5383 | -121.0785
2791.9062 | 122.6944 | -61.6516 | 60.9055 | 0.019379 | 0.0064344 | 0.0058042 | 0.0053961 | -0.00027139 | -0.00093346 | 0.0034115 | -61.3815 | 61.0062 | -61.94 | 60.7086 | 58.9325 | 60.2921 | 60.5988 | 4.3304 | 60.8368 | -62.0178 | -0.28839 | 0.10071 | 0.27008 | 122.3602 | -1.973 | -0.36621 | -0.068665 | 0.55847 | 122.2504 | 65.9821 | 120.5841 | 122.6578 | 0.27008 | 122.4884 | 121.9437 | -0.36621 | 122.6578 | 0.27008 | 121.9437 | 120.5841 | 122.4884 | -122.8455 | -122.9233
2792.9062 | 122.9553 | -57.3349 | 64.6866 | 0.034637 | 0.0047254 | 0.0045224 | 0.0066779 | -0.001553 | -0.0011471 | 0.0038389 | -59.6237 | 62.5397 | -60.1501 | 64.0091 | 62.8922 | 62.8143 | 62.2147 | 2.6505 | 63.1989 | -58.58 | -2.8152 | -2.1469 | -2.2888 | 121.344 | -1.7944 | -1.2451 | -1.4877 | 0.52643 | 119.5496 | 59.9854 | 120.2271 | 119.8746 | -2.2888 | 120.5338 | 120.1492 | -1.2451 | 119.8746 | -2.2888 | 120.1492 | 120.2271 | 120.5338 | -124.8367 | -123.2666
2793.9062 | 122.7127 | -57.4722 | 65.0894 | 0.13382 | 0.0062208 | 0.0025998 | 0.0045417 | 0.00015601 | -0.0017881 | 0.0038389 | -57.637 | 64.7278 | -58.1223 | 65.0436 | 63.2584 | 63.1668 | 64.6362 | 3.923 | 64.9979 | -57.8934 | -0.65002 | -0.36163 | -0.16479 | 122.5159 | -1.8311 | -0.42114 | -0.091553 | 0.48523 | 122.1085 | 61.3953 | 120.7306 | 122.2 | -0.16479 | 122.4701 | 120.639 | -0.42114 | 122.2 | -0.16479 | 120.639 | 120.7306 | 122.4701 | -123.2117 | -122.9828
2794.9062 | 122.7081 | -58.9417 | 63.5468 | -0.11032 | 0.0042982 | 0.0028134 | 0.0066779 | -0.00069859 | 0.00013454 | 0.0038389 | -59.404 | 62.9929 | -59.7748 | 63.5056 | 61.7706 | 61.4273 | 63.1027 | 4.9347 | 63.5056 | -59.3399 | -0.83313 | -0.55389 | -0.46234 | 122.4472 | -1.7761 | -0.39825 | -0.041199 | 0.37079 | 122.0444 | 63.8763 | 120.7123 | 121.9345 | -0.46234 | 122.4472 | 120.369 | -0.39825 | 121.9345 | -0.46234 | 120.369 | 120.7123 | 122.4472 | -123.3215 | -122.8867
2795.9062 | 122.6303 | -60.7086 | 61.8393 | -0.087433 | 0.0017346 | 0.010717 | 0.0051825 | 0.00058321 | 0.00013454 | 0.0051205 | -60.5804 | 61.3266 | -61.2854 | 62.1826 | 60.5072 | 59.7702 | 61.8073 | 4.6875 | 61.9766 | -60.9695 | -0.57678 | -0.5127 | 0.12817 | 122.8912 | -1.3321 | -0.26093 | 0.13733 | 0.70496 | 122.5159 | 65.3961 | 121.2158 | 122.0352 | 0.12817 | 122.6852 | 120.4788 | -0.26093 | 122.0352 | 0.12817 | 120.4788 | 121.2158 | 122.6852 | -123.1247 | -122.8088
2796.9062 | 122.7036 | -60.0128 | 62.5351 | 0.042267 | 0.0038708 | 0.0049496 | 0.0077459 | -0.0013394 | -0.00071986 | 0.0025571 | -59.9854 | 62.5305 | -60.4202 | 62.2879 | 60.5621 | 57.2479 | 62.4619 | 4.5593 | 62.4115 | -60.379 | -0.40741 | -0.004577 | 0.027465 | 122.3007 | -1.973 | -0.36621 | -0.1236 | 0.43487 | 122.4747 | 64.5721 | 120.575 | 122.5433 | 0.027465 | 122.4243 | 117.2607 | -0.36621 | 122.5433 | 0.027465 | 117.2607 | 120.575 | 122.4243 | -122.9553 | -122.9141
2797.9062 | 122.7493 | -60.0266 | 62.5305 | -0.041657 | 0.0042982 | 3.6382e-05 | 0.0066779 | -0.0017666 | -0.00093346 | 0.0029843 | -59.9808 | 62.5122 | -60.3882 | 62.6312 | 60.7452 | 61.5829 | 62.1826 | 5.278 | 62.4435 | -60.4065 | -0.36163 | -0.018311 | 0.045776 | 122.6578 | -1.7853 | -0.37994 | -0.086976 | 0.40741 | 122.2092 | 65.3046 | 120.7718 | 122.5388 | 0.045776 | 122.4701 | 121.6095 | -0.37994 | 122.5388 | 0.045776 | 121.6095 | 120.7718 | 122.4701 | -122.9187 | -122.937
2798.9062 | 122.8363 | -59.1934 | 63.2446 | 0.16434 | 0.0013074 | 0.003027 | 0.013941 | -0.0011258 | -0.00029266 | 0.02221 | -59.285 | 63.0936 | -59.7198 | 63.5056 | 61.6562 | 61.2854 | 62.1689 | 5.6488 | 63.1668 | -59.5688 | -0.52643 | -0.15106 | -0.091553 | 122.699 | -1.5884 | -0.37537 | -0.07782 | 0.43488 | 121.3623 | 64.8422 | 120.8496 | 122.287 | -0.091553 | 122.3602 | 120.4788 | -0.37537 | 122.287 | -0.091553 | 120.4788 | 120.8496 | 122.3602 | -122.9645 | -122.8134
2799.9062 | 122.7448 | -59.3536 | 63.0341 | -0.026398 | 0.0051526 | 0.0032406 | 0.0064643 | -0.0017666 | -0.0015745 | 0.0029843 | -58.4152 | 65.3503 | -58.168 | 63.2492 | 61.4319 | 61.7477 | 63.0203 | 5.3879 | 63.1622 | -59.6786 | 1.1856 | 2.3163 | 0.93842 | 122.6028 | -1.6022 | -0.32501 | 0.12817 | -0.24719 | 122.374 | 64.7415 | 120.7855 | 124.704 | 0.93842 | 122.5159 | 121.1014 | -0.32501 | 124.704 | 0.93842 | 121.1014 | 120.7855 | 122.5159 | -121.2021 | -122.7127
2800.9062 | 121.9254 | -4.3076 | 113.0447 | -0.1561 | 0.0045118 | 0.0040952 | 0.49716 | -0.0026212 | 0.00013454 | 0.51397 | -4.5136 | 118.0527 | -5.04 | 117.9886 | 114.9078 | 54.332 | 117.7551 | 20.636 | 117.984 | -4.921 | -0.73242 | 5.0079 | -0.20599 | 122.2961 | 1.8631 | -0.6134 | 4.9393 | 0.52643 | 122.0627 | 24.9435 | 119.2154 | 122.3602 | -0.20599 | 122.2916 | 58.6395 | -0.6134 | 122.3602 | -0.20599 | 58.6395 | 119.2154 | 122.2916 | -118.0847 | -117.9657
2801.9062 | 122.1222 | -4.39 | 117.5812 | -0.2095 | 0.0036572 | 0.0015316 | 0.14105 | -0.0017666 | 0.00098914 | 0.16897 | -4.2892 | 118.309 | -4.8019 | 118.2358 | 115.1321 | 12.822 | 117.9703 | 19.693 | 118.2312 | -4.7791 | -0.41199 | 0.72784 | 0.10071 | 122.6257 | -2.449 | -0.3891 | 0.65002 | 0.51269 | 122.3602 | 24.0829 | 119.5221 | 122.699 | 0.10071 | 122.6212 | 17.2119 | -0.3891 | 122.699 | 0.10071 | 17.2119 | 119.5221 | 122.6212 | -122.3831 | -122.3602
2802.9062 | 122.1634 | -4.2206 | 117.9062 | -0.17899 | 0.0038708 | 0.0040952 | 0.035944 | -0.0026212 | -0.0013609 | 0.055108 | -4.1199 | 118.4326 | -4.6555 | 118.4509 | 115.2649 | -0.27924 | 118.1168 | 20.4391 | 118.3868 | -4.6143 | -0.43488 | 0.52643 | 0.10071 | 122.6715 | -2.6413 | -0.39368 | 0.48065 | 0.53558 | 122.3373 | 24.6597 | 119.4855 | 122.6532 | 0.10071 | 122.6074 | 3.9413 | -0.39368 | 122.6532 | 0.10071 | 3.9413 | 119.4855 | 122.6074 | -122.5616 | -122.5204
2803.9062 | 122.8592 | -4.3716 | 117.9977 | -2.3228 | 0.0040846 | 0.001318 | 0.0062507 | -0.0043302 | 0.00013454 | 0.021569 | -4.1885 | 118.3685 | -4.7287 | 118.3182 | 115.3015 | 116.2674 | 117.9977 | 24.2935 | 118.2953 | -4.7516 | -0.35706 | 0.37079 | 0.1831 | 122.6898 | -2.6962 | -0.37994 | 0.29755 | 0.54016 | 122.3694 | 28.6652 | 119.6732 | 122.7402 | 0.1831 | 122.6669 | 120.639 | -0.37994 | 122.7402 | 0.1831 | 120.639 | 119.6732 | 122.6669 | -122.7264 | -122.7493
2804.9062 | 116.8808 | -4.4495 | 118.4738 | -0.21713 | 0.0051526 | 0.0028134 | 0.0073187 | -0.003262 | -0.00050626 | 0.01986 | -4.097 | 118.4921 | -4.6097 | 118.5013 | 115.4755 | 116.6473 | 118.1763 | 25.0031 | 118.4189 | -4.6051 | -0.16022 | 0.01831 | 0.35248 | 122.9507 | -2.9984 | -0.15564 | -0.054932 | 0.51269 | 122.6257 | 29.4525 | 119.9249 | 122.9416 | 0.35248 | 122.8683 | 121.0968 | -0.15564 | 122.9416 | 0.35248 | 121.0968 | 119.9249 | 122.8683 | -123.0835 | -123.0789
2805.9062 | 122.2687 | -4.1702 | 117.8329 | -0.11795 | 0.0042982 | 0.00067718 | 0.0088141 | -0.0026212 | 0.00056194 | 0.01922 | -4.097 | 118.483 | -4.6234 | 118.4738 | 115.5075 | 117.0319 | 118.1488 | 24.646 | 118.3731 | -4.6005 | -0.45319 | 0.65002 | 0.073242 | 122.644 | -2.3254 | -0.4303 | 0.54016 | 0.52643 | 122.319 | 28.8162 | 119.6777 | 122.6532 | 0.073242 | 122.5433 | 121.2021 | -0.4303 | 122.6532 | 0.073242 | 121.2021 | 119.6777 | 122.5433 | -122.4564 | -122.4335
2806.9062 | 122.7905 | -4.2206 | 118.1488 | -0.17136 | 0.0036572 | 0.00067718 | 0.0056097 | -0.0034756 | -0.0024289 | 0.017724 | -4.0924 | 118.4601 | -4.6234 | 118.4784 | 115.5075 | 116.9952 | 118.1992 | 24.0372 | 118.4418 | -4.6097 | -0.40283 | 0.31128 | 0.12817 | 122.699 | -2.6413 | -0.3891 | 0.29297 | 0.53101 | 122.4197 | 28.2578 | 119.7281 | 122.6807 | 0.12817 | 122.6624 | 121.2158 | -0.3891 | 122.6807 | 0.12817 | 121.2158 | 119.7281 | 122.6624 | -122.7722 | -122.7585
2807.9062 | 122.0261 | -4.3854 | 118.2129 | -0.19424 | 0.0017346 | 0.003027 | 0.0004827 | -0.0041166 | -7.9062e-05 | 0.01922 | -4.2252 | 118.3456 | -4.7241 | 118.3502 | 115.416 | 116.9083 | 118.0801 | 24.1882 | 118.2907 | -4.7287 | -0.33875 | 0.13275 | 0.16022 | 122.7356 | -2.7969 | -0.34332 | 0.077819 | 0.49896 | 122.4655 | 28.5736 | 119.8013 | 122.731 | 0.16022 | 122.6761 | 121.2936 | -0.34332 | 122.731 | 0.16022 | 121.2936 | 119.8013 | 122.6761 | -122.937 | -122.9416
2808.9062 | 122.2824 | -4.5136 | 118.2266 | -0.21713 | 0.001521 | 0.00024998 | 0.0028327 | -0.0043302 | 0.00034814 | 0.017938 | -4.2343 | 118.277 | -4.7653 | 118.3273 | 115.3564 | 116.7114 | 117.9977 | 24.6414 | 118.2083 | -4.7882 | -0.25177 | 0.050354 | 0.27924 | 122.8409 | -2.8702 | -0.27466 | -0.018311 | 0.53101 | 122.5113 | 29.155 | 119.87 | 122.7905 | 0.27924 | 122.7219 | 121.225 | -0.27466 | 122.7905 | 0.27924 | 121.225 | 119.87 | 122.7219 | -122.9919 | -123.0148
2809.9062 | 122.113 | -3.8452 | 118.8995 | -0.25528 | 0.0025892 | 0.0017454 | 0.0032599 | -0.0045438 | -0.00029266 | 0.020074 | -3.6438 | 118.927 | -4.1473 | 118.9774 | 115.979 | 117.1829 | 118.6981 | 25.0031 | 118.9041 | -4.1245 | -0.30212 | 0.027466 | 0.20142 | 122.8226 | -2.9205 | -0.27924 | 0.004578 | 0.50354 | 122.5433 | 28.8483 | 119.8242 | 122.7722 | 0.20142 | 122.7493 | 121.0281 | -0.27924 | 122.7722 | 0.20142 | 121.0281 | 119.8242 | 122.7493 | -123.0469 | -123.024
2810.9062 | 121.962 | -3.6758 | 119.0094 | -0.23239 | 0.0030164 | 0.00046358 | 0.0071051 | -0.0064664 | -0.00029266 | 0.019433 | -3.3188 | 119.133 | -4.0192 | 119.0689 | 116.066 | 117.1692 | 118.8126 | 24.9756 | 119.0277 | -4.0054 | -0.34332 | 0.1236 | 0.35705 | 122.7448 | -2.9434 | -0.32959 | 0.018311 | 0.70038 | 122.4884 | 28.6514 | 119.7418 | 122.8088 | 0.35705 | 122.7036 | 120.845 | -0.32959 | 122.8088 | 0.35705 | 120.845 | 119.7418 | 122.7036 | -123.0286 | -123.0148
2811.9062 | 121.9254 | -3.5797 | 119.165 | -0.17136 | 0.0040846 | 0.0032406 | 0.0058233 | -0.0051846 | 0.00056194 | 0.019433 | -3.4378 | 119.1422 | -3.9505 | 119.1605 | 116.1392 | 117.6407 | 118.8766 | 24.852 | 119.0735 | -3.9505 | -0.37079 | -0.022888 | 0.14191 | 122.7402 | -3.0258 | -0.37079 | -0.091553 | 0.51269 | 122.4564 | 28.4317 | 119.7189 | 122.7219 | 0.14191 | 122.6532 | 121.2204 | -0.37079 | 122.7219 | 0.14191 | 121.2204 | 119.7189 | 122.6532 | -123.1155 | -123.1155
2812.9062 | 122.0032 | -3.6255 | 119.1238 | -0.31631 | 0.0040846 | -0.0012454 | 0.0043281 | -0.0062528 | -7.9062e-05 | 0.01922 | -3.3691 | 119.1559 | -3.891 | 119.2154 | 116.2399 | 117.3477 | 118.9087 | 24.6689 | 119.1513 | -3.8818 | -0.2655 | 0.032044 | 0.25635 | 122.8409 | -2.8839 | -0.25635 | 0.027466 | 0.52185 | 122.5342 | 28.2944 | 119.8654 | 122.7814 | 0.25635 | 122.7768 | 120.9732 | -0.25635 | 122.7814 | 0.25635 | 120.9732 | 119.8654 | 122.7768 | -123.0148 | -123.0057
2813.9062 | 122.4884 | -3.5248 | 119.2245 | -0.21713 | 0.0013074 | 0.00089078 | 0.0041143 | -0.0047574 | -0.00029266 | 0.020288 | -3.2684 | 119.1971 | -3.7994 | 119.3527 | 116.3589 | 110.9482 | 118.9682 | 25.058 | 119.2017 | -3.7811 | -0.27466 | -0.027465 | 0.25635 | 122.8775 | -2.8656 | -0.25635 | -0.022888 | 0.531 | 122.493 | 28.5828 | 119.8837 | 122.7219 | 0.25635 | 122.7264 | 114.473 | -0.25635 | 122.7219 | 0.25635 | 114.473 | 119.8837 | 122.7264 | -123.024 | -123.0057
2814.9062 | 122.7631 | -3.4927 | 119.1742 | -0.48416 | 0.00066656 | -0.00081822 | 0.0026191 | -0.0060392 | -0.0017881 | 0.018365 | -3.1998 | 119.1834 | -3.7949 | 119.4214 | 116.4276 | 116.5192 | 118.8583 | 25.0443 | 119.165 | -3.7765 | -0.30212 | 0.009156 | 0.29297 | 122.9141 | -2.7466 | -0.28381 | -0.009155 | 0.59509 | 122.3511 | 28.537 | 119.9203 | 122.6761 | 0.29297 | 122.6578 | 120.0119 | -0.28381 | 122.6761 | 0.29297 | 120.0119 | 119.9203 | 122.6578 | -122.9691 | -122.9507
2815.9062 | 122.7402 | -3.5202 | 119.165 | -0.14847 | -0.00082884 | -0.0033816 | 0.0036871 | -0.0071072 | -0.0015745 | 0.020288 | -3.2455 | 119.133 | -3.8132 | 119.22 | 116.2125 | 117.659 | 118.895 | 25.3922 | 119.133 | -3.8315 | -0.29297 | -0.032043 | 0.27466 | 122.7402 | -2.9526 | -0.31128 | -0.032043 | 0.56763 | 122.4152 | 28.9124 | 119.7327 | 122.6532 | 0.27466 | 122.6532 | 121.1792 | -0.31128 | 122.6532 | 0.27466 | 121.1792 | 119.7327 | 122.6532 | -122.9782 | -122.9965
2816.9062 | 122.1588 | -3.4744 | 119.3024 | -0.20187 | 0.0034436 | 0.00046358 | 0.0073187 | -0.0071072 | -0.0011471 | 0.018579 | -3.2684 | 119.3253 | -3.7811 | 119.5587 | 116.3864 | 117.4118 | 118.9957 | 26.1063 | 119.2886 | -3.7491 | -0.3067 | 0.022888 | 0.20599 | 123.0331 | -2.916 | -0.27466 | -0.013733 | 0.51269 | 122.4701 | 29.5807 | 119.8608 | 122.7997 | 0.20599 | 122.7631 | 120.8862 | -0.27466 | 122.7997 | 0.20599 | 120.8862 | 119.8608 | 122.7631 | -123.0835 | -123.0515
2817.9062 | 122.4609 | -3.6804 | 119.0186 | -0.24002 | 0.0017346 | -0.0012454 | 0.0053961 | -0.0068936 | -0.0032835 | 0.01922 | -3.4195 | 119.0506 | -3.9642 | 119.2108 | 116.2033 | 116.9586 | 118.7302 | 26.4175 | 119.0277 | -3.9413 | -0.28381 | 0.032043 | 0.26092 | 122.8912 | -2.8152 | -0.26093 | 0.009155 | 0.54474 | 122.4106 | 30.098 | 119.8837 | 122.731 | 0.26092 | 122.7081 | 120.639 | -0.26093 | 122.731 | 0.26092 | 120.639 | 119.8837 | 122.7081 | -122.9828 | -122.9599
2818.9219 | 122.8317 | -3.6118 | 119.0735 | -0.041657 | 0.002162 | 0.00024998 | 0.012018 | -0.002194 | -0.0013609 | 0.020074 | -3.3188 | 119.2154 | -3.8818 | 119.2566 | 116.2216 | 117.2699 | 118.808 | 26.5869 | 119.0826 | -3.9001 | -0.27008 | 0.14191 | 0.29297 | 122.8683 | -2.8519 | -0.28839 | 0.009156 | 0.56305 | 122.4197 | 30.1987 | 119.8334 | 122.8271 | 0.29297 | 122.6944 | 120.8817 | -0.28839 | 122.8271 | 0.29297 | 120.8817 | 119.8334 | 122.6944 | -122.9553 | -122.9736
2819.9062 | 122.5525 | -3.7033 | 119.046 | -0.2095 | 0.0023756 | 0.00046358 | 0.0034735 | -0.0034756 | -0.0020017 | 0.019433 | -3.4287 | 119.0964 | -3.9413 | 119.1879 | 116.1942 | 117.659 | 118.8217 | 26.7609 | 119.0643 | -3.9276 | -0.23804 | 0.050354 | 0.27466 | 122.8912 | -2.8519 | -0.2243 | 0.01831 | 0.51269 | 122.525 | 30.4642 | 119.8975 | 122.7997 | 0.27466 | 122.7676 | 121.3623 | -0.2243 | 122.7997 | 0.27466 | 121.3623 | 119.8975 | 122.7676 | -122.9874 | -122.9736
2820.9062 | 122.7676 | -3.4882 | 119.2291 | -0.14084 | -0.001256 | -0.001459 | 0.0036871 | -0.0077482 | -0.0026425 | 0.019433 | -3.1677 | 119.0048 | -3.978 | 119.5358 | 116.5329 | 117.897 | 118.8904 | 27.2141 | 119.1925 | -3.7949 | -0.48981 | -0.2243 | 0.32043 | 123.024 | -2.6962 | -0.3067 | -0.036621 | 0.81024 | 122.3785 | 30.7022 | 120.0211 | 122.493 | 0.32043 | 122.6807 | 121.3852 | -0.3067 | 122.493 | 0.32043 | 121.3852 | 120.0211 | 122.6807 | -123.2071 | -123.024
2821.9062 | 122.8638 | -4.3945 | 118.2678 | -0.095062 | 0.00066656 | -0.0010318 | 0.0039007 | -0.0077482 | 0.0016299 | 0.017724 | -4.1107 | 118.3044 | -4.6417 | 118.5516 | 115.567 | 116.6702 | 117.9199 | 27.1729 | 118.2724 | -4.6326 | -0.24719 | 0.036621 | 0.28381 | 122.9462 | -2.7008 | -0.23804 | 0.004578 | 0.53101 | 122.3145 | 31.5674 | 119.9615 | 122.699 | 0.28381 | 122.6669 | 121.0648 | -0.23804 | 122.699 | 0.28381 | 121.0648 | 119.9615 | 122.6669 | -122.9095 | -122.9004
2822.9062 | 122.85 | -4.0192 | 118.6432 | -0.049286 | 0.00066656 | 0.001959 | 0.0043281 | -0.0077482 | 0.00056194 | 0.019433 | -3.7674 | 118.6523 | -4.3121 | 118.8766 | 115.8783 | 117.3203 | 118.2587 | 27.4384 | 118.6111 | -4.2938 | -0.29297 | 0.009156 | 0.25177 | 122.8958 | -2.7649 | -0.27466 | -0.032043 | 0.54474 | 122.2778 | 31.4575 | 119.8975 | 122.6715 | 0.25177 | 122.6303 | 121.3394 | -0.27466 | 122.6715 | 0.25177 | 121.3394 | 119.8975 | 122.6303 | -122.9553 | -122.937
2823.9062 | 122.8271 | -3.5706 | 119.1834 | -0.19424 | 0.001521 | -0.0012454 | 0.0051825 | -0.0077482 | 0.00013454 | 0.01922 | -3.2913 | 119.1193 | -3.8452 | 119.339 | 116.3818 | 117.9657 | 118.808 | 27.5757 | 119.1147 | -3.804 | -0.27466 | -0.064087 | 0.27924 | 122.9095 | -2.8015 | -0.23346 | -0.068665 | 0.55389 | 122.3785 | 31.1462 | 119.9524 | 122.6898 | 0.27924 | 122.6852 | 121.5363 | -0.23346 | 122.6898 | 0.27924 | 121.5363 | 119.9524 | 122.6852 | -123.0286 | -122.9874
2824.9062 | 122.612 | -4.9026 | 117.8101 | -0.27817 | 2.5564e-05 | 0.0015316 | 0.0073187 | -0.0056118 | 0.00077554 | 0.018579 | -4.6509 | 117.8101 | -5.1682 | 118.0252 | 115.0726 | 115.8325 | 117.453 | 26.9577 | 117.7505 | -5.159 | -0.2655 | 0 | 0.25177 | 122.9279 | -2.7374 | -0.25635 | -0.05951 | 0.51727 | 122.3557 | 31.8604 | 119.9753 | 122.7127 | 0.25177 | 122.6532 | 120.7352 | -0.25635 | 122.7127 | 0.25177 | 120.7352 | 119.9753 | 122.6532 | -122.9782 | -122.9691
2825.9062 | 122.818 | -4.7836 | 117.9108 | -0.11795 | 0.00066656 | 0.0040952 | 0.0030463 | -0.0077482 | -0.00029266 | 0.018579 | -4.4769 | 117.9199 | -5.04 | 118.1488 | 115.2008 | 111.4563 | 117.572 | 26.7334 | 117.8696 | -5.0125 | -0.25635 | 0.009155 | 0.3067 | 122.9324 | -2.71 | -0.22888 | -0.041199 | 0.56305 | 122.3557 | 31.517 | 119.9844 | 122.7036 | 0.3067 | 122.6532 | 116.2399 | -0.22888 | 122.7036 | 0.3067 | 116.2399 | 119.9844 | 122.6532 | -122.9507 | -122.9233
2826.9062 | 122.8683 | -5.0034 | 117.6727 | -0.30869 | 0.00045296 | 0.0021726 | 0.0034735 | -0.0077482 | 0.0018435 | 0.018365 | -4.8111 | 117.6544 | -5.3238 | 117.9062 | 114.9399 | 116.0797 | 117.3248 | 27.1729 | 117.6315 | -5.2597 | -0.32043 | -0.01831 | 0.19226 | 122.9095 | -2.7328 | -0.25635 | -0.041198 | 0.5127 | 122.3282 | 32.1762 | 119.9432 | 122.6578 | 0.19226 | 122.6349 | 121.0831 | -0.25635 | 122.6578 | 0.19226 | 121.0831 | 119.9432 | 122.6349 | -122.9965 | -122.9324
2827.9062 | 122.5845 | -3.0853 | 119.6869 | -0.13321 | 0.001521 | 0.0038816 | 0.0030463 | -0.0064664 | -0.0017881 | 0.01687 | -2.7695 | 119.664 | -3.3188 | 119.8608 | 116.89 | 118.515 | 119.3298 | 27.4292 | 119.6136 | -3.3234 | -0.23346 | -0.022889 | 0.31586 | 122.9462 | -2.7969 | -0.23804 | -0.073243 | 0.54932 | 122.4152 | 30.5145 | 119.9753 | 122.7493 | 0.31586 | 122.699 | 121.6003 | -0.23804 | 122.7493 | 0.31586 | 121.6003 | 119.9753 | 122.699 | -123.0057 | -123.0103
2828.9062 | 122.4838 | -3.0716 | 119.7144 | -0.22476 | 0.0028028 | 0.001959 | 0.0043281 | -0.0053982 | -7.9062e-05 | 0.018792 | -2.7969 | 119.7372 | -3.3554 | 119.8334 | 116.7938 | 118.1168 | 119.4534 | 27.0493 | 119.6869 | -3.3371 | -0.28381 | 0.022889 | 0.27466 | 122.905 | -2.9205 | -0.2655 | -0.027465 | 0.55847 | 122.525 | 30.1208 | 119.8654 | 122.8088 | 0.27466 | 122.7585 | 121.1884 | -0.2655 | 122.8088 | 0.27466 | 121.1884 | 119.8654 | 122.7585 | -123.0698 | -123.0515
2829.9062 | 122.8683 | -3.1586 | 119.5358 | -0.056915 | -0.0010424 | -0.0042362 | 0.0019781 | -0.0058256 | -0.00071986 | 0.01922 | -2.9022 | 119.5404 | -3.4378 | 119.7693 | 116.7847 | 117.8925 | 119.1605 | 27.6672 | 119.5312 | -3.4195 | -0.27924 | 0.004577 | 0.25635 | 122.9279 | -2.7512 | -0.26093 | -0.004578 | 0.53558 | 122.319 | 30.8258 | 119.9432 | 122.699 | 0.25635 | 122.6898 | 121.051 | -0.26093 | 122.699 | 0.25635 | 121.051 | 119.9432 | 122.6898 | -122.9736 | -122.9553
2830.9062 | 122.8821 | -3.1631 | 119.545 | -0.095062 | 0.00023916 | -0.0010318 | 0.0039007 | -0.0068936 | -0.00050626 | 0.01922 | -2.8748 | 119.5221 | -3.4515 | 119.783 | 116.8579 | 118.2404 | 119.1376 | 27.182 | 119.4855 | -3.4103 | -0.28839 | -0.022888 | 0.28839 | 122.9462 | -2.6871 | -0.24719 | -0.059509 | 0.57678 | 122.3007 | 30.3452 | 120.0211 | 122.6852 | 0.28839 | 122.6486 | 121.4035 | -0.24719 | 122.6852 | 0.28839 | 121.4035 | 120.0211 | 122.6486 | -122.9965 | -122.9553
2831.9062 | 122.8775 | -3.154 | 119.5404 | -0.27817 | -0.00018804 | 0.0017454 | 0.0049689 | -0.0077482 | 0.0014163 | 0.01986 | -2.9022 | 119.5541 | -3.4287 | 119.8013 | 116.8213 | 117.9977 | 119.2108 | 27.7084 | 119.5084 | -3.4195 | -0.27466 | 0.013733 | 0.25177 | 122.9553 | -2.7191 | -0.2655 | -0.032043 | 0.52643 | 122.3648 | 30.8624 | 119.9753 | 122.7081 | 0.25177 | 122.6624 | 121.1517 | -0.2655 | 122.7081 | 0.25177 | 121.1517 | 119.9753 | 122.6624 | -122.9691 | -122.9599
2832.9062 | 122.8546 | -3.1265 | 119.6136 | -0.16373 | -0.0014696 | 0.0049496 | 0.0064643 | -0.0086026 | 0.00077554 | 0.021569 | -2.861 | 119.577 | -3.4241 | 119.783 | 116.8213 | 117.984 | 119.2245 | 28.0289 | 119.5267 | -3.3783 | -0.29755 | -0.036621 | 0.2655 | 122.9095 | -2.7924 | -0.25177 | -0.086975 | 0.56305 | 122.3511 | 31.1554 | 119.9478 | 122.7036 | 0.2655 | 122.6532 | 121.1105 | -0.25177 | 122.7036 | 0.2655 | 121.1105 | 119.9478 | 122.6532 | -123.0377 | -122.9919
2833.9062 | 122.3877 | -3.2089 | 119.5908 | -0.22476 | 0.00066656 | -0.00017722 | 0.0098823 | -0.0030484 | 0.00077554 | 0.018151 | -2.9984 | 119.6777 | -3.4287 | 119.7235 | 116.7114 | 118.0847 | 119.3665 | 27.7359 | 119.5587 | -3.4241 | -0.21973 | 0.086975 | 0.21057 | 122.9324 | -2.8793 | -0.21515 | -0.032043 | 0.4303 | 122.5754 | 30.9448 | 119.9203 | 122.8867 | 0.21057 | 122.7676 | 121.2936 | -0.21515 | 122.8867 | 0.21057 | 121.2936 | 119.9203 | 122.7676 | -123.0194 | -123.0148
2834.9062 | 122.9004 | -3.0853 | 119.6091 | 0.0041197 | 0.00045296 | -0.00017722 | 0.0034735 | -0.004971 | 0.00056194 | 0.01986 | -2.8015 | 119.6045 | -3.3646 | 119.8517 | 116.89 | 118.2541 | 119.2062 | 28.0472 | 119.5679 | -3.3508 | -0.27924 | -0.004578 | 0.28381 | 122.937 | -2.7191 | -0.2655 | -0.041199 | 0.56305 | 122.2916 | 31.1325 | 119.9753 | 122.6898 | 0.28381 | 122.6532 | 121.3394 | -0.2655 | 122.6898 | 0.28381 | 121.3394 | 119.9753 | 122.6532 | -122.9736 | -122.9599
2835.9062 | 122.0123 | -3.0991 | 119.5908 | -0.064545 | 0.0051526 | 0.001959 | 0.012659 | -0.0034756 | 0.00056194 | 0.017297 | -2.9572 | 119.5724 | -3.5248 | 119.7372 | 116.716 | 118.4601 | 119.2795 | 27.9831 | 119.5358 | -3.4287 | -0.42572 | -0.01831 | 0.14191 | 122.8363 | -2.8748 | -0.32959 | -0.054931 | 0.56763 | 122.3785 | 31.0822 | 119.8151 | 122.6715 | 0.14191 | 122.6349 | 121.5591 | -0.32959 | 122.6715 | 0.14191 | 121.5591 | 119.8151 | 122.6349 | -123.1155 | -123.0194
2836.9062 | 122.8363 | -3.2593 | 119.4809 | 0.034637 | 0.0013074 | 0.00067718 | 0.0013373 | -0.0045438 | 0.0018435 | 0.018792 | -3.0487 | 119.4489 | -3.5477 | 119.6274 | 116.6565 | 118.071 | 119.1422 | 28.3035 | 119.4443 | -3.5065 | -0.28839 | -0.032043 | 0.21057 | 122.8867 | -2.8244 | -0.24719 | -0.036621 | 0.49896 | 122.4014 | 31.5628 | 119.9158 | 122.7081 | 0.21057 | 122.7036 | 121.3303 | -0.24719 | 122.7081 | 0.21057 | 121.3303 | 119.9158 | 122.7036 | -123.0286 | -122.9874
2837.9062 | 122.8729 | -60.759 | 61.7111 | -0.056915 | 0.0017346 | -0.00081822 | 0.0011237 | -0.00668 | -0.00071986 | 0.0021299 | -60.0037 | 61.9308 | -60.8139 | 61.7935 | 59.8389 | 59.935 | 60.5072 | 7.6172 | 61.203 | -61.3358 | -0.054932 | 0.21973 | 0.75531 | 122.5525 | -1.8723 | -0.57678 | -0.50812 | 0.81024 | 121.2662 | 68.3762 | 120.5978 | 122.6898 | 0.75531 | 121.962 | 120.694 | -0.57678 | 122.6898 | 0.75531 | 120.694 | 120.5978 | 121.962 | -122.525 | -123.0469
2838.9062 | 122.6257 | -114.6744 | 7.9742 | -0.22476 | 0.0028028 | -0.0029544 | 0.018641 | -0.00668 | -0.0017881 | 0.0017027 | -114.2624 | 7.988 | -114.9811 | 7.8049 | 7.3151 | 7.3196 | 7.4432 | -11.1603 | 8.0017 | -115.0406 | -0.3067 | 0.013733 | 0.41199 | 122.4792 | -0.65918 | -0.36621 | 0.027466 | 0.71869 | 122.1176 | 103.5141 | 121.9894 | 122.6624 | 0.41199 | 122.6761 | 121.994 | -0.36621 | 122.6624 | 0.41199 | 121.994 | 121.9894 | 122.6761 | -122.9553 | -123.0148
2839.9062 | 122.9004 | -64.2426 | 58.2047 | -0.034027 | 0.0017346 | 0.0034544 | -0.0001581 | -0.004971 | -0.0011471 | 0.0012753 | -64.7095 | 57.7057 | -65.1398 | 58.7448 | 57.3212 | 56.9183 | 58.3511 | 6.1157 | 58.3923 | -64.4211 | -0.89722 | -0.49896 | -0.46692 | 122.9874 | -0.88348 | -0.17853 | 0.18768 | 0.4303 | 122.5937 | 70.3583 | 121.5637 | 121.9482 | -0.46692 | 122.6349 | 121.1609 | -0.17853 | 121.9482 | -0.46692 | 121.1609 | 121.5637 | 122.6349 | -123.3444 | -122.6257
2840.9219 | 122.7676 | -63.2217 | 59.3399 | 0.057526 | 0.0038708 | 0.003668 | 0.0083869 | -0.00668 | -0.0011471 | 0.00063446 | -63.1805 | 59.3903 | -63.6017 | 59.4864 | 57.8339 | 57.9758 | 59.23 | 6.4636 | 59.3536 | -63.5284 | -0.37994 | 0.050354 | 0.041199 | 122.7081 | -1.506 | -0.3067 | 0.013733 | 0.42114 | 122.4518 | 69.6854 | 121.0556 | 122.612 | 0.041199 | 122.5754 | 121.1975 | -0.3067 | 122.612 | 0.041199 | 121.1975 | 121.0556 | 122.5754 | -122.9416 | -122.8683
2841.9062 | 122.8409 | -63.0249 | 59.523 | -0.0035098 | 0.0030164 | 0.00067718 | -0.0016535 | -0.0041166 | 0.00098914 | 0.0031979 | -62.8326 | 59.5779 | -63.2858 | 59.7656 | 58.0124 | 56.9641 | 59.2484 | 6.6742 | 59.5139 | -63.3133 | -0.26093 | 0.054932 | 0.19226 | 122.7905 | -1.5106 | -0.28839 | -0.009155 | 0.45319 | 122.2733 | 69.6991 | 121.0373 | 122.6028 | 0.19226 | 122.5388 | 119.989 | -0.28839 | 122.6028 | 0.19226 | 119.989 | 121.0373 | 122.5388 | -122.8088 | -122.8363
2842.9062 | 122.8317 | -62.5488 | 59.9533 | 0.049896 | 0.00066656 | -0.0010318 | 0.0024053 | -0.0062528 | -0.00071986 | 0.0019163 | -62.5717 | 59.8022 | -63.0386 | 59.8618 | 58.2733 | 57.5912 | 59.7519 | 6.7978 | 59.8846 | -62.8281 | -0.48981 | -0.15106 | -0.022888 | 122.4106 | -1.68 | -0.27924 | -0.068664 | 0.46692 | 122.3007 | 69.3466 | 120.8221 | 122.3511 | -0.022888 | 122.4335 | 120.1401 | -0.27924 | 122.3511 | -0.022888 | 120.1401 | 120.8221 | 122.4335 | -122.9919 | -122.7814
2843.9062 | 122.8409 | -62.9333 | 59.5093 | -0.2858 | 0.0017346 | 0.0015316 | 0.0032599 | -0.0062528 | -0.0015745 | 0.0038389 | -62.7045 | 59.6283 | -63.2812 | 59.6695 | 58.0353 | 57.811 | 59.7107 | 7.283 | 59.7473 | -62.9974 | -0.3479 | 0.11902 | 0.22888 | 122.6028 | -1.474 | -0.064087 | 0.23804 | 0.57678 | 122.644 | 70.2164 | 120.9686 | 122.5616 | 0.22888 | 122.6807 | 120.7443 | -0.064087 | 122.5616 | 0.22888 | 120.7443 | 120.9686 | 122.6807 | -122.7905 | -122.5067
2844.9062 | 122.8546 | -62.8693 | 59.6649 | -0.064545 | -0.00018804 | -0.00039102 | -0.0003717 | -0.004971 | -0.0017881 | 0.00042086 | -62.6221 | 59.6329 | -63.1531 | 59.8663 | 58.1451 | 56.7352 | 59.5963 | 6.7474 | 59.7015 | -63.0936 | -0.28381 | -0.032043 | 0.24719 | 122.7356 | -1.5198 | -0.2243 | 0.036621 | 0.53101 | 122.4655 | 69.6167 | 121.0144 | 122.5021 | 0.24719 | 122.5708 | 119.6045 | -0.2243 | 122.5021 | 0.24719 | 119.6045 | 121.0144 | 122.5708 | -122.818 | -122.7585
2845.9219 | 122.7905 | -63.295 | 59.2484 | -0.16373 | 0.0023756 | 0.0034544 | 0.0092413 | -0.003903 | -0.0011471 | 0.0010617 | -62.5031 | 59.8434 | -63.0707 | 59.6695 | 57.9529 | 56.9595 | 59.2026 | 6.3766 | 59.4635 | -63.4827 | 0.2243 | 0.59509 | 0.79193 | 122.9645 | -1.2955 | -0.18768 | 0.21515 | 0.56763 | 122.4976 | 69.6716 | 121.2479 | 123.1384 | 0.79193 | 122.7585 | 120.2545 | -0.18768 | 123.1384 | 0.79193 | 120.2545 | 121.2479 | 122.7585 | -122.319 | -122.731
2846.9062 | 122.8271 | -64.1876 | 58.4152 | 0.14145 | 2.5564e-05 | 0.0025998 | -0.0003717 | -0.0051846 | -0.00029266 | 0.0012753 | -64.183 | 58.0856 | -64.6957 | 58.5068 | 57.0374 | 56.8085 | 58.0582 | 6.0471 | 58.2962 | -64.5035 | -0.50812 | -0.32959 | 0.004578 | 122.6944 | -1.3779 | -0.31586 | -0.11902 | 0.5127 | 122.2458 | 70.2347 | 121.225 | 122.2733 | 0.004578 | 122.4838 | 120.9961 | -0.31586 | 122.2733 | 0.004578 | 120.9961 | 121.225 | 122.4838 | -123.111 | -122.9187
2847.9062 | 122.8134 | -63.4735 | 59.1019 | -0.858 | 0.0019482 | -0.00017722 | 0.0015509 | -0.0077482 | -0.00071986 | 0.0049069 | -63.3774 | 59.0607 | -63.7711 | 59.2941 | 57.6782 | 56.6574 | 58.7952 | 6.6055 | 59.0424 | -63.7802 | -0.29755 | -0.041199 | 0.096131 | 122.7676 | -1.4236 | -0.3067 | -0.05951 | 0.39368 | 122.2687 | 70.079 | 121.1517 | 122.5342 | 0.096131 | 122.5159 | 120.1309 | -0.3067 | 122.5342 | 0.096131 | 120.1309 | 121.1517 | 122.5159 | -122.8729 | -122.8821
2848.9062 | 122.8226 | -62.6129 | 59.8663 | -0.21713 | 0.00066656 | 0.0015316 | 0.0049689 | -0.0077482 | -0.00071986 | 0.0019163 | -62.6083 | 59.7107 | -63.0936 | 60.379 | 58.6121 | 58.5114 | 60.0952 | 7.1228 | 60.1318 | -62.7182 | -0.48065 | -0.15564 | 0.004578 | 122.9919 | -1.2543 | -0.10529 | 0.2655 | 0.48523 | 122.7081 | 69.7357 | 121.225 | 122.3236 | 0.004578 | 122.7448 | 121.1243 | -0.10529 | 122.3236 | 0.004578 | 121.1243 | 121.225 | 122.7448 | -122.9599 | -122.5845
2849.9062 | 122.85 | -62.9608 | 59.5047 | 0.25589 | 0.00045296 | -0.001459 | 0.0017645 | -0.0062528 | -0.0022153 | 0.0031979 | -62.1918 | 60.0861 | -62.7869 | 59.816 | 58.4702 | 58.1085 | 59.6191 | 7.1182 | 59.7702 | -63.1027 | 0.17395 | 0.58136 | 0.76904 | 122.7768 | -1.0345 | -0.14191 | 0.2655 | 0.59509 | 122.58 | 70.079 | 121.431 | 123.0469 | 0.76904 | 122.731 | 121.0693 | -0.14191 | 123.0469 | 0.76904 | 121.0693 | 121.431 | 122.731 | -122.2916 | -122.6074
2850.9062 | 122.8592 | -63.0249 | 59.4955 | -0.011139 | 2.5564e-05 | -0.0023136 | 0.0019781 | -0.0051846 | 0.00013454 | 0.0038389 | -62.764 | 59.6054 | -63.2538 | 59.761 | 58.168 | 57.1747 | 59.5139 | 7.3975 | 59.5734 | -63.2904 | -0.22888 | 0.10986 | 0.26093 | 122.7859 | -1.3275 | -0.2655 | 0.07782 | 0.48981 | 122.5388 | 70.4224 | 121.1929 | 122.6303 | 0.26093 | 122.5983 | 120.1996 | -0.2655 | 122.6303 | 0.26093 | 120.1996 | 121.1929 | 122.5983 | -122.7493 | -122.7859
2851.9062 | 122.818 | -62.1323 | 60.2692 | -0.011139 | 0.0025892 | 0.0060178 | 0.0019781 | -0.0056118 | 0.00077554 | 0.0044797 | -60.9787 | 61.4548 | -61.4182 | 61.322 | 59.523 | 58.699 | 60.9695 | 7.6172 | 61.0245 | -62.0544 | 0.71411 | 1.1856 | 1.1536 | 123.4543 | -0.74616 | 0.07782 | 0.75531 | 0.43945 | 123.1018 | 69.7494 | 121.6553 | 123.587 | 1.1536 | 123.1567 | 120.8313 | 0.07782 | 123.587 | 1.1536 | 120.8313 | 121.6553 | 123.1567 | -121.6873 | -122.3236
2852.9062 | 122.8775 | -62.851 | 59.7473 | 0.065155 | 0.0019482 | 0.0015316 | 0.0032599 | -0.00668 | 0.00077554 | 0.0038389 | -62.5717 | 59.8709 | -63.0066 | 59.7565 | 58.0948 | 58.0673 | 59.4681 | 7.7042 | 59.6375 | -63.1302 | -0.15564 | 0.1236 | 0.27924 | 122.6074 | -1.6525 | -0.27924 | -0.10986 | 0.43488 | 122.319 | 70.5551 | 120.9457 | 122.7219 | 0.27924 | 122.4884 | 120.9183 | -0.27924 | 122.7219 | 0.27924 | 120.9183 | 120.9457 | 122.4884 | -122.7539 | -122.8775
2853.9062 | 122.8867 | -61.4227 | 61.1755 | -0.14084 | -0.0016834 | 0.0011044 | 0.0051825 | -0.0079618 | -0.0026425 | 0.0027707 | -61.2671 | 60.9879 | -61.7981 | 61.4639 | 59.5779 | 59.2163 | 60.7132 | 8.1253 | 61.0062 | -61.7477 | -0.37537 | -0.18768 | 0.15564 | 122.8867 | -1.5976 | -0.32501 | -0.16937 | 0.53101 | 122.1359 | 69.548 | 121.0007 | 122.4106 | 0.15564 | 122.4289 | 120.639 | -0.32501 | 122.4106 | 0.15564 | 120.639 | 121.0007 | 122.4289 | -122.9736 | -122.9233
2854.9062 | 122.8271 | -62.5534 | 60.0769 | 0.11093 | 0.0017346 | -0.001459 | 0.0004827 | -0.0064664 | 0.00056194 | 0.0025571 | -62.2604 | 60.0861 | -62.6724 | 60.3333 | 58.6624 | 57.2845 | 59.5276 | 7.0496 | 59.8709 | -62.9974 | -0.11902 | 0.009156 | 0.29297 | 122.8867 | -1.4145 | -0.44403 | -0.20599 | 0.41199 | 122.081 | 69.603 | 121.2158 | 122.6395 | 0.29297 | 122.4243 | 119.838 | -0.44403 | 122.6395 | 0.29297 | 119.838 | 121.2158 | 122.4243 | -122.7493 | -123.0743
2855.9062 | 122.8409 | -62.5809 | 59.9213 | 0.11093 | 0.0025892 | 0.0038816 | 0.0024053 | -0.0053982 | 0.00077554 | 0.0034115 | -62.3611 | 59.9808 | -62.8784 | 60.2737 | 58.4702 | 58.1406 | 59.8755 | 7.196 | 59.9991 | -62.8326 | -0.29755 | 0.059509 | 0.21973 | 122.8546 | -1.4511 | -0.25177 | 0.077819 | 0.51727 | 122.4564 | 69.7769 | 121.051 | 122.5616 | 0.21973 | 122.58 | 120.7214 | -0.25177 | 122.5616 | 0.21973 | 120.7214 | 121.051 | 122.58 | -122.7997 | -122.7539
2856.9062 | 89.9826 | -106.8146 | 15.5731 | 0.1796 | 0.0028028 | 0.004736 | 0.020136 | -0.0053982 | -0.0039243 | 0.0038389 | -101.2299 | 18.3884 | -104.3152 | 15.6692 | 15.0146 | 14.5569 | 14.7583 | -7.8506 | 15.5914 | -107.1259 | 2.4994 | 2.8152 | 5.5847 | 122.4838 | -0.55847 | -0.31128 | 0.018311 | 3.0853 | 121.5729 | 98.9639 | 121.8292 | 125.2029 | 5.5847 | 122.406 | 121.3715 | -0.31128 | 125.2029 | 5.5847 | 121.3715 | 121.8292 | 122.406 | -119.8883 | -122.699
2857.9062 | 122.8775 | -114.5828 | 7.9834 | 0.25589 | 0.0017346 | 0.0038816 | 0.019282 | -0.0045438 | 0.0014163 | 0.0036253 | -114.1388 | 7.8918 | -114.9261 | 7.9468 | 7.5302 | 6.4087 | 7.2739 | -10.4782 | 8.0246 | -114.8895 | -0.34332 | -0.091552 | 0.44403 | 122.5296 | -0.45319 | -0.3067 | 0.041199 | 0.78735 | 121.8567 | 104.1046 | 122.113 | 122.4747 | 0.44403 | 122.6074 | 120.9915 | -0.3067 | 122.4747 | 0.44403 | 120.9915 | 122.113 | 122.6074 | -122.9095 | -122.8729
2858.9219 | 122.8409 | -62.4802 | 59.6146 | -0.24765 | -0.0010424 | 0.001318 | 0.0019781 | -0.0060392 | 0.0016299 | 0.0042661 | -61.972 | 60.4477 | -62.384 | 59.7931 | 58.1085 | 57.55 | 59.6237 | 7.3608 | 59.7656 | -62.9517 | 0.096131 | 0.83313 | 0.50812 | 122.2733 | -1.506 | -0.4715 | 0.15106 | 0.41199 | 122.1039 | 69.841 | 120.5887 | 122.9279 | 0.50812 | 122.2458 | 120.0302 | -0.4715 | 122.9279 | 0.50812 | 120.0302 | 120.5887 | 122.2458 | -121.9986 | -122.5662
2859.9062 | 122.7997 | -54.9362 | 67.1814 | 0.16434 | 0.00088016 | 0.0015316 | 0.0051825 | -0.003262 | -0.0026425 | 0.0042661 | -55.1697 | 66.4856 | -56.0211 | 68.7836 | 66.0507 | 65.0574 | 67.9413 | 10.2127 | 68.1747 | -54.9454 | -1.0849 | -0.6958 | -0.23346 | 123.7198 | -1.1307 | -0.009156 | 0.99335 | 0.85144 | 122.8775 | 65.1489 | 120.9869 | 121.4218 | -0.23346 | 123.111 | 119.9936 | -0.009156 | 121.4218 | -0.23346 | 119.9936 | 120.9869 | 123.111 | -123.2025 | -122.1268
2860.9062 | 122.8546 | -61.9629 | 60.3424 | 0.6221 | 0.0019482 | 0.003027 | 0.0064643 | -0.0043302 | 0.0012027 | 0.0023435 | -59.6237 | 62.0132 | -60.4752 | 61.3541 | 59.5871 | 58.5892 | 60.3836 | 6.7429 | 60.7727 | -62.2147 | 1.4877 | 1.6708 | 2.3392 | 123.317 | -0.75531 | -0.25177 | 0.4303 | 0.85144 | 122.3465 | 68.7057 | 121.55 | 123.9761 | 2.3392 | 122.7356 | 120.5521 | -0.25177 | 123.9761 | 2.3392 | 120.5521 | 121.55 | 122.7356 | -120.8176 | -122.5571
2861.9062 | 122.8683 | -61.8439 | 60.6354 | 0.18723 | 0.0034436 | 0.0038816 | 0.0071051 | -0.0045438 | -0.0015745 | 0.0019163 | -61.8393 | 60.3058 | -62.4481 | 61.0199 | 59.2621 | 58.0307 | 60.2692 | 7.5851 | 60.6583 | -62.1323 | -0.60425 | -0.32959 | 0.004578 | 122.8638 | -1.3733 | -0.28839 | 0.022888 | 0.60883 | 122.113 | 69.429 | 121.106 | 122.1497 | 0.004578 | 122.5021 | 119.8746 | -0.28839 | 122.1497 | 0.004578 | 119.8746 | 121.106 | 122.5021 | -123.0835 | -122.7676
2862.9062 | 122.7585 | -61.3953 | 60.704 | 0.1796 | 0.0045118 | 0.0051632 | 0.0068915 | -0.0041166 | 0.00034814 | 0.0038389 | -60.553 | 61.8576 | -61.1801 | 61.0886 | 59.2896 | 57.4356 | 60.8505 | 7.1594 | 61.0062 | -61.8347 | 0.21515 | 1.1536 | 0.84228 | 122.4838 | -1.4145 | -0.43945 | 0.30212 | 0.62714 | 122.2458 | 68.5547 | 120.6848 | 123.2529 | 0.84228 | 122.4014 | 118.8309 | -0.43945 | 123.2529 | 0.84228 | 118.8309 | 120.6848 | 122.4014 | -121.8842 | -122.5388
2863.9062 | 122.8317 | -61.7752 | 60.5484 | 0.11093 | 0.0010938 | 0.0055906 | 0.0024053 | -0.0047574 | -0.00029266 | 0.0031979 | -61.4273 | 60.9283 | -61.8805 | 61.3541 | 59.4635 | 58.3923 | 60.4889 | 7.2052 | 60.8643 | -62.0178 | -0.10529 | 0.37994 | 0.3479 | 123.1293 | -1.0849 | -0.24261 | 0.31586 | 0.45319 | 122.2641 | 68.9804 | 121.2387 | 122.7036 | 0.3479 | 122.6395 | 120.1675 | -0.24261 | 122.7036 | 0.3479 | 120.1675 | 121.2387 | 122.6395 | -122.4289 | -122.5662
2864.9062 | 122.8226 | -60.5484 | 61.7706 | 0.16434 | 0.0047254 | 0.0017454 | 0.010523 | -0.0051846 | -0.00029266 | 0.0040525 | -60.3882 | 62.0407 | -60.8597 | 62.0865 | 60.3104 | 59.491 | 61.7706 | 7.6813 | 61.9766 | -60.9192 | -0.31128 | 0.27008 | 0.16022 | 122.6349 | -1.4603 | -0.37079 | 0.20599 | 0.4715 | 122.319 | 68.2297 | 120.8588 | 122.5891 | 0.16022 | 122.525 | 120.0394 | -0.37079 | 122.5891 | 0.16022 | 120.0394 | 120.8588 | 122.525 | -122.6303 | -122.6898
2865.9062 | 122.8683 | -62.4023 | 59.9442 | 0.25589 | 0.00088016 | 3.6382e-05 | 0.0071051 | -0.0036892 | -0.0015745 | 0.0021299 | -61.94 | 60.5392 | -62.4161 | 60.4202 | 58.58 | 54.8538 | 59.6237 | 7.0358 | 60.0861 | -62.645 | -0.013733 | 0.59509 | 0.46234 | 122.8226 | -1.3641 | -0.24261 | 0.14191 | 0.47608 | 122.0261 | 69.4382 | 120.9824 | 122.9416 | 0.46234 | 122.4884 | 117.2562 | -0.24261 | 122.9416 | 0.46234 | 117.2562 | 120.9824 | 122.4884 | -122.3602 | -122.5891
2866.9062 | 122.818 | -61.29 | 61.3037 | 0.1796 | 0.0040846 | 0.0051632 | 0.0075323 | -0.0011258 | -0.00093346 | 0.0031979 | -61.203 | 61.235 | -61.7157 | 61.1664 | 59.5734 | 57.2433 | 61.1481 | 7.457 | 61.2442 | -61.6745 | -0.42572 | -0.068665 | 0.086975 | 122.4564 | -1.7303 | -0.38452 | -0.059509 | 0.5127 | 122.438 | 68.7469 | 120.8633 | 122.525 | 0.086975 | 122.5342 | 118.5333 | -0.38452 | 122.525 | 0.086975 | 118.5333 | 120.8633 | 122.5342 | -123.0194 | -122.9782
2867.9062 | 122.7539 | -61.8027 | 60.4523 | 0.12619 | 0.0053662 | 0.0051632 | 0.011805 | -0.0017666 | 0.00013454 | 0.0055479 | -61.2991 | 61.1847 | -61.8484 | 61.1206 | 59.3536 | 52.6382 | 60.791 | 6.6559 | 60.9009 | -62.1002 | -0.045777 | 0.73242 | 0.50354 | 122.9233 | -1.0986 | -0.29755 | 0.44861 | 0.54932 | 122.5937 | 68.4586 | 121.1563 | 122.9874 | 0.50354 | 122.7036 | 114.4409 | -0.29755 | 122.9874 | 0.50354 | 114.4409 | 121.1563 | 122.7036 | -122.3007 | -122.5525
2868.9062 | 122.8683 | -63.5147 | 58.8638 | 0.20248 | 0.0010938 | 0.003027 | 0.0071051 | -0.00048499 | -0.00029266 | 0.0044797 | -62.8876 | 59.4131 | -63.4918 | 59.1248 | 57.4127 | 53.2608 | 58.9417 | 6.2805 | 59.0881 | -63.8077 | 0.022888 | 0.54932 | 0.62714 | 122.6395 | -1.4511 | -0.29297 | 0.2243 | 0.60425 | 122.4564 | 69.7952 | 120.9274 | 122.9279 | 0.62714 | 122.6028 | 116.7755 | -0.29297 | 122.9279 | 0.62714 | 116.7755 | 120.9274 | 122.6028 | -122.3557 | -122.6715
2869.9062 | 122.7585 | -63.5147 | 58.7906 | 0.049896 | 0.0036572 | 0.0038816 | 0.011805 | -0.0030484 | -0.0013609 | 0.0051205 | -61.409 | 61.1114 | -61.8713 | 59.8389 | 57.8751 | 54.7211 | 59.1293 | 5.7907 | 59.4543 | -63.6154 | 1.6434 | 2.3209 | 2.1057 | 123.3536 | -0.91553 | -0.10071 | 0.66376 | 0.46234 | 122.644 | 69.3054 | 121.3898 | 124.6262 | 2.1057 | 122.9691 | 118.2358 | -0.10071 | 124.6262 | 2.1057 | 118.2358 | 121.3898 | 122.9691 | -120.6619 | -122.406
2870.9062 | 122.7493 | -64.2288 | 58.374 | 0.011749 | 0.004939 | 0.0062314 | 0.010523 | -0.002194 | -0.0026425 | 0.0027707 | -63.5147 | 58.992 | -64.0366 | 58.6853 | 56.8863 | 53.2562 | 58.3511 | 5.7449 | 58.4839 | -64.5676 | 0.19226 | 0.61798 | 0.71411 | 122.9141 | -1.4877 | -0.33875 | 0.10986 | 0.52185 | 122.58 | 69.9738 | 121.1151 | 123.2208 | 0.71411 | 122.7127 | 117.485 | -0.33875 | 123.2208 | 0.71411 | 117.485 | 121.1151 | 122.7127 | -122.4106 | -122.9416
2871.9062 | 122.7127 | -62.146 | 60.4797 | 0.12619 | 0.0062208 | 0.0023862 | 0.010309 | -0.0013394 | -0.0037107 | 0.0044797 | -62.3932 | 60.0174 | -63.1348 | 59.3857 | 58.3878 | 56.3553 | 60.8231 | 6.9397 | 60.3607 | -62.4893 | -0.98877 | -0.46234 | -0.24719 | 121.5317 | -2.092 | -0.34332 | -0.11902 | 0.74158 | 122.9691 | 69.0857 | 120.5338 | 122.1634 | -0.24719 | 122.5067 | 118.5013 | -0.34332 | 122.1634 | -0.24719 | 118.5013 | 120.5338 | 122.5067 | -123.6145 | -122.9691
2872.9062 | 122.7081 | -61.0291 | 61.615 | 0.080414 | 0.0045118 | 0.0038816 | 0.0075323 | -0.0028348 | -0.0030697 | 0.0044797 | -60.4111 | 61.8622 | -61.0153 | 61.9537 | 60.1501 | 56.662 | 61.3266 | 6.8893 | 61.7065 | -61.1938 | 0.013733 | 0.24719 | 0.61798 | 122.9828 | -1.4648 | -0.1648 | 0.091553 | 0.60425 | 122.3557 | 67.9184 | 121.1792 | 122.8912 | 0.61798 | 122.7356 | 117.691 | -0.1648 | 122.8912 | 0.61798 | 117.691 | 121.1792 | 122.7356 | -122.6303 | -122.8088
2873.9062 | 122.8775 | -63.6841 | 58.8181 | 0.21011 | 0.0045118 | 0.0058042 | 0.0066779 | -0.00091219 | -0.00093346 | 0.0049069 | -63.414 | 59.2346 | -63.7985 | 59.3033 | 57.4997 | 54.4006 | 58.4976 | 6.4774 | 58.8867 | -64.032 | -0.11444 | 0.41657 | 0.27008 | 122.9874 | -1.3184 | -0.3479 | 0.068665 | 0.38452 | 122.1817 | 70.1614 | 121.1838 | 122.9187 | 0.27008 | 122.5708 | 118.0847 | -0.3479 | 122.9187 | 0.27008 | 118.0847 | 121.1838 | 122.5708 | -122.6166 | -122.85
2874.9062 | 122.7859 | -60.6949 | 61.7294 | 0.0041197 | 0.0060072 | 0.0045224 | 0.010096 | 0.00058321 | -7.9062e-05 | 0.0057615 | -60.2829 | 62.1048 | -60.8734 | 62.0911 | 60.3241 | 57.3532 | 61.8118 | 7.576 | 61.9354 | -61.0245 | -0.17853 | 0.37537 | 0.41199 | 122.7859 | -1.4053 | -0.32959 | 0.20599 | 0.59051 | 122.5067 | 68.2709 | 121.019 | 122.7997 | 0.41199 | 122.6303 | 118.0481 | -0.32959 | 122.7997 | 0.41199 | 118.0481 | 121.019 | 122.6303 | -122.6028 | -122.7539
2875.9062 | 122.7814 | -61.3953 | 61.1572 | 0.0041197 | 0.0025892 | 0.0079404 | 0.0071051 | 0.00036961 | -7.9062e-05 | 0.0053343 | -60.672 | 61.6882 | -61.2946 | 61.8668 | 60.141 | 55.9204 | 61.0428 | 6.9397 | 61.4136 | -61.734 | 0.10071 | 0.53101 | 0.72327 | 123.262 | -1.0162 | -0.33875 | 0.25635 | 0.62256 | 122.4381 | 68.335 | 121.5363 | 123.0835 | 0.72327 | 122.8088 | 117.3157 | -0.33875 | 123.0835 | 0.72327 | 117.3157 | 121.5363 | 122.8088 | -122.4518 | -122.8912
2876.9062 | 122.8043 | -61.7706 | 61.0519 | -0.13321 | 0.0028028 | -0.001459 | 0.0068915 | -0.00048499 | -0.0024289 | 0.0036253 | -63.2355 | 59.2987 | -63.5925 | 59.4681 | 57.8201 | 55.8563 | 59.6649 | 7.1503 | 60.0082 | -62.5854 | -1.8219 | -1.7532 | -1.4648 | 121.2387 | -3.2318 | -0.81482 | -1.0437 | 0.35705 | 121.4355 | 68.9209 | 119.5908 | 121.0693 | -1.4648 | 121.7789 | 117.627 | -0.81482 | 121.0693 | -1.4648 | 117.627 | 119.5908 | 121.7789 | -124.6445 | -123.6374
2877.9062 | 122.8134 | -61.6928 | 60.9558 | -0.19424 | 0.0053662 | 0.0015316 | 0.0083869 | -0.0013394 | -0.0017881 | 0.0046933 | -61.3678 | 61.1069 | -61.9034 | 60.91 | 59.2392 | 56.8176 | 60.7407 | 7.1274 | 60.8917 | -62.0132 | -0.21057 | 0.15106 | 0.32501 | 122.6028 | -1.7166 | -0.32043 | -0.064087 | 0.53558 | 122.4335 | 68.8202 | 120.932 | 122.7997 | 0.32501 | 122.5845 | 118.5104 | -0.32043 | 122.7997 | 0.32501 | 118.5104 | 120.932 | 122.5845 | -122.8592 | -122.9691
2878.9062 | 122.7814 | -60.7864 | 61.7935 | 0.027008 | 0.004939 | 0.0038816 | 0.0066779 | 0.001224 | -0.0011471 | 0.0040525 | -61.0886 | 61.4456 | -61.5143 | 61.7661 | 60.1135 | 57.5958 | 61.7386 | 7.3883 | 61.8301 | -61.1023 | -0.72784 | -0.3479 | -0.30212 | 122.5525 | -1.68 | -0.31586 | 0.036621 | 0.42572 | 122.525 | 68.1747 | 120.9 | 122.2321 | -0.30212 | 122.6166 | 118.3823 | -0.31586 | 122.2321 | -0.30212 | 118.3823 | 120.9 | 122.6166 | -123.3078 | -122.8958
2879.9062 | 122.8729 | -60.4248 | 62.1277 | -0.11795 | 0.0060072 | 0.0051632 | 0.0053961 | 0.001224 | -0.0028561 | 0.0061887 | -60.2829 | 62.0636 | -60.8917 | 62.5534 | 60.6583 | 60.0723 | 62.0819 | 7.4799 | 62.2467 | -60.704 | -0.46692 | -0.064087 | 0.14191 | 122.9782 | -1.4694 | -0.27924 | 0.11902 | 0.60883 | 122.5067 | 67.9047 | 121.0831 | 122.4884 | 0.14191 | 122.6715 | 120.4971 | -0.27924 | 122.4884 | 0.14191 | 120.4971 | 121.0831 | 122.6715 | -123.0194 | -122.8317
2880.9062 | 122.7859 | -62.1277 | 60.5118 | -0.13321 | 0.0019482 | 0.0043088 | 0.0083869 | -0.001553 | -0.0022153 | 0.0053343 | -61.3541 | 60.8963 | -62.0682 | 60.2051 | 59.2804 | 55.6915 | 61.0565 | 6.8115 | 60.6628 | -62.3657 | 0.05951 | 0.38452 | 0.77362 | 122.3328 | -1.2314 | -0.23804 | 0.15106 | 0.71411 | 123.1842 | 68.9392 | 121.4081 | 123.024 | 0.77362 | 122.7905 | 117.8192 | -0.23804 | 123.024 | 0.77362 | 117.8192 | 121.4081 | 122.7905 | -122.58 | -122.8775
2881.9062 | 122.7997 | -60.4477 | 62.178 | -0.026398 | 0.0053662 | 0.0028134 | 0.0066779 | 0.00036961 | 0.00077554 | 0.0046933 | -60.4706 | 61.9354 | -61.0016 | 61.9766 | 60.5438 | 57.5272 | 62.1185 | 7.489 | 62.1689 | -60.8047 | -0.55389 | -0.24262 | -0.022888 | 122.4243 | -1.6342 | -0.35706 | -0.009156 | 0.53101 | 122.5662 | 67.9367 | 120.9915 | 122.3831 | -0.022888 | 122.6166 | 117.9749 | -0.35706 | 122.3831 | -0.022888 | 117.9749 | 120.9915 | 122.6166 | -123.1796 | -122.9828
2882.9062 | 122.8088 | -62.915 | 59.729 | -0.18662 | 0.0042982 | 0.001318 | 0.0030463 | -0.0024076 | -0.00050626 | 0.0023435 | -62.6358 | 59.935 | -63.0798 | 59.8846 | 58.223 | 54.0024 | 59.9945 | 6.5231 | 59.9487 | -63.089 | -0.16479 | 0.20599 | 0.27924 | 122.7997 | -1.506 | -0.17395 | 0.21973 | 0.44403 | 122.9095 | 69.4382 | 121.138 | 122.85 | 0.27924 | 122.8638 | 116.9174 | -0.17395 | 122.85 | 0.27924 | 116.9174 | 121.138 | 122.8638 | -122.8088 | -122.818
2883.9062 | 122.7585 | -59.7198 | 62.8967 | 0.12619 | 0.0045118 | 0.004736 | 0.0073187 | -0.0019802 | -0.0022153 | 0.0059751 | -59.4864 | 63.0569 | -59.9808 | 62.8281 | 61.0474 | 58.5388 | 62.764 | 7.3792 | 62.9333 | -59.9945 | -0.26092 | 0.16022 | 0.23346 | 122.5479 | -1.8494 | -0.27466 | 0.036621 | 0.49438 | 122.4838 | 67.099 | 120.7672 | 122.7768 | 0.23346 | 122.6532 | 118.2587 | -0.27466 | 122.7768 | 0.23346 | 118.2587 | 120.7672 | 122.6532 | -122.8775 | -122.8912
2884.9062 | 122.7173 | -63.0386 | 59.5367 | -0.20187 | 0.0023756 | 0.0028134 | 0.0019781 | -0.00048499 | 0.00077554 | 0.0057615 | -62.1368 | 60.1547 | -62.6907 | 59.8801 | 58.0353 | 55.3619 | 59.3719 | 6.1295 | 59.6237 | -63.3728 | 0.3479 | 0.61798 | 0.90179 | 122.9187 | -1.5015 | -0.33417 | 0.086975 | 0.55389 | 122.4106 | 69.1681 | 121.0739 | 123.1934 | 0.90179 | 122.6624 | 118.4006 | -0.33417 | 123.1934 | 0.90179 | 118.4006 | 121.0739 | 122.6624 | -122.2275 | -122.9095
2885.9062 | 122.7951 | -61.6974 | 60.7452 | -0.65964 | 0.0042982 | 0.0025998 | 0.0032599 | -0.0026212 | -0.00071986 | 0.0046933 | -59.3811 | 63.1851 | -59.8206 | 63.1851 | 61.3266 | 57.0328 | 60.7178 | 5.7678 | 61.7615 | -61.5784 | 1.8768 | 2.4399 | 2.3163 | 124.8825 | 0.58136 | 0.11902 | 1.0162 | 0.43945 | 122.4152 | 67.4652 | 123.024 | 124.8825 | 2.3163 | 123.4589 | 118.7302 | 0.11902 | 124.8825 | 2.3163 | 118.7302 | 123.024 | 123.4589 | -120.5658 | -122.3236
2886.9062 | 122.8088 | -63.3041 | 59.2575 | -0.16373 | 0.0028028 | 0.0058042 | 0.0056097 | -0.0047574 | -0.0011471 | 0.0057615 | -60.5072 | 61.8073 | -61.29 | 59.5184 | 57.9483 | 58.049 | 59.2667 | 6.0837 | 59.4727 | -63.5468 | 2.0142 | 2.5497 | 2.7969 | 122.8226 | -1.3092 | -0.24262 | 0.21515 | 0.78278 | 122.5708 | 69.3878 | 121.2524 | 125.1114 | 2.7969 | 122.7768 | 121.3531 | -0.24262 | 125.1114 | 2.7969 | 121.3531 | 121.2524 | 122.7768 | -120.5475 | -122.8043
2887.9062 | 122.7631 | -63.62 | 58.9828 | -0.17899 | 0.0025892 | 0.00089078 | 0.0045417 | -0.0028348 | -0.0013609 | 0.0051205 | -63.0478 | 59.2392 | -63.7527 | 59.2209 | 57.4905 | 53.0045 | 58.8547 | 5.9921 | 59.0057 | -63.9633 | -0.13275 | 0.25635 | 0.5722 | 122.8409 | -1.4923 | -0.34332 | 0.022888 | 0.70496 | 122.4747 | 69.6121 | 121.1105 | 122.8592 | 0.5722 | 122.6257 | 116.6245 | -0.34332 | 122.8592 | 0.5722 | 116.6245 | 121.1105 | 122.6257 | -122.7356 | -122.9462
2888.9062 | 122.8363 | -59.8068 | 62.8647 | 0.19485 | 0.0038708 | 0.0032406 | 0.0077459 | -0.0028348 | -0.00029266 | 0.0057615 | -60.0677 | 62.3749 | -60.878 | 62.7045 | 61.0657 | 60.3973 | 62.5488 | 7.6721 | 62.6541 | -60.228 | -1.0712 | -0.48981 | -0.26093 | 122.5113 | -1.799 | -0.42114 | -0.21057 | 0.81024 | 122.3557 | 67.4789 | 120.8725 | 122.1817 | -0.26093 | 122.4609 | 120.2042 | -0.42114 | 122.1817 | -0.26093 | 120.2042 | 120.8725 | 122.4609 | -123.7427 | -123.0927
2889.9062 | 122.7951 | -61.6516 | 60.8093 | -0.14847 | 0.0010938 | 0.0023862 | 0.0039007 | -0.0056118 | -0.0015745 | 0.0027707 | -61.203 | 61.2305 | -61.3495 | 61.3953 | 59.404 | 58.255 | 61.2762 | 6.7154 | 61.2442 | -61.8301 | 0.30212 | 0.42114 | 0.44861 | 123.0469 | -1.4053 | -0.17853 | 0.43488 | 0.14648 | 122.9279 | 68.367 | 121.0556 | 122.8821 | 0.44861 | 122.8958 | 119.9066 | -0.17853 | 122.8821 | 0.44861 | 119.9066 | 121.0556 | 122.8958 | -122.1588 | -122.6395
2890.9062 | 122.8134 | -58.9233 | 63.6383 | -0.21713 | 2.5564e-05 | -0.0010318 | 0.0045417 | -0.0045438 | 0.00056194 | 0.0066159 | -58.7952 | 63.5193 | -59.3994 | 63.7527 | 61.9904 | 58.2367 | 63.4735 | 7.869 | 63.6017 | -59.3216 | -0.47607 | -0.11902 | 0.12817 | 122.6761 | -1.648 | -0.39825 | -0.036621 | 0.60425 | 122.3969 | 66.7923 | 120.9137 | 122.4426 | 0.12817 | 122.525 | 117.16 | -0.39825 | 122.4426 | 0.12817 | 117.16 | 120.9137 | 122.525 | -123.0377 | -122.9599
2891.9062 | 122.8821 | -61.5784 | 61.0519 | -0.14084 | -0.00082884 | 0.0028134 | 0.0028327 | -0.004971 | 0.00013454 | 0.0042661 | -61.1572 | 61.0794 | -61.821 | 61.0474 | 59.4727 | 57.019 | 60.8368 | 6.7612 | 60.965 | -61.9675 | -0.24262 | 0.027466 | 0.42114 | 122.6257 | -1.5793 | -0.3891 | -0.086975 | 0.66376 | 122.4152 | 68.3395 | 121.051 | 122.6578 | 0.42114 | 122.5433 | 118.5974 | -0.3891 | 122.6578 | 0.42114 | 118.5974 | 121.051 | 122.5433 | -122.8729 | -123.0194
2892.9062 | 122.7585 | -62.6587 | 60.0266 | -0.34683 | 0.0013074 | -0.00060462 | 0.0045417 | -0.0060392 | 0.0012027 | 0.0040525 | -59.23 | 63.2217 | -60.1227 | 59.8618 | 58.049 | 56.868 | 59.5917 | 6.2439 | 59.8984 | -63.089 | 2.536 | 3.1952 | 3.4286 | 122.5204 | -1.9775 | -0.4303 | -0.12817 | 0.89264 | 122.2504 | 68.9026 | 120.7077 | 125.8804 | 3.4286 | 122.5571 | 119.5267 | -0.4303 | 125.8804 | 3.4286 | 119.5267 | 120.7077 | 122.5571 | -120.1492 | -123.1155
2893.9062 | 122.7905 | -62.3657 | 60.2875 | -0.20187 | 0.0042982 | 0.0060178 | 0.010737 | -0.0056118 | -0.00050626 | 0.0023435 | -61.9492 | 60.5347 | -62.4298 | 60.3928 | 58.6029 | 57.1106 | 59.8709 | 6.7108 | 60.1822 | -62.8006 | -0.064087 | 0.24719 | 0.41657 | 122.7585 | -1.6846 | -0.43487 | -0.10529 | 0.48065 | 122.2366 | 69.0765 | 120.9686 | 122.9004 | 0.41657 | 122.5479 | 119.4763 | -0.43487 | 122.9004 | 0.41657 | 119.4763 | 120.9686 | 122.5479 | -122.7173 | -123.0881
2894.9062 | 122.7859 | -60.585 | 62.0636 | -0.23239 | 0.0023756 | 0.00089078 | 0.0056097 | -0.0034756 | -0.0017881 | 0.0044797 | -61.5646 | 60.4935 | -62.4435 | 62.5397 | 61.1069 | 58.3878 | 62.233 | 7.7591 | 62.1735 | -60.7636 | -1.8585 | -1.5701 | -0.97961 | 123.1247 | -0.95673 | -0.17853 | 0.10986 | 0.87891 | 122.818 | 68.3441 | 121.6919 | 121.0785 | -0.97961 | 122.7585 | 118.9728 | -0.17853 | 121.0785 | -0.97961 | 118.9728 | 121.6919 | 122.7585 | -124.5071 | -122.8271
2895.9062 | 122.8363 | -62.3749 | 60.26 | -0.25528 | -0.00018804 | 0.00089078 | 0.0028327 | -0.0045438 | -0.0017881 | 0.0036253 | -62.1231 | 60.2142 | -62.7228 | 60.3241 | 58.7036 | 57.4814 | 60.0037 | 6.7978 | 60.173 | -62.7731 | -0.3479 | -0.045777 | 0.25177 | 122.699 | -1.5564 | -0.39825 | -0.086975 | 0.59967 | 122.3785 | 69.1727 | 121.0785 | 122.5891 | 0.25177 | 122.5479 | 119.8563 | -0.39825 | 122.5891 | 0.25177 | 119.8563 | 121.0785 | 122.5479 | -122.9828 | -123.0331
2896.9062 | 122.8455 | -61.5417 | 61.0107 | -0.21713 | 0.0023756 | 0.0034544 | 0.0028327 | -0.0056118 | -0.0022153 | 0.0027707 | -61.4227 | 60.9009 | -61.9354 | 61.0474 | 59.4086 | 58.6121 | 60.8459 | 7.2189 | 61.0153 | -61.853 | -0.39368 | -0.10986 | 0.11902 | 122.5891 | -1.6022 | -0.31128 | 0.004578 | 0.5127 | 122.3877 | 68.7607 | 120.9503 | 122.4426 | 0.11902 | 122.5571 | 120.1538 | -0.31128 | 122.4426 | 0.11902 | 120.1538 | 120.9503 | 122.5571 | -122.9462 | -122.8638
2897.9062 | 122.9919 | -60.6628 | 61.7615 | -0.10269 | 0.00045296 | -0.0029544 | 5.5496e-05 | -0.010098 | -7.9062e-05 | 0.0057615 | -60.4477 | 61.7889 | -61.0382 | 61.2808 | 59.6695 | 59.5413 | 61.5784 | 7.2556 | 61.6516 | -61.1481 | -0.37537 | 0.027465 | 0.21515 | 121.9437 | -2.092 | -0.48523 | -0.10986 | 0.59051 | 122.2412 | 67.9184 | 120.3323 | 122.4518 | 0.21515 | 122.3145 | 120.2042 | -0.48523 | 122.4518 | 0.21515 | 120.2042 | 120.3323 | 122.3145 | -122.7997 | -122.9095
2898.9062 | 122.8226 | -62.0224 | 60.6628 | -0.19424 | 0.0017346 | 0.005377 | 0.0094549 | -0.0081754 | -0.0011471 | 0.0066159 | -61.6882 | 61.0245 | -61.972 | 61.2854 | 59.2575 | 58.6212 | 60.2875 | 6.1752 | 60.5392 | -62.4023 | 0.050354 | 0.36163 | 0.33417 | 123.3078 | -1.4053 | -0.37994 | -0.1236 | 0.28381 | 122.3099 | 68.1976 | 121.2799 | 123.0469 | 0.33417 | 122.5616 | 120.6436 | -0.37994 | 123.0469 | 0.33417 | 120.6436 | 121.2799 | 122.5616 | -122.6349 | -123.0652
2899.9062 | 122.7356 | -61.9171 | 60.5621 | -0.20187 | 0.001521 | 0.0049496 | 0.0051825 | -0.00668 | 0.00013454 | 0.0031979 | -61.4502 | 61.0153 | -61.9446 | 60.9787 | 59.3445 | 59.198 | 60.7773 | 7.0129 | 60.9558 | -62.0132 | -0.027466 | 0.45319 | 0.46692 | 122.8958 | -1.2177 | -0.096131 | 0.39368 | 0.49439 | 122.6944 | 68.9301 | 121.2616 | 122.9324 | 0.46692 | 122.8729 | 121.1151 | -0.096131 | 122.9324 | 0.46692 | 121.1151 | 121.2616 | 122.8729 | -122.5067 | -122.5754
2900.9062 | 122.8226 | -62.2009 | 60.4477 | -0.17136 | 0.0013074 | 0.00067718 | 0.0053961 | -0.0034756 | -0.00093346 | 0.0040525 | -61.9171 | 60.2234 | -62.6175 | 60.2966 | 59.1202 | 59.4131 | 60.6903 | 6.7383 | 60.5484 | -62.4252 | -0.41657 | -0.2243 | 0.28381 | 122.4976 | -1.3275 | -0.2243 | 0.10071 | 0.70038 | 122.8912 | 68.9392 | 121.3211 | 122.4243 | 0.28381 | 122.7493 | 121.6141 | -0.2243 | 122.4243 | 0.28381 | 121.6141 | 121.3211 | 122.7493 | -123.0652 | -122.8729
2901.9062 | 122.8683 | -61.8301 | 60.6674 | -0.20187 | 0.00023916 | 0.00089078 | 0.0047553 | -0.0062528 | -7.9062e-05 | 0.0036253 | -61.4914 | 60.7498 | -62.0682 | 61.2076 | 59.3124 | 58.9554 | 60.7773 | 6.5186 | 60.9604 | -62.027 | -0.23804 | 0.082398 | 0.33875 | 123.0377 | -1.355 | -0.19684 | 0.29297 | 0.57678 | 122.6074 | 68.3487 | 121.1426 | 122.58 | 0.33875 | 122.7905 | 120.7855 | -0.19684 | 122.58 | 0.33875 | 120.7855 | 121.1426 | 122.7905 | -122.7356 | -122.6944
2902.9062 | 122.8729 | -57.811 | 64.7324 | -0.2858 | 0.0013074 | 0.00089078 | 0.0047553 | -0.0058256 | -0.00093346 | 0.0031979 | -57.5592 | 64.7919 | -58.0673 | 64.769 | 63.0798 | 62.1048 | 64.5126 | 7.7774 | 64.6774 | -58.1955 | -0.25635 | 0.059509 | 0.25177 | 122.58 | -1.6525 | -0.38452 | -0.054932 | 0.50812 | 122.3236 | 65.5884 | 120.8908 | 122.6028 | 0.25177 | 122.4884 | 119.9158 | -0.38452 | 122.6028 | 0.25177 | 119.9158 | 120.8908 | 122.4884 | -122.7997 | -122.9279
2903.9062 | 122.7768 | -62.3886 | 60.2188 | -0.26291 | 0.0040846 | 0.003668 | 0.0066779 | -0.0073208 | 0.00013454 | 0.0021299 | -62.4207 | 59.9945 | -62.9288 | 60.4889 | 58.7677 | 57.8156 | 60.0952 | 6.3171 | 60.2554 | -62.7502 | -0.54016 | -0.2243 | -0.032043 | 122.8775 | -1.4511 | -0.36163 | 0.036621 | 0.50812 | 122.4838 | 68.7057 | 121.1563 | 122.3831 | -0.032043 | 122.644 | 120.2042 | -0.36163 | 122.3831 | -0.032043 | 120.2042 | 121.1563 | 122.644 | -123.1476 | -122.9691
2904.9062 | 122.9187 | -62.0773 | 60.4294 | -0.064545 | -0.00040164 | -0.001459 | 0.0024053 | -0.0060392 | 0.00013454 | 0.0038389 | -61.4685 | 60.5988 | -62.1231 | 61.2762 | 59.5871 | 58.4244 | 60.3928 | 6.5964 | 60.7315 | -62.2421 | -0.045776 | 0.16937 | 0.60883 | 123.3536 | -0.84228 | -0.16479 | 0.30212 | 0.6546 | 122.4701 | 68.6737 | 121.6644 | 122.6761 | 0.60883 | 122.8088 | 120.5017 | -0.16479 | 122.6761 | 0.60883 | 120.5017 | 121.6644 | 122.8088 | -122.5525 | -122.6715
2905.9062 | 122.8775 | -60.2921 | 62.2513 | -0.056915 | 0.00066656 | 0.00024998 | 0.0036871 | -0.0062528 | 0.0014163 | 0.0023435 | -59.9945 | 62.2513 | -60.5392 | 62.1002 | 60.5301 | 60.1913 | 62.2238 | 7.3975 | 62.2101 | -60.6079 | -0.24719 | 0 | 0.29755 | 122.3923 | -1.7212 | -0.31586 | -0.041199 | 0.54474 | 122.5159 | 67.6895 | 120.8221 | 122.5433 | 0.29755 | 122.5021 | 120.4834 | -0.31586 | 122.5433 | 0.29755 | 120.4834 | 120.8221 | 122.5021 | -122.7905 | -122.8592
2906.9062 | 122.8912 | -58.461 | 64.1739 | -0.064545 | 0.0010938 | 0.001959 | 0.0043281 | -0.008389 | 0.00077554 | 0.0055479 | -58.7494 | 63.6154 | -59.2209 | 64.2746 | 62.5946 | 62.5076 | 63.8031 | 8.0017 | 64.0411 | -58.8135 | -0.75989 | -0.55847 | -0.28839 | 122.7356 | -1.5793 | -0.35248 | -0.13275 | 0.4715 | 122.2641 | 66.4627 | 121.0556 | 122.0764 | -0.28839 | 122.5021 | 120.9686 | -0.35248 | 122.0764 | -0.28839 | 120.9686 | 121.0556 | 122.5021 | -123.3948 | -122.9874
2907.9062 | 122.9324 | -62.0682 | 60.4568 | -0.65964 | 0.0025892 | 0.00067718 | 0.0028327 | -0.0077482 | -0.00093346 | 0.0027707 | -61.7889 | 60.4843 | -62.3932 | 60.791 | 59.1705 | 57.0007 | 60.2417 | 6.7429 | 60.4706 | -62.3886 | -0.32501 | 0.027466 | 0.27924 | 122.8592 | -1.2863 | -0.32043 | 0.013733 | 0.60425 | 122.3099 | 68.811 | 121.2387 | 122.5525 | 0.27924 | 122.5388 | 119.0689 | -0.32043 | 122.5525 | 0.27924 | 119.0689 | 121.2387 | 122.5388 | -122.85 | -122.8455
2908.9219 | 122.8271 | -61.8347 | 60.8002 | -0.064545 | 0.00323 | 0.0058042 | 0.011164 | -0.0060392 | -0.00093346 | 0.0010617 | -61.6653 | 60.6628 | -62.2925 | 60.6766 | 58.9554 | 57.6462 | 60.5255 | 6.6879 | 60.6628 | -62.2421 | -0.45776 | -0.13733 | 0.16937 | 122.5113 | -1.8448 | -0.40741 | -0.13733 | 0.62714 | 122.3602 | 68.5226 | 120.7901 | 122.4976 | 0.16937 | 122.4976 | 119.4809 | -0.40741 | 122.4976 | 0.16937 | 119.4809 | 120.7901 | 122.4976 | -123.0927 | -123.0423
2909.9062 | 122.9187 | -61.2717 | 61.2717 | -0.17136 | -0.0010424 | 0.0017454 | 0.0026191 | -0.0041166 | -0.00029266 | 0.0031979 | -61.8622 | 60.4431 | -62.4161 | 60.9879 | 59.5367 | 58.4976 | 61.4548 | 6.871 | 61.0794 | -61.7386 | -1.1444 | -0.82855 | -0.59052 | 122.2595 | -1.7349 | -0.46692 | -0.19226 | 0.55389 | 122.7264 | 68.1427 | 120.8084 | 121.7148 | -0.59052 | 122.3511 | 119.7693 | -0.46692 | 121.7148 | -0.59052 | 119.7693 | 120.8084 | 122.3511 | -123.6877 | -123.0103
2910.9062 | 122.9233 | -61.2167 | 61.2946 | -0.087433 | 0.0010938 | 0.003027 | 0.0028327 | -0.0077482 | 0.00013454 | 0.0029843 | -61.0245 | 61.4044 | -61.5143 | 61.3449 | 59.6191 | 59.3124 | 60.9787 | 6.7703 | 61.1801 | -61.6104 | -0.29755 | 0.10986 | 0.19226 | 122.5616 | -1.6754 | -0.39368 | -0.11444 | 0.48981 | 122.1954 | 67.9871 | 120.8359 | 122.6212 | 0.19226 | 122.3969 | 120.5292 | -0.39368 | 122.6212 | 0.19226 | 120.5292 | 120.8359 | 122.3969 | -122.8088 | -122.905
2911.9062 | 122.9141 | -62.6175 | 59.8114 | -0.072174 | 0.0010938 | 0.0011044 | 0.0047553 | -0.0077482 | -0.0013609 | 0.0049069 | -62.0316 | 60.2509 | -62.4939 | 59.7565 | 58.3282 | 57.8522 | 59.9304 | 6.3309 | 59.9304 | -62.9425 | 0.1236 | 0.43945 | 0.58594 | 122.374 | -1.4832 | -0.32501 | 0.11902 | 0.46234 | 122.5479 | 68.9484 | 120.9457 | 122.8683 | 0.58594 | 122.5479 | 120.4697 | -0.32501 | 122.8683 | 0.58594 | 120.4697 | 120.9457 | 122.5479 | -122.3053 | -122.7539
2912.9062 | 122.9187 | -61.4182 | 61.0794 | 0.042267 | 0.00088016 | 0.00024998 | 0.0043281 | -0.0086026 | -0.00050626 | 0.0010617 | -61.3266 | 60.9558 | -61.9171 | 61.4868 | 59.8251 | 58.3328 | 60.8963 | 6.7657 | 61.171 | -61.6333 | -0.49896 | -0.1236 | 0.091553 | 122.905 | -1.2543 | -0.21515 | 0.091552 | 0.59051 | 122.3145 | 68.1839 | 121.2433 | 122.374 | 0.091553 | 122.5891 | 119.751 | -0.21515 | 122.374 | 0.091553 | 119.751 | 121.2433 | 122.5891 | -122.9965 | -122.7127
2913.9062 | 122.8043 | -61.3083 | 61.3632 | -0.29343 | 2.5564e-05 | 0.0011044 | 0.0034735 | -0.008389 | -0.0030697 | 0.0044797 | -61.0657 | 61.2717 | -61.6196 | 61.3678 | 59.8526 | 58.9188 | 61.0657 | 6.6559 | 61.2167 | -61.702 | -0.31128 | -0.091553 | 0.24262 | 122.6761 | -1.5106 | -0.39368 | -0.14648 | 0.55389 | 122.374 | 67.9642 | 121.1609 | 122.58 | 0.24262 | 122.525 | 120.2271 | -0.39368 | 122.58 | 0.24262 | 120.2271 | 121.1609 | 122.525 | -122.9828 | -123.0652
2914.9062 | 122.9004 | -61.3861 | 61.1847 | -0.16373 | 2.5564e-05 | 0.00024998 | 0.0036871 | -0.0073208 | 0.00098914 | 0.0040525 | -61.2854 | 61.0336 | -61.8256 | 61.5234 | 59.8938 | 59.0927 | 60.9146 | 6.3446 | 61.1252 | -61.8164 | -0.43945 | -0.15106 | 0.10071 | 122.9095 | -1.2909 | -0.4303 | -0.059509 | 0.54016 | 122.3007 | 67.7307 | 121.2799 | 122.4197 | 0.10071 | 122.5113 | 120.4788 | -0.4303 | 122.4197 | 0.10071 | 120.4788 | 121.2799 | 122.5113 | -123.0103 | -123.0011
2915.9062 | 122.905 | -60.7452 | 61.8713 | -0.034027 | 2.5564e-05 | 0.0015316 | 0.0034735 | -0.0062528 | -0.00029266 | 0.0049069 | -61.0931 | 61.3907 | -61.5509 | 61.8942 | 60.022 | 59.1339 | 61.3083 | 6.6101 | 61.5738 | -61.1618 | -0.80566 | -0.48065 | -0.3479 | 122.6395 | -1.8494 | -0.41656 | -0.29755 | 0.45776 | 122.0535 | 67.3553 | 120.7672 | 122.1359 | -0.3479 | 122.319 | 119.8791 | -0.41656 | 122.1359 | -0.3479 | 119.8791 | 120.7672 | 122.319 | -123.4222 | -123.0331
2916.9219 | 122.7951 | -62.3428 | 60.3561 | -0.041657 | 0.0064344 | 0.001959 | 0.0133 | -0.0045438 | 0.00077554 | 0.0034115 | -62.0636 | 60.228 | -62.709 | 60.1364 | 58.5983 | 57.1609 | 59.903 | 6.2714 | 60.054 | -62.8326 | -0.36621 | -0.12817 | 0.27923 | 122.4792 | -1.7578 | -0.48981 | -0.30212 | 0.64545 | 122.2458 | 68.6142 | 120.9412 | 122.5708 | 0.27923 | 122.3969 | 119.5038 | -0.48981 | 122.5708 | 0.27923 | 119.5038 | 120.9412 | 122.3969 | -123.0652 | -123.1888
2917.9062 | 122.8546 | -61.7432 | 60.8459 | -0.0035098 | 0.0023756 | 0.0025998 | 0.0017645 | -0.0056118 | -0.0017881 | 0.0031979 | -61.6241 | 60.6674 | -62.2147 | 61.0153 | 59.3628 | 58.3282 | 60.6857 | 6.8939 | 60.8597 | -62.0316 | -0.4715 | -0.17853 | 0.11902 | 122.7585 | -1.4832 | -0.28839 | 0.013733 | 0.59051 | 122.4289 | 68.6371 | 121.106 | 122.4106 | 0.11902 | 122.6028 | 120.0714 | -0.28839 | 122.4106 | 0.11902 | 120.0714 | 121.106 | 122.6028 | -123.0606 | -122.8775
2918.9062 | 122.9279 | -61.4273 | 61.0428 | -0.24002 | 2.5564e-05 | 0.0028134 | 0.0034735 | -0.0081754 | 0.0014163 | 0.0046933 | -60.6354 | 61.4548 | -61.3403 | 61.4319 | 59.6008 | 57.4722 | 60.9283 | 6.871 | 61.1298 | -61.7249 | 0.086975 | 0.41199 | 0.79193 | 122.8592 | -1.442 | -0.29755 | 0.086975 | 0.70496 | 122.3557 | 68.2983 | 121.0281 | 122.8821 | 0.79193 | 122.5571 | 118.8995 | -0.29755 | 122.8821 | 0.79193 | 118.8995 | 121.0281 | 122.5571 | -122.3831 | -122.7676
2919.9062 | 122.8271 | -61.8668 | 60.6628 | 0.057526 | 0.00045296 | 0.0021726 | 0.0045417 | -0.0073208 | 0.0016299 | 0.0040525 | -60.7315 | 61.9766 | -61.0428 | 61.2991 | 59.3308 | 58.5114 | 61.0382 | 6.4774 | 60.997 | -61.972 | 0.82397 | 1.3138 | 1.1353 | 123.1659 | -1.3321 | -0.10529 | 0.33417 | 0.31128 | 122.905 | 68.3441 | 121.1975 | 123.8434 | 1.1353 | 122.8638 | 120.3781 | -0.10529 | 123.8434 | 1.1353 | 120.3781 | 121.1975 | 122.8638 | -121.7056 | -122.6349
2920.9062 | 122.8775 | -60.4294 | 62.1323 | 0.11856 | 0.0017346 | 0.0045224 | 0.0043281 | -0.0058256 | 0.00056194 | 0.0061887 | -62.4573 | 59.6237 | -63.1577 | 61.8576 | 60.6216 | 61.2717 | 61.7752 | 7.3654 | 61.647 | -61.0336 | -2.7283 | -2.5085 | -2.0279 | 122.287 | -1.5106 | -0.60425 | -0.48523 | 0.70038 | 122.2046 | 67.7948 | 121.051 | 120.0531 | -2.0279 | 122.0764 | 121.701 | -0.60425 | 120.0531 | -2.0279 | 121.701 | 121.051 | 122.0764 | -125.2899 | -123.1659
2921.9219 | 122.818 | -62.7686 | 59.8251 | -0.2858 | 0.0028028 | 0.0051632 | 0.0060369 | -0.00668 | -0.0022153 | 0.0029843 | -62.4161 | 60.1685 | -62.8693 | 59.9808 | 58.0719 | 58.6945 | 59.4727 | 6.102 | 59.6924 | -63.1668 | -0.10071 | 0.34332 | 0.35248 | 122.7493 | -1.7532 | -0.39825 | -0.13275 | 0.45319 | 122.2412 | 68.8705 | 120.8405 | 122.937 | 0.35248 | 122.4609 | 121.463 | -0.39825 | 122.937 | 0.35248 | 121.463 | 120.8405 | 122.4609 | -122.6944 | -122.9919
2922.9062 | 122.8592 | -62.0544 | 60.5026 | 0.1796 | 0.0017346 | 0.0025998 | 0.0060369 | -0.0081754 | -0.0011471 | 0.0038389 | -61.7157 | 60.6674 | -62.1872 | 61.1206 | 59.8801 | 59.8572 | 60.553 | 6.3492 | 60.8231 | -62.1506 | -0.13275 | 0.16479 | 0.33874 | 123.175 | -0.62256 | -0.096131 | 0.32043 | 0.4715 | 122.6074 | 68.4036 | 121.9345 | 122.7219 | 0.33874 | 122.8775 | 121.9116 | -0.096131 | 122.7219 | 0.33874 | 121.9116 | 121.9345 | 122.8775 | -122.6898 | -122.6532
2923.9062 | 122.7905 | -62.2833 | 60.6903 | 0.14908 | 0.00045296 | -0.0010318 | 0.0049689 | -0.0062528 | -0.0020017 | 0.0029843 | -62.5305 | 59.9258 | -62.9883 | 60.173 | 58.5022 | 59.2621 | 59.935 | 6.3629 | 59.9854 | -62.9105 | -0.70496 | -0.76447 | -0.24719 | 122.4564 | -2.1881 | -0.62714 | -0.70496 | 0.45776 | 122.2183 | 68.6462 | 120.7855 | 122.2092 | -0.24719 | 122.2687 | 121.5454 | -0.62714 | 122.2092 | -0.24719 | 121.5454 | 120.7855 | 122.2687 | -123.6786 | -123.6008
2924.9062 | 122.8775 | -62.6541 | 59.8938 | 0.17197 | 0.00088016 | 0.0038816 | 0.0062507 | -0.0058256 | -0.00029266 | 0.0021299 | -62.3108 | 59.9854 | -62.8738 | 60.1227 | 58.4106 | 58.9142 | 59.7061 | 6.2622 | 59.967 | -62.9196 | -0.21973 | 0.091553 | 0.34332 | 122.7768 | -1.4832 | -0.2655 | 0.073242 | 0.56305 | 122.3602 | 68.9163 | 121.0648 | 122.6395 | 0.34332 | 122.6212 | 121.5683 | -0.2655 | 122.6395 | 0.34332 | 121.5683 | 121.0648 | 122.6212 | -122.7676 | -122.8134
2925.9062 | 122.9141 | -62.233 | 60.2783 | 0.27878 | 0.00323 | 0.0077268 | 0.0086005 | -0.0041166 | -0.00050626 | 0.0049069 | -62.6083 | 59.7473 | -63.0936 | 60.6995 | 59.0607 | 57.6416 | 60.173 | 6.4636 | 60.3745 | -62.5168 | -0.8606 | -0.53101 | -0.37537 | 122.9324 | -1.2177 | -0.28381 | 0.096131 | 0.48523 | 122.406 | 68.6966 | 121.2936 | 121.9803 | -0.37537 | 122.6074 | 119.8746 | -0.28381 | 121.9803 | -0.37537 | 119.8746 | 121.2936 | 122.6074 | -123.3719 | -122.7951
2926.9062 | 122.8867 | -60.8002 | 61.8576 | -1.4226 | 0.00323 | 0.0049496 | 0.0058233 | -0.0064664 | 0.0012027 | 0.0038389 | -62.0224 | 60.6537 | -62.3291 | 61.2946 | 60.141 | 59.3948 | 61.0153 | 7.1503 | 61.2946 | -61.3449 | -1.5289 | -1.2039 | -1.2222 | 122.0947 | -1.7166 | -0.54474 | -0.56305 | 0.3067 | 121.8155 | 67.9504 | 120.9412 | 121.4539 | -1.2222 | 122.0947 | 120.195 | -0.54474 | 121.4539 | -1.2222 | 120.195 | 120.9412 | 122.0947 | -124.1867 | -123.2025
2927.9062 | 122.9004 | -61.6058 | 60.9741 | 0.3093 | 0.0036572 | 0.0049496 | 0.0062507 | -0.0073208 | 0.0016299 | 0.0044797 | -61.6196 | 60.6949 | -62.1506 | 61.2534 | 59.5322 | 58.6716 | 60.6903 | 6.4133 | 60.9055 | -61.9675 | -0.54474 | -0.27924 | -0.013733 | 122.8592 | -1.442 | -0.36163 | -0.068664 | 0.53101 | 122.2961 | 68.0191 | 121.138 | 122.3007 | -0.013733 | 122.5113 | 120.2774 | -0.36163 | 122.3007 | -0.013733 | 120.2774 | 121.138 | 122.5113 | -123.1247 | -122.9416
2928.9062 | 122.8912 | -61.7432 | 60.791 | 0.0041197 | 0.00066656 | 0.00046358 | 0.0039007 | -0.0045438 | 0.0012027 | 0.0040525 | -59.9487 | 62.2833 | -60.4202 | 61.647 | 59.2758 | 58.7997 | 60.4523 | 5.9189 | 61.1252 | -61.9263 | 1.3229 | 1.4923 | 1.7944 | 123.3902 | -1.5152 | -0.18311 | 0.33417 | 0.4715 | 122.1954 | 67.662 | 121.019 | 124.0265 | 1.7944 | 122.8683 | 120.5429 | -0.18311 | 124.0265 | 1.7944 | 120.5429 | 121.019 | 122.8683 | -121.2112 | -122.7173
2929.9062 | 122.8683 | -61.5601 | 61.2671 | 0.17197 | 0.0023756 | 0.0055906 | 0.0092413 | -0.0034756 | 0.00013454 | 0.0010617 | -61.615 | 60.9421 | -62.1048 | 60.672 | 58.9645 | 58.1635 | 60.2646 | 6.5277 | 60.4935 | -62.2101 | -0.54474 | -0.32501 | -0.054931 | 122.2321 | -2.3026 | -0.65002 | -0.77362 | 0.48981 | 121.8246 | 68.0878 | 120.5246 | 122.5021 | -0.054931 | 122.0535 | 119.7235 | -0.65002 | 122.5021 | -0.054931 | 119.7235 | 120.5246 | 122.0535 | -123.3719 | -123.4772
2930.9062 | 122.2961 | -3.241 | 118.8583 | 0.24063 | 0.0042982 | 0.003668 | 0.011591 | -0.003903 | 0.00056194 | 0.01986 | -2.948 | 119.6411 | -3.5431 | 119.7189 | 116.7023 | 115.5029 | 119.1788 | 26.4359 | 119.4901 | -3.5019 | -0.30212 | 0.78278 | 0.29297 | 122.9599 | -2.1561 | -0.26092 | 0.63171 | 0.59509 | 122.4197 | 29.6768 | 119.9432 | 122.8821 | 0.29297 | 122.731 | 118.7439 | -0.26092 | 122.8821 | 0.29297 | 118.7439 | 119.9432 | 122.731 | -122.4014 | -122.3602
2931.9062 | 122.818 | -62.9608 | 59.5367 | 0.15671 | 0.0045118 | 0.0058042 | 0.0083869 | -0.0024076 | -0.00093346 | 0.0051205 | -62.0087 | 60.3333 | -62.4985 | 60.2829 | 58.287 | 57.3944 | 59.5139 | 5.5161 | 59.8068 | -63.2401 | 0.46234 | 0.79651 | 0.95215 | 123.2437 | -1.2497 | -0.27924 | 0.27008 | 0.48981 | 122.4747 | 68.4769 | 121.2479 | 123.2941 | 0.95215 | 122.7676 | 120.3552 | -0.27924 | 123.2941 | 0.95215 | 120.3552 | 121.2479 | 122.7676 | -122.0352 | -122.7768
2932.9062 | 122.7768 | -61.2625 | 61.4777 | 0.1033 | 0.0047254 | 0.006445 | 0.010523 | -0.0053982 | -0.0022153 | 0.0042661 | -61.2122 | 61.0977 | -61.8118 | 61.2167 | 59.5413 | 58.429 | 60.9375 | 6.5323 | 61.0886 | -61.7981 | -0.54932 | -0.37994 | 0.050354 | 122.4792 | -1.9363 | -0.53558 | -0.3891 | 0.59967 | 122.2 | 67.7948 | 120.8038 | 122.3602 | 0.050354 | 122.3511 | 119.6915 | -0.53558 | 122.3602 | 0.050354 | 119.6915 | 120.8038 | 122.3511 | -123.2895 | -123.2758
2933.9062 | 122.8271 | -62.2147 | 60.3882 | 0.18723 | 0.0030164 | 0.0045224 | 0.0086005 | -0.001553 | -0.00071986 | 0.0059751 | -61.8118 | 60.6766 | -62.3154 | 60.6216 | 58.9737 | 58.2458 | 60.4202 | 6.3034 | 60.5392 | -62.4664 | -0.10071 | 0.28839 | 0.40283 | 122.8363 | -1.4145 | -0.25177 | 0.15106 | 0.50354 | 122.6349 | 68.5181 | 121.1884 | 122.8912 | 0.40283 | 122.7539 | 120.4605 | -0.25177 | 122.8912 | 0.40283 | 120.4605 | 121.1884 | 122.7539 | -122.7036 | -122.8546
2934.9062 | 122.8043 | -61.5555 | 61.0931 | 0.042267 | 0.004939 | 0.0038816 | 0.0096685 | -0.002194 | -0.0020017 | 0.0038389 | -61.4182 | 61.0748 | -61.9492 | 61.0657 | 59.6008 | 58.8593 | 61.0016 | 6.546 | 61.1069 | -61.8484 | -0.39368 | -0.018311 | 0.13733 | 122.6212 | -1.4923 | -0.29297 | 0.013733 | 0.53101 | 122.5571 | 68.1015 | 121.1563 | 122.6303 | 0.13733 | 122.6624 | 120.4147 | -0.29297 | 122.6303 | 0.13733 | 120.4147 | 121.1563 | 122.6624 | -123.0423 | -122.9416
2935.9062 | 122.731 | -61.1069 | 61.4914 | 0.14145 | 0.0075024 | 0.0072996 | 0.0088141 | 0.0016512 | 0.00098914 | 0.0034115 | -60.5392 | 62.0956 | -60.9924 | 62.0773 | 60.3058 | 58.8593 | 61.0611 | 6.546 | 61.4594 | -61.6104 | 0.11444 | 0.60425 | 0.56763 | 123.1842 | -1.1856 | -0.50354 | -0.032043 | 0.45319 | 122.168 | 67.6529 | 121.4127 | 123.2025 | 0.56763 | 122.5662 | 119.9661 | -0.50354 | 123.2025 | 0.56763 | 119.9661 | 121.4127 | 122.5662 | -122.4838 | -123.1018
2936.9062 | 122.7905 | -61.2854 | 61.3129 | 0.088043 | 0.0042982 | 0.001959 | 0.0083869 | -0.00048499 | -0.0017881 | 0.0046933 | -60.8688 | 61.5509 | -61.4365 | 61.4868 | 59.6558 | 58.8364 | 61.4777 | 6.6879 | 61.496 | -61.5097 | -0.15106 | 0.23804 | 0.41657 | 122.7722 | -1.6571 | -0.2243 | 0.18311 | 0.56763 | 122.7631 | 67.9733 | 120.9412 | 122.8363 | 0.41657 | 122.7814 | 120.1218 | -0.2243 | 122.8363 | 0.41657 | 120.1218 | 120.9412 | 122.7814 | -122.7493 | -122.8226
2937.9062 | 122.7722 | -60.6262 | 62.1597 | 0.049896 | 0.0038708 | 0.0025998 | 0.0092413 | -5.7592e-05 | -0.00050626 | 0.0057615 | -60.8231 | 61.7569 | -61.3083 | 62.0316 | 60.3012 | 59.0973 | 61.7752 | 6.8161 | 61.8622 | -61.0657 | -0.68207 | -0.40283 | -0.19684 | 122.6578 | -1.8585 | -0.43945 | -0.29755 | 0.48523 | 122.4014 | 67.4423 | 120.9274 | 122.3831 | -0.19684 | 122.4884 | 119.7235 | -0.43945 | 122.3831 | -0.19684 | 119.7235 | 120.9274 | 122.4884 | -123.468 | -123.2254
2938.9219 | 122.85 | -60.9146 | 61.6241 | 0.21011 | 0.00023916 | 0.0045224 | 0.0013373 | -0.0017666 | 0.0016299 | 0.0070431 | -60.553 | 61.6516 | -61.2259 | 61.9217 | 60.2737 | 59.7382 | 61.4319 | 6.6055 | 61.6287 | -61.2534 | -0.31128 | 0.027465 | 0.36163 | 122.8363 | -1.3504 | -0.33875 | 0.004577 | 0.67291 | 122.3465 | 67.5201 | 121.1884 | 122.5662 | 0.36163 | 122.5433 | 120.6528 | -0.33875 | 122.5662 | 0.36163 | 120.6528 | 121.1884 | 122.5433 | -122.85 | -122.8775
2939.9062 | 103.3173 | -5.3925 | 99.9664 | 0.019379 | 0.0036572 | 0.001318 | 0.010096 | -0.0036892 | -0.0011471 | 0.021142 | -4.7882 | 117.7872 | -5.3925 | 117.8009 | 114.8117 | 113.1042 | 117.3752 | 26.0422 | 117.6361 | -5.4016 | 0 | 17.8207 | 0.60425 | 123.1934 | 14.8453 | -0.009155 | 17.6697 | 0.60425 | 122.7676 | 31.4346 | 120.2042 | 123.1796 | 0.60425 | 123.0286 | 118.4967 | -0.009155 | 123.1796 | 0.60425 | 118.4967 | 120.2042 | 123.0286 | -105.3589 | -105.368
2940.9062 | 118.1259 | -4.2755 | 118.1534 | -0.11032 | 0.0042982 | 0.0094358 | 0.0081733 | -0.00048499 | 0.00056194 | 0.020715 | -3.9093 | 118.6981 | -4.4815 | 118.7714 | 115.7913 | 114.0701 | 118.2999 | 26.2711 | 118.6203 | -4.4312 | -0.20599 | 0.54474 | 0.36621 | 123.0469 | -2.3621 | -0.15564 | 0.46692 | 0.5722 | 122.5754 | 30.5466 | 120.0668 | 122.9736 | 0.36621 | 122.8958 | 118.3456 | -0.15564 | 122.9736 | 0.36621 | 118.3456 | 120.0668 | 122.8958 | -122.6349 | -122.5845
2941.9062 | 121.9894 | -3.9322 | 118.4189 | 0.065155 | 0.0062208 | 0.0025998 | 0.012659 | -0.002194 | -0.0017881 | 0.023065 | -3.5934 | 119.0094 | -4.1611 | 119.0277 | 116.0202 | 116.3086 | 118.6203 | 26.6235 | 118.8812 | -4.2023 | -0.22888 | 0.59051 | 0.33874 | 122.9599 | -2.3987 | -0.27008 | 0.46234 | 0.56763 | 122.5525 | 30.5557 | 119.9524 | 122.9416 | 0.33874 | 122.8134 | 120.2408 | -0.27008 | 122.9416 | 0.33874 | 120.2408 | 119.9524 | 122.8134 | -122.58 | -122.6212
2942.9062 | 122.1085 | -3.8589 | 118.0801 | -0.087433 | 0.0051526 | 0.0055906 | 0.011164 | -0.0019802 | -0.0013609 | 0.021997 | -3.6301 | 118.9819 | -4.216 | 119.0186 | 116.2537 | 113.9648 | 118.7759 | 27.0355 | 118.9316 | -4.1336 | -0.35705 | 0.90179 | 0.22888 | 122.8775 | -1.8265 | -0.27466 | 0.85144 | 0.58594 | 122.6349 | 30.8945 | 120.1126 | 122.8409 | 0.22888 | 122.7905 | 117.8238 | -0.27466 | 122.8409 | 0.22888 | 117.8238 | 120.1126 | 122.7905 | -122.2961 | -122.2137
2943.9062 | 122.1634 | -3.9597 | 118.5791 | -0.20187 | 0.0028028 | -0.00060462 | 0.012659 | -0.0013394 | -0.0017881 | 0.023065 | -3.6255 | 119.0094 | -4.184 | 119.0002 | 115.9973 | 113.8046 | 118.5883 | 26.8341 | 118.8675 | -4.2068 | -0.2243 | 0.4303 | 0.33417 | 122.9599 | -2.5818 | -0.24719 | 0.28839 | 0.55847 | 122.5479 | 30.7938 | 119.957 | 122.9691 | 0.33417 | 122.8271 | 117.7643 | -0.24719 | 122.9691 | 0.33417 | 117.7643 | 119.957 | 122.8271 | -122.7631 | -122.7859
2944.9062 | 122.8226 | -9.0179 | 114.3173 | -0.27054 | 0.0040846 | 0.003668 | 0.0083869 | -0.0028348 | -0.00029266 | 0.017724 | -8.4503 | 113.1454 | -10.6384 | 112.9211 | 110.5133 | 0.5722 | 113.5117 | 21.8307 | 113.2599 | -9.9106 | -1.6205 | -1.1719 | 0.56763 | 121.9391 | -3.804 | -0.89264 | -1.0574 | 2.1881 | 122.5296 | 30.8487 | 119.5312 | 122.1634 | 0.56763 | 122.2778 | 9.5901 | -0.89264 | 122.1634 | 0.56763 | 9.5901 | 119.5312 | 122.2778 | -124.9558 | -124.2279
2945.9062 | 122.4655 | -5.9647 | 116.8854 | -0.3392 | 0.0036572 | -0.00081822 | 0.0060369 | -0.003262 | -0.00093346 | 0.021997 | -5.5252 | 116.9815 | -6.2439 | 116.7892 | 113.7817 | 0.30212 | 116.6153 | 22.1466 | 116.8716 | -6.2347 | -0.27923 | 0.09613 | 0.43945 | 122.7539 | -3.1036 | -0.27008 | -0.013733 | 0.71869 | 122.58 | 28.1113 | 119.7464 | 122.9462 | 0.43945 | 122.8363 | 6.2668 | -0.27008 | 122.9462 | 0.43945 | 6.2668 | 119.7464 | 122.8363 | -123.1293 | -123.1201
2946.9062 | 122.8271 | -60.91 | 61.6837 | -0.24765 | 0.0017346 | 0.0045224 | 0.0036871 | -0.002194 | -0.00071986 | 0.0040525 | -60.4477 | 62.0819 | -60.7361 | 61.9995 | 60.0769 | 0.10986 | 61.7752 | 4.4403 | 61.8942 | -61.1069 | 0.17395 | 0.39825 | 0.46234 | 122.9095 | -1.6068 | -0.19684 | 0.21057 | 0.28839 | 122.6852 | 65.3503 | 120.9869 | 122.9919 | 0.46234 | 122.8043 | 61.0199 | -0.19684 | 122.9919 | 0.46234 | 61.0199 | 120.9869 | 122.8043 | -122.4197 | -122.7905
2947.9062 | 121.9849 | -62.0819 | 57.9666 | -1.7888 | 0.00045296 | -0.0018862 | 0.0039007 | -0.0019802 | -0.0020017 | 0.0025571 | -63.8626 | 59.0881 | -64.0778 | 59.0515 | 57.962 | 0.10986 | 59.3994 | 3.8864 | 59.3719 | -63.4735 | -1.9958 | 1.1215 | -1.7807 | 121.1334 | -0.004578 | -1.3916 | 1.4053 | 0.21515 | 121.4813 | 65.9683 | 120.0439 | 121.17 | -1.7807 | 121.4539 | 62.1918 | -1.3916 | 121.17 | -1.7807 | 62.1918 | 120.0439 | 121.4539 | -122.0444 | -121.4401
2948.9062 | 122.8043 | -60.26 | 61.8576 | -0.041657 | 0.0051526 | 0.0090086 | 0.0081733 | -0.0026212 | -0.00029266 | 0.0031979 | -60.1822 | 62.114 | -60.8368 | 62.2192 | 60.4477 | 0.091553 | 63.382 | 5.4108 | 62.915 | -60.0815 | -0.57678 | 0.25635 | 0.07782 | 122.4792 | -1.4099 | 0.17853 | 1.0574 | 0.6546 | 123.642 | 65.6708 | 120.7077 | 122.374 | 0.07782 | 123.175 | 60.3516 | 0.17853 | 122.374 | 0.07782 | 60.3516 | 120.7077 | 123.175 | -122.6944 | -121.9391
2949.9062 | 122.7173 | -59.1568 | 62.3291 | 0.90439 | 0.0028028 | 0.0015316 | 0.0017645 | -0.0043302 | 0.00034814 | 0.0042661 | -60.2325 | 62.178 | -60.8826 | 62.3108 | 60.6903 | -0.045776 | 62.8098 | 4.8798 | 62.6404 | -60.2463 | -1.7258 | -0.15106 | -1.0757 | 121.4676 | -1.6388 | -1.0895 | 0.31128 | 0.65002 | 121.9666 | 64.0366 | 119.8471 | 121.3348 | -1.0757 | 121.7972 | 59.111 | -1.0895 | 121.3348 | -1.0757 | 59.111 | 119.8471 | 121.7972 | -123.2117 | -122.5754
2950.9062 | 122.0673 | -61.5601 | 60.3973 | -0.19424 | 0.0023756 | 0.0028134 | 0.0006965 | -0.0030484 | -0.00050626 | 0.0023435 | -62.1368 | 60.4111 | -62.558 | 61.2396 | 59.5642 | 0.045776 | 60.759 | 3.978 | 60.8871 | -62.2375 | -0.99792 | 0.013733 | -0.57678 | 122.7997 | -0.83313 | -0.67749 | 0.48981 | 0.42114 | 122.319 | 65.538 | 121.1243 | 121.9711 | -0.57678 | 122.4472 | 61.6058 | -0.67749 | 121.9711 | -0.57678 | 61.6058 | 121.1243 | 122.4472 | -122.9553 | -122.6349
2951.9062 | 122.0215 | -62.1323 | 59.8297 | -0.32394 | 0.0013074 | 0.0075132 | 0.0017645 | -0.0041166 | -7.9062e-05 | 0.0038389 | -62.1185 | 60.3104 | -62.7502 | 60.2097 | 58.4564 | 0.059509 | 60.1273 | 4.0833 | 60.1547 | -62.8006 | -0.61798 | 0.48065 | 0.013733 | 122.3419 | -1.3733 | -0.66833 | 0.32501 | 0.63171 | 122.2595 | 66.2155 | 120.5887 | 122.4426 | 0.013733 | 122.287 | 62.1918 | -0.66833 | 122.4426 | 0.013733 | 62.1918 | 120.5887 | 122.287 | -122.58 | -122.6303
2952.9062 | 122.7585 | -63.002 | 59.3536 | -0.072174 | 0.00023916 | -0.00060462 | 0.0013373 | -0.0041166 | -0.00071986 | 0.0036253 | -62.7731 | 59.3811 | -63.4827 | 59.9396 | 58.1863 | 0.1831 | 59.3124 | 4.0237 | 59.5322 | -63.4003 | -0.48065 | 0.027466 | 0.22888 | 122.9416 | -1.1673 | -0.39825 | 0.17853 | 0.70953 | 122.3145 | 67.0258 | 121.1884 | 122.3831 | 0.22888 | 122.5342 | 63.1851 | -0.39825 | 122.3831 | 0.22888 | 63.1851 | 121.1884 | 122.5342 | -122.8363 | -122.7539
2953.9062 | 122.818 | -62.9288 | 59.7153 | -0.1561 | 0.0030164 | 0.00089078 | 0.0062507 | -0.0041166 | -0.0017881 | -0.00021994 | -62.851 | 59.6329 | -63.3865 | 59.4543 | 57.6553 | 0.10529 | 59.6466 | 4.0192 | 59.6008 | -63.3179 | -0.45776 | -0.082397 | 0.07782 | 122.3831 | -2.0599 | -0.3891 | -0.11444 | 0.53558 | 122.5754 | 66.9479 | 120.5841 | 122.5616 | 0.07782 | 122.5296 | 63.0341 | -0.3891 | 122.5616 | 0.07782 | 63.0341 | 120.5841 | 122.5296 | -123.1018 | -123.0331
2954.9062 | 122.5662 | -61.5555 | 61.1206 | -0.19424 | 0.002162 | 0.0011044 | 0.0011237 | -0.0056118 | -7.9062e-05 | 0.0049069 | -61.6241 | 61.1435 | -62.0132 | 60.8459 | 59.2255 | 0.22888 | 60.5667 | 4.6051 | 60.8276 | -61.9492 | -0.45776 | 0.022889 | -0.068665 | 122.4014 | -1.8951 | -0.39368 | -0.29297 | 0.3891 | 122.1222 | 66.1606 | 120.7809 | 122.699 | -0.068665 | 122.3831 | 61.7844 | -0.39368 | 122.699 | -0.068665 | 61.7844 | 120.7809 | 122.3831 | -123.1338 | -123.0698
2955.9062 | 122.6074 | -61.7661 | 60.8185 | -0.18662 | 0.0023756 | 0.003668 | 0.0045417 | -0.0062528 | 0.00034814 | 0.0014889 | -61.9171 | 60.3699 | -62.5397 | 60.8917 | 58.9783 | 0.16479 | 60.5392 | 4.7104 | 60.759 | -62.0499 | -0.77362 | -0.44861 | -0.15106 | 122.6578 | -1.8402 | -0.28381 | -0.059509 | 0.62256 | 122.3053 | 66.4764 | 120.7443 | 122.1359 | -0.15106 | 122.525 | 61.9308 | -0.28381 | 122.1359 | -0.15106 | 61.9308 | 120.7443 | 122.525 | -123.3582 | -122.8683
2956.9062 | 122.8958 | -61.6013 | 60.9741 | -0.19424 | 0.00088016 | 3.6382e-05 | 0.0032599 | -0.0056118 | -0.0011471 | 0.0014889 | -59.9762 | 62.2559 | -60.6171 | 61.2122 | 59.4086 | 0.17853 | 60.8414 | 4.5776 | 61.0977 | -61.8118 | 0.98419 | 1.2817 | 1.6251 | 122.8134 | -1.5656 | -0.21057 | 0.1236 | 0.64087 | 122.4426 | 66.1789 | 121.0098 | 123.8571 | 1.6251 | 122.699 | 61.7798 | -0.21057 | 123.8571 | 1.6251 | 61.7798 | 121.0098 | 122.699 | -121.5912 | -122.7859
2957.9062 | 122.9416 | -61.0062 | 61.5829 | -0.31631 | -0.001256 | 0.0051632 | 0.0036871 | -0.0062528 | -0.0032835 | 0.0017027 | -60.9421 | 61.4502 | -61.4227 | 61.6653 | 59.8663 | 0.2243 | 61.2534 | 4.7653 | 61.4777 | -61.3632 | -0.41656 | -0.13275 | 0.064087 | 122.6715 | -1.7166 | -0.35705 | -0.10529 | 0.48065 | 122.2595 | 65.7715 | 120.8725 | 122.4564 | 0.064087 | 122.4838 | 61.2305 | -0.35705 | 122.4564 | 0.064087 | 61.2305 | 120.8725 | 122.4838 | -123.0057 | -122.9462
2958.9062 | 122.7859 | -62.3108 | 60.347 | 0.0041197 | 0.00323 | -0.00060462 | 0.0133 | -0.0051846 | 0.00056194 | 0.0038389 | -62.0224 | 60.3424 | -62.6221 | 60.6628 | 58.6166 | 0.073242 | 60.3241 | 4.0741 | 60.4065 | -62.5992 | -0.31128 | -0.004578 | 0.28839 | 122.9736 | -1.7303 | -0.28839 | 0.059509 | 0.59967 | 122.6349 | 66.3849 | 120.9274 | 122.6532 | 0.28839 | 122.7173 | 62.384 | -0.28839 | 122.6532 | 0.28839 | 62.384 | 120.9274 | 122.7173 | -122.9691 | -122.9462
2959.9062 | 122.8867 | -60.7178 | 61.9858 | -0.087433 | 0.00066656 | -0.0020998 | -0.0001581 | -0.004971 | -0.0011471 | 0.0027707 | -61.0062 | 61.322 | -61.5189 | 61.5372 | 59.7565 | 0.2243 | 61.4182 | 4.7928 | 61.5463 | -61.2717 | -0.80109 | -0.66376 | -0.28839 | 122.2549 | -2.2293 | -0.55389 | -0.43945 | 0.51269 | 122.1359 | 65.5106 | 120.4742 | 122.0398 | -0.28839 | 122.2641 | 60.9421 | -0.55389 | 122.0398 | -0.28839 | 60.9421 | 120.4742 | 122.2641 | -123.5046 | -123.2574
2960.9062 | 122.9095 | -60.1868 | 62.3154 | -0.2858 | -0.0010424 | -0.00017722 | 0.0058233 | -0.0068936 | -0.0024289 | 0.0031979 | -60.2463 | 62.027 | -60.8505 | 62.265 | 60.4385 | 0.24261 | 62.1552 | 5.4291 | 62.2925 | -60.466 | -0.66376 | -0.28839 | -0.059509 | 122.4518 | -1.8768 | -0.27923 | -0.022889 | 0.60425 | 122.3419 | 65.6158 | 120.6253 | 122.2137 | -0.059509 | 122.4792 | 60.4294 | -0.27923 | 122.2137 | -0.059509 | 60.4294 | 120.6253 | 122.4792 | -123.1659 | -122.7814
2961.9062 | 122.9324 | -59.5367 | 63.0844 | -0.10269 | -0.00040164 | 0.0032406 | 0.0028327 | -0.010312 | -0.0020017 | 0.0040525 | -58.287 | 63.9038 | -59.1751 | 62.4664 | 60.7086 | 0.14648 | 62.5397 | 5.3833 | 62.5946 | -60.1135 | 0.36163 | 0.8194 | 1.2497 | 122.0032 | -2.3758 | -0.57678 | -0.48981 | 0.88806 | 122.0764 | 64.92 | 120.2454 | 123.4406 | 1.2497 | 122.1313 | 59.6832 | -0.57678 | 123.4406 | 1.2497 | 59.6832 | 120.2454 | 122.1313 | -122.2595 | -123.1979
2962.9062 | 122.8775 | -60.26 | 62.384 | -0.14847 | -0.002965 | 0.0017454 | 0.0030463 | -0.0088162 | -7.9062e-05 | 0.0040525 | -59.5825 | 62.6862 | -60.1639 | 63.3911 | 61.7477 | 0.21057 | 62.0865 | 4.8889 | 62.5809 | -60.4568 | 0.096131 | 0.30212 | 0.67749 | 123.6511 | -0.63629 | -0.19684 | 0.19684 | 0.58136 | 122.3465 | 65.1489 | 122.0078 | 122.9462 | 0.67749 | 122.8409 | 60.4706 | -0.19684 | 122.9462 | 0.67749 | 60.4706 | 122.0078 | 122.8409 | -122.5479 | -122.8409
2963.9062 | 122.8088 | -66.4352 | 56.1676 | -0.24765 | 0.001521 | 0.0075132 | 0.0079595 | -0.0086026 | -0.0017881 | 0.0014889 | -66.7007 | 55.719 | -67.2363 | 56.1584 | 54.364 | 0.22888 | 55.8334 | 2.8198 | 55.9753 | -66.9434 | -0.80109 | -0.44861 | -0.2655 | 122.5937 | -1.8036 | -0.50812 | -0.19226 | 0.53558 | 122.2687 | 69.2551 | 120.7993 | 122.1542 | -0.2655 | 122.4106 | 66.6641 | -0.50812 | 122.1542 | -0.2655 | 66.6641 | 120.7993 | 122.4106 | -123.4039 | -123.111
2964.9062 | 122.9233 | -64.183 | 58.4564 | -0.10269 | -0.001897 | 0.0038816 | 0.0028327 | -0.0068936 | -0.00093346 | 0.0038389 | -64.27 | 57.9529 | -64.8514 | 58.2184 | 56.5247 | 0.34332 | 57.6874 | 3.6392 | 58.0902 | -64.6454 | -0.66833 | -0.50354 | -0.086976 | 122.4014 | -1.9318 | -0.46234 | -0.36621 | 0.58136 | 121.8704 | 67.8223 | 120.7077 | 122.1359 | -0.086976 | 122.2733 | 64.5264 | -0.46234 | 122.1359 | -0.086976 | 64.5264 | 120.7077 | 122.2733 | -123.3078 | -123.1018
2965.9062 | 93.782 | -112.2528 | 10.2951 | -0.026398 | 0.00045296 | 0.0060178 | 0.018213 | -0.0071072 | 0.00034814 | 0.0034115 | -111.7218 | 10.4141 | -112.532 | 10.405 | 9.8373 | 0.72784 | 10.0204 | -10.8902 | 10.405 | -112.6694 | -0.27923 | 0.11902 | 0.53101 | 122.6578 | -0.45776 | -0.41656 | 0.10986 | 0.81024 | 122.2733 | 101.3626 | 122.0901 | 122.6669 | 0.53101 | 122.6578 | 112.9807 | -0.41656 | 122.6669 | 0.53101 | 112.9807 | 122.0901 | 122.6578 | -122.8271 | -122.9645
2966.9062 | 122.8683 | -111.9781 | 10.6064 | -0.34683 | 0.0013074 | 0.0034544 | 0.015436 | -0.00668 | -0.0011471 | 0.0040525 | -111.5295 | 10.524 | -112.3947 | 10.5057 | 9.993 | 2.5314 | 10.025 | -10.6293 | 10.6339 | -112.3169 | -0.41656 | -0.082397 | 0.44861 | 122.4838 | -0.6134 | -0.33875 | 0.027466 | 0.86517 | 122.0032 | 101.3489 | 121.9711 | 122.5021 | 0.44861 | 122.612 | 114.5096 | -0.33875 | 122.5021 | 0.44861 | 114.5096 | 121.9711 | 122.612 | -123.0011 | -122.9233
2967.9062 | 122.6715 | -65.0391 | 57.1014 | 0.034637 | 0.00045296 | 0.0034544 | 0.0017645 | -0.0062528 | 0.00098914 | 0.0021299 | -64.3341 | 57.9483 | -64.8102 | 58.5251 | 56.3644 | -0.022888 | 56.4011 | 2.7466 | 57.4356 | -65.4602 | 0.22888 | 0.84686 | 0.70496 | 123.5641 | -0.737 | -0.42114 | 0.33417 | 0.47607 | 121.4401 | 67.7856 | 121.4035 | 122.9874 | 0.70496 | 122.4747 | 65.0162 | -0.42114 | 122.9874 | 0.70496 | 65.0162 | 121.4035 | 122.4747 | -121.9116 | -122.5616
2968.9062 | 122.493 | -63.707 | 57.93 | -0.2858 | 2.5564e-05 | 0.0021726 | 0.0043281 | -0.0068936 | 0.00077554 | 0.00063446 | -63.1027 | 59.1934 | -63.6795 | 59.3628 | 57.4356 | 0.20599 | 59.0561 | 4.2435 | 59.1843 | -63.8626 | 0.027466 | 1.2634 | 0.60425 | 123.0698 | -0.49439 | -0.15564 | 1.2543 | 0.57678 | 122.7631 | 67.9504 | 121.1426 | 122.9004 | 0.60425 | 122.8912 | 63.913 | -0.15564 | 122.9004 | 0.60425 | 63.913 | 121.1426 | 122.8912 | -121.6095 | -121.7926
2969.9062 | 122.8821 | -97.9797 | 24.646 | -0.018768 | -0.00082884 | 0.0015316 | 0.012873 | -0.0062528 | -0.0011471 | 0.00084806 | -97.5677 | 24.4995 | -98.2819 | 23.9685 | 23.172 | 2.1103 | 24.0143 | -6.6147 | 24.1196 | -98.6343 | -0.30212 | -0.14648 | 0.41199 | 121.9482 | -1.474 | -0.6546 | -0.52643 | 0.71411 | 121.994 | 91.3651 | 121.1517 | 122.4792 | 0.41199 | 122.0993 | 100.09 | -0.6546 | 122.4792 | 0.41199 | 100.09 | 121.1517 | 122.0993 | -122.9279 | -123.2803
2970.9062 | 122.9187 | -113.53 | 9.0408 | -0.0035098 | -0.0010424 | 0.0051632 | 0.016291 | -0.0062528 | 0.00056194 | 0.0036253 | -113.1638 | 9.0042 | -113.8779 | 9.0179 | 8.4595 | 1.1627 | 8.7936 | -11.1465 | 9.0729 | -113.9282 | -0.3479 | -0.036622 | 0.36621 | 122.5479 | -0.58136 | -0.39826 | 0.032043 | 0.71411 | 122.3236 | 102.3834 | 121.9894 | 122.5342 | 0.36621 | 122.6028 | 114.6927 | -0.39826 | 122.5342 | 0.36621 | 114.6927 | 121.9894 | 122.6028 | -122.9187 | -122.9691
2971.9062 | 122.8683 | -113.15 | 9.4025 | 0.17197 | 0.00023916 | 0.00024998 | 0.015436 | -0.0088162 | -0.00071986 | 0.0027707 | -112.8159 | 9.343 | -113.5849 | 9.3384 | 8.7753 | 1.6937 | 9.1599 | -10.9314 | 9.4391 | -113.5849 | -0.43488 | -0.059509 | 0.33417 | 122.4884 | -0.62714 | -0.43488 | 0.036621 | 0.76904 | 122.3099 | 102.2186 | 121.9254 | 122.493 | 0.33417 | 122.5891 | 114.8438 | -0.43488 | 122.493 | 0.33417 | 114.8438 | 121.9254 | 122.5891 | -122.9874 | -122.9874
2972.9062 | 122.8592 | -114.5737 | 8.0429 | 0.095673 | -0.00040164 | 0.001959 | 0.018427 | -0.00668 | -0.0017881 | 0.0010617 | -114.093 | 8.0429 | -114.9445 | 7.8735 | 7.4615 | 2.0096 | 7.7637 | -11.4075 | 8.0109 | -114.9353 | -0.37079 | 0 | 0.48065 | 122.4472 | -0.58136 | -0.36163 | -0.032044 | 0.85144 | 122.3373 | 103.1662 | 122.0352 | 122.6166 | 0.48065 | 122.5845 | 116.5833 | -0.36163 | 122.6166 | 0.48065 | 116.5833 | 122.0352 | 122.5845 | -122.9874 | -122.9782
2973.9062 | 122.9141 | -113.6948 | 8.9172 | -0.0035098 | 0.00088016 | 0.0011044 | 0.017573 | -0.0056118 | -0.00093346 | 0.0036253 | -113.7314 | 8.3908 | -114.1113 | 8.8577 | 8.3176 | 2.1194 | 8.4503 | -11.2335 | 9.0454 | -113.9786 | -0.41657 | -0.52643 | -0.036621 | 122.5525 | -0.59967 | -0.28381 | 0.12817 | 0.37994 | 122.1451 | 102.4612 | 122.0123 | 122.0856 | -0.036621 | 122.7402 | 115.8142 | -0.28381 | 122.0856 | -0.036621 | 115.8142 | 122.0123 | 122.7402 | -123.0286 | -122.8958
2974.9062 | 122.9233 | -112.9166 | 9.7092 | 0.16434 | 0.00066656 | 0.005377 | 0.016932 | -0.0092434 | 0.00077554 | 0.0019163 | -112.5137 | 9.5169 | -113.3331 | 9.6222 | 9.0683 | 2.6642 | 9.3842 | -10.6155 | 9.7183 | -113.1683 | -0.41656 | -0.19226 | 0.40283 | 122.5388 | -0.64087 | -0.25177 | 0.009156 | 0.8194 | 122.3007 | 102.301 | 121.9849 | 122.4335 | 0.40283 | 122.6349 | 115.5808 | -0.25177 | 122.4335 | 0.40283 | 115.5808 | 121.9849 | 122.6349 | -123.0423 | -122.8775
2975.9062 | 122.8912 | -113.2919 | 9.3933 | 0.12619 | 0.00066656 | 0.0045224 | 0.016077 | -0.0073208 | -0.0013609 | 0.0046933 | -112.944 | 9.2148 | -113.6948 | 9.3338 | 8.7158 | 2.774 | 8.7112 | -10.6293 | 9.3842 | -113.5666 | -0.40283 | -0.17853 | 0.3479 | 122.6257 | -0.67749 | -0.27466 | -0.009156 | 0.75073 | 122.0032 | 102.6627 | 122.0078 | 122.5067 | 0.3479 | 122.6761 | 116.066 | -0.27466 | 122.5067 | 0.3479 | 116.066 | 122.0078 | 122.6761 | -123.0881 | -122.9599
2976.9688 | 122.9004 | -113.4705 | 9.1232 | 0.21011 | 0.00023916 | 0.003668 | 0.018854 | -0.0053982 | -0.0015745 | 0.0021299 | -112.8983 | 9.1827 | -113.7543 | 9.1141 | 8.5693 | 2.2614 | 8.7753 | -10.4736 | 9.1049 | -113.8687 | -0.28381 | 0.059509 | 0.57221 | 122.5845 | -0.55389 | -0.39825 | -0.018311 | 0.85602 | 122.2458 | 102.9968 | 122.0398 | 122.6532 | 0.57221 | 122.5754 | 115.7318 | -0.39825 | 122.6532 | 0.57221 | 115.7318 | 122.0398 | 122.5754 | -122.8775 | -122.9919
2977.9062 | 122.8821 | -112.7563 | 9.874 | 0.12619 | -0.0016834 | 0.001318 | 0.016291 | -0.0060392 | -0.0013609 | 0.0025571 | -111.9827 | 10.1578 | -112.8204 | 9.8831 | 9.2285 | 1.799 | 9.7 | -10.199 | 9.993 | -113.0356 | -0.064087 | 0.28381 | 0.77362 | 122.6395 | -0.64545 | -0.27923 | 0.11902 | 0.83771 | 122.4564 | 102.5574 | 121.9849 | 122.9141 | 0.77362 | 122.7493 | 114.5554 | -0.27923 | 122.9141 | 0.77362 | 114.5554 | 121.9849 | 122.7493 | -122.6944 | -122.9095
2978.9062 | 122.8867 | -114.5279 | 8.0338 | 0.18723 | 0.002162 | 3.6382e-05 | 0.01565 | -0.0060392 | 0.0012027 | 0.0040525 | -113.7268 | 8.3862 | -114.5004 | 8.0475 | 7.4387 | 2.1561 | 7.814 | -9.0637 | 8.0658 | -114.8987 | 0.027466 | 0.35248 | 0.80109 | 122.5754 | -0.59509 | -0.37079 | 0.032044 | 0.77362 | 122.3419 | 105.4642 | 121.9666 | 122.9141 | 0.80109 | 122.5937 | 116.684 | -0.37079 | 122.9141 | 0.80109 | 116.684 | 121.9666 | 122.5937 | -122.5342 | -122.9324
2979.9062 | 122.8683 | -114.2487 | 8.3633 | 0.1796 | -0.0010424 | 0.0011044 | 0.018641 | -0.0077482 | -0.0015745 | 0.0029843 | -113.8412 | 8.3038 | -114.6194 | 8.5281 | 7.9971 | 1.8494 | 8.0566 | -9.1187 | 8.4457 | -114.6194 | -0.37079 | -0.059509 | 0.40741 | 122.7768 | -0.36621 | -0.37079 | 0.082398 | 0.7782 | 122.3053 | 105.13 | 122.2458 | 122.5525 | 0.40741 | 122.6944 | 116.098 | -0.37079 | 122.5525 | 0.40741 | 116.098 | 122.2458 | 122.6944 | -122.9828 | -122.9828
2980.9062 | 122.937 | -114.9902 | 7.5623 | 1.5605 | 0.0028028 | 0.0011044 | 0.019709 | -0.0068936 | 0.00098914 | 0.0049069 | -114.4226 | 7.5577 | -115.3656 | 7.7042 | 7.1182 | 1.5244 | 7.1777 | -9.0591 | 7.6126 | -115.4068 | -0.37537 | -0.004578 | 0.56763 | 122.6944 | -0.44403 | -0.41657 | 0.050354 | 0.94299 | 122.168 | 105.9311 | 122.1085 | 122.5479 | 0.56763 | 122.6028 | 116.5146 | -0.41657 | 122.5479 | 0.56763 | 116.5146 | 122.1085 | 122.6028 | -122.9279 | -122.9691
2981.9062 | 119.5862 | -105.6839 | 15.8066 | 0.19485 | 0.0025892 | 0.0092222 | 0.017145 | -0.0051846 | -0.00071986 | 0.0027707 | -91.0492 | 31.0089 | -91.7999 | 19.8441 | 18.2556 | 2.3849 | 16.3284 | -8.5098 | 18.4341 | -105.4321 | 13.884 | 15.2023 | 14.6347 | 125.528 | 2.449 | 0.25177 | 2.6276 | 0.75073 | 122.0123 | 97.1741 | 123.9395 | 136.6928 | 14.6347 | 124.118 | 108.0688 | 0.25177 | 136.6928 | 14.6347 | 108.0688 | 123.9395 | 124.118 | -107.6065 | -121.2387
2982.9062 | 122.9462 | -113.1134 | 9.4711 | 0.26352 | 0.0019482 | 0.0032406 | 0.019068 | -0.0043302 | -0.0013609 | 0.0036253 | -112.3947 | 9.6817 | -113.2187 | 9.7229 | 9.1736 | 2.9572 | 8.8577 | -8.9584 | 9.581 | -113.4796 | -0.10529 | 0.21057 | 0.71869 | 122.8363 | -0.29755 | -0.36621 | 0.10986 | 0.82398 | 121.9711 | 104.155 | 122.287 | 122.7951 | 0.71869 | 122.6944 | 116.0706 | -0.36621 | 122.7951 | 0.71869 | 116.0706 | 122.287 | 122.6944 | -122.6898 | -122.9507
2983.9062 | 122.9141 | -106.8878 | 15.6692 | -0.056915 | -0.00061524 | 0.00089078 | 0.013514 | -0.0068936 | -0.00093346 | 0.0023435 | -105.9082 | 16.0538 | -106.7551 | 15.7059 | 15.0742 | 2.5909 | 15.4175 | -7.1503 | 15.6372 | -107.2311 | 0.13275 | 0.38452 | 0.97961 | 122.5937 | -0.59509 | -0.34332 | -0.032043 | 0.84686 | 122.3053 | 99.7375 | 121.962 | 122.9416 | 0.97961 | 122.525 | 109.4788 | -0.34332 | 122.9416 | 0.97961 | 109.4788 | 121.962 | 122.525 | -122.4243 | -122.9004
2984.9062 | 122.8867 | -58.8318 | 63.1805 | 0.1033 | 0.00066656 | 0.00024998 | 0.0015509 | -0.0058256 | -0.0013609 | 0.0061887 | -58.493 | 63.707 | -59.0195 | 63.7894 | 62.0087 | 0.28381 | 63.4277 | 4.6326 | 63.6749 | -59.1843 | -0.18768 | 0.52643 | 0.33874 | 122.6212 | -1.1719 | -0.35248 | 0.49438 | 0.52643 | 122.2595 | 63.4644 | 120.8405 | 122.5388 | 0.33874 | 122.5067 | 59.1156 | -0.35248 | 122.5388 | 0.33874 | 59.1156 | 120.8405 | 122.5067 | -122.2 | -122.3648
2985.9062 | 122.9507 | -60.141 | 62.3383 | 0.21011 | 0.00088016 | 0.0062314 | 0.0039007 | -0.0058256 | -0.00050626 | 0.0014889 | -60.2646 | 62.1506 | -60.8139 | 62.2787 | 59.8572 | 0.21057 | 62.1094 | 4.9072 | 62.1323 | -60.5347 | -0.67291 | -0.18768 | -0.1236 | 122.4197 | -2.4811 | -0.39368 | -0.20599 | 0.54932 | 122.2504 | 65.0482 | 119.9982 | 122.2916 | -0.1236 | 122.2733 | 60.3516 | -0.39368 | 122.2916 | -0.1236 | 60.3516 | 119.9982 | 122.2733 | -123.1522 | -122.8729
2986.9062 | 122.9233 | -60.2829 | 62.2696 | 0.088043 | 0.00323 | 0.0034544 | 0.0051825 | -0.0053982 | -0.0011471 | 0.0023435 | -60.5026 | 61.8576 | -61.0245 | 62.5946 | 60.6812 | 0.27924 | 61.8073 | 4.5685 | 62.1277 | -60.7178 | -0.74158 | -0.41199 | -0.21973 | 122.8775 | -1.5884 | -0.43487 | -0.14191 | 0.52185 | 122.0901 | 64.8514 | 120.9641 | 122.1405 | -0.21973 | 122.4106 | 60.5621 | -0.43487 | 122.1405 | -0.21973 | 60.5621 | 120.9641 | 122.4106 | -123.2941 | -122.9874
2987.9219 | 122.8546 | -62.233 | 60.2875 | -0.27817 | 0.0030164 | 0.0049496 | 0.0045417 | -0.0068936 | -0.0020017 | 0.0025571 | -62.2833 | 60.2463 | -62.7274 | 60.3653 | 58.6716 | 0.19226 | 60.1868 | 4.2664 | 60.3104 | -62.5351 | -0.49439 | -0.041199 | -0.050354 | 122.5983 | -1.6159 | -0.30212 | 0.022888 | 0.44403 | 122.4197 | 66.4993 | 120.9045 | 122.4792 | -0.050354 | 122.5433 | 62.4252 | -0.30212 | 122.4792 | -0.050354 | 62.4252 | 120.9045 | 122.5433 | -123.0148 | -122.8226
2988.9062 | 122.9141 | -60.3699 | 62.0911 | -0.011139 | -0.00061524 | -0.0010318 | 5.5496e-05 | -0.0075344 | -0.0017881 | 0.0034115 | -59.9579 | 62.352 | -60.5209 | 64.1052 | 60.8047 | 0.28839 | 61.9125 | 4.216 | 62.5259 | -60.4752 | -0.15106 | 0.26093 | 0.41199 | 124.4751 | -1.2863 | -0.10529 | 0.43488 | 0.56305 | 122.2824 | 64.5859 | 121.1746 | 122.7219 | 0.41199 | 122.8958 | 60.6583 | -0.10529 | 122.7219 | 0.41199 | 60.6583 | 121.1746 | 122.8958 | -122.612 | -122.5662
2989.9062 | 122.9279 | -60.3241 | 62.3474 | 0.25589 | 0.0017346 | 0.010077 | 0.0064643 | -0.0053982 | 0.00098914 | 0.0036253 | -60.5942 | 61.6974 | -61.1618 | 62.439 | 60.2783 | 0.3479 | 61.6882 | 4.4815 | 61.9171 | -60.8002 | -0.83771 | -0.65002 | -0.27008 | 122.7631 | -2.0691 | -0.47607 | -0.4303 | 0.56763 | 122.0123 | 64.8056 | 120.6024 | 122.0215 | -0.27008 | 122.2412 | 60.672 | -0.47607 | 122.0215 | -0.27008 | 60.672 | 120.6024 | 122.2412 | -123.5092 | -123.1476
2990.9062 | 122.9187 | -63.1119 | 59.3948 | -1.1327 | 0.0025892 | 0.0021726 | 0.0039007 | -0.0056118 | -0.0011471 | 0.0027707 | -62.7594 | 59.5688 | -63.1805 | 59.7427 | 57.962 | 0.26093 | 59.8068 | 3.9368 | 59.7382 | -63.1805 | -0.068665 | 0.17395 | 0.35248 | 122.8546 | -1.4328 | -0.068665 | 0.34332 | 0.42114 | 122.9187 | 67.0486 | 121.0739 | 122.6807 | 0.35248 | 122.85 | 63.3728 | -0.068665 | 122.6807 | 0.35248 | 63.3728 | 121.0739 | 122.85 | -122.5754 | -122.5754
2991.9219 | 122.9095 | -60.9924 | 61.7569 | -1.1784 | -0.00018804 | 0.0049496 | 0.0071051 | -0.0036892 | -0.0017881 | 0.0021299 | -60.8917 | 61.3129 | -61.5234 | 61.3449 | 59.6329 | 0.31586 | 60.9924 | 4.4769 | 61.2396 | -61.5829 | -0.53101 | -0.44403 | 0.10071 | 122.3373 | -2.124 | -0.59051 | -0.51727 | 0.63171 | 121.9849 | 65.4694 | 120.6253 | 122.3053 | 0.10071 | 122.2321 | 61.3083 | -0.59051 | 122.3053 | 0.10071 | 61.3083 | 120.6253 | 122.2321 | -123.2803 | -123.3398
2992.9844 | 122.9279 | -60.379 | 62.1185 | -0.22476 | 0.001521 | 0.0015316 | 0.0039007 | -0.0051846 | -0.0020017 | 0.0017027 | -60.2417 | 62.059 | -60.7544 | 62.4847 | 60.8597 | 0.31586 | 62.2101 | 4.9118 | 62.4207 | -60.4797 | -0.37537 | -0.059509 | 0.13733 | 122.8638 | -1.2589 | -0.10071 | 0.30212 | 0.5127 | 122.5891 | 65.2908 | 121.2387 | 122.438 | 0.13733 | 122.7997 | 60.6949 | -0.10071 | 122.438 | 0.13733 | 60.6949 | 121.2387 | 122.7997 | -122.8729 | -122.5983
2993.9219 | 122.7768 | -60.6445 | 62.0407 | -0.20187 | 0.0028028 | 0.00024998 | 0.0073187 | -0.0075344 | -0.00071986 | 0.00084806 | -60.3882 | 62.0499 | -60.91 | 62.4069 | 60.0037 | 0.29755 | 61.702 | 4.6463 | 61.8576 | -61.0245 | -0.2655 | 0.009156 | 0.25635 | 123.0515 | -2.037 | -0.37994 | -0.1831 | 0.52185 | 122.3465 | 65.2908 | 120.6482 | 122.6944 | 0.25635 | 122.5021 | 60.9421 | -0.37994 | 122.6944 | 0.25635 | 60.9421 | 120.6482 | 122.5021 | -122.9507 | -123.0652
2994.9844 | 122.8546 | -60.4385 | 61.8301 | -0.2095 | 0.0034436 | 0.005377 | 0.011164 | -0.0024076 | -0.00050626 | 0.0034115 | -60.5942 | 61.8301 | -61.1664 | 61.9766 | 60.0769 | 0.2655 | 61.6196 | 4.4998 | 61.8027 | -61.116 | -0.72784 | 0 | -0.15564 | 122.4152 | -1.7532 | -0.67749 | -0.027466 | 0.5722 | 122.0581 | 64.9384 | 120.5154 | 122.2687 | -0.15564 | 122.2412 | 60.704 | -0.67749 | 122.2687 | -0.15564 | 60.704 | 120.5154 | 122.2412 | -122.9965 | -122.9462
2995.9844 | 122.8729 | -64.1327 | 58.1268 | 0.15671 | 0.0062208 | 0.0068722 | 0.0075323 | -0.0034756 | -0.00050626 | 0.00084806 | -65.9317 | 56.4056 | -66.1926 | 59.2529 | 57.5638 | 0.26093 | 60.0128 | 3.9597 | 59.4818 | -63.7573 | -2.0599 | -1.7212 | -1.799 | 123.3856 | -0.56305 | 0.37537 | 1.355 | 0.26093 | 124.1455 | 68.0923 | 121.6965 | 120.5383 | -1.799 | 123.6145 | 64.3936 | 0.37537 | 120.5383 | -1.799 | 64.3936 | 121.6965 | 123.6145 | -124.3195 | -121.8842
2996.9531 | 122.8226 | -65.3961 | 57.3029 | -0.12558 | 0.00323 | 0.0017454 | 0.0071051 | -0.0053982 | -0.0011471 | 0.0021299 | -65.0986 | 57.3349 | -65.7486 | 57.3715 | 55.7465 | 0.23804 | 57.1198 | 3.1036 | 57.2159 | -65.7715 | -0.35248 | 0.032044 | 0.29755 | 122.7676 | -1.5564 | -0.37537 | -0.086975 | 0.65002 | 122.5159 | 68.4998 | 121.1426 | 122.731 | 0.29755 | 122.612 | 65.6342 | -0.37537 | 122.731 | 0.29755 | 65.6342 | 121.1426 | 122.612 | -123.0515 | -123.0743
2997.9062 | 122.8775 | -66.6641 | 56.1722 | 0.18723 | 0.0025892 | 0.0049496 | 0.0075323 | -0.0019802 | -7.9062e-05 | 0.0029843 | -66.7328 | 55.8289 | -67.2409 | 56.3141 | 54.4327 | 0.3891 | 55.5954 | 2.6184 | 55.6824 | -67.2455 | -0.57678 | -0.34332 | -0.068664 | 122.9782 | -1.7395 | -0.58136 | -0.48981 | 0.50812 | 122.2595 | 69.2825 | 121.0968 | 122.493 | -0.068664 | 122.3465 | 67.0532 | -0.58136 | 122.493 | -0.068664 | 67.0532 | 121.0968 | 122.3465 | -123.4131 | -123.4177
2998.9219 | 122.9004 | -65.9958 | 56.4743 | 0.11093 | -0.00040164 | 0.0028134 | 0.0028327 | -0.0036892 | -0.0011471 | 0.0040525 | -65.3961 | 56.7169 | -66.124 | 57.8567 | 55.6503 | 0.40741 | 57.6553 | 3.2776 | 57.3715 | -65.7852 | -0.12817 | 0.24262 | 0.59967 | 123.8525 | -0.82397 | 0.21057 | 0.89722 | 0.72784 | 123.6511 | 69.2734 | 121.6461 | 122.7127 | 0.59967 | 123.3673 | 66.4032 | 0.21057 | 122.7127 | 0.59967 | 66.4032 | 121.6461 | 123.3673 | -122.5983 | -122.2595
2999.9688 | 122.2549 | -63.3041 | 59.4086 | 0.042267 | 0.006648 | 0.004736 | 0.0081733 | -0.0026212 | -0.0013609 | 0.0023435 | -63.3911 | 58.6304 | -64.1373 | 59.2896 | 57.5226 | 0.2655 | 59.1522 | 3.9185 | 59.2667 | -63.7024 | -0.83313 | -0.7782 | -0.086975 | 122.5937 | -1.886 | -0.39825 | -0.14191 | 0.74616 | 122.4564 | 67.2226 | 120.8267 | 121.9345 | -0.086975 | 122.5708 | 63.5696 | -0.39825 | 121.9345 | -0.086975 | 63.5696 | 120.8267 | 122.5708 | -123.5458 | -123.111
3000.9062 | 122.2641 | -62.9288 | 60.0266 | 0.019379 | 0.0053662 | 0.0045224 | 0.0071051 | -0.0024076 | -0.0011471 | 0.0023435 | -62.2192 | 60.0723 | -62.9059 | 59.9396 | 58.2596 | 0.24719 | 59.0973 | 3.6713 | 59.5596 | -63.5513 | 0.022888 | 0.045777 | 0.70953 | 122.8683 | -1.767 | -0.62256 | -0.46692 | 0.68665 | 122.0261 | 66.6 | 121.1884 | 123.0011 | 0.70953 | 122.4884 | 63.176 | -0.62256 | 123.0011 | 0.70953 | 63.176 | 121.1884 | 122.4884 | -122.9324 | -123.5779
3001.9062 | 122.7768 | -66.3712 | 56.4835 | 0.072784 | 0.006648 | 0.0075132 | 0.0090277 | -0.0013394 | -0.0011471 | 0.0017027 | -66.4169 | 57.2708 | -66.5039 | 57.0969 | 54.9957 | 0.23346 | 55.2841 | 1.8127 | 55.9845 | -67.2089 | -0.13275 | 0.78735 | -0.045776 | 123.468 | -1.4877 | -0.83771 | -0.49896 | 0.086975 | 121.6553 | 68.1839 | 121.3669 | 123.642 | -0.045776 | 122.3557 | 66.6046 | -0.83771 | 123.642 | -0.045776 | 66.6046 | 121.3669 | 122.3557 | -122.9874 | -123.6923
3002.9062 | 122.8226 | -64.5401 | 58.1451 | 0.027008 | 0.004939 | 0.0058042 | 0.0094549 | -5.7592e-05 | -0.0026425 | 0.00063446 | -64.2059 | 58.1589 | -64.9521 | 58.3923 | 56.5659 | 0.3479 | 58.0673 | 3.4653 | 58.1451 | -64.888 | -0.41199 | 0.013733 | 0.33417 | 122.9324 | -1.5793 | -0.3479 | 0 | 0.74615 | 122.6074 | 68.0054 | 121.106 | 122.699 | 0.33417 | 122.6852 | 64.888 | -0.3479 | 122.699 | 0.33417 | 64.888 | 121.106 | 122.6852 | -123.0972 | -123.0331
3003.9219 | 122.85 | -66.5451 | 56.1996 | 0.034637 | 0.0010938 | 0.0060178 | -0.0016535 | -0.0045438 | 0.00098914 | 0.0025571 | -65.9958 | 56.2225 | -66.6733 | 56.3049 | 54.6616 | 0.38452 | 55.6274 | 2.9434 | 56.0165 | -66.9159 | -0.12817 | 0.022888 | 0.54932 | 122.85 | -1.5381 | -0.37079 | -0.18311 | 0.67749 | 122.1725 | 69.4885 | 121.2067 | 122.7676 | 0.54932 | 122.5616 | 66.9296 | -0.37079 | 122.7676 | 0.54932 | 66.9296 | 121.2067 | 122.5616 | -122.8729 | -123.1155
3004.9062 | 110.3348 | -5.8777 | 99.4308 | 0.14908 | 0.0070752 | 0.0015316 | 0.0053961 | -0.0056118 | 0.00098914 | 0.017297 | -5.4108 | 117.1783 | -6.015 | 117.1738 | 113.887 | -0.83313 | 116.7114 | 18.544 | 117.041 | -6.0196 | -0.13733 | 17.7475 | 0.46692 | 123.0515 | 14.4562 | -0.14191 | 17.6102 | 0.60425 | 122.5891 | 24.4217 | 119.7647 | 123.056 | 0.46692 | 122.9187 | 5.0446 | -0.14191 | 123.056 | 0.46692 | 5.0446 | 119.7647 | 122.9187 | -105.4459 | -105.4504
3005.9688 | 94.9997 | 0.17853 | 85.8536 | -0.034027 | 0.0060072 | 0.0045224 | 0.010523 | -0.0041166 | -0.00071986 | 0.018792 | -7.5531 | 115.0726 | -8.1116 | 115.1642 | 111.8774 | -2.8473 | 114.7568 | 17.6971 | 115.0131 | -8.075 | -8.2901 | 29.2191 | -7.7316 | 114.9857 | 26.0239 | -8.2535 | 29.1595 | 0.55847 | 114.5782 | 17.5186 | 111.6989 | 114.8941 | -7.7316 | 114.8346 | -3.0258 | -8.2535 | 114.8941 | -7.7316 | -3.0258 | 111.6989 | 114.8346 | -93.9651 | -93.9285
3006.9062 | 122.6166 | -81.9992 | 40.8966 | 0.13382 | 0.0057934 | 0.0058042 | 0.020136 | -0.0026212 | -0.00050626 | 0.0049069 | -79.4724 | 41.7297 | -81.2073 | 40.6906 | 38.356 | 1.4969 | 38.7497 | 0.1236 | 40.0497 | -82.4387 | 0.79193 | 0.83313 | 2.5269 | 122.6898 | -2.5406 | -0.43945 | -0.84686 | 1.7349 | 120.7489 | 82.1228 | 120.3552 | 123.7289 | 2.5269 | 122.049 | 83.4961 | -0.43945 | 123.7289 | 2.5269 | 83.4961 | 120.3552 | 122.049 | -122.1039 | -123.3353
3007.9062 | 122.3328 | -65.0848 | 50.1343 | 0.027008 | 0.0060072 | 0.0055906 | 0.0083869 | -0.0026212 | -0.0037107 | 0.0014889 | -64.3295 | 58.0124 | -65.0116 | 57.8293 | 56.0165 | 0.09613 | 57.5638 | 3.1723 | 57.756 | -65.419 | 0.073242 | 7.8781 | 0.75531 | 122.9141 | 5.8823 | -0.33417 | 7.6218 | 0.68207 | 122.6486 | 68.2571 | 121.1014 | 123.0972 | 0.75531 | 122.8409 | 65.181 | -0.33417 | 123.0972 | 0.75531 | 65.181 | 121.1014 | 122.8409 | -115.1459 | -115.5533
3008.9062 | 122.818 | -114.4272 | 8.2306 | -0.034027 | 0.004939 | 0.0087948 | 0.024408 | 0.0010104 | -0.0022153 | 0.0040525 | -113.9053 | 8.2031 | -114.8071 | 8.1436 | 7.6355 | 1.6708 | 8.0658 | -9.4162 | 8.2947 | -114.8163 | -0.37994 | -0.027466 | 0.52185 | 122.5708 | -0.59509 | -0.3891 | 0.064087 | 0.9018 | 122.493 | 105.011 | 122.0627 | 122.6303 | 0.52185 | 122.7219 | 116.098 | -0.3891 | 122.6303 | 0.52185 | 116.098 | 122.0627 | 122.7219 | -123.0377 | -123.0469
3009.9062 | 122.8134 | -110.9436 | 11.4395 | 0.019379 | 0.0038708 | 0.0077268 | 0.020136 | -0.00048499 | -0.00093346 | 0.0053343 | -110.4813 | 11.7142 | -111.3602 | 11.7188 | 11.1465 | 2.8244 | 11.7966 | -8.4091 | 11.8744 | -111.2823 | -0.41656 | 0.27466 | 0.46234 | 122.6624 | -0.29297 | -0.33875 | 0.43488 | 0.87891 | 122.7402 | 102.5345 | 122.0901 | 122.6578 | 0.46234 | 122.818 | 113.768 | -0.33875 | 122.6578 | 0.46234 | 113.768 | 122.0901 | 122.818 | -122.7997 | -122.7219
3010.9062 | 122.7859 | -113.3881 | 9.1965 | 0.1033 | 0.00323 | 0.0040952 | 0.021418 | 0.0014376 | -0.0017881 | 0.0021299 | -113.0493 | 9.169 | -113.855 | 9.1187 | 8.5602 | 2.2888 | 9.0866 | -8.7936 | 9.3063 | -113.7955 | -0.46692 | -0.027466 | 0.33875 | 122.5067 | -0.63629 | -0.40741 | 0.10986 | 0.80566 | 122.4747 | 104.5944 | 121.9482 | 122.5571 | 0.33875 | 122.6944 | 115.6769 | -0.40741 | 122.5571 | 0.33875 | 115.6769 | 121.9482 | 122.6944 | -123.0515 | -122.9919
3011.9062 | 122.8043 | -110.3714 | 12.236 | 0.065155 | 0.0038708 | 0.0034544 | 0.019709 | -0.00091219 | -0.00071986 | 0.0025571 | -110.0006 | 12.2772 | -110.8017 | 12.1399 | 11.5768 | 2.6825 | 12.2498 | -7.933 | 12.3047 | -110.7834 | -0.4303 | 0.041199 | 0.37079 | 122.5113 | -0.65918 | -0.41199 | 0.068664 | 0.80109 | 122.6212 | 102.4384 | 121.9482 | 122.6486 | 0.37079 | 122.6761 | 113.0539 | -0.41199 | 122.6486 | 0.37079 | 113.0539 | 121.9482 | 122.6761 | -123.0377 | -123.0194
3012.9062 | 122.7859 | -114.0152 | 8.6517 | 0.1033 | 0.0040846 | 0.009863 | 0.018427 | -0.00048499 | -0.0030697 | 0.0023435 | -113.5666 | 8.5922 | -114.3906 | 8.4824 | 8.0612 | 2.8839 | 8.6151 | -8.5739 | 8.9401 | -114.3997 | -0.37537 | -0.059509 | 0.44861 | 122.4976 | -0.59051 | -0.38452 | 0.28839 | 0.82398 | 122.6303 | 105.4413 | 122.0764 | 122.6074 | 0.44861 | 122.9553 | 116.8991 | -0.38452 | 122.6074 | 0.44861 | 116.8991 | 122.0764 | 122.9553 | -123.0423 | -123.0515
3013.9062 | 122.7997 | -112.6373 | 9.993 | 0.26352 | 0.0025892 | 0.0062314 | 0.019709 | -0.0028348 | -0.0022153 | 0.0038389 | -112.3993 | 9.7504 | -113.1638 | 9.7733 | 8.6975 | 2.417 | 10.2905 | -7.8598 | 10.2127 | -113.0722 | -0.52643 | -0.24262 | 0.23804 | 122.4106 | -1.2955 | -0.43488 | 0.21973 | 0.76447 | 122.9279 | 104.7775 | 121.3348 | 122.3877 | 0.23804 | 122.85 | 115.0543 | -0.43488 | 122.3877 | 0.23804 | 115.0543 | 121.3348 | 122.85 | -123.1567 | -123.0652
3014.9062 | 122.8546 | -113.1454 | 9.4391 | 0.027008 | 0.0042982 | 0.0077268 | 0.020136 | 0.00058321 | -0.0020017 | 0.0044797 | -112.6602 | 9.5261 | -113.5254 | 9.1919 | 8.6243 | 2.0462 | 9.1873 | -8.3542 | 9.3887 | -113.6673 | -0.37994 | 0.086975 | 0.48523 | 122.3373 | -0.81482 | -0.52185 | -0.050354 | 0.86517 | 122.3328 | 104.7913 | 121.7697 | 122.6715 | 0.48523 | 122.5342 | 115.1917 | -0.52185 | 122.6715 | 0.48523 | 115.1917 | 121.7697 | 122.5342 | -122.9645 | -123.1064
3015.9062 | 122.8546 | -115.7455 | 6.9397 | -0.064545 | 0.0040846 | 0.0049496 | 0.020991 | -0.002194 | -0.0043515 | 0.0057615 | -115.274 | 6.8893 | -116.0934 | 6.7703 | 6.2942 | 1.593 | 6.7017 | -8.6609 | 6.9809 | -116.1484 | -0.3479 | -0.050354 | 0.4715 | 122.5159 | -0.64545 | -0.40283 | 0.041199 | 0.8194 | 122.4472 | 107.0847 | 122.0398 | 122.6349 | 0.4715 | 122.7264 | 117.3386 | -0.40283 | 122.6349 | 0.4715 | 117.3386 | 122.0398 | 122.7264 | -123.0331 | -123.0881
3016.9062 | 122.8317 | -114.6561 | 7.9697 | -0.14847 | 0.0034436 | 0.0062314 | 0.021631 | -0.00069859 | -0.00071986 | 0.0051205 | -114.2624 | 7.8232 | -115.1688 | 7.6859 | 7.2739 | 1.2405 | 7.7316 | -8.3176 | 7.901 | -115.1871 | -0.5127 | -0.14649 | 0.39368 | 122.3419 | -0.6958 | -0.53101 | -0.068665 | 0.90637 | 122.3877 | 106.3385 | 121.9299 | 122.4792 | 0.39368 | 122.5571 | 115.8966 | -0.53101 | 122.4792 | 0.39368 | 115.8966 | 121.9299 | 122.5571 | -123.1384 | -123.1567
3017.9062 | 122.8043 | -115.9012 | 6.7749 | 0.042267 | 0.002162 | 0.0058042 | 0.020563 | -0.0024076 | -0.0022153 | 0.0051205 | -115.4114 | 6.7291 | -116.2445 | 6.6376 | 6.189 | 0.91095 | 6.6055 | -8.7158 | 6.8298 | -116.3086 | -0.34332 | -0.045776 | 0.48981 | 122.5388 | -0.58594 | -0.40741 | 0.054932 | 0.83313 | 122.5067 | 107.1854 | 122.0901 | 122.6303 | 0.48981 | 122.731 | 116.8121 | -0.40741 | 122.6303 | 0.48981 | 116.8121 | 122.0901 | 122.731 | -123.0194 | -123.0835
3018.9219 | 122.8958 | -113.4659 | 9.1644 | 0.14145 | -0.001256 | 0.0083676 | 0.01095 | -0.0024076 | -0.0030697 | 0.0027707 | -112.9944 | 9.0637 | -113.8596 | 9.0088 | 8.5281 | 1.7899 | 8.9218 | -8.1665 | 9.2102 | -113.8184 | -0.39368 | -0.10071 | 0.4715 | 122.4747 | -0.63629 | -0.35248 | 0.045776 | 0.86517 | 122.3877 | 105.2994 | 121.994 | 122.5296 | 0.4715 | 122.6761 | 115.2557 | -0.35248 | 122.5296 | 0.4715 | 115.2557 | 121.994 | 122.6761 | -123.024 | -122.9828
3019.9062 | 122.8226 | -113.4705 | 9.2331 | 0.011749 | 0.0028028 | 0.0043088 | 0.022059 | -0.0034756 | -0.0026425 | 0.0021299 | -112.9852 | 9.1278 | -113.8687 | 9.05 | 8.5098 | 1.68 | 9.0179 | -8.0246 | 9.2377 | -113.9099 | -0.39825 | -0.10529 | 0.48523 | 122.5204 | -0.72327 | -0.43945 | 0.004578 | 0.88348 | 122.4884 | 105.4459 | 121.9803 | 122.5983 | 0.48523 | 122.7081 | 115.1505 | -0.43945 | 122.5983 | 0.48523 | 115.1505 | 121.9803 | 122.7081 | -123.1018 | -123.143
3020.9062 | 122.818 | -112.5412 | 10.1486 | -0.026398 | 0.0057934 | 0.0068722 | 0.019709 | -0.00027139 | -7.9062e-05 | 0.0051205 | -112.0102 | 9.8969 | -113.0127 | 10.1532 | 9.6771 | 1.4694 | 10.0067 | -8.345 | 10.1898 | -112.9715 | -0.4715 | -0.25177 | 0.53101 | 122.6944 | -0.4715 | -0.4303 | 0.041198 | 1.0025 | 122.5479 | 104.1962 | 122.2183 | 122.4381 | 0.53101 | 122.731 | 114.0106 | -0.4303 | 122.4381 | 0.53101 | 114.0106 | 122.2183 | 122.731 | -123.1613 | -123.1201
3021.9062 | 122.8683 | -114.8209 | 7.8232 | -0.026398 | 0.0036572 | 0.0040952 | 0.021631 | 0.00036961 | -0.0030697 | 0.0038389 | -114.0381 | 8.3542 | -114.8758 | 7.5668 | 7.1686 | 2.1652 | 7.5668 | -8.8989 | 7.8186 | -115.2924 | -0.054931 | 0.53101 | 0.78278 | 122.3877 | -0.6546 | -0.4715 | -0.004577 | 0.83771 | 122.3877 | 105.9219 | 121.9894 | 123.175 | 0.78278 | 122.6395 | 116.9861 | -0.4715 | 123.175 | 0.78278 | 116.9861 | 121.9894 | 122.6395 | -122.699 | -123.1155
3022.9062 | 122.8363 | -112.1658 | 10.4462 | -0.10269 | 0.0023756 | 0.0055906 | 0.020991 | -0.002194 | -0.00071986 | 0.0029843 | -111.5479 | 10.556 | -112.4817 | 10.4462 | 9.8373 | 2.4719 | 10.2997 | -8.3862 | 10.5469 | -112.6144 | -0.31586 | 0.10986 | 0.61798 | 122.612 | -0.60883 | -0.44861 | 0.10071 | 0.93384 | 122.4655 | 103.7796 | 122.0032 | 122.7219 | 0.61798 | 122.7127 | 114.6378 | -0.44861 | 122.7219 | 0.61798 | 114.6378 | 122.0032 | 122.7127 | -122.9279 | -123.0606
3023.9062 | 122.8226 | -114.0701 | 8.6014 | 0.17197 | 0.004939 | 0.0079404 | 0.018 | -0.002194 | 0.00098914 | 0.0074705 | -113.6673 | 8.5098 | -114.6286 | 8.2672 | 7.9056 | 1.8677 | 8.5922 | -8.8669 | 8.5648 | -114.4226 | -0.55847 | -0.091552 | 0.40283 | 122.3373 | -0.6958 | -0.35248 | -0.036621 | 0.9613 | 122.6624 | 105.2032 | 121.9757 | 122.58 | 0.40283 | 122.6349 | 115.9378 | -0.35248 | 122.58 | 0.40283 | 115.9378 | 121.9757 | 122.6349 | -123.23 | -123.024
3024.9062 | 122.85 | -115.0909 | 7.5531 | -0.0035098 | 0.0042982 | 0.0058042 | 0.025477 | -0.00048499 | -0.0022153 | 0.0066159 | -114.7842 | 7.2556 | -115.6769 | 7.4524 | 6.7886 | 2.2522 | 7.4295 | -9.1507 | 7.6035 | -115.5624 | -0.58594 | -0.29755 | 0.3067 | 122.5433 | -0.76447 | -0.4715 | 0.050354 | 0.89264 | 122.5204 | 105.9402 | 121.8796 | 122.3465 | 0.3067 | 122.6944 | 117.3431 | -0.4715 | 122.3465 | 0.3067 | 117.3431 | 121.8796 | 122.6944 | -123.23 | -123.1155
3025.9062 | 122.8546 | -114.5737 | 8.107 | -0.10269 | 0.0025892 | 0.004736 | 0.017573 | -0.00091219 | -0.0015745 | 0.0034115 | -113.9145 | 8.1802 | -114.7888 | 8.0978 | 7.6035 | 2.1652 | 7.9788 | -8.8715 | 8.1985 | -114.9582 | -0.21515 | 0.073242 | 0.65918 | 122.6715 | -0.50354 | -0.38452 | 0.091552 | 0.87433 | 122.5525 | 105.7022 | 122.1771 | 122.7539 | 0.65918 | 122.7722 | 116.7389 | -0.38452 | 122.7539 | 0.65918 | 116.7389 | 122.1771 | 122.7722 | -122.8958 | -123.0652
3026.9062 | 122.7676 | -114.1434 | 8.4366 | -0.034027 | 0.0034436 | 0.0060178 | 0.021631 | -0.0011258 | -0.0022153 | 0.0023435 | -113.9008 | 8.0383 | -114.8758 | 8.0704 | 7.608 | 1.9318 | 8.0154 | -8.9813 | 8.2626 | -114.8849 | -0.73242 | -0.39825 | 0.24262 | 122.2137 | -0.82855 | -0.74158 | -0.17395 | 0.97504 | 122.1588 | 105.162 | 121.7514 | 122.1817 | 0.24262 | 122.406 | 116.0751 | -0.74158 | 122.1817 | 0.24262 | 116.0751 | 121.7514 | 122.406 | -123.3124 | -123.3215
3027.9062 | 122.8683 | -114.3723 | 8.2993 | -0.11032 | 0.0034436 | 0.003027 | 0.022059 | -0.0028348 | -0.0024289 | 0.0046933 | -114.1525 | 7.7957 | -114.9536 | 8.2077 | 7.4799 | 2.1057 | 8.2214 | -8.9081 | 8.3679 | -114.7247 | -0.58136 | -0.50354 | 0.21973 | 122.58 | -0.8194 | -0.35248 | 0.068665 | 0.80109 | 122.5937 | 105.4642 | 121.8521 | 122.168 | 0.21973 | 122.7402 | 116.478 | -0.35248 | 122.168 | 0.21973 | 116.478 | 121.8521 | 122.7402 | -123.2529 | -123.024
3028.9062 | 122.8775 | -114.4409 | 8.2489 | -0.079803 | 0.0010938 | 0.008154 | 0.020136 | -0.0019802 | -0.0015745 | 0.0055479 | -114.1022 | 8.2855 | -114.8849 | 7.8781 | 7.402 | 1.7807 | 7.9834 | -8.7982 | 8.139 | -114.798 | -0.44403 | 0.036621 | 0.33875 | 122.319 | -0.84686 | -0.35706 | -0.10986 | 0.78278 | 122.4243 | 105.6427 | 121.843 | 122.7264 | 0.33875 | 122.58 | 116.2216 | -0.35706 | 122.7264 | 0.33875 | 116.2216 | 121.843 | 122.58 | -123.1339 | -123.0469
3029.9062 | 122.8271 | -113.9694 | 8.67 | -0.2095 | 0.00323 | 0.0043088 | 0.018854 | -0.00091219 | -0.0017881 | 0.0040525 | -113.6902 | 8.5052 | -114.4455 | 8.6655 | 8.107 | 1.9089 | 8.5831 | -9.0408 | 8.7936 | -114.418 | -0.47608 | -0.1648 | 0.27923 | 122.6349 | -0.56305 | -0.44861 | 0.1236 | 0.75531 | 122.5525 | 104.9286 | 122.0764 | 122.4747 | 0.27923 | 122.7631 | 115.8783 | -0.44861 | 122.4747 | 0.27923 | 115.8783 | 122.0764 | 122.7631 | -123.1155 | -123.0881
3030.9062 | 122.8271 | -113.5254 | 9.1507 | -0.27817 | 0.0034436 | 0.0011044 | 0.018854 | -0.0051846 | -0.00029266 | 0.0025571 | -113.0676 | 9.2651 | -113.8412 | 8.9539 | 8.4686 | 1.3046 | 9.0454 | -8.7524 | 9.1782 | -113.9282 | -0.31586 | 0.11444 | 0.45776 | 122.4792 | -0.68207 | -0.40283 | 0.027466 | 0.77362 | 122.5708 | 104.7729 | 121.994 | 122.7905 | 0.45776 | 122.7036 | 114.83 | -0.40283 | 122.7905 | 0.45776 | 114.83 | 121.994 | 122.7036 | -122.9919 | -123.0789
3031.9062 | 122.8592 | -114.1663 | 8.4686 | -0.18662 | 0.00323 | 0.00046358 | 0.016718 | -0.003262 | -0.0015745 | 0.0040525 | -113.7268 | 8.4778 | -114.5737 | 8.3496 | 7.8598 | 1.799 | 8.3221 | -8.8943 | 8.519 | -114.5874 | -0.40741 | 0.009155 | 0.43945 | 122.5159 | -0.60883 | -0.42114 | 0.050354 | 0.84686 | 122.4884 | 105.2719 | 122.0261 | 122.644 | 0.43945 | 122.6852 | 115.9653 | -0.42114 | 122.644 | 0.43945 | 115.9653 | 122.0261 | 122.6852 | -123.0423 | -123.056
3032.9062 | 122.8226 | -113.855 | 8.8028 | 0.072784 | 0.0030164 | 0.0051632 | 0.019068 | -0.0034756 | -0.00071986 | 0.0038389 | -113.443 | 8.7936 | -114.2807 | 8.6609 | 8.3633 | 1.8539 | 8.6975 | -9.0179 | 8.8486 | -114.3265 | -0.42572 | -0.009155 | 0.41199 | 122.5159 | -0.43945 | -0.4715 | 0.045777 | 0.83771 | 122.5525 | 104.837 | 122.2183 | 122.6486 | 0.41199 | 122.7036 | 115.7089 | -0.4715 | 122.6486 | 0.41199 | 115.7089 | 122.2183 | 122.7036 | -123.0835 | -123.1293
3033.9062 | 122.7631 | -115.0726 | 7.6538 | -0.18662 | 0.0025892 | -0.00017722 | 0.016932 | -0.0030484 | -0.0022153 | 0.0051205 | -114.6652 | 7.5485 | -115.4846 | 7.4295 | 6.8939 | 1.3733 | 7.6218 | -8.9447 | 7.6584 | -115.4526 | -0.41199 | -0.10529 | 0.40741 | 122.5021 | -0.75989 | -0.37994 | 0.004577 | 0.8194 | 122.6944 | 106.1279 | 121.9666 | 122.6212 | 0.40741 | 122.731 | 116.4459 | -0.37994 | 122.6212 | 0.40741 | 116.4459 | 121.9666 | 122.731 | -123.1384 | -123.1064
3034.9062 | 122.8317 | -114.4867 | 8.2581 | -0.25528 | 0.00045296 | 0.003027 | 0.016077 | -0.0034756 | -0.0011471 | 0.0019163 | -113.9603 | 8.1665 | -114.7888 | 8.0521 | 7.6035 | 0.87891 | 8.1299 | -9.3292 | 8.3038 | -114.8346 | -0.30212 | -0.091553 | 0.52643 | 122.5388 | -0.6546 | -0.3479 | 0.045776 | 0.82855 | 122.6166 | 105.1575 | 122.0901 | 122.6532 | 0.52643 | 122.7905 | 115.3656 | -0.3479 | 122.6532 | 0.52643 | 115.3656 | 122.0901 | 122.7905 | -123.0469 | -123.0927
3035.9062 | 122.9279 | -106.2881 | 16.2827 | -0.5986 | 0.0019482 | 0.0055906 | 0.010523 | -0.0041166 | -0.0017881 | 0.0042661 | -105.6244 | 16.2964 | -106.4621 | 16.0767 | 15.3488 | 2.6276 | 16.1636 | -7.3242 | 16.1865 | -106.7322 | -0.17395 | 0.013733 | 0.66376 | 122.3648 | -0.93384 | -0.44403 | -0.096131 | 0.83771 | 122.4518 | 98.9639 | 121.637 | 122.5845 | 0.66376 | 122.4747 | 108.9157 | -0.44403 | 122.5845 | 0.66376 | 108.9157 | 121.637 | 122.4747 | -122.7448 | -123.0148
3036.9062 | 123.0286 | -114.917 | 7.7911 | -0.14084 | 0.002162 | -0.001459 | 0.014795 | -0.0053982 | 0.00013454 | 0.0038389 | -114.537 | 7.5989 | -115.3381 | 7.7683 | 7.196 | 1.7532 | 7.5806 | -8.8348 | 7.8186 | -115.1413 | -0.42114 | -0.19226 | 0.37994 | 122.6852 | -0.59509 | -0.2243 | 0.027466 | 0.80109 | 122.4976 | 106.0822 | 122.113 | 122.5159 | 0.37994 | 122.7356 | 116.6702 | -0.2243 | 122.5159 | 0.37994 | 116.6702 | 122.113 | 122.7356 | -123.1293 | -122.9324
3037.9062 | 123.0011 | -105.1895 | 17.3172 | -0.19424 | -0.00018804 | 0.0062314 | 0.0077459 | -0.0092434 | -0.0043515 | 0.0040525 | -104.8508 | 17.2897 | -105.7022 | 17.0975 | 16.2872 | 2.6459 | 17.0105 | -6.8802 | 17.2073 | -105.6656 | -0.51269 | -0.027466 | 0.33875 | 122.287 | -1.03 | -0.47607 | -0.10986 | 0.85144 | 122.2 | 98.3093 | 121.4767 | 122.4792 | 0.33875 | 122.3969 | 107.8354 | -0.47607 | 122.4792 | 0.33875 | 107.8354 | 121.4767 | 122.3969 | -123.0194 | -122.9828
3038.9062 | 122.8455 | -113.2965 | 9.3475 | -0.25528 | 0.0030164 | 0.0072996 | 0.020777 | -0.0051846 | -0.00071986 | 0.0027707 | -112.3856 | 9.7137 | -113.2736 | 9.2468 | 8.8852 | 1.1215 | 9.2102 | -8.7479 | 9.4986 | -113.7268 | 0.022888 | 0.36621 | 0.91095 | 122.5433 | -0.46234 | -0.4303 | 0.15106 | 0.88806 | 122.5067 | 104.5486 | 122.1817 | 123.0103 | 0.91095 | 122.7951 | 114.418 | -0.4303 | 123.0103 | 0.91095 | 114.418 | 122.1817 | 122.7951 | -122.6212 | -123.0743
3039.9062 | 122.9599 | -115.6998 | 6.958 | -0.13321 | -0.00082884 | 0.0015316 | 0.014155 | -0.0056118 | -0.0022153 | 0.0044797 | -115.0864 | 6.9031 | -116.0156 | 7.0175 | 6.4362 | 0.82855 | 6.6101 | -9.0134 | 6.9809 | -116.066 | -0.31586 | -0.054932 | 0.6134 | 122.7173 | -0.52185 | -0.36621 | 0.022888 | 0.92926 | 122.3099 | 106.6864 | 122.1359 | 122.6028 | 0.6134 | 122.6807 | 116.5283 | -0.36621 | 122.6028 | 0.6134 | 116.5283 | 122.1359 | 122.6807 | -122.9736 | -123.024
3040.9062 | 122.9324 | -101.6556 | 20.8557 | -0.072174 | -0.0014696 | -0.00060462 | 0.011805 | -0.0062528 | -0.0026425 | 0.0012753 | -100.6531 | 21.6476 | -101.3855 | 21.286 | 20.4254 | 2.5177 | 21.0159 | -6.1157 | 21.2265 | -101.8295 | 0.27008 | 0.79193 | 1.0025 | 122.9416 | -0.4303 | -0.17395 | 0.37079 | 0.73242 | 122.6715 | 95.5399 | 122.081 | 123.3032 | 1.0025 | 122.8821 | 104.1733 | -0.17395 | 123.3032 | 1.0025 | 104.1733 | 122.081 | 122.8821 | -122.2412 | -122.6852
3041.9062 | 122.9004 | -114.9216 | 7.7087 | 0.019379 | -0.0025378 | 0.0015316 | 0.016291 | -0.008389 | -0.0017881 | 0.0014889 | -114.3631 | 8.3405 | -115.0635 | 7.6355 | 7.1457 | 2.0142 | 7.4524 | -9.0683 | 7.6355 | -115.2969 | -0.14191 | 0.63171 | 0.55847 | 122.5571 | -0.56305 | -0.37537 | -0.073242 | 0.70038 | 122.374 | 105.8533 | 122.0673 | 123.262 | 0.55847 | 122.5571 | 116.9357 | -0.37537 | 123.262 | 0.55847 | 116.9357 | 122.0673 | 122.5571 | -122.7722 | -123.0057
3042.9062 | 122.8958 | -112.5046 | 10.199 | -0.68253 | -0.00082884 | 0.001318 | 0.018427 | -0.0075344 | -0.00093346 | 0.0040525 | -111.9461 | 10.1486 | -112.825 | 10.2905 | 9.6954 | 1.2863 | 10.0296 | -8.5419 | 10.2814 | -112.8067 | -0.32043 | -0.050354 | 0.55847 | 122.7951 | -0.50354 | -0.30212 | 0.082397 | 0.87891 | 122.5342 | 103.9627 | 122.2 | 122.6532 | 0.55847 | 122.7859 | 113.7909 | -0.30212 | 122.6532 | 0.55847 | 113.7909 | 122.2 | 122.7859 | -123.024 | -123.0057
3043.9062 | 123.0423 | -114.8849 | 7.7637 | -0.1561 | 0.0013074 | 0.0051632 | 0.017359 | -0.0086026 | -0.0011471 | 0.0023435 | -114.1525 | 7.8323 | -115.0772 | 7.8598 | 7.251 | 0.95215 | 7.5302 | -9.1141 | 7.8598 | -115.1871 | -0.19226 | 0.068664 | 0.73242 | 122.7448 | -0.51269 | -0.30212 | 0.09613 | 0.92468 | 122.4152 | 105.7709 | 122.1359 | 122.7173 | 0.73242 | 122.7448 | 115.8371 | -0.30212 | 122.7173 | 0.73242 | 115.8371 | 122.1359 | 122.7448 | -122.8409 | -122.9507
3044.9062 | 122.8958 | -114.7659 | 7.8049 | 0.16434 | 0.00023916 | 0.003027 | 0.017359 | -0.0077482 | 0.00077554 | 0.0057615 | -114.4638 | 7.7408 | -115.2466 | 7.7591 | 7.3013 | 1.8539 | 7.5531 | -9.3658 | 7.814 | -115.242 | -0.48065 | -0.064087 | 0.30212 | 122.525 | -0.50354 | -0.47607 | 0.009155 | 0.78278 | 122.319 | 105.4001 | 122.0673 | 122.5067 | 0.30212 | 122.58 | 116.6199 | -0.47607 | 122.5067 | 0.30212 | 116.6199 | 122.0673 | 122.58 | -123.0515 | -123.0469
3045.9062 | 122.905 | -115.3152 | 7.3288 | 0.17197 | 0.0023756 | 0.0038816 | 0.017573 | -0.0079618 | -0.0017881 | 0.0025571 | -114.7888 | 7.3517 | -115.6082 | 7.2281 | 6.6971 | 1.5381 | 7.045 | -9.4162 | 7.3105 | -115.741 | -0.29297 | 0.022889 | 0.52643 | 122.5433 | -0.63171 | -0.42572 | -0.01831 | 0.8194 | 122.3602 | 105.899 | 122.0123 | 122.6669 | 0.52643 | 122.6257 | 116.8533 | -0.42572 | 122.6669 | 0.52643 | 116.8533 | 122.0123 | 122.6257 | -122.937 | -123.0698
3046.9062 | 122.8867 | -106.1508 | 16.4062 | 0.17197 | -0.00018804 | 0.0017454 | 0.015864 | -0.0071072 | 0.00077554 | 0.0064023 | -105.8212 | 16.2369 | -106.6818 | 16.571 | 15.6326 | 2.8656 | 16.0904 | -7.3242 | 16.4474 | -106.5674 | -0.53101 | -0.16937 | 0.32959 | 122.7219 | -0.77362 | -0.41657 | 0.041199 | 0.8606 | 122.2412 | 98.8266 | 121.7834 | 122.3877 | 0.32959 | 122.5983 | 109.0164 | -0.41657 | 122.3877 | 0.32959 | 109.0164 | 121.7834 | 122.5983 | -123.0881 | -122.9736
3047.9062 | 122.905 | -108.609 | 14.0305 | 0.27878 | 0.0034436 | 0.0060178 | 0.019282 | -0.0053982 | -0.0020017 | 0.0051205 | -108.3069 | 13.8382 | -109.1354 | 14.6988 | 13.6826 | 3.0579 | 13.7695 | -7.9514 | 14.1998 | -108.9249 | -0.52643 | -0.19226 | 0.30212 | 123.3078 | -0.3479 | -0.31586 | 0.16937 | 0.82855 | 122.3785 | 100.6577 | 122.2916 | 122.4472 | 0.30212 | 122.8088 | 111.6669 | -0.31586 | 122.4472 | 0.30212 | 111.6669 | 122.2916 | 122.8088 | -123.1659 | -122.9553
3048.9219 | 122.8455 | -110.9253 | 11.7508 | -0.24002 | 0.0010938 | 0.0023862 | 0.018854 | -0.0071072 | 0.00013454 | 0.0029843 | -110.2341 | 11.8698 | -111.0764 | 12.0163 | 11.38 | 3.2043 | 11.7142 | -8.4045 | 12.03 | -111.2732 | -0.15106 | 0.11902 | 0.69122 | 122.9416 | -0.37079 | -0.3479 | 0.27924 | 0.84229 | 122.6395 | 102.5208 | 122.3053 | 122.7951 | 0.69122 | 122.9553 | 114.1296 | -0.3479 | 122.7951 | 0.69122 | 114.1296 | 122.3053 | 122.9553 | -122.8271 | -123.024
3049.9062 | 122.8683 | -113.1729 | 9.3979 | 0.1796 | 0.004939 | 0.006445 | 0.019922 | -0.003903 | -0.0011471 | 0.0034115 | -112.6648 | 9.5444 | -113.4979 | 9.3384 | 8.725 | 2.4628 | 9.2102 | -8.7708 | 9.4528 | -113.6444 | -0.32501 | 0.14649 | 0.50812 | 122.5113 | -0.67291 | -0.4715 | 0.054932 | 0.83313 | 122.3831 | 104.4022 | 121.8979 | 122.7173 | 0.50812 | 122.6257 | 115.6357 | -0.4715 | 122.7173 | 0.50812 | 115.6357 | 121.8979 | 122.6257 | -122.8958 | -123.0423
3050.9062 | 122.818 | -110.5637 | 11.9614 | 0.32455 | 0.0040846 | 0.0045224 | 0.023554 | -0.003262 | -0.00071986 | 0.0021299 | -110.2524 | 11.8561 | -111.1313 | 11.8011 | 11.2747 | 2.2797 | 12.0895 | -8.1253 | 12.0666 | -110.9985 | -0.56763 | -0.10529 | 0.31128 | 122.3648 | -0.68665 | -0.43488 | 0.10528 | 0.87891 | 122.6532 | 102.4384 | 121.8384 | 122.4197 | 0.31128 | 122.6303 | 112.8433 | -0.43488 | 122.4197 | 0.31128 | 112.8433 | 121.8384 | 122.6303 | -123.0927 | -122.9599
3051.9062 | 122.8729 | -109.5703 | 13.0005 | 0.1796 | 0.0036572 | 0.0060178 | 0.019282 | -0.0036892 | 0.00077554 | 0.0021299 | -109.0805 | 13.0966 | -109.9228 | 13.0737 | 12.3596 | 2.8107 | 12.9501 | -7.9147 | 13.1012 | -109.9411 | -0.35248 | 0.096131 | 0.48981 | 122.644 | -0.64087 | -0.37079 | 0.10071 | 0.84229 | 122.5204 | 101.6556 | 121.9299 | 122.6669 | 0.48981 | 122.6715 | 112.381 | -0.37079 | 122.6669 | 0.48981 | 112.381 | 121.9299 | 122.6715 | -122.9233 | -122.9416
3052.9062 | 122.8546 | -107.222 | 15.4266 | 0.1796 | 0.0053662 | 0.0085812 | 0.022486 | -0.0017666 | -0.0026425 | 0.0083249 | -107.0206 | 15.239 | -107.7713 | 15.0604 | 14.3188 | 2.9709 | 15.2664 | -7.5256 | 15.2435 | -107.7621 | -0.54932 | -0.18768 | 0.20142 | 122.2824 | -1.1078 | -0.54016 | -0.18311 | 0.75073 | 122.4884 | 99.6964 | 121.5408 | 122.4609 | 0.20142 | 122.4655 | 110.1929 | -0.54016 | 122.4609 | 0.20142 | 110.1929 | 121.5408 | 122.4655 | -123.1979 | -123.1888
3053.9219 | 122.9416 | -107.6706 | 14.9048 | 0.87387 | -0.001256 | 0.0045224 | 0.012873 | -0.0053982 | -0.0028561 | 0.0042661 | -107.2311 | 14.7491 | -108.1879 | 14.9643 | 14.3463 | 2.8381 | 14.7537 | -7.4066 | 14.9643 | -107.9498 | -0.51727 | -0.15564 | 0.43945 | 122.6349 | -0.55847 | -0.27924 | 0.059509 | 0.95673 | 122.4243 | 100.264 | 122.0169 | 122.4197 | 0.43945 | 122.6349 | 110.5087 | -0.27924 | 122.4197 | 0.43945 | 110.5087 | 122.0169 | 122.6349 | -123.0927 | -122.8546
3054.9062 | 122.8317 | -105.8807 | 16.8091 | 0.1796 | 0.0017346 | 0.0068722 | 0.018213 | -0.0019802 | -7.9062e-05 | 0.0021299 | -105.5374 | 16.6718 | -106.3751 | 16.8274 | 16.0355 | 2.6138 | 16.6168 | -7.2784 | 16.7038 | -106.0959 | -0.49439 | -0.13733 | 0.34332 | 122.7081 | -0.77362 | -0.21515 | -0.10529 | 0.83771 | 122.4976 | 98.6023 | 121.9162 | 122.5525 | 0.34332 | 122.5845 | 108.4946 | -0.21515 | 122.5525 | 0.34332 | 108.4946 | 121.9162 | 122.5845 | -123.1842 | -122.905
3055.9062 | 122.7951 | -109.7031 | 13.0737 | 0.049896 | 0.0038708 | 0.005377 | 0.023554 | -0.0019802 | -0.0015745 | 0.0023435 | -109.6573 | 12.4741 | -110.4767 | 12.9501 | 12.2681 | 2.7924 | 12.8906 | -7.8461 | 12.9776 | -110.0876 | -0.77362 | -0.59967 | 0.045776 | 122.6532 | -0.80566 | -0.38452 | -0.09613 | 0.8194 | 122.5937 | 101.857 | 121.9711 | 122.1771 | 0.045776 | 122.6807 | 112.4954 | -0.38452 | 122.1771 | 0.045776 | 112.4954 | 121.9711 | 122.6807 | -123.5504 | -123.1613
3056.9062 | 122.8226 | -107.46 | 15.1382 | -0.12558 | 0.0040846 | 0.008154 | 0.020777 | -0.002194 | -0.0015745 | 0.0031979 | -107.0572 | 14.9826 | -108.0185 | 14.9231 | 14.2822 | 2.7924 | 14.946 | -8.1985 | 15.0467 | -107.9498 | -0.55847 | -0.15564 | 0.40283 | 122.3831 | -0.85602 | -0.48981 | -0.091553 | 0.9613 | 122.406 | 99.2615 | 121.7422 | 122.4426 | 0.40283 | 122.5067 | 110.2524 | -0.48981 | 122.4426 | 0.40283 | 110.2524 | 121.7422 | 122.5067 | -123.1567 | -123.0881
3057.9062 | 122.8455 | -107.8766 | 14.827 | -0.14084 | 0.00323 | 0.0062314 | 0.018 | -0.0011258 | -0.00093346 | 0.0025571 | -107.3776 | 14.772 | -108.2703 | 14.7766 | 14.209 | 3.0441 | 14.7308 | -7.8094 | 14.8544 | -108.252 | -0.39368 | -0.054931 | 0.49896 | 122.6532 | -0.61798 | -0.37537 | 0.027466 | 0.89264 | 122.6074 | 100.0671 | 122.0856 | 122.6486 | 0.49896 | 122.731 | 110.9207 | -0.37537 | 122.6486 | 0.49896 | 110.9207 | 122.0856 | 122.731 | -123.0972 | -123.0789
3058.9219 | 122.9004 | -114.8117 | 7.8094 | 0.042267 | 0.001521 | 0.0023862 | 0.012232 | -0.0013394 | -0.00093346 | 0.0027707 | -114.3127 | 7.8003 | -115.1916 | 7.7637 | 7.1274 | 0.99335 | 7.4707 | -9.7092 | 7.814 | -115.1825 | -0.37994 | -0.009155 | 0.49896 | 122.5754 | -0.68207 | -0.37079 | 0.004578 | 0.87891 | 122.2824 | 105.1025 | 121.9391 | 122.612 | 0.49896 | 122.6257 | 115.8051 | -0.37079 | 122.612 | 0.49896 | 115.8051 | 121.9391 | 122.6257 | -123.0011 | -122.9919
3059.9062 | 122.8455 | -114.5096 | 8.2077 | -0.018768 | 0.0028028 | 0.0043088 | 0.024408 | -0.003903 | -0.0020017 | 0.0014889 | -113.9465 | 8.075 | -114.8941 | 8.2764 | 7.6675 | 1.1307 | 8.107 | -9.9609 | 8.3496 | -114.8529 | -0.38452 | -0.13275 | 0.56305 | 122.786 | -0.54016 | -0.34332 | 0.14191 | 0.94757 | 122.6166 | 104.5486 | 122.1771 | 122.5845 | 0.56305 | 122.8592 | 115.6403 | -0.34332 | 122.5845 | 0.56305 | 115.6403 | 122.1771 | 122.8592 | -123.1018 | -123.0606
3060.9062 | 122.8592 | -114.9902 | 7.6721 | -0.095062 | 0.0036572 | 0.00089078 | 0.021631 | -0.0026212 | -0.0017881 | 0.0070431 | -113.9374 | 7.8369 | -115.0909 | 7.5577 | 7.0312 | 1.1078 | 7.457 | -10.6476 | 7.6996 | -115.3885 | -0.10071 | 0.16479 | 1.0529 | 122.5479 | -0.64087 | -0.39826 | 0.027466 | 1.1536 | 122.4472 | 104.3427 | 122.0215 | 122.8271 | 1.0529 | 122.6898 | 116.098 | -0.39826 | 122.8271 | 1.0529 | 116.098 | 122.0215 | 122.6898 | -122.7631 | -123.0606
3061.9062 | 122.8317 | -113.2004 | 9.4894 | -0.2095 | 0.0036572 | 0.0077268 | 0.020777 | -0.00091219 | -0.0024289 | 0.0046933 | -112.5916 | 9.5169 | -113.5345 | 9.4162 | 8.8806 | 1.7395 | 9.375 | -8.6609 | 9.5535 | -113.5666 | -0.33417 | 0.027466 | 0.60882 | 122.6166 | -0.60883 | -0.36621 | 0.064087 | 0.94299 | 122.5754 | 104.5395 | 122.081 | 122.7173 | 0.60882 | 122.7539 | 114.9399 | -0.36621 | 122.7173 | 0.60882 | 114.9399 | 122.081 | 122.7539 | -123.024 | -123.056
3062.9062 | 122.8912 | -114.006 | 8.725 | -0.24002 | 0.0034436 | 0.004736 | 0.016932 | -0.001553 | -0.0013609 | 0.0025571 | -113.4109 | 8.7296 | -114.3036 | 8.6655 | 8.107 | 1.2634 | 8.5648 | -11.5585 | 8.7662 | -114.3539 | -0.29755 | 0.004577 | 0.59509 | 122.6715 | -0.61798 | -0.3479 | 0.041198 | 0.89264 | 122.5708 | 102.4475 | 122.113 | 122.7356 | 0.59509 | 122.7722 | 115.2695 | -0.3479 | 122.7356 | 0.59509 | 115.2695 | 122.113 | 122.7722 | -123.0286 | -123.0789
3063.9062 | 122.8592 | -113.1363 | 9.5581 | -0.049286 | 0.0040846 | 0.006445 | 0.021204 | -0.0026212 | -0.0020017 | 0.0019163 | -112.5549 | 9.5581 | -113.4476 | 9.4437 | 8.8806 | 0.67749 | 9.4391 | -8.8028 | 9.6313 | -113.475 | -0.31128 | 0 | 0.58136 | 122.58 | -0.67749 | -0.33875 | 0.073243 | 0.89264 | 122.5754 | 104.3335 | 122.0169 | 122.6944 | 0.58136 | 122.7676 | 113.8138 | -0.33875 | 122.6944 | 0.58136 | 113.8138 | 122.0169 | 122.7676 | -123.0057 | -123.0331
3064.9062 | 122.818 | -114.5599 | 8.1894 | -0.26291 | 2.5564e-05 | 0.004736 | 0.014795 | -0.0060392 | -0.0013609 | 0.0029843 | -113.9694 | 8.1253 | -114.8254 | 8.0292 | 7.5165 | 1.0666 | 8.0246 | -9.9335 | 8.2489 | -114.8895 | -0.2655 | -0.064087 | 0.59052 | 122.5891 | -0.67291 | -0.32959 | 0.059509 | 0.85602 | 122.5845 | 104.6265 | 122.0764 | 122.6852 | 0.59052 | 122.8088 | 115.6265 | -0.32959 | 122.6852 | 0.59052 | 115.6265 | 122.0764 | 122.8088 | -123.0148 | -123.0789
3065.9062 | 122.8729 | -113.8687 | 8.8531 | -0.056915 | 0.0019482 | 0.0049496 | 0.022486 | -0.0028348 | -0.00093346 | 0.0081113 | -113.2553 | 8.844 | -114.1846 | 8.8165 | 8.2169 | 0.41657 | 8.7387 | -9.6085 | 8.9127 | -114.1983 | -0.31586 | -0.009155 | 0.6134 | 122.6852 | -0.63629 | -0.32959 | 0.05951 | 0.92926 | 122.6074 | 104.2603 | 122.0856 | 122.7127 | 0.6134 | 122.7814 | 114.2853 | -0.32959 | 122.7127 | 0.6134 | 114.2853 | 122.0856 | 122.7814 | -123.0377 | -123.0515
3066.9062 | 122.818 | -115.0909 | 7.7545 | -0.3392 | 0.001521 | 0.001959 | 0.019709 | -0.0024076 | -0.00093346 | 0.0046933 | -114.4775 | 7.5119 | -115.4068 | 7.5211 | 7.045 | 0.11902 | 7.814 | -10.0983 | 7.8506 | -115.2283 | -0.31586 | -0.24261 | 0.6134 | 122.612 | -0.70953 | -0.13733 | 0.09613 | 0.92926 | 122.905 | 104.9927 | 122.1359 | 122.6028 | 0.6134 | 122.9416 | 115.21 | -0.13733 | 122.6028 | 0.6134 | 115.21 | 122.1359 | 122.9416 | -123.1613 | -122.9828
3067.9062 | 122.8043 | -109.3369 | 13.3438 | -0.4155 | -0.0010424 | 0.0058042 | 0.014582 | -0.0041166 | -0.0034971 | 0.0025571 | -109.1537 | 13.0829 | -109.9045 | 13.0005 | 12.4283 | 2.8519 | 13.2706 | -8.4778 | 13.2111 | -109.7763 | -0.56763 | -0.26093 | 0.18311 | 122.3373 | -0.91553 | -0.43945 | -0.13275 | 0.75073 | 122.6074 | 100.8591 | 121.7651 | 122.4197 | 0.18311 | 122.5479 | 112.1887 | -0.43945 | 122.4197 | 0.18311 | 112.1887 | 121.7651 | 122.5479 | -123.2483 | -123.1201
3068.9062 | 122.85 | -111.1862 | 11.4075 | -0.13321 | 0.0019482 | 0.0055906 | 0.026545 | -0.0034756 | -0.0017881 | 0.0029843 | -109.5703 | 12.1628 | -110.6598 | 11.5173 | 10.8215 | 3.035 | 11.2289 | -9.0866 | 11.5997 | -111.5753 | 0.52643 | 0.75531 | 1.6159 | 122.7036 | -0.58594 | -0.3891 | 0.19226 | 1.0895 | 122.4152 | 102.0996 | 122.0078 | 123.349 | 1.6159 | 122.7859 | 114.2212 | -0.3891 | 123.349 | 1.6159 | 114.2212 | 122.0078 | 122.7859 | -122.0673 | -122.9828
3069.9062 | 122.8363 | -103.1067 | 19.4778 | -0.17899 | 0.0030164 | 0.0028134 | 0.014795 | -0.0073208 | -0.0011471 | 0.0061887 | -103.2074 | 19.1299 | -103.9169 | 19.5236 | 18.5165 | 2.5589 | 19.3817 | -7.3105 | 19.4321 | -103.6194 | -0.81024 | -0.3479 | -0.10071 | 122.6303 | -0.9613 | -0.5127 | -0.045776 | 0.70953 | 122.4884 | 95.7962 | 121.6232 | 122.2366 | -0.10071 | 122.5388 | 105.6656 | -0.5127 | 122.2366 | -0.10071 | 105.6656 | 121.6232 | 122.5388 | -123.3948 | -123.0972
3070.9062 | 122.9736 | -113.7909 | 8.7845 | -0.12558 | -0.00040164 | -0.0012454 | 0.0133 | -0.0053982 | -0.0022153 | 0.0023435 | -113.0905 | 8.844 | -113.9008 | 8.9767 | 8.2993 | 0.52185 | 8.4 | -9.8557 | 8.9722 | -114.1068 | -0.10986 | 0.059509 | 0.70038 | 122.7676 | -0.48523 | -0.31586 | 0.18768 | 0.81024 | 122.1909 | 103.9352 | 122.0901 | 122.6349 | 0.70038 | 122.7631 | 114.3127 | -0.31586 | 122.6349 | 0.70038 | 114.3127 | 122.0901 | 122.7631 | -122.6852 | -122.8912
3071.9062 | 122.9507 | -111.8317 | 10.7483 | -0.079803 | 0.00045296 | 0.005377 | 0.013727 | -0.0056118 | -0.0026425 | 0.0038389 | -111.2366 | 10.8444 | -112.0834 | 10.9177 | 10.3912 | 3.186 | 10.6842 | -8.9401 | 10.9268 | -112.1567 | -0.25177 | 0.09613 | 0.59509 | 122.7493 | -0.35706 | -0.32501 | 0.17853 | 0.84686 | 122.5159 | 102.8915 | 122.2229 | 122.6761 | 0.59509 | 122.7585 | 115.0177 | -0.32501 | 122.6761 | 0.59509 | 115.0177 | 122.2229 | 122.7585 | -122.8317 | -122.905
3072.9062 | 122.9324 | -108.8287 | 13.7146 | -0.2858 | 0.001521 | 0.0015316 | 0.015864 | -0.0075344 | -0.0013609 | 0.0038389 | -108.3115 | 14.0442 | -109.108 | 13.8336 | 12.9959 | 2.9114 | 13.4903 | -8.2581 | 13.7192 | -109.2865 | -0.27924 | 0.32959 | 0.51727 | 122.6624 | -0.71869 | -0.45776 | 0.004577 | 0.79651 | 122.319 | 100.5707 | 121.8246 | 122.8729 | 0.51727 | 122.5479 | 111.7401 | -0.45776 | 122.8729 | 0.51727 | 111.7401 | 121.8246 | 122.5479 | -122.8226 | -123.0011
3073.9062 | 122.9553 | -106.2378 | 16.3559 | -0.1561 | 0.00023916 | -0.003168 | 0.012659 | -0.0096708 | -0.0024289 | 0.0034115 | -105.5466 | 16.5802 | -106.5537 | 16.4886 | 15.5869 | 2.861 | 16.6397 | -7.7408 | 16.5756 | -106.4804 | -0.31586 | 0.2243 | 0.69122 | 122.7264 | -0.76904 | -0.24262 | 0.21973 | 1.0071 | 122.8775 | 98.497 | 121.8246 | 122.818 | 0.69122 | 122.8134 | 109.0988 | -0.24262 | 122.818 | 0.69122 | 109.0988 | 121.8246 | 122.8134 | -122.9095 | -122.8363
3074.9062 | 123.0057 | -99.1333 | 23.378 | -0.12558 | 0.00066656 | 0.0032406 | 0.013086 | -0.0075344 | -0.0041379 | 0.00084806 | -99.1837 | 22.879 | -99.9207 | 22.9431 | 22.2153 | 2.4719 | 22.8561 | -6.3812 | 23.0392 | -99.7375 | -0.78735 | -0.49896 | -0.050354 | 122.0764 | -1.1627 | -0.60425 | -0.33875 | 0.737 | 121.9894 | 92.7521 | 121.3486 | 122.0123 | -0.050354 | 122.1725 | 101.6052 | -0.60425 | 122.0123 | -0.050354 | 101.6052 | 121.3486 | 122.1725 | -123.2986 | -123.1155
3075.9062 | 122.9416 | -116.9403 | 5.6717 | -0.079803 | 0.0013074 | 0.0051632 | 0.01565 | -0.0096708 | 0.00034814 | 0.0019163 | -116.4001 | 5.5984 | -117.334 | 5.6488 | 5.2094 | 1.4923 | 5.4886 | -10.0433 | 5.7358 | -117.3248 | -0.39368 | -0.073242 | 0.54016 | 122.5891 | -0.46234 | -0.38452 | 0.064087 | 0.93384 | 122.4289 | 106.897 | 122.1497 | 122.5388 | 0.54016 | 122.6761 | 118.4326 | -0.38452 | 122.5388 | 0.54016 | 118.4326 | 122.1497 | 122.6761 | -123.0057 | -122.9965
3076.9062 | 122.9095 | -104.7455 | 17.7475 | -0.064545 | -0.0016834 | 0.0011044 | 0.013941 | -0.0077482 | -0.00093346 | 0.0021299 | -104.3564 | 17.7567 | -105.2673 | 18.3929 | 16.9144 | 2.7512 | 17.2577 | -7.5211 | 17.7338 | -105.3223 | -0.52185 | 0.009155 | 0.3891 | 123.1384 | -0.83313 | -0.57678 | -0.013733 | 0.91095 | 122.0032 | 97.2244 | 121.6599 | 122.5021 | 0.3891 | 122.4792 | 107.4966 | -0.57678 | 122.5021 | 0.3891 | 107.4966 | 121.6599 | 122.4792 | -123.0148 | -123.0698
3077.9062 | 122.9233 | -107.4371 | 15.1382 | 0.034637 | 0.0010938 | 0.001318 | 0.013941 | -0.0075344 | 0.0012027 | 0.0040525 | -107.0847 | 15.1611 | -107.8217 | 15.3214 | 14.978 | 2.8839 | 14.978 | -7.9056 | 15.2893 | -107.7621 | -0.38452 | 0.022888 | 0.35248 | 122.7585 | -0.16022 | -0.32501 | 0.15106 | 0.737 | 122.4152 | 99.5316 | 122.4152 | 122.5983 | 0.35248 | 122.7264 | 110.321 | -0.32501 | 122.5983 | 0.35248 | 110.321 | 122.4152 | 122.7264 | -122.9599 | -122.9004
3078.9062 | 122.9141 | -106.2607 | 16.3651 | 0.233 | -0.00018804 | -0.00039102 | 0.015223 | -0.0077482 | -0.0030697 | 0.0049069 | -106.0226 | 16.008 | -106.8192 | 16.2048 | 15.4953 | 2.6962 | 16.1041 | -7.0541 | 16.42 | -104.686 | -0.55847 | -0.35706 | 0.23804 | 122.4655 | -0.86975 | 1.5747 | 0.054932 | 0.79651 | 122.3648 | 99.2065 | 121.756 | 122.2687 | 0.23804 | 122.6807 | 108.9569 | 1.5747 | 122.2687 | 0.23804 | 108.9569 | 121.756 | 122.6807 | -123.1842 | -121.051
3079.9062 | 122.9828 | -107.0847 | 15.5045 | -0.049286 | -0.00018804 | 0.0021726 | 0.013727 | -0.0062528 | -0.00029266 | 0.0027707 | -106.6269 | 15.4221 | -107.5378 | 15.4999 | 14.7125 | 2.7832 | 15.2756 | -8.1436 | 15.4816 | -107.4692 | -0.45319 | -0.082398 | 0.45776 | 122.5845 | -0.79193 | -0.38452 | -0.022889 | 0.91095 | 122.3602 | 98.941 | 121.7972 | 122.5067 | 0.45776 | 122.5662 | 109.8679 | -0.38452 | 122.5067 | 0.45776 | 109.8679 | 121.7972 | 122.5662 | -123.0423 | -122.9736
3080.9062 | 122.9095 | -108.7601 | 13.9023 | 0.21011 | 0.00066656 | -0.00017722 | 0.015436 | -0.004971 | -0.0011471 | 0.0023435 | -108.3801 | 13.4949 | -109.2773 | 13.6551 | 13.0051 | 2.8427 | 13.6047 | -8.1207 | 13.7741 | -109.1812 | -0.51727 | -0.40741 | 0.37994 | 122.4152 | -0.89722 | -0.42114 | -0.12817 | 0.89722 | 122.3648 | 100.6393 | 121.7651 | 122.2549 | 0.37994 | 122.5342 | 111.6028 | -0.42114 | 122.2549 | 0.37994 | 111.6028 | 121.7651 | 122.5342 | -123.1796 | -123.0835
3081.9062 | 122.8958 | -112.4405 | 10.1807 | -0.072174 | 0.0019482 | 0.0015316 | 0.01565 | -0.0053982 | 0.00034814 | 0.0040525 | -111.9781 | 10.1624 | -112.825 | 10.3592 | 9.6588 | 3.0075 | 10.0296 | -9.0912 | 10.2676 | -112.8159 | -0.38452 | -0.01831 | 0.46234 | 122.7997 | -0.52185 | -0.37537 | 0.086975 | 0.84686 | 122.4701 | 103.3493 | 122.0993 | 122.6028 | 0.46234 | 122.7081 | 115.448 | -0.37537 | 122.6028 | 0.46234 | 115.448 | 122.0993 | 122.7081 | -123.0057 | -122.9965
3082.9062 | 122.8775 | -103.7933 | 18.718 | 0.11093 | 0.00066656 | 0.00024998 | 0.014368 | -0.0043302 | -7.9062e-05 | 0.0019163 | -102.887 | 18.8416 | -103.7979 | 18.544 | 17.6422 | 2.4948 | 18.6768 | -6.8481 | 18.8461 | -104.1641 | -0.004578 | 0.1236 | 0.90637 | 122.3373 | -1.0757 | -0.37079 | 0.12817 | 0.91095 | 122.4701 | 96.9452 | 121.4355 | 122.6349 | 0.90637 | 122.6395 | 106.2881 | -0.37079 | 122.6349 | 0.90637 | 106.2881 | 121.4355 | 122.6395 | -122.5159 | -122.8821
3083.9062 | 120.4697 | -109.5474 | 13.028 | -2.1245 | 0.00066656 | 0.01029 | 0.015436 | -0.0068936 | -0.0011471 | 0.00084806 | -109.0347 | 12.9456 | -109.9274 | 13.2248 | 12.5015 | 3.0808 | 12.8128 | -7.9926 | 13.0371 | -109.877 | -0.37994 | -0.082397 | 0.5127 | 122.7722 | -0.52643 | -0.32959 | 0.009155 | 0.89264 | 122.3602 | 101.5549 | 122.049 | 122.493 | 0.5127 | 122.5845 | 112.6282 | -0.32959 | 122.493 | 0.5127 | 112.6282 | 122.049 | 122.5845 | -122.9553 | -122.905
3084.9062 | 122.9645 | -112.326 | 10.2219 | -0.17899 | 0.00023916 | 0.0034544 | 0.020136 | -0.0053982 | -0.00071986 | 0.0066159 | -111.8912 | 10.1852 | -112.7792 | 10.4736 | 9.668 | 2.3392 | 9.9152 | -9.6725 | 10.318 | -112.7563 | -0.45319 | -0.036621 | 0.43488 | 122.7997 | -0.55389 | -0.4303 | 0.09613 | 0.88806 | 122.2412 | 102.6535 | 121.994 | 122.5113 | 0.43488 | 122.644 | 114.6652 | -0.4303 | 122.5113 | 0.43488 | 114.6652 | 121.994 | 122.644 | -123.0011 | -122.9782
3085.9062 | 122.9004 | -114.2395 | 8.3771 | 0.18723 | 0.0017346 | 3.6382e-05 | 0.019495 | -0.0058256 | -0.0022153 | 0.0040525 | -113.7405 | 8.0612 | -114.7018 | 8.3084 | 7.8461 | 1.7624 | 8.0566 | -9.6954 | 8.3221 | -114.7568 | -0.46234 | -0.31586 | 0.49896 | 122.5479 | -0.53101 | -0.51727 | -0.054931 | 0.9613 | 122.2961 | 104.5441 | 122.0856 | 122.3007 | 0.49896 | 122.5616 | 116.0019 | -0.51727 | 122.3007 | 0.49896 | 116.0019 | 122.0856 | 122.5616 | -123.0789 | -123.1339
3086.9062 | 122.9004 | -102.6306 | 19.9814 | 0.18723 | 0.0017346 | 0.005377 | 0.012873 | -0.0056118 | -7.9062e-05 | 0.0036253 | -102.0721 | 20.0912 | -102.887 | 20.2194 | 19.1803 | 2.5406 | 19.9493 | -7.5302 | 20.0729 | -102.9053 | -0.25635 | 0.10986 | 0.55847 | 122.85 | -0.80109 | -0.27466 | 0.091553 | 0.81482 | 122.58 | 95.1004 | 121.8109 | 122.7219 | 0.55847 | 122.7036 | 105.1712 | -0.27466 | 122.7219 | 0.55847 | 105.1712 | 121.8109 | 122.7036 | -122.8683 | -122.8867
3087.9062 | 122.8455 | -115.8554 | 6.7932 | 0.17197 | 0.001521 | 3.6382e-05 | 0.018641 | -0.0062528 | -0.0013609 | 0.0042661 | -115.3107 | 6.7474 | -116.2262 | 6.7612 | 6.2347 | 1.2863 | 6.4774 | -10.5881 | 6.8207 | -116.2628 | -0.37079 | -0.045776 | 0.54474 | 122.6166 | -0.55847 | -0.40741 | 0.027466 | 0.91553 | 122.3328 | 105.2673 | 122.0901 | 122.6028 | 0.54474 | 122.6761 | 117.1417 | -0.40741 | 122.6028 | 0.54474 | 117.1417 | 122.0901 | 122.6761 | -123.0194 | -123.056
3088.9219 | 122.9416 | -114.9033 | 7.782 | -0.23239 | 0.002162 | 0.0055906 | 0.016932 | -0.0075344 | -0.0015745 | 0.0042661 | -114.4455 | 7.5439 | -115.3336 | 7.7316 | 7.2784 | 0.87433 | 7.5302 | -9.8648 | 7.782 | -115.2237 | -0.4303 | -0.23804 | 0.45776 | 122.6349 | -0.50354 | -0.32043 | 0 | 0.88806 | 122.4335 | 105.0385 | 122.1817 | 122.4472 | 0.45776 | 122.6852 | 115.7776 | -0.32043 | 122.4472 | 0.45776 | 115.7776 | 122.1817 | 122.6852 | -123.1155 | -123.0057
3089.9062 | 122.9324 | -107.254 | 15.6921 | 0.20248 | 0.0019482 | 0.008154 | 0.01565 | -0.0068936 | -0.0017881 | 0.0034115 | -106.81 | 15.2252 | -107.7576 | 15.2161 | 14.4516 | 2.8427 | 14.9048 | -8.5052 | 15.1428 | -107.8217 | -0.50354 | -0.46692 | 0.44403 | 122.4701 | -1.2405 | -0.56763 | -0.54932 | 0.94757 | 122.1588 | 98.7488 | 121.7056 | 122.4792 | 0.44403 | 122.3969 | 110.0967 | -0.56763 | 122.4792 | 0.44403 | 110.0967 | 121.7056 | 122.3969 | -123.4497 | -123.5138
3090.9062 | 122.9324 | -107.9086 | 14.653 | 0.50766 | 0.0013074 | 0.0070858 | 0.018427 | -0.0047574 | -0.00050626 | 0.0036253 | -107.1167 | 14.7491 | -108.1512 | 14.8682 | 14.1998 | 2.9068 | 14.5569 | -8.4549 | 14.8087 | -108.1879 | -0.24262 | 0.096131 | 0.79193 | 122.7768 | -0.45319 | -0.27924 | 0.15564 | 1.0345 | 122.4655 | 99.4537 | 122.1085 | 122.6578 | 0.79193 | 122.7173 | 110.8154 | -0.27924 | 122.6578 | 0.79193 | 110.8154 | 122.1085 | 122.7173 | -122.8043 | -122.8409
3091.9062 | 122.9599 | -106.8604 | 15.7242 | 0.24063 | 0.0025892 | 0.0051632 | 0.019922 | -0.0034756 | -0.0015745 | 0.0019163 | -106.6681 | 15.4541 | -107.5104 | 15.4495 | 14.74 | 2.8336 | 15.1703 | -8.1116 | 15.4678 | -107.3959 | -0.65002 | -0.27008 | 0.19226 | 122.3099 | -0.98419 | -0.53558 | -0.25635 | 0.84228 | 122.0306 | 98.7488 | 121.6003 | 122.3145 | 0.19226 | 122.3282 | 109.6939 | -0.53558 | 122.3145 | 0.19226 | 109.6939 | 121.6003 | 122.3282 | -123.2346 | -123.1201
3092.9062 | 122.8821 | -109.1217 | 13.504 | 0.20248 | 0.0034436 | 0.005377 | 0.020777 | -0.004971 | -0.0013609 | 0.0027707 | -108.6639 | 13.4171 | -109.5291 | 13.5818 | 12.7945 | 2.8748 | 13.2889 | -8.6517 | 13.5315 | -109.5016 | -0.40741 | -0.086975 | 0.45776 | 122.7036 | -0.70953 | -0.37994 | 0.027466 | 0.86517 | 122.4106 | 100.47 | 121.9162 | 122.5388 | 0.45776 | 122.6532 | 111.9965 | -0.37994 | 122.5388 | 0.45776 | 111.9965 | 121.9162 | 122.6532 | -123.0331 | -123.0057
3093.9062 | 122.9462 | -109.0942 | 13.4537 | -0.17136 | 0.0017346 | 0.0034544 | 0.017786 | -0.0043302 | -0.0013609 | 0.0042661 | -108.4167 | 13.678 | -109.2545 | 13.7833 | 13.0142 | 2.9114 | 13.1332 | -8.8577 | 13.5681 | -109.4696 | -0.16022 | 0.22431 | 0.67749 | 122.8775 | -0.43945 | -0.37537 | 0.11444 | 0.83771 | 122.2275 | 100.2365 | 122.1085 | 122.7722 | 0.67749 | 122.6624 | 112.0056 | -0.37537 | 122.7722 | 0.67749 | 112.0056 | 122.1085 | 122.6624 | -122.7081 | -122.9233
3094.9062 | 122.9233 | -110.8017 | 11.792 | 0.21774 | 0.00066656 | 0.0055906 | 0.019922 | -0.0077482 | -0.0032835 | 0.0044797 | -110.0006 | 11.8698 | -111.0535 | 11.7554 | 11.3113 | 2.8839 | 11.5356 | -9.1324 | 11.8103 | -111.1725 | -0.25177 | 0.07782 | 0.80109 | 122.5571 | -0.48065 | -0.37079 | 0.018311 | 1.0529 | 122.3373 | 101.6693 | 122.113 | 122.6715 | 0.80109 | 122.612 | 113.6856 | -0.37079 | 122.6715 | 0.80109 | 113.6856 | 122.113 | 122.612 | -122.8455 | -122.9645
3095.9062 | 122.9553 | -116.2537 | 6.459 | 0.21774 | 2.5564e-05 | 0.0049496 | 0.019495 | -0.0030484 | -0.0022153 | 0.0053343 | -115.6448 | 6.395 | -116.5695 | 6.9031 | 6.0883 | 1.4328 | 6.1066 | -11.3937 | 6.6101 | -116.5604 | -0.31586 | -0.064087 | 0.60883 | 123.1567 | -0.37079 | -0.3067 | 0.15106 | 0.92468 | 122.3602 | 104.8599 | 122.3419 | 122.6486 | 0.60883 | 122.8638 | 117.6865 | -0.3067 | 122.6486 | 0.60883 | 117.6865 | 122.3419 | 122.8638 | -123.0286 | -123.0194
3096.9062 | 122.9507 | -115.8142 | 6.8024 | 0.17197 | 0.0038708 | 0.0077268 | 0.022699 | -0.0056118 | -0.00050626 | 0.0014889 | -115.2695 | 6.8024 | -116.1392 | 6.7612 | 6.2439 | 0.64087 | 6.4728 | -10.5469 | 6.8756 | -116.1896 | -0.32501 | 0 | 0.54474 | 122.5754 | -0.55847 | -0.37537 | 0.073242 | 0.86975 | 122.287 | 105.2673 | 122.0581 | 122.6166 | 0.54474 | 122.6898 | 116.4551 | -0.37537 | 122.6166 | 0.54474 | 116.4551 | 122.0581 | 122.6898 | -122.9416 | -122.9919
3097.9062 | 122.9462 | -116.0339 | 6.5872 | 0.24826 | 0.0038708 | 0.003668 | 0.022059 | -0.003262 | -0.0013609 | 0.0051205 | -115.448 | 6.5735 | -116.3544 | 6.5414 | 6.0654 | 0.35706 | 6.2576 | -10.1807 | 6.6238 | -116.4368 | -0.32043 | -0.013733 | 0.58594 | 122.5754 | -0.52185 | -0.40283 | 0.036621 | 0.90637 | 122.2916 | 105.8533 | 122.0993 | 122.6074 | 0.58594 | 122.6578 | 116.391 | -0.40283 | 122.6074 | 0.58594 | 116.391 | 122.0993 | 122.6578 | -122.9416 | -123.024
3098.9062 | 122.937 | -114.1068 | 8.4778 | 0.1033 | 0.0019482 | 0.0045224 | 0.019282 | -0.0034756 | -0.0039243 | 0.0049069 | -113.5529 | 8.4961 | -114.5233 | 8.4778 | 8.0154 | 1.1902 | 8.2764 | -9.6085 | 8.4961 | -114.4867 | -0.41656 | 0.018311 | 0.55389 | 122.5845 | -0.46234 | -0.37994 | 0.018311 | 0.97046 | 122.3831 | 104.4983 | 122.1222 | 122.6028 | 0.55389 | 122.6028 | 115.2969 | -0.37994 | 122.6028 | 0.55389 | 115.2969 | 122.1222 | 122.6028 | -123.0011 | -122.9645
3099.9062 | 122.8363 | -116.7664 | 5.9235 | 0.16434 | 0.0045118 | 0.0043088 | 0.022272 | -0.0043302 | -0.00071986 | 0.0044797 | -116.2125 | 5.9326 | -117.1097 | 5.8182 | 5.3284 | 0.71869 | 5.7266 | -10.3226 | 5.9784 | -117.1646 | -0.34332 | 0.009155 | 0.55389 | 122.5845 | -0.59509 | -0.39826 | 0.054932 | 0.89722 | 122.493 | 106.4438 | 122.0947 | 122.699 | 0.55389 | 122.7448 | 117.485 | -0.39826 | 122.699 | 0.55389 | 117.485 | 122.0947 | 122.7448 | -123.0331 | -123.0881
3100.9062 | 122.8912 | -116.5512 | 6.0699 | 0.22537 | 0.0040846 | 0.0068722 | 0.024195 | -0.0041166 | -0.0011471 | 0.0010617 | -116.0568 | 6.0699 | -116.954 | 5.9418 | 5.4749 | 0.93384 | 5.7999 | -10.2951 | 6.0883 | -116.9861 | -0.40283 | 0 | 0.49438 | 122.493 | -0.59509 | -0.43488 | 0.018311 | 0.89722 | 122.3511 | 106.2561 | 122.0261 | 122.6212 | 0.49438 | 122.6395 | 117.485 | -0.43488 | 122.6212 | 0.49438 | 117.485 | 122.0261 | 122.6395 | -123.024 | -123.056
3101.9062 | 122.85 | -111.7401 | 10.9497 | 0.21011 | 0.0042982 | 0.006445 | 0.020991 | -0.00091219 | -7.9062e-05 | 0.0034115 | -111.1221 | 10.9406 | -112.0468 | 10.7712 | 10.1944 | 2.8152 | 10.881 | -9.1644 | 11.0092 | -112.0377 | -0.3067 | -0.009155 | 0.61798 | 122.5113 | -0.75531 | -0.29755 | 0.059509 | 0.92468 | 122.6212 | 102.5757 | 121.9345 | 122.6807 | 0.61798 | 122.7493 | 114.5554 | -0.29755 | 122.6807 | 0.61798 | 114.5554 | 121.9345 | 122.7493 | -122.9965 | -122.9874
3102.9062 | 122.8271 | -111.351 | 11.2106 | 0.21011 | 0.0045118 | 0.0032406 | 0.022272 | -0.0036892 | -0.0032835 | 0.0034115 | -110.6781 | 11.3434 | -111.6623 | 11.087 | 10.4965 | 2.7145 | 11.0641 | -9.2468 | 11.2427 | -111.8546 | -0.31128 | 0.13275 | 0.67291 | 122.438 | -0.71411 | -0.50354 | 0.032044 | 0.98419 | 122.4152 | 102.1042 | 121.8475 | 122.6944 | 0.67291 | 122.5937 | 114.0656 | -0.50354 | 122.6944 | 0.67291 | 114.0656 | 121.8475 | 122.5937 | -122.8729 | -123.0652
3103.9062 | 122.8775 | -111.8088 | 10.8673 | 0.16434 | 0.0038708 | 0.0070858 | 0.020563 | -0.0030484 | -0.0037107 | 0.0044797 | -111.1588 | 10.8948 | -112.1201 | 10.936 | 10.3363 | 2.7328 | 10.73 | -9.3979 | 10.9222 | -112.1841 | -0.31128 | 0.027465 | 0.65002 | 122.7448 | -0.53101 | -0.37537 | 0.054931 | 0.9613 | 122.5388 | 102.4109 | 122.1451 | 122.7036 | 0.65002 | 122.731 | 114.5416 | -0.37537 | 122.7036 | 0.65002 | 114.5416 | 122.1451 | 122.731 | -122.9874 | -123.0515
3104.9062 | 122.7859 | -115.036 | 7.6172 | 0.13382 | 0.00323 | 0.0079404 | 0.021631 | -0.00069859 | -0.0020017 | 0.0040525 | -114.6011 | 7.5577 | -115.4984 | 7.3517 | 6.8619 | 1.6251 | 7.4707 | -10.144 | 7.6035 | -115.5029 | -0.46234 | -0.059509 | 0.43488 | 122.3877 | -0.75531 | -0.46692 | -0.013732 | 0.89722 | 122.5067 | 104.892 | 121.8979 | 122.5937 | 0.43488 | 122.6395 | 116.6611 | -0.46692 | 122.5937 | 0.43488 | 116.6611 | 121.8979 | 122.6395 | -123.1155 | -123.1201
3105.9062 | 122.8088 | -66.2659 | 56.1768 | -0.064545 | 0.00323 | 0.0085812 | 0.0073187 | 0.00036961 | -0.0037107 | 0.0029843 | -64.9475 | 57.0877 | -65.8905 | 57.1014 | 54.8904 | 0.40741 | 57.1793 | 1.8448 | 56.9962 | -66.33 | 0.37537 | 0.91095 | 1.3184 | 123.3673 | -1.2863 | -0.064087 | 0.8194 | 0.94299 | 123.4451 | 68.1107 | 121.1563 | 123.3536 | 1.3184 | 123.262 | 66.6733 | -0.064087 | 123.3536 | 1.3184 | 66.6733 | 121.1563 | 123.262 | -122.0673 | -122.5067
3106.9062 | 122.818 | -109.7397 | 12.8448 | -0.59097 | 0.00323 | 0.0087948 | 0.021631 | -0.001553 | -0.0013609 | 0.0021299 | -109.1904 | 13.0051 | -110.051 | 12.767 | 12.0666 | 2.4811 | 12.6526 | -9.581 | 12.8036 | -110.2524 | -0.31128 | 0.16022 | 0.54932 | 122.5067 | -0.7782 | -0.5127 | -0.041199 | 0.86059 | 122.3923 | 100.1587 | 121.8063 | 122.7448 | 0.54932 | 122.5433 | 112.2208 | -0.5127 | 122.7448 | 0.54932 | 112.2208 | 121.8063 | 122.5433 | -122.8958 | -123.0972
3107.9062 | 122.8088 | -111.0352 | 11.6272 | 0.049896 | 0.0042982 | 0.0060178 | 0.021418 | -0.001553 | -0.0030697 | 0.0046933 | -110.6644 | 11.5494 | -111.4334 | 11.4761 | 10.849 | 2.8198 | 11.5585 | -9.8969 | 11.6364 | -111.4563 | -0.39826 | -0.07782 | 0.37079 | 122.5113 | -0.7782 | -0.42114 | 0.009156 | 0.76904 | 122.5937 | 101.1383 | 121.8842 | 122.5845 | 0.37079 | 122.6715 | 113.855 | -0.42114 | 122.5845 | 0.37079 | 113.855 | 121.8842 | 122.6715 | -123.0606 | -123.0835
3108.9219 | 122.9324 | -107.2586 | 15.3214 | 0.16434 | 0.0013074 | 0.0058042 | 0.011164 | -0.00091219 | -0.0022153 | 0.0046933 | -106.7551 | 15.4129 | -107.6614 | 15.2618 | 14.621 | 2.6093 | 15.0467 | -8.5419 | 15.2664 | -107.6706 | -0.40283 | 0.091553 | 0.50354 | 122.5204 | -0.70038 | -0.41199 | -0.054932 | 0.90637 | 122.3053 | 98.7167 | 121.8796 | 122.6715 | 0.50354 | 122.525 | 109.8679 | -0.41199 | 122.6715 | 0.50354 | 109.8679 | 121.8796 | 122.525 | -122.9828 | -122.9919
3109.9062 | 122.8409 | -107.5653 | 15.033 | -0.0035098 | 0.0034436 | 0.0058042 | 0.022059 | -0.0017666 | -0.0030697 | 0.0034115 | -107.1213 | 15.1016 | -108.0414 | 15.3351 | 14.4424 | 2.3529 | 14.4836 | -8.8852 | 15.0146 | -108.0734 | -0.47607 | 0.068665 | 0.44403 | 122.9004 | -0.59051 | -0.50812 | -0.018311 | 0.9201 | 122.049 | 98.6801 | 122.0078 | 122.6669 | 0.44403 | 122.58 | 109.9182 | -0.50812 | 122.6669 | 0.44403 | 109.9182 | 122.0078 | 122.58 | -123.0743 | -123.1064
3110.9062 | 122.7859 | -77.6779 | 44.3253 | 0.027008 | 0.0034436 | 0.0062314 | 0.01095 | 0.00015601 | -0.0032835 | 0.0025571 | -78.7033 | 42.366 | -79.8843 | 44.8563 | 45.2454 | 0.60425 | 45.6436 | -0.6134 | 45.7672 | -77.0874 | -2.2064 | -1.9592 | -1.0254 | 122.5342 | 0.9201 | 0.59051 | 1.442 | 1.181 | 123.3215 | 77.0645 | 122.9233 | 120.0439 | -1.0254 | 123.4451 | 78.2822 | 0.59051 | 120.0439 | -1.0254 | 78.2822 | 122.9233 | 123.4451 | -124.2096 | -121.4127
3111.9062 | 122.9141 | -62.7594 | 53.9383 | -0.17136 | 0.0028028 | 0.0060178 | 0.0075323 | -0.0019802 | -0.0024289 | 0.0059751 | -64.0045 | 58.2687 | -64.769 | 59.0057 | 57.4402 | 0.050354 | 59.4131 | 2.8976 | 59.3994 | -63.4598 | -2.0096 | 4.3304 | -1.2451 | 121.7651 | 3.5019 | -0.70038 | 5.4611 | 0.76446 | 122.1725 | 65.657 | 120.1996 | 121.0281 | -1.2451 | 122.1588 | 62.8098 | -0.70038 | 121.0281 | -1.2451 | 62.8098 | 120.1996 | 122.1588 | -118.7073 | -117.3981
3112.9062 | 123.0148 | -85.2356 | 37.207 | -0.24002 | 0.0038708 | 0.0032406 | 0.015436 | -0.003262 | -0.00093346 | 0.0027707 | -88.0463 | 33.1512 | -89.5432 | 34.1812 | 32.5104 | 0.8194 | 37.738 | -1.0941 | 36.2045 | -86.0229 | -4.3076 | -4.0558 | -2.8107 | 119.4168 | -4.6967 | -0.78735 | -1.0025 | 1.4969 | 122.9736 | 84.1415 | 117.746 | 118.3868 | -2.8107 | 121.4401 | 86.055 | -0.78735 | 118.3868 | -2.8107 | 86.055 | 117.746 | 121.4401 | -126.7502 | -123.23
3113.9062 | 122.9691 | -108.6365 | 13.9252 | -0.041657 | 0.00323 | 0.0075132 | 0.020136 | -0.0011258 | -0.00029266 | 0.0031979 | -108.252 | 13.7695 | -109.2453 | 13.9206 | 13.266 | 1.5884 | 13.7604 | -9.462 | 13.9252 | -109.1949 | -0.60882 | -0.15564 | 0.38452 | 122.5571 | -0.65918 | -0.55847 | 0 | 0.99335 | 122.3969 | 99.1745 | 121.9025 | 122.406 | 0.38452 | 122.5616 | 110.2249 | -0.55847 | 122.406 | 0.38452 | 110.2249 | 121.9025 | 122.5616 | -123.1705 | -123.1201
3114.9062 | 122.8867 | -107.9956 | 14.6255 | -0.14847 | 0.0053662 | 0.0058042 | 0.018641 | -0.0013394 | -0.0028561 | 0.0038389 | -107.5653 | 14.5248 | -108.522 | 14.4974 | 13.8977 | 1.6663 | 14.5111 | -9.0958 | 14.6759 | -108.4579 | -0.52643 | -0.10071 | 0.4303 | 122.493 | -0.72784 | -0.46234 | 0.050354 | 0.95673 | 122.5067 | 98.8998 | 121.8933 | 122.5204 | 0.4303 | 122.6715 | 109.6619 | -0.46234 | 122.5204 | 0.4303 | 109.6619 | 121.8933 | 122.6715 | -123.1476 | -123.0835
3115.9062 | 122.8912 | -67.5797 | 54.4922 | -0.24765 | 0.0028028 | -0.0010318 | 0.0060369 | -0.0024076 | -0.00029266 | 0.0027707 | -66.7145 | 55.7693 | -67.3279 | 54.3961 | 53.1052 | 0.19226 | 55.1376 | 1.3046 | 55.069 | -67.8909 | 0.25177 | 1.2772 | 0.86517 | 121.9757 | -1.387 | -0.31128 | 0.57678 | 0.6134 | 122.7173 | 68.8843 | 120.6848 | 123.349 | 0.86517 | 122.6486 | 67.7719 | -0.31128 | 123.349 | 0.86517 | 67.7719 | 120.6848 | 122.6486 | -121.8201 | -122.3831
3116.9062 | 122.9828 | -66.1377 | 50.885 | -0.19424 | 0.0036572 | 0.006445 | 0.0043281 | -0.00091219 | -0.0032835 | 0.0027707 | -66.5955 | 55.8243 | -67.2363 | 55.7327 | 53.9566 | 0.16937 | 55.8746 | 1.355 | 55.8701 | -67.1951 | -1.0986 | 4.9393 | -0.45776 | 121.8704 | 3.0716 | -1.0574 | 4.985 | 0.64087 | 122.0123 | 67.4927 | 120.0943 | 121.962 | -0.45776 | 122.0078 | 66.3071 | -1.0574 | 121.962 | -0.45776 | 66.3071 | 120.0943 | 122.0078 | -118.1213 | -118.0801
3117.9062 | 122.8775 | -67.2409 | 55.069 | -0.1561 | 0.0019482 | -0.00017722 | 0.0032599 | -0.002194 | -0.0026425 | 0.0023435 | -67.0212 | 55.4855 | -67.4011 | 55.0781 | 52.3911 | 0.21973 | 54.0802 | 1.7441 | 54.6433 | -67.8909 | -0.16022 | 0.41656 | 0.21973 | 122.319 | -2.6779 | -0.65002 | -0.42572 | 0.37994 | 121.3211 | 68.985 | 119.632 | 122.7264 | 0.21973 | 121.8842 | 67.4606 | -0.65002 | 122.7264 | 0.21973 | 67.4606 | 119.632 | 121.8842 | -122.4701 | -122.9599
3118.9062 | 122.8729 | -71.608 | 50.4822 | -0.37735 | 0.0036572 | 0.005377 | 0.0094549 | -0.0024076 | -0.0015745 | 0.0044797 | -88.7833 | 25.5295 | -92.5873 | 51.828 | 48.4131 | 0.59052 | 51.0773 | 1.2589 | 50.7065 | -72.1024 | -20.9793 | -24.9527 | -17.1753 | 123.436 | -2.0691 | -0.49438 | 0.2243 | 3.804 | 122.6852 | 72.8668 | 120.0211 | 97.1375 | -17.1753 | 122.3145 | 72.1985 | -0.49438 | 97.1375 | -17.1753 | 72.1985 | 120.0211 | 122.3145 | -143.0695 | -122.5845
3119.9688 | 122.0627 | -81.5277 | 49.1089 | -0.19424 | 0.00045296 | 3.6382e-05 | 0.016718 | -0.0058256 | -0.0011471 | 0.0042661 | -110.2112 | 11.9156 | -111.1038 | 11.8607 | 13.7329 | 3.6804 | 47.9187 | 14.8911 | 33.7418 | -89.0945 | -29.5761 | -37.1933 | -28.6835 | 93.3884 | -35.376 | -7.5668 | -15.3671 | 0.89264 | 129.4464 | 96.4188 | 95.2606 | 93.4433 | -28.6835 | 115.2695 | 85.2081 | -7.5668 | 93.4433 | -28.6835 | 85.2081 | 95.2606 | 115.2695 | -160.2127 | -138.2034
3120.9062 | 122.8226 | -63.4781 | 58.4427 | -0.23239 | 0.0028028 | 0.0051632 | -0.0025079 | -0.0041166 | 0.00034814 | 0.0038389 | -63.8809 | 58.5617 | -64.4989 | 58.4656 | 56.8039 | 0.10071 | 58.9142 | 2.0462 | 58.8226 | -64.1464 | -1.0208 | 0.11902 | -0.40283 | 121.9437 | -1.6388 | -0.66833 | 0.37994 | 0.61798 | 122.3923 | 65.5243 | 120.282 | 122.0398 | -0.40283 | 122.3007 | 63.5788 | -0.66833 | 122.0398 | -0.40283 | 63.5788 | 120.282 | 122.3007 | -122.9416 | -122.5891
3121.9062 | 122.7814 | -63.8809 | 58.1863 | -0.18662 | 0.0045118 | 0.004736 | 0.0043281 | -0.0043302 | -0.0015745 | 0.0014889 | -63.6703 | 58.6029 | -64.3662 | 59.1843 | 56.9229 | 0.13733 | 58.6945 | 1.6891 | 58.7631 | -64.3753 | -0.48523 | 0.41656 | 0.21057 | 123.0652 | -1.2634 | -0.49438 | 0.57678 | 0.6958 | 122.5754 | 65.5701 | 120.8038 | 122.4838 | 0.21057 | 122.644 | 64.0182 | -0.49438 | 122.4838 | 0.21057 | 64.0182 | 120.8038 | 122.644 | -122.5525 | -122.5616
3122.9062 | 122.4792 | -63.1622 | 58.7631 | -0.14084 | 0.0019482 | 0.0028134 | 0.0060369 | -0.003903 | -0.0011471 | 0.0040525 | -63.6292 | 58.6761 | -64.3616 | 58.9096 | 57.1289 | 0.1236 | 59.024 | 1.8997 | 58.9188 | -64.2059 | -1.1993 | -0.086976 | -0.46692 | 122.0718 | -1.6342 | -1.0437 | 0.15564 | 0.73242 | 122.1863 | 65.0619 | 120.2911 | 121.8384 | -0.46692 | 122.081 | 63.2858 | -1.0437 | 121.8384 | -0.46692 | 63.2858 | 120.2911 | 122.081 | -123.1247 | -122.9691
3123.9062 | 122.9233 | -64.7232 | 52.0432 | -0.064545 | 0.0028028 | 0.0021726 | 0.0075323 | -0.001553 | -0.0013609 | 0.00042086 | -65.4465 | 56.7444 | -66.2247 | 56.9504 | 55.1788 | 0.16479 | 56.8039 | 1.6937 | 57.074 | -65.7669 | -1.5015 | 4.7012 | -0.72327 | 121.6736 | 3.1357 | -1.0437 | 5.0308 | 0.7782 | 121.5271 | 66.4169 | 119.902 | 121.4676 | -0.72327 | 121.7972 | 64.888 | -1.0437 | 121.4676 | -0.72327 | 64.888 | 119.902 | 121.7972 | -118.2678 | -117.8101
3124.9062 | 122.4564 | -65.0711 | 57.2983 | -0.18662 | 0.0030164 | 0.0023862 | 0.0056097 | -0.0028348 | -0.0015745 | 0.0036253 | -63.9313 | 57.6599 | -65.2176 | 57.3257 | 55.5038 | 0.13733 | 57.3532 | 1.8585 | 57.4722 | -65.5106 | -0.14648 | 0.36163 | 1.1398 | 122.3969 | -1.7944 | -0.43945 | 0.17395 | 1.2863 | 122.4243 | 66.9296 | 120.575 | 122.731 | 1.1398 | 122.5433 | 65.2084 | -0.43945 | 122.731 | 1.1398 | 65.2084 | 120.575 | 122.5433 | -122.5159 | -122.8088
3125.9062 | 122.9095 | -67.2226 | 54.7485 | -0.24002 | 0.00066656 | 0.0040952 | 0.0036871 | -0.0053982 | -7.9062e-05 | 0.0014889 | -66.2018 | 57.1335 | -66.4673 | 55.7465 | 53.9017 | 0.22888 | 55.4764 | 0.89722 | 55.5313 | -67.5385 | 0.75531 | 2.3849 | 1.0208 | 122.9691 | -0.84686 | -0.31586 | 0.78278 | 0.2655 | 122.699 | 68.1198 | 121.1243 | 124.3561 | 1.0208 | 122.7539 | 67.4515 | -0.31586 | 124.3561 | 1.0208 | 67.4515 | 121.1243 | 122.7539 | -121.2158 | -122.287
3126.9062 | 122.6486 | -68.2343 | 54.0344 | -0.22476 | 0.00045296 | 0.0025998 | 0.0006965 | -0.00668 | -0.0015745 | 0.0019163 | -68.0099 | 54.2084 | -68.7424 | 54.6844 | 52.858 | 0.32044 | 53.8879 | 0.3479 | 54.1809 | -68.8889 | -0.50812 | 0.17395 | 0.2243 | 122.9187 | -1.1765 | -0.6546 | 0.14648 | 0.73242 | 122.1222 | 68.5822 | 121.0922 | 122.4426 | 0.2243 | 122.4152 | 68.5547 | -0.6546 | 122.4426 | 0.2243 | 68.5547 | 121.0922 | 122.4152 | -122.7768 | -122.9233
3127.9062 | 122.85 | -67.955 | 54.6936 | -0.24002 | 2.5564e-05 | 0.00089078 | 0.0056097 | -0.004971 | -0.0015745 | 0.0014889 | -67.6025 | 54.6158 | -68.3121 | 54.7852 | 52.9678 | 0.20142 | 54.8172 | 1.0071 | 54.808 | -68.1931 | -0.35706 | -0.07782 | 0.35248 | 122.7402 | -1.7258 | -0.23804 | 0.11444 | 0.70953 | 122.7722 | 68.9621 | 120.9229 | 122.5708 | 0.35248 | 122.7631 | 68.1564 | -0.23804 | 122.5708 | 0.35248 | 68.1564 | 120.9229 | 122.7631 | -123.0057 | -122.8867
3128.9062 | 122.8317 | -68.9804 | 53.2791 | 0.034637 | 0.0051526 | 0.0058042 | 0.010523 | -0.0041166 | -0.00093346 | 0.0012753 | -68.898 | 53.4302 | -69.5297 | 53.6682 | 51.7044 | 0.25177 | 53.1326 | 0.50354 | 53.3844 | -69.6671 | -0.54932 | 0.15106 | 0.082398 | 122.6486 | -1.5747 | -0.68664 | 0.10529 | 0.63171 | 122.113 | 69.4839 | 120.6848 | 122.4106 | 0.082398 | 122.3648 | 69.2322 | -0.68664 | 122.4106 | 0.082398 | 69.2322 | 120.6848 | 122.3648 | -122.8088 | -122.9462
3129.9219 | 122.9004 | -70.285 | 52.359 | 0.11856 | 0.0019482 | -0.00017722 | 0.0049689 | -0.0026212 | -0.00050626 | 0.0019163 | -69.7128 | 52.4185 | -70.5093 | 52.4185 | 50.5508 | 0.41199 | 52.1713 | 0.45319 | 52.3224 | -70.6238 | -0.2243 | 0.059509 | 0.5722 | 122.7036 | -1.8082 | -0.33875 | -0.036621 | 0.79651 | 122.4564 | 70.7382 | 120.8359 | 122.7036 | 0.5722 | 122.6074 | 70.697 | -0.33875 | 122.7036 | 0.5722 | 70.697 | 120.8359 | 122.6074 | -122.8683 | -122.9828
3130.9062 | 122.818 | -71.2692 | 51.3199 | -0.29343 | 0.0017346 | 0.0032406 | 0.0079595 | -0.0053982 | -0.00093346 | 0.0017027 | -69.7861 | 51.8784 | -70.871 | 52.1576 | 50.2075 | 0.31128 | 51.4114 | -0.1831 | 51.7044 | -71.4935 | 0.39825 | 0.55847 | 1.4832 | 123.4268 | -1.1124 | -0.2243 | 0.38452 | 1.0849 | 122.6807 | 71.0861 | 121.4767 | 123.1476 | 1.4832 | 122.9736 | 71.5805 | -0.2243 | 123.1476 | 1.4832 | 71.5805 | 121.4767 | 122.9736 | -122.1909 | -122.8134
3131.9062 | 122.8226 | -71.2143 | 51.5121 | -0.16373 | 0.0013074 | -0.00060462 | 0.0077459 | -0.0062528 | -0.00050626 | 0.0017027 | -70.8984 | 51.4481 | -71.5713 | 51.7914 | 50.0977 | 0.35248 | 51.5121 | 0.16937 | 51.5991 | -71.4798 | -0.35706 | -0.064087 | 0.31586 | 123.0057 | -1.4145 | -0.2655 | 0.086975 | 0.67291 | 122.7264 | 71.3837 | 121.3119 | 122.6624 | 0.31586 | 122.8134 | 71.5668 | -0.2655 | 122.6624 | 0.31586 | 71.5668 | 121.3119 | 122.8134 | -123.0835 | -122.9919
3132.9062 | 122.9736 | -71.8002 | 50.7935 | -0.17136 | -0.00061524 | 0.004736 | 0.0051825 | -0.0062528 | -0.0022153 | 0.0021299 | -71.2097 | 50.9216 | -71.9513 | 51.3382 | 49.5529 | 0.49896 | 50.6012 | 0.10529 | 50.9125 | -72.0703 | -0.15106 | 0.12817 | 0.59051 | 123.1384 | -1.2405 | -0.27008 | 0.11902 | 0.74158 | 122.4014 | 71.9055 | 121.3531 | 122.7219 | 0.59051 | 122.7127 | 72.2992 | -0.27008 | 122.7219 | 0.59051 | 72.2992 | 121.3531 | 122.7127 | -122.7448 | -122.8638
3133.9062 | 122.8867 | -105.0659 | 17.3401 | -0.2095 | 0.0047254 | 0.00067718 | 0.023768 | -0.003903 | 0.00013454 | 0.0051205 | -102.6855 | 20.0317 | -103.4363 | 18.1458 | 17.2806 | 1.5381 | 17.6285 | -8.8715 | 17.9489 | -105.3452 | 1.6296 | 2.6916 | 2.3804 | 123.2117 | -0.059509 | -0.27924 | 0.60883 | 0.75073 | 122.6944 | 96.1945 | 122.3465 | 125.0977 | 2.3804 | 123.0148 | 106.604 | -0.27924 | 125.0977 | 2.3804 | 106.604 | 122.3465 | 123.0148 | -120.7764 | -122.6852
3134.9219 | 122.8546 | -105.3406 | 17.2485 | 0.065155 | 0.0072888 | 0.0079404 | 0.022486 | -0.0019802 | -0.0026425 | 0.0014889 | -104.7592 | 17.395 | -105.6839 | 17.2256 | 16.4017 | 1.5152 | 17.2256 | -8.8257 | 17.3218 | -105.7297 | -0.34332 | 0.14648 | 0.58136 | 122.5662 | -0.84686 | -0.3891 | 0.073242 | 0.92468 | 122.5662 | 96.5149 | 121.7422 | 122.7356 | 0.58136 | 122.6624 | 106.8558 | -0.3891 | 122.7356 | 0.58136 | 106.8558 | 121.7422 | 122.6624 | -122.9324 | -122.9782
3135.9062 | 122.8317 | -105.9586 | 16.658 | -0.25528 | 0.0010938 | 0.0025998 | 0.014155 | -0.0041166 | -0.0026425 | 0.0023435 | -105.368 | 16.7175 | -106.2698 | 16.7999 | 16.0172 | 1.5884 | 16.777 | -8.931 | 16.864 | -106.311 | -0.31128 | 0.059509 | 0.59051 | 122.7585 | -0.64087 | -0.35248 | 0.20599 | 0.90179 | 122.7356 | 97.0276 | 121.9757 | 122.6761 | 0.59051 | 122.8226 | 107.547 | -0.35248 | 122.6761 | 0.59051 | 107.547 | 121.9757 | 122.8226 | -122.9279 | -122.9691
3136.9062 | 122.8775 | -107.4371 | 15.0742 | -0.2095 | 0.0013074 | 0.0015316 | 0.01565 | -0.0047574 | -0.0011471 | 0.0019163 | -106.1188 | 16.6809 | -106.7459 | 14.9643 | 14.2044 | 1.6205 | 15.1199 | -9.288 | 15.1062 | -107.8674 | 0.69122 | 1.6067 | 1.3184 | 122.4014 | -0.86975 | -0.4303 | 0.032043 | 0.62714 | 122.5571 | 98.1491 | 121.6415 | 124.118 | 1.3184 | 122.5433 | 109.0576 | -0.4303 | 124.118 | 1.3184 | 109.0576 | 121.6415 | 122.5433 | -121.8201 | -122.9416
3137.9062 | 122.8775 | -102.2507 | 20.3018 | -0.21713 | 0.0028028 | 0.0049496 | 0.0133 | -0.0056118 | -0.0011471 | 0.0059751 | -101.9577 | 20.0043 | -102.919 | 20.311 | 19.4366 | 1.4969 | 20.1279 | -8.0109 | 20.2835 | -102.713 | -0.66833 | -0.29755 | 0.29297 | 122.5616 | -0.86517 | -0.46234 | -0.018311 | 0.9613 | 122.3785 | 94.2398 | 121.6873 | 122.2549 | 0.29297 | 122.5342 | 103.7476 | -0.46234 | 122.2549 | 0.29297 | 103.7476 | 121.6873 | 122.5342 | -123.2208 | -123.0148
3138.9062 | 122.8958 | -65.863 | 56.4102 | -0.0035098 | 0.0036572 | 0.0072996 | 0.0086005 | -0.0013394 | 0.00077554 | 0.0019163 | -65.1947 | 57.2662 | -65.8447 | 57.6096 | 54.9637 | 0.46234 | 53.1281 | 1.2543 | 55.4443 | -67.218 | 0.01831 | 0.85602 | 0.66833 | 123.4726 | -1.4465 | -1.355 | -0.96588 | 0.65002 | 118.9911 | 67.1173 | 120.8267 | 123.1293 | 0.66833 | 121.3074 | 66.3254 | -1.355 | 123.1293 | 0.66833 | 66.3254 | 120.8267 | 121.3074 | -122.2549 | -123.6282
3139.9219 | 122.6624 | -107.6843 | 14.9323 | 0.088043 | 0.0019482 | 0.0077268 | 0.022486 | -0.0045438 | -0.0022153 | 0.0038389 | -107.1671 | 15.0375 | -108.1146 | 14.7446 | 14.0625 | 1.6067 | 14.9094 | -9.8602 | 14.9689 | -108.0414 | -0.4303 | 0.10529 | 0.51727 | 122.4289 | -0.86975 | -0.35706 | 0.036621 | 0.94757 | 122.5937 | 97.8241 | 121.7468 | 122.7219 | 0.51727 | 122.6532 | 109.2911 | -0.35706 | 122.7219 | 0.51727 | 109.2911 | 121.7468 | 122.6532 | -123.0469 | -122.9736
3140.9062 | 122.9691 | -107.9865 | 14.5798 | -0.18662 | 0.00045296 | 0.0011044 | 0.011591 | -0.0064664 | -7.9062e-05 | 0.0042661 | -107.4051 | 14.5706 | -108.284 | 14.7171 | 14.1541 | 1.8082 | 14.5157 | -9.8511 | 14.7766 | -108.371 | -0.29755 | -0.009155 | 0.58136 | 122.7036 | -0.42572 | -0.38452 | 0.19684 | 0.87891 | 122.5021 | 98.1354 | 122.1405 | 122.5571 | 0.58136 | 122.7631 | 109.7946 | -0.38452 | 122.5571 | 0.58136 | 109.7946 | 122.1405 | 122.7631 | -122.8638 | -122.9507
3141.9062 | 122.9141 | -66.5909 | 56.0761 | -0.30106 | 0.0019482 | 0.00089078 | 0.0011237 | -0.0073208 | -0.0026425 | 0.0025571 | -67.5934 | 54.8172 | -68.3899 | 55.4993 | 54.0985 | 0.21515 | 56.012 | 1.5976 | 55.8243 | -67.0303 | -1.799 | -1.2589 | -1.0025 | 122.0901 | -1.9775 | -0.43945 | -0.25177 | 0.79651 | 122.6028 | 68.1885 | 120.6894 | 121.4081 | -1.0025 | 122.4152 | 66.806 | -0.43945 | 121.4081 | -1.0025 | 66.806 | 120.6894 | 122.4152 | -124.4659 | -123.1064
3142.9062 | 122.9279 | -108.3252 | 14.2502 | -0.20187 | 2.5564e-05 | 0.0034544 | 0.014795 | -0.0053982 | -0.0024289 | 0.0025571 | -107.9865 | 13.9847 | -108.9661 | 14.2136 | 13.5132 | 1.7944 | 14.0854 | -9.8694 | 14.1998 | -108.7967 | -0.64087 | -0.2655 | 0.33874 | 122.5388 | -0.737 | -0.4715 | -0.050354 | 0.97961 | 122.4106 | 98.4558 | 121.8384 | 122.3099 | 0.33874 | 122.525 | 110.1196 | -0.4715 | 122.3099 | 0.33874 | 110.1196 | 121.8384 | 122.525 | -123.2162 | -123.0469
3143.9062 | 122.438 | -108.0048 | 14.534 | -0.12558 | 0.0017346 | 0.003668 | 0.023981 | -0.0030484 | -0.0013609 | 0.0031979 | -107.1945 | 14.7263 | -108.2016 | 14.8087 | 14.0854 | 1.6754 | 14.2502 | -9.8007 | 14.6896 | -108.4991 | -0.19684 | 0.19226 | 0.81024 | 122.8134 | -0.44861 | -0.49438 | 0.15564 | 1.0071 | 122.2549 | 98.204 | 122.0901 | 122.731 | 0.81024 | 122.6944 | 109.6802 | -0.49438 | 122.731 | 0.81024 | 109.6802 | 122.0901 | 122.6944 | -122.7356 | -123.0331
3144.9062 | 122.4564 | -66.0278 | 55.6137 | -0.25528 | -0.00061524 | 0.0058042 | 0.0028327 | -0.0043302 | -0.0032835 | 0.0029843 | -65.7715 | 56.4056 | -66.5497 | 56.3873 | 54.4785 | 0.27924 | 56.1172 | 1.4145 | 56.218 | -66.687 | -0.52185 | 0.79193 | 0.25635 | 122.4152 | -1.1353 | -0.65918 | 0.60425 | 0.7782 | 122.1451 | 67.4423 | 120.5063 | 122.4335 | 0.25635 | 122.2458 | 66.3071 | -0.65918 | 122.4335 | 0.25635 | 66.3071 | 120.5063 | 122.2458 | -122.1634 | -122.3007
3145.9062 | 122.4838 | -66.5588 | 54.9683 | -0.78171 | -0.0033922 | 0.005377 | 5.5496e-05 | -0.0043302 | -0.0022153 | 0.00020726 | -66.069 | 55.7739 | -66.8976 | 56.4743 | 54.6112 | 0.3479 | 56.282 | 1.5152 | 56.369 | -66.806 | -0.33875 | 0.80566 | 0.48981 | 123.0331 | -0.35706 | -0.24719 | 1.4008 | 0.82855 | 122.8409 | 68.074 | 121.17 | 122.3328 | 0.48981 | 122.9279 | 66.9067 | -0.24719 | 122.3328 | 0.48981 | 66.9067 | 121.17 | 122.9279 | -121.8658 | -121.7743
3146.9062 | 123.1384 | -83.3405 | 38.8596 | 0.12619 | -0.00082884 | -0.00017722 | 0.0013373 | -0.0068936 | -0.0013609 | 0.0038389 | -79.9072 | 40.2008 | -81.189 | 44.8288 | 41.4825 | 0.97504 | 37.175 | -5.8136 | 41.3223 | -82.1777 | 2.1515 | 1.3412 | 3.4332 | 128.1692 | 2.623 | 1.1627 | 2.4628 | 1.2817 | 120.5154 | 77.5269 | 124.823 | 123.5413 | 3.4332 | 124.6628 | 84.3155 | 1.1627 | 123.5413 | 3.4332 | 84.3155 | 124.823 | 124.6628 | -120.0485 | -121.0373
3147.9062 | 122.4518 | -8.0521 | 114.1663 | -0.056915 | 0.0019482 | 0.0015316 | 0.0017645 | -0.0079618 | 0.043073 | 0.060022 | -7.782 | 114.6286 | -8.4091 | 114.8987 | 33.7601 | -2.1515 | 114.3402 | 16.333 | 114.6332 | -8.3496 | -0.35706 | 0.46234 | 0.27008 | 122.9507 | -80.4062 | -0.29755 | 0.46692 | 0.62714 | 122.3923 | 24.3851 | 41.8121 | 122.6807 | 0.27008 | 122.6852 | 5.9006 | -0.29755 | 122.6807 | 0.27008 | 5.9006 | 41.8121 | 122.6852 | -122.5754 | -122.5159
3148.9062 | 118.4921 | -6.8619 | 98.5107 | -0.21713 | 0.0023756 | 0.00089078 | 0.0045417 | -0.00668 | 0.046491 | 0.061944 | -6.514 | 116.0248 | -7.132 | 116.1713 | 27.1042 | -2.0462 | 115.8234 | 15.7379 | 116.011 | -7.0679 | -0.27008 | 17.514 | 0.3479 | 123.0331 | -71.4066 | -0.20599 | 17.5003 | 0.61798 | 122.6852 | 22.5998 | 33.9661 | 122.8867 | 0.3479 | 122.8729 | 4.8157 | -0.20599 | 122.8867 | 0.3479 | 4.8157 | 33.9661 | 122.8729 | -105.6427 | -105.5786
3149.9062 | 122.2092 | -6.5002 | 115.1321 | -0.14084 | 0.00066656 | 0.0011044 | 0.0028327 | -0.0064664 | 0.049054 | 0.066858 | -6.2073 | 116.1804 | -6.8848 | 116.4276 | 25.0259 | -1.3962 | 115.6723 | 14.9689 | 116.0934 | -6.926 | -0.38452 | 1.0483 | 0.29297 | 122.9279 | -90.1062 | -0.42572 | 0.9613 | 0.67749 | 122.1725 | 21.4691 | 31.5262 | 122.6807 | 0.29297 | 122.5937 | 5.1041 | -0.42572 | 122.6807 | 0.29297 | 5.1041 | 31.5262 | 122.5937 | -122.0169 | -122.0581
3150.9062 | 122.3007 | -6.4636 | 115.1642 | -0.19424 | 2.5564e-05 | 0.00024998 | 0.0019781 | -0.0041166 | 0.048627 | 0.067285 | -6.1752 | 116.1804 | -6.8436 | 116.4642 | 23.7396 | -2.1149 | 115.773 | 14.0213 | 116.1667 | -6.8298 | -0.37994 | 1.0162 | 0.28839 | 122.9279 | -91.4246 | -0.36621 | 1.0025 | 0.66833 | 122.2366 | 20.4849 | 30.2032 | 122.644 | 0.28839 | 122.6303 | 4.3488 | -0.36621 | 122.644 | 0.28839 | 4.3488 | 30.2032 | 122.6303 | -122.0078 | -121.994
3151.9062 | 122.1863 | -6.4545 | 115.686 | -0.78934 | -0.0014696 | 3.6382e-05 | 0.0049689 | -0.0045438 | 0.049909 | 0.066644 | -6.2714 | 116.0934 | -6.9397 | 116.4185 | 22.8745 | -1.68 | 115.8188 | 13.8062 | 116.1255 | -6.8802 | -0.48523 | 0.40741 | 0.18311 | 122.8729 | -92.8116 | -0.42572 | 0.43945 | 0.66833 | 122.2733 | 20.2606 | 29.3289 | 122.5479 | 0.18311 | 122.58 | 4.7745 | -0.42572 | 122.5479 | 0.18311 | 4.7745 | 29.3289 | 122.58 | -122.6257 | -122.5662
3152.9062 | 122.4655 | -6.6742 | 115.4755 | -0.049286 | 0.00023916 | -0.0020998 | 0.0030463 | -0.0073208 | 0.05055 | 0.068994 | -6.3538 | 116.0614 | -6.9763 | 116.3361 | 22.4121 | -1.5747 | 115.6998 | 14.1769 | 116.0385 | -6.9443 | -0.30212 | 0.58594 | 0.32043 | 123.0103 | -93.0634 | -0.27008 | 0.56305 | 0.62256 | 122.374 | 20.8511 | 29.0863 | 122.7356 | 0.32043 | 122.7127 | 5.0995 | -0.27008 | 122.7356 | 0.32043 | 5.0995 | 29.0863 | 122.7127 | -122.4518 | -122.4197
3153.9062 | 120.5795 | -6.3446 | 116.2582 | -0.21713 | 0.00045296 | -0.001459 | 0.0083869 | -0.0058256 | 0.049482 | 0.067285 | -6.2439 | 116.2994 | -6.8619 | 116.3818 | 21.6476 | -1.5015 | 116.2766 | 13.7283 | 116.2994 | -6.7841 | -0.51727 | 0.041198 | 0.10071 | 122.7264 | -94.6106 | -0.43945 | 0.041198 | 0.61798 | 122.6212 | 20.0729 | 27.9922 | 122.644 | 0.10071 | 122.644 | 4.8431 | -0.43945 | 122.644 | 0.10071 | 4.8431 | 27.9922 | 122.644 | -123.1201 | -123.0423
3154.9062 | 122.4655 | -6.2393 | 116.2125 | 0.080414 | -0.00040164 | 0.0011044 | 0.0058233 | -0.0068936 | 0.05055 | 0.069421 | -5.896 | 116.5558 | -6.5277 | 116.7114 | 21.3547 | -1.5656 | 116.1713 | 14.003 | 116.5237 | -6.5048 | -0.28839 | 0.34332 | 0.34332 | 122.9507 | -94.8578 | -0.2655 | 0.31128 | 0.63171 | 122.4106 | 20.2423 | 27.594 | 122.7951 | 0.34332 | 122.7631 | 4.6738 | -0.2655 | 122.7951 | 0.34332 | 4.6738 | 27.594 | 122.7631 | -122.7402 | -122.7173
3155.9062 | 122.9507 | -99.4812 | 23.0438 | -0.064545 | 0.00023916 | 0.0015316 | 0.0030463 | -0.0045438 | 0.0069705 | 0.0036253 | -99.147 | 23.1125 | -100.0351 | 23.877 | 5.4932 | 0.33417 | 22.6456 | -7.4249 | 23.1903 | -99.8383 | -0.55389 | 0.068665 | 0.33417 | 123.3582 | -17.5507 | -0.35706 | 0.14649 | 0.88806 | 122.1268 | 92.0563 | 104.9744 | 122.5937 | 0.33417 | 122.6715 | 99.8154 | -0.35706 | 122.5937 | 0.33417 | 99.8154 | 104.9744 | 122.6715 | -123.0789 | -122.8821
3156.9062 | 122.9507 | -98.4558 | 24.0463 | -0.018768 | 0.002162 | 0.0049496 | 0.0043281 | -0.0088162 | 0.010175 | 0.0021299 | -97.8745 | 24.147 | -98.79 | 24.3805 | 5.9921 | 0.24261 | 23.9456 | -7.1732 | 24.1608 | -98.8266 | -0.33417 | 0.10071 | 0.58136 | 122.8363 | -18.0542 | -0.37079 | 0.11444 | 0.91553 | 122.4014 | 91.2827 | 104.4479 | 122.6028 | 0.58136 | 122.6166 | 98.6984 | -0.37079 | 122.6028 | 0.58136 | 98.6984 | 104.4479 | 122.6166 | -122.8363 | -122.8729
3157.9062 | 122.9233 | -97.3297 | 25.209 | -0.064545 | 0.001521 | 0.0023862 | 0.0036871 | -0.0064664 | 0.0088931 | 0.0038389 | -97.2931 | 24.9985 | -98.0484 | 25.0717 | 6.3629 | 0.14648 | 25.2136 | -6.7886 | 25.1999 | -97.7371 | -0.71869 | -0.21057 | 0.036621 | 122.4014 | -18.8461 | -0.40741 | -0.009155 | 0.75531 | 122.5433 | 90.5411 | 103.6926 | 122.3282 | 0.036621 | 122.5296 | 97.4762 | -0.40741 | 122.3282 | 0.036621 | 97.4762 | 103.6926 | 122.5296 | -123.2574 | -122.9462
3158.9062 | 122.9141 | -109.4833 | 13.1287 | -0.18662 | 0.00066656 | 0.0032406 | 0.012873 | -0.0053982 | 0.0039797 | 0.0038389 | -109.0759 | 13.0005 | -110.0098 | 13.1653 | 3.4058 | 1.1307 | 12.9044 | -9.5078 | 13.0829 | -109.8907 | -0.52643 | -0.12817 | 0.40741 | 122.6486 | -9.7229 | -0.40741 | -0.045776 | 0.93384 | 122.3877 | 99.9756 | 112.8891 | 122.4838 | 0.40741 | 122.5662 | 110.614 | -0.40741 | 122.4838 | 0.40741 | 110.614 | 112.8891 | 122.5662 | -123.1384 | -123.0194
3159.9062 | 122.9233 | -110.1105 | 12.5153 | -0.0035098 | 0.0019482 | -0.00039102 | 0.010096 | -0.0073208 | 0.0035525 | 0.0072569 | -110.17 | 11.6867 | -111.1862 | 12.6022 | 3.2822 | 1.1078 | 12.323 | -10.144 | 12.6114 | -110.257 | -1.0757 | -0.82855 | -0.059509 | 122.7127 | -9.2331 | -0.14648 | 0.09613 | 1.0162 | 122.4335 | 99.9664 | 113.3926 | 121.7972 | -0.059509 | 122.7219 | 111.2183 | -0.14648 | 121.7972 | -0.059509 | 111.2183 | 113.3926 | 122.7219 | -123.7015 | -122.7722
3160.9062 | 122.9233 | -109.7946 | 12.7579 | 0.1796 | 0.0030164 | 0.0062314 | 0.011805 | -0.0068936 | 0.0033389 | 0.0034115 | -109.3369 | 12.5977 | -110.3165 | 12.8448 | 3.4058 | 0.86517 | 12.4237 | -9.4208 | 12.7487 | -110.1883 | -0.52185 | -0.16022 | 0.45776 | 122.6395 | -9.3521 | -0.39368 | -0.009156 | 0.97961 | 122.2183 | 100.3738 | 113.2004 | 122.3923 | 0.45776 | 122.5433 | 110.6598 | -0.39368 | 122.3923 | 0.45776 | 110.6598 | 113.2004 | 122.5433 | -123.0743 | -122.9462
3161.9062 | 91.3376 | -117.7277 | 4.8798 | 0.14145 | 0.00023916 | 0.00046358 | 0.019495 | -0.0062528 | -0.0013609 | 0.0023435 | -117.2241 | 4.7333 | -118.222 | 4.7928 | 1.2955 | 1.6434 | 4.4952 | -11.7874 | 4.866 | -118.1305 | -0.49439 | -0.14649 | 0.50354 | 122.5204 | -3.5843 | -0.40283 | -0.013733 | 0.99793 | 122.2229 | 105.9402 | 119.0231 | 122.4609 | 0.50354 | 122.5937 | 119.371 | -0.40283 | 122.4609 | 0.50354 | 119.371 | 119.0231 | 122.5937 | -123.1018 | -123.0103
3162.9062 | 122.9599 | -94.4733 | 28.0701 | 0.065155 | 0.0017346 | 0.00089078 | 0.0006965 | -0.0053982 | 0.011029 | 0.0031979 | -94.6106 | 27.3788 | -95.4666 | 28.1479 | 7.5851 | 0.064087 | 27.7496 | -6.3446 | 27.9739 | -94.8303 | -0.99335 | -0.69122 | -0.13733 | 122.6212 | -20.4849 | -0.35705 | -0.09613 | 0.85602 | 122.2229 | 88.1287 | 102.0584 | 121.8521 | -0.13733 | 122.4472 | 94.5374 | -0.35705 | 121.8521 | -0.13733 | 94.5374 | 102.0584 | 122.4472 | -123.5367 | -122.9004
3163.9062 | 122.9553 | -114.3494 | 8.2764 | -0.92667 | -0.0023242 | 0.006445 | 0.01565 | -0.0064664 | 0.0026981 | 0.0031979 | -114.1663 | 7.7637 | -115.1596 | 8.3359 | 2.2888 | 0.79651 | 7.8964 | -11.087 | 8.4686 | -114.7293 | -0.81024 | -0.5127 | 0.18311 | 122.6852 | -5.9875 | -0.37994 | 0.19226 | 0.99335 | 122.2458 | 103.2623 | 116.6382 | 122.113 | 0.18311 | 122.818 | 115.1459 | -0.37994 | 122.113 | 0.18311 | 115.1459 | 116.6382 | 122.818 | -123.436 | -123.0057
3164.9062 | 122.8958 | -95.0317 | 27.6031 | 0.13382 | 0.0036572 | 0.0060178 | 0.0024053 | -0.0081754 | 0.0088931 | 0.0029843 | -94.3497 | 27.0035 | -95.4346 | 27.7954 | 7.4707 | 0.013733 | 26.9211 | -5.9509 | 27.4338 | -95.4208 | -0.40283 | -0.59967 | 0.68207 | 122.8271 | -20.1324 | -0.3891 | -0.16937 | 1.0849 | 121.9528 | 89.0808 | 102.5024 | 122.0352 | 0.68207 | 122.4655 | 95.0455 | -0.3891 | 122.0352 | 0.68207 | 95.0455 | 102.5024 | 122.4655 | -123.0377 | -123.024
3165.9062 | 122.9095 | -104.7592 | 17.775 | 0.21011 | 0.0010938 | 0.003027 | 0.0096685 | -0.0060392 | 0.0052615 | 0.0031979 | -104.2877 | 17.9489 | -105.0476 | 17.8528 | 4.9164 | 0.79651 | 17.6468 | -7.7728 | 17.8391 | -105.13 | -0.28839 | 0.17395 | 0.4715 | 122.612 | -12.8586 | -0.37079 | 0.064087 | 0.75989 | 122.406 | 96.9864 | 109.6756 | 122.7081 | 0.4715 | 122.5983 | 105.5557 | -0.37079 | 122.7081 | 0.4715 | 105.5557 | 109.6756 | 122.5983 | -122.8226 | -122.905
3166.9062 | 122.9004 | -110.6781 | 11.9019 | 0.11093 | 0.0019482 | 0.0090086 | 0.012659 | -0.0047574 | 0.0022707 | 0.0055479 | -109.8495 | 11.9202 | -110.9894 | 11.9019 | 3.2913 | 1.2909 | 11.8011 | -9.6359 | 11.9064 | -111.0764 | -0.31128 | 0.018311 | 0.82855 | 122.58 | -8.6105 | -0.39825 | 0.004578 | 1.1398 | 122.4792 | 101.0422 | 113.9694 | 122.5983 | 0.82855 | 122.5845 | 111.969 | -0.39825 | 122.5983 | 0.82855 | 111.969 | 113.9694 | 122.5845 | -122.8912 | -122.9782
3167.9062 | 122.9599 | -106.5125 | 16.0675 | 0.233 | 0.0023756 | 0.0051632 | 0.013086 | -0.0056118 | 0.0026981 | 0.0034115 | -106.1783 | 15.9622 | -106.9473 | 16.0629 | 4.4403 | 0.94299 | 15.8295 | -8.4183 | 16.0034 | -106.9611 | -0.43488 | -0.10529 | 0.33417 | 122.5754 | -11.6272 | -0.44861 | -0.064087 | 0.76904 | 122.3419 | 98.0942 | 110.9528 | 122.4747 | 0.33417 | 122.5159 | 107.4554 | -0.44861 | 122.4747 | 0.33417 | 107.4554 | 110.9528 | 122.5159 | -123.0148 | -123.0286
3168.9062 | 122.905 | -105.1987 | 17.3813 | 0.088043 | 0.0025892 | 0.0060178 | 0.0077459 | -0.0092434 | 0.0065433 | 0.0044797 | -104.6677 | 17.3996 | -105.574 | 17.2668 | 4.7516 | 0.80566 | 17.1295 | -8.6975 | 17.3401 | -105.5695 | -0.37537 | 0.01831 | 0.531 | 122.4655 | -12.6297 | -0.37079 | -0.041199 | 0.90637 | 122.3282 | 96.5012 | 109.9503 | 122.5983 | 0.531 | 122.5388 | 106.0043 | -0.37079 | 122.5983 | 0.531 | 106.0043 | 109.9503 | 122.5388 | -122.9553 | -122.9507
3169.9062 | 122.9187 | -107.5653 | 15.0284 | 0.17197 | 0.001521 | 0.0049496 | 0.011377 | -0.0026212 | 0.0044071 | 0.0038389 | -106.8146 | 15.0238 | -107.8354 | 15.0467 | 4.184 | 1.0254 | 14.8132 | -8.8348 | 15.0513 | -107.9498 | -0.27008 | -0.004577 | 0.75073 | 122.612 | -10.8444 | -0.38452 | 0.022889 | 1.0208 | 122.3785 | 98.7305 | 111.7493 | 122.5891 | 0.75073 | 122.6166 | 108.5907 | -0.38452 | 122.5891 | 0.75073 | 108.5907 | 111.7493 | 122.6166 | -122.8638 | -122.9782
3170.9062 | 122.9324 | -106.6772 | 15.8981 | 0.1796 | 0.0028028 | 0.0034544 | 0.016718 | -0.0030484 | 0.0061161 | 0.0010617 | -106.2561 | 15.7242 | -107.1854 | 16.0217 | 4.8019 | 0.97046 | 15.6509 | -8.7021 | 16.1179 | -107.0023 | -0.50812 | -0.17395 | 0.42114 | 122.699 | -11.0962 | -0.32501 | 0.21973 | 0.92926 | 122.3282 | 97.9752 | 111.4792 | 122.4014 | 0.42114 | 122.7951 | 107.6477 | -0.32501 | 122.4014 | 0.42114 | 107.6477 | 111.4792 | 122.7951 | -123.0835 | -122.9004
3171.9062 | 122.9507 | -101.1612 | 21.3089 | 0.31693 | 0.0023756 | 0.0060178 | 0.0096685 | -0.0024076 | 0.0054751 | 0.0036253 | -100.5753 | 21.3409 | -101.5411 | 21.5515 | 6.0242 | 0.58594 | 21.048 | -7.1594 | 21.3181 | -101.6418 | -0.37994 | 0.032043 | 0.58594 | 122.7127 | -15.2847 | -0.48065 | 0.009155 | 0.96588 | 122.2092 | 94.0018 | 107.1854 | 122.5021 | 0.58594 | 122.4792 | 101.7471 | -0.48065 | 122.5021 | 0.58594 | 101.7471 | 107.1854 | 122.4792 | -122.85 | -122.9507
3172.9062 | 122.9416 | -97.5174 | 25.1221 | 0.21011 | 0.0025892 | 0.0055906 | 0.0056097 | -0.0036892 | 0.0076113 | 0.0021299 | -96.9269 | 25.1953 | -97.8195 | 25.2502 | 6.9992 | 0.25635 | 24.8657 | -6.2759 | 25.1175 | -97.879 | -0.30212 | 0.073242 | 0.59051 | 122.7676 | -18.1229 | -0.36163 | -0.004577 | 0.89264 | 122.3831 | 91.2415 | 104.5166 | 122.7127 | 0.59051 | 122.6349 | 97.7737 | -0.36163 | 122.7127 | 0.59051 | 97.7737 | 104.5166 | 122.6349 | -122.9416 | -123.0011
3173.9062 | 88.0966 | -108.6731 | 13.9252 | 0.17197 | 0.0040846 | 0.0090086 | 0.016718 | -0.0030484 | 0.0033389 | 0.0049069 | -106.5765 | 14.2456 | -108.4076 | 15.0421 | 3.9551 | 1.0254 | 14.621 | -8.0658 | 14.6713 | -108.577 | 0.2655 | 0.32043 | 2.0966 | 123.7152 | -9.9701 | 0.096131 | 0.74615 | 1.8311 | 123.2941 | 100.6073 | 112.6282 | 122.9187 | 2.0966 | 123.3444 | 109.6985 | 0.096131 | 122.9187 | 2.0966 | 109.6985 | 112.6282 | 123.3444 | -122.3328 | -122.5021
3174.9062 | 122.818 | -98.3871 | 24.2477 | -0.011139 | 0.0042982 | 0.008154 | 0.0090277 | -0.003262 | 0.0071841 | 0.0027707 | -97.5357 | 24.5178 | -98.4741 | 24.6185 | 6.7749 | 0.19226 | 24.3073 | -6.3492 | 24.5132 | -98.7076 | -0.086975 | 0.27008 | 0.85144 | 123.0057 | -17.4728 | -0.32044 | 0.2655 | 0.93841 | 122.6944 | 92.038 | 105.162 | 122.905 | 0.85144 | 122.9004 | 98.5794 | -0.32044 | 122.905 | 0.85144 | 98.5794 | 105.162 | 122.9004 | -122.7219 | -122.9553
3175.9062 | 122.9004 | -97.7783 | 24.765 | 0.17197 | 0.0028028 | 0.0043088 | 0.0094549 | -0.0019802 | 0.010389 | 0.00020726 | -97.2473 | 24.8154 | -98.2224 | 24.4949 | 6.8344 | 0.21515 | 25.2457 | -5.9463 | 25.0214 | -98.0301 | -0.44403 | 0.050354 | 0.53101 | 122.2733 | -17.9306 | -0.25177 | 0.25635 | 0.97504 | 123.024 | 91.832 | 104.6127 | 122.5937 | 0.53101 | 122.7997 | 97.9935 | -0.25177 | 122.5937 | 0.53101 | 97.9935 | 104.6127 | 122.7997 | -122.9874 | -122.7951
3176.9062 | 122.9599 | -98.0301 | 24.5865 | 0.1796 | 0.0064344 | 0.0055906 | 0.0086005 | -0.0011258 | 0.0082523 | 0.0038389 | -97.5815 | 24.4537 | -98.4741 | 24.5865 | 6.8207 | 0.26093 | 24.6918 | -6.1111 | 24.6689 | -98.2956 | -0.44403 | -0.13275 | 0.44861 | 122.6166 | -17.7658 | -0.2655 | 0.082397 | 0.89264 | 122.7219 | 91.9189 | 104.8508 | 122.4838 | 0.44861 | 122.699 | 98.291 | -0.2655 | 122.4838 | 0.44861 | 98.291 | 104.8508 | 122.699 | -123.0606 | -122.8821
3177.9062 | 122.9599 | -106.4438 | 16.1179 | 0.25589 | 0.0023756 | 0.011145 | 0.012659 | -0.0030484 | 0.0056887 | 0.0025571 | -106.1554 | 15.9164 | -107.103 | 16.2323 | 4.6005 | 1.0345 | 16.1133 | -8.3954 | 16.2094 | -106.7734 | -0.65918 | -0.20142 | 0.28839 | 122.6761 | -11.5173 | -0.32959 | 0.091553 | 0.94757 | 122.5571 | 98.0484 | 111.0443 | 122.3602 | 0.28839 | 122.6532 | 107.4783 | -0.32959 | 122.3602 | 0.28839 | 107.4783 | 111.0443 | 122.6532 | -123.2208 | -122.8912
3178.9219 | 122.8317 | -95.6314 | 27.1545 | 0.080414 | 0.00045296 | 0.00089078 | 0.0006965 | -0.0047574 | 0.0093203 | 0.0064023 | -95.8786 | 26.0422 | -96.7758 | 26.4084 | 7.3608 | 0.23804 | 25.6439 | -6.6055 | 26.001 | -96.9223 | -1.1444 | -1.1124 | -0.24719 | 122.0398 | -19.7937 | -1.2909 | -1.1536 | 0.89722 | 121.2753 | 89.0259 | 102.9922 | 121.6736 | -0.24719 | 121.6324 | 95.8694 | -1.2909 | 121.6736 | -0.24719 | 95.8694 | 102.9922 | 121.6324 | -123.9304 | -124.0768
3179.9062 | 122.818 | -98.2178 | 24.3988 | 0.15671 | 0.0047254 | 0.006445 | 0.01095 | -0.0051846 | 0.0086795 | 0.0034115 | -97.9385 | 24.3668 | -98.7808 | 24.2523 | 6.8069 | 0.22888 | 24.4308 | -6.7062 | 24.3576 | -98.6893 | -0.56305 | -0.032044 | 0.27923 | 122.4701 | -17.5919 | -0.4715 | -0.041199 | 0.84229 | 122.6486 | 91.5115 | 105.0247 | 122.5845 | 0.27923 | 122.5754 | 98.4467 | -0.4715 | 122.5845 | 0.27923 | 98.4467 | 105.0247 | 122.5754 | -123.1796 | -123.0881
3180.9062 | 91.7862 | -95.1141 | 25.8728 | 0.439 | 0.0034436 | 0.0015316 | 0.0056097 | -0.003262 | 0.0071841 | 0.0042661 | -92.7521 | 41.5146 | -92.0654 | 26.5457 | 7.2739 | -0.027466 | 27.1271 | -6.4682 | 20.2469 | -95.3476 | 3.0487 | 15.6418 | 2.3621 | 121.6599 | -18.5989 | -0.23346 | -5.6259 | -0.68664 | 122.2412 | 88.6459 | 102.388 | 136.6287 | 2.3621 | 115.361 | 95.0867 | -0.23346 | 136.6287 | 2.3621 | 95.0867 | 102.388 | 115.361 | -117.9382 | -121.2204
3181.9062 | 122.8638 | -108.9386 | 13.7421 | 0.080414 | 0.0045118 | 0.005377 | 0.017359 | 0.00015601 | 0.0048343 | 0.0034115 | -108.609 | 13.6276 | -109.3231 | 13.5681 | 3.7765 | 1.1261 | 13.7375 | -9.3933 | 13.7787 | -109.314 | -0.38452 | -0.11444 | 0.32959 | 122.5067 | -9.9655 | -0.37537 | 0.036622 | 0.71411 | 122.6761 | 99.5453 | 112.7151 | 122.5662 | 0.32959 | 122.7173 | 110.0647 | -0.37537 | 122.5662 | 0.32959 | 110.0647 | 112.7151 | 122.7173 | -123.0652 | -123.056
3182.9062 | 122.85 | -109.7122 | 12.9684 | 0.049896 | 0.0053662 | 0.0055906 | 0.016932 | -0.0017666 | 0.00013454 | 0.0036253 | -109.0988 | 12.886 | -110.1196 | 12.8632 | 3.5934 | 1.1353 | 12.8769 | -9.9106 | 13.028 | -110.1379 | -0.40741 | -0.082398 | 0.6134 | 122.5754 | -9.375 | -0.42572 | 0.059509 | 1.0208 | 122.5891 | 99.8016 | 113.3057 | 122.5983 | 0.6134 | 122.7402 | 110.8475 | -0.42572 | 122.5983 | 0.6134 | 110.8475 | 113.3057 | 122.7402 | -123.0881 | -123.1064
3183.9219 | 122.9553 | -109.3735 | 13.2019 | 0.065155 | 0.00045296 | 0.0032406 | 0.0073187 | -0.0019802 | 0.0020571 | 0.0025571 | -108.9478 | 13.2156 | -109.8358 | 13.3209 | 3.7857 | 1.2039 | 12.973 | -10.0021 | 13.266 | -109.79 | -0.46234 | 0.013733 | 0.42572 | 122.6944 | -9.4162 | -0.41656 | 0.064087 | 0.88806 | 122.3465 | 99.3713 | 113.1592 | 122.5891 | 0.42572 | 122.6395 | 110.5774 | -0.41656 | 122.5891 | 0.42572 | 110.5774 | 113.1592 | 122.6395 | -123.0377 | -122.9919
3184.9062 | 122.8455 | -102.8 | 19.8257 | -0.026398 | 0.0034436 | 0.003668 | 0.013514 | -0.0030484 | 0.0052615 | 0.0044797 | -101.9073 | 20.3201 | -102.8275 | 19.8807 | 5.6442 | 0.54932 | 19.7937 | -7.814 | 19.9631 | -103.1982 | -0.027466 | 0.49438 | 0.89264 | 122.6807 | -14.1815 | -0.39825 | 0.13733 | 0.92011 | 122.5937 | 94.986 | 108.4442 | 123.1201 | 0.89264 | 122.7631 | 103.3493 | -0.39825 | 123.1201 | 0.89264 | 103.3493 | 108.4442 | 122.7631 | -122.6532 | -123.024
3185.9062 | 122.8455 | -94.3359 | 28.3585 | 0.79758 | 0.0023756 | 0.0025998 | 0.0058233 | -0.0034756 | 0.010175 | 0.0036253 | -93.8232 | 28.038 | -94.9951 | 27.9282 | 7.9285 | -0.041199 | 28.5049 | -5.6946 | 28.3493 | -94.6014 | -0.65918 | -0.32043 | 0.5127 | 122.2641 | -20.43 | -0.2655 | -0.009155 | 1.1719 | 122.8409 | 88.6414 | 102.2644 | 122.374 | 0.5127 | 122.6852 | 94.2947 | -0.2655 | 122.374 | 0.5127 | 94.2947 | 102.2644 | 122.6852 | -123.3536 | -122.9599
3186.9062 | 122.8134 | -94.9539 | 27.4429 | 0.17197 | 0.0034436 | 0.0087948 | 0.0060369 | 0.0033602 | 0.010389 | 0.0034115 | -94.5648 | 27.6352 | -95.4529 | 27.6855 | 7.9514 | 0.054932 | 27.4475 | -6.308 | 27.6581 | -95.4575 | -0.49896 | 0.19226 | 0.3891 | 122.6395 | -19.4916 | -0.50354 | 0.21515 | 0.88806 | 122.4014 | 88.6459 | 102.9053 | 122.5891 | 0.3891 | 122.612 | 95.0088 | -0.50354 | 122.5891 | 0.3891 | 95.0088 | 102.9053 | 122.612 | -122.8958 | -122.9004
3187.9062 | 122.9279 | -94.8532 | 27.8046 | 0.18723 | 0.0062208 | 0.006445 | 0.0071051 | -0.0013394 | 0.0088931 | 0.0040525 | -94.4687 | 29.4113 | -94.7159 | 27.6993 | 7.7545 | -0.086975 | 27.8915 | -6.0974 | 27.9419 | -95.1508 | 0.13733 | 1.6068 | 0.38452 | 122.5525 | -20.05 | -0.29755 | 0.13733 | 0.24719 | 122.7448 | 88.7558 | 102.6077 | 124.2645 | 0.38452 | 122.7951 | 94.7662 | -0.29755 | 124.2645 | 0.38452 | 94.7662 | 102.6077 | 122.7951 | -122.5204 | -122.9553
3188.9062 | 122.8592 | -94.693 | 27.9282 | -0.49179 | 0.0038708 | 0.005377 | 0.0053961 | -0.00027139 | 0.0095339 | 0.0053343 | -93.8644 | 28.157 | -94.78 | 27.7908 | 7.7774 | -0.059509 | 27.7496 | -6.1249 | 27.9053 | -95.05 | -0.086975 | 0.22888 | 0.82855 | 122.4838 | -20.1508 | -0.35706 | -0.022889 | 0.91553 | 122.4426 | 88.5681 | 102.4704 | 122.85 | 0.82855 | 122.5983 | 94.6335 | -0.35706 | 122.85 | 0.82855 | 94.6335 | 102.4704 | 122.5983 | -122.7081 | -122.9782
3189.9062 | 122.85 | -106.0547 | 16.6168 | 0.080414 | 0.004939 | 0.011572 | 0.013941 | -0.0011258 | 0.0033389 | 0.0029843 | -105.5466 | 16.4246 | -106.5537 | 16.4291 | 4.6051 | 0.84686 | 16.6489 | -7.8323 | 16.6534 | -106.398 | -0.49896 | -0.19226 | 0.50812 | 122.4838 | -12.0117 | -0.34332 | 0.036621 | 1.0071 | 122.7036 | 98.2224 | 110.6598 | 122.4792 | 0.50812 | 122.7081 | 106.9016 | -0.34332 | 122.4792 | 0.50812 | 106.9016 | 110.6598 | 122.7081 | -123.1705 | -123.0148
3190.9062 | 122.7997 | -94.8441 | 27.8091 | 0.095673 | 0.0030164 | 0.0079404 | 0.0047553 | 0.0010104 | 0.011029 | 0.0031979 | -94.4962 | 27.5574 | -95.343 | 27.626 | 7.8873 | -0.073242 | 27.8549 | -6.2302 | 27.9007 | -95.2286 | -0.49896 | -0.25177 | 0.3479 | 122.4701 | -19.9219 | -0.38452 | 0.091553 | 0.84686 | 122.699 | 88.6139 | 102.7313 | 122.4014 | 0.3479 | 122.7448 | 94.7708 | -0.38452 | 122.4014 | 0.3479 | 94.7708 | 102.7313 | 122.7448 | -123.1522 | -123.0377
3191.9062 | 122.8363 | -112.1063 | 10.5286 | -0.20187 | 0.0045118 | 0.0040952 | 0.018213 | -0.0013394 | 0.00077554 | 0.0023435 | -111.4746 | 10.5881 | -112.4405 | 10.3683 | 2.9297 | 0.58594 | 10.3729 | -10.4828 | 10.5789 | -112.5366 | -0.33417 | 0.05951 | 0.63171 | 122.4747 | -7.5989 | -0.4303 | 0.050354 | 0.96588 | 122.4792 | 101.6235 | 115.036 | 122.6944 | 0.63171 | 122.6852 | 112.6923 | -0.4303 | 122.6944 | 0.63171 | 112.6923 | 115.036 | 122.6852 | -122.9691 | -123.0652
3192.9062 | 122.8134 | -108.577 | 14.1357 | 0.019379 | 0.0053662 | 0.003027 | 0.014795 | 0.001224 | 0.0037661 | 0.0057615 | -107.9453 | 14.1495 | -108.8974 | 13.9847 | 4.0054 | 1.062 | 13.9984 | -9.343 | 14.1724 | -108.934 | -0.32044 | 0.013733 | 0.63171 | 122.5616 | -10.1303 | -0.35706 | 0.036621 | 0.95215 | 122.5754 | 99.234 | 112.5824 | 122.7264 | 0.63171 | 122.7493 | 109.639 | -0.35706 | 122.7264 | 0.63171 | 109.639 | 112.5824 | 122.7493 | -123.0331 | -123.0698
3193.9062 | 122.937 | -105.1071 | 17.514 | 0.22537 | 0.0070752 | 0.0025998 | 0.0096685 | -0.00048499 | 0.0050479 | 0.0044797 | -104.5486 | 17.6102 | -105.1666 | 17.7704 | 5.1315 | 0.83771 | 17.3492 | -7.6538 | 17.6788 | -105.3818 | -0.059509 | 0.09613 | 0.55847 | 122.8775 | -12.3825 | -0.27466 | 0.1648 | 0.61798 | 122.4564 | 97.4533 | 110.2386 | 122.7173 | 0.55847 | 122.7859 | 105.9448 | -0.27466 | 122.7173 | 0.55847 | 105.9448 | 110.2386 | 122.7859 | -122.6807 | -122.8958
3194.9062 | 122.8271 | -107.1304 | 15.4861 | 0.027008 | 0.0042982 | 0.0034544 | 0.014155 | -0.0017666 | 0.0039797 | 0.0044797 | -106.6818 | 15.4449 | -107.5516 | 15.1474 | 4.3396 | 0.79651 | 15.3351 | -8.5831 | 15.3534 | -107.5836 | -0.42114 | -0.041199 | 0.44861 | 122.2778 | -11.1465 | -0.45319 | -0.13275 | 0.86975 | 122.4655 | 98.5474 | 111.47 | 122.5754 | 0.44861 | 122.4838 | 107.9269 | -0.45319 | 122.5754 | 0.44861 | 107.9269 | 111.47 | 122.4838 | -123.0377 | -123.0698
3195.9062 | 122.8821 | -110.9985 | 11.6547 | -0.11795 | 0.0042982 | 0.001959 | 0.017145 | -0.0013394 | 0.0026981 | 0.0038389 | -110.3897 | 11.6592 | -111.3876 | 12.0529 | 3.4149 | 1.2085 | 11.5906 | -9.7916 | 11.8332 | -111.4197 | -0.3891 | 0.004578 | 0.60883 | 123.0515 | -8.2397 | -0.42114 | 0.17853 | 0.99793 | 122.5891 | 101.207 | 114.4135 | 122.6578 | 0.60883 | 122.8317 | 112.207 | -0.42114 | 122.6578 | 0.60883 | 112.207 | 114.4135 | 122.8317 | -123.0423 | -123.0743
3196.9062 | 122.8821 | -107.9636 | 14.6805 | -0.011139 | 0.0042982 | 0.0038816 | 0.017786 | -0.0013394 | 0.0026981 | 0.0031979 | -107.6981 | 14.3829 | -108.6639 | 14.3829 | 4.2252 | 0.88806 | 14.6942 | -8.4641 | 14.7217 | -108.3847 | -0.70038 | -0.29755 | 0.2655 | 122.3465 | -10.4553 | -0.42114 | 0.041199 | 0.96588 | 122.6578 | 99.4995 | 112.1887 | 122.3465 | 0.2655 | 122.6852 | 108.8516 | -0.42114 | 122.3465 | 0.2655 | 108.8516 | 112.1887 | 122.6852 | -123.3444 | -123.0652
3197.9062 | 122.8317 | -110.2295 | 12.2589 | 0.080414 | 0.0053662 | 0.0070858 | 0.017145 | 0.00036961 | 0.0037661 | 0.0023435 | -109.2361 | 13.4903 | -110.0098 | 12.6022 | 3.6438 | 0.9613 | 12.5656 | -9.6359 | 12.6709 | -110.3668 | 0.21973 | 1.2314 | 0.99335 | 122.8317 | -8.6151 | -0.13733 | 0.41199 | 0.77362 | 122.7951 | 100.5936 | 113.8733 | 123.7198 | 0.99335 | 122.9004 | 111.1908 | -0.13733 | 123.7198 | 0.99335 | 111.1908 | 113.8733 | 122.9004 | -122.2687 | -122.6257
3198.9062 | 123.056 | -91.6763 | 31.0822 | -0.0035098 | 0.0040846 | 0.0043088 | 0.0039007 | 0.00036961 | 0.0084659 | 0.0049069 | -93.8187 | 28.3676 | -94.8898 | 28.5049 | 8.551 | -0.20142 | 29.0634 | -5.6534 | 29.2145 | -93.718 | -3.2135 | -2.7145 | -2.1423 | 120.1813 | -22.5311 | -2.0416 | -1.8677 | 1.0712 | 120.7397 | 86.023 | 100.2274 | 120.0439 | -2.1423 | 120.8908 | 91.4749 | -2.0416 | 120.0439 | -2.1423 | 91.4749 | 100.2274 | 120.8908 | -125.972 | -124.8001
3199.9062 | 122.8455 | -94.8807 | 27.4292 | 0.027008 | 0.004939 | 0.0049496 | 0.0051825 | -0.00027139 | 0.0071841 | 0.0038389 | -94.0933 | 28.1113 | -94.9997 | 27.7634 | 7.9285 | -0.045776 | 27.7222 | -5.7175 | 27.7954 | -95.2332 | -0.11902 | 0.68207 | 0.78735 | 122.644 | -19.5007 | -0.35248 | 0.36621 | 0.90637 | 122.6028 | 89.1632 | 102.8091 | 122.9919 | 0.78735 | 122.6761 | 94.8349 | -0.35248 | 122.9919 | 0.78735 | 94.8349 | 102.8091 | 122.6761 | -122.4289 | -122.6624
3200.9062 | 122.8638 | -106.5857 | 15.9714 | 0.027008 | 0.0040846 | 0.0045224 | 0.015009 | -0.00091219 | 0.0056887 | 0.0044797 | -105.9494 | 16.1224 | -106.9336 | 15.9988 | 4.6463 | 0.98877 | 15.889 | -8.6563 | 16.1453 | -107.0023 | -0.3479 | 0.15106 | 0.63629 | 122.5845 | -11.3251 | -0.41656 | 0.17395 | 0.98419 | 122.4747 | 97.9294 | 111.232 | 122.7081 | 0.63629 | 122.731 | 107.5745 | -0.41656 | 122.7081 | 0.63629 | 107.5745 | 111.232 | 122.731 | -122.905 | -122.9736
3201.9062 | 122.9004 | -94.2581 | 27.8046 | 0.019379 | 0.0051526 | 0.0062314 | 0.0045417 | -0.00027139 | 0.0095339 | 0.0021299 | -94.0613 | 28.1662 | -94.8395 | 28.244 | 8.2626 | 0.027466 | 28.2303 | -5.6763 | 28.3997 | -94.7067 | -0.58136 | 0.36163 | 0.19684 | 122.5021 | -19.5419 | -0.44861 | 0.59509 | 0.7782 | 122.4884 | 88.5818 | 102.5208 | 122.4243 | 0.19684 | 122.6578 | 94.2856 | -0.44861 | 122.4243 | 0.19684 | 94.2856 | 102.5208 | 122.6578 | -122.644 | -122.5113
3202.9062 | 122.9736 | -94.1986 | 28.3173 | -0.19424 | 0.00323 | 0.0075132 | 0.0045417 | -0.0028348 | 0.010389 | 0.0031979 | -93.3792 | 28.4912 | -94.3771 | 27.9465 | 8.1619 | -0.013733 | 28.3539 | -5.7358 | 28.3997 | -94.7159 | -0.17853 | 0.17395 | 0.8194 | 122.1451 | -20.1553 | -0.51727 | 0.082397 | 0.99792 | 122.5525 | 88.4628 | 102.3605 | 122.6898 | 0.8194 | 122.5983 | 94.1849 | -0.51727 | 122.6898 | 0.8194 | 94.1849 | 102.3605 | 122.5983 | -122.6944 | -123.0331
3203.9062 | 122.8638 | -105.368 | 17.2302 | 0.13382 | 0.0047254 | 0.0028134 | 0.0098823 | -0.001553 | 0.0046207 | 0.0044797 | -104.7363 | 17.5049 | -105.7388 | 17.0334 | 4.9484 | 0.91095 | 17.0197 | -7.5623 | 17.1707 | -105.8533 | -0.37079 | 0.27466 | 0.63171 | 122.4014 | -12.2818 | -0.48523 | -0.05951 | 1.0025 | 122.3877 | 97.8058 | 110.3165 | 122.8729 | 0.63171 | 122.5388 | 106.279 | -0.48523 | 122.8729 | 0.63171 | 106.279 | 110.3165 | 122.5388 | -122.9691 | -123.0835
3204.9062 | 122.8775 | -94.075 | 27.9602 | -0.041657 | 0.0036572 | 0.0075132 | 0.0062507 | -0.0017666 | 0.0082523 | 0.0038389 | -93.6951 | 28.363 | -94.6518 | 28.5965 | 8.2214 | -0.09613 | 28.6469 | -5.5984 | 28.7476 | -94.4366 | -0.57678 | 0.40283 | 0.37994 | 122.6715 | -19.7388 | -0.36163 | 0.78735 | 0.95673 | 122.7219 | 88.4766 | 102.2964 | 122.438 | 0.37994 | 122.8226 | 93.9789 | -0.36163 | 122.438 | 0.37994 | 93.9789 | 102.2964 | 122.8226 | -122.612 | -122.3969
3205.9062 | 122.8729 | -95.3979 | 27.2964 | -0.034027 | 0.0017346 | 0.0051632 | 0.0045417 | -0.00048499 | 0.0088931 | 0.0027707 | -94.5328 | 27.4017 | -95.5719 | 27.388 | 7.7454 | 0.082397 | 27.0218 | -5.9967 | 27.2781 | -95.8374 | -0.17395 | 0.10528 | 0.86517 | 122.7859 | -19.5511 | -0.43945 | -0.018311 | 1.0391 | 122.4197 | 89.4012 | 103.1433 | 122.7997 | 0.86517 | 122.6761 | 95.4803 | -0.43945 | 122.7997 | 0.86517 | 95.4803 | 103.1433 | 122.6761 | -122.8683 | -123.1338
3206.9062 | 122.8546 | -94.3497 | 28.4042 | -0.026398 | 0.0038708 | 0.0066586 | 0.0056097 | 0.0010104 | 0.0088931 | 0.0014889 | -93.782 | 28.3127 | -94.7388 | 28.4912 | 8.1345 | 0.036621 | 28.1067 | -5.9692 | 28.3035 | -94.8624 | -0.3891 | -0.091553 | 0.56763 | 122.8409 | -20.2698 | -0.5127 | -0.10071 | 0.95673 | 122.4564 | 88.3804 | 102.4841 | 122.6624 | 0.56763 | 122.6532 | 94.3863 | -0.5127 | 122.6624 | 0.56763 | 94.3863 | 102.4841 | 122.6532 | -123.143 | -123.2666
3207.9062 | 122.8363 | -94.1437 | 28.4821 | -0.079803 | 0.0051526 | 0.005377 | 0.0034735 | -0.0013394 | 0.0097475 | 0.0061887 | -93.7958 | 28.5828 | -94.6289 | 28.6835 | 8.1619 | 0 | 28.1525 | -6.1295 | 28.4409 | -94.6793 | -0.48523 | 0.10071 | 0.3479 | 122.8271 | -20.3201 | -0.53558 | -0.041199 | 0.83313 | 122.2961 | 88.0142 | 102.3056 | 122.7264 | 0.3479 | 122.5845 | 94.1437 | -0.53558 | 122.7264 | 0.3479 | 94.1437 | 102.3056 | 122.5845 | -123.111 | -123.1613
3208.9062 | 122.8455 | -93.5028 | 29.0451 | 0.027008 | 0.0055798 | 0.0068722 | 0.0066779 | -0.00091219 | 0.010175 | 0.0025571 | -92.7521 | 29.3243 | -93.6218 | 29.4342 | 8.3221 | -0.24719 | 30.043 | -5.0262 | 29.805 | -93.5623 | -0.11902 | 0.27924 | 0.75073 | 122.937 | -20.723 | -0.059509 | 0.75989 | 0.86975 | 123.5458 | 88.4766 | 101.825 | 122.8271 | 0.75073 | 123.3078 | 93.2556 | -0.059509 | 122.8271 | 0.75073 | 93.2556 | 101.825 | 123.3078 | -122.6669 | -122.6074
3209.9062 | 122.8729 | -94.2856 | 28.2715 | -0.18662 | 0.0036572 | 0.0068722 | 0.0039007 | -0.0024076 | 0.010175 | 0.0042661 | -93.4296 | 28.9719 | -91.0538 | 28.2028 | 8.0063 | -0.022888 | 28.212 | -5.8044 | 28.3585 | -94.5923 | 3.2318 | 0.70038 | 0.85602 | 122.4884 | -20.2652 | -0.3067 | 0.086975 | -2.3758 | 122.4976 | 88.4811 | 102.2919 | 123.2574 | 0.85602 | 122.644 | 94.2627 | -0.3067 | 123.2574 | 0.85602 | 94.2627 | 102.2919 | 122.644 | -119.3253 | -122.8638
3210.9219 | 122.9141 | -94.194 | 28.5324 | 0.16434 | 0.0034436 | 0.0060178 | 0.0039007 | -0.0013394 | 0.010175 | 0.0040525 | -93.338 | 28.6514 | -94.3451 | 28.7018 | 8.0566 | -0.041199 | 28.3539 | -5.2963 | 28.5507 | -94.5145 | -0.15106 | 0.11902 | 0.85602 | 122.8958 | -20.4758 | -0.32043 | 0.01831 | 1.0071 | 122.5479 | 88.8977 | 102.2507 | 122.8455 | 0.85602 | 122.7448 | 94.1528 | -0.32043 | 122.8455 | 0.85602 | 94.1528 | 102.2507 | 122.7448 | -122.8775 | -123.0469
3211.9062 | 122.8226 | -91.3651 | 30.4413 | -0.049286 | 0.0053662 | 0.0058042 | 0.0049689 | -0.0011258 | 0.0091067 | 0.0040525 | -94.1666 | 27.9465 | -95.1233 | 27.8732 | 7.9788 | -0.93842 | 53.2333 | -1.8402 | 35.7422 | -88.266 | -3.7582 | -2.4948 | -2.8015 | 119.2383 | -22.4625 | 3.0991 | 5.3009 | 0.95673 | 144.5984 | 89.5248 | 99.3439 | 119.3115 | -2.8015 | 127.1072 | 90.4266 | 3.0991 | 119.3115 | -2.8015 | 90.4266 | 99.3439 | 127.1072 | -125.5646 | -118.7073
3212.9062 | 122.9095 | -94.2627 | 28.4317 | -0.14847 | 0.0019482 | 0.0032406 | 0.0058233 | -5.7592e-05 | 0.0082523 | 0.0040525 | -93.8278 | 28.1525 | -94.8349 | 28.6469 | 8.0704 | -0.032043 | 28.0975 | -5.4382 | 28.299 | -94.7342 | -0.57221 | -0.27924 | 0.43487 | 122.9095 | -20.3613 | -0.4715 | -0.13275 | 1.0071 | 122.3602 | 88.8245 | 102.3331 | 122.4152 | 0.43487 | 122.5616 | 94.2307 | -0.4715 | 122.4152 | 0.43487 | 94.2307 | 102.3331 | 122.5616 | -123.2666 | -123.1659
3213.9062 | 122.8683 | -94.1071 | 28.624 | -0.30869 | 0.0053662 | 0.010717 | 0.0043281 | -0.0024076 | 0.010389 | 0.0038389 | -93.3746 | 28.7155 | -94.2719 | 28.6148 | 8.1116 | -0.07782 | 28.7247 | -5.3375 | 28.743 | -94.4092 | -0.16479 | 0.091553 | 0.73242 | 122.7219 | -20.5124 | -0.30212 | 0.11902 | 0.89722 | 122.8317 | 88.7695 | 102.2186 | 122.8226 | 0.73242 | 122.85 | 94.0292 | -0.30212 | 122.8226 | 0.73242 | 94.0292 | 102.2186 | 122.85 | -122.8958 | -123.0331
3214.9062 | 122.8638 | -94.6243 | 28.0792 | -0.19424 | 0.0030164 | 0.0060178 | 0.0051825 | -0.00048499 | 0.010602 | 0.0046933 | -94.0018 | 28.1616 | -94.9402 | 28.0106 | 8.0017 | 0 | 27.8961 | -4.8614 | 28.038 | -95.0226 | -0.31586 | 0.082397 | 0.62256 | 122.6349 | -20.0775 | -0.39825 | -0.041199 | 0.93842 | 122.5204 | 89.7629 | 102.626 | 122.7859 | 0.62256 | 122.6624 | 94.6243 | -0.39825 | 122.7859 | 0.62256 | 94.6243 | 102.626 | 122.6624 | -123.0194 | -123.1018
3215.9062 | 122.8683 | -94.3726 | 28.2715 | 0.14908 | 0.0047254 | 0.0049496 | 0.0066779 | -0.00048499 | 0.0082523 | 0.0066159 | -94.0018 | 28.1433 | -94.9402 | 27.9694 | 7.8781 | -0.045776 | 28.3676 | -5.4291 | 28.331 | -94.7388 | -0.56763 | -0.12817 | 0.37079 | 122.3419 | -20.3934 | -0.36621 | 0.05951 | 0.93842 | 122.7402 | 88.9435 | 102.2507 | 122.5159 | 0.37079 | 122.7036 | 94.3268 | -0.36621 | 122.5159 | 0.37079 | 94.3268 | 102.2507 | 122.7036 | -123.2117 | -123.0103
3216.9062 | 122.8043 | -93.7408 | 28.8574 | 1.0875 | 0.0045118 | 0.0028134 | 0.0017645 | -0.0047574 | 0.010816 | 0.0036253 | -93.4341 | 28.6148 | -94.3771 | 29.0039 | 8.3862 | -0.1236 | 29.0268 | -5.896 | 29.155 | -94.1208 | -0.63629 | -0.24262 | 0.3067 | 122.7448 | -20.4712 | -0.37994 | 0.29755 | 0.94299 | 122.7676 | 87.8448 | 102.1271 | 122.3557 | 0.3067 | 122.8958 | 93.6172 | -0.37994 | 122.3557 | 0.3067 | 93.6172 | 102.1271 | 122.8958 | -123.2346 | -122.9782
3217.9062 | 122.9095 | -107.9041 | 14.7354 | -0.12558 | 0.0036572 | 0.0079404 | 0.012873 | -0.002194 | 0.0039797 | 0.0010617 | -107.2449 | 14.6942 | -108.2932 | 14.6988 | 4.2847 | 1.0757 | 14.6118 | -8.2306 | 14.8132 | -108.3572 | -0.3891 | -0.041199 | 0.65918 | 122.6028 | -10.4507 | -0.45319 | 0.077819 | 1.0483 | 122.5159 | 99.6735 | 112.1887 | 122.5983 | 0.65918 | 122.7173 | 108.9798 | -0.45319 | 122.5983 | 0.65918 | 108.9798 | 112.1887 | 122.7173 | -123.0286 | -123.0927
3218.9062 | 122.8867 | -109.8129 | 12.7808 | -0.10269 | 0.0036572 | 0.0043088 | 0.014795 | -0.0019802 | 0.0026981 | 0.0031979 | -109.2728 | 12.7533 | -110.3073 | 12.5336 | 3.6575 | -0.022888 | 12.5748 | -8.4 | 12.7762 | -110.2798 | -0.49438 | -0.027466 | 0.54016 | 122.3465 | -9.1232 | -0.46692 | -0.004578 | 1.0345 | 122.3877 | 101.413 | 113.4705 | 122.5662 | 0.54016 | 122.5891 | 109.79 | -0.46692 | 122.5662 | 0.54016 | 109.79 | 113.4705 | 122.5891 | -123.0881 | -123.0606
3219.9062 | 122.8775 | -99.5682 | 23.0988 | -0.18662 | 0.0038708 | 0.0043088 | 0.0081733 | -0.0013394 | 0.0061161 | 0.0019163 | -98.9594 | 23.053 | -99.9985 | 23.0347 | 6.6055 | 0.39368 | 23.0667 | -6.514 | 23.1491 | -99.9069 | -0.4303 | -0.045776 | 0.60882 | 122.6028 | -16.4932 | -0.33875 | 0.050354 | 1.0391 | 122.6349 | 93.0542 | 106.1737 | 122.6212 | 0.60882 | 122.7173 | 99.9619 | -0.33875 | 122.6212 | 0.60882 | 99.9619 | 106.1737 | 122.7173 | -123.0972 | -123.0057
3220.9219 | 122.9828 | -103.8437 | 18.6218 | 0.24063 | 0.0040846 | 0.0049496 | 0.0077459 | -0.0013394 | 0.0069705 | 0.0040525 | -103.5461 | 18.3884 | -104.5807 | 18.2877 | 5.3421 | 0.86517 | 18.0954 | -7.4799 | 18.3929 | -104.6814 | -0.737 | -0.23346 | 0.29755 | 122.1313 | -13.2797 | -0.83771 | -0.22888 | 1.0345 | 121.9391 | 96.3638 | 109.1858 | 122.2321 | 0.29755 | 122.2366 | 104.7089 | -0.83771 | 122.2321 | 0.29755 | 104.7089 | 109.1858 | 122.2366 | -123.2025 | -123.3032
3221.9062 | 122.8958 | -110.0555 | 12.5702 | -0.24002 | 0.0030164 | 0.0070858 | 0.013514 | -0.0019802 | 0.0046207 | 0.0040525 | -108.934 | 12.7899 | -109.9915 | 12.5381 | 3.6575 | 1.2497 | 12.5748 | -8.6838 | 12.7213 | -110.463 | 0.064087 | 0.21973 | 1.1215 | 122.5937 | -8.9127 | -0.40741 | 0.15106 | 1.0574 | 122.6303 | 101.3718 | 113.7131 | 122.8455 | 1.1215 | 122.7768 | 111.3052 | -0.40741 | 122.8455 | 1.1215 | 111.3052 | 113.7131 | 122.7768 | -122.5616 | -123.0331
3222.9062 | 122.8729 | -103.6102 | 19.0567 | -0.27054 | 0.0010938 | 0.006445 | 0.0090277 | -0.0019802 | 0.0059023 | 0.0051205 | -103.3127 | 18.6859 | -104.1367 | 18.8187 | 5.4108 | 0.7782 | 20.8099 | -6.4362 | 19.4824 | -103.7567 | -0.52643 | -0.37079 | 0.29755 | 122.4289 | -13.6459 | -0.14648 | 0.42572 | 0.82397 | 124.4202 | 97.1741 | 109.021 | 122.2961 | 0.29755 | 123.0927 | 104.3884 | -0.14648 | 122.2961 | 0.29755 | 104.3884 | 109.021 | 123.0927 | -123.1934 | -122.8134
3223.9062 | 122.8134 | -107.9086 | 14.7537 | 0.11856 | 0.0045118 | 0.009863 | 0.014582 | -0.002194 | 0.0061161 | 0.0040525 | -107.1396 | 14.8453 | -108.1741 | 14.6576 | 4.2389 | 1.0162 | 14.7034 | -8.4366 | 14.8636 | -108.284 | -0.2655 | 0.091553 | 0.76904 | 122.5662 | -10.5148 | -0.37537 | 0.10986 | 1.0345 | 122.612 | 99.472 | 112.1475 | 122.7539 | 0.76904 | 122.7722 | 108.9249 | -0.37537 | 122.7539 | 0.76904 | 108.9249 | 112.1475 | 122.7722 | -122.9279 | -123.0377
3224.9062 | 122.9233 | -94.5145 | 28.1433 | -0.14847 | 0.0030164 | 0.0062314 | 0.0041143 | -0.0017666 | 0.0093203 | 0.0044797 | -93.1091 | 28.7247 | -94.1437 | 28.8483 | 8.3588 | 0 | 28.1479 | -5.484 | 28.4637 | -94.8349 | 0.37079 | 0.58136 | 1.4053 | 123.3627 | -19.7845 | -0.32044 | 0.32043 | 1.0345 | 122.6624 | 89.0305 | 102.8732 | 123.2391 | 1.4053 | 122.9782 | 94.5145 | -0.32044 | 123.2391 | 1.4053 | 94.5145 | 102.8732 | 122.9782 | -122.287 | -122.9782
3225.9062 | 122.9279 | -103.3997 | 19.1574 | 0.27115 | 0.0025892 | 0.0079404 | 0.0051825 | 0.003574 | 0.0067569 | 0.0040525 | -102.8366 | 19.1986 | -103.7979 | 19.5877 | 5.8273 | 0.82855 | 18.8828 | -6.6605 | 19.2444 | -103.7979 | -0.39825 | 0.041198 | 0.56305 | 122.9874 | -13.3301 | -0.39825 | 0.086975 | 0.9613 | 122.2824 | 96.7392 | 109.227 | 122.5983 | 0.56305 | 122.644 | 104.2282 | -0.39825 | 122.5983 | 0.56305 | 104.2282 | 109.227 | 122.644 | -122.9553 | -122.9553
3226.9062 | 122.8958 | -106.4255 | 16.1865 | -0.26291 | 0.0042982 | 0.0043088 | 0.012659 | -0.0026212 | 0.0031253 | 0.0017027 | -106.1142 | 16.0309 | -107.0801 | 16.1728 | 4.6646 | 0.96588 | 16.0995 | -7.3837 | 16.2506 | -106.8832 | -0.6546 | -0.15564 | 0.31128 | 122.5983 | -11.5219 | -0.45776 | 0.064087 | 0.96588 | 122.525 | 99.0417 | 111.0901 | 122.4564 | 0.31128 | 122.6761 | 107.3914 | -0.45776 | 122.4564 | 0.31128 | 107.3914 | 111.0901 | 122.6761 | -123.2666 | -123.0698
3227.9062 | 122.8958 | -93.5211 | 29.1138 | -0.14847 | 0.0038708 | 0.0094358 | 0.0034735 | -0.0036892 | 0.0093203 | 0.0029843 | -92.6834 | 29.3243 | -93.718 | 29.1183 | 8.3954 | -0.10986 | 29.4022 | -4.9393 | 29.3976 | -93.6584 | -0.19684 | 0.21057 | 0.83771 | 122.6395 | -20.7184 | -0.13733 | 0.28381 | 1.0345 | 122.9233 | 88.5818 | 101.9165 | 122.8455 | 0.83771 | 122.9187 | 93.4113 | -0.13733 | 122.8455 | 0.83771 | 93.4113 | 101.9165 | 122.9187 | -122.8317 | -122.7722
3228.9062 | 122.8455 | -108.2977 | 14.3784 | -0.25528 | 0.0038708 | 0.0055906 | 0.013514 | -0.0030484 | 0.0018435 | 0.0017027 | -107.6431 | 14.4012 | -108.6914 | 14.3234 | 4.2435 | 1.1307 | 14.328 | -8.5144 | 14.4104 | -108.7418 | -0.39368 | 0.022888 | 0.6546 | 122.6212 | -10.1349 | -0.44403 | 0.032043 | 1.0483 | 122.6257 | 99.7833 | 112.5412 | 122.699 | 0.6546 | 122.7081 | 109.4284 | -0.44403 | 122.699 | 0.6546 | 109.4284 | 112.5412 | 122.7081 | -123.0698 | -123.1201
3229.9062 | 122.8729 | -104.6677 | 17.9398 | -0.064545 | 0.0023756 | 0.0083676 | 0.013727 | -0.00069859 | 0.0029117 | 0.0025571 | -104.1504 | 17.8894 | -105.1529 | 17.6743 | 5.2551 | 0.87891 | 17.7109 | -7.6996 | 17.8207 | -105.2032 | -0.48523 | -0.050354 | 0.51727 | 122.3419 | -12.6846 | -0.53558 | -0.11902 | 1.0025 | 122.3785 | 96.9681 | 109.9228 | 122.5571 | 0.51727 | 122.4884 | 105.5466 | -0.53558 | 122.5571 | 0.51727 | 105.5466 | 109.9228 | 122.4884 | -123.0927 | -123.143
3230.9062 | 122.85 | -108.5861 | 14.0762 | -0.70541 | 0.0010938 | 0.0066586 | 0.013514 | -0.0013394 | 0.0026981 | 0.0044797 | -107.7026 | 14.3234 | -108.7006 | 14.1495 | 4.2389 | 1.1078 | 14.415 | -8.6563 | 14.3921 | -108.8791 | -0.11444 | 0.24719 | 0.88348 | 122.7356 | -9.8373 | -0.29297 | 0.31586 | 0.99793 | 123.0011 | 99.9298 | 112.825 | 122.9095 | 0.88348 | 122.9782 | 109.6939 | -0.29297 | 122.9095 | 0.88348 | 109.6939 | 112.825 | 122.9782 | -122.7768 | -122.9553
3231.9062 | 122.85 | -108.2932 | 14.2639 | -0.12558 | 0.004939 | 0.012426 | 0.015009 | -0.0026212 | 0.0031253 | 0.0044797 | -107.4554 | 14.3143 | -108.6044 | 14.2319 | 4.2664 | 1.1856 | 14.0945 | -8.3908 | 14.3097 | -108.8242 | -0.31128 | 0.050354 | 0.83771 | 122.525 | -9.9976 | -0.53101 | 0.045776 | 1.149 | 122.3877 | 99.9023 | 112.5595 | 122.6074 | 0.83771 | 122.6028 | 109.4788 | -0.53101 | 122.6074 | 0.83771 | 109.4788 | 112.5595 | 122.6028 | -122.8683 | -123.0881
3232.9062 | 122.905 | -108.5129 | 14.1129 | -0.26291 | 0.0034436 | 0.0068722 | 0.014155 | -0.0013394 | 0.0041933 | 0.0059751 | -107.7621 | 14.1724 | -108.4488 | 14.6988 | 4.2801 | 1.1902 | 14.0442 | -8.2169 | 14.3875 | -108.8242 | 0.064086 | 0.059509 | 0.75073 | 123.2117 | -9.8328 | -0.31128 | 0.27466 | 0.68665 | 122.5571 | 100.296 | 112.793 | 122.6852 | 0.75073 | 122.9004 | 109.7031 | -0.31128 | 122.6852 | 0.75073 | 109.7031 | 112.793 | 122.9004 | -122.5616 | -122.937
3233.9062 | 122.8729 | -116.3406 | 6.3995 | 0.27115 | 0.0042982 | 0.0077268 | 0.018641 | -0.00091219 | 0.0033389 | 0.0038389 | -115.6036 | 6.3492 | -116.7343 | 6.2073 | 1.8173 | 1.387 | 6.2119 | -9.6771 | 6.4407 | -116.716 | -0.39368 | -0.050354 | 0.737 | 122.5479 | -4.5822 | -0.37537 | 0.041199 | 1.1307 | 122.5525 | 106.6635 | 118.158 | 122.6898 | 0.737 | 122.7814 | 117.7277 | -0.37537 | 122.6898 | 0.737 | 117.7277 | 118.158 | 122.7814 | -123.1338 | -123.1155
3234.9062 | 122.9004 | -98.1171 | 24.1837 | -0.16373 | 0.0034436 | 0.0077268 | 0.0056097 | -0.0013394 | 0.0063297 | 0.0036253 | -97.5861 | 24.5361 | -98.5519 | 24.1837 | 7.1777 | 0.3479 | 24.0738 | -5.6625 | 24.2203 | -98.6984 | -0.43488 | 0.35248 | 0.531 | 122.3007 | -17.0059 | -0.58136 | 0.036621 | 0.96588 | 122.1909 | 92.4545 | 105.2948 | 122.6532 | 0.531 | 122.3373 | 98.465 | -0.58136 | 122.6532 | 0.531 | 98.465 | 105.2948 | 122.3373 | -122.7356 | -122.8821
3235.9062 | 122.8912 | -105.9265 | 16.3971 | -0.11795 | 0.00323 | 0.0062314 | 0.012018 | -0.001553 | 0.0063297 | 0.0021299 | -105.3955 | 16.6901 | -106.4209 | 16.5482 | 5.0354 | 0.98419 | 16.8091 | -7.3425 | 16.832 | -106.2653 | -0.49438 | 0.29297 | 0.53101 | 122.4747 | -11.3617 | -0.33875 | 0.43487 | 1.0254 | 122.7356 | 98.584 | 110.9619 | 122.6166 | 0.53101 | 122.7585 | 106.9107 | -0.33875 | 122.6166 | 0.53101 | 106.9107 | 110.9619 | 122.7585 | -122.818 | -122.6624
3236.9062 | 122.8088 | -101.2161 | 21.3409 | -0.19424 | 0.0030164 | 0.00089078 | 0.0064643 | -0.0047574 | 0.0067569 | 0.0031979 | -100.1907 | 21.7026 | -101.3809 | 21.2082 | 6.3171 | 0.54016 | 21.4554 | -6.0425 | 21.4188 | -101.6922 | -0.16479 | 0.36163 | 1.0254 | 122.4243 | -15.0238 | -0.47607 | 0.07782 | 1.1902 | 122.6715 | 95.1736 | 107.5333 | 122.9187 | 1.0254 | 122.6349 | 101.7563 | -0.47607 | 122.9187 | 1.0254 | 101.7563 | 107.5333 | 122.6349 | -122.7219 | -123.0331
3237.9062 | 122.8775 | -106.2195 | 16.4749 | -0.22476 | 0.0034436 | 0.0034544 | 0.010523 | -0.00091219 | 0.0052615 | 0.0034115 | -105.5695 | 16.2735 | -106.6956 | 16.4291 | 4.953 | 1.0071 | 16.5298 | -6.6193 | 16.626 | -106.5262 | -0.47607 | -0.20142 | 0.65002 | 122.6486 | -11.5219 | -0.3067 | 0.15106 | 1.1261 | 122.7493 | 99.6002 | 111.1725 | 122.493 | 0.65002 | 122.8455 | 107.2266 | -0.3067 | 122.493 | 0.65002 | 107.2266 | 111.1725 | 122.8455 | -123.1705 | -123.0011
3238.9062 | 122.7631 | -102.9465 | 19.6976 | 0.065155 | 0.0062208 | 0.001959 | 0.0098823 | 0.0014376 | 0.0059023 | 0.0027707 | -102.3514 | 19.6426 | -103.4683 | 19.487 | 5.7449 | 0.71411 | 19.3039 | -6.9168 | 19.5374 | -103.5553 | -0.52185 | -0.054932 | 0.59509 | 122.4335 | -13.9526 | -0.60883 | -0.16022 | 1.1169 | 122.2504 | 96.0297 | 108.6914 | 122.5891 | 0.59509 | 122.4838 | 103.6606 | -0.60883 | 122.5891 | 0.59509 | 103.6606 | 108.6914 | 122.4838 | -123.1659 | -123.2529
3239.9062 | 122.8043 | -104.1367 | 18.4616 | -0.11032 | 0.0062208 | 0.0083676 | 0.012232 | -0.0013394 | 0.0052615 | 0.0036253 | -103.4225 | 18.4662 | -104.567 | 18.5303 | 5.5435 | 0.87433 | 18.3563 | -7.5394 | 18.5349 | -104.631 | -0.4303 | 0.004578 | 0.71411 | 122.6669 | -12.9181 | -0.49438 | 0.073242 | 1.1444 | 122.493 | 96.5973 | 109.6802 | 122.6028 | 0.71411 | 122.6715 | 105.011 | -0.49438 | 122.6028 | 0.71411 | 105.011 | 109.6802 | 122.6715 | -123.0286 | -123.0927
3240.9062 | 122.8958 | -104.8233 | 17.7704 | -0.056915 | 0.0055798 | 0.0062314 | 0.0133 | 0.00015601 | 0.0048343 | 0.0029843 | -104.1412 | 17.7567 | -105.2078 | 17.807 | 5.3421 | 0.88348 | 17.6514 | -7.1136 | 17.8391 | -105.3085 | -0.38452 | -0.013733 | 0.68207 | 122.6303 | -12.4283 | -0.48523 | 0.068664 | 1.0666 | 122.4747 | 97.7097 | 110.1654 | 122.58 | 0.68207 | 122.6624 | 105.7068 | -0.48523 | 122.58 | 0.68207 | 105.7068 | 110.1654 | 122.6624 | -122.9782 | -123.0789
3241.9062 | 122.9553 | -104.718 | 17.9123 | -0.079803 | 0.0057934 | 0.003668 | 0.012873 | -0.0026212 | 0.0052615 | 0.0055479 | -104.1092 | 17.7612 | -105.2124 | 18.1091 | 5.3833 | 0.94299 | 17.7887 | -6.5414 | 18.0496 | -105.1209 | -0.49438 | -0.15106 | 0.60883 | 122.8271 | -12.529 | -0.40283 | 0.13733 | 1.1032 | 122.5067 | 98.1766 | 110.1013 | 122.4792 | 0.60883 | 122.7676 | 105.661 | -0.40283 | 122.4792 | 0.60883 | 105.661 | 110.1013 | 122.7676 | -123.1247 | -123.0331
3242.9062 | 122.8546 | -105.1437 | 17.4957 | -0.14847 | 0.004939 | 0.0043088 | 0.012232 | -0.0028348 | 0.0052615 | 0.0078977 | -104.3381 | 17.6193 | -105.3955 | 18.3472 | 5.3421 | 0.91095 | 17.4728 | -6.8161 | 17.7109 | -105.455 | -0.25177 | 0.1236 | 0.80566 | 123.4909 | -12.1536 | -0.31128 | 0.21515 | 1.0574 | 122.6166 | 98.3276 | 110.4858 | 122.7631 | 0.80566 | 122.8546 | 106.0547 | -0.31128 | 122.7631 | 0.80566 | 106.0547 | 110.4858 | 122.8546 | -122.8912 | -122.9507
3243.9062 | 122.8455 | -108.3664 | 14.3417 | 0.080414 | 0.0053662 | 0.0051632 | 0.015436 | 0.00058321 | 0.0041933 | 0.0051205 | -107.8079 | 14.122 | -108.8425 | 14.0396 | 4.2068 | 1.1215 | 14.1357 | -7.9514 | 14.3417 | -108.7738 | -0.47607 | -0.21973 | 0.55847 | 122.406 | -10.1349 | -0.40741 | 0 | 1.0345 | 122.5021 | 100.415 | 112.5732 | 122.4884 | 0.55847 | 122.7081 | 109.4879 | -0.40741 | 122.4884 | 0.55847 | 109.4879 | 112.5732 | 122.7081 | -123.1842 | -123.1155
3244.9062 | 122.8363 | -93.6813 | 28.9673 | -0.22476 | 0.0030164 | 0.0072996 | 0.0017645 | -0.0024076 | 0.010816 | 0.0049069 | -93.0679 | 29.0314 | -94.0338 | 29.2053 | 8.5876 | -0.086975 | 28.8895 | -4.8935 | 29.0222 | -94.0704 | -0.35248 | 0.064087 | 0.6134 | 122.8867 | -20.3796 | -0.3891 | 0.054932 | 0.96588 | 122.5708 | 88.7878 | 102.269 | 122.7127 | 0.6134 | 122.7036 | 93.5944 | -0.3891 | 122.7127 | 0.6134 | 93.5944 | 102.269 | 122.7036 | -123.0011 | -123.0377
3245.9062 | 122.8867 | -93.5806 | 29.1641 | -0.14084 | 0.0040846 | 0.0068722 | 0.0024053 | -0.0026212 | 0.0086795 | 0.0034115 | -92.7475 | 28.9856 | -93.8187 | 29.3335 | 8.5922 | -0.050354 | 29.0588 | -5.3146 | 29.1824 | -93.988 | -0.23804 | -0.17853 | 0.83313 | 122.9141 | -20.5719 | -0.40741 | 0.01831 | 1.0712 | 122.6395 | 88.266 | 102.1729 | 122.5662 | 0.83313 | 122.7631 | 93.5303 | -0.40741 | 122.5662 | 0.83313 | 93.5303 | 102.1729 | 122.7631 | -122.9828 | -123.1522
3246.9062 | 122.8867 | -93.869 | 28.8116 | -0.056915 | 0.0023756 | 0.0075132 | 0.0053961 | -0.00027139 | 0.0059023 | 0.0031979 | -93.0771 | 28.9673 | -94.0018 | 28.8437 | 8.638 | -0.018311 | 28.7338 | -5.7312 | 28.9032 | -94.2719 | -0.13275 | 0.15564 | 0.79193 | 122.7127 | -20.1736 | -0.40283 | 0.091552 | 0.92468 | 122.6028 | 88.1378 | 102.507 | 122.8363 | 0.79193 | 122.7722 | 93.8507 | -0.40283 | 122.8363 | 0.79193 | 93.8507 | 102.507 | 122.7722 | -122.8134 | -123.0835
3247.9062 | 122.8821 | -93.3197 | 29.425 | -0.095062 | 0.004939 | 0.0062314 | 0.0056097 | -0.00091219 | 0.0091067 | 0.0023435 | -93.1412 | 29.0634 | -94.1254 | 29.4525 | 8.7158 | -0.041199 | 29.3518 | -5.3696 | 29.4113 | -93.6035 | -0.80566 | -0.36163 | 0.17853 | 122.7722 | -20.7092 | -0.28381 | -0.013733 | 0.98419 | 122.6715 | 87.9501 | 102.0355 | 122.3831 | 0.17853 | 122.731 | 93.2785 | -0.28381 | 122.3831 | 0.17853 | 93.2785 | 102.0355 | 122.731 | -123.5504 | -123.0286
3248.9062 | 122.85 | -105.3543 | 17.3172 | 0.27115 | 0.0051526 | 0.0034544 | 0.012232 | -5.7592e-05 | 0.0063297 | 0.0040525 | -104.4067 | 17.4316 | -105.574 | 17.07 | 5.1727 | 0.91553 | 17.1936 | -7.045 | 17.3401 | -105.7571 | -0.21973 | 0.11444 | 0.94757 | 122.4243 | -12.1445 | -0.40283 | 0.022888 | 1.1673 | 122.5479 | 98.3093 | 110.527 | 122.7859 | 0.94757 | 122.6944 | 106.2698 | -0.40283 | 122.7859 | 0.94757 | 106.2698 | 110.527 | 122.6944 | -122.8912 | -123.0743
3249.9062 | 122.8958 | -108.4076 | 14.2822 | -0.17136 | 0.0034436 | 0.010717 | 0.014368 | -0.002194 | 0.0033389 | 0.0055479 | -107.8354 | 14.2502 | -108.8745 | 14.1632 | 4.3625 | 1.2268 | 14.0854 | -7.5211 | 14.2639 | -108.7601 | -0.46692 | -0.032044 | 0.57221 | 122.5708 | -9.9197 | -0.35248 | -0.018311 | 1.0391 | 122.493 | 100.8865 | 112.7701 | 122.6578 | 0.57221 | 122.6715 | 109.6344 | -0.35248 | 122.6578 | 0.57221 | 109.6344 | 112.7701 | 122.6715 | -123.1567 | -123.0423
3250.9062 | 122.8638 | -108.7143 | 13.9343 | -0.21713 | 0.0025892 | 0.008154 | 0.011377 | -0.00091219 | 0.0044071 | 0.0040525 | -107.9361 | 13.9847 | -109.0347 | 13.8931 | 4.2297 | 1.1856 | 13.8336 | -7.4753 | 13.9481 | -109.1766 | -0.32044 | 0.050354 | 0.7782 | 122.6074 | -9.7046 | -0.46234 | 0.013733 | 1.0986 | 122.5479 | 101.239 | 112.944 | 122.699 | 0.7782 | 122.6624 | 109.8999 | -0.46234 | 122.699 | 0.7782 | 109.8999 | 112.944 | 122.6624 | -122.9691 | -123.111
3251.9062 | 122.8455 | -94.0201 | 28.743 | -0.12558 | 0.0030164 | 0.0070858 | 0.0021917 | -0.0043302 | 0.0097475 | 0.00084806 | -93.4387 | 28.6606 | -94.4046 | 28.5599 | 8.5648 | -0.091553 | 29.0359 | -4.9026 | 28.7933 | -94.3176 | -0.38452 | -0.082398 | 0.58136 | 122.58 | -20.1782 | -0.29755 | 0.050354 | 0.96588 | 123.056 | 89.1174 | 102.5848 | 122.6807 | 0.58136 | 122.8134 | 93.9285 | -0.29755 | 122.6807 | 0.58136 | 93.9285 | 102.5848 | 122.8134 | -123.1476 | -123.0606
3252.9062 | 122.905 | -93.6172 | 29.155 | -0.018768 | 0.0040846 | 0.0021726 | 0.0062507 | -0.0024076 | 0.0086795 | 0.00042086 | -93.2968 | 28.8116 | -94.2581 | 28.8803 | 8.6884 | -0.009155 | 29.1733 | -4.4907 | 29.0497 | -94.0018 | -0.64087 | -0.34332 | 0.32044 | 122.4976 | -20.4666 | -0.38452 | -0.10528 | 0.9613 | 122.7905 | 89.1266 | 102.3056 | 122.4289 | 0.32044 | 122.6669 | 93.6081 | -0.38452 | 122.4289 | 0.32044 | 93.6081 | 102.3056 | 122.6669 | -123.4131 | -123.1567
3253.9062 | 122.8821 | -93.8004 | 28.83 | 0.16434 | 0.0042982 | 0.005377 | 0.0047553 | -0.0019802 | 0.010816 | 0.0044797 | -93.3243 | 28.743 | -94.3405 | 28.8254 | 8.5739 | -0.059509 | 28.6331 | -4.66 | 28.8254 | -94.2444 | -0.54016 | -0.086975 | 0.47607 | 122.6257 | -20.256 | -0.44403 | -0.004578 | 1.0162 | 122.4335 | 89.1403 | 102.3743 | 122.5433 | 0.47607 | 122.6257 | 93.7408 | -0.44403 | 122.5433 | 0.47607 | 93.7408 | 102.3743 | 122.6257 | -123.1705 | -123.0743
3254.9062 | 122.9279 | -93.8873 | 28.7567 | -0.10269 | 0.0017346 | 0.0070858 | 0.0045417 | -0.002194 | 0.0086795 | 0.0042661 | -93.1686 | 28.7842 | -94.1803 | 28.7613 | 8.5556 | 0.07782 | 28.5416 | -5.2185 | 28.7292 | -94.3268 | -0.29297 | 0.027466 | 0.71869 | 122.6486 | -20.2011 | -0.43945 | -0.027466 | 1.0117 | 122.4289 | 88.6688 | 102.4429 | 122.6715 | 0.71869 | 122.6166 | 93.9651 | -0.43945 | 122.6715 | 0.71869 | 93.9651 | 102.4429 | 122.6166 | -122.937 | -123.0835
3255.9062 | 122.8775 | -93.5989 | 29.0726 | 0.0041197 | 0.0034436 | 0.003027 | 0.0068915 | -5.7592e-05 | 0.0097475 | 0.0057615 | -92.7521 | 29.4571 | -93.6676 | 29.1916 | 8.9355 | 0.20599 | 29.0451 | -4.715 | 29.2603 | -93.9331 | -0.068665 | 0.38452 | 0.84686 | 122.7905 | -20.137 | -0.33417 | 0.18768 | 0.91553 | 122.644 | 88.884 | 102.5345 | 123.056 | 0.84686 | 122.8592 | 93.8049 | -0.33417 | 123.056 | 0.84686 | 93.8049 | 102.5345 | 122.8592 | -122.7402 | -123.0057
3256.9062 | 122.8958 | -93.9651 | 28.6423 | -0.034027 | 0.0038708 | 0.0085812 | 0.0068915 | -0.0019802 | 0.0091067 | 0.0025571 | -93.2327 | 29.155 | -94.0567 | 28.7888 | 8.5785 | -0.009155 | 28.4454 | -5.0858 | 28.6697 | -94.4321 | -0.091553 | 0.5127 | 0.73242 | 122.7539 | -20.0638 | -0.46692 | 0.027466 | 0.82398 | 122.4106 | 88.8794 | 102.5436 | 123.1201 | 0.73242 | 122.6349 | 93.956 | -0.46692 | 123.1201 | 0.73242 | 93.956 | 102.5436 | 122.6349 | -122.699 | -123.0743
3257.9062 | 122.8912 | -94.075 | 28.6377 | -0.17899 | 0.0042982 | 0.0021726 | 0.0049689 | 0.00036961 | 0.0086795 | 0.0012753 | -93.2556 | 28.5965 | -94.4275 | 28.5324 | 8.5144 | -0.050354 | 28.6423 | -5.2505 | 28.6789 | -94.4641 | -0.35248 | -0.041198 | 0.8194 | 122.6074 | -20.1233 | -0.3891 | 0.041199 | 1.1719 | 122.7173 | 88.8245 | 102.5894 | 122.6715 | 0.8194 | 122.7539 | 94.0247 | -0.3891 | 122.6715 | 0.8194 | 94.0247 | 102.5894 | 122.7539 | -123.0652 | -123.1018
3258.9062 | 122.818 | -94.1849 | 28.5278 | 0.080414 | 0.0045118 | 0.0049496 | 0.0073187 | -0.00048499 | 0.0091067 | 0.0027707 | -93.7363 | 28.3722 | -94.6976 | 28.5873 | 8.4778 | -0.086975 | 28.5828 | -5.5023 | 28.6057 | -94.5419 | -0.5127 | -0.15564 | 0.44861 | 122.7722 | -20.05 | -0.35706 | 0.07782 | 0.9613 | 122.7676 | 88.6826 | 102.6627 | 122.5571 | 0.44861 | 122.7905 | 94.0979 | -0.35706 | 122.5571 | 0.44861 | 94.0979 | 102.6627 | 122.7905 | -123.2254 | -123.0698
3259.9062 | 122.8867 | -93.6539 | 29.0176 | 0.011749 | 0.0064344 | 0.0058042 | 0.0058233 | -0.0019802 | 0.010816 | 0.0027707 | -93.0679 | 28.8986 | -94.1528 | 28.5645 | 8.4869 | -0.036621 | 29.425 | -4.6005 | 29.0497 | -93.9972 | -0.49896 | -0.11902 | 0.58594 | 122.2183 | -20.5307 | -0.34332 | 0.032044 | 1.0849 | 123.0789 | 89.0533 | 102.1408 | 122.5525 | 0.58594 | 122.7036 | 93.6172 | -0.34332 | 122.5525 | 0.58594 | 93.6172 | 102.1408 | 122.7036 | -123.1705 | -123.0148
3260.9062 | 122.8821 | -93.4616 | 29.2603 | 0.042267 | 0.0038708 | 0.0055906 | 0.0068915 | -0.0011258 | 0.0078249 | 0.0036253 | -93.5165 | 28.6148 | -94.487 | 28.3081 | 8.4686 | -0.059509 | 28.3813 | -4.3259 | 28.6926 | -94.0155 | -1.0254 | -0.64545 | -0.054932 | 121.7697 | -20.7916 | -0.55389 | -0.56763 | 0.97046 | 121.843 | 89.1357 | 101.9302 | 122.0764 | -0.054932 | 122.1542 | 93.4021 | -0.55389 | 122.0764 | -0.054932 | 93.4021 | 101.9302 | 122.1542 | -123.7473 | -123.2758
3261.9062 | 122.8455 | -113.2782 | 9.3933 | 0.049896 | 0.0040846 | 0.0058042 | 0.017573 | -0.00027139 | 0.0020571 | 0.0044797 | -112.3627 | 9.5169 | -113.5574 | 9.3063 | 2.7924 | 1.5793 | 9.256 | -8.4183 | 9.4528 | -113.7405 | -0.27924 | 0.1236 | 0.91553 | 122.5845 | -6.601 | -0.46234 | 0.059509 | 1.1948 | 122.5342 | 104.8599 | 116.0706 | 122.7951 | 0.91553 | 122.731 | 114.8575 | -0.46234 | 122.7951 | 0.91553 | 114.8575 | 116.0706 | 122.731 | -122.9507 | -123.1339
3262.9062 | 122.8729 | -93.9194 | 28.6331 | -0.0035098 | 0.0077162 | 0.0049496 | 0.0036871 | -0.0011258 | 0.0091067 | 0.0049069 | -93.7637 | 28.2166 | -94.7388 | 29.5258 | 8.8348 | -0.068665 | 28.7201 | -5.3238 | 29.2328 | -94.1666 | -0.8194 | -0.41656 | 0.15564 | 123.4451 | -19.7983 | -0.24719 | 0.59967 | 0.97504 | 122.6395 | 88.5956 | 102.7542 | 122.1359 | 0.15564 | 123.1522 | 93.8507 | -0.24719 | 122.1359 | 0.15564 | 93.8507 | 102.7542 | 123.1522 | -123.3719 | -122.7997
3263.9062 | 122.905 | -105.9677 | 16.658 | 0.233 | 0.0030164 | 0.0072996 | 0.011805 | 0.001224 | 0.0031253 | 0.0042661 | -105.0293 | 17.0837 | -106.1874 | 16.507 | 4.9301 | 1.1536 | 17.4866 | -7.2922 | 16.9373 | -106.2515 | -0.21973 | 0.42572 | 0.93842 | 122.4747 | -11.7279 | -0.28381 | 0.27924 | 1.1581 | 123.4543 | 98.6755 | 110.8978 | 123.0515 | 0.93842 | 122.905 | 107.1213 | -0.28381 | 123.0515 | 0.93842 | 107.1213 | 110.8978 | 122.905 | -122.8455 | -122.9095
3264.9062 | 122.9416 | -93.4799 | 28.8803 | -0.0035098 | 0.006648 | 0.004736 | 0.0041143 | -0.001553 | 0.010389 | 0.0017027 | -92.72 | 29.3243 | -93.7271 | 29.2099 | 8.6105 | -0.10529 | 29.1321 | -4.9942 | 29.2099 | -93.8553 | -0.24719 | 0.44403 | 0.75989 | 122.6898 | -20.2698 | -0.37537 | 0.32959 | 1.0071 | 122.612 | 88.4857 | 102.0905 | 122.8043 | 0.75989 | 122.6898 | 93.3746 | -0.37537 | 122.8043 | 0.75989 | 93.3746 | 102.0905 | 122.6898 | -122.6074 | -122.7356
3265.9062 | 122.8958 | -93.3197 | 29.3518 | -0.0035098 | 0.0060072 | 0.0090086 | 0.0045417 | -0.003262 | 0.0078249 | 0.0027707 | -93.2053 | 28.8345 | -94.1986 | 28.8895 | 8.6014 | -0.091553 | 29.3747 | -4.2984 | 29.3655 | -93.4845 | -0.87891 | -0.51727 | 0.11444 | 122.2092 | -20.7504 | -0.16479 | 0.013733 | 0.99335 | 122.6944 | 89.0213 | 101.9211 | 122.1542 | 0.11444 | 122.6852 | 93.2281 | -0.16479 | 122.1542 | 0.11444 | 93.2281 | 101.9211 | 122.6852 | -123.5504 | -122.8363
3266.9062 | 122.8363 | -94.2764 | 28.418 | 0.057526 | 0.0040846 | 0.0066586 | 0.0047553 | -0.0030484 | 0.010175 | 0.0012753 | -93.6722 | 28.4088 | -94.6335 | 28.4454 | 8.4137 | -0.086975 | 28.4363 | -4.7836 | 28.5187 | -94.6014 | -0.35706 | -0.009156 | 0.60425 | 122.7219 | -20.0043 | -0.32501 | 0.10071 | 0.9613 | 122.7127 | 89.4928 | 102.6901 | 122.6852 | 0.60425 | 122.7951 | 94.1895 | -0.32501 | 122.6852 | 0.60425 | 94.1895 | 102.6901 | 122.7951 | -123.0515 | -123.0194
3267.9062 | 122.8363 | -93.8187 | 28.8254 | 0.11093 | 0.006648 | 0.0055906 | 0.0039007 | -0.0011258 | 0.011029 | 0.0023435 | -92.8482 | 29.0634 | -93.9514 | 29.1458 | 8.5922 | -0.086975 | 28.7888 | -4.5181 | 28.9627 | -94.1986 | -0.13275 | 0.23804 | 0.97046 | 122.9645 | -20.2332 | -0.37994 | 0.13733 | 1.1032 | 122.6074 | 89.3005 | 102.4109 | 122.8821 | 0.97046 | 122.7814 | 93.7317 | -0.37994 | 122.8821 | 0.97046 | 93.7317 | 102.4109 | 122.7814 | -122.7768 | -123.024
3268.9062 | 122.8958 | -94.0613 | 28.6148 | 0.28641 | 0.0053662 | 0.006445 | 0.0047553 | -0.0024076 | 0.0076113 | 0.0049069 | -93.5898 | 28.45 | -94.6381 | 28.569 | 8.4549 | -0.068665 | 28.4454 | -4.6326 | 28.6331 | -94.4824 | -0.57678 | -0.16479 | 0.4715 | 122.6303 | -20.1599 | -0.42114 | 0.018311 | 1.0483 | 122.5067 | 89.4287 | 102.5162 | 122.5113 | 0.4715 | 122.6944 | 93.9926 | -0.42114 | 122.5113 | 0.4715 | 93.9926 | 102.5162 | 122.6944 | -123.2529 | -123.0972
3269.9062 | 122.8546 | -94.0796 | 28.5461 | 0.12619 | 0.0047254 | 0.0043088 | 0.0086005 | -0.00048499 | 0.010389 | 0.0053343 | -93.3792 | 28.6148 | -94.3909 | 28.5278 | 8.4595 | -0.13275 | 28.6285 | -4.3442 | 28.6926 | -94.4641 | -0.31128 | 0.068664 | 0.70038 | 122.6074 | -20.0867 | -0.38452 | 0.14648 | 1.0117 | 122.7081 | 89.7354 | 102.5391 | 122.6944 | 0.70038 | 122.7722 | 93.9468 | -0.38452 | 122.6944 | 0.70038 | 93.9468 | 102.5391 | 122.7722 | -122.937 | -123.0103
3270.9062 | 122.8317 | -93.9835 | 28.6331 | 0.16434 | 0.0034436 | 0.0040952 | 0.0034735 | 0.00015601 | 0.0086795 | 0.0057615 | -92.7567 | 29.6585 | -93.6951 | 29.361 | 8.6426 | -0.068665 | 28.5919 | -4.7745 | 29.0726 | -94.2261 | 0.28839 | 1.0254 | 1.2268 | 123.3444 | -19.9905 | -0.24262 | 0.43945 | 0.93842 | 122.5754 | 89.209 | 102.626 | 123.642 | 1.2268 | 123.056 | 93.9148 | -0.24262 | 123.642 | 1.2268 | 93.9148 | 102.626 | 123.056 | -122.3282 | -122.8592
3271.9062 | 122.8455 | -94.8898 | 27.7313 | 0.065155 | 0.0047254 | 0.0025998 | 0.0079595 | -0.0036892 | 0.0069705 | 0.0029843 | -94.0338 | 28.0197 | -94.9722 | 27.8046 | 7.9742 | -0.086975 | 27.7954 | -4.7104 | 27.9007 | -95.1645 | -0.082397 | 0.28839 | 0.85602 | 122.6944 | -19.7571 | -0.27466 | 0.16937 | 0.93842 | 122.6852 | 90.1794 | 102.8641 | 122.9095 | 0.85602 | 122.7905 | 94.8029 | -0.27466 | 122.9095 | 0.85602 | 94.8029 | 102.8641 | 122.7905 | -122.7036 | -122.8958
3272.9062 | 122.8546 | -94.0613 | 28.5919 | 0.20248 | 0.0038708 | 0.008154 | 0.0051825 | -0.0011258 | 0.0097475 | 0.0036253 | -93.7683 | 28.2486 | -94.7342 | 28.3585 | 8.3267 | -0.073242 | 27.9785 | -4.6509 | 28.244 | -94.8715 | -0.67291 | -0.34332 | 0.29297 | 122.4197 | -20.2652 | -0.81024 | -0.3479 | 0.96588 | 122.0398 | 89.4104 | 102.388 | 122.3099 | 0.29297 | 122.3053 | 93.988 | -0.81024 | 122.3099 | 0.29297 | 93.988 | 102.388 | 122.3053 | -123.3261 | -123.4634
3273.9062 | 122.9645 | -94.249 | 28.3035 | 0.56107 | 0.0036572 | 0.0094358 | 0.0009101 | -0.00091219 | 0.0095339 | 0.0049069 | -93.5715 | 28.2578 | -94.6198 | 28.45 | 8.5007 | 0.059509 | 28.0289 | -4.5685 | 28.3539 | -94.6655 | -0.37079 | -0.045777 | 0.67749 | 122.699 | -19.8029 | -0.41656 | 0.050354 | 1.0483 | 122.2778 | 89.6805 | 102.7496 | 122.5067 | 0.67749 | 122.6028 | 94.3085 | -0.41656 | 122.5067 | 0.67749 | 94.3085 | 102.7496 | 122.6028 | -122.9233 | -122.9691
3274.9062 | 122.8409 | -94.4641 | 28.1296 | 0.25589 | 0.006648 | 0.0075132 | 0.0053961 | -0.0026212 | 0.010175 | 0.0031979 | -93.4525 | 29.8965 | -94.0842 | 28.093 | 8.313 | -0.045776 | 28.0609 | -4.9484 | 28.1021 | -95.0043 | 0.37994 | 1.767 | 1.0117 | 122.5571 | -19.8166 | -0.54016 | -0.027466 | 0.63171 | 122.525 | 89.5157 | 102.7771 | 124.3607 | 1.0117 | 122.5662 | 94.4183 | -0.54016 | 124.3607 | 1.0117 | 94.4183 | 102.7771 | 122.5662 | -122.2137 | -123.1338
3275.9062 | 122.8226 | -94.0109 | 28.6102 | -0.69778 | 0.0062208 | 0.008154 | 0.0058233 | -0.0030484 | 0.011243 | 0.0055479 | -93.2419 | 28.7521 | -94.3039 | 28.6469 | 8.4595 | -0.12817 | 28.5553 | -4.6188 | 28.6697 | -94.4962 | -0.29297 | 0.14191 | 0.76904 | 122.6578 | -20.1508 | -0.48523 | 0.05951 | 1.062 | 122.5662 | 89.3921 | 102.4704 | 122.7631 | 0.76904 | 122.6807 | 93.8828 | -0.48523 | 122.7631 | 0.76904 | 93.8828 | 102.4704 | 122.6807 | -122.9141 | -123.1064
3276.9062 | 122.8683 | -94.2032 | 28.418 | 0.16434 | 0.0062208 | 0.010717 | 0.0053961 | -0.0019802 | 0.015088 | 0.0051205 | -93.8232 | 28.1708 | -94.8074 | 28.3813 | 8.3725 | 0.027466 | 28.4729 | -4.7974 | 28.5461 | -94.6289 | -0.60425 | -0.24719 | 0.37994 | 122.5845 | -20.0455 | -0.42572 | 0.12817 | 0.98419 | 122.6761 | 89.4058 | 102.5757 | 122.374 | 0.37994 | 122.7493 | 94.2307 | -0.42572 | 122.374 | 0.37994 | 94.2307 | 102.5757 | 122.7493 | -123.2254 | -123.0469
3277.9062 | 122.8546 | -94.1299 | 28.4454 | 0.12619 | 0.004939 | 0.010077 | 0.0045417 | -0.00091219 | 0.0082523 | 0.0012753 | -92.9398 | 29.068 | -93.9377 | 28.6148 | 8.4045 | -0.10529 | 28.4729 | -4.6188 | 28.688 | -94.4458 | 0.19226 | 0.62256 | 1.1902 | 122.7448 | -20.0409 | -0.31586 | 0.24261 | 0.99793 | 122.6028 | 89.5111 | 102.5345 | 123.1979 | 1.1902 | 122.818 | 94.0247 | -0.31586 | 123.1979 | 1.1902 | 94.0247 | 102.5345 | 122.818 | -122.3831 | -122.8912
3278.9062 | 122.9736 | -94.2398 | 28.2944 | 0.17197 | 0.0036572 | 0.0094358 | 0.0024053 | -0.002194 | 0.0093203 | 0.0036253 | -93.9102 | 28.0838 | -94.9631 | 28.4042 | 8.3038 | 0.036621 | 28.2349 | -4.4815 | 28.4134 | -94.5831 | -0.72327 | -0.21057 | 0.32959 | 122.644 | -19.9905 | -0.34332 | 0.11902 | 1.0529 | 122.4747 | 89.7583 | 102.5436 | 122.3236 | 0.32959 | 122.6532 | 94.2764 | -0.34332 | 122.3236 | 0.32959 | 94.2764 | 102.5436 | 122.6532 | -123.2574 | -122.8775
3279.9062 | 122.8271 | -93.0267 | 29.6402 | 0.072784 | 0.0042982 | 0.0058042 | 0.0066779 | -0.001553 | 0.010816 | 0.0044797 | -92.5552 | 28.9581 | -93.718 | 29.4296 | 8.606 | -0.10529 | 29.4983 | -4.5319 | 29.5944 | -93.5211 | -0.69122 | -0.68207 | 0.4715 | 122.4564 | -21.0342 | -0.49439 | -0.045777 | 1.1627 | 122.525 | 88.4949 | 101.6327 | 121.9849 | 0.4715 | 122.6212 | 92.9214 | -0.49439 | 121.9849 | 0.4715 | 92.9214 | 101.6327 | 122.6212 | -123.3582 | -123.1613
3280.9062 | 122.8271 | -93.8736 | 28.7064 | 0.20248 | 0.0064344 | 0.0068722 | 0.0021917 | -0.0017666 | 0.0093203 | 0.0031979 | -93.0359 | 29.0863 | -94.0842 | 29.3015 | 8.67 | -0.064087 | 28.862 | -4.6967 | 29.1367 | -94.2169 | -0.21057 | 0.37994 | 0.83771 | 123.175 | -20.0363 | -0.34332 | 0.4303 | 1.0483 | 122.7356 | 89.1769 | 102.5436 | 122.9599 | 0.83771 | 123.0103 | 93.8095 | -0.34332 | 122.9599 | 0.83771 | 93.8095 | 102.5436 | 123.0103 | -122.7905 | -122.9233
3281.9062 | 122.8592 | -94.3863 | 28.2166 | 0.1796 | 0.0057934 | 0.0096494 | 0.0045417 | -0.00091219 | 0.0086795 | 0.0046933 | -93.7729 | 28.2211 | -94.7937 | 28.1708 | 8.2947 | -0.086975 | 28.1982 | -4.5181 | 28.2761 | -94.8624 | -0.40741 | 0.004577 | 0.6134 | 122.5571 | -19.9219 | -0.47607 | 0.059509 | 1.0208 | 122.5845 | 89.8682 | 102.681 | 122.6074 | 0.6134 | 122.6624 | 94.2993 | -0.47607 | 122.6074 | 0.6134 | 94.2993 | 102.681 | 122.6624 | -123.0103 | -123.0789
3282.9062 | 122.8317 | -94.3222 | 28.3127 | 0.13382 | 0.0045118 | 0.0040952 | 0.0043281 | -0.0017666 | 0.0095339 | 0.0053343 | -93.5623 | 28.3722 | -94.6152 | 28.2257 | 8.313 | -0.082397 | 28.1891 | -4.8157 | 28.299 | -94.8532 | -0.29297 | 0.059509 | 0.75989 | 122.5479 | -19.9997 | -0.53101 | -0.013733 | 1.0529 | 122.5113 | 89.5065 | 102.6352 | 122.6944 | 0.75989 | 122.6212 | 94.2398 | -0.53101 | 122.6944 | 0.75989 | 94.2398 | 102.6352 | 122.6212 | -122.9279 | -123.1659
3283.9062 | 122.9462 | -94.0247 | 28.4866 | 0.1796 | 0.0034436 | 0.0062314 | -0.0020807 | -0.002194 | 0.0080387 | 0.0031979 | -93.338 | 28.4409 | -94.4458 | 28.7292 | 8.5373 | 0.050354 | 28.1387 | -4.6463 | 28.4683 | -94.5465 | -0.42114 | -0.045776 | 0.68664 | 122.7539 | -19.9493 | -0.52185 | -0.01831 | 1.1078 | 122.1634 | 89.3784 | 102.5619 | 122.4655 | 0.68664 | 122.493 | 94.075 | -0.52185 | 122.4655 | 0.68664 | 94.075 | 102.5619 | 122.493 | -122.9324 | -123.0331
3284.9062 | 122.8043 | -94.2032 | 28.4592 | 0.065155 | 0.0055798 | 0.0096494 | 0.0062507 | -0.0026212 | 0.0093203 | 0.0034115 | -93.5303 | 28.5553 | -94.519 | 28.4134 | 8.3679 | -0.10071 | 28.418 | -4.7424 | 28.4958 | -94.6655 | -0.31586 | 0.096131 | 0.67291 | 122.6166 | -20.0912 | -0.46234 | 0.036622 | 0.98877 | 122.6212 | 89.4608 | 102.5711 | 122.7585 | 0.67291 | 122.699 | 94.1025 | -0.46234 | 122.7585 | 0.67291 | 94.1025 | 102.5711 | 122.699 | -122.9782 | -123.1247
3285.9062 | 122.85 | -93.7271 | 28.8712 | -0.0035098 | 0.0075024 | 0.0043088 | 0.0068915 | -0.0017666 | 0.0080387 | 0.0040525 | -91.2827 | 30.4459 | -92.5003 | 29.2099 | 8.6792 | -0.09613 | 28.894 | -4.9347 | 29.1412 | -94.075 | 1.2268 | 1.5747 | 2.4445 | 122.937 | -20.192 | -0.3479 | 0.27008 | 1.2177 | 122.6212 | 88.7924 | 102.4063 | 124.173 | 2.4445 | 122.8683 | 93.631 | -0.3479 | 124.173 | 2.4445 | 93.631 | 102.4063 | 122.8683 | -121.3715 | -122.9462
3286.9062 | 122.8958 | -93.631 | 28.9398 | 0.042267 | 0.0047254 | 0.0090086 | 0.0075323 | -0.0017666 | 0.0082523 | 0.0044797 | -93.4479 | 28.6148 | -94.487 | 28.9261 | 8.5922 | -0.07782 | 28.9673 | -4.7562 | 29.155 | -93.9651 | -0.85602 | -0.32501 | 0.18311 | 122.5571 | -20.3476 | -0.33417 | 0.21515 | 1.0391 | 122.5983 | 88.8748 | 102.2232 | 122.2458 | 0.18311 | 122.7859 | 93.5532 | -0.33417 | 122.2458 | 0.18311 | 93.5532 | 102.2232 | 122.7859 | -123.4268 | -122.905
3287.9062 | 122.818 | -94.6472 | 27.9556 | 0.13382 | 0.0042982 | 0.0083676 | 0.0049689 | -5.7592e-05 | 0.0073977 | 0.0025571 | -93.8232 | 28.2257 | -94.8532 | 28.3081 | 8.3267 | -0.073242 | 27.8412 | -5.0583 | 28.1387 | -95.1279 | -0.20599 | 0.27008 | 0.82398 | 122.9553 | -19.6289 | -0.48065 | 0.18311 | 1.03 | 122.4884 | 89.5889 | 102.9739 | 122.8729 | 0.82398 | 122.7859 | 94.574 | -0.48065 | 122.8729 | 0.82398 | 94.574 | 102.9739 | 122.7859 | -122.8088 | -123.0835
3288.9062 | 122.9599 | -94.1116 | 28.4409 | 0.21774 | 0.0036572 | 0.005377 | 0.0015509 | -0.0041166 | 0.0088931 | 0.0019163 | -93.5349 | 28.3493 | -94.5831 | 28.2623 | 8.313 | 0.068665 | 28.1433 | -4.6829 | 28.3356 | -94.6518 | -0.4715 | -0.091553 | 0.57678 | 122.374 | -20.1279 | -0.54016 | -0.10529 | 1.0483 | 122.2549 | 89.4287 | 102.4246 | 122.4609 | 0.57678 | 122.4472 | 94.1803 | -0.54016 | 122.4609 | 0.57678 | 94.1803 | 102.4246 | 122.4472 | -123.024 | -123.0927
3289.9062 | 122.85 | -93.4982 | 29.1641 | 0.019379 | 0.0028028 | 0.0096494 | 0.0066779 | -0.002194 | 0.010816 | 0.0031979 | -93.2098 | 28.9124 | -94.2169 | 29.0131 | 8.5785 | -0.11902 | 29.6082 | -4.8019 | 29.3198 | -93.8919 | -0.71869 | -0.25177 | 0.28839 | 122.5113 | -20.5856 | -0.39368 | 0.15564 | 1.0071 | 123.1064 | 88.6963 | 102.0767 | 122.4106 | 0.28839 | 122.818 | 93.3792 | -0.39368 | 122.4106 | 0.28839 | 93.3792 | 102.0767 | 122.818 | -123.381 | -123.056
3290.9062 | 122.8592 | -93.8324 | 28.8025 | 0.042267 | 0.0036572 | 0.009863 | 0.0066779 | -0.0026212 | 0.010175 | 0.0038389 | -93.219 | 28.894 | -94.2352 | 28.9124 | 8.5236 | -0.09613 | 28.6652 | -4.9118 | 28.8986 | -94.2444 | -0.40283 | 0.091553 | 0.6134 | 122.7448 | -20.2789 | -0.41199 | 0.096131 | 1.0162 | 122.4976 | 88.9206 | 102.356 | 122.7264 | 0.6134 | 122.731 | 93.7363 | -0.41199 | 122.7264 | 0.6134 | 93.7363 | 102.356 | 122.731 | -123.0377 | -123.0469
3291.9219 | 122.905 | -92.8848 | 29.5761 | 0.1033 | 0.0013074 | 0.0062314 | -0.0022943 | -0.0030484 | 0.010175 | 0.0057615 | -92.1204 | 30.0339 | -92.9169 | 30.574 | 9.082 | -0.018311 | 29.837 | -5.1727 | 30.162 | -93.1595 | -0.032043 | 0.45776 | 0.76447 | 123.4589 | -20.4941 | -0.27466 | 0.58594 | 0.79651 | 122.7219 | 87.7121 | 101.9669 | 122.9187 | 0.76447 | 123.0469 | 92.8665 | -0.27466 | 122.9187 | 0.76447 | 92.8665 | 101.9669 | 123.0469 | -122.493 | -122.7356
3292.9062 | 122.8638 | -93.0267 | 29.5212 | -0.026398 | 0.0051526 | 0.0070858 | 0.0045417 | -0.003903 | 0.0093203 | 0.0055479 | -92.5186 | 29.5441 | -93.5074 | 30.3268 | 8.8943 | -0.032043 | 29.6631 | -4.8157 | 29.9606 | -93.3243 | -0.48065 | 0.022888 | 0.50812 | 123.3536 | -20.6268 | -0.29755 | 0.43945 | 0.98877 | 122.6898 | 88.2111 | 101.9211 | 122.5708 | 0.50812 | 122.9874 | 92.9947 | -0.29755 | 122.5708 | 0.50812 | 92.9947 | 101.9211 | 122.9874 | -123.0286 | -122.8455
3293.9062 | 122.6807 | -88.3484 | 34.964 | 0.26352 | 0.0023756 | 0.0051632 | 0.0034735 | -0.0017666 | 0.0091067 | 0.0031979 | -92.9581 | 29.6494 | -93.6905 | 29.393 | 8.7479 | 0.036621 | 28.9352 | -4.2984 | 29.2831 | -93.5669 | -5.3421 | -5.3146 | -4.6097 | 117.7414 | -26.2161 | -5.2185 | -5.6808 | 0.73242 | 117.2836 | 84.05 | 97.0963 | 117.9977 | -4.6097 | 117.6315 | 88.385 | -5.2185 | 117.9977 | -4.6097 | 88.385 | 97.0963 | 117.6315 | -128.6545 | -128.5309
3294.9062 | 122.8409 | -93.9789 | 28.6148 | 0.0041197 | 0.0023756 | 0.0055906 | 0.0058233 | -0.003262 | 0.0071841 | 0.0012753 | -93.425 | 28.5919 | -94.5099 | 28.6011 | 8.3679 | -0.082397 | 28.5599 | -4.8203 | 28.6148 | -94.4778 | -0.53101 | -0.022888 | 0.55389 | 122.58 | -20.2469 | -0.49896 | 0 | 1.0849 | 122.5388 | 89.1586 | 102.3468 | 122.5708 | 0.55389 | 122.5937 | 93.8965 | -0.49896 | 122.5708 | 0.55389 | 93.8965 | 102.3468 | 122.5937 | -123.1247 | -123.0927
3295.9062 | 122.8317 | -93.8599 | 28.8162 | 0.042267 | 0.0064344 | 0.009863 | 0.0053961 | -0.0019802 | 0.0071841 | 0.0019163 | -92.8116 | 29.3243 | -93.7592 | 28.6606 | 8.4229 | -0.09613 | 28.5599 | -4.7058 | 28.7567 | -94.3497 | 0.10071 | 0.50812 | 1.0483 | 122.5204 | -20.3934 | -0.48981 | -0.059509 | 0.94757 | 122.4197 | 89.1541 | 102.2827 | 123.1842 | 1.0483 | 122.6166 | 93.7637 | -0.48981 | 123.1842 | 1.0483 | 93.7637 | 102.2827 | 122.6166 | -122.5754 | -123.1659
3296.9062 | 122.9828 | -94.1849 | 28.3401 | 0.28641 | 0.002162 | 0.003027 | 0.0019781 | -0.002194 | 0.0088931 | 0.0014889 | -92.2119 | 28.5828 | -94.162 | 28.3951 | 8.4137 | 0.086975 | 28.1296 | -4.4357 | 28.3127 | -94.6609 | 0.022888 | 0.24262 | 1.973 | 122.58 | -19.9265 | -0.47607 | -0.027466 | 1.9501 | 122.3145 | 89.7491 | 102.5986 | 122.7676 | 1.973 | 122.4976 | 94.2719 | -0.47607 | 122.7676 | 1.973 | 94.2719 | 102.5986 | 122.4976 | -122.5021 | -123.0011
3297.9062 | 122.8729 | -93.9102 | 28.7521 | -0.049286 | 0.0062208 | 0.0032406 | 0.0090277 | -0.00069859 | 0.0093203 | 0.0025571 | -94.0475 | 28.1296 | -94.9356 | 28.6606 | 8.4549 | -0.064087 | 28.6285 | -4.5456 | 28.7384 | -94.3771 | -1.0254 | -0.62256 | -0.13733 | 122.5708 | -20.2972 | -0.46692 | -0.013733 | 0.88806 | 122.5388 | 89.3646 | 102.3651 | 122.0398 | -0.13733 | 122.6486 | 93.8461 | -0.46692 | 122.0398 | -0.13733 | 93.8461 | 102.3651 | 122.6486 | -123.6877 | -123.1293
3298.9062 | 122.818 | -93.8965 | 28.7384 | -0.087433 | 0.0055798 | 0.0049496 | 0.0047553 | -0.0026212 | 0.0088931 | 0.0040525 | -93.1274 | 29.1275 | -93.9056 | 29.0909 | 8.5693 | -0.050354 | 28.8437 | -4.6417 | 28.9032 | -94.3039 | -0.009156 | 0.3891 | 0.76904 | 122.9874 | -20.1691 | -0.40741 | 0.16479 | 0.7782 | 122.7402 | 89.2548 | 102.4658 | 123.024 | 0.76904 | 122.7997 | 93.8461 | -0.40741 | 123.024 | 0.76904 | 93.8461 | 102.4658 | 122.7997 | -122.644 | -123.0423
3299.9062 | 122.8912 | -93.8049 | 28.8071 | -0.24002 | 0.0040846 | 0.0070858 | 0.0051825 | -5.7592e-05 | 0.0088931 | 0.0038389 | -93.0405 | 28.8666 | -94.043 | 28.7476 | 8.5144 | -0.032043 | 28.7109 | -4.2984 | 28.8757 | -94.1162 | -0.23804 | 0.059509 | 0.76447 | 122.5525 | -20.2927 | -0.31128 | 0.068664 | 1.0025 | 122.5159 | 89.5065 | 102.3193 | 122.6715 | 0.76447 | 122.6807 | 93.7729 | -0.31128 | 122.6715 | 0.76447 | 93.7729 | 102.3193 | 122.6807 | -122.85 | -122.9233
3300.9062 | 122.8134 | -92.7521 | 29.8233 | -0.011139 | 0.0034436 | 0.0055906 | 0.0053961 | 0.00036961 | 0.0091067 | 0.0040525 | -91.7679 | 30.3497 | -92.6331 | 30.5099 | 8.9081 | -0.14648 | 29.6448 | -4.6051 | 30.0842 | -93.187 | 0.11902 | 0.52643 | 0.98419 | 123.262 | -20.9152 | -0.43488 | 0.26093 | 0.86517 | 122.3969 | 88.147 | 101.6602 | 123.1018 | 0.98419 | 122.8363 | 92.6056 | -0.43488 | 123.1018 | 0.98419 | 92.6056 | 101.6602 | 122.8363 | -122.4564 | -123.0103
3301.9219 | 122.9279 | -94.0292 | 28.5233 | 0.072784 | 0.0013074 | 0.004736 | -0.0054987 | -0.0030484 | 0.0095339 | 0.0053343 | -93.4982 | 28.5049 | -94.487 | 28.7476 | 8.5007 | 0.045776 | 28.3676 | -4.5456 | 28.6057 | -94.4229 | -0.45776 | -0.01831 | 0.53101 | 122.7768 | -20.0226 | -0.39368 | 0.082398 | 0.98877 | 122.3969 | 89.4836 | 102.5299 | 122.5342 | 0.53101 | 122.6349 | 94.075 | -0.39368 | 122.5342 | 0.53101 | 94.075 | 102.5299 | 122.6349 | -123.0103 | -122.9462
3302.9062 | 122.9004 | -93.8324 | 28.775 | -0.011139 | 0.0053662 | 0.0045224 | 0.0064643 | -0.002194 | 0.0093203 | 0.0031979 | -92.4042 | 29.6768 | -93.4479 | 29.0222 | 8.5464 | -0.032043 | 28.5828 | -4.5776 | 28.9124 | -94.2398 | 0.38452 | 0.90179 | 1.4282 | 122.8546 | -20.2286 | -0.40741 | 0.13733 | 1.0437 | 122.4152 | 89.2548 | 102.3788 | 123.5092 | 1.4282 | 122.7448 | 93.8004 | -0.40741 | 123.5092 | 1.4282 | 93.8004 | 102.3788 | 122.7448 | -122.2229 | -123.0148
3303.9219 | 122.9828 | -93.3975 | 29.2145 | 0.18723 | 0.0019482 | 0.010931 | 0.0004827 | -5.7592e-05 | 0.010816 | 0.0046933 | -92.3492 | 29.3427 | -93.457 | 29.5303 | 8.8303 | 0.032043 | 29.4067 | -4.2252 | 29.3335 | -93.7317 | -0.059509 | 0.12817 | 1.0483 | 122.9279 | -20.3842 | -0.33417 | 0.11902 | 1.1078 | 122.8043 | 89.1724 | 102.2278 | 122.7402 | 1.0483 | 122.731 | 93.4296 | -0.33417 | 122.7402 | 1.0483 | 93.4296 | 102.2278 | 122.731 | -122.6715 | -122.9462
3304.9062 | 122.8912 | -93.869 | 28.7521 | -0.21713 | 0.004939 | 0.0070858 | 0.0079595 | -0.002194 | 0.0099613 | 0.0038389 | -92.9947 | 28.9627 | -94.1345 | 28.9764 | 8.5464 | -0.059509 | 28.8254 | -4.39 | 28.9169 | -94.2627 | -0.2655 | 0.21057 | 0.87433 | 122.8455 | -20.2057 | -0.39368 | 0.1648 | 1.1398 | 122.6944 | 89.4791 | 102.4155 | 122.8317 | 0.87433 | 122.7859 | 93.8095 | -0.39368 | 122.8317 | 0.87433 | 93.8095 | 102.4155 | 122.7859 | -122.8867 | -123.0148
3305.9062 | 122.9004 | -93.5898 | 29.0588 | -0.18662 | 0.004939 | 0.0045224 | 0.0041143 | -0.0041166 | 0.011884 | 0.00084806 | -92.7063 | 29.5074 | -93.6218 | 29.2603 | 8.606 | -0.041199 | 28.7659 | -4.5181 | 29.1183 | -94.0338 | -0.032043 | 0.44861 | 0.88348 | 122.85 | -20.4529 | -0.44403 | 0.059509 | 0.91553 | 122.3557 | 89.0717 | 102.1957 | 123.0972 | 0.88348 | 122.7081 | 93.5486 | -0.44403 | 123.0972 | 0.88348 | 93.5486 | 102.1957 | 122.7081 | -122.6807 | -123.0927
3306.9219 | 122.9645 | -94.1162 | 28.3951 | 0.21774 | 0.0038708 | 0.0085812 | 0.0041143 | -0.0019802 | 0.010816 | 0.0034115 | -92.9398 | 29.4479 | -93.0862 | 28.7888 | 8.5281 | 0.036621 | 28.4042 | -4.5639 | 28.7659 | -94.3085 | 1.03 | 1.0529 | 1.1765 | 122.905 | -19.8669 | -0.19226 | 0.37079 | 0.14648 | 122.5204 | 89.5523 | 102.6443 | 123.5641 | 1.1765 | 122.8821 | 94.1528 | -0.19226 | 123.5641 | 1.1765 | 94.1528 | 102.6443 | 122.8821 | -121.4813 | -122.7036
3307.9062 | 122.8958 | -93.7317 | 28.894 | -0.034027 | 0.0060072 | 0.006445 | 0.0064643 | -0.0024076 | 0.0067569 | 0.0031979 | -93.2831 | 28.5919 | -94.4183 | 28.7613 | 8.4869 | -0.059509 | 28.9581 | -4.4266 | 28.9307 | -94.1299 | -0.68665 | -0.30212 | 0.44861 | 122.493 | -20.4071 | -0.39825 | 0.036621 | 1.1353 | 122.6898 | 89.3051 | 102.2186 | 122.3236 | 0.44861 | 122.6624 | 93.6722 | -0.39825 | 122.3236 | 0.44861 | 93.6722 | 102.2186 | 122.6624 | -123.3124 | -123.024
3308.9219 | 122.937 | -94.043 | 28.5324 | 0.1796 | 0.0036572 | 0.0058042 | -0.0003717 | -0.0017666 | 0.010389 | 0.0023435 | -93.5394 | 28.3127 | -94.6472 | 28.6194 | 8.5098 | 0.068665 | 28.3401 | -4.4952 | 28.5645 | -94.4733 | -0.60425 | -0.21973 | 0.50354 | 122.6624 | -20.0226 | -0.4303 | 0.032043 | 1.1078 | 122.3831 | 89.5477 | 102.5528 | 122.3557 | 0.50354 | 122.6074 | 94.1116 | -0.4303 | 122.3557 | 0.50354 | 94.1116 | 102.5528 | 122.6074 | -123.1796 | -123.0057
3309.9062 | 122.8821 | -93.544 | 29.068 | -0.30869 | 0.0062208 | 0.0055906 | 0.0075323 | -0.0034756 | 0.0093203 | 0.0040525 | -93.1732 | 28.894 | -94.1208 | 29.0405 | 8.5556 | -0.050354 | 28.8162 | -4.5044 | 29.0039 | -94.0521 | -0.57678 | -0.17395 | 0.37079 | 122.5845 | -20.5124 | -0.50812 | -0.064087 | 0.94757 | 122.3602 | 89.0396 | 102.0996 | 122.438 | 0.37079 | 122.5479 | 93.4937 | -0.50812 | 122.438 | 0.37079 | 93.4937 | 102.0996 | 122.5479 | -123.1888 | -123.1201
3310.9062 | 122.9004 | -92.8207 | 29.7638 | -0.18662 | 0.0034436 | 0.006445 | 0.0045417 | -0.0026212 | 0.0080387 | 0.0027707 | -92.157 | 30.5466 | -92.9672 | 29.48 | 8.5648 | -0.068665 | 29.3335 | -4.1748 | 29.3976 | -93.4891 | -0.14648 | 0.78278 | 0.66376 | 122.3007 | -21.199 | -0.66833 | -0.36621 | 0.81024 | 122.1542 | 88.6459 | 101.3855 | 123.3673 | 0.66376 | 122.2183 | 92.7521 | -0.66833 | 123.3673 | 0.66376 | 92.7521 | 101.3855 | 122.2183 | -122.731 | -123.2529
3311.9062 | 122.85 | -92.5323 | 30.0247 | -0.079803 | 0.0051526 | 0.006445 | 0.0058233 | -0.00091219 | 0.010389 | 0.0049069 | -91.4062 | 30.4825 | -92.395 | 30.2765 | 8.757 | -0.073242 | 29.5715 | -4.4952 | 29.9057 | -93.1915 | 0.13733 | 0.45776 | 1.1261 | 122.8088 | -21.2677 | -0.65918 | -0.11902 | 0.98877 | 122.1039 | 88.0371 | 101.2894 | 123.0148 | 1.1261 | 122.4381 | 92.4591 | -0.65918 | 123.0148 | 1.1261 | 92.4591 | 101.2894 | 122.4381 | -122.4197 | -123.2162
3312.9062 | 122.8638 | -93.6859 | 28.9398 | -0.17899 | 0.0042982 | 0.0049496 | 0.0045417 | -0.001553 | 0.010389 | 0.0021299 | -92.8391 | 29.1641 | -93.9789 | 28.8849 | 8.4686 | -0.11444 | 29.0955 | -4.3396 | 29.0131 | -94.1299 | -0.29297 | 0.22431 | 0.84686 | 122.5708 | -20.4712 | -0.44403 | 0.073243 | 1.1398 | 122.7814 | 89.3463 | 102.1545 | 122.85 | 0.84686 | 122.699 | 93.5715 | -0.44403 | 122.85 | 0.84686 | 93.5715 | 102.1545 | 122.699 | -122.9187 | -123.0698
3313.9062 | 122.8546 | -93.6447 | 29.0085 | 0.30167 | 0.001521 | 0.001318 | 0.0015509 | 0.00079681 | 0.010175 | 0.0049069 | -92.7979 | 29.0543 | -94.0796 | 28.7064 | 8.4366 | -0.09613 | 28.5919 | -4.5364 | 28.8025 | -94.1483 | -0.43488 | 0.045776 | 0.84686 | 122.3511 | -20.5719 | -0.50354 | -0.20599 | 1.2817 | 122.2366 | 89.1083 | 102.0813 | 122.699 | 0.84686 | 122.4472 | 93.5486 | -0.50354 | 122.699 | 0.84686 | 93.5486 | 102.0813 | 122.4472 | -123.0881 | -123.1567
3314.9062 | 122.8821 | -93.2144 | 29.3289 | -0.026398 | 0.0042982 | 0.0070858 | 0.0068915 | -0.0017666 | 0.0097475 | 0.0034115 | -91.9785 | 29.8645 | -93.1686 | 30.0339 | 8.5464 | -0.082397 | 29.0955 | -4.747 | 29.4296 | -93.6859 | 0.045777 | 0.53558 | 1.236 | 123.2483 | -20.7825 | -0.4715 | 0.10071 | 1.1902 | 122.3099 | 88.4674 | 101.7609 | 123.0789 | 1.236 | 122.644 | 93.132 | -0.4715 | 123.0789 | 1.236 | 93.132 | 101.7609 | 122.644 | -122.4976 | -123.0148
3315.9062 | 122.0581 | -91.2735 | 32.3135 | 0.011749 | 0.0051526 | 0.010077 | 0.0053961 | 0.001224 | 0.0093203 | 0.0023435 | -91.9098 | 30.8441 | -92.7155 | 29.6631 | 8.6746 | -0.10071 | 29.9332 | -4.6875 | 29.8416 | -93.1732 | -1.442 | -1.4694 | -0.63629 | 120.9366 | -23.6389 | -1.8997 | -2.4719 | 0.80566 | 121.2067 | 86.586 | 99.9481 | 122.1176 | -0.63629 | 121.1151 | 91.1728 | -1.8997 | 122.1176 | -0.63629 | 91.1728 | 99.9481 | 121.1151 | -125.029 | -125.4868
3316.9062 | 122.8958 | -93.6035 | 28.9948 | 0.011749 | 0.0064344 | 0.0079404 | 0.0036871 | -0.001553 | 0.0073977 | 0.0017027 | -92.8665 | 28.9261 | -94.075 | 28.7888 | 8.4366 | -0.068665 | 28.8757 | -4.4128 | 28.9948 | -94.0613 | -0.4715 | -0.068665 | 0.737 | 122.3923 | -20.5582 | -0.45776 | 0 | 1.2085 | 122.4792 | 89.1907 | 102.0401 | 122.5296 | 0.737 | 122.5983 | 93.5349 | -0.45776 | 122.5296 | 0.737 | 93.5349 | 102.0401 | 122.5983 | -123.0698 | -123.056
3317.9062 | 122.8867 | -90.9576 | 31.3202 | 0.034637 | 0.004939 | 0.0079404 | 0.0062507 | -0.0017666 | 0.011457 | 0.0053343 | -92.4271 | 29.4846 | -93.1229 | 30.217 | 8.757 | -1.4191 | 44.8242 | -4.6509 | 34.9136 | -88.5864 | -2.1652 | -1.8356 | -1.4694 | 121.1746 | -22.5632 | 2.3712 | 3.5934 | 0.6958 | 135.7819 | 86.3068 | 99.7147 | 120.4422 | -1.4694 | 125.8713 | 89.5386 | 2.3712 | 120.4422 | -1.4694 | 89.5386 | 99.7147 | 125.8713 | -124.4431 | -119.9066
3318.9062 | 122.937 | -93.8416 | 28.6926 | 0.26352 | 0.0025892 | 0.006445 | 0.0019781 | -0.0011258 | 0.010602 | 0.0049069 | -93.0954 | 28.7979 | -94.1162 | 29.1229 | 8.551 | 0.027466 | 28.5828 | -4.4632 | 28.9352 | -94.1895 | -0.27466 | 0.10529 | 0.74616 | 122.9645 | -20.1416 | -0.3479 | 0.24261 | 1.0208 | 122.4243 | 89.3784 | 102.3926 | 122.6395 | 0.74616 | 122.7768 | 93.869 | -0.3479 | 122.6395 | 0.74616 | 93.869 | 102.3926 | 122.7768 | -122.8088 | -122.8821
3319.9062 | 122.8088 | -92.3355 | 30.4596 | -0.034027 | 0.0036572 | 0.0083676 | 0.0068915 | -0.001553 | 0.0099613 | 0.0053343 | -92.189 | 29.6494 | -93.4021 | 29.9423 | 8.725 | 0.13275 | 29.6768 | -4.0329 | 29.8965 | -93.0771 | -1.0666 | -0.81024 | 0.14648 | 122.2778 | -21.7346 | -0.74158 | -0.56305 | 1.2131 | 122.0123 | 88.3026 | 101.0605 | 121.9849 | 0.14648 | 122.2321 | 92.4683 | -0.74158 | 121.9849 | 0.14648 | 92.4683 | 101.0605 | 122.2321 | -123.8617 | -123.5367
3320.9062 | 122.8592 | -93.7775 | 28.8483 | -0.034027 | 0.0028028 | 0.0060178 | 0.0053961 | -0.0043302 | 0.0076113 | 0.0023435 | -93.1686 | 28.6835 | -94.2993 | 28.8437 | 8.8074 | 0.09613 | 28.7476 | -4.3945 | 28.9673 | -94.2444 | -0.52185 | -0.1648 | 0.60883 | 122.6212 | -20.0409 | -0.46692 | 0.11902 | 1.1307 | 122.525 | 89.3829 | 102.5848 | 122.4609 | 0.60883 | 122.7448 | 93.8736 | -0.46692 | 122.4609 | 0.60883 | 93.8736 | 102.5848 | 122.7448 | -123.1476 | -123.0927
3321.9062 | 122.8592 | -93.2968 | 29.3289 | 0.14145 | 0.0079298 | 0.010077 | 0.0034735 | -0.0056118 | 0.010602 | 0.0040525 | -93.1686 | 28.894 | -94.1711 | 29.3106 | 8.5007 | -0.14191 | 29.4937 | -5.1315 | 29.4983 | -93.7363 | -0.87433 | -0.43488 | 0.12817 | 122.6074 | -20.8282 | -0.43945 | 0.16937 | 1.0025 | 122.7905 | 88.1653 | 101.7975 | 122.1909 | 0.12817 | 122.7951 | 93.1549 | -0.43945 | 122.1909 | 0.12817 | 93.1549 | 101.7975 | 122.7951 | -123.5001 | -123.0652
3322.9062 | 122.8592 | -92.9077 | 29.8233 | 0.027008 | 0.0042982 | 0.0083676 | 0.0036871 | -0.0045438 | 0.0071841 | 0.0042661 | -92.8482 | 29.274 | -93.8644 | 28.949 | 8.3908 | -0.13733 | 29.4388 | -4.7058 | 29.274 | -93.5028 | -0.95673 | -0.54932 | 0.059509 | 121.8567 | -21.4325 | -0.59509 | -0.54932 | 1.0162 | 122.3465 | 88.2019 | 101.2985 | 122.1817 | 0.059509 | 122.1817 | 92.7704 | -0.59509 | 122.1817 | 0.059509 | 92.7704 | 101.2985 | 122.1817 | -123.6877 | -123.3261
3323.9062 | 122.9507 | -93.8828 | 28.6697 | 0.233 | 0.0030164 | 0.0034544 | 0.0021917 | -0.0011258 | 0.0099613 | 0.0040525 | -93.132 | 29.0863 | -94.1483 | 28.7888 | 8.4732 | 0.009155 | 28.4958 | -4.9622 | 28.743 | -94.3359 | -0.2655 | 0.41656 | 0.75073 | 122.6715 | -20.1965 | -0.45319 | 0.073242 | 1.0162 | 122.3785 | 88.9206 | 102.356 | 122.9691 | 0.75073 | 122.6257 | 93.8919 | -0.45319 | 122.9691 | 0.75073 | 93.8919 | 102.356 | 122.6257 | -122.818 | -123.0057
3324.9062 | 122.8821 | -94.1391 | 28.5049 | 0.042267 | 0.004939 | 0.004736 | 0.0071051 | -0.00069859 | 0.0091067 | 0.0017027 | -93.5806 | 28.5461 | -94.6152 | 28.4958 | 8.3176 | -0.10986 | 28.8025 | -4.9667 | 28.6743 | -94.5053 | -0.47607 | 0.041199 | 0.55847 | 122.6349 | -20.1874 | -0.36621 | 0.16937 | 1.0345 | 122.9416 | 89.1724 | 102.4567 | 122.6852 | 0.55847 | 122.8134 | 94.0292 | -0.36621 | 122.6852 | 0.55847 | 94.0292 | 102.4567 | 122.8134 | -123.1201 | -123.0103
3325.9062 | 122.8592 | -94.2169 | 28.4271 | 0.042267 | 0.0051526 | 0.010717 | 0.0071051 | 0.00036961 | 0.0097475 | 0.0027707 | -93.1641 | 28.4958 | -94.3268 | 28.3813 | 8.2672 | -0.068665 | 28.2806 | -4.7928 | 28.3722 | -95.2789 | -0.10986 | 0.068665 | 1.0529 | 122.5983 | -20.1599 | -1.062 | -0.054932 | 1.1627 | 122.4976 | 89.4241 | 102.4841 | 122.7127 | 1.0529 | 122.5891 | 94.1483 | -1.062 | 122.7127 | 1.0529 | 94.1483 | 102.4841 | 122.5891 | -122.7539 | -123.7061
3326.9062 | 122.8363 | -93.8278 | 28.7933 | 0.057526 | 0.0068616 | 0.0068722 | 0.0056097 | 0.00079681 | 0.0095339 | 0.0034115 | -93.0954 | 28.6972 | -94.3176 | 28.7704 | 8.3725 | -0.15106 | 29.0634 | -4.6738 | 29.0039 | -94.1483 | -0.48981 | -0.09613 | 0.73242 | 122.5983 | -20.4208 | -0.32043 | 0.21057 | 1.2222 | 122.8912 | 89.1541 | 102.2003 | 122.525 | 0.73242 | 122.8317 | 93.6768 | -0.32043 | 122.525 | 0.73242 | 93.6768 | 102.2003 | 122.8317 | -123.111 | -122.9416
3327.9062 | 122.8821 | -94.0979 | 28.4912 | 0.065155 | 0.0017346 | 0.0079404 | 0.0053961 | -5.7592e-05 | 0.0086795 | 0.0031979 | -92.9764 | 28.9627 | -94.1757 | 28.8666 | 8.3633 | -0.018311 | 28.5461 | -4.8294 | 28.6835 | -94.4733 | -0.07782 | 0.4715 | 1.1215 | 122.9645 | -20.1279 | -0.37537 | 0.19226 | 1.1993 | 122.644 | 89.2685 | 102.4612 | 123.0606 | 1.1215 | 122.7814 | 94.0796 | -0.37537 | 123.0606 | 1.1215 | 94.0796 | 102.4612 | 122.7814 | -122.6669 | -122.9645
3328.9219 | 122.9279 | -93.956 | 28.6057 | 0.21774 | 0.0010938 | 0.003668 | -0.0016535 | -0.002194 | 0.0082523 | 0.0025571 | -93.0359 | 28.743 | -94.249 | 28.6423 | 8.3679 | 0.036621 | 28.3813 | -4.7104 | 28.6194 | -94.3451 | -0.29297 | 0.13733 | 0.92011 | 122.5983 | -20.2377 | -0.3891 | 0.013733 | 1.2131 | 122.3373 | 89.2456 | 102.3239 | 122.699 | 0.92011 | 122.5754 | 93.9926 | -0.3891 | 122.699 | 0.92011 | 93.9926 | 102.3239 | 122.5754 | -122.8546 | -122.9507
3329.9062 | 122.525 | -91.6168 | 33.5541 | 0.019379 | 0.004939 | 0.010077 | 0.0053961 | -0.0019802 | 0.010389 | 0.0027707 | -93.3334 | 28.8391 | -94.2902 | 28.9398 | 8.3542 | -0.11902 | 28.6652 | -4.7653 | 28.9124 | -94.249 | -2.6733 | -4.715 | -1.7166 | 120.5566 | -25.1999 | -2.6321 | -4.6417 | 0.95673 | 120.282 | 86.8515 | 99.971 | 120.4559 | -1.7166 | 120.5292 | 91.4978 | -2.6321 | 120.4559 | -1.7166 | 91.4978 | 99.971 | 120.5292 | -127.8442 | -127.803
3330.9062 | 122.8592 | -93.1229 | 29.2191 | 0.088043 | 0.0053662 | 0.0040952 | 0.0060369 | 0.001224 | 0.010602 | 0.00020726 | -93.1366 | 28.7979 | -95.2332 | 28.4317 | 8.2718 | -0.10986 | 28.6606 | -4.0054 | 28.9444 | -91.7496 | -2.1103 | -0.42114 | -0.013733 | 121.5546 | -20.9473 | 1.3733 | -0.27466 | 2.0966 | 121.7834 | 89.1174 | 101.3947 | 121.9208 | -0.013733 | 122.0673 | 93.013 | 1.3733 | 121.9208 | -0.013733 | 93.013 | 101.3947 | 122.0673 | -124.4522 | -120.9686
3331.9062 | 122.9462 | -93.8736 | 28.6926 | 0.37796 | 0.001521 | 0.001959 | -0.0005853 | -0.002194 | 0.0086795 | 0.0031979 | -92.8574 | 28.6285 | -94.2215 | 28.9124 | 8.4915 | 0.045776 | 28.3218 | -4.3671 | 28.7476 | -94.2902 | -0.3479 | -0.064087 | 1.0162 | 122.786 | -20.2011 | -0.41656 | 0.054932 | 1.3641 | 122.1954 | 89.5065 | 102.3651 | 122.5021 | 1.0162 | 122.6212 | 93.9194 | -0.41656 | 122.5021 | 1.0162 | 93.9194 | 102.3651 | 122.6212 | -122.9141 | -122.9828
3332.9062 | 122.818 | -93.3838 | 29.3015 | 0.049896 | 0.0077162 | 0.0085812 | 0.0062507 | -0.0017666 | 0.010389 | 0.0029843 | -93.0954 | 28.775 | -94.2261 | 28.9032 | 8.3817 | -0.11444 | 29.1595 | -4.3533 | 29.1733 | -93.8965 | -0.84229 | -0.52643 | 0.28839 | 122.287 | -20.9198 | -0.5127 | -0.12817 | 1.1307 | 122.5433 | 89.0305 | 101.7654 | 122.1588 | 0.28839 | 122.5571 | 93.2693 | -0.5127 | 122.1588 | 0.28839 | 93.2693 | 101.7654 | 122.5571 | -123.5275 | -123.1979
3333.9062 | 122.9187 | -93.3975 | 29.187 | 0.019379 | 0.002162 | 0.0015316 | -0.0012261 | -0.003903 | 0.010602 | 0.0040525 | -92.7704 | 29.361 | -93.7592 | 29.2648 | 8.5968 | -0.027466 | 28.9993 | -4.2206 | 29.2603 | -93.8049 | -0.36163 | 0.17395 | 0.62714 | 122.6624 | -20.5902 | -0.40741 | 0.073242 | 0.98877 | 122.3969 | 89.1769 | 101.9943 | 122.7585 | 0.62714 | 122.6578 | 93.3701 | -0.40741 | 122.7585 | 0.62714 | 93.3701 | 101.9943 | 122.6578 | -122.9462 | -122.9919
3334.9062 | 122.85 | -94.1437 | 28.5461 | 0.057526 | 0.0060072 | 0.0072996 | 0.010523 | -0.0026212 | 0.0091067 | 0.0025571 | -93.5669 | 28.5553 | -94.5831 | 28.1479 | 8.1161 | -0.068665 | 28.1845 | -4.7562 | 28.2578 | -94.78 | -0.43945 | 0.009155 | 0.57678 | 122.2916 | -20.43 | -0.63629 | -0.28839 | 1.0162 | 122.3282 | 89.3875 | 102.2598 | 122.699 | 0.57678 | 122.4014 | 94.075 | -0.63629 | 122.699 | 0.57678 | 94.075 | 102.2598 | 122.4014 | -123.1293 | -123.3261
3335.9062 | 122.8317 | -93.7729 | 28.775 | 0.088043 | 0.0040846 | 0.0038816 | 0.0075323 | -0.001553 | 0.0078249 | 0.0021299 | -92.6743 | 29.2145 | -93.8095 | 29.2465 | 8.3954 | -0.13733 | 28.7659 | -4.4998 | 29.0085 | -94.2032 | -0.036621 | 0.43945 | 1.0986 | 123.0194 | -20.3796 | -0.4303 | 0.23346 | 1.1353 | 122.5388 | 89.2731 | 102.1683 | 122.9874 | 1.0986 | 122.7814 | 93.6356 | -0.4303 | 122.9874 | 1.0986 | 93.6356 | 102.1683 | 122.7814 | -122.5845 | -122.9782
3336.9062 | 122.9324 | -91.3376 | 31.3797 | 0.21011 | 0.00023916 | 0.0083676 | -0.0001581 | -0.0024076 | 0.010175 | 0.0036253 | -92.6331 | 29.0909 | -93.8553 | 30.3864 | 8.9859 | 0.059509 | 30.6656 | -3.7445 | 30.5923 | -92.2028 | -2.5177 | -2.2888 | -1.2955 | 121.7239 | -22.3938 | -0.86517 | -0.78735 | 1.2222 | 122.0032 | 87.5931 | 100.3235 | 120.4285 | -1.2955 | 121.9299 | 91.3971 | -0.86517 | 120.4285 | -1.2955 | 91.3971 | 100.3235 | 121.9299 | -125.235 | -123.5825
3337.9062 | 122.8455 | -92.7567 | 29.9103 | 0.072784 | 0.0060072 | 0.011145 | 0.0075323 | -0.0019802 | 0.0082523 | 0.0040525 | -92.5003 | 29.2282 | -93.6584 | 29.9011 | 8.638 | -0.10986 | 30.0339 | -4.6417 | 29.9698 | -93.1458 | -0.90179 | -0.68207 | 0.25635 | 122.6578 | -21.2723 | -0.3891 | 0.05951 | 1.1581 | 122.7905 | 88.1149 | 101.3947 | 121.9849 | 0.25635 | 122.7264 | 92.6468 | -0.3891 | 121.9849 | 0.25635 | 92.6468 | 101.3947 | 122.7264 | -123.5687 | -123.056
3338.9062 | 149.9954 | -103.0426 | 20.8557 | -0.36972 | 0.0013074 | 0.0055906 | 0.0021917 | -0.0034756 | 0.0069705 | 0.0029843 | -101.5274 | 20.5032 | -102.6215 | 20.5078 | 6.0974 | 0.52643 | 20.4483 | -6.0471 | 20.549 | -102.6031 | 0.42114 | -0.35248 | 1.5152 | 123.5504 | -14.7583 | 0.43945 | -0.3067 | 1.0941 | 123.4909 | 96.9955 | 109.14 | 123.5458 | 1.5152 | 123.5916 | 103.569 | 0.43945 | 123.5458 | 1.5152 | 103.569 | 109.14 | 123.5916 | -123.4772 | -123.4589
3339.9062 | 122.8455 | -94.0887 | 28.1754 | 0.095673 | 0.0034436 | 0.011786 | 0.0075323 | -0.003262 | 0.0078249 | 0.0027707 | -93.5623 | 28.4363 | -94.6701 | 28.418 | 8.3176 | -0.068665 | 28.331 | -4.5181 | 28.5187 | -94.6106 | -0.58136 | 0.26093 | 0.52643 | 122.5067 | -19.8578 | -0.52185 | 0.34332 | 1.1078 | 122.4197 | 89.5706 | 102.4063 | 122.525 | 0.52643 | 122.6074 | 94.0201 | -0.52185 | 122.525 | 0.52643 | 94.0201 | 102.4063 | 122.6074 | -122.8455 | -122.7859
3340.9062 | 122.8638 | -94.4229 | 28.1204 | -0.0035098 | 0.0042982 | 0.0087948 | 0.0083869 | -0.0028348 | 0.0091067 | 0.0029843 | -93.7775 | 28.1158 | -94.9219 | 28.2806 | 8.2214 | -0.013733 | 28.1204 | -4.6143 | 28.2394 | -94.9356 | -0.49896 | -0.004577 | 0.64545 | 122.7036 | -19.899 | -0.5127 | 0.11902 | 1.1444 | 122.5433 | 89.8087 | 102.6443 | 122.5388 | 0.64545 | 122.6624 | 94.4092 | -0.5127 | 122.5388 | 0.64545 | 94.4092 | 102.6443 | 122.6624 | -123.0423 | -123.056
3341.9219 | 122.9828 | -93.988 | 28.5324 | 0.15671 | -0.00040164 | 0.0092222 | 0.0015509 | -0.0034756 | 0.0078249 | 0.0057615 | -93.3884 | 28.3493 | -94.7388 | 29.0222 | 8.5419 | 0.036621 | 28.1113 | -4.5319 | 28.569 | -94.4321 | -0.75073 | -0.18311 | 0.59967 | 123.0103 | -19.9905 | -0.44403 | 0.036621 | 1.3504 | 122.0993 | 89.4562 | 102.5299 | 122.3373 | 0.59967 | 122.5571 | 94.0247 | -0.44403 | 122.3373 | 0.59967 | 94.0247 | 102.5299 | 122.5571 | -123.2712 | -122.9645
3342.9062 | 122.818 | -94.5419 | 27.9327 | 0.1033 | 0.004939 | 0.0092222 | 0.0060369 | -0.0062528 | 0.0073977 | 0.0051205 | -93.6172 | 28.6835 | -94.6106 | 30.0797 | 8.6243 | -0.041199 | 27.9327 | -4.8889 | 28.5919 | -94.4183 | -0.068665 | 0.75073 | 0.92468 | 124.6216 | -19.3085 | 0.1236 | 0.65918 | 0.99335 | 122.4747 | 89.653 | 103.1662 | 123.2254 | 0.92468 | 123.1339 | 94.5007 | 0.1236 | 123.2254 | 0.92468 | 94.5007 | 103.1662 | 123.1339 | -122.5433 | -122.3511
3343.9062 | 122.8271 | -94.8303 | 27.7817 | 0.042267 | 0.004939 | 0.0077268 | 0.0073187 | -0.0024076 | 0.0078249 | 0.0053343 | -94.3359 | 27.7542 | -95.4483 | 27.6901 | 8.0109 | -0.009155 | 27.713 | -4.4907 | 27.7542 | -95.3796 | -0.61798 | -0.027466 | 0.49438 | 122.5204 | -19.7708 | -0.54932 | -0.027466 | 1.1124 | 122.5433 | 90.3397 | 102.8412 | 122.5845 | 0.49438 | 122.5845 | 94.8212 | -0.54932 | 122.5845 | 0.49438 | 94.8212 | 102.8412 | 122.5845 | -123.23 | -123.1613
3344.9062 | 122.85 | -98.8037 | 23.6618 | 0.11093 | 0.0072888 | 0.006445 | 0.0092413 | -0.003262 | 0.0093203 | 0.0014889 | -97.6913 | 24.0601 | -98.9182 | 24.559 | 6.8573 | 0.3891 | 23.4924 | -5.2368 | 24.0738 | -98.9594 | -0.11444 | 0.39825 | 1.1124 | 123.3627 | -16.8045 | -0.15564 | 0.41199 | 1.2268 | 122.2961 | 93.5669 | 105.661 | 122.8638 | 1.1124 | 122.8775 | 99.1928 | -0.15564 | 122.8638 | 1.1124 | 99.1928 | 105.661 | 122.8775 | -122.58 | -122.6212
3345.9062 | 122.8363 | -93.9331 | 28.2532 | 0.049896 | 0.0055798 | 0.004736 | 0.0075323 | 0.00079681 | 0.0093203 | 0.0034115 | -93.3701 | 28.5553 | -94.5007 | 28.569 | 8.3221 | -0.10529 | 28.7933 | -4.248 | 28.8803 | -94.0887 | -0.56763 | 0.30212 | 0.56305 | 122.5021 | -19.931 | -0.15564 | 0.62714 | 1.1307 | 122.7264 | 89.6851 | 102.2552 | 122.4884 | 0.56305 | 122.8134 | 93.8278 | -0.15564 | 122.4884 | 0.56305 | 93.8278 | 102.2552 | 122.8134 | -122.7539 | -122.3419
3346.9219 | 122.8912 | -94.0247 | 28.5553 | -0.21713 | -0.00082884 | 0.0043088 | -0.0037897 | -0.001553 | 0.0084659 | 0.0031979 | -93.4113 | 28.5049 | -94.5511 | 28.5004 | 8.3221 | -0.027466 | 28.4454 | -4.4724 | 28.5049 | -94.5145 | -0.52643 | -0.050354 | 0.6134 | 122.525 | -20.2332 | -0.48981 | -0.050354 | 1.1398 | 122.4701 | 89.5523 | 102.3468 | 122.5296 | 0.6134 | 122.5296 | 93.9972 | -0.48981 | 122.5296 | 0.6134 | 93.9972 | 102.3468 | 122.5296 | -123.1064 | -123.0698
3347.9062 | 122.8867 | -94.0292 | 28.418 | -0.041657 | 0.0053662 | 0.0062314 | 0.0077459 | -0.0017666 | 0.0093203 | 0.0040525 | -93.425 | 28.4134 | -94.5786 | 28.6057 | 8.2993 | -0.027466 | 28.3813 | -4.3945 | 28.5828 | -94.5007 | -0.54932 | -0.004578 | 0.60425 | 122.6349 | -20.1187 | -0.4715 | 0.1648 | 1.1536 | 122.4106 | 89.6347 | 102.3285 | 122.4426 | 0.60425 | 122.612 | 94.0018 | -0.4715 | 122.4426 | 0.60425 | 94.0018 | 102.3285 | 122.612 | -122.9965 | -122.9187
3348.9062 | 122.8592 | -93.6722 | 28.9124 | 0.28641 | 0.0042982 | 0.0075132 | 0.0028327 | -0.0024076 | 0.0091067 | 0.0049069 | -91.4658 | 29.3564 | -93.1549 | 28.9032 | 8.3313 | -0.068665 | 28.7521 | -4.4449 | 28.9581 | -94.1071 | 0.51727 | 0.44403 | 2.2064 | 122.5754 | -20.5811 | -0.43488 | 0.045776 | 1.6891 | 122.4243 | 89.2273 | 102.0035 | 123.0286 | 2.2064 | 122.6303 | 93.6035 | -0.43488 | 123.0286 | 2.2064 | 93.6035 | 102.0035 | 122.6303 | -122.0673 | -123.0194
3349.9062 | 122.7081 | -92.4912 | 29.9927 | 0.088043 | 0.0047254 | 0.0072996 | 0.0083869 | -0.0028348 | 0.0086795 | 0.0040525 | -93.0817 | 28.7521 | -94.281 | 28.9856 | 8.3862 | -0.18768 | 31.6177 | -3.8635 | 30.0385 | -90.3168 | -1.7899 | -1.2405 | -0.59051 | 121.4767 | -21.6064 | 2.1744 | 0.045776 | 1.1993 | 124.1089 | 88.6276 | 100.8774 | 121.2433 | -0.59051 | 122.5296 | 92.3035 | 2.1744 | 121.2433 | -0.59051 | 92.3035 | 100.8774 | 122.5296 | -124.2737 | -120.3094
3350.9062 | 122.9187 | -93.3517 | 29.274 | -0.24002 | 0.0053662 | 0.0032406 | 0.0049689 | 0.001224 | 0.0091067 | 0.0040525 | -92.9947 | 28.9124 | -94.1254 | 28.5324 | 8.2489 | -0.082397 | 28.5736 | -4.2801 | 28.6835 | -93.8461 | -0.77362 | -0.36163 | 0.35706 | 121.8842 | -21.0251 | -0.49438 | -0.59052 | 1.1307 | 121.9254 | 89.0717 | 101.6006 | 122.2641 | 0.35706 | 122.0352 | 93.2693 | -0.49438 | 122.2641 | 0.35706 | 93.2693 | 101.6006 | 122.0352 | -123.3994 | -123.1201
3351.9219 | 122.8271 | -94.1437 | 28.4271 | 0.027008 | 0.0030164 | 0.0079404 | 0.0068915 | -0.00048499 | 0.0099613 | 0.0046933 | -93.4067 | 28.4683 | -94.5328 | 28.4637 | 8.2031 | -0.059509 | 28.4775 | -4.4128 | 28.537 | -94.5694 | -0.3891 | 0.041199 | 0.737 | 122.6074 | -20.224 | -0.42572 | 0.10986 | 1.1261 | 122.6212 | 89.7308 | 102.3468 | 122.612 | 0.737 | 122.6807 | 94.0842 | -0.42572 | 122.612 | 0.737 | 94.0842 | 102.3468 | 122.6807 | -122.9599 | -122.9965
3352.9062 | 122.85 | -93.1 | 29.5258 | 0.21774 | 0.0051526 | 0.012213 | 5.5496e-05 | -0.002194 | 0.012311 | 0.0034115 | -92.308 | 29.4525 | -93.5806 | 29.2099 | 8.5236 | -0.11902 | 29.2465 | -4.5364 | 29.393 | -93.6859 | -0.48065 | -0.073242 | 0.79193 | 122.3099 | -21.0022 | -0.58594 | -0.13275 | 1.2726 | 122.3465 | 88.5635 | 101.6235 | 122.5525 | 0.79193 | 122.493 | 92.981 | -0.58594 | 122.5525 | 0.79193 | 92.981 | 101.6235 | 122.493 | -123.1064 | -123.2117
3353.9219 | 122.9233 | -94.1025 | 28.4454 | 0.20248 | 0.00066656 | 0.0025998 | -0.0037897 | -0.0030484 | 0.0093203 | 0.0046933 | -93.4387 | 28.3859 | -94.6472 | 28.6331 | 8.2901 | 0.027466 | 28.299 | -4.2023 | 28.4775 | -94.5282 | -0.54474 | -0.05951 | 0.66376 | 122.7356 | -20.1553 | -0.42572 | 0.032043 | 1.2085 | 122.4014 | 89.9002 | 102.3926 | 122.4884 | 0.66376 | 122.58 | 94.1299 | -0.42572 | 122.4884 | 0.66376 | 94.1299 | 102.3926 | 122.58 | -123.0927 | -122.9736
3354.9062 | 122.8775 | -93.7271 | 28.83 | -0.072174 | 0.0025892 | 0.0068722 | 0.0056097 | -0.0056118 | 0.0097475 | 0.0029843 | -93.0038 | 28.8437 | -94.1711 | 29.1367 | 8.3725 | -0.054932 | 28.8025 | -4.2297 | 28.9536 | -94.1849 | -0.44403 | 0.013733 | 0.72327 | 122.8638 | -20.4575 | -0.45776 | 0.1236 | 1.1673 | 122.5296 | 89.4974 | 102.0996 | 122.5708 | 0.72327 | 122.6807 | 93.6722 | -0.45776 | 122.5708 | 0.72327 | 93.6722 | 102.0996 | 122.6807 | -123.0011 | -123.0148
3355.9062 | 122.818 | -94.0933 | 28.5278 | 0.080414 | 0.0060072 | 0.0075132 | 0.0096685 | -0.00027139 | 0.0097475 | 0.0021299 | -93.3426 | 28.5233 | -94.5053 | 28.4775 | 8.2489 | -0.09613 | 28.4225 | -4.7058 | 28.6285 | -94.4687 | -0.41199 | -0.004578 | 0.75073 | 122.5708 | -20.2789 | -0.37537 | 0.10071 | 1.1627 | 122.5159 | 89.3875 | 102.3422 | 122.6166 | 0.75073 | 122.7219 | 93.9972 | -0.37537 | 122.6166 | 0.75073 | 93.9972 | 102.3422 | 122.7219 | -123.0331 | -122.9965
3356.9219 | 122.8683 | -93.8049 | 28.7292 | 0.1033 | 0.0038708 | 0.006445 | 0.0039007 | -0.0026212 | 0.010389 | 0.0034115 | -92.7795 | 29.2786 | -93.7775 | 29.2557 | 8.4045 | -0.28381 | 29.4708 | -5.4199 | 29.5624 | -93.8873 | 0.027466 | 0.54932 | 1.0254 | 123.0606 | -20.3247 | -0.082397 | 0.83313 | 0.99793 | 123.2758 | 88.385 | 102.2095 | 123.0835 | 1.0254 | 123.3673 | 93.5211 | -0.082397 | 123.0835 | 1.0254 | 93.5211 | 102.2095 | 123.3673 | -122.5067 | -122.6166
3357.9062 | 122.8867 | -93.924 | 28.6423 | 0.16434 | 0.006648 | 0.0070858 | 0.0036871 | -0.002194 | 0.0084659 | 0.0053343 | -93.1137 | 28.7888 | -94.2307 | 28.8803 | 8.3588 | -0.059509 | 28.5645 | -5.0354 | 28.7888 | -94.3726 | -0.3067 | 0.14648 | 0.81024 | 122.8043 | -20.2835 | -0.44861 | 0.14648 | 1.1169 | 122.4884 | 88.8886 | 102.2827 | 122.7127 | 0.81024 | 122.7127 | 93.8644 | -0.44861 | 122.7127 | 0.81024 | 93.8644 | 102.2827 | 122.7127 | -122.8729 | -123.0148
3358.9062 | 122.9233 | -93.4341 | 29.1321 | 0.21774 | 0.00323 | 0.0058042 | 0.0026191 | -0.00069859 | 0.010175 | 0.0036253 | -93.1778 | 28.6514 | -94.3726 | 29.0314 | 8.4412 | 0.050354 | 28.9856 | -4.3808 | 29.1229 | -93.9835 | -0.93842 | -0.48065 | 0.25635 | 122.4655 | -20.6909 | -0.54932 | -0.009155 | 1.1948 | 122.4197 | 89.0533 | 101.8753 | 122.0856 | 0.25635 | 122.5571 | 93.4845 | -0.54932 | 122.0856 | 0.25635 | 93.4845 | 101.8753 | 122.5571 | -123.5046 | -123.1155
3359.9062 | 122.8638 | -94.3634 | 28.2303 | 0.19485 | 0.0053662 | 0.0094358 | 0.0036871 | -0.0011258 | 0.0097475 | 0.0034115 | -93.2922 | 28.5782 | -94.4733 | 28.2669 | 8.1299 | -0.041199 | 28.1113 | -5.191 | 28.2532 | -94.8624 | -0.10986 | 0.3479 | 1.0712 | 122.6303 | -20.1004 | -0.49896 | 0.022888 | 1.181 | 122.4747 | 89.1724 | 102.4933 | 122.9416 | 1.0712 | 122.6166 | 94.3222 | -0.49896 | 122.9416 | 1.0712 | 94.3222 | 102.4933 | 122.6166 | -122.7036 | -123.0927
3360.9062 | 122.8867 | -94.1483 | 28.4225 | 0.21774 | 0.0055798 | 0.0085812 | 0.0036871 | -0.0017666 | 0.0086795 | 0.0023435 | -93.5257 | 28.3356 | -94.6884 | 28.5599 | 8.2581 | -0.032043 | 28.4134 | -4.2343 | 28.5553 | -94.6243 | -0.54016 | -0.086975 | 0.62256 | 122.7081 | -20.1645 | -0.47608 | 0.13275 | 1.1627 | 122.5616 | 89.9139 | 102.4063 | 122.4838 | 0.62256 | 122.7036 | 94.1162 | -0.47608 | 122.4838 | 0.62256 | 94.1162 | 102.4063 | 122.7036 | -123.111 | -123.0469
3361.9219 | 122.9233 | -94.0109 | 28.5233 | 0.20248 | 0.0040846 | 0.0062314 | 0.0036871 | -0.0030484 | 0.0091067 | 0.0049069 | -93.2144 | 28.6194 | -94.4458 | 28.8528 | 8.3405 | -0.022888 | 28.4546 | -4.3716 | 28.6423 | -94.4504 | -0.43488 | 0.096131 | 0.79651 | 122.8638 | -20.1828 | -0.43945 | 0.11902 | 1.2314 | 122.4655 | 89.6393 | 102.3514 | 122.6303 | 0.79651 | 122.6532 | 93.988 | -0.43945 | 122.6303 | 0.79651 | 93.988 | 102.3514 | 122.6532 | -122.9691 | -122.9736
3362.9062 | 122.8638 | -94.1574 | 28.4409 | 0.14908 | 0.0036572 | 0.0017454 | 0.0047553 | 0.00015601 | 0.0082523 | 0.0038389 | -93.3884 | 28.6743 | -94.4275 | 28.4958 | 8.2123 | -0.054932 | 28.3768 | -4.0558 | 28.5461 | -94.5328 | -0.27008 | 0.23346 | 0.76904 | 122.6532 | -20.2286 | -0.37537 | 0.10529 | 1.0391 | 122.5342 | 90.1016 | 102.3697 | 122.8317 | 0.76904 | 122.7036 | 94.1025 | -0.37537 | 122.8317 | 0.76904 | 94.1025 | 102.3697 | 122.7036 | -122.8683 | -122.9736
3363.9062 | 122.8317 | -94.0475 | 28.5782 | 0.1033 | 0.006648 | 0.0092222 | 0.0071051 | -0.00048499 | 0.0091067 | 0.0023435 | -93.4479 | 28.5141 | -94.5877 | 28.4912 | 8.194 | -0.10071 | 28.4317 | -4.1382 | 28.5416 | -94.574 | -0.54016 | -0.064087 | 0.59967 | 122.5388 | -20.3842 | -0.52643 | -0.036621 | 1.1398 | 122.4792 | 89.9094 | 102.2415 | 122.5616 | 0.59967 | 122.5891 | 93.9468 | -0.52643 | 122.5616 | 0.59967 | 93.9468 | 102.2415 | 122.5891 | -123.1659 | -123.1522
3364.9062 | 122.8363 | -94.0613 | 28.5187 | -0.55283 | 0.0085706 | 0.0070858 | 0.0062507 | -5.7592e-05 | 0.011029 | 0.00084806 | -93.2007 | 29.1412 | -93.9743 | 28.7888 | 8.2809 | -0.086975 | 28.6423 | -4.2526 | 28.7064 | -94.455 | 0.086975 | 0.62256 | 0.8606 | 122.85 | -20.2377 | -0.39368 | 0.18768 | 0.77362 | 122.7036 | 89.8087 | 102.3422 | 123.2025 | 0.8606 | 122.7676 | 93.9743 | -0.39368 | 123.2025 | 0.8606 | 93.9743 | 102.3422 | 122.7676 | -122.493 | -122.9736
3365.9062 | 122.8455 | -94.0109 | 28.5965 | 0.13382 | 0.0068616 | 0.003027 | 0.0051825 | -0.0013394 | 0.014234 | 0.0053343 | -92.8299 | 28.8116 | -94.194 | 28.5599 | 8.4641 | 0.07782 | 28.5233 | -4.129 | 28.7384 | -94.4321 | -0.18311 | 0.21515 | 1.181 | 122.5708 | -20.1324 | -0.42114 | 0.14191 | 1.3641 | 122.5342 | 89.8819 | 102.475 | 122.8226 | 1.181 | 122.7493 | 94.0887 | -0.42114 | 122.8226 | 1.181 | 94.0887 | 102.475 | 122.7493 | -122.7905 | -123.0286
3366.9219 | 122.8683 | -93.9468 | 28.6789 | -0.13321 | 0.0045118 | 0.008154 | 0.0015509 | -0.0030484 | 0.010602 | 0.0031979 | -93.2098 | 28.656 | -94.4229 | 28.7064 | 8.2214 | -0.050354 | 28.4821 | -4.0604 | 28.6697 | -94.3954 | -0.47607 | -0.022888 | 0.737 | 122.6532 | -20.4575 | -0.44861 | -0.009155 | 1.2131 | 122.4289 | 89.8865 | 102.1683 | 122.6028 | 0.737 | 122.6166 | 93.8965 | -0.44861 | 122.6028 | 0.737 | 93.8965 | 102.1683 | 122.6166 | -123.1018 | -123.0743
3367.9062 | 122.8683 | -93.5028 | 29.1595 | 0.049896 | 0.0055798 | 0.0038816 | 0.0077459 | -0.00069859 | 0.010175 | 0.0046933 | -93.0496 | 29.0039 | -94.0933 | 28.9536 | 8.3267 | -0.09613 | 28.9719 | -4.0604 | 29.0863 | -93.9789 | -0.59051 | -0.15564 | 0.45319 | 122.4564 | -20.8328 | -0.47607 | -0.073242 | 1.0437 | 122.4747 | 89.4424 | 101.8295 | 122.5067 | 0.45319 | 122.5891 | 93.4067 | -0.47607 | 122.5067 | 0.45319 | 93.4067 | 101.8295 | 122.5891 | -123.2529 | -123.1384
3368.9219 | 122.9507 | -94.1025 | 28.4637 | 0.13382 | 0.0023756 | 0.0055906 | -0.0010125 | -0.0019802 | 0.01167 | 0.0038389 | -93.2648 | 28.3356 | -94.574 | 28.9719 | 8.4 | 0.041199 | 28.4866 | -4.7562 | 28.7521 | -94.3817 | -0.4715 | -0.12817 | 0.83771 | 123.0743 | -20.0638 | -0.27924 | 0.28839 | 1.3092 | 122.5891 | 89.3463 | 102.5024 | 122.438 | 0.83771 | 122.8546 | 94.1437 | -0.27924 | 122.438 | 0.83771 | 94.1437 | 102.5024 | 122.8546 | -123.0377 | -122.8455
3369.9062 | 122.8592 | -93.8782 | 28.7659 | 0.13382 | 0.0053662 | 0.0045224 | 0.0068915 | -0.003262 | 0.011884 | 0.0042661 | -93.3746 | 28.5416 | -94.5557 | 28.6926 | 8.2306 | -0.064087 | 29.155 | -4.1794 | 28.8528 | -94.3085 | -0.67749 | -0.2243 | 0.50354 | 122.5708 | -20.5353 | -0.4303 | 0.086975 | 1.181 | 123.0331 | 89.6988 | 102.1088 | 122.4197 | 0.50354 | 122.731 | 93.8141 | -0.4303 | 122.4197 | 0.50354 | 93.8141 | 102.1088 | 122.731 | -123.3215 | -123.0743
3370.9062 | 122.9141 | -94.0063 | 28.7155 | 0.22537 | 0.0060072 | 0.0070858 | 0.0036871 | -0.0013394 | 0.0091067 | 0.0017027 | -93.1915 | 28.6652 | -94.3451 | 28.7476 | 8.3313 | -0.036621 | 28.5782 | -4.1061 | 28.7613 | -94.368 | -0.33875 | -0.050354 | 0.81482 | 122.7539 | -20.3842 | -0.36163 | 0.045777 | 1.1536 | 122.5845 | 89.9002 | 102.3376 | 122.6715 | 0.81482 | 122.7676 | 93.9697 | -0.36163 | 122.6715 | 0.81482 | 93.9697 | 102.3376 | 122.7676 | -123.0606 | -123.0835
3371.9219 | 122.9965 | -94.0018 | 28.4866 | 0.61447 | 0.00066656 | 0.0045224 | -0.0010125 | -0.0034756 | 0.0084659 | 0.0017027 | -92.9764 | 28.4866 | -94.4 | 28.9032 | 8.4549 | 0.054932 | 28.4454 | -4.9667 | 28.688 | -94.3954 | -0.39825 | 0 | 1.0254 | 122.905 | -20.0317 | -0.39368 | 0.20142 | 1.4236 | 122.4472 | 89.035 | 102.4567 | 122.4884 | 1.0254 | 122.6898 | 94.0567 | -0.39368 | 122.4884 | 1.0254 | 94.0567 | 102.4567 | 122.6898 | -122.8867 | -122.8821
3372.9062 | 122.9004 | -94.2673 | 28.418 | -0.18662 | 0.0062208 | 0.0075132 | 0.0092413 | -0.0028348 | 0.0099613 | 0.0031979 | -93.4204 | 28.4134 | -94.6518 | 28.2349 | 8.1848 | -0.009155 | 28.1525 | -4.2709 | 28.2532 | -94.7662 | -0.38452 | -0.004578 | 0.84686 | 122.5021 | -20.2332 | -0.49896 | -0.16479 | 1.2314 | 122.4197 | 89.9963 | 102.4521 | 122.6807 | 0.84686 | 122.5204 | 94.2581 | -0.49896 | 122.6807 | 0.84686 | 94.2581 | 102.4521 | 122.5204 | -123.0698 | -123.1842
3373.9062 | 122.9645 | -92.6056 | 30.0613 | 0.28641 | 0.0042982 | 0.0049496 | 0.0064643 | -0.0013394 | 0.0084659 | 0.0036253 | -92.363 | 29.5166 | -93.6859 | 29.512 | 8.5464 | -0.082397 | 29.425 | -3.7399 | 29.5486 | -93.1778 | -1.0803 | -0.54474 | 0.24262 | 122.1176 | -21.5149 | -0.5722 | -0.5127 | 1.3229 | 122.0306 | 88.8657 | 101.152 | 122.1222 | 0.24262 | 122.1542 | 92.5232 | -0.5722 | 122.1222 | 0.24262 | 92.5232 | 101.152 | 122.1542 | -123.7473 | -123.2391
3374.9219 | 122.9187 | -93.6722 | 28.9673 | -0.4155 | 0.0042982 | 0.011145 | 0.0071051 | -0.0019802 | 0.0078249 | 0.0019163 | -93.0222 | 28.9215 | -94.2123 | 29.1367 | 8.4549 | -0.086975 | 28.9581 | -4.5593 | 29.0771 | -94.1208 | -0.54016 | -0.045776 | 0.65002 | 122.8088 | -20.5124 | -0.44861 | 0.10986 | 1.1902 | 122.6303 | 89.1129 | 102.1271 | 122.5937 | 0.65002 | 122.7493 | 93.5852 | -0.44861 | 122.5937 | 0.65002 | 93.5852 | 102.1271 | 122.7493 | -123.1796 | -123.0881
3375.9062 | 122.8683 | -93.5715 | 29.0955 | 0.049896 | 0.0040846 | 0.003027 | -0.0001581 | -0.004971 | 0.0088931 | 0.0046933 | -92.688 | 29.2511 | -93.8782 | 29.8737 | 8.551 | -0.12817 | 29.0359 | -4.0878 | 29.4479 | -93.9194 | -0.3067 | 0.15564 | 0.88348 | 123.4451 | -20.5444 | -0.3479 | 0.35248 | 1.1902 | 122.6074 | 89.4836 | 102.1225 | 122.8226 | 0.88348 | 123.0194 | 93.4433 | -0.3479 | 122.8226 | 0.88348 | 93.4433 | 102.1225 | 123.0194 | -122.9736 | -123.0148
3376.9219 | 122.9233 | -93.6401 | 28.9215 | 0.21011 | 0.0038708 | 0.0070858 | 0.0039007 | -0.0028348 | 0.0099613 | 0.0038389 | -92.926 | 28.8345 | -94.1757 | 29.7226 | 8.5831 | -0.068665 | 28.6926 | -4.1428 | 29.2328 | -94.0018 | -0.53558 | -0.086975 | 0.71411 | 123.3627 | -20.3384 | -0.36163 | 0.31128 | 1.2497 | 122.3328 | 89.4974 | 102.2232 | 122.4747 | 0.71411 | 122.8729 | 93.5715 | -0.36163 | 122.4747 | 0.71411 | 93.5715 | 102.2232 | 122.8729 | -123.0972 | -122.9233
3377.9219 | 122.9095 | -93.9468 | 28.6057 | 0.057526 | 0.00066656 | -0.00039102 | -0.0031489 | -0.0028348 | 0.0088931 | 0.0036253 | -93.1732 | 28.7888 | -94.2307 | 29.0726 | 8.345 | -0.050354 | 28.8025 | -4.2526 | 28.7933 | -94.3542 | -0.28381 | 0.18311 | 0.77362 | 123.0194 | -20.2606 | -0.40741 | 0.18768 | 1.0574 | 122.7493 | 89.6942 | 102.2919 | 122.7356 | 0.77362 | 122.7402 | 93.8965 | -0.40741 | 122.7356 | 0.77362 | 93.8965 | 102.2919 | 122.7402 | -122.8363 | -122.9599
3378.9062 | 122.85 | -93.2236 | 29.3884 | -0.026398 | 0.0045118 | 0.0068722 | 0.0058233 | -0.0034756 | 0.0093203 | 0.0019163 | -92.8207 | 28.949 | -94.1254 | 29.0176 | 8.4824 | -0.13733 | 29.6539 | -4.1473 | 29.3976 | -93.8278 | -0.90179 | -0.43945 | 0.40283 | 122.2412 | -20.9061 | -0.60425 | 0.009155 | 1.3046 | 122.8775 | 89.0762 | 101.7059 | 122.1725 | 0.40283 | 122.6212 | 93.0862 | -0.60425 | 122.1725 | 0.40283 | 93.0862 | 101.7059 | 122.6212 | -123.5138 | -123.2162
3379.9219 | 122.8088 | -91.4841 | 31.2012 | 0.14145 | 0.0051526 | 0.004736 | 0.0079595 | -0.0011258 | 0.011029 | 0.0038389 | -90.9119 | 31.2561 | -91.6397 | 30.3314 | 8.5922 | -0.17395 | 31.1508 | -3.4103 | 30.9769 | -91.9922 | -0.15564 | 0.054932 | 0.5722 | 121.8155 | -22.6089 | -0.50812 | -0.2243 | 0.72784 | 122.6349 | 88.0737 | 100.0763 | 122.7402 | 0.5722 | 122.4609 | 91.3101 | -0.50812 | 122.7402 | 0.5722 | 91.3101 | 100.0763 | 122.4609 | -122.8409 | -123.1934
3380.9062 | 122.9004 | -93.6951 | 29.0085 | -0.17899 | 0.00323 | 0.0045224 | 0.0047553 | -0.00069859 | 0.0086795 | 0.0019163 | -93.045 | 28.8391 | -94.1574 | 28.6194 | 8.2764 | -0.086975 | 28.8483 | -4.1702 | 28.7933 | -94.249 | -0.46234 | -0.16937 | 0.65002 | 122.3145 | -20.7321 | -0.55389 | -0.21515 | 1.1124 | 122.5433 | 89.5248 | 101.9714 | 122.5342 | 0.65002 | 122.4884 | 93.6081 | -0.55389 | 122.5342 | 0.65002 | 93.6081 | 101.9714 | 122.4884 | -123.1659 | -123.2574
3381.9062 | 122.9233 | -94.0887 | 28.4729 | -0.16373 | 0.0047254 | 0.0085812 | 0.0066779 | -0.00027139 | 0.0091067 | 0.0036253 | -92.3401 | 32.1167 | -92.4179 | 28.5828 | 8.226 | -0.022888 | 28.2623 | -4.184 | 28.418 | -94.6014 | 1.6708 | 3.6438 | 1.7487 | 122.6715 | -20.2469 | -0.51269 | -0.054931 | 0.07782 | 122.3511 | 89.9048 | 102.3148 | 126.2054 | 1.7487 | 122.5067 | 94.0659 | -0.51269 | 126.2054 | 1.7487 | 94.0659 | 102.3148 | 122.5067 | -120.8908 | -123.0743
3382.9219 | 122.9095 | -90.5685 | 31.1005 | 0.072784 | 0.00066656 | 0.0060178 | -0.0016535 | -0.0045438 | 0.010602 | 0.0017027 | -92.6743 | 28.8437 | -93.8049 | 29.0405 | 8.2764 | -2.9572 | 45.6345 | -8.7204 | 37.1658 | -88.0875 | -3.2364 | -2.2568 | -2.1057 | 119.6091 | -22.8241 | 2.4811 | 6.0654 | 1.1307 | 136.203 | 81.8481 | 98.8449 | 119.4122 | -2.1057 | 127.7344 | 87.6114 | 2.4811 | 119.4122 | -2.1057 | 87.6114 | 98.8449 | 127.7344 | -124.9054 | -119.1879
3383.9062 | 122.9095 | -94.5465 | 28.0884 | -0.17136 | 0.0025892 | 0.0090086 | 0.0060369 | -0.0019802 | 0.01167 | 0.0034115 | -93.2556 | 28.2303 | -94.6152 | 28.2761 | 8.139 | -0.013733 | 27.9694 | -4.2755 | 28.2074 | -94.9722 | -0.068664 | 0.14191 | 1.2909 | 122.8226 | -19.9493 | -0.42572 | 0.11902 | 1.3596 | 122.5159 | 90.271 | 102.6855 | 122.7768 | 1.2909 | 122.7539 | 94.5328 | -0.42572 | 122.7768 | 1.2909 | 94.5328 | 102.6855 | 122.7539 | -122.7036 | -123.0606
3384.9062 | 122.905 | -93.9148 | 28.6697 | -0.22476 | 0.0019482 | 0.0040952 | 0.0060369 | -0.001553 | 0.0088931 | 0.0029843 | -93.1183 | 28.7247 | -94.3085 | 28.8895 | 8.2581 | -0.054932 | 28.8025 | -4.0604 | 28.8345 | -94.3039 | -0.39368 | 0.054931 | 0.79651 | 122.8043 | -20.4117 | -0.3891 | 0.1648 | 1.1902 | 122.7173 | 89.8544 | 102.1729 | 122.6395 | 0.79651 | 122.7493 | 93.8599 | -0.3891 | 122.6395 | 0.79651 | 93.8599 | 102.1729 | 122.7493 | -122.9782 | -122.9736
3385.9219 | 122.9599 | -93.2693 | 29.2923 | 0.17197 | 0.0023756 | 0.006445 | 0.0045417 | -0.00069859 | 0.0091067 | 0.0038389 | -92.7429 | 28.9719 | -93.9651 | 29.2648 | 8.3771 | -0.004578 | 28.9719 | -3.9185 | 29.1229 | -93.8187 | -0.6958 | -0.32043 | 0.52643 | 122.5342 | -20.9152 | -0.54932 | -0.16937 | 1.2222 | 122.2412 | 89.3509 | 101.6464 | 122.2412 | 0.52643 | 122.3923 | 93.2648 | -0.54932 | 122.2412 | 0.52643 | 93.2648 | 101.6464 | 122.3923 | -123.2574 | -123.111
3386.9062 | 92.6468 | -11.0092 | 69.9554 | 0.011749 | 0.0068616 | 0.0028134 | 0.0075323 | -0.0030484 | 0.037732 | 0.053827 | -22.8653 | 99.3484 | -23.8083 | 99.6643 | 24.7559 | -6.0699 | 98.877 | 7.045 | 99.2569 | -23.8358 | -12.7991 | 29.393 | -11.8561 | 110.6735 | -45.1996 | -12.8265 | 29.3015 | 0.94299 | 109.8862 | 18.0542 | 35.7651 | 110.3577 | -11.8561 | 110.2661 | 4.9393 | -12.8265 | 110.3577 | -11.8561 | 4.9393 | 35.7651 | 110.2661 | -93.7637 | -93.7912
3387.9219 | 122.2092 | -5.191 | 112.6923 | 0.21774 | 0.0028028 | 0.0043088 | 0.0060369 | 0.00036961 | 0.050977 | 0.070916 | -4.628 | 117.5171 | -5.6259 | 117.746 | 22.9935 | -2.3575 | 116.9312 | 9.7046 | 117.4484 | -5.6122 | -0.43488 | 4.8248 | 0.56305 | 122.937 | -89.6988 | -0.42114 | 4.7562 | 0.99793 | 122.1222 | 14.8956 | 28.1845 | 122.7081 | 0.56305 | 122.6395 | 2.8336 | -0.42114 | 122.7081 | 0.56305 | 2.8336 | 28.1845 | 122.6395 | -118.3182 | -118.3044
3388.9219 | 122.3465 | -6.8985 | 112.9715 | 0.19485 | 0.0045118 | 0.0075132 | 0.0056097 | -0.0036892 | 0.049909 | 0.06878 | -6.3766 | 115.8005 | -7.3059 | 115.9515 | 21.1304 | -3.0899 | 115.4755 | 9.494 | 115.7181 | -7.3334 | -0.40741 | 2.829 | 0.52185 | 122.85 | -91.8411 | -0.43487 | 2.7466 | 0.92926 | 122.374 | 16.3925 | 28.0289 | 122.699 | 0.52185 | 122.6166 | 3.8086 | -0.43487 | 122.699 | 0.52185 | 3.8086 | 28.0289 | 122.6166 | -120.2774 | -120.3049
3389.9062 | 105.2948 | -7.196 | 88.1836 | -0.18662 | 0.0040846 | 0.001959 | 0.011377 | -0.0034756 | 0.050122 | 0.067498 | -6.308 | 115.9607 | -7.2739 | 116.0385 | 20.6772 | -3.1448 | 115.5624 | 9.6085 | 115.86 | -7.2556 | -0.07782 | 27.7771 | 0.88806 | 123.2346 | -67.5064 | -0.059509 | 27.6764 | 0.96588 | 122.7585 | 16.8045 | 27.8732 | 123.1567 | 0.88806 | 123.056 | 4.0512 | -0.059509 | 123.1567 | 0.88806 | 4.0512 | 27.8732 | 123.056 | -95.4575 | -95.4391
3390.9062 | 104.1229 | -7.164 | 111.0123 | 1.179 | 0.0060072 | 0.006445 | 0.0086005 | -0.0034756 | 0.050122 | 0.068994 | -6.3171 | 116.0248 | -7.2327 | 116.011 | 20.2286 | -3.067 | 115.535 | 9.137 | 115.8829 | -7.2556 | -0.068665 | 5.0125 | 0.84686 | 123.175 | -90.7837 | -0.091553 | 4.8706 | 0.91553 | 122.699 | 16.301 | 27.3926 | 123.1888 | 0.84686 | 123.0469 | 4.097 | -0.091553 | 123.1888 | 0.84686 | 4.097 | 27.3926 | 123.0469 | -118.2449 | -118.2678
3391.9062 | 104.6677 | -7.2372 | 115.5441 | 0.011749 | 0.0051526 | 0.003668 | 0.0096685 | -0.0026212 | 0.050336 | 0.070276 | -6.4362 | 115.8417 | -7.3883 | 115.86 | 19.8349 | -3.0899 | 115.416 | 9.256 | 115.7272 | -7.3837 | -0.15106 | 0.29755 | 0.80109 | 123.0972 | -95.7092 | -0.14648 | 0.18311 | 0.95215 | 122.6532 | 16.4932 | 27.0721 | 123.0789 | 0.80109 | 122.9645 | 4.1473 | -0.14648 | 123.0789 | 0.80109 | 4.1473 | 27.0721 | 122.9645 | -122.9324 | -122.9279
3392.9219 | 122.6028 | -5.3558 | 117.1051 | 0.17197 | 0.0045118 | 0.0051632 | 0.0032599 | -0.001553 | 0.052259 | 0.07113 | -4.6875 | 117.4988 | -5.658 | 117.5903 | 19.9173 | -2.1469 | 116.9678 | 9.1736 | 117.4072 | -5.6671 | -0.30212 | 0.39368 | 0.66833 | 122.9462 | -97.1878 | -0.31128 | 0.30212 | 0.97046 | 122.3236 | 14.5294 | 25.2731 | 122.8546 | 0.66833 | 122.7631 | 3.2089 | -0.31128 | 122.8546 | 0.66833 | 3.2089 | 25.2731 | 122.7631 | -122.7631 | -122.7722
3393.9062 | 110.7605 | -5.3925 | 110.5591 | 0.042267 | 0.0062208 | 0.0066586 | 0.0092413 | -0.00069859 | 0.051831 | 0.070062 | -4.6417 | 117.6727 | -5.5893 | 117.6682 | 19.5328 | -2.2339 | 117.2745 | 8.8577 | 117.5674 | -5.5481 | -0.19684 | 7.1136 | 0.75073 | 123.0606 | -91.0263 | -0.15564 | 7.0084 | 0.94757 | 122.6669 | 14.2502 | 24.9252 | 123.0652 | 0.75073 | 122.9599 | 3.1586 | -0.15564 | 123.0652 | 0.75073 | 3.1586 | 24.9252 | 122.9599 | -116.1484 | -116.1072
3394.9219 | 122.8363 | -4.9301 | 117.041 | 0.15671 | 0.0036572 | 0.005377 | 0.0049689 | -0.0011258 | 0.051191 | 0.073266 | -4.2984 | 117.8375 | -5.2414 | 118.0115 | 19.4778 | -1.7166 | 117.4255 | 8.6472 | 117.8055 | -5.2185 | -0.31128 | 0.79651 | 0.63171 | 122.9416 | -97.5632 | -0.28839 | 0.76447 | 0.94299 | 122.3557 | 13.5773 | 24.408 | 122.7676 | 0.63171 | 122.7356 | 3.2135 | -0.28839 | 122.7676 | 0.63171 | 3.2135 | 24.408 | 122.7356 | -122.2824 | -122.2595
3395.9062 | 122.4564 | -4.8614 | 118.071 | -0.24765 | 0.0053662 | -0.00017722 | 0.0071051 | -0.0064664 | 0.051618 | 0.072198 | -4.2252 | 118.0847 | -5.1819 | 118.0756 | 19.2215 | -1.4236 | 117.7643 | 8.3679 | 117.9794 | -5.1498 | -0.32044 | 0.013733 | 0.63629 | 122.937 | -98.8495 | -0.28839 | -0.091553 | 0.95673 | 122.6257 | 13.2294 | 24.0829 | 122.9462 | 0.63629 | 122.8409 | 3.4378 | -0.28839 | 122.9462 | 0.63629 | 3.4378 | 24.0829 | 122.8409 | -123.2529 | -123.2208
3396.9062 | 113.8458 | -4.8752 | 117.7551 | -0.23239 | 0.0047254 | 0.0021726 | 0.0081733 | -0.003903 | 0.049695 | 0.070062 | -4.129 | 118.1671 | -5.0858 | 118.2037 | 19.1025 | -1.5198 | 117.7826 | 8.2352 | 118.0618 | -5.0629 | -0.21057 | 0.41199 | 0.74615 | 123.0789 | -98.6526 | -0.18768 | 0.3067 | 0.95673 | 122.6578 | 13.1104 | 23.9777 | 123.0423 | 0.74615 | 122.937 | 3.3554 | -0.18768 | 123.0423 | 0.74615 | 3.3554 | 23.9777 | 122.937 | -122.8409 | -122.818
3397.9062 | 109.9411 | -4.6967 | 118.0344 | 0.042267 | 0.0070752 | 0.0079404 | 0.010309 | -0.0041166 | 0.052259 | 0.070916 | -3.9047 | 118.3731 | -4.8614 | 118.3731 | 18.9606 | -1.8723 | 117.984 | 8.4137 | 118.2861 | -4.8431 | -0.16479 | 0.33875 | 0.79193 | 123.0698 | -99.0738 | -0.14649 | 0.25177 | 0.95673 | 122.6807 | 13.1104 | 23.6572 | 123.0698 | 0.79193 | 122.9828 | 2.8244 | -0.14649 | 123.0698 | 0.79193 | 2.8244 | 23.6572 | 122.9828 | -122.8958 | -122.8775
3398.9062 | 122.3602 | -4.6829 | 117.3431 | -0.11032 | 0.0064344 | -0.00017722 | 0.0077459 | -0.0030484 | 0.052472 | 0.072839 | -4.0833 | 118.1671 | -5.072 | 118.2175 | 18.8507 | -1.3458 | 117.7322 | 8.2718 | 118.0344 | -5.072 | -0.3891 | 0.82397 | 0.59967 | 122.9004 | -98.4924 | -0.3891 | 0.69122 | 0.98877 | 122.4152 | 12.9547 | 23.5336 | 122.85 | 0.59967 | 122.7173 | 3.3371 | -0.3891 | 122.85 | 0.59967 | 3.3371 | 23.5336 | 122.7173 | -122.4152 | -122.4152
3399.9062 | 122.1909 | -10.2905 | 112.2803 | -0.12558 | 0.0042982 | 0.0060178 | 0.011164 | -0.0013394 | 0.050977 | 0.067926 | -9.7 | 112.6007 | -10.6155 | 112.6648 | 18.1503 | -4.4357 | 112.1979 | 7.8827 | 112.4863 | -10.5698 | -0.32501 | 0.32044 | 0.59052 | 122.9553 | -94.1299 | -0.27924 | 0.20599 | 0.91553 | 122.4884 | 18.1732 | 28.4409 | 122.8912 | 0.59052 | 122.7768 | 5.8548 | -0.27924 | 122.8912 | 0.59052 | 5.8548 | 28.4409 | 122.7768 | -122.8958 | -122.85
3400.9062 | 116.153 | -5.5481 | 117.2653 | 0.13382 | 0.0068616 | 0.006445 | 0.0092413 | -0.0019802 | 0.052259 | 0.072625 | -4.9255 | 117.421 | -5.8548 | 117.3615 | 18.5852 | -2.4033 | 117.0502 | 8.1116 | 117.3294 | -5.8182 | -0.3067 | 0.15564 | 0.62256 | 122.9095 | -98.6801 | -0.27008 | 0.064087 | 0.92926 | 122.5983 | 13.6597 | 24.1333 | 122.9691 | 0.62256 | 122.8775 | 3.1448 | -0.27008 | 122.9691 | 0.62256 | 3.1448 | 24.1333 | 122.8775 | -123.1201 | -123.0835
3401.9062 | 109.8953 | -6.4911 | 115.9287 | 0.034637 | 0.004939 | 0.0062314 | 0.010096 | -0.00048499 | 0.051831 | 0.07113 | -5.8044 | 116.4825 | -6.7474 | 116.51 | 18.3563 | -2.774 | 116.1072 | 8.0887 | 116.4093 | -6.7108 | -0.25635 | 0.55389 | 0.68665 | 123.0011 | -97.5723 | -0.21973 | 0.48065 | 0.94299 | 122.5983 | 14.5798 | 24.8474 | 122.9736 | 0.68665 | 122.9004 | 3.717 | -0.21973 | 122.9736 | 0.68665 | 3.717 | 24.8474 | 122.9004 | -122.6761 | -122.6395
3402.9062 | 122.0764 | -6.2622 | 116.0065 | -0.20187 | 0.0055798 | 3.6382e-05 | 0.0047553 | -0.001553 | 0.053113 | 0.072198 | -5.5939 | 116.716 | -6.514 | 116.716 | 18.2785 | -1.6937 | 116.3864 | 7.9514 | 116.6245 | -6.5231 | -0.25177 | 0.70953 | 0.66833 | 122.9782 | -97.728 | -0.26093 | 0.61798 | 0.9201 | 122.6486 | 14.2136 | 24.5407 | 122.9782 | 0.66833 | 122.8867 | 4.5685 | -0.26093 | 122.9782 | 0.66833 | 4.5685 | 24.5407 | 122.8867 | -122.5204 | -122.5296
3403.9219 | 122.7539 | -5.3146 | 116.8396 | 0.18723 | 0.0051526 | 0.004736 | 0.0045417 | 0.00058321 | 0.051404 | 0.070489 | -4.6783 | 117.5583 | -5.6351 | 117.627 | 18.2968 | -1.4969 | 117.1417 | 7.5714 | 117.4988 | -5.5893 | -0.32043 | 0.71869 | 0.63629 | 122.9416 | -98.5428 | -0.27466 | 0.65918 | 0.95673 | 122.4564 | 12.886 | 23.6115 | 122.8729 | 0.63629 | 122.8134 | 3.8177 | -0.27466 | 122.8729 | 0.63629 | 3.8177 | 23.6115 | 122.8134 | -122.4747 | -122.4289
3404.9062 | 122.5525 | -5.127 | 111.763 | -0.018768 | 0.006648 | 0.0045224 | 0.0079595 | -0.0026212 | 0.051618 | 0.07113 | -4.3488 | 117.8375 | -5.4245 | 117.8513 | 18.2465 | -1.8906 | 117.3843 | 7.782 | 117.7231 | -5.4016 | -0.29755 | 6.0745 | 0.7782 | 122.9782 | -93.5165 | -0.27466 | 5.9601 | 1.0757 | 122.5113 | 12.9089 | 23.3734 | 122.9645 | 0.7782 | 122.85 | 3.2364 | -0.27466 | 122.9645 | 0.7782 | 3.2364 | 23.3734 | 122.85 | -117.1875 | -117.1646
3405.9062 | 116.3086 | -5.2185 | 117.2333 | -0.0035098 | 0.0062208 | 0.0055906 | 0.0075323 | -0.0017666 | 0.0529 | 0.073693 | -4.5181 | 117.7322 | -5.5161 | 117.7414 | 18.0634 | -1.7441 | 117.3019 | 7.2098 | 117.6407 | -5.4977 | -0.29755 | 0.49896 | 0.70038 | 122.9599 | -99.1699 | -0.27924 | 0.40741 | 0.99793 | 122.5204 | 12.4283 | 23.2819 | 122.9507 | 0.70038 | 122.8592 | 3.4744 | -0.27924 | 122.9507 | 0.70038 | 3.4744 | 23.2819 | 122.8592 | -122.7493 | -122.731
3406.9219 | 122.6166 | -5.0217 | 117.5949 | 0.24826 | 0.0053662 | 0.0043088 | 0.0043281 | -0.00091219 | 0.050763 | 0.072412 | -4.3488 | 117.8101 | -5.3238 | 117.9428 | 18.0908 | -1.4465 | 117.3065 | 7.489 | 117.7551 | -5.3192 | -0.30213 | 0.21515 | 0.67291 | 122.9645 | -99.5041 | -0.29755 | 0.16022 | 0.97504 | 122.3282 | 12.5107 | 23.1125 | 122.8317 | 0.67291 | 122.7768 | 3.5751 | -0.29755 | 122.8317 | 0.67291 | 3.5751 | 23.1125 | 122.7768 | -122.9187 | -122.9141
3407.9062 | 122.2916 | -4.8065 | 117.7551 | -0.018768 | 0.0047254 | 0.0060178 | 0.0086005 | -0.0024076 | 0.052686 | 0.073693 | -4.1977 | 118.0115 | -5.2139 | 118.0847 | 17.9947 | -1.6754 | 117.6773 | 7.2052 | 118.0389 | -5.1224 | -0.40741 | 0.25635 | 0.60883 | 122.8912 | -99.7604 | -0.31586 | 0.28381 | 1.0162 | 122.4838 | 12.0117 | 22.8012 | 122.818 | 0.60883 | 122.8455 | 3.1311 | -0.31586 | 122.818 | 0.60883 | 3.1311 | 22.8012 | 122.8455 | -122.9691 | -122.8775
3408.9062 | 122.4655 | -4.8203 | 118.0298 | -0.056915 | 0.0053662 | 0.005377 | 0.0071051 | -0.00069859 | 0.05354 | 0.072625 | -4.097 | 118.1305 | -5.1178 | 118.1534 | 17.8757 | -1.8402 | 117.7048 | 7.6355 | 118.0389 | -5.0903 | -0.29755 | 0.10071 | 0.72327 | 122.9736 | -100.1541 | -0.27008 | 0.009155 | 1.0208 | 122.525 | 12.4557 | 22.6959 | 122.9507 | 0.72327 | 122.8592 | 2.98 | -0.27008 | 122.9507 | 0.72327 | 2.98 | 22.6959 | 122.8592 | -123.1476 | -123.1201
3409.9219 | 122.9645 | -4.8477 | 117.7689 | 0.24826 | 0.0034436 | 0.0070858 | 0.0026191 | -0.0017666 | 0.053754 | 0.073266 | -4.3533 | 117.8833 | -5.2277 | 118.1305 | 17.8986 | -1.3092 | 117.4713 | 7.6218 | 117.9153 | -5.1407 | -0.37994 | 0.11444 | 0.49438 | 122.9782 | -99.8703 | -0.29297 | 0.14648 | 0.87433 | 122.319 | 12.4695 | 22.7463 | 122.731 | 0.49438 | 122.7631 | 3.5385 | -0.29297 | 122.731 | 0.49438 | 3.5385 | 22.7463 | 122.7631 | -122.9965 | -122.9095
3410.9062 | 122.2229 | -5.0262 | 116.9998 | -0.19424 | 0.0055798 | 0.0043088 | 0.0086005 | -0.002194 | 0.052472 | 0.072412 | -4.2892 | 117.9611 | -5.2689 | 117.9977 | 17.7475 | -1.3321 | 117.5446 | 7.0587 | 117.8741 | -5.2643 | -0.24261 | 0.9613 | 0.737 | 123.024 | -99.2523 | -0.23804 | 0.87433 | 0.97961 | 122.5708 | 12.085 | 22.7737 | 122.9874 | 0.737 | 122.9004 | 3.6942 | -0.23804 | 122.9874 | 0.737 | 3.6942 | 22.7737 | 122.9004 | -122.2687 | -122.2641
3411.9062 | 122.493 | -4.747 | 118.0573 | 0.17197 | 0.0053662 | 0.0043088 | 0.0064643 | -0.0019802 | 0.050977 | 0.074975 | -4.1016 | 118.158 | -5.0674 | 118.1717 | 17.6697 | -1.4008 | 117.7734 | 7.3288 | 118.0939 | -5.0125 | -0.32043 | 0.10071 | 0.64545 | 122.9187 | -100.3876 | -0.2655 | 0.036621 | 0.96588 | 122.5204 | 12.0758 | 22.4167 | 122.905 | 0.64545 | 122.8409 | 3.3463 | -0.2655 | 122.905 | 0.64545 | 3.3463 | 22.4167 | 122.8409 | -123.1247 | -123.0698
3412.9062 | 122.0718 | -4.7379 | 117.334 | -0.041657 | 0.0055798 | 0.0068722 | 0.0088141 | -0.001553 | 0.053968 | 0.07348 | -4.0283 | 118.1854 | -5.0446 | 118.2495 | 17.6605 | -1.3779 | 117.7872 | 7.7499 | 118.0984 | -5.0079 | -0.3067 | 0.85144 | 0.70953 | 122.9874 | -99.6735 | -0.27008 | 0.76447 | 1.0162 | 122.525 | 12.4878 | 22.3984 | 122.9233 | 0.70953 | 122.8363 | 3.36 | -0.27008 | 122.9233 | 0.70953 | 3.36 | 22.3984 | 122.8363 | -122.3785 | -122.3419
3413.9062 | 122.3419 | -4.5227 | 117.9703 | 0.065155 | 0.0064344 | 0.0049496 | 0.0086005 | -0.00069859 | 0.055249 | 0.07348 | -3.7903 | 118.4555 | -4.8019 | 118.4418 | 17.5873 | -1.2817 | 118.0161 | 6.9717 | 118.3731 | -4.7882 | -0.27924 | 0.48523 | 0.73242 | 122.9645 | -100.383 | -0.2655 | 0.40283 | 1.0117 | 122.5388 | 11.4944 | 22.11 | 122.9782 | 0.73242 | 122.8958 | 3.241 | -0.2655 | 122.9782 | 0.73242 | 3.241 | 22.11 | 122.8958 | -122.7722 | -122.7585
3414.9062 | 122.525 | -4.3625 | 118.3456 | 0.11856 | 0.0055798 | 0.0066586 | 0.0077459 | -0.00027139 | 0.054395 | 0.08352 | -3.6942 | 118.602 | -4.6646 | 118.4326 | 17.5507 | -1.6251 | 118.19 | 7.1457 | 118.5425 | -4.628 | -0.30212 | 0.25635 | 0.66833 | 122.7951 | -100.795 | -0.2655 | 0.19684 | 0.97046 | 122.5525 | 11.5082 | 21.9131 | 122.9645 | 0.66833 | 122.905 | 2.7374 | -0.2655 | 122.9645 | 0.66833 | 2.7374 | 21.9131 | 122.905 | -123.0103 | -122.9736
3415.9062 | 122.0535 | -4.2389 | 117.8604 | -0.049286 | 0.004939 | 0.0055906 | 0.0077459 | -0.00069859 | 0.052472 | 0.07348 | -3.4973 | 118.7073 | -4.5136 | 118.7256 | 17.5507 | -1.7899 | 118.277 | 7.0953 | 118.6203 | -4.5364 | -0.27466 | 0.84686 | 0.74158 | 122.9645 | -100.3098 | -0.29755 | 0.75989 | 1.0162 | 122.5159 | 11.3342 | 21.7896 | 122.9462 | 0.74158 | 122.8592 | 2.449 | -0.29755 | 122.9462 | 0.74158 | 2.449 | 21.7896 | 122.8592 | -122.374 | -122.3969
3416.9062 | 122.438 | -4.4312 | 117.8146 | -0.12558 | 0.0060072 | 0.0015316 | 0.0083869 | -0.0026212 | 0.052259 | 0.075402 | -3.7857 | 118.4326 | -4.7974 | 118.4738 | 17.4728 | -1.2314 | 118.0115 | 7.0816 | 118.3456 | -4.7882 | -0.36621 | 0.61798 | 0.64545 | 122.905 | -100.3418 | -0.35706 | 0.53101 | 1.0117 | 122.4426 | 11.5128 | 21.904 | 122.8638 | 0.64545 | 122.7768 | 3.1998 | -0.35706 | 122.8638 | 0.64545 | 3.1998 | 21.904 | 122.7768 | -122.612 | -122.6028
3417.9219 | 122.9507 | -4.3533 | 118.4235 | 0.1796 | 0.0028028 | 0.005377 | 0.0017645 | -0.0034756 | 0.054822 | 0.072625 | -3.6346 | 118.4509 | -4.6555 | 118.6157 | 17.5186 | -1.3962 | 117.9703 | 6.8436 | 118.4006 | -4.628 | -0.30212 | 0.027466 | 0.71869 | 122.9691 | -100.9048 | -0.27466 | -0.022888 | 1.0208 | 122.3236 | 11.1969 | 21.8719 | 122.8043 | 0.71869 | 122.7539 | 2.9572 | -0.27466 | 122.8043 | 0.71869 | 2.9572 | 21.8719 | 122.7539 | -123.0789 | -123.0515
3418.9062 | 122.3007 | -4.2343 | 118.19 | 0.034637 | 0.0081434 | 0.010504 | 0.0096685 | -0.0034756 | 0.054609 | 0.075402 | -3.5202 | 118.7576 | -4.4907 | 118.7119 | 17.3401 | -1.8723 | 118.2587 | 6.9031 | 118.5928 | -4.5319 | -0.25635 | 0.56763 | 0.71411 | 122.9462 | -100.8499 | -0.29755 | 0.40283 | 0.97046 | 122.493 | 11.1374 | 21.5744 | 122.9919 | 0.71411 | 122.8271 | 2.3621 | -0.29755 | 122.9919 | 0.71411 | 2.3621 | 21.5744 | 122.8271 | -122.6807 | -122.7219
3419.9062 | 122.5067 | -4.2252 | 118.1259 | 0.027008 | 0.0077162 | 0.0060178 | 0.010096 | -0.00027139 | 0.05354 | 0.071557 | -3.5477 | 118.6523 | -4.5868 | 118.6386 | 17.2943 | -1.5381 | 118.2266 | 7.4982 | 118.5699 | -4.5959 | -0.36163 | 0.52643 | 0.67749 | 122.8638 | -100.8316 | -0.37079 | 0.44403 | 1.0391 | 122.4518 | 11.7233 | 21.5195 | 122.8775 | 0.67749 | 122.7951 | 2.6871 | -0.37079 | 122.8775 | 0.67749 | 2.6871 | 21.5195 | 122.7951 | -122.7127 | -122.7219
3420.9219 | 122.9507 | -4.2068 | 118.3731 | 0.18723 | 0.0045118 | 0.0043088 | 0.0024053 | -0.0051846 | 0.053327 | 0.074975 | -3.7399 | 118.364 | -4.6875 | 118.7622 | 17.363 | -1.4877 | 118.0984 | 7.2006 | 118.5562 | -4.5044 | -0.48065 | -0.009155 | 0.46692 | 122.9691 | -101.0101 | -0.29755 | 0.1831 | 0.94757 | 122.3053 | 11.4075 | 21.5698 | 122.5708 | 0.46692 | 122.7631 | 2.7191 | -0.29755 | 122.5708 | 0.46692 | 2.7191 | 21.5698 | 122.7631 | -123.0606 | -122.8775
3421.9062 | 122.7219 | -4.5319 | 117.6773 | 0.18723 | 0.010066 | 0.0066586 | 0.010523 | -0.003903 | 0.054822 | 0.073693 | -3.8452 | 118.4326 | -4.8294 | 118.4097 | 17.1432 | -1.3092 | 118.0389 | 6.8985 | 118.3365 | -4.7882 | -0.29755 | 0.75531 | 0.68664 | 122.9416 | -100.5341 | -0.25635 | 0.65918 | 0.98419 | 122.5708 | 11.4304 | 21.6751 | 122.9645 | 0.68664 | 122.8683 | 3.2227 | -0.25635 | 122.9645 | 0.68664 | 3.2227 | 21.6751 | 122.8683 | -122.5067 | -122.4655
3422.9062 | 122.9233 | -4.4083 | 118.158 | 0.25589 | 0.0072888 | 0.0049496 | 0.0077459 | -0.001553 | 0.054609 | 0.07348 | -3.6942 | 118.5196 | -4.6875 | 118.5562 | 17.1844 | -1.3596 | 118.0206 | 6.8344 | 118.4326 | -4.6646 | -0.27924 | 0.36163 | 0.71411 | 122.9645 | -100.9735 | -0.25635 | 0.27466 | 0.99335 | 122.4289 | 11.2427 | 21.5927 | 122.9279 | 0.71411 | 122.8409 | 3.0487 | -0.25635 | 122.9279 | 0.71411 | 3.0487 | 21.5927 | 122.8409 | -122.8455 | -122.8226
3423.9062 | 122.5067 | -4.3762 | 117.6682 | -0.31631 | 0.0064344 | 0.0055906 | 0.010096 | -0.0017666 | 0.052259 | 0.073266 | -3.6255 | 118.5928 | -4.6326 | 118.5791 | 17.157 | -1.3779 | 118.1305 | 7.6126 | 118.4463 | -4.6646 | -0.25635 | 0.92468 | 0.75073 | 122.9553 | -100.5112 | -0.28839 | 0.7782 | 1.0071 | 122.5067 | 11.9888 | 21.5332 | 122.9691 | 0.75073 | 122.8226 | 2.9984 | -0.28839 | 122.9691 | 0.75073 | 2.9984 | 21.5332 | 122.8226 | -122.3007 | -122.3328
3424.9062 | 122.4838 | -4.4403 | 118.2175 | 0.042267 | 0.0081434 | 0.0072996 | 0.0092413 | -0.0026212 | 0.055463 | 0.071984 | -3.6942 | 118.4784 | -4.7516 | 118.5242 | 17.0975 | -1.3779 | 118.071 | 6.6376 | 118.4372 | -4.7058 | -0.31128 | 0.26093 | 0.74615 | 122.9645 | -101.12 | -0.2655 | 0.21973 | 1.0574 | 122.5113 | 11.0779 | 21.5378 | 122.9187 | 0.74615 | 122.8775 | 3.0624 | -0.2655 | 122.9187 | 0.74615 | 3.0624 | 21.5378 | 122.8775 | -122.9691 | -122.9233
3425.9062 | 122.9416 | -4.3716 | 118.3777 | 0.27878 | 0.0045118 | 0.0043088 | 0.0041143 | -0.00069859 | 0.051191 | 0.07348 | -3.598 | 118.4647 | -4.6692 | 118.6066 | 17.1478 | -1.3412 | 117.9657 | 6.8024 | 118.396 | -4.6555 | -0.29755 | 0.086975 | 0.77362 | 122.9782 | -101.2299 | -0.28381 | 0.01831 | 1.0712 | 122.3373 | 11.174 | 21.5195 | 122.8363 | 0.77362 | 122.7676 | 3.0304 | -0.28381 | 122.8363 | 0.77362 | 3.0304 | 21.5195 | 122.7676 | -123.0469 | -123.0331
3426.9062 | 122.8317 | -4.4403 | 118.19 | 0.16434 | 0.0057934 | 0.0045224 | 0.0083869 | -5.7592e-05 | 0.054822 | 0.074762 | -3.7216 | 118.483 | -4.7562 | 118.4875 | 17.0242 | -1.4969 | 118.0618 | 7.2327 | 118.4052 | -4.7104 | -0.31586 | 0.29297 | 0.71869 | 122.9279 | -101.1658 | -0.27008 | 0.21515 | 1.0345 | 122.5021 | 11.673 | 21.4645 | 122.9233 | 0.71869 | 122.8455 | 2.9434 | -0.27008 | 122.9233 | 0.71869 | 2.9434 | 21.4645 | 122.8455 | -122.9462 | -122.9004
3427.9219 | 122.9279 | -4.5364 | 118.2449 | 0.1796 | 0.0053662 | 0.0028134 | 0.0051825 | -0.0043302 | 0.054609 | 0.07882 | -3.8132 | 118.2541 | -4.8248 | 118.4006 | 17.0425 | -1.3092 | 117.8238 | 6.9489 | 118.2404 | -4.7928 | -0.28839 | 0.009155 | 0.72327 | 122.937 | -101.2024 | -0.25635 | -0.004578 | 1.0117 | 122.3602 | 11.4853 | 21.579 | 122.7905 | 0.72327 | 122.7768 | 3.2272 | -0.25635 | 122.7905 | 0.72327 | 3.2272 | 21.579 | 122.7768 | -123.0698 | -123.0377
3428.9062 | 122.5113 | -4.4083 | 117.9428 | 0.065155 | 0.0070752 | 0.0015316 | 0.0098823 | -0.0041166 | 0.055677 | 0.074121 | -3.6621 | 118.5059 | -4.7058 | 118.4921 | 16.8961 | -1.6205 | 118.1213 | 7.3425 | 118.3914 | -4.7012 | -0.29755 | 0.56305 | 0.74615 | 122.9004 | -101.0468 | -0.29297 | 0.44861 | 1.0437 | 122.5296 | 11.7508 | 21.3043 | 122.9141 | 0.74615 | 122.7997 | 2.7878 | -0.29297 | 122.9141 | 0.74615 | 2.7878 | 21.3043 | 122.7997 | -122.6486 | -122.644
3429.9062 | 122.7127 | -4.3304 | 118.2907 | 0.18723 | 0.0068616 | 0.0085812 | 0.0083869 | -0.00048499 | 0.053327 | 0.075189 | -3.5568 | 118.634 | -4.5822 | 118.6478 | 16.9647 | -1.7761 | 118.1717 | 6.6055 | 118.5516 | -4.6005 | -0.25177 | 0.34332 | 0.77362 | 122.9782 | -101.326 | -0.27008 | 0.26093 | 1.0254 | 122.5021 | 10.936 | 21.2952 | 122.9645 | 0.77362 | 122.8821 | 2.5543 | -0.27008 | 122.9645 | 0.77362 | 2.5543 | 21.2952 | 122.8821 | -122.8729 | -122.8912
3430.9219 | 122.9233 | -4.3213 | 118.4372 | 0.11093 | 0.0040846 | 0.00046358 | 0.0006965 | -0.0030484 | 0.055036 | 0.074762 | -3.6209 | 118.4601 | -4.6509 | 118.5883 | 16.9464 | -1.6525 | 118.0481 | 6.5735 | 118.4692 | -4.6051 | -0.32959 | 0.022888 | 0.70038 | 122.9095 | -101.4908 | -0.28381 | 0.032043 | 1.03 | 122.3694 | 10.8948 | 21.2677 | 122.7814 | 0.70038 | 122.7905 | 2.6688 | -0.28381 | 122.7814 | 0.70038 | 2.6688 | 21.2677 | 122.7905 | -123.0881 | -123.0423
3431.9062 | 122.2687 | -4.3121 | 118.1763 | 0.095673 | 0.0079298 | 0.0049496 | 0.010309 | -0.0045438 | 0.054395 | 0.073266 | -3.5431 | 118.6295 | -4.6051 | 118.6203 | 16.8365 | -1.8356 | 118.2266 | 6.5918 | 118.5196 | -4.5868 | -0.29297 | 0.45319 | 0.76904 | 122.9324 | -101.3397 | -0.27466 | 0.34332 | 1.062 | 122.5388 | 10.9039 | 21.1487 | 122.9416 | 0.76904 | 122.8317 | 2.4765 | -0.27466 | 122.9416 | 0.76904 | 2.4765 | 21.1487 | 122.8317 | -122.7814 | -122.7631
3432.9062 | 122.7997 | -4.129 | 118.6478 | 0.24826 | 0.0060072 | 0.004736 | 0.0088141 | -0.0019802 | 0.053968 | 0.074762 | -3.4195 | 118.7668 | -4.4632 | 118.7805 | 16.8182 | -1.973 | 118.3777 | 6.5048 | 118.7256 | -4.4083 | -0.33417 | 0.11902 | 0.70953 | 122.9095 | -101.8295 | -0.27924 | 0.07782 | 1.0437 | 122.5067 | 10.6338 | 20.9473 | 122.8958 | 0.70953 | 122.8546 | 2.1561 | -0.27924 | 122.8958 | 0.70953 | 2.1561 | 20.9473 | 122.8546 | -123.111 | -123.056
3433.9062 | 122.7539 | -4.2114 | 118.3868 | 0.24826 | 0.0062208 | 0.0083676 | 0.019922 | -0.0034756 | 0.054395 | 0.077539 | -3.4653 | 118.7622 | -4.4586 | 118.6661 | 16.7633 | -2.0187 | 118.3228 | 6.4362 | 118.6615 | -4.4907 | -0.24719 | 0.37537 | 0.74616 | 122.8775 | -101.6235 | -0.27924 | 0.27466 | 0.99335 | 122.5342 | 10.6476 | 20.9747 | 122.9736 | 0.74616 | 122.8729 | 2.1927 | -0.27924 | 122.9736 | 0.74616 | 2.1927 | 20.9747 | 122.8729 | -122.8455 | -122.8775
3434.9062 | 122.8683 | -4.4174 | 118.2175 | 0.22537 | 0.0051526 | 0.0072996 | 0.0083869 | -0.0013394 | 0.054609 | 0.074548 | -3.6942 | 118.4692 | -4.7195 | 118.5104 | 16.7404 | -1.6159 | 118.0115 | 5.9006 | 118.4143 | -4.6829 | -0.30212 | 0.25177 | 0.72327 | 122.9279 | -101.4771 | -0.2655 | 0.19684 | 1.0254 | 122.4289 | 10.318 | 21.1578 | 122.8867 | 0.72327 | 122.8317 | 2.8015 | -0.2655 | 122.8867 | 0.72327 | 2.8015 | 21.1578 | 122.8317 | -122.937 | -122.9004
3435.9062 | 122.5433 | -4.3304 | 118.0069 | 0.080414 | 0.0075024 | 0.0062314 | 0.0092413 | -0.0019802 | 0.055249 | 0.074548 | -3.5614 | 118.634 | -4.6234 | 118.5928 | 16.6946 | -1.973 | 118.2266 | 6.0516 | 118.5471 | -4.6005 | -0.29297 | 0.62714 | 0.76904 | 122.9233 | -101.3123 | -0.27008 | 0.54016 | 1.062 | 122.5571 | 10.3821 | 21.0251 | 122.9645 | 0.76904 | 122.8775 | 2.3575 | -0.27008 | 122.9645 | 0.76904 | 2.3575 | 21.0251 | 122.8775 | -122.6303 | -122.6074
3436.9062 | 122.6166 | -4.4769 | 118.0344 | 0.088043 | 0.0068616 | 0.0032406 | 0.010523 | -0.0013394 | 0.055036 | 0.073907 | -3.7537 | 118.428 | -4.7791 | 118.4097 | 16.6443 | -2.3987 | 118.0344 | 6.0837 | 118.3456 | -4.7745 | -0.30212 | 0.39368 | 0.72327 | 122.8867 | -101.3901 | -0.29755 | 0.31128 | 1.0254 | 122.5113 | 10.5606 | 21.1212 | 122.905 | 0.72327 | 122.8226 | 2.0782 | -0.29755 | 122.905 | 0.72327 | 2.0782 | 21.1212 | 122.8226 | -122.8134 | -122.8088
3437.9219 | 122.8912 | -4.4724 | 118.2678 | 0.85861 | 0.001521 | 0.00067718 | -0.0010125 | -0.004971 | 0.054609 | 0.074975 | -3.7903 | 118.2266 | -4.8614 | 118.4326 | 16.713 | -1.973 | 117.9062 | 6.2027 | 118.2816 | -4.7379 | -0.3891 | -0.041198 | 0.68207 | 122.905 | -101.5549 | -0.2655 | 0.013733 | 1.0712 | 122.3785 | 10.675 | 21.1853 | 122.699 | 0.68207 | 122.7539 | 2.4994 | -0.2655 | 122.699 | 0.68207 | 2.4994 | 21.1853 | 122.7539 | -123.1293 | -123.0057
3438.9062 | 122.5204 | -4.5914 | 118.2587 | 0.14908 | 0.008357 | 0.0023862 | 0.011164 | -0.0030484 | 0.053113 | 0.07348 | -3.8132 | 118.3685 | -4.8752 | 118.3136 | 16.5756 | -2.1698 | 117.9749 | 5.9692 | 118.277 | -4.8477 | -0.28381 | 0.10986 | 0.7782 | 122.905 | -101.683 | -0.25635 | 0.018311 | 1.062 | 122.5662 | 10.5606 | 21.167 | 122.9599 | 0.7782 | 122.8683 | 2.4216 | -0.25635 | 122.9599 | 0.7782 | 2.4216 | 21.167 | 122.8683 | -123.1338 | -123.1064
3439.9062 | 122.6944 | -9.5123 | 116.0889 | 0.15671 | 0.0064344 | 0.0096494 | 0.011591 | -0.00069859 | 0.052686 | 0.076471 | -3.5934 | 118.6157 | -4.5273 | 118.5562 | 16.5207 | -6.6422 | 106.9199 | 1.1215 | 111.6577 | -10.1624 | 4.985 | 2.5269 | 5.9189 | 128.0685 | -99.5682 | -0.65003 | -4.4312 | 0.93384 | 116.4322 | 10.6338 | 26.033 | 128.1281 | 5.9189 | 121.17 | 2.8702 | -0.65003 | 128.1281 | 5.9189 | 2.8702 | 26.033 | 121.17 | -120.6161 | -126.2512
3440.9062 | 122.9507 | -4.1199 | 118.5745 | 0.3627 | 0.0060072 | 0.0043088 | 0.0068915 | -0.0024076 | 0.055463 | 0.073053 | -3.3508 | 118.6798 | -4.4357 | 118.84 | 16.6672 | -2.2522 | 118.2037 | 6.1478 | 118.6523 | -4.4083 | -0.31586 | 0.10529 | 0.76904 | 122.9599 | -101.9073 | -0.28839 | 0.07782 | 1.0849 | 122.3236 | 10.2676 | 20.787 | 122.7997 | 0.76904 | 122.7722 | 1.8677 | -0.28839 | 122.7997 | 0.76904 | 1.8677 | 20.787 | 122.7722 | -123.0103 | -122.9828
3441.9062 | 122.7264 | -4.216 | 118.3228 | 0.17197 | 0.0062208 | 0.01264 | 0.0088141 | -0.00091219 | 0.055463 | 0.074334 | -3.4561 | 118.7485 | -4.4769 | 118.7759 | 16.5848 | -2.3987 | 118.3044 | 6.9626 | 118.6203 | -4.4907 | -0.26093 | 0.42572 | 0.75989 | 122.9919 | -101.738 | -0.27466 | 0.29755 | 1.0208 | 122.5204 | 11.1786 | 20.8008 | 122.9645 | 0.75989 | 122.8363 | 1.8173 | -0.27466 | 122.9645 | 0.75989 | 1.8173 | 20.8008 | 122.8363 | -122.7997 | -122.8134
3442.9062 | 122.937 | -4.2023 | 118.4921 | 0.27878 | 0.0072888 | 0.0058042 | 0.0066779 | -0.00027139 | 0.055677 | 0.075402 | -3.4515 | 118.6249 | -4.5181 | 118.7576 | 16.6168 | -2.2797 | 118.0984 | 6.8527 | 118.5425 | -4.4861 | -0.31586 | 0.13275 | 0.75073 | 122.9599 | -101.8753 | -0.28381 | 0.050354 | 1.0666 | 122.3007 | 11.055 | 20.8191 | 122.8271 | 0.75073 | 122.7448 | 1.9226 | -0.28381 | 122.8271 | 0.75073 | 1.9226 | 20.8191 | 122.7448 | -123.0103 | -122.9782
3443.9062 | 122.5342 | -4.5044 | 117.8146 | 0.049896 | 0.0060072 | 0.0066586 | 0.0098823 | -0.0011258 | 0.054181 | 0.073266 | -3.717 | 118.4967 | -4.7607 | 118.4509 | 16.4429 | -1.9958 | 118.0435 | 6.7017 | 118.3685 | -4.7424 | -0.25635 | 0.68207 | 0.78735 | 122.9553 | -101.3718 | -0.23804 | 0.55389 | 1.0437 | 122.5479 | 11.2061 | 20.9473 | 123.0011 | 0.78735 | 122.8729 | 2.5085 | -0.23804 | 123.0011 | 0.78735 | 2.5085 | 20.9473 | 122.8729 | -122.5754 | -122.5571
3444.9062 | 122.6166 | -4.3304 | 118.1488 | -0.018768 | 0.0064344 | 0.003668 | 0.0083869 | -0.0013394 | 0.053113 | 0.073053 | -3.5431 | 118.602 | -4.6326 | 118.6203 | 16.4795 | -2.2064 | 118.1625 | 5.9692 | 118.5059 | -4.6005 | -0.30212 | 0.45319 | 0.78735 | 122.9507 | -101.6693 | -0.27008 | 0.35706 | 1.0895 | 122.493 | 10.2997 | 20.8099 | 122.9324 | 0.78735 | 122.8363 | 2.124 | -0.27008 | 122.9324 | 0.78735 | 2.124 | 20.8099 | 122.8363 | -122.7814 | -122.7493
3445.9219 | 122.905 | -4.6051 | 118.1534 | 0.17197 | 0.0040846 | 0.0038816 | -0.0001581 | -0.004971 | 0.055036 | 0.074121 | -3.8818 | 118.1625 | -4.9118 | 118.3136 | 16.4658 | -1.8219 | 117.7734 | 6.0562 | 118.1808 | -4.8477 | -0.3067 | 0.009156 | 0.72327 | 122.9187 | -101.6876 | -0.24261 | 0.027466 | 1.03 | 122.3785 | 10.6613 | 21.0709 | 122.7676 | 0.72327 | 122.7859 | 2.7832 | -0.24261 | 122.7676 | 0.72327 | 2.7832 | 21.0709 | 122.7859 | -123.0652 | -123.0011
3446.9062 | 122.7081 | -4.541 | 118.2404 | -0.49179 | 0.0070752 | 0.0032406 | 0.0094549 | -0.0043302 | 0.05589 | 0.07348 | -3.8498 | 118.3777 | -4.8386 | 118.3685 | 16.3513 | -2.1744 | 117.9703 | 6.5552 | 118.2907 | -4.8203 | -0.29755 | 0.13733 | 0.69122 | 122.9095 | -101.889 | -0.27923 | 0.050354 | 0.98877 | 122.5113 | 11.0962 | 20.8923 | 122.9187 | 0.69122 | 122.8317 | 2.3666 | -0.27923 | 122.9187 | 0.69122 | 2.3666 | 20.8923 | 122.8317 | -123.0789 | -123.0606
3447.9062 | 122.85 | -4.7195 | 118.0527 | 0.17197 | 0.0087842 | 0.005377 | 0.0060369 | -0.00069859 | 0.054181 | 0.073053 | -3.9688 | 118.1946 | -4.9988 | 118.222 | 16.3422 | -2.2522 | 117.746 | 6.8115 | 118.1122 | -4.9896 | -0.27924 | 0.14191 | 0.75073 | 122.9416 | -101.7105 | -0.27008 | 0.05951 | 1.03 | 122.4655 | 11.5311 | 21.0617 | 122.9141 | 0.75073 | 122.8317 | 2.4673 | -0.27008 | 122.9141 | 0.75073 | 2.4673 | 21.0617 | 122.8317 | -123.0515 | -123.0423
3448.9062 | 122.5342 | -4.5364 | 117.9062 | 0.088043 | 0.0070752 | 0.011358 | 0.011377 | -0.002194 | 0.054395 | 0.076898 | -3.772 | 118.4189 | -4.8065 | 118.3777 | 16.2964 | -2.6047 | 117.984 | 6.6376 | 118.2999 | -4.7974 | -0.27008 | 0.5127 | 0.76447 | 122.9141 | -101.6098 | -0.26092 | 0.39368 | 1.0345 | 122.5204 | 11.174 | 20.8328 | 122.9553 | 0.76447 | 122.8363 | 1.9318 | -0.26092 | 122.9553 | 0.76447 | 1.9318 | 20.8328 | 122.8363 | -122.7127 | -122.7036
3449.9062 | 122.6486 | -4.7104 | 117.897 | 0.065155 | 0.0051526 | 0.0072996 | 0.0083869 | -0.00091219 | 0.053113 | 0.074334 | -3.9459 | 118.2404 | -4.9896 | 118.222 | 16.2598 | -2.71 | 117.8192 | 6.8207 | 118.1717 | -4.9896 | -0.27924 | 0.34332 | 0.76446 | 122.9324 | -101.6373 | -0.27924 | 0.27466 | 1.0437 | 122.5296 | 11.5311 | 20.9702 | 122.9507 | 0.76446 | 122.8821 | 2.0004 | -0.27924 | 122.9507 | 0.76446 | 2.0004 | 20.9702 | 122.8821 | -122.8867 | -122.8867
3450.9062 | 122.7814 | -5.0583 | 117.7689 | 0.14908 | 0.006648 | 0.005377 | 0.015223 | -0.00048499 | 0.053968 | 0.072412 | -4.3213 | 117.9108 | -5.3604 | 117.9977 | 16.2415 | -2.8107 | 117.5674 | 6.9443 | 117.7826 | -5.3284 | -0.30212 | 0.14191 | 0.737 | 123.056 | -101.5274 | -0.27008 | 0.013733 | 1.0391 | 122.6257 | 12.0026 | 21.2997 | 122.9691 | 0.737 | 122.8409 | 2.2476 | -0.27008 | 122.9691 | 0.737 | 2.2476 | 21.2997 | 122.8409 | -123.1293 | -123.0972
3451.9062 | 122.7219 | -5.0171 | 117.5491 | -0.095062 | 0.0075024 | 0.0062314 | 0.010523 | -0.0011258 | 0.05354 | 0.074975 | -4.2297 | 117.8879 | -5.3146 | 117.9062 | 16.2231 | -2.6779 | 117.4713 | 6.6925 | 117.8101 | -5.3284 | -0.29755 | 0.33875 | 0.78735 | 122.9233 | -101.326 | -0.31128 | 0.26093 | 1.0849 | 122.4884 | 11.7096 | 21.2402 | 122.905 | 0.78735 | 122.8271 | 2.3392 | -0.31128 | 122.905 | 0.78735 | 2.3392 | 21.2402 | 122.8271 | -122.8638 | -122.8775
3452.9062 | 122.8592 | -5.0262 | 117.8146 | 0.14908 | 0.0064344 | 0.0087948 | 0.0086005 | -0.0013394 | 0.055249 | 0.076471 | -4.2618 | 117.9291 | -5.2826 | 117.9062 | 16.1682 | -2.8061 | 117.4942 | 5.6671 | 117.8558 | -5.2551 | -0.25635 | 0.11444 | 0.76447 | 122.9324 | -101.6464 | -0.22888 | 0.041199 | 1.0208 | 122.5204 | 10.6934 | 21.1945 | 122.9553 | 0.76447 | 122.8821 | 2.2202 | -0.22888 | 122.9553 | 0.76447 | 2.2202 | 21.1945 | 122.8821 | -123.0972 | -123.0698
3453.9062 | 122.9187 | -4.6143 | 118.1305 | 0.17197 | 0.0042982 | 0.001318 | 0.0021917 | -0.0019802 | 0.05354 | 0.076257 | -3.8681 | 118.1534 | -4.921 | 118.3319 | 16.2827 | -2.005 | 117.7048 | 6.5964 | 118.1442 | -4.8706 | -0.3067 | 0.022888 | 0.74616 | 122.9462 | -101.8478 | -0.25635 | 0.013733 | 1.0529 | 122.319 | 11.2106 | 20.8969 | 122.7676 | 0.74616 | 122.7585 | 2.6093 | -0.25635 | 122.7676 | 0.74616 | 2.6093 | 20.8969 | 122.7585 | -123.0515 | -123.0011
3454.9062 | 122.8271 | -4.6875 | 118.1122 | 0.057526 | 0.0053662 | 0.0062314 | 0.0096685 | -0.003903 | 0.055036 | 0.075189 | -3.9505 | 118.277 | -4.9622 | 118.222 | 16.127 | -2.1515 | 117.8192 | 6.308 | 118.1534 | -4.9301 | -0.27466 | 0.16479 | 0.737 | 122.9095 | -101.9852 | -0.24261 | 0.041198 | 1.0117 | 122.5067 | 10.9955 | 20.8145 | 122.9645 | 0.737 | 122.8409 | 2.536 | -0.24261 | 122.9645 | 0.737 | 2.536 | 20.8145 | 122.8409 | -123.0743 | -123.0423
3455.9219 | 122.8775 | -4.454 | 118.3502 | 0.042267 | 0.0042982 | 0.0045224 | -0.0014399 | -0.0045438 | 0.053754 | 0.075402 | -3.6896 | 118.3685 | -4.715 | 118.4647 | 16.2598 | -2.4353 | 117.9428 | 6.7474 | 118.3456 | -4.715 | -0.26093 | 0.01831 | 0.76447 | 122.9187 | -102.0905 | -0.26093 | -0.004578 | 1.0254 | 122.3969 | 11.2015 | 20.7138 | 122.8226 | 0.76447 | 122.7997 | 2.0187 | -0.26093 | 122.8226 | 0.76447 | 2.0187 | 20.7138 | 122.7997 | -123.0652 | -123.0652
3456.9062 | 122.5296 | -4.6967 | 117.9932 | 0.080414 | 0.0070752 | 0.0040952 | 0.011164 | -0.0058256 | 0.0529 | 0.076257 | -3.9642 | 118.2449 | -5.0079 | 118.1992 | 16.0858 | -2.1011 | 117.8284 | 5.9143 | 118.1305 | -4.985 | -0.31128 | 0.25177 | 0.73242 | 122.8958 | -101.9073 | -0.28839 | 0.13733 | 1.0437 | 122.525 | 10.611 | 20.7825 | 122.9416 | 0.73242 | 122.8271 | 2.5955 | -0.28839 | 122.9416 | 0.73242 | 2.5955 | 20.7825 | 122.8271 | -123.0011 | -122.9782
3457.9062 | 122.9507 | -3.8956 | 118.8309 | 0.24063 | 0.0034436 | 0.008154 | 0.0053961 | -0.0019802 | 0.055463 | 0.075402 | -3.1219 | 118.9041 | -4.2297 | 119.0506 | 16.2598 | -2.6871 | 118.3914 | 6.2622 | 118.8538 | -4.1748 | -0.33417 | 0.073242 | 0.77362 | 122.9462 | -102.5711 | -0.27924 | 0.022888 | 1.1078 | 122.287 | 10.1578 | 20.1553 | 122.7997 | 0.77362 | 122.7493 | 1.2085 | -0.27924 | 122.7997 | 0.77362 | 1.2085 | 20.1553 | 122.7493 | -123.0606 | -123.0057
3458.9062 | 122.9279 | -3.9551 | 118.7851 | 0.24063 | 0.0051526 | 0.0028134 | 0.0071051 | -0.0043302 | 0.053968 | 0.075616 | -3.154 | 118.8126 | -4.2709 | 118.9957 | 16.2369 | -2.6825 | 118.3365 | 6.752 | 118.7485 | -4.2435 | -0.31586 | 0.027466 | 0.80109 | 122.9507 | -102.5482 | -0.28839 | -0.036621 | 1.1169 | 122.2916 | 10.7071 | 20.192 | 122.7676 | 0.80109 | 122.7036 | 1.2726 | -0.28839 | 122.7676 | 0.80109 | 1.2726 | 20.192 | 122.7036 | -123.056 | -123.0286
3459.9062 | 122.7219 | -4.0192 | 118.5333 | 0.17197 | 0.0051526 | 0.006445 | 0.013727 | -0.0024076 | 0.055036 | 0.074975 | -3.4195 | 118.9499 | -4.2664 | 118.9224 | 16.0584 | -2.8244 | 118.5425 | 6.6605 | 118.8309 | -4.2801 | -0.24719 | 0.41656 | 0.59967 | 122.9416 | -102.475 | -0.26093 | 0.29755 | 0.84686 | 122.5616 | 10.6796 | 20.0775 | 122.9691 | 0.59967 | 122.85 | 1.1948 | -0.26093 | 122.9691 | 0.59967 | 1.1948 | 20.0775 | 122.85 | -122.7997 | -122.8134
3460.9062 | 122.9279 | -4.1473 | 118.5425 | -0.7283 | 0.0051526 | 0.001318 | 0.0066779 | -0.0041166 | 0.055463 | 0.076257 | -3.3005 | 118.6157 | -4.4907 | 118.808 | 16.1682 | -2.1606 | 118.1442 | 6.9534 | 118.5654 | -4.4449 | -0.34332 | 0.073243 | 0.84686 | 122.9553 | -102.3743 | -0.29755 | 0.022889 | 1.1902 | 122.2916 | 11.1008 | 20.3156 | 122.7631 | 0.84686 | 122.7127 | 1.9867 | -0.29755 | 122.7631 | 0.84686 | 1.9867 | 20.3156 | 122.7127 | -123.0331 | -122.9874
3461.9062 | 122.7814 | -4.1199 | 118.428 | 0.11093 | 0.0077162 | 0.0077268 | 0.014795 | -0.0019802 | 0.056318 | 0.077966 | -3.3737 | 118.7897 | -4.4312 | 118.7531 | 16.2689 | -2.3987 | 118.2266 | 6.5964 | 118.7119 | -4.39 | -0.31128 | 0.36163 | 0.74615 | 122.8729 | -102.1591 | -0.27008 | 0.28381 | 1.0574 | 122.3465 | 10.7162 | 20.3888 | 122.9095 | 0.74615 | 122.8317 | 1.7212 | -0.27008 | 122.9095 | 0.74615 | 1.7212 | 20.3888 | 122.8317 | -122.8592 | -122.818
3462.9219 | 122.9187 | -4.0787 | 118.6523 | 0.11856 | 0.0055798 | 0.001318 | 0.0047553 | -0.0034756 | 0.055249 | 0.079461 | -3.3234 | 118.7073 | -4.3762 | 118.8171 | 16.0858 | -2.4765 | 118.2953 | 6.2439 | 118.6935 | -4.3488 | -0.29755 | 0.054931 | 0.75531 | 122.8958 | -102.5665 | -0.27008 | 0.041198 | 1.0529 | 122.374 | 10.3226 | 20.1645 | 122.7859 | 0.75531 | 122.7722 | 1.6022 | -0.27008 | 122.7859 | 0.75531 | 1.6022 | 20.1645 | 122.7722 | -123.0286 | -123.0011
3463.9219 | 122.8638 | -4.1336 | 118.6386 | 0.072784 | 0.0023756 | 0.00024998 | 0.0043281 | -0.0058256 | 0.055463 | 0.076898 | -3.3463 | 118.7164 | -4.3762 | 118.7347 | 16.0629 | -2.5452 | 118.2495 | 6.5598 | 118.6386 | -4.4083 | -0.24261 | 0.07782 | 0.78735 | 122.8683 | -102.5757 | -0.27466 | 0 | 1.03 | 122.3831 | 10.6934 | 20.1965 | 122.85 | 0.78735 | 122.7722 | 1.5884 | -0.27466 | 122.85 | 0.78735 | 1.5884 | 20.1965 | 122.7722 | -123.0148 | -123.0469
3464.9062 | 122.5113 | -4.335 | 118.428 | 0.11093 | 0.010066 | 0.0072996 | 0.013086 | -0.0062528 | 0.055036 | 0.075189 | -3.5248 | 118.634 | -4.6051 | 118.5974 | 15.9439 | -2.7695 | 118.2037 | 6.4819 | 118.4875 | -4.5822 | -0.27008 | 0.20599 | 0.81024 | 122.9324 | -102.4841 | -0.24719 | 0.059509 | 1.0803 | 122.5388 | 10.817 | 20.2789 | 122.9691 | 0.81024 | 122.8226 | 1.5656 | -0.24719 | 122.9691 | 0.81024 | 1.5656 | 20.2789 | 122.8226 | -123.0331 | -123.0103
3465.9062 | 122.937 | -4.2709 | 118.4372 | 0.52292 | 0.0023756 | 0.005377 | 0.0062507 | -0.003903 | 0.054822 | 0.07818 | -3.4927 | 118.5104 | -4.6097 | 118.6798 | 16.0492 | -2.6321 | 118.0115 | 5.6717 | 118.4692 | -4.541 | -0.33875 | 0.073242 | 0.7782 | 122.9507 | -102.388 | -0.27008 | 0.032043 | 1.1169 | 122.2824 | 9.9426 | 20.3201 | 122.7814 | 0.7782 | 122.7402 | 1.6388 | -0.27008 | 122.7814 | 0.7782 | 1.6388 | 20.3201 | 122.7402 | -123.0469 | -122.9782
3466.9062 | 122.8043 | -4.0878 | 118.5196 | 0.11093 | 0.008357 | 0.0079404 | 0.0098823 | -0.0043302 | 0.057172 | 0.077966 | -3.3325 | 118.8263 | -4.3762 | 118.7622 | 16.1133 | -2.655 | 118.3136 | 6.4636 | 118.7347 | -4.3442 | -0.28839 | 0.3067 | 0.75531 | 122.85 | -102.4063 | -0.25635 | 0.21515 | 1.0437 | 122.4014 | 10.5515 | 20.2011 | 122.9141 | 0.75531 | 122.8226 | 1.4328 | -0.25635 | 122.9141 | 0.75531 | 1.4328 | 20.2011 | 122.8226 | -122.8958 | -122.8638
3467.9062 | 122.9141 | -4.0512 | 118.7119 | 0.16434 | 0.0055798 | 0.004736 | 0.0090277 | 0.0014376 | 0.055463 | 0.074762 | -3.2089 | 118.7759 | -4.3671 | 119.0231 | 16.0538 | -2.7008 | 118.2541 | 6.3126 | 118.6798 | -4.3167 | -0.31586 | 0.064087 | 0.84228 | 123.0743 | -102.6581 | -0.2655 | -0.032043 | 1.1581 | 122.3053 | 10.3638 | 20.105 | 122.8271 | 0.84228 | 122.731 | 1.3504 | -0.2655 | 122.8271 | 0.84228 | 1.3504 | 20.105 | 122.731 | -123.0789 | -123.0286
3468.9219 | 122.8729 | -4.0466 | 118.7256 | 0.20248 | 0.0025892 | 0.0045224 | 0.0051825 | -0.0051846 | 0.055463 | 0.076471 | -3.2822 | 118.7393 | -4.3213 | 118.8858 | 15.9439 | -2.7374 | 118.3182 | 6.546 | 118.689 | -4.3121 | -0.27466 | 0.013733 | 0.76446 | 122.9324 | -102.7817 | -0.2655 | -0.036621 | 1.0391 | 122.3648 | 10.5927 | 19.9905 | 122.7859 | 0.76446 | 122.7356 | 1.3092 | -0.2655 | 122.7859 | 0.76446 | 1.3092 | 19.9905 | 122.7356 | -123.0469 | -123.0377
3469.9062 | 122.5479 | -4.1565 | 118.5104 | 0.18723 | 0.0075024 | 0.004736 | 0.013941 | -0.0043302 | 0.056958 | 0.076043 | -3.3508 | 118.8171 | -4.4357 | 118.7576 | 15.8203 | -2.8793 | 118.3777 | 5.7266 | 118.6569 | -4.4083 | -0.27924 | 0.3067 | 0.80566 | 122.9141 | -102.6901 | -0.25177 | 0.14648 | 1.0849 | 122.5342 | 9.8831 | 19.9768 | 122.9736 | 0.80566 | 122.8134 | 1.2772 | -0.25177 | 122.9736 | 0.80566 | 1.2772 | 19.9768 | 122.8134 | -122.9462 | -122.9187
3470.9062 | 122.8729 | -4.0787 | 118.6752 | 0.027008 | 0.0028028 | 0.0017454 | 0.0002691 | -0.0064664 | 0.056318 | 0.074762 | -3.3646 | 118.5608 | -4.6463 | 118.8446 | 15.9256 | -2.8061 | 118.2861 | 6.4682 | 118.689 | -4.3396 | -0.56763 | -0.11444 | 0.71411 | 122.9233 | -102.7496 | -0.26093 | 0.013733 | 1.2817 | 122.3648 | 10.5469 | 20.0043 | 122.6395 | 0.71411 | 122.7676 | 1.2726 | -0.26093 | 122.6395 | 0.71411 | 1.2726 | 20.0043 | 122.7676 | -123.3215 | -123.0148
3471.9062 | 122.6074 | -4.0466 | 118.6707 | 0.027008 | 0.006648 | 0.0058042 | 0.015436 | -0.0041166 | 0.055249 | 0.075616 | -3.1906 | 118.8858 | -4.3076 | 118.895 | 15.8295 | -2.7832 | 118.4555 | 6.2622 | 118.7439 | -4.3167 | -0.26093 | 0.21515 | 0.85602 | 122.9416 | -102.8412 | -0.27008 | 0.073242 | 1.1169 | 122.5021 | 10.3088 | 19.8761 | 122.9324 | 0.85602 | 122.7905 | 1.2634 | -0.27008 | 122.9324 | 0.85602 | 1.2634 | 19.8761 | 122.7905 | -122.9782 | -122.9874
3472.9062 | 122.8729 | -4.0878 | 118.7073 | 0.18723 | 0.0038708 | 0.0055906 | 0.010737 | -0.002194 | 0.056958 | 0.079675 | -3.2867 | 118.7988 | -4.39 | 118.7943 | 15.8066 | -2.8198 | 118.3685 | 6.102 | 118.7119 | -4.3625 | -0.30212 | 0.091553 | 0.80109 | 122.8821 | -102.9007 | -0.27466 | 0.004578 | 1.1032 | 122.4564 | 10.1898 | 19.8944 | 122.8867 | 0.80109 | 122.7997 | 1.268 | -0.27466 | 122.8867 | 0.80109 | 1.268 | 19.8944 | 122.7997 | -123.0972 | -123.0698
3473.9062 | 122.8363 | -4.7562 | 117.984 | 2.7888 | 0.0064344 | 0.0025998 | 0.036371 | -0.0026212 | 0.056104 | 0.10275 | -3.7582 | 118.2816 | -4.9347 | 118.1534 | 15.7104 | -2.7512 | 117.7368 | 6.1203 | 118.0756 | -5.0034 | -0.17853 | 0.29755 | 0.99793 | 122.9095 | -102.2736 | -0.24719 | 0.091553 | 1.1765 | 122.493 | 10.8765 | 20.4666 | 123.0377 | 0.99793 | 122.8317 | 2.005 | -0.24719 | 123.0377 | 0.99793 | 2.005 | 20.4666 | 122.8317 | -122.9187 | -122.9874
3474.9062 | 122.8043 | -3.9688 | 118.8217 | 0.1796 | 0.0057934 | 0.0077268 | 0.016718 | -0.002194 | 0.055677 | 0.083947 | -3.0945 | 119.0643 | -4.1153 | 119.0002 | 15.8066 | 0.032043 | 118.2083 | 6.0059 | 118.8492 | -4.2023 | -0.14648 | 0.24262 | 0.87433 | 122.9691 | -103.0151 | -0.23346 | 0.027466 | 1.0208 | 122.1771 | 9.9747 | 19.7754 | 123.0331 | 0.87433 | 122.818 | 4.0009 | -0.23346 | 123.0331 | 0.87433 | 4.0009 | 19.7754 | 122.818 | -122.937 | -123.024
3475.9062 | 122.937 | -3.4149 | 119.3024 | -0.5452 | 0.0062208 | 0.0025998 | 0.0064643 | -0.0026212 | 0.05589 | 0.079034 | -2.6047 | 119.3481 | -3.7582 | 119.5404 | 15.9027 | -0.32501 | 118.9911 | 6.395 | 119.2932 | -3.6942 | -0.34332 | 0.045777 | 0.81024 | 122.9553 | -103.3997 | -0.27924 | -0.009155 | 1.1536 | 122.406 | 9.8099 | 19.3176 | 122.7631 | 0.81024 | 122.7081 | 3.0899 | -0.27924 | 122.7631 | 0.81024 | 3.0899 | 19.3176 | 122.7081 | -123.0606 | -122.9965
3476.9062 | 122.7539 | -3.4332 | 119.0689 | 0.14145 | 0.0075024 | 0.0049496 | 0.018213 | -0.0017666 | 0.052472 | 0.078607 | -2.5772 | 119.5496 | -3.7033 | 119.6228 | 15.7288 | -0.79651 | 119.2657 | 6.2897 | 119.3802 | -3.6942 | -0.27008 | 0.48065 | 0.85602 | 123.056 | -103.3401 | -0.26092 | 0.31128 | 1.1261 | 122.699 | 9.7229 | 19.162 | 122.9828 | 0.85602 | 122.8134 | 2.6367 | -0.26092 | 122.9828 | 0.85602 | 2.6367 | 19.162 | 122.8134 | -122.7722 | -122.7631
3477.9062 | 122.9507 | -3.3096 | 119.3893 | 0.17197 | 0.0036572 | 0.0017454 | 0.0058233 | -0.0034756 | 0.054822 | 0.077539 | -2.4765 | 119.4763 | -3.6438 | 119.5953 | 15.8524 | -0.67749 | 119.1284 | 6.2622 | 119.4077 | -3.5934 | -0.33417 | 0.086975 | 0.83313 | 122.905 | -103.537 | -0.28381 | 0.018311 | 1.1673 | 122.438 | 9.5718 | 19.162 | 122.7859 | 0.83313 | 122.7173 | 2.6321 | -0.28381 | 122.7859 | 0.83313 | 2.6321 | 19.162 | 122.7173 | -123.0331 | -122.9828
3478.9062 | 122.85 | -3.241 | 119.545 | 0.11093 | 0.0072888 | 0.0070858 | 0.010096 | -0.0030484 | 0.055677 | 0.077325 | -2.3987 | 119.6777 | -3.5248 | 119.6732 | 15.7471 | -0.87433 | 119.339 | 5.7953 | 119.5679 | -3.5294 | -0.28381 | 0.13275 | 0.84228 | 122.9141 | -103.7979 | -0.28839 | 0.022888 | 1.1261 | 122.58 | 9.0363 | 18.988 | 122.9187 | 0.84228 | 122.8088 | 2.3666 | -0.28839 | 122.9187 | 0.84228 | 2.3666 | 18.988 | 122.8088 | -123.0698 | -123.0743
3479.9062 | 122.4609 | -3.2959 | 119.4534 | 0.0041197 | 0.0072888 | 0.0028134 | 0.0094549 | -0.0019802 | 0.05589 | 0.077111 | -2.4216 | 119.6503 | -3.5614 | 119.6503 | 15.7013 | -0.9201 | 119.3344 | 6.0562 | 119.5038 | -3.566 | -0.2655 | 0.19684 | 0.87433 | 122.9462 | -103.7521 | -0.27008 | 0.050354 | 1.1398 | 122.6303 | 9.3521 | 18.9972 | 122.9462 | 0.87433 | 122.7997 | 2.3758 | -0.27008 | 122.9462 | 0.87433 | 2.3758 | 18.9972 | 122.7997 | -123.0148 | -123.0194
3480.9219 | 122.9004 | -3.4241 | 119.3527 | -0.041657 | 0.0036572 | 0.0034544 | 0.0019781 | -0.0041166 | 0.056318 | 0.076257 | -2.5772 | 119.3848 | -3.7033 | 119.5221 | 15.8112 | -0.5722 | 119.0826 | 6.8665 | 119.3527 | -3.6804 | -0.27924 | 0.032044 | 0.84686 | 122.9462 | -103.5416 | -0.25635 | 0 | 1.1261 | 122.5067 | 10.2905 | 19.2352 | 122.8088 | 0.84686 | 122.7768 | 2.8519 | -0.25635 | 122.8088 | 0.84686 | 2.8519 | 19.2352 | 122.7768 | -123.056 | -123.0331
3481.9062 | 122.8226 | -3.2913 | 119.5129 | 0.15671 | 0.0070752 | 0.0055906 | 0.012659 | -0.0026212 | 0.05589 | 0.075616 | -2.4765 | 119.6228 | -3.6118 | 119.6411 | 15.6784 | -0.84228 | 119.2841 | 6.0974 | 119.5175 | -3.5522 | -0.32043 | 0.10986 | 0.81482 | 122.9324 | -103.8345 | -0.26092 | 0.004578 | 1.1353 | 122.5754 | 9.3887 | 18.9697 | 122.9141 | 0.81482 | 122.8088 | 2.449 | -0.26092 | 122.9141 | 0.81482 | 2.449 | 18.9697 | 122.8088 | -123.1247 | -123.0652
3482.9062 | 122.8729 | -3.3508 | 119.252 | 0.15671 | 0.0045118 | 0.0060178 | 0.0077459 | -0.0058256 | 0.056531 | 0.079889 | -2.449 | 119.5038 | -3.5843 | 119.6274 | 15.77 | -0.71869 | 118.9636 | 6.8436 | 119.4077 | -3.5751 | -0.23346 | 0.25177 | 0.90179 | 122.9782 | -103.4821 | -0.2243 | 0.15564 | 1.1353 | 122.3145 | 10.1944 | 19.1208 | 122.8546 | 0.90179 | 122.7585 | 2.6321 | -0.2243 | 122.8546 | 0.90179 | 2.6321 | 19.1208 | 122.7585 | -122.8363 | -122.8271
3483.9062 | 122.9279 | -3.273 | 119.4672 | 1.7055 | 0.0040846 | 0.0055906 | 0.0090277 | -0.0036892 | 0.056318 | 0.074762 | -2.3529 | 119.5175 | -3.5843 | 119.7006 | 15.7379 | -0.68207 | 119.0964 | 5.9235 | 119.4534 | -3.5202 | -0.31128 | 0.050354 | 0.92011 | 122.9736 | -103.7292 | -0.24719 | -0.013733 | 1.2314 | 122.3694 | 9.1965 | 19.0109 | 122.7905 | 0.92011 | 122.7264 | 2.5909 | -0.24719 | 122.7905 | 0.92011 | 2.5909 | 19.0109 | 122.7264 | -123.0515 | -122.9874
3484.9062 | 122.9324 | -3.2913 | 119.4534 | 0.14908 | 0.0036572 | 0.0062314 | 0.0094549 | -0.0041166 | 0.055249 | 0.074121 | -2.4124 | 119.5679 | -3.6026 | 119.6915 | 15.7059 | -0.737 | 119.1376 | 6.8069 | 119.458 | -3.5568 | -0.31128 | 0.11444 | 0.87891 | 122.9828 | -103.7476 | -0.2655 | 0.004578 | 1.1902 | 122.4289 | 10.0983 | 18.9972 | 122.8592 | 0.87891 | 122.7493 | 2.5543 | -0.2655 | 122.8592 | 0.87891 | 2.5543 | 18.9972 | 122.7493 | -123.056 | -123.0103
3485.9062 | 122.8912 | -3.1952 | 119.5679 | 0.11856 | 0.00323 | 0.0025998 | 0.0028327 | -0.0060392 | 0.055677 | 0.076471 | -2.3483 | 119.5953 | -3.4882 | 119.7235 | 15.6876 | -0.84228 | 119.3069 | 6.5872 | 119.5587 | -3.4607 | -0.29297 | 0.027466 | 0.84686 | 122.9187 | -103.8803 | -0.2655 | -0.009155 | 1.1398 | 122.5021 | 9.7824 | 18.8828 | 122.7905 | 0.84686 | 122.7539 | 2.3529 | -0.2655 | 122.7905 | 0.84686 | 2.3529 | 18.8828 | 122.7539 | -123.056 | -123.0286
3486.9062 | 122.9553 | -3.3508 | 119.3115 | 0.233 | 0.0019482 | 0.0085812 | 0.021418 | -0.0062528 | 0.055463 | 0.077966 | -2.4033 | 119.5587 | -3.5889 | 119.6869 | 15.6418 | -0.52643 | 118.9774 | 6.7886 | 119.4031 | -3.6026 | -0.23804 | 0.24719 | 0.94757 | 123.0377 | -103.6697 | -0.25177 | 0.091553 | 1.1856 | 122.3282 | 10.1395 | 18.9926 | 122.9095 | 0.94757 | 122.7539 | 2.8244 | -0.25177 | 122.9095 | 0.94757 | 2.8244 | 18.9926 | 122.7539 | -122.9004 | -122.9141
3487.9062 | 122.8867 | -3.2547 | 119.5129 | 0.057526 | 0.0038708 | 0.0028134 | 0.0043281 | -0.0075344 | 0.053968 | 0.076898 | -2.4353 | 119.5221 | -3.5156 | 119.6869 | 15.6189 | -0.72327 | 119.2383 | 5.7037 | 119.4855 | -3.5065 | -0.26092 | 0.009156 | 0.8194 | 122.9416 | -103.894 | -0.25177 | -0.027465 | 1.0803 | 122.493 | 8.9584 | 18.8736 | 122.7768 | 0.8194 | 122.7402 | 2.5314 | -0.25177 | 122.7768 | 0.8194 | 2.5314 | 18.8736 | 122.7402 | -123.0286 | -123.0194
3488.9062 | 122.9187 | -3.2227 | 119.5312 | 0.25589 | 0.0064344 | 0.0085812 | 0.0088141 | -0.004971 | 0.056745 | 0.07583 | -2.3529 | 119.5633 | -3.5843 | 119.7601 | 15.6326 | -0.76446 | 119.2429 | 6.2897 | 119.5038 | -3.5202 | -0.36163 | 0.032043 | 0.86975 | 122.9828 | -103.8986 | -0.29755 | -0.027466 | 1.2314 | 122.4655 | 9.5123 | 18.8553 | 122.7859 | 0.86975 | 122.7264 | 2.4582 | -0.29755 | 122.7859 | 0.86975 | 2.4582 | 18.8553 | 122.7264 | -123.1155 | -123.0515
3489.9062 | 122.905 | -2.8519 | 119.9203 | 0.1796 | 0.0057934 | 0.0055906 | 0.0086005 | -0.003903 | 0.053968 | 0.075616 | -1.973 | 120.0119 | -3.1311 | 120.1218 | 15.6738 | -1.2314 | 119.5633 | 6.5598 | 119.8883 | -3.1128 | -0.27924 | 0.091553 | 0.87891 | 122.9736 | -104.2465 | -0.26092 | -0.032043 | 1.1581 | 122.4152 | 9.4116 | 18.5257 | 122.8638 | 0.87891 | 122.7402 | 1.6205 | -0.26092 | 122.8638 | 0.87891 | 1.6205 | 18.5257 | 122.7402 | -123.0515 | -123.0331
3490.9062 | 122.9599 | -2.8885 | 119.87 | -0.19424 | 0.0017346 | -0.0018862 | 0.0056097 | -0.0053982 | 0.054395 | 0.076684 | -2.0462 | 119.9066 | -3.1631 | 120.108 | 15.6784 | -1.1902 | 119.5953 | 6.6605 | 119.8746 | -3.154 | -0.27466 | 0.036621 | 0.84228 | 122.9965 | -104.1916 | -0.2655 | 0.004578 | 1.1169 | 122.4838 | 9.5489 | 18.5669 | 122.7951 | 0.84228 | 122.7631 | 1.6983 | -0.2655 | 122.7951 | 0.84228 | 1.6983 | 18.5669 | 122.7631 | -123.0331 | -123.024
3491.9062 | 122.9233 | -2.9068 | 119.8242 | 0.1796 | 0.0038708 | 0.0060178 | 0.0071051 | -0.0030484 | 0.055463 | 0.075616 | -2.0279 | 119.9112 | -3.186 | 120.0577 | 15.6235 | -1.2085 | 119.4763 | 6.3217 | 119.8242 | -3.1494 | -0.27924 | 0.086975 | 0.87891 | 122.9645 | -104.2007 | -0.24262 | 0 | 1.1581 | 122.3831 | 9.2285 | 18.5303 | 122.818 | 0.87891 | 122.731 | 1.6983 | -0.24262 | 122.818 | 0.87891 | 1.6983 | 18.5303 | 122.731 | -123.0103 | -122.9736
3492.9062 | 122.9187 | -3.0075 | 119.7784 | 0.25589 | 0.0053662 | 0.010931 | 0.016291 | -0.004971 | 0.055036 | 0.08352 | -2.1149 | 119.8563 | -3.273 | 119.9066 | 15.5731 | -1.2039 | 119.4122 | 6.7749 | 119.7556 | -3.2867 | -0.2655 | 0.07782 | 0.89264 | 122.9141 | -104.2053 | -0.27924 | -0.022888 | 1.1581 | 122.4197 | 9.7824 | 18.5806 | 122.8638 | 0.89264 | 122.7631 | 1.8036 | -0.27924 | 122.8638 | 0.89264 | 1.8036 | 18.5806 | 122.7631 | -123.0515 | -123.0652
3493.9062 | 122.9095 | -2.9617 | 119.751 | -0.94193 | 0.0055798 | 0.0045224 | 0.0096685 | -0.003262 | 0.055677 | 0.076684 | -2.0691 | 119.8334 | -3.2593 | 120.0531 | 15.5869 | -1.1993 | 119.4763 | 6.5689 | 119.7693 | -3.1952 | -0.29755 | 0.082397 | 0.89264 | 123.0148 | -104.1641 | -0.23346 | 0.01831 | 1.1902 | 122.438 | 9.5306 | 18.5486 | 122.7951 | 0.89264 | 122.731 | 1.7624 | -0.23346 | 122.7951 | 0.89264 | 1.7624 | 18.5486 | 122.731 | -123.0103 | -122.9462
3494.9062 | 122.9004 | -3.0304 | 119.6915 | 0.17197 | 0.0055798 | 0.0028134 | 0.016718 | -0.0068936 | 0.055677 | 0.081384 | -2.1378 | 119.7784 | -3.2867 | 119.9295 | 15.5502 | -1.1902 | 119.2062 | 6.4819 | 119.6777 | -3.3188 | -0.25635 | 0.086975 | 0.89264 | 122.9599 | -104.1412 | -0.28839 | -0.013733 | 1.149 | 122.2366 | 9.5123 | 18.5806 | 122.8088 | 0.89264 | 122.7081 | 1.8402 | -0.28839 | 122.8088 | 0.89264 | 1.8402 | 18.5806 | 122.7081 | -122.9782 | -123.0103
3495.9219 | 122.9233 | -2.9068 | 119.8334 | -0.16373 | 0.0038708 | 0.0034544 | 0.0064643 | -0.0081754 | 0.054181 | 0.076898 | -1.9958 | 119.8929 | -3.2135 | 120.1035 | 15.596 | -1.2497 | 119.5999 | 6.6513 | 119.8105 | -3.1631 | -0.3067 | 0.059509 | 0.91095 | 123.0103 | -104.2374 | -0.25635 | -0.022888 | 1.2177 | 122.5067 | 9.5581 | 18.5028 | 122.7997 | 0.91095 | 122.7173 | 1.6571 | -0.25635 | 122.7997 | 0.91095 | 1.6571 | 18.5028 | 122.7173 | -123.0469 | -122.9965
3496.9062 | 122.9187 | -2.948 | 119.8059 | 0.027008 | 0.0040846 | 0.0043088 | 0.0092413 | -0.0051846 | 0.055036 | 0.074762 | -1.9455 | 119.838 | -3.2684 | 120.0439 | 15.564 | -1.0071 | 119.4626 | 6.7795 | 119.7693 | -3.1998 | -0.32043 | 0.032044 | 1.0025 | 122.9919 | -104.2419 | -0.25177 | -0.036621 | 1.3229 | 122.4106 | 9.7275 | 18.512 | 122.7859 | 1.0025 | 122.7173 | 1.9409 | -0.25177 | 122.7859 | 1.0025 | 1.9409 | 18.512 | 122.7173 | -123.0743 | -123.0057
3497.9062 | 122.8775 | -3.1677 | 119.6045 | 0.11093 | 0.0051526 | 0.0062314 | 0.0056097 | -0.0079618 | 0.056104 | 0.077325 | -2.2888 | 119.664 | -3.4149 | 119.7601 | 15.4816 | -0.72784 | 119.3344 | 6.3904 | 119.5679 | -3.4241 | -0.24719 | 0.059509 | 0.87891 | 122.9279 | -104.1229 | -0.25635 | -0.036621 | 1.1261 | 122.5021 | 9.5581 | 18.6493 | 122.8317 | 0.87891 | 122.7356 | 2.4399 | -0.25635 | 122.8317 | 0.87891 | 2.4399 | 18.6493 | 122.7356 | -123.0194 | -123.0286
3498.9062 | 122.8592 | -3.1265 | 119.545 | 0.14908 | 0.0040846 | 0.0049496 | 0.0096685 | -0.0071072 | 0.054822 | 0.080957 | -2.2202 | 119.6274 | -3.4287 | 119.8563 | 15.5045 | -0.66834 | 119.2657 | 5.6946 | 119.545 | -3.4058 | -0.30212 | 0.082397 | 0.90637 | 122.9828 | -104.0405 | -0.27924 | 0 | 1.2085 | 122.3923 | 8.8211 | 18.631 | 122.7539 | 0.90637 | 122.6715 | 2.4582 | -0.27924 | 122.7539 | 0.90637 | 2.4582 | 18.631 | 122.6715 | -122.9736 | -122.9507
3499.9062 | 122.9004 | -3.3966 | 119.3527 | 0.14145 | 0.0038708 | 0.0051632 | 0.0079595 | -0.0058256 | 0.056318 | 0.077539 | -2.4673 | 119.3939 | -3.6713 | 119.5633 | 15.4587 | -0.068665 | 119.0002 | 5.571 | 119.3069 | -3.6484 | -0.27466 | 0.041199 | 0.92926 | 122.9599 | -103.894 | -0.25177 | -0.045776 | 1.2039 | 122.3969 | 8.9676 | 18.8553 | 122.7905 | 0.92926 | 122.7036 | 3.3279 | -0.25177 | 122.7905 | 0.92926 | 3.3279 | 18.8553 | 122.7036 | -123.024 | -123.0011
3500.9062 | 122.9004 | -3.4973 | 119.3665 | -0.026398 | 0.0023756 | -0.00060462 | 0.0051825 | -0.0071072 | 0.056318 | 0.08352 | -2.7374 | 119.252 | -3.7537 | 119.3024 | 15.3763 | 0.11902 | 118.9224 | 5.6625 | 119.1788 | -3.7674 | -0.25635 | -0.11444 | 0.75989 | 122.7997 | -103.9902 | -0.27008 | -0.18768 | 1.0162 | 122.4197 | 9.1599 | 18.8736 | 122.7493 | 0.75989 | 122.6761 | 3.6163 | -0.27008 | 122.7493 | 0.75989 | 3.6163 | 18.8736 | 122.6761 | -123.1201 | -123.1338
3501.9062 | 122.8226 | -3.5934 | 119.2062 | 0.19485 | 0.0034436 | 0.004736 | 0.0086005 | -0.0081754 | 0.057386 | 0.085656 | -2.5543 | 119.2795 | -3.7582 | 119.2795 | 15.3809 | 0.15106 | 118.8995 | 6.2897 | 119.1422 | -3.8635 | -0.16479 | 0.073242 | 1.0391 | 122.8729 | -103.8254 | -0.27008 | -0.064087 | 1.2039 | 122.493 | 9.8831 | 18.9743 | 122.8729 | 1.0391 | 122.7356 | 3.7445 | -0.27008 | 122.8729 | 1.0391 | 3.7445 | 18.9743 | 122.7356 | -122.9645 | -123.0698
3502.9062 | 122.9828 | -3.4973 | 119.165 | 0.042267 | 0.0010938 | -0.0018862 | 0.0062507 | -0.0079618 | 0.055677 | 0.080529 | -2.5726 | 119.3253 | -3.7354 | 119.5175 | 15.3992 | 0.009155 | 118.9636 | 5.5664 | 119.252 | -3.7308 | -0.23804 | 0.16022 | 0.92468 | 123.0148 | -103.7659 | -0.23346 | 0.086975 | 1.1627 | 122.4609 | 9.0637 | 18.8965 | 122.8226 | 0.92468 | 122.7493 | 3.5065 | -0.23346 | 122.8226 | 0.92468 | 3.5065 | 18.8965 | 122.7493 | -122.9004 | -122.8958
3503.9062 | 122.9095 | -3.1174 | 119.6457 | 0.19485 | 0.0045118 | 0.0021726 | 0.0066779 | -0.0068936 | 0.060163 | 0.075402 | -2.3026 | 119.6182 | -3.4332 | 119.8471 | 15.4037 | -0.64087 | 119.3253 | 6.5414 | 119.5953 | -3.3646 | -0.31586 | -0.027466 | 0.81482 | 122.9645 | -104.2419 | -0.24719 | -0.050354 | 1.1307 | 122.4426 | 9.6588 | 18.5211 | 122.7356 | 0.81482 | 122.7127 | 2.4765 | -0.24719 | 122.7356 | 0.81482 | 2.4765 | 18.5211 | 122.7127 | -123.0789 | -123.0103
3504.9062 | 122.9187 | -3.4653 | 119.133 | 0.14908 | 0.0047254 | -0.00039102 | 0.0133 | -0.00668 | 0.055463 | 0.07882 | -2.6321 | 119.22 | -3.804 | 119.5953 | 15.39 | -0.16479 | 118.9499 | 6.6147 | 119.2245 | -3.685 | -0.33874 | 0.086975 | 0.83313 | 123.0606 | -103.743 | -0.21973 | 0.091552 | 1.1719 | 122.4152 | 10.08 | 18.8553 | 122.6852 | 0.83313 | 122.6898 | 3.3005 | -0.21973 | 122.6852 | 0.83313 | 3.3005 | 18.8553 | 122.6898 | -122.937 | -122.818
3505.9062 | 122.9233 | -3.6026 | 119.0872 | -0.041657 | 0.0045118 | 0.0023862 | 0.0098823 | -0.0068936 | 0.055463 | 0.086297 | -2.7237 | 119.0048 | -4.1885 | 119.2337 | 15.3397 | 0.3067 | 118.7714 | 6.4911 | 119.0186 | -3.8177 | -0.58594 | -0.082397 | 0.87891 | 122.8363 | -103.7476 | -0.21515 | -0.068664 | 1.4648 | 122.374 | 10.0937 | 18.9423 | 122.6074 | 0.87891 | 122.6212 | 3.9093 | -0.21515 | 122.6074 | 0.87891 | 3.9093 | 18.9423 | 122.6212 | -123.2758 | -122.905
3506.9062 | 122.9095 | -3.5797 | 119.1696 | 0.68314 | 0.0045118 | 0.0051632 | 0.010309 | -0.004971 | 0.057172 | 0.083307 | -2.5864 | 119.2337 | -3.8589 | 119.3481 | 15.3397 | 0.19684 | 118.6981 | 6.3629 | 119.0689 | -3.8727 | -0.27924 | 0.064087 | 0.99335 | 122.9279 | -103.83 | -0.29297 | -0.10071 | 1.2726 | 122.2778 | 9.9426 | 18.9194 | 122.8134 | 0.99335 | 122.6486 | 3.7765 | -0.29297 | 122.8134 | 0.99335 | 3.7765 | 18.9194 | 122.6486 | -123.0286 | -123.0423
3507.9062 | 122.9187 | -3.5751 | 119.1101 | 0.14908 | 0.0034436 | -0.0018862 | 0.010737 | -0.004971 | 0.054609 | 0.084161 | -2.6688 | 119.1925 | -3.8681 | 119.3756 | 15.2985 | 0.018311 | 118.9087 | 6.0654 | 119.165 | -3.8177 | -0.29297 | 0.082398 | 0.90637 | 122.9507 | -103.8116 | -0.24262 | 0.054932 | 1.1993 | 122.4838 | 9.6405 | 18.8736 | 122.7676 | 0.90637 | 122.7402 | 3.5934 | -0.24262 | 122.7676 | 0.90637 | 3.5934 | 18.8736 | 122.7402 | -122.9782 | -122.9279
3508.9062 | 122.8821 | -3.3234 | 119.3985 | -0.072174 | 0.0051526 | 0.0040952 | 0.0088141 | -0.0088162 | 0.055677 | 0.081384 | -2.3758 | 119.4534 | -3.6621 | 119.664 | 15.3351 | -0.52643 | 119.2566 | 5.452 | 119.4214 | -3.5431 | -0.33874 | 0.054931 | 0.94757 | 122.9874 | -104.0634 | -0.21973 | 0.022888 | 1.2863 | 122.58 | 8.7753 | 18.6584 | 122.7768 | 0.94757 | 122.7448 | 2.7969 | -0.21973 | 122.7768 | 0.94757 | 2.7969 | 18.6584 | 122.7448 | -123.0606 | -122.9416
3509.9062 | 122.8775 | -25.7538 | 96.7667 | 0.14145 | 0.0060072 | 0.0051632 | 0.90133 | -0.0056118 | 0.044995 | 0.95681 | -25.1083 | 96.7529 | -26.1612 | 96.9864 | 12.7853 | 11.7554 | 96.405 | -2.861 | 96.698 | -25.9918 | -0.40741 | -0.013733 | 0.64545 | 122.7402 | -83.9813 | -0.23804 | -0.068665 | 1.0529 | 122.1588 | 22.8928 | 38.5391 | 122.5067 | 0.64545 | 122.4518 | 37.5092 | -0.23804 | 122.5067 | 0.64545 | 37.5092 | 38.5391 | 122.4518 | -122.9279 | -122.7585
3510.9219 | 122.7539 | -34.0668 | 89.2136 | -0.53757 | 0.00023916 | 0.0034544 | 1.4134 | -0.0077482 | 0.042432 | 1.3729 | -34.5062 | 87.355 | -35.4309 | 88.266 | 11.7462 | 42.8787 | 87.1857 | -7.1457 | 87.5839 | -34.964 | -1.3641 | -1.8585 | -0.43945 | 122.3328 | -77.4673 | -0.89722 | -1.6296 | 0.92468 | 121.2524 | 26.9211 | 45.813 | 121.4218 | -0.43945 | 121.6507 | 76.9455 | -0.89722 | 121.4218 | -0.43945 | 76.9455 | 45.813 | 121.6507 | -124.6445 | -124.1776
3511.9062 | 122.4976 | -47.8134 | 75.1007 | 0.1796 | 0.0028028 | 0.0034544 | 1.9795 | -0.0062528 | 0.034101 | 1.8754 | -45.1904 | 75.206 | -47.7036 | 75.032 | 10.1166 | 33.6868 | 74.1074 | -13.7924 | 74.3271 | -48.1155 | 0.10986 | 0.10529 | 2.623 | 122.8455 | -64.9841 | -0.30212 | -0.77362 | 2.5131 | 121.9208 | 34.021 | 57.93 | 123.0194 | 2.623 | 122.1405 | 81.5002 | -0.30212 | 123.0194 | 2.623 | 81.5002 | 57.93 | 122.1405 | -122.8043 | -123.2162
3512.9062 | 122.6532 | -46.55 | 75.8606 | -0.10269 | 0.0030164 | -0.0010318 | 2.9562 | -0.0088162 | 0.034314 | 3.023 | -45.1035 | 76.3092 | -46.3165 | 75.6958 | 11.0367 | 33.1146 | 74.3362 | -16.6489 | 75.3479 | -46.3898 | 0.23346 | 0.44861 | 1.4465 | 122.2458 | -64.8239 | 0.16022 | -0.5127 | 1.2131 | 120.8862 | 29.9011 | 57.5867 | 122.8592 | 1.4465 | 121.8979 | 79.6646 | 0.16022 | 122.8592 | 1.4465 | 79.6646 | 57.5867 | 121.8979 | -122.1771 | -122.2504
3513.9062 | 122.5983 | -5.8548 | 116.423 | 0.1796 | 0.0023756 | 0.0011044 | 0.56787 | -0.0056118 | 0.053754 | 0.62142 | -6.871 | 114.4592 | -8.4686 | 116.6885 | 16.0767 | 3.8086 | 108.7875 | 4.0192 | 116.3269 | -6.0425 | -2.6138 | -1.9638 | -1.0162 | 122.5433 | -100.3464 | -0.18768 | -0.096131 | 1.5976 | 114.6423 | 9.874 | 21.9315 | 120.314 | -1.0162 | 122.1817 | 9.6634 | -0.18768 | 120.314 | -1.0162 | 9.6634 | 21.9315 | 122.1817 | -124.8917 | -122.4655
3514.9062 | 122.4701 | -17.807 | 104.3976 | 0.18723 | 0.0025892 | 0.0070858 | 3.0623 | -0.0034756 | 0.049268 | 3.0516 | -17.3447 | 104.2694 | -18.2739 | 104.3335 | 14.4241 | 43.9957 | 103.5965 | 0.29755 | 104.1092 | -17.8299 | -0.46692 | -0.12817 | 0.46234 | 122.1405 | -89.9734 | -0.022888 | -0.28839 | 0.92926 | 121.4035 | 18.1046 | 32.2311 | 122.0764 | 0.46234 | 121.9162 | 61.8027 | -0.022888 | 122.0764 | 0.46234 | 61.8027 | 32.2311 | 121.9162 | -122.6715 | -122.2275
3515.9062 | 122.4426 | -20.0867 | 101.5137 | -0.11795 | 0.00023916 | 0.0028134 | 3.2356 | -0.0077482 | 0.047986 | 3.4212 | -18.8461 | 102.2827 | -20.0409 | 100.1816 | 13.4766 | 55.9204 | 102.3788 | -1.2177 | 102.2003 | -19.5374 | 0.045776 | 0.76904 | 1.2405 | 120.2682 | -88.0371 | 0.54932 | 0.68664 | 1.1948 | 122.4655 | 18.869 | 33.5632 | 122.3694 | 1.2405 | 122.287 | 76.0071 | 0.54932 | 122.3694 | 1.2405 | 76.0071 | 33.5632 | 122.287 | -121.5546 | -121.051
3516.9062 | 122.2458 | -33.3893 | 88.6002 | 0.072784 | 0.002162 | 0.003668 | 2.2264 | -0.0051846 | 0.042646 | 2.0967 | -33.6914 | 87.2589 | -35.0647 | 89.5111 | 12.6251 | 61.4273 | 88.7009 | -4.0421 | 89.003 | -32.8354 | -1.6754 | -1.3412 | -0.30212 | 122.9004 | -75.975 | 0.55389 | 0.40283 | 1.3733 | 122.0901 | 29.3472 | 46.0144 | 120.6482 | -0.30212 | 122.3923 | 94.8166 | 0.55389 | 120.6482 | -0.30212 | 94.8166 | 46.0144 | 122.3923 | -123.6649 | -121.4355
3517.9062 | 121.9986 | -52.2034 | 69.5251 | 0.24826 | 0.0038708 | 0.0023862 | 3.5424 | -0.004971 | 0.011884 | 3.6709 | -52.0935 | 68.779 | -53.2516 | 69.3054 | 49.3927 | 69.3741 | 65.7623 | -22.6868 | 69.2459 | -52.0752 | -1.0483 | -0.74615 | 0.10986 | 121.5088 | -20.1324 | 0.12817 | -0.27923 | 1.1581 | 117.9657 | 29.5166 | 101.5961 | 120.9824 | 0.10986 | 121.4493 | 121.5775 | 0.12817 | 120.9824 | 0.10986 | 121.5775 | 101.5961 | 121.4493 | -122.7768 | -121.6003
3518.9062 | 122.5479 | -32.341 | 88.2385 | 0.14145 | 0.0036572 | 0.0040952 | 0.64199 | -0.0036892 | 0.055249 | 0.66842 | -20.668 | 100.6714 | -21.6202 | 90.6967 | 0.73242 | 93.0313 | -2.916 | -1.1536 | 92.4957 | -30.2856 | 10.7208 | 12.4329 | 11.673 | 123.0377 | -87.5061 | 2.0554 | 4.2572 | 0.95215 | 29.425 | 31.1874 | 33.0734 | 133.0124 | 11.673 | 124.8367 | 125.3723 | 2.0554 | 133.0124 | 11.673 | 125.3723 | 33.0734 | 124.8367 | -109.8587 | -118.5242
3519.9062 | 95.5673 | -78.5568 | 38.8046 | 0.22537 | 0.02267 | 0.014135 | 0.013941 | -0.003903 | 0.054609 | 0.072625 | -53.7689 | 57.0145 | -60.0586 | 92.7246 | -0.027466 | 0.09613 | -0.082397 | 0.21515 | 75.2975 | -59.2575 | 18.4982 | 18.2098 | 24.7879 | 171.2814 | -38.8321 | 19.2993 | 36.4929 | 6.2897 | 78.4744 | 78.772 | 78.5294 | 135.5713 | 24.7879 | 153.8544 | 78.653 | 19.2993 | 135.5713 | 24.7879 | 78.653 | 78.5294 | 153.8544 | -98.8632 | -98.0621
3520.9062 | 122.0993 | -120.9503 | 1.0757 | 0.1796 | 0.97201 | 0.97715 | 0.029963 | -0.0030484 | 0.0033389 | 0.028192 | -91.8365 | 0.59967 | -121.3806 | 1.2177 | 0.091553 | 0.44861 | -0.1236 | 0.18768 | 1.1627 | -121.1243 | -0.4303 | -0.47607 | 29.1138 | 122.168 | -0.98419 | -0.17395 | 0.086975 | 29.5441 | 120.8267 | 121.138 | 121.0419 | 121.55 | 29.1138 | 122.113 | 121.3989 | -0.17395 | 121.55 | 29.1138 | 121.3989 | 121.0419 | 122.113 | -122.4564 | -122.2
3521.9062 | 122.0993 | -121.3074 | 0.70496 | 0.19485 | 1.2034 | 1.1957 | 0.022272 | -0.0043302 | 0.00098914 | 0.0096067 | -92.0425 | 0.52185 | -121.5042 | 0.44861 | 0.11444 | 0.21515 | -0.082397 | 0.24261 | 0.74158 | -121.5546 | -0.19684 | -0.18311 | 29.2648 | 121.756 | -0.59052 | -0.24719 | 0.036621 | 29.4617 | 121.225 | 121.55 | 121.4218 | 121.8292 | 29.2648 | 122.049 | 121.5225 | -0.24719 | 121.8292 | 29.2648 | 121.5225 | 121.4218 | 122.049 | -122.2092 | -122.2595
3522.9062 | 122.1542 | -121.1472 | 0.8606 | -0.034027 | 1.1709 | 1.2311 | 0.021204 | -0.0060392 | 0.00098914 | 0.0070431 | -91.2918 | 0.67749 | -121.3577 | 0.50812 | 0.16937 | 0.16479 | 0.32959 | 0.3891 | 0.89264 | -121.4447 | -0.21057 | -0.18311 | 29.8553 | 121.6553 | -0.69122 | -0.29755 | 0.032043 | 30.0659 | 121.4767 | 121.5363 | 121.3165 | 121.8246 | 29.8553 | 122.0398 | 121.312 | -0.29755 | 121.8246 | 29.8553 | 121.312 | 121.3165 | 122.0398 | -122.2183 | -122.3053
3523.9062 | 122.1634 | -121.1014 | 0.93842 | 0.22537 | 1.4377 | 1.4439 | 0.022913 | -0.0064664 | 0.00034814 | 0.0096067 | -90.7974 | 0.71411 | -121.2708 | 0.37079 | 0.082397 | 0.19684 | 0 | 0.24261 | 0.94757 | -121.3669 | -0.16937 | -0.2243 | 30.304 | 121.4722 | -0.85602 | -0.2655 | 0.009155 | 30.4733 | 121.1014 | 121.344 | 121.1838 | 121.8155 | 30.304 | 122.0489 | 121.2982 | -0.2655 | 121.8155 | 30.304 | 121.2982 | 121.1838 | 122.0489 | -122.2092 | -122.3053
3524.9062 | 122.2321 | -120.9961 | 1.1261 | -0.45364 | 0.008357 | 0.014349 | 0.021845 | -0.0081754 | 0.0012027 | 0.010034 | -90.39 | 1.0071 | -121.3348 | 0.31128 | 0.059509 | 0.16022 | 0.022888 | 0.24719 | 1.1215 | -121.257 | -0.33875 | -0.11902 | 30.6061 | 121.3074 | -1.0666 | -0.26093 | -0.004578 | 30.9448 | 121.019 | 121.2433 | 121.0556 | 122.0032 | 30.6061 | 122.1176 | 121.1563 | -0.26093 | 122.0032 | 30.6061 | 121.1563 | 121.0556 | 122.1176 | -122.4609 | -122.3831
3525.9062 | 122.3373 | -120.8725 | 1.2131 | -0.095062 | 0.0098524 | 0.0092222 | 0.022486 | -0.0088162 | -0.00071986 | 0.0089657 | -90.0467 | 1.1856 | -121.1792 | 0.3891 | 0.14648 | 0.25177 | 0 | 0.33417 | 1.2497 | -121.1792 | -0.3067 | -0.027466 | 30.8258 | 121.2616 | -1.0666 | -0.3067 | 0.036621 | 31.1325 | 120.8725 | 121.2067 | 121.019 | 122.0581 | 30.8258 | 122.1222 | 121.1243 | -0.3067 | 122.0581 | 30.8258 | 121.1243 | 121.019 | 122.1222 | -122.3923 | -122.3923
3526.9062 | 122.2778 | -120.845 | 1.2909 | 0.16434 | 0.0096388 | 0.012213 | 0.025263 | -0.0060392 | 0.0016299 | 0.0076841 | -89.8682 | 1.2177 | -121.1288 | 0.33875 | 0.086975 | 0.21057 | 0 | 0.25635 | 1.3092 | -121.1288 | -0.28381 | -0.073243 | 30.9769 | 121.1838 | -1.2039 | -0.28381 | 0.01831 | 31.2607 | 120.845 | 121.1014 | 120.932 | 122.0627 | 30.9769 | 122.1542 | 121.0556 | -0.28381 | 122.0627 | 30.9769 | 121.0556 | 120.932 | 122.1542 | -122.4197 | -122.4197
3527.9062 | 122.3145 | -120.7489 | 1.2772 | -0.23239 | 0.010493 | 0.016058 | 0.025477 | -0.0064664 | -0.0013609 | 0.0076841 | -89.7491 | 1.2177 | -121.1884 | 0.31586 | 0.10986 | 0.1831 | 0.086975 | 0.29297 | 1.3092 | -121.2067 | -0.43945 | -0.05951 | 30.9998 | 121.0648 | -1.1673 | -0.45776 | 0.032043 | 31.4392 | 120.8359 | 121.0419 | 120.8588 | 121.9666 | 30.9998 | 122.0581 | 120.932 | -0.45776 | 121.9666 | 30.9998 | 120.932 | 120.8588 | 122.0581 | -122.4655 | -122.4838
3528.9062 | 122.3373 | -120.8405 | 1.3046 | 0.18723 | 0.011348 | 0.011999 | 0.027399 | -0.0056118 | -0.0017881 | 0.0081113 | -89.5981 | 1.2039 | -121.1563 | 0.31586 | 0.1236 | 0.24261 | -0.013733 | 0.28381 | 1.3184 | -121.1426 | -0.31586 | -0.10071 | 31.2424 | 121.1563 | -1.181 | -0.30212 | 0.013733 | 31.5582 | 120.8267 | 121.1243 | 120.9641 | 122.0444 | 31.2424 | 122.1588 | 121.0831 | -0.30212 | 122.0444 | 31.2424 | 121.0831 | 120.9641 | 122.1588 | -122.4609 | -122.4472
3529.9062 | 122.3694 | -120.9915 | 1.1765 | 0.17197 | 0.010493 | 0.012426 | 0.026331 | -0.0056118 | -0.0017881 | 0.0083249 | -89.621 | 1.1032 | -121.2936 | 0.37079 | 0.12817 | 0.25177 | -0.022888 | 0.28381 | 1.2085 | -121.257 | -0.30212 | -0.073243 | 31.3705 | 121.3623 | -1.0483 | -0.2655 | 0.032043 | 31.6727 | 120.9686 | 121.2753 | 121.1197 | 122.0947 | 31.3705 | 122.2 | 121.2433 | -0.2655 | 122.0947 | 31.3705 | 121.2433 | 121.1197 | 122.2 | -122.4701 | -122.4335
3530.9062 | 122.4014 | -121.0052 | 1.1902 | -0.079803 | 0.009425 | 0.011786 | 0.024195 | -0.0081754 | -0.00071986 | 0.0059751 | -89.5889 | 1.0941 | -121.3257 | 0.34332 | 0.14191 | 0.27466 | 0.054932 | 0.32501 | 1.1948 | -121.2982 | -0.32043 | -0.096131 | 31.4163 | 121.3486 | -1.0483 | -0.29297 | 0.004577 | 31.7368 | 121.0602 | 121.3303 | 121.1472 | 122.0993 | 31.4163 | 122.2 | 121.2799 | -0.29297 | 122.0993 | 31.4163 | 121.2799 | 121.1472 | 122.2 | -122.5159 | -122.4884
3531.9062 | 122.3785 | -121.1014 | 1.0803 | 0.1796 | 0.0096388 | 0.010931 | 0.027399 | -0.0060392 | -0.00050626 | 0.0083249 | -89.5157 | 1.0162 | -121.3852 | 0.31586 | 0.10986 | 0.2655 | 0.004578 | 0.27924 | 1.0941 | -121.4127 | -0.28381 | -0.064087 | 31.5857 | 121.4172 | -0.97046 | -0.31128 | 0.013733 | 31.8695 | 121.106 | 121.3806 | 121.2112 | 122.1176 | 31.5857 | 122.1954 | 121.3669 | -0.31128 | 122.1176 | 31.5857 | 121.3669 | 121.2112 | 122.1954 | -122.4655 | -122.493
3532.9062 | 122.3923 | -121.17 | 1.0574 | -0.018768 | 0.0098524 | 0.012854 | 0.023554 | -0.0068936 | -0.00029266 | 0.0096067 | -89.4928 | 0.95673 | -121.4905 | 0.28381 | 0.11902 | 0.2655 | 0.064087 | 0.29297 | 1.0757 | -121.4767 | -0.32043 | -0.10071 | 31.6772 | 121.4539 | -0.93841 | -0.3067 | 0.018311 | 31.9977 | 121.2341 | 121.463 | 121.2891 | 122.1268 | 31.6772 | 122.2458 | 121.4355 | -0.3067 | 122.1268 | 31.6772 | 121.4355 | 121.2891 | 122.2458 | -122.5479 | -122.5342
3533.9062 | 122.3557 | -118.9362 | 3.1998 | 0.28641 | 0.013698 | 0.013922 | 0.025904 | -0.002194 | -0.0017881 | 0.010888 | -87.117 | 3.2043 | -119.2245 | 0.3479 | 0.15564 | 0.19684 | -0.082397 | 0.27008 | 3.2776 | -119.2291 | -0.28839 | 0.004578 | 31.8192 | 119.2841 | -3.0441 | -0.29297 | 0.07782 | 32.1075 | 118.8538 | 119.2062 | 119.0918 | 122.1405 | 31.8192 | 122.2137 | 119.133 | -0.29297 | 122.1405 | 31.8192 | 119.133 | 119.0918 | 122.2137 | -122.4243 | -122.4289
3534.9062 | 122.4197 | -120.694 | 1.5244 | 0.26352 | 0.013484 | 0.018622 | 0.02804 | -0.0028348 | -0.0011471 | 0.0093931 | -88.6871 | 1.4832 | -120.9641 | 0.25635 | 0.14648 | 0.20142 | -0.054932 | 0.2655 | 1.5564 | -120.9915 | -0.27008 | -0.041199 | 32.0068 | 120.9503 | -1.3779 | -0.29755 | 0.032043 | 32.2769 | 120.639 | 120.9595 | 120.8405 | 122.1771 | 32.0068 | 122.2504 | 120.8954 | -0.29755 | 122.1771 | 32.0068 | 120.8954 | 120.8405 | 122.2504 | -122.4884 | -122.5159
3535.9219 | 122.4426 | -120.7397 | 1.4786 | -0.13321 | 0.01092 | 0.014563 | 0.023768 | -0.0034756 | 0.00077554 | 0.0096067 | -88.71 | 1.4191 | -121.0464 | 0.28381 | 0.20599 | 0.24719 | -0.032043 | 0.37079 | 1.5015 | -121.0098 | -0.3067 | -0.05951 | 32.0297 | 121.0236 | -1.2726 | -0.27008 | 0.022888 | 32.3364 | 120.7077 | 121.1105 | 120.9457 | 122.1588 | 32.0297 | 122.2412 | 120.9869 | -0.27008 | 122.1588 | 32.0297 | 120.9869 | 120.9457 | 122.2412 | -122.525 | -122.4884
3536.9062 | 122.3785 | -120.7901 | 1.4694 | 0.13382 | 0.01028 | 0.010717 | 0.025477 | -0.0060392 | 0.00077554 | 0.010247 | -88.6734 | 1.4008 | -121.0464 | 0.20142 | 0.1236 | 0.17853 | 0.009155 | 0.26093 | 1.4923 | -121.0876 | -0.25635 | -0.068664 | 32.1167 | 120.9915 | -1.3458 | -0.29755 | 0.022889 | 32.373 | 120.7993 | 121.051 | 120.9137 | 122.1909 | 32.1167 | 122.2824 | 120.9686 | -0.29755 | 122.1909 | 32.1167 | 120.9686 | 120.9137 | 122.2824 | -122.5159 | -122.5571
3537.9062 | 122.4197 | -120.813 | 1.4236 | 0.1796 | 0.0098524 | 0.014776 | 0.025477 | -0.0064664 | -0.0013609 | 0.0072569 | -88.5681 | 1.3641 | -121.0739 | 0.22888 | 0.14191 | 0.20599 | -0.009155 | 0.26093 | 1.4374 | -121.1334 | -0.26093 | -0.059509 | 32.2449 | 121.0419 | -1.2817 | -0.32043 | 0.013733 | 32.5058 | 120.8038 | 121.0739 | 120.9549 | 122.1771 | 32.2449 | 122.2504 | 121.019 | -0.32043 | 122.1771 | 32.2449 | 121.019 | 120.9549 | 122.2504 | -122.4976 | -122.5571
3538.9062 | 122.4472 | -120.8313 | 1.4191 | -0.92667 | 0.013911 | 0.019476 | 0.028254 | -0.0019802 | -0.0011471 | 0.011956 | -88.4628 | 1.3138 | -121.1472 | 0.27924 | 0.16022 | 0.21057 | -0.059509 | 0.30212 | 1.4465 | -121.138 | -0.31586 | -0.10529 | 32.3685 | 121.1105 | -1.2589 | -0.3067 | 0.027466 | 32.6843 | 120.7718 | 121.1334 | 120.9915 | 122.1451 | 32.3685 | 122.2778 | 121.0419 | -0.3067 | 122.1451 | 32.3685 | 121.0419 | 120.9915 | 122.2778 | -122.5662 | -122.5571
3539.9062 | 122.4518 | -120.8313 | 1.4099 | -2.9561 | 0.009425 | 0.014349 | 0.024622 | -0.0056118 | -0.0017881 | 0.011102 | -88.2156 | 1.3458 | -121.1609 | 0.28839 | 0.21515 | 0.24719 | -0.013733 | 0.35706 | 1.4282 | -121.1334 | -0.32959 | -0.064087 | 32.6157 | 121.1197 | -1.1948 | -0.30212 | 0.018311 | 32.9453 | 120.8176 | 121.1884 | 121.0464 | 122.1771 | 32.6157 | 122.2595 | 121.0785 | -0.30212 | 122.1771 | 32.6157 | 121.0785 | 121.0464 | 122.2595 | -122.5708 | -122.5433
3540.9062 | 122.4518 | -120.8313 | 1.4053 | 0.19485 | 0.012416 | 0.01264 | 0.028254 | -0.003903 | -0.00093346 | 0.0098203 | -88.2065 | 1.3367 | -121.1334 | 0.27008 | 0.16479 | 0.22888 | -0.059509 | 0.3067 | 1.4053 | -121.1655 | -0.30212 | -0.068664 | 32.6248 | 121.1014 | -1.2405 | -0.33417 | 0 | 32.9269 | 120.7718 | 121.138 | 120.9961 | 122.168 | 32.6248 | 122.2366 | 121.0602 | -0.33417 | 122.168 | 32.6248 | 121.0602 | 120.9961 | 122.2366 | -122.5388 | -122.5708
3541.9062 | 122.3648 | -120.8679 | 1.4603 | -0.5452 | 0.014125 | 0.019049 | 0.033167 | -0.0030484 | -0.00071986 | 0.0083249 | -88.1424 | 1.4236 | -121.1517 | 0.16022 | 0.036621 | 0.10071 | 0.11444 | 0.16937 | 1.4694 | -121.2112 | -0.28381 | -0.036621 | 32.7255 | 121.0281 | -1.4236 | -0.34332 | 0.009155 | 33.0093 | 120.9824 | 121.0373 | 120.9045 | 122.2916 | 32.7255 | 122.3373 | 120.9686 | -0.34332 | 122.2916 | 32.7255 | 120.9686 | 120.9045 | 122.3373 | -122.612 | -122.6715
3542.9062 | 122.2916 | -120.8588 | 1.4923 | -0.17899 | 0.014125 | 0.014563 | 0.026117 | -0.0045438 | -0.0011471 | 0.0085385 | -87.9135 | 1.387 | -121.2112 | 0.16022 | 0.068665 | 0.09613 | 0.17395 | 0.36163 | 1.4877 | -121.1563 | -0.35248 | -0.10529 | 32.9453 | 121.019 | -1.4236 | -0.29755 | -0.004578 | 33.2977 | 121.0327 | 121.2204 | 120.9274 | 122.2458 | 32.9453 | 122.3465 | 120.9549 | -0.29755 | 122.2458 | 32.9453 | 120.9549 | 120.9274 | 122.3465 | -122.7036 | -122.6486
3543.9062 | 122.4792 | -120.8908 | 1.3596 | 0.20248 | 0.013057 | 0.018622 | 0.029749 | -0.0030484 | -0.00071986 | 0.0096067 | -87.6755 | 1.3275 | -121.2112 | 0.23346 | 0.13275 | 0.19226 | 0.004578 | 0.31128 | 1.3779 | -121.1838 | -0.32043 | -0.032043 | 33.2153 | 121.1243 | -1.2268 | -0.29297 | 0.018311 | 33.5358 | 120.8954 | 121.2021 | 121.0236 | 122.2183 | 33.2153 | 122.2687 | 121.0831 | -0.29297 | 122.2183 | 33.2153 | 121.0831 | 121.0236 | 122.2687 | -122.5708 | -122.5433
3544.9219 | 122.5159 | -120.8633 | 1.3779 | -0.17899 | 0.01092 | 0.017553 | 0.023127 | -0.0051846 | -0.0013609 | 0.0085385 | -87.5839 | 1.3138 | -121.225 | 0.27008 | 0.19684 | 0.24719 | 0.013733 | 0.39825 | 1.4053 | -121.1609 | -0.36163 | -0.064087 | 33.2794 | 121.1334 | -1.181 | -0.29755 | 0.027465 | 33.6411 | 120.8771 | 121.2616 | 121.0602 | 122.1771 | 33.2794 | 122.2687 | 121.1105 | -0.29755 | 122.1771 | 33.2794 | 121.1105 | 121.0602 | 122.2687 | -122.6028 | -122.5388
3545.9062 | 122.4747 | -120.8954 | 1.3687 | 0.24063 | 0.011561 | 0.018835 | 0.032526 | -0.00069859 | -0.00071986 | 0.0066159 | -87.529 | 1.3229 | -121.1884 | 0.36621 | 0.24719 | 0.22888 | -0.086975 | 0.36621 | 1.3596 | -121.2341 | -0.29297 | -0.045776 | 33.3664 | 121.2616 | -1.1215 | -0.33875 | -0.009155 | 33.6594 | 120.8084 | 121.2616 | 121.1426 | 122.2183 | 33.3664 | 122.2549 | 121.1243 | -0.33875 | 122.2183 | 33.3664 | 121.1243 | 121.1426 | 122.2549 | -122.5571 | -122.6028
3546.9062 | 122.5067 | -120.9412 | 1.3412 | 0.19485 | 0.013484 | 0.016485 | 0.028254 | -0.003262 | 0.0016299 | 0.0091795 | -87.5015 | 1.2909 | -121.2387 | 0.25635 | 0.15106 | 0.24261 | -0.009155 | 0.32959 | 1.387 | -121.257 | -0.29755 | -0.050354 | 33.4396 | 121.1975 | -1.1902 | -0.31586 | 0.045776 | 33.7372 | 120.932 | 121.2708 | 121.0922 | 122.2321 | 33.4396 | 122.3282 | 121.1838 | -0.31586 | 122.2321 | 33.4396 | 121.1838 | 121.0922 | 122.3282 | -122.58 | -122.5983
3547.9062 | 122.4747 | -120.9549 | 1.3229 | -0.17136 | 0.012416 | 0.016699 | 0.025049 | -0.0045438 | -0.00050626 | 0.010034 | -87.4741 | 1.2589 | -121.2296 | 0.26093 | 0.15564 | 0.13275 | 0.3891 | 0.44861 | 1.355 | -121.2936 | -0.27466 | -0.064087 | 33.4808 | 121.2158 | -1.1673 | -0.33875 | 0.032043 | 33.7555 | 121.344 | 121.4035 | 121.1105 | 122.2137 | 33.4808 | 122.3099 | 121.0876 | -0.33875 | 122.2137 | 33.4808 | 121.0876 | 121.1105 | 122.3099 | -122.5525 | -122.6166
3548.9062 | 122.4884 | -120.9915 | 1.3184 | 0.25589 | 0.012629 | 0.016272 | 0.030604 | -0.0034756 | 0.00013454 | 0.010675 | -87.5931 | 1.236 | -121.2616 | 0.25635 | 0.13275 | 0.2243 | -0.041199 | 0.33875 | 1.3458 | -121.3211 | -0.27008 | -0.082397 | 33.3984 | 121.2479 | -1.1856 | -0.32959 | 0.027466 | 33.6685 | 120.9503 | 121.3303 | 121.1243 | 122.2275 | 33.3984 | 122.3373 | 121.2158 | -0.32959 | 122.2275 | 33.3984 | 121.2158 | 121.1243 | 122.3373 | -122.58 | -122.6395
3549.9219 | 122.3877 | -121.051 | 1.3321 | -1.9261 | 0.01092 | 0.017126 | 0.030817 | -0.00668 | -0.00093346 | 0.0089657 | -87.6297 | 1.3275 | -121.2936 | 0.17853 | 0.086975 | 0.11902 | 0.19684 | 0.26093 | 1.3962 | -121.3486 | -0.24262 | -0.004577 | 33.4213 | 121.2296 | -1.2451 | -0.29755 | 0.064087 | 33.6639 | 121.2479 | 121.3119 | 121.138 | 122.3785 | 33.4213 | 122.4472 | 121.17 | -0.29755 | 122.3785 | 33.4213 | 121.17 | 121.138 | 122.4472 | -122.6257 | -122.6807
3550.9062 | 122.4564 | -121.019 | 1.2955 | 0.0041197 | 0.010707 | 0.013495 | 0.024622 | -0.0047574 | -0.0011471 | 0.010888 | -87.6846 | 1.2222 | -121.3486 | 0.21057 | 0.12817 | 0.19226 | 0.036621 | 0.31586 | 1.3275 | -121.3303 | -0.32959 | -0.073242 | 33.3344 | 121.2296 | -1.1673 | -0.31128 | 0.032044 | 33.6639 | 121.0556 | 121.3348 | 121.1472 | 122.2412 | 33.3344 | 122.3465 | 121.2112 | -0.31128 | 122.2412 | 33.3344 | 121.2112 | 121.1472 | 122.3465 | -122.644 | -122.6257
3551.9062 | 122.4976 | -120.9595 | 1.3229 | -1.2547 | 0.0096388 | 0.014776 | 0.028467 | -0.0064664 | -0.0011471 | 0.0083249 | -87.5931 | 1.2222 | -121.3028 | 0.26093 | 0.13275 | 0.23346 | -0.041199 | 0.33417 | 1.3092 | -121.3348 | -0.34332 | -0.10071 | 33.3664 | 121.2204 | -1.1902 | -0.37537 | -0.013733 | 33.7097 | 120.9183 | 121.2936 | 121.0922 | 122.1817 | 33.3664 | 122.2687 | 121.1929 | -0.37537 | 122.1817 | 33.3664 | 121.1929 | 121.0922 | 122.2687 | -122.6257 | -122.6578
3552.9062 | 122.4655 | -121.0052 | 1.3275 | 0.065155 | 0.011348 | 0.015631 | 0.027186 | -0.0064664 | 0.00056194 | 0.0081113 | -87.6984 | 1.1993 | -121.3165 | 0.20142 | 0.11444 | 0.18768 | 0.050354 | 0.31586 | 1.3184 | -121.376 | -0.31128 | -0.12817 | 33.3069 | 121.2067 | -1.2131 | -0.37079 | -0.009156 | 33.6182 | 121.0556 | 121.3211 | 121.1197 | 122.2046 | 33.3069 | 122.3236 | 121.1929 | -0.37079 | 122.2046 | 33.3069 | 121.1929 | 121.1197 | 122.3236 | -122.644 | -122.7036
3553.9062 | 122.493 | -121.051 | 1.3046 | 0.24063 | 0.014766 | 0.018622 | 0.033167 | -0.004971 | 0.00077554 | 0.0089657 | -87.7213 | 1.2405 | -121.3669 | 0.19684 | 0.091553 | 0.16479 | 0.032043 | 0.3067 | 1.3092 | -121.376 | -0.31586 | -0.064086 | 33.3298 | 121.2479 | -1.2131 | -0.32501 | 0.004578 | 33.6456 | 121.0831 | 121.3577 | 121.1426 | 122.2916 | 33.3298 | 122.3602 | 121.2158 | -0.32501 | 122.2916 | 33.3298 | 121.2158 | 121.1426 | 122.3602 | -122.6715 | -122.6807
3554.9062 | 122.4426 | -121.1014 | 1.268 | 0.233 | 0.015193 | 0.018622 | 0.03039 | -0.002194 | -0.00050626 | 0.0098203 | -87.8128 | 1.2405 | -121.3806 | 0.19684 | 0.068665 | 0.15106 | 0.068665 | 0.27924 | 1.3 | -121.4081 | -0.27924 | -0.027465 | 33.2886 | 121.2982 | -1.1993 | -0.3067 | 0.032044 | 33.5678 | 121.17 | 121.3806 | 121.17 | 122.3419 | 33.2886 | 122.4014 | 121.2524 | -0.3067 | 122.3419 | 33.2886 | 121.2524 | 121.17 | 122.4014 | -122.6486 | -122.6761
3555.9062 | 122.4792 | -121.1243 | 1.1902 | 0.049896 | 0.012629 | 0.015204 | 0.024408 | -0.0051846 | -0.00029266 | 0.010461 | -87.9318 | 1.1719 | -121.376 | 0.19226 | 0.11444 | -0.032043 | -0.045776 | 0.15564 | 1.2405 | -121.4676 | -0.25177 | -0.018311 | 33.1924 | 121.3165 | -1.0757 | -0.34332 | 0.050354 | 33.4442 | 121.0785 | 121.2799 | 121.2387 | 122.2961 | 33.1924 | 122.3648 | 121.0922 | -0.34332 | 122.2961 | 33.1924 | 121.0922 | 121.2387 | 122.3648 | -122.5662 | -122.6578
3556.9062 | 122.5388 | -121.0876 | 1.2268 | 0.21774 | 0.015834 | 0.016058 | 0.029963 | -0.003903 | -0.00071986 | 0.0089657 | -87.7167 | 1.1581 | -121.4172 | 0.25177 | 0.12817 | 0.21973 | 0 | 0.33417 | 1.2634 | -121.4218 | -0.32959 | -0.068665 | 33.371 | 121.3394 | -1.0986 | -0.33417 | 0.036621 | 33.7006 | 121.0876 | 121.4218 | 121.2158 | 122.2458 | 33.371 | 122.3511 | 121.3074 | -0.33417 | 122.2458 | 33.371 | 121.3074 | 121.2158 | 122.3511 | -122.644 | -122.6486
3557.9062 | 122.4976 | -120.8633 | 1.5106 | -0.34683 | 0.010066 | 0.015631 | 0.024408 | -0.0068936 | 0.00098914 | 0.0076841 | -87.4054 | 1.3779 | -121.1792 | 0.20142 | 0.10986 | 0.19226 | 0.10071 | 0.34332 | 1.5381 | -121.2021 | -0.31586 | -0.13275 | 33.4579 | 121.0648 | -1.4008 | -0.33875 | 0.027466 | 33.7738 | 120.9641 | 121.2067 | 120.9732 | 122.2412 | 33.4579 | 122.4014 | 121.0556 | -0.33875 | 122.2412 | 33.4579 | 121.0556 | 120.9732 | 122.4014 | -122.6898 | -122.7127
3558.9062 | 122.5067 | -120.8267 | 1.5472 | 0.21774 | 0.014979 | 0.014135 | 0.03039 | -0.0026212 | -0.00050626 | 0.0089657 | -87.3138 | 1.4832 | -121.1517 | 0.1831 | 0.064087 | 0.14191 | 0.082397 | 0.28839 | 1.5518 | -121.17 | -0.32501 | -0.064087 | 33.5129 | 121.0098 | -1.4832 | -0.34332 | 0.004578 | 33.8379 | 120.9091 | 121.1151 | 120.8908 | 122.3099 | 33.5129 | 122.3785 | 120.9686 | -0.34332 | 122.3099 | 33.5129 | 120.9686 | 120.8908 | 122.3785 | -122.699 | -122.7173
3559.9062 | 122.4564 | -120.7764 | 1.6113 | 0.16434 | 0.01562 | 0.019476 | 0.032313 | -0.0058256 | -0.00050626 | 0.010247 | -87.2086 | 1.5656 | -121.0785 | 0.17395 | 0.054932 | 0.11902 | 0.13275 | 0.27008 | 1.6342 | -121.0922 | -0.30212 | -0.045776 | 33.5678 | 120.9503 | -1.5564 | -0.31586 | 0.022888 | 33.8699 | 120.9091 | 121.0464 | 120.8313 | 122.3419 | 33.5678 | 122.4106 | 120.8954 | -0.31586 | 122.3419 | 33.5678 | 120.8954 | 120.8313 | 122.4106 | -122.6898 | -122.7036
3560.9062 | 122.493 | -120.7397 | 1.6022 | 0.24063 | 0.01327 | 0.01969 | 0.029322 | -0.0058256 | -7.9062e-05 | 0.0076841 | -87.1994 | 1.5381 | -121.0648 | 0.2243 | 0.091553 | 0.19684 | 0.091553 | 0.35248 | 1.6205 | -121.1426 | -0.32501 | -0.064087 | 33.5403 | 120.9641 | -1.5106 | -0.40283 | 0.01831 | 33.8654 | 120.8313 | 121.0922 | 120.8313 | 122.2778 | 33.5403 | 122.3602 | 120.9366 | -0.40283 | 122.2778 | 33.5403 | 120.9366 | 120.8313 | 122.3602 | -122.6669 | -122.7448
3561.9062 | 122.4197 | -120.7352 | 1.6525 | 0.11856 | 0.015193 | 0.018622 | 0.033381 | -0.0036892 | -0.0011471 | 0.010034 | -87.1674 | 1.6251 | -121.0144 | 0.11902 | 0.022888 | 0.064087 | 0.24719 | 0.23346 | 1.7029 | -121.0922 | -0.27924 | -0.027466 | 33.5678 | 120.8542 | -1.6296 | -0.35706 | 0.050354 | 33.847 | 120.9824 | 120.9686 | 120.7581 | 122.3602 | 33.5678 | 122.438 | 120.7993 | -0.35706 | 122.3602 | 33.5678 | 120.7993 | 120.7581 | 122.438 | -122.6669 | -122.7448
3562.9062 | 122.4655 | -120.8359 | 1.5564 | 0.18723 | 0.013484 | 0.016485 | 0.029535 | -0.0028348 | 0.00034814 | 0.0096067 | -87.3047 | 1.5152 | -121.1288 | 0.15564 | 0.073242 | 0.1236 | 0.15106 | 0.27466 | 1.5656 | -121.1563 | -0.29297 | -0.041198 | 33.5312 | 120.9915 | -1.4832 | -0.32044 | 0.009156 | 33.8242 | 120.9869 | 121.1105 | 120.9091 | 122.3511 | 33.5312 | 122.4014 | 120.9595 | -0.32044 | 122.3511 | 33.5312 | 120.9595 | 120.9091 | 122.4014 | -122.6852 | -122.7127
3563.9062 | 122.4426 | -120.8542 | 1.5564 | 0.1796 | 0.014338 | 0.016699 | 0.031031 | -0.002194 | -0.0015745 | 0.010034 | -87.2589 | 1.5289 | -121.1609 | 0.14191 | 0.032043 | 0.10986 | 0.20599 | 0.25635 | 1.5793 | -121.1792 | -0.3067 | -0.027465 | 33.5953 | 120.9961 | -1.5244 | -0.32501 | 0.022889 | 33.902 | 121.0602 | 121.1105 | 120.8862 | 122.3831 | 33.5953 | 122.4335 | 120.9641 | -0.32501 | 122.3831 | 33.5953 | 120.9641 | 120.8862 | 122.4335 | -122.7173 | -122.7356
3564.9062 | 122.4335 | -120.7535 | 1.6525 | 0.33218 | 0.014766 | 0.019476 | 0.028895 | -0.0011258 | 0.00013454 | 0.010034 | -87.0941 | 1.6205 | -121.051 | 0.13275 | 0.036621 | 0.091553 | 0.2243 | 0.24261 | 1.6846 | -121.0831 | -0.29755 | -0.032044 | 33.6594 | 120.8862 | -1.6159 | -0.32959 | 0.032043 | 33.9569 | 120.9778 | 120.9961 | 120.7901 | 122.374 | 33.6594 | 122.438 | 120.845 | -0.32959 | 122.374 | 33.6594 | 120.845 | 120.7901 | 122.438 | -122.7036 | -122.7356
3565.9062 | 122.5571 | -120.6802 | 1.6663 | -0.10269 | 0.012843 | 0.013922 | 0.023554 | -0.0036892 | -0.00071986 | 0.010675 | -86.9476 | 1.5747 | -120.9961 | 0.27924 | 0.11444 | 0.2655 | 0.064087 | 0.39368 | 1.6754 | -120.9824 | -0.31586 | -0.091553 | 33.7326 | 120.9595 | -1.5518 | -0.30212 | 0.009155 | 34.0485 | 120.7443 | 121.0739 | 120.7947 | 122.2549 | 33.7326 | 122.3557 | 120.9457 | -0.30212 | 122.2549 | 33.7326 | 120.9457 | 120.7947 | 122.3557 | -122.6624 | -122.6486
3566.9062 | 122.2412 | -120.7581 | 1.5976 | 0.1033 | 0.016688 | 0.01969 | 0.031031 | -0.0028348 | 0.00098914 | 0.010034 | -86.8973 | 1.5564 | -121.1197 | 0.21515 | -0.027466 | 0.10986 | 0.22888 | 0.23804 | 1.6388 | -121.17 | -0.36163 | -0.041199 | 33.8608 | 120.9732 | -1.6251 | -0.41199 | 0.041199 | 34.2224 | 120.9869 | 120.9961 | 120.7306 | 122.3145 | 33.8608 | 122.3969 | 120.8679 | -0.41199 | 122.3145 | 33.8608 | 120.8679 | 120.7306 | 122.3969 | -122.7173 | -122.7676
3567.9062 | 122.438 | -120.6802 | 1.7166 | -0.58334 | 0.013911 | 0.021826 | 0.029749 | -0.0019802 | -0.0011471 | 0.0093931 | -86.6043 | 1.6983 | -121.0052 | 0.23346 | -0.004578 | 0.11902 | 0.24261 | 0.25177 | 1.767 | -120.9915 | -0.32501 | -0.018311 | 34.0759 | 120.9137 | -1.7212 | -0.31128 | 0.050354 | 34.4009 | 120.9229 | 120.932 | 120.6757 | 122.3785 | 34.0759 | 122.4472 | 120.7993 | -0.31128 | 122.3785 | 34.0759 | 120.7993 | 120.6757 | 122.4472 | -122.7219 | -122.7081
3568.9062 | 122.4655 | -120.7077 | 1.7075 | -0.0035098 | 0.013911 | 0.017126 | 0.029322 | -0.002194 | -0.0015745 | 0.011529 | -86.3892 | 1.6663 | -121.0098 | 0.31586 | 0.041199 | 0.19226 | 0.20599 | 0.31586 | 1.7303 | -121.051 | -0.30212 | -0.041198 | 34.3185 | 121.0236 | -1.6663 | -0.34332 | 0.022889 | 34.6207 | 120.9137 | 121.0236 | 120.7489 | 122.374 | 34.3185 | 122.438 | 120.9 | -0.34332 | 122.374 | 34.3185 | 120.9 | 120.7489 | 122.438 | -122.7173 | -122.7585
3569.9062 | 122.4747 | -120.6482 | 1.7807 | -0.095062 | 0.014766 | 0.017981 | 0.030176 | -0.00048499 | -0.00093346 | 0.0072569 | -86.1877 | 1.767 | -120.9366 | 0.32501 | 0.050354 | 0.19684 | 0.21057 | 0.33875 | 1.8173 | -120.9595 | -0.28839 | -0.013733 | 34.4604 | 120.9732 | -1.7303 | -0.31128 | 0.036621 | 34.7488 | 120.8588 | 120.9869 | 120.6985 | 122.4152 | 34.4604 | 122.4655 | 120.845 | -0.31128 | 122.4152 | 34.4604 | 120.845 | 120.6985 | 122.4655 | -122.7173 | -122.7402
3570.9062 | 122.5388 | -120.7077 | 1.6388 | -0.0035098 | 0.014125 | 0.016913 | 0.024622 | -0.0011258 | -7.9062e-05 | 0.011102 | -86.1694 | 1.6205 | -120.9824 | 0.36163 | 0.10529 | 0.28381 | 0.07782 | 0.39368 | 1.6846 | -120.9824 | -0.27466 | -0.018311 | 34.5383 | 121.0693 | -1.5335 | -0.27466 | 0.045776 | 34.8129 | 120.7855 | 121.1014 | 120.813 | 122.3282 | 34.5383 | 122.3923 | 120.9915 | -0.27466 | 122.3282 | 34.5383 | 120.9915 | 120.813 | 122.3923 | -122.6212 | -122.6212
3571.9062 | 122.4472 | -120.607 | 1.8127 | 0.027008 | 0.015193 | 0.020971 | 0.029963 | -0.0024076 | -0.00071986 | 0.011529 | -86.1191 | 1.7944 | -120.9137 | 0.25177 | 0 | 0.13275 | 0.27008 | 0.25177 | 1.8402 | -120.9641 | -0.3067 | -0.01831 | 34.4879 | 120.8588 | -1.8127 | -0.35706 | 0.027466 | 34.7946 | 120.8771 | 120.8588 | 120.607 | 122.4014 | 34.4879 | 122.4472 | 120.7397 | -0.35706 | 122.4014 | 34.4879 | 120.7397 | 120.607 | 122.4472 | -122.7264 | -122.7768
3572.9062 | 122.4747 | -120.6116 | 1.8219 | 0.18723 | 0.014979 | 0.019903 | 0.029108 | 0.00036961 | -0.0026425 | 0.0089657 | -86.0687 | 1.7761 | -120.9045 | 0.25635 | 0.009155 | 0.15106 | 0.22888 | 0.28381 | 1.8814 | -120.9549 | -0.29297 | -0.045776 | 34.5428 | 120.8679 | -1.8127 | -0.34332 | 0.05951 | 34.8358 | 120.8405 | 120.8954 | 120.6207 | 122.3877 | 34.5428 | 122.493 | 120.7626 | -0.34332 | 122.3877 | 34.5428 | 120.7626 | 120.6207 | 122.493 | -122.7264 | -122.7768
3573.9062 | 122.4609 | -120.7031 | 1.7624 | 0.1033 | 0.016688 | 0.019049 | 0.029535 | -0.0013394 | 0.00077554 | 0.0087521 | -86.0596 | 1.7258 | -120.9732 | 0.24261 | -0.027466 | 0.10986 | 0.28381 | 0.23804 | 1.7899 | -121.019 | -0.27008 | -0.036621 | 34.6436 | 120.9457 | -1.7899 | -0.31586 | 0.027466 | 34.9136 | 120.9869 | 120.9412 | 120.6757 | 122.4289 | 34.6436 | 122.493 | 120.813 | -0.31586 | 122.4289 | 34.6436 | 120.813 | 120.6757 | 122.493 | -122.7356 | -122.7814
3574.9062 | 122.4335 | -120.6757 | 1.7624 | 0.54581 | 0.016475 | 0.017767 | 0.029108 | -0.0019802 | 0.00077554 | 0.0087521 | -85.9863 | 1.7258 | -120.9595 | 0.24261 | -0.022888 | 0.14191 | 0.27008 | 0.25177 | 1.7944 | -121.0098 | -0.28381 | -0.036621 | 34.6893 | 120.9183 | -1.7853 | -0.33417 | 0.032044 | 34.9731 | 120.9457 | 120.9274 | 120.6528 | 122.4014 | 34.6893 | 122.4701 | 120.8176 | -0.33417 | 122.4014 | 34.6893 | 120.8176 | 120.6528 | 122.4701 | -122.7219 | -122.7722
3575.9062 | 104.1275 | -71.2372 | 41.6748 | 0.11856 | 0.014125 | 0.020971 | 2.2367 | 0.011264 | 0.018079 | 2.2832 | -47.4884 | 41.6656 | -80.928 | 21.4737 | 5.5527 | 12.3001 | -5.0537 | -12.2131 | 41.5009 | -80.7449 | -9.6909 | -0.009156 | 23.7488 | 92.7109 | -36.1221 | -9.5078 | -0.17395 | 33.4396 | 66.1835 | 59.024 | 76.7899 | 112.9028 | 23.7488 | 112.738 | 83.5373 | -9.5078 | 112.9028 | 23.7488 | 83.5373 | 76.7899 | 112.738 | -122.6028 | -122.4197
3576.9062 | 122.4655 | -119.2062 | 3.1815 | 0.29404 | 0.014338 | 0.021399 | 0.029322 | 0.00015601 | 0.00013454 | 0.0096067 | -84.3292 | 3.1403 | -119.545 | 0.49439 | 0.064087 | 0.11444 | 0.050354 | 0.13733 | 3.2227 | -119.6136 | -0.33875 | -0.041199 | 34.877 | 119.7006 | -3.1174 | -0.40741 | 0.041198 | 35.2158 | 119.2566 | 119.3436 | 119.2703 | 122.3465 | 34.877 | 122.4289 | 119.3207 | -0.40741 | 122.3465 | 34.877 | 119.3207 | 119.2703 | 122.4289 | -122.7264 | -122.7951
3577.9062 | 122.5571 | -119.4397 | 2.9297 | 0.14145 | 0.012629 | 0.020758 | 0.023768 | -0.00048499 | 0.0024845 | 0.010247 | -84.1827 | 2.8564 | -119.7647 | 0.68207 | 0.16022 | 0.23804 | -0.091553 | 0.27008 | 2.9572 | -119.7647 | -0.32501 | -0.073242 | 35.257 | 120.1218 | -2.7695 | -0.32501 | 0.027466 | 35.582 | 119.3481 | 119.7098 | 119.5999 | 122.2961 | 35.257 | 122.3969 | 119.6777 | -0.32501 | 122.2961 | 35.257 | 119.6777 | 119.5999 | 122.3969 | -122.6944 | -122.6944
3578.9062 | 122.4701 | -119.4763 | 2.9572 | 0.011749 | 0.016047 | 0.023321 | 0.029108 | -0.0024076 | -0.00093346 | 0.010034 | -84.0363 | 2.9297 | -119.7556 | 0.64087 | 0.091553 | 0.15106 | 0.041199 | 0.18768 | 2.9938 | -119.8242 | -0.27924 | -0.027466 | 35.4401 | 120.1172 | -2.8656 | -0.3479 | 0.036621 | 35.7193 | 119.5175 | 119.664 | 119.5679 | 122.406 | 35.4401 | 122.4701 | 119.6274 | -0.3479 | 122.406 | 35.4401 | 119.6274 | 119.5679 | 122.4701 | -122.7127 | -122.7814
3579.9062 | 122.4976 | -119.4122 | 2.9938 | 0.034637 | 0.016047 | 0.021826 | 0.026545 | -5.7592e-05 | -0.0020017 | 0.0089657 | -83.7708 | 2.9617 | -119.7372 | 0.67291 | 0.10529 | 0.16022 | 0.041199 | 0.19226 | 3.0396 | -119.7556 | -0.32501 | -0.032043 | 35.6415 | 120.0851 | -2.8885 | -0.34332 | 0.045777 | 35.9665 | 119.4534 | 119.6045 | 119.5175 | 122.374 | 35.6415 | 122.4518 | 119.5724 | -0.34332 | 122.374 | 35.6415 | 119.5724 | 119.5175 | 122.4518 | -122.731 | -122.7493
3580.9062 | 122.5571 | -119.3298 | 3.0579 | 0.1796 | 0.014552 | 0.01499 | 0.020777 | -0.0024076 | 0.0016299 | 0.010247 | -83.5236 | 2.9984 | -119.6136 | 0.72327 | 0.16937 | 0.24719 | -0.082397 | 0.26093 | 3.0853 | -119.6548 | -0.28381 | -0.059509 | 35.8063 | 120.0531 | -2.8885 | -0.32501 | 0.027466 | 36.0901 | 119.2474 | 119.5908 | 119.4992 | 122.3282 | 35.8063 | 122.4152 | 119.577 | -0.32501 | 122.3282 | 35.8063 | 119.577 | 119.4992 | 122.4152 | -122.6715 | -122.7127
3581.9062 | 122.493 | -119.3207 | 3.1174 | -0.14084 | 0.016902 | 0.017126 | 0.027826 | -0.00091219 | 0.0020571 | 0.011529 | -83.4137 | 3.0396 | -119.6548 | 0.76904 | 0.14648 | 0.22888 | 0.041199 | 0.21515 | 3.1723 | -119.6823 | -0.33417 | -0.07782 | 35.907 | 120.0897 | -2.9709 | -0.36163 | 0.054931 | 36.2412 | 119.3619 | 119.5358 | 119.4672 | 122.3602 | 35.907 | 122.493 | 119.5496 | -0.36163 | 122.3602 | 35.907 | 119.5496 | 119.4672 | 122.493 | -122.7722 | -122.7997
3582.9062 | 122.525 | -119.1925 | 3.2593 | -0.17899 | 0.014125 | 0.017767 | 0.027186 | -0.0024076 | -0.00071986 | 0.0093931 | -83.2443 | 3.2272 | -119.4901 | 0.72327 | 0.068665 | 0.13733 | 0.082397 | 0.20142 | 3.2959 | -119.5267 | -0.29755 | -0.032043 | 35.9482 | 119.9158 | -3.1906 | -0.33417 | 0.036621 | 36.2457 | 119.2749 | 119.3939 | 119.2612 | 122.4197 | 35.9482 | 122.4884 | 119.3298 | -0.33417 | 122.4197 | 35.9482 | 119.3298 | 119.2612 | 122.4884 | -122.7493 | -122.7859
3583.9062 | 122.4884 | -119.2154 | 3.2364 | -0.1561 | 0.014766 | 0.016058 | 0.025263 | -0.0013394 | -0.00071986 | 0.0093931 | -83.3084 | 3.2043 | -119.5129 | 0.70953 | 0.073242 | 0.13733 | 0.091553 | 0.17853 | 3.2959 | -119.5358 | -0.29755 | -0.032043 | 35.907 | 119.9249 | -3.1631 | -0.32043 | 0.059509 | 36.2045 | 119.3069 | 119.3939 | 119.2886 | 122.4197 | 35.907 | 122.5113 | 119.3527 | -0.32043 | 122.4197 | 35.907 | 119.3527 | 119.2886 | 122.5113 | -122.7493 | -122.7722
3584.9062 | 122.5067 | -119.0918 | 3.3463 | -0.026398 | 0.014766 | 0.017553 | 0.027613 | -0.00048499 | 0.00013454 | 0.010034 | -83.226 | 3.241 | -119.4534 | 0.77362 | 0.19226 | 0.37079 | 0.17395 | 0.37994 | 3.3646 | -119.4168 | -0.36163 | -0.10528 | 35.8658 | 119.8654 | -3.154 | -0.32501 | 0.018311 | 36.2274 | 119.2657 | 119.4717 | 119.2841 | 122.3328 | 35.8658 | 122.4564 | 119.4626 | -0.32501 | 122.3328 | 35.8658 | 119.4626 | 119.2841 | 122.4564 | -122.7997 | -122.7631
3585.9062 | 122.5159 | -119.1513 | 3.273 | -0.13321 | 0.015193 | 0.014349 | 0.027399 | -0.00069859 | 0.00098914 | 0.0098203 | -83.2352 | 3.273 | -119.458 | 0.7782 | 0.11444 | 0.1831 | 0.045776 | 0.20142 | 3.3096 | -119.5084 | -0.3067 | 0 | 35.9161 | 119.9295 | -3.1586 | -0.35706 | 0.036621 | 36.2228 | 119.1971 | 119.3527 | 119.2657 | 122.4243 | 35.9161 | 122.4609 | 119.3344 | -0.35706 | 122.4243 | 35.9161 | 119.3344 | 119.2657 | 122.4609 | -122.731 | -122.7814
3586.9062 | 122.5342 | -119.1238 | 3.3005 | -0.18662 | 0.015834 | 0.020544 | 0.027186 | -0.0034756 | 0.00098914 | 0.0098203 | -83.2352 | 3.2639 | -119.4351 | 0.78278 | 0.10986 | 0.16022 | 0.054932 | 0.21515 | 3.3279 | -119.4763 | -0.31128 | -0.036621 | 35.8887 | 119.9066 | -3.1906 | -0.35248 | 0.027466 | 36.2 | 119.1788 | 119.339 | 119.2337 | 122.3877 | 35.8887 | 122.4518 | 119.2841 | -0.35248 | 122.3877 | 35.8887 | 119.2841 | 119.2337 | 122.4518 | -122.7356 | -122.7768
3587.9062 | 122.5159 | -119.133 | 3.2913 | -0.1561 | 0.013057 | 0.018408 | 0.025049 | -5.7592e-05 | -0.0020017 | 0.0089657 | -83.226 | 3.2501 | -119.4489 | 0.75531 | 0.10071 | 0.15106 | 0.086975 | 0.19226 | 3.3279 | -119.4672 | -0.31586 | -0.041199 | 35.907 | 119.8883 | -3.1906 | -0.33417 | 0.036621 | 36.2228 | 119.22 | 119.3253 | 119.2337 | 122.3831 | 35.907 | 122.4609 | 119.2841 | -0.33417 | 122.3831 | 35.907 | 119.2841 | 119.2337 | 122.4609 | -122.7402 | -122.7585
3588.9062 | 122.5159 | -119.1742 | 3.3096 | -0.19424 | 0.014338 | 0.016699 | 0.022699 | -0.0013394 | 0.0018435 | 0.0085385 | -83.2809 | 3.2455 | -119.4901 | 0.74158 | 0.09613 | 0.15564 | 0.10529 | 0.18768 | 3.3463 | -119.4763 | -0.31586 | -0.064087 | 35.8932 | 119.9158 | -3.2135 | -0.30212 | 0.036621 | 36.2091 | 119.2795 | 119.3619 | 119.2703 | 122.4197 | 35.8932 | 122.5204 | 119.3298 | -0.30212 | 122.4197 | 35.8932 | 119.3298 | 119.2703 | 122.5204 | -122.7997 | -122.7859
3589.9062 | 122.4976 | -119.1971 | 3.2684 | -0.19424 | 0.013911 | 0.015417 | 0.022272 | -0.0036892 | 0.0012027 | 0.0098203 | -83.2809 | 3.2135 | -119.4672 | 0.74158 | 0.10986 | 0.14191 | 0.10529 | 0.19684 | 3.2959 | -119.5129 | -0.27008 | -0.054932 | 35.9161 | 119.9387 | -3.1586 | -0.31586 | 0.027465 | 36.1862 | 119.3024 | 119.3939 | 119.3069 | 122.4106 | 35.9161 | 122.493 | 119.339 | -0.31586 | 122.4106 | 35.9161 | 119.339 | 119.3069 | 122.493 | -122.7356 | -122.7814
3590.9062 | 122.5204 | -119.2017 | 3.2684 | 0.011749 | 0.015834 | 0.023321 | 0.030604 | -0.0011258 | -0.00071986 | 0.0098203 | -83.1345 | 3.2272 | -119.4717 | 0.75989 | 0.091553 | 0.16022 | 0.036621 | 0.15564 | 3.3051 | -119.5038 | -0.27008 | -0.041199 | 36.0672 | 119.9615 | -3.1769 | -0.30212 | 0.036621 | 36.3373 | 119.2383 | 119.3573 | 119.2932 | 122.4289 | 36.0672 | 122.5067 | 119.3619 | -0.30212 | 122.4289 | 36.0672 | 119.3619 | 119.2932 | 122.5067 | -122.7402 | -122.7722
3591.9062 | 122.5159 | -119.2154 | 3.2547 | -0.18662 | 0.014338 | 0.012213 | 0.022486 | -0.001553 | -0.0013609 | 0.0093931 | -83.194 | 3.2318 | -119.545 | 0.737 | 0.10529 | 0.14648 | 0.11902 | 0.17853 | 3.3096 | -119.5267 | -0.32959 | -0.022888 | 36.0214 | 119.9524 | -3.1494 | -0.31128 | 0.054931 | 36.351 | 119.3344 | 119.3939 | 119.3207 | 122.4472 | 36.0214 | 122.525 | 119.3619 | -0.31128 | 122.4472 | 36.0214 | 119.3619 | 119.3207 | 122.525 | -122.7997 | -122.7814
3592.9062 | 122.4792 | -119.6594 | 2.8152 | -0.21713 | 0.012416 | 0.013067 | 0.021845 | -0.0017666 | 0.0012027 | 0.010247 | -83.7387 | 2.742 | -119.989 | 0.76904 | 0.15106 | 0.19226 | 0.082397 | 0.19226 | 2.8931 | -119.9936 | -0.32959 | -0.073243 | 35.9207 | 120.4285 | -2.6642 | -0.33417 | 0.077819 | 36.2503 | 119.7418 | 119.8517 | 119.8105 | 122.4014 | 35.9207 | 122.5525 | 119.8517 | -0.33417 | 122.4014 | 35.9207 | 119.8517 | 119.8105 | 122.5525 | -122.8043 | -122.8088
3593.9062 | 122.5159 | -119.6823 | 2.7786 | -0.35446 | 0.012843 | 0.017553 | 0.021845 | -0.0041166 | -0.00071986 | 0.0087521 | -83.8074 | 2.71 | -120.0256 | 0.78735 | 0.09613 | 0.15564 | 0.1236 | 0.19684 | 2.8015 | -119.9936 | -0.34332 | -0.068664 | 35.8749 | 120.4697 | -2.6825 | -0.31128 | 0.022889 | 36.2183 | 119.8059 | 119.8791 | 119.7784 | 122.3923 | 35.8749 | 122.4838 | 119.838 | -0.31128 | 122.3923 | 35.8749 | 119.838 | 119.7784 | 122.4838 | -122.8043 | -122.7722
3594.9062 | 122.525 | -119.7189 | 2.7557 | -0.2095 | 0.011775 | 0.015417 | 0.023554 | -0.0060392 | -0.00071986 | 0.010034 | -83.519 | 2.6779 | -120.0256 | 0.83313 | 0.14191 | 0.19684 | 0.086975 | 0.19684 | 2.7969 | -119.989 | -0.3067 | -0.07782 | 36.2 | 120.5521 | -2.6138 | -0.27008 | 0.041199 | 36.5067 | 119.8059 | 119.9158 | 119.8608 | 122.3969 | 36.2 | 122.5159 | 119.9158 | -0.27008 | 122.3969 | 36.2 | 119.9158 | 119.8608 | 122.5159 | -122.7814 | -122.7448
3595.9062 | 122.5525 | -119.6869 | 2.7328 | -0.21713 | 0.011561 | 0.016485 | 0.022272 | -0.0047574 | -0.00093346 | 0.0087521 | -83.4045 | 2.6505 | -120.0027 | 0.88806 | 0.17853 | 0.24719 | 0.013733 | 0.27924 | 2.7695 | -119.9753 | -0.31586 | -0.082397 | 36.2823 | 120.575 | -2.5543 | -0.28839 | 0.036621 | 36.5982 | 119.7006 | 119.9661 | 119.8654 | 122.3373 | 36.2823 | 122.4564 | 119.9341 | -0.28839 | 122.3373 | 36.2823 | 119.9341 | 119.8654 | 122.4564 | -122.7356 | -122.7081
3596.9062 | 122.6486 | -119.6686 | 2.7008 | -0.14847 | 0.012843 | 0.014135 | 0.021845 | -0.0024076 | -0.0017881 | 0.010675 | -83.3817 | 2.6367 | -119.9844 | 0.91553 | -0.068665 | 0.3067 | 0.036621 | -0.013733 | 2.7374 | -120.0073 | -0.31586 | -0.064087 | 36.2869 | 120.5841 | -2.7695 | -0.33875 | 0.036621 | 36.6028 | 119.7052 | 119.6548 | 119.5999 | 122.3053 | 36.2869 | 122.406 | 119.9753 | -0.33875 | 122.3053 | 36.2869 | 119.9753 | 119.5999 | 122.406 | -122.6852 | -122.7081
3597.9062 | 122.644 | -119.7098 | 2.6871 | 0.48477 | 0.012202 | 0.020758 | 0.022699 | -0.00668 | -7.9062e-05 | 0.0091795 | -83.4229 | 2.6138 | -120.0256 | 0.93384 | 0.19684 | 0.27008 | -0.064087 | 0.31586 | 2.7008 | -120.0119 | -0.31586 | -0.073242 | 36.2869 | 120.6436 | -2.4902 | -0.30212 | 0.013733 | 36.6028 | 119.6457 | 120.0256 | 119.9066 | 122.3236 | 36.2869 | 122.4106 | 119.9799 | -0.30212 | 122.3236 | 36.2869 | 119.9799 | 119.9066 | 122.4106 | -122.7127 | -122.699
3598.9062 | 122.5708 | -119.664 | 2.7237 | -0.19424 | 0.013057 | 0.012426 | 0.026331 | -0.0062528 | 0.0014163 | 0.0074705 | -83.4366 | 2.623 | -120.0119 | 0.92468 | 0.18768 | 0.25635 | -0.022888 | 0.30212 | 2.7786 | -119.9844 | -0.3479 | -0.10071 | 36.2274 | 120.5887 | -2.536 | -0.32044 | 0.054931 | 36.5753 | 119.6411 | 119.9661 | 119.8517 | 122.287 | 36.2274 | 122.4426 | 119.9203 | -0.32044 | 122.287 | 36.2274 | 119.9203 | 119.8517 | 122.4426 | -122.7356 | -122.7081
3599.9062 | 122.6349 | -119.7052 | 2.7054 | -0.087433 | 0.012629 | 0.018622 | 0.022272 | -0.004971 | -0.0011471 | 0.0093931 | -83.2993 | 2.6413 | -120.0027 | 0.92926 | 0.21973 | 0.28381 | -0.045776 | 0.32044 | 2.7328 | -120.0027 | -0.29755 | -0.064087 | 36.4059 | 120.6345 | -2.4857 | -0.29755 | 0.027466 | 36.7035 | 119.6594 | 120.0256 | 119.9249 | 122.3465 | 36.4059 | 122.438 | 119.989 | -0.29755 | 122.3465 | 36.4059 | 119.989 | 119.9249 | 122.438 | -122.7081 | -122.7081
3600.9062 | 122.5388 | -119.7601 | 2.7145 | -0.14084 | 0.012629 | 0.016058 | 0.031885 | -0.0056118 | -7.9062e-05 | 0.010034 | -83.2031 | 2.6596 | -120.0577 | 0.8606 | 0.10071 | 0.15564 | 0.064087 | 0.19226 | 2.742 | -120.0851 | -0.29755 | -0.054932 | 36.557 | 120.6207 | -2.6138 | -0.32501 | 0.027465 | 36.8546 | 119.8242 | 119.9524 | 119.8608 | 122.4197 | 36.557 | 122.5021 | 119.9158 | -0.32501 | 122.4197 | 36.557 | 119.9158 | 119.8608 | 122.5021 | -122.7722 | -122.7997
3601.9062 | 122.493 | -119.7189 | 2.7008 | -0.1561 | 0.011775 | 0.013708 | 0.022272 | -0.0041166 | -0.0020017 | 0.0083249 | -83.0109 | 2.6093 | -120.0165 | 0.95215 | 0.23346 | 0.28839 | -0.086975 | 0.58136 | 2.7328 | -120.0668 | -0.29755 | -0.091553 | 36.7081 | 120.6711 | -2.4673 | -0.3479 | 0.032043 | 37.0056 | 119.632 | 120.3003 | 119.9524 | 122.3282 | 36.7081 | 122.4518 | 120.0073 | -0.3479 | 122.3282 | 36.7081 | 120.0073 | 119.9524 | 122.4518 | -122.7173 | -122.7676
3602.9062 | 122.6486 | -119.7006 | 2.6825 | -0.079803 | 0.012629 | 0.019903 | 0.022486 | -0.0053982 | -0.0022153 | 0.0089657 | -82.8461 | 2.6321 | -120.0394 | 0.93842 | 0.25177 | 0.29755 | -0.082397 | 0.31586 | 2.7191 | -120.0073 | -0.33875 | -0.050354 | 36.8546 | 120.639 | -2.4307 | -0.3067 | 0.036621 | 37.1933 | 119.6182 | 120.0165 | 119.9524 | 122.3328 | 36.8546 | 122.4197 | 119.9982 | -0.3067 | 122.3328 | 36.8546 | 119.9982 | 119.9524 | 122.4197 | -122.7219 | -122.6898
3603.9062 | 122.6074 | -119.7556 | 2.655 | 0.011749 | 0.01327 | 0.014135 | 0.023554 | -0.0071072 | 0.00034814 | 0.0091795 | -82.7591 | 2.5909 | -120.108 | 0.88806 | 0.17395 | 0.24719 | -0.050354 | 0.26093 | 2.6825 | -120.0943 | -0.35248 | -0.064087 | 36.9965 | 120.6436 | -2.4811 | -0.33875 | 0.027466 | 37.3489 | 119.7052 | 120.0165 | 119.9295 | 122.3465 | 36.9965 | 122.438 | 120.0027 | -0.33875 | 122.3465 | 36.9965 | 120.0027 | 119.9295 | 122.438 | -122.7631 | -122.7493
3604.9062 | 122.612 | -119.7464 | 2.6596 | -0.049286 | 0.013484 | 0.01499 | 0.023768 | -0.0062528 | -0.00050626 | 0.0085385 | -82.6584 | 2.5726 | -120.0623 | 0.94299 | 0.21515 | 0.29297 | -0.064087 | 0.29755 | 2.6733 | -120.0623 | -0.31586 | -0.086975 | 37.088 | 120.6894 | -2.4445 | -0.31586 | 0.013733 | 37.4039 | 119.6823 | 120.0439 | 119.9615 | 122.319 | 37.088 | 122.4197 | 120.0394 | -0.31586 | 122.319 | 37.088 | 120.0394 | 119.9615 | 122.4197 | -122.7219 | -122.7219
3605.9062 | 122.5067 | -119.751 | 2.7374 | -0.27054 | 0.011348 | 0.014776 | 0.028254 | -0.0068936 | -0.00029266 | 0.0089657 | -82.7133 | 2.5909 | -120.108 | 0.84686 | 0.10529 | 0.13733 | 0.09613 | 0.16937 | 2.71 | -120.1263 | -0.35705 | -0.14648 | 37.0377 | 120.5978 | -2.6321 | -0.37537 | -0.027466 | 37.3947 | 119.8471 | 119.9203 | 119.8563 | 122.3419 | 37.0377 | 122.4609 | 119.8883 | -0.37537 | 122.3419 | 37.0377 | 119.8883 | 119.8563 | 122.4609 | -122.8455 | -122.8638
3606.9062 | 122.6257 | -119.7601 | 2.655 | -0.064545 | 0.011561 | 0.013495 | 0.022699 | -0.0068936 | -0.00029266 | 0.011102 | -82.5577 | 2.5955 | -120.108 | 0.97961 | 0.24261 | 0.27924 | -0.07782 | 0.32501 | 2.6733 | -120.0623 | -0.3479 | -0.059509 | 37.2025 | 120.7397 | -2.4124 | -0.30212 | 0.018311 | 37.5504 | 119.6823 | 120.0851 | 120.0027 | 122.3557 | 37.2025 | 122.4335 | 120.0394 | -0.30212 | 122.3557 | 37.2025 | 120.0394 | 120.0027 | 122.4335 | -122.7631 | -122.7173
3607.9062 | 122.6395 | -119.783 | 2.6459 | -0.064545 | 0.013911 | 0.016913 | 0.022486 | -0.0047574 | -0.00050626 | 0.0081113 | -82.5485 | 2.5543 | -120.0851 | 0.9613 | 0.2243 | 0.28839 | -0.054932 | 0.32959 | 2.6642 | -120.0714 | -0.30212 | -0.091553 | 37.2345 | 120.7443 | -2.4216 | -0.28839 | 0.018311 | 37.5366 | 119.7281 | 120.1126 | 120.0073 | 122.3373 | 37.2345 | 122.4472 | 120.0714 | -0.28839 | 122.3373 | 37.2345 | 120.0714 | 120.0073 | 122.4472 | -122.731 | -122.7173
3608.9062 | 122.6349 | -119.7784 | 2.6367 | -0.064545 | 0.012202 | 0.011786 | 0.023127 | -0.0071072 | -0.0032835 | 0.0078977 | -82.5256 | 2.5406 | -120.1263 | 0.93842 | 0.20599 | 0.27008 | -0.054932 | 0.29755 | 2.655 | -120.0851 | -0.3479 | -0.096131 | 37.2528 | 120.7169 | -2.4307 | -0.3067 | 0.01831 | 37.6007 | 119.7235 | 120.076 | 119.9844 | 122.319 | 37.2528 | 122.4335 | 120.0485 | -0.3067 | 122.319 | 37.2528 | 120.0485 | 119.9844 | 122.4335 | -122.7631 | -122.7219
3609.9062 | 122.6303 | -119.7601 | 2.6413 | 0.011749 | 0.011989 | 0.014563 | 0.022272 | -0.0058256 | -0.0015745 | 0.0087521 | -82.4615 | 2.536 | -120.108 | 0.92926 | 0.20142 | 0.2655 | -0.032043 | 0.29755 | 2.6459 | -120.0897 | -0.3479 | -0.10529 | 37.2986 | 120.6894 | -2.4399 | -0.32959 | 0.004578 | 37.6465 | 119.7281 | 120.0577 | 119.9615 | 122.2961 | 37.2986 | 122.406 | 120.0256 | -0.32959 | 122.2961 | 37.2986 | 120.0256 | 119.9615 | 122.406 | -122.7493 | -122.731
3610.9062 | 122.5845 | -119.838 | 2.5909 | 0.14908 | 0.012629 | 0.017126 | 0.024836 | -0.00668 | -0.0045651 | 0.0093931 | -82.4478 | 2.5589 | -120.1263 | 0.86975 | 0.064087 | 0.17853 | -0.027466 | 0.20599 | 2.6047 | -120.1218 | -0.28839 | -0.032043 | 37.3901 | 120.7077 | -2.5269 | -0.28381 | 0.013733 | 37.6785 | 119.8105 | 120.0439 | 119.902 | 122.3969 | 37.3901 | 122.4426 | 120.0165 | -0.28381 | 122.3969 | 37.3901 | 120.0165 | 119.902 | 122.4426 | -122.7173 | -122.7127
3611.9062 | 122.5937 | -119.8059 | 2.6184 | 0.0041197 | 0.012416 | 0.014563 | 0.023554 | -0.0075344 | 0.0020571 | 0.0078977 | -82.5211 | 2.5589 | -120.1492 | 0.89722 | 0.18768 | 0.25177 | -0.054932 | 0.25177 | 2.6505 | -120.1172 | -0.34332 | -0.059509 | 37.2849 | 120.7031 | -2.4307 | -0.31128 | 0.032044 | 37.6282 | 119.751 | 120.0577 | 119.9936 | 122.3648 | 37.2849 | 122.4564 | 120.0577 | -0.31128 | 122.3648 | 37.2849 | 120.0577 | 119.9936 | 122.4564 | -122.7676 | -122.7356
3612.9062 | 122.6349 | -119.7556 | 2.6733 | -0.018768 | 0.01092 | 0.014776 | 0.021845 | -0.0081754 | -0.00029266 | 0.0085385 | -82.5302 | 2.5681 | -120.1035 | 0.97961 | 0.21973 | 0.2655 | -0.050354 | 0.29297 | 2.6779 | -120.0577 | -0.3479 | -0.10529 | 37.2253 | 120.7352 | -2.4536 | -0.30212 | 0.004577 | 37.5732 | 119.7052 | 120.0485 | 119.9753 | 122.3236 | 37.2253 | 122.4335 | 120.0211 | -0.30212 | 122.3236 | 37.2253 | 120.0211 | 119.9753 | 122.4335 | -122.7768 | -122.731
3613.9062 | 122.644 | -119.7739 | 2.6459 | -0.026398 | 0.012629 | 0.017981 | 0.022699 | -0.00668 | -0.00050626 | 0.0087521 | -82.5943 | 2.5681 | -120.0943 | 0.9613 | 0.21515 | 0.2655 | -0.054932 | 0.29297 | 2.6642 | -120.0668 | -0.32043 | -0.07782 | 37.1796 | 120.7352 | -2.4307 | -0.29297 | 0.018311 | 37.5 | 119.7189 | 120.0668 | 119.989 | 122.3419 | 37.1796 | 122.4381 | 120.0394 | -0.29297 | 122.3419 | 37.1796 | 120.0394 | 119.989 | 122.4381 | -122.7402 | -122.7127
3614.9062 | 122.5891 | -120.0714 | 2.3712 | 0.042267 | 0.027369 | 0.041266 | 0.02334 | -0.0060392 | 0.0012027 | 0.0083249 | -82.8186 | 2.2751 | -120.4056 | 0.85602 | 0.18768 | 0.26093 | 0.013733 | 0.31586 | 2.3895 | -120.3827 | -0.33417 | -0.096131 | 37.2528 | 120.9274 | -2.1835 | -0.31128 | 0.01831 | 37.587 | 120.0851 | 120.3873 | 120.2591 | 122.3465 | 37.2528 | 122.4609 | 120.3323 | -0.31128 | 122.3465 | 37.2528 | 120.3323 | 120.2591 | 122.4609 | -122.7768 | -122.7539
3615.9219 | 122.5067 | -120.1675 | 2.298 | -0.11032 | 0.17562 | 0.17692 | 0.032313 | -0.0051846 | 0.0014163 | 0.0072569 | -82.7637 | 2.2247 | -120.4834 | 0.78278 | 0.13733 | 0.16937 | 0.11444 | 0.24719 | 2.3209 | -120.5338 | -0.31586 | -0.073243 | 37.4039 | 120.9503 | -2.1606 | -0.36621 | 0.022888 | 37.7197 | 120.282 | 120.4147 | 120.3049 | 122.3923 | 37.4039 | 122.4884 | 120.3369 | -0.36621 | 122.3923 | 37.4039 | 120.3369 | 120.3049 | 122.4884 | -122.7814 | -122.8317
3616.9062 | 122.5891 | -120.726 | 1.6754 | 0.027008 | -0.0033922 | -0.0091494 | 0.016077 | -0.0068936 | -0.0024289 | 0.0064023 | -0.76446 | -0.53101 | -1.0849 | 0.67291 | 0.16937 | 0.20142 | 0.018311 | 0.27466 | 1.712 | -121.0419 | 119.6411 | -2.2064 | 119.9615 | 121.3989 | -1.506 | -0.31586 | 0.036621 | 0.32044 | 120.7443 | 121.0007 | 120.8954 | 120.195 | 119.9615 | 122.438 | 120.9274 | -0.31586 | 120.195 | 119.9615 | 120.9274 | 120.8954 | 122.438 | -2.7603 | -122.7173
3617.9062 | 122.5937 | -120.813 | 1.5884 | 0.11856 | -0.003606 | -0.011713 | 0.020136 | -0.0053982 | -0.0017881 | 0.0093931 | -0.73242 | -0.48981 | -1.0529 | 0.61798 | 0.14191 | 0.1831 | 0.018311 | 0.27008 | 1.6067 | -121.138 | 119.7601 | -2.0782 | 120.0806 | 121.431 | -1.4465 | -0.32501 | 0.01831 | 0.32043 | 120.8313 | 121.0831 | 120.9549 | 120.3232 | 120.0806 | 122.4197 | 120.9961 | -0.32501 | 120.3232 | 120.0806 | 120.9961 | 120.9549 | 122.4197 | -2.6413 | -122.7264
3618.9062 | 122.5937 | -120.845 | 1.6159 | 0.18723 | -0.0027514 | -0.011072 | 0.018213 | -0.0064664 | -0.0013609 | 0.0093931 | -0.70953 | -0.48981 | -1.0483 | 0.59509 | 0.14648 | 0.17395 | 0.032043 | 0.27466 | 1.5976 | -121.1609 | 119.7968 | -2.1057 | 120.1355 | 121.4401 | -1.4694 | -0.31586 | -0.018311 | 0.33874 | 120.8771 | 121.1197 | 120.9915 | 120.3552 | 120.1355 | 122.4426 | 121.019 | -0.31586 | 120.3552 | 120.1355 | 121.019 | 120.9915 | 122.4426 | -2.6642 | -122.7768
3619.9062 | 122.6212 | -120.7809 | 1.6663 | -0.018768 | -0.0057422 | -0.012354 | 0.017573 | -0.0056118 | 0.0012027 | 0.010034 | -0.65002 | -0.46692 | -1.03 | 0.6546 | 0.1831 | 0.22888 | 0.013733 | 0.30212 | 1.6525 | -121.0922 | 119.751 | -2.1332 | 120.1309 | 121.4355 | -1.4832 | -0.31128 | -0.013733 | 0.37994 | 120.7947 | 121.0831 | 120.9641 | 120.314 | 120.1309 | 122.4335 | 121.0098 | -0.31128 | 120.314 | 120.1309 | 121.0098 | 120.9641 | 122.4335 | -2.6962 | -122.7585
3620.9219 | 122.5433 | -120.845 | 1.6617 | 0.22537 | 0.001521 | -0.011286 | 0.024195 | -0.0064664 | 0.0014163 | 0.010247 | -0.66376 | -0.44403 | -1.0391 | 0.58136 | 0.082397 | 0.13275 | 0.073242 | 0.19226 | 1.6754 | -121.1334 | 119.8059 | -2.1057 | 120.1813 | 121.4264 | -1.5793 | -0.28839 | 0.013733 | 0.37537 | 120.9183 | 121.0373 | 120.9274 | 120.401 | 120.1813 | 122.5204 | 120.9778 | -0.28839 | 120.401 | 120.1813 | 120.9778 | 120.9274 | 122.5204 | -2.7008 | -122.7951
3621.9062 | 122.6303 | -120.7535 | 1.6617 | 0.011749 | -0.0038196 | -0.0085086 | 0.018213 | -0.0079618 | 0.00013454 | 0.0091795 | -0.64545 | -0.42572 | -1.0162 | 0.67291 | 0.19226 | 0.21515 | 0.013733 | 0.29755 | 1.6983 | -121.0739 | 119.7372 | -2.0874 | 120.108 | 121.4264 | -1.4694 | -0.32044 | 0.036621 | 0.37079 | 120.7672 | 121.051 | 120.9457 | 120.3278 | 120.108 | 122.4518 | 120.9686 | -0.32044 | 120.3278 | 120.108 | 120.9686 | 120.9457 | 122.4518 | -2.6779 | -122.7356
3622.9062 | 122.6257 | -120.7169 | 1.7166 | -0.0035098 | -0.0027514 | -0.01214 | 0.019068 | -0.0073208 | 0.00056194 | 0.0089657 | -0.64087 | -0.42114 | -0.97046 | 0.68207 | 0.19226 | 0.21515 | 0.013733 | 0.28839 | 1.7349 | -121.019 | 119.7464 | -2.1378 | 120.076 | 121.3989 | -1.5244 | -0.30212 | 0.01831 | 0.32959 | 120.7306 | 121.0052 | 120.9091 | 120.2957 | 120.076 | 122.4518 | 120.932 | -0.30212 | 120.2957 | 120.076 | 120.932 | 120.9091 | 122.4518 | -2.6871 | -122.7356
3623.9062 | 122.6257 | -120.7855 | 1.6617 | -0.0035098 | -0.005315 | -0.0095766 | 0.018427 | -0.008389 | -0.00071986 | 0.010247 | -0.63629 | -0.42114 | -0.9613 | 0.6546 | 0.18768 | 0.21515 | 0.004578 | 0.28381 | 1.6891 | -121.0968 | 119.8242 | -2.0828 | 120.1492 | 121.4401 | -1.474 | -0.31128 | 0.027466 | 0.32501 | 120.7901 | 121.0693 | 120.9732 | 120.3644 | 120.1492 | 122.4747 | 121.0007 | -0.31128 | 120.3644 | 120.1492 | 121.0007 | 120.9732 | 122.4747 | -2.623 | -122.7585
3624.9062 | 122.6074 | -120.8588 | 1.6159 | 0.019379 | -0.0031786 | -0.0089358 | 0.022272 | -0.0062528 | 0.00013454 | 0.010675 | -0.63629 | -0.42572 | -0.97046 | 0.63629 | 0.15106 | 0.20599 | 0.018311 | 0.2655 | 1.6891 | -121.17 | 119.8883 | -2.0416 | 120.2225 | 121.4951 | -1.4648 | -0.31128 | 0.073242 | 0.33417 | 120.8771 | 121.1243 | 121.0098 | 120.433 | 120.2225 | 122.5479 | 121.0648 | -0.31128 | 120.433 | 120.2225 | 121.0648 | 121.0098 | 122.5479 | -2.5864 | -122.7859
3625.9219 | 122.5662 | -120.7901 | 1.6983 | -0.23239 | 0.0017346 | -0.0042362 | 0.026331 | -0.0071072 | -0.0017881 | 0.0081113 | -0.6134 | -0.36621 | -0.96588 | 0.58594 | 0.11444 | 0.13733 | 0.16022 | 0.21515 | 1.7166 | -121.1334 | 119.8242 | -2.0645 | 120.1767 | 121.376 | -1.5839 | -0.34332 | 0.018311 | 0.35248 | 120.9503 | 121.0052 | 120.9045 | 120.4239 | 120.1767 | 122.5067 | 120.9274 | -0.34332 | 120.4239 | 120.1767 | 120.9274 | 120.9045 | 122.5067 | -2.6642 | -122.8317
3626.9062 | 122.6578 | -120.7718 | 1.6754 | -0.056915 | -0.0044604 | -0.010218 | 0.018 | -0.0060392 | -0.00071986 | 0.010675 | -0.60425 | -0.39825 | -0.94299 | 0.69122 | 0.22888 | 0.25635 | 0 | 0.34332 | 1.6937 | -121.0281 | 119.8288 | -2.0737 | 120.1675 | 121.463 | -1.4465 | -0.25635 | 0.018311 | 0.33874 | 120.7718 | 121.1151 | 121.0007 | 120.3735 | 120.1675 | 122.4655 | 121.0281 | -0.25635 | 120.3735 | 120.1675 | 121.0281 | 121.0007 | 122.4655 | -2.6184 | -122.7036
3627.9062 | 122.6578 | -120.7352 | 1.6937 | -0.079803 | -0.0042468 | -0.010004 | 0.019709 | -0.0058256 | 0.0012027 | 0.0085385 | -0.6134 | -0.40741 | -0.93384 | 0.6958 | 0.20142 | 0.25177 | 0.004578 | 0.33417 | 1.6891 | -121.0373 | 119.8013 | -2.1011 | 120.1218 | 121.431 | -1.4923 | -0.30212 | -0.004578 | 0.32043 | 120.7397 | 121.0693 | 120.9366 | 120.3278 | 120.1218 | 122.4243 | 120.9869 | -0.30212 | 120.3278 | 120.1218 | 120.9869 | 120.9366 | 122.4243 | -2.6276 | -122.731
3628.9062 | 122.6486 | -120.7443 | 1.68 | -0.041657 | -0.0025378 | -0.01214 | 0.019495 | -0.00668 | -0.00093346 | 0.0070431 | -0.58136 | -0.39825 | -0.94757 | 0.71411 | 0.21057 | 0.24719 | 0.004578 | 0.33875 | 1.7029 | -121.0419 | 119.7968 | -2.0782 | 120.163 | 121.4584 | -1.4694 | -0.29755 | 0.022888 | 0.36621 | 120.7489 | 121.0831 | 120.9549 | 120.3461 | 120.163 | 122.4472 | 120.9915 | -0.29755 | 120.3461 | 120.163 | 120.9915 | 120.9549 | 122.4472 | -2.6276 | -122.7219
3629.9062 | 122.6624 | -120.7169 | 1.7441 | -0.064545 | -0.0042468 | -0.011072 | 0.018 | -0.0075344 | -0.00050626 | 0.0087521 | -0.57678 | -0.39368 | -0.92926 | 0.71411 | 0.21973 | 0.27008 | -0.013733 | 0.32044 | 1.7761 | -120.9595 | 119.7876 | -2.1378 | 120.1401 | 121.431 | -1.5244 | -0.24262 | 0.032043 | 0.35248 | 120.7031 | 121.0373 | 120.9366 | 120.3232 | 120.1401 | 122.493 | 120.9869 | -0.24262 | 120.3232 | 120.1401 | 120.9869 | 120.9366 | 122.493 | -2.6733 | -122.7036
3630.9062 | 122.5525 | -120.6619 | 1.8356 | 0.14145 | -0.0023242 | -0.011499 | 0.027613 | -0.0045438 | 0.00056194 | 0.0072569 | -0.63171 | -0.40741 | -0.98877 | 0.66376 | 0.10529 | 0.15106 | 0.013733 | 0.19226 | 1.8814 | -120.9595 | 119.6732 | -2.243 | 120.0302 | 121.3257 | -1.7303 | -0.29755 | 0.045777 | 0.35706 | 120.6757 | 120.8542 | 120.7672 | 120.2545 | 120.0302 | 122.5433 | 120.813 | -0.29755 | 120.2545 | 120.0302 | 120.813 | 120.7672 | 122.5433 | -2.8244 | -122.7951
3631.9062 | 122.6257 | -120.6345 | 1.8219 | 0.15671 | -0.0040332 | -0.010431 | 0.017573 | -0.00668 | -0.00071986 | 0.0091795 | -0.63171 | -0.43488 | -0.97046 | 0.70496 | 0.17395 | 0.23346 | -0.004578 | 0.2655 | 1.8585 | -120.9229 | 119.664 | -2.2568 | 120.0027 | 121.3394 | -1.6479 | -0.28839 | 0.036622 | 0.33874 | 120.6299 | 120.9 | 120.8084 | 120.1996 | 120.0027 | 122.493 | 120.8679 | -0.28839 | 120.1996 | 120.0027 | 120.8679 | 120.8084 | 122.493 | -2.7924 | -122.7448
3632.9062 | 122.5067 | -120.6619 | 1.8127 | -0.12558 | -0.004674 | -0.013636 | 0.018854 | -0.00668 | -0.00093346 | 0.010247 | -0.51727 | -0.3891 | -0.89722 | 0.79651 | 0.25177 | 0.29755 | -0.054932 | 0.35706 | 1.8402 | -120.9045 | 119.7647 | -2.2018 | 120.1447 | 121.4584 | -1.561 | -0.24262 | 0.027466 | 0.37994 | 120.607 | 121.019 | 120.9137 | 120.2728 | 120.1447 | 122.5021 | 120.9595 | -0.24262 | 120.2728 | 120.1447 | 120.9595 | 120.9137 | 122.5021 | -2.71 | -122.7173
3633.9062 | 122.699 | -120.6207 | 1.799 | -0.22476 | -0.004674 | -0.011072 | 0.019495 | -0.0060392 | -0.0017881 | 0.0089657 | -0.54932 | -0.3891 | -0.90179 | 0.78278 | 0.2243 | 0.27924 | -0.041199 | 0.35706 | 1.8265 | -120.932 | 119.7189 | -2.1881 | 120.0714 | 121.4035 | -1.5747 | -0.31128 | 0.027466 | 0.35248 | 120.5795 | 120.9778 | 120.845 | 120.2316 | 120.0714 | 122.4472 | 120.9 | -0.31128 | 120.2316 | 120.0714 | 120.9 | 120.845 | 122.4472 | -2.7008 | -122.731
3634.9062 | 122.699 | -120.6436 | 1.8173 | -0.064545 | -0.0031786 | -0.010431 | 0.020563 | -0.0060392 | -0.00093346 | 0.010247 | -0.52185 | -0.36163 | -0.87433 | 0.79651 | 0.25177 | 0.28381 | -0.054932 | 0.3479 | 1.8265 | -120.9274 | 119.7693 | -2.179 | 120.1218 | 121.4401 | -1.5656 | -0.28381 | 0.009155 | 0.35248 | 120.5887 | 120.9915 | 120.8954 | 120.282 | 120.1218 | 122.4701 | 120.9274 | -0.28381 | 120.282 | 120.1218 | 120.9274 | 120.8954 | 122.4701 | -2.6917 | -122.7448
3635.9062 | 122.6852 | -120.5978 | 1.8631 | -0.041657 | -0.0040332 | -0.011286 | 0.019922 | -0.0058256 | -0.00029266 | 0.0070431 | -0.52643 | -0.35248 | -0.87891 | 0.80109 | 0.20599 | 0.27466 | -0.036621 | 0.35248 | 1.8631 | -120.8954 | 119.7189 | -2.2156 | 120.0714 | 121.3989 | -1.6571 | -0.29755 | 0 | 0.35248 | 120.5612 | 120.9503 | 120.8038 | 120.2454 | 120.0714 | 122.4609 | 120.8725 | -0.29755 | 120.2454 | 120.0714 | 120.8725 | 120.8038 | 122.4609 | -2.742 | -122.7585
3636.9062 | 122.6852 | -120.5887 | 1.8631 | -0.079803 | -0.0025378 | -0.011072 | 0.019709 | -0.0053982 | -0.0020017 | 0.0085385 | -0.54016 | -0.39825 | -0.9201 | 0.78735 | 0.2243 | 0.28839 | -0.032043 | 0.32959 | 1.8814 | -120.8679 | 119.6686 | -2.2614 | 120.0485 | 121.376 | -1.6388 | -0.27924 | 0.018311 | 0.37994 | 120.5566 | 120.9183 | 120.813 | 120.1904 | 120.0485 | 122.4701 | 120.8771 | -0.27924 | 120.1904 | 120.0485 | 120.8771 | 120.813 | 122.4701 | -2.7832 | -122.731
3637.9062 | 122.6532 | -120.607 | 1.8585 | -0.087433 | -0.004674 | -0.011713 | 0.018641 | -0.0058256 | -0.0017881 | 0.010675 | -0.55389 | -0.38452 | -0.9201 | 0.78735 | 0.23804 | 0.28381 | -0.041199 | 0.32044 | 1.8723 | -120.8954 | 119.6869 | -2.243 | 120.0531 | 121.3943 | -1.6205 | -0.28839 | 0.013732 | 0.36621 | 120.5658 | 120.9274 | 120.845 | 120.2225 | 120.0531 | 122.4792 | 120.8908 | -0.28839 | 120.2225 | 120.0531 | 120.8908 | 120.845 | 122.4792 | -2.7786 | -122.7539
3638.9062 | 122.6486 | -120.639 | 1.8448 | 0.065155 | -0.003606 | -0.0089358 | 0.019922 | -0.0064664 | -0.0017881 | 0.0096067 | -0.60883 | -0.41199 | -0.9201 | 0.72784 | 0.18768 | 0.23804 | -0.009155 | 0.26093 | 1.8814 | -120.8908 | 119.7189 | -2.2568 | 120.0302 | 121.3669 | -1.6571 | -0.25177 | 0.036621 | 0.31128 | 120.6299 | 120.9 | 120.8267 | 120.2271 | 120.0302 | 122.5204 | 120.8771 | -0.25177 | 120.2271 | 120.0302 | 120.8771 | 120.8267 | 122.5204 | -2.7649 | -122.7356
3639.9062 | 122.6944 | -120.5612 | 1.8723 | -0.095062 | -0.0014696 | -0.0089358 | 0.018854 | -0.0081754 | 0.0018435 | 0.0076841 | -0.5722 | -0.3891 | -0.91095 | 0.78735 | 0.2243 | 0.27924 | -0.054932 | 0.31586 | 1.8723 | -120.8542 | 119.6503 | -2.2614 | 119.989 | 121.3486 | -1.6479 | -0.29297 | 0 | 0.33875 | 120.5063 | 120.8771 | 120.7855 | 120.1721 | 119.989 | 122.4335 | 120.8405 | -0.29297 | 120.1721 | 119.989 | 120.8405 | 120.7855 | 122.4335 | -2.7832 | -122.7264
3640.9062 | 122.5616 | -120.6482 | 1.8997 | -0.22476 | -0.001897 | -0.010431 | 0.02569 | -0.0058256 | -0.00093346 | 0.0085385 | -0.59967 | -0.35248 | -0.9201 | 0.72327 | 0.10986 | 0.14191 | 0.11444 | 0.1831 | 1.9089 | -120.9183 | 119.7281 | -2.2522 | 120.0485 | 121.3715 | -1.7899 | -0.27008 | 0.009156 | 0.32043 | 120.7626 | 120.8313 | 120.7581 | 120.2957 | 120.0485 | 122.5571 | 120.7901 | -0.27008 | 120.2957 | 120.0485 | 120.7901 | 120.7581 | 122.5571 | -2.8198 | -122.818
3641.9062 | 122.6944 | -120.5429 | 1.9135 | -0.11032 | -0.0033922 | -0.0089358 | 0.018213 | -0.0073208 | -0.00029266 | 0.0098203 | -0.54474 | -0.39368 | -0.87891 | 0.83771 | 0.25177 | 0.29297 | -0.086975 | 0.32959 | 1.9363 | -120.8359 | 119.664 | -2.3071 | 119.9982 | 121.3806 | -1.6617 | -0.29297 | 0.022888 | 0.33417 | 120.4559 | 120.8725 | 120.7947 | 120.1492 | 119.9982 | 122.4792 | 120.8359 | -0.29297 | 120.1492 | 119.9982 | 120.8359 | 120.7947 | 122.4792 | -2.7924 | -122.7493
3642.9062 | 122.6944 | -120.5429 | 1.9089 | -0.072174 | -0.0042468 | -0.01214 | 0.018641 | -0.0075344 | -0.0011471 | 0.0091795 | -0.56763 | -0.38452 | -0.90637 | 0.8194 | 0.24261 | 0.29297 | -0.068665 | 0.33417 | 1.9272 | -120.8405 | 119.6365 | -2.2934 | 119.9753 | 121.3623 | -1.6663 | -0.29755 | 0.01831 | 0.33874 | 120.4742 | 120.8771 | 120.7855 | 120.1584 | 119.9753 | 122.4701 | 120.8359 | -0.29755 | 120.1584 | 119.9753 | 120.8359 | 120.7855 | 122.4701 | -2.8152 | -122.7493
3643.9062 | 122.7081 | -120.5795 | 1.8814 | -0.095062 | -0.005315 | -0.0097904 | 0.021845 | -0.0056118 | -0.0015745 | 0.0091795 | -0.54016 | -0.37079 | -0.91553 | 0.78735 | 0.24261 | 0.27924 | -0.059509 | 0.33417 | 1.9043 | -120.8817 | 119.664 | -2.2522 | 120.0394 | 121.3669 | -1.6388 | -0.30212 | 0.022888 | 0.37537 | 120.52 | 120.9137 | 120.8221 | 120.2087 | 120.0394 | 122.4838 | 120.8588 | -0.30212 | 120.2087 | 120.0394 | 120.8588 | 120.8221 | 122.4838 | -2.7969 | -122.7631
3644.9062 | 122.6715 | -120.575 | 1.8723 | -0.0035098 | -0.0038196 | -0.01214 | 0.019068 | -0.0064664 | -7.9062e-05 | 0.0087521 | -0.59509 | -0.3891 | -0.91553 | 0.75073 | 0.21057 | 0.26093 | -0.022888 | 0.29297 | 1.9043 | -120.8908 | 119.6594 | -2.2614 | 119.9799 | 121.3257 | -1.6617 | -0.31586 | 0.032044 | 0.32043 | 120.5521 | 120.8679 | 120.7855 | 120.1859 | 119.9799 | 122.4792 | 120.8359 | -0.31586 | 120.1859 | 119.9799 | 120.8359 | 120.7855 | 122.4792 | -2.7878 | -122.7631
3645.9219 | 122.5937 | -120.6116 | 1.8951 | -0.14084 | -0.001897 | -0.0091494 | 0.026758 | -0.0077482 | 0.0014163 | 0.0064023 | -0.6134 | -0.37537 | -0.93384 | 0.70496 | 0.12817 | 0.16937 | 0.082397 | 0.20599 | 1.9135 | -120.9641 | 119.6777 | -2.2705 | 119.9982 | 121.3165 | -1.767 | -0.35248 | 0.01831 | 0.32043 | 120.694 | 120.8176 | 120.7397 | 120.2362 | 119.9982 | 122.525 | 120.7809 | -0.35248 | 120.2362 | 119.9982 | 120.7809 | 120.7397 | 122.525 | -2.829 | -122.8592
3646.9062 | 122.6898 | -120.575 | 1.8906 | -0.10269 | -0.0040332 | -0.011286 | 0.018854 | -0.0060392 | 0.0020571 | 0.0096067 | -0.5722 | -0.41199 | -0.94299 | 0.79651 | 0.24719 | 0.30212 | -0.064087 | 0.32959 | 1.8951 | -120.8725 | 119.632 | -2.3026 | 120.0027 | 121.3715 | -1.6434 | -0.29755 | 0.004578 | 0.37079 | 120.5109 | 120.9045 | 120.8221 | 120.163 | 120.0027 | 122.4701 | 120.8771 | -0.29755 | 120.163 | 120.0027 | 120.8771 | 120.8221 | 122.4701 | -2.8336 | -122.7631
3647.9062 | 122.6852 | -120.575 | 1.9089 | 1.2706 | -0.005315 | -0.015772 | 0.019709 | -0.0071072 | -0.0013609 | 0.0093931 | -0.48065 | -0.38452 | -0.88806 | 0.80566 | 0.22888 | 0.29755 | -0.036621 | 0.32044 | 1.9135 | -120.8771 | 119.6869 | -2.2934 | 120.0943 | 121.3806 | -1.68 | -0.30212 | 0.004577 | 0.40741 | 120.5383 | 120.8954 | 120.8038 | 120.1904 | 120.0943 | 122.4884 | 120.8725 | -0.30212 | 120.1904 | 120.0943 | 120.8725 | 120.8038 | 122.4884 | -2.7969 | -122.7859
3648.9062 | 122.6852 | -120.5338 | 1.9318 | 1.9496 | -0.0014696 | -0.012781 | 0.019495 | -0.0064664 | -0.0013609 | 0.010675 | -0.52643 | -0.39825 | -0.89722 | 0.80109 | 0.23346 | 0.30212 | -0.050354 | 0.31586 | 1.9547 | -120.8313 | 119.6365 | -2.33 | 120.0073 | 121.3348 | -1.6983 | -0.29755 | 0.022888 | 0.37079 | 120.4834 | 120.8496 | 120.7672 | 120.1355 | 120.0073 | 122.4884 | 120.8359 | -0.29755 | 120.1355 | 120.0073 | 120.8359 | 120.7672 | 122.4884 | -2.829 | -122.7631
3649.9062 | 122.7036 | -120.5841 | 1.8814 | 2.3158 | -0.0040332 | -0.01214 | 0.02035 | -0.0071072 | 0.00077554 | 0.0074705 | -0.62256 | -0.37994 | -0.87891 | 0.78278 | 0.20142 | 0.27466 | -0.022888 | 0.31586 | 1.8814 | -120.9 | 119.7052 | -2.2614 | 119.9615 | 121.3669 | -1.68 | -0.31586 | 0 | 0.25635 | 120.5612 | 120.9 | 120.7855 | 120.2042 | 119.9615 | 122.4655 | 120.8588 | -0.31586 | 120.2042 | 119.9615 | 120.8588 | 120.7855 | 122.4655 | -2.7603 | -122.7814
3650.9062 | 122.5433 | -120.6436 | 1.9043 | -0.24002 | -0.001897 | -0.012354 | 0.024408 | -0.0043302 | -0.00093346 | 0.0081113 | -0.60883 | -0.3067 | -0.91095 | 0.67749 | 0.11444 | 0.15106 | 0.14648 | 0.1831 | 1.9135 | -120.9549 | 119.7327 | -2.211 | 120.0348 | 121.3211 | -1.7899 | -0.31128 | 0.009155 | 0.30212 | 120.7901 | 120.8267 | 120.7581 | 120.3369 | 120.0348 | 122.5571 | 120.7947 | -0.31128 | 120.3369 | 120.0348 | 120.7947 | 120.7581 | 122.5571 | -2.8152 | -122.8592
3651.9062 | 122.7036 | -120.5704 | 1.8814 | -0.095062 | -0.0042468 | -0.010645 | 0.019068 | -0.0058256 | -0.00050626 | 0.010034 | -0.54474 | -0.39825 | -0.92926 | 0.79193 | 0.24261 | 0.28839 | -0.041199 | 0.34332 | 1.8951 | -120.8862 | 119.6411 | -2.2797 | 120.0256 | 121.3623 | -1.6388 | -0.31586 | 0.013733 | 0.38452 | 120.5292 | 120.9137 | 120.813 | 120.1721 | 120.0256 | 122.4655 | 120.8588 | -0.31586 | 120.1721 | 120.0256 | 120.8588 | 120.813 | 122.4655 | -2.8107 | -122.7676
3652.9062 | 122.699 | -120.6024 | 1.886 | -0.087433 | -0.0033922 | -0.009363 | 0.019068 | -0.0060392 | -0.0013609 | 0.0098203 | -0.54932 | -0.37079 | -0.89264 | 0.76904 | 0.23346 | 0.30212 | -0.032043 | 0.33417 | 1.8997 | -120.9 | 119.7098 | -2.2568 | 120.0531 | 121.3715 | -1.6525 | -0.29755 | 0.013733 | 0.34332 | 120.5704 | 120.9366 | 120.8359 | 120.2316 | 120.0531 | 122.5021 | 120.9045 | -0.29755 | 120.2316 | 120.0531 | 120.9045 | 120.8359 | 122.5021 | -2.7786 | -122.7859
3653.9062 | 122.6578 | -120.5704 | 1.9135 | -0.2095 | -0.0057422 | -0.0089358 | 0.021845 | -0.0045438 | -0.00050626 | 0.0068295 | -0.53558 | -0.38452 | -0.89722 | 0.75531 | 0.19226 | 0.24261 | 0.045776 | 0.31128 | 1.918 | -120.9091 | 119.6732 | -2.298 | 120.0348 | 121.3257 | -1.7212 | -0.33875 | 0.004578 | 0.36163 | 120.6162 | 120.8817 | 120.7626 | 120.1859 | 120.0348 | 122.4884 | 120.813 | -0.33875 | 120.1859 | 120.0348 | 120.813 | 120.7626 | 122.4884 | -2.8107 | -122.8226
3654.9062 | 122.6395 | -120.5658 | 1.9318 | -0.17899 | -0.0065966 | -0.0078678 | 0.020563 | -0.0051846 | -0.0015745 | 0.0081113 | -0.5127 | -0.35706 | -0.86517 | 0.7782 | 0.21515 | 0.24719 | 0.036621 | 0.29755 | 1.9638 | -120.8542 | 119.7006 | -2.2888 | 120.0531 | 121.344 | -1.7166 | -0.28839 | 0.032043 | 0.35248 | 120.6024 | 120.8633 | 120.7809 | 120.2087 | 120.0531 | 122.5296 | 120.813 | -0.28839 | 120.2087 | 120.0531 | 120.813 | 120.7809 | 122.5296 | -2.7969 | -122.7859
3655.9062 | 122.5937 | -120.6299 | 1.9547 | -0.23239 | -0.0027514 | -0.011499 | 0.027186 | -0.0051846 | -0.00029266 | 0.0083249 | -0.56763 | -0.31586 | -0.89264 | 0.70038 | 0.10071 | 0.15564 | 0.10986 | 0.21057 | 1.9684 | -120.9045 | 119.7372 | -2.2705 | 120.0623 | 121.3303 | -1.8539 | -0.27466 | 0.013733 | 0.32501 | 120.7397 | 120.8405 | 120.7306 | 120.314 | 120.0623 | 122.5983 | 120.7855 | -0.27466 | 120.314 | 120.0623 | 120.7855 | 120.7306 | 122.5983 | -2.8473 | -122.8592
3656.9062 | 122.6578 | -120.5933 | 1.9363 | -0.17899 | -0.0023242 | -0.0097904 | 0.020563 | -0.0056118 | -0.0024289 | 0.0093931 | -0.54016 | -0.3891 | -0.89722 | 0.78278 | 0.21515 | 0.25635 | 0.013733 | 0.29297 | 1.9638 | -120.8725 | 119.696 | -2.3254 | 120.0531 | 121.376 | -1.7212 | -0.27924 | 0.027466 | 0.35706 | 120.607 | 120.8862 | 120.8084 | 120.2042 | 120.0531 | 122.5571 | 120.8496 | -0.27924 | 120.2042 | 120.0531 | 120.8496 | 120.8084 | 122.5571 | -2.8336 | -122.8088
3657.9062 | 122.6486 | -120.5841 | 1.918 | -0.13321 | -0.0023242 | -0.010431 | 0.019068 | -0.0058256 | -0.0015745 | 0.0087521 | -0.55389 | -0.38452 | -0.88348 | 0.79651 | 0.23346 | 0.27924 | 0.013733 | 0.30212 | 1.918 | -120.9 | 119.7006 | -2.3026 | 120.0302 | 121.3806 | -1.6846 | -0.31586 | 0 | 0.32959 | 120.5978 | 120.8862 | 120.8176 | 120.1996 | 120.0302 | 122.5021 | 120.8633 | -0.31586 | 120.1996 | 120.0302 | 120.8633 | 120.8176 | 122.5021 | -2.8015 | -122.818
3658.9062 | 122.7127 | -120.4468 | 2.0096 | -0.16373 | -0.0059558 | -0.014917 | 0.019495 | -0.0068936 | -0.0013609 | 0.010675 | -0.35706 | -0.37537 | -0.89264 | 0.78735 | 0.23346 | 0.32501 | -0.068665 | 0.31128 | 2.005 | -120.7764 | 119.5541 | -2.3849 | 120.0897 | 121.2341 | -1.7761 | -0.32959 | -0.004578 | 0.53558 | 120.3781 | 120.7581 | 120.6802 | 120.0714 | 120.0897 | 122.4518 | 120.7718 | -0.32959 | 120.0714 | 120.0897 | 120.7718 | 120.6802 | 122.4518 | -2.9022 | -122.7859
3659.9062 | 122.7219 | -120.4514 | 2.037 | -0.14847 | -0.0038196 | -0.016626 | 0.021418 | -0.0075344 | -0.00071986 | 0.010034 | -0.42572 | -0.39825 | -0.89264 | 0.78735 | 0.18768 | 0.31128 | -0.068665 | 0.29297 | 2.037 | -120.7764 | 119.5587 | -2.4353 | 120.0256 | 121.2387 | -1.8494 | -0.32501 | 0 | 0.46692 | 120.3827 | 120.7443 | 120.639 | 120.0531 | 120.0256 | 122.4884 | 120.7626 | -0.32501 | 120.0531 | 120.0256 | 120.7626 | 120.639 | 122.4884 | -2.9297 | -122.8134
3660.9062 | 122.5845 | -120.4834 | 2.0691 | -0.25528 | -0.0014696 | -0.014276 | 0.021418 | -0.0056118 | -0.0034971 | 0.0081113 | -0.52643 | -0.33875 | -0.86517 | 0.77362 | 0.15564 | 0.20142 | 0.091553 | 0.19684 | 2.092 | -120.7947 | 119.6182 | -2.4078 | 119.957 | 121.257 | -1.9135 | -0.31128 | 0.022888 | 0.33874 | 120.575 | 120.6802 | 120.639 | 120.1447 | 119.957 | 122.5754 | 120.6848 | -0.31128 | 120.1447 | 119.957 | 120.6848 | 120.639 | 122.5754 | -2.9343 | -122.8638
3661.9062 | 122.6074 | -120.5429 | 2.0233 | -0.25528 | -0.0023242 | -0.011499 | 0.021631 | -0.0060392 | -0.0015745 | 0.0098203 | -0.52643 | -0.33875 | -0.86517 | 0.76446 | 0.16022 | 0.18768 | 0.07782 | 0.23346 | 2.0508 | -120.8313 | 119.6777 | -2.3621 | 120.0165 | 121.3074 | -1.8631 | -0.28839 | 0.027466 | 0.33874 | 120.6207 | 120.7764 | 120.7031 | 120.2042 | 120.0165 | 122.5937 | 120.7306 | -0.28839 | 120.2042 | 120.0165 | 120.7306 | 120.7031 | 122.5937 | -2.8885 | -122.8546
3662.9062 | 122.6166 | -120.488 | 2.0279 | -0.20187 | -0.005315 | -0.010858 | 0.022913 | -0.0053982 | -7.9062e-05 | 0.0089657 | -0.54932 | -0.36163 | -0.8606 | 0.7782 | 0.1831 | 0.21515 | 0.073242 | 0.20599 | 2.0416 | -120.7947 | 119.6274 | -2.3895 | 119.9387 | 121.2662 | -1.8448 | -0.3067 | 0.013733 | 0.31128 | 120.5612 | 120.694 | 120.6711 | 120.1263 | 119.9387 | 122.5296 | 120.7031 | -0.3067 | 120.1263 | 119.9387 | 120.7031 | 120.6711 | 122.5296 | -2.8885 | -122.8226
3663.9062 | 122.6028 | -120.575 | 1.9913 | -0.24765 | -0.0016834 | -0.013208 | 0.023554 | -0.0041166 | -0.0030697 | 0.0087521 | -0.56305 | -0.36163 | -0.89722 | 0.76904 | 0.16022 | 0.21515 | 0.059509 | 0.21973 | 1.9958 | -120.8313 | 119.6777 | -2.3529 | 120.0119 | 121.344 | -1.8311 | -0.25635 | 0.004578 | 0.33417 | 120.6345 | 120.7947 | 120.7352 | 120.2133 | 120.0119 | 122.5708 | 120.7901 | -0.25635 | 120.2133 | 120.0119 | 120.7901 | 120.7352 | 122.5708 | -2.8885 | -122.8226
3664.9062 | 122.6349 | -120.5612 | 2.0004 | -0.21713 | -0.0023242 | -0.010218 | 0.023768 | -0.0077482 | -0.0022153 | 0.0070431 | -0.56763 | -0.40283 | -0.90637 | 0.7782 | 0.16022 | 0.21515 | 0.09613 | 0.21515 | 2.0325 | -120.845 | 119.6548 | -2.4033 | 119.9936 | 121.3394 | -1.8402 | -0.28381 | 0.032044 | 0.33874 | 120.6573 | 120.7764 | 120.7214 | 120.1584 | 119.9936 | 122.5937 | 120.7764 | -0.28381 | 120.1584 | 119.9936 | 120.7764 | 120.7214 | 122.5937 | -2.9068 | -122.8455
3665.9062 | 122.6257 | -120.7581 | 1.7853 | -0.57571 | -0.00082884 | -0.011927 | 0.029108 | -0.0036892 | -0.0026425 | 0.0083249 | -0.48065 | -0.33417 | -0.86975 | 0.7782 | 0.16937 | 0.20599 | 0.027466 | 0.19684 | 1.8219 | -121.0602 | 119.8883 | -2.1194 | 120.2774 | 121.5363 | -1.6159 | -0.30212 | 0.036621 | 0.3891 | 120.7855 | 120.9549 | 120.9274 | 120.4239 | 120.2774 | 122.58 | 120.9641 | -0.30212 | 120.4239 | 120.2774 | 120.9641 | 120.9274 | 122.58 | -2.655 | -122.8455
3666.9062 | 122.6257 | -120.6985 | 1.8814 | -0.22476 | -0.0033922 | -0.0055178 | 0.022059 | -0.0047574 | -0.0024289 | 0.0087521 | -0.55847 | -0.35706 | -0.89264 | 0.73242 | 0.16937 | 0.23804 | 0.054932 | 0.22888 | 1.9135 | -120.9961 | 119.8059 | -2.2385 | 120.1401 | 121.431 | -1.712 | -0.29755 | 0.032043 | 0.33417 | 120.7535 | 120.9274 | 120.8679 | 120.3415 | 120.1401 | 122.612 | 120.9366 | -0.29755 | 120.3415 | 120.1401 | 120.9366 | 120.8679 | 122.612 | -2.774 | -122.8775
3667.9062 | 122.5937 | -120.7397 | 1.8539 | -0.24002 | -0.0021106 | -0.0055178 | 0.024408 | -0.0056118 | -0.0028561 | 0.0085385 | -0.63629 | -0.35248 | -0.92468 | 0.86975 | 0.24261 | 0.11902 | 0.091553 | 0.25177 | 1.8723 | -121.051 | 119.8151 | -2.2064 | 120.1035 | 121.6095 | -1.6113 | -0.31128 | 0.01831 | 0.28839 | 120.8313 | 120.9915 | 120.9824 | 120.3873 | 120.1035 | 122.612 | 120.8588 | -0.31128 | 120.3873 | 120.1035 | 120.8588 | 120.9824 | 122.612 | -2.7786 | -122.905
3668.9062 | 122.5662 | -120.8176 | 1.8036 | -0.2095 | -0.0031786 | -0.012567 | 0.026117 | -0.0026212 | -0.0024289 | 0.0098203 | -0.61798 | -0.32959 | -0.9201 | 0.85602 | 0.33417 | 0.2243 | -0.018311 | 0.21057 | 1.8173 | -121.1151 | 119.8975 | -2.1332 | 120.1996 | 121.6736 | -1.4694 | -0.29755 | 0.013733 | 0.30212 | 120.7993 | 121.0281 | 121.1517 | 120.488 | 120.1996 | 122.6349 | 121.0419 | -0.29755 | 120.488 | 120.1996 | 121.0419 | 121.1517 | 122.6349 | -2.7237 | -122.9187
3669.9062 | 122.612 | -120.8084 | 1.7899 | -0.19424 | -0.00061524 | -0.013636 | 0.022699 | -0.0036892 | -0.0024289 | 0.0096067 | -0.59967 | -0.34332 | -0.89722 | 0.62256 | 0.21057 | 0.36163 | 0.22888 | 0.027466 | 1.8127 | -121.1151 | 119.9112 | -2.1332 | 120.2087 | 121.431 | -1.5793 | -0.3067 | 0.022888 | 0.29755 | 121.0373 | 120.8359 | 121.019 | 120.4651 | 120.2087 | 122.6212 | 121.17 | -0.3067 | 120.4651 | 120.2087 | 121.17 | 121.019 | 122.6212 | -2.6871 | -122.905
3670.9062 | 122.5571 | -120.8405 | 1.7258 | -0.27054 | -0.0027514 | -0.011713 | 0.02334 | -0.0058256 | -0.0017881 | 0.0093931 | -0.54474 | -0.28381 | -0.88348 | 0.60883 | 0.10986 | 0.15106 | 0.16937 | 0.35706 | 1.7258 | -121.1243 | 119.957 | -2.0096 | 120.2957 | 121.4493 | -1.6159 | -0.28381 | 0 | 0.33875 | 121.0098 | 121.1975 | 120.9503 | 120.5566 | 120.2957 | 122.5662 | 120.9915 | -0.28381 | 120.5566 | 120.2957 | 120.9915 | 120.9503 | 122.5662 | -2.6093 | -122.85
3671.9062 | 122.5891 | -120.9457 | 1.6342 | -0.072174 | -0.0010424 | -0.0091494 | 0.022913 | -0.0028348 | -0.0026425 | 0.011316 | -0.59509 | -0.34332 | -0.90637 | 0.5722 | 0.11902 | 0.14191 | 0.19226 | 0.23804 | 1.6342 | -121.2662 | 120.0394 | -1.9775 | 120.3506 | 121.5179 | -1.5152 | -0.32043 | 0 | 0.31128 | 121.138 | 121.1838 | 121.0648 | 120.6024 | 120.3506 | 122.58 | 121.0876 | -0.32043 | 120.6024 | 120.3506 | 121.0876 | 121.0648 | 122.58 | -2.5406 | -122.9004
3672.9062 | 122.6624 | -120.9869 | 1.5381 | -0.21713 | -0.0048876 | -0.0091494 | 0.021631 | -0.0058256 | -0.0030697 | 0.010675 | -0.4715 | -0.32044 | -0.85144 | 0.61798 | 0.20599 | 0.21515 | 0.10529 | 0.31586 | 1.5701 | -121.2845 | 120.1355 | -1.8585 | 120.5154 | 121.6049 | -1.3321 | -0.29755 | 0.032043 | 0.37994 | 121.0922 | 121.3028 | 121.1929 | 120.6665 | 120.5154 | 122.5571 | 121.2021 | -0.29755 | 120.6665 | 120.5154 | 121.2021 | 121.1929 | 122.5571 | -2.3895 | -122.8226
3673.9062 | 122.6166 | -120.9503 | 1.6388 | -0.20187 | -0.0025378 | -0.010858 | 0.024408 | -0.003903 | -0.00071986 | 0.0068295 | -0.55847 | -0.32501 | -0.86975 | 0.60425 | 0.1236 | 0.15564 | 0.16937 | 0.2243 | 1.6891 | -121.257 | 120.0806 | -1.9638 | 120.3918 | 121.5546 | -1.5152 | -0.3067 | 0.050354 | 0.31128 | 121.1197 | 121.1746 | 121.0739 | 120.6253 | 120.3918 | 122.6395 | 121.106 | -0.3067 | 120.6253 | 120.3918 | 121.106 | 121.0739 | 122.6395 | -2.5085 | -122.8958
3674.9062 | 122.6028 | -120.8588 | 1.7487 | 0.19485 | -0.0023242 | -0.010431 | 0.025263 | -0.0043302 | -0.0024289 | 0.0093931 | -0.56763 | -0.27466 | -0.87891 | 0.62714 | 0.12817 | 0.14648 | 0.16479 | 0.19684 | 1.7532 | -121.1655 | 119.9799 | -2.0233 | 120.2911 | 121.4859 | -1.6205 | -0.3067 | 0.004578 | 0.31128 | 121.0236 | 121.0556 | 120.9869 | 120.5841 | 120.2911 | 122.612 | 121.0052 | -0.3067 | 120.5841 | 120.2911 | 121.0052 | 120.9869 | 122.612 | -2.6276 | -122.9141
3675.9219 | 122.4976 | -120.8359 | 1.7166 | 0.13382 | 0.00066656 | -0.0070132 | 0.027613 | -0.002194 | -0.0022153 | 0.011102 | -0.62714 | -0.37079 | -0.94757 | 0.59052 | 0.064087 | 0.11902 | 0.1236 | 0.14191 | 1.7441 | -121.1838 | 119.8883 | -2.0874 | 120.2087 | 121.4264 | -1.6525 | -0.3479 | 0.027466 | 0.32044 | 120.9595 | 120.9778 | 120.9 | 120.4651 | 120.2087 | 122.58 | 120.9549 | -0.3479 | 120.4651 | 120.2087 | 120.9549 | 120.9 | 122.58 | -2.6642 | -122.9004
3676.9062 | 122.5983 | -120.7626 | 1.8311 | -0.63675 | -0.0038196 | -0.011713 | 0.022486 | -0.0028348 | -0.0030697 | 0.0087521 | -0.48981 | -0.33417 | -0.91553 | 0.67749 | 0.14648 | 0.16937 | 0.12817 | 0.19226 | 1.8723 | -121.0831 | 119.8471 | -2.1652 | 120.2728 | 121.4401 | -1.6846 | -0.32043 | 0.041198 | 0.42572 | 120.8908 | 120.9549 | 120.9091 | 120.4285 | 120.2728 | 122.6349 | 120.932 | -0.32043 | 120.4285 | 120.2728 | 120.932 | 120.9091 | 122.6349 | -2.7466 | -122.9141
3677.9062 | 122.5937 | -120.8588 | 1.7395 | -0.17899 | -0.0014696 | -0.011072 | 0.022699 | -0.003262 | -0.00050626 | 0.0081113 | -0.65918 | -0.37079 | -0.91553 | 0.59967 | 0.16022 | 0.20599 | 0.13733 | 0.21057 | 1.7761 | -121.1746 | 119.9432 | -2.1103 | 120.1996 | 121.4584 | -1.5793 | -0.31586 | 0.036621 | 0.25635 | 120.9961 | 121.0693 | 121.019 | 120.488 | 120.1996 | 122.6349 | 121.0648 | -0.31586 | 120.488 | 120.1996 | 121.0648 | 121.019 | 122.6349 | -2.655 | -122.9141
3678.9062 | 122.58 | -120.8633 | 1.767 | -0.24002 | 0.00023916 | -0.012354 | 0.023768 | -0.0030484 | -0.0015745 | 0.010461 | -0.64087 | -0.36163 | -0.91095 | 0.80566 | 0.17853 | 0.10986 | 0.13733 | 0.27008 | 1.799 | -121.1517 | 119.9524 | -2.1286 | 120.2225 | 121.669 | -1.5884 | -0.28839 | 0.032043 | 0.27008 | 121.0007 | 121.1334 | 121.0419 | 120.5017 | 120.2225 | 122.6624 | 120.9732 | -0.28839 | 120.5017 | 120.2225 | 120.9732 | 121.0419 | 122.6624 | -2.6779 | -122.9187
3679.9062 | 122.6578 | -120.8633 | 1.712 | -0.20187 | -0.0023242 | -0.012781 | 0.020991 | -0.0051846 | -0.0015745 | 0.0091795 | -0.54016 | -0.3891 | -0.89722 | 0.65002 | 0.17853 | 0.21515 | 0.11444 | 0.28381 | 1.7029 | -121.2067 | 119.9661 | -2.1011 | 120.3232 | 121.5134 | -1.5335 | -0.34332 | -0.009155 | 0.35706 | 120.9778 | 121.1472 | 121.0419 | 120.4742 | 120.3232 | 122.5662 | 121.0785 | -0.34332 | 120.4742 | 120.3232 | 121.0785 | 121.0419 | 122.5662 | -2.6093 | -122.9187
3680.9062 | 122.6257 | -120.8908 | 1.68 | -0.011139 | -0.001256 | -0.0055178 | 0.026545 | -0.0030484 | -0.0024289 | 0.0078977 | -0.56305 | -0.39368 | -0.9201 | 0.63629 | 0.12817 | 0.17853 | 0.10071 | 0.21515 | 1.7075 | -121.2296 | 119.9707 | -2.0737 | 120.3278 | 121.5271 | -1.5518 | -0.33874 | 0.027465 | 0.35706 | 120.9915 | 121.106 | 121.019 | 120.4971 | 120.3278 | 122.5983 | 121.0693 | -0.33874 | 120.4971 | 120.3278 | 121.0693 | 121.019 | 122.5983 | -2.6001 | -122.9095
3681.9062 | 122.5891 | -121.0602 | 1.5656 | -0.27054 | -0.0033922 | -0.007654 | 0.022699 | -0.0017666 | -0.0013609 | 0.010461 | -0.59967 | -0.33417 | -0.89722 | 0.53558 | 0.11902 | 0.13733 | 0.2243 | 0.22888 | 1.5884 | -121.3577 | 120.163 | -1.8997 | 120.4605 | 121.5958 | -1.4465 | -0.29755 | 0.022888 | 0.29755 | 121.2845 | 121.2891 | 121.1792 | 120.726 | 120.4605 | 122.6486 | 121.1975 | -0.29755 | 120.726 | 120.4605 | 121.1975 | 121.1792 | 122.6486 | -2.4628 | -122.9233
3682.9062 | 122.6074 | -121.1243 | 1.4923 | -0.30869 | -0.0021106 | -0.0095766 | 0.022272 | -0.0028348 | -0.0028561 | 0.010461 | -0.59509 | -0.30212 | -0.88806 | 0.50354 | 0.10071 | 0.12817 | 0.2655 | 0.23346 | 1.5244 | -121.4447 | 120.2362 | -1.7944 | 120.5292 | 121.6278 | -1.3916 | -0.32043 | 0.032043 | 0.29297 | 121.3898 | 121.3577 | 121.225 | 120.8221 | 120.5292 | 122.6486 | 121.2524 | -0.32043 | 120.8221 | 120.5292 | 121.2524 | 121.225 | 122.6486 | -2.3804 | -122.937
3683.9062 | 122.6074 | -121.1014 | 1.506 | -0.60623 | -0.0010424 | -0.010218 | 0.02334 | -0.0019802 | -0.00050626 | 0.010461 | -0.6134 | -0.31128 | -0.84686 | 0.49896 | 0.086975 | 0.11902 | 0.27008 | 0.25177 | 1.5152 | -121.4127 | 120.2545 | -1.8173 | 120.488 | 121.6003 | -1.4191 | -0.31128 | 0.009156 | 0.23346 | 121.3715 | 121.3531 | 121.1884 | 120.7901 | 120.488 | 122.6166 | 121.2204 | -0.31128 | 120.7901 | 120.488 | 121.2204 | 121.1884 | 122.6166 | -2.3529 | -122.9187
3684.9062 | 122.5983 | -121.1517 | 1.4648 | 0.53818 | -0.0023242 | -0.0063724 | 0.023127 | -0.0028348 | -0.0015745 | 0.0087521 | -0.67291 | -0.27466 | -0.84228 | 0.4715 | 0.10071 | 0.10529 | 0.29755 | 0.24261 | 1.5015 | -121.4447 | 120.3094 | -1.7395 | 120.4788 | 121.6232 | -1.3641 | -0.29297 | 0.036621 | 0.16937 | 121.4493 | 121.3943 | 121.2524 | 120.8771 | 120.4788 | 122.6532 | 121.257 | -0.29297 | 120.8771 | 120.4788 | 121.257 | 121.2524 | 122.6532 | -2.3071 | -122.9095
3685.9062 | 122.612 | -121.1288 | 1.4328 | -0.2095 | -0.0031786 | -0.0089358 | 0.020777 | -0.003903 | -0.0032835 | 0.0093931 | -0.31586 | -0.27008 | -0.82855 | 0.44403 | 0.10986 | 0.12817 | 0.26093 | 0.25177 | 1.4923 | -121.4722 | 120.3003 | -1.7029 | 120.813 | 121.5729 | -1.3229 | -0.34332 | 0.05951 | 0.51269 | 121.3898 | 121.3806 | 121.2387 | 120.8588 | 120.813 | 122.6212 | 121.257 | -0.34332 | 120.8588 | 120.813 | 121.257 | 121.2387 | 122.6212 | -2.2614 | -122.905
3686.9062 | 122.6303 | -121.1838 | 1.4236 | -0.23239 | -0.0042468 | -0.016199 | 0.021845 | -0.004971 | -0.0011471 | 0.0087521 | -0.50354 | -0.29755 | -0.81024 | 0.48523 | 0.12817 | 0.14648 | 0.2243 | 0.29755 | 1.4557 | -121.4539 | 120.3735 | -1.7212 | 120.6802 | 121.669 | -1.2955 | -0.27008 | 0.032043 | 0.3067 | 121.4081 | 121.4813 | 121.312 | 120.8862 | 120.6802 | 122.6395 | 121.3303 | -0.27008 | 120.8862 | 120.6802 | 121.3303 | 121.312 | 122.6395 | -2.2339 | -122.8775
3687.9062 | 122.58 | -121.0648 | 1.5152 | -0.24765 | -0.00082884 | -0.0057314 | 0.025263 | -0.0045438 | 0.00034814 | 0.0098203 | -0.46234 | -0.21057 | -0.77362 | 0.53101 | 0.16022 | 0.15106 | 0.23804 | 0.2655 | 1.561 | -121.4127 | 120.2911 | -1.7258 | 120.6024 | 121.5958 | -1.355 | -0.3479 | 0.045776 | 0.31128 | 121.3028 | 121.3303 | 121.225 | 120.8542 | 120.6024 | 122.6257 | 121.2158 | -0.3479 | 120.8542 | 120.6024 | 121.2158 | 121.225 | 122.6257 | -2.2888 | -122.9279
3688.9062 | 122.6303 | -120.9732 | 1.6022 | -0.13321 | -0.00061524 | -0.0067996 | 0.025263 | -0.0060392 | 0.00034814 | 0.0057615 | -0.28839 | -0.045776 | -0.62256 | 0.57678 | 0.10986 | 0.14191 | 0.19684 | 0.2243 | 1.6525 | -121.2891 | 120.3506 | -1.6479 | 120.6848 | 121.55 | -1.4923 | -0.31586 | 0.050354 | 0.33417 | 121.17 | 121.1975 | 121.0831 | 120.9274 | 120.6848 | 122.6257 | 121.1151 | -0.31586 | 120.9274 | 120.6848 | 121.1151 | 121.0831 | 122.6257 | -2.2247 | -122.8912
3689.9062 | 122.6257 | -121.0739 | 1.4969 | -0.18662 | -0.001256 | -0.012781 | 0.025263 | -0.0024076 | -0.0028561 | 0.0091795 | -0.29755 | -0.068665 | -0.63171 | 0.53101 | 0.10529 | 0.14191 | 0.21973 | 0.23346 | 1.5472 | -121.4081 | 120.4422 | -1.5656 | 120.7764 | 121.6049 | -1.3916 | -0.33417 | 0.050354 | 0.33417 | 121.2936 | 121.3074 | 121.1792 | 121.0052 | 120.7764 | 122.6212 | 121.2158 | -0.33417 | 121.0052 | 120.7764 | 121.2158 | 121.1792 | 122.6212 | -2.1286 | -122.905
3690.9062 | 122.6578 | -121.2158 | 1.3733 | -0.056915 | -0.00082884 | -0.011072 | 0.026545 | -0.00091219 | -0.0043515 | 0.0096067 | -0.036621 | -0.059509 | -0.60883 | 0.51727 | 0.16022 | 0.16937 | 0.20599 | 0.28839 | 1.4236 | -121.5454 | 120.607 | -1.4328 | 121.1792 | 121.7331 | -1.2131 | -0.32959 | 0.050354 | 0.5722 | 121.4218 | 121.5042 | 121.376 | 121.1563 | 121.1792 | 122.6395 | 121.3852 | -0.32959 | 121.1563 | 121.1792 | 121.3852 | 121.376 | 122.6395 | -1.9821 | -122.9187
3691.9062 | 122.644 | -121.2753 | 1.3184 | -0.17899 | -0.0014696 | -0.0078678 | 0.024836 | -0.002194 | -0.0028561 | 0.0096067 | -0.28839 | -0.059509 | -0.62256 | 0.44403 | 0.091553 | 0.11444 | 0.27924 | 0.26093 | 1.3458 | -121.5866 | 120.6528 | -1.3779 | 120.9869 | 121.7194 | -1.2268 | -0.31128 | 0.027466 | 0.33417 | 121.5546 | 121.5363 | 121.3669 | 121.2158 | 120.9869 | 122.6212 | 121.3898 | -0.31128 | 121.2158 | 120.9869 | 121.3898 | 121.3669 | 122.6212 | -1.9409 | -122.905
3692.9062 | 122.5937 | -121.3165 | 1.3138 | -0.24002 | -0.002965 | -0.0097904 | 0.024408 | -0.0051846 | -0.0028561 | 0.010675 | -0.30212 | -0.036621 | -0.6134 | 0.43945 | 0.09613 | 0.10071 | 0.29297 | 0.2655 | 1.3367 | -121.6324 | 120.7031 | -1.3504 | 121.0144 | 121.756 | -1.2177 | -0.31586 | 0.022888 | 0.31128 | 121.6095 | 121.582 | 121.4127 | 121.2799 | 121.0144 | 122.6532 | 121.4172 | -0.31586 | 121.2799 | 121.0144 | 121.4172 | 121.4127 | 122.6532 | -1.9272 | -122.9462
3693.9062 | 122.6303 | -121.2662 | 1.3504 | -0.45364 | -0.00040164 | -0.0089358 | 0.019495 | -0.003262 | -0.0017881 | 0.0091795 | -0.30212 | -0.073242 | -0.61798 | 0.45776 | 0.10529 | 0.11902 | 0.28381 | 0.2655 | 1.387 | -121.5683 | 120.6482 | -1.4236 | 120.9641 | 121.7239 | -1.2451 | -0.30212 | 0.036621 | 0.31586 | 121.55 | 121.5317 | 121.3715 | 121.1929 | 120.9641 | 122.6532 | 121.3852 | -0.30212 | 121.1929 | 120.9641 | 121.3852 | 121.3715 | 122.6532 | -1.9684 | -122.9187
3694.9062 | 122.6074 | -121.2845 | 1.3458 | -0.14084 | -0.0014696 | -0.010858 | 0.024408 | -0.003903 | -0.0032835 | 0.011956 | -0.32501 | -0.036621 | -0.63629 | 0.46692 | 0.082397 | 0.12817 | 0.3067 | 0.25177 | 1.3504 | -121.6232 | 120.6482 | -1.3824 | 120.9595 | 121.7514 | -1.2634 | -0.33875 | 0.004578 | 0.31128 | 121.5912 | 121.5363 | 121.3669 | 121.2479 | 120.9595 | 122.6349 | 121.4127 | -0.33875 | 121.2479 | 120.9595 | 121.4127 | 121.3669 | 122.6349 | -1.9821 | -122.9691
3695.9062 | 122.6486 | -121.2845 | 1.3138 | -0.21713 | 0.00023916 | -0.0085086 | 0.025904 | -0.0051846 | -0.00093346 | 0.0053343 | -0.30212 | -0.064087 | -0.61798 | 0.4715 | 0.10986 | 0.12817 | 0.26093 | 0.27466 | 1.3367 | -121.6095 | 120.6665 | -1.3779 | 120.9824 | 121.756 | -1.2039 | -0.32501 | 0.022888 | 0.31586 | 121.5454 | 121.5591 | 121.3943 | 121.2204 | 120.9824 | 122.6212 | 121.4127 | -0.32501 | 121.2204 | 120.9824 | 121.4127 | 121.3943 | 122.6212 | -1.9318 | -122.9233
3696.9219 | 122.6212 | -121.2936 | 1.3275 | 0.24826 | -0.0021106 | -0.0087222 | 0.02569 | -0.0028348 | -0.0011471 | 0.0085385 | -0.32044 | -0.082397 | -0.67291 | 0.44861 | 0.082397 | 0.11444 | 0.20599 | 0.2243 | 1.3412 | -121.6141 | 120.6207 | -1.4099 | 120.9732 | 121.7422 | -1.2451 | -0.32044 | 0.013733 | 0.35248 | 121.4996 | 121.5179 | 121.376 | 121.2112 | 120.9732 | 122.6349 | 121.4081 | -0.32044 | 121.2112 | 120.9732 | 121.4081 | 121.376 | 122.6349 | -2.0004 | -122.9416
3697.9062 | 122.644 | -121.3074 | 1.2909 | -0.1561 | -0.0016834 | -0.010858 | 0.026545 | -0.0013394 | 0.00034814 | 0.010461 | -0.27466 | -0.045776 | -0.59967 | 0.45776 | 0.09613 | 0.1236 | 0.27924 | 0.27008 | 1.3412 | -121.637 | 120.7077 | -1.3367 | 121.0327 | 121.7651 | -1.1948 | -0.32959 | 0.050354 | 0.32501 | 121.5866 | 121.5775 | 121.4035 | 121.2616 | 121.0327 | 122.6486 | 121.431 | -0.32959 | 121.2616 | 121.0327 | 121.431 | 121.4035 | 122.6486 | -1.8906 | -122.9279
3698.9062 | 122.6395 | -121.3486 | 1.2726 | -0.21713 | -0.003606 | -0.010858 | 0.022699 | -0.0011258 | -0.0028561 | 0.0087521 | -0.27924 | -0.027466 | -0.60425 | 0.45319 | 0.09613 | 0.1236 | 0.29297 | 0.28381 | 1.3092 | -121.6415 | 120.7443 | -1.3 | 121.0693 | 121.8018 | -1.1765 | -0.29297 | 0.036621 | 0.32501 | 121.6415 | 121.6324 | 121.4447 | 121.3211 | 121.0693 | 122.6578 | 121.4722 | -0.29297 | 121.3211 | 121.0693 | 121.4722 | 121.4447 | 122.6578 | -1.8768 | -122.9141
3699.9062 | 122.644 | -121.3806 | 1.2726 | -0.20187 | -0.0025378 | -0.0074404 | 0.023768 | -0.0024076 | -0.0045651 | 0.0081113 | -0.28839 | -0.027466 | -0.58594 | 0.43488 | 0.091553 | 0.10071 | 0.3067 | 0.27008 | 1.2817 | -121.6873 | 120.7947 | -1.3 | 121.0922 | 121.8155 | -1.181 | -0.3067 | 0.009155 | 0.29755 | 121.6873 | 121.6507 | 121.4722 | 121.3531 | 121.0922 | 122.6624 | 121.4813 | -0.3067 | 121.3531 | 121.0922 | 121.4813 | 121.4722 | 122.6624 | -1.8585 | -122.9599
3700.9062 | 122.6624 | -121.3486 | 1.268 | -0.27054 | -0.0033922 | -0.0059452 | 0.020777 | -0.0030484 | -0.0011471 | 0.0098203 | -0.33417 | -0.059509 | -0.60883 | 0.39825 | 0.32044 | 0.27466 | 0.21057 | 0.15564 | 1.3138 | -121.6827 | 120.7397 | -1.3275 | 121.0144 | 121.7468 | -0.94757 | -0.33417 | 0.045777 | 0.27466 | 121.5591 | 121.5042 | 121.669 | 121.2891 | 121.0144 | 122.6624 | 121.6232 | -0.33417 | 121.2891 | 121.0144 | 121.6232 | 121.669 | 122.6624 | -1.8768 | -122.9507
3701.9219 | 122.644 | -121.4035 | 1.1993 | 0.13382 | 0.00023916 | -0.010858 | 0.026331 | -0.0047574 | -7.9062e-05 | 0.0078977 | -0.29297 | -0.064087 | -0.61798 | 0.40283 | 0.09613 | 0.11902 | 0.21057 | 0.25635 | 1.2451 | -121.7285 | 120.7855 | -1.2634 | 121.1105 | 121.8063 | -1.1032 | -0.32501 | 0.045776 | 0.32501 | 121.6141 | 121.6599 | 121.4996 | 121.3394 | 121.1105 | 122.6486 | 121.5225 | -0.32501 | 121.3394 | 121.1105 | 121.5225 | 121.4996 | 122.6486 | -1.8173 | -122.9279
3702.9062 | 122.6624 | -121.431 | 1.181 | -0.22476 | -0.00082884 | -0.006586 | 0.026117 | -0.0045438 | -0.0011471 | 0.0098203 | -0.25177 | -0.045776 | -0.59509 | 0.43488 | 0.10071 | 0.13275 | 0.27924 | 0.29297 | 1.2497 | -121.7377 | 120.8359 | -1.2268 | 121.1792 | 121.8658 | -1.0803 | -0.3067 | 0.068665 | 0.34332 | 121.7102 | 121.7239 | 121.5317 | 121.3852 | 121.1792 | 122.6807 | 121.5637 | -0.3067 | 121.3852 | 121.1792 | 121.5637 | 121.5317 | 122.6807 | -1.7761 | -122.9187
3703.9062 | 122.6624 | -121.4401 | 1.1719 | -0.10269 | -0.002965 | -0.010431 | 0.026331 | -0.0019802 | -0.0011471 | 0.0091795 | -0.29297 | -0.064087 | -0.64087 | 0.41199 | 0.10071 | 0.10986 | 0.28839 | 0.3067 | 1.2222 | -121.7606 | 120.7993 | -1.236 | 121.1472 | 121.8521 | -1.0712 | -0.32043 | 0.050354 | 0.3479 | 121.7285 | 121.7468 | 121.5408 | 121.376 | 121.1472 | 122.6624 | 121.55 | -0.32043 | 121.376 | 121.1472 | 121.55 | 121.5408 | 122.6624 | -1.8127 | -122.9324
3704.9062 | 122.6669 | -121.4172 | 1.1719 | -0.1561 | -0.00061524 | -0.009363 | 0.024622 | -0.0034756 | -0.0030697 | 0.0089657 | -0.32959 | -0.10071 | -0.64087 | 0.39368 | 0.082397 | 0.10986 | 0.31128 | 0.28839 | 1.2222 | -121.7514 | 120.7764 | -1.2726 | 121.0876 | 121.8109 | -1.0895 | -0.33417 | 0.050354 | 0.31128 | 121.7285 | 121.7056 | 121.4996 | 121.3165 | 121.0876 | 122.6395 | 121.5271 | -0.33417 | 121.3165 | 121.0876 | 121.5271 | 121.4996 | 122.6395 | -1.8127 | -122.9233
3705.9062 | 122.6624 | -121.4218 | 1.1902 | -0.17899 | 0.00023916 | -0.010431 | 0.027186 | -0.0036892 | -0.0037107 | 0.0089657 | -0.2655 | -0.082397 | -0.63171 | 0.43945 | 0.14648 | 0.15564 | 0.24261 | 0.31586 | 1.2268 | -121.7514 | 120.7901 | -1.2726 | 121.1563 | 121.8613 | -1.0437 | -0.32959 | 0.036621 | 0.36621 | 121.6644 | 121.7377 | 121.5683 | 121.3394 | 121.1563 | 122.6486 | 121.5775 | -0.32959 | 121.3394 | 121.1563 | 121.5775 | 121.5683 | 122.6486 | -1.8219 | -122.9416
3706.9219 | 122.731 | -121.3531 | 1.1627 | 0.12619 | -0.00061524 | -0.0059452 | 0.018854 | -0.00091219 | -0.0011471 | 0.0083249 | -0.26093 | -0.15564 | -0.62714 | 0.48981 | 0.18768 | 0.23346 | 0.11444 | 0.38452 | 1.1948 | -121.6965 | 120.726 | -1.3184 | 121.0922 | 121.843 | -0.97504 | -0.34332 | 0.032043 | 0.36621 | 121.4676 | 121.7377 | 121.5408 | 121.1975 | 121.0922 | 122.5479 | 121.5866 | -0.34332 | 121.1975 | 121.0922 | 121.5866 | 121.5408 | 122.5479 | -1.7899 | -122.8592
3707.9062 | 122.5937 | -121.4035 | 1.2405 | -0.23239 | -0.00061524 | -0.0091494 | 0.02035 | -0.0043302 | 0.00056194 | 0.0081113 | -0.32501 | -0.068665 | -0.59509 | 0.38452 | 0.082397 | 0.059509 | 0.74158 | 0.42572 | 1.2634 | -121.7148 | 120.8084 | -1.3092 | 121.0785 | 121.788 | -1.1581 | -0.31128 | 0.022888 | 0.27008 | 122.1451 | 121.8292 | 121.4859 | 121.3348 | 121.0785 | 122.6669 | 121.463 | -0.31128 | 121.3348 | 121.0785 | 121.463 | 121.4859 | 122.6669 | -1.8356 | -122.9553
3708.9062 | 122.6395 | -121.4493 | 1.1765 | -0.17136 | -0.00018804 | -0.012354 | 0.024622 | -0.0041166 | -0.0026425 | 0.0096067 | -0.30212 | -0.064087 | -0.62256 | 0.38452 | 0.10071 | 0.10071 | 0.33417 | 0.27008 | 1.2131 | -121.7789 | 120.8267 | -1.2405 | 121.1472 | 121.8338 | -1.0757 | -0.32959 | 0.036621 | 0.32043 | 121.7834 | 121.7194 | 121.55 | 121.3852 | 121.1472 | 122.6624 | 121.55 | -0.32959 | 121.3852 | 121.1472 | 121.55 | 121.55 | 122.6624 | -1.799 | -122.9553
3709.9062 | 122.6486 | -121.4218 | 1.181 | -0.14847 | 0.00066656 | -0.0095766 | 0.024836 | -0.0013394 | -0.0013609 | 0.0081113 | -0.30212 | -0.064087 | -0.63171 | 0.41199 | 0.10071 | 0.10986 | 0.32501 | 0.31128 | 1.2314 | -121.7377 | 120.7901 | -1.2451 | 121.1197 | 121.8338 | -1.0803 | -0.31586 | 0.050354 | 0.32959 | 121.7468 | 121.7331 | 121.5225 | 121.3577 | 121.1197 | 122.6532 | 121.5317 | -0.31586 | 121.3577 | 121.1197 | 121.5317 | 121.5225 | 122.6532 | -1.8127 | -122.9187
3710.9219 | 122.6303 | -121.4401 | 1.1765 | 0.24063 | 2.5564e-05 | -0.0070132 | 0.026545 | -0.0019802 | -0.00071986 | 0.0072569 | -0.32501 | -0.086975 | -0.65002 | 0.40283 | 0.059509 | 0.10986 | 0.27008 | 0.26093 | 1.2314 | -121.7331 | 120.7901 | -1.2634 | 121.1151 | 121.843 | -1.1169 | -0.29297 | 0.054931 | 0.32501 | 121.7102 | 121.701 | 121.4996 | 121.3531 | 121.1151 | 122.6715 | 121.55 | -0.29297 | 121.3531 | 121.1151 | 121.55 | 121.4996 | 122.6715 | -1.8265 | -122.9095
3711.9062 | 122.6532 | -121.4355 | 1.2085 | -0.18662 | 0.00066656 | -0.006586 | 0.02334 | -0.0026212 | 0.00056194 | 0.0098203 | -0.31586 | -0.068665 | -0.63629 | 0.41199 | 0.086975 | 0.11902 | 0.32501 | 0.28839 | 1.2497 | -121.7422 | 120.7993 | -1.2772 | 121.1197 | 121.8475 | -1.1215 | -0.3067 | 0.041199 | 0.32043 | 121.7606 | 121.7239 | 121.5225 | 121.3669 | 121.1197 | 122.6852 | 121.5546 | -0.3067 | 121.3669 | 121.1197 | 121.5546 | 121.5225 | 122.6852 | -1.8448 | -122.9507
3712.9062 | 122.6624 | -121.4401 | 1.1765 | -0.20187 | -0.0021106 | -0.0070132 | 0.024195 | -0.0036892 | -0.0028561 | 0.0098203 | -0.33417 | -0.086975 | -0.6546 | 0.41199 | 0.082397 | 0.11902 | 0.33417 | 0.28839 | 1.2268 | -121.7651 | 120.7855 | -1.2634 | 121.106 | 121.8521 | -1.0941 | -0.32501 | 0.050354 | 0.32044 | 121.7743 | 121.7285 | 121.5225 | 121.3531 | 121.106 | 122.6669 | 121.5591 | -0.32501 | 121.3531 | 121.106 | 121.5591 | 121.5225 | 122.6669 | -1.8311 | -122.9416
3713.9062 | 122.6486 | -121.4401 | 1.1765 | -0.20187 | -0.002965 | -0.008295 | 0.024836 | -0.0017666 | -0.00071986 | 0.0098203 | -0.32959 | -0.082397 | -0.64087 | 0.40283 | 0.091553 | 0.10529 | 0.33875 | 0.30212 | 1.2222 | -121.756 | 120.7993 | -1.2589 | 121.1105 | 121.843 | -1.0849 | -0.31586 | 0.045776 | 0.31128 | 121.7789 | 121.7422 | 121.5317 | 121.3577 | 121.1105 | 122.6624 | 121.5454 | -0.31586 | 121.3577 | 121.1105 | 121.5454 | 121.5317 | 122.6624 | -1.8173 | -122.9324
3714.9062 | 122.6257 | -121.4355 | 1.1765 | -0.19424 | -0.0025378 | -0.008295 | 0.020563 | -0.0024076 | -0.0039243 | 0.010888 | -0.33417 | -0.064087 | -0.62714 | 0.3891 | 0.086975 | 0.10986 | 0.3479 | 0.3067 | 1.2222 | -121.7422 | 120.8084 | -1.2405 | 121.1014 | 121.8246 | -1.0895 | -0.3067 | 0.045776 | 0.29297 | 121.7834 | 121.7422 | 121.5225 | 121.3715 | 121.1014 | 122.6578 | 121.5454 | -0.3067 | 121.3715 | 121.1014 | 121.5454 | 121.5225 | 122.6578 | -1.8036 | -122.9187
3715.9062 | 122.6761 | -121.4401 | 1.1673 | -0.20187 | 2.5564e-05 | -0.011072 | 0.026758 | -0.0030484 | 0.0014163 | 0.0087521 | -0.29755 | -0.068665 | -0.63629 | 0.40283 | 0.091553 | 0.11444 | 0.32044 | 0.31128 | 1.1993 | -121.7789 | 120.8038 | -1.236 | 121.1426 | 121.843 | -1.0757 | -0.33875 | 0.032044 | 0.33875 | 121.7606 | 121.7514 | 121.5317 | 121.3715 | 121.1426 | 122.6395 | 121.5546 | -0.33875 | 121.3715 | 121.1426 | 121.5546 | 121.5317 | 122.6395 | -1.8036 | -122.9462
3716.9062 | 122.6624 | -121.463 | 1.181 | -0.16373 | -0.001256 | -0.0072268 | 0.025049 | -0.0034756 | -0.0017881 | 0.0072569 | -0.28839 | -0.064087 | -0.60883 | 0.40283 | 0.086975 | 0.10071 | 0.32044 | 0.31128 | 1.1948 | -121.7834 | 120.8542 | -1.2451 | 121.1746 | 121.8658 | -1.0941 | -0.32043 | 0.013733 | 0.32043 | 121.7834 | 121.7743 | 121.55 | 121.3989 | 121.1746 | 122.6578 | 121.5637 | -0.32043 | 121.3989 | 121.1746 | 121.5637 | 121.55 | 122.6578 | -1.7899 | -122.9645
3717.9062 | 122.6578 | -121.4767 | 1.181 | -0.18662 | -0.002965 | -0.0095766 | 0.024622 | -0.003262 | -7.9062e-05 | 0.010888 | -0.30212 | -0.041199 | -0.59509 | 0.3891 | 0.086975 | 0.091553 | 0.32501 | 0.30212 | 1.2039 | -121.7972 | 120.8817 | -1.2222 | 121.1746 | 121.8658 | -1.0941 | -0.32043 | 0.022888 | 0.29297 | 121.8018 | 121.7789 | 121.5637 | 121.4355 | 121.1746 | 122.6807 | 121.5683 | -0.32043 | 121.4355 | 121.1746 | 121.5683 | 121.5637 | 122.6807 | -1.7761 | -122.9782
3718.9062 | 122.6395 | -121.4493 | 1.1581 | -0.17899 | -0.00040164 | -0.009363 | 0.024195 | -0.0034756 | -0.0028561 | 0.0093931 | -0.29297 | -0.050354 | -0.6134 | 0.39368 | 0.082397 | 0.10529 | 0.34332 | 0.29297 | 1.1948 | -121.8063 | 120.8359 | -1.2085 | 121.1563 | 121.843 | -1.0757 | -0.35706 | 0.036621 | 0.32043 | 121.7926 | 121.7422 | 121.5317 | 121.3989 | 121.1563 | 122.644 | 121.5546 | -0.35706 | 121.3989 | 121.1563 | 121.5546 | 121.5317 | 122.644 | -1.7715 | -122.9645
3719.9062 | 122.6486 | -121.4767 | 1.1765 | -0.25528 | -0.0031786 | -0.0085086 | 0.022913 | -0.0030484 | -0.00071986 | 0.0089657 | -0.30212 | -0.050354 | -0.59967 | 0.3891 | 0.086975 | 0.10986 | 0.33875 | 0.30212 | 1.2222 | -121.7789 | 120.8771 | -1.2268 | 121.1746 | 121.8658 | -1.0895 | -0.30212 | 0.045776 | 0.29755 | 121.8155 | 121.7789 | 121.5637 | 121.4264 | 121.1746 | 122.699 | 121.5866 | -0.30212 | 121.4264 | 121.1746 | 121.5866 | 121.5637 | 122.699 | -1.7761 | -122.9553
3720.9062 | 122.6395 | -121.4676 | 1.1536 | 0.027008 | -0.00018804 | -0.0044498 | 0.026117 | -0.0011258 | -0.0022153 | 0.0078977 | -0.30212 | -0.10529 | -0.63171 | 0.37994 | 0.054932 | 0.091553 | 0.27924 | 0.24719 | 1.1948 | -121.7926 | 120.8359 | -1.2589 | 121.1655 | 121.8475 | -1.0986 | -0.32501 | 0.041199 | 0.32959 | 121.7468 | 121.7148 | 121.5225 | 121.3623 | 121.1655 | 122.6624 | 121.5591 | -0.32501 | 121.3623 | 121.1655 | 121.5591 | 121.5225 | 122.6624 | -1.7853 | -122.9462
3721.9062 | 122.6303 | -121.4767 | 1.1719 | -0.26291 | -0.0025378 | -0.013208 | 0.018854 | -0.0041166 | -0.0015745 | 0.0072569 | -0.2655 | -0.059509 | -0.57678 | 0.39825 | 0.09613 | 0.09613 | 0.32959 | 0.31128 | 1.1993 | -121.788 | 120.9 | -1.2314 | 121.2112 | 121.875 | -1.0757 | -0.31128 | 0.027466 | 0.31128 | 121.8063 | 121.788 | 121.5729 | 121.4172 | 121.2112 | 122.6761 | 121.5729 | -0.31128 | 121.4172 | 121.2112 | 121.5729 | 121.5729 | 122.6761 | -1.7487 | -122.9599
3722.9062 | 122.644 | -121.4447 | 1.2177 | -0.2095 | -0.001256 | -0.012567 | 0.02334 | -0.0024076 | 0.00077554 | 0.010034 | -0.064087 | -0.022888 | -0.57678 | 0.39368 | 0.09613 | 0.11444 | 0.35706 | 0.30212 | 1.2634 | -121.7422 | 120.8679 | -1.2405 | 121.3806 | 121.8384 | -1.1215 | -0.29755 | 0.045777 | 0.5127 | 121.8018 | 121.7468 | 121.5408 | 121.4218 | 121.3806 | 122.7081 | 121.5591 | -0.29755 | 121.4218 | 121.3806 | 121.5591 | 121.5408 | 122.7081 | -1.7944 | -122.9599
3723.9062 | 122.6624 | -121.3989 | 1.236 | -0.17899 | -0.001256 | -0.006586 | 0.025263 | -0.0028348 | -7.9062e-05 | 0.0096067 | -0.30212 | -0.07782 | -0.62256 | 0.43945 | 0.091553 | 0.1236 | 0.32044 | 0.29297 | 1.2955 | -121.7285 | 120.7764 | -1.3138 | 121.0968 | 121.8384 | -1.1444 | -0.32959 | 0.059509 | 0.32043 | 121.7194 | 121.6919 | 121.4905 | 121.3211 | 121.0968 | 122.6944 | 121.5225 | -0.32959 | 121.3211 | 121.0968 | 121.5225 | 121.4905 | 122.6944 | -1.8585 | -122.9645
3724.9062 | 122.644 | -121.3715 | 1.2634 | -0.18662 | -0.0014696 | -0.0053042 | 0.023554 | -0.0034756 | -0.0022153 | 0.0093931 | -0.30212 | -0.045776 | -0.6134 | 0.43488 | 0.10529 | 0.10071 | 0.31128 | 0.29297 | 1.2863 | -121.7148 | 120.7581 | -1.3092 | 121.0693 | 121.8063 | -1.1581 | -0.34332 | 0.022888 | 0.31128 | 121.6827 | 121.6644 | 121.4767 | 121.3257 | 121.0693 | 122.6578 | 121.4722 | -0.34332 | 121.3257 | 121.0693 | 121.4722 | 121.4767 | 122.6578 | -1.8768 | -122.9782
3725.9062 | 122.6944 | -121.344 | 1.2817 | -0.072174 | -0.0021106 | -0.0078678 | 0.025904 | -0.0017666 | 0.00056194 | 0.0089657 | -0.23804 | -0.041199 | -0.60883 | 0.65918 | 0.16022 | 0.13733 | 0.41657 | 0.35248 | 1.3321 | -121.6599 | 120.7352 | -1.3229 | 121.106 | 122.0032 | -1.1215 | -0.31586 | 0.050354 | 0.37079 | 121.7606 | 121.6965 | 121.5042 | 121.3028 | 121.106 | 122.6761 | 121.4813 | -0.31586 | 121.3028 | 121.106 | 121.4813 | 121.5042 | 122.6761 | -1.8906 | -122.9416
3726.9062 | 122.6532 | -121.4035 | 1.2314 | -0.19424 | -0.00061524 | -0.0074404 | 0.021631 | -0.0017666 | -0.0030697 | 0.0089657 | -0.29755 | -0.041199 | -0.61798 | 0.41199 | 0.10529 | 0.1236 | 0.32501 | 0.27466 | 1.2726 | -121.7377 | 120.7855 | -1.2726 | 121.106 | 121.8155 | -1.1261 | -0.33417 | 0.041199 | 0.32044 | 121.7285 | 121.6782 | 121.5088 | 121.3623 | 121.106 | 122.6761 | 121.5271 | -0.33417 | 121.3623 | 121.106 | 121.5271 | 121.5088 | 122.6761 | -1.8494 | -122.9691
3727.9062 | 122.6486 | -121.4264 | 1.2039 | -0.42313 | -0.0025378 | -0.010431 | 0.022486 | -0.003262 | -0.0022153 | 0.0093931 | -0.32501 | -0.045776 | -0.60883 | 0.41657 | 0.10986 | 0.10071 | 0.35248 | 0.28839 | 1.2314 | -121.788 | 120.8176 | -1.2497 | 121.1014 | 121.843 | -1.0941 | -0.36163 | 0.027466 | 0.28381 | 121.7789 | 121.7148 | 121.5363 | 121.3806 | 121.1014 | 122.6578 | 121.5271 | -0.36163 | 121.3806 | 121.1014 | 121.5271 | 121.5363 | 122.6578 | -1.8127 | -122.9919
3728.9062 | 122.6532 | -121.431 | 1.181 | -0.22476 | -0.0031786 | -0.0097904 | 0.019709 | -0.0060392 | 0.00013454 | 0.0087521 | -0.24261 | -0.045776 | -0.55847 | 0.42572 | 0.11902 | 0.15106 | 0.29755 | 0.3067 | 1.2268 | -121.7514 | 120.8725 | -1.2268 | 121.1884 | 121.8567 | -1.062 | -0.32043 | 0.045777 | 0.31586 | 121.7285 | 121.7377 | 121.55 | 121.3852 | 121.1884 | 122.6578 | 121.582 | -0.32043 | 121.3852 | 121.1884 | 121.582 | 121.55 | 122.6578 | -1.7395 | -122.9324
3729.9062 | 122.644 | -121.4264 | 1.2177 | -1.7583 | 2.5564e-05 | -0.010431 | 0.022486 | -0.003903 | -0.0011471 | 0.010461 | -0.21057 | 0 | -0.54474 | 0.43488 | 0.10071 | 0.10986 | 0.3479 | 0.29755 | 1.2543 | -121.7834 | 120.8817 | -1.2177 | 121.2158 | 121.8613 | -1.1169 | -0.35705 | 0.036621 | 0.33417 | 121.7743 | 121.7239 | 121.5271 | 121.4264 | 121.2158 | 122.6807 | 121.5363 | -0.35705 | 121.4264 | 121.2158 | 121.5363 | 121.5271 | 122.6807 | -1.7624 | -123.0011
3730.9062 | 122.6212 | -121.4081 | 1.2268 | 0.042267 | -0.0010424 | -0.0063724 | 0.027186 | -0.0036892 | -0.0011471 | 0.0070431 | -0.27466 | -0.045776 | -0.60425 | 0.40283 | 0.059509 | 0.091553 | 0.28839 | 0.21973 | 1.2497 | -121.7651 | 120.8038 | -1.2726 | 121.1334 | 121.8109 | -1.1673 | -0.35706 | 0.022888 | 0.32959 | 121.6965 | 121.6278 | 121.4676 | 121.3623 | 121.1334 | 122.6578 | 121.4996 | -0.35706 | 121.3623 | 121.1334 | 121.4996 | 121.4676 | 122.6578 | -1.8311 | -122.9919
3731.9062 | 122.6486 | -121.431 | 1.1993 | -0.17136 | -0.00082884 | -0.0091494 | 0.021204 | -0.0013394 | -0.00093346 | 0.0089657 | -0.27466 | -0.022888 | -0.59052 | 0.40741 | 0.10529 | 0.1236 | 0.32959 | 0.28839 | 1.2451 | -121.756 | 120.8405 | -1.2222 | 121.1563 | 121.8384 | -1.0941 | -0.32501 | 0.045776 | 0.31586 | 121.7606 | 121.7194 | 121.5363 | 121.4081 | 121.1563 | 122.6761 | 121.5546 | -0.32501 | 121.4081 | 121.1563 | 121.5546 | 121.5363 | 122.6761 | -1.7899 | -122.9553
3732.9062 | 122.6395 | -121.4539 | 1.2222 | -0.20187 | -0.0031786 | -0.010004 | 0.025263 | -0.003903 | -0.0026425 | 0.010034 | -0.27466 | -0.018311 | -0.59052 | 0.41199 | 0.091553 | 0.11902 | 0.32501 | 0.29755 | 1.2543 | -121.7422 | 120.8633 | -1.2405 | 121.1792 | 121.8658 | -1.1307 | -0.28839 | 0.032043 | 0.31586 | 121.7789 | 121.7514 | 121.5454 | 121.4355 | 121.1792 | 122.7081 | 121.5729 | -0.28839 | 121.4355 | 121.1792 | 121.5729 | 121.5454 | 122.7081 | -1.8127 | -122.9645
3733.9062 | 122.644 | -121.4401 | 1.1902 | -0.24002 | -0.00061524 | -0.006586 | 0.02334 | -0.0026212 | -0.00071986 | 0.0074705 | -0.27008 | -0.027466 | -0.59967 | 0.41657 | 0.091553 | 0.10529 | 0.34332 | 0.29297 | 1.2268 | -121.756 | 120.8405 | -1.2177 | 121.17 | 121.8567 | -1.0986 | -0.31586 | 0.036621 | 0.32959 | 121.7834 | 121.7331 | 121.5317 | 121.4127 | 121.17 | 122.6669 | 121.5454 | -0.31586 | 121.4127 | 121.17 | 121.5454 | 121.5317 | 122.6669 | -1.7899 | -122.9462
3734.9062 | 122.6624 | -121.4264 | 1.1948 | -0.12558 | -0.0038196 | -0.010858 | 0.020563 | -0.0036892 | -0.0020017 | 0.0089657 | -0.27924 | -0.036621 | -0.58136 | 0.39368 | 0.10071 | 0.11444 | 0.36163 | 0.29297 | 1.2405 | -121.7834 | 120.845 | -1.2314 | 121.1472 | 121.8201 | -1.0941 | -0.35705 | 0.045777 | 0.30212 | 121.788 | 121.7194 | 121.5271 | 121.3898 | 121.1472 | 122.6669 | 121.5408 | -0.35705 | 121.3898 | 121.1472 | 121.5408 | 121.5271 | 122.6669 | -1.7761 | -122.9782
3735.9062 | 122.6807 | -121.4493 | 1.1765 | -0.19424 | 0.00045296 | -0.010431 | 0.027186 | -0.0030484 | -0.0011471 | 0.011102 | -0.27466 | -0.041199 | -0.59052 | 0.4303 | 0.086975 | 0.11444 | 0.32044 | 0.3067 | 1.2268 | -121.8109 | 120.8588 | -1.2177 | 121.1746 | 121.8796 | -1.0895 | -0.36163 | 0.050354 | 0.31586 | 121.7697 | 121.756 | 121.5363 | 121.4081 | 121.1746 | 122.6761 | 121.5637 | -0.36163 | 121.4081 | 121.1746 | 121.5637 | 121.5363 | 122.6761 | -1.767 | -122.9874
3736.9062 | 122.6898 | -121.463 | 1.1581 | -0.14847 | -0.00082884 | -0.0097904 | 0.025049 | -0.0026212 | -0.0024289 | 0.0083249 | -0.27466 | -0.036621 | -0.59967 | 0.42114 | 0.082397 | 0.10986 | 0.33417 | 0.30212 | 1.1993 | -121.8063 | 120.8633 | -1.1948 | 121.1884 | 121.8842 | -1.0757 | -0.34332 | 0.041199 | 0.32501 | 121.7972 | 121.7651 | 121.5454 | 121.4264 | 121.1884 | 122.6624 | 121.5729 | -0.34332 | 121.4264 | 121.1884 | 121.5729 | 121.5454 | 122.6624 | -1.7578 | -122.9645
3737.9062 | 122.6944 | -121.463 | 1.1902 | -0.21713 | -0.001256 | -0.0061588 | 0.025477 | -0.0026212 | -0.0015745 | 0.0089657 | -0.2655 | -0.050354 | -0.59509 | 0.41657 | 0.082397 | 0.11902 | 0.32501 | 0.29755 | 1.236 | -121.8109 | 120.8679 | -1.2405 | 121.1975 | 121.8796 | -1.1078 | -0.3479 | 0.045776 | 0.32959 | 121.788 | 121.7606 | 121.5454 | 121.4127 | 121.1975 | 122.699 | 121.582 | -0.3479 | 121.4127 | 121.1975 | 121.582 | 121.5454 | 122.699 | -1.7853 | -123.0011
3738.9062 | 122.6669 | -121.4493 | 1.1902 | -0.19424 | -0.0027514 | -0.0097904 | 0.024195 | -0.0051846 | -0.0032835 | 0.0081113 | -0.30212 | -0.064087 | -0.59967 | 0.41199 | 0.091553 | 0.10986 | 0.33875 | 0.28381 | 1.2222 | -121.7743 | 120.8496 | -1.2543 | 121.1472 | 121.8613 | -1.0986 | -0.32501 | 0.032043 | 0.29755 | 121.788 | 121.7331 | 121.5408 | 121.3852 | 121.1472 | 122.6715 | 121.5591 | -0.32501 | 121.3852 | 121.1472 | 121.5591 | 121.5408 | 122.6715 | -1.7899 | -122.9645
3739.9062 | 122.6669 | -121.4722 | 1.181 | -0.1561 | -0.001256 | -0.012567 | 0.025049 | -0.0024076 | -0.0015745 | 0.010034 | -0.31128 | -0.068665 | -0.59967 | 0.40741 | 0.10071 | 0.1236 | 0.32501 | 0.28839 | 1.2085 | -121.8018 | 120.8725 | -1.2497 | 121.1609 | 121.8796 | -1.0803 | -0.32959 | 0.027466 | 0.28839 | 121.7972 | 121.7606 | 121.5729 | 121.4035 | 121.1609 | 122.6807 | 121.5958 | -0.32959 | 121.4035 | 121.1609 | 121.5958 | 121.5729 | 122.6807 | -1.7807 | -122.9828
3740.9062 | 122.7036 | -121.3943 | 1.2177 | -1.4607 | 2.5564e-05 | -0.007654 | 0.028467 | -0.001553 | -0.0017881 | 0.010034 | -0.20599 | -0.027466 | -0.59052 | 0.4303 | 0.1236 | 0.15106 | 0.28381 | 0.32501 | 1.268 | -121.7422 | 120.8038 | -1.2451 | 121.1884 | 121.8246 | -1.0941 | -0.3479 | 0.050354 | 0.38452 | 121.6782 | 121.7194 | 121.5179 | 121.3669 | 121.1884 | 122.6624 | 121.5454 | -0.3479 | 121.3669 | 121.1884 | 121.5454 | 121.5179 | 122.6624 | -1.8082 | -122.9599
3741.9062 | 122.644 | -121.431 | 1.2726 | -0.18662 | -0.0033922 | -0.01214 | 0.02035 | -0.0017666 | -0.00093346 | 0.0087521 | -0.31128 | -0.041199 | -0.60883 | 0.46692 | 0.032043 | 0.009155 | 0.42572 | 0.35706 | 1.2772 | -121.7468 | 120.8221 | -1.3138 | 121.1197 | 121.8979 | -1.2405 | -0.31586 | 0.004578 | 0.29755 | 121.8567 | 121.788 | 121.463 | 121.3898 | 121.1197 | 122.7081 | 121.4401 | -0.31586 | 121.3898 | 121.1197 | 121.4401 | 121.463 | 122.7081 | -1.8814 | -123.0194
3742.9062 | 122.6669 | -121.4172 | 1.2589 | -0.20187 | -0.004674 | -0.006586 | 0.019922 | -0.0051846 | -0.0017881 | 0.0091795 | -0.28839 | -0.018311 | -0.56305 | 0.37994 | 0.1831 | 0.30212 | 0.43488 | 0.11444 | 1.2726 | -121.7102 | 120.8542 | -1.2772 | 121.1288 | 121.7972 | -1.0757 | -0.29297 | 0.013733 | 0.27466 | 121.8521 | 121.5317 | 121.6003 | 121.3989 | 121.1288 | 122.6898 | 121.7194 | -0.29297 | 121.3989 | 121.1288 | 121.7194 | 121.6003 | 122.6898 | -1.8219 | -122.9691
3743.9062 | 122.6807 | -121.4447 | 1.1948 | -0.11032 | -0.0031786 | -0.0074404 | 0.026117 | -0.002194 | -0.0026425 | 0.0098203 | -0.25177 | -0.036621 | -0.58136 | 0.41657 | 0.11444 | 0.12817 | 0.30212 | 0.31128 | 1.236 | -121.7606 | 120.8633 | -1.2314 | 121.1929 | 121.8613 | -1.0803 | -0.31586 | 0.041199 | 0.32959 | 121.7468 | 121.756 | 121.5591 | 121.4081 | 121.1929 | 122.6807 | 121.5729 | -0.31586 | 121.4081 | 121.1929 | 121.5729 | 121.5591 | 122.6807 | -1.7761 | -122.9553
3744.9062 | 122.7081 | -121.4447 | 1.1993 | -0.20187 | -0.00040164 | -0.0050906 | 0.026972 | -0.001553 | 0.00077554 | 0.011102 | -0.26093 | -0.027466 | -0.59967 | 0.41657 | 0.09613 | 0.1236 | 0.31128 | 0.32501 | 1.2405 | -121.7514 | 120.845 | -1.2268 | 121.1838 | 121.8613 | -1.1032 | -0.3067 | 0.041199 | 0.33875 | 121.756 | 121.7697 | 121.5408 | 121.4172 | 121.1838 | 122.6852 | 121.5683 | -0.3067 | 121.4172 | 121.1838 | 121.5683 | 121.5408 | 122.6852 | -1.799 | -122.9507
3745.9062 | 122.6624 | -121.4355 | 1.2177 | 0.1796 | 0.00066656 | -0.006586 | 0.029749 | -5.7592e-05 | -0.0028561 | 0.010888 | -0.56305 | -0.054932 | -0.59967 | 0.36163 | 0.022888 | 0.073242 | 0.32501 | 0.23804 | 1.2634 | -121.7606 | 120.8359 | -1.2726 | 120.8725 | 121.7972 | -1.1948 | -0.32501 | 0.045777 | 0.036621 | 121.7606 | 121.6736 | 121.4584 | 121.3806 | 120.8725 | 122.699 | 121.5088 | -0.32501 | 121.3806 | 120.8725 | 121.5088 | 121.4584 | 122.699 | -1.8173 | -122.9782
3746.9062 | 122.7081 | -121.4264 | 1.181 | -0.18662 | -0.0010424 | -0.0074404 | 0.025263 | -0.0028348 | -0.0017881 | 0.010034 | -0.27924 | -0.041199 | -0.60883 | 0.40283 | 0.10986 | 0.1236 | 0.3067 | 0.31128 | 1.2451 | -121.7834 | 120.8176 | -1.2222 | 121.1472 | 121.8292 | -1.0712 | -0.35705 | 0.064087 | 0.32959 | 121.7331 | 121.7377 | 121.5363 | 121.3852 | 121.1472 | 122.6715 | 121.55 | -0.35705 | 121.3852 | 121.1472 | 121.55 | 121.5363 | 122.6715 | -1.7899 | -122.9645
3747.9062 | 122.699 | -121.4172 | 1.2131 | -0.1561 | -0.00082884 | -0.0072268 | 0.024408 | -0.00091219 | -0.00050626 | 0.010034 | -0.28381 | -0.027466 | -0.59509 | 0.40741 | 0.10071 | 0.12817 | 0.29755 | 0.31586 | 1.2543 | -121.7422 | 120.8221 | -1.2405 | 121.1334 | 121.8246 | -1.1124 | -0.32501 | 0.041198 | 0.31128 | 121.7148 | 121.7331 | 121.5179 | 121.3898 | 121.1334 | 122.6715 | 121.5454 | -0.32501 | 121.3898 | 121.1334 | 121.5454 | 121.5179 | 122.6715 | -1.8082 | -122.9553
3748.9062 | 122.6486 | -121.4035 | 1.236 | -0.27054 | -0.00040164 | -0.011713 | 0.022913 | -0.0026212 | 0.00034814 | 0.0076841 | -0.28839 | -0.036621 | -0.59509 | 0.37994 | 0.082397 | 0.09613 | 0.36163 | 0.29755 | 1.2497 | -121.7743 | 120.8084 | -1.2726 | 121.1151 | 121.7834 | -1.1536 | -0.37079 | 0.013733 | 0.3067 | 121.7651 | 121.701 | 121.4859 | 121.3669 | 121.1151 | 122.6532 | 121.4996 | -0.37079 | 121.3669 | 121.1151 | 121.4996 | 121.4859 | 122.6532 | -1.8311 | -123.0103
3749.9062 | 122.699 | -121.4401 | 1.2131 | -0.17899 | -0.0038196 | -0.010858 | 0.023981 | -0.0013394 | -0.00071986 | 0.010034 | -0.30212 | -0.073242 | -0.6134 | 0.37994 | 0.086975 | 0.11444 | 0.33417 | 0.32501 | 1.2222 | -121.7789 | 120.8267 | -1.2863 | 121.138 | 121.8201 | -1.1261 | -0.33875 | 0.009155 | 0.31128 | 121.7743 | 121.7651 | 121.5271 | 121.3669 | 121.138 | 122.6624 | 121.5546 | -0.33875 | 121.3669 | 121.138 | 121.5546 | 121.5271 | 122.6624 | -1.8265 | -122.9919
3750.9219 | 122.6807 | -121.4355 | 1.1948 | 0.13382 | 0.00066656 | -0.010645 | 0.025263 | -0.00048499 | -0.0011471 | 0.010247 | -0.32501 | -0.086975 | -0.63171 | 0.35706 | 0.064087 | 0.10071 | 0.2655 | 0.27008 | 1.2131 | -121.788 | 120.8038 | -1.2817 | 121.1105 | 121.7926 | -1.1307 | -0.35248 | 0.018311 | 0.3067 | 121.701 | 121.7056 | 121.4996 | 121.3486 | 121.1105 | 122.6486 | 121.5363 | -0.35248 | 121.3486 | 121.1105 | 121.5363 | 121.4996 | 122.6486 | -1.8265 | -122.9828
3751.9062 | 122.699 | -121.3715 | 1.1948 | -0.12558 | 2.5564e-05 | -0.012567 | 0.026972 | -0.002194 | -0.00093346 | 0.0089657 | -0.2243 | -0.045776 | -0.60425 | 0.38452 | 0.10071 | 0.14191 | 0.28381 | 0.34332 | 1.2177 | -121.7926 | 120.7672 | -1.2405 | 121.1472 | 121.756 | -1.0941 | -0.42114 | 0.022888 | 0.37994 | 121.6553 | 121.7148 | 121.4722 | 121.3257 | 121.1472 | 122.5891 | 121.5134 | -0.42114 | 121.3257 | 121.1472 | 121.5134 | 121.4722 | 122.5891 | -1.799 | -122.9874
3752.9062 | 122.7081 | -121.4172 | 1.1856 | -0.13321 | 2.5564e-05 | -0.0078678 | 0.026331 | -0.0030484 | -7.9062e-05 | 0.010034 | -0.22888 | -0.041199 | -0.59967 | 0.39825 | 0.10986 | 0.15106 | 0.28381 | 0.3479 | 1.2131 | -121.7789 | 120.8176 | -1.2268 | 121.1884 | 121.8155 | -1.0757 | -0.36163 | 0.027466 | 0.37079 | 121.701 | 121.7651 | 121.5271 | 121.376 | 121.1884 | 122.6303 | 121.5683 | -0.36163 | 121.376 | 121.1884 | 121.5683 | 121.5271 | 122.6303 | -1.7853 | -122.9645
3753.9062 | 122.7219 | -121.431 | 1.2039 | -0.0035098 | -0.0023242 | -0.0070132 | 0.026545 | -0.0013394 | -0.0011471 | 0.0089657 | -0.2243 | -0.027466 | -0.58136 | 0.41199 | 0.086975 | 0.13733 | 0.28381 | 0.32959 | 1.2222 | -121.8063 | 120.8496 | -1.2314 | 121.2067 | 121.843 | -1.1169 | -0.37537 | 0.018311 | 0.35706 | 121.7148 | 121.7606 | 121.5179 | 121.4035 | 121.2067 | 122.6532 | 121.5683 | -0.37537 | 121.4035 | 121.2067 | 121.5683 | 121.5179 | 122.6532 | -1.7853 | -123.0103
3754.9062 | 122.699 | -121.4584 | 1.1902 | -0.079803 | -0.0027514 | -0.0050906 | 0.024836 | -0.00091219 | -0.00050626 | 0.0093931 | -0.23346 | -0.045776 | -0.56763 | 0.40741 | 0.11444 | 0.14191 | 0.28839 | 0.32501 | 1.2131 | -121.8246 | 120.8908 | -1.236 | 121.225 | 121.8658 | -1.0757 | -0.36621 | 0.022888 | 0.33417 | 121.7468 | 121.7834 | 121.5729 | 121.4127 | 121.225 | 122.6715 | 121.6003 | -0.36621 | 121.4127 | 121.225 | 121.6003 | 121.5729 | 122.6715 | -1.7578 | -123.0148
3755.9062 | 122.6715 | -121.4539 | 1.1627 | 0.1033 | -0.00061524 | -0.0050906 | 0.024622 | -0.00048499 | 0.0014163 | 0.010888 | -0.31128 | -0.059509 | -0.60883 | 0.35706 | 0.064087 | 0.10986 | 0.28839 | 0.26093 | 1.2177 | -121.8063 | 120.845 | -1.2222 | 121.1426 | 121.8109 | -1.0986 | -0.35248 | 0.054931 | 0.29755 | 121.7422 | 121.7148 | 121.5179 | 121.3943 | 121.1426 | 122.6715 | 121.5637 | -0.35248 | 121.3943 | 121.1426 | 121.5637 | 121.5179 | 122.6715 | -1.7715 | -122.9691
3756.9062 | 122.699 | -121.4401 | 1.1719 | -0.11032 | -0.0016834 | -0.0070132 | 0.026331 | -0.002194 | -0.0043515 | 0.0091795 | -0.2243 | -0.036621 | -0.60425 | 0.40283 | 0.11444 | 0.15564 | 0.29297 | 0.33875 | 1.2085 | -121.8201 | 120.8359 | -1.2085 | 121.2158 | 121.843 | -1.0574 | -0.37994 | 0.036621 | 0.37994 | 121.7331 | 121.7789 | 121.5546 | 121.4035 | 121.2158 | 122.6486 | 121.5958 | -0.37994 | 121.4035 | 121.2158 | 121.5958 | 121.5546 | 122.6486 | -1.7761 | -122.9919
3757.9062 | 122.6944 | -121.4584 | 1.1719 | 0.0041197 | -0.00061524 | -0.007654 | 0.028467 | -0.0013394 | -7.9062e-05 | 0.0074705 | -0.21515 | -0.050354 | -0.59509 | 0.40283 | 0.09613 | 0.1236 | 0.30212 | 0.32044 | 1.236 | -121.7972 | 120.8633 | -1.2222 | 121.2433 | 121.8613 | -1.0757 | -0.33875 | 0.064087 | 0.37994 | 121.7606 | 121.7789 | 121.5546 | 121.4081 | 121.2433 | 122.6944 | 121.582 | -0.33875 | 121.4081 | 121.2433 | 121.582 | 121.5546 | 122.6944 | -1.767 | -122.9691
3758.9062 | 122.6944 | -121.4264 | 1.1902 | -0.0035098 | 0.0010938 | -0.0095766 | 0.026758 | -0.00069859 | -0.0013609 | 0.0087521 | -0.21057 | -0.059509 | -0.58136 | 0.38452 | 0.09613 | 0.1236 | 0.29755 | 0.3067 | 1.2314 | -121.8018 | 120.845 | -1.2497 | 121.2158 | 121.8109 | -1.0941 | -0.37537 | 0.041198 | 0.37079 | 121.7239 | 121.7331 | 121.5225 | 121.3669 | 121.2158 | 122.6578 | 121.55 | -0.37537 | 121.3669 | 121.2158 | 121.55 | 121.5225 | 122.6578 | -1.7715 | -122.9919
3759.9062 | 122.699 | -121.431 | 1.1902 | -0.072174 | -0.0014696 | -0.010858 | 0.025477 | -0.0019802 | -0.0015745 | 0.0087521 | -0.22888 | -0.041199 | -0.58594 | 0.37079 | 0.09613 | 0.12817 | 0.31128 | 0.32501 | 1.2268 | -121.7789 | 120.845 | -1.2314 | 121.2021 | 121.8018 | -1.0941 | -0.3479 | 0.036621 | 0.35706 | 121.7422 | 121.756 | 121.5271 | 121.3898 | 121.2021 | 122.6578 | 121.5591 | -0.3479 | 121.3898 | 121.2021 | 121.5591 | 121.5271 | 122.6578 | -1.7761 | -122.9691
3760.9062 | 122.7676 | -121.4264 | 1.1856 | 0.21011 | -0.00082884 | -0.0067996 | 0.021204 | -0.001553 | -0.00050626 | 0.0089657 | -0.25177 | -0.082397 | -0.59052 | 0.41199 | 0.14191 | 0.20142 | 0.17853 | 0.36621 | 1.2085 | -121.756 | 120.8359 | -1.268 | 121.1746 | 121.8384 | -1.0437 | -0.32959 | 0.022888 | 0.33875 | 121.6049 | 121.7926 | 121.5683 | 121.344 | 121.1746 | 122.6349 | 121.6278 | -0.32959 | 121.344 | 121.1746 | 121.6278 | 121.5683 | 122.6349 | -1.7761 | -122.9416
3761.9062 | 122.6807 | -121.4584 | 1.2039 | -0.056915 | 0.0013074 | -0.0061588 | 0.026545 | -0.0019802 | 0.00013454 | 0.0087521 | -0.21515 | -0.041199 | -0.59967 | 0.37994 | 0.082397 | 0.12817 | 0.3067 | 0.30212 | 1.2497 | -121.843 | 120.8588 | -1.2451 | 121.2433 | 121.8384 | -1.1215 | -0.38452 | 0.045777 | 0.38452 | 121.7651 | 121.7606 | 121.5408 | 121.4172 | 121.2433 | 122.7081 | 121.5866 | -0.38452 | 121.4172 | 121.2433 | 121.5866 | 121.5408 | 122.7081 | -1.8036 | -123.0469
3762.9062 | 122.6944 | -121.4035 | 1.2772 | -0.095062 | -0.001897 | -0.012354 | 0.02569 | -0.0011258 | 0.0012027 | 0.010461 | -0.20599 | -0.018311 | -0.54932 | 0.41657 | 0.1831 | 0.18768 | 0.27924 | 0.3479 | 1.3 | -121.756 | 120.8542 | -1.2955 | 121.1975 | 121.8201 | -1.0941 | -0.35248 | 0.022888 | 0.34332 | 121.6827 | 121.7514 | 121.5866 | 121.3852 | 121.1975 | 122.7036 | 121.5912 | -0.35248 | 121.3852 | 121.1975 | 121.5912 | 121.5866 | 122.7036 | -1.8265 | -123.0331
3763.9062 | 122.6852 | -121.4493 | 1.1993 | 0.0041197 | 0.00066656 | -0.0061588 | 0.025904 | -0.002194 | -0.0020017 | 0.0091795 | -0.21515 | -0.013733 | -0.54474 | 0.36621 | 0.09613 | 0.10986 | 0.30212 | 0.28839 | 1.2177 | -121.8063 | 120.9045 | -1.2131 | 121.2341 | 121.8155 | -1.1032 | -0.35706 | 0.01831 | 0.32959 | 121.7514 | 121.7377 | 121.5454 | 121.4355 | 121.2341 | 122.6669 | 121.5591 | -0.35706 | 121.4355 | 121.2341 | 121.5591 | 121.5454 | 122.6669 | -1.7441 | -123.0057
3764.9062 | 122.6624 | -121.4584 | 1.1856 | 0.042267 | 0.00088016 | -0.0091494 | 0.024836 | -0.00069859 | -7.9062e-05 | 0.010675 | -0.27466 | -0.027466 | -0.59052 | 0.32501 | 0.054932 | 0.07782 | 0.34332 | 0.23346 | 1.2222 | -121.8201 | 120.8679 | -1.2131 | 121.1838 | 121.7834 | -1.1307 | -0.36163 | 0.036621 | 0.31586 | 121.8018 | 121.6919 | 121.5134 | 121.431 | 121.1838 | 122.6807 | 121.5363 | -0.36163 | 121.431 | 121.1838 | 121.5363 | 121.5134 | 122.6807 | -1.7761 | -123.0057
3765.9062 | 122.644 | -121.463 | 1.1719 | -1.331 | -0.00040164 | -0.0063724 | 0.026545 | -0.0013394 | -0.0015745 | 0.010461 | -0.32959 | -0.032043 | -0.59052 | 0.32501 | 0.050354 | 0.068665 | 0.31586 | 0.23804 | 1.2177 | -121.8384 | 120.8725 | -1.2039 | 121.1334 | 121.788 | -1.1215 | -0.37537 | 0.045776 | 0.26093 | 121.7789 | 121.7011 | 121.5134 | 121.431 | 121.1334 | 122.6807 | 121.5317 | -0.37537 | 121.431 | 121.1334 | 121.5317 | 121.5134 | 122.6807 | -1.7624 | -123.0103
3766.9062 | 122.6532 | -121.4722 | 1.181 | 0.065155 | 0.0017346 | -0.0053042 | 0.023981 | -0.0013394 | -0.00050626 | 0.0093931 | -0.27466 | -0.041199 | -0.59967 | 0.29755 | 0.045776 | 0.086975 | 0.33875 | 0.24719 | 1.2085 | -121.8613 | 120.8725 | -1.2222 | 121.1975 | 121.7697 | -1.1353 | -0.3891 | 0.027466 | 0.32501 | 121.8109 | 121.7194 | 121.5179 | 121.431 | 121.1975 | 122.6807 | 121.5591 | -0.3891 | 121.431 | 121.1975 | 121.5591 | 121.5179 | 122.6807 | -1.7807 | -123.0423
3767.9062 | 122.6624 | -121.5179 | 1.1673 | 0.065155 | -0.001256 | -0.0040226 | 0.024836 | -0.0026212 | 0.00098914 | 0.0096067 | -0.27466 | -0.032043 | -0.58594 | 0.32501 | 0.050354 | 0.064087 | 0.32501 | 0.22888 | 1.181 | -121.8887 | 120.932 | -1.1993 | 121.2433 | 121.843 | -1.1169 | -0.37079 | 0.013733 | 0.31128 | 121.843 | 121.7468 | 121.5683 | 121.4859 | 121.2433 | 122.699 | 121.582 | -0.37079 | 121.4859 | 121.2433 | 121.582 | 121.5683 | 122.699 | -1.7532 | -123.056
3768.9062 | 122.6395 | -121.5088 | 1.149 | 0.072784 | -0.0010424 | -0.0085086 | 0.026117 | 0.00036961 | -0.00050626 | 0.0083249 | -0.26093 | -0.013733 | -0.55847 | 0.31128 | 0.059509 | 0.09613 | 0.32501 | 0.25177 | 1.181 | -121.8658 | 120.9503 | -1.1627 | 121.2479 | 121.8201 | -1.0895 | -0.35706 | 0.032043 | 0.29755 | 121.8338 | 121.7606 | 121.5683 | 121.4951 | 121.2479 | 122.6898 | 121.6049 | -0.35706 | 121.4951 | 121.2479 | 121.6049 | 121.5683 | 122.6898 | -1.7075 | -123.0148
3769.9062 | 122.6807 | -121.4996 | 1.1536 | -0.018768 | 2.5564e-05 | -0.008295 | 0.027613 | 0.00036961 | -0.0015745 | 0.0089657 | -0.23346 | -0.041199 | -0.56305 | 0.36621 | 0.09613 | 0.13733 | 0.28839 | 0.28381 | 1.1856 | -121.8567 | 120.9366 | -1.1948 | 121.2662 | 121.8658 | -1.0574 | -0.35706 | 0.032044 | 0.32959 | 121.788 | 121.7834 | 121.5958 | 121.4584 | 121.2662 | 122.6852 | 121.637 | -0.35706 | 121.4584 | 121.2662 | 121.637 | 121.5958 | 122.6852 | -1.7166 | -123.0103
3770.9062 | 122.6486 | -121.4905 | 1.1581 | 0.14145 | 0.002162 | -0.0018862 | 0.024622 | 0.00015601 | -0.0022153 | 0.0096067 | -0.45319 | -0.036621 | -0.58136 | 0.37079 | 0.07782 | 0.064087 | 0.32044 | 0.24719 | 1.2039 | -121.8658 | 120.9091 | -1.1948 | 121.0373 | 121.8613 | -1.0803 | -0.37537 | 0.045776 | 0.12817 | 121.8109 | 121.7377 | 121.5683 | 121.4539 | 121.0373 | 122.6944 | 121.5546 | -0.37537 | 121.4539 | 121.0373 | 121.5546 | 121.5683 | 122.6944 | -1.7395 | -123.024
3771.9062 | 122.6715 | -121.5454 | 1.1353 | 0.14908 | -0.00082884 | -0.0061588 | 0.026545 | -0.0047574 | -0.0020017 | 0.011956 | -0.29297 | -0.022888 | -0.58136 | 0.28381 | -0.022888 | 0.10986 | 0.33875 | 0.18768 | 1.1902 | -121.8796 | 120.9641 | -1.1581 | 121.2524 | 121.8292 | -1.1581 | -0.33417 | 0.054932 | 0.28839 | 121.8842 | 121.7331 | 121.5225 | 121.5225 | 121.2524 | 122.7356 | 121.6553 | -0.33417 | 121.5225 | 121.2524 | 121.6553 | 121.5225 | 122.7356 | -1.7166 | -123.0148
3772.9219 | 122.731 | -121.4813 | 1.1215 | 0.21011 | -0.0014696 | -0.011286 | 0.01565 | -0.0036892 | 0.00098914 | 0.0098203 | -0.27466 | -0.10071 | -0.57678 | 0.37079 | 0.13275 | 0.1831 | 0.20142 | 0.33417 | 1.1673 | -121.8155 | 120.9045 | -1.2222 | 121.2067 | 121.8521 | -0.98877 | -0.33417 | 0.045776 | 0.30212 | 121.6827 | 121.8155 | 121.6141 | 121.3806 | 121.2067 | 122.6486 | 121.6644 | -0.33417 | 121.3806 | 121.2067 | 121.6644 | 121.6141 | 122.6486 | -1.6983 | -122.937
3773.9062 | 122.7402 | -121.5225 | 1.1536 | 0.1033 | -0.00040164 | -0.0085086 | 0.026758 | -0.0028348 | -0.0024289 | 0.0096067 | -0.28381 | -0.032043 | -0.59052 | 0.34332 | 0.054932 | 0.16479 | -0.041199 | 0.14648 | 1.1765 | -121.8521 | 120.932 | -1.1856 | 121.2387 | 121.8658 | -1.0986 | -0.32959 | 0.022889 | 0.3067 | 121.4813 | 121.669 | 121.5775 | 121.4905 | 121.2387 | 122.699 | 121.6873 | -0.32959 | 121.4905 | 121.2387 | 121.6873 | 121.5775 | 122.699 | -1.7441 | -123.0057
3774.9062 | 122.493 | -121.4951 | 1.1307 | 0.065155 | 2.5564e-05 | -0.0072268 | 0.025477 | -0.002194 | -0.0017881 | 0.010461 | -0.27924 | -0.036621 | -0.58136 | 0.31586 | 0.027466 | 0.064087 | 0.29297 | 0.24261 | 1.1856 | -121.8842 | 120.9137 | -1.1673 | 121.2158 | 121.8109 | -1.1032 | -0.3891 | 0.054932 | 0.30212 | 121.788 | 121.7377 | 121.5225 | 121.4584 | 121.2158 | 122.6807 | 121.5591 | -0.3891 | 121.4584 | 121.2158 | 121.5591 | 121.5225 | 122.6807 | -1.712 | -123.0148
3775.9219 | 122.7631 | -121.4401 | 1.149 | 0.12619 | -0.0027514 | -0.010004 | 0.019922 | -0.0041166 | -0.0022153 | 0.010888 | -0.27466 | -0.068665 | -0.54474 | 0.38452 | 0.12817 | 0.14648 | 0.20142 | 0.31586 | 1.1353 | -121.788 | 120.8954 | -1.2177 | 121.1655 | 121.8246 | -1.0208 | -0.3479 | -0.013733 | 0.27008 | 121.6415 | 121.756 | 121.5683 | 121.3715 | 121.1655 | 122.5754 | 121.5866 | -0.3479 | 121.3715 | 121.1655 | 121.5866 | 121.5683 | 122.5754 | -1.6937 | -122.937
3776.9062 | 122.6715 | -121.5408 | 1.1215 | 0.0041197 | -0.0021106 | -0.0074404 | 0.027186 | -0.0043302 | -0.00050626 | 0.011316 | -0.23346 | -0.027466 | -0.54932 | 0.35248 | 0.064087 | 0.10986 | 0.27924 | 0.2655 | 1.1719 | -121.9254 | 120.9915 | -1.149 | 121.3074 | 121.8933 | -1.0574 | -0.38452 | 0.050354 | 0.31586 | 121.8201 | 121.8063 | 121.6049 | 121.5134 | 121.3074 | 122.7127 | 121.6507 | -0.38452 | 121.5134 | 121.3074 | 121.6507 | 121.6049 | 122.7127 | -1.6708 | -123.0469
3777.9219 | 122.7768 | -121.4951 | 1.0941 | 0.042267 | -0.0033922 | -0.011499 | 0.017786 | -0.0045438 | -0.0020017 | 0.010675 | -0.2655 | -0.086975 | -0.55389 | 0.3891 | 0.15564 | 0.21515 | 0.1831 | 0.37537 | 1.1444 | -121.843 | 120.9412 | -1.181 | 121.2296 | 121.8842 | -0.93841 | -0.3479 | 0.050354 | 0.28839 | 121.6782 | 121.8704 | 121.6507 | 121.4081 | 121.2296 | 122.6395 | 121.7102 | -0.3479 | 121.4081 | 121.2296 | 121.7102 | 121.6507 | 122.6395 | -1.6479 | -122.937
3778.9062 | 122.6669 | -121.5317 | 1.0895 | 0.94254 | 0.00066656 | -0.0046634 | 0.027186 | -0.0036892 | -0.0024289 | 0.0085385 | -0.24719 | -0.032043 | -0.57678 | 0.32501 | 0.045776 | 0.10071 | 0.25177 | 0.23346 | 1.1398 | -121.9254 | 120.9549 | -1.1215 | 121.2845 | 121.8567 | -1.0437 | -0.39368 | 0.050354 | 0.32959 | 121.7834 | 121.7651 | 121.5775 | 121.4996 | 121.2845 | 122.6715 | 121.6324 | -0.39368 | 121.4996 | 121.2845 | 121.6324 | 121.5775 | 122.6715 | -1.6663 | -123.0148
3779.9062 | 122.6669 | -121.5408 | 1.0941 | 1.7741 | 0.00023916 | -0.012354 | 0.026331 | -0.0034756 | -0.00071986 | 0.0089657 | -0.10529 | -0.032043 | -0.5722 | 0.29755 | 0.054932 | 0.10986 | 0.26093 | 0.2243 | 1.1536 | -121.9345 | 120.9686 | -1.1261 | 121.4355 | 121.8384 | -1.0391 | -0.39368 | 0.059509 | 0.46692 | 121.8018 | 121.7651 | 121.5958 | 121.5088 | 121.4355 | 122.6944 | 121.6507 | -0.39368 | 121.5088 | 121.4355 | 121.6507 | 121.5958 | 122.6944 | -1.6663 | -123.0286
3780.9062 | 122.8043 | -121.4996 | 1.0574 | 0.55344 | -0.001256 | -0.008295 | 0.02334 | 0.00036961 | -0.0022153 | 0.0081113 | -0.22888 | -0.13733 | -0.58136 | 0.4303 | 0.17853 | 0.23804 | 0.10529 | 0.37079 | 1.0941 | -121.8384 | 120.9183 | -1.1948 | 121.2708 | 121.9299 | -0.87891 | -0.33875 | 0.036621 | 0.35248 | 121.6049 | 121.8704 | 121.6782 | 121.3623 | 121.2708 | 122.5937 | 121.7377 | -0.33875 | 121.3623 | 121.2708 | 121.7377 | 121.6782 | 122.5937 | -1.6388 | -122.8958
3781.9062 | 122.6761 | -121.5408 | 1.1169 | 0.14145 | 0.00088016 | -0.0070132 | 0.027826 | -0.001553 | 0.00098914 | 0.010034 | -0.29755 | -0.022888 | -0.58594 | 0.29755 | 0.21515 | 0.24719 | 0.20142 | 0.17395 | 1.1673 | -121.9116 | 120.9549 | -1.1398 | 121.2433 | 121.8384 | -0.90179 | -0.37079 | 0.050354 | 0.28839 | 121.7422 | 121.7148 | 121.756 | 121.5179 | 121.2433 | 122.7081 | 121.788 | -0.37079 | 121.5179 | 121.2433 | 121.788 | 121.756 | 122.7081 | -1.7029 | -123.0286
3782.9219 | 122.7905 | -121.5134 | 1.1124 | -0.064545 | -0.0023242 | -0.011286 | 0.016932 | -0.0053982 | -0.0013609 | 0.011529 | -0.26093 | -0.082397 | -0.54474 | 0.43945 | 0.16937 | 0.21515 | 0.19684 | 0.39825 | 1.1215 | -121.8338 | 120.9686 | -1.1948 | 121.2524 | 121.9528 | -0.94299 | -0.32043 | 0.009155 | 0.28381 | 121.7102 | 121.9116 | 121.6827 | 121.431 | 121.2524 | 122.6349 | 121.7285 | -0.32043 | 121.431 | 121.2524 | 121.7285 | 121.6827 | 122.6349 | -1.6571 | -122.9462
3783.9062 | 122.6715 | -121.5454 | 1.1032 | 0.034637 | -0.00018804 | -0.007654 | 0.028895 | -0.0026212 | -0.0013609 | 0.0089657 | -0.21973 | -0.050354 | -0.5722 | 0.3479 | 0.059509 | 0.09613 | 0.2655 | 0.24261 | 1.1398 | -121.9345 | 120.9732 | -1.1536 | 121.3257 | 121.8933 | -1.0437 | -0.3891 | 0.036622 | 0.35248 | 121.8109 | 121.788 | 121.6049 | 121.4951 | 121.3257 | 122.6852 | 121.6415 | -0.3891 | 121.4951 | 121.3257 | 121.6415 | 121.6049 | 122.6852 | -1.6754 | -123.0377
3784.9062 | 122.6578 | -121.5683 | 1.1215 | 0.14908 | 0.001521 | -0.0059452 | 0.028895 | -0.00069859 | -0.0015745 | 0.0083249 | -0.28381 | -0.041199 | -0.59052 | 0.36163 | 0.059509 | 0.086975 | 0.3067 | 0.21057 | 1.1536 | -121.8979 | 120.9778 | -1.1627 | 121.2845 | 121.9299 | -1.062 | -0.32959 | 0.032043 | 0.3067 | 121.875 | 121.7789 | 121.6278 | 121.5271 | 121.2845 | 122.7219 | 121.6553 | -0.32959 | 121.5271 | 121.2845 | 121.6553 | 121.6278 | 122.7219 | -1.712 | -123.0194
3785.9062 | 122.6715 | -121.55 | 1.1169 | 0.45425 | -0.001897 | -0.0089358 | 0.027399 | -0.0043302 | -0.0024289 | 0.0089657 | -0.28381 | -0.013733 | -0.56763 | 0.3479 | 0.064087 | 0.091553 | 0.27924 | 0.24719 | 1.1581 | -121.9162 | 120.9824 | -1.1307 | 121.2662 | 121.8979 | -1.0529 | -0.36621 | 0.041199 | 0.28381 | 121.8292 | 121.7972 | 121.6141 | 121.5363 | 121.2662 | 122.7081 | 121.6415 | -0.36621 | 121.5363 | 121.2662 | 121.6415 | 121.6141 | 122.7081 | -1.6846 | -123.0331
3786.9062 | 122.6715 | -121.5363 | 1.1124 | 0.81284 | 0.0010938 | -0.0070132 | 0.024195 | -0.001553 | -0.0020017 | 0.0081113 | -0.23804 | -0.027466 | -0.58594 | 0.34332 | 0.064087 | 0.10071 | 0.27008 | 0.23346 | 1.149 | -121.9162 | 120.9503 | -1.1398 | 121.2982 | 121.8796 | -1.0483 | -0.37994 | 0.036621 | 0.3479 | 121.8063 | 121.7697 | 121.6003 | 121.5088 | 121.2982 | 122.6852 | 121.637 | -0.37994 | 121.5088 | 121.2982 | 121.637 | 121.6003 | 122.6852 | -1.6983 | -123.0286
3787.9062 | 122.6761 | -121.5683 | 1.1169 | 0.75943 | -0.0014696 | -0.011713 | 0.022486 | -0.00069859 | -0.00029266 | 0.0096067 | -0.082397 | -0.036621 | -0.58136 | 0.35248 | 0.091553 | 0.11444 | 0.27008 | 0.23804 | 1.1398 | -121.9299 | 120.9869 | -1.1536 | 121.4859 | 121.9208 | -1.0254 | -0.36163 | 0.022889 | 0.49896 | 121.8384 | 121.8063 | 121.6599 | 121.5317 | 121.4859 | 122.7081 | 121.6827 | -0.36163 | 121.5317 | 121.4859 | 121.6827 | 121.6599 | 122.7081 | -1.6983 | -123.0469
3788.9062 | 122.6807 | -121.5866 | 1.1261 | 0.1033 | -0.00018804 | -0.011286 | 0.02334 | -0.0011258 | -0.0011471 | 0.010461 | -0.27466 | -0.022888 | -0.58136 | 0.30212 | 0.07782 | 0.14191 | 0.27008 | 0.20599 | 1.1398 | -121.9208 | 121.0052 | -1.149 | 121.312 | 121.8887 | -1.0483 | -0.33417 | 0.013733 | 0.3067 | 121.8567 | 121.7926 | 121.6644 | 121.5637 | 121.312 | 122.7264 | 121.7285 | -0.33417 | 121.5637 | 121.312 | 121.7285 | 121.6644 | 122.7264 | -1.7075 | -123.0469
3789.9062 | 122.6761 | -121.5637 | 1.1169 | 0.15671 | 0.00066656 | -0.0097904 | 0.026117 | -0.0017666 | 0.0012027 | 0.011956 | -0.29297 | -0.032043 | -0.58136 | 0.34332 | 0.25177 | 0.25635 | 0.18768 | 0.21057 | 1.1536 | -121.8979 | 120.9824 | -1.149 | 121.2708 | 121.907 | -0.86517 | -0.33417 | 0.036621 | 0.28839 | 121.7514 | 121.7743 | 121.8155 | 121.5317 | 121.2708 | 122.7173 | 121.8201 | -0.33417 | 121.5317 | 121.2708 | 121.8201 | 121.8155 | 122.7173 | -1.6983 | -123.0148
3790.9062 | 122.7859 | -121.5225 | 1.0666 | 0.027008 | -0.0025378 | -0.012354 | 0.016291 | -0.0028348 | -0.0017881 | 0.0089657 | -0.26093 | -0.07782 | -0.54016 | 0.42572 | 0.17395 | 0.22888 | 0.20142 | 0.3891 | 1.1124 | -121.8567 | 120.9824 | -1.1444 | 121.2616 | 121.9482 | -0.89264 | -0.33417 | 0.045777 | 0.27924 | 121.7239 | 121.9116 | 121.6965 | 121.4447 | 121.2616 | 122.6349 | 121.7514 | -0.33417 | 121.4447 | 121.2616 | 121.7514 | 121.6965 | 122.6349 | -1.6067 | -122.9233
3791.9062 | 122.7905 | -121.5637 | 1.1169 | 0.088043 | -0.00018804 | -0.0042362 | 0.026972 | -0.0045438 | -0.00050626 | 0.0098203 | -0.27924 | -0.036621 | -0.57678 | 0.32959 | 0.045776 | 0.082397 | 0.28839 | -0.027466 | 1.1169 | -121.8979 | 120.9869 | -1.1536 | 121.2845 | 121.8933 | -1.0712 | -0.33417 | 0 | 0.29755 | 121.8521 | 121.5363 | 121.6095 | 121.5271 | 121.2845 | 122.6807 | 121.6461 | -0.33417 | 121.5271 | 121.2845 | 121.6461 | 121.6095 | 122.6807 | -1.6937 | -123.0148
3792.9062 | 122.699 | -121.582 | 1.0757 | 0.24063 | 0.0010938 | -0.007654 | 0.025477 | -0.0030484 | 0.00013454 | 0.010247 | -0.27924 | -0.009155 | -0.56763 | 0.36621 | 0.064087 | 0.11444 | 0.27466 | 0.24719 | 1.1261 | -121.9299 | 121.0144 | -1.0849 | 121.3028 | 121.9482 | -1.0117 | -0.3479 | 0.050354 | 0.28839 | 121.8567 | 121.8292 | 121.6461 | 121.5729 | 121.3028 | 122.7081 | 121.6965 | -0.3479 | 121.5729 | 121.3028 | 121.6965 | 121.6461 | 122.7081 | -1.6434 | -123.0057
3793.9062 | 122.6944 | -121.5683 | 1.1078 | 0.11093 | -0.001897 | -0.0053042 | 0.026545 | -0.001553 | -0.0011471 | 0.010034 | -0.28381 | -0.041199 | -0.59509 | 0.36163 | 0.068665 | 0.10529 | 0.27008 | 0.24719 | 1.1627 | -121.9391 | 120.9732 | -1.149 | 121.2845 | 121.9299 | -1.0391 | -0.37079 | 0.054932 | 0.31128 | 121.8384 | 121.8155 | 121.637 | 121.5271 | 121.2845 | 122.731 | 121.6736 | -0.37079 | 121.5271 | 121.2845 | 121.6736 | 121.637 | 122.731 | -1.7029 | -123.0469
3794.9062 | 122.6944 | -121.5637 | 1.1032 | 0.088043 | -0.00018804 | -0.0072268 | 0.025049 | -0.0017666 | -0.0013609 | 0.0076841 | -0.28381 | -0.022888 | -0.57678 | 0.37537 | 0.07782 | 0.11444 | 0.27924 | 0.23804 | 1.1398 | -121.9208 | 120.9869 | -1.1261 | 121.2799 | 121.9391 | -1.0254 | -0.35706 | 0.036622 | 0.29297 | 121.843 | 121.8018 | 121.6415 | 121.5408 | 121.2799 | 122.7036 | 121.6782 | -0.35706 | 121.5408 | 121.2799 | 121.6782 | 121.6415 | 122.7036 | -1.68 | -123.024
3795.9062 | 122.7814 | -121.5408 | 1.03 | 0.16434 | -0.0014696 | -0.0078678 | 0.024195 | -0.001553 | -0.0022153 | 0.011956 | -0.19684 | -0.082397 | -0.5722 | 0.47607 | 0.032043 | 0.050354 | 0.15106 | 0.54016 | 1.062 | -121.907 | 120.9686 | -1.1124 | 121.344 | 122.0169 | -0.99792 | -0.36621 | 0.032044 | 0.37537 | 121.6919 | 122.081 | 121.5729 | 121.4584 | 121.344 | 122.6028 | 121.5912 | -0.36621 | 121.4584 | 121.344 | 121.5912 | 121.5729 | 122.6028 | -1.6022 | -122.937
3796.9062 | 122.6944 | -121.5729 | 1.0986 | 0.14145 | -0.0023242 | -0.0067996 | 0.023981 | -0.0017666 | -0.00071986 | 0.010034 | -0.27924 | -0.027466 | -0.57678 | 0.35706 | 0.073242 | 0.11444 | 0.27924 | 0.24719 | 1.1261 | -121.9254 | 120.9961 | -1.1261 | 121.2936 | 121.9299 | -1.0254 | -0.35248 | 0.027466 | 0.29755 | 121.8521 | 121.8201 | 121.6461 | 121.5454 | 121.2936 | 122.699 | 121.6873 | -0.35248 | 121.5454 | 121.2936 | 121.6873 | 121.6461 | 122.699 | -1.6754 | -123.024
3797.9062 | 122.699 | -121.5591 | 1.0895 | 0.21774 | 0.0013074 | -0.011927 | 0.02569 | -0.0024076 | -0.0037107 | 0.0078977 | -0.27466 | -0.022888 | -0.58136 | 0.36163 | 0.086975 | 0.11902 | 0.27008 | 0.24719 | 1.1444 | -121.9345 | 120.9778 | -1.1124 | 121.2845 | 121.9208 | -1.0025 | -0.37537 | 0.054931 | 0.3067 | 121.8292 | 121.8063 | 121.6461 | 121.5363 | 121.2845 | 122.7036 | 121.6782 | -0.37537 | 121.5363 | 121.2845 | 121.6782 | 121.6461 | 122.7036 | -1.6708 | -123.024
3798.9062 | 122.6898 | -121.5591 | 1.0574 | 0.27115 | -0.0016834 | -0.0091494 | 0.02334 | -0.0019802 | 0.00077554 | 0.010461 | -0.27924 | -0.013733 | -0.55847 | 0.3479 | 0.082397 | 0.11444 | 0.27008 | 0.25177 | 1.1215 | -121.8887 | 121.0007 | -1.0712 | 121.2799 | 121.907 | -0.97504 | -0.32959 | 0.064087 | 0.27924 | 121.8292 | 121.8109 | 121.6415 | 121.5454 | 121.2799 | 122.6807 | 121.6736 | -0.32959 | 121.5454 | 121.2799 | 121.6736 | 121.6415 | 122.6807 | -1.6159 | -122.9462
3799.9062 | 122.7768 | -121.5088 | 1.0803 | 0.24826 | 2.5564e-05 | -0.0040226 | 0.024408 | -0.00091219 | 0.00056194 | 0.0098203 | -0.24719 | -0.059509 | -0.5722 | 0.40283 | 0.15564 | 0.20142 | 0.17395 | 0.33875 | 1.1169 | -121.8796 | 120.9366 | -1.1398 | 121.2616 | 121.9116 | -0.92468 | -0.37079 | 0.036621 | 0.32501 | 121.6827 | 121.8475 | 121.6644 | 121.4493 | 121.2616 | 122.6257 | 121.7102 | -0.37079 | 121.4493 | 121.2616 | 121.7102 | 121.6644 | 122.6257 | -1.6525 | -122.9599
3800.9062 | 122.7768 | -121.5042 | 1.1169 | 0.21774 | -0.003606 | -0.013208 | 0.014795 | -0.0043302 | -0.0024289 | 0.0089657 | -0.29297 | -0.10986 | -0.58136 | 0.38452 | 0.15106 | 0.1831 | 0.20599 | 0.35248 | 1.1398 | -121.8521 | 120.9229 | -1.2268 | 121.2112 | 121.8887 | -0.96588 | -0.3479 | 0.022889 | 0.28839 | 121.7102 | 121.8567 | 121.6553 | 121.3943 | 121.2112 | 122.644 | 121.6873 | -0.3479 | 121.3943 | 121.2112 | 121.6873 | 121.6553 | 122.644 | -1.6983 | -122.9691
3801.9062 | 122.8088 | -121.4767 | 1.0986 | 0.26352 | -0.00061524 | -0.0067996 | 0.024836 | -0.003903 | -0.0017881 | 0.010247 | -0.24261 | -0.07782 | -0.57678 | 0.44861 | 0.15564 | 0.21973 | 0.16937 | 0.37537 | 1.1169 | -121.8613 | 120.9 | -1.1765 | 121.2341 | 121.9254 | -0.94299 | -0.38452 | 0.01831 | 0.33417 | 121.6461 | 121.8521 | 121.6324 | 121.3989 | 121.2341 | 122.5937 | 121.6965 | -0.38452 | 121.3989 | 121.2341 | 121.6965 | 121.6324 | 122.5937 | -1.6754 | -122.9599
3802.9062 | 122.8043 | -121.4584 | 1.1124 | 0.19485 | -0.00018804 | -0.0016726 | 0.024622 | -0.0036892 | -0.00071986 | 0.0087521 | -0.21973 | -0.091553 | -0.58594 | 0.44403 | 0.17853 | 0.21973 | 0.13733 | 0.36621 | 1.1353 | -121.8384 | 120.8725 | -1.2039 | 121.2387 | 121.9025 | -0.93384 | -0.37994 | 0.022888 | 0.36621 | 121.5958 | 121.8246 | 121.637 | 121.3669 | 121.2387 | 122.5937 | 121.6782 | -0.37994 | 121.3669 | 121.2387 | 121.6782 | 121.637 | 122.5937 | -1.6983 | -122.9507
3803.9062 | 122.7951 | -121.4813 | 1.1307 | 0.16434 | 0.00066656 | -0.0085086 | 0.024195 | -0.0034756 | -0.0015745 | 0.010034 | -0.20142 | -0.07782 | -0.56305 | 0.45776 | 0.17853 | 0.24261 | 0.13733 | 0.37079 | 1.1215 | -121.8338 | 120.9183 | -1.2085 | 121.2799 | 121.9391 | -0.95215 | -0.35248 | -0.009155 | 0.36163 | 121.6187 | 121.8521 | 121.6599 | 121.4035 | 121.2799 | 122.6028 | 121.7239 | -0.35248 | 121.4035 | 121.2799 | 121.7239 | 121.6599 | 122.6028 | -1.6937 | -122.9645
3804.9062 | 122.7997 | -121.4813 | 1.0941 | 0.42374 | -0.0014696 | -0.0074404 | 0.026331 | -0.002194 | -0.00050626 | 0.010888 | -0.23804 | -0.091553 | -0.58136 | 0.4715 | 0.16022 | 0.2243 | 0.13275 | 0.37994 | 1.1444 | -121.843 | 120.9 | -1.1856 | 121.2433 | 121.9528 | -0.93384 | -0.36163 | 0.050354 | 0.34332 | 121.6141 | 121.8613 | 121.6415 | 121.3898 | 121.2433 | 122.6257 | 121.7056 | -0.36163 | 121.3898 | 121.2433 | 121.7056 | 121.6415 | 122.6257 | -1.6754 | -122.937
3805.9062 | 122.7722 | -121.4813 | 1.1124 | 0.0041197 | -0.002965 | -0.011072 | 0.018641 | -0.0068936 | 0.00098914 | 0.010247 | -0.27008 | -0.07782 | -0.54474 | 0.43945 | 0.17853 | 0.20599 | 0.19684 | 0.36621 | 1.1444 | -121.8246 | 120.9366 | -1.1902 | 121.2112 | 121.9208 | -0.93384 | -0.34332 | 0.032043 | 0.27466 | 121.6782 | 121.8475 | 121.6599 | 121.4035 | 121.2112 | 122.6257 | 121.6873 | -0.34332 | 121.4035 | 121.2112 | 121.6873 | 121.6599 | 122.6257 | -1.6571 | -122.937
3806.9062 | 122.7997 | -121.4951 | 1.1032 | 0.17197 | -0.0040332 | -0.0080814 | 0.024408 | -0.004971 | -0.0015745 | 0.0096067 | -0.21973 | -0.09613 | -0.56305 | 0.47607 | 0.1831 | 0.23804 | 0.14648 | 0.3891 | 1.1169 | -121.8658 | 120.932 | -1.1993 | 121.2753 | 121.9711 | -0.92011 | -0.37079 | 0.013733 | 0.34332 | 121.6415 | 121.8842 | 121.6782 | 121.3989 | 121.2753 | 122.612 | 121.7331 | -0.37079 | 121.3989 | 121.2753 | 121.7331 | 121.6782 | 122.612 | -1.6663 | -122.9691
3807.9062 | 122.7814 | -121.4813 | 1.0986 | 0.21011 | -0.0021106 | -0.0063724 | 0.024195 | -0.0051846 | -0.0011471 | 0.0089657 | -0.22888 | -0.10529 | -0.55389 | 0.46234 | 0.16937 | 0.24261 | 0.13733 | 0.38452 | 1.1398 | -121.8567 | 120.9274 | -1.2039 | 121.2524 | 121.9437 | -0.92926 | -0.37537 | 0.041199 | 0.32501 | 121.6187 | 121.8658 | 121.6507 | 121.376 | 121.2524 | 122.6212 | 121.7239 | -0.37537 | 121.376 | 121.2524 | 121.7239 | 121.6507 | 122.6212 | -1.6525 | -122.9553
3808.9062 | 122.7768 | -121.4905 | 1.0895 | 0.17197 | -0.0023242 | -0.0080814 | 0.024408 | -0.0045438 | -0.00050626 | 0.0081113 | -0.21973 | -0.11444 | -0.55389 | 0.47607 | 0.16937 | 0.23346 | 0.13733 | 0.37537 | 1.1261 | -121.8292 | 120.9366 | -1.2039 | 121.2708 | 121.9666 | -0.9201 | -0.33875 | 0.036621 | 0.33417 | 121.6278 | 121.8658 | 121.6599 | 121.376 | 121.2708 | 122.6166 | 121.7239 | -0.33875 | 121.376 | 121.2708 | 121.7239 | 121.6599 | 122.6166 | -1.6434 | -122.9187
3809.9062 | 122.7814 | -121.4951 | 1.0986 | 0.16434 | -0.0033922 | -0.0057314 | 0.024622 | -0.0062528 | -0.00050626 | 0.0089657 | -0.23346 | -0.091553 | -0.55847 | 0.46234 | 0.17853 | 0.23804 | 0.13275 | 0.36163 | 1.1215 | -121.8384 | 120.9366 | -1.1902 | 121.2616 | 121.9574 | -0.9201 | -0.34332 | 0.022888 | 0.32501 | 121.6278 | 121.8567 | 121.6736 | 121.4035 | 121.2616 | 122.6166 | 121.7331 | -0.34332 | 121.4035 | 121.2616 | 121.7331 | 121.6736 | 122.6166 | -1.6571 | -122.937
3810.9062 | 122.7859 | -121.4996 | 1.1032 | 0.15671 | -0.004674 | -0.0072268 | 0.023981 | -0.0073208 | 0.00013454 | 0.0093931 | -0.23804 | -0.10529 | -0.54932 | 0.45776 | 0.18768 | 0.2243 | 0.14648 | 0.37994 | 1.1078 | -121.8521 | 120.9503 | -1.2085 | 121.2616 | 121.9574 | -0.91553 | -0.35248 | 0.004578 | 0.31128 | 121.6461 | 121.8796 | 121.6873 | 121.3943 | 121.2616 | 122.6074 | 121.7239 | -0.35248 | 121.3943 | 121.2616 | 121.7239 | 121.6873 | 122.6074 | -1.6525 | -122.9553
3811.9062 | 122.7722 | -121.4951 | 1.0895 | 0.1796 | -0.0010424 | -0.010645 | 0.023127 | -0.0064664 | -0.0022153 | 0.0089657 | -0.23346 | -0.11444 | -0.55847 | 0.46692 | 0.17853 | 0.23804 | 0.14191 | 0.37079 | 1.1169 | -121.8109 | 120.9366 | -1.2039 | 121.2616 | 121.962 | -0.91095 | -0.31586 | 0.027465 | 0.32501 | 121.637 | 121.8658 | 121.6736 | 121.3806 | 121.2616 | 122.612 | 121.7331 | -0.31586 | 121.3806 | 121.2616 | 121.7331 | 121.6736 | 122.612 | -1.6479 | -122.9004
3812.9062 | 122.7859 | -121.582 | 1.0941 | 0.17197 | -0.0031786 | -0.012354 | 0.021631 | -0.0056118 | -0.0017881 | 0.0087521 | -0.27466 | -0.086975 | -0.55847 | 0.43945 | 0.13733 | 0.18768 | 0.20599 | 0.35248 | 1.1353 | -121.8475 | 121.0236 | -1.181 | 121.3074 | 122.0215 | -0.95673 | -0.2655 | 0.041199 | 0.28381 | 121.788 | 121.9345 | 121.7194 | 121.4951 | 121.3074 | 122.7173 | 121.7697 | -0.2655 | 121.4951 | 121.3074 | 121.7697 | 121.7194 | 122.7173 | -1.6525 | -122.9416
3813.9062 | 122.7814 | -121.4905 | 1.1124 | 0.019379 | -0.003606 | -0.015558 | 0.020991 | -0.0081754 | -0.0011471 | 0.0093931 | -0.27466 | -0.086975 | -0.56305 | 0.45319 | 0.18768 | 0.19684 | 0.19684 | 0.37537 | 1.1353 | -121.8201 | 120.9274 | -1.1993 | 121.2158 | 121.9437 | -0.92468 | -0.32959 | 0.022888 | 0.28839 | 121.6873 | 121.8658 | 121.6782 | 121.4035 | 121.2158 | 122.6257 | 121.6873 | -0.32959 | 121.4035 | 121.2158 | 121.6873 | 121.6782 | 122.6257 | -1.6754 | -122.9324
3814.9062 | 122.7905 | -121.5225 | 1.0757 | 0.065155 | -0.0042468 | -0.0097904 | 0.02334 | -0.008389 | -0.0022153 | 0.0064023 | -0.26093 | -0.091553 | -0.54932 | 0.40741 | 0.054932 | 0.13733 | 0.22888 | 0.31586 | 1.0757 | -121.8658 | 120.9732 | -1.1673 | 121.2616 | 121.9299 | -1.0208 | -0.34332 | 0 | 0.28839 | 121.7514 | 121.8384 | 121.5775 | 121.431 | 121.2616 | 122.5983 | 121.6599 | -0.34332 | 121.431 | 121.2616 | 121.6599 | 121.5775 | 122.5983 | -1.6251 | -122.9416
3815.9062 | 122.8271 | -121.4859 | 1.1169 | -0.079803 | -0.004674 | -0.0074404 | 0.022059 | -0.0071072 | -0.0022153 | 0.0078977 | -0.1831 | -0.054932 | -0.50354 | 0.50812 | 0.21057 | 0.25635 | 0.16022 | 0.4303 | 1.1353 | -121.8338 | 120.9824 | -1.1719 | 121.3028 | 121.994 | -0.90637 | -0.3479 | 0.018311 | 0.32044 | 121.6461 | 121.9162 | 121.6965 | 121.431 | 121.3028 | 122.6212 | 121.7422 | -0.3479 | 121.431 | 121.3028 | 121.7422 | 121.6965 | 122.6212 | -1.6205 | -122.9507
3816.9062 | 122.7676 | -121.5134 | 1.1215 | 0.68314 | -0.0027514 | -0.014063 | 0.020136 | -0.0081754 | -0.0013609 | 0.0081113 | -0.3067 | -0.068665 | -0.53558 | 0.44403 | 0.16022 | 0.1831 | 0.21057 | 0.35706 | 1.1261 | -121.8338 | 120.9778 | -1.1902 | 121.2067 | 121.9574 | -0.9613 | -0.32043 | 0.004578 | 0.22888 | 121.7239 | 121.8704 | 121.6736 | 121.4447 | 121.2067 | 122.6395 | 121.6965 | -0.32043 | 121.4447 | 121.2067 | 121.6965 | 121.6736 | 122.6395 | -1.6571 | -122.9553
3817.9062 | 122.7631 | -121.5408 | 1.1032 | 0.14145 | -0.0025378 | -0.011499 | 0.020991 | -0.0062528 | -0.0013609 | 0.011316 | -0.23346 | -0.07782 | -0.50354 | 0.45776 | 0.16022 | 0.19684 | 0.18768 | 0.33875 | 1.1261 | -121.8109 | 121.0373 | -1.181 | 121.3074 | 121.9986 | -0.94299 | -0.27008 | 0.022889 | 0.27008 | 121.7285 | 121.8796 | 121.7011 | 121.463 | 121.3074 | 122.6669 | 121.7377 | -0.27008 | 121.463 | 121.3074 | 121.7377 | 121.7011 | 122.6669 | -1.6067 | -122.9141
3818.9062 | 122.7768 | -121.4905 | 1.1261 | 0.11093 | -0.0033922 | -0.010645 | 0.02035 | -0.0081754 | -0.00071986 | 0.010461 | -0.2655 | -0.073242 | -0.55389 | 0.45319 | 0.16479 | 0.1831 | 0.19684 | 0.35248 | 1.1215 | -121.8567 | 120.9366 | -1.1993 | 121.225 | 121.9437 | -0.9613 | -0.36621 | -0.004578 | 0.28839 | 121.6873 | 121.843 | 121.6553 | 121.4172 | 121.225 | 122.612 | 121.6736 | -0.36621 | 121.4172 | 121.225 | 121.6736 | 121.6553 | 122.612 | -1.68 | -122.9828
3819.9062 | 122.8088 | -121.5042 | 1.1353 | -0.034027 | -0.0042468 | -0.0072268 | 0.019922 | -0.00668 | -0.00029266 | 0.0059751 | -0.21515 | -0.059509 | -0.53101 | 0.49896 | 0.21057 | 0.23804 | 0.1831 | 0.39825 | 1.149 | -121.8292 | 120.9732 | -1.1948 | 121.2891 | 122.0032 | -0.92468 | -0.32501 | 0.013733 | 0.31586 | 121.6873 | 121.9025 | 121.7148 | 121.4447 | 121.2891 | 122.6532 | 121.7422 | -0.32501 | 121.4447 | 121.2891 | 121.7422 | 121.7148 | 122.6532 | -1.6663 | -122.9645
3820.9219 | 122.7127 | -121.5363 | 1.1536 | -0.19424 | -0.0021106 | -0.0097904 | 0.027826 | -0.0071072 | -0.0026425 | 0.0089657 | -0.26093 | -0.032043 | -0.56763 | 0.42114 | 0.10071 | 0.10986 | 0.33875 | 0.28839 | 1.1673 | -121.8613 | 120.9686 | -1.1856 | 121.2753 | 121.9574 | -1.0529 | -0.32501 | 0.013733 | 0.3067 | 121.875 | 121.8246 | 121.637 | 121.5042 | 121.2753 | 122.7036 | 121.6461 | -0.32501 | 121.5042 | 121.2753 | 121.6461 | 121.637 | 122.7036 | -1.7212 | -123.0148
3821.9062 | 122.818 | -121.4996 | 1.1307 | -0.018768 | -0.0042468 | -0.015131 | 0.017359 | -0.0058256 | 0.00013454 | 0.012384 | -0.25635 | -0.068665 | -0.53558 | 0.49896 | 0.21515 | 0.24719 | 0.19684 | 0.41657 | 1.1581 | -121.7834 | 120.9641 | -1.1993 | 121.2433 | 121.9986 | -0.91553 | -0.28381 | 0.027466 | 0.27924 | 121.6965 | 121.9162 | 121.7148 | 121.431 | 121.2433 | 122.6578 | 121.7468 | -0.28381 | 121.431 | 121.2433 | 121.7468 | 121.7148 | 122.6578 | -1.6663 | -122.9141
3822.9062 | 122.818 | -121.5042 | 1.1124 | -0.018768 | -0.0040332 | -0.011286 | 0.021418 | -0.0088162 | 0.00098914 | 0.0074705 | -0.23346 | -0.073242 | -0.54474 | 0.49439 | 0.2243 | 0.24719 | 0.1831 | 0.40741 | 1.1353 | -121.8109 | 120.9595 | -1.1856 | 121.2708 | 121.9986 | -0.88806 | -0.3067 | 0.022888 | 0.31128 | 121.6873 | 121.9116 | 121.7285 | 121.431 | 121.2708 | 122.6395 | 121.7514 | -0.3067 | 121.431 | 121.2708 | 121.7514 | 121.7285 | 122.6395 | -1.6571 | -122.9233
3823.9062 | 122.8226 | -121.4813 | 1.1215 | -0.049286 | -0.0055286 | -0.016626 | 0.018213 | -0.004971 | 0.00056194 | 0.010461 | -0.23346 | -0.059509 | -0.54474 | 0.51727 | 0.21515 | 0.24719 | 0.17853 | 0.41657 | 1.1444 | -121.7651 | 120.9366 | -1.181 | 121.2479 | 121.9986 | -0.90637 | -0.28381 | 0.022888 | 0.31128 | 121.6599 | 121.8979 | 121.6965 | 121.4218 | 121.2479 | 122.6257 | 121.7285 | -0.28381 | 121.4218 | 121.2479 | 121.7285 | 121.6965 | 122.6257 | -1.6663 | -122.8867
3824.9062 | 122.7722 | -121.5179 | 1.1215 | -0.018768 | -0.0040332 | -0.0097904 | 0.020777 | -0.0081754 | -0.0026425 | 0.0098203 | -0.27008 | -0.07782 | -0.55847 | 0.44861 | 0.16479 | 0.18768 | 0.20142 | 0.35248 | 1.1398 | -121.8201 | 120.9595 | -1.1993 | 121.2479 | 121.9666 | -0.95673 | -0.30212 | 0.018311 | 0.28839 | 121.7194 | 121.8704 | 121.6827 | 121.4401 | 121.2479 | 122.6578 | 121.7056 | -0.30212 | 121.4401 | 121.2479 | 121.7056 | 121.6827 | 122.6578 | -1.68 | -122.9416
3825.9062 | 122.699 | -121.5637 | 1.1536 | -0.20187 | -0.0016834 | -0.0091494 | 0.02334 | -0.0096708 | 0.00013454 | 0.0081113 | -0.27466 | -0.027466 | -0.55847 | 0.31128 | 0.054932 | 0.14191 | 0.37537 | 0.24719 | 1.1948 | -121.875 | 121.0052 | -1.181 | 121.2891 | 121.875 | -1.0986 | -0.31128 | 0.041199 | 0.28381 | 121.9391 | 121.8109 | 121.6187 | 121.5363 | 121.2891 | 122.7585 | 121.7056 | -0.31128 | 121.5363 | 121.2891 | 121.7056 | 121.6187 | 122.7585 | -1.712 | -123.0286
3826.9062 | 122.8088 | -121.4996 | 1.0895 | -0.13321 | -0.0051012 | -0.011072 | 0.020563 | -0.0077482 | -0.00093346 | 0.010675 | -0.19226 | -0.07782 | -0.53558 | 0.51727 | 0.23346 | 0.027466 | 0.48981 | 0.39825 | 1.1215 | -121.8246 | 120.9641 | -1.1673 | 121.3074 | 122.0169 | -0.85602 | -0.32501 | 0.032043 | 0.34332 | 121.9894 | 121.8979 | 121.7331 | 121.4218 | 121.3074 | 122.6212 | 121.5271 | -0.32501 | 121.4218 | 121.3074 | 121.5271 | 121.7331 | 122.6212 | -1.6251 | -122.9141
3827.9062 | 122.7951 | -121.4996 | 1.0849 | -0.1561 | -0.0025378 | -0.011713 | 0.022272 | -0.0088162 | -0.0011471 | 0.012811 | -0.16937 | -0.07782 | -0.52643 | 0.5722 | 0.36621 | 0.33875 | -0.1236 | 0.43488 | 1.1353 | -121.8063 | 120.9732 | -1.1627 | 121.3303 | 122.0718 | -0.71869 | -0.3067 | 0.050354 | 0.35706 | 121.376 | 121.9345 | 121.8658 | 121.4218 | 121.3303 | 122.6349 | 121.8384 | -0.3067 | 121.4218 | 121.3303 | 121.8384 | 121.8658 | 122.6349 | -1.6113 | -122.8912
3828.9062 | 122.8546 | -121.5134 | 1.0849 | -0.14847 | -0.0051012 | -0.01449 | 0.019495 | -0.00668 | -0.0026425 | 0.0083249 | -0.16937 | -0.064087 | -0.53101 | 0.50354 | 0.041199 | 0.09613 | 0.28839 | 0.45319 | 1.0941 | -121.7972 | 120.9824 | -1.149 | 121.344 | 122.0169 | -1.0437 | -0.28381 | 0.009155 | 0.36163 | 121.8018 | 121.9666 | 121.5546 | 121.4493 | 121.344 | 122.6074 | 121.6095 | -0.28381 | 121.4493 | 121.344 | 121.6095 | 121.5546 | 122.6074 | -1.6159 | -122.8821
3829.9062 | 122.8363 | -121.5134 | 1.0849 | -0.14847 | -0.0044604 | -0.013849 | 0.016932 | -0.0062528 | 0.0020571 | 0.010675 | -0.17853 | -0.086975 | -0.53101 | 0.39825 | 0.26093 | 0.31586 | 0.064087 | 0.41657 | 1.0849 | -121.8338 | 120.9824 | -1.1719 | 121.3348 | 121.9116 | -0.82397 | -0.32043 | 0 | 0.35248 | 121.5775 | 121.9299 | 121.7743 | 121.4264 | 121.3348 | 122.5983 | 121.8292 | -0.32043 | 121.4264 | 121.3348 | 121.8292 | 121.7743 | 122.5983 | -1.6159 | -122.9187
3830.9062 | 122.7219 | -121.5683 | 1.1307 | -0.17899 | -0.0016834 | -0.012567 | 0.026117 | -0.0053982 | -0.00050626 | 0.0081113 | -0.24719 | -0.009155 | -0.55389 | 0.40283 | 0.1236 | 0.12817 | 0.33417 | 0.31128 | 1.1581 | -121.8842 | 121.0144 | -1.1398 | 121.3211 | 121.9711 | -1.0071 | -0.31586 | 0.027466 | 0.3067 | 121.9025 | 121.8796 | 121.6919 | 121.5591 | 121.3211 | 122.7264 | 121.6965 | -0.31586 | 121.5591 | 121.3211 | 121.6965 | 121.6919 | 122.7264 | -1.6846 | -123.0148
3831.9062 | 122.85 | -121.5408 | 1.1032 | -0.064545 | -0.0027514 | -0.0095766 | 0.018641 | -0.0068936 | -0.00071986 | 0.0083249 | -0.20599 | -0.064087 | -0.52185 | 0.49896 | 0.21973 | 0.2655 | 0.19226 | 0.44403 | 1.1169 | -121.8155 | 121.019 | -1.1673 | 121.3348 | 122.0398 | -0.88348 | -0.27466 | 0.013733 | 0.31586 | 121.7331 | 121.9849 | 121.7606 | 121.4767 | 121.3348 | 122.6578 | 121.8063 | -0.27466 | 121.4767 | 121.3348 | 121.8063 | 121.7606 | 122.6578 | -1.6251 | -122.9187
3832.9062 | 122.8134 | -121.4996 | 1.0941 | 1.1943 | -0.003606 | -0.01214 | 0.021204 | -0.0088162 | 0.00056194 | 0.0087521 | -0.1236 | -0.07782 | -0.54016 | 0.49896 | 0.23804 | 0.26093 | 0.19684 | 0.42114 | 1.1215 | -121.8246 | 120.9595 | -1.1719 | 121.376 | 121.9986 | -0.85602 | -0.32501 | 0.027466 | 0.41657 | 121.6965 | 121.9208 | 121.7377 | 121.4218 | 121.376 | 122.6212 | 121.7606 | -0.32501 | 121.4218 | 121.376 | 121.7606 | 121.7377 | 122.6212 | -1.6342 | -122.9187
3833.9062 | 122.7585 | -121.5179 | 1.1307 | -0.23239 | -0.0038196 | -0.013208 | 0.023127 | -0.0071072 | -0.0028561 | 0.010461 | -0.20599 | -0.045776 | -0.51727 | 0.46234 | 0.19684 | 0.18768 | 0.27466 | 0.37537 | 1.1215 | -121.843 | 121.0007 | -1.1765 | 121.3119 | 121.9803 | -0.93384 | -0.32501 | -0.009155 | 0.31128 | 121.7926 | 121.8933 | 121.7148 | 121.4722 | 121.3119 | 122.6395 | 121.7056 | -0.32501 | 121.4722 | 121.3119 | 121.7056 | 121.7148 | 122.6395 | -1.6479 | -122.9736
3834.9062 | 122.7402 | -121.55 | 1.1169 | -0.21713 | -0.004674 | -0.013422 | 0.023127 | -0.0056118 | -0.0015745 | 0.0089657 | -0.23346 | -0.073242 | -0.54932 | 0.45319 | 0.17853 | 0.17853 | 0.3067 | 0.38452 | 1.1215 | -121.8338 | 121.0007 | -1.1902 | 121.3165 | 122.0032 | -0.93841 | -0.28381 | 0.004578 | 0.31586 | 121.8567 | 121.9345 | 121.7285 | 121.4767 | 121.3165 | 122.6715 | 121.7285 | -0.28381 | 121.4767 | 121.3165 | 121.7285 | 121.7285 | 122.6715 | -1.6663 | -122.9507
3835.9062 | 122.7448 | -121.5271 | 1.1215 | -0.27054 | -0.0025378 | -0.0095766 | 0.023981 | -0.0045438 | -0.00050626 | 0.0064023 | -0.2243 | -0.068665 | -0.54932 | 0.41657 | 0.15564 | 0.16479 | 0.31128 | 0.36163 | 1.1673 | -121.8338 | 120.9778 | -1.1902 | 121.3028 | 121.9437 | -0.96588 | -0.3067 | 0.045776 | 0.32501 | 121.8384 | 121.8887 | 121.6827 | 121.4584 | 121.3028 | 122.6944 | 121.6919 | -0.3067 | 121.4584 | 121.3028 | 121.6919 | 121.6827 | 122.6944 | -1.6708 | -122.9553
3836.9062 | 122.7219 | -121.5637 | 1.1307 | -0.24765 | -0.0033922 | -0.01214 | 0.025049 | -0.0092434 | 0.00056194 | 0.0068295 | -0.21973 | -0.054932 | -0.53558 | 0.41199 | 0.13733 | 0.16022 | 0.32501 | 0.34332 | 1.1673 | -121.843 | 121.0281 | -1.1856 | 121.344 | 121.9757 | -0.99335 | -0.27924 | 0.036621 | 0.31586 | 121.8887 | 121.907 | 121.701 | 121.5088 | 121.344 | 122.731 | 121.7239 | -0.27924 | 121.5088 | 121.344 | 121.7239 | 121.701 | 122.731 | -1.6663 | -122.9736
3837.9062 | 122.7127 | -121.5866 | 1.1261 | -0.24002 | -0.0048876 | -0.012995 | 0.022059 | -0.0060392 | -0.0013609 | 0.0083249 | -0.23346 | -0.027466 | -0.53558 | 0.38452 | 0.1236 | 0.13733 | 0.35248 | 0.31586 | 1.1444 | -121.8567 | 121.051 | -1.1536 | 121.3531 | 121.9711 | -1.0025 | -0.27008 | 0.01831 | 0.30212 | 121.9391 | 121.9025 | 121.7102 | 121.5591 | 121.3531 | 122.731 | 121.7239 | -0.27008 | 121.5591 | 121.3531 | 121.7239 | 121.7102 | 122.731 | -1.6617 | -122.9828
3838.9062 | 122.7859 | -121.5363 | 1.0941 | -0.17899 | -0.004674 | -0.0080814 | 0.023127 | -0.0079618 | -0.0013609 | 0.0096067 | -0.19684 | -0.068665 | -0.51727 | 0.47607 | 0.20142 | 0.21973 | 0.26093 | 0.41657 | 1.1078 | -121.8246 | 121.019 | -1.1627 | 121.3394 | 122.0123 | -0.89264 | -0.28839 | 0.013733 | 0.32043 | 121.7972 | 121.9528 | 121.7377 | 121.4676 | 121.3394 | 122.644 | 121.756 | -0.28839 | 121.4676 | 121.3394 | 121.756 | 121.7377 | 122.644 | -1.6113 | -122.9187
3839.9062 | 122.699 | -121.5866 | 1.1353 | -0.23239 | 0.0013074 | -0.013208 | 0.023768 | -0.0062528 | -0.0022153 | 0.0078977 | -0.23804 | -0.022888 | -0.53101 | 0.36621 | 0.10986 | 0.12817 | 0.36621 | 0.29755 | 1.1444 | -121.9116 | 121.0556 | -1.1581 | 121.3486 | 121.9528 | -1.0254 | -0.32501 | 0.009155 | 0.29297 | 121.9528 | 121.8842 | 121.6965 | 121.5637 | 121.3486 | 122.731 | 121.7148 | -0.32501 | 121.5637 | 121.3486 | 121.7148 | 121.6965 | 122.731 | -1.6663 | -123.0469
3840.9062 | 122.7173 | -121.5683 | 1.1032 | -0.018768 | -0.001256 | -0.008295 | 0.029963 | -0.004971 | -0.0030697 | 0.0081113 | -0.21057 | -0.027466 | -0.55847 | 0.40741 | 0.11444 | 0.14191 | 0.29297 | 0.31128 | 1.1307 | -121.8887 | 121.0098 | -1.1307 | 121.3577 | 121.9757 | -0.98877 | -0.32044 | 0.027466 | 0.3479 | 121.8613 | 121.8796 | 121.6827 | 121.5408 | 121.3577 | 122.699 | 121.7102 | -0.32044 | 121.5408 | 121.3577 | 121.7102 | 121.6827 | 122.699 | -1.6617 | -122.9919
3841.9062 | 122.7173 | -121.582 | 1.1124 | -0.2095 | 0.00045296 | -0.010431 | 0.02569 | -0.0024076 | 0.00077554 | 0.0091795 | -0.27008 | 0.009155 | -0.55389 | 0.38452 | 0.10529 | 0.11444 | 0.37079 | 0.29755 | 1.1353 | -121.9116 | 121.0281 | -1.1032 | 121.3119 | 121.9666 | -1.0071 | -0.32959 | 0.022888 | 0.28381 | 121.9528 | 121.8796 | 121.6873 | 121.5912 | 121.3119 | 122.7173 | 121.6965 | -0.32959 | 121.5912 | 121.3119 | 121.6965 | 121.6873 | 122.7173 | -1.6663 | -123.024
3842.9062 | 122.7036 | -121.582 | 1.1261 | -0.19424 | -0.001897 | -0.0087222 | 0.026758 | -0.0019802 | -0.0020017 | 0.0076841 | -0.24261 | 0.004578 | -0.54474 | 0.37994 | 0.11444 | 0.1236 | 0.35706 | 0.29755 | 1.149 | -121.8887 | 121.0373 | -1.1215 | 121.3394 | 121.962 | -1.0117 | -0.3067 | 0.022888 | 0.30212 | 121.9391 | 121.8796 | 121.6965 | 121.5866 | 121.3394 | 122.731 | 121.7056 | -0.3067 | 121.5866 | 121.3394 | 121.7056 | 121.6965 | 122.731 | -1.6708 | -123.0148
3843.9062 | 122.731 | -121.5042 | 1.1948 | -0.17899 | -0.001897 | -0.0089358 | 0.026117 | -0.0028348 | -0.0030697 | 0.010034 | -0.25177 | 0.009155 | -0.53558 | 0.45776 | 0.16022 | 0.17853 | 0.40741 | 0.32044 | 1.1993 | -121.8384 | 120.9686 | -1.1856 | 121.2524 | 121.962 | -1.0345 | -0.33417 | 0.004578 | 0.28381 | 121.9116 | 121.8246 | 121.6644 | 121.5134 | 121.2524 | 122.7036 | 121.6827 | -0.33417 | 121.5134 | 121.2524 | 121.6827 | 121.6644 | 122.7036 | -1.7303 | -123.0331
3844.9062 | 122.7356 | -121.4493 | 1.2314 | -0.14847 | -0.0016834 | -0.0089358 | 0.025049 | -0.0030484 | -0.0024289 | 0.0083249 | -0.2655 | 0.004578 | -0.55389 | 0.44403 | 0.14648 | 0.18768 | 0.37079 | 0.31128 | 1.2634 | -121.7606 | 120.8954 | -1.2268 | 121.1838 | 121.8933 | -1.0849 | -0.31128 | 0.032044 | 0.28839 | 121.8201 | 121.7606 | 121.5958 | 121.4539 | 121.1838 | 122.7127 | 121.637 | -0.31128 | 121.4539 | 121.1838 | 121.637 | 121.5958 | 122.7127 | -1.7853 | -122.9919
3845.9062 | 122.8134 | -121.4218 | 1.1856 | 0.24826 | -0.00082884 | -0.0074404 | 0.025049 | -0.0028348 | -0.0024289 | 0.0096067 | -0.19226 | -0.041199 | -0.52185 | 0.52643 | 0.24261 | 0.3067 | 0.16479 | 0.37994 | 1.2131 | -121.756 | 120.9 | -1.2268 | 121.2296 | 121.9482 | -0.94299 | -0.33417 | 0.027466 | 0.32959 | 121.5866 | 121.8018 | 121.6644 | 121.3806 | 121.2296 | 122.6349 | 121.7285 | -0.33417 | 121.3806 | 121.2296 | 121.7285 | 121.6644 | 122.6349 | -1.7075 | -122.9416
3846.9062 | 122.7036 | -121.4905 | 1.2039 | -0.16373 | 0.00023916 | -0.0074404 | 0.025904 | -0.0041166 | -0.0041379 | 0.0096067 | -0.23346 | 0.027466 | -0.54016 | 0.45319 | 0.17853 | 0.19226 | 0.35706 | 0.31128 | 1.2405 | -121.8201 | 120.9503 | -1.1765 | 121.257 | 121.9437 | -1.0254 | -0.32959 | 0.036622 | 0.3067 | 121.8475 | 121.8018 | 121.669 | 121.5179 | 121.257 | 122.731 | 121.6827 | -0.32959 | 121.5179 | 121.257 | 121.6827 | 121.669 | 122.731 | -1.7441 | -123.024
3847.9062 | 122.7448 | -121.4767 | 1.1902 | -0.16373 | -0.0023242 | -0.0067996 | 0.025904 | -0.0047574 | -0.0024289 | 0.010034 | -0.17853 | 0.022888 | -0.52643 | 0.48981 | 0.18768 | 0.22888 | 0.31586 | 0.3479 | 1.2314 | -121.8155 | 120.9503 | -1.1673 | 121.2982 | 121.9666 | -1.0025 | -0.33874 | 0.041198 | 0.3479 | 121.7926 | 121.8246 | 121.6644 | 121.4996 | 121.2982 | 122.7081 | 121.7056 | -0.33874 | 121.4996 | 121.2982 | 121.7056 | 121.6644 | 122.7081 | -1.7166 | -123.0057
3848.9062 | 122.7127 | -121.4996 | 1.1765 | 0.042267 | -0.00082884 | -0.004877 | 0.025049 | -0.0026212 | -0.0020017 | 0.0074705 | -0.20142 | 0.004578 | -0.53101 | 0.43488 | 0.14191 | 0.18768 | 0.32501 | 0.29297 | 1.2131 | -121.8338 | 120.9686 | -1.1719 | 121.2982 | 121.9345 | -1.0345 | -0.33417 | 0.036621 | 0.32959 | 121.8246 | 121.7926 | 121.6415 | 121.5042 | 121.2982 | 122.7127 | 121.6873 | -0.33417 | 121.5042 | 121.2982 | 121.6873 | 121.6415 | 122.7127 | -1.7075 | -123.0103
3849.9062 | 122.7448 | -121.4859 | 1.2177 | -0.17136 | 0.00088016 | -0.0046634 | 0.024836 | 0.0014376 | -0.0026425 | 0.0085385 | -0.18768 | 0.022888 | -0.51727 | 0.47607 | 0.18768 | 0.21057 | 0.34332 | 0.34332 | 1.2177 | -121.8109 | 120.9686 | -1.1948 | 121.2982 | 121.962 | -1.03 | -0.32501 | 0 | 0.32959 | 121.8292 | 121.8292 | 121.6736 | 121.5088 | 121.2982 | 122.7036 | 121.6965 | -0.32501 | 121.5088 | 121.2982 | 121.6965 | 121.6736 | 122.7036 | -1.7349 | -123.0286
3850.9062 | 122.7356 | -121.5042 | 1.1902 | -0.041657 | -0.0010424 | -0.0053042 | 0.02569 | 0.0010104 | -0.00071986 | 0.0087521 | -0.20599 | -0.022888 | -0.53558 | 0.46234 | 0.17395 | 0.21057 | 0.33417 | 0.32044 | 1.2222 | -121.843 | 120.9686 | -1.2131 | 121.2982 | 121.9666 | -1.0162 | -0.33875 | 0.032043 | 0.32959 | 121.8384 | 121.8246 | 121.6782 | 121.4813 | 121.2982 | 122.7264 | 121.7148 | -0.33875 | 121.4813 | 121.2982 | 121.7148 | 121.6782 | 122.7264 | -1.7258 | -123.0331
3851.9062 | 122.6761 | -121.4035 | 1.2314 | -0.018768 | -0.001256 | -0.0089358 | 0.026758 | -0.0028348 | -0.0032835 | 0.0087521 | -0.21057 | -0.009155 | -0.53101 | 0.47607 | 0.16937 | 0.2243 | 0.32959 | 0.36621 | 1.1993 | -121.788 | 120.8725 | -1.2405 | 121.1929 | 121.8796 | -1.062 | -0.38452 | -0.032043 | 0.32043 | 121.7331 | 121.7697 | 121.5729 | 121.3943 | 121.1929 | 122.6028 | 121.6278 | -0.38452 | 121.3943 | 121.1929 | 121.6278 | 121.5729 | 122.6028 | -1.7624 | -123.0194
3852.9062 | 122.7402 | -121.5134 | 1.1719 | -0.11032 | -0.0023242 | -0.010431 | 0.02569 | -0.00027139 | 0.00098914 | 0.0083249 | -0.23804 | 0.004578 | -0.54932 | 0.44403 | 0.17395 | 0.20142 | 0.35248 | 0.33875 | 1.2039 | -121.875 | 120.9641 | -1.1673 | 121.2753 | 121.9574 | -0.99792 | -0.36163 | 0.032043 | 0.31128 | 121.8658 | 121.8521 | 121.6873 | 121.5179 | 121.2753 | 122.7173 | 121.7148 | -0.36163 | 121.5179 | 121.2753 | 121.7148 | 121.6873 | 122.7173 | -1.7212 | -123.0469
3853.9219 | 122.8409 | -121.4584 | 1.1444 | -0.17899 | -0.001897 | -0.0074404 | 0.020563 | -0.002194 | -0.0022153 | 0.0087521 | -0.21057 | -0.09613 | -0.55847 | 0.5127 | 0.24261 | 0.29755 | 0.1831 | 0.4303 | 1.1765 | -121.7834 | 120.9 | -1.2405 | 121.2479 | 121.9711 | -0.90179 | -0.32501 | 0.032044 | 0.3479 | 121.6415 | 121.8887 | 121.701 | 121.3623 | 121.2479 | 122.6349 | 121.756 | -0.32501 | 121.3623 | 121.2479 | 121.756 | 121.701 | 122.6349 | -1.7029 | -122.9279
3854.9062 | 122.7402 | -121.5179 | 1.1719 | -0.026398 | 0.00045296 | -0.0078678 | 0.02569 | -0.0036892 | -0.0020017 | 0.0085385 | -0.18768 | 0 | -0.53558 | 0.45319 | 0.15564 | 0.20599 | 0.3479 | 0.31128 | 1.2085 | -121.8384 | 120.9824 | -1.1719 | 121.3303 | 121.9711 | -1.0162 | -0.32044 | 0.036621 | 0.3479 | 121.8658 | 121.8292 | 121.6736 | 121.5179 | 121.3303 | 122.7264 | 121.7239 | -0.32044 | 121.5179 | 121.3303 | 121.7239 | 121.6736 | 122.7264 | -1.7075 | -123.0103
3855.9062 | 122.7356 | -121.4996 | 1.1719 | -0.018768 | -0.0031786 | -0.0059452 | 0.026972 | -0.002194 | -0.0011471 | 0.0089657 | -0.20142 | -0.041199 | -0.54016 | 0.45319 | 0.16022 | 0.19684 | 0.33875 | 0.30212 | 1.2177 | -121.8613 | 120.9595 | -1.2131 | 121.2982 | 121.9528 | -1.0117 | -0.36163 | 0.045776 | 0.33874 | 121.8384 | 121.8018 | 121.6599 | 121.4584 | 121.2982 | 122.7173 | 121.6965 | -0.36163 | 121.4584 | 121.2982 | 121.6965 | 121.6599 | 122.7173 | -1.712 | -123.0331
3856.9062 | 122.7264 | -121.5088 | 1.1765 | 0.065155 | -0.00040164 | -0.008295 | 0.027186 | 0.00079681 | -0.0022153 | 0.010247 | -0.21515 | -0.013733 | -0.54474 | 0.45319 | 0.16022 | 0.19684 | 0.34332 | 0.29755 | 1.2268 | -121.8796 | 120.964 | -1.1902 | 121.2936 | 121.962 | -1.0162 | -0.37079 | 0.050354 | 0.32959 | 121.8521 | 121.8063 | 121.669 | 121.4951 | 121.2936 | 122.7356 | 121.7056 | -0.37079 | 121.4951 | 121.2936 | 121.7056 | 121.669 | 122.7356 | -1.7212 | -123.056
3857.9062 | 122.7264 | -121.5225 | 1.1673 | 0.011749 | 0.00088016 | -0.0063724 | 0.025049 | -0.001553 | 0.00077554 | 0.0087521 | -0.24719 | -0.022888 | -0.54474 | 0.43945 | 0.15106 | 0.1831 | 0.34332 | 0.29297 | 1.2131 | -121.8567 | 120.9778 | -1.1902 | 121.2753 | 121.962 | -1.0162 | -0.33417 | 0.045777 | 0.29755 | 121.8658 | 121.8155 | 121.6736 | 121.4996 | 121.2753 | 122.7356 | 121.7056 | -0.33417 | 121.4996 | 121.2753 | 121.7056 | 121.6736 | 122.7356 | -1.712 | -123.024
3858.9219 | 122.8271 | -121.4813 | 1.1673 | 0.034637 | -0.002965 | -0.008295 | 0.0133 | -0.002194 | -0.00093346 | 0.011743 | -0.25177 | -0.045776 | -0.54016 | 0.5127 | 0.24719 | 0.29297 | 0.25177 | 0.4303 | 1.1948 | -121.788 | 120.9412 | -1.2131 | 121.2296 | 121.994 | -0.92011 | -0.3067 | 0.027466 | 0.28839 | 121.7331 | 121.9116 | 121.7285 | 121.4355 | 121.2296 | 122.6761 | 121.7743 | -0.3067 | 121.4355 | 121.2296 | 121.7743 | 121.7285 | 122.6761 | -1.7075 | -122.9553
3859.9062 | 122.7493 | -121.4905 | 1.1719 | -0.064545 | -0.00082884 | -0.0055178 | 0.02804 | -0.0030484 | -0.0026425 | 0.0085385 | -0.19226 | 0.009155 | -0.50812 | 0.49439 | 0.17853 | 0.21515 | 0.31128 | 0.36621 | 1.2039 | -121.875 | 120.9824 | -1.1627 | 121.2982 | 121.9849 | -0.99335 | -0.38452 | 0.032043 | 0.31586 | 121.8018 | 121.8567 | 121.669 | 121.4996 | 121.2982 | 122.6944 | 121.7056 | -0.38452 | 121.4996 | 121.2982 | 121.7056 | 121.669 | 122.6944 | -1.68 | -123.0469
3860.9219 | 122.818 | -121.4905 | 1.1627 | 0.1796 | -0.003606 | -0.0091494 | 0.019709 | -0.002194 | -0.00093346 | 0.010888 | -0.20599 | -0.07782 | -0.53558 | 0.51727 | 0.24719 | 0.32959 | 0.19684 | 0.45776 | 1.1902 | -121.7972 | 120.9549 | -1.2405 | 121.2845 | 122.0078 | -0.91553 | -0.3067 | 0.027466 | 0.32959 | 121.6873 | 121.9482 | 121.7377 | 121.4127 | 121.2845 | 122.6807 | 121.8201 | -0.3067 | 121.4127 | 121.2845 | 121.8201 | 121.7377 | 122.6807 | -1.6983 | -122.9599
3861.9062 | 122.6624 | -121.5179 | 1.1993 | 0.14908 | 0.0010938 | -0.0063724 | 0.02804 | -0.0024076 | 0.0014163 | 0.0093931 | -0.25177 | -0.009155 | -0.56763 | 0.4303 | 0.30212 | 0.09613 | 0.44403 | 0.63171 | 1.2177 | -121.8887 | 120.9503 | -1.2085 | 121.2662 | 121.9482 | -0.89722 | -0.37079 | 0.01831 | 0.31586 | 121.962 | 122.1497 | 121.8201 | 121.5088 | 121.2662 | 122.7356 | 121.6141 | -0.37079 | 121.5088 | 121.2662 | 121.6141 | 121.8201 | 122.7356 | -1.767 | -123.0881
3862.9062 | 122.7219 | -121.5179 | 1.1993 | 0.095673 | -0.0010424 | -0.0057314 | 0.027826 | -0.0043302 | -0.00093346 | 0.0089657 | -0.25177 | 0.018311 | -0.55389 | 0.49896 | -0.064087 | 0.004578 | 0.71411 | 0.45319 | 1.2222 | -121.8475 | 120.9641 | -1.181 | 121.2662 | 122.0169 | -1.2634 | -0.32959 | 0.022888 | 0.30212 | 122.2321 | 121.9711 | 121.4539 | 121.5363 | 121.2662 | 122.7402 | 121.5225 | -0.32959 | 121.5363 | 121.2662 | 121.5225 | 121.4539 | 122.7402 | -1.7532 | -123.0469
3863.9062 | 122.818 | -121.4813 | 1.1673 | 0.18723 | -0.0031786 | -0.0097904 | 0.020777 | -0.0024076 | -0.0017881 | 0.010461 | -0.19226 | -0.068665 | -0.51727 | 0.52643 | 0.24719 | 0.29755 | 0.20142 | 0.46234 | 1.1765 | -121.8018 | 120.9641 | -1.236 | 121.2891 | 122.0078 | -0.92011 | -0.32044 | 0.009156 | 0.32501 | 121.6827 | 121.9437 | 121.7285 | 121.4127 | 121.2891 | 122.6578 | 121.7789 | -0.32044 | 121.4127 | 121.2891 | 121.7789 | 121.7285 | 122.6578 | -1.6846 | -122.9691
3864.9062 | 122.6715 | -121.4951 | 1.2131 | 0.11856 | 2.5564e-05 | -0.0078678 | 0.027613 | -0.001553 | -0.00071986 | 0.011316 | -0.27466 | -0.027466 | -0.59509 | 0.42572 | 0.28839 | 0.17853 | 0.22888 | 0.66376 | 1.236 | -121.8567 | 120.9 | -1.2405 | 121.2204 | 121.9208 | -0.92468 | -0.36163 | 0.022888 | 0.32043 | 121.7239 | 122.1588 | 121.7834 | 121.4676 | 121.2204 | 122.731 | 121.6736 | -0.36163 | 121.4676 | 121.2204 | 121.6736 | 121.7834 | 122.731 | -1.8082 | -123.0698
3865.9062 | 122.7997 | -121.463 | 1.181 | 0.233 | -0.00018804 | -0.0057314 | 0.025263 | -0.00069859 | -0.00071986 | 0.011743 | -0.25635 | -0.045776 | -0.55847 | 0.48981 | 0.20142 | 0.25177 | 0.23804 | 0.39825 | 1.2177 | -121.8246 | 120.9045 | -1.2268 | 121.2067 | 121.9528 | -0.97961 | -0.36163 | 0.036621 | 0.30212 | 121.7011 | 121.8613 | 121.6644 | 121.4172 | 121.2067 | 122.6807 | 121.7148 | -0.36163 | 121.4172 | 121.2067 | 121.7148 | 121.6644 | 122.6807 | -1.7395 | -123.0057
3866.9062 | 122.7264 | -121.4905 | 1.1902 | 0.072784 | 2.5564e-05 | -0.0038088 | 0.028254 | -0.0024076 | -0.0020017 | 0.0098203 | -0.23804 | -0.027466 | -0.55847 | 0.45776 | 0.14648 | 0.1831 | 0.33875 | 0.33875 | 1.236 | -121.8796 | 120.932 | -1.2177 | 121.2524 | 121.9482 | -1.0437 | -0.3891 | 0.045776 | 0.32043 | 121.8292 | 121.8292 | 121.637 | 121.463 | 121.2524 | 122.7264 | 121.6736 | -0.3891 | 121.463 | 121.2524 | 121.6736 | 121.637 | 122.7264 | -1.7487 | -123.0698
3867.9062 | 122.6852 | -121.4951 | 1.2131 | 0.21011 | 0.00045296 | -0.006586 | 0.026117 | -0.0013394 | -0.0022153 | 0.0089657 | -0.27924 | -0.027466 | -0.56763 | 0.41199 | 0.12817 | 0.16479 | 0.37994 | 0.30212 | 1.2314 | -121.8613 | 120.9274 | -1.2405 | 121.2158 | 121.907 | -1.0849 | -0.36621 | 0.01831 | 0.28839 | 121.875 | 121.7972 | 121.6232 | 121.4676 | 121.2158 | 122.7264 | 121.6599 | -0.36621 | 121.4676 | 121.2158 | 121.6599 | 121.6232 | 122.7264 | -1.7807 | -123.0743
3868.9062 | 122.8134 | -121.4859 | 1.1856 | -0.21713 | -0.0014696 | -0.007654 | 0.018854 | -0.0041166 | -0.00071986 | 0.0096067 | -0.15564 | -0.059509 | -0.52185 | 0.54932 | 0.29755 | 0.31128 | 0.27466 | 0.48981 | 1.1993 | -121.8246 | 120.9641 | -1.2451 | 121.3303 | 122.0352 | -0.88806 | -0.33875 | 0.013733 | 0.36621 | 121.7606 | 121.9757 | 121.7834 | 121.4264 | 121.3303 | 122.6852 | 121.7972 | -0.33875 | 121.4264 | 121.3303 | 121.7972 | 121.7834 | 122.6852 | -1.7075 | -123.0103
3869.9062 | 122.7127 | -121.5042 | 1.2085 | 0.47714 | 2.5564e-05 | -0.0078678 | 0.026331 | -0.0030484 | -7.9062e-05 | 0.010461 | -0.27008 | -0.004578 | -0.56305 | 0.44403 | 0.14191 | 0.17853 | 0.3479 | 0.30212 | 1.2543 | -121.8475 | 120.9412 | -1.2131 | 121.2341 | 121.9482 | -1.0666 | -0.34332 | 0.045776 | 0.29297 | 121.8521 | 121.8063 | 121.6461 | 121.4996 | 121.2341 | 122.7585 | 121.6827 | -0.34332 | 121.4996 | 121.2341 | 121.6827 | 121.6461 | 122.7585 | -1.7715 | -123.056
3870.9219 | 122.8043 | -121.4355 | 1.1856 | 0.011749 | -0.003606 | -0.0080814 | 0.018427 | -0.0043302 | -0.0017881 | 0.0093931 | -0.22888 | -0.032043 | -0.50354 | 0.49896 | 0.22888 | 0.27008 | 0.27924 | 0.43488 | 1.2222 | -121.788 | 120.932 | -1.2177 | 121.2067 | 121.9345 | -0.95673 | -0.35248 | 0.036621 | 0.27466 | 121.7148 | 121.8704 | 121.6644 | 121.4035 | 121.2067 | 122.6578 | 121.7056 | -0.35248 | 121.4035 | 121.2067 | 121.7056 | 121.6644 | 122.6578 | -1.6891 | -122.9736
3871.9062 | 122.699 | -121.4859 | 1.1993 | 0.14145 | 2.5564e-05 | -0.007654 | 0.027399 | -0.0041166 | 0.0012027 | 0.0085385 | -0.23346 | 0.009155 | -0.54016 | 0.4303 | 0.15564 | 0.18768 | 0.37079 | 0.32501 | 1.236 | -121.8567 | 120.9457 | -1.1902 | 121.2524 | 121.9162 | -1.0437 | -0.37079 | 0.036621 | 0.3067 | 121.8567 | 121.8109 | 121.6415 | 121.4951 | 121.2524 | 122.7219 | 121.6736 | -0.37079 | 121.4951 | 121.2524 | 121.6736 | 121.6415 | 122.7219 | -1.7395 | -123.056
3872.9062 | 122.7081 | -121.5088 | 1.2222 | 0.14145 | 0.00088016 | -0.0063724 | 0.025263 | -0.0028348 | 0.00034814 | 0.0068295 | -0.23346 | 0 | -0.51727 | 0.44861 | 0.17853 | 0.20599 | 0.36163 | 0.32044 | 1.2451 | -121.8567 | 120.9915 | -1.2222 | 121.2753 | 121.9574 | -1.0437 | -0.3479 | 0.022888 | 0.28381 | 121.8704 | 121.8292 | 121.6873 | 121.5088 | 121.2753 | 122.7539 | 121.7148 | -0.3479 | 121.5088 | 121.2753 | 121.7148 | 121.6873 | 122.7539 | -1.7395 | -123.0789
3873.9062 | 122.7081 | -121.4859 | 1.2131 | 0.019379 | -0.00082884 | -0.0046634 | 0.02804 | -0.002194 | -0.00050626 | 0.0083249 | -0.2243 | -0.022888 | -0.53558 | 0.4715 | 0.17395 | 0.20599 | 0.37079 | 0.33875 | 1.2634 | -121.8704 | 120.9503 | -1.236 | 121.2616 | 121.9574 | -1.0391 | -0.38452 | 0.050354 | 0.31128 | 121.8567 | 121.8246 | 121.6599 | 121.463 | 121.2616 | 122.7493 | 121.6919 | -0.38452 | 121.463 | 121.2616 | 121.6919 | 121.6599 | 122.7493 | -1.7487 | -123.0835
3874.9062 | 122.6898 | -121.6141 | 1.062 | 0.065155 | 0.00045296 | -0.0061588 | 0.028681 | -0.00091219 | -0.0017881 | 0.011316 | -0.31128 | -0.036621 | -0.59509 | 0.64087 | 0.10529 | 0.16022 | 0.10071 | 0.17853 | 1.0895 | -122.0169 | 121.019 | -1.0986 | 121.3028 | 122.2549 | -0.95673 | -0.40283 | 0.027466 | 0.28381 | 121.7148 | 121.7926 | 121.7194 | 121.5775 | 121.3028 | 122.7036 | 121.7743 | -0.40283 | 121.5775 | 121.3028 | 121.7743 | 121.7194 | 122.7036 | -1.6571 | -123.0789
3875.9219 | 122.7951 | -121.582 | 1.0208 | 0.065155 | -0.005315 | -0.010431 | 0.018641 | -0.0026212 | -0.00050626 | 0.0070431 | -0.29755 | -0.073242 | -0.55847 | 0.70038 | 0.18768 | 0.27008 | 0.004578 | 0.30212 | 1.062 | -121.9437 | 121.0236 | -1.0941 | 121.2845 | 122.2824 | -0.83313 | -0.36163 | 0.041199 | 0.26093 | 121.5866 | 121.8842 | 121.7697 | 121.5088 | 121.2845 | 122.644 | 121.8521 | -0.36163 | 121.5088 | 121.2845 | 121.8521 | 121.7697 | 122.644 | -1.5793 | -122.9645
3876.9062 | 122.731 | -121.637 | 1.0803 | 0.21011 | -0.00018804 | -0.0095766 | 0.027186 | -0.0045438 | -0.0020017 | 0.010247 | -0.28381 | -0.004578 | -0.56305 | 0.65918 | 0.10986 | 0.1831 | 0.073242 | 0.1831 | 1.0895 | -122.0306 | 121.0739 | -1.0849 | 121.3531 | 122.2961 | -0.97046 | -0.39368 | 0.009156 | 0.27924 | 121.7102 | 121.8201 | 121.7468 | 121.6324 | 121.3531 | 122.7264 | 121.8201 | -0.39368 | 121.6324 | 121.3531 | 121.8201 | 121.7468 | 122.7264 | -1.6434 | -123.111
3877.9062 | 122.7219 | -121.6415 | 1.0483 | 0.17197 | 0.00088016 | -0.007654 | 0.026545 | -0.0019802 | -0.0013609 | 0.0093931 | -0.2655 | -0.004578 | -0.54016 | 0.63629 | 0.11444 | 0.17395 | 0.073242 | 0.17853 | 1.0941 | -122.0123 | 121.1014 | -1.0529 | 121.376 | 122.2778 | -0.93384 | -0.37079 | 0.045776 | 0.27466 | 121.7148 | 121.8201 | 121.756 | 121.637 | 121.376 | 122.7356 | 121.8155 | -0.37079 | 121.637 | 121.376 | 121.8155 | 121.756 | 122.7356 | -1.5884 | -123.0606
3878.9062 | 122.7219 | -121.6461 | 1.062 | 0.17197 | 0.0019482 | -0.007654 | 0.026545 | -0.0028348 | 0.00098914 | 0.0085385 | -0.27466 | -0.009155 | -0.54016 | 0.64545 | 0.09613 | 0.16937 | 0.082397 | 0.1831 | 1.0849 | -122.0215 | 121.106 | -1.0712 | 121.3715 | 122.2916 | -0.96588 | -0.37537 | 0.022888 | 0.2655 | 121.7285 | 121.8292 | 121.7422 | 121.637 | 121.3715 | 122.731 | 121.8155 | -0.37537 | 121.637 | 121.3715 | 121.8155 | 121.7422 | 122.731 | -1.6022 | -123.0835
3879.9062 | 122.731 | -121.6324 | 1.0529 | 0.22537 | -0.00082884 | -0.0091494 | 0.025477 | -0.0017666 | -0.0022153 | 0.010461 | -0.28839 | -0.054932 | -0.5722 | 0.6546 | 0.13275 | 0.19684 | 0.068665 | 0.20599 | 1.0757 | -122.0169 | 121.0602 | -1.1078 | 121.344 | 122.287 | -0.9201 | -0.38452 | 0.022889 | 0.28381 | 121.701 | 121.8384 | 121.7651 | 121.5775 | 121.344 | 122.7081 | 121.8292 | -0.38452 | 121.5775 | 121.344 | 121.8292 | 121.7651 | 122.7081 | -1.6251 | -123.0698
3880.9062 | 122.7356 | -121.6644 | 1.0208 | 0.1796 | 0.002162 | -0.0089358 | 0.026117 | -0.0028348 | 0.0016299 | 0.0068295 | -0.29297 | -0.041199 | -0.59052 | 0.63629 | 0.11444 | 0.1831 | 0.091553 | 0.20599 | 1.0712 | -122.0261 | 121.0739 | -1.062 | 121.3715 | 122.3007 | -0.90637 | -0.36163 | 0.050354 | 0.29755 | 121.756 | 121.8704 | 121.7789 | 121.6232 | 121.3715 | 122.7356 | 121.8475 | -0.36163 | 121.6232 | 121.3715 | 121.8475 | 121.7789 | 122.7356 | -1.6113 | -123.0469
3881.9062 | 122.6898 | -121.7194 | 0.97504 | 0.21011 | -0.00040164 | -0.0055178 | 0.02804 | -0.003262 | -0.0015745 | 0.0070431 | -0.28381 | -0.018311 | -0.56305 | 0.58136 | 0.091553 | 0.13275 | 0.15564 | 0.18768 | 1.0208 | -122.0764 | 121.1563 | -0.99335 | 121.4355 | 122.3007 | -0.88348 | -0.35706 | 0.045776 | 0.27924 | 121.875 | 121.907 | 121.8109 | 121.701 | 121.4355 | 122.7402 | 121.8521 | -0.35706 | 121.701 | 121.4355 | 121.8521 | 121.8109 | 122.7402 | -1.5381 | -123.0515
3882.9062 | 122.6944 | -121.7606 | 0.94299 | 0.14908 | -0.00082884 | -0.0072268 | 0.026117 | -0.00048499 | -0.00093346 | 0.0083249 | -0.29297 | -0.013733 | -0.5722 | 0.54474 | 0.10071 | 0.15564 | 0.13733 | 0.18768 | 0.97961 | -122.1176 | 121.1884 | -0.95673 | 121.4676 | 122.3053 | -0.84228 | -0.35706 | 0.036621 | 0.27924 | 121.8979 | 121.9482 | 121.8613 | 121.7468 | 121.4676 | 122.7402 | 121.9162 | -0.35706 | 121.7468 | 121.4676 | 121.9162 | 121.8613 | 122.7402 | -1.5152 | -123.0606
3883.9062 | 122.7081 | -121.7606 | 0.93384 | 0.16434 | -0.00018804 | -0.0087222 | 0.026545 | -0.0024076 | -0.0020017 | 0.0091795 | -0.27466 | -0.004578 | -0.54474 | 0.54016 | 0.10529 | 0.15106 | 0.13733 | 0.18768 | 1.0025 | -122.113 | 121.2158 | -0.93842 | 121.4859 | 122.3007 | -0.82855 | -0.35248 | 0.068664 | 0.27008 | 121.8979 | 121.9482 | 121.8658 | 121.756 | 121.4859 | 122.7631 | 121.9116 | -0.35248 | 121.756 | 121.4859 | 121.9116 | 121.8658 | 122.7631 | -1.4786 | -123.0469
3884.9062 | 122.6898 | -121.7651 | 0.95673 | 0.072784 | -0.0010424 | -0.008295 | 0.02804 | -0.0011258 | -7.9062e-05 | 0.0083249 | -0.27466 | -0.004578 | -0.54932 | 0.54474 | 0.10071 | 0.15106 | 0.15564 | 0.20142 | 0.97961 | -122.1451 | 121.2158 | -0.9613 | 121.4905 | 122.3099 | -0.85602 | -0.37994 | 0.022888 | 0.27466 | 121.9208 | 121.9666 | 121.8658 | 121.7606 | 121.4905 | 122.7448 | 121.9162 | -0.37994 | 121.7606 | 121.4905 | 121.9162 | 121.8658 | 122.7448 | -1.506 | -123.1018
3885.9062 | 122.8271 | -121.6919 | 0.92926 | 0.20248 | -0.001897 | -0.0020998 | 0.019709 | -0.0045438 | 0.00077554 | 0.0096067 | -0.19684 | -0.068665 | -0.50812 | 0.6546 | 0.21057 | 0.30212 | -0.027466 | 0.3479 | 0.93842 | -122.0581 | 121.1838 | -0.99792 | 121.4951 | 122.3465 | -0.71869 | -0.36621 | 0.009156 | 0.31128 | 121.6644 | 122.0398 | 121.9025 | 121.6232 | 121.4951 | 122.6303 | 121.994 | -0.36621 | 121.6232 | 121.4951 | 121.994 | 121.9025 | 122.6303 | -1.4374 | -122.9874
3886.9062 | 122.7127 | -121.7606 | 0.9613 | 0.1033 | 0.00088016 | -0.0038088 | 0.028467 | -0.00091219 | -0.0026425 | 0.0091795 | -0.22888 | -0.009155 | -0.54016 | 0.55847 | 0.10986 | 0.15564 | 0.15564 | 0.21973 | 0.97961 | -122.1359 | 121.2204 | -0.97046 | 121.5317 | 122.319 | -0.85144 | -0.37537 | 0.01831 | 0.31128 | 121.9162 | 121.9803 | 121.8704 | 121.7514 | 121.5317 | 122.7402 | 121.9162 | -0.37537 | 121.7514 | 121.5317 | 121.9162 | 121.8704 | 122.7402 | -1.5015 | -123.0972
3887.9062 | 122.7402 | -121.7606 | 0.91553 | -0.026398 | -0.0021106 | -0.0080814 | 0.027399 | -0.0028348 | 0.00098914 | 0.010675 | -0.20142 | -0.022888 | -0.55389 | 0.59509 | 0.14648 | 0.20142 | 0.13733 | 0.27924 | 0.97046 | -122.1497 | 121.2067 | -0.93841 | 121.5591 | 122.3557 | -0.76904 | -0.3891 | 0.054932 | 0.35248 | 121.8979 | 122.0398 | 121.907 | 121.7377 | 121.5591 | 122.731 | 121.962 | -0.3891 | 121.7377 | 121.5591 | 121.962 | 121.907 | 122.731 | -1.4694 | -123.0652
3888.9062 | 122.7402 | -121.8155 | 0.92926 | 0.042267 | 0.0013074 | -0.0059452 | 0.025904 | -0.0026212 | -0.0013609 | 0.010034 | -0.21973 | -0.013733 | -0.54932 | 0.55847 | 0.11902 | 0.17853 | 0.13733 | 0.2243 | 0.95673 | -122.1542 | 121.2662 | -0.94299 | 121.5958 | 122.374 | -0.81024 | -0.33875 | 0.027466 | 0.32959 | 121.9528 | 122.0398 | 121.9345 | 121.8018 | 121.5958 | 122.7722 | 121.994 | -0.33875 | 121.8018 | 121.5958 | 121.994 | 121.9345 | 122.7722 | -1.4786 | -123.0835
3889.9062 | 122.7264 | -121.8201 | 0.93384 | 0.072784 | 0.00066656 | -0.007654 | 0.026331 | -0.0019802 | -0.00093346 | 0.0096067 | -0.25177 | -0.013733 | -0.56763 | 0.54474 | 0.10071 | 0.15106 | 0.17853 | 0.20142 | 0.95673 | -122.1771 | 121.2524 | -0.94757 | 121.5683 | 122.3648 | -0.83313 | -0.35706 | 0.022888 | 0.31586 | 121.9986 | 122.0215 | 121.9208 | 121.8063 | 121.5683 | 122.7768 | 121.9711 | -0.35706 | 121.8063 | 121.5683 | 121.9711 | 121.9208 | 122.7768 | -1.5015 | -123.111
3890.9062 | 122.818 | -121.7514 | 0.88348 | 0.233 | 0.00088016 | -0.0061588 | 0.023768 | -0.00048499 | -0.0017881 | 0.010247 | -0.23804 | -0.050354 | -0.54016 | 0.61798 | 0.19226 | 0.27008 | 0 | 0.30212 | 0.93842 | -122.081 | 121.2112 | -0.93384 | 121.5134 | 122.3694 | -0.69122 | -0.32959 | 0.054932 | 0.30212 | 121.7514 | 122.0535 | 121.9437 | 121.701 | 121.5134 | 122.6898 | 122.0215 | -0.32959 | 121.701 | 121.5134 | 122.0215 | 121.9437 | 122.6898 | -1.4236 | -122.9645
3891.9062 | 122.731 | -121.7697 | 0.93842 | 0.027008 | 0.00088016 | -0.0097904 | 0.028254 | -0.00091219 | -0.0017881 | 0.0096067 | -0.25177 | -0.050354 | -0.56763 | 0.55847 | 0.10529 | 0.17395 | 0.15564 | 0.24261 | 0.9613 | -122.1588 | 121.2021 | -0.98877 | 121.5179 | 122.3282 | -0.83313 | -0.3891 | 0.022888 | 0.31586 | 121.9254 | 122.0123 | 121.875 | 121.7194 | 121.5179 | 122.731 | 121.9437 | -0.3891 | 121.7194 | 121.5179 | 121.9437 | 121.875 | 122.731 | -1.506 | -123.0972
3892.9062 | 122.7402 | -121.7743 | 0.92468 | 0.019379 | 0.00088016 | -0.006586 | 0.027399 | -0.00091219 | -0.0024289 | 0.0068295 | -0.23346 | -0.027466 | -0.56763 | 0.57678 | 0.13275 | 0.17395 | 0.13275 | 0.24261 | 0.95673 | -122.1313 | 121.2067 | -0.95215 | 121.5408 | 122.3511 | -0.79193 | -0.35706 | 0.032043 | 0.33417 | 121.907 | 122.0169 | 121.907 | 121.7468 | 121.5408 | 122.731 | 121.9482 | -0.35706 | 121.7468 | 121.5408 | 121.9482 | 121.907 | 122.731 | -1.4923 | -123.056
3893.9062 | 122.7402 | -121.7972 | 0.89722 | 0.042267 | -0.0010424 | -0.0055178 | 0.028681 | -0.0017666 | -0.00071986 | 0.010461 | -0.22888 | -0.045776 | -0.56763 | 0.58136 | 0.14648 | 0.19684 | 0.13275 | 0.2655 | 0.94757 | -122.1405 | 121.2296 | -0.94299 | 121.5683 | 122.3785 | -0.75073 | -0.34332 | 0.050354 | 0.33874 | 121.9299 | 122.0627 | 121.9437 | 121.7514 | 121.5683 | 122.7448 | 121.994 | -0.34332 | 121.7514 | 121.5683 | 121.994 | 121.9437 | 122.7448 | -1.4648 | -123.0377
3894.9062 | 122.7585 | -121.8109 | 0.92468 | -0.034027 | -0.00040164 | -0.0057314 | 0.025263 | -0.001553 | -7.9062e-05 | 0.0083249 | -0.20599 | 0 | -0.54932 | 0.59052 | 0.14191 | 0.21057 | 0.13275 | 0.27924 | 0.94757 | -122.1313 | 121.2616 | -0.92468 | 121.6049 | 122.4014 | -0.78278 | -0.32044 | 0.022888 | 0.34332 | 121.9437 | 122.0901 | 121.9528 | 121.8109 | 121.6049 | 122.7585 | 122.0215 | -0.32044 | 121.8109 | 121.6049 | 122.0215 | 121.9528 | 122.7585 | -1.474 | -123.056
3895.9062 | 122.7356 | -121.7743 | 0.93842 | -0.011139 | 0.00023916 | -0.0080814 | 0.026972 | 0.00036961 | 0.00013454 | 0.0087521 | -0.2243 | 0.018311 | -0.53101 | 0.58594 | 0.12817 | 0.19226 | 0.14191 | 0.26093 | 0.98419 | -122.1085 | 121.2433 | -0.92011 | 121.55 | 122.3602 | -0.81024 | -0.33417 | 0.045776 | 0.3067 | 121.9162 | 122.0352 | 121.9025 | 121.7926 | 121.55 | 122.7585 | 121.9666 | -0.33417 | 121.7926 | 121.55 | 121.9666 | 121.9025 | 122.7585 | -1.4694 | -123.0469
3896.9062 | 122.7493 | -121.788 | 0.9201 | -0.026398 | 2.5564e-05 | -0.0085086 | 0.026972 | -0.00069859 | -0.0037107 | 0.0098203 | -0.22888 | -0.013733 | -0.54474 | 0.58136 | 0.12817 | 0.19684 | 0.13275 | 0.25635 | 0.97961 | -122.1222 | 121.2433 | -0.93384 | 121.5591 | 122.3694 | -0.79193 | -0.33417 | 0.059509 | 0.31586 | 121.9208 | 122.0444 | 121.9162 | 121.7743 | 121.5591 | 122.7676 | 121.9849 | -0.33417 | 121.7743 | 121.5591 | 121.9849 | 121.9162 | 122.7676 | -1.4648 | -123.0423
3897.9062 | 122.7493 | -121.8018 | 0.91095 | -0.011139 | -0.00018804 | -0.004877 | 0.024622 | -0.0017666 | -0.0022153 | 0.0093931 | -0.21057 | -0.041199 | -0.56305 | 0.59052 | 0.14648 | 0.21057 | 0.14191 | 0.2655 | 0.95673 | -122.1497 | 121.2387 | -0.95215 | 121.5912 | 122.3923 | -0.76447 | -0.3479 | 0.045776 | 0.35248 | 121.9437 | 122.0673 | 121.9482 | 121.7606 | 121.5912 | 122.7585 | 122.0123 | -0.3479 | 121.7606 | 121.5912 | 122.0123 | 121.9482 | 122.7585 | -1.474 | -123.0606
3898.9062 | 122.7585 | -121.8018 | 0.91095 | -0.064545 | -0.001897 | -0.007654 | 0.026117 | 0.00036961 | -0.0015745 | 0.0076841 | -0.19226 | -0.004578 | -0.51727 | 0.57678 | 0.14191 | 0.21057 | 0.13733 | 0.27008 | 0.93384 | -122.1313 | 121.2845 | -0.91553 | 121.6095 | 122.3785 | -0.76904 | -0.32959 | 0.022888 | 0.32501 | 121.9391 | 122.0718 | 121.9437 | 121.7972 | 121.6095 | 122.7356 | 122.0123 | -0.32959 | 121.7972 | 121.6095 | 122.0123 | 121.9437 | 122.7356 | -1.4282 | -123.0423
3899.9062 | 122.7493 | -121.7926 | 0.91553 | -0.11032 | 0.00066656 | -0.0061588 | 0.026117 | -0.00091219 | -0.0015745 | 0.012384 | -0.20599 | -0.045776 | -0.55389 | 0.58594 | 0.15564 | 0.21057 | 0.12817 | 0.2655 | 0.95673 | -122.1588 | 121.2387 | -0.9613 | 121.5866 | 122.3785 | -0.75989 | -0.36621 | 0.041199 | 0.3479 | 121.9208 | 122.0581 | 121.9482 | 121.7468 | 121.5866 | 122.7493 | 122.0032 | -0.36621 | 121.7468 | 121.5866 | 122.0032 | 121.9482 | 122.7493 | -1.4694 | -123.0743
3900.9062 | 122.8271 | -121.7422 | 0.86517 | 0.19485 | -0.0031786 | -0.010004 | 0.017573 | -0.00091219 | 0.00077554 | 0.010247 | -0.22888 | -0.09613 | -0.56305 | 0.60883 | 0.21057 | 0.28839 | -0.009155 | 0.33875 | 0.9201 | -122.0947 | 121.1792 | -0.9613 | 121.5134 | 122.3511 | -0.6546 | -0.35248 | 0.054932 | 0.33417 | 121.7331 | 122.081 | 121.9528 | 121.6461 | 121.5134 | 122.6624 | 122.0306 | -0.35248 | 121.6461 | 121.5134 | 122.0306 | 121.9528 | 122.6624 | -1.4282 | -122.9599
3901.9062 | 122.7768 | -121.7972 | 0.91553 | -0.12558 | -0.00040164 | -0.0070132 | 0.028467 | -0.0041166 | -0.0017881 | 0.0078977 | -0.24261 | -0.054932 | -0.56763 | 0.59052 | 0.14191 | 0.2243 | 0.12817 | 0.27924 | 0.93842 | -122.1725 | 121.2296 | -0.97046 | 121.5546 | 122.3877 | -0.77362 | -0.37537 | 0.022889 | 0.32501 | 121.9254 | 122.0764 | 121.9391 | 121.7422 | 121.5546 | 122.7356 | 122.0215 | -0.37537 | 121.7422 | 121.5546 | 122.0215 | 121.9391 | 122.7356 | -1.4832 | -123.0881
3902.9062 | 122.7631 | -121.8201 | 0.89264 | -0.056915 | 0.00088016 | -0.0080814 | 0.026331 | -0.0011258 | -0.0013609 | 0.0096067 | -0.25177 | -0.036621 | -0.58594 | 0.58136 | 0.15564 | 0.20599 | 0.13733 | 0.27924 | 0.93384 | -122.1634 | 121.2341 | -0.92926 | 121.5683 | 122.4014 | -0.737 | -0.34332 | 0.041199 | 0.33417 | 121.9574 | 122.0993 | 121.9757 | 121.7834 | 121.5683 | 122.7539 | 122.0261 | -0.34332 | 121.7834 | 121.5683 | 122.0261 | 121.9757 | 122.7539 | -1.4786 | -123.056
3903.9062 | 122.7539 | -121.7514 | 0.88806 | -0.072174 | -0.0014696 | -0.010431 | 0.028895 | -0.00027139 | -0.0015745 | 0.0098203 | -0.24719 | -0.082397 | -0.59052 | 0.58594 | 0.13733 | 0.20599 | 0.11902 | 0.27466 | 0.9201 | -122.1588 | 121.1609 | -0.97046 | 121.5042 | 122.3373 | -0.75073 | -0.40741 | 0.032043 | 0.34332 | 121.8704 | 122.0261 | 121.8887 | 121.669 | 121.5042 | 122.6715 | 121.9574 | -0.40741 | 121.669 | 121.5042 | 121.9574 | 121.8887 | 122.6715 | -1.4786 | -123.0469
3904.9062 | 122.7722 | -121.8109 | 0.90179 | -0.072174 | 0.0010938 | -0.0040226 | 0.027399 | -0.0013394 | -0.0011471 | 0.010675 | -0.25635 | -0.068665 | -0.5722 | 0.58136 | 0.14648 | 0.21057 | 0.12817 | 0.27008 | 0.94757 | -122.168 | 121.2387 | -0.97046 | 121.5546 | 122.3923 | -0.75531 | -0.35706 | 0.045777 | 0.31586 | 121.9391 | 122.081 | 121.9574 | 121.7422 | 121.5546 | 122.7585 | 122.0215 | -0.35706 | 121.7422 | 121.5546 | 122.0215 | 121.9574 | 122.7585 | -1.474 | -123.0698
3905.9062 | 122.7081 | -121.8521 | 0.89722 | 0.15671 | -0.0031786 | -0.004877 | 0.025904 | -0.00069859 | -0.0030697 | 0.010461 | -0.32501 | -0.091553 | -0.60883 | 0.5127 | 0.10071 | 0.15564 | 0.15564 | 0.1831 | 0.92468 | -122.1725 | 121.2433 | -0.98877 | 121.5271 | 122.3648 | -0.79651 | -0.32043 | 0.027466 | 0.28381 | 122.0078 | 122.0352 | 121.9528 | 121.7606 | 121.5271 | 122.7768 | 122.0078 | -0.32043 | 121.7606 | 121.5271 | 122.0078 | 121.9528 | 122.7768 | -1.506 | -123.0698
3906.9062 | 122.7631 | -121.8246 | 0.86975 | -0.072174 | 0.00045296 | -0.010645 | 0.027399 | -0.0041166 | -0.0022153 | 0.0093931 | -0.27466 | -0.082397 | -0.59509 | 0.57678 | 0.16479 | 0.21057 | 0.11902 | 0.27466 | 0.91095 | -122.1497 | 121.2296 | -0.95215 | 121.55 | 122.4014 | -0.70496 | -0.32501 | 0.041199 | 0.32043 | 121.9437 | 122.0993 | 121.9894 | 121.7422 | 121.55 | 122.7356 | 122.0352 | -0.32501 | 121.7422 | 121.55 | 122.0352 | 121.9894 | 122.7356 | -1.4648 | -123.0194
3907.9062 | 122.7448 | -121.875 | 0.84228 | -0.18662 | 0.00088016 | -0.011072 | 0.026331 | -0.0024076 | -0.0015745 | 0.010461 | -0.35248 | -0.09613 | -0.6134 | 0.5127 | 0.11444 | 0.17853 | 0.1831 | 0.23804 | 0.87433 | -122.2321 | 121.2616 | -0.93841 | 121.5225 | 122.3877 | -0.72784 | -0.35706 | 0.032044 | 0.26093 | 122.0581 | 122.113 | 121.9894 | 121.7789 | 121.5225 | 122.7493 | 122.0535 | -0.35706 | 121.7789 | 121.5225 | 122.0535 | 121.9894 | 122.7493 | -1.4557 | -123.0743
3908.9062 | 122.7722 | -121.8887 | 0.82398 | -0.17899 | 0.00045296 | -0.0042362 | 0.026972 | -0.0026212 | -0.0028561 | 0.0089657 | -0.3067 | -0.11444 | -0.64087 | 0.53558 | 0.1831 | 0.21057 | 0.14648 | 0.28839 | 0.87433 | -122.2641 | 121.2479 | -0.93842 | 121.582 | 122.4243 | -0.64087 | -0.37537 | 0.050354 | 0.33417 | 122.0352 | 122.1771 | 122.0718 | 121.7743 | 121.582 | 122.7631 | 122.0993 | -0.37537 | 121.7743 | 121.582 | 122.0993 | 122.0718 | 122.7631 | -1.4648 | -123.0881
3909.9062 | 122.7585 | -121.8796 | 0.83313 | -0.079803 | -0.001256 | -0.0097904 | 0.023768 | -0.0017666 | -0.00071986 | 0.010675 | -0.32044 | -0.11902 | -0.6546 | 0.53558 | 0.16937 | 0.23346 | 0.1236 | 0.25177 | 0.85602 | -122.2321 | 121.225 | -0.95215 | 121.5591 | 122.4152 | -0.66376 | -0.35248 | 0.022888 | 0.33417 | 122.0032 | 122.1313 | 122.049 | 121.7606 | 121.5591 | 122.7356 | 122.113 | -0.35248 | 121.7606 | 121.5591 | 122.113 | 122.049 | 122.7356 | -1.4877 | -123.0652
3910.9062 | 122.7631 | -121.8658 | 0.82855 | 0.18723 | -0.0016834 | -0.0074404 | 0.024622 | -0.0024076 | -0.0020017 | 0.011316 | -0.40283 | -0.15106 | -0.66376 | 0.5127 | 0.14648 | 0.20142 | 0.09613 | 0.23804 | 0.87433 | -122.2275 | 121.2021 | -0.97961 | 121.463 | 122.3785 | -0.68207 | -0.36163 | 0.045777 | 0.26093 | 121.962 | 122.1039 | 122.0123 | 121.7148 | 121.463 | 122.7402 | 122.0673 | -0.36163 | 121.7148 | 121.463 | 122.0673 | 122.0123 | 122.7402 | -1.4923 | -123.056
3911.9062 | 122.7768 | -121.843 | 0.84228 | -0.041657 | -0.0014696 | -0.010858 | 0.024408 | -0.0026212 | -0.0011471 | 0.011102 | -0.32044 | -0.11444 | -0.63171 | 0.55389 | 0.16479 | 0.2243 | 0.11902 | 0.28839 | 0.88348 | -122.2504 | 121.2112 | -0.95673 | 121.5225 | 122.3969 | -0.67749 | -0.40741 | 0.041199 | 0.31128 | 121.962 | 122.1313 | 122.0078 | 121.7285 | 121.5225 | 122.7264 | 122.0673 | -0.40741 | 121.7285 | 121.5225 | 122.0673 | 122.0078 | 122.7264 | -1.474 | -123.0927
3912.9062 | 122.7631 | -121.8521 | 0.84228 | -0.11795 | -0.0014696 | -0.0091494 | 0.02569 | 0.00058321 | -0.00029266 | 0.010888 | -0.30212 | -0.10986 | -0.62714 | 0.56305 | 0.17395 | 0.22888 | 0.13733 | 0.29297 | 0.87891 | -122.2137 | 121.225 | -0.95215 | 121.55 | 122.4152 | -0.66833 | -0.36163 | 0.036621 | 0.32501 | 121.9894 | 122.1451 | 122.0261 | 121.7422 | 121.55 | 122.731 | 122.081 | -0.36163 | 121.7422 | 121.55 | 122.081 | 122.0261 | 122.731 | -1.4694 | -123.056
3913.9062 | 122.7676 | -121.843 | 0.86517 | -0.095062 | -0.0025378 | -0.013849 | 0.025904 | -0.0026212 | -0.0017881 | 0.011316 | -0.27924 | -0.09613 | -0.63171 | 0.56305 | 0.17395 | 0.23346 | 0.15106 | 0.28839 | 0.88806 | -122.2183 | 121.2112 | -0.9613 | 121.5637 | 122.406 | -0.69122 | -0.37537 | 0.022889 | 0.35248 | 121.994 | 122.1313 | 122.0169 | 121.7468 | 121.5637 | 122.731 | 122.0764 | -0.37537 | 121.7468 | 121.5637 | 122.0764 | 122.0169 | 122.731 | -1.4969 | -123.0835
3914.9062 | 122.7539 | -121.875 | 0.86517 | -0.16373 | 0.00066656 | -0.010218 | 0.02334 | -0.0034756 | -0.00071986 | 0.0091795 | -0.36163 | -0.10986 | -0.63171 | 0.52185 | 0.15106 | 0.19226 | 0.21515 | 0.25635 | 0.88806 | -122.2183 | 121.2433 | -0.97504 | 121.5134 | 122.3969 | -0.71411 | -0.34332 | 0.022889 | 0.27008 | 122.0901 | 122.1313 | 122.0261 | 121.7651 | 121.5134 | 122.7631 | 122.0673 | -0.34332 | 121.7651 | 121.5134 | 122.0673 | 122.0261 | 122.7631 | -1.4969 | -123.0835
3915.9062 | 122.7814 | -121.8384 | 0.87891 | -0.21713 | -0.003606 | -0.007654 | 0.024622 | -0.0019802 | -0.0011471 | 0.0087521 | -0.32959 | -0.12817 | -0.65002 | 0.56305 | 0.1831 | 0.22888 | 0.17853 | 0.30212 | 0.90637 | -122.2 | 121.1884 | -1.0071 | 121.5088 | 122.4014 | -0.6958 | -0.36163 | 0.027466 | 0.32043 | 122.0169 | 122.1405 | 122.0215 | 121.7102 | 121.5088 | 122.7448 | 122.0673 | -0.36163 | 121.7102 | 121.5088 | 122.0673 | 122.0215 | 122.7448 | -1.5289 | -123.0789
3916.9062 | 122.7722 | -121.8658 | 0.85144 | -0.049286 | -0.0014696 | -0.0063724 | 0.026331 | -0.002194 | -0.00071986 | 0.010675 | -0.3067 | -0.11902 | -0.63629 | 0.56763 | 0.16937 | 0.23346 | 0.16479 | 0.29297 | 0.89722 | -122.1954 | 121.2296 | -0.97046 | 121.5591 | 122.4335 | -0.68207 | -0.32959 | 0.045777 | 0.32959 | 122.0306 | 122.1588 | 122.0352 | 121.7468 | 121.5591 | 122.7631 | 122.0993 | -0.32959 | 121.7468 | 121.5591 | 122.0993 | 122.0352 | 122.7631 | -1.4877 | -123.0469
3917.9062 | 122.7768 | -121.8475 | 0.84686 | -0.1561 | 0.00088016 | -0.0074404 | 0.027186 | -0.00069859 | -0.0015745 | 0.0083249 | -0.32044 | -0.11444 | -0.6546 | 0.58136 | 0.17395 | 0.22888 | 0.14648 | 0.29755 | 0.9201 | -122.1771 | 121.1929 | -0.9613 | 121.5271 | 122.4289 | -0.67291 | -0.32959 | 0.073242 | 0.33417 | 121.994 | 122.1451 | 122.0215 | 121.7331 | 121.5271 | 122.7676 | 122.0764 | -0.32959 | 121.7331 | 121.5271 | 122.0764 | 122.0215 | 122.7676 | -1.5015 | -123.024
3918.9062 | 122.7676 | -121.8613 | 0.86517 | -0.1561 | -0.00082884 | -0.010004 | 0.025904 | -0.0026212 | -0.00071986 | 0.0098203 | -0.32044 | -0.11902 | -0.64087 | 0.56763 | 0.19226 | 0.24261 | 0.16022 | 0.29755 | 0.91095 | -122.1909 | 121.2204 | -0.98419 | 121.5408 | 122.4289 | -0.67291 | -0.32959 | 0.045777 | 0.32043 | 122.0215 | 122.1588 | 122.0535 | 121.7422 | 121.5408 | 122.7722 | 122.1039 | -0.32959 | 121.7422 | 121.5408 | 122.1039 | 122.0535 | 122.7722 | -1.506 | -123.056
3919.9062 | 122.7768 | -121.8384 | 0.84686 | -0.2095 | 0.00023916 | -0.012781 | 0.026117 | -0.0013394 | -0.0017881 | 0.0096067 | -0.33417 | -0.13733 | -0.65918 | 0.55847 | 0.17395 | 0.2243 | 0.16479 | 0.28381 | 0.89722 | -122.2046 | 121.1792 | -0.98419 | 121.5042 | 122.3969 | -0.67291 | -0.36621 | 0.050354 | 0.32501 | 122.0032 | 122.1222 | 122.0123 | 121.7011 | 121.5042 | 122.7356 | 122.0627 | -0.36621 | 121.7011 | 121.5042 | 122.0627 | 122.0123 | 122.7356 | -1.506 | -123.0515
3920.9062 | 122.7264 | -121.8567 | 0.88806 | 0.16434 | -0.00040164 | -0.0091494 | 0.025263 | -0.001553 | -0.0022153 | 0.0087521 | -0.40283 | -0.14191 | -0.67749 | 0.50812 | 0.11902 | 0.20142 | 0.16937 | 0.20599 | 0.91553 | -122.2137 | 121.1792 | -1.03 | 121.4539 | 122.3648 | -0.76904 | -0.35706 | 0.027465 | 0.27466 | 122.0261 | 122.0627 | 121.9757 | 121.7148 | 121.4539 | 122.7722 | 122.0581 | -0.35706 | 121.7148 | 121.4539 | 122.0581 | 121.9757 | 122.7722 | -1.5656 | -123.1018
3921.9062 | 122.7402 | -121.8979 | 0.86517 | -0.20187 | -0.0016834 | -0.008295 | 0.02334 | -0.0036892 | -0.0015745 | 0.0078977 | -0.38452 | -0.10529 | -0.66376 | 0.51727 | 0.13733 | 0.19226 | 0.22888 | 0.24719 | 0.90637 | -122.2321 | 121.2341 | -0.97046 | 121.5134 | 122.4152 | -0.72784 | -0.33417 | 0.041199 | 0.27924 | 122.1268 | 122.1451 | 122.0352 | 121.7926 | 121.5134 | 122.8043 | 122.0901 | -0.33417 | 121.7926 | 121.5134 | 122.0901 | 122.0352 | 122.8043 | -1.5289 | -123.0972
3922.9062 | 122.7814 | -121.8704 | 0.84228 | -0.13321 | -0.00018804 | -0.0087222 | 0.026331 | -0.0026212 | -7.9062e-05 | 0.010034 | -0.36621 | -0.13733 | -0.68207 | 0.54474 | 0.17853 | 0.21515 | 0.20142 | 0.30212 | 0.89722 | -122.2137 | 121.1884 | -0.97961 | 121.5042 | 122.4152 | -0.66376 | -0.34332 | 0.054932 | 0.31586 | 122.0718 | 122.1725 | 122.049 | 121.7331 | 121.5042 | 122.7676 | 122.0856 | -0.34332 | 121.7331 | 121.5042 | 122.0856 | 122.049 | 122.7676 | -1.5244 | -123.056
3923.9062 | 122.7722 | -121.8521 | 0.86517 | -0.13321 | -0.00040164 | -0.0072268 | 0.027399 | -0.0013394 | -0.0030697 | 0.011529 | -0.33875 | -0.13275 | -0.66834 | 0.55847 | 0.1831 | 0.23804 | 0.16022 | 0.28839 | 0.88348 | -122.2183 | 121.1838 | -0.99792 | 121.5134 | 122.4106 | -0.68207 | -0.36621 | 0.018311 | 0.32959 | 122.0123 | 122.1405 | 122.0352 | 121.7194 | 121.5134 | 122.7356 | 122.0901 | -0.36621 | 121.7194 | 121.5134 | 122.0901 | 122.0352 | 122.7356 | -1.5335 | -123.0835
3924.9062 | 122.7768 | -121.8613 | 0.84686 | -0.10269 | -0.00018804 | -0.008295 | 0.027186 | -0.0019802 | 0.00077554 | 0.0091795 | -0.36163 | -0.15106 | -0.68665 | 0.56305 | 0.1831 | 0.23804 | 0.16022 | 0.30212 | 0.90179 | -122.2046 | 121.1746 | -0.99793 | 121.4996 | 122.4243 | -0.66376 | -0.34332 | 0.054931 | 0.32501 | 122.0215 | 122.1634 | 122.0444 | 121.7102 | 121.4996 | 122.7631 | 122.0993 | -0.34332 | 121.7102 | 121.4996 | 122.0993 | 122.0444 | 122.7631 | -1.5335 | -123.0515
3925.9219 | 122.8088 | -121.8475 | 0.83771 | 0.22537 | -0.00061524 | -0.011286 | 0.022913 | -0.001553 | 0.0016299 | 0.0081113 | -0.37994 | -0.17853 | -0.68207 | 0.54016 | 0.1831 | 0.25177 | 0.07782 | 0.27466 | 0.88348 | -122.2046 | 121.1655 | -1.0162 | 121.4676 | 122.3877 | -0.6546 | -0.35706 | 0.045776 | 0.30212 | 121.9254 | 122.1222 | 122.0306 | 121.669 | 121.4676 | 122.731 | 122.0993 | -0.35706 | 121.669 | 121.4676 | 122.0993 | 122.0306 | 122.731 | -1.5198 | -123.0423
3926.9062 | 122.7768 | -121.8613 | 0.85144 | -0.20187 | -0.001256 | -0.0085086 | 0.024836 | -0.0017666 | -0.0013609 | 0.0078977 | -0.31586 | -0.082397 | -0.6134 | 0.56763 | 0.19226 | 0.25177 | 0.17395 | 0.29755 | 0.88806 | -122.2183 | 121.2479 | -0.93384 | 121.5454 | 122.4289 | -0.65918 | -0.35706 | 0.036622 | 0.29755 | 122.0352 | 122.1588 | 122.0535 | 121.7789 | 121.5454 | 122.7493 | 122.113 | -0.35706 | 121.7789 | 121.5454 | 122.113 | 122.0535 | 122.7493 | -1.4648 | -123.0698
3927.9062 | 122.7676 | -121.843 | 0.90637 | -0.2095 | -0.00040164 | -0.0059452 | 0.022913 | -0.0034756 | -0.0028561 | 0.0083249 | -0.37079 | -0.12817 | -0.67291 | 0.60425 | 0.19684 | 0.2655 | 0.20142 | 0.31586 | 0.92468 | -122.1954 | 121.17 | -1.0345 | 121.4722 | 122.4472 | -0.70953 | -0.35248 | 0.018311 | 0.30212 | 122.0444 | 122.1588 | 122.0398 | 121.7148 | 121.4722 | 122.7676 | 122.1085 | -0.35248 | 121.7148 | 121.4722 | 122.1085 | 122.0398 | 122.7676 | -1.5793 | -123.1018
3928.9062 | 122.7539 | -121.8475 | 0.88806 | -0.22476 | -0.00061524 | -0.0097904 | 0.022272 | -0.0028348 | -0.00029266 | 0.0096067 | -0.41199 | -0.11444 | -0.68207 | 0.56763 | 0.17395 | 0.23346 | 0.24261 | 0.25635 | 0.94299 | -122.1725 | 121.1655 | -1.0025 | 121.4355 | 122.4152 | -0.71411 | -0.32501 | 0.054931 | 0.27008 | 122.0901 | 122.1039 | 122.0215 | 121.7331 | 121.4355 | 122.7905 | 122.081 | -0.32501 | 121.7331 | 121.4355 | 122.081 | 122.0215 | 122.7905 | -1.5701 | -123.0606
3929.9062 | 122.7722 | -121.8109 | 0.92926 | -0.18662 | -0.00040164 | -0.010004 | 0.026758 | -0.0041166 | -0.0017881 | 0.0093931 | -0.37079 | -0.11902 | -0.66376 | 0.5722 | 0.19226 | 0.24719 | 0.22888 | 0.27466 | 0.95673 | -122.1725 | 121.1472 | -1.0483 | 121.4401 | 122.3831 | -0.737 | -0.36163 | 0.027466 | 0.29297 | 122.0398 | 122.0856 | 122.0032 | 121.6919 | 121.4401 | 122.7676 | 122.0581 | -0.36163 | 121.6919 | 121.4401 | 122.0581 | 122.0032 | 122.7676 | -1.593 | -123.1018
3930.9062 | 122.7951 | -121.7972 | 0.89722 | -0.17899 | 0.00066656 | -0.0055178 | 0.026545 | -0.00048499 | -0.0030697 | 0.011102 | -0.28839 | -0.12817 | -0.65002 | 0.6134 | 0.20599 | 0.27466 | 0.16022 | 0.29755 | 0.94299 | -122.1634 | 121.1472 | -1.0254 | 121.5088 | 122.4106 | -0.69122 | -0.36621 | 0.045776 | 0.36163 | 121.9574 | 122.0947 | 122.0032 | 121.669 | 121.5088 | 122.7402 | 122.0718 | -0.36621 | 121.669 | 121.5088 | 122.0718 | 122.0032 | 122.7402 | -1.5472 | -123.0606
3931.9062 | 122.7722 | -121.8475 | 0.89264 | -0.14084 | -0.0021106 | -0.006586 | 0.026972 | -0.001553 | -0.0028561 | 0.0096067 | -0.32959 | -0.14191 | -0.64087 | 0.60883 | 0.20142 | 0.27466 | 0.17853 | 0.28839 | 0.93842 | -122.1542 | 121.2067 | -1.0345 | 121.5179 | 122.4564 | -0.69122 | -0.3067 | 0.045777 | 0.31128 | 122.0261 | 122.1359 | 122.0489 | 121.7056 | 121.5179 | 122.7859 | 122.1222 | -0.3067 | 121.7056 | 121.5179 | 122.1222 | 122.0489 | 122.7859 | -1.5335 | -123.0469
3932.9062 | 122.7676 | -121.8246 | 0.89722 | -0.12558 | -0.0021106 | -0.0091494 | 0.026117 | -0.002194 | -0.0041379 | 0.0098203 | -0.34332 | -0.11902 | -0.65002 | 0.60883 | 0.20599 | 0.27466 | 0.17395 | 0.29755 | 0.92926 | -122.1771 | 121.1746 | -1.0162 | 121.4813 | 122.4335 | -0.69122 | -0.35248 | 0.032043 | 0.3067 | 121.9986 | 122.1222 | 122.0306 | 121.7056 | 121.4813 | 122.7539 | 122.0993 | -0.35248 | 121.7056 | 121.4813 | 122.0993 | 122.0306 | 122.7539 | -1.5472 | -123.0743
3933.9062 | 122.7859 | -121.8018 | 0.91553 | -0.2095 | -0.0014696 | -0.010218 | 0.026758 | -0.00048499 | -0.0026425 | 0.010675 | -0.3479 | -0.10529 | -0.65002 | 0.60425 | 0.21057 | 0.28381 | 0.1831 | 0.28381 | 0.94757 | -122.1542 | 121.1517 | -1.0208 | 121.4539 | 122.406 | -0.70496 | -0.35248 | 0.032044 | 0.30212 | 121.9849 | 122.0856 | 122.0123 | 121.6965 | 121.4539 | 122.7493 | 122.0856 | -0.35248 | 121.6965 | 121.4539 | 122.0856 | 122.0123 | 122.7493 | -1.5656 | -123.0698
3934.9062 | 122.8592 | -121.756 | 0.8606 | 0.18723 | 0.0010938 | -0.011927 | 0.021631 | -0.0026212 | -0.0022153 | 0.010461 | -0.29297 | -0.17395 | -0.62714 | 0.65918 | 0.27924 | 0.37537 | -0.004578 | 0.35248 | 0.89264 | -122.1542 | 121.1288 | -1.0345 | 121.463 | 122.4152 | -0.58136 | -0.39825 | 0.032043 | 0.33417 | 121.7514 | 122.1085 | 122.0352 | 121.582 | 121.463 | 122.6486 | 122.1313 | -0.39825 | 121.582 | 121.463 | 122.1313 | 122.0352 | 122.6486 | -1.4877 | -123.0148
3935.9062 | 122.7173 | -121.8155 | 0.91553 | 0.072784 | 2.5564e-05 | -0.010218 | 0.027186 | -0.0013394 | -0.0011471 | 0.0091795 | -0.39825 | -0.15106 | -0.65918 | 0.53558 | 0.13733 | 0.19684 | 0.21515 | 0.18768 | 0.94299 | -122.1863 | 121.1563 | -1.0666 | 121.4172 | 122.3511 | -0.7782 | -0.37079 | 0.027466 | 0.26093 | 122.0306 | 122.0032 | 121.9528 | 121.6644 | 121.4172 | 122.7585 | 122.0123 | -0.37079 | 121.6644 | 121.4172 | 122.0123 | 121.9528 | 122.7585 | -1.5747 | -123.1018
3936.9062 | 122.7448 | -121.8246 | 0.90179 | -0.2095 | 0.00088016 | -0.0087222 | 0.022913 | -0.0034756 | -0.0020017 | 0.0078977 | -0.3891 | -0.13275 | -0.66834 | 0.56763 | 0.17853 | 0.23346 | 0.23804 | 0.26093 | 0.94757 | -122.1634 | 121.1563 | -1.0345 | 121.4355 | 122.3923 | -0.72327 | -0.33875 | 0.045777 | 0.27924 | 122.0627 | 122.0856 | 122.0032 | 121.6919 | 121.4355 | 122.7722 | 122.0581 | -0.33875 | 121.6919 | 121.4355 | 122.0581 | 122.0032 | 122.7722 | -1.5701 | -123.0652
3937.9062 | 122.7814 | -121.843 | 0.88806 | -0.2095 | -0.0021106 | -0.0059452 | 0.024836 | -0.0013394 | -0.0024289 | 0.0096067 | -0.37079 | -0.13733 | -0.67291 | 0.60425 | 0.20599 | 0.27008 | 0.21057 | 0.28381 | 0.9201 | -122.1634 | 121.17 | -1.0254 | 121.4722 | 122.4472 | -0.68207 | -0.32043 | 0.032043 | 0.30212 | 122.0535 | 122.1268 | 122.049 | 121.7056 | 121.4722 | 122.7631 | 122.113 | -0.32043 | 121.7056 | 121.4722 | 122.113 | 122.049 | 122.7631 | -1.561 | -123.0515
3938.9062 | 122.7448 | -121.8246 | 0.89264 | -0.1561 | -0.00040164 | -0.0063724 | 0.026331 | -0.0024076 | -0.00050626 | 0.0089657 | -0.25635 | -0.009155 | -0.55847 | 0.57678 | 0.20599 | 0.2655 | 0.2243 | 0.26093 | 0.93842 | -122.1771 | 121.2662 | -0.90179 | 121.5683 | 122.4014 | -0.68664 | -0.35248 | 0.045777 | 0.30212 | 122.049 | 122.0856 | 122.0306 | 121.8155 | 121.5683 | 122.7631 | 122.0901 | -0.35248 | 121.8155 | 121.5683 | 122.0901 | 122.0306 | 122.7631 | -1.4511 | -123.0698
3939.9219 | 122.7585 | -121.8521 | 0.87891 | 0.18723 | -0.00061524 | -0.0035952 | 0.026545 | -0.00091219 | -0.0011471 | 0.011102 | -0.38452 | -0.13275 | -0.66834 | 0.54474 | 0.16937 | 0.23804 | 0.16479 | 0.21057 | 0.92468 | -122.2046 | 121.1838 | -1.0117 | 121.4676 | 122.3969 | -0.70953 | -0.35248 | 0.045777 | 0.28381 | 122.0169 | 122.0627 | 122.0215 | 121.7194 | 121.4676 | 122.7768 | 122.0901 | -0.35248 | 121.7194 | 121.4676 | 122.0901 | 122.0215 | 122.7768 | -1.5472 | -123.0835
3940.9062 | 122.8226 | -121.7926 | 0.88348 | 0.22537 | -0.001256 | -0.0080814 | 0.023981 | -0.0024076 | -7.9062e-05 | 0.0078977 | -0.33417 | -0.15564 | -0.64545 | 0.64087 | 0.24719 | 0.33417 | 0.068665 | 0.31586 | 0.89722 | -122.1542 | 121.1472 | -1.0391 | 121.4584 | 122.4335 | -0.63629 | -0.36163 | 0.013733 | 0.31128 | 121.8613 | 122.1085 | 122.0398 | 121.637 | 121.4584 | 122.6898 | 122.1268 | -0.36163 | 121.637 | 121.4584 | 122.1268 | 122.0398 | 122.6898 | -1.5289 | -123.0377
3941.9062 | 122.7264 | -121.8018 | 0.92926 | -0.22476 | -0.0025378 | -0.010004 | 0.023554 | -0.004971 | -0.0022153 | 0.0085385 | -0.25177 | 0.032043 | -0.50812 | 0.59509 | 0.18768 | 0.24261 | 0.25635 | 0.25177 | 0.95673 | -122.1542 | 121.2936 | -0.89722 | 121.55 | 122.3969 | -0.74158 | -0.35248 | 0.027466 | 0.25635 | 122.0581 | 122.0535 | 121.9894 | 121.8338 | 121.55 | 122.7585 | 122.0444 | -0.35248 | 121.8338 | 121.55 | 122.0444 | 121.9894 | 122.7585 | -1.4374 | -123.0835
3942.9062 | 122.7859 | -121.788 | 0.95215 | -0.26291 | -0.0042468 | -0.011927 | 0.022059 | -0.003903 | -0.0013609 | 0.0078977 | -0.31586 | -0.09613 | -0.59967 | 0.62256 | 0.20142 | 0.27466 | 0.19684 | 0.28381 | 0.97046 | -122.1359 | 121.1884 | -1.0483 | 121.4722 | 122.4106 | -0.75073 | -0.3479 | 0.018311 | 0.28381 | 121.9849 | 122.0718 | 121.9894 | 121.6919 | 121.4722 | 122.7585 | 122.0627 | -0.3479 | 121.6919 | 121.4722 | 122.0627 | 121.9894 | 122.7585 | -1.5518 | -123.0881
3943.9062 | 122.7539 | -121.7743 | 0.95215 | -0.23239 | -0.001897 | -0.0097904 | 0.023127 | -0.0053982 | -0.00050626 | 0.0087521 | -0.27466 | -0.009155 | -0.52185 | 0.59509 | 0.16479 | 0.24261 | 0.24261 | 0.25635 | 0.97961 | -122.1451 | 121.2524 | -0.9613 | 121.4996 | 122.3694 | -0.78735 | -0.37079 | 0.027466 | 0.24719 | 122.0169 | 122.0306 | 121.9391 | 121.7651 | 121.4996 | 122.7539 | 122.0169 | -0.37079 | 121.7651 | 121.4996 | 122.0169 | 121.9391 | 122.7539 | -1.474 | -123.0972
3944.9219 | 122.7631 | -121.8109 | 0.90637 | 0.19485 | -0.002965 | -0.0080814 | 0.028467 | -0.0024076 | 0.00034814 | 0.0074705 | -0.29297 | -0.050354 | -0.58136 | 0.58136 | 0.16937 | 0.26093 | 0.13733 | 0.2243 | 0.97046 | -122.1313 | 121.2296 | -0.95673 | 121.5179 | 122.3923 | -0.737 | -0.32044 | 0.064087 | 0.28839 | 121.9482 | 122.0352 | 121.9803 | 121.7606 | 121.5179 | 122.7814 | 122.0718 | -0.32044 | 121.7606 | 121.5179 | 122.0718 | 121.9803 | 122.7814 | -1.4877 | -123.0377
3945.9062 | 122.7402 | -121.7743 | 0.98419 | 0.034637 | 0.0017346 | -0.0053042 | 0.028681 | -0.0034756 | -0.0015745 | 0.0083249 | -0.30212 | -0.09613 | -0.63171 | 0.62714 | 0.15564 | 0.23346 | 0.1831 | 0.23346 | 0.99792 | -122.1268 | 121.1426 | -1.0803 | 121.4722 | 122.4014 | -0.82855 | -0.35248 | 0.013733 | 0.32959 | 121.9574 | 122.0078 | 121.9299 | 121.6782 | 121.4722 | 122.7722 | 122.0078 | -0.35248 | 121.6782 | 121.4722 | 122.0078 | 121.9299 | 122.7722 | -1.6159 | -123.111
3946.9062 | 122.731 | -121.7468 | 0.98877 | -0.19424 | -0.0023242 | -0.007654 | 0.022486 | -0.0034756 | 0.00013454 | 0.0083249 | -0.33875 | -0.068665 | -0.59509 | 0.62256 | 0.16937 | 0.22888 | 0.23346 | 0.2655 | 1.0208 | -122.0764 | 121.1517 | -1.0574 | 121.4081 | 122.3694 | -0.8194 | -0.32959 | 0.032043 | 0.25635 | 121.9803 | 122.0123 | 121.9162 | 121.6782 | 121.4081 | 122.7676 | 121.9757 | -0.32959 | 121.6782 | 121.4081 | 121.9757 | 121.9162 | 122.7676 | -1.5839 | -123.0652
3947.9062 | 122.7448 | -121.7377 | 0.98419 | -0.16373 | -0.00040164 | -0.011713 | 0.022272 | -0.0041166 | -0.0026425 | 0.0085385 | -0.33417 | -0.041199 | -0.58594 | 0.62714 | 0.17395 | 0.23804 | 0.25635 | 0.25177 | 1.0254 | -122.0993 | 121.1517 | -1.0254 | 121.4035 | 122.3648 | -0.81024 | -0.36163 | 0.041199 | 0.25177 | 121.994 | 121.9894 | 121.9116 | 121.6965 | 121.4035 | 122.7631 | 121.9757 | -0.36163 | 121.6965 | 121.4035 | 121.9757 | 121.9116 | 122.7631 | -1.5701 | -123.0835
3948.9062 | 122.7356 | -121.7194 | 1.0254 | -0.17136 | -0.0033922 | -0.010858 | 0.020777 | -0.0053982 | 0.00013454 | 0.0093931 | -0.36163 | -0.10071 | -0.60883 | 0.6546 | 0.16022 | 0.25177 | 0.23804 | 0.25177 | 1.0757 | -122.0535 | 121.1105 | -1.1261 | 121.3577 | 122.374 | -0.86517 | -0.33417 | 0.050354 | 0.24719 | 121.9574 | 121.9711 | 121.8796 | 121.6187 | 121.3577 | 122.7951 | 121.9711 | -0.33417 | 121.6187 | 121.3577 | 121.9711 | 121.8796 | 122.7951 | -1.6342 | -123.0789
3949.9062 | 122.818 | -121.6827 | 1.0162 | -0.20187 | -0.003606 | -0.0095766 | 0.020136 | -0.003903 | -0.0011471 | 0.0098203 | -0.27924 | -0.13733 | -0.58136 | 0.78278 | 0.24719 | 0.35706 | 0.1236 | 0.36163 | 1.0483 | -121.9666 | 121.1014 | -1.1536 | 121.4035 | 122.4655 | -0.76904 | -0.28381 | 0.032044 | 0.30212 | 121.8063 | 122.0444 | 121.9299 | 121.5454 | 121.4035 | 122.731 | 122.0398 | -0.28381 | 121.5454 | 121.4035 | 122.0398 | 121.9299 | 122.731 | -1.5976 | -122.9828
3950.9062 | 122.7585 | -121.7239 | 1.0666 | -0.27054 | -0.0025378 | -0.010218 | 0.022272 | -0.0062528 | -0.0032835 | 0.0091795 | -0.3067 | -0.14191 | -0.6134 | 0.71869 | 0.19684 | 0.2655 | 0.21973 | 0.29755 | 1.0666 | -122.0078 | 121.1105 | -1.2085 | 121.4172 | 122.4426 | -0.86975 | -0.28381 | 0 | 0.3067 | 121.9437 | 122.0215 | 121.9208 | 121.582 | 121.4172 | 122.7905 | 121.9894 | -0.28381 | 121.582 | 121.4172 | 121.9894 | 121.9208 | 122.7905 | -1.68 | -123.0743
3951.9062 | 122.7448 | -121.7148 | 1.0574 | -0.25528 | -0.0023242 | -0.015558 | 0.023981 | -0.0051846 | -0.00071986 | 0.0089657 | -0.37537 | -0.10986 | -0.65918 | 0.68207 | 0.16937 | 0.23346 | 0.25177 | 0.2655 | 1.0803 | -122.0398 | 121.0556 | -1.1673 | 121.3394 | 122.3969 | -0.88806 | -0.32501 | 0.022888 | 0.28381 | 121.9666 | 121.9803 | 121.8842 | 121.6049 | 121.3394 | 122.7951 | 121.9482 | -0.32501 | 121.6049 | 121.3394 | 121.9482 | 121.8842 | 122.7951 | -1.7166 | -123.0972
3952.9062 | 122.7356 | -121.7056 | 1.0757 | -0.23239 | -0.00082884 | -0.011713 | 0.023554 | -0.00668 | -0.00093346 | 0.0096067 | -0.39368 | -0.13275 | -0.65002 | 0.6958 | 0.17395 | 0.24719 | 0.24261 | 0.26093 | 1.0712 | -122.0306 | 121.0556 | -1.2085 | 121.312 | 122.4014 | -0.90179 | -0.32501 | -0.004578 | 0.25635 | 121.9482 | 121.9666 | 121.8796 | 121.5729 | 121.312 | 122.7768 | 121.9528 | -0.32501 | 121.5729 | 121.312 | 121.9528 | 121.8796 | 122.7768 | -1.7258 | -123.1064
3953.9062 | 122.7539 | -121.6599 | 1.0941 | -0.2858 | -0.0027514 | -0.01214 | 0.023554 | -0.0036892 | -0.00050626 | 0.0083249 | -0.36621 | -0.11444 | -0.62714 | 0.72327 | 0.1831 | 0.23804 | 0.22888 | 0.27008 | 1.0941 | -121.994 | 121.0327 | -1.2085 | 121.2936 | 122.3831 | -0.91095 | -0.33417 | 0 | 0.26093 | 121.8887 | 121.9299 | 121.843 | 121.5454 | 121.2936 | 122.7539 | 121.8979 | -0.33417 | 121.5454 | 121.2936 | 121.8979 | 121.843 | 122.7539 | -1.7212 | -123.0881
3954.9062 | 122.7448 | -121.6507 | 1.0803 | -0.22476 | -0.0033922 | -0.011072 | 0.023768 | -0.00668 | -0.0032835 | 0.011102 | -0.34332 | -0.11902 | -0.61798 | 0.73242 | 0.20142 | 0.26093 | 0.2243 | 0.27466 | 1.0941 | -121.962 | 121.0327 | -1.1993 | 121.3074 | 122.3831 | -0.87891 | -0.31128 | 0.013733 | 0.27466 | 121.875 | 121.9254 | 121.8521 | 121.5317 | 121.3074 | 122.7448 | 121.9116 | -0.31128 | 121.5317 | 121.3074 | 121.9116 | 121.8521 | 122.7448 | -1.6983 | -123.0423
3955.9062 | 122.7722 | -121.6736 | 1.0666 | -0.026398 | -0.00040164 | -0.0074404 | 0.028467 | -0.003903 | -0.0013609 | 0.0093931 | -0.2655 | -0.12817 | -0.61798 | 0.76904 | 0.20599 | 0.28839 | 0.16022 | 0.27008 | 1.1124 | -122.0123 | 121.0556 | -1.1948 | 121.4081 | 122.4426 | -0.86059 | -0.33874 | 0.045777 | 0.35248 | 121.8338 | 121.9437 | 121.8796 | 121.5454 | 121.4081 | 122.7859 | 121.962 | -0.33874 | 121.5454 | 121.4081 | 121.962 | 121.8796 | 122.7859 | -1.6846 | -123.0789
3956.9062 | 122.7768 | -121.6278 | 1.1124 | -0.27054 | -0.0010424 | -0.0089358 | 0.020777 | -0.0045438 | -0.0028561 | 0.0081113 | -0.32501 | -0.13733 | -0.6134 | 0.76904 | 0.23346 | 0.28839 | 0.17395 | 0.27466 | 1.1398 | -121.9482 | 121.0144 | -1.2497 | 121.3028 | 122.3969 | -0.87891 | -0.32043 | 0.027466 | 0.28839 | 121.8018 | 121.9025 | 121.8613 | 121.4905 | 121.3028 | 122.7676 | 121.9162 | -0.32043 | 121.4905 | 121.3028 | 121.9162 | 121.8613 | 122.7676 | -1.7258 | -123.0606
3957.9062 | 122.7768 | -121.6415 | 1.0803 | -0.24002 | -0.0055286 | -0.014704 | 0.022699 | -0.0051846 | -0.0028561 | 0.0089657 | -0.30212 | -0.1236 | -0.60883 | 0.78278 | 0.21973 | 0.29755 | 0.18768 | 0.28381 | 1.1124 | -121.9574 | 121.0327 | -1.2039 | 121.3394 | 122.4243 | -0.86059 | -0.31586 | 0.032044 | 0.3067 | 121.8292 | 121.9254 | 121.8613 | 121.5179 | 121.3394 | 122.7539 | 121.9391 | -0.31586 | 121.5179 | 121.3394 | 121.9391 | 121.8613 | 122.7539 | -1.6891 | -123.0377
3958.9062 | 122.7402 | -121.6873 | 1.0666 | -0.20187 | -0.0016834 | -0.011286 | 0.02334 | -0.00668 | -0.00029266 | 0.0083249 | -0.37079 | -0.09613 | -0.62256 | 0.73242 | 0.18768 | 0.25635 | 0.2243 | 0.25635 | 1.1032 | -122.0215 | 121.0648 | -1.1627 | 121.3165 | 122.4197 | -0.87891 | -0.33417 | 0.036621 | 0.25177 | 121.9116 | 121.9437 | 121.875 | 121.5912 | 121.3165 | 122.7905 | 121.9437 | -0.33417 | 121.5912 | 121.3165 | 121.9437 | 121.875 | 122.7905 | -1.6891 | -123.0881
3959.9062 | 122.731 | -121.6507 | 1.0666 | -0.19424 | -0.001897 | -0.013208 | 0.023768 | -0.004971 | -0.0017881 | 0.0087521 | -0.36163 | -0.091553 | -0.61798 | 0.73242 | 0.1831 | 0.25635 | 0.23804 | 0.25177 | 1.1215 | -122.0032 | 121.0327 | -1.1581 | 121.2891 | 122.3831 | -0.88348 | -0.35248 | 0.054932 | 0.25635 | 121.8887 | 121.9025 | 121.8338 | 121.5591 | 121.2891 | 122.7722 | 121.907 | -0.35248 | 121.5591 | 121.2891 | 121.907 | 121.8338 | 122.7722 | -1.6846 | -123.0698
3960.9062 | 122.7631 | -121.6232 | 1.0895 | 0.0041197 | -0.0010424 | -0.010004 | 0.029322 | -0.0043302 | -0.0032835 | 0.010675 | -0.23804 | -0.059509 | -0.55847 | 0.78735 | 0.1831 | 0.27924 | 0.15106 | 0.24719 | 1.1215 | -121.9711 | 121.0648 | -1.149 | 121.3852 | 122.4106 | -0.90637 | -0.3479 | 0.032043 | 0.32043 | 121.7743 | 121.8704 | 121.8063 | 121.5637 | 121.3852 | 122.7448 | 121.9025 | -0.3479 | 121.5637 | 121.3852 | 121.9025 | 121.8063 | 122.7448 | -1.6479 | -123.0606
3961.9062 | 122.731 | -121.6553 | 1.1169 | -0.26291 | -0.0023242 | -0.0070132 | 0.023127 | -0.0051846 | -0.0017881 | 0.0098203 | -0.36163 | -0.07782 | -0.60883 | 0.76446 | 0.20142 | 0.24719 | 0.23346 | 0.24719 | 1.1398 | -121.9574 | 121.0464 | -1.1948 | 121.2936 | 122.4197 | -0.91553 | -0.30212 | 0.022889 | 0.24719 | 121.8887 | 121.9025 | 121.8567 | 121.5775 | 121.2936 | 122.7951 | 121.9025 | -0.30212 | 121.5775 | 121.2936 | 121.9025 | 121.8567 | 122.7951 | -1.7258 | -123.0743
3962.9062 | 122.7448 | -121.6415 | 1.1307 | -0.2095 | -0.0031786 | -0.0089358 | 0.024195 | -0.0043302 | -0.0030697 | 0.0089657 | -0.36621 | -0.073242 | -0.60883 | 0.75531 | 0.18768 | 0.24261 | 0.22888 | 0.26093 | 1.1673 | -121.9482 | 121.0327 | -1.2039 | 121.2753 | 122.3969 | -0.94299 | -0.3067 | 0.036621 | 0.24261 | 121.8704 | 121.9025 | 121.8292 | 121.5683 | 121.2753 | 122.8088 | 121.8842 | -0.3067 | 121.5683 | 121.2753 | 121.8842 | 121.8292 | 122.8088 | -1.7395 | -123.0789
3963.9062 | 122.8088 | -121.6095 | 1.0757 | -0.27054 | -0.0040332 | -0.008295 | 0.02334 | -0.00668 | -0.0011471 | 0.0074705 | -0.28381 | -0.09613 | -0.57678 | 0.81024 | 0.23346 | 0.31586 | 0.15106 | 0.32959 | 1.1353 | -121.9345 | 121.0327 | -1.1719 | 121.3257 | 122.4197 | -0.84229 | -0.32501 | 0.059509 | 0.29297 | 121.7606 | 121.9391 | 121.843 | 121.5134 | 121.3257 | 122.7448 | 121.9254 | -0.32501 | 121.5134 | 121.3257 | 121.9254 | 121.843 | 122.7448 | -1.6525 | -123.0103
3964.9062 | 122.7631 | -121.6415 | 1.0757 | -0.29343 | -0.0027514 | -0.010218 | 0.024408 | -0.0043302 | 0.00013454 | 0.0083249 | -0.34332 | -0.064087 | -0.58594 | 0.75531 | 0.17395 | 0.25177 | 0.24719 | 0.24719 | 1.1353 | -122.0078 | 121.0556 | -1.1398 | 121.2982 | 122.3969 | -0.90179 | -0.36621 | 0.059509 | 0.24261 | 121.8887 | 121.8887 | 121.8155 | 121.5775 | 121.2982 | 122.7768 | 121.8933 | -0.36621 | 121.5775 | 121.2982 | 121.8933 | 121.8155 | 122.7768 | -1.6617 | -123.0835
3965.9062 | 122.7356 | -121.669 | 1.0849 | 0.057526 | 0.00088016 | -0.0057314 | 0.026972 | -0.0043302 | -0.0026425 | 0.0091795 | -0.31128 | -0.068665 | -0.6134 | 0.74158 | 0.14648 | 0.23804 | 0.21057 | 0.21973 | 1.1307 | -121.9757 | 121.0556 | -1.1536 | 121.3577 | 122.4106 | -0.93842 | -0.3067 | 0.045776 | 0.30212 | 121.8796 | 121.8887 | 121.8155 | 121.6003 | 121.3577 | 122.7997 | 121.907 | -0.3067 | 121.6003 | 121.3577 | 121.907 | 121.8155 | 122.7997 | -1.6983 | -123.0606
3966.9062 | 122.7631 | -121.6461 | 1.0803 | -0.20187 | -0.0021106 | -0.012781 | 0.02569 | -0.002194 | -0.0024289 | 0.0081113 | -0.35706 | -0.07782 | -0.6134 | 0.75073 | 0.18768 | 0.24719 | 0.24719 | 0.24719 | 1.1307 | -121.994 | 121.0327 | -1.1581 | 121.2891 | 122.3969 | -0.89264 | -0.3479 | 0.050354 | 0.25635 | 121.8933 | 121.8933 | 121.8338 | 121.5683 | 121.2891 | 122.7768 | 121.8933 | -0.3479 | 121.5683 | 121.2891 | 121.8933 | 121.8338 | 122.7768 | -1.6937 | -123.0743
3967.9062 | 122.7448 | -121.6827 | 1.0757 | -0.19424 | -0.00018804 | -0.0050906 | 0.025049 | -0.0028348 | -0.0043515 | 0.0096067 | -0.35706 | -0.068665 | -0.59967 | 0.72327 | 0.18768 | 0.25177 | 0.25635 | 0.23804 | 1.1124 | -122.0032 | 121.0831 | -1.1444 | 121.3257 | 122.406 | -0.88806 | -0.32044 | 0.036621 | 0.24261 | 121.9391 | 121.9208 | 121.8704 | 121.6141 | 121.3257 | 122.7951 | 121.9345 | -0.32044 | 121.6141 | 121.3257 | 121.9345 | 121.8704 | 122.7951 | -1.6754 | -123.0789
3968.9062 | 122.7585 | -121.6873 | 1.0986 | -0.21713 | -0.00082884 | -0.0091494 | 0.025477 | -0.003262 | -0.0015745 | 0.0083249 | -0.35248 | -0.086975 | -0.6134 | 0.74616 | 0.19226 | 0.25177 | 0.24719 | 0.25635 | 1.1444 | -121.994 | 121.0739 | -1.1856 | 121.3348 | 122.4335 | -0.90637 | -0.3067 | 0.045776 | 0.26093 | 121.9345 | 121.9437 | 121.8796 | 121.6003 | 121.3348 | 122.8317 | 121.9391 | -0.3067 | 121.6003 | 121.3348 | 121.9391 | 121.8796 | 122.8317 | -1.712 | -123.0927
3969.9062 | 122.7585 | -121.701 | 1.0666 | -0.22476 | -0.0016834 | -0.011286 | 0.023768 | -0.0053982 | -0.0037107 | 0.011102 | -0.3067 | -0.022888 | -0.56305 | 0.71869 | 0.17853 | 0.25635 | 0.25177 | 0.23804 | 1.0986 | -122.0123 | 121.138 | -1.0895 | 121.3943 | 122.4197 | -0.88806 | -0.31128 | 0.032044 | 0.25635 | 121.9528 | 121.9391 | 121.8796 | 121.6782 | 121.3943 | 122.7997 | 121.9574 | -0.31128 | 121.6782 | 121.3943 | 121.9574 | 121.8796 | 122.7997 | -1.6296 | -123.0789
3970.9062 | 122.7905 | -121.6827 | 1.062 | -0.13321 | -0.0031786 | -0.0053042 | 0.027399 | -0.004971 | -7.9062e-05 | 0.0087521 | -0.30212 | -0.032043 | -0.55847 | 0.75073 | 0.21973 | 0.29297 | 0.21973 | 0.28381 | 1.0941 | -122.0261 | 121.1243 | -1.0941 | 121.3806 | 122.4335 | -0.84228 | -0.34332 | 0.032043 | 0.25635 | 121.9025 | 121.9666 | 121.9025 | 121.6507 | 121.3806 | 122.7768 | 121.9757 | -0.34332 | 121.6507 | 121.3806 | 121.9757 | 121.9025 | 122.7768 | -1.6205 | -123.0881
3971.9062 | 122.7631 | -121.669 | 1.0895 | -0.2095 | -0.00061524 | -0.009363 | 0.023554 | -0.0036892 | 0.00013454 | 0.0072569 | -0.28839 | -0.009155 | -0.55389 | 0.73242 | 0.17853 | 0.2655 | 0.25635 | 0.24719 | 1.1307 | -121.9986 | 121.1151 | -1.0986 | 121.3806 | 122.4014 | -0.91095 | -0.32959 | 0.041198 | 0.2655 | 121.9254 | 121.9162 | 121.8475 | 121.6599 | 121.3806 | 122.7997 | 121.9345 | -0.32959 | 121.6599 | 121.3806 | 121.9345 | 121.8475 | 122.7997 | -1.6434 | -123.0881
3972.9062 | 122.8043 | -121.6553 | 1.0666 | -0.12558 | -0.00061524 | -0.0080814 | 0.025049 | -0.0017666 | -0.0026425 | 0.010461 | -0.23804 | -0.009155 | -0.54016 | 0.75989 | 0.21515 | 0.30212 | 0.18768 | 0.27924 | 1.0986 | -121.994 | 121.1151 | -1.0757 | 121.4172 | 122.4152 | -0.85144 | -0.33875 | 0.032044 | 0.30212 | 121.843 | 121.9345 | 121.8704 | 121.6461 | 121.4172 | 122.7539 | 121.9574 | -0.33875 | 121.6461 | 121.4172 | 121.9574 | 121.8704 | 122.7539 | -1.6067 | -123.0606
3973.9062 | 122.7905 | -121.6461 | 1.0712 | -0.2095 | 0.00045296 | -0.0091494 | 0.026758 | -0.0026212 | -0.0032835 | 0.0057615 | -0.21515 | 0.027466 | -0.49896 | 0.77362 | 0.19684 | 0.31128 | 0.19684 | 0.28839 | 1.1215 | -121.9849 | 121.1472 | -1.0437 | 121.431 | 122.4197 | -0.87433 | -0.33875 | 0.050354 | 0.28381 | 121.843 | 121.9345 | 121.843 | 121.6736 | 121.431 | 122.7676 | 121.9574 | -0.33875 | 121.6736 | 121.431 | 121.9574 | 121.843 | 122.7676 | -1.5701 | -123.056
3974.9062 | 122.7951 | -121.669 | 1.0757 | -0.12558 | -0.00061524 | -0.0067996 | 0.023554 | -0.0028348 | -0.0017881 | 0.011316 | -0.21973 | 0.041199 | -0.50354 | 0.75531 | 0.2243 | 0.31128 | 0.21057 | 0.27466 | 1.1169 | -121.9894 | 121.1655 | -1.0345 | 121.4493 | 122.4243 | -0.85144 | -0.32044 | 0.041198 | 0.28381 | 121.8796 | 121.9437 | 121.8933 | 121.7102 | 121.4493 | 122.7859 | 121.9803 | -0.32044 | 121.7102 | 121.4493 | 121.9803 | 121.8933 | 122.7859 | -1.5793 | -123.0652
3975.9062 | 122.8729 | -121.6232 | 1.0529 | 0.25589 | -0.00018804 | -0.0074404 | 0.023554 | -5.7592e-05 | -7.9062e-05 | 0.010034 | -0.16022 | -0.068665 | -0.50812 | 0.83313 | 0.28839 | 0.42114 | 0.018311 | 0.33875 | 1.062 | -121.9666 | 121.1151 | -1.1215 | 121.463 | 122.4564 | -0.76446 | -0.34332 | 0.009156 | 0.3479 | 121.6415 | 121.962 | 121.9116 | 121.5546 | 121.463 | 122.6852 | 122.0444 | -0.34332 | 121.5546 | 121.463 | 122.0444 | 121.9116 | 122.6852 | -1.561 | -123.0194
3976.9062 | 122.7951 | -121.6415 | 1.0849 | -0.23239 | 0.00045296 | -0.0091494 | 0.025477 | -0.0024076 | -0.0015745 | 0.0089657 | -0.23346 | 0.009155 | -0.53558 | 0.76904 | 0.20599 | 0.29755 | 0.20142 | 0.28381 | 1.1261 | -122.0123 | 121.106 | -1.0757 | 121.4081 | 122.4106 | -0.87891 | -0.37079 | 0.041199 | 0.30212 | 121.843 | 121.9254 | 121.8475 | 121.6507 | 121.4081 | 122.7676 | 121.9391 | -0.37079 | 121.6507 | 121.4081 | 121.9391 | 121.8475 | 122.7676 | -1.6205 | -123.0972
3977.9062 | 122.7814 | -121.637 | 1.0849 | -0.1561 | -0.001256 | -0.0070132 | 0.026331 | -0.001553 | -0.0026425 | 0.0078977 | -0.24261 | -0.022888 | -0.52643 | 0.78278 | 0.22888 | 0.3067 | 0.21057 | 0.27466 | 1.1124 | -121.9757 | 121.1105 | -1.1078 | 121.3943 | 122.4197 | -0.85602 | -0.33875 | 0.027466 | 0.28381 | 121.8475 | 121.9116 | 121.8658 | 121.6141 | 121.3943 | 122.7493 | 121.9437 | -0.33875 | 121.6141 | 121.3943 | 121.9437 | 121.8658 | 122.7493 | -1.6113 | -123.0606
3978.9062 | 122.7814 | -121.6507 | 1.0803 | -0.17899 | -0.0033922 | -0.012995 | 0.024408 | -0.0041166 | -0.00071986 | 0.0093931 | -0.29755 | -0.050354 | -0.59509 | 0.78278 | 0.22888 | 0.29297 | 0.20599 | 0.28839 | 1.1215 | -121.9894 | 121.0556 | -1.1307 | 121.3531 | 122.4335 | -0.85144 | -0.33875 | 0.041199 | 0.29755 | 121.8567 | 121.9391 | 121.8796 | 121.6003 | 121.3531 | 122.7722 | 121.9437 | -0.33875 | 121.6003 | 121.3531 | 121.9437 | 121.8796 | 122.7722 | -1.6754 | -123.0698
3979.9062 | 122.7951 | -121.6049 | 1.1169 | -0.034027 | -0.001256 | -0.0061588 | 0.027613 | -0.00069859 | -0.0011471 | 0.0057615 | -0.24261 | -0.041199 | -0.55389 | 0.81024 | 0.21973 | 0.3067 | 0.17395 | 0.27466 | 1.1353 | -121.9757 | 121.051 | -1.1581 | 121.3623 | 122.4152 | -0.89722 | -0.37079 | 0.018311 | 0.31128 | 121.7789 | 121.8796 | 121.8246 | 121.5637 | 121.3623 | 122.7402 | 121.9116 | -0.37079 | 121.5637 | 121.3623 | 121.9116 | 121.8246 | 122.7402 | -1.6708 | -123.0927
3980.9062 | 122.7951 | -121.6232 | 1.0849 | 0.16434 | -0.001256 | -0.0085086 | 0.02569 | -0.0013394 | -0.0015745 | 0.011743 | -0.24261 | -0.013733 | -0.54932 | 0.75073 | 0.19226 | 0.28381 | 0.13733 | 0.23346 | 1.1124 | -121.962 | 121.0739 | -1.0986 | 121.3806 | 122.374 | -0.89264 | -0.33874 | 0.027466 | 0.3067 | 121.7606 | 121.8567 | 121.8155 | 121.6095 | 121.3806 | 122.7356 | 121.907 | -0.33874 | 121.6095 | 121.3806 | 121.907 | 121.8155 | 122.7356 | -1.6342 | -123.0469
3981.9062 | 122.7997 | -121.6415 | 1.1032 | -0.13321 | 0.0017346 | -0.0046634 | 0.026331 | -0.0011258 | 0.00013454 | 0.010461 | -0.24719 | -0.050354 | -0.57678 | 0.78735 | 0.21973 | 0.31586 | 0.17395 | 0.27008 | 1.1353 | -121.994 | 121.0648 | -1.1536 | 121.3943 | 122.4289 | -0.88348 | -0.35248 | 0.032044 | 0.32959 | 121.8155 | 121.9116 | 121.8613 | 121.5912 | 121.3943 | 122.7768 | 121.9574 | -0.35248 | 121.5912 | 121.3943 | 121.9574 | 121.8613 | 122.7768 | -1.68 | -123.0972
3982.9062 | 122.818 | -121.637 | 1.0895 | -0.034027 | 0.00023916 | -0.006586 | 0.027399 | -0.002194 | -7.9062e-05 | 0.0083249 | -0.24261 | -0.045776 | -0.5722 | 0.79651 | 0.21057 | 0.31128 | 0.16479 | 0.29297 | 1.1215 | -121.9894 | 121.0648 | -1.1353 | 121.3943 | 122.4335 | -0.87891 | -0.35248 | 0.032043 | 0.32959 | 121.8018 | 121.9299 | 121.8475 | 121.5912 | 121.3943 | 122.7585 | 121.9482 | -0.35248 | 121.5912 | 121.3943 | 121.9482 | 121.8475 | 122.7585 | -1.6617 | -123.0789
3983.9062 | 122.7859 | -121.6232 | 1.0941 | -0.10269 | -0.0014696 | -0.0042362 | 0.02569 | -0.0019802 | -0.0017881 | 0.010034 | -0.25177 | -0.073242 | -0.59509 | 0.78735 | 0.22888 | 0.31586 | 0.17395 | 0.28839 | 1.1169 | -121.9711 | 121.0281 | -1.1673 | 121.3715 | 122.4106 | -0.86517 | -0.3479 | 0.022888 | 0.34332 | 121.7972 | 121.9116 | 121.8521 | 121.55 | 121.3715 | 122.7402 | 121.9391 | -0.3479 | 121.55 | 121.3715 | 121.9391 | 121.8521 | 122.7402 | -1.6891 | -123.0652
3984.9062 | 122.7951 | -121.6553 | 1.0803 | -0.064545 | 0.00023916 | -0.010645 | 0.027186 | -0.00027139 | -0.0024289 | 0.011102 | -0.25635 | -0.082397 | -0.59509 | 0.78278 | 0.20599 | 0.32501 | 0.16937 | 0.27924 | 1.1169 | -121.9528 | 121.0602 | -1.1627 | 121.3989 | 122.438 | -0.87433 | -0.29755 | 0.036621 | 0.33874 | 121.8246 | 121.9345 | 121.8613 | 121.5729 | 121.3989 | 122.7722 | 121.9803 | -0.29755 | 121.5729 | 121.3989 | 121.9803 | 121.8613 | 122.7722 | -1.6754 | -123.0331
3985.9062 | 122.7814 | -121.6324 | 1.1032 | 0.17197 | -0.0021106 | -0.0063724 | 0.025904 | -0.00027139 | -0.0015745 | 0.012811 | -0.33417 | -0.09613 | -0.60883 | 0.75073 | 0.17395 | 0.27008 | 0.16479 | 0.21515 | 1.1353 | -121.9666 | 121.0236 | -1.1993 | 121.2982 | 122.3831 | -0.92926 | -0.33417 | 0.032044 | 0.27466 | 121.7972 | 121.8475 | 121.8063 | 121.5363 | 121.2982 | 122.7676 | 121.9025 | -0.33417 | 121.5363 | 121.2982 | 121.9025 | 121.8063 | 122.7676 | -1.712 | -123.0698
3986.9062 | 122.7859 | -121.5958 | 1.1124 | -0.049286 | 0.0013074 | -0.010431 | 0.027399 | -0.0024076 | -0.0030697 | 0.0087521 | -0.27466 | -0.07782 | -0.59967 | 0.81024 | 0.19684 | 0.3067 | 0.1831 | 0.27924 | 1.149 | -121.9666 | 120.9961 | -1.1902 | 121.3211 | 122.406 | -0.91553 | -0.37079 | 0.036621 | 0.32501 | 121.7789 | 121.875 | 121.7926 | 121.5179 | 121.3211 | 122.7448 | 121.9025 | -0.37079 | 121.5179 | 121.3211 | 121.9025 | 121.7926 | 122.7448 | -1.712 | -123.0789
3987.9062 | 122.7859 | -121.5958 | 1.1307 | -0.049286 | 0.0030164 | -0.0061588 | 0.025477 | -0.002194 | -7.9062e-05 | 0.0085385 | -0.27008 | -0.086975 | -0.59052 | 0.81024 | 0.21057 | 0.29297 | 0.17395 | 0.27008 | 1.1581 | -121.9299 | 121.0052 | -1.2177 | 121.3257 | 122.406 | -0.9201 | -0.33417 | 0.027466 | 0.32043 | 121.7697 | 121.8658 | 121.8063 | 121.5088 | 121.3257 | 122.7539 | 121.8887 | -0.33417 | 121.5088 | 121.3257 | 121.8887 | 121.8063 | 122.7539 | -1.7212 | -123.0606
3988.9062 | 122.7859 | -121.582 | 1.1307 | -0.049286 | -0.00061524 | -0.009363 | 0.025263 | -0.0030484 | -0.0026425 | 0.0091795 | -0.29297 | -0.07782 | -0.62256 | 0.82398 | 0.19226 | 0.3067 | 0.17395 | 0.27924 | 1.1627 | -121.9345 | 120.9595 | -1.2085 | 121.2891 | 122.406 | -0.93841 | -0.35248 | 0.032044 | 0.32959 | 121.756 | 121.8613 | 121.7743 | 121.5042 | 121.2891 | 122.7448 | 121.8887 | -0.35248 | 121.5042 | 121.2891 | 121.8887 | 121.7743 | 122.7448 | -1.7532 | -123.0652
3989.9062 | 122.7951 | -121.6095 | 1.1078 | -0.034027 | -0.0027514 | -0.010431 | 0.027186 | -0.0011258 | -0.00029266 | 0.0085385 | -0.24261 | -0.027466 | -0.55389 | 0.79193 | 0.21515 | 0.3067 | 0.16937 | 0.28381 | 1.1536 | -121.9849 | 121.0556 | -1.1353 | 121.3669 | 122.4014 | -0.89264 | -0.37537 | 0.045776 | 0.31128 | 121.7789 | 121.8933 | 121.8246 | 121.582 | 121.3669 | 122.7631 | 121.9162 | -0.37537 | 121.582 | 121.3669 | 121.9162 | 121.8246 | 122.7631 | -1.6617 | -123.0927
3990.9062 | 122.7951 | -121.5958 | 1.1353 | -0.17136 | -0.00040164 | -0.0038088 | 0.02569 | -5.7592e-05 | -0.0041379 | 0.0085385 | -0.32044 | -0.07782 | -0.61798 | 0.82398 | 0.21057 | 0.30212 | 0.19684 | 0.30212 | 1.1765 | -121.9345 | 120.9778 | -1.2131 | 121.2753 | 122.4197 | -0.92468 | -0.33875 | 0.041199 | 0.29755 | 121.7926 | 121.8979 | 121.8063 | 121.5179 | 121.2753 | 122.7722 | 121.8979 | -0.33875 | 121.5179 | 121.2753 | 121.8979 | 121.8063 | 122.7722 | -1.7532 | -123.0698
3991.9062 | 122.8043 | -121.6232 | 1.1169 | -0.11032 | -0.00040164 | -0.0057314 | 0.024622 | -0.0028348 | -0.00093346 | 0.010034 | -0.21515 | -0.018311 | -0.54932 | 0.81482 | 0.21057 | 0.3067 | 0.17395 | 0.27924 | 1.1673 | -121.9666 | 121.0739 | -1.1353 | 121.4081 | 122.438 | -0.90637 | -0.34332 | 0.050354 | 0.33417 | 121.7972 | 121.9025 | 121.8338 | 121.6049 | 121.4081 | 122.7905 | 121.9299 | -0.34332 | 121.6049 | 121.4081 | 121.9299 | 121.8338 | 122.7905 | -1.6663 | -123.0835
3992.9062 | 122.7997 | -121.6141 | 1.1078 | -0.056915 | -0.0010424 | -0.010645 | 0.026545 | 0.00015601 | -0.0024289 | 0.0078977 | -0.2243 | -0.027466 | -0.53558 | 0.80566 | 0.2243 | 0.3067 | 0.1831 | 0.29297 | 1.149 | -121.9666 | 121.0785 | -1.1353 | 121.3898 | 122.4197 | -0.88348 | -0.35248 | 0.041199 | 0.31128 | 121.7972 | 121.907 | 121.8384 | 121.5866 | 121.3898 | 122.7631 | 121.9208 | -0.35248 | 121.5866 | 121.3898 | 121.9208 | 121.8384 | 122.7631 | -1.6434 | -123.0743
3993.9062 | 122.7859 | -121.637 | 1.0941 | -0.041657 | 0.00023916 | -0.010431 | 0.028681 | -0.0026212 | -0.0024289 | 0.0081113 | -0.21057 | -0.045776 | -0.54474 | 0.79651 | 0.21515 | 0.30212 | 0.18768 | 0.27008 | 1.1398 | -121.9757 | 121.0922 | -1.1398 | 121.4264 | 122.4335 | -0.87891 | -0.33875 | 0.045777 | 0.33417 | 121.8246 | 121.907 | 121.8521 | 121.5912 | 121.4264 | 122.7768 | 121.9391 | -0.33875 | 121.5912 | 121.4264 | 121.9391 | 121.8521 | 122.7768 | -1.6388 | -123.0698
3994.9062 | 122.7905 | -121.6324 | 1.0895 | -0.026398 | 0.00023916 | -0.0070132 | 0.026331 | -0.0024076 | -0.0028561 | 0.0093931 | -0.2243 | -0.036621 | -0.54932 | 0.80109 | 0.19684 | 0.29755 | 0.17395 | 0.27008 | 1.1215 | -121.994 | 121.0831 | -1.1261 | 121.4081 | 122.4335 | -0.89264 | -0.36163 | 0.032043 | 0.32501 | 121.8063 | 121.9025 | 121.8292 | 121.5958 | 121.4081 | 122.7539 | 121.9299 | -0.36163 | 121.5958 | 121.4081 | 121.9299 | 121.8292 | 122.7539 | -1.6388 | -123.0835
3995.9062 | 122.8088 | -121.6095 | 1.0803 | 0.21011 | -0.0031786 | -0.009363 | 0.025049 | -0.0026212 | -0.0020017 | 0.010461 | -0.29297 | -0.059509 | -0.5722 | 0.75531 | 0.21057 | 0.31128 | 0.11444 | 0.26093 | 1.1353 | -121.962 | 121.0373 | -1.1398 | 121.3165 | 122.3648 | -0.86975 | -0.35248 | 0.054932 | 0.27924 | 121.7239 | 121.8704 | 121.8201 | 121.55 | 121.3165 | 122.7448 | 121.9208 | -0.35248 | 121.55 | 121.3165 | 121.9208 | 121.8201 | 122.7448 | -1.6525 | -123.0423
3996.9688 | 122.7814 | -121.6553 | 1.0986 | -0.16373 | -0.00018804 | -0.0072268 | 0.024622 | -0.0024076 | -0.00029266 | 0.0089657 | -0.29297 | -0.018311 | -0.54932 | 0.75073 | 0.20142 | 0.27924 | 0.23804 | 0.2655 | 1.1307 | -122.0123 | 121.106 | -1.1169 | 121.3623 | 122.406 | -0.89722 | -0.35706 | 0.032043 | 0.25635 | 121.8933 | 121.9208 | 121.8567 | 121.637 | 121.3623 | 122.7859 | 121.9345 | -0.35706 | 121.637 | 121.3623 | 121.9345 | 121.8567 | 122.7859 | -1.6479 | -123.111
3997.9062 | 122.7722 | -121.6553 | 1.0986 | -0.1561 | -0.00061524 | -0.0078678 | 0.025049 | -0.001553 | 0.00056194 | 0.0081113 | -0.25177 | -0.018311 | -0.5722 | 0.77362 | 0.21057 | 0.28381 | 0.20599 | 0.27924 | 1.1215 | -122.0032 | 121.0831 | -1.1169 | 121.4035 | 122.4289 | -0.88806 | -0.3479 | 0.022888 | 0.32043 | 121.8613 | 121.9345 | 121.8658 | 121.637 | 121.4035 | 122.7768 | 121.9391 | -0.3479 | 121.637 | 121.4035 | 121.9391 | 121.8658 | 122.7768 | -1.6708 | -123.1018
3998.9062 | 122.8088 | -121.6644 | 1.0895 | -0.1561 | -0.001256 | -0.0091494 | 0.026758 | -0.00048499 | -0.0039243 | 0.0098203 | -0.17853 | 0.009155 | -0.5127 | 0.79193 | 0.21515 | 0.31128 | 0.1831 | 0.29755 | 1.1169 | -122.0078 | 121.1517 | -1.0803 | 121.4859 | 122.4564 | -0.87433 | -0.34332 | 0.027465 | 0.33417 | 121.8475 | 121.962 | 121.8796 | 121.6736 | 121.4859 | 122.7814 | 121.9757 | -0.34332 | 121.6736 | 121.4859 | 121.9757 | 121.8796 | 122.7814 | -1.6022 | -123.0972
3999.9062 | 122.7951 | -121.6049 | 1.1215 | -0.13321 | 2.5564e-05 | -0.0070132 | 0.025263 | -0.00027139 | -0.0015745 | 0.01217 | -0.1831 | 0.004578 | -0.50354 | 0.81024 | 0.20142 | 0.30212 | 0.16022 | 0.27466 | 1.1536 | -121.9666 | 121.1014 | -1.1169 | 121.4218 | 122.4152 | -0.9201 | -0.36163 | 0.032043 | 0.32044 | 121.7651 | 121.8796 | 121.8063 | 121.6095 | 121.4218 | 122.7585 | 121.907 | -0.36163 | 121.6095 | 121.4218 | 121.907 | 121.8063 | 122.7585 | -1.6251 | -123.0881
4000.9062 | 122.8088 | -121.6003 | 1.149 | -0.1561 | 0.0013074 | -0.004877 | 0.025263 | -0.0019802 | -0.0030697 | 0.0083249 | -0.19226 | 0.004578 | -0.49439 | 0.82398 | 0.21515 | 0.31128 | 0.17395 | 0.27924 | 1.1627 | -121.9482 | 121.106 | -1.1444 | 121.4081 | 122.4243 | -0.93384 | -0.3479 | 0.013733 | 0.30212 | 121.7743 | 121.8796 | 121.8155 | 121.6049 | 121.4081 | 122.7631 | 121.9116 | -0.3479 | 121.6049 | 121.4081 | 121.9116 | 121.8155 | 122.7631 | -1.6434 | -123.0972
4001.9062 | 122.8043 | -121.6003 | 1.1673 | -0.11795 | -0.0023242 | -0.0074404 | 0.024195 | -0.002194 | -0.0037107 | 0.0083249 | -0.17395 | 0.022888 | -0.48065 | 0.83771 | 0.21057 | 0.31128 | 0.16937 | 0.28381 | 1.1765 | -121.9116 | 121.1197 | -1.1444 | 121.4264 | 122.4381 | -0.95673 | -0.31128 | 0.009156 | 0.3067 | 121.7697 | 121.8842 | 121.8109 | 121.6232 | 121.4264 | 122.7768 | 121.9116 | -0.31128 | 121.6232 | 121.4264 | 121.9116 | 121.8109 | 122.7768 | -1.6479 | -123.0789
4002.9062 | 122.8043 | -121.5866 | 1.1581 | -0.16373 | -0.0010424 | -0.0080814 | 0.026117 | -0.00069859 | -0.0020017 | 0.0085385 | -0.17853 | 0 | -0.52643 | 0.82855 | 0.21515 | 0.29755 | 0.17395 | 0.27924 | 1.1856 | -121.9345 | 121.0602 | -1.1581 | 121.4081 | 122.4152 | -0.94299 | -0.3479 | 0.027466 | 0.3479 | 121.7606 | 121.8658 | 121.8018 | 121.5866 | 121.4081 | 122.7722 | 121.8842 | -0.3479 | 121.5866 | 121.4081 | 121.8842 | 121.8018 | 122.7722 | -1.6846 | -123.0927
4003.9062 | 122.8088 | -121.6095 | 1.1215 | -0.24765 | -0.0040332 | -0.012354 | 0.023554 | -0.0026212 | -0.0020017 | 0.0089657 | -0.20599 | 0.004578 | -0.51727 | 0.80566 | 0.21515 | 0.28381 | 0.19226 | 0.27466 | 1.181 | -121.962 | 121.0922 | -1.1169 | 121.4035 | 122.4152 | -0.90637 | -0.35248 | 0.059509 | 0.31128 | 121.8018 | 121.8842 | 121.8246 | 121.6141 | 121.4035 | 122.7905 | 121.8933 | -0.35248 | 121.6141 | 121.4035 | 121.8933 | 121.8246 | 122.7905 | -1.6388 | -123.0835
4004.9062 | 122.7631 | -121.6049 | 1.149 | -0.20187 | -0.001897 | -0.0087222 | 0.020563 | -0.0011258 | -0.00071986 | 0.0083249 | -0.24719 | 0.027466 | -0.51727 | 0.76904 | 0.1831 | 0.24261 | 0.25177 | 0.25177 | 1.1719 | -121.9437 | 121.0876 | -1.1215 | 121.3577 | 122.374 | -0.96588 | -0.33875 | 0.022888 | 0.27008 | 121.8567 | 121.8567 | 121.788 | 121.6324 | 121.3577 | 122.7768 | 121.8475 | -0.33875 | 121.6324 | 121.3577 | 121.8475 | 121.788 | 122.7768 | -1.6663 | -123.0927
4005.9062 | 122.7768 | -121.6278 | 1.149 | -0.20187 | -0.001256 | -0.010645 | 0.025477 | -0.001553 | -0.0013609 | 0.011529 | -0.21515 | 0.032043 | -0.49896 | 0.78735 | 0.18768 | 0.27466 | 0.23346 | 0.2655 | 1.1673 | -121.9711 | 121.1288 | -1.1169 | 121.4127 | 122.4152 | -0.9613 | -0.34332 | 0.01831 | 0.28381 | 121.8613 | 121.8933 | 121.8155 | 121.6599 | 121.4127 | 122.7951 | 121.9025 | -0.34332 | 121.6599 | 121.4127 | 121.9025 | 121.8155 | 122.7951 | -1.6479 | -123.1201
4006.9062 | 122.7905 | -121.5958 | 1.1444 | -0.11032 | -0.001897 | -0.007654 | 0.026972 | -0.0036892 | -0.0013609 | 0.0093931 | -0.19684 | 0.032043 | -0.49896 | 0.81024 | 0.21973 | 0.29297 | 0.20142 | 0.28839 | 1.1856 | -121.9528 | 121.0968 | -1.1124 | 121.3989 | 122.406 | -0.92468 | -0.35706 | 0.041199 | 0.30212 | 121.7972 | 121.8842 | 121.8155 | 121.6278 | 121.3989 | 122.7814 | 121.8887 | -0.35706 | 121.6278 | 121.3989 | 121.8887 | 121.8155 | 122.7814 | -1.6434 | -123.0972
4007.9062 | 122.7768 | -121.637 | 1.0986 | -0.19424 | -0.0010424 | -0.0061588 | 0.023554 | -0.0011258 | -0.0020017 | 0.0076841 | -0.21057 | 0.013733 | -0.49439 | 0.79193 | 0.17853 | 0.27008 | 0.23804 | 0.2655 | 1.181 | -121.9666 | 121.1426 | -1.0849 | 121.4264 | 122.4289 | -0.9201 | -0.32959 | 0.082397 | 0.28381 | 121.875 | 121.9025 | 121.8155 | 121.6507 | 121.4264 | 122.818 | 121.907 | -0.32959 | 121.6507 | 121.4264 | 121.907 | 121.8155 | 122.818 | -1.593 | -123.0652
4008.9062 | 122.7722 | -121.669 | 1.1078 | -0.2095 | -0.003606 | -0.0095766 | 0.023981 | -0.0034756 | -0.0022153 | 0.0096067 | -0.23804 | 0.054932 | -0.48981 | 0.76904 | 0.18768 | 0.26093 | 0.24719 | 0.26093 | 1.1536 | -121.9894 | 121.1792 | -1.0529 | 121.431 | 122.438 | -0.9201 | -0.32044 | 0.045776 | 0.25177 | 121.9162 | 121.9299 | 121.8567 | 121.7239 | 121.431 | 122.8226 | 121.9299 | -0.32044 | 121.7239 | 121.431 | 121.9299 | 121.8567 | 122.8226 | -1.5976 | -123.0972
4009.9062 | 122.7631 | -121.6599 | 1.1124 | -0.23239 | -0.0031786 | -0.007654 | 0.022059 | -0.0053982 | -0.0013609 | 0.0076841 | -0.24261 | 0.036621 | -0.50354 | 0.75531 | 0.17853 | 0.25635 | 0.2655 | 0.23804 | 1.1581 | -121.994 | 121.1563 | -1.0757 | 121.4172 | 122.4152 | -0.93384 | -0.33417 | 0.045776 | 0.26092 | 121.9254 | 121.8979 | 121.8384 | 121.6965 | 121.4172 | 122.818 | 121.9162 | -0.33417 | 121.6965 | 121.4172 | 121.9162 | 121.8384 | 122.818 | -1.6159 | -123.1064
4010.9219 | 122.85 | -121.5363 | 1.1078 | 0.21774 | -0.0021106 | -0.0072268 | 0.021845 | -0.0034756 | -0.00093346 | 0.010461 | -0.16479 | -0.041199 | -0.48523 | 0.89722 | 0.27466 | 0.37079 | 0.013733 | 0.3479 | 1.1398 | -121.8887 | 121.051 | -1.149 | 121.3715 | 122.4335 | -0.83313 | -0.35248 | 0.032044 | 0.32043 | 121.55 | 121.8842 | 121.8109 | 121.4951 | 121.3715 | 122.6761 | 121.907 | -0.35248 | 121.4951 | 121.3715 | 121.907 | 121.8109 | 122.6761 | -1.593 | -122.9965
4011.9062 | 122.8043 | -121.6095 | 1.1124 | -0.24002 | -0.0048876 | -0.0072268 | 0.020136 | -0.003903 | -0.0020017 | 0.0068295 | -0.1831 | 0.009155 | -0.49896 | 0.85602 | 0.24261 | 0.32501 | 0.16937 | 0.32959 | 1.1307 | -121.9666 | 121.1105 | -1.1032 | 121.4264 | 122.4655 | -0.86975 | -0.35706 | 0.01831 | 0.31586 | 121.7789 | 121.9391 | 121.8521 | 121.6187 | 121.4264 | 122.7402 | 121.9345 | -0.35706 | 121.6187 | 121.4264 | 121.9345 | 121.8521 | 122.7402 | -1.6113 | -123.0789
4012.9062 | 122.7585 | -121.6415 | 1.1261 | -0.22476 | -0.0033922 | -0.011286 | 0.021845 | -0.0056118 | 0.00056194 | 0.010675 | -0.22888 | 0 | -0.49896 | 0.78735 | 0.19226 | 0.25635 | 0.22888 | 0.27466 | 1.1765 | -121.9711 | 121.1426 | -1.1261 | 121.4127 | 122.4289 | -0.93384 | -0.32959 | 0.050354 | 0.27008 | 121.8704 | 121.9162 | 121.8338 | 121.6415 | 121.4127 | 122.818 | 121.8979 | -0.32959 | 121.6415 | 121.4127 | 121.8979 | 121.8338 | 122.818 | -1.6251 | -123.0972
4013.9062 | 122.7493 | -121.6232 | 1.1536 | -0.21713 | -0.001897 | -0.014917 | 0.023768 | -0.0060392 | -0.0024289 | 0.0087521 | -0.25635 | 0.018311 | -0.50354 | 0.7782 | 0.1831 | 0.25177 | 0.26093 | 0.24261 | 1.1719 | -121.962 | 121.1197 | -1.1353 | 121.3669 | 122.4014 | -0.97046 | -0.33874 | 0.018311 | 0.24719 | 121.8842 | 121.8658 | 121.8063 | 121.6415 | 121.3669 | 122.7951 | 121.875 | -0.33874 | 121.6415 | 121.3669 | 121.875 | 121.8063 | 122.7951 | -1.6571 | -123.1155
4014.9062 | 122.7631 | -121.6461 | 1.1261 | -0.2095 | -0.0016834 | -0.008295 | 0.024622 | -0.0068936 | -0.00029266 | 0.0081113 | -0.25177 | 0.004578 | -0.50812 | 0.7782 | 0.1831 | 0.26093 | 0.23804 | 0.2655 | 1.1627 | -121.9666 | 121.138 | -1.1215 | 121.3943 | 122.4243 | -0.94299 | -0.32044 | 0.036621 | 0.25635 | 121.8842 | 121.9116 | 121.8292 | 121.6507 | 121.3943 | 122.8088 | 121.907 | -0.32044 | 121.6507 | 121.3943 | 121.907 | 121.8292 | 122.8088 | -1.6342 | -123.0927
4015.9219 | 122.7402 | -121.6415 | 1.1261 | 0.065155 | -0.0010424 | -0.0087222 | 0.028254 | -0.0051846 | -7.9062e-05 | 0.0098203 | -0.23804 | 0.009155 | -0.53101 | 0.75531 | 0.14191 | 0.22888 | 0.20142 | 0.19684 | 1.1627 | -121.9894 | 121.1105 | -1.1169 | 121.4035 | 122.3969 | -0.98419 | -0.3479 | 0.036621 | 0.29297 | 121.843 | 121.8384 | 121.7834 | 121.6507 | 121.4035 | 122.8043 | 121.8704 | -0.3479 | 121.6507 | 121.4035 | 121.8704 | 121.7834 | 122.8043 | -1.6571 | -123.1155
4016.9062 | 122.8317 | -121.6049 | 1.1169 | -0.19424 | -0.001897 | -0.01449 | 0.020136 | -0.0043302 | -0.0024289 | 0.0089657 | -0.20142 | -0.041199 | -0.50354 | 0.84228 | 0.27008 | 0.32959 | 0.17853 | 0.32501 | 1.1307 | -121.9528 | 121.1014 | -1.1581 | 121.4035 | 122.4472 | -0.84686 | -0.3479 | 0.013733 | 0.30212 | 121.7834 | 121.9299 | 121.875 | 121.5637 | 121.4035 | 122.7356 | 121.9345 | -0.3479 | 121.5637 | 121.4035 | 121.9345 | 121.875 | 122.7356 | -1.6205 | -123.0698
4017.9062 | 122.8317 | -121.5958 | 1.1032 | -0.17899 | -0.0040332 | -0.011927 | 0.021204 | -0.0043302 | -0.0022153 | 0.0078977 | -0.17395 | -0.027466 | -0.49439 | 0.86517 | 0.28381 | 0.3479 | 0.12817 | 0.3479 | 1.1261 | -121.8979 | 121.1014 | -1.1307 | 121.4218 | 122.4609 | -0.8194 | -0.30212 | 0.022889 | 0.32044 | 121.7239 | 121.9437 | 121.8796 | 121.5683 | 121.4218 | 122.7219 | 121.9437 | -0.30212 | 121.5683 | 121.4218 | 121.9437 | 121.8796 | 122.7219 | -1.5976 | -123.0011
4018.9062 | 122.9095 | -121.5683 | 1.1078 | -0.14847 | -0.003606 | -0.0095766 | 0.020136 | -0.008389 | -0.00071986 | 0.010888 | -0.16937 | -0.054932 | -0.4715 | 0.90179 | 0.28839 | 0.38452 | 0.073242 | 0.38452 | 1.1169 | -121.8979 | 121.0968 | -1.1627 | 121.3989 | 122.4701 | -0.8194 | -0.32959 | 0.009155 | 0.30212 | 121.6415 | 121.9528 | 121.8567 | 121.5134 | 121.3989 | 122.6852 | 121.9528 | -0.32959 | 121.5134 | 121.3989 | 121.9528 | 121.8567 | 122.6852 | -1.5793 | -123.0057
4019.9062 | 122.8867 | -121.5637 | 1.1261 | -0.23239 | -0.0038196 | -0.010858 | 0.023554 | -0.0081754 | -0.00050626 | 0.010461 | -0.16937 | -0.041199 | -0.46234 | 0.91095 | 0.27924 | 0.35706 | 0.09613 | 0.3891 | 1.1353 | -121.9254 | 121.1014 | -1.1673 | 121.3943 | 122.4747 | -0.84686 | -0.36163 | 0.009155 | 0.29297 | 121.6599 | 121.9528 | 121.843 | 121.5225 | 121.3943 | 122.699 | 121.9208 | -0.36163 | 121.5225 | 121.3943 | 121.9208 | 121.843 | 122.699 | -1.5884 | -123.0515
4020.9219 | 122.8592 | -121.5729 | 1.1032 | 0.15671 | -0.001256 | -0.010004 | 0.024836 | -0.0086026 | -0.0034971 | 0.0087521 | -0.18768 | -0.07782 | -0.50354 | 0.87433 | 0.26093 | 0.37079 | 0.045776 | 0.34332 | 1.1307 | -121.8979 | 121.0693 | -1.181 | 121.3852 | 122.4472 | -0.84228 | -0.32501 | 0.027466 | 0.31586 | 121.6187 | 121.9162 | 121.8338 | 121.4951 | 121.3852 | 122.7036 | 121.9437 | -0.32501 | 121.4951 | 121.3852 | 121.9437 | 121.8338 | 122.7036 | -1.6067 | -123.0011
4021.9062 | 122.8867 | -121.5591 | 1.1307 | -0.17899 | -0.002965 | -0.0089358 | 0.026117 | -0.0086026 | -0.0037107 | 0.0096067 | -0.17395 | -0.018311 | -0.48065 | 0.90179 | 0.27008 | 0.3479 | 0.10986 | 0.37079 | 1.149 | -121.8979 | 121.0785 | -1.149 | 121.3852 | 122.4609 | -0.86059 | -0.33874 | 0.018311 | 0.3067 | 121.669 | 121.9299 | 121.8292 | 121.5408 | 121.3852 | 122.7081 | 121.907 | -0.33874 | 121.5408 | 121.3852 | 121.907 | 121.8292 | 122.7081 | -1.6113 | -123.0286
4022.9062 | 122.8775 | -121.5179 | 1.1673 | -0.23239 | -0.0021106 | -0.010431 | 0.022272 | -0.0073208 | -0.00071986 | 0.0089657 | -0.16022 | -0.050354 | -0.4715 | 0.9613 | 0.27466 | 0.35706 | 0.091553 | 0.37994 | 1.181 | -121.8658 | 121.0464 | -1.2177 | 121.3577 | 122.4792 | -0.89264 | -0.3479 | 0.013733 | 0.31128 | 121.6095 | 121.8979 | 121.7926 | 121.4676 | 121.3577 | 122.699 | 121.875 | -0.3479 | 121.4676 | 121.3577 | 121.875 | 121.7926 | 122.699 | -1.6388 | -123.0331
4023.9062 | 122.8867 | -121.4905 | 1.1993 | -0.20187 | -0.0040332 | -0.010431 | 0.022699 | -0.0077482 | -0.0017881 | 0.0081113 | -0.17395 | -0.045776 | -0.45776 | 0.98419 | 0.27924 | 0.37994 | 0.073242 | 0.38452 | 1.1902 | -121.8201 | 121.0327 | -1.2451 | 121.3165 | 122.4747 | -0.9201 | -0.32959 | -0.009155 | 0.28381 | 121.5637 | 121.875 | 121.7697 | 121.4447 | 121.3165 | 122.6807 | 121.8704 | -0.32959 | 121.4447 | 121.3165 | 121.8704 | 121.7697 | 122.6807 | -1.6571 | -123.0194
4024.9062 | 122.8912 | -121.5088 | 1.1627 | -0.20187 | -0.0059558 | -0.011499 | 0.022913 | -0.0079618 | -0.0013609 | 0.0093931 | -0.16479 | -0.022888 | -0.4715 | 0.95673 | 0.29297 | 0.37079 | 0.059509 | 0.3891 | 1.1948 | -121.8567 | 121.0373 | -1.1856 | 121.344 | 122.4655 | -0.86975 | -0.3479 | 0.032043 | 0.3067 | 121.5683 | 121.8979 | 121.8018 | 121.4859 | 121.344 | 122.7036 | 121.8796 | -0.3479 | 121.4859 | 121.344 | 121.8796 | 121.8018 | 122.7036 | -1.6342 | -123.0194
4025.9219 | 122.7859 | -121.5683 | 1.149 | -0.034027 | -0.0025378 | -0.0074404 | 0.030817 | -0.0034756 | -0.0032835 | 0.0074705 | -0.17395 | 0 | -0.49439 | 0.88806 | 0.21973 | 0.30212 | 0.15564 | 0.26093 | 1.1765 | -121.9437 | 121.0739 | -1.149 | 121.3943 | 122.4564 | -0.92926 | -0.37537 | 0.027466 | 0.32044 | 121.7239 | 121.8292 | 121.788 | 121.5683 | 121.3943 | 122.7448 | 121.8704 | -0.37537 | 121.5683 | 121.3943 | 121.8704 | 121.788 | 122.7448 | -1.6434 | -123.0927
4026.9062 | 122.9141 | -121.5775 | 1.1032 | -0.087433 | -0.0055286 | -0.014276 | 0.019922 | -0.0058256 | -0.0011471 | 0.0089657 | -0.15106 | -0.045776 | -0.48981 | 0.93384 | 0.30212 | 0.39825 | 0.068665 | 0.37994 | 1.1261 | -121.8796 | 121.0876 | -1.149 | 121.4264 | 122.5113 | -0.80109 | -0.30212 | 0.022889 | 0.33874 | 121.6461 | 121.9574 | 121.8796 | 121.5317 | 121.4264 | 122.7036 | 121.9757 | -0.30212 | 121.5317 | 121.4264 | 121.9757 | 121.8796 | 122.7036 | -1.593 | -122.9828
4027.9062 | 122.8867 | -121.5546 | 1.1169 | -0.21713 | -0.0051012 | -0.011927 | 0.022913 | -0.0088162 | 0.00056194 | 0.010034 | -0.16022 | -0.027466 | -0.44861 | 0.93384 | 0.29755 | 0.36621 | 0.082397 | 0.37537 | 1.1398 | -121.8979 | 121.106 | -1.1444 | 121.3943 | 122.4884 | -0.8194 | -0.34332 | 0.022889 | 0.28839 | 121.637 | 121.9299 | 121.8521 | 121.5271 | 121.3943 | 122.6944 | 121.9208 | -0.34332 | 121.5271 | 121.3943 | 121.9208 | 121.8521 | 122.6944 | -1.5656 | -123.0148
4028.9062 | 122.8363 | -121.5729 | 1.1398 | -0.18662 | -0.0038196 | -0.01449 | 0.023554 | -0.0062528 | -0.0034971 | 0.0085385 | -0.17395 | -0.004578 | -0.48065 | 0.88806 | 0.27008 | 0.32959 | 0.15564 | 0.34332 | 1.1444 | -121.8979 | 121.0922 | -1.1444 | 121.3989 | 122.4609 | -0.86975 | -0.32501 | 0.004577 | 0.3067 | 121.7285 | 121.9162 | 121.843 | 121.5683 | 121.3989 | 122.7173 | 121.9025 | -0.32501 | 121.5683 | 121.3989 | 121.9025 | 121.843 | 122.7173 | -1.6205 | -123.0377
4029.9062 | 122.8867 | -121.6095 | 1.0529 | -0.21713 | -0.0025378 | -0.0097904 | 0.020136 | -0.0092434 | -0.0022153 | 0.0083249 | -0.16479 | -0.018311 | -0.48065 | 0.87891 | 0.2243 | 0.32044 | 0.050354 | 0.36163 | 1.0666 | -121.9528 | 121.1288 | -1.0712 | 121.4447 | 122.4884 | -0.82855 | -0.34332 | 0.013733 | 0.31586 | 121.6599 | 121.9711 | 121.8338 | 121.5912 | 121.4447 | 122.6761 | 121.9299 | -0.34332 | 121.5912 | 121.4447 | 121.9299 | 121.8338 | 122.6761 | -1.5335 | -123.0057
4030.9062 | 122.7905 | -121.6736 | 1.1032 | -0.19424 | -0.001897 | -0.0085086 | 0.029535 | -0.0058256 | -0.0017881 | 0.0089657 | -0.21057 | 0.041199 | -0.50354 | 0.76904 | 0.10529 | 0.20599 | 0.20599 | 0.24719 | 1.1169 | -122.0123 | 121.17 | -1.062 | 121.463 | 122.4426 | -0.99792 | -0.33874 | 0.013733 | 0.29297 | 121.8796 | 121.9208 | 121.7789 | 121.7148 | 121.463 | 122.7905 | 121.8796 | -0.33874 | 121.7148 | 121.463 | 121.8796 | 121.7789 | 122.7905 | -1.6067 | -123.1155
4031.9062 | 122.9095 | -121.6232 | 1.0345 | -0.13321 | -0.0025378 | -0.011072 | 0.019922 | -0.0079618 | 0.00013454 | 0.0093931 | -0.15564 | -0.027466 | -0.4715 | 0.88348 | 0.25635 | 0.3479 | 0.036621 | 0.36163 | 1.0712 | -121.9208 | 121.1517 | -1.062 | 121.4676 | 122.5067 | -0.7782 | -0.29755 | 0.036621 | 0.31586 | 121.6599 | 121.9849 | 121.8796 | 121.5958 | 121.4676 | 122.6944 | 121.9711 | -0.29755 | 121.5958 | 121.4676 | 121.9711 | 121.8796 | 122.6944 | -1.506 | -122.9553
4032.9062 | 122.9141 | -121.6095 | 1.0712 | -0.14847 | -0.0025378 | -0.012995 | 0.022913 | -0.0075344 | -0.0011471 | 0.010034 | -0.17853 | -0.036621 | -0.49439 | 0.88348 | 0.2243 | 0.3479 | 0.018311 | 0.37079 | 1.0757 | -121.9345 | 121.1151 | -1.1078 | 121.431 | 122.493 | -0.84686 | -0.32501 | 0.004578 | 0.31586 | 121.6278 | 121.9803 | 121.8338 | 121.5729 | 121.431 | 122.6852 | 121.9574 | -0.32501 | 121.5729 | 121.431 | 121.9574 | 121.8338 | 122.6852 | -1.5656 | -123.0057
4033.9062 | 122.8958 | -121.637 | 1.0529 | -0.064545 | -0.0038196 | -0.013208 | 0.021845 | -0.00668 | 0.00013454 | 0.010247 | -0.1831 | -0.041199 | -0.50354 | 0.87891 | 0.22888 | 0.33417 | 0.013733 | 0.35706 | 1.0757 | -121.9254 | 121.1334 | -1.0941 | 121.4539 | 122.5159 | -0.82397 | -0.28839 | 0.022889 | 0.32044 | 121.6507 | 121.994 | 121.8658 | 121.5958 | 121.4539 | 122.7127 | 121.9711 | -0.28839 | 121.5958 | 121.4539 | 121.9711 | 121.8658 | 122.7127 | -1.5564 | -122.9782
4034.9062 | 122.8912 | -121.6141 | 1.0345 | -0.18662 | -0.0042468 | -0.0087222 | 0.021204 | -0.0088162 | -0.0015745 | 0.0059751 | -0.19684 | -0.041199 | -0.48981 | 0.8606 | 0.22888 | 0.34332 | 0.032043 | 0.35706 | 1.0666 | -121.9391 | 121.1243 | -1.0757 | 121.4172 | 122.4747 | -0.80566 | -0.32501 | 0.032043 | 0.29297 | 121.6461 | 121.9711 | 121.843 | 121.5729 | 121.4172 | 122.6807 | 121.9574 | -0.32501 | 121.5729 | 121.4172 | 121.9574 | 121.843 | 122.6807 | -1.5244 | -122.9736
4035.9062 | 122.8638 | -121.6141 | 1.0574 | -0.1561 | -0.0042468 | -0.0074404 | 0.023768 | -0.0098844 | -0.0013609 | 0.0078977 | -0.16479 | -0.032043 | -0.46692 | 0.84686 | 0.20599 | 0.32501 | 0.059509 | 0.34332 | 1.062 | -121.9666 | 121.1472 | -1.0895 | 121.4493 | 122.4609 | -0.85144 | -0.35248 | 0.004578 | 0.30212 | 121.6736 | 121.9574 | 121.8201 | 121.582 | 121.4493 | 122.6761 | 121.9391 | -0.35248 | 121.582 | 121.4493 | 121.9391 | 121.8201 | 122.6761 | -1.5244 | -123.024
4036.9062 | 122.9187 | -121.6324 | 1.062 | -0.095062 | -0.0038196 | -0.011927 | 0.021631 | -0.0058256 | -0.0013609 | 0.0078977 | -0.1831 | -0.054932 | -0.49896 | 0.90179 | 0.24719 | 0.35248 | 0.027466 | 0.36621 | 1.0803 | -121.9025 | 121.1334 | -1.1169 | 121.4493 | 122.5342 | -0.81482 | -0.27008 | 0.01831 | 0.31586 | 121.6599 | 121.9986 | 121.8796 | 121.5775 | 121.4493 | 122.7127 | 121.9849 | -0.27008 | 121.5775 | 121.4493 | 121.9849 | 121.8796 | 122.7127 | -1.561 | -122.9645
4037.9062 | 122.9233 | -121.5958 | 1.0712 | -0.087433 | -0.0040332 | -0.010858 | 0.019922 | -0.0077482 | -0.0017881 | 0.0085385 | -0.19684 | -0.064087 | -0.50354 | 0.90179 | 0.21973 | 0.35248 | 0.013733 | 0.36621 | 1.0941 | -121.9116 | 121.0922 | -1.1353 | 121.3989 | 122.4976 | -0.85144 | -0.31586 | 0.022888 | 0.3067 | 121.6095 | 121.962 | 121.8155 | 121.5317 | 121.3989 | 122.6898 | 121.9482 | -0.31586 | 121.5317 | 121.3989 | 121.9482 | 121.8155 | 122.6898 | -1.5747 | -122.9828
4038.9062 | 122.8958 | -121.6049 | 1.0712 | -0.095062 | -0.002965 | -0.009363 | 0.02035 | -0.0077482 | -0.00029266 | 0.0098203 | -0.20599 | -0.059509 | -0.49439 | 0.88806 | 0.24261 | 0.35248 | 0.009155 | 0.36621 | 1.0849 | -121.9299 | 121.1105 | -1.1307 | 121.3989 | 122.493 | -0.82855 | -0.32501 | 0.013733 | 0.28839 | 121.6141 | 121.9711 | 121.8475 | 121.5454 | 121.3989 | 122.6898 | 121.9574 | -0.32501 | 121.5454 | 121.3989 | 121.9574 | 121.8475 | 122.6898 | -1.5656 | -123.0011
4039.9062 | 122.8958 | -121.5729 | 1.0757 | 0.0041197 | -0.0044604 | -0.013636 | 0.02035 | -0.0075344 | -0.0011471 | 0.0085385 | -0.21057 | -0.045776 | -0.5127 | 0.89722 | 0.23346 | 0.32959 | 0.009155 | 0.3479 | 1.0849 | -121.9345 | 121.0602 | -1.1215 | 121.3623 | 122.4701 | -0.84229 | -0.36163 | 0.009155 | 0.30212 | 121.582 | 121.9208 | 121.8063 | 121.5271 | 121.3623 | 122.6578 | 121.9025 | -0.36163 | 121.5271 | 121.3623 | 121.9025 | 121.8063 | 122.6578 | -1.5884 | -123.0103
4040.9219 | 122.7997 | -121.6599 | 1.0941 | -0.13321 | 2.5564e-05 | -0.0087222 | 0.026117 | -0.0062528 | -0.0024289 | 0.0085385 | -0.21973 | 0.009155 | -0.50354 | 0.81482 | 0.11902 | 0.23346 | 0.19226 | 0.22888 | 1.1215 | -121.9757 | 121.1563 | -1.0849 | 121.4401 | 122.4747 | -0.97504 | -0.31586 | 0.027466 | 0.28381 | 121.8521 | 121.8887 | 121.7789 | 121.669 | 121.4401 | 122.7814 | 121.8933 | -0.31586 | 121.669 | 121.4401 | 121.8933 | 121.7789 | 122.7814 | -1.5976 | -123.0698
4041.9062 | 122.8958 | -121.6187 | 1.0803 | -0.095062 | -0.0044604 | -0.012995 | 0.019922 | -0.0060392 | -0.0026425 | 0.0091795 | -0.16479 | -0.022888 | -0.4715 | 0.92468 | 0.24261 | 0.36621 | 0.009155 | 0.36621 | 1.0986 | -121.8979 | 121.1472 | -1.1032 | 121.4539 | 122.5433 | -0.83771 | -0.27924 | 0.018311 | 0.3067 | 121.6278 | 121.9849 | 121.8613 | 121.5958 | 121.4539 | 122.7173 | 121.9849 | -0.27924 | 121.5958 | 121.4539 | 121.9849 | 121.8613 | 122.7173 | -1.5518 | -122.9782
4042.9062 | 122.9324 | -121.5637 | 1.1307 | -0.17136 | -0.0027514 | -0.012354 | 0.020563 | -0.0073208 | -0.0022153 | 0.0081113 | -0.16937 | -0.045776 | -0.49896 | 0.96588 | 0.25177 | 0.36621 | -0.004578 | 0.36163 | 1.1398 | -121.8384 | 121.0648 | -1.1765 | 121.3943 | 122.5296 | -0.87891 | -0.27466 | 0.009156 | 0.32959 | 121.5591 | 121.9254 | 121.8155 | 121.5179 | 121.3943 | 122.7036 | 121.9299 | -0.27466 | 121.5179 | 121.3943 | 121.9299 | 121.8155 | 122.7036 | -1.6296 | -122.9691
4043.9062 | 122.905 | -121.5408 | 1.1444 | -0.079803 | -0.002965 | -0.009363 | 0.020777 | -0.010312 | -0.0011471 | 0.0087521 | -0.18768 | -0.032043 | -0.48065 | 0.97046 | 0.23804 | 0.35706 | -0.027466 | 0.36163 | 1.1536 | -121.8292 | 121.0602 | -1.1765 | 121.3531 | 122.5113 | -0.90637 | -0.28839 | 0.009155 | 0.29297 | 121.5134 | 121.9025 | 121.7789 | 121.5088 | 121.3531 | 122.6944 | 121.8979 | -0.28839 | 121.5088 | 121.3531 | 121.8979 | 121.7789 | 122.6944 | -1.6251 | -122.9736
4044.9062 | 122.8958 | -121.5637 | 1.1124 | -0.11795 | -0.0055286 | -0.010645 | 0.019922 | -0.0081754 | -0.00093346 | 0.0078977 | -0.1831 | -0.036621 | -0.50354 | 0.9613 | 0.23804 | 0.37079 | -0.022888 | 0.34332 | 1.1444 | -121.8521 | 121.0602 | -1.149 | 121.3806 | 122.525 | -0.87433 | -0.28839 | 0.032043 | 0.32044 | 121.5408 | 121.907 | 121.8018 | 121.5271 | 121.3806 | 122.7081 | 121.9345 | -0.28839 | 121.5271 | 121.3806 | 121.9345 | 121.8018 | 122.7081 | -1.6159 | -122.9645
4045.9062 | 122.8821 | -121.5408 | 1.1444 | -0.041657 | -0.0048876 | -0.013208 | 0.019282 | -0.0060392 | -0.0015745 | 0.0089657 | -0.19684 | -0.018311 | -0.48981 | 0.94757 | 0.21973 | 0.35706 | -0.013733 | 0.33875 | 1.1353 | -121.875 | 121.051 | -1.1627 | 121.344 | 122.4884 | -0.92468 | -0.33417 | -0.009155 | 0.29297 | 121.5271 | 121.8796 | 121.7606 | 121.5225 | 121.344 | 122.6761 | 121.8979 | -0.33417 | 121.5225 | 121.344 | 121.8979 | 121.7606 | 122.6761 | -1.6342 | -123.0194
4046.9062 | 122.8912 | -121.5546 | 1.1536 | -0.056915 | -0.0059558 | -0.013636 | 0.020991 | -0.0079618 | -0.0030697 | 0.011102 | -0.21973 | -0.050354 | -0.49896 | 0.93842 | 0.24261 | 0.36163 | 0 | 0.32959 | 1.1398 | -121.8613 | 121.0556 | -1.2039 | 121.3348 | 122.493 | -0.91095 | -0.3067 | -0.013732 | 0.27924 | 121.5546 | 121.8842 | 121.7972 | 121.5042 | 121.3348 | 122.6944 | 121.9162 | -0.3067 | 121.5042 | 121.3348 | 121.9162 | 121.7972 | 122.6944 | -1.6525 | -123.0148
4047.9062 | 122.8867 | -121.5775 | 1.1078 | -0.2095 | -0.0042468 | -0.013849 | 0.022272 | -0.0077482 | -0.0022153 | 0.0093931 | -0.17395 | -0.064087 | -0.48981 | 0.93842 | 0.2243 | 0.35248 | 0.004578 | 0.36163 | 1.1261 | -121.8658 | 121.0876 | -1.1719 | 121.4035 | 122.5159 | -0.88348 | -0.28839 | 0.018311 | 0.31586 | 121.582 | 121.9391 | 121.8018 | 121.5134 | 121.4035 | 122.7036 | 121.9299 | -0.28839 | 121.5134 | 121.4035 | 121.9299 | 121.8018 | 122.7036 | -1.5976 | -122.9736
4048.9062 | 122.9095 | -121.5271 | 1.1124 | -0.087433 | -0.005315 | -0.0095766 | 0.019922 | -0.0096708 | -0.00071986 | 0.0068295 | -0.1831 | -0.050354 | -0.48523 | 0.9613 | 0.2243 | 0.36163 | 0.004578 | 0.36163 | 1.1444 | -121.8521 | 121.0419 | -1.1627 | 121.344 | 122.4884 | -0.88806 | -0.32501 | 0.032043 | 0.30212 | 121.5317 | 121.8887 | 121.7514 | 121.4767 | 121.344 | 122.6715 | 121.8887 | -0.32501 | 121.4767 | 121.344 | 121.8887 | 121.7514 | 122.6715 | -1.5976 | -122.9645
4049.9062 | 122.9141 | -121.5088 | 1.1261 | -0.034027 | -0.0021106 | -0.01214 | 0.019709 | -0.0051846 | 0.00034814 | 0.0096067 | -0.1831 | -0.050354 | -0.49439 | 0.97046 | 0.25635 | 0.35706 | -0.004578 | 0.35248 | 1.1398 | -121.8567 | 121.0144 | -1.1765 | 121.3257 | 122.4792 | -0.86975 | -0.3479 | 0.013733 | 0.31128 | 121.5042 | 121.8613 | 121.7651 | 121.4584 | 121.3257 | 122.6486 | 121.8658 | -0.3479 | 121.4584 | 121.3257 | 121.8658 | 121.7651 | 122.6486 | -1.6205 | -122.9828
4050.9219 | 122.8134 | -121.6003 | 1.1398 | -0.041657 | -0.00061524 | -0.008295 | 0.029749 | -0.0064664 | -0.00050626 | 0.0072569 | -0.19684 | -0.013733 | -0.52185 | 0.90179 | 0.14191 | 0.2655 | 0.10071 | 0.25177 | 1.1719 | -121.907 | 121.0785 | -1.1536 | 121.4035 | 122.5021 | -0.99792 | -0.3067 | 0.032043 | 0.32501 | 121.701 | 121.8521 | 121.7422 | 121.5866 | 121.4035 | 122.7722 | 121.8658 | -0.3067 | 121.5866 | 121.4035 | 121.8658 | 121.7422 | 122.7722 | -1.6617 | -123.0469
4051.9062 | 122.8958 | -121.5271 | 1.1307 | -0.079803 | -0.0031786 | -0.011713 | 0.019922 | -0.0045438 | -0.0039243 | 0.0089657 | -0.18768 | -0.032043 | -0.48523 | 0.96588 | 0.21973 | 0.36163 | -0.004578 | 0.35248 | 1.1627 | -121.8201 | 121.0419 | -1.1627 | 121.3394 | 122.493 | -0.91095 | -0.29297 | 0.032044 | 0.29755 | 121.5225 | 121.8796 | 121.7468 | 121.4951 | 121.3394 | 122.6898 | 121.8887 | -0.29297 | 121.4951 | 121.3394 | 121.8887 | 121.7468 | 122.6898 | -1.6159 | -122.9507
4052.9062 | 122.9095 | -121.5363 | 1.149 | -0.049286 | -0.0040332 | -0.0097904 | 0.022699 | -0.0081754 | -0.0020017 | 0.0081113 | -0.21057 | -0.036621 | -0.48065 | 0.96588 | 0.23804 | 0.36163 | -0.018311 | 0.3479 | 1.1581 | -121.8613 | 121.0556 | -1.1856 | 121.3257 | 122.5021 | -0.91095 | -0.32501 | 0.009155 | 0.27008 | 121.5179 | 121.8842 | 121.7743 | 121.4996 | 121.3257 | 122.6944 | 121.8979 | -0.32501 | 121.4996 | 121.3257 | 121.8979 | 121.7743 | 122.6944 | -1.6296 | -123.0103
4053.9062 | 122.9095 | -121.5454 | 1.1124 | -0.079803 | -0.003606 | -0.014704 | 0.021418 | -0.0077482 | -0.00029266 | 0.0096067 | -0.20142 | -0.054932 | -0.49896 | 0.93384 | 0.2243 | 0.36163 | 0 | 0.35706 | 1.1627 | -121.8521 | 121.0464 | -1.1673 | 121.344 | 122.4792 | -0.88806 | -0.3067 | 0.050354 | 0.29755 | 121.5454 | 121.9025 | 121.7697 | 121.4905 | 121.344 | 122.7081 | 121.907 | -0.3067 | 121.4905 | 121.344 | 121.907 | 121.7697 | 122.7081 | -1.6113 | -122.9645
4054.9062 | 122.905 | -121.5729 | 1.1261 | -0.079803 | -0.0042468 | -0.013208 | 0.022272 | -0.0088162 | -7.9062e-05 | 0.0083249 | -0.22888 | -0.050354 | -0.50812 | 0.93842 | 0.2243 | 0.35706 | -0.004578 | 0.33417 | 1.1398 | -121.8567 | 121.0648 | -1.1765 | 121.344 | 122.5113 | -0.90179 | -0.28381 | 0.013733 | 0.27924 | 121.5683 | 121.907 | 121.7972 | 121.5225 | 121.344 | 122.7127 | 121.9299 | -0.28381 | 121.5225 | 121.344 | 121.9299 | 121.7972 | 122.7127 | -1.6342 | -122.9828
4055.9062 | 122.8043 | -121.6187 | 1.1719 | -0.19424 | -0.00082884 | -0.011499 | 0.027399 | -0.0073208 | -0.00029266 | 0.0083249 | -0.25635 | 0.009155 | -0.52185 | 0.86517 | 0.11444 | 0.23346 | 0.16022 | 0.21515 | 1.1902 | -121.9254 | 121.0968 | -1.1627 | 121.3623 | 122.4838 | -1.0574 | -0.3067 | 0.018311 | 0.2655 | 121.7789 | 121.8338 | 121.7331 | 121.6278 | 121.3623 | 122.8088 | 121.8521 | -0.3067 | 121.6278 | 121.3623 | 121.8521 | 121.7331 | 122.8088 | -1.6937 | -123.0972
4056.9062 | 122.9095 | -121.5408 | 1.1307 | -0.079803 | -0.0048876 | -0.011713 | 0.019068 | -0.0064664 | -0.0026425 | 0.010247 | -0.20599 | -0.059509 | -0.49896 | 0.9613 | 0.25177 | 0.37537 | -0.009155 | 0.37537 | 1.1307 | -121.8567 | 121.0419 | -1.1902 | 121.3348 | 122.5021 | -0.87891 | -0.31586 | 0 | 0.29297 | 121.5317 | 121.9162 | 121.7926 | 121.4813 | 121.3348 | 122.6715 | 121.9162 | -0.31586 | 121.4813 | 121.3348 | 121.9162 | 121.7926 | 122.6715 | -1.6296 | -122.9874
4057.9062 | 122.9141 | -121.5408 | 1.1398 | -0.095062 | -0.004674 | -0.010218 | 0.019709 | -0.0094572 | -0.00029266 | 0.0087521 | -0.20599 | -0.059509 | -0.50354 | 0.96588 | 0.24261 | 0.37079 | -0.009155 | 0.34332 | 1.1398 | -121.8338 | 121.0373 | -1.1993 | 121.3348 | 122.5067 | -0.89722 | -0.29297 | 0 | 0.29755 | 121.5317 | 121.8842 | 121.7834 | 121.4813 | 121.3348 | 122.6807 | 121.9116 | -0.29297 | 121.4813 | 121.3348 | 121.9116 | 121.7834 | 122.6807 | -1.6434 | -122.9736
4058.9062 | 122.9004 | -121.5591 | 1.1398 | -0.056915 | -0.0040332 | -0.012995 | 0.020991 | -0.0056118 | -0.0028561 | 0.010888 | -0.18768 | -0.027466 | -0.46692 | 0.9613 | 0.22888 | 0.37079 | -0.022888 | 0.3479 | 1.1353 | -121.843 | 121.0922 | -1.1673 | 121.3715 | 122.5204 | -0.91095 | -0.28381 | -0.004578 | 0.27924 | 121.5363 | 121.907 | 121.788 | 121.5317 | 121.3715 | 122.6944 | 121.9299 | -0.28381 | 121.5317 | 121.3715 | 121.9299 | 121.788 | 122.6944 | -1.6068 | -122.9828
4059.9062 | 122.905 | -121.55 | 1.1353 | -0.087433 | -0.0027514 | -0.011072 | 0.018213 | -0.0086026 | -0.0011471 | 0.0096067 | -0.19684 | -0.032043 | -0.48523 | 0.95215 | 0.21973 | 0.37994 | -0.009155 | 0.32959 | 1.1627 | -121.8796 | 121.0648 | -1.1673 | 121.3531 | 122.5021 | -0.91553 | -0.32959 | 0.027466 | 0.28839 | 121.5408 | 121.8796 | 121.7697 | 121.5179 | 121.3531 | 122.7127 | 121.9299 | -0.32959 | 121.5179 | 121.3531 | 121.9299 | 121.7697 | 122.7127 | -1.6205 | -123.0148
4060.9062 | 122.8683 | -121.5637 | 1.1353 | -0.17136 | -0.0044604 | -0.0074404 | 0.020777 | -0.0062528 | -0.0011471 | 0.0093931 | -0.16937 | -0.018311 | -0.4715 | 0.93842 | 0.20142 | 0.33875 | 0.032043 | 0.3479 | 1.1627 | -121.875 | 121.0922 | -1.1536 | 121.3943 | 122.5021 | -0.93384 | -0.31128 | 0.027466 | 0.30212 | 121.5958 | 121.9116 | 121.7651 | 121.5454 | 121.3943 | 122.7264 | 121.9025 | -0.31128 | 121.5454 | 121.3943 | 121.9025 | 121.7651 | 122.7264 | -1.6068 | -123.0103
4061.9062 | 122.9095 | -121.5454 | 1.1307 | -0.056915 | -0.0042468 | -0.0097904 | 0.020136 | -0.0073208 | 0.00056194 | 0.0070431 | -0.20599 | -0.022888 | -0.48523 | 0.93384 | 0.21057 | 0.35706 | 0.009155 | 0.32044 | 1.1444 | -121.8613 | 121.0602 | -1.1536 | 121.3394 | 122.4792 | -0.9201 | -0.31586 | 0.013733 | 0.27924 | 121.5546 | 121.8658 | 121.756 | 121.5225 | 121.3394 | 122.6898 | 121.9025 | -0.31586 | 121.5225 | 121.3394 | 121.9025 | 121.756 | 122.6898 | -1.6159 | -122.9919
4062.9062 | 122.9141 | -121.5363 | 1.1444 | -0.10269 | -0.004674 | -0.01214 | 0.022059 | -0.0077482 | -7.9062e-05 | 0.0093931 | -0.1831 | -0.022888 | -0.48523 | 0.97961 | 0.24261 | 0.38452 | -0.018311 | 0.36621 | 1.1261 | -121.8521 | 121.051 | -1.1673 | 121.3531 | 122.5159 | -0.90179 | -0.31586 | -0.01831 | 0.30212 | 121.5179 | 121.9025 | 121.7789 | 121.5134 | 121.3531 | 122.6624 | 121.9208 | -0.31586 | 121.5134 | 121.3531 | 121.9208 | 121.7789 | 122.6624 | -1.6296 | -122.9965
4063.9062 | 122.9187 | -121.5637 | 1.1353 | -0.041657 | -0.003606 | -0.012567 | 0.020136 | -0.0073208 | 0.0016299 | 0.0093931 | -0.1831 | -0.036621 | -0.50354 | 0.97504 | 0.24719 | 0.37537 | -0.022888 | 0.35706 | 1.1353 | -121.8567 | 121.0602 | -1.1719 | 121.3806 | 122.5388 | -0.88806 | -0.29297 | 0 | 0.32044 | 121.5408 | 121.9208 | 121.8109 | 121.5271 | 121.3806 | 122.699 | 121.9391 | -0.29297 | 121.5271 | 121.3806 | 121.9391 | 121.8109 | 122.699 | -1.6388 | -122.9919
4064.9062 | 122.9095 | -121.4951 | 1.1993 | -0.079803 | -0.0033922 | -0.011927 | 0.021631 | -0.0081754 | -0.00050626 | 0.0098203 | -0.1831 | -0.041199 | -0.48981 | 1.0162 | 0.25177 | 0.43488 | 0 | 0.3479 | 1.1993 | -121.7789 | 121.0052 | -1.2405 | 121.312 | 122.5113 | -0.94757 | -0.28381 | 0 | 0.3067 | 121.4951 | 121.843 | 121.7468 | 121.4539 | 121.312 | 122.6944 | 121.9299 | -0.28381 | 121.4539 | 121.312 | 121.9299 | 121.7468 | 122.6944 | -1.6891 | -122.9782
4065.9062 | 122.7814 | -121.5225 | 1.2222 | -0.2095 | -0.0038196 | -0.014917 | 0.023554 | -0.0073208 | -0.0017881 | 0.0089657 | -0.2243 | -0.009155 | -0.49439 | 0.9201 | 0.15106 | 0.3067 | 0.15106 | 0.24719 | 1.236 | -121.8475 | 121.0281 | -1.2314 | 121.2982 | 122.4426 | -1.0712 | -0.32501 | 0.013733 | 0.27008 | 121.6736 | 121.7697 | 121.6736 | 121.5134 | 121.2982 | 122.7585 | 121.8292 | -0.32501 | 121.5134 | 121.2982 | 121.8292 | 121.6736 | 122.7585 | -1.7166 | -123.0698
4066.9062 | 122.8958 | -121.4996 | 1.1856 | -0.018768 | -0.0038196 | -0.010218 | 0.018854 | -0.0064664 | -0.00050626 | 0.0096067 | -0.2243 | -0.050354 | -0.49896 | 0.99792 | 0.24261 | 0.40283 | 0.013733 | 0.33875 | 1.2131 | -121.7834 | 121.0007 | -1.236 | 121.2753 | 122.4976 | -0.94299 | -0.28381 | 0.027466 | 0.27466 | 121.5134 | 121.8384 | 121.7422 | 121.4493 | 121.2753 | 122.7127 | 121.9025 | -0.28381 | 121.4493 | 121.2753 | 121.9025 | 121.7422 | 122.7127 | -1.6846 | -122.9691
4067.9062 | 122.8958 | -121.5179 | 1.181 | -0.041657 | -0.004674 | -0.007654 | 0.019922 | -0.0071072 | 0.00077554 | 0.0093931 | -0.23346 | -0.032043 | -0.49439 | 1.0071 | 0.23346 | 0.40741 | 0.018311 | 0.32959 | 1.1902 | -121.8018 | 121.0236 | -1.2131 | 121.2845 | 122.525 | -0.94757 | -0.28381 | 0.009156 | 0.26093 | 121.5363 | 121.8475 | 121.7514 | 121.4859 | 121.2845 | 122.7081 | 121.9254 | -0.28381 | 121.4859 | 121.2845 | 121.9254 | 121.7514 | 122.7081 | -1.6754 | -122.9828
4068.9062 | 122.8683 | -121.4996 | 1.1902 | -0.041657 | -0.0044604 | -0.010645 | 0.019495 | -0.0079618 | 0.00034814 | 0.0093931 | -0.23804 | -0.054932 | -0.50812 | 1.0025 | 0.23804 | 0.40283 | 0.018311 | 0.32959 | 1.2131 | -121.7972 | 120.9915 | -1.2451 | 121.2616 | 122.5021 | -0.95215 | -0.29755 | 0.022888 | 0.27008 | 121.5179 | 121.8292 | 121.7377 | 121.4447 | 121.2616 | 122.7127 | 121.9025 | -0.29755 | 121.4447 | 121.2616 | 121.9025 | 121.7377 | 122.7127 | -1.6983 | -122.9874
4069.9062 | 122.9095 | -121.4767 | 1.1765 | -0.10269 | -0.002965 | -0.01214 | 0.020136 | -0.0053982 | -0.00029266 | 0.0091795 | -0.18768 | -0.054932 | -0.50354 | 1.0208 | 0.25635 | 0.42572 | -0.004578 | 0.36163 | 1.1719 | -121.7697 | 120.9732 | -1.2314 | 121.2891 | 122.4976 | -0.9201 | -0.29297 | -0.004578 | 0.31586 | 121.4722 | 121.8384 | 121.7331 | 121.4218 | 121.2891 | 122.6486 | 121.9025 | -0.29297 | 121.4218 | 121.2891 | 121.9025 | 121.7331 | 122.6486 | -1.68 | -122.9462
4070.9062 | 122.9141 | -121.5042 | 1.181 | -0.087433 | -0.0055286 | -0.011927 | 0.019282 | -0.0096708 | -0.0022153 | 0.0098203 | -0.20599 | -0.064087 | -0.48523 | 1.0117 | 0.25635 | 0.42572 | -0.022888 | 0.36163 | 1.1993 | -121.8063 | 121.019 | -1.2451 | 121.2982 | 122.5159 | -0.92468 | -0.30212 | 0.018311 | 0.27924 | 121.4813 | 121.8658 | 121.7606 | 121.4401 | 121.2982 | 122.7036 | 121.9299 | -0.30212 | 121.4401 | 121.2982 | 121.9299 | 121.7606 | 122.7036 | -1.6663 | -122.9874
4071.9062 | 122.9095 | -121.4905 | 1.2085 | -0.064545 | -0.0059558 | -0.011713 | 0.019282 | -0.010098 | -0.0015745 | 0.011316 | -0.21515 | -0.059509 | -0.50812 | 1.0254 | 0.24719 | 0.42114 | -0.004578 | 0.3479 | 1.1902 | -121.8063 | 120.9824 | -1.268 | 121.2753 | 122.5159 | -0.9613 | -0.31586 | -0.01831 | 0.29297 | 121.4859 | 121.8384 | 121.7377 | 121.431 | 121.2753 | 122.6807 | 121.9116 | -0.31586 | 121.431 | 121.2753 | 121.9116 | 121.7377 | 122.6807 | -1.7166 | -123.0148
4072.9062 | 122.8912 | -121.4951 | 1.2039 | -0.072174 | -0.006383 | -0.010431 | 0.019709 | -0.0077482 | -0.00093346 | 0.0091795 | -0.21973 | -0.041199 | -0.49439 | 1.0391 | 0.24719 | 0.39825 | -0.013733 | 0.34332 | 1.2268 | -121.7834 | 121.0007 | -1.2451 | 121.2753 | 122.5342 | -0.95673 | -0.28839 | 0.022889 | 0.27466 | 121.4813 | 121.8384 | 121.7422 | 121.4539 | 121.2753 | 122.7219 | 121.8933 | -0.28839 | 121.4539 | 121.2753 | 121.8933 | 121.7422 | 122.7219 | -1.6983 | -122.9874
4073.9062 | 122.9004 | -121.4996 | 1.2039 | 0.0041197 | -0.0023242 | -0.014063 | 0.019922 | -0.0058256 | 0.00013454 | 0.0091795 | -0.22888 | -0.059509 | -0.48065 | 1.0071 | 0.24719 | 0.40283 | 0.018311 | 0.33875 | 1.1993 | -121.7926 | 121.019 | -1.2634 | 121.2708 | 122.5067 | -0.95673 | -0.29297 | -0.004577 | 0.25177 | 121.5179 | 121.8384 | 121.7468 | 121.4401 | 121.2708 | 122.699 | 121.9025 | -0.29297 | 121.4401 | 121.2708 | 121.9025 | 121.7468 | 122.699 | -1.6846 | -122.9965
4074.9062 | 122.905 | -121.5042 | 1.1948 | -0.049286 | -0.004674 | -0.0089358 | 0.020777 | -0.008389 | -0.0011471 | 0.0068295 | -0.2243 | -0.032043 | -0.49439 | 0.99792 | 0.24261 | 0.41199 | -0.004578 | 0.33417 | 1.2039 | -121.7834 | 121.0098 | -1.2268 | 121.2799 | 122.5021 | -0.95215 | -0.27924 | 0.009155 | 0.27008 | 121.4996 | 121.8384 | 121.7468 | 121.4722 | 121.2799 | 122.7081 | 121.9162 | -0.27924 | 121.4722 | 121.2799 | 121.9162 | 121.7468 | 122.7081 | -1.6891 | -122.9782
4075.9062 | 122.7814 | -121.5546 | 1.2268 | -0.20187 | -0.001256 | -0.013636 | 0.024836 | -0.008389 | 0.00077554 | 0.0083249 | -0.25177 | 0.004578 | -0.53101 | 0.92468 | 0.13275 | 0.27466 | 0.1831 | 0.21057 | 1.2497 | -121.8613 | 121.0236 | -1.2222 | 121.3028 | 122.4792 | -1.0941 | -0.3067 | 0.022888 | 0.27924 | 121.7377 | 121.7651 | 121.6873 | 121.5591 | 121.3028 | 122.8043 | 121.8292 | -0.3067 | 121.5591 | 121.3028 | 121.8292 | 121.6873 | 122.8043 | -1.7578 | -123.0881
4076.9219 | 122.8088 | -121.5179 | 1.236 | -0.13321 | -0.00061524 | -0.0078678 | 0.027399 | -0.0045438 | -0.00050626 | 0.0085385 | -0.21515 | 0 | -0.50812 | 0.97046 | 0.19226 | 0.32501 | 0.13275 | 0.23804 | 1.2451 | -121.8567 | 121.0098 | -1.236 | 121.3028 | 122.4884 | -1.0437 | -0.33875 | 0.009155 | 0.29297 | 121.6507 | 121.756 | 121.7102 | 121.5179 | 121.3028 | 122.7631 | 121.843 | -0.33875 | 121.5179 | 121.3028 | 121.843 | 121.7102 | 122.7631 | -1.7441 | -123.0927
4077.9062 | 122.9095 | -121.4584 | 1.2131 | -0.026398 | -0.0059558 | -0.010645 | 0.020777 | -0.0064664 | -0.0017881 | 0.010247 | -0.20599 | -0.054932 | -0.49896 | 1.0391 | 0.25635 | 0.43488 | -0.027466 | 0.34332 | 1.236 | -121.7422 | 120.9595 | -1.268 | 121.2524 | 122.4976 | -0.95673 | -0.28381 | 0.022888 | 0.29297 | 121.431 | 121.8018 | 121.7148 | 121.4035 | 121.2524 | 122.6944 | 121.8933 | -0.28381 | 121.4035 | 121.2524 | 121.8933 | 121.7148 | 122.6944 | -1.712 | -122.9553
4078.9062 | 122.905 | -121.4767 | 1.2085 | -0.018768 | -0.0044604 | -0.014276 | 0.020991 | -0.0058256 | -0.0024289 | 0.010247 | -0.23346 | -0.041199 | -0.49896 | 1.0483 | 0.25635 | 0.43945 | -0.018311 | 0.35248 | 1.2177 | -121.7743 | 120.9778 | -1.2497 | 121.2433 | 122.525 | -0.95215 | -0.29755 | 0.009155 | 0.2655 | 121.4584 | 121.8292 | 121.7331 | 121.4355 | 121.2433 | 122.6944 | 121.9162 | -0.29755 | 121.4355 | 121.2433 | 121.9162 | 121.7331 | 122.6944 | -1.7075 | -122.9828
4079.9062 | 122.8867 | -121.463 | 1.2451 | -0.041657 | -0.0057422 | -0.015345 | 0.019922 | -0.0060392 | -0.00093346 | 0.0089657 | -0.21057 | -0.045776 | -0.50354 | 1.0529 | 0.25635 | 0.43945 | -0.018311 | 0.34332 | 1.2589 | -121.7697 | 120.9595 | -1.2909 | 121.2524 | 122.5159 | -0.98877 | -0.3067 | 0.013733 | 0.29297 | 121.4447 | 121.8063 | 121.7194 | 121.4172 | 121.2524 | 122.7219 | 121.9025 | -0.3067 | 121.4172 | 121.2524 | 121.9025 | 121.7194 | 122.7219 | -1.7487 | -123.0148
4080.9062 | 122.8226 | -121.4905 | 1.2405 | -0.095062 | 0.0010938 | -0.010218 | 0.029963 | -0.0045438 | -0.0015745 | 0.0089657 | -0.19226 | 0.009155 | -0.50812 | 1.0208 | 0.1831 | 0.34332 | 0.073242 | 0.23346 | 1.2909 | -121.8338 | 120.9824 | -1.2314 | 121.2982 | 122.5113 | -1.0574 | -0.34332 | 0.050354 | 0.31586 | 121.5637 | 121.7239 | 121.6736 | 121.4996 | 121.2982 | 122.7814 | 121.8338 | -0.34332 | 121.4996 | 121.2982 | 121.8338 | 121.6736 | 122.7814 | -1.7487 | -123.0743
4081.9219 | 122.7631 | -121.4767 | 1.268 | 0.065155 | 2.5564e-05 | -0.0063724 | 0.027399 | -0.0036892 | 0.00034814 | 0.0093931 | -0.23346 | 0 | -0.53558 | 0.94757 | 0.14191 | 0.3067 | 0.11902 | 0.17395 | 1.2863 | -121.8246 | 120.9412 | -1.268 | 121.2433 | 122.4243 | -1.1261 | -0.3479 | 0.018311 | 0.30212 | 121.5958 | 121.6507 | 121.6187 | 121.4767 | 121.2433 | 122.7631 | 121.7834 | -0.3479 | 121.4767 | 121.2433 | 121.7834 | 121.6187 | 122.7631 | -1.8036 | -123.0927
4082.9062 | 122.905 | -121.4355 | 1.2451 | -0.072174 | -0.0031786 | -0.0080814 | 0.016291 | -0.0051846 | -0.0013609 | 0.0089657 | -0.20142 | -0.036621 | -0.48523 | 1.0529 | 0.27466 | 0.44403 | -0.018311 | 0.3479 | 1.2543 | -121.7606 | 120.9503 | -1.2817 | 121.2341 | 122.4884 | -0.97046 | -0.32501 | 0.009155 | 0.28381 | 121.4172 | 121.7834 | 121.7102 | 121.3989 | 121.2341 | 122.6898 | 121.8796 | -0.32501 | 121.3989 | 121.2341 | 121.8796 | 121.7102 | 122.6898 | -1.7303 | -123.0057
4083.9062 | 122.9141 | -121.4401 | 1.2314 | -0.056915 | -0.0055286 | -0.011286 | 0.019495 | -0.0086026 | -0.0020017 | 0.0089657 | -0.2243 | -0.032043 | -0.49896 | 1.0529 | 0.25177 | 0.4303 | -0.013733 | 0.33875 | 1.236 | -121.7422 | 120.9412 | -1.2634 | 121.2158 | 122.493 | -0.97961 | -0.30212 | 0.004578 | 0.27466 | 121.4264 | 121.7789 | 121.6919 | 121.4081 | 121.2158 | 122.6761 | 121.8704 | -0.30212 | 121.4081 | 121.2158 | 121.8704 | 121.6919 | 122.6761 | -1.7303 | -122.9736
4084.9062 | 122.905 | -121.4447 | 1.2222 | -0.079803 | -0.003606 | -0.010858 | 0.021418 | -0.0077482 | -0.0024289 | 0.0085385 | -0.23346 | -0.045776 | -0.48981 | 1.0345 | 0.25635 | 0.43945 | -0.018311 | 0.32959 | 1.2543 | -121.7743 | 120.9549 | -1.268 | 121.2112 | 122.4792 | -0.96588 | -0.32959 | 0.032043 | 0.25635 | 121.4264 | 121.7743 | 121.7011 | 121.3989 | 121.2112 | 122.699 | 121.8842 | -0.32959 | 121.3989 | 121.2112 | 121.8842 | 121.7011 | 122.699 | -1.712 | -122.9965
4085.9219 | 122.818 | -121.4813 | 1.2497 | -0.14084 | -0.002965 | -0.01214 | 0.028681 | -0.0058256 | 0.00013454 | 0.0085385 | -0.19684 | 0.004578 | -0.52185 | 0.99792 | 0.19226 | 0.34332 | 0.10071 | 0.24261 | 1.268 | -121.843 | 120.9595 | -1.2451 | 121.2845 | 122.4792 | -1.0574 | -0.36163 | 0.01831 | 0.32501 | 121.582 | 121.7239 | 121.6736 | 121.4859 | 121.2845 | 122.7493 | 121.8246 | -0.36163 | 121.4859 | 121.2845 | 121.8246 | 121.6736 | 122.7493 | -1.7715 | -123.0927
4086.9219 | 122.8134 | -121.4447 | 1.268 | -0.13321 | -0.0016834 | -0.0078678 | 0.026117 | -0.0041166 | -0.0015745 | 0.0074705 | -0.21515 | 0.004578 | -0.52185 | 1.0208 | 0.19226 | 0.35706 | 0.12817 | 0.26093 | 1.3046 | -121.788 | 120.9229 | -1.2634 | 121.2296 | 122.4655 | -1.0757 | -0.34332 | 0.036621 | 0.3067 | 121.5729 | 121.7056 | 121.637 | 121.4493 | 121.2296 | 122.7493 | 121.8018 | -0.34332 | 121.4493 | 121.2296 | 121.8018 | 121.637 | 122.7493 | -1.7899 | -123.056
4087.9062 | 122.9233 | -121.431 | 1.2497 | -0.072174 | -0.0038196 | -0.011286 | 0.020777 | -0.0036892 | -0.00071986 | 0.0083249 | -0.19684 | -0.050354 | -0.49896 | 1.0666 | 0.27924 | 0.46234 | -0.027466 | 0.36163 | 1.2772 | -121.7331 | 120.932 | -1.3 | 121.2341 | 122.4976 | -0.97046 | -0.30212 | 0.027466 | 0.30212 | 121.4035 | 121.7926 | 121.7102 | 121.3806 | 121.2341 | 122.7081 | 121.8933 | -0.30212 | 121.3806 | 121.2341 | 121.8933 | 121.7102 | 122.7081 | -1.7487 | -122.9828
4088.9062 | 122.8821 | -121.4401 | 1.2405 | 0.019379 | -0.0057422 | -0.01214 | 0.020136 | -0.0079618 | -0.0017881 | 0.012384 | -0.25177 | -0.045776 | -0.49439 | 1.0117 | 0.23346 | 0.4303 | 0.004578 | 0.31128 | 1.2405 | -121.7834 | 120.9457 | -1.2863 | 121.1884 | 122.4518 | -1.0071 | -0.34332 | 0 | 0.24262 | 121.4447 | 121.7514 | 121.6736 | 121.3943 | 121.1884 | 122.6807 | 121.8704 | -0.34332 | 121.3943 | 121.1884 | 121.8704 | 121.6736 | 122.6807 | -1.7349 | -123.024
4089.9062 | 122.905 | -121.4676 | 1.2268 | -0.11032 | -0.003606 | -0.011072 | 0.020777 | -0.0090298 | 0.00034814 | 0.0098203 | -0.19226 | -0.027466 | -0.48981 | 1.0529 | 0.27008 | 0.45776 | -0.022888 | 0.35706 | 1.2405 | -121.7606 | 120.9778 | -1.2543 | 121.2753 | 122.5204 | -0.95673 | -0.29297 | 0.013733 | 0.29755 | 121.4447 | 121.8246 | 121.7377 | 121.4401 | 121.2753 | 122.7081 | 121.9254 | -0.29297 | 121.4401 | 121.2753 | 121.9254 | 121.7377 | 122.7081 | -1.7166 | -122.9874
4090.9062 | 122.7768 | -121.5042 | 1.2451 | -0.25528 | -0.002965 | -0.0072268 | 0.02569 | -0.0068936 | -0.00050626 | 0.010247 | -0.26093 | 0.004578 | -0.50354 | 0.94757 | 0.14191 | 0.32501 | 0.15564 | 0.22888 | 1.2863 | -121.8246 | 121.0007 | -1.2405 | 121.2433 | 122.4518 | -1.1032 | -0.32044 | 0.041199 | 0.24261 | 121.6599 | 121.7331 | 121.6461 | 121.5088 | 121.2433 | 122.7905 | 121.8292 | -0.32044 | 121.5088 | 121.2433 | 121.8292 | 121.6461 | 122.7905 | -1.7487 | -123.0698
4091.9219 | 122.7768 | -121.4951 | 1.2955 | 0.034637 | 0.00066656 | -0.0044498 | 0.031458 | -0.004971 | -0.0024289 | 0.0078977 | -0.19684 | 0.009155 | -0.50812 | 0.97961 | 0.15106 | 0.31128 | 0.11902 | 0.19226 | 1.3092 | -121.788 | 120.9869 | -1.2863 | 121.2982 | 122.4747 | -1.1444 | -0.29297 | 0.013733 | 0.31128 | 121.6141 | 121.6873 | 121.6461 | 121.5042 | 121.2982 | 122.8043 | 121.8063 | -0.29297 | 121.5042 | 121.2982 | 121.8063 | 121.6461 | 122.8043 | -1.8036 | -123.0835
4092.9062 | 122.905 | -121.4355 | 1.2543 | -0.056915 | -0.0051012 | -0.011499 | 0.019709 | -0.0062528 | -0.0011471 | 0.010888 | -0.20599 | -0.036621 | -0.4715 | 1.0803 | 0.2655 | 0.44861 | -0.018311 | 0.34332 | 1.2955 | -121.7148 | 120.9641 | -1.2909 | 121.2296 | 122.5159 | -0.98877 | -0.27924 | 0.041199 | 0.2655 | 121.4172 | 121.7789 | 121.701 | 121.3989 | 121.2296 | 122.731 | 121.8842 | -0.27924 | 121.3989 | 121.2296 | 121.8842 | 121.701 | 122.731 | -1.7258 | -122.9691
4093.9062 | 122.9187 | -121.4493 | 1.2497 | -0.064545 | -0.0048876 | -0.0089358 | 0.022486 | -0.0081754 | -7.9062e-05 | 0.0096067 | -0.21515 | -0.027466 | -0.49439 | 1.0529 | 0.25177 | 0.44861 | -0.013733 | 0.3479 | 1.268 | -121.7468 | 120.9549 | -1.2772 | 121.2341 | 122.5021 | -0.99792 | -0.29755 | 0.01831 | 0.27924 | 121.4355 | 121.7972 | 121.701 | 121.4218 | 121.2341 | 122.7173 | 121.8979 | -0.29755 | 121.4218 | 121.2341 | 121.8979 | 121.701 | 122.7173 | -1.7441 | -122.9965
4094.9062 | 122.8821 | -121.4127 | 1.2634 | 0.0041197 | -0.0044604 | -0.012781 | 0.022699 | -0.0062528 | -0.0011471 | 0.0091795 | -0.24719 | -0.032043 | -0.49896 | 1.0345 | 0.21973 | 0.39825 | 0.013733 | 0.31128 | 1.2634 | -121.7606 | 120.9137 | -1.2955 | 121.1655 | 122.4472 | -1.0437 | -0.3479 | 0 | 0.25177 | 121.4264 | 121.7239 | 121.6324 | 121.3806 | 121.1655 | 122.6761 | 121.8109 | -0.3479 | 121.3806 | 121.1655 | 121.8109 | 121.6324 | 122.6761 | -1.7624 | -123.024
4095.9062 | 122.7814 | -121.4539 | 1.3138 | -0.25528 | -0.003606 | -0.0091494 | 0.026331 | -0.00668 | 0.00098914 | 0.0078977 | -0.24719 | 0.018311 | -0.50354 | 0.98419 | 0.12817 | 0.34332 | 0.16937 | 0.21973 | 1.3367 | -121.7926 | 120.9503 | -1.2955 | 121.2067 | 122.438 | -1.1856 | -0.33875 | 0.022888 | 0.25635 | 121.6232 | 121.6736 | 121.582 | 121.4722 | 121.2067 | 122.7905 | 121.7972 | -0.33875 | 121.4722 | 121.2067 | 121.7972 | 121.582 | 122.7905 | -1.8173 | -123.1064
4096.9062 | 122.905 | -121.4355 | 1.2589 | -0.17136 | -0.0042468 | -0.013208 | 0.023127 | -0.0064664 | -0.0026425 | 0.0098203 | -0.16479 | -0.054932 | -0.47607 | 1.0849 | 0.26093 | 0.4715 | -0.009155 | 0.36163 | 1.2817 | -121.7102 | 120.9595 | -1.3138 | 121.2708 | 122.5204 | -0.99792 | -0.27466 | 0.022888 | 0.31128 | 121.4264 | 121.7972 | 121.6965 | 121.3806 | 121.2708 | 122.7173 | 121.907 | -0.27466 | 121.3806 | 121.2708 | 121.907 | 121.6965 | 122.7173 | -1.7349 | -122.9691
4097.9062 | 122.9279 | -121.3898 | 1.2634 | -0.13321 | -0.0055286 | -0.010645 | 0.020991 | -0.0036892 | -0.0020017 | 0.0074705 | -0.16937 | -0.045776 | -0.49439 | 1.0803 | 0.27008 | 0.45776 | -0.018311 | 0.3479 | 1.2817 | -121.7239 | 120.8954 | -1.3092 | 121.2204 | 122.4701 | -0.99335 | -0.33417 | 0.01831 | 0.32501 | 121.3715 | 121.7377 | 121.6599 | 121.344 | 121.2204 | 122.6715 | 121.8475 | -0.33417 | 121.344 | 121.2204 | 121.8475 | 121.6599 | 122.6715 | -1.7578 | -122.9874
4098.9062 | 122.937 | -121.4447 | 1.2314 | -0.13321 | -0.004674 | -0.014276 | 0.020777 | -0.0068936 | -0.0011471 | 0.010461 | -0.16937 | -0.045776 | -0.46234 | 1.0941 | 0.27008 | 0.46692 | -0.013733 | 0.36163 | 1.2634 | -121.756 | 120.9824 | -1.2772 | 121.2753 | 122.5388 | -0.9613 | -0.31128 | 0.032044 | 0.29297 | 121.431 | 121.8063 | 121.7148 | 121.3989 | 121.2753 | 122.7081 | 121.9116 | -0.31128 | 121.3989 | 121.2753 | 121.9116 | 121.7148 | 122.7081 | -1.6937 | -122.9874
4099.9062 | 122.9553 | -121.4355 | 1.2314 | -0.13321 | -0.0031786 | -0.0078678 | 0.022486 | -0.0071072 | -0.0028561 | 0.010034 | -0.17395 | -0.050354 | -0.47607 | 1.0895 | 0.29297 | 0.46692 | -0.018311 | 0.3479 | 1.2497 | -121.7789 | 120.9595 | -1.2817 | 121.2616 | 122.525 | -0.93841 | -0.34332 | 0.018311 | 0.30212 | 121.4172 | 121.7834 | 121.7285 | 121.3852 | 121.2616 | 122.6852 | 121.9025 | -0.34332 | 121.3852 | 121.2616 | 121.9025 | 121.7285 | 122.6852 | -1.7075 | -123.0103
4100.9062 | 122.9233 | -121.463 | 1.236 | -0.079803 | -0.0023242 | -0.010004 | 0.019068 | -0.0073208 | -0.00050626 | 0.0096067 | -0.16937 | -0.054932 | -0.47607 | 1.0941 | 0.27466 | 0.48065 | -0.032043 | 0.34332 | 1.2314 | -121.7422 | 120.9869 | -1.2909 | 121.2936 | 122.5571 | -0.9613 | -0.27924 | -0.004578 | 0.3067 | 121.431 | 121.8063 | 121.7377 | 121.4081 | 121.2936 | 122.6944 | 121.9437 | -0.27924 | 121.4081 | 121.2936 | 121.9437 | 121.7377 | 122.6944 | -1.712 | -122.9782
4101.9062 | 122.9187 | -121.4722 | 1.2268 | -0.14847 | -0.0044604 | -0.013849 | 0.019709 | -0.0088162 | -0.0037107 | 0.0098203 | -0.16022 | -0.036621 | -0.45776 | 1.0803 | 0.25177 | 0.46234 | -0.032043 | 0.36163 | 1.2451 | -121.7606 | 121.0144 | -1.2634 | 121.312 | 122.5525 | -0.97504 | -0.28839 | 0.01831 | 0.29755 | 121.4401 | 121.8338 | 121.7239 | 121.4355 | 121.312 | 122.7173 | 121.9345 | -0.28839 | 121.4355 | 121.312 | 121.9345 | 121.7239 | 122.7173 | -1.6846 | -122.9874
4102.9062 | 122.9324 | -121.4447 | 1.2222 | -0.072174 | -0.0033922 | -0.010858 | 0.020777 | -0.0075344 | -0.00093346 | 0.0072569 | -0.17853 | -0.041199 | -0.48523 | 1.0757 | 0.27924 | 0.46692 | -0.032043 | 0.35706 | 1.2405 | -121.756 | 120.9595 | -1.2634 | 121.2662 | 122.5204 | -0.94299 | -0.31128 | 0.018311 | 0.3067 | 121.4127 | 121.8018 | 121.7239 | 121.4035 | 121.2662 | 122.6852 | 121.9116 | -0.31128 | 121.4035 | 121.2662 | 121.9116 | 121.7239 | 122.6852 | -1.7075 | -122.9782
4103.9062 | 122.905 | -121.463 | 1.2405 | -0.21713 | -0.0042468 | -0.010645 | 0.020991 | -0.0056118 | -0.00093346 | 0.0096067 | -0.17395 | -0.032043 | -0.4715 | 1.0574 | 0.25635 | 0.42114 | 0.004578 | 0.34332 | 1.2543 | -121.756 | 120.9915 | -1.2726 | 121.2891 | 122.5204 | -0.98419 | -0.29297 | 0.013732 | 0.29755 | 121.4676 | 121.8063 | 121.7194 | 121.431 | 121.2891 | 122.7173 | 121.8842 | -0.29297 | 121.431 | 121.2891 | 121.8842 | 121.7194 | 122.7173 | -1.712 | -122.9965
4104.9062 | 122.8958 | -121.4493 | 1.2314 | -0.18662 | -0.0040332 | -0.012567 | 0.022059 | -0.0053982 | -0.0020017 | 0.0074705 | -0.17395 | -0.036621 | -0.48523 | 1.0666 | 0.25635 | 0.43488 | 0 | 0.34332 | 1.2817 | -121.7651 | 120.9641 | -1.268 | 121.2753 | 122.5159 | -0.97504 | -0.31586 | 0.050354 | 0.31128 | 121.4493 | 121.7926 | 121.7056 | 121.4127 | 121.2753 | 122.731 | 121.8842 | -0.31586 | 121.4127 | 121.2753 | 121.8842 | 121.7056 | 122.731 | -1.7166 | -122.9965
4105.9219 | 122.8226 | -121.5134 | 1.2543 | -0.11795 | -0.00061524 | -0.0091494 | 0.029963 | -0.0045438 | -0.0045651 | 0.0085385 | -0.17853 | 0.018311 | -0.49896 | 0.99335 | 0.1831 | 0.33875 | 0.086975 | 0.24719 | 1.2543 | -121.8475 | 121.0144 | -1.236 | 121.3348 | 122.5067 | -1.0712 | -0.33417 | 0 | 0.32043 | 121.6003 | 121.7606 | 121.6965 | 121.5317 | 121.3348 | 122.7676 | 121.8521 | -0.33417 | 121.5317 | 121.3348 | 121.8521 | 121.6965 | 122.7676 | -1.7532 | -123.1018
4106.9062 | 122.9095 | -121.4676 | 1.1993 | -0.17899 | -0.0048876 | -0.011927 | 0.019709 | -0.0047574 | 0.00013454 | 0.0096067 | -0.18768 | -0.027466 | -0.49439 | 1.0712 | 0.27924 | 0.43488 | -0.009155 | 0.3479 | 1.2222 | -121.7651 | 120.9732 | -1.2268 | 121.2799 | 122.5388 | -0.9201 | -0.29755 | 0.022888 | 0.3067 | 121.4584 | 121.8155 | 121.7468 | 121.4401 | 121.2799 | 122.6898 | 121.9025 | -0.29755 | 121.4401 | 121.2799 | 121.9025 | 121.7468 | 122.6898 | -1.6937 | -122.9645
4107.9062 | 122.8592 | -121.5042 | 1.2085 | -0.24765 | -0.0059558 | -0.013849 | 0.022486 | -0.004971 | -0.00093346 | 0.0072569 | -0.17395 | -0.045776 | -0.45319 | 1.0208 | 0.25635 | 0.42114 | 0.022888 | 0.32501 | 1.236 | -121.7834 | 121.051 | -1.2543 | 121.3303 | 122.525 | -0.95215 | -0.27924 | 0.027466 | 0.27924 | 121.5271 | 121.8292 | 121.7606 | 121.4584 | 121.3303 | 122.7402 | 121.9254 | -0.27924 | 121.4584 | 121.3303 | 121.9254 | 121.7606 | 122.7402 | -1.6617 | -122.9919
4108.9062 | 122.9187 | -121.4951 | 1.1993 | -0.13321 | -0.0068102 | -0.011713 | 0.02334 | -0.0051846 | -0.0028561 | 0.0074705 | -0.1831 | -0.064087 | -0.5127 | 1.0391 | 0.27924 | 0.43488 | -0.022888 | 0.3479 | 1.2131 | -121.7789 | 120.9824 | -1.2634 | 121.312 | 122.5342 | -0.9201 | -0.28381 | 0.013733 | 0.32959 | 121.4722 | 121.843 | 121.7743 | 121.431 | 121.312 | 122.7081 | 121.9299 | -0.28381 | 121.431 | 121.312 | 121.9299 | 121.7743 | 122.7081 | -1.712 | -122.9782
4109.9062 | 122.9279 | -121.4813 | 1.2177 | -0.14847 | -0.0040332 | -0.018549 | 0.020991 | -0.0071072 | -0.00029266 | 0.0098203 | -0.18768 | -0.054932 | -0.48981 | 1.062 | 0.28839 | 0.46234 | -0.045776 | 0.38452 | 1.2314 | -121.7834 | 120.9915 | -1.2726 | 121.2936 | 122.5433 | -0.92926 | -0.30212 | 0.013733 | 0.30212 | 121.4355 | 121.8658 | 121.7697 | 121.4264 | 121.2936 | 122.7127 | 121.9437 | -0.30212 | 121.4264 | 121.2936 | 121.9437 | 121.7697 | 122.7127 | -1.7075 | -123.0011
4110.9062 | 122.7951 | -121.5271 | 1.2497 | -0.20187 | -0.001897 | -0.0091494 | 0.025049 | -0.0058256 | -0.0034971 | 0.010675 | -0.2655 | 0.004578 | -0.54016 | 0.95215 | 0.15106 | 0.29297 | 0.15106 | 0.21515 | 1.268 | -121.8521 | 120.9869 | -1.2451 | 121.2616 | 122.4792 | -1.0986 | -0.32501 | 0.01831 | 0.27466 | 121.6782 | 121.7422 | 121.6782 | 121.5317 | 121.2616 | 122.7951 | 121.8201 | -0.32501 | 121.5317 | 121.2616 | 121.8201 | 121.6782 | 122.7951 | -1.7899 | -123.1018
4111.9062 | 122.9095 | -121.4539 | 1.2268 | -0.18662 | -0.0044604 | -0.0080814 | 0.023127 | -0.0068936 | 0.00034814 | 0.010461 | -0.19226 | -0.050354 | -0.49439 | 1.0574 | 0.27466 | 0.44403 | -0.009155 | 0.34332 | 1.2405 | -121.7606 | 120.9595 | -1.2772 | 121.2616 | 122.5113 | -0.95215 | -0.3067 | 0.013733 | 0.30212 | 121.4447 | 121.7972 | 121.7285 | 121.4035 | 121.2616 | 122.6944 | 121.8979 | -0.3067 | 121.4035 | 121.2616 | 121.8979 | 121.7285 | 122.6944 | -1.7212 | -122.9874
4112.9062 | 122.9004 | -121.4584 | 1.2543 | -0.18662 | -0.005315 | -0.010431 | 0.021418 | -0.0073208 | -0.0022153 | 0.0076841 | -0.20142 | -0.073242 | -0.51727 | 1.062 | 0.27924 | 0.44403 | -0.004578 | 0.35706 | 1.2817 | -121.7468 | 120.9412 | -1.3275 | 121.257 | 122.5204 | -0.97504 | -0.28839 | 0.027466 | 0.31586 | 121.4539 | 121.8155 | 121.7377 | 121.3852 | 121.257 | 122.7402 | 121.9025 | -0.28839 | 121.3852 | 121.257 | 121.9025 | 121.7377 | 122.7402 | -1.7715 | -123.0011
4113.9062 | 122.9187 | -121.4584 | 1.2314 | -0.16373 | -0.0038196 | -0.0097904 | 0.019495 | -0.0092434 | -0.0011471 | 0.0083249 | -0.17395 | -0.045776 | -0.48981 | 1.0803 | 0.25635 | 0.44403 | -0.004578 | 0.36163 | 1.2589 | -121.7606 | 120.9686 | -1.2772 | 121.2845 | 122.5388 | -0.97504 | -0.30212 | 0.027466 | 0.31586 | 121.4539 | 121.8201 | 121.7148 | 121.4127 | 121.2845 | 122.7173 | 121.9025 | -0.30212 | 121.4127 | 121.2845 | 121.9025 | 121.7148 | 122.7173 | -1.7212 | -122.9919
4114.9062 | 122.9416 | -121.4584 | 1.2451 | -0.13321 | -0.0044604 | -0.010431 | 0.021418 | -0.0077482 | -0.00071986 | 0.0083249 | -0.18768 | -0.054932 | -0.47607 | 1.0849 | 0.27924 | 0.46692 | -0.009155 | 0.3479 | 1.2543 | -121.7651 | 120.9824 | -1.3 | 121.2708 | 122.5433 | -0.96588 | -0.3067 | 0.009155 | 0.28839 | 121.4493 | 121.8063 | 121.7377 | 121.4035 | 121.2708 | 122.7127 | 121.9254 | -0.3067 | 121.4035 | 121.2708 | 121.9254 | 121.7377 | 122.7127 | -1.7212 | -123.0103
4115.9062 | 122.7997 | -121.5042 | 1.2726 | -0.026398 | -0.0010424 | -0.0091494 | 0.030604 | -0.0051846 | -0.0013609 | 0.0083249 | -0.21057 | -0.013733 | -0.48981 | 0.99792 | 0.17853 | 0.3479 | 0.086975 | 0.22888 | 1.2863 | -121.8201 | 121.0144 | -1.2863 | 121.2936 | 122.5021 | -1.0941 | -0.31586 | 0.013733 | 0.27924 | 121.5912 | 121.7331 | 121.6827 | 121.4905 | 121.2936 | 122.7905 | 121.8521 | -0.31586 | 121.4905 | 121.2936 | 121.8521 | 121.6827 | 122.7905 | -1.7624 | -123.0927
4116.9062 | 122.9095 | -121.463 | 1.236 | -0.049286 | -0.0040332 | -0.010004 | 0.017573 | -0.004971 | -0.00050626 | 0.0091795 | -0.2243 | -0.041199 | -0.48981 | 1.0529 | 0.26093 | 0.45319 | -0.022888 | 0.35706 | 1.2589 | -121.7422 | 120.9732 | -1.2772 | 121.2387 | 122.5159 | -0.97504 | -0.27924 | 0.022888 | 0.2655 | 121.4401 | 121.8201 | 121.7239 | 121.4218 | 121.2387 | 122.7219 | 121.9162 | -0.27924 | 121.4218 | 121.2387 | 121.9162 | 121.7239 | 122.7219 | -1.7258 | -122.9782
4117.9062 | 122.9324 | -121.4539 | 1.2268 | -0.11795 | -0.0025378 | -0.01449 | 0.023554 | -0.0068936 | -0.0037107 | 0.010461 | -0.21057 | -0.082397 | -0.51727 | 1.0666 | 0.28381 | 0.43488 | -0.013733 | 0.36163 | 1.2497 | -121.7743 | 120.9366 | -1.3092 | 121.2433 | 122.5204 | -0.94299 | -0.32044 | 0.022888 | 0.3067 | 121.4401 | 121.8155 | 121.7377 | 121.3715 | 121.2433 | 122.7036 | 121.8887 | -0.32044 | 121.3715 | 121.2433 | 121.8887 | 121.7377 | 122.7036 | -1.7441 | -123.0011
4118.9062 | 122.9416 | -121.4584 | 1.2589 | -0.14084 | -0.0038196 | -0.010431 | 0.023554 | -0.0086026 | -0.0022153 | 0.0093931 | -0.23804 | -0.10529 | -0.51727 | 1.0849 | 0.27008 | 0.44403 | -0.009155 | 0.35248 | 1.2497 | -121.7651 | 120.9412 | -1.3641 | 121.2204 | 122.5433 | -0.98877 | -0.3067 | -0.009155 | 0.27924 | 121.4493 | 121.8109 | 121.7285 | 121.3531 | 121.2204 | 122.7081 | 121.9025 | -0.3067 | 121.3531 | 121.2204 | 121.9025 | 121.7285 | 122.7081 | -1.7761 | -123.024
4119.9062 | 122.9279 | -121.4584 | 1.2589 | -0.072174 | -0.005315 | -0.011713 | 0.020777 | -0.0081754 | -0.0017881 | 0.0098203 | -0.2243 | -0.10986 | -0.53558 | 1.0712 | 0.28839 | 0.44403 | -0.022888 | 0.37537 | 1.2589 | -121.7468 | 120.9229 | -1.3687 | 121.2341 | 122.5296 | -0.97046 | -0.28839 | 0 | 0.31128 | 121.4355 | 121.8338 | 121.7468 | 121.3486 | 121.2341 | 122.7173 | 121.9025 | -0.28839 | 121.3486 | 121.2341 | 121.9025 | 121.7468 | 122.7173 | -1.7944 | -123.0057
4120.9219 | 122.8134 | -121.4264 | 1.2955 | -0.10269 | -0.00061524 | -0.0055178 | 0.030604 | -0.0047574 | -0.0034971 | 0.0093931 | -0.23346 | -0.032043 | -0.55389 | 1.0437 | 0.20142 | 0.3479 | 0.086975 | 0.25177 | 1.3504 | -121.8018 | 120.8725 | -1.3275 | 121.1929 | 122.4701 | -1.0941 | -0.37537 | 0.054932 | 0.32044 | 121.5134 | 121.6782 | 121.6278 | 121.3943 | 121.1929 | 122.7768 | 121.7743 | -0.37537 | 121.3943 | 121.1929 | 121.7743 | 121.6278 | 122.7768 | -1.8494 | -123.0972
4121.9062 | 122.9187 | -121.3852 | 1.3046 | -0.072174 | -0.002965 | -0.013849 | 0.020563 | -0.0051846 | -0.00029266 | 0.0098203 | -0.2243 | -0.050354 | -0.49896 | 1.0986 | 0.26093 | 0.4303 | -0.013733 | 0.32959 | 1.3184 | -121.6782 | 120.8862 | -1.355 | 121.1609 | 122.4838 | -1.0437 | -0.29297 | 0.013733 | 0.27466 | 121.3715 | 121.7148 | 121.6461 | 121.3348 | 121.1609 | 122.7036 | 121.8155 | -0.29297 | 121.3348 | 121.1609 | 121.8155 | 121.6461 | 122.7036 | -1.8036 | -122.9828
4122.9062 | 122.9095 | -121.3348 | 1.3641 | -0.018768 | -0.0055286 | -0.012995 | 0.018213 | -0.0073208 | -0.00071986 | 0.0087521 | -0.21973 | -0.036621 | -0.50354 | 1.1261 | 0.25635 | 0.41199 | 0.004578 | 0.3479 | 1.3596 | -121.6599 | 120.8313 | -1.4008 | 121.1151 | 122.4609 | -1.1078 | -0.32501 | -0.004578 | 0.28381 | 121.3394 | 121.6827 | 121.5912 | 121.2982 | 121.1151 | 122.6944 | 121.7468 | -0.32501 | 121.2982 | 121.1151 | 121.7468 | 121.5912 | 122.6944 | -1.8677 | -123.024
4123.9062 | 122.9004 | -121.3486 | 1.3824 | -0.041657 | -0.0038196 | -0.011927 | 0.020777 | -0.0073208 | -0.0011471 | 0.0093931 | -0.25177 | -0.022888 | -0.49439 | 1.1307 | 0.24719 | 0.39825 | 0.018311 | 0.32501 | 1.387 | -121.6415 | 120.8542 | -1.4053 | 121.0968 | 122.4792 | -1.1353 | -0.29297 | 0.004578 | 0.24262 | 121.3669 | 121.6736 | 121.5958 | 121.3257 | 121.0968 | 122.7356 | 121.7468 | -0.29297 | 121.3257 | 121.0968 | 121.7468 | 121.5958 | 122.7356 | -1.8768 | -123.024
4124.9062 | 122.905 | -121.3165 | 1.3779 | -0.064545 | -0.0040332 | -0.010004 | 0.019495 | -0.0077482 | 0.00077554 | 0.0089657 | -0.20599 | -0.050354 | -0.50354 | 1.181 | 0.27008 | 0.42572 | -0.018311 | 0.33875 | 1.3779 | -121.6141 | 120.813 | -1.4282 | 121.1105 | 122.4976 | -1.1078 | -0.29755 | 0 | 0.29755 | 121.2982 | 121.6553 | 121.5866 | 121.2662 | 121.1105 | 122.6944 | 121.7422 | -0.29755 | 121.2662 | 121.1105 | 121.7422 | 121.5866 | 122.6944 | -1.8814 | -122.9919
4125.9062 | 122.8867 | -121.3074 | 1.355 | -0.18662 | -0.0042468 | -0.0089358 | 0.022913 | -0.0073208 | -0.0011471 | 0.0076841 | -0.17395 | -0.036621 | -0.47607 | 1.1536 | 0.2655 | 0.41657 | 0.022888 | 0.34332 | 1.3962 | -121.6461 | 120.8313 | -1.3916 | 121.1334 | 122.4609 | -1.0895 | -0.33875 | 0.041199 | 0.30212 | 121.3303 | 121.6507 | 121.5729 | 121.2708 | 121.1334 | 122.7036 | 121.7239 | -0.33875 | 121.2708 | 121.1334 | 121.7239 | 121.5729 | 122.7036 | -1.8311 | -123.0011
4126.9062 | 122.8958 | -121.3028 | 1.387 | 0.011749 | -0.0040332 | -0.013208 | 0.018641 | -0.0056118 | -0.0024289 | 0.010034 | -0.24719 | -0.045776 | -0.51727 | 1.1673 | 0.24719 | 0.40741 | 0 | 0.32044 | 1.3824 | -121.5958 | 120.7855 | -1.4328 | 121.0556 | 122.4701 | -1.1398 | -0.29297 | -0.004578 | 0.27008 | 121.3028 | 121.6232 | 121.55 | 121.257 | 121.0556 | 122.6852 | 121.7102 | -0.29297 | 121.257 | 121.0556 | 121.7102 | 121.55 | 122.6852 | -1.9043 | -122.9828
4127.9062 | 122.9004 | -121.3257 | 1.3779 | -0.049286 | -0.0044604 | -0.014063 | 0.017786 | -0.0077482 | 0.00098914 | 0.0085385 | -0.24719 | -0.050354 | -0.50812 | 1.1398 | 0.23804 | 0.39368 | 0.009155 | 0.30212 | 1.387 | -121.6415 | 120.8176 | -1.4282 | 121.0785 | 122.4655 | -1.1398 | -0.31586 | 0.009155 | 0.26093 | 121.3348 | 121.6278 | 121.5637 | 121.2753 | 121.0785 | 122.7127 | 121.7194 | -0.31586 | 121.2753 | 121.0785 | 121.7194 | 121.5637 | 122.7127 | -1.886 | -123.0194
4128.9062 | 122.8775 | -121.3348 | 1.3687 | 0.027008 | -0.0027514 | -0.013636 | 0.020563 | -0.0071072 | 0.00013454 | 0.0081113 | -0.27008 | -0.045776 | -0.52185 | 1.1215 | 0.23346 | 0.40283 | 0.022888 | 0.30212 | 1.387 | -121.6461 | 120.813 | -1.4145 | 121.0648 | 122.4564 | -1.1353 | -0.31128 | 0.018311 | 0.25177 | 121.3577 | 121.637 | 121.5683 | 121.2891 | 121.0648 | 122.7219 | 121.7377 | -0.31128 | 121.2891 | 121.0648 | 121.7377 | 121.5683 | 122.7219 | -1.8906 | -123.0148
4129.9062 | 122.8775 | -121.3394 | 1.3687 | 0.042267 | -0.0040332 | -0.01449 | 0.018641 | -0.0077482 | -0.00093346 | 0.0093931 | -0.27008 | -0.050354 | -0.5127 | 1.1215 | 0.21515 | 0.40283 | 0.018311 | 0.28839 | 1.3824 | -121.6507 | 120.8267 | -1.4191 | 121.0693 | 122.4609 | -1.1536 | -0.31128 | 0.013733 | 0.24261 | 121.3577 | 121.6278 | 121.5546 | 121.2891 | 121.0693 | 122.7219 | 121.7422 | -0.31128 | 121.2891 | 121.0693 | 121.7422 | 121.5546 | 122.7219 | -1.8814 | -123.0194
4130.9062 | 122.8775 | -121.3348 | 1.3733 | 0.034637 | -0.0021106 | -0.011713 | 0.019922 | -0.0068936 | -0.00093346 | 0.0078977 | -0.28381 | -0.054932 | -0.54016 | 1.1261 | 0.21515 | 0.37537 | 0.022888 | 0.28381 | 1.3962 | -121.6599 | 120.7947 | -1.4282 | 121.051 | 122.4609 | -1.1581 | -0.32501 | 0.022888 | 0.25635 | 121.3577 | 121.6187 | 121.55 | 121.2799 | 121.051 | 122.731 | 121.7102 | -0.32501 | 121.2799 | 121.051 | 121.7102 | 121.55 | 122.731 | -1.9135 | -123.0331
4131.9062 | 122.8775 | -121.3257 | 1.3641 | -0.011139 | -0.0044604 | -0.013208 | 0.021845 | -0.0081754 | 0.0020571 | 0.0078977 | -0.3067 | -0.064087 | -0.54474 | 1.1215 | 0.23346 | 0.38452 | 0.013733 | 0.30212 | 1.387 | -121.637 | 120.7809 | -1.4282 | 121.019 | 122.4472 | -1.1307 | -0.31128 | 0.022888 | 0.23804 | 121.3394 | 121.6278 | 121.5591 | 121.2616 | 121.019 | 122.7127 | 121.7102 | -0.31128 | 121.2616 | 121.019 | 121.7102 | 121.5591 | 122.7127 | -1.9089 | -123.0011
4132.9062 | 122.8775 | -121.2891 | 1.4099 | -0.026398 | -0.0042468 | -0.014063 | 0.021418 | -0.0073208 | -0.00093346 | 0.0072569 | -0.3067 | -0.07782 | -0.54474 | 1.1581 | 0.23804 | 0.40741 | -0.009155 | 0.28839 | 1.4374 | -121.582 | 120.7443 | -1.4877 | 120.9824 | 122.4472 | -1.1719 | -0.29297 | 0.027466 | 0.23804 | 121.2799 | 121.5775 | 121.5271 | 121.2112 | 120.9824 | 122.7264 | 121.6965 | -0.29297 | 121.2112 | 120.9824 | 121.6965 | 121.5271 | 122.7264 | -1.9547 | -122.9919
4133.9062 | 122.8683 | -121.3211 | 1.387 | -0.0035098 | -0.003606 | -0.013422 | 0.020991 | -0.0062528 | -0.0024289 | 0.0061887 | -0.3067 | -0.086975 | -0.55389 | 1.1444 | 0.22888 | 0.39825 | 0.004578 | 0.27466 | 1.4053 | -121.6187 | 120.7672 | -1.474 | 121.0144 | 122.4655 | -1.1581 | -0.29755 | 0.01831 | 0.24719 | 121.3257 | 121.5958 | 121.55 | 121.2341 | 121.0144 | 122.7264 | 121.7194 | -0.29755 | 121.2341 | 121.0144 | 121.7194 | 121.55 | 122.7264 | -1.9409 | -123.0057
4134.9062 | 122.8592 | -121.3257 | 1.4008 | 0.0041197 | -0.002965 | -0.016413 | 0.021631 | -0.0098844 | 0.00077554 | 0.0074705 | -0.30212 | -0.07782 | -0.54474 | 1.1398 | 0.21057 | 0.40283 | 0.009155 | 0.28381 | 1.3962 | -121.6049 | 120.7809 | -1.4786 | 121.0236 | 122.4655 | -1.1902 | -0.27923 | -0.004578 | 0.24261 | 121.3348 | 121.6095 | 121.5363 | 121.2479 | 121.0236 | 122.7219 | 121.7285 | -0.27923 | 121.2479 | 121.0236 | 121.7285 | 121.5363 | 122.7219 | -1.9455 | -123.0057
4135.9062 | 122.8821 | -121.3303 | 1.387 | -0.18662 | -0.0051012 | -0.0074404 | 0.023127 | -0.0086026 | -0.00093346 | 0.0074705 | -0.23804 | -0.086975 | -0.54474 | 1.181 | 0.27008 | 0.40741 | 0.032043 | 0.32501 | 1.4008 | -121.6324 | 120.7855 | -1.474 | 121.0922 | 122.5113 | -1.1169 | -0.30212 | 0.013733 | 0.3067 | 121.3623 | 121.6553 | 121.6003 | 121.2433 | 121.0922 | 122.731 | 121.7377 | -0.30212 | 121.2433 | 121.0922 | 121.7377 | 121.6003 | 122.731 | -1.9318 | -123.0194
4136.9062 | 122.8638 | -121.3211 | 1.387 | 0.088043 | -0.0038196 | -0.01214 | 0.020563 | -0.0081754 | 0.00056194 | 0.0076841 | -0.31586 | -0.10986 | -0.55389 | 1.1215 | 0.22888 | 0.3891 | 0.018311 | 0.27924 | 1.4008 | -121.6141 | 120.7672 | -1.4969 | 121.0052 | 122.4426 | -1.1581 | -0.29297 | 0.013733 | 0.23804 | 121.3394 | 121.6003 | 121.55 | 121.2112 | 121.0052 | 122.7219 | 121.7102 | -0.29297 | 121.2112 | 121.0052 | 121.7102 | 121.55 | 122.7219 | -1.9409 | -123.0011
4137.9062 | 122.8821 | -121.3074 | 1.4145 | 0.13382 | -0.0048876 | -0.012567 | 0.021631 | -0.0077482 | -0.00071986 | 0.0098203 | -0.31586 | -0.086975 | -0.54474 | 1.1307 | 0.23804 | 0.3891 | 0.004578 | 0.26093 | 1.4099 | -121.6141 | 120.7626 | -1.5015 | 120.9915 | 122.438 | -1.1765 | -0.3067 | -0.004578 | 0.22888 | 121.312 | 121.5683 | 121.5454 | 121.2204 | 120.9915 | 122.7173 | 121.6965 | -0.3067 | 121.2204 | 120.9915 | 121.6965 | 121.5454 | 122.7173 | -1.9592 | -123.0286
4138.9062 | 122.8821 | -121.2708 | 1.4465 | 0.0041197 | -0.0027514 | -0.014276 | 0.019068 | -0.0068936 | -0.0013609 | 0.0078977 | -0.30212 | -0.10529 | -0.55389 | 1.181 | 0.23346 | 0.39825 | 0.032043 | 0.28381 | 1.4557 | -121.5637 | 120.7169 | -1.5518 | 120.9686 | 122.4518 | -1.2131 | -0.29297 | 0.009155 | 0.25177 | 121.3028 | 121.5546 | 121.5042 | 121.1655 | 120.9686 | 122.7264 | 121.669 | -0.29297 | 121.1655 | 120.9686 | 121.669 | 121.5042 | 122.7264 | -2.0004 | -123.0103
4139.9062 | 122.8683 | -121.2341 | 1.442 | 0.034637 | -0.0023242 | -0.010218 | 0.019495 | -0.0088162 | -7.9062e-05 | 0.0083249 | -0.28839 | -0.07782 | -0.54016 | 1.1948 | 0.22888 | 0.38452 | 0.022888 | 0.27008 | 1.4603 | -121.5591 | 120.694 | -1.5198 | 120.9457 | 122.4289 | -1.2131 | -0.32501 | 0.01831 | 0.25177 | 121.257 | 121.5042 | 121.463 | 121.1563 | 120.9457 | 122.6944 | 121.6187 | -0.32501 | 121.1563 | 120.9457 | 121.6187 | 121.463 | 122.6944 | -1.9821 | -123.0011
4140.9062 | 122.8638 | -121.2387 | 1.4694 | -0.049286 | -0.0040332 | -0.010858 | 0.018854 | -0.0088162 | -0.0011471 | 0.011529 | -0.29297 | -0.073242 | -0.53558 | 1.2085 | 0.23346 | 0.37537 | 0.013733 | 0.27924 | 1.4969 | -121.5363 | 120.7031 | -1.5427 | 120.9457 | 122.4472 | -1.236 | -0.29755 | 0.027466 | 0.24261 | 121.2524 | 121.5179 | 121.4722 | 121.1655 | 120.9457 | 122.7356 | 121.6141 | -0.29755 | 121.1655 | 120.9457 | 121.6141 | 121.4722 | 122.7356 | -2.005 | -123.0057
4141.9062 | 122.8729 | -121.2387 | 1.506 | 0.019379 | -0.0031786 | -0.013208 | 0.019282 | -0.0075344 | -0.0011471 | 0.0087521 | -0.29297 | -0.082397 | -0.54016 | 1.2222 | 0.22888 | 0.3891 | 0.027466 | 0.27008 | 1.5106 | -121.5546 | 120.6985 | -1.5884 | 120.9457 | 122.4609 | -1.2772 | -0.31586 | 0.004578 | 0.24719 | 121.2662 | 121.5088 | 121.4676 | 121.1563 | 120.9457 | 122.7493 | 121.6278 | -0.31586 | 121.1563 | 120.9457 | 121.6278 | 121.4676 | 122.7493 | -2.0462 | -123.0606
4142.9062 | 122.8729 | -121.2158 | 1.4832 | 0.072784 | -0.004674 | -0.010645 | 0.020563 | -0.0086026 | -7.9062e-05 | 0.0055479 | -0.3067 | -0.09613 | -0.54932 | 1.2543 | 0.19226 | 0.38452 | 0.027466 | 0.27008 | 1.5289 | -121.5088 | 120.6665 | -1.5793 | 120.9091 | 122.4701 | -1.2909 | -0.29297 | 0.045777 | 0.24261 | 121.2433 | 121.4859 | 121.4081 | 121.1197 | 120.9091 | 122.7448 | 121.6003 | -0.29297 | 121.1197 | 120.9091 | 121.6003 | 121.4081 | 122.7448 | -2.0325 | -122.9919
4143.9062 | 122.8638 | -121.2067 | 1.5106 | 0.049896 | -0.0038196 | -0.012354 | 0.021418 | -0.0071072 | -0.0013609 | 0.0076841 | -0.29755 | -0.09613 | -0.54016 | 1.2405 | 0.21057 | 0.37537 | 0.013733 | 0.26093 | 1.5152 | -121.5225 | 120.6665 | -1.6068 | 120.9091 | 122.4472 | -1.3 | -0.31586 | 0.004578 | 0.24262 | 121.2204 | 121.4676 | 121.4172 | 121.1105 | 120.9091 | 122.7219 | 121.582 | -0.31586 | 121.1105 | 120.9091 | 121.582 | 121.4172 | 122.7219 | -2.0508 | -123.0331
4144.9062 | 122.8729 | -121.2341 | 1.474 | 0.080414 | -0.003606 | -0.010858 | 0.021204 | -0.0071072 | 0.00077554 | 0.0096067 | -0.29755 | -0.086975 | -0.54016 | 1.2222 | 0.21973 | 0.3891 | 0.009155 | 0.27008 | 1.5015 | -121.5454 | 120.694 | -1.561 | 120.9366 | 122.4564 | -1.2543 | -0.31128 | 0.027466 | 0.24262 | 121.2433 | 121.5042 | 121.4539 | 121.1472 | 120.9366 | 122.7356 | 121.6232 | -0.31128 | 121.1472 | 120.9366 | 121.6232 | 121.4539 | 122.7356 | -2.0142 | -123.0194
4145.9844 | 122.8317 | -121.2524 | 1.5106 | -0.095062 | -0.00082884 | -0.013849 | 0.026758 | -0.0056118 | 0.00098914 | 0.0081113 | -0.25635 | -0.059509 | -0.56305 | 1.2405 | 0.20142 | 0.35248 | 0.082397 | 0.25635 | 1.5152 | -121.6095 | 120.6894 | -1.5701 | 120.9961 | 122.493 | -1.3092 | -0.35706 | 0.004578 | 0.3067 | 121.3348 | 121.5088 | 121.4539 | 121.1929 | 120.9961 | 122.7676 | 121.6049 | -0.35706 | 121.1929 | 120.9961 | 121.6049 | 121.4539 | 122.7676 | -2.0737 | -123.1201
4146.9062 | 122.9004 | -121.2387 | 1.4648 | 0.034637 | -0.0051012 | -0.011286 | 0.016291 | -0.0047574 | -0.0013609 | 0.0098203 | -0.33417 | -0.086975 | -0.56305 | 1.2131 | 0.23804 | 0.3891 | 0.018311 | 0.27008 | 1.4877 | -121.5317 | 120.6757 | -1.5518 | 120.9045 | 122.4518 | -1.2268 | -0.29297 | 0.022888 | 0.22888 | 121.257 | 121.5088 | 121.4767 | 121.1517 | 120.9045 | 122.7264 | 121.6278 | -0.29297 | 121.1517 | 120.9045 | 121.6278 | 121.4767 | 122.7264 | -2.0279 | -122.9965
4147.9062 | 122.8729 | -121.2616 | 1.474 | -0.0035098 | -0.0057422 | -0.014276 | 0.018854 | -0.0060392 | -0.0011471 | 0.0085385 | -0.33417 | -0.091553 | -0.54474 | 1.2085 | 0.2243 | 0.39825 | 0.009155 | 0.28839 | 1.4969 | -121.5683 | 120.7169 | -1.5656 | 120.9274 | 122.4701 | -1.2497 | -0.3067 | 0.022888 | 0.21057 | 121.2708 | 121.55 | 121.4859 | 121.17 | 120.9274 | 122.7585 | 121.6599 | -0.3067 | 121.17 | 120.9274 | 121.6599 | 121.4859 | 122.7585 | -2.0187 | -123.0423
4148.9062 | 122.8683 | -121.2708 | 1.4648 | -0.026398 | -0.002965 | -0.010858 | 0.019922 | -0.0064664 | 0.0012027 | 0.011102 | -0.32501 | -0.091553 | -0.54932 | 1.1948 | 0.22888 | 0.37537 | 0.027466 | 0.27924 | 1.4648 | -121.5637 | 120.7214 | -1.5564 | 120.9457 | 122.4655 | -1.236 | -0.29297 | 0 | 0.2243 | 121.2982 | 121.55 | 121.4996 | 121.1792 | 120.9457 | 122.7356 | 121.6461 | -0.29297 | 121.1792 | 120.9457 | 121.6461 | 121.4996 | 122.7356 | -2.0142 | -123.0286
4149.9062 | 122.8683 | -121.257 | 1.4511 | -0.018768 | -0.0048876 | -0.010004 | 0.019709 | -0.008389 | -0.0026425 | 0.0083249 | -0.32044 | -0.09613 | -0.54016 | 1.1902 | 0.21515 | 0.38452 | 0.022888 | 0.28381 | 1.4557 | -121.5637 | 120.7169 | -1.5472 | 120.9366 | 122.4472 | -1.236 | -0.3067 | 0.004577 | 0.21973 | 121.2799 | 121.5408 | 121.4722 | 121.1609 | 120.9366 | 122.7127 | 121.6415 | -0.3067 | 121.1609 | 120.9366 | 121.6415 | 121.4722 | 122.7127 | -1.9913 | -123.0148
4150.9844 | 122.8363 | -121.2982 | 1.4832 | 0.0041197 | 0.0030164 | -0.0072268 | 0.031458 | -0.0053982 | -0.00093346 | 0.0078977 | -0.25635 | -0.050354 | -0.55389 | 1.1719 | 0.18768 | 0.33875 | 0.10529 | 0.23804 | 1.4832 | -121.6232 | 120.7443 | -1.5335 | 121.0419 | 122.4701 | -1.2955 | -0.32501 | 0 | 0.29755 | 121.4035 | 121.5363 | 121.4859 | 121.2479 | 121.0419 | 122.7814 | 121.637 | -0.32501 | 121.2479 | 121.0419 | 121.637 | 121.4859 | 122.7814 | -2.037 | -123.1064
4151.9062 | 122.9004 | -121.2662 | 1.442 | -0.026398 | -0.0038196 | -0.010431 | 0.018427 | -0.0064664 | -0.0028561 | 0.0089657 | -0.3067 | -0.09613 | -0.56305 | 1.2222 | 0.25635 | 0.43488 | -0.004578 | 0.31128 | 1.4648 | -121.5454 | 120.7031 | -1.5381 | 120.9595 | 122.4884 | -1.1856 | -0.27924 | 0.022888 | 0.25635 | 121.2616 | 121.5775 | 121.5225 | 121.17 | 120.9595 | 122.731 | 121.701 | -0.27924 | 121.17 | 120.9595 | 121.701 | 121.5225 | 122.731 | -2.005 | -122.9874
4152.9062 | 122.9095 | -121.2753 | 1.442 | -0.011139 | -0.0051012 | -0.013422 | 0.02035 | -0.0056118 | 0.00077554 | 0.010034 | -0.32501 | -0.10986 | -0.56305 | 1.2131 | 0.25177 | 0.41657 | 0 | 0.31128 | 1.4511 | -121.5591 | 120.7123 | -1.5518 | 120.9503 | 122.4884 | -1.1902 | -0.28381 | 0.009155 | 0.23804 | 121.2753 | 121.5866 | 121.5271 | 121.1655 | 120.9503 | 122.7264 | 121.6919 | -0.28381 | 121.1655 | 120.9503 | 121.6919 | 121.5271 | 122.7264 | -2.005 | -123.0011
4153.9062 | 122.905 | -121.2616 | 1.442 | -0.0035098 | -0.0027514 | -0.0072268 | 0.018854 | -0.0060392 | 0.0016299 | 0.0087521 | -0.30212 | -0.09613 | -0.53558 | 1.2268 | 0.24719 | 0.41657 | 0 | 0.31128 | 1.4603 | -121.5591 | 120.726 | -1.5381 | 120.9595 | 122.4884 | -1.1948 | -0.29755 | 0.01831 | 0.23346 | 121.2616 | 121.5729 | 121.5088 | 121.1655 | 120.9595 | 122.7219 | 121.6782 | -0.29755 | 121.1655 | 120.9595 | 121.6782 | 121.5088 | 122.7219 | -1.9775 | -123.0011
4154.9062 | 122.9095 | -121.2112 | 1.4832 | -0.0035098 | -0.0051012 | -0.010004 | 0.020777 | -0.0092434 | 0.0016299 | 0.010247 | -0.31586 | -0.091553 | -0.57678 | 1.236 | 0.23804 | 0.42572 | 0.009155 | 0.32501 | 1.4923 | -121.5317 | 120.6345 | -1.5747 | 120.8954 | 122.4472 | -1.2451 | -0.32043 | 0.009156 | 0.26093 | 121.2204 | 121.5363 | 121.4493 | 121.1197 | 120.8954 | 122.7036 | 121.637 | -0.32043 | 121.1197 | 120.8954 | 121.637 | 121.4493 | 122.7036 | -2.0599 | -123.0148
4155.9219 | 122.8363 | -121.2799 | 1.5198 | -0.20187 | -0.001256 | -0.011499 | 0.027399 | -0.00668 | -7.9062e-05 | 0.010888 | -0.29755 | -0.036621 | -0.56763 | 1.2039 | 0.17853 | 0.32501 | 0.15106 | 0.23346 | 1.5335 | -121.5866 | 120.7123 | -1.5564 | 120.9824 | 122.4838 | -1.3412 | -0.3067 | 0.013733 | 0.27008 | 121.431 | 121.5134 | 121.4584 | 121.2433 | 120.9824 | 122.8134 | 121.6049 | -0.3067 | 121.2433 | 120.9824 | 121.6049 | 121.4584 | 122.8134 | -2.0874 | -123.1064
4156.9062 | 122.9004 | -121.1792 | 1.5518 | -0.0035098 | -0.003606 | -0.012781 | 0.018 | -0.008389 | -7.9062e-05 | 0.0098203 | -0.33417 | -0.1236 | -0.56763 | 1.3046 | 0.25635 | 0.41199 | 0.018311 | 0.28381 | 1.561 | -121.4584 | 120.6116 | -1.6754 | 120.845 | 122.4838 | -1.2955 | -0.27924 | 0.009155 | 0.23346 | 121.1975 | 121.463 | 121.4355 | 121.0556 | 120.845 | 122.7402 | 121.5912 | -0.27924 | 121.0556 | 120.845 | 121.5912 | 121.4355 | 122.7402 | -2.1194 | -123.0103
4157.9219 | 122.7951 | -121.2204 | 1.5518 | 0.0041197 | -0.00018804 | -0.010431 | 0.029322 | -0.0056118 | 0.00013454 | 0.0083249 | -0.28381 | -0.054932 | -0.57678 | 1.2177 | 0.16479 | 0.32501 | 0.10986 | 0.19226 | 1.593 | -121.5546 | 120.6436 | -1.6068 | 120.9366 | 122.438 | -1.387 | -0.33417 | 0.041199 | 0.29297 | 121.3303 | 121.4127 | 121.3852 | 121.1655 | 120.9366 | 122.8134 | 121.5454 | -0.33417 | 121.1655 | 120.9366 | 121.5454 | 121.3852 | 122.8134 | -2.1286 | -123.1064
4158.9062 | 122.9324 | -121.2112 | 1.4923 | -0.056915 | -0.0059558 | -0.0074404 | 0.019495 | -0.0060392 | -0.0026425 | 0.010034 | -0.30212 | -0.11444 | -0.56305 | 1.268 | 0.27466 | 0.43945 | 0.018311 | 0.34332 | 1.5289 | -121.5179 | 120.6482 | -1.6068 | 120.9091 | 122.4792 | -1.2177 | -0.3067 | 0.036621 | 0.26093 | 121.2296 | 121.5546 | 121.4859 | 121.0968 | 120.9091 | 122.7402 | 121.6507 | -0.3067 | 121.0968 | 120.9091 | 121.6507 | 121.4859 | 122.7402 | -2.0554 | -123.0103
4159.9062 | 122.9187 | -121.1517 | 1.561 | -0.064545 | -0.002965 | -0.0074404 | 0.019709 | -0.008389 | -0.0022153 | 0.0096067 | -0.29755 | -0.09613 | -0.55389 | 1.3229 | 0.3067 | 0.48065 | 0.018311 | 0.32959 | 1.5701 | -121.4493 | 120.5978 | -1.6571 | 120.8542 | 122.4747 | -1.2543 | -0.29755 | 0.009155 | 0.25635 | 121.17 | 121.4813 | 121.4584 | 121.0556 | 120.8542 | 122.7219 | 121.6324 | -0.29755 | 121.0556 | 120.8542 | 121.6324 | 121.4584 | 122.7219 | -2.1149 | -123.0103
4160.9219 | 122.8043 | -121.2296 | 1.5701 | -0.21713 | -0.0010424 | -0.0074404 | 0.026545 | -0.0071072 | -0.0011471 | 0.0078977 | -0.31128 | -0.036621 | -0.56305 | 1.2222 | 0.20599 | 0.36163 | 0.19226 | 0.22888 | 1.5701 | -121.55 | 120.6665 | -1.6068 | 120.9183 | 122.4518 | -1.3641 | -0.32044 | 0 | 0.25177 | 121.4218 | 121.4584 | 121.4355 | 121.1929 | 120.9183 | 122.7997 | 121.5912 | -0.32044 | 121.1929 | 120.9183 | 121.5912 | 121.4355 | 122.7997 | -2.1332 | -123.1201
4161.9062 | 122.8912 | -121.225 | 1.4923 | -0.041657 | -0.0038196 | -0.010858 | 0.019068 | -0.0071072 | 0.00013454 | 0.0096067 | -0.32959 | -0.09613 | -0.57678 | 1.2314 | 0.28381 | 0.4715 | 0.059509 | 0.31586 | 1.5106 | -121.4996 | 120.6482 | -1.5884 | 120.8954 | 122.4564 | -1.2085 | -0.27466 | 0.01831 | 0.24719 | 121.2845 | 121.5408 | 121.5088 | 121.1288 | 120.8954 | 122.7356 | 121.6965 | -0.27466 | 121.1288 | 120.8954 | 121.6965 | 121.5088 | 122.7356 | -2.0691 | -122.9919
4162.9219 | 122.8226 | -121.3074 | 1.474 | -0.19424 | -0.0010424 | -0.0087222 | 0.026972 | -0.003262 | -0.00093346 | 0.0076841 | -0.32044 | -0.054932 | -0.59052 | 1.1536 | 0.19684 | 0.35706 | 0.20142 | 0.24261 | 1.5015 | -121.5958 | 120.7169 | -1.5289 | 120.9869 | 122.4609 | -1.2772 | -0.28839 | 0.027466 | 0.27008 | 121.5088 | 121.55 | 121.5042 | 121.2524 | 120.9869 | 122.8088 | 121.6644 | -0.28839 | 121.2524 | 120.9869 | 121.6644 | 121.5042 | 122.8088 | -2.0645 | -123.0698
4163.9062 | 122.8592 | -121.2616 | 1.4511 | 0.072784 | -0.0061694 | -0.011286 | 0.018427 | -0.0062528 | -0.0034971 | 0.0098203 | -0.31128 | -0.09613 | -0.56305 | 1.1444 | 0.23804 | 0.41657 | 0.091553 | 0.28839 | 1.4603 | -121.5775 | 120.6985 | -1.5472 | 120.9503 | 122.406 | -1.2131 | -0.31586 | 0.009155 | 0.25177 | 121.3531 | 121.55 | 121.4996 | 121.1655 | 120.9503 | 122.7219 | 121.6782 | -0.31586 | 121.1655 | 120.9503 | 121.6782 | 121.4996 | 122.7219 | -2.0142 | -123.0286
4164.9062 | 122.8821 | -121.2616 | 1.4694 | -0.026398 | -0.004674 | -0.013422 | 0.019922 | -0.00668 | 0.00056194 | 0.0098203 | -0.33875 | -0.10529 | -0.5722 | 1.1765 | 0.25177 | 0.43945 | 0.054932 | 0.29297 | 1.4694 | -121.5958 | 120.6894 | -1.5747 | 120.9229 | 122.438 | -1.2177 | -0.33417 | 0 | 0.23346 | 121.3165 | 121.5546 | 121.5134 | 121.1563 | 120.9229 | 122.731 | 121.701 | -0.33417 | 121.1563 | 120.9229 | 121.701 | 121.5134 | 122.731 | -2.0416 | -123.0652
4165.9062 | 122.8683 | -121.2616 | 1.4465 | 0.042267 | -0.0044604 | -0.0087222 | 0.019709 | -0.0088162 | -0.0022153 | 0.0085385 | -0.32044 | -0.10529 | -0.56763 | 1.1719 | 0.24719 | 0.42572 | 0.068665 | 0.29755 | 1.4694 | -121.5637 | 120.694 | -1.5518 | 120.9412 | 122.4335 | -1.1993 | -0.30212 | 0.022888 | 0.24719 | 121.3303 | 121.5591 | 121.5088 | 121.1563 | 120.9412 | 122.731 | 121.6873 | -0.30212 | 121.1563 | 120.9412 | 121.6873 | 121.5088 | 122.731 | -2.0142 | -123.0103
4166.9062 | 122.8912 | -121.2662 | 1.4511 | 0.019379 | -0.0040332 | -0.011499 | 0.020563 | -0.0077482 | -0.0022153 | 0.0085385 | -0.30212 | -0.1236 | -0.56305 | 1.1993 | 0.2655 | 0.45319 | 0.050354 | 0.32501 | 1.4694 | -121.5775 | 120.7031 | -1.5747 | 120.9641 | 122.4655 | -1.1856 | -0.31128 | 0.01831 | 0.26093 | 121.3165 | 121.5912 | 121.5317 | 121.1426 | 120.9641 | 122.7356 | 121.7194 | -0.31128 | 121.1426 | 120.9641 | 121.7194 | 121.5317 | 122.7356 | -2.0142 | -123.0286
4167.9219 | 122.8455 | -121.2936 | 1.4923 | -0.11032 | -0.00082884 | -0.010645 | 0.029535 | -0.0058256 | -0.0026425 | 0.0076841 | -0.27008 | -0.064087 | -0.5722 | 1.1719 | 0.21057 | 0.37994 | 0.14648 | 0.26093 | 1.4786 | -121.6324 | 120.7214 | -1.5564 | 121.0236 | 122.4655 | -1.2817 | -0.33875 | -0.013733 | 0.30212 | 121.4401 | 121.5546 | 121.5042 | 121.2296 | 121.0236 | 122.7722 | 121.6736 | -0.33875 | 121.2296 | 121.0236 | 121.6736 | 121.5042 | 122.7722 | -2.0645 | -123.1247
4168.9062 | 122.8958 | -121.2616 | 1.4603 | -0.034027 | -0.0031786 | -0.01214 | 0.019068 | -0.0053982 | -0.0017881 | 0.0085385 | -0.31586 | -0.086975 | -0.56763 | 1.1719 | 0.26093 | 0.44403 | 0.07782 | 0.31128 | 1.474 | -121.5637 | 120.694 | -1.5472 | 120.9457 | 122.4335 | -1.1993 | -0.30212 | 0.013733 | 0.25177 | 121.3394 | 121.5729 | 121.5225 | 121.1746 | 120.9457 | 122.7356 | 121.7056 | -0.30212 | 121.1746 | 120.9457 | 121.7056 | 121.5225 | 122.7356 | -2.0279 | -123.024
4169.9062 | 122.8867 | -121.2799 | 1.4511 | -0.026398 | -0.0055286 | -0.0089358 | 0.021204 | -0.0079618 | -0.0034971 | 0.0083249 | -0.32044 | -0.086975 | -0.55847 | 1.1673 | 0.24719 | 0.43488 | 0.07782 | 0.30212 | 1.4832 | -121.5729 | 120.7214 | -1.5381 | 120.9595 | 122.4472 | -1.2039 | -0.29297 | 0.032043 | 0.23804 | 121.3577 | 121.582 | 121.5271 | 121.1929 | 120.9595 | 122.7631 | 121.7148 | -0.29297 | 121.1929 | 120.9595 | 121.7148 | 121.5271 | 122.7631 | -2.0096 | -123.024
4170.9062 | 122.8912 | -121.2799 | 1.4603 | -0.14847 | -0.0044604 | -0.010645 | 0.022059 | -0.0081754 | -0.00093346 | 0.0091795 | -0.25635 | -0.10529 | -0.54932 | 1.2314 | 0.27924 | 0.44861 | 0.082397 | 0.3479 | 1.4465 | -121.5591 | 120.7306 | -1.5656 | 121.0236 | 122.5113 | -1.181 | -0.27924 | -0.013733 | 0.29297 | 121.3623 | 121.6278 | 121.5591 | 121.1746 | 121.0236 | 122.7264 | 121.7285 | -0.27924 | 121.1746 | 121.0236 | 121.7285 | 121.5591 | 122.7264 | -2.0096 | -123.0194
4171.9062 | 122.8775 | -121.2158 | 1.474 | -0.034027 | -0.001897 | -0.014063 | 0.022272 | -0.0075344 | 0.00034814 | 0.010888 | -0.32959 | -0.09613 | -0.54474 | 1.1993 | 0.24261 | 0.41657 | 0.073242 | 0.28381 | 1.5106 | -121.5408 | 120.6711 | -1.5701 | 120.8862 | 122.4152 | -1.2314 | -0.32501 | 0.036621 | 0.21515 | 121.2891 | 121.4996 | 121.4584 | 121.1197 | 120.8862 | 122.7264 | 121.6324 | -0.32501 | 121.1197 | 120.8862 | 121.6324 | 121.4584 | 122.7264 | -2.0187 | -123.0148
4172.9062 | 122.9187 | -121.225 | 1.4603 | 0.019379 | -0.0027514 | -0.015558 | 0.019495 | -0.0081754 | -0.00071986 | 0.0087521 | -0.3067 | -0.07782 | -0.55389 | 1.2039 | 0.27466 | 0.43945 | 0.054932 | 0.32501 | 1.4648 | -121.5454 | 120.6711 | -1.5381 | 120.9183 | 122.4289 | -1.1856 | -0.32043 | 0.004578 | 0.24719 | 121.2799 | 121.55 | 121.4996 | 121.1472 | 120.9183 | 122.6898 | 121.6644 | -0.32043 | 121.1472 | 120.9183 | 121.6644 | 121.4996 | 122.6898 | -2.0142 | -123.0057
4173.9062 | 122.8958 | -121.2662 | 1.4694 | 0.057526 | -0.0055286 | -0.011286 | 0.019282 | -0.0088162 | -0.0013609 | 0.010675 | -0.33417 | -0.09613 | -0.5722 | 1.1993 | 0.2655 | 0.41657 | 0.068665 | 0.31586 | 1.4786 | -121.5637 | 120.694 | -1.5656 | 120.932 | 122.4655 | -1.2039 | -0.29755 | 0.009156 | 0.23804 | 121.3348 | 121.582 | 121.5317 | 121.17 | 120.932 | 122.7448 | 121.6827 | -0.29755 | 121.17 | 120.932 | 121.6827 | 121.5317 | 122.7448 | -2.0416 | -123.0331
4174.9062 | 0.20142 | -0.09613 | 0.16479 | 0.027008 | -0.0021106 | -0.009363 | 0.0079595 | -0.0079618 | -7.9062e-05 | 0.0083249 | -0.064087 | 0.13275 | -0.32501 | 0.068665 | 0.045776 | 0.064087 | -0.068665 | 0.24261 | 0.20599 | -0.4303 | -0.22888 | -0.032044 | 0.032043 | 0.16479 | -0.11902 | -0.33417 | 0.041199 | 0.26093 | 0.027465 | 0.33874 | 0.14191 | 0.22888 | 0.032043 | 0.30212 | 0.16022 | -0.33417 | 0.22888 | 0.032043 | 0.16022 | 0.14191 | 0.30212 | -0.48981 | -0.59509
4175.9062 | 0.10529 | -0.073242 | 0.16479 | -0.2095 | -0.0042468 | -0.012781 | 0.010523 | -0.0098844 | -0.00029266 | 0.0072569 | -0.027466 | 0.15106 | -0.31586 | 0.054932 | 0.032043 | 0.013733 | 0.032043 | 0.21973 | 0.20142 | -0.39368 | -0.24261 | -0.013733 | 0.045776 | 0.12817 | -0.13275 | -0.32044 | 0.036621 | 0.28839 | 0.10529 | 0.29297 | 0.10529 | 0.2243 | 0.045776 | 0.27466 | 0.086975 | -0.32044 | 0.2243 | 0.045776 | 0.086975 | 0.10529 | 0.27466 | -0.48065 | -0.55847
4176.9062 | 0.18768 | -0.086975 | 0.15564 | -0.079803 | -0.0044604 | -0.012354 | 0.0073187 | -0.00668 | -0.00071986 | 0.0070431 | -0.054932 | 0.15564 | -0.32501 | 0.059509 | 0.032043 | 0.036621 | -0.059509 | 0.23346 | 0.20599 | -0.3891 | -0.23804 | 0 | 0.032043 | 0.14648 | -0.1236 | -0.30212 | 0.050354 | 0.27008 | 0.027466 | 0.32043 | 0.11902 | 0.24261 | 0.032043 | 0.29297 | 0.1236 | -0.30212 | 0.24261 | 0.032043 | 0.1236 | 0.11902 | 0.29297 | -0.48065 | -0.54474
4177.9062 | 0.17853 | -0.082397 | 0.13275 | 0.072784 | -0.0044604 | -0.011713 | 0.0047553 | -0.0079618 | 0.00056194 | 0.0074705 | -0.082397 | 0.11902 | -0.32044 | 0.041199 | 0.045776 | 0.050354 | -0.064087 | 0.23346 | 0.21057 | -0.39825 | -0.23804 | -0.013732 | 0 | 0.1236 | -0.086975 | -0.31586 | 0.07782 | 0.23804 | 0.01831 | 0.31586 | 0.12817 | 0.20142 | 0 | 0.29297 | 0.13275 | -0.31586 | 0.20142 | 0 | 0.13275 | 0.12817 | 0.29297 | -0.45319 | -0.531
4178.9062 | 0.1831 | -0.091553 | 0.12817 | 0.049896 | -0.0042468 | -0.011927 | 0.0058233 | -0.0071072 | -0.00093346 | 0.0061887 | -0.045776 | 0.14191 | -0.33417 | 0.054932 | 0.050354 | 0.050354 | -0.07782 | 0.21973 | 0.19684 | -0.39825 | -0.24261 | 0.013733 | 0.045777 | 0.14649 | -0.07782 | -0.3067 | 0.068664 | 0.28839 | 0.013733 | 0.31128 | 0.14191 | 0.23346 | 0.045777 | 0.28839 | 0.14191 | -0.3067 | 0.23346 | 0.045777 | 0.14191 | 0.14191 | 0.28839 | -0.46234 | -0.52643
4179.9062 | 0.1831 | -0.086975 | 0.15106 | 0.0041197 | -0.0025378 | -0.0061588 | 0.0053961 | -0.0077482 | 0.00056194 | 0.0078977 | -0.064087 | 0.14648 | -0.31586 | 0.064087 | 0.059509 | 0.059509 | -0.086975 | 0.23346 | 0.19226 | -0.40283 | -0.22888 | -0.004578 | 0.022888 | 0.15106 | -0.091553 | -0.31586 | 0.041199 | 0.25177 | 0 | 0.32043 | 0.14648 | 0.23346 | 0.022888 | 0.27924 | 0.14648 | -0.31586 | 0.23346 | 0.022888 | 0.14648 | 0.14648 | 0.27924 | -0.46692 | -0.55389
4180.9062 | 0.082397 | -0.086975 | 0.16022 | -0.20187 | -0.0038196 | -0.010858 | 0.0094549 | -0.0079618 | -0.0017881 | 0.0066159 | -0.018311 | 0.15106 | -0.32044 | 0.059509 | 0.032043 | 0.036621 | 0.022888 | 0.2243 | 0.23346 | -0.39368 | -0.23346 | -0.009155 | 0.068664 | 0.14648 | -0.12817 | -0.3067 | 0.073242 | 0.30212 | 0.10986 | 0.31128 | 0.11902 | 0.23804 | 0.068664 | 0.32043 | 0.1236 | -0.3067 | 0.23804 | 0.068664 | 0.1236 | 0.11902 | 0.32043 | -0.48065 | -0.55389
4181.9062 | 0.16937 | -0.068665 | 0.15106 | 0.011749 | -0.0040332 | -0.008295 | 0.0060369 | -0.0073208 | 0.0012027 | 0.0096067 | -0.07782 | 0.13733 | -0.31586 | 0.050354 | 0.054932 | 0.059509 | -0.064087 | 0.2243 | 0.19226 | -0.38452 | -0.24719 | -0.013733 | -0.009155 | 0.11902 | -0.09613 | -0.31586 | 0.041199 | 0.23804 | 0.004578 | 0.29297 | 0.1236 | 0.20599 | -0.009155 | 0.26093 | 0.12817 | -0.31586 | 0.20599 | -0.009155 | 0.12817 | 0.1236 | 0.26093 | -0.46692 | -0.53558
4182.9062 | 0.16937 | -0.059509 | 0.15106 | 0.0041197 | -0.0040332 | -0.0074404 | 0.0071051 | -0.008389 | 0.00013454 | 0.0083249 | -0.07782 | 0.12817 | -0.32959 | 0.054932 | 0.045776 | 0.041199 | -0.054932 | 0.23346 | 0.21515 | -0.37994 | -0.27008 | -0.022888 | -0.018311 | 0.11444 | -0.10529 | -0.32044 | 0.064087 | 0.25177 | 0.004577 | 0.29297 | 0.10528 | 0.18768 | -0.018311 | 0.27466 | 0.10071 | -0.32044 | 0.18768 | -0.018311 | 0.10071 | 0.10528 | 0.27466 | -0.48065 | -0.53101
4183.9062 | 0.17853 | -0.068665 | 0.13733 | 0.080414 | -0.0042468 | -0.013636 | 0.0060369 | -0.0062528 | -0.00029266 | 0.0074705 | -0.041199 | 0.12817 | -0.31128 | 0.050354 | 0.054932 | 0.050354 | -0.064087 | 0.23346 | 0.19226 | -0.36621 | -0.24261 | -0.009155 | 0.027466 | 0.11902 | -0.082397 | -0.29755 | 0.054932 | 0.27008 | 0.004578 | 0.30212 | 0.1236 | 0.19684 | 0.027466 | 0.26093 | 0.11902 | -0.29755 | 0.19684 | 0.027466 | 0.11902 | 0.1236 | 0.26093 | -0.44861 | -0.50354
4184.9062 | 0.16479 | -0.082397 | 0.14191 | 0.027008 | -0.0033922 | -0.007654 | 0.0066779 | -0.0071072 | 0.0014163 | 0.0083249 | -0.064087 | 0.12817 | -0.31128 | 0.059509 | 0.045776 | 0.059509 | -0.07782 | 0.21973 | 0.18768 | -0.39368 | -0.22888 | -0.013733 | 0.01831 | 0.14191 | -0.096131 | -0.31128 | 0.045776 | 0.24719 | 0.004577 | 0.30212 | 0.12817 | 0.21057 | 0.01831 | 0.27008 | 0.14191 | -0.31128 | 0.21057 | 0.01831 | 0.14191 | 0.12817 | 0.27008 | -0.45319 | -0.53558
4185.9062 | 0.17395 | -0.068665 | 0.16022 | 0.14145 | -0.0048876 | -0.006586 | 0.0053961 | -0.00668 | -0.0015745 | 0.0087521 | -0.054932 | 0.13275 | -0.31128 | 0.068665 | 0.050354 | 0.050354 | -0.082397 | 0.21057 | 0.20142 | -0.40741 | -0.24261 | -0.027466 | 0.013733 | 0.13733 | -0.10986 | -0.33874 | 0.041199 | 0.25635 | -0.013732 | 0.27924 | 0.11902 | 0.20142 | 0.013733 | 0.27008 | 0.11902 | -0.33874 | 0.20142 | 0.013733 | 0.11902 | 0.11902 | 0.27008 | -0.4715 | -0.56763
4186.9062 | 0.17395 | -0.064087 | 0.13733 | 0.13382 | -0.0016834 | -0.015345 | 0.0094549 | -0.0073208 | -0.0041379 | 0.0076841 | -0.068665 | 0.15564 | -0.31586 | 0.068665 | 0.054932 | 0.032043 | -0.054932 | 0.22888 | 0.20599 | -0.37537 | -0.25177 | 0.018311 | -0.004578 | 0.13275 | -0.082397 | -0.31128 | 0.068665 | 0.24719 | 0.009155 | 0.29297 | 0.11902 | 0.21973 | -0.004578 | 0.27008 | 0.09613 | -0.31128 | 0.21973 | -0.004578 | 0.09613 | 0.11902 | 0.27008 | -0.45319 | -0.5127
4187.9062 | 0.16937 | -0.068665 | 0.13733 | 0.1033 | -0.0051012 | -0.0097904 | 0.0068915 | -0.0071072 | 0.00056194 | 0.0085385 | -0.068665 | 0.14648 | -0.30212 | 0.054932 | 0.036621 | 0.032043 | -0.07782 | 0.21973 | 0.19684 | -0.37079 | -0.23346 | 0.009155 | 0 | 0.1236 | -0.10071 | -0.30212 | 0.059509 | 0.23346 | -0.009155 | 0.28839 | 0.10529 | 0.21515 | 0 | 0.2655 | 0.10071 | -0.30212 | 0.21515 | 0 | 0.10071 | 0.10529 | 0.2655 | -0.43945 | -0.50812
4188.9062 | 0.15106 | -0.07782 | 0.14191 | 0.14145 | -0.0031786 | -0.0080814 | 0.0094549 | -0.0064664 | -0.00029266 | 0.0083249 | -0.068665 | 0.12817 | -0.32501 | 0.050354 | 0.050354 | 0.050354 | -0.068665 | 0.22888 | 0.19226 | -0.39368 | -0.24719 | -0.013733 | 0.009155 | 0.12817 | -0.091553 | -0.31586 | 0.050354 | 0.25635 | 0.009155 | 0.3067 | 0.12817 | 0.20599 | 0.009155 | 0.27008 | 0.12817 | -0.31586 | 0.20599 | 0.009155 | 0.12817 | 0.12817 | 0.27008 | -0.46692 | -0.53558
4189.9062 | 0.1831 | -0.064087 | 0.13733 | 0.16434 | -0.0033922 | -0.008295 | 0.0060369 | -0.0088162 | -0.0017881 | 0.0061887 | -0.059509 | 0.13733 | -0.30212 | 0.041199 | 0.054932 | 0.059509 | -0.086975 | 0.21057 | 0.20599 | -0.40283 | -0.23804 | 0 | 0.004578 | 0.10529 | -0.082397 | -0.33875 | 0.068665 | 0.24261 | -0.022888 | 0.27466 | 0.11902 | 0.20142 | 0.004578 | 0.27008 | 0.1236 | -0.33875 | 0.20142 | 0.004578 | 0.1236 | 0.11902 | 0.27008 | -0.43945 | -0.54016
4190.9219 | 0.068665 | -0.07782 | 0.16479 | -0.17136 | -0.0025378 | -0.008295 | 0.010309 | -0.0088162 | 0.00098914 | 0.0078977 | -0.086975 | 0.1831 | -0.32044 | 0.018311 | -0.009155 | -0.022888 | 0.07782 | 0.16937 | 0.23346 | -0.37079 | -0.24262 | 0.01831 | -0.009155 | 0.096131 | -0.17395 | -0.29297 | 0.068664 | 0.23346 | 0.15564 | 0.24719 | 0.068665 | 0.26092 | -0.009155 | 0.31128 | 0.054932 | -0.29297 | 0.26092 | -0.009155 | 0.054932 | 0.068665 | 0.31128 | -0.48523 | -0.53558
4191.9062 | 0.16937 | -0.07782 | 0.13733 | 0.088043 | -0.0016834 | -0.010858 | 0.0068915 | -0.00668 | -0.0011471 | 0.0085385 | -0.059509 | 0.16022 | -0.31128 | 0.045776 | 0.041199 | 0.064087 | -0.086975 | 0.2243 | 0.21057 | -0.36621 | -0.23346 | 0.022888 | 0.018311 | 0.1236 | -0.09613 | -0.28839 | 0.073242 | 0.25177 | -0.009155 | 0.30212 | 0.11902 | 0.23804 | 0.018311 | 0.28839 | 0.14191 | -0.28839 | 0.23804 | 0.018311 | 0.14191 | 0.11902 | 0.28839 | -0.44861 | -0.50354
4192.9062 | 0.17395 | -0.073242 | 0.14191 | 0.1796 | -0.0031786 | -0.011072 | 0.0068915 | -0.0086026 | -0.00029266 | 0.0085385 | -0.054932 | 0.11444 | -0.3479 | 0.050354 | 0.041199 | 0.059509 | -0.073242 | 0.21973 | 0.19684 | -0.37537 | -0.27466 | -0.027466 | 0.01831 | 0.1236 | -0.10071 | -0.30212 | 0.054931 | 0.29297 | 0 | 0.29297 | 0.11444 | 0.18768 | 0.01831 | 0.27008 | 0.13275 | -0.30212 | 0.18768 | 0.01831 | 0.13275 | 0.11444 | 0.27008 | -0.48981 | -0.51727
4193.9062 | 0.17395 | -0.07782 | 0.15564 | 0.034637 | -0.0016834 | -0.013422 | 0.0079595 | -0.0064664 | -0.00071986 | 0.0081113 | -0.073242 | 0.14191 | -0.32501 | 0.041199 | 0.045776 | 0.045776 | -0.064087 | 0.23346 | 0.19684 | -0.37994 | -0.24719 | -0.013733 | 0.004578 | 0.11902 | -0.10986 | -0.30212 | 0.041198 | 0.25177 | 0.013733 | 0.31128 | 0.1236 | 0.21973 | 0.004578 | 0.27466 | 0.1236 | -0.30212 | 0.21973 | 0.004578 | 0.1236 | 0.1236 | 0.27466 | -0.48065 | -0.53558
4194.9062 | 0.17395 | -0.064087 | 0.13275 | 0.095673 | -0.0055286 | -0.011927 | 0.0068915 | -0.0064664 | -0.0015745 | 0.0074705 | -0.082397 | 0.16479 | -0.31128 | 0.054932 | 0.050354 | 0.050354 | -0.073242 | 0.23804 | 0.19684 | -0.37079 | -0.24719 | 0.032044 | -0.01831 | 0.11902 | -0.082397 | -0.3067 | 0.064087 | 0.22888 | -0.009155 | 0.30212 | 0.11444 | 0.22888 | -0.01831 | 0.26093 | 0.11444 | -0.3067 | 0.22888 | -0.01831 | 0.11444 | 0.11444 | 0.26093 | -0.44403 | -0.50354
4195.9062 | 0.16479 | -0.091553 | 0.14191 | 0.072784 | -0.0048876 | -0.0078678 | 0.0083869 | -0.008389 | -0.00029266 | 0.0068295 | -0.082397 | 0.13733 | -0.31586 | 0.059509 | 0.045776 | 0.059509 | -0.073242 | 0.21973 | 0.18768 | -0.37994 | -0.2243 | -0.004578 | 0.009156 | 0.15106 | -0.096131 | -0.28839 | 0.045776 | 0.23346 | 0.018311 | 0.31128 | 0.13733 | 0.22888 | 0.009156 | 0.27924 | 0.15106 | -0.28839 | 0.22888 | 0.009156 | 0.15106 | 0.13733 | 0.27924 | -0.45776 | -0.52185
4196.9062 | 0.17395 | -0.068665 | 0.15106 | 0.065155 | -0.0016834 | -0.013422 | 0.0068915 | -0.0081754 | 0.00077554 | 0.0076841 | -0.082397 | 0.1236 | -0.31128 | 0.059509 | 0.045776 | 0.064087 | -0.068665 | 0.2243 | 0.20599 | -0.37994 | -0.24261 | -0.027466 | -0.013732 | 0.12817 | -0.10529 | -0.31128 | 0.054932 | 0.22888 | 0 | 0.29297 | 0.11444 | 0.19226 | -0.013732 | 0.27466 | 0.13275 | -0.31128 | 0.19226 | -0.013732 | 0.13275 | 0.11444 | 0.27466 | -0.46234 | -0.53101
4197.9062 | 0.15106 | -0.07782 | 0.14191 | 0.049896 | -0.0031786 | -0.0074404 | 0.0058233 | -0.0073208 | -0.00071986 | 0.0072569 | -0.07782 | 0.13275 | -0.31586 | 0.059509 | 0.054932 | 0.064087 | -0.064087 | 0.23346 | 0.20599 | -0.36621 | -0.23804 | -0.009156 | 0 | 0.13733 | -0.086975 | -0.28839 | 0.064087 | 0.23804 | 0.013733 | 0.31128 | 0.13275 | 0.21057 | 0 | 0.28381 | 0.14191 | -0.28839 | 0.21057 | 0 | 0.14191 | 0.13275 | 0.28381 | -0.45776 | -0.50812
4198.9062 | 0.16022 | -0.073242 | 0.13275 | 0.095673 | -0.001897 | -0.013422 | 0.0071051 | -0.0073208 | -0.0015745 | 0.0059751 | -0.07782 | 0.14191 | -0.31586 | 0.068665 | 0.054932 | 0.050354 | -0.073242 | 0.23346 | 0.18768 | -0.35706 | -0.24261 | 0.009156 | -0.004578 | 0.14191 | -0.077819 | -0.28381 | 0.054932 | 0.23804 | 0 | 0.3067 | 0.12817 | 0.21515 | -0.004578 | 0.26092 | 0.1236 | -0.28381 | 0.21515 | -0.004578 | 0.1236 | 0.12817 | 0.26092 | -0.44861 | -0.48981
4199.9062 | 0.17395 | -0.07782 | 0.14648 | 0.088043 | -0.005315 | -0.011713 | 0.0066779 | -0.0068936 | -0.0017881 | 0.0072569 | -0.091553 | 0.1236 | -0.3067 | 0.054932 | 0.041199 | 0.054932 | -0.068665 | 0.22888 | 0.19226 | -0.37537 | -0.22888 | -0.022888 | -0.013733 | 0.13275 | -0.10529 | -0.29755 | 0.045777 | 0.21515 | 0.009155 | 0.3067 | 0.11902 | 0.20142 | -0.013733 | 0.27008 | 0.13275 | -0.29755 | 0.20142 | -0.013733 | 0.13275 | 0.11902 | 0.27008 | -0.45319 | -0.52185
4200.9062 | 0.21515 | -0.036621 | 0.14648 | -0.1561 | -0.003606 | -0.010218 | 0.0053961 | -0.0077482 | 0.00034814 | 0.0083249 | -0.004578 | 0.13733 | -0.30212 | 0.12817 | 0.09613 | 0.091553 | -0.10529 | 0.3067 | 0.20142 | -0.33875 | -0.2655 | -0.009155 | 0.032043 | 0.1648 | -0.050354 | -0.30212 | 0.054932 | 0.29755 | -0.068665 | 0.34332 | 0.13275 | 0.17395 | 0.032043 | 0.23804 | 0.12817 | -0.30212 | 0.17395 | 0.032043 | 0.12817 | 0.13275 | 0.23804 | -0.44861 | -0.48523
4201.9062 | 0.18768 | -0.064087 | 0.14648 | -0.018768 | -0.003606 | -0.015985 | 0.0064643 | -0.0053982 | -0.0041379 | 0.0081113 | -0.073242 | 0.14191 | -0.32044 | 0.050354 | 0.050354 | 0.059509 | -0.068665 | 0.23804 | 0.19226 | -0.35248 | -0.25635 | -0.004577 | -0.009155 | 0.11444 | -0.09613 | -0.28839 | 0.045777 | 0.24719 | -0.004578 | 0.30212 | 0.11444 | 0.20599 | -0.009155 | 0.25635 | 0.1236 | -0.28839 | 0.20599 | -0.009155 | 0.1236 | 0.11444 | 0.25635 | -0.46692 | -0.49896
4202.9062 | 0.19226 | -0.086975 | 0.14648 | -0.011139 | -0.0055286 | -0.010218 | 0.0060369 | -0.010739 | -0.00029266 | 0.0068295 | -0.073242 | 0.13733 | -0.31586 | 0.082397 | 0.045776 | 0.054932 | -0.07782 | 0.22888 | 0.21515 | -0.35706 | -0.22888 | -0.009155 | 0.013733 | 0.16937 | -0.10071 | -0.27008 | 0.068665 | 0.24261 | 0.009155 | 0.31586 | 0.13275 | 0.2243 | 0.013733 | 0.30212 | 0.14191 | -0.27008 | 0.2243 | 0.013733 | 0.14191 | 0.13275 | 0.30212 | -0.46234 | -0.50354
4203.9062 | 0.16022 | -0.064087 | 0.14191 | 0.019379 | -0.0033922 | -0.0087222 | 0.0045417 | -0.0060392 | -0.00050626 | 0.0068295 | -0.073242 | 0.13733 | -0.31128 | 0.064087 | 0.054932 | 0.054932 | -0.064087 | 0.2243 | 0.21515 | -0.36163 | -0.24719 | -0.004578 | -0.009155 | 0.12817 | -0.086975 | -0.29755 | 0.073242 | 0.23804 | 0 | 0.28839 | 0.11902 | 0.20142 | -0.009155 | 0.27924 | 0.11902 | -0.29755 | 0.20142 | -0.009155 | 0.11902 | 0.11902 | 0.27924 | -0.45319 | -0.50354
4204.9062 | 0.1831 | -0.059509 | 0.13275 | 0.049896 | -0.0033922 | -0.015131 | 0.0058233 | -0.0051846 | -0.0015745 | 0.0064023 | -0.064087 | 0.14191 | -0.31128 | 0.073242 | 0.054932 | 0.064087 | -0.064087 | 0.22888 | 0.19226 | -0.36621 | -0.25177 | 0.009156 | -0.004578 | 0.13275 | -0.077819 | -0.3067 | 0.05951 | 0.24719 | -0.004578 | 0.28839 | 0.11444 | 0.20142 | -0.004578 | 0.25177 | 0.1236 | -0.3067 | 0.20142 | -0.004578 | 0.1236 | 0.11444 | 0.25177 | -0.44403 | -0.49896
4205.9062 | 0.07782 | -0.086975 | 0.16937 | -0.17136 | -0.001897 | -0.010858 | 0.012446 | -0.0071072 | 0.00056194 | 0.0074705 | -0.050354 | 0.17853 | -0.32501 | 0.013733 | -0.004578 | -0.018311 | 0.086975 | 0.18768 | 0.2243 | -0.37537 | -0.23804 | 0.009155 | 0.036621 | 0.10071 | -0.17395 | -0.28839 | 0.054931 | 0.27466 | 0.17395 | 0.27466 | 0.082397 | 0.2655 | 0.036621 | 0.31128 | 0.068664 | -0.28839 | 0.2655 | 0.036621 | 0.068664 | 0.082397 | 0.31128 | -0.49439 | -0.54474
4206.9062 | 0.18768 | -0.07782 | 0.14648 | 0.080414 | -0.0038196 | -0.0095766 | 0.0079595 | -0.004971 | -0.0020017 | 0.0074705 | -0.082397 | 0.14191 | -0.34332 | 0.054932 | 0.045776 | 0.064087 | -0.064087 | 0.22888 | 0.20142 | -0.34332 | -0.2655 | -0.004577 | -0.004577 | 0.13275 | -0.10071 | -0.2655 | 0.054932 | 0.26093 | 0.013733 | 0.3067 | 0.1236 | 0.21973 | -0.004577 | 0.27924 | 0.14191 | -0.2655 | 0.21973 | -0.004577 | 0.14191 | 0.1236 | 0.27924 | -0.48981 | -0.48981
4207.9062 | 0.18768 | -0.064087 | 0.13733 | -0.018768 | -0.0025378 | -0.013208 | 0.0051825 | -0.0064664 | 0.0016299 | 0.0081113 | -0.064087 | 0.14191 | -0.33417 | 0.068665 | 0.064087 | 0.07782 | -0.091553 | 0.2655 | 0.20599 | -0.35706 | -0.27008 | 0.004578 | 0 | 0.13275 | -0.073242 | -0.29297 | 0.068665 | 0.27008 | -0.027466 | 0.32959 | 0.12817 | 0.20599 | 0 | 0.27008 | 0.14191 | -0.29297 | 0.20599 | 0 | 0.14191 | 0.12817 | 0.27008 | -0.4715 | -0.49438
4208.9062 | 0.16937 | -0.054932 | 0.14191 | -0.011139 | -0.0051012 | -0.013636 | 0.0083869 | -0.010312 | -0.00029266 | 0.0070431 | -0.07782 | 0.15106 | -0.29755 | 0.054932 | 0.068665 | 0.07782 | -0.045776 | 0.27008 | 0.20142 | -0.35706 | -0.24261 | 0.009155 | -0.022888 | 0.10986 | -0.073242 | -0.30212 | 0.059509 | 0.21973 | 0.009156 | 0.32501 | 0.1236 | 0.20599 | -0.022888 | 0.25635 | 0.13275 | -0.30212 | 0.20599 | -0.022888 | 0.13275 | 0.1236 | 0.25635 | -0.43945 | -0.49896
4209.9062 | 0.17395 | -0.050354 | 0.12817 | -0.011139 | -0.0038196 | -0.013208 | 0.0066779 | -0.0081754 | 0.00077554 | 0.0083249 | -0.07782 | 0.13275 | -0.32044 | 0.07782 | 0.068665 | 0.073242 | -0.07782 | 0.25177 | 0.20599 | -0.3479 | -0.27008 | 0.004577 | -0.027466 | 0.12817 | -0.059509 | -0.29755 | 0.07782 | 0.24262 | -0.027466 | 0.30212 | 0.11902 | 0.18311 | -0.027466 | 0.25635 | 0.1236 | -0.29755 | 0.18311 | -0.027466 | 0.1236 | 0.11902 | 0.25635 | -0.44861 | -0.47607
4210.9062 | 0.19226 | -0.054932 | 0.16479 | 0.065155 | -0.0040332 | -0.0091494 | 0.0077459 | -0.0081754 | -7.9062e-05 | 0.0087521 | -0.054932 | 0.13275 | -0.32044 | 0.07782 | 0.059509 | 0.068665 | -0.086975 | 0.24719 | 0.20599 | -0.35248 | -0.2655 | -0.032044 | 0 | 0.13275 | -0.10529 | -0.29755 | 0.041199 | 0.2655 | -0.032043 | 0.30212 | 0.11444 | 0.18768 | 0 | 0.26093 | 0.1236 | -0.29755 | 0.18768 | 0 | 0.1236 | 0.11444 | 0.26093 | -0.48523 | -0.51727
4211.9062 | 0.16479 | -0.059509 | 0.14191 | 0.019379 | -0.003606 | -0.011286 | 0.0062507 | -0.0081754 | -0.00029266 | 0.0087521 | -0.068665 | 0.14648 | -0.32044 | 0.068665 | 0.064087 | 0.059509 | -0.082397 | 0.24261 | 0.20142 | -0.35248 | -0.26093 | 0.004577 | -0.009156 | 0.12817 | -0.07782 | -0.29297 | 0.059509 | 0.25177 | -0.022888 | 0.30212 | 0.1236 | 0.20599 | -0.009156 | 0.26093 | 0.11902 | -0.29297 | 0.20599 | -0.009156 | 0.11902 | 0.1236 | 0.26093 | -0.46234 | -0.49439
4212.9062 | 0.17395 | -0.068665 | 0.15106 | 0.049896 | -0.0051012 | -0.013422 | 0.0043281 | -0.0058256 | -0.0011471 | 0.0066159 | -0.082397 | 0.12817 | -0.31586 | 0.045776 | 0.054932 | 0.050354 | -0.073242 | 0.22888 | 0.20599 | -0.35248 | -0.24719 | -0.022888 | -0.013732 | 0.11444 | -0.09613 | -0.28381 | 0.054932 | 0.23346 | -0.004577 | 0.29755 | 0.1236 | 0.19684 | -0.013732 | 0.27466 | 0.11902 | -0.28381 | 0.19684 | -0.013732 | 0.11902 | 0.1236 | 0.27466 | -0.46692 | -0.50354
4213.9062 | 0.16479 | -0.054932 | 0.16479 | 0.0041197 | -0.0051012 | -0.013636 | 0.0079595 | -0.0098844 | -0.0017881 | 0.0083249 | -0.068665 | 0.13733 | -0.33417 | 0.064087 | 0.050354 | 0.064087 | -0.068665 | 0.24261 | 0.19684 | -0.3479 | -0.27924 | -0.027466 | -0.013733 | 0.11902 | -0.11444 | -0.29297 | 0.032043 | 0.2655 | -0.013733 | 0.29755 | 0.10529 | 0.19226 | -0.013733 | 0.25177 | 0.11902 | -0.29297 | 0.19226 | -0.013733 | 0.11902 | 0.10529 | 0.25177 | -0.49896 | -0.5127
4214.9062 | 0.19226 | -0.059509 | 0.14648 | -0.018768 | -0.0044604 | -0.010431 | 0.0049689 | -0.008389 | -0.0020017 | 0.0066159 | -0.054932 | 0.14648 | -0.3067 | 0.10071 | 0.07782 | 0.073242 | -0.07782 | 0.27466 | 0.19226 | -0.33417 | -0.24719 | 0 | 0.004577 | 0.16022 | -0.068664 | -0.27466 | 0.045777 | 0.25177 | -0.018311 | 0.33417 | 0.13733 | 0.20599 | 0.004577 | 0.25177 | 0.13275 | -0.27466 | 0.20599 | 0.004577 | 0.13275 | 0.13733 | 0.25177 | -0.45319 | -0.48065
4215.9062 | 0.059509 | -0.064087 | 0.19226 | -0.31631 | -0.0021106 | -0.0087222 | 0.0094549 | -0.0096708 | -0.0013609 | 0.0064023 | -0.073242 | 0.17853 | -0.32501 | 0.013733 | -0.009155 | -0.036621 | 0.068665 | 0.1831 | 0.22888 | -0.37079 | -0.26093 | -0.013733 | -0.009155 | 0.07782 | -0.20142 | -0.3067 | 0.036621 | 0.25177 | 0.13275 | 0.24719 | 0.054932 | 0.24261 | -0.009155 | 0.29297 | 0.027466 | -0.3067 | 0.24261 | -0.009155 | 0.027466 | 0.054932 | 0.29297 | -0.51727 | -0.56305
4216.9062 | 0.17395 | -0.059509 | 0.14648 | -0.018768 | -0.0044604 | -0.014276 | 0.0051825 | -0.0077482 | -0.0032835 | 0.0093931 | -0.059509 | 0.15106 | -0.31128 | 0.086975 | 0.07782 | 0.086975 | -0.07782 | 0.27466 | 0.17853 | -0.33875 | -0.25177 | 0.004578 | 0 | 0.14648 | -0.068664 | -0.27924 | 0.032044 | 0.25177 | -0.018311 | 0.33417 | 0.13733 | 0.21057 | 0 | 0.23804 | 0.14648 | -0.27924 | 0.21057 | 0 | 0.14648 | 0.13733 | 0.23804 | -0.45776 | -0.48523
4217.9062 | 0.19684 | -0.059509 | 0.16022 | 0.019379 | -0.0040332 | -0.011072 | 0.0058233 | -0.0094572 | -0.00071986 | 0.0091795 | -0.064087 | 0.13275 | -0.3067 | 0.082397 | 0.086975 | 0.086975 | -0.07782 | 0.2655 | 0.19684 | -0.35248 | -0.24719 | -0.027466 | -0.004578 | 0.14191 | -0.073242 | -0.29297 | 0.036621 | 0.24261 | -0.018311 | 0.32501 | 0.14648 | 0.19226 | -0.004578 | 0.25635 | 0.14648 | -0.29297 | 0.19226 | -0.004578 | 0.14648 | 0.14648 | 0.25635 | -0.46692 | -0.5127
4218.9062 | 0.17853 | -0.064087 | 0.16479 | 0.0041197 | -0.003606 | -0.0070132 | 0.0071051 | -0.00668 | -0.0015745 | 0.0061887 | -0.068665 | 0.15106 | -0.32044 | 0.07782 | 0.07782 | 0.064087 | -0.07782 | 0.26093 | 0.20142 | -0.33417 | -0.25635 | -0.013733 | -0.004578 | 0.14191 | -0.086975 | -0.27008 | 0.036621 | 0.25177 | -0.013733 | 0.32501 | 0.14191 | 0.21515 | -0.004578 | 0.2655 | 0.12817 | -0.27008 | 0.21515 | -0.004578 | 0.12817 | 0.14191 | 0.2655 | -0.48523 | -0.49896
4219.9062 | 0.17853 | -0.064087 | 0.14191 | -0.0035098 | -0.0031786 | -0.011072 | 0.0058233 | -0.0088162 | -0.00029266 | 0.0093931 | -0.064087 | 0.15564 | -0.3067 | 0.086975 | 0.073242 | 0.086975 | -0.073242 | 0.27008 | 0.19226 | -0.33417 | -0.24261 | 0.013733 | 0 | 0.15106 | -0.068665 | -0.27008 | 0.050354 | 0.24261 | -0.009155 | 0.33417 | 0.13733 | 0.21973 | 0 | 0.25635 | 0.15106 | -0.27008 | 0.21973 | 0 | 0.15106 | 0.13733 | 0.25635 | -0.44861 | -0.47607
4220.9219 | 0.059509 | -0.07782 | 0.16479 | -0.19424 | -0.0025378 | -0.011499 | 0.013086 | -0.0047574 | -0.0022153 | 0.0068295 | -0.073242 | 0.19226 | -0.32501 | 0.032043 | -0.004578 | -0.032043 | 0.082397 | 0.16937 | 0.23346 | -0.35706 | -0.24719 | 0.027466 | 0.004578 | 0.10986 | -0.16937 | -0.27924 | 0.068664 | 0.25177 | 0.16022 | 0.24719 | 0.073242 | 0.27008 | 0.004578 | 0.31128 | 0.045777 | -0.27924 | 0.27008 | 0.004578 | 0.045777 | 0.073242 | 0.31128 | -0.48981 | -0.52185
4221.9062 | 0.19226 | -0.022888 | 0.14648 | -0.1561 | -0.0040332 | -0.0087222 | 0.0071051 | -0.0094572 | 0.00077554 | 0.0055479 | -0.027466 | 0.15106 | -0.30212 | 0.11902 | 0.10986 | 0.11902 | -0.11444 | 0.31586 | 0.1831 | -0.35248 | -0.27924 | 0.004578 | -0.004578 | 0.14191 | -0.036621 | -0.32959 | 0.036621 | 0.27466 | -0.091553 | 0.33875 | 0.13275 | 0.17395 | -0.004578 | 0.20599 | 0.14191 | -0.32959 | 0.17395 | -0.004578 | 0.14191 | 0.13275 | 0.20599 | -0.44861 | -0.49896
4222.9062 | 0.20142 | -0.036621 | 0.13733 | -0.072174 | -0.0044604 | -0.011499 | 0.0062507 | -0.008389 | -0.0015745 | 0.0066159 | -0.027466 | 0.13275 | -0.31586 | 0.11444 | 0.10529 | 0.10986 | -0.10986 | 0.30212 | 0.20142 | -0.37537 | -0.27924 | -0.004578 | 0.009155 | 0.15106 | -0.032043 | -0.33874 | 0.064087 | 0.28839 | -0.073242 | 0.33875 | 0.14191 | 0.16937 | 0.009155 | 0.23804 | 0.14648 | -0.33874 | 0.16937 | 0.009155 | 0.14648 | 0.14191 | 0.23804 | -0.45319 | -0.5127
4223.9062 | 0.19226 | -0.022888 | 0.15564 | -0.079803 | -0.0051012 | -0.013422 | 0.0075323 | -0.0075344 | -0.0013609 | 0.0091795 | -0.013733 | 0.15564 | -0.31586 | 0.11902 | 0.10071 | 0.10529 | -0.10529 | 0.3067 | 0.18768 | -0.37079 | -0.29297 | 0 | 0.009155 | 0.14191 | -0.054932 | -0.3479 | 0.032043 | 0.30212 | -0.082398 | 0.32959 | 0.1236 | 0.17853 | 0.009155 | 0.21057 | 0.12817 | -0.3479 | 0.17853 | 0.009155 | 0.12817 | 0.1236 | 0.21057 | -0.4715 | -0.52643
4224.9062 | 0.20599 | -0.036621 | 0.14191 | -0.12558 | -0.0068102 | -0.0085086 | 0.0071051 | -0.0077482 | -0.0015745 | 0.0057615 | -0.036621 | 0.13275 | -0.30212 | 0.10986 | 0.10529 | 0.11444 | -0.11444 | 0.30212 | 0.19684 | -0.37079 | -0.2655 | -0.009156 | 0 | 0.14648 | -0.036621 | -0.33417 | 0.054931 | 0.2655 | -0.07782 | 0.33875 | 0.14191 | 0.16937 | 0 | 0.23346 | 0.15106 | -0.33417 | 0.16937 | 0 | 0.15106 | 0.14191 | 0.23346 | -0.44403 | -0.5127
4225.9062 | 0.20142 | -0.032043 | 0.1236 | -0.041657 | -0.0021106 | -0.010645 | 0.0049689 | -0.0081754 | -0.0022153 | 0.0070431 | -0.032043 | 0.13733 | -0.3067 | 0.10529 | 0.09613 | 0.11444 | -0.10529 | 0.29755 | 0.18768 | -0.35706 | -0.27466 | 0.013733 | 0 | 0.13733 | -0.027466 | -0.32501 | 0.064087 | 0.27466 | -0.073243 | 0.32959 | 0.12817 | 0.16937 | 0 | 0.21973 | 0.14648 | -0.32501 | 0.16937 | 0 | 0.14648 | 0.12817 | 0.21973 | -0.4303 | -0.48065
4226.9062 | 0.20599 | -0.041199 | 0.11902 | -0.10269 | -0.0042468 | -0.012567 | 0.0073187 | -0.0079618 | -0.00071986 | 0.0055479 | -0.022888 | 0.12817 | -0.32044 | 0.1236 | 0.09613 | 0.10986 | -0.10529 | 0.29297 | 0.19684 | -0.36163 | -0.27924 | 0.009155 | 0.018311 | 0.16479 | -0.022889 | -0.32043 | 0.077819 | 0.29755 | -0.064087 | 0.33417 | 0.13733 | 0.16937 | 0.018311 | 0.23804 | 0.15106 | -0.32043 | 0.16937 | 0.018311 | 0.15106 | 0.13733 | 0.23804 | -0.43945 | -0.48065
4227.9062 | 0.19684 | -0.050354 | 0.11444 | -0.072174 | -0.0048876 | -0.0095766 | 0.0060369 | -0.0086026 | -0.00029266 | 0.0064023 | -0.027466 | 0.13275 | -0.32044 | 0.09613 | 0.10529 | 0.10071 | -0.10529 | 0.30212 | 0.20599 | -0.35706 | -0.27008 | 0.01831 | 0.022888 | 0.14648 | -0.009155 | -0.3067 | 0.091553 | 0.29297 | -0.054932 | 0.35248 | 0.15564 | 0.18311 | 0.022888 | 0.25635 | 0.15106 | -0.3067 | 0.18311 | 0.022888 | 0.15106 | 0.15564 | 0.25635 | -0.43488 | -0.4715
4228.9062 | 0.18768 | -0.027466 | 0.15106 | -0.16373 | -0.002965 | -0.011499 | 0.0081733 | -0.00668 | -0.0024289 | 0.0059751 | -0.004578 | 0.13275 | -0.29297 | 0.11902 | 0.10071 | 0.11444 | -0.086975 | 0.32501 | 0.17853 | -0.33417 | -0.2655 | -0.018311 | 0.022888 | 0.14649 | -0.050354 | -0.3067 | 0.027466 | 0.28839 | -0.059509 | 0.35248 | 0.12817 | 0.16022 | 0.022888 | 0.20599 | 0.14191 | -0.3067 | 0.16022 | 0.022888 | 0.14191 | 0.12817 | 0.20599 | -0.44403 | -0.48523
4229.9062 | 0.19684 | -0.022888 | 0.13733 | -0.11032 | -0.0033922 | -0.011072 | 0.0041143 | -0.0079618 | -7.9062e-05 | 0.0070431 | 0.018311 | 0.14191 | -0.30212 | 0.1236 | 0.086975 | 0.10529 | -0.086975 | 0.31586 | 0.19226 | -0.32959 | -0.27924 | 0.004578 | 0.041199 | 0.14648 | -0.050354 | -0.3067 | 0.054932 | 0.32044 | -0.064087 | 0.33875 | 0.10986 | 0.16479 | 0.041199 | 0.21515 | 0.12817 | -0.3067 | 0.16479 | 0.041199 | 0.12817 | 0.10986 | 0.21515 | -0.43945 | -0.46692
4230.9062 | 0.050354 | -0.064087 | 0.18768 | -0.25528 | -0.0023242 | -0.0089358 | 0.010523 | -0.0075344 | -0.0011471 | 0.0059751 | -0.059509 | 0.19684 | -0.33417 | 0.013733 | -0.013733 | -0.036621 | 0.086975 | 0.16022 | 0.2243 | -0.32959 | -0.27008 | 0.009155 | 0.004578 | 0.07782 | -0.20142 | -0.2655 | 0.036621 | 0.27466 | 0.15106 | 0.2243 | 0.050354 | 0.26093 | 0.004578 | 0.28839 | 0.027466 | -0.2655 | 0.26093 | 0.004578 | 0.027466 | 0.050354 | 0.28839 | -0.52185 | -0.51727
4231.9062 | 0.17395 | -0.027466 | 0.13733 | -0.11032 | -0.0048876 | -0.01214 | 0.0083869 | -0.008389 | -0.0030697 | 0.0055479 | 0 | 0.14191 | -0.3067 | 0.10071 | 0.10071 | 0.10986 | -0.10071 | 0.3067 | 0.19226 | -0.34332 | -0.27924 | 0.004578 | 0.027466 | 0.12817 | -0.036621 | -0.31586 | 0.054932 | 0.3067 | -0.073242 | 0.33417 | 0.12817 | 0.16937 | 0.027466 | 0.21973 | 0.13733 | -0.31586 | 0.16937 | 0.027466 | 0.13733 | 0.12817 | 0.21973 | -0.44403 | -0.48065
4232.9062 | 0.20142 | -0.050354 | 0.15106 | -0.12558 | -0.0048876 | -0.012781 | 0.0077459 | -0.0090298 | -0.0013609 | 0.0055479 | 0.013733 | 0.11902 | -0.32044 | 0.13733 | 0.12817 | 0.12817 | -0.086975 | 0.32044 | 0.17853 | -0.35248 | -0.27008 | -0.032043 | 0.064087 | 0.18768 | -0.022888 | -0.30212 | 0.027466 | 0.33417 | -0.036621 | 0.37079 | 0.17853 | 0.16937 | 0.064087 | 0.22888 | 0.17853 | -0.30212 | 0.16937 | 0.064087 | 0.17853 | 0.17853 | 0.22888 | -0.4715 | -0.50354
4233.9219 | 0.082397 | -0.10529 | 0.16022 | 0.19485 | 0.00023916 | -0.0097904 | 0.015436 | -0.0060392 | -0.0013609 | 0.0081113 | -0.064087 | 0.17853 | -0.3479 | 0.004578 | -0.032043 | -0.027466 | 0.022888 | 0.11444 | 0.23346 | -0.45776 | -0.24261 | 0.018311 | 0.041199 | 0.10986 | -0.19226 | -0.35248 | 0.073242 | 0.28381 | 0.12817 | 0.21973 | 0.073243 | 0.28381 | 0.041199 | 0.33875 | 0.07782 | -0.35248 | 0.28381 | 0.041199 | 0.07782 | 0.073243 | 0.33875 | -0.50812 | -0.61798
4234.9062 | 0.20142 | -0.027466 | 0.13275 | -0.056915 | -0.0057422 | -0.010004 | 0.0051825 | -0.0064664 | -0.00029266 | 0.0083249 | -0.004578 | 0.13733 | -0.29755 | 0.11444 | 0.13275 | 0.11902 | -0.10071 | 0.3067 | 0.20142 | -0.33875 | -0.27008 | 0.004578 | 0.022888 | 0.14191 | 0 | -0.31128 | 0.068665 | 0.29297 | -0.073242 | 0.33417 | 0.16022 | 0.16479 | 0.022888 | 0.22888 | 0.14649 | -0.31128 | 0.16479 | 0.022888 | 0.14649 | 0.16022 | 0.22888 | -0.4303 | -0.4715
4235.9219 | 0.10071 | -0.059509 | 0.17395 | -0.11032 | 0.0010938 | -0.010645 | 0.018 | -0.004971 | -0.0011471 | 0.0031979 | -0.022888 | 0.1831 | -0.32044 | 0.045776 | 0.041199 | 0.018311 | -0.009155 | 0.19684 | 0.23346 | -0.37079 | -0.26093 | 0.009155 | 0.036621 | 0.10528 | -0.13275 | -0.31128 | 0.059509 | 0.29755 | 0.050354 | 0.25635 | 0.10071 | 0.24261 | 0.036621 | 0.29297 | 0.07782 | -0.31128 | 0.24261 | 0.036621 | 0.07782 | 0.10071 | 0.29297 | -0.49439 | -0.54474
4236.9062 | 0.17395 | -0.022888 | 0.15106 | -0.2095 | -0.0048876 | -0.014063 | 0.0068915 | -0.0068936 | -0.0022153 | 0.0091795 | -0.018311 | 0.13733 | -0.3067 | 0.10529 | 0.10986 | 0.1236 | -0.07782 | 0.32044 | 0.19684 | -0.31128 | -0.28381 | -0.013733 | 0.004577 | 0.12817 | -0.041199 | -0.28839 | 0.045776 | 0.28839 | -0.054932 | 0.34332 | 0.13275 | 0.16022 | 0.004577 | 0.21973 | 0.14648 | -0.28839 | 0.16022 | 0.004577 | 0.14648 | 0.13275 | 0.21973 | -0.45776 | -0.46234
4237.9062 | 0.20142 | -0.027466 | 0.13733 | -0.17899 | -0.0048876 | -0.014917 | 0.0062507 | -0.0058256 | -0.0030697 | 0.0068295 | -0.004578 | 0.1236 | -0.30212 | 0.10986 | 0.10986 | 0.10529 | -0.09613 | 0.29297 | 0.19684 | -0.32044 | -0.27466 | -0.013733 | 0.022888 | 0.13733 | -0.027466 | -0.29297 | 0.059509 | 0.29755 | -0.068664 | 0.32043 | 0.13733 | 0.15106 | 0.022888 | 0.2243 | 0.13275 | -0.29297 | 0.15106 | 0.022888 | 0.13275 | 0.13733 | 0.2243 | -0.43945 | -0.45776
4238.9062 | 0.07782 | -0.054932 | 0.16479 | -0.18662 | -0.00040164 | -0.010858 | 0.016077 | -0.0041166 | -0.0032835 | 0.0085385 | -0.059509 | 0.19684 | -0.3479 | 0.022888 | 0 | -0.018311 | 0.068665 | 0.17395 | 0.24261 | -0.33875 | -0.29297 | 0.032043 | -0.004577 | 0.07782 | -0.16479 | -0.28381 | 0.07782 | 0.28839 | 0.1236 | 0.22888 | 0.054932 | 0.25177 | -0.004577 | 0.29755 | 0.036621 | -0.28381 | 0.25177 | -0.004577 | 0.036621 | 0.054932 | 0.29755 | -0.5127 | -0.50354
4239.9062 | 0.19226 | -0.041199 | 0.13733 | -0.14084 | -0.004674 | -0.0070132 | 0.0060369 | -0.0051846 | -0.0020017 | 0.0089657 | -0.004578 | 0.14648 | -0.30212 | 0.10986 | 0.10986 | 0.13275 | -0.082397 | 0.29755 | 0.19684 | -0.32501 | -0.26093 | 0.009155 | 0.036621 | 0.15106 | -0.027466 | -0.28381 | 0.059509 | 0.29755 | -0.041198 | 0.33874 | 0.15106 | 0.18768 | 0.036621 | 0.23804 | 0.17395 | -0.28381 | 0.18768 | 0.036621 | 0.17395 | 0.15106 | 0.23804 | -0.43945 | -0.46234
4240.9062 | 0.07782 | -0.064087 | 0.17395 | -0.18662 | -0.0014696 | -0.010645 | 0.012659 | -0.0086026 | -0.0011471 | 0.0072569 | -0.068665 | 0.20142 | -0.33875 | -0.004578 | 0.004578 | -0.018311 | 0.07782 | 0.17395 | 0.22888 | -0.32501 | -0.27466 | 0.027466 | -0.004578 | 0.059509 | -0.16937 | -0.26093 | 0.054932 | 0.27008 | 0.14191 | 0.23804 | 0.068665 | 0.2655 | -0.004578 | 0.29297 | 0.045776 | -0.26093 | 0.2655 | -0.004578 | 0.045776 | 0.068665 | 0.29297 | -0.5127 | -0.49896
4241.9062 | 0.16479 | -0.032043 | 0.14648 | -0.21713 | -0.0078784 | -0.016626 | 0.0077459 | -0.0071072 | -0.0017881 | 0.0081113 | 0 | 0.13275 | -0.29755 | 0.10071 | 0.11902 | 0.10529 | -0.07782 | 0.29755 | 0.19684 | -0.33417 | -0.2655 | -0.013733 | 0.032043 | 0.13275 | -0.027465 | -0.30212 | 0.050354 | 0.29755 | -0.045777 | 0.32959 | 0.15106 | 0.16479 | 0.032043 | 0.22888 | 0.13733 | -0.30212 | 0.16479 | 0.032043 | 0.13733 | 0.15106 | 0.22888 | -0.44403 | -0.48065
4242.9062 | 0.17853 | -0.032043 | 0.12817 | -0.2095 | -0.002965 | -0.010218 | 0.0073187 | -0.0068936 | -0.0047787 | 0.0072569 | -0.013733 | 0.13275 | -0.30212 | 0.10986 | 0.10529 | 0.10986 | -0.07782 | 0.31128 | 0.18768 | -0.34332 | -0.27008 | 0.004577 | 0.01831 | 0.14191 | -0.022888 | -0.31128 | 0.059509 | 0.28839 | -0.045777 | 0.34332 | 0.13733 | 0.16479 | 0.01831 | 0.21973 | 0.14191 | -0.31128 | 0.16479 | 0.01831 | 0.14191 | 0.13733 | 0.21973 | -0.4303 | -0.4715
4243.9219 | 0.086975 | -0.07782 | 0.16479 | 0.072784 | -0.00040164 | -0.0080814 | 0.017573 | -0.0053982 | -0.0028561 | 0.0070431 | -0.041199 | 0.1831 | -0.32959 | 0 | -0.027466 | -0.018311 | 0.032043 | 0.15106 | 0.24261 | -0.39368 | -0.25177 | 0.01831 | 0.036621 | 0.07782 | -0.19226 | -0.31586 | 0.07782 | 0.28839 | 0.10986 | 0.22888 | 0.050354 | 0.26092 | 0.036621 | 0.32044 | 0.059509 | -0.31586 | 0.26092 | 0.036621 | 0.059509 | 0.050354 | 0.32044 | -0.49438 | -0.55847
4244.9062 | 0.18768 | -0.036621 | 0.14648 | -0.10269 | -0.0027514 | -0.011713 | 0.0051825 | -0.004971 | -0.0054197 | 0.0078977 | -0.009155 | 0.12817 | -0.3067 | 0.10529 | 0.11902 | 0.10529 | -0.10529 | 0.3067 | 0.19684 | -0.33875 | -0.27008 | -0.01831 | 0.027466 | 0.14191 | -0.027465 | -0.30212 | 0.050354 | 0.29755 | -0.068665 | 0.34332 | 0.15564 | 0.1648 | 0.027466 | 0.23346 | 0.14191 | -0.30212 | 0.1648 | 0.027466 | 0.14191 | 0.15564 | 0.23346 | -0.45319 | -0.48523
4245.9062 | 0.068665 | -0.064087 | 0.1831 | -0.23239 | -0.00061524 | -0.0087222 | 0.011591 | -0.0062528 | -0.0028561 | 0.0081113 | -0.073242 | 0.20142 | -0.32959 | 0.004578 | -0.013733 | -0.022888 | 0.073242 | 0.17853 | 0.23346 | -0.33417 | -0.2655 | 0.018311 | -0.009155 | 0.068665 | -0.19684 | -0.27008 | 0.050354 | 0.25635 | 0.13733 | 0.24261 | 0.050354 | 0.2655 | -0.009155 | 0.29755 | 0.041199 | -0.27008 | 0.2655 | -0.009155 | 0.041199 | 0.050354 | 0.29755 | -0.5127 | -0.51727
4246.9062 | 0.17395 | -0.013733 | 0.13275 | -0.2095 | -0.0044604 | -0.01449 | 0.0083869 | -0.0060392 | -0.0013609 | 0.0081113 | -0.004578 | 0.13275 | -0.27924 | 0.09613 | 0.09613 | 0.11902 | -0.059509 | 0.31128 | 0.19226 | -0.3067 | -0.2655 | 0 | 0.009155 | 0.10986 | -0.036621 | -0.29297 | 0.05951 | 0.27466 | -0.045776 | 0.32501 | 0.10986 | 0.14648 | 0.009155 | 0.20599 | 0.13275 | -0.29297 | 0.14648 | 0.009155 | 0.13275 | 0.10986 | 0.20599 | -0.41199 | -0.43945
4247.9062 | 0.20142 | -0.050354 | 0.14648 | -0.041657 | -0.0044604 | -0.011499 | 0.0058233 | -0.00668 | -0.0013609 | 0.0091795 | -0.032043 | 0.14648 | -0.32044 | 0.07782 | 0.09613 | 0.10071 | -0.10071 | 0.28381 | 0.19684 | -0.34332 | -0.27008 | 0 | 0.018311 | 0.12817 | -0.050354 | -0.29297 | 0.050354 | 0.28839 | -0.050354 | 0.33417 | 0.14648 | 0.19684 | 0.018311 | 0.24719 | 0.15106 | -0.29297 | 0.19684 | 0.018311 | 0.15106 | 0.14648 | 0.24719 | -0.46692 | -0.48981
4248.9062 | 0.041199 | -0.086975 | 0.16479 | -0.18662 | -0.0040332 | -0.0097904 | 0.011805 | -0.0081754 | -0.00050626 | 0.0085385 | -0.086975 | 0.1831 | -0.34332 | 0 | -0.013733 | -0.036621 | 0.073242 | 0.18768 | 0.23804 | -0.32959 | -0.25635 | 0.01831 | 0 | 0.086975 | -0.17853 | -0.24261 | 0.073242 | 0.25635 | 0.16022 | 0.27466 | 0.073242 | 0.27008 | 0 | 0.32501 | 0.050354 | -0.24261 | 0.27008 | 0 | 0.050354 | 0.073242 | 0.32501 | -0.50812 | -0.49438
4249.9062 | 0.21057 | -0.045776 | 0.13275 | -0.087433 | -0.0051012 | -0.012567 | 0.0066779 | -0.0058256 | -0.0026425 | 0.010675 | -0.032043 | 0.12817 | -0.32959 | 0.086975 | 0.09613 | 0.11902 | -0.10986 | 0.32044 | 0.19226 | -0.32044 | -0.28381 | -0.004577 | 0.013733 | 0.13275 | -0.036621 | -0.27466 | 0.05951 | 0.29755 | -0.064087 | 0.36621 | 0.14191 | 0.17395 | 0.013733 | 0.23804 | 0.16479 | -0.27466 | 0.17395 | 0.013733 | 0.16479 | 0.14191 | 0.23804 | -0.46234 | -0.45319
4250.9062 | 0.19684 | -0.027466 | 0.15106 | -0.14084 | -0.0048876 | -0.013422 | 0.0058233 | -0.0068936 | -0.0028561 | 0.0076841 | 0.004578 | 0.14191 | -0.3067 | 0.10986 | 0.10071 | 0.10529 | -0.091553 | 0.31586 | 0.18768 | -0.31586 | -0.27924 | -0.009155 | 0.032044 | 0.13733 | -0.050354 | -0.28839 | 0.036621 | 0.31128 | -0.064087 | 0.34332 | 0.12817 | 0.16937 | 0.032044 | 0.21515 | 0.13275 | -0.28839 | 0.16937 | 0.032044 | 0.13275 | 0.12817 | 0.21515 | -0.45776 | -0.46692
4251.9062 | 0.17395 | -0.059509 | 0.13733 | -0.034027 | -0.005315 | -0.011499 | 0.0060369 | -0.0075344 | 0.0012027 | 0.0051205 | -0.036621 | 0.12817 | -0.31128 | 0.082397 | 0.073242 | 0.09613 | -0.07782 | 0.27466 | 0.21515 | -0.33417 | -0.25177 | -0.009155 | 0.022888 | 0.14191 | -0.064087 | -0.27466 | 0.07782 | 0.27466 | -0.018311 | 0.33417 | 0.13275 | 0.18768 | 0.022888 | 0.27466 | 0.15564 | -0.27466 | 0.18768 | 0.022888 | 0.15564 | 0.13275 | 0.27466 | -0.44861 | -0.4715
4252.9062 | 0.17395 | -0.054932 | 0.15106 | 0.034637 | -0.003606 | -0.008295 | 0.0064643 | -0.0090298 | -0.00029266 | 0.0087521 | -0.073242 | 0.11902 | -0.3067 | 0.068665 | 0.054932 | 0.07782 | -0.082397 | 0.28381 | 0.20142 | -0.37994 | -0.25177 | -0.032043 | -0.01831 | 0.1236 | -0.09613 | -0.32501 | 0.050354 | 0.23346 | -0.027465 | 0.33874 | 0.10986 | 0.17395 | -0.01831 | 0.25635 | 0.13275 | -0.32501 | 0.17395 | -0.01831 | 0.13275 | 0.10986 | 0.25635 | -0.45776 | -0.53101
4253.9062 | 0.20599 | -0.050354 | 0.14648 | -0.064545 | -0.0048876 | -0.012781 | 0.0060369 | -0.0075344 | -0.0020017 | 0.0070431 | -0.018311 | 0.14191 | -0.30212 | 0.086975 | 0.09613 | 0.10529 | -0.09613 | 0.29755 | 0.21057 | -0.3479 | -0.25177 | -0.004577 | 0.032043 | 0.13733 | -0.050354 | -0.29755 | 0.064087 | 0.28381 | -0.045776 | 0.3479 | 0.14648 | 0.19226 | 0.032043 | 0.26093 | 0.15564 | -0.29755 | 0.19226 | 0.032043 | 0.15564 | 0.14648 | 0.26093 | -0.44861 | -0.49438
4254.9062 | 0.17395 | -0.068665 | 0.15106 | 0.019379 | -0.004674 | -0.007654 | 0.0041143 | -0.0047574 | -0.00050626 | 0.0059751 | -0.054932 | 0.13275 | -0.31128 | 0.054932 | 0.054932 | 0.059509 | -0.07782 | 0.24719 | 0.21973 | -0.37994 | -0.24261 | -0.018311 | 0.013733 | 0.1236 | -0.09613 | -0.31128 | 0.068665 | 0.25635 | -0.009155 | 0.31586 | 0.1236 | 0.20142 | 0.013733 | 0.28839 | 0.12817 | -0.31128 | 0.20142 | 0.013733 | 0.12817 | 0.1236 | 0.28839 | -0.46234 | -0.53101
4255.9219 | 0.050354 | -0.059509 | 0.18768 | -0.2095 | -0.0025378 | -0.0080814 | 0.012232 | -0.0075344 | -0.00093346 | 0.0074705 | -0.059509 | 0.18768 | -0.3479 | 0 | -0.022888 | -0.027466 | 0.07782 | 0.17853 | 0.24719 | -0.33875 | -0.28839 | 0 | 0 | 0.059509 | -0.21057 | -0.27924 | 0.059509 | 0.28839 | 0.13733 | 0.23804 | 0.036621 | 0.24719 | 0 | 0.3067 | 0.032043 | -0.27924 | 0.24719 | 0 | 0.032043 | 0.036621 | 0.3067 | -0.53558 | -0.52643
4256.9062 | 0.17395 | -0.045776 | 0.15106 | 0.0041197 | -0.0033922 | -0.0074404 | 0.0081733 | -0.0073208 | -0.00093346 | 0.0076841 | -0.059509 | 0.14191 | -0.32044 | 0.054932 | 0.068665 | 0.059509 | -0.073242 | 0.25177 | 0.19684 | -0.37994 | -0.27466 | -0.009155 | -0.013733 | 0.10071 | -0.082397 | -0.33417 | 0.045776 | 0.26093 | -0.027466 | 0.29755 | 0.11444 | 0.18768 | -0.013733 | 0.24261 | 0.10528 | -0.33417 | 0.18768 | -0.013733 | 0.10528 | 0.11444 | 0.24261 | -0.4715 | -0.53101
4257.9062 | 0.17395 | -0.068665 | 0.13275 | -0.026398 | -0.002965 | -0.014917 | 0.0062507 | -0.0071072 | -0.0013609 | 0.010888 | -0.068665 | 0.12817 | -0.31128 | 0.050354 | 0.054932 | 0.054932 | -0.073242 | 0.24261 | 0.1831 | -0.36621 | -0.24261 | -0.004577 | 0 | 0.11902 | -0.077819 | -0.29755 | 0.050354 | 0.24261 | -0.004577 | 0.31128 | 0.1236 | 0.19684 | 0 | 0.25177 | 0.1236 | -0.29755 | 0.19684 | 0 | 0.1236 | 0.1236 | 0.25177 | -0.44403 | -0.49896
4258.9062 | 0.16022 | -0.059509 | 0.13733 | -0.041657 | -0.0040332 | -0.015131 | 0.0064643 | -0.0090298 | 0.00013454 | 0.0059751 | -0.073242 | 0.13275 | -0.3067 | 0.064087 | 0.050354 | 0.045776 | -0.073242 | 0.23804 | 0.20142 | -0.37994 | -0.24719 | -0.004578 | -0.013733 | 0.1236 | -0.086975 | -0.32044 | 0.064087 | 0.23346 | -0.013733 | 0.29755 | 0.10986 | 0.19226 | -0.013733 | 0.26093 | 0.10528 | -0.32044 | 0.19226 | -0.013733 | 0.10528 | 0.10986 | 0.26093 | -0.44403 | -0.51727
4259.9062 | 0.15564 | -0.054932 | 0.14191 | 0.057526 | -0.0031786 | -0.0089358 | 0.0066779 | -0.0053982 | -0.0022153 | 0.0078977 | -0.059509 | 0.14191 | -0.32501 | 0.050354 | 0.059509 | 0.064087 | -0.073242 | 0.23804 | 0.21515 | -0.38452 | -0.27008 | 0 | -0.004577 | 0.10529 | -0.082398 | -0.32959 | 0.073242 | 0.2655 | -0.01831 | 0.29297 | 0.11444 | 0.19684 | -0.004577 | 0.27008 | 0.11902 | -0.32959 | 0.19684 | -0.004577 | 0.11902 | 0.11444 | 0.27008 | -0.46692 | -0.52643
4260.9062 | 0.10529 | -0.054932 | 0.16022 | -0.23239 | -0.0025378 | -0.012567 | 0.0092413 | -0.0068936 | -0.00093346 | 0.0068295 | -0.032043 | 0.15106 | -0.32044 | 0.054932 | 0.045776 | 0.041199 | 0.009155 | 0.25177 | 0.21515 | -0.31128 | -0.2655 | -0.009155 | 0.022889 | 0.10986 | -0.11444 | -0.25635 | 0.054932 | 0.28839 | 0.064087 | 0.3067 | 0.10071 | 0.20599 | 0.022889 | 0.27008 | 0.096131 | -0.25635 | 0.20599 | 0.022889 | 0.096131 | 0.10071 | 0.27008 | -0.48065 | -0.4715
4261.9062 | 0.15106 | -0.050354 | 0.14191 | 0.065155 | -0.0051012 | -0.010645 | 0.0075323 | -0.0094572 | -0.00093346 | 0.0085385 | -0.073242 | 0.13275 | -0.3067 | 0.050354 | 0.064087 | 0.050354 | -0.059509 | 0.22888 | 0.19684 | -0.37994 | -0.25635 | -0.009156 | -0.022888 | 0.10071 | -0.07782 | -0.32959 | 0.054931 | 0.23346 | -0.009155 | 0.27924 | 0.11444 | 0.18311 | -0.022888 | 0.24719 | 0.10071 | -0.32959 | 0.18311 | -0.022888 | 0.10071 | 0.11444 | 0.24719 | -0.44861 | -0.52185
4262.9062 | 0.16937 | -0.059509 | 0.13733 | 0.011749 | -0.0021106 | -0.012354 | 0.0062507 | -0.0088162 | -0.00029266 | 0.0083249 | -0.073242 | 0.14648 | -0.3067 | 0.068665 | 0.073242 | 0.073242 | -0.073242 | 0.27466 | 0.20142 | -0.36621 | -0.24719 | 0.009155 | -0.013733 | 0.12817 | -0.064087 | -0.3067 | 0.064087 | 0.23346 | -0.013733 | 0.33417 | 0.13275 | 0.20599 | -0.013733 | 0.26093 | 0.13275 | -0.3067 | 0.20599 | -0.013733 | 0.13275 | 0.13275 | 0.26093 | -0.44403 | -0.50354
4263.9062 | 0.16937 | -0.059509 | 0.13275 | 0.027008 | -0.0042468 | -0.009363 | 0.0056097 | -0.0086026 | -0.00029266 | 0.0089657 | -0.059509 | 0.14191 | -0.32959 | 0.073242 | 0.050354 | 0.064087 | -0.073242 | 0.2655 | 0.20599 | -0.35248 | -0.27008 | 0.009156 | 0 | 0.13275 | -0.082397 | -0.29297 | 0.073243 | 0.27008 | -0.013733 | 0.32501 | 0.10986 | 0.20142 | 0 | 0.2655 | 0.1236 | -0.29297 | 0.20142 | 0 | 0.1236 | 0.10986 | 0.2655 | -0.46234 | -0.48523
4264.9062 | 0.17853 | -0.068665 | 0.15106 | 0.0041197 | -0.0042468 | -0.0095766 | 0.0064643 | -0.004971 | -7.9062e-05 | 0.0091795 | -0.036621 | 0.15106 | -0.31586 | 0.068665 | 0.045776 | 0.059509 | -0.082397 | 0.24719 | 0.21057 | -0.35706 | -0.24719 | 0 | 0.032044 | 0.13733 | -0.10529 | -0.28839 | 0.059509 | 0.27924 | -0.013732 | 0.31586 | 0.11444 | 0.21973 | 0.032044 | 0.27924 | 0.12817 | -0.28839 | 0.21973 | 0.032044 | 0.12817 | 0.11444 | 0.27924 | -0.46692 | -0.50812
4265.9062 | 0.10986 | -0.073242 | 0.15564 | -0.12558 | -0.0021106 | -0.010645 | 0.013727 | -0.0053982 | -0.0037107 | 0.0076841 | -0.027466 | 0.16937 | -0.32959 | 0.068665 | 0.041199 | 0.013733 | 0.009155 | 0.20599 | 0.22888 | -0.32044 | -0.25635 | 0.013733 | 0.045776 | 0.14191 | -0.11444 | -0.24719 | 0.073242 | 0.30212 | 0.082397 | 0.27924 | 0.11444 | 0.24261 | 0.045776 | 0.30212 | 0.086975 | -0.24719 | 0.24261 | 0.045776 | 0.086975 | 0.11444 | 0.30212 | -0.48523 | -0.47608
4266.9062 | 0.16022 | -0.07782 | 0.1236 | -0.011139 | -0.0038196 | -0.011499 | 0.0071051 | -0.0056118 | -0.0022153 | 0.010034 | -0.073242 | 0.14648 | -0.32959 | 0.059509 | 0.07782 | 0.059509 | -0.073242 | 0.22888 | 0.20142 | -0.37079 | -0.25177 | 0.022888 | 0.004578 | 0.13733 | -0.045776 | -0.29297 | 0.07782 | 0.25635 | 0.004578 | 0.3067 | 0.15564 | 0.2243 | 0.004578 | 0.27924 | 0.13733 | -0.29297 | 0.2243 | 0.004578 | 0.13733 | 0.15564 | 0.27924 | -0.45319 | -0.49438
4267.9062 | 0.17853 | -0.054932 | 0.15106 | 0.019379 | -0.004674 | -0.011286 | 0.0051825 | -0.0086026 | 0.00034814 | 0.0081113 | -0.07782 | 0.14191 | -0.31128 | 0.059509 | 0.054932 | 0.064087 | -0.064087 | 0.24719 | 0.1831 | -0.37537 | -0.25635 | -0.009155 | -0.022888 | 0.11444 | -0.09613 | -0.32043 | 0.032043 | 0.23346 | -0.009155 | 0.30212 | 0.10986 | 0.19684 | -0.022888 | 0.23804 | 0.11902 | -0.32043 | 0.19684 | -0.022888 | 0.11902 | 0.10986 | 0.23804 | -0.46234 | -0.52643
4268.9062 | 0.16937 | -0.041199 | 0.15564 | -0.0035098 | -0.001256 | -0.011286 | 0.0073187 | -0.0073208 | -0.0024289 | 0.0076841 | -0.07782 | 0.13275 | -0.32959 | 0.064087 | 0.054932 | 0.059509 | -0.086975 | 0.23804 | 0.1831 | -0.38452 | -0.28839 | -0.022889 | -0.036621 | 0.10529 | -0.10071 | -0.34332 | 0.027465 | 0.25177 | -0.045776 | 0.27924 | 0.096131 | 0.17395 | -0.036621 | 0.2243 | 0.10071 | -0.34332 | 0.17395 | -0.036621 | 0.10071 | 0.096131 | 0.2243 | -0.48523 | -0.54016
4269.9062 | 0.19226 | -0.032043 | 0.13275 | -0.064545 | -0.004674 | -0.01684 | 0.0049689 | -0.0077482 | -0.0024289 | 0.0091795 | -0.036621 | 0.13733 | -0.29755 | 0.09613 | 0.082397 | 0.11444 | -0.10071 | 0.28381 | 0.18768 | -0.33875 | -0.2655 | 0.004578 | -0.004578 | 0.12817 | -0.050354 | -0.3067 | 0.054932 | 0.26092 | -0.068665 | 0.31586 | 0.11444 | 0.16937 | -0.004578 | 0.21973 | 0.14648 | -0.3067 | 0.16937 | -0.004578 | 0.14648 | 0.11444 | 0.21973 | -0.4303 | -0.4715
4270.9219 | 0.086975 | -0.068665 | 0.17395 | -0.1561 | 0.0017346 | -0.011286 | 0.011805 | -0.008389 | 0.00034814 | 0.0081113 | -0.045776 | 0.17395 | -0.3479 | 0.022888 | 0.004578 | 0 | 0.07782 | 0.1831 | 0.2243 | -0.31128 | -0.27924 | 0 | 0.022889 | 0.091553 | -0.16937 | -0.24261 | 0.050354 | 0.30212 | 0.14649 | 0.25177 | 0.073243 | 0.24261 | 0.022889 | 0.29297 | 0.068665 | -0.24261 | 0.24261 | 0.022889 | 0.068665 | 0.073243 | 0.29297 | -0.52185 | -0.48523
4271.9062 | 0.19226 | -0.045776 | 0.14191 | -0.064545 | -0.005315 | -0.011927 | 0.0041143 | -0.0064664 | -0.00071986 | 0.0083249 | -0.045776 | 0.13275 | -0.31128 | 0.082397 | 0.10071 | 0.10529 | -0.10071 | 0.27466 | 0.21057 | -0.33417 | -0.2655 | -0.009156 | 0 | 0.12817 | -0.041199 | -0.28839 | 0.068664 | 0.2655 | -0.054932 | 0.32043 | 0.14648 | 0.17853 | 0 | 0.25635 | 0.15106 | -0.28839 | 0.17853 | 0 | 0.15106 | 0.14648 | 0.25635 | -0.45319 | -0.47607
4272.9062 | 0.1831 | -0.054932 | 0.14648 | -0.056915 | -0.0048876 | -0.0097904 | 0.0062507 | -0.0088162 | -0.0013609 | 0.0068295 | -0.041199 | 0.13733 | -0.30212 | 0.07782 | 0.082397 | 0.09613 | -0.09613 | 0.28839 | 0.19684 | -0.34332 | -0.24719 | -0.009155 | 0.013733 | 0.13275 | -0.064087 | -0.28839 | 0.050354 | 0.26093 | -0.041198 | 0.34332 | 0.13733 | 0.19226 | 0.013733 | 0.25177 | 0.15106 | -0.28839 | 0.19226 | 0.013733 | 0.15106 | 0.13733 | 0.25177 | -0.44861 | -0.48981
4273.9062 | 0.18768 | -0.059509 | 0.15106 | -0.064545 | -0.0065966 | -0.0085086 | 0.0043281 | -0.0073208 | -0.00050626 | 0.0078977 | -0.041199 | 0.14191 | -0.31128 | 0.07782 | 0.086975 | 0.10071 | -0.07782 | 0.27924 | 0.19684 | -0.33875 | -0.25177 | -0.009155 | 0.01831 | 0.13733 | -0.064087 | -0.27924 | 0.045776 | 0.27008 | -0.018311 | 0.33874 | 0.14648 | 0.20142 | 0.01831 | 0.25635 | 0.16022 | -0.27924 | 0.20142 | 0.01831 | 0.16022 | 0.14648 | 0.25635 | -0.46234 | -0.48981
4274.9062 | 0.1831 | -0.045776 | 0.13275 | -0.034027 | -0.004674 | -0.011713 | 0.0051825 | -0.0068936 | -0.0015745 | 0.0066159 | -0.050354 | 0.13275 | -0.33417 | 0.086975 | 0.082397 | 0.086975 | -0.091553 | 0.2655 | 0.20142 | -0.36163 | -0.28839 | 0 | -0.004578 | 0.13275 | -0.050354 | -0.31586 | 0.068665 | 0.28381 | -0.045777 | 0.31128 | 0.12817 | 0.17853 | -0.004578 | 0.24719 | 0.13275 | -0.31586 | 0.17853 | -0.004578 | 0.13275 | 0.12817 | 0.24719 | -0.46692 | -0.49438
4275.9062 | 0.045776 | -0.073242 | 0.1831 | -0.24002 | -0.0023242 | -0.0078678 | 0.010309 | -0.0077482 | -0.0011471 | 0.0066159 | -0.073242 | 0.19684 | -0.33417 | 0.004578 | -0.018311 | -0.036621 | 0.07782 | 0.16479 | 0.23804 | -0.32959 | -0.26092 | 0.013733 | 0 | 0.07782 | -0.20142 | -0.25635 | 0.054932 | 0.26092 | 0.15106 | 0.23804 | 0.054931 | 0.27008 | 0 | 0.31128 | 0.036621 | -0.25635 | 0.27008 | 0 | 0.036621 | 0.054931 | 0.31128 | -0.51727 | -0.5127
4276.9062 | 0.18768 | -0.032043 | 0.14648 | -0.095062 | -0.0048876 | -0.0072268 | 0.0068915 | -0.0064664 | -0.0013609 | 0.0061887 | -0.018311 | 0.12817 | -0.3067 | 0.10071 | 0.10529 | 0.11902 | -0.10071 | 0.3067 | 0.19226 | -0.31586 | -0.27466 | -0.01831 | 0.013732 | 0.13275 | -0.041198 | -0.28381 | 0.045777 | 0.28839 | -0.068665 | 0.33874 | 0.13733 | 0.16022 | 0.013732 | 0.2243 | 0.15106 | -0.28381 | 0.16022 | 0.013732 | 0.15106 | 0.13733 | 0.2243 | -0.45319 | -0.46234
4277.9062 | 0.19684 | -0.041199 | 0.14191 | -0.10269 | -0.0031786 | -0.011713 | 0.0058233 | -0.0071072 | -0.0030697 | 0.0072569 | -0.022888 | 0.12817 | -0.31128 | 0.10986 | 0.10071 | 0.09613 | -0.11444 | 0.29297 | 0.20142 | -0.33417 | -0.27008 | -0.013733 | 0.018311 | 0.15106 | -0.041199 | -0.29297 | 0.059509 | 0.28839 | -0.073242 | 0.33417 | 0.14191 | 0.16937 | 0.018311 | 0.24262 | 0.13733 | -0.29297 | 0.16937 | 0.018311 | 0.13733 | 0.14191 | 0.24262 | -0.45319 | -0.47607
4278.9062 | 0.20599 | -0.032043 | 0.12817 | -0.049286 | -0.0057422 | -0.011286 | 0.0056097 | -0.0079618 | -0.0030697 | 0.0068295 | -0.022888 | 0.14648 | -0.30212 | 0.10071 | 0.10071 | 0.10986 | -0.091553 | 0.30212 | 0.19684 | -0.33417 | -0.27008 | 0.01831 | 0.009155 | 0.13275 | -0.027466 | -0.30212 | 0.068664 | 0.27924 | -0.05951 | 0.33417 | 0.13275 | 0.17853 | 0.009155 | 0.22888 | 0.14191 | -0.30212 | 0.17853 | 0.009155 | 0.14191 | 0.13275 | 0.22888 | -0.4303 | -0.46234
4279.9062 | 0.20142 | -0.036621 | 0.14191 | -0.087433 | -0.0025378 | -0.014917 | 0.0062507 | -0.004971 | -0.00029266 | 0.0076841 | -0.032043 | 0.13733 | -0.31586 | 0.091553 | 0.07782 | 0.091553 | -0.10071 | 0.28839 | 0.20142 | -0.35248 | -0.27924 | -0.004578 | 0.004578 | 0.12817 | -0.064087 | -0.31586 | 0.059509 | 0.28381 | -0.064087 | 0.32501 | 0.11444 | 0.17395 | 0.004578 | 0.23804 | 0.12817 | -0.31586 | 0.17395 | 0.004578 | 0.12817 | 0.11444 | 0.23804 | -0.45776 | -0.49439
4280.9062 | 0.16937 | -0.041199 | 0.14191 | -0.14084 | -0.0010424 | -0.0080814 | 0.0083869 | -0.0088162 | -0.0013609 | 0.0096067 | -0.004578 | 0.14648 | -0.29297 | 0.10071 | 0.082397 | 0.082397 | -0.07782 | 0.27008 | 0.21057 | -0.3067 | -0.25177 | 0.004577 | 0.036621 | 0.14191 | -0.05951 | -0.2655 | 0.068664 | 0.28839 | -0.036621 | 0.31128 | 0.1236 | 0.18768 | 0.036621 | 0.25177 | 0.1236 | -0.2655 | 0.18768 | 0.036621 | 0.1236 | 0.1236 | 0.25177 | -0.43488 | -0.44861
4281.9062 | 0.18768 | -0.036621 | 0.14648 | -0.056915 | -0.0033922 | -0.010858 | 0.0077459 | -0.0075344 | -0.0011471 | 0.0083249 | -0.050354 | 0.13733 | -0.32044 | 0.091553 | 0.10529 | 0.10529 | -0.09613 | 0.28839 | 0.20142 | -0.35248 | -0.28381 | -0.009155 | -0.013733 | 0.12817 | -0.041198 | -0.31586 | 0.054932 | 0.27008 | -0.059509 | 0.32501 | 0.14191 | 0.17395 | -0.013733 | 0.23804 | 0.14191 | -0.31586 | 0.17395 | -0.013733 | 0.14191 | 0.14191 | 0.23804 | -0.46692 | -0.49896
4282.9062 | 0.18768 | -0.064087 | 0.14648 | 0.0041197 | -0.0059558 | -0.011927 | 0.0053961 | -0.0094572 | -0.00093346 | 0.0089657 | -0.050354 | 0.14191 | -0.30212 | 0.07782 | 0.082397 | 0.091553 | -0.082397 | 0.25177 | 0.20142 | -0.33875 | -0.23804 | -0.004577 | 0.013733 | 0.14191 | -0.064087 | -0.27466 | 0.054932 | 0.25177 | -0.01831 | 0.31586 | 0.14648 | 0.20599 | 0.013733 | 0.2655 | 0.15564 | -0.27466 | 0.20599 | 0.013733 | 0.15564 | 0.14648 | 0.2655 | -0.44861 | -0.48523
4283.9062 | 0.20142 | -0.032043 | 0.11902 | -0.064545 | -0.0025378 | -0.010645 | 0.0064643 | -0.008389 | 0.00034814 | 0.0078977 | -0.027466 | 0.12817 | -0.30212 | 0.13275 | 0.09613 | 0.11902 | -0.12817 | 0.31586 | 0.19684 | -0.33417 | -0.27008 | 0.009155 | 0.004577 | 0.16479 | -0.022889 | -0.30212 | 0.077819 | 0.27466 | -0.096131 | 0.3479 | 0.12817 | 0.16022 | 0.004577 | 0.22888 | 0.15106 | -0.30212 | 0.16022 | 0.004577 | 0.15106 | 0.12817 | 0.22888 | -0.42114 | -0.45319
4284.9062 | 0.20142 | -0.041199 | 0.12817 | -0.087433 | -0.0033922 | -0.0097904 | 0.0071051 | -0.00668 | -0.00050626 | 0.0093931 | -0.022888 | 0.14191 | -0.31128 | 0.1236 | 0.10986 | 0.11444 | -0.10986 | 0.31586 | 0.17853 | -0.32044 | -0.27008 | 0.013733 | 0.018311 | 0.16479 | -0.018311 | -0.27924 | 0.050354 | 0.28839 | -0.068664 | 0.35706 | 0.15106 | 0.18311 | 0.018311 | 0.21973 | 0.15564 | -0.27924 | 0.18311 | 0.018311 | 0.15564 | 0.15106 | 0.21973 | -0.43945 | -0.44861
4285.9219 | 0.11444 | -0.064087 | 0.17395 | -0.2095 | -0.0040332 | -0.010218 | 0.0088141 | -0.0086026 | -0.0013609 | 0.0070431 | -0.018311 | 0.14648 | -0.31586 | 0.073242 | 0.041199 | 0.045776 | -0.004578 | 0.24261 | 0.21057 | -0.32959 | -0.25177 | -0.027466 | 0.045776 | 0.13733 | -0.13275 | -0.2655 | 0.036621 | 0.29755 | 0.059509 | 0.3067 | 0.10529 | 0.21057 | 0.045776 | 0.27466 | 0.10986 | -0.2655 | 0.21057 | 0.045776 | 0.10986 | 0.10529 | 0.27466 | -0.48981 | -0.50354
4286.9062 | 0.19226 | -0.045776 | 0.12817 | -0.049286 | -0.0048876 | -0.01214 | 0.0071051 | -0.0068936 | -0.0013609 | 0.0042661 | -0.036621 | 0.13275 | -0.31586 | 0.09613 | 0.086975 | 0.10071 | -0.10071 | 0.28381 | 0.20599 | -0.33875 | -0.27008 | 0.004577 | 0.009155 | 0.14191 | -0.041199 | -0.29297 | 0.07782 | 0.27924 | -0.054932 | 0.32959 | 0.13275 | 0.17853 | 0.009155 | 0.25177 | 0.14648 | -0.29297 | 0.17853 | 0.009155 | 0.14648 | 0.13275 | 0.25177 | -0.44403 | -0.46692
4287.9062 | 0.18768 | -0.036621 | 0.12817 | -0.13321 | -0.0042468 | -0.012781 | 0.0058233 | -0.0081754 | -0.0022153 | 0.0074705 | -0.041199 | 0.12817 | -0.29755 | 0.10986 | 0.09613 | 0.09613 | -0.09613 | 0.30212 | 0.19226 | -0.33417 | -0.26092 | 0 | -0.004578 | 0.14648 | -0.032044 | -0.29755 | 0.064087 | 0.25635 | -0.059509 | 0.33875 | 0.13275 | 0.1648 | -0.004578 | 0.22888 | 0.13275 | -0.29755 | 0.1648 | -0.004578 | 0.13275 | 0.13275 | 0.22888 | -0.42572 | -0.46234
4288.9062 | 0.18768 | -0.054932 | 0.14191 | -0.064545 | -0.0040332 | -0.011286 | 0.0060369 | -0.0090298 | -0.00093346 | 0.0085385 | -0.054932 | 0.13733 | -0.31586 | 0.086975 | 0.07782 | 0.086975 | -0.10071 | 0.28839 | 0.19684 | -0.3479 | -0.26093 | -0.004578 | 0 | 0.14191 | -0.064087 | -0.29297 | 0.054931 | 0.26093 | -0.045776 | 0.34332 | 0.13275 | 0.19226 | 0 | 0.25177 | 0.14191 | -0.29297 | 0.19226 | 0 | 0.14191 | 0.13275 | 0.25177 | -0.45776 | -0.48981
4289.9062 | 0.1831 | -0.045776 | 0.15106 | -0.0035098 | -0.0038196 | -0.0074404 | 0.0039007 | -0.0056118 | 0.00077554 | 0.0070431 | -0.050354 | 0.12817 | -0.32501 | 0.10071 | 0.068665 | 0.10071 | -0.09613 | 0.27466 | 0.19226 | -0.34332 | -0.27924 | -0.022888 | -0.004578 | 0.14648 | -0.082397 | -0.29755 | 0.041199 | 0.27466 | -0.050354 | 0.32043 | 0.11444 | 0.17395 | -0.004578 | 0.23804 | 0.14648 | -0.29755 | 0.17395 | -0.004578 | 0.14648 | 0.11444 | 0.23804 | -0.47607 | -0.49438
4290.9062 | 0.18768 | -0.032043 | 0.13733 | -0.17899 | -0.0040332 | -0.0072268 | 0.0077459 | -0.0071072 | -0.00029266 | 0.0068295 | 0.009155 | 0.13733 | -0.3067 | 0.12817 | 0.10986 | 0.09613 | -0.082397 | 0.30212 | 0.17395 | -0.29755 | -0.27466 | 0 | 0.041198 | 0.16022 | -0.027466 | -0.2655 | 0.036621 | 0.31586 | -0.050354 | 0.33417 | 0.14191 | 0.16937 | 0.041198 | 0.20599 | 0.12817 | -0.2655 | 0.16937 | 0.041198 | 0.12817 | 0.14191 | 0.20599 | -0.44403 | -0.43488
4291.9062 | 0.20142 | -0.045776 | 0.13733 | -0.072174 | -0.0042468 | -0.011499 | 0.0066779 | -0.0075344 | -0.0015745 | 0.0059751 | -0.022888 | 0.15106 | -0.30212 | 0.10986 | 0.09613 | 0.10986 | -0.10529 | 0.30212 | 0.19684 | -0.32044 | -0.25635 | 0.013733 | 0.022888 | 0.15564 | -0.041199 | -0.27466 | 0.059509 | 0.27924 | -0.05951 | 0.3479 | 0.14191 | 0.19684 | 0.022888 | 0.24261 | 0.15564 | -0.27466 | 0.19684 | 0.022888 | 0.15564 | 0.14191 | 0.24261 | -0.43945 | -0.45776
4292.9062 | 0.17853 | -0.036621 | 0.1236 | -0.079803 | -0.0031786 | -0.010431 | 0.0071051 | -0.0081754 | 0.00013454 | 0.0074705 | -0.041199 | 0.14648 | -0.29297 | 0.10529 | 0.09613 | 0.086975 | -0.10071 | 0.28381 | 0.1831 | -0.34332 | -0.25635 | 0.022888 | -0.004578 | 0.14191 | -0.027466 | -0.3067 | 0.059509 | 0.25177 | -0.064087 | 0.32043 | 0.13275 | 0.18311 | -0.004578 | 0.21973 | 0.1236 | -0.3067 | 0.18311 | -0.004578 | 0.1236 | 0.13275 | 0.21973 | -0.41656 | -0.46692
4293.9062 | 0.19226 | -0.036621 | 0.14191 | -0.079803 | -0.0061694 | -0.014917 | 0.0073187 | -0.0081754 | -0.00071986 | 0.0089657 | -0.027466 | 0.1236 | -0.30212 | 0.10071 | 0.086975 | 0.086975 | -0.091553 | 0.27924 | 0.19226 | -0.31128 | -0.2655 | -0.018311 | 0.009155 | 0.13733 | -0.054932 | -0.27466 | 0.050354 | 0.27466 | -0.054932 | 0.31586 | 0.1236 | 0.16022 | 0.009155 | 0.22888 | 0.1236 | -0.27466 | 0.16022 | 0.009155 | 0.1236 | 0.1236 | 0.22888 | -0.44403 | -0.45319
4294.9062 | 0.18768 | -0.045776 | 0.13275 | -0.011139 | -0.0038196 | -0.01684 | 0.0073187 | -0.0075344 | -0.0013609 | 0.0070431 | -0.041199 | 0.13733 | -0.31586 | 0.07782 | 0.073242 | 0.07782 | -0.091553 | 0.27466 | 0.19226 | -0.3479 | -0.27008 | 0.004578 | 0.004577 | 0.1236 | -0.059509 | -0.30212 | 0.05951 | 0.27466 | -0.045777 | 0.32043 | 0.11902 | 0.18311 | 0.004577 | 0.23804 | 0.1236 | -0.30212 | 0.18311 | 0.004577 | 0.1236 | 0.11902 | 0.23804 | -0.44861 | -0.48065
4295.9062 | 0.18768 | -0.032043 | 0.15106 | -0.19424 | -0.005315 | -0.007654 | 0.0058233 | -0.0090298 | -0.00093346 | 0.0055479 | -0.004578 | 0.13733 | -0.29755 | 0.1236 | 0.11902 | 0.10071 | -0.082397 | 0.31128 | 0.19226 | -0.31128 | -0.2655 | -0.013733 | 0.027465 | 0.15564 | -0.032043 | -0.27924 | 0.041199 | 0.29297 | -0.050354 | 0.34332 | 0.15106 | 0.16937 | 0.027465 | 0.2243 | 0.13275 | -0.27924 | 0.16937 | 0.027465 | 0.13275 | 0.15106 | 0.2243 | -0.44861 | -0.46234
4296.9062 | 0.16937 | -0.050354 | 0.15106 | -0.011139 | -0.0044604 | -0.012567 | 0.0075323 | -0.0090298 | -7.9062e-05 | 0.0083249 | -0.068665 | 0.15564 | -0.32501 | 0.064087 | 0.073242 | 0.064087 | -0.064087 | 0.24261 | 0.18768 | -0.36163 | -0.27466 | 0.004578 | -0.018311 | 0.11444 | -0.07782 | -0.31128 | 0.036621 | 0.25635 | -0.013733 | 0.29297 | 0.1236 | 0.20599 | -0.018311 | 0.23804 | 0.11444 | -0.31128 | 0.20599 | -0.018311 | 0.11444 | 0.1236 | 0.23804 | -0.47607 | -0.5127
4297.9062 | 0.20142 | -0.050354 | 0.12817 | -0.087433 | -0.003606 | -0.014704 | 0.0071051 | -0.0090298 | -0.0020017 | 0.0061887 | -0.045776 | 0.13733 | -0.31128 | 0.086975 | 0.086975 | 0.10071 | -0.10529 | 0.28839 | 0.1831 | -0.32501 | -0.26092 | 0.009155 | 0.004578 | 0.13733 | -0.041199 | -0.27466 | 0.054931 | 0.2655 | -0.054932 | 0.33875 | 0.13733 | 0.18768 | 0.004578 | 0.23346 | 0.15106 | -0.27466 | 0.18768 | 0.004578 | 0.15106 | 0.13733 | 0.23346 | -0.43945 | -0.45319
4298.9062 | 0.19226 | -0.045776 | 0.13733 | -0.11032 | -0.0038196 | -0.010645 | 0.0043281 | -0.0073208 | -0.0015745 | 0.0072569 | -0.045776 | 0.15106 | -0.29755 | 0.091553 | 0.082397 | 0.09613 | -0.09613 | 0.28381 | 0.18768 | -0.35706 | -0.25177 | 0.013733 | 0 | 0.13733 | -0.054932 | -0.31128 | 0.050354 | 0.25177 | -0.050354 | 0.32959 | 0.12817 | 0.19684 | 0 | 0.23346 | 0.14191 | -0.31128 | 0.19684 | 0 | 0.14191 | 0.12817 | 0.23346 | -0.43488 | -0.49438
4299.9062 | 0.17853 | -0.036621 | 0.13275 | -0.041657 | -0.0016834 | -0.013422 | 0.0077459 | -0.0088162 | 0.0014163 | 0.0085385 | -0.054932 | 0.1236 | -0.32044 | 0.07782 | 0.082397 | 0.09613 | -0.07782 | 0.28839 | 0.21515 | -0.33417 | -0.28381 | -0.009155 | -0.018311 | 0.11444 | -0.050354 | -0.29755 | 0.082398 | 0.2655 | -0.041199 | 0.32501 | 0.11902 | 0.16022 | -0.018311 | 0.25177 | 0.13275 | -0.29755 | 0.16022 | -0.018311 | 0.13275 | 0.11902 | 0.25177 | -0.45319 | -0.46692
4300.9062 | 0.013733 | -0.073242 | 0.16479 | -0.26291 | -0.0031786 | -0.011927 | 0.011591 | -0.0088162 | -0.0011471 | 0.0068295 | -0.082397 | 0.16479 | -0.33417 | 0.013733 | 0.004578 | -0.041199 | 0.07782 | 0.17853 | 0.25177 | -0.3067 | -0.26092 | 0 | -0.009155 | 0.086975 | -0.16022 | -0.23346 | 0.086975 | 0.25177 | 0.15106 | 0.25177 | 0.07782 | 0.23804 | -0.009155 | 0.32501 | 0.032043 | -0.23346 | 0.23804 | -0.009155 | 0.032043 | 0.07782 | 0.32501 | -0.49896 | -0.4715
4301.9062 | 0.21973 | -0.027466 | 0.1236 | -0.049286 | -0.0025378 | -0.0097904 | 0.0056097 | -0.0092434 | -0.0011471 | 0.0070431 | -0.022888 | 0.13275 | -0.31586 | 0.1236 | 0.09613 | 0.10986 | -0.11444 | 0.30212 | 0.19684 | -0.31586 | -0.28839 | 0.009155 | 0.004578 | 0.15106 | -0.027466 | -0.28839 | 0.073242 | 0.29297 | -0.086975 | 0.32959 | 0.1236 | 0.16022 | 0.004578 | 0.2243 | 0.13733 | -0.28839 | 0.16022 | 0.004578 | 0.13733 | 0.1236 | 0.2243 | -0.43945 | -0.43945
4302.9062 | 0.16022 | -0.050354 | 0.17395 | 0.0041197 | -0.0044604 | -0.0080814 | 0.0066779 | -0.0098844 | 0.00077554 | 0.0083249 | -0.068665 | 0.14191 | -0.31586 | 0.064087 | 0.068665 | 0.059509 | -0.073242 | 0.2655 | 0.20142 | -0.35248 | -0.2655 | -0.032043 | -0.018311 | 0.11444 | -0.10528 | -0.30212 | 0.027466 | 0.24719 | -0.022888 | 0.31586 | 0.11902 | 0.19226 | -0.018311 | 0.25177 | 0.10986 | -0.30212 | 0.19226 | -0.018311 | 0.10986 | 0.11902 | 0.25177 | -0.48981 | -0.52643
4303.9062 | 0.17853 | -0.050354 | 0.16022 | 0.019379 | -0.0055286 | -0.015345 | 0.0081733 | -0.0060392 | -0.0017881 | 0.0076841 | -0.073242 | 0.1236 | -0.32501 | 0.050354 | 0.045776 | 0.068665 | -0.07782 | 0.25177 | 0.19226 | -0.34332 | -0.27466 | -0.036621 | -0.022888 | 0.10071 | -0.11444 | -0.29297 | 0.032044 | 0.25177 | -0.027466 | 0.30212 | 0.09613 | 0.17395 | -0.022888 | 0.24261 | 0.11902 | -0.29297 | 0.17395 | -0.022888 | 0.11902 | 0.09613 | 0.24261 | -0.48523 | -0.50354
4304.9062 | 0.19684 | -0.041199 | 0.12817 | -0.095062 | -0.0048876 | -0.016413 | 0.0051825 | -0.0096708 | -0.00029266 | 0.0072569 | -0.027466 | 0.11902 | -0.30212 | 0.11444 | 0.082397 | 0.10986 | -0.10071 | 0.27466 | 0.18768 | -0.34332 | -0.26093 | -0.009155 | 0.013733 | 0.15564 | -0.045777 | -0.30212 | 0.059509 | 0.27466 | -0.059509 | 0.31586 | 0.1236 | 0.16022 | 0.013733 | 0.22888 | 0.15106 | -0.30212 | 0.16022 | 0.013733 | 0.15106 | 0.1236 | 0.22888 | -0.4303 | -0.4715
4305.9219 | 0.059509 | -0.07782 | 0.1831 | -0.17899 | -0.0014696 | -0.0095766 | 0.014155 | -0.00668 | 0.00098914 | 0.0053343 | -0.054932 | 0.18768 | -0.32959 | 0.032043 | -0.004578 | -0.022888 | 0.059509 | 0.16937 | 0.2243 | -0.31586 | -0.25177 | 0.004578 | 0.022888 | 0.10986 | -0.18768 | -0.23804 | 0.041199 | 0.27466 | 0.13733 | 0.24719 | 0.073242 | 0.2655 | 0.022888 | 0.30212 | 0.054932 | -0.23804 | 0.2655 | 0.022888 | 0.054932 | 0.073242 | 0.30212 | -0.5127 | -0.49896
4306.9062 | 0.20599 | -0.032043 | 0.14648 | -0.018768 | -0.0074512 | -0.011499 | 0.0056097 | -0.0058256 | 0.00013454 | 0.0072569 | -0.036621 | 0.11902 | -0.30212 | 0.09613 | 0.091553 | 0.10986 | -0.086975 | 0.28839 | 0.18768 | -0.32959 | -0.27008 | -0.027465 | -0.004578 | 0.12817 | -0.054931 | -0.29755 | 0.041199 | 0.2655 | -0.054932 | 0.32043 | 0.1236 | 0.15106 | -0.004578 | 0.21973 | 0.14191 | -0.29755 | 0.15106 | -0.004578 | 0.14191 | 0.1236 | 0.21973 | -0.44861 | -0.47607
4307.9062 | 0.20599 | -0.050354 | 0.13733 | -0.072174 | -0.002965 | -0.01214 | 0.0086005 | -0.0071072 | 0.00013454 | 0.0083249 | -0.041199 | 0.1236 | -0.32959 | 0.09613 | 0.09613 | 0.09613 | -0.10986 | 0.28381 | 0.19684 | -0.32959 | -0.27924 | -0.013733 | 0.009155 | 0.14648 | -0.041199 | -0.27924 | 0.059509 | 0.28839 | -0.059509 | 0.33417 | 0.14648 | 0.17395 | 0.009155 | 0.24719 | 0.14648 | -0.27924 | 0.17395 | 0.009155 | 0.14648 | 0.14648 | 0.24719 | -0.46692 | -0.46692
4308.9062 | 0.19684 | -0.018311 | 0.15564 | -0.14084 | -0.0040332 | -0.014276 | 0.0068915 | -0.0079618 | -0.00071986 | 0.0055479 | 0.009155 | 0.1236 | -0.30212 | 0.10986 | 0.10071 | 0.10986 | -0.082397 | 0.32501 | 0.18768 | -0.29297 | -0.28381 | -0.032044 | 0.027466 | 0.12817 | -0.054932 | -0.27466 | 0.032043 | 0.31128 | -0.064086 | 0.34332 | 0.11902 | 0.14191 | 0.027466 | 0.20599 | 0.12817 | -0.27466 | 0.14191 | 0.027466 | 0.12817 | 0.11902 | 0.20599 | -0.45776 | -0.44861
4309.9062 | 0.19226 | -0.045776 | 0.14191 | -0.087433 | -0.0025378 | -0.013636 | 0.0053961 | -0.0088162 | -0.0017881 | 0.0072569 | -0.036621 | 0.12817 | -0.32501 | 0.10071 | 0.10071 | 0.09613 | -0.091553 | 0.27466 | 0.19684 | -0.32959 | -0.27924 | -0.013733 | 0.009155 | 0.14648 | -0.041199 | -0.28381 | 0.054931 | 0.28839 | -0.045777 | 0.32043 | 0.14648 | 0.17395 | 0.009155 | 0.24261 | 0.14191 | -0.28381 | 0.17395 | 0.009155 | 0.14191 | 0.14648 | 0.24261 | -0.46692 | -0.4715
4310.9062 | 0.073242 | -0.064087 | 0.16022 | -0.24765 | -0.0044604 | -0.011713 | 0.0090277 | -0.0064664 | 0.00056194 | 0.0061887 | -0.036621 | 0.16937 | -0.3067 | 0.045776 | 0.036621 | 0.009155 | 0.045776 | 0.19226 | 0.22888 | -0.3067 | -0.24261 | 0.009156 | 0.027466 | 0.10986 | -0.1236 | -0.24261 | 0.068665 | 0.27008 | 0.10986 | 0.25635 | 0.10071 | 0.23346 | 0.027466 | 0.29297 | 0.073242 | -0.24261 | 0.23346 | 0.027466 | 0.073242 | 0.10071 | 0.29297 | -0.46692 | -0.46692
4311.9062 | 0.19226 | -0.036621 | 0.12817 | -0.14084 | -0.0048876 | -0.012354 | 0.0075323 | -0.0064664 | -0.0026425 | 0.010247 | -0.004578 | 0.13275 | -0.29297 | 0.1236 | 0.10071 | 0.10529 | -0.082397 | 0.30212 | 0.19684 | -0.30212 | -0.25635 | 0.004577 | 0.032043 | 0.16022 | -0.027466 | -0.2655 | 0.068664 | 0.28839 | -0.045776 | 0.33875 | 0.13733 | 0.16937 | 0.032043 | 0.23346 | 0.14191 | -0.2655 | 0.16937 | 0.032043 | 0.14191 | 0.13733 | 0.23346 | -0.42114 | -0.4303
4312.9062 | 0.19226 | -0.032043 | 0.14191 | -0.11795 | -0.0044604 | -0.010645 | 0.0073187 | -0.0077482 | -0.0032835 | 0.0085385 | 0 | 0.11902 | -0.3067 | 0.11444 | 0.09613 | 0.09613 | -0.091553 | 0.31128 | 0.19684 | -0.29297 | -0.27466 | -0.022888 | 0.032043 | 0.14648 | -0.045777 | -0.26093 | 0.054931 | 0.3067 | -0.05951 | 0.34332 | 0.12817 | 0.15106 | 0.032043 | 0.22888 | 0.12817 | -0.26093 | 0.15106 | 0.032043 | 0.12817 | 0.12817 | 0.22888 | -0.44861 | -0.43488
4313.9062 | 0.073242 | -0.054932 | 0.17395 | -0.22476 | -0.0025378 | -0.009363 | 0.010737 | -0.008389 | -0.0028561 | 0.0074705 | -0.041199 | 0.15106 | -0.32959 | 0.045776 | 0.018311 | 0.013733 | 0.036621 | 0.20142 | 0.23804 | -0.31586 | -0.27466 | -0.022888 | 0.013733 | 0.10071 | -0.15564 | -0.26093 | 0.064087 | 0.28839 | 0.091553 | 0.25635 | 0.073243 | 0.20599 | 0.013733 | 0.29297 | 0.068665 | -0.26093 | 0.20599 | 0.013733 | 0.068665 | 0.073243 | 0.29297 | -0.50354 | -0.48981
4314.9219 | 0.10529 | -0.073242 | 0.16479 | -0.087433 | -0.00040164 | -0.004877 | 0.013727 | -0.0034756 | -0.0013609 | 0.0068295 | -0.018311 | 0.17853 | -0.32959 | 0.054932 | 0.013733 | 0.009155 | 0 | 0.18768 | 0.21515 | -0.34332 | -0.25635 | 0.013733 | 0.054931 | 0.12817 | -0.15106 | -0.27008 | 0.050354 | 0.31128 | 0.073242 | 0.26092 | 0.086975 | 0.25177 | 0.054931 | 0.28839 | 0.082397 | -0.27008 | 0.25177 | 0.054931 | 0.082397 | 0.086975 | 0.28839 | -0.49438 | -0.50812
4315.9219 | 0.10529 | -0.073242 | 0.16479 | -0.0035098 | 0.00045296 | -0.0080814 | 0.016077 | -0.0017666 | -0.0013609 | 0.0072569 | -0.018311 | 0.1831 | -0.33875 | 0.045776 | 0.041199 | 0.022888 | -0.009155 | 0.17853 | 0.23346 | -0.34332 | -0.2655 | 0.01831 | 0.054931 | 0.11902 | -0.1236 | -0.27008 | 0.068664 | 0.32043 | 0.064087 | 0.25177 | 0.11444 | 0.25635 | 0.054931 | 0.3067 | 0.09613 | -0.27008 | 0.25635 | 0.054931 | 0.09613 | 0.11444 | 0.3067 | -0.50354 | -0.50812
4316.9062 | 0.18768 | -0.036621 | 0.12817 | -0.12558 | -0.0051012 | -0.010218 | 0.0041143 | -0.003903 | -0.0026425 | 0.0066159 | -0.009155 | 0.13733 | -0.30212 | 0.091553 | 0.10986 | 0.10529 | -0.082397 | 0.30212 | 0.19226 | -0.29755 | -0.2655 | 0.009155 | 0.027466 | 0.12817 | -0.018311 | -0.26092 | 0.064087 | 0.29297 | -0.045776 | 0.33875 | 0.14648 | 0.17395 | 0.027466 | 0.22888 | 0.14191 | -0.26092 | 0.17395 | 0.027466 | 0.14191 | 0.14648 | 0.22888 | -0.4303 | -0.42572
4317.9062 | 0.19684 | -0.045776 | 0.13733 | -0.087433 | -0.0057422 | -0.015131 | 0.0073187 | -0.0068936 | -0.0013609 | 0.0083249 | -0.004578 | 0.10986 | -0.3067 | 0.09613 | 0.10986 | 0.11902 | -0.07782 | 0.31128 | 0.19226 | -0.3067 | -0.26093 | -0.027466 | 0.041198 | 0.14191 | -0.027466 | -0.26093 | 0.054932 | 0.30212 | -0.032044 | 0.35705 | 0.15564 | 0.15564 | 0.041198 | 0.23804 | 0.16479 | -0.26093 | 0.15564 | 0.041198 | 0.16479 | 0.15564 | 0.23804 | -0.44403 | -0.44403
4318.9062 | 0.036621 | -0.082397 | 0.1831 | -0.24765 | -0.0014696 | -0.0091494 | 0.010309 | -0.008389 | -0.0022153 | 0.0061887 | -0.07782 | 0.21515 | -0.32501 | -0.013733 | -0.004578 | -0.027466 | 0.086975 | 0.16937 | 0.23346 | -0.29297 | -0.24262 | 0.032044 | 0.004577 | 0.068664 | -0.18768 | -0.21057 | 0.050354 | 0.24719 | 0.16937 | 0.25177 | 0.077819 | 0.29755 | 0.004577 | 0.31586 | 0.054931 | -0.21057 | 0.29755 | 0.004577 | 0.054931 | 0.077819 | 0.31586 | -0.50812 | -0.47607
4319.9062 | 0.10071 | -0.054932 | 0.16937 | -0.11795 | -0.0031786 | -0.0085086 | 0.017573 | -0.0030484 | -0.0015745 | 0.0089657 | -0.027466 | 0.20142 | -0.32959 | 0.059509 | 0.041199 | 0.032043 | 0.018311 | 0.21057 | 0.22888 | -0.3067 | -0.27466 | 0.032043 | 0.027466 | 0.11444 | -0.12817 | -0.25177 | 0.059509 | 0.30212 | 0.073243 | 0.2655 | 0.096131 | 0.25635 | 0.027466 | 0.28381 | 0.086975 | -0.25177 | 0.25635 | 0.027466 | 0.086975 | 0.096131 | 0.28381 | -0.49896 | -0.47607
4320.9062 | 0.082397 | -0.064087 | 0.17853 | -0.23239 | -0.0033922 | -0.01449 | 0.010096 | -0.0045438 | -0.0015745 | 0.0057615 | -0.041199 | 0.15106 | -0.31586 | 0.018311 | 0.036621 | 0.004578 | 0.045776 | 0.19684 | 0.21973 | -0.28839 | -0.25177 | -0.027466 | 0.022888 | 0.082398 | -0.14191 | -0.2243 | 0.041199 | 0.27466 | 0.10986 | 0.26093 | 0.10071 | 0.21515 | 0.022888 | 0.28381 | 0.068665 | -0.2243 | 0.21515 | 0.022888 | 0.068665 | 0.10071 | 0.28381 | -0.49438 | -0.46692
4321.9062 | 0.15564 | -0.013733 | 0.12817 | -0.18662 | -0.0027514 | -0.011927 | 0.0075323 | -0.0047574 | -0.0026425 | 0.0078977 | 0.009155 | 0.1236 | -0.31128 | 0.07782 | 0.09613 | 0.10986 | -0.036621 | 0.27924 | 0.19684 | -0.28839 | -0.29755 | -0.004578 | 0.022888 | 0.091553 | -0.032044 | -0.27466 | 0.068664 | 0.32043 | -0.022888 | 0.29297 | 0.10986 | 0.13733 | 0.022888 | 0.21057 | 0.1236 | -0.27466 | 0.13733 | 0.022888 | 0.1236 | 0.10986 | 0.21057 | -0.43945 | -0.41657
4322.9062 | 0.068665 | -0.073242 | 0.16937 | -0.27054 | -0.0044604 | -0.011499 | 0.010523 | -0.0071072 | -0.0034971 | 0.0072569 | -0.027466 | 0.16937 | -0.32044 | 0.004578 | 0.022888 | 0.004578 | 0.041199 | 0.19684 | 0.21515 | -0.31586 | -0.24719 | 0 | 0.045776 | 0.07782 | -0.14649 | -0.24261 | 0.045776 | 0.29297 | 0.11444 | 0.27008 | 0.09613 | 0.24261 | 0.045776 | 0.28839 | 0.07782 | -0.24261 | 0.24261 | 0.045776 | 0.07782 | 0.09613 | 0.28839 | -0.48981 | -0.48523
4323.9219 | 0.091553 | -0.086975 | 0.16479 | 0.072784 | 0.00088016 | -0.0097904 | 0.015009 | -0.0034756 | -0.0015745 | 0.0068295 | -0.013733 | 0.1831 | -0.33417 | 0.018311 | -0.013733 | -0.013733 | 0.027466 | 0.15106 | 0.22888 | -0.38452 | -0.24719 | 0.01831 | 0.073242 | 0.10529 | -0.17853 | -0.29755 | 0.064087 | 0.32043 | 0.11444 | 0.23804 | 0.073242 | 0.27008 | 0.073242 | 0.31586 | 0.073242 | -0.29755 | 0.27008 | 0.073242 | 0.073242 | 0.073242 | 0.31586 | -0.49896 | -0.54932
4324.9219 | 0.15564 | -0.082397 | 0.13275 | 0.20248 | -0.002965 | -0.0089358 | 0.015864 | -0.0019802 | -0.0026425 | 0.0078977 | -0.091553 | 0.15106 | -0.35248 | 0.013733 | 0.018311 | 0.022888 | -0.050354 | 0.19226 | 0.22888 | -0.40283 | -0.27008 | 0.018311 | -0.009156 | 0.09613 | -0.11444 | -0.32044 | 0.096131 | 0.26093 | 0.032043 | 0.27466 | 0.10071 | 0.23346 | -0.009156 | 0.31128 | 0.10528 | -0.32044 | 0.23346 | -0.009156 | 0.10528 | 0.10071 | 0.31128 | -0.48523 | -0.53558
4325.9062 | 0.11444 | -0.068665 | 0.14648 | -0.018768 | -0.00040164 | -0.0089358 | 0.013727 | -0.0043302 | -0.0024289 | 0.0068295 | -0.027466 | 0.1831 | -0.34332 | 0.041199 | 0.022888 | 0.036621 | 0.004578 | 0.20142 | 0.21057 | -0.34332 | -0.27466 | 0.036621 | 0.041199 | 0.10986 | -0.1236 | -0.27466 | 0.064087 | 0.31586 | 0.073243 | 0.27008 | 0.091553 | 0.25177 | 0.041199 | 0.27924 | 0.10529 | -0.27466 | 0.25177 | 0.041199 | 0.10529 | 0.091553 | 0.27924 | -0.48981 | -0.48981
4326.9062 | 0.091553 | -0.050354 | 0.17395 | -0.26291 | -0.0031786 | -0.010431 | 0.0060369 | -0.0034756 | -0.0028561 | 0.0083249 | -0.036621 | 0.15106 | -0.31128 | 0.041199 | 0.050354 | 0.041199 | 0.032043 | 0.21973 | 0.23346 | -0.29755 | -0.26092 | -0.022888 | 0.013733 | 0.091553 | -0.1236 | -0.24719 | 0.059509 | 0.27466 | 0.082397 | 0.27008 | 0.10071 | 0.20142 | 0.013733 | 0.28381 | 0.091553 | -0.24719 | 0.20142 | 0.013733 | 0.091553 | 0.10071 | 0.28381 | -0.48523 | -0.4715
4327.9062 | 0.10529 | -0.036621 | 0.16937 | -0.26291 | -0.0031786 | -0.014704 | 0.0071051 | -0.0056118 | -0.0028561 | 0.0081113 | -0.036621 | 0.14648 | -0.3067 | 0.036621 | 0.054932 | 0.041199 | 0.013733 | 0.21973 | 0.21515 | -0.3067 | -0.27008 | -0.022889 | 0 | 0.073242 | -0.11444 | -0.27008 | 0.045776 | 0.27008 | 0.050354 | 0.25635 | 0.091553 | 0.18311 | 0 | 0.25177 | 0.07782 | -0.27008 | 0.18311 | 0 | 0.07782 | 0.091553 | 0.25177 | -0.47607 | -0.47607
4328.9062 | 0.073242 | -0.10071 | 0.17395 | 0.11093 | 0.0013074 | -0.0055178 | 0.014795 | -0.0030484 | -0.0020017 | 0.0076841 | -0.068665 | 0.17395 | -0.36163 | -0.013733 | -0.036621 | -0.022888 | 0.032043 | 0.11902 | 0.23804 | -0.40741 | -0.26092 | 0 | 0.032043 | 0.086975 | -0.21057 | -0.3067 | 0.064087 | 0.29297 | 0.13275 | 0.21973 | 0.064087 | 0.27466 | 0.032043 | 0.33875 | 0.07782 | -0.3067 | 0.27466 | 0.032043 | 0.07782 | 0.064087 | 0.33875 | -0.53558 | -0.58136
4329.9062 | 0.050354 | -0.086975 | 0.17395 | -0.32394 | -0.0021106 | -0.010645 | 0.0096685 | -0.0045438 | -0.0020017 | 0.010034 | -0.07782 | 0.17395 | -0.33417 | -0.022888 | -0.009155 | -0.022888 | 0.091553 | 0.19684 | 0.24719 | -0.29297 | -0.24719 | 0 | 0.009155 | 0.064087 | -0.1831 | -0.20599 | 0.073242 | 0.25635 | 0.17853 | 0.28381 | 0.07782 | 0.26092 | 0.009155 | 0.33417 | 0.064087 | -0.20599 | 0.26092 | 0.009155 | 0.064087 | 0.07782 | 0.33417 | -0.50812 | -0.46692
4330.9062 | 0.14648 | -0.050354 | 0.15564 | -0.20187 | -0.0061694 | -0.014276 | 0.0077459 | -0.0043302 | -0.0032835 | 0.0081113 | -0.013733 | 0.12817 | -0.29755 | 0.050354 | 0.068665 | 0.07782 | -0.018311 | 0.27924 | 0.20599 | -0.27924 | -0.24719 | -0.027466 | 0.036621 | 0.10071 | -0.086975 | -0.22888 | 0.050354 | 0.28381 | 0.032043 | 0.32959 | 0.11902 | 0.17853 | 0.036621 | 0.25635 | 0.12817 | -0.22888 | 0.17853 | 0.036621 | 0.12817 | 0.11902 | 0.25635 | -0.45319 | -0.43488
4331.9062 | 0.16022 | -0.050354 | 0.14191 | -0.14084 | -0.002965 | -0.011927 | 0.0056097 | -0.0068936 | -0.0034971 | 0.0085385 | -0.013733 | 0.13275 | -0.3067 | 0.064087 | 0.082397 | 0.07782 | -0.036621 | 0.27008 | 0.20599 | -0.30212 | -0.25635 | -0.009156 | 0.036621 | 0.11444 | -0.05951 | -0.25177 | 0.064087 | 0.29297 | 0.013733 | 0.32044 | 0.13275 | 0.18311 | 0.036621 | 0.25635 | 0.12817 | -0.25177 | 0.18311 | 0.036621 | 0.12817 | 0.13275 | 0.25635 | -0.44861 | -0.44403
4332.9062 | 0.068665 | -0.064087 | 0.18768 | -0.24002 | -0.0040332 | -0.014063 | 0.0086005 | -0.0088162 | -0.0026425 | 0.0072569 | -0.050354 | 0.16937 | -0.32044 | 0 | -0.013733 | -0.009155 | 0.050354 | 0.20599 | 0.2243 | -0.30212 | -0.25635 | -0.01831 | 0.013733 | 0.064087 | -0.20142 | -0.23804 | 0.036621 | 0.27008 | 0.11444 | 0.27008 | 0.050354 | 0.23346 | 0.013733 | 0.28839 | 0.054932 | -0.23804 | 0.23346 | 0.013733 | 0.054932 | 0.050354 | 0.28839 | -0.50812 | -0.48981
4333.9219 | 0.14648 | -0.086975 | 0.14648 | 0.18723 | -0.0027514 | -0.0080814 | 0.011805 | -0.0047574 | -0.0024289 | 0.0074705 | -0.068665 | 0.14191 | -0.33875 | 0.009155 | -0.018311 | 0.032043 | -0.050354 | 0.17395 | 0.21515 | -0.41657 | -0.25177 | -0.004577 | 0.01831 | 0.09613 | -0.16479 | -0.32959 | 0.068665 | 0.27008 | 0.036621 | 0.26092 | 0.068664 | 0.22888 | 0.01831 | 0.30212 | 0.11902 | -0.32959 | 0.22888 | 0.01831 | 0.11902 | 0.068664 | 0.30212 | -0.48523 | -0.56305
4334.9062 | 0.059509 | -0.086975 | 0.18768 | -0.21713 | -0.003606 | -0.0089358 | 0.012446 | -0.0062528 | -0.0020017 | 0.0087521 | -0.068665 | 0.19684 | -0.33875 | -0.009155 | -0.022888 | -0.009155 | 0.073242 | 0.17395 | 0.23804 | -0.27924 | -0.25177 | 0.009155 | 0.01831 | 0.07782 | -0.21057 | -0.19226 | 0.050354 | 0.27008 | 0.16022 | 0.26092 | 0.064087 | 0.28381 | 0.01831 | 0.32501 | 0.07782 | -0.19226 | 0.28381 | 0.01831 | 0.07782 | 0.064087 | 0.32501 | -0.52643 | -0.46692
4335.9062 | 0.10529 | -0.064087 | 0.15106 | -0.034027 | 0.00045296 | -0.0089358 | 0.015009 | -0.0047574 | -0.0020017 | 0.0087521 | -0.022888 | 0.17395 | -0.35248 | 0.041199 | 0.032043 | 0.027466 | 0.018311 | 0.20142 | 0.2243 | -0.32501 | -0.28839 | 0.022888 | 0.041199 | 0.10529 | -0.11902 | -0.26093 | 0.073242 | 0.32959 | 0.082398 | 0.2655 | 0.09613 | 0.23804 | 0.041199 | 0.28839 | 0.091553 | -0.26093 | 0.23804 | 0.041199 | 0.091553 | 0.09613 | 0.28839 | -0.50354 | -0.47607
4336.9062 | 0.045776 | -0.068665 | 0.17395 | -0.27817 | -0.0021106 | -0.0074404 | 0.0083869 | -0.0043302 | -0.0026425 | 0.0055479 | -0.07782 | 0.1831 | -0.32501 | -0.004578 | 0 | -0.013733 | 0.086975 | 0.19226 | 0.24261 | -0.29297 | -0.25635 | 0.009155 | -0.009155 | 0.064087 | -0.17395 | -0.2243 | 0.068665 | 0.24719 | 0.15564 | 0.26093 | 0.068665 | 0.25177 | -0.009155 | 0.31128 | 0.054932 | -0.2243 | 0.25177 | -0.009155 | 0.054932 | 0.068665 | 0.31128 | -0.49896 | -0.46692
4337.9062 | 0.13275 | -0.050354 | 0.16022 | -0.14847 | -0.0023242 | -0.011072 | 0.0073187 | -0.0053982 | -0.0015745 | 0.0061887 | -0.004578 | 0.13733 | -0.31128 | 0.068665 | 0.082397 | 0.073242 | -0.013733 | 0.2655 | 0.21515 | -0.30212 | -0.26092 | -0.022888 | 0.045776 | 0.11902 | -0.07782 | -0.25177 | 0.054932 | 0.3067 | 0.036621 | 0.31586 | 0.13275 | 0.18768 | 0.045776 | 0.2655 | 0.1236 | -0.25177 | 0.18768 | 0.045776 | 0.1236 | 0.13275 | 0.2655 | -0.4715 | -0.46234
4338.9219 | 0.21057 | -0.032043 | 0.13275 | -0.056915 | -0.004674 | -0.011072 | 0.0071051 | -0.00668 | -0.0015745 | 0.0074705 | -0.018311 | 0.12817 | -0.31128 | 0.091553 | 0.10071 | 0.10529 | -0.10071 | 0.3067 | 0.19226 | -0.3067 | -0.27924 | -0.004577 | 0.013732 | 0.1236 | -0.032043 | -0.27466 | 0.05951 | 0.29297 | -0.068665 | 0.33874 | 0.13275 | 0.16022 | 0.013732 | 0.2243 | 0.13733 | -0.27466 | 0.16022 | 0.013732 | 0.13733 | 0.13275 | 0.2243 | -0.44403 | -0.43945
4339.9062 | 0.07782 | -0.054932 | 0.17395 | -0.24765 | -0.0057422 | -0.010431 | 0.010737 | -0.0060392 | -0.0015745 | 0.0068295 | -0.050354 | 0.14648 | -0.32959 | -0.004578 | -0.018311 | -0.013733 | 0.09613 | 0.1831 | 0.24261 | -0.30212 | -0.27466 | -0.027466 | 0.004578 | 0.050354 | -0.19226 | -0.24719 | 0.068665 | 0.27924 | 0.15106 | 0.23804 | 0.036621 | 0.20142 | 0.004578 | 0.29755 | 0.041199 | -0.24719 | 0.20142 | 0.004578 | 0.041199 | 0.036621 | 0.29755 | -0.50354 | -0.47607
4340.9219 | 0.16479 | -0.07782 | 0.14191 | 0.22537 | 0.00066656 | -0.0097904 | 0.017145 | -0.0026212 | -0.00093346 | 0.0064023 | -0.064087 | 0.14648 | -0.35706 | 0.018311 | 0.009155 | 0.032043 | -0.068665 | 0.1831 | 0.22888 | -0.40741 | -0.27924 | 0.004577 | 0.013733 | 0.096131 | -0.13275 | -0.32959 | 0.086975 | 0.29297 | 0.009155 | 0.26092 | 0.086975 | 0.2243 | 0.013733 | 0.3067 | 0.10986 | -0.32959 | 0.2243 | 0.013733 | 0.10986 | 0.086975 | 0.3067 | -0.49896 | -0.54932
4341.9062 | 0.050354 | -0.068665 | 0.16479 | -0.2095 | -0.002965 | -0.0085086 | 0.0092413 | -0.0058256 | -0.0024289 | 0.0096067 | -0.082397 | 0.19226 | -0.34332 | -0.009155 | -0.027466 | -0.036621 | 0.091553 | 0.1831 | 0.25635 | -0.3067 | -0.27466 | 0.027466 | -0.013732 | 0.05951 | -0.19226 | -0.23804 | 0.091553 | 0.26093 | 0.16022 | 0.25177 | 0.041199 | 0.26093 | -0.013732 | 0.32501 | 0.032044 | -0.23804 | 0.26093 | -0.013732 | 0.032044 | 0.041199 | 0.32501 | -0.50812 | -0.4715
4342.9219 | 0.07782 | -0.10529 | 0.19226 | 0.057526 | 2.5564e-05 | -0.0035952 | 0.017573 | -0.0041166 | -0.0028561 | 0.0098203 | -0.041199 | 0.16937 | -0.35706 | -0.009155 | -0.036621 | -0.045776 | 0.045776 | 0.13275 | 0.23346 | -0.39825 | -0.25177 | -0.022888 | 0.064087 | 0.096131 | -0.22888 | -0.29297 | 0.041198 | 0.31586 | 0.15106 | 0.23804 | 0.068665 | 0.27466 | 0.064087 | 0.33875 | 0.05951 | -0.29297 | 0.27466 | 0.064087 | 0.05951 | 0.068665 | 0.33875 | -0.54932 | -0.59052
4343.9219 | 0.050354 | -0.073242 | 0.17395 | -0.17899 | -0.0023242 | -0.012567 | 0.0094549 | -0.0043302 | -0.00071986 | 0.0083249 | -0.086975 | 0.17853 | -0.32959 | -0.018311 | -0.013733 | -0.022888 | 0.09613 | 0.17395 | 0.2655 | -0.27924 | -0.25635 | 0.004578 | -0.013733 | 0.054931 | -0.18768 | -0.20599 | 0.091553 | 0.24261 | 0.16937 | 0.24719 | 0.059509 | 0.25177 | -0.013733 | 0.33874 | 0.050354 | -0.20599 | 0.25177 | -0.013733 | 0.050354 | 0.059509 | 0.33874 | -0.50354 | -0.45319
4344.9062 | 0.091553 | -0.064087 | 0.16479 | -0.011139 | -0.0014696 | -0.0087222 | 0.01565 | -0.0045438 | -0.0022153 | 0.0096067 | -0.013733 | 0.17853 | -0.3479 | 0.018311 | 0.009155 | 0.004578 | 0.013733 | 0.1831 | 0.23346 | -0.34332 | -0.28381 | 0.013733 | 0.050354 | 0.082398 | -0.15564 | -0.27924 | 0.068664 | 0.33417 | 0.07782 | 0.24719 | 0.073242 | 0.24261 | 0.050354 | 0.29755 | 0.068665 | -0.27924 | 0.24261 | 0.050354 | 0.068665 | 0.073242 | 0.29755 | -0.5127 | -0.50812
4345.9062 | 0.045776 | -0.082397 | 0.17853 | -0.23239 | -0.00040164 | -0.013849 | 0.011164 | -0.0047574 | -0.0011471 | 0.0087521 | -0.073242 | 0.20142 | -0.34332 | -0.018311 | -0.013733 | -0.022888 | 0.10529 | 0.16937 | 0.22888 | -0.28839 | -0.26093 | 0.022888 | 0.009155 | 0.064086 | -0.19226 | -0.20599 | 0.050354 | 0.27008 | 0.18768 | 0.25177 | 0.068664 | 0.28381 | 0.009155 | 0.31128 | 0.059509 | -0.20599 | 0.28381 | 0.009155 | 0.059509 | 0.068664 | 0.31128 | -0.52185 | -0.46692
4346.9062 | 0.10529 | -0.068665 | 0.16937 | -0.14084 | -0.0021106 | -0.010858 | 0.014155 | -0.0034756 | -7.9062e-05 | 0.0055479 | -0.009155 | 0.16479 | -0.3479 | 0.022888 | 0.036621 | 0.022888 | 0.022888 | 0.21057 | 0.2243 | -0.32959 | -0.27924 | -0.004578 | 0.05951 | 0.091553 | -0.13275 | -0.26092 | 0.054931 | 0.33874 | 0.091553 | 0.27924 | 0.10529 | 0.23346 | 0.05951 | 0.29297 | 0.091553 | -0.26092 | 0.23346 | 0.05951 | 0.091553 | 0.10529 | 0.29297 | -0.51727 | -0.49896
4347.9062 | 0.11444 | -0.07782 | 0.17395 | -0.22476 | -0.0025378 | -0.008295 | 0.013514 | -0.0034756 | -0.0015745 | 0.0057615 | -0.009155 | 0.17853 | -0.33417 | 0.054932 | 0.022888 | 0.027466 | 0.018311 | 0.21057 | 0.2243 | -0.32044 | -0.25635 | 0.004578 | 0.068665 | 0.13275 | -0.15106 | -0.24262 | 0.050354 | 0.32501 | 0.096131 | 0.28839 | 0.10071 | 0.25635 | 0.068665 | 0.30212 | 0.10529 | -0.24262 | 0.25635 | 0.068665 | 0.10529 | 0.10071 | 0.30212 | -0.50812 | -0.49439
4348.9219 | 0.073242 | -0.091553 | 0.16479 | -0.11032 | 2.5564e-05 | -0.0091494 | 0.011591 | -0.001553 | -0.0022153 | 0.0064023 | -0.045776 | 0.19226 | -0.3479 | -0.009155 | 0.004578 | -0.009155 | 0.073242 | 0.17853 | 0.24261 | -0.28839 | -0.25635 | 0.027466 | 0.045777 | 0.082398 | -0.16022 | -0.19684 | 0.07782 | 0.30212 | 0.16479 | 0.27008 | 0.096131 | 0.28381 | 0.045777 | 0.33417 | 0.082398 | -0.19684 | 0.28381 | 0.045777 | 0.082398 | 0.096131 | 0.33417 | -0.5127 | -0.45319
4349.9062 | 0.068665 | -0.059509 | 0.16022 | -0.24765 | -0.002965 | -0.010218 | 0.0081733 | -0.0045438 | -0.0020017 | 0.0089657 | -0.082397 | 0.20142 | -0.33417 | -0.022888 | -0.013733 | -0.022888 | 0.10071 | 0.16937 | 0.24261 | -0.28381 | -0.27466 | 0.041199 | -0.022888 | 0.036621 | -0.17395 | -0.2243 | 0.082398 | 0.25177 | 0.16022 | 0.22888 | 0.045776 | 0.26093 | -0.022888 | 0.30212 | 0.036621 | -0.2243 | 0.26093 | -0.022888 | 0.036621 | 0.045776 | 0.30212 | -0.49438 | -0.44403
4350.9219 | 0.068665 | -0.10529 | 0.16937 | 0.14145 | 0.00023916 | -0.0059452 | 0.01565 | -0.0017666 | -0.00071986 | 0.0096067 | -0.059509 | 0.16479 | -0.36621 | -0.022888 | -0.036621 | -0.018311 | 0.041199 | 0.09613 | 0.24719 | -0.41199 | -0.26093 | -0.004578 | 0.045777 | 0.082398 | -0.20599 | -0.3067 | 0.077819 | 0.3067 | 0.14649 | 0.20142 | 0.068665 | 0.27008 | 0.045777 | 0.35248 | 0.086975 | -0.3067 | 0.27008 | 0.045777 | 0.086975 | 0.068665 | 0.35248 | -0.53558 | -0.58136
4351.9062 | 0.054932 | -0.068665 | 0.1831 | -0.24765 | -0.00040164 | -0.0087222 | 0.0090277 | -0.0024076 | 0.00034814 | 0.0091795 | -0.068665 | 0.19684 | -0.32959 | -0.022888 | -0.018311 | -0.022888 | 0.10529 | 0.15564 | 0.25635 | -0.27924 | -0.26092 | 0.013733 | 0 | 0.045777 | -0.20142 | -0.21057 | 0.073243 | 0.26092 | 0.17395 | 0.22431 | 0.050354 | 0.2655 | 0 | 0.32501 | 0.045777 | -0.21057 | 0.2655 | 0 | 0.045777 | 0.050354 | 0.32501 | -0.5127 | -0.46234
4352.9219 | 0.091553 | -0.11902 | 0.15564 | 0.22537 | -0.00061524 | -0.0067996 | 0.012873 | -0.002194 | -0.0028561 | 0.0087521 | -0.086975 | 0.16479 | -0.3479 | -0.032043 | -0.041199 | -0.022888 | 0.027466 | 0.13733 | 0.22888 | -0.43488 | -0.22888 | 0.009155 | 0.032044 | 0.086976 | -0.19684 | -0.31586 | 0.073242 | 0.26092 | 0.14649 | 0.25635 | 0.07782 | 0.28381 | 0.032044 | 0.3479 | 0.096131 | -0.31586 | 0.28381 | 0.032044 | 0.096131 | 0.07782 | 0.3479 | -0.50354 | -0.59052
4353.9219 | 0.14648 | -0.064087 | 0.14648 | 0.019379 | -0.0044604 | -0.0087222 | 0.0060369 | -0.0024076 | -0.00071986 | 0.0091795 | -0.091553 | 0.13733 | -0.32959 | 0.032043 | 0.036621 | 0.059509 | -0.054932 | 0.21973 | 0.20142 | -0.36163 | -0.2655 | -0.009155 | -0.027466 | 0.09613 | -0.10986 | -0.29755 | 0.054932 | 0.23804 | 0.009155 | 0.28381 | 0.10071 | 0.20142 | -0.027466 | 0.2655 | 0.1236 | -0.29755 | 0.20142 | -0.027466 | 0.1236 | 0.10071 | 0.2655 | -0.47607 | -0.50812
4354.9062 | 0.07782 | -0.068665 | 0.17853 | -0.2095 | -0.003606 | -0.0070132 | 0.014582 | -0.0079618 | -0.0047787 | 0.0093931 | -0.064087 | 0.19226 | -0.33417 | -0.004578 | -0.018311 | -0.018311 | 0.07782 | 0.1831 | 0.22888 | -0.31586 | -0.2655 | 0.013733 | 0.004578 | 0.064087 | -0.19684 | -0.24719 | 0.050354 | 0.27008 | 0.14649 | 0.25177 | 0.050354 | 0.26093 | 0.004578 | 0.29755 | 0.050354 | -0.24719 | 0.26093 | 0.004578 | 0.050354 | 0.050354 | 0.29755 | -0.5127 | -0.49438
4355.9062 | 0.068665 | -0.07782 | 0.16937 | -0.16373 | -0.00061524 | -0.010645 | 0.013086 | -0.0051846 | -0.0030697 | 0.0098203 | -0.068665 | 0.18768 | -0.33875 | -0.018311 | -0.004578 | -0.022888 | 0.073242 | 0.16937 | 0.24719 | -0.3067 | -0.26093 | 0.01831 | 0.009155 | 0.059509 | -0.17395 | -0.22888 | 0.077819 | 0.27008 | 0.15106 | 0.24719 | 0.073242 | 0.2655 | 0.009155 | 0.32501 | 0.054932 | -0.22888 | 0.2655 | 0.009155 | 0.054932 | 0.073242 | 0.32501 | -0.50812 | -0.47607
4356.9062 | 0.10529 | -0.068665 | 0.15106 | -0.064545 | 0.00045296 | -0.010218 | 0.014795 | -0.0036892 | 0.00013454 | 0.0076841 | -0.004578 | 0.17853 | -0.33417 | 0.036621 | 0.018311 | 0.022888 | -0.004578 | 0.19684 | 0.21973 | -0.33417 | -0.2655 | 0.027466 | 0.064087 | 0.10529 | -0.13275 | -0.2655 | 0.068665 | 0.32959 | 0.064087 | 0.2655 | 0.086976 | 0.24719 | 0.064087 | 0.28839 | 0.091553 | -0.2655 | 0.24719 | 0.064087 | 0.091553 | 0.086976 | 0.28839 | -0.48523 | -0.48523
4357.9062 | 0.12817 | -0.059509 | 0.16479 | -0.19424 | -0.0021106 | -0.008295 | 0.0051825 | -0.0030484 | -0.0015745 | 0.0087521 | -0.013733 | 0.14191 | -0.31128 | 0.032043 | 0.054932 | 0.041199 | 0.009155 | 0.24719 | 0.21057 | -0.29297 | -0.25177 | -0.022888 | 0.045776 | 0.091552 | -0.10986 | -0.23346 | 0.045776 | 0.29755 | 0.068664 | 0.3067 | 0.11444 | 0.20142 | 0.045776 | 0.27008 | 0.10071 | -0.23346 | 0.20142 | 0.045776 | 0.10071 | 0.11444 | 0.27008 | -0.47607 | -0.45776
4358.9219 | 0.054932 | -0.07782 | 0.1831 | -0.16373 | -0.003606 | -0.010858 | 0.013086 | -0.003903 | -0.0020017 | 0.010675 | -0.068665 | 0.19684 | -0.33875 | 0.004578 | -0.018311 | -0.022888 | 0.059509 | 0.17395 | 0.24719 | -0.28381 | -0.26093 | 0.013733 | 0.009155 | 0.082398 | -0.20142 | -0.20599 | 0.064087 | 0.27008 | 0.13733 | 0.25177 | 0.059509 | 0.27466 | 0.009155 | 0.32501 | 0.054932 | -0.20599 | 0.27466 | 0.009155 | 0.054932 | 0.059509 | 0.32501 | -0.52185 | -0.46692
4359.9062 | 0.059509 | -0.073242 | 0.17395 | -0.21713 | -0.0038196 | -0.010858 | 0.012232 | -0.0045438 | -0.00050626 | 0.0066159 | -0.059509 | 0.19684 | -0.32044 | -0.018311 | -0.018311 | -0.022888 | 0.09613 | 0.16479 | 0.24719 | -0.29755 | -0.24719 | 0.022888 | 0.013733 | 0.054931 | -0.19226 | -0.2243 | 0.073242 | 0.26093 | 0.16937 | 0.23804 | 0.054931 | 0.27008 | 0.013733 | 0.32043 | 0.050354 | -0.2243 | 0.27008 | 0.013733 | 0.050354 | 0.054931 | 0.32043 | -0.49439 | -0.4715
4360.9219 | 0.068665 | -0.09613 | 0.17395 | 0.1033 | -0.0010424 | -0.010645 | 0.015436 | -0.0028348 | -0.0032835 | 0.0076841 | -0.041199 | 0.16937 | -0.35248 | -0.013733 | -0.027466 | -0.018311 | 0.032043 | 0.11444 | 0.26093 | -0.3891 | -0.25635 | -0.004577 | 0.054931 | 0.082397 | -0.20142 | -0.29297 | 0.086975 | 0.31128 | 0.12817 | 0.21057 | 0.068664 | 0.2655 | 0.054931 | 0.35706 | 0.077819 | -0.29297 | 0.2655 | 0.054931 | 0.077819 | 0.068664 | 0.35706 | -0.52643 | -0.56305
4361.9062 | 0.059509 | -0.07782 | 0.16479 | -0.22476 | -0.0048876 | -0.0095766 | 0.0092413 | -0.0060392 | -0.00050626 | 0.0081113 | -0.073242 | 0.18768 | -0.34332 | -0.018311 | 0.004578 | -0.009155 | 0.059509 | 0.17853 | 0.24261 | -0.28839 | -0.2655 | 0.022888 | 0.004578 | 0.059509 | -0.16022 | -0.21057 | 0.07782 | 0.27008 | 0.13733 | 0.25635 | 0.082398 | 0.2655 | 0.004578 | 0.32044 | 0.068665 | -0.21057 | 0.2655 | 0.004578 | 0.068665 | 0.082398 | 0.32044 | -0.50812 | -0.45319
4362.9062 | 0.09613 | -0.059509 | 0.15564 | -0.087433 | -0.002965 | -0.0085086 | 0.014155 | -0.0034756 | -0.00093346 | 0.0066159 | 0 | 0.17395 | -0.33417 | 0.027466 | 0.027466 | 0.013733 | 0.009155 | 0.20142 | 0.2243 | -0.32501 | -0.27466 | 0.01831 | 0.059509 | 0.086975 | -0.12817 | -0.2655 | 0.068664 | 0.33417 | 0.068664 | 0.26093 | 0.086975 | 0.23346 | 0.059509 | 0.28381 | 0.073242 | -0.2655 | 0.23346 | 0.059509 | 0.073242 | 0.086975 | 0.28381 | -0.48981 | -0.48065
4363.9062 | 0.10529 | -0.07782 | 0.16479 | -0.23239 | -0.00040164 | -0.0080814 | 0.011591 | -0.0047574 | -0.0022153 | 0.0068295 | -0.059509 | 0.18768 | -0.34332 | -0.004578 | 0.018311 | -0.009155 | 0.064087 | 0.17853 | 0.23346 | -0.28381 | -0.2655 | 0.022888 | 0.018311 | 0.073242 | -0.14648 | -0.20599 | 0.068664 | 0.28381 | 0.14191 | 0.25635 | 0.096131 | 0.2655 | 0.018311 | 0.31128 | 0.068665 | -0.20599 | 0.2655 | 0.018311 | 0.068665 | 0.096131 | 0.31128 | -0.50812 | -0.44861
4364.9062 | 0.09613 | -0.07782 | 0.15106 | -0.049286 | -0.0021106 | -0.0080814 | 0.014582 | -0.0034756 | -0.0017881 | 0.0074705 | -0.004578 | 0.16479 | -0.3479 | 0.022888 | 0.018311 | 0.013733 | 0.009155 | 0.17395 | 0.22888 | -0.33875 | -0.27008 | 0.013733 | 0.073242 | 0.10071 | -0.13275 | -0.26093 | 0.07782 | 0.34332 | 0.086975 | 0.25177 | 0.096131 | 0.24261 | 0.073242 | 0.3067 | 0.091553 | -0.26093 | 0.24261 | 0.073242 | 0.091553 | 0.096131 | 0.3067 | -0.49896 | -0.48981
4365.9062 | 0.059509 | -0.086975 | 0.16937 | -0.079803 | -0.0033922 | -0.008295 | 0.0075323 | -0.0056118 | -0.00050626 | 0.0072569 | -0.064087 | 0.17395 | -0.33417 | -0.022888 | -0.013733 | -0.013733 | 0.068665 | 0.18768 | 0.23804 | -0.28839 | -0.24719 | 0.004577 | 0.022888 | 0.064087 | -0.18311 | -0.20142 | 0.068664 | 0.27008 | 0.15564 | 0.27466 | 0.073242 | 0.26092 | 0.022888 | 0.32501 | 0.073242 | -0.20142 | 0.26092 | 0.022888 | 0.073242 | 0.073242 | 0.32501 | -0.50354 | -0.45776
4366.9219 | 0.18768 | -0.068665 | 0.13275 | 0.24826 | 2.5564e-05 | -0.010004 | 0.01095 | -0.0056118 | -0.0017881 | 0.0074705 | -0.054932 | 0.1236 | -0.35706 | 0.032043 | 0.041199 | 0.068665 | -0.10071 | 0.21973 | 0.19684 | -0.40283 | -0.28839 | -0.009155 | 0.013733 | 0.10071 | -0.091552 | -0.33417 | 0.064087 | 0.30212 | -0.032043 | 0.28839 | 0.10986 | 0.19226 | 0.013733 | 0.2655 | 0.13733 | -0.33417 | 0.19226 | 0.013733 | 0.13733 | 0.10986 | 0.2655 | -0.48981 | -0.53558
4367.9062 | 0.082397 | -0.068665 | 0.17853 | -0.18662 | -0.002965 | -0.010218 | 0.010523 | -0.0028348 | -0.0013609 | 0.0042661 | -0.064087 | 0.17395 | -0.32959 | 0 | -0.004578 | -0.018311 | 0.068665 | 0.1831 | 0.23346 | -0.29297 | -0.26092 | -0.004578 | 0.004578 | 0.068665 | -0.18311 | -0.2243 | 0.054931 | 0.2655 | 0.13733 | 0.25177 | 0.064087 | 0.24261 | 0.004578 | 0.30212 | 0.050354 | -0.2243 | 0.24261 | 0.004578 | 0.050354 | 0.064087 | 0.30212 | -0.50812 | -0.4715
4368.9219 | 0.082397 | -0.073242 | 0.15106 | 0.080414 | -0.0025378 | -0.0063724 | 0.015223 | -0.002194 | -0.0030697 | 0.0074705 | -0.091553 | 0.16022 | -0.36163 | -0.050354 | -0.050354 | -0.050354 | 0.059509 | 0.10986 | 0.25177 | -0.3891 | -0.28839 | 0.009155 | -0.018311 | 0.022888 | -0.20142 | -0.31586 | 0.10071 | 0.27008 | 0.13275 | 0.18311 | 0.022888 | 0.23346 | -0.018311 | 0.32501 | 0.022888 | -0.31586 | 0.23346 | -0.018311 | 0.022888 | 0.022888 | 0.32501 | -0.5127 | -0.54016
4369.9062 | 0.11444 | -0.082397 | 0.14648 | 0.15671 | 2.5564e-05 | -0.010858 | 0.010523 | -0.001553 | -0.00050626 | 0.0076841 | -0.073242 | 0.15106 | -0.35706 | -0.022888 | -0.004578 | 0.009155 | -0.013733 | 0.15106 | 0.2243 | -0.43945 | -0.27466 | 0.004578 | 0.009155 | 0.059509 | -0.15106 | -0.35706 | 0.07782 | 0.28381 | 0.068664 | 0.23346 | 0.077819 | 0.23346 | 0.009155 | 0.3067 | 0.091552 | -0.35706 | 0.23346 | 0.009155 | 0.091552 | 0.077819 | 0.3067 | -0.50354 | -0.58594
4370.9062 | 0.10071 | -0.068665 | 0.16479 | -0.14084 | -0.0016834 | -0.0097904 | 0.011164 | -0.0024076 | -0.0015745 | 0.0061887 | -0.013733 | 0.17395 | -0.34332 | 0.041199 | 0.027466 | 0.013733 | 0.032043 | 0.21057 | 0.23804 | -0.28839 | -0.27466 | 0.009155 | 0.054932 | 0.10986 | -0.13733 | -0.21973 | 0.073242 | 0.32959 | 0.10071 | 0.27924 | 0.096131 | 0.24261 | 0.054932 | 0.3067 | 0.082398 | -0.21973 | 0.24261 | 0.054932 | 0.082398 | 0.096131 | 0.3067 | -0.50812 | -0.45319
4371.9062 | 0.050354 | -0.07782 | 0.16937 | -0.26291 | -0.001256 | -0.0061588 | 0.0090277 | -0.0034756 | -0.0020017 | 0.0066159 | -0.064087 | 0.17395 | -0.33875 | -0.036621 | -0.004578 | -0.027466 | 0.10071 | 0.16022 | 0.24261 | -0.29755 | -0.26093 | 0.004577 | 0.013733 | 0.041199 | -0.17395 | -0.21973 | 0.073242 | 0.27466 | 0.17853 | 0.23804 | 0.073242 | 0.25177 | 0.013733 | 0.32044 | 0.050354 | -0.21973 | 0.25177 | 0.013733 | 0.050354 | 0.073242 | 0.32044 | -0.50812 | -0.46692
4372.9062 | 0.10529 | -0.07782 | 0.16937 | -0.0035098 | -0.003606 | -0.006586 | 0.014368 | -0.0024076 | -0.0015745 | 0.0083249 | -0.004578 | 0.16479 | -0.32044 | 0.004578 | -0.004578 | 0.009155 | 0.013733 | 0.17395 | 0.22888 | -0.3479 | -0.24262 | -0.004578 | 0.073242 | 0.082398 | -0.17395 | -0.27008 | 0.059509 | 0.31586 | 0.091553 | 0.25177 | 0.073242 | 0.24261 | 0.073242 | 0.3067 | 0.086975 | -0.27008 | 0.24261 | 0.073242 | 0.086975 | 0.073242 | 0.3067 | -0.48981 | -0.51727
4373.9062 | 0.050354 | -0.07782 | 0.1831 | -0.18662 | -0.0025378 | -0.010218 | 0.0073187 | -0.0034756 | -0.0022153 | 0.0057615 | -0.073242 | 0.18768 | -0.32959 | -0.027466 | -0.032043 | -0.036621 | 0.091553 | 0.16022 | 0.23346 | -0.27924 | -0.25177 | 0.004578 | 0.004578 | 0.050354 | -0.21515 | -0.20142 | 0.050354 | 0.25635 | 0.16937 | 0.23804 | 0.045777 | 0.2655 | 0.004578 | 0.31128 | 0.041199 | -0.20142 | 0.2655 | 0.004578 | 0.041199 | 0.045777 | 0.31128 | -0.5127 | -0.46234
4374.9062 | 0.091553 | -0.068665 | 0.17853 | -0.095062 | -0.00040164 | -0.010004 | 0.010523 | -0.0036892 | -0.0020017 | 0.0081113 | 0.009155 | 0.17853 | -0.3479 | 0.027466 | 0.022888 | 0.009155 | 0.013733 | 0.21057 | 0.23804 | -0.29755 | -0.27924 | 0 | 0.07782 | 0.096131 | -0.15564 | -0.22888 | 0.059509 | 0.35706 | 0.082398 | 0.27924 | 0.091553 | 0.24719 | 0.07782 | 0.3067 | 0.07782 | -0.22888 | 0.24719 | 0.07782 | 0.07782 | 0.091553 | 0.3067 | -0.52643 | -0.47607
4375.9219 | 0.091553 | -0.091553 | 0.16022 | 0.14145 | 0.00088016 | -0.010645 | 0.014155 | -0.0028348 | -0.00093346 | 0.0083249 | -0.07782 | 0.14191 | -0.36621 | -0.050354 | -0.032043 | -0.027466 | 0.018311 | 0.11902 | 0.24261 | -0.40283 | -0.27466 | -0.01831 | 0.013733 | 0.041199 | -0.19226 | -0.31128 | 0.082398 | 0.28839 | 0.10986 | 0.21057 | 0.05951 | 0.23346 | 0.013733 | 0.33417 | 0.064087 | -0.31128 | 0.23346 | 0.013733 | 0.064087 | 0.05951 | 0.33417 | -0.52643 | -0.56305
4376.9062 | 0.10529 | -0.086975 | 0.15564 | -0.041657 | -0.001256 | -0.010004 | 0.011591 | -0.003262 | -0.0017881 | 0.0081113 | -0.009155 | 0.16022 | -0.34332 | 0 | 0.004578 | -0.009155 | 0.018311 | 0.15106 | 0.24719 | -0.3479 | -0.25635 | 0.004577 | 0.07782 | 0.086975 | -0.15106 | -0.26092 | 0.091552 | 0.33417 | 0.10529 | 0.23804 | 0.091553 | 0.24719 | 0.07782 | 0.33417 | 0.07782 | -0.26092 | 0.24719 | 0.07782 | 0.07782 | 0.091553 | 0.33417 | -0.49896 | -0.50354
4377.9219 | 0.19684 | -0.050354 | 0.11902 | 0.21011 | 0.00066656 | -0.0059452 | 0.0066779 | -0.0017666 | 0.00056194 | 0.0083249 | -0.013733 | 0.082397 | -0.34332 | 0.064087 | 0.082397 | 0.10529 | -0.15106 | 0.25635 | 0.20599 | -0.40283 | -0.29297 | -0.036622 | 0.036621 | 0.11444 | -0.036622 | -0.35248 | 0.086975 | 0.32959 | -0.10071 | 0.3067 | 0.13275 | 0.13275 | 0.036621 | 0.25635 | 0.15564 | -0.35248 | 0.13275 | 0.036621 | 0.15564 | 0.13275 | 0.25635 | -0.46234 | -0.52185
4378.9062 | 0.09613 | -0.064087 | 0.15564 | -0.20187 | -0.001897 | -0.0085086 | 0.011164 | -0.0034756 | -0.00093346 | 0.0091795 | -0.041199 | 0.1831 | -0.3479 | -0.004578 | 0.004578 | 0 | 0.054932 | 0.18768 | 0.24261 | -0.31586 | -0.28381 | 0.027465 | 0.022888 | 0.059509 | -0.15106 | -0.25177 | 0.086975 | 0.3067 | 0.11902 | 0.25177 | 0.068665 | 0.24719 | 0.022888 | 0.3067 | 0.064087 | -0.25177 | 0.24719 | 0.022888 | 0.064087 | 0.068665 | 0.3067 | -0.50354 | -0.4715
4379.9062 | 0.050354 | -0.068665 | 0.16479 | -0.17899 | -0.0031786 | -0.0063724 | 0.0062507 | -0.0047574 | -0.0032835 | 0.0087521 | -0.054932 | 0.16937 | -0.32501 | -0.009155 | -0.004578 | -0.018311 | 0.07782 | 0.18768 | 0.24261 | -0.3067 | -0.25635 | 0.004578 | 0.013733 | 0.05951 | -0.16937 | -0.23804 | 0.07782 | 0.27008 | 0.14649 | 0.25635 | 0.064087 | 0.23804 | 0.013733 | 0.31128 | 0.050354 | -0.23804 | 0.23804 | 0.013733 | 0.050354 | 0.064087 | 0.31128 | -0.48981 | -0.4715
4380.9062 | 0.086975 | -0.10071 | 0.15106 | -0.041657 | 0.0010938 | -0.0055178 | 0.015009 | -0.0026212 | -0.0022153 | 0.0081113 | -0.004578 | 0.16937 | -0.33417 | 0.022888 | -0.004578 | 0.009155 | 0.022888 | 0.1831 | 0.2243 | -0.35248 | -0.23346 | 0.018311 | 0.09613 | 0.1236 | -0.15564 | -0.25177 | 0.073242 | 0.32959 | 0.1236 | 0.28381 | 0.09613 | 0.27008 | 0.09613 | 0.32501 | 0.10986 | -0.25177 | 0.27008 | 0.09613 | 0.10986 | 0.09613 | 0.32501 | -0.48523 | -0.50354
4381.9062 | 0.10529 | -0.068665 | 0.17395 | -0.011139 | 0.00023916 | -0.0044498 | 0.011805 | -0.001553 | -0.0039243 | 0.0074705 | -0.004578 | 0.18768 | -0.33417 | 0.027466 | 0.022888 | 0.013733 | 0.004578 | 0.20142 | 0.23346 | -0.3479 | -0.2655 | 0.013733 | 0.064087 | 0.096131 | -0.15106 | -0.27924 | 0.059509 | 0.32959 | 0.073243 | 0.27008 | 0.091553 | 0.25635 | 0.064087 | 0.30212 | 0.082398 | -0.27924 | 0.25635 | 0.064087 | 0.082398 | 0.091553 | 0.30212 | -0.50812 | -0.52185
4382.9062 | 0.073242 | -0.073242 | 0.1831 | -0.19424 | -0.0023242 | -0.012995 | 0.0096685 | -0.0013394 | -7.9062e-05 | 0.0076841 | -0.059509 | 0.18768 | -0.3479 | -0.027466 | -0.018311 | -0.022888 | 0.07782 | 0.1831 | 0.23804 | -0.26093 | -0.27466 | 0.004578 | 0.013733 | 0.045776 | -0.20142 | -0.18768 | 0.054932 | 0.28839 | 0.15106 | 0.25635 | 0.054931 | 0.26092 | 0.013733 | 0.31128 | 0.050354 | -0.18768 | 0.26092 | 0.013733 | 0.050354 | 0.054931 | 0.31128 | -0.531 | -0.44403
4383.9062 | 0.054932 | -0.068665 | 0.1831 | -0.17136 | -0.0031786 | -0.0089358 | 0.0075323 | -0.0036892 | -0.0037107 | 0.010461 | -0.07782 | 0.16022 | -0.33417 | -0.018311 | -0.009155 | -0.022888 | 0.086975 | 0.16937 | 0.21973 | -0.29755 | -0.2655 | -0.022888 | -0.009155 | 0.050354 | -0.19226 | -0.22888 | 0.036622 | 0.25635 | 0.15564 | 0.23804 | 0.05951 | 0.22888 | -0.009155 | 0.28839 | 0.045777 | -0.22888 | 0.22888 | -0.009155 | 0.045777 | 0.05951 | 0.28839 | -0.51727 | -0.48065
4384.9062 | 0.082397 | -0.07782 | 0.16022 | -0.0035098 | -0.001256 | -0.010431 | 0.013727 | -0.003262 | -0.0024289 | 0.0078977 | -0.022888 | 0.15564 | -0.33417 | -0.004578 | 0.009155 | -0.004578 | 0.022888 | 0.17395 | 0.23804 | -0.36163 | -0.25635 | -0.004577 | 0.054932 | 0.073242 | -0.15106 | -0.28381 | 0.07782 | 0.31128 | 0.10071 | 0.25177 | 0.086975 | 0.23346 | 0.054932 | 0.31586 | 0.073242 | -0.28381 | 0.23346 | 0.054932 | 0.073242 | 0.086975 | 0.31586 | -0.49438 | -0.52185
4385.9062 | 0.068665 | -0.064087 | 0.19226 | -0.21713 | -0.0010424 | -0.009363 | 0.0096685 | -0.0028348 | -0.00093346 | 0.0064023 | -0.045776 | 0.1831 | -0.33875 | -0.027466 | -0.022888 | -0.027466 | 0.082397 | 0.16022 | 0.24719 | -0.27924 | -0.27466 | -0.009156 | 0.018311 | 0.036621 | -0.21515 | -0.21515 | 0.054931 | 0.29297 | 0.14648 | 0.2243 | 0.041199 | 0.24719 | 0.018311 | 0.31128 | 0.036621 | -0.21515 | 0.24719 | 0.018311 | 0.036621 | 0.041199 | 0.31128 | -0.53101 | -0.4715
4386.9062 | 0.073242 | -0.068665 | 0.17395 | -0.23239 | -0.0027514 | -0.0089358 | 0.0092413 | -0.0036892 | -0.0022153 | 0.0081113 | -0.064087 | 0.16937 | -0.32501 | -0.036621 | -0.022888 | -0.018311 | 0.086975 | 0.16937 | 0.22888 | -0.27924 | -0.25635 | -0.004577 | 0.004578 | 0.032044 | -0.19684 | -0.21057 | 0.054932 | 0.26093 | 0.15564 | 0.23804 | 0.045777 | 0.23804 | 0.004578 | 0.29755 | 0.050354 | -0.21057 | 0.23804 | 0.004578 | 0.050354 | 0.045777 | 0.29755 | -0.49896 | -0.45319
4387.9219 | 0.050354 | -0.09613 | 0.16479 | 0.065155 | -0.00082884 | -0.0050906 | 0.014795 | -0.0013394 | -0.00093346 | 0.0064023 | -0.045776 | 0.15564 | -0.35706 | -0.027466 | -0.032043 | -0.027466 | 0.054932 | 0.13275 | 0.23804 | -0.37079 | -0.26093 | -0.009155 | 0.050354 | 0.068664 | -0.19684 | -0.27466 | 0.073242 | 0.31128 | 0.15106 | 0.22888 | 0.064087 | 0.25177 | 0.050354 | 0.33417 | 0.068664 | -0.27466 | 0.25177 | 0.050354 | 0.068664 | 0.064087 | 0.33417 | -0.52185 | -0.53558
4388.9062 | 0.09613 | -0.064087 | 0.15564 | -0.072174 | 0.00066656 | -0.0059452 | 0.013086 | -0.00069859 | -0.0026425 | 0.0068295 | 0.004578 | 0.17853 | -0.33417 | 0.018311 | 0.018311 | 0.004578 | 0.004578 | 0.1831 | 0.25177 | -0.36163 | -0.27008 | 0.022888 | 0.068665 | 0.082398 | -0.13733 | -0.29755 | 0.09613 | 0.33875 | 0.068665 | 0.24719 | 0.082398 | 0.24261 | 0.068665 | 0.31586 | 0.068665 | -0.29755 | 0.24261 | 0.068665 | 0.068665 | 0.082398 | 0.31586 | -0.48981 | -0.51727
4389.9062 | 0.064087 | -0.091553 | 0.17853 | -0.2095 | -0.0016834 | -0.011072 | 0.0090277 | -0.0030484 | -0.0011471 | 0.0085385 | -0.068665 | 0.1831 | -0.35248 | -0.022888 | -0.022888 | -0.027466 | 0.082397 | 0.16937 | 0.24261 | -0.27008 | -0.26093 | 0.004577 | 0.022888 | 0.068665 | -0.20142 | -0.17853 | 0.064087 | 0.28381 | 0.17395 | 0.26093 | 0.068665 | 0.27466 | 0.022888 | 0.33417 | 0.064087 | -0.17853 | 0.27466 | 0.022888 | 0.064087 | 0.068665 | 0.33417 | -0.53101 | -0.44861
4390.9219 | 0.18768 | -0.07782 | 0.14191 | 0.22537 | -0.0016834 | -0.009363 | 0.010309 | -0.0045438 | -0.0011471 | 0.0087521 | -0.054932 | 0.12817 | -0.35706 | 0.032043 | 0.041199 | 0.054932 | -0.091553 | 0.21515 | 0.19684 | -0.41657 | -0.27924 | -0.013733 | 0.022888 | 0.10986 | -0.10071 | -0.33875 | 0.054931 | 0.30212 | -0.013733 | 0.29297 | 0.11902 | 0.20599 | 0.022888 | 0.27466 | 0.13275 | -0.33875 | 0.20599 | 0.022888 | 0.13275 | 0.11902 | 0.27466 | -0.49896 | -0.55847
4391.9062 | 0.07782 | -0.073242 | 0.15564 | -0.14847 | 0.0013074 | -0.010218 | 0.010523 | -0.004971 | -0.00093346 | 0.0083249 | -0.059509 | 0.19684 | -0.33875 | 0.004578 | -0.004578 | -0.004578 | 0.07782 | 0.16937 | 0.27008 | -0.29297 | -0.2655 | 0.041198 | 0.013733 | 0.07782 | -0.16022 | -0.21973 | 0.11444 | 0.27924 | 0.15106 | 0.24261 | 0.068664 | 0.27008 | 0.013733 | 0.34332 | 0.068664 | -0.21973 | 0.27008 | 0.013733 | 0.068664 | 0.068664 | 0.34332 | -0.49439 | -0.44861
4392.9062 | 0.10529 | -0.073242 | 0.16022 | -0.064545 | -0.00018804 | -0.0046634 | 0.014155 | -0.00048499 | -0.0022153 | 0.0078977 | 0 | 0.17395 | -0.33417 | 0.004578 | 0 | 0.009155 | 0.009155 | 0.19226 | 0.2243 | -0.33417 | -0.26092 | 0.013733 | 0.073242 | 0.07782 | -0.16022 | -0.26092 | 0.064087 | 0.33417 | 0.082397 | 0.2655 | 0.073242 | 0.24719 | 0.073242 | 0.29755 | 0.082397 | -0.26092 | 0.24719 | 0.073242 | 0.082397 | 0.073242 | 0.29755 | -0.49438 | -0.49438
4393.9219 | 0.15106 | -0.10071 | 0.12817 | 0.22537 | -0.001256 | -0.0091494 | 0.010309 | -0.0030484 | -0.0028561 | 0.0085385 | -0.059509 | 0.13275 | -0.35248 | 0.004578 | 0.013733 | 0.036621 | -0.059509 | 0.1831 | 0.21057 | -0.40283 | -0.25177 | 0.004577 | 0.041199 | 0.10529 | -0.11444 | -0.30212 | 0.082397 | 0.29297 | 0.041199 | 0.28381 | 0.11444 | 0.23346 | 0.041199 | 0.31128 | 0.13733 | -0.30212 | 0.23346 | 0.041199 | 0.13733 | 0.11444 | 0.31128 | -0.48065 | -0.53101
4394.9062 | 0.10986 | -0.059509 | 0.16022 | -0.19424 | -0.0016834 | -0.006586 | 0.01095 | -0.0034756 | -0.00093346 | 0.0070431 | -0.013733 | 0.16937 | -0.32959 | 0.050354 | 0.041199 | 0.013733 | 0.032043 | 0.21515 | 0.23804 | -0.3067 | -0.27008 | 0.009156 | 0.045776 | 0.10986 | -0.11902 | -0.24719 | 0.07782 | 0.31586 | 0.091552 | 0.27466 | 0.10071 | 0.22888 | 0.045776 | 0.29755 | 0.073242 | -0.24719 | 0.22888 | 0.045776 | 0.073242 | 0.10071 | 0.29755 | -0.48981 | -0.46692
4395.9219 | 0.15564 | -0.068665 | 0.15106 | 0.21774 | 2.5564e-05 | -0.011713 | 0.0098823 | -0.0019802 | 0.00077554 | 0.0089657 | -0.064087 | 0.14191 | -0.3479 | -0.013733 | -0.004578 | 0.013733 | -0.059509 | 0.17853 | 0.22888 | -0.40283 | -0.27924 | -0.009155 | 0.004578 | 0.054932 | -0.15564 | -0.33417 | 0.07782 | 0.28381 | 0.009156 | 0.24719 | 0.064087 | 0.21057 | 0.004578 | 0.29755 | 0.082398 | -0.33417 | 0.21057 | 0.004578 | 0.082398 | 0.064087 | 0.29755 | -0.49896 | -0.55389
4396.9219 | 0.19226 | -0.068665 | 0.1236 | 0.3627 | -0.001256 | -0.007654 | 0.0090277 | -0.00091219 | -0.0037107 | 0.0057615 | 0.004578 | 0.10071 | -0.36163 | 0.064087 | 0.082397 | 0.091553 | -0.13275 | 0.25635 | 0.18768 | -0.41199 | -0.29297 | -0.022888 | 0.073243 | 0.13275 | -0.041199 | -0.34332 | 0.064087 | 0.36621 | -0.064086 | 0.32501 | 0.15106 | 0.16937 | 0.073243 | 0.25635 | 0.16022 | -0.34332 | 0.16937 | 0.073243 | 0.16022 | 0.15106 | 0.25635 | -0.48523 | -0.53558
4397.9062 | 0.064087 | -0.068665 | 0.1831 | -0.2095 | -0.00061524 | -0.011286 | 0.0098823 | -0.004971 | -0.0017881 | 0.0070431 | -0.068665 | 0.17853 | -0.32959 | -0.018311 | -0.004578 | -0.027466 | 0.082397 | 0.17853 | 0.24719 | -0.28381 | -0.26092 | -0.004577 | 0 | 0.050354 | -0.18768 | -0.21515 | 0.064087 | 0.26092 | 0.15106 | 0.24719 | 0.064087 | 0.24719 | 0 | 0.31586 | 0.041199 | -0.21515 | 0.24719 | 0 | 0.041199 | 0.064087 | 0.31586 | -0.5127 | -0.46692
4398.9062 | 0.10986 | -0.068665 | 0.15106 | -0.087433 | -0.0025378 | -0.009363 | 0.013086 | -0.0041166 | -0.00071986 | 0.0078977 | 0.013733 | 0.16022 | -0.31586 | 0.027466 | 0.013733 | 0.018311 | 0.013733 | 0.18768 | 0.23346 | -0.33875 | -0.24719 | 0.009155 | 0.082398 | 0.096131 | -0.13733 | -0.27008 | 0.082397 | 0.32959 | 0.082398 | 0.25635 | 0.082398 | 0.22888 | 0.082398 | 0.30212 | 0.086976 | -0.27008 | 0.22888 | 0.082398 | 0.086976 | 0.082398 | 0.30212 | -0.46692 | -0.48981
4399.9375 | 0.20599 | -0.064087 | 0.12817 | 0.20248 | -0.0014696 | -0.0072268 | 0.010523 | -0.0017666 | -0.00093346 | 0.0087521 | -0.004578 | 0.082397 | -0.34332 | 0.059509 | 0.086975 | 0.10071 | -0.13733 | 0.2655 | 0.17853 | -0.41657 | -0.27924 | -0.045777 | 0.059509 | 0.1236 | -0.041199 | -0.35248 | 0.050354 | 0.33874 | -0.073242 | 0.32959 | 0.15106 | 0.14648 | 0.059509 | 0.24261 | 0.1648 | -0.35248 | 0.14648 | 0.059509 | 0.1648 | 0.15106 | 0.24261 | -0.4715 | -0.54474
4400.9844 | 0.19226 | -0.032043 | 0.13733 | -0.27054 | -0.0033922 | -0.011072 | 0.0066779 | -0.0043302 | -0.0015745 | 0.0070431 | 0.004578 | 0.11902 | -0.31586 | 0.082397 | 0.09613 | 0.09613 | -0.073242 | 0.31128 | 0.20599 | -0.28381 | -0.28381 | -0.01831 | 0.036621 | 0.11444 | -0.041199 | -0.25177 | 0.068665 | 0.32044 | -0.041199 | 0.34332 | 0.12817 | 0.15106 | 0.036621 | 0.23804 | 0.12817 | -0.25177 | 0.15106 | 0.036621 | 0.12817 | 0.12817 | 0.23804 | -0.45319 | -0.42114

## Thermal Data
Fire Time | North 25 C | Conduit Top | Conduit Bottom | TC Cable
-0.3865 | 242.8535 | 63.1095 | 59.7094 | 32.5953
0.6135 | 243.0958 | 63.247 | 59.8393 | 32.6542
1.6135 | 243.3518 | 63.4024 | 59.9859 | 32.7139
2.6135 | 243.728 | 63.54 | 60.1632 | 32.7705
3.6135 | 244.7209 | 63.7089 | 60.3398 | 32.8268
4.6135 | 246.5754 | 63.8783 | 60.6022 | 32.8943
5.6135 | 249.145 | 64.06 | 60.7781 | 32.9485
6.6135 | 252.1823 | 64.2755 | 60.8868 | 33.0055
7.6135 | 255.6467 | 64.5176 | 61.0444 | 33.0549
8.6135 | 259.3749 | 64.7223 | 61.2333 | 33.1332
9.6135 | 263.4694 | 64.9575 | 61.3945 | 33.1915
10.6135 | 267.804 | 65.1751 | 61.6568 | 33.2399
11.6135 | 272.2448 | 65.4346 | 62.0719 | 33.2964
12.6135 | 276.9213 | 65.7018 | 62.3125 | 33.3525
13.6135 | 281.6025 | 65.9564 | 62.4528 | 33.4174
14.6135 | 286.3652 | 66.2479 | 62.6748 | 33.4733
15.6135 | 291.2027 | 66.5889 | 62.9032 | 33.5263
16.6135 | 296.1773 | 66.9145 | 63.147 | 33.5892
17.6135 | 301.1382 | 67.2726 | 63.449 | 33.6573
18.6135 | 306.1977 | 67.6196 | 63.8003 | 33.7126
19.6135 | 311.2164 | 67.9421 | 64.037 | 33.7731
20.6135 | 316.2996 | 68.3406 | 64.3278 | 33.8346
21.6135 | 321.2295 | 68.7393 | 64.7184 | 33.8926
22.6135 | 326.436 | 69.1362 | 65.1495 | 33.9578
23.6135 | 331.6483 | 69.5332 | 65.593 | 34.016
24.6135 | 336.7887 | 70.0259 | 65.9853 | 34.0746
25.6135 | 341.8622 | 70.4762 | 66.2931 | 34.1421
26.6135 | 347.0085 | 70.8597 | 66.7051 | 34.2126
27.6135 | 352.2201 | 71.313 | 67.2577 | 34.2641
28.6135 | 357.3841 | 71.8576 | 67.7111 | 34.3329
29.6135 | 362.5691 | 72.4325 | 68.2073 | 34.4011
30.6135 | 367.5946 | 72.9454 | 68.7017 | 34.4611
31.6135 | 372.6551 | 73.5406 | 69.1926 | 34.528
32.6135 | 377.7106 | 74.152 | 69.6031 | 34.5886
33.6135 | 382.6869 | 74.7068 | 70.1781 | 34.6603
34.6135 | 387.6375 | 75.2945 | 70.623 | 34.7337
35.6135 | 392.6839 | 75.9766 | 70.9637 | 34.8033
36.6135 | 397.5625 | 76.5894 | 71.4795 | 34.8739
37.6135 | 402.5849 | 77.1951 | 72.1154 | 34.9433
38.6135 | 407.58 | 77.8809 | 72.8077 | 35.0236
39.6135 | 412.5346 | 78.5841 | 73.3865 | 35.1046
40.6135 | 417.5467 | 79.2256 | 73.9046 | 35.176
41.6135 | 422.2324 | 79.9211 | 74.6347 | 35.2532
42.6135 | 426.3508 | 80.6388 | 75.1446 | 35.3358
43.6135 | 430.0888 | 81.4409 | 75.7825 | 35.418
44.6135 | 433.6481 | 82.1318 | 76.3283 | 35.4949
45.7229 | 437.2043 | 82.9204 | 76.9297 | 35.5858
46.6135 | 439.888 | 83.585 | 77.5634 | 35.6613
47.6135 | 442.8938 | 84.3431 | 78.1978 | 35.7481
48.6135 | 445.7876 | 85.1144 | 78.911 | 35.8368
49.6135 | 448.6452 | 85.8301 | 79.6185 | 35.9271
50.6135 | 451.3932 | 86.6835 | 80.1848 | 36.018
51.6135 | 453.9656 | 87.421 | 80.8856 | 36.107
52.6135 | 456.2658 | 88.2665 | 81.4207 | 36.2053
53.6135 | 458.2684 | 89.0124 | 82.1184 | 36.3026
54.6135 | 460.0264 | 89.8474 | 82.6955 | 36.4039
55.6135 | 461.5043 | 90.6251 | 83.4136 | 36.4968
56.6135 | 462.7377 | 91.372 | 84.2093 | 36.6062
57.6135 | 463.9199 | 92.1202 | 84.9102 | 36.7123
58.6135 | 464.7996 | 92.9198 | 85.5686 | 36.8184
59.6135 | 465.4535 | 93.8472 | 86.255 | 36.928
60.6135 | 465.9761 | 94.9091 | 86.9374 | 37.0394
61.6135 | 466.3664 | 95.7938 | 87.7582 | 37.1591
62.6135 | 466.63 | 96.5558 | 88.377 | 37.2784
63.6135 | 466.7186 | 97.2155 | 88.8896 | 37.4075
64.6135 | 466.8335 | 97.7823 | 89.6093 | 37.5292
65.6135 | 466.8301 | 98.7438 | 90.3095 | 37.6442
66.6135 | 466.762 | 99.488 | 90.9908 | 37.7583
67.6135 | 466.7475 | 100.2202 | 91.4957 | 37.8718
68.6135 | 466.7183 | 101.3347 | 92.0568 | 37.9927
69.6135 | 466.562 | 101.9817 | 92.7589 | 38.1145
70.6135 | 466.4072 | 102.7241 | 93.403 | 38.243
71.6135 | 466.2336 | 103.3312 | 94.0643 | 38.38
72.6135 | 465.9621 | 103.9273 | 94.6609 | 38.5161
73.6135 | 465.8411 | 104.5953 | 95.231 | 38.6467
74.6135 | 465.7554 | 105.4576 | 95.9307 | 38.7825
75.6135 | 465.5498 | 106.1608 | 96.6167 | 38.9116
76.6135 | 465.4985 | 106.9627 | 97.3781 | 39.0466
77.6135 | 465.4479 | 107.6558 | 97.9329 | 39.1892
78.6135 | 465.4406 | 108.1794 | 98.5799 | 39.3311
79.6135 | 465.5406 | 108.8857 | 99.1705 | 39.4836
80.6135 | 465.673 | 109.6165 | 99.7651 | 39.6367
81.6135 | 465.6466 | 110.3419 | 100.458 | 39.7894
82.6135 | 465.7955 | 111.1853 | 101.1602 | 39.9493
83.6135 | 465.9856 | 111.8273 | 101.8758 | 40.1036
84.6135 | 465.993 | 112.5395 | 102.4794 | 40.2582
85.6135 | 465.8872 | 113.2302 | 103.0902 | 40.4227
86.6135 | 465.8411 | 113.9232 | 103.6791 | 40.5817
87.6135 | 466.0042 | 114.5796 | 104.4162 | 40.7391
88.6135 | 466.289 | 115.2861 | 105.073 | 40.9091
89.6135 | 466.4929 | 115.9613 | 105.6726 | 41.0802
90.6135 | 466.7229 | 116.6647 | 106.3234 | 41.2473
91.6135 | 466.753 | 117.3832 | 106.9056 | 41.4102
92.6135 | 466.8826 | 118.1766 | 107.4993 | 41.5893
93.6135 | 467.1049 | 118.9307 | 108.0928 | 41.7553
94.6135 | 467.2365 | 119.5571 | 108.7704 | 41.9259
95.6135 | 467.294 | 120.1919 | 109.4913 | 42.0667
96.6135 | 467.4088 | 120.9183 | 110.1847 | 42.204
97.6135 | 467.595 | 121.741 | 110.8008 | 42.3059
98.6135 | 467.5481 | 122.3588 | 111.4459 | 42.2873
99.6135 | 467.6668 | 123.0659 | 112.081 | 42.4676
100.6135 | 467.6327 | 123.662 | 112.767 | 42.647
101.6135 | 467.6629 | 124.3546 | 113.3706 | 42.8285
102.6135 | 467.8525 | 124.9933 | 114.0592 | 43.0213
103.6135 | 467.9454 | 125.8023 | 114.7395 | 43.1696
104.6135 | 468.0522 | 126.4825 | 115.4247 | 43.3365
105.6135 | 468.0453 | 127.22 | 115.984 | 43.517
106.6135 | 468.0958 | 127.9103 | 116.6028 | 43.6847
107.6135 | 468.252 | 128.6134 | 117.3769 | 43.8593
108.6135 | 468.1962 | 129.3351 | 117.9637 | 44.0396
109.6135 | 468.1655 | 130.0327 | 118.5788 | 44.2059
110.6135 | 468.0538 | 130.6105 | 119.1712 | 44.3781
111.6135 | 468.0417 | 131.3349 | 119.772 | 44.557
112.6135 | 467.9762 | 131.9934 | 120.4557 | 44.7374
113.6135 | 467.8411 | 132.7936 | 121.157 | 44.9157
114.6135 | 467.8602 | 133.462 | 121.838 | 45.1128
115.6135 | 467.8297 | 134.097 | 122.4113 | 45.3019
116.6135 | 467.8468 | 134.6981 | 122.9776 | 45.5103
117.6135 | 467.7306 | 135.3572 | 123.6637 | 45.713
118.6135 | 467.7047 | 135.9646 | 124.3348 | 45.9116
119.6135 | 467.763 | 136.6701 | 124.8564 | 46.1135
120.6135 | 467.8105 | 137.3182 | 125.4472 | 46.3118
121.6135 | 467.8777 | 138.0675 | 126.0936 | 46.5251
122.6135 | 467.8582 | 138.6982 | 126.8865 | 46.7306
123.6135 | 467.8865 | 139.2899 | 127.5126 | 46.9459
124.6135 | 467.9548 | 139.9505 | 128.1497 | 47.1702
125.6135 | 468.0776 | 140.6629 | 128.7268 | 47.3568
126.6135 | 468.0817 | 141.3163 | 129.3036 | 47.5674
127.6135 | 468.1909 | 141.9162 | 129.9612 | 47.7755
128.6135 | 468.3541 | 142.5214 | 130.5613 | 47.997
129.6135 | 468.4637 | 143.2286 | 131.1552 | 48.2144
130.6135 | 468.4741 | 144.0295 | 131.7831 | 48.4327
131.6135 | 468.364 | 144.6814 | 132.3545 | 48.6416
132.6135 | 468.4192 | 145.2845 | 133.0144 | 48.8553
133.6135 | 468.3259 | 145.8891 | 133.6504 | 49.0545
134.6135 | 468.3332 | 146.5397 | 134.374 | 49.2559
135.6135 | 468.366 | 147.1469 | 134.9183 | 49.4664
136.6135 | 468.2485 | 147.8071 | 135.5692 | 49.6665
137.6135 | 468.1996 | 148.3897 | 136.1939 | 49.8751
138.6135 | 468.1609 | 149.0103 | 136.7504 | 50.1044
139.6135 | 468.1287 | 149.6442 | 137.3426 | 50.3314
140.6135 | 468.0748 | 150.2538 | 137.9513 | 50.5725
141.6135 | 468.0797 | 150.9215 | 138.5712 | 50.811
142.6135 | 468.1294 | 151.5123 | 139.1591 | 51.0502
143.6135 | 468.0887 | 152.1532 | 139.744 | 51.286
144.6135 | 468.1154 | 152.7909 | 140.3839 | 51.5313
145.6135 | 468.0512 | 153.4555 | 141.0062 | 51.7795
146.6135 | 468.1123 | 154.2341 | 141.5767 | 52.0297
147.6135 | 468.2136 | 154.8214 | 142.1881 | 52.2765
148.6135 | 468.3616 | 155.5115 | 142.8037 | 52.5256
149.6135 | 468.4484 | 156.0906 | 143.4004 | 52.7892
150.6135 | 468.4361 | 156.7133 | 143.9618 | 53.0269
151.6135 | 468.441 | 157.3363 | 144.5618 | 53.3063
152.6135 | 468.472 | 157.947 | 145.2134 | 53.5649
153.6135 | 468.4955 | 158.5396 | 145.8932 | 53.8274
154.6135 | 468.5485 | 159.2116 | 146.4976 | 54.0879
155.6135 | 468.7351 | 159.8106 | 147.1208 | 54.3473
156.6135 | 468.8128 | 160.417 | 147.6957 | 54.6097
157.6135 | 468.7865 | 161.0182 | 148.2717 | 54.8813
158.6135 | 468.8626 | 161.6591 | 148.8387 | 55.1522
159.6135 | 468.9793 | 162.2733 | 149.4698 | 55.4271
160.6135 | 468.9555 | 162.8236 | 150.0505 | 55.7063
161.6135 | 468.9584 | 163.4409 | 150.6594 | 55.9703
162.6135 | 469.0099 | 164.0058 | 151.2685 | 56.2402
163.6135 | 468.9673 | 164.6348 | 151.9762 | 56.5194
164.6135 | 469.02 | 165.2085 | 152.5315 | 56.7899
165.6135 | 468.9472 | 165.836 | 153.1037 | 57.0606
166.6135 | 468.9695 | 166.4195 | 153.6734 | 57.3361
167.6135 | 468.939 | 166.953 | 154.2798 | 57.6068
168.6135 | 468.7727 | 167.5813 | 154.8238 | 57.8823
169.6135 | 468.6665 | 168.2259 | 155.4416 | 58.1504
170.6135 | 468.8307 | 168.8309 | 156.0372 | 58.4303
171.6135 | 468.8771 | 169.3876 | 156.6017 | 58.7064
172.6135 | 468.7694 | 169.9831 | 157.1498 | 59.0144
173.6135 | 468.837 | 170.5879 | 157.71 | 59.3243
174.6135 | 468.918 | 171.1456 | 158.324 | 59.8286
175.6135 | 469.0561 | 171.6688 | 158.9426 | 60.2224
176.6135 | 469.0472 | 172.3206 | 159.53 | 60.5341
177.6135 | 469.1226 | 172.8903 | 160.0662 | 60.8918
178.6135 | 469.0809 | 173.5115 | 160.6464 | 61.2149
179.6135 | 469.0333 | 174.1223 | 161.1882 | 61.5072
180.6135 | 469.0353 | 174.7437 | 161.7495 | 61.8157
181.6135 | 468.9158 | 175.2388 | 162.3304 | 62.1143
182.6135 | 468.8645 | 175.7922 | 162.9186 | 62.423
183.6135 | 468.6895 | 176.3405 | 163.556 | 62.7114
184.6135 | 468.4795 | 176.9102 | 164.1351 | 63.0168
185.6135 | 468.4692 | 177.4841 | 164.7235 | 63.3189
186.6135 | 468.615 | 178.0433 | 165.2508 | 63.6246
187.6135 | 468.7178 | 178.6096 | 165.8148 | 63.9262
188.6135 | 468.7352 | 179.2123 | 166.3206 | 64.2344
189.6135 | 468.7923 | 179.7332 | 166.8343 | 64.5406
190.6135 | 468.7627 | 180.3085 | 167.3776 | 64.8419
191.6135 | 468.8359 | 180.8641 | 167.9632 | 65.1735
192.6135 | 468.7624 | 181.4363 | 168.5044 | 65.4761
193.6135 | 468.6634 | 181.9708 | 169.0729 | 65.8003
194.6135 | 468.6852 | 182.5673 | 169.6052 | 66.1048
195.6135 | 468.6723 | 183.1058 | 170.1741 | 66.4107
196.6135 | 468.5369 | 183.642 | 170.7962 | 66.7207
197.6135 | 468.5562 | 184.183 | 171.3636 | 67.0217
198.6135 | 468.636 | 184.7357 | 171.8966 | 67.3285
199.6135 | 468.6624 | 185.3145 | 172.4535 | 67.6342
200.6135 | 468.6718 | 185.873 | 172.9438 | 67.983
201.6135 | 468.7517 | 186.41 | 173.5736 | 68.3045
202.6135 | 468.6884 | 186.9464 | 174.087 | 68.6176
203.6135 | 468.5554 | 187.4673 | 174.5871 | 68.9348
204.6135 | 468.5894 | 188.0471 | 175.0574 | 69.2522
205.6135 | 468.6062 | 188.5637 | 175.5892 | 69.5662
206.6135 | 468.524 | 189.1594 | 176.1238 | 69.8548
207.6135 | 468.4984 | 189.6773 | 176.6766 | 70.1691
208.6135 | 468.5364 | 190.1963 | 177.2644 | 70.4824
209.6135 | 468.5828 | 190.7205 | 177.8088 | 70.7792
210.6135 | 468.5125 | 191.256 | 178.3079 | 71.0874
211.6135 | 468.451 | 191.797 | 178.7947 | 71.4047
212.6135 | 468.3851 | 192.351 | 179.2625 | 71.7156
213.6135 | 468.2402 | 192.917 | 179.8119 | 72.056
214.6135 | 468.193 | 193.4756 | 180.3289 | 72.3742
215.6135 | 467.9871 | 193.985 | 180.8725 | 72.7055
216.6135 | 467.7717 | 194.5055 | 181.424 | 73.038
217.6135 | 467.7493 | 195.0463 | 181.9612 | 73.3414
218.6135 | 467.6466 | 195.5277 | 182.4282 | 73.6443
219.6135 | 467.5481 | 196.0799 | 182.987 | 73.9574
220.6135 | 467.5143 | 196.6243 | 183.5764 | 74.2753
221.6135 | 467.5642 | 197.1633 | 184.1251 | 74.5986
222.6135 | 467.4914 | 197.6462 | 184.685 | 74.9028
223.6135 | 467.6582 | 198.2005 | 185.1541 | 75.2453
224.6135 | 467.7516 | 198.7112 | 185.5913 | 75.5378
225.6135 | 467.6912 | 199.214 | 186.1428 | 75.8409
226.6135 | 467.7234 | 199.7536 | 186.6002 | 76.1503
227.6135 | 467.7338 | 200.2765 | 187.1234 | 76.4462
228.6135 | 467.6134 | 200.7914 | 187.5838 | 76.8181
229.6135 | 467.6717 | 201.2966 | 188.1092 | 77.1263
230.6135 | 467.6352 | 201.8127 | 188.6437 | 77.4374
231.6135 | 467.7411 | 202.34 | 189.1618 | 77.7412
232.6135 | 467.8181 | 202.8502 | 189.5985 | 78.0822
233.6135 | 467.8392 | 203.3521 | 190.1175 | 78.3547
234.6135 | 467.9114 | 203.8657 | 190.6278 | 78.6743
235.6135 | 467.9988 | 204.3652 | 191.085 | 78.9813
236.6135 | 467.9655 | 204.8081 | 191.6132 | 79.2718
237.6135 | 467.9832 | 205.372 | 192.1295 | 79.5398
238.6135 | 467.8845 | 205.871 | 192.659 | 79.7559
239.6135 | 467.8291 | 206.4115 | 193.1538 | 80.2624
240.6135 | 467.8297 | 206.8745 | 193.6385 | 80.5855
241.6135 | 467.9041 | 207.3848 | 194.1075 | 80.8657
242.6135 | 467.8741 | 207.8878 | 194.6204 | 81.1735
243.6135 | 467.7896 | 208.4475 | 195.079 | 81.5004
244.6135 | 467.7994 | 208.9353 | 195.5171 | 81.8236
245.6135 | 467.8652 | 209.4243 | 196.0264 | 82.0883
246.6135 | 467.7834 | 209.9543 | 196.5339 | 82.4145
247.6135 | 467.8007 | 210.4253 | 197.0435 | 82.5585
248.6135 | 467.8549 | 210.9444 | 197.491 | 82.8913
249.6135 | 467.983 | 211.4498 | 197.9863 | 83.1992
250.6135 | 467.9684 | 211.9614 | 198.407 | 83.5634
251.6135 | 468.0181 | 212.4546 | 198.94 | 84.0141
252.6135 | 468.1481 | 212.9607 | 199.4401 | 84.8038
253.6135 | 468.1681 | 213.4692 | 199.9411 | 85.2386
254.6135 | 468.2394 | 213.9733 | 200.352 | 85.5833
255.6135 | 468.3768 | 214.4513 | 200.887 | 85.8878
256.6135 | 468.4724 | 214.9435 | 201.4027 | 86.1705
257.6135 | 468.4802 | 215.4316 | 201.8215 | 86.4668
258.6135 | 468.5531 | 215.9219 | 202.2829 | 86.7885
259.6135 | 468.5755 | 216.4333 | 202.8101 | 87.1031
260.6135 | 468.5821 | 216.9234 | 203.2584 | 87.2051
261.6135 | 468.5148 | 217.4426 | 203.8023 | 87.5357
262.6135 | 468.5617 | 217.9416 | 204.293 | 87.8058
263.6135 | 468.4269 | 218.4297 | 204.749 | 88.0794
264.6135 | 468.3705 | 218.9109 | 205.2834 | 88.377
265.6135 | 468.2968 | 219.4156 | 205.7568 | 88.7154
266.6135 | 468.3749 | 219.9481 | 206.2208 | 88.8341
267.6135 | 468.4184 | 220.4443 | 206.7144 | 89.1555
268.6135 | 468.4227 | 220.8847 | 207.2067 | 89.4896
269.6135 | 468.1667 | 221.3741 | 207.7166 | 89.7878
270.6135 | 468.0819 | 221.8512 | 208.1726 | 90.1518
271.6135 | 467.9792 | 222.3464 | 208.6334 | 90.4013
272.6135 | 467.8734 | 222.83 | 209.0396 | 90.6307
273.6135 | 467.7459 | 223.3429 | 209.5463 | 90.897
274.6135 | 467.6583 | 223.8271 | 210.0306 | 91.1521
275.6135 | 467.444 | 224.294 | 210.4059 | 91.3602
276.6135 | 467.2392 | 224.7642 | 210.8824 | 91.4172
277.6135 | 467.2596 | 225.2095 | 211.2766 | 91.7057
278.6135 | 467.3059 | 225.6782 | 211.6873 | 91.9197
279.6135 | 467.2446 | 226.1414 | 212.1452 | 92.1406
280.6135 | 467.0345 | 226.6303 | 212.5358 | 92.4682
281.6135 | 466.9896 | 227.1106 | 212.8976 | 92.6337
282.6135 | 467.0533 | 227.5954 | 213.2988 | 92.9507
283.6135 | 466.9926 | 228.0653 | 213.8052 | 92.8022
284.6135 | 466.8962 | 228.5433 | 214.2127 | 92.6698
285.6135 | 466.9075 | 229.0291 | 214.7159 | 92.902
286.6135 | 467.0232 | 229.4892 | 215.1641 | 93.1579
287.6135 | 467.1139 | 229.9599 | 215.6896 | 93.5442
288.6135 | 467.3119 | 230.4124 | 216.2138 | 94.134
289.6135 | 467.335 | 230.8732 | 216.7104 | 94.4537
290.6135 | 467.4229 | 231.3608 | 217.142 | 94.8951
291.6135 | 467.4505 | 231.8455 | 217.6643 | 95.2337
292.6135 | 467.483 | 232.3224 | 218.1609 | 95.4759
293.6135 | 467.6283 | 232.8036 | 218.6472 | 95.7667
294.6135 | 467.9655 | 233.2506 | 219.136 | 96.1331
295.6135 | 468.0481 | 233.7456 | 219.5999 | 96.3783
296.6135 | 468.1423 | 234.2012 | 220.0538 | 96.3952
297.6135 | 468.1287 | 234.6437 | 220.5152 | 96.5295
298.6135 | 468.1463 | 235.124 | 220.9645 | 96.7603
299.6135 | 468.2694 | 235.5858 | 221.3766 | 96.9572
300.6135 | 468.2575 | 236.0644 | 221.7239 | 97.246
301.6135 | 468.3145 | 236.5345 | 222.1489 | 97.4646
302.6135 | 468.2285 | 236.9766 | 222.6226 | 97.7387
303.6135 | 468.192 | 237.4437 | 223.0825 | 97.9405
304.6135 | 468.1965 | 237.8965 | 223.5117 | 98.217
305.6135 | 468.188 | 238.3402 | 223.9076 | 98.3722
306.6135 | 468.2208 | 238.8175 | 224.3016 | 98.6178
307.6135 | 468.2703 | 239.2887 | 224.7931 | 98.4466
308.6135 | 468.1614 | 239.7583 | 225.1941 | 98.5084
309.6135 | 468.1654 | 240.2277 | 225.6624 | 98.848
310.6135 | 468.1285 | 240.6844 | 226.036 | 99.2804
311.6135 | 468.1337 | 241.1532 | 226.4569 | 98.9541
312.6135 | 468.1461 | 241.6013 | 226.8209 | 99.275
313.6135 | 468.0533 | 242.0307 | 227.3177 | 99.7991
314.6135 | 467.9989 | 242.4655 | 227.6365 | 100.1008
315.6135 | 467.9791 | 242.9077 | 228.0176 | 100.56
316.6135 | 468.0439 | 243.376 | 228.5086 | 100.9952
317.6135 | 468.0737 | 243.8909 | 228.9745 | 101.413
318.6135 | 468.1397 | 244.3335 | 229.4368 | 101.7608
319.6135 | 468.0755 | 244.7644 | 229.8538 | 101.2838
320.6135 | 468.0803 | 245.2008 | 230.3173 | 101.7069
321.6135 | 468.0189 | 245.6581 | 230.6869 | 101.9803
322.6135 | 467.9255 | 246.0965 | 231.1171 | 102.2372
323.6135 | 467.7179 | 246.5133 | 231.506 | 103.9137
324.6135 | 467.7703 | 246.945 | 231.873 | 103.5108
325.6135 | 467.7853 | 247.3813 | 232.2587 | 104.1437
326.6135 | 467.7213 | 247.7939 | 232.7447 | 105.2678
327.6135 | 467.7863 | 248.2539 | 233.2195 | 105.4414
328.6135 | 467.6697 | 248.7054 | 233.6478 | 105.7566
329.6135 | 467.4616 | 249.1422 | 234.0713 | 105.8943
330.6135 | 467.2307 | 249.5884 | 234.5366 | 105.745
331.6135 | 467.1423 | 250.0323 | 234.9784 | 106.5731
332.6135 | 467.0766 | 250.4514 | 235.3181 | 107.3691
333.6135 | 466.9928 | 250.8837 | 235.6177 | 107.5872
334.6135 | 466.963 | 251.3081 | 236.0361 | 107.0877
335.6135 | 466.9003 | 251.7119 | 236.5362 | 106.8996
336.6135 | 466.7472 | 252.1222 | 236.8862 | 107.351
337.6135 | 466.7269 | 252.5761 | 237.1916 | 108.4029
338.6135 | 466.74 | 253.0254 | 237.6625 | 110.0848
339.6135 | 466.9478 | 253.4431 | 238.0657 | 110.6383
340.6135 | 467.0792 | 253.8514 | 238.4299 | 111.1421
341.6135 | 467.1443 | 254.2741 | 238.8367 | 111.3977
342.6135 | 467.2172 | 254.7134 | 239.226 | 111.8126
343.6135 | 467.1876 | 255.1056 | 239.5685 | 112.5878
344.6135 | 467.1635 | 255.5436 | 239.8205 | 113.0302
345.6135 | 467.1517 | 255.9504 | 240.2081 | 113.4057
346.6135 | 467.3108 | 256.4149 | 240.5922 | 113.7707
347.6135 | 467.4562 | 256.845 | 241.0924 | 114.0698
348.6135 | 467.5629 | 257.2867 | 241.3009 | 114.4514
349.6135 | 467.5566 | 257.7265 | 241.7572 | 114.8872
350.6135 | 467.5798 | 258.1413 | 242.2964 | 115.0211
351.6135 | 467.6087 | 258.5346 | 242.7495 | 115.3257
352.6135 | 467.6637 | 258.9726 | 243.0176 | 115.68
353.6135 | 467.6312 | 259.3867 | 243.3078 | 116.0988
354.6135 | 467.659 | 259.7875 | 243.8095 | 116.4548
355.6135 | 467.5804 | 260.2257 | 244.3201 | 116.8496
356.6135 | 467.5922 | 260.6554 | 244.7565 | 117.1843
357.6135 | 467.5144 | 261.0717 | 245.2115 | 117.6033
358.6135 | 467.5078 | 261.4708 | 245.6597 | 118.1493
359.6135 | 467.5659 | 261.8761 | 246.0515 | 118.2966
360.6135 | 467.4831 | 262.2768 | 246.4499 | 118.6913
361.6135 | 467.4972 | 262.6958 | 246.8417 | 119.1164
362.6135 | 467.4037 | 263.0938 | 247.2392 | 119.5079
363.6135 | 467.4631 | 263.5191 | 247.6444 | 119.8688
364.6135 | 467.3209 | 263.9368 | 247.9683 | 120.1476
365.6135 | 467.2238 | 264.3548 | 248.2899 | 120.239
366.6135 | 467.265 | 264.7778 | 248.6507 | 120.7021
367.6135 | 467.1185 | 265.1809 | 248.9213 | 120.9099
368.6135 | 466.9045 | 265.5529 | 249.3612 | 121.3149
369.6135 | 466.8052 | 265.9265 | 249.6767 | 121.7176
370.6135 | 466.7445 | 266.3267 | 250.0525 | 122.0692
371.6135 | 466.6738 | 266.7291 | 250.4817 | 122.2625
372.6135 | 466.6916 | 267.149 | 250.8953 | 122.6758
373.6135 | 466.5309 | 267.5787 | 251.2717 | 122.8971
374.6135 | 466.5434 | 267.9803 | 251.6368 | 123.2115
375.6135 | 466.4671 | 268.3942 | 251.9037 | 123.4831
376.6135 | 466.3752 | 268.7638 | 252.3361 | 123.7959
377.6135 | 466.4121 | 269.1533 | 252.7853 | 124.0606
378.6135 | 466.3271 | 269.5336 | 253.192 | 124.1171
379.6135 | 466.3344 | 269.9468 | 253.4498 | 124.3904
380.6135 | 466.2447 | 270.3506 | 253.8603 | 124.3834
381.6135 | 466.1519 | 270.7349 | 254.0681 | 123.2754
382.6135 | 466.1037 | 271.1425 | 254.4236 | 124.0848
383.6135 | 466.1819 | 271.543 | 254.7678 | 124.433
384.6135 | 466.3279 | 271.9442 | 255.0965 | 124.742
385.6135 | 466.339 | 272.2944 | 255.3617 | 125.0283
386.6135 | 466.3049 | 272.6931 | 255.7814 | 125.2719
387.6135 | 466.3983 | 273.0648 | 256.2152 | 126.4899
388.6135 | 466.5257 | 273.4598 | 256.318 | 126.7183
389.6135 | 466.6741 | 273.8509 | 256.655 | 126.8861
390.6135 | 466.8317 | 274.2328 | 257.0425 | 127.1429
391.6135 | 466.9187 | 274.6421 | 257.2558 | 127.5308
392.6135 | 467.0114 | 275.065 | 257.7735 | 127.7602
393.6135 | 467.0752 | 275.4742 | 258.3164 | 128.0129
394.6135 | 467.2654 | 275.8221 | 258.7446 | 128.241
395.6135 | 467.3287 | 276.24 | 259.0476 | 128.6252
396.6135 | 467.4364 | 276.5946 | 259.377 | 128.9067
397.6135 | 467.6579 | 277.0065 | 259.8417 | 129.2913
398.6135 | 467.8236 | 277.4289 | 260.2063 | 129.6201
399.6135 | 467.88 | 277.8052 | 260.5289 | 129.8809
400.6135 | 468.0605 | 278.2195 | 260.9266 | 130.1684
401.6135 | 467.9811 | 278.5889 | 261.3564 | 130.4183
402.6135 | 467.8606 | 278.9828 | 261.711 | 130.6584
403.6135 | 467.9048 | 279.3836 | 262.1633 | 131.1326
404.6135 | 467.9972 | 279.7918 | 262.4926 | 131.3936
405.6135 | 467.9567 | 280.1853 | 262.8733 | 131.6879
406.6135 | 468.0119 | 280.5435 | 263.2543 | 132.0232
407.6135 | 467.9901 | 280.9453 | 263.6202 | 132.3276
408.6135 | 468.0322 | 281.3172 | 263.9314 | 132.5973
409.6135 | 468.1074 | 281.697 | 264.3457 | 132.9166
410.6135 | 468.0761 | 282.0781 | 264.7477 | 133.3047
411.6135 | 468.0529 | 282.4548 | 265.1186 | 133.6378
412.6135 | 468.0075 | 282.8468 | 265.4447 | 133.9401
413.6135 | 467.8984 | 283.2202 | 265.6113 | 134.2211
414.6135 | 467.8595 | 283.5841 | 265.786 | 134.4955
415.6135 | 467.9737 | 283.9684 | 266.1272 | 134.7912
416.6135 | 468.0279 | 284.3329 | 266.5546 | 135.1514
417.6135 | 468.1846 | 284.7338 | 266.9573 | 135.6461
418.6135 | 468.2863 | 285.0527 | 267.166 | 135.9065
419.6135 | 468.3776 | 285.4486 | 267.5452 | 136.1961
420.6135 | 468.3046 | 285.8013 | 267.9568 | 136.4388
421.6135 | 468.3478 | 286.2025 | 268.311 | 136.6504
422.6135 | 468.3406 | 286.609 | 268.7523 | 137.0545
423.6135 | 468.2577 | 286.9791 | 268.9963 | 137.2146
424.6135 | 468.2861 | 287.3211 | 269.2038 | 137.4634
425.6135 | 468.1309 | 287.7089 | 269.6963 | 137.6389
426.6135 | 467.9104 | 288.1205 | 270.1152 | 137.9442
427.6135 | 467.8525 | 288.5057 | 270.3696 | 138.4188
428.6135 | 467.8708 | 288.8441 | 270.7764 | 138.6056
429.6135 | 467.9256 | 289.2052 | 271.1743 | 138.7982
430.6135 | 467.856 | 289.5654 | 271.4703 | 138.8937
431.6135 | 467.762 | 289.9209 | 271.7404 | 139.2214
432.6135 | 467.8002 | 290.3108 | 271.9651 | 139.4878
433.6135 | 467.848 | 290.687 | 272.2858 | 139.6706
434.6135 | 467.8289 | 290.979 | 272.5292 | 140.083
435.6135 | 467.8136 | 291.3002 | 272.6413 | 140.3097
436.6135 | 467.8218 | 291.6211 | 272.9513 | 140.6117
437.6135 | 467.7125 | 292.0343 | 273.5274 | 140.8912
438.6135 | 467.7501 | 292.3911 | 273.9513 | 141.0071
439.6135 | 467.7954 | 292.7898 | 274.1429 | 141.106
440.6135 | 467.755 | 293.1784 | 274.4829 | 141.5304
441.6135 | 467.5322 | 293.497 | 274.8928 | 141.6517
442.6135 | 467.4778 | 293.853 | 275.2562 | 141.81
443.6135 | 467.4894 | 294.2478 | 275.4403 | 142.1091
444.6135 | 467.3868 | 294.5861 | 275.7772 | 142.3959
445.6135 | 467.3125 | 294.9549 | 275.9915 | 142.3123
446.6135 | 467.3958 | 295.3604 | 276.4451 | 142.5789
447.6135 | 467.2631 | 295.7522 | 276.9152 | 142.8689
448.6135 | 467.1552 | 296.1074 | 277.1469 | 143.0607
449.6135 | 467.1704 | 296.442 | 277.5845 | 143.0718
450.6135 | 467.0808 | 296.7919 | 277.9721 | 142.8629
451.6135 | 467.2074 | 297.163 | 278.3348 | 142.9814
452.6135 | 467.3232 | 297.5063 | 278.7296 | 143.108
453.6135 | 467.2595 | 297.8719 | 279.0911 | 143.2458
454.6135 | 467.1888 | 298.2304 | 279.4101 | 143.3007
455.6135 | 467.1348 | 298.5578 | 279.6844 | 143.513
456.6135 | 467.0892 | 298.8861 | 280.0728 | 143.7061
457.6135 | 467.1527 | 299.2672 | 280.3932 | 143.869
458.6135 | 467.1589 | 299.594 | 280.7434 | 144.0713
459.6135 | 467.0623 | 299.9651 | 281.0601 | 144.1815
460.6135 | 466.9574 | 300.3272 | 281.4093 | 144.1092
461.6135 | 466.766 | 300.6308 | 281.7244 | 143.9831
462.6135 | 466.6184 | 300.9329 | 282.0451 | 144.4379
463.6135 | 466.5002 | 301.299 | 282.014 | 144.6565
464.6135 | 466.4935 | 301.6659 | 282.4417 | 144.8398
465.6135 | 466.5012 | 302.0401 | 282.8966 | 144.7604
466.6135 | 466.4938 | 302.387 | 283.2687 | 144.802
467.6135 | 466.4442 | 302.7375 | 283.5722 | 145.1055
468.6135 | 466.253 | 303.0652 | 283.8611 | 145.2769
469.6135 | 466.1176 | 303.3834 | 284.0923 | 145.3838
470.6135 | 465.9508 | 303.7519 | 284.4429 | 145.8035
471.6135 | 465.9163 | 304.0885 | 284.5954 | 145.8023
472.6135 | 465.9692 | 304.4381 | 284.9492 | 145.9636
473.6135 | 465.9464 | 304.7758 | 285.2992 | 146.1277
474.6135 | 465.9148 | 305.152 | 285.6697 | 146.292
475.6135 | 465.7589 | 305.488 | 285.9111 | 146.319
476.6135 | 465.7954 | 305.8147 | 286.2481 | 146.5119
477.6135 | 465.8319 | 306.1303 | 286.6317 | 146.6573
478.6135 | 465.8265 | 306.4811 | 286.9195 | 146.9037
479.6135 | 465.7429 | 306.7789 | 287.2236 | 147.1575
480.6135 | 465.6876 | 307.1067 | 287.5262 | 147.5316
481.6135 | 465.6051 | 307.4033 | 287.863 | 147.6665
482.6135 | 465.7072 | 307.7097 | 288.1454 | 147.9585
483.6135 | 465.9016 | 307.9982 | 288.4357 | 148.2807
484.6135 | 466.033 | 308.371 | 288.7903 | 148.413
485.6135 | 465.9987 | 308.7262 | 289.0987 | 148.6504
486.6135 | 465.9838 | 309.0999 | 289.3457 | 148.9206
487.6135 | 465.9474 | 309.4774 | 289.701 | 149.2854
488.6135 | 465.9501 | 309.798 | 289.9567 | 149.5221
489.6135 | 465.9623 | 310.1443 | 290.3275 | 149.8277
490.6135 | 466.0566 | 310.4007 | 290.6282 | 150.0887
491.6135 | 466.0982 | 310.7328 | 290.9179 | 150.3941
492.6135 | 466.0934 | 311.0536 | 291.1858 | 150.7035
493.6135 | 466.1835 | 311.3163 | 291.4614 | 151.2161
494.6135 | 466.2663 | 311.6711 | 291.7145 | 151.6998
495.6135 | 466.329 | 311.9997 | 291.8617 | 152.0387
496.6135 | 466.4007 | 312.2545 | 292.0971 | 152.4085
497.6135 | 466.5908 | 312.5857 | 292.1756 | 152.8171
498.6135 | 466.6793 | 312.9097 | 292.5657 | 153.2352
499.6135 | 466.6579 | 313.2681 | 292.9895 | 153.5905
500.6135 | 466.6738 | 313.5787 | 293.2251 | 154.0492
501.6135 | 466.7937 | 313.9013 | 293.5264 | 154.4773
502.6135 | 467.0028 | 314.2484 | 293.8578 | 155.0863
503.6135 | 467.0741 | 314.5523 | 294.1772 | 155.4905
504.6135 | 467.1224 | 314.8969 | 294.4782 | 155.9188
505.6135 | 467.2203 | 315.229 | 294.7041 | 156.3901
506.6135 | 467.159 | 315.5733 | 295.083 | 156.8443
507.6135 | 467.1412 | 315.9059 | 295.4525 | 157.2971
508.6135 | 467.2041 | 316.2198 | 295.6448 | 157.7436
509.6135 | 467.4603 | 316.5615 | 295.9066 | 158.1974
510.6135 | 467.4998 | 316.87 | 296.292 | 158.6457
511.6135 | 467.4208 | 317.2111 | 296.6091 | 159.1298
512.6135 | 467.3475 | 317.476 | 296.9077 | 159.6273
513.6135 | 467.302 | 317.8252 | 297.2193 | 160.2523
514.6135 | 467.3288 | 318.1441 | 297.4661 | 160.7417
515.6135 | 467.3762 | 318.4677 | 297.7068 | 161.1959
516.6135 | 467.4101 | 318.7514 | 297.8538 | 161.6948
517.6135 | 467.3417 | 319.0835 | 298.1834 | 162.1697
518.6135 | 467.3377 | 319.3855 | 298.4747 | 162.7187
519.6135 | 467.3351 | 319.6872 | 298.6292 | 163.325
520.6135 | 467.3123 | 319.9694 | 298.7781 | 163.5139
521.6135 | 467.2602 | 320.2686 | 298.8415 | 164.128
522.6135 | 467.2408 | 320.5501 | 299.2199 | 164.7342
523.6135 | 467.3327 | 320.8709 | 299.2814 | 165.1469
524.6135 | 467.3153 | 321.1679 | 299.6293 | 165.6865
525.6135 | 467.346 | 321.4327 | 300.0422 | 166.1554
526.6135 | 467.3137 | 321.7389 | 300.4069 | 166.6752
527.6135 | 467.2961 | 322.0113 | 300.7068 | 167.3282
528.6135 | 467.2389 | 322.3014 | 300.9226 | 167.7244
529.6135 | 467.1671 | 322.641 | 301.2629 | 168.1868
530.6135 | 467.2819 | 322.948 | 301.4344 | 168.7117
531.6135 | 467.3666 | 323.2599 | 301.7705 | 169.0222
532.6135 | 467.4105 | 323.5519 | 302.105 | 169.6445
533.6135 | 467.4231 | 323.8354 | 302.2907 | 170.1524
534.6135 | 467.4756 | 324.1916 | 302.6611 | 170.6389
535.6135 | 467.5083 | 324.4676 | 303.0183 | 171.1101
536.6135 | 467.4552 | 324.7532 | 303.2741 | 171.6215
537.6135 | 467.534 | 325.073 | 303.5019 | 172.1139
538.6135 | 467.4346 | 325.4032 | 303.7424 | 172.7944
539.6135 | 467.4868 | 325.6965 | 303.7494 | 173.1429
540.6135 | 467.4635 | 325.9965 | 304.0807 | 173.7055
541.6135 | 467.2726 | 326.3054 | 304.333 | 174.1731
542.6135 | 467.1869 | 326.6034 | 304.6701 | 174.825
543.6135 | 467.2248 | 326.8741 | 304.9609 | 175.3918
544.6135 | 467.2102 | 327.1865 | 305.2871 | 175.8838
545.6135 | 467.0857 | 327.4718 | 305.4004 | 176.3193
546.6135 | 467.0914 | 327.7247 | 305.5137 | 176.7667
547.6135 | 467.1752 | 328.0226 | 305.4698 | 177.23
548.6135 | 467.1517 | 328.3166 | 305.6464 | 177.7013
549.6135 | 467.1689 | 328.6305 | 306.1377 | 178.381
550.6135 | 467.1658 | 328.9566 | 306.3355 | 178.8973
551.6135 | 467.2248 | 329.2038 | 306.6692 | 179.3406
552.6135 | 467.2644 | 329.5 | 306.8379 | 179.7818
553.6135 | 467.3904 | 329.7814 | 307.0175 | 180.2599
554.6135 | 467.6413 | 330.1197 | 307.2841 | 180.7859
555.6135 | 467.6693 | 330.4051 | 307.674 | 181.1977
556.6135 | 467.7023 | 330.6638 | 307.9883 | 181.6854
557.6135 | 467.8617 | 330.9819 | 308.3771 | 182.1533
558.6135 | 468.0578 | 331.2081 | 308.6015 | 182.5649
559.6135 | 468.4465 | 331.4939 | 308.8614 | 182.9647
560.6135 | 468.6044 | 331.7732 | 309.0754 | 183.4776
561.6135 | 468.5961 | 332.1114 | 309.3678 | 183.7971
562.6135 | 468.6738 | 332.4399 | 309.5855 | 184.317
563.6135 | 468.6849 | 332.7152 | 309.9288 | 184.7735
564.6135 | 468.8665 | 332.9551 | 310.0662 | 185.3147
565.6135 | 468.8239 | 333.2901 | 310.4432 | 185.6791
566.6135 | 468.9421 | 333.6142 | 310.7834 | 186.0934
567.6135 | 468.8919 | 333.8374 | 311.0499 | 186.5652
568.6135 | 468.7658 | 334.1218 | 311.2493 | 187.0652
569.6135 | 468.7529 | 334.4262 | 311.5822 | 187.4657
570.6135 | 468.8112 | 334.7187 | 311.8483 | 187.8868
571.6135 | 468.7395 | 335.01 | 312.1482 | 188.3453
572.6135 | 468.6139 | 335.2786 | 312.2333 | 188.8459
573.6135 | 468.5911 | 335.5688 | 312.1338 | 189.3633
574.6135 | 468.5406 | 335.8375 | 312.607 | 189.9641
575.6135 | 468.4051 | 336.1409 | 312.8754 | 190.4106
576.6135 | 468.3463 | 336.4205 | 313.2102 | 190.9591
577.6135 | 468.0919 | 336.6506 | 313.578 | 191.5209
578.6135 | 467.8557 | 336.8198 | 313.8636 | 192.0006
579.6135 | 467.6108 | 337.1081 | 314.0969 | 192.4144
580.6135 | 467.4632 | 337.4239 | 314.2913 | 192.9296
581.6135 | 467.3035 | 337.7279 | 314.5387 | 193.4796
582.6135 | 467.2278 | 337.9805 | 314.651 | 193.8631
583.6135 | 467.0951 | 338.2627 | 314.945 | 194.4271
584.6135 | 466.9719 | 338.4995 | 315.2079 | 194.9061
585.6135 | 466.8755 | 338.7685 | 315.4289 | 195.3734
586.6135 | 466.7658 | 339.0619 | 315.7331 | 195.8571
587.6135 | 466.7699 | 339.3129 | 315.9722 | 196.2576
588.6135 | 466.7277 | 339.5553 | 316.0858 | 196.6751
589.6135 | 466.8124 | 339.8076 | 316.3038 | 197.1338
590.6135 | 466.7688 | 340.1088 | 316.5043 | 197.5695
591.6135 | 466.7451 | 340.3816 | 316.7293 | 197.9675
592.6135 | 466.8485 | 340.626 | 316.9663 | 198.5082
593.6135 | 466.7385 | 340.8476 | 317.2458 | 199.0149
594.6135 | 466.7356 | 341.1166 | 317.4153 | 199.3774
595.6135 | 466.803 | 341.3902 | 317.5624 | 199.5855
596.6135 | 466.8511 | 341.5461 | 317.732 | 200.0185
597.6135 | 466.7459 | 341.8068 | 317.8739 | 200.5331
598.6135 | 466.6319 | 342.091 | 318.0631 | 200.9325
599.6135 | 466.7049 | 342.3472 | 318.4603 | 201.3393
600.6135 | 467.0188 | 342.6698 | 318.7507 | 201.8246
601.6135 | 467.2934 | 342.9724 | 318.9686 | 202.2789
602.6135 | 467.4742 | 343.2122 | 319.1472 | 202.7491
603.6135 | 467.5423 | 343.3686 | 319.2714 | 203.2607
604.6135 | 467.5152 | 343.6828 | 319.6305 | 203.7059
605.6135 | 467.4491 | 343.91 | 319.8954 | 204.0677
606.6135 | 467.4417 | 344.124 | 320.0858 | 204.5104
607.6135 | 467.4585 | 344.4194 | 320.3155 | 205.0248
608.6135 | 467.5068 | 344.669 | 320.4893 | 205.5224
609.6135 | 467.4756 | 344.9265 | 320.8198 | 205.8853
610.6135 | 467.6301 | 345.1726 | 321.0224 | 206.429
611.6135 | 467.582 | 345.3598 | 321.1709 | 206.9499
612.6135 | 467.5549 | 345.6454 | 321.4023 | 207.3756
613.6135 | 467.5115 | 345.9013 | 321.3672 | 207.7592
614.6135 | 467.4505 | 346.0979 | 321.712 | 208.2349
615.6135 | 467.4077 | 346.3659 | 322.0475 | 208.5995
616.6135 | 467.407 | 346.6167 | 322.2171 | 209.0162
617.6135 | 467.447 | 346.8753 | 322.1886 | 209.4018
618.6135 | 467.4379 | 347.1724 | 322.3758 | 209.8489
619.6135 | 467.4764 | 347.3829 | 322.6751 | 210.2645
620.6135 | 467.4994 | 347.63 | 323.0818 | 210.6696
621.6135 | 467.4256 | 347.8722 | 323.4094 | 211.0314
622.6135 | 467.4618 | 348.0996 | 323.7199 | 211.5005
623.6135 | 467.5367 | 348.3391 | 323.9362 | 211.8416
624.6135 | 467.5619 | 348.6052 | 324.1141 | 212.1863
625.6135 | 467.4432 | 348.8237 | 324.3817 | 212.5708
626.6135 | 467.414 | 349.0806 | 324.6054 | 213.0801
627.6135 | 467.3588 | 349.3128 | 324.8628 | 213.5053
628.6135 | 467.3625 | 349.5295 | 325.0876 | 213.9282
629.6135 | 467.3948 | 349.774 | 325.3045 | 214.4281
630.6135 | 467.3993 | 349.9981 | 325.2854 | 214.8856
631.6135 | 467.1971 | 350.2537 | 325.6127 | 215.3729
632.6135 | 467.0861 | 350.5193 | 325.8904 | 215.7295
633.6135 | 466.9001 | 350.7782 | 326.0781 | 216.0982
634.6135 | 466.7455 | 351.0197 | 326.3358 | 216.4656
635.6135 | 466.6508 | 351.2415 | 326.5528 | 216.7467
636.6135 | 466.6641 | 351.484 | 326.7629 | 217.096
637.6135 | 466.6884 | 351.7055 | 327.0118 | 217.3856
638.6135 | 466.7643 | 351.9813 | 326.9953 | 217.7561
639.6135 | 466.7556 | 352.1979 | 327.2078 | 218.103
640.6135 | 466.6834 | 352.4062 | 327.454 | 218.6302
641.6135 | 466.6031 | 352.6268 | 327.7146 | 219.0392
642.6135 | 466.4961 | 352.8634 | 327.9396 | 219.4418
643.6135 | 466.4622 | 353.0698 | 328.1592 | 219.8323
644.6135 | 466.4554 | 353.332 | 328.375 | 220.2747
645.6135 | 466.368 | 353.5056 | 328.5799 | 220.5813
646.6135 | 466.3672 | 353.7231 | 328.8067 | 220.9541
647.6135 | 466.39 | 353.9901 | 329.0506 | 221.3551
648.6135 | 466.3651 | 354.2122 | 329.2001 | 221.6935
649.6135 | 466.2878 | 354.3642 | 329.3846 | 221.9845
650.6135 | 466.2835 | 354.6188 | 329.5947 | 222.3686
651.6135 | 466.2168 | 354.856 | 329.8364 | 222.7872
652.6135 | 466.2631 | 355.0438 | 330.0618 | 223.0781
653.6135 | 466.1957 | 355.2972 | 330.2458 | 223.4645
654.6135 | 466.147 | 355.5354 | 330.4987 | 223.8095
655.6135 | 466.2139 | 355.7325 | 330.5018 | 224.1441
656.6135 | 466.1944 | 355.9724 | 330.8402 | 224.4821
657.6135 | 466.1635 | 356.1655 | 330.9317 | 224.8748
658.6135 | 466.1303 | 356.3647 | 331.0976 | 225.203
659.6135 | 466.12 | 356.5615 | 331.3981 | 225.7064
660.6135 | 466.1816 | 356.7823 | 331.6666 | 226.1344
661.6135 | 466.2813 | 357.0051 | 331.853 | 226.513
662.6135 | 466.2707 | 357.1864 | 331.9743 | 226.8193
663.6135 | 466.2491 | 357.425 | 332.2468 | 227.2438
664.6135 | 466.3516 | 357.7014 | 332.3635 | 227.6727
665.6135 | 466.3419 | 357.8148 | 332.6472 | 227.9635
666.6135 | 466.3063 | 357.9486 | 332.8352 | 228.3418
667.6135 | 466.1543 | 358.2685 | 332.9891 | 228.7619
668.6135 | 466.1123 | 358.4651 | 333.2442 | 229.0543
669.6135 | 466.1387 | 358.6918 | 333.4409 | 229.411
670.6135 | 466.1681 | 358.9133 | 333.5794 | 229.702
671.6135 | 466.1099 | 359.1497 | 333.7626 | 230.0851
672.6135 | 466.1131 | 359.383 | 333.943 | 230.4539
673.6135 | 466.2298 | 359.6075 | 334.0923 | 230.7597
674.6135 | 466.261 | 359.8088 | 334.2668 | 231.0814
675.6135 | 466.2296 | 359.9893 | 334.1381 | 231.3786
676.6135 | 466.1777 | 360.2156 | 334.4612 | 231.5969
677.6135 | 466.2799 | 360.4378 | 334.8203 | 231.8731
678.6135 | 466.333 | 360.6396 | 335.1116 | 232.19
679.6135 | 466.3169 | 360.8658 | 335.2536 | 232.595
680.6135 | 466.2922 | 361.003 | 335.3703 | 232.8096
681.6135 | 466.317 | 361.1876 | 335.5349 | 232.9843
682.6135 | 466.28 | 361.4236 | 335.7743 | 233.2502
683.6135 | 466.2161 | 361.6343 | 336.0156 | 233.4479
684.6135 | 466.265 | 361.8072 | 336.2005 | 233.6046
685.6135 | 466.2534 | 361.9813 | 336.4709 | 233.7672
686.6135 | 466.2257 | 362.2163 | 336.6972 | 233.971
687.6135 | 466.2583 | 362.4511 | 336.8544 | 234.2259
688.6135 | 466.2326 | 362.6584 | 337.0776 | 234.4337
689.6135 | 466.1716 | 362.8379 | 337.2708 | 234.6528
690.6135 | 466.1729 | 362.9809 | 337.2698 | 234.8165
691.6135 | 466.2141 | 363.2019 | 337.5557 | 235.0891
692.6135 | 466.1745 | 363.451 | 337.7188 | 235.411
693.6135 | 466.1322 | 363.6647 | 337.8931 | 235.6633
694.6135 | 466.1619 | 363.856 | 338.0499 | 235.8449
695.6135 | 466.0098 | 364.0686 | 338.2381 | 236.0977
696.6135 | 465.9337 | 364.179 | 338.4454 | 236.3494
697.6135 | 466.0612 | 364.3689 | 338.6569 | 236.7232
698.6135 | 466.1432 | 364.575 | 338.8081 | 236.986
699.6135 | 466.0764 | 364.815 | 339.0793 | 237.2501
700.6135 | 466.0612 | 364.9727 | 338.9986 | 237.5073
701.6135 | 466.2073 | 365.1781 | 339.0138 | 237.7713
702.6135 | 466.4493 | 365.3617 | 339.3165 | 238.1548
703.6135 | 466.5098 | 365.5571 | 339.512 | 238.3994
704.6135 | 466.6324 | 365.7709 | 339.7091 | 238.6952
705.6135 | 466.5938 | 366.0169 | 339.9275 | 238.8937
706.6135 | 466.6543 | 366.2048 | 340.1442 | 239.186
707.6135 | 466.678 | 366.4499 | 340.4096 | 239.572
708.6135 | 466.6596 | 366.61 | 340.7347 | 239.9631
709.6135 | 466.7583 | 366.7686 | 340.9329 | 240.3886
710.6135 | 466.7401 | 366.9244 | 341.0941 | 240.6835
711.6135 | 466.65 | 367.1279 | 341.1698 | 240.9998
712.6135 | 466.605 | 367.2686 | 341.2951 | 241.3553
713.6135 | 466.7949 | 367.4353 | 341.5353 | 241.7141
714.6135 | 466.7802 | 367.6336 | 341.6715 | 241.9952
715.6135 | 466.7619 | 367.7277 | 341.7147 | 242.3022
716.6135 | 466.7736 | 368.0373 | 341.7647 | 242.7318
717.6135 | 466.8237 | 368.2527 | 342.024 | 243.159
718.6135 | 466.9355 | 368.4478 | 342.3858 | 243.5725
719.6135 | 467.1715 | 368.69 | 342.5644 | 243.9955
720.6135 | 467.176 | 368.9011 | 342.8178 | 244.4092
721.6135 | 467.2639 | 369.1239 | 342.8406 | 244.8188
722.6135 | 467.5144 | 369.2973 | 343.0708 | 245.223
723.6135 | 467.5576 | 369.4487 | 343.2023 | 245.6758
724.6135 | 467.4461 | 369.6224 | 343.1561 | 246.0756
725.6135 | 467.4289 | 369.8557 | 343.194 | 246.5345
726.6135 | 467.5122 | 370.0716 | 343.5769 | 246.9551
727.6135 | 467.5311 | 370.2408 | 343.8454 | 247.4111
728.6135 | 467.4949 | 370.3553 | 343.8845 | 247.945
729.6135 | 467.5787 | 370.5567 | 343.9511 | 248.4417
730.6135 | 467.5776 | 370.749 | 344.1779 | 248.9089
731.6135 | 467.4455 | 370.8934 | 344.2506 | 249.3602
732.6135 | 467.3725 | 371.1124 | 344.5705 | 249.9243
733.6135 | 467.3118 | 371.26 | 344.9378 | 250.4392
734.6135 | 467.3092 | 371.4397 | 345.1093 | 251.0114
735.6135 | 467.3065 | 371.6861 | 345.2658 | 251.4922
736.6135 | 467.4197 | 371.858 | 345.4986 | 251.9489
737.6135 | 467.3533 | 371.9784 | 345.7029 | 252.6371
738.6135 | 467.381 | 372.1662 | 345.8996 | 253.2112
739.6135 | 467.431 | 372.3876 | 345.9284 | 253.7279
740.6135 | 467.4058 | 372.569 | 346.2582 | 254.2219
741.6135 | 467.2779 | 372.8109 | 346.4211 | 254.7239
742.6135 | 467.2824 | 373.0016 | 346.6751 | 255.2872
743.6135 | 467.2489 | 373.1321 | 346.7503 | 255.8243
744.6135 | 467.1333 | 373.3155 | 347.0045 | 256.4521
745.6135 | 467.0844 | 373.5094 | 347.2263 | 256.9175
746.6135 | 466.9564 | 373.7086 | 347.3878 | 257.4649
747.6135 | 466.8599 | 373.9033 | 347.4392 | 257.9849
748.6135 | 466.8763 | 374.0501 | 347.5237 | 258.4899
749.6135 | 467.0157 | 374.2689 | 347.7389 | 258.9046
750.6135 | 467.1115 | 374.3685 | 347.9099 | 259.3122
751.6135 | 467.049 | 374.5617 | 347.8453 | 259.7575
752.6135 | 467.0677 | 374.6919 | 348.0681 | 260.2756
753.6135 | 467.0787 | 374.8459 | 348.3414 | 260.6096
754.6135 | 467.0449 | 375.0041 | 348.6231 | 260.9279
755.6135 | 466.9573 | 375.2407 | 348.7821 | 261.2922
756.6135 | 466.9742 | 375.3776 | 348.8284 | 261.6298
757.6135 | 466.9518 | 375.5265 | 348.8622 | 261.9467
758.6135 | 467.0354 | 375.6925 | 349.0702 | 262.3344
759.6135 | 467.0747 | 375.8462 | 349.329 | 262.6566
760.6135 | 467.1967 | 376.0331 | 349.3771 | 262.9939
761.6135 | 467.2719 | 376.2488 | 349.6842 | 263.3674
762.6135 | 467.2582 | 376.4352 | 349.8927 | 263.6966
763.6135 | 467.2267 | 376.5187 | 350.005 | 264.0435
764.6135 | 467.2596 | 376.7522 | 350.2026 | 264.382
765.6135 | 467.2389 | 376.9672 | 350.4566 | 264.7209
766.6135 | 467.2606 | 377.0983 | 350.6503 | 265.0622
767.6135 | 467.2027 | 377.3278 | 350.7965 | 265.411
768.6135 | 467.1815 | 377.5138 | 350.9921 | 265.7802
769.6135 | 467.2564 | 377.6771 | 351.1999 | 266.1507
770.6135 | 467.2703 | 377.7997 | 351.4098 | 266.5611
771.6135 | 467.2381 | 377.9776 | 351.6222 | 266.9895
772.6135 | 467.1754 | 378.146 | 351.7576 | 267.3259
773.6135 | 467.0571 | 378.2912 | 351.8833 | 267.6334
774.6135 | 467.0186 | 378.4254 | 352.1485 | 267.9449
775.6135 | 467.0191 | 378.5744 | 352.3508 | 268.2364
776.6135 | 466.9517 | 378.8248 | 352.465 | 268.5791
777.6135 | 466.7631 | 378.9442 | 352.6173 | 268.9474
778.6135 | 466.6839 | 379.0947 | 352.6788 | 269.292
779.6135 | 466.5882 | 379.3371 | 352.8604 | 269.6633
780.6135 | 466.4302 | 379.454 | 353.0772 | 270.0191
781.6135 | 466.3128 | 379.6003 | 353.0702 | 270.3708
782.6135 | 466.2546 | 379.6944 | 353.1922 | 270.7189
783.6135 | 466.0958 | 379.9285 | 353.4026 | 271.0846
784.6135 | 465.9682 | 380.1674 | 353.5983 | 271.5096
785.6135 | 465.9499 | 380.2302 | 353.8162 | 271.8776
786.6135 | 465.8893 | 380.4508 | 354.023 | 272.1897
787.6135 | 465.7849 | 380.6657 | 354.2244 | 272.5443
788.6135 | 465.7399 | 380.8757 | 354.4379 | 272.9491
789.6135 | 465.8284 | 380.9817 | 354.4996 | 273.259
790.6135 | 465.7812 | 381.114 | 354.6783 | 273.4937
791.6135 | 465.867 | 381.3 | 354.8032 | 273.9477
792.6135 | 465.8283 | 381.4115 | 354.8939 | 274.3088
793.6135 | 465.8693 | 381.6095 | 354.9884 | 274.4798
794.6135 | 465.9198 | 381.8136 | 355.1455 | 274.7232
795.6135 | 465.989 | 382.0022 | 355.3429 | 274.8707
796.6135 | 466.1066 | 382.123 | 355.5041 | 275.0666
797.6135 | 466.2489 | 382.2805 | 355.5672 | 275.2342
798.6135 | 466.3033 | 382.4682 | 355.7852 | 275.3613
799.6135 | 466.3574 | 382.6011 | 355.9764 | 275.557
800.6135 | 466.3666 | 382.7351 | 356.2308 | 275.7523
801.6135 | 466.4777 | 382.8666 | 356.406 | 275.8819
802.6135 | 466.4979 | 383.0996 | 356.5551 | 275.9541
803.6135 | 466.4636 | 383.2288 | 356.6638 | 276.0442
804.6135 | 466.5212 | 383.4413 | 356.6763 | 276.1149
805.6135 | 466.6011 | 383.5551 | 356.8497 | 276.3278
806.6135 | 466.6662 | 383.7443 | 357.1416 | 276.5552
807.6135 | 466.6793 | 383.9044 | 357.2354 | 276.8142
808.6135 | 466.6531 | 384.0847 | 357.36 | 276.9969
809.6135 | 466.6508 | 384.3014 | 357.5553 | 277.2171
810.6135 | 466.6951 | 384.4541 | 357.6463 | 277.4196
811.6135 | 466.6636 | 384.6058 | 357.8432 | 277.7549
812.6135 | 466.7708 | 384.7174 | 357.9804 | 278.037
813.6135 | 466.9435 | 384.8431 | 358.2271 | 278.3376
814.6135 | 466.8937 | 384.9975 | 358.4653 | 278.6127
815.6135 | 466.7622 | 385.1176 | 358.6367 | 278.9308
816.6135 | 466.7654 | 385.3233 | 358.7799 | 279.1048
817.6135 | 466.8479 | 385.4493 | 359.0085 | 279.4349
818.6135 | 466.6844 | 385.5428 | 359.1583 | 279.7779
819.6135 | 466.6793 | 385.731 | 359.2356 | 280.0113
820.6135 | 466.7777 | 385.9086 | 359.464 | 280.2251
821.6135 | 466.62 | 386.0979 | 359.6347 | 280.479
822.6135 | 466.5753 | 386.2701 | 359.808 | 280.7649
823.6135 | 466.6637 | 386.3985 | 360.0071 | 281.029
824.6135 | 466.6809 | 386.5748 | 360.1027 | 281.2934
825.6135 | 466.5629 | 386.7121 | 360.3258 | 281.5639
826.6135 | 466.4899 | 386.9203 | 360.4323 | 281.8319
827.6135 | 466.474 | 387.0296 | 360.5745 | 282.1381
828.6135 | 466.3958 | 387.1785 | 360.7022 | 282.4062
829.6135 | 466.3208 | 387.3348 | 360.9514 | 282.6717
830.6135 | 466.4317 | 387.5229 | 361.0652 | 282.917
831.6135 | 466.5128 | 387.6338 | 361.1063 | 283.2034
832.6135 | 466.4247 | 387.7988 | 361.3088 | 283.4944
833.6135 | 466.4962 | 387.9592 | 361.591 | 283.7986
834.6135 | 466.5385 | 388.1677 | 361.7359 | 283.9317
835.6135 | 466.6446 | 388.3413 | 361.8443 | 284.0342
836.6135 | 466.7083 | 388.4435 | 361.9644 | 284.3317
837.6135 | 466.5239 | 388.5582 | 362.0877 | 284.5608
838.6135 | 466.4417 | 388.6891 | 362.2099 | 284.8005
839.6135 | 466.4027 | 388.8085 | 362.4475 | 285.0908
840.6135 | 466.2653 | 389.0522 | 362.5637 | 285.2481
841.6135 | 466.3164 | 389.269 | 362.6554 | 285.5146
842.6135 | 466.3973 | 389.4361 | 362.8196 | 285.8311
843.6135 | 466.3998 | 389.5751 | 362.9449 | 286.1095
844.6135 | 466.3387 | 389.6682 | 363.0456 | 286.3645
845.6135 | 466.2444 | 389.8072 | 363.1319 | 286.6686
846.6135 | 466.1716 | 389.9505 | 363.3778 | 286.9237
847.6135 | 466.1895 | 390.1228 | 363.5178 | 287.1287
848.6135 | 466.3353 | 390.3252 | 363.7052 | 287.3146
849.6135 | 466.451 | 390.4841 | 363.5753 | 287.5415
850.6135 | 466.4842 | 390.6661 | 363.7814 | 287.7896
851.6135 | 466.5276 | 390.7701 | 363.7911 | 288.0374
852.6135 | 466.5351 | 390.8561 | 364.0853 | 288.2792
853.6135 | 466.5806 | 391.0298 | 364.304 | 288.5043
854.6135 | 466.7551 | 391.2094 | 364.4405 | 288.7269
855.6135 | 466.766 | 391.3946 | 364.5689 | 288.9414
856.6135 | 466.7697 | 391.5585 | 364.7676 | 289.1572
857.6135 | 466.9073 | 391.7601 | 364.7149 | 289.3382
858.6135 | 467.0446 | 391.7935 | 364.9472 | 289.6276
859.6135 | 467.136 | 391.9039 | 365.0871 | 290.8189
860.6135 | 467.2631 | 392.1098 | 365.3366 | 290.7942
861.6135 | 467.2942 | 392.3167 | 365.259 | 290.8022
862.6135 | 467.3734 | 392.5006 | 365.5252 | 290.9533
863.6135 | 467.3921 | 392.6252 | 365.7616 | 290.9893
864.6135 | 467.4623 | 392.8007 | 365.9531 | 291.133
865.6135 | 467.4125 | 392.9822 | 366.1201 | 291.1628
866.6135 | 467.4472 | 393.1231 | 366.1795 | 290.9465
867.6135 | 467.3917 | 393.2649 | 366.4548 | 291.004
868.6135 | 467.2971 | 393.3777 | 366.6582 | 291.0798
869.6135 | 467.2933 | 393.5159 | 366.7852 | 291.2035
870.6135 | 467.2579 | 393.6715 | 366.9137 | 291.3264
871.6135 | 467.1866 | 393.7675 | 366.9981 | 291.4896
872.6135 | 467.0145 | 393.9406 | 367.1437 | 291.667
873.6135 | 467.0188 | 394.1003 | 367.317 | 291.9826
874.6135 | 466.9726 | 394.2462 | 367.5062 | 292.1699
875.6135 | 466.8899 | 394.1049 | 367.7497 | 292.2966
876.6135 | 466.8713 | 394.3818 | 367.906 | 292.4576
877.6135 | 466.8416 | 394.601 | 367.9753 | 292.7369
878.6135 | 466.7903 | 394.8663 | 368.1559 | 292.9306
879.6135 | 466.8341 | 395.0496 | 368.3041 | 293.1063
880.6135 | 466.8643 | 395.1774 | 368.3543 | 293.2384
881.6135 | 466.9066 | 395.3484 | 368.5127 | 293.4413
882.6135 | 466.9727 | 395.4664 | 368.7507 | 294.5562
883.6135 | 466.9313 | 395.5803 | 368.8524 | 294.7622
884.6135 | 466.9135 | 395.6838 | 368.988 | 295.204
885.6135 | 466.9847 | 395.8835 | 369.0887 | 295.2912
886.6135 | 467.0623 | 396.0901 | 369.1635 | 295.5097
887.6135 | 466.9804 | 396.1661 | 369.3318 | 295.484
888.6135 | 466.9128 | 396.3322 | 369.414 | 295.3176
889.6135 | 466.9434 | 396.4759 | 369.4896 | 295.1958
890.6135 | 466.9051 | 396.652 | 369.7312 | 295.2755
891.6135 | 466.7933 | 396.6901 | 369.9852 | 295.3696
892.6135 | 466.7903 | 396.8597 | 370.1434 | 295.521
893.6135 | 466.6583 | 397.0009 | 370.3302 | 295.6781
894.6135 | 466.6327 | 397.0547 | 370.4005 | 295.7533
895.6135 | 466.6879 | 397.1615 | 370.5237 | 295.8539
896.6135 | 466.7222 | 397.3856 | 370.5206 | 295.9758
897.6135 | 466.7028 | 397.4625 | 370.6913 | 296.5503
898.6135 | 466.6255 | 397.6093 | 370.8553 | 296.3268
899.6135 | 466.4905 | 397.8066 | 371.0672 | 296.3834
900.6135 | 466.3581 | 397.9372 | 371.1341 | 296.4351
901.6135 | 466.3225 | 398.1385 | 371.3074 | 296.5273
902.6135 | 466.3337 | 398.2869 | 371.4317 | 296.8994
903.6135 | 466.3732 | 398.4063 | 371.5721 | 297.1202
904.6135 | 466.3548 | 398.5231 | 371.6735 | 297.3167
905.6135 | 466.3249 | 398.5947 | 371.8722 | 297.391
906.6135 | 466.2097 | 398.7943 | 371.9351 | 297.4829
907.6135 | 466.2383 | 398.9462 | 372.0532 | 298.3536
908.6135 | 466.2226 | 398.9787 | 372.305 | 298.4997
909.6135 | 466.1657 | 399.0095 | 372.4063 | 298.9155
910.6135 | 466.1171 | 399.1515 | 372.3862 | 298.8076
911.6135 | 466.0446 | 399.3787 | 372.4176 | 298.7513
912.6135 | 466.0964 | 399.5436 | 372.6008 | 298.5152
913.6135 | 466.055 | 399.7255 | 372.6344 | 298.5101
914.6135 | 465.9533 | 399.7745 | 372.5776 | 298.5953
915.6135 | 465.803 | 399.8527 | 372.948 | 298.5622
916.6135 | 465.841 | 399.9321 | 372.9009 | 298.6895
917.6135 | 465.9396 | 400.0668 | 373.1076 | 298.7991
918.6135 | 465.9823 | 400.2571 | 373.2171 | 298.9296
919.6135 | 466.1149 | 400.3819 | 373.3356 | 298.9601
920.6135 | 466.2476 | 400.5753 | 373.4846 | 298.9888
921.6135 | 466.2991 | 400.7146 | 373.5263 | 299.0695
922.6135 | 466.2397 | 400.8017 | 373.6408 | 299.1039
923.6135 | 466.1133 | 400.9451 | 373.5196 | 299.1191
924.6135 | 466.1157 | 401.0679 | 373.7559 | 299.2294
925.6135 | 466.2176 | 401.1949 | 374.0584 | 299.2129
926.6135 | 466.2531 | 401.2658 | 374.1189 | 299.223
927.6135 | 466.32 | 401.4132 | 374.2781 | 299.5022
928.6135 | 466.2587 | 401.5636 | 374.4385 | 299.5528
929.6135 | 466.1698 | 401.7104 | 374.5717 | 299.5892
930.6135 | 466.1666 | 401.8225 | 374.7044 | 299.5422
931.6135 | 466.1589 | 401.9327 | 374.8829 | 299.5797
932.6135 | 466.141 | 402.0388 | 375.0169 | 299.6337
933.6135 | 466.0561 | 402.1208 | 375.0425 | 299.7466
934.6135 | 466.126 | 402.273 | 375.2514 | 299.8643
935.6135 | 466.1509 | 402.4023 | 375.238 | 299.8527
936.6135 | 466.2184 | 402.5349 | 375.4144 | 299.8691
937.6135 | 466.0985 | 402.6042 | 375.5996 | 299.9909
938.6135 | 466.0598 | 402.7495 | 375.719 | 300.1727
939.6135 | 466.0005 | 402.7612 | 375.8582 | 300.3457
940.6135 | 465.8454 | 402.948 | 375.9495 | 300.5714
941.6135 | 465.7883 | 403.1265 | 376.0697 | 300.7761
942.6135 | 465.8057 | 403.2681 | 376.3011 | 300.8435
943.6135 | 465.8234 | 403.3133 | 376.2943 | 300.9075
944.6135 | 465.8065 | 403.3752 | 376.3774 | 301.0212
945.6135 | 465.7698 | 403.5042 | 376.3715 | 301.155
946.6135 | 465.7643 | 403.6623 | 376.543 | 301.388
947.6135 | 465.8011 | 403.7768 | 376.5992 | 301.4221
948.6135 | 465.8695 | 403.8254 | 376.8765 | 301.5912
949.6135 | 466.0194 | 403.8013 | 376.9448 | 302.2833
950.6135 | 465.9745 | 403.9951 | 376.9569 | 301.9976
951.6135 | 465.9152 | 404.146 | 377.1604 | 302.1023
952.6135 | 465.964 | 404.1923 | 377.2754 | 302.2471
953.6135 | 465.9678 | 404.3101 | 377.4403 | 302.3543
954.6135 | 465.9985 | 404.329 | 377.3995 | 302.5408
955.6135 | 466.0838 | 404.4504 | 377.5663 | 302.9669
956.6135 | 466.1267 | 404.5218 | 377.7366 | 302.8326
957.6135 | 466.104 | 404.5603 | 377.8483 | 302.8466
958.6135 | 466.1701 | 404.6108 | 377.9294 | 302.9743
959.6135 | 466.3501 | 404.7491 | 378.0255 | 303.62
960.6135 | 466.3399 | 404.8887 | 378.1373 | 303.3103
961.6135 | 466.377 | 404.9657 | 378.2473 | 303.3344
962.6135 | 466.3926 | 405.0491 | 378.3963 | 303.4278
963.6135 | 466.4349 | 405.1158 | 378.4699 | 303.6044
964.6135 | 466.4435 | 405.2153 | 378.1787 | 303.887
965.6135 | 466.4929 | 405.2267 | 378.4459 | 304.1698
966.6135 | 466.4661 | 405.3163 | 378.5747 | 304.3253
967.6135 | 466.6155 | 405.3243 | 378.7371 | 304.1655
968.6135 | 466.6848 | 405.4253 | 378.9245 | 304.1003
969.6135 | 466.6763 | 405.5741 | 379.1342 | 304.11
970.6135 | 466.5814 | 405.6635 | 379.1653 | 304.1904
971.6135 | 466.609 | 405.8173 | 379.3175 | 304.2256
972.6135 | 466.6415 | 405.9086 | 379.4376 | 304.3323
973.6135 | 466.5568 | 406.0121 | 379.203 | 304.3872
974.6135 | 466.4217 | 406.0407 | 379.431 | 304.3914
975.6135 | 466.3735 | 406.127 | 379.6097 | 304.5406
976.6135 | 466.493 | 406.2325 | 379.7567 | 304.7996
977.6135 | 466.5312 | 406.3444 | 379.8584 | 304.8507
978.6135 | 466.574 | 406.3686 | 380.0113 | 304.795
979.6135 | 466.6126 | 406.4399 | 380.1919 | 305.2836
980.6135 | 466.6121 | 406.5894 | 380.2083 | 304.8699
981.6135 | 466.4884 | 406.5446 | 380.2206 | 304.8944
982.6135 | 466.44 | 406.6219 | 380.4395 | 305.0231
983.6135 | 466.4333 | 406.7503 | 380.5566 | 304.9726
984.6135 | 466.3364 | 406.8848 | 380.6454 | 305.0242
985.6135 | 466.2684 | 406.9855 | 380.7926 | 304.8694
986.6135 | 466.1817 | 407.0211 | 380.7915 | 305.1931
987.6135 | 466.2149 | 407.0698 | 380.9732 | 305.3866
988.6135 | 466.2541 | 407.1237 | 381.1594 | 305.3592
989.6135 | 466.1538 | 407.2494 | 381.2337 | 305.126
990.6135 | 466.1808 | 407.2358 | 381.3321 | 305.1669
991.6135 | 466.2323 | 407.2862 | 381.2163 | 305.3703
992.6135 | 466.153 | 407.3564 | 381.4187 | 305.4215
993.6135 | 466.195 | 407.4351 | 381.5458 | 305.5804
994.6135 | 466.1285 | 407.4903 | 381.6674 | 305.9223
995.6135 | 466.1078 | 407.5998 | 381.3206 | 305.5759
996.6135 | 466.1629 | 407.6299 | 381.0515 | 305.6746
997.6135 | 466.2447 | 407.7588 | 381.3519 | 305.6804
998.6135 | 466.2173 | 407.9256 | 381.6481 | 305.756
999.6135 | 466.2864 | 407.9638 | 381.8507 | 305.9987
1000.6135 | 466.3675 | 408.0041 | 381.9366 | 306.2074
1001.6135 | 466.4609 | 408.0729 | 382.1136 | 306.2306
1002.6135 | 466.5955 | 408.1645 | 382.3177 | 306.561
1003.6135 | 466.6333 | 408.2353 | 382.4409 | 306.5589
1004.6135 | 466.6351 | 408.2973 | 382.5079 | 306.5852
1005.6135 | 466.6636 | 408.3802 | 382.3097 | 306.5644
1006.6135 | 466.7052 | 408.4413 | 382.4534 | 306.5352
1007.6135 | 466.8112 | 408.4863 | 382.6248 | 306.5656
1008.6135 | 466.7509 | 408.5987 | 382.761 | 306.6345
1009.6135 | 466.84 | 408.6919 | 382.9421 | 306.8173
1010.6135 | 466.8853 | 408.7849 | 383.1047 | 306.9123
1011.6135 | 466.8715 | 408.7707 | 383.1852 | 306.8465
1012.6135 | 466.8163 | 408.8581 | 383.2764 | 306.943
1013.6135 | 466.732 | 408.8769 | 383.2993 | 306.9717
1014.6135 | 466.646 | 408.952 | 383.3525 | 307.1033
1015.6135 | 466.4427 | 409.0515 | 383.4203 | 307.1409
1016.6135 | 466.2686 | 409.1037 | 383.4564 | 307.3121
1017.6135 | 466.2966 | 409.1415 | 383.5603 | 307.523
1018.6135 | 466.1682 | 409.224 | 383.7141 | 307.6457
1019.6135 | 465.9374 | 409.2362 | 383.7694 | 307.8337
1020.6135 | 465.8811 | 409.2144 | 383.7874 | 307.9413
1021.6135 | 465.9349 | 409.3809 | 383.8634 | 307.9783
1022.6135 | 465.9117 | 409.4469 | 383.9574 | 308.2964
1023.6135 | 465.856 | 409.5096 | 383.9997 | 308.7435
1024.6135 | 465.8194 | 409.6405 | 383.9481 | 308.7274
1025.6135 | 465.8163 | 409.7154 | 384.0446 | 308.7871
1026.6135 | 465.7283 | 409.7759 | 384.261 | 308.9505
1027.6135 | 465.7935 | 409.8198 | 384.475 | 309.1032
1028.6135 | 465.8386 | 409.8538 | 384.5243 | 309.3235
1029.6135 | 465.9209 | 409.8062 | 384.5304 | 309.5199
1030.6135 | 465.9087 | 409.8863 | 384.6924 | 309.82
1031.6135 | 466.0349 | 409.9117 | 384.9425 | 309.7289
1032.6135 | 465.9977 | 410.0057 | 385.0339 | 310.259
1033.6135 | 466.0327 | 410.0471 | 385.1103 | 310.4607
1034.6135 | 466.0595 | 410.1468 | 385.0607 | 310.8034
1035.6135 | 466.091 | 410.2065 | 385.2312 | 311.1078
1036.6135 | 466.0454 | 410.2761 | 385.3962 | 311.0325
1037.6135 | 466.0551 | 410.3197 | 385.4452 | 311.1869
1038.6135 | 465.9229 | 410.4148 | 385.5762 | 311.5262
1039.6135 | 465.9606 | 410.4897 | 385.5465 | 311.346
1040.6135 | 466.0294 | 410.4846 | 385.6781 | 311.5982
1041.6135 | 466.1805 | 410.5222 | 385.761 | 311.5909
1042.6135 | 466.1825 | 410.5601 | 385.8983 | 311.5499
1043.6135 | 466.1726 | 410.6468 | 386.0203 | 311.5934
1044.6135 | 466.2458 | 410.7009 | 386.1255 | 311.7593
1045.6135 | 466.276 | 410.7807 | 386.0668 | 312.0637
1046.6135 | 466.2502 | 410.8382 | 386.1996 | 312.1486
1047.6135 | 466.2718 | 410.8847 | 386.2924 | 312.4432
1048.6135 | 466.2827 | 410.9584 | 386.4528 | 313.001
1049.6135 | 466.2107 | 410.998 | 386.5496 | 313.0211
1050.6135 | 466.0765 | 411.0576 | 386.6116 | 313.0532
1051.6135 | 466.0665 | 411.152 | 386.6394 | 313.1901
1052.6135 | 466.0173 | 411.1426 | 386.6974 | 313.4885
1053.6135 | 466.0286 | 411.1944 | 386.838 | 313.6259
1054.6135 | 466.0587 | 411.2236 | 386.9697 | 313.9079
1055.6135 | 465.96 | 411.2404 | 386.9685 | 314.0857
1056.6135 | 466.0313 | 411.3213 | 387.0401 | 314.2787
1057.6135 | 466.0302 | 411.3861 | 387.1457 | 314.5708
1058.6135 | 466.1714 | 411.397 | 387.2516 | 314.9226
1059.6135 | 466.1554 | 411.3708 | 387.2074 | 314.9558
1060.6135 | 465.9909 | 411.4329 | 387.2283 | 315.0677
1061.6135 | 465.9499 | 411.5111 | 387.3496 | 315.3446
1062.6135 | 466.0806 | 411.5798 | 387.6197 | 315.6373
1063.6135 | 466.0453 | 411.5702 | 387.643 | 316.126
1064.6135 | 466.0707 | 411.6498 | 387.6582 | 316.3564
1065.6135 | 465.962 | 411.7164 | 387.7521 | 316.335
1066.6135 | 465.997 | 411.6342 | 387.8423 | 316.4934
1067.6135 | 465.9912 | 411.6601 | 387.9113 | 316.6246
1068.6135 | 465.9713 | 411.788 | 387.9745 | 316.8749
1069.6135 | 466.0719 | 411.7491 | 388.1276 | 317.1016
1070.6135 | 466.2291 | 411.7814 | 388.2035 | 317.3501
1071.6135 | 466.2761 | 411.7721 | 388.367 | 317.5867
1072.6135 | 466.3116 | 411.8549 | 388.3238 | 317.7172
1073.6135 | 466.2724 | 412.0125 | 388.2744 | 318.0139
1074.6135 | 466.1749 | 412.0374 | 388.3568 | 318.4052
1075.6135 | 466.2164 | 412.1322 | 388.4203 | 318.7696
1076.6135 | 466.2274 | 412.2109 | 388.4307 | 319.001
1077.6135 | 466.2378 | 412.2143 | 388.519 | 319.1509
1078.6135 | 466.1295 | 412.2731 | 388.6483 | 319.3812
1079.6135 | 466.0807 | 412.2794 | 388.7198 | 319.936
1080.6135 | 466.0603 | 412.273 | 388.8562 | 320.233
1081.6135 | 466.0325 | 412.3477 | 388.9627 | 320.8139
1082.6135 | 465.9014 | 412.3692 | 389.1097 | 321.2283
1083.6135 | 466.0599 | 412.4179 | 389.1517 | 321.3484
1084.6135 | 466.1117 | 412.4849 | 389.1457 | 321.6843
1085.6135 | 466.054 | 412.5099 | 389.2393 | 321.8851
1086.6135 | 465.9811 | 412.5076 | 389.2588 | 322.1692
1087.6135 | 465.8916 | 412.5475 | 389.2837 | 322.392
1088.6135 | 465.8922 | 412.6545 | 389.3501 | 322.9264
1089.6135 | 465.8753 | 412.6868 | 389.2565 | 323.3348
1090.6135 | 465.8067 | 412.7003 | 388.9053 | 323.3047
1091.6135 | 465.7533 | 412.7646 | 389.1109 | 323.7004
1092.6135 | 465.7784 | 412.8502 | 389.4133 | 323.8318
1093.6135 | 465.6343 | 412.9205 | 389.513 | 323.9543
1094.6135 | 465.5622 | 412.9758 | 389.526 | 324.1851
1095.6135 | 465.5715 | 413.0044 | 389.6858 | 324.3863
1096.6135 | 465.76 | 412.9949 | 389.7837 | 325.0843
1097.6135 | 465.8618 | 413.1128 | 389.9306 | 325.2153
1098.6135 | 466.0015 | 413.1576 | 389.9624 | 325.3729
1099.6135 | 465.9802 | 413.1517 | 390.0197 | 325.7784
1100.6135 | 466.0321 | 413.2273 | 390.1107 | 325.8708
1101.6135 | 466.1787 | 413.1971 | 390.1336 | 326.4121
1102.6135 | 466.2309 | 413.2407 | 390.2505 | 326.5761
1103.6135 | 466.2249 | 413.3093 | 390.3214 | 326.7387
1104.6135 | 466.2496 | 413.3755 | 390.1158 | 326.6021
1105.6135 | 466.3531 | 413.4003 | 390.2011 | 326.6597
1106.6135 | 466.3317 | 413.4326 | 390.1353 | 327.1635
1107.6135 | 466.368 | 413.3976 | 390.3217 | 327.9275
1108.6135 | 466.4897 | 413.4688 | 390.5469 | 328.2026
1109.6135 | 466.5293 | 413.597 | 390.5975 | 328.6494
1110.6135 | 466.5569 | 413.6156 | 390.7126 | 329.135
1111.6135 | 466.615 | 413.6304 | 390.7285 | 329.6262
1112.6135 | 466.6655 | 413.7183 | 390.8261 | 329.8405
1113.6135 | 466.6089 | 413.7933 | 390.7733 | 330.2041
1114.6135 | 466.626 | 413.7998 | 390.8763 | 330.4338
1115.6135 | 466.6859 | 413.7925 | 390.8976 | 330.6205
1116.6135 | 466.8527 | 413.8544 | 391.0197 | 330.8745
1117.6135 | 466.9137 | 413.8443 | 391.0139 | 331.6693
1118.6135 | 466.923 | 413.9183 | 391.0103 | 332.0136
1119.6135 | 466.8976 | 413.895 | 391.2072 | 332.3259
1120.6135 | 466.8948 | 413.9008 | 391.2673 | 332.5439
1121.6135 | 466.8839 | 414.0241 | 391.2605 | 332.6989
1122.6135 | 466.8724 | 414.0607 | 391.3796 | 333.221
1123.6135 | 466.926 | 414.1049 | 391.4522 | 333.5908
1124.6135 | 467.0224 | 414.1799 | 391.5304 | 333.9991
1125.6135 | 467.0042 | 414.272 | 391.5598 | 334.2151
1126.6135 | 466.9809 | 414.3169 | 391.7324 | 334.5602
1127.6135 | 467.0065 | 414.3931 | 391.6827 | 334.9995
1128.6135 | 466.9241 | 414.4039 | 391.7609 | 335.2354
1129.6135 | 466.7954 | 414.4351 | 391.8216 | 335.5114
1130.6135 | 466.7761 | 414.4747 | 391.9438 | 335.8692
1131.6135 | 466.8026 | 414.4998 | 391.9484 | 336.2202
1132.6135 | 466.6553 | 414.5105 | 391.9331 | 336.5914
1133.6135 | 466.7394 | 414.556 | 392.0121 | 336.7125
1134.6135 | 466.7236 | 414.5235 | 392.086 | 336.9672
1135.6135 | 466.7747 | 414.6039 | 392.174 | 336.9015
1136.6135 | 466.664 | 414.6067 | 392.1826 | 337.3204
1137.6135 | 466.5328 | 414.6012 | 392.2674 | 337.6094
1138.6135 | 466.503 | 414.6727 | 392.3269 | 338.0644
1139.6135 | 466.4927 | 414.7232 | 392.281 | 338.262
1140.6135 | 466.4595 | 414.8112 | 392.3564 | 338.9143
1141.6135 | 466.4193 | 414.7859 | 392.4627 | 339.8936
1142.6135 | 466.3581 | 414.8338 | 392.4682 | 340.5477
1143.6135 | 466.4327 | 414.8369 | 392.458 | 340.9254
1144.6135 | 466.5259 | 414.9086 | 392.5063 | 341.104
1145.6135 | 466.6051 | 414.9812 | 392.5217 | 340.9563
1146.6135 | 466.6352 | 415.0082 | 392.7013 | 341.3205
1147.6135 | 466.6997 | 415.0813 | 392.8031 | 341.7048
1148.6135 | 466.6771 | 415.0979 | 392.8911 | 342.0376
1149.6135 | 466.7678 | 415.0853 | 392.9013 | 342.424
1150.6135 | 466.7431 | 415.1354 | 393.0158 | 342.1667
1151.6135 | 466.6573 | 415.1703 | 393.0064 | 342.5267
1152.6135 | 466.4757 | 415.177 | 392.9899 | 342.6739
1153.6135 | 466.5048 | 415.227 | 392.9342 | 343.2762
1154.6135 | 466.5642 | 415.2628 | 393.0369 | 343.4937
1155.6135 | 466.6077 | 415.2458 | 392.9752 | 343.7239
1156.6135 | 466.5667 | 415.3097 | 393.0305 | 343.9423
1157.6135 | 466.6825 | 415.3641 | 393.0426 | 344.2981
1158.6135 | 466.7323 | 415.4176 | 393.1784 | 343.9951
1159.6135 | 466.6729 | 415.4646 | 393.3394 | 344.5984
1160.6135 | 466.5278 | 415.565 | 393.4042 | 345.0418
1161.6135 | 466.4096 | 415.6125 | 393.5014 | 345.0971
1162.6135 | 466.3597 | 415.6427 | 393.6525 | 345.2844
1163.6135 | 466.3535 | 415.6596 | 393.6096 | 345.354
1164.6135 | 466.2996 | 415.7009 | 393.6888 | 344.9275
1165.6135 | 466.1159 | 415.7387 | 393.7862 | 344.7253
1166.6135 | 466.0404 | 415.819 | 393.9111 | 345.2578
1167.6135 | 466.0889 | 415.8438 | 393.9134 | 345.567
1168.6135 | 466.1359 | 415.876 | 393.9059 | 346.1932
1169.6135 | 466.0793 | 415.9104 | 393.9495 | 347.0501
1170.6135 | 466.0725 | 415.9146 | 394.0429 | 347.6401
1171.6135 | 466.128 | 416.0045 | 394.0733 | 347.7926
1172.6135 | 466.1203 | 416.0061 | 394.0627 | 348.0322
1173.6135 | 466.2872 | 416.0503 | 394.0008 | 348.6118
1174.6135 | 466.394 | 416.0554 | 394.1021 | 348.9743
1175.6135 | 466.4611 | 416.065 | 394.2253 | 348.6467
1176.6135 | 466.4753 | 416.0571 | 394.2657 | 349.0142
1177.6135 | 466.4818 | 416.1765 | 394.2396 | 349.4269
1178.6135 | 466.5204 | 416.2403 | 394.284 | 349.9269
1179.6135 | 466.5145 | 416.2424 | 394.4569 | 350.7109
1180.6135 | 466.5416 | 416.2021 | 394.5417 | 351.0341
1181.6135 | 466.4873 | 416.2571 | 394.6614 | 350.4623
1182.6135 | 466.4473 | 416.352 | 394.6498 | 350.0857
1183.6135 | 466.436 | 416.3781 | 394.6096 | 350.6845
1184.6135 | 466.4843 | 416.3186 | 394.6025 | 350.5367
1185.6135 | 466.4492 | 416.4334 | 394.6456 | 350.0119
1186.6135 | 466.4154 | 416.4292 | 394.6457 | 350.5521
1187.6135 | 466.3917 | 416.3941 | 394.7733 | 351.038
1188.6135 | 466.4978 | 416.4596 | 394.7232 | 350.7451
1189.6135 | 466.5137 | 416.5188 | 394.825 | 350.2165
1190.6135 | 466.5244 | 416.5695 | 394.9787 | 351.3956
1191.6135 | 466.5764 | 416.5927 | 395.1016 | 351.377
1192.6135 | 466.5541 | 416.5849 | 395.2107 | 351.0889
1193.6135 | 466.5592 | 416.7075 | 395.252 | 352.0362
1194.6135 | 466.6351 | 416.7054 | 395.2345 | 352.439
1195.6135 | 466.7115 | 416.7596 | 395.3102 | 352.5276
1196.6135 | 466.704 | 416.7709 | 395.2709 | 353.2409
1197.6135 | 466.6674 | 416.7383 | 395.2176 | 354.0019
1198.6135 | 466.6904 | 416.8128 | 395.3688 | 354.2789
1199.6135 | 466.7813 | 416.9035 | 395.3865 | 354.1928
1200.6135 | 466.7651 | 416.8751 | 395.3797 | 353.9309
1201.6135 | 466.771 | 416.9008 | 395.5609 | 353.7762
1202.6135 | 466.7839 | 416.9102 | 395.5992 | 354.0819
1203.6135 | 466.7975 | 416.9127 | 395.6787 | 353.2152
1204.6135 | 466.8901 | 416.9915 | 395.5633 | 354.8689
1205.6135 | 466.957 | 417.0109 | 395.5744 | 355.0514
1206.6135 | 466.9527 | 417.0611 | 395.6343 | 354.9721
1207.6135 | 466.8687 | 417.0901 | 395.7735 | 355.2001
1208.6135 | 466.7386 | 417.1676 | 395.6518 | 355.1952
1209.6135 | 466.7017 | 417.1759 | 395.7904 | 355.2609
1210.6135 | 466.6633 | 417.2189 | 395.5375 | 354.4744
1211.6135 | 466.7123 | 417.1736 | 395.3238 | 353.8539
1212.6135 | 466.7715 | 417.1525 | 395.5213 | 353.0025
1213.6135 | 466.7341 | 417.2845 | 395.4883 | 354.0562
1214.6135 | 466.5984 | 417.3858 | 395.3922 | 354.7778
1215.6135 | 466.7473 | 417.3498 | 395.352 | 353.4973
1216.6135 | 466.7526 | 417.3959 | 395.5713 | 354.5273
1217.6135 | 466.7672 | 417.4396 | 395.8434 | 355.784
1218.6135 | 466.7654 | 417.3901 | 395.9368 | 355.7265
1219.6135 | 466.7843 | 417.4568 | 396.0042 | 356.6603
1220.6135 | 466.8457 | 417.4701 | 396.1138 | 357.3539
1221.6135 | 466.9295 | 417.5546 | 396.1068 | 358.0582
1222.6135 | 466.8618 | 417.5809 | 396.171 | 357.9991
1223.6135 | 466.8646 | 417.6954 | 396.264 | 359.4853
1224.6135 | 466.871 | 417.7016 | 396.4175 | 360.0136
1225.6135 | 466.9754 | 417.735 | 396.4722 | 360.1325
1226.6135 | 467.0991 | 417.7484 | 396.4405 | 359.9506
1227.6135 | 467.028 | 417.831 | 396.588 | 359.6919
1228.6135 | 467.0017 | 417.8661 | 396.6576 | 360.88
1229.6135 | 466.9287 | 417.8427 | 396.5794 | 361.1248
1230.6135 | 466.8329 | 417.8713 | 396.6594 | 361.7097
1231.6135 | 466.7333 | 417.8783 | 396.7586 | 361.7112
1232.6135 | 466.8086 | 417.9333 | 396.7221 | 362.7168
1233.6135 | 466.7261 | 417.9816 | 396.7832 | 362.7148
1234.6135 | 466.6808 | 418.0043 | 396.8144 | 362.9417
1235.6135 | 466.6186 | 418.0372 | 396.926 | 362.6829
1236.6135 | 466.5105 | 418.0476 | 396.9525 | 361.5997
1237.6135 | 466.4995 | 418.0959 | 396.8312 | 363.6733
1238.6135 | 466.3477 | 418.1406 | 396.903 | 365.7744
1239.6135 | 466.187 | 418.1754 | 396.8022 | 366.0977
1240.6135 | 466.0959 | 418.2339 | 396.973 | 365.9881
1241.6135 | 465.9749 | 418.2274 | 397.088 | 366.6324
1242.6135 | 466.0136 | 418.122 | 397.0869 | 368.4738
1243.6135 | 466.1018 | 418.2061 | 397.1231 | 368.0974
1244.6135 | 466.1056 | 418.2662 | 397.14 | 368.2188
1245.6135 | 466.1371 | 418.2289 | 397.2299 | 369.3733
1246.6135 | 466.1545 | 418.282 | 397.2911 | 369.425
1247.6135 | 466.2452 | 418.3909 | 397.4697 | 372.6743
1248.6135 | 466.4269 | 418.4238 | 397.6287 | 373.7109
1249.6135 | 466.5699 | 418.4485 | 397.6431 | 374.1862
1250.6135 | 466.6008 | 418.4673 | 397.5435 | 373.8299
1251.6135 | 466.5773 | 418.3473 | 397.558 | 373.8671
1252.6135 | 466.642 | 418.4513 | 397.6683 | 375.0333
1253.6135 | 466.8711 | 418.6016 | 397.6231 | 375.3248
1254.6135 | 467.0054 | 418.6439 | 397.6502 | 373.6694
1255.6135 | 467.0183 | 418.6784 | 397.29 | 377.7762
1256.6135 | 466.976 | 418.6027 | 397.5042 | 377.0022
1257.6135 | 467.0141 | 418.5965 | 397.7093 | 377.923
1258.6135 | 466.992 | 418.6382 | 397.7977 | 377.1388
1259.6135 | 467.0149 | 418.7382 | 397.8603 | 378.5092
1260.6135 | 467.1688 | 418.8242 | 397.7676 | 379.354
1261.6135 | 467.1612 | 418.7737 | 397.97 | 381.5197
1262.6135 | 467.1241 | 418.7864 | 398.1458 | 382.1984
1263.6135 | 467.1652 | 418.7667 | 398.1156 | 380.2991
1264.6135 | 467.0469 | 418.868 | 398.2822 | 381.686
1265.6135 | 467.1155 | 418.8961 | 398.3449 | 381.8423
1266.6135 | 467.0907 | 418.7927 | 398.4261 | 383.9883
1267.6135 | 467.033 | 418.9039 | 398.4355 | 382.6688
1268.6135 | 467.1118 | 419.0159 | 398.4667 | 380.9706
1269.6135 | 466.9869 | 419.0699 | 398.4785 | 381.241
1270.6135 | 466.8815 | 419.0632 | 398.6433 | 384.3202
1271.6135 | 466.8026 | 419.0708 | 398.5933 | 384.2639
1272.6135 | 466.7679 | 419.0679 | 398.6408 | 384.1096
1273.6135 | 466.6496 | 419.0867 | 398.6831 | 385.3541
1274.6604 | 466.5909 | 419.1865 | 398.7118 | 387.6455
1275.6135 | 466.5717 | 419.2657 | 398.8304 | 386.5201
1276.6135 | 466.4747 | 419.2451 | 398.7179 | 389.7343
1277.6135 | 466.3104 | 419.2831 | 398.7773 | 389.5391
1278.6135 | 466.2315 | 419.3134 | 398.7193 | 390.343
1279.6135 | 466.2349 | 419.2773 | 398.7534 | 391.3983
1280.6135 | 466.2655 | 419.3616 | 398.9445 | 391.376
1281.6135 | 466.4244 | 419.3838 | 398.9114 | 390.332
1282.6135 | 466.5066 | 419.3995 | 398.8951 | 391.6202
1283.6135 | 466.2908 | 419.3731 | 398.8722 | 391.9038
1284.6135 | 466.1901 | 419.3712 | 398.9258 | 397.6202
1285.6135 | 466.2461 | 419.4239 | 398.9522 | 396.6326
1286.6135 | 466.3317 | 419.477 | 398.9698 | 400.1947
1287.6135 | 466.2564 | 419.5319 | 398.9687 | 402.2683
1288.6135 | 466.208 | 419.5278 | 398.9623 | 401.5545
1289.6135 | 466.1997 | 419.5223 | 398.9712 | 402.822
1290.6135 | 466.3481 | 419.5617 | 399.0767 | 404.7485
1291.6135 | 466.3191 | 419.595 | 399.2388 | 404.4904
1292.6135 | 466.3735 | 419.65 | 399.1493 | 405.1939
1293.6135 | 466.3672 | 419.6458 | 399.264 | 405.4044
1294.6135 | 466.318 | 419.7163 | 399.3458 | 405.8944
1295.6135 | 466.3179 | 419.7322 | 399.2117 | 408.1929
1296.6135 | 466.3138 | 419.7559 | 399.4619 | 407.7815
1297.6135 | 466.2819 | 419.677 | 399.4573 | 409.3592
1298.6135 | 466.2701 | 419.6459 | 399.458 | 411.1737
1299.6135 | 466.3624 | 419.7717 | 399.5462 | 409.5678
1300.6135 | 466.3338 | 419.8306 | 399.5625 | 410.1395
1301.6135 | 466.1631 | 419.9345 | 399.6402 | 411.2445
1302.6135 | 465.9941 | 419.9338 | 399.7878 | 412.9085
1303.6135 | 465.974 | 419.9483 | 399.7966 | 410.6601
1304.6135 | 465.938 | 420.0056 | 399.6621 | 411.8626
1305.6135 | 465.8609 | 420.0566 | 399.6373 | 414.4723
1306.6135 | 465.762 | 420.0084 | 399.7607 | 415.6828
1307.6135 | 465.6837 | 420.0497 | 399.845 | 416.8393
1308.6135 | 465.7128 | 420.0816 | 399.8603 | 413.38
1309.6135 | 465.696 | 420.1461 | 399.9264 | 410.446
1310.6135 | 465.6917 | 420.1922 | 400.0348 | 410.355
1311.6135 | 465.6997 | 420.2389 | 400.0717 | 410.2059
1312.6135 | 465.5552 | 420.2874 | 399.8697 | 412.7311
1313.6135 | 465.4933 | 420.3248 | 400.0519 | 410.9061
1314.6135 | 465.5988 | 420.3167 | 399.9927 | 409.8762
1315.6135 | 465.6153 | 420.3631 | 400.1211 | 408.4417
1316.6135 | 465.6557 | 420.4175 | 400.0982 | 412.2114
1317.6135 | 465.7256 | 420.4338 | 400.055 | 412.5669
1318.6135 | 465.8433 | 420.4606 | 399.9947 | 411.5873
1319.6135 | 465.8878 | 420.4279 | 400.0211 | 411.883
1320.6135 | 465.8636 | 420.4783 | 400.1748 | 411.7278
1321.6135 | 465.8704 | 420.4686 | 400.2339 | 413.7684
1322.6135 | 465.869 | 420.458 | 400.2682 | 413.8511
1323.6135 | 465.8995 | 420.4901 | 400.2512 | 412.6661
1324.6135 | 465.9476 | 420.4887 | 400.3128 | 414.2191
1325.6135 | 465.9773 | 420.5277 | 400.1868 | 416.0564
1326.6135 | 466.1612 | 420.5428 | 400.3656 | 416.0447
1327.6135 | 466.2024 | 420.6222 | 400.5198 | 416.9561
1328.6135 | 466.256 | 420.6843 | 400.5039 | 414.3893
1329.6135 | 466.2804 | 420.7523 | 400.6492 | 413.3333
1330.6135 | 466.2857 | 420.7511 | 400.7968 | 414.4103
1331.6135 | 466.3488 | 420.7598 | 400.8179 | 413.7749
1332.6135 | 466.3902 | 420.7756 | 400.6106 | 414.9129
1333.6135 | 466.4604 | 420.8138 | 400.228 | 416.4491
1334.6135 | 466.6241 | 420.8588 | 400.5167 | 415.5172
1335.6135 | 466.715 | 420.8865 | 400.4379 | 419.0312
1336.6135 | 466.6667 | 420.9289 | 400.6167 | 417.0214
1337.6135 | 466.6212 | 420.995 | 400.7549 | 416.82
1338.6135 | 466.6606 | 420.9626 | 400.8228 | 418.8071
1339.6135 | 466.5571 | 421.0281 | 400.8554 | 417.9881
1340.6135 | 466.5004 | 421.0132 | 400.9218 | 419.6362
1341.6135 | 466.4916 | 421.0277 | 400.8667 | 419.8492
1342.6135 | 466.4362 | 421.0156 | 400.982 | 420.4566
1343.6135 | 466.4947 | 421.0507 | 401.0458 | 422.0344
1344.6135 | 466.4987 | 420.9974 | 401.185 | 421.0036
1345.6135 | 466.5559 | 421.1148 | 401.3177 | 420.0704
1346.6135 | 466.5252 | 421.139 | 401.332 | 424.9008
1347.6135 | 466.5406 | 421.1441 | 401.211 | 426.5025
1348.6135 | 466.5458 | 421.1993 | 401.2014 | 422.9167
1349.6135 | 466.4763 | 421.1524 | 401.3089 | 424.9806
1350.6135 | 466.5254 | 421.1416 | 401.3256 | 423.97
1351.6135 | 466.4794 | 421.2696 | 401.3333 | 420.5367
1352.6135 | 466.4048 | 421.2702 | 401.3479 | 422.5245
1353.6135 | 466.3661 | 421.2574 | 401.4058 | 419.6095
1354.6135 | 466.3381 | 421.2681 | 401.4775 | 421.525
1355.6135 | 466.2316 | 421.3471 | 401.5302 | 422.6368
1356.6135 | 466.2339 | 421.3323 | 401.4683 | 419.3296
1357.6135 | 466.1839 | 421.249 | 401.4855 | 416.5019
1358.6135 | 466.1141 | 421.2109 | 401.6183 | 414.9498
1359.6135 | 466.0809 | 421.163 | 401.7228 | 414.7975
1360.6135 | 465.9705 | 421.1684 | 401.7792 | 417.2917
1361.6135 | 465.8716 | 421.3085 | 401.7501 | 413.0551
1362.6135 | 465.8074 | 421.3604 | 401.753 | 415.5319
1363.6135 | 465.8347 | 421.3911 | 401.6884 | 412.3307
1364.6135 | 465.8643 | 421.4951 | 401.7272 | 414.7581
1365.6135 | 465.8828 | 421.5445 | 401.8251 | 413.5752
1366.6135 | 465.9104 | 421.6101 | 401.8801 | 413.9137
1367.6135 | 465.8649 | 421.6327 | 401.9452 | 414.5719
1368.6135 | 465.8882 | 421.6461 | 401.7601 | 414.9675
1369.6135 | 466.0152 | 421.6372 | 401.8169 | 415.3477
1370.6135 | 466.181 | 421.6974 | 401.9157 | 415.5614
1371.6135 | 466.2316 | 421.6624 | 401.9362 | 415.6753
1372.6135 | 466.2885 | 421.7045 | 402.0051 | 417.905
1373.6135 | 466.3234 | 421.7549 | 402.0373 | 418.4059
1374.6135 | 466.3367 | 421.8115 | 402.0724 | 415.0154
1375.6135 | 466.4192 | 421.8211 | 402.069 | 414.4508
1376.6135 | 466.4819 | 421.8244 | 402.1997 | 415.8264
1377.6135 | 466.3974 | 421.8797 | 402.2073 | 417.3504
1378.6135 | 466.2687 | 421.8692 | 402.2523 | 416.8914
1379.6135 | 466.2912 | 421.819 | 402.2578 | 417.0544
1380.6135 | 466.2522 | 421.9368 | 402.2001 | 417.3451
1381.6135 | 466.0894 | 421.871 | 402.2764 | 419.0105
1382.6135 | 466.0682 | 421.8534 | 402.3339 | 415.9089
1383.6135 | 466.077 | 421.9251 | 402.3687 | 420.4964
1384.6135 | 466.1199 | 421.9439 | 402.5132 | 419.9311
1385.6135 | 466.1581 | 421.9206 | 402.619 | 417.1784
1386.6135 | 466.1395 | 421.9954 | 402.6209 | 417.9453
1387.6135 | 466.1666 | 422.0548 | 402.5822 | 418.2355
1388.6135 | 466.2226 | 422.1006 | 402.6796 | 420.9808
1389.6135 | 466.1935 | 422.0294 | 402.7277 | 427.5191
1390.6135 | 466.0613 | 422.0909 | 402.7136 | 423.2607
1391.6135 | 465.9984 | 422.2001 | 402.6626 | 421.4866
1392.6135 | 466.0485 | 422.2401 | 402.5916 | 416.6324
1393.6135 | 466.0729 | 422.3079 | 402.6438 | 416.9653
1394.6135 | 466.1343 | 422.2678 | 402.7909 | 415.887
1395.6135 | 466.0605 | 422.2853 | 402.6928 | 417.9312
1396.6135 | 466.0742 | 422.2399 | 402.6801 | 420.1528
1397.6135 | 466.0652 | 422.2775 | 402.8678 | 418.4928
1398.6135 | 466.0115 | 422.3226 | 402.968 | 421.4359
1399.6135 | 466.0767 | 422.3622 | 403.0298 | 416.5022
1400.6135 | 466.1279 | 422.3761 | 402.9372 | 417.6521
1401.6135 | 466.2198 | 422.4042 | 402.8663 | 426.5247
1402.6135 | 466.1882 | 422.4754 | 402.9799 | 424.6857
1403.6135 | 466.1409 | 422.4445 | 402.9159 | 422.3432
1404.6135 | 466.2514 | 422.3786 | 403.0102 | 417.6994
1405.6135 | 466.3338 | 422.4293 | 403.1026 | 422.2618
1406.6135 | 466.3942 | 422.4592 | 403.1197 | 421.7496
1407.6135 | 466.4164 | 422.4845 | 403.1121 | 420.9406
1408.6135 | 466.43 | 422.5495 | 403.08 | 419.2625
1409.6135 | 466.4527 | 422.5657 | 403.0861 | 419.1427
1410.6135 | 466.43 | 422.4852 | 403.169 | 422.0537
1411.6135 | 466.4524 | 422.5737 | 403.3121 | 427.2235
1412.6135 | 466.3793 | 422.698 | 403.3473 | 426.7382
1413.6135 | 466.5494 | 422.7624 | 403.2949 | 424.8321
1414.6135 | 466.6114 | 422.7886 | 403.2901 | 425.3224
1415.6135 | 466.6937 | 422.7806 | 403.4645 | 425.6382
1416.6135 | 466.9 | 422.7897 | 403.5285 | 422.2777
1417.6135 | 466.9483 | 422.8394 | 403.6588 | 427.9393
1418.6135 | 466.9072 | 422.8842 | 403.7091 | 427.8344
1419.6135 | 466.9179 | 422.8967 | 403.5538 | 426.204
1420.6135 | 466.7395 | 422.894 | 403.473 | 422.1715
1421.6135 | 466.6406 | 422.8937 | 403.5156 | 423.4698
1422.6135 | 466.5646 | 422.9841 | 403.4933 | 431.0258
1423.6135 | 466.5941 | 423.0497 | 403.5615 | 435.8488
1424.6135 | 466.5887 | 423.0308 | 403.6685 | 429.6226
1425.6135 | 466.536 | 423.0963 | 403.5786 | 427.39
1426.6135 | 466.5359 | 423.143 | 403.6351 | 431.8445
1427.6135 | 466.5637 | 423.0462 | 403.726 | 433.669
1428.6135 | 466.6349 | 423.0739 | 403.8253 | 435.8588
1429.6135 | 466.6531 | 423.0815 | 403.9315 | 436.8558
1430.6135 | 466.634 | 423.1519 | 403.9225 | 431.341
1431.6135 | 466.6111 | 423.186 | 403.7876 | 432.3043
1432.6135 | 466.6842 | 423.2444 | 403.8135 | 431.9922
1433.6135 | 466.6878 | 423.3 | 403.927 | 431.5378
1434.6135 | 466.7177 | 423.2761 | 403.9112 | 433.1291
1435.6135 | 466.7241 | 423.3555 | 404.017 | 432.9396
1436.6135 | 466.8095 | 423.3778 | 403.9833 | 435.7587
1437.6135 | 466.8272 | 423.3869 | 404.0212 | 437.3426
1438.6135 | 466.8423 | 423.2881 | 404.0795 | 439.2666
1439.6135 | 466.7852 | 423.4021 | 404.1837 | 439.89
1440.6135 | 466.6624 | 423.3915 | 404.2715 | 444.3951
1441.6135 | 466.6927 | 423.3641 | 404.2953 | 443.7053
1442.6135 | 466.7735 | 423.4237 | 404.3528 | 442.413
1443.6135 | 466.771 | 423.3557 | 404.3589 | 440.5344
1444.6135 | 466.7783 | 423.4471 | 404.2679 | 439.1597
1445.6135 | 466.7725 | 423.5225 | 404.3584 | 434.9128
1446.6135 | 466.7819 | 423.535 | 404.4929 | 434.4124
1447.6135 | 466.7246 | 423.6004 | 404.4738 | 434.7091
1448.6135 | 466.6147 | 423.6484 | 404.5576 | 432.4371
1449.6135 | 466.5919 | 423.6237 | 404.555 | 432.372
1450.6135 | 466.589 | 423.7039 | 404.4756 | 433.1502
1451.6135 | 466.5905 | 423.7089 | 404.472 | 436.648
1452.6135 | 466.5807 | 423.7326 | 404.4904 | 434.0218
1453.6135 | 466.5557 | 423.7491 | 404.5937 | 434.1266
1454.6135 | 466.5462 | 423.8125 | 404.6207 | 430.7263
1455.6135 | 466.5194 | 423.8423 | 404.5383 | 439.1176
1456.6135 | 466.55 | 423.7868 | 404.4914 | 438.0941
1457.6135 | 466.4825 | 423.8061 | 404.4773 | 438.5197
1458.6135 | 466.4984 | 423.8614 | 404.6283 | 432.7039
1459.6135 | 466.5354 | 423.9267 | 404.5868 | 436.4979
1460.6135 | 466.4189 | 424.0009 | 404.6965 | 437.9008
1461.6135 | 466.4068 | 423.9534 | 404.7993 | 435.8709
1462.6135 | 466.4155 | 423.948 | 404.8552 | 438.3128
1463.6135 | 466.5123 | 423.9736 | 404.8028 | 435.7019
1464.6135 | 466.6599 | 423.9753 | 404.8316 | 440.4102
1465.6135 | 466.6768 | 424.0106 | 404.9481 | 441.4675
1466.6135 | 466.7292 | 424.0796 | 405.0491 | 442.4055
1467.6135 | 466.8027 | 424.0865 | 404.9246 | 442.936
1468.6135 | 466.8178 | 424.0339 | 404.9608 | 440.3501
1469.6135 | 466.7828 | 424.053 | 405.1031 | 436.5423
1470.6135 | 466.8578 | 424.0526 | 405.1139 | 438.506
1471.6135 | 466.9364 | 424.0568 | 404.8605 | 438.9492
1472.6135 | 467.0345 | 424.1185 | 405.0064 | 439.7661
1473.6135 | 467.1299 | 424.1672 | 405.1485 | 432.3827
1474.6135 | 466.9923 | 424.1374 | 405.1416 | 431.7764
1475.6135 | 466.9844 | 424.1981 | 405.3166 | 436.8931
1476.6135 | 467.0251 | 424.2447 | 405.3843 | 433.4033
1477.6135 | 467.0123 | 424.3165 | 405.3587 | 437.4608
1478.6135 | 466.9539 | 424.3218 | 405.3694 | 439.5299
1479.6135 | 466.8508 | 424.3693 | 405.3332 | 442.2397
1480.6135 | 466.9233 | 424.3848 | 405.4393 | 441.244
1481.6135 | 467.0669 | 424.4374 | 405.5552 | 445.4233
1482.6135 | 467.0358 | 424.427 | 405.6013 | 440.2499
1483.6135 | 467.0367 | 424.4663 | 405.6158 | 435.8509
1484.6135 | 467.0766 | 424.315 | 405.5641 | 439.6331
1485.6135 | 466.9808 | 424.4073 | 405.5855 | 440.7632
1486.6135 | 466.9874 | 424.4653 | 405.6575 | 442.8647
1487.6135 | 466.8382 | 424.5331 | 405.6637 | 443.102
1488.6135 | 466.7501 | 424.4715 | 405.7118 | 443.5393
1489.6135 | 466.7617 | 424.537 | 405.728 | 448.2118
1490.6135 | 466.6749 | 424.6053 | 405.6852 | 443.8871
1491.6135 | 466.6475 | 424.5972 | 405.506 | 443.7047
1492.6135 | 466.6094 | 424.6113 | 405.6448 | 444.0064
1493.6135 | 466.6687 | 424.6017 | 405.7322 | 441.6157
1494.6135 | 466.5996 | 424.6661 | 405.7846 | 450.1115
1495.6135 | 466.5792 | 424.7196 | 405.8004 | 449.2082
1496.6135 | 466.5588 | 424.7809 | 405.8377 | 447.8227
1497.6135 | 466.6832 | 424.8519 | 405.934 | 446.4555
1498.6135 | 466.764 | 424.8509 | 406.0363 | 448.8697
1499.6135 | 466.7101 | 424.731 | 406.082 | 448.8712
1500.6135 | 466.7922 | 424.7907 | 405.9956 | 444.8558
1501.6135 | 466.8595 | 424.8383 | 405.9804 | 443.474
1502.6135 | 466.818 | 424.862 | 406.0782 | 446.1933
1503.6135 | 466.8853 | 424.9115 | 406.1888 | 448.21
1504.6135 | 466.8974 | 424.9235 | 406.1653 | 452.638
1505.6135 | 466.7691 | 424.9558 | 406.2014 | 453.7928
1506.6135 | 466.7035 | 425.02 | 406.2366 | 447.957
1507.6135 | 466.6601 | 424.9648 | 406.195 | 446.8347
1508.6135 | 466.7593 | 425.0066 | 406.241 | 444.9731
1509.6135 | 466.831 | 425.022 | 406.2658 | 452.3765
1510.6135 | 466.9934 | 424.9804 | 406.3322 | 449.9214
1511.6135 | 467.0339 | 424.9447 | 406.3248 | 449.8858
1512.6135 | 467.1058 | 425.0215 | 406.3711 | 447.0517
1513.6135 | 467.0811 | 425.0462 | 406.5546 | 451.9233
1514.6135 | 466.9828 | 425.0539 | 406.402 | 452.2222
1515.6135 | 466.9457 | 424.9719 | 406.4613 | 450.4315
1516.6135 | 466.9574 | 425.0384 | 406.423 | 453.6055
1517.6135 | 466.9605 | 425.0851 | 406.5069 | 458.7716
1518.6135 | 466.8958 | 425.0773 | 406.6461 | 456.8422
1519.6135 | 466.8586 | 425.0958 | 406.7463 | 452.5256
1520.6135 | 466.8972 | 425.1152 | 406.7058 | 455.1503
1521.6135 | 466.9468 | 425.1866 | 406.7053 | 449.9564
1522.6135 | 466.9836 | 425.235 | 406.6525 | 456.805
1523.6135 | 466.9192 | 425.3408 | 406.6363 | 455.2735
1524.6135 | 466.8458 | 425.3904 | 406.582 | 450.8264
1525.6135 | 466.7514 | 425.3657 | 406.5991 | 450.3404
1526.6135 | 466.7285 | 425.4035 | 406.7421 | 458.8921
1527.6135 | 466.6561 | 425.4095 | 406.8379 | 457.4449
1528.6135 | 466.3928 | 425.4472 | 406.7989 | 460.145
1529.6135 | 466.3353 | 425.4602 | 406.9163 | 457.9032
1530.6135 | 466.2549 | 425.3912 | 406.9221 | 458.228
1531.6135 | 466.2138 | 425.3707 | 406.9419 | 456.1442
1532.6135 | 466.1964 | 425.4501 | 407.0359 | 457.2399
1533.6135 | 466.0997 | 425.4113 | 406.7898 | 455.6912
1534.6135 | 466.0954 | 425.4312 | 406.9518 | 453.9842
1535.6135 | 466.0706 | 425.446 | 407.0145 | 449.6568
1536.6135 | 466.1148 | 425.4939 | 407.2257 | 451.5475
1537.6135 | 466.1338 | 425.5302 | 407.2644 | 457.7097
1538.6135 | 466.3377 | 425.5246 | 407.2312 | 458.1935
1539.6135 | 466.4552 | 425.4953 | 407.1598 | 457.2852
1540.6135 | 466.4577 | 425.5119 | 407.1024 | 459.2374
1541.6135 | 466.6056 | 425.606 | 407.1666 | 455.5699
1542.6135 | 466.6441 | 425.6622 | 407.2568 | 455.1921
1543.6135 | 466.5953 | 425.688 | 407.2937 | 450.696
1544.6135 | 466.5072 | 425.6561 | 407.2033 | 450.2008
1545.6135 | 466.5082 | 425.7187 | 407.2085 | 452.2261
1546.6135 | 466.5651 | 425.6812 | 407.158 | 454.1617
1547.6135 | 466.5434 | 425.7076 | 407.2522 | 456.4479
1548.6135 | 466.4664 | 425.7481 | 407.2565 | 458.3772
1549.6135 | 466.4716 | 425.7501 | 407.238 | 457.0807
1550.6135 | 466.4576 | 425.7388 | 407.3124 | 456.136
1551.6135 | 466.5676 | 425.7306 | 407.3834 | 457.1176
1552.6135 | 466.5365 | 425.8539 | 407.4716 | 455.5017
1553.6135 | 466.5199 | 425.8763 | 407.6288 | 457.117
1554.6135 | 466.6215 | 425.8878 | 407.5846 | 458.5633
1555.6135 | 466.7602 | 425.8396 | 407.3893 | 461.6401
1556.6135 | 466.7159 | 425.8967 | 407.5175 | 461.3814
1557.6135 | 466.6715 | 425.8215 | 407.5933 | 459.4026
1558.6135 | 466.6307 | 425.8027 | 407.646 | 459.3501
1559.6135 | 466.613 | 425.8915 | 407.6515 | 460.0501
1560.6135 | 466.5053 | 425.8925 | 407.6727 | 457.2374
1561.6135 | 466.56 | 425.8811 | 407.7772 | 456.3359
1562.6135 | 466.607 | 425.9244 | 407.7103 | 453.2769
1563.6135 | 466.6459 | 425.9876 | 407.7409 | 454.1095
1564.6135 | 466.5957 | 425.9957 | 407.8032 | 453.1894
1565.6135 | 466.4784 | 426.0114 | 407.8425 | 456.6076
1566.6135 | 466.3406 | 426.0289 | 407.6031 | 460.7086
1567.6135 | 466.3036 | 426.0553 | 407.7486 | 459.6807
1568.6135 | 466.357 | 425.998 | 407.8218 | 458.4213
1569.6135 | 466.3426 | 426.0465 | 407.8496 | 458.4376
1570.6135 | 466.4195 | 426.0367 | 407.604 | 460.7748
1571.6135 | 466.3783 | 426.1619 | 407.5264 | 462.1225
1572.6135 | 466.439 | 426.118 | 407.7782 | 461.4196
1573.6135 | 466.4222 | 426.134 | 407.9726 | 460.8181
1574.6135 | 466.3801 | 426.1934 | 407.9412 | 460.984
1575.6135 | 466.2497 | 426.2169 | 407.9796 | 459.978
1576.6135 | 466.1309 | 426.2955 | 408.0565 | 457.787
1577.6135 | 466.0928 | 426.3033 | 407.9858 | 459.9937
1578.6135 | 466.0663 | 426.2729 | 407.7994 | 460.4594
1579.6135 | 466.0587 | 426.3257 | 408.0089 | 459.6076
1580.6135 | 466.1152 | 426.2578 | 408.1295 | 458.9058
1581.6135 | 466.1739 | 426.3232 | 408.1165 | 458.3115
1582.6135 | 466.2081 | 426.3881 | 407.8923 | 458.6846
1583.6135 | 466.2272 | 426.4909 | 407.9392 | 458.3107
1584.6135 | 466.2111 | 426.5045 | 407.7257 | 457.402
1585.6135 | 466.318 | 426.5614 | 407.8848 | 457.9434
1586.6135 | 466.3438 | 426.5993 | 408.0296 | 456.9456
1587.6135 | 466.4329 | 426.6602 | 407.9846 | 458.6327
1588.6135 | 466.5102 | 426.7032 | 408.1056 | 459.8064
1589.6135 | 466.7343 | 426.7054 | 408.1547 | 462.0043
1590.6135 | 466.7196 | 426.7482 | 408.2852 | 461.5284
1591.6135 | 466.6893 | 426.772 | 408.4005 | 463.4133
1592.6135 | 466.8499 | 426.7471 | 408.4952 | 464.6883
1593.6135 | 466.8684 | 426.7553 | 408.5701 | 461.5451
1594.6135 | 466.893 | 426.7795 | 408.3604 | 459.8015
1595.6135 | 466.9606 | 426.7721 | 408.5794 | 460.2244
1596.6135 | 467.0824 | 426.8929 | 408.538 | 462.4404
1597.6135 | 467.2409 | 426.9206 | 408.6301 | 467.5023
1598.6135 | 467.2684 | 426.9583 | 408.5088 | 465.974
1599.6135 | 467.2583 | 426.9234 | 408.3257 | 466.06
1600.6135 | 467.2825 | 427.0017 | 408.5323 | 462.3052
1601.6135 | 467.3008 | 427.0581 | 408.68 | 464.0881
1602.6135 | 467.3243 | 427.0983 | 408.7167 | 465.6871
1603.6135 | 467.2857 | 427.1153 | 408.7502 | 465.3404
1604.6135 | 467.2787 | 427.1948 | 408.697 | 464.1614
1605.6135 | 467.1101 | 427.1514 | 408.7993 | 461.3795
1606.6135 | 466.9804 | 427.2222 | 408.9682 | 460.6968
1607.6135 | 466.9132 | 427.2732 | 409.0051 | 461.3277
1608.6135 | 466.86 | 427.2661 | 409.0912 | 462.8595
1609.6135 | 466.661 | 427.3149 | 409.0208 | 463.1148
1610.6135 | 466.6596 | 427.4404 | 408.9497 | 461.3809
1611.6135 | 466.6567 | 427.4358 | 408.9223 | 461.5059
1612.6135 | 466.65 | 427.5163 | 408.9332 | 463.4181
1613.6135 | 466.7614 | 427.5402 | 409.0644 | 464.7299
1614.6135 | 466.7473 | 427.6183 | 409.0928 | 467.6392
1615.6135 | 466.7558 | 427.5605 | 408.8685 | 464.9183
1616.6135 | 466.8714 | 427.5046 | 408.7613 | 465.1872
1617.6135 | 466.7676 | 427.5979 | 408.8898 | 463.7225
1618.6135 | 466.6449 | 427.6707 | 408.7523 | 466.2303
1619.6135 | 466.7031 | 427.741 | 408.8903 | 466.229
1620.6135 | 466.7717 | 427.7674 | 408.9734 | 464.0345
1621.6135 | 466.8838 | 427.8057 | 409.0964 | 464.198
1622.6135 | 466.8632 | 427.8233 | 409.179 | 465.207
1623.6135 | 466.8647 | 427.8028 | 409.2454 | 466.7164
1624.6135 | 466.9579 | 427.8499 | 408.9755 | 465.2491
1625.6135 | 466.9636 | 427.895 | 409.1821 | 465.2128
1626.6135 | 466.9816 | 427.9086 | 409.3118 | 464.2439
1627.6135 | 467.0855 | 427.8667 | 409.2546 | 464.9794
1628.6135 | 467.2214 | 427.9253 | 409.2502 | 464.0672
1629.6135 | 467.3318 | 427.976 | 409.4236 | 464.6677
1630.6135 | 467.3442 | 428.0183 | 409.4558 | 465.4699
1631.6135 | 467.3984 | 428.0814 | 409.5153 | 462.8886
1632.6135 | 467.2602 | 428.1737 | 409.3926 | 460.648
1633.6135 | 467.1974 | 428.2106 | 409.4547 | 462.169
1634.6135 | 467.1435 | 428.1726 | 409.5849 | 462.0283
1635.6135 | 467.0517 | 428.2385 | 409.4914 | 461.9997
1636.6135 | 466.9582 | 428.2787 | 409.5486 | 461.2139
1637.6135 | 466.9984 | 428.3411 | 409.6444 | 461.7967
1638.6135 | 466.8629 | 428.3887 | 409.615 | 464.9206
1639.6135 | 466.6886 | 428.4297 | 409.4397 | 465.5232
1640.6135 | 466.6882 | 428.4446 | 409.4355 | 463.9657
1641.6135 | 466.7215 | 428.4299 | 409.5092 | 463.7
1642.6135 | 466.8436 | 428.4977 | 409.5594 | 465.2736
1643.6135 | 466.803 | 428.553 | 409.6196 | 466.1958
1644.6135 | 466.7142 | 428.5406 | 409.6998 | 465.4217
1645.6135 | 466.8108 | 428.643 | 409.6595 | 467.2241
1646.6135 | 466.9136 | 428.6502 | 409.5975 | 468.0311
1647.6135 | 467.014 | 428.702 | 409.6194 | 469.6348
1648.6135 | 467.0546 | 428.7891 | 409.6697 | 468.2696
1649.6135 | 467.1624 | 428.8543 | 409.6927 | 465.4683
1650.6135 | 467.1959 | 428.9408 | 409.8194 | 465.8571
1651.6135 | 467.131 | 429.0224 | 409.8362 | 466.5405
1652.6135 | 467.1234 | 429.0278 | 409.8184 | 467.643
1653.6135 | 467.154 | 429.0551 | 409.8415 | 468.6103
1654.6135 | 467.1474 | 429.0715 | 410.0301 | 468.9763
1655.6135 | 467.1066 | 429.1182 | 410.0851 | 473.2838
1656.6135 | 467.1375 | 429.2118 | 410.049 | 473.9141
1657.6135 | 467.1632 | 429.2008 | 409.883 | 472.6563
1658.6135 | 467.2576 | 429.2416 | 409.9465 | 471.6518
1659.6135 | 467.2482 | 429.3685 | 409.8716 | 471.0486
1660.6135 | 467.2164 | 429.4351 | 410.067 | 473.4153
1661.6135 | 467.2193 | 429.4424 | 410.0585 | 471.3946
1662.6135 | 467.3557 | 429.4297 | 410.069 | 470.9451
1663.6135 | 467.411 | 429.5205 | 409.9795 | 471.0592
1664.6135 | 467.3595 | 429.5419 | 410.1562 | 473.3629
1665.6135 | 467.3256 | 429.5525 | 410.1921 | 471.6397
1666.6135 | 467.2964 | 429.6374 | 409.9926 | 473.0937
1667.6135 | 467.3771 | 429.7723 | 410.1092 | 470.0254
1668.6135 | 467.3523 | 429.8023 | 410.1686 | 474.2821
1669.6135 | 467.2787 | 429.8396 | 410.3488 | 476.0119
1670.6135 | 467.1698 | 429.9159 | 410.2547 | 476.2379
1671.6135 | 467.1856 | 429.9407 | 410.3536 | 474.1997
1672.6135 | 467.1988 | 429.9985 | 410.371 | 474.2908
1673.6135 | 467.1047 | 430.0573 | 410.3623 | 474.1868
1674.6135 | 467.1245 | 430.143 | 410.2881 | 473.8334
1675.6135 | 467.1233 | 430.1404 | 410.2362 | 472.5709
1676.6135 | 467.156 | 430.1047 | 410.3852 | 473.6065
1677.6135 | 467.2138 | 430.1343 | 410.4524 | 473.154
1678.6135 | 467.2231 | 430.1137 | 409.9915 | 474.6658
1679.6135 | 467.2969 | 430.2346 | 409.8248 | 472.6384
1680.6135 | 467.2733 | 430.1419 | 409.7154 | 472.1375
1681.6135 | 467.2058 | 430.2585 | 410.0362 | 471.6596
1682.6135 | 467.081 | 430.3247 | 410.2269 | 471.8705
1683.6135 | 467.0043 | 430.3387 | 410.3076 | 472.2165
1684.6135 | 466.9719 | 430.3837 | 410.3503 | 471.5496
1685.6135 | 466.9945 | 430.3913 | 410.3611 | 472.3469
1686.6135 | 467.0444 | 430.4151 | 410.2649 | 473.4388
1687.6135 | 467.0381 | 430.5398 | 410.3858 | 474.368
1688.6135 | 467.028 | 430.609 | 410.3858 | 475.2168
1689.6135 | 467.1197 | 430.6112 | 410.2281 | 475.6529
1690.6135 | 467.1862 | 430.6757 | 410.4882 | 475.578
1691.6135 | 467.2299 | 430.74 | 410.4489 | 473.9625
1692.6135 | 467.1586 | 430.7892 | 410.5605 | 473.3834
1693.6135 | 467.1427 | 430.8008 | 410.5724 | 474.7922
1694.6135 | 467.2324 | 430.9129 | 410.709 | 474.7436
1695.6135 | 467.3475 | 430.9573 | 410.8105 | 475.2135
1696.6135 | 467.327 | 430.9765 | 410.5966 | 475.314
1697.6135 | 467.3526 | 431.0647 | 410.6663 | 475.803
1698.6135 | 467.3825 | 431.0874 | 410.8299 | 476.7435
1699.6135 | 467.4031 | 431.1603 | 410.9454 | 475.4359
1700.6135 | 467.4082 | 431.0777 | 411.0417 | 475.2094
1701.6135 | 467.2826 | 431.141 | 411.2256 | 475.579
1702.6135 | 467.2485 | 431.131 | 411.2895 | 473.894
1703.6135 | 467.2849 | 431.2254 | 411.1756 | 473.8177
1704.6135 | 467.2567 | 431.3467 | 411.143 | 472.6278
1705.6135 | 467.2012 | 431.4287 | 411.0021 | 473.6637
1706.6135 | 467.2372 | 431.492 | 411.0408 | 473.0546
1707.6135 | 467.3325 | 431.5193 | 411.0291 | 475.8457
1708.6135 | 467.3749 | 431.4977 | 411.0587 | 474.9755
1709.6135 | 467.2742 | 431.5568 | 411.2939 | 476.7758
1710.6135 | 467.2565 | 431.6629 | 411.387 | 476.1236
1711.6135 | 467.2983 | 431.6398 | 411.4101 | 477.3544
1712.6135 | 467.27 | 431.6999 | 411.3032 | 477.7148
1713.6135 | 467.2617 | 431.7104 | 411.3763 | 478.3391
1714.6135 | 467.169 | 431.7853 | 411.3995 | 479.3827
1715.6135 | 467.0979 | 431.8337 | 411.5495 | 478.3339
1716.6135 | 467.0538 | 431.8701 | 411.6163 | 475.3922
1717.6135 | 466.983 | 431.9335 | 411.4533 | 478.0571
1718.6135 | 467.0375 | 431.959 | 411.5365 | 479.6111
1719.6135 | 467.0756 | 432.0753 | 411.5435 | 479.0913
1720.6135 | 467.1123 | 432.1162 | 411.2902 | 480.6866
1721.6135 | 467.0781 | 432.0722 | 411.3804 | 481.3104
1722.6135 | 467.1132 | 432.1652 | 411.6002 | 481.1413
1723.6135 | 467.1415 | 432.1997 | 411.7102 | 480.9545
1724.6135 | 467.0935 | 432.1623 | 411.8092 | 481.6112
1725.6135 | 467.0131 | 432.2529 | 411.7514 | 480.6035
1726.6135 | 466.8797 | 432.3354 | 411.8119 | 482.0206
1727.6135 | 466.7899 | 432.2866 | 411.9235 | 482.1218
1728.6135 | 466.8242 | 432.3775 | 411.9262 | 482.4165
1729.6135 | 466.8276 | 432.3669 | 411.9082 | 482.3965
1730.6135 | 466.7719 | 432.4912 | 411.9482 | 483.0778
1731.6135 | 466.713 | 432.4652 | 412.1362 | 484.4486
1732.6135 | 466.7138 | 432.4978 | 412.2449 | 483.9453
1733.6135 | 466.757 | 432.5064 | 412.3086 | 484.3353
1734.6135 | 466.7458 | 432.4233 | 412.3174 | 484.9561
1735.6135 | 466.8073 | 432.4999 | 412.3007 | 484.3361
1736.6135 | 466.8847 | 432.6529 | 412.1325 | 485.3562
1737.6135 | 466.841 | 432.6451 | 412.2997 | 485.7693
1738.6135 | 466.9002 | 432.7392 | 412.3113 | 486.7877
1739.6135 | 466.9722 | 432.8887 | 412.4038 | 486.9528
1740.6135 | 466.8682 | 432.9131 | 412.4086 | 484.6085
1741.6135 | 466.7784 | 433.0009 | 412.2592 | 486.186
1742.6135 | 466.9169 | 433.0493 | 412.1966 | 483.5754
1743.6135 | 467.06 | 433.0551 | 412.3781 | 483.0903
1744.6135 | 467.0858 | 433.0393 | 412.4289 | 484.4659
1745.6135 | 467.1579 | 433.1297 | 412.4732 | 485.8961
1746.6135 | 467.1684 | 433.1857 | 412.5167 | 486.5763
1747.6135 | 467.2012 | 433.2268 | 412.442 | 486.5208
1748.6135 | 467.223 | 433.2594 | 412.4553 | 486.4924
1749.6135 | 467.3623 | 433.319 | 412.3761 | 487.1512
1750.6135 | 467.408 | 433.3402 | 412.5488 | 487.7446
1751.6135 | 467.4626 | 433.3894 | 412.6132 | 489.8714
1752.6135 | 467.5143 | 433.4573 | 412.5575 | 488.7764
1753.6135 | 467.4986 | 433.5041 | 412.5894 | 487.2502
1754.6135 | 467.6532 | 433.595 | 412.5528 | 486.6392
1755.6135 | 467.9748 | 433.6513 | 412.7322 | 487.247
1756.6135 | 468.0987 | 433.6758 | 412.8078 | 486.7326
1757.6135 | 468.1477 | 433.7182 | 412.8388 | 484.7469
1758.6135 | 468.214 | 433.7501 | 412.8223 | 486.0159
1759.6135 | 468.3179 | 433.843 | 412.6296 | 486.6036
1760.6135 | 468.4209 | 433.9081 | 412.6538 | 486.4753
1761.6135 | 468.3418 | 433.9763 | 412.7084 | 487.7526
1762.6135 | 468.3835 | 434.0055 | 412.9443 | 487.8161
1763.6135 | 468.3349 | 434.044 | 413.0314 | 488.5451
1764.6135 | 468.309 | 434.0206 | 412.9031 | 487.6569
1765.6135 | 468.4195 | 434.059 | 413.0063 | 488.9368
1766.6135 | 468.4621 | 434.0924 | 412.8977 | 487.8994
1767.6135 | 468.5818 | 434.2023 | 413.0483 | 487.2236
1768.6135 | 468.6833 | 434.2071 | 413.2218 | 487.3827
1769.6135 | 468.638 | 434.2113 | 413.4015 | 487.4519
1770.6135 | 468.7222 | 434.2459 | 413.4014 | 488.5271
1771.6135 | 468.71 | 434.2388 | 413.3611 | 490.0141
1772.6135 | 468.6887 | 434.2488 | 413.5016 | 490.0629
1773.6135 | 468.6253 | 434.3209 | 413.5155 | 490.4007
1774.6135 | 468.5103 | 434.3853 | 413.6285 | 490.3716
1775.6135 | 468.3376 | 434.4986 | 413.6889 | 490.4482
1776.6135 | 468.2284 | 434.5075 | 413.6285 | 492.0382
1777.6135 | 468.1686 | 434.5757 | 413.7546 | 490.5621
1778.6135 | 467.9892 | 434.6108 | 413.8279 | 490.938
1779.6135 | 467.9429 | 434.7232 | 413.6276 | 490.9176
1780.6135 | 467.8271 | 434.6937 | 413.7025 | 490.9051
1781.6135 | 467.5647 | 434.7774 | 413.8108 | 490.8968
1782.6135 | 467.4769 | 434.8041 | 413.8674 | 491.7426
1783.6135 | 467.3842 | 434.8363 | 413.9566 | 490.5574
1784.6135 | 467.3982 | 434.9102 | 413.9675 | 491.1538
1785.6135 | 467.4423 | 435.0197 | 414.0299 | 490.3034
1786.6135 | 467.3251 | 435.039 | 414.0275 | 488.8035
1787.6135 | 467.4052 | 435.0342 | 413.9912 | 489.3677
1788.6135 | 467.4272 | 435.0595 | 414.099 | 488.9825
1789.6135 | 467.3835 | 435.148 | 414.1901 | 487.5034
1790.6135 | 467.3212 | 435.2479 | 414.1784 | 488.2543
1791.6135 | 467.2982 | 435.3192 | 414.226 | 489.8191
1792.6135 | 467.1558 | 435.3093 | 414.3034 | 488.3744
1793.6135 | 467.0387 | 435.3991 | 414.3788 | 487.5509
1794.6135 | 466.9498 | 435.422 | 414.3041 | 487.8019
1795.6135 | 466.9807 | 435.4697 | 414.2379 | 487.173
1796.6135 | 467.0444 | 435.4571 | 414.1984 | 490.577
1797.6135 | 466.9429 | 435.553 | 414.1476 | 489.8073
1798.6135 | 466.8845 | 435.5835 | 414.2665 | 488.9668
1799.6135 | 466.8769 | 435.6916 | 414.3039 | 489.793
1800.6135 | 466.9197 | 435.7373 | 414.3507 | 489.0272
1801.6135 | 466.9488 | 435.7726 | 414.5131 | 488.9191
1802.6135 | 466.9088 | 435.8637 | 414.5144 | 488.4773
1803.6135 | 466.7882 | 435.9671 | 414.589 | 487.3002
1804.6135 | 466.785 | 435.9832 | 414.4789 | 488.148
1805.6135 | 466.9035 | 435.9583 | 414.5892 | 487.7614
1806.6135 | 466.9769 | 436.0185 | 414.7001 | 487.6445
1807.6135 | 466.9504 | 436.0063 | 414.655 | 487.5473
1808.6135 | 466.9812 | 436.0386 | 414.7232 | 487.7556
1809.6135 | 467.0431 | 435.995 | 414.7665 | 488.7067
1810.6135 | 467.0879 | 436.0649 | 414.8121 | 487.4946
1811.6135 | 467.1143 | 436.1036 | 414.8157 | 486.3912
1812.6135 | 467.1186 | 436.2289 | 414.8018 | 487.7502
1813.6135 | 467.1301 | 436.2037 | 414.9035 | 489.3296
1814.6135 | 467.0565 | 436.2353 | 415.0046 | 489.5028
1815.6135 | 467.1298 | 436.2881 | 414.9778 | 488.6018
1816.6135 | 467.2682 | 436.3744 | 415.0386 | 487.8132
1817.6135 | 467.3532 | 436.3154 | 414.9264 | 487.0888
1818.6135 | 467.2851 | 436.4236 | 414.9182 | 488.1021
1819.6135 | 467.1653 | 436.5351 | 414.828 | 488.8361
1820.6135 | 467.1842 | 436.605 | 414.9585 | 489.805
1821.6135 | 467.2425 | 436.6196 | 415.0237 | 489.1093
1822.6135 | 467.216 | 436.6529 | 415.1312 | 488.7603
1823.6135 | 467.2309 | 436.7321 | 415.1922 | 488.4792
1824.6135 | 467.1775 | 436.7324 | 415.2806 | 487.8535
1825.6135 | 467.1678 | 436.8338 | 415.4161 | 487.7632
1826.6135 | 467.1274 | 436.8431 | 415.2107 | 489.145
1827.6135 | 467.0636 | 436.928 | 415.1276 | 490.6757
1828.6135 | 467.1063 | 436.9456 | 415.3378 | 493.6419
1829.6135 | 467.107 | 436.8602 | 415.4231 | 489.9497
1830.6135 | 467.0947 | 436.9772 | 415.5056 | 489.4957
1831.6135 | 467.0578 | 437.0389 | 415.5094 | 488.0071
1832.6135 | 467.0674 | 437.0802 | 415.5537 | 488.6825
1833.6135 | 466.9945 | 437.118 | 415.5231 | 488.9444
1834.6135 | 466.9625 | 437.1209 | 415.5332 | 487.9815
1835.6135 | 466.9013 | 437.2328 | 415.7604 | 489.2637
1836.6135 | 466.9785 | 437.293 | 415.8093 | 488.8283
1837.6135 | 467.0183 | 437.3323 | 415.7869 | 488.7127
1838.6135 | 467.0332 | 437.3986 | 415.8313 | 488.1924
1839.6135 | 467.1387 | 437.4784 | 415.9362 | 487.2452
1840.6135 | 467.1732 | 437.4877 | 415.9631 | 488.0956
1841.6135 | 467.2851 | 437.4724 | 415.9784 | 487.2206
1842.6135 | 467.3393 | 437.5068 | 415.9875 | 486.6255
1843.6135 | 467.4134 | 437.5657 | 415.9583 | 487.2289
1844.6135 | 467.3897 | 437.6242 | 415.9298 | 487.5558
1845.6135 | 467.2771 | 437.5644 | 415.9877 | 486.8539
1846.6135 | 467.274 | 437.6231 | 416.1266 | 486.7351
1847.6135 | 467.2812 | 437.6442 | 416.1126 | 485.5599
1848.6135 | 467.212 | 437.7726 | 416.071 | 484.9694
1849.6135 | 467.176 | 437.8309 | 415.9751 | 486.0196
1850.6135 | 467.1542 | 437.8139 | 416.0923 | 486.0111
1851.6135 | 467.2078 | 437.8433 | 416.2182 | 486.3134
1852.6135 | 467.2418 | 437.9261 | 416.0748 | 485.8539
1853.6135 | 467.1563 | 437.8712 | 416.2372 | 484.1202
1854.6135 | 467.1843 | 437.9598 | 416.4063 | 483.9995
1855.6135 | 467.0986 | 438.0108 | 416.5551 | 484.5572
1856.6135 | 467.0446 | 438.0994 | 416.2447 | 485.2862
1857.6135 | 467.2272 | 438.1899 | 416.3526 | 486.0012
1858.6135 | 467.3008 | 438.2189 | 416.4744 | 485.736
1859.6135 | 467.2737 | 438.2829 | 416.319 | 486.0229
1860.6135 | 467.3129 | 438.3466 | 416.4318 | 486.0814
1861.6135 | 467.3318 | 438.3766 | 416.4817 | 485.3049
1862.6135 | 467.2859 | 438.4223 | 416.5884 | 485.2328
1863.6135 | 467.3434 | 438.3619 | 416.5035 | 485.4269
1864.6135 | 467.4198 | 438.4608 | 416.5987 | 485.6154
1865.6135 | 467.3029 | 438.4415 | 416.6686 | 486.9337
1866.6135 | 467.234 | 438.4642 | 416.6581 | 486.7378
1867.6135 | 467.1774 | 438.5363 | 416.7749 | 486.1417
1868.6135 | 467.0614 | 438.6044 | 416.7613 | 486.4697
1869.6135 | 467.1184 | 438.6581 | 416.8366 | 485.9559
1870.6135 | 467.115 | 438.7282 | 416.8972 | 486.2956
1871.6135 | 467.0844 | 438.6051 | 416.9219 | 486.8727
1872.6135 | 467.0487 | 438.5907 | 417.0264 | 486.5005
1873.6135 | 467.0488 | 438.7651 | 417.1152 | 486.7735
1874.6135 | 466.9305 | 438.8192 | 417.2033 | 485.2348
1875.6135 | 466.8784 | 438.8244 | 417.229 | 485.9261
1876.6135 | 466.9252 | 438.887 | 417.1827 | 487.0073
1877.6135 | 466.9808 | 438.8494 | 417.1961 | 487.1389
1878.6135 | 466.9861 | 438.8138 | 417.2409 | 486.1111
1879.6135 | 467.0471 | 438.9097 | 417.2492 | 485.7764
1880.6135 | 466.9843 | 438.9453 | 417.2812 | 487.2746
1881.6135 | 466.9462 | 439.0586 | 417.3638 | 487.2695
1882.6135 | 466.8645 | 439.1203 | 417.4175 | 487.5071
1883.6135 | 466.9043 | 439.098 | 417.4637 | 487.4692
1884.6135 | 466.958 | 439.0647 | 417.4844 | 487.4689
1885.6135 | 466.8969 | 439.1132 | 417.485 | 486.9931
1886.6135 | 466.7978 | 439.1209 | 417.5588 | 487.6768
1887.6135 | 466.7714 | 439.1885 | 417.6194 | 487.7823
1888.6135 | 466.7527 | 439.2473 | 417.5758 | 488.5351
1889.6135 | 466.6912 | 439.2613 | 417.6076 | 488.0722
1890.6135 | 466.837 | 439.3219 | 417.6211 | 488.1202
1891.6135 | 466.8419 | 439.3575 | 417.7469 | 488.0599
1892.6135 | 466.832 | 439.4093 | 417.6729 | 488.6873
1893.6135 | 466.674 | 439.3325 | 417.6524 | 488.3191
1894.6135 | 466.5719 | 439.4421 | 417.7939 | 485.948
1895.6135 | 466.5225 | 439.5049 | 417.8046 | 485.4453
1896.6135 | 466.4608 | 439.5946 | 417.6876 | 484.8767
1897.6135 | 466.4743 | 439.5279 | 417.8092 | 486.4443
1898.6135 | 466.5073 | 439.5887 | 417.9799 | 485.128
1899.6135 | 466.4922 | 439.6238 | 418.057 | 486.3473
1900.6135 | 466.4708 | 439.5673 | 417.9122 | 485.552
1901.6135 | 466.4516 | 439.6269 | 417.975 | 486.7939
1902.6135 | 466.3077 | 439.7053 | 418.0898 | 486.8188
1903.6135 | 466.2375 | 439.7458 | 418.0479 | 487.2493
1904.6135 | 466.1441 | 439.7864 | 418.0934 | 487.6478
1905.6135 | 466.2316 | 439.8348 | 418.1235 | 487.034
1906.6135 | 466.3793 | 439.9013 | 418.2848 | 486.9633
1907.6135 | 466.4014 | 439.9158 | 418.3604 | 487.4515
1908.6135 | 466.4747 | 439.9405 | 418.3428 | 488.0398
1909.6135 | 466.5082 | 439.9808 | 418.2146 | 487.2317
1910.6135 | 466.5496 | 440.0693 | 418.289 | 486.6139
1911.6135 | 466.5954 | 440.1171 | 418.4318 | 487.6964
1912.6135 | 466.6396 | 440.0346 | 418.4024 | 487.588
1913.6135 | 466.5421 | 440.0784 | 418.4885 | 488.7914
1914.6135 | 466.5233 | 440.1101 | 418.3637 | 488.2624
1915.6135 | 466.4983 | 440.135 | 418.3621 | 487.5297
1916.6135 | 466.4824 | 440.1815 | 418.2492 | 486.5507
1917.6135 | 466.5713 | 440.1818 | 418.3689 | 486.9894
1918.6135 | 466.5464 | 440.1967 | 418.5017 | 486.606
1919.6135 | 466.5092 | 440.2682 | 418.5941 | 486.8903
1920.6135 | 466.4729 | 440.2916 | 418.6701 | 487.2192
1921.6135 | 466.4206 | 440.3603 | 418.5776 | 487.5087
1922.6135 | 466.4121 | 440.3248 | 418.542 | 486.9073
1923.6135 | 466.397 | 440.3295 | 418.6959 | 487.2319
1924.6135 | 466.3372 | 440.4106 | 418.756 | 486.2516
1925.6135 | 466.295 | 440.4004 | 418.8014 | 485.9023
1926.6135 | 466.3444 | 440.4241 | 418.8858 | 486.9051
1927.6135 | 466.394 | 440.453 | 418.918 | 485.6183
1928.6135 | 466.4173 | 440.5292 | 418.801 | 486.6129
1929.6135 | 466.2859 | 440.5649 | 418.7857 | 486.942
1930.6135 | 466.2479 | 440.5879 | 418.8408 | 486.6547
1931.6135 | 466.2608 | 440.5837 | 418.9121 | 486.9081
1932.6135 | 466.2777 | 440.6579 | 418.8454 | 486.5801
1933.6135 | 466.3866 | 440.7047 | 418.8842 | 485.8796
1934.6135 | 466.4109 | 440.7496 | 418.9959 | 486.6528
1935.6135 | 466.3903 | 440.751 | 419.1464 | 486.7356
1936.6135 | 466.3775 | 440.8144 | 418.9886 | 486.0784
1937.6135 | 466.4185 | 440.9145 | 418.7654 | 486.3928
1938.6135 | 466.348 | 440.9443 | 418.9037 | 486.4114
1939.6135 | 466.3531 | 440.9283 | 419.028 | 486.1636
1940.6135 | 466.3077 | 440.8458 | 419.1508 | 486.0079
1941.6135 | 466.2942 | 440.8072 | 419.1945 | 486.1141
1942.6135 | 466.2222 | 440.968 | 419.2658 | 486.9056
1943.6135 | 466.2661 | 441.0057 | 419.2575 | 486.6436
1944.6135 | 466.3099 | 440.9984 | 419.158 | 486.2827
1945.6135 | 466.3849 | 441.0582 | 419.2896 | 486.9089
1946.6135 | 466.3177 | 441.1018 | 419.3274 | 486.7312
1947.6135 | 466.3166 | 441.016 | 419.3271 | 486.4424
1948.6135 | 466.3034 | 441.0999 | 419.139 | 487.1298
1949.6135 | 466.3736 | 441.1594 | 419.2949 | 486.9997
1950.6135 | 466.4277 | 441.2222 | 419.4264 | 486.1704
1951.6135 | 466.5402 | 441.2279 | 419.2374 | 486.5341
1952.6135 | 466.5921 | 441.3007 | 419.3419 | 487.5128
1953.6135 | 466.6185 | 441.3232 | 419.3967 | 485.778
1954.6135 | 466.5603 | 441.3198 | 419.504 | 485.1691
1955.6135 | 466.683 | 441.3847 | 419.5008 | 486.0206
1956.6135 | 466.73 | 441.4893 | 419.5137 | 486.569
1957.6135 | 466.6866 | 441.5251 | 419.5343 | 486.6958
1958.6135 | 466.7264 | 441.4411 | 419.619 | 487.3466
1959.6135 | 466.7988 | 441.5509 | 419.7586 | 486.8929
1960.6135 | 466.7467 | 441.6676 | 419.8257 | 487.1383
1961.6135 | 466.8266 | 441.6977 | 419.8332 | 486.6155
1962.6135 | 466.7461 | 441.6471 | 419.8368 | 486.9598
1963.6135 | 466.653 | 441.5783 | 419.9943 | 486.4959
1964.6135 | 466.7081 | 441.6512 | 419.9335 | 487.1432
1965.6135 | 466.7348 | 441.7476 | 419.9193 | 488.2691
1966.6135 | 466.6837 | 441.8395 | 420.0018 | 487.7811
1967.6135 | 466.5946 | 441.8645 | 419.9221 | 487.136
1968.6135 | 466.574 | 441.9121 | 419.921 | 487.0416
1969.6135 | 466.5734 | 441.9657 | 420.0722 | 486.6182
1970.6135 | 466.5336 | 442.0472 | 420.1346 | 486.2834
1971.6135 | 466.5082 | 442.0068 | 420.2117 | 485.9198
1972.6135 | 466.3779 | 442.1021 | 420.1792 | 486.2164
1973.6135 | 466.306 | 442.1164 | 420.0472 | 486.3687
1974.6135 | 466.4233 | 442.1442 | 419.7943 | 486.9038
1975.6135 | 466.4499 | 442.1207 | 419.8902 | 486.8263
1976.6135 | 466.5741 | 442.0498 | 419.9973 | 487.1145
1977.6135 | 466.5931 | 442.1449 | 420.1519 | 487.6889
1978.6135 | 466.516 | 442.1921 | 420.2339 | 487.6547
1979.6135 | 466.5065 | 442.2718 | 420.3406 | 487.4843
1980.6135 | 466.4973 | 442.3006 | 420.3339 | 487.1349
1981.6135 | 466.4275 | 442.3268 | 420.284 | 487.1927
1982.6135 | 466.4268 | 442.3582 | 420.1362 | 486.7202
1983.6135 | 466.443 | 442.4325 | 420.2832 | 486.75
1984.6135 | 466.4137 | 442.4481 | 420.4785 | 487.0436
1985.6135 | 466.4029 | 442.4615 | 420.4959 | 487.3783
1986.6135 | 466.3719 | 442.489 | 420.6017 | 487.457
1987.6135 | 466.3202 | 442.4961 | 420.4227 | 486.7285
1988.6135 | 466.4047 | 442.5959 | 420.498 | 487.487
1989.6135 | 466.3572 | 442.683 | 420.4375 | 486.8417
1990.6135 | 466.3205 | 442.7178 | 420.3549 | 486.5086
1991.6135 | 466.2737 | 442.707 | 420.5054 | 486.9517
1992.6135 | 466.2684 | 442.7683 | 420.4201 | 487.0431
1993.6135 | 466.3552 | 442.8112 | 420.4728 | 486.7537
1994.6135 | 466.5173 | 442.7843 | 420.7218 | 486.5376
1995.6135 | 466.6079 | 442.7092 | 420.6573 | 486.4397
1996.6135 | 466.7886 | 442.7577 | 420.7262 | 486.4526
1997.6135 | 466.9236 | 442.8402 | 420.8443 | 486.3419
1998.6135 | 466.9154 | 442.8812 | 420.7487 | 486.578
1999.6135 | 466.9142 | 442.9309 | 420.821 | 486.5004
2000.6135 | 466.9889 | 442.9777 | 420.8648 | 485.9314
2001.6135 | 467.0291 | 443.0698 | 420.8801 | 485.5346
2002.6135 | 467.1367 | 443.1173 | 420.9153 | 484.7135
2003.6135 | 466.997 | 443.027 | 420.8653 | 485.0245
2004.6135 | 466.9165 | 443.0677 | 421.0311 | 485.2938
2005.6135 | 466.9772 | 443.0032 | 421.1528 | 485.5624
2006.6135 | 467.076 | 443.1157 | 421.243 | 485.6828
2007.6135 | 467.0771 | 443.1951 | 421.2238 | 485.8113
2008.6135 | 467.12 | 443.2583 | 421.2043 | 485.7867
2009.6135 | 467.1656 | 443.2347 | 421.1914 | 485.2351
2010.6135 | 467.1945 | 443.1126 | 421.3021 | 485.1955
2011.6135 | 467.1036 | 443.1998 | 421.281 | 485.0524
2012.6135 | 467.0641 | 443.2734 | 421.2761 | 485.138
2013.6135 | 467.1175 | 443.3422 | 421.1946 | 485.0997
2014.6135 | 467 | 443.3168 | 421.33 | 485.123
2015.6135 | 466.8725 | 443.328 | 421.3309 | 485.3213
2016.6135 | 466.8531 | 443.4462 | 421.3861 | 485.3833
2017.6135 | 466.9273 | 443.5571 | 421.4538 | 485.3284
2018.6135 | 466.9757 | 443.6419 | 421.483 | 485.5525
2019.6135 | 466.9634 | 443.6105 | 421.5105 | 485.5111
2020.6135 | 467.0002 | 443.5724 | 421.6451 | 485.6545
2021.6135 | 467.0419 | 443.5063 | 421.4811 | 485.3321
2022.6135 | 467.0113 | 443.5735 | 421.3873 | 484.8061
2023.6135 | 467.0769 | 443.6376 | 421.5165 | 486.003
2024.6135 | 467.204 | 443.7086 | 421.6578 | 486.2261
2025.6135 | 467.1903 | 443.7284 | 421.5855 | 485.9842
2026.6135 | 467.2878 | 443.7736 | 421.6763 | 486.3217
2027.6135 | 467.268 | 443.8358 | 421.858 | 489.8197
2028.6135 | 467.1741 | 443.7346 | 421.8843 | 486.2574
2029.6135 | 467.1981 | 443.8252 | 421.9645 | 486.1762
2030.6135 | 467.1816 | 443.8344 | 422.0158 | 485.8794
2031.6135 | 467.1092 | 443.9146 | 421.9334 | 485.6845
2032.6135 | 467.0644 | 443.9197 | 422.0016 | 485.3218
2033.6135 | 467.1481 | 443.9486 | 422.0952 | 484.7767
2034.6135 | 467.097 | 443.985 | 422.1866 | 484.6492
2035.6135 | 467.1394 | 444.1208 | 422.1924 | 484.5145
2036.6135 | 467.052 | 444.1399 | 422.3018 | 484.6428
2037.6135 | 466.9458 | 444.1601 | 422.3628 | 484.2831
2038.6135 | 466.8424 | 444.2491 | 422.2644 | 483.6276
2039.6135 | 466.6488 | 444.2369 | 422.2767 | 483.8529
2040.6135 | 466.6556 | 444.2009 | 422.3727 | 484.4702
2041.6135 | 466.6639 | 444.218 | 422.3846 | 484.4384
2042.6135 | 466.6582 | 444.2727 | 422.1672 | 484.4634
2043.6135 | 466.6449 | 444.3366 | 422.2461 | 484.0988
2044.6135 | 466.5335 | 444.3774 | 422.4129 | 483.8202
2045.6135 | 466.4834 | 444.4391 | 422.505 | 483.84
2046.6135 | 466.4738 | 444.4792 | 422.5719 | 484.3716
2047.6135 | 466.5883 | 444.5567 | 422.4978 | 485.0255
2048.6135 | 466.4909 | 444.6045 | 422.5932 | 485.2005
2049.6135 | 466.4459 | 444.627 | 422.6618 | 485.7456
2050.6135 | 466.3692 | 444.6134 | 422.6412 | 485.7762
2051.6135 | 466.3265 | 444.5453 | 422.6044 | 487.6038
2052.6135 | 466.2758 | 444.5937 | 422.6622 | 488.671
2053.6135 | 466.3357 | 444.6888 | 422.6129 | 488.4479
2054.6135 | 466.3527 | 444.644 | 422.5788 | 487.3596
2055.6135 | 466.4388 | 444.7516 | 422.5662 | 487.0879
2056.6135 | 466.5472 | 444.7532 | 422.5955 | 487.9369
2057.6135 | 466.648 | 444.7321 | 422.7007 | 487.3302
2058.6135 | 466.6955 | 444.8395 | 422.7636 | 487.7181
2059.6135 | 466.6495 | 444.7722 | 422.6846 | 487.0907
2060.6135 | 466.6619 | 444.8367 | 422.8432 | 487.6929
2061.6135 | 466.8199 | 444.8709 | 422.8926 | 487.8311
2062.6135 | 466.9355 | 444.8947 | 422.8293 | 487.6604
2063.6135 | 466.9938 | 444.9136 | 422.8288 | 487.2896
2064.6135 | 466.97 | 444.9655 | 422.8225 | 487.1429
2065.6135 | 467.0391 | 445.0007 | 422.8909 | 487.4757
2066.6135 | 467.065 | 444.9625 | 422.9225 | 486.9338
2067.6135 | 467.0586 | 445.0126 | 422.9574 | 486.7057
2068.6135 | 467.0445 | 445.1162 | 423.0214 | 488.2638
2069.6135 | 467.0724 | 445.1793 | 422.9209 | 487.0819
2070.6135 | 467.17 | 445.2319 | 423.0968 | 486.5938
2071.6135 | 467.1564 | 445.295 | 423.106 | 486.9953
2072.6135 | 467.1393 | 445.3608 | 423.2753 | 487.0269
2073.6135 | 467.1707 | 445.3745 | 423.2334 | 487.1745
2074.6135 | 467.1761 | 445.3486 | 423.2278 | 488.6584
2075.6135 | 467.1175 | 445.3688 | 423.2457 | 488.5778
2076.6135 | 467.1104 | 445.3709 | 423.2719 | 488.6034
2077.6135 | 467.0231 | 445.3674 | 423.2603 | 488.6919
2078.6135 | 466.9813 | 445.466 | 423.2824 | 488.9772
2079.6135 | 466.8784 | 445.4817 | 423.39 | 488.3788
2080.6135 | 466.7992 | 445.5321 | 423.2156 | 490.705
2081.6135 | 466.8665 | 445.5543 | 422.9267 | 490.7832
2082.6135 | 466.7845 | 445.5724 | 423.0875 | 490.5441
2083.6135 | 466.7545 | 445.6011 | 422.9927 | 491.6905
2084.6135 | 466.8161 | 445.6181 | 423.1899 | 490.9566
2085.6135 | 466.8766 | 445.6673 | 423.2954 | 490.845
2086.6135 | 466.9573 | 445.6414 | 423.3499 | 490.6932
2087.6135 | 467.017 | 445.6342 | 423.246 | 490.6893
2088.6135 | 466.9635 | 445.6907 | 423.4279 | 490.7516
2089.6135 | 466.8934 | 445.7364 | 423.3517 | 490.9633
2090.6135 | 466.822 | 445.6769 | 423.5388 | 490.5183
2091.6135 | 466.5884 | 445.6718 | 423.3423 | 490.6641
2092.6135 | 466.4951 | 445.7165 | 423.3182 | 491.1296
2093.6135 | 466.4711 | 445.7734 | 423.5279 | 491.0683
2094.6135 | 466.4112 | 445.8285 | 423.3713 | 490.6867
2095.6135 | 466.3929 | 445.7465 | 423.5093 | 490.5722
2096.6135 | 466.3996 | 445.8028 | 423.615 | 490.8666
2097.6135 | 466.4692 | 445.9042 | 423.704 | 490.8274
2098.6135 | 466.6929 | 445.9007 | 423.7754 | 490.7283
2099.6135 | 466.6705 | 445.8591 | 423.6845 | 490.2951
2100.6135 | 466.714 | 445.9255 | 423.8436 | 490.3345
2101.6135 | 466.634 | 445.9425 | 423.879 | 490.6077
2102.6135 | 466.7827 | 446.0065 | 423.5713 | 490.6108
2103.6135 | 466.6933 | 446.0349 | 423.5935 | 490.2818
2104.6135 | 466.6659 | 446.0918 | 423.6787 | 489.9198
2105.6135 | 466.6991 | 446.1535 | 423.6293 | 489.9763
2106.6135 | 466.6763 | 446.1368 | 423.5589 | 490.8096
2107.6135 | 466.761 | 446.1378 | 423.6532 | 491.0986
2108.6135 | 466.911 | 446.2044 | 423.8281 | 490.4048
2109.6135 | 467.0158 | 446.209 | 423.9441 | 490.8394
2110.6135 | 466.9956 | 446.2401 | 424.0613 | 490.6285
2111.6135 | 467.0966 | 446.2115 | 423.8921 | 487.3774
2112.6135 | 467.1059 | 446.1593 | 423.1836 | 486.3382
2113.6135 | 467.1532 | 446.1841 | 423.5604 | 486.8381
2114.6135 | 467.249 | 446.3223 | 423.7793 | 486.678
2115.6135 | 467.3198 | 446.2566 | 423.7407 | 486.4955
2116.6135 | 467.4416 | 446.3843 | 423.738 | 486.8021
2117.6135 | 467.4614 | 446.4496 | 423.9067 | 486.6192
2118.6135 | 467.4762 | 446.4069 | 424.0353 | 486.3592
2119.6135 | 467.543 | 446.4093 | 424.0474 | 486.5868
2120.6135 | 467.6359 | 446.4991 | 424.1179 | 486.8372
2121.6135 | 467.5633 | 446.5317 | 424.2485 | 486.6887
2122.6135 | 467.5007 | 446.5741 | 424.1835 | 486.8932
2123.6135 | 467.3866 | 446.5726 | 424.3198 | 487.2371
2124.6135 | 467.3119 | 446.634 | 424.2866 | 487.1913
2125.6135 | 467.3718 | 446.7058 | 424.3344 | 487.1615
2126.6135 | 467.4222 | 446.7499 | 424.389 | 486.9952
2127.6135 | 467.4299 | 446.8073 | 424.2676 | 486.974
2128.6135 | 467.3766 | 446.8072 | 424.4363 | 487.0037
2129.6135 | 467.2654 | 446.8237 | 424.5056 | 487.9621
2130.6135 | 467.0656 | 446.7937 | 424.4115 | 487.3994
2131.6135 | 467.0642 | 446.7903 | 424.517 | 486.9976
2132.6135 | 467.1399 | 446.8084 | 424.4877 | 487.0579
2133.6135 | 467.1315 | 446.9194 | 424.5222 | 488.0818
2134.6135 | 467.0884 | 446.9202 | 424.5172 | 488.0416
2135.6135 | 466.9963 | 446.9235 | 424.5115 | 487.9496
2136.6135 | 466.9704 | 447.0223 | 424.4986 | 488.4485
2137.6135 | 467.0184 | 447.0668 | 424.5759 | 488.7704
2138.6135 | 467.011 | 447.0666 | 424.6614 | 488.7693
2139.6135 | 467.0335 | 447.0819 | 424.6358 | 489.0093
2140.6135 | 467.0309 | 447.1293 | 424.6432 | 489.0752
2141.6135 | 467.0402 | 447.1867 | 424.6931 | 489.1601
2142.6135 | 467.0118 | 447.1648 | 424.713 | 488.9264
2143.6135 | 466.962 | 447.1925 | 424.8554 | 488.7744
2144.6135 | 467.0214 | 447.2756 | 424.8999 | 488.7463
2145.6135 | 466.9773 | 447.3074 | 424.9208 | 488.0986
2146.6135 | 467.0141 | 447.3465 | 424.8941 | 488.1161
2147.6135 | 467.0141 | 447.3689 | 424.8771 | 488.7777
2148.6135 | 467.1953 | 447.3224 | 425.0304 | 488.5688
2149.6135 | 467.3783 | 447.3457 | 425.1454 | 488.7377
2150.6135 | 467.3277 | 447.4052 | 425.049 | 488.9043
2151.6135 | 467.1975 | 447.4131 | 425.0981 | 488.5383
2152.6135 | 467.1164 | 447.4411 | 425.2054 | 488.7916
2153.6135 | 467.1725 | 447.4134 | 425.3802 | 488.6217
2154.6135 | 467.1873 | 447.4733 | 425.2267 | 489.0573
2155.6135 | 467.1942 | 447.5487 | 425.2624 | 489.3157
2156.6135 | 467.2596 | 447.554 | 425.3343 | 489.4111
2157.6135 | 467.1915 | 447.4996 | 425.1002 | 489.1528
2158.6135 | 467.2007 | 447.555 | 425.116 | 489.2354
2159.6135 | 467.2157 | 447.5735 | 425.0812 | 489.0543
2160.6135 | 467.1412 | 447.6329 | 425.15 | 488.535
2161.6135 | 467.1221 | 447.6061 | 425.0954 | 489.1081
2162.6135 | 467.1324 | 447.6053 | 424.9308 | 488.9002
2163.6135 | 467.2291 | 447.5798 | 425.1841 | 488.9512
2164.6135 | 467.2264 | 447.6565 | 425.2772 | 489.0607
2165.6135 | 467.2414 | 447.799 | 425.305 | 488.5536
2166.6135 | 467.2668 | 447.8306 | 425.3653 | 489.2079
2167.6135 | 467.3257 | 447.867 | 425.4326 | 488.8388
2168.6135 | 467.3688 | 447.8888 | 425.4772 | 488.9639
2169.6135 | 467.3307 | 447.9433 | 425.517 | 488.7973
2170.6135 | 467.2558 | 447.9349 | 425.3197 | 488.3174
2171.6135 | 467.2463 | 447.9472 | 425.5026 | 487.8381
2172.6135 | 467.3269 | 447.8458 | 425.664 | 487.6414
2173.6135 | 467.322 | 447.9548 | 425.6896 | 487.8605
2174.6135 | 467.2734 | 448.018 | 425.7088 | 487.7951
2175.6135 | 467.2755 | 448.0374 | 425.8119 | 487.8845
2176.6135 | 467.2192 | 448.0472 | 425.8161 | 487.513
2177.6135 | 467.2728 | 447.8618 | 425.8384 | 487.3219
2178.6135 | 467.2357 | 447.9141 | 425.8931 | 487.4258
2179.6135 | 467.2477 | 448.0333 | 425.8797 | 487.7231
2180.6135 | 467.3268 | 448.0907 | 425.8968 | 487.3223
2181.6135 | 467.3466 | 448.119 | 426.0097 | 487.3004
2182.6135 | 467.402 | 448.1598 | 426.0351 | 490.6865
2183.6135 | 467.3999 | 448.1399 | 426.0152 | 491.3283
2184.6135 | 467.2845 | 448.2148 | 426.0381 | 491.4741
2185.6135 | 467.2235 | 448.2137 | 425.9557 | 491.2175
2186.6135 | 467.1925 | 448.2214 | 426.1007 | 491.302
2187.6135 | 467.1657 | 448.3447 | 425.8688 | 490.8911
2188.6135 | 467.224 | 448.3752 | 425.8949 | 490.0482
2189.6135 | 467.201 | 448.38 | 426.0729 | 490.0385
2190.6135 | 467.1953 | 448.3536 | 426.2656 | 490.1383
2191.6135 | 467.109 | 448.3687 | 426.3039 | 489.9404
2192.6135 | 466.9076 | 448.4261 | 426.3008 | 489.816
2193.6135 | 466.942 | 448.5141 | 426.164 | 486.2641
2194.6135 | 466.9945 | 448.4508 | 426.2118 | 487.9728
2195.6135 | 466.965 | 448.4488 | 426.4152 | 487.2308
2196.6135 | 466.8915 | 448.4586 | 426.3244 | 486.3679
2197.6135 | 466.8195 | 448.6257 | 426.3393 | 486.302
2198.6135 | 466.7855 | 448.6781 | 426.3228 | 489.2758
2199.6135 | 466.7238 | 448.68 | 426.3933 | 489.6376
2200.6135 | 466.7034 | 448.7692 | 426.4827 | 489.2903
2201.6135 | 466.6988 | 448.6188 | 426.3684 | 489.5475
2202.6135 | 466.7014 | 448.6427 | 426.5157 | 491.7309
2203.6135 | 466.6713 | 448.715 | 426.6323 | 491.9385
2204.6135 | 466.5898 | 448.7753 | 426.616 | 491.3709
2205.6135 | 466.5012 | 448.8283 | 426.5531 | 491.3061
2206.6135 | 466.5009 | 448.8394 | 426.4518 | 491.8365
2207.6135 | 466.4772 | 448.8522 | 426.4589 | 491.9989
2208.6135 | 466.427 | 448.9077 | 426.4756 | 491.7076
2209.6135 | 466.3652 | 448.9877 | 426.4877 | 491.3422
2210.6135 | 466.3532 | 449.0181 | 426.5406 | 491.1129
2211.6135 | 466.4117 | 449.0184 | 426.693 | 491.8017
2212.6135 | 466.3367 | 448.938 | 426.6586 | 491.7124
2213.6135 | 466.4176 | 449.0147 | 426.6808 | 491.8387
2214.6135 | 466.5821 | 449.0655 | 426.6286 | 491.6867
2215.6135 | 466.6575 | 449.1264 | 426.6394 | 491.1488
2216.6135 | 466.6882 | 449.0754 | 426.6558 | 492.4024
2217.6135 | 466.7004 | 449.1105 | 426.7919 | 492.4897
2218.6135 | 466.5952 | 449.1158 | 426.7236 | 492.4423
2219.6135 | 466.7217 | 449.0141 | 426.5802 | 492.4818
2220.6135 | 466.8347 | 449.0769 | 426.7895 | 492.3755
2221.6135 | 466.9627 | 449.0906 | 426.8914 | 492.3423
2222.6135 | 467.0011 | 449.0414 | 426.694 | 492.6829
2223.6135 | 467.0533 | 449.1043 | 426.7361 | 489.5142
2224.6135 | 467.1829 | 449.1407 | 426.7674 | 492.4848
2225.6135 | 467.2609 | 449.2387 | 426.7853 | 492.1838
2226.6135 | 467.3279 | 449.2691 | 426.8865 | 492.6491
2227.6135 | 467.3714 | 449.3214 | 426.904 | 492.5625
2228.6135 | 467.3786 | 449.3623 | 426.9024 | 492.2688
2229.6135 | 467.4379 | 449.4382 | 426.8948 | 492.9914
2230.6135 | 467.3847 | 449.4806 | 426.9323 | 492.472
2231.6135 | 467.4095 | 449.4983 | 427.0024 | 492.5317
2232.6135 | 467.4187 | 449.5449 | 426.8446 | 492.3724
2233.6135 | 467.4469 | 449.5227 | 427.1259 | 492.2953
2234.6135 | 467.4034 | 449.5266 | 427.1445 | 492.4778
2235.6135 | 467.3441 | 449.5592 | 427.1521 | 490.4069
2236.6135 | 467.3225 | 449.6556 | 427.1855 | 491.8256
2237.6135 | 467.2667 | 449.6688 | 427.1815 | 492.3609
2238.6135 | 467.2452 | 449.7055 | 427.0569 | 492.2328
2239.6135 | 467.1766 | 449.6542 | 427.1565 | 492.7465
2240.6135 | 467.0468 | 449.7466 | 427.1129 | 492.9896
2241.6135 | 467.0014 | 449.6826 | 427.2484 | 492.9753
2242.6135 | 467.0253 | 449.6786 | 427.2676 | 493.1763
2243.6135 | 467.0898 | 449.7181 | 427.2896 | 493.1678
2244.6135 | 467.089 | 449.7989 | 427.3192 | 492.8874
2245.6135 | 467.0966 | 449.7533 | 427.3994 | 489.8262
2246.6135 | 467.0756 | 449.7176 | 427.501 | 491.7637
2247.6135 | 467.1366 | 449.7685 | 427.5269 | 492.2775
2248.6135 | 467.0722 | 449.8897 | 427.4294 | 492.6974
2249.6135 | 466.9597 | 449.9445 | 427.5954 | 492.8526
2250.6135 | 466.7568 | 449.9721 | 427.6116 | 492.2729
2251.6135 | 466.6996 | 449.8965 | 427.5163 | 489.9848
2252.6135 | 466.7241 | 449.9666 | 427.5181 | 489.8844
2253.6135 | 466.7919 | 450.0479 | 427.4988 | 489.4158
2254.6135 | 466.8866 | 450.0093 | 427.3451 | 489.6981
2255.6135 | 467.0679 | 449.9418 | 427.4577 | 489.4379
2256.6135 | 467.0594 | 449.9474 | 427.5704 | 489.8443
2257.6135 | 467.0207 | 450.0648 | 427.6282 | 489.8351
2258.6135 | 466.989 | 450.066 | 427.6787 | 489.4318
2259.6135 | 466.8949 | 450.0908 | 427.4326 | 489.2405
2260.6135 | 466.8187 | 450.0242 | 427.2891 | 489.4331
2261.6135 | 466.8902 | 450.0972 | 427.5464 | 489.1293
2262.6135 | 466.8897 | 450.2106 | 427.5641 | 489.2358
2263.6135 | 466.909 | 450.2346 | 427.6623 | 489.6045
2264.6135 | 466.8769 | 450.2509 | 427.6219 | 489.2544
2265.6135 | 466.8836 | 450.272 | 427.7371 | 489.6378
2266.6135 | 466.8444 | 450.2066 | 427.7841 | 490.3392
2267.6135 | 466.7883 | 450.2208 | 427.7103 | 489.5257
2268.6135 | 466.862 | 450.294 | 427.4963 | 489.7384
2269.6135 | 466.9216 | 450.2518 | 427.8202 | 489.7053
2270.6135 | 466.9804 | 450.3184 | 427.8794 | 489.5971
2271.6135 | 466.9394 | 450.3729 | 427.8924 | 490.0566
2272.6135 | 466.9456 | 450.4617 | 427.8437 | 489.9374
2273.6135 | 466.954 | 450.4565 | 427.904 | 489.5355
2274.6135 | 466.9701 | 450.3087 | 428.0894 | 492.2797
2275.6135 | 467.0643 | 450.3427 | 428.284 | 492.3568
2276.6135 | 467.1776 | 450.4072 | 428.2765 | 492.4792
2277.6135 | 467.2107 | 450.4786 | 428.0904 | 492.6078
2278.6135 | 467.2461 | 450.4907 | 428.1385 | 492.9991
2279.6135 | 467.2456 | 450.469 | 428.2167 | 493.1319
2280.6135 | 467.0936 | 450.5171 | 427.9897 | 492.3953
2281.6135 | 467.1051 | 450.4891 | 427.9305 | 493.343
2282.6135 | 467.0727 | 450.5274 | 428.0497 | 493.4289
2283.6135 | 467.106 | 450.5615 | 427.7524 | 493.1585
2284.6135 | 467.1387 | 450.6093 | 427.9718 | 493.4562
2285.6135 | 467.1619 | 450.6456 | 428.0023 | 492.748
2286.6135 | 467.2133 | 450.598 | 427.9238 | 492.8403
2287.6135 | 467.2143 | 450.6214 | 428.1436 | 493.2039
2288.6135 | 467.2036 | 450.6494 | 428.1398 | 492.9395
2289.6135 | 467.1925 | 450.6727 | 428.193 | 493.1175
2290.6135 | 467.2856 | 450.6763 | 428.2086 | 493.3396
2291.6135 | 467.2008 | 450.7649 | 428.2949 | 493.4654
2292.6135 | 467.1015 | 450.7725 | 428.1715 | 491.8849
2293.6135 | 467.1128 | 450.7739 | 428.3096 | 491.997
2294.6135 | 467.1846 | 450.7366 | 428.3372 | 493.9453
2295.6135 | 467.1783 | 450.7638 | 428.3667 | 491.7778
2296.6135 | 467.2917 | 450.792 | 428.4447 | 491.5348
2297.6135 | 467.3253 | 450.6988 | 428.4766 | 491.1309
2298.6135 | 467.3874 | 450.8133 | 428.4321 | 491.8779
2299.6135 | 467.3192 | 450.8625 | 428.4096 | 492.0729
2300.6135 | 467.3085 | 450.8337 | 428.187 | 494.0059
2301.6135 | 467.4064 | 450.8495 | 428.2483 | 494.7375
2302.6135 | 467.4792 | 450.8952 | 428.2009 | 494.9734
2303.6135 | 467.5161 | 450.8847 | 428.403 | 495.1438
2304.6135 | 467.4475 | 450.9504 | 428.5125 | 494.5627
2305.6135 | 467.4473 | 450.9224 | 428.5301 | 494.1328
2306.6135 | 467.5088 | 450.9782 | 428.5349 | 494.764
2307.6135 | 467.4674 | 450.9895 | 428.6359 | 494.5276
2308.6135 | 467.501 | 451.0065 | 428.5905 | 494.8323
2309.6135 | 467.4547 | 451.0447 | 428.6702 | 494.668
2310.6135 | 467.4314 | 451.0174 | 428.6407 | 494.3795
2311.6135 | 467.4112 | 451.0626 | 428.5338 | 494.6674
2312.6135 | 467.4188 | 451.0967 | 428.3373 | 495.059
2313.6135 | 467.327 | 451.0407 | 428.6353 | 495.1278
2314.6135 | 467.3995 | 451.1393 | 428.6237 | 495.3426
2315.6135 | 467.4222 | 451.1593 | 428.7265 | 495.1189
2316.6135 | 467.3954 | 451.169 | 429.0179 | 495.3303
2317.6135 | 467.3764 | 451.1564 | 428.9948 | 495.3265
2318.6135 | 467.3657 | 451.1092 | 429.1185 | 495.0437
2319.6135 | 467.3477 | 451.183 | 429.1175 | 494.6908
2320.6135 | 467.2521 | 451.14 | 429.0764 | 494.7077
2321.6135 | 467.1546 | 451.1394 | 429.0842 | 494.7662
2322.6135 | 467.0463 | 451.2269 | 429.0299 | 495.2636
2323.6135 | 467.0175 | 451.3152 | 429.0108 | 495.3774
2324.6135 | 467.011 | 451.2633 | 429.0607 | 495.0981
2325.6135 | 467.008 | 451.2905 | 429.0558 | 494.8938
2326.6135 | 466.9886 | 451.3378 | 429.1293 | 495.1798
2327.6135 | 466.9091 | 451.3669 | 429.1654 | 495.2465
2328.6135 | 466.9753 | 451.4159 | 429.2667 | 495.6411
2329.6135 | 467.0232 | 451.4293 | 429.0902 | 495.8966
2330.6135 | 467.1134 | 451.4306 | 429.1489 | 495.9555
2331.6135 | 467.0386 | 451.5166 | 429.0902 | 495.6672
2332.6135 | 467.0474 | 451.5713 | 429.1751 | 495.9728
2333.6135 | 467.0317 | 451.5192 | 429.154 | 495.5592
2334.6135 | 467.0312 | 451.5594 | 429.1641 | 493.2506
2335.6135 | 467.1519 | 451.4926 | 429.2196 | 492.6391
2336.6135 | 467.186 | 451.4562 | 429.2812 | 492.5783
2337.6135 | 467.2943 | 451.5317 | 429.3552 | 492.4464
2338.6135 | 467.4032 | 451.5335 | 429.4062 | 492.3696
2339.6135 | 467.3787 | 451.5933 | 429.2838 | 492.2509
2340.6135 | 467.4082 | 451.6151 | 429.2501 | 495.3878
2341.6135 | 467.3064 | 451.6608 | 429.3568 | 495.8375
2342.6135 | 467.2734 | 451.6266 | 429.48 | 495.4227
2343.6135 | 467.3743 | 451.5775 | 429.5971 | 495.0257
2344.6135 | 467.4106 | 451.6088 | 429.604 | 493.5797
2345.6135 | 467.4193 | 451.6192 | 429.6214 | 493.353
2346.6135 | 467.3462 | 451.6699 | 429.4244 | 493.2461
2347.6135 | 467.3642 | 451.6234 | 429.2964 | 493.7306
2348.6135 | 467.3429 | 451.7426 | 429.5146 | 493.686
2349.6135 | 467.1632 | 451.7374 | 429.5155 | 494.178
2350.6135 | 467.0443 | 451.7656 | 429.572 | 494.0307
2351.6135 | 467.1195 | 451.7722 | 429.6282 | 493.8161
2352.6135 | 467.2007 | 451.7909 | 429.5567 | 493.6432
2353.6135 | 467.1693 | 451.8362 | 429.4676 | 493.791
2354.6135 | 467.1263 | 451.8614 | 429.3616 | 493.3603
2355.6135 | 467.1481 | 451.8477 | 429.5466 | 493.2456
2356.6135 | 467.1311 | 451.8849 | 429.4974 | 493.3703
2357.6135 | 467.0258 | 451.9689 | 429.59 | 493.5841
2358.6135 | 466.9674 | 451.9528 | 429.6445 | 493.4143
2359.6135 | 467.0108 | 451.9689 | 429.7209 | 493.4176
2360.6135 | 467.0821 | 451.8738 | 429.6134 | 493.4735
2361.6135 | 467.1267 | 451.9353 | 429.5855 | 493.5754
2362.6135 | 467.1641 | 451.9849 | 429.5745 | 493.2622
2363.6135 | 467.2052 | 452.0275 | 429.6646 | 493.0473
2364.6135 | 467.3102 | 452.0896 | 429.7928 | 493.3523
2365.6135 | 467.3504 | 452.1047 | 429.8012 | 492.8454
2366.6135 | 467.3734 | 452.1515 | 429.9177 | 492.9113
2367.6135 | 467.4353 | 452.1906 | 430.0017 | 493.3177
2368.6135 | 467.3944 | 452.1798 | 430.0467 | 493.049
2369.6135 | 467.2643 | 452.2052 | 429.9974 | 493.6472
2370.6135 | 467.235 | 452.2386 | 430.0077 | 494.0279
2371.6135 | 467.2913 | 452.0851 | 430.053 | 493.9268
2372.6135 | 467.1237 | 452.1726 | 429.9781 | 493.66
2373.6135 | 467.0324 | 452.2016 | 430.0658 | 493.4813
2374.6135 | 467.093 | 452.2358 | 430.1003 | 493.3711
2375.6135 | 466.9885 | 452.2184 | 430.1502 | 492.8997
2376.6135 | 467.0435 | 452.2671 | 430.1688 | 493.5325
2377.6135 | 467.0279 | 452.1888 | 430.1601 | 493.3363
2378.6135 | 466.962 | 452.1863 | 430.1072 | 493.3155
2379.6135 | 466.7917 | 452.1925 | 430.1869 | 492.9813
2380.6135 | 466.7333 | 452.2316 | 430.1692 | 492.8385
2381.6135 | 466.6833 | 452.2826 | 430.0763 | 493.1179
2382.6135 | 466.6427 | 452.3195 | 430.0987 | 492.9092
2383.6135 | 466.5907 | 452.3522 | 430.2142 | 492.709
2384.6135 | 466.674 | 452.4037 | 430.3245 | 493.2281
2385.6135 | 466.675 | 452.3961 | 430.2989 | 493.3787
2386.6135 | 466.6889 | 452.4535 | 430.2482 | 494.23
2387.6135 | 466.6713 | 452.4582 | 430.1834 | 494.2087
2388.6135 | 466.7146 | 452.4197 | 430.1419 | 494.0655
2389.6135 | 466.5981 | 452.401 | 430.0654 | 493.8986
2390.6135 | 466.602 | 452.4113 | 430.2458 | 493.7532
2391.6135 | 466.6186 | 452.4389 | 430.2158 | 493.5717
2392.6135 | 466.6213 | 452.4471 | 430.2764 | 493.3386
2393.6135 | 466.7166 | 452.4948 | 430.2768 | 493.4217
2394.6135 | 466.7477 | 452.4532 | 430.1422 | 493.3945
2395.6135 | 466.7736 | 452.5087 | 430.1651 | 493.8814
2396.6135 | 466.7448 | 452.531 | 430.2962 | 493.6244
2397.6135 | 466.773 | 452.5139 | 430.3719 | 493.8839
2398.6135 | 466.7926 | 452.6154 | 430.2315 | 494.7324
2399.6135 | 466.8129 | 452.5963 | 430.3369 | 493.8152
2400.6135 | 466.9526 | 452.641 | 430.4003 | 495.8743
2401.6135 | 467.0156 | 452.653 | 430.3019 | 493.9907
2402.6135 | 467.0626 | 452.609 | 430.4283 | 494.8474
2403.6135 | 467.0634 | 452.6091 | 430.4306 | 497.9147
2404.6135 | 467.0866 | 452.6408 | 430.4033 | 497.6782
2405.6135 | 467.1935 | 452.6674 | 430.4832 | 497.7644
2406.6135 | 467.1533 | 452.6749 | 430.6115 | 498.1929
2407.6135 | 467.1438 | 452.5826 | 430.6347 | 494.4935
2408.6135 | 467.2012 | 452.5713 | 430.6112 | 494.2415
2409.6135 | 467.1795 | 452.5384 | 430.5701 | 494.2837
2410.6135 | 467.067 | 452.5844 | 430.5924 | 494.0905
2411.6135 | 467.0556 | 452.6517 | 430.5291 | 494.9403
2412.6135 | 467.0073 | 452.7124 | 430.4613 | 494.4275
2413.6135 | 466.8764 | 452.7772 | 430.4859 | 496.9518
2414.6135 | 466.7215 | 452.8019 | 430.032 | 497.5149
2415.6135 | 466.7147 | 452.7944 | 430.1702 | 497.5111
2416.6135 | 466.6438 | 452.8626 | 430.3958 | 497.8289
2417.6135 | 466.6005 | 452.867 | 430.5295 | 497.6503
2418.6135 | 466.637 | 452.861 | 430.5827 | 497.4672
2419.6135 | 466.6551 | 452.8109 | 430.4112 | 495.1237
2420.6135 | 466.6439 | 452.8075 | 430.4789 | 497.3556
2421.6135 | 466.6333 | 452.7492 | 430.3091 | 497.8852
2422.6135 | 466.6142 | 452.8044 | 430.3874 | 497.6951
2423.6135 | 466.4559 | 452.8443 | 430.278 | 497.5056
2424.6135 | 466.519 | 452.7967 | 430.2722 | 496.9664
2425.6135 | 466.6524 | 452.8593 | 430.401 | 497.3933
2426.6135 | 466.6717 | 452.8989 | 430.2146 | 497.0916
2427.6135 | 466.7136 | 452.9098 | 430.2703 | 496.7835
2428.6135 | 466.8894 | 452.9177 | 430.3639 | 496.2938
2429.6135 | 467.059 | 452.9995 | 430.2749 | 496.4115
2430.6135 | 467.3152 | 453.0207 | 430.2192 | 496.003
2431.6135 | 467.4691 | 453.0404 | 429.8952 | 496.203
2432.6135 | 467.5674 | 453.0603 | 429.9365 | 496.1216
2433.6135 | 467.667 | 453.07 | 430.0152 | 495.9937
2434.6135 | 467.7806 | 452.8989 | 430.1604 | 495.914
2435.6135 | 467.864 | 452.9927 | 430.3529 | 495.4883
2436.6135 | 468.0413 | 452.9162 | 430.5546 | 495.3344
2437.6135 | 468.094 | 452.9985 | 430.5368 | 495.4887
2438.6135 | 468.1689 | 453.0333 | 430.6723 | 494.6268
2439.6135 | 468.2655 | 453.0645 | 430.781 | 494.837
2440.6135 | 468.3131 | 453.1243 | 430.7446 | 494.5661
2441.6135 | 468.292 | 453.1837 | 430.6637 | 494.676
2442.6135 | 468.405 | 453.1913 | 430.7782 | 494.9921
2443.6135 | 468.4826 | 453.2706 | 430.7035 | 494.8992
2444.6135 | 468.4825 | 453.2211 | 430.8217 | 494.9031
2445.6135 | 468.4912 | 453.1912 | 430.5592 | 495.4442
2446.6135 | 468.4249 | 453.1678 | 430.6844 | 495.7855
2447.6135 | 468.5363 | 453.2851 | 430.8301 | 495.5989
2448.6135 | 468.533 | 453.34 | 430.9134 | 495.6332
2449.6135 | 468.5707 | 453.3683 | 430.9185 | 495.6003
2450.6135 | 468.6413 | 453.3697 | 430.8564 | 495.3627
2451.6135 | 468.6859 | 453.4132 | 430.9076 | 495.584
2452.6135 | 468.6024 | 453.3754 | 430.881 | 495.5251
2453.6135 | 468.4961 | 453.3751 | 430.8283 | 495.4691
2454.6135 | 468.3184 | 453.3524 | 430.7533 | 495.1095
2455.6135 | 468.2362 | 453.3876 | 430.8396 | 494.9053
2456.6135 | 468.2527 | 453.3623 | 430.9459 | 494.8485
2457.6135 | 468.2292 | 453.3262 | 430.9958 | 495.3578
2458.6135 | 468.1597 | 453.4129 | 430.997 | 495.1557
2459.6135 | 468.153 | 453.4534 | 430.9519 | 494.9478
2460.6135 | 468.196 | 453.4766 | 430.907 | 494.7149
2461.6135 | 468.1909 | 453.51 | 430.9006 | 494.8856
2462.6135 | 468.2066 | 453.5599 | 430.8691 | 494.2267
2463.6135 | 468.2524 | 453.5002 | 431.0087 | 494.7007
2464.6135 | 468.3095 | 453.4453 | 431.1653 | 494.9502
2465.6135 | 468.2777 | 453.4977 | 431.1623 | 494.9768
2466.6135 | 468.1642 | 453.5901 | 431.0772 | 495.0687
2467.6135 | 468.0926 | 453.5554 | 431.0869 | 495.3562
2468.6135 | 468.0039 | 453.575 | 430.9693 | 495.303
2469.6135 | 467.8978 | 453.5353 | 430.9853 | 495.2007
2470.6135 | 467.8935 | 453.6335 | 431.1391 | 495.3258
2471.6135 | 467.9936 | 453.5423 | 431.2086 | 496.1073
2472.6135 | 468.0161 | 453.6109 | 431.241 | 495.9304
2473.6135 | 468.0347 | 453.6732 | 431.1276 | 495.5189
2474.6135 | 467.9771 | 453.7174 | 430.9449 | 494.672
2475.6135 | 467.8894 | 453.7269 | 430.8417 | 495.55
2476.6135 | 467.8753 | 453.7454 | 430.7395 | 495.2247
2477.6135 | 467.7119 | 453.7039 | 430.8816 | 495.1443
2478.6135 | 467.7424 | 453.7506 | 431.0272 | 494.7252
2479.6135 | 467.6783 | 453.7606 | 430.9996 | 494.9873
2480.6135 | 467.5169 | 453.7912 | 431.1695 | 495.2298
2481.6135 | 467.4601 | 453.7371 | 431.2253 | 495.0352
2482.6135 | 467.4864 | 453.702 | 431.3246 | 494.7766
2483.6135 | 467.4809 | 453.7235 | 431.3585 | 494.9487
2484.6135 | 467.5427 | 453.7983 | 431.3239 | 494.7555
2485.6135 | 467.4771 | 453.8518 | 431.3908 | 495.1653
2486.6135 | 467.4925 | 453.8706 | 431.3319 | 495.0395
2487.6135 | 467.5768 | 453.8898 | 431.4426 | 494.7839
2488.6135 | 467.5085 | 453.8289 | 431.4783 | 494.4442
2489.6135 | 467.4929 | 453.826 | 431.524 | 494.9699
2490.6135 | 467.442 | 453.7142 | 431.6435 | 494.7698
2491.6135 | 467.4076 | 453.8126 | 431.6219 | 494.9733
2492.6135 | 467.4095 | 453.8784 | 431.4937 | 495.3232
2493.6135 | 467.3708 | 453.9412 | 431.2844 | 495.4993
2494.6135 | 467.3941 | 453.8788 | 431.3843 | 495.2363
2495.6135 | 467.4917 | 453.9196 | 431.3564 | 495.1505
2496.6135 | 467.5218 | 453.9386 | 431.5374 | 495.6313
2497.6135 | 467.5613 | 453.9533 | 431.5308 | 495.8778
2498.6135 | 467.5975 | 454.0387 | 431.5693 | 495.6061
2499.6135 | 467.6003 | 454.0088 | 431.7008 | 495.5217
2500.6135 | 467.6387 | 454.0505 | 431.7743 | 495.758
2501.6135 | 467.6137 | 454.0504 | 431.6334 | 495.6395
2502.6135 | 467.6133 | 453.9882 | 431.7105 | 495.5674
2503.6135 | 467.6195 | 454.0105 | 431.5999 | 495.5957
2504.6135 | 467.6392 | 454.0452 | 431.6576 | 495.9038
2505.6135 | 467.6203 | 454.0347 | 431.7702 | 495.8146
2506.6135 | 467.6497 | 454.1038 | 431.8286 | 495.9671
2507.6135 | 467.571 | 454.1586 | 431.8855 | 495.7277
2508.6135 | 467.4125 | 454.1788 | 431.807 | 495.7928
2509.6135 | 467.3821 | 454.1754 | 431.6763 | 495.6349
2510.6135 | 467.3931 | 454.2255 | 431.7211 | 495.727
2511.6135 | 467.3795 | 454.2501 | 431.8247 | 496.1886
2512.6135 | 467.445 | 454.3014 | 431.6928 | 496.1294
2513.6135 | 467.3517 | 454.2583 | 431.8378 | 496.2426
2514.6135 | 467.3848 | 454.2443 | 431.8827 | 496.0964
2515.6135 | 467.369 | 454.2596 | 431.8475 | 495.9604
2516.6135 | 467.3399 | 454.2561 | 431.9269 | 496.1232
2517.6135 | 467.2191 | 454.2811 | 432.0694 | 496.1304
2518.6135 | 467.2189 | 454.279 | 432.0819 | 496.3982
2519.6135 | 467.2946 | 454.2912 | 432.0602 | 496.3468
2520.6135 | 467.3349 | 454.3113 | 432.123 | 495.8944
2521.6135 | 467.2915 | 454.3474 | 432.105 | 496.0298
2522.6135 | 467.3509 | 454.4035 | 432.0796 | 496.0627
2523.6135 | 467.3386 | 454.3867 | 432.0411 | 496.0714
2524.6135 | 467.3413 | 454.3977 | 431.9727 | 496.1607
2525.6135 | 467.3237 | 454.4598 | 432.1328 | 496.492
2526.6135 | 467.3651 | 454.5252 | 432.163 | 496.6317
2527.6135 | 467.4371 | 454.4014 | 432.2616 | 496.4224
2528.6135 | 467.4231 | 454.4841 | 432.2468 | 496.7735
2529.6135 | 467.4497 | 454.5203 | 432.1203 | 496.5073
2530.6135 | 467.5103 | 454.5337 | 432.1845 | 496.543
2531.6135 | 467.4619 | 454.515 | 432.1894 | 496.7678
2532.6135 | 467.3978 | 454.5585 | 432.2094 | 496.6244
2533.6135 | 467.3123 | 454.5701 | 432.3375 | 496.3285
2534.6135 | 467.3832 | 454.5023 | 432.2563 | 496.4088
2535.6135 | 467.4378 | 454.4605 | 432.3904 | 496.5113
2536.6135 | 467.3777 | 454.5089 | 432.2011 | 496.7387
2537.6135 | 467.2965 | 454.4679 | 432.0762 | 496.8364
2538.6135 | 467.1833 | 454.572 | 432.1527 | 496.947
2539.6135 | 467.1755 | 454.6427 | 432.2504 | 496.8273
2540.6135 | 467.2823 | 454.6163 | 432.1726 | 496.9672
2541.6135 | 467.2975 | 454.5708 | 432.2847 | 496.8096
2542.6135 | 467.1505 | 454.6471 | 432.3384 | 496.7701
2543.6135 | 467.2118 | 454.6601 | 432.3562 | 496.6003
2544.6135 | 467.2207 | 454.7097 | 432.3205 | 496.8627
2545.6135 | 467.3703 | 454.6505 | 432.4855 | 496.9398
2546.6135 | 467.4616 | 454.5386 | 432.3514 | 497.2222
2547.6135 | 467.4228 | 454.6558 | 432.3946 | 497.2108
2548.6135 | 467.4277 | 454.6914 | 432.5078 | 497.2187
2549.6135 | 467.4983 | 454.6672 | 432.594 | 497.3644
2550.6135 | 467.4489 | 454.7835 | 432.5443 | 497.6401
2551.6135 | 467.419 | 454.8317 | 432.5413 | 497.1983
2552.6135 | 467.4831 | 454.8487 | 432.4819 | 497.1126
2553.6135 | 467.507 | 454.8746 | 432.5298 | 496.5238
2554.6135 | 467.517 | 454.8671 | 432.6118 | 496.7408
2555.6135 | 467.4723 | 454.8945 | 432.6982 | 496.9079
2556.6135 | 467.3744 | 454.8834 | 432.4829 | 496.7152
2557.6135 | 467.2897 | 454.9256 | 432.4177 | 496.5982
2558.6135 | 467.308 | 454.973 | 432.2949 | 496.4331
2559.6135 | 467.4179 | 454.9466 | 432.3778 | 496.407
2560.6135 | 467.4219 | 454.9795 | 432.5355 | 496.1961
2561.6135 | 467.4464 | 454.969 | 432.6277 | 496.3002
2562.6135 | 467.5151 | 454.9659 | 432.718 | 496.0648
2563.6135 | 467.5262 | 454.9157 | 432.8723 | 495.8874
2564.6135 | 467.5811 | 454.9302 | 432.8833 | 495.7144
2565.6135 | 467.6203 | 455.0254 | 432.7821 | 495.1879
2566.6135 | 467.5516 | 455.0734 | 432.6309 | 495.4379
2567.6135 | 467.5727 | 454.9974 | 432.5717 | 493.7007
2568.6135 | 467.6462 | 455.0165 | 432.5847 | 492.2129
2569.6135 | 467.6498 | 455.0799 | 432.6644 | 494.9438
2570.6135 | 467.6042 | 455.1351 | 432.6761 | 495.2312
2571.6135 | 467.6248 | 455.1432 | 432.7117 | 492.5565
2572.6135 | 467.5288 | 455.1824 | 432.7761 | 493.4435
2573.6135 | 467.4498 | 455.1932 | 432.7704 | 491.6143
2574.6135 | 467.4863 | 455.1957 | 432.6693 | 491.7343
2575.6135 | 467.5077 | 455.2286 | 432.7902 | 493.2186
2576.6135 | 467.5202 | 455.2807 | 432.8786 | 492.2214
2577.6135 | 467.6028 | 455.1942 | 432.6723 | 492.3081
2578.6135 | 467.6538 | 455.2279 | 432.505 | 491.785
2579.6135 | 467.7823 | 455.1773 | 432.5022 | 491.5519
2580.6135 | 467.7971 | 455.2029 | 432.7602 | 492.1984
2581.6135 | 467.7906 | 455.1912 | 432.8339 | 492.0374
2582.6135 | 467.8266 | 455.2584 | 432.7096 | 491.2657
2583.6135 | 467.8632 | 455.2002 | 432.7112 | 493.572
2584.6135 | 467.8548 | 455.2022 | 432.7644 | 493.4552
2585.6135 | 467.8271 | 455.1749 | 432.7816 | 494.9024
2586.6135 | 467.733 | 455.2612 | 432.6486 | 495.1757
2587.6135 | 467.6578 | 455.275 | 432.8344 | 495.5619
2588.6135 | 467.5815 | 455.2692 | 432.9447 | 495.0497
2589.6135 | 467.5032 | 455.3293 | 432.934 | 495.3285
2590.6135 | 467.5611 | 455.3276 | 432.8752 | 495.0307
2591.6135 | 467.5465 | 455.3333 | 432.7331 | 495.511
2592.6135 | 467.4906 | 455.2757 | 432.9156 | 495.2429
2593.6135 | 467.4476 | 455.4125 | 432.9645 | 495.6683
2594.6135 | 467.3831 | 455.3547 | 433.1704 | 496.0992
2595.6135 | 467.2293 | 455.36 | 433.088 | 496.1184
2596.6135 | 467.2284 | 455.4083 | 432.8337 | 496.2039
2597.6135 | 467.204 | 455.3637 | 432.9251 | 496.445
2598.6135 | 467.0276 | 455.4523 | 432.9385 | 494.9074
2599.6135 | 467.0073 | 455.4969 | 433.15 | 494.9813
2600.6135 | 467.0153 | 455.4754 | 433.2692 | 495.2311
2601.6135 | 466.9767 | 455.5331 | 433.3472 | 494.9295
2602.6135 | 466.86 | 455.5267 | 433.2574 | 495.1202
2603.6135 | 466.84 | 455.5665 | 433.3272 | 495.0078
2604.6135 | 466.9157 | 455.6126 | 433.2766 | 494.3454
2605.6135 | 466.8483 | 455.5633 | 433.1623 | 494.6977
2606.6135 | 466.9696 | 455.4822 | 433.1259 | 495.2386
2607.6135 | 467.073 | 455.5115 | 433.1417 | 495.4906
2608.6135 | 467.079 | 455.5579 | 433.1196 | 495.1567
2609.6135 | 467.0873 | 455.6562 | 433.2466 | 497.1637
2610.6135 | 466.9577 | 455.5847 | 433.358 | 497.2012
2611.6135 | 466.8064 | 455.6541 | 433.32 | 497.0233
2612.6135 | 466.6956 | 455.6015 | 433.2141 | 497.0902
2613.6135 | 466.6526 | 455.6695 | 433.3549 | 496.9166
2614.6135 | 466.5537 | 455.7268 | 433.1635 | 496.6506
2615.6135 | 466.5425 | 455.7966 | 432.7894 | 496.7334
2616.6135 | 466.5253 | 455.7746 | 432.8126 | 496.421
2617.6135 | 466.5031 | 455.7316 | 433.0396 | 496.3715
2618.6135 | 466.4985 | 455.8031 | 433.0708 | 494.8243
2619.6135 | 466.6084 | 455.7796 | 433.1846 | 494.9226
2620.6135 | 466.5548 | 455.7063 | 433.1953 | 494.9787
2621.6135 | 466.5096 | 455.75 | 433.3677 | 494.4166
2622.6135 | 466.4883 | 455.7771 | 433.4059 | 494.602
2623.6135 | 466.521 | 455.8378 | 433.3304 | 494.4359
2624.6135 | 466.5864 | 455.873 | 433.4406 | 495.0558
2625.6135 | 466.6223 | 455.9127 | 433.4232 | 495.0135
2626.6135 | 466.5591 | 455.9284 | 433.4005 | 495.0627
2627.6135 | 466.5319 | 455.9635 | 433.457 | 495.1002
2628.6135 | 466.5222 | 456.0218 | 433.4515 | 495.4164
2629.6135 | 466.47 | 455.9334 | 433.5505 | 495.3159
2630.6135 | 466.609 | 455.8706 | 433.6207 | 495.481
2631.6135 | 466.7635 | 455.8619 | 433.814 | 495.4618
2632.6135 | 466.9035 | 455.8505 | 433.7389 | 495.394
2633.6135 | 466.8189 | 455.8699 | 433.5967 | 495.1006
2634.6135 | 466.6164 | 456.0087 | 433.6394 | 495.1287
2635.6135 | 466.6051 | 456.036 | 433.6587 | 494.9455
2636.6135 | 466.7067 | 455.9602 | 433.735 | 494.8636
2637.6135 | 466.6564 | 456.0392 | 433.7138 | 495.2105
2638.6135 | 466.6485 | 456.02 | 433.758 | 495.2301
2639.6135 | 466.6237 | 455.9891 | 433.7545 | 495.1479
2640.6135 | 466.6491 | 455.9773 | 433.5914 | 495.1981
2641.6135 | 466.648 | 455.9566 | 433.6698 | 495.1658
2642.6135 | 466.5575 | 456.0191 | 433.7362 | 495.2132
2643.6135 | 466.5218 | 456.1026 | 433.8319 | 494.839
2644.6135 | 466.6079 | 456.0495 | 433.7793 | 494.7715
2645.6135 | 466.6059 | 456.1124 | 433.82 | 494.5205
2646.6135 | 466.5193 | 456.1123 | 433.8651 | 494.4918
2647.6135 | 466.5061 | 456.1666 | 433.6942 | 494.4224
2648.6135 | 466.4695 | 456.1514 | 433.7055 | 494.5919
2649.6135 | 466.5241 | 456.1928 | 433.6806 | 494.7485
2650.6135 | 466.6153 | 456.1403 | 433.749 | 494.8853
2651.6135 | 466.7529 | 456.1855 | 433.5071 | 494.7146
2652.6135 | 466.7798 | 456.1418 | 433.4433 | 494.4699
2653.6135 | 466.7848 | 456.1542 | 433.5925 | 494.3591
2654.6135 | 466.9255 | 456.086 | 433.687 | 494.6093
2655.6135 | 466.8997 | 456.1353 | 433.6574 | 494.7359
2656.6135 | 466.8715 | 456.2185 | 433.7963 | 494.6322
2657.6135 | 466.8442 | 456.2319 | 433.4827 | 494.4429
2658.6135 | 466.8184 | 456.316 | 433.296 | 494.8747
2659.6135 | 466.9175 | 456.2799 | 433.5646 | 494.9119
2660.6135 | 467.0022 | 456.3099 | 433.678 | 494.9145
2661.6135 | 466.9981 | 456.303 | 433.56 | 494.9509
2662.6135 | 466.9714 | 456.2615 | 433.5888 | 495.1259
2663.6135 | 466.9659 | 456.3422 | 433.6291 | 495.1177
2664.6135 | 467.0423 | 456.3513 | 433.6304 | 495.4444
2665.6135 | 467.1569 | 456.3453 | 433.6724 | 495.6595
2666.6135 | 467.2459 | 456.2828 | 433.5204 | 495.7238
2667.6135 | 467.2751 | 456.2951 | 433.6917 | 495.6103
2668.6135 | 467.3406 | 456.2956 | 433.3769 | 495.4796
2669.6135 | 467.4369 | 456.3441 | 433.4442 | 495.5253
2670.6135 | 467.5414 | 456.3566 | 433.4666 | 495.2808
2671.6135 | 467.6061 | 456.2902 | 433.5445 | 495.4055
2672.6135 | 467.7571 | 456.2326 | 433.5828 | 495.291
2673.6135 | 467.8356 | 456.2109 | 433.5699 | 495.335
2674.6135 | 467.9948 | 456.3422 | 433.7315 | 495.8629
2675.6135 | 468.0425 | 456.2463 | 433.8113 | 495.7338
2676.6135 | 467.9795 | 456.3217 | 433.7721 | 495.6641
2677.6135 | 468.0524 | 456.3539 | 433.6283 | 496.0391
2678.6135 | 468.1146 | 456.4073 | 433.6741 | 496.2026
2679.6135 | 468.1751 | 456.4806 | 433.7572 | 496.1179
2680.6135 | 468.2615 | 456.396 | 433.744 | 496.2379
2681.6135 | 468.3804 | 456.3568 | 433.8221 | 496.1371
2682.6135 | 468.5048 | 456.4128 | 433.9115 | 496.1589
2683.6135 | 468.6483 | 456.4689 | 433.9984 | 496.2219
2684.6135 | 468.7294 | 456.5355 | 433.9923 | 495.9484
2685.6135 | 468.826 | 456.5808 | 433.9846 | 495.8508
2686.6135 | 468.9763 | 456.4784 | 433.844 | 495.7581
2687.6135 | 469.0295 | 456.4679 | 433.6858 | 495.7259
2688.6135 | 469.0086 | 456.4295 | 433.8266 | 495.6333
2689.6135 | 468.9852 | 456.4505 | 433.9837 | 495.7032
2690.6135 | 468.8863 | 456.4447 | 433.9282 | 495.6538
2691.6135 | 468.8728 | 456.5249 | 433.9201 | 495.3915
2692.6135 | 468.9747 | 456.5975 | 433.8959 | 495.6806
2693.6135 | 469.0348 | 456.6104 | 434.1033 | 495.6065
2694.6135 | 469.0984 | 456.6313 | 434.0847 | 495.902
2695.6135 | 469.0931 | 456.688 | 434.0318 | 495.7272
2696.6135 | 468.9409 | 456.6485 | 434.0729 | 495.8558
2697.6135 | 468.898 | 456.5963 | 433.646 | 495.7053
2698.6135 | 468.851 | 456.5715 | 433.616 | 495.7779
2699.6135 | 468.9773 | 456.5591 | 433.8997 | 496.1836
2700.6135 | 468.9517 | 456.6361 | 433.7286 | 496.0066
2701.6135 | 468.7798 | 456.6184 | 433.7268 | 495.9812
2702.6135 | 468.6066 | 456.5705 | 434.0215 | 495.9423
2703.6135 | 468.4631 | 456.4189 | 434.1725 | 496.1553
2704.6135 | 468.4694 | 456.4788 | 434.0417 | 496.1982
2705.6135 | 468.6485 | 456.544 | 434.1005 | 496.8374
2706.6135 | 468.7397 | 456.5507 | 434.0422 | 496.1494
2707.6135 | 468.7543 | 456.5884 | 434.218 | 495.9407
2708.6135 | 468.7784 | 456.6317 | 434.1442 | 495.6873
2709.6135 | 468.6597 | 456.6517 | 434.2504 | 495.6471
2710.6135 | 468.5667 | 456.7131 | 434.2973 | 495.7242
2711.6135 | 468.4525 | 456.7685 | 434.2462 | 495.5373
2712.6135 | 468.3956 | 456.7289 | 434.2681 | 497.4034
2713.6135 | 468.3471 | 456.8244 | 434.2939 | 496.2536
2714.6135 | 468.2894 | 456.8422 | 434.2458 | 496.3931
2715.6135 | 468.2588 | 456.9079 | 434.3118 | 496.0439
2716.6135 | 468.1471 | 456.9305 | 434.3268 | 496.098
2717.6135 | 467.9564 | 456.9128 | 434.5013 | 496.1273
2718.6135 | 467.8535 | 456.909 | 434.4386 | 495.8921
2719.6135 | 467.8014 | 456.8833 | 434.2739 | 495.8211
2720.6135 | 467.6977 | 456.8732 | 434.2793 | 495.7759
2721.6135 | 467.6676 | 456.8336 | 434.4161 | 495.7552
2722.6135 | 467.531 | 456.8497 | 434.4084 | 495.918
2723.6135 | 467.5557 | 456.907 | 434.4087 | 496.4091
2724.6135 | 467.6014 | 456.9399 | 434.4519 | 496.783
2725.6135 | 467.6348 | 456.936 | 434.4269 | 496.5762
2726.6135 | 467.6584 | 456.8665 | 434.3859 | 496.4222
2727.6135 | 467.6864 | 456.8615 | 434.2612 | 496.5552
2728.6135 | 467.6179 | 456.9369 | 434.1918 | 498.4936
2729.6135 | 467.5357 | 456.9409 | 434.2225 | 498.6429
2730.6135 | 467.4666 | 456.9026 | 434.3314 | 496.8101
2731.6135 | 467.4156 | 456.956 | 434.147 | 496.3682
2732.6135 | 467.3136 | 456.8273 | 433.9954 | 496.5458
2733.6135 | 467.2941 | 456.8995 | 433.9308 | 496.5077
2734.6135 | 467.3234 | 456.978 | 434.2084 | 496.4481
2735.6135 | 467.2133 | 456.9389 | 434.1092 | 496.3222
2736.6135 | 467.127 | 456.9033 | 434.3579 | 496.4586
2737.6135 | 467.1539 | 456.8719 | 434.4538 | 496.4422
2738.6135 | 467.1348 | 456.9091 | 434.4713 | 496.3581
2739.6135 | 467.071 | 456.7854 | 434.3472 | 496.2156
2740.6135 | 467.0478 | 456.9199 | 434.3391 | 495.9037
2741.6135 | 467.058 | 457.0219 | 434.4338 | 496.3119
2742.6135 | 467.0228 | 457.1103 | 434.4007 | 496.1159
2743.6135 | 466.9256 | 457.1238 | 434.3746 | 495.644
2744.6135 | 466.8085 | 457.1405 | 434.3839 | 495.3276
2745.6135 | 466.7408 | 457.1613 | 434.3517 | 495.4664
2746.6135 | 466.6904 | 457.1374 | 434.4922 | 495.3183
2747.6135 | 466.6071 | 457.1419 | 434.5081 | 495.6136
2748.6135 | 466.6647 | 457.1711 | 434.5552 | 495.5545
2749.6135 | 466.6333 | 457.1069 | 434.5851 | 495.7403
2750.6135 | 466.6496 | 456.9879 | 434.4041 | 496.04
2751.6135 | 466.673 | 457.0418 | 434.4304 | 496.5307
2752.6135 | 466.6731 | 456.9903 | 434.5305 | 496.4919
2753.6135 | 466.6991 | 457.0769 | 434.5989 | 496.3536
2754.6135 | 466.7772 | 457.1382 | 434.5114 | 496.231
2755.6135 | 466.8005 | 457.1299 | 434.593 | 496.2101
2756.6135 | 466.8497 | 457.0853 | 434.2625 | 496.4353
2757.6135 | 466.8875 | 457.0343 | 434.2731 | 496.2544
2758.6135 | 466.9105 | 457.0368 | 434.4498 | 495.9743
2759.6135 | 466.8802 | 457.1203 | 434.5769 | 496.069
2760.6135 | 466.8409 | 457.1335 | 434.5552 | 496.1316
2761.6135 | 466.787 | 457.1395 | 434.6498 | 496.5645
2762.6135 | 466.8159 | 457.0748 | 434.6669 | 496.2644
2763.6135 | 466.7889 | 457.0112 | 434.5873 | 497.0083
2764.6135 | 466.8019 | 457.1078 | 434.6415 | 497.8475
2765.6135 | 466.8997 | 457.1711 | 434.7365 | 497.5346
2766.6135 | 466.8933 | 457.142 | 434.7787 | 497.2786
2767.6135 | 466.9298 | 457.1701 | 434.7736 | 497.1672
2768.6135 | 466.9237 | 457.1984 | 434.6659 | 497.7128
2769.6135 | 466.9187 | 457.2415 | 434.8179 | 497.494
2770.6135 | 466.9687 | 457.2583 | 434.8523 | 497.4383
2771.6135 | 466.9278 | 457.3186 | 434.8623 | 497.6652
2772.6135 | 466.8682 | 457.3091 | 434.9085 | 497.8617
2773.6135 | 466.8318 | 457.3087 | 434.9378 | 498.0306
2774.6135 | 466.9259 | 457.3316 | 434.9684 | 497.9152
2775.6135 | 467.1388 | 457.2311 | 435.0339 | 497.7232
2776.6135 | 467.2669 | 457.2768 | 434.9359 | 497.7758
2777.6135 | 467.3021 | 457.3198 | 434.8185 | 495.3958
2778.6135 | 467.2699 | 457.2987 | 434.8437 | 493.923
2779.6135 | 467.2388 | 457.3239 | 434.8818 | 493.7549
2780.6135 | 467.2751 | 457.2891 | 434.8105 | 494.9001
2781.6135 | 467.2676 | 457.3216 | 434.8718 | 494.6965
2782.6135 | 467.3462 | 457.244 | 435.0021 | 494.6393
2783.6135 | 467.3056 | 457.2815 | 434.971 | 494.53
2784.6135 | 467.3989 | 457.2943 | 434.9733 | 494.348
2785.6135 | 467.4702 | 457.3478 | 435.0626 | 494.5721
2786.6135 | 467.4865 | 457.3541 | 435.0839 | 494.5063
2787.6135 | 467.4401 | 457.3133 | 435.1394 | 494.6629
2788.6135 | 467.4429 | 457.3889 | 435.0781 | 494.9209
2789.6135 | 467.3751 | 457.3692 | 435.0791 | 495.0525
2790.6135 | 467.3101 | 457.4277 | 435.1604 | 495.2762
2791.6135 | 467.2481 | 457.4478 | 434.9865 | 495.1002
2792.6135 | 467.2147 | 457.4642 | 435.0171 | 495.1284
2793.6135 | 467.1556 | 457.4592 | 434.9993 | 494.9371
2794.6135 | 467.0921 | 457.3365 | 435.016 | 495.0254
2795.6135 | 467.1493 | 457.4122 | 435.0801 | 494.8819
2796.6135 | 467.181 | 457.4357 | 434.9595 | 494.9444
2797.6135 | 467.1632 | 457.4539 | 434.9974 | 494.7937
2798.6135 | 467.1691 | 457.4218 | 435.0895 | 495.0456
2799.6135 | 467.0691 | 457.3244 | 435.119 | 495.2487
2800.6135 | 467.0759 | 457.3531 | 434.9814 | 495.3695
2801.6135 | 467.1768 | 457.3734 | 434.8171 | 495.1961
2802.6135 | 467.2205 | 457.302 | 434.9497 | 497.3288
2803.6135 | 467.1603 | 457.3371 | 434.9615 | 497.3442
2804.6135 | 467.0609 | 457.3407 | 434.9064 | 497.3005
2805.6135 | 467.1266 | 457.385 | 434.9441 | 497.2454
2806.6135 | 467.0367 | 457.4987 | 434.8366 | 497.4188
2807.6135 | 466.9413 | 457.5734 | 434.9699 | 497.3606
2808.6135 | 466.8458 | 457.4838 | 435.0988 | 497.4733
2809.6135 | 466.817 | 457.5314 | 435.2431 | 497.6119
2810.6135 | 466.8248 | 457.5927 | 435.0974 | 497.4207
2811.6135 | 466.8218 | 457.6432 | 434.9515 | 497.4136
2812.6135 | 466.7607 | 457.6078 | 435.0698 | 497.8296
2813.6135 | 466.7275 | 457.6185 | 434.9832 | 497.6446
2814.6135 | 466.7155 | 457.5309 | 435.1086 | 497.4289
2815.6135 | 466.7153 | 457.4632 | 435.2002 | 497.1168
2816.6135 | 466.671 | 457.5407 | 435.1596 | 497.4282
2817.6135 | 466.6446 | 457.5955 | 435.1052 | 497.5266
2818.6135 | 466.5624 | 457.6081 | 435.1372 | 497.6882
2819.6135 | 466.5119 | 457.5104 | 435.1751 | 498.1268
2820.6135 | 466.4907 | 457.5304 | 435.2792 | 497.9628
2821.6135 | 466.6268 | 457.5487 | 435.1938 | 497.8197
2822.6135 | 466.7164 | 457.5022 | 435.2757 | 497.7631
2823.6135 | 466.7498 | 457.5735 | 435.3394 | 497.7178
2824.6135 | 466.7591 | 457.5864 | 435.5 | 497.7409
2825.6135 | 466.7363 | 457.6473 | 435.2549 | 497.7449
2826.6135 | 466.8148 | 457.696 | 435.309 | 497.7276
2827.6135 | 466.8483 | 457.6574 | 435.2641 | 497.6033
2828.6135 | 466.9629 | 457.6999 | 435.2713 | 497.5002
2829.6135 | 467.0064 | 457.7075 | 435.051 | 497.7798
2830.6135 | 467.0797 | 457.7495 | 435.0912 | 497.6425
2831.6135 | 467.0266 | 457.6973 | 435.2773 | 497.5314
2832.6135 | 466.9927 | 457.6883 | 435.2287 | 497.9885
2833.6135 | 467.0787 | 457.7183 | 435.1647 | 497.9578
2834.6135 | 467.0872 | 457.7134 | 434.9676 | 498.0908
2835.6135 | 467.1392 | 457.7322 | 434.9898 | 497.8135
2836.6135 | 467.0561 | 457.73 | 434.9248 | 497.9732
2837.6135 | 467.0753 | 457.7395 | 434.931 | 498.1211
2838.6135 | 467.0746 | 457.7622 | 435.1911 | 498.5103
2839.6135 | 467.0346 | 457.6532 | 435.0658 | 495.8679
2840.6135 | 466.9946 | 457.6192 | 435.1181 | 493.6228
2841.6135 | 466.9995 | 457.7132 | 435.0609 | 495.5049
2842.6135 | 467.0939 | 457.6968 | 435.1225 | 495.4839
2843.6135 | 467.1389 | 457.7856 | 435.2715 | 495.1675
2844.6135 | 467.2662 | 457.6852 | 435.2809 | 495.2251
2845.6135 | 467.3675 | 457.7271 | 435.3766 | 495.1739
2846.6135 | 467.3709 | 457.7032 | 435.3155 | 495.1511
2847.6135 | 467.3069 | 457.7293 | 435.243 | 495.0478
2848.6135 | 467.2249 | 457.7248 | 435.1285 | 495.1619
2849.6135 | 467.0987 | 457.6828 | 435.2785 | 495.3831
2850.6135 | 467.061 | 457.656 | 435.2467 | 495.2512
2851.6135 | 467.0028 | 457.6953 | 435.2141 | 495.3241
2852.6135 | 466.9484 | 457.6987 | 435.1208 | 495.7098
2853.6135 | 466.9329 | 457.7048 | 435.117 | 495.5809
2854.6135 | 466.9131 | 457.7042 | 435.2806 | 495.4977
2855.6135 | 466.9262 | 457.7734 | 435.4121 | 495.3507
2856.6135 | 466.9169 | 457.7701 | 435.3075 | 495.6957
2857.6135 | 466.8685 | 457.8033 | 435.2957 | 495.5506
2858.6135 | 466.7835 | 457.8807 | 435.3305 | 495.3504
2859.6135 | 466.7767 | 457.8498 | 435.4464 | 493.8714
2860.6135 | 466.8725 | 457.8612 | 435.5479 | 495.5123
2861.6135 | 466.9519 | 457.9169 | 435.6781 | 495.5074
2862.6135 | 466.9788 | 457.7982 | 435.5759 | 495.4681
2863.6135 | 466.9403 | 457.8372 | 435.6071 | 495.6133
2864.6135 | 466.9148 | 457.8048 | 435.5973 | 495.6582
2865.6135 | 466.8621 | 457.6513 | 435.595 | 495.9063
2866.6135 | 466.8485 | 457.7817 | 435.6114 | 495.6428
2867.6135 | 466.9352 | 457.8196 | 435.6491 | 496.2108
2868.6135 | 466.9778 | 457.8961 | 435.6108 | 496.1284
2869.6135 | 467.0393 | 457.8481 | 435.5438 | 496.0624
2870.6135 | 467.0278 | 457.8728 | 435.4643 | 495.844
2871.6135 | 467.1495 | 457.9395 | 435.4836 | 495.4697
2872.6135 | 467.2333 | 457.9163 | 435.5642 | 495.4943
2873.6135 | 467.2837 | 457.9641 | 435.5442 | 495.6887
2874.6135 | 467.2204 | 457.9503 | 435.6003 | 495.455
2875.6135 | 467.1247 | 457.94 | 435.6682 | 495.3704
2876.6135 | 467.1317 | 457.9456 | 435.7743 | 495.5394
2877.6135 | 467.1016 | 457.921 | 435.8266 | 495.3446
2878.6135 | 467.1893 | 457.7437 | 435.7021 | 495.5462
2879.6135 | 467.2373 | 457.7543 | 435.7486 | 495.3652
2880.6135 | 467.2082 | 457.866 | 435.6647 | 495.4337
2881.6135 | 467.1708 | 457.8766 | 435.6456 | 495.4198
2882.6135 | 467.1264 | 457.9353 | 435.5907 | 495.4219
2883.6135 | 467.1966 | 457.9968 | 435.6439 | 495.3352
2884.6135 | 467.3062 | 457.9873 | 435.549 | 495.2298
2885.6135 | 467.3171 | 457.9936 | 435.652 | 495.2741
2886.6135 | 467.2938 | 457.9765 | 435.7506 | 495.1726
2887.6135 | 467.2806 | 458.0038 | 435.6815 | 495.3673
2888.6135 | 467.281 | 458.033 | 435.8201 | 495.3918
2889.6135 | 467.2831 | 458.0434 | 435.9361 | 495.465
2890.6135 | 467.2843 | 458.0354 | 435.9915 | 495.6912
2891.6135 | 467.3856 | 458.0665 | 435.8976 | 495.6935
2892.6135 | 467.5862 | 458.0624 | 436.0178 | 495.8512
2893.6135 | 467.6365 | 458.019 | 435.9987 | 496.0719
2894.6135 | 467.6606 | 457.9855 | 435.8939 | 495.8205
2895.6135 | 467.609 | 458.0811 | 435.8344 | 495.683
2896.6135 | 467.4646 | 458.0363 | 435.8771 | 495.5893
2897.6135 | 467.5209 | 457.952 | 435.8536 | 495.3038
2898.6135 | 467.5223 | 458.0104 | 435.7297 | 495.5274
2899.6135 | 467.5432 | 458.0335 | 435.9552 | 496.4331
2900.6135 | 467.5827 | 458.0591 | 436.0606 | 496.5009
2901.6135 | 467.5536 | 458.1246 | 435.838 | 496.4843
2902.6135 | 467.5665 | 458.0151 | 435.8712 | 496.4692
2903.6135 | 467.5387 | 458.0321 | 435.9194 | 496.5367
2904.6135 | 467.4823 | 457.9843 | 435.9185 | 496.551
2905.6135 | 467.3939 | 458.0616 | 436.0606 | 496.5757
2906.6135 | 467.4001 | 458.1466 | 435.8647 | 497.582
2907.6135 | 467.3087 | 458.0168 | 435.9706 | 497.4328
2908.6135 | 467.2905 | 458.0842 | 435.8043 | 497.7477
2909.6135 | 467.3124 | 458.1507 | 435.7922 | 497.7617
2910.6135 | 467.3849 | 458.1409 | 435.8939 | 497.7742
2911.6135 | 467.1883 | 458.15 | 436.1925 | 497.6918
2912.6135 | 467.0231 | 458.1153 | 436.1252 | 498.1537
2913.6135 | 466.9479 | 458.0607 | 436.1056 | 498.081
2914.6135 | 467.0123 | 458.1309 | 436.0116 | 498.3722
2915.6135 | 467.0762 | 458.1419 | 435.9603 | 498.2081
2916.6135 | 466.9459 | 458.2193 | 436.1747 | 498.4479
2917.6135 | 466.9488 | 458.2457 | 436.1202 | 498.2813
2918.6135 | 467.0601 | 458.2892 | 436.115 | 498.2457
2919.6135 | 467.1133 | 458.3184 | 436.1789 | 498.3385
2920.6135 | 467.0449 | 458.3236 | 436.1661 | 498.2677
2921.6135 | 466.9504 | 458.2189 | 436.1294 | 498.2697
2922.6135 | 466.9261 | 458.2593 | 436.2286 | 498.4282
2923.6135 | 466.9586 | 458.2862 | 436.2428 | 498.5409
2924.6135 | 467.0151 | 458.3324 | 436.3498 | 498.7132
2925.6135 | 466.931 | 458.3541 | 436.2551 | 498.7067
2926.6135 | 466.7337 | 458.3375 | 436.165 | 498.8902
2927.6135 | 466.6518 | 458.2684 | 436.185 | 498.4041
2928.6135 | 466.7045 | 458.2668 | 436.167 | 498.43
2929.6135 | 466.788 | 458.3023 | 436.1762 | 498.4085
2930.6135 | 466.9095 | 458.3663 | 436.1985 | 498.286
2931.6135 | 467.0154 | 458.0775 | 436.0907 | 498.3747
2932.6135 | 467.091 | 458.0899 | 436.1621 | 500.2574
2933.6135 | 467.0892 | 458.1005 | 435.6511 | 498.4463
2934.6135 | 467.0969 | 458.0941 | 435.9563 | 498.3406
2935.6135 | 467.0957 | 458.2202 | 436.1583 | 498.2639
2936.6135 | 467.0798 | 458.2921 | 436.1298 | 498.4684
2937.6135 | 467.0135 | 458.2613 | 436.1102 | 498.3346
2938.6135 | 467.0717 | 458.247 | 436.1005 | 498.0613
2939.6135 | 467.1626 | 458.3043 | 436.1535 | 498.036
2940.6135 | 467.2258 | 458.3855 | 435.9808 | 497.9045
2941.6135 | 467.2718 | 458.3957 | 435.782 | 500.5874
2942.6135 | 467.2499 | 458.3752 | 435.8612 | 500.7294
2943.6135 | 467.3542 | 458.3887 | 436.0966 | 500.8264
2944.6135 | 467.3582 | 458.4152 | 436.1546 | 500.7921
2945.6135 | 467.3109 | 458.3668 | 436.315 | 500.7629
2946.6135 | 467.331 | 458.3588 | 436.3823 | 500.2859
2947.6135 | 467.3632 | 458.4117 | 436.2836 | 500.2337
2948.6135 | 467.3283 | 458.3781 | 436.2346 | 497.9982
2949.6135 | 467.3212 | 458.3765 | 436.324 | 498.2389
2950.6135 | 467.3539 | 458.3397 | 436.2663 | 498.2703
2951.6135 | 467.2506 | 458.4094 | 436.3954 | 498.3191
2952.6135 | 467.142 | 458.447 | 436.1925 | 498.1381
2953.6135 | 467.1886 | 458.4232 | 436.2708 | 498.2224
2954.6135 | 467.2596 | 458.4563 | 436.2189 | 497.9701
2955.6135 | 467.178 | 458.516 | 436.2684 | 497.6201
2956.6135 | 467.1065 | 458.4203 | 436.3063 | 497.4786
2957.6135 | 467.1319 | 458.4695 | 436.3381 | 497.5333
2958.6135 | 467.0618 | 458.5055 | 436.2799 | 497.8758
2959.6135 | 467.084 | 458.465 | 436.3265 | 497.9014
2960.6135 | 467.094 | 458.4565 | 436.4214 | 497.6999
2961.6135 | 467.043 | 458.4574 | 436.506 | 497.5861
2962.6135 | 467.0491 | 458.3859 | 436.3229 | 497.5057
2963.6135 | 466.9814 | 458.3889 | 436.3641 | 497.6927
2964.6135 | 466.9497 | 458.3652 | 436.3829 | 497.6464
2965.6135 | 466.93 | 458.467 | 436.5075 | 497.4351
2966.6135 | 466.904 | 458.4954 | 436.4798 | 497.2294
2967.6135 | 466.8289 | 458.484 | 436.5007 | 496.0041
2968.6135 | 466.9522 | 458.4645 | 436.4724 | 495.5855
2969.6135 | 466.9817 | 458.4252 | 436.4302 | 497.4867
2970.6135 | 467.0193 | 458.5146 | 436.4115 | 497.5543
2971.6135 | 466.9026 | 458.5402 | 436.4953 | 495.6373
2972.6135 | 466.8861 | 458.5671 | 436.5837 | 495.4517
2973.6135 | 466.8764 | 458.5502 | 436.6521 | 495.4617
2974.6135 | 466.9158 | 458.5217 | 436.6682 | 495.6372
2975.6135 | 466.821 | 458.4917 | 436.744 | 495.9206
2976.6135 | 466.7442 | 458.5101 | 436.7431 | 495.8641
2977.6135 | 466.7397 | 458.4701 | 436.6344 | 495.5123
2978.6135 | 466.691 | 458.5112 | 436.5938 | 495.545
2979.6135 | 466.6481 | 458.5333 | 436.663 | 495.4771
2980.6135 | 466.7357 | 458.5559 | 436.6633 | 495.3761
2981.6135 | 466.7041 | 458.571 | 436.5555 | 495.1525
2982.6135 | 466.6953 | 458.6254 | 436.5475 | 495.0064
2983.6135 | 466.7319 | 458.542 | 436.5651 | 494.7669
2984.6135 | 466.6145 | 458.5695 | 436.5712 | 495.0052
2985.6135 | 466.5805 | 458.5649 | 436.5716 | 495.2753
2986.6135 | 466.6062 | 458.5986 | 436.5222 | 497.2403
2987.6135 | 466.7214 | 458.6023 | 436.654 | 497.1125
2988.6135 | 466.7896 | 458.5382 | 436.6287 | 496.9768
2989.6135 | 466.7213 | 458.5054 | 436.7579 | 496.7877
2990.6135 | 466.6591 | 458.5289 | 436.6716 | 496.8714
2991.6135 | 466.8073 | 458.4709 | 436.6182 | 496.8399
2992.6135 | 466.8441 | 458.5011 | 436.6929 | 496.5713
2993.6135 | 466.8467 | 458.4657 | 436.6816 | 496.9538
2994.6135 | 466.9097 | 458.5638 | 436.5073 | 496.9104
2995.6135 | 466.9707 | 458.5802 | 436.5001 | 497.1358
2996.6135 | 467.0297 | 458.5827 | 436.628 | 497.183
2997.6135 | 467.0453 | 458.6345 | 436.6182 | 497.0848
2998.6135 | 466.909 | 458.6261 | 436.7131 | 496.7435
2999.6135 | 466.9044 | 458.6172 | 436.5583 | 496.7385
3000.6135 | 466.8698 | 458.4746 | 436.2844 | 497.0002
3001.6135 | 466.8037 | 458.4319 | 436.5448 | 496.998
3002.6135 | 466.8303 | 458.5278 | 436.4807 | 497.0456
3003.6135 | 466.8826 | 458.5539 | 436.439 | 497.1949
3004.6135 | 466.8875 | 458.6078 | 436.6316 | 497.4177
3005.6135 | 466.8595 | 458.6285 | 436.707 | 497.7733
3006.6135 | 466.8823 | 458.5767 | 436.5105 | 500.1467
3007.6135 | 466.9483 | 458.5476 | 436.5536 | 499.406
3008.6135 | 467.0878 | 458.6374 | 436.6217 | 499.8036
3009.6135 | 467.2193 | 458.5686 | 436.652 | 496.9411
3010.6135 | 467.3766 | 458.5919 | 436.834 | 495.2344
3011.6135 | 467.3683 | 458.6952 | 436.8262 | 495.3207
3012.6135 | 467.2488 | 458.737 | 436.7756 | 495.2998
3013.6135 | 467.3271 | 458.7282 | 436.7999 | 495.2828
3014.6135 | 467.4024 | 458.7536 | 436.7454 | 495.8317
3015.6135 | 467.3902 | 458.744 | 436.7691 | 495.6388
3016.6135 | 467.3489 | 458.7246 | 436.8706 | 495.3287
3017.6135 | 467.3522 | 458.7451 | 436.6399 | 495.0727
3018.6135 | 467.5055 | 458.7667 | 436.7919 | 494.983
3019.6135 | 467.4531 | 458.7866 | 436.9235 | 494.8366
3020.6135 | 467.3617 | 458.7368 | 437.0218 | 494.8179
3021.6135 | 467.4036 | 458.6627 | 436.9742 | 495.0226
3022.6135 | 467.4876 | 458.5116 | 437 | 494.9995
3023.6135 | 467.4732 | 458.5726 | 436.97 | 494.9714
3024.6135 | 467.414 | 458.5523 | 436.9263 | 494.8699
3025.6135 | 467.449 | 458.5601 | 436.6432 | 494.8846
3026.6135 | 467.5267 | 458.675 | 436.7752 | 494.703
3027.6135 | 467.6435 | 458.6504 | 436.8901 | 494.8885
3028.6135 | 467.6303 | 458.6905 | 436.924 | 495.2896
3029.6135 | 467.721 | 458.7106 | 436.9369 | 495.4923
3030.6135 | 467.7306 | 458.6907 | 437.1173 | 495.0926
3031.6135 | 467.6745 | 458.7382 | 437.099 | 494.9196
3032.6135 | 467.6431 | 458.7558 | 437.0396 | 495.007
3033.6135 | 467.5192 | 458.7377 | 436.9184 | 495.4309
3034.6135 | 467.4793 | 458.7249 | 436.9977 | 495.5032
3035.6135 | 467.4439 | 458.7995 | 437.0924 | 495.4457
3036.6135 | 467.4747 | 458.8302 | 437.1332 | 495.6303
3037.6135 | 467.4508 | 458.8158 | 437.0757 | 495.6701
3038.6135 | 467.4362 | 458.8232 | 436.9469 | 495.1743
3039.6135 | 467.4485 | 458.8567 | 437.0816 | 495.4199
3040.6135 | 467.4777 | 458.8588 | 437.0095 | 495.3078
3041.6135 | 467.5735 | 458.8932 | 437.0393 | 495.2875
3042.6135 | 467.5794 | 458.921 | 437.1864 | 495.3138
3043.6135 | 467.6322 | 458.8763 | 437.2574 | 495.0819
3044.6135 | 467.6354 | 458.8067 | 437.0931 | 495.1549
3045.6135 | 467.4615 | 458.7442 | 437.2081 | 495.004
3046.6135 | 467.3972 | 458.7985 | 437.1144 | 495.0079
3047.6135 | 467.4121 | 458.8423 | 437.0454 | 494.9102
3048.6135 | 467.3895 | 458.8425 | 437.0727 | 495.7106
3049.6135 | 467.3832 | 458.9422 | 437.1382 | 495.9127
3050.6135 | 467.3656 | 458.9241 | 437.1026 | 495.6868
3051.6135 | 467.3036 | 458.9316 | 437.0721 | 495.2224
3052.6135 | 467.2687 | 458.9559 | 436.9917 | 495.1788
3053.6135 | 467.2348 | 458.964 | 436.7635 | 495.207
3054.6135 | 467.1429 | 458.9787 | 436.9165 | 494.8415
3055.6135 | 467.1276 | 458.9424 | 436.9397 | 494.935
3056.6135 | 467.1133 | 458.9916 | 437.0701 | 494.9687
3057.6135 | 467.0326 | 459.0357 | 437.1709 | 494.9543
3058.6135 | 467.0077 | 459.0323 | 437.1385 | 495.3138
3059.6135 | 467.0564 | 458.9941 | 437.0986 | 494.9733
3060.6135 | 466.9809 | 459.0419 | 437.1587 | 494.5181
3061.6135 | 466.9481 | 459.0174 | 437.2485 | 494.5496
3062.6135 | 467.0356 | 459.0735 | 437.0997 | 494.413
3063.6135 | 467.1098 | 459.1182 | 436.8963 | 494.5465
3064.6135 | 467.1072 | 459.071 | 436.7859 | 494.8247
3065.6135 | 466.9958 | 459.0389 | 436.9143 | 494.7088
3066.6135 | 467.0625 | 459.0859 | 437.1676 | 494.7252
3067.6135 | 467.0371 | 459.0954 | 437.0922 | 494.635
3068.6135 | 466.9773 | 459.1448 | 437.1318 | 494.5601
3069.6135 | 466.8905 | 459.138 | 437.1279 | 495.4042
3070.6135 | 466.9241 | 459.1768 | 437.2295 | 495.0626
3071.6135 | 467.0047 | 459.1681 | 437.2706 | 495.2473
3072.6135 | 467.1708 | 459.073 | 437.2601 | 494.7083
3073.6135 | 467.1864 | 459.0905 | 437.168 | 495.1139
3074.6135 | 467.1921 | 459.02 | 437.2655 | 495.42
3075.6135 | 467.2312 | 459.0963 | 437.1812 | 494.6776
3076.6135 | 467.2645 | 459.0751 | 437.2383 | 495.7664
3077.6135 | 467.2599 | 459.1075 | 437.3389 | 495.4228
3078.6135 | 467.2759 | 459.2112 | 437.3245 | 495.4631
3079.6135 | 467.363 | 459.1768 | 437.3407 | 494.9117
3080.6135 | 467.353 | 459.1463 | 437.4123 | 494.9088
3081.6135 | 467.2966 | 459.1183 | 437.3076 | 494.5923
3082.6135 | 467.2529 | 459.1835 | 437.2451 | 494.9474
3083.6135 | 467.1973 | 459.216 | 437.2257 | 495.0649
3084.6135 | 467.2207 | 459.1722 | 437.3188 | 495.7524
3085.6135 | 467.1145 | 459.1529 | 437.27 | 495.4732
3086.6135 | 467.1573 | 459.1257 | 437.2448 | 495.7006
3087.6135 | 467.1922 | 459.1079 | 437.2555 | 495.4653
3088.6135 | 467.2649 | 459.1135 | 437.1256 | 496.5295
3089.6135 | 467.2722 | 459.2315 | 437.2793 | 495.3584
3090.6135 | 467.2034 | 459.2361 | 437.3151 | 495.1356
3091.6135 | 467.1292 | 459.2503 | 436.9471 | 495.5857
3092.6135 | 466.9882 | 459.2912 | 437.0931 | 495.3508
3093.6135 | 466.9559 | 459.2942 | 437.1622 | 495.2844
3094.6135 | 466.9566 | 459.3023 | 437.3021 | 495.3838
3095.6135 | 466.9372 | 459.3157 | 437.3101 | 495.4097
3096.6135 | 466.9007 | 459.2984 | 437.2411 | 495.1973
3097.6135 | 466.9376 | 459.3405 | 437.2481 | 494.6276
3098.6135 | 466.9204 | 459.3044 | 437.3901 | 494.9187
3099.6135 | 466.8633 | 459.2985 | 437.1985 | 494.5376
3100.6135 | 466.8249 | 459.345 | 437.1538 | 494.5878
3101.6135 | 466.9472 | 459.3862 | 437.2276 | 494.5776
3102.6135 | 467.0639 | 459.3697 | 437.3008 | 494.7317
3103.6135 | 467.0361 | 459.3944 | 437.3399 | 495.4307
3104.6135 | 466.9079 | 459.4208 | 437.2618 | 495.41
3105.6135 | 466.8031 | 459.4268 | 437.3096 | 495.1749
3106.6135 | 466.8033 | 459.4048 | 437.3401 | 495.629
3107.6135 | 466.767 | 459.3704 | 437.4815 | 496.2697
3108.6135 | 466.7513 | 459.3745 | 437.5333 | 495.5471
3109.6135 | 466.7454 | 459.3868 | 437.2124 | 495.5284
3110.6135 | 466.7777 | 459.4263 | 437.1632 | 495.1179
3111.6135 | 466.9472 | 459.367 | 437.2518 | 494.9836
3112.6135 | 466.9446 | 459.3644 | 437.3458 | 496.5703
3113.6135 | 466.9106 | 459.3257 | 437.2947 | 497.4364
3114.6135 | 466.8643 | 459.3077 | 437.2749 | 495.9232
3115.6135 | 466.7987 | 459.3694 | 437.273 | 495.6745
3116.6135 | 466.7079 | 459.4656 | 437.3549 | 496.5113
3117.6135 | 466.6774 | 459.5144 | 437.2678 | 496.3911
3118.6135 | 466.6359 | 459.5091 | 437.1856 | 496.4502
3119.6135 | 466.608 | 459.462 | 437.2576 | 496.5326
3120.6135 | 466.6481 | 459.4255 | 437.2871 | 496.6036
3121.6135 | 466.7475 | 459.361 | 437.2876 | 496.873
3122.6135 | 466.6949 | 459.3291 | 437.3167 | 498.4321
3123.6135 | 466.7575 | 459.3899 | 437.3405 | 498.3286
3124.6135 | 466.8014 | 459.4192 | 437.2818 | 498.4684
3125.6135 | 466.8154 | 459.3467 | 437.2615 | 498.5161
3126.6135 | 466.7778 | 459.3773 | 437.3246 | 499.2399
3127.6135 | 466.8079 | 459.4745 | 437.1573 | 498.8805
3128.6135 | 466.7786 | 459.4867 | 437.1702 | 499.121
3129.6135 | 466.756 | 459.4113 | 437.4415 | 499.1483
3130.6135 | 466.6937 | 459.4619 | 437.4376 | 498.9833
3131.6135 | 466.674 | 459.4898 | 437.3801 | 498.8993
3132.6135 | 466.7511 | 459.5514 | 437.3914 | 498.7328
3133.6135 | 466.7832 | 459.4676 | 437.4313 | 499.0604
3134.6135 | 466.7653 | 459.521 | 437.4707 | 498.6796
3135.6135 | 466.7143 | 459.5669 | 437.4459 | 496.4886
3136.6135 | 466.7408 | 459.6031 | 437.2011 | 496.9786
3137.6135 | 466.9165 | 459.6071 | 437.1831 | 496.4005
3138.6135 | 467.0018 | 459.58 | 437.2227 | 495.978
3139.6135 | 467.1467 | 459.5566 | 437.2953 | 495.9109
3140.6135 | 467.1785 | 459.5911 | 437.2403 | 497.2673
3141.6135 | 467.0622 | 459.5956 | 437.5645 | 496.8542
3142.6135 | 467.0806 | 459.6329 | 437.5112 | 496.8698
3143.6135 | 467.2497 | 459.5702 | 437.463 | 496.9252
3144.6135 | 467.4313 | 459.5129 | 437.4425 | 496.5936
3145.6135 | 467.4304 | 459.5241 | 437.5425 | 497.1225
3146.6135 | 467.422 | 459.5173 | 437.59 | 498.18
3147.6135 | 467.5327 | 459.4513 | 437.5458 | 498.4827
3148.6135 | 467.5691 | 459.5363 | 437.5901 | 497.5252
3149.6135 | 467.5827 | 459.5962 | 437.5927 | 501.0239
3150.6135 | 467.6078 | 459.6422 | 437.4344 | 500.9333
3151.6135 | 467.6374 | 459.63 | 437.3519 | 500.8803
3152.6135 | 467.5985 | 459.6327 | 437.3975 | 500.6016
3153.6135 | 467.5892 | 459.6103 | 437.5941 | 500.4948
3154.6135 | 467.7226 | 459.6038 | 437.6783 | 500.4717
3155.6135 | 467.6358 | 459.6224 | 437.6803 | 500.5765
3156.6135 | 467.5471 | 459.6327 | 437.661 | 500.9077
3157.6135 | 467.465 | 459.653 | 437.6277 | 495.615
3158.6135 | 467.4252 | 459.7255 | 437.6704 | 495.5434
3159.6135 | 467.2871 | 459.7337 | 437.7407 | 495.5426
3160.6135 | 467.3078 | 459.6801 | 437.5056 | 495.2158
3161.6135 | 467.2176 | 459.6136 | 437.5485 | 495.2404
3162.6135 | 467.0708 | 459.6942 | 437.5344 | 495.1442
3163.6135 | 466.9839 | 459.5773 | 437.6165 | 494.9204
3164.6135 | 466.9707 | 459.6475 | 437.5951 | 495.214
3165.6135 | 466.9508 | 459.6755 | 437.7229 | 495.0337
3166.6135 | 466.9313 | 459.7199 | 437.7822 | 495.9331
3167.6135 | 466.9969 | 459.6898 | 437.7548 | 495.3173
3168.6135 | 466.9559 | 459.7189 | 437.6915 | 495.6266
3169.6135 | 466.9889 | 459.7279 | 437.6349 | 495.6973
3170.6135 | 467.0769 | 459.7666 | 437.6979 | 495.835
3171.6135 | 467.1905 | 459.7589 | 437.7533 | 495.4021
3172.6135 | 467.2404 | 459.7715 | 437.848 | 495.5136
3173.6135 | 467.3295 | 459.7556 | 437.7242 | 495.7074
3174.6135 | 467.3799 | 459.7263 | 437.709 | 495.8412
3175.6135 | 467.4844 | 459.6723 | 437.7763 | 495.4431
3176.6135 | 467.5288 | 459.7072 | 437.804 | 495.8761
3177.6135 | 467.5528 | 459.6908 | 437.7876 | 495.7695
3178.6135 | 467.6025 | 459.6615 | 437.8114 | 495.7787
3179.6135 | 467.6267 | 459.6286 | 437.8603 | 495.2274
3180.6135 | 467.5825 | 459.6354 | 437.9606 | 495.8981
3181.6135 | 467.5346 | 459.6518 | 437.8554 | 495.936
3182.6135 | 467.4327 | 459.7013 | 437.849 | 496.4729
3183.6135 | 467.3913 | 459.6577 | 437.8303 | 495.4884
3184.6135 | 467.3648 | 459.6178 | 437.767 | 494.9975
3185.6135 | 467.4002 | 459.6002 | 437.8603 | 495.178
3186.6135 | 467.3991 | 459.6586 | 437.6228 | 495.3133
3187.6135 | 467.4318 | 459.7344 | 437.8145 | 495.345
3188.6135 | 467.4692 | 459.7649 | 437.8218 | 495.9477
3189.6135 | 467.4283 | 459.7787 | 437.9202 | 496.0964
3190.6135 | 467.47 | 459.7211 | 437.9322 | 495.6722
3191.6135 | 467.5277 | 459.78 | 437.9927 | 495.6055
3192.6135 | 467.5351 | 459.7932 | 438.0124 | 496.5913
3193.6135 | 467.4542 | 459.7643 | 437.9391 | 495.4621
3194.6135 | 467.4065 | 459.7055 | 437.9637 | 495.9663
3195.6135 | 467.4787 | 459.6857 | 437.964 | 496.3166
3196.6135 | 467.4906 | 459.7854 | 437.9755 | 496.518
3197.6135 | 467.4975 | 459.7898 | 437.856 | 495.92
3198.6135 | 467.4484 | 459.7944 | 437.8599 | 495.7452
3199.6135 | 467.2766 | 459.8226 | 437.9423 | 495.4965
3200.6135 | 467.2971 | 459.8239 | 437.9951 | 496.0162
3201.6135 | 467.2642 | 459.8684 | 438.0177 | 496.1854
3202.6135 | 467.2322 | 459.8115 | 437.9858 | 495.4989
3203.6135 | 467.1579 | 459.8243 | 437.9719 | 495.7959
3204.6135 | 467.1746 | 459.8166 | 438.1361 | 496.0257
3205.6135 | 467.1917 | 459.8321 | 438.082 | 495.4818
3206.6135 | 467.3127 | 459.8526 | 438.0108 | 495.9591
3207.6135 | 467.4126 | 459.877 | 437.9624 | 495.9984
3208.6135 | 467.349 | 459.9026 | 438.0107 | 496.1751
3209.6135 | 467.2363 | 459.8988 | 438.0119 | 495.9827
3210.6135 | 467.2383 | 459.8218 | 438.1805 | 495.7912
3211.6135 | 467.1755 | 459.8595 | 438.1722 | 495.94
3212.6135 | 467.1384 | 459.8833 | 438.1436 | 495.9592
3213.6135 | 467.1265 | 459.8789 | 438.0823 | 495.8288
3214.6135 | 467.1419 | 459.927 | 438.0858 | 495.8303
3215.6135 | 467.0903 | 459.9344 | 438.0621 | 495.8087
3216.6135 | 467.0517 | 459.8775 | 438.2481 | 495.9675
3217.6135 | 467.1075 | 459.9104 | 438.1159 | 495.8453
3218.6135 | 467.1897 | 459.9543 | 438.0546 | 495.7263
3219.6135 | 467.2685 | 459.9592 | 438.0245 | 494.9361
3220.6135 | 467.2905 | 459.8386 | 438.0226 | 495.6078
3221.6135 | 467.2891 | 459.8292 | 438.133 | 495.7049
3222.6135 | 467.3574 | 459.8304 | 438.2019 | 495.3808
3223.6135 | 467.4053 | 459.8778 | 438.166 | 495.2041
3224.6135 | 467.4992 | 459.9163 | 438.138 | 495.3621
3225.6135 | 467.5687 | 459.9684 | 438.1669 | 494.9033
3226.6135 | 467.5501 | 459.995 | 437.9218 | 495.5271
3227.6135 | 467.5482 | 460.0085 | 438.0129 | 495.0634
3228.6135 | 467.485 | 460.0483 | 437.8702 | 495.8294
3229.6135 | 467.4814 | 460.105 | 438.0724 | 496.2095
3230.6135 | 467.4811 | 460.0742 | 437.5435 | 495.4904
3231.6135 | 467.4672 | 460.1045 | 437.813 | 495.2422
3232.6135 | 467.4651 | 460.0941 | 438.0107 | 495.1848
3233.6135 | 467.3529 | 460.1084 | 438.0943 | 495.1379
3234.6135 | 467.3191 | 460.0954 | 437.8776 | 494.8601
3235.6135 | 467.2142 | 460.0137 | 437.8531 | 494.7011
3236.6135 | 467.1766 | 460.0137 | 437.9655 | 495.439
3237.6135 | 467.1587 | 460.117 | 438.0042 | 495.0452
3238.6135 | 467.1133 | 460.1881 | 437.8766 | 495.3035
3239.6135 | 467.1806 | 460.1737 | 437.9542 | 495.0907
3240.6135 | 467.2327 | 460.1178 | 438.0664 | 495.0801
3241.6135 | 467.169 | 460.0515 | 438.142 | 495.2432
3242.6135 | 467.0847 | 460.0827 | 437.8554 | 495.2309
3243.6135 | 466.9976 | 460.0665 | 437.8702 | 495.112
3244.6135 | 466.9737 | 460.1409 | 437.9922 | 494.989
3245.6135 | 466.9377 | 460.1482 | 438.0508 | 494.8837
3246.6135 | 466.9142 | 460.2072 | 437.9808 | 495.8822
3247.6135 | 466.8967 | 460.2363 | 438.0414 | 495.7071
3248.6135 | 466.8991 | 460.2347 | 437.98 | 495.8574
3249.6135 | 466.8576 | 460.2039 | 437.9694 | 495.8567
3250.6135 | 466.779 | 460.1862 | 438.0766 | 495.3408
3251.6135 | 466.8361 | 460.1601 | 438.0379 | 494.9575
3252.6135 | 466.8824 | 460.2067 | 438.1693 | 494.7593
3253.6135 | 466.8884 | 460.2388 | 438.1107 | 495.6257
3254.6135 | 466.8147 | 460.1869 | 438.1121 | 495.7934
3255.6135 | 466.8388 | 460.1454 | 438.0713 | 496.0012
3256.6135 | 466.8128 | 460.1978 | 438.1631 | 495.7647
3257.6135 | 466.7161 | 460.2649 | 438.2143 | 495.8658
3258.6135 | 466.6843 | 460.1747 | 438.0456 | 496.0505
3259.6135 | 466.6994 | 460.1155 | 437.9289 | 495.8766
3260.6135 | 466.6317 | 460.1362 | 437.9299 | 495.6703
3261.6135 | 466.5882 | 460.0947 | 438.008 | 495.6447
3262.6135 | 466.585 | 460.1399 | 438.1256 | 495.5579
3263.6135 | 466.5576 | 460.1784 | 438.1868 | 494.5761
3264.6135 | 466.7489 | 460.1646 | 438.1649 | 495.364
3265.6135 | 467.7405 | 460.1404 | 438.1962 | 495.0444
3266.6135 | 469.4341 | 460.2544 | 438.2218 | 495.4355
3267.6135 | 471.7671 | 460.3723 | 438.2737 | 495.6258
3268.6135 | 474.5647 | 460.5271 | 438.4755 | 495.4105
3269.6135 | 477.6676 | 460.622 | 438.4518 | 495.1436
3270.6135 | 481.1175 | 460.7661 | 438.6016 | 495.0334
3271.6135 | 484.8487 | 460.891 | 438.6752 | 495.0635
3272.6135 | 488.7295 | 461.0602 | 438.9499 | 494.9128
3273.6135 | 492.5014 | 461.2045 | 439.2248 | 494.6393
3274.6135 | 495.9798 | 461.4127 | 439.1223 | 494.8273
3275.6135 | 499.077 | 461.6248 | 439.3746 | 495.074
3276.6135 | 501.6108 | 461.7803 | 439.5028 | 495.0432
3277.6135 | 503.6385 | 461.936 | 439.7526 | 495.121
3278.6135 | 505.3363 | 462.1299 | 439.9644 | 494.9234
3279.6135 | 506.5687 | 462.1819 | 440.2727 | 495.1029
3280.6135 | 507.3595 | 462.33 | 440.4396 | 495.113
3281.6135 | 507.8309 | 462.5413 | 440.2626 | 495.2892
3282.6135 | 508.0279 | 462.5933 | 440.6894 | 495.3987
3283.6135 | 508.0976 | 462.7026 | 440.602 | 495.5272
3284.6135 | 508.0235 | 462.934 | 440.9123 | 495.6973
3285.6135 | 507.8165 | 463.0566 | 440.9684 | 495.7181
3286.6135 | 507.413 | 463.1464 | 441.1495 | 495.731
3287.6135 | 506.9286 | 463.3344 | 441.3546 | 496.029
3288.6135 | 506.4285 | 463.4599 | 441.5631 | 496.1327
3289.6135 | 505.7836 | 463.6557 | 441.6892 | 496.1429
3290.6135 | 505.1827 | 463.7715 | 441.7575 | 496.2844
3291.6135 | 504.357 | 463.8815 | 441.8522 | 496.4514
3292.6135 | 503.6713 | 463.999 | 441.9378 | 496.8049
3293.6135 | 502.9804 | 464.1618 | 441.9521 | 496.903
3294.6135 | 502.3444 | 464.2054 | 442.0751 | 497.0499
3295.6135 | 501.7905 | 464.3564 | 442.1845 | 497.1666
3296.6135 | 501.2429 | 464.4685 | 442.2949 | 497.3378
3297.6135 | 500.6814 | 464.558 | 442.3716 | 497.2918
3298.6135 | 500.1297 | 464.6498 | 442.5093 | 497.4117
3299.6135 | 499.8379 | 464.7673 | 442.6121 | 497.5296
3300.6135 | 499.5072 | 464.8173 | 442.6915 | 497.5358
3301.6135 | 499.1496 | 464.8868 | 442.7212 | 497.7607
3302.6135 | 498.7354 | 464.9941 | 442.7281 | 497.7122
3303.6135 | 498.3994 | 465.1555 | 442.849 | 497.7019
3304.6135 | 498.1659 | 465.181 | 442.9268 | 497.749
3305.6135 | 497.989 | 465.2017 | 443.0756 | 497.7947
3306.6135 | 497.7103 | 465.3035 | 443.1321 | 497.8341
3307.6135 | 497.4602 | 465.3992 | 443.2393 | 497.9545
3308.6135 | 497.17 | 465.4864 | 443.3038 | 497.8329
3309.6135 | 497.0531 | 465.6033 | 443.2227 | 498.0166
3310.6135 | 496.9651 | 465.7206 | 443.4108 | 498.4914
3311.6135 | 496.8784 | 465.8181 | 443.4321 | 498.6062
3312.6135 | 496.8326 | 465.9398 | 443.5819 | 498.5632
3313.6135 | 496.7654 | 466.0102 | 443.5888 | 498.4965
3314.6135 | 496.7695 | 466.0983 | 443.6473 | 498.5938
3315.6135 | 496.6289 | 466.2107 | 443.8004 | 498.7493
3316.6135 | 496.5901 | 466.2854 | 443.9507 | 498.609
3317.6135 | 496.4184 | 466.3477 | 444.002 | 498.2223
3318.6135 | 496.217 | 466.4498 | 444.0903 | 498.5129
3319.6135 | 496.1526 | 466.5275 | 444.1155 | 498.3459
3320.6135 | 496.1548 | 466.6545 | 444.272 | 498.2017
3321.6135 | 496.0949 | 466.7574 | 444.1869 | 498.1319
3322.6135 | 496.1881 | 466.828 | 444.3903 | 498.1407
3323.6135 | 496.2922 | 466.9316 | 444.4217 | 498.1036
3324.6135 | 496.3594 | 467.0103 | 444.4343 | 498.217
3325.6135 | 496.3715 | 467.0537 | 444.5782 | 498.2379
3326.6135 | 496.4877 | 467.0713 | 444.6918 | 498.0976
3327.6135 | 496.5879 | 467.2653 | 444.7232 | 498.1168
3328.6135 | 496.4194 | 467.3697 | 444.6124 | 498.3296
3329.6135 | 496.4604 | 467.4971 | 444.586 | 498.2888
3330.6135 | 496.5639 | 467.5288 | 444.878 | 498.2219
3331.6135 | 496.7047 | 467.5997 | 445.0623 | 498.0735
3332.6135 | 496.787 | 467.7266 | 445.1556 | 498.0575
3333.6135 | 496.9157 | 467.7737 | 445.1504 | 498.2334
3334.6135 | 497.0395 | 467.8552 | 445.2879 | 498.4328
3335.6135 | 497.0452 | 467.9945 | 445.4082 | 498.3817
3336.6135 | 497.0452 | 468.0786 | 445.4301 | 498.3798
3337.6135 | 497.1591 | 468.1195 | 445.686 | 498.493
3338.6135 | 497.3896 | 468.1747 | 445.7313 | 498.7214
3339.6135 | 497.4973 | 468.2706 | 445.8264 | 498.99
3340.6135 | 497.6692 | 468.3812 | 445.7466 | 498.4101
3341.6135 | 497.577 | 468.4781 | 445.8282 | 498.9987
3342.6135 | 497.4351 | 468.3552 | 445.8819 | 498.7885
3343.6135 | 497.3962 | 468.4981 | 445.9723 | 498.7712
3344.6135 | 497.4793 | 468.6608 | 446.1385 | 499.0499
3345.6135 | 497.4369 | 468.7897 | 446.191 | 499.1658
3346.6135 | 497.4404 | 468.8262 | 446.2356 | 498.8247
3347.6135 | 497.4792 | 468.898 | 446.4157 | 498.9581
3348.6135 | 497.4626 | 468.9923 | 446.3542 | 499.0401
3349.6135 | 497.2978 | 469.1047 | 446.4597 | 499.1381
3350.6135 | 497.3353 | 469.1918 | 446.4504 | 498.9647
3351.6135 | 497.2108 | 469.2636 | 446.6128 | 498.9656
3352.6135 | 497.131 | 469.2455 | 446.6425 | 499.0061
3353.6135 | 497.0988 | 469.3798 | 446.6758 | 499.193
3354.6135 | 496.9966 | 469.4192 | 446.7831 | 499.2762
3355.6135 | 496.9761 | 469.5562 | 446.8362 | 499.3878
3356.6135 | 497.0123 | 469.6613 | 446.7504 | 499.5255
3357.6135 | 496.9459 | 469.6938 | 446.8923 | 499.6523
3358.6135 | 497.0213 | 469.7009 | 446.687 | 499.7763
3359.6135 | 497.1109 | 469.7821 | 446.8865 | 499.6669
3360.6135 | 497.1423 | 469.8183 | 447.1869 | 499.8756
3361.6135 | 497.1505 | 469.8959 | 447.2733 | 499.9644
3362.6135 | 497.2023 | 469.9261 | 447.217 | 499.8808
3363.6135 | 497.1809 | 469.9874 | 447.1095 | 500.0068
3364.6135 | 497.3038 | 470.1322 | 447.1122 | 500.0151
3365.6135 | 497.4638 | 470.253 | 447.1589 | 500.109
3366.6135 | 497.3272 | 470.373 | 447.0851 | 500.0876
3367.6135 | 497.3042 | 470.4349 | 447.1749 | 500.2833
3368.6135 | 497.411 | 470.4584 | 447.2434 | 500.451
3369.6135 | 497.452 | 470.5076 | 447.2948 | 500.9531
3370.6135 | 497.5529 | 470.4631 | 447.2357 | 501.0536
3371.6135 | 497.6802 | 470.617 | 447.4011 | 500.9325
3372.6135 | 497.8297 | 470.707 | 447.5832 | 500.8265
3373.6135 | 497.9104 | 470.7582 | 447.789 | 500.8844
3374.6135 | 498.0691 | 470.8249 | 447.8395 | 500.7439
3375.6135 | 498.2065 | 470.889 | 447.8853 | 500.9019
3376.6135 | 498.342 | 470.9704 | 447.8925 | 500.866
3377.6135 | 498.3394 | 471.0783 | 447.766 | 500.9046
3378.6135 | 498.2585 | 471.1362 | 447.8491 | 500.9843
3379.6135 | 498.3015 | 471.2418 | 448.0357 | 501.0241
3380.6135 | 498.3495 | 471.261 | 448.1963 | 501.2294
3381.6135 | 498.4547 | 471.268 | 448.0343 | 501.4049
3382.6135 | 498.5345 | 471.2613 | 448.0383 | 501.2929
3383.6135 | 498.476 | 471.4114 | 448.0512 | 501.4555
3384.6135 | 498.587 | 471.487 | 447.8178 | 501.6182
3385.6135 | 498.4142 | 471.5691 | 448.1995 | 501.384
3386.6135 | 498.2974 | 471.6816 | 448.3876 | 501.6189
3387.6135 | 498.3417 | 471.7096 | 448.5138 | 501.602
3388.6135 | 498.2927 | 471.8529 | 448.6288 | 504.7947
3389.6135 | 498.2225 | 471.744 | 448.6657 | 508.679
3390.6135 | 498.208 | 471.866 | 448.7373 | 508.4924
3391.6135 | 498.186 | 471.9626 | 448.7601 | 508.4555
3392.6135 | 498.0659 | 472.0797 | 448.7479 | 508.5401
3393.6135 | 498.0646 | 472.2126 | 448.8144 | 508.4017
3394.6135 | 497.9912 | 472.2426 | 448.9347 | 508.6108
3395.6135 | 497.8506 | 472.3295 | 448.8795 | 508.5651
3396.6135 | 497.7748 | 472.444 | 449.0515 | 508.456
3397.6135 | 497.7701 | 472.5 | 449.0475 | 508.4383
3398.6135 | 497.9183 | 472.4812 | 449.2431 | 508.4259
3399.6135 | 497.9617 | 472.5792 | 449.4385 | 508.3535
3400.6135 | 497.8501 | 472.6681 | 449.6472 | 508.3329
3401.6135 | 497.8798 | 472.714 | 449.7858 | 507.7957
3402.6135 | 497.815 | 472.857 | 449.7365 | 508.2431
3403.6135 | 497.944 | 472.8436 | 449.8584 | 508.0392
3404.6135 | 497.856 | 472.9467 | 449.8374 | 507.8344
3405.6135 | 497.8039 | 472.9742 | 449.9238 | 507.8559
3406.6135 | 497.8785 | 473.0883 | 449.9438 | 507.9194
3407.6135 | 497.8739 | 473.1482 | 449.8791 | 507.8355
3408.6135 | 497.8986 | 473.1401 | 449.8755 | 507.9976
3409.6135 | 497.9537 | 473.1097 | 450.1112 | 508.2541
3410.6135 | 497.7265 | 473.199 | 450.1302 | 508.2067
3411.6135 | 497.6528 | 473.3104 | 450.1215 | 508.3022
3412.6135 | 497.6208 | 473.3825 | 450.1649 | 508.3143
3413.6135 | 497.6123 | 473.479 | 450.2131 | 508.5148
3414.6135 | 497.6337 | 473.5558 | 450.3192 | 508.9516
3415.6135 | 497.6107 | 473.5173 | 450.121 | 508.9414
3416.6135 | 497.5493 | 473.5798 | 450.2816 | 509.0431
3417.6135 | 497.4888 | 473.6903 | 450.4411 | 508.9052
3418.6135 | 497.3778 | 473.6847 | 450.6926 | 508.9781
3419.6135 | 497.3565 | 473.7657 | 450.661 | 508.9049
3420.6135 | 497.355 | 473.8695 | 450.7556 | 508.9777
3421.6135 | 497.2533 | 473.9458 | 450.6988 | 508.833
3422.6135 | 497.1637 | 473.9859 | 450.72 | 508.9477
3423.6135 | 497.1436 | 474.0931 | 450.8254 | 508.9093
3424.6135 | 497.1085 | 474.0654 | 450.9313 | 509.0767
3425.6135 | 496.9953 | 474.1419 | 450.7584 | 509.4031
3426.6135 | 497.035 | 474.235 | 450.7992 | 509.8877
3427.6135 | 496.9633 | 474.3455 | 450.8886 | 509.5257
3428.6135 | 496.9112 | 474.3615 | 451.0205 | 509.8196
3429.6135 | 496.9595 | 474.3399 | 451.1839 | 509.6827
3430.6135 | 496.9768 | 474.368 | 451.1914 | 509.3849
3431.6135 | 497.0277 | 474.4993 | 451.2023 | 509.6224
3432.6135 | 496.9808 | 474.5897 | 451.2216 | 509.6064
3433.6135 | 496.9151 | 474.5418 | 450.8514 | 509.9892
3434.6135 | 496.8275 | 474.6195 | 451.1714 | 510.2135
3435.6135 | 496.8805 | 474.633 | 451.3093 | 510.2357
3436.6135 | 496.9557 | 474.6825 | 451.3816 | 510.3482
3437.6135 | 497.0668 | 474.7707 | 451.5177 | 510.3569
3438.6135 | 497.0895 | 474.8332 | 451.5235 | 510.248
3439.6135 | 497.1214 | 474.9077 | 451.6064 | 510.4012
3440.6135 | 497.2348 | 474.9339 | 451.7132 | 510.3212
3441.6135 | 497.2723 | 475.0406 | 451.7809 | 510.5866
3442.6135 | 497.2852 | 475.1021 | 451.5577 | 510.5918
3443.6135 | 497.1635 | 475.1755 | 451.3767 | 510.5846
3444.6135 | 497.0297 | 475.0961 | 451.4636 | 510.5016
3445.6135 | 496.9336 | 475.0726 | 451.499 | 510.4946
3446.6135 | 496.9627 | 475.0885 | 451.4628 | 510.6872
3447.6135 | 496.9589 | 475.2102 | 451.6615 | 510.4641
3448.6135 | 496.9778 | 475.3069 | 451.5301 | 510.5115
3449.6135 | 496.9767 | 475.307 | 451.7207 | 510.6364
3450.6135 | 496.9355 | 475.3396 | 452.0201 | 510.4523
3451.6135 | 496.833 | 475.4357 | 452.1981 | 510.6039
3452.6135 | 496.8856 | 475.5741 | 452.24 | 510.4903
3453.6135 | 496.9487 | 475.5814 | 452.2799 | 510.5895
3454.6135 | 496.9653 | 475.6401 | 452.2429 | 510.4401
3455.6135 | 496.7959 | 475.7551 | 452.2013 | 510.6261
3456.6135 | 496.6793 | 475.7412 | 452.2309 | 510.6395
3457.6135 | 496.9126 | 475.761 | 452.2992 | 510.5886
3458.6135 | 497.0766 | 475.7937 | 452.1949 | 510.6935
3459.6135 | 497.1621 | 475.9008 | 452.0618 | 510.9374
3460.6135 | 497.1617 | 475.9515 | 452.3573 | 511.0436
3461.6135 | 497.1973 | 475.9238 | 452.4136 | 510.9004
3462.6135 | 497.2926 | 475.9434 | 452.5138 | 510.7673
3463.6135 | 497.1668 | 475.9958 | 452.6504 | 510.9829
3464.6135 | 497.0234 | 476.0189 | 452.7966 | 511.2175
3465.6135 | 497.0692 | 476.0044 | 452.8969 | 511.2115
3466.6135 | 497.0643 | 476.0873 | 452.8194 | 511.2371
3467.6135 | 497.0912 | 476.2527 | 452.9346 | 511.0292
3468.6135 | 497.0095 | 476.355 | 452.9913 | 511.416
3469.6135 | 496.9358 | 476.4293 | 453.0003 | 511.4133
3470.6135 | 496.9046 | 476.3933 | 452.9878 | 511.5797
3471.6135 | 496.9172 | 476.379 | 452.9567 | 511.4909
3472.6135 | 496.8338 | 476.4649 | 452.7294 | 511.5365
3473.6135 | 496.8068 | 476.4848 | 452.871 | 511.5602
3474.6135 | 496.8113 | 476.5108 | 453.1523 | 511.5597
3475.6135 | 496.7269 | 476.618 | 453.2697 | 511.5854
3476.6135 | 496.7483 | 476.6443 | 453.2331 | 511.7056
3477.6135 | 496.7758 | 476.7582 | 453.2902 | 511.6814
3478.6135 | 496.7604 | 476.7154 | 453.2596 | 511.7621
3479.6135 | 496.8048 | 476.8429 | 453.2254 | 511.8551
3480.6135 | 496.76 | 476.9176 | 453.2819 | 511.7674
3481.6135 | 496.8222 | 477.028 | 453.027 | 511.1697
3482.6135 | 496.9325 | 477.0153 | 453.1032 | 510.9466
3483.6135 | 497.0054 | 477.0761 | 453.4268 | 510.9877
3484.6135 | 497.0589 | 477.1013 | 453.6065 | 511.0223
3485.6135 | 497.1045 | 477.1799 | 453.6337 | 511.1022
3486.6135 | 497.2413 | 477.2132 | 453.5972 | 511.2894
3487.6135 | 497.3115 | 477.1836 | 453.4799 | 511.4139
3488.6135 | 497.3789 | 477.2073 | 453.6478 | 511.582
3489.6135 | 497.2552 | 477.2683 | 453.8225 | 511.5504
3490.6135 | 497.0687 | 477.3516 | 453.8437 | 511.5619
3491.6135 | 497.1077 | 477.3425 | 453.7007 | 511.5505
3492.6135 | 497.182 | 477.3898 | 453.8103 | 511.2773
3493.6135 | 497.1866 | 477.4554 | 453.8929 | 511.3332
3494.6135 | 497.1671 | 477.5702 | 454.0695 | 511.3028
3495.6135 | 497.1343 | 477.5548 | 454.031 | 511.3724
3496.6135 | 497.1848 | 477.6627 | 453.9678 | 511.2194
3497.6135 | 497.3172 | 477.6704 | 454.0981 | 510.936
3498.6135 | 497.5072 | 477.7543 | 454.2516 | 510.8574
3499.6135 | 497.4996 | 477.8586 | 454.402 | 510.7885
3500.6135 | 497.5644 | 477.889 | 454.3576 | 510.8018
3501.6135 | 497.6208 | 477.9442 | 454.4286 | 510.8328
3502.6135 | 497.6263 | 477.9626 | 454.5503 | 510.53
3503.6135 | 497.5878 | 477.933 | 454.5319 | 510.6231
3504.6135 | 497.6206 | 478.0118 | 454.5593 | 510.8864
3505.6135 | 497.5545 | 477.9679 | 454.4466 | 511.1941
3506.6135 | 497.5921 | 478.0365 | 454.3958 | 511.2719
3507.6135 | 497.6823 | 478.075 | 454.5462 | 511.2148
3508.6135 | 497.7455 | 478.1079 | 454.7648 | 511.275
3509.6135 | 497.5989 | 478.1326 | 454.8288 | 511.3239
3510.6135 | 497.3548 | 478.1872 | 454.8219 | 510.9899
3511.6135 | 497.2408 | 478.2232 | 454.8282 | 509.6265
3512.6135 | 497.1676 | 478.2954 | 454.7518 | 510.2525
3513.6135 | 497.1594 | 478.3264 | 454.8268 | 508.2131
3514.6135 | 497.0896 | 478.386 | 454.8934 | 507.0496
3515.6135 | 496.7961 | 478.4736 | 454.9263 | 509.5645
3516.6135 | 496.6859 | 478.5167 | 454.5973 | 510.0109
3517.6135 | 496.6841 | 478.489 | 454.4257 | 509.442
3518.6135 | 496.7256 | 478.4754 | 454.1357 | 508.5281
3519.6135 | 496.7423 | 478.5818 | 454.2596 | 507.8225
3520.6135 | 496.8638 | 478.5309 | 454.5859 | 508.887
3521.6135 | 496.8371 | 478.624 | 454.5895 | 507.2507
3522.6135 | 496.9802 | 478.6899 | 454.7183 | 502.012
3523.6135 | 497.1437 | 478.7095 | 454.99 | 502.1629
3524.6135 | 497.2136 | 478.6922 | 455.1163 | 502.2909
3525.6135 | 497.2154 | 478.6644 | 455.0574 | 502.7573
3526.6135 | 497.2335 | 478.7272 | 454.8425 | 502.824
3527.6135 | 497.3575 | 478.7595 | 454.9296 | 502.8837
3528.6135 | 497.396 | 478.8804 | 455.1612 | 503.0098
3529.6135 | 497.49 | 478.9411 | 455.2159 | 503.2345
3530.6135 | 497.5545 | 479.0132 | 455.1971 | 503.2566
3531.6135 | 497.6598 | 479.0781 | 455.1255 | 503.3617
3532.6135 | 497.7223 | 479.1277 | 455.2474 | 503.2674
3533.6135 | 497.6498 | 479.167 | 455.3099 | 503.2555
3534.6135 | 497.6959 | 479.225 | 455.3856 | 503.4302
3535.6135 | 497.7605 | 479.3184 | 455.3717 | 503.6278
3536.6135 | 497.5482 | 479.3945 | 455.3832 | 503.1735
3537.6135 | 497.5582 | 479.28 | 455.2221 | 502.892
3538.6135 | 497.6105 | 479.2706 | 454.8968 | 502.8458
3539.6135 | 497.6445 | 479.3879 | 455.185 | 502.8167
3540.6135 | 497.5814 | 479.4227 | 455.1298 | 502.8674
3541.6135 | 497.4883 | 479.5323 | 455.3878 | 502.8497
3542.6135 | 497.5096 | 479.5311 | 455.4861 | 502.856
3543.6135 | 497.4087 | 479.4496 | 455.3707 | 502.5001
3544.6135 | 497.3713 | 479.5872 | 455.3864 | 502.4606
3545.6135 | 497.3799 | 479.5475 | 455.6586 | 502.5711
3546.6135 | 497.328 | 479.612 | 455.7705 | 502.5629
3547.6135 | 497.2481 | 479.7049 | 455.4796 | 502.5532
3548.6135 | 497.2011 | 479.7608 | 455.5603 | 502.6293
3549.6135 | 497.2602 | 479.7631 | 455.7333 | 502.8624
3550.6135 | 497.4408 | 479.7792 | 455.7404 | 502.9948
3551.6135 | 497.4026 | 479.8532 | 455.7269 | 502.9321
3552.6135 | 497.4352 | 479.9444 | 455.7199 | 502.6244
3553.6135 | 497.3674 | 479.9922 | 455.7795 | 502.4414
3554.6135 | 497.3603 | 480.0379 | 455.7126 | 502.3564
3555.6135 | 497.3585 | 480.0272 | 455.7808 | 502.4735
3556.6135 | 497.4564 | 479.9923 | 455.8602 | 502.512
3557.6135 | 497.5307 | 480.0378 | 455.9901 | 502.4009
3558.6135 | 497.3126 | 480.0059 | 456.1547 | 502.4733
3559.6135 | 497.2509 | 480.0232 | 456.1069 | 502.6289
3560.6135 | 497.2287 | 480.0998 | 456.1776 | 502.7371
3561.6135 | 497.3526 | 480.1464 | 456.0136 | 502.7292
3562.6135 | 497.444 | 480.1814 | 456.1266 | 503.0553
3563.6135 | 497.4314 | 480.1845 | 456.0697 | 503.3103
3564.6135 | 497.4792 | 480.2004 | 456.0812 | 503.3065
3565.6135 | 497.3498 | 480.2725 | 456.1914 | 503.3058
3566.6135 | 497.2857 | 480.1711 | 456.2415 | 503.1811
3567.6135 | 497.3528 | 480.2267 | 456.1977 | 502.9429
3568.6135 | 497.358 | 480.2612 | 456.4264 | 502.807
3569.6135 | 497.4177 | 480.3371 | 456.5476 | 503.0102
3570.6135 | 497.4318 | 480.306 | 456.494 | 503.0105
3571.6135 | 497.3774 | 480.3607 | 456.574 | 503.0028
3572.6135 | 497.3912 | 480.3582 | 456.5424 | 503.0264
3573.6135 | 497.4489 | 480.4426 | 456.7095 | 503.1209
3574.6135 | 497.5056 | 480.5087 | 456.8854 | 503.1531
3575.6135 | 497.5099 | 480.5514 | 457.0116 | 502.8431
3576.6135 | 497.617 | 480.5915 | 457.0396 | 502.8386
3577.6135 | 497.6268 | 480.6403 | 456.9277 | 504.6563
3578.6135 | 497.6816 | 480.504 | 457.0657 | 502.8341
3579.6135 | 497.7164 | 480.6396 | 457.1164 | 502.6242
3580.6135 | 497.7572 | 480.6522 | 457.1378 | 502.6719
3581.6135 | 497.6493 | 480.6014 | 457.138 | 502.7423
3582.6135 | 497.4147 | 480.5722 | 457.1979 | 502.3979
3583.6135 | 497.4534 | 480.6346 | 457.0789 | 502.4729
3584.6135 | 497.4402 | 480.7238 | 457.0489 | 502.5951
3585.6135 | 497.3558 | 480.696 | 457.0811 | 502.7267
3586.6135 | 497.3949 | 480.7307 | 457.1697 | 502.7755
3587.6135 | 497.3094 | 480.8017 | 456.9436 | 502.7028
3588.6135 | 497.2624 | 480.8103 | 457.1255 | 503.0614
3589.6135 | 497.2414 | 480.7338 | 457.2897 | 503.1467
3590.6135 | 497.1668 | 480.77 | 457.2837 | 503.3367
3591.6135 | 497.1957 | 480.8706 | 457.4221 | 503.2865
3592.6135 | 497.2452 | 480.8132 | 457.567 | 503.105
3593.6135 | 497.3495 | 480.8565 | 457.522 | 503.5318
3594.6135 | 497.4406 | 480.9981 | 457.4008 | 503.5406
3595.6135 | 497.3616 | 480.8868 | 457.5009 | 503.5963
3596.6135 | 497.338 | 480.9216 | 457.6263 | 503.6608
3597.6135 | 497.4048 | 481.0685 | 457.6093 | 503.7264
3598.6135 | 497.4522 | 481.0823 | 457.6907 | 503.7301
3599.6135 | 497.4042 | 481.1213 | 457.696 | 503.7452
3600.6135 | 497.3531 | 481.1623 | 457.7379 | 503.7396
3601.6135 | 497.1951 | 481.1127 | 457.8084 | 503.8475
3602.6135 | 497.1382 | 481.1233 | 457.7108 | 503.8765
3603.6135 | 497.0943 | 481.1684 | 457.7793 | 503.9446
3604.6135 | 497.1715 | 481.1731 | 457.759 | 503.8666
3605.6135 | 497.29 | 481.2275 | 457.8083 | 504.0333
3606.6135 | 497.1992 | 481.2439 | 457.9294 | 504.19
3607.6135 | 497.0921 | 481.2743 | 457.9564 | 503.9966
3608.6135 | 496.9956 | 481.2336 | 457.7612 | 504.4041
3609.6135 | 496.9787 | 481.2885 | 457.8052 | 504.4312
3610.6135 | 496.9715 | 481.3199 | 457.875 | 504.3504
3611.6135 | 497.0349 | 481.3674 | 458.0109 | 504.2203
3612.6135 | 497.0082 | 481.4258 | 457.9973 | 504.2174
3613.6135 | 497.0316 | 481.3492 | 457.9851 | 504.2347
3614.6135 | 497.2058 | 481.413 | 458.0146 | 504.2343
3615.6135 | 497.3313 | 481.5079 | 457.9207 | 504.2031
3616.6135 | 497.3895 | 481.5183 | 458.018 | 504.1124
3617.6135 | 497.4382 | 481.5353 | 458.1756 | 504.3873
3618.6135 | 497.4777 | 481.6259 | 457.9161 | 511.4577
3619.6135 | 497.4833 | 481.6439 | 457.9012 | 511.5498
3620.6135 | 497.4857 | 481.6533 | 458.1088 | 511.787
3621.6135 | 497.4625 | 481.7111 | 458.1181 | 511.7577
3622.6135 | 497.4544 | 481.7768 | 458.1457 | 511.6139
3623.6135 | 497.5698 | 481.7637 | 458.3361 | 511.6591
3624.6135 | 497.6251 | 481.7374 | 458.258 | 511.7512
3625.6135 | 497.7244 | 481.7867 | 458.2264 | 511.581
3626.6135 | 497.7284 | 481.6914 | 458.439 | 511.8288
3627.6135 | 497.7317 | 481.8032 | 458.5009 | 511.7997
3628.6135 | 497.7241 | 481.7955 | 458.4275 | 511.6973
3629.6135 | 497.5071 | 481.7539 | 458.3224 | 511.674
3630.6135 | 497.3467 | 481.8689 | 458.3521 | 511.5881
3631.6135 | 497.3936 | 481.9372 | 458.4948 | 511.5909
3632.6135 | 497.3181 | 481.9232 | 458.5226 | 511.6079
3633.6135 | 497.2626 | 482.0113 | 458.5999 | 511.5116
3634.6135 | 497.2484 | 482.038 | 458.6336 | 511.6843
3635.6135 | 497.2647 | 482.0455 | 458.5737 | 511.7803
3636.6135 | 497.3744 | 482.0776 | 458.4323 | 511.8102
3637.6135 | 497.4742 | 482.1174 | 458.4445 | 511.7989
3638.6135 | 497.4431 | 482.091 | 458.3521 | 511.6258
3639.6135 | 497.47 | 482.0914 | 458.3961 | 511.7801
3640.6135 | 497.4954 | 482.0465 | 458.6183 | 511.802
3641.6135 | 497.4856 | 482.0442 | 458.6787 | 512.2645
3642.6135 | 497.6175 | 481.9911 | 458.7423 | 512.1041
3643.6135 | 497.6208 | 482.1035 | 458.7952 | 511.9657
3644.6135 | 497.5033 | 482.1731 | 458.7901 | 511.8762
3645.6135 | 497.4313 | 482.2554 | 458.8451 | 511.5957
3646.6135 | 497.4423 | 482.3225 | 459.081 | 511.318
3647.6135 | 497.4991 | 482.342 | 459.1065 | 511.1477
3648.6135 | 497.5856 | 482.3324 | 459.1002 | 511.2107
3649.6135 | 497.5519 | 482.3388 | 459.0843 | 511.0838
3650.6135 | 497.5564 | 482.2494 | 458.901 | 511.1111
3651.6135 | 497.5592 | 482.2798 | 458.9927 | 511.1499
3652.6135 | 497.4573 | 482.3293 | 459.0497 | 511.1746
3653.6135 | 497.3496 | 482.3214 | 459.1565 | 511.244
3654.6135 | 497.2663 | 482.3683 | 459.2299 | 511.329
3655.6135 | 497.1952 | 482.3561 | 459.2211 | 511.3848
3656.6135 | 497.1871 | 482.3954 | 459.2261 | 511.2597
3657.6135 | 497.1458 | 482.4098 | 459.2083 | 511.1864
3658.6135 | 497.0906 | 482.4899 | 459.1215 | 511.0772
3659.6135 | 497.0329 | 482.5337 | 459.0606 | 510.9038
3660.6135 | 496.9384 | 482.4701 | 459.1692 | 510.8524
3661.6135 | 496.9553 | 482.4947 | 459.208 | 510.8366
3662.6135 | 496.8815 | 482.5454 | 459.243 | 510.934
3663.6135 | 496.8646 | 482.5167 | 459.2194 | 510.8801
3664.6135 | 496.8934 | 482.4917 | 459.2499 | 510.9709
3665.6135 | 496.8304 | 482.4789 | 459.4452 | 511.0592
3666.6135 | 496.7493 | 482.478 | 459.5181 | 511.1942
3667.6135 | 496.7854 | 482.5446 | 459.455 | 511.3888
3668.6135 | 496.8103 | 482.5417 | 459.2811 | 511.327
3669.6135 | 496.9084 | 482.4327 | 459.2944 | 511.3304
3670.6135 | 497.0228 | 482.6073 | 458.9639 | 511.4132
3671.6135 | 497.1492 | 482.6845 | 459.0415 | 511.3653
3672.6135 | 497.098 | 482.7045 | 459.2104 | 511.3573
3673.6135 | 497.1002 | 482.5442 | 459.3861 | 511.3734
3674.6135 | 497.1501 | 482.6661 | 459.3538 | 511.329
3675.6135 | 497.05 | 482.6718 | 459.2329 | 511.6083
3676.6135 | 497.0834 | 482.667 | 459.042 | 511.5192
3677.6135 | 497.0781 | 482.7227 | 459.3305 | 511.414
3678.6135 | 497.1224 | 482.7542 | 459.4328 | 511.4048
3679.6135 | 497.1732 | 482.7806 | 459.194 | 511.3658
3680.6135 | 497.2919 | 482.8713 | 459.34 | 511.1899
3681.6135 | 497.4551 | 482.8862 | 459.4257 | 511.0256
3682.6135 | 497.4743 | 482.9187 | 459.3679 | 510.9114
3683.6135 | 497.3867 | 482.9325 | 459.412 | 510.9153
3684.6135 | 497.4327 | 482.9455 | 459.418 | 510.9738
3685.6135 | 497.4046 | 482.9391 | 459.5565 | 511.0596
3686.6135 | 497.4533 | 482.9328 | 459.3692 | 511.0149
3687.6135 | 497.4232 | 482.9736 | 459.4092 | 510.8775
3688.6135 | 497.3224 | 482.9948 | 459.562 | 511.0009
3689.6135 | 497.1665 | 482.9139 | 459.4428 | 510.8
3690.6135 | 497.1116 | 483.0012 | 459.368 | 510.9386
3691.6135 | 497.0668 | 483.0748 | 459.6007 | 510.8089
3692.6135 | 497.0962 | 483.1445 | 459.6754 | 510.7201
3693.6135 | 497.0248 | 483.1607 | 459.6375 | 510.803
3694.6135 | 497.022 | 483.1846 | 459.6701 | 510.9409
3695.6135 | 496.9423 | 483.1283 | 459.7844 | 510.9982
3696.6135 | 496.964 | 483.0242 | 459.7939 | 511.0984
3697.6135 | 497.0608 | 483.0961 | 459.6669 | 511.1689
3698.6135 | 496.9513 | 483.1462 | 459.7471 | 511.3535
3699.6135 | 496.7639 | 483.1705 | 459.6558 | 511.2501
3700.6135 | 496.7407 | 483.132 | 459.6693 | 511.2293
3701.6135 | 496.864 | 483.106 | 459.8064 | 511.3684
3702.6135 | 496.8908 | 483.1477 | 459.9228 | 511.4279
3703.6135 | 496.8389 | 483.2347 | 459.8525 | 511.6548
3704.6135 | 496.8864 | 483.2424 | 459.84 | 511.6861
3705.6135 | 496.8801 | 483.2693 | 459.8152 | 511.7389
3706.6135 | 496.8555 | 483.3668 | 459.9236 | 511.7738
3707.6135 | 496.9035 | 483.3687 | 459.9666 | 511.6006
3708.6135 | 496.9899 | 483.3637 | 460.0759 | 511.7912
3709.6135 | 497.0785 | 483.3358 | 460.1706 | 511.8812
3710.6135 | 497.1477 | 483.3674 | 460.2087 | 512.0605
3711.6135 | 497.3109 | 483.4041 | 460.0442 | 512.0517
3712.6135 | 497.4301 | 483.4765 | 460.1402 | 511.593
3713.6135 | 497.4092 | 483.4897 | 460.1781 | 511.6457
3714.6135 | 497.4335 | 483.4635 | 460.2525 | 511.9077
3715.6135 | 497.4638 | 483.5029 | 460.2908 | 511.8033
3716.6135 | 497.5461 | 483.5605 | 460.3813 | 511.8647
3717.6135 | 497.587 | 483.5898 | 460.3562 | 511.763
3718.6135 | 497.5767 | 483.5257 | 460.125 | 512.0203
3719.6135 | 497.4194 | 483.4459 | 460.348 | 511.9746
3720.6135 | 497.2823 | 483.5089 | 460.3778 | 511.9615
3721.6135 | 497.1809 | 483.5238 | 460.5105 | 511.9514
3722.6135 | 497.1328 | 483.6004 | 460.5076 | 511.8548
3723.6135 | 497.0334 | 483.6353 | 460.4239 | 511.5889
3724.6135 | 496.9379 | 483.6099 | 460.4524 | 511.8907
3725.6135 | 496.9096 | 483.6321 | 460.4064 | 512.0033
3726.6135 | 496.9603 | 483.6547 | 460.5983 | 511.9929
3727.6135 | 496.9098 | 483.6853 | 460.653 | 511.8437
3728.6135 | 496.9121 | 483.7274 | 460.6278 | 511.9846
3729.6135 | 496.8121 | 483.7494 | 460.6159 | 511.8835
3730.6135 | 496.8239 | 483.8378 | 460.6068 | 511.7839
3731.6135 | 496.8856 | 483.7968 | 460.5822 | 511.9855
3732.6135 | 497.0339 | 483.7968 | 460.6063 | 511.8399
3733.6135 | 497.1462 | 483.8285 | 460.6032 | 511.8899
3734.6135 | 497.2168 | 483.7875 | 460.458 | 511.9344
3735.6135 | 497.1745 | 483.8187 | 460.3747 | 511.9757
3736.6135 | 497.1285 | 483.7882 | 460.4332 | 511.8771
3737.6135 | 497.1764 | 483.7892 | 460.2771 | 511.5142
3738.6135 | 497.1102 | 483.8298 | 460.4765 | 511.8471
3739.6135 | 497.0697 | 483.8904 | 460.4661 | 511.7039
3740.6135 | 497.0979 | 483.901 | 460.4408 | 511.7861
3741.6135 | 497.0924 | 483.8902 | 460.5004 | 512.0337
3742.6135 | 497.1217 | 483.9545 | 460.6241 | 511.831
3743.6135 | 497.3363 | 483.9487 | 460.7585 | 511.9562
3744.6135 | 497.3216 | 483.973 | 460.7361 | 511.9635
3745.6135 | 497.2751 | 484.0227 | 460.8373 | 512.047
3746.6135 | 497.3234 | 483.9758 | 460.7088 | 512.2936
3747.6135 | 497.3035 | 484.0004 | 460.9763 | 512.0731
3748.6135 | 497.1668 | 484.0549 | 460.9939 | 512.2422
3749.6135 | 497.1493 | 484.1158 | 460.9725 | 512.3747
3750.6135 | 497.2098 | 484.0661 | 460.9882 | 512.4601
3751.6135 | 497.1635 | 483.9192 | 460.9644 | 512.5063
3752.6135 | 497.1746 | 483.9815 | 461.0861 | 512.4529
3753.6135 | 497.1806 | 484.0858 | 461.1451 | 512.5306
3754.6135 | 497.0489 | 484.0888 | 461.1012 | 512.6173
3755.6135 | 497.0491 | 484.1186 | 460.9787 | 512.6183
3756.6135 | 497.1156 | 484.1565 | 461.0694 | 512.4753
3757.6135 | 497.1674 | 484.1121 | 461.2004 | 512.3477
3758.6135 | 497.2759 | 484.0146 | 461.1691 | 512.6838
3759.6135 | 497.3819 | 484.0794 | 461.229 | 512.8947
3760.6135 | 497.3949 | 484.125 | 461.2086 | 512.8698
3761.6135 | 497.4018 | 484.1587 | 461.2362 | 513.0035
3762.6135 | 497.3347 | 484.2379 | 461.2728 | 512.6075
3763.6135 | 497.4309 | 484.232 | 461.2402 | 512.8517
3764.6135 | 497.4541 | 484.271 | 461.1144 | 512.746
3765.6135 | 497.3958 | 484.3335 | 461.1318 | 512.5766
3766.6135 | 497.4381 | 484.3004 | 461.1589 | 512.4824
3767.6135 | 497.4214 | 484.2862 | 460.8459 | 512.2722
3768.6135 | 497.5112 | 484.2645 | 460.8151 | 512.3919
3769.6135 | 497.4897 | 484.2593 | 461.0625 | 512.2224
3770.6135 | 497.57 | 484.2682 | 461.2088 | 512.375
3771.6135 | 497.5181 | 484.3581 | 461.2274 | 512.2449
3772.6135 | 497.5292 | 484.3216 | 461.3371 | 512.0434
3773.6135 | 497.322 | 484.3967 | 461.2014 | 512.1209
3774.6135 | 497.2347 | 484.4117 | 461.0944 | 511.9607
3775.6135 | 497.1462 | 484.4429 | 461.1768 | 512.0049
3776.6135 | 497.2162 | 484.3941 | 461.2695 | 512.0405
3777.6135 | 497.2555 | 484.3796 | 461.3107 | 511.7702
3778.6135 | 497.201 | 484.4279 | 461.2454 | 512.0111
3779.6135 | 497.1202 | 484.4674 | 461.3504 | 512.0749
3780.6135 | 497.1016 | 484.4734 | 461.4044 | 512.0084
3781.6135 | 497.1519 | 484.4658 | 461.341 | 512.1214
3782.6135 | 497.1593 | 484.4864 | 461.2763 | 511.6742
3783.6135 | 497.2346 | 484.4288 | 461.3044 | 512.1604
3784.6135 | 497.2611 | 484.4728 | 461.3097 | 511.7252
3785.6135 | 496.9919 | 484.5388 | 461.2547 | 512.0075
3786.6135 | 496.8506 | 484.5732 | 461.3178 | 512.0262
3787.6135 | 496.9033 | 484.6269 | 461.34 | 511.8057
3788.6135 | 496.9469 | 484.6223 | 461.3993 | 512.2172
3789.6135 | 497.0118 | 484.5301 | 461.5457 | 512.0943
3790.6135 | 497.0944 | 484.493 | 461.5685 | 512.171
3791.6135 | 497.1555 | 484.5769 | 461.5148 | 512.2319
3792.6135 | 497.1929 | 484.5339 | 461.5288 | 511.84
3793.6135 | 497.2174 | 484.5787 | 461.4311 | 512.0815
3794.6135 | 497.2699 | 484.4977 | 461.4729 | 512.0579
3795.6135 | 497.2911 | 484.5703 | 461.3628 | 512.0119
3796.6135 | 497.4517 | 484.5666 | 461.4536 | 512.1703
3797.6135 | 497.4856 | 484.6191 | 461.4161 | 511.7077
3798.6135 | 497.5737 | 484.6452 | 461.3859 | 512.4041
3799.6135 | 497.6121 | 484.6586 | 461.5313 | 512.6603
3800.6135 | 497.6439 | 484.7246 | 461.5416 | 512.7406
3801.6135 | 497.615 | 484.7245 | 461.6165 | 512.6754
3802.6135 | 497.5446 | 484.7309 | 461.5578 | 512.2883
3803.6135 | 497.5451 | 484.731 | 461.687 | 512.5884
3804.6135 | 497.4384 | 484.7719 | 461.598 | 512.6011
3805.6135 | 497.4848 | 484.753 | 461.6592 | 512.5837
3806.6135 | 497.4881 | 484.7808 | 461.6277 | 512.6429
3807.6135 | 497.4574 | 484.8478 | 461.6495 | 512.6727
3808.6135 | 497.4102 | 484.8344 | 461.5658 | 512.9034
3809.6135 | 497.3148 | 484.8653 | 461.6881 | 512.9859
3810.6135 | 497.1998 | 484.8873 | 461.7541 | 513.0399
3811.6135 | 497.2983 | 484.8852 | 461.6386 | 513.1127
3812.6135 | 497.2814 | 484.9222 | 461.7019 | 513.1614
3813.6135 | 497.1722 | 484.9396 | 461.7636 | 513.0584
3814.6135 | 497.1668 | 484.9227 | 461.8436 | 512.9629
3815.6135 | 497.1709 | 484.9613 | 461.6582 | 513.1645
3816.6135 | 497.0652 | 484.7889 | 461.4607 | 512.8566
3817.6135 | 497.1006 | 484.8318 | 461.5883 | 513.1923
3818.6135 | 497.1645 | 484.9277 | 461.6454 | 513.2262
3819.6135 | 497.1524 | 484.958 | 461.4883 | 513.2007
3820.6135 | 497.1399 | 484.9253 | 461.5797 | 513.1875
3821.6135 | 497.1464 | 484.8472 | 461.7465 | 513.2059
3822.6135 | 497.192 | 484.8262 | 461.8099 | 513.0185
3823.6135 | 497.1753 | 484.8749 | 461.8781 | 512.6954
3824.6135 | 497.1661 | 484.9152 | 461.903 | 512.7573
3825.6135 | 497.242 | 484.9872 | 461.7351 | 512.7709
3826.6135 | 497.2955 | 484.8731 | 461.8286 | 512.8132
3827.6135 | 497.3196 | 484.9461 | 461.7051 | 512.8711
3828.6135 | 497.3486 | 484.9086 | 461.7978 | 513.245
3829.6135 | 497.3522 | 484.956 | 461.7297 | 512.9449
3830.6135 | 497.3522 | 484.9697 | 461.6439 | 513.1016
3831.6135 | 497.305 | 484.9149 | 461.8071 | 513.1316
3832.6135 | 497.3233 | 484.9733 | 461.9167 | 512.6171
3833.6135 | 497.3933 | 484.9346 | 461.9083 | 512.6628
3834.6135 | 497.4938 | 484.9665 | 461.7884 | 512.6161
3835.6135 | 497.4874 | 484.9923 | 461.7889 | 512.4986
3836.6135 | 497.4648 | 484.9586 | 461.8973 | 512.5414
3837.6135 | 497.3408 | 485.0441 | 461.8403 | 512.4706
3838.6135 | 497.1181 | 484.9973 | 461.8123 | 512.4866
3839.6135 | 497.141 | 484.9248 | 462.0134 | 512.5312
3840.6135 | 497.1394 | 484.9747 | 462.1671 | 512.5878
3841.6135 | 497.2549 | 485.038 | 462.1303 | 512.368
3842.6135 | 497.383 | 485.108 | 461.9426 | 512.2428
3843.6135 | 497.3613 | 485.1109 | 461.8667 | 512.3037
3844.6135 | 497.3516 | 485.0689 | 461.8828 | 512.6086
3845.6135 | 497.4736 | 485.0414 | 461.9768 | 512.8934
3846.6135 | 497.4524 | 485.0879 | 461.9084 | 512.9036
3847.6135 | 497.4147 | 485.0984 | 461.92 | 512.6384
3848.6135 | 497.2834 | 485.1755 | 461.9861 | 512.1846
3849.6135 | 497.2499 | 485.1987 | 461.7015 | 512.1033
3850.6135 | 497.2399 | 485.1834 | 461.8519 | 512.2231
3851.6135 | 497.3712 | 485.114 | 462.0662 | 512.4487
3852.6135 | 497.3372 | 485.1624 | 462.0327 | 512.4209
3853.6135 | 497.3211 | 485.1206 | 462.127 | 512.4407
3854.6135 | 497.2722 | 485.165 | 462.1198 | 512.4657
3855.6135 | 497.2362 | 485.1046 | 462.2578 | 512.4187
3856.6135 | 497.1557 | 485.0177 | 462.0824 | 512.3646
3857.6135 | 497.111 | 485.0208 | 462.1825 | 512.3848
3858.6135 | 497.0387 | 485.0956 | 462.1706 | 512.2061
3859.6135 | 496.9279 | 485.135 | 462.2728 | 512.0281
3860.6135 | 497.0419 | 485.1862 | 462.3123 | 512.3342
3861.6135 | 497.0191 | 485.2421 | 462.3105 | 512.3258
3862.6135 | 497.0105 | 485.2335 | 462.1969 | 512.0511
3863.6135 | 496.9761 | 485.2281 | 462.1136 | 511.8033
3864.6135 | 496.9794 | 485.2655 | 462.2414 | 511.4047
3865.6135 | 496.9877 | 485.3278 | 462.0995 | 511.711
3866.6135 | 496.9998 | 485.3258 | 462.0609 | 511.8243
3867.6135 | 497.0645 | 485.295 | 462.0923 | 511.487
3868.6135 | 497.1307 | 485.2261 | 462.0473 | 511.7898
3869.6135 | 497.3246 | 485.2371 | 462.2279 | 511.7381
3870.6135 | 497.3219 | 485.2529 | 462.34 | 511.7792
3871.6135 | 497.3597 | 485.2113 | 462.3175 | 511.7184
3872.6135 | 497.4249 | 485.2224 | 462.4004 | 511.614
3873.6135 | 497.375 | 485.2527 | 462.3991 | 511.6503
3874.6135 | 497.2666 | 485.2317 | 462.4267 | 511.547
3875.6135 | 497.0153 | 485.2243 | 462.5027 | 511.804
3876.6135 | 496.7111 | 485.2889 | 462.4688 | 511.8778
3877.6135 | 496.2556 | 485.2956 | 462.2936 | 511.9172
3878.6135 | 495.5989 | 485.2831 | 462.4279 | 512.129
3879.6135 | 494.861 | 485.2937 | 462.403 | 512.1801
3880.6135 | 494.064 | 485.2941 | 462.2656 | 512.3626
3881.6135 | 493.2937 | 485.2508 | 462.3688 | 512.4464
3882.6135 | 492.4962 | 485.2344 | 462.156 | 512.1904
3883.6135 | 491.7174 | 485.1165 | 462.1435 | 512.3443
3884.6135 | 490.9553 | 485.1425 | 462.0195 | 512.3691
3885.6135 | 490.2994 | 485.1296 | 462.1275 | 512.0774
3886.6135 | 489.4859 | 485.1036 | 462.0918 | 512.1811
3887.6135 | 488.6517 | 485.1209 | 462.1338 | 511.9962
3888.6135 | 487.8795 | 485.0559 | 462.1195 | 512.0918
3889.6135 | 487.0981 | 485.0449 | 462.1327 | 511.9364
3890.6135 | 486.2103 | 485.0503 | 461.9174 | 511.6534
3891.6135 | 485.4628 | 484.8836 | 461.881 | 511.7843
3892.6135 | 484.6044 | 484.8041 | 461.81 | 511.6114
3893.6135 | 483.8314 | 484.8168 | 461.5706 | 511.7223
3894.6135 | 482.9981 | 484.737 | 461.3834 | 511.5995
3895.6135 | 482.0469 | 484.7074 | 461.466 | 511.6264
3896.6135 | 481.2014 | 484.5811 | 461.4679 | 511.5603
3897.6135 | 480.3178 | 484.4142 | 461.3799 | 511.3334
3898.6135 | 479.4482 | 484.4281 | 461.1453 | 511.5453
3899.6135 | 478.613 | 484.3913 | 461.1468 | 511.6913
3900.6135 | 477.7488 | 484.2751 | 460.9813 | 511.6608
3901.6135 | 477.0543 | 484.2287 | 460.3557 | 511.6418
3902.6135 | 476.2088 | 484.206 | 460.3587 | 511.4036
3903.6135 | 475.3014 | 484.136 | 460.2393 | 511.5408
3904.6135 | 474.423 | 483.9048 | 460.1765 | 511.3869
3905.6135 | 473.447 | 483.8748 | 459.8124 | 511.6016
3906.6135 | 472.6711 | 483.8419 | 459.9784 | 511.8402
3907.6135 | 471.7844 | 483.6661 | 459.9418 | 511.7713
3908.6135 | 471.0147 | 483.5702 | 459.6288 | 511.8286
3909.6135 | 470.1348 | 483.5618 | 459.6218 | 511.6016
3910.6135 | 469.2797 | 483.5188 | 459.7284 | 511.3207
3911.6135 | 468.4036 | 483.3979 | 459.7661 | 511.3367
3912.6135 | 467.533 | 483.3042 | 459.863 | 511.0219
3913.6135 | 466.6865 | 483.1687 | 459.8244 | 511.1969
3914.6135 | 465.7958 | 483.0756 | 459.7663 | 510.9995
3915.6135 | 464.9201 | 482.9189 | 459.6198 | 511.0358
3916.6135 | 464.0359 | 482.845 | 459.6252 | 511.0593
3917.6135 | 463.1377 | 482.7501 | 459.6373 | 510.8039
3918.6135 | 462.3203 | 482.5793 | 459.521 | 510.8057
3919.6135 | 461.4418 | 482.5134 | 459.4435 | 510.9604
3920.6135 | 460.5424 | 482.3873 | 459.3354 | 510.9448
3921.6135 | 459.7594 | 482.2379 | 458.9634 | 510.8366
3922.6135 | 458.9242 | 482.2157 | 458.919 | 510.3558
3923.6135 | 458.0726 | 481.9479 | 458.9166 | 510.8522
3924.6135 | 457.3147 | 481.9114 | 458.7205 | 510.7431
3925.6135 | 456.5052 | 481.7982 | 458.5796 | 510.4797
3926.6135 | 455.6362 | 481.6687 | 458.444 | 510.3036
3927.6135 | 454.7697 | 481.5445 | 458.3132 | 510.0815
3928.6135 | 453.9178 | 481.3419 | 458.2747 | 510.222
3929.6135 | 453.1678 | 481.2022 | 458.1241 | 510.077
3930.6135 | 452.2622 | 481.0589 | 457.9695 | 510.0416
3931.6135 | 451.3195 | 480.8729 | 458.0428 | 509.8392
3932.6135 | 450.5444 | 480.7099 | 457.6864 | 509.5023
3933.6135 | 449.817 | 480.6292 | 457.5991 | 510.007
3934.6135 | 449.0589 | 480.451 | 457.4161 | 510.4782
3935.6135 | 448.2839 | 480.2457 | 457.387 | 510.7025
3936.6135 | 447.4831 | 480.0045 | 457.3426 | 510.947
3937.6135 | 446.7195 | 479.756 | 457.2476 | 510.5853
3938.6135 | 446.0388 | 479.675 | 456.918 | 510.8057
3939.6135 | 445.3864 | 479.616 | 456.6722 | 510.5161
3940.6135 | 444.5962 | 479.5828 | 456.7398 | 510.0196
3941.6135 | 443.7113 | 479.4813 | 456.5922 | 509.5083
3942.6135 | 442.9125 | 479.3099 | 456.4536 | 508.8066
3943.6135 | 442.0844 | 479.1595 | 456.4493 | 508.5991
3944.6135 | 441.3159 | 479.0448 | 456.1457 | 508.2845
3945.6135 | 440.5265 | 478.9104 | 456.0337 | 507.4983
3946.6135 | 439.7895 | 478.7264 | 455.9031 | 507.254
3947.6135 | 439.0859 | 478.5241 | 455.6203 | 506.3498
3948.6135 | 438.3503 | 478.3712 | 455.5083 | 505.969
3949.6135 | 437.5286 | 478.1834 | 455.3289 | 505.895
3950.6135 | 436.6832 | 478.0535 | 455.179 | 505.4555
3951.6135 | 435.8433 | 477.929 | 455.1095 | 505.4103
3952.6135 | 435.0781 | 477.7438 | 454.5894 | 504.8438
3953.6135 | 434.1912 | 477.5559 | 454.2575 | 504.8806
3954.6135 | 433.387 | 477.3818 | 454.2198 | 504.3387
3955.6135 | 432.6392 | 477.1962 | 454.155 | 504.1076
3956.6135 | 431.9402 | 476.9308 | 453.9758 | 503.7724
3957.6135 | 431.1787 | 476.7867 | 453.6899 | 502.8499
3958.6135 | 430.3908 | 476.6689 | 453.5252 | 503.1054
3959.6135 | 429.5475 | 476.5281 | 453.4813 | 502.9123
3960.6135 | 428.8971 | 476.2581 | 453.3444 | 502.6747
3961.6135 | 428.1871 | 476.1161 | 453.342 | 502.5541
3962.6135 | 427.4535 | 475.9402 | 453.2141 | 502.2489
3963.6135 | 426.6737 | 475.7542 | 453.0974 | 502.2125
3964.6135 | 425.9312 | 475.587 | 452.9556 | 502.1261
3965.6135 | 425.141 | 475.3862 | 452.7161 | 501.9498
3966.6135 | 424.3934 | 475.189 | 452.5824 | 501.6937
3967.6135 | 423.6723 | 474.9605 | 452.3282 | 500.7577
3968.6135 | 422.9233 | 474.7885 | 452.0667 | 500.8914
3969.6135 | 422.2891 | 474.5818 | 451.9336 | 501.0491
3970.6135 | 421.5827 | 474.3641 | 451.9137 | 500.9151
3971.6135 | 420.8927 | 474.1381 | 451.7979 | 500.516
3972.6135 | 420.2073 | 473.9377 | 451.4207 | 500.0264
3973.6135 | 419.4501 | 473.6985 | 451.0036 | 500.564
3974.6135 | 418.6803 | 473.5145 | 450.8583 | 500.4792
3975.6135 | 417.9255 | 473.3155 | 450.6516 | 500.3549
3976.6135 | 417.1341 | 473.0082 | 450.4222 | 500.0109
3977.6135 | 416.3548 | 472.8327 | 450.1721 | 499.8935
3978.6135 | 415.6776 | 472.6367 | 450.0104 | 499.9641
3979.6135 | 415.0454 | 472.4442 | 449.9097 | 499.7111
3980.6135 | 414.3864 | 472.2066 | 449.6566 | 499.4236
3981.6135 | 413.6875 | 472.0554 | 449.4751 | 499.217
3982.6135 | 412.9755 | 471.7828 | 449.0607 | 498.7584
3983.6135 | 412.3053 | 471.6354 | 449.0405 | 498.8745
3984.6135 | 411.6707 | 471.4696 | 448.8572 | 498.7256
3985.6135 | 410.9413 | 471.1764 | 448.7939 | 498.4343
3986.6135 | 410.2168 | 471.0306 | 448.5511 | 498.2488
3987.6135 | 409.5944 | 470.8158 | 448.3423 | 497.8066
3988.6135 | 408.9245 | 470.564 | 447.8948 | 497.991
3989.6135 | 408.2356 | 470.3195 | 447.7677 | 497.8208
3990.6135 | 407.4995 | 470.0803 | 447.5851 | 497.7486
3991.6135 | 406.7946 | 469.8601 | 447.4641 | 497.5689
3992.6135 | 406.0733 | 469.6344 | 447.2147 | 497.3872
3993.6135 | 405.3385 | 469.4361 | 447.1661 | 497.5334
3994.6135 | 404.6266 | 469.2388 | 446.9159 | 497.2196
3995.6135 | 403.9933 | 469.0772 | 446.4843 | 497.0673
3996.6135 | 403.2435 | 468.8449 | 446.4093 | 496.7247
3997.6135 | 402.5319 | 468.5998 | 446.2566 | 495.9744
3998.6135 | 401.8262 | 468.3404 | 445.9874 | 495.8884
3999.6135 | 401.1682 | 468.1858 | 445.711 | 495.6869
4000.6135 | 400.4923 | 467.963 | 445.4589 | 495.4158
4001.6135 | 399.8881 | 467.7074 | 445.1386 | 495.4008
4002.6135 | 399.358 | 467.5198 | 444.9392 | 494.886
4003.6135 | 398.748 | 467.3286 | 444.9661 | 495.0404
4004.6135 | 398.1604 | 467.1316 | 444.8091 | 494.8002
4005.6135 | 397.471 | 466.8318 | 444.548 | 494.5432
4006.6135 | 396.8181 | 466.5837 | 444.348 | 494.3263
4007.6135 | 396.1554 | 466.3684 | 444.2063 | 493.7427
4008.6135 | 395.5859 | 466.1052 | 444.1372 | 493.6481
4009.6135 | 394.9495 | 465.8837 | 443.8428 | 493.2338
4010.6135 | 394.3255 | 465.5879 | 443.5863 | 492.8549
4011.6135 | 393.6341 | 465.314 | 443.4189 | 492.6593
4012.6135 | 392.9393 | 465.1037 | 443.1139 | 492.1575
4013.6135 | 392.2461 | 464.6425 | 443.0113 | 492.1365
4014.6135 | 391.6221 | 464.4723 | 442.7285 | 491.7926
4015.6135 | 390.9918 | 464.26 | 442.4491 | 491.4729
4016.6135 | 390.3898 | 464.0791 | 442.1867 | 491.2306
4017.6135 | 389.7532 | 463.8616 | 441.8604 | 491.1687
4018.6135 | 389.1697 | 463.5316 | 441.6252 | 491.0695
4019.6135 | 388.5492 | 463.3289 | 441.6812 | 490.7564
4020.6135 | 387.8827 | 463.1427 | 441.5829 | 490.6014
4021.6135 | 387.2729 | 462.9459 | 441.2774 | 490.2681
4022.6135 | 386.6869 | 462.6702 | 440.9563 | 489.5734
4023.6135 | 386.0601 | 462.3835 | 440.8332 | 489.7214
4024.6135 | 385.4298 | 462.1407 | 440.582 | 489.421
4025.6135 | 384.8379 | 461.9358 | 440.2073 | 489.1119
4026.6135 | 384.2609 | 461.6379 | 440.0385 | 488.9042
4027.6135 | 383.6018 | 461.3373 | 439.7915 | 488.3972
4028.6135 | 382.9045 | 461.135 | 439.2194 | 488.3306
4029.6135 | 382.2656 | 460.9251 | 438.8151 | 488.2407
4030.6135 | 381.6517 | 460.6914 | 438.4808 | 488.0767
4031.6135 | 381.1171 | 460.3979 | 438.3639 | 487.9026
4032.6135 | 380.4989 | 460.1438 | 438.2762 | 487.5987
4033.6135 | 379.9216 | 459.8696 | 438.4054 | 487.5179
4034.6135 | 379.3672 | 459.6306 | 438.1167 | 487.1959
4035.6135 | 378.7874 | 459.3855 | 437.9154 | 486.7725
4036.6135 | 378.1896 | 459.1238 | 437.6958 | 486.6899
4037.6135 | 377.6567 | 458.783 | 437.1901 | 486.4132
4038.6135 | 377.1087 | 458.4648 | 436.9943 | 486.5127
4039.6135 | 376.4715 | 458.1249 | 436.9313 | 486.4463
4040.6135 | 375.9009 | 458.0049 | 436.7923 | 486.2418
4041.6135 | 375.3403 | 457.7504 | 436.5206 | 486.1187
4042.6135 | 374.795 | 457.5148 | 436.052 | 485.7408
4043.6135 | 374.2378 | 457.2642 | 435.8447 | 485.9775
4044.6135 | 373.6402 | 457.0448 | 435.5776 | 485.8915
4045.6135 | 372.9777 | 456.8411 | 435.3965 | 485.7258
4046.6135 | 372.3365 | 456.5147 | 435.2736 | 485.5471
4047.6135 | 371.7411 | 456.2089 | 435.0568 | 485.1535
4048.6135 | 371.1906 | 455.9128 | 434.519 | 485.2978
4049.6135 | 370.6223 | 455.6638 | 434.484 | 485.1264
4050.6135 | 369.989 | 455.416 | 434.306 | 484.7844
4051.6135 | 369.4013 | 455.1473 | 434.1781 | 484.6726
4052.6135 | 368.935 | 454.9519 | 433.7006 | 484.1154
4053.6135 | 368.3566 | 454.7087 | 433.5452 | 484.0234
4054.6135 | 367.7303 | 454.4672 | 433.1756 | 483.9291
4055.6135 | 367.1437 | 454.1829 | 433.212 | 483.6798
4056.6135 | 366.6518 | 453.8712 | 432.8054 | 483.3625
4057.6135 | 366.1042 | 453.6345 | 432.5593 | 482.96
4058.6135 | 365.564 | 453.4122 | 432.4403 | 483.2008
4059.6135 | 364.9923 | 453.1678 | 432.0119 | 482.8557
4060.6135 | 364.4727 | 452.9012 | 431.5935 | 482.6714
4061.6135 | 363.9217 | 452.5718 | 431.2848 | 482.4966
4062.6135 | 363.4072 | 452.4188 | 431.2291 | 481.8052
4063.6135 | 362.8797 | 452.0703 | 430.9979 | 481.8948
4064.6135 | 362.3385 | 451.829 | 430.957 | 481.7498
4065.6135 | 361.8011 | 451.6135 | 430.7321 | 481.5739
4066.6135 | 361.2812 | 451.344 | 430.4353 | 481.5312
4067.6135 | 360.6821 | 451.069 | 429.9702 | 481.1982
4068.6135 | 360.1459 | 450.7244 | 429.7584 | 481.4353
4069.6135 | 359.6377 | 450.4668 | 429.5352 | 481.322
4070.6135 | 359.12 | 450.2041 | 428.9856 | 481.2246
4071.6135 | 358.5156 | 449.883 | 429.0719 | 480.9799
4072.6135 | 357.9436 | 449.6419 | 428.8497 | 480.5171
4073.6135 | 357.3379 | 449.4014 | 428.7317 | 483.3176
4074.6135 | 356.8498 | 449.1698 | 428.3297 | 482.9652
4075.6135 | 356.2965 | 448.9235 | 427.9911 | 482.7127
4076.6135 | 355.8253 | 448.7069 | 427.4415 | 482.4082
4077.6135 | 355.3696 | 448.3597 | 427.1319 | 481.8706
4078.6135 | 354.8944 | 448.1361 | 427.009 | 481.8724
4079.6135 | 354.3418 | 447.8774 | 426.9904 | 481.6457
4080.6135 | 353.843 | 447.5309 | 426.7281 | 481.5745
4081.6135 | 353.3504 | 447.2938 | 426.4557 | 481.3159
4082.6135 | 352.7532 | 447.014 | 426.0554 | 481.0237
4083.6135 | 352.2682 | 446.7047 | 426.0442 | 481.213
4084.6135 | 351.7935 | 446.4361 | 426.0097 | 481.0136
4085.6135 | 351.2923 | 446.2328 | 425.7157 | 480.8403
4086.6135 | 350.7705 | 445.9794 | 425.6074 | 480.7275
4087.6135 | 350.2929 | 445.7388 | 425.3116 | 480.341
4088.6135 | 349.8528 | 445.4719 | 424.726 | 480.4393
4089.6135 | 349.4073 | 445.1912 | 424.44 | 480.1635
4090.6135 | 348.8697 | 444.909 | 423.9755 | 479.8902
4091.6135 | 348.3195 | 444.6697 | 423.961 | 479.711
4092.6135 | 347.8046 | 444.337 | 423.8864 | 479.205
4093.6135 | 347.2252 | 444.0996 | 423.6528 | 479.0425
4094.6135 | 346.643 | 443.7749 | 423.613 | 478.804
4095.6135 | 346.1314 | 443.5543 | 423.2334 | 478.6356
4096.6135 | 345.6699 | 443.2809 | 422.9952 | 478.4874
4097.6135 | 345.2268 | 443.0415 | 422.8282 | 477.893
4098.6135 | 344.7942 | 442.7539 | 422.5392 | 478.0006
4099.6135 | 344.2741 | 442.4325 | 422.4024 | 477.8228
4100.6135 | 343.8226 | 442.0919 | 421.9052 | 477.4668
4101.6135 | 343.4252 | 441.8125 | 421.8046 | 477.131
4102.6135 | 342.8901 | 441.5682 | 421.5482 | 476.5775
4103.6135 | 342.3118 | 441.3623 | 421.4292 | 476.8183
4104.6135 | 341.9227 | 441.0787 | 421.1605 | 476.7372
4105.6135 | 341.4903 | 440.7978 | 421.0122 | 476.4403
4106.6135 | 341.0296 | 440.5736 | 420.8692 | 476.4462
4107.6135 | 340.5823 | 440.3597 | 420.6318 | 475.8553
4108.6135 | 340.116 | 440.043 | 420.2119 | 475.9323
4109.6135 | 339.6473 | 439.7836 | 419.9378 | 476.0318
4110.6135 | 339.1699 | 439.5238 | 419.8371 | 475.9878
4111.6135 | 338.7139 | 439.1807 | 419.7547 | 476.0866
4112.6135 | 338.2521 | 439.0089 | 419.5349 | 475.5302
4113.6135 | 337.7049 | 438.6614 | 419.1679 | 475.7551
4114.6135 | 337.2001 | 438.398 | 418.9007 | 475.4208
4115.6135 | 336.7421 | 438.0793 | 418.6966 | 475.2044
4116.6135 | 336.2484 | 437.8716 | 418.4552 | 475.1666
4117.6135 | 335.8031 | 437.6827 | 418.2284 | 474.6566
4118.6135 | 335.384 | 437.3698 | 417.9253 | 475.1539
4119.6135 | 334.9284 | 437.1413 | 417.8091 | 474.9068
4120.6135 | 334.455 | 436.9178 | 417.6812 | 474.9985
4121.6135 | 333.966 | 436.6571 | 417.1118 | 474.56
4122.6135 | 333.4708 | 436.3389 | 416.8879 | 473.9446
4123.6135 | 332.9906 | 436.1225 | 416.6702 | 474.0544
4124.6135 | 332.4388 | 435.8577 | 416.3855 | 473.9021
4125.6135 | 332.0754 | 435.6091 | 416.1697 | 473.7033
4126.6135 | 331.6963 | 435.2625 | 415.9467 | 473.3252
4127.6135 | 331.2453 | 434.9644 | 415.7477 | 472.8335
4128.6135 | 330.7928 | 434.7069 | 415.3542 | 472.7115
4129.6135 | 330.2933 | 434.4647 | 415.0073 | 472.5945
4130.6135 | 329.8696 | 434.1931 | 414.7848 | 472.3482
4131.6135 | 329.4545 | 433.9227 | 414.7451 | 472.2788
4132.6135 | 329.0432 | 433.6225 | 414.5307 | 471.8286
4133.6135 | 328.6006 | 433.3179 | 414.2512 | 471.9235
4134.6135 | 328.0718 | 433.0801 | 413.9977 | 471.7457
4135.6135 | 327.6158 | 432.9101 | 413.7521 | 471.42
4136.6135 | 327.2121 | 432.4954 | 413.4077 | 471.0783
4137.6135 | 326.8336 | 432.2278 | 413.2774 | 470.7723
4138.6135 | 326.3569 | 432.0613 | 413.0739 | 470.9124
4139.6135 | 325.9198 | 431.8155 | 412.6837 | 470.7388
4140.6135 | 325.49 | 431.4559 | 412.6021 | 470.6113
4141.6135 | 325.0287 | 431.1217 | 412.2393 | 470.4288
4142.6135 | 324.6685 | 430.9043 | 412.0488 | 469.9648
4143.6135 | 324.243 | 430.5914 | 411.8439 | 469.9472
4144.6135 | 323.788 | 430.3578 | 411.651 | 469.7812
4145.6135 | 323.3 | 430.1208 | 411.3642 | 469.5476
4146.6135 | 322.8203 | 429.93 | 410.8552 | 469.2383
4147.6135 | 322.3568 | 429.5049 | 410.5392 | 468.7585
4148.6135 | 321.967 | 429.2679 | 410.3414 | 468.7975
4149.6135 | 321.5651 | 429.0342 | 410.2938 | 468.5546
4150.6135 | 321.1034 | 428.8315 | 410.1044 | 468.251
4151.6135 | 320.7539 | 428.6147 | 409.9291 | 468.047
4152.6135 | 320.3392 | 428.2737 | 409.5693 | 467.5794
4153.6135 | 319.9239 | 428.0256 | 409.323 | 467.6758
4154.6135 | 319.5043 | 427.8059 | 408.8597 | 467.4615
4155.6135 | 319.0643 | 427.5551 | 408.533 | 467.2912
4156.6135 | 318.598 | 427.2174 | 408.3769 | 467.4275
4157.6135 | 318.1928 | 426.9735 | 408.1015 | 466.7712
4158.6135 | 317.8399 | 426.7444 | 407.8966 | 466.9003
4159.6135 | 317.4198 | 426.5261 | 407.7751 | 466.7341
4160.6135 | 316.9402 | 426.302 | 407.6032 | 466.5813
4161.6135 | 316.4988 | 425.9992 | 407.4037 | 466.4453
4162.6135 | 316.0814 | 425.68 | 407.1863 | 466.0285
4163.6135 | 315.6506 | 425.4808 | 406.8557 | 466.1738
4164.6135 | 315.2326 | 425.2459 | 406.6119 | 466.0122
4165.6135 | 314.7771 | 424.9864 | 406.4284 | 465.6871
4166.6135 | 314.3153 | 424.6804 | 406.2452 | 465.416
4167.6135 | 313.8625 | 424.436 | 405.9841 | 464.8835
4168.6135 | 313.4506 | 424.2554 | 405.4557 | 465.0229
4169.6135 | 313.0557 | 423.9468 | 405.0755 | 464.8934
4170.6135 | 312.7209 | 423.6786 | 404.9718 | 464.5607
4171.6135 | 312.3863 | 423.4417 | 404.8105 | 464.3943
4172.6135 | 311.9736 | 423.161 | 404.6267 | 463.815
4173.6135 | 311.6062 | 422.8866 | 404.4628 | 463.9061
4174.6135 | 311.189 | 422.6171 | 404.0001 | 463.6833
4175.6135 | 310.77 | 422.3923 | 403.7128 | 463.4082
4176.6135 | 310.3436 | 422.0944 | 403.3453 | 463.159
4177.6135 | 309.9449 | 421.8083 | 403.2528 | 462.5713
4178.6135 | 309.5637 | 421.5467 | 403.0557 | 462.4737
4179.6135 | 309.1934 | 421.3032 | 402.9143 | 462.2287
4180.6135 | 308.6949 | 421.0798 | 402.5937 | 461.6653
4181.6135 | 308.235 | 420.7723 | 402.1247 | 461.3078
4182.6135 | 307.8479 | 420.5238 | 401.7821 | 461.3724
4183.6135 | 307.4276 | 420.2765 | 401.6658 | 461.8601
4184.6135 | 307.0446 | 420.0797 | 401.3832 | 461.5467
4185.6135 | 306.7053 | 419.8662 | 401.3069 | 461.6182
4186.6135 | 306.2427 | 419.481 | 401.1327 | 461.3725
4187.6135 | 305.7774 | 419.237 | 400.9478 | 460.7215
4188.6135 | 305.4174 | 418.985 | 400.5913 | 460.8828
4189.6135 | 305.0536 | 418.7356 | 400.5014 | 460.6882
4190.6135 | 304.6737 | 418.507 | 400.3496 | 460.4606
4191.6135 | 304.3018 | 418.2374 | 400.1612 | 460.27
4192.6135 | 303.9072 | 417.9648 | 399.9627 | 459.8868
4193.6135 | 303.4949 | 417.7495 | 399.7166 | 459.9711
4194.6135 | 303.1514 | 417.5022 | 399.1917 | 459.7682
4195.6135 | 302.7297 | 417.2264 | 398.9703 | 459.6291
4196.6135 | 302.303 | 416.918 | 398.7685 | 459.465
4197.6135 | 301.8947 | 416.7043 | 398.5912 | 458.9563
4198.6135 | 301.5216 | 416.3941 | 398.3556 | 458.8655
4199.6135 | 301.1283 | 416.1508 | 398.2378 | 458.7312
4200.6135 | 300.761 | 415.8704 | 398.0876 | 458.4896
4201.6135 | 300.3074 | 415.5628 | 397.6692 | 458.3764
4202.6135 | 299.8912 | 415.3923 | 397.4711 | 458.0411
4203.6135 | 299.5356 | 415.149 | 397.4076 | 458.0713
4204.6135 | 299.2001 | 414.9008 | 397.291 | 457.8328
4205.6135 | 298.7982 | 414.5518 | 397.0353 | 457.4033
4206.6135 | 298.4206 | 414.354 | 396.699 | 457.392
4207.6135 | 298.0989 | 414.1064 | 396.3822 | 456.7933
4208.6135 | 297.7539 | 413.791 | 396.1135 | 456.8948
4209.6135 | 297.436 | 413.5241 | 395.8868 | 456.7253
4210.6135 | 297.0693 | 413.3034 | 395.525 | 456.8258
4211.6135 | 296.6382 | 413.0129 | 395.2443 | 456.7691
4212.6135 | 296.2338 | 412.7395 | 394.892 | 456.2864
4213.6135 | 295.9098 | 412.4997 | 394.6938 | 456.2982
4214.6135 | 295.5915 | 412.2495 | 394.5469 | 456.187
4215.6135 | 295.2371 | 412.0359 | 394.3889 | 456.0028
4216.6135 | 294.8822 | 411.7498 | 394.0902 | 455.9607
4217.6135 | 294.5076 | 411.4199 | 393.9967 | 455.5544
4218.6135 | 294.1127 | 411.1372 | 393.5016 | 455.7094
4219.6135 | 293.7417 | 410.955 | 393.2999 | 455.3989
4220.6135 | 293.3806 | 410.6551 | 393.0885 | 455.0888
4221.6135 | 293.0082 | 410.388 | 392.9464 | 455.0721
4222.6135 | 292.6532 | 410.1407 | 392.7506 | 454.7864
4223.6135 | 292.2038 | 409.897 | 392.5062 | 455.1099
4224.6135 | 291.8206 | 409.6228 | 392.1613 | 455.0128
4225.6135 | 291.5183 | 409.4476 | 391.8351 | 454.8129
4226.6135 | 291.133 | 409.176 | 391.1747 | 454.6347
4227.6135 | 290.6406 | 408.8883 | 391.1726 | 454.3106
4228.6135 | 290.1941 | 408.6899 | 391.1485 | 454.4648
4229.6135 | 289.8125 | 408.4614 | 391.0311 | 454.232
4230.6135 | 289.4204 | 408.2315 | 390.5018 | 453.7708
4231.6135 | 289.0922 | 407.9933 | 390.4496 | 453.6606
4232.6135 | 288.7621 | 407.7602 | 390.3053 | 453.1743
4233.6135 | 288.3854 | 407.4459 | 389.7931 | 453.1636
4234.6135 | 288.0587 | 407.2061 | 389.5289 | 452.9122
4235.6135 | 287.7148 | 406.8888 | 389.2546 | 452.5965
4236.6135 | 287.3979 | 406.6631 | 389.3208 | 452.3416
4237.6135 | 287.1045 | 406.4313 | 389.3028 | 451.8363
4238.6135 | 286.7507 | 406.1315 | 389.0354 | 451.8346
4239.6135 | 286.3772 | 405.9059 | 388.8096 | 451.5019
4240.6135 | 286.0981 | 405.6639 | 388.6768 | 451.3517
4241.6135 | 285.7992 | 405.3713 | 388.3922 | 451.033
4242.6135 | 285.4384 | 405.0774 | 388.0836 | 450.6652
4243.6135 | 285.1128 | 404.8852 | 387.8532 | 450.7773
4244.6135 | 284.7997 | 404.6683 | 387.6779 | 450.6355
4245.6135 | 284.4875 | 404.3845 | 387.5144 | 450.4247
4246.6135 | 284.1599 | 404.1782 | 387.1382 | 450.3635
4247.6135 | 283.7888 | 403.8413 | 386.7858 | 449.7972
4248.6135 | 283.4439 | 403.5132 | 386.2674 | 449.9017
4249.6135 | 283.1133 | 403.3669 | 386.253 | 449.5875
4250.6135 | 282.7692 | 403.1413 | 385.9559 | 449.4253
4251.6135 | 282.4092 | 402.8595 | 385.7616 | 449.2633
4252.6135 | 282.0181 | 402.6568 | 385.4874 | 448.9906
4253.6135 | 281.6908 | 402.2977 | 385.3385 | 449.0152
4254.6135 | 281.3985 | 402.058 | 385.1463 | 448.8289
4255.6135 | 281.1388 | 401.785 | 384.9619 | 448.5757
4256.6135 | 280.7867 | 401.5569 | 384.8019 | 448.4113
4257.6135 | 280.415 | 401.3728 | 384.6489 | 448.0014
4258.6135 | 280.0784 | 401.136 | 384.2616 | 448.1123
4259.6135 | 279.6873 | 400.877 | 384.0076 | 447.8526
4260.6135 | 279.3184 | 400.5805 | 383.4797 | 447.6084
4261.6135 | 279.0011 | 400.3024 | 383.3351 | 447.4867
4262.6135 | 278.7081 | 399.8998 | 383.2923 | 447.0357
4263.6135 | 278.3873 | 399.6921 | 383.1611 | 447.2062
4264.6135 | 278.0736 | 399.5635 | 382.9619 | 447.0185
4265.6135 | 277.7498 | 399.3645 | 382.7757 | 446.7648
4266.6135 | 277.4362 | 399.1344 | 382.2854 | 446.6936
4267.6135 | 277.1274 | 398.8223 | 381.9798 | 446.3528
4268.6135 | 276.77 | 398.597 | 381.9033 | 446.5904
4269.6135 | 276.4946 | 398.3487 | 381.7999 | 446.4072
4270.6135 | 276.2053 | 398.0865 | 381.7309 | 446.2658
4271.6135 | 275.8592 | 397.8871 | 381.5995 | 446.2397
4272.6135 | 275.5475 | 397.6137 | 381.2793 | 445.709
4273.6135 | 275.2261 | 397.3296 | 381.0167 | 445.9631
4274.6135 | 274.8729 | 397.039 | 380.673 | 445.875
4275.6135 | 274.5245 | 396.8169 | 380.2093 | 445.6958
4276.6135 | 274.1689 | 396.6091 | 380.0656 | 445.6011
4277.6135 | 273.8264 | 396.3628 | 379.963 | 445.1403
4278.6135 | 273.5013 | 396.1293 | 379.664 | 445.2023
4279.6135 | 273.1653 | 395.9146 | 379.5322 | 444.9746
4280.6135 | 272.8483 | 395.6782 | 379.3134 | 444.6663
4281.6135 | 272.5238 | 395.4321 | 378.9202 | 444.3461
4282.6135 | 272.2296 | 395.185 | 378.8463 | 443.8571
4283.6135 | 271.9194 | 394.9766 | 378.5548 | 443.8715
4284.6135 | 271.5894 | 394.7494 | 378.3517 | 443.6838
4285.6135 | 271.2857 | 394.4212 | 378.2435 | 443.1744
4286.6135 | 270.9204 | 394.1622 | 378.0612 | 443.1439
4287.6135 | 270.5634 | 393.9864 | 377.7205 | 442.4953
4288.6135 | 270.2856 | 393.7581 | 377.3942 | 442.5778
4289.6135 | 269.9871 | 393.5173 | 377.2253 | 442.4507
4290.6135 | 269.666 | 393.2893 | 377.1035 | 442.2001
4291.6135 | 269.2988 | 393.0377 | 376.8319 | 442.1225
4292.6135 | 268.9914 | 392.7502 | 376.6182 | 441.6741
4293.6135 | 268.7324 | 392.4887 | 376.3877 | 441.8849
4294.6135 | 268.4676 | 392.2574 | 376.2142 | 441.7584
4295.6135 | 268.1785 | 391.9634 | 375.8407 | 441.6592
4296.6135 | 267.8693 | 391.7443 | 375.6781 | 441.6231
4297.6135 | 267.5746 | 391.5491 | 375.4686 | 441.1223
4298.6135 | 267.2344 | 391.3568 | 375.3654 | 441.2339
4299.6135 | 266.9793 | 391.0116 | 375.131 | 441.146
4300.6135 | 266.6649 | 390.817 | 374.8209 | 440.9566
4301.6135 | 266.396 | 390.5661 | 374.6443 | 440.8385
4302.6135 | 266.0644 | 390.3341 | 374.4927 | 440.4018
4303.6135 | 265.7791 | 390.1289 | 374.345 | 440.4171
4304.6135 | 265.5107 | 389.9255 | 374.0265 | 440.4181
4305.6135 | 265.2364 | 389.6802 | 373.7884 | 440.1856
4306.6135 | 264.8724 | 389.4675 | 373.4985 | 440.149
4307.6135 | 264.5759 | 389.1695 | 373.2287 | 439.7612
4308.6135 | 264.2541 | 388.8333 | 373.132 | 439.8985
4309.6135 | 263.9666 | 388.6686 | 372.9744 | 439.8509
4310.6135 | 263.6885 | 388.4542 | 372.7729 | 439.7021
4311.6135 | 263.4422 | 388.2439 | 372.5695 | 439.5796
4312.6135 | 263.1114 | 388.0741 | 372.289 | 439.0816
4313.6135 | 262.778 | 387.8407 | 372.16 | 439.166
4314.6135 | 262.4697 | 387.5991 | 371.9629 | 438.9313
4315.6135 | 262.1697 | 387.3344 | 371.6808 | 438.7198
4316.6135 | 261.85 | 387.0364 | 371.3578 | 438.6472
4317.6135 | 261.5602 | 386.8659 | 371.2091 | 438.1805
4318.6135 | 261.2453 | 386.5809 | 370.9521 | 438.2434
4319.6135 | 260.9517 | 386.2825 | 370.8137 | 438.08
4320.6135 | 260.6639 | 386.0183 | 370.5486 | 437.7732
4321.6135 | 260.3656 | 385.8492 | 370.3966 | 437.8237
4322.6135 | 260.062 | 385.6683 | 370.1065 | 437.199
4323.6135 | 259.7793 | 385.2973 | 369.8895 | 437.1323
4324.6135 | 259.511 | 385.0782 | 369.6247 | 436.9238
4325.6135 | 259.2457 | 384.9257 | 369.4312 | 436.6749
4326.6135 | 258.9463 | 384.7112 | 369.2849 | 436.3698
4327.6135 | 258.6409 | 384.5278 | 369.0334 | 435.9103
4328.6135 | 258.3642 | 384.2921 | 368.7631 | 435.863
4329.6135 | 258.0647 | 384.069 | 368.5851 | 435.6016
4330.6135 | 257.7431 | 383.8277 | 368.4857 | 435.3183
4331.6135 | 257.4407 | 383.5267 | 368.1088 | 435.2043
4332.6135 | 257.1586 | 383.3399 | 367.6477 | 434.703
4333.6135 | 256.8627 | 383.1081 | 367.5219 | 434.6489
4334.6135 | 256.5794 | 382.8694 | 367.4849 | 434.3634
4335.6135 | 256.3066 | 382.704 | 367.3196 | 433.9261
4336.6135 | 256.0108 | 382.4464 | 367.1223 | 433.6902
4337.6135 | 255.7443 | 382.1554 | 367.0364 | 432.9723
4338.6135 | 255.4498 | 381.9722 | 366.7295 | 432.9617
4339.6135 | 255.1678 | 381.7526 | 366.5139 | 432.7578
4340.6135 | 254.9265 | 381.4384 | 366.0929 | 432.5016
4341.6135 | 254.6805 | 381.211 | 365.9031 | 432.201
4342.6135 | 254.4187 | 380.969 | 365.7591 | 431.778
4343.6135 | 254.1496 | 380.6976 | 365.5781 | 431.8132
4344.6135 | 253.8419 | 380.5109 | 365.3575 | 431.6374
4345.6135 | 253.5451 | 380.3459 | 365.1367 | 431.3769
4346.6135 | 253.261 | 380.1142 | 365.0385 | 431.0288
4347.6135 | 252.9706 | 379.8621 | 364.7014 | 430.5254
4348.6135 | 252.6649 | 379.678 | 364.3621 | 430.5094
4349.6135 | 252.3796 | 379.4095 | 364.111 | 430.1789
4350.6135 | 252.1353 | 379.1701 | 364.0351 | 429.8493
4351.6135 | 251.8989 | 378.9062 | 363.8839 | 429.6908
4352.6135 | 251.6318 | 378.7267 | 363.7388 | 429.1253
4353.6135 | 251.331 | 378.5132 | 363.4055 | 429.1314
4354.6135 | 251.0105 | 378.2577 | 363.1076 | 428.8673
4355.6135 | 250.7059 | 378.0704 | 363.0251 | 428.6715
4356.6135 | 250.4313 | 377.794 | 362.8281 | 428.4281
4357.6135 | 250.1398 | 377.5357 | 362.5761 | 427.908
4358.6135 | 249.8775 | 377.311 | 362.5222 | 428.0167
4359.6135 | 249.5821 | 377.0831 | 362.1913 | 427.7131
4360.6135 | 249.2967 | 376.8907 | 361.9424 | 427.4223
4361.6135 | 249.0166 | 376.6537 | 361.8462 | 427.2614
4362.6135 | 248.7708 | 376.4038 | 361.7191 | 426.8506
4363.6135 | 248.5279 | 376.2166 | 361.4786 | 426.9993
4364.6135 | 248.2699 | 375.9762 | 361.2954 | 426.6034
4365.6135 | 248.0068 | 375.6741 | 361.0833 | 426.3676
4366.6135 | 247.7445 | 375.2957 | 360.693 | 426.1596
4367.6135 | 247.4649 | 375.1604 | 360.3135 | 425.61
4368.6135 | 247.2051 | 375.0063 | 360.1354 | 425.6741
4369.6135 | 246.9338 | 374.7704 | 359.9276 | 425.4361
4370.6135 | 246.6667 | 374.6286 | 359.754 | 425.1719
4371.6135 | 246.3653 | 374.3703 | 359.5708 | 425.1189
4372.6135 | 246.1244 | 374.0706 | 359.4221 | 424.5547
4373.6135 | 245.8504 | 373.8809 | 359.1149 | 424.663
4374.6135 | 245.6106 | 373.6477 | 358.9951 | 424.493
4375.6135 | 245.3497 | 373.383 | 358.7985 | 424.0687
4376.6135 | 245.0766 | 373.2431 | 358.5428 | 423.888
4377.6135 | 244.8015 | 373.0289 | 358.3682 | 423.6059
4378.6135 | 244.5507 | 372.7091 | 358.1087 | 423.7256
4379.6135 | 244.295 | 372.513 | 357.9528 | 423.2601
4380.6135 | 244.0413 | 372.2937 | 357.6089 | 422.9186
4381.6135 | 243.803 | 372.0372 | 357.4988 | 422.6245
4382.6135 | 243.5586 | 371.8483 | 357.3096 | 422.1323
4383.6135 | 243.2571 | 371.647 | 357.12 | 422.2245
4384.6135 | 243.0198 | 371.4407 | 356.9039 | 421.9474
4385.6135 | 242.7517 | 371.2265 | 356.7259 | 421.6802
4386.6135 | 242.5353 | 370.9273 | 356.6421 | 421.4893
4387.6135 | 242.2792 | 370.7615 | 356.4662 | 420.9297
4388.6135 | 242.0141 | 370.4856 | 356.225 | 420.9577
4389.6135 | 241.7678 | 370.2948 | 355.9902 | 420.7119
4390.6135 | 241.5 | 370.0495 | 355.6273 | 420.3815
4391.6135 | 241.2354 | 369.8743 | 355.5075 | 420.1436
4392.6135 | 240.9835 | 369.6558 | 355.2538 | 419.6285
4393.6135 | 240.7564 | 369.3992 | 355.114 | 419.8058
4394.6135 | 240.5391 | 369.1714 | 354.9874 | 419.4916
4395.6135 | 240.272 | 369.0009 | 354.8041 | 419.2019
4396.6135 | 239.9925 | 368.7703 | 354.5716 | 418.9428
4397.6135 | 239.6999 | 368.5515 | 354.3984 | 418.4364
4398.6135 | 239.4172 | 368.25 | 354.0706 | 418.5137
4399.6135 | 239.1907 | 368.0527 | 353.7718 | 418.2374
4400.6135 | 238.9272 | 367.861 | 353.7096 | 417.9828
4401.6135 | 238.6283 | 367.5915 | 353.5267 | 417.7861
4402.6135 | 238.3739 | 367.3803 | 353.2258 | 417.2826
4403.6135 | 238.0968 | 367.1175 | 353.0223 | 417.34
4404.6135 | 237.8518 | 366.9467 | 352.8455 | 417.0202
4405.6135 | 237.5593 | 366.781 | 352.6857 | 416.7712
4406.6135 | 237.3161 | 366.545 | 352.448 | 416.5097
4407.6135 | 237.0334 | 366.3706 | 352.2535 | 415.9765
4408.6135 | 236.7888 | 366.1593 | 352.0695 | 416.023
4409.6135 | 236.5654 | 365.9084 | 351.9225 | 415.8143
4410.6135 | 236.338 | 365.6453 | 351.7561 | 415.5803
4411.6135 | 236.0973 | 365.4482 | 351.5076 | 415.1883
4412.6135 | 235.9121 | 365.2333 | 351.4693 | 414.6893
4413.6135 | 235.6703 | 364.9858 | 351.3344 | 414.7618
4414.6135 | 235.4223 | 364.7462 | 351.1358 | 414.5768
4415.6135 | 235.1825 | 364.5553 | 350.8894 | 414.3318
4416.6135 | 234.9381 | 364.3864 | 350.5834 | 414.1342
4417.6135 | 234.7028 | 364.1881 | 350.3064 | 413.6139
4418.6135 | 234.4937 | 363.9682 | 350.1488 | 413.6549
4419.6135 | 234.2141 | 363.7821 | 349.9375 | 413.4151
4420.6135 | 233.9741 | 363.5842 | 349.7026 | 413.189
4421.6135 | 233.701 | 363.3579 | 349.4605 | 412.9481
4422.6135 | 233.4462 | 363.1414 | 349.3177 | 412.2826
4423.6135 | 233.2275 | 362.9174 | 349.1845 | 412.306
4424.6135 | 232.9495 | 362.7315 | 349.0542 | 411.9923
4425.6135 | 232.7101 | 362.5783 | 348.8151 | 411.8235
4426.6135 | 232.4652 | 362.3843 | 348.6088 | 411.6434
4427.6135 | 232.2224 | 362.1594 | 348.3575 | 411.1406
4428.6135 | 231.9615 | 361.9026 | 348.2443 | 411.1095
4429.6135 | 231.7249 | 361.6957 | 348.0735 | 410.1932
4430.6135 | 231.5195 | 361.4352 | 347.8557 | 410.5767
4431.6135 | 231.3065 | 361.2391 | 347.5916 | 410.3398
4432.6135 | 231.065 | 361.0135 | 347.4273 | 409.7818
4433.6135 | 230.8086 | 360.7593 | 347.3214 | 409.7367
4434.6135 | 230.593 | 360.5327 | 347.0997 | 409.5754
4435.6135 | 230.3661 | 360.3904 | 346.845 | 409.0183
4436.6135 | 230.1341 | 360.0958 | 346.7325 | 408.8466
4437.6135 | 229.9293 | 359.8375 | 346.4808 | 408.5376
4438.6135 | 229.6656 | 359.663 | 346.1526 | 408.5363
4439.6135 | 229.3748 | 359.4761 | 345.9968 | 408.2557
4440.6135 | 229.1219 | 359.254 | 345.8904 | 407.6493