## Test Conditions
DESIREE-FIRE Test Number 37 - Circuit Simulator Data Only
Test Date: | 2009-09-23
DCSim DAQ Start Time | 14:19
DCSim Time for Synchronization | 14:38
Heat Source Synchronization | 0:47 | minutes:seconds
Heat Source DAQ Start Time | 14:37
Fire Time | 14:39
Offset | 0:20 | minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 1180 | seconds
Heat Source Offset | 0:02 | minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 108 | seconds
Heat Source Stop Time | 15:09
Test Duration | 0:31 | minutes:seconds
| 1830 | seconds
CT500 turns | 2 | 1 or 2 | This is the number of times the lead conductor within the DCSim Panels were wrapped around the Hall Effect Device of the current transducer.
CT35 turns | 5 | 1 or 5
Pre-Test Baseline: | Gathered | Gathered or Not Gathered
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit number | Cable Type |  | Cable TC channel | Air TC Channel
MOV 1 | XLPE/CSPE, 7c, 12AWG |  | Channel 3 and Channel 4 represent the side and top of the thermocouple cable, respectively. | TC11 in the Temperature Data File
MOV 2 | XLPE/CSPE, 7c, 12AWG |  | Channel 3 and Channel 4 represent the side and top of the thermocouple cable, respectively. | TC11 in the Temperature Data File
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds. Two different current transducers were for each circuit. One current transducer (Ohio Semitronics, model number CTL-51/35) was used to detect lower (0 - 35A) amperage transient behavior through a paired and calibrated signal conditioner (CTA201RX5). The other transducer (Ohio Semitronics, model number CTL-601/500) was set to detect transient current increases from 0 - 500A. These were also paired and calibrated with a signal conditioner (CTA2-1X5).
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | MOV-1_CT500 | MOV-1a_CT35_1_P | MOV-1a_CT35_2_N | MOV-1b_CT35_1_G | MOV-1b_CT35_2_R | MOV-1b_CT35_3_YO | MOV-1b_CT35_4_YC | MOV-2_CT500 | MOV-2a_CT35_1_P | MOV-2a_CT35_2_N | MOV-2b_CT35_1_G | MOV-2b_CT35_2_R | MOV-2b_CT35_3_YO | 2b_CT35_4_YC1 | MOV-1a_VT7_1_SP | MOV-1a_VTU_1_P | MOV-1a_VTU_2_N | MOV-1b_VT7_1_G | MOV-1b_VT7_2_R | MOV-1b_VT7_3_YO1 | MOV-1b_VT7_4_YC1 | MOV-2a_VT7_1_SP | MOV-2a_VTU_1_P | MOV-2a_VTU_2_N | MOV-2b_VT7_1_G | MOV-2b_VT7_2_R | 2b_VT7_3_YO1 | MOV-2b_VT7_4_YC1 | {MOV1} V(N) - V(Batt -) | {MOV1} V(P) - V(Batt +) | {MOV1} V(G) - V(Batt +) | {MOV1} V(R) - V(Batt -) | {MOV1} V(YC1) - V(Batt -) | {MOV1} V(YO1) - V(Batt -) | {MOV1} V(YC1) - V(N) | {MOV1} V(YO1) - V(N) | {MOV2} V(N) - V(Batt -) | {MOV2} V(P) - V(Batt +) | {MOV2} V(G) - V(Batt +) | {MOV2} V(R) - V(Batt -) | {MOV2} V(YC1) - V(Batt -) | {MOV2} V(YO1) - V(Batt -) | {MOV2} V(YC1) - V(N) | {MOV2} V(YO1) - V(N) | {MOV-1} V(R) - V(N) | {MOV-1} V(G) - V(N) | {MOV-2} V(R) - V(N) | {MOV-2} V(G) - V(N) | {MOV-1} V(P) - V(N) | {MOV-2} V(P) - V(N) | {MOV-1} V(P) - V(Batt -) | {MOV-2} V(P) - V(Batt -) | {MOV-1} V(N) - V(Batt +) | {MOV-2} V(N) - V(Batt +) | {MOV-1} V(G) - V(Batt -) | {MOV2} V(G) - V(Batt-) | {MOV1} V(SP) - V(Batt -) | {MOV2} V(SP) - V(Batt -)
-0.6875 | 122.731 | -59.2712 | 63.0981 | -0.042954 | 0.0009122 | 0.065085 | 0.061517 | -0.00029898 | -0.0025336 | 0.00055974 | -0.027466 | 0.00099115 | 0.067157 | 0.06178 | -0.002273 | 0.0049517 | -0.0030954 | -0.07782 | 63.0066 | -59.3399 | 63.2767 | -59.1934 | -59.5551 | -59.5596 | -0.054932 | 62.9745 | -59.2712 | 63.2401 | -59.2941 | -59.4177 | -59.3811 | -0.068665 | -0.091553 | 0.17853 | 0.07782 | -0.28839 | -0.28381 | -0.21973 | -0.21515 | 0 | -0.1236 | 0.14191 | -0.022888 | -0.10986 | -0.14648 | -0.10986 | -0.14648 | 0.14648 | 122.6166 | -0.022888 | 122.5113 | 122.3465 | 122.2458 | 122.2778 | 122.2458 | -122.4381 | -122.3694 | 122.5479 | 122.5113 | 59.1934 | 59.2163
0.3125 | 122.7585 | -59.2804 | 63.0707 | -0.042954 | 0.002194 | 0.066366 | 0.061944 | -0.005426 | -0.0016792 | 0.0014141 | -0.01831 | 0.00035035 | 0.06502 | 0.066266 | -0.0031274 | 0.0026019 | 0.001177 | -0.013733 | 62.9654 | -59.2941 | 63.2996 | -59.1202 | -59.5367 | -59.491 | -0.013733 | 62.9517 | -59.2438 | 63.2538 | -59.2667 | -59.404 | -59.3719 | -0.013732 | -0.10529 | 0.22888 | 0.16022 | -0.21057 | -0.25635 | -0.19684 | -0.24262 | 0.036622 | -0.11902 | 0.18311 | 0.013733 | -0.091552 | -0.1236 | -0.12817 | -0.16022 | 0.17395 | 122.5937 | -0.022889 | 122.4976 | 122.2595 | 122.1954 | 122.2458 | 122.2321 | -122.3648 | -122.3145 | 122.58 | 122.5342 | 59.2667 | 59.2667
1.3125 | 122.7219 | -59.2941 | 63.089 | -0.11925 | 0.0036892 | 0.065085 | 0.061731 | -0.0024354 | 0.00088444 | 0.00034614 | -0.036621 | -0.00050405 | 0.066089 | 0.054944 | -0.003341 | 0.0049517 | -0.0037362 | -0.013733 | 62.9562 | -59.2896 | 63.0615 | -59.2163 | -59.4086 | -59.4727 | 0.009155 | 62.9288 | -59.2529 | 63.2538 | -59.2758 | -59.404 | -59.3948 | 0.004577 | -0.13275 | -0.027466 | 0.077819 | -0.17853 | -0.11444 | -0.1831 | -0.11902 | 0.041198 | -0.16022 | 0.1648 | 0.01831 | -0.10071 | -0.10986 | -0.14191 | -0.15106 | 0.073242 | 122.3511 | -0.022888 | 122.5067 | 122.2458 | 122.1817 | 122.2504 | 122.2229 | -122.3785 | -122.3419 | 122.3557 | 122.5479 | 59.2804 | 59.3033
2.3125 | 122.7402 | -59.2392 | 63.1302 | -0.027695 | 0.0009122 | 0.064016 | 0.060449 | 0.0011962 | -0.0029608 | -0.0024311 | 0.012207 | -0.0015723 | 0.066516 | 0.06178 | -0.0041956 | 0.0045245 | -0.0013864 | 0.050354 | 63.0112 | -59.2484 | 63.3682 | -59.0424 | -59.4223 | -59.436 | 0.11444 | 62.9929 | -59.2392 | 63.2675 | -59.2072 | -59.3399 | -59.3536 | -0.009155 | -0.11902 | 0.23804 | 0.19684 | -0.19684 | -0.18311 | -0.18768 | -0.17395 | 0 | -0.13733 | 0.13733 | 0.032044 | -0.11444 | -0.10071 | -0.11444 | -0.10071 | 0.20599 | 122.6166 | 0.032044 | 122.5067 | 122.2595 | 122.2321 | 122.2504 | 122.2321 | -122.3785 | -122.3694 | 122.6074 | 122.5067 | 59.2896 | 59.3536
3.3125 | 122.7585 | -59.2529 | 63.1165 | -0.14214 | 0.0019802 | 0.064657 | 0.062799 | 0.0020508 | -0.004029 | 0.0012005 | -0.036621 | 0.00077755 | 0.064593 | 0.066266 | -0.003982 | 0.0040973 | 0.0005362 | -0.013733 | 62.9562 | -59.3262 | 63.3133 | -59.1248 | -59.4955 | -59.5047 | -0.018311 | 62.9288 | -59.2438 | 63.2492 | -59.2712 | -59.4131 | -59.3857 | -0.073242 | -0.16022 | 0.19684 | 0.12817 | -0.25177 | -0.24261 | -0.17853 | -0.16937 | 0.009156 | -0.18768 | 0.13275 | -0.01831 | -0.13275 | -0.16022 | -0.14191 | -0.16937 | 0.20142 | 122.6395 | -0.027466 | 122.493 | 122.2824 | 122.1725 | 122.2092 | 122.1817 | -122.4426 | -122.3602 | 122.5662 | 122.5021 | 59.2392 | 59.2346
4.3125 | 122.7631 | -59.2804 | 63.1119 | -0.081101 | 0.002194 | 0.063803 | 0.062585 | -0.00051278 | -0.0042426 | -0.0013629 | -0.039673 | 0.00099115 | 0.065448 | 0.065625 | -0.0027002 | 0.0043109 | -0.0009592 | -0.022888 | 62.9608 | -59.3399 | 63.3133 | -59.1293 | -59.523 | -59.491 | -0.027466 | 62.9288 | -59.2712 | 63.2812 | -59.2896 | -59.4086 | -59.3674 | -0.059509 | -0.15106 | 0.20142 | 0.15106 | -0.21057 | -0.24261 | -0.15106 | -0.1831 | 0.009156 | -0.1831 | 0.16937 | -0.009155 | -0.086975 | -0.12817 | -0.096131 | -0.13733 | 0.21057 | 122.6532 | -0.018311 | 122.5525 | 122.3007 | 122.2 | 122.2412 | 122.2092 | -122.4518 | -122.3831 | 122.5937 | 122.5616 | 59.2575 | 59.2529
5.3125 | 122.7631 | -59.2804 | 63.0981 | -0.13451 | 0.002194 | 0.065085 | 0.062372 | 0.0011962 | -0.0031744 | 0.0016277 | -0.01831 | 0.00099115 | 0.065661 | 0.065411 | -0.0041956 | 0.0026019 | 0.0005362 | 0 | 62.9745 | -59.3033 | 63.3316 | -59.0927 | -59.5139 | -59.4864 | -0.013733 | 62.9288 | -59.2529 | 63.2629 | -59.2758 | -59.3765 | -59.3811 | -0.022888 | -0.1236 | 0.23346 | 0.18768 | -0.20599 | -0.23346 | -0.18311 | -0.21057 | 0.027466 | -0.16937 | 0.16479 | 0.004578 | -0.10071 | -0.09613 | -0.12817 | -0.1236 | 0.21057 | 122.6349 | -0.022888 | 122.5159 | 122.2778 | 122.1817 | 122.2549 | 122.2092 | -122.4014 | -122.3511 | 122.612 | 122.5433 | 59.2804 | 59.2667
6.3125 | 122.6624 | -59.2758 | 63.1531 | -0.020065 | 5.76e-05 | 0.06188 | 0.060449 | -0.003717 | -0.00082456 | -0.00072206 | -0.0030517 | 0.0012047 | 0.065234 | 0.061352 | -0.0016322 | 0.0038837 | -0.0007456 | 0.054932 | 63.002 | -59.2804 | 63.3453 | -59.2667 | -59.5551 | -59.3994 | 0.027466 | 63.0066 | -59.2392 | 63.176 | -59.2987 | -59.4498 | -59.4543 | -0.004578 | -0.15106 | 0.19226 | 0.009155 | -0.1236 | -0.27924 | -0.11902 | -0.27466 | 0.036621 | -0.14648 | 0.022888 | -0.022888 | -0.17853 | -0.17395 | -0.21515 | -0.21057 | 0.013733 | 122.6257 | -0.059509 | 122.4152 | 122.2824 | 122.2458 | 122.2778 | 122.2824 | -122.4335 | -122.3923 | 122.6212 | 122.4518 | 59.3308 | 59.3033
7.3125 | 122.6898 | -59.2758 | 63.1393 | -0.050583 | 0.0013394 | 0.064016 | 0.062158 | -0.0015808 | -0.0021064 | -0.0034991 | 0.0091553 | 0.0014185 | 0.06502 | 0.06413 | 0.00093143 | 0.0015337 | -0.0018136 | -0.022888 | 62.9791 | -59.3308 | 63.2675 | -59.166 | -59.5367 | -59.523 | -0.064087 | 62.9608 | -59.2529 | 63.208 | -59.3079 | -59.404 | -59.4223 | -0.054932 | -0.16022 | 0.12817 | 0.10986 | -0.24719 | -0.26093 | -0.19226 | -0.20599 | 0.022888 | -0.17853 | 0.068665 | -0.032043 | -0.14648 | -0.12817 | -0.16937 | -0.15106 | 0.1648 | 122.5983 | -0.054931 | 122.4609 | 122.3099 | 122.2137 | 122.2549 | 122.2366 | -122.4701 | -122.3923 | 122.5433 | 122.4838 | 59.2529 | 59.2117
8.3125 | 122.7081 | -59.2804 | 63.1073 | -0.11162 | 0.0028348 | 0.065939 | 0.061944 | 0.0018372 | -0.00018376 | 0.00013254 | -0.0091553 | -0.00029045 | 0.065875 | 0.05473 | -0.0014184 | 0.0066607 | -0.0013864 | -0.032043 | 62.9562 | -59.2987 | 63.327 | -59.0836 | -59.5139 | -59.5001 | 0.004578 | 62.9425 | -59.2484 | 63.2309 | -59.2804 | -59.3948 | -59.3811 | -0.01831 | -0.15106 | 0.21973 | 0.19684 | -0.21973 | -0.23346 | -0.20142 | -0.21515 | 0.032044 | -0.1648 | 0.1236 | 0 | -0.10071 | -0.11444 | -0.13275 | -0.14648 | 0.21515 | 122.6257 | -0.032044 | 122.4792 | 122.2549 | 122.1909 | 122.2366 | 122.2229 | -122.406 | -122.3557 | 122.6074 | 122.5113 | 59.2484 | 59.285
9.3125 | 122.731 | -59.2712 | 63.0936 | -0.14977 | 0.0009122 | 0.066153 | 0.061731 | 0.00098262 | -0.0029608 | 0.0018413 | -0.0061035 | 0.00013675 | 0.066943 | 0.06413 | -0.00013677 | 0.0060199 | 0.0016044 | -0.022888 | 62.9562 | -59.2941 | 63.3133 | -59.1156 | -59.5001 | -59.4864 | -0.004578 | 62.9242 | -59.2621 | 63.2538 | -59.2758 | -59.3857 | -59.3811 | -0.022888 | -0.13733 | 0.21973 | 0.15564 | -0.21515 | -0.22888 | -0.19226 | -0.20599 | 0.009155 | -0.16937 | 0.16022 | -0.004578 | -0.10986 | -0.11444 | -0.11902 | -0.1236 | 0.17853 | 122.6074 | -0.013733 | 122.5159 | 122.2504 | 122.1863 | 122.2275 | 122.1954 | -122.3877 | -122.3557 | 122.5845 | 122.525 | 59.2484 | 59.2667
10.3125 | 122.7631 | -59.2896 | 63.1256 | -0.050583 | 0.0009122 | 0.064871 | 0.064081 | -0.0024354 | 0.001098 | 0.00098694 | -0.05188 | -0.00050405 | 0.065234 | 0.067334 | -0.002273 | 0.0040973 | -0.0007456 | -0.009155 | 62.9517 | -59.3216 | 63.3179 | -59.1339 | -59.523 | -59.5001 | -0.018311 | 62.9471 | -59.2621 | 63.2355 | -59.2712 | -59.3994 | -59.3674 | -0.032043 | -0.17395 | 0.19226 | 0.15564 | -0.21057 | -0.23346 | -0.17853 | -0.20142 | 0.027466 | -0.17853 | 0.10986 | 0.018311 | -0.07782 | -0.10986 | -0.10529 | -0.13733 | 0.18768 | 122.6395 | -0.009155 | 122.4976 | 122.2733 | 122.2092 | 122.2412 | 122.2366 | -122.4472 | -122.3877 | 122.6074 | 122.525 | 59.2804 | 59.2712
11.3125 | 122.6944 | -59.2575 | 63.1577 | -0.058212 | 0.0006986 | 0.064871 | 0.062158 | 0.0031188 | 0.00067084 | -0.00093566 | 0.0030517 | -0.00029045 | 0.065234 | 0.05943 | 7.6828e-05 | 0.0043109 | -0.0028818 | 0.082397 | 63.0112 | -59.2667 | 63.3545 | -59.0698 | -59.4452 | -59.4498 | 0.09613 | 62.9791 | -59.2346 | 63.2401 | -59.2438 | -59.3765 | -59.3765 | -0.009156 | -0.14648 | 0.19684 | 0.18768 | -0.19226 | -0.18768 | -0.1831 | -0.17853 | 0.022888 | -0.17853 | 0.082397 | 0.013733 | -0.11902 | -0.11902 | -0.14191 | -0.14191 | 0.19684 | 122.6212 | -0.009155 | 122.4747 | 122.2778 | 122.2137 | 122.2687 | 122.2366 | -122.4243 | -122.3923 | 122.612 | 122.4976 | 59.3399 | 59.3536
12.3125 | 122.7036 | -59.2758 | 63.1073 | -0.065842 | 0.0028348 | 0.06423 | 0.061944 | -0.0017944 | 2.9842e-05 | -8.1264e-05 | -0.012207 | 0.0012047 | 0.067798 | 0.058148 | -0.0016322 | 0.0021747 | 0.0020316 | -0.027466 | 62.9608 | -59.3124 | 63.3087 | -59.111 | -59.5184 | -59.4955 | -0.027466 | 62.97 | -59.2712 | 63.1714 | -59.2621 | -59.4177 | -59.436 | -0.036621 | -0.14649 | 0.20142 | 0.16479 | -0.21973 | -0.24262 | -0.18311 | -0.20599 | 0.004578 | -0.13733 | 0.064087 | 0.013733 | -0.16022 | -0.14191 | -0.16479 | -0.14648 | 0.20142 | 122.6212 | 0.009155 | 122.4426 | 122.2733 | 122.2412 | 122.2366 | 122.2458 | -122.4197 | -122.3785 | 122.5845 | 122.4472 | 59.2484 | 59.2484
13.3125 | 122.731 | -59.2804 | 63.0936 | -0.065842 | 0.0026212 | 0.064657 | 0.061517 | 0.0011962 | -0.0010382 | 0.0014141 | -0.030517 | -0.00093145 | 0.067584 | 0.064557 | -0.002273 | 0.0036699 | -0.0043772 | 0 | 62.9425 | -59.317 | 63.3179 | -59.1156 | -59.5001 | -59.4955 | -0.004578 | 62.9196 | -59.2667 | 63.2538 | -59.2758 | -59.3994 | -59.3674 | -0.036621 | -0.15106 | 0.2243 | 0.1648 | -0.21515 | -0.21973 | -0.17853 | -0.1831 | 0.013733 | -0.17395 | 0.16022 | 0.004578 | -0.086975 | -0.11902 | -0.10071 | -0.13275 | 0.20142 | 122.6349 | -0.009155 | 122.5204 | 122.2595 | 122.1863 | 122.2229 | 122.2 | -122.4106 | -122.3602 | 122.5983 | 122.5342 | 59.2804 | 59.2758
14.3125 | 122.7539 | -59.2667 | 63.1393 | -0.058212 | 0.0019802 | 0.06423 | 0.062158 | -8.538e-05 | -0.0025336 | 0.0014141 | -0.01831 | -0.0013587 | 0.065448 | 0.063275 | -0.0024866 | 0.0017473 | -0.0013864 | -0.032043 | 62.9562 | -59.2987 | 63.3224 | -59.1019 | -59.5184 | -59.491 | 0 | 62.9379 | -59.2712 | 63.2492 | -59.2987 | -59.4177 | -59.491 | -0.032043 | -0.1831 | 0.18311 | 0.16479 | -0.2243 | -0.25177 | -0.19226 | -0.21973 | -0.004577 | -0.20142 | 0.10986 | -0.032043 | -0.2243 | -0.15106 | -0.21973 | -0.14648 | 0.19684 | 122.6212 | -0.027466 | 122.5204 | 122.2549 | 122.2092 | 122.2229 | 122.2046 | -122.438 | -122.4106 | 122.5891 | 122.5159 | 59.2346 | 59.2667
15.3125 | 122.7539 | -59.285 | 63.0936 | -0.058212 | 0.0026212 | 0.066153 | 0.062799 | -0.00029898 | -0.0016792 | -0.0034991 | -0.036621 | 0.00035035 | 0.064807 | 0.060284 | -0.0027002 | 0.0047381 | -0.0011728 | -0.027466 | 62.9837 | -59.3262 | 63.3224 | -59.1248 | -59.5093 | -59.491 | -0.032043 | 62.9105 | -59.2621 | 63.2492 | -59.2484 | -59.3948 | -59.3628 | -0.041199 | -0.10986 | 0.22888 | 0.16022 | -0.20599 | -0.2243 | -0.16479 | -0.1831 | 0.022888 | -0.18311 | 0.15564 | 0.036621 | -0.07782 | -0.10986 | -0.10071 | -0.13275 | 0.20142 | 122.6486 | 0.013733 | 122.5113 | 122.3099 | 122.1725 | 122.2687 | 122.1954 | -122.4197 | -122.3557 | 122.6074 | 122.5342 | 59.2575 | 59.2529
16.3125 | 122.6074 | -59.2621 | 63.176 | 0.018082 | 0.0013394 | 0.062735 | 0.060449 | 0.0016236 | -0.0055244 | -0.0015765 | -0.045776 | 0.00056395 | 0.065234 | 0.067761 | -0.00077757 | 0.0049517 | 0.0007498 | -0.009155 | 63.0432 | -59.317 | 63.2309 | -59.2072 | -59.5596 | -59.5551 | -0.018311 | 63.0203 | -59.2621 | 63.1622 | -59.3353 | -59.4543 | -59.4452 | -0.054932 | -0.13275 | 0.054932 | 0.054932 | -0.29297 | -0.29755 | -0.23804 | -0.24261 | 0 | -0.15564 | -0.013733 | -0.073242 | -0.1831 | -0.19226 | -0.1831 | -0.19226 | 0.10986 | 122.5479 | -0.073242 | 122.4243 | 122.3602 | 122.2824 | 122.3053 | 122.2824 | -122.493 | -122.438 | 122.493 | 122.4243 | 59.2529 | 59.2438
17.3125 | 122.6898 | -59.2621 | 63.121 | -0.058212 | 0.0013394 | 0.06658 | 0.062372 | -0.0013672 | -0.0012518 | -0.00072206 | -0.0061035 | 0.0012047 | 0.065875 | 0.063275 | -0.00099117 | 0.0030291 | -0.0054452 | -0.027466 | 62.9791 | -59.3124 | 63.2721 | -59.2484 | -59.6008 | -59.4955 | -0.073242 | 62.9379 | -59.2758 | 63.2034 | -59.3033 | -59.404 | -59.4223 | -0.050354 | -0.14191 | 0.15106 | 0.013733 | -0.23346 | -0.33875 | -0.18311 | -0.28839 | -0.013733 | -0.18311 | 0.082397 | -0.041199 | -0.16022 | -0.14191 | -0.14648 | -0.12817 | 0.064087 | 122.5845 | -0.027466 | 122.4792 | 122.2916 | 122.2137 | 122.2412 | 122.2 | -122.4335 | -122.3969 | 122.5342 | 122.4655 | 59.2346 | 59.1888
18.3125 | 122.7219 | -59.3262 | 63.1165 | -0.012436 | 0.0019802 | 0.063589 | 0.063867 | -0.0035034 | -0.0014654 | -0.0020039 | -0.076294 | 0.0012047 | 0.065234 | 0.067761 | -0.0020594 | 0.0064471 | 0.0020316 | -0.07782 | 62.9791 | -59.3399 | 63.2309 | -59.2209 | -59.5825 | -59.5734 | -0.10071 | 62.9791 | -59.285 | 63.1805 | -59.2804 | -59.4589 | -59.436 | -0.013733 | -0.13733 | 0.11444 | 0.10529 | -0.24719 | -0.25635 | -0.23346 | -0.24262 | 0.041199 | -0.13733 | 0.064087 | 0.045776 | -0.10986 | -0.13275 | -0.15106 | -0.17395 | 0.11902 | 122.5708 | 0.004577 | 122.4655 | 122.319 | 122.2641 | 122.3053 | 122.3053 | -122.4564 | -122.4014 | 122.5571 | 122.5067 | 59.2484 | 59.2255
19.3125 | 122.7448 | -59.2896 | 63.0707 | -0.08873 | 0.0011258 | 0.066153 | 0.061944 | -0.004358 | -0.0031744 | 0.00098694 | -0.061035 | 0.0024865 | 0.065875 | 0.063916 | -0.003982 | 0.0066607 | 0.0009634 | -0.032043 | 62.9791 | -59.3445 | 63.3087 | -59.1339 | -59.523 | -59.5001 | -0.027466 | 62.9379 | -59.2667 | 63.2584 | -59.2621 | -59.3903 | -59.3582 | -0.054931 | -0.091553 | 0.23804 | 0.15564 | -0.21057 | -0.23346 | -0.15564 | -0.17853 | 0.022888 | -0.13275 | 0.18768 | 0.027466 | -0.068664 | -0.10071 | -0.091552 | -0.1236 | 0.21057 | 122.6532 | 0.004578 | 122.525 | 122.3236 | 122.2046 | 122.2687 | 122.2275 | -122.4152 | -122.3373 | 122.5983 | 122.5479 | 59.2575 | 59.2621
20.3125 | 122.7448 | -59.285 | 63.089 | -0.10399 | 0.0006986 | 0.064444 | 0.061944 | -0.0022218 | -0.00061096 | -0.00029486 | -0.024414 | 0.0027001 | 0.064593 | 0.065839 | -0.003341 | 0.0053789 | -0.0020272 | -0.045776 | 62.9654 | -59.3216 | 63.3133 | -59.1431 | -59.5322 | -59.5139 | -0.059509 | 62.9425 | -59.2758 | 63.2446 | -59.2712 | -59.3994 | -59.3765 | -0.036621 | -0.1236 | 0.2243 | 0.14191 | -0.22888 | -0.24719 | -0.19226 | -0.21057 | 0.009155 | -0.14648 | 0.15564 | 0.013733 | -0.091553 | -0.11444 | -0.10071 | -0.1236 | 0.17853 | 122.6349 | 0.004578 | 122.5204 | 122.287 | 122.2183 | 122.2504 | 122.2275 | -122.4106 | -122.3648 | 122.5983 | 122.5296 | 59.2392 | 59.2255
21.3125 | 122.644 | -59.2896 | 63.1714 | -0.042954 | 0.0019802 | 0.063589 | 0.060235 | -0.0015808 | -0.0016792 | -0.0011493 | -0.024414 | -7.6854e-05 | 0.065661 | 0.065625 | -0.0012048 | 0.0026019 | -0.0048044 | 0.041199 | 63.0569 | -59.2758 | 63.3041 | -59.0973 | -59.4727 | -59.6008 | 0.10986 | 63.002 | -59.23 | 63.2034 | -59.3124 | -59.4406 | -59.436 | 0.013733 | -0.11444 | 0.13275 | 0.19226 | -0.31128 | -0.1831 | -0.32501 | -0.19684 | 0.059509 | -0.16937 | 0.032043 | -0.022888 | -0.14648 | -0.15106 | -0.20599 | -0.21057 | 0.17853 | 122.58 | -0.082397 | 122.4335 | 122.3328 | 122.2321 | 122.3465 | 122.2916 | -122.4472 | -122.4014 | 122.5937 | 122.493 | 59.3308 | 59.3994
22.3125 | 122.7402 | -59.2575 | 63.1439 | -0.058212 | 0.0006986 | 0.062094 | 0.061303 | 0.0014098 | -0.00232 | -0.0024311 | 0.033569 | 0.00056395 | 0.067584 | 0.057294 | -0.0020594 | 0.0028155 | -0.0011728 | 0 | 63.0066 | -59.2667 | 63.3087 | -59.0927 | -59.4635 | -59.4635 | 0.032043 | 62.9654 | -59.2529 | 63.2675 | -59.2484 | -59.3582 | -59.3582 | -0.009156 | -0.13733 | 0.16479 | 0.16479 | -0.20599 | -0.20599 | -0.19684 | -0.19684 | 0.004577 | -0.17853 | 0.1236 | 0.009155 | -0.10071 | -0.10071 | -0.10529 | -0.10529 | 0.17395 | 122.5754 | 0.004578 | 122.5204 | 122.2733 | 122.2183 | 122.2641 | 122.2229 | -122.4106 | -122.3969 | 122.5662 | 122.525 | 59.2575 | 59.2895
23.3125 | 122.7585 | -59.2484 | 63.1027 | -0.11925 | 0.002194 | 0.064444 | 0.061731 | -0.00029898 | -0.0029608 | 0.0018413 | -0.01831 | 0.00035035 | 0.065875 | 0.057935 | -0.003341 | 0.0051653 | -0.0035226 | -0.009155 | 62.9517 | -59.3216 | 63.3133 | -59.1248 | -59.5093 | -59.491 | 0 | 62.9379 | -59.2758 | 63.2355 | -59.2712 | -59.3765 | -59.3674 | -0.073242 | -0.15106 | 0.21057 | 0.1236 | -0.24262 | -0.26093 | -0.16937 | -0.18768 | -0.027466 | -0.16479 | 0.13275 | -0.022888 | -0.11902 | -0.12817 | -0.091553 | -0.10071 | 0.19684 | 122.6349 | 0.004578 | 122.5113 | 122.2733 | 122.2137 | 122.2 | 122.1863 | -122.4243 | -122.3785 | 122.5616 | 122.4838 | 59.2392 | 59.2484
24.3125 | 122.7173 | -59.2987 | 63.089 | -0.073471 | 0.0017666 | 0.063376 | 0.063653 | -8.538e-05 | -0.0010382 | -0.00050846 | -0.064087 | 0.0022729 | 0.065448 | 0.065411 | -0.0020594 | 0.0040973 | 0.0039542 | -0.073242 | 62.9745 | -59.3445 | 63.2172 | -59.2163 | -59.5917 | -59.5642 | -0.11444 | 62.9791 | -59.2667 | 63.2172 | -59.3399 | -59.4223 | -59.3903 | -0.045776 | -0.11444 | 0.12817 | 0.082397 | -0.2655 | -0.29297 | -0.21973 | -0.24719 | 0.032043 | -0.10986 | 0.12817 | -0.041199 | -0.091553 | -0.1236 | -0.1236 | -0.15564 | 0.12817 | 122.5616 | -0.073242 | 122.4838 | 122.319 | 122.2458 | 122.2733 | 122.2778 | -122.4335 | -122.3557 | 122.5159 | 122.5159 | 59.2255 | 59.1843
25.3125 | 122.7036 | -59.2712 | 63.1073 | -0.08873 | 0.0019802 | 0.063376 | 0.063226 | -0.00029898 | -0.003388 | -0.0015765 | -0.076294 | 0.00077755 | 0.06737 | 0.067761 | -0.0029138 | 0.0047381 | 0.000109 | -0.082397 | 62.9837 | -59.3536 | 63.2126 | -59.2117 | -59.6008 | -59.5917 | -0.10986 | 62.9562 | -59.2804 | 63.2401 | -59.2255 | -59.5642 | -59.5322 | -0.082398 | -0.1236 | 0.10528 | 0.059509 | -0.32044 | -0.32959 | -0.23804 | -0.24719 | -0.009156 | -0.15106 | 0.13275 | 0.045776 | -0.26093 | -0.29297 | -0.25177 | -0.28381 | 0.14191 | 122.5662 | 0.054932 | 122.5204 | 122.3373 | 122.2366 | 122.2549 | 122.2275 | -122.4609 | -122.3877 | 122.4838 | 122.5113 | 59.1888 | 59.1614
26.3125 | 122.7539 | -59.2529 | 63.0844 | -0.073471 | 0.0034756 | 0.064871 | 0.064294 | -0.002008 | -0.005097 | -0.0032855 | -0.030517 | 0.0012047 | 0.065661 | 0.062634 | -0.0016322 | 0.0049517 | -0.000532 | -0.054932 | 62.9883 | -59.3262 | 63.2904 | -59.1385 | -59.5139 | -59.5139 | -0.027466 | 62.9196 | -59.2484 | 63.2446 | -59.2712 | -59.3903 | -59.3628 | -0.073242 | -0.096131 | 0.20599 | 0.11444 | -0.26093 | -0.26093 | -0.18768 | -0.18768 | 0.004578 | -0.16479 | 0.16022 | -0.01831 | -0.10986 | -0.13733 | -0.11444 | -0.14191 | 0.18768 | 122.6166 | -0.022888 | 122.493 | 122.3145 | 122.168 | 122.2412 | 122.1725 | -122.4106 | -122.3328 | 122.5433 | 122.4976 | 59.198 | 59.2255
27.3125 | 122.7173 | -59.2758 | 63.0981 | -0.042954 | 0.0026212 | 0.065725 | 0.061517 | -0.00093998 | -0.004029 | -0.0017903 | -0.024414 | 0.0039819 | 0.065875 | 0.063489 | -0.002273 | 0.0060199 | -0.0048044 | -0.068665 | 63.0066 | -59.3124 | 63.2904 | -59.1385 | -59.5505 | -59.5184 | -0.054932 | 62.9288 | -59.285 | 63.2355 | -59.2621 | -59.404 | -59.3536 | -0.036621 | -0.091553 | 0.19226 | 0.13733 | -0.24262 | -0.27466 | -0.20599 | -0.23804 | -0.009155 | -0.16937 | 0.13733 | 0.013733 | -0.07782 | -0.12817 | -0.068665 | -0.11902 | 0.17395 | 122.6028 | 0.022888 | 122.5204 | 122.319 | 122.2137 | 122.2824 | 122.2046 | -122.4106 | -122.3831 | 122.5662 | 122.5113 | 59.2072 | 59.2209
28.3125 | 122.7585 | -59.2712 | 63.1073 | -0.081101 | 0.0017666 | 0.066366 | 0.060235 | 0.00012822 | -0.0016792 | 0.0041913 | -0.015259 | 0.0027001 | 0.066089 | 0.060498 | -0.0014184 | 0.0045245 | -0.0028818 | -0.027466 | 62.9562 | -59.3124 | 63.3087 | -59.111 | -59.5001 | -59.4955 | -0.022888 | 62.9333 | -59.2758 | 63.2446 | -59.2438 | -59.3674 | -59.3582 | -0.041199 | -0.15106 | 0.20142 | 0.16022 | -0.2243 | -0.22888 | -0.18311 | -0.18768 | -0.004578 | -0.17395 | 0.13733 | 0.027466 | -0.086975 | -0.096131 | -0.082397 | -0.091553 | 0.20142 | 122.6212 | 0.032044 | 122.5204 | 122.2687 | 122.2092 | 122.2275 | 122.2046 | -122.4197 | -122.3831 | 122.58 | 122.5159 | 59.2438 | 59.2484
29.3125 | 122.7356 | -59.2804 | 63.089 | -0.13451 | 0.0030484 | 0.063376 | 0.062799 | -0.00029898 | -0.00039736 | -0.0015765 | -0.042725 | -0.00050405 | 0.066089 | 0.061993 | -0.0041956 | 0.0043109 | -0.0016 | -0.022888 | 62.9562 | -59.3216 | 63.3179 | -59.111 | -59.4955 | -59.5001 | -0.022888 | 62.9517 | -59.2758 | 63.2446 | -59.2712 | -59.3811 | -59.3628 | -0.041198 | -0.13275 | 0.22888 | 0.16937 | -0.21973 | -0.21515 | -0.17853 | -0.17395 | 0.004578 | -0.13733 | 0.15564 | 0.009156 | -0.082397 | -0.10071 | -0.086975 | -0.10529 | 0.21057 | 122.6395 | 0.004578 | 122.5204 | 122.2778 | 122.2275 | 122.2366 | 122.2321 | -122.4106 | -122.3648 | 122.5983 | 122.525 | 59.2575 | 59.2575
30.3125 | 122.7676 | -59.2667 | 63.0615 | -0.065842 | 0.0026212 | 0.066153 | 0.063012 | -0.0015808 | -0.0036018 | -0.00072206 | -0.027466 | 0.0016321 | 0.066089 | 0.057935 | -0.0029138 | 0.0045245 | -0.0001046 | -0.022888 | 62.9562 | -59.2896 | 63.2996 | -59.1339 | -59.4955 | -59.4864 | -0.018311 | 62.9288 | -59.2667 | 63.2401 | -59.2621 | -59.3948 | -59.3719 | -0.022888 | -0.10529 | 0.23804 | 0.13275 | -0.21973 | -0.22888 | -0.19684 | -0.20599 | 0 | -0.13275 | 0.17853 | 0.004578 | -0.10529 | -0.12817 | -0.10529 | -0.12817 | 0.15564 | 122.5891 | 0.004578 | 122.5067 | 122.2458 | 122.1954 | 122.2229 | 122.1954 | -122.3511 | -122.3282 | 122.5662 | 122.5067 | 59.2438 | 59.2484
31.3125 | 122.6944 | -59.285 | 63.0936 | -0.020065 | 0.0019802 | 0.065085 | 0.063012 | 0.0048278 | -0.005738 | -0.0032855 | -0.064087 | 0.00099115 | 0.065875 | 0.062207 | -0.0041956 | 0.0034563 | 0.0005362 | -0.086975 | 63.002 | -59.3536 | 63.208 | -59.2209 | -59.5917 | -59.5551 | -0.11902 | 62.97 | -59.2712 | 63.2996 | -59.4589 | -59.5779 | -59.4498 | -0.068665 | -0.091553 | 0.11444 | 0.064087 | -0.27008 | -0.3067 | -0.20142 | -0.23804 | 0.013733 | -0.1236 | 0.20599 | -0.17395 | -0.16479 | -0.29297 | -0.17853 | -0.3067 | 0.13275 | 122.5616 | -0.18768 | 122.5708 | 122.3557 | 122.2412 | 122.287 | 122.2549 | -122.4472 | -122.3648 | 122.493 | 122.5845 | 59.198 | 59.166
32.3125 | 122.7173 | -59.2575 | 63.1485 | -0.13451 | 0.0039028 | 0.062948 | 0.060876 | -0.00072638 | -0.0021064 | -0.0020039 | 0.021362 | -0.0015723 | 0.066302 | 0.065198 | -0.0014184 | 0.0036699 | -0.0026682 | -0.045776 | 62.9929 | -59.3033 | 63.2584 | -59.1431 | -59.5139 | -59.5047 | -0.059509 | 62.9562 | -59.2621 | 63.2034 | -59.2987 | -59.4177 | -59.4131 | -0.045777 | -0.15564 | 0.10986 | 0.11444 | -0.24719 | -0.25635 | -0.20142 | -0.21057 | -0.004578 | -0.19226 | 0.054931 | -0.041199 | -0.15564 | -0.16022 | -0.15106 | -0.15564 | 0.16022 | 122.5616 | -0.036621 | 122.4655 | 122.2961 | 122.2183 | 122.2504 | 122.2137 | -122.4518 | -122.4106 | 122.5159 | 122.4609 | 59.2117 | 59.198
33.3125 | 122.7402 | -59.2758 | 63.1027 | 0.10963 | 0.002194 | 0.06423 | 0.062158 | 0.004187 | -0.0027472 | -0.0026447 | -0.048828 | -0.00071785 | 0.065661 | 0.060071 | -0.0035548 | 0.0060199 | -0.0039498 | -0.14191 | 62.9837 | -59.317 | 63.2721 | -59.1705 | -59.5276 | -59.5047 | -0.045776 | 62.9333 | -59.2575 | 63.2492 | -59.2621 | -59.3903 | -59.3811 | -0.041199 | -0.11902 | 0.16937 | 0.10529 | -0.22888 | -0.25177 | -0.18768 | -0.21057 | 0.018311 | -0.16937 | 0.14648 | 0.013733 | -0.10529 | -0.11444 | -0.1236 | -0.13275 | 0.14648 | 122.5891 | -0.004578 | 122.5067 | 122.3007 | 122.1909 | 122.2595 | 122.2092 | -122.4197 | -122.3602 | 122.5479 | 122.525 | 59.1339 | 59.23
34.3125 | 122.731 | -59.2667 | 63.0707 | -0.10399 | 0.0006986 | 0.065298 | 0.064294 | 0.0029052 | -0.00018376 | -0.0015765 | -0.033569 | 0.0020593 | 0.067157 | 0.06477 | -0.0027002 | 0.0058063 | 0.0020316 | -0.073242 | 62.9608 | -59.3399 | 63.2401 | -59.1293 | -59.5779 | -59.5322 | -0.059509 | 62.9425 | -59.2621 | 63.2309 | -59.2804 | -59.4131 | -59.3857 | -0.073242 | -0.10986 | 0.16937 | 0.13733 | -0.2655 | -0.31128 | -0.19226 | -0.23804 | 0.004578 | -0.12817 | 0.16022 | -0.013733 | -0.11902 | -0.14648 | -0.1236 | -0.15106 | 0.21057 | 122.58 | -0.018311 | 122.493 | 122.3007 | 122.2046 | 122.2275 | 122.2092 | -122.4106 | -122.3328 | 122.5067 | 122.4976 | 59.1934 | 59.2072
35.3125 | 122.731 | -59.2758 | 63.0844 | -0.096359 | 0.001553 | 0.065512 | 0.061944 | 0.0018372 | -0.0016792 | 0.00034614 | -0.021362 | 0.00077755 | 0.067584 | 0.066479 | -0.0018458 | 0.0030291 | -0.003309 | -0.027466 | 62.9425 | -59.3079 | 63.3087 | -59.1019 | -59.5093 | -59.4772 | -0.022888 | 62.9425 | -59.2621 | 63.2492 | -59.2621 | -59.3811 | -59.3674 | -0.032043 | -0.14191 | 0.2243 | 0.17395 | -0.20142 | -0.23346 | -0.16937 | -0.20142 | 0.013733 | -0.14191 | 0.16479 | 0.013733 | -0.091553 | -0.10529 | -0.10529 | -0.11902 | 0.20599 | 122.6166 | 0 | 122.5113 | 122.2504 | 122.2046 | 122.2183 | 122.2183 | -122.3923 | -122.3465 | 122.5845 | 122.525 | 59.2484 | 59.2529
36.3125 | 122.7402 | -59.2712 | 63.0661 | -0.058212 | 0.0047574 | 0.06423 | 0.062799 | 0.0014098 | -0.0010382 | -0.0013629 | -0.036621 | 0.00077755 | 0.064593 | 0.059644 | -0.0016322 | 0.0040973 | -0.0013864 | -0.018311 | 62.97 | -59.3033 | 63.2996 | -59.1156 | -59.5047 | -59.4955 | -0.013733 | 62.9242 | -59.2529 | 63.2355 | -59.2621 | -59.404 | -59.3491 | -0.032044 | -0.09613 | 0.23346 | 0.15564 | -0.2243 | -0.23346 | -0.19226 | -0.20142 | 0.01831 | -0.14191 | 0.16937 | 0.009155 | -0.07782 | -0.13275 | -0.09613 | -0.15106 | 0.18768 | 122.6028 | -0.009155 | 122.4884 | 122.2733 | 122.1771 | 122.2412 | 122.1954 | -122.3694 | -122.319 | 122.5708 | 122.5067 | 59.2529 | 59.2575
37.3125 | 122.7356 | -59.285 | 63.0798 | -0.073471 | 0.0028348 | 0.065085 | 0.064294 | 0.00098262 | -0.0031744 | 0.00098694 | -0.0030517 | -7.6854e-05 | 0.064593 | 0.055585 | -0.0020594 | 0.0036699 | -0.0016 | -0.018311 | 62.9471 | -59.3262 | 63.3041 | -59.1019 | -59.5139 | -59.4818 | -0.004578 | 62.9288 | -59.2667 | 63.2401 | -59.2667 | -59.3948 | -59.3719 | -0.041199 | -0.13275 | 0.2243 | 0.1831 | -0.19684 | -0.22888 | -0.15564 | -0.18768 | 0.01831 | -0.15106 | 0.16022 | 0.01831 | -0.086975 | -0.10986 | -0.10529 | -0.12817 | 0.2243 | 122.6303 | 0 | 122.5067 | 122.2733 | 122.1954 | 122.2321 | 122.2137 | -122.406 | -122.3465 | 122.5891 | 122.525 | 59.2667 | 59.2804
38.3125 | 122.6944 | -59.2758 | 63.1439 | -0.073471 | 0.0011258 | 0.062521 | 0.062158 | 0.00034182 | -0.00061096 | 0.0022687 | -0.054932 | 0.0014185 | 0.065234 | 0.059003 | -0.0048364 | 0.0053789 | 0.0022452 | -0.073242 | 63.0157 | -59.3399 | 63.2126 | -59.2072 | -59.6146 | -59.5871 | -0.10529 | 62.9974 | -59.2712 | 63.1943 | -59.3445 | -59.523 | -59.3857 | -0.064087 | -0.12817 | 0.068664 | 0.068665 | -0.31128 | -0.33874 | -0.24719 | -0.27466 | 0.004578 | -0.14648 | 0.050354 | -0.068664 | -0.10986 | -0.24719 | -0.11444 | -0.25177 | 0.13275 | 122.5525 | -0.073242 | 122.4655 | 122.3557 | 122.2687 | 122.2916 | 122.2733 | -122.4838 | -122.4152 | 122.4884 | 122.4701 | 59.2026 | 59.1705
39.3125 | 122.7585 | -59.2712 | 63.0798 | 0.071487 | 0.0034756 | 0.065298 | 0.060235 | -0.0024354 | -0.0025336 | -8.1264e-05 | -0.07019 | 0.0022729 | 0.065875 | 0.059644 | 0.00050423 | 0.0049517 | -0.0016 | -0.13733 | 62.9929 | -59.3308 | 63.2721 | -59.1614 | -59.5139 | -59.5276 | -0.036621 | 62.9517 | -59.2667 | 63.2401 | -59.2667 | -59.3948 | -59.3674 | -0.05951 | -0.086975 | 0.19226 | 0.10986 | -0.25635 | -0.24262 | -0.19684 | -0.1831 | 0.004577 | -0.12817 | 0.16022 | 0.004577 | -0.096131 | -0.1236 | -0.10071 | -0.12817 | 0.16937 | 122.6028 | 0 | 122.5067 | 122.3236 | 122.2183 | 122.2641 | 122.2229 | -122.4106 | -122.3465 | 122.5433 | 122.5113 | 59.1339 | 59.2346
40.3125 | 122.7356 | -59.2712 | 63.0844 | -0.020065 | 0.0028348 | 0.063376 | 0.062585 | -0.0045716 | 0.00024344 | -0.0037129 | -0.073242 | -7.6854e-05 | 0.067584 | 0.069257 | -0.0020594 | 0.0053789 | -0.0007456 | -0.082397 | 62.9837 | -59.3262 | 63.1851 | -59.2941 | -59.5596 | -59.5276 | -0.050354 | 62.9379 | -59.2712 | 63.2309 | -59.2804 | -59.3948 | -59.3674 | -0.054932 | -0.10071 | 0.10071 | -0.022888 | -0.25635 | -0.28839 | -0.20142 | -0.23346 | 0 | -0.14648 | 0.14648 | -0.009156 | -0.096131 | -0.1236 | -0.096131 | -0.1236 | 0.032044 | 122.5113 | -0.009156 | 122.5021 | 122.3099 | 122.2092 | 122.2549 | 122.2092 | -122.4106 | -122.3557 | 122.4564 | 122.5021 | 59.1888 | 59.2209
41.3125 | 122.7356 | -59.285 | 63.0753 | -0.020065 | 0.001553 | 0.064444 | 0.063012 | 0.0046142 | -0.0031744 | -0.00093566 | -0.033569 | 0.0033411 | 0.066089 | 0.064557 | 0.00029043 | 0.0028155 | -0.0013864 | -0.07782 | 62.9929 | -59.3445 | 63.2263 | -59.198 | -59.5779 | -59.5551 | 0.022888 | 62.97 | -59.2667 | 63.2126 | -59.3079 | -59.436 | -59.3994 | -0.059509 | -0.082397 | 0.15106 | 0.086975 | -0.27008 | -0.29297 | -0.21057 | -0.23346 | 0.01831 | -0.10529 | 0.13733 | -0.022888 | -0.11444 | -0.15106 | -0.13275 | -0.16937 | 0.14648 | 122.5708 | -0.041198 | 122.4792 | 122.3373 | 122.2366 | 122.2778 | 122.2549 | -122.4197 | -122.3419 | 122.5113 | 122.4976 | 59.2072 | 59.3079
42.3125 | 122.7539 | -59.2804 | 63.121 | -0.11162 | 0.0028348 | 0.065725 | 0.061303 | 0.0014098 | -0.00039736 | -0.0013629 | -0.021362 | 0.0012047 | 0.065661 | 0.060071 | -0.003982 | 0.0068743 | -0.0026682 | -0.041199 | 62.97 | -59.3262 | 63.2858 | -59.1248 | -59.5047 | -59.5001 | -0.018311 | 62.9562 | -59.2667 | 63.2446 | -59.2712 | -59.3811 | -59.3536 | -0.045776 | -0.15106 | 0.1648 | 0.15564 | -0.21973 | -0.2243 | -0.17395 | -0.17853 | 0.013733 | -0.16479 | 0.1236 | 0.009156 | -0.073242 | -0.10071 | -0.086975 | -0.11444 | 0.20142 | 122.612 | -0.004577 | 122.5113 | 122.2961 | 122.2229 | 122.2504 | 122.2366 | -122.4472 | -122.3877 | 122.5662 | 122.525 | 59.2392 | 59.2621
43.3125 | 122.7448 | -59.2712 | 63.0981 | -0.020065 | 0.0009122 | 0.065298 | 0.061517 | -0.00072638 | -0.00061096 | 0.00013254 | -0.012207 | 0.00077755 | 0.065661 | 0.066693 | -0.003341 | 0.0060199 | -0.0030954 | -0.13733 | 62.9608 | -59.317 | 63.2675 | -59.1522 | -59.523 | -59.523 | -0.041199 | 62.9288 | -59.2529 | 63.2263 | -59.2667 | -59.404 | -59.3491 | -0.045777 | -0.13733 | 0.16937 | 0.11902 | -0.25177 | -0.25177 | -0.20599 | -0.20599 | 0.01831 | -0.16937 | 0.12817 | 0.004577 | -0.07782 | -0.13275 | -0.09613 | -0.15106 | 0.16479 | 122.5845 | -0.013733 | 122.4792 | 122.2778 | 122.1817 | 122.2321 | 122.2 | -122.4152 | -122.3511 | 122.5388 | 122.4976 | 59.1339 | 59.23
44.3125 | 122.7768 | -59.2667 | 63.0844 | -0.058212 | 0.0041166 | 0.065298 | 0.060449 | -0.0028626 | -0.00039736 | 0.00098694 | -0.01831 | 0.00099115 | 0.066089 | 0.058362 | -0.0020594 | 0.0030291 | -0.0022408 | -0.013733 | 62.9471 | -59.3124 | 63.2904 | -59.111 | -59.491 | -59.4818 | -0.004578 | 62.9333 | -59.2529 | 63.2538 | -59.2575 | -59.3811 | -59.3582 | -0.045776 | -0.13733 | 0.20599 | 0.15564 | -0.21515 | -0.2243 | -0.16937 | -0.17853 | 0.013733 | -0.15106 | 0.16937 | 0.009156 | -0.091552 | -0.11444 | -0.10529 | -0.12817 | 0.20142 | 122.6028 | -0.004577 | 122.5067 | 122.2595 | 122.1863 | 122.2137 | 122.2 | -122.3969 | -122.3373 | 122.5571 | 122.5204 | 59.2529 | 59.2621
45.3125 | 122.7036 | -59.3033 | 63.1073 | -0.081101 | 0.0024076 | 0.065298 | 0.064508 | 0.0011962 | -0.0010382 | -0.00072206 | -0.048828 | -0.00093145 | 0.065448 | 0.063702 | -0.003982 | 0.0034563 | 0.0005362 | -0.073242 | 62.9929 | -59.3491 | 63.2172 | -59.2072 | -59.5825 | -59.5642 | 0.013733 | 62.9929 | -59.2392 | 63.2034 | -59.3124 | -59.4131 | -59.404 | -0.045776 | -0.11444 | 0.10986 | 0.096131 | -0.26093 | -0.27924 | -0.21515 | -0.23346 | 0.064087 | -0.11444 | 0.09613 | -0.009155 | -0.10071 | -0.10986 | -0.1648 | -0.17395 | 0.14191 | 122.5662 | -0.073242 | 122.4426 | 122.3419 | 122.2321 | 122.2961 | 122.2961 | -122.4564 | -122.3465 | 122.5204 | 122.5067 | 59.23 | 59.317
46.3125 | 122.6578 | -59.2896 | 63.1073 | -0.020065 | -0.0003696 | 0.063589 | 0.063226 | 0.0046142 | -0.00018376 | -0.0020039 | -0.036621 | 0.00077755 | 0.064807 | 0.060498 | -0.0018458 | 0.0053789 | -0.0069406 | -0.086975 | 63.0066 | -59.3353 | 63.2172 | -59.2072 | -59.6008 | -59.5734 | -0.11444 | 62.9791 | -59.2758 | 63.1027 | -59.2117 | -59.3903 | -59.4498 | -0.045776 | -0.10071 | 0.10986 | 0.082398 | -0.28381 | -0.31128 | -0.23804 | -0.2655 | 0.013733 | -0.12817 | -0.004578 | 0.07782 | -0.16022 | -0.10071 | -0.17395 | -0.11444 | 0.12817 | 122.5525 | 0.064087 | 122.3785 | 122.3419 | 122.2549 | 122.2961 | 122.2687 | -122.4426 | -122.3831 | 122.5067 | 122.3923 | 59.2026 | 59.1751
47.3125 | 122.7493 | -59.2575 | 63.089 | -0.096359 | 0.002194 | 0.066794 | 0.062158 | 0.0033324 | -0.0016792 | 0.0014141 | -0.01831 | 0.00013675 | 0.06438 | 0.062634 | -0.003341 | 0.0055927 | -0.0018136 | -0.09613 | 62.97 | -59.3308 | 63.2584 | -59.1248 | -59.523 | -59.5184 | -0.041199 | 62.9425 | -59.2529 | 63.2446 | -59.2667 | -59.404 | -59.3674 | -0.073243 | -0.11902 | 0.16937 | 0.13275 | -0.26093 | -0.2655 | -0.18768 | -0.19226 | 0.004577 | -0.14648 | 0.15564 | -0.009156 | -0.10986 | -0.14649 | -0.11444 | -0.15106 | 0.20599 | 122.5891 | -0.013733 | 122.4976 | 122.3007 | 122.1954 | 122.2275 | 122.2 | -122.4197 | -122.3419 | 122.5159 | 122.5021 | 59.1614 | 59.2163
48.3125 | 122.7448 | -59.285 | 63.1027 | -0.081101 | 0.001553 | 0.063376 | 0.062799 | 0.0016236 | -0.0010382 | 0.00013254 | -0.045776 | 0.0018457 | 0.065661 | 0.062848 | -0.0031274 | 0.0032427 | 0.0022452 | -0.073242 | 63.002 | -59.3582 | 63.2126 | -59.1431 | -59.5779 | -59.5551 | -0.054932 | 62.9562 | -59.2484 | 63.2309 | -59.2621 | -59.3765 | -59.3582 | -0.073242 | -0.10071 | 0.10986 | 0.14191 | -0.27008 | -0.29297 | -0.19684 | -0.21973 | 0.036621 | -0.14648 | 0.12817 | 0.022888 | -0.073242 | -0.091553 | -0.10986 | -0.12817 | 0.21515 | 122.5708 | -0.013733 | 122.4792 | 122.3602 | 122.2046 | 122.287 | 122.2412 | -122.4609 | -122.3511 | 122.4976 | 122.5159 | 59.2117 | 59.23
49.3125 | 122.7539 | -59.2712 | 63.089 | -0.073471 | 0.0011258 | 0.06658 | 0.062372 | -0.0013672 | -0.0010382 | -0.0015765 | -0.0030517 | 0.0012047 | 0.064166 | 0.061352 | -0.0027002 | 0.0023883 | 0.0009634 | -0.009155 | 62.9425 | -59.3079 | 63.295 | -59.1202 | -59.5001 | -59.4864 | -0.013733 | 62.9196 | -59.285 | 63.2492 | -59.2529 | -59.3857 | -59.3582 | -0.036621 | -0.14648 | 0.20599 | 0.15106 | -0.21515 | -0.22888 | -0.17853 | -0.19226 | -0.013733 | -0.16937 | 0.16022 | 0.01831 | -0.086975 | -0.11444 | -0.073242 | -0.10071 | 0.18768 | 122.6028 | 0.032043 | 122.5342 | 122.2504 | 122.2046 | 122.2137 | 122.1909 | -122.3969 | -122.374 | 122.5662 | 122.5204 | 59.2621 | 59.2575
50.3125 | 122.7493 | -59.2529 | 63.1073 | -0.058212 | 0.0011258 | 0.062735 | 0.061944 | -0.0041444 | -0.003388 | -0.0013629 | -0.027466 | 0.00013675 | 0.065448 | 0.066907 | -0.0027002 | 0.0068743 | 0.000109 | -0.022888 | 62.9745 | -59.3124 | 63.2858 | -59.0973 | -59.5001 | -59.491 | -0.032043 | 62.9288 | -59.2529 | 63.2355 | -59.2529 | -59.3903 | -59.3399 | -0.059509 | -0.13275 | 0.17853 | 0.15564 | -0.23804 | -0.24719 | -0.17853 | -0.18768 | 0 | -0.17853 | 0.12817 | 0 | -0.086975 | -0.13733 | -0.086975 | -0.13733 | 0.21515 | 122.5983 | 0 | 122.4884 | 122.287 | 122.1817 | 122.2275 | 122.1817 | -122.4197 | -122.3602 | 122.5388 | 122.4884 | 59.23 | 59.2209
51.3125 | 122.7676 | -59.2621 | 63.1119 | -0.10399 | 0.0030484 | 0.064871 | 0.062372 | -0.0011536 | 2.9842e-05 | 0.0014141 | -0.01831 | 0.0012047 | 0.068652 | 0.066266 | -0.0018458 | 0.0051653 | -0.0018136 | -0.041199 | 62.9654 | -59.3216 | 63.2858 | -59.1064 | -59.5184 | -59.4955 | -0.032043 | 62.9333 | -59.2575 | 63.2538 | -59.2758 | -59.3811 | -59.3445 | -0.059509 | -0.14648 | 0.17395 | 0.15564 | -0.23346 | -0.25635 | -0.17395 | -0.19684 | 0.004578 | -0.17853 | 0.14191 | -0.013733 | -0.082397 | -0.11902 | -0.086975 | -0.1236 | 0.21515 | 122.6074 | -0.018311 | 122.5113 | 122.287 | 122.1909 | 122.2275 | 122.1954 | -122.4335 | -122.3694 | 122.5479 | 122.5159 | 59.2209 | 59.23
52.3125 | 122.7402 | -59.2667 | 63.0844 | -0.081101 | 0.003262 | 0.063589 | 0.061517 | -8.538e-05 | 0.00045724 | -0.00093566 | -0.021362 | 0.00099115 | 0.065448 | 0.054944 | -0.002273 | 0.0060199 | -0.0028818 | -0.045776 | 62.9745 | -59.3216 | 63.295 | -59.1339 | -59.5276 | -59.5139 | -0.036621 | 62.9333 | -59.2804 | 63.2263 | -59.2758 | -59.404 | -59.3628 | -0.054931 | -0.10986 | 0.21057 | 0.13275 | -0.24719 | -0.26093 | -0.19226 | -0.20599 | -0.013733 | -0.15106 | 0.14191 | -0.009155 | -0.09613 | -0.13733 | -0.082397 | -0.1236 | 0.18768 | 122.6166 | 0.004578 | 122.5067 | 122.2961 | 122.2137 | 122.2412 | 122.2 | -122.406 | -122.3648 | 122.5616 | 122.493 | 59.2209 | 59.23
53.3125 | 122.7631 | -59.2529 | 63.1119 | -0.08873 | 0.0028348 | 0.065512 | 0.063012 | 0.0029052 | -0.0027472 | 0.0061139 | -0.054932 | 0.0024865 | 0.06737 | 0.069897 | -0.0018458 | 0.0043109 | 0.001177 | -0.07782 | 63.0066 | -59.3216 | 63.2767 | -59.1431 | -59.5276 | -59.5093 | -0.036621 | 62.9471 | -59.2438 | 63.2263 | -59.2575 | -59.3903 | -59.3536 | -0.068664 | -0.10529 | 0.16479 | 0.10986 | -0.25635 | -0.27466 | -0.18768 | -0.20599 | 0.009156 | -0.16479 | 0.11444 | -0.004577 | -0.10071 | -0.13733 | -0.10986 | -0.14648 | 0.17853 | 122.5983 | -0.013733 | 122.4701 | 122.3282 | 122.1909 | 122.2595 | 122.2 | -122.4335 | -122.3557 | 122.5296 | 122.4792 | 59.1751 | 59.2163
54.3125 | 122.6624 | -59.285 | 63.1531 | -0.081101 | 0.0009122 | 0.061026 | 0.061944 | -8.538e-05 | -0.0031744 | 0.0014141 | -0.054932 | 0.00099115 | 0.067798 | 0.059644 | -0.0027002 | 0.0053789 | -0.0054452 | -0.10071 | 63.0112 | -59.3445 | 63.176 | -59.23 | -59.6146 | -59.6054 | -0.14191 | 62.9929 | -59.2987 | 63.1577 | -59.3445 | -59.4955 | -59.4543 | -0.059509 | -0.14191 | 0.022888 | 0.054931 | -0.32043 | -0.32959 | -0.26093 | -0.27008 | -0.013733 | -0.16022 | 0.004578 | -0.059509 | -0.16937 | -0.21057 | -0.15564 | -0.19684 | 0.11444 | 122.5204 | -0.045776 | 122.4564 | 122.3557 | 122.2916 | 122.2961 | 122.2778 | -122.4976 | -122.4518 | 122.4609 | 122.4426 | 59.1843 | 59.1431
55.3125 | 122.7127 | -59.2529 | 63.089 | -0.035324 | 0.0024076 | 0.064871 | 0.061731 | -0.0035034 | -0.0018928 | 0.00055974 | -0.027466 | 0.0029137 | 0.066302 | 0.063702 | -0.0014184 | 0.0068743 | 0.0007498 | -0.082397 | 62.9929 | -59.3262 | 63.3087 | -59.1476 | -59.7198 | -59.5917 | -0.082397 | 62.9562 | -59.2712 | 63.2355 | -59.2804 | -59.3903 | -59.3582 | -0.073242 | -0.09613 | 0.21973 | 0.10529 | -0.33875 | -0.46692 | -0.2655 | -0.39368 | -0.01831 | -0.13275 | 0.14649 | -0.027466 | -0.10529 | -0.13733 | -0.086975 | -0.11902 | 0.17853 | 122.6349 | -0.009156 | 122.5067 | 122.319 | 122.2275 | 122.2458 | 122.2092 | -122.4152 | -122.3602 | 122.5616 | 122.4884 | 59.1705 | 59.1705
56.3125 | 122.7539 | -59.2804 | 63.089 | -0.12688 | 0.0026212 | 0.064871 | 0.060663 | 0.00055542 | -0.0014654 | -0.0022175 | -0.097656 | 0.0027001 | 0.063525 | 0.067334 | -0.0014184 | 0.0060199 | 0.0020316 | -0.091553 | 62.9837 | -59.3399 | 63.2263 | -59.1797 | -59.3628 | -59.4589 | -0.064087 | 62.9562 | -59.2804 | 63.2217 | -59.2941 | -59.4406 | -59.3857 | -0.059509 | -0.10528 | 0.13733 | 0.10071 | -0.17853 | -0.082397 | -0.11902 | -0.022888 | 0 | -0.13275 | 0.13275 | -0.013732 | -0.10528 | -0.16022 | -0.10528 | -0.16022 | 0.16022 | 122.5662 | -0.013732 | 122.5021 | 122.3236 | 122.2366 | 122.2641 | 122.2366 | -122.4289 | -122.3694 | 122.5067 | 122.5021 | 59.1888 | 59.2163
57.3125 | 122.7081 | -59.2667 | 63.1027 | -0.11162 | 0.0030484 | 0.065512 | 0.060876 | -0.0022218 | -0.0014654 | 0.00055974 | 0.0030517 | 0.0018457 | 0.06737 | 0.063702 | -0.0027002 | 0.0045245 | -0.0003182 | -0.045776 | 62.9745 | -59.2941 | 63.1897 | -59.2117 | -59.5093 | -59.4727 | -0.054932 | 62.9333 | -59.2529 | 63.1805 | -59.2987 | -59.4131 | -59.3857 | -0.027465 | -0.12817 | 0.086975 | 0.054932 | -0.20599 | -0.24261 | -0.17853 | -0.21515 | 0.013733 | -0.16937 | 0.07782 | -0.032043 | -0.11902 | -0.14648 | -0.13275 | -0.16022 | 0.082397 | 122.4838 | -0.045776 | 122.4335 | 122.2687 | 122.1863 | 122.2412 | 122.2 | -122.3969 | -122.3557 | 122.4564 | 122.4472 | 59.2209 | 59.2117
58.3125 | 122.6486 | -59.3079 | 63.1439 | -0.042954 | 0.0006986 | 0.064871 | 0.063226 | -0.00093998 | -0.0010382 | -0.00029486 | -0.054932 | 0.0014185 | 0.064593 | 0.062421 | -0.0020594 | 0.0064471 | 0.0007498 | -0.091553 | 63.0157 | -59.3491 | 63.1668 | -59.2438 | -59.6237 | -59.5963 | -0.17395 | 62.9929 | -59.2896 | 63.1577 | -59.3719 | -59.523 | -59.4498 | -0.041199 | -0.12817 | 0.022888 | 0.064087 | -0.28839 | -0.31586 | -0.24719 | -0.27466 | 0.01831 | -0.15106 | 0.013733 | -0.064087 | -0.14191 | -0.21515 | -0.16022 | -0.23346 | 0.10529 | 122.5159 | -0.082397 | 122.4472 | 122.3648 | 122.2824 | 122.3236 | 122.3007 | -122.493 | -122.4335 | 122.4747 | 122.4655 | 59.2163 | 59.1339
59.3125 | 122.6166 | -59.3079 | 63.1165 | -0.020065 | 0.0026212 | 0.065512 | 0.060663 | -0.0028626 | -0.0021064 | -0.00029486 | -0.045776 | 0.00077755 | 0.066302 | 0.059003 | 0.00029043 | 0.0045245 | -0.0024546 | -0.091553 | 62.9883 | -59.3536 | 63.1577 | -59.2484 | -59.6237 | -59.6191 | -0.16479 | 63.002 | -59.2896 | 63.1393 | -59.3765 | -59.523 | -59.4635 | -0.045777 | -0.12817 | 0.041199 | 0.059509 | -0.31128 | -0.31586 | -0.2655 | -0.27008 | 0.01831 | -0.11444 | 0.022888 | -0.068665 | -0.15564 | -0.21515 | -0.17395 | -0.23346 | 0.10529 | 122.5113 | -0.086975 | 122.4289 | 122.3419 | 122.2916 | 122.2961 | 122.3099 | -122.4701 | -122.406 | 122.4655 | 122.4472 | 59.2163 | 59.1431
60.3125 | 122.699 | -59.285 | 63.0981 | -0.10399 | 0.0043302 | 0.063376 | 0.061944 | -0.0030762 | -0.00018376 | 0.00034614 | -0.048828 | 0.0020593 | 0.066302 | 0.063275 | -0.00099117 | 0.0077289 | -0.000532 | -0.082397 | 63.0066 | -59.3536 | 63.1989 | -59.1934 | -59.5779 | -59.5642 | -0.10986 | 62.9517 | -59.2804 | 63.1439 | -59.2804 | -59.4589 | -59.4086 | -0.068665 | -0.091553 | 0.10071 | 0.091553 | -0.27924 | -0.29297 | -0.21057 | -0.2243 | 0.004577 | -0.14649 | 0.045776 | 0.004577 | -0.1236 | -0.17395 | -0.12817 | -0.17853 | 0.16022 | 122.5525 | 0 | 122.4243 | 122.3602 | 122.2321 | 122.2916 | 122.2366 | -122.4518 | -122.3785 | 122.4838 | 122.4289 | 59.2026 | 59.1751
61.3125 | 122.6807 | -59.2941 | 63.089 | -0.042954 | -0.0003696 | 0.06423 | 0.062372 | -0.0013672 | -0.0012518 | 0.00013254 | -0.021362 | -0.00093145 | 0.066516 | 0.065198 | -0.0035548 | 0.0055927 | -0.0035226 | -0.07782 | 63.0157 | -59.3582 | 63.1943 | -59.2117 | -59.5688 | -59.5734 | -0.11902 | 62.9562 | -59.2941 | 63.1302 | -59.3582 | -59.4315 | -59.3857 | -0.064087 | -0.073242 | 0.10529 | 0.082397 | -0.27924 | -0.27466 | -0.21515 | -0.21057 | 0 | -0.13275 | 0.041199 | -0.064087 | -0.091553 | -0.13733 | -0.091553 | -0.13733 | 0.14648 | 122.5525 | -0.064087 | 122.4243 | 122.374 | 122.2504 | 122.3099 | 122.2504 | -122.4472 | -122.3831 | 122.4884 | 122.4243 | 59.2163 | 59.1751
62.3125 | 122.7219 | -59.3216 | 63.1119 | -0.020065 | 0.002194 | 0.06658 | 0.062799 | -0.0022218 | -0.0021064 | -8.1264e-05 | -0.048828 | 0.0020593 | 0.066302 | 0.062848 | -0.0035548 | 0.0030291 | -0.0052316 | -0.086975 | 62.9974 | -59.3308 | 63.2126 | -59.2163 | -59.5917 | -59.5779 | -0.11902 | 62.9562 | -59.2529 | 63.295 | -59.4543 | -59.5413 | -59.4223 | -0.009156 | -0.11444 | 0.10071 | 0.10528 | -0.25635 | -0.27008 | -0.24719 | -0.26093 | 0.068664 | -0.15564 | 0.18311 | -0.13275 | -0.10071 | -0.21973 | -0.16937 | -0.28839 | 0.11444 | 122.5433 | -0.20142 | 122.5479 | 122.3282 | 122.2092 | 122.319 | 122.2778 | -122.4426 | -122.3648 | 122.5342 | 122.6166 | 59.2346 | 59.2026
63.3125 | 122.7356 | -59.285 | 63.0981 | -0.081101 | 0.002194 | 0.064871 | 0.063012 | 0.0011962 | -0.00061096 | -0.0013629 | -0.0061035 | 0.0020593 | 0.065661 | 0.065411 | -0.0027002 | 0.0045245 | -0.0003182 | -0.027466 | 62.9791 | -59.3124 | 63.2858 | -59.1202 | -59.5047 | -59.4772 | -0.022888 | 62.9242 | -59.2712 | 63.2355 | -59.2575 | -59.3948 | -59.3399 | -0.027466 | -0.11902 | 0.18768 | 0.16479 | -0.19226 | -0.21973 | -0.1648 | -0.19226 | 0.013733 | -0.17395 | 0.13733 | 0.027466 | -0.054932 | -0.10986 | -0.068665 | -0.1236 | 0.19226 | 122.5983 | 0.013733 | 122.5067 | 122.2916 | 122.1954 | 122.2641 | 122.2092 | -122.4106 | -122.3694 | 122.5708 | 122.5204 | 59.2575 | 59.2621
64.3125 | 122.7173 | -59.2575 | 63.0844 | -0.065842 | 0.0036892 | 0.064657 | 0.059808 | -0.003717 | -0.0012518 | 0.0026959 | -0.027466 | 0.00077755 | 0.065875 | 0.065411 | -0.0035548 | 0.0058063 | -0.0018136 | -0.032043 | 62.9929 | -59.3308 | 63.2858 | -59.111 | -59.5139 | -59.4818 | -0.022888 | 62.9288 | -59.2667 | 63.2446 | -59.2529 | -59.3994 | -59.3536 | -0.073243 | -0.091553 | 0.20142 | 0.14648 | -0.22431 | -0.25635 | -0.15106 | -0.1831 | -0.009156 | -0.15564 | 0.16022 | 0.004577 | -0.096131 | -0.14191 | -0.086975 | -0.13275 | 0.21973 | 122.6166 | 0.013733 | 122.5113 | 122.3236 | 122.1954 | 122.2504 | 122.1863 | -122.4152 | -122.3511 | 122.5433 | 122.5021 | 59.2255 | 59.2346
65.3125 | 122.6486 | -59.3079 | 63.0936 | -0.050583 | 0.0030484 | 0.062308 | 0.062372 | 0.00012822 | -0.004029 | 0.00034614 | -0.061035 | 0.0031273 | 0.066943 | 0.063275 | -0.0016322 | 0.0066607 | -0.0003182 | -0.091553 | 63.0249 | -59.3445 | 63.1897 | -59.1934 | -59.6008 | -59.5779 | -0.1236 | 62.9471 | -59.2621 | 63.1851 | -59.3262 | -59.3445 | -59.3124 | -0.036621 | -0.068665 | 0.09613 | 0.11444 | -0.27008 | -0.29297 | -0.23346 | -0.25635 | 0.045776 | -0.14648 | 0.091553 | -0.018311 | -0.004578 | -0.036621 | -0.050354 | -0.082397 | 0.15106 | 122.5342 | -0.064087 | 122.4472 | 122.3694 | 122.2092 | 122.3328 | 122.2549 | -122.438 | -122.3557 | 122.4976 | 122.493 | 59.2163 | 59.1843
66.3125 | 122.7127 | -59.2529 | 63.1348 | -0.050583 | 5.76e-05 | 0.064444 | 0.063226 | -0.004358 | -0.0012518 | 0.0016277 | -0.054932 | 0.0018457 | 0.065661 | 0.059003 | -0.0018458 | 0.0053789 | 0.0005362 | -0.086975 | 63.0112 | -59.3353 | 63.1897 | -59.2072 | -59.61 | -59.5779 | -0.13275 | 62.9654 | -59.2438 | 63.1851 | -59.3308 | -59.3216 | -59.3445 | -0.082397 | -0.1236 | 0.054931 | 0.045777 | -0.32501 | -0.35706 | -0.24262 | -0.27466 | 0.009156 | -0.16937 | 0.050354 | -0.07782 | -0.091552 | -0.068664 | -0.10071 | -0.07782 | 0.12817 | 122.525 | -0.086976 | 122.4289 | 122.3465 | 122.2092 | 122.2641 | 122.2183 | -122.4701 | -122.3785 | 122.4426 | 122.4381 | 59.166 | 59.1202
67.3125 | 122.6852 | -59.2529 | 63.1027 | -0.096359 | 0.001553 | 0.063589 | 0.060876 | -0.00029898 | -0.00018376 | -0.00093566 | 0.0091553 | 0.0027001 | 0.066729 | 0.060284 | -0.0063318 | 0.0045245 | -0.0028818 | -0.045776 | 62.9837 | -59.3216 | 63.2812 | -59.0973 | -59.5093 | -59.4955 | -0.045776 | 62.9333 | -59.2484 | 63.1714 | -59.3719 | -59.3903 | -59.3491 | -0.068664 | -0.11902 | 0.17853 | 0.15564 | -0.24261 | -0.25635 | -0.17395 | -0.18768 | 0.004578 | -0.16937 | 0.068665 | -0.11902 | -0.09613 | -0.13733 | -0.10071 | -0.14191 | 0.2243 | 122.6028 | -0.1236 | 122.4197 | 122.3053 | 122.1817 | 122.2366 | 122.1863 | -122.4243 | -122.3511 | 122.5342 | 122.4243 | 59.2072 | 59.2072
68.3125 | 122.7493 | -59.2529 | 63.0753 | -0.11925 | 0.0009122 | 0.065939 | 0.062799 | 0.0020508 | -0.0010382 | -0.00093566 | -0.0061035 | 0.00013675 | 0.065875 | 0.062207 | -0.0048364 | 0.0040973 | -0.0013864 | -0.045776 | 62.9791 | -59.3262 | 63.2721 | -59.1339 | -59.5276 | -59.5184 | -0.022888 | 62.9333 | -59.23 | 63.2217 | -59.2804 | -59.3765 | -59.3353 | -0.073242 | -0.09613 | 0.19684 | 0.11902 | -0.2655 | -0.27466 | -0.19226 | -0.20142 | 0.022888 | -0.14191 | 0.14648 | -0.027466 | -0.082397 | -0.1236 | -0.10529 | -0.14648 | 0.19226 | 122.5983 | -0.050354 | 122.4518 | 122.3053 | 122.1634 | 122.2321 | 122.1863 | -122.4014 | -122.3053 | 122.525 | 122.4747 | 59.2072 | 59.23
69.3125 | 122.7356 | -59.2758 | 63.0753 | -0.14977 | 0.0019802 | 0.066153 | 0.060876 | 0.0011962 | -0.0018928 | -0.0030719 | -0.021362 | -0.00029045 | 0.064807 | 0.055585 | -0.0048364 | 0.0047381 | -0.003309 | -0.009155 | 62.9654 | -59.3079 | 63.295 | -59.0973 | -59.5001 | -59.4818 | -0.013733 | 62.9196 | -59.2758 | 63.2355 | -59.2621 | -59.3857 | -59.3536 | -0.032043 | -0.10986 | 0.21973 | 0.17853 | -0.20599 | -0.2243 | -0.17395 | -0.19226 | 0 | -0.15564 | 0.16022 | 0.013733 | -0.07782 | -0.10986 | -0.07782 | -0.10986 | 0.21057 | 122.6028 | 0.013733 | 122.5113 | 122.2733 | 122.1954 | 122.2412 | 122.1954 | -122.3831 | -122.3511 | 122.5708 | 122.5113 | 59.2667 | 59.2621
70.3125 | 122.7585 | -59.2575 | 63.1348 | -0.042954 | 0.0043302 | 0.064444 | 0.05874 | -0.00029898 | -0.00082456 | 0.00034614 | -0.012207 | 0.00056395 | 0.067157 | 0.059003 | -0.0041956 | 0.0040973 | -0.0013864 | -0.022888 | 62.9654 | -59.285 | 63.2812 | -59.0927 | -59.5047 | -59.4727 | -0.004578 | 62.9471 | -59.2575 | 63.2034 | -59.2804 | -59.4131 | -59.4086 | -0.027466 | -0.16937 | 0.14648 | 0.16479 | -0.21515 | -0.24719 | -0.18768 | -0.21973 | 0 | -0.18768 | 0.068664 | -0.022889 | -0.15106 | -0.15564 | -0.15106 | -0.15564 | 0.19226 | 122.5662 | -0.022889 | 122.4609 | 122.2504 | 122.2046 | 122.2229 | 122.2046 | -122.4197 | -122.3923 | 122.5388 | 122.4609 | 59.2346 | 59.2529
71.3125 | 122.7402 | -59.285 | 63.0981 | -0.042954 | 0.0017666 | 0.064657 | 0.060663 | 0.0022644 | -0.0021064 | -0.0013629 | -0.01831 | 0.00035035 | 0.066302 | 0.063061 | -0.0046228 | 0.0060199 | -0.0009592 | -0.022888 | 62.97 | -59.2987 | 63.295 | -59.1019 | -59.5093 | -59.4772 | -0.013733 | 62.9333 | -59.2209 | 63.2401 | -59.2621 | -59.3765 | -59.3445 | -0.013733 | -0.12817 | 0.19684 | 0.1831 | -0.19226 | -0.2243 | -0.17853 | -0.21057 | 0.064087 | -0.1648 | 0.14191 | 0.022888 | -0.059509 | -0.091553 | -0.1236 | -0.15564 | 0.19684 | 122.5937 | -0.041199 | 122.4609 | 122.2687 | 122.1542 | 122.2549 | 122.2183 | -122.3969 | -122.319 | 122.58 | 122.525 | 59.2621 | 59.2712
72.3125 | 122.7493 | -59.2758 | 63.1073 | -0.08873 | 0.0024076 | 0.065298 | 0.063226 | 0.0022644 | -0.0018928 | 0.00077334 | -0.036621 | 0.0029137 | 0.066943 | 0.066693 | -0.0046228 | 0.0060199 | -0.0037362 | -0.068665 | 62.9837 | -59.3262 | 63.176 | -59.1385 | -59.5551 | -59.5367 | -0.068665 | 62.9425 | -59.2667 | 63.2446 | -59.2667 | -59.3903 | -59.3445 | -0.050354 | -0.1236 | 0.068664 | 0.13733 | -0.26093 | -0.27924 | -0.21057 | -0.22888 | 0.009155 | -0.1648 | 0.13733 | 0.009155 | -0.068664 | -0.11444 | -0.077819 | -0.1236 | 0.18768 | 122.5021 | 0 | 122.5113 | 122.3099 | 122.2092 | 122.2595 | 122.2183 | -122.4335 | -122.374 | 122.4518 | 122.5204 | 59.2072 | 59.2072
73.3125 | 122.7173 | -59.2667 | 63.089 | -0.073471 | 0.003262 | 0.066366 | 0.063226 | 0.00076902 | -0.0014654 | -0.00072206 | -0.033569 | 0.0031273 | 0.066516 | 0.063916 | -0.0020594 | 0.0045245 | -0.005018 | -0.068665 | 62.9929 | -59.3308 | 63.3224 | -59.1202 | -59.729 | -59.6008 | -0.068665 | 62.9471 | -59.2667 | 63.2172 | -59.2758 | -59.404 | -59.3399 | -0.064087 | -0.09613 | 0.23346 | 0.14648 | -0.33417 | -0.46234 | -0.27008 | -0.39825 | 0 | -0.14191 | 0.12817 | -0.009155 | -0.073242 | -0.13733 | -0.073242 | -0.13733 | 0.21057 | 122.6532 | -0.009155 | 122.4838 | 122.3236 | 122.2137 | 122.2595 | 122.2137 | -122.4197 | -122.3557 | 122.5891 | 122.4838 | 59.198 | 59.198
74.3125 | 122.7448 | -59.2712 | 63.0798 | -0.081101 | 0.0028348 | 0.065085 | 0.061303 | -0.0015808 | -0.0027472 | 0.0012005 | 0.0061035 | 0.0014185 | 0.06502 | 0.062207 | -0.0027002 | 0.0053789 | -0.0020272 | -0.009155 | 62.97 | -59.317 | 63.2858 | -59.111 | -59.5139 | -59.4864 | -0.013733 | 62.9425 | -59.2621 | 63.2355 | -59.2575 | -59.3765 | -59.3582 | -0.045777 | -0.10986 | 0.20599 | 0.16022 | -0.21515 | -0.24262 | -0.16937 | -0.19684 | 0.009155 | -0.13733 | 0.15564 | 0.013733 | -0.086975 | -0.10529 | -0.09613 | -0.11444 | 0.20599 | 122.6028 | 0.004578 | 122.4976 | 122.287 | 122.2046 | 122.2412 | 122.2137 | -122.3969 | -122.3419 | 122.5571 | 122.5067 | 59.2621 | 59.2575
75.3125 | 122.7585 | -59.2758 | 63.0798 | -0.081101 | 0.002194 | 0.063803 | 0.060449 | -0.0017944 | -0.00061096 | 0.0016277 | -0.01831 | 0.0022729 | 0.064807 | 0.062848 | -0.0029138 | 0.0064471 | -0.0026682 | -0.027466 | 62.97 | -59.3308 | 63.2721 | -59.1019 | -59.491 | -59.4864 | -0.027466 | 62.9379 | -59.2667 | 63.2401 | -59.2484 | -59.3857 | -59.3582 | -0.054932 | -0.10986 | 0.19226 | 0.17395 | -0.21057 | -0.21515 | -0.15564 | -0.16022 | 0.009155 | -0.14191 | 0.16022 | 0.027466 | -0.082397 | -0.10986 | -0.091552 | -0.11902 | 0.22888 | 122.6028 | 0.018311 | 122.5067 | 122.3007 | 122.2046 | 122.2458 | 122.2137 | -122.4106 | -122.3465 | 122.5479 | 122.5159 | 59.2484 | 59.2484
76.3125 | 122.7127 | -59.2438 | 63.0844 | -0.11925 | 5.76e-05 | 0.064444 | 0.062585 | 0.0039734 | -0.0018928 | -8.1264e-05 | -0.012207 | 0.0020593 | 0.067798 | 0.066479 | -0.0031274 | 0.0047381 | 0.0003226 | -0.009155 | 62.9654 | -59.2941 | 63.3041 | -59.0927 | -59.5184 | -59.5001 | -0.004578 | 62.9242 | -59.2392 | 63.2355 | -59.2484 | -59.3765 | -59.3491 | -0.050354 | -0.11902 | 0.21973 | 0.15106 | -0.25635 | -0.27466 | -0.20599 | -0.22431 | 0.004577 | -0.16022 | 0.15106 | -0.004578 | -0.10529 | -0.13275 | -0.10986 | -0.13733 | 0.20142 | 122.5983 | -0.009155 | 122.4747 | 122.2595 | 122.1634 | 122.2092 | 122.168 | -122.3785 | -122.3236 | 122.5479 | 122.4792 | 59.2346 | 59.2392
77.3125 | 122.6761 | -59.2621 | 63.1027 | -0.081101 | 0.0017666 | 0.064016 | 0.058954 | -0.0030762 | -0.0016792 | 0.00013254 | -0.0061035 | -7.6854e-05 | 0.066729 | 0.056866 | -0.0016322 | 0.0047381 | -0.0003182 | -0.041199 | 62.9562 | -59.3033 | 63.2721 | -59.1019 | -59.523 | -59.4818 | 0.10986 | 62.9562 | -59.2484 | 63.1577 | -59.3308 | -59.4131 | -59.3903 | -0.041199 | -0.14648 | 0.16937 | 0.16022 | -0.21973 | -0.26093 | -0.17853 | -0.21973 | 0.013733 | -0.14648 | 0.054932 | -0.068665 | -0.12817 | -0.15106 | -0.14191 | -0.1648 | 0.20142 | 122.5754 | -0.082398 | 122.406 | 122.2595 | 122.2046 | 122.2183 | 122.2183 | -122.406 | -122.3511 | 122.5342 | 122.4197 | 59.2209 | 59.3719
78.3125 | 122.7264 | -59.2758 | 63.0707 | -0.035324 | 0.0017666 | 0.066794 | 0.061731 | 0.00076902 | -0.0029608 | 0.0012005 | -0.01831 | 0.0012047 | 0.065234 | 0.066907 | -0.0012048 | 0.0045245 | -0.0026682 | -0.027466 | 62.9654 | -59.2896 | 63.295 | -59.1019 | -59.4772 | -59.4772 | 0 | 62.9425 | -59.2621 | 63.2401 | -59.2484 | -59.3765 | -59.3491 | -0.013733 | -0.10529 | 0.2243 | 0.17395 | -0.20142 | -0.20142 | -0.18768 | -0.18768 | 0.013733 | -0.12817 | 0.16937 | 0.027466 | -0.073242 | -0.10071 | -0.086975 | -0.11444 | 0.18768 | 122.5845 | 0.013733 | 122.5021 | 122.2549 | 122.2046 | 122.2412 | 122.2183 | -122.3602 | -122.3328 | 122.5708 | 122.5159 | 59.2484 | 59.2758
79.3125 | 122.7356 | -59.2575 | 63.0798 | -0.012436 | 0.0024076 | 0.065085 | 0.06344 | 0.0011962 | -0.00061096 | 0.0031231 | -0.039673 | 0.0024865 | 0.066302 | 0.065411 | -0.0020594 | 0.0049517 | -0.000532 | -0.15106 | 62.9974 | -59.3445 | 63.2538 | -59.1248 | -59.5139 | -59.5139 | -0.036621 | 62.9379 | -59.2484 | 63.2263 | -59.2667 | -59.3903 | -59.3399 | -0.086975 | -0.082397 | 0.17395 | 0.13275 | -0.25635 | -0.25635 | -0.16937 | -0.16937 | 0.009155 | -0.14191 | 0.14648 | -0.009156 | -0.082398 | -0.13275 | -0.091553 | -0.14191 | 0.21973 | 122.5983 | -0.018311 | 122.4747 | 122.3419 | 122.1863 | 122.2549 | 122.1954 | -122.4243 | -122.3282 | 122.5113 | 122.4838 | 59.1064 | 59.2209
80.3125 | 122.699 | -59.2529 | 63.0844 | -0.081101 | 0.0028348 | 0.064016 | 0.060876 | 0.0044006 | 0.00024344 | -0.00029486 | 0.021362 | 0.00056395 | 0.066089 | 0.061566 | -0.002273 | 0.0038837 | -0.0009592 | -0.036621 | 62.9562 | -59.2941 | 63.2904 | -59.0836 | -59.5047 | -59.4818 | -0.004578 | 62.9333 | -59.2529 | 63.208 | -59.2896 | -59.3903 | -59.3765 | -0.041198 | -0.12817 | 0.20599 | 0.16937 | -0.22888 | -0.25177 | -0.18768 | -0.21057 | 0 | -0.15106 | 0.1236 | -0.036621 | -0.1236 | -0.13733 | -0.1236 | -0.13733 | 0.21057 | 122.5845 | -0.036621 | 122.4609 | 122.2504 | 122.1863 | 122.2092 | 122.1863 | -122.3785 | -122.3373 | 122.5433 | 122.4609 | 59.2163 | 59.2484
81.3125 | 122.7127 | -59.2758 | 63.0981 | -0.058212 | 0.000485 | 0.067862 | 0.062585 | -0.00072638 | -0.0012518 | -0.0020039 | -0.036621 | -0.00050405 | 0.067584 | 0.062848 | -0.0012048 | 0.0034563 | 0.0007498 | -0.032043 | 62.9471 | -59.3079 | 63.2904 | -59.0973 | -59.4955 | -59.4818 | -0.009155 | 62.9471 | -59.2392 | 63.2355 | -59.2712 | -59.3857 | -59.3674 | -0.032043 | -0.15106 | 0.19226 | 0.17853 | -0.20599 | -0.21973 | -0.17395 | -0.18768 | 0.036621 | -0.15106 | 0.13733 | 0.004578 | -0.091553 | -0.10986 | -0.12817 | -0.14648 | 0.21057 | 122.5983 | -0.032043 | 122.4747 | 122.2549 | 122.1863 | 122.2229 | 122.2229 | -122.406 | -122.3373 | 122.5662 | 122.5113 | 59.2438 | 59.2667
82.3125 | 122.7081 | -59.2712 | 63.1119 | -0.027695 | 0.0026212 | 0.064657 | 0.061517 | 0.00034182 | -0.00232 | -0.00072206 | 0.0091553 | 0.0014185 | 0.06502 | 0.052808 | -0.00099117 | 0.0040973 | -0.0030954 | -0.009155 | 63.0066 | -59.2987 | 63.2812 | -59.1156 | -59.4864 | -59.4681 | 0.013733 | 62.97 | -59.2209 | 63.2309 | -59.2392 | -59.3536 | -59.3445 | -0.027466 | -0.10529 | 0.16937 | 0.15564 | -0.19684 | -0.21515 | -0.16937 | -0.18768 | 0.050354 | -0.14191 | 0.11902 | 0.032043 | -0.073242 | -0.082398 | -0.1236 | -0.13275 | 0.18311 | 122.58 | -0.018311 | 122.4518 | 122.3053 | 122.1909 | 122.2778 | 122.2412 | -122.4106 | -122.3328 | 122.5525 | 122.5021 | 59.2621 | 59.285
83.3125 | 122.7219 | -59.2438 | 63.1119 | -0.050583 | 0.0030484 | 0.064016 | 0.061517 | 0.0018372 | -0.00232 | -0.0013629 | -0.033569 | 0.00035035 | 0.065234 | 0.068402 | -0.0044092 | 0.0047381 | -0.0022408 | -0.036621 | 62.9654 | -59.3033 | 63.3041 | -59.0973 | -59.491 | -59.4635 | 0.018311 | 62.9608 | -59.2346 | 63.2538 | -59.2438 | -59.3811 | -59.3536 | -0.05951 | -0.14648 | 0.19226 | 0.14648 | -0.21973 | -0.24719 | -0.16022 | -0.18768 | 0.009155 | -0.15106 | 0.14191 | 0 | -0.10986 | -0.13733 | -0.11902 | -0.14648 | 0.20599 | 122.6074 | -0.009155 | 122.4884 | 122.2687 | 122.1954 | 122.2092 | 122.2046 | -122.4152 | -122.3465 | 122.5479 | 122.4976 | 59.2072 | 59.2621
84.3125 | 122.7127 | -59.2667 | 63.0936 | -0.096359 | 0.001553 | 0.064444 | 0.062372 | 0.0016236 | -0.00232 | -0.0024311 | -0.0061035 | -0.00093145 | 0.065875 | 0.06178 | -0.002273 | 0.0049517 | -0.0041636 | -0.022888 | 62.9791 | -59.3079 | 63.2858 | -59.0927 | -59.523 | -59.5001 | -0.004578 | 62.9471 | -59.2575 | 63.1897 | -59.3903 | -59.4086 | -59.3399 | -0.041198 | -0.11444 | 0.19226 | 0.17395 | -0.23346 | -0.25635 | -0.19226 | -0.21515 | 0.009156 | -0.14648 | 0.09613 | -0.1236 | -0.073242 | -0.14191 | -0.082398 | -0.15106 | 0.21515 | 122.5937 | -0.13275 | 122.4472 | 122.287 | 122.2046 | 122.2458 | 122.2137 | -122.4014 | -122.3511 | 122.5525 | 122.4564 | 59.2438 | 59.2621
85.3125 | 122.7081 | -59.2529 | 63.1256 | -0.050583 | 0.000485 | 0.06423 | 0.060663 | -0.00093998 | -0.0012518 | -0.0020039 | -0.021362 | 0.00077755 | 0.068225 | 0.065625 | -0.0024866 | 0.0047381 | 0.0003226 | -0.022888 | 62.9745 | -59.2941 | 63.2812 | -59.0881 | -59.5001 | -59.4681 | -0.009155 | 62.9471 | -59.2392 | 63.2172 | -59.2987 | -59.3994 | -59.3674 | -0.041198 | -0.15106 | 0.15564 | 0.16479 | -0.21515 | -0.24719 | -0.17395 | -0.20599 | 0.013733 | -0.17853 | 0.091553 | -0.045776 | -0.11444 | -0.14648 | -0.12817 | -0.16022 | 0.20599 | 122.5754 | -0.059509 | 122.4564 | 122.2687 | 122.1863 | 122.2275 | 122.2 | -122.4197 | -122.3648 | 122.5342 | 122.4701 | 59.23 | 59.2438
86.3125 | 122.7219 | -59.2575 | 63.0936 | -0.096359 | 0.0026212 | 0.064016 | 0.063012 | -0.00051278 | -0.0012518 | -0.0028583 | -0.033569 | -0.0026405 | 0.066943 | 0.06947 | -0.002273 | 0.0055927 | -0.0013864 | -0.013733 | 62.9517 | -59.3399 | 63.2904 | -59.079 | -59.4955 | -59.4818 | -0.009155 | 62.9562 | -59.2667 | 63.2446 | -59.2438 | -59.3948 | -59.3445 | -0.082398 | -0.14191 | 0.19684 | 0.17853 | -0.22431 | -0.23804 | -0.14191 | -0.15564 | -0.009156 | -0.13733 | 0.15106 | 0.013733 | -0.086975 | -0.13733 | -0.077819 | -0.12817 | 0.26093 | 122.6303 | 0.022889 | 122.5113 | 122.2916 | 122.2229 | 122.2092 | 122.2137 | -122.4335 | -122.3602 | 122.5479 | 122.5021 | 59.2438 | 59.2484
87.3125 | 122.7585 | -59.2529 | 63.1073 | -0.13451 | 0.001553 | 0.061667 | 0.059595 | 0.00012822 | -0.0031744 | -0.0013629 | 0.0091553 | -0.00029045 | 0.065661 | 0.064343 | -0.0018458 | 0.0051653 | -0.0001046 | 0.027466 | 63.0112 | -59.2575 | 63.3087 | -59.0652 | -59.4635 | -59.4131 | 0.11902 | 62.9608 | -59.2163 | 63.2812 | -59.1797 | -59.3033 | -59.317 | -0.004577 | -0.096131 | 0.20142 | 0.18768 | -0.16022 | -0.21057 | -0.15564 | -0.20599 | 0.036621 | -0.14649 | 0.17395 | 0.073243 | -0.064087 | -0.050354 | -0.10071 | -0.086975 | 0.19226 | 122.5662 | 0.036622 | 122.4976 | 122.2687 | 122.1771 | 122.2641 | 122.2137 | -122.3648 | -122.3236 | 122.5616 | 122.5342 | 59.2804 | 59.3719
88.3125 | 122.7127 | -59.2529 | 63.0981 | -0.13451 | 0.0041166 | 0.064657 | 0.060022 | -0.0032898 | -0.0014654 | 0.00098694 | -0.042725 | 0.0016321 | 0.065234 | 0.064984 | -0.0031274 | 0.0045245 | -0.003309 | -0.022888 | 62.9517 | -59.3033 | 63.3041 | -59.0973 | -59.4955 | -59.4589 | -0.004578 | 62.9242 | -59.2529 | 63.2401 | -59.2392 | -59.3857 | -59.3582 | -0.050354 | -0.14649 | 0.20599 | 0.15564 | -0.20599 | -0.24261 | -0.15564 | -0.19226 | 0 | -0.17395 | 0.14191 | 0.013733 | -0.10529 | -0.13275 | -0.10529 | -0.13275 | 0.20599 | 122.6074 | 0.013733 | 122.493 | 122.2549 | 122.1771 | 122.2046 | 122.1771 | -122.4014 | -122.3511 | 122.5571 | 122.493 | 59.23 | 59.2484
89.3125 | 122.731 | -59.2667 | 63.1027 | -0.050583 | 0.0028348 | 0.065298 | 0.062799 | -0.0022218 | -0.0012518 | -0.0020039 | -0.036621 | 0.0020593 | 0.064593 | 0.056866 | -0.0012048 | 0.0053789 | -0.0028818 | -0.018311 | 62.9562 | -59.317 | 63.2904 | -59.1019 | -59.4955 | -59.4818 | -0.009155 | 62.97 | -59.2484 | 63.2584 | -59.2209 | -59.3765 | -59.3491 | -0.050354 | -0.14648 | 0.18768 | 0.16479 | -0.21515 | -0.22888 | -0.16479 | -0.17853 | 0.018311 | -0.13275 | 0.15564 | 0.045777 | -0.082397 | -0.10986 | -0.10071 | -0.12817 | 0.21515 | 122.6074 | 0.027466 | 122.5067 | 122.2733 | 122.2183 | 122.2229 | 122.2366 | -122.4197 | -122.3511 | 122.5571 | 122.525 | 59.2484 | 59.2575
90.3125 | 122.6669 | -59.2529 | 63.0981 | -0.050583 | 0.0045438 | 0.06423 | 0.060876 | 0.0044006 | -0.0027472 | -0.00072206 | -0.024414 | 0.0016321 | 0.06502 | 0.065198 | -0.0029138 | 0.0058063 | 0.0013906 | -0.059509 | 62.9745 | -59.2896 | 63.2492 | -59.1339 | -59.5367 | -59.5047 | -0.050354 | 62.9425 | -59.2529 | 63.208 | -59.2758 | -59.3811 | -59.3765 | -0.036621 | -0.1236 | 0.15106 | 0.11902 | -0.25177 | -0.28381 | -0.21515 | -0.24719 | 0 | -0.15564 | 0.10986 | -0.022888 | -0.1236 | -0.12817 | -0.1236 | -0.12817 | 0.15564 | 122.5388 | -0.022888 | 122.4609 | 122.2641 | 122.1954 | 122.2275 | 122.1954 | -122.3877 | -122.3511 | 122.5021 | 122.4609 | 59.1934 | 59.2026
91.3125 | 122.7402 | -59.2621 | 63.0981 | -0.081101 | 0.000485 | 0.064444 | 0.062585 | -0.0028626 | -0.00232 | -0.0024311 | -0.05188 | 0.00013675 | 0.065234 | 0.061993 | -0.002273 | 0.0051653 | -0.0030954 | -0.036621 | 62.9562 | -59.3262 | 63.2675 | -59.1019 | -59.5047 | -59.4955 | -0.027466 | 62.9471 | -59.2529 | 63.2309 | -59.2621 | -59.3857 | -59.3308 | -0.064087 | -0.14191 | 0.16937 | 0.16022 | -0.23346 | -0.24262 | -0.16937 | -0.17853 | 0.009155 | -0.15106 | 0.13275 | 0 | -0.068665 | -0.1236 | -0.07782 | -0.13275 | 0.2243 | 122.5937 | -0.009155 | 122.4838 | 122.2824 | 122.2 | 122.2183 | 122.2092 | -122.4243 | -122.3511 | 122.5296 | 122.493 | 59.2255 | 59.2346
92.3125 | 122.6944 | -59.2621 | 63.1256 | -0.065842 | 0.0026212 | 0.063162 | 0.062372 | 0.00012822 | -0.00039736 | -0.0020039 | 0.0091553 | 0.00077755 | 0.066729 | 0.061566 | -0.0027002 | 0.0026019 | -0.000532 | -0.041199 | 62.9929 | -59.2896 | 63.2538 | -59.1339 | -59.5139 | -59.4818 | -0.027466 | 62.9608 | -59.2438 | 63.2034 | -59.2712 | -59.3811 | -59.3628 | -0.027466 | -0.13275 | 0.12817 | 0.12817 | -0.21973 | -0.25177 | -0.19226 | -0.2243 | 0.018311 | -0.1648 | 0.07782 | -0.009155 | -0.10071 | -0.11902 | -0.11902 | -0.13733 | 0.15564 | 122.5433 | -0.027466 | 122.4472 | 122.2824 | 122.2046 | 122.2549 | 122.2229 | -122.4152 | -122.3694 | 122.5159 | 122.4655 | 59.2209 | 59.2346
93.3125 | 122.612 | -59.3124 | 63.1165 | -0.027695 | -0.000156 | 0.065298 | 0.063653 | -0.00051278 | -0.00039736 | 0.00034614 | -0.094604 | 0.0012047 | 0.066729 | 0.062634 | -0.0029138 | 0.0055927 | -0.0013864 | -0.09613 | 63.0066 | -59.3536 | 63.1805 | -59.2392 | -59.6191 | -59.5871 | -0.14191 | 62.9654 | -59.2758 | 63.1531 | -59.3719 | -59.4772 | -59.4131 | -0.041199 | -0.10986 | 0.064087 | 0.073242 | -0.27466 | -0.3067 | -0.23346 | -0.2655 | 0.036621 | -0.15106 | 0.036621 | -0.059509 | -0.10071 | -0.1648 | -0.13733 | -0.20142 | 0.11444 | 122.5342 | -0.09613 | 122.4289 | 122.3602 | 122.2412 | 122.319 | 122.2778 | -122.4701 | -122.3923 | 122.493 | 122.4655 | 59.2163 | 59.1705
94.3125 | 122.6944 | -59.2758 | 63.1119 | -0.042954 | 0.0006986 | 0.064871 | 0.061944 | -0.0013672 | -0.00039736 | 0.00055974 | -0.082397 | 0.00077755 | 0.06502 | 0.061993 | -0.0037684 | 0.0073015 | 0.000109 | -0.068665 | 63.0157 | -59.3308 | 63.1622 | -59.1934 | -59.5871 | -59.5871 | -0.11444 | 62.9562 | -59.2896 | 63.176 | -59.3124 | -59.4452 | -59.404 | -0.054932 | -0.09613 | 0.050354 | 0.082398 | -0.31128 | -0.31128 | -0.25635 | -0.25635 | -0.013733 | -0.15564 | 0.064087 | -0.036621 | -0.12817 | -0.16937 | -0.11444 | -0.15564 | 0.13733 | 122.493 | -0.022888 | 122.4655 | 122.3465 | 122.2458 | 122.2916 | 122.2321 | -122.4426 | -122.4014 | 122.438 | 122.4518 | 59.2072 | 59.1614
95.3125 | 122.7173 | -59.2621 | 63.089 | -0.081101 | 0.0009122 | 0.063589 | 0.063867 | 0.0011962 | -0.0031744 | -8.1264e-05 | -0.042725 | -7.6854e-05 | 0.066729 | 0.06178 | -0.0037684 | 0.0040973 | -0.0009592 | -0.064087 | 62.9883 | -59.3308 | 63.2538 | -59.1568 | -59.5184 | -59.5001 | -0.027466 | 62.9562 | -59.2667 | 63.2446 | -59.2575 | -59.3948 | -59.3399 | -0.068665 | -0.10071 | 0.1648 | 0.10529 | -0.23804 | -0.25635 | -0.16937 | -0.18768 | -0.004578 | -0.13275 | 0.15564 | 0.004578 | -0.07782 | -0.13275 | -0.073242 | -0.12817 | 0.17395 | 122.5845 | 0.009156 | 122.5113 | 122.319 | 122.2229 | 122.2504 | 122.2183 | -122.4197 | -122.3557 | 122.5159 | 122.5067 | 59.198 | 59.2346
96.3125 | 122.7127 | -59.2758 | 63.0798 | -0.042954 | -0.0007968 | 0.063803 | 0.061944 | 0.00098262 | -0.0016792 | -0.0022175 | -0.061035 | 0.0020593 | 0.066729 | 0.061993 | -0.0031274 | 0.0070879 | -0.0035226 | -0.041199 | 63.0295 | -59.3353 | 63.208 | -59.198 | -59.5825 | -59.5551 | -0.091553 | 62.9745 | -59.2804 | 63.2263 | -59.2758 | -59.4086 | -59.3628 | -0.059509 | -0.050354 | 0.12817 | 0.07782 | -0.27924 | -0.3067 | -0.21973 | -0.24719 | -0.004578 | -0.10529 | 0.14648 | 0 | -0.086975 | -0.13275 | -0.082397 | -0.12817 | 0.13733 | 122.5433 | 0.004578 | 122.5067 | 122.3648 | 122.2549 | 122.3053 | 122.2504 | -122.4152 | -122.3602 | 122.4838 | 122.5021 | 59.2346 | 59.1843
97.3125 | 122.7264 | -59.2529 | 63.1165 | -0.081101 | 0.0064664 | 0.059317 | 0.058526 | -0.0017944 | -0.0021064 | 0.00034614 | 0.048828 | 0.0022729 | 0.066729 | 0.070538 | -0.0027002 | 0.0055927 | 0.0005362 | 0.32501 | 63.0615 | -59.2529 | 63.2355 | -59.0561 | -59.4406 | -59.4452 | 0.054932 | 62.9608 | -59.2255 | 63.2538 | -59.2026 | -59.317 | -59.3124 | 0 | -0.054932 | 0.11902 | 0.19684 | -0.19226 | -0.18768 | -0.19226 | -0.18768 | 0.027466 | -0.15564 | 0.13733 | 0.050354 | -0.059509 | -0.064087 | -0.086975 | -0.091553 | 0.19684 | 122.4884 | 0.022888 | 122.4792 | 122.3145 | 122.1863 | 122.3145 | 122.2137 | -122.3694 | -122.3419 | 122.4884 | 122.5067 | 59.5779 | 59.3079
98.3125 | 122.7036 | -59.2667 | 63.0707 | -0.058212 | 0.0013394 | 0.068503 | 0.06109 | -0.00029898 | -0.0018928 | -0.0022175 | -0.039673 | 0.0016321 | 0.066089 | 0.065198 | -0.0027002 | 0.0070879 | -0.0039498 | -0.18768 | 62.9333 | -59.3536 | 63.2584 | -59.1568 | -59.5322 | -59.4955 | -0.059509 | 62.9654 | -59.2575 | 63.2355 | -59.2667 | -59.3948 | -59.3536 | -0.086975 | -0.13733 | 0.18768 | 0.10986 | -0.22888 | -0.2655 | -0.14191 | -0.17853 | 0.009156 | -0.10529 | 0.1648 | 0 | -0.086975 | -0.12817 | -0.096131 | -0.13733 | 0.19684 | 122.612 | -0.009156 | 122.493 | 122.287 | 122.2229 | 122.2 | 122.2321 | -122.4243 | -122.3282 | 122.525 | 122.5021 | 59.079 | 59.2072
99.3125 | 122.6898 | -59.2667 | 63.0981 | -0.073471 | 0.0036892 | 0.063589 | 0.063653 | 0.0016236 | -0.0010382 | 0.00013254 | -0.061035 | 0.0024865 | 0.068225 | 0.072247 | -0.00505 | 0.0055927 | 0.000109 | -0.086975 | 62.9974 | -59.3445 | 63.2034 | -59.1751 | -59.5825 | -59.5505 | -0.09613 | 62.97 | -59.2621 | 63.2355 | -59.3582 | -59.4315 | -59.3445 | -0.077819 | -0.10071 | 0.10528 | 0.091553 | -0.28381 | -0.31586 | -0.20599 | -0.23804 | 0.004578 | -0.12817 | 0.13733 | -0.091552 | -0.077819 | -0.16479 | -0.082397 | -0.16937 | 0.16937 | 122.5479 | -0.09613 | 122.4976 | 122.3419 | 122.2321 | 122.2641 | 122.2366 | -122.4426 | -122.3602 | 122.4701 | 122.5021 | 59.1797 | 59.1705
100.3125 | 122.644 | -59.2987 | 63.1027 | -0.027695 | 0.0043302 | 0.064444 | 0.061303 | -0.0011536 | -0.00018376 | -0.0022175 | -0.05188 | 0.0024865 | 0.06737 | 0.057721 | 0.00029043 | 0.0070879 | -0.000532 | -0.073242 | 63.0066 | -59.3491 | 63.1943 | -59.2117 | -59.6054 | -59.5688 | -0.1236 | 62.9425 | -59.2941 | 63.1851 | -59.317 | -59.4543 | -59.4131 | -0.050354 | -0.09613 | 0.091553 | 0.086975 | -0.27008 | -0.3067 | -0.21973 | -0.25635 | 0.004578 | -0.16022 | 0.082398 | -0.018311 | -0.11444 | -0.15564 | -0.11902 | -0.16022 | 0.13733 | 122.5433 | -0.022889 | 122.4792 | 122.3557 | 122.2366 | 122.3053 | 122.2412 | -122.4518 | -122.3969 | 122.493 | 122.4838 | 59.2255 | 59.1751
101.3125 | 122.6257 | -59.3216 | 63.1302 | -0.065842 | 0.001553 | 0.063589 | 0.063653 | 0.002478 | -0.0044562 | -0.00093566 | -0.076294 | 0.00077755 | 0.06502 | 0.06178 | -0.0035548 | 0.0060199 | -0.000532 | -0.045776 | 63.0295 | -59.3399 | 63.1485 | -59.2438 | -59.6191 | -59.6191 | -0.16022 | 62.9883 | -59.2758 | 63.1256 | -59.3948 | -59.5276 | -59.4727 | -0.018311 | -0.10071 | 0.018311 | 0.07782 | -0.29755 | -0.29755 | -0.27924 | -0.27924 | 0.045776 | -0.14191 | -0.004578 | -0.073242 | -0.15106 | -0.20599 | -0.19684 | -0.25177 | 0.096131 | 122.4884 | -0.11902 | 122.4014 | 122.3694 | 122.2641 | 122.3511 | 122.3099 | -122.4701 | -122.406 | 122.4701 | 122.4472 | 59.2758 | 59.1614
102.3281 | 122.6532 | -59.285 | 63.1577 | -0.035324 | 0.0013394 | 0.064871 | 0.062158 | 0.0022644 | -0.0018928 | 0.00077334 | -0.042725 | 0.0029137 | 0.064807 | 0.062207 | -0.0020594 | 0.0055927 | -0.0037362 | -0.009155 | 63.0249 | -59.3079 | 63.2401 | -59.1705 | -59.5001 | -59.523 | -0.013733 | 63.0066 | -59.2575 | 63.1943 | -59.2758 | -59.4131 | -59.3948 | -0.022888 | -0.13275 | 0.082397 | 0.11444 | -0.23804 | -0.21515 | -0.21515 | -0.19226 | 0.027466 | -0.15106 | 0.036621 | 0.009155 | -0.10986 | -0.12817 | -0.13733 | -0.15564 | 0.13733 | 122.5479 | -0.018311 | 122.4518 | 122.3328 | 122.2641 | 122.3099 | 122.2916 | -122.4655 | -122.4152 | 122.525 | 122.4792 | 59.2758 | 59.2712
103.3125 | 122.6944 | -59.2896 | 63.0981 | -0.11925 | 0.0017666 | 0.065298 | 0.061944 | 0.0014098 | -0.0014654 | 0.0033367 | -0.057983 | 0.00013675 | 0.064807 | 0.063061 | -0.003341 | 0.0058063 | 0.0024588 | -0.07782 | 62.9974 | -59.3262 | 63.1851 | -59.2026 | -59.5779 | -59.5642 | -0.10986 | 62.9608 | -59.2804 | 63.1943 | -59.3033 | -59.4452 | -59.3948 | -0.036621 | -0.10071 | 0.086975 | 0.086975 | -0.27466 | -0.28839 | -0.23804 | -0.25177 | 0.009155 | -0.13733 | 0.09613 | -0.013733 | -0.10528 | -0.15564 | -0.11444 | -0.16479 | 0.1236 | 122.5113 | -0.022888 | 122.4747 | 122.3236 | 122.2412 | 122.287 | 122.2504 | -122.4243 | -122.3785 | 122.4747 | 122.4838 | 59.2117 | 59.1797
104.3125 | 122.6624 | -59.2804 | 63.121 | -0.058212 | 0.001553 | 0.063162 | 0.061517 | 0.00076902 | -0.0010382 | 0.00013254 | -0.05188 | 0.0020593 | 0.068438 | 0.066907 | -0.0024866 | 0.0062335 | -0.0007456 | -0.086975 | 63.0157 | -59.3399 | 63.1531 | -59.2163 | -59.6008 | -59.5825 | -0.13275 | 62.9745 | -59.2712 | 63.1577 | -59.3262 | -59.4772 | -59.4131 | -0.059509 | -0.10529 | 0.032043 | 0.064087 | -0.30212 | -0.32043 | -0.24262 | -0.26093 | 0.009156 | -0.14648 | 0.036621 | -0.045776 | -0.13275 | -0.19684 | -0.14191 | -0.20599 | 0.1236 | 122.493 | -0.054932 | 122.4289 | 122.3557 | 122.2458 | 122.2961 | 122.2549 | -122.4609 | -122.3923 | 122.4335 | 122.4381 | 59.1934 | 59.1476
105.3125 | 122.5845 | -59.285 | 63.1256 | -0.050583 | 0.0034756 | 0.064657 | 0.062799 | 0.008673 | -0.0018928 | -0.0047809 | -0.012207 | 0.0020593 | 0.068011 | 0.057935 | -0.003982 | 0.0066607 | -0.0007456 | -0.091553 | 63.0341 | -59.3674 | 63.3087 | -58.9325 | -59.5734 | -59.6329 | -0.17395 | 63.0112 | -59.2896 | 63.1256 | -59.404 | -59.5413 | -59.4681 | -0.082398 | -0.091552 | 0.18311 | 0.35248 | -0.3479 | -0.28839 | -0.2655 | -0.20599 | -0.004578 | -0.11444 | 0 | -0.11902 | -0.18311 | -0.25635 | -0.17853 | -0.25177 | 0.43488 | 122.6761 | -0.11444 | 122.4152 | 122.4014 | 122.3007 | 122.319 | 122.2961 | -122.493 | -122.4152 | 122.5937 | 122.4106 | 59.1934 | 59.111
106.3125 | 122.5571 | -59.2804 | 63.1531 | -0.042954 | 0.0011258 | 0.065725 | 0.060663 | -8.538e-05 | -0.00061096 | 0.00098694 | -0.057983 | 0.0014185 | 0.067584 | 0.058362 | -0.0035548 | 0.0066607 | 0.000109 | -0.082397 | 63.0112 | -59.3628 | 63.1439 | -59.2758 | -59.6237 | -59.6237 | -0.18768 | 62.9883 | -59.3079 | 63.0753 | -59.3765 | -59.4772 | -59.4269 | -0.082397 | -0.14191 | -0.009155 | 0.004578 | -0.34332 | -0.34332 | -0.26092 | -0.26092 | -0.027465 | -0.16479 | -0.07782 | -0.09613 | -0.14648 | -0.19684 | -0.11902 | -0.16937 | 0.086975 | 122.5067 | -0.068665 | 122.3831 | 122.374 | 122.2961 | 122.2916 | 122.2687 | -122.5159 | -122.4609 | 122.4243 | 122.3557 | 59.198 | 59.0927
107.3125 | 122.6807 | -59.2529 | 63.0981 | -0.065842 | 0.0030484 | 0.064871 | 0.059808 | 0.0061096 | -0.00082456 | 0.00013254 | 0.033569 | -7.6854e-05 | 0.068438 | 0.05708 | -0.0018458 | 0.0062335 | 0.001177 | -0.045776 | 62.9883 | -59.2804 | 63.2172 | -59.1385 | -59.4452 | -59.2667 | -0.11902 | 62.9471 | -59.285 | 63.1485 | -59.2941 | -59.4269 | -59.404 | -0.027466 | -0.10986 | 0.11902 | 0.11444 | -0.013733 | -0.19226 | 0.013733 | -0.16479 | -0.032043 | -0.15106 | 0.050354 | -0.041198 | -0.15106 | -0.17395 | -0.11902 | -0.14191 | 0.14191 | 122.4976 | -0.009155 | 122.4335 | 122.2687 | 122.2321 | 122.2412 | 122.2 | -122.3785 | -122.3831 | 122.4701 | 122.4014 | 59.2072 | 59.1339
108.3125 | 122.644 | -59.2712 | 63.1622 | -0.027695 | 0.0019802 | 0.062948 | 0.06109 | 0.0018372 | -0.0014654 | -0.0034991 | -0.036621 | 0.0024865 | 0.066943 | 0.061139 | -0.0041956 | 0.0064471 | -0.0060862 | -0.004578 | 62.9974 | -59.3308 | 63.2309 | -59.1614 | -59.5459 | -59.5551 | -0.041199 | 63.0066 | -59.2484 | 63.1531 | -59.3308 | -59.4681 | -59.4086 | -0.05951 | -0.16479 | 0.068665 | 0.10986 | -0.28381 | -0.27466 | -0.2243 | -0.21515 | 0.022888 | -0.15564 | -0.009155 | -0.05951 | -0.13733 | -0.19684 | -0.16022 | -0.21973 | 0.16937 | 122.5616 | -0.082398 | 122.4014 | 122.3282 | 122.2549 | 122.2687 | 122.2778 | -122.493 | -122.4106 | 122.5021 | 122.4243 | 59.2667 | 59.23
109.3125 | 122.5845 | -59.3079 | 63.1622 | -0.08873 | 0.000485 | 0.064444 | 0.06344 | 0.00098262 | -0.0025336 | -0.00072206 | -0.07019 | 0.00077755 | 0.066516 | 0.070752 | -0.0018458 | 0.0064471 | 0.0003226 | -0.041199 | 63.0203 | -59.3216 | 63.1989 | -59.2117 | -59.5963 | -59.5734 | -0.11902 | 63.0066 | -59.2758 | 63.121 | -59.3719 | -59.523 | -59.4543 | -0.013733 | -0.14191 | 0.036622 | 0.09613 | -0.2655 | -0.28839 | -0.25177 | -0.27466 | 0.032043 | -0.15564 | -0.041198 | -0.064087 | -0.14648 | -0.21515 | -0.17853 | -0.24719 | 0.10986 | 122.5204 | -0.09613 | 122.3969 | 122.3419 | 122.2824 | 122.3282 | 122.3145 | -122.4838 | -122.438 | 122.5067 | 122.4289 | 59.2667 | 59.1888
110.3125 | 122.6074 | -59.3079 | 63.1119 | -0.050583 | 0.002194 | 0.063376 | 0.059595 | -0.00029898 | -0.0016792 | -0.0024311 | -0.030517 | 0.0020593 | 0.066943 | 0.060712 | -0.0031274 | 0.0053789 | -0.005018 | -0.09613 | 63.0066 | -59.3445 | 63.1622 | -59.2346 | -59.6283 | -59.6008 | -0.15106 | 62.9837 | -59.2896 | 63.1302 | -59.3628 | -59.4955 | -59.4406 | -0.036621 | -0.10529 | 0.050354 | 0.073242 | -0.29297 | -0.32043 | -0.25635 | -0.28381 | 0.01831 | -0.12817 | 0.018311 | -0.054932 | -0.13275 | -0.18768 | -0.15106 | -0.20599 | 0.10986 | 122.5067 | -0.073242 | 122.4197 | 122.3511 | 122.2733 | 122.3145 | 122.2916 | -122.4564 | -122.4014 | 122.4701 | 122.438 | 59.2117 | 59.1568
111.3125 | 122.6898 | -59.3033 | 63.1805 | -0.042954 | 0.002194 | 0.065298 | 0.062372 | 0.002478 | -0.00232 | 0.0014141 | -0.079346 | 0.0020593 | 0.067798 | 0.066266 | -0.0024866 | 0.0060199 | 0.0033134 | -0.064087 | 63.0432 | -59.3399 | 63.1531 | -59.2392 | -59.6146 | -59.6008 | -0.1831 | 63.002 | -59.2804 | 63.1714 | -59.7107 | -59.8297 | -59.4955 | -0.036621 | -0.13733 | -0.027466 | 0.064087 | -0.29755 | -0.31128 | -0.26093 | -0.27466 | 0.022888 | -0.17853 | -0.009155 | -0.40741 | -0.19226 | -0.52643 | -0.21515 | -0.54932 | 0.10071 | 122.493 | -0.4303 | 122.4518 | 122.3831 | 122.2824 | 122.3465 | 122.3053 | -122.5204 | -122.4609 | 122.4564 | 122.4747 | 59.2392 | 59.1202
112.3125 | 122.7173 | -59.198 | 63.1348 | -0.065842 | 0.0034756 | 0.065085 | 0.059381 | -0.0011536 | -0.003388 | -0.0037129 | 0.061035 | 0.00035035 | 0.066089 | 0.052167 | -0.0027002 | 0.0026019 | -0.0030954 | 0.059509 | 63.0249 | -59.2621 | 63.446 | -59.3445 | -59.729 | -59.4269 | 0.07782 | 62.9517 | -59.23 | 63.2492 | -59.198 | -59.2621 | -59.2758 | -0.064087 | -0.10986 | 0.31128 | -0.14648 | -0.22888 | -0.53101 | -0.16479 | -0.46692 | -0.032044 | -0.18311 | 0.11444 | 0 | -0.07782 | -0.064087 | -0.045776 | -0.032043 | -0.082397 | 122.7081 | 0.032044 | 122.4792 | 122.287 | 122.1817 | 122.2229 | 122.1497 | -122.3969 | -122.3648 | 122.644 | 122.4472 | 59.2575 | 59.2758
113.3125 | 122.6074 | -59.3079 | 63.1577 | -0.042954 | 0.002194 | 0.063376 | 0.06344 | -8.538e-05 | -0.003388 | 0.0022687 | -0.039673 | 0.0014185 | 0.065875 | 0.066907 | -0.003341 | 0.0045245 | -0.0056588 | -0.045776 | 63.0203 | -59.3445 | 63.176 | -59.2209 | -59.6054 | -59.5917 | -0.14191 | 63.0112 | -59.2896 | 63.1119 | -59.3948 | -59.5367 | -59.4727 | -0.036621 | -0.13733 | 0.01831 | 0.086975 | -0.28381 | -0.29755 | -0.24719 | -0.26093 | 0.01831 | -0.14648 | -0.045777 | -0.086975 | -0.16479 | -0.22888 | -0.1831 | -0.24719 | 0.1236 | 122.5204 | -0.10528 | 122.4014 | 122.3648 | 122.3007 | 122.3282 | 122.319 | -122.5021 | -122.4472 | 122.4838 | 122.4197 | 59.2621 | 59.166
114.3125 | 122.6074 | -59.2712 | 63.1485 | -0.035324 | 0.0002714 | 0.066153 | 0.062799 | -0.002008 | -0.00082456 | 0.0026959 | -0.036621 | 0.0018457 | 0.066729 | 0.063275 | -0.00013677 | 0.0047381 | -0.0020272 | 0.009155 | 63.0066 | -59.3079 | 63.2263 | -59.1522 | -59.5551 | -59.5413 | -0.032043 | 63.002 | -59.2712 | 63.1622 | -59.3262 | -59.4727 | -59.4269 | -0.036621 | -0.14191 | 0.077819 | 0.11902 | -0.27008 | -0.28381 | -0.23346 | -0.24719 | 0 | -0.14648 | 0.013732 | -0.054932 | -0.15564 | -0.20142 | -0.15564 | -0.20142 | 0.15564 | 122.5342 | -0.054932 | 122.4335 | 122.3145 | 122.2733 | 122.2778 | 122.2733 | -122.4564 | -122.4197 | 122.4976 | 122.4335 | 59.2804 | 59.2392
115.3125 | 122.644 | -59.2758 | 63.1531 | -0.012436 | 0.0034756 | 0.064871 | 0.063012 | -0.0017944 | -0.0016792 | -8.1264e-05 | -0.030517 | 0.0022729 | 0.066302 | 0.062207 | -0.002273 | 0.0040973 | -0.0018136 | -0.004578 | 63.0157 | -59.3124 | 63.2263 | -59.1476 | -59.5184 | -59.5276 | -0.022888 | 62.9883 | -59.2575 | 63.1577 | -59.3079 | -59.4589 | -59.4223 | -0.036621 | -0.13733 | 0.073242 | 0.12817 | -0.25177 | -0.24262 | -0.21515 | -0.20599 | 0.018311 | -0.16479 | 0.004578 | -0.032043 | -0.14648 | -0.1831 | -0.1648 | -0.20142 | 0.16479 | 122.5388 | -0.050354 | 122.4152 | 122.3282 | 122.2458 | 122.2916 | 122.2641 | -122.4655 | -122.4106 | 122.5021 | 122.4335 | 59.2712 | 59.2529
116.3125 | 122.5662 | -59.2667 | 63.1531 | -0.012436 | 5.76e-05 | 0.063803 | 0.062158 | -0.002008 | -0.0027472 | 0.0020551 | -0.021362 | 0.00056395 | 0.067584 | 0.05943 | -0.00077757 | 0.0062335 | -0.0001046 | -0.022888 | 63.0524 | -59.3216 | 63.1851 | -59.1843 | -59.5688 | -59.5551 | -0.07782 | 62.9929 | -59.2667 | 63.1348 | -59.3445 | -59.5184 | -59.436 | -0.054931 | -0.10071 | 0.032044 | 0.082398 | -0.28839 | -0.30212 | -0.23346 | -0.24719 | 0 | -0.16022 | -0.01831 | -0.077819 | -0.16937 | -0.25177 | -0.16937 | -0.25177 | 0.13733 | 122.5067 | -0.077819 | 122.4014 | 122.374 | 122.2595 | 122.319 | 122.2595 | -122.4747 | -122.4197 | 122.4518 | 122.4014 | 59.2438 | 59.1888
117.3125 | 122.6074 | -59.2941 | 63.1302 | -0.012436 | 0.0045438 | 0.063589 | 0.062585 | -0.00029898 | -0.0021064 | -0.00029486 | -0.048828 | 0.0022729 | 0.068652 | 0.067761 | -0.0029138 | 0.0049517 | -0.0016 | -0.013733 | 63.0249 | -59.3079 | 63.1989 | -59.1705 | -59.5596 | -59.5505 | -0.059509 | 62.9974 | -59.2438 | 63.1348 | -59.3399 | -59.4818 | -59.4406 | -0.013733 | -0.10529 | 0.068665 | 0.1236 | -0.25635 | -0.2655 | -0.24262 | -0.25177 | 0.050354 | -0.13275 | 0.004578 | -0.045777 | -0.14648 | -0.18768 | -0.19684 | -0.23804 | 0.13733 | 122.5067 | -0.096131 | 122.3785 | 122.3328 | 122.2412 | 122.319 | 122.2916 | -122.438 | -122.374 | 122.493 | 122.4289 | 59.2804 | 59.2346
118.3125 | 122.5571 | -59.2438 | 63.1531 | -0.0048066 | 0.0013394 | 0.062735 | 0.063226 | -0.00072638 | -0.0018928 | 0.0024823 | -0.021362 | 0.00077755 | 0.065448 | 0.059644 | -0.003341 | 0.0077289 | 0.0013906 | -0.054932 | 63.0432 | -59.3353 | 63.1668 | -59.2575 | -59.6054 | -59.5871 | -0.16022 | 62.9974 | -59.2712 | 62.8464 | -59.0286 | -59.2438 | -59.3994 | -0.091553 | -0.10986 | 0.013733 | -0.013733 | -0.34332 | -0.36163 | -0.25177 | -0.27008 | -0.027466 | -0.15564 | -0.3067 | 0.21515 | -0.15564 | 0 | -0.12817 | 0.027466 | 0.07782 | 122.5021 | 0.24262 | 122.1176 | 122.3785 | 122.2687 | 122.287 | 122.2412 | -122.4884 | -122.4243 | 122.4106 | 122.0901 | 59.1888 | 59.0836
119.3125 | 122.3969 | -59.3445 | 63.0386 | -0.020065 | 0.0013394 | 0.064016 | 0.061944 | -0.0015808 | -0.0012518 | 0.00098694 | -0.021362 | 0.0014185 | 0.068011 | 0.060712 | -0.002273 | 0.0077289 | 0.001177 | -0.054932 | 62.9974 | -59.3353 | 63.1668 | -59.2209 | -59.5825 | -59.5779 | -0.15564 | 63.0066 | -59.2529 | 63.0936 | -59.3765 | -59.5505 | -59.3445 | 0.009155 | -0.041198 | 0.12817 | 0.1236 | -0.23346 | -0.23804 | -0.24262 | -0.24719 | 0.091552 | -0.032043 | 0.054932 | -0.032044 | 0 | -0.20599 | -0.091552 | -0.29755 | 0.11444 | 122.5021 | -0.1236 | 122.3465 | 122.3328 | 122.2595 | 122.3419 | 122.3511 | -122.374 | -122.2916 | 122.5113 | 122.438 | 59.2895 | 59.1888
120.3125 | 122.5983 | -59.285 | 63.1531 | -0.058212 | 0.0006986 | 0.06658 | 0.062372 | 0.0020508 | -0.0016792 | -0.00029486 | -0.033569 | 0.0018457 | 0.066302 | 0.064343 | -0.0020594 | 0.0051653 | 0.0016044 | -0.041199 | 63.002 | -59.3124 | 63.1851 | -59.2163 | -59.5825 | -59.5779 | -0.13733 | 62.9974 | -59.2712 | 63.0981 | -59.3903 | -59.5367 | -59.4498 | -0.027466 | -0.15106 | 0.032044 | 0.068664 | -0.29297 | -0.29755 | -0.2655 | -0.27008 | 0.013733 | -0.15564 | -0.054931 | -0.10529 | -0.16479 | -0.25177 | -0.17853 | -0.2655 | 0.09613 | 122.4976 | -0.11902 | 122.3694 | 122.3145 | 122.2687 | 122.287 | 122.2824 | -122.4655 | -122.4243 | 122.4701 | 122.3831 | 59.2438 | 59.1476
121.3125 | 122.6395 | -59.2758 | 63.1485 | -0.042954 | 0.0011258 | 0.064444 | 0.060876 | -0.0017944 | -0.0010382 | -8.1264e-05 | -0.024414 | 0.0018457 | 0.064807 | 0.065839 | -0.003341 | 0.0060199 | -0.0007456 | 0.004578 | 62.9929 | -59.3124 | 63.2263 | -59.1522 | -59.5322 | -59.5184 | -0.009155 | 63.0112 | -59.2575 | 63.1668 | -59.317 | -59.436 | -59.4086 | -0.036621 | -0.15564 | 0.077819 | 0.1236 | -0.24262 | -0.25635 | -0.20599 | -0.21973 | 0.018311 | -0.13733 | 0.01831 | -0.041199 | -0.13275 | -0.16022 | -0.15106 | -0.17853 | 0.16022 | 122.5388 | -0.05951 | 122.4243 | 122.3053 | 122.2687 | 122.2687 | 122.287 | -122.4609 | -122.406 | 122.5021 | 122.4426 | 59.2804 | 59.2667
122.3125 | 122.6212 | -59.2712 | 63.1302 | -0.012436 | 0.0019802 | 0.065085 | 0.062372 | -0.0022218 | -0.0053108 | -0.00093566 | -0.01831 | 0.00099115 | 0.06737 | 0.057294 | -0.0029138 | 0.0058063 | -0.0020272 | -0.013733 | 63.0203 | -59.2987 | 63.1897 | -59.1843 | -59.5779 | -59.5688 | -0.068665 | 62.9929 | -59.2804 | 63.1393 | -59.3628 | -59.4955 | -59.4406 | -0.027466 | -0.10986 | 0.059509 | 0.086975 | -0.29755 | -0.3067 | -0.27008 | -0.27924 | -0.009156 | -0.13733 | 0.009155 | -0.091553 | -0.16937 | -0.2243 | -0.16022 | -0.21515 | 0.11444 | 122.4884 | -0.082397 | 122.4197 | 122.319 | 122.2733 | 122.2916 | 122.2641 | -122.4289 | -122.4106 | 122.4609 | 122.4106 | 59.2575 | 59.2026
123.3125 | 122.58 | -59.2758 | 63.1531 | -0.081101 | 0.0017666 | 0.065298 | 0.061944 | 0.00098262 | -0.0048834 | 0.00098694 | -0.05188 | 0.0027001 | 0.068011 | 0.062421 | -0.0014184 | 0.0070879 | -0.005018 | 0 | 63.0066 | -59.3353 | 63.1989 | -59.1797 | -59.5551 | -59.5551 | -0.068665 | 62.9745 | -59.2529 | 63.1165 | -59.3536 | -59.4818 | -59.436 | -0.059509 | -0.14648 | 0.045777 | 0.096131 | -0.27924 | -0.27924 | -0.21973 | -0.21973 | 0.022888 | -0.17853 | -0.036621 | -0.07782 | -0.16022 | -0.20599 | -0.1831 | -0.22888 | 0.15564 | 122.5342 | -0.10071 | 122.3694 | 122.3419 | 122.2275 | 122.2824 | 122.2504 | -122.4884 | -122.406 | 122.4747 | 122.3923 | 59.2758 | 59.2072
124.3125 | 122.6166 | -59.2712 | 63.1348 | -0.027695 | -0.000156 | 0.065725 | 0.062158 | -0.00029898 | -0.0010382 | 0.00034614 | -8.6e-08 | 0.0029137 | 0.067798 | 0.06477 | -0.0014184 | 0.0062335 | -0.0026682 | -0.018311 | 63.0249 | -59.2987 | 63.2126 | -59.1705 | -59.5551 | -59.5413 | -0.064087 | 63.0066 | -59.2621 | 63.1531 | -59.3536 | -59.4543 | -59.4131 | -0.027466 | -0.10986 | 0.077819 | 0.10071 | -0.27008 | -0.28381 | -0.24262 | -0.25635 | 0.009155 | -0.12817 | 0.01831 | -0.082398 | -0.14191 | -0.18311 | -0.15106 | -0.19226 | 0.12817 | 122.5113 | -0.091553 | 122.4152 | 122.3236 | 122.2687 | 122.2961 | 122.2778 | -122.4335 | -122.3969 | 122.4838 | 122.4243 | 59.2529 | 59.2072
125.3125 | 122.5891 | -59.2804 | 63.1622 | -0.058212 | 0.0011258 | 0.063803 | 0.060663 | 0.0031188 | 0.00024344 | -0.00029486 | -0.024414 | 0.0033411 | 0.068866 | 0.065839 | -0.0029138 | 0.0055927 | 0.0003226 | -0.045776 | 63.002 | -59.3399 | 63.1714 | -59.198 | -59.6054 | -59.5734 | -0.13275 | 63.002 | -59.2529 | 63.1165 | -59.3811 | -59.5276 | -59.4635 | -0.059509 | -0.16022 | 0.009156 | 0.082398 | -0.29297 | -0.32501 | -0.23346 | -0.2655 | 0.027466 | -0.16022 | -0.045776 | -0.10071 | -0.1831 | -0.24719 | -0.21057 | -0.27466 | 0.14191 | 122.5113 | -0.12817 | 122.3694 | 122.3419 | 122.2549 | 122.2824 | 122.2824 | -122.5021 | -122.4152 | 122.4518 | 122.3969 | 59.2346 | 59.1476
126.3125 | 122.5937 | -59.2804 | 63.1531 | -0.081101 | 0.0006986 | 0.063803 | 0.059595 | 0.0011962 | -0.0014654 | 0.0016277 | -0.015259 | 0.00056395 | 0.067584 | 0.064343 | -0.003341 | 0.0073015 | -0.0022408 | -0.041199 | 63.0066 | -59.3262 | 63.1622 | -59.1934 | -59.5734 | -59.5596 | -0.10529 | 63.002 | -59.2758 | 63.1165 | -59.3765 | -59.5139 | -59.4452 | -0.045776 | -0.14648 | 0.009155 | 0.086976 | -0.27923 | -0.29297 | -0.23346 | -0.24719 | 0.004578 | -0.15106 | -0.036621 | -0.09613 | -0.16479 | -0.23346 | -0.16937 | -0.23804 | 0.13275 | 122.4884 | -0.10071 | 122.3923 | 122.3328 | 122.2778 | 122.287 | 122.2824 | -122.4792 | -122.4289 | 122.4426 | 122.3969 | 59.2392 | 59.1751
127.3125 | 122.5937 | -59.285 | 63.1577 | -0.10399 | 0.001553 | 0.064871 | 0.063226 | -0.0011536 | -0.0025336 | 0.00055974 | -0.012207 | 0.0033411 | 0.067157 | 0.068616 | -0.0027002 | 0.0049517 | -0.0028818 | -0.036621 | 63.0295 | -59.3308 | 63.1851 | -59.1888 | -59.5734 | -59.5459 | -0.082397 | 62.97 | -59.2621 | 63.1073 | -59.3582 | -59.491 | -59.4406 | -0.045777 | -0.12817 | 0.027466 | 0.09613 | -0.26093 | -0.28839 | -0.21515 | -0.24261 | 0.022888 | -0.18768 | -0.050354 | -0.073242 | -0.15564 | -0.20599 | -0.17853 | -0.22888 | 0.14191 | 122.5159 | -0.09613 | 122.3694 | 122.3602 | 122.2321 | 122.3145 | 122.2549 | -122.4884 | -122.4197 | 122.4701 | 122.3923 | 59.2484 | 59.2026
128.3125 | 122.6532 | -59.2529 | 63.1531 | -0.035324 | 0.0034756 | 0.065085 | 0.06109 | -0.00093998 | -0.00039736 | 0.00013254 | -0.024414 | 0.0018457 | 0.066516 | 0.06178 | -0.0012048 | 0.0085833 | 0.0007498 | 0.032043 | 63.0386 | -59.2804 | 63.2172 | -59.1202 | -59.5093 | -59.4955 | 0.004578 | 63.0341 | -59.2346 | 63.1668 | -59.3033 | -59.4498 | -59.3948 | -0.027466 | -0.11444 | 0.064087 | 0.13275 | -0.24261 | -0.25635 | -0.21515 | -0.22888 | 0.018311 | -0.11902 | 0.013733 | -0.050354 | -0.14191 | -0.19684 | -0.16022 | -0.21515 | 0.16022 | 122.4976 | -0.068665 | 122.4014 | 122.319 | 122.2687 | 122.2916 | 122.287 | -122.4335 | -122.3877 | 122.4701 | 122.4197 | 59.285 | 59.2575
129.3125 | 122.6212 | -59.2758 | 63.1439 | -0.13451 | 0.000485 | 0.064444 | 0.060876 | 0.00012822 | -0.0027472 | 0.00055974 | -0.0030517 | 0.0016321 | 0.067157 | 0.055371 | -0.0024866 | 0.0058063 | -0.0013864 | 0.14191 | 63.0524 | -59.3124 | 63.2492 | -59.1019 | -59.4955 | -59.5047 | 0.018311 | 62.9791 | -59.2392 | 63.1897 | -59.2896 | -59.4269 | -59.3857 | -0.036621 | -0.091553 | 0.10529 | 0.17395 | -0.22888 | -0.21973 | -0.19226 | -0.18311 | 0.036621 | -0.16479 | 0.045776 | -0.013733 | -0.10986 | -0.15106 | -0.14648 | -0.18768 | 0.21057 | 122.5616 | -0.050354 | 122.4289 | 122.3648 | 122.2183 | 122.3282 | 122.2549 | -122.4564 | -122.3831 | 122.525 | 122.4655 | 59.4177 | 59.2941
130.3125 | 122.644 | -59.2804 | 63.0981 | -0.0048066 | 0.003262 | 0.064016 | 0.06344 | -0.0011536 | 0.00045724 | -0.0015765 | -0.012207 | 0.0037683 | 0.066516 | 0.060712 | -0.0046228 | 0.0058063 | 0.0013906 | -0.086975 | 63.0112 | -59.3308 | 63.1485 | -59.2392 | -59.6146 | -59.5779 | -0.13733 | 62.9654 | -59.2758 | 63.1531 | -59.3491 | -59.4772 | -59.4223 | -0.050354 | -0.086976 | 0.050354 | 0.041199 | -0.29755 | -0.33417 | -0.24719 | -0.28381 | 0.004578 | -0.13275 | 0.054931 | -0.068664 | -0.14191 | -0.19684 | -0.14648 | -0.20142 | 0.091553 | 122.4792 | -0.073242 | 122.4289 | 122.3419 | 122.2412 | 122.2916 | 122.2458 | -122.4289 | -122.374 | 122.4289 | 122.4335 | 59.1934 | 59.1431
131.3125 | 122.6074 | -59.2987 | 63.1485 | -0.073471 | 5.76e-05 | 0.063803 | 0.066858 | -0.0022218 | -0.00232 | -0.00072206 | 0.0091553 | 0.00013675 | 0.064166 | 0.060925 | -0.0027002 | 0.0070879 | -0.0030954 | -0.082397 | 63.0249 | -59.3491 | 63.3591 | -59.2941 | -59.6649 | -59.5413 | -0.15564 | 63.0295 | -59.2667 | 63.1073 | -59.4177 | -59.523 | -59.4452 | -0.050354 | -0.1236 | 0.21057 | 0.004578 | -0.24262 | -0.36621 | -0.19226 | -0.31586 | 0.032043 | -0.11902 | -0.041199 | -0.11902 | -0.14648 | -0.2243 | -0.17853 | -0.25635 | 0.054932 | 122.7081 | -0.15106 | 122.374 | 122.374 | 122.2961 | 122.3236 | 122.3282 | -122.4976 | -122.4152 | 122.6578 | 122.406 | 59.2163 | 59.1431
132.3125 | 122.6074 | -59.3033 | 63.1027 | -0.058212 | 0.0053982 | 0.063803 | 0.062158 | -0.007776 | -0.00082456 | 0.00077334 | 0.033569 | 0.0012047 | 0.067157 | 0.06712 | -0.0029138 | 0.0053789 | -0.0048044 | -0.073242 | 63.0066 | -59.3491 | 63.1393 | -59.2758 | -59.7656 | -59.9945 | 0.09613 | 62.9929 | -59.2346 | 63.0981 | -59.3811 | -59.5001 | -59.4543 | -0.045776 | -0.09613 | 0.036621 | 0.027466 | -0.69122 | -0.46234 | -0.64545 | -0.41656 | 0.068665 | -0.10986 | -0.004577 | -0.07782 | -0.15106 | -0.19684 | -0.21973 | -0.2655 | 0.073242 | 122.4884 | -0.14648 | 122.3328 | 122.3557 | 122.2275 | 122.3099 | 122.2961 | -122.4518 | -122.3373 | 122.4426 | 122.4014 | 59.23 | 59.3994
133.3125 | 122.5662 | -59.2804 | 63.1302 | -0.020065 | 0.001553 | 0.065512 | 0.061731 | 0.00098262 | -0.00232 | -0.0026447 | -0.021362 | 0.00035035 | 0.065234 | 0.066693 | -0.0029138 | 0.0060199 | 0.001177 | -0.018311 | 63.0478 | -59.2941 | 63.2034 | -59.166 | -59.5459 | -59.5551 | -0.064087 | 62.9837 | -59.2667 | 63.1256 | -59.3445 | -59.4772 | -59.4086 | -0.013732 | -0.082397 | 0.073242 | 0.11444 | -0.27466 | -0.2655 | -0.26093 | -0.25177 | 0.013733 | -0.14648 | -0.004578 | -0.064086 | -0.12817 | -0.19684 | -0.14191 | -0.21057 | 0.12817 | 122.4976 | -0.077819 | 122.3923 | 122.3419 | 122.2504 | 122.3282 | 122.2641 | -122.4243 | -122.3969 | 122.4838 | 122.406 | 59.2621 | 59.2163
134.3125 | 122.6074 | -59.2758 | 63.1577 | -0.027695 | 0.0036892 | 0.064016 | 0.063226 | 0.0020508 | -0.0031744 | -0.0011493 | -0.012207 | 0.0027001 | 0.067798 | 0.05708 | -0.00013677 | 0.0066607 | -0.0024546 | -0.013733 | 63.0249 | -59.3308 | 63.2126 | -59.1614 | -59.5505 | -59.5459 | -0.050354 | 63.0112 | -59.2484 | 63.121 | -59.3353 | -59.4727 | -59.4223 | -0.054932 | -0.13275 | 0.054931 | 0.11444 | -0.27008 | -0.27466 | -0.21515 | -0.21973 | 0.027466 | -0.14648 | -0.036621 | -0.059509 | -0.14648 | -0.19684 | -0.17395 | -0.2243 | 0.16937 | 122.5433 | -0.086975 | 122.3694 | 122.3557 | 122.2595 | 122.3007 | 122.287 | -122.4884 | -122.406 | 122.4884 | 122.3969 | 59.2621 | 59.2255
135.3125 | 122.6028 | -59.2896 | 63.1393 | 0.19356 | 0.0036892 | 0.064657 | 0.060876 | 0.0014098 | -0.0029608 | -0.00050846 | -0.015259 | 0.0029137 | 0.065875 | 0.064984 | -0.00013677 | 0.0049517 | -0.0001046 | -0.10529 | 63.0341 | -59.3308 | 63.1531 | -59.2575 | -59.6191 | -59.5779 | -0.17853 | 62.9929 | -59.2667 | 63.1119 | -59.3948 | -59.5184 | -59.4498 | -0.041199 | -0.10528 | 0.013733 | 0.032044 | -0.28839 | -0.32959 | -0.24719 | -0.28839 | 0.022888 | -0.14648 | -0.027466 | -0.10528 | -0.16022 | -0.22888 | -0.1831 | -0.25177 | 0.073243 | 122.4838 | -0.12817 | 122.3785 | 122.3648 | 122.2595 | 122.3236 | 122.2824 | -122.4701 | -122.406 | 122.4426 | 122.4014 | 59.1843 | 59.111
136.3125 | 122.6349 | -59.2712 | 63.1348 | -0.020065 | 0.0028348 | 0.063803 | 0.062372 | 0.00055542 | -0.0018928 | 0.00077334 | -0.024414 | -0.00029045 | 0.064807 | 0.061993 | -0.003341 | 0.0055927 | 0.000109 | -0.004578 | 63.0249 | -59.3033 | 63.2217 | -59.1431 | -59.5367 | -59.5322 | -0.009155 | 62.97 | -59.2575 | 63.1531 | -59.3216 | -59.4681 | -59.404 | -0.032044 | -0.10986 | 0.086975 | 0.12817 | -0.26093 | -0.2655 | -0.22888 | -0.23346 | 0.013733 | -0.16479 | 0.01831 | -0.050354 | -0.13275 | -0.19684 | -0.14649 | -0.21057 | 0.16022 | 122.525 | -0.064087 | 122.4106 | 122.3282 | 122.2275 | 122.2961 | 122.2412 | -122.4381 | -122.3923 | 122.493 | 122.4243 | 59.2667 | 59.2621
137.3125 | 122.7264 | -59.2484 | 63.089 | -0.36339 | 0.0041166 | 0.065939 | 0.060235 | 0.0022644 | -0.0025336 | -0.0020039 | 0.042725 | 0.0014185 | 0.066729 | 0.059644 | -0.003982 | 0.0034563 | -0.000532 | 0.041199 | 62.9471 | -59.2758 | 63.2629 | -59.0973 | -59.4589 | -59.4589 | -0.004578 | 62.9059 | -59.2667 | 63.2217 | -59.2621 | -59.3811 | -59.3445 | -0.027466 | -0.14191 | 0.17395 | 0.15106 | -0.21057 | -0.21057 | -0.1831 | -0.1831 | -0.018311 | -0.1831 | 0.13275 | -0.013733 | -0.09613 | -0.13275 | -0.077819 | -0.11444 | 0.17853 | 122.5388 | 0.004578 | 122.4884 | 122.2229 | 122.1725 | 122.1954 | 122.1542 | -122.3648 | -122.3557 | 122.5113 | 122.4701 | 59.2896 | 59.2438
138.3125 | 122.6257 | -59.2667 | 63.1485 | -0.10399 | 0.0017666 | 0.065085 | 0.060449 | 0.002478 | 0.00024344 | 0.00098694 | -0.01831 | 0.0016321 | 0.067157 | 0.070111 | -0.0044092 | 0.0053789 | -0.000532 | 0.013733 | 63.0203 | -59.3262 | 63.2172 | -59.1339 | -59.5322 | -59.5184 | 0.009155 | 63.0112 | -59.2529 | 63.1531 | -59.3216 | -59.4452 | -59.3857 | -0.059509 | -0.12817 | 0.068664 | 0.13275 | -0.25177 | -0.2655 | -0.19226 | -0.20599 | 0.013733 | -0.13733 | 0.004577 | -0.054931 | -0.11902 | -0.17853 | -0.13275 | -0.19226 | 0.19226 | 122.5433 | -0.068664 | 122.406 | 122.3465 | 122.2641 | 122.287 | 122.2778 | -122.4747 | -122.4014 | 122.4838 | 122.4197 | 59.2804 | 59.2758
139.3125 | 122.5891 | -59.2896 | 63.176 | -0.042954 | 0.0013394 | 0.064016 | 0.063226 | 0.00076902 | -0.0025336 | 0.00098694 | -0.0061035 | 0.00056395 | 0.073565 | 0.061566 | -0.0027002 | 0.0077289 | -0.0016 | -0.068665 | 63.0203 | -59.3308 | 63.1439 | -59.2529 | -59.6329 | -59.5963 | -0.26093 | 62.9471 | -59.3674 | 63.0615 | -59.2987 | -59.5551 | -59.4681 | -0.041199 | -0.15564 | -0.032043 | 0.036621 | -0.3067 | -0.34332 | -0.2655 | -0.30212 | -0.07782 | -0.22888 | -0.11444 | -0.009155 | -0.17853 | -0.2655 | -0.10071 | -0.18768 | 0.07782 | 122.4747 | 0.068665 | 122.4289 | 122.3511 | 122.3145 | 122.3099 | 122.2366 | -122.5067 | -122.5433 | 122.4335 | 122.3511 | 59.2209 | 59.0286
140.3125 | 122.6944 | -59.2392 | 63.1027 | -0.11925 | 0.0013394 | 0.064657 | 0.060449 | -0.00051278 | -0.00061096 | 0.0012005 | 0.061035 | 0.00013675 | 0.066943 | 0.057721 | -0.0018458 | 0.0023883 | -0.0001046 | -0.032043 | 62.9974 | -59.2987 | 63.2309 | -59.1202 | -59.5322 | -59.4727 | -0.027466 | 62.9517 | -59.2392 | 63.1943 | -59.2941 | -59.4131 | -59.3536 | -0.059509 | -0.10529 | 0.12817 | 0.11902 | -0.23346 | -0.29297 | -0.17395 | -0.23346 | 0 | -0.15106 | 0.091553 | -0.054931 | -0.11444 | -0.17395 | -0.11444 | -0.17395 | 0.17853 | 122.5296 | -0.054931 | 122.4335 | 122.2961 | 122.1909 | 122.2366 | 122.1909 | -122.4014 | -122.3419 | 122.4701 | 122.4335 | 59.2072 | 59.2117
141.3125 | 122.438 | -59.3445 | 63.0615 | -0.027695 | 0.002194 | 0.063162 | 0.061303 | 0.0031188 | -0.00061096 | -0.0011493 | -0.042725 | -0.00029045 | 0.066943 | 0.062421 | -0.0035548 | 0.0053789 | -0.0041636 | -0.054932 | 63.0066 | -59.3536 | 63.1622 | -59.2255 | -59.6054 | -59.5871 | -0.15106 | 63.0157 | -59.2575 | 63.089 | -59.3948 | -59.4086 | -59.5688 | -0.009156 | -0.054931 | 0.10071 | 0.11902 | -0.24262 | -0.26093 | -0.23346 | -0.25177 | 0.086975 | -0.045776 | 0.027466 | -0.050354 | -0.22431 | -0.064087 | -0.31128 | -0.15106 | 0.12817 | 122.5159 | -0.13733 | 122.3465 | 122.3602 | 122.2733 | 122.3511 | 122.3602 | -122.4152 | -122.319 | 122.5067 | 122.4335 | 59.2895 | 59.1934
142.3125 | 122.644 | -59.2941 | 63.121 | -0.042954 | 0.0024076 | 0.063162 | 0.061731 | 0.0022644 | -0.00061096 | -0.0015765 | -0.021362 | 0.0020593 | 0.068225 | 0.060284 | -0.002273 | 0.0051653 | 0.0009634 | -0.07782 | 63.0157 | -59.3536 | 63.1622 | -59.2163 | -59.6146 | -59.5779 | -0.12817 | 62.9883 | -59.285 | 63.1348 | -59.3399 | -59.4635 | -59.4131 | -0.05951 | -0.10529 | 0.041198 | 0.077819 | -0.28381 | -0.32043 | -0.2243 | -0.26093 | 0.009155 | -0.13275 | 0.013733 | -0.045777 | -0.11902 | -0.16937 | -0.12817 | -0.17853 | 0.13733 | 122.5159 | -0.054932 | 122.4197 | 122.3694 | 122.2733 | 122.3099 | 122.2824 | -122.4747 | -122.406 | 122.4564 | 122.4289 | 59.2163 | 59.166
143.3125 | 122.644 | -59.2758 | 63.1393 | 0.010452 | 0.0041166 | 0.063589 | 0.060663 | 0.00076902 | -0.00082456 | 0.00034614 | -0.030517 | 0.0012047 | 0.066729 | 0.067334 | -0.003341 | 0.0064471 | -0.0035226 | 0.004578 | 63.0295 | -59.3124 | 63.208 | -59.1522 | -59.5413 | -59.523 | -0.004578 | 62.9974 | -59.2621 | 63.1714 | -59.3124 | -59.4498 | -59.3994 | -0.036621 | -0.10986 | 0.068665 | 0.1236 | -0.24719 | -0.2655 | -0.21057 | -0.22888 | 0.013733 | -0.14191 | 0.032044 | -0.036621 | -0.1236 | -0.17395 | -0.13733 | -0.18768 | 0.16022 | 122.5204 | -0.050354 | 122.4335 | 122.3419 | 122.2595 | 122.3053 | 122.2733 | -122.4518 | -122.4014 | 122.4838 | 122.4472 | 59.2804 | 59.2712
144.3125 | 122.5937 | -59.2529 | 63.1165 | -0.08873 | 0.0013394 | 0.064871 | 0.062372 | 0.0014098 | -0.0010382 | 0.0029095 | -0.045776 | 0.00035035 | 0.065875 | 0.060071 | -0.0018458 | 0.0060199 | -0.005018 | -0.013733 | 63.0157 | -59.3353 | 63.1943 | -59.166 | -59.5688 | -59.5459 | -0.082397 | 62.9883 | -59.2575 | 63.121 | -59.3536 | -59.4955 | -59.4452 | -0.082397 | -0.10071 | 0.07782 | 0.086975 | -0.29297 | -0.31586 | -0.21057 | -0.23346 | -0.004577 | -0.12817 | 0.004578 | -0.10071 | -0.19226 | -0.24261 | -0.18768 | -0.23804 | 0.16937 | 122.5296 | -0.096131 | 122.3785 | 122.3511 | 122.2458 | 122.2687 | 122.2412 | -122.4518 | -122.374 | 122.4472 | 122.374 | 59.2392 | 59.1705
145.3125 | 122.8867 | -59.1522 | 63.1622 | -0.042954 | -0.0003696 | 0.063376 | 0.060022 | -0.0011536 | 2.9842e-05 | -0.0013629 | 0.064087 | 0.00056395 | 0.066943 | 0.054089 | -0.0031274 | 0.0049517 | -0.0003182 | 0.027466 | 62.9929 | -59.2896 | 63.295 | -59.0469 | -59.4269 | -59.4223 | 0.10529 | 62.9654 | -59.2255 | 63.2401 | -59.1934 | -59.2804 | -58.9554 | -0.13733 | -0.16937 | 0.13275 | 0.10529 | -0.27008 | -0.27466 | -0.13275 | -0.13733 | -0.073242 | -0.19684 | 0.07782 | -0.041198 | 0.19684 | -0.12817 | 0.27008 | -0.054932 | 0.24262 | 122.5845 | 0.032044 | 122.4655 | 122.2824 | 122.1909 | 122.1451 | 122.1176 | -122.4518 | -122.3877 | 122.4472 | 122.3923 | 59.1797 | 59.2575
146.3125 | 122.5891 | -59.2667 | 63.1439 | -0.08873 | 0.0011258 | 0.065085 | 0.061731 | -0.00051278 | -0.0025336 | 0.00077334 | -0.027466 | 0.0029137 | 0.065234 | 0.062848 | -0.003982 | 0.0073015 | -0.0003182 | -0.013733 | 63.0203 | -59.3308 | 63.208 | -59.1568 | -59.5413 | -59.5322 | -0.045776 | 63.0066 | -59.2529 | 63.1485 | -59.3491 | -59.4864 | -59.4177 | -0.064087 | -0.1236 | 0.064087 | 0.10986 | -0.2655 | -0.27466 | -0.20142 | -0.21057 | 0.013733 | -0.13733 | 0.004578 | -0.082397 | -0.15106 | -0.21973 | -0.16479 | -0.23346 | 0.17395 | 122.5388 | -0.09613 | 122.4014 | 122.3511 | 122.2595 | 122.287 | 122.2733 | -122.4747 | -122.3969 | 122.4747 | 122.4152 | 59.2529 | 59.2209
147.3125 | 122.731 | -59.2392 | 63.1073 | -0.096359 | 0.0030484 | 0.065939 | 0.058313 | 0.0014098 | -0.00039736 | -8.1264e-05 | 0.015259 | 0.00099115 | 0.065875 | 0.062848 | -0.0031274 | 0.0079425 | -0.0022408 | -0.032043 | 62.97 | -59.285 | 63.2812 | -59.079 | -59.4818 | -59.4498 | 0.004578 | 62.9196 | -59.2392 | 63.208 | -59.2484 | -59.3719 | -59.3216 | -0.045776 | -0.13733 | 0.17395 | 0.16022 | -0.21057 | -0.24262 | -0.16479 | -0.19684 | 0 | -0.18768 | 0.10071 | -0.009155 | -0.082397 | -0.13275 | -0.082397 | -0.13275 | 0.20599 | 122.5662 | -0.009155 | 122.4472 | 122.2549 | 122.1588 | 122.2092 | 122.1588 | -122.3923 | -122.3465 | 122.5204 | 122.4472 | 59.2072 | 59.2438
148.3125 | 122.6074 | -59.285 | 63.1485 | -0.081101 | 0.0011258 | 0.062735 | 0.063867 | -0.0015808 | -0.004029 | -0.00050846 | -0.036621 | 0.0035547 | 0.066516 | 0.06178 | -0.0031274 | 0.0073015 | 0.0039542 | 0.018311 | 63.0386 | -59.3124 | 63.2217 | -59.1431 | -59.523 | -59.5322 | -0.013733 | 62.9883 | -59.2621 | 63.1668 | -59.3124 | -59.4543 | -59.3903 | -0.027466 | -0.10986 | 0.073242 | 0.14191 | -0.24719 | -0.23804 | -0.21973 | -0.21057 | 0.022888 | -0.16022 | 0.01831 | -0.027466 | -0.10529 | -0.16937 | -0.12817 | -0.19226 | 0.16937 | 122.5342 | -0.050354 | 122.4289 | 122.3511 | 122.2504 | 122.3236 | 122.2733 | -122.4609 | -122.4106 | 122.5067 | 122.4518 | 59.3033 | 59.2712
149.3125 | 122.6028 | -59.2621 | 63.1485 | -0.042954 | 0.0019802 | 0.065298 | 0.062158 | 0.0033324 | -0.00018376 | -0.0011493 | -0.045776 | 0.00056395 | 0.066943 | 0.063916 | -0.0020594 | 0.0058063 | -0.0016 | 0.013733 | 63.0157 | -59.2987 | 63.2309 | -59.1385 | -59.523 | -59.5184 | 0.004578 | 63.0112 | -59.2529 | 63.176 | -59.3124 | -59.4452 | -59.3948 | -0.036621 | -0.13275 | 0.082397 | 0.1236 | -0.25635 | -0.26093 | -0.21973 | -0.2243 | 0.009155 | -0.13733 | 0.027465 | -0.050354 | -0.13275 | -0.1831 | -0.14191 | -0.19226 | 0.16022 | 122.5296 | -0.059509 | 122.4289 | 122.3145 | 122.2641 | 122.2778 | 122.2733 | -122.4472 | -122.4014 | 122.493 | 122.438 | 59.2758 | 59.2667
150.3281 | 122.6395 | -59.2621 | 63.1531 | -0.050583 | 0.0009122 | 0.063376 | 0.060235 | -0.00072638 | -0.00232 | 0.0014141 | -0.0061035 | 0.00056395 | 0.066729 | 0.06413 | -0.0024866 | 0.0055927 | -0.0022408 | 0.004578 | 63.0707 | -59.3124 | 63.1989 | -59.1934 | -59.5184 | -59.523 | -0.032043 | 63.0386 | -59.23 | 63.1622 | -59.285 | -59.4177 | -59.3765 | -0.050354 | -0.082397 | 0.045777 | 0.068665 | -0.26093 | -0.25635 | -0.21057 | -0.20599 | 0.032043 | -0.11444 | 0.009155 | -0.022888 | -0.11444 | -0.15564 | -0.14648 | -0.18768 | 0.11902 | 122.5113 | -0.054931 | 122.3923 | 122.3831 | 122.2687 | 122.3328 | 122.3007 | -122.4655 | -122.3831 | 122.4609 | 122.4243 | 59.2667 | 59.23
151.3125 | 122.6395 | -59.2529 | 63.1439 | 0.0028229 | 0.002194 | 0.064016 | 0.062585 | 0.0020508 | 0.00088444 | 0.0016277 | -0.042725 | 0.0024865 | 0.066516 | 0.063916 | -0.0024866 | 0.0077289 | 0.0026724 | 0.054932 | 63.0478 | -59.3124 | 63.2492 | -59.111 | -59.491 | -59.491 | 0.022888 | 62.9791 | -59.2392 | 63.1668 | -59.2896 | -59.436 | -59.3765 | -0.059509 | -0.09613 | 0.10529 | 0.14191 | -0.23804 | -0.23804 | -0.17853 | -0.17853 | 0.013733 | -0.16479 | 0.022888 | -0.036621 | -0.1236 | -0.1831 | -0.13733 | -0.19684 | 0.20142 | 122.5616 | -0.050354 | 122.406 | 122.3602 | 122.2183 | 122.3007 | 122.2321 | -122.4564 | -122.3831 | 122.5021 | 122.4197 | 59.3079 | 59.2758
152.3125 | 122.7768 | -59.2484 | 63.0936 | -0.10399 | 0.002194 | 0.063162 | 0.060663 | 0.00012822 | -0.00018376 | -0.0020039 | 0.0061035 | -0.0013587 | 0.068438 | 0.059003 | -0.0035548 | 0.0034563 | -0.0018136 | -0.064087 | 62.9745 | -59.3124 | 63.2401 | -59.1064 | -59.5093 | -59.5001 | -0.018311 | 62.9425 | -59.2667 | 63.3408 | -59.4589 | -59.5001 | -59.2758 | -0.064087 | -0.11902 | 0.14648 | 0.14191 | -0.25177 | -0.26093 | -0.18768 | -0.19684 | -0.018311 | -0.15106 | 0.24719 | -0.21057 | -0.027466 | -0.25177 | -0.009155 | -0.23346 | 0.20599 | 122.5525 | -0.19226 | 122.6074 | 122.287 | 122.2092 | 122.2229 | 122.1909 | -122.406 | -122.3602 | 122.4884 | 122.5891 | 59.1843 | 59.23
153.3125 | 122.6395 | -59.2667 | 63.1668 | -0.065842 | 0.002194 | 0.062094 | 0.063226 | -0.00072638 | -0.0038154 | 0.00013254 | -0.024414 | 0.0037683 | 0.066089 | 0.068829 | -0.0037684 | 0.0055927 | -0.0013864 | 0.013733 | 63.0066 | -59.3033 | 63.208 | -59.1476 | -59.5184 | -59.5139 | -0.013733 | 62.9883 | -59.2392 | 63.1485 | -59.3124 | -59.4543 | -59.3903 | -0.036621 | -0.16022 | 0.041199 | 0.11902 | -0.24719 | -0.25177 | -0.21057 | -0.21515 | 0.027466 | -0.17853 | -0.01831 | -0.045776 | -0.1236 | -0.18768 | -0.15106 | -0.21515 | 0.15564 | 122.5113 | -0.073242 | 122.3877 | 122.3099 | 122.2275 | 122.2733 | 122.2549 | -122.4701 | -122.406 | 122.4747 | 122.4152 | 59.2804 | 59.2529
154.3125 | 122.6028 | -59.2804 | 63.1622 | -0.027695 | 0.0011258 | 0.06423 | 0.061944 | 0.0018372 | -0.0014654 | -0.0013629 | -0.039673 | 0.0029137 | 0.06502 | 0.06413 | -0.0031274 | 0.0060199 | 0.0007498 | -0.027466 | 63.0249 | -59.3491 | 63.1897 | -59.1751 | -59.5688 | -59.5596 | -0.086975 | 62.9837 | -59.285 | 63.121 | -59.3582 | -59.4818 | -59.4406 | -0.068664 | -0.13733 | 0.027466 | 0.10529 | -0.27923 | -0.28839 | -0.21057 | -0.21973 | -0.004577 | -0.17853 | -0.041198 | -0.077819 | -0.16022 | -0.20142 | -0.15564 | -0.19684 | 0.17395 | 122.5388 | -0.073242 | 122.406 | 122.374 | 122.2687 | 122.3053 | 122.2641 | -122.5113 | -122.4472 | 122.4701 | 122.4014 | 59.2529 | 59.1934
155.3281 | 122.58 | -59.2804 | 63.1485 | -0.065842 | 0.0026212 | 0.063162 | 0.062585 | 0.0031188 | -0.0012518 | -0.0015765 | -0.0030517 | 0.0035547 | 0.068011 | 0.058362 | -0.0031274 | 0.0062335 | -0.0022408 | -0.091553 | 63.0341 | -59.3536 | 63.3362 | -58.9279 | -59.6008 | -59.6237 | -0.1831 | 63.0203 | -59.2667 | 63.1073 | -59.3903 | -59.5459 | -59.4543 | -0.073242 | -0.11444 | 0.18768 | 0.35248 | -0.34332 | -0.32043 | -0.27008 | -0.24719 | 0.013733 | -0.12817 | -0.041199 | -0.10986 | -0.17395 | -0.2655 | -0.18768 | -0.27923 | 0.42572 | 122.6898 | -0.1236 | 122.374 | 122.3877 | 122.287 | 122.3145 | 122.3007 | -122.5021 | -122.4152 | 122.6166 | 122.3877 | 59.1888 | 59.0973
156.3125 | 122.644 | -59.2529 | 63.1348 | -0.096359 | 0.001553 | 0.063803 | 0.060876 | -0.0011536 | -0.0021064 | -0.0013629 | -0.021362 | 0.0014185 | 0.069079 | 0.063489 | -0.0031274 | 0.0075153 | -0.0024546 | 0.09613 | 63.0432 | -59.2987 | 63.2446 | -59.111 | -59.5001 | -59.5001 | 0.009155 | 63.0066 | -59.2529 | 63.1851 | -59.285 | -59.4177 | -59.3811 | -0.045776 | -0.091553 | 0.10986 | 0.14191 | -0.24719 | -0.24719 | -0.20142 | -0.20142 | 0 | -0.12817 | 0.050354 | -0.032043 | -0.12817 | -0.16479 | -0.12817 | -0.16479 | 0.18768 | 122.5433 | -0.032043 | 122.4381 | 122.3419 | 122.2595 | 122.2961 | 122.2595 | -122.4335 | -122.3877 | 122.4976 | 122.4381 | 59.3491 | 59.2621
157.3125 | 122.5983 | -59.3033 | 63.1302 | -0.050583 | 0.0017666 | 0.062521 | 0.060235 | -0.00029898 | -0.0010382 | -0.00029486 | -0.030517 | 0.0027001 | 0.064166 | 0.064343 | -0.0029138 | 0.0060199 | -0.0030954 | -0.045776 | 63.0341 | -59.3124 | 63.1714 | -59.2163 | -59.5871 | -59.5917 | -0.14191 | 62.9837 | -59.2621 | 63.0936 | -59.3994 | -59.5139 | -59.436 | -0.009155 | -0.09613 | 0.041199 | 0.086975 | -0.28839 | -0.28381 | -0.27924 | -0.27466 | 0.041199 | -0.14648 | -0.036621 | -0.09613 | -0.13275 | -0.21057 | -0.17395 | -0.25177 | 0.09613 | 122.4838 | -0.13733 | 122.3557 | 122.3465 | 122.2458 | 122.3373 | 122.287 | -122.4426 | -122.3923 | 122.4747 | 122.3969 | 59.2575 | 59.1614
158.3125 | 122.5845 | -59.2941 | 63.1256 | 0.010452 | 0.001553 | 0.06423 | 0.059167 | -0.0015808 | 0.00067084 | 0.0022687 | -0.0030517 | 0.0020593 | 0.068225 | 0.061566 | -0.00077757 | 0.0051653 | -0.0003182 | -0.004578 | 62.9883 | -59.3674 | 63.1027 | -59.166 | -59.6191 | -59.642 | -0.15106 | 62.9929 | -59.2712 | 63.0981 | -59.3903 | -59.4955 | -59.4223 | -0.073243 | -0.13733 | -0.022888 | 0.12817 | -0.3479 | -0.32501 | -0.27466 | -0.25177 | 0.022888 | -0.13275 | -0.027465 | -0.096131 | -0.12817 | -0.20142 | -0.15106 | -0.2243 | 0.20142 | 122.4701 | -0.11902 | 122.3694 | 122.3557 | 122.2641 | 122.2824 | 122.287 | -122.493 | -122.3969 | 122.3969 | 122.3923 | 59.2895 | 59.1431
159.3125 | 122.6074 | -59.2758 | 63.1119 | -0.10399 | 0.002194 | 0.064016 | 0.061517 | -0.003717 | 2.9842e-05 | -0.0022175 | -0.01831 | 0.0020593 | 0.06502 | 0.064984 | -0.0037684 | 0.0026019 | -0.0024546 | -0.086975 | 63.0295 | -59.3445 | 63.1393 | -59.2346 | -59.6191 | -59.5871 | -0.14648 | 62.9654 | -59.285 | 63.1302 | -59.3628 | -59.4772 | -59.4177 | -0.068664 | -0.082397 | 0.027466 | 0.041199 | -0.31128 | -0.34332 | -0.24262 | -0.27466 | -0.009155 | -0.14648 | 0.018311 | -0.086975 | -0.14191 | -0.20142 | -0.13275 | -0.19226 | 0.10986 | 122.4838 | -0.07782 | 122.4152 | 122.374 | 122.2504 | 122.3053 | 122.2412 | -122.4564 | -122.3969 | 122.4152 | 122.406 | 59.1888 | 59.1293
160.3281 | 122.6257 | -59.2804 | 63.1302 | -0.0048066 | 0.0013394 | 0.06423 | 0.060449 | 0.0048278 | -0.0025336 | -0.00029486 | -0.0091553 | 0.0031273 | 0.063952 | 0.063916 | -0.0016322 | 0.0058063 | 0.0007498 | 0.018311 | 63.0386 | -59.2987 | 63.2309 | -59.3765 | -59.6512 | -59.3857 | 0 | 62.9883 | -59.2392 | 63.1805 | -59.2804 | -59.4086 | -59.3674 | -0.01831 | -0.091553 | 0.10071 | -0.09613 | -0.10528 | -0.37079 | -0.086975 | -0.35248 | 0.041199 | -0.14191 | 0.050354 | 0 | -0.086975 | -0.12817 | -0.12817 | -0.16937 | -0.07782 | 122.5296 | -0.041199 | 122.4197 | 122.3373 | 122.2275 | 122.319 | 122.2687 | -122.4289 | -122.3694 | 122.5113 | 122.4609 | 59.2987 | 59.2804
161.3125 | 122.644 | -59.285 | 63.1622 | 0.063858 | 0.003262 | 0.064871 | 0.061944 | 0.0016236 | -0.0038154 | -0.00050846 | -0.012207 | 0.0022729 | 0.063525 | 0.05943 | 0.00071783 | 0.0053789 | -0.0037362 | 0 | 63.0524 | -59.2896 | 63.2172 | -59.1385 | -59.523 | -59.5047 | 0.009155 | 62.9837 | -59.2346 | 63.1485 | -59.2941 | -59.4315 | -59.3765 | -0.004578 | -0.10986 | 0.054932 | 0.14648 | -0.21973 | -0.23804 | -0.21515 | -0.23346 | 0.050354 | -0.17853 | -0.013732 | -0.009155 | -0.091553 | -0.14648 | -0.14191 | -0.19684 | 0.15106 | 122.5067 | -0.059509 | 122.3831 | 122.3419 | 122.2183 | 122.3373 | 122.2687 | -122.4518 | -122.3969 | 122.5021 | 122.4335 | 59.285 | 59.2941
162.3125 | 122.6578 | -59.2804 | 63.0936 | -0.035324 | 0.003262 | 0.062948 | 0.058954 | -0.002008 | -0.0012518 | -0.0032855 | 0.033569 | 0.0027001 | 0.065448 | 0.057294 | -0.0035548 | 0.0051653 | -0.0011728 | -0.041199 | 62.9608 | -59.2758 | 63.2309 | -59.1064 | -59.5139 | -59.4818 | -0.041199 | 62.9333 | -59.2529 | 63.1714 | -59.2804 | -59.3948 | -59.3582 | 0.004578 | -0.13275 | 0.13733 | 0.17395 | -0.20142 | -0.23346 | -0.20599 | -0.23804 | 0.027466 | -0.16022 | 0.07782 | 0 | -0.077819 | -0.11444 | -0.10529 | -0.14191 | 0.16937 | 122.5067 | -0.027466 | 122.4243 | 122.2366 | 122.1863 | 122.2412 | 122.2137 | -122.3694 | -122.3465 | 122.5113 | 122.4518 | 59.2392 | 59.2392
163.3125 | 122.6212 | -59.2712 | 63.1393 | -0.050583 | 0.0034756 | 0.063589 | 0.064294 | 0.0035462 | -0.0018928 | -0.0017903 | -0.039673 | 0.0020593 | 0.066516 | 0.061993 | -0.0035548 | 0.0062335 | 0.0013906 | -0.009155 | 63.0203 | -59.3216 | 63.2126 | -59.1751 | -59.5505 | -59.5276 | -0.045776 | 62.9974 | -59.2346 | 63.1393 | -59.3216 | -59.4543 | -59.4086 | -0.050354 | -0.11902 | 0.073242 | 0.09613 | -0.25635 | -0.27924 | -0.20599 | -0.22888 | 0.036621 | -0.14191 | 0 | -0.050354 | -0.13733 | -0.18311 | -0.17395 | -0.21973 | 0.14648 | 122.5342 | -0.086975 | 122.374 | 122.3419 | 122.2321 | 122.2916 | 122.2687 | -122.4609 | -122.374 | 122.4838 | 122.4106 | 59.2621 | 59.2255
164.3125 | 122.5616 | -59.285 | 63.1577 | 0.0028229 | 0.0009122 | 0.065298 | 0.06344 | 0.00055542 | -0.0016792 | -0.00050846 | -0.042725 | 0.0037683 | 0.06737 | 0.064343 | -0.0027002 | 0.0047381 | -0.0052316 | -0.045776 | 63.0478 | -59.3399 | 63.1531 | -59.2026 | -59.5871 | -59.5642 | -0.13733 | 62.9883 | -59.285 | 63.089 | -59.3765 | -59.5093 | -59.4452 | -0.054932 | -0.10986 | -0.004578 | 0.082397 | -0.27924 | -0.30212 | -0.2243 | -0.24719 | 0 | -0.16937 | -0.068665 | -0.091553 | -0.16022 | -0.2243 | -0.16022 | -0.2243 | 0.13733 | 122.493 | -0.091553 | 122.374 | 122.3877 | 122.2733 | 122.3328 | 122.2733 | -122.4976 | -122.4426 | 122.438 | 122.374 | 59.2392 | 59.1476
165.3281 | 122.612 | -59.2621 | 63.1714 | 0.0028229 | 0.000485 | 0.064016 | 0.057886 | -0.00093998 | -0.0021064 | -0.0017903 | 0.018311 | 0.0022729 | 0.068438 | 0.058148 | -0.0024866 | 0.0040973 | -0.0009592 | -0.027466 | 63.0569 | -59.3033 | 63.0249 | -59.1843 | -59.4406 | -59.5047 | -0.022888 | 63.0249 | -59.2484 | 63.1302 | -59.3079 | -59.4635 | -59.436 | -0.041199 | -0.11444 | -0.14649 | 0.07782 | -0.24262 | -0.17853 | -0.20142 | -0.13733 | 0.013733 | -0.14649 | -0.041199 | -0.045776 | -0.17395 | -0.20142 | -0.18768 | -0.21515 | 0.11902 | 122.3282 | -0.059509 | 122.3785 | 122.3602 | 122.2733 | 122.319 | 122.287 | -122.4747 | -122.4197 | 122.287 | 122.3923 | 59.2346 | 59.2392
166.3125 | 122.6074 | -59.2941 | 63.1393 | -0.042954 | 0.0011258 | 0.065512 | 0.064508 | 0.0054688 | -0.0036018 | -0.0024311 | 0.015259 | 0.0035547 | 0.066516 | 0.06413 | -0.0018458 | 0.0070879 | -0.0013864 | -0.082397 | 63.0386 | -59.3353 | 63.3774 | -59.0378 | -59.7198 | -59.5871 | -0.17395 | 62.9837 | -59.2804 | 63.1119 | -59.3903 | -59.523 | -59.4223 | -0.041199 | -0.10071 | 0.23804 | 0.25635 | -0.29297 | -0.42572 | -0.25177 | -0.38452 | 0.013732 | -0.15564 | -0.027466 | -0.096131 | -0.12817 | -0.22888 | -0.14191 | -0.24261 | 0.29755 | 122.7127 | -0.10986 | 122.3923 | 122.374 | 122.2641 | 122.3328 | 122.2778 | -122.4747 | -122.4197 | 122.6715 | 122.406 | 59.2117 | 59.1202
167.3125 | 122.7036 | -59.2621 | 63.1073 | -0.073471 | 0.0034756 | 0.060812 | 0.06109 | -0.0013672 | -0.0021064 | -0.0024311 | 0.064087 | -0.00071785 | 0.069507 | 0.057294 | -0.00099117 | 0.0038837 | -0.0001046 | -0.082397 | 62.9929 | -59.3124 | 63.2126 | -59.1476 | -59.5184 | -59.4772 | -0.050354 | 62.9517 | -59.2392 | 63.1851 | -59.2621 | -59.3674 | -59.3536 | -0.050354 | -0.11444 | 0.10528 | 0.11444 | -0.21515 | -0.25635 | -0.1648 | -0.20599 | 0.022888 | -0.15564 | 0.07782 | 0 | -0.091553 | -0.10529 | -0.11444 | -0.12817 | 0.16479 | 122.525 | -0.022888 | 122.4243 | 122.3053 | 122.1909 | 122.2549 | 122.2137 | -122.4197 | -122.3465 | 122.4747 | 122.4472 | 59.1797 | 59.2117
168.3125 | 122.5983 | -59.2575 | 63.1531 | -0.050583 | 0.0028348 | 0.064444 | 0.063653 | 0.002478 | -0.0021064 | -0.00029486 | -0.033569 | 0.0037683 | 0.066729 | 0.069257 | -0.0037684 | 0.0043109 | -0.0037362 | -0.022888 | 63.0203 | -59.317 | 63.176 | -59.1797 | -59.5596 | -59.5551 | -0.082397 | 62.9974 | -59.2758 | 63.1439 | -59.3445 | -59.5093 | -59.4315 | -0.05951 | -0.13275 | 0.022888 | 0.07782 | -0.29755 | -0.30212 | -0.23804 | -0.24261 | -0.018311 | -0.15564 | -0.009155 | -0.086975 | -0.17395 | -0.25177 | -0.15564 | -0.23346 | 0.13733 | 122.493 | -0.068664 | 122.4197 | 122.3373 | 122.2733 | 122.2778 | 122.2549 | -122.4701 | -122.4289 | 122.4335 | 122.4014 | 59.2346 | 59.1751
169.3125 | 122.6028 | -59.2941 | 63.1073 | -0.081101 | 0.001553 | 0.063376 | 0.063226 | 0.0022644 | -0.0027472 | 0.0024823 | -0.027466 | 0.0027001 | 0.065661 | 0.067761 | -0.0037684 | 0.0068743 | -0.0018136 | -0.07782 | 63.0341 | -59.3445 | 63.1256 | -59.2484 | -59.5871 | -59.5779 | -0.13275 | 62.9745 | -59.2712 | 63.1119 | -59.3719 | -59.4955 | -59.4177 | -0.050354 | -0.073242 | 0.01831 | 0.045776 | -0.28381 | -0.29297 | -0.23346 | -0.24262 | 0.022888 | -0.13275 | 0.004577 | -0.07782 | -0.1236 | -0.20142 | -0.14648 | -0.2243 | 0.09613 | 122.4701 | -0.10071 | 122.3831 | 122.3785 | 122.2458 | 122.3282 | 122.2687 | -122.4518 | -122.3785 | 122.4197 | 122.406 | 59.2163 | 59.1614
170.3281 | 122.5891 | -59.2667 | 63.121 | -0.065842 | 0.0026212 | 0.064444 | 0.063012 | -0.0022218 | -0.0029608 | -0.0032855 | -0.048828 | 0.0022729 | 0.066729 | 0.066693 | -0.0035548 | 0.0075153 | -0.0016 | -0.022888 | 63.0112 | -59.3399 | 63.1851 | -59.1797 | -59.5688 | -59.5642 | -0.09613 | 62.9929 | -59.2575 | 63.1027 | -59.3719 | -59.491 | -59.4269 | -0.073242 | -0.10986 | 0.064087 | 0.086976 | -0.29755 | -0.30212 | -0.2243 | -0.22888 | 0.009156 | -0.12817 | -0.018311 | -0.10529 | -0.16022 | -0.2243 | -0.16937 | -0.23346 | 0.16022 | 122.525 | -0.11444 | 122.3602 | 122.3511 | 122.2504 | 122.2778 | 122.2595 | -122.4609 | -122.3785 | 122.4518 | 122.3694 | 59.2438 | 59.1705
171.3125 | 122.5891 | -59.2987 | 63.1165 | -0.08873 | 0.0013394 | 0.06188 | 0.060449 | 0.0029052 | -0.0016792 | 0.00077334 | -0.01831 | 0.00077755 | 0.066943 | 0.064984 | -0.0024866 | 0.0051653 | -0.005018 | -0.027466 | 63.0341 | -59.3353 | 63.1256 | -59.2392 | -59.6466 | -59.5917 | -0.13733 | 63.0112 | -59.2896 | 63.1027 | -59.3903 | -59.5047 | -59.4223 | -0.036621 | -0.082397 | 0.009155 | 0.059509 | -0.29297 | -0.3479 | -0.25635 | -0.31128 | 0.009155 | -0.10529 | -0.013733 | -0.091553 | -0.1236 | -0.20599 | -0.13275 | -0.21515 | 0.09613 | 122.4609 | -0.10071 | 122.3923 | 122.3694 | 122.3007 | 122.3328 | 122.3099 | -122.4518 | -122.406 | 122.4243 | 122.4014 | 59.2712 | 59.1614
172.3281 | 122.7036 | -59.2438 | 63.121 | -0.065842 | 0.0043302 | 0.063376 | 0.058526 | -0.0017944 | -0.0036018 | -0.0028583 | 0.036621 | -7.6854e-05 | 0.067157 | 0.060071 | -0.002273 | 0.0045245 | -0.0024546 | 0.054932 | 62.9974 | -59.2575 | 63.3911 | -58.6166 | -59.2667 | -59.6741 | 0.19226 | 62.9608 | -59.2346 | 63.2401 | -59.1614 | -59.2987 | -59.2758 | -0.013733 | -0.1236 | 0.27008 | 0.62714 | -0.4303 | -0.022889 | -0.41657 | -0.009156 | 0.009155 | -0.16022 | 0.11902 | 0.082397 | -0.032044 | -0.054932 | -0.041199 | -0.064087 | 0.64087 | 122.6486 | 0.073242 | 122.4747 | 122.2549 | 122.1954 | 122.2412 | 122.2046 | -122.3785 | -122.3557 | 122.6349 | 122.4838 | 59.2987 | 59.436
173.3125 | 122.6166 | -59.2758 | 63.1348 | -0.042954 | 0.003262 | 0.063162 | 0.062799 | -0.0011536 | -0.0029608 | 0.00077334 | -0.042725 | 0.00077755 | 0.065234 | 0.064343 | -0.003341 | 0.0045245 | -0.0001046 | 0 | 63.0341 | -59.3216 | 63.2263 | -59.1431 | -59.5367 | -59.5322 | -0.027466 | 62.9929 | -59.2484 | 63.1393 | -59.317 | -59.4452 | -59.3857 | -0.045776 | -0.10071 | 0.091552 | 0.13275 | -0.25635 | -0.26093 | -0.21057 | -0.21515 | 0.027466 | -0.14191 | 0.004577 | -0.041199 | -0.10986 | -0.16937 | -0.13733 | -0.19684 | 0.17853 | 122.5479 | -0.068665 | 122.3877 | 122.3557 | 122.2412 | 122.3099 | 122.2687 | -122.4564 | -122.3831 | 122.5021 | 122.4152 | 59.2758 | 59.2484
174.3125 | 122.58 | -59.3079 | 63.1531 | -0.035324 | 0.0019802 | 0.064657 | 0.06344 | -8.538e-05 | -0.0014654 | -0.0013629 | -0.036621 | 0.0020593 | 0.067798 | 0.065625 | -0.0041956 | 0.0068743 | -0.0035226 | -0.036621 | 63.0249 | -59.317 | 63.1668 | -59.1888 | -59.5825 | -59.5459 | -0.09613 | 63.0066 | -59.2621 | 63.1256 | -59.3674 | -59.5001 | -59.4269 | -0.009156 | -0.12817 | 0.013733 | 0.11902 | -0.23804 | -0.27466 | -0.22888 | -0.2655 | 0.045776 | -0.14648 | -0.027466 | -0.05951 | -0.11902 | -0.19226 | -0.16479 | -0.23804 | 0.12817 | 122.4838 | -0.10529 | 122.3877 | 122.3419 | 122.2687 | 122.3328 | 122.3145 | -122.4701 | -122.4152 | 122.4747 | 122.4335 | 59.2712 | 59.2117
175.3125 | 122.6669 | -59.2575 | 63.1027 | -0.081101 | 0.0013394 | 0.064871 | 0.059595 | 0.00034182 | -0.0016792 | -0.0013629 | 0.027466 | 0.0014185 | 0.068225 | 0.064984 | -0.002273 | 0.0040973 | -0.0048044 | -0.045776 | 62.9974 | -59.2712 | 63.2126 | -59.1293 | -59.5139 | -59.4955 | -0.036621 | 62.9196 | -59.2255 | 63.1805 | -59.285 | -59.3857 | -59.3628 | -0.013733 | -0.10529 | 0.10986 | 0.12817 | -0.23804 | -0.25635 | -0.2243 | -0.24262 | 0.032043 | -0.1831 | 0.07782 | -0.027466 | -0.10529 | -0.12817 | -0.13733 | -0.16022 | 0.14191 | 122.4838 | -0.059509 | 122.406 | 122.2687 | 122.1451 | 122.2549 | 122.1771 | -122.374 | -122.3282 | 122.4701 | 122.438 | 59.2117 | 59.2209
176.3125 | 122.5662 | -59.3033 | 63.1348 | -0.027695 | -0.000156 | 0.06423 | 0.061944 | -0.00051278 | -0.0018928 | -0.00072206 | -0.039673 | 0.00035035 | 0.068652 | 0.059857 | -0.0027002 | 0.0055927 | -0.000532 | 0.032043 | 63.0432 | -59.3033 | 63.2355 | -59.1293 | -59.4955 | -59.5047 | 0.013733 | 63.0295 | -59.2438 | 63.1989 | -59.2758 | -59.5779 | -59.5871 | 0 | -0.091553 | 0.10071 | 0.17395 | -0.20142 | -0.19226 | -0.20142 | -0.19226 | 0.05951 | -0.10529 | 0.064087 | 0.027466 | -0.28381 | -0.27466 | -0.34332 | -0.33417 | 0.17395 | 122.5388 | -0.032044 | 122.4426 | 122.3465 | 122.2733 | 122.3465 | 122.3328 | -122.4381 | -122.3785 | 122.5388 | 122.5021 | 59.3353 | 59.317
177.3125 | 122.5937 | -59.2987 | 63.1485 | 0.018082 | -0.0007968 | 0.06423 | 0.062585 | 0.0039734 | -0.0029608 | -0.0013629 | -0.064087 | 0.0016321 | 0.066089 | 0.061993 | -0.0027002 | 0.0060199 | -0.0022408 | -0.073242 | 63.0386 | -59.3399 | 63.1073 | -59.2392 | -59.6008 | -59.5779 | -0.16022 | 63.002 | -59.2941 | 63.1165 | -59.3719 | -59.523 | -59.4406 | -0.041199 | -0.10986 | -0.041199 | 0.059509 | -0.27924 | -0.30212 | -0.23804 | -0.26093 | 0.004578 | -0.14648 | -0.032044 | -0.073242 | -0.14191 | -0.2243 | -0.14648 | -0.22888 | 0.10071 | 122.4472 | -0.07782 | 122.4106 | 122.3785 | 122.2961 | 122.3373 | 122.3007 | -122.4884 | -122.4426 | 122.406 | 122.4152 | 59.2255 | 59.1385
178.3125 | 122.5845 | -59.2712 | 63.1256 | -0.058212 | 0.0039028 | 0.06423 | 0.061731 | 0.00012822 | 0.0017388 | 0.00055974 | -0.033569 | 0.0014185 | 0.064593 | 0.06413 | -0.003982 | 0.0066607 | -0.0018136 | -0.004578 | 63.0524 | -59.3124 | 63.208 | -59.1476 | -59.5413 | -59.5551 | -0.027466 | 63.0112 | -59.2621 | 63.1439 | -59.3216 | -59.4772 | -59.404 | -0.041199 | -0.073242 | 0.082398 | 0.1236 | -0.28381 | -0.27008 | -0.24262 | -0.22888 | 0.009155 | -0.11444 | 0.018311 | -0.050354 | -0.13275 | -0.20599 | -0.14191 | -0.21515 | 0.16479 | 122.5204 | -0.059509 | 122.406 | 122.3648 | 122.2733 | 122.3236 | 122.2824 | -122.438 | -122.3877 | 122.4792 | 122.4152 | 59.2667 | 59.2438
179.3125 | 122.5754 | -59.2896 | 63.1439 | -0.042954 | 0.002194 | 0.064444 | 0.060449 | -0.0013672 | -0.0021064 | 0.00013254 | -0.05188 | 0.0024865 | 0.069934 | 0.063061 | -0.0020594 | 0.0073015 | 0.0009634 | -0.045776 | 63.0341 | -59.3308 | 63.1531 | -59.2072 | -59.5734 | -59.5825 | -0.1236 | 63.002 | -59.2575 | 63.0936 | -59.3719 | -59.5276 | -59.4315 | -0.041199 | -0.10986 | 0.009155 | 0.082398 | -0.29297 | -0.28381 | -0.25177 | -0.24261 | 0.032044 | -0.14191 | -0.050354 | -0.082397 | -0.14191 | -0.23804 | -0.17395 | -0.27008 | 0.1236 | 122.4838 | -0.11444 | 122.3511 | 122.3648 | 122.2595 | 122.3236 | 122.2916 | -122.4747 | -122.4014 | 122.4426 | 122.3831 | 59.2438 | 59.166
180.3281 | 122.7036 | -59.2346 | 63.1302 | -0.027695 | 0.0034756 | 0.063589 | 0.058313 | -0.0011536 | -0.004029 | -8.1264e-05 | 0.042725 | -0.00071785 | 0.06737 | 0.063061 | -0.0020594 | 0.0053789 | -0.0009592 | 0.073242 | 63.0295 | -59.2667 | 63.3133 | -59.0149 | -59.3994 | -59.3948 | 0.10529 | 62.9929 | -59.2117 | 63.2263 | -59.1934 | -59.3079 | -59.3079 | -0.032044 | -0.10071 | 0.18311 | 0.21973 | -0.16022 | -0.16479 | -0.12817 | -0.13275 | 0.022888 | -0.13733 | 0.09613 | 0.041199 | -0.073242 | -0.073242 | -0.09613 | -0.09613 | 0.25177 | 122.58 | 0.018311 | 122.438 | 122.2961 | 122.2046 | 122.2641 | 122.2275 | -122.3969 | -122.3419 | 122.5479 | 122.4609 | 59.3079 | 59.3399
181.3125 | 122.6166 | -59.2712 | 63.1622 | -0.08873 | 0.0034756 | 0.064871 | 0.063653 | -0.00093998 | -0.0016792 | -0.0013629 | -0.07019 | 0.0024865 | 0.06972 | 0.067334 | -0.0024866 | 0.0073015 | -0.0024546 | 0.013733 | 63.0249 | -59.3124 | 63.2309 | -59.1293 | -59.5276 | -59.5139 | 0.009155 | 63.002 | -59.2438 | 63.1622 | -59.2941 | -59.4406 | -59.3765 | -0.041199 | -0.13733 | 0.068665 | 0.14191 | -0.24262 | -0.25635 | -0.20142 | -0.21515 | 0.027466 | -0.16022 | 0 | -0.022888 | -0.10529 | -0.16937 | -0.13275 | -0.19684 | 0.18311 | 122.5433 | -0.050354 | 122.406 | 122.3373 | 122.2458 | 122.2961 | 122.2733 | -122.4747 | -122.406 | 122.5021 | 122.4335 | 59.285 | 59.2804
182.3125 | 122.6532 | -59.2575 | 63.121 | -0.096359 | 0.0030484 | 0.065298 | 0.059595 | -0.002008 | -0.00082456 | -0.0022175 | 0.039673 | 0.00077755 | 0.065875 | 0.061139 | -0.0024866 | 0.0083697 | 0.0013906 | -0.041199 | 62.9883 | -59.3308 | 63.2263 | -59.111 | -59.5139 | -59.4727 | -0.036621 | 62.9288 | -59.2392 | 63.1668 | -59.2896 | -59.3903 | -59.3582 | -0.073243 | -0.13275 | 0.10529 | 0.14648 | -0.21515 | -0.25635 | -0.14191 | -0.1831 | 0.01831 | -0.19226 | 0.045776 | -0.032044 | -0.10071 | -0.13275 | -0.11902 | -0.15106 | 0.21973 | 122.5571 | -0.050354 | 122.406 | 122.319 | 122.168 | 122.2458 | 122.1863 | -122.4518 | -122.3602 | 122.4838 | 122.4243 | 59.2163 | 59.2209
183.3125 | 122.6166 | -59.2484 | 63.1348 | 0.086746 | 0.002194 | 0.064444 | 0.061944 | 0.0014098 | -0.0016792 | -0.0022175 | -0.036621 | 0.0018457 | 0.067157 | 0.060071 | -0.0046228 | 0.0066607 | -0.0056588 | 0.036621 | 63.0386 | -59.3216 | 63.2309 | -59.111 | -59.4818 | -59.4955 | 0.032043 | 63.0066 | -59.2438 | 63.176 | -59.285 | -59.404 | -59.3719 | -0.073242 | -0.096131 | 0.09613 | 0.13733 | -0.24719 | -0.23346 | -0.17395 | -0.16022 | 0.004578 | -0.12817 | 0.041198 | -0.036621 | -0.1236 | -0.15564 | -0.12817 | -0.16022 | 0.21057 | 122.5525 | -0.041199 | 122.4197 | 122.3602 | 122.2504 | 122.287 | 122.2549 | -122.4564 | -122.3785 | 122.4792 | 122.4243 | 59.285 | 59.2804
184.3125 | 122.5937 | -59.2758 | 63.1485 | -0.050583 | 0.002194 | 0.064657 | 0.063226 | 0.00076902 | -0.0031744 | -0.0011493 | -0.036621 | 0.00099115 | 0.066516 | 0.062848 | -0.0044092 | 0.0058063 | -0.0026682 | -0.045776 | 63.0341 | -59.3399 | 63.1485 | -59.2026 | -59.5871 | -59.5871 | -0.11444 | 63.002 | -59.2438 | 63.0936 | -59.3903 | -59.5184 | -59.4406 | -0.064087 | -0.11444 | 0 | 0.073242 | -0.31128 | -0.31128 | -0.24719 | -0.24719 | 0.032044 | -0.14648 | -0.054932 | -0.11444 | -0.16479 | -0.24262 | -0.19684 | -0.27466 | 0.13733 | 122.4884 | -0.14648 | 122.3373 | 122.374 | 122.2458 | 122.3099 | 122.2778 | -122.4884 | -122.3923 | 122.4243 | 122.3694 | 59.23 | 59.1614
185.3125 | 122.5571 | -59.285 | 63.1668 | -0.058212 | 0.0034756 | 0.062521 | 0.062158 | 0.0020508 | -0.0025336 | 0.0018413 | -0.054932 | 0.0022729 | 0.064807 | 0.063275 | -0.0031274 | 0.0060199 | -0.0039498 | -0.036621 | 63.0066 | -59.3353 | 63.1668 | -59.198 | -59.5688 | -59.5779 | -0.09613 | 62.9883 | -59.2484 | 63.1165 | -59.3765 | -59.4955 | -59.4223 | -0.050354 | -0.16022 | 0 | 0.086975 | -0.29297 | -0.28381 | -0.24262 | -0.23346 | 0.036621 | -0.17853 | -0.050354 | -0.091553 | -0.13733 | -0.21057 | -0.17395 | -0.24719 | 0.13733 | 122.5021 | -0.12817 | 122.3648 | 122.3419 | 122.2366 | 122.2916 | 122.2733 | -122.5021 | -122.4152 | 122.4518 | 122.4014 | 59.2484 | 59.1888
186.3125 | 122.6074 | -59.2621 | 63.1256 | 0.0028229 | 0.0028348 | 0.063162 | 0.062585 | -0.0015808 | -0.0018928 | -8.1264e-05 | -0.036621 | 0.0018457 | 0.068438 | 0.058789 | -0.00056397 | 0.0062335 | -0.0016 | 0.032043 | 63.0615 | -59.317 | 63.2263 | -59.1339 | -59.5047 | -59.5001 | 0 | 62.9929 | -59.2346 | 63.1622 | -59.2941 | -59.4498 | -59.3582 | -0.054932 | -0.064087 | 0.10071 | 0.12817 | -0.23804 | -0.24262 | -0.1831 | -0.18768 | 0.027466 | -0.13275 | 0.036621 | -0.032043 | -0.09613 | -0.18768 | -0.1236 | -0.21515 | 0.18311 | 122.5433 | -0.059509 | 122.3969 | 122.3785 | 122.2275 | 122.3236 | 122.2549 | -122.4426 | -122.3602 | 122.4884 | 122.4243 | 59.2941 | 59.2621
187.3125 | 122.5433 | -59.2712 | 63.1668 | -0.042954 | 0.0026212 | 0.063803 | 0.061517 | 0.0026916 | -0.00232 | -0.0013629 | -0.045776 | 0.0027001 | 0.068011 | 0.063489 | -0.0041956 | 0.0085833 | -0.0024546 | -0.064087 | 63.0157 | -59.3353 | 63.1348 | -59.2392 | -59.61 | -59.5871 | -0.16937 | 62.97 | -59.2804 | 63.0478 | -59.0378 | -59.3811 | -59.4727 | -0.064087 | -0.15106 | -0.032043 | 0.032043 | -0.31586 | -0.33875 | -0.25177 | -0.27466 | -0.009156 | -0.19684 | -0.11902 | 0.23346 | -0.20142 | -0.10986 | -0.19226 | -0.10071 | 0.09613 | 122.4701 | 0.24262 | 122.3282 | 122.3511 | 122.2504 | 122.287 | 122.2412 | -122.5021 | -122.4472 | 122.406 | 122.319 | 59.2072 | 59.1019
188.3125 | 122.6486 | -59.2667 | 63.1073 | -0.10399 | 0.0026212 | 0.065085 | 0.060449 | -0.0056396 | 0.00045724 | 0.0018413 | 0.030518 | 0.0020593 | 0.065875 | 0.060925 | -0.0027002 | 0.0045245 | -0.0043772 | -0.036621 | 62.9929 | -59.2987 | 63.2263 | -59.0881 | -59.5047 | -59.4772 | -0.018311 | 62.9654 | -59.2438 | 63.176 | -59.2758 | -59.3765 | -59.3628 | -0.032043 | -0.11444 | 0.11902 | 0.17853 | -0.21057 | -0.23804 | -0.17853 | -0.20599 | 0.022889 | -0.14191 | 0.068664 | -0.009155 | -0.09613 | -0.10986 | -0.11902 | -0.13275 | 0.21057 | 122.525 | -0.032044 | 122.4197 | 122.2916 | 122.2092 | 122.2595 | 122.2321 | -122.406 | -122.3511 | 122.493 | 122.4426 | 59.23 | 59.2484
189.3281 | 122.7081 | -59.2255 | 63.1302 | -0.027695 | 0.0043302 | 0.063803 | 0.062372 | -0.002008 | 0.00067084 | 0.0014141 | 0.054932 | 0.0016321 | 0.066729 | 0.060498 | -0.0054774 | 0.0047381 | -0.0018136 | 0.054932 | 63.0112 | -59.2575 | 63.2858 | -59.0378 | -59.4086 | -59.4086 | 0.13275 | 62.9608 | -59.1934 | 63.2355 | -59.1934 | -59.3124 | -59.2941 | -0.032043 | -0.11902 | 0.15564 | 0.18768 | -0.1831 | -0.1831 | -0.15106 | -0.15106 | 0.032044 | -0.16937 | 0.10529 | 0.032044 | -0.068664 | -0.086975 | -0.10071 | -0.11902 | 0.21973 | 122.5433 | 0 | 122.4289 | 122.2687 | 122.1542 | 122.2366 | 122.1863 | -122.3877 | -122.3236 | 122.5113 | 122.4609 | 59.2804 | 59.3582
190.3125 | 122.5983 | -59.2484 | 63.1851 | -0.027695 | 0.0013394 | 0.063162 | 0.06109 | -0.0022218 | -0.003388 | 0.00013254 | -0.030517 | 0.0024865 | 0.067157 | 0.06413 | -0.0041956 | 0.0068743 | -0.0026682 | 0.009155 | 63.0615 | -59.3124 | 63.1897 | -59.1751 | -59.523 | -59.5276 | -0.009155 | 63.0249 | -59.23 | 63.1668 | -59.2941 | -59.4177 | -59.3491 | -0.064087 | -0.1236 | 0.004577 | 0.073242 | -0.27924 | -0.27466 | -0.21515 | -0.21057 | 0.01831 | -0.16022 | -0.018311 | -0.045776 | -0.10071 | -0.16937 | -0.11902 | -0.18768 | 0.13733 | 122.5021 | -0.064086 | 122.3969 | 122.374 | 122.2549 | 122.3099 | 122.2733 | -122.4976 | -122.4152 | 122.438 | 122.4152 | 59.2575 | 59.2392
191.3125 | 122.7264 | -59.2758 | 63.0753 | -0.096359 | 0.0051846 | 0.063589 | 0.061731 | 0.0044006 | -0.0021064 | -0.0013629 | -0.054932 | 0.00035035 | 0.066729 | 0.065198 | -0.0041956 | 0.0070879 | -0.0009592 | -0.013733 | 62.9929 | -59.3033 | 63.0844 | -59.0607 | -59.1431 | -59.3216 | 0.018311 | 62.9379 | -59.23 | 63.2263 | -59.2255 | -59.3857 | -59.3353 | -0.027466 | -0.082397 | 0.009156 | 0.21515 | -0.045776 | 0.13275 | -0.01831 | 0.16022 | 0.045776 | -0.13733 | 0.15106 | 0.050354 | -0.059509 | -0.10986 | -0.10529 | -0.15564 | 0.24262 | 122.3877 | 0.004578 | 122.4564 | 122.2961 | 122.168 | 122.2687 | 122.2137 | -122.3785 | -122.3053 | 122.3602 | 122.5021 | 59.2621 | 59.2941
192.3125 | 122.6303 | -59.2484 | 63.1439 | 0.0028229 | 0.0030484 | 0.064444 | 0.06109 | -0.0041444 | 0.00024344 | 0.00034614 | -0.024414 | -0.00029045 | 0.06737 | 0.059644 | -0.0037684 | 0.0066607 | -0.0037362 | 0.032043 | 63.0478 | -59.317 | 63.2172 | -59.1248 | -59.5001 | -59.4955 | 0.036621 | 63.0341 | -59.2346 | 63.1577 | -59.2896 | -59.4131 | -59.3445 | -0.068665 | -0.09613 | 0.073242 | 0.1236 | -0.24719 | -0.25177 | -0.17853 | -0.1831 | 0.013733 | -0.10986 | 0.013733 | -0.041199 | -0.09613 | -0.1648 | -0.10986 | -0.17853 | 0.19226 | 122.5342 | -0.054932 | 122.3923 | 122.3648 | 122.2687 | 122.2961 | 122.2824 | -122.4609 | -122.3785 | 122.4655 | 122.406 | 59.2804 | 59.285
193.3281 | 122.6761 | -59.2438 | 63.1165 | -0.096359 | 0.0013394 | 0.064871 | 0.058526 | -0.0039306 | -0.00061096 | -0.0034991 | 0.048828 | 0.0014185 | 0.066729 | 0.060498 | -0.0020594 | 0.0051653 | -0.0011728 | -0.027466 | 63.0066 | -59.2896 | 63.2172 | -59.1202 | -59.491 | -59.4772 | 0 | 62.9517 | -59.2575 | 63.1897 | -59.2529 | -59.3536 | -59.3079 | -0.045777 | -0.10986 | 0.10071 | 0.1236 | -0.23346 | -0.24719 | -0.18768 | -0.20142 | -0.013733 | -0.1648 | 0.073242 | -0.009156 | -0.064087 | -0.10986 | -0.050354 | -0.096131 | 0.16937 | 122.5067 | 0.004577 | 122.4472 | 122.2961 | 122.2092 | 122.2504 | 122.1954 | -122.406 | -122.374 | 122.4609 | 122.4335 | 59.2163 | 59.2438
194.3125 | 122.6669 | -59.285 | 63.1073 | 0.03334 | 0.0028348 | 0.062948 | 0.061303 | 0.0026916 | -0.00039736 | -8.1264e-05 | -0.042725 | 0.0022729 | 0.066943 | 0.059644 | -0.0029138 | 0.0064471 | -0.0028818 | -0.086975 | 63.0066 | -59.3399 | 63.1714 | -59.2072 | -59.5963 | -59.5688 | -0.10986 | 62.9745 | -59.2621 | 63.1531 | -59.3079 | -59.4635 | -59.3857 | -0.054932 | -0.10071 | 0.064087 | 0.07782 | -0.28381 | -0.31128 | -0.22888 | -0.25635 | 0.022888 | -0.13275 | 0.045776 | -0.022888 | -0.10071 | -0.17853 | -0.1236 | -0.20142 | 0.13275 | 122.5113 | -0.045776 | 122.4152 | 122.3465 | 122.2366 | 122.2916 | 122.2595 | -122.4472 | -122.3694 | 122.4564 | 122.438 | 59.198 | 59.1751
195.3125 | 122.6074 | -59.2621 | 63.1348 | 0.0028229 | 0.0024076 | 0.065512 | 0.06344 | 0.0037598 | -0.003388 | -0.00072206 | -0.067139 | 0.0014185 | 0.065661 | 0.067761 | -0.0029138 | 0.0090105 | -0.0007456 | 0.018311 | 63.0157 | -59.3216 | 63.2217 | -59.1293 | -59.523 | -59.5139 | -0.009155 | 63.0341 | -59.2255 | 63.1485 | -59.2987 | -59.4406 | -59.3903 | -0.059509 | -0.11902 | 0.086975 | 0.13275 | -0.25177 | -0.26093 | -0.19226 | -0.20142 | 0.036621 | -0.10071 | 0.013733 | -0.036621 | -0.12817 | -0.17853 | -0.16479 | -0.21515 | 0.19226 | 122.5433 | -0.073242 | 122.374 | 122.3373 | 122.2595 | 122.2778 | 122.2961 | -122.4564 | -122.3602 | 122.4838 | 122.4106 | 59.2804 | 59.2529
196.3125 | 122.5662 | -59.285 | 63.1485 | -0.081101 | 0.0026212 | 0.063376 | 0.062372 | 0.00098262 | 0.00067084 | 0.00013254 | -0.033569 | 0.0029137 | 0.067798 | 0.061993 | -0.0018458 | 0.0049517 | -0.003309 | -0.045776 | 63.0295 | -59.3308 | 63.1805 | -59.2026 | -59.5688 | -59.5596 | -0.082397 | 63.002 | -59.2621 | 63.1073 | -59.3628 | -59.5001 | -59.4223 | -0.045777 | -0.11902 | 0.032043 | 0.082397 | -0.27466 | -0.28381 | -0.22888 | -0.23804 | 0.022888 | -0.14648 | -0.041199 | -0.07782 | -0.13733 | -0.21515 | -0.16022 | -0.23804 | 0.12817 | 122.5113 | -0.10071 | 122.3694 | 122.3602 | 122.2641 | 122.3145 | 122.287 | -122.4792 | -122.4106 | 122.4655 | 122.3923 | 59.2392 | 59.2026
197.3125 | 122.6578 | -59.2575 | 63.0981 | -0.035324 | 0.001553 | 0.066794 | 0.061517 | -0.0045716 | -0.0044562 | -0.0013629 | 0.039673 | 0.00035035 | 0.065661 | 0.058362 | -0.0018458 | 0.0043109 | -0.0018136 | -0.045776 | 62.9883 | -59.2484 | 63.2126 | -59.1248 | -59.5276 | -59.4818 | -0.041199 | 62.9608 | -59.2484 | 63.1714 | -59.285 | -59.3948 | -59.3491 | 0.009155 | -0.10986 | 0.11444 | 0.13275 | -0.22431 | -0.27008 | -0.23346 | -0.27924 | 0.009155 | -0.13733 | 0.073242 | -0.027466 | -0.091553 | -0.13733 | -0.10071 | -0.14648 | 0.1236 | 122.4609 | -0.036621 | 122.4197 | 122.2366 | 122.2092 | 122.2458 | 122.2183 | -122.3465 | -122.3465 | 122.4701 | 122.4289 | 59.2117 | 59.2163
198.3125 | 122.731 | -59.23 | 63.0844 | -0.10399 | 0.0030484 | 0.06658 | 0.060235 | 0.0037598 | -0.0027472 | -8.1264e-05 | 0.0061035 | 0.00056395 | 0.063952 | 0.066907 | -0.003341 | 0.0077289 | -0.0065134 | -0.018311 | 62.9654 | -59.3124 | 63.2172 | -59.3262 | -59.4864 | -59.2712 | -0.068665 | 62.9471 | -59.2392 | 63.2217 | -59.2529 | -59.3674 | -59.3079 | -0.082397 | -0.11902 | 0.13275 | -0.09613 | -0.041198 | -0.25635 | 0.041199 | -0.17395 | -0.009155 | -0.13733 | 0.13733 | -0.022888 | -0.077819 | -0.13733 | -0.068664 | -0.12817 | -0.013733 | 122.5296 | -0.013733 | 122.4609 | 122.2778 | 122.1863 | 122.1954 | 122.1771 | -122.3969 | -122.3236 | 122.4472 | 122.4518 | 59.2117 | 59.1614
199.3125 | 122.6349 | -59.2621 | 63.1348 | -0.065842 | 0.0026212 | 0.062735 | 0.059808 | -0.00093998 | -0.0010382 | -0.0013629 | -0.054932 | 0.0018457 | 0.067584 | 0.066693 | -0.003982 | 0.0060199 | -0.0065134 | -0.013733 | 63.0386 | -59.3262 | 63.2309 | -59.1248 | -59.5139 | -59.5093 | 0.032043 | 63.0203 | -59.2392 | 63.176 | -59.2804 | -59.4223 | -59.3719 | -0.064087 | -0.096131 | 0.09613 | 0.13733 | -0.24719 | -0.25177 | -0.1831 | -0.18768 | 0.022888 | -0.11444 | 0.041198 | -0.018311 | -0.10986 | -0.16022 | -0.13275 | -0.18311 | 0.20142 | 122.5571 | -0.041199 | 122.4152 | 122.3648 | 122.2595 | 122.3007 | 122.2824 | -122.4609 | -122.374 | 122.493 | 122.438 | 59.2484 | 59.2941
200.3125 | 122.58 | -59.285 | 63.1393 | -0.0048066 | 0.0026212 | 0.06423 | 0.062585 | 0.0022644 | -0.0025336 | 0.0033367 | -0.039673 | 0.0035547 | 0.066943 | 0.063061 | -0.0029138 | 0.0073015 | 0.0005362 | -0.018311 | 63.0249 | -59.317 | 63.1943 | -59.1476 | -59.5596 | -59.5596 | -0.050354 | 62.9883 | -59.2667 | 63.1165 | -59.3399 | -59.4681 | -59.4086 | -0.032044 | -0.11444 | 0.054932 | 0.13733 | -0.27466 | -0.27466 | -0.24261 | -0.24261 | 0.01831 | -0.15106 | -0.022888 | -0.054932 | -0.1236 | -0.18311 | -0.14191 | -0.20142 | 0.16937 | 122.5113 | -0.073242 | 122.3831 | 122.3419 | 122.2549 | 122.3099 | 122.2733 | -122.4564 | -122.406 | 122.4792 | 122.4014 | 59.2667 | 59.2346
201.3125 | 122.6624 | -59.2667 | 63.1027 | -0.065842 | 0.0024076 | 0.065939 | 0.061731 | -0.00051278 | -0.00061096 | -0.0013629 | -0.0030517 | 0.0029137 | 0.066943 | 0.061993 | -0.0046228 | 0.0062335 | -0.0009592 | -0.073242 | 63.0249 | -59.3674 | 63.1485 | -59.2072 | -59.5688 | -59.5322 | -0.10529 | 62.9517 | -59.2712 | 63.176 | -59.3079 | -59.4315 | -59.3536 | -0.10071 | -0.07782 | 0.045777 | 0.05951 | -0.2655 | -0.30212 | -0.16479 | -0.20142 | -0.004577 | -0.15106 | 0.073242 | -0.041198 | -0.086975 | -0.16479 | -0.082398 | -0.16022 | 0.16022 | 122.5159 | -0.036621 | 122.4472 | 122.3923 | 122.2229 | 122.2916 | 122.2183 | -122.4701 | -122.374 | 122.4152 | 122.4426 | 59.1934 | 59.1614
202.3125 | 122.6669 | -59.2529 | 63.0981 | -0.050583 | 0.0017666 | 0.065725 | 0.059595 | -0.00072638 | -0.003388 | 0.0012005 | 0.039673 | 0.00035035 | 0.066943 | 0.063061 | -0.0014184 | 0.0053789 | -0.0020272 | -0.050354 | 63.0249 | -59.3079 | 63.3911 | -59.2255 | -59.6512 | -59.4818 | -0.045776 | 62.9608 | -59.2621 | 63.1485 | -59.2758 | -59.3811 | -59.3353 | -0.054931 | -0.073243 | 0.29297 | 0.027466 | -0.22888 | -0.39825 | -0.17395 | -0.34332 | -0.009155 | -0.13733 | 0.050354 | -0.022888 | -0.082397 | -0.12817 | -0.073242 | -0.11902 | 0.082397 | 122.699 | -0.013733 | 122.4106 | 122.3328 | 122.2229 | 122.2778 | 122.2137 | -122.406 | -122.3602 | 122.644 | 122.4014 | 59.2026 | 59.2072
203.3125 | 122.6532 | -59.2392 | 63.1027 | -0.10399 | 0.0017666 | 0.064657 | 0.059381 | 0.00034182 | 2.9842e-05 | -0.00050846 | 0.015259 | -7.6854e-05 | 0.065661 | 0.057935 | -0.0065454 | 0.0053789 | 0.0037406 | -0.036621 | 62.9654 | -59.285 | 63.208 | -59.1156 | -59.5001 | -59.4864 | -0.018311 | 62.915 | -59.2392 | 63.176 | -59.2621 | -59.3857 | -59.3353 | -0.045776 | -0.13733 | 0.10529 | 0.1236 | -0.24719 | -0.26093 | -0.20142 | -0.21515 | 0 | -0.18768 | 0.073242 | -0.022888 | -0.09613 | -0.14648 | -0.09613 | -0.14648 | 0.16937 | 122.493 | -0.022888 | 122.4152 | 122.2504 | 122.1542 | 122.2046 | 122.1542 | -122.3877 | -122.3419 | 122.4472 | 122.4152 | 59.2026 | 59.2209
204.3125 | 122.6624 | -59.2484 | 63.1485 | -0.027695 | 0.0039028 | 0.064016 | 0.061303 | -0.002649 | -0.0029608 | -0.0011493 | -0.054932 | 0.0016321 | 0.068011 | 0.063916 | -0.0037684 | 0.0070879 | -0.0024546 | 0.018311 | 63.0661 | -59.3124 | 63.2172 | -59.1385 | -59.4864 | -59.5001 | 0.036621 | 63.0203 | -59.2484 | 63.1622 | -59.2484 | -59.4177 | -59.3674 | -0.064087 | -0.082398 | 0.068664 | 0.10986 | -0.25177 | -0.23804 | -0.18768 | -0.17395 | 0 | -0.12817 | 0.013732 | 0 | -0.11902 | -0.16937 | -0.11902 | -0.16937 | 0.17395 | 122.5296 | 0 | 122.4106 | 122.3785 | 122.2687 | 122.3145 | 122.2687 | -122.4609 | -122.3969 | 122.4655 | 122.4106 | 59.2667 | 59.285
205.3125 | 122.6257 | -59.2438 | 63.1439 | -0.020065 | 0.0013394 | 0.063376 | 0.063653 | -0.0011536 | -0.0029608 | 0.00077334 | -0.067139 | 0.0029137 | 0.067798 | 0.068616 | -0.0037684 | 0.0051653 | 0.000109 | -0.004578 | 63.0432 | -59.3079 | 63.2217 | -59.1293 | -59.4727 | -59.4772 | 0.032043 | 63.002 | -59.2529 | 63.1714 | -59.2941 | -59.4223 | -59.3674 | -0.064087 | -0.10071 | 0.07782 | 0.11444 | -0.23346 | -0.22888 | -0.16937 | -0.16479 | -0.009156 | -0.14191 | 0.027466 | -0.050354 | -0.1236 | -0.17853 | -0.11444 | -0.16937 | 0.17853 | 122.5296 | -0.041198 | 122.4243 | 122.3511 | 122.2549 | 122.287 | 122.2458 | -122.4518 | -122.3969 | 122.4655 | 122.4152 | 59.2392 | 59.2758
206.3125 | 122.6578 | -59.2575 | 63.0981 | -0.035324 | 0.0011258 | 0.065512 | 0.061517 | 0.0014098 | 0.00024344 | 0.00034614 | 0.024414 | 0.0029137 | 0.068438 | 0.058362 | -0.0024866 | 0.0051653 | -0.0026682 | -0.027466 | 62.9883 | -59.3079 | 63.2172 | -59.1064 | -59.5001 | -59.4727 | -0.022888 | 62.9425 | -59.2712 | 63.1622 | -59.2667 | -59.3811 | -59.3491 | -0.050354 | -0.10986 | 0.11902 | 0.15106 | -0.21515 | -0.24262 | -0.16479 | -0.19226 | -0.013733 | -0.15564 | 0.064086 | -0.009156 | -0.091553 | -0.1236 | -0.07782 | -0.10986 | 0.20142 | 122.525 | 0.004577 | 122.4335 | 122.2961 | 122.2137 | 122.2458 | 122.2 | -122.406 | -122.3694 | 122.4747 | 122.4197 | 59.23 | 59.2346
207.3125 | 122.5342 | -59.2621 | 63.1714 | -0.073471 | 0.0043302 | 0.06423 | 0.06109 | -0.0013672 | -0.003388 | 0.00098694 | -0.073242 | 0.0027001 | 0.066516 | 0.066479 | 0.0017858 | 0.0073015 | -0.0013864 | -0.068665 | 63.0386 | -59.3353 | 63.1485 | -59.2484 | -59.6008 | -59.5871 | -0.16479 | 63.0066 | -59.2529 | 62.9562 | -59.0332 | -59.3216 | -59.4086 | -0.073242 | -0.13275 | -0.022888 | 0.013733 | -0.32501 | -0.33875 | -0.25177 | -0.2655 | 0.009155 | -0.1648 | -0.21515 | 0.22888 | -0.14648 | -0.059509 | -0.15564 | -0.068664 | 0.086975 | 122.4838 | 0.21973 | 122.2092 | 122.374 | 122.2595 | 122.3007 | 122.2687 | -122.5067 | -122.4243 | 122.4106 | 122.2183 | 59.1934 | 59.0973
208.3125 | 122.6761 | -59.23 | 63.1119 | -0.096359 | 0.000485 | 0.064016 | 0.057031 | -0.00093998 | -0.00232 | -0.0028583 | 0.05188 | -0.00029045 | 0.067584 | 0.059644 | -0.0031274 | 0.0047381 | -0.0054452 | -0.032043 | 62.9883 | -59.2804 | 63.2172 | -59.1156 | -59.4727 | -59.4543 | 0 | 62.97 | -59.2255 | 63.1989 | -59.2255 | -59.3491 | -59.317 | -0.050354 | -0.1236 | 0.10529 | 0.11444 | -0.2243 | -0.24261 | -0.17395 | -0.19226 | 0.004578 | -0.14191 | 0.086976 | 0.004578 | -0.086975 | -0.11902 | -0.091553 | -0.1236 | 0.1648 | 122.4976 | 0 | 122.4243 | 122.2687 | 122.1954 | 122.2183 | 122.2 | -122.3923 | -122.3373 | 122.4472 | 122.4289 | 59.198 | 59.23
209.3125 | 122.6486 | -59.2392 | 63.1302 | -0.020065 | 0.0019802 | 0.062948 | 0.059381 | -8.538e-05 | -0.0016792 | 0.00013254 | 0.012207 | 0.0020593 | 0.065234 | 0.063275 | -0.002273 | 0.0053789 | -0.005018 | -0.013733 | 63.0112 | -59.2758 | 63.208 | -59.1843 | -59.4589 | -59.5047 | -0.045776 | 62.9471 | -59.2163 | 63.1714 | -59.2758 | -59.4131 | -59.3536 | -0.036621 | -0.11902 | 0.07782 | 0.054932 | -0.2655 | -0.21973 | -0.22888 | -0.1831 | 0.022888 | -0.1831 | 0.041199 | -0.036621 | -0.11444 | -0.17395 | -0.13733 | -0.19684 | 0.091553 | 122.4838 | -0.059509 | 122.3877 | 122.287 | 122.1634 | 122.2504 | 122.1863 | -122.406 | -122.3465 | 122.4472 | 122.4106 | 59.2255 | 59.1934
210.3125 | 122.5845 | -59.2712 | 63.1348 | -0.073471 | 0.002194 | 0.065298 | 0.06344 | 0.0022644 | -0.0016792 | 0.00055974 | -0.07019 | 0.0041955 | 0.066089 | 0.061139 | -0.0029138 | 0.0058063 | -0.0039498 | -0.068665 | 63.0066 | -59.3445 | 63.121 | -59.2438 | -59.6237 | -59.5963 | -0.55389 | 62.8876 | -59.3262 | 63.1393 | -59.3399 | -59.5459 | -59.4269 | -0.073242 | -0.12817 | -0.013733 | 0.027466 | -0.32501 | -0.35248 | -0.25177 | -0.27924 | -0.054932 | -0.24719 | 0.004577 | -0.068665 | -0.15564 | -0.27466 | -0.10071 | -0.21973 | 0.10071 | 122.4655 | -0.013733 | 122.4655 | 122.3511 | 122.2137 | 122.2778 | 122.1588 | -122.4792 | -122.4609 | 122.3923 | 122.4106 | 59.2026 | 58.7173
211.3125 | 122.6028 | -59.2712 | 63.1256 | -0.065842 | 0.0019802 | 0.064657 | 0.06579 | 0.0011962 | -0.0025336 | 0.00098694 | -0.064087 | 0.0014185 | 0.068438 | 0.06413 | -0.0052638 | 0.0053789 | -0.0045908 | -0.068665 | 63.0386 | -59.3353 | 63.1256 | -59.2621 | -59.642 | -59.5963 | -0.55847 | 62.915 | -59.3308 | 63.1485 | -59.3903 | -59.5184 | -59.4269 | -0.064087 | -0.086975 | 0 | 0.009155 | -0.32501 | -0.37079 | -0.26093 | -0.3067 | -0.05951 | -0.21057 | 0.022889 | -0.11902 | -0.15564 | -0.24719 | -0.09613 | -0.18768 | 0.073242 | 122.4609 | -0.059509 | 122.4792 | 122.374 | 122.2458 | 122.3099 | 122.1863 | -122.4609 | -122.4564 | 122.3969 | 122.4197 | 59.2026 | 58.7128
212.3125 | 122.6074 | -59.2987 | 63.1256 | -0.10399 | 0.0017666 | 0.06423 | 0.061731 | 0.00055542 | -0.00232 | -0.0028583 | -0.045776 | 0.00077755 | 0.065234 | 0.061993 | -0.002273 | 0.0058063 | -0.000532 | -0.07782 | 63.0249 | -59.317 | 63.1256 | -59.2209 | -59.6054 | -59.5779 | -0.15564 | 62.9974 | -59.2667 | 63.1119 | -59.3628 | -59.4955 | -59.404 | -0.018311 | -0.10071 | 0 | 0.07782 | -0.27924 | -0.3067 | -0.26093 | -0.28839 | 0.032043 | -0.12817 | -0.013733 | -0.064087 | -0.10529 | -0.19684 | -0.13733 | -0.22888 | 0.096131 | 122.4426 | -0.09613 | 122.3785 | 122.3419 | 122.2641 | 122.3236 | 122.2961 | -122.4426 | -122.3923 | 122.4243 | 122.4106 | 59.2209 | 59.1431
213.3125 | 122.6028 | -59.2941 | 63.1165 | -0.096359 | 0.0026212 | 0.06423 | 0.062158 | 0.00012822 | -0.0038154 | -0.0017903 | -0.079346 | 0.0039819 | 0.066943 | 0.064557 | -0.003341 | 0.0062335 | -0.000532 | -0.086975 | 63.0157 | -59.3353 | 63.1302 | -59.2392 | -59.61 | -59.6054 | -0.48065 | 62.9517 | -59.2941 | 63.1485 | -59.3903 | -59.5093 | -59.3903 | -0.041199 | -0.10071 | 0.013733 | 0.054931 | -0.31128 | -0.31586 | -0.27008 | -0.27466 | 0 | -0.1648 | 0.032044 | -0.096131 | -0.096131 | -0.21515 | -0.096131 | -0.21515 | 0.09613 | 122.4655 | -0.096131 | 122.4426 | 122.3511 | 122.2458 | 122.3099 | 122.2458 | -122.4518 | -122.4106 | 122.4243 | 122.4426 | 59.2072 | 58.8135
214.3125 | 122.58 | -59.2621 | 63.1348 | -0.073471 | 0.0045438 | 0.064444 | 0.061731 | 0.0018372 | -0.0016792 | 0.00077334 | -0.054932 | 0.0033411 | 0.070361 | 0.060071 | -0.0029138 | 0.0049517 | -0.0003182 | -0.082397 | 63.0249 | -59.3628 | 63.1256 | -59.2438 | -59.6329 | -59.6191 | -0.52185 | 62.8967 | -59.317 | 63.1531 | -59.3674 | -59.5184 | -59.4131 | -0.10071 | -0.10986 | -0.009156 | 0.018311 | -0.35706 | -0.37079 | -0.25635 | -0.27008 | -0.054932 | -0.23804 | 0.01831 | -0.10529 | -0.15106 | -0.25635 | -0.09613 | -0.20142 | 0.11902 | 122.4884 | -0.050354 | 122.4701 | 122.3877 | 122.2137 | 122.287 | 122.1588 | -122.4976 | -122.4518 | 122.3877 | 122.4152 | 59.1797 | 58.7402
215.3125 | 122.6303 | -59.2026 | 63.1714 | -0.020065 | 0.0013394 | 0.06188 | 0.056817 | -0.005426 | -0.00039736 | 0.00055974 | 0.076294 | 0.0020593 | 0.066516 | 0.051739 | -0.0016322 | 0.0049517 | -0.0039498 | 0.022888 | 63.0203 | -59.285 | 63.2721 | -59.024 | -59.4086 | -59.4086 | 0.11444 | 62.9654 | -59.2072 | 63.2584 | -59.1614 | -59.2667 | -59.2621 | -0.082397 | -0.15106 | 0.10071 | 0.17853 | -0.20599 | -0.20599 | -0.1236 | -0.1236 | -0.004577 | -0.20599 | 0.086975 | 0.041199 | -0.059509 | -0.064087 | -0.054932 | -0.05951 | 0.26093 | 122.5571 | 0.045776 | 122.4655 | 122.3053 | 122.1725 | 122.2229 | 122.168 | -122.4564 | -122.3785 | 122.4747 | 122.4609 | 59.2255 | 59.317
216.3125 | 122.6624 | -59.2575 | 63.1119 | -0.042954 | 0.0041166 | 0.065512 | 0.06109 | 0.00076902 | 0.00067084 | 0.00013254 | -0.036621 | 0.0020593 | 0.067157 | 0.064343 | -0.0035548 | 0.0066607 | -0.0020272 | -0.086975 | 63.0295 | -59.3308 | 63.1668 | -59.198 | -59.5642 | -59.5367 | -0.09613 | 62.9745 | -59.2438 | 63.176 | -59.285 | -59.4177 | -59.3536 | -0.073243 | -0.082397 | 0.054932 | 0.059509 | -0.27924 | -0.3067 | -0.20599 | -0.23346 | 0.013733 | -0.13733 | 0.064087 | -0.027466 | -0.096131 | -0.16022 | -0.10986 | -0.17395 | 0.13275 | 122.4976 | -0.041199 | 122.4197 | 122.3602 | 122.2183 | 122.287 | 122.2321 | -122.4426 | -122.3557 | 122.4243 | 122.4335 | 59.1705 | 59.1614
217.3125 | 122.5891 | -59.2575 | 63.1165 | -0.012436 | 0.0026212 | 0.06658 | 0.061731 | -0.0022218 | -0.0021064 | -0.0015765 | -0.045776 | 0.0033411 | 0.064807 | 0.064984 | -0.002273 | 0.0081561 | -0.0013864 | -0.07782 | 63.002 | -59.317 | 63.121 | -59.2255 | -59.6054 | -59.5734 | -0.15564 | 62.9745 | -59.2712 | 63.1073 | -59.3674 | -59.491 | -59.4086 | -0.05951 | -0.11444 | 0.004578 | 0.032043 | -0.31586 | -0.3479 | -0.25635 | -0.28839 | -0.013733 | -0.14191 | -0.009155 | -0.10986 | -0.15106 | -0.23346 | -0.13733 | -0.21973 | 0.091553 | 122.4381 | -0.096131 | 122.3785 | 122.319 | 122.2458 | 122.2595 | 122.2321 | -122.4335 | -122.3877 | 122.3785 | 122.3648 | 59.1797 | 59.1019
218.3125 | 122.6395 | -59.2529 | 63.1027 | -0.08873 | 0.0013394 | 0.062948 | 0.05874 | -0.00072638 | -0.00061096 | -0.0034991 | 0.024414 | 0.0018457 | 0.067157 | 0.063702 | -0.0031274 | 0.0066607 | -0.0001046 | -0.041199 | 62.9654 | -59.2896 | 63.2355 | -59.111 | -59.5047 | -59.4772 | -0.036621 | 62.9425 | -59.2392 | 63.176 | -59.285 | -59.3903 | -59.3353 | -0.036621 | -0.13733 | 0.13275 | 0.14191 | -0.2243 | -0.25177 | -0.18768 | -0.21515 | 0.013733 | -0.16022 | 0.073242 | -0.032043 | -0.082397 | -0.13733 | -0.09613 | -0.15106 | 0.17853 | 122.525 | -0.045776 | 122.4152 | 122.2549 | 122.1817 | 122.2183 | 122.1954 | -122.3923 | -122.3419 | 122.4884 | 122.4289 | 59.2117 | 59.2163
219.3125 | 122.58 | -59.2804 | 63.1393 | -0.10399 | 0.002194 | 0.063803 | 0.062372 | 0.00098262 | -0.0031744 | -0.00029486 | -0.067139 | -0.00029045 | 0.067798 | 0.064343 | -0.0024866 | 0.0077289 | 0.0007498 | -0.068665 | 63.0157 | -59.3262 | 63.121 | -59.2346 | -59.6237 | -59.5779 | -0.14648 | 63.002 | -59.2987 | 63.0981 | -59.3719 | -59.5139 | -59.4269 | -0.045776 | -0.1236 | -0.01831 | 0.045777 | -0.29755 | -0.34332 | -0.25177 | -0.29755 | -0.01831 | -0.13733 | -0.041198 | -0.091552 | -0.14648 | -0.23346 | -0.12817 | -0.21515 | 0.091553 | 122.4472 | -0.073242 | 122.3969 | 122.3419 | 122.3007 | 122.2961 | 122.2824 | -122.4655 | -122.438 | 122.4014 | 122.3785 | 59.2117 | 59.1339
220.3125 | 122.6669 | -59.2758 | 63.1165 | -0.035324 | -0.0005832 | 0.063803 | 0.062372 | -0.0028626 | -0.00018376 | -0.00029486 | -0.042725 | 0.0016321 | 0.06502 | 0.068402 | -0.0014184 | 0.0055927 | 0.001177 | -0.073242 | 62.9883 | -59.3582 | 63.1348 | -59.1888 | -59.5917 | -59.5642 | -0.11902 | 62.9791 | -59.2804 | 63.1531 | -59.317 | -59.4452 | -59.3857 | -0.082397 | -0.12817 | 0.018311 | 0.086975 | -0.28839 | -0.31586 | -0.20599 | -0.23346 | -0.004578 | -0.13733 | 0.036621 | -0.041199 | -0.10986 | -0.16937 | -0.10528 | -0.16479 | 0.16937 | 122.493 | -0.036621 | 122.4335 | 122.3465 | 122.2595 | 122.2641 | 122.2549 | -122.4747 | -122.3969 | 122.4106 | 122.4289 | 59.2026 | 59.1568
221.3125 | 122.6624 | -59.2438 | 63.089 | -0.0048066 | 0.0017666 | 0.065939 | 0.060876 | -0.0011536 | -0.0025336 | -0.0034991 | 0.036621 | -0.0022131 | 0.066089 | 0.059857 | -0.0035548 | 0.0060199 | 0.0009634 | -0.07782 | 62.9791 | -59.2896 | 63.208 | -59.1293 | -59.491 | -59.4635 | 0.1831 | 62.9974 | -59.2346 | 63.1531 | -59.2667 | -59.3903 | -59.3765 | -0.045777 | -0.10986 | 0.11902 | 0.11444 | -0.21973 | -0.24719 | -0.17395 | -0.20142 | 0.009155 | -0.091552 | 0.064087 | -0.022889 | -0.13275 | -0.14648 | -0.14191 | -0.15564 | 0.16022 | 122.4976 | -0.032044 | 122.3877 | 122.2687 | 122.2321 | 122.2229 | 122.2412 | -122.3785 | -122.3236 | 122.4518 | 122.3969 | 59.166 | 59.4269
222.3125 | 122.5891 | -59.2896 | 63.1165 | -0.30998 | 0.002194 | 0.062735 | 0.063653 | 0.0018372 | -0.0018928 | -0.0022175 | -0.048828 | 0.0027001 | 0.06737 | 0.065411 | -0.003982 | 0.0087969 | -0.0065134 | 0.13275 | 62.9974 | -59.3262 | 63.1165 | -59.2346 | -59.5596 | -59.5871 | -0.15564 | 63.0112 | -59.2575 | 63.1119 | -59.3719 | -59.523 | -59.4498 | -0.036621 | -0.11902 | 0 | 0.054932 | -0.29755 | -0.27008 | -0.26093 | -0.23346 | 0.032044 | -0.10529 | -0.004578 | -0.082397 | -0.16022 | -0.23346 | -0.19226 | -0.2655 | 0.091553 | 122.4426 | -0.11444 | 122.3694 | 122.3236 | 122.2687 | 122.287 | 122.3007 | -122.4426 | -122.374 | 122.406 | 122.4014 | 59.4223 | 59.1339
223.3125 | 122.6028 | -59.2712 | 63.1165 | -0.050583 | 0.0024076 | 0.063376 | 0.06109 | -0.00051278 | 2.9842e-05 | -0.0013629 | -0.045776 | 0.0022729 | 0.066302 | 0.06413 | -0.003982 | 0.0064471 | -0.0037362 | -0.10071 | 63.0157 | -59.3445 | 63.1485 | -59.1934 | -59.5917 | -59.5642 | -0.13275 | 62.9791 | -59.2667 | 63.1348 | -59.3399 | -59.4772 | -59.3948 | -0.073242 | -0.10071 | 0.032044 | 0.07782 | -0.29297 | -0.32044 | -0.21973 | -0.24719 | 0.004577 | -0.13733 | 0.018311 | -0.068665 | -0.1236 | -0.20599 | -0.12817 | -0.21057 | 0.15106 | 122.493 | -0.073242 | 122.4014 | 122.3602 | 122.2458 | 122.287 | 122.2504 | -122.4609 | -122.3831 | 122.4197 | 122.406 | 59.1705 | 59.1385
224.3125 | 122.7539 | -59.2346 | 63.1393 | -0.012436 | 0.0009122 | 0.064016 | 0.060449 | -0.00051278 | -0.0048834 | -8.1264e-05 | 0.015259 | 0.00035035 | 0.067798 | 0.060071 | -0.0037684 | 0.0073015 | -0.0013864 | -0.054932 | 62.9929 | -59.2987 | 63.1989 | -59.1156 | -59.5093 | -59.4864 | -0.054932 | 62.9425 | -59.2346 | 63.1622 | -59.2712 | -59.3857 | -59.3216 | -0.064087 | -0.14648 | 0.05951 | 0.11902 | -0.25177 | -0.27466 | -0.18768 | -0.21057 | 0 | -0.19684 | 0.022888 | -0.036621 | -0.086975 | -0.15106 | -0.086975 | -0.15106 | 0.18311 | 122.4976 | -0.036621 | 122.3969 | 122.2916 | 122.1771 | 122.2275 | 122.1771 | -122.438 | -122.374 | 122.4335 | 122.3969 | 59.1797 | 59.1797
225.3125 | 122.58 | -59.2941 | 63.1348 | -0.050583 | 0.0024076 | 0.065085 | 0.061731 | 0.002478 | -0.0038154 | -0.00050846 | 0.085449 | 0.00035035 | 0.067584 | 0.066907 | -0.003341 | 0.0051653 | -0.0041636 | -0.073242 | 63.0524 | -59.3445 | 63.0936 | -59.1339 | -60.1318 | -59.8984 | -0.10529 | 63.0341 | -59.2667 | 63.1027 | -59.3811 | -59.5139 | -59.4223 | -0.050354 | -0.082398 | -0.041199 | 0.16022 | -0.60425 | -0.83771 | -0.55389 | -0.78735 | 0.027465 | -0.10071 | -0.032044 | -0.086976 | -0.12817 | -0.21973 | -0.15564 | -0.24719 | 0.21057 | 122.438 | -0.11444 | 122.3694 | 122.3969 | 122.3007 | 122.3465 | 122.3282 | -122.4792 | -122.4014 | 122.3877 | 122.3969 | 59.2209 | 59.1888
226.3125 | 122.5754 | -59.2804 | 63.1119 | -0.073471 | 0.0053982 | 0.06423 | 0.062799 | 0.0037598 | -0.0018928 | 0.0014141 | -0.067139 | 0.0014185 | 0.067584 | 0.072888 | -0.0014184 | 0.0055927 | -0.0024546 | -0.064087 | 63.0386 | -59.3399 | 63.1073 | -59.2712 | -59.6191 | -59.61 | -0.54016 | 62.9013 | -59.3124 | 63.1531 | -59.3857 | -59.5093 | -59.404 | -0.059509 | -0.073242 | -0.004577 | 0.009156 | -0.32959 | -0.33874 | -0.27008 | -0.27924 | -0.032043 | -0.21057 | 0.041199 | -0.10528 | -0.1236 | -0.22888 | -0.091553 | -0.19684 | 0.068665 | 122.4472 | -0.073242 | 122.4655 | 122.3785 | 122.2137 | 122.319 | 122.1817 | -122.4518 | -122.4243 | 122.3877 | 122.4335 | 59.2163 | 58.7402
227.3125 | 122.6669 | -59.2209 | 63.089 | -0.058212 | 0.0026212 | 0.062948 | 0.059381 | 0.0011962 | 2.9842e-05 | -8.1264e-05 | 0.033569 | -0.00029045 | 0.066302 | 0.055798 | -0.002273 | 0.0060199 | 0.0003226 | -0.013733 | 63.0157 | -59.3033 | 63.2309 | -59.1156 | -59.4818 | -59.4452 | 0.004578 | 62.9425 | -59.2163 | 63.208 | -59.2209 | -59.3262 | -59.2941 | -0.082398 | -0.073242 | 0.14191 | 0.10529 | -0.2243 | -0.26093 | -0.14191 | -0.17853 | 0.004577 | -0.14648 | 0.11902 | 0 | -0.073242 | -0.10529 | -0.077819 | -0.10986 | 0.18768 | 122.5342 | -0.004577 | 122.4243 | 122.319 | 122.1588 | 122.2366 | 122.1634 | -122.3923 | -122.3053 | 122.4518 | 122.4289 | 59.2072 | 59.2255
228.3125 | 122.5662 | -59.2575 | 63.1393 | -0.058212 | 0.0006986 | 0.064444 | 0.062158 | -8.538e-05 | -0.0016792 | 0.00034614 | -0.05188 | 0.0020593 | 0.066089 | 0.063702 | -0.00077757 | 0.0083697 | -0.0024546 | -0.059509 | 62.9974 | -59.3262 | 63.1165 | -59.2529 | -59.6146 | -59.5871 | -0.17853 | 63.0157 | -59.285 | 63.089 | -59.0515 | -59.4131 | -59.4589 | -0.068665 | -0.14191 | -0.022888 | 0.004577 | -0.32959 | -0.35706 | -0.26093 | -0.28839 | -0.027466 | -0.1236 | -0.050354 | 0.20599 | -0.20142 | -0.15564 | -0.17395 | -0.12817 | 0.073242 | 122.4426 | 0.23346 | 122.374 | 122.3236 | 122.3007 | 122.2549 | 122.2733 | -122.4655 | -122.4243 | 122.374 | 122.3465 | 59.198 | 59.079
229.3125 | 122.6807 | -59.2392 | 63.0844 | -0.096359 | 0.0045438 | 0.06658 | 0.062799 | 0.0039734 | -0.0010382 | 0.0014141 | 0.0030517 | 0.00099115 | 0.065448 | 0.062634 | -0.003982 | 0.0066607 | -0.0035226 | -0.022888 | 62.9654 | -59.2987 | 63.2446 | -59.0881 | -59.4955 | -59.4543 | -0.004578 | 62.9379 | -59.2255 | 63.2263 | -59.2255 | -59.3628 | -59.317 | -0.059509 | -0.11902 | 0.16022 | 0.15106 | -0.21515 | -0.25635 | -0.15564 | -0.19684 | 0.013733 | -0.14648 | 0.14191 | 0.013733 | -0.07782 | -0.1236 | -0.091553 | -0.13733 | 0.21057 | 122.5433 | 0 | 122.4518 | 122.2641 | 122.1634 | 122.2046 | 122.1771 | -122.3831 | -122.3099 | 122.4838 | 122.4655 | 59.2163 | 59.2346
230.3125 | 122.5891 | -59.2804 | 63.089 | -0.042954 | 0.0011258 | 0.063803 | 0.062158 | 0.00098262 | -0.0031744 | -0.0022175 | -0.054932 | 0.0022729 | 0.06737 | 0.062421 | -0.0037684 | 0.0075153 | -0.0016 | -0.07782 | 63.0341 | -59.3353 | 63.1165 | -59.2438 | -59.6146 | -59.5871 | -0.14648 | 63.0066 | -59.2438 | 63.1119 | -59.3582 | -59.4818 | -59.4177 | -0.054931 | -0.054931 | 0.027466 | 0.036622 | -0.3067 | -0.33417 | -0.25177 | -0.27924 | 0.036622 | -0.082397 | 0.022888 | -0.077819 | -0.13733 | -0.20142 | -0.17395 | -0.23804 | 0.091553 | 122.4518 | -0.11444 | 122.3557 | 122.3694 | 122.2504 | 122.3145 | 122.287 | -122.4243 | -122.3328 | 122.3969 | 122.3923 | 59.2026 | 59.1339
231.3125 | 122.6532 | -59.2484 | 63.1027 | -0.065842 | 0.0028348 | 0.064444 | 0.063226 | -8.538e-05 | -0.0029608 | -0.0015765 | -0.042725 | 0.0014185 | 0.066516 | 0.059644 | -0.003341 | 0.0064471 | -0.0039498 | -0.091553 | 62.9929 | -59.3353 | 63.1439 | -59.2072 | -59.5688 | -59.5459 | -0.10986 | 62.9745 | -59.2484 | 63.1622 | -59.2941 | -59.4131 | -59.3628 | -0.086975 | -0.10986 | 0.041199 | 0.041199 | -0.29755 | -0.32044 | -0.21057 | -0.23346 | 0 | -0.12817 | 0.059509 | -0.045776 | -0.11444 | -0.1648 | -0.11444 | -0.1648 | 0.12817 | 122.4792 | -0.045776 | 122.4106 | 122.3282 | 122.2229 | 122.2412 | 122.2229 | -122.438 | -122.3511 | 122.3923 | 122.4106 | 59.1568 | 59.1385
232.3125 | 122.731 | -59.2163 | 63.1165 | -0.050583 | 0.0036892 | 0.062735 | 0.057031 | 0.00076902 | -0.00039736 | -0.0011493 | 0.067139 | -0.0015723 | 0.065875 | 0.061566 | -0.002273 | 0.0043109 | 0.0003226 | 0.050354 | 63.0295 | -59.2529 | 63.2675 | -58.9279 | -59.4498 | -59.4452 | 0.07782 | 62.9562 | -59.2117 | 63.2584 | -59.166 | -59.2987 | -59.2941 | -0.036621 | -0.086975 | 0.15106 | 0.28839 | -0.22888 | -0.23346 | -0.19226 | -0.19684 | 0.004578 | -0.16022 | 0.14191 | 0.050354 | -0.077819 | -0.082397 | -0.082397 | -0.086975 | 0.32501 | 122.5204 | 0.045776 | 122.4701 | 122.2824 | 122.168 | 122.2458 | 122.1725 | -122.3694 | -122.3282 | 122.4838 | 122.4747 | 59.2667 | 59.2941
233.3125 | 122.5662 | -59.2621 | 63.1073 | -0.050583 | 0.0013394 | 0.064016 | 0.061517 | 0.00098262 | -0.00018376 | 0.00055974 | -0.07019 | 0.0014185 | 0.067584 | 0.062848 | -0.0031274 | 0.0038837 | 0.0022452 | -0.10071 | 63.0478 | -59.3445 | 63.121 | -59.2621 | -59.5963 | -59.5734 | -0.14191 | 62.9974 | -59.2667 | 63.1119 | -59.3674 | -59.491 | -59.3994 | -0.082397 | -0.059509 | 0.013733 | 0 | -0.31128 | -0.33417 | -0.22888 | -0.25177 | -0.004578 | -0.10986 | 0.004577 | -0.10529 | -0.13733 | -0.22888 | -0.13275 | -0.2243 | 0.082397 | 122.4655 | -0.10071 | 122.3785 | 122.3923 | 122.2641 | 122.3099 | 122.2595 | -122.4518 | -122.374 | 122.3831 | 122.374 | 59.1614 | 59.1202
234.3125 | 122.6761 | -59.2529 | 63.1027 | -0.081101 | 0.0019802 | 0.063376 | 0.059808 | -0.00093998 | -0.00232 | 0.00055974 | -0.024414 | 0.0018457 | 0.067157 | 0.060284 | -0.002273 | 0.0062335 | -0.0039498 | -0.032043 | 62.9562 | -59.2987 | 63.2217 | -59.0744 | -59.4955 | -59.4543 | -0.022888 | 62.9425 | -59.2621 | 63.1714 | -59.2667 | -59.3719 | -59.3399 | -0.045776 | -0.14648 | 0.11902 | 0.17853 | -0.20142 | -0.24261 | -0.15564 | -0.19684 | -0.009155 | -0.16022 | 0.068665 | -0.013733 | -0.086975 | -0.11902 | -0.07782 | -0.10986 | 0.2243 | 122.5204 | -0.004578 | 122.4335 | 122.2549 | 122.2046 | 122.2092 | 122.1954 | -122.4014 | -122.3648 | 122.4747 | 122.4243 | 59.2209 | 59.23
235.3125 | 122.7676 | -59.2804 | 63.0936 | -0.10399 | 0.0043302 | 0.064444 | 0.061517 | 0.0061096 | -0.0012518 | 0.00077334 | -0.042725 | 0.0012047 | 0.068011 | 0.054944 | -0.0046228 | 0.0066607 | -0.0013864 | -0.050354 | 62.9791 | -59.3353 | 63.2355 | -59.1248 | -59.5322 | -59.4864 | -0.041199 | 62.9242 | -59.2529 | 63.2034 | -59.2163 | -59.642 | -59.4315 | -0.054931 | -0.11444 | 0.14191 | 0.15564 | -0.20599 | -0.25177 | -0.15106 | -0.19684 | 0.027466 | -0.16937 | 0.10986 | 0.064087 | -0.15106 | -0.36163 | -0.17853 | -0.3891 | 0.21057 | 122.5708 | 0.036621 | 122.4564 | 122.3145 | 122.1771 | 122.2595 | 122.2046 | -122.4289 | -122.3465 | 122.5159 | 122.4838 | 59.23 | 59.2392
236.3125 | 122.6898 | -59.2484 | 63.0798 | -0.042954 | 0.0024076 | 0.067434 | 0.061517 | -0.003717 | -0.0018928 | 0.0018413 | -8.6e-08 | 0.0024865 | 0.06737 | 0.062634 | -0.005691 | 0.0062335 | -0.0039498 | -0.013733 | 62.9791 | -59.3124 | 63.2492 | -59.079 | -59.5139 | -59.4727 | 0 | 62.915 | -59.2529 | 63.2217 | -59.2484 | -59.3491 | -59.3124 | -0.064087 | -0.10071 | 0.16937 | 0.16937 | -0.2243 | -0.2655 | -0.16022 | -0.20142 | -0.004578 | -0.16479 | 0.14191 | 0 | -0.064087 | -0.10071 | -0.059509 | -0.09613 | 0.23346 | 122.5616 | 0.004578 | 122.4747 | 122.2916 | 122.168 | 122.2275 | 122.1634 | -122.3923 | -122.3328 | 122.4976 | 122.4701 | 59.2346 | 59.2484
237.3125 | 122.6532 | -59.2484 | 63.1027 | -0.10399 | 0.0013394 | 0.063589 | 0.059381 | 0.00098262 | -0.0014654 | -0.0020039 | 0.012207 | 0.0014185 | 0.067157 | 0.059644 | -0.0027002 | 0.0049517 | 0.0016044 | -0.032043 | 62.9562 | -59.3033 | 63.2263 | -59.0744 | -59.4864 | -59.4635 | -0.022888 | 62.9608 | -59.2392 | 63.1851 | -59.2575 | -59.3536 | -59.3216 | -0.054932 | -0.14648 | 0.1236 | 0.17395 | -0.21515 | -0.23804 | -0.16022 | -0.18311 | 0.009155 | -0.14191 | 0.082398 | -0.009155 | -0.073242 | -0.10529 | -0.082397 | -0.11444 | 0.22888 | 122.5296 | -0.01831 | 122.4243 | 122.2595 | 122.2 | 122.2046 | 122.2092 | -122.406 | -122.3419 | 122.4747 | 122.4335 | 59.2163 | 59.2255
238.3125 | 122.6257 | -59.2621 | 63.1165 | -0.081101 | 0.0030484 | 0.062521 | 0.062372 | 0.0033324 | -0.0029608 | 0.00013254 | -0.057983 | 0.0012047 | 0.064166 | 0.063916 | -0.0024866 | 0.0058063 | -0.0022408 | -0.086975 | 63.0249 | -59.3353 | 63.1302 | -59.2072 | -59.5871 | -59.5596 | -0.13733 | 63.002 | -59.2621 | 63.1393 | -59.3216 | -59.4818 | -59.404 | -0.073242 | -0.091553 | 0.013733 | 0.054932 | -0.29755 | -0.32501 | -0.2243 | -0.25177 | 0 | -0.11444 | 0.022888 | -0.059509 | -0.14191 | -0.21973 | -0.14191 | -0.21973 | 0.12817 | 122.4655 | -0.059509 | 122.4014 | 122.3602 | 122.2641 | 122.287 | 122.2641 | -122.4518 | -122.3785 | 122.3923 | 122.4014 | 59.1751 | 59.1248
239.3125 | 122.699 | -59.2163 | 63.1027 | -0.020065 | 0.0019802 | 0.063376 | 0.058954 | 0.00012822 | -0.0016792 | -0.0022175 | 0.027466 | 0.00013675 | 0.067798 | 0.064984 | -0.0037684 | 0.0032427 | -0.0018136 | 0.054932 | 62.9974 | -59.2575 | 63.2858 | -59.0195 | -59.3903 | -59.3765 | 0.16937 | 62.9791 | -59.1522 | 63.3087 | -59.2575 | -59.2758 | -59.2255 | -0.041198 | -0.10529 | 0.18311 | 0.19684 | -0.16022 | -0.17395 | -0.11902 | -0.13275 | 0.064087 | -0.1236 | 0.20599 | -0.041198 | -0.009155 | -0.059509 | -0.073242 | -0.1236 | 0.23804 | 122.5433 | -0.10528 | 122.4609 | 122.2549 | 122.1313 | 122.2137 | 122.1954 | -122.3602 | -122.2549 | 122.5021 | 122.525 | 59.2712 | 59.3857
240.3125 | 122.6852 | -59.2346 | 63.1165 | -0.027695 | 0.0009122 | 0.067221 | 0.062158 | -0.002008 | -0.0010382 | 0.0026959 | -0.05188 | 0.00035035 | 0.066729 | 0.060498 | -0.0044092 | 0.0060199 | -0.0016 | -0.059509 | 63.0066 | -59.3445 | 63.1714 | -59.1568 | -59.5413 | -59.5093 | -0.068665 | 62.97 | -59.2438 | 63.1897 | -59.285 | -59.3857 | -59.3079 | -0.10986 | -0.10986 | 0.054932 | 0.07782 | -0.27466 | -0.3067 | -0.16479 | -0.19684 | -0.009155 | -0.14648 | 0.073242 | -0.050354 | -0.073242 | -0.15106 | -0.064087 | -0.14191 | 0.18768 | 122.5159 | -0.041199 | 122.4335 | 122.3511 | 122.2137 | 122.2412 | 122.2046 | -122.4609 | -122.3602 | 122.406 | 122.4243 | 59.1751 | 59.166
241.3125 | 122.6532 | -59.2529 | 63.0615 | -0.012436 | 0.0019802 | 0.062948 | 0.061944 | 0.0016236 | -0.0010382 | -0.00029486 | -0.054932 | 0.0024865 | 0.066516 | 0.067761 | -0.0052638 | 0.0058063 | 0.001818 | -0.07782 | 63.002 | -59.3491 | 63.176 | -59.1797 | -59.5688 | -59.5322 | -0.086975 | 62.9562 | -59.2667 | 63.2034 | -59.2621 | -59.3994 | -59.3308 | -0.09613 | -0.059509 | 0.11444 | 0.073243 | -0.27924 | -0.31586 | -0.18311 | -0.21973 | -0.013733 | -0.10529 | 0.14191 | -0.009155 | -0.07782 | -0.14648 | -0.064087 | -0.13275 | 0.16937 | 122.525 | 0.004578 | 122.4701 | 122.3511 | 122.2229 | 122.2549 | 122.2092 | -122.4106 | -122.3282 | 122.4289 | 122.4564 | 59.1751 | 59.166
242.3125 | 122.6715 | -59.2438 | 63.0844 | -0.14214 | 0.0051846 | 0.065725 | 0.060663 | -0.0028626 | -0.0010382 | 0.0037639 | 0.0091553 | 0.0031273 | 0.064166 | 0.056653 | -0.0027002 | 0.0079425 | -0.0016 | -0.009155 | 62.9791 | -59.3033 | 63.2446 | -59.0744 | -59.4864 | -59.4635 | -0.004578 | 62.9471 | -59.23 | 63.2309 | -59.2392 | -59.3628 | -59.3124 | -0.05951 | -0.10529 | 0.16022 | 0.16937 | -0.21973 | -0.24262 | -0.16022 | -0.18311 | 0.013732 | -0.13733 | 0.14648 | 0.004577 | -0.068665 | -0.11902 | -0.082397 | -0.13275 | 0.22888 | 122.5479 | -0.009155 | 122.4609 | 122.2824 | 122.1771 | 122.2229 | 122.1909 | -122.3877 | -122.3145 | 122.4884 | 122.4747 | 59.2346 | 59.2392
243.3125 | 122.6715 | -59.2117 | 63.1027 | -0.027695 | -0.0010104 | 0.062308 | 0.061944 | 0.0031188 | -0.0038154 | 0.0012005 | -0.024414 | 0.00077755 | 0.066516 | 0.068616 | -0.0031274 | 0.0064471 | -0.0035226 | -0.032043 | 62.9883 | -59.3262 | 63.2034 | -59.1064 | -59.4818 | -59.4681 | -0.041199 | 62.9517 | -59.2255 | 63.0981 | -59.3765 | -59.1385 | -59.079 | -0.11444 | -0.11444 | 0.10071 | 0.10529 | -0.25635 | -0.27008 | -0.14191 | -0.15564 | -0.013733 | -0.15106 | -0.004577 | -0.16479 | 0.13275 | 0.073242 | 0.14649 | 0.086975 | 0.21973 | 122.5296 | -0.15106 | 122.3236 | 122.3145 | 122.1771 | 122.2 | 122.1634 | -122.4289 | -122.3282 | 122.4152 | 122.3099 | 59.1797 | 59.1705
244.3125 | 122.6898 | -59.2392 | 63.1165 | -0.050583 | 0.0039028 | 0.064016 | 0.060876 | -0.0015808 | -0.0031744 | -0.00029486 | 0.027466 | 0.00099115 | 0.065875 | 0.057935 | -0.002273 | 0.0062335 | -0.0024546 | 0 | 63.0066 | -59.2987 | 63.2538 | -59.0881 | -59.4452 | -59.4177 | 0.027466 | 62.97 | -59.2117 | 63.2172 | -59.2026 | -59.317 | -59.2896 | -0.059509 | -0.10986 | 0.13733 | 0.15106 | -0.17853 | -0.20599 | -0.11902 | -0.14648 | 0.027466 | -0.14648 | 0.10071 | 0.036621 | -0.050354 | -0.07782 | -0.07782 | -0.10529 | 0.21057 | 122.5525 | 0.009155 | 122.4289 | 122.3053 | 122.1817 | 122.2458 | 122.2092 | -122.4152 | -122.3282 | 122.493 | 122.4564 | 59.2392 | 59.2667
245.3125 | 122.6028 | -59.2667 | 63.121 | -0.035324 | 0.0006986 | 0.063376 | 0.062799 | 0.0061096 | -0.0016792 | -0.0017903 | -0.076294 | 0.0012047 | 0.068866 | 0.063916 | -0.003341 | 0.0062335 | -0.005018 | -0.082397 | 62.9974 | -59.3536 | 63.1119 | -59.23 | -59.5917 | -59.5642 | -0.13733 | 62.9654 | -59.2667 | 63.1119 | -59.3353 | -59.4818 | -59.3857 | -0.086975 | -0.1236 | -0.009156 | 0.036621 | -0.29755 | -0.32501 | -0.21057 | -0.23804 | 0 | -0.15564 | -0.009156 | -0.068664 | -0.11902 | -0.21515 | -0.11902 | -0.21515 | 0.1236 | 122.4655 | -0.068664 | 122.3785 | 122.3511 | 122.2321 | 122.2641 | 122.2321 | -122.4747 | -122.3877 | 122.3785 | 122.3785 | 59.1843 | 59.1293
246.3125 | 122.5754 | -59.2896 | 63.1165 | -0.035324 | 0.0043302 | 0.063376 | 0.062372 | -8.538e-05 | -0.0014654 | -0.0052081 | -0.057983 | 0.0027001 | 0.065234 | 0.063916 | -0.0037684 | 0.0077289 | -0.0062998 | -0.086975 | 63.0066 | -59.3536 | 63.1119 | -59.2255 | -59.5917 | -59.5825 | -0.15106 | 62.9791 | -59.2896 | 63.1119 | -59.3536 | -59.491 | -59.404 | -0.064087 | -0.10986 | -0.004578 | 0.064087 | -0.29297 | -0.30212 | -0.22888 | -0.23804 | 0 | -0.13733 | -0.004578 | -0.064087 | -0.11444 | -0.20142 | -0.11444 | -0.20142 | 0.12817 | 122.4655 | -0.064087 | 122.4014 | 122.3602 | 122.2687 | 122.2961 | 122.2687 | -122.4701 | -122.406 | 122.4014 | 122.4014 | 59.2026 | 59.1385
247.3125 | 122.6166 | -59.2529 | 63.0798 | -0.042954 | 0.0036892 | 0.064016 | 0.058954 | -0.002008 | -0.003388 | -0.0028583 | 0.054932 | -0.00093145 | 0.066943 | 0.064984 | -0.00013677 | 0.0051653 | 0.001177 | -0.064087 | 62.9929 | -59.2896 | 63.1897 | -59.1339 | -59.4955 | -59.4818 | 0.15106 | 63.002 | -59.2346 | 63.1714 | -59.285 | -59.3994 | -59.3765 | -0.036621 | -0.086975 | 0.10986 | 0.11902 | -0.22888 | -0.24261 | -0.19226 | -0.20599 | 0.018311 | -0.07782 | 0.091553 | -0.032043 | -0.1236 | -0.14648 | -0.14191 | -0.16479 | 0.15564 | 122.4792 | -0.050354 | 122.406 | 122.2824 | 122.2366 | 122.2458 | 122.2549 | -122.3694 | -122.3145 | 122.4426 | 122.4243 | 59.1888 | 59.404
248.3125 | 122.6761 | -59.2438 | 63.089 | 0.10963 | 0.0034756 | 0.065939 | 0.061944 | 0.0033324 | -0.0021064 | -0.0030719 | -0.024414 | 0.0018457 | 0.065234 | 0.063275 | -0.0029138 | 0.0087969 | 0.0005362 | -0.032043 | 62.97 | -59.3079 | 63.2492 | -59.0836 | -59.4818 | -59.4315 | -0.036621 | 62.9471 | -59.2438 | 63.2172 | -59.2438 | -59.3628 | -59.285 | -0.064087 | -0.11902 | 0.16022 | 0.16022 | -0.18768 | -0.23804 | -0.1236 | -0.17395 | 0 | -0.14191 | 0.12817 | 0 | -0.041199 | -0.11902 | -0.041199 | -0.11902 | 0.2243 | 122.5571 | 0 | 122.4609 | 122.2778 | 122.1909 | 122.2137 | 122.1909 | -122.3969 | -122.3328 | 122.493 | 122.4609 | 59.2117 | 59.2072
249.3125 | 122.6898 | -59.2209 | 63.1256 | -0.027695 | 0.002194 | 0.062735 | 0.061303 | -0.0013672 | -0.003388 | -0.0020039 | 0.021362 | 0.0012047 | 0.065448 | 0.060712 | -0.006759 | 0.0064471 | 0.0007498 | 0.013733 | 63.0112 | -59.2667 | 63.295 | -59.0195 | -59.4086 | -59.3857 | 0.12817 | 62.9883 | -59.2163 | 63.2263 | -59.1751 | -59.3033 | -59.2621 | -0.045777 | -0.11444 | 0.16937 | 0.20142 | -0.16479 | -0.18768 | -0.11902 | -0.14191 | 0.004577 | -0.13733 | 0.10071 | 0.045776 | -0.041199 | -0.082398 | -0.045776 | -0.086975 | 0.24719 | 122.5616 | 0.041199 | 122.4426 | 122.2778 | 122.2046 | 122.2321 | 122.2092 | -122.3923 | -122.3419 | 122.5159 | 122.4472 | 59.2346 | 59.3491
250.3125 | 122.58 | -59.2804 | 63.1027 | -0.035324 | 0.0017666 | 0.062948 | 0.064935 | 0.0026916 | -0.0031744 | 0.0018413 | -0.10681 | 0.00056395 | 0.065875 | 0.065625 | -0.0046228 | 0.0070879 | 0.0005362 | -0.07782 | 63.0112 | -59.3719 | 63.1485 | -59.23 | -59.5963 | -59.5734 | -0.14191 | 62.9883 | -59.2712 | 63.1027 | -59.3536 | -59.491 | -59.404 | -0.091552 | -0.091553 | 0.045777 | 0.050354 | -0.29297 | -0.31586 | -0.20142 | -0.2243 | 0.009156 | -0.11444 | 0 | -0.073242 | -0.1236 | -0.21057 | -0.13275 | -0.21973 | 0.14191 | 122.5204 | -0.082398 | 122.374 | 122.3831 | 122.2595 | 122.2916 | 122.2687 | -122.4747 | -122.374 | 122.4289 | 122.3831 | 59.2026 | 59.1385
251.3125 | 122.6166 | -59.2758 | 63.0798 | -0.050583 | 0.0030484 | 0.063376 | 0.062158 | 0.0067504 | -0.003388 | -0.0015765 | -0.057983 | 0.0024865 | 0.06502 | 0.066693 | -0.0027002 | 0.0070879 | -0.0011728 | -0.086975 | 63.0112 | -59.3353 | 63.1348 | -59.1934 | -59.6008 | -59.5551 | -0.12817 | 62.9745 | -59.285 | 63.1393 | -59.3216 | -59.4406 | -59.3719 | -0.059509 | -0.068665 | 0.054932 | 0.082398 | -0.27924 | -0.32501 | -0.21973 | -0.2655 | -0.009155 | -0.10529 | 0.059509 | -0.045776 | -0.09613 | -0.16479 | -0.086975 | -0.15564 | 0.14191 | 122.4701 | -0.036621 | 122.4243 | 122.3465 | 122.2595 | 122.287 | 122.2504 | -122.4152 | -122.3648 | 122.4106 | 122.4152 | 59.1888 | 59.1476
252.3125 | 122.6807 | -59.2667 | 63.1027 | -0.027695 | 0.0013394 | 0.062094 | 0.058313 | -0.002008 | -0.0016792 | 0.00034614 | 0.021362 | 0.00099115 | 0.066516 | 0.058148 | -0.0046228 | 0.0038837 | -0.0007456 | -0.050354 | 62.9974 | -59.3079 | 63.1989 | -59.1293 | -59.491 | -59.4681 | -0.032043 | 62.9608 | -59.2346 | 63.1851 | -59.2346 | -59.3765 | -59.317 | -0.041198 | -0.10529 | 0.096131 | 0.13733 | -0.20142 | -0.2243 | -0.16022 | -0.18311 | 0.032044 | -0.14191 | 0.082398 | 0.032044 | -0.050354 | -0.10986 | -0.082398 | -0.14191 | 0.17853 | 122.5067 | 0 | 122.4197 | 122.3053 | 122.1954 | 122.2641 | 122.2275 | -122.4106 | -122.3373 | 122.4655 | 122.4518 | 59.2163 | 59.2346
253.3125 | 122.58 | -59.2438 | 63.1302 | -0.073471 | 0.0026212 | 0.063589 | 0.064721 | 0.00012822 | -0.0055244 | -0.0022175 | -0.082397 | 0.00035035 | 0.065234 | 0.069257 | -0.0031274 | 0.0062335 | -0.0009592 | -0.027466 | 63.0569 | -59.3445 | 63.1714 | -59.1522 | -59.5459 | -59.5505 | -0.07782 | 62.9837 | -59.2575 | 63.1302 | -59.3445 | -59.4864 | -59.3948 | -0.10071 | -0.073242 | 0.041199 | 0.091552 | -0.3067 | -0.30212 | -0.20599 | -0.20142 | -0.013733 | -0.14648 | 0 | -0.10071 | -0.15106 | -0.24262 | -0.13733 | -0.22888 | 0.19226 | 122.5159 | -0.086975 | 122.3877 | 122.4014 | 122.2412 | 122.3007 | 122.2275 | -122.4747 | -122.3877 | 122.4152 | 122.374 | 59.2163 | 59.166
254.3125 | 122.6807 | -59.2209 | 63.1119 | -0.035324 | 0.0043302 | 0.06423 | 0.058954 | 0.0011962 | -0.0014654 | -0.0015765 | 0.021362 | 0.0027001 | 0.066729 | 0.061139 | -0.0024866 | 0.0066607 | -0.0073678 | -0.009155 | 62.9974 | -59.2667 | 63.2126 | -59.1019 | -59.4635 | -59.4498 | 0.004578 | 62.9837 | -59.2392 | 63.208 | -59.2209 | -59.3308 | -59.2941 | -0.045777 | -0.11444 | 0.10071 | 0.11902 | -0.22888 | -0.24262 | -0.1831 | -0.19684 | -0.018311 | -0.12817 | 0.096131 | 0 | -0.073242 | -0.10986 | -0.054931 | -0.091553 | 0.16479 | 122.4792 | 0.018311 | 122.4472 | 122.2641 | 122.2229 | 122.2183 | 122.2046 | -122.3785 | -122.3511 | 122.4335 | 122.4289 | 59.2117 | 59.2255
255.3125 | 122.5754 | -59.2896 | 63.1439 | 0.063858 | 0.001553 | 0.065939 | 0.061731 | 0.00034182 | -0.0031744 | -0.00029486 | -0.10071 | 0.0022729 | 0.067584 | 0.069043 | -0.0031274 | 0.0060199 | -0.0022408 | -0.14191 | 63.0157 | -59.3353 | 63.1165 | -59.2484 | -59.5963 | -59.5596 | -0.14648 | 62.9974 | -59.2667 | 63.1165 | -59.3674 | -59.5001 | -59.3857 | -0.045776 | -0.12817 | -0.027466 | 0.041199 | -0.27008 | -0.3067 | -0.2243 | -0.26093 | 0.022888 | -0.14648 | -0.027466 | -0.07782 | -0.09613 | -0.21057 | -0.11902 | -0.23346 | 0.086975 | 122.4518 | -0.10071 | 122.3831 | 122.3511 | 122.2641 | 122.3053 | 122.287 | -122.4792 | -122.4106 | 122.406 | 122.406 | 59.1476 | 59.1431
256.3125 | 122.6761 | -59.2346 | 63.0661 | -0.31761 | 0.0047574 | 0.065512 | 0.059381 | -0.00029898 | -0.0029608 | 0.0016277 | -0.012207 | -0.00071785 | 0.066089 | 0.062421 | -0.0031274 | 0.0062335 | -0.0056588 | 0.041199 | 62.9425 | -59.3124 | 63.2355 | -59.079 | -59.4452 | -59.4452 | -0.013733 | 62.9196 | -59.23 | 63.2172 | -59.2209 | -59.3536 | -59.3216 | -0.07782 | -0.1236 | 0.16937 | 0.15564 | -0.21057 | -0.21057 | -0.13275 | -0.13275 | 0.004577 | -0.14648 | 0.15106 | 0.013733 | -0.086975 | -0.11902 | -0.091552 | -0.1236 | 0.23346 | 122.5479 | 0.009156 | 122.4472 | 122.2549 | 122.1497 | 122.1771 | 122.1542 | -122.3785 | -122.2961 | 122.4701 | 122.4518 | 59.2758 | 59.2209
257.3125 | 122.6807 | -59.2117 | 63.1119 | -0.020065 | 0.0013394 | 0.061667 | 0.058313 | 0.00012822 | -0.003388 | -0.00050846 | 0.024414 | -0.00029045 | 0.067157 | 0.062421 | -0.0035548 | 0.0070879 | -0.0037362 | -0.022888 | 63.0432 | -59.2758 | 63.2172 | -59.1019 | -59.4727 | -59.4406 | 0.004578 | 62.9608 | -59.2346 | 63.2126 | -59.2163 | -59.3308 | -59.285 | -0.064087 | -0.068664 | 0.10529 | 0.10986 | -0.22888 | -0.26093 | -0.16479 | -0.19684 | -0.022888 | -0.15106 | 0.10071 | -0.004578 | -0.073242 | -0.11902 | -0.050354 | -0.096131 | 0.17395 | 122.493 | 0.01831 | 122.4472 | 122.319 | 122.1954 | 122.2549 | 122.1725 | -122.3877 | -122.3465 | 122.4289 | 122.4243 | 59.1888 | 59.2163
258.3125 | 122.4243 | -59.3262 | 63.0615 | -0.065842 | 0.0028348 | 0.064657 | 0.063867 | 0.0037598 | -0.0029608 | -0.00029486 | -0.10071 | 0.0020593 | 0.066089 | 0.066693 | -0.0029138 | 0.0077289 | -0.0045908 | -0.054932 | 63.0112 | -59.3308 | 63.1302 | -59.2209 | -59.6191 | -59.5917 | -0.14648 | 62.9883 | -59.2804 | 63.0753 | -59.404 | -59.5276 | -59.436 | -0.004578 | -0.050354 | 0.068665 | 0.10529 | -0.2655 | -0.29297 | -0.26093 | -0.28839 | 0.045776 | -0.073242 | 0.013733 | -0.07782 | -0.10986 | -0.20142 | -0.15564 | -0.24719 | 0.10986 | 122.4609 | -0.1236 | 122.3557 | 122.3419 | 122.2687 | 122.3373 | 122.3145 | -122.3923 | -122.3419 | 122.4564 | 122.4014 | 59.2712 | 59.1797
259.3125 | 122.6715 | -59.2667 | 63.0981 | -0.065842 | 0.0030484 | 0.062948 | 0.060663 | -0.0024354 | -0.00082456 | -0.0028583 | 0.024414 | 0.00056395 | 0.064807 | 0.057935 | -0.0035548 | 0.0038837 | -0.0011728 | -0.064087 | 62.9974 | -59.3216 | 63.1897 | -59.1385 | -59.491 | -59.4543 | -0.064087 | 62.9654 | -59.2392 | 63.3224 | -59.4406 | -59.4452 | -59.3308 | -0.054931 | -0.10071 | 0.091552 | 0.12817 | -0.18768 | -0.2243 | -0.13275 | -0.16937 | 0.027466 | -0.13275 | 0.2243 | -0.17395 | -0.064087 | -0.17853 | -0.091553 | -0.20599 | 0.1831 | 122.5113 | -0.20142 | 122.5616 | 122.319 | 122.2046 | 122.2641 | 122.2321 | -122.4197 | -122.3373 | 122.4564 | 122.5891 | 59.2026 | 59.2026
260.3125 | 122.5479 | -59.2758 | 63.1256 | -0.050583 | 0.0030484 | 0.06423 | 0.063012 | -0.00072638 | -0.005097 | 0.00013254 | -0.1709 | 0.00099115 | 0.064807 | 0.067975 | -0.003982 | 0.0064471 | -0.0013864 | -0.082397 | 63.0386 | -59.3491 | 63.1119 | -59.2484 | -59.6329 | -59.8846 | 0.18768 | 63.0295 | -59.2484 | 63.1027 | -59.3445 | -59.4864 | -59.404 | -0.073242 | -0.086975 | -0.013733 | 0.027466 | -0.60883 | -0.35706 | -0.53558 | -0.28381 | 0.027466 | -0.09613 | -0.022888 | -0.068664 | -0.12817 | -0.21057 | -0.15564 | -0.23804 | 0.10071 | 122.4609 | -0.09613 | 122.3511 | 122.3877 | 122.2778 | 122.3145 | 122.3053 | -122.4747 | -122.374 | 122.3877 | 122.3785 | 59.1934 | 59.4635
261.3125 | 122.5616 | -59.2712 | 63.1256 | -0.058212 | 0.0028348 | 0.063376 | 0.064081 | -0.0013672 | -0.0031744 | 0.0029095 | -0.085449 | 0.0041955 | 0.068225 | 0.061352 | -0.0029138 | 0.0070879 | 0.0009634 | -0.082397 | 63.0112 | -59.3399 | 63.1165 | -59.2209 | -59.5825 | -59.5734 | -0.15106 | 63.002 | -59.2667 | 63.1119 | -59.3491 | -59.5047 | -59.404 | -0.068665 | -0.11444 | -0.009155 | 0.050354 | -0.30212 | -0.31128 | -0.23346 | -0.24262 | 0.004577 | -0.1236 | -0.013733 | -0.07782 | -0.13275 | -0.23346 | -0.13733 | -0.23804 | 0.11902 | 122.4564 | -0.082397 | 122.3785 | 122.3511 | 122.2687 | 122.2824 | 122.2733 | -122.4655 | -122.3923 | 122.3877 | 122.3831 | 59.1888 | 59.1202
262.3125 | 122.6532 | -59.2392 | 63.0981 | -0.073471 | 0.0039028 | 0.065725 | 0.058526 | -0.00029898 | -0.003388 | -0.0028583 | 0.030518 | 0.0024865 | 0.066089 | 0.059857 | -0.0037684 | 0.0060199 | -0.0035226 | -0.027466 | 63.0386 | -59.3033 | 63.208 | -59.111 | -59.4727 | -59.4681 | -0.009155 | 62.9517 | -59.2209 | 63.2034 | -59.23 | -59.3491 | -59.3079 | -0.064087 | -0.05951 | 0.10986 | 0.12817 | -0.22888 | -0.23346 | -0.1648 | -0.16937 | 0.018311 | -0.14649 | 0.10528 | 0.009155 | -0.068664 | -0.10986 | -0.086975 | -0.12817 | 0.19226 | 122.5113 | -0.009156 | 122.4243 | 122.3419 | 122.1725 | 122.2778 | 122.1909 | -122.4014 | -122.319 | 122.4472 | 122.4426 | 59.2117 | 59.23
263.3125 | 122.58 | -59.2804 | 63.1302 | -0.035324 | 0.002194 | 0.065725 | 0.061944 | -0.0011536 | -0.0016792 | -0.00050846 | -0.085449 | 0.0018457 | 0.066516 | 0.060925 | -0.003982 | 0.0053789 | 0.0020316 | -0.041199 | 63.0249 | -59.3491 | 63.1622 | -59.198 | -59.5734 | -59.5642 | -0.11444 | 62.9837 | -59.2804 | 63.1073 | -59.3857 | -59.5047 | -59.4131 | -0.068664 | -0.10529 | 0.032043 | 0.082398 | -0.28381 | -0.29297 | -0.21515 | -0.2243 | 0 | -0.14648 | -0.022888 | -0.10528 | -0.13275 | -0.2243 | -0.13275 | -0.2243 | 0.15106 | 122.5113 | -0.10528 | 122.3877 | 122.374 | 122.2641 | 122.3053 | 122.2641 | -122.4792 | -122.4106 | 122.4426 | 122.3877 | 59.2392 | 59.166
264.3125 | 122.6624 | -59.2346 | 63.1256 | -0.0048066 | 0.002194 | 0.065725 | 0.059808 | -0.00029898 | -0.00232 | -0.0020039 | 0.05188 | 0.0012047 | 0.066729 | 0.060071 | -0.0027002 | 0.0073015 | 0.001177 | -0.068665 | 62.9974 | -59.3124 | 63.1897 | -59.1293 | -59.4727 | -59.4727 | -0.032043 | 62.9837 | -59.2438 | 63.1714 | -59.2575 | -59.3582 | -59.3124 | -0.07782 | -0.12817 | 0.064087 | 0.10529 | -0.23804 | -0.23804 | -0.16022 | -0.16022 | -0.009155 | -0.14191 | 0.045777 | -0.022888 | -0.07782 | -0.1236 | -0.068665 | -0.11444 | 0.18311 | 122.5021 | -0.013733 | 122.4152 | 122.3099 | 122.2275 | 122.2321 | 122.2183 | -122.438 | -122.3694 | 122.4243 | 122.406 | 59.166 | 59.2026
265.3125 | 122.6028 | -59.2804 | 63.1393 | -0.096359 | 0.0043302 | 0.063589 | 0.06344 | 0.00012822 | -0.0016792 | -0.0030719 | -0.07019 | 0.0031273 | 0.06737 | 0.062634 | -0.0041956 | 0.0070879 | -0.0030954 | -0.09613 | 63.0066 | -59.3536 | 63.1256 | -59.2346 | -59.6054 | -59.5688 | -0.13275 | 62.9837 | -59.2575 | 63.1165 | -59.3536 | -59.4772 | -59.3857 | -0.073242 | -0.13275 | -0.013733 | 0.045777 | -0.28839 | -0.32501 | -0.21515 | -0.25177 | 0.022889 | -0.15564 | -0.022888 | -0.073242 | -0.10528 | -0.19684 | -0.12817 | -0.21973 | 0.11902 | 122.4792 | -0.096131 | 122.374 | 122.3602 | 122.2412 | 122.287 | 122.2641 | -122.493 | -122.3969 | 122.406 | 122.3969 | 59.1843 | 59.1476
266.3125 | 122.5342 | -59.2255 | 63.1439 | -0.020065 | 0.0028348 | 0.063589 | 0.063653 | 0.00076902 | -0.0016792 | 0.0014141 | -0.076294 | 0.0031273 | 0.066943 | 0.060071 | -0.003341 | 0.0079425 | 0.0022452 | -0.07782 | 63.0203 | -59.3308 | 63.1256 | -59.2255 | -59.5917 | -59.5871 | -0.16479 | 63.002 | -59.2712 | 62.8738 | -59.4086 | -59.1202 | -59.1156 | -0.10529 | -0.1236 | -0.018311 | 0 | -0.36163 | -0.36621 | -0.25635 | -0.26093 | -0.045776 | -0.14191 | -0.27008 | -0.1831 | 0.10986 | 0.10529 | 0.15564 | 0.15106 | 0.10529 | 122.4564 | -0.13733 | 122.1451 | 122.3511 | 122.2733 | 122.2458 | 122.2275 | -122.4747 | -122.4152 | 122.3511 | 122.0993 | 59.1476 | 59.0607
267.3125 | 122.699 | -59.2163 | 63.0661 | -0.14214 | 0.0028348 | 0.063162 | 0.060876 | -0.002008 | -0.0010382 | 0.00013254 | -0.027466 | 0.0020593 | 0.065234 | 0.061566 | -0.0029138 | 0.0081561 | -0.0028818 | -0.050354 | 62.9929 | -59.317 | 63.2172 | -59.0698 | -59.4864 | -59.4727 | -0.018311 | 62.9425 | -59.2575 | 63.1531 | -59.024 | -59.198 | -59.2621 | -0.10071 | -0.073242 | 0.15106 | 0.14649 | -0.25635 | -0.27008 | -0.15564 | -0.16937 | -0.041198 | -0.1236 | 0.086975 | 0.19226 | -0.045776 | 0.018311 | -0.004578 | 0.059509 | 0.24719 | 122.5342 | 0.23346 | 122.4106 | 122.3099 | 122.2 | 122.2092 | 122.1588 | -122.3831 | -122.3236 | 122.4335 | 122.3694 | 59.166 | 59.198
268.3125 | 122.5388 | -59.2758 | 63.1256 | -0.073471 | 0.0039028 | 0.065512 | 0.061731 | -8.538e-05 | 0.00024344 | -0.0026447 | -0.07019 | 0.00099115 | 0.064807 | 0.06413 | -0.0031274 | 0.0068743 | -0.0024546 | -0.045776 | 63.0295 | -59.3308 | 63.1485 | -59.1934 | -59.5688 | -59.5642 | -0.12817 | 62.9883 | -59.2484 | 63.089 | -59.3719 | -59.5047 | -59.4131 | -0.054932 | -0.09613 | 0.022889 | 0.082398 | -0.28839 | -0.29297 | -0.23346 | -0.23804 | 0.027466 | -0.13733 | -0.036621 | -0.09613 | -0.13733 | -0.22888 | -0.1648 | -0.25635 | 0.13733 | 122.4792 | -0.1236 | 122.3373 | 122.3602 | 122.2366 | 122.3053 | 122.2641 | -122.4564 | -122.374 | 122.4243 | 122.3648 | 59.23 | 59.1476
269.3125 | 122.6578 | -59.2346 | 63.1119 | -0.058212 | 0.0039028 | 0.06188 | 0.058526 | -0.0024354 | -0.004029 | -0.0017903 | 0.033569 | -0.00050405 | 0.065448 | 0.064984 | -0.0027002 | 0.0064471 | -0.0045908 | -0.032043 | 62.9791 | -59.2987 | 63.1943 | -59.1522 | -59.5001 | -59.4818 | -0.050354 | 62.9333 | -59.2575 | 63.1714 | -59.2529 | -59.3582 | -59.317 | -0.064087 | -0.13275 | 0.082398 | 0.082397 | -0.24719 | -0.2655 | -0.18311 | -0.20142 | -0.022888 | -0.17853 | 0.05951 | -0.018311 | -0.082398 | -0.1236 | -0.05951 | -0.10071 | 0.14648 | 122.493 | 0.004577 | 122.4289 | 122.2778 | 122.1909 | 122.2137 | 122.168 | -122.4106 | -122.3694 | 122.4289 | 122.406 | 59.2026 | 59.1843
270.3125 | 122.5845 | -59.2529 | 63.1531 | -0.11925 | 0.0019802 | 0.06423 | 0.061944 | 0.0014098 | -0.0014654 | -0.0013629 | -0.085449 | 0.00035035 | 0.067798 | 0.068829 | -0.0029138 | 0.0049517 | 0.000109 | -0.013733 | 63.002 | -59.3124 | 63.1805 | -59.1568 | -59.5596 | -59.5367 | -0.068665 | 62.9837 | -59.2438 | 63.1256 | -59.3308 | -59.4772 | -59.3857 | -0.059509 | -0.15106 | 0.027466 | 0.096131 | -0.28381 | -0.3067 | -0.2243 | -0.24719 | 0.009156 | -0.16937 | -0.027466 | -0.07782 | -0.13275 | -0.2243 | -0.14191 | -0.23346 | 0.15564 | 122.493 | -0.086976 | 122.3694 | 122.3145 | 122.2275 | 122.2549 | 122.2366 | -122.4655 | -122.3969 | 122.4335 | 122.3785 | 59.2392 | 59.1843
271.3125 | 122.5021 | -59.2941 | 63.0615 | -0.11162 | 0.0026212 | 0.065298 | 0.062799 | 0.00034182 | -0.003388 | -0.00050846 | -0.064087 | 0.0012047 | 0.063739 | 0.060498 | -0.0020594 | 0.0092241 | -0.0026682 | -0.059509 | 63.0112 | -59.3445 | 63.1165 | -59.2209 | -59.5871 | -59.5688 | -0.15564 | 62.9974 | -59.2529 | 63.0981 | -59.3903 | -59.5047 | -59.4269 | -0.050354 | -0.050354 | 0.054932 | 0.073242 | -0.27466 | -0.29297 | -0.22431 | -0.24262 | 0.041198 | -0.064086 | 0.036622 | -0.096131 | -0.13275 | -0.21057 | -0.17395 | -0.25177 | 0.1236 | 122.4609 | -0.13733 | 122.3511 | 122.3557 | 122.2504 | 122.3053 | 122.2916 | -122.406 | -122.3145 | 122.4106 | 122.3923 | 59.2346 | 59.1385
272.3125 | 122.6212 | -59.2621 | 63.089 | -0.050583 | 0.0036892 | 0.063376 | 0.060235 | -0.002008 | -0.0031744 | -0.0015765 | 0.018311 | 0.0014185 | 0.067157 | 0.061352 | -0.0027002 | 0.0068743 | -0.000532 | -0.032043 | 62.97 | -59.317 | 63.2126 | -59.0652 | -59.491 | -59.4498 | 0.009155 | 62.9242 | -59.2209 | 63.1897 | -59.2392 | -59.3811 | -59.317 | -0.054932 | -0.11902 | 0.1236 | 0.19684 | -0.18768 | -0.22888 | -0.13275 | -0.17395 | 0.041199 | -0.16479 | 0.10071 | 0.022888 | -0.054932 | -0.11902 | -0.096131 | -0.16022 | 0.25177 | 122.5296 | -0.018311 | 122.4106 | 122.287 | 122.1451 | 122.2321 | 122.1863 | -122.406 | -122.3099 | 122.4747 | 122.4518 | 59.23 | 59.2712
273.3125 | 122.5342 | -59.2804 | 63.121 | -0.10399 | 0.003262 | 0.06423 | 0.062799 | 0.0020508 | -0.0018928 | 0.00077334 | 0.061035 | 0.0012047 | 0.066943 | 0.063061 | -0.0029138 | 0.0070879 | 0.0009634 | -0.07782 | 63.0203 | -59.3536 | 63.1027 | -59.4177 | -60.1089 | -59.6375 | -0.2243 | 62.9974 | -59.2529 | 63.1119 | -59.3948 | -59.4864 | -59.4131 | -0.073242 | -0.10071 | -0.018311 | -0.13733 | -0.35705 | -0.82855 | -0.28381 | -0.75531 | 0.027466 | -0.1236 | -0.009156 | -0.11444 | -0.13275 | -0.20599 | -0.16022 | -0.23346 | -0.064087 | 122.4564 | -0.14191 | 122.3648 | 122.374 | 122.2504 | 122.3007 | 122.2778 | -122.4747 | -122.374 | 122.3831 | 122.3923 | 59.2026 | 59.0561
274.3125 | 122.6532 | -59.23 | 63.1027 | -0.035324 | 0.0017666 | 0.062735 | 0.060663 | -0.0011536 | -0.00232 | -0.0032855 | 0.012207 | 0.00099115 | 0.068438 | 0.061566 | -0.0024866 | 0.0055927 | -0.0020272 | -0.091553 | 63.0341 | -59.2621 | 63.208 | -59.1705 | -59.5001 | -59.4635 | -0.068665 | 62.9654 | -59.2484 | 63.1668 | -59.2712 | -59.3674 | -59.3216 | -0.032043 | -0.068664 | 0.10529 | 0.05951 | -0.23346 | -0.27008 | -0.20142 | -0.23804 | -0.01831 | -0.13733 | 0.064087 | -0.041198 | -0.091552 | -0.13733 | -0.073242 | -0.11902 | 0.091553 | 122.4701 | -0.022888 | 122.4152 | 122.2961 | 122.2137 | 122.2641 | 122.1954 | -122.3648 | -122.3511 | 122.4381 | 122.3969 | 59.1385 | 59.1614
275.3125 | 122.5754 | -59.2575 | 63.1165 | -0.0048066 | 0.0024076 | 0.065512 | 0.061303 | 0.00098262 | -0.00232 | 0.0020551 | -0.045776 | 0.0029137 | 0.068866 | 0.063702 | -0.0027002 | 0.0079425 | -0.0013864 | -0.004578 | 63.0341 | -59.3262 | 63.1989 | -59.1476 | -59.5322 | -59.5322 | -0.041199 | 63.0157 | -59.2255 | 63.1393 | -59.3079 | -59.4543 | -59.3719 | -0.068665 | -0.082397 | 0.082398 | 0.10986 | -0.27466 | -0.27466 | -0.20599 | -0.20599 | 0.032043 | -0.10071 | 0.022888 | -0.050354 | -0.11444 | -0.19684 | -0.14648 | -0.22888 | 0.17853 | 122.525 | -0.082397 | 122.3648 | 122.3602 | 122.2412 | 122.2916 | 122.2733 | -122.4426 | -122.3419 | 122.4564 | 122.3969 | 59.2529 | 59.2163
276.3125 | 122.5433 | -59.2667 | 63.1393 | -0.042954 | 0.0030484 | 0.065939 | 0.062158 | 0.0031188 | -0.0014654 | 0.00098694 | -0.064087 | 0.00013675 | 0.066089 | 0.053021 | -0.0016322 | 0.0058063 | -0.0020272 | -0.050354 | 63.0386 | -59.3124 | 63.1485 | -59.198 | -59.5779 | -59.5459 | -0.1236 | 63.0203 | -59.2575 | 63.0981 | -59.3536 | -59.5139 | -59.4086 | -0.045776 | -0.10071 | 0.009156 | 0.068665 | -0.27923 | -0.31128 | -0.23346 | -0.2655 | 0.009156 | -0.11902 | -0.041198 | -0.086975 | -0.14191 | -0.24719 | -0.15106 | -0.25635 | 0.11444 | 122.4609 | -0.096131 | 122.3557 | 122.3511 | 122.2778 | 122.3053 | 122.287 | -122.4518 | -122.3969 | 122.4152 | 122.3648 | 59.2163 | 59.1431
277.3125 | 122.6807 | -59.2621 | 63.0707 | -0.058212 | 0.0041166 | 0.065725 | 0.058526 | -0.0015808 | 2.9842e-05 | -0.0030719 | 0.0061035 | 0.00077755 | 0.067157 | 0.05708 | -0.0031274 | 0.0087969 | -0.0003182 | -0.036621 | 62.9745 | -59.2896 | 63.2309 | -59.0652 | -59.4635 | -59.4589 | 0.009155 | 62.9288 | -59.2346 | 63.208 | -59.2255 | -59.3674 | -59.3124 | -0.027466 | -0.096131 | 0.16022 | 0.19684 | -0.19684 | -0.20142 | -0.16937 | -0.17395 | 0.027466 | -0.14191 | 0.13733 | 0.036621 | -0.050354 | -0.10529 | -0.07782 | -0.13275 | 0.2243 | 122.5204 | 0.009155 | 122.4426 | 122.2641 | 122.1634 | 122.2366 | 122.1909 | -122.3602 | -122.3053 | 122.493 | 122.4701 | 59.2255 | 59.2712
278.3125 | 122.6028 | -59.2529 | 63.1256 | -0.035324 | 0.0036892 | 0.063376 | 0.061303 | -0.002008 | -0.0014654 | -0.0013629 | -0.039673 | 0.0014185 | 0.066729 | 0.062848 | -0.0029138 | 0.0075153 | -0.0022408 | 0.013733 | 63.0432 | -59.317 | 63.2034 | -59.1202 | -59.491 | -59.5001 | 0.018311 | 62.9974 | -59.23 | 63.1668 | -59.285 | -59.4223 | -59.3674 | -0.064087 | -0.082397 | 0.07782 | 0.13275 | -0.24719 | -0.23804 | -0.1831 | -0.17395 | 0.022888 | -0.12817 | 0.041199 | -0.032043 | -0.11444 | -0.16937 | -0.13733 | -0.19226 | 0.19684 | 122.5204 | -0.054931 | 122.3969 | 122.3602 | 122.2275 | 122.2961 | 122.2504 | -122.4426 | -122.3557 | 122.4564 | 122.4197 | 59.2667 | 59.2712
279.3281 | 122.5571 | -59.2255 | 63.1485 | -0.0048066 | 0.0024076 | 0.064871 | 0.060449 | 0.0029052 | -0.0021064 | -0.0015765 | -0.0091553 | 0.0024865 | 0.066729 | 0.060712 | -0.0016322 | 0.0068743 | 0.0007498 | -0.054932 | 63.0569 | -59.317 | 63.1531 | -59.1705 | -59.5001 | -59.491 | -0.027466 | 63.0341 | -59.2667 | 63.1393 | -59.3079 | -59.4223 | -59.3765 | -0.091553 | -0.091553 | 0.004577 | 0.054932 | -0.2655 | -0.27466 | -0.17395 | -0.1831 | -0.041199 | -0.11444 | -0.009156 | -0.082397 | -0.15106 | -0.19684 | -0.10986 | -0.15564 | 0.14648 | 122.4701 | -0.041198 | 122.406 | 122.374 | 122.3007 | 122.2824 | 122.2595 | -122.4655 | -122.4152 | 122.3785 | 122.3648 | 59.1705 | 59.198
280.3125 | 122.5845 | -59.2529 | 63.1577 | -0.050583 | 0.0041166 | 0.064871 | 0.061517 | -0.00029898 | -0.0025336 | -0.00093566 | -0.054932 | 0.00077755 | 0.067798 | 0.06477 | -0.0035548 | 0.0085833 | -0.0003182 | -0.018311 | 63.0386 | -59.3262 | 63.1851 | -59.1431 | -59.5367 | -59.5093 | -0.018311 | 63.0157 | -59.2438 | 63.1256 | -59.3033 | -59.4406 | -59.3811 | -0.073242 | -0.11902 | 0.027466 | 0.10986 | -0.25635 | -0.28381 | -0.1831 | -0.21057 | 0.009156 | -0.14191 | -0.032044 | -0.050354 | -0.12817 | -0.18768 | -0.13733 | -0.19684 | 0.18311 | 122.5113 | -0.05951 | 122.3694 | 122.3648 | 122.2595 | 122.2916 | 122.2687 | -122.4838 | -122.4014 | 122.4381 | 122.3785 | 59.2346 | 59.2346
281.3125 | 122.5983 | -59.2438 | 63.1531 | -0.020065 | 0.0043302 | 0.062948 | 0.062799 | 0.0044006 | -0.0042426 | 0.00098694 | -0.021362 | 0.0022729 | 0.06737 | 0.06712 | -0.0012048 | 0.0077289 | -0.0018136 | -0.013733 | 63.0295 | -59.3124 | 63.1897 | -59.1248 | -59.5001 | -59.5047 | -0.018311 | 62.9883 | -59.2529 | 63.1393 | -59.2896 | -59.4498 | -59.3536 | -0.068665 | -0.1236 | 0.036621 | 0.11902 | -0.26093 | -0.25635 | -0.19226 | -0.18768 | -0.009156 | -0.16479 | -0.013733 | -0.045777 | -0.10986 | -0.20599 | -0.10071 | -0.19684 | 0.18768 | 122.5021 | -0.036621 | 122.3923 | 122.3419 | 122.2412 | 122.2733 | 122.2321 | -122.4655 | -122.406 | 122.4335 | 122.3831 | 59.23 | 59.2255
282.3125 | 122.5708 | -59.2529 | 63.1439 | -0.058212 | 0.0056118 | 0.066153 | 0.060876 | 0.0016236 | -0.0044562 | 0.00013254 | -0.26245 | 0.0020593 | 0.065234 | 0.063275 | -0.0012048 | 0.0062335 | -0.0039498 | -0.082397 | 63.0249 | -59.3399 | 63.0981 | -59.2575 | -59.6146 | -59.6008 | -0.059509 | 62.9654 | -59.2484 | 63.1165 | -59.3628 | -59.4818 | -59.3719 | -0.086975 | -0.11902 | -0.045776 | -0.004577 | -0.3479 | -0.36163 | -0.26093 | -0.27466 | 0.004578 | -0.17853 | -0.027466 | -0.10986 | -0.11902 | -0.22888 | -0.1236 | -0.23346 | 0.082398 | 122.4381 | -0.11444 | 122.3648 | 122.3648 | 122.2137 | 122.2778 | 122.2183 | -122.4838 | -122.3923 | 122.3511 | 122.3694 | 59.1705 | 59.1934
283.3125 | 122.5983 | -59.2529 | 63.1531 | -0.058212 | 0.0009122 | 0.064657 | 0.060022 | 0.0031188 | 2.9842e-05 | -0.00050846 | -0.039673 | 0.00056395 | 0.065234 | 0.058148 | -0.0029138 | 0.0073015 | -0.0001046 | -0.027466 | 63.0341 | -59.3033 | 63.1577 | -59.1522 | -59.5459 | -59.5367 | -0.064087 | 62.9929 | -59.2667 | 63.121 | -59.3262 | -59.4589 | -59.3857 | -0.050354 | -0.11902 | 0.004578 | 0.10071 | -0.28381 | -0.29297 | -0.23346 | -0.24261 | -0.013733 | -0.16022 | -0.032043 | -0.073242 | -0.13275 | -0.20599 | -0.11902 | -0.19226 | 0.15106 | 122.4609 | -0.059509 | 122.3877 | 122.3373 | 122.2595 | 122.287 | 122.2458 | -122.4564 | -122.4197 | 122.4106 | 122.374 | 59.2255 | 59.1888
284.3281 | 122.699 | -59.2072 | 63.1027 | 0.010452 | 0.002194 | 0.062521 | 0.056604 | -0.00093998 | -0.0014654 | -0.0034991 | 0.085449 | 0.0018457 | 0.06737 | 0.059644 | -0.0046228 | 0.0055927 | 0.0007498 | -0.004578 | 63.0112 | -59.2896 | 63.2309 | -59.0652 | -59.4223 | -59.4086 | 0.073242 | 62.9608 | -59.2255 | 63.2263 | -59.1705 | -59.2712 | -59.2346 | -0.082398 | -0.091553 | 0.12817 | 0.14191 | -0.20142 | -0.21515 | -0.11902 | -0.13275 | -0.018311 | -0.14191 | 0.1236 | 0.036621 | -0.027466 | -0.064087 | -0.009155 | -0.045776 | 0.2243 | 122.5204 | 0.054932 | 122.4518 | 122.3007 | 122.1863 | 122.2183 | 122.168 | -122.3923 | -122.3282 | 122.438 | 122.4335 | 59.2026 | 59.2804
285.3125 | 122.5616 | -59.2575 | 63.1302 | -0.096359 | 0.000485 | 0.064444 | 0.062158 | -0.002008 | -0.0012518 | 0.00098694 | -0.05188 | 0.0024865 | 0.06438 | 0.056653 | -0.0029138 | 0.0077289 | -0.0011728 | -0.032043 | 63.0341 | -59.317 | 63.1485 | -59.1888 | -59.5596 | -59.5551 | -0.09613 | 62.9929 | -59.2438 | 63.089 | -59.3811 | -59.4864 | -59.404 | -0.05951 | -0.09613 | 0.018311 | 0.068664 | -0.29755 | -0.30212 | -0.23804 | -0.24261 | 0.013733 | -0.13733 | -0.041199 | -0.1236 | -0.14649 | -0.22888 | -0.16022 | -0.24262 | 0.12817 | 122.4655 | -0.13733 | 122.3328 | 122.3511 | 122.2366 | 122.2916 | 122.2504 | -122.4472 | -122.374 | 122.406 | 122.3465 | 59.2255 | 59.1614
286.3125 | 122.58 | -59.2667 | 63.1348 | -0.050583 | 0.003262 | 0.065725 | 0.06344 | 0.0016236 | -0.0010382 | 0.0014141 | -0.10681 | -0.00071785 | 0.064593 | 0.065198 | -0.0016322 | 0.0070879 | -0.0013864 | -0.073242 | 63.0249 | -59.3445 | 63.0798 | -59.2484 | -59.6283 | -59.8846 | 0.11902 | 63.0249 | -59.2392 | 63.089 | -59.3582 | -59.4727 | -59.3948 | -0.077819 | -0.10986 | -0.054932 | 0.018311 | -0.61798 | -0.36163 | -0.54016 | -0.28381 | 0.027466 | -0.10986 | -0.045777 | -0.091552 | -0.12817 | -0.20599 | -0.15564 | -0.23346 | 0.09613 | 122.4243 | -0.11902 | 122.3282 | 122.3694 | 122.2641 | 122.2916 | 122.2916 | -122.4792 | -122.374 | 122.3465 | 122.3557 | 59.1934 | 59.3857
287.3125 | 122.7127 | -59.2346 | 63.0936 | -0.08873 | 0.0030484 | 0.065512 | 0.060022 | -0.004358 | 0.00067084 | -0.0034991 | -0.0091553 | 0.00035035 | 0.065875 | 0.061566 | -0.0024866 | 0.0062335 | 0.0005362 | -0.009155 | 62.9745 | -59.2987 | 63.2172 | -59.1019 | -59.4681 | -59.4498 | -0.22888 | 62.8738 | -59.2896 | 63.2217 | -59.2255 | -59.3491 | -59.2438 | -0.064087 | -0.11902 | 0.1236 | 0.13275 | -0.21515 | -0.23346 | -0.15106 | -0.16937 | -0.054932 | -0.21973 | 0.12817 | 0.009155 | -0.009155 | -0.11444 | 0.045777 | -0.059509 | 0.19684 | 122.5159 | 0.064087 | 122.5113 | 122.2733 | 122.1634 | 122.2092 | 122.1085 | -122.3923 | -122.3831 | 122.4518 | 122.4564 | 59.2255 | 59.0057
288.3125 | 122.6028 | -59.2163 | 63.1256 | -0.0048066 | 0.001553 | 0.06423 | 0.061303 | -0.0032898 | -0.0038154 | 0.00013254 | -0.012207 | 0.0014185 | 0.066089 | 0.057507 | -0.0027002 | 0.0077289 | -0.0013864 | 0.004578 | 63.0661 | -59.2896 | 63.1897 | -59.1385 | -59.4772 | -59.5139 | 0.009155 | 63.0249 | -59.2346 | 63.1714 | -59.2575 | -59.3811 | -59.3262 | -0.073242 | -0.059509 | 0.064087 | 0.07782 | -0.29755 | -0.26093 | -0.2243 | -0.18768 | -0.01831 | -0.10071 | 0.045777 | -0.041198 | -0.10986 | -0.16479 | -0.091553 | -0.14648 | 0.15106 | 122.4792 | -0.022888 | 122.406 | 122.3557 | 122.2595 | 122.2824 | 122.2412 | -122.4152 | -122.3602 | 122.406 | 122.3877 | 59.2209 | 59.2255
289.3281 | 122.5891 | -59.2392 | 63.1668 | -0.096359 | 0.003262 | 0.062948 | 0.059381 | 0.0011962 | -0.0031744 | 0.00013254 | 0.076294 | 0.0037683 | 0.068652 | 0.064343 | -0.0016322 | 0.0058063 | -0.0026682 | -0.009155 | 63.0386 | -59.2758 | 63.1439 | -59.1385 | -59.5001 | -59.4086 | -0.21057 | 63.0295 | -59.2484 | 63.1027 | -59.3033 | -59.4452 | -59.3765 | -0.036621 | -0.12817 | -0.022888 | 0.10071 | -0.16937 | -0.26093 | -0.13275 | -0.2243 | -0.009155 | -0.13733 | -0.064087 | -0.064087 | -0.13733 | -0.20599 | -0.12817 | -0.19684 | 0.13733 | 122.4197 | -0.054932 | 122.3511 | 122.3145 | 122.2778 | 122.2778 | 122.2687 | -122.4426 | -122.4152 | 122.3831 | 122.3419 | 59.23 | 59.0286
290.3125 | 122.6166 | -59.2392 | 63.176 | 0.010452 | -0.000156 | 0.06423 | 0.061944 | 0.0050414 | 2.9842e-05 | -0.0013629 | -0.0030517 | 0.0027001 | 0.068225 | 0.062634 | -0.0029138 | 0.0068743 | 0.001177 | -0.004578 | 63.0753 | -59.2987 | 63.1714 | -59.1568 | -59.5093 | -59.5001 | -0.022888 | 63.0112 | -59.2346 | 63.1393 | -59.2758 | -59.4086 | -59.3399 | -0.059509 | -0.10071 | -0.004577 | 0.082398 | -0.26093 | -0.27008 | -0.20142 | -0.21057 | 0.004578 | -0.16479 | -0.036621 | -0.036621 | -0.10071 | -0.16937 | -0.10529 | -0.17395 | 0.14191 | 122.4701 | -0.041199 | 122.374 | 122.374 | 122.2458 | 122.3145 | 122.2504 | -122.4747 | -122.4106 | 122.4106 | 122.3785 | 59.2346 | 59.2163
291.3125 | 122.6166 | -59.2484 | 63.1622 | -0.11162 | 0.003262 | 0.065085 | 0.061303 | 0.0039734 | -0.0025336 | 0.00013254 | -0.012207 | 0.00013675 | 0.06737 | 0.068616 | -0.0016322 | 0.0062335 | -0.0024546 | 0.009155 | 63.0066 | -59.3262 | 63.1943 | -59.079 | -59.4864 | -59.4772 | 0.004578 | 62.9929 | -59.2392 | 63.1622 | -59.2667 | -59.4086 | -59.3399 | -0.07782 | -0.15564 | 0.032044 | 0.16937 | -0.22888 | -0.23804 | -0.15106 | -0.16022 | 0.009155 | -0.16937 | 0 | -0.018311 | -0.091553 | -0.16022 | -0.10071 | -0.16937 | 0.24719 | 122.5204 | -0.027466 | 122.4014 | 122.3328 | 122.2321 | 122.2549 | 122.2412 | -122.4884 | -122.4014 | 122.4426 | 122.4106 | 59.2575 | 59.2529
292.3125 | 122.6257 | -59.2209 | 63.1485 | -0.020065 | 0.001553 | 0.064016 | 0.060876 | 0.0037598 | -0.0014654 | -0.0022175 | -0.015259 | 0.00013675 | 0.065661 | 0.068188 | -0.0054774 | 0.0077289 | -0.0020272 | 0.032043 | 63.0432 | -59.3079 | 63.2401 | -59.285 | -59.697 | -59.4498 | 0.009155 | 63.0066 | -59.2346 | 63.1668 | -59.2575 | -59.3948 | -59.3308 | -0.086975 | -0.10529 | 0.091552 | -0.064087 | -0.22888 | -0.47607 | -0.14191 | -0.3891 | -0.013733 | -0.14191 | 0.01831 | -0.036621 | -0.10986 | -0.17395 | -0.096131 | -0.16022 | 0.022888 | 122.5479 | -0.022888 | 122.4014 | 122.3511 | 122.2412 | 122.2641 | 122.2275 | -122.4564 | -122.3831 | 122.4609 | 122.3877 | 59.2529 | 59.23
293.3125 | 122.612 | -59.2529 | 63.1393 | -0.020065 | 0.0013394 | 0.065939 | 0.062158 | 0.0018372 | -0.0027472 | -0.0020039 | -0.027466 | 0.0012047 | 0.067157 | 0.06712 | -0.0035548 | 0.0092241 | 0.0007498 | 0.009155 | 63.0249 | -59.3216 | 63.1897 | -59.1064 | -59.5001 | -59.4955 | 0.013733 | 62.9883 | -59.2438 | 63.1668 | -59.2804 | -59.4269 | -59.3353 | -0.068664 | -0.11444 | 0.050354 | 0.14648 | -0.24261 | -0.24719 | -0.17395 | -0.17853 | 0.009156 | -0.15106 | 0.027466 | -0.027466 | -0.082397 | -0.17395 | -0.091553 | -0.18311 | 0.21515 | 122.5113 | -0.036622 | 122.4106 | 122.3465 | 122.2321 | 122.2778 | 122.2412 | -122.4609 | -122.3831 | 122.4426 | 122.4197 | 59.2621 | 59.2667
294.3125 | 122.6852 | -59.2255 | 63.1256 | -0.035324 | 0.0030484 | 0.063589 | 0.059595 | -0.00051278 | -0.0016792 | 0.00034614 | 0.094605 | 0.0022729 | 0.066089 | 0.054303 | -0.003341 | 0.0077289 | -0.0028818 | 0.009155 | 62.9974 | -59.2621 | 63.2263 | -59.0698 | -59.4223 | -59.4223 | 0.054932 | 62.9425 | -59.23 | 63.2172 | -59.1797 | -59.2987 | -59.2484 | -0.036621 | -0.12817 | 0.10071 | 0.15564 | -0.19684 | -0.19684 | -0.16022 | -0.16022 | -0.004578 | -0.18311 | 0.091553 | 0.045777 | -0.022888 | -0.073242 | -0.01831 | -0.068664 | 0.19226 | 122.4884 | 0.050355 | 122.4472 | 122.2595 | 122.1725 | 122.2229 | 122.168 | -122.3877 | -122.3557 | 122.4518 | 122.4426 | 59.2346 | 59.2804
295.3125 | 122.6349 | -59.2392 | 63.1577 | -0.020065 | 0.002194 | 0.062735 | 0.061944 | -0.00093998 | -0.00082456 | -8.1264e-05 | -0.030517 | 0.0022729 | 0.068652 | 0.065625 | -0.0029138 | 0.0073015 | 0.0003226 | 0.013733 | 63.0341 | -59.2712 | 63.1714 | -59.1476 | -59.4955 | -59.4864 | 0.018311 | 63.0066 | -59.2255 | 63.1577 | -59.2621 | -59.3948 | -59.3262 | -0.032043 | -0.1236 | 0.013733 | 0.091553 | -0.24719 | -0.25635 | -0.21515 | -0.2243 | 0.013733 | -0.15106 | 0 | -0.022888 | -0.086975 | -0.15564 | -0.10071 | -0.16937 | 0.1236 | 122.4426 | -0.036621 | 122.3831 | 122.3053 | 122.2321 | 122.2733 | 122.2458 | -122.4289 | -122.3831 | 122.4106 | 122.3969 | 59.2529 | 59.2575
296.3125 | 122.5937 | -59.2438 | 63.1485 | -0.0048066 | 0.0026212 | 0.065512 | 0.060663 | 0.00076902 | -0.00061096 | -0.00029486 | -0.027466 | 0.0014185 | 0.067798 | 0.060284 | -0.003341 | 0.0068743 | -0.0030954 | 0.013733 | 63.0524 | -59.2987 | 63.1622 | -59.1522 | -59.491 | -59.491 | -0.004578 | 63.0249 | -59.2255 | 63.1393 | -59.2575 | -59.3994 | -59.3262 | -0.054932 | -0.096131 | 0.013732 | 0.091552 | -0.24719 | -0.24719 | -0.19226 | -0.19226 | 0.01831 | -0.1236 | -0.009156 | -0.013733 | -0.082398 | -0.15564 | -0.10071 | -0.17395 | 0.14648 | 122.4609 | -0.032043 | 122.3648 | 122.3511 | 122.2504 | 122.2961 | 122.2687 | -122.4472 | -122.374 | 122.406 | 122.3831 | 59.2575 | 59.2392
297.3125 | 122.6532 | -59.2804 | 63.1073 | -0.027695 | 0.002194 | 0.064657 | 0.061303 | 0.00034182 | -0.0036018 | -0.0034991 | -0.039673 | 0.0018457 | 0.067584 | 0.064557 | -0.002273 | 0.0075153 | 0.0016044 | -0.082397 | 63.002 | -59.3308 | 63.1485 | -59.1522 | -59.5596 | -59.5276 | -0.064087 | 62.9608 | -59.2529 | 63.1668 | -59.2392 | -59.3948 | -59.3033 | -0.050354 | -0.10529 | 0.041199 | 0.12817 | -0.24719 | -0.27923 | -0.19684 | -0.22888 | 0.027466 | -0.14649 | 0.059509 | 0.041199 | -0.022888 | -0.11444 | -0.050354 | -0.14191 | 0.17853 | 122.4792 | 0.013733 | 122.4197 | 122.3328 | 122.2137 | 122.2824 | 122.2412 | -122.4381 | -122.3602 | 122.4289 | 122.4472 | 59.198 | 59.2163
298.3125 | 122.58 | -59.2484 | 63.1531 | 0.010452 | 0.0030484 | 0.064871 | 0.061517 | 0.004187 | -0.0010382 | 0.00098694 | -0.030517 | 0.0012047 | 0.066089 | 0.063061 | -0.003982 | 0.0064471 | -0.0020272 | 0.018311 | 63.0524 | -59.3079 | 63.1943 | -59.0927 | -59.4818 | -59.4681 | 0.027466 | 62.9791 | -59.2346 | 63.176 | -59.2758 | -59.4131 | -59.3399 | -0.059509 | -0.10071 | 0.041199 | 0.15564 | -0.21973 | -0.23346 | -0.16022 | -0.17395 | 0.013733 | -0.17395 | 0.022888 | -0.027466 | -0.091553 | -0.1648 | -0.10529 | -0.17853 | 0.21515 | 122.5021 | -0.041199 | 122.4106 | 122.3602 | 122.2137 | 122.3007 | 122.2275 | -122.4609 | -122.3877 | 122.4426 | 122.4243 | 59.2667 | 59.2758
299.3125 | 122.5754 | -59.2575 | 63.1393 | -0.081101 | 0.0034756 | 0.064657 | 0.061731 | 0.0018372 | -0.0025336 | -0.00093566 | -0.048828 | 0.0020593 | 0.066943 | 0.067761 | -0.003982 | 0.0068743 | -0.000532 | -0.004578 | 63.0341 | -59.3079 | 63.1714 | -59.1385 | -59.5367 | -59.5139 | -0.022888 | 62.9883 | -59.2529 | 63.121 | -59.3124 | -59.4452 | -59.3628 | -0.050354 | -0.10528 | 0.032044 | 0.11902 | -0.25635 | -0.27924 | -0.20599 | -0.22888 | 0.004577 | -0.15106 | -0.01831 | -0.054932 | -0.10529 | -0.18768 | -0.10986 | -0.19226 | 0.16937 | 122.4792 | -0.059509 | 122.374 | 122.3419 | 122.2412 | 122.2916 | 122.2458 | -122.4472 | -122.3923 | 122.4289 | 122.3785 | 59.2529 | 59.2346
300.3125 | 122.5616 | -59.2484 | 63.1577 | -0.020065 | 0.0026212 | 0.062308 | 0.059167 | -0.0024354 | -0.0016792 | 0.00034614 | -0.0061035 | 0.0024865 | 0.06737 | 0.060712 | -0.0044092 | 0.0064471 | 0.0048086 | -0.004578 | 63.0707 | -59.2987 | 63.1531 | -59.1705 | -59.5322 | -59.5139 | -0.004578 | 63.0157 | -59.2438 | 63.1165 | -59.3124 | -59.4269 | -59.3582 | -0.050354 | -0.086975 | -0.004578 | 0.07782 | -0.2655 | -0.28381 | -0.21515 | -0.23346 | 0.004578 | -0.14191 | -0.041199 | -0.064087 | -0.10986 | -0.17853 | -0.11444 | -0.18311 | 0.12817 | 122.4518 | -0.068665 | 122.3602 | 122.3694 | 122.2595 | 122.319 | 122.2641 | -122.4564 | -122.4014 | 122.4014 | 122.3648 | 59.2438 | 59.2438
301.3125 | 122.6028 | -59.2346 | 63.1714 | -0.027695 | 0.000485 | 0.063376 | 0.061944 | -0.0015808 | -0.0018928 | -0.0022175 | 0.0030517 | 0.0035547 | 0.067798 | 0.063489 | -0.0029138 | 0.0051653 | -0.0030954 | 0.018311 | 63.0707 | -59.285 | 63.1577 | -59.1522 | -59.5184 | -59.5139 | -0.013733 | 63.0066 | -59.23 | 63.1393 | -59.2758 | -59.3994 | -59.3353 | -0.050354 | -0.10071 | -0.013733 | 0.082397 | -0.27924 | -0.28381 | -0.22888 | -0.23346 | 0.004577 | -0.1648 | -0.032044 | -0.041199 | -0.10071 | -0.16479 | -0.10529 | -0.16937 | 0.13275 | 122.4426 | -0.045776 | 122.3694 | 122.3557 | 122.2366 | 122.3053 | 122.2412 | -122.4564 | -122.4014 | 122.3923 | 122.374 | 59.2529 | 59.2209
302.3125 | 122.6532 | -59.2667 | 63.1027 | -0.027695 | 0.0024076 | 0.062094 | 0.060663 | 0.0020508 | -0.00082456 | 0.0014141 | -0.015259 | 0.00035035 | 0.066089 | 0.063275 | -0.003982 | 0.0060199 | -0.0016 | -0.086975 | 63.0112 | -59.317 | 63.1302 | -59.1888 | -59.5688 | -59.5505 | -0.10529 | 62.9745 | -59.2712 | 63.1439 | -59.2987 | -59.4177 | -59.3399 | -0.050354 | -0.091553 | 0.027466 | 0.07782 | -0.28381 | -0.30212 | -0.23346 | -0.25177 | -0.004577 | -0.12817 | 0.041199 | -0.032043 | -0.073242 | -0.15106 | -0.068665 | -0.14648 | 0.12817 | 122.4472 | -0.027466 | 122.4152 | 122.3282 | 122.2458 | 122.2778 | 122.2412 | -122.4197 | -122.374 | 122.3969 | 122.4106 | 59.1797 | 59.1614
303.3125 | 122.5296 | -59.2529 | 63.1668 | 0.0028229 | 0.0024076 | 0.063162 | 0.060449 | -0.0039306 | -0.003388 | -0.0013629 | 0.015259 | 0.0024865 | 0.066302 | 0.062848 | -0.0035548 | 0.0064471 | -0.0001046 | 0.013733 | 63.0661 | -59.2941 | 63.1485 | -59.1522 | -59.5047 | -59.4955 | 0.13733 | 63.0798 | -59.1843 | 63.1439 | -59.3308 | -59.3994 | -59.3674 | -0.041198 | -0.10071 | -0.01831 | 0.10071 | -0.24261 | -0.25177 | -0.20142 | -0.21057 | 0.068665 | -0.086975 | -0.022888 | -0.07782 | -0.11444 | -0.14648 | -0.18311 | -0.21515 | 0.14191 | 122.4426 | -0.14648 | 122.3282 | 122.3602 | 122.2641 | 122.319 | 122.3328 | -122.4609 | -122.3511 | 122.4014 | 122.3969 | 59.2667 | 59.3903
304.3125 | 122.5845 | -59.2438 | 63.1897 | 0.0028229 | 0.001553 | 0.06188 | 0.059381 | 0.00034182 | -0.0027472 | 0.00098694 | 0.0061035 | 0.0022729 | 0.065875 | 0.062207 | -0.0041956 | 0.0062335 | 0.0022452 | 0.009155 | 63.0798 | -59.3216 | 63.1577 | -59.1522 | -59.5047 | -59.4955 | 0.009155 | 63.0203 | -59.2255 | 63.1531 | -59.2758 | -59.404 | -59.3399 | -0.07782 | -0.10986 | -0.032043 | 0.091552 | -0.25177 | -0.26093 | -0.17395 | -0.18311 | 0.01831 | -0.16937 | -0.036621 | -0.032044 | -0.096131 | -0.16022 | -0.11444 | -0.17853 | 0.16937 | 122.4792 | -0.050354 | 122.3785 | 122.4014 | 122.2458 | 122.3236 | 122.2641 | -122.5113 | -122.4152 | 122.4014 | 122.3969 | 59.2529 | 59.2529
305.3125 | 122.612 | -59.2392 | 63.1668 | -0.020065 | -0.000156 | 0.062948 | 0.061303 | 0.0026916 | -0.00232 | -0.00050846 | 0.0030517 | 0.00077755 | 0.067584 | 0.060498 | -0.0037684 | 0.0064471 | -0.0020272 | 0 | 63.0615 | -59.2804 | 63.1622 | -59.166 | -59.5413 | -59.5001 | -0.022888 | 63.0066 | -59.2117 | 63.1302 | -59.2667 | -59.3994 | -59.3262 | -0.041199 | -0.10529 | -0.004578 | 0.073242 | -0.26093 | -0.30212 | -0.21973 | -0.26093 | 0.027466 | -0.16022 | -0.036621 | -0.027466 | -0.086975 | -0.16022 | -0.11444 | -0.18768 | 0.11444 | 122.4426 | -0.054932 | 122.3419 | 122.3419 | 122.2183 | 122.3007 | 122.2458 | -122.4472 | -122.3785 | 122.4014 | 122.3694 | 59.2392 | 59.2163
306.3125 | 122.6212 | -59.2438 | 63.1622 | -0.027695 | 0.0026212 | 0.064444 | 0.060663 | -0.0013672 | -0.0027472 | -0.00093566 | -0.01831 | 0.00099115 | 0.06737 | 0.061993 | -0.0029138 | 0.0075153 | 0.001177 | 0.027466 | 63.0569 | -59.3216 | 63.1943 | -59.1293 | -59.4955 | -59.4727 | 0.045776 | 63.0066 | -59.2117 | 63.1485 | -59.2575 | -59.3994 | -59.3353 | -0.07782 | -0.10528 | 0.032044 | 0.11444 | -0.22888 | -0.25177 | -0.15106 | -0.17395 | 0.032043 | -0.15564 | -0.013732 | -0.013733 | -0.091553 | -0.15564 | -0.1236 | -0.18768 | 0.19226 | 122.5159 | -0.045776 | 122.3602 | 122.3785 | 122.2183 | 122.3007 | 122.2504 | -122.4838 | -122.374 | 122.438 | 122.3923 | 59.2712 | 59.2895
307.3125 | 122.6257 | -59.2346 | 63.1393 | -0.012436 | 0.0006986 | 0.063589 | 0.062372 | 0.0020508 | -0.003388 | -0.0020039 | -8.6e-08 | 0.00035035 | 0.066943 | 0.06413 | -0.0035548 | 0.0070879 | -0.0026682 | 0.027466 | 63.0615 | -59.2987 | 63.176 | -59.1522 | -59.5001 | -59.4864 | 0.013733 | 63.0295 | -59.2072 | 63.1439 | -59.2529 | -59.3948 | -59.3124 | -0.064087 | -0.07782 | 0.036621 | 0.082397 | -0.25177 | -0.2655 | -0.18768 | -0.20142 | 0.027466 | -0.10986 | 0.004578 | -0.018311 | -0.07782 | -0.16022 | -0.10529 | -0.18768 | 0.14648 | 122.4747 | -0.045777 | 122.3511 | 122.3602 | 122.2366 | 122.2961 | 122.2641 | -122.438 | -122.3465 | 122.4106 | 122.3785 | 59.2621 | 59.2484
308.3125 | 122.5983 | -59.2621 | 63.1714 | -0.042954 | 0.0017666 | 0.062735 | 0.060235 | -0.0022218 | -0.0016792 | -0.0022175 | 0.030518 | 0.0024865 | 0.068866 | 0.061139 | -0.0024866 | 0.0062335 | -0.0026682 | 0.018311 | 63.0249 | -59.2941 | 63.1577 | -59.1522 | -59.5001 | -59.4955 | 0.004578 | 63.002 | -59.2438 | 63.1622 | -59.4727 | -59.5779 | -59.4269 | -0.032043 | -0.14649 | -0.013733 | 0.10986 | -0.23346 | -0.23804 | -0.20142 | -0.20599 | 0.018311 | -0.16937 | -0.009156 | -0.21057 | -0.16479 | -0.31586 | -0.18311 | -0.33417 | 0.14191 | 122.4518 | -0.22888 | 122.406 | 122.319 | 122.2458 | 122.287 | 122.2641 | -122.4655 | -122.4152 | 122.4197 | 122.4243 | 59.2804 | 59.2667
309.3125 | 122.5388 | -59.2484 | 63.1851 | -0.14214 | 0.002194 | 0.062094 | 0.060876 | -0.0030762 | -0.0021064 | 0.0014141 | 0.0061035 | 0.0029137 | 0.066302 | 0.063916 | -0.002273 | 0.0087969 | -0.0009592 | 0.022888 | 63.0478 | -59.2941 | 63.1439 | -59.1522 | -59.5139 | -59.5184 | -0.004578 | 63.0203 | -59.2072 | 63.121 | -59.3033 | -59.4131 | -59.3582 | -0.045776 | -0.13733 | -0.041199 | 0.09613 | -0.27008 | -0.2655 | -0.22431 | -0.21973 | 0.041199 | -0.16479 | -0.064087 | -0.054932 | -0.10986 | -0.1648 | -0.15106 | -0.20599 | 0.14191 | 122.438 | -0.096131 | 122.3282 | 122.3419 | 122.2275 | 122.2961 | 122.2687 | -122.4792 | -122.3923 | 122.3923 | 122.3694 | 59.2712 | 59.2438
310.3125 | 122.5937 | -59.2392 | 63.1805 | -0.027695 | 0.0030484 | 0.065725 | 0.060876 | 0.00098262 | -0.0027472 | -0.00050846 | 0.045776 | -0.00050405 | 0.066089 | 0.067975 | -0.0041956 | 0.0060199 | 0.0003226 | 0.045776 | 63.0569 | -59.2712 | 63.2172 | -59.0881 | -59.4635 | -59.4406 | 0.032043 | 63.0432 | -59.1888 | 63.1302 | -59.2484 | -59.3994 | -59.3628 | -0.032043 | -0.1236 | 0.036621 | 0.15106 | -0.20142 | -0.2243 | -0.16937 | -0.19226 | 0.050354 | -0.13733 | -0.050354 | -0.009155 | -0.1236 | -0.16022 | -0.17395 | -0.21057 | 0.1831 | 122.4884 | -0.059509 | 122.319 | 122.3282 | 122.2321 | 122.2961 | 122.2824 | -122.4518 | -122.3694 | 122.4564 | 122.3694 | 59.285 | 59.2712
311.3125 | 122.6257 | -59.2392 | 63.1348 | -0.042954 | 0.0030484 | 0.065512 | 0.062372 | 0.0031188 | -0.0016792 | 0.0012005 | -0.039673 | 0.0016321 | 0.067157 | 0.070111 | -0.0037684 | 0.0062335 | 0.0024588 | 0.018311 | 63.0295 | -59.3308 | 63.2034 | -59.0652 | -59.5139 | -59.4772 | 0.032043 | 63.0112 | -59.2163 | 63.1714 | -59.2712 | -59.3994 | -59.3445 | -0.091553 | -0.10529 | 0.068664 | 0.17395 | -0.23804 | -0.27466 | -0.14648 | -0.1831 | 0.022888 | -0.1236 | 0.036621 | -0.032043 | -0.10529 | -0.16022 | -0.12817 | -0.1831 | 0.2655 | 122.5342 | -0.054931 | 122.3877 | 122.3602 | 122.2275 | 122.2687 | 122.2504 | -122.4655 | -122.3511 | 122.4426 | 122.4106 | 59.2575 | 59.2712
312.3125 | 122.5479 | -59.285 | 63.1302 | -0.042954 | 0.0041166 | 0.062948 | 0.061944 | -0.00072638 | -0.0014654 | 0.00034614 | -0.045776 | 0.00099115 | 0.068011 | 0.060498 | -0.0027002 | 0.0066607 | 0.0022452 | -0.027466 | 63.0341 | -59.3445 | 63.1439 | -59.1888 | -59.5688 | -59.5459 | -0.11902 | 63.0066 | -59.2484 | 63.0798 | -59.3399 | -59.4955 | -59.3994 | -0.059509 | -0.09613 | 0.013733 | 0.09613 | -0.26093 | -0.28381 | -0.20142 | -0.22431 | 0.036621 | -0.1236 | -0.050354 | -0.054932 | -0.11444 | -0.21057 | -0.15106 | -0.24719 | 0.15564 | 122.4884 | -0.091553 | 122.3282 | 122.3785 | 122.2549 | 122.319 | 122.2916 | -122.4747 | -122.3785 | 122.4289 | 122.3648 | 59.2575 | 59.166
313.3125 | 122.5891 | -59.2484 | 63.1668 | -0.042954 | 0.0006986 | 0.06423 | 0.060663 | 0.00012822 | -0.0031744 | -0.00093566 | -0.0061035 | 0.00099115 | 0.067157 | 0.063061 | -0.0029138 | 0.0049517 | -0.0024546 | 0 | 63.0432 | -59.3033 | 63.1348 | -59.1522 | -59.5047 | -59.4955 | -0.013733 | 63.0249 | -59.2117 | 63.1165 | -59.285 | -59.4269 | -59.3674 | -0.054932 | -0.1236 | -0.032043 | 0.09613 | -0.24719 | -0.25635 | -0.19226 | -0.20142 | 0.036621 | -0.14191 | -0.050354 | -0.036621 | -0.11902 | -0.17853 | -0.15564 | -0.21515 | 0.15106 | 122.4381 | -0.073242 | 122.3282 | 122.3465 | 122.2366 | 122.2916 | 122.2733 | -122.4701 | -122.3785 | 122.3831 | 122.3648 | 59.2484 | 59.2346
314.3125 | 122.5891 | -59.2529 | 63.1577 | -0.050583 | 0.0026212 | 0.062735 | 0.063226 | 0.0020508 | -0.003388 | -0.00072206 | -0.067139 | 0.0018457 | 0.068438 | 0.06413 | -0.003341 | 0.0047381 | 0.0020316 | -0.064087 | 63.0478 | -59.3582 | 63.1027 | -59.2529 | -59.6054 | -59.5642 | -0.18768 | 62.9791 | -59.2667 | 63.2217 | -59.4269 | -59.4818 | -59.3994 | -0.10529 | -0.10986 | -0.054932 | 0 | -0.31128 | -0.35248 | -0.20599 | -0.24719 | -0.013733 | -0.17853 | 0.064087 | -0.17395 | -0.14648 | -0.22888 | -0.13275 | -0.21515 | 0.10529 | 122.4609 | -0.16022 | 122.4884 | 122.406 | 122.2458 | 122.3007 | 122.2321 | -122.5159 | -122.4243 | 122.3557 | 122.4747 | 59.1888 | 59.0652
315.3125 | 122.6486 | -59.1843 | 63.1302 | -0.027695 | 0.0030484 | 0.065939 | 0.060663 | 0.0016236 | -0.0027472 | -0.00050846 | 0.054932 | 0.0029137 | 0.065661 | 0.056653 | -0.0046228 | 0.0081561 | -0.0060862 | 0.068665 | 63.0249 | -59.2712 | 63.2721 | -59.0103 | -59.3811 | -59.3811 | 0.10986 | 62.9837 | -59.2117 | 63.2034 | -59.1797 | -59.3033 | -59.2758 | -0.086975 | -0.10529 | 0.14191 | 0.17395 | -0.19684 | -0.19684 | -0.10986 | -0.10986 | -0.027466 | -0.14648 | 0.073242 | 0.004578 | -0.091553 | -0.11902 | -0.064087 | -0.091553 | 0.26093 | 122.5433 | 0.032044 | 122.4152 | 122.2961 | 122.1954 | 122.2092 | 122.168 | -122.4014 | -122.3419 | 122.4564 | 122.3877 | 59.2529 | 59.2941
316.3125 | 122.5891 | -59.2072 | 63.1531 | -0.050583 | 0.0039028 | 0.065725 | 0.061517 | -0.0032898 | -0.00232 | -8.1264e-05 | 0.036621 | 0.00099115 | 0.067157 | 0.065198 | -0.0046228 | 0.0060199 | -0.0028818 | 0.064087 | 63.0295 | -59.2941 | 63.2309 | -59.0607 | -59.4177 | -59.3948 | 0.082397 | 63.0112 | -59.2209 | 63.1348 | -59.2575 | -59.3719 | -59.3216 | -0.086975 | -0.1236 | 0.07782 | 0.14648 | -0.18768 | -0.21057 | -0.10071 | -0.1236 | -0.013733 | -0.14191 | -0.01831 | -0.050354 | -0.11444 | -0.1648 | -0.10071 | -0.15106 | 0.23346 | 122.525 | -0.036621 | 122.3557 | 122.3236 | 122.2321 | 122.2366 | 122.2183 | -122.4472 | -122.374 | 122.438 | 122.3419 | 59.2712 | 59.2895
317.3125 | 122.5937 | -59.2529 | 63.1393 | -0.020065 | 0.0019802 | 0.065298 | 0.06344 | -0.00029898 | -0.003388 | 0.0014141 | -0.057983 | 0.0018457 | 0.066089 | 0.05708 | -0.0031274 | 0.0066607 | -0.0018136 | 0.032043 | 63.0066 | -59.2987 | 63.1943 | -59.1202 | -59.5322 | -59.5001 | -0.004578 | 62.9929 | -59.2529 | 63.1485 | -59.3033 | -59.4498 | -59.3582 | -0.045776 | -0.13275 | 0.054932 | 0.13275 | -0.24719 | -0.27924 | -0.20142 | -0.23346 | 0 | -0.14648 | 0.009156 | -0.050354 | -0.10529 | -0.19684 | -0.10529 | -0.19684 | 0.17853 | 122.493 | -0.050354 | 122.4014 | 122.3053 | 122.2458 | 122.2595 | 122.2458 | -122.438 | -122.3923 | 122.4472 | 122.4014 | 59.285 | 59.2484
318.3125 | 122.612 | -59.2117 | 63.1302 | -0.0048066 | 0.0019802 | 0.061239 | 0.059167 | 0.0014098 | -0.0025336 | -8.1264e-05 | 0.024414 | 0.00077755 | 0.065234 | 0.062421 | -0.0035548 | 0.0053789 | -0.0013864 | 0.073242 | 63.0157 | -59.2804 | 63.2538 | -59.0378 | -59.4177 | -59.404 | 0.10986 | 63.0066 | -59.2209 | 63.1943 | -59.2163 | -59.3353 | -59.2987 | -0.068665 | -0.11444 | 0.1236 | 0.17395 | -0.19226 | -0.20599 | -0.1236 | -0.13733 | -0.009155 | -0.1236 | 0.064087 | -0.004578 | -0.086975 | -0.1236 | -0.07782 | -0.11444 | 0.24262 | 122.5342 | 0.004577 | 122.4152 | 122.2961 | 122.2275 | 122.2275 | 122.2183 | -122.4106 | -122.3511 | 122.4655 | 122.406 | 59.285 | 59.3216
319.3125 | 122.5891 | -59.2484 | 63.1622 | -0.08873 | 0.0024076 | 0.063376 | 0.061731 | 0.00055542 | -0.0021064 | 0.00034614 | -0.07019 | 0.0012047 | 0.068011 | 0.063061 | -0.0029138 | 0.0075153 | -0.0030954 | 0.032043 | 63.0295 | -59.3216 | 63.1897 | -59.1248 | -59.491 | -59.4864 | 0.018311 | 63.0157 | -59.2255 | 63.1531 | -59.2804 | -59.4177 | -59.3399 | -0.073242 | -0.13275 | 0.027466 | 0.1236 | -0.23804 | -0.24262 | -0.1648 | -0.16937 | 0.022888 | -0.14648 | -0.009155 | -0.032044 | -0.091553 | -0.16937 | -0.11444 | -0.19226 | 0.19684 | 122.5113 | -0.054932 | 122.3785 | 122.3511 | 122.2412 | 122.2778 | 122.2641 | -122.4838 | -122.3877 | 122.438 | 122.4014 | 59.2804 | 59.2667
320.3125 | 122.5662 | -59.2438 | 63.1622 | -0.058212 | 0.001553 | 0.060599 | 0.060235 | 0.0016236 | -0.0031744 | -0.0015765 | 0.021362 | 0.0018457 | 0.067157 | 0.058789 | -0.0037684 | 0.0060199 | 0.0003226 | 0.1831 | 63.1165 | -59.2575 | 63.1256 | -59.166 | -59.5047 | -59.5139 | 0 | 63.0386 | -59.2392 | 63.1027 | -59.3033 | -59.4131 | -59.3491 | -0.013733 | -0.045776 | -0.036621 | 0.077819 | -0.27008 | -0.26093 | -0.25635 | -0.24719 | 0.004577 | -0.1236 | -0.059509 | -0.05951 | -0.10529 | -0.16937 | -0.10986 | -0.17395 | 0.091552 | 122.3831 | -0.064087 | 122.3419 | 122.374 | 122.2778 | 122.3602 | 122.2824 | -122.4197 | -122.4014 | 122.3694 | 122.3465 | 59.4269 | 59.2438
321.3125 | 122.5983 | -59.2484 | 63.1714 | -0.050583 | 0.0030484 | 0.064657 | 0.058954 | 0.0022644 | -0.003388 | -0.00093566 | -8.6e-08 | 0.00056395 | 0.066943 | 0.057935 | -0.0024866 | 0.0068743 | -0.0043772 | 0 | 63.0661 | -59.2941 | 63.1622 | -59.1614 | -59.5093 | -59.5047 | -0.018311 | 63.0157 | -59.23 | 63.1348 | -59.2987 | -59.4223 | -59.3399 | -0.045776 | -0.10529 | -0.009156 | 0.086975 | -0.25635 | -0.26093 | -0.21057 | -0.21515 | 0.01831 | -0.15564 | -0.036621 | -0.050354 | -0.091553 | -0.17395 | -0.10986 | -0.19226 | 0.13275 | 122.4564 | -0.068664 | 122.3648 | 122.3602 | 122.2458 | 122.3145 | 122.2641 | -122.4655 | -122.4014 | 122.4106 | 122.3831 | 59.2484 | 59.23
322.3125 | 122.5525 | -59.2575 | 63.1348 | -0.012436 | 0.0019802 | 0.065939 | 0.062799 | 0.0011962 | -0.0025336 | 0.00098694 | -0.039673 | 0.0035547 | 0.067798 | 0.059857 | -0.0027002 | 0.0070879 | 0.000109 | -0.041199 | 63.0203 | -59.3399 | 63.121 | -59.2026 | -59.5963 | -59.5551 | -0.14648 | 62.9929 | -59.2758 | 63.0936 | -59.3674 | -59.5093 | -59.404 | -0.082398 | -0.11444 | -0.013733 | 0.054931 | -0.29755 | -0.33875 | -0.21515 | -0.25635 | -0.018311 | -0.14191 | -0.041199 | -0.10986 | -0.14649 | -0.25177 | -0.12817 | -0.23346 | 0.13733 | 122.4609 | -0.091553 | 122.3694 | 122.3602 | 122.2687 | 122.2778 | 122.2504 | -122.4747 | -122.4106 | 122.3785 | 122.3511 | 59.2163 | 59.111
323.3125 | 122.6807 | -59.2072 | 63.1256 | -0.035324 | 0.0043302 | 0.061026 | 0.059595 | -0.0013672 | -0.0031744 | -0.0020039 | 0.064087 | 0.00056395 | 0.068011 | 0.059644 | -0.0041956 | 0.0055927 | -0.0028818 | 0.041199 | 62.9974 | -59.2667 | 63.2629 | -59.0149 | -59.3994 | -59.3857 | 0.13275 | 62.9608 | -59.1797 | 63.2217 | -59.1751 | -59.2758 | -59.2392 | -0.05951 | -0.12817 | 0.13733 | 0.19226 | -0.17853 | -0.19226 | -0.11902 | -0.13275 | 0.027466 | -0.1648 | 0.096131 | 0.032043 | -0.032044 | -0.068665 | -0.05951 | -0.096131 | 0.25177 | 122.5296 | 0.004577 | 122.4014 | 122.2641 | 122.1405 | 122.2046 | 122.168 | -122.3923 | -122.3053 | 122.4701 | 122.4289 | 59.2484 | 59.3399
324.3125 | 122.5479 | -59.2621 | 63.1668 | 0.03334 | 0.001553 | 0.060599 | 0.063226 | 0.00055542 | -0.0029608 | -8.1264e-05 | -0.033569 | 0.0022729 | 0.066302 | 0.06178 | -0.003982 | 0.0055927 | -0.0020272 | 0.009155 | 63.0707 | -59.2896 | 63.1439 | -59.1568 | -59.523 | -59.5093 | -0.018311 | 62.9929 | -59.2346 | 63.1302 | -59.2804 | -59.4131 | -59.3674 | -0.027466 | -0.09613 | -0.022888 | 0.10529 | -0.24719 | -0.26093 | -0.21973 | -0.23346 | 0.027466 | -0.17395 | -0.036621 | -0.018311 | -0.10529 | -0.15106 | -0.13275 | -0.17853 | 0.13275 | 122.4335 | -0.045777 | 122.3648 | 122.3602 | 122.2275 | 122.3328 | 122.2549 | -122.4564 | -122.4014 | 122.406 | 122.3923 | 59.2712 | 59.2438
325.3125 | 122.5479 | -59.2484 | 63.1348 | -0.027695 | 0.0030484 | 0.06423 | 0.060663 | -0.002008 | -0.003388 | -8.1264e-05 | 0.012207 | 0.0018457 | 0.068011 | 0.058789 | -0.0029138 | 0.0058063 | -0.003309 | 0.032043 | 63.0524 | -59.2667 | 63.1851 | -59.1019 | -59.5001 | -59.5001 | 0.009155 | 63.0203 | -59.2209 | 63.2355 | -59.2163 | -59.6283 | -59.5642 | -0.018311 | -0.082398 | 0.050354 | 0.14648 | -0.25177 | -0.25177 | -0.23346 | -0.23346 | 0.027466 | -0.11444 | 0.10071 | 0.032043 | -0.31586 | -0.37994 | -0.34332 | -0.40741 | 0.16479 | 122.4518 | 0.004577 | 122.4564 | 122.319 | 122.2412 | 122.3007 | 122.2687 | -122.4014 | -122.3557 | 122.4335 | 122.4838 | 59.2804 | 59.2575
326.3125 | 122.6166 | -59.2209 | 63.1531 | -0.050583 | 0.001553 | 0.063803 | 0.060663 | 0.002478 | -0.00061096 | -0.00050846 | -0.015259 | 0.0016321 | 0.064807 | 0.062634 | -0.0035548 | 0.0081561 | -0.0028818 | 0.009155 | 63.0661 | -59.3033 | 63.1622 | -59.1568 | -59.5139 | -59.5001 | 0 | 63.0524 | -59.23 | 63.1348 | -59.2712 | -59.3857 | -59.3353 | -0.082398 | -0.086975 | 0.009155 | 0.064087 | -0.27924 | -0.29297 | -0.19684 | -0.21057 | -0.009156 | -0.10071 | -0.01831 | -0.050354 | -0.11444 | -0.16479 | -0.10529 | -0.15564 | 0.14648 | 122.4655 | -0.041198 | 122.3648 | 122.3694 | 122.2824 | 122.287 | 122.2733 | -122.4564 | -122.3831 | 122.3831 | 122.3557 | 59.23 | 59.2209
327.3125 | 122.6303 | -59.2438 | 63.1577 | -0.050583 | 0.0034756 | 0.065512 | 0.062158 | 0.0037598 | -0.0021064 | -0.00050846 | -0.033569 | 0.0022729 | 0.066302 | 0.061993 | -0.0048364 | 0.0085833 | -0.0013864 | 0.041199 | 63.0386 | -59.3033 | 63.208 | -59.0881 | -59.4864 | -59.4864 | 0.041199 | 63.0066 | -59.2209 | 63.1073 | -59.4681 | -59.3033 | -59.2026 | -0.05951 | -0.11902 | 0.050354 | 0.15564 | -0.24262 | -0.24262 | -0.18311 | -0.18311 | 0.022888 | -0.15106 | -0.050354 | -0.22431 | 0.041198 | -0.05951 | 0.01831 | -0.082398 | 0.21515 | 122.5113 | -0.24719 | 122.3282 | 122.3419 | 122.2275 | 122.2824 | 122.2504 | -122.4609 | -122.3785 | 122.4518 | 122.3511 | 59.285 | 59.285
328.3125 | 122.5388 | -59.2392 | 63.1577 | -0.0048066 | 0.0024076 | 0.064444 | 0.060876 | 0.0029052 | -0.0021064 | -8.1264e-05 | 0.027466 | 0.00056395 | 0.067798 | 0.063061 | -0.003982 | 0.0053789 | 0.000109 | 0.054932 | 63.0386 | -59.2621 | 63.2172 | -59.0836 | -59.4543 | -59.4589 | 0.022888 | 63.0066 | -59.2255 | 63.121 | -59.2896 | -59.404 | -59.3582 | -0.022888 | -0.11902 | 0.059509 | 0.15564 | -0.21973 | -0.21515 | -0.19684 | -0.19226 | 0.013733 | -0.15106 | -0.036621 | -0.050354 | -0.11902 | -0.1648 | -0.13275 | -0.17853 | 0.17853 | 122.4792 | -0.064087 | 122.3465 | 122.3007 | 122.2321 | 122.2778 | 122.2458 | -122.4197 | -122.3831 | 122.4564 | 122.3602 | 59.2941 | 59.2621
329.3125 | 122.5983 | -59.2484 | 63.1622 | -0.058212 | 0.0002714 | 0.064444 | 0.060449 | 0.0029052 | -0.0021064 | -0.0011493 | -0.030517 | 0.0033411 | 0.067157 | 0.067548 | -0.005691 | 0.0060199 | 0.0024588 | 0.009155 | 63.0569 | -59.3124 | 63.1668 | -59.1248 | -59.491 | -59.4772 | 0.054932 | 63.0066 | -59.198 | 63.1577 | -59.2667 | -59.4086 | -59.3308 | -0.064087 | -0.10528 | 0.004578 | 0.1236 | -0.22888 | -0.24262 | -0.1648 | -0.17853 | 0.050354 | -0.15564 | -0.004577 | -0.018311 | -0.082398 | -0.16022 | -0.13275 | -0.21057 | 0.18768 | 122.4792 | -0.068665 | 122.3557 | 122.3694 | 122.2046 | 122.3053 | 122.2549 | -122.4747 | -122.3602 | 122.4152 | 122.406 | 59.2575 | 59.3033
330.3125 | 122.5296 | -59.2392 | 63.1622 | -0.042954 | 0.0024076 | 0.063376 | 0.060235 | -0.00093998 | -0.0010382 | 0.0020551 | -0.073242 | 0.0031273 | 0.068011 | 0.058362 | -0.005691 | 0.0060199 | -0.0009592 | -0.009155 | 63.0386 | -59.3033 | 63.1622 | -59.0881 | -59.23 | -59.5642 | 0.032043 | 63.002 | -59.2575 | 63.1165 | -59.2896 | -59.4177 | -59.3491 | -0.064087 | -0.1236 | 0 | 0.15106 | -0.32501 | 0.009155 | -0.26093 | 0.073242 | -0.01831 | -0.16022 | -0.045776 | -0.050354 | -0.10986 | -0.17853 | -0.091553 | -0.16022 | 0.21515 | 122.4655 | -0.032044 | 122.374 | 122.3419 | 122.2595 | 122.2778 | 122.2412 | -122.4655 | -122.4197 | 122.4014 | 122.3557 | 59.23 | 59.2712
331.3125 | 122.6166 | -59.2529 | 63.1668 | -0.042954 | 0.003262 | 0.062308 | 0.060876 | 0.0014098 | -0.0029608 | -0.0020039 | -0.030517 | 0.0031273 | 0.068011 | 0.060925 | -0.0035548 | 0.0079425 | -0.0009592 | 0.004578 | 63.0386 | -59.3124 | 63.1851 | -59.1248 | -59.5047 | -59.4818 | 0.018311 | 63.0066 | -59.23 | 63.1439 | -59.2575 | -59.3811 | -59.3124 | -0.059509 | -0.12817 | 0.018311 | 0.12817 | -0.22888 | -0.25177 | -0.16937 | -0.19226 | 0.022888 | -0.16022 | -0.022888 | -0.004577 | -0.059509 | -0.12817 | -0.082397 | -0.15106 | 0.18768 | 122.4976 | -0.027465 | 122.374 | 122.3511 | 122.2366 | 122.2916 | 122.2595 | -122.4792 | -122.3969 | 122.4381 | 122.3969 | 59.2575 | 59.2712
332.3125 | 122.5845 | -59.2438 | 63.1256 | -0.081101 | 0.0030484 | 0.061453 | 0.060876 | 0.002478 | -0.0029608 | -0.0015765 | -0.045776 | 0.0031273 | 0.066516 | 0.068188 | -0.003982 | 0.0060199 | 0.0003226 | 0.004578 | 63.0432 | -59.3124 | 63.176 | -59.1339 | -59.5184 | -59.5047 | -0.004578 | 62.9837 | -59.2529 | 63.1439 | -59.2896 | -59.4131 | -59.3399 | -0.068665 | -0.082397 | 0.050354 | 0.10986 | -0.26093 | -0.27466 | -0.19226 | -0.20599 | -0.009156 | -0.14191 | 0.018311 | -0.045777 | -0.096131 | -0.16937 | -0.086975 | -0.16022 | 0.17853 | 122.4884 | -0.036621 | 122.3969 | 122.3557 | 122.2366 | 122.287 | 122.2275 | -122.438 | -122.3785 | 122.4197 | 122.3877 | 59.2484 | 59.2392
333.3125 | 122.5708 | -59.2438 | 63.1531 | -0.058212 | 0.0028348 | 0.062308 | 0.060022 | -0.0045716 | -0.0016792 | -0.00050846 | 0.024414 | 0.0014185 | 0.067798 | 0.051526 | -0.0041956 | 0.0036699 | -0.0026682 | 0.027466 | 63.0615 | -59.2987 | 63.1577 | -59.1431 | -59.5139 | -59.4818 | 0 | 63.0066 | -59.2346 | 63.2401 | -59.2758 | -59.642 | -59.5505 | -0.054932 | -0.091553 | 0.004578 | 0.10071 | -0.23804 | -0.27008 | -0.18311 | -0.21515 | 0.009155 | -0.14648 | 0.086975 | -0.032044 | -0.3067 | -0.39825 | -0.31586 | -0.40741 | 0.15564 | 122.4564 | -0.041199 | 122.4747 | 122.3602 | 122.2412 | 122.3053 | 122.2504 | -122.4518 | -122.3877 | 122.4014 | 122.4838 | 59.2712 | 59.2438
334.3125 | 122.5891 | -59.2438 | 63.1531 | -0.073471 | 0.0036892 | 0.06423 | 0.063653 | -0.0022218 | -0.0038154 | -0.0017903 | -0.027466 | 0.0014185 | 0.066302 | 0.062848 | -0.0031274 | 0.0083697 | -0.0007456 | 0.022888 | 63.0249 | -59.2896 | 63.1805 | -59.1019 | -59.5001 | -59.5001 | 0.013733 | 63.002 | -59.2117 | 63.1393 | -59.2896 | -59.4315 | -59.3445 | -0.045777 | -0.12817 | 0.027466 | 0.14191 | -0.25635 | -0.25635 | -0.21057 | -0.21057 | 0.032043 | -0.15106 | -0.013733 | -0.045777 | -0.10071 | -0.18768 | -0.13275 | -0.21973 | 0.18768 | 122.4701 | -0.07782 | 122.3511 | 122.3145 | 122.2137 | 122.2687 | 122.2458 | -122.4426 | -122.3648 | 122.4243 | 122.3831 | 59.2667 | 59.2575
335.3125 | 122.5571 | -59.23 | 63.1714 | -0.065842 | 0.0026212 | 0.064444 | 0.059595 | -0.002008 | -0.0025336 | -0.00093566 | 0.036621 | 0.0020593 | 0.068011 | 0.064984 | -0.0037684 | 0.0058063 | -0.0011728 | 0.041199 | 63.0432 | -59.2804 | 63.1805 | -59.1248 | -59.4818 | -59.4727 | 0.013733 | 63.0295 | -59.2072 | 63.1165 | -59.2987 | -59.3903 | -59.3491 | -0.050354 | -0.12817 | 0.009155 | 0.10529 | -0.24261 | -0.25177 | -0.19226 | -0.20142 | 0.022889 | -0.14191 | -0.054932 | -0.068664 | -0.11902 | -0.16022 | -0.14191 | -0.18311 | 0.15564 | 122.4609 | -0.091553 | 122.3236 | 122.3236 | 122.2366 | 122.2733 | 122.2595 | -122.4518 | -122.3785 | 122.4106 | 122.3465 | 59.2712 | 59.2438
336.3125 | 122.5525 | -59.2484 | 63.176 | 0.086746 | 0.0028348 | 0.062308 | 0.059808 | -0.0028626 | -0.00018376 | -0.0015765 | -0.0030517 | 0.0024865 | 0.068225 | 0.05943 | -0.0041956 | 0.0077289 | -0.0009592 | -0.11444 | 63.089 | -59.3262 | 63.1302 | -59.166 | -59.5459 | -59.5001 | -0.018311 | 63.0066 | -59.2163 | 63.1073 | -59.2941 | -59.4086 | -59.3353 | -0.07782 | -0.086975 | -0.045776 | 0.082397 | -0.25177 | -0.29755 | -0.17395 | -0.21973 | 0.032043 | -0.16937 | -0.068664 | -0.045776 | -0.086975 | -0.16022 | -0.11902 | -0.19226 | 0.16022 | 122.4564 | -0.077819 | 122.3236 | 122.4152 | 122.2229 | 122.3373 | 122.2549 | -122.5021 | -122.3923 | 122.3785 | 122.3557 | 59.1339 | 59.23
337.3125 | 122.5708 | -59.2529 | 63.1668 | 0.03334 | 0.0026212 | 0.063589 | 0.061303 | -0.0022218 | -0.004029 | -0.0011493 | -0.012207 | 0.0037683 | 0.068225 | 0.068188 | -0.0041956 | 0.0047381 | -0.0013864 | 0.086975 | 63.0798 | -59.2575 | 63.1348 | -59.1797 | -59.491 | -59.5001 | -0.009155 | 63.0432 | -59.2346 | 63.1119 | -59.3124 | -59.4223 | -59.3491 | -0.004577 | -0.086975 | -0.032043 | 0.073243 | -0.24719 | -0.23804 | -0.24262 | -0.23346 | 0.018311 | -0.1236 | -0.054932 | -0.059509 | -0.09613 | -0.16937 | -0.11444 | -0.18768 | 0.07782 | 122.3923 | -0.07782 | 122.3465 | 122.3373 | 122.2778 | 122.3328 | 122.2961 | -122.4243 | -122.4014 | 122.3877 | 122.3648 | 59.3399 | 59.2438
338.3125 | 122.5891 | -59.2392 | 63.208 | -0.042954 | 0.0019802 | 0.064657 | 0.061303 | 0.00076902 | -0.0046698 | -0.0020039 | -0.0061035 | 0.0020593 | 0.068652 | 0.06712 | -0.0046228 | 0.0060199 | -0.0043772 | 0.013733 | 63.0661 | -59.3033 | 63.1577 | -59.166 | -59.5093 | -59.4955 | -0.027466 | 63.0112 | -59.23 | 63.1256 | -59.2804 | -59.4177 | -59.3308 | -0.064087 | -0.14191 | -0.050354 | 0.073242 | -0.25635 | -0.27008 | -0.19226 | -0.20599 | 0.009155 | -0.19684 | -0.082398 | -0.041199 | -0.091553 | -0.17853 | -0.10071 | -0.18768 | 0.13733 | 122.4609 | -0.050354 | 122.3557 | 122.3694 | 122.2412 | 122.3053 | 122.2504 | -122.5113 | -122.4381 | 122.3969 | 122.3648 | 59.2529 | 59.2117
339.3125 | 122.5708 | -59.2438 | 63.1393 | -0.042954 | 0.0039028 | 0.064871 | 0.062799 | 0.00034182 | -0.0027472 | 0.0026959 | -0.030517 | 0.0033411 | 0.067157 | 0.064984 | -0.0041956 | 0.0073015 | -0.0009592 | 0.004578 | 63.0112 | -59.3262 | 63.1668 | -59.1385 | -59.523 | -59.5276 | -0.022888 | 63.0295 | -59.2667 | 63.1302 | -59.3033 | -59.4589 | -59.3719 | -0.082398 | -0.12817 | 0.027466 | 0.10529 | -0.28381 | -0.27924 | -0.20142 | -0.19684 | -0.022889 | -0.10986 | -0.009155 | -0.05951 | -0.12817 | -0.21515 | -0.10529 | -0.19226 | 0.18768 | 122.493 | -0.036621 | 122.3969 | 122.3373 | 122.2961 | 122.2549 | 122.2733 | -122.4655 | -122.406 | 122.4106 | 122.374 | 59.2484 | 59.2209
340.3125 | 122.5845 | -59.2392 | 63.1897 | -0.012436 | 0.0045438 | 0.062735 | 0.061303 | 0.0039734 | -0.0029608 | -8.1264e-05 | -0.0030517 | 0.0039819 | 0.067798 | 0.060712 | -0.0035548 | 0.0083697 | -0.0020272 | 0 | 63.0661 | -59.3079 | 63.1348 | -59.1614 | -59.5184 | -59.491 | -0.013733 | 63.0203 | -59.2346 | 63.1165 | -59.2896 | -59.3994 | -59.3445 | -0.068664 | -0.1236 | -0.054931 | 0.07782 | -0.25177 | -0.27924 | -0.18311 | -0.21057 | 0.004578 | -0.16937 | -0.073242 | -0.050354 | -0.10529 | -0.16022 | -0.10986 | -0.16479 | 0.14648 | 122.4426 | -0.054932 | 122.3511 | 122.374 | 122.2549 | 122.3053 | 122.2595 | -122.4976 | -122.4243 | 122.374 | 122.3557 | 59.2392 | 59.2255
341.3125 | 122.6028 | -59.2255 | 63.1531 | -0.012436 | 5.76e-05 | 0.065298 | 0.060449 | 0.0014098 | -0.00018376 | 0.00034614 | 0.05188 | 0.0014185 | 0.068011 | 0.064984 | -0.0054774 | 0.0060199 | -0.0013864 | 0.009155 | 63.0432 | -59.3079 | 63.1897 | -59.0607 | -59.8022 | -59.6054 | 0.027466 | 63.0157 | -59.2438 | 63.176 | -59.2529 | -59.3719 | -59.3033 | -0.082397 | -0.10986 | 0.036621 | 0.1648 | -0.37994 | -0.57678 | -0.29755 | -0.49438 | -0.01831 | -0.13733 | 0.022888 | -0.027466 | -0.07782 | -0.14648 | -0.05951 | -0.12817 | 0.24719 | 122.4976 | -0.009156 | 122.4197 | 122.3511 | 122.2595 | 122.2687 | 122.2412 | -122.4609 | -122.3969 | 122.4152 | 122.4014 | 59.2346 | 59.2529
342.3125 | 122.5662 | -59.2712 | 63.1256 | -0.012436 | 0.0030484 | 0.063589 | 0.061731 | 0.0014098 | 0.00088444 | -0.0011493 | -0.036621 | 0.0018457 | 0.066729 | 0.066052 | -0.0059046 | 0.0066607 | -0.0024546 | -0.10071 | 63.0386 | -59.3628 | 62.8967 | -58.9371 | -59.2712 | -59.5139 | -0.11444 | 63.0157 | -59.2438 | 63.0936 | -59.3582 | -59.523 | -59.4131 | -0.091553 | -0.086975 | -0.22888 | 0.33417 | -0.24262 | 0 | -0.15106 | 0.091553 | 0.027466 | -0.10986 | -0.032043 | -0.086975 | -0.14191 | -0.25177 | -0.16937 | -0.27924 | 0.42572 | 122.2595 | -0.11444 | 122.3373 | 122.4014 | 122.2595 | 122.3099 | 122.287 | -122.4884 | -122.3694 | 122.168 | 122.3648 | 59.1705 | 59.1568
343.3125 | 122.6578 | -59.2163 | 63.1393 | -0.027695 | 0.0024076 | 0.064016 | 0.058954 | -0.00093998 | -0.0029608 | -0.0022175 | 0.067139 | 0.0018457 | 0.066943 | 0.058148 | -0.0044092 | 0.0068743 | -0.0007456 | 0.068665 | 63.0157 | -59.2484 | 63.2492 | -59.0286 | -59.404 | -59.3857 | 0.10529 | 62.9837 | -59.2163 | 63.1989 | -59.2117 | -59.3308 | -59.285 | -0.032043 | -0.1236 | 0.10986 | 0.18768 | -0.16937 | -0.18768 | -0.13733 | -0.15564 | 0 | -0.15564 | 0.05951 | 0.004578 | -0.068664 | -0.11444 | -0.068664 | -0.11444 | 0.21973 | 122.4976 | 0.004578 | 122.4152 | 122.2641 | 122.2 | 122.2321 | 122.2 | -122.3877 | -122.3557 | 122.4655 | 122.4152 | 59.285 | 59.3216
344.3125 | 122.5983 | -59.2392 | 63.1714 | -0.042954 | 0.0017666 | 0.062948 | 0.062799 | -0.00093998 | -0.0014654 | -0.0017903 | -0.024414 | 0.00077755 | 0.068438 | 0.063916 | -0.00505 | 0.0094379 | -0.0016 | 0.013733 | 63.0432 | -59.2987 | 63.1439 | -59.1522 | -59.5139 | -59.5047 | -0.013733 | 63.0203 | -59.2438 | 63.1256 | -59.2758 | -59.404 | -59.3308 | -0.059509 | -0.12817 | -0.027466 | 0.086975 | -0.2655 | -0.27466 | -0.20599 | -0.21515 | -0.004577 | -0.15106 | -0.045777 | -0.036621 | -0.091553 | -0.1648 | -0.086976 | -0.16022 | 0.14648 | 122.4426 | -0.032044 | 122.3694 | 122.3419 | 122.2641 | 122.2824 | 122.2595 | -122.4701 | -122.4152 | 122.3831 | 122.3648 | 59.2529 | 59.2255
345.3125 | 122.5525 | -59.2667 | 63.1577 | -0.020065 | 0.0019802 | 0.062735 | 0.059381 | 0.00055542 | -0.00061096 | -0.0024311 | 0.036621 | 0.0020593 | 0.066943 | 0.054303 | -0.0029138 | 0.0081561 | 0.0007498 | -0.013733 | 63.0707 | -59.285 | 63.1485 | -59.1202 | -59.5184 | -59.5047 | -0.027466 | 63.0341 | -59.2438 | 63.1119 | -59.3079 | -59.4223 | -59.3811 | -0.01831 | -0.086975 | -0.009155 | 0.14648 | -0.23804 | -0.25177 | -0.21973 | -0.23346 | 0.022889 | -0.1236 | -0.045777 | -0.041198 | -0.11444 | -0.15564 | -0.13733 | -0.17853 | 0.16479 | 122.4335 | -0.064087 | 122.3557 | 122.3557 | 122.2778 | 122.3373 | 122.3007 | -122.4426 | -122.4014 | 122.4152 | 122.3785 | 59.2529 | 59.2392
346.3125 | 122.5708 | -59.2346 | 63.1943 | 0.025711 | 0.0002714 | 0.063589 | 0.059595 | -0.0041444 | -0.00018376 | -0.00072206 | -0.0030517 | 0.0012047 | 0.067584 | 0.063275 | -0.0018458 | 0.0049517 | -0.0013864 | 0.022888 | 63.0569 | -59.2987 | 63.1485 | -59.1568 | -59.5139 | -59.5001 | -0.013733 | 63.0432 | -59.2255 | 63.121 | -59.285 | -59.404 | -59.3445 | -0.064087 | -0.13733 | -0.045776 | 0.07782 | -0.2655 | -0.27924 | -0.20142 | -0.21515 | 0.009155 | -0.15106 | -0.073242 | -0.050354 | -0.10986 | -0.16937 | -0.11902 | -0.17853 | 0.14191 | 122.4472 | -0.059509 | 122.3465 | 122.3557 | 122.2687 | 122.2916 | 122.2778 | -122.493 | -122.4197 | 122.3831 | 122.3557 | 59.2575 | 59.2209
347.3125 | 122.5433 | -59.2758 | 63.1256 | 0.071487 | 0.0013394 | 0.065298 | 0.063653 | 0.0014098 | -0.0036018 | -0.00050846 | -0.027466 | 0.0016321 | 0.065875 | 0.060498 | -0.0018458 | 0.0068743 | -0.0024546 | 0.036621 | 63.0524 | -59.3216 | 63.1165 | -59.2163 | -59.5825 | -59.5551 | -0.16022 | 62.9883 | -59.2575 | 63.0844 | -59.3582 | -59.5001 | -59.3765 | -0.045776 | -0.073242 | -0.009155 | 0.059509 | -0.27924 | -0.3067 | -0.23346 | -0.26093 | 0.018311 | -0.13733 | -0.041198 | -0.082397 | -0.10071 | -0.2243 | -0.11902 | -0.24262 | 0.10528 | 122.438 | -0.10071 | 122.3419 | 122.374 | 122.2458 | 122.3282 | 122.2641 | -122.4472 | -122.3831 | 122.3923 | 122.3602 | 59.3124 | 59.1156
348.3125 | 122.5342 | -59.2255 | 63.1714 | -0.012436 | 0.0034756 | 0.063589 | 0.060235 | -0.0049988 | -0.0012518 | -0.00093566 | -8.6e-08 | 0.0031273 | 0.067584 | 0.061993 | -0.0031274 | 0.0060199 | -0.0039498 | 0.009155 | 63.0844 | -59.285 | 63.1393 | -59.1385 | -59.5184 | -59.5001 | -0.032043 | 63.0249 | -59.2163 | 63.1256 | -59.2987 | -59.4223 | -59.3628 | -0.059509 | -0.086975 | -0.032044 | 0.086975 | -0.27466 | -0.29297 | -0.21515 | -0.23346 | 0.009155 | -0.14649 | -0.045777 | -0.073242 | -0.13733 | -0.19684 | -0.14648 | -0.20599 | 0.14648 | 122.4243 | -0.082397 | 122.3419 | 122.3694 | 122.2412 | 122.3099 | 122.2504 | -122.4564 | -122.3877 | 122.3648 | 122.3511 | 59.2346 | 59.1934
349.3125 | 122.5891 | -59.2346 | 63.1348 | 0.010452 | 0.0026212 | 0.063376 | 0.061944 | -0.0022218 | -0.0025336 | -0.0015765 | -0.082397 | -0.00050405 | 0.067157 | 0.060925 | -0.003341 | 0.0068743 | -0.005018 | 0.045776 | 63.0341 | -59.317 | 63.1897 | -59.1019 | -59.4955 | -59.5825 | 0.13733 | 63.0112 | -59.2209 | 63.1714 | -59.2484 | -59.3811 | -59.3216 | -0.082398 | -0.10071 | 0.054931 | 0.13275 | -0.3479 | -0.26093 | -0.2655 | -0.17853 | 0.013733 | -0.1236 | 0.036621 | -0.013733 | -0.086975 | -0.14648 | -0.10071 | -0.16022 | 0.21515 | 122.5067 | -0.027466 | 122.3923 | 122.3511 | 122.2321 | 122.2687 | 122.2458 | -122.4518 | -122.3557 | 122.4243 | 122.406 | 59.2804 | 59.3719
350.3125 | 122.4655 | -59.2484 | 63.1302 | -0.0048066 | 0.0026212 | 0.062948 | 0.060022 | 0.0014098 | -0.0029608 | -0.0024311 | 0.024414 | 0.0035547 | 0.068438 | 0.058789 | -0.003341 | 0.0055927 | -0.0007456 | 0.041199 | 63.0432 | -59.2712 | 63.1668 | -59.1156 | -59.4589 | -59.4681 | 0.009155 | 63.0295 | -59.2484 | 63.002 | -59.1934 | -59.1614 | -59.3491 | -0.022888 | -0.086975 | 0.036621 | 0.13275 | -0.21973 | -0.21057 | -0.19684 | -0.18768 | 0 | -0.10071 | -0.12817 | 0.054932 | -0.10071 | 0.086975 | -0.10071 | 0.086975 | 0.15564 | 122.438 | 0.054932 | 122.2504 | 122.3145 | 122.2778 | 122.2916 | 122.2778 | -122.4014 | -122.3785 | 122.4152 | 122.2504 | 59.2896 | 59.2575
351.3125 | 122.5845 | -59.2392 | 63.1622 | -0.0048066 | 0.0009122 | 0.063376 | 0.061303 | 0.00076902 | -0.003388 | -0.0011493 | 0.0061035 | 0.0031273 | 0.068652 | 0.062634 | -0.0046228 | 0.0070879 | -0.000532 | 0 | 63.0569 | -59.3216 | 63.1393 | -59.1568 | -59.5047 | -59.4955 | -0.036621 | 63.0386 | -59.23 | 63.1073 | -59.2941 | -59.4315 | -59.3674 | -0.082397 | -0.10528 | -0.022888 | 0.082398 | -0.25635 | -0.2655 | -0.17395 | -0.18311 | 0.009155 | -0.1236 | -0.054931 | -0.054931 | -0.12817 | -0.19226 | -0.13733 | -0.20142 | 0.16479 | 122.4609 | -0.064086 | 122.3373 | 122.3785 | 122.2687 | 122.2961 | 122.2778 | -122.4838 | -122.3923 | 122.3785 | 122.3465 | 59.2392 | 59.2026
352.3125 | 122.5708 | -59.2346 | 63.176 | 0.04097 | 0.001553 | 0.063589 | 0.060663 | -0.0015808 | -0.003388 | -8.1264e-05 | -0.0030517 | 0.0018457 | 0.06737 | 0.060712 | -0.0035548 | 0.0077289 | -0.006727 | -0.16022 | 63.0524 | -59.317 | 63.1439 | -59.166 | -59.523 | -59.5093 | -0.004578 | 63.0524 | -59.2255 | 63.1073 | -59.285 | -59.4086 | -59.3262 | -0.082398 | -0.1236 | -0.032043 | 0.068664 | -0.27466 | -0.28839 | -0.19226 | -0.20599 | 0.009155 | -0.1236 | -0.068664 | -0.050354 | -0.091553 | -0.17395 | -0.10071 | -0.1831 | 0.15106 | 122.4609 | -0.059509 | 122.3328 | 122.3694 | 122.2778 | 122.287 | 122.287 | -122.493 | -122.4014 | 122.3785 | 122.3419 | 59.0744 | 59.23
353.3125 | 122.5754 | -59.2255 | 63.1531 | -0.035324 | 0.0019802 | 0.063589 | 0.06109 | 0.0020508 | -0.0021064 | -0.00072206 | -0.030517 | 0.0029137 | 0.065234 | 0.071393 | -0.0027002 | 0.0053789 | -0.0003182 | 0.004578 | 63.0569 | -59.3216 | 63.1531 | -59.166 | -59.5139 | -59.491 | -0.018311 | 63.0295 | -59.2117 | 63.121 | -59.2804 | -59.4086 | -59.3399 | -0.09613 | -0.09613 | 0 | 0.059509 | -0.2655 | -0.28839 | -0.16937 | -0.19226 | 0.013733 | -0.1236 | -0.032043 | -0.054932 | -0.11444 | -0.1831 | -0.12817 | -0.19684 | 0.15564 | 122.4747 | -0.068665 | 122.3328 | 122.3785 | 122.2412 | 122.2824 | 122.2549 | -122.4747 | -122.3648 | 122.3785 | 122.3465 | 59.23 | 59.2072
354.3125 | 122.5662 | -59.2484 | 63.1393 | -0.020065 | 0.0011258 | 0.063589 | 0.061944 | 0.0035462 | -0.0044562 | 0.00034614 | -0.07019 | 0.0012047 | 0.065448 | 0.063702 | -0.0031274 | 0.0073015 | -0.0035226 | -0.004578 | 63.0203 | -59.3308 | 63.1485 | -59.1339 | -59.5367 | -59.5093 | -0.032043 | 63.0112 | -59.2255 | 63.121 | -59.3124 | -59.4498 | -59.3536 | -0.082398 | -0.11902 | 0.009156 | 0.11444 | -0.26093 | -0.28839 | -0.17853 | -0.20599 | 0.022888 | -0.12817 | -0.01831 | -0.064087 | -0.10529 | -0.20142 | -0.12817 | -0.2243 | 0.19684 | 122.4792 | -0.086975 | 122.3465 | 122.3511 | 122.2366 | 122.2687 | 122.2595 | -122.4701 | -122.3648 | 122.3969 | 122.3694 | 59.2438 | 59.2163
355.3125 | 122.5845 | -59.2209 | 63.1439 | -0.0048066 | 0.0034756 | 0.062521 | 0.059808 | 0.0016236 | 0.0017388 | -0.00029486 | -0.030517 | 0.0018457 | 0.066302 | 0.061139 | -0.00505 | 0.0066607 | -0.0011728 | 0.009155 | 63.0569 | -59.285 | 63.1851 | -59.1339 | -59.4818 | -59.4772 | 0.013733 | 63.0203 | -59.23 | 63.1668 | -59.23 | -59.3948 | -59.3216 | -0.064087 | -0.086975 | 0.041199 | 0.086975 | -0.25635 | -0.26093 | -0.19226 | -0.19684 | -0.009156 | -0.1236 | 0.022888 | -0.009156 | -0.10071 | -0.17395 | -0.091552 | -0.16479 | 0.15106 | 122.4701 | 0 | 122.3969 | 122.3419 | 122.2504 | 122.2778 | 122.2412 | -122.4289 | -122.374 | 122.406 | 122.3877 | 59.23 | 59.2346
356.3125 | 122.58 | -59.23 | 63.1393 | 0.018082 | 0.0028348 | 0.066794 | 0.062585 | 0.002478 | -0.004029 | -0.0013629 | -0.027466 | 0.0031273 | 0.066302 | 0.063061 | -0.0037684 | 0.0073015 | -0.005018 | 0.036621 | 63.0157 | -59.3079 | 63.2217 | -59.3262 | -59.6786 | -59.4086 | 0.013733 | 63.0249 | -59.2346 | 63.1668 | -59.2484 | -59.3811 | -59.3124 | -0.077819 | -0.1236 | 0.082398 | -0.09613 | -0.17853 | -0.44861 | -0.10071 | -0.37079 | -0.004577 | -0.11444 | 0.027466 | -0.01831 | -0.082397 | -0.15106 | -0.07782 | -0.14648 | -0.018311 | 122.5296 | -0.013733 | 122.4014 | 122.3236 | 122.2595 | 122.2458 | 122.2549 | -122.4472 | -122.374 | 122.4518 | 122.3969 | 59.2667 | 59.2438
357.3125 | 122.5754 | -59.2346 | 63.1439 | -0.096359 | 0.0043302 | 0.064657 | 0.061731 | 0.0011962 | -0.0027472 | -0.00072206 | -0.036621 | 0.0018457 | 0.068438 | 0.063061 | -0.003982 | 0.0060199 | -0.0030954 | 0.009155 | 63.0249 | -59.3353 | 63.176 | -59.1202 | -59.5047 | -59.4727 | -0.009155 | 63.0112 | -59.2438 | 63.1485 | -59.2896 | -59.4315 | -59.3216 | -0.10071 | -0.11902 | 0.032043 | 0.11444 | -0.23804 | -0.27008 | -0.13733 | -0.16937 | -0.009155 | -0.13275 | 0.004578 | -0.054932 | -0.086975 | -0.19684 | -0.07782 | -0.18768 | 0.21515 | 122.5113 | -0.045777 | 122.3923 | 122.3602 | 122.2549 | 122.2595 | 122.2458 | -122.4792 | -122.3877 | 122.4106 | 122.3831 | 59.2438 | 59.2255
358.3125 | 122.6166 | -59.2026 | 63.1989 | -0.035324 | 0.0017666 | 0.062948 | 0.059167 | 0.0022644 | -0.0021064 | 0.0012005 | 0.021362 | 0.0012047 | 0.068866 | 0.056866 | -0.0031274 | 0.0066607 | -0.0001046 | 0.027466 | 63.0615 | -59.2758 | 63.1714 | -59.1156 | -59.4589 | -59.4727 | 0.004578 | 63.0295 | -59.2346 | 63.089 | -59.285 | -59.3994 | -59.3719 | -0.073242 | -0.13733 | -0.027466 | 0.086975 | -0.27008 | -0.25635 | -0.19684 | -0.1831 | -0.032043 | -0.16937 | -0.10986 | -0.082397 | -0.16937 | -0.19684 | -0.13733 | -0.16479 | 0.16022 | 122.4472 | -0.050354 | 122.3236 | 122.3373 | 122.2641 | 122.2641 | 122.2321 | -122.4747 | -122.4335 | 122.374 | 122.2916 | 59.23 | 59.2072
359.3125 | 122.5754 | -59.2392 | 63.1256 | -0.058212 | 0.0053982 | 0.065298 | 0.060022 | 0.0046142 | -0.004029 | 0.0020551 | -0.048828 | 0.0033411 | 0.069079 | 0.063275 | -0.00505 | 0.0073015 | -0.0001046 | -0.082397 | 63.0157 | -59.3491 | 63.0844 | -59.2438 | -59.6191 | -59.5917 | -0.42572 | 62.9425 | -59.2941 | 63.1027 | -59.3445 | -59.5322 | -59.3948 | -0.10986 | -0.10986 | -0.041198 | -0.004577 | -0.35248 | -0.37994 | -0.24262 | -0.27008 | -0.054931 | -0.18311 | -0.022888 | -0.10529 | -0.15564 | -0.29297 | -0.10071 | -0.23804 | 0.10529 | 122.4335 | -0.050354 | 122.3969 | 122.3648 | 122.2366 | 122.2549 | 122.1817 | -122.4747 | -122.4197 | 122.3236 | 122.3419 | 59.1568 | 58.8135
360.3125 | 122.5708 | -59.23 | 63.1714 | 0.010452 | 0.0013394 | 0.062735 | 0.057886 | 0.0018372 | -0.0029608 | -0.00093566 | 0.018311 | 0.0027001 | 0.066089 | 0.066907 | -0.0031274 | 0.0062335 | -0.0009592 | 0.041199 | 63.1165 | -59.2758 | 63.1165 | -59.1568 | -59.5184 | -59.5139 | -0.018311 | 63.0203 | -59.2255 | 63.1165 | -59.2758 | -59.4131 | -59.3399 | -0.045776 | -0.054932 | -0.054932 | 0.073243 | -0.28381 | -0.28839 | -0.23804 | -0.24262 | 0.004578 | -0.15106 | -0.054932 | -0.045776 | -0.10986 | -0.18311 | -0.11444 | -0.18768 | 0.11902 | 122.3923 | -0.050354 | 122.3419 | 122.3923 | 122.2458 | 122.3465 | 122.2504 | -122.4472 | -122.3969 | 122.3465 | 122.3465 | 59.2712 | 59.2117
361.3125 | 122.5937 | -59.23 | 63.1714 | 0.03334 | 5.76e-05 | 0.063803 | 0.062158 | -0.00093998 | -0.0025336 | -0.0011493 | -0.021362 | 0.00035035 | 0.065661 | 0.059644 | -0.0059046 | 0.0064471 | -0.0030954 | 0 | 63.0524 | -59.2667 | 63.1439 | -59.1568 | -59.5093 | -59.5001 | -0.032043 | 63.0432 | -59.2209 | 63.1256 | -59.2758 | -59.4086 | -59.3353 | -0.036621 | -0.11902 | -0.027466 | 0.073243 | -0.27008 | -0.27923 | -0.23346 | -0.24261 | 0.009156 | -0.12817 | -0.045777 | -0.045776 | -0.10529 | -0.17853 | -0.11444 | -0.18768 | 0.10986 | 122.4106 | -0.054932 | 122.3465 | 122.319 | 122.2641 | 122.2824 | 122.2733 | -122.4381 | -122.3923 | 122.374 | 122.3557 | 59.23 | 59.198
362.3125 | 122.5891 | -59.23 | 63.1668 | -0.020065 | 0.0030484 | 0.063376 | 0.060449 | 0.0029052 | 0.00067084 | -0.0011493 | 0.0030517 | 0.0024865 | 0.068225 | 0.063489 | -0.0044092 | 0.0073015 | -0.0026682 | 0.004578 | 63.0753 | -59.2896 | 63.1531 | -59.1705 | -59.5001 | -59.5184 | -0.018311 | 63.0295 | -59.2529 | 63.121 | -59.2712 | -59.3994 | -59.3262 | -0.059509 | -0.091553 | -0.013733 | 0.05951 | -0.28839 | -0.27008 | -0.22888 | -0.21057 | -0.022888 | -0.13733 | -0.045776 | -0.041198 | -0.09613 | -0.16937 | -0.073242 | -0.14648 | 0.11902 | 122.4426 | -0.01831 | 122.374 | 122.3648 | 122.2824 | 122.3053 | 122.2595 | -122.4564 | -122.4197 | 122.3831 | 122.3511 | 59.2346 | 59.2117
363.3125 | 122.6074 | -59.2117 | 63.1622 | -0.020065 | 0.0058256 | 0.065725 | 0.061731 | 0.0011962 | -0.0031744 | -0.0013629 | -8.6e-08 | 0.0024865 | 0.069079 | 0.061566 | -0.0065454 | 0.0077289 | -0.0030954 | 0.027466 | 63.0478 | -59.3262 | 63.1714 | -59.1248 | -59.4864 | -59.4727 | 0.032043 | 62.9974 | -59.2346 | 63.1577 | -59.2621 | -59.3948 | -59.3124 | -0.11444 | -0.11444 | 0.009156 | 0.086975 | -0.26093 | -0.27466 | -0.14648 | -0.16022 | -0.022888 | -0.16479 | -0.004577 | -0.050354 | -0.10071 | -0.1831 | -0.07782 | -0.16022 | 0.20142 | 122.4976 | -0.027466 | 122.3923 | 122.374 | 122.2321 | 122.2595 | 122.2092 | -122.4884 | -122.3969 | 122.3831 | 122.3694 | 59.2392 | 59.2438
364.3125 | 122.5433 | -59.2758 | 63.1119 | 0.0028229 | -0.0007968 | 0.061026 | 0.060876 | 0.0026916 | -0.0027472 | 0.00098694 | -0.01831 | 0.0020593 | 0.068652 | 0.067975 | -0.0029138 | 0.0062335 | 0.0003226 | 0.086975 | 63.0661 | -59.3124 | 63.0844 | -59.2163 | -59.5779 | -59.5459 | -0.14191 | 62.9791 | -59.2392 | 63.089 | -59.3628 | -59.5093 | -59.3903 | -0.036621 | -0.045776 | -0.027465 | 0.059509 | -0.27008 | -0.30212 | -0.23346 | -0.2655 | 0.036621 | -0.13275 | -0.022888 | -0.086975 | -0.11444 | -0.23346 | -0.15106 | -0.27008 | 0.09613 | 122.3969 | -0.1236 | 122.3282 | 122.3785 | 122.2183 | 122.3419 | 122.2549 | -122.4243 | -122.3511 | 122.3602 | 122.3648 | 59.3628 | 59.1339
365.3125 | 122.5479 | -59.23 | 63.1714 | 0.04097 | 0.0019802 | 0.062735 | 0.060022 | -0.0015808 | -0.0016792 | -0.0015765 | 0.015259 | 0.0024865 | 0.065875 | 0.059644 | -0.002273 | 0.0060199 | 0.000109 | 0.009155 | 63.0615 | -59.2804 | 63.1348 | -59.1385 | -59.5184 | -59.4864 | 0.22888 | 63.0798 | -59.2117 | 63.0936 | -59.285 | -59.4131 | -59.3765 | -0.050354 | -0.10986 | -0.036621 | 0.091553 | -0.25635 | -0.28839 | -0.20599 | -0.23804 | 0.018311 | -0.091553 | -0.07782 | -0.054931 | -0.14648 | -0.18311 | -0.16479 | -0.20142 | 0.14191 | 122.4152 | -0.073242 | 122.3053 | 122.3419 | 122.2916 | 122.2916 | 122.3099 | -122.4518 | -122.3831 | 122.3648 | 122.3236 | 59.2392 | 59.4589
366.3125 | 122.5479 | -59.2346 | 63.176 | -0.012436 | 0.002194 | 0.062308 | 0.059381 | -0.0039306 | -0.0025336 | -0.0039265 | -0.021362 | 0.0029137 | 0.068652 | 0.061566 | -0.0031274 | 0.0045245 | -0.0024546 | 0.004578 | 63.0707 | -59.2896 | 63.1439 | -59.166 | -59.4864 | -59.491 | -0.013733 | 63.0249 | -59.2484 | 63.0936 | -59.2941 | -59.4315 | -59.3445 | -0.054932 | -0.10529 | -0.032043 | 0.068664 | -0.25635 | -0.25177 | -0.20142 | -0.19684 | -0.013733 | -0.15106 | -0.082397 | -0.059509 | -0.10986 | -0.19684 | -0.09613 | -0.18311 | 0.1236 | 122.4335 | -0.045776 | 122.3419 | 122.3602 | 122.2733 | 122.3053 | 122.2595 | -122.4655 | -122.4243 | 122.3785 | 122.3282 | 59.2392 | 59.2209
367.3125 | 122.58 | -59.2712 | 63.1073 | -0.058212 | 0.0013394 | 0.06658 | 0.061944 | -0.00093998 | -0.0012518 | -0.0011493 | -0.024414 | 0.0027001 | 0.067584 | 0.064343 | -0.0037684 | 0.0070879 | -0.000532 | -0.082397 | 62.9929 | -59.3674 | 63.1073 | -59.1934 | -59.6008 | -59.5551 | -0.13275 | 63.002 | -59.2758 | 63.1027 | -59.3308 | -59.4452 | -59.3582 | -0.096131 | -0.11444 | 0 | 0.07782 | -0.28381 | -0.32959 | -0.18768 | -0.23346 | -0.004578 | -0.10529 | -0.004578 | -0.05951 | -0.086975 | -0.17395 | -0.082397 | -0.16937 | 0.17395 | 122.4747 | -0.054932 | 122.3785 | 122.3602 | 122.2778 | 122.2641 | 122.2733 | -122.4747 | -122.3831 | 122.3785 | 122.374 | 59.1888 | 59.1385
368.3125 | 122.5983 | -59.2117 | 63.1485 | -0.012436 | 0.002194 | 0.062735 | 0.059595 | 0.00098262 | -0.0012518 | -0.0024311 | 0.0030517 | 0.0014185 | 0.064807 | 0.062634 | -0.00505 | 0.0085833 | -0.000532 | 0.004578 | 63.0569 | -59.2758 | 63.1485 | -59.1431 | -59.491 | -59.4727 | 0 | 63.0157 | -59.2255 | 63.1531 | -59.2484 | -59.3857 | -59.3033 | -0.064087 | -0.091553 | 0 | 0.068665 | -0.26093 | -0.27924 | -0.19684 | -0.21515 | -0.013733 | -0.13275 | 0.004577 | -0.036621 | -0.091553 | -0.17395 | -0.07782 | -0.16022 | 0.13275 | 122.4243 | -0.022888 | 122.3785 | 122.3328 | 122.2412 | 122.2687 | 122.2275 | -122.4243 | -122.374 | 122.3602 | 122.3648 | 59.2163 | 59.2117
369.3125 | 122.5571 | -59.2621 | 63.0936 | -0.11162 | 0.0017666 | 0.064444 | 0.061944 | 0.0014098 | -0.004029 | 0.0022687 | -0.036621 | 0.0020593 | 0.065875 | 0.064557 | -0.00505 | 0.0066607 | 0.0026724 | -0.086975 | 63.0295 | -59.3353 | 63.0798 | -59.2026 | -59.5963 | -59.5642 | -0.14191 | 62.9654 | -59.2621 | 63.0981 | -59.3262 | -59.4543 | -59.3719 | -0.073242 | -0.064087 | -0.013733 | 0.059509 | -0.30212 | -0.33417 | -0.22888 | -0.26093 | 0 | -0.12817 | 0.004578 | -0.064087 | -0.10986 | -0.19226 | -0.10986 | -0.19226 | 0.13275 | 122.4152 | -0.064087 | 122.3602 | 122.3648 | 122.2275 | 122.2916 | 122.2275 | -122.4289 | -122.3557 | 122.3419 | 122.3602 | 59.1751 | 59.1202
370.3125 | 122.644 | -59.2392 | 63.0981 | -0.081101 | 0.0013394 | 0.064444 | 0.05874 | 0.0018372 | -0.005097 | 0.00098694 | 0.045776 | 0.0018457 | 0.067157 | 0.062634 | -0.003982 | 0.0070879 | -0.0009592 | -0.018311 | 62.9837 | -59.2896 | 63.208 | -59.0515 | -59.4635 | -59.4406 | 0.013733 | 62.9654 | -59.23 | 63.1943 | -59.2255 | -59.3399 | -59.2667 | -0.050354 | -0.11444 | 0.10986 | 0.18768 | -0.20142 | -0.2243 | -0.15106 | -0.17395 | 0.009155 | -0.13275 | 0.09613 | 0.013733 | -0.027466 | -0.10071 | -0.036621 | -0.10986 | 0.23804 | 122.4976 | 0.004578 | 122.4243 | 122.2733 | 122.1954 | 122.2229 | 122.2046 | -122.3877 | -122.3282 | 122.4472 | 122.4335 | 59.2209 | 59.2529
371.3125 | 122.5937 | -59.2209 | 63.1439 | -0.058212 | 0.0017666 | 0.063803 | 0.060449 | -0.0022218 | -0.0021064 | -0.0022175 | -0.024414 | 0.00013675 | 0.066516 | 0.062207 | -0.0048364 | 0.0058063 | -0.0013864 | -0.004578 | 63.0615 | -59.3079 | 63.1348 | -59.166 | -59.5093 | -59.4772 | -0.009155 | 63.0386 | -59.2255 | 63.1256 | -59.2712 | -59.3948 | -59.3262 | -0.086975 | -0.082398 | -0.009155 | 0.054931 | -0.25635 | -0.28839 | -0.16937 | -0.20142 | -0.004578 | -0.10529 | -0.018311 | -0.050354 | -0.10529 | -0.17395 | -0.10071 | -0.16937 | 0.14191 | 122.4426 | -0.045776 | 122.3511 | 122.3694 | 122.2641 | 122.2824 | 122.2595 | -122.4518 | -122.3694 | 122.3557 | 122.3465 | 59.2163 | 59.2117
372.3125 | 122.5616 | -59.2575 | 63.1073 | -0.065842 | 0.0036892 | 0.06423 | 0.060663 | 0.0022644 | 0.00067084 | 0.00034614 | -0.048828 | -0.00071785 | 0.067584 | 0.062848 | -0.0041956 | 0.0066607 | -0.0007456 | -0.09613 | 63.0341 | -59.3308 | 63.0753 | -59.2072 | -59.5963 | -59.5551 | -0.14191 | 62.9791 | -59.2667 | 63.1073 | -59.3353 | -59.4727 | -59.3765 | -0.073243 | -0.073242 | -0.032044 | 0.050354 | -0.29755 | -0.33875 | -0.2243 | -0.2655 | -0.009156 | -0.12817 | 0 | -0.07782 | -0.11902 | -0.21515 | -0.10986 | -0.20599 | 0.1236 | 122.406 | -0.068664 | 122.374 | 122.3648 | 122.2458 | 122.2916 | 122.2366 | -122.4381 | -122.374 | 122.3328 | 122.3648 | 59.1614 | 59.1156
373.3125 | 122.58 | -59.2255 | 63.1577 | -0.012436 | 0.0009122 | 0.062948 | 0.059381 | -0.0013672 | -0.0027472 | 0.00013254 | 0.0091553 | 0.0035547 | 0.066302 | 0.06178 | -0.002273 | 0.0064471 | -0.0075814 | 0 | 63.0798 | -59.3216 | 63.1531 | -59.166 | -59.5047 | -59.4955 | -0.032043 | 63.0203 | -59.2163 | 63.1302 | -59.2667 | -59.3948 | -59.3216 | -0.09613 | -0.07782 | -0.004578 | 0.059509 | -0.27008 | -0.27924 | -0.17395 | -0.18311 | 0.009155 | -0.13733 | -0.027466 | -0.041199 | -0.09613 | -0.16937 | -0.10528 | -0.17853 | 0.15564 | 122.4747 | -0.050354 | 122.3465 | 122.4014 | 122.2366 | 122.3053 | 122.2458 | -122.4792 | -122.374 | 122.3785 | 122.3557 | 59.2255 | 59.1934
374.3125 | 122.5479 | -59.2575 | 63.1302 | -0.042954 | 0.0043302 | 0.063376 | 0.062372 | 0.0014098 | -0.003388 | -8.1264e-05 | -0.036621 | 0.0018457 | 0.065875 | 0.062634 | -0.003982 | 0.0073015 | -0.0016 | -0.022888 | 63.0341 | -59.317 | 63.1439 | -59.1476 | -59.5367 | -59.5139 | -0.050354 | 62.9929 | -59.2438 | 63.0936 | -59.3079 | -59.4589 | -59.3674 | -0.05951 | -0.09613 | 0.013733 | 0.10986 | -0.25635 | -0.27924 | -0.19684 | -0.21973 | 0.013733 | -0.13733 | -0.036621 | -0.050354 | -0.10986 | -0.20142 | -0.1236 | -0.21515 | 0.16937 | 122.4609 | -0.064087 | 122.3373 | 122.3511 | 122.2366 | 122.2916 | 122.2504 | -122.4472 | -122.374 | 122.4014 | 122.3511 | 59.2346 | 59.2072
375.3125 | 122.5433 | -59.2758 | 63.1027 | -0.050583 | 0.0026212 | 0.062521 | 0.062158 | 0.00034182 | -0.00039736 | -0.00029486 | -0.027466 | 0.0031273 | 0.067584 | 0.060712 | -0.0014184 | 0.0070879 | -0.0037362 | -0.073242 | 63.0157 | -59.3399 | 63.089 | -59.2117 | -59.5825 | -59.5688 | -0.13275 | 63.002 | -59.2575 | 63.1027 | -59.3491 | -59.4727 | -59.3903 | -0.064087 | -0.086975 | -0.013733 | 0.064087 | -0.29297 | -0.3067 | -0.22888 | -0.24262 | 0.018311 | -0.10071 | 0 | -0.073242 | -0.11444 | -0.19684 | -0.13275 | -0.21515 | 0.12817 | 122.4289 | -0.091553 | 122.3602 | 122.3557 | 122.2595 | 122.2916 | 122.2778 | -122.4426 | -122.3602 | 122.3648 | 122.3785 | 59.2026 | 59.1431
376.3125 | 122.5754 | -59.2575 | 63.1485 | -0.027695 | 0.0006986 | 0.062521 | 0.061731 | 0.0026916 | 0.00088444 | -0.0013629 | -0.01831 | 0.0016321 | 0.066943 | 0.061566 | -0.0041956 | 0.0073015 | -0.0024546 | 0.022888 | 63.0936 | -59.2758 | 63.1943 | -59.1064 | -59.4727 | -59.4681 | 0.004578 | 63.0249 | -59.2026 | 63.1577 | -59.2438 | -59.3903 | -59.317 | -0.018311 | -0.054932 | 0.045776 | 0.15106 | -0.21057 | -0.21515 | -0.19226 | -0.19684 | 0.054931 | -0.1236 | 0.009155 | 0.013733 | -0.05951 | -0.13275 | -0.11444 | -0.18768 | 0.16937 | 122.4701 | -0.041198 | 122.3602 | 122.3694 | 122.2275 | 122.3511 | 122.2824 | -122.4243 | -122.3511 | 122.4518 | 122.4152 | 59.2804 | 59.2621
377.3125 | 122.58 | -59.2712 | 63.1073 | -0.096359 | 0.002194 | 0.062948 | 0.060022 | -0.00051278 | -0.0012518 | -0.00072206 | -0.021362 | 0.0029137 | 0.06737 | 0.060284 | -0.003341 | 0.0064471 | -0.0039498 | -0.091553 | 63.0295 | -59.3308 | 63.0798 | -59.2209 | -59.5825 | -59.5551 | -0.14191 | 62.9974 | -59.2621 | 63.0936 | -59.3353 | -59.491 | -59.3582 | -0.05951 | -0.07782 | -0.027466 | 0.050354 | -0.28381 | -0.31128 | -0.2243 | -0.25177 | 0.009155 | -0.10986 | -0.013733 | -0.064087 | -0.086975 | -0.21973 | -0.09613 | -0.22888 | 0.10986 | 122.4106 | -0.073242 | 122.3557 | 122.3602 | 122.2595 | 122.3007 | 122.2687 | -122.4381 | -122.3694 | 122.3511 | 122.3648 | 59.1797 | 59.1293
378.3125 | 122.5845 | -59.2346 | 63.1485 | -0.065842 | 0.0019802 | 0.062308 | 0.057886 | -0.0045716 | -0.0025336 | 0.0020551 | -0.0061035 | 0.0016321 | 0.068652 | 0.060712 | -0.003341 | 0.0083697 | 0.0020316 | -0.009155 | 63.0753 | -59.3124 | 63.1348 | -59.1522 | -59.5276 | -59.491 | -0.027466 | 63.0249 | -59.2209 | 63.1073 | -59.2941 | -59.4086 | -59.3216 | -0.07782 | -0.073243 | -0.013733 | 0.082397 | -0.25635 | -0.29297 | -0.17853 | -0.21515 | 0.013733 | -0.1236 | -0.041199 | -0.059509 | -0.086975 | -0.17395 | -0.10071 | -0.18768 | 0.16022 | 122.4472 | -0.073242 | 122.3282 | 122.3877 | 122.2458 | 122.3099 | 122.2595 | -122.4609 | -122.3694 | 122.3694 | 122.3419 | 59.2255 | 59.2072
379.3125 | 122.5616 | -59.2438 | 63.1348 | -0.065842 | 0.004971 | 0.062308 | 0.060022 | 0.002478 | -0.00018376 | -0.0024311 | -0.024414 | 0.00077755 | 0.066302 | 0.062421 | -0.0037684 | 0.0085833 | -0.000532 | -0.091553 | 62.9745 | -59.3262 | 63.089 | -59.2346 | -59.5734 | -59.5596 | -0.13733 | 63.0203 | -59.2712 | 63.0844 | -59.3491 | -59.5093 | -59.3857 | -0.082398 | -0.16022 | -0.045777 | 0.009155 | -0.31586 | -0.32959 | -0.23346 | -0.24719 | -0.027466 | -0.11444 | -0.050354 | -0.10529 | -0.14191 | -0.2655 | -0.11444 | -0.23804 | 0.091553 | 122.4152 | -0.07782 | 122.3557 | 122.3007 | 122.2916 | 122.2183 | 122.2641 | -122.4609 | -122.406 | 122.3328 | 122.3282 | 59.1522 | 59.1064
380.3125 | 122.7356 | -59.2392 | 63.0157 | -0.10399 | 0.002194 | 0.064871 | 0.060235 | -0.00051278 | -0.0029608 | 0.0020551 | 0.0030517 | 0.0012047 | 0.065875 | 0.059003 | -0.0029138 | 0.0087969 | -0.0037362 | -0.064087 | 62.9791 | -59.3216 | 63.1668 | -59.0973 | -59.5139 | -59.4681 | -0.013733 | 62.9608 | -59.2484 | 63.1943 | -59.23 | -59.3262 | -59.2667 | -0.082397 | -0.036621 | 0.15106 | 0.14191 | -0.22888 | -0.27466 | -0.14649 | -0.19226 | -0.009155 | -0.054932 | 0.17853 | 0.009155 | -0.027466 | -0.086975 | -0.018311 | -0.07782 | 0.2243 | 122.4884 | 0.01831 | 122.4426 | 122.3007 | 122.2092 | 122.2183 | 122.2 | -122.3373 | -122.2641 | 122.406 | 122.4335 | 59.1751 | 59.2255
381.3125 | 122.6212 | -59.2255 | 63.1668 | -0.042954 | 0.0024076 | 0.06188 | 0.060449 | -0.0030762 | 0.00067084 | -0.0011493 | -0.021362 | 0.0018457 | 0.066516 | 0.058789 | -0.0071864 | 0.0070879 | 0.0020316 | -0.013733 | 63.0753 | -59.2987 | 63.1668 | -59.1476 | -59.4727 | -59.4818 | 0.004578 | 63.0341 | -59.2117 | 63.1531 | -59.2575 | -59.3857 | -59.2941 | -0.073242 | -0.091553 | 0 | 0.07782 | -0.25635 | -0.24719 | -0.18311 | -0.17395 | 0.013733 | -0.13275 | -0.013733 | -0.032043 | -0.068664 | -0.16022 | -0.082397 | -0.17395 | 0.15106 | 122.4655 | -0.045776 | 122.3648 | 122.374 | 122.2458 | 122.3007 | 122.2595 | -122.4655 | -122.3785 | 122.3923 | 122.3785 | 59.2117 | 59.23
382.3125 | 122.6028 | -59.2026 | 63.1531 | -0.050583 | 5.76e-05 | 0.064444 | 0.056604 | 0.00012822 | -0.0044562 | 0.0014141 | 0.045776 | 0.00035035 | 0.068652 | 0.05708 | -0.00505 | 0.0049517 | -0.0030954 | 0.059509 | 62.9883 | -59.2804 | 63.2355 | -59.0424 | -59.4131 | -59.4086 | 0.082397 | 62.9791 | -59.2117 | 63.1668 | -59.23 | -59.3491 | -59.3033 | -0.07782 | -0.16479 | 0.082398 | 0.16022 | -0.20599 | -0.21057 | -0.12817 | -0.13275 | -0.009155 | -0.17395 | 0.013733 | -0.027466 | -0.10071 | -0.14648 | -0.091553 | -0.13733 | 0.23804 | 122.5159 | -0.018311 | 122.3785 | 122.2687 | 122.1909 | 122.1909 | 122.1817 | -122.4335 | -122.3648 | 122.4381 | 122.3694 | 59.2621 | 59.285
383.3125 | 122.5754 | -59.2255 | 63.1256 | -0.073471 | 0.0024076 | 0.063589 | 0.060876 | 0.00076902 | -0.0038154 | 0.0020551 | -0.048828 | 0.0024865 | 0.066729 | 0.063702 | -0.0027002 | 0.0077289 | 0.0007498 | 0.013733 | 63.0249 | -59.3079 | 63.1622 | -59.1293 | -59.4955 | -59.4955 | -0.009155 | 63.0157 | -59.2346 | 63.1348 | -59.285 | -59.4269 | -59.3445 | -0.082397 | -0.10071 | 0.036621 | 0.096131 | -0.27008 | -0.27008 | -0.18768 | -0.18768 | -0.009155 | -0.10986 | 0.009156 | -0.059509 | -0.11902 | -0.20142 | -0.10986 | -0.19226 | 0.17853 | 122.4701 | -0.050354 | 122.3694 | 122.3328 | 122.2504 | 122.2504 | 122.2412 | -122.4335 | -122.3602 | 122.3877 | 122.3602 | 59.2392 | 59.2163
384.3125 | 122.6669 | -59.2209 | 63.089 | -0.065842 | 0.0045438 | 0.066794 | 0.06109 | -0.00029898 | -0.0018928 | -0.00072206 | 0.0030517 | 0.0029137 | 0.066516 | 0.055371 | -0.0027002 | 0.0085833 | -0.0001046 | -0.21973 | 62.9105 | -59.3445 | 63.2309 | -59.0515 | -59.4727 | -59.4406 | -0.004578 | 62.9471 | -59.2392 | 63.1897 | -59.2255 | -59.3491 | -59.2758 | -0.1236 | -0.17853 | 0.14191 | 0.16937 | -0.21973 | -0.25177 | -0.096131 | -0.12817 | -0.018311 | -0.14191 | 0.10071 | -0.004578 | -0.054932 | -0.12817 | -0.036621 | -0.10986 | 0.29297 | 122.5754 | 0.013733 | 122.4289 | 122.2549 | 122.1863 | 122.1313 | 122.168 | -122.4335 | -122.3282 | 122.4518 | 122.4106 | 59.0012 | 59.2163
385.3125 | 122.5616 | -59.2667 | 63.1393 | -0.027695 | 0.0053982 | 0.065939 | 0.063226 | 0.00098262 | -0.0021064 | 0.0014141 | 0.030518 | 0.00077755 | 0.066943 | 0.057721 | -0.0044092 | 0.0064471 | -0.0039498 | -0.07782 | 63.0203 | -59.3399 | 63.1714 | -59.5459 | -60.0403 | -59.4589 | -0.20142 | 63.002 | -59.2484 | 63.0981 | -59.3491 | -59.4772 | -59.3948 | -0.073242 | -0.11902 | 0.032044 | -0.27923 | -0.19226 | -0.77362 | -0.11902 | -0.70038 | 0.018311 | -0.13733 | -0.041198 | -0.082397 | -0.12817 | -0.21057 | -0.14648 | -0.22888 | -0.20599 | 122.5113 | -0.10071 | 122.3465 | 122.3602 | 122.2504 | 122.287 | 122.2687 | -122.4792 | -122.3877 | 122.4381 | 122.3648 | 59.1888 | 59.0652
386.3125 | 122.58 | -59.23 | 63.1348 | 0.0028229 | 0.002194 | 0.063803 | 0.061944 | 0.0016236 | -0.00082456 | -0.0015765 | -0.0091553 | 0.0037683 | 0.068225 | 0.069257 | -0.0054774 | 0.0073015 | -0.0039498 | 0.032043 | 63.0569 | -59.3262 | 63.1851 | -59.1202 | -59.4818 | -59.4818 | 0.027466 | 63.0112 | -59.23 | 62.9654 | -59.1019 | -59.3033 | -59.2667 | -0.09613 | -0.07782 | 0.050354 | 0.10986 | -0.25177 | -0.25177 | -0.15564 | -0.15564 | 0 | -0.1236 | -0.16937 | 0.12817 | -0.036621 | -0.073242 | -0.036621 | -0.073242 | 0.20599 | 122.5113 | 0.12817 | 122.1954 | 122.3831 | 122.2412 | 122.287 | 122.2412 | -122.4609 | -122.3648 | 122.4152 | 122.1954 | 59.2621 | 59.2575
387.3125 | 122.525 | -59.2529 | 63.1439 | -0.035324 | 0.0017666 | 0.065725 | 0.062372 | 0.0031188 | -0.0025336 | -0.0030719 | -0.048828 | 0.0012047 | 0.064593 | 0.069257 | -0.0037684 | 0.0066607 | -0.0043772 | -0.027466 | 63.0295 | -59.3216 | 63.1348 | -59.1614 | -59.5459 | -59.5184 | -0.054932 | 63.0112 | -59.2575 | 63.1073 | -59.3216 | -59.4498 | -59.3536 | -0.068664 | -0.11444 | -0.009155 | 0.091553 | -0.2655 | -0.29297 | -0.19684 | -0.2243 | -0.004577 | -0.13275 | -0.036621 | -0.068664 | -0.10071 | -0.19684 | -0.096131 | -0.19226 | 0.16022 | 122.4564 | -0.064087 | 122.3648 | 122.3511 | 122.2687 | 122.2824 | 122.2641 | -122.4655 | -122.4014 | 122.3877 | 122.3602 | 59.2255 | 59.198
388.3125 | 122.58 | -59.2484 | 63.1165 | -0.050583 | 0.0009122 | 0.063803 | 0.061731 | 0.00012822 | -0.0029608 | -0.0015765 | -0.036621 | 0.0014185 | 0.065875 | 0.061352 | -0.0052638 | 0.0062335 | -0.000532 | -0.018311 | 63.0157 | -59.3262 | 63.1485 | -59.1248 | -59.523 | -59.5047 | -0.068665 | 62.9837 | -59.2758 | 63.121 | -59.3399 | -59.4452 | -59.3308 | -0.07782 | -0.10071 | 0.032044 | 0.1236 | -0.25635 | -0.27466 | -0.17853 | -0.19684 | -0.027466 | -0.13275 | 0.004578 | -0.091553 | -0.082398 | -0.19684 | -0.054932 | -0.16937 | 0.20142 | 122.4747 | -0.064087 | 122.3969 | 122.3419 | 122.2595 | 122.2641 | 122.2321 | -122.4426 | -122.3923 | 122.3969 | 122.3694 | 59.23 | 59.1797
389.3125 | 122.6028 | -59.2529 | 63.089 | -0.10399 | 0.0056118 | 0.062521 | 0.058526 | 0.0056824 | -0.0021064 | -8.1264e-05 | -0.015259 | 0.0020593 | 0.067584 | 0.060071 | -0.0016322 | 0.0068743 | -0.003309 | -0.07782 | 63.0432 | -59.3536 | 63.1073 | -59.1797 | -59.5551 | -59.523 | -0.10071 | 62.9562 | -59.2758 | 63.1439 | -59.2804 | -59.4177 | -59.3216 | -0.10071 | -0.045776 | 0.018311 | 0.073243 | -0.27008 | -0.30212 | -0.16937 | -0.20142 | -0.022888 | -0.13275 | 0.054932 | -0.027466 | -0.068664 | -0.16479 | -0.045776 | -0.14191 | 0.17395 | 122.4609 | -0.004578 | 122.4197 | 122.3969 | 122.2321 | 122.2961 | 122.2092 | -122.4426 | -122.3648 | 122.3602 | 122.3969 | 59.1751 | 59.1522
390.3125 | 122.6074 | -59.2346 | 63.1531 | 0.03334 | 0.0024076 | 0.065085 | 0.059595 | 0.0011962 | -0.004029 | -0.00050846 | -0.033569 | 0.0016321 | 0.065875 | 0.061566 | -0.0041956 | 0.0075153 | -0.0045908 | 0.018311 | 63.0753 | -59.3079 | 63.1714 | -59.1339 | -59.4727 | -59.4818 | 0.009155 | 63.0066 | -59.23 | 63.1485 | -59.2575 | -59.3674 | -59.2941 | -0.073242 | -0.07782 | 0.018311 | 0.10071 | -0.24719 | -0.23804 | -0.17395 | -0.16479 | 0.004577 | -0.14648 | -0.004577 | -0.022888 | -0.059509 | -0.13275 | -0.064086 | -0.13733 | 0.17395 | 122.4792 | -0.027465 | 122.3785 | 122.3831 | 122.2366 | 122.3099 | 122.2412 | -122.4609 | -122.3831 | 122.406 | 122.3831 | 59.2529 | 59.2438
391.3125 | 122.5525 | -59.2575 | 63.1668 | -0.050583 | 0.0019802 | 0.062948 | 0.060663 | -0.00093998 | -0.0021064 | -0.0011493 | 0.018311 | 0.0027001 | 0.068011 | 0.060071 | -0.0029138 | 0.0060199 | 0.000109 | 0.004578 | 63.0798 | -59.3033 | 63.1165 | -59.1476 | -59.5001 | -59.4818 | -0.022888 | 63.0386 | -59.2438 | 63.1073 | -59.2987 | -59.4177 | -59.3491 | -0.045777 | -0.086975 | -0.050354 | 0.10986 | -0.22431 | -0.24262 | -0.17853 | -0.19684 | 0.013733 | -0.12817 | -0.059509 | -0.041199 | -0.091553 | -0.16022 | -0.10529 | -0.17395 | 0.15564 | 122.4197 | -0.054932 | 122.3511 | 122.3831 | 122.2824 | 122.3373 | 122.2961 | -122.4701 | -122.4106 | 122.374 | 122.3648 | 59.2621 | 59.2346
392.3125 | 122.6486 | -59.23 | 63.0844 | 0.04097 | 0.0006986 | 0.063803 | 0.060235 | 0.0018372 | -0.0048834 | -0.0022175 | 0.018311 | -0.0028541 | 0.066943 | 0.052594 | -0.0044092 | 0.0077289 | 0.0005362 | 0.045776 | 63.002 | -59.2667 | 63.2126 | -59.079 | -59.4498 | -59.4315 | -0.004578 | 62.9379 | -59.2346 | 63.1989 | -59.2026 | -59.3353 | -59.2621 | -0.036621 | -0.082398 | 0.12817 | 0.15106 | -0.20142 | -0.21973 | -0.16479 | -0.1831 | -0.004577 | -0.14648 | 0.11444 | 0.027466 | -0.032043 | -0.10529 | -0.027466 | -0.10071 | 0.18768 | 122.4792 | 0.032043 | 122.4335 | 122.2687 | 122.1725 | 122.2321 | 122.168 | -122.3511 | -122.319 | 122.4426 | 122.4289 | 59.2758 | 59.2255
393.3125 | 122.5845 | -59.2163 | 63.1348 | -0.035324 | 0.002194 | 0.064016 | 0.061731 | -0.0024354 | -0.004029 | -0.0015765 | -0.01831 | 0.0056909 | 0.066302 | 0.064557 | -0.003341 | 0.0070879 | -0.0045908 | 0.022888 | 63.0478 | -59.3033 | 63.1668 | -59.111 | -59.4864 | -59.4818 | -0.21057 | 62.9883 | -59.2438 | 63.1531 | -59.2438 | -59.3719 | -59.2896 | -0.086975 | -0.086975 | 0.032043 | 0.10529 | -0.2655 | -0.27008 | -0.17853 | -0.18311 | -0.027465 | -0.14648 | 0.01831 | -0.027465 | -0.073242 | -0.15564 | -0.045777 | -0.12817 | 0.19226 | 122.4701 | 0 | 122.3969 | 122.3511 | 122.2321 | 122.2641 | 122.2046 | -122.4381 | -122.3785 | 122.3831 | 122.3694 | 59.2392 | 59.0057
394.3125 | 122.5662 | -59.2346 | 63.1348 | -0.050583 | 0.002194 | 0.064016 | 0.061731 | 0.00076902 | -0.00061096 | -0.0022175 | -0.054932 | 0.0018457 | 0.06737 | 0.065411 | -0.0041956 | 0.0066607 | -0.0013864 | 0.009155 | 63.0157 | -59.3079 | 63.1805 | -59.111 | -59.5093 | -59.4864 | 0 | 63.002 | -59.23 | 63.1302 | -59.2896 | -59.4269 | -59.3353 | -0.073242 | -0.11902 | 0.045776 | 0.1236 | -0.25177 | -0.27466 | -0.17853 | -0.20142 | 0.004577 | -0.13275 | -0.004578 | -0.054932 | -0.10071 | -0.19226 | -0.10529 | -0.19684 | 0.19684 | 122.4884 | -0.059509 | 122.3602 | 122.3236 | 122.2321 | 122.2504 | 122.2366 | -122.4426 | -122.3648 | 122.4152 | 122.3648 | 59.2438 | 59.2346
395.3125 | 122.5754 | -59.2575 | 63.1393 | -0.035324 | 0.0043302 | 0.061453 | 0.06109 | 0.0029052 | -0.0044562 | -0.0039265 | -0.0030517 | 0.0031273 | 0.068652 | 0.060284 | -0.0044092 | 0.0064471 | -0.0009592 | 0.027466 | 63.0295 | -59.3079 | 63.1714 | -59.1156 | -59.4864 | -59.4864 | 0.013733 | 62.9974 | -59.2209 | 63.1256 | -59.2667 | -59.4086 | -59.3216 | -0.050354 | -0.10986 | 0.032044 | 0.14191 | -0.22888 | -0.22888 | -0.17853 | -0.17853 | 0.036621 | -0.14191 | -0.013733 | -0.009156 | -0.064087 | -0.15106 | -0.10071 | -0.18768 | 0.19226 | 122.4792 | -0.045777 | 122.3465 | 122.3373 | 122.2183 | 122.287 | 122.2549 | -122.4472 | -122.3602 | 122.4289 | 122.3831 | 59.285 | 59.2712
396.3125 | 122.5342 | -59.2484 | 63.1439 | -0.050583 | 0.0034756 | 0.066153 | 0.060235 | -0.0022218 | -0.0014654 | -0.0030719 | -0.024414 | 0.0022729 | 0.066302 | 0.065198 | -0.0037684 | 0.0070879 | -0.0013864 | -0.027466 | 63.0249 | -59.3216 | 63.1302 | -59.166 | -59.5322 | -59.5184 | -0.07782 | 63.0066 | -59.2346 | 63.0936 | -59.3124 | -59.4772 | -59.3536 | -0.073242 | -0.11902 | -0.013733 | 0.082397 | -0.27008 | -0.28381 | -0.19684 | -0.21057 | 0.013733 | -0.13733 | -0.050354 | -0.064087 | -0.10529 | -0.22888 | -0.11902 | -0.24262 | 0.15564 | 122.4518 | -0.07782 | 122.3282 | 122.3465 | 122.2412 | 122.2733 | 122.2549 | -122.4655 | -122.3785 | 122.3785 | 122.3419 | 59.2209 | 59.1705
397.3125 | 122.5388 | -59.2575 | 63.1348 | -0.058212 | 0.0036892 | 0.065298 | 0.061517 | 0.00034182 | -0.003388 | -0.0034991 | -0.036621 | 0.0024865 | 0.06972 | 0.061352 | -0.0024866 | 0.0094379 | -0.0018136 | -0.064087 | 63.0249 | -59.3445 | 63.089 | -59.23 | -59.6191 | -59.5917 | -0.43488 | 62.9471 | -59.317 | 63.089 | -59.3079 | -59.5184 | -59.3903 | -0.086975 | -0.10986 | -0.045777 | 0.027465 | -0.33417 | -0.36163 | -0.24719 | -0.27466 | -0.05951 | -0.18768 | -0.045777 | -0.050354 | -0.13275 | -0.26093 | -0.073242 | -0.20142 | 0.11444 | 122.4335 | 0.009156 | 122.406 | 122.3694 | 122.2641 | 122.2824 | 122.2046 | -122.4792 | -122.4518 | 122.3465 | 122.3465 | 59.1934 | 58.8226
398.3125 | 122.58 | -59.2484 | 63.1439 | -0.012436 | 0.0013394 | 0.064657 | 0.062372 | 0.0011962 | -0.0042426 | -8.1264e-05 | -0.027466 | 0.0018457 | 0.069934 | 0.061993 | -0.0037684 | 0.0096515 | -0.0018136 | 0.032043 | 63.0569 | -59.285 | 63.1668 | -59.0973 | -59.4635 | -59.4635 | 0.027466 | 63.0203 | -59.2575 | 63.1531 | -59.2026 | -59.6146 | -59.5093 | -0.036621 | -0.086975 | 0.022888 | 0.15106 | -0.21515 | -0.21515 | -0.17853 | -0.17853 | -0.009155 | -0.1236 | 0.009155 | 0.045776 | -0.26093 | -0.36621 | -0.25177 | -0.35706 | 0.18768 | 122.4518 | 0.054931 | 122.4106 | 122.3419 | 122.2778 | 122.3053 | 122.2687 | -122.4289 | -122.4014 | 122.4152 | 122.4014 | 59.2804 | 59.2758
399.3125 | 122.5845 | -59.23 | 63.121 | -0.035324 | 0.0011258 | 0.063162 | 0.061731 | 0.00076902 | -0.0018928 | -0.00029486 | -0.027466 | 0.0024865 | 0.065234 | 0.061566 | -0.0065454 | 0.0068743 | -0.0026682 | 0.018311 | 63.0478 | -59.3079 | 63.1714 | -59.0927 | -59.4772 | -59.4681 | 0.018311 | 63.0066 | -59.2117 | 63.1577 | -59.2621 | -59.4131 | -59.2987 | -0.077819 | -0.073242 | 0.050354 | 0.13733 | -0.23804 | -0.24719 | -0.16022 | -0.16937 | 0.018311 | -0.11444 | 0.036621 | -0.032043 | -0.068664 | -0.18311 | -0.086975 | -0.20142 | 0.21515 | 122.4792 | -0.050354 | 122.3694 | 122.3557 | 122.2183 | 122.2778 | 122.2366 | -122.4289 | -122.3328 | 122.4014 | 122.3877 | 59.2484 | 59.2484
400.3125 | 122.6074 | -59.2209 | 63.1256 | 0.063858 | 0.003262 | 0.064016 | 0.060449 | -0.0017944 | -0.0016792 | -0.0011493 | -0.015259 | 0.0029137 | 0.066089 | 0.060712 | -0.0048364 | 0.0079425 | -0.0048044 | -0.004578 | 63.0432 | -59.3033 | 63.1943 | -59.079 | -59.4818 | -59.4589 | 0.013733 | 62.9929 | -59.2392 | 63.1577 | -59.2575 | -59.3994 | -59.2987 | -0.082398 | -0.082397 | 0.068665 | 0.14191 | -0.23804 | -0.26093 | -0.15564 | -0.17853 | -0.018311 | -0.13275 | 0.032044 | -0.036621 | -0.07782 | -0.17853 | -0.059509 | -0.16022 | 0.22431 | 122.4976 | -0.01831 | 122.3969 | 122.3465 | 122.2321 | 122.2641 | 122.2137 | -122.4289 | -122.3648 | 122.4152 | 122.3785 | 59.2163 | 59.2346
401.3125 | 122.5891 | -59.2209 | 63.1393 | -0.027695 | 0.0013394 | 0.062735 | 0.059595 | 0.0044006 | -0.0025336 | 0.0014141 | -0.0030517 | 0.00099115 | 0.067798 | 0.065625 | -0.0027002 | 0.0075153 | 0.0009634 | 0.027466 | 63.0569 | -59.2941 | 63.1439 | -59.1064 | -59.4818 | -59.4772 | 0.027466 | 63.0157 | -59.2163 | 63.1531 | -59.2392 | -59.3765 | -59.3079 | -0.073242 | -0.082397 | 0.004578 | 0.11444 | -0.25635 | -0.26093 | -0.18311 | -0.18768 | 0.004577 | -0.1236 | 0.013733 | -0.018311 | -0.086975 | -0.15564 | -0.091552 | -0.16022 | 0.18768 | 122.438 | -0.022888 | 122.3694 | 122.3511 | 122.2321 | 122.2778 | 122.2366 | -122.4335 | -122.3557 | 122.3648 | 122.374 | 59.2484 | 59.2484
402.3125 | 122.6624 | -59.2163 | 63.0753 | -0.096359 | 0.0017666 | 0.063162 | 0.060663 | 0.0020508 | -0.00039736 | -0.0013629 | 0.015259 | 0.0027001 | 0.066943 | 0.062207 | -0.003341 | 0.0083697 | -0.0041636 | -0.041199 | 63.0112 | -59.3262 | 63.1622 | -59.0973 | -59.4681 | -59.4589 | -0.022888 | 62.9517 | -59.23 | 63.121 | -59.0378 | -59.2026 | -59.2392 | -0.10986 | -0.064087 | 0.086975 | 0.11902 | -0.24261 | -0.25177 | -0.13275 | -0.14191 | -0.013733 | -0.1236 | 0.045777 | 0.17853 | -0.022888 | 0.013733 | -0.009155 | 0.027466 | 0.22888 | 122.4884 | 0.19226 | 122.3511 | 122.3373 | 122.1817 | 122.2275 | 122.168 | -122.4014 | -122.3053 | 122.3785 | 122.3373 | 59.1751 | 59.1934
403.3125 | 122.5891 | -59.2346 | 63.1119 | -0.020065 | 0.002194 | 0.063162 | 0.060449 | -0.0013672 | -0.0016792 | -0.0039265 | -0.027466 | 0.0012047 | 0.065661 | 0.060284 | -0.0035548 | 0.0070879 | -0.0022408 | -0.009155 | 63.0569 | -59.3216 | 63.1577 | -59.1293 | -59.5047 | -59.4772 | -0.032043 | 62.9883 | -59.2163 | 63.121 | -59.3079 | -59.4315 | -59.3399 | -0.086975 | -0.054931 | 0.045777 | 0.10529 | -0.24262 | -0.27008 | -0.15564 | -0.18311 | 0.01831 | -0.1236 | 0.009156 | -0.073242 | -0.10529 | -0.19684 | -0.1236 | -0.21515 | 0.19226 | 122.4792 | -0.091552 | 122.3373 | 122.3785 | 122.2046 | 122.2916 | 122.2229 | -122.4335 | -122.3282 | 122.3923 | 122.3557 | 59.2255 | 59.2026
404.3125 | 122.5296 | -59.2712 | 63.0981 | 0.0028229 | 0.0006986 | 0.067434 | 0.060663 | -0.003717 | -0.0031744 | -0.00093566 | -0.039673 | 0.0033411 | 0.066302 | 0.062848 | -0.0059046 | 0.0077289 | 0.0022452 | -0.37079 | 62.9425 | -59.3719 | 63.0936 | -59.2255 | -59.5825 | -59.5505 | -0.15106 | 62.9837 | -59.2667 | 63.089 | -59.3491 | -59.4864 | -59.3948 | -0.10071 | -0.15564 | -0.004578 | 0.045776 | -0.27924 | -0.31128 | -0.17853 | -0.21057 | 0.004577 | -0.11444 | -0.009156 | -0.07782 | -0.1236 | -0.21515 | -0.12817 | -0.21973 | 0.14648 | 122.4655 | -0.082397 | 122.3557 | 122.3145 | 122.2504 | 122.2137 | 122.2549 | -122.4701 | -122.3648 | 122.3648 | 122.3602 | 58.9005 | 59.1202
405.3125 | 122.5937 | -59.2163 | 63.1622 | -0.027695 | 0.0024076 | 0.066153 | 0.060235 | 0.0029052 | -0.0036018 | 0.00013254 | 0.0030517 | 0.00099115 | 0.06737 | 0.061139 | -0.0046228 | 0.0077289 | -0.0058724 | 0 | 63.0524 | -59.2941 | 63.1485 | -59.1339 | -59.4818 | -59.4818 | -0.004578 | 63.0203 | -59.2209 | 63.1348 | -59.2484 | -59.3903 | -59.2941 | -0.077819 | -0.10986 | -0.013732 | 0.082398 | -0.2655 | -0.2655 | -0.18768 | -0.18768 | -0.004577 | -0.14191 | -0.027465 | -0.032043 | -0.077819 | -0.17395 | -0.073242 | -0.16937 | 0.16022 | 122.4426 | -0.027466 | 122.3557 | 122.3465 | 122.2412 | 122.2687 | 122.2366 | -122.4564 | -122.3831 | 122.3648 | 122.3511 | 59.2163 | 59.2117
406.3125 | 122.5983 | -59.2346 | 63.1165 | -0.0048066 | 0.0026212 | 0.064016 | 0.060449 | 0.00055542 | -0.0018928 | -0.0030719 | -0.015259 | 0.0016321 | 0.070147 | 0.063916 | -0.0029138 | 0.0070879 | -0.0022408 | 0.041199 | 63.0478 | -59.317 | 63.1714 | -59.0973 | -59.4727 | -59.4589 | -0.19226 | 62.97 | -59.2621 | 63.1805 | -59.2667 | -59.3719 | -59.285 | -0.082398 | -0.068664 | 0.054932 | 0.13733 | -0.2243 | -0.23804 | -0.14191 | -0.15564 | -0.027466 | -0.14648 | 0.064087 | -0.032044 | -0.050354 | -0.13733 | -0.022888 | -0.10986 | 0.21973 | 122.4884 | -0.004578 | 122.4426 | 122.3648 | 122.2321 | 122.2824 | 122.2046 | -122.4335 | -122.3785 | 122.406 | 122.4152 | 59.2758 | 59.0424
407.3125 | 122.6669 | -59.2255 | 63.0753 | -0.073471 | 0.0041166 | 0.065939 | 0.060022 | -8.538e-05 | -0.0027472 | -0.0024311 | 0.030518 | 0.0016321 | 0.064807 | 0.060498 | -0.0063318 | 0.0077289 | -0.0043772 | -0.018311 | 62.9837 | -59.2941 | 63.3408 | -59.0698 | -59.5047 | -59.4315 | -0.004578 | 62.9333 | -59.2575 | 63.2034 | -59.2209 | -59.3308 | -59.2255 | -0.068664 | -0.091552 | 0.2655 | 0.15564 | -0.20599 | -0.27924 | -0.13733 | -0.21057 | -0.032043 | -0.14191 | 0.12817 | 0.004578 | 0 | -0.10529 | 0.032043 | -0.073243 | 0.2243 | 122.6349 | 0.036621 | 122.4609 | 122.2778 | 122.1909 | 122.2092 | 122.1588 | -122.3694 | -122.3328 | 122.5662 | 122.4289 | 59.2072 | 59.2209
408.3125 | 122.5433 | -59.2209 | 63.0981 | -0.012436 | 0.002194 | 0.061453 | 0.061303 | 0.0011962 | -0.0021064 | -0.0026447 | -0.024414 | 0.0012047 | 0.067584 | 0.057507 | -0.0052638 | 0.0064471 | -0.0030954 | 0.032043 | 63.0432 | -59.3124 | 63.1714 | -59.0927 | -59.4818 | -59.4772 | 0 | 62.9929 | -59.2255 | 63.1348 | -59.2712 | -59.4086 | -59.3262 | -0.091553 | -0.054932 | 0.073242 | 0.12817 | -0.25635 | -0.26093 | -0.1648 | -0.16937 | -0.004578 | -0.10529 | 0.036621 | -0.050354 | -0.10529 | -0.18768 | -0.10071 | -0.1831 | 0.21973 | 122.4838 | -0.045776 | 122.3602 | 122.3557 | 122.2183 | 122.2641 | 122.2137 | -122.4106 | -122.3236 | 122.3923 | 122.3557 | 59.2529 | 59.2209
409.3125 | 122.6212 | -59.2484 | 63.0753 | -0.081101 | 0.001553 | 0.062521 | 0.060449 | 0.0011962 | -0.00232 | -0.00029486 | -0.030517 | 0.0014185 | 0.066943 | 0.062207 | -0.0031274 | 0.0049517 | 0.003527 | -0.086975 | 63.0157 | -59.3399 | 63.0936 | -59.166 | -59.5459 | -59.523 | -0.10071 | 62.9654 | -59.2484 | 63.1393 | -59.2896 | -59.3948 | -59.2896 | -0.091553 | -0.059509 | 0.018311 | 0.082397 | -0.27466 | -0.29755 | -0.1831 | -0.20599 | 0 | -0.10986 | 0.064087 | -0.041199 | -0.041199 | -0.14648 | -0.041199 | -0.14648 | 0.17395 | 122.4335 | -0.041199 | 122.3877 | 122.3557 | 122.2137 | 122.2641 | 122.2137 | -122.4152 | -122.3236 | 122.3419 | 122.3877 | 59.1614 | 59.1476
410.3125 | 122.5433 | -59.2575 | 63.1531 | -0.081101 | 0.002194 | 0.064016 | 0.062585 | 0.00098262 | -0.0029608 | 0.0014141 | -0.024414 | 0.0020593 | 0.064807 | 0.064984 | -0.0044092 | 0.0068743 | -0.0024546 | -0.009155 | 63.0432 | -59.3033 | 63.1485 | -59.1385 | -59.5276 | -59.5093 | -0.054932 | 62.9883 | -59.2438 | 63.1256 | -59.3124 | -59.4543 | -59.3399 | -0.045777 | -0.10986 | -0.004577 | 0.11902 | -0.25177 | -0.27008 | -0.20599 | -0.2243 | 0.013733 | -0.16479 | -0.027466 | -0.054932 | -0.082398 | -0.19684 | -0.096131 | -0.21057 | 0.16479 | 122.4518 | -0.068665 | 122.3694 | 122.3465 | 122.2321 | 122.3007 | 122.2458 | -122.4564 | -122.3969 | 122.406 | 122.3831 | 59.2484 | 59.2026
411.3125 | 122.5296 | -59.2804 | 63.1485 | -0.058212 | 0.0045438 | 0.065512 | 0.059381 | -0.0013672 | -0.00082456 | -0.00050846 | -0.036621 | 0.0024865 | 0.066729 | 0.066052 | -0.0037684 | 0.0085833 | -0.0028818 | -0.041199 | 63.0432 | -59.3262 | 63.0981 | -59.1843 | -59.5688 | -59.5505 | -0.12817 | 62.9974 | -59.2438 | 63.0661 | -59.3582 | -59.4818 | -59.3719 | -0.045776 | -0.10529 | -0.050354 | 0.096131 | -0.27008 | -0.28839 | -0.2243 | -0.24262 | 0.036622 | -0.15106 | -0.082398 | -0.077819 | -0.091552 | -0.20142 | -0.12817 | -0.23804 | 0.14191 | 122.4243 | -0.11444 | 122.3099 | 122.3694 | 122.2412 | 122.3236 | 122.2778 | -122.4747 | -122.3923 | 122.3785 | 122.3465 | 59.2392 | 59.1522
412.3125 | 122.5983 | -59.2346 | 63.089 | -0.065842 | 0.003262 | 0.064657 | 0.061944 | 0.0026916 | -0.0016792 | -0.0015765 | -0.021362 | 0.0022729 | 0.066943 | 0.068829 | -0.00505 | 0.0075153 | -0.0022408 | -0.10071 | 63.002 | -59.3353 | 63.089 | -59.198 | -59.5688 | -59.5596 | -0.1236 | 62.9745 | -59.2575 | 63.0981 | -59.3216 | -59.4223 | -59.3445 | -0.10071 | -0.086975 | 0 | 0.036621 | -0.32501 | -0.33417 | -0.2243 | -0.23346 | -0.022888 | -0.11444 | 0.009156 | -0.086975 | -0.10986 | -0.18768 | -0.086975 | -0.1648 | 0.13733 | 122.4243 | -0.064087 | 122.3557 | 122.3373 | 122.2321 | 122.2366 | 122.2092 | -122.4243 | -122.3465 | 122.3236 | 122.3328 | 59.1339 | 59.111
413.3125 | 122.5662 | -59.2346 | 63.1439 | 0.010452 | 0.0030484 | 0.063589 | 0.059808 | -0.0015808 | -0.0061652 | 0.00098694 | 0.0030517 | 0.0029137 | 0.068652 | 0.069684 | -0.0046228 | 0.0064471 | -0.0056588 | 0.009155 | 63.0478 | -59.3033 | 63.1439 | -59.1431 | -59.4818 | -59.491 | -0.027466 | 63.0249 | -59.2026 | 63.1302 | -59.2575 | -59.3948 | -59.3079 | -0.068665 | -0.09613 | 0 | 0.091553 | -0.25635 | -0.24719 | -0.18768 | -0.17853 | 0.032043 | -0.11902 | -0.013733 | -0.022888 | -0.073242 | -0.16022 | -0.10529 | -0.19226 | 0.16022 | 122.4472 | -0.054931 | 122.3328 | 122.3511 | 122.2275 | 122.2824 | 122.2595 | -122.4472 | -122.3465 | 122.3785 | 122.3648 | 59.2438 | 59.2072
414.3125 | 122.5662 | -59.2346 | 63.1439 | -0.020065 | 0.0041166 | 0.067434 | 0.059381 | 0.00076902 | 0.0017388 | -0.00072206 | -0.015259 | 0.0035547 | 0.066729 | 0.061139 | -0.0048364 | 0.0083697 | -0.0035226 | 0.022888 | 63.0615 | -59.2941 | 63.1714 | -59.0973 | -59.491 | -59.4681 | 0 | 63.0295 | -59.2255 | 63.1485 | -59.2712 | -59.404 | -59.3079 | -0.059509 | -0.082398 | 0.027466 | 0.13733 | -0.23346 | -0.25635 | -0.17395 | -0.19684 | 0.009155 | -0.11444 | 0.004578 | -0.036621 | -0.073242 | -0.16937 | -0.082397 | -0.17853 | 0.19684 | 122.4655 | -0.045776 | 122.374 | 122.3557 | 122.2549 | 122.2961 | 122.2641 | -122.438 | -122.3694 | 122.406 | 122.3831 | 59.2575 | 59.2346
415.3125 | 122.5983 | -59.2575 | 63.1119 | -0.073471 | 0.0011258 | 0.062094 | 0.058313 | 0.002478 | -0.0029608 | -0.0013629 | -0.033569 | 0.0016321 | 0.066943 | 0.071606 | -0.0065454 | 0.0058063 | -0.0026682 | 0.032043 | 63.0386 | -59.2896 | 63.1805 | -59.0881 | -59.4864 | -59.4589 | 0.018311 | 62.9837 | -59.2438 | 63.1348 | -59.2484 | -59.3857 | -59.3124 | -0.032044 | -0.073242 | 0.068665 | 0.16937 | -0.20142 | -0.22888 | -0.16937 | -0.19684 | 0.013733 | -0.12817 | 0.022889 | 0.009155 | -0.054932 | -0.12817 | -0.068665 | -0.14191 | 0.20142 | 122.4701 | -0.004578 | 122.3785 | 122.3282 | 122.2275 | 122.2961 | 122.2412 | -122.4014 | -122.3557 | 122.438 | 122.3923 | 59.2895 | 59.2758
416.3125 | 122.6074 | -59.2255 | 63.1302 | -0.0048066 | 0.0036892 | 0.062735 | 0.061731 | 0.0020508 | -0.0016792 | 0.00055974 | -0.039673 | 0.0029137 | 0.066516 | 0.060071 | -0.0048364 | 0.0083697 | -0.0022408 | -0.17395 | 62.9837 | -59.3262 | 63.176 | -59.111 | -59.4635 | -59.4589 | 0.018311 | 63.002 | -59.2255 | 63.1531 | -59.2621 | -59.3857 | -59.3079 | -0.10071 | -0.14648 | 0.045776 | 0.11444 | -0.23346 | -0.23804 | -0.13275 | -0.13733 | 0 | -0.12817 | 0.022888 | -0.036621 | -0.082397 | -0.16022 | -0.082397 | -0.16022 | 0.21515 | 122.5021 | -0.036621 | 122.3785 | 122.3099 | 122.2275 | 122.2092 | 122.2275 | -122.4564 | -122.3557 | 122.4014 | 122.3785 | 59.0515 | 59.2438
417.3125 | 122.6212 | -59.2346 | 63.089 | -0.18791 | 0.0002714 | 0.062094 | 0.057672 | -0.00051278 | -0.0025336 | -8.1264e-05 | 0.067139 | 0.00035035 | 0.065661 | 0.065625 | -0.003341 | 0.0068743 | -0.0028818 | -0.068665 | 62.9929 | -59.2804 | 63.1531 | -59.1293 | -59.4864 | -59.4589 | -0.018311 | 62.9929 | -59.2209 | 63.1119 | -59.2758 | -59.3124 | -59.2941 | -0.045777 | -0.09613 | 0.064087 | 0.10529 | -0.2243 | -0.25177 | -0.17853 | -0.20599 | 0.013733 | -0.09613 | 0.022888 | -0.041199 | -0.059509 | -0.07782 | -0.073242 | -0.091553 | 0.15106 | 122.4335 | -0.054932 | 122.3328 | 122.2733 | 122.2137 | 122.2275 | 122.2275 | -122.3694 | -122.3099 | 122.3877 | 122.3465 | 59.166 | 59.2163
418.3125 | 122.5983 | -59.2392 | 63.1348 | 0.010452 | 0.0043302 | 0.062948 | 0.062372 | -0.0028626 | -0.0021064 | -0.00093566 | -0.012207 | 0.0039819 | 0.068011 | 0.063916 | -0.0048364 | 0.0087969 | -0.0022408 | 0.018311 | 63.0478 | -59.3033 | 63.208 | -59.2529 | -59.6741 | -59.4498 | 0.027466 | 63.0157 | -59.2163 | 63.1622 | -59.2529 | -59.3719 | -59.2987 | -0.064087 | -0.086975 | 0.073242 | -0.013733 | -0.21057 | -0.43488 | -0.14648 | -0.37079 | 0.022888 | -0.11902 | 0.027465 | -0.013733 | -0.059509 | -0.13275 | -0.082397 | -0.15564 | 0.050354 | 122.5113 | -0.036621 | 122.3785 | 122.3511 | 122.2321 | 122.287 | 122.2549 | -122.4381 | -122.3511 | 122.4472 | 122.4014 | 59.2575 | 59.2667
419.3125 | 122.5754 | -59.2346 | 63.1348 | -0.042954 | 0.0039028 | 0.065512 | 0.060663 | 0.0029052 | -0.0012518 | -0.00050846 | -0.11597 | 0.0016321 | 0.066729 | 0.067548 | -0.0020594 | 0.0081561 | -0.0039498 | 0.013733 | 63.0569 | -59.3079 | 63.1714 | -59.111 | -59.4772 | -59.5047 | 0.13275 | 63.0157 | -59.2438 | 63.1714 | -59.2163 | -59.3903 | -59.285 | -0.073242 | -0.07782 | 0.036621 | 0.1236 | -0.27008 | -0.24262 | -0.19684 | -0.16937 | -0.009155 | -0.11902 | 0.036621 | 0.01831 | -0.050354 | -0.15564 | -0.041199 | -0.14648 | 0.19684 | 122.4792 | 0.027465 | 122.4152 | 122.3648 | 122.2595 | 122.2916 | 122.2504 | -122.4426 | -122.3785 | 122.406 | 122.406 | 59.2484 | 59.3674
420.3125 | 122.58 | -59.1934 | 63.1393 | -0.027695 | 0.002194 | 0.062948 | 0.060449 | -8.538e-05 | 0.00045724 | -0.0013629 | -0.042725 | 0.0014185 | 0.068225 | 0.062848 | -0.0061182 | 0.0064471 | -0.0011728 | 0.032043 | 63.0341 | -59.3079 | 63.1531 | -59.111 | -59.4864 | -59.4727 | 0.086975 | 63.0157 | -59.2392 | 63.1531 | -59.198 | -59.4086 | -59.3124 | -0.11444 | -0.10528 | 0.013733 | 0.082397 | -0.27924 | -0.29297 | -0.16479 | -0.17853 | -0.045777 | -0.1236 | 0.013733 | -0.004578 | -0.11902 | -0.21515 | -0.073242 | -0.16937 | 0.19684 | 122.4609 | 0.041199 | 122.3923 | 122.3419 | 122.2549 | 122.2275 | 122.2092 | -122.4472 | -122.3785 | 122.3465 | 122.3465 | 59.2255 | 59.2804
421.3125 | 122.5616 | -59.2346 | 63.1393 | -0.065842 | 0.0043302 | 0.063162 | 0.060235 | -0.0013672 | -0.0025336 | -0.0015765 | -0.021362 | 0.0016321 | 0.065661 | 0.060071 | -0.0041956 | 0.0085833 | -0.0016 | 0.022888 | 63.0341 | -59.3033 | 63.1668 | -59.0973 | -59.5047 | -59.4818 | 0.009155 | 63.0112 | -59.2438 | 63.1439 | -59.2667 | -59.4131 | -59.3124 | -0.068665 | -0.10528 | 0.027466 | 0.13733 | -0.24719 | -0.27008 | -0.17853 | -0.20142 | -0.009155 | -0.12817 | 0.004578 | -0.032044 | -0.07782 | -0.17853 | -0.068665 | -0.16937 | 0.20599 | 122.4701 | -0.022889 | 122.3877 | 122.3373 | 122.2549 | 122.2687 | 122.2458 | -122.4426 | -122.3831 | 122.4014 | 122.3785 | 59.2575 | 59.2438
422.3125 | 122.5616 | -59.2484 | 63.1302 | -0.050583 | 0.0024076 | 0.063162 | 0.063226 | 0.0022644 | -0.0021064 | 0.00055974 | -0.05188 | 0.0020593 | 0.065448 | 0.060925 | -0.0059046 | 0.0064471 | -0.0011728 | -0.032043 | 63.0203 | -59.3079 | 63.1256 | -59.1385 | -59.5413 | -59.5322 | -0.064087 | 62.9974 | -59.2529 | 63.0844 | -59.317 | -59.4589 | -59.3491 | -0.059509 | -0.10986 | -0.004578 | 0.10986 | -0.28381 | -0.29297 | -0.2243 | -0.23346 | -0.004578 | -0.13275 | -0.045776 | -0.068665 | -0.10071 | -0.21057 | -0.09613 | -0.20599 | 0.16937 | 122.4335 | -0.064087 | 122.3373 | 122.3282 | 122.2504 | 122.2687 | 122.2458 | -122.438 | -122.3831 | 122.374 | 122.3328 | 59.2163 | 59.1843
423.3125 | 122.5342 | -59.23 | 63.1348 | -0.050583 | 0.0041166 | 0.064016 | 0.060449 | 0.0022644 | -0.0029608 | 0.00098694 | -0.024414 | 0.0018457 | 0.06737 | 0.057721 | -0.0020594 | 0.0079425 | -0.0030954 | -0.032043 | 63.0386 | -59.3216 | 63.1531 | -59.1568 | -59.5276 | -59.5322 | -0.073242 | 62.9974 | -59.2346 | 63.1027 | -59.3216 | -59.4543 | -59.3536 | -0.091552 | -0.096131 | 0.01831 | 0.073243 | -0.30212 | -0.29755 | -0.21057 | -0.20599 | -0.004577 | -0.13733 | -0.032044 | -0.091552 | -0.1236 | -0.2243 | -0.11902 | -0.21973 | 0.16479 | 122.4747 | -0.086975 | 122.3373 | 122.3602 | 122.2321 | 122.2687 | 122.2275 | -122.4564 | -122.3694 | 122.3831 | 122.3328 | 59.198 | 59.1568
424.3125 | 122.5525 | -59.2667 | 63.1439 | 0.03334 | 0.0028348 | 0.064657 | 0.060022 | 0.00055542 | -0.0031744 | 0.0012005 | -0.036621 | 0.0024865 | 0.066089 | 0.05943 | -0.003341 | 0.0070879 | -0.0018136 | -0.009155 | 63.0295 | -59.3124 | 63.1393 | -59.1339 | -59.523 | -59.4864 | -0.050354 | 62.9974 | -59.2392 | 63.0981 | -59.3033 | -59.4543 | -59.3399 | -0.045776 | -0.11444 | -0.004578 | 0.13275 | -0.21973 | -0.25635 | -0.17395 | -0.21057 | 0.027466 | -0.14648 | -0.045776 | -0.036621 | -0.073242 | -0.18768 | -0.10071 | -0.21515 | 0.17853 | 122.4518 | -0.064087 | 122.3373 | 122.3419 | 122.2366 | 122.2961 | 122.2641 | -122.4564 | -122.3831 | 122.406 | 122.3648 | 59.2575 | 59.2163
425.3125 | 122.5571 | -59.2438 | 63.0936 | -0.058212 | 0.0036892 | 0.064444 | 0.060235 | 0.0020508 | -0.0021064 | 0.00055974 | -0.042725 | 0.0022729 | 0.065875 | 0.058148 | -0.0044092 | 0.0079425 | -0.0041636 | -0.009155 | 63.0478 | -59.3079 | 63.1439 | -59.1156 | -59.5139 | -59.5001 | -0.045776 | 63.002 | -59.2529 | 63.1302 | -59.2896 | -59.436 | -59.3353 | -0.064087 | -0.045776 | 0.050354 | 0.12817 | -0.25635 | -0.27008 | -0.19226 | -0.20599 | -0.009156 | -0.091553 | 0.036621 | -0.045777 | -0.091553 | -0.19226 | -0.082397 | -0.1831 | 0.19226 | 122.4518 | -0.036621 | 122.3831 | 122.3557 | 122.2549 | 122.2916 | 122.2458 | -122.4014 | -122.3465 | 122.3877 | 122.374 | 59.2346 | 59.198
426.3125 | 122.5937 | -59.2072 | 63.1302 | -0.058212 | 0.0028348 | 0.064871 | 0.058526 | -0.002649 | -0.0038154 | 0.00055974 | -0.021362 | 0.0012047 | 0.064593 | 0.06712 | -0.0048364 | 0.0062335 | -0.000532 | 0.013733 | 63.0386 | -59.3079 | 63.0981 | -59.3216 | -59.4955 | -59.3811 | 0.036621 | 63.002 | -59.2072 | 63.1531 | -59.2255 | -59.3719 | -59.2804 | -0.10071 | -0.091553 | -0.032043 | -0.11444 | -0.17395 | -0.28839 | -0.073243 | -0.18768 | 0 | -0.12817 | 0.022888 | -0.018311 | -0.073243 | -0.1648 | -0.073243 | -0.1648 | -0.013733 | 122.406 | -0.018311 | 122.3602 | 122.3465 | 122.2092 | 122.2458 | 122.2092 | -122.438 | -122.3373 | 122.3053 | 122.3602 | 59.2209 | 59.2438
427.3125 | 122.6715 | -59.2209 | 63.0707 | -0.18791 | 0.002194 | 0.064871 | 0.060663 | 0.00055542 | -0.0014654 | -0.0020039 | 0.018311 | 0.00077755 | 0.066729 | 0.059003 | -0.0035548 | 0.0070879 | -0.0001046 | -0.054932 | 62.9471 | -59.2941 | 63.1989 | -59.0469 | -59.4406 | -59.436 | 0.004578 | 62.9562 | -59.23 | 63.1897 | -59.2117 | -59.317 | -59.2712 | -0.073242 | -0.1236 | 0.12817 | 0.17395 | -0.21515 | -0.21973 | -0.14191 | -0.14648 | -0.009156 | -0.11444 | 0.11902 | 0.009155 | -0.050354 | -0.096131 | -0.041198 | -0.086975 | 0.24719 | 122.493 | 0.018311 | 122.4197 | 122.2412 | 122.1863 | 122.168 | 122.1771 | -122.3648 | -122.3007 | 122.4197 | 122.4106 | 59.166 | 59.2255
428.3125 | 122.6395 | -59.2346 | 63.1531 | 0.018082 | 0.0030484 | 0.064871 | 0.060876 | -0.00029898 | -0.0031744 | -0.00050846 | -0.015259 | 0.0027001 | 0.066089 | 0.065198 | -0.0046228 | 0.0066607 | 0.0007498 | 0.013733 | 63.0478 | -59.3079 | 63.1622 | -59.0836 | -59.4955 | -59.4681 | 0.022888 | 62.9883 | -59.2163 | 63.1256 | -59.436 | -59.3491 | -59.1843 | -0.073242 | -0.10529 | 0.009155 | 0.15106 | -0.23346 | -0.26093 | -0.16022 | -0.18768 | 0.01831 | -0.16479 | -0.027466 | -0.20142 | 0.050354 | -0.11444 | 0.032044 | -0.13275 | 0.2243 | 122.4701 | -0.21973 | 122.3419 | 122.3557 | 122.2046 | 122.2824 | 122.2229 | -122.4609 | -122.3694 | 122.3969 | 122.3602 | 59.2484 | 59.2575
429.3125 | 122.5525 | -59.23 | 63.1485 | -0.0048066 | 0.0047574 | 0.064444 | 0.060876 | 0.0026916 | -0.0046698 | 0.0029095 | -0.027466 | 0.0035547 | 0.069507 | 0.060071 | -0.0035548 | 0.0081561 | -0.0030954 | -0.027466 | 63.0157 | -59.3124 | 63.1348 | -59.1476 | -59.5184 | -59.5093 | -0.050354 | 63.0112 | -59.2255 | 63.1027 | -59.3033 | -59.4406 | -59.3399 | -0.082397 | -0.13275 | -0.013733 | 0.082398 | -0.27923 | -0.28839 | -0.19684 | -0.20599 | 0.004578 | -0.13733 | -0.045777 | -0.073242 | -0.10986 | -0.21057 | -0.11444 | -0.21515 | 0.16479 | 122.4472 | -0.07782 | 122.3282 | 122.3282 | 122.2366 | 122.2458 | 122.2412 | -122.4609 | -122.374 | 122.3648 | 122.3328 | 59.2026 | 59.1797
430.3125 | 122.6028 | -59.2209 | 63.1165 | -0.065842 | 0.0013394 | 0.064657 | 0.060235 | 0.0067504 | -0.0038154 | 0.00013254 | -0.0061035 | -0.00050405 | 0.065448 | 0.062848 | -0.0048364 | 0.0068743 | -0.0022408 | 0.013733 | 63.0432 | -59.3308 | 63.3041 | -59.0561 | -59.4955 | -59.4543 | 0.027466 | 63.0112 | -59.2163 | 63.1439 | -59.2575 | -59.3857 | -59.2896 | -0.10986 | -0.073242 | 0.18768 | 0.16479 | -0.23346 | -0.27466 | -0.1236 | -0.16479 | 0.004577 | -0.10529 | 0.027466 | -0.036621 | -0.068665 | -0.16479 | -0.073242 | -0.16937 | 0.27466 | 122.6349 | -0.041198 | 122.3602 | 122.374 | 122.2275 | 122.2641 | 122.2321 | -122.4472 | -122.3328 | 122.525 | 122.3648 | 59.2346 | 59.2484
431.3125 | 122.5388 | -59.2255 | 63.1302 | -0.042954 | 0.0017666 | 0.064016 | 0.062585 | -0.0013672 | -0.0016792 | 0.00034614 | -0.021362 | 0.0029137 | 0.068438 | 0.063702 | -0.003982 | 0.0077289 | -0.0016 | -0.009155 | 63.0478 | -59.3079 | 63.1668 | -59.1019 | -59.5047 | -59.4864 | -0.004578 | 63.0157 | -59.2117 | 63.1393 | -59.2758 | -59.4223 | -59.3262 | -0.082397 | -0.082397 | 0.036621 | 0.1236 | -0.26093 | -0.27924 | -0.17853 | -0.19684 | 0.013733 | -0.11444 | 0.009155 | -0.050354 | -0.10071 | -0.19684 | -0.11444 | -0.21057 | 0.20599 | 122.4747 | -0.064087 | 122.3511 | 122.3557 | 122.2275 | 122.2733 | 122.2412 | -122.438 | -122.3419 | 122.3923 | 122.3648 | 59.2163 | 59.2209
432.3125 | 122.5616 | -59.23 | 63.121 | -0.042954 | 0.0043302 | 0.064657 | 0.060663 | -0.0024354 | -0.0010382 | -0.0020039 | -0.021362 | 0.0024865 | 0.066516 | 0.069043 | -0.0037684 | 0.0075153 | -0.0001046 | -0.009155 | 63.0478 | -59.3124 | 63.1577 | -59.0927 | -59.4681 | -59.4681 | 0.027466 | 63.002 | -59.2392 | 63.1302 | -59.2529 | -59.3857 | -59.2987 | -0.082397 | -0.073242 | 0.036621 | 0.13733 | -0.23804 | -0.23804 | -0.15564 | -0.15564 | -0.009155 | -0.11902 | 0.009155 | -0.022888 | -0.068664 | -0.15564 | -0.059509 | -0.14648 | 0.21973 | 122.4701 | -0.013733 | 122.3694 | 122.3602 | 122.2412 | 122.2778 | 122.2321 | -122.4335 | -122.3602 | 122.3877 | 122.3602 | 59.2209 | 59.2575
433.3125 | 122.5616 | -59.23 | 63.176 | -0.012436 | 0.000485 | 0.065085 | 0.059808 | 0.00098262 | -0.0025336 | 0.0046185 | -0.0030517 | 0.0027001 | 0.066943 | 0.063916 | -0.00505 | 0.0066607 | 0.0020316 | 0.009155 | 63.0569 | -59.3124 | 63.1531 | -59.111 | -59.4772 | -59.4772 | 0.009155 | 63.0203 | -59.2026 | 63.1439 | -59.2529 | -59.3857 | -59.2896 | -0.082397 | -0.11902 | -0.022888 | 0.11902 | -0.24719 | -0.24719 | -0.1648 | -0.1648 | 0.027466 | -0.15564 | -0.032043 | -0.022888 | -0.059509 | -0.15564 | -0.086975 | -0.1831 | 0.20142 | 122.4655 | -0.050354 | 122.3465 | 122.3694 | 122.2229 | 122.287 | 122.2504 | -122.4884 | -122.3785 | 122.3831 | 122.374 | 59.2392 | 59.2392
434.3125 | 122.5891 | -59.2163 | 63.1577 | -0.065842 | 0.0030484 | 0.062094 | 0.059595 | 0.0016236 | -0.0027472 | -0.00072206 | 0.0091553 | 0.0024865 | 0.066516 | 0.059216 | -0.0037684 | 0.0062335 | -0.0026682 | 0 | 63.0432 | -59.2896 | 63.1393 | -59.1385 | -59.4681 | -59.4727 | -0.009155 | 63.0249 | -59.2255 | 63.1439 | -59.2484 | -59.3857 | -59.3079 | -0.073242 | -0.11444 | -0.018311 | 0.07782 | -0.25635 | -0.25177 | -0.1831 | -0.17853 | -0.009155 | -0.13275 | -0.013733 | -0.032043 | -0.091552 | -0.16937 | -0.082397 | -0.16022 | 0.15106 | 122.4289 | -0.022888 | 122.3694 | 122.3328 | 122.2504 | 122.2595 | 122.2412 | -122.4472 | -122.3831 | 122.3557 | 122.3602 | 59.2163 | 59.2072
435.3125 | 122.5662 | -59.2117 | 63.1531 | -0.035324 | 0.0019802 | 0.062735 | 0.060235 | 0.00034182 | -0.0016792 | 0.00013254 | 0.015259 | 0.0018457 | 0.065448 | 0.062207 | -0.0035548 | 0.0075153 | -0.0026682 | -0.013733 | 63.0798 | -59.2987 | 63.121 | -59.1614 | -59.5093 | -59.491 | -0.013733 | 63.0341 | -59.2392 | 63.1302 | -59.2529 | -59.3948 | -59.317 | -0.086975 | -0.073242 | -0.032043 | 0.050354 | -0.27924 | -0.29755 | -0.19226 | -0.21057 | -0.027466 | -0.11902 | -0.022888 | -0.041199 | -0.10529 | -0.1831 | -0.07782 | -0.15564 | 0.13733 | 122.4197 | -0.013733 | 122.3694 | 122.3785 | 122.2733 | 122.2916 | 122.2458 | -122.4518 | -122.3923 | 122.3328 | 122.3419 | 59.198 | 59.198
436.3125 | 122.5891 | -59.2392 | 63.1439 | -0.08873 | 0.0011258 | 0.064444 | 0.060449 | 0.0011962 | -0.003388 | -0.0032855 | -0.0091553 | 0.0027001 | 0.06737 | 0.060712 | -0.0037684 | 0.0087969 | -0.0024546 | 0.018311 | 63.0203 | -59.2987 | 63.0341 | -59.2621 | -59.2804 | -59.4131 | 0.050354 | 63.002 | -59.2255 | 63.1622 | -59.23 | -59.3811 | -59.285 | -0.059509 | -0.1236 | -0.10986 | -0.022888 | -0.17395 | -0.041199 | -0.11444 | 0.01831 | 0.013733 | -0.14191 | 0.01831 | 0.009155 | -0.045776 | -0.14191 | -0.059509 | -0.15564 | 0.036621 | 122.3328 | -0.004578 | 122.3877 | 122.319 | 122.2275 | 122.2595 | 122.2412 | -122.4426 | -122.3694 | 122.2733 | 122.4014 | 59.2575 | 59.2896
437.3125 | 122.6486 | -59.2163 | 63.1119 | -0.050583 | 0.0043302 | 0.062735 | 0.061731 | 0.00055542 | 2.9842e-05 | 0.0012005 | -0.0061035 | 0.0016321 | 0.065234 | 0.064343 | -0.0031274 | 0.0062335 | -0.0020272 | -0.07782 | 63.0112 | -59.3399 | 63.1302 | -59.1522 | -59.5184 | -59.4864 | -0.068665 | 62.9791 | -59.2621 | 63.1851 | -59.2529 | -59.3719 | -59.2804 | -0.1236 | -0.10071 | 0.018311 | 0.064087 | -0.27008 | -0.30212 | -0.14648 | -0.17853 | -0.045776 | -0.13275 | 0.073243 | -0.036621 | -0.064087 | -0.15564 | -0.018311 | -0.10986 | 0.18768 | 122.4701 | 0.009155 | 122.4472 | 122.3511 | 122.2412 | 122.2275 | 122.1954 | -122.4518 | -122.374 | 122.3465 | 122.4014 | 59.1385 | 59.1476
438.3125 | 122.5754 | -59.2255 | 63.1531 | -0.012436 | 0.0019802 | 0.062948 | 0.058954 | -0.0067078 | -0.0012518 | 0.00077334 | -0.0091553 | 0.0022729 | 0.06737 | 0.055798 | -0.0046228 | 0.0064471 | -0.0026682 | 0 | 63.0844 | -59.285 | 63.121 | -59.1568 | -59.4864 | -59.5047 | -0.032043 | 63.0112 | -59.2392 | 63.1073 | -59.2804 | -59.4086 | -59.3216 | -0.059509 | -0.068664 | -0.032043 | 0.068665 | -0.27924 | -0.26093 | -0.21973 | -0.20142 | -0.013733 | -0.14191 | -0.045776 | -0.054932 | -0.09613 | -0.1831 | -0.082397 | -0.16937 | 0.12817 | 122.406 | -0.041199 | 122.3465 | 122.3694 | 122.2504 | 122.3099 | 122.2366 | -122.438 | -122.3923 | 122.3465 | 122.3328 | 59.2255 | 59.1934
439.3125 | 122.58 | -59.2209 | 63.1622 | -0.020065 | 0.0019802 | 0.065939 | 0.059595 | -0.00093998 | -0.0038154 | -0.0020039 | -0.0030517 | 0.0031273 | 0.067798 | 0.061352 | -0.0054774 | 0.0085833 | -0.0011728 | 0.004578 | 63.0386 | -59.3124 | 63.1348 | -59.1431 | -59.4635 | -59.4727 | 0 | 63.0432 | -59.2209 | 63.1393 | -59.2484 | -59.404 | -59.2896 | -0.091553 | -0.1236 | -0.027465 | 0.07782 | -0.25177 | -0.24262 | -0.16022 | -0.15106 | 0 | -0.11902 | -0.022888 | -0.027466 | -0.068665 | -0.18311 | -0.068665 | -0.18311 | 0.16937 | 122.4472 | -0.027466 | 122.3602 | 122.3511 | 122.2641 | 122.2595 | 122.2641 | -122.4747 | -122.3831 | 122.3557 | 122.3602 | 59.2255 | 59.2209
440.3125 | 122.5296 | -59.2392 | 63.1531 | -0.027695 | 0.0026212 | 0.064871 | 0.05874 | -0.0022218 | -0.0031744 | -0.0028583 | 0.045776 | 0.0022729 | 0.068011 | 0.057507 | -0.0041956 | 0.0066607 | 0.0009634 | 0.027466 | 63.0341 | -59.2712 | 63.1805 | -59.0881 | -59.436 | -59.4635 | 0.032043 | 63.0112 | -59.1934 | 63.1119 | -59.2804 | -59.3811 | -59.317 | -0.032043 | -0.11902 | 0.027466 | 0.15106 | -0.2243 | -0.19684 | -0.19226 | -0.16479 | 0.045777 | -0.14191 | -0.041199 | -0.041199 | -0.07782 | -0.14191 | -0.1236 | -0.18768 | 0.1831 | 122.4518 | -0.086976 | 122.3053 | 122.3053 | 122.2046 | 122.2733 | 122.2504 | -122.4243 | -122.3465 | 122.4197 | 122.3511 | 59.2667 | 59.2712
441.3125 | 122.525 | -59.2255 | 63.1622 | -0.012436 | 0.0030484 | 0.063803 | 0.059167 | 0.0016236 | -0.00061096 | -0.0015765 | 0.076294 | 0.0020593 | 0.070788 | 0.063061 | -0.0029138 | 0.0066607 | -0.0062998 | -0.004578 | 63.0478 | -59.3033 | 63.121 | -59.1248 | -59.4955 | -59.4589 | -0.15106 | 63.0386 | -59.2209 | 63.1073 | -59.2987 | -59.4315 | -59.3536 | -0.07782 | -0.11444 | -0.041198 | 0.10071 | -0.23346 | -0.27008 | -0.15564 | -0.19226 | 0.004578 | -0.1236 | -0.054931 | -0.073242 | -0.12817 | -0.20599 | -0.13275 | -0.21057 | 0.17853 | 122.4243 | -0.07782 | 122.3282 | 122.3511 | 122.2595 | 122.2733 | 122.2641 | -122.4655 | -122.3831 | 122.3465 | 122.3328 | 59.2209 | 59.0744
442.3125 | 122.5937 | -59.2209 | 63.1531 | -0.027695 | 0.002194 | 0.062948 | 0.061303 | -0.0015808 | -0.0012518 | 0.0012005 | -0.027466 | 0.0029137 | 0.066943 | 0.063916 | -0.0063318 | 0.0075153 | -0.0007456 | 0 | 63.0753 | -59.2896 | 63.1393 | -59.1431 | -59.5093 | -59.4818 | -0.013733 | 63.0386 | -59.2346 | 63.1302 | -59.2529 | -59.3857 | -59.3033 | -0.068665 | -0.07782 | -0.013733 | 0.07782 | -0.26093 | -0.28839 | -0.19226 | -0.21973 | -0.013733 | -0.11444 | -0.022888 | -0.032044 | -0.082398 | -0.16479 | -0.068665 | -0.15106 | 0.14649 | 122.4289 | -0.018311 | 122.3648 | 122.3648 | 122.2733 | 122.2961 | 122.2595 | -122.4426 | -122.3877 | 122.3602 | 122.3511 | 59.2209 | 59.2072
443.3125 | 122.5296 | -59.2438 | 63.1622 | 0.0028229 | 0.0028348 | 0.063162 | 0.060022 | -0.0015808 | -0.0018928 | -0.00050846 | 0.030518 | 0.0027001 | 0.066729 | 0.063702 | -0.0044092 | 0.0064471 | 0.0016044 | -0.009155 | 63.0936 | -59.3033 | 63.0981 | -59.1202 | -59.5001 | -59.4818 | -0.041199 | 63.0386 | -59.2026 | 63.1119 | -59.285 | -59.4269 | -59.3628 | -0.05951 | -0.068664 | -0.064086 | 0.1236 | -0.23804 | -0.25635 | -0.17853 | -0.19684 | 0.041198 | -0.1236 | -0.050354 | -0.041199 | -0.11902 | -0.18311 | -0.16022 | -0.2243 | 0.18311 | 122.4014 | -0.082397 | 122.3145 | 122.3969 | 122.2412 | 122.3373 | 122.2824 | -122.4655 | -122.3648 | 122.3419 | 122.3557 | 59.2346 | 59.2026
444.3125 | 122.5708 | -59.2346 | 63.1622 | 0.0028229 | 0.0026212 | 0.062521 | 0.061731 | 0.0022644 | -0.0018928 | -0.0028583 | 0.0091553 | 0.0016321 | 0.066516 | 0.063916 | -0.003341 | 0.0073015 | -0.003309 | -0.009155 | 63.0844 | -59.3124 | 63.1256 | -59.1522 | -59.5047 | -59.4818 | -0.027466 | 63.0478 | -59.2529 | 63.1165 | -59.2804 | -59.4086 | -59.3308 | -0.07782 | -0.077819 | -0.036621 | 0.082397 | -0.24719 | -0.27008 | -0.16937 | -0.19226 | -0.018311 | -0.11444 | -0.045776 | -0.045777 | -0.096131 | -0.17395 | -0.07782 | -0.15564 | 0.16022 | 122.438 | -0.027466 | 122.3694 | 122.3969 | 122.3007 | 122.319 | 122.2824 | -122.4747 | -122.4152 | 122.3602 | 122.3511 | 59.2255 | 59.2072
445.3125 | 122.5708 | -59.198 | 63.1851 | -0.027695 | 0.001553 | 0.063589 | 0.058099 | -0.003717 | -0.0031744 | -0.0013629 | 0.033569 | 0.00099115 | 0.066302 | 0.058789 | -0.0037684 | 0.0066607 | -0.0037362 | 0.009155 | 63.0524 | -59.2712 | 63.1439 | -59.0973 | -59.5047 | -59.4818 | 0.013733 | 63.0295 | -59.2484 | 63.1119 | -59.285 | -59.4543 | -59.2804 | -0.073242 | -0.13275 | -0.041199 | 0.10071 | -0.28381 | -0.3067 | -0.21057 | -0.23346 | -0.050354 | -0.15564 | -0.073243 | -0.086975 | -0.082398 | -0.25635 | -0.032044 | -0.20599 | 0.17395 | 122.4152 | -0.036621 | 122.3602 | 122.3236 | 122.2778 | 122.2504 | 122.2275 | -122.4564 | -122.4335 | 122.3419 | 122.3099 | 59.2072 | 59.2117
446.3125 | 122.5342 | -59.2392 | 63.1393 | -0.058212 | 0.0030484 | 0.064871 | 0.060235 | -0.0039306 | -0.003388 | -0.0030719 | 0.030518 | 0.0035547 | 0.068438 | 0.059644 | -0.0029138 | 0.0075153 | -0.0018136 | 0.054932 | 63.0341 | -59.2484 | 63.1989 | -59.079 | -59.4406 | -59.436 | 0.018311 | 63.0157 | -59.1934 | 63.1073 | -59.2575 | -59.3857 | -59.3262 | -0.009155 | -0.10528 | 0.05951 | 0.16022 | -0.19684 | -0.20142 | -0.18768 | -0.19226 | 0.045777 | -0.1236 | -0.032043 | -0.01831 | -0.086975 | -0.14648 | -0.13275 | -0.19226 | 0.16937 | 122.4472 | -0.064087 | 122.3007 | 122.2824 | 122.2092 | 122.2733 | 122.2549 | -122.3877 | -122.3328 | 122.4381 | 122.3465 | 59.2941 | 59.2575
447.3125 | 122.5845 | -59.2346 | 63.1485 | -0.035324 | 0.0045438 | 0.063376 | 0.062158 | 0.0029052 | -0.0042426 | -0.0015765 | -0.039673 | 0.0027001 | 0.067157 | 0.06477 | -0.0029138 | 0.0085833 | -0.0028818 | 0.018311 | 63.0707 | -59.3079 | 63.1668 | -59.1202 | -59.4772 | -59.4635 | 0.018311 | 63.0341 | -59.1934 | 63.1485 | -59.2758 | -59.3857 | -59.2941 | -0.073242 | -0.07782 | 0.01831 | 0.11444 | -0.22888 | -0.24262 | -0.15564 | -0.16937 | 0.041199 | -0.11444 | 0 | -0.041199 | -0.059509 | -0.15106 | -0.10071 | -0.19226 | 0.18768 | 122.4747 | -0.082398 | 122.3419 | 122.3785 | 122.2275 | 122.3053 | 122.2687 | -122.4564 | -122.3419 | 122.4014 | 122.3831 | 59.2529 | 59.2529
448.3125 | 122.6028 | -59.198 | 63.121 | -0.050583 | 0.003262 | 0.063162 | 0.058954 | -0.00072638 | -0.00061096 | -0.00050846 | 0.048828 | -0.00029045 | 0.065448 | 0.063702 | -0.0024866 | 0.0058063 | -0.0041636 | 0.050354 | 63.0341 | -59.2667 | 63.208 | -59.0424 | -59.3948 | -59.3994 | 0.082397 | 62.9974 | -59.1934 | 63.1714 | -59.1934 | -59.3353 | -59.2667 | -0.068665 | -0.086975 | 0.086975 | 0.15564 | -0.20142 | -0.19684 | -0.13275 | -0.12817 | 0.004578 | -0.1236 | 0.050354 | 0.004578 | -0.068665 | -0.13733 | -0.073243 | -0.14191 | 0.22431 | 122.4747 | 0 | 122.3648 | 122.3007 | 122.1909 | 122.2321 | 122.1954 | -122.3877 | -122.3145 | 122.406 | 122.3694 | 59.2484 | 59.2804
449.3125 | 122.5388 | -59.2529 | 63.1714 | -0.0048066 | 0.001553 | 0.064016 | 0.058099 | -0.002649 | -0.0031744 | -0.0054217 | 0.0091553 | 0.0012047 | 0.066516 | 0.059644 | -0.0061182 | 0.0064471 | 0.0016044 | 0.041199 | 63.0569 | -59.285 | 63.1622 | -59.1064 | -59.4543 | -59.4498 | 0.032043 | 63.0249 | -59.2026 | 63.1256 | -59.2758 | -59.3903 | -59.317 | -0.032043 | -0.11444 | -0.009156 | 0.14648 | -0.19684 | -0.20142 | -0.16479 | -0.16937 | 0.050354 | -0.14649 | -0.045777 | -0.022888 | -0.064087 | -0.13733 | -0.11444 | -0.18768 | 0.17853 | 122.4472 | -0.073242 | 122.3282 | 122.3419 | 122.2275 | 122.3099 | 122.2778 | -122.4564 | -122.374 | 122.4152 | 122.3785 | 59.2941 | 59.285
450.3125 | 122.5525 | -59.2438 | 63.1622 | -0.035324 | 0.0026212 | 0.061239 | 0.059167 | -0.0011536 | -0.003388 | -0.0015765 | -0.05188 | 0.0024865 | 0.065875 | 0.057935 | -0.0041956 | 0.0055927 | -0.0013864 | -0.022888 | 63.0569 | -59.3079 | 63.0707 | -59.3536 | -59.5825 | -59.4635 | -0.013733 | 63.0478 | -59.2392 | 63.089 | -59.2896 | -59.3903 | -59.3445 | -0.064087 | -0.10528 | -0.091552 | -0.10986 | -0.21973 | -0.33875 | -0.15564 | -0.27466 | 0.004577 | -0.11444 | -0.073242 | -0.045777 | -0.10071 | -0.14648 | -0.10529 | -0.15106 | -0.045777 | 122.3785 | -0.050354 | 122.3282 | 122.3648 | 122.287 | 122.3007 | 122.2916 | -122.4701 | -122.4014 | 122.3145 | 122.3328 | 59.2209 | 59.23
451.3125 | 122.5204 | -59.2255 | 63.1577 | -0.050583 | 0.0034756 | 0.062948 | 0.059808 | -0.0039306 | -0.003388 | -0.0017903 | 0.015259 | 0.00013675 | 0.064593 | 0.063489 | -0.0063318 | 0.0075153 | -0.0037362 | -0.009155 | 63.0753 | -59.3033 | 63.121 | -59.1385 | -59.4955 | -59.4818 | 0.20142 | 63.089 | -59.1843 | 63.089 | -59.2987 | -59.4086 | -59.3628 | -0.07782 | -0.082398 | -0.036621 | 0.086975 | -0.25635 | -0.27008 | -0.17853 | -0.19226 | 0.041199 | -0.068665 | -0.068665 | -0.073242 | -0.13733 | -0.1831 | -0.17853 | -0.2243 | 0.16479 | 122.4243 | -0.11444 | 122.2733 | 122.3785 | 122.2733 | 122.3007 | 122.3145 | -122.4609 | -122.3419 | 122.3465 | 122.3145 | 59.2163 | 59.4269
452.3125 | 122.58 | -59.2163 | 63.176 | -0.012436 | 0.003262 | 0.063376 | 0.060663 | -0.00051278 | -0.004029 | 0.00077334 | -0.015259 | 0.0029137 | 0.066516 | 0.058575 | -0.003341 | 0.0073015 | 0.002886 | -0.004578 | 63.0844 | -59.3124 | 63.1165 | -59.1431 | -59.523 | -59.5001 | 0 | 63.0524 | -59.2621 | 63.1027 | -59.285 | -59.4086 | -59.3216 | -0.09613 | -0.091552 | -0.059509 | 0.073243 | -0.28381 | -0.3067 | -0.18768 | -0.21057 | -0.045776 | -0.1236 | -0.073242 | -0.068664 | -0.10528 | -0.19226 | -0.059509 | -0.14648 | 0.16937 | 122.4289 | -0.022888 | 122.3648 | 122.3969 | 122.3145 | 122.3007 | 122.2687 | -122.4884 | -122.438 | 122.3328 | 122.319 | 59.2117 | 59.2163
453.3125 | 122.612 | -59.198 | 63.1485 | 0.018082 | 0.003262 | 0.062094 | 0.058313 | -0.0032898 | -0.0048834 | 0.0012005 | 0.036621 | 0.00077755 | 0.066302 | 0.058789 | -0.0041956 | 0.0066607 | -0.0009592 | 0.064087 | 63.0203 | -59.2575 | 63.2446 | -59.0057 | -59.3811 | -59.3811 | 0.10071 | 62.9837 | -59.2026 | 63.1943 | -59.1751 | -59.3033 | -59.2484 | -0.059509 | -0.12817 | 0.09613 | 0.19226 | -0.18311 | -0.18311 | -0.1236 | -0.1236 | -0.004578 | -0.16479 | 0.045776 | 0.022888 | -0.050354 | -0.10529 | -0.045776 | -0.10071 | 0.25177 | 122.5021 | 0.027466 | 122.3969 | 122.2778 | 122.1863 | 122.2183 | 122.1817 | -122.406 | -122.3511 | 122.4426 | 122.3923 | 59.2621 | 59.2987
454.3125 | 122.6166 | -59.2163 | 63.1348 | -0.065842 | 0.002194 | 0.062521 | 0.059167 | 0.00098262 | -0.004029 | -0.0020039 | 0.042725 | 0.0014185 | 0.066089 | 0.064343 | -0.0024866 | 0.0068743 | 0.0016044 | 0.068665 | 63.0066 | -59.2667 | 63.2355 | -59.0057 | -59.3994 | -59.3765 | 0.13733 | 62.9837 | -59.1843 | 63.1943 | -59.1797 | -59.2941 | -59.2346 | -0.050354 | -0.12817 | 0.10071 | 0.21057 | -0.16022 | -0.1831 | -0.10986 | -0.13275 | 0.032044 | -0.15106 | 0.059509 | 0.036622 | -0.01831 | -0.077819 | -0.050354 | -0.10986 | 0.26093 | 122.5021 | 0.004578 | 122.3785 | 122.2733 | 122.168 | 122.2229 | 122.2 | -122.4014 | -122.319 | 122.4518 | 122.4106 | 59.285 | 59.3536
455.3125 | 122.6349 | -59.1797 | 63.1485 | -0.042954 | 0.0019802 | 0.064444 | 0.057245 | -0.0035034 | -0.0016792 | 0.00055974 | 0.018311 | 0.0027001 | 0.065448 | 0.054517 | -0.0044092 | 0.0081561 | -0.0026682 | 0.07782 | 63.0112 | -59.2529 | 63.2492 | -59.0012 | -59.3719 | -59.3674 | 0.1236 | 62.9791 | -59.2163 | 63.2217 | -59.166 | -59.2758 | -59.2209 | -0.073243 | -0.13733 | 0.10071 | 0.17853 | -0.18768 | -0.19226 | -0.11444 | -0.11902 | -0.036622 | -0.16937 | 0.073242 | 0.013732 | -0.041199 | -0.096131 | -0.004577 | -0.059509 | 0.25177 | 122.5021 | 0.050354 | 122.4381 | 122.2641 | 122.1954 | 122.1909 | 122.1588 | -122.4014 | -122.3648 | 122.4289 | 122.4014 | 59.2575 | 59.3033
456.3125 | 122.5662 | -59.2209 | 63.1668 | -0.073471 | 0.0036892 | 0.063162 | 0.060876 | -0.0013672 | -0.0018928 | -0.0017903 | 0.018311 | 0.0027001 | 0.06737 | 0.060071 | -0.0035548 | 0.0073015 | -0.0018136 | 0.068665 | 63.0066 | -59.2758 | 63.2355 | -59.0378 | -59.3948 | -59.3948 | 0.09613 | 63.0112 | -59.2163 | 63.1577 | -59.2209 | -59.3353 | -59.2758 | -0.054932 | -0.16022 | 0.068665 | 0.1831 | -0.17395 | -0.17395 | -0.11902 | -0.11902 | 0.004577 | -0.15564 | -0.009155 | 0 | -0.054932 | -0.11444 | -0.059509 | -0.11902 | 0.23804 | 122.5113 | -0.004577 | 122.374 | 122.2824 | 122.2275 | 122.2275 | 122.2321 | -122.4426 | -122.3831 | 122.4564 | 122.3785 | 59.2896 | 59.317
457.3125 | 122.5616 | -59.2346 | 63.1348 | -0.058212 | 0.0039028 | 0.06188 | 0.062158 | -0.0035034 | -0.0036018 | -0.00029486 | -0.091553 | 0.0012047 | 0.066516 | 0.064984 | -0.0044092 | 0.0077289 | -0.0013864 | 0.022888 | 63.0295 | -59.3262 | 63.1714 | -59.1156 | -59.5139 | -59.4864 | 0.018311 | 63.0203 | -59.2484 | 63.1256 | -59.2712 | -59.4269 | -59.317 | -0.091553 | -0.10529 | 0.036621 | 0.11902 | -0.25177 | -0.27924 | -0.16022 | -0.18768 | -0.013733 | -0.11444 | -0.009156 | -0.036621 | -0.082398 | -0.19226 | -0.068665 | -0.17853 | 0.21057 | 122.4976 | -0.022888 | 122.374 | 122.3557 | 122.2687 | 122.2641 | 122.2549 | -122.4609 | -122.3831 | 122.406 | 122.3602 | 59.2575 | 59.2529
458.3125 | 122.6303 | -59.2072 | 63.1622 | -0.027695 | 0.0047574 | 0.064657 | 0.059808 | -0.0022218 | -0.0021064 | -0.00093566 | 0.018311 | 0.0022729 | 0.065875 | 0.061993 | -0.0029138 | 0.0068743 | -0.0041636 | 0.068665 | 63.0386 | -59.2667 | 63.2355 | -59.0195 | -59.3903 | -59.3765 | 0.10529 | 62.9883 | -59.2072 | 63.1897 | -59.1843 | -59.3033 | -59.2392 | -0.05951 | -0.1236 | 0.073243 | 0.18768 | -0.16937 | -0.18311 | -0.10986 | -0.1236 | 0 | -0.17395 | 0.027466 | 0.022888 | -0.032044 | -0.096131 | -0.032044 | -0.096131 | 0.24719 | 122.5021 | 0.022888 | 122.3969 | 122.3053 | 122.1954 | 122.2458 | 122.1954 | -122.4289 | -122.3694 | 122.4426 | 122.3969 | 59.2758 | 59.3124
459.3125 | 122.525 | -59.2255 | 63.1714 | -0.027695 | 0.0019802 | 0.063803 | 0.060663 | -0.002008 | -0.004029 | -0.00050846 | 0.0061035 | 0.00056395 | 0.06737 | 0.054517 | -0.0035548 | 0.0058063 | -0.0041636 | 0.050354 | 63.0432 | -59.2758 | 63.1851 | -59.0973 | -59.4498 | -59.436 | 0.032043 | 63.0112 | -59.2163 | 63.1027 | -59.2529 | -59.3811 | -59.3216 | -0.050354 | -0.12817 | 0.013733 | 0.12817 | -0.21057 | -0.2243 | -0.16022 | -0.17395 | 0.009155 | -0.16022 | -0.068665 | -0.027466 | -0.09613 | -0.15564 | -0.10528 | -0.16479 | 0.17853 | 122.4609 | -0.036621 | 122.319 | 122.319 | 122.2275 | 122.2687 | 122.2366 | -122.4472 | -122.3877 | 122.4106 | 122.3282 | 59.2758 | 59.2575
460.3125 | 122.6578 | -59.198 | 63.1302 | -0.073471 | 0.0036892 | 0.063803 | 0.058954 | -0.004358 | -0.0042426 | 0.0016277 | 0.033569 | 0.0020593 | 0.064593 | 0.057935 | -0.0037684 | 0.0077289 | 0.0009634 | 0.059509 | 63.0066 | -59.2667 | 63.2538 | -59.0057 | -59.3903 | -59.3674 | 0.11902 | 62.9929 | -59.1888 | 63.2217 | -59.1751 | -59.2712 | -59.2117 | -0.068665 | -0.1236 | 0.1236 | 0.19226 | -0.16937 | -0.19226 | -0.10071 | -0.1236 | 0.009155 | -0.13733 | 0.091553 | 0.022888 | -0.013733 | -0.073242 | -0.022888 | -0.082397 | 0.26093 | 122.5204 | 0.013733 | 122.4106 | 122.2733 | 122.1817 | 122.2046 | 122.1909 | -122.3969 | -122.319 | 122.4518 | 122.4197 | 59.2575 | 59.317
461.3125 | 122.5296 | -59.2529 | 63.1302 | -0.065842 | 0.0041166 | 0.063376 | 0.063867 | 0.00098262 | -0.0021064 | -0.00072206 | -0.091553 | 0.0012047 | 0.06502 | 0.06413 | -0.0048364 | 0.0087969 | 0.002886 | -0.041199 | 63.0066 | -59.317 | 63.1119 | -59.1843 | -59.5642 | -59.5459 | -0.13733 | 63.0066 | -59.2392 | 63.0753 | -59.3445 | -59.4772 | -59.3765 | -0.064087 | -0.1236 | -0.018311 | 0.068665 | -0.29297 | -0.31128 | -0.22888 | -0.24719 | 0.013733 | -0.1236 | -0.054932 | -0.091552 | -0.1236 | -0.2243 | -0.13733 | -0.23804 | 0.13275 | 122.4289 | -0.10529 | 122.3145 | 122.3236 | 122.2458 | 122.2595 | 122.2595 | -122.4472 | -122.3694 | 122.3648 | 122.3282 | 59.2117 | 59.1156
462.3125 | 122.5616 | -59.23 | 63.1439 | -0.027695 | 0.002194 | 0.064444 | 0.062158 | 0.00098262 | -0.0048834 | -0.0028583 | -0.012207 | 0.0037683 | 0.067157 | 0.066907 | -0.0044092 | 0.0081561 | -0.0035226 | -0.004578 | 63.0753 | -59.2941 | 63.1119 | -59.1385 | -59.5047 | -59.4818 | -0.009155 | 63.0341 | -59.2392 | 63.1165 | -59.2758 | -59.4131 | -59.3262 | -0.064086 | -0.068665 | -0.032044 | 0.091553 | -0.25177 | -0.27466 | -0.18768 | -0.21057 | -0.009155 | -0.10986 | -0.027466 | -0.045776 | -0.09613 | -0.18311 | -0.086975 | -0.17395 | 0.15564 | 122.406 | -0.036621 | 122.3557 | 122.3694 | 122.2733 | 122.3053 | 122.2641 | -122.438 | -122.3831 | 122.3419 | 122.3465 | 59.2255 | 59.2209
463.3125 | 122.6715 | -59.1934 | 63.1256 | 0.30037 | 0.0002714 | 0.066153 | 0.059381 | 0.0031188 | -0.00082456 | 0.00013254 | 0.027466 | 0.00077755 | 0.065875 | 0.05473 | -0.0052638 | 0.0081561 | -0.0026682 | -0.13733 | 63.0661 | -59.285 | 63.2492 | -59.0149 | -59.3903 | -59.3811 | 0.13733 | 62.9745 | -59.198 | 63.2263 | -59.1476 | -59.2621 | -59.1934 | -0.091553 | -0.059509 | 0.1236 | 0.17853 | -0.18768 | -0.19684 | -0.096131 | -0.10529 | -0.004578 | -0.15106 | 0.10071 | 0.045776 | 0 | -0.068665 | 0.004578 | -0.064087 | 0.27008 | 122.5342 | 0.050354 | 122.4243 | 122.3511 | 122.1725 | 122.2595 | 122.168 | -122.4106 | -122.3236 | 122.4426 | 122.4197 | 59.0561 | 59.3307
464.3125 | 122.5388 | -59.2484 | 63.1577 | -0.012436 | 0.0039028 | 0.064016 | 0.060235 | 0.00034182 | -0.004029 | -0.00072206 | 0.0091553 | 0.0012047 | 0.066729 | 0.070111 | -0.0041956 | 0.0079425 | -0.0011728 | 0.036621 | 63.0478 | -59.285 | 63.1531 | -59.1064 | -59.4635 | -59.4543 | 0.032043 | 63.0203 | -59.2117 | 63.1302 | -59.2712 | -59.4131 | -59.3445 | -0.036621 | -0.10986 | -0.004578 | 0.14191 | -0.20599 | -0.21515 | -0.16937 | -0.17853 | 0.036621 | -0.13733 | -0.027466 | -0.022888 | -0.09613 | -0.1648 | -0.13275 | -0.20142 | 0.17853 | 122.438 | -0.059509 | 122.3419 | 122.3328 | 122.2321 | 122.2961 | 122.2687 | -122.4426 | -122.3694 | 122.4014 | 122.3785 | 59.285 | 59.2804
465.3125 | 122.644 | -59.2117 | 63.1439 | -0.0048066 | 0.0034756 | 0.064657 | 0.060449 | -0.00093998 | -0.0027472 | 0.00055974 | 0.030518 | 0.00077755 | 0.067798 | 0.058362 | -0.005691 | 0.0079425 | -0.0052316 | 0.050354 | 63.002 | -59.2712 | 63.2355 | -59.0012 | -59.3811 | -59.3674 | 0.11902 | 62.9745 | -59.2072 | 63.2126 | -59.1751 | -59.285 | -59.2209 | -0.059509 | -0.14191 | 0.091553 | 0.21057 | -0.15564 | -0.16937 | -0.096131 | -0.10986 | 0.004578 | -0.16937 | 0.068664 | 0.036621 | -0.009155 | -0.073242 | -0.013733 | -0.07782 | 0.27008 | 122.5067 | 0.032043 | 122.4197 | 122.2733 | 122.1817 | 122.2137 | 122.1863 | -122.4152 | -122.3511 | 122.4472 | 122.4243 | 59.2621 | 59.3308
466.3125 | 122.5342 | -59.2438 | 63.1393 | -0.0048066 | 0.0043302 | 0.062735 | 0.060876 | 0.0011962 | -0.0031744 | 0.00034614 | -0.094604 | 0.0035547 | 0.065448 | 0.059003 | -0.0041956 | 0.0081561 | -0.0030954 | -0.018311 | 63.0432 | -59.3308 | 63.1531 | -59.1248 | -59.5139 | -59.4955 | -0.041199 | 63.002 | -59.2392 | 63.1393 | -59.285 | -59.4315 | -59.3216 | -0.086976 | -0.09613 | 0.013733 | 0.11902 | -0.25177 | -0.27008 | -0.16479 | -0.1831 | 0.004577 | -0.13733 | 0 | -0.041199 | -0.07782 | -0.18768 | -0.082397 | -0.19226 | 0.20599 | 122.4838 | -0.045776 | 122.3785 | 122.374 | 122.2412 | 122.287 | 122.2458 | -122.4701 | -122.3785 | 122.3969 | 122.3831 | 59.2255 | 59.2026
467.3125 | 122.5388 | -59.2484 | 63.1165 | -0.050583 | 0.0030484 | 0.064871 | 0.059595 | 0.0033324 | -0.0016792 | 0.00013254 | -0.064087 | 0.0022729 | 0.06737 | 0.065198 | -0.0054774 | 0.0083697 | -0.0020272 | 0 | 63.0157 | -59.2896 | 63.1622 | -59.1156 | -59.5047 | -59.491 | -0.013733 | 63.0112 | -59.23 | 63.1302 | -59.2941 | -59.4223 | -59.317 | -0.041199 | -0.10071 | 0.045776 | 0.13275 | -0.24262 | -0.25635 | -0.20142 | -0.21515 | 0.01831 | -0.10529 | 0.013733 | -0.045776 | -0.068665 | -0.17395 | -0.086975 | -0.19226 | 0.17395 | 122.4518 | -0.064086 | 122.3602 | 122.3053 | 122.2412 | 122.2641 | 122.2595 | -122.406 | -122.3465 | 122.4106 | 122.3785 | 59.2484 | 59.2346
468.3125 | 122.6715 | -59.1751 | 63.1073 | -0.058212 | 0.0028348 | 0.063803 | 0.060449 | -0.00051278 | -0.0029608 | -0.0039265 | 0.076294 | -0.00029045 | 0.06737 | 0.057935 | -0.0020594 | 0.0049517 | -0.0013864 | 0.022888 | 63.0157 | -59.2712 | 63.2172 | -59.0149 | -59.3903 | -59.3811 | 0.12817 | 62.9883 | -59.2117 | 63.2355 | -59.1156 | -59.2529 | -59.198 | -0.09613 | -0.091553 | 0.10986 | 0.16022 | -0.20599 | -0.21515 | -0.10986 | -0.11902 | -0.036621 | -0.11902 | 0.12817 | 0.059509 | -0.022888 | -0.07782 | 0.013733 | -0.041199 | 0.25635 | 122.4884 | 0.09613 | 122.4472 | 122.287 | 122.2 | 122.1909 | 122.1634 | -122.3785 | -122.319 | 122.3923 | 122.4106 | 59.198 | 59.3033
469.3125 | 122.6166 | -59.198 | 63.1256 | -0.058212 | 0.0034756 | 0.063376 | 0.060235 | -0.0011536 | -0.0042426 | -0.0022175 | 0.033569 | 0.00013675 | 0.066302 | 0.062634 | -0.0052638 | 0.0092241 | -0.0028818 | 0.064087 | 63.0112 | -59.2667 | 63.2446 | -59.0195 | -59.3903 | -59.3719 | 0.10986 | 62.9837 | -59.2117 | 63.1943 | -59.1751 | -59.2896 | -59.2438 | -0.068665 | -0.11444 | 0.11902 | 0.17853 | -0.17395 | -0.19226 | -0.10529 | -0.1236 | -0.013733 | -0.14191 | 0.068665 | 0.022888 | -0.045776 | -0.091553 | -0.032043 | -0.07782 | 0.24719 | 122.5113 | 0.036621 | 122.406 | 122.2778 | 122.1954 | 122.2092 | 122.1817 | -122.3923 | -122.3373 | 122.4426 | 122.3923 | 59.2621 | 59.3079
470.3125 | 122.6349 | -59.1843 | 63.1439 | -0.020065 | 0.0026212 | 0.06188 | 0.058099 | -0.0022218 | -0.0029608 | 0.00098694 | 0.0091553 | 0.0016321 | 0.068438 | 0.060925 | -0.0052638 | 0.0079425 | -0.0028818 | 0.050354 | 63.0249 | -59.2529 | 63.2446 | -59.0103 | -59.3948 | -59.3811 | 0.13275 | 63.0066 | -59.2163 | 63.2126 | -59.1568 | -59.285 | -59.2209 | -0.068665 | -0.11902 | 0.10071 | 0.17395 | -0.19684 | -0.21057 | -0.12817 | -0.14191 | -0.032044 | -0.13733 | 0.068664 | 0.027466 | -0.036621 | -0.10071 | -0.004577 | -0.068664 | 0.24262 | 122.4976 | 0.05951 | 122.4289 | 122.2778 | 122.2229 | 122.2092 | 122.1909 | -122.3969 | -122.3602 | 122.4289 | 122.3969 | 59.2346 | 59.317
471.3125 | 122.5204 | -59.2484 | 63.1119 | -0.14977 | 0.0006986 | 0.062094 | 0.064081 | 0.0016236 | -0.0021064 | 0.0024823 | -0.094604 | 0.0012047 | 0.066089 | 0.059216 | -0.0054774 | 0.0081561 | -0.0009592 | 0.13275 | 63.0386 | -59.3262 | 63.0844 | -59.1934 | -59.5642 | -59.5459 | -0.15564 | 63.0157 | -59.2484 | 63.089 | -59.3628 | -59.491 | -59.3582 | -0.07782 | -0.073242 | -0.027465 | 0.054932 | -0.29755 | -0.31586 | -0.21973 | -0.23804 | 0 | -0.09613 | -0.022888 | -0.11444 | -0.10986 | -0.24262 | -0.10986 | -0.24262 | 0.13275 | 122.4106 | -0.11444 | 122.3373 | 122.3648 | 122.2641 | 122.287 | 122.2641 | -122.438 | -122.3602 | 122.3328 | 122.3373 | 59.3811 | 59.0927
472.3125 | 122.525 | -59.23 | 63.1668 | -0.012436 | 0.0019802 | 0.062308 | 0.057245 | -0.0032898 | -0.0053108 | -0.0013629 | 0.0061035 | 0.0024865 | 0.068438 | 0.056866 | -0.0029138 | 0.0096515 | -0.0020272 | -0.004578 | 63.0386 | -59.3033 | 63.1393 | -59.1339 | -59.5093 | -59.4864 | -0.009155 | 63.0341 | -59.2255 | 62.9837 | -59.2392 | -59.3628 | -59.2941 | -0.073242 | -0.12817 | -0.027466 | 0.096131 | -0.25635 | -0.27923 | -0.18311 | -0.20599 | 0.004578 | -0.13275 | -0.1831 | -0.009155 | -0.064086 | -0.13275 | -0.068664 | -0.13733 | 0.16937 | 122.4426 | -0.013733 | 122.2092 | 122.3419 | 122.2595 | 122.2687 | 122.2641 | -122.4701 | -122.3923 | 122.3694 | 122.2137 | 59.2255 | 59.2209
473.3125 | 122.6624 | -59.2072 | 63.1348 | 0.15541 | -0.000156 | 0.063162 | 0.056817 | -0.0047852 | -0.00061096 | 0.0024823 | 0.030518 | -0.00050405 | 0.065234 | 0.05708 | -0.0052638 | 0.0094379 | -0.0013864 | 0.10986 | 63.0798 | -59.2575 | 63.2492 | -58.9783 | -59.4131 | -59.3765 | 0.12817 | 62.9883 | -59.1934 | 63.208 | -59.1339 | -59.2621 | -59.1888 | -0.050354 | -0.054932 | 0.11444 | 0.22888 | -0.16937 | -0.20599 | -0.11902 | -0.15564 | 0.013733 | -0.14648 | 0.073242 | 0.073242 | 0.01831 | -0.054932 | 0.004577 | -0.068665 | 0.27924 | 122.5067 | 0.059509 | 122.4014 | 122.3373 | 122.1817 | 122.287 | 122.1954 | -122.3923 | -122.3282 | 122.4564 | 122.4152 | 59.317 | 59.3353
474.3125 | 122.612 | -59.1934 | 63.1256 | -0.0048066 | 0.001553 | 0.063162 | 0.058954 | 0.0014098 | -0.0016792 | -0.0015765 | 0.039673 | 0.0020593 | 0.066089 | 0.057294 | -0.0054774 | 0.0073015 | -0.0028818 | 0.054932 | 63.0066 | -59.2575 | 63.2355 | -59.0149 | -59.4086 | -59.3811 | 0.10071 | 62.9974 | -59.1934 | 63.1989 | -59.1797 | -59.2941 | -59.23 | -0.064087 | -0.11902 | 0.10986 | 0.17853 | -0.18768 | -0.21515 | -0.1236 | -0.15106 | 0 | -0.12817 | 0.073243 | 0.013733 | -0.036622 | -0.10071 | -0.036622 | -0.10071 | 0.24261 | 122.493 | 0.013733 | 122.3923 | 122.2641 | 122.1909 | 122.2 | 122.1909 | -122.3831 | -122.319 | 122.4289 | 122.3923 | 59.2484 | 59.2941
475.3125 | 122.6669 | -59.2026 | 63.1119 | -0.027695 | 0.0011258 | 0.064657 | 0.057886 | 0.00098262 | -0.0010382 | -8.1264e-05 | 0.23193 | 0.00077755 | 0.070361 | 0.060712 | -0.0044092 | 0.0058063 | -0.0003182 | 0.050354 | 63.0112 | -59.2575 | 63.2721 | -58.9645 | -59.3582 | -59.3445 | 0.041199 | 63.0066 | -59.198 | 63.2172 | -59.1614 | -59.3079 | -59.2392 | -0.054931 | -0.10071 | 0.16022 | 0.23804 | -0.14191 | -0.15564 | -0.086975 | -0.10071 | 0.004578 | -0.10529 | 0.10529 | 0.041199 | -0.036621 | -0.10529 | -0.041199 | -0.10986 | 0.29297 | 122.5296 | 0.036621 | 122.4152 | 122.2687 | 122.2046 | 122.2137 | 122.2092 | -122.3694 | -122.3099 | 122.4747 | 122.4197 | 59.2529 | 59.2438
476.3125 | 122.5708 | -59.198 | 63.1393 | -0.012436 | 0.002194 | 0.064657 | 0.062158 | -0.00029898 | -0.0027472 | 0.00013254 | -0.054932 | 0.00035035 | 0.064807 | 0.06413 | -0.0071864 | 0.0068743 | -0.0011728 | 0.022888 | 63.0524 | -59.3124 | 63.1805 | -59.111 | -59.4818 | -59.4589 | 0.027466 | 63.0249 | -59.2438 | 63.1577 | -59.2255 | -59.3765 | -59.2667 | -0.11444 | -0.086975 | 0.041199 | 0.086975 | -0.26093 | -0.28381 | -0.14648 | -0.16937 | -0.045776 | -0.11444 | 0.018311 | -0.027466 | -0.068665 | -0.17853 | -0.022889 | -0.13275 | 0.20142 | 122.493 | 0.01831 | 122.4014 | 122.3648 | 122.2687 | 122.2504 | 122.2229 | -122.4518 | -122.3831 | 122.3785 | 122.3557 | 59.2209 | 59.2255
477.3125 | 122.525 | -59.23 | 63.1531 | -0.020065 | 0.003262 | 0.063589 | 0.061303 | 0.00076902 | -0.0018928 | -0.0020039 | -0.039673 | 0.0024865 | 0.06737 | 0.062634 | -0.002273 | 0.0092241 | -0.0028818 | 0.004578 | 63.0478 | -59.2758 | 63.1119 | -59.1339 | -59.4955 | -59.4955 | -0.018311 | 63.0386 | -59.2209 | 63.1119 | -59.2667 | -59.4086 | -59.3353 | -0.045776 | -0.10529 | -0.041199 | 0.096131 | -0.2655 | -0.2655 | -0.21973 | -0.21973 | 0.009156 | -0.11444 | -0.041199 | -0.036621 | -0.10529 | -0.17853 | -0.11444 | -0.18768 | 0.14191 | 122.3877 | -0.045777 | 122.3328 | 122.3236 | 122.2595 | 122.2778 | 122.2687 | -122.4289 | -122.374 | 122.3419 | 122.3419 | 59.2346 | 59.2117
478.3125 | 122.6669 | -59.1934 | 63.1256 | -0.0048066 | -0.000156 | 0.061239 | 0.057886 | -0.0011536 | -0.0012518 | -0.0034991 | 0.039673 | 0.0020593 | 0.066729 | 0.056012 | -0.0048364 | 0.0075153 | -0.0054452 | 0.2243 | 63.0753 | -59.2438 | 63.2309 | -58.9691 | -59.3994 | -59.3628 | 0.13275 | 62.9837 | -59.1797 | 63.2309 | -59.1476 | -59.2575 | -59.198 | -0.050354 | -0.050354 | 0.10529 | 0.2243 | -0.16937 | -0.20599 | -0.11902 | -0.15564 | 0.013733 | -0.14191 | 0.10529 | 0.045776 | -0.004578 | -0.064087 | -0.018311 | -0.07782 | 0.27466 | 122.4747 | 0.032043 | 122.4106 | 122.319 | 122.1634 | 122.2687 | 122.1771 | -122.3694 | -122.3053 | 122.4243 | 122.4243 | 59.4177 | 59.3262
479.3125 | 122.6303 | -59.2072 | 63.1622 | -0.020065 | 0.0034756 | 0.064016 | 0.058526 | -8.538e-05 | -0.0053108 | -0.00029486 | 0.015259 | 0.0024865 | 0.067157 | 0.06178 | -0.0044092 | 0.0079425 | -0.0035226 | 0.086975 | 63.0066 | -59.285 | 63.2309 | -59.0195 | -59.3994 | -59.3811 | 0.1236 | 63.002 | -59.1934 | 63.1989 | -59.166 | -59.2987 | -59.2255 | -0.07782 | -0.15564 | 0.068665 | 0.18768 | -0.17395 | -0.19226 | -0.096131 | -0.11444 | 0.013733 | -0.16022 | 0.036622 | 0.041198 | -0.018311 | -0.091553 | -0.032044 | -0.10529 | 0.2655 | 122.5159 | 0.027465 | 122.3923 | 122.2916 | 122.1954 | 122.2137 | 122.2092 | -122.4472 | -122.3557 | 122.438 | 122.406 | 59.2941 | 59.3307
480.3125 | 122.6212 | -59.1843 | 63.1393 | -0.0048066 | 0.0026212 | 0.062308 | 0.060235 | -0.0011536 | -0.0027472 | 0.00034614 | 0.015259 | 0.0012047 | 0.068011 | 0.059003 | -0.0044092 | 0.0058063 | -0.0020272 | 0.073242 | 63.0066 | -59.2529 | 63.2401 | -59.0012 | -59.3811 | -59.3674 | 0.1236 | 62.9929 | -59.1888 | 63.1989 | -59.166 | -59.2941 | -59.2529 | -0.068665 | -0.13275 | 0.10071 | 0.18311 | -0.18311 | -0.19684 | -0.11444 | -0.12817 | -0.004578 | -0.14648 | 0.05951 | 0.01831 | -0.068665 | -0.10986 | -0.064087 | -0.10529 | 0.25177 | 122.493 | 0.022888 | 122.3877 | 122.2595 | 122.1817 | 122.1909 | 122.1771 | -122.3923 | -122.3282 | 122.4243 | 122.3831 | 59.2575 | 59.3079
481.3125 | 122.6807 | -59.1888 | 63.1165 | -0.020065 | 0.0043302 | 0.062948 | 0.060449 | -0.002008 | 2.9842e-05 | -0.00050846 | 0.057983 | 0.00099115 | 0.068225 | 0.060712 | -0.0044092 | 0.0064471 | -0.0045908 | 0.041199 | 63.0249 | -59.2804 | 63.2675 | -58.9737 | -59.3536 | -59.3399 | 0.32959 | 63.0203 | -59.1385 | 63.2355 | -59.198 | -59.2026 | -59.1797 | -0.091553 | -0.091553 | 0.15106 | 0.21515 | -0.15106 | -0.16479 | -0.059509 | -0.073242 | 0.050354 | -0.09613 | 0.11902 | -0.009155 | 0.009156 | -0.013733 | -0.041198 | -0.064087 | 0.3067 | 122.5479 | -0.059509 | 122.374 | 122.3053 | 122.1588 | 122.2137 | 122.2092 | -122.3969 | -122.2549 | 122.4564 | 122.4243 | 59.23 | 59.5184
482.3125 | 122.6669 | -59.2209 | 63.0844 | -0.042954 | 0.0028348 | 0.065298 | 0.058954 | 0.0035462 | -0.00039736 | -0.0028583 | 0.027466 | 0.0022729 | 0.066516 | 0.053021 | -0.0052638 | 0.0066607 | -0.0045908 | -0.004578 | 63.0203 | -59.2987 | 63.176 | -59.0652 | -59.4315 | -59.3948 | 0.036621 | 62.9883 | -59.2163 | 63.1897 | -59.1751 | -59.2941 | -59.2117 | -0.07782 | -0.064087 | 0.091552 | 0.15564 | -0.17395 | -0.21057 | -0.09613 | -0.13275 | 0.004577 | -0.096131 | 0.10529 | 0.045776 | 0.009155 | -0.073242 | 0.004578 | -0.077819 | 0.23346 | 122.4747 | 0.041199 | 122.406 | 122.319 | 122.2046 | 122.2412 | 122.2092 | -122.3831 | -122.3007 | 122.3969 | 122.4106 | 59.2163 | 59.2575
483.3125 | 122.6486 | -59.2026 | 63.1348 | -0.027695 | 0.0024076 | 0.063376 | 0.060876 | 0.0018372 | -0.0012518 | 0.00077334 | 0.021362 | 0.0012047 | 0.068438 | 0.062207 | -0.0054774 | 0.0070879 | -0.0039498 | 0.050354 | 62.9745 | -59.2896 | 63.2767 | -58.992 | -59.3811 | -59.3674 | 0.13275 | 63.002 | -59.1888 | 63.2126 | -59.1431 | -59.2529 | -59.2117 | -0.086975 | -0.16022 | 0.14191 | 0.21057 | -0.16479 | -0.17853 | -0.07782 | -0.091553 | 0.013733 | -0.13275 | 0.077819 | 0.05951 | -0.009155 | -0.050354 | -0.022888 | -0.064087 | 0.29755 | 122.5662 | 0.045777 | 122.4014 | 122.2641 | 122.1909 | 122.1771 | 122.2046 | -122.4243 | -122.3236 | 122.4792 | 122.4152 | 59.2529 | 59.3353
484.3125 | 122.6578 | -59.1797 | 63.1165 | -0.08873 | 0.0019802 | 0.059744 | 0.058099 | 0.00055542 | -0.0018928 | -0.0026447 | 0.027466 | 0.00056395 | 0.065448 | 0.065839 | -0.0054774 | 0.0079425 | -0.0016 | 0.34332 | 63.0981 | -59.2438 | 63.2217 | -58.9645 | -59.3445 | -59.3719 | 0.14648 | 62.9883 | -59.198 | 63.2172 | -59.1476 | -59.2667 | -59.2117 | -0.064087 | -0.01831 | 0.10529 | 0.21515 | -0.19226 | -0.16479 | -0.12817 | -0.10071 | -0.018311 | -0.12817 | 0.10071 | 0.032043 | -0.032044 | -0.086976 | -0.013733 | -0.068665 | 0.27923 | 122.4655 | 0.050354 | 122.4152 | 122.3419 | 122.1863 | 122.2778 | 122.168 | -122.3602 | -122.3145 | 122.4014 | 122.3969 | 59.523 | 59.3262
485.3125 | 122.6715 | -59.198 | 63.1027 | -0.020065 | 0.0041166 | 0.062308 | 0.057031 | -0.0062806 | -0.0044562 | -0.0013629 | -8.6e-08 | 0.0014185 | 0.06737 | 0.060498 | -0.0052638 | 0.0066607 | -0.0043772 | 0.059509 | 63.0157 | -59.285 | 63.3179 | -59.2941 | -59.6191 | -59.3948 | 0.12817 | 62.9837 | -59.2209 | 63.2172 | -59.1431 | -59.2117 | -59.1888 | -0.086975 | -0.086975 | 0.21515 | -0.09613 | -0.19684 | -0.42114 | -0.10986 | -0.33417 | -0.022888 | -0.11902 | 0.11444 | 0.054932 | 0.009155 | -0.013733 | 0.032043 | 0.009155 | -0.009155 | 122.6028 | 0.07782 | 122.438 | 122.3007 | 122.2046 | 122.2137 | 122.1817 | -122.3877 | -122.3236 | 122.5159 | 122.4152 | 59.2575 | 59.3262
486.3125 | 122.6578 | -59.198 | 63.1439 | -0.035324 | 0.0024076 | 0.063162 | 0.060663 | 0.00034182 | -0.0010382 | -0.00072206 | -8.6e-08 | 0.0014185 | 0.068866 | 0.065625 | -0.0063318 | 0.0081561 | -0.0026682 | 0.054932 | 63.002 | -59.2758 | 63.2446 | -59.0149 | -59.3719 | -59.3674 | 0.11444 | 62.97 | -59.1934 | 63.208 | -59.1568 | -59.2667 | -59.2209 | -0.07782 | -0.14191 | 0.10071 | 0.1831 | -0.16937 | -0.17395 | -0.091553 | -0.09613 | 0.004578 | -0.17395 | 0.064087 | 0.041199 | -0.022888 | -0.068665 | -0.027466 | -0.073243 | 0.26093 | 122.5204 | 0.036621 | 122.4014 | 122.2778 | 122.1634 | 122.2 | 122.168 | -122.4197 | -122.3373 | 122.4426 | 122.406 | 59.2529 | 59.3124
487.3125 | 122.5616 | -59.2438 | 63.1485 | -0.027695 | 0.0011258 | 0.06188 | 0.061944 | -0.00051278 | -0.0014654 | -0.0013629 | -0.061035 | 0.0012047 | 0.06737 | 0.061352 | -0.0041956 | 0.0092241 | -0.0035226 | -0.004578 | 63.0707 | -59.3262 | 63.1256 | -59.1476 | -59.5139 | -59.4955 | -0.036621 | 63.0569 | -59.2392 | 63.1256 | -59.2804 | -59.4086 | -59.3308 | -0.082398 | -0.07782 | -0.022889 | 0.09613 | -0.25177 | -0.27008 | -0.16937 | -0.18768 | 0.004577 | -0.091553 | -0.022889 | -0.036622 | -0.086976 | -0.16479 | -0.091553 | -0.16937 | 0.17853 | 122.4518 | -0.041199 | 122.3648 | 122.3969 | 122.2961 | 122.3145 | 122.3007 | -122.4747 | -122.3877 | 122.3694 | 122.3694 | 59.2392 | 59.2072
488.3125 | 122.6303 | -59.2072 | 63.1302 | -0.027695 | 0.001553 | 0.060812 | 0.057886 | 0.00055542 | -0.0014654 | 0.0014141 | 0.0091553 | 0.0022729 | 0.06502 | 0.05943 | -0.0048364 | 0.0060199 | -0.0003182 | -0.022888 | 63.002 | -59.2896 | 63.1851 | -59.0561 | -59.4406 | -59.4177 | 0.036621 | 62.9929 | -59.1888 | 63.1943 | -59.1888 | -59.3079 | -59.2346 | -0.082398 | -0.12817 | 0.054932 | 0.15106 | -0.21057 | -0.23346 | -0.12817 | -0.15106 | 0.01831 | -0.13733 | 0.064087 | 0.01831 | -0.027466 | -0.10071 | -0.045776 | -0.11902 | 0.23346 | 122.4747 | 0 | 122.3831 | 122.2916 | 122.1817 | 122.2092 | 122.2 | -122.4197 | -122.319 | 122.3923 | 122.4014 | 59.1843 | 59.2438
489.3125 | 122.6624 | -59.1934 | 63.1256 | -0.020065 | 0.0041166 | 0.063803 | 0.06109 | -8.538e-05 | -0.003388 | -8.1264e-05 | 0.018311 | 0.0014185 | 0.067798 | 0.060284 | -0.0048364 | 0.0087969 | -0.003309 | 0.018311 | 63.0203 | -59.2712 | 63.2401 | -58.9966 | -59.3857 | -59.3674 | 0.13733 | 62.9745 | -59.1934 | 63.2492 | -59.1339 | -59.2484 | -59.1888 | -0.07782 | -0.10529 | 0.11444 | 0.19684 | -0.17395 | -0.19226 | -0.096131 | -0.11444 | 0 | -0.15106 | 0.1236 | 0.059509 | 0.004577 | -0.054932 | 0.004577 | -0.054932 | 0.27466 | 122.5113 | 0.059509 | 122.4426 | 122.2916 | 122.168 | 122.2137 | 122.168 | -122.3969 | -122.319 | 122.4335 | 122.4426 | 59.2117 | 59.3307
490.3125 | 122.6532 | -59.1751 | 63.0981 | -0.050583 | 0.003262 | 0.062735 | 0.057245 | 0.0014098 | -0.00018376 | -0.00072206 | -0.021362 | 0.0016321 | 0.066089 | 0.063061 | -0.0059046 | 0.0092241 | -0.0022408 | 0.073242 | 63.0157 | -59.2758 | 63.0524 | -59.0607 | -59.3308 | -59.3765 | 0.13275 | 62.9791 | -59.1888 | 63.2126 | -59.1248 | -59.2529 | -59.2209 | -0.10071 | -0.082398 | -0.045777 | 0.11444 | -0.20142 | -0.15564 | -0.10071 | -0.054932 | -0.013733 | -0.11902 | 0.11444 | 0.050354 | -0.045776 | -0.07782 | -0.032043 | -0.064087 | 0.21515 | 122.3282 | 0.064087 | 122.4014 | 122.2916 | 122.168 | 122.1909 | 122.1542 | -122.374 | -122.287 | 122.2275 | 122.3877 | 59.2484 | 59.3079
491.3125 | 122.6166 | -59.198 | 63.1531 | 0.010452 | 0.0028348 | 0.06423 | 0.058526 | -0.0017944 | -0.005097 | 0.00013254 | 0.0061035 | 0.0022729 | 0.065661 | 0.061993 | -0.0044092 | 0.0068743 | -0.0039498 | 0.059509 | 63.0112 | -59.2712 | 63.2492 | -59.0149 | -59.3948 | -59.3811 | 0.10986 | 62.9929 | -59.1934 | 63.2126 | -59.1751 | -59.285 | -59.2255 | -0.073242 | -0.14191 | 0.096131 | 0.1831 | -0.18311 | -0.19684 | -0.10986 | -0.1236 | 0.004578 | -0.16022 | 0.059509 | 0.022888 | -0.027466 | -0.086975 | -0.032044 | -0.091553 | 0.25635 | 122.5204 | 0.01831 | 122.406 | 122.2824 | 122.1863 | 122.2092 | 122.1909 | -122.4243 | -122.3465 | 122.4472 | 122.4106 | 59.2575 | 59.3079
492.3125 | 122.5754 | -59.2117 | 63.1119 | -0.027695 | 0.0030484 | 0.065298 | 0.062799 | 0.00012822 | -0.0014654 | -0.00050846 | -0.097656 | 0.0022729 | 0.066943 | 0.061566 | -0.002273 | 0.0090105 | 0.0005362 | 0.013733 | 63.0615 | -59.3033 | 63.176 | -59.111 | -59.4681 | -59.4681 | 0.022888 | 63.0249 | -59.2392 | 63.1668 | -59.2255 | -59.3857 | -59.285 | -0.091553 | -0.050354 | 0.064087 | 0.10071 | -0.25635 | -0.25635 | -0.1648 | -0.1648 | -0.027466 | -0.086975 | 0.054932 | -0.013733 | -0.073242 | -0.17395 | -0.045776 | -0.14648 | 0.19226 | 122.4792 | 0.013733 | 122.406 | 122.3648 | 122.2641 | 122.2733 | 122.2366 | -122.4152 | -122.3511 | 122.3877 | 122.3785 | 59.2255 | 59.2346
493.3125 | 122.8043 | -59.1568 | 63.1714 | -0.020065 | 0.003262 | 0.065085 | 0.058313 | 0.0020508 | -0.0029608 | -0.0034991 | 0.015259 | 0.0018457 | 0.066943 | 0.071179 | -0.0027002 | 0.0064471 | -0.0011728 | 0.036621 | 63.0386 | -59.2621 | 63.2309 | -58.9828 | -59.3674 | -59.3399 | 0.14191 | 62.97 | -59.1797 | 63.2629 | -59.111 | -59.2255 | -59.0195 | -0.10529 | -0.13275 | 0.059509 | 0.17395 | -0.18311 | -0.21057 | -0.07782 | -0.10529 | -0.022888 | -0.20142 | 0.091552 | 0.045776 | 0.13733 | -0.068665 | 0.16022 | -0.045777 | 0.27924 | 122.493 | 0.068664 | 122.4426 | 122.3007 | 122.1497 | 122.1954 | 122.1268 | -122.4335 | -122.3511 | 122.3877 | 122.4197 | 59.1934 | 59.2987
494.3125 | 122.6578 | -59.1934 | 63.1073 | -0.081101 | 0.0036892 | 0.058249 | 0.060876 | -0.0030762 | -0.0038154 | -0.0032855 | 0.0061035 | 0.0014185 | 0.06438 | 0.06413 | -0.0048364 | 0.0068743 | 0.0007498 | 0.34332 | 63.0981 | -59.2255 | 63.2034 | -58.9966 | -59.3674 | -59.3857 | 0.14648 | 62.9791 | -59.1888 | 63.2172 | -59.1431 | -59.2712 | -59.2117 | -0.032044 | -0.009155 | 0.09613 | 0.19684 | -0.19226 | -0.17395 | -0.16022 | -0.14191 | 0.004577 | -0.12817 | 0.10986 | 0.050354 | -0.018311 | -0.07782 | -0.022888 | -0.082397 | 0.22888 | 122.4289 | 0.045777 | 122.406 | 122.3236 | 122.168 | 122.2916 | 122.1725 | -122.3328 | -122.2961 | 122.3969 | 122.4106 | 59.5367 | 59.3399
495.3125 | 122.6532 | -59.2209 | 63.1073 | -0.027695 | 0.0051846 | 0.064444 | 0.059808 | -0.002008 | -0.0048834 | -0.0013629 | 0.012207 | 0.00013675 | 0.064593 | 0.06712 | -0.0037684 | 0.0073015 | 0.000109 | -0.032043 | 63.0249 | -59.317 | 63.1714 | -59.079 | -59.4452 | -59.4406 | -0.018311 | 62.9745 | -59.2163 | 63.1668 | -59.2163 | -59.317 | -59.2529 | -0.096131 | -0.082398 | 0.064087 | 0.14191 | -0.21973 | -0.2243 | -0.1236 | -0.12817 | 0.004577 | -0.13275 | 0.059509 | 0.004577 | -0.032044 | -0.096131 | -0.036621 | -0.10071 | 0.23804 | 122.4884 | 0 | 122.3831 | 122.3419 | 122.1909 | 122.2458 | 122.1954 | -122.4243 | -122.3236 | 122.3923 | 122.3877 | 59.1888 | 59.2026
496.3125 | 122.6303 | -59.1705 | 63.0981 | -0.065842 | 0.002194 | 0.063376 | 0.062372 | -0.002008 | -0.0014654 | -0.0022175 | 0.0061035 | 0.00035035 | 0.066729 | 0.058362 | -0.0046228 | 0.0062335 | 0.0022452 | 0 | 63.002 | -59.2896 | 63.208 | -59.0607 | -59.4086 | -59.3994 | 0.059509 | 63.002 | -59.2163 | 63.2172 | -59.1705 | -59.3033 | -59.23 | -0.11902 | -0.096131 | 0.10986 | 0.10986 | -0.22888 | -0.23804 | -0.10986 | -0.11902 | -0.045777 | -0.096131 | 0.11902 | 0 | -0.05951 | -0.13275 | -0.013733 | -0.086975 | 0.22888 | 122.4976 | 0.045777 | 122.4335 | 122.2916 | 122.2183 | 122.1725 | 122.1725 | -122.3877 | -122.3145 | 122.3785 | 122.3877 | 59.1705 | 59.23
497.3125 | 122.493 | -59.2346 | 63.1302 | -0.073471 | 0.0034756 | 0.063162 | 0.060663 | 0.00055542 | -0.0027472 | -0.0028583 | -0.054932 | 0.0018457 | 0.064807 | 0.058575 | -0.0044092 | 0.0079425 | -0.0020272 | 0.004578 | 63.0478 | -59.2941 | 63.1348 | -59.1202 | -59.4864 | -59.4818 | -0.004578 | 63.0295 | -59.2117 | 63.1805 | -59.111 | -59.5963 | -59.4955 | -0.059509 | -0.082397 | 0.004578 | 0.11444 | -0.24719 | -0.25177 | -0.18768 | -0.19226 | 0.022888 | -0.10071 | 0.050354 | 0.1236 | -0.26093 | -0.36163 | -0.28381 | -0.38452 | 0.17395 | 122.4289 | 0.10071 | 122.3923 | 122.3419 | 122.2412 | 122.2824 | 122.2641 | -122.4243 | -122.3419 | 122.3694 | 122.4152 | 59.2392 | 59.23
498.3125 | 122.6395 | -59.198 | 63.121 | -0.035324 | 0.001553 | 0.061667 | 0.058313 | -0.00093998 | -0.0031744 | 0.00013254 | 0.0061035 | 0.0016321 | 0.066516 | 0.060925 | -0.0035548 | 0.0060199 | -0.006727 | 0.018311 | 63.0066 | -59.2896 | 63.208 | -59.0149 | -59.3948 | -59.3719 | 0.086975 | 62.97 | -59.198 | 63.2309 | -59.1431 | -59.2667 | -59.2072 | -0.091553 | -0.11444 | 0.086975 | 0.1831 | -0.17395 | -0.19684 | -0.082397 | -0.10528 | 0 | -0.15106 | 0.10986 | 0.054932 | -0.009155 | -0.068665 | -0.009155 | -0.068665 | 0.27466 | 122.4976 | 0.054932 | 122.4289 | 122.2961 | 122.168 | 122.2046 | 122.168 | -122.4106 | -122.319 | 122.406 | 122.4289 | 59.2163 | 59.285
499.3125 | 122.6669 | -59.2117 | 63.089 | -0.058212 | 0.0047574 | 0.064016 | 0.060663 | 0.0018372 | -0.0021064 | 0.00034614 | -0.01831 | -7.6854e-05 | 0.062884 | 0.055157 | -0.0048364 | 0.010506 | -0.000532 | 0.045776 | 63.0112 | -59.2529 | 63.2538 | -58.9737 | -59.3536 | -59.3399 | 0.16479 | 62.9837 | -59.1705 | 63.0569 | -59.0973 | -59.2621 | -59.198 | -0.041199 | -0.07782 | 0.1648 | 0.23804 | -0.12817 | -0.14191 | -0.086975 | -0.10071 | 0.041199 | -0.10528 | -0.032043 | 0.11444 | 0.013733 | -0.050354 | -0.027466 | -0.091553 | 0.27924 | 122.5067 | 0.073242 | 122.2275 | 122.2641 | 122.1542 | 122.2229 | 122.1954 | -122.3419 | -122.2595 | 122.4655 | 122.2687 | 59.2575 | 59.3765
500.3125 | 122.6349 | -59.198 | 63.0981 | -0.035324 | 0.0024076 | 0.06423 | 0.06344 | 0.0054688 | -0.006806 | -0.0011493 | -0.0061035 | 0.0018457 | 0.066089 | 0.057935 | -0.0048364 | 0.0070879 | -0.0020272 | -0.013733 | 63.002 | -59.2896 | 63.1805 | -59.0698 | -59.4543 | -59.436 | 0.027466 | 62.9471 | -59.2209 | 63.1897 | -59.1843 | -59.3033 | -59.2255 | -0.091553 | -0.096131 | 0.082397 | 0.12817 | -0.23804 | -0.25635 | -0.14648 | -0.16479 | -0.022888 | -0.15106 | 0.091552 | 0.013733 | -0.027466 | -0.10529 | -0.004578 | -0.082398 | 0.21973 | 122.4701 | 0.036621 | 122.4106 | 122.2916 | 122.168 | 122.2 | 122.1451 | -122.3877 | -122.319 | 122.3785 | 122.3877 | 59.1843 | 59.2255
501.3125 | 122.6624 | -59.1888 | 63.121 | -0.012436 | 0.0030484 | 0.063803 | 0.059167 | -0.0035034 | -0.0016792 | 0.00034614 | -0.0061035 | 0.0018457 | 0.068225 | 0.061566 | -0.0046228 | 0.0087969 | -0.000532 | 0.004578 | 63.0157 | -59.2804 | 63.2126 | -59.0332 | -59.4177 | -59.3948 | 0.068665 | 62.9929 | -59.2163 | 63.2172 | -59.1522 | -59.2621 | -59.2163 | -0.091553 | -0.10529 | 0.091552 | 0.15564 | -0.20599 | -0.22888 | -0.11444 | -0.13733 | -0.027466 | -0.12817 | 0.09613 | 0.036621 | -0.027466 | -0.073242 | 0 | -0.045776 | 0.24719 | 122.493 | 0.064087 | 122.4335 | 122.2961 | 122.2092 | 122.2046 | 122.1817 | -122.4014 | -122.3373 | 122.4014 | 122.406 | 59.1934 | 59.2575
502.3125 | 122.6212 | -59.2163 | 63.089 | -0.042954 | 0.002194 | 0.065085 | 0.060449 | -0.0032898 | 2.9842e-05 | 0.0018413 | -0.048828 | 0.0016321 | 0.065448 | 0.061352 | -0.0052638 | 0.0073015 | -0.0003182 | -0.050354 | 62.9745 | -59.285 | 63.1531 | -59.0881 | -59.4818 | -59.4498 | -0.054932 | 62.9654 | -59.2255 | 63.1577 | -59.2392 | -59.3353 | -59.2712 | -0.068664 | -0.11444 | 0.064087 | 0.12817 | -0.23346 | -0.2655 | -0.16479 | -0.19684 | -0.009155 | -0.1236 | 0.068665 | -0.022888 | -0.054931 | -0.11902 | -0.045776 | -0.10986 | 0.19684 | 122.438 | -0.013733 | 122.3831 | 122.2595 | 122.1909 | 122.1909 | 122.1817 | -122.374 | -122.3145 | 122.3694 | 122.374 | 59.166 | 59.1614
503.3125 | 122.58 | -59.2438 | 63.0707 | -0.050583 | 0.002194 | 0.065512 | 0.061944 | -0.00051278 | -0.0018928 | -0.0022175 | -0.015259 | -0.00029045 | 0.066516 | 0.061566 | -0.0048364 | 0.0070879 | -0.000532 | -0.045776 | 62.9791 | -59.2987 | 63.1805 | -59.0561 | -59.4864 | -59.4452 | -0.027466 | 62.9654 | -59.2392 | 63.1668 | -59.2575 | -59.3536 | -59.2712 | -0.054932 | -0.091553 | 0.10986 | 0.18768 | -0.20142 | -0.24262 | -0.14648 | -0.18768 | 0.004577 | -0.10529 | 0.09613 | -0.013733 | -0.027466 | -0.10986 | -0.032043 | -0.11444 | 0.24262 | 122.4792 | -0.01831 | 122.406 | 122.2778 | 122.2046 | 122.2229 | 122.2092 | -122.3694 | -122.3099 | 122.4243 | 122.4106 | 59.198 | 59.2163
504.3125 | 122.6212 | -59.2392 | 63.1165 | -0.042954 | 0.0017666 | 0.065725 | 0.060876 | -0.0035034 | -0.0014654 | -0.0015765 | 0.015259 | 0.00056395 | 0.064807 | 0.062848 | -0.005691 | 0.0073015 | -0.003309 | -0.041199 | 63.0157 | -59.2987 | 63.1485 | -59.0927 | -59.4681 | -59.4315 | -0.013733 | 62.9745 | -59.2117 | 63.1805 | -59.2209 | -59.3262 | -59.2575 | -0.059509 | -0.10071 | 0.032044 | 0.14648 | -0.19226 | -0.22888 | -0.13275 | -0.16937 | 0.027466 | -0.14191 | 0.064087 | 0.018311 | -0.01831 | -0.086975 | -0.045776 | -0.11444 | 0.20599 | 122.4472 | -0.009155 | 122.3923 | 122.3145 | 122.1863 | 122.2549 | 122.2137 | -122.4152 | -122.3282 | 122.3877 | 122.4197 | 59.198 | 59.2255
505.3125 | 122.612 | -59.2255 | 63.0981 | -0.050583 | 0.004971 | 0.059958 | 0.059808 | -0.0011536 | -0.00232 | -8.1264e-05 | -0.0091553 | 0.0016321 | 0.066302 | 0.063061 | -0.0041956 | 0.0075153 | -0.0016 | 0.15106 | 63.0615 | -59.2712 | 63.1439 | -59.0973 | -59.4772 | -59.4727 | -0.050354 | 62.9929 | -59.2346 | 63.1622 | -59.2438 | -59.3399 | -59.2804 | -0.045776 | -0.036622 | 0.045776 | 0.12817 | -0.24719 | -0.25177 | -0.20142 | -0.20599 | -0.009155 | -0.10529 | 0.064086 | -0.01831 | -0.054932 | -0.11444 | -0.045777 | -0.10529 | 0.17395 | 122.4152 | -0.009155 | 122.3969 | 122.3328 | 122.2275 | 122.287 | 122.2183 | -122.3694 | -122.3328 | 122.3694 | 122.3877 | 59.3765 | 59.1751
506.3125 | 122.6486 | -59.2163 | 63.0981 | -0.012436 | 5.76e-05 | 0.062735 | 0.059167 | -0.0011536 | -0.003388 | -0.0022175 | -0.027466 | -0.00029045 | 0.067157 | 0.063702 | -0.0037684 | 0.0079425 | -0.0043772 | -0.032043 | 63.0066 | -59.3308 | 63.1714 | -59.0881 | -59.4452 | -59.4406 | -0.009155 | 62.9791 | -59.2072 | 63.1897 | -59.2117 | -59.3079 | -59.2392 | -0.11444 | -0.091553 | 0.073242 | 0.12817 | -0.2243 | -0.22888 | -0.10986 | -0.11444 | 0.009156 | -0.11902 | 0.091552 | 0.004578 | -0.022888 | -0.091552 | -0.032044 | -0.10071 | 0.24262 | 122.5021 | -0.004578 | 122.3969 | 122.3373 | 122.1863 | 122.2229 | 122.1954 | -122.4289 | -122.3053 | 122.3877 | 122.406 | 59.1843 | 59.2072
507.3125 | 122.6395 | -59.1888 | 63.0936 | -0.012436 | 0.0034756 | 0.064657 | 0.061303 | 0.00098262 | -0.004029 | 0.00034614 | -0.01831 | 0.0037683 | 0.066943 | 0.06178 | -0.00505 | 0.0070879 | -0.0054452 | -0.054932 | 62.9883 | -59.3308 | 63.1531 | -59.0927 | -59.5001 | -59.4452 | -0.050354 | 62.9883 | -59.2346 | 63.1622 | -59.2346 | -59.1614 | -59.0973 | -0.14191 | -0.10529 | 0.059509 | 0.096131 | -0.25635 | -0.31128 | -0.11444 | -0.16937 | -0.045776 | -0.10529 | 0.068664 | -0.045776 | 0.091553 | 0.027466 | 0.13733 | 0.073242 | 0.23804 | 122.4838 | 0 | 122.3969 | 122.319 | 122.2229 | 122.1771 | 122.1771 | -122.4243 | -122.3282 | 122.3419 | 122.3511 | 59.1339 | 59.1385
508.3125 | 122.5891 | -59.2026 | 63.1165 | -0.065842 | 0.0017666 | 0.060599 | 0.062799 | -0.00051278 | -0.0031744 | 0.00098694 | -0.01831 | 0.0012047 | 0.064166 | 0.062634 | -0.0052638 | 0.0079425 | -0.003309 | 0.10986 | 63.0569 | -59.2621 | 63.1439 | -59.0973 | -59.4818 | -59.4681 | -0.054932 | 62.9837 | -59.2117 | 63.1622 | -59.2392 | -59.3536 | -59.285 | -0.059509 | -0.059509 | 0.027466 | 0.10529 | -0.2655 | -0.27924 | -0.20599 | -0.21973 | -0.009155 | -0.13275 | 0.045776 | -0.036621 | -0.082397 | -0.15106 | -0.073242 | -0.14191 | 0.16479 | 122.406 | -0.027466 | 122.374 | 122.319 | 122.1954 | 122.2595 | 122.1863 | -122.3785 | -122.3282 | 122.3465 | 122.3648 | 59.3124 | 59.1476
509.3125 | 122.5845 | -59.2392 | 63.089 | -0.065842 | 0.0045438 | 0.064657 | 0.061303 | 0.0014098 | -0.0021064 | 0.00034614 | -0.073242 | 0.00056395 | 0.06502 | 0.06413 | -0.0054774 | 0.0081561 | -0.0022408 | -0.036621 | 62.9745 | -59.3124 | 63.1714 | -59.0744 | -59.491 | -59.436 | -0.009155 | 62.9379 | -59.2438 | 63.1668 | -59.2392 | -59.3536 | -59.2621 | -0.073242 | -0.11444 | 0.082398 | 0.16479 | -0.19684 | -0.25177 | -0.1236 | -0.17853 | -0.004577 | -0.15106 | 0.07782 | 0 | -0.022888 | -0.11444 | -0.018311 | -0.10986 | 0.23804 | 122.4838 | 0.004577 | 122.4106 | 122.287 | 122.1817 | 122.2137 | 122.1771 | -122.4014 | -122.3328 | 122.4106 | 122.406 | 59.2026 | 59.23
510.3125 | 122.6395 | -59.2163 | 63.0707 | 0.056229 | 0.0024076 | 0.064871 | 0.063867 | 0.0014098 | 0.0013116 | -8.1264e-05 | -0.045776 | 0.0039819 | 0.063952 | 0.057294 | -0.0065454 | 0.0073015 | -0.0022408 | -0.018311 | 62.9883 | -59.2896 | 63.2034 | -59.0652 | -59.4498 | -59.3948 | 0 | 62.9517 | -59.2117 | 63.208 | -59.198 | -59.3308 | -59.2255 | -0.073242 | -0.082398 | 0.13275 | 0.15106 | -0.17853 | -0.23346 | -0.10528 | -0.16022 | 0.004578 | -0.11902 | 0.13733 | 0.018311 | -0.009155 | -0.11444 | -0.013733 | -0.11902 | 0.2243 | 122.493 | 0.013733 | 122.4197 | 122.2778 | 122.1634 | 122.2046 | 122.168 | -122.3602 | -122.2824 | 122.4197 | 122.4243 | 59.198 | 59.2163
511.3125 | 122.58 | -59.2346 | 63.0844 | -0.081101 | 0.002194 | 0.063803 | 0.058954 | -8.538e-05 | -0.003388 | -0.0022175 | -0.042725 | 0.00099115 | 0.065448 | 0.058148 | -0.005691 | 0.0081561 | -0.003309 | -0.045776 | 62.9654 | -59.285 | 63.176 | -59.0973 | -59.4818 | -59.4543 | -0.054932 | 62.9745 | -59.2484 | 63.1714 | -59.2255 | -59.3399 | -59.2712 | -0.050354 | -0.11902 | 0.091552 | 0.13733 | -0.21973 | -0.24719 | -0.16937 | -0.19684 | -0.013733 | -0.10986 | 0.086975 | 0.009155 | -0.036621 | -0.10529 | -0.022888 | -0.091553 | 0.18768 | 122.4609 | 0.022888 | 122.4197 | 122.2504 | 122.2229 | 122.2 | 122.2092 | -122.3694 | -122.3328 | 122.4106 | 122.406 | 59.1888 | 59.1797
512.3125 | 122.644 | -59.1843 | 63.089 | 0.10963 | 0.0036892 | 0.067862 | 0.060663 | 0.00076902 | -0.003388 | 0.00098694 | -0.0061035 | 0.0018457 | 0.06502 | 0.058789 | -0.0054774 | 0.0085833 | -0.0026682 | -0.14648 | 63.0432 | -59.2804 | 63.2492 | -59.0012 | -59.4086 | -59.3582 | 0.13733 | 62.9929 | -59.1843 | 63.2401 | -59.1385 | -59.2484 | -59.1934 | -0.096131 | -0.045776 | 0.16022 | 0.18311 | -0.17395 | -0.2243 | -0.077819 | -0.12817 | 0 | -0.09613 | 0.15106 | 0.045776 | -0.009155 | -0.064087 | -0.009155 | -0.064087 | 0.27924 | 122.5296 | 0.045776 | 122.4243 | 122.3236 | 122.1771 | 122.2275 | 122.1771 | -122.3694 | -122.2733 | 122.4335 | 122.4243 | 59.0378 | 59.3216
513.3125 | 122.6028 | -59.2438 | 63.0844 | -0.10399 | 0.0026212 | 0.062948 | 0.06109 | -0.00072638 | -0.0012518 | 0.00013254 | -0.045776 | 0.0033411 | 0.064807 | 0.061139 | -0.0029138 | 0.0062335 | -0.0016 | -0.050354 | 62.97 | -59.3079 | 63.1897 | -59.0607 | -59.4818 | -59.4406 | -0.027466 | 62.9608 | -59.2255 | 63.176 | -59.2438 | -59.3582 | -59.2758 | -0.064087 | -0.11444 | 0.10529 | 0.18311 | -0.19684 | -0.23804 | -0.13275 | -0.17395 | 0.01831 | -0.1236 | 0.091552 | 0 | -0.032044 | -0.11444 | -0.050354 | -0.13275 | 0.24719 | 122.4976 | -0.01831 | 122.4014 | 122.2778 | 122.1863 | 122.2137 | 122.2046 | -122.3923 | -122.3099 | 122.4335 | 122.4197 | 59.1934 | 59.2163
514.3125 | 122.612 | -59.2392 | 63.0844 | -0.081101 | 0.0024076 | 0.06423 | 0.059167 | 0.0039734 | -0.0046698 | -0.0011493 | -0.015259 | 0.0018457 | 0.066516 | 0.058362 | -0.0054774 | 0.0040973 | -0.0030954 | -0.050354 | 63.0157 | -59.2987 | 63.1531 | -59.1064 | -59.4818 | -59.4406 | -0.041199 | 62.9517 | -59.2209 | 63.327 | -59.4086 | -59.4086 | -59.2758 | -0.059509 | -0.068665 | 0.068664 | 0.13275 | -0.20142 | -0.24262 | -0.14191 | -0.18311 | 0.018311 | -0.13275 | 0.24261 | -0.16937 | -0.036621 | -0.16937 | -0.054932 | -0.18768 | 0.19226 | 122.4518 | -0.18768 | 122.5479 | 122.3145 | 122.1725 | 122.2549 | 122.1909 | -122.3831 | -122.3053 | 122.3923 | 122.5662 | 59.1888 | 59.198
515.3125 | 122.6349 | -59.2346 | 63.0661 | -0.08873 | 0.0026212 | 0.06423 | 0.061944 | -0.003717 | -0.0014654 | 0.0020551 | -0.057983 | 0.0031273 | 0.066943 | 0.062634 | -0.0054774 | 0.0073015 | 0.0016044 | -0.027466 | 62.9608 | -59.3033 | 63.1943 | -59.0424 | -59.4681 | -59.4315 | 0.004578 | 62.9471 | -59.2163 | 63.1943 | -59.2072 | -59.3353 | -59.2484 | -0.068665 | -0.10529 | 0.12817 | 0.19226 | -0.19684 | -0.23346 | -0.12817 | -0.1648 | 0.01831 | -0.11902 | 0.12817 | 0.027466 | -0.013733 | -0.10071 | -0.032043 | -0.11902 | 0.26093 | 122.4976 | 0.009156 | 122.4106 | 122.2641 | 122.1634 | 122.1954 | 122.1817 | -122.3694 | -122.2824 | 122.4289 | 122.4289 | 59.2072 | 59.2392
516.3125 | 122.6578 | -59.2026 | 63.0707 | -0.058212 | 0.003262 | 0.063162 | 0.058954 | -0.00093998 | -0.0044562 | -0.0015765 | -0.033569 | 0.0024865 | 0.063952 | 0.061139 | -0.0041956 | 0.0081561 | -0.0026682 | -0.036621 | 62.97 | -59.3262 | 63.1897 | -59.0561 | -59.4543 | -59.4086 | 0.013733 | 62.9425 | -59.2117 | 63.1943 | -59.198 | -59.3262 | -59.2346 | -0.1236 | -0.10071 | 0.11902 | 0.14648 | -0.20599 | -0.25177 | -0.082397 | -0.12817 | -0.009155 | -0.12817 | 0.1236 | 0.004578 | -0.032043 | -0.1236 | -0.022888 | -0.11444 | 0.27008 | 122.5159 | 0.013733 | 122.406 | 122.2961 | 122.1542 | 122.1725 | 122.1451 | -122.3969 | -122.2824 | 122.3923 | 122.3969 | 59.166 | 59.2163
517.3125 | 122.6074 | -59.2392 | 63.1073 | -0.073471 | 0.0028348 | 0.06423 | 0.058954 | -0.0030762 | -0.0027472 | -0.00029486 | -0.021362 | 0.0014185 | 0.067584 | 0.061566 | -0.00505 | 0.0068743 | -0.0035226 | 0.050354 | 63.0341 | -59.2621 | 63.2172 | -59.024 | -59.404 | -59.3765 | 0.091553 | 63.0112 | -59.2026 | 63.1897 | -59.1843 | -59.2896 | -59.2255 | -0.022888 | -0.073242 | 0.10986 | 0.21515 | -0.13733 | -0.1648 | -0.11444 | -0.14191 | 0.036621 | -0.096131 | 0.082397 | 0.054932 | 0.013733 | -0.050354 | -0.022888 | -0.086975 | 0.23804 | 122.4792 | 0.018311 | 122.3923 | 122.2961 | 122.2137 | 122.2733 | 122.2504 | -122.3694 | -122.3099 | 122.4564 | 122.4289 | 59.2896 | 59.3307
518.3125 | 122.6166 | -59.2163 | 63.0569 | -0.058212 | 0.0024076 | 0.062521 | 0.063226 | -0.00072638 | 2.9842e-05 | -0.0013629 | -0.061035 | 0.00013675 | 0.066943 | 0.060498 | -0.00505 | 0.0083697 | 0.0024588 | -0.045776 | 62.9837 | -59.2804 | 63.2034 | -59.0561 | -59.436 | -59.404 | 0.004578 | 62.9333 | -59.2392 | 63.208 | -59.1934 | -59.3399 | -59.2346 | -0.064087 | -0.073242 | 0.14648 | 0.16022 | -0.18768 | -0.21973 | -0.1236 | -0.15564 | -0.022888 | -0.1236 | 0.15106 | 0.022889 | -0.01831 | -0.1236 | 0.004578 | -0.10071 | 0.22431 | 122.4838 | 0.045777 | 122.4472 | 122.2641 | 122.1725 | 122.2 | 122.1497 | -122.3373 | -122.2961 | 122.4197 | 122.4243 | 59.1705 | 59.2209
519.3125 | 122.6074 | -59.2392 | 63.0844 | -0.096359 | 0.0017666 | 0.063162 | 0.062372 | -0.0017944 | -0.00232 | -0.0030719 | -0.024414 | 0.0016321 | 0.065234 | 0.061352 | -0.002273 | 0.0055927 | -0.0007456 | -0.07782 | 62.9883 | -59.317 | 63.1622 | -59.1019 | -59.4772 | -59.4406 | -0.059509 | 62.9654 | -59.2392 | 63.3362 | -59.4177 | -59.4131 | -59.2667 | -0.07782 | -0.096131 | 0.077819 | 0.13733 | -0.20142 | -0.23804 | -0.1236 | -0.16022 | 0 | -0.11902 | 0.25177 | -0.17853 | -0.027466 | -0.17395 | -0.027466 | -0.17395 | 0.21515 | 122.4792 | -0.17853 | 122.5754 | 122.3053 | 122.2046 | 122.2275 | 122.2046 | -122.4014 | -122.3236 | 122.4014 | 122.5754 | 59.1614 | 59.1797
520.3125 | 122.58 | -59.2072 | 63.1348 | -0.065842 | 0.0002714 | 0.064657 | 0.060449 | -0.00072638 | -0.0016792 | -0.0011493 | -0.024414 | 0.0027001 | 0.065234 | 0.053448 | -0.0071864 | 0.0079425 | -0.0001046 | -0.054932 | 63.002 | -59.3216 | 63.1485 | -59.1019 | -59.4864 | -59.4543 | -0.054932 | 62.9562 | -59.23 | 63.1622 | -59.23 | -59.3353 | -59.2758 | -0.11444 | -0.13275 | 0.013733 | 0.10528 | -0.24719 | -0.27924 | -0.13275 | -0.1648 | -0.022889 | -0.17853 | 0.027465 | -0.022889 | -0.068665 | -0.12817 | -0.045776 | -0.10529 | 0.21973 | 122.4701 | 0 | 122.3923 | 122.3236 | 122.1863 | 122.2092 | 122.1634 | -122.4564 | -122.3648 | 122.3557 | 122.3694 | 59.1522 | 59.1522
521.3125 | 122.5983 | -59.2026 | 63.0981 | -0.11162 | 0.0036892 | 0.06188 | 0.059381 | 0.0035462 | -0.0016792 | 0.00013254 | -0.036621 | 0.00035035 | 0.066089 | 0.057935 | -0.0037684 | 0.0079425 | 0.0005362 | -0.050354 | 62.9745 | -59.3033 | 63.1531 | -59.0973 | -59.4864 | -59.4498 | -0.073242 | 62.97 | -59.2117 | 63.1851 | -59.2255 | -59.3445 | -59.2712 | -0.10071 | -0.1236 | 0.054931 | 0.10529 | -0.24719 | -0.28381 | -0.14648 | -0.18311 | -0.009155 | -0.12817 | 0.086975 | -0.022888 | -0.068664 | -0.14191 | -0.059509 | -0.13275 | 0.20599 | 122.4564 | -0.013733 | 122.3969 | 122.2778 | 122.1817 | 122.1771 | 122.1725 | -122.4014 | -122.3099 | 122.3557 | 122.3877 | 59.1522 | 59.1293
522.3125 | 122.5937 | -59.1934 | 63.089 | -0.11162 | 0.0013394 | 0.064016 | 0.06109 | -0.00093998 | -0.0010382 | -0.0030719 | -0.012207 | 0.0029137 | 0.066302 | 0.061566 | -0.0052638 | 0.0081561 | -0.0037362 | -0.064087 | 62.9929 | -59.317 | 63.1531 | -59.0973 | -59.4818 | -59.4543 | -0.045776 | 62.9517 | -59.2392 | 63.176 | -59.2438 | -59.3491 | -59.2575 | -0.1236 | -0.09613 | 0.064087 | 0.09613 | -0.26093 | -0.28839 | -0.13733 | -0.16479 | -0.045777 | -0.13733 | 0.086975 | -0.050354 | -0.064087 | -0.15564 | -0.01831 | -0.10986 | 0.21973 | 122.4701 | -0.004577 | 122.4152 | 122.3099 | 122.1909 | 122.1863 | 122.1451 | -122.406 | -122.3282 | 122.3465 | 122.3694 | 59.1293 | 59.1476
523.3125 | 122.6669 | -59.2163 | 63.0569 | -0.11162 | 0.0030484 | 0.065939 | 0.060235 | -0.00029898 | -0.0018928 | -0.0039265 | -0.067139 | 0.0016321 | 0.066302 | 0.060284 | -0.0046228 | 0.01072 | -0.0065134 | -0.041199 | 63.0066 | -59.2987 | 63.2034 | -59.0424 | -59.4543 | -59.4269 | 0.004578 | 62.9745 | -59.2072 | 63.208 | -59.2026 | -59.3445 | -59.23 | -0.082397 | -0.050354 | 0.14648 | 0.17395 | -0.21057 | -0.23804 | -0.12817 | -0.15564 | 0.009156 | -0.082398 | 0.15106 | 0.013733 | -0.013733 | -0.12817 | -0.022889 | -0.13733 | 0.25635 | 122.5021 | 0.004577 | 122.4152 | 122.3053 | 122.1817 | 122.2229 | 122.1909 | -122.3557 | -122.2641 | 122.4197 | 122.4243 | 59.1751 | 59.2209
524.3125 | 122.6349 | -59.2209 | 63.0615 | -0.065842 | 0.004971 | 0.065085 | 0.062158 | 0.0031188 | -0.0014654 | -0.00050846 | -0.048828 | 0.0024865 | 0.066302 | 0.05943 | -0.00505 | 0.0075153 | -0.0001046 | -0.022888 | 62.9791 | -59.2896 | 63.2034 | -59.0332 | -59.4498 | -59.4086 | -0.013733 | 62.9425 | -59.2346 | 63.2034 | -59.2117 | -59.3308 | -59.23 | -0.068665 | -0.082397 | 0.14191 | 0.18768 | -0.18768 | -0.22888 | -0.11902 | -0.16022 | -0.013733 | -0.11902 | 0.14191 | 0.009155 | -0.009156 | -0.10986 | 0.004577 | -0.096131 | 0.25635 | 122.493 | 0.022888 | 122.438 | 122.2687 | 122.1771 | 122.2 | 122.1634 | -122.3511 | -122.2961 | 122.4243 | 122.4243 | 59.198 | 59.2072
525.3125 | 122.612 | -59.2392 | 63.0798 | -0.050583 | 0.001553 | 0.064657 | 0.062158 | -0.0011536 | -0.0014654 | -0.0015765 | -0.030517 | 0.0012047 | 0.066516 | 0.061566 | -0.0048364 | 0.01072 | -0.0024546 | -0.041199 | 62.9837 | -59.317 | 63.1897 | -59.0424 | -59.4543 | -59.4269 | 0 | 62.97 | -59.2392 | 63.1714 | -59.2346 | -59.3491 | -59.2529 | -0.07782 | -0.09613 | 0.10986 | 0.19684 | -0.18768 | -0.21515 | -0.10986 | -0.13733 | 0 | -0.10986 | 0.091553 | 0.004578 | -0.013733 | -0.10986 | -0.013733 | -0.10986 | 0.27466 | 122.5067 | 0.004578 | 122.4106 | 122.3007 | 122.2092 | 122.2229 | 122.2092 | -122.3969 | -122.319 | 122.4289 | 122.4106 | 59.198 | 59.2392
526.3125 | 122.5571 | -59.2026 | 63.0661 | -0.042954 | 0.0030484 | 0.063162 | 0.06109 | -0.00072638 | -0.0010382 | -0.00029486 | -0.015259 | 0.0016321 | 0.066943 | 0.062207 | -0.003341 | 0.0083697 | -0.0035226 | -0.059509 | 62.9654 | -59.2941 | 63.1622 | -59.1156 | -59.4727 | -59.4452 | -0.054932 | 62.9517 | -59.2392 | 63.176 | -59.2392 | -59.1156 | -59.0378 | -0.091552 | -0.10071 | 0.09613 | 0.086975 | -0.24261 | -0.27008 | -0.15106 | -0.17853 | -0.036621 | -0.11444 | 0.10986 | -0.036621 | 0.16479 | 0.086975 | 0.20142 | 0.1236 | 0.17853 | 122.4564 | 0 | 122.4152 | 122.2595 | 122.1909 | 122.168 | 122.1542 | -122.3602 | -122.3053 | 122.3648 | 122.3785 | 59.1431 | 59.1476
527.3125 | 122.6624 | -59.1797 | 63.121 | -0.027695 | 0.001553 | 0.063162 | 0.060876 | 0.0018372 | -0.004029 | -0.0011493 | 0.0061035 | 0.00035035 | 0.065234 | 0.057935 | -0.00505 | 0.0075153 | -0.0028818 | 0.027466 | 63.0295 | -59.2758 | 63.2401 | -58.9874 | -59.3582 | -59.3719 | 0.11444 | 62.9883 | -59.1934 | 63.2263 | -59.1431 | -59.2575 | -59.2072 | -0.096131 | -0.091553 | 0.11902 | 0.19226 | -0.19226 | -0.17853 | -0.09613 | -0.082397 | -0.013733 | -0.13275 | 0.10529 | 0.036621 | -0.027466 | -0.07782 | -0.013733 | -0.064087 | 0.28839 | 122.5159 | 0.050354 | 122.4197 | 122.3053 | 122.1817 | 122.2092 | 122.168 | -122.3969 | -122.3145 | 122.4197 | 122.406 | 59.2072 | 59.2941
528.3125 | 122.6349 | -59.2117 | 63.0798 | -0.096359 | 0.0030484 | 0.063162 | 0.059595 | -0.0015808 | -0.0044562 | -8.1264e-05 | -0.033569 | -7.6854e-05 | 0.064166 | 0.061352 | -0.0054774 | 0.0085833 | -0.0039498 | -0.036621 | 62.9837 | -59.2896 | 63.1943 | -59.0515 | -59.4452 | -59.4131 | 0.004578 | 62.9333 | -59.2209 | 63.1943 | -59.2026 | -59.317 | -59.2255 | -0.07782 | -0.09613 | 0.11444 | 0.16022 | -0.20142 | -0.23346 | -0.1236 | -0.15564 | -0.009155 | -0.14648 | 0.11444 | 0.009155 | -0.013733 | -0.10529 | -0.004578 | -0.096131 | 0.23804 | 122.4838 | 0.01831 | 122.4152 | 122.2733 | 122.1542 | 122.1954 | 122.1451 | -122.3694 | -122.3007 | 122.406 | 122.406 | 59.1751 | 59.2163
529.3125 | 122.612 | -59.2163 | 63.0936 | -0.058212 | 0.003262 | 0.063589 | 0.060449 | 0.0014098 | -0.0018928 | -0.0037129 | -0.042725 | 0.00013675 | 0.063525 | 0.058362 | -0.0048364 | 0.0085833 | -0.0048044 | -0.050354 | 62.97 | -59.3079 | 63.1714 | -59.0607 | -59.4864 | -59.4177 | -0.032043 | 62.9425 | -59.2346 | 63.1577 | -59.23 | -59.3536 | -59.2438 | -0.091552 | -0.1236 | 0.07782 | 0.15564 | -0.20142 | -0.27008 | -0.10986 | -0.17853 | -0.01831 | -0.15106 | 0.064087 | -0.013733 | -0.027465 | -0.13733 | -0.009155 | -0.11902 | 0.24719 | 122.4792 | 0.004577 | 122.3923 | 122.2778 | 122.1771 | 122.1863 | 122.1588 | -122.4014 | -122.3282 | 122.3877 | 122.374 | 59.166 | 59.1843
530.3125 | 122.6212 | -59.1934 | 63.0569 | -0.027695 | 0.0028348 | 0.064657 | 0.064081 | 0.0026916 | -0.0021064 | 0.00077334 | -0.097656 | 0.00077755 | 0.066302 | 0.072675 | -0.0059046 | 0.010506 | -0.0035226 | -0.054932 | 62.9791 | -59.317 | 63.1622 | -59.0744 | -59.4498 | -59.436 | -0.032043 | 62.9608 | -59.2438 | 63.0936 | -59.23 | -59.1019 | -59.0286 | -0.1236 | -0.07782 | 0.10528 | 0.11902 | -0.24261 | -0.25635 | -0.11902 | -0.13275 | -0.050354 | -0.096131 | 0.036621 | -0.036622 | 0.1648 | 0.091552 | 0.21515 | 0.14191 | 0.24262 | 122.4792 | 0.013732 | 122.3373 | 122.2961 | 122.2046 | 122.1725 | 122.1542 | -122.374 | -122.3007 | 122.3557 | 122.287 | 59.1385 | 59.1614
531.3125 | 122.6486 | -59.2072 | 63.0707 | -0.065842 | 0.0039028 | 0.063376 | 0.060235 | 0.00055542 | -0.00082456 | 0.0022687 | -0.057983 | 0.0020593 | 0.066729 | 0.059003 | -0.0059046 | 0.010079 | -0.0007456 | -0.054932 | 62.9837 | -59.2941 | 63.1851 | -59.0378 | -59.4543 | -59.4315 | 0.004578 | 62.9608 | -59.2117 | 63.2034 | -59.1843 | -59.3079 | -59.2117 | -0.086975 | -0.086975 | 0.11444 | 0.16937 | -0.22431 | -0.24719 | -0.13733 | -0.16022 | -0.004578 | -0.10986 | 0.13275 | 0.022888 | -0.004578 | -0.10071 | 0 | -0.09613 | 0.25635 | 122.4792 | 0.027466 | 122.4152 | 122.2778 | 122.1725 | 122.1909 | 122.168 | -122.3648 | -122.2824 | 122.3923 | 122.4106 | 59.1522 | 59.2117
532.3125 | 122.644 | -59.2163 | 63.0661 | -0.012436 | 0.0028348 | 0.062735 | 0.059381 | -8.538e-05 | -0.003388 | -0.00050846 | 0.0091553 | 0.0041955 | 0.066089 | 0.061993 | -0.0035548 | 0.0081561 | -0.0028818 | 0.009155 | 63.0249 | -59.2758 | 63.2263 | -58.9874 | -59.3628 | -59.3491 | 0.14648 | 62.9791 | -59.166 | 63.4186 | -59.436 | -59.4681 | -59.2392 | -0.059509 | -0.041199 | 0.16022 | 0.22888 | -0.13275 | -0.14648 | -0.073242 | -0.086975 | 0.050354 | -0.086975 | 0.35248 | -0.21973 | -0.022888 | -0.25177 | -0.073242 | -0.30212 | 0.28839 | 122.5021 | -0.27008 | 122.5845 | 122.3007 | 122.1451 | 122.2412 | 122.1954 | -122.3419 | -122.2321 | 122.4426 | 122.6349 | 59.2255 | 59.3628
533.3125 | 122.6257 | -59.2209 | 63.0753 | -0.10399 | 0.0030484 | 0.065512 | 0.060663 | 0.0016236 | -0.0018928 | 0.00055974 | -0.05188 | 0.00077755 | 0.066729 | 0.064557 | -0.0048364 | 0.0085833 | -0.0009592 | -0.036621 | 62.9654 | -59.317 | 63.1897 | -59.0424 | -59.4498 | -59.4086 | 0.004578 | 62.9608 | -59.2209 | 63.1989 | -59.2163 | -59.3216 | -59.2346 | -0.096131 | -0.10986 | 0.11444 | 0.17853 | -0.18768 | -0.22888 | -0.091552 | -0.13275 | 0 | -0.11444 | 0.1236 | 0.004577 | -0.013733 | -0.10071 | -0.013733 | -0.10071 | 0.27466 | 122.5067 | 0.004577 | 122.4197 | 122.2824 | 122.1817 | 122.1863 | 122.1817 | -122.3923 | -122.2961 | 122.4106 | 122.4197 | 59.1843 | 59.2255
534.3125 | 122.6349 | -59.2209 | 63.089 | -0.11162 | 0.0024076 | 0.064657 | 0.062372 | -8.538e-05 | -0.0021064 | -0.0032855 | -0.033569 | 0.0018457 | 0.065661 | 0.064984 | -0.0046228 | 0.0098651 | -0.0028818 | -0.041199 | 62.9608 | -59.2987 | 63.1668 | -59.0652 | -59.4818 | -59.4269 | -0.045776 | 62.9608 | -59.2255 | 63.1805 | -59.2392 | -59.3582 | -59.2667 | -0.07782 | -0.12817 | 0.07782 | 0.15564 | -0.20599 | -0.26093 | -0.12817 | -0.18311 | -0.004578 | -0.12817 | 0.091553 | -0.018311 | -0.045777 | -0.13733 | -0.041199 | -0.13275 | 0.23346 | 122.4655 | -0.013733 | 122.406 | 122.2595 | 122.1863 | 122.1817 | 122.1817 | -122.3877 | -122.3145 | 122.3877 | 122.4014 | 59.1797 | 59.1751
535.3125 | 122.6349 | -59.2117 | 63.0844 | -0.10399 | 0.0030484 | 0.064657 | 0.060449 | 0.00055542 | -0.0042426 | -0.0026447 | -0.042725 | 0.00077755 | 0.067157 | 0.058362 | -0.0044092 | 0.0081561 | -0.0030954 | -0.032043 | 62.9837 | -59.3033 | 63.1989 | -59.0515 | -59.4727 | -59.4223 | -0.009155 | 62.9471 | -59.2209 | 63.1989 | -59.1888 | -59.317 | -59.23 | -0.091553 | -0.10071 | 0.11444 | 0.16022 | -0.21057 | -0.26093 | -0.11902 | -0.16937 | -0.009155 | -0.13733 | 0.11444 | 0.022888 | -0.018311 | -0.10529 | -0.009156 | -0.096131 | 0.25177 | 122.5021 | 0.032043 | 122.4197 | 122.287 | 122.168 | 122.1954 | 122.1588 | -122.3877 | -122.3053 | 122.4106 | 122.4106 | 59.1797 | 59.2026
536.3125 | 122.6395 | -59.2026 | 63.089 | -0.081101 | 0.0028348 | 0.066153 | 0.060449 | 0.0026916 | -0.0012518 | -0.00050846 | -0.027466 | 0.0014185 | 0.06502 | 0.057935 | -0.0054774 | 0.0092241 | -0.0035226 | -0.032043 | 62.97 | -59.2987 | 63.208 | -59.0424 | -59.4589 | -59.4269 | 0.009155 | 62.9608 | -59.2117 | 63.1805 | -59.2209 | -59.3445 | -59.2392 | -0.09613 | -0.11902 | 0.11902 | 0.16022 | -0.2243 | -0.25635 | -0.12817 | -0.16022 | -0.009155 | -0.12817 | 0.091553 | -0.01831 | -0.036621 | -0.14191 | -0.027466 | -0.13275 | 0.25635 | 122.5067 | -0.009155 | 122.3923 | 122.2687 | 122.1725 | 122.1725 | 122.1634 | -122.3877 | -122.3007 | 122.4106 | 122.3831 | 59.1705 | 59.2117
537.3125 | 122.644 | -59.2209 | 63.0936 | -0.035324 | 0.0036892 | 0.06188 | 0.062158 | 0.00034182 | -0.0027472 | -0.0017903 | 0.045776 | 0.0016321 | 0.068011 | 0.06477 | -0.0035548 | 0.0073015 | -0.003309 | -0.041199 | 62.9837 | -59.2941 | 63.1897 | -59.0561 | -59.7565 | -59.4589 | -0.050354 | 62.9425 | -59.2163 | 63.2172 | -59.2117 | -59.317 | -59.23 | -0.073242 | -0.10986 | 0.09613 | 0.16479 | -0.23804 | -0.53558 | -0.16479 | -0.46234 | 0.004577 | -0.15106 | 0.1236 | 0.009155 | -0.009156 | -0.096131 | -0.013733 | -0.10071 | 0.23804 | 122.4838 | 0.004578 | 122.4335 | 122.2778 | 122.1588 | 122.2046 | 122.1634 | -122.3877 | -122.3099 | 122.4106 | 122.438 | 59.1797 | 59.1705
538.3125 | 122.6486 | -59.2072 | 63.0569 | -0.081101 | 0.0030484 | 0.066153 | 0.060235 | 0.0018372 | -0.0010382 | 0.00077334 | -0.067139 | 0.0022729 | 0.068225 | 0.063489 | -0.0024866 | 0.01072 | -0.0020272 | -0.041199 | 62.97 | -59.2987 | 63.1897 | -59.0561 | -59.4589 | -59.436 | -0.018311 | 62.9562 | -59.2346 | 63.2172 | -59.0103 | -59.2667 | -59.2621 | -0.091553 | -0.086975 | 0.13275 | 0.15106 | -0.22888 | -0.25177 | -0.13733 | -0.16022 | -0.027466 | -0.10071 | 0.16022 | 0.19684 | -0.054932 | -0.05951 | -0.027466 | -0.032044 | 0.24262 | 122.4884 | 0.2243 | 122.4518 | 122.2687 | 122.1909 | 122.1771 | 122.1634 | -122.3557 | -122.2916 | 122.3969 | 122.4243 | 59.166 | 59.1888
539.3125 | 122.6349 | -59.2255 | 63.0844 | 0.056229 | 0.000485 | 0.064871 | 0.061303 | 0.00076902 | 0.00045724 | -0.0034991 | -0.027466 | -0.00050405 | 0.065875 | 0.063489 | -0.003341 | 0.0081561 | -0.0022408 | -0.004578 | 62.9837 | -59.3033 | 63.1943 | -59.0652 | -59.4498 | -59.4086 | -0.013733 | 62.9517 | -59.2255 | 63.208 | -59.1843 | -59.3353 | -59.2117 | -0.07782 | -0.10071 | 0.10986 | 0.16022 | -0.1831 | -0.2243 | -0.10529 | -0.14648 | 0 | -0.13275 | 0.1236 | 0.041199 | 0.013733 | -0.10986 | 0.013733 | -0.10986 | 0.23804 | 122.4976 | 0.041199 | 122.4335 | 122.287 | 122.1771 | 122.2092 | 122.1771 | -122.3877 | -122.3099 | 122.4197 | 122.4335 | 59.2209 | 59.2117
540.3125 | 122.6349 | -59.198 | 63.0615 | -0.11162 | 0.0017666 | 0.066366 | 0.061944 | 0.00012822 | -0.0029608 | 0.0018413 | -0.015259 | 0.0016321 | 0.062457 | 0.065625 | -0.0029138 | 0.0083697 | 0.0003226 | -0.036621 | 62.9929 | -59.3216 | 63.1851 | -59.0378 | -59.4543 | -59.4315 | -0.009155 | 62.9471 | -59.2209 | 63.2034 | -59.2117 | -59.3216 | -59.2209 | -0.1236 | -0.068664 | 0.1236 | 0.16022 | -0.23346 | -0.25635 | -0.10986 | -0.13275 | -0.022888 | -0.11444 | 0.14191 | -0.013733 | -0.022888 | -0.1236 | 0 | -0.10071 | 0.28381 | 122.5067 | 0.009155 | 122.4243 | 122.3145 | 122.168 | 122.1909 | 122.1451 | -122.3831 | -122.2824 | 122.3831 | 122.4014 | 59.1614 | 59.1888
541.3125 | 122.6028 | -59.2163 | 63.0615 | -0.065842 | 0.0028348 | 0.062948 | 0.056604 | 0.00076902 | -0.00232 | -0.0017903 | -0.039673 | 0.00099115 | 0.066516 | 0.062848 | -0.0059046 | 0.0090105 | -0.0026682 | -0.036621 | 62.9883 | -59.3033 | 63.1943 | -59.0424 | -59.4635 | -59.4269 | -0.009155 | 62.9425 | -59.2209 | 63.2126 | -59.198 | -59.3262 | -59.2255 | -0.086975 | -0.073242 | 0.13275 | 0.17395 | -0.21057 | -0.24719 | -0.1236 | -0.16022 | -0.004577 | -0.11902 | 0.15106 | 0.018311 | -0.009155 | -0.10986 | -0.004578 | -0.10529 | 0.26093 | 122.4976 | 0.022888 | 122.4335 | 122.2916 | 122.1634 | 122.2046 | 122.1588 | -122.3648 | -122.2824 | 122.4106 | 122.4289 | 59.1797 | 59.2072
542.3125 | 122.6532 | -59.2072 | 63.0707 | -0.11925 | 0.0028348 | 0.063803 | 0.060022 | -8.538e-05 | -0.0014654 | -0.00072206 | -0.039673 | 0.00013675 | 0.066302 | 0.057507 | -0.005691 | 0.0092241 | -0.0056588 | -0.018311 | 62.9745 | -59.2896 | 63.2034 | -59.0515 | -59.4772 | -59.4498 | -0.004578 | 62.9608 | -59.23 | 63.2172 | -59.2026 | -59.3124 | -59.2117 | -0.082398 | -0.096131 | 0.13275 | 0.15564 | -0.24262 | -0.27008 | -0.16022 | -0.18768 | -0.022889 | -0.10986 | 0.14648 | 0.004577 | -0.004578 | -0.10529 | 0.018311 | -0.082397 | 0.23804 | 122.493 | 0.027466 | 122.4472 | 122.2641 | 122.1909 | 122.1817 | 122.168 | -122.3602 | -122.3007 | 122.4106 | 122.4243 | 59.1888 | 59.2026
543.3125 | 122.6257 | -59.2346 | 63.0936 | -0.10399 | 0.0028348 | 0.062521 | 0.061303 | 0.0022644 | -0.0038154 | -0.0015765 | -0.07019 | 0.0037683 | 0.063098 | 0.062634 | -0.0044092 | 0.0087969 | 0.000109 | -0.09613 | 63.002 | -59.3628 | 63.1393 | -59.1248 | -59.5139 | -59.4681 | -0.064087 | 62.9471 | -59.2392 | 63.1805 | -59.2255 | -59.3308 | -59.2209 | -0.12817 | -0.091553 | 0.045776 | 0.10986 | -0.23346 | -0.27924 | -0.10529 | -0.15106 | -0.004578 | -0.14648 | 0.086975 | 0.009155 | 0.013733 | -0.096131 | 0.018311 | -0.091553 | 0.23804 | 122.5021 | 0.013733 | 122.4197 | 122.3648 | 122.1863 | 122.2366 | 122.1817 | -122.4564 | -122.3328 | 122.374 | 122.4152 | 59.1385 | 59.1705
544.3125 | 122.6395 | -59.2575 | 63.0844 | -0.081101 | 0.0039028 | 0.063803 | 0.059167 | -0.00072638 | -0.0031744 | -0.0041401 | -0.079346 | 0.00035035 | 0.065875 | 0.069897 | -0.0035548 | 0.010079 | -0.0011728 | -0.086975 | 63.0157 | -59.3399 | 63.089 | -59.1431 | -59.5459 | -59.5047 | -0.09613 | 62.9745 | -59.23 | 63.176 | -59.23 | -59.3811 | -59.2484 | -0.082398 | -0.068665 | 0.004577 | 0.11444 | -0.24719 | -0.28839 | -0.16479 | -0.20599 | 0.027465 | -0.10986 | 0.091552 | 0.027465 | 0.009155 | -0.1236 | -0.01831 | -0.15106 | 0.19684 | 122.4289 | 0 | 122.406 | 122.3557 | 122.2046 | 122.2733 | 122.2321 | -122.4243 | -122.3145 | 122.3465 | 122.4335 | 59.1705 | 59.1614
545.3125 | 122.5754 | -59.23 | 63.0615 | -0.050583 | 0.0019802 | 0.062735 | 0.061944 | -0.00029898 | -0.0042426 | -0.00050846 | -0.064087 | 0.00013675 | 0.066089 | 0.062207 | -0.0046228 | 0.01072 | -0.0020272 | -0.10986 | 63.0157 | -59.3262 | 63.0844 | -59.1614 | -59.5596 | -59.5184 | -0.11902 | 62.9745 | -59.2346 | 63.1577 | -59.2804 | -59.404 | -59.285 | -0.09613 | -0.045776 | 0.022889 | 0.068665 | -0.28839 | -0.32959 | -0.19226 | -0.23346 | -0.004577 | -0.086975 | 0.096131 | -0.050354 | -0.054931 | -0.17395 | -0.050354 | -0.16937 | 0.16479 | 122.4106 | -0.045777 | 122.3923 | 122.3419 | 122.2092 | 122.2458 | 122.2046 | -122.3877 | -122.2961 | 122.3145 | 122.3877 | 59.1202 | 59.111
546.3125 | 122.6532 | -59.2209 | 63.0432 | -0.050583 | 0.0041166 | 0.062308 | 0.060663 | 0.00055542 | -0.0018928 | 0.00055974 | -0.054932 | 0.0024865 | 0.064807 | 0.057935 | -0.0048364 | 0.0092241 | -0.0007456 | -0.054932 | 62.9791 | -59.3124 | 63.1393 | -59.0744 | -59.4772 | -59.4406 | -0.022888 | 62.9562 | -59.2529 | 63.1989 | -59.2072 | -59.3262 | -59.2117 | -0.091553 | -0.064087 | 0.09613 | 0.14648 | -0.21973 | -0.25635 | -0.12817 | -0.1648 | -0.032044 | -0.086975 | 0.15564 | 0.013733 | 0.009155 | -0.10529 | 0.041199 | -0.073242 | 0.23804 | 122.4518 | 0.045777 | 122.4518 | 122.2916 | 122.2092 | 122.2 | 122.1771 | -122.3557 | -122.2961 | 122.3602 | 122.4197 | 59.166 | 59.198
547.3125 | 122.6303 | -59.198 | 63.0661 | -0.08873 | 0.0013394 | 0.062948 | 0.060663 | -0.005426 | -0.005738 | -0.00093566 | -0.027466 | 0.0018457 | 0.066943 | 0.055798 | -0.0063318 | 0.0090105 | -0.0020272 | -0.027466 | 62.9883 | -59.2896 | 63.1851 | -59.0973 | -59.4406 | -59.436 | 0 | 62.9379 | -59.2117 | 63.2126 | -59.2026 | -59.3079 | -59.2117 | -0.091553 | -0.07782 | 0.11902 | 0.10071 | -0.23804 | -0.24262 | -0.14648 | -0.15106 | -0.013733 | -0.12817 | 0.14648 | -0.004578 | -0.013733 | -0.10986 | 0 | -0.09613 | 0.19226 | 122.4747 | 0.009155 | 122.4243 | 122.2778 | 122.1497 | 122.1863 | 122.1359 | -122.3557 | -122.2778 | 122.3831 | 122.4106 | 59.1705 | 59.198
548.3125 | 122.6486 | -59.2209 | 63.0661 | -0.08873 | 0.0034756 | 0.066153 | 0.060022 | 0.0033324 | -0.00232 | -0.00093566 | 0.057983 | -0.00029045 | 0.068011 | 0.060925 | -0.0054774 | 0.0092241 | -0.003309 | -0.036621 | 62.9654 | -59.3216 | 63.1805 | -59.0195 | -59.7153 | -59.5734 | 0.009155 | 62.9654 | -59.2026 | 63.2034 | -59.2026 | -59.3124 | -59.2209 | -0.10071 | -0.10071 | 0.11444 | 0.20142 | -0.35248 | -0.49439 | -0.25177 | -0.39368 | 0.01831 | -0.10071 | 0.13733 | 0.01831 | 0 | -0.091553 | -0.01831 | -0.10986 | 0.30212 | 122.5021 | 0 | 122.406 | 122.287 | 122.168 | 122.1863 | 122.1863 | -122.3877 | -122.2687 | 122.4014 | 122.4243 | 59.1843 | 59.23
549.3125 | 122.6395 | -59.2117 | 63.0524 | -0.065842 | 0.0013394 | 0.066153 | 0.060022 | -0.002008 | -0.00039736 | -0.0028583 | -0.030517 | 0.0020593 | 0.068225 | 0.059216 | -0.005691 | 0.0083697 | -0.0018136 | -0.045776 | 62.9974 | -59.2987 | 63.1714 | -59.0744 | -59.4498 | -59.4223 | -0.027466 | 62.9562 | -59.2346 | 63.1989 | -59.2163 | -59.3399 | -59.2209 | -0.086975 | -0.054931 | 0.11902 | 0.13733 | -0.21057 | -0.23804 | -0.1236 | -0.15106 | -0.022888 | -0.09613 | 0.14648 | -0.004578 | -0.009155 | -0.12817 | 0.013733 | -0.10529 | 0.2243 | 122.4701 | 0.01831 | 122.4335 | 122.2961 | 122.1909 | 122.2092 | 122.168 | -122.3511 | -122.287 | 122.3831 | 122.4106 | 59.166 | 59.1843
550.3125 | 122.5891 | -59.2438 | 63.0981 | -0.050583 | 0.0017666 | 0.063803 | 0.062585 | 0.0018372 | -0.0016792 | 0.0014141 | -0.048828 | 0.0039819 | 0.067157 | 0.067761 | -0.006759 | 0.0090105 | 0.0005362 | -0.09613 | 63.002 | -59.3079 | 63.0798 | -59.166 | -59.5596 | -59.5276 | -0.11902 | 62.97 | -59.2484 | 63.1256 | -59.2804 | -59.4086 | -59.2896 | -0.064087 | -0.096131 | -0.018311 | 0.077819 | -0.28381 | -0.31586 | -0.21973 | -0.25177 | -0.004578 | -0.12817 | 0.027465 | -0.036622 | -0.045777 | -0.16479 | -0.041199 | -0.16022 | 0.14191 | 122.3877 | -0.032044 | 122.374 | 122.3099 | 122.2183 | 122.2458 | 122.2137 | -122.406 | -122.3465 | 122.3236 | 122.3694 | 59.1476 | 59.1248
551.3125 | 122.5388 | -59.2438 | 63.0936 | -0.081101 | 0.0017666 | 0.063589 | 0.061303 | -0.00093998 | -0.0042426 | -0.00093566 | -0.057983 | 0.00077755 | 0.068225 | 0.061139 | -0.0041956 | 0.01072 | -0.0003182 | -0.09613 | 63.0249 | -59.3399 | 63.0569 | -59.1751 | -59.5551 | -59.5367 | -0.13275 | 62.9883 | -59.2575 | 63.1073 | -59.2941 | -59.4452 | -59.317 | -0.096131 | -0.068665 | -0.036621 | 0.068664 | -0.29297 | -0.31128 | -0.19684 | -0.21515 | -0.013733 | -0.10529 | 0.013733 | -0.050354 | -0.073243 | -0.20142 | -0.05951 | -0.18768 | 0.1648 | 122.3969 | -0.036621 | 122.3648 | 122.3648 | 122.2458 | 122.2687 | 122.2321 | -122.4335 | -122.3511 | 122.3007 | 122.3511 | 59.1476 | 59.111
552.3281 | 122.5388 | -59.2209 | 63.1073 | -0.0048066 | 0.0034756 | 0.063376 | 0.060663 | -8.538e-05 | -0.0059516 | 0.0024823 | -0.088501 | 0.0031273 | 0.065661 | 0.064984 | -0.003982 | 0.0085833 | -0.0028818 | -0.018311 | 63.0112 | -59.2941 | 63.1439 | -59.111 | -59.491 | -59.4818 | -0.022888 | 62.9929 | -59.23 | 63.121 | -59.2758 | -59.404 | -59.3033 | -0.073242 | -0.096131 | 0.036621 | 0.10986 | -0.26093 | -0.27008 | -0.18768 | -0.19684 | -0.009156 | -0.11444 | 0.013733 | -0.054932 | -0.082398 | -0.18311 | -0.073242 | -0.17395 | 0.1831 | 122.438 | -0.045776 | 122.3511 | 122.3053 | 122.2229 | 122.2321 | 122.2137 | -122.4014 | -122.3373 | 122.3648 | 122.3419 | 59.2026 | 59.198
553.3125 | 122.58 | -59.2209 | 63.0615 | -0.0048066 | 0.0011258 | 0.065298 | 0.06109 | -0.0022218 | -0.0012518 | 0.00013254 | -0.01831 | 0.0031273 | 0.067157 | 0.063275 | -0.0046228 | 0.0092241 | -0.0018136 | -0.091553 | 63.0112 | -59.3353 | 63.1073 | -59.1476 | -59.5505 | -59.5001 | -0.10071 | 62.9929 | -59.2392 | 63.1485 | -59.2392 | -59.3857 | -59.2667 | -0.11444 | -0.050354 | 0.045777 | 0.073242 | -0.27924 | -0.32959 | -0.16479 | -0.21515 | -0.018311 | -0.068664 | 0.086976 | -0.018311 | -0.045777 | -0.16479 | -0.027466 | -0.14648 | 0.18768 | 122.4426 | 0 | 122.3877 | 122.3465 | 122.2321 | 122.2321 | 122.2137 | -122.3969 | -122.3007 | 122.3282 | 122.3694 | 59.1293 | 59.1202
554.3125 | 122.5937 | -59.198 | 63.0661 | -0.081101 | 0.0041166 | 0.06423 | 0.058954 | -0.00093998 | -0.00061096 | -0.0017903 | -0.024414 | 0.0012047 | 0.066089 | 0.059003 | -0.003982 | 0.01072 | -0.0016 | -0.041199 | 62.9745 | -59.3262 | 63.176 | -59.079 | -59.4635 | -59.4406 | -0.036621 | 62.9288 | -59.2346 | 63.1073 | -59.0332 | -59.1156 | -59.1248 | -0.12817 | -0.091553 | 0.10986 | 0.11902 | -0.24262 | -0.2655 | -0.11444 | -0.13733 | -0.036621 | -0.13733 | 0.041199 | 0.16479 | 0.073242 | 0.082397 | 0.10986 | 0.11902 | 0.24719 | 122.5021 | 0.20142 | 122.3419 | 122.3007 | 122.1634 | 122.1725 | 122.1268 | -122.3923 | -122.3007 | 122.374 | 122.3053 | 59.1568 | 59.1614
555.3125 | 122.5525 | -59.2438 | 63.0798 | -0.0048066 | 0.0011258 | 0.066366 | 0.060449 | -0.00029898 | -0.0031744 | -0.0011493 | -0.033569 | 0.0022729 | 0.06502 | 0.064984 | -0.00505 | 0.0094379 | -0.0013864 | -0.10529 | 63.0249 | -59.3308 | 63.0707 | -59.1705 | -59.5551 | -59.5322 | -0.13733 | 63.002 | -59.2667 | 63.1119 | -59.3079 | -59.4177 | -59.3124 | -0.086976 | -0.054932 | -0.009155 | 0.073242 | -0.28839 | -0.31128 | -0.20142 | -0.2243 | -0.022889 | -0.07782 | 0.032043 | -0.064087 | -0.068665 | -0.17395 | -0.045776 | -0.15106 | 0.16022 | 122.4014 | -0.041198 | 122.3785 | 122.3557 | 122.2687 | 122.2687 | 122.2458 | -122.4106 | -122.3465 | 122.3145 | 122.3557 | 59.1385 | 59.1064
556.3125 | 122.6166 | -59.2255 | 63.0478 | -0.14214 | 0.002194 | 0.063376 | 0.059167 | -0.0011536 | -0.0038154 | -0.0015765 | -0.030517 | 0.0024865 | 0.067157 | 0.05473 | -0.003341 | 0.0081561 | -0.0030954 | -0.10529 | 63.002 | -59.3262 | 63.1119 | -59.1202 | -59.5047 | -59.4818 | -0.064087 | 62.9517 | -59.2392 | 63.1668 | -59.2255 | -59.3308 | -59.2026 | -0.10071 | -0.045777 | 0.064086 | 0.10529 | -0.25635 | -0.27924 | -0.15564 | -0.17853 | -0.013733 | -0.096131 | 0.11902 | 0 | 0.022888 | -0.10529 | 0.036621 | -0.091553 | 0.20599 | 122.438 | 0.013733 | 122.406 | 122.3282 | 122.1909 | 122.2275 | 122.1771 | -122.374 | -122.287 | 122.3373 | 122.3923 | 59.1202 | 59.1614
557.3125 | 122.5388 | -59.23 | 63.1531 | -0.012436 | 0.0041166 | 0.063162 | 0.061731 | -0.0013672 | -0.0014654 | -0.0043537 | -0.01831 | 0.0018457 | 0.066516 | 0.06712 | -0.0037684 | 0.0087969 | -0.0045908 | -0.013733 | 63.0615 | -59.285 | 63.1119 | -59.1431 | -59.5139 | -59.4635 | -0.022888 | 63.0341 | -59.2392 | 63.1256 | -59.2438 | -59.3765 | -59.2758 | -0.054931 | -0.091553 | -0.041199 | 0.086976 | -0.23346 | -0.28381 | -0.17853 | -0.22888 | -0.009155 | -0.11902 | -0.027466 | -0.013732 | -0.045776 | -0.14648 | -0.036621 | -0.13733 | 0.14191 | 122.3969 | -0.004577 | 122.3648 | 122.3465 | 122.2733 | 122.2916 | 122.2641 | -122.438 | -122.3923 | 122.3419 | 122.3557 | 59.2163 | 59.2072
558.3125 | 122.5479 | -59.2621 | 63.1073 | -0.050583 | 0.0017666 | 0.064657 | 0.063012 | 0.00034182 | -0.00039736 | -0.0011493 | -0.076294 | 0.0022729 | 0.068225 | 0.060498 | -0.0031274 | 0.0083697 | 0.0022452 | -0.1236 | 63.0478 | -59.3536 | 63.0386 | -59.2346 | -59.5505 | -59.5413 | -0.13733 | 63.0066 | -59.2529 | 63.0844 | -59.3262 | -59.4589 | -59.317 | -0.091553 | -0.059509 | -0.068665 | 0.027466 | -0.27924 | -0.28839 | -0.18768 | -0.19684 | 0.009155 | -0.10071 | -0.022888 | -0.064087 | -0.054932 | -0.19684 | -0.064087 | -0.20599 | 0.11902 | 122.3923 | -0.073242 | 122.3373 | 122.4014 | 122.2595 | 122.3099 | 122.2687 | -122.4609 | -122.3602 | 122.3007 | 122.3465 | 59.1385 | 59.1248
559.3125 | 122.5021 | -59.2575 | 63.1119 | -0.13451 | 0.0036892 | 0.062948 | 0.059808 | -0.0028626 | -0.0038154 | -0.0017903 | -0.05188 | 0.0044091 | 0.068011 | 0.060498 | -0.0024866 | 0.0094379 | 0.000109 | -0.032043 | 63.0157 | -59.3536 | 63.0066 | -59.166 | -59.5047 | -59.5688 | -0.15564 | 63.0112 | -59.2575 | 63.0844 | -59.3399 | -59.4406 | -59.3216 | -0.096131 | -0.09613 | -0.10529 | 0.091552 | -0.31128 | -0.24719 | -0.21515 | -0.15106 | 0 | -0.10071 | -0.027465 | -0.082398 | -0.064087 | -0.18311 | -0.064087 | -0.18311 | 0.18768 | 122.3602 | -0.082398 | 122.3419 | 122.3694 | 122.2687 | 122.2733 | 122.2687 | -122.4655 | -122.3694 | 122.2641 | 122.3419 | 59.2255 | 59.1019
560.3125 | 122.6395 | -59.2346 | 63.0753 | -0.081101 | 0.0017666 | 0.06423 | 0.061731 | -0.0015808 | -0.00082456 | -0.0026447 | -0.015259 | 0.0022729 | 0.066516 | 0.061993 | -0.0048364 | 0.0098651 | -0.0018136 | -0.07782 | 62.9974 | -59.3353 | 63.1165 | -59.1293 | -59.5093 | -59.4681 | -0.073242 | 62.9517 | -59.2255 | 63.1805 | -59.2026 | -59.3491 | -59.2346 | -0.10071 | -0.077819 | 0.041199 | 0.10529 | -0.23346 | -0.27466 | -0.13275 | -0.17395 | 0.009155 | -0.1236 | 0.10529 | 0.032043 | 0 | -0.11444 | -0.009155 | -0.1236 | 0.20599 | 122.4518 | 0.022888 | 122.406 | 122.3328 | 122.1771 | 122.2321 | 122.1863 | -122.4106 | -122.3007 | 122.3511 | 122.4152 | 59.1568 | 59.1614
561.3125 | 122.5388 | -59.2438 | 63.0936 | -0.08873 | 0.0036892 | 0.063162 | 0.060235 | -0.0035034 | -0.0038154 | -0.00050846 | -0.048828 | 0.0020593 | 0.065875 | 0.066052 | -0.003982 | 0.0066607 | -0.0020272 | -0.10071 | 63.0157 | -59.3308 | 63.0615 | -59.1843 | -59.5871 | -59.5459 | -0.16022 | 62.9929 | -59.2575 | 63.0798 | -59.3353 | -59.436 | -59.3262 | -0.086976 | -0.07782 | -0.032044 | 0.059509 | -0.30212 | -0.34332 | -0.21515 | -0.25635 | -0.013733 | -0.10071 | -0.013733 | -0.091553 | -0.082398 | -0.19226 | -0.068665 | -0.17853 | 0.14648 | 122.3923 | -0.07782 | 122.3373 | 122.3465 | 122.2504 | 122.2595 | 122.2366 | -122.4243 | -122.3511 | 122.3053 | 122.3236 | 59.1431 | 59.0836
562.3125 | 122.6303 | -59.1888 | 63.1256 | -0.073471 | 0.0034756 | 0.056967 | 0.059381 | -0.0039306 | -0.0048834 | 0.0016277 | 0.042725 | 0.00099115 | 0.066302 | 0.055157 | -0.005691 | 0.0085833 | -0.000532 | 0.24719 | 63.1027 | -59.2209 | 63.1943 | -59.0469 | -59.317 | -59.3491 | 0.13733 | 62.97 | -59.198 | 63.2172 | -59.1385 | -59.2667 | -59.1843 | -0.032043 | -0.022888 | 0.068665 | 0.14191 | -0.16022 | -0.12817 | -0.12817 | -0.096131 | -0.009155 | -0.15564 | 0.091553 | 0.050354 | 0.004578 | -0.07782 | 0.013733 | -0.068665 | 0.17395 | 122.4152 | 0.059509 | 122.4152 | 122.3236 | 122.168 | 122.2916 | 122.1588 | -122.3465 | -122.3236 | 122.3831 | 122.406 | 59.436 | 59.3262
563.3125 | 122.5067 | -59.2529 | 63.1027 | 0.071487 | 0.0036892 | 0.064444 | 0.060449 | 0.00012822 | -0.0042426 | -8.1264e-05 | -0.064087 | 0.0037683 | 0.070361 | 0.063489 | -0.0041956 | 0.0096515 | -0.0030954 | -0.041199 | 63.0157 | -59.3399 | 63.0661 | -59.2072 | -59.5734 | -59.5184 | -0.15564 | 62.9883 | -59.2438 | 63.0844 | -59.3033 | -59.4818 | -59.3308 | -0.086975 | -0.086975 | -0.036621 | 0.045777 | -0.2655 | -0.32043 | -0.17853 | -0.23346 | 0.009156 | -0.11444 | -0.01831 | -0.050354 | -0.07782 | -0.22888 | -0.086976 | -0.23804 | 0.13275 | 122.406 | -0.05951 | 122.3282 | 122.3557 | 122.2321 | 122.2687 | 122.2412 | -122.4426 | -122.3465 | 122.319 | 122.3373 | 59.2117 | 59.0973
564.3125 | 122.5708 | -59.23 | 63.0569 | -0.058212 | 0.0017666 | 0.064444 | 0.062158 | -0.00093998 | -0.0021064 | -0.00072206 | -0.045776 | 0.00077755 | 0.06737 | 0.059003 | -0.0044092 | 0.0081561 | -0.0043772 | -0.09613 | 63.0341 | -59.3308 | 63.0844 | -59.1751 | -59.5551 | -59.5139 | -0.11444 | 62.9745 | -59.2484 | 63.1119 | -59.2987 | -59.4131 | -59.2987 | -0.10071 | -0.022888 | 0.027466 | 0.054932 | -0.28381 | -0.32501 | -0.1831 | -0.2243 | -0.01831 | -0.082398 | 0.054931 | -0.068664 | -0.068664 | -0.18311 | -0.050354 | -0.1648 | 0.15564 | 122.4152 | -0.050354 | 122.3602 | 122.3648 | 122.2229 | 122.2641 | 122.2046 | -122.3877 | -122.3053 | 122.3145 | 122.3419 | 59.1339 | 59.1156
565.3125 | 122.5113 | -59.2438 | 63.121 | -0.081101 | 0.0047574 | 0.065725 | 0.061944 | 0.00012822 | -0.003388 | -0.0045673 | -0.094604 | 0.0018457 | 0.06737 | 0.065625 | -0.0041956 | 0.0090105 | -0.0007456 | -0.091553 | 63.0524 | -59.3582 | 62.7411 | -59.4864 | -59.1614 | -59.2667 | -0.11902 | 63.0249 | -59.2529 | 63.0661 | -59.3353 | -59.4681 | -59.3536 | -0.11444 | -0.068665 | -0.37994 | -0.24262 | -0.022889 | 0.082397 | 0.091552 | 0.19684 | -0.009156 | -0.096131 | -0.054932 | -0.091553 | -0.10986 | -0.22431 | -0.10071 | -0.21515 | -0.12817 | 122.0993 | -0.082397 | 122.319 | 122.4106 | 122.2778 | 122.2961 | 122.2687 | -122.4792 | -122.374 | 121.9849 | 122.3099 | 59.1522 | 59.1248
566.3125 | 122.5204 | -59.23 | 63.1027 | 0.0028229 | 0.0026212 | 0.066366 | 0.060663 | 0.0016236 | -0.004029 | -0.0011493 | -0.054932 | 0.0029137 | 0.068011 | 0.063702 | -0.0024866 | 0.0094379 | -0.000532 | -0.082397 | 63.0341 | -59.3308 | 63.0478 | -59.2438 | -59.61 | -59.5734 | -0.45776 | 62.9242 | -59.3124 | 63.1119 | -59.3124 | -59.5184 | -59.3399 | -0.10071 | -0.068664 | -0.054931 | -0.013732 | -0.34332 | -0.37994 | -0.24261 | -0.27923 | -0.082397 | -0.17853 | 0.009155 | -0.082397 | -0.10986 | -0.28839 | -0.027466 | -0.20599 | 0.086976 | 122.3785 | 0 | 122.4243 | 122.3648 | 122.2366 | 122.2641 | 122.1542 | -122.4335 | -122.4152 | 122.2778 | 122.3419 | 59.1476 | 58.7723
567.3281 | 122.406 | -59.2163 | 63.1393 | -0.012436 | 0.0026212 | 0.063589 | 0.055963 | -0.0013672 | -0.0010382 | -0.0011493 | 0.042725 | 0.0035547 | 0.06502 | 0.065839 | -0.0041956 | 0.0096515 | -0.0030954 | 0.018311 | 63.0524 | -59.2529 | 63.1302 | -59.1064 | -59.491 | -59.4589 | -0.022888 | 63.0157 | -59.2209 | 63.0524 | -59.1797 | -59.1385 | -59.2484 | -0.036621 | -0.086975 | -0.009155 | 0.10986 | -0.24261 | -0.27466 | -0.20599 | -0.23804 | -0.004577 | -0.1236 | -0.086975 | 0.036622 | -0.032043 | 0.07782 | -0.027466 | 0.082397 | 0.14648 | 122.3831 | 0.041199 | 122.2733 | 122.3053 | 122.2366 | 122.2687 | 122.2321 | -122.3923 | -122.3602 | 122.3465 | 122.2687 | 59.2346 | 59.1934
568.3125 | 122.5113 | -59.2529 | 63.0844 | -0.020065 | 0.0009122 | 0.063376 | 0.062585 | -0.0017944 | -0.00232 | -0.00093566 | -0.05188 | 0.0029137 | 0.067157 | 0.062634 | -0.0044092 | 0.0085833 | -0.0003182 | -0.10986 | 63.0295 | -59.3353 | 63.0524 | -59.2117 | -59.6054 | -59.5551 | -0.14191 | 62.9974 | -59.2575 | 63.089 | -59.3216 | -59.4498 | -59.3262 | -0.082397 | -0.054932 | -0.032044 | 0.041199 | -0.30212 | -0.35248 | -0.21973 | -0.27008 | -0.004577 | -0.086975 | 0.004577 | -0.068664 | -0.073242 | -0.19684 | -0.068665 | -0.19226 | 0.1236 | 122.3877 | -0.064087 | 122.3465 | 122.3648 | 122.2549 | 122.2824 | 122.2504 | -122.4197 | -122.3419 | 122.3053 | 122.3419 | 59.1431 | 59.111
569.3125 | 122.5983 | -59.2346 | 63.089 | 0.0028229 | 0.0009122 | 0.065298 | 0.061944 | -0.0017944 | -0.0036018 | -0.0022175 | -0.033569 | 0.0033411 | 0.065448 | 0.062848 | -0.0037684 | 0.0079425 | -0.0035226 | -0.10986 | 63.0249 | -59.3491 | 63.0798 | -59.1705 | -59.5505 | -59.523 | -0.11902 | 62.9791 | -59.2529 | 63.1256 | -59.2804 | -59.404 | -59.2804 | -0.11444 | -0.064087 | -0.009155 | 0.064087 | -0.28839 | -0.31586 | -0.17395 | -0.20142 | -0.018311 | -0.10986 | 0.036621 | -0.045777 | -0.045777 | -0.16937 | -0.027466 | -0.15106 | 0.17853 | 122.4289 | -0.027466 | 122.3785 | 122.374 | 122.2321 | 122.2595 | 122.2137 | -122.438 | -122.3419 | 122.3145 | 122.3602 | 59.1248 | 59.1156
570.3125 | 122.5662 | -59.2438 | 63.0844 | -0.11162 | 0.0017666 | 0.065298 | 0.060663 | -0.0028626 | -0.00232 | -8.1264e-05 | -0.048828 | 0.0022729 | 0.067584 | 0.062207 | -0.003982 | 0.01072 | -0.0060862 | -0.086975 | 63.0157 | -59.3491 | 63.0798 | -59.1705 | -59.5505 | -59.523 | -0.13275 | 62.9608 | -59.2529 | 63.1165 | -59.2941 | -59.4086 | -59.2987 | -0.10529 | -0.068665 | -0.004578 | 0.073242 | -0.27924 | -0.3067 | -0.17395 | -0.20142 | -0.009156 | -0.1236 | 0.032043 | -0.050354 | -0.054932 | -0.16479 | -0.045776 | -0.15564 | 0.17853 | 122.4289 | -0.041198 | 122.3694 | 122.3648 | 122.2137 | 122.2595 | 122.2046 | -122.4335 | -122.3373 | 122.3236 | 122.3602 | 59.1568 | 59.111
571.3125 | 122.5204 | -59.2438 | 63.1165 | -0.073471 | 0.0039028 | 0.062948 | 0.061517 | 0.0016236 | -0.003388 | -0.00029486 | -0.064087 | 0.0044091 | 0.066302 | 0.063702 | -0.0078272 | 0.0073015 | -0.0007456 | -0.045776 | 63.0386 | -59.3079 | 63.089 | -59.1751 | -59.5551 | -59.5093 | -0.14648 | 63.0157 | -59.2346 | 63.0844 | -59.3308 | -59.4543 | -59.3399 | -0.064087 | -0.07782 | -0.027466 | 0.068664 | -0.2655 | -0.31128 | -0.20142 | -0.24719 | 0.009155 | -0.10071 | -0.032043 | -0.086976 | -0.096131 | -0.21057 | -0.10529 | -0.21973 | 0.13275 | 122.3969 | -0.096131 | 122.319 | 122.3465 | 122.2504 | 122.2824 | 122.2595 | -122.4243 | -122.3511 | 122.3328 | 122.3282 | 59.198 | 59.0973
572.3125 | 122.6624 | -59.1843 | 63.1027 | -0.073471 | 0.0026212 | 0.062735 | 0.057458 | 0.0039734 | -0.0027472 | 0.00034614 | 0.042725 | 0.0031273 | 0.066089 | 0.058148 | -0.0041956 | 0.0085833 | -0.0018136 | -0.068665 | 62.9929 | -59.2941 | 63.121 | -59.0744 | -59.4589 | -59.4406 | -0.064087 | 62.9562 | -59.2346 | 63.1393 | -59.2438 | -59.3079 | -59.111 | -0.10986 | -0.10986 | 0.018311 | 0.10986 | -0.25635 | -0.27466 | -0.14648 | -0.16479 | -0.050354 | -0.14648 | 0.036621 | -0.059509 | 0.073242 | -0.1236 | 0.1236 | -0.073242 | 0.21973 | 122.4152 | -0.009155 | 122.374 | 122.287 | 122.1909 | 122.1771 | 122.1405 | -122.3969 | -122.3373 | 122.3053 | 122.3236 | 59.1156 | 59.1202
573.3125 | 122.5159 | -59.2484 | 63.121 | -0.035324 | 0.0026212 | 0.062948 | 0.062158 | 0.002478 | -0.0027472 | -0.0037129 | -0.079346 | 0.0039819 | 0.066089 | 0.062848 | -0.0059046 | 0.0087969 | -0.003309 | -0.10071 | 63.0295 | -59.3399 | 62.8189 | -59.5322 | -59.3536 | -59.2438 | -0.15106 | 63.0157 | -59.2392 | 63.0707 | -59.3536 | -59.4635 | -59.3491 | -0.091553 | -0.091553 | -0.30212 | -0.28381 | 0.004578 | -0.10529 | 0.096131 | -0.013733 | 0.009155 | -0.10529 | -0.050354 | -0.10529 | -0.10071 | -0.21515 | -0.10986 | -0.2243 | -0.19226 | 122.1588 | -0.11444 | 122.3099 | 122.3694 | 122.2549 | 122.2778 | 122.2641 | -122.4609 | -122.3602 | 122.0673 | 122.319 | 59.1476 | 59.0973
574.3125 | 122.6486 | -59.2255 | 63.0707 | -0.073471 | 0.0017666 | 0.063376 | 0.06109 | -8.538e-05 | -0.00018376 | -0.0026447 | -8.6e-08 | 0.0035547 | 0.066089 | 0.065625 | -0.0052638 | 0.0079425 | -0.0026682 | -0.086975 | 62.9974 | -59.317 | 63.1256 | -59.1156 | -59.5001 | -59.4681 | -0.064087 | 62.9471 | -59.2346 | 63.1805 | -59.2163 | -59.3491 | -59.2163 | -0.091553 | -0.073242 | 0.054931 | 0.10986 | -0.24262 | -0.27466 | -0.15106 | -0.1831 | -0.009155 | -0.1236 | 0.10986 | 0.009155 | 0.009155 | -0.1236 | 0.01831 | -0.11444 | 0.20142 | 122.4426 | 0.01831 | 122.4152 | 122.3145 | 122.1817 | 122.2229 | 122.1725 | -122.3877 | -122.3053 | 122.3511 | 122.406 | 59.1385 | 59.1614
575.3125 | 122.5433 | -59.2346 | 63.089 | -0.096359 | 0.0034756 | 0.065725 | 0.060663 | 0.00034182 | -0.00082456 | -0.0017903 | -0.024414 | 0.0022729 | 0.067798 | 0.056226 | -0.0046228 | 0.0075153 | -0.0009592 | -0.09613 | 63.0295 | -59.3262 | 63.0569 | -59.1934 | -59.5551 | -59.5322 | -0.14191 | 62.9929 | -59.2621 | 63.089 | -59.3124 | -59.4315 | -59.3079 | -0.091553 | -0.059509 | -0.032043 | 0.041199 | -0.29755 | -0.32043 | -0.20599 | -0.22888 | -0.027466 | -0.09613 | 0 | -0.07782 | -0.073242 | -0.19684 | -0.045776 | -0.16937 | 0.13275 | 122.3831 | -0.050354 | 122.3511 | 122.3557 | 122.2549 | 122.2641 | 122.2275 | -122.4152 | -122.3511 | 122.2916 | 122.3236 | 59.1385 | 59.0927
576.3125 | 122.6486 | -59.2255 | 63.089 | -0.050583 | 0.002194 | 0.062948 | 0.059595 | -0.002649 | -0.0042426 | -0.0026447 | -0.021362 | 0.0016321 | 0.067584 | 0.064557 | -0.0035548 | 0.0077289 | -0.0018136 | -0.091553 | 62.9974 | -59.3079 | 63.1165 | -59.1019 | -59.5139 | -59.4681 | -0.064087 | 62.9608 | -59.23 | 63.1851 | -59.2163 | -59.3399 | -59.2209 | -0.082397 | -0.091552 | 0.027466 | 0.1236 | -0.24262 | -0.28839 | -0.16022 | -0.20599 | -0.004578 | -0.12817 | 0.096131 | 0.009155 | 0.004578 | -0.11444 | 0.009156 | -0.10986 | 0.20599 | 122.4243 | 0.013733 | 122.4152 | 122.3053 | 122.1909 | 122.2229 | 122.1863 | -122.3969 | -122.319 | 122.3419 | 122.4106 | 59.1339 | 59.1614
577.3125 | 122.6486 | -59.1843 | 63.1119 | -0.020065 | 0.002194 | 0.06423 | 0.058954 | -0.0035034 | -0.0036018 | 0.00055974 | 0.039673 | 0.0014185 | 0.068225 | 0.05708 | -0.0052638 | 0.0068743 | -0.003309 | -0.013733 | 63.0341 | -59.2804 | 63.1622 | -59.0378 | -59.4315 | -59.3857 | 0.041199 | 62.9608 | -59.2072 | 63.1668 | -59.1614 | -59.2667 | -59.198 | -0.096131 | -0.077819 | 0.050354 | 0.14648 | -0.20142 | -0.24719 | -0.10528 | -0.15106 | -0.022888 | -0.15106 | 0.054932 | 0.022888 | -0.013733 | -0.082398 | 0.009155 | -0.05951 | 0.24262 | 122.4426 | 0.045776 | 122.374 | 122.3145 | 122.168 | 122.2183 | 122.1451 | -122.3923 | -122.319 | 122.3465 | 122.3511 | 59.1705 | 59.2255
578.3125 | 122.5433 | -59.2484 | 63.089 | -0.058212 | 0.0028348 | 0.062735 | 0.061303 | -0.00029898 | 2.9842e-05 | 0.0020551 | -0.091553 | 0.0027001 | 0.066729 | 0.064343 | -0.0048364 | 0.0096515 | -0.0028818 | -0.086975 | 63.0249 | -59.3674 | 62.8098 | -58.9233 | -59.1934 | -59.4772 | -0.10071 | 63.0203 | -59.23 | 63.0707 | -59.3445 | -59.5093 | -59.3674 | -0.11902 | -0.064087 | -0.27924 | 0.32501 | -0.22888 | 0.054932 | -0.10986 | 0.17395 | 0.01831 | -0.068664 | -0.01831 | -0.09613 | -0.11902 | -0.26093 | -0.13733 | -0.27923 | 0.44403 | 122.1771 | -0.11444 | 122.3007 | 122.3923 | 122.2504 | 122.2733 | 122.2687 | -122.4564 | -122.319 | 122.0581 | 122.319 | 59.1614 | 59.1476
579.3125 | 122.5662 | -59.2346 | 63.1119 | -0.035324 | 0.0036892 | 0.062308 | 0.061303 | 0.00055542 | 0.00024344 | -0.0028583 | -0.021362 | 0.0035547 | 0.066516 | 0.064343 | -0.003982 | 0.010506 | -0.0035226 | -0.11902 | 63.0203 | -59.3491 | 63.0615 | -59.1843 | -59.5596 | -59.5322 | -0.13733 | 62.9745 | -59.2621 | 63.1119 | -59.3033 | -59.4406 | -59.2987 | -0.11444 | -0.091552 | -0.050354 | 0.050354 | -0.29755 | -0.32501 | -0.18311 | -0.21057 | -0.027466 | -0.13733 | 0 | -0.068665 | -0.064087 | -0.20599 | -0.036621 | -0.17853 | 0.16479 | 122.4106 | -0.041199 | 122.374 | 122.3694 | 122.2366 | 122.2549 | 122.2092 | -122.4609 | -122.374 | 122.2961 | 122.3465 | 59.1156 | 59.0973
580.3125 | 122.644 | -59.2072 | 63.0569 | -0.035324 | 0.0028348 | 0.062948 | 0.060235 | 0.00076902 | -0.00082456 | -0.0015765 | -0.042725 | 0.0029137 | 0.067584 | 0.065411 | -0.0046228 | 0.0081561 | -0.0011728 | -0.07782 | 62.9745 | -59.317 | 63.1485 | -59.1019 | -59.4864 | -59.4452 | -0.064087 | 62.9654 | -59.2392 | 63.1714 | -59.2072 | -59.3308 | -59.2117 | -0.10986 | -0.082398 | 0.091553 | 0.10528 | -0.23804 | -0.27924 | -0.12817 | -0.16937 | -0.032044 | -0.091553 | 0.11444 | 0 | -0.004578 | -0.1236 | 0.027466 | -0.091553 | 0.21515 | 122.4655 | 0.032044 | 122.4106 | 122.2916 | 122.2046 | 122.1817 | 122.1725 | -122.374 | -122.2961 | 122.3557 | 122.3785 | 59.1293 | 59.1431
581.3125 | 122.6212 | -59.198 | 63.0661 | 0.03334 | 0.0043302 | 0.064016 | 0.05874 | -8.538e-05 | -0.0014654 | -0.0020039 | 0.0030517 | 0.0016321 | 0.068438 | 0.066693 | -0.0046228 | 0.0094379 | -0.0011728 | 0.032043 | 62.9883 | -59.2712 | 63.1943 | -59.0561 | -59.4452 | -59.4086 | -0.022888 | 62.9517 | -59.2438 | 63.1851 | -59.1934 | -59.3216 | -59.2163 | -0.073242 | -0.07782 | 0.12817 | 0.14191 | -0.21057 | -0.24719 | -0.13733 | -0.17395 | -0.045776 | -0.11444 | 0.11902 | 0.004578 | -0.018311 | -0.1236 | 0.027465 | -0.07782 | 0.21515 | 122.4655 | 0.050354 | 122.4289 | 122.2595 | 122.1954 | 122.1863 | 122.1497 | -122.3373 | -122.3099 | 122.3923 | 122.3831 | 59.23 | 59.1751
582.3125 | 122.6715 | -59.198 | 63.0936 | -0.042954 | 0.0017666 | 0.063376 | 0.059808 | -0.00029898 | -0.0027472 | 0.00055974 | 0.033569 | 0.00099115 | 0.068438 | 0.056226 | -0.0046228 | 0.0090105 | 0.000109 | -0.009155 | 63.0112 | -59.2804 | 63.1805 | -59.0378 | -59.4086 | -59.3994 | 0.041199 | 62.9562 | -59.1843 | 63.1943 | -59.1614 | -59.2667 | -59.1888 | -0.082398 | -0.082398 | 0.086975 | 0.16022 | -0.20142 | -0.21057 | -0.11902 | -0.12817 | 0.013733 | -0.13733 | 0.10071 | 0.036621 | 0.009155 | -0.068665 | -0.004578 | -0.082398 | 0.24262 | 122.4609 | 0.022888 | 122.3785 | 122.2916 | 122.1405 | 122.2092 | 122.1542 | -122.374 | -122.2778 | 122.3785 | 122.3923 | 59.1888 | 59.2392
583.3125 | 122.6257 | -59.2072 | 63.0432 | -0.042954 | 0.0024076 | 0.061453 | 0.060449 | -0.0011536 | -0.0014654 | -0.00072206 | -0.033569 | 0.0020593 | 0.065661 | 0.060712 | -0.0046228 | 0.0075153 | -0.0054452 | -0.07782 | 62.9883 | -59.3216 | 63.1485 | -59.1064 | -59.5047 | -59.4406 | -0.054932 | 62.9471 | -59.23 | 63.1897 | -59.2117 | -59.3262 | -59.2209 | -0.11444 | -0.054932 | 0.10529 | 0.10071 | -0.23346 | -0.29755 | -0.11902 | -0.18311 | -0.022889 | -0.09613 | 0.14648 | -0.004578 | -0.013733 | -0.11902 | 0.009156 | -0.09613 | 0.21515 | 122.4701 | 0.018311 | 122.4197 | 122.3099 | 122.1771 | 122.1954 | 122.1542 | -122.3648 | -122.2733 | 122.3557 | 122.3969 | 59.1293 | 59.1522
584.3125 | 122.6303 | -59.2026 | 63.0661 | -0.29472 | 0.0019802 | 0.064657 | 0.060022 | 0.0029052 | -0.0018928 | -0.00050846 | -0.021362 | 0.0035547 | 0.068225 | 0.065198 | -0.0061182 | 0.0058063 | -0.0045908 | 0.004578 | 62.9471 | -59.2896 | 63.1897 | -59.0515 | -59.4269 | -59.3994 | -0.004578 | 62.9471 | -59.2484 | 63.1943 | -59.2072 | -59.3216 | -59.2438 | -0.086975 | -0.11902 | 0.1236 | 0.15106 | -0.19684 | -0.2243 | -0.10986 | -0.13733 | -0.045776 | -0.11902 | 0.12817 | -0.004577 | -0.041198 | -0.11902 | 0.004578 | -0.073242 | 0.23804 | 122.4792 | 0.041199 | 122.4426 | 122.2366 | 122.1954 | 122.1497 | 122.1497 | -122.3557 | -122.3145 | 122.3923 | 122.3969 | 59.2072 | 59.198
585.3125 | 122.6578 | -59.2163 | 63.0753 | -0.058212 | 0.0011258 | 0.065725 | 0.061731 | -0.0024354 | -0.0025336 | 0.00013254 | -0.05188 | 0.0016321 | 0.068011 | 0.063275 | -0.006759 | 0.010506 | -0.0043772 | -0.09613 | 63.0157 | -59.3124 | 63.1393 | -59.1064 | -59.5093 | -59.4635 | -0.050354 | 62.9608 | -59.2484 | 63.176 | -59.2163 | -59.3124 | -59.2117 | -0.09613 | -0.059509 | 0.064087 | 0.10986 | -0.24719 | -0.29297 | -0.15106 | -0.19684 | -0.032043 | -0.11444 | 0.10071 | 0 | 0.004578 | -0.09613 | 0.036621 | -0.064087 | 0.20599 | 122.4518 | 0.032043 | 122.4243 | 122.3282 | 122.2092 | 122.2321 | 122.1771 | -122.3877 | -122.3236 | 122.3557 | 122.3923 | 59.1202 | 59.166
586.3125 | 122.6532 | -59.2438 | 63.0707 | -0.042954 | 0.0026212 | 0.063162 | 0.060449 | -0.00093998 | -0.0029608 | -0.0015765 | -0.054932 | 0.0018457 | 0.065875 | 0.063916 | -0.0044092 | 0.0092241 | -0.0013864 | -0.086975 | 62.9883 | -59.3353 | 63.121 | -59.0927 | -59.4955 | -59.4727 | -0.050354 | 62.9562 | -59.2346 | 63.1851 | -59.2209 | -59.3445 | -59.2072 | -0.091553 | -0.082398 | 0.050354 | 0.15106 | -0.22888 | -0.25177 | -0.13733 | -0.16022 | 0.009155 | -0.11444 | 0.11444 | 0.022888 | 0.036621 | -0.10071 | 0.027466 | -0.10986 | 0.24262 | 122.4564 | 0.013733 | 122.4197 | 122.3236 | 122.1909 | 122.2321 | 122.2 | -122.406 | -122.3053 | 122.3648 | 122.4289 | 59.1568 | 59.1934
587.3125 | 122.58 | -59.2163 | 63.0844 | -0.027695 | 0.003262 | 0.06423 | 0.05639 | -0.0030762 | -0.0027472 | -0.0030719 | 0.021362 | 0.00013675 | 0.066943 | 0.059003 | -0.00505 | 0.0081561 | -0.0026682 | -0.059509 | 63.0112 | -59.2758 | 63.1348 | -59.0927 | -59.4727 | -59.4543 | -0.059509 | 62.9562 | -59.23 | 63.1439 | -59.2163 | -59.3445 | -59.2484 | -0.059509 | -0.073243 | 0.050354 | 0.1236 | -0.23804 | -0.25635 | -0.17853 | -0.19684 | -0.013733 | -0.12817 | 0.059509 | 0 | -0.032043 | -0.12817 | -0.01831 | -0.11444 | 0.18311 | 122.4106 | 0.013733 | 122.374 | 122.287 | 122.1863 | 122.2275 | 122.1725 | -122.3602 | -122.3145 | 122.3511 | 122.3602 | 59.1568 | 59.1568
588.3125 | 122.6578 | -59.1888 | 63.0798 | -0.081101 | 0.0017666 | 0.065298 | 0.060022 | 0.0056824 | 0.0013116 | 0.0018413 | -0.0030517 | 0.0039819 | 0.06438 | 0.055157 | -0.0052638 | 0.0070879 | -0.0001046 | -0.050354 | 62.9837 | -59.3124 | 63.2355 | -58.8364 | -59.3308 | -59.4498 | 0.009155 | 62.9608 | -59.2163 | 63.208 | -59.1705 | -59.3308 | -59.2117 | -0.1236 | -0.09613 | 0.15564 | 0.35248 | -0.26093 | -0.14191 | -0.13733 | -0.018311 | -0.027466 | -0.11902 | 0.12817 | 0.018311 | -0.022888 | -0.14191 | 0.004578 | -0.11444 | 0.47607 | 122.5479 | 0.045777 | 122.4243 | 122.2961 | 122.1771 | 122.1725 | 122.1497 | -122.3923 | -122.2961 | 122.4243 | 122.3969 | 59.1385 | 59.198
589.3125 | 122.6257 | -59.2072 | 63.0936 | -0.096359 | 0.0028348 | 0.064657 | 0.060876 | 0.002478 | 0.00067084 | 0.0012005 | -0.0030517 | 0.0027001 | 0.066729 | 0.066693 | -0.0044092 | 0.0092241 | -0.0024546 | -0.041199 | 62.9745 | -59.285 | 63.1943 | -59.0378 | -59.4452 | -59.4223 | -0.004578 | 62.9425 | -59.2117 | 63.1943 | -59.2026 | -59.317 | -59.2484 | -0.07782 | -0.11902 | 0.10071 | 0.16937 | -0.21515 | -0.23804 | -0.13733 | -0.16022 | -0.004578 | -0.15106 | 0.10071 | 0.004577 | -0.041199 | -0.10986 | -0.036621 | -0.10529 | 0.24719 | 122.4792 | 0.009155 | 122.406 | 122.2595 | 122.1542 | 122.1817 | 122.1497 | -122.3785 | -122.3053 | 122.4014 | 122.4014 | 59.166 | 59.2026
590.3125 | 122.6257 | -59.23 | 63.0432 | -0.11162 | 0.0041166 | 0.06423 | 0.060235 | -8.538e-05 | -0.0029608 | -0.0015765 | 0.0030517 | 0.00035035 | 0.064593 | 0.062207 | -0.0061182 | 0.0075153 | 0.0005362 | -0.032043 | 62.9974 | -59.285 | 63.1943 | -59.0469 | -59.4498 | -59.3948 | 0 | 62.9425 | -59.2209 | 63.1851 | -59.2026 | -59.317 | -59.2163 | -0.054931 | -0.045776 | 0.15106 | 0.18311 | -0.16479 | -0.21973 | -0.10986 | -0.16479 | 0.009156 | -0.10071 | 0.14191 | 0.027466 | 0.013733 | -0.086975 | 0.004577 | -0.096131 | 0.23804 | 122.4792 | 0.01831 | 122.406 | 122.2824 | 122.1634 | 122.2275 | 122.1725 | -122.3282 | -122.2641 | 122.4243 | 122.4152 | 59.198 | 59.23
591.3125 | 122.6349 | -59.2209 | 63.0798 | -0.050583 | 0.0030484 | 0.064871 | 0.059808 | -0.0039306 | -0.003388 | -0.0022175 | -0.0030517 | 0.0031273 | 0.068225 | 0.062634 | -0.0061182 | 0.0066607 | 0.0009634 | -0.036621 | 62.9791 | -59.285 | 63.176 | -59.0469 | -59.4498 | -59.4223 | 0.004578 | 62.9608 | -59.2255 | 63.1851 | -59.2072 | -59.317 | -59.2392 | -0.064087 | -0.10071 | 0.09613 | 0.17395 | -0.20142 | -0.22888 | -0.13733 | -0.16479 | -0.004578 | -0.11902 | 0.10529 | 0.013733 | -0.018311 | -0.096131 | -0.013733 | -0.091553 | 0.23804 | 122.4609 | 0.018311 | 122.4106 | 122.2641 | 122.1863 | 122.2 | 122.1817 | -122.3648 | -122.3053 | 122.3969 | 122.406 | 59.1843 | 59.2255
592.3125 | 122.6486 | -59.2163 | 63.089 | -0.11162 | 0.0024076 | 0.062735 | 0.062158 | -0.00029898 | -0.0016792 | -0.00029486 | -0.039673 | 0.0016321 | 0.065875 | 0.05943 | -0.006759 | 0.0060199 | -0.0030954 | -0.032043 | 62.9791 | -59.3079 | 63.1714 | -59.0652 | -59.4635 | -59.4223 | -0.013733 | 62.9379 | -59.2392 | 63.2446 | -59.2712 | -59.3445 | -59.2209 | -0.091552 | -0.10986 | 0.082398 | 0.15106 | -0.20599 | -0.24719 | -0.11444 | -0.15564 | -0.022888 | -0.15106 | 0.15564 | -0.054931 | -0.004577 | -0.12817 | 0.018311 | -0.10529 | 0.24261 | 122.4792 | -0.032043 | 122.4838 | 122.287 | 122.1771 | 122.1954 | 122.1542 | -122.3969 | -122.3282 | 122.3877 | 122.4609 | 59.1843 | 59.2026
593.3125 | 122.5571 | -59.2026 | 63.0844 | 0.0028229 | 0.0017666 | 0.064657 | 0.063226 | 0.00012822 | -0.0025336 | -0.00093566 | -0.054932 | 0.0016321 | 0.065448 | 0.064984 | -0.003982 | 0.0098651 | -0.0003182 | -0.10071 | 63.0249 | -59.3262 | 63.1073 | -59.1614 | -59.5551 | -59.5093 | -0.10071 | 62.97 | -59.2392 | 63.1302 | -59.2712 | -59.3903 | -59.2896 | -0.1236 | -0.05951 | 0.022888 | 0.041199 | -0.3067 | -0.35248 | -0.1831 | -0.22888 | -0.036621 | -0.11444 | 0.045776 | -0.068664 | -0.086975 | -0.18768 | -0.050354 | -0.15106 | 0.16479 | 122.4335 | -0.032043 | 122.3694 | 122.3511 | 122.2092 | 122.2275 | 122.1725 | -122.4106 | -122.3236 | 122.3099 | 122.3328 | 59.1019 | 59.1019
594.3125 | 122.644 | -59.198 | 63.0844 | -0.073471 | 0.0028348 | 0.064871 | 0.060235 | -0.0024354 | -0.0029608 | 0.00013254 | -0.030517 | 0.0016321 | 0.065875 | 0.058148 | -0.0046228 | 0.0090105 | -0.0065134 | -0.036621 | 62.9654 | -59.3216 | 63.1851 | -59.0469 | -59.4269 | -59.404 | 0.004578 | 62.9517 | -59.2392 | 63.1943 | -59.2072 | -59.3216 | -59.2209 | -0.1236 | -0.11902 | 0.10071 | 0.15106 | -0.20599 | -0.22888 | -0.082398 | -0.10529 | -0.041199 | -0.13275 | 0.10986 | -0.009155 | -0.022888 | -0.1236 | 0.018311 | -0.082397 | 0.27466 | 122.5067 | 0.032044 | 122.4335 | 122.287 | 122.1909 | 122.1634 | 122.1497 | -122.406 | -122.3236 | 122.3831 | 122.3923 | 59.1614 | 59.2026
595.3125 | 122.6486 | -59.2163 | 63.0798 | -0.042954 | 0.0039028 | 0.065725 | 0.059595 | 0.00098262 | -0.0021064 | -0.0015765 | -0.033569 | 0.0012047 | 0.066729 | 0.062207 | -0.0041956 | 0.0087969 | -0.003309 | -0.09613 | 62.9562 | -59.2987 | 63.1668 | -59.0698 | -59.4498 | -59.4131 | 0 | 62.9471 | -59.2163 | 63.1943 | -59.1934 | -59.3079 | -59.2117 | -0.082397 | -0.1236 | 0.086975 | 0.14649 | -0.19684 | -0.23346 | -0.11444 | -0.15106 | 0 | -0.13275 | 0.11444 | 0.022889 | 0.004578 | -0.091552 | 0.004578 | -0.091552 | 0.22888 | 122.4655 | 0.022889 | 122.4106 | 122.2549 | 122.1634 | 122.1725 | 122.1634 | -122.3785 | -122.2961 | 122.3831 | 122.4106 | 59.1202 | 59.2163
596.3125 | 122.612 | -59.2072 | 63.089 | -0.096359 | 0.0026212 | 0.064016 | 0.058526 | 0.002478 | -0.0010382 | -0.0020039 | -0.024414 | 0.0018457 | 0.063525 | 0.05943 | -0.0041956 | 0.0085833 | 0.000109 | -0.041199 | 62.9745 | -59.285 | 63.176 | -59.0469 | -59.4452 | -59.4131 | -0.004578 | 62.9745 | -59.2255 | 63.1714 | -59.2026 | -59.3353 | -59.2392 | -0.07782 | -0.11444 | 0.086975 | 0.16022 | -0.20599 | -0.23804 | -0.12817 | -0.16022 | -0.018311 | -0.11444 | 0.082398 | 0.004577 | -0.032044 | -0.12817 | -0.013733 | -0.10986 | 0.23804 | 122.4609 | 0.022888 | 122.3969 | 122.2595 | 122.2 | 122.1817 | 122.1817 | -122.374 | -122.3145 | 122.3831 | 122.3785 | 59.166 | 59.2026
597.3125 | 122.6349 | -59.2163 | 63.121 | -0.058212 | 0.001553 | 0.060599 | 0.058099 | -0.00029898 | -0.003388 | 0.0012005 | 0.027466 | 0.00013675 | 0.066729 | 0.060071 | -0.0037684 | 0.0075153 | -0.0013864 | -0.032043 | 63.0157 | -59.2804 | 63.1714 | -59.0744 | -59.4177 | -59.404 | 0.027466 | 62.9791 | -59.2209 | 63.176 | -59.1843 | -59.2941 | -59.2117 | -0.064087 | -0.10529 | 0.050354 | 0.14191 | -0.18768 | -0.20142 | -0.1236 | -0.13733 | -0.004577 | -0.14191 | 0.054931 | 0.032044 | 0.004578 | -0.077819 | 0.009155 | -0.073242 | 0.20599 | 122.4518 | 0.036621 | 122.3969 | 122.2961 | 122.2 | 122.2321 | 122.1954 | -122.4014 | -122.3419 | 122.3877 | 122.3923 | 59.1843 | 59.2438
598.3125 | 122.6349 | -59.2117 | 63.0753 | -0.081101 | 0.0024076 | 0.063376 | 0.061303 | 0.0026916 | -0.0031744 | -0.00029486 | 0.0061035 | 0.00099115 | 0.064593 | 0.061566 | -0.0052638 | 0.010079 | -0.0020272 | -0.027466 | 62.97 | -59.3033 | 63.1714 | -59.0652 | -59.5413 | -59.6008 | 0.14191 | 62.9837 | -59.2117 | 63.1943 | -59.1888 | -59.3079 | -59.2072 | -0.091553 | -0.10529 | 0.096131 | 0.14648 | -0.3891 | -0.32959 | -0.29755 | -0.23804 | 0 | -0.091552 | 0.11902 | 0.022888 | 0.004578 | -0.09613 | 0.004578 | -0.09613 | 0.23804 | 122.4747 | 0.022888 | 122.406 | 122.2733 | 122.1954 | 122.1817 | 122.1954 | -122.3785 | -122.287 | 122.3831 | 122.406 | 59.1843 | 59.3536
599.3125 | 122.6303 | -59.198 | 63.0753 | -0.035324 | 0.003262 | 0.065298 | 0.059595 | 0.0014098 | -0.00018376 | -0.0030719 | -0.085449 | 0.00013675 | 0.066516 | 0.057721 | -0.0074 | 0.0083697 | -0.0054452 | -0.036621 | 62.9837 | -59.3308 | 63.1622 | -59.0652 | -59.4406 | -59.4269 | -0.013733 | 62.9654 | -59.2163 | 63.2217 | -59.2484 | -59.3399 | -59.2026 | -0.13275 | -0.091552 | 0.086975 | 0.13275 | -0.22888 | -0.24262 | -0.09613 | -0.10986 | -0.018311 | -0.10986 | 0.14648 | -0.050354 | -0.004578 | -0.14191 | 0.013733 | -0.1236 | 0.2655 | 122.493 | -0.032043 | 122.4381 | 122.3145 | 122.1817 | 122.1817 | 122.1634 | -122.406 | -122.2916 | 122.3602 | 122.4197 | 59.1614 | 59.1843
600.3125 | 122.6303 | -59.2346 | 63.0615 | -0.027695 | 0.0013394 | 0.063803 | 0.061517 | -0.002008 | -0.0029608 | -8.1264e-05 | -0.061035 | 0.0014185 | 0.064807 | 0.060925 | -0.0048364 | 0.0098651 | -0.0016 | -0.059509 | 62.9929 | -59.3216 | 63.1668 | -59.0927 | -59.5001 | -59.4269 | -0.041199 | 62.9517 | -59.2209 | 63.1897 | -59.2026 | -59.4269 | -59.3719 | -0.086975 | -0.068664 | 0.10529 | 0.14191 | -0.19226 | -0.2655 | -0.10529 | -0.17853 | 0.013733 | -0.10986 | 0.12817 | 0.032043 | -0.13733 | -0.19226 | -0.15106 | -0.20599 | 0.22888 | 122.4884 | 0.01831 | 122.4106 | 122.3145 | 122.1725 | 122.2275 | 122.1863 | -122.3831 | -122.2824 | 122.4014 | 122.4243 | 59.1751 | 59.1934
601.3125 | 122.6486 | -59.2026 | 63.0661 | -0.25658 | 0.0036892 | 0.062094 | 0.059381 | 0.0026916 | -0.0016792 | 0.0012005 | -0.027466 | -7.6854e-05 | 0.065661 | 0.066266 | -0.006759 | 0.0087969 | -0.0026682 | 0.14191 | 62.9837 | -59.285 | 63.1851 | -59.0332 | -59.4223 | -59.404 | -0.004578 | 62.9471 | -59.2438 | 63.1989 | -59.1934 | -59.3399 | -59.2255 | -0.082397 | -0.082397 | 0.11902 | 0.16937 | -0.20142 | -0.21973 | -0.11902 | -0.13733 | -0.041198 | -0.11902 | 0.13275 | 0.009156 | -0.022888 | -0.13733 | 0.01831 | -0.096131 | 0.25177 | 122.4701 | 0.050354 | 122.4426 | 122.2687 | 122.1909 | 122.1863 | 122.1497 | -122.3511 | -122.3099 | 122.3877 | 122.4014 | 59.3445 | 59.198
602.3125 | 122.5662 | -59.2072 | 63.089 | -0.042954 | 0.003262 | 0.063589 | 0.059167 | -0.0024354 | -0.0048834 | -0.0026447 | 0.012207 | -7.6854e-05 | 0.067584 | 0.063702 | -0.0041956 | 0.0085833 | 0.0009634 | -0.059509 | 62.9883 | -59.2896 | 63.1439 | -59.0744 | -59.491 | -59.4452 | -0.054932 | 62.9654 | -59.23 | 63.1439 | -59.2346 | -59.3353 | -59.23 | -0.082398 | -0.10071 | 0.054932 | 0.13275 | -0.23804 | -0.28381 | -0.15564 | -0.20142 | -0.022889 | -0.1236 | 0.054932 | -0.027466 | -0.022889 | -0.12817 | 0 | -0.10529 | 0.21515 | 122.4335 | -0.004577 | 122.374 | 122.2778 | 122.1954 | 122.1954 | 122.1725 | -122.3785 | -122.319 | 122.3511 | 122.3511 | 59.1476 | 59.1522
603.3125 | 122.6257 | -59.2026 | 63.0753 | -0.096359 | 0.0019802 | 0.063376 | 0.060022 | -0.00093998 | -0.0012518 | 0.00013254 | -0.012207 | 0.00077755 | 0.06737 | 0.065198 | -0.0041956 | 0.010079 | -0.0048044 | -0.036621 | 62.9745 | -59.2941 | 63.1851 | -59.0424 | -59.4589 | -59.4223 | -0.009155 | 62.9608 | -59.23 | 63.1943 | -59.2026 | -59.3033 | -59.2072 | -0.091552 | -0.10071 | 0.10986 | 0.16022 | -0.21973 | -0.25635 | -0.12817 | -0.16479 | -0.027466 | -0.11444 | 0.11902 | 0 | -0.004577 | -0.10071 | 0.022889 | -0.073242 | 0.25177 | 122.4792 | 0.027466 | 122.4243 | 122.2687 | 122.1909 | 122.1771 | 122.1634 | -122.3694 | -122.3053 | 122.3877 | 122.3969 | 59.166 | 59.1934
604.3125 | 122.644 | -59.2117 | 63.0798 | -0.11162 | 0.0028348 | 0.064444 | 0.060876 | -0.00093998 | -0.0012518 | -0.0026447 | -0.036621 | 0.0020593 | 0.064807 | 0.067975 | -0.0035548 | 0.0083697 | -0.0018136 | -0.022888 | 62.9608 | -59.2941 | 63.176 | -59.0515 | -59.4498 | -59.4086 | -0.018311 | 62.9379 | -59.2072 | 63.1989 | -59.2026 | -59.3216 | -59.2255 | -0.082397 | -0.11902 | 0.09613 | 0.16022 | -0.19684 | -0.23804 | -0.11444 | -0.15564 | 0.004578 | -0.14191 | 0.11902 | 0.009155 | -0.013733 | -0.10986 | -0.018311 | -0.11444 | 0.24261 | 122.4701 | 0.004577 | 122.406 | 122.2549 | 122.1451 | 122.1725 | 122.1497 | -122.374 | -122.287 | 122.3877 | 122.4106 | 59.1888 | 59.1934
605.3125 | 122.6395 | -59.2209 | 63.0661 | -0.073471 | 0.0019802 | 0.062948 | 0.060235 | -0.0045716 | -0.0029608 | 0.0031231 | -0.07019 | 0.0027001 | 0.066516 | 0.056653 | -0.0052638 | 0.01072 | -0.000532 | -0.082397 | 63.0066 | -59.3262 | 63.1302 | -59.0836 | -59.491 | -59.4681 | -0.045776 | 62.9745 | -59.2484 | 63.1897 | -59.2163 | -59.3308 | -59.2026 | -0.10529 | -0.059509 | 0.064087 | 0.13733 | -0.24719 | -0.27008 | -0.14191 | -0.16479 | -0.027466 | -0.091553 | 0.1236 | 0.004577 | 0.01831 | -0.10986 | 0.045776 | -0.082398 | 0.24262 | 122.4564 | 0.032043 | 122.438 | 122.3328 | 122.2229 | 122.2275 | 122.1954 | -122.3923 | -122.3145 | 122.3511 | 122.4106 | 59.1385 | 59.1751
606.3125 | 122.6395 | -59.23 | 63.0753 | -0.042954 | 0.0026212 | 0.064016 | 0.061731 | -8.538e-05 | -0.0044562 | -0.0017903 | -0.076294 | 0.0046227 | 0.066089 | 0.063702 | -0.0031274 | 0.0092241 | 0.0007498 | -0.10071 | 63.0249 | -59.3399 | 63.1256 | -59.1385 | -59.5184 | -59.4818 | -0.086975 | 62.9562 | -59.23 | 63.1714 | -59.2255 | -59.3536 | -59.2346 | -0.10986 | -0.050354 | 0.050354 | 0.091553 | -0.25177 | -0.28839 | -0.14191 | -0.17853 | 0 | -0.11902 | 0.096131 | 0.004578 | -0.004577 | -0.1236 | -0.004577 | -0.1236 | 0.20142 | 122.4655 | 0.004578 | 122.4014 | 122.3648 | 122.1863 | 122.2549 | 122.1863 | -122.4152 | -122.3053 | 122.3557 | 122.4014 | 59.1293 | 59.1431
607.3125 | 122.5754 | -59.2026 | 63.089 | -0.042954 | 0.003262 | 0.064657 | 0.060449 | -0.00093998 | -0.0027472 | -0.0026447 | -0.07019 | 0.00077755 | 0.066943 | 0.056866 | -0.0048364 | 0.0066607 | -0.0001046 | -0.059509 | 63.002 | -59.2804 | 63.121 | -59.0607 | -59.1431 | -59.3124 | -0.036621 | 62.9791 | -59.2392 | 63.1439 | -59.2392 | -59.3628 | -59.2667 | -0.07782 | -0.086975 | 0.032044 | 0.14191 | -0.10986 | 0.05951 | -0.032043 | 0.13733 | -0.036621 | -0.10986 | 0.054932 | -0.036621 | -0.064087 | -0.16022 | -0.027466 | -0.1236 | 0.21973 | 122.4014 | 0 | 122.3831 | 122.2824 | 122.2183 | 122.2046 | 122.1817 | -122.3694 | -122.3282 | 122.3236 | 122.3465 | 59.1431 | 59.166
608.3125 | 122.5754 | -59.2484 | 63.0753 | -0.065842 | 0.001553 | 0.063589 | 0.064081 | -0.0013672 | -0.0021064 | -0.0024311 | -0.079346 | 0.0016321 | 0.065448 | 0.065411 | -0.00505 | 0.0092241 | 0.0022452 | -0.09613 | 63.0203 | -59.3399 | 63.0753 | -59.1797 | -59.5551 | -59.5139 | -0.11444 | 63.0066 | -59.2346 | 63.1119 | -59.2804 | -59.4177 | -59.285 | -0.091553 | -0.054931 | 0 | 0.068665 | -0.2655 | -0.3067 | -0.17395 | -0.21515 | 0.013733 | -0.068664 | 0.036621 | -0.032044 | -0.036621 | -0.16937 | -0.050354 | -0.18311 | 0.16022 | 122.4152 | -0.045777 | 122.3465 | 122.3602 | 122.2412 | 122.2687 | 122.2549 | -122.4152 | -122.3099 | 122.3236 | 122.3602 | 59.1522 | 59.1339
609.3125 | 122.6578 | -59.198 | 63.0661 | -0.065842 | 0.0058256 | 0.063589 | 0.060876 | 0.0016236 | -0.0025336 | 0.0014141 | -0.054932 | 0.0029137 | 0.064166 | 0.063061 | -0.0044092 | 0.0090105 | -0.0013864 | -0.018311 | 62.9791 | -59.3308 | 63.3224 | -59.0561 | -59.5093 | -59.4223 | -0.004578 | 62.9333 | -59.2209 | 63.2034 | -59.1934 | -59.3033 | -59.1843 | -0.13275 | -0.086975 | 0.25635 | 0.14191 | -0.2243 | -0.31128 | -0.091552 | -0.17853 | -0.022888 | -0.13275 | 0.13733 | 0.004578 | 0.013733 | -0.10529 | 0.036621 | -0.082398 | 0.27466 | 122.6532 | 0.027466 | 122.4243 | 122.3099 | 122.1542 | 122.1771 | 122.1313 | -122.3969 | -122.287 | 122.5204 | 122.4014 | 59.1797 | 59.1934
610.3125 | 122.6578 | -59.2117 | 63.0661 | -0.050583 | 0.0041166 | 0.065298 | 0.058313 | -0.00072638 | 0.00045724 | -8.1264e-05 | -0.030517 | 0.0029137 | 0.068652 | 0.055585 | -0.005691 | 0.0087969 | -0.0056588 | -0.045776 | 62.9608 | -59.2941 | 63.1714 | -59.0561 | -59.4681 | -59.4315 | -0.16937 | 62.8876 | -59.2667 | 63.1805 | -59.1476 | -59.3353 | -59.1934 | -0.082397 | -0.10529 | 0.10529 | 0.15564 | -0.21973 | -0.25635 | -0.13733 | -0.17395 | -0.054932 | -0.17853 | 0.11444 | 0.064087 | 0.018311 | -0.1236 | 0.073243 | -0.068664 | 0.23804 | 122.4655 | 0.11902 | 122.4472 | 122.2549 | 122.1542 | 122.1725 | 122.0993 | -122.3602 | -122.3328 | 122.3831 | 122.3923 | 59.166 | 59.0424
611.3125 | 122.612 | -59.2209 | 63.0112 | -0.10399 | 0.0036892 | 0.063803 | 0.061731 | 0.0020508 | -0.0031744 | -0.00029486 | -0.045776 | 0.0033411 | 0.064593 | 0.062634 | -0.0048364 | 0.0098651 | -0.0020272 | -0.07782 | 62.9929 | -59.3262 | 63.1485 | -59.0836 | -59.4635 | -59.4452 | -0.041199 | 62.9745 | -59.2255 | 63.1943 | -59.2026 | -59.3124 | -59.2072 | -0.10529 | -0.01831 | 0.13733 | 0.13733 | -0.2243 | -0.24262 | -0.11902 | -0.13733 | -0.004578 | -0.036621 | 0.18311 | 0.01831 | 0.013733 | -0.091553 | 0.018311 | -0.086975 | 0.24262 | 122.4747 | 0.022888 | 122.4197 | 122.319 | 122.2 | 122.2137 | 122.1954 | -122.3373 | -122.2366 | 122.3694 | 122.4152 | 59.1431 | 59.1797
612.3125 | 122.6257 | -59.2255 | 63.0661 | -0.073471 | 0.0017666 | 0.06423 | 0.059808 | 0.0037598 | -0.0021064 | -0.0032855 | 0.0061035 | -0.0017859 | 0.065875 | 0.062421 | -0.0041956 | 0.0081561 | -0.0026682 | -0.032043 | 62.9883 | -59.285 | 63.327 | -58.9279 | -59.523 | -59.4315 | -0.022888 | 62.9471 | -59.2072 | 63.2034 | -59.2072 | -59.3262 | -59.1797 | -0.059509 | -0.07782 | 0.26092 | 0.29755 | -0.20599 | -0.29755 | -0.14648 | -0.23804 | 0.018311 | -0.11902 | 0.13733 | 0.018311 | 0.045777 | -0.10071 | 0.027466 | -0.11902 | 0.35706 | 122.612 | 0 | 122.4106 | 122.2733 | 122.1542 | 122.2137 | 122.1725 | -122.3511 | -122.2733 | 122.5525 | 122.4289 | 59.1934 | 59.2026
613.3125 | 122.5113 | -59.2667 | 63.089 | -0.065842 | 0.0045438 | 0.06423 | 0.059595 | -0.0024354 | -0.0021064 | -0.0011493 | -0.079346 | 0.0033411 | 0.066943 | 0.065411 | -0.0052638 | 0.0079425 | 0.001818 | -0.086975 | 63.0341 | -59.317 | 63.0478 | -59.2072 | -59.5688 | -59.5459 | -0.15564 | 63.0203 | -59.2712 | 63.0798 | -59.3124 | -59.4543 | -59.3308 | -0.050354 | -0.054931 | -0.041198 | 0.05951 | -0.27923 | -0.30212 | -0.22888 | -0.25177 | -0.004577 | -0.068664 | -0.009155 | -0.045776 | -0.064087 | -0.18768 | -0.05951 | -0.18311 | 0.10986 | 122.3648 | -0.041199 | 122.3511 | 122.3511 | 122.2916 | 122.3007 | 122.287 | -122.406 | -122.3602 | 122.3145 | 122.3465 | 59.1797 | 59.111
614.3125 | 122.525 | -59.2484 | 63.0981 | -0.065842 | 0.0034756 | 0.063803 | 0.059595 | -0.0022218 | -0.0042426 | -0.00072206 | -0.076294 | 0.0035547 | 0.068011 | 0.056653 | -0.0041956 | 0.0092241 | 0.0005362 | 0 | 62.9974 | -59.3628 | 63.0203 | -59.1064 | -59.5642 | -59.5917 | -0.13733 | 63.0066 | -59.2621 | 63.0707 | -59.317 | -59.4406 | -59.3216 | -0.11444 | -0.10071 | -0.07782 | 0.14191 | -0.34332 | -0.31586 | -0.22888 | -0.20142 | -0.013733 | -0.091553 | -0.027466 | -0.068665 | -0.073242 | -0.19226 | -0.059509 | -0.17853 | 0.25635 | 122.3831 | -0.054932 | 122.3328 | 122.3602 | 122.2687 | 122.2458 | 122.2549 | -122.4609 | -122.3602 | 122.2687 | 122.319 | 59.2484 | 59.111
615.3125 | 122.6166 | -59.2072 | 63.0524 | -0.081101 | 0.0030484 | 0.064444 | 0.059808 | -0.00051278 | -0.003388 | -0.0024311 | -0.042725 | 0.0037683 | 0.06737 | 0.056226 | -0.0041956 | 0.0096515 | -0.005018 | -0.10071 | 63.0066 | -59.2987 | 63.0936 | -59.1293 | -59.523 | -59.4772 | -0.068665 | 62.9425 | -59.2529 | 63.176 | -59.2255 | -59.3536 | -59.2255 | -0.091553 | -0.045776 | 0.041199 | 0.07782 | -0.27008 | -0.31586 | -0.17853 | -0.2243 | -0.045777 | -0.10986 | 0.1236 | -0.018311 | -0.018311 | -0.14648 | 0.027466 | -0.10071 | 0.16937 | 122.3923 | 0.027466 | 122.4289 | 122.3053 | 122.1954 | 122.2137 | 122.1497 | -122.3511 | -122.3053 | 122.3007 | 122.3831 | 59.1064 | 59.1385
616.3125 | 122.5891 | -59.23 | 63.0432 | -0.027695 | 0.0009122 | 0.062521 | 0.062799 | -0.00072638 | -0.0027472 | 0.00077334 | -0.039673 | 0.0024865 | 0.067157 | 0.065198 | -0.0044092 | 0.0096515 | -0.0058724 | -0.10529 | 63.0066 | -59.317 | 63.0936 | -59.1476 | -59.5367 | -59.5093 | -0.09613 | 62.9654 | -59.2667 | 63.1531 | -59.2484 | -59.3765 | -59.2529 | -0.086975 | -0.036621 | 0.050354 | 0.082398 | -0.27923 | -0.3067 | -0.19226 | -0.21973 | -0.036621 | -0.07782 | 0.10986 | -0.01831 | -0.022888 | -0.14648 | 0.013733 | -0.10986 | 0.16937 | 122.4106 | 0.018311 | 122.4197 | 122.3236 | 122.2321 | 122.2366 | 122.1954 | -122.3602 | -122.3099 | 122.3236 | 122.3831 | 59.1248 | 59.1339
617.3125 | 122.5662 | -59.2255 | 63.0798 | -0.096359 | 0.0034756 | 0.062308 | 0.058099 | 0.0018372 | -0.0036018 | -0.00029486 | -8.6e-08 | 0.0029137 | 0.067584 | 0.06413 | -0.002273 | 0.0077289 | -0.0016 | -0.050354 | 62.9974 | -59.317 | 63.1577 | -59.0424 | -59.4589 | -59.4177 | -0.022888 | 62.9379 | -59.23 | 63.1714 | -59.2255 | -59.3353 | -59.2484 | -0.091553 | -0.082397 | 0.07782 | 0.18311 | -0.19226 | -0.23346 | -0.10071 | -0.14191 | -0.004578 | -0.14191 | 0.091553 | 0 | -0.022888 | -0.10986 | -0.01831 | -0.10529 | 0.27466 | 122.4747 | 0.004578 | 122.4014 | 122.3145 | 122.168 | 122.2229 | 122.1634 | -122.3969 | -122.3099 | 122.3831 | 122.3969 | 59.1751 | 59.2026
618.3125 | 122.5067 | -59.2529 | 63.089 | -0.096359 | 0.0026212 | 0.065085 | 0.063653 | -0.002008 | -0.0029608 | -0.0026447 | 0.012207 | 0.0031273 | 0.06737 | 0.067334 | -0.0061182 | 0.0098651 | -0.0030954 | -0.09613 | 63.0203 | -59.3491 | 63.0569 | -59.5642 | -59.9167 | -59.3491 | -0.24719 | 63.0249 | -59.2255 | 63.0798 | -59.3582 | -59.4635 | -59.3308 | -0.09613 | -0.068664 | -0.032043 | -0.31128 | -0.09613 | -0.66376 | 0 | -0.56763 | 0.027466 | -0.064087 | -0.009155 | -0.10529 | -0.07782 | -0.21057 | -0.10529 | -0.23804 | -0.21515 | 122.406 | -0.13275 | 122.3053 | 122.3694 | 122.2504 | 122.2733 | 122.2778 | -122.438 | -122.3145 | 122.3099 | 122.3328 | 59.1568 | 59.0057
619.3125 | 122.5342 | -59.2529 | 63.1119 | 0.010452 | 0.0026212 | 0.062094 | 0.061303 | 0.00012822 | -0.0031744 | 0.0016277 | -0.061035 | 0.0012047 | 0.069079 | 0.060498 | -0.00505 | 0.0092241 | -0.0018136 | -0.10529 | 63.0203 | -59.3399 | 63.0524 | -59.1843 | -59.5551 | -59.5459 | -0.14648 | 62.9791 | -59.2575 | 63.0798 | -59.3262 | -59.4406 | -59.2987 | -0.086975 | -0.091552 | -0.059509 | 0.068665 | -0.29297 | -0.30212 | -0.20599 | -0.21515 | -0.004577 | -0.13275 | -0.032043 | -0.073242 | -0.045776 | -0.18768 | -0.041199 | -0.18311 | 0.15564 | 122.3923 | -0.068665 | 122.3373 | 122.3602 | 122.2366 | 122.2733 | 122.2321 | -122.4518 | -122.3694 | 122.3053 | 122.3328 | 59.1476 | 59.1064
620.3125 | 122.5754 | -59.2438 | 63.0386 | -0.065842 | 0.0039028 | 0.063803 | 0.060449 | -0.0017944 | -0.0029608 | -0.00072206 | -0.048828 | 0.00056395 | 0.064593 | 0.063916 | -0.0041956 | 0.0070879 | 0.0033134 | -0.064087 | 63.0203 | -59.3491 | 63.0569 | -59.2117 | -59.5642 | -59.5322 | -0.16022 | 63.0295 | -59.2621 | 63.0478 | -59.3674 | -59.4818 | -59.3536 | -0.10529 | -0.01831 | 0.018311 | 0.032043 | -0.28839 | -0.32043 | -0.18311 | -0.21515 | -0.018311 | -0.009155 | 0.009156 | -0.1236 | -0.10986 | -0.23804 | -0.091553 | -0.21973 | 0.13733 | 122.406 | -0.10529 | 122.3099 | 122.3694 | 122.2916 | 122.2641 | 122.2733 | -122.3877 | -122.3007 | 122.3007 | 122.2916 | 59.1797 | 59.0836
621.3125 | 122.4838 | -59.2529 | 63.121 | -0.012436 | 0.0045438 | 0.064444 | 0.060876 | 0.00076902 | -0.0025336 | 0.00077334 | -0.054932 | 0.0018457 | 0.065875 | 0.064343 | -0.0031274 | 0.011574 | -0.0022408 | -0.064087 | 63.0203 | -59.3353 | 63.0661 | -59.1843 | -59.5642 | -59.5322 | -0.15106 | 62.9974 | -59.2484 | 63.0661 | -59.3308 | -59.4681 | -59.3216 | -0.082397 | -0.10071 | -0.054932 | 0.068665 | -0.27924 | -0.31128 | -0.19684 | -0.22888 | 0.004578 | -0.1236 | -0.054932 | -0.07782 | -0.068664 | -0.21515 | -0.073242 | -0.21973 | 0.15106 | 122.4014 | -0.082398 | 122.3145 | 122.3557 | 122.2458 | 122.2733 | 122.2504 | -122.4564 | -122.3694 | 122.319 | 122.319 | 59.1888 | 59.1019
622.3125 | 122.6349 | -59.23 | 63.0615 | -0.10399 | 0.0017666 | 0.065725 | 0.059595 | 0.0026916 | -0.0018928 | -0.0015765 | -8.6e-08 | 0.0035547 | 0.06737 | 0.054517 | -0.0037684 | 0.0079425 | -0.0001046 | -0.19684 | 62.9791 | -59.317 | 63.1851 | -59.0424 | -59.4406 | -59.404 | -0.013733 | 62.9379 | -59.23 | 63.1851 | -59.1934 | -59.317 | -59.2117 | -0.086975 | -0.082397 | 0.1236 | 0.18768 | -0.17395 | -0.21057 | -0.086975 | -0.1236 | 0 | -0.1236 | 0.1236 | 0.036622 | 0.018311 | -0.086975 | 0.018311 | -0.086975 | 0.27466 | 122.5021 | 0.036622 | 122.4152 | 122.2961 | 122.168 | 122.2092 | 122.168 | -122.3785 | -122.2916 | 122.4152 | 122.4152 | 59.0332 | 59.2163
623.3125 | 122.5021 | -59.2392 | 63.0936 | -0.058212 | 0.0028348 | 0.063376 | 0.061731 | 0.00098262 | -0.0027472 | -8.1264e-05 | -0.14648 | 0.0027001 | 0.065661 | 0.065625 | -0.003982 | 0.0075153 | -0.0003182 | -0.086975 | 63.0295 | -59.3445 | 63.0432 | -59.23 | -59.6054 | -59.5642 | -0.20142 | 62.9517 | -59.2575 | 63.0981 | -59.3628 | -59.4452 | -59.285 | -0.10529 | -0.064087 | -0.050354 | 0.009155 | -0.32501 | -0.36621 | -0.21973 | -0.26093 | -0.01831 | -0.14191 | 0.004578 | -0.1236 | -0.045776 | -0.20599 | -0.027466 | -0.18768 | 0.11444 | 122.3877 | -0.10529 | 122.3557 | 122.374 | 122.2092 | 122.2687 | 122.1909 | -122.438 | -122.3511 | 122.2824 | 122.3373 | 59.1522 | 59.0378
624.3125 | 122.5296 | -59.2392 | 63.1165 | -0.035324 | 0.0017666 | 0.064444 | 0.060022 | -0.0011536 | -0.0048834 | 0.00098694 | -0.039673 | 0.0012047 | 0.065234 | 0.059857 | -0.005691 | 0.010292 | -0.0003182 | -0.10071 | 63.0386 | -59.3216 | 63.0341 | -59.1888 | -59.5688 | -59.523 | -0.14648 | 62.9974 | -59.2804 | 63.0981 | -59.3033 | -59.4406 | -59.2941 | -0.082397 | -0.07782 | -0.082397 | 0.050354 | -0.28381 | -0.32959 | -0.20142 | -0.24719 | -0.041199 | -0.11902 | -0.01831 | -0.064087 | -0.054931 | -0.20142 | -0.013732 | -0.16022 | 0.13275 | 122.3557 | -0.022888 | 122.3785 | 122.3602 | 122.2778 | 122.2778 | 122.2366 | -122.438 | -122.3969 | 122.2733 | 122.3373 | 59.1385 | 59.0927
625.3125 | 122.5479 | -59.2804 | 63.1119 | -0.012436 | 0.0013394 | 0.062948 | 0.062158 | -0.00051278 | -0.00232 | -0.00029486 | -0.057983 | 0.0035547 | 0.066089 | 0.066907 | -0.0027002 | 0.0098651 | -0.0020272 | -0.07782 | 63.0341 | -59.3399 | 63.0569 | -59.1888 | -59.5825 | -59.5551 | -0.1831 | 63.0157 | -59.2621 | 63.0569 | -59.3262 | -59.848 | -59.6466 | -0.059509 | -0.077819 | -0.054931 | 0.091553 | -0.27466 | -0.30212 | -0.21515 | -0.24262 | 0.018311 | -0.09613 | -0.054931 | -0.045776 | -0.36621 | -0.56763 | -0.38452 | -0.58594 | 0.15106 | 122.3969 | -0.064087 | 122.319 | 122.374 | 122.2778 | 122.3145 | 122.2961 | -122.4518 | -122.374 | 122.3373 | 122.3373 | 59.2026 | 59.0973
626.3125 | 122.4976 | -59.2255 | 63.1027 | 0.094376 | 0.0026212 | 0.064444 | 0.059381 | 0.00055542 | -0.003388 | -0.0032855 | -0.061035 | 0.0027001 | 0.06737 | 0.067761 | -0.0048364 | 0.0073015 | -0.0037362 | -0.17395 | 63.0386 | -59.3216 | 63.0524 | -59.2209 | -59.5688 | -59.5276 | -0.15564 | 63.0112 | -59.2392 | 63.0798 | -59.3353 | -59.4543 | -59.3124 | -0.09613 | -0.064087 | -0.050354 | 0.004578 | -0.30212 | -0.34332 | -0.20599 | -0.24719 | -0.013733 | -0.091553 | -0.022888 | -0.10986 | -0.086975 | -0.22888 | -0.073242 | -0.21515 | 0.10071 | 122.374 | -0.09613 | 122.319 | 122.3602 | 122.2504 | 122.2641 | 122.2366 | -122.4243 | -122.3419 | 122.2778 | 122.3053 | 59.0515 | 59.0698
627.3125 | 122.5296 | -59.2438 | 63.1027 | -0.058212 | 0.001553 | 0.065085 | 0.058954 | 0.0020508 | -0.005097 | -0.00072206 | -0.033569 | 0.00099115 | 0.067157 | 0.059216 | -0.0048364 | 0.0075153 | -0.000532 | -0.35706 | 62.9562 | -59.3903 | 63.1073 | -59.1476 | -59.6558 | -59.5322 | -0.16937 | 62.9974 | -59.2804 | 63.0798 | -59.3399 | -59.4589 | -59.3124 | -0.14648 | -0.14648 | 0.004578 | 0.09613 | -0.28839 | -0.41199 | -0.14191 | -0.2655 | -0.036622 | -0.10529 | -0.022888 | -0.096131 | -0.068665 | -0.21515 | -0.032043 | -0.17853 | 0.24262 | 122.4976 | -0.059509 | 122.3602 | 122.3465 | 122.2778 | 122.2 | 122.2412 | -122.493 | -122.3831 | 122.3511 | 122.3236 | 58.8867 | 59.0744
628.3125 | 122.5159 | -59.2438 | 63.1073 | -0.13451 | 0.0036892 | 0.064016 | 0.060876 | 0.0018372 | -0.0038154 | 0.00013254 | -0.061035 | 0.0029137 | 0.067798 | 0.060284 | -0.0059046 | 0.0094379 | -0.0037362 | -0.064087 | 63.0478 | -59.3262 | 63.0707 | -59.1568 | -59.5505 | -59.5184 | -0.10986 | 63.0066 | -59.2072 | 63.0798 | -59.3491 | -59.4772 | -59.3124 | -0.082398 | -0.059509 | -0.036621 | 0.086975 | -0.27466 | -0.3067 | -0.19226 | -0.2243 | 0.036621 | -0.10071 | -0.027466 | -0.10529 | -0.068665 | -0.23346 | -0.10529 | -0.27008 | 0.16937 | 122.3969 | -0.14191 | 122.287 | 122.374 | 122.2137 | 122.2916 | 122.2504 | -122.4335 | -122.3145 | 122.3145 | 122.3236 | 59.1797 | 59.1339
629.3125 | 122.5342 | -59.2529 | 63.1027 | -0.058212 | 0.0024076 | 0.06423 | 0.060663 | 0.0026916 | -0.0018928 | -0.00029486 | -0.07019 | 0.00077755 | 0.070147 | 0.062848 | -0.0031274 | 0.0083697 | -0.0024546 | -0.10529 | 63.0524 | -59.3262 | 63.0249 | -59.198 | -59.6008 | -59.5688 | -0.48523 | 62.9242 | -59.2896 | 63.1165 | -59.3445 | -59.4955 | -59.3124 | -0.073242 | -0.050354 | -0.07782 | 0.054932 | -0.31586 | -0.3479 | -0.24262 | -0.27466 | -0.036621 | -0.17853 | 0.013733 | -0.091552 | -0.059509 | -0.24261 | -0.022888 | -0.20599 | 0.12817 | 122.3511 | -0.054931 | 122.406 | 122.3785 | 122.2137 | 122.3053 | 122.1771 | -122.4289 | -122.3923 | 122.2778 | 122.3694 | 59.1476 | 58.7677
630.3125 | 122.5388 | -59.2529 | 63.0844 | -0.042954 | 0.0026212 | 0.062308 | 0.059167 | -0.00093998 | -0.0036018 | -0.0020039 | -0.0030517 | 0.0018457 | 0.06438 | 0.061566 | -0.0044092 | 0.0092241 | -0.0026682 | -0.09613 | 63.0112 | -59.3308 | 63.0478 | -59.1934 | -59.5505 | -59.5139 | -0.16022 | 62.9929 | -59.2575 | 63.0707 | -59.3079 | -59.4543 | -59.3216 | -0.07782 | -0.073243 | -0.036621 | 0.05951 | -0.26093 | -0.29755 | -0.1831 | -0.21973 | -0.004577 | -0.091553 | -0.013733 | -0.054931 | -0.068664 | -0.20142 | -0.064087 | -0.19684 | 0.13733 | 122.3785 | -0.050354 | 122.3282 | 122.3419 | 122.2504 | 122.2641 | 122.2458 | -122.4152 | -122.3419 | 122.3007 | 122.3236 | 59.1568 | 59.0927
631.3125 | 122.5342 | -59.2529 | 63.0981 | -0.08873 | 0.0045438 | 0.062948 | 0.060876 | -0.0017944 | -0.0055244 | -0.00050846 | -0.024414 | 0.0018457 | 0.069293 | 0.062634 | -0.0018458 | 0.010933 | -0.000532 | -0.09613 | 63.0478 | -59.3262 | 63.0341 | -59.2026 | -59.5688 | -59.5322 | -0.14648 | 62.9929 | -59.2575 | 63.0707 | -59.3353 | -59.4543 | -59.2941 | -0.073242 | -0.050354 | -0.064087 | 0.050354 | -0.27924 | -0.31586 | -0.20599 | -0.24262 | -0.004577 | -0.10529 | -0.027466 | -0.082397 | -0.041198 | -0.20142 | -0.036621 | -0.19684 | 0.1236 | 122.3602 | -0.07782 | 122.3282 | 122.374 | 122.2504 | 122.3007 | 122.2458 | -122.4243 | -122.3557 | 122.287 | 122.3236 | 59.1568 | 59.1064
632.3125 | 122.5113 | -59.2346 | 63.1027 | -0.027695 | 0.0034756 | 0.066794 | 0.05874 | -0.00072638 | -0.0018928 | -0.00029486 | -0.045776 | 0.0035547 | 0.066516 | 0.057507 | -0.0054774 | 0.0083697 | -0.0028818 | -0.3891 | 62.9105 | -59.3674 | 63.1073 | -59.2117 | -59.6283 | -59.523 | -0.16937 | 62.9883 | -59.2484 | 63.0615 | -59.3353 | -59.436 | -59.3124 | -0.13275 | -0.19226 | 0.004578 | 0.022888 | -0.28839 | -0.39368 | -0.15564 | -0.26093 | -0.013733 | -0.11444 | -0.041199 | -0.10071 | -0.07782 | -0.20142 | -0.064087 | -0.18768 | 0.15564 | 122.4747 | -0.086975 | 122.3099 | 122.2778 | 122.2366 | 122.1451 | 122.2229 | -122.4701 | -122.3511 | 122.3419 | 122.2961 | 58.8455 | 59.0652
633.3125 | 122.5479 | -59.2575 | 63.0753 | -0.058212 | 0.001553 | 0.063376 | 0.060449 | -0.0011536 | -0.0021064 | 0.0016277 | -0.012207 | 0.0037683 | 0.067157 | 0.05473 | -0.0054774 | 0.0087969 | -0.0026682 | -0.11444 | 63.0157 | -59.3262 | 63.0615 | -59.1797 | -59.5596 | -59.5276 | -0.13733 | 62.9654 | -59.2392 | 63.1027 | -59.285 | -59.4131 | -59.2896 | -0.068665 | -0.059509 | -0.013733 | 0.07782 | -0.27008 | -0.30212 | -0.20142 | -0.23346 | 0.01831 | -0.10986 | 0.027466 | -0.027466 | -0.032044 | -0.15564 | -0.050354 | -0.17395 | 0.14648 | 122.3877 | -0.045776 | 122.3419 | 122.3419 | 122.2046 | 122.2733 | 122.2229 | -122.4014 | -122.3145 | 122.319 | 122.3602 | 59.1431 | 59.1202
634.3125 | 122.5021 | -59.2621 | 63.1119 | -0.050583 | 0.0034756 | 0.065298 | 0.062585 | -8.538e-05 | -0.0016792 | -0.0013629 | -0.15564 | 0.0031273 | 0.068011 | 0.058575 | -0.003982 | 0.0079425 | 0.0005362 | -0.082397 | 63.0661 | -59.3216 | 63.0295 | -59.23 | -59.5825 | -59.5688 | -0.18768 | 62.9471 | -59.2575 | 63.0936 | -59.3445 | -59.4406 | -59.2758 | -0.059509 | -0.045776 | -0.082397 | 0.032043 | -0.3067 | -0.32044 | -0.24719 | -0.26093 | 0.004578 | -0.16479 | -0.01831 | -0.082397 | -0.013733 | -0.17853 | -0.018311 | -0.18311 | 0.091552 | 122.3511 | -0.086975 | 122.3511 | 122.3877 | 122.2046 | 122.3282 | 122.2092 | -122.4335 | -122.3694 | 122.2916 | 122.3557 | 59.1797 | 59.0744
635.3125 | 122.5296 | -59.2484 | 63.1119 | -0.042954 | 0.0024076 | 0.064871 | 0.061303 | 0.0011962 | -0.0018928 | 0.00077334 | -0.048828 | 0.0024865 | 0.066516 | 0.06712 | -0.0035548 | 0.0092241 | -0.0020272 | -0.041199 | 63.0524 | -59.3216 | 63.0981 | -59.1202 | -59.5184 | -59.5047 | -0.07782 | 63.0112 | -59.2209 | 63.089 | -59.285 | -59.4269 | -59.3033 | -0.073242 | -0.059509 | -0.013732 | 0.12817 | -0.25635 | -0.27008 | -0.18311 | -0.19684 | 0.027466 | -0.10071 | -0.022888 | -0.036621 | -0.054932 | -0.17853 | -0.082398 | -0.20599 | 0.20142 | 122.4197 | -0.064087 | 122.3099 | 122.374 | 122.2321 | 122.3007 | 122.2595 | -122.4335 | -122.3328 | 122.3465 | 122.3373 | 59.2072 | 59.1705
636.3125 | 122.3557 | -59.2758 | 63.0386 | -0.035324 | 0.000485 | 0.067221 | 0.059595 | 0.0031188 | -0.0027472 | -0.0022175 | -0.012207 | 0.0033411 | 0.066089 | 0.064557 | -0.003341 | 0.0096515 | -0.0022408 | -0.059509 | 63.0478 | -59.3124 | 63.0341 | -59.2072 | -59.5596 | -59.5459 | -0.16022 | 63.0295 | -59.2346 | 63.0432 | -59.3491 | -59.4864 | -59.1339 | -0.036621 | 0.009156 | -0.004577 | 0.068665 | -0.27008 | -0.28381 | -0.23346 | -0.24719 | 0.041199 | -0.009155 | 0.004578 | -0.073242 | 0.14191 | -0.21057 | 0.10071 | -0.25177 | 0.10529 | 122.3465 | -0.11444 | 122.2778 | 122.3602 | 122.2641 | 122.3236 | 122.3053 | -122.3511 | -122.2733 | 122.3099 | 122.319 | 59.2163 | 59.1156
637.3125 | 122.612 | -59.2255 | 63.089 | -0.096359 | 0.0011258 | 0.06423 | 0.059595 | -0.0011536 | -0.00232 | -0.00072206 | 0.057983 | 0.0018457 | 0.06737 | 0.06178 | -0.0054774 | 0.0079425 | -0.0003182 | -0.045776 | 62.9837 | -59.2804 | 63.1485 | -59.0469 | -59.4452 | -59.404 | -0.018311 | 62.9471 | -59.2392 | 63.1439 | -59.2392 | -59.3308 | -59.2438 | -0.054932 | -0.10528 | 0.05951 | 0.17853 | -0.17853 | -0.21973 | -0.1236 | -0.16479 | -0.013733 | -0.14191 | 0.054932 | -0.013733 | -0.01831 | -0.10529 | -0.004577 | -0.091553 | 0.23346 | 122.4289 | 0 | 122.3831 | 122.2641 | 122.1863 | 122.2092 | 122.1725 | -122.3694 | -122.3282 | 122.374 | 122.3694 | 59.1797 | 59.2072
638.3125 | 122.4976 | -59.23 | 63.1256 | -0.042954 | 0.0045438 | 0.065512 | 0.059381 | -0.0015808 | -0.0042426 | -8.1264e-05 | -0.045776 | 0.00099115 | 0.066089 | 0.067548 | -0.0071864 | 0.0085833 | -0.0037362 | -0.045776 | 63.0478 | -59.3353 | 63.0936 | -59.1568 | -59.5596 | -59.523 | -0.1236 | 62.9883 | -59.2392 | 63.0707 | -59.3216 | -59.4681 | -59.317 | -0.10529 | -0.077819 | -0.032043 | 0.073243 | -0.29297 | -0.32959 | -0.18768 | -0.2243 | -0.009155 | -0.13733 | -0.054931 | -0.091552 | -0.086975 | -0.23804 | -0.07782 | -0.22888 | 0.17853 | 122.4289 | -0.082397 | 122.3099 | 122.3831 | 122.2275 | 122.2778 | 122.2183 | -122.4609 | -122.3648 | 122.3236 | 122.3007 | 59.1843 | 59.1064
639.3125 | 122.5113 | -59.2529 | 63.1302 | -0.050583 | 0.0017666 | 0.064657 | 0.059808 | 0.0011962 | -0.0016792 | 0.00034614 | 0.11597 | 0.0022729 | 0.067157 | 0.062207 | -0.0063318 | 0.0087969 | -0.0039498 | -0.09613 | 63.0341 | -59.3399 | 63.0203 | -59.166 | -60.1227 | -59.7519 | -0.18768 | 63.0249 | -59.2438 | 63.0844 | -59.3308 | -59.4635 | -59.3353 | -0.086975 | -0.09613 | -0.10986 | 0.086975 | -0.49896 | -0.86975 | -0.41199 | -0.78278 | 0.009156 | -0.10529 | -0.045776 | -0.07782 | -0.082397 | -0.21057 | -0.091553 | -0.21973 | 0.17395 | 122.3602 | -0.086976 | 122.3282 | 122.374 | 122.2687 | 122.287 | 122.2778 | -122.4701 | -122.374 | 122.2733 | 122.3373 | 59.1568 | 59.0652
640.3125 | 122.4976 | -59.2346 | 63.1119 | -0.096359 | 0.0034756 | 0.064016 | 0.061303 | -0.00029898 | -0.0021064 | -0.0022175 | -0.042725 | 0.00077755 | 0.067584 | 0.065625 | -0.0052638 | 0.010506 | -0.0003182 | -0.045776 | 63.0569 | -59.2987 | 63.0844 | -59.1339 | -59.5139 | -59.5001 | -0.07782 | 62.9929 | -59.2255 | 63.0936 | -59.2987 | -59.4315 | -59.3079 | -0.064087 | -0.054931 | -0.027465 | 0.10071 | -0.2655 | -0.27924 | -0.20142 | -0.21515 | 0.009155 | -0.11902 | -0.01831 | -0.064087 | -0.073242 | -0.19684 | -0.082397 | -0.20599 | 0.1648 | 122.3831 | -0.073242 | 122.319 | 122.3557 | 122.2183 | 122.2916 | 122.2275 | -122.4106 | -122.3373 | 122.319 | 122.3282 | 59.1888 | 59.1568
641.3125 | 122.5296 | -59.2255 | 63.1165 | -0.027695 | 0.004971 | 0.064444 | 0.061303 | 0.0016236 | -0.0010382 | -0.00050846 | -0.045776 | 0.0039819 | 0.068438 | 0.066052 | -0.0031274 | 0.0096515 | -0.0028818 | -0.022888 | 63.0432 | -59.3124 | 63.1119 | -59.1248 | -59.5322 | -59.4864 | -0.064087 | 63.0112 | -59.2346 | 63.0936 | -59.2941 | -59.4269 | -59.3033 | -0.086975 | -0.073242 | -0.004578 | 0.10071 | -0.26093 | -0.3067 | -0.17395 | -0.21973 | -0.009155 | -0.10529 | -0.022888 | -0.068664 | -0.07782 | -0.20142 | -0.068665 | -0.19226 | 0.18768 | 122.4243 | -0.059509 | 122.3282 | 122.3557 | 122.2458 | 122.2687 | 122.2366 | -122.4289 | -122.3511 | 122.3373 | 122.319 | 59.2026 | 59.1614
642.3125 | 122.525 | -59.2438 | 63.121 | -0.042954 | 0.0030484 | 0.063803 | 0.06109 | 0.00098262 | -0.00082456 | -0.0015765 | -0.036621 | 0.0031273 | 0.066729 | 0.057935 | -0.0046228 | 0.01072 | 0.0020316 | -0.032043 | 63.0524 | -59.317 | 63.1027 | -59.1156 | -59.5001 | -59.4818 | -0.050354 | 63.002 | -59.2346 | 63.0981 | -59.2896 | -59.4223 | -59.2896 | -0.073243 | -0.068665 | -0.018311 | 0.12817 | -0.23804 | -0.25635 | -0.16479 | -0.1831 | 0.009155 | -0.11902 | -0.022888 | -0.045777 | -0.045777 | -0.17853 | -0.054932 | -0.18768 | 0.20142 | 122.4197 | -0.054932 | 122.3328 | 122.3694 | 122.2366 | 122.2961 | 122.2458 | -122.4381 | -122.3557 | 122.3465 | 122.3419 | 59.2117 | 59.1934
643.3125 | 122.5937 | -59.2163 | 63.0753 | -0.096359 | 0.0013394 | 0.062735 | 0.057458 | 0.00034182 | -0.0025336 | -0.0026447 | 0.057983 | 0.00013675 | 0.066943 | 0.057507 | -0.0031274 | 0.0073015 | 0.0003226 | -0.07782 | 63.0066 | -59.2575 | 63.1119 | -59.0881 | -59.4635 | -59.436 | -0.045776 | 62.9517 | -59.1888 | 63.1348 | -59.2804 | -59.3216 | -59.2072 | -0.041198 | -0.068664 | 0.036621 | 0.12817 | -0.21973 | -0.24719 | -0.17853 | -0.20599 | 0.027466 | -0.1236 | 0.05951 | -0.064087 | 0.009156 | -0.10528 | -0.01831 | -0.13275 | 0.16937 | 122.3694 | -0.091553 | 122.3236 | 122.2641 | 122.1405 | 122.2229 | 122.168 | -122.3328 | -122.2641 | 122.3282 | 122.3511 | 59.1385 | 59.1705
644.3125 | 122.4976 | -59.2575 | 63.1393 | -0.012436 | 0.0030484 | 0.065085 | 0.060235 | -0.00029898 | -0.0029608 | -0.0013629 | -0.042725 | 0.0018457 | 0.065661 | 0.060925 | -0.003982 | 0.0092241 | -0.0039498 | -0.059509 | 63.0432 | -59.3079 | 63.0753 | -59.1705 | -59.5551 | -59.5184 | -0.13275 | 63.0112 | -59.2255 | 63.0524 | -59.3353 | -59.4589 | -59.3262 | -0.050354 | -0.09613 | -0.064087 | 0.086975 | -0.26093 | -0.29755 | -0.21057 | -0.24719 | 0.032043 | -0.12817 | -0.086975 | -0.07782 | -0.068665 | -0.20142 | -0.10071 | -0.23346 | 0.13733 | 122.3831 | -0.10986 | 122.2778 | 122.3511 | 122.2366 | 122.3007 | 122.2687 | -122.4472 | -122.3648 | 122.3328 | 122.3099 | 59.198 | 59.1248
645.3125 | 122.525 | -59.2484 | 63.1165 | -0.042954 | 0.0013394 | 0.064444 | 0.061731 | -0.00072638 | 0.001098 | -0.00029486 | -0.05188 | 0.0018457 | 0.06737 | 0.06178 | -0.0054774 | 0.0096515 | -0.0028818 | -0.10071 | 63.0386 | -59.3536 | 62.8555 | -58.8913 | -59.2117 | -59.5139 | -0.11444 | 63.0295 | -59.2529 | 63.0707 | -59.3308 | -59.4955 | -59.3491 | -0.10529 | -0.07782 | -0.26093 | 0.35706 | -0.2655 | 0.036621 | -0.16022 | 0.14191 | -0.004578 | -0.086975 | -0.045776 | -0.082398 | -0.10071 | -0.24719 | -0.09613 | -0.24261 | 0.46234 | 122.2092 | -0.07782 | 122.3236 | 122.3923 | 122.2824 | 122.287 | 122.2778 | -122.4701 | -122.3694 | 122.1039 | 122.319 | 59.1476 | 59.1339
646.3125 | 122.5342 | -59.2575 | 63.1119 | -0.065842 | 0.0024076 | 0.062308 | 0.061517 | 0.00034182 | -0.0036018 | -0.0030719 | -0.0061035 | 0.0033411 | 0.066943 | 0.057935 | -0.006759 | 0.0096515 | 0.0005362 | -0.10071 | 63.0157 | -59.3491 | 63.0569 | -59.1751 | -59.5551 | -59.5276 | -0.13733 | 62.9974 | -59.2529 | 63.089 | -59.3079 | -59.4223 | -59.3033 | -0.091553 | -0.09613 | -0.054931 | 0.082397 | -0.27008 | -0.29755 | -0.17853 | -0.20599 | 0.004577 | -0.11444 | -0.022888 | -0.050354 | -0.045777 | -0.1648 | -0.050354 | -0.16937 | 0.17395 | 122.406 | -0.054931 | 122.3419 | 122.3648 | 122.2504 | 122.2733 | 122.2549 | -122.4609 | -122.3648 | 122.3145 | 122.3465 | 59.1568 | 59.1202
647.3125 | 122.4976 | -59.23 | 63.1119 | -0.042954 | 0.0047574 | 0.065298 | 0.062799 | 0.004187 | -0.0036018 | -0.0024311 | -0.030517 | 0.0016321 | 0.068866 | 0.058575 | -0.0041956 | 0.0081561 | -0.0028818 | -0.045776 | 63.0341 | -59.3262 | 63.0981 | -59.1568 | -59.5322 | -59.5001 | -0.086975 | 63.0066 | -59.2484 | 63.0798 | -59.3033 | -59.436 | -59.2987 | -0.09613 | -0.077819 | -0.013732 | 0.073243 | -0.27008 | -0.30212 | -0.17395 | -0.20599 | -0.01831 | -0.10529 | -0.032043 | -0.073242 | -0.068664 | -0.20599 | -0.050354 | -0.18768 | 0.16937 | 122.4243 | -0.054932 | 122.3282 | 122.3602 | 122.2549 | 122.2641 | 122.2366 | -122.438 | -122.3602 | 122.3282 | 122.3099 | 59.1843 | 59.1431
648.3125 | 122.6715 | -59.1614 | 63.0844 | -0.081101 | 0.002194 | 0.065085 | 0.05639 | -0.0017944 | -0.0021064 | -0.0026447 | 0.082398 | 0.0012047 | 0.067798 | 0.062634 | -0.0044092 | 0.0068743 | -0.0026682 | 0.004578 | 63.0478 | -59.2758 | 63.1577 | -59.0012 | -59.3948 | -59.3765 | 0.10071 | 62.9745 | -59.198 | 63.2172 | -59.1431 | -59.2438 | -59.166 | -0.11444 | -0.036621 | 0.073242 | 0.16022 | -0.21515 | -0.23346 | -0.10071 | -0.11902 | -0.036621 | -0.10986 | 0.13275 | 0.018311 | -0.004578 | -0.082397 | 0.032043 | -0.045776 | 0.27466 | 122.4335 | 0.054932 | 122.4152 | 122.3236 | 122.1725 | 122.2092 | 122.1359 | -122.3602 | -122.2824 | 122.319 | 122.3785 | 59.166 | 59.2621
649.3125 | 122.5388 | -59.2392 | 63.1439 | -0.081101 | 0.0024076 | 0.062094 | 0.061731 | -0.00051278 | -0.0014654 | 0.00098694 | -0.042725 | 0.0033411 | 0.065875 | 0.06477 | -0.0052638 | 0.0094379 | 0.001818 | -0.018311 | 63.0341 | -59.3262 | 63.1073 | -59.1064 | -59.5047 | -59.4818 | -0.027466 | 62.9974 | -59.23 | 63.0981 | -59.285 | -59.4223 | -59.3033 | -0.086975 | -0.10986 | -0.036621 | 0.13275 | -0.24262 | -0.2655 | -0.15564 | -0.17853 | 0.009155 | -0.14648 | -0.045776 | -0.045776 | -0.064087 | -0.18311 | -0.073242 | -0.19226 | 0.21973 | 122.4335 | -0.054931 | 122.3282 | 122.3602 | 122.2275 | 122.2733 | 122.2366 | -122.4701 | -122.374 | 122.3465 | 122.3373 | 59.2209 | 59.2117
650.3125 | 122.5021 | -59.2667 | 63.1027 | -0.058212 | 0.0036892 | 0.064871 | 0.063226 | -0.0011536 | -0.0042426 | -0.00050846 | -0.027466 | 0.0027001 | 0.065234 | 0.063061 | -0.003982 | 0.0096515 | 0.001818 | -0.059509 | 63.0341 | -59.3308 | 63.0707 | -59.1797 | -59.5505 | -59.523 | -0.12817 | 63.0203 | -59.2484 | 63.0615 | -59.3353 | -59.4772 | -59.3262 | -0.064087 | -0.068664 | -0.032043 | 0.086976 | -0.25635 | -0.28381 | -0.19226 | -0.21973 | 0.018311 | -0.082397 | -0.041199 | -0.068664 | -0.059509 | -0.21057 | -0.07782 | -0.22888 | 0.15106 | 122.4014 | -0.086975 | 122.3099 | 122.3648 | 122.2687 | 122.3007 | 122.287 | -122.4335 | -122.3511 | 122.3373 | 122.3282 | 59.2072 | 59.1385
651.3125 | 122.5159 | -59.2484 | 63.121 | -0.10399 | 0.0017666 | 0.063803 | 0.059595 | 0.0035462 | -0.0042426 | 0.0016277 | 0.073242 | 0.0016321 | 0.064593 | 0.055371 | -0.0052638 | 0.0075153 | 0.0003226 | -0.10529 | 63.0112 | -59.3628 | 63.0798 | -59.5688 | -59.9396 | -59.3536 | -0.25177 | 63.0066 | -59.23 | 63.0707 | -59.3582 | -59.4543 | -59.3399 | -0.11444 | -0.10986 | -0.041199 | -0.32044 | -0.10529 | -0.69122 | 0.009155 | -0.57678 | 0.01831 | -0.11444 | -0.050354 | -0.10986 | -0.091553 | -0.20599 | -0.10986 | -0.2243 | -0.20599 | 122.4426 | -0.12817 | 122.3007 | 122.374 | 122.2366 | 122.2595 | 122.2549 | -122.4838 | -122.3511 | 122.3282 | 122.319 | 59.1431 | 58.9966
652.3125 | 122.5891 | -59.2163 | 63.0432 | -0.065842 | 0.0051846 | 0.065085 | 0.059381 | 0.0026916 | -0.0014654 | -0.0020039 | 0.039673 | 0.0020593 | 0.068011 | 0.061566 | -0.006759 | 0.0077289 | -0.0018136 | -0.045776 | 62.9974 | -59.2987 | 63.1668 | -59.0332 | -59.436 | -59.404 | 0 | 62.9471 | -59.23 | 63.1714 | -59.2163 | -59.3079 | -59.2026 | -0.082397 | -0.045776 | 0.1236 | 0.18311 | -0.18768 | -0.21973 | -0.10529 | -0.13733 | -0.013733 | -0.09613 | 0.12817 | 0 | 0.013733 | -0.091552 | 0.027466 | -0.077819 | 0.2655 | 122.4655 | 0.013733 | 122.4014 | 122.2961 | 122.1771 | 122.2137 | 122.1634 | -122.3419 | -122.2733 | 122.3831 | 122.3877 | 59.1705 | 59.2163
653.3125 | 122.6303 | -59.1934 | 63.0661 | -0.12688 | 0.0028348 | 0.064016 | 0.060876 | 0.0016236 | -0.00018376 | 0.00034614 | 0.039673 | 0.0014185 | 0.065661 | 0.058362 | -0.0059046 | 0.0081561 | -0.0024546 | -0.027466 | 63.002 | -59.2896 | 63.1622 | -59.0469 | -59.4452 | -59.4131 | 0.009155 | 62.9425 | -59.2117 | 63.1943 | -59.1934 | -59.3216 | -59.2072 | -0.096131 | -0.064087 | 0.09613 | 0.14648 | -0.21973 | -0.25177 | -0.1236 | -0.15564 | -0.018311 | -0.1236 | 0.12817 | 0 | -0.013733 | -0.12817 | 0.004578 | -0.10986 | 0.24262 | 122.4518 | 0.018311 | 122.406 | 122.2916 | 122.1542 | 122.1954 | 122.1359 | -122.3557 | -122.2778 | 122.3557 | 122.3877 | 59.166 | 59.2026
654.3125 | 122.5525 | -59.2209 | 63.1165 | -0.020065 | 0.0039028 | 0.063589 | 0.061944 | 0.0031188 | -0.00232 | 0.00013254 | -0.048828 | 0.0016321 | 0.066089 | 0.065411 | -0.0076136 | 0.0085833 | -0.0026682 | -0.027466 | 63.0707 | -59.3033 | 63.1119 | -59.1019 | -59.5047 | -59.4681 | -0.027466 | 63.0157 | -59.2163 | 63.0981 | -59.2758 | -59.404 | -59.2941 | -0.082398 | -0.045776 | -0.004578 | 0.11902 | -0.24719 | -0.28381 | -0.1648 | -0.20142 | 0.004577 | -0.10071 | -0.01831 | -0.054932 | -0.073242 | -0.18311 | -0.077819 | -0.18768 | 0.20142 | 122.4152 | -0.059509 | 122.3145 | 122.374 | 122.2321 | 122.2916 | 122.2366 | -122.4197 | -122.3328 | 122.3328 | 122.319 | 59.1934 | 59.1934
655.3125 | 122.5479 | -59.2117 | 63.1256 | -0.020065 | 0.0041166 | 0.063589 | 0.060663 | -0.0013672 | -0.0016792 | -0.0020039 | -0.042725 | 0.0029137 | 0.065875 | 0.063702 | -0.0065454 | 0.010079 | -0.0030954 | 0.009155 | 63.0341 | -59.2941 | 63.1348 | -59.0836 | -59.4727 | -59.4543 | -0.21515 | 63.002 | -59.2346 | 63.1302 | -59.2117 | -59.3491 | -59.23 | -0.082397 | -0.091552 | 0.009156 | 0.12817 | -0.24262 | -0.26093 | -0.16022 | -0.17853 | -0.022888 | -0.1236 | 0.004578 | 0 | -0.018311 | -0.13733 | 0.004577 | -0.11444 | 0.21057 | 122.4289 | 0.022888 | 122.3648 | 122.3282 | 122.2366 | 122.2458 | 122.2137 | -122.4197 | -122.3602 | 122.3465 | 122.3419 | 59.2209 | 58.9966
656.3125 | 122.5159 | -59.23 | 63.1119 | -0.0048066 | 0.001553 | 0.061239 | 0.061303 | 0.0020508 | -0.0010382 | -0.0011493 | -0.045776 | 0.0027001 | 0.065875 | 0.065198 | -0.005691 | 0.0083697 | -0.0018136 | -0.045776 | 63.0295 | -59.3124 | 63.1027 | -59.1385 | -59.523 | -59.5139 | -0.086975 | 63.0112 | -59.2575 | 63.0661 | -59.2987 | -59.436 | -59.317 | -0.082397 | -0.082397 | -0.009155 | 0.091553 | -0.28381 | -0.29297 | -0.20142 | -0.21057 | -0.027465 | -0.10071 | -0.045776 | -0.068664 | -0.086975 | -0.20599 | -0.05951 | -0.17853 | 0.17395 | 122.4152 | -0.041199 | 122.3236 | 122.3419 | 122.2687 | 122.2595 | 122.2412 | -122.4243 | -122.3694 | 122.3328 | 122.2961 | 59.1843 | 59.1431
657.3125 | 122.6303 | -59.2072 | 63.0844 | -0.096359 | 0.0036892 | 0.064016 | 0.058954 | 0.0020508 | -0.0027472 | -0.00050846 | 0.012207 | 0.00013675 | 0.066943 | 0.058148 | -0.0063318 | 0.0090105 | -0.0024546 | -0.022888 | 62.97 | -59.2804 | 63.1668 | -59.024 | -59.436 | -59.4131 | -0.004578 | 62.9654 | -59.2072 | 63.1485 | -59.198 | -59.2987 | -59.2209 | -0.073243 | -0.11444 | 0.082397 | 0.1831 | -0.20599 | -0.22888 | -0.13275 | -0.15564 | 0 | -0.11902 | 0.064087 | 0.009155 | -0.013733 | -0.091553 | -0.013733 | -0.091553 | 0.25635 | 122.4472 | 0.009155 | 122.3557 | 122.2504 | 122.1725 | 122.1771 | 122.1725 | -122.3648 | -122.2916 | 122.374 | 122.3557 | 59.1843 | 59.2026
658.3125 | 122.5342 | -59.2255 | 63.1302 | -0.073471 | 0.0026212 | 0.063589 | 0.062585 | -0.0035034 | -0.0021064 | -0.00050846 | -0.045776 | 0.0022729 | 0.066516 | 0.053235 | -0.0082544 | 0.0073015 | -0.0039498 | -0.027466 | 63.0569 | -59.317 | 63.1027 | -59.111 | -59.5047 | -59.4727 | -0.041199 | 63.0157 | -59.2209 | 63.0981 | -59.2804 | -59.4177 | -59.285 | -0.091553 | -0.073242 | -0.027466 | 0.11444 | -0.24719 | -0.27924 | -0.15564 | -0.18768 | 0.004578 | -0.11444 | -0.032043 | -0.054932 | -0.059509 | -0.19226 | -0.064087 | -0.19684 | 0.20599 | 122.4197 | -0.05951 | 122.319 | 122.374 | 122.2366 | 122.2824 | 122.2412 | -122.4472 | -122.3511 | 122.3282 | 122.3236 | 59.198 | 59.1843
659.3125 | 122.4838 | -59.2529 | 63.1165 | -0.050583 | 0.002194 | 0.063589 | 0.059808 | -8.538e-05 | -0.004029 | -0.0030719 | -0.042725 | 0.0031273 | 0.066089 | 0.06477 | -0.0044092 | 0.0090105 | -0.0003182 | -0.045776 | 63.0478 | -59.3353 | 63.0798 | -59.1843 | -59.5459 | -59.5093 | -0.13733 | 63.002 | -59.2117 | 63.0707 | -59.3216 | -59.4635 | -59.317 | -0.082397 | -0.068664 | -0.036621 | 0.068665 | -0.25635 | -0.29297 | -0.17395 | -0.21057 | 0.041199 | -0.11444 | -0.045776 | -0.068664 | -0.064087 | -0.21057 | -0.10529 | -0.25177 | 0.15106 | 122.4152 | -0.10986 | 122.2824 | 122.3831 | 122.2137 | 122.3007 | 122.2549 | -122.4518 | -122.3282 | 122.3328 | 122.3236 | 59.2072 | 59.1156
660.3125 | 122.5433 | -59.23 | 63.1119 | -0.020065 | 0.001553 | 0.062521 | 0.063012 | 0.00034182 | -0.003388 | -0.0024311 | -0.048828 | 0.0018457 | 0.065875 | 0.060071 | -0.0044092 | 0.011361 | -0.0024546 | 0.004578 | 63.0569 | -59.3124 | 63.1256 | -59.0881 | -59.5047 | -59.4727 | -0.009155 | 63.0112 | -59.2346 | 63.1119 | -59.2346 | -59.3903 | -59.2575 | -0.082397 | -0.054931 | 0.013733 | 0.14191 | -0.24261 | -0.27466 | -0.16022 | -0.19226 | -0.004577 | -0.10071 | 0 | -0.004577 | -0.027465 | -0.16022 | -0.022888 | -0.15564 | 0.2243 | 122.438 | 0 | 122.3465 | 122.3694 | 122.2458 | 122.287 | 122.2412 | -122.4243 | -122.3465 | 122.3557 | 122.3419 | 59.2346 | 59.2209
661.3125 | 122.4884 | -59.2438 | 63.121 | -0.073471 | 0.0019802 | 0.063376 | 0.05874 | 0.0035462 | -0.004029 | -0.0028583 | -0.048828 | 0.00099115 | 0.068225 | 0.05943 | -0.0063318 | 0.0098651 | -0.0022408 | -0.036621 | 63.0295 | -59.317 | 63.0798 | -59.1385 | -59.5093 | -59.4955 | -0.073242 | 63.0112 | -59.2392 | 63.0707 | -59.3124 | -59.4406 | -59.3079 | -0.073243 | -0.091553 | -0.041199 | 0.10529 | -0.25177 | -0.2655 | -0.17853 | -0.19226 | 0.004577 | -0.10986 | -0.050354 | -0.068665 | -0.064087 | -0.19684 | -0.068664 | -0.20142 | 0.17853 | 122.3969 | -0.073242 | 122.3099 | 122.3465 | 122.2504 | 122.2733 | 122.2549 | -122.4381 | -122.3602 | 122.3236 | 122.3145 | 59.2072 | 59.1705
662.3125 | 122.5204 | -59.2346 | 63.121 | -0.027695 | 0.0006986 | 0.06423 | 0.062585 | 0.0014098 | -0.0031744 | -0.00093566 | -0.048828 | 0.0018457 | 0.06502 | 0.068188 | -0.0048364 | 0.0092241 | -0.0001046 | -0.027466 | 63.0386 | -59.2987 | 63.1073 | -59.1202 | -59.5139 | -59.491 | -0.041199 | 63.0066 | -59.2255 | 63.0981 | -59.2987 | -59.4269 | -59.2896 | -0.064087 | -0.082398 | -0.013733 | 0.11444 | -0.25635 | -0.27924 | -0.19226 | -0.21515 | 0.009155 | -0.11444 | -0.022888 | -0.064087 | -0.054932 | -0.19226 | -0.064087 | -0.20142 | 0.17853 | 122.406 | -0.073242 | 122.3236 | 122.3373 | 122.2321 | 122.2733 | 122.2412 | -122.4197 | -122.3465 | 122.3419 | 122.3328 | 59.2072 | 59.1934
663.3125 | 122.5616 | -59.2346 | 63.1348 | -0.027695 | 0.0006986 | 0.064871 | 0.060449 | -0.0011536 | -0.00039736 | 0.0033367 | -0.024414 | 0.0018457 | 0.067798 | 0.064343 | -0.0052638 | 0.0096515 | -0.0035226 | 0.009155 | 63.0478 | -59.3308 | 63.1348 | -59.0469 | -59.4772 | -59.4589 | 0.022888 | 62.9974 | -59.2163 | 63.1348 | -59.2438 | -59.3674 | -59.2484 | -0.096131 | -0.086975 | 0 | 0.18768 | -0.2243 | -0.24262 | -0.12817 | -0.14648 | 0.01831 | -0.13733 | 0 | -0.009155 | -0.013733 | -0.13275 | -0.032043 | -0.15106 | 0.28381 | 122.4655 | -0.027465 | 122.3511 | 122.3785 | 122.2137 | 122.2824 | 122.2321 | -122.4655 | -122.3511 | 122.3694 | 122.3694 | 59.2438 | 59.2575
664.3125 | 122.5525 | -59.23 | 63.1073 | -0.058212 | 0.0039028 | 0.064444 | 0.061303 | 0.0029052 | -0.0031744 | -8.1264e-05 | -0.030517 | 0.0024865 | 0.068225 | 0.05943 | -0.0063318 | 0.010079 | 0.0009634 | -0.013733 | 63.0295 | -59.3033 | 63.1027 | -59.1064 | -59.4864 | -59.4681 | -0.027466 | 62.9929 | -59.2163 | 63.1119 | -59.2575 | -59.3994 | -59.2896 | -0.073242 | -0.07782 | -0.004578 | 0.1236 | -0.23804 | -0.25635 | -0.1648 | -0.18311 | 0.013733 | -0.11444 | 0.004577 | -0.027465 | -0.059509 | -0.16937 | -0.073242 | -0.1831 | 0.19684 | 122.406 | -0.041198 | 122.3282 | 122.3328 | 122.2092 | 122.2595 | 122.2229 | -122.4106 | -122.3236 | 122.3328 | 122.3419 | 59.2163 | 59.2026
665.3125 | 122.4747 | -59.2484 | 63.1256 | -0.050583 | 0.0041166 | 0.065725 | 0.061517 | -0.0028626 | -0.0016792 | 0.00055974 | -0.024414 | 0.00099115 | 0.067798 | 0.056439 | -0.006759 | 0.011147 | -0.0037362 | -0.050354 | 63.0386 | -59.3124 | 63.0707 | -59.1522 | -59.5139 | -59.5093 | -0.10986 | 63.0112 | -59.2255 | 63.0936 | -59.3124 | -59.4681 | -59.3262 | -0.064087 | -0.086975 | -0.054931 | 0.09613 | -0.26093 | -0.2655 | -0.19684 | -0.20142 | 0.022888 | -0.11444 | -0.032043 | -0.064087 | -0.07782 | -0.21973 | -0.10071 | -0.24262 | 0.16022 | 122.3831 | -0.086975 | 122.319 | 122.3511 | 122.2366 | 122.287 | 122.2595 | -122.438 | -122.3511 | 122.319 | 122.3419 | 59.198 | 59.1385
666.3125 | 122.5296 | -59.23 | 63.1485 | 0.0028229 | 0.0030484 | 0.063162 | 0.060022 | 0.00098262 | -0.00232 | -0.0030719 | -0.027466 | 0.00077755 | 0.06737 | 0.067548 | -0.00505 | 0.0096515 | -0.0048044 | -0.032043 | 63.0386 | -59.2941 | 63.0753 | -59.1385 | -59.5139 | -59.5001 | -0.082397 | 62.9929 | -59.2346 | 63.0844 | -59.3033 | -59.4269 | -59.3033 | -0.064086 | -0.10986 | -0.073243 | 0.091553 | -0.27008 | -0.28381 | -0.20599 | -0.21973 | -0.004577 | -0.15564 | -0.064087 | -0.073242 | -0.073242 | -0.19684 | -0.068665 | -0.19226 | 0.15564 | 122.3694 | -0.068665 | 122.319 | 122.3328 | 122.2275 | 122.2687 | 122.2229 | -122.4426 | -122.3831 | 122.3053 | 122.3145 | 59.198 | 59.1476
667.3125 | 122.6486 | -59.2117 | 63.0707 | -0.042954 | 0.0039028 | 0.062521 | 0.059381 | 0.0016236 | -0.0010382 | -0.0011493 | -0.024414 | 0.00056395 | 0.065234 | 0.060498 | -0.0054774 | 0.0064471 | 0.0020316 | -0.050354 | 63.002 | -59.2896 | 63.1531 | -59.0515 | -59.4543 | -59.4086 | -0.10986 | 62.8876 | -59.2117 | 63.1989 | -59.2072 | -59.285 | -59.1614 | -0.07782 | -0.068665 | 0.082397 | 0.16022 | -0.19684 | -0.24262 | -0.11902 | -0.16479 | 0 | -0.18311 | 0.12817 | 0.004578 | 0.050354 | -0.073242 | 0.050354 | -0.073242 | 0.23804 | 122.4426 | 0.004578 | 122.4106 | 122.2916 | 122.0993 | 122.2137 | 122.0993 | -122.3602 | -122.2824 | 122.3648 | 122.4106 | 59.1614 | 59.1019
668.3125 | 122.5616 | -59.2163 | 63.1485 | -0.035324 | 0.0030484 | 0.062948 | 0.05874 | 0.0022644 | -0.0014654 | -0.0022175 | -0.0061035 | 0.0029137 | 0.068438 | 0.062848 | -0.008468 | 0.0094379 | -0.0026682 | 0 | 63.0661 | -59.2987 | 63.1073 | -59.0927 | -59.4498 | -59.4452 | 0.018311 | 62.9974 | -59.2117 | 63.1302 | -59.2255 | -59.3628 | -59.2392 | -0.082397 | -0.082398 | -0.041199 | 0.1236 | -0.22888 | -0.23346 | -0.14648 | -0.15106 | 0.004578 | -0.15106 | -0.018311 | -0.009155 | -0.022888 | -0.14648 | -0.027466 | -0.15106 | 0.20599 | 122.406 | -0.013733 | 122.3419 | 122.3648 | 122.2092 | 122.2824 | 122.2137 | -122.4472 | -122.3602 | 122.3236 | 122.3465 | 59.2163 | 59.2346
669.3125 | 122.5662 | -59.2163 | 63.1393 | -0.0048066 | 0.0026212 | 0.063589 | 0.060663 | 0.0022644 | -0.0027472 | 0.00098694 | -0.039673 | 0.0027001 | 0.068438 | 0.059644 | -0.005691 | 0.0085833 | 0.0013906 | 0.004578 | 63.0524 | -59.317 | 62.9562 | -59.2209 | -59.2346 | -59.3811 | 0.045776 | 63.0203 | -59.2163 | 63.1439 | -59.2209 | -59.3674 | -59.2484 | -0.10071 | -0.086975 | -0.1831 | -0.004577 | -0.16479 | -0.01831 | -0.064087 | 0.082398 | 0 | -0.11902 | 0.004578 | -0.004577 | -0.032043 | -0.15106 | -0.032043 | -0.15106 | 0.096131 | 122.2733 | -0.004577 | 122.3602 | 122.3694 | 122.2366 | 122.2687 | 122.2366 | -122.4564 | -122.3557 | 122.1725 | 122.3602 | 59.2209 | 59.2621
670.3125 | 122.5708 | -59.198 | 63.1119 | -0.0048066 | 0.0041166 | 0.062735 | 0.060663 | -8.538e-05 | -0.0025336 | 0.00077334 | -0.024414 | 0.00099115 | 0.066943 | 0.069257 | -0.0074 | 0.0079425 | -0.0028818 | 0.013733 | 63.0661 | -59.2987 | 63.1256 | -59.0744 | -59.4681 | -59.4498 | -0.23346 | 62.9608 | -59.2484 | 63.1302 | -59.23 | -59.3536 | -59.2346 | -0.10071 | -0.045776 | 0.013733 | 0.1236 | -0.25177 | -0.27008 | -0.15106 | -0.16937 | -0.050354 | -0.15106 | 0.018311 | -0.032044 | -0.036621 | -0.15564 | 0.013733 | -0.10529 | 0.2243 | 122.4243 | 0.01831 | 122.3785 | 122.3648 | 122.2092 | 122.2641 | 122.1588 | -122.4106 | -122.3602 | 122.3236 | 122.3282 | 59.2117 | 58.9645
671.3125 | 122.5204 | -59.2392 | 63.0981 | -0.058212 | 0.0024076 | 0.062735 | 0.061731 | 0.0054688 | -0.0025336 | -0.00093566 | -0.030517 | 0.00099115 | 0.067798 | 0.060284 | -0.0044092 | 0.0081561 | -0.0020272 | -0.054932 | 63.0386 | -59.3079 | 63.0844 | -59.1248 | -59.5139 | -59.5139 | -0.07782 | 63.0249 | -59.2346 | 63.0753 | -59.2987 | -59.4223 | -59.3124 | -0.068664 | -0.05951 | -0.013733 | 0.11444 | -0.27466 | -0.27466 | -0.20599 | -0.20599 | 0.004578 | -0.073243 | -0.022889 | -0.059509 | -0.073242 | -0.18311 | -0.07782 | -0.18768 | 0.18311 | 122.3923 | -0.064087 | 122.3099 | 122.3465 | 122.2595 | 122.2778 | 122.2641 | -122.406 | -122.3328 | 122.3236 | 122.3145 | 59.1843 | 59.1614
672.3125 | 122.5296 | -59.2392 | 63.1027 | -0.073471 | 0.0006986 | 0.063803 | 0.059167 | -0.0013672 | -0.0021064 | 0.00013254 | -0.030517 | 0.0031273 | 0.066516 | 0.060925 | -0.0037684 | 0.0066607 | -0.0007456 | -0.12817 | 63.0249 | -59.3262 | 63.0386 | -59.1843 | -59.5734 | -59.523 | -0.13275 | 62.9929 | -59.23 | 63.0615 | -59.3262 | -59.4452 | -59.2941 | -0.086975 | -0.07782 | -0.064087 | 0.054932 | -0.28381 | -0.33417 | -0.19684 | -0.24719 | 0.009155 | -0.10986 | -0.041199 | -0.086975 | -0.054931 | -0.20599 | -0.064086 | -0.21515 | 0.14191 | 122.3648 | -0.09613 | 122.2916 | 122.3511 | 122.2229 | 122.2641 | 122.2321 | -122.4289 | -122.3328 | 122.2778 | 122.3007 | 59.111 | 59.1064
673.3125 | 122.5388 | -59.2117 | 63.1119 | -0.10399 | 0.002194 | 0.062308 | 0.060449 | -0.0035034 | -0.0053108 | -0.00029486 | -0.015259 | 0.0027001 | 0.065875 | 0.060498 | -0.0063318 | 0.0092241 | 0.0005362 | 0.032043 | 63.0569 | -59.3033 | 63.1348 | -59.0744 | -59.4635 | -59.4452 | 0.009155 | 62.9974 | -59.2209 | 63.1256 | -59.2438 | -59.3719 | -59.2529 | -0.091553 | -0.054931 | 0.022889 | 0.13733 | -0.23346 | -0.25177 | -0.14191 | -0.16022 | -0.009155 | -0.11444 | 0.013733 | -0.032043 | -0.041199 | -0.16022 | -0.032044 | -0.15106 | 0.22888 | 122.4381 | -0.022888 | 122.3465 | 122.3602 | 122.2183 | 122.2687 | 122.2092 | -122.4152 | -122.3328 | 122.3465 | 122.3373 | 59.2438 | 59.2209
674.3125 | 122.5616 | -59.2117 | 63.1165 | -0.065842 | 0.001553 | 0.064657 | 0.05874 | -8.538e-05 | -0.0046698 | 0.00034614 | -0.024414 | 0.0012047 | 0.070147 | 0.062207 | -0.0065454 | 0.0098651 | 0.000109 | 0.059509 | 63.0524 | -59.317 | 63.1531 | -59.0744 | -59.4543 | -59.4315 | 0.018311 | 63.0203 | -59.2117 | 63.1302 | -59.2529 | -59.3674 | -59.2621 | -0.10529 | -0.064087 | 0.036621 | 0.13733 | -0.21973 | -0.24262 | -0.11444 | -0.13733 | 0 | -0.09613 | 0.013733 | -0.041199 | -0.050354 | -0.15564 | -0.050354 | -0.15564 | 0.24262 | 122.4701 | -0.041199 | 122.3419 | 122.3694 | 122.2321 | 122.2641 | 122.2321 | -122.4335 | -122.3282 | 122.3648 | 122.3419 | 59.2712 | 59.23
675.3125 | 122.5525 | -59.2209 | 63.1073 | 0.025711 | 0.002194 | 0.062521 | 0.06109 | -0.002008 | -0.0012518 | -0.0015765 | 0.0061035 | 0.0035547 | 0.066943 | 0.060284 | -0.0063318 | 0.0060199 | -0.0030954 | 0.013733 | 63.0569 | -59.2941 | 63.1027 | -59.0973 | -59.4498 | -59.4543 | 0.027466 | 63.0295 | -59.198 | 63.1165 | -59.23 | -59.3491 | -59.2392 | -0.073242 | -0.050354 | -0.004578 | 0.1236 | -0.23346 | -0.22888 | -0.16022 | -0.15564 | 0.022888 | -0.07782 | 0.009155 | -0.009156 | -0.018311 | -0.12817 | -0.041199 | -0.15106 | 0.19684 | 122.3969 | -0.032044 | 122.3145 | 122.3511 | 122.2275 | 122.2778 | 122.2504 | -122.4014 | -122.3053 | 122.3236 | 122.3373 | 59.2346 | 59.2484
676.3125 | 122.5525 | -59.2026 | 63.1256 | -0.042954 | 0.0026212 | 0.064657 | 0.061944 | -0.00093998 | -0.005738 | -8.1264e-05 | -0.012207 | 0.0016321 | 0.06737 | 0.057935 | -0.00505 | 0.010292 | 0.0030996 | 0 | 63.0341 | -59.2987 | 63.1073 | -59.0836 | -59.4269 | -59.4498 | 0.032043 | 63.0112 | -59.2117 | 63.1485 | -59.2392 | -59.3445 | -59.2392 | -0.09613 | -0.091552 | -0.01831 | 0.11902 | -0.24719 | -0.2243 | -0.15106 | -0.12817 | -0.009155 | -0.11444 | 0.022889 | -0.036621 | -0.036621 | -0.14191 | -0.027466 | -0.13275 | 0.21515 | 122.406 | -0.027466 | 122.3602 | 122.3328 | 122.2229 | 122.2366 | 122.2137 | -122.4243 | -122.3373 | 122.3099 | 122.3511 | 59.2026 | 59.2346
677.3125 | 122.5708 | -59.2255 | 63.0981 | -0.012436 | 0.0030484 | 0.063589 | 0.060235 | 0.0026916 | -0.0018928 | -0.0028583 | -0.0030517 | 0.0029137 | 0.066302 | 0.061139 | -0.0063318 | 0.0083697 | -0.0022408 | -0.10529 | 63.0478 | -59.317 | 63.0524 | -59.166 | -59.5459 | -59.5184 | -0.11444 | 62.9654 | -59.2346 | 63.0936 | -59.2621 | -59.3674 | -59.2758 | -0.091553 | -0.050354 | -0.045777 | 0.059509 | -0.29297 | -0.32043 | -0.20142 | -0.22888 | -0.009155 | -0.13275 | -0.004578 | -0.036621 | -0.050354 | -0.14191 | -0.041199 | -0.13275 | 0.15106 | 122.3694 | -0.027466 | 122.3282 | 122.3648 | 122.2 | 122.2733 | 122.1909 | -122.4152 | -122.3328 | 122.2778 | 122.319 | 59.1202 | 59.111
678.3125 | 122.5204 | -59.23 | 63.1027 | -0.073471 | 0.0026212 | 0.064016 | 0.062158 | 0.0022644 | -0.0038154 | -0.0034991 | -0.027466 | 0.0037683 | 0.068866 | 0.065625 | -0.0059046 | 0.010079 | -0.0003182 | -0.027466 | 63.0432 | -59.3124 | 63.1073 | -59.1202 | -59.4864 | -59.4681 | -0.041199 | 63.0203 | -59.2346 | 63.1256 | -59.2896 | -59.404 | -59.2758 | -0.082397 | -0.059509 | 0.004578 | 0.10986 | -0.23804 | -0.25635 | -0.15564 | -0.17395 | -0.004577 | -0.082397 | 0.022888 | -0.059509 | -0.045776 | -0.17395 | -0.041199 | -0.16937 | 0.19226 | 122.4197 | -0.054932 | 122.3602 | 122.3557 | 122.2549 | 122.2733 | 122.2504 | -122.4152 | -122.3373 | 122.3373 | 122.3557 | 59.2026 | 59.1888
679.3125 | 122.5159 | -59.2484 | 63.1393 | -0.058212 | 0.0011258 | 0.062735 | 0.059381 | -0.0028626 | -0.00061096 | -0.00072206 | -0.027466 | 0.0024865 | 0.067157 | 0.058148 | -0.0044092 | 0.0085833 | -0.000532 | 0 | 63.0341 | -59.3124 | 63.1119 | -59.1019 | -59.5001 | -59.4727 | -0.027466 | 63.0066 | -59.23 | 63.1027 | -59.2667 | -59.3994 | -59.2621 | -0.064087 | -0.10528 | -0.027466 | 0.14648 | -0.2243 | -0.25177 | -0.16022 | -0.18768 | 0.01831 | -0.13275 | -0.036621 | -0.018311 | -0.013733 | -0.15106 | -0.032043 | -0.16937 | 0.21057 | 122.4243 | -0.036621 | 122.3328 | 122.3465 | 122.2366 | 122.2824 | 122.2549 | -122.4518 | -122.3694 | 122.3602 | 122.3511 | 59.2484 | 59.2209
680.3125 | 122.5296 | -59.2117 | 63.1348 | -0.035324 | 0.0028348 | 0.06423 | 0.061731 | 0.002478 | -0.003388 | -0.0013629 | -0.027466 | 0.0014185 | 0.069079 | 0.059644 | -0.0054774 | 0.0087969 | -0.0026682 | -0.013733 | 63.0432 | -59.3079 | 63.1119 | -59.0973 | -59.4772 | -59.4681 | -0.022888 | 63.0203 | -59.23 | 63.0844 | -59.2667 | -59.3994 | -59.2621 | -0.09613 | -0.091553 | -0.022889 | 0.11444 | -0.25635 | -0.2655 | -0.16022 | -0.16937 | -0.018311 | -0.11444 | -0.050354 | -0.054932 | -0.050354 | -0.18768 | -0.032043 | -0.16937 | 0.21057 | 122.4197 | -0.036621 | 122.3145 | 122.3511 | 122.2504 | 122.2549 | 122.2321 | -122.4426 | -122.3648 | 122.3236 | 122.2961 | 59.198 | 59.1888
681.3125 | 122.4701 | -59.23 | 63.1302 | -0.10399 | 0.0039028 | 0.064871 | 0.060235 | -0.0013672 | -0.004029 | -8.1264e-05 | -0.030517 | 0.0024865 | 0.065448 | 0.063061 | -0.0069726 | 0.0094379 | -0.0018136 | -0.045776 | 63.0295 | -59.3399 | 63.0661 | -59.1568 | -59.5322 | -59.5093 | -0.10529 | 63.002 | -59.2346 | 63.0569 | -59.3124 | -59.4498 | -59.3124 | -0.10986 | -0.10071 | -0.064087 | 0.073243 | -0.27923 | -0.30212 | -0.16937 | -0.19226 | -0.004577 | -0.12817 | -0.073242 | -0.082397 | -0.082397 | -0.21973 | -0.07782 | -0.21515 | 0.18311 | 122.406 | -0.07782 | 122.2916 | 122.3694 | 122.2366 | 122.2595 | 122.2321 | -122.4701 | -122.3648 | 122.2961 | 122.287 | 59.1843 | 59.1248
682.3125 | 122.5937 | -59.1934 | 63.0615 | -0.12688 | 0.0028348 | 0.064016 | 0.058526 | -8.538e-05 | -0.0027472 | -0.00050846 | 0.045776 | -0.00029045 | 0.068225 | 0.057507 | -0.0059046 | 0.0094379 | 0.0005362 | -0.041199 | 62.9929 | -59.285 | 63.1393 | -59.0286 | -59.436 | -59.3994 | -0.013733 | 62.9379 | -59.2209 | 63.1439 | -59.2117 | -59.3308 | -59.2117 | -0.091553 | -0.068664 | 0.07782 | 0.1648 | -0.20599 | -0.24261 | -0.11444 | -0.15106 | -0.027466 | -0.1236 | 0.082398 | -0.018311 | -0.018311 | -0.13733 | 0.009155 | -0.10986 | 0.25635 | 122.4243 | 0.009155 | 122.3648 | 122.2778 | 122.1588 | 122.1863 | 122.1313 | -122.3465 | -122.2824 | 122.3328 | 122.3373 | 59.1522 | 59.1797
683.3125 | 122.5845 | -59.2163 | 63.1485 | -0.0048066 | 0.0013394 | 0.064016 | 0.062585 | -0.0013672 | -0.00061096 | -0.0032855 | -0.012207 | 0.0012047 | 0.067798 | 0.062207 | -0.0076136 | 0.0081561 | -0.0065134 | 0.013733 | 63.0341 | -59.2987 | 63.1119 | -59.0927 | -59.4772 | -59.4406 | 0.022888 | 63.0112 | -59.2209 | 63.1577 | -59.23 | -59.3399 | -59.2163 | -0.082397 | -0.11444 | -0.036622 | 0.1236 | -0.2243 | -0.26093 | -0.14191 | -0.17853 | -0.004577 | -0.13733 | 0.009155 | -0.013733 | 0 | -0.1236 | 0.004577 | -0.11902 | 0.20599 | 122.4106 | -0.009156 | 122.3785 | 122.3328 | 122.2321 | 122.2504 | 122.2275 | -122.4472 | -122.3694 | 122.3282 | 122.374 | 59.23 | 59.2392
684.3125 | 122.5479 | -59.2209 | 63.1119 | -0.058212 | 0.003262 | 0.063376 | 0.060235 | 0.0020508 | -0.0025336 | 0.0020551 | -0.042725 | 0.0012047 | 0.066943 | 0.06178 | -0.0065454 | 0.0092241 | -0.0018136 | -0.013733 | 63.0341 | -59.3033 | 63.1073 | -59.0973 | -59.4635 | -59.4406 | 0 | 63.002 | -59.2346 | 63.1073 | -59.2529 | -59.3948 | -59.2667 | -0.082398 | -0.077819 | -0.004577 | 0.1236 | -0.21973 | -0.24262 | -0.13733 | -0.16022 | -0.013733 | -0.10986 | -0.004577 | -0.032044 | -0.045777 | -0.17395 | -0.032044 | -0.16022 | 0.20599 | 122.4106 | -0.018311 | 122.3419 | 122.3373 | 122.2366 | 122.2549 | 122.2229 | -122.4152 | -122.3465 | 122.3282 | 122.3282 | 59.2072 | 59.2209
685.3125 | 122.4884 | -59.2392 | 63.1348 | -0.027695 | 0.0036892 | 0.06423 | 0.060876 | -0.0013672 | -0.0036018 | -0.0017903 | -0.033569 | 0.0018457 | 0.068438 | 0.061352 | -0.0044092 | 0.0087969 | -0.0009592 | -0.045776 | 63.0386 | -59.3216 | 63.0753 | -59.1339 | -59.5139 | -59.5093 | -0.091553 | 63.0066 | -59.2209 | 63.0569 | -59.3079 | -59.4406 | -59.2987 | -0.082397 | -0.096131 | -0.05951 | 0.10529 | -0.27008 | -0.27466 | -0.18768 | -0.19226 | 0.018311 | -0.12817 | -0.07782 | -0.068664 | -0.059509 | -0.20142 | -0.07782 | -0.21973 | 0.18768 | 122.3969 | -0.086975 | 122.2778 | 122.3602 | 122.2275 | 122.2778 | 122.2458 | -122.4564 | -122.3557 | 122.3145 | 122.2961 | 59.1934 | 59.1476
686.3125 | 122.5067 | -59.2209 | 63.121 | -0.012436 | 0.0024076 | 0.064016 | 0.060449 | 0.00034182 | -0.0010382 | -0.00093566 | -0.20447 | 0.0041955 | 0.065448 | 0.072034 | -0.00505 | 0.0083697 | -0.0007456 | -0.10986 | 63.0203 | -59.3399 | 63.002 | -59.2163 | -59.5734 | -59.5505 | -0.041199 | 62.9379 | -59.2438 | 63.0661 | -59.3399 | -59.4177 | -59.2758 | -0.11902 | -0.10071 | -0.11902 | 0.004577 | -0.32959 | -0.35248 | -0.21057 | -0.23346 | -0.022888 | -0.18311 | -0.054932 | -0.11902 | -0.054932 | -0.19684 | -0.032044 | -0.17395 | 0.1236 | 122.3419 | -0.096131 | 122.3099 | 122.3602 | 122.1817 | 122.2412 | 122.1588 | -122.4609 | -122.3648 | 122.2229 | 122.287 | 59.111 | 59.1797
687.3125 | 122.6028 | -59.2026 | 63.0569 | -0.073471 | 0.002194 | 0.063162 | 0.060663 | 0.0016236 | 2.9842e-05 | -0.0013629 | 0.024414 | 0.0016321 | 0.06737 | 0.056439 | -0.0054774 | 0.0090105 | -0.0009592 | -0.059509 | 62.9929 | -59.2941 | 63.1439 | -59.0378 | -59.4315 | -59.4131 | -0.009155 | 62.9425 | -59.2392 | 63.1714 | -59.2026 | -59.3124 | -59.2117 | -0.091552 | -0.064087 | 0.086975 | 0.16479 | -0.21057 | -0.22888 | -0.11902 | -0.13733 | -0.036621 | -0.11444 | 0.11444 | 0 | -0.009155 | -0.10986 | 0.027466 | -0.073242 | 0.25635 | 122.438 | 0.036621 | 122.4106 | 122.287 | 122.1817 | 122.1954 | 122.1451 | -122.3511 | -122.2961 | 122.3465 | 122.374 | 59.1431 | 59.1934
688.3125 | 122.5204 | -59.2072 | 63.121 | -0.073471 | 0.003262 | 0.062521 | 0.060235 | -0.0028626 | -0.00232 | -0.00093566 | -0.05188 | 0.0024865 | 0.068011 | 0.056226 | -0.003982 | 0.0077289 | -0.0022408 | -0.027466 | 63.0432 | -59.317 | 63.0707 | -59.1431 | -59.5139 | -59.4955 | -0.086975 | 63.0157 | -59.2484 | 63.0798 | -59.3033 | -59.4269 | -59.3033 | -0.10986 | -0.07782 | -0.050354 | 0.064087 | -0.28839 | -0.3067 | -0.17853 | -0.19684 | -0.041199 | -0.10529 | -0.041199 | -0.096131 | -0.096131 | -0.21973 | -0.054932 | -0.17853 | 0.17395 | 122.3877 | -0.054932 | 122.3282 | 122.3602 | 122.2641 | 122.2504 | 122.2229 | -122.4381 | -122.3694 | 122.2778 | 122.287 | 59.1797 | 59.1202
689.3125 | 122.4976 | -59.2346 | 63.121 | -0.081101 | 0.003262 | 0.065298 | 0.062585 | 0.00098262 | -0.0036018 | 0.00055974 | -0.045776 | 0.0033411 | 0.065875 | 0.062634 | -0.0048364 | 0.0083697 | -0.0016 | -0.045776 | 63.0341 | -59.3124 | 63.0707 | -59.1339 | -59.5139 | -59.4955 | -0.073242 | 63.0203 | -59.2484 | 63.089 | -59.2896 | -59.4406 | -59.3124 | -0.07782 | -0.086975 | -0.050354 | 0.10071 | -0.26093 | -0.27924 | -0.18311 | -0.20142 | -0.013733 | -0.10071 | -0.032044 | -0.054932 | -0.07782 | -0.20599 | -0.064087 | -0.19226 | 0.17853 | 122.3831 | -0.041199 | 122.3373 | 122.3465 | 122.2687 | 122.2687 | 122.2549 | -122.4335 | -122.3694 | 122.3053 | 122.3236 | 59.1888 | 59.1614
690.3125 | 122.525 | -59.2438 | 63.121 | -0.065842 | 0.0028348 | 0.063376 | 0.060235 | -0.0030762 | -0.0014654 | -0.0020039 | -0.027466 | 0.0020593 | 0.066089 | 0.057935 | -0.0063318 | 0.0092241 | 0.0007498 | -0.018311 | 63.0524 | -59.3033 | 63.1348 | -59.0652 | -59.4498 | -59.4269 | 0.009155 | 63.0112 | -59.2072 | 63.1348 | -59.2346 | -59.3765 | -59.2484 | -0.05951 | -0.068665 | 0.013733 | 0.17853 | -0.18311 | -0.20599 | -0.1236 | -0.14648 | 0.036621 | -0.10986 | 0.013733 | 0.009155 | -0.004578 | -0.13275 | -0.041199 | -0.16937 | 0.23804 | 122.4381 | -0.027466 | 122.3419 | 122.3557 | 122.2183 | 122.2961 | 122.2549 | -122.4243 | -122.3282 | 122.3785 | 122.3785 | 59.2255 | 59.2529
691.3125 | 122.6028 | -59.2117 | 63.0707 | -0.073471 | 0.002194 | 0.063376 | 0.062585 | -0.00093998 | -0.0010382 | -0.00093566 | -0.0061035 | 0.0012047 | 0.066089 | 0.060498 | -0.005691 | 0.0090105 | 0.0020316 | -0.091553 | 63.0203 | -59.3308 | 63.0707 | -59.1339 | -59.523 | -59.5001 | -0.10071 | 62.97 | -59.2438 | 63.1302 | -59.2346 | -59.3628 | -59.2392 | -0.11902 | -0.050354 | 0 | 0.07782 | -0.28839 | -0.31128 | -0.16937 | -0.19226 | -0.032043 | -0.10071 | 0.059509 | -0.022888 | -0.027466 | -0.15106 | 0.004577 | -0.11902 | 0.19684 | 122.4014 | 0.009155 | 122.374 | 122.3511 | 122.2137 | 122.2321 | 122.1817 | -122.4014 | -122.3145 | 122.2824 | 122.3419 | 59.1202 | 59.111
692.3125 | 122.493 | -59.2438 | 63.0844 | 0.018082 | 0.0009122 | 0.065085 | 0.063226 | 0.00012822 | -0.0029608 | -0.0047809 | -0.012207 | 0.0031273 | 0.068866 | 0.059216 | -0.005691 | 0.0055927 | -0.0013864 | -0.07782 | 63.0569 | -59.3399 | 63.0203 | -59.2117 | -59.5825 | -59.5505 | -0.13733 | 62.9929 | -59.2163 | 63.0798 | -59.3079 | -59.4406 | -59.3033 | -0.096131 | -0.027466 | -0.064087 | 0.032043 | -0.3067 | -0.33875 | -0.21057 | -0.24262 | 0.027465 | -0.091553 | -0.004578 | -0.064087 | -0.05951 | -0.19684 | -0.086975 | -0.2243 | 0.12817 | 122.3602 | -0.091552 | 122.2961 | 122.3969 | 122.2092 | 122.3007 | 122.2366 | -122.4243 | -122.3007 | 122.2641 | 122.3236 | 59.166 | 59.1064
693.3125 | 122.493 | -59.2438 | 63.1256 | -0.027695 | 0.003262 | 0.063589 | 0.060663 | -0.00093998 | -0.004029 | -0.00029486 | -0.039673 | 0.0016321 | 0.069079 | 0.063275 | -0.0065454 | 0.0081561 | -0.0024546 | -0.068665 | 63.0432 | -59.3124 | 63.0524 | -59.1888 | -59.5596 | -59.523 | -0.15106 | 63.0112 | -59.2529 | 63.0478 | -59.3445 | -59.4772 | -59.317 | -0.068665 | -0.082397 | -0.073242 | 0.054931 | -0.27924 | -0.31586 | -0.21057 | -0.24719 | -0.009156 | -0.11444 | -0.077819 | -0.10071 | -0.073243 | -0.23346 | -0.064087 | -0.2243 | 0.1236 | 122.3648 | -0.091552 | 122.3007 | 122.3557 | 122.2641 | 122.287 | 122.2549 | -122.438 | -122.3785 | 122.2961 | 122.2916 | 59.1751 | 59.0927
694.3125 | 122.5067 | -59.2667 | 63.1165 | -0.40154 | 0.0051846 | 0.064657 | 0.061944 | -0.0015808 | -0.0010382 | -0.00029486 | -0.045776 | 0.0027001 | 0.06438 | 0.056866 | -0.0046228 | 0.0075153 | -0.0035226 | -0.19684 | 62.9745 | -59.3582 | 63.0432 | -59.2346 | -59.5596 | -59.5184 | -0.16022 | 62.9929 | -59.2392 | 63.0615 | -59.3399 | -59.4543 | -59.3216 | -0.091552 | -0.14191 | -0.073242 | 0.032044 | -0.25177 | -0.29297 | -0.16022 | -0.20142 | 0.027466 | -0.1236 | -0.054932 | -0.073242 | -0.054931 | -0.18768 | -0.082397 | -0.21515 | 0.1236 | 122.4014 | -0.10071 | 122.3007 | 122.3328 | 122.2321 | 122.2412 | 122.2595 | -122.4747 | -122.3557 | 122.3099 | 122.3282 | 59.0698 | 59.1064
695.3125 | 122.4838 | -59.2484 | 63.1165 | -0.081101 | 0.0017666 | 0.062948 | 0.061731 | 0.00098262 | -0.0025336 | -0.00072206 | -0.027466 | 0.0031273 | 0.065875 | 0.064343 | -0.0061182 | 0.010079 | -0.0039498 | -0.059509 | 63.0753 | -59.3216 | 63.0615 | -59.166 | -59.5505 | -59.5184 | -0.13275 | 63.0112 | -59.2438 | 63.0569 | -59.317 | -59.4543 | -59.3124 | -0.073242 | -0.041199 | -0.054932 | 0.082397 | -0.27008 | -0.30212 | -0.19684 | -0.22888 | 0.004578 | -0.10529 | -0.059509 | -0.068665 | -0.064087 | -0.20599 | -0.068665 | -0.21057 | 0.15564 | 122.3831 | -0.073243 | 122.3007 | 122.3969 | 122.2549 | 122.3236 | 122.2595 | -122.438 | -122.3602 | 122.3099 | 122.3053 | 59.1888 | 59.1156
696.3125 | 122.5159 | -59.2346 | 63.1165 | -0.073471 | 0.0028348 | 0.063376 | 0.061303 | -0.00029898 | -0.004029 | 0.0012005 | -0.042725 | 0.0037683 | 0.066516 | 0.061139 | -0.003982 | 0.010079 | -0.0011728 | -0.064087 | 63.0432 | -59.3308 | 63.0615 | -59.1568 | -59.523 | -59.5139 | -0.11444 | 63.002 | -59.2484 | 63.0432 | -59.3262 | -59.4543 | -59.3124 | -0.096131 | -0.073242 | -0.054932 | 0.07782 | -0.27924 | -0.28839 | -0.1831 | -0.19226 | -0.013733 | -0.11444 | -0.073242 | -0.091553 | -0.07782 | -0.21973 | -0.064087 | -0.20599 | 0.17395 | 122.3923 | -0.07782 | 122.2916 | 122.374 | 122.2504 | 122.2778 | 122.2366 | -122.4472 | -122.3648 | 122.2961 | 122.2778 | 59.1705 | 59.1202
697.3125 | 122.6395 | -59.2026 | 63.0615 | -0.10399 | 0.001553 | 0.063803 | 0.059381 | -0.00093998 | -0.0031744 | -0.0013629 | 0.0091553 | 0.0016321 | 0.066089 | 0.061993 | -0.0046228 | 0.0075153 | -0.003309 | -0.19684 | 62.9333 | -59.2987 | 63.1622 | -59.0424 | -59.436 | -59.3994 | -0.013733 | 62.9471 | -59.2255 | 63.1714 | -59.1888 | -59.3262 | -59.2163 | -0.09613 | -0.12817 | 0.10071 | 0.16022 | -0.19684 | -0.23346 | -0.10071 | -0.13733 | -0.022888 | -0.11444 | 0.10986 | 0.013733 | -0.013733 | -0.1236 | 0.009155 | -0.10071 | 0.25635 | 122.4609 | 0.036621 | 122.3969 | 122.2321 | 122.1725 | 122.1359 | 122.1497 | -122.3602 | -122.287 | 122.3648 | 122.374 | 59.0057 | 59.1888
698.3125 | 122.4976 | -59.2529 | 63.1302 | -0.073471 | 0.0036892 | 0.063803 | 0.064508 | -0.0028626 | -0.0021064 | 0.0012005 | -0.01831 | 0.0018457 | 0.065448 | 0.06178 | -0.0071864 | 0.0085833 | -0.0013864 | -0.050354 | 63.0341 | -59.3216 | 63.0661 | -59.1385 | -59.5093 | -59.491 | -0.07782 | 63.002 | -59.2255 | 63.0661 | -59.3079 | -59.4315 | -59.3033 | -0.068664 | -0.09613 | -0.064087 | 0.11444 | -0.23804 | -0.25635 | -0.16937 | -0.18768 | 0.027466 | -0.12817 | -0.064087 | -0.054931 | -0.050354 | -0.17853 | -0.07782 | -0.20599 | 0.1831 | 122.3877 | -0.082397 | 122.2916 | 122.3557 | 122.2275 | 122.287 | 122.2549 | -122.4518 | -122.3557 | 122.319 | 122.319 | 59.2026 | 59.1751
699.3125 | 122.525 | -59.2484 | 63.1073 | -0.08873 | 0.0034756 | 0.06658 | 0.060022 | 0.0020508 | -0.0021064 | 0.0018413 | -0.021362 | 0.0022729 | 0.066943 | 0.059644 | -0.003341 | 0.0051653 | -0.0003182 | -0.11444 | 63.0157 | -59.3491 | 63.0295 | -59.1705 | -59.5779 | -59.5413 | -0.15564 | 62.9974 | -59.2484 | 63.089 | -59.317 | -59.4269 | -59.3079 | -0.10071 | -0.091553 | -0.07782 | 0.07782 | -0.29297 | -0.32959 | -0.19226 | -0.22888 | 0 | -0.10986 | -0.018311 | -0.068665 | -0.059509 | -0.17853 | -0.059509 | -0.17853 | 0.17853 | 122.3785 | -0.068665 | 122.3373 | 122.3648 | 122.2458 | 122.2641 | 122.2458 | -122.4564 | -122.3557 | 122.2778 | 122.3373 | 59.1339 | 59.0927
700.3125 | 122.5296 | -59.23 | 63.1348 | -0.020065 | 0.0039028 | 0.062735 | 0.061517 | 0.0018372 | -0.0010382 | -0.0020039 | -0.033569 | 0.0031273 | 0.066729 | 0.067548 | -0.0020594 | 0.0077289 | -0.0016 | -0.082397 | 63.0341 | -59.3124 | 63.0295 | -59.1888 | -59.5734 | -59.5322 | -0.17853 | 63.0066 | -59.2758 | 63.1393 | -59.0469 | -59.4727 | -59.3857 | -0.082397 | -0.10071 | -0.10529 | 0.041199 | -0.30212 | -0.34332 | -0.21973 | -0.26093 | -0.045776 | -0.12817 | 0.004577 | 0.18311 | -0.15564 | -0.24261 | -0.10986 | -0.19684 | 0.1236 | 122.3419 | 0.22888 | 122.4152 | 122.3465 | 122.2824 | 122.2641 | 122.2366 | -122.4472 | -122.4106 | 122.2595 | 122.3694 | 59.1476 | 59.0515
701.3125 | 122.5159 | -59.2529 | 63.1439 | -0.0048066 | 0.002194 | 0.064657 | 0.060022 | 0.002478 | 2.9842e-05 | -0.0015765 | -0.054932 | 0.0039819 | 0.066089 | 0.061566 | -0.0048364 | 0.0085833 | -0.0043772 | -0.10986 | 63.0569 | -59.3353 | 63.0203 | -59.1934 | -59.5963 | -59.5367 | -0.15106 | 63.002 | -59.23 | 63.0753 | -59.3262 | -59.436 | -59.3124 | -0.082397 | -0.086975 | -0.1236 | 0.05951 | -0.28381 | -0.34332 | -0.20142 | -0.26093 | 0.022888 | -0.14191 | -0.068665 | -0.073242 | -0.059509 | -0.1831 | -0.082397 | -0.20599 | 0.14191 | 122.3557 | -0.09613 | 122.3053 | 122.3923 | 122.2321 | 122.3099 | 122.2549 | -122.4792 | -122.374 | 122.2733 | 122.3282 | 59.1431 | 59.1019
702.3125 | 122.5891 | -59.2163 | 63.0569 | -0.10399 | 0.0039028 | 0.064016 | 0.060022 | -8.538e-05 | -0.00232 | -0.0039265 | 0.036621 | -0.00029045 | 0.066302 | 0.059857 | -0.00505 | 0.0073015 | -0.0018136 | -0.045776 | 63.002 | -59.285 | 63.1302 | -59.0561 | -59.4589 | -59.4131 | -0.027466 | 62.9425 | -59.2117 | 63.1531 | -59.2163 | -59.3308 | -59.23 | -0.068664 | -0.054932 | 0.073242 | 0.16022 | -0.19684 | -0.24261 | -0.12817 | -0.17395 | 0.004578 | -0.11444 | 0.09613 | 0 | -0.013733 | -0.11444 | -0.018311 | -0.11902 | 0.22888 | 122.4152 | -0.004578 | 122.3648 | 122.287 | 122.1542 | 122.2183 | 122.1588 | -122.3419 | -122.2687 | 122.3465 | 122.3694 | 59.1705 | 59.1888
703.3125 | 122.5159 | -59.2346 | 63.1485 | -0.065842 | 0.003262 | 0.062094 | 0.061517 | -0.0011536 | -0.0027472 | -0.0028583 | -0.01831 | 0.0020593 | 0.067798 | 0.060071 | -0.0069726 | 0.010292 | -0.0028818 | -0.027466 | 63.0707 | -59.317 | 63.1073 | -59.0927 | -59.4864 | -59.4681 | -0.022888 | 63.0157 | -59.23 | 63.1119 | -59.2804 | -59.3994 | -59.2758 | -0.082398 | -0.07782 | -0.041199 | 0.14191 | -0.23346 | -0.25177 | -0.15106 | -0.16937 | 0.004577 | -0.13275 | -0.036622 | -0.045777 | -0.041199 | -0.16479 | -0.045776 | -0.16937 | 0.22431 | 122.4243 | -0.050354 | 122.3419 | 122.3877 | 122.2458 | 122.3053 | 122.2504 | -122.4655 | -122.3785 | 122.3419 | 122.3465 | 59.2072 | 59.2117
704.3125 | 122.4884 | -59.2392 | 63.1577 | -0.050583 | 0.002194 | 0.06188 | 0.063012 | -0.00093998 | -0.0027472 | -0.0017903 | -0.042725 | 0.0014185 | 0.068011 | 0.051312 | -0.0069726 | 0.0083697 | -0.0024546 | -0.059509 | 63.0432 | -59.3216 | 63.0615 | -59.1476 | -59.5322 | -59.5139 | -0.11444 | 63.0386 | -59.2392 | 63.0661 | -59.317 | -59.4635 | -59.3124 | -0.082397 | -0.11444 | -0.096131 | 0.091553 | -0.27466 | -0.29297 | -0.19226 | -0.21057 | 0 | -0.11902 | -0.091553 | -0.07782 | -0.073242 | -0.2243 | -0.073242 | -0.2243 | 0.17395 | 122.3831 | -0.07782 | 122.3053 | 122.3648 | 122.2778 | 122.2824 | 122.2778 | -122.4792 | -122.3969 | 122.3007 | 122.3053 | 59.1797 | 59.1248
705.3125 | 122.4792 | -59.2346 | 63.1119 | -0.065842 | 0.0019802 | 0.061453 | 0.059167 | -0.0024354 | 0.00024344 | -0.00072206 | -0.033569 | 0.0031273 | 0.065448 | 0.063702 | -0.00505 | 0.0087969 | -0.0003182 | -0.11444 | 63.0203 | -59.3353 | 62.8555 | -58.8867 | -59.23 | -59.5139 | -0.10986 | 63.0066 | -59.2392 | 63.0615 | -59.317 | -59.4864 | -59.3308 | -0.10071 | -0.091552 | -0.25635 | 0.3479 | -0.27924 | 0.004577 | -0.17853 | 0.10529 | -0.004578 | -0.10529 | -0.050354 | -0.082398 | -0.096131 | -0.25177 | -0.091553 | -0.24719 | 0.44861 | 122.1909 | -0.07782 | 122.3007 | 122.3557 | 122.2458 | 122.2549 | 122.2412 | -122.4472 | -122.3511 | 122.0901 | 122.2961 | 59.1202 | 59.1248
706.3125 | 122.5204 | -59.2529 | 63.1073 | -0.027695 | 0.0026212 | 0.063376 | 0.060663 | 0.00034182 | -0.0010382 | -0.00093566 | -0.042725 | 0.0020593 | 0.06438 | 0.060712 | -0.0046228 | 0.0081561 | 0.0039542 | -0.10071 | 63.0203 | -59.3308 | 63.0386 | -59.1705 | -59.5505 | -59.5184 | -0.13275 | 62.9974 | -59.2575 | 63.0844 | -59.2941 | -59.4269 | -59.2896 | -0.07782 | -0.086975 | -0.068665 | 0.082398 | -0.2655 | -0.29755 | -0.18768 | -0.21973 | -0.004577 | -0.10986 | -0.022888 | -0.041198 | -0.036621 | -0.17395 | -0.032044 | -0.16937 | 0.16022 | 122.3694 | -0.036621 | 122.3419 | 122.3511 | 122.2549 | 122.2733 | 122.2504 | -122.4381 | -122.3648 | 122.2916 | 122.3373 | 59.1522 | 59.1202
707.3125 | 122.6028 | -59.2026 | 63.0478 | -0.10399 | 0.0041166 | 0.064871 | 0.058526 | -0.0013672 | -0.0021064 | -0.0017903 | 0.024414 | 0.00077755 | 0.066729 | 0.056012 | -0.0044092 | 0.0077289 | -0.0011728 | -0.050354 | 62.9837 | -59.2896 | 63.1531 | -59.024 | -59.4498 | -59.4131 | 0 | 62.9745 | -59.2163 | 63.1577 | -59.198 | -59.3124 | -59.2117 | -0.086975 | -0.064087 | 0.10529 | 0.17853 | -0.21057 | -0.24719 | -0.1236 | -0.16022 | -0.013733 | -0.073243 | 0.10986 | 0.004578 | -0.009155 | -0.10986 | 0.004578 | -0.09613 | 0.2655 | 122.4426 | 0.018311 | 122.374 | 122.2733 | 122.1909 | 122.1863 | 122.1771 | -122.3373 | -122.2641 | 122.3557 | 122.3602 | 59.1522 | 59.2026
708.3125 | 122.5021 | -59.2484 | 63.1348 | -0.020065 | 0.0019802 | 0.063376 | 0.062372 | -0.00051278 | -0.00232 | -0.0013629 | -0.054932 | 0.00056395 | 0.066943 | 0.068188 | -0.005691 | 0.0094379 | -0.0016 | -0.091553 | 63.0478 | -59.3262 | 63.0295 | -59.2255 | -59.5963 | -59.5596 | -0.4303 | 62.9379 | -59.3079 | 63.0661 | -59.2575 | -59.5139 | -59.3536 | -0.07782 | -0.086975 | -0.10529 | 0.022888 | -0.31128 | -0.3479 | -0.23346 | -0.27008 | -0.059509 | -0.19684 | -0.068665 | -0.009155 | -0.10529 | -0.2655 | -0.045777 | -0.20599 | 0.10071 | 122.3557 | 0.050354 | 122.374 | 122.374 | 122.2458 | 122.2961 | 122.1863 | -122.4609 | -122.4426 | 122.2778 | 122.3145 | 59.1568 | 58.8181
709.3125 | 122.5204 | -59.2255 | 63.0936 | -0.11162 | 0.0036892 | 0.063803 | 0.061517 | -0.0030762 | -0.003388 | 0.00055974 | -0.021362 | 0.0018457 | 0.068866 | 0.055371 | -0.0052638 | 0.0087969 | -0.0026682 | -0.12817 | 63.0249 | -59.3445 | 63.0341 | -59.1888 | -59.5734 | -59.5322 | -0.15564 | 63.0112 | -59.2621 | 63.0798 | -59.2941 | -59.4177 | -59.2712 | -0.11902 | -0.068665 | -0.059509 | 0.036621 | -0.3067 | -0.3479 | -0.18768 | -0.22888 | -0.036621 | -0.082398 | -0.013733 | -0.068664 | -0.045776 | -0.19226 | -0.009155 | -0.15564 | 0.15564 | 122.3785 | -0.032043 | 122.3419 | 122.3694 | 122.2733 | 122.2504 | 122.2366 | -122.438 | -122.3557 | 122.2595 | 122.3053 | 59.0973 | 59.0698
710.3125 | 122.5388 | -59.2438 | 63.1302 | -0.058212 | 0.004971 | 0.06423 | 0.060876 | 0.0014098 | -0.0038154 | -0.00072206 | -0.039673 | 0.0012047 | 0.068438 | 0.060498 | -0.0024866 | 0.0068743 | -0.0058724 | -0.091553 | 63.0386 | -59.3353 | 63.0341 | -59.198 | -59.5825 | -59.5642 | -0.1831 | 62.9974 | -59.2667 | 63.2492 | -59.2941 | -59.5322 | -59.3536 | -0.091553 | -0.091553 | -0.09613 | 0.045776 | -0.32043 | -0.33875 | -0.22888 | -0.24719 | -0.022889 | -0.13275 | 0.11902 | -0.050354 | -0.10986 | -0.28839 | -0.086975 | -0.2655 | 0.13733 | 122.3694 | -0.027465 | 122.5159 | 122.374 | 122.2641 | 122.2824 | 122.2412 | -122.4655 | -122.3969 | 122.2778 | 122.493 | 59.1522 | 59.0607
711.3125 | 122.5525 | -59.2392 | 63.1073 | -0.058212 | 0.0041166 | 0.063589 | 0.063012 | -0.0035034 | -0.0025336 | 0.0035503 | -0.061035 | 0.0037683 | 0.065875 | 0.067975 | -0.0048364 | 0.0077289 | -0.0028818 | -0.086975 | 63.0386 | -59.3353 | 63.0203 | -59.2117 | -59.5917 | -59.5505 | -0.19226 | 63.0157 | -59.2712 | 63.208 | -59.1751 | -59.5322 | -59.3857 | -0.09613 | -0.068665 | -0.086975 | 0.027466 | -0.31128 | -0.35248 | -0.21515 | -0.25635 | -0.032043 | -0.091553 | 0.10071 | 0.064087 | -0.14648 | -0.29297 | -0.11444 | -0.26093 | 0.1236 | 122.3557 | 0.09613 | 122.4792 | 122.374 | 122.287 | 122.2778 | 122.2549 | -122.4426 | -122.3785 | 122.2595 | 122.4472 | 59.1522 | 59.0469
712.3125 | 122.612 | -59.2026 | 63.0753 | -0.11162 | 0.0043302 | 0.063162 | 0.058099 | 0.0031188 | -0.0027472 | -0.0017903 | -0.097656 | -7.6854e-05 | 0.065234 | 0.058148 | -0.006759 | 0.0092241 | 0.0009634 | -0.036621 | 62.9654 | -59.3124 | 63.1348 | -59.0469 | -59.436 | -59.3948 | 0.045776 | 62.9333 | -59.2209 | 63.2034 | -59.1888 | -59.2712 | -59.1522 | -0.10986 | -0.10986 | 0.05951 | 0.15564 | -0.19226 | -0.23346 | -0.082397 | -0.1236 | -0.01831 | -0.14191 | 0.12817 | 0.013733 | 0.050354 | -0.068664 | 0.068664 | -0.050354 | 0.2655 | 122.4472 | 0.032043 | 122.4243 | 122.2778 | 122.1542 | 122.168 | 122.1359 | -122.3877 | -122.2961 | 122.3373 | 122.406 | 59.166 | 59.2484
713.3125 | 122.5891 | -59.2255 | 63.0524 | -0.073471 | 0.000485 | 0.065085 | 0.06109 | -0.002649 | 2.9842e-05 | -0.0037129 | -0.027466 | 0.0027001 | 0.068011 | 0.057721 | -0.0078272 | 0.0079425 | -0.000532 | -0.10529 | 63.0341 | -59.3308 | 63.089 | -59.1293 | -59.5184 | -59.4864 | -0.082397 | 62.9791 | -59.2392 | 63.1439 | -59.2255 | -59.3491 | -59.2117 | -0.10529 | -0.01831 | 0.036621 | 0.096131 | -0.26093 | -0.29297 | -0.15564 | -0.18768 | -0.013733 | -0.073242 | 0.091553 | 0 | 0.013733 | -0.1236 | 0.027466 | -0.10986 | 0.20142 | 122.4197 | 0.013733 | 122.3831 | 122.3648 | 122.2183 | 122.2595 | 122.2046 | -122.3831 | -122.2916 | 122.3145 | 122.3694 | 59.1202 | 59.1431
714.3125 | 122.6074 | -59.2117 | 63.0798 | -0.065842 | 5.76e-05 | 0.06423 | 0.060449 | -0.00051278 | -0.0012518 | 0.00013254 | -0.039673 | 0.0022729 | 0.066729 | 0.064557 | -0.0069726 | 0.0087969 | 0.0022452 | -0.11444 | 63.002 | -59.3308 | 63.0844 | -59.1339 | -59.5093 | -59.4955 | -0.10071 | 62.97 | -59.2346 | 63.1393 | -59.2117 | -59.3582 | -59.2072 | -0.11902 | -0.07782 | 0.004578 | 0.07782 | -0.28381 | -0.29755 | -0.16479 | -0.17853 | -0.022888 | -0.10986 | 0.059509 | 0 | 0.004578 | -0.14648 | 0.027466 | -0.1236 | 0.19684 | 122.4152 | 0.022888 | 122.374 | 122.3328 | 122.2046 | 122.2137 | 122.1817 | -122.4106 | -122.3145 | 122.2961 | 122.3511 | 59.0973 | 59.111
715.3125 | 122.5983 | -59.2117 | 63.0753 | -0.050583 | 0.0041166 | 0.065085 | 0.059595 | -0.0022218 | -0.0038154 | -0.0011493 | -0.024414 | 0.0022729 | 0.067584 | 0.064343 | -0.0059046 | 0.0094379 | -0.0052316 | -0.10529 | 63.0203 | -59.3399 | 63.0707 | -59.1202 | -59.5139 | -59.4772 | -0.086975 | 62.9929 | -59.2163 | 63.1439 | -59.2209 | -59.3353 | -59.198 | -0.12817 | -0.054931 | -0.004577 | 0.091553 | -0.2655 | -0.30212 | -0.13733 | -0.17395 | -0.004578 | -0.082397 | 0.068665 | -0.009155 | 0.013733 | -0.1236 | 0.018311 | -0.11902 | 0.21973 | 122.4106 | -0.004577 | 122.3602 | 122.3602 | 122.2092 | 122.2321 | 122.2046 | -122.4152 | -122.2916 | 122.2824 | 122.3557 | 59.1064 | 59.1248
716.3125 | 122.5983 | -59.2072 | 63.0661 | -0.058212 | 0.0024076 | 0.061667 | 0.059381 | -0.0015808 | -0.0036018 | -0.0020039 | -0.021362 | 0.0029137 | 0.06438 | 0.060925 | -0.0061182 | 0.0090105 | -0.0020272 | -0.09613 | 63.0112 | -59.3399 | 63.0798 | -59.1339 | -59.5184 | -59.4772 | -0.082397 | 62.9791 | -59.2392 | 63.1485 | -59.2209 | -59.3399 | -59.198 | -0.13275 | -0.054932 | 0.013733 | 0.073242 | -0.27008 | -0.31128 | -0.13733 | -0.17853 | -0.032044 | -0.086975 | 0.082398 | -0.013733 | 0.009155 | -0.13275 | 0.041199 | -0.10071 | 0.20599 | 122.4197 | 0.018311 | 122.3877 | 122.3511 | 122.2183 | 122.2183 | 122.1863 | -122.406 | -122.3053 | 122.287 | 122.3557 | 59.111 | 59.1248
717.3125 | 122.5983 | -59.2026 | 63.0798 | -0.020065 | 0.0030484 | 0.06423 | 0.057672 | 0.0011962 | -0.00232 | -0.0028583 | 0.05188 | 0.00035035 | 0.067157 | 0.063275 | -0.0061182 | 0.0077289 | -0.0016 | -0.073242 | 63.0066 | -59.2758 | 63.1165 | -59.0881 | -59.5093 | -59.4315 | -0.064087 | 62.9562 | -59.2072 | 63.1256 | -59.23 | -59.3491 | -59.2255 | -0.073242 | -0.073242 | 0.036621 | 0.11444 | -0.22888 | -0.3067 | -0.15564 | -0.23346 | -0.004577 | -0.1236 | 0.045776 | -0.027466 | -0.022888 | -0.14648 | -0.018311 | -0.14191 | 0.18768 | 122.3923 | -0.022889 | 122.3328 | 122.2824 | 122.1634 | 122.2092 | 122.1588 | -122.3557 | -122.287 | 122.319 | 122.3282 | 59.1293 | 59.1385
718.3125 | 122.4792 | -59.23 | 63.1119 | -0.065842 | 0.002194 | 0.064016 | 0.063226 | -0.0032898 | -0.0046698 | 0.0012005 | -0.094604 | 0.0027001 | 0.066516 | 0.061139 | -0.0082544 | 0.0092241 | -0.0020272 | -0.09613 | 63.0432 | -59.3216 | 63.0341 | -59.198 | -59.5917 | -59.5505 | 0 | 63.0066 | -59.2667 | 63.002 | -59.2941 | -59.404 | -59.317 | -0.091552 | -0.068664 | -0.077819 | 0.032044 | -0.32043 | -0.36163 | -0.22888 | -0.27008 | -0.036621 | -0.10529 | -0.10986 | -0.064086 | -0.086975 | -0.17395 | -0.050354 | -0.13733 | 0.1236 | 122.3557 | -0.027465 | 122.2687 | 122.3648 | 122.2733 | 122.2733 | 122.2366 | -122.4335 | -122.3785 | 122.2641 | 122.2321 | 59.1339 | 59.23
719.3125 | 122.5937 | -59.2209 | 63.0661 | -0.081101 | 0.0024076 | 0.066366 | 0.059595 | -0.002008 | -0.00232 | -0.0017903 | -0.0091553 | -0.0011451 | 0.067157 | 0.06413 | -0.0054774 | 0.0085833 | 0.0016044 | -0.050354 | 62.97 | -59.3079 | 63.1622 | -59.0332 | -59.4406 | -59.4086 | -0.009155 | 62.9608 | -59.2072 | 63.1851 | -59.2026 | -59.317 | -59.1843 | -0.086975 | -0.09613 | 0.09613 | 0.18768 | -0.18768 | -0.21973 | -0.10071 | -0.13275 | 0.013733 | -0.10529 | 0.11902 | 0.01831 | 0.036621 | -0.096131 | 0.022888 | -0.10986 | 0.27466 | 122.4701 | 0.004577 | 122.3923 | 122.2778 | 122.168 | 122.1909 | 122.1817 | -122.374 | -122.2733 | 122.3831 | 122.406 | 59.1705 | 59.2117
720.3125 | 122.6074 | -59.1934 | 63.0661 | -0.042954 | 0.0013394 | 0.062948 | 0.060876 | -0.00093998 | -0.003388 | -0.00050846 | 0.0061035 | 0.0012047 | 0.065448 | 0.059644 | -0.006759 | 0.0070879 | -0.0039498 | -0.027466 | 62.9929 | -59.3079 | 63.176 | -59.2896 | -59.5047 | -59.2072 | -0.059509 | 62.9745 | -59.2163 | 63.1805 | -59.1888 | -59.2987 | -59.2117 | -0.11444 | -0.073242 | 0.10986 | -0.096131 | -0.013733 | -0.31128 | 0.10071 | -0.19684 | -0.022889 | -0.091553 | 0.11444 | 0.004577 | -0.018311 | -0.10529 | 0.004578 | -0.082397 | 0.01831 | 122.4838 | 0.027466 | 122.3969 | 122.3007 | 122.1909 | 122.1863 | 122.168 | -122.374 | -122.2824 | 122.3694 | 122.374 | 59.166 | 59.1339
721.3125 | 122.5891 | -59.198 | 63.0615 | -0.050583 | 0.0036892 | 0.063589 | 0.05874 | -0.0015808 | -0.00039736 | -0.0015765 | 0.0091553 | 0.00077755 | 0.065875 | 0.065198 | -0.0078272 | 0.011361 | -0.0045908 | -0.032043 | 62.97 | -59.3124 | 63.1989 | -59.2438 | -59.5734 | -59.23 | -0.082397 | 62.9562 | -59.198 | 63.1714 | -59.2072 | -59.3124 | -59.198 | -0.11444 | -0.091552 | 0.13733 | -0.045776 | -0.032044 | -0.37537 | 0.082397 | -0.26093 | 0 | -0.10529 | 0.10986 | -0.009155 | 0 | -0.11444 | 0 | -0.11444 | 0.068665 | 122.5113 | -0.009155 | 122.3694 | 122.2824 | 122.1542 | 122.168 | 122.1542 | -122.374 | -122.2595 | 122.3969 | 122.3694 | 59.166 | 59.1156
722.3125 | 122.5662 | -59.2072 | 63.0936 | -0.058212 | 0.0028348 | 0.063162 | 0.060449 | -0.00029898 | -0.0036018 | 0.00098694 | 0.024414 | 0.0031273 | 0.067157 | 0.060498 | -0.0052638 | 0.0055927 | -0.0082224 | -0.12817 | 63.0066 | -59.285 | 63.1302 | -59.1385 | -59.4269 | -59.4223 | -0.050354 | 62.9745 | -59.2209 | 63.1393 | -59.2072 | -59.3491 | -59.2117 | -0.07782 | -0.086975 | 0.036621 | 0.068664 | -0.21515 | -0.21973 | -0.13733 | -0.14191 | -0.013733 | -0.11902 | 0.045776 | 0 | -0.004578 | -0.14191 | 0.009155 | -0.12817 | 0.14648 | 122.4152 | 0.013733 | 122.3602 | 122.2916 | 122.1954 | 122.2137 | 122.1817 | -122.3785 | -122.3145 | 122.3373 | 122.3465 | 59.079 | 59.1568
723.3125 | 122.6028 | -59.198 | 63.0753 | -0.096359 | 0.0047574 | 0.065085 | 0.063012 | 0.0018372 | -0.0025336 | 0.00077334 | -0.088501 | 0.0016321 | 0.067157 | 0.068829 | -0.005691 | 0.010079 | -0.0013864 | -0.09613 | 63.0249 | -59.3582 | 63.0753 | -59.1385 | -59.5184 | -59.4772 | -0.086975 | 62.9791 | -59.2575 | 63.1485 | -59.2209 | -59.3445 | -59.2117 | -0.16022 | -0.050354 | 0 | 0.059509 | -0.27924 | -0.32044 | -0.11902 | -0.16022 | -0.059509 | -0.09613 | 0.073243 | -0.022888 | -0.013733 | -0.14648 | 0.045776 | -0.086975 | 0.21973 | 122.4335 | 0.036621 | 122.406 | 122.3831 | 122.2366 | 122.2229 | 122.1771 | -122.4335 | -122.3328 | 122.2733 | 122.3465 | 59.1019 | 59.111
724.3125 | 122.5983 | -59.2255 | 63.0524 | -0.081101 | 0.003262 | 0.064444 | 0.059595 | -0.0013672 | -0.0016792 | 0.00098694 | -0.064087 | 0.0029137 | 0.06502 | 0.061352 | -0.0041956 | 0.0090105 | -0.0080088 | -0.10529 | 63.0157 | -59.3262 | 63.0615 | -59.1339 | -59.5276 | -59.4864 | -0.10529 | 62.9883 | -59.2575 | 63.1485 | -59.23 | -59.3719 | -59.2163 | -0.10071 | -0.036621 | 0.009155 | 0.091553 | -0.26093 | -0.30212 | -0.16022 | -0.20142 | -0.032043 | -0.064087 | 0.096131 | -0.004578 | 0.009155 | -0.14648 | 0.041198 | -0.11444 | 0.19226 | 122.3877 | 0.027465 | 122.406 | 122.3419 | 122.2458 | 122.2412 | 122.2137 | -122.3785 | -122.3099 | 122.287 | 122.374 | 59.1202 | 59.1202
725.3125 | 122.5983 | -59.23 | 63.0615 | -0.020065 | 0.0034756 | 0.065298 | 0.06109 | 0.0014098 | -0.00039736 | -0.0015765 | -0.054932 | 0.0020593 | 0.066943 | 0.063702 | -0.0037684 | 0.01072 | -0.0062998 | -0.10986 | 63.0249 | -59.3399 | 63.0753 | -59.1339 | -59.5322 | -59.491 | -0.11444 | 62.9837 | -59.2346 | 63.1348 | -59.2484 | -59.3628 | -59.2484 | -0.10986 | -0.036621 | 0.013733 | 0.096131 | -0.26093 | -0.30212 | -0.15106 | -0.19226 | -0.004577 | -0.077819 | 0.073243 | -0.01831 | -0.01831 | -0.13275 | -0.013733 | -0.12817 | 0.20599 | 122.4152 | -0.013733 | 122.3694 | 122.3648 | 122.2183 | 122.2549 | 122.2137 | -122.4014 | -122.2961 | 122.3053 | 122.3648 | 59.1202 | 59.1156
726.3125 | 122.5891 | -59.2163 | 63.0661 | -0.020065 | 0.0034756 | 0.064444 | 0.060022 | 0.00098262 | -0.00018376 | -0.0026447 | 0.021362 | 0.0027001 | 0.066516 | 0.058148 | -0.0059046 | 0.0070879 | -0.0013864 | -0.068665 | 62.9837 | -59.2941 | 63.1439 | -59.0607 | -59.4772 | -59.4269 | -0.059509 | 62.9791 | -59.2163 | 63.1348 | -59.2209 | -59.3399 | -59.2163 | -0.077819 | -0.082397 | 0.07782 | 0.15564 | -0.21057 | -0.26093 | -0.13275 | -0.18311 | 0 | -0.086975 | 0.068665 | -0.004577 | 0 | -0.1236 | 0 | -0.1236 | 0.23346 | 122.438 | -0.004577 | 122.3511 | 122.2778 | 122.1954 | 122.2 | 122.1954 | -122.3602 | -122.2824 | 122.3602 | 122.3511 | 59.1476 | 59.1568
727.3125 | 122.6669 | -59.166 | 63.089 | -0.035324 | 0.001553 | 0.062308 | 0.06109 | -0.005426 | -0.0025336 | 0.0012005 | 0.039673 | -0.00093145 | 0.066302 | 0.05238 | -0.00505 | 0.0087969 | 0.000109 | -0.018311 | 63.0295 | -59.2758 | 63.1805 | -59.024 | -59.3994 | -59.3674 | 0.064087 | 62.97 | -59.2072 | 63.2309 | -59.1248 | -59.23 | -59.1614 | -0.10986 | -0.059509 | 0.091553 | 0.14191 | -0.20142 | -0.23346 | -0.091553 | -0.1236 | -0.041198 | -0.11902 | 0.14191 | 0.041199 | 0.004578 | -0.064087 | 0.045776 | -0.022889 | 0.25177 | 122.4564 | 0.082397 | 122.438 | 122.3053 | 122.1771 | 122.1954 | 122.1359 | -122.3648 | -122.2961 | 122.3465 | 122.3969 | 59.1476 | 59.23
728.3125 | 122.6028 | -59.1888 | 63.0798 | -0.10399 | 0.0039028 | 0.062948 | 0.060235 | 0.0054688 | -0.0021064 | -8.1264e-05 | -0.036621 | 0.0024865 | 0.065448 | 0.062848 | -0.005691 | 0.0096515 | -0.0018136 | -0.054932 | 63.002 | -59.3262 | 63.1577 | -59.0607 | -59.4543 | -59.4177 | -0.027466 | 62.9517 | -59.2072 | 63.0615 | -59.2163 | -59.0469 | -58.9783 | -0.13733 | -0.07782 | 0.07782 | 0.12817 | -0.22888 | -0.2655 | -0.091553 | -0.12817 | -0.01831 | -0.12817 | -0.018311 | -0.027466 | 0.21057 | 0.14191 | 0.22888 | 0.16022 | 0.2655 | 122.4838 | -0.009156 | 122.2687 | 122.3282 | 122.1588 | 122.1909 | 122.1405 | -122.406 | -122.287 | 122.3465 | 122.2504 | 59.1339 | 59.1614
729.3125 | 122.6257 | -59.2346 | 63.0569 | -0.096359 | 0.002194 | 0.06423 | 0.059595 | 0.002478 | -0.0031744 | 0.00034614 | -0.039673 | 0.0012047 | 0.064593 | 0.058362 | -0.008468 | 0.0096515 | -0.0060862 | -0.036621 | 62.9745 | -59.2896 | 63.1668 | -59.0286 | -59.4635 | -59.4269 | -0.009155 | 62.9608 | -59.2163 | 63.176 | -59.1934 | -59.2804 | -59.2026 | -0.054932 | -0.082398 | 0.10986 | 0.20599 | -0.19226 | -0.22888 | -0.13733 | -0.17395 | 0.01831 | -0.096131 | 0.11902 | 0.041199 | 0.032043 | -0.045777 | 0.013733 | -0.064087 | 0.26093 | 122.4564 | 0.022889 | 122.3923 | 122.2641 | 122.1771 | 122.2092 | 122.1954 | -122.3465 | -122.2733 | 122.4014 | 122.4106 | 59.198 | 59.2255
730.3125 | 122.6166 | -59.2163 | 63.0661 | 0.071487 | 0.0043302 | 0.065725 | 0.060235 | -0.0047852 | -0.00232 | -0.0024311 | -0.039673 | 0.0018457 | 0.065234 | 0.065625 | -0.0052638 | 0.0090105 | -0.0020272 | -0.036621 | 63.0066 | -59.2758 | 63.1714 | -59.0561 | -59.4406 | -59.3857 | -0.027466 | 62.9562 | -59.198 | 63.1714 | -59.1705 | -59.3124 | -59.1751 | -0.059509 | -0.059509 | 0.10529 | 0.16022 | -0.16937 | -0.2243 | -0.10986 | -0.16479 | 0.018311 | -0.10986 | 0.10529 | 0.045777 | 0.041199 | -0.09613 | 0.022888 | -0.11444 | 0.21973 | 122.4472 | 0.027466 | 122.3694 | 122.2824 | 122.1542 | 122.2229 | 122.1725 | -122.3419 | -122.2641 | 122.3877 | 122.3877 | 59.1797 | 59.1888
731.3125 | 122.6028 | -59.2026 | 63.0798 | -0.020065 | 0.002194 | 0.065085 | 0.062799 | 0.00076902 | -0.0044562 | -0.0013629 | -0.064087 | 0.0024865 | 0.065234 | 0.070325 | -0.005691 | 0.0094379 | -0.0035226 | -0.091553 | 63.0203 | -59.3079 | 63.121 | -59.1019 | -59.4864 | -59.4406 | -0.050354 | 62.9837 | -59.2346 | 63.1897 | -59.2072 | -59.3308 | -59.198 | -0.10529 | -0.059509 | 0.041199 | 0.10071 | -0.23804 | -0.28381 | -0.13275 | -0.17853 | -0.032043 | -0.09613 | 0.10986 | -0.004577 | 0.004578 | -0.12817 | 0.036621 | -0.096131 | 0.20599 | 122.4289 | 0.027466 | 122.4243 | 122.3282 | 122.2183 | 122.2229 | 122.1863 | -122.3877 | -122.3145 | 122.3236 | 122.3923 | 59.111 | 59.1522
732.3125 | 122.612 | -59.1888 | 63.0936 | -0.065842 | 0.0028348 | 0.062308 | 0.060235 | -0.0022218 | -0.0044562 | -0.00050846 | 0.039673 | 0.0016321 | 0.065448 | 0.059857 | -0.0044092 | 0.0083697 | 0.0009634 | -0.036621 | 63.0249 | -59.2758 | 63.1439 | -59.0469 | -59.4177 | -59.3903 | 0.009155 | 62.9929 | -59.2209 | 63.1714 | -59.1476 | -59.2804 | -59.166 | -0.086975 | -0.068665 | 0.050354 | 0.14191 | -0.20142 | -0.22888 | -0.11444 | -0.14191 | -0.032043 | -0.10071 | 0.07782 | 0.041199 | 0.022888 | -0.091553 | 0.054931 | -0.05951 | 0.22888 | 122.4197 | 0.073242 | 122.3923 | 122.3007 | 122.2137 | 122.2137 | 122.1817 | -122.3694 | -122.3145 | 122.3328 | 122.3602 | 59.1522 | 59.198
733.3125 | 122.5983 | -59.198 | 63.0661 | -0.11925 | 0.004971 | 0.065085 | 0.061303 | -0.00093998 | -0.00082456 | -0.00072206 | -0.076294 | -7.6854e-05 | 0.063952 | 0.06477 | -0.005691 | 0.0085833 | -0.0069406 | -0.032043 | 62.9608 | -59.2987 | 63.1577 | -59.0515 | -59.4315 | -59.5642 | 0.18768 | 62.9745 | -59.1888 | 63.1943 | -59.166 | -59.2896 | -59.1751 | -0.10071 | -0.10529 | 0.091553 | 0.14648 | -0.36621 | -0.23346 | -0.2655 | -0.13275 | 0.009155 | -0.091553 | 0.12817 | 0.032043 | 0.022888 | -0.091553 | 0.013733 | -0.10071 | 0.24719 | 122.4564 | 0.022888 | 122.3831 | 122.2595 | 122.1634 | 122.1588 | 122.1725 | -122.3648 | -122.2549 | 122.3557 | 122.3923 | 59.166 | 59.3857
734.3125 | 122.493 | -59.2026 | 63.1393 | -0.11925 | 0.0036892 | 0.060171 | 0.058954 | -0.002649 | -0.00082456 | 0.00034614 | -0.039673 | 0.0033411 | 0.066089 | 0.062207 | -0.00505 | 0.0068743 | -0.0024546 | 0.018311 | 63.0524 | -59.2804 | 63.0844 | -59.1202 | -59.4772 | -59.4772 | -0.041199 | 63.0478 | -59.2255 | 63.1073 | -59.2621 | -59.3811 | -59.285 | -0.07782 | -0.086975 | -0.054931 | 0.082398 | -0.27466 | -0.27466 | -0.19684 | -0.19684 | -0.022888 | -0.091552 | -0.032043 | -0.059509 | -0.082397 | -0.17853 | -0.059509 | -0.15564 | 0.16022 | 122.3648 | -0.036621 | 122.3328 | 122.3328 | 122.2733 | 122.2549 | 122.2504 | -122.4197 | -122.3648 | 122.287 | 122.3099 | 59.2209 | 59.1614
735.3125 | 122.6761 | -59.23 | 63.1165 | -0.10399 | 0.0011258 | 0.065085 | 0.06109 | 0.0029052 | -0.0038154 | -0.0037129 | -0.064087 | 0.0012047 | 0.063739 | 0.060712 | -0.0048364 | 0.010506 | -0.0018136 | -0.068665 | 62.9974 | -59.3491 | 63.121 | -59.0698 | -59.4223 | -59.4131 | -0.032043 | 62.9471 | -59.198 | 63.1943 | -59.1751 | -59.5734 | -59.3353 | -0.11902 | -0.11902 | 0.004578 | 0.16022 | -0.18311 | -0.19226 | -0.064087 | -0.073242 | 0.032044 | -0.16937 | 0.07782 | 0.054932 | -0.10529 | -0.34332 | -0.13733 | -0.37537 | 0.27924 | 122.4701 | 0.022888 | 122.3923 | 122.3465 | 122.1451 | 122.2275 | 122.1771 | -122.4655 | -122.3145 | 122.3511 | 122.4243 | 59.1614 | 59.198
736.3125 | 122.5983 | -59.198 | 63.0661 | 0.025711 | 0.0028348 | 0.064871 | 0.059595 | 0.00076902 | -0.0014654 | -0.0017903 | -0.0091553 | 0.0014185 | 0.062671 | 0.05943 | -0.0031274 | 0.0096515 | 0.0003226 | 0.041199 | 62.9929 | -59.2758 | 63.1668 | -59.0378 | -59.4406 | -59.3948 | -0.022888 | 62.9608 | -59.2163 | 63.1714 | -59.1797 | -59.3124 | -59.1751 | -0.07782 | -0.073242 | 0.10071 | 0.16022 | -0.19684 | -0.24262 | -0.11902 | -0.16479 | -0.018311 | -0.10529 | 0.10529 | 0.018311 | 0.022888 | -0.11444 | 0.041199 | -0.09613 | 0.23804 | 122.4426 | 0.036622 | 122.3877 | 122.2687 | 122.1771 | 122.1909 | 122.1588 | -122.3419 | -122.2824 | 122.3648 | 122.3694 | 59.2392 | 59.1751
737.3125 | 122.5754 | -59.2163 | 63.0844 | -0.081101 | 0.0034756 | 0.063803 | 0.056817 | 0.00012822 | -0.0025336 | 0.0029095 | 0.024414 | 0.0012047 | 0.066302 | 0.054303 | -0.00505 | 0.0070879 | -0.0026682 | -0.068665 | 63.0112 | -59.317 | 63.1119 | -59.1019 | -59.4727 | -59.436 | -0.050354 | 62.9791 | -59.2209 | 63.1393 | -59.2117 | -59.3216 | -59.1934 | -0.10071 | -0.073243 | 0.027465 | 0.11444 | -0.21973 | -0.25635 | -0.11902 | -0.15564 | -0.004577 | -0.10529 | 0.054931 | 0.004578 | 0.022889 | -0.10528 | 0.027466 | -0.10071 | 0.21515 | 122.4289 | 0.009155 | 122.3602 | 122.3282 | 122.2 | 122.2275 | 122.1954 | -122.4014 | -122.3053 | 122.3282 | 122.3557 | 59.1476 | 59.166
738.3125 | 122.5342 | -59.2529 | 63.0981 | -0.050583 | 0.0036892 | 0.063589 | 0.062585 | 0.0018372 | -0.0027472 | 0.0033367 | -0.085449 | 0.0041955 | 0.068438 | 0.063489 | -0.0048364 | 0.010933 | -0.000532 | -0.10986 | 63.0295 | -59.3353 | 63.0386 | -59.1797 | -59.5779 | -59.5276 | -0.14648 | 63.0066 | -59.2438 | 63.0936 | -59.2987 | -59.4177 | -59.2941 | -0.082397 | -0.068665 | -0.05951 | 0.073243 | -0.27466 | -0.32501 | -0.19226 | -0.24262 | 0.009156 | -0.091553 | -0.004578 | -0.045776 | -0.041198 | -0.16479 | -0.050354 | -0.17395 | 0.15564 | 122.374 | -0.054932 | 122.3373 | 122.3648 | 122.2504 | 122.2824 | 122.2595 | -122.4335 | -122.3419 | 122.2916 | 122.3465 | 59.1431 | 59.1064
739.3125 | 122.6395 | -59.1888 | 63.1027 | -0.042954 | 0.0028348 | 0.062948 | 0.060235 | -0.00051278 | -0.0012518 | -0.0020039 | 0.015259 | 0.0014185 | 0.065875 | 0.060284 | -0.0048364 | 0.0087969 | -0.0026682 | 0.086975 | 63.0615 | -59.2026 | 63.2263 | -59.0561 | -59.3262 | -59.2987 | 0.10071 | 62.9837 | -59.1614 | 63.2126 | -59.1293 | -59.2529 | -59.1568 | -0.013733 | -0.041199 | 0.1236 | 0.13275 | -0.10986 | -0.13733 | -0.09613 | -0.1236 | 0.027466 | -0.11902 | 0.10986 | 0.05951 | 0.032044 | -0.064087 | 0.004578 | -0.091553 | 0.14648 | 122.4289 | 0.032044 | 122.374 | 122.2641 | 122.1451 | 122.2504 | 122.1725 | -122.3053 | -122.2641 | 122.4152 | 122.4014 | 59.2758 | 59.2896
740.3125 | 122.7036 | -59.2117 | 63.0798 | -0.08873 | 0.0013394 | 0.062948 | 0.062799 | 0.0056824 | -0.0042426 | -0.0011493 | -0.048828 | 0.0012047 | 0.065661 | 0.05943 | -0.00505 | 0.0081561 | 0.000109 | -0.068665 | 62.9883 | -59.317 | 63.1485 | -59.0515 | -59.4543 | -59.4177 | -0.027466 | 62.97 | -59.2255 | 63.2721 | -59.2896 | -59.5413 | -59.2438 | -0.10529 | -0.091553 | 0.068665 | 0.16022 | -0.20599 | -0.24262 | -0.10071 | -0.13733 | -0.013733 | -0.10986 | 0.19226 | -0.07782 | -0.032043 | -0.32959 | -0.01831 | -0.31586 | 0.2655 | 122.4655 | -0.064087 | 122.4976 | 122.3053 | 122.1954 | 122.2 | 122.1817 | -122.3969 | -122.3053 | 122.3602 | 122.4838 | 59.1431 | 59.1843
741.3125 | 122.6395 | -59.2026 | 63.0524 | -0.0048066 | -0.0007968 | 0.063376 | 0.060022 | 0.0048278 | -0.0021064 | -0.0017903 | -0.01831 | 0.0012047 | 0.066302 | 0.066052 | -0.005691 | 0.0081561 | -0.0043772 | 0.064087 | 62.9883 | -59.2896 | 63.1714 | -59.0332 | -59.4406 | -59.3994 | -0.027466 | 62.9654 | -59.2117 | 63.1989 | -59.1843 | -59.2941 | -59.1843 | -0.086975 | -0.064087 | 0.11902 | 0.16937 | -0.19684 | -0.23804 | -0.10986 | -0.15106 | -0.009155 | -0.086975 | 0.14648 | 0.018311 | 0.018311 | -0.091552 | 0.027466 | -0.082397 | 0.25635 | 122.4609 | 0.027466 | 122.4106 | 122.2778 | 122.1771 | 122.1909 | 122.168 | -122.3419 | -122.2641 | 122.374 | 122.4014 | 59.2667 | 59.1751
742.3125 | 122.6624 | -59.198 | 63.089 | -0.012436 | 0.0024076 | 0.063589 | 0.057886 | -0.004358 | -0.0016792 | 0.00013254 | 0.030518 | 0.0012047 | 0.068011 | 0.058148 | -0.0046228 | 0.0055927 | 0.0016044 | 0.013733 | 63.0249 | -59.2621 | 63.2126 | -58.9691 | -59.3445 | -59.3262 | 0.1236 | 62.9745 | -59.1705 | 63.4872 | -59.3765 | -59.5825 | -59.317 | -0.064087 | -0.064087 | 0.1236 | 0.22888 | -0.12817 | -0.14648 | -0.064087 | -0.082397 | 0.027466 | -0.11444 | 0.39825 | -0.17853 | -0.11902 | -0.38452 | -0.14648 | -0.41199 | 0.29297 | 122.4747 | -0.20599 | 122.6578 | 122.287 | 122.1451 | 122.2229 | 122.1725 | -122.3511 | -122.2595 | 122.4106 | 122.6852 | 59.2117 | 59.3216
743.3125 | 122.5891 | -59.2026 | 63.0844 | -0.065842 | 0.0030484 | 0.06423 | 0.059595 | 0.0018372 | -0.0055244 | 0.0018413 | -0.082397 | 0.0014185 | 0.065875 | 0.065198 | -0.0069726 | 0.010079 | -0.0018136 | -0.10986 | 62.9837 | -59.3491 | 63.089 | -59.1385 | -59.5184 | -59.4818 | -0.09613 | 62.9837 | -59.2163 | 63.1668 | -59.2117 | -59.3399 | -59.2026 | -0.14648 | -0.10071 | 0.004577 | 0.064087 | -0.27924 | -0.31586 | -0.13275 | -0.16937 | -0.013733 | -0.10071 | 0.082397 | -0.009155 | 0 | -0.13733 | 0.013733 | -0.1236 | 0.21057 | 122.438 | 0.004578 | 122.3831 | 122.3328 | 122.2 | 122.1863 | 122.1863 | -122.4335 | -122.3007 | 122.2916 | 122.3694 | 59.0927 | 59.1064
744.3125 | 122.6212 | -59.1614 | 63.1073 | -0.050583 | 0.0030484 | 0.06423 | 0.060449 | -0.00072638 | -0.0042426 | -0.0011493 | -0.0091553 | 0.00077755 | 0.066729 | 0.062207 | -0.0069726 | 0.0094379 | -0.0039498 | 0.21515 | 63.0569 | -59.1934 | 63.1943 | -59.0607 | -59.2896 | -59.3079 | 0.10986 | 62.9883 | -59.1705 | 63.2126 | -59.1156 | -59.2438 | -59.1476 | -0.032043 | -0.050354 | 0.086975 | 0.10071 | -0.14648 | -0.12817 | -0.11444 | -0.096131 | -0.009155 | -0.11902 | 0.10528 | 0.045776 | 0.013733 | -0.082397 | 0.022888 | -0.073242 | 0.13275 | 122.3877 | 0.054931 | 122.3831 | 122.2504 | 122.1588 | 122.2183 | 122.1497 | -122.3007 | -122.2778 | 122.3557 | 122.374 | 59.3765 | 59.2712
745.3125 | 122.493 | -59.2392 | 63.1165 | -0.073471 | 0.0011258 | 0.063162 | 0.061517 | -0.0022218 | -0.00232 | 0.00098694 | -0.10071 | 0.0024865 | 0.064807 | 0.063489 | -0.0031274 | 0.010079 | -0.0024546 | 0.13733 | 63.0341 | -59.3308 | 63.0386 | -59.166 | -59.5459 | -59.5322 | -0.17395 | 63.0066 | -59.2484 | 63.0981 | -59.3353 | -59.4452 | -59.2987 | -0.091553 | -0.082397 | -0.07782 | 0.073242 | -0.29297 | -0.3067 | -0.20142 | -0.21515 | -0.009155 | -0.10986 | -0.01831 | -0.09613 | -0.059509 | -0.20599 | -0.050354 | -0.19684 | 0.1648 | 122.3694 | -0.086975 | 122.3465 | 122.3648 | 122.2549 | 122.2733 | 122.2458 | -122.4472 | -122.3648 | 122.2778 | 122.3373 | 59.3765 | 59.0652
746.3125 | 122.5342 | -59.2072 | 63.089 | -0.050583 | 0.0024076 | 0.064657 | 0.061517 | -0.002008 | -0.0027472 | -0.00050846 | -0.085449 | 0.0022729 | 0.068866 | 0.066907 | -0.008468 | 0.0081561 | -0.0024546 | -0.091553 | 63.0478 | -59.3536 | 63.0615 | -59.166 | -59.5505 | -59.523 | -0.1236 | 62.9837 | -59.2392 | 63.0981 | -59.2621 | -59.4269 | -59.2758 | -0.14648 | -0.041198 | -0.027466 | 0.041198 | -0.31586 | -0.34332 | -0.16937 | -0.19684 | -0.032044 | -0.10528 | 0.009156 | -0.054932 | -0.068665 | -0.21973 | -0.036621 | -0.18768 | 0.18768 | 122.4152 | -0.022888 | 122.3373 | 122.4014 | 122.2229 | 122.2549 | 122.1909 | -122.4426 | -122.3282 | 122.2687 | 122.3053 | 59.1156 | 59.0836
747.3125 | 122.5891 | -59.2026 | 63.0981 | -0.11925 | 0.0026212 | 0.06423 | 0.059595 | -0.0024354 | -0.003388 | -0.0022175 | 0.0030517 | 0.0024865 | 0.065875 | 0.063061 | -0.00505 | 0.0070879 | -0.0045908 | -0.07782 | 62.9791 | -59.317 | 63.1027 | -59.079 | -59.4727 | -59.4269 | -0.07782 | 62.9608 | -59.23 | 63.1577 | -59.2209 | -59.3262 | -59.23 | -0.11444 | -0.11902 | 0.004577 | 0.1236 | -0.2243 | -0.27008 | -0.10986 | -0.15564 | -0.027466 | -0.13733 | 0.059509 | -0.01831 | -0.027466 | -0.1236 | 0 | -0.09613 | 0.23804 | 122.4197 | 0.009156 | 122.3877 | 122.2961 | 122.1909 | 122.1817 | 122.1634 | -122.4152 | -122.3282 | 122.3053 | 122.3602 | 59.1248 | 59.1248
748.3125 | 122.5754 | -59.2072 | 63.0661 | -0.13451 | 0.0036892 | 0.063803 | 0.060663 | -0.0024354 | -0.0025336 | -0.0017903 | -0.067139 | 0.0016321 | 0.068866 | 0.063489 | -0.00505 | 0.010292 | -0.000532 | -0.11444 | 63.0432 | -59.3491 | 63.0844 | -59.1248 | -59.5276 | -59.4818 | -0.09613 | 62.9745 | -59.2346 | 63.1668 | -59.2117 | -59.3719 | -59.2026 | -0.14191 | -0.022888 | 0.018311 | 0.082397 | -0.27466 | -0.32044 | -0.13275 | -0.17853 | -0.027466 | -0.091553 | 0.10071 | -0.004578 | 0.004577 | -0.1648 | 0.032043 | -0.13733 | 0.2243 | 122.4335 | 0.022888 | 122.4014 | 122.3923 | 122.2092 | 122.2504 | 122.1817 | -122.4152 | -122.3007 | 122.2916 | 122.374 | 59.0927 | 59.111
749.3125 | 122.5937 | -59.1843 | 63.0386 | -0.11162 | 0.0039028 | 0.062094 | 0.062799 | 0.00034182 | -0.00039736 | 0.00034614 | -0.061035 | -0.00093145 | 0.065448 | 0.059216 | -0.0074 | 0.012642 | -0.0018136 | -0.045776 | 62.9883 | -59.3216 | 63.1348 | -59.0469 | -59.4269 | -59.4131 | -0.027466 | 62.9745 | -59.2026 | 63.0615 | -59.0515 | -59.0881 | -59.0378 | -0.13733 | -0.050354 | 0.096131 | 0.13733 | -0.22888 | -0.24261 | -0.091553 | -0.10529 | -0.018311 | -0.064087 | 0.022888 | 0.13275 | 0.14648 | 0.09613 | 0.16479 | 0.11444 | 0.27466 | 122.4564 | 0.15106 | 122.2641 | 122.3099 | 122.1771 | 122.1725 | 122.1588 | -122.3602 | -122.2412 | 122.319 | 122.2458 | 59.1385 | 59.1568
750.3125 | 122.525 | -59.2209 | 63.0981 | -0.096359 | 0.0024076 | 0.064657 | 0.060876 | 0.0063232 | -0.004029 | 0.00034614 | -0.027466 | 0.0035547 | 0.067157 | 0.064984 | -0.00505 | 0.011147 | -0.0011728 | -0.10986 | 63.0203 | -59.317 | 63.0478 | -59.1522 | -59.5459 | -59.5184 | -0.13275 | 62.97 | -59.2392 | 63.1119 | -59.2667 | -59.4131 | -59.2621 | -0.096131 | -0.07782 | -0.050354 | 0.068664 | -0.29755 | -0.32501 | -0.20142 | -0.22888 | -0.018311 | -0.12817 | 0.013732 | -0.045777 | -0.041199 | -0.19226 | -0.022888 | -0.17395 | 0.16479 | 122.3648 | -0.027466 | 122.3511 | 122.3373 | 122.2092 | 122.2412 | 122.1909 | -122.4152 | -122.3373 | 122.2687 | 122.3328 | 59.111 | 59.0881
751.3125 | 122.6074 | -59.2209 | 63.0569 | -0.081101 | 0.0028348 | 0.064871 | 0.061517 | -0.0015808 | -0.0012518 | 0.00098694 | -0.07019 | 0.0018457 | 0.065661 | 0.061566 | -0.0063318 | 0.010079 | -0.005018 | -0.09613 | 63.0066 | -59.3308 | 63.0844 | -59.111 | -59.4727 | -59.4406 | -0.059509 | 62.9654 | -59.2209 | 63.176 | -59.2117 | -59.3216 | -59.1888 | -0.10986 | -0.050354 | 0.027466 | 0.10986 | -0.21973 | -0.25177 | -0.10986 | -0.14191 | 0 | -0.091553 | 0.11902 | 0.009155 | 0.032043 | -0.10071 | 0.032043 | -0.10071 | 0.21973 | 122.4152 | 0.009155 | 122.3969 | 122.3373 | 122.1863 | 122.2275 | 122.1863 | -122.3877 | -122.2778 | 122.3053 | 122.3969 | 59.1248 | 59.1614
752.3125 | 122.5708 | -59.2255 | 63.0569 | -0.081101 | 0.0019802 | 0.063589 | 0.062158 | 0.0035462 | -0.0025336 | -0.0020039 | -0.042725 | 0.00099115 | 0.06438 | 0.063275 | -0.0059046 | 0.0096515 | 0.0030996 | -0.091553 | 63.0157 | -59.3079 | 63.0661 | -59.1202 | -59.5322 | -59.4864 | -0.09613 | 62.9791 | -59.23 | 63.1622 | -59.2117 | -59.3262 | -59.2026 | -0.082397 | -0.041199 | 0.009155 | 0.10529 | -0.26093 | -0.3067 | -0.17853 | -0.2243 | -0.004578 | -0.07782 | 0.10528 | 0.013733 | 0.022888 | -0.10071 | 0.027466 | -0.09613 | 0.18768 | 122.374 | 0.018311 | 122.3923 | 122.3236 | 122.2092 | 122.2412 | 122.2046 | -122.3648 | -122.287 | 122.2916 | 122.3877 | 59.1339 | 59.1293
753.3125 | 122.5296 | -59.2484 | 63.1165 | -0.11925 | 0.0006986 | 0.064016 | 0.060449 | -0.0024354 | -0.003388 | -0.00029486 | -0.079346 | 0.00013675 | 0.06737 | 0.059857 | -0.0059046 | 0.0083697 | -0.0024546 | -0.045776 | 63.0478 | -59.3262 | 63.0432 | -59.1705 | -59.5871 | -59.5505 | -0.13733 | 63.002 | -59.2621 | 63.0753 | -59.3124 | -59.436 | -59.2758 | -0.07782 | -0.068664 | -0.073242 | 0.07782 | -0.30212 | -0.33875 | -0.2243 | -0.26093 | -0.013733 | -0.11444 | -0.041199 | -0.064087 | -0.027466 | -0.18768 | -0.013733 | -0.17395 | 0.15564 | 122.3694 | -0.050354 | 122.3373 | 122.374 | 122.2641 | 122.2961 | 122.2504 | -122.4426 | -122.3785 | 122.2916 | 122.3236 | 59.2026 | 59.111
754.3125 | 122.6212 | -59.2072 | 63.0753 | 0.04097 | 0.0041166 | 0.063803 | 0.059167 | -0.00051278 | -0.00082456 | -0.0013629 | -0.0061035 | 0.0024865 | 0.064807 | 0.067975 | -0.0052638 | 0.0081561 | -0.0018136 | -0.032043 | 62.97 | -59.285 | 63.1485 | -59.0149 | -59.4589 | -59.4086 | -0.004578 | 62.9745 | -59.2117 | 63.1851 | -59.1797 | -59.3033 | -59.1843 | -0.07782 | -0.10529 | 0.073243 | 0.19226 | -0.20142 | -0.25177 | -0.1236 | -0.17395 | -0.004578 | -0.10071 | 0.10986 | 0.027466 | 0.022888 | -0.096131 | 0.027466 | -0.091553 | 0.27008 | 122.4335 | 0.032044 | 122.3969 | 122.2549 | 122.1863 | 122.1771 | 122.1817 | -122.3602 | -122.287 | 122.3557 | 122.3923 | 59.1751 | 59.2026
755.3125 | 122.5479 | -59.2438 | 63.089 | -0.058212 | 0.000485 | 0.062948 | 0.060022 | 0.004187 | -0.0018928 | -8.1264e-05 | -0.064087 | 0.0035547 | 0.067157 | 0.062848 | -0.0069726 | 0.0085833 | -0.000532 | -0.1236 | 63.0341 | -59.3308 | 63.0432 | -59.1385 | -59.5505 | -59.5276 | -0.13733 | 62.9791 | -59.2392 | 63.1073 | -59.285 | -59.4086 | -59.2667 | -0.086976 | -0.054931 | -0.045776 | 0.10529 | -0.28381 | -0.3067 | -0.19684 | -0.21973 | 0.004577 | -0.10986 | 0.018311 | -0.041199 | -0.022889 | -0.16479 | -0.027466 | -0.16937 | 0.19226 | 122.374 | -0.045776 | 122.3465 | 122.3648 | 122.2183 | 122.2778 | 122.2229 | -122.4197 | -122.3282 | 122.287 | 122.3511 | 59.1202 | 59.1064
756.3125 | 122.6303 | -59.1934 | 63.0844 | -0.073471 | 0.0041166 | 0.065298 | 0.061944 | 0.00098262 | -0.0027472 | -0.00050846 | -0.036621 | 0.0022729 | 0.067798 | 0.060712 | -0.0065454 | 0.010933 | -0.0026682 | -0.10986 | 63.002 | -59.3353 | 63.0844 | -59.1156 | -59.4864 | -59.4681 | -0.091553 | 62.9791 | -59.2117 | 63.1668 | -59.2346 | -59.3399 | -59.1843 | -0.14191 | -0.082398 | 0 | 0.077819 | -0.27466 | -0.29297 | -0.13275 | -0.15106 | -0.018311 | -0.10529 | 0.082397 | -0.041199 | 0.009155 | -0.14648 | 0.027466 | -0.12817 | 0.21973 | 122.4197 | -0.022888 | 122.3785 | 122.3373 | 122.1909 | 122.1954 | 122.1725 | -122.4197 | -122.2961 | 122.2778 | 122.3602 | 59.0836 | 59.1019
757.3125 | 122.6212 | -59.1614 | 63.0798 | -0.11925 | 0.0024076 | 0.063589 | 0.059595 | 0.00076902 | -0.0014654 | -0.0028583 | -0.036621 | 0.0020593 | 0.066089 | 0.059644 | -0.00505 | 0.0087969 | 0.0007498 | -0.064087 | 62.9654 | -59.3033 | 63.1485 | -59.0424 | -59.4315 | -59.404 | -0.1236 | 62.9196 | -59.2346 | 63.1989 | -59.2026 | -59.2758 | -59.1476 | -0.14191 | -0.11444 | 0.068665 | 0.11902 | -0.24262 | -0.27008 | -0.10071 | -0.12817 | -0.073242 | -0.16022 | 0.11902 | -0.041199 | 0.013733 | -0.11444 | 0.086975 | -0.041199 | 0.26093 | 122.4518 | 0.032043 | 122.4335 | 122.2687 | 122.1542 | 122.1268 | 122.081 | -122.3831 | -122.3145 | 122.3099 | 122.3602 | 59.0973 | 59.0378
758.3125 | 122.5616 | -59.1934 | 63.0707 | -0.11925 | 0.0017666 | 0.059744 | 0.06109 | 0.00012822 | -0.0042426 | -0.00072206 | -0.061035 | 0.0027001 | 0.067157 | 0.062421 | -0.0061182 | 0.0094379 | -0.0030954 | -0.1236 | 63.0249 | -59.3262 | 63.0615 | -59.1522 | -59.5367 | -59.5047 | -0.12817 | 62.9837 | -59.2667 | 63.1348 | -59.2529 | -59.3903 | -59.2484 | -0.13275 | -0.045777 | -0.009156 | 0.041198 | -0.31128 | -0.34332 | -0.17853 | -0.21057 | -0.073243 | -0.086975 | 0.064087 | -0.05951 | -0.054932 | -0.19684 | 0.018311 | -0.1236 | 0.17395 | 122.3877 | 0.013733 | 122.4014 | 122.3511 | 122.2504 | 122.2183 | 122.1771 | -122.3969 | -122.3373 | 122.2549 | 122.3282 | 59.0698 | 59.0652
759.3125 | 122.4792 | -59.2392 | 63.1073 | -0.020065 | 0.0041166 | 0.064657 | 0.05874 | -0.00093998 | -0.003388 | -0.0017903 | -0.082397 | 0.0012047 | 0.066302 | 0.059857 | -0.003341 | 0.0092241 | -0.0045908 | -0.1236 | 63.0386 | -59.3399 | 62.9608 | -59.1705 | -59.491 | -59.5505 | -0.13733 | 63.0478 | -59.2575 | 63.0661 | -59.3124 | -59.4223 | -59.2941 | -0.10071 | -0.068665 | -0.14649 | 0.068665 | -0.31128 | -0.25177 | -0.21057 | -0.15106 | -0.01831 | -0.059509 | -0.041199 | -0.073242 | -0.054931 | -0.18311 | -0.036621 | -0.1648 | 0.16937 | 122.3007 | -0.054932 | 122.3236 | 122.3785 | 122.3053 | 122.2778 | 122.287 | -122.4472 | -122.3648 | 122.2 | 122.3053 | 59.1156 | 59.1019
760.3125 | 122.5113 | -59.2438 | 63.1165 | -0.081101 | 0.0019802 | 0.063803 | 0.06109 | 0.00034182 | -0.00082456 | -0.0020039 | 0.05188 | 0.0033411 | 0.065661 | 0.060284 | -0.0065454 | 0.010079 | -0.0009592 | -0.11444 | 63.0524 | -59.3445 | 63.1165 | -59.523 | -59.9762 | -59.404 | -0.23804 | 63.0157 | -59.2529 | 63.0753 | -59.3399 | -59.4406 | -59.2987 | -0.10071 | -0.064087 | 0 | -0.27924 | -0.16022 | -0.73242 | -0.05951 | -0.63171 | -0.009156 | -0.10071 | -0.041199 | -0.096131 | -0.054932 | -0.19684 | -0.045776 | -0.18768 | -0.17853 | 122.4609 | -0.086975 | 122.3282 | 122.3969 | 122.2687 | 122.2961 | 122.2595 | -122.4609 | -122.3694 | 122.3602 | 122.319 | 59.1293 | 59.0057
761.3125 | 122.6028 | -59.1934 | 63.0569 | -0.050583 | 0.002194 | 0.062735 | 0.05874 | 0.00012822 | -0.0025336 | -0.0013629 | -0.027466 | 0.00099115 | 0.065448 | 0.066266 | -0.005691 | 0.010506 | -0.0048044 | -0.11902 | 62.9974 | -59.3262 | 63.0707 | -59.1202 | -59.523 | -59.4818 | -0.09613 | 62.97 | -59.2346 | 63.1577 | -59.23 | -59.3262 | -59.1888 | -0.13275 | -0.059509 | 0.013733 | 0.073242 | -0.28839 | -0.32959 | -0.15564 | -0.19684 | -0.041199 | -0.086975 | 0.10071 | -0.036622 | 0.004577 | -0.13275 | 0.045776 | -0.091553 | 0.20599 | 122.3969 | 0.004577 | 122.3923 | 122.3236 | 122.2046 | 122.1909 | 122.1634 | -122.3831 | -122.2916 | 122.2641 | 122.3511 | 59.0744 | 59.0973
762.3125 | 122.5983 | -59.198 | 63.0798 | -0.042954 | 0.0017666 | 0.061453 | 0.05639 | -0.0015808 | -0.0027472 | -0.0037129 | -0.088501 | 0.0012047 | 0.066089 | 0.052808 | -0.0041956 | 0.0085833 | 0.0003226 | -0.09613 | 63.0203 | -59.2804 | 63.1119 | -59.079 | -59.1843 | -59.2804 | -0.068665 | 62.9654 | -59.2392 | 63.1119 | -59.23 | -59.3491 | -59.2392 | -0.082398 | -0.059509 | 0.032043 | 0.11902 | -0.082398 | 0.013733 | 0 | 0.096131 | -0.041199 | -0.11444 | 0.032043 | -0.032044 | -0.041199 | -0.15106 | 0 | -0.10986 | 0.20142 | 122.3923 | 0.009155 | 122.3511 | 122.3007 | 122.2046 | 122.2183 | 122.1634 | -122.3602 | -122.319 | 122.3099 | 122.3099 | 59.1019 | 59.1293
763.3125 | 122.493 | -59.2392 | 63.0936 | -0.24895 | 0.0028348 | 0.062521 | 0.06109 | -0.0035034 | -0.0038154 | -0.00072206 | -0.076294 | 0.0024865 | 0.068438 | 0.06413 | -0.0046228 | 0.010292 | -0.0003182 | 0.027466 | 63.002 | -59.317 | 63.0249 | -59.1843 | -59.5184 | -59.5139 | -0.13733 | 63.0157 | -59.2392 | 63.089 | -59.3079 | -59.4589 | -59.3079 | -0.07782 | -0.091553 | -0.068665 | 0.054932 | -0.27466 | -0.27924 | -0.19684 | -0.20142 | 0 | -0.07782 | -0.004578 | -0.068664 | -0.068664 | -0.21973 | -0.068664 | -0.21973 | 0.13275 | 122.3419 | -0.068664 | 122.3282 | 122.319 | 122.2549 | 122.2412 | 122.2549 | -122.4106 | -122.3328 | 122.2641 | 122.3282 | 59.2667 | 59.1019
764.3125 | 122.525 | -59.2667 | 63.1119 | -0.058212 | 0.0011258 | 0.062308 | 0.059808 | 0.00098262 | -0.0038154 | -0.0041401 | -0.073242 | 0.0039819 | 0.068011 | 0.062848 | -0.0048364 | 0.0087969 | 0.0022452 | -0.12817 | 63.0066 | -59.3399 | 63.0432 | -59.1522 | -59.5459 | -59.5093 | -0.14191 | 63.0066 | -59.2575 | 63.0981 | -59.2804 | -59.404 | -59.2529 | -0.073242 | -0.10529 | -0.068664 | 0.11444 | -0.24261 | -0.27923 | -0.16937 | -0.20599 | 0.009156 | -0.10529 | -0.013732 | -0.013733 | 0.013733 | -0.13733 | 0.004577 | -0.14649 | 0.18768 | 122.3831 | -0.022889 | 122.3557 | 122.3465 | 122.2641 | 122.2733 | 122.2733 | -122.4518 | -122.3694 | 122.3099 | 122.3648 | 59.1385 | 59.1248
765.3125 | 122.4609 | -59.2438 | 63.1165 | -0.058212 | 0.0045438 | 0.063803 | 0.062372 | -0.0024354 | -0.00232 | 0.00098694 | -0.067139 | 0.0014185 | 0.067798 | 0.060071 | -0.006759 | 0.0096515 | 0.003527 | -0.054932 | 63.0432 | -59.3124 | 63.0707 | -59.1339 | -59.5184 | -59.491 | -0.09613 | 63.0295 | -59.2438 | 63.0753 | -59.317 | -59.4177 | -59.2804 | -0.068665 | -0.073242 | -0.045776 | 0.10986 | -0.24719 | -0.27466 | -0.17853 | -0.20599 | 0 | -0.086975 | -0.041199 | -0.073243 | -0.036622 | -0.17395 | -0.036622 | -0.17395 | 0.17853 | 122.3831 | -0.073243 | 122.319 | 122.3557 | 122.2733 | 122.287 | 122.2733 | -122.4289 | -122.3602 | 122.3145 | 122.319 | 59.1888 | 59.1476
766.3125 | 122.5296 | -59.2026 | 63.1165 | -0.012436 | 0.0024076 | 0.061667 | 0.061731 | 0.00012822 | -0.0018928 | -0.0028583 | -0.042725 | 0.0024865 | 0.065448 | 0.063489 | -0.0041956 | 0.010506 | -0.000532 | -0.091553 | 63.0432 | -59.3262 | 63.0341 | -59.198 | -59.5734 | -59.523 | -0.19684 | 63.0066 | -59.2575 | 62.9745 | -59.6375 | -59.1843 | -59.0149 | -0.1236 | -0.073242 | -0.082397 | 0.004578 | -0.32043 | -0.37079 | -0.19684 | -0.24719 | -0.054931 | -0.10986 | -0.14191 | -0.43487 | 0.18768 | 0.018311 | 0.24261 | 0.073242 | 0.12817 | 122.3602 | -0.37994 | 122.2321 | 122.3694 | 122.2641 | 122.2458 | 122.2092 | -122.4426 | -122.374 | 122.2366 | 122.1771 | 59.111 | 59.0057
767.3125 | 122.5937 | -59.2209 | 63.0753 | -0.058212 | 0.0019802 | 0.063376 | 0.058313 | 0.00098262 | -0.0031744 | -0.00029486 | 0.015259 | 0.00056395 | 0.068011 | 0.060071 | -0.0054774 | 0.010292 | -0.0001046 | -0.050354 | 63.0112 | -59.2758 | 63.1531 | -59.0195 | -59.4223 | -59.3948 | -0.022888 | 62.9517 | -59.2072 | 63.1805 | -59.1751 | -59.285 | -59.1751 | -0.054932 | -0.064087 | 0.07782 | 0.20142 | -0.17395 | -0.20142 | -0.11902 | -0.14648 | 0.013733 | -0.1236 | 0.10529 | 0.045776 | 0.045776 | -0.064087 | 0.032043 | -0.07782 | 0.25635 | 122.4289 | 0.032043 | 122.3877 | 122.287 | 122.1588 | 122.2321 | 122.1725 | -122.3511 | -122.2824 | 122.374 | 122.4014 | 59.1705 | 59.198
768.3125 | 122.5296 | -59.2392 | 63.1165 | -0.042954 | 0.0019802 | 0.07128 | 0.059595 | 0.0044006 | 0.00024344 | -0.0034991 | -0.057983 | 0.0016321 | 0.068225 | 0.061139 | -0.0041956 | 0.0087969 | -0.0003182 | -0.32501 | 62.9791 | -59.3857 | 63.0753 | -59.1019 | -59.6375 | -59.5276 | -0.17853 | 63.0066 | -59.2529 | 63.0707 | -59.3079 | -59.436 | -59.2804 | -0.14648 | -0.13733 | -0.041199 | 0.13733 | -0.28839 | -0.39825 | -0.14191 | -0.25177 | -0.013733 | -0.10986 | -0.045776 | -0.068664 | -0.041199 | -0.19684 | -0.027466 | -0.1831 | 0.28381 | 122.4609 | -0.054931 | 122.3236 | 122.3648 | 122.2595 | 122.2183 | 122.2458 | -122.5021 | -122.3694 | 122.3145 | 122.3099 | 58.9142 | 59.0607
769.3125 | 122.5525 | -59.2163 | 63.089 | -0.058212 | 0.003262 | 0.063376 | 0.060022 | 0.00098262 | -0.00232 | -0.00029486 | -0.039673 | 0.0033411 | 0.068652 | 0.060712 | -0.0048364 | 0.0090105 | -0.000532 | -0.14191 | 63.0249 | -59.3308 | 63.0432 | -59.166 | -59.5413 | -59.5047 | -0.15106 | 62.9791 | -59.2438 | 63.089 | -59.2987 | -59.4131 | -59.2621 | -0.11444 | -0.064087 | -0.045776 | 0.050354 | -0.28839 | -0.32501 | -0.17395 | -0.21057 | -0.027465 | -0.10986 | 0 | -0.082397 | -0.045776 | -0.19684 | -0.018311 | -0.16937 | 0.1648 | 122.374 | -0.054932 | 122.3328 | 122.3557 | 122.2229 | 122.2412 | 122.1954 | -122.4197 | -122.3328 | 122.2595 | 122.3053 | 59.0744 | 59.0652
770.3125 | 122.5113 | -59.1888 | 63.1348 | -0.073471 | 0.0039028 | 0.06423 | 0.061303 | -0.00051278 | -0.0036018 | -0.00050846 | -0.064087 | 0.0027001 | 0.067798 | 0.063489 | -0.003982 | 0.0079425 | -0.0018136 | -0.10986 | 63.0478 | -59.3445 | 63.0066 | -59.2163 | -59.5779 | -59.5505 | -0.45776 | 62.9379 | -59.2987 | 63.121 | -59.2896 | -59.491 | -59.2941 | -0.15564 | -0.086975 | -0.12817 | -0.027466 | -0.36163 | -0.3891 | -0.20599 | -0.23346 | -0.10986 | -0.19684 | -0.013733 | -0.10071 | -0.10529 | -0.30212 | 0.004578 | -0.19226 | 0.12817 | 122.3511 | 0.009155 | 122.4197 | 122.3923 | 122.2366 | 122.2366 | 122.1268 | -122.4792 | -122.4335 | 122.1954 | 122.3099 | 59.079 | 58.7311
771.3125 | 122.5433 | -59.2346 | 63.0753 | -0.050583 | 0.0039028 | 0.063162 | 0.063867 | 0.0044006 | -0.003388 | -0.00072206 | -0.042725 | 0.0035547 | 0.066302 | 0.062421 | -0.0046228 | 0.010506 | -0.0048044 | -0.10071 | 63.0569 | -59.3262 | 63.0386 | -59.1888 | -59.5367 | -59.523 | -0.15106 | 63.0066 | -59.2575 | 63.0844 | -59.3079 | -59.4177 | -59.2896 | -0.091553 | -0.01831 | -0.036621 | 0.045776 | -0.28839 | -0.30212 | -0.19684 | -0.21057 | -0.022888 | -0.068664 | 0.009156 | -0.073242 | -0.054932 | -0.18311 | -0.032044 | -0.16022 | 0.13733 | 122.3648 | -0.050354 | 122.3419 | 122.3831 | 122.2641 | 122.2916 | 122.2412 | -122.4014 | -122.3328 | 122.2733 | 122.319 | 59.1339 | 59.0836
772.3125 | 122.5754 | -59.23 | 63.0753 | -0.073471 | 0.0017666 | 0.06188 | 0.060663 | 0.0016236 | -0.0042426 | 0.00034614 | -0.027466 | 0.0020593 | 0.065875 | 0.06178 | -0.0048364 | 0.0098651 | -0.0028818 | -0.10986 | 63.0432 | -59.3262 | 63.0524 | -59.1293 | -59.5367 | -59.4864 | -0.11902 | 62.9974 | -59.2255 | 63.1256 | -59.2575 | -59.3765 | -59.2484 | -0.09613 | -0.032043 | -0.022888 | 0.10071 | -0.25635 | -0.3067 | -0.16022 | -0.21057 | 0.004578 | -0.077819 | 0.050354 | -0.027465 | -0.01831 | -0.14648 | -0.022888 | -0.15106 | 0.19684 | 122.3785 | -0.032043 | 122.3511 | 122.3694 | 122.2229 | 122.2733 | 122.2275 | -122.4014 | -122.3007 | 122.2824 | 122.3557 | 59.1202 | 59.111
773.3125 | 122.4701 | -59.2117 | 63.1302 | -0.012436 | 0.0024076 | 0.064871 | 0.061303 | -0.00093998 | -0.0048834 | 0.0039777 | -0.039673 | 0.0035547 | 0.066729 | 0.059216 | -0.006759 | 0.012215 | -0.000532 | -0.07782 | 63.0432 | -59.3033 | 63.0478 | -59.1522 | -59.5459 | -59.5093 | -0.13733 | 63.0066 | -59.2392 | 63.0478 | -59.3262 | -59.4498 | -59.2804 | -0.091553 | -0.086975 | -0.082397 | 0.059509 | -0.29755 | -0.33417 | -0.20599 | -0.24261 | -0.027466 | -0.1236 | -0.082397 | -0.11444 | -0.068665 | -0.23804 | -0.041199 | -0.21057 | 0.15106 | 122.3511 | -0.086975 | 122.287 | 122.3465 | 122.2458 | 122.2549 | 122.2183 | -122.4335 | -122.3694 | 122.2595 | 122.2595 | 59.1339 | 59.0744
774.3125 | 122.4792 | -59.2346 | 63.1027 | -0.042954 | 0.0024076 | 0.063589 | 0.061944 | 0.0039734 | -0.004029 | 0.0022687 | -0.07019 | 0.0012047 | 0.06502 | 0.062848 | -0.0048364 | 0.011147 | -0.0020272 | -0.1236 | 63.0341 | -59.3445 | 62.7731 | -59.491 | -59.2712 | -59.2346 | -0.16022 | 63.0432 | -59.2255 | 63.0661 | -59.3124 | -59.4543 | -59.317 | -0.10986 | -0.068664 | -0.32959 | -0.25635 | 0 | -0.036621 | 0.10986 | 0.073242 | 0.009155 | -0.059509 | -0.036621 | -0.07782 | -0.082398 | -0.21973 | -0.091553 | -0.22888 | -0.14648 | 122.1176 | -0.086975 | 122.2916 | 122.3785 | 122.2687 | 122.2687 | 122.2778 | -122.4472 | -122.3282 | 122.0078 | 122.3007 | 59.111 | 59.0744
775.3125 | 122.5067 | -59.2255 | 63.1165 | -0.058212 | 0.0026212 | 0.063803 | 0.062372 | 0.0020508 | -0.0025336 | -0.0037129 | -0.021362 | 0.0027001 | 0.063952 | 0.063916 | -0.0071864 | 0.0096515 | 0.003527 | -0.11444 | 63.0386 | -59.3445 | 62.9974 | -59.2255 | -59.5871 | -59.5413 | -0.31586 | 62.9379 | -59.2987 | 63.0249 | -59.2346 | -59.4955 | -59.3308 | -0.11902 | -0.07782 | -0.11902 | 0 | -0.31586 | -0.36163 | -0.19684 | -0.24262 | -0.073242 | -0.17853 | -0.091553 | -0.009155 | -0.10529 | -0.27008 | -0.032044 | -0.19684 | 0.11902 | 122.3419 | 0.064087 | 122.3236 | 122.3831 | 122.2366 | 122.2641 | 122.1634 | -122.4609 | -122.4152 | 122.2229 | 122.2504 | 59.111 | 58.9096
776.3125 | 122.4747 | -59.2484 | 63.1302 | -0.08873 | 0.0026212 | 0.063376 | 0.060876 | -0.00072638 | -0.003388 | 0.00055974 | -0.039673 | 0.0014185 | 0.067584 | 0.059003 | -0.0037684 | 0.0075153 | -0.0016 | -0.086975 | 63.0249 | -59.3399 | 63.0249 | -59.166 | -59.5551 | -59.523 | -0.15564 | 63.0112 | -59.2438 | 63.0753 | -59.3033 | -59.4315 | -59.285 | -0.091553 | -0.10529 | -0.10529 | 0.082397 | -0.27466 | -0.3067 | -0.1831 | -0.21515 | 0.004578 | -0.11902 | -0.054932 | -0.054932 | -0.036621 | -0.18311 | -0.041199 | -0.18768 | 0.17395 | 122.3648 | -0.05951 | 122.319 | 122.3648 | 122.2549 | 122.2733 | 122.2595 | -122.4701 | -122.374 | 122.2733 | 122.3236 | 59.1614 | 59.0927
777.3125 | 122.5662 | -59.2255 | 63.0798 | -0.08873 | 0.0028348 | 0.062521 | 0.059381 | 0.00012822 | -0.0018928 | -0.00093566 | -0.015259 | 0.0029137 | 0.068225 | 0.062634 | -0.006759 | 0.010079 | 0.002886 | -0.11444 | 63.0203 | -59.3308 | 63.0524 | -59.1476 | -59.5322 | -59.491 | -0.11902 | 62.9745 | -59.2484 | 63.1165 | -59.2529 | -59.3765 | -59.2392 | -0.10529 | -0.059509 | -0.027466 | 0.07782 | -0.2655 | -0.3067 | -0.16022 | -0.20142 | -0.022888 | -0.10529 | 0.036621 | -0.027466 | -0.013733 | -0.15106 | 0.009155 | -0.12817 | 0.18311 | 122.3831 | -0.004578 | 122.3648 | 122.3511 | 122.2229 | 122.2458 | 122.2 | -122.4106 | -122.3282 | 122.2778 | 122.3419 | 59.111 | 59.1064
778.3125 | 122.4838 | -59.2484 | 63.0798 | -0.073471 | 0.0026212 | 0.063162 | 0.060663 | -0.004358 | -0.0018928 | -8.1264e-05 | -0.048828 | 0.0031273 | 0.06438 | 0.062207 | -0.005691 | 0.0094379 | -0.0035226 | -0.12817 | 63.0524 | -59.3491 | 62.9562 | -59.2072 | -59.4727 | -59.5276 | -0.14191 | 63.0249 | -59.2392 | 63.0661 | -59.3079 | -59.4086 | -59.2712 | -0.10071 | -0.027466 | -0.1236 | 0.041199 | -0.27924 | -0.2243 | -0.17853 | -0.1236 | 0.009155 | -0.054932 | -0.013733 | -0.059509 | -0.022888 | -0.16022 | -0.032043 | -0.16937 | 0.14191 | 122.3053 | -0.068664 | 122.3053 | 122.4014 | 122.2641 | 122.3007 | 122.2733 | -122.4289 | -122.319 | 122.2046 | 122.3145 | 59.1202 | 59.1064
779.3125 | 122.4976 | -59.2438 | 63.0981 | -0.027695 | 0.0013394 | 0.063376 | 0.057672 | 0.00034182 | -0.00039736 | -0.00050846 | 0.045776 | 0.0029137 | 0.068866 | 0.05943 | -0.0069726 | 0.0098651 | 0.0013906 | -0.11902 | 63.0524 | -59.3308 | 63.0707 | -59.523 | -59.9213 | -59.3674 | -0.27008 | 63.0295 | -59.2255 | 63.0753 | -59.3353 | -59.4498 | -59.3033 | -0.086976 | -0.045777 | -0.027466 | -0.27924 | -0.1236 | -0.67749 | -0.036621 | -0.59051 | 0.01831 | -0.068665 | -0.022889 | -0.091553 | -0.05951 | -0.20599 | -0.07782 | -0.2243 | -0.19226 | 122.4014 | -0.10986 | 122.3007 | 122.3831 | 122.2549 | 122.2961 | 122.2733 | -122.4289 | -122.3236 | 122.3145 | 122.319 | 59.1248 | 58.9737
780.3125 | 122.5067 | -59.2163 | 63.1165 | -0.035324 | 0.003262 | 0.062735 | 0.060876 | 0.002478 | -0.0021064 | 0.00098694 | -0.061035 | 0.0016321 | 0.067157 | 0.061566 | -0.00505 | 0.01072 | 0.000109 | -0.068665 | 63.0478 | -59.3124 | 63.0844 | -59.1202 | -59.5139 | -59.491 | -0.082397 | 63.0386 | -59.2209 | 63.0798 | -59.2941 | -59.4269 | -59.2667 | -0.09613 | -0.068664 | -0.032043 | 0.096131 | -0.27466 | -0.29755 | -0.17853 | -0.20142 | -0.004577 | -0.07782 | -0.036621 | -0.077819 | -0.050354 | -0.21057 | -0.045777 | -0.20599 | 0.19226 | 122.3969 | -0.073242 | 122.3007 | 122.3602 | 122.2595 | 122.2641 | 122.2549 | -122.4289 | -122.3373 | 122.3007 | 122.2961 | 59.1476 | 59.1339
781.3125 | 122.5388 | -59.2346 | 63.1485 | -0.035324 | 0.0028348 | 0.063589 | 0.059808 | -0.0015808 | -0.00232 | -0.0017903 | -0.064087 | 0.0037683 | 0.066302 | 0.053021 | -0.0054774 | 0.0096515 | -0.0018136 | -0.10071 | 63.0524 | -59.3216 | 63.0203 | -59.198 | -59.5596 | -59.5322 | -0.19684 | 63.0157 | -59.2712 | 63.1622 | -59.0881 | -59.4772 | -59.3582 | -0.086975 | -0.096131 | -0.12817 | 0.036621 | -0.29755 | -0.32501 | -0.21057 | -0.23804 | -0.036621 | -0.13275 | 0.013732 | 0.14648 | -0.1236 | -0.24262 | -0.086975 | -0.20599 | 0.1236 | 122.3419 | 0.1831 | 122.4335 | 122.374 | 122.287 | 122.287 | 122.2504 | -122.4701 | -122.4197 | 122.2549 | 122.3969 | 59.1339 | 59.0378
782.3125 | 122.5845 | -59.2026 | 63.1073 | -0.042954 | 0.0030484 | 0.062735 | 0.058526 | -0.0028626 | -0.003388 | 0.0016277 | 0.073242 | 0.0027001 | 0.06972 | 0.053021 | -0.0048364 | 0.0092241 | -0.003309 | -0.09613 | 63.0295 | -59.2804 | 63.176 | -58.8501 | -59.3994 | -59.5367 | -0.07782 | 62.9608 | -59.2072 | 63.1165 | -59.2346 | -59.317 | -59.2026 | -0.07782 | -0.07782 | 0.068664 | 0.35248 | -0.33417 | -0.19684 | -0.25635 | -0.11902 | -0.004577 | -0.14649 | 0.009155 | -0.032043 | 0 | -0.11444 | 0.004577 | -0.10986 | 0.4303 | 122.4564 | -0.027466 | 122.3236 | 122.3099 | 122.168 | 122.2321 | 122.1634 | -122.3877 | -122.3145 | 122.3785 | 122.319 | 59.1064 | 59.1248
783.3125 | 122.4747 | -59.2392 | 63.1165 | -0.065842 | 0.0039028 | 0.064016 | 0.062585 | 0.00034182 | -0.0025336 | -0.0020039 | -0.061035 | 0.0041955 | 0.066516 | 0.061993 | -0.00505 | 0.010506 | -0.0011728 | -0.07782 | 63.0478 | -59.317 | 63.0615 | -59.1888 | -59.5734 | -59.5322 | -0.17853 | 63.0066 | -59.2346 | 63.0615 | -59.3491 | -59.4681 | -59.2896 | -0.07782 | -0.068664 | -0.054932 | 0.050354 | -0.29297 | -0.33417 | -0.21515 | -0.25635 | 0.004578 | -0.10986 | -0.054932 | -0.10986 | -0.050354 | -0.22888 | -0.054932 | -0.23346 | 0.12817 | 122.3785 | -0.11444 | 122.2961 | 122.3648 | 122.2412 | 122.287 | 122.2458 | -122.4335 | -122.3511 | 122.3007 | 122.3007 | 59.1614 | 59.0607
784.3125 | 122.5021 | -59.2255 | 63.1119 | -0.16502 | 0.002194 | 0.061453 | 0.061944 | 0.00034182 | -0.0016792 | -0.00093566 | -0.057983 | 0.0020593 | 0.069079 | 0.063702 | -0.0063318 | 0.010292 | -0.0011728 | 0.10986 | 63.0569 | -59.3216 | 63.0249 | -59.1751 | -59.5276 | -59.523 | -0.16937 | 63.0249 | -59.2346 | 63.0707 | -59.3079 | -59.4498 | -59.3079 | -0.09613 | -0.054931 | -0.086975 | 0.050354 | -0.29755 | -0.30212 | -0.20142 | -0.20599 | -0.009155 | -0.086975 | -0.041198 | -0.082397 | -0.082397 | -0.2243 | -0.073242 | -0.21515 | 0.14648 | 122.3465 | -0.073242 | 122.3053 | 122.3785 | 122.2595 | 122.2824 | 122.2504 | -122.4335 | -122.3465 | 122.2504 | 122.2961 | 59.3353 | 59.0561
785.3125 | 122.5159 | -59.2438 | 63.089 | -0.042954 | 0.001553 | 0.065085 | 0.059167 | -0.0022218 | -0.0044562 | -0.0011493 | -0.030517 | 0.0018457 | 0.066302 | 0.063916 | -0.0048364 | 0.0075153 | 0.0007498 | -0.027466 | 63.0157 | -59.3674 | 62.9883 | -59.111 | -59.5367 | -59.5825 | -0.16937 | 63.0203 | -59.2484 | 63.0478 | -59.3079 | -59.4269 | -59.2758 | -0.1236 | -0.073242 | -0.10071 | 0.13275 | -0.33875 | -0.29297 | -0.21515 | -0.16937 | -0.004578 | -0.068664 | -0.041198 | -0.064087 | -0.032044 | -0.18311 | -0.027466 | -0.17853 | 0.25635 | 122.3557 | -0.059509 | 122.2961 | 122.3831 | 122.2687 | 122.2595 | 122.2641 | -122.4564 | -122.3373 | 122.2321 | 122.2916 | 59.2163 | 59.0744
786.3125 | 122.5021 | -59.2438 | 63.1485 | -0.073471 | 0.0043302 | 0.065512 | 0.06109 | 0.00055542 | -0.0036018 | -8.1264e-05 | -0.033569 | 0.0033411 | 0.066302 | 0.065411 | -0.0059046 | 0.010506 | 0.0016044 | -0.07782 | 63.0341 | -59.3124 | 63.0615 | -59.1476 | -59.5184 | -59.4955 | -0.1236 | 63.0112 | -59.2484 | 63.0432 | -59.3124 | -59.4498 | -59.285 | -0.068665 | -0.11444 | -0.086976 | 0.09613 | -0.25177 | -0.27466 | -0.18311 | -0.20599 | -0.004578 | -0.13733 | -0.10529 | -0.068665 | -0.041199 | -0.20599 | -0.036621 | -0.20142 | 0.16479 | 122.374 | -0.064087 | 122.2916 | 122.3465 | 122.2595 | 122.2778 | 122.2549 | -122.4609 | -122.3969 | 122.3053 | 122.287 | 59.166 | 59.1202
787.3125 | 122.5433 | -59.2438 | 63.0981 | -0.081101 | 0.001553 | 0.063589 | 0.058954 | -0.00051278 | -0.0036018 | -0.0045673 | -0.024414 | 0.0022729 | 0.066089 | 0.059216 | -0.0074 | 0.010079 | 0.0005362 | -0.12817 | 63.0569 | -59.3262 | 63.0249 | -59.1522 | -59.5459 | -59.5093 | -0.15564 | 62.97 | -59.2529 | 63.089 | -59.2804 | -59.3948 | -59.285 | -0.082398 | -0.041199 | -0.073243 | 0.091552 | -0.2655 | -0.30212 | -0.1831 | -0.21973 | -0.009156 | -0.12817 | -0.009156 | -0.036622 | -0.041199 | -0.15106 | -0.032043 | -0.14191 | 0.17395 | 122.3511 | -0.027466 | 122.3419 | 122.3831 | 122.2229 | 122.3007 | 122.2137 | -122.4243 | -122.3511 | 122.2687 | 122.3328 | 59.1156 | 59.0881
788.3125 | 122.5159 | -59.23 | 63.1027 | -0.08873 | 0.0036892 | 0.062521 | 0.061731 | 0.0020508 | -0.0038154 | 0.00055974 | -0.05188 | 0.0033411 | 0.066089 | 0.068829 | -0.0044092 | 0.010079 | 0.0030996 | -0.1236 | 63.0569 | -59.3353 | 62.8876 | -59.5871 | -59.5276 | -59.2163 | -0.21515 | 63.0249 | -59.2392 | 63.0615 | -59.3399 | -59.4406 | -59.3216 | -0.10529 | -0.045776 | -0.21515 | -0.35706 | 0.013733 | -0.29755 | 0.11902 | -0.19226 | -0.009155 | -0.07782 | -0.041199 | -0.10986 | -0.091552 | -0.21057 | -0.082397 | -0.20142 | -0.25177 | 122.2229 | -0.10071 | 122.3007 | 122.3923 | 122.2641 | 122.287 | 122.2549 | -122.438 | -122.3419 | 122.1176 | 122.2916 | 59.1064 | 59.0149
789.3125 | 122.525 | -59.2209 | 63.089 | -0.073471 | 0.0043302 | 0.064016 | 0.060022 | -0.0028626 | -0.0063788 | 0.00013254 | -0.027466 | 0.0037683 | 0.065875 | 0.05473 | -0.0052638 | 0.0094379 | -0.0035226 | -0.12817 | 63.0341 | -59.3399 | 63.0386 | -59.1568 | -59.5505 | -59.523 | -0.16022 | 63.002 | -59.2438 | 63.0661 | -59.2758 | -59.4223 | -59.2758 | -0.11902 | -0.054931 | -0.050354 | 0.064087 | -0.30212 | -0.32959 | -0.1831 | -0.21057 | -0.022888 | -0.086975 | -0.022888 | -0.054932 | -0.054932 | -0.20142 | -0.032044 | -0.17853 | 0.18311 | 122.3785 | -0.032044 | 122.3099 | 122.374 | 122.2458 | 122.2549 | 122.2229 | -122.4289 | -122.3328 | 122.2595 | 122.287 | 59.0927 | 59.0607
790.3125 | 122.5204 | -59.2575 | 63.1119 | -0.096359 | 0.0043302 | 0.062308 | 0.063226 | 0.0052552 | -0.0012518 | -0.0022175 | -0.024414 | 0.0018457 | 0.064593 | 0.060925 | -0.0048364 | 0.0092241 | -0.0056588 | -0.13733 | 63.0432 | -59.3399 | 63.0341 | -59.1522 | -59.5734 | -59.523 | -0.15564 | 62.9974 | -59.2484 | 63.089 | -59.3079 | -59.4223 | -59.2667 | -0.082398 | -0.068664 | -0.077819 | 0.10528 | -0.2655 | -0.31586 | -0.1831 | -0.23346 | 0.009155 | -0.11444 | -0.022888 | -0.050354 | -0.009156 | -0.1648 | -0.018311 | -0.17395 | 0.18768 | 122.374 | -0.059509 | 122.3373 | 122.3831 | 122.2458 | 122.3007 | 122.2549 | -122.4518 | -122.3602 | 122.2916 | 122.3465 | 59.1202 | 59.1019
791.3125 | 122.525 | -59.2392 | 63.089 | -0.08873 | 0.0030484 | 0.063803 | 0.061731 | -0.00072638 | -0.0053108 | -0.00072206 | -0.042725 | 0.0035547 | 0.06502 | 0.063702 | -0.005691 | 0.0087969 | -0.0024546 | -0.13733 | 63.0478 | -59.3353 | 63.0203 | -59.1568 | -59.5688 | -59.5001 | -0.17395 | 63.002 | -59.2438 | 63.0798 | -59.3033 | -59.4131 | -59.2896 | -0.09613 | -0.041198 | -0.068664 | 0.082398 | -0.26093 | -0.32959 | -0.16479 | -0.23346 | -0.004577 | -0.086975 | -0.009155 | -0.064087 | -0.050354 | -0.17395 | -0.045777 | -0.16937 | 0.17853 | 122.3557 | -0.05951 | 122.3236 | 122.3831 | 122.2458 | 122.287 | 122.2412 | -122.4243 | -122.3328 | 122.2595 | 122.319 | 59.1019 | 59.0652
792.3125 | 122.5937 | -59.1843 | 63.0753 | -0.081101 | 0.003262 | 0.063803 | 0.060022 | -0.0030762 | -0.0014654 | -0.00050846 | -0.024414 | 0.00013675 | 0.06737 | 0.059216 | -0.0063318 | 0.0092241 | 0.0041678 | -0.14191 | 63.0157 | -59.3216 | 63.0615 | -59.1156 | -59.5093 | -59.4864 | -0.11444 | 62.9791 | -59.23 | 63.1485 | -59.2072 | -59.3216 | -59.166 | -0.13733 | -0.059509 | -0.013733 | 0.068664 | -0.30212 | -0.32501 | -0.1648 | -0.18768 | -0.045777 | -0.09613 | 0.073243 | -0.022888 | 0.01831 | -0.13733 | 0.064087 | -0.091552 | 0.20599 | 122.3831 | 0.022889 | 122.3785 | 122.3373 | 122.2092 | 122.2 | 122.1634 | -122.3969 | -122.3053 | 122.2458 | 122.3328 | 59.0424 | 59.0698
793.3125 | 122.4289 | -59.2438 | 63.1393 | -0.035324 | 0.0045438 | 0.064444 | 0.060876 | -0.0013672 | -0.0025336 | 0.0016277 | -0.061035 | 0.0016321 | 0.066302 | 0.069043 | -0.0031274 | 0.01072 | -0.0058724 | -0.11444 | 63.0615 | -59.3445 | 63.0249 | -59.2026 | -59.5825 | -59.5276 | -0.18768 | 63.0295 | -59.2209 | 62.8967 | -58.9966 | -59.2163 | -59.2529 | -0.10071 | -0.07782 | -0.11444 | 0.041198 | -0.28381 | -0.33875 | -0.18311 | -0.23804 | 0.022888 | -0.10986 | -0.24261 | 0.24719 | -0.009156 | 0.027465 | -0.032044 | 0.004577 | 0.14191 | 122.3694 | 0.2243 | 122.1176 | 122.406 | 122.2504 | 122.3053 | 122.2733 | -122.4838 | -122.3602 | 122.2687 | 122.1405 | 59.1293 | 59.0561
794.3125 | 122.5479 | -59.2255 | 63.1348 | -0.058212 | 0.0026212 | 0.066153 | 0.060022 | 0.0044006 | -0.0038154 | 0.00013254 | -0.030517 | 0.0046227 | 0.065448 | 0.060712 | -0.0048364 | 0.0085833 | -0.0030954 | -0.10071 | 63.0386 | -59.3308 | 63.0203 | -59.1934 | -59.5779 | -59.5322 | -0.20142 | 63.0386 | -59.2529 | 62.9837 | -59.6191 | -59.3308 | -59.0744 | -0.10529 | -0.096131 | -0.11444 | 0.032044 | -0.3067 | -0.35248 | -0.20142 | -0.24719 | -0.027466 | -0.096131 | -0.15106 | -0.39368 | 0.15106 | -0.10529 | 0.17853 | -0.07782 | 0.13733 | 122.3511 | -0.36621 | 122.2366 | 122.3694 | 122.2916 | 122.2641 | 122.2641 | -122.4655 | -122.3877 | 122.2458 | 122.2092 | 59.1248 | 59.024
795.3125 | 122.5067 | -59.2209 | 63.1119 | -0.058212 | 0.002194 | 0.063589 | 0.059167 | 0.00034182 | -0.0029608 | -8.1264e-05 | -0.024414 | 0.0022729 | 0.06502 | 0.060498 | -0.0054774 | 0.0083697 | 0.0007498 | -0.15564 | 63.0524 | -59.3262 | 63.0249 | -59.1751 | -59.5734 | -59.5322 | -0.17395 | 62.9837 | -59.2438 | 63.0753 | -59.2941 | -59.4269 | -59.285 | -0.10529 | -0.059509 | -0.086975 | 0.045776 | -0.31128 | -0.35248 | -0.20599 | -0.24719 | -0.022888 | -0.12817 | -0.036621 | -0.073242 | -0.064087 | -0.20599 | -0.041199 | -0.18311 | 0.15106 | 122.3511 | -0.050354 | 122.319 | 122.3785 | 122.2275 | 122.2733 | 122.2046 | -122.438 | -122.3557 | 122.2458 | 122.2961 | 59.0652 | 59.0469
796.3125 | 122.5525 | -59.1934 | 63.0524 | -0.065842 | 0.0036892 | 0.061453 | 0.061517 | 0.0029052 | -0.0018928 | -0.0011493 | -0.024414 | -0.00029045 | 0.067157 | 0.061993 | -0.003982 | 0.010933 | -0.003309 | -0.13733 | 63.0295 | -59.3079 | 63.0432 | -59.1248 | -59.5322 | -59.4818 | -0.10986 | 62.97 | -59.2255 | 63.1073 | -59.2346 | -59.3674 | -59.23 | -0.11444 | -0.022888 | -0.009155 | 0.068664 | -0.28839 | -0.33875 | -0.17395 | -0.2243 | -0.032044 | -0.082397 | 0.054932 | -0.041199 | -0.036622 | -0.17395 | -0.004578 | -0.14191 | 0.18311 | 122.3511 | -0.009155 | 122.3328 | 122.3373 | 122.1954 | 122.2229 | 122.1634 | -122.3602 | -122.2778 | 122.2366 | 122.3007 | 59.0561 | 59.0836
797.3125 | 122.5983 | -59.1888 | 63.0753 | -0.081101 | 0.003262 | 0.062308 | 0.05874 | 0.004187 | 0.00045724 | 0.0012005 | 0.015259 | 0.00035035 | 0.066943 | 0.067548 | -0.005691 | 0.0085833 | -0.0009592 | -0.086975 | 62.9929 | -59.3124 | 63.1302 | -59.0286 | -59.436 | -59.3994 | -0.036621 | 62.9471 | -59.23 | 63.0478 | -59.0698 | -59.0469 | -59.0057 | -0.1236 | -0.082397 | 0.054932 | 0.16022 | -0.21057 | -0.24719 | -0.086975 | -0.1236 | -0.041199 | -0.12817 | -0.027465 | 0.11902 | 0.18311 | 0.14191 | 0.2243 | 0.18311 | 0.28381 | 122.4426 | 0.16022 | 122.2778 | 122.3053 | 122.1771 | 122.1817 | 122.1359 | -122.3877 | -122.3053 | 122.319 | 122.2366 | 59.1019 | 59.1522
798.3125 | 122.5525 | -59.2209 | 63.089 | -0.096359 | 0.0009122 | 0.06423 | 0.059381 | 0.00098262 | -0.0012518 | 0.00013254 | -0.030517 | 0.0020593 | 0.064166 | 0.057935 | -0.0054774 | 0.0083697 | -0.0041636 | -0.13733 | 63.0524 | -59.317 | 63.0569 | -59.1293 | -59.5322 | -59.491 | -0.13733 | 62.9791 | -59.2346 | 63.1119 | -59.2621 | -59.3582 | -59.2392 | -0.096131 | -0.036621 | -0.032043 | 0.091553 | -0.27008 | -0.31128 | -0.17395 | -0.21515 | -0.013733 | -0.10986 | 0.022888 | -0.041199 | -0.018311 | -0.13733 | -0.004578 | -0.1236 | 0.18768 | 122.374 | -0.027466 | 122.3465 | 122.3694 | 122.2137 | 122.2733 | 122.2 | -122.406 | -122.3236 | 122.2778 | 122.3328 | 59.0836 | 59.0836
799.3125 | 122.5479 | -59.2163 | 63.0707 | -0.020065 | 0.0024076 | 0.062308 | 0.060663 | -0.0015808 | -0.0012518 | -0.00050846 | -0.030517 | 0.0022729 | 0.068652 | 0.062207 | -0.0061182 | 0.0075153 | 0.001818 | -0.12817 | 63.0386 | -59.3216 | 63.0615 | -59.1476 | -59.5184 | -59.4955 | -0.1236 | 62.9745 | -59.2484 | 63.1073 | -59.2621 | -59.3857 | -59.2346 | -0.10528 | -0.032044 | -0.009156 | 0.068665 | -0.27923 | -0.30212 | -0.17395 | -0.19684 | -0.032043 | -0.096131 | 0.036621 | -0.045776 | -0.01831 | -0.16937 | 0.013733 | -0.13733 | 0.17395 | 122.3831 | -0.013733 | 122.3557 | 122.3602 | 122.2229 | 122.2549 | 122.1909 | -122.3923 | -122.319 | 122.2778 | 122.3236 | 59.0881 | 59.0927
800.3125 | 122.5159 | -59.2346 | 63.1073 | 0.10963 | 0.0017666 | 0.065939 | 0.061303 | 0.0046142 | -0.0044562 | -0.0020039 | -0.05188 | 0.0022729 | 0.068866 | 0.053662 | -0.0044092 | 0.010292 | -0.0001046 | -0.15106 | 63.0615 | -59.3216 | 63.0386 | -59.1843 | -59.5642 | -59.4955 | -0.18768 | 63.0066 | -59.23 | 63.0753 | -59.2987 | -59.436 | -59.2667 | -0.086975 | -0.045777 | -0.068665 | 0.050354 | -0.26093 | -0.32959 | -0.17395 | -0.24262 | 0.004577 | -0.10071 | -0.032044 | -0.064087 | -0.032044 | -0.20142 | -0.036621 | -0.20599 | 0.13733 | 122.3602 | -0.068664 | 122.3053 | 122.3831 | 122.2366 | 122.2961 | 122.2412 | -122.4289 | -122.3373 | 122.2733 | 122.3099 | 59.0836 | 59.0469
801.3125 | 122.5113 | -59.2392 | 63.1027 | 0.13252 | 0.0017666 | 0.06423 | 0.061517 | -8.538e-05 | -0.004029 | -0.0028583 | -0.036621 | 0.0035547 | 0.068011 | 0.05708 | -0.0054774 | 0.010933 | 0.000109 | -0.054932 | 63.0798 | -59.3124 | 63.0478 | -59.166 | -59.5596 | -59.5184 | -0.19226 | 63.0066 | -59.2484 | 63.0569 | -59.3079 | -59.4452 | -59.2987 | -0.073242 | -0.022888 | -0.054931 | 0.073242 | -0.27924 | -0.32043 | -0.20599 | -0.24719 | -0.009155 | -0.09613 | -0.045776 | -0.068664 | -0.059509 | -0.20599 | -0.050354 | -0.19684 | 0.14648 | 122.3602 | -0.059509 | 122.3053 | 122.3923 | 122.2549 | 122.319 | 122.2458 | -122.4152 | -122.3511 | 122.287 | 122.2961 | 59.1843 | 59.0469
802.3125 | 122.5616 | -59.2255 | 63.0707 | -0.073471 | 0.0019802 | 0.062308 | 0.058313 | -0.0032898 | -0.0021064 | 0.00013254 | 0.064087 | 0.00035035 | 0.065875 | 0.054944 | -0.0059046 | 0.0092241 | -0.0018136 | -0.10986 | 63.0295 | -59.3079 | 63.089 | -59.0881 | -59.4727 | -59.4223 | -0.041199 | 62.9654 | -59.1751 | 63.1119 | -59.2392 | -59.285 | -59.2117 | -0.082397 | -0.041199 | 0.01831 | 0.13733 | -0.19684 | -0.24719 | -0.11444 | -0.16479 | 0.050354 | -0.10529 | 0.041198 | -0.013733 | 0.013733 | -0.059509 | -0.036621 | -0.10986 | 0.21973 | 122.3969 | -0.064087 | 122.287 | 122.3373 | 122.1405 | 122.2549 | 122.1909 | -122.3785 | -122.2458 | 122.3145 | 122.3373 | 59.1156 | 59.1843
803.3125 | 122.5662 | -59.2209 | 63.0844 | -0.058212 | 0.001553 | 0.062735 | 0.060449 | -0.00072638 | -0.0027472 | -0.00050846 | -0.045776 | 0.00099115 | 0.06737 | 0.057935 | -0.0069726 | 0.0090105 | 0.0009634 | -0.13275 | 63.0157 | -59.3079 | 63.0524 | -59.166 | -59.5322 | -59.4864 | -0.13733 | 62.9837 | -59.2209 | 63.1027 | -59.2529 | -59.3811 | -59.2438 | -0.086975 | -0.068665 | -0.032044 | 0.054931 | -0.2655 | -0.31128 | -0.17853 | -0.2243 | 0 | -0.10071 | 0.01831 | -0.032044 | -0.022888 | -0.16022 | -0.022888 | -0.16022 | 0.14191 | 122.3602 | -0.032044 | 122.3236 | 122.3236 | 122.2046 | 122.2366 | 122.2046 | -122.3923 | -122.3053 | 122.2733 | 122.3236 | 59.0881 | 59.0836
804.3125 | 122.6486 | -59.2255 | 63.0707 | -0.10399 | 0.0041166 | 0.063803 | 0.060663 | 0.0018372 | -0.0044562 | -0.0015765 | -0.0030517 | 0.0020593 | 0.066516 | 0.061566 | -0.0069726 | 0.011147 | -0.003309 | -0.091553 | 62.9974 | -59.3262 | 63.1348 | -59.0469 | -59.4452 | -59.4086 | -0.041199 | 62.9517 | -59.2209 | 63.1714 | -59.1431 | -59.4406 | -59.3079 | -0.10071 | -0.073242 | 0.064087 | 0.17853 | -0.1831 | -0.21973 | -0.082397 | -0.11902 | 0.004578 | -0.11902 | 0.10071 | 0.082398 | -0.082397 | -0.21515 | -0.086975 | -0.21973 | 0.27924 | 122.4609 | 0.07782 | 122.3923 | 122.3236 | 122.1725 | 122.2229 | 122.1771 | -122.3969 | -122.2916 | 122.3602 | 122.3969 | 59.1339 | 59.1843
805.3125 | 122.612 | -59.2117 | 63.0203 | -0.08873 | 0.003262 | 0.062308 | 0.06109 | 0.0037598 | -0.0025336 | -0.0015765 | -0.024414 | 0.0039819 | 0.066302 | 0.058148 | -0.0065454 | 0.0096515 | -0.0065134 | -0.10986 | 63.002 | -59.3216 | 63.1256 | -59.0744 | -59.4498 | -59.3994 | -0.064087 | 62.9608 | -59.2117 | 63.1805 | -59.1934 | -59.2987 | -59.1385 | -0.10986 | -0.018311 | 0.10529 | 0.13733 | -0.18768 | -0.23804 | -0.07782 | -0.12817 | 0 | -0.05951 | 0.16022 | 0.018311 | 0.073242 | -0.086975 | 0.073242 | -0.086975 | 0.24719 | 122.4472 | 0.018311 | 122.3923 | 122.3236 | 122.1725 | 122.2137 | 122.1725 | -122.3419 | -122.2321 | 122.3373 | 122.3923 | 59.1019 | 59.1476
806.3125 | 122.6257 | -59.1843 | 63.0524 | -0.020065 | 5.76e-05 | 0.061667 | 0.059381 | -0.0056396 | 0.00045724 | -0.0034991 | -0.057983 | 0.0027001 | 0.06438 | 0.059216 | -0.0076136 | 0.010079 | -0.0003182 | -0.10529 | 62.9791 | -59.3262 | 63.121 | -59.0515 | -59.4589 | -59.4315 | -0.054932 | 62.9562 | -59.2255 | 63.1805 | -59.198 | -59.3216 | -59.1614 | -0.14191 | -0.073242 | 0.068665 | 0.13275 | -0.24719 | -0.27466 | -0.10529 | -0.13275 | -0.041199 | -0.09613 | 0.12817 | -0.013733 | 0.022888 | -0.13733 | 0.064087 | -0.09613 | 0.27466 | 122.4472 | 0.027466 | 122.406 | 122.3053 | 122.1817 | 122.1634 | 122.1405 | -122.3785 | -122.2778 | 122.3053 | 122.3648 | 59.079 | 59.1293
807.3125 | 122.5296 | -59.2392 | 63.0936 | -0.058212 | 0.0017666 | 0.061453 | 0.061731 | -0.004358 | -0.0048834 | 0.0014141 | -0.057983 | 0.0016321 | 0.066729 | 0.061139 | -0.0031274 | 0.0090105 | 0.000109 | -0.13733 | 63.0341 | -59.3216 | 63.0341 | -59.166 | -59.5459 | -59.4955 | -0.15564 | 63.0066 | -59.2346 | 63.0936 | -59.2804 | -59.3903 | -59.2438 | -0.082397 | -0.059509 | -0.059509 | 0.073242 | -0.25635 | -0.3067 | -0.17395 | -0.2243 | 0.004578 | -0.086975 | 0 | -0.041199 | -0.004577 | -0.15106 | -0.009155 | -0.15564 | 0.15564 | 122.3557 | -0.045777 | 122.3282 | 122.3557 | 122.2412 | 122.2733 | 122.2458 | -122.4152 | -122.3282 | 122.2733 | 122.3328 | 59.1019 | 59.0836
808.3125 | 122.5021 | -59.2392 | 63.089 | -0.065842 | 5.76e-05 | 0.064444 | 0.060876 | -0.00029898 | -0.0031744 | -0.00029486 | -0.039673 | 0.0024865 | 0.068652 | 0.060498 | -0.005691 | 0.010079 | 0.0009634 | -0.1236 | 63.0432 | -59.3353 | 63.0295 | -59.1705 | -59.5505 | -59.523 | -0.16022 | 63.002 | -59.2255 | 63.0798 | -59.285 | -59.4177 | -59.2667 | -0.09613 | -0.045776 | -0.059509 | 0.068665 | -0.28381 | -0.31128 | -0.18768 | -0.21515 | 0.013733 | -0.086975 | -0.009155 | -0.045776 | -0.027466 | -0.17853 | -0.041199 | -0.19226 | 0.16479 | 122.3648 | -0.059509 | 122.3053 | 122.3785 | 122.2275 | 122.2824 | 122.2412 | -122.4243 | -122.3145 | 122.2687 | 122.319 | 59.1156 | 59.079
809.3125 | 122.6303 | -59.198 | 63.0707 | -0.065842 | 0.003262 | 0.061026 | 0.059595 | 0.0014098 | -0.004029 | -0.0028583 | 0.079346 | 0.0012047 | 0.067798 | 0.057935 | -0.0061182 | 0.0070879 | -0.0041636 | -0.064087 | 62.9883 | -59.2712 | 63.1439 | -58.9828 | -59.697 | -59.5551 | -0.027466 | 62.9471 | -59.1934 | 63.1851 | -59.1888 | -59.2941 | -59.1751 | -0.073242 | -0.082398 | 0.073242 | 0.21515 | -0.35706 | -0.49896 | -0.28381 | -0.42572 | 0.004578 | -0.1236 | 0.11444 | 0.009155 | 0.022888 | -0.09613 | 0.01831 | -0.10071 | 0.28839 | 122.4152 | 0.004577 | 122.3785 | 122.2595 | 122.1405 | 122.1863 | 122.1451 | -122.3419 | -122.2641 | 122.3419 | 122.3831 | 59.1339 | 59.1705
810.3125 | 122.6212 | -59.1843 | 63.0569 | -0.081101 | 0.003262 | 0.063803 | 0.061303 | -0.0039306 | -0.00018376 | -0.0045673 | -0.01831 | -0.00071785 | 0.064166 | 0.059644 | -0.0071864 | 0.0096515 | -0.0013864 | -0.082397 | 62.9883 | -59.3262 | 63.1485 | -59.0424 | -59.4269 | -59.404 | -0.041199 | 62.9608 | -59.2209 | 63.1897 | -59.2117 | -59.3124 | -59.166 | -0.14191 | -0.068665 | 0.091553 | 0.14191 | -0.21973 | -0.24261 | -0.07782 | -0.10071 | -0.036621 | -0.096131 | 0.13275 | -0.027466 | 0.01831 | -0.12817 | 0.054931 | -0.091553 | 0.28381 | 122.4747 | 0.009155 | 122.4106 | 122.3145 | 122.1817 | 122.1725 | 122.1451 | -122.3831 | -122.2778 | 122.3328 | 122.374 | 59.1019 | 59.1431
811.3125 | 122.5754 | -59.2392 | 63.0432 | -0.08873 | 0.001553 | 0.065512 | 0.060663 | -0.0024354 | -0.0042426 | 0.00098694 | -0.042725 | 0.0022729 | 0.067157 | 0.063489 | -0.0065454 | 0.010292 | -0.0026682 | -0.086975 | 63.0066 | -59.317 | 63.1073 | -59.0561 | -59.4223 | -59.404 | -0.064087 | 62.9608 | -59.1888 | 63.1805 | -59.1797 | -59.4635 | -59.3445 | -0.07782 | -0.036621 | 0.064087 | 0.18311 | -0.1648 | -0.18311 | -0.086975 | -0.10529 | 0.050354 | -0.082398 | 0.13733 | 0.05951 | -0.10529 | -0.2243 | -0.15564 | -0.27466 | 0.26093 | 122.4243 | 0.009156 | 122.3694 | 122.3236 | 122.1497 | 122.2458 | 122.2 | -122.3602 | -122.2321 | 122.3465 | 122.4197 | 59.1522 | 59.1751
812.3125 | 122.6349 | -59.1797 | 63.0707 | -0.081101 | 0.003262 | 0.063376 | 0.058313 | 0.00034182 | -0.0031744 | -0.0028583 | 0.021362 | 0.0020593 | 0.06502 | 0.061566 | -0.003982 | 0.0090105 | 0.0016044 | -0.10529 | 63.0157 | -59.2941 | 63.089 | -59.0881 | -59.4543 | -59.4131 | -0.07782 | 62.9608 | -59.2026 | 63.1439 | -59.2072 | -59.3262 | -59.0652 | -0.11444 | -0.054932 | 0.01831 | 0.091552 | -0.23346 | -0.27466 | -0.11902 | -0.16022 | -0.022889 | -0.10986 | 0.073242 | -0.027466 | 0.11444 | -0.14648 | 0.13733 | -0.1236 | 0.20599 | 122.3831 | -0.004577 | 122.3465 | 122.3099 | 122.1634 | 122.1954 | 122.1405 | -122.3648 | -122.2733 | 122.2687 | 122.3236 | 59.0744 | 59.1019
813.3125 | 122.5113 | -59.2346 | 63.089 | -0.073471 | 0.001553 | 0.063162 | 0.061517 | -0.0011536 | -0.0010382 | 0.00055974 | -0.064087 | 0.0020593 | 0.067157 | 0.059216 | -0.0054774 | 0.0085833 | -0.0026682 | -0.14191 | 63.0341 | -59.3079 | 63.0203 | -59.1751 | -59.5688 | -59.5139 | -0.15106 | 62.9837 | -59.2255 | 63.0753 | -59.3033 | -59.4177 | -59.2804 | -0.073242 | -0.054931 | -0.068664 | 0.059509 | -0.27924 | -0.33417 | -0.20599 | -0.26093 | 0.009155 | -0.10528 | -0.013733 | -0.068665 | -0.045777 | -0.18311 | -0.054932 | -0.19226 | 0.13275 | 122.3282 | -0.07782 | 122.3007 | 122.3419 | 122.2092 | 122.2687 | 122.2183 | -122.3969 | -122.3145 | 122.2549 | 122.3099 | 59.0927 | 59.0836
814.3125 | 122.5021 | -59.23 | 63.1027 | -0.020065 | 0.001553 | 0.064444 | 0.062372 | -0.0035034 | -0.004029 | -0.0020039 | -0.082397 | 0.0012047 | 0.068225 | 0.060498 | -0.0052638 | 0.011361 | 0.000109 | -0.12817 | 63.0432 | -59.317 | 63.0341 | -59.1797 | -59.5688 | -59.5093 | -0.16937 | 63.0112 | -59.2392 | 63.0798 | -59.2941 | -59.4315 | -59.2758 | -0.086975 | -0.059509 | -0.068664 | 0.050355 | -0.27923 | -0.33875 | -0.19226 | -0.25177 | -0.009155 | -0.091553 | -0.022888 | -0.064086 | -0.045776 | -0.20142 | -0.036621 | -0.19226 | 0.13733 | 122.3511 | -0.054931 | 122.319 | 122.3602 | 122.2504 | 122.2733 | 122.2412 | -122.4197 | -122.3419 | 122.2641 | 122.3099 | 59.1019 | 59.0607
815.3125 | 122.5067 | -59.2163 | 63.1027 | -0.096359 | -0.001224 | 0.067007 | 0.061731 | 0.0044006 | -0.0029608 | -0.00029486 | -0.073242 | 0.0016321 | 0.065661 | 0.063489 | -0.005691 | 0.011574 | 0.001818 | -0.40283 | 62.97 | -59.3719 | 63.0844 | -59.1888 | -59.6054 | -59.523 | -0.1831 | 63.002 | -59.2392 | 63.089 | -59.317 | -59.4315 | -59.2804 | -0.15564 | -0.13275 | -0.01831 | 0.027466 | -0.3067 | -0.3891 | -0.15106 | -0.23346 | -0.022888 | -0.10071 | -0.013733 | -0.10071 | -0.064087 | -0.21515 | -0.041199 | -0.19226 | 0.18311 | 122.4564 | -0.07782 | 122.3282 | 122.3419 | 122.2412 | 122.1863 | 122.2183 | -122.4747 | -122.3419 | 122.3007 | 122.3053 | 58.8135 | 59.0332
816.3125 | 122.6303 | -59.2026 | 63.0569 | -0.073471 | 0.0036892 | 0.062735 | 0.062372 | -0.00029898 | -0.0021064 | -0.0045673 | -0.048828 | 0.0016321 | 0.066943 | 0.056866 | -0.006759 | 0.011361 | -0.0024546 | -0.11902 | 63.0112 | -59.3262 | 63.089 | -59.0836 | -59.4681 | -59.4589 | -0.07782 | 62.9837 | -59.2484 | 63.1668 | -59.1934 | -59.3124 | -59.1751 | -0.1236 | -0.045777 | 0.032043 | 0.11902 | -0.25635 | -0.2655 | -0.13275 | -0.14191 | -0.045776 | -0.073242 | 0.10986 | 0.009156 | 0.027466 | -0.10986 | 0.073242 | -0.064087 | 0.24262 | 122.4152 | 0.054932 | 122.4152 | 122.3373 | 122.2321 | 122.2137 | 122.1863 | -122.3831 | -122.3053 | 122.2916 | 122.3694 | 59.0836 | 59.1248
817.3125 | 122.5983 | -59.1797 | 63.0661 | -0.10399 | 0.0019802 | 0.06423 | 0.059381 | 0.0050414 | -0.003388 | -0.00050846 | -0.10376 | -0.00093145 | 0.067157 | 0.060284 | -0.0059046 | 0.0083697 | -0.0022408 | -0.059509 | 63.0066 | -59.317 | 63.1485 | -59.0195 | -59.436 | -59.4406 | 0.14191 | 62.9654 | -59.2026 | 63.1851 | -59.1614 | -59.2667 | -59.1293 | -0.13733 | -0.059509 | 0.082398 | 0.16022 | -0.26093 | -0.25635 | -0.1236 | -0.11902 | -0.022889 | -0.10071 | 0.11902 | 0.01831 | 0.050354 | -0.086976 | 0.073243 | -0.064087 | 0.29755 | 122.4655 | 0.041199 | 122.3877 | 122.3236 | 122.168 | 122.1863 | 122.1451 | -122.3831 | -122.2687 | 122.3282 | 122.3648 | 59.1202 | 59.3216
818.3125 | 122.5342 | -59.2346 | 63.0707 | -0.058212 | 0.0030484 | 0.062948 | 0.060876 | 0.0016236 | -0.0014654 | 0.00055974 | -0.05188 | 0.0033411 | 0.068011 | 0.05943 | -0.00505 | 0.011361 | -0.003309 | -0.13733 | 63.0249 | -59.3399 | 63.0478 | -59.1339 | -59.523 | -59.4818 | -0.14648 | 62.9791 | -59.2438 | 63.1256 | -59.2621 | -59.3582 | -59.2438 | -0.10529 | -0.045777 | -0.022888 | 0.10071 | -0.24719 | -0.28839 | -0.14191 | -0.1831 | -0.009155 | -0.091553 | 0.054931 | -0.027466 | -0.009155 | -0.1236 | 0 | -0.11444 | 0.20599 | 122.3877 | -0.018311 | 122.3694 | 122.3648 | 122.2229 | 122.2595 | 122.2137 | -122.4106 | -122.3145 | 122.2824 | 122.3602 | 59.0973 | 59.0881
819.3125 | 122.525 | -59.2255 | 63.0981 | -0.020065 | 0.0013394 | 0.064016 | 0.062158 | 0.0020508 | -0.0044562 | -0.00050846 | -0.054932 | 0.0020593 | 0.067798 | 0.062634 | -0.0080408 | 0.0096515 | -0.003309 | -0.15106 | 63.0249 | -59.3262 | 63.0569 | -59.1614 | -59.5551 | -59.5047 | -0.15564 | 62.9883 | -59.2163 | 63.1073 | -59.2758 | -59.3994 | -59.23 | -0.10071 | -0.073243 | -0.041199 | 0.064087 | -0.27924 | -0.32959 | -0.17853 | -0.22888 | 0.009155 | -0.10986 | 0.009155 | -0.050354 | -0.004578 | -0.17395 | -0.013733 | -0.1831 | 0.16479 | 122.3831 | -0.059509 | 122.3236 | 122.3511 | 122.2046 | 122.2504 | 122.2137 | -122.4243 | -122.3145 | 122.2824 | 122.3328 | 59.0744 | 59.0698
820.3125 | 122.5113 | -59.2209 | 63.1027 | -0.050583 | 0.001553 | 0.063589 | 0.058526 | -0.0032898 | 0.00067084 | -0.0028583 | -0.057983 | 0.0016321 | 0.066729 | 0.061993 | -0.00505 | 0.0090105 | -0.0058724 | -0.15106 | 63.0432 | -59.3536 | 63.0341 | -59.1797 | -59.5551 | -59.5047 | -0.16479 | 63.0066 | -59.2438 | 63.0798 | -59.2941 | -59.4223 | -59.2712 | -0.13275 | -0.059509 | -0.068664 | 0.041199 | -0.28381 | -0.33417 | -0.15106 | -0.20142 | -0.022888 | -0.09613 | -0.022888 | -0.073242 | -0.050354 | -0.20142 | -0.027466 | -0.17853 | 0.17395 | 122.3877 | -0.050354 | 122.3236 | 122.3969 | 122.2504 | 122.2641 | 122.2275 | -122.4564 | -122.3465 | 122.2549 | 122.3007 | 59.0698 | 59.0561
821.3125 | 122.5433 | -59.2758 | 63.1348 | -0.058212 | 0.0047574 | 0.06423 | 0.061731 | 0.00034182 | -0.00232 | 0.0012005 | -0.082397 | 0.0035547 | 0.065875 | 0.062207 | -0.0052638 | 0.0092241 | -0.0030954 | -0.10986 | 63.0569 | -59.3216 | 63.0341 | -59.1797 | -59.5642 | -59.5139 | -0.20142 | 63.0203 | -59.2621 | 63.0478 | -59.2941 | -59.7977 | -59.5917 | -0.045776 | -0.07782 | -0.10071 | 0.096131 | -0.23804 | -0.28839 | -0.19226 | -0.24262 | 0.013733 | -0.11444 | -0.086975 | -0.01831 | -0.31586 | -0.52185 | -0.32959 | -0.53558 | 0.14191 | 122.3557 | -0.032043 | 122.3099 | 122.3785 | 122.2824 | 122.3328 | 122.2961 | -122.4564 | -122.3969 | 122.3099 | 122.3236 | 59.166 | 59.0744
822.3125 | 122.5891 | -59.2255 | 63.0341 | -0.035324 | 0.0045438 | 0.064016 | 0.058526 | 0.00034182 | -0.0053108 | -0.0020039 | -0.01831 | 0.0022729 | 0.064166 | 0.060498 | -0.0061182 | 0.0081561 | -0.0009592 | -0.10529 | 63.0249 | -59.3262 | 63.1256 | -59.0378 | -59.436 | -59.4086 | -0.045776 | 62.9471 | -59.2255 | 63.1805 | -59.1705 | -59.2941 | -59.2621 | -0.10071 | -0.009156 | 0.091552 | 0.18768 | -0.1831 | -0.21057 | -0.082397 | -0.10986 | 0 | -0.086975 | 0.14648 | 0.054932 | -0.036621 | -0.068664 | -0.036621 | -0.068664 | 0.28839 | 122.4518 | 0.054932 | 122.406 | 122.3511 | 122.1725 | 122.2504 | 122.1725 | -122.3602 | -122.2595 | 122.3511 | 122.406 | 59.1202 | 59.1797
823.3125 | 122.5388 | -59.2163 | 63.0707 | -0.058212 | 0.0041166 | 0.064444 | 0.061303 | -0.0013672 | -0.004029 | -0.0028583 | -0.030517 | 0.0027001 | 0.067157 | 0.054089 | -0.0044092 | 0.0083697 | 0.001177 | -0.13275 | 63.0478 | -59.3353 | 63.0249 | -59.1568 | -59.5276 | -59.5093 | -0.16022 | 63.002 | -59.2438 | 63.0981 | -59.2667 | -59.404 | -59.2484 | -0.11902 | -0.022888 | -0.045777 | 0.05951 | -0.29297 | -0.31128 | -0.17395 | -0.19226 | -0.027465 | -0.068665 | 0.027466 | -0.050354 | -0.032043 | -0.18768 | -0.004578 | -0.16022 | 0.17853 | 122.3602 | -0.022889 | 122.3419 | 122.3831 | 122.2458 | 122.2641 | 122.2183 | -122.406 | -122.3145 | 122.2412 | 122.3145 | 59.0836 | 59.0561
824.3125 | 122.5204 | -59.2392 | 63.0844 | -0.096359 | 0.0024076 | 0.063162 | 0.061731 | 0.0011962 | -0.0016792 | -0.00093566 | -0.061035 | 0.0027001 | 0.068652 | 0.063061 | -0.0078272 | 0.0094379 | -0.0022408 | -0.13733 | 63.0569 | -59.3536 | 63.0157 | -59.1614 | -59.5688 | -59.4955 | -0.16022 | 62.9974 | -59.23 | 63.089 | -59.285 | -59.4177 | -59.2667 | -0.11444 | -0.027466 | -0.068665 | 0.07782 | -0.25635 | -0.32959 | -0.14191 | -0.21515 | 0.009155 | -0.086975 | 0.004577 | -0.045776 | -0.027466 | -0.17853 | -0.036621 | -0.18768 | 0.19226 | 122.3694 | -0.054931 | 122.319 | 122.4106 | 122.2275 | 122.2961 | 122.2366 | -122.4381 | -122.3145 | 122.2549 | 122.3282 | 59.1019 | 59.079
825.3125 | 122.5616 | -59.2072 | 63.089 | -0.065842 | 0.0041166 | 0.062948 | 0.058313 | -0.0067078 | -0.0012518 | -0.0045673 | 0.045776 | 0.0016321 | 0.069507 | 0.063061 | -0.0061182 | 0.0075153 | -0.0048044 | -0.09613 | 63.0203 | -59.2758 | 63.1165 | -58.8593 | -59.3033 | -59.4955 | -0.07782 | 62.9791 | -59.2163 | 63.1348 | -59.2163 | -59.3124 | -59.198 | -0.068665 | -0.068664 | 0.027466 | 0.3479 | -0.28839 | -0.096131 | -0.21973 | -0.027466 | -0.009156 | -0.10986 | 0.045777 | -0.009156 | 0.009155 | -0.10529 | 0.018311 | -0.09613 | 0.41656 | 122.3923 | 0 | 122.3511 | 122.2961 | 122.1954 | 122.2275 | 122.1863 | -122.3648 | -122.3053 | 122.3236 | 122.3419 | 59.111 | 59.1293
826.3125 | 122.4701 | -59.2209 | 63.1027 | -0.10399 | 0.0034756 | 0.06423 | 0.063012 | -8.538e-05 | -0.0031744 | 0.00034614 | -0.079346 | 0.0031273 | 0.066943 | 0.060498 | -0.006759 | 0.0094379 | -0.0013864 | -0.09613 | 63.0615 | -59.3536 | 63.0432 | -59.1751 | -59.5596 | -59.5276 | -0.1831 | 63.0386 | -59.2621 | 63.0478 | -59.3216 | -59.4727 | -59.2804 | -0.13275 | -0.041199 | -0.059509 | 0.045776 | -0.3067 | -0.33875 | -0.17395 | -0.20599 | -0.041199 | -0.064087 | -0.054931 | -0.10071 | -0.05951 | -0.25177 | -0.018311 | -0.21057 | 0.17853 | 122.3969 | -0.059509 | 122.3099 | 122.4152 | 122.3007 | 122.2824 | 122.2595 | -122.4564 | -122.3648 | 122.2641 | 122.2687 | 59.1248 | 59.0378
827.3125 | 122.5845 | -59.198 | 63.0798 | -0.08873 | 0.0041166 | 0.065085 | 0.057886 | 0.00076902 | -0.00232 | -0.0032855 | -0.012207 | 0.0018457 | 0.067798 | 0.056866 | -0.0044092 | 0.010079 | -0.0003182 | -0.07782 | 62.9883 | -59.2941 | 63.1348 | -59.0286 | -59.4406 | -59.3948 | -0.032043 | 62.9333 | -59.2026 | 63.1393 | -59.2072 | -59.3124 | -59.2026 | -0.09613 | -0.091553 | 0.054932 | 0.16937 | -0.19684 | -0.24262 | -0.10071 | -0.14648 | -0.004578 | -0.14648 | 0.059509 | -0.009155 | -0.004578 | -0.11444 | 0 | -0.10986 | 0.2655 | 122.4289 | -0.004577 | 122.3419 | 122.2824 | 122.1359 | 122.1863 | 122.1313 | -122.374 | -122.2824 | 122.3328 | 122.3373 | 59.1202 | 59.166
828.3125 | 122.493 | -59.1888 | 63.121 | -0.012436 | 0.0028348 | 0.062735 | 0.061303 | -0.00093998 | -0.0029608 | -0.0039265 | -0.061035 | 0.0033411 | 0.065234 | 0.064984 | -0.0065454 | 0.010079 | -0.0043772 | -0.022888 | 63.0524 | -59.3033 | 63.1027 | -59.079 | -59.4681 | -59.4315 | -0.064087 | 63.0432 | -59.1843 | 63.121 | -59.2346 | -59.3811 | -59.2392 | -0.11444 | -0.068665 | -0.018311 | 0.10986 | -0.24262 | -0.27924 | -0.12817 | -0.1648 | 0.004578 | -0.07782 | 0 | -0.045776 | -0.050354 | -0.19226 | -0.054932 | -0.19684 | 0.22431 | 122.406 | -0.050354 | 122.3053 | 122.3557 | 122.2275 | 122.2412 | 122.2321 | -122.4243 | -122.3053 | 122.2916 | 122.3099 | 59.166 | 59.1248
829.3125 | 122.5021 | -59.2255 | 63.1348 | -0.035324 | 0.0039028 | 0.062308 | 0.062585 | -0.0013672 | -0.0025336 | -0.0020039 | -0.05188 | 0.0012047 | 0.064807 | 0.06947 | -0.0052638 | 0.010079 | 0.000109 | -0.064087 | 63.0524 | -59.2987 | 63.0661 | -59.1202 | -59.5047 | -59.4864 | -0.10071 | 63.0157 | -59.2209 | 63.0844 | -59.2941 | -59.4269 | -59.2621 | -0.073242 | -0.082398 | -0.068665 | 0.10529 | -0.26093 | -0.27924 | -0.18768 | -0.20599 | 0.004578 | -0.11902 | -0.050354 | -0.068664 | -0.036621 | -0.20142 | -0.041199 | -0.20599 | 0.17853 | 122.3648 | -0.073242 | 122.3053 | 122.3511 | 122.2366 | 122.2778 | 122.2412 | -122.4335 | -122.3557 | 122.2916 | 122.3099 | 59.1614 | 59.1248
830.3125 | 122.5891 | -59.1843 | 63.1073 | -0.042954 | 0.0036892 | 0.063803 | 0.055749 | -0.0030762 | -0.0021064 | -0.0015765 | 0.057983 | 0.0022729 | 0.065875 | 0.050458 | -0.006759 | 0.0068743 | -0.003309 | -0.082397 | 63.0295 | -59.2575 | 62.9883 | -59.1248 | -59.4315 | -59.4406 | -0.10529 | 62.9654 | -59.2072 | 63.1393 | -59.2072 | -59.2987 | -59.1934 | -0.073242 | -0.07782 | -0.11902 | 0.059509 | -0.25635 | -0.24719 | -0.18311 | -0.17395 | -0.022888 | -0.14191 | 0.032043 | -0.022888 | -0.009155 | -0.11444 | 0.013733 | -0.091553 | 0.13275 | 122.2458 | 0 | 122.3465 | 122.287 | 122.1725 | 122.2137 | 122.1497 | -122.3648 | -122.3145 | 122.1725 | 122.3236 | 59.1019 | 59.079
831.3125 | 122.3465 | -59.2621 | 63.0432 | -0.050583 | 0.0026212 | 0.063803 | 0.060235 | -0.0017944 | -0.0016792 | 0.00055974 | -0.07019 | 0.0012047 | 0.066089 | 0.063061 | -0.0052638 | 0.0085833 | -0.005018 | -0.10529 | 63.0295 | -59.3216 | 63.0432 | -59.1751 | -59.5551 | -59.5413 | -0.19226 | 62.9974 | -59.2346 | 63.0432 | -59.3353 | -59.4635 | -59.2941 | -0.059509 | -0.013733 | 0 | 0.086975 | -0.27924 | -0.29297 | -0.21973 | -0.23346 | 0.027466 | -0.045776 | 0 | -0.073242 | -0.032043 | -0.20142 | -0.059509 | -0.22888 | 0.14648 | 122.3648 | -0.10071 | 122.2778 | 122.3511 | 122.2321 | 122.2916 | 122.2595 | -122.3648 | -122.2778 | 122.3053 | 122.3053 | 59.1568 | 59.0698
832.3125 | 122.6074 | -59.1843 | 63.0753 | -0.096359 | 0.0041166 | 0.065085 | 0.059808 | 0.0011962 | -0.0016792 | -0.0030719 | -0.0091553 | -0.00093145 | 0.06502 | 0.061352 | -0.0044092 | 0.0070879 | -0.0024546 | -0.050354 | 62.9745 | -59.285 | 63.1485 | -59.024 | -59.4177 | -59.3811 | -0.050354 | 62.9791 | -59.2209 | 63.1805 | -59.166 | -59.2941 | -59.1751 | -0.10071 | -0.10071 | 0.073243 | 0.16022 | -0.19684 | -0.23346 | -0.096131 | -0.13275 | -0.036621 | -0.09613 | 0.10529 | 0.01831 | 0.009155 | -0.10986 | 0.045776 | -0.073242 | 0.26093 | 122.4335 | 0.054931 | 122.4014 | 122.2595 | 122.2 | 122.1588 | 122.1634 | -122.3602 | -122.2961 | 122.3328 | 122.3648 | 59.1339 | 59.1339
833.3125 | 122.5021 | -59.2346 | 63.1348 | -0.012436 | 0.001553 | 0.062735 | 0.062585 | 0.00098262 | -0.0025336 | 0.0035503 | -0.061035 | 0.0039819 | 0.068011 | 0.05943 | -0.0052638 | 0.0081561 | -0.0011728 | -0.091553 | 63.0569 | -59.3308 | 63.0615 | -59.1431 | -59.5276 | -59.4955 | -0.16479 | 63.0386 | -59.2163 | 63.0798 | -59.3124 | -59.436 | -59.2896 | -0.096131 | -0.07782 | -0.073243 | 0.091553 | -0.26093 | -0.29297 | -0.16479 | -0.19684 | 0.01831 | -0.096131 | -0.054932 | -0.07782 | -0.054932 | -0.20142 | -0.073242 | -0.21973 | 0.18768 | 122.3923 | -0.09613 | 122.2961 | 122.3877 | 122.2549 | 122.2916 | 122.2733 | -122.4655 | -122.3511 | 122.2961 | 122.3145 | 59.1431 | 59.0698
834.3125 | 122.4884 | -59.2163 | 63.1119 | -0.081101 | 0.000485 | 0.062948 | 0.063012 | 0.0031188 | 0.0013116 | 0.00055974 | -0.10681 | 0.0018457 | 0.066302 | 0.056012 | -0.0061182 | 0.0096515 | -0.0020272 | -0.14191 | 63.0432 | -59.3308 | 62.7823 | -59.2529 | -59.0836 | -59.3308 | -0.10986 | 63.0295 | -59.2438 | 63.0707 | -59.2941 | -59.4543 | -59.2941 | -0.11444 | -0.068664 | -0.32959 | -0.036621 | -0.11444 | 0.13275 | 0 | 0.24719 | -0.027465 | -0.082397 | -0.041198 | -0.077819 | -0.077819 | -0.23804 | -0.050354 | -0.21057 | 0.07782 | 122.113 | -0.050354 | 122.3145 | 122.374 | 122.2733 | 122.2595 | 122.2458 | -122.4426 | -122.3557 | 121.9986 | 122.287 | 59.0744 | 59.1064
835.3125 | 122.5708 | -59.1934 | 63.0981 | -0.16502 | 0.0019802 | 0.063803 | 0.058313 | -0.00093998 | -0.0027472 | -0.00050846 | 0.061035 | 0.00077755 | 0.066943 | 0.059216 | -0.0037684 | 0.0075153 | -0.0007456 | -0.07782 | 63.0432 | -59.285 | 63.0936 | -59.079 | -59.4543 | -59.4177 | -0.068665 | 63.002 | -59.2026 | 63.1348 | -59.1843 | -59.3033 | -59.1797 | -0.091553 | -0.054932 | -0.004578 | 0.11444 | -0.2243 | -0.26093 | -0.13275 | -0.16937 | -0.009156 | -0.096131 | 0.036621 | 0.009155 | 0.013733 | -0.10986 | 0.022889 | -0.10071 | 0.20599 | 122.3785 | 0.018311 | 122.3373 | 122.3282 | 122.2046 | 122.2366 | 122.1954 | -122.3831 | -122.3007 | 122.287 | 122.3282 | 59.1156 | 59.1248
836.3125 | 122.5296 | -59.2072 | 63.1256 | -0.08873 | 0.0036892 | 0.06423 | 0.06344 | 0.002478 | -0.004029 | -0.00029486 | -0.079346 | 0.0022729 | 0.065448 | 0.057935 | -0.005691 | 0.010933 | -0.0026682 | -0.004578 | 63.0386 | -59.2987 | 63.1256 | -59.0698 | -59.4727 | -59.436 | -0.045776 | 63.0341 | -59.2026 | 63.1165 | -59.2209 | -59.3582 | -59.23 | -0.091553 | -0.086975 | 0 | 0.13733 | -0.22888 | -0.2655 | -0.13733 | -0.17395 | 0.004577 | -0.091552 | -0.009155 | -0.013733 | -0.022889 | -0.15106 | -0.027466 | -0.15564 | 0.22888 | 122.4243 | -0.01831 | 122.319 | 122.3373 | 122.2366 | 122.2458 | 122.2412 | -122.4243 | -122.3282 | 122.3328 | 122.3236 | 59.2026 | 59.1614
837.3125 | 122.6303 | -59.1705 | 63.0753 | -0.081101 | 0.0039028 | 0.064657 | 0.060022 | -0.002649 | -0.0031744 | -0.00072206 | 0.015259 | -7.6854e-05 | 0.06438 | 0.060925 | -0.006759 | 0.0087969 | -0.0018136 | -0.050354 | 63.0203 | -59.2804 | 63.1485 | -59.0378 | -59.5139 | -59.6054 | 0.10529 | 63.002 | -59.2026 | 63.1805 | -59.1797 | -59.2896 | -59.1568 | -0.10986 | -0.054931 | 0.073243 | 0.13275 | -0.43488 | -0.34332 | -0.32501 | -0.23346 | -0.032044 | -0.073242 | 0.10529 | -0.009155 | 0.013733 | -0.11902 | 0.045777 | -0.086975 | 0.24262 | 122.4289 | 0.022889 | 122.3831 | 122.3007 | 122.2046 | 122.1909 | 122.1725 | -122.3557 | -122.2778 | 122.319 | 122.3511 | 59.1202 | 59.2758
838.3125 | 122.525 | -59.2209 | 63.1485 | -0.065842 | 0.0011258 | 0.063803 | 0.061944 | 0.0011962 | -0.0027472 | -0.00029486 | -0.076294 | 0.0022729 | 0.065875 | 0.063916 | -0.0065454 | 0.0083697 | -0.0007456 | -0.10986 | 63.0524 | -59.3079 | 63.0295 | -59.1843 | -59.5642 | -59.5184 | -0.21973 | 63.0157 | -59.2529 | 62.9791 | -59.6329 | -59.1934 | -59.024 | -0.086975 | -0.096131 | -0.11902 | 0.036621 | -0.29755 | -0.34332 | -0.21057 | -0.25635 | -0.032044 | -0.13275 | -0.16937 | -0.41199 | 0.19684 | 0.027466 | 0.22888 | 0.05951 | 0.1236 | 122.3373 | -0.37994 | 122.2321 | 122.3602 | 122.2687 | 122.2733 | 122.2366 | -122.4564 | -122.4014 | 122.2504 | 122.2 | 59.111 | 59.0012
839.3125 | 122.5067 | -59.2255 | 63.1119 | -0.096359 | 0.0034756 | 0.064016 | 0.060022 | 0.0014098 | -0.0044562 | -0.0015765 | -0.073242 | 0.0018457 | 0.066089 | 0.060284 | -0.003982 | 0.0079425 | -0.0030954 | -0.14648 | 63.0432 | -59.3262 | 63.0295 | -59.1843 | -59.5551 | -59.523 | -0.19226 | 63.002 | -59.2346 | 63.0661 | -59.3033 | -59.4269 | -59.285 | -0.10071 | -0.068664 | -0.082397 | 0.041199 | -0.29755 | -0.32959 | -0.19684 | -0.22888 | -0.009155 | -0.10986 | -0.045776 | -0.07782 | -0.059509 | -0.20142 | -0.050354 | -0.19226 | 0.14191 | 122.3557 | -0.068665 | 122.3007 | 122.3694 | 122.2366 | 122.2687 | 122.2275 | -122.438 | -122.3465 | 122.2549 | 122.2916 | 59.079 | 59.0332
840.3125 | 122.612 | -59.1522 | 63.0936 | -0.073471 | 0.0024076 | 0.062521 | 0.057672 | -0.0022218 | 0.00088444 | -0.0043537 | 0.070191 | 0.0018457 | 0.065234 | 0.057935 | -0.00505 | 0.0092241 | -0.0003182 | -0.032043 | 63.0386 | -59.2529 | 63.1714 | -58.9783 | -59.3719 | -59.3536 | 0.050354 | 62.9791 | -59.2026 | 63.2217 | -59.0881 | -59.198 | -59.1202 | -0.10071 | -0.054932 | 0.07782 | 0.17395 | -0.20142 | -0.21973 | -0.10071 | -0.11902 | -0.050354 | -0.11444 | 0.12817 | 0.064087 | 0.032044 | -0.045776 | 0.082398 | 0.004578 | 0.27466 | 122.4243 | 0.11444 | 122.4243 | 122.2916 | 122.1817 | 122.1909 | 122.1313 | -122.3465 | -122.2961 | 122.3236 | 122.374 | 59.1202 | 59.2026
841.3125 | 122.4747 | -59.2438 | 63.1348 | -0.035324 | 0.0036892 | 0.06423 | 0.061944 | -8.538e-05 | -0.0029608 | -0.00029486 | -0.082397 | 0.0035547 | 0.06737 | 0.063275 | -0.0052638 | 0.01072 | -0.0030954 | -0.10529 | 63.0615 | -59.317 | 63.0524 | -59.1705 | -59.5551 | -59.5093 | -0.17853 | 63.002 | -59.2209 | 63.0478 | -59.317 | -59.4589 | -59.285 | -0.073243 | -0.073243 | -0.082398 | 0.073242 | -0.2655 | -0.31128 | -0.19226 | -0.23804 | 0.022888 | -0.13275 | -0.086975 | -0.073243 | -0.041199 | -0.21515 | -0.064087 | -0.23804 | 0.14648 | 122.3694 | -0.096131 | 122.2687 | 122.3785 | 122.2229 | 122.3053 | 122.2458 | -122.4518 | -122.3557 | 122.2961 | 122.2916 | 59.1385 | 59.0652
842.3125 | 122.5571 | -59.2117 | 63.0798 | -0.11925 | 0.0011258 | 0.065085 | 0.058526 | -0.0013672 | -0.0018928 | -0.00072206 | 0.030518 | 0.0022729 | 0.064166 | 0.063916 | -0.0063318 | 0.011147 | 0.001177 | -0.073242 | 62.9791 | -59.2804 | 63.1256 | -59.0286 | -59.4543 | -59.404 | -0.059509 | 62.9517 | -59.2026 | 63.1485 | -59.198 | -59.317 | -59.1843 | -0.068665 | -0.10071 | 0.045776 | 0.18311 | -0.19226 | -0.24262 | -0.1236 | -0.17395 | 0.009155 | -0.12817 | 0.068665 | 0.013733 | 0.027466 | -0.10529 | 0.018311 | -0.11444 | 0.25177 | 122.406 | 0.004578 | 122.3511 | 122.2595 | 122.1542 | 122.1909 | 122.1634 | -122.3602 | -122.2824 | 122.3373 | 122.3602 | 59.1385 | 59.1522
843.3125 | 122.525 | -59.2163 | 63.1393 | -0.050583 | 0.0013394 | 0.064871 | 0.060876 | -0.00029898 | -0.0016792 | -0.0020039 | -0.07019 | 0.0018457 | 0.06502 | 0.063489 | -0.0065454 | 0.0081561 | -0.0022408 | -0.027466 | 63.0615 | -59.3124 | 63.1027 | -59.0698 | -59.4818 | -59.4543 | -0.059509 | 63.0478 | -59.2209 | 63.1165 | -59.2346 | -59.3994 | -59.23 | -0.09613 | -0.07782 | -0.036621 | 0.14649 | -0.23804 | -0.2655 | -0.14191 | -0.16937 | -0.004577 | -0.091552 | -0.022888 | -0.01831 | -0.013733 | -0.1831 | -0.009156 | -0.17853 | 0.24262 | 122.4152 | -0.013733 | 122.3373 | 122.374 | 122.2687 | 122.2778 | 122.2641 | -122.4518 | -122.3602 | 122.319 | 122.3328 | 59.1888 | 59.1568
844.3125 | 122.5525 | -59.2026 | 63.0936 | -0.096359 | 0.003262 | 0.062094 | 0.06344 | 0.00098262 | -0.0038154 | -0.00029486 | -0.042725 | 0.0041955 | 0.065661 | 0.066266 | -0.0048364 | 0.011361 | -0.0018136 | -0.11902 | 63.0432 | -59.317 | 63.0478 | -59.1385 | -59.5276 | -59.4955 | -0.15564 | 63.0066 | -59.2438 | 63.1027 | -59.2529 | -59.3765 | -59.2392 | -0.11444 | -0.050354 | -0.045776 | 0.064087 | -0.29297 | -0.32501 | -0.17853 | -0.21057 | -0.041198 | -0.086975 | 0.009155 | -0.050354 | -0.036621 | -0.17395 | 0.004577 | -0.13275 | 0.17853 | 122.3648 | -0.009156 | 122.3465 | 122.3602 | 122.2504 | 122.2458 | 122.2092 | -122.4106 | -122.3373 | 122.2504 | 122.3053 | 59.0836 | 59.0469
845.3125 | 122.5479 | -59.2209 | 63.0936 | -0.11162 | 0.0034756 | 0.064657 | 0.061303 | -0.0030762 | -0.003388 | -0.0032855 | -0.042725 | 0.0024865 | 0.066943 | 0.060071 | -0.0061182 | 0.0083697 | -0.0043772 | -0.12817 | 63.0295 | -59.3399 | 63.0478 | -59.1339 | -59.5184 | -59.5001 | -0.17853 | 62.9929 | -59.2438 | 63.1119 | -59.2621 | -59.3811 | -59.2392 | -0.11902 | -0.064087 | -0.045776 | 0.086975 | -0.27924 | -0.29755 | -0.16022 | -0.17853 | -0.022888 | -0.10071 | 0.01831 | -0.041199 | -0.018311 | -0.16022 | 0.004577 | -0.13733 | 0.20599 | 122.3877 | -0.018311 | 122.3557 | 122.3694 | 122.2366 | 122.2504 | 122.2137 | -122.4335 | -122.3373 | 122.2687 | 122.3328 | 59.0927 | 59.0424
846.3125 | 122.4838 | -59.2346 | 63.1348 | -0.44731 | 0.0051846 | 0.064657 | 0.060022 | -0.0041444 | -0.003388 | -0.0013629 | -0.042725 | 0.0029137 | 0.068225 | 0.062421 | -0.0046228 | 0.0092241 | 0.001818 | -0.20142 | 62.9608 | -59.3445 | 63.0249 | -59.198 | -59.5184 | -59.5093 | -0.20142 | 63.0157 | -59.2209 | 63.0707 | -59.3033 | -59.4406 | -59.2621 | -0.10986 | -0.17395 | -0.10986 | 0.036621 | -0.27466 | -0.28381 | -0.16479 | -0.17395 | 0.013733 | -0.11902 | -0.064087 | -0.068665 | -0.027466 | -0.20599 | -0.041199 | -0.21973 | 0.14648 | 122.3694 | -0.082398 | 122.2916 | 122.3053 | 122.2366 | 122.1954 | 122.2504 | -122.4792 | -122.3557 | 122.2595 | 122.3053 | 59.0332 | 59.0332
847.3125 | 122.5845 | -59.1751 | 63.0981 | -0.081101 | 0.0017666 | 0.062735 | 0.05874 | 0.0026916 | -0.0025336 | -0.0013629 | 0.042725 | 0.0024865 | 0.065234 | 0.056866 | -0.0063318 | 0.0075153 | -0.0026682 | -0.07782 | 63.0066 | -59.2575 | 63.1439 | -59.0195 | -59.4269 | -59.3857 | -0.041199 | 62.97 | -59.2209 | 63.1348 | -59.1888 | -59.3079 | -59.1888 | -0.082397 | -0.091553 | 0.045776 | 0.15564 | -0.21057 | -0.25177 | -0.12817 | -0.16937 | -0.045776 | -0.12817 | 0.036621 | -0.013733 | -0.013733 | -0.13275 | 0.032043 | -0.086975 | 0.23804 | 122.4014 | 0.032043 | 122.3557 | 122.2641 | 122.1909 | 122.1817 | 122.1451 | -122.3557 | -122.319 | 122.319 | 122.3099 | 59.0973 | 59.1339
848.3125 | 122.5067 | -59.2346 | 63.1302 | -0.08873 | -0.0010104 | 0.066153 | 0.060022 | 0.00034182 | -0.0036018 | -0.00093566 | -0.07019 | 0.00035035 | 0.066516 | 0.061993 | -0.0059046 | 0.010079 | -0.0060862 | -0.40283 | 62.9837 | -59.3536 | 63.0798 | -59.1705 | -59.5917 | -59.5093 | -0.19226 | 63.0157 | -59.2346 | 63.0615 | -59.3033 | -59.4269 | -59.2758 | -0.11902 | -0.14648 | -0.050354 | 0.064087 | -0.27466 | -0.35706 | -0.15564 | -0.23804 | 0 | -0.11444 | -0.068665 | -0.068665 | -0.041199 | -0.19226 | -0.041199 | -0.19226 | 0.18311 | 122.4335 | -0.068665 | 122.2961 | 122.3373 | 122.2504 | 122.2183 | 122.2504 | -122.4838 | -122.3648 | 122.3145 | 122.2961 | 58.8318 | 59.0424
849.3125 | 122.493 | -59.2255 | 63.1393 | -0.058212 | 0.0053982 | 0.065512 | 0.060663 | 0.0011962 | -0.0031744 | -0.00072206 | -0.067139 | 0.00099115 | 0.066089 | 0.060925 | -0.006759 | 0.011147 | -0.0013864 | -0.39825 | 62.97 | -59.3765 | 63.1073 | -59.1614 | -59.6283 | -59.5276 | -0.19684 | 63.0249 | -59.2392 | 63.0844 | -59.3033 | -59.4131 | -59.2667 | -0.15106 | -0.16937 | -0.032043 | 0.064087 | -0.30212 | -0.40283 | -0.15106 | -0.25177 | -0.013733 | -0.11444 | -0.054931 | -0.07782 | -0.041199 | -0.18768 | -0.027466 | -0.17395 | 0.21515 | 122.4838 | -0.064087 | 122.3236 | 122.3465 | 122.2641 | 122.1954 | 122.2504 | -122.5159 | -122.3785 | 122.3328 | 122.3099 | 58.8272 | 59.0286
850.3125 | 122.4976 | -59.2529 | 63.121 | -0.065842 | 0.004971 | 0.069143 | 0.058954 | 0.0014098 | -0.0029608 | -0.0020039 | -0.045776 | 0.0056909 | 0.065875 | 0.063702 | -0.005691 | 0.0092241 | -0.0020272 | -0.32959 | 62.9837 | -59.3719 | 63.0615 | -59.111 | -59.6191 | -59.5367 | -0.20142 | 63.0066 | -59.2484 | 63.0798 | -59.2987 | -59.4223 | -59.2712 | -0.11902 | -0.13733 | -0.05951 | 0.14191 | -0.28381 | -0.36621 | -0.16479 | -0.24719 | 0.004578 | -0.11444 | -0.041199 | -0.045776 | -0.01831 | -0.16937 | -0.022888 | -0.17395 | 0.26093 | 122.4335 | -0.050354 | 122.3282 | 122.3557 | 122.2549 | 122.2366 | 122.2595 | -122.493 | -122.3694 | 122.3145 | 122.3328 | 58.9233 | 59.0515
851.3125 | 122.5388 | -59.2117 | 63.1119 | -0.11925 | 0.0041166 | 0.063803 | 0.061731 | 0.00076902 | -0.0031744 | -0.00072206 | -0.036621 | 0.0027001 | 0.067798 | 0.063489 | -0.0063318 | 0.0083697 | 0.0005362 | -0.1236 | 63.0432 | -59.3308 | 63.0386 | -59.1431 | -59.5184 | -59.4864 | -0.17395 | 63.002 | -59.2438 | 63.1073 | -59.2529 | -59.3765 | -59.23 | -0.11902 | -0.068664 | -0.073242 | 0.068665 | -0.27466 | -0.3067 | -0.15564 | -0.18768 | -0.032043 | -0.10986 | -0.004577 | -0.041199 | -0.018311 | -0.16479 | 0.013732 | -0.13275 | 0.18768 | 122.3694 | -0.009156 | 122.3511 | 122.374 | 122.2458 | 122.2549 | 122.2137 | -122.4426 | -122.3557 | 122.2504 | 122.319 | 59.0881 | 59.0378
852.3125 | 122.5891 | -59.1797 | 63.1073 | -0.12688 | 0.0024076 | 0.063589 | 0.055963 | -0.002008 | -0.0014654 | -0.0032855 | 0.061035 | 0.00077755 | 0.066302 | 0.064343 | -0.00505 | 0.0092241 | -0.0009592 | -0.091553 | 63.0386 | -59.2896 | 63.0936 | -59.0607 | -59.4452 | -59.3994 | -0.068665 | 62.9883 | -59.198 | 63.1531 | -59.1797 | -59.2667 | -59.1751 | -0.10986 | -0.068665 | -0.013733 | 0.11902 | -0.21973 | -0.2655 | -0.10986 | -0.15564 | -0.018311 | -0.11902 | 0.045776 | 0 | 0.004577 | -0.086976 | 0.022888 | -0.068665 | 0.22888 | 122.3831 | 0.018311 | 122.3511 | 122.3282 | 122.1863 | 122.2183 | 122.168 | -122.3969 | -122.3053 | 122.2733 | 122.3328 | 59.0881 | 59.111
853.3125 | 122.5571 | -59.23 | 63.121 | -0.0048066 | 0.0009122 | 0.064016 | 0.060663 | -0.00051278 | -0.0042426 | -0.0024311 | -0.057983 | 0.0046227 | 0.066302 | 0.065625 | -0.0071864 | 0.010079 | 0.000109 | -0.11902 | 63.0478 | -59.3308 | 63.0386 | -59.1476 | -59.5459 | -59.4818 | -0.16479 | 62.9883 | -59.2346 | 63.0936 | -59.2712 | -59.3994 | -59.2163 | -0.10071 | -0.073242 | -0.082398 | 0.082398 | -0.25177 | -0.31586 | -0.15106 | -0.21515 | -0.004577 | -0.13275 | -0.027466 | -0.041198 | 0.013733 | -0.16937 | 0.01831 | -0.16479 | 0.18311 | 122.3694 | -0.036621 | 122.3282 | 122.3785 | 122.2229 | 122.2778 | 122.2183 | -122.4518 | -122.3557 | 122.2687 | 122.3236 | 59.111 | 59.0652
854.3125 | 122.6028 | -59.1934 | 63.0798 | -0.065842 | 0.0026212 | 0.062735 | 0.059167 | 0.0029052 | -0.0036018 | -0.0022175 | -0.039673 | 0.0018457 | 0.066943 | 0.060284 | -0.0063318 | 0.010292 | -0.0016 | -0.11444 | 63.0203 | -59.2987 | 63.1073 | -59.0927 | -59.4543 | -59.4315 | -0.09613 | 62.9837 | -59.2117 | 63.1622 | -59.1934 | -59.3033 | -59.1568 | -0.10529 | -0.059509 | 0.027466 | 0.10071 | -0.23804 | -0.26093 | -0.13275 | -0.15564 | -0.018311 | -0.09613 | 0.082397 | 0 | 0.036621 | -0.10986 | 0.054932 | -0.091553 | 0.20599 | 122.406 | 0.018311 | 122.374 | 122.319 | 122.1954 | 122.2137 | 122.1771 | -122.3785 | -122.2916 | 122.3007 | 122.3557 | 59.079 | 59.0973
855.3125 | 122.612 | -59.166 | 63.0798 | -0.096359 | 0.0024076 | 0.064444 | 0.062158 | -8.538e-05 | -0.0018928 | 0.00034614 | -0.039673 | 0.0018457 | 0.06502 | 0.054303 | -0.0071864 | 0.0092241 | -0.0007456 | -0.10071 | 63.0066 | -59.3308 | 63.089 | -59.0836 | -59.4727 | -59.4452 | -0.082397 | 62.97 | -59.2255 | 63.1714 | -59.1888 | -59.3079 | -59.166 | -0.1648 | -0.073242 | 0.009155 | 0.082398 | -0.27923 | -0.3067 | -0.11444 | -0.14191 | -0.059509 | -0.10986 | 0.091553 | -0.022888 | 0 | -0.14191 | 0.059509 | -0.082397 | 0.24719 | 122.4197 | 0.036621 | 122.3969 | 122.3373 | 122.1954 | 122.1725 | 122.1359 | -122.4106 | -122.3053 | 122.2549 | 122.3373 | 59.0652 | 59.0836
856.3125 | 122.4884 | -59.23 | 63.1439 | 0.010452 | 0.0039028 | 0.064444 | 0.062799 | 0.0011962 | -0.0046698 | -0.0013629 | -0.25024 | 0.0039819 | 0.06502 | 0.057294 | -0.0071864 | 0.010506 | -0.0024546 | -0.12817 | 63.0386 | -59.317 | 63.0112 | -59.2117 | -59.5688 | -59.5322 | 0.018311 | 63.002 | -59.2072 | 63.0615 | -59.2941 | -59.3903 | -59.23 | -0.086975 | -0.10529 | -0.13275 | 0.018311 | -0.30212 | -0.33875 | -0.21515 | -0.25177 | 0.022889 | -0.14191 | -0.082398 | -0.064086 | 0 | -0.16022 | -0.022889 | -0.18311 | 0.10529 | 122.3282 | -0.086975 | 122.2687 | 122.3557 | 122.2092 | 122.2687 | 122.2321 | -122.4609 | -122.3511 | 122.2412 | 122.2916 | 59.1019 | 59.2484
857.3125 | 122.5525 | -59.1934 | 63.0569 | -0.035324 | 0.0028348 | 0.063803 | 0.056177 | 0.00076902 | -0.0053108 | -0.0069171 | 0.018311 | 0.0018457 | 0.066089 | 0.05003 | -0.0041956 | 0.0083697 | -0.000532 | -0.10071 | 63.002 | -59.285 | 63.121 | -59.0698 | -59.4681 | -59.3994 | -0.09613 | 62.9745 | -59.2117 | 63.1393 | -59.2072 | -59.317 | -59.1888 | -0.091553 | -0.054932 | 0.064087 | 0.1236 | -0.20599 | -0.27466 | -0.11444 | -0.18311 | -0.018311 | -0.082398 | 0.082397 | -0.013733 | 0.004577 | -0.1236 | 0.022888 | -0.10529 | 0.21515 | 122.406 | 0.004578 | 122.3511 | 122.287 | 122.1863 | 122.1954 | 122.168 | -122.3419 | -122.2687 | 122.3145 | 122.3328 | 59.0927 | 59.0973
858.3125 | 122.5891 | -59.1888 | 63.0615 | -0.058212 | 0.0026212 | 0.063376 | 0.060876 | 0.0011962 | -0.0042426 | 0.00055974 | -0.021362 | 0.0018457 | 0.065875 | 0.062848 | -0.0061182 | 0.011361 | -0.000532 | -0.1236 | 63.0295 | -59.3399 | 63.0524 | -59.1064 | -59.5139 | -59.4543 | -0.12817 | 62.9745 | -59.2117 | 63.1622 | -59.2072 | -59.3308 | -59.1751 | -0.15106 | -0.032043 | -0.009155 | 0.082398 | -0.2655 | -0.32501 | -0.11444 | -0.17395 | -0.022888 | -0.086975 | 0.10071 | -0.01831 | 0.013733 | -0.14191 | 0.036621 | -0.11902 | 0.23346 | 122.3923 | 0.004578 | 122.374 | 122.3694 | 122.1863 | 122.2183 | 122.1634 | -122.4014 | -122.2733 | 122.2412 | 122.3511 | 59.0652 | 59.0607
859.3125 | 122.6303 | -59.1843 | 63.0478 | -0.11925 | 0.0028348 | 0.065298 | 0.059808 | 0.0020508 | -0.0012518 | -0.0017903 | -0.12207 | -0.00093145 | 0.064166 | 0.05943 | -0.0069726 | 0.010292 | -0.0048044 | -0.068665 | 62.9745 | -59.2804 | 63.1439 | -59.0149 | -59.4086 | -59.3948 | 0.073242 | 62.9333 | -59.1888 | 63.1851 | -59.1614 | -59.2575 | -59.1156 | -0.096131 | -0.073243 | 0.09613 | 0.16937 | -0.21057 | -0.2243 | -0.11444 | -0.12817 | -0.004578 | -0.11444 | 0.13733 | 0.022888 | 0.068664 | -0.073242 | 0.073242 | -0.068664 | 0.2655 | 122.4243 | 0.027466 | 122.374 | 122.2549 | 122.1222 | 122.1588 | 122.1176 | -122.3282 | -122.2366 | 122.3282 | 122.3694 | 59.1156 | 59.2575
860.3125 | 122.6395 | -59.1843 | 63.0615 | -0.12688 | 0.0026212 | 0.064657 | 0.058526 | -0.00051278 | -0.0036018 | 0.00098694 | -0.14648 | 0.00035035 | 0.066089 | 0.062421 | -0.0059046 | 0.010506 | -0.0020272 | -0.073242 | 62.9791 | -59.3033 | 63.1439 | -59.0286 | -59.4131 | -59.3857 | 0 | 62.9196 | -59.198 | 63.1989 | -59.1614 | -59.2392 | -59.1019 | -0.11902 | -0.082397 | 0.082398 | 0.15564 | -0.20142 | -0.22888 | -0.082397 | -0.10986 | -0.013733 | -0.14191 | 0.13733 | 0.022888 | 0.082397 | -0.054932 | 0.09613 | -0.041199 | 0.27466 | 122.4472 | 0.036621 | 122.3969 | 122.2824 | 122.1176 | 122.1634 | 122.1039 | -122.3648 | -122.2595 | 122.3282 | 122.3831 | 59.111 | 59.1843
861.3125 | 122.5845 | -59.198 | 63.121 | -0.096359 | 0.0006986 | 0.064871 | 0.063012 | -8.538e-05 | -0.00232 | -0.0013629 | -0.064087 | 0.0035547 | 0.066302 | 0.058362 | -0.0065454 | 0.0094379 | -0.0013864 | -0.12817 | 63.0157 | -59.3124 | 63.0753 | -59.111 | -59.5139 | -59.4589 | -0.14648 | 62.9791 | -59.2117 | 63.1439 | -59.2026 | -59.3308 | -59.1888 | -0.11444 | -0.10529 | -0.045777 | 0.086975 | -0.26093 | -0.31586 | -0.14648 | -0.20142 | -0.013733 | -0.14191 | 0.022888 | -0.004578 | 0.009155 | -0.13275 | 0.022888 | -0.11902 | 0.20142 | 122.3877 | 0.009155 | 122.3557 | 122.3282 | 122.1909 | 122.2137 | 122.1771 | -122.4335 | -122.3328 | 122.2733 | 122.3419 | 59.0698 | 59.0515
862.3125 | 122.612 | -59.1568 | 63.0936 | -0.042954 | 0.0013394 | 0.061239 | 0.057672 | 0.00055542 | -0.0029608 | -0.0039265 | 0.067139 | -0.00029045 | 0.06737 | 0.05708 | -0.0041956 | 0.0075153 | -0.006727 | -0.064087 | 63.0341 | -59.285 | 63.1302 | -59.0378 | -59.4086 | -59.3765 | -0.045776 | 63.0112 | -59.198 | 63.176 | -59.1522 | -59.2758 | -59.1522 | -0.12817 | -0.059509 | 0.036621 | 0.11902 | -0.21973 | -0.25177 | -0.091553 | -0.1236 | -0.041199 | -0.082398 | 0.082397 | 0.004577 | 0.004577 | -0.11902 | 0.045776 | -0.07782 | 0.24719 | 122.4152 | 0.045776 | 122.374 | 122.319 | 122.2092 | 122.1909 | 122.168 | -122.3785 | -122.2916 | 122.287 | 122.3328 | 59.0927 | 59.111
863.3125 | 122.5159 | -59.2255 | 63.1165 | -0.08873 | 0.0030484 | 0.063162 | 0.06109 | 0.0048278 | -0.00061096 | -0.0026447 | -0.067139 | 0.0012047 | 0.066516 | 0.059003 | -0.0063318 | 0.0083697 | -0.0030954 | -0.11902 | 63.0249 | -59.3124 | 63.0341 | -59.1614 | -59.5322 | -59.491 | -0.17853 | 63.0295 | -59.2255 | 63.089 | -59.2758 | -59.4406 | -59.2438 | -0.086975 | -0.091553 | -0.082397 | 0.064087 | -0.2655 | -0.3067 | -0.17853 | -0.21973 | 0 | -0.086975 | -0.027466 | -0.050354 | -0.01831 | -0.21515 | -0.01831 | -0.21515 | 0.15106 | 122.3465 | -0.050354 | 122.3145 | 122.3373 | 122.2549 | 122.2504 | 122.2549 | -122.4289 | -122.3419 | 122.2595 | 122.3145 | 59.1064 | 59.0469
864.3125 | 122.6349 | -59.1522 | 63.0798 | -0.035324 | 0.0036892 | 0.065085 | 0.058954 | 0.00076902 | -0.0025336 | -0.0015765 | 0.024414 | -0.0011451 | 0.065661 | 0.056866 | -0.0054774 | 0.010506 | 0.000109 | -0.050354 | 62.9929 | -59.285 | 63.1577 | -59.0103 | -59.6191 | -59.5963 | 0.045776 | 63.0203 | -59.1751 | 63.1897 | -59.166 | -59.2804 | -59.1522 | -0.13275 | -0.086975 | 0.07782 | 0.14191 | -0.44403 | -0.46692 | -0.31128 | -0.33417 | -0.022888 | -0.059509 | 0.10986 | -0.013733 | 0 | -0.12817 | 0.022888 | -0.10529 | 0.27466 | 122.4426 | 0.009155 | 122.3648 | 122.2778 | 122.1954 | 122.1451 | 122.1725 | -122.3648 | -122.2549 | 122.3099 | 122.3419 | 59.1019 | 59.198
865.3125 | 122.5845 | -59.198 | 63.0524 | -0.11162 | 0.0028348 | 0.063376 | 0.05874 | 0.00034182 | -0.0029608 | -0.0013629 | -0.0091553 | 0.0033411 | 0.063952 | 0.060712 | -0.0046228 | 0.0079425 | -0.0039498 | -0.07782 | 63.002 | -59.2758 | 63.1485 | -59.0057 | -59.4269 | -59.3719 | -0.036621 | 62.9654 | -59.1751 | 63.1714 | -59.1751 | -59.2896 | -59.1476 | -0.07782 | -0.050354 | 0.096131 | 0.19226 | -0.17395 | -0.22888 | -0.09613 | -0.15106 | 0.022888 | -0.086975 | 0.11902 | 0.022888 | 0.050354 | -0.091553 | 0.027466 | -0.11444 | 0.27008 | 122.4243 | 0 | 122.3465 | 122.2778 | 122.1405 | 122.2 | 122.1634 | -122.3282 | -122.2275 | 122.3465 | 122.3694 | 59.1202 | 59.1614
866.3125 | 122.6074 | -59.1934 | 63.089 | -0.11925 | 0.0024076 | 0.062948 | 0.060449 | -0.00093998 | -0.00018376 | -0.0028583 | -0.07019 | 0.0020593 | 0.06737 | 0.063489 | -0.006759 | 0.0077289 | -0.0048044 | -0.059509 | 62.9791 | -59.285 | 63.0112 | -58.9279 | -59.1156 | -59.2987 | -0.013733 | 62.9791 | -59.166 | 63.1897 | -59.1431 | -59.285 | -59.1614 | -0.091553 | -0.10986 | -0.07782 | 0.2655 | -0.10529 | 0.077819 | -0.013733 | 0.16937 | 0.027465 | -0.10986 | 0.10071 | 0.050354 | 0.032043 | -0.091553 | 0.004578 | -0.11902 | 0.35706 | 122.2961 | 0.022889 | 122.3557 | 122.2641 | 122.1451 | 122.1725 | 122.1725 | -122.374 | -122.2549 | 122.2046 | 122.3831 | 59.1339 | 59.1797
867.3125 | 122.644 | -59.1248 | 63.1256 | -0.020065 | 0.0041166 | 0.062735 | 0.058526 | 0.00055542 | -0.0010382 | -0.0017903 | 0.036621 | 0.0020593 | 0.066302 | 0.060498 | -0.0059046 | 0.0096515 | -0.0018136 | -0.009155 | 63.0386 | -59.2712 | 63.1989 | -58.9554 | -59.3353 | -59.317 | 0.091553 | 62.9974 | -59.1522 | 63.2446 | -59.1797 | -58.8089 | -58.8455 | -0.14648 | -0.086975 | 0.073243 | 0.16937 | -0.19226 | -0.21057 | -0.045777 | -0.064087 | -0.027466 | -0.12817 | 0.11902 | -0.054931 | 0.27924 | 0.31586 | 0.3067 | 0.34332 | 0.31586 | 122.4701 | -0.027465 | 122.3969 | 122.3099 | 122.1497 | 122.1634 | 122.1222 | -122.3969 | -122.2778 | 122.3236 | 122.3694 | 59.1156 | 59.2163
868.3125 | 122.6257 | -59.1888 | 63.0798 | -0.096359 | 0.0045438 | 0.063162 | 0.059808 | -0.0013672 | -0.00039736 | -0.0011493 | -0.045776 | -7.6854e-05 | 0.066516 | 0.067975 | -0.0048364 | 0.0077289 | -0.0058724 | -0.045776 | 62.9883 | -59.2804 | 63.1714 | -59.0973 | -59.4223 | -59.3674 | -0.032043 | 62.9654 | -59.2026 | 63.1851 | -59.1568 | -59.2575 | -59.1293 | -0.091553 | -0.091553 | 0.091553 | 0.091553 | -0.17853 | -0.23346 | -0.086975 | -0.14191 | -0.013733 | -0.11444 | 0.10529 | 0.032044 | 0.05951 | -0.068664 | 0.073243 | -0.054931 | 0.18311 | 122.4518 | 0.045777 | 122.3877 | 122.2687 | 122.168 | 122.1771 | 122.1542 | -122.3602 | -122.2824 | 122.3602 | 122.374 | 59.1431 | 59.1568
869.3125 | 122.5616 | -59.1751 | 63.089 | -0.050583 | 0.0043302 | 0.062735 | 0.059808 | -0.0017944 | -0.00232 | -0.0032855 | 0.012207 | -7.6854e-05 | 0.066302 | 0.05708 | -0.005691 | 0.0092241 | -0.0026682 | -0.073242 | 63.002 | -59.2804 | 63.1485 | -59.024 | -59.4269 | -59.3765 | -0.054932 | 62.9654 | -59.1934 | 63.1668 | -59.198 | -59.2987 | -59.1705 | -0.10529 | -0.086975 | 0.05951 | 0.15106 | -0.20142 | -0.25177 | -0.09613 | -0.14648 | -0.01831 | -0.1236 | 0.07782 | -0.022888 | 0.004578 | -0.1236 | 0.022888 | -0.10529 | 0.25635 | 122.4289 | -0.004578 | 122.3602 | 122.2824 | 122.1588 | 122.1771 | 122.1405 | -122.3694 | -122.2824 | 122.3236 | 122.3419 | 59.1019 | 59.1202
870.3125 | 122.6166 | -59.1797 | 63.0844 | -0.058212 | 0.0024076 | 0.065298 | 0.05874 | -0.005426 | -0.0012518 | 0.00013254 | -0.021362 | 0.0012047 | 0.065661 | 0.062421 | -0.0061182 | 0.0090105 | -0.0026682 | -0.064087 | 62.97 | -59.3262 | 63.1302 | -58.9737 | -59.4406 | -59.4177 | -0.036621 | 62.9654 | -59.1934 | 63.1989 | -59.1522 | -59.2758 | -59.1522 | -0.14648 | -0.11444 | 0.045776 | 0.20599 | -0.23804 | -0.26093 | -0.091553 | -0.11444 | -0.013733 | -0.11902 | 0.11444 | 0.027465 | 0.027465 | -0.096131 | 0.041198 | -0.082398 | 0.35248 | 122.4564 | 0.041198 | 122.3923 | 122.2961 | 122.1588 | 122.1497 | 122.1451 | -122.4106 | -122.2778 | 122.3099 | 122.3785 | 59.1156 | 59.1431
871.3125 | 122.5525 | -59.1888 | 63.0844 | -0.10399 | 0.0051846 | 0.063376 | 0.059381 | 0.0022644 | -0.004029 | -0.0020039 | -0.024414 | 0.0022729 | 0.066516 | 0.060498 | -0.0054774 | 0.010079 | -0.0013864 | -0.064087 | 63.0066 | -59.2758 | 63.1439 | -59.0149 | -59.4223 | -59.3765 | -0.059509 | 62.9562 | -59.2163 | 63.1714 | -59.1751 | -59.2941 | -59.1705 | -0.086975 | -0.07782 | 0.059509 | 0.17395 | -0.18768 | -0.23346 | -0.10071 | -0.14648 | -0.027466 | -0.12817 | 0.086975 | 0.013733 | 0.018311 | -0.10529 | 0.045777 | -0.077819 | 0.26093 | 122.4197 | 0.041199 | 122.3877 | 122.2824 | 122.1725 | 122.1954 | 122.1451 | -122.3602 | -122.3007 | 122.3328 | 122.3602 | 59.1248 | 59.1293
872.3125 | 122.6257 | -59.1476 | 63.1302 | -0.050583 | 0.0019802 | 0.064871 | 0.057245 | -0.0028626 | -0.0038154 | -0.0017903 | 0.018311 | 0.0024865 | 0.063525 | 0.060712 | -0.006759 | 0.01072 | -0.0037362 | 0.032043 | 63.0386 | -59.2484 | 63.1989 | -58.9462 | -59.3536 | -59.3216 | 0.073242 | 63.0203 | -59.1614 | 63.2034 | -59.1248 | -59.2392 | -59.1385 | -0.10071 | -0.091553 | 0.068665 | 0.20142 | -0.17395 | -0.20599 | -0.073242 | -0.10529 | -0.013733 | -0.10986 | 0.073242 | 0.022888 | 0.009155 | -0.091553 | 0.022888 | -0.07782 | 0.30212 | 122.4472 | 0.036621 | 122.3648 | 122.287 | 122.1817 | 122.1863 | 122.168 | -122.3785 | -122.2916 | 122.3465 | 122.3511 | 59.1797 | 59.2209
873.3125 | 122.5708 | -59.1522 | 63.1027 | -0.058212 | 0.0030484 | 0.062948 | 0.059381 | -0.00072638 | -0.0029608 | -0.0015765 | -0.036621 | 0.0024865 | 0.066302 | 0.058789 | -0.0052638 | 0.0083697 | -0.0013864 | -0.064087 | 62.9837 | -59.2804 | 63.1485 | -59.0195 | -59.4315 | -59.3857 | -0.032043 | 62.97 | -59.2117 | 63.1714 | -59.1888 | -59.317 | -59.1614 | -0.12817 | -0.11902 | 0.045777 | 0.13275 | -0.23346 | -0.27924 | -0.10528 | -0.15106 | -0.059509 | -0.13275 | 0.068665 | -0.036621 | -0.009155 | -0.16479 | 0.050354 | -0.10529 | 0.26093 | 122.4289 | 0.022888 | 122.3831 | 122.2641 | 122.1817 | 122.1359 | 122.1222 | -122.3831 | -122.3145 | 122.3007 | 122.3236 | 59.0881 | 59.1202
874.3125 | 122.644 | -59.1522 | 63.1256 | -0.08873 | 0.0043302 | 0.06188 | 0.059595 | -0.0024354 | -0.0025336 | -0.0015765 | -0.012207 | 0.0020593 | 0.066089 | 0.06178 | -0.0048364 | 0.0083697 | -0.003309 | -0.091553 | 62.9974 | -59.2941 | 63.1119 | -59.0744 | -59.4681 | -59.404 | -0.09613 | 62.97 | -59.2163 | 63.1393 | -59.1888 | -59.2987 | -59.2209 | -0.14191 | -0.12817 | -0.013733 | 0.07782 | -0.25177 | -0.31586 | -0.10986 | -0.17395 | -0.064087 | -0.15564 | 0.013733 | -0.036621 | -0.068664 | -0.14648 | -0.004577 | -0.082397 | 0.21973 | 122.406 | 0.027466 | 122.3557 | 122.2916 | 122.1863 | 122.1497 | 122.1222 | -122.4197 | -122.3419 | 122.2641 | 122.2916 | 59.0607 | 59.0561
875.3125 | 122.5891 | -59.1934 | 63.1531 | -0.058212 | 0.0002714 | 0.064016 | 0.060235 | -0.0013672 | -0.003388 | -0.0067035 | -0.021362 | 0.0024865 | 0.066516 | 0.058575 | -0.0061182 | 0.0098651 | -0.0024546 | -0.10529 | 63.0157 | -59.3033 | 63.1256 | -59.0744 | -59.4543 | -59.4177 | -0.07782 | 62.9883 | -59.2072 | 63.1393 | -59.1934 | -59.2896 | -59.1751 | -0.10986 | -0.13733 | -0.027466 | 0.11902 | -0.2243 | -0.26093 | -0.11444 | -0.15106 | -0.013733 | -0.16479 | -0.013733 | 0 | 0.01831 | -0.096131 | 0.032043 | -0.082398 | 0.22888 | 122.4289 | 0.013733 | 122.3465 | 122.319 | 122.1954 | 122.2092 | 122.1817 | -122.4564 | -122.3602 | 122.319 | 122.3328 | 59.0881 | 59.1156
876.3125 | 122.4976 | -59.1568 | 63.1256 | -0.073471 | 0.0024076 | 0.06423 | 0.060449 | -0.00051278 | -0.0025336 | -0.0013629 | -0.015259 | -7.6854e-05 | 0.063952 | 0.063916 | -0.0063318 | 0.010933 | -0.0018136 | -0.091553 | 63.002 | -59.3079 | 63.1302 | -59.0561 | -59.4635 | -59.4177 | -0.09613 | 62.9883 | -59.23 | 63.1531 | -59.2026 | -59.3033 | -59.1751 | -0.15106 | -0.1236 | 0.004578 | 0.10071 | -0.26093 | -0.3067 | -0.10986 | -0.15564 | -0.073243 | -0.13733 | 0.027466 | -0.045777 | -0.018311 | -0.14648 | 0.054932 | -0.073242 | 0.25177 | 122.438 | 0.027466 | 122.3831 | 122.3099 | 122.2183 | 122.1588 | 122.1451 | -122.4335 | -122.3557 | 122.287 | 122.3099 | 59.0652 | 59.0607
877.3125 | 122.644 | -59.1843 | 63.089 | -0.081101 | 0.0026212 | 0.061453 | 0.057886 | -0.00051278 | -0.0044562 | -0.0022175 | 0.0061035 | 0.0029137 | 0.065875 | 0.062421 | -0.0071864 | 0.0045245 | -0.0026682 | -0.018311 | 63.0432 | -59.2712 | 63.208 | -58.9233 | -59.3216 | -59.3216 | 0.11902 | 62.9974 | -59.1705 | 63.4598 | -59.2667 | -59.5917 | -59.3628 | -0.086975 | -0.045776 | 0.11902 | 0.26093 | -0.13733 | -0.13733 | -0.050354 | -0.050354 | 0.013733 | -0.091552 | 0.37079 | -0.082398 | -0.17853 | -0.40741 | -0.19226 | -0.42114 | 0.3479 | 122.4792 | -0.096131 | 122.6303 | 122.3145 | 122.168 | 122.2275 | 122.1817 | -122.3602 | -122.2595 | 122.3923 | 122.644 | 59.166 | 59.3033
878.3125 | 122.5616 | -59.1843 | 63.1027 | -0.08873 | 0.0011258 | 0.065725 | 0.060876 | -0.003717 | -0.0044562 | -0.0034991 | -0.015259 | 0.0020593 | 0.068225 | 0.062421 | -0.0054774 | 0.010292 | -0.0045908 | -0.09613 | 62.9791 | -59.285 | 63.1256 | -59.0561 | -59.4543 | -59.404 | -0.091553 | 62.9837 | -59.2163 | 63.1577 | -59.1797 | -59.3079 | -59.1751 | -0.10071 | -0.1236 | 0.022888 | 0.12817 | -0.21973 | -0.27008 | -0.11902 | -0.16937 | -0.032044 | -0.11902 | 0.054932 | 0.004578 | 0.009155 | -0.1236 | 0.041199 | -0.091552 | 0.22888 | 122.4106 | 0.036622 | 122.374 | 122.2641 | 122.2 | 122.1634 | 122.168 | -122.3877 | -122.319 | 122.3099 | 122.3419 | 59.0881 | 59.0927
879.3125 | 122.58 | -59.1843 | 63.1348 | -0.035324 | 0.0036892 | 0.063376 | 0.06109 | 0.0037598 | -0.0042426 | -0.0015765 | -0.012207 | 0.0012047 | 0.066089 | 0.06477 | -0.0052638 | 0.01072 | -0.0035226 | -0.022888 | 63.0524 | -59.2712 | 63.0844 | -59.0744 | -59.4223 | -59.4269 | -0.10529 | 62.9837 | -59.1888 | 63.1531 | -59.1751 | -59.3124 | -59.1843 | -0.086975 | -0.082398 | -0.050354 | 0.10986 | -0.24261 | -0.23804 | -0.15564 | -0.15106 | -0.004578 | -0.15106 | 0.01831 | 0.009155 | 0 | -0.12817 | 0.004578 | -0.1236 | 0.19684 | 122.3557 | 0.013733 | 122.3419 | 122.3236 | 122.1725 | 122.2366 | 122.168 | -122.406 | -122.3236 | 122.2687 | 122.3373 | 59.1614 | 59.079
880.3125 | 122.6212 | -59.1797 | 63.0981 | 0.0028229 | 0.0013394 | 0.062735 | 0.057672 | -0.0030762 | -0.0016792 | -0.00072206 | -0.0030517 | 0.0012047 | 0.065448 | 0.058148 | -0.0069726 | 0.0094379 | -0.0011728 | -0.064087 | 63.0112 | -59.285 | 63.1485 | -59.0469 | -59.4086 | -59.3674 | -0.022888 | 62.9883 | -59.2072 | 63.1897 | -59.1476 | -59.2712 | -59.1568 | -0.10529 | -0.086976 | 0.050354 | 0.13275 | -0.18768 | -0.22888 | -0.082398 | -0.1236 | -0.027466 | -0.10986 | 0.091552 | 0.032043 | 0.022888 | -0.091553 | 0.050354 | -0.064087 | 0.23804 | 122.4335 | 0.059509 | 122.3969 | 122.2961 | 122.1954 | 122.1909 | 122.168 | -122.3831 | -122.3053 | 122.3282 | 122.3694 | 59.1156 | 59.1568
881.3125 | 122.5296 | -59.1797 | 63.1027 | -0.065842 | 0.001553 | 0.062735 | 0.06109 | -0.0013672 | -0.0036018 | -0.0017903 | 0.11597 | 0.0024865 | 0.067798 | 0.059216 | -0.005691 | 0.0090105 | -0.0013864 | -0.091553 | 63.0386 | -59.2896 | 63.121 | -59.0744 | -59.4498 | -59.3948 | -0.25177 | 62.9837 | -59.1797 | 63.1622 | -59.2392 | -59.317 | -59.198 | -0.10986 | -0.064087 | 0.018311 | 0.10529 | -0.21515 | -0.27008 | -0.10528 | -0.16022 | 0 | -0.11902 | 0.059509 | -0.05951 | -0.018311 | -0.13733 | -0.018311 | -0.13733 | 0.21515 | 122.4106 | -0.05951 | 122.3419 | 122.3282 | 122.1634 | 122.2183 | 122.1634 | -122.3923 | -122.2824 | 122.3007 | 122.3419 | 59.0881 | 58.9279
882.3125 | 122.5296 | -59.198 | 63.1622 | -0.027695 | 0.0011258 | 0.063803 | 0.060235 | -0.0024354 | -0.0016792 | 0.0029095 | -0.091553 | 0.0014185 | 0.065875 | 0.064343 | -0.0080408 | 0.0077289 | -0.0030954 | -0.022888 | 63.0981 | -59.3033 | 63.0981 | -59.1019 | -59.4452 | -59.4452 | -0.064087 | 63.0661 | -59.1888 | 63.1256 | -59.2255 | -59.3399 | -59.2072 | -0.10529 | -0.064086 | -0.064086 | 0.09613 | -0.24719 | -0.24719 | -0.14191 | -0.14191 | 0.009155 | -0.09613 | -0.036621 | -0.027466 | -0.009155 | -0.14191 | -0.01831 | -0.15106 | 0.20142 | 122.4014 | -0.036621 | 122.3145 | 122.4014 | 122.2549 | 122.2961 | 122.2641 | -122.4655 | -122.3511 | 122.2961 | 122.3236 | 59.1751 | 59.1339
883.3125 | 122.5525 | -59.1934 | 63.0707 | -0.065842 | 0.001553 | 0.064871 | 0.059167 | 0.0031188 | -0.003388 | 0.00034614 | -0.033569 | 0.0024865 | 0.066089 | 0.060712 | -0.0059046 | 0.0096515 | -0.0039498 | -0.068665 | 63.0066 | -59.2667 | 63.1531 | -59.0195 | -59.4223 | -59.3857 | -0.036621 | 62.9745 | -59.2026 | 63.176 | -59.1797 | -59.2987 | -59.1614 | -0.073243 | -0.064087 | 0.082397 | 0.17395 | -0.19226 | -0.22888 | -0.11902 | -0.15564 | -0.009156 | -0.096131 | 0.10529 | 0.013733 | 0.032043 | -0.10529 | 0.041199 | -0.09613 | 0.24719 | 122.4197 | 0.022889 | 122.3785 | 122.2733 | 122.1771 | 122.2 | 122.168 | -122.3373 | -122.2733 | 122.3465 | 122.3694 | 59.1248 | 59.1568
884.3125 | 122.58 | -59.1797 | 63.0798 | -0.081101 | 0.0039028 | 0.06423 | 0.060022 | 0.00034182 | -0.005097 | -0.00093566 | -0.061035 | 0.0018457 | 0.064593 | 0.062634 | -0.0059046 | 0.0096515 | -0.0037362 | -0.064087 | 62.9974 | -59.2804 | 63.1714 | -59.0057 | -59.4223 | -59.3765 | -0.032043 | 62.9745 | -59.2026 | 63.1851 | -59.1522 | -59.2804 | -59.1385 | -0.10071 | -0.082397 | 0.091553 | 0.17395 | -0.19684 | -0.24262 | -0.09613 | -0.14191 | -0.022889 | -0.10529 | 0.10529 | 0.027465 | 0.041198 | -0.10071 | 0.064087 | -0.07782 | 0.27466 | 122.4518 | 0.050354 | 122.3877 | 122.2778 | 122.1771 | 122.1771 | 122.1542 | -122.3602 | -122.2824 | 122.3511 | 122.3648 | 59.1156 | 59.1476
885.3125 | 122.5754 | -59.1797 | 63.0981 | -0.096359 | 0.001553 | 0.061667 | 0.060449 | 0.0033324 | -0.0042426 | -0.00029486 | -0.073242 | 0.0020593 | 0.063952 | 0.05943 | -0.0054774 | 0.0081561 | -0.0035226 | -0.082397 | 63.0295 | -59.2758 | 63.1119 | -59.0881 | -59.1385 | -59.3033 | -0.054932 | 63.0157 | -59.1888 | 63.1302 | -59.1934 | -59.3262 | -59.1934 | -0.096131 | -0.068665 | 0.013732 | 0.091552 | -0.1236 | 0.041198 | -0.027466 | 0.13733 | -0.009156 | -0.082398 | 0.032043 | -0.013733 | -0.013733 | -0.14648 | -0.004577 | -0.13733 | 0.18768 | 122.3877 | -0.004577 | 122.319 | 122.3053 | 122.2046 | 122.2092 | 122.1954 | -122.374 | -122.287 | 122.2916 | 122.3099 | 59.0973 | 59.1248
886.3125 | 122.6028 | -59.1751 | 63.0707 | -0.042954 | 0.0024076 | 0.063589 | 0.05874 | 0.0016236 | -0.0012518 | 0.00034614 | -0.021362 | 0.0018457 | 0.065448 | 0.060712 | -0.0052638 | 0.0092241 | 0.0009634 | -0.10529 | 63.0295 | -59.2987 | 63.1256 | -59.0378 | -59.4543 | -59.3948 | -0.091553 | 63.002 | -59.1843 | 63.1485 | -59.1934 | -59.3216 | -59.1614 | -0.1236 | -0.041199 | 0.054931 | 0.13733 | -0.21973 | -0.27924 | -0.09613 | -0.15564 | -0.009155 | -0.068665 | 0.07782 | -0.01831 | 0.013733 | -0.14648 | 0.022888 | -0.13733 | 0.26093 | 122.4243 | -0.009155 | 122.3328 | 122.3282 | 122.1863 | 122.2046 | 122.1771 | -122.3694 | -122.2549 | 122.3007 | 122.3236 | 59.0698 | 59.0836
887.3125 | 122.6074 | -59.1705 | 63.1119 | -0.042954 | 0.0024076 | 0.06188 | 0.058526 | -0.0028626 | -0.0059516 | -0.0030719 | 0.012207 | 0.0020593 | 0.06502 | 0.062634 | -0.0082544 | 0.010506 | -0.0013864 | 0.027466 | 63.0569 | -59.2667 | 63.2309 | -58.9645 | -59.3445 | -59.317 | 0.064087 | 63.0249 | -59.1797 | 63.208 | -59.1064 | -59.2163 | -59.1248 | -0.096131 | -0.054931 | 0.11902 | 0.20599 | -0.14648 | -0.17395 | -0.050354 | -0.077819 | -0.009155 | -0.086975 | 0.096131 | 0.064087 | 0.045776 | -0.045777 | 0.054931 | -0.036622 | 0.30212 | 122.4976 | 0.073242 | 122.3877 | 122.3236 | 122.2046 | 122.2275 | 122.1954 | -122.3785 | -122.2916 | 122.4014 | 122.3785 | 59.198 | 59.2346
888.3125 | 122.58 | -59.1797 | 63.0844 | -0.096359 | 0.0026212 | 0.062735 | 0.060449 | 0.002478 | -0.0025336 | -0.0013629 | -0.024414 | 0.0020593 | 0.065661 | 0.060071 | -0.0071864 | 0.0090105 | 0.0005362 | -0.068665 | 62.9974 | -59.285 | 63.1577 | -58.9966 | -59.4223 | -59.3765 | -0.036621 | 62.9654 | -59.1843 | 63.1897 | -59.1568 | -59.2804 | -59.1614 | -0.10529 | -0.086975 | 0.073242 | 0.18311 | -0.19684 | -0.24262 | -0.091553 | -0.13733 | -0.004578 | -0.11902 | 0.10529 | 0.022888 | 0.01831 | -0.10071 | 0.022888 | -0.096131 | 0.28839 | 122.4426 | 0.027466 | 122.374 | 122.2824 | 122.1497 | 122.1771 | 122.1451 | -122.3694 | -122.2687 | 122.3373 | 122.3694 | 59.111 | 59.1431
889.3125 | 122.5616 | -59.1614 | 63.0753 | -0.058212 | 0.0062528 | 0.061453 | 0.059167 | -0.0032898 | -0.003388 | -0.0026447 | -0.01831 | 0.00077755 | 0.067157 | 0.054944 | -0.0071864 | 0.0068743 | -0.0018136 | -0.091553 | 63.002 | -59.285 | 63.1165 | -59.0515 | -59.4543 | -59.404 | -0.091553 | 62.9883 | -59.2209 | 63.1531 | -59.1888 | -59.3033 | -59.1705 | -0.1236 | -0.073242 | 0.041199 | 0.10986 | -0.24262 | -0.29297 | -0.11902 | -0.16937 | -0.059509 | -0.086975 | 0.07782 | -0.027466 | -0.009155 | -0.14191 | 0.050354 | -0.082398 | 0.23346 | 122.4014 | 0.032043 | 122.374 | 122.287 | 122.2092 | 122.1634 | 122.1497 | -122.3602 | -122.2961 | 122.2778 | 122.3145 | 59.0698 | 59.0698
890.3125 | 122.6212 | -59.2072 | 63.0615 | -0.11925 | 0.0039028 | 0.064016 | 0.058526 | 0.0029052 | -0.0021064 | -0.0013629 | -0.054932 | 0.00077755 | 0.064807 | 0.056226 | -0.0061182 | 0.010292 | -0.0035226 | -0.068665 | 63.002 | -59.2667 | 63.1622 | -59.0012 | -59.4177 | -59.3719 | -0.027466 | 62.97 | -59.1888 | 63.1851 | -59.1522 | -59.2804 | -59.1339 | -0.05951 | -0.059509 | 0.10071 | 0.20599 | -0.1648 | -0.21057 | -0.10529 | -0.15106 | 0.01831 | -0.091552 | 0.1236 | 0.054931 | 0.073242 | -0.073243 | 0.054932 | -0.091553 | 0.2655 | 122.4289 | 0.036621 | 122.374 | 122.2687 | 122.1588 | 122.2092 | 122.1771 | -122.3282 | -122.2504 | 122.3694 | 122.3923 | 59.1385 | 59.1797
891.3125 | 122.5937 | -59.1614 | 63.0707 | -0.10399 | 0.0051846 | 0.065725 | 0.060449 | 0.0054688 | -0.0014654 | 0.0012005 | -0.054932 | 0.0022729 | 0.065448 | 0.058575 | -0.0048364 | 0.0094379 | -0.0035226 | -0.059509 | 62.9837 | -59.3033 | 63.1805 | -58.9874 | -59.4177 | -59.3765 | -0.036621 | 62.97 | -59.2117 | 63.208 | -59.1293 | -59.2758 | -59.1476 | -0.14191 | -0.086975 | 0.10986 | 0.17395 | -0.21515 | -0.25635 | -0.073242 | -0.11444 | -0.050354 | -0.10071 | 0.13733 | 0.032044 | 0.013733 | -0.11444 | 0.064087 | -0.064087 | 0.31586 | 122.4838 | 0.082398 | 122.4197 | 122.287 | 122.1817 | 122.1451 | 122.1313 | -122.374 | -122.2824 | 122.3419 | 122.3694 | 59.1019 | 59.1248
892.3125 | 122.5708 | -59.1797 | 63.1256 | -0.0048066 | 0.0034756 | 0.06188 | 0.059167 | -0.0028626 | -0.0010382 | -0.0024311 | -8.6e-08 | 0.00035035 | 0.064166 | 0.062207 | -0.0065454 | 0.0090105 | -0.0054452 | -0.054932 | 63.0341 | -59.2896 | 63.1302 | -59.0286 | -59.3994 | -59.3857 | -0.041199 | 62.9974 | -59.1888 | 63.176 | -59.1614 | -59.2529 | -59.1705 | -0.10986 | -0.091552 | 0.004578 | 0.15106 | -0.20599 | -0.21973 | -0.09613 | -0.10986 | -0.009156 | -0.12817 | 0.050354 | 0.01831 | 0.009155 | -0.073243 | 0.018311 | -0.064087 | 0.26093 | 122.4197 | 0.027466 | 122.3648 | 122.3236 | 122.1863 | 122.2137 | 122.1771 | -122.4152 | -122.3145 | 122.3099 | 122.3557 | 59.1248 | 59.1385
893.3125 | 122.5662 | -59.198 | 63.0753 | -0.12688 | 0.0024076 | 0.062094 | 0.058313 | -0.00029898 | -0.00082456 | -8.1264e-05 | -0.033569 | 0.0024865 | 0.066943 | 0.060071 | -0.0078272 | 0.0083697 | -0.0041636 | -0.10529 | 63.0203 | -59.2896 | 63.1165 | -59.0652 | -59.4315 | -59.3948 | -0.086975 | 63.0157 | -59.2117 | 63.1027 | -59.2529 | -59.2896 | -59.1705 | -0.091553 | -0.054931 | 0.041199 | 0.13275 | -0.19684 | -0.23346 | -0.10528 | -0.14191 | -0.013733 | -0.059509 | 0.027466 | -0.054932 | 0.027466 | -0.091553 | 0.041199 | -0.07782 | 0.2243 | 122.406 | -0.041199 | 122.3145 | 122.3099 | 122.2275 | 122.2183 | 122.2137 | -122.3648 | -122.287 | 122.3145 | 122.3007 | 59.0927 | 59.111
894.3125 | 122.5113 | -59.1476 | 63.0844 | -0.08873 | 0.0011258 | 0.06423 | 0.059167 | -0.00093998 | -0.0018928 | -0.00093566 | -0.012207 | 0.00077755 | 0.06737 | 0.057935 | -0.0069726 | 0.0092241 | -0.0003182 | -0.11902 | 63.0203 | -59.2987 | 63.1256 | -59.0607 | -59.4406 | -59.3948 | -0.086975 | 62.9837 | -59.2026 | 63.1393 | -59.1019 | -59.0973 | -59.0012 | -0.15106 | -0.064087 | 0.041198 | 0.086975 | -0.24719 | -0.29297 | -0.09613 | -0.14191 | -0.054932 | -0.10071 | 0.054931 | 0.045776 | 0.14648 | 0.050354 | 0.20142 | 0.10529 | 0.23804 | 122.4243 | 0.10071 | 122.3419 | 122.319 | 122.1863 | 122.168 | 122.1313 | -122.3831 | -122.287 | 122.2733 | 122.287 | 59.0286 | 59.0607
895.3125 | 122.6898 | -59.1522 | 63.1302 | -0.11925 | 0.0013394 | 0.065298 | 0.059808 | 0.0011962 | -0.0031744 | 0.00034614 | -0.021362 | 0.0012047 | 0.066302 | 0.054517 | -0.005691 | 0.0092241 | -0.0028818 | -0.09613 | 63.0295 | -59.2758 | 63.1119 | -59.0515 | -59.4498 | -59.3903 | -0.09613 | 62.9974 | -59.1934 | 63.1531 | -59.1888 | -59.2941 | -59.1522 | -0.1236 | -0.10071 | -0.018311 | 0.10071 | -0.23804 | -0.29755 | -0.11444 | -0.17395 | -0.041198 | -0.13275 | 0.022888 | -0.036621 | 0 | -0.14191 | 0.041198 | -0.10071 | 0.2243 | 122.3877 | 0.004577 | 122.3465 | 122.3053 | 122.1909 | 122.1817 | 122.1497 | -122.406 | -122.3236 | 122.2641 | 122.3053 | 59.0561 | 59.0561
896.3125 | 122.5891 | -59.1568 | 63.0981 | -0.096359 | 0.0039028 | 0.064016 | 0.059381 | -0.0022218 | -0.004029 | -0.0024311 | 0.0030517 | 0.00099115 | 0.065661 | 0.056226 | -0.0061182 | 0.0096515 | -0.0030954 | -0.09613 | 63.0295 | -59.2758 | 63.1119 | -59.0652 | -59.4269 | -59.3994 | -0.059509 | 62.9929 | -59.2026 | 63.1531 | -59.1614 | -59.2896 | -59.1614 | -0.11902 | -0.068665 | 0.013732 | 0.091552 | -0.24262 | -0.27008 | -0.1236 | -0.15106 | -0.045777 | -0.10529 | 0.054931 | -0.004578 | -0.004578 | -0.13275 | 0.041199 | -0.086975 | 0.21057 | 122.3877 | 0.041199 | 122.3557 | 122.3053 | 122.1954 | 122.1863 | 122.1497 | -122.374 | -122.3007 | 122.2687 | 122.3099 | 59.0607 | 59.0973
897.3125 | 122.5754 | -59.2072 | 63.0798 | -0.081101 | 0.0041166 | 0.06423 | 0.060876 | 0.0035462 | -0.00232 | -0.0024311 | -0.0061035 | 0.0012047 | 0.065448 | 0.060712 | -0.0069726 | 0.0068743 | -0.0009592 | -0.10529 | 63.0112 | -59.3033 | 63.1302 | -59.0607 | -59.4498 | -59.4269 | -0.091553 | 62.9974 | -59.1888 | 63.1531 | -59.1797 | -59.2804 | -59.166 | -0.096131 | -0.068665 | 0.050354 | 0.14648 | -0.21973 | -0.24262 | -0.1236 | -0.14648 | 0.01831 | -0.082397 | 0.073242 | 0.027466 | 0.041198 | -0.073243 | 0.022888 | -0.091553 | 0.24262 | 122.4335 | 0.009156 | 122.3419 | 122.3145 | 122.1863 | 122.2183 | 122.2046 | -122.3831 | -122.2687 | 122.3373 | 122.3602 | 59.1019 | 59.1156
898.3125 | 122.5708 | -59.1751 | 63.0936 | -0.065842 | 0.0019802 | 0.063376 | 0.060876 | -0.002008 | -0.0029608 | -0.0022175 | -0.05188 | 0.0033411 | 0.065875 | 0.064557 | -0.0059046 | 0.0098651 | -0.0043772 | -0.091553 | 63.0157 | -59.3216 | 63.1348 | -59.0515 | -59.4543 | -59.3994 | -0.09613 | 63.002 | -59.1843 | 63.1622 | -59.1843 | -59.2896 | -59.1568 | -0.14648 | -0.07782 | 0.041199 | 0.1236 | -0.2243 | -0.27924 | -0.07782 | -0.13275 | -0.009155 | -0.091553 | 0.068664 | -0.009155 | 0.018311 | -0.11444 | 0.027466 | -0.10529 | 0.27008 | 122.4564 | 0 | 122.3465 | 122.3373 | 122.1863 | 122.1909 | 122.1771 | -122.4152 | -122.2778 | 122.3099 | 122.3373 | 59.0836 | 59.079
899.3125 | 122.58 | -59.1797 | 63.121 | -0.027695 | 0.0002714 | 0.063162 | 0.05874 | 0.00034182 | -0.0025336 | -0.0022175 | -0.015259 | 0.0024865 | 0.067798 | 0.06477 | -0.0044092 | 0.012429 | -0.0003182 | 0.10986 | 63.0844 | -59.2484 | 63.1256 | -59.0469 | -59.436 | -59.4131 | -0.091553 | 63.0157 | -59.23 | 63.1577 | -59.1843 | -59.3033 | -59.166 | -0.068665 | -0.036621 | 0.004577 | 0.13275 | -0.23346 | -0.25635 | -0.1648 | -0.18768 | -0.050355 | -0.10529 | 0.036621 | -0.004578 | 0.013732 | -0.1236 | 0.064087 | -0.073242 | 0.20142 | 122.374 | 0.045777 | 122.3877 | 122.3328 | 122.2458 | 122.2641 | 122.1954 | -122.3694 | -122.3511 | 122.3053 | 122.3373 | 59.2895 | 59.0881
900.3125 | 122.5616 | -59.1522 | 63.1027 | -0.10399 | -0.001224 | 0.05953 | 0.057886 | -0.0045716 | -0.0036018 | -0.0026447 | -0.01831 | 0.0033411 | 0.066302 | 0.063702 | -0.005691 | 0.0098651 | -0.003309 | 0.10986 | 63.0798 | -59.2438 | 63.1348 | -59.0607 | -59.4543 | -59.404 | -0.091553 | 63.0066 | -59.2072 | 63.1622 | -59.1751 | -59.2987 | -59.1705 | -0.091552 | -0.022888 | 0.032044 | 0.091553 | -0.25177 | -0.30212 | -0.16022 | -0.21057 | -0.054931 | -0.09613 | 0.059509 | -0.022888 | -0.01831 | -0.14648 | 0.036621 | -0.091553 | 0.18311 | 122.3785 | 0.032043 | 122.3694 | 122.3236 | 122.2137 | 122.2321 | 122.1588 | -122.3465 | -122.3099 | 122.287 | 122.3145 | 59.2621 | 59.0607
901.3125 | 122.5616 | -59.1888 | 63.1073 | -0.073471 | 0.0011258 | 0.062308 | 0.059381 | -0.0028626 | -0.0027472 | -0.0011493 | -8.6e-08 | 0.0014185 | 0.067157 | 0.058148 | -0.006759 | 0.0090105 | -0.0024546 | 0.064087 | 63.0615 | -59.2667 | 63.1165 | -59.024 | -59.4589 | -59.4223 | -0.07782 | 63.0112 | -59.1843 | 63.1668 | -59.1614 | -59.2804 | -59.166 | -0.07782 | -0.045777 | 0.009155 | 0.16479 | -0.23346 | -0.27008 | -0.15564 | -0.19226 | 0.004578 | -0.096131 | 0.059509 | 0.027466 | 0.022888 | -0.091553 | 0.01831 | -0.096131 | 0.24262 | 122.3831 | 0.022888 | 122.3511 | 122.3282 | 122.1954 | 122.2504 | 122.2 | -122.374 | -122.2916 | 122.3053 | 122.3557 | 59.2529 | 59.111
902.3125 | 122.6074 | -59.1751 | 63.1393 | 0.048599 | 0.0024076 | 0.066153 | 0.060235 | -0.0047852 | -0.0025336 | -0.00050846 | -0.015259 | 0.0020593 | 0.065448 | 0.059644 | -0.0078272 | 0.010079 | -0.009504 | -0.045776 | 63.0478 | -59.2529 | 63.2309 | -58.96 | -59.3353 | -59.2941 | 0.073242 | 63.0295 | -59.1751 | 63.2263 | -59.111 | -59.2163 | -59.1248 | -0.07782 | -0.091552 | 0.091553 | 0.21515 | -0.11902 | -0.16022 | -0.041198 | -0.082397 | 0 | -0.10986 | 0.086975 | 0.064087 | 0.050354 | -0.041199 | 0.050354 | -0.041199 | 0.29297 | 122.4838 | 0.064087 | 122.4014 | 122.3007 | 122.2046 | 122.2229 | 122.2046 | -122.3923 | -122.3145 | 122.406 | 122.4014 | 59.1293 | 59.2484
903.3125 | 122.5525 | -59.166 | 63.1119 | -0.096359 | 0.001553 | 0.063803 | 0.060449 | -0.00051278 | -0.003388 | -0.0011493 | -0.039673 | 0.0014185 | 0.06737 | 0.055371 | -0.0074 | 0.0079425 | -0.0011728 | -0.082397 | 63.0157 | -59.2804 | 63.1256 | -59.0286 | -59.4315 | -59.404 | -0.086975 | 62.9974 | -59.2163 | 63.1531 | -59.1843 | -59.2987 | -59.1751 | -0.11444 | -0.09613 | 0.013733 | 0.13733 | -0.23804 | -0.2655 | -0.1236 | -0.15106 | -0.050354 | -0.11444 | 0.041199 | -0.01831 | -0.009155 | -0.13275 | 0.041199 | -0.082397 | 0.25177 | 122.406 | 0.032044 | 122.3694 | 122.2961 | 122.2137 | 122.1817 | 122.1634 | -122.3923 | -122.3282 | 122.2916 | 122.319 | 59.0836 | 59.079
904.3125 | 122.5845 | -59.1843 | 63.1119 | -0.050583 | 0.003262 | 0.064657 | 0.059595 | 0.00098262 | -0.00082456 | -0.00050846 | -0.054932 | 0.00099115 | 0.063098 | 0.057935 | -0.0065454 | 0.0083697 | -0.0043772 | -0.082397 | 63.0524 | -59.2621 | 63.1256 | -59.079 | -59.4498 | -59.3811 | -0.10529 | 63.0066 | -59.2072 | 63.1622 | -59.1705 | -59.2987 | -59.1568 | -0.07782 | -0.059509 | 0.013733 | 0.10529 | -0.19684 | -0.2655 | -0.11902 | -0.18768 | -0.022888 | -0.10529 | 0.050354 | 0.013733 | 0.027466 | -0.11444 | 0.050354 | -0.091553 | 0.18311 | 122.3877 | 0.036621 | 122.3694 | 122.3145 | 122.2137 | 122.2366 | 122.1909 | -122.374 | -122.319 | 122.3099 | 122.3465 | 59.1019 | 59.079
905.3125 | 122.5616 | -59.1843 | 63.121 | -0.096359 | 0.0047574 | 0.061239 | 0.05874 | 0.0018372 | -0.0018928 | -0.0015765 | -0.036621 | 0.0014185 | 0.064593 | 0.066479 | -0.0052638 | 0.0090105 | -0.0022408 | -0.086975 | 63.0478 | -59.2621 | 63.1439 | -59.0744 | -59.4635 | -59.3903 | -0.09613 | 62.9974 | -59.2117 | 63.1668 | -59.1888 | -59.3033 | -59.166 | -0.07782 | -0.073242 | 0.022888 | 0.10986 | -0.20599 | -0.27924 | -0.12817 | -0.20142 | -0.027466 | -0.1236 | 0.045776 | -0.004578 | 0.01831 | -0.11902 | 0.045776 | -0.091553 | 0.18768 | 122.406 | 0.022888 | 122.3785 | 122.3099 | 122.2092 | 122.2321 | 122.1817 | -122.3831 | -122.3328 | 122.3282 | 122.3511 | 59.0973 | 59.0881
906.3125 | 122.6257 | -59.1019 | 63.121 | -0.027695 | 0.0019802 | 0.062521 | 0.060663 | -0.00029898 | -0.00082456 | -0.0028583 | -0.0091553 | 0.00013675 | 0.066943 | 0.054303 | -0.0063318 | 0.011147 | -0.0035226 | -0.013733 | 63.0615 | -59.2575 | 63.1943 | -58.9554 | -59.3445 | -59.3308 | 0.10071 | 63.0295 | -59.1705 | 63.2401 | -59.0744 | -59.198 | -59.0927 | -0.15564 | -0.05951 | 0.073242 | 0.14649 | -0.22888 | -0.24261 | -0.073243 | -0.086975 | -0.068664 | -0.091553 | 0.11902 | 0.027466 | 0.009156 | -0.09613 | 0.07782 | -0.027466 | 0.30212 | 122.4518 | 0.09613 | 122.4106 | 122.319 | 122.2 | 122.1634 | 122.1313 | -122.3785 | -122.2916 | 122.2961 | 122.3419 | 59.0881 | 59.2026
907.3125 | 122.5845 | -59.1522 | 63.1073 | 0.094376 | 0.0019802 | 0.062948 | 0.060022 | -0.002008 | -0.0012518 | -0.0022175 | -0.01831 | 0.00077755 | 0.065875 | 0.056653 | -0.0063318 | 0.010506 | -0.0016 | 0.086975 | 63.0981 | -59.2758 | 63.2217 | -58.9096 | -59.3399 | -59.317 | 0.091553 | 63.0249 | -59.166 | 63.2172 | -59.0881 | -59.2117 | -59.0881 | -0.1236 | -0.009155 | 0.11444 | 0.24262 | -0.16479 | -0.18768 | -0.041199 | -0.064087 | -0.013733 | -0.082398 | 0.10986 | 0.064087 | 0.064087 | -0.059509 | 0.07782 | -0.045776 | 0.36621 | 122.4976 | 0.07782 | 122.3831 | 122.374 | 122.1909 | 122.2504 | 122.1771 | -122.3831 | -122.2733 | 122.374 | 122.3694 | 59.2392 | 59.2438
908.3125 | 122.5937 | -59.1705 | 63.121 | -0.081101 | 0.0030484 | 0.063376 | 0.058954 | -0.0035034 | -0.0031744 | -0.0032855 | -0.042725 | 0.0029137 | 0.066943 | 0.067975 | -0.0061182 | 0.010079 | -0.0030954 | -0.086975 | 63.0341 | -59.2896 | 63.2812 | -59.0973 | -59.5642 | -59.404 | -0.082397 | 63.002 | -59.2163 | 63.1439 | -59.1934 | -59.2987 | -59.1705 | -0.11902 | -0.086975 | 0.16022 | 0.073242 | -0.23346 | -0.39368 | -0.11444 | -0.27466 | -0.045777 | -0.11902 | 0.022888 | -0.022888 | 0 | -0.12817 | 0.045777 | -0.082397 | 0.19226 | 122.5708 | 0.022889 | 122.3602 | 122.3236 | 122.2183 | 122.2046 | 122.1725 | -122.4106 | -122.3373 | 122.4518 | 122.3145 | 59.0836 | 59.0881
909.3125 | 122.5891 | -59.1476 | 63.1256 | -0.058212 | 0.0026212 | 0.062948 | 0.059167 | 0.0026916 | -0.0046698 | -0.00093566 | 0.0030517 | 0.0020593 | 0.066089 | 0.062207 | -0.0080408 | 0.0096515 | -0.0016 | -0.054932 | 63.0432 | -59.2667 | 63.1531 | -59.0332 | -59.4131 | -59.3582 | -0.027466 | 63.0066 | -59.1888 | 63.1989 | -59.1385 | -59.2392 | -59.1156 | -0.11902 | -0.082397 | 0.027466 | 0.11444 | -0.21057 | -0.2655 | -0.091552 | -0.14648 | -0.041199 | -0.11902 | 0.073243 | 0.009155 | 0.032043 | -0.091553 | 0.073242 | -0.050354 | 0.23346 | 122.4197 | 0.050354 | 122.3877 | 122.3099 | 122.1954 | 122.1909 | 122.1542 | -122.3923 | -122.3145 | 122.3007 | 122.3465 | 59.0927 | 59.1202
910.3125 | 122.612 | -59.1934 | 63.121 | -0.096359 | 0.0030484 | 0.061026 | 0.057031 | 0.0011962 | -0.0053108 | -0.0015765 | 0.0091553 | 0.0037683 | 0.063739 | 0.059644 | -0.0054774 | 0.0090105 | -0.005018 | -0.064087 | 63.0432 | -59.2758 | 63.1393 | -59.0424 | -59.404 | -59.3582 | -0.032043 | 63.0112 | -59.1843 | 63.1943 | -59.1522 | -59.2621 | -59.1293 | -0.082398 | -0.07782 | 0.01831 | 0.15106 | -0.16479 | -0.21057 | -0.082397 | -0.12817 | 0.009155 | -0.10986 | 0.073242 | 0.041198 | 0.064087 | -0.068665 | 0.054932 | -0.07782 | 0.23346 | 122.4152 | 0.032043 | 122.3785 | 122.319 | 122.1954 | 122.2366 | 122.2046 | -122.3969 | -122.3053 | 122.3328 | 122.3877 | 59.1293 | 59.1614
911.3125 | 122.5159 | -59.1797 | 63.1989 | 0.018082 | 0.002194 | 0.063376 | 0.061303 | -0.0017944 | -0.0036018 | -0.00072206 | -0.094604 | 0.0027001 | 0.066729 | 0.066693 | -0.005691 | 0.0075153 | -0.0039498 | -0.036621 | 63.1073 | -59.2712 | 63.1119 | -59.0836 | -59.4406 | -59.4223 | -0.045776 | 63.0753 | -59.1934 | 63.1485 | -59.198 | -59.3353 | -59.1797 | -0.091553 | -0.091553 | -0.086976 | 0.09613 | -0.24262 | -0.26093 | -0.15106 | -0.16937 | -0.013733 | -0.1236 | -0.050354 | -0.018311 | 0 | -0.15564 | 0.013733 | -0.14191 | 0.18768 | 122.3831 | -0.004578 | 122.3419 | 122.3785 | 122.2687 | 122.287 | 122.2549 | -122.4701 | -122.3923 | 122.2916 | 122.3282 | 59.1431 | 59.1339
912.3125 | 122.6349 | -59.1522 | 63.121 | -0.027695 | 0.0011258 | 0.062094 | 0.055322 | 0.004187 | -0.0027472 | 0.0020551 | 0.0091553 | 0.0016321 | 0.065661 | 0.056866 | -0.0059046 | 0.0077289 | -0.000532 | -0.022888 | 63.0249 | -59.2621 | 63.1668 | -58.9828 | -59.3582 | -59.3262 | 0.041199 | 63.0066 | -59.1888 | 63.2172 | -59.1019 | -59.2117 | -59.1156 | -0.10986 | -0.096131 | 0.045776 | 0.16937 | -0.17395 | -0.20599 | -0.064087 | -0.09613 | -0.036621 | -0.11444 | 0.09613 | 0.050354 | 0.036621 | -0.059509 | 0.073242 | -0.022888 | 0.27924 | 122.4289 | 0.086975 | 122.406 | 122.287 | 122.1954 | 122.1771 | 122.1588 | -122.3831 | -122.3099 | 122.319 | 122.3694 | 59.1293 | 59.1934
913.3125 | 122.6028 | -59.1431 | 63.1119 | -0.096359 | 0.0024076 | 0.064016 | 0.061303 | -0.0011536 | -0.0036018 | -0.0011493 | 0.012207 | 0.0020593 | 0.067157 | 0.062421 | -0.0061182 | 0.010292 | -0.0011728 | -0.018311 | 63.0569 | -59.2941 | 63.1668 | -58.9966 | -59.3628 | -59.3216 | 0.050354 | 62.9929 | -59.166 | 63.2126 | -59.0973 | -59.2163 | -59.111 | -0.15106 | -0.054931 | 0.054932 | 0.14648 | -0.17853 | -0.21973 | -0.027466 | -0.068665 | -0.022889 | -0.11902 | 0.10071 | 0.045776 | 0.032043 | -0.073243 | 0.054932 | -0.050354 | 0.29755 | 122.4609 | 0.068665 | 122.3785 | 122.3511 | 122.1588 | 122.2 | 122.1359 | -122.406 | -122.2778 | 122.3099 | 122.3557 | 59.1248 | 59.1934
914.3125 | 122.612 | -59.1614 | 63.1073 | -0.0048066 | 0.002194 | 0.062735 | 0.05874 | -0.0024354 | -0.0027472 | -0.0032855 | 0.0061035 | 0.00056395 | 0.065448 | 0.066693 | -0.0078272 | 0.010292 | -0.0013864 | 0.018311 | 63.0569 | -59.2575 | 63.2309 | -58.9279 | -59.3124 | -59.2987 | 0.36163 | 63.0661 | -59.1064 | 63.2309 | -59.1476 | -59.1522 | -59.0652 | -0.09613 | -0.050354 | 0.1236 | 0.23346 | -0.13733 | -0.15106 | -0.041199 | -0.054932 | 0.054932 | -0.041199 | 0.1236 | 0.013733 | 0.09613 | 0.009155 | 0.041198 | -0.045777 | 0.32959 | 122.4884 | -0.041199 | 122.3373 | 122.3145 | 122.1725 | 122.2183 | 122.2275 | -122.3648 | -122.2137 | 122.3923 | 122.3923 | 59.1797 | 59.523
915.3125 | 122.5937 | -59.1385 | 63.1119 | -0.08873 | 0.0024076 | 0.060812 | 0.058954 | -0.0039306 | -0.0042426 | -0.0032855 | -0.015259 | 0.00056395 | 0.065448 | 0.053662 | -0.0069726 | 0.0081561 | -0.0001046 | -0.022888 | 63.0341 | -59.2667 | 63.1531 | -58.992 | -59.3674 | -59.3445 | 0.004578 | 63.0341 | -59.1934 | 63.2126 | -59.1019 | -59.2209 | -59.1202 | -0.12817 | -0.077819 | 0.041199 | 0.14648 | -0.20599 | -0.22888 | -0.077819 | -0.10071 | -0.054931 | -0.077819 | 0.10071 | 0.036621 | 0.018311 | -0.082397 | 0.073242 | -0.027466 | 0.27466 | 122.4197 | 0.091552 | 122.406 | 122.3007 | 122.2275 | 122.1725 | 122.1725 | -122.3785 | -122.3053 | 122.2916 | 122.3511 | 59.1156 | 59.1431
916.3125 | 122.5204 | -59.1888 | 63.1577 | -0.027695 | 0.0034756 | 0.062948 | 0.059595 | -0.0024354 | -0.0021064 | -0.00072206 | -0.091553 | 0.0048363 | 0.065234 | 0.066052 | -0.0069726 | 0.010292 | -0.005018 | -0.022888 | 63.0844 | -59.2804 | 63.1348 | -59.0652 | -59.4223 | -59.4131 | -0.004578 | 63.0661 | -59.1843 | 63.1577 | -59.1888 | -59.3124 | -59.1751 | -0.091553 | -0.073242 | -0.022888 | 0.1236 | -0.2243 | -0.23346 | -0.13275 | -0.14191 | 0.004578 | -0.091553 | 0 | 0 | 0.013733 | -0.1236 | 0.009155 | -0.12817 | 0.21515 | 122.4152 | -0.004578 | 122.3419 | 122.3648 | 122.2504 | 122.2733 | 122.2549 | -122.4381 | -122.3419 | 122.3236 | 122.3465 | 59.166 | 59.1843
917.3125 | 122.612 | -59.1476 | 63.1256 | -0.073471 | 0.0028348 | 0.063589 | 0.059167 | 0.00098262 | -0.0042426 | -8.1264e-05 | -0.030517 | 0.0037683 | 0.065875 | 0.062848 | -0.0054774 | 0.0087969 | -0.0035226 | -0.013733 | 63.0157 | -59.2575 | 63.2172 | -58.9279 | -59.2896 | -59.2896 | 0.082397 | 63.0203 | -59.1614 | 63.1989 | -59.0881 | -59.2117 | -59.1019 | -0.10986 | -0.10986 | 0.091553 | 0.21973 | -0.14191 | -0.14191 | -0.032044 | -0.032044 | -0.013733 | -0.10529 | 0.073243 | 0.059509 | 0.045776 | -0.064087 | 0.059509 | -0.050354 | 0.32959 | 122.4747 | 0.073242 | 122.3602 | 122.2733 | 122.1817 | 122.1634 | 122.168 | -122.3831 | -122.287 | 122.3648 | 122.3465 | 59.1339 | 59.23
918.3125 | 122.5571 | -59.1888 | 63.1348 | -0.020065 | 0.0036892 | 0.064444 | 0.058099 | -0.00051278 | -0.0027472 | -8.1264e-05 | -0.01831 | 0.00077755 | 0.066302 | 0.059216 | -0.0065454 | 0.0094379 | -0.003309 | -0.082397 | 63.0386 | -59.2667 | 63.121 | -59.0286 | -59.4772 | -59.4177 | -0.091553 | 63.0112 | -59.2209 | 63.1714 | -59.1797 | -59.2941 | -59.1797 | -0.07782 | -0.096131 | -0.013733 | 0.16022 | -0.22888 | -0.28839 | -0.15106 | -0.21057 | -0.032043 | -0.1236 | 0.036621 | 0.009156 | 0.009156 | -0.10529 | 0.041199 | -0.073242 | 0.23804 | 122.3877 | 0.041199 | 122.3923 | 122.3053 | 122.2321 | 122.2275 | 122.2 | -122.4014 | -122.3557 | 122.3099 | 122.3602 | 59.1064 | 59.0973
919.3125 | 122.5983 | -59.1522 | 63.1073 | -0.081101 | 0.0039028 | 0.065725 | 0.060449 | -0.00093998 | 0.001098 | -0.0015765 | 0.018311 | 0.0014185 | 0.066089 | 0.065411 | -0.0052638 | 0.0085833 | -0.0060862 | -0.041199 | 63.0661 | -59.2575 | 63.1439 | -59.0195 | -59.3903 | -59.3536 | -0.041199 | 63.0066 | -59.1843 | 63.1989 | -59.1339 | -59.2392 | -59.1156 | -0.10528 | -0.041199 | 0.036621 | 0.13275 | -0.20142 | -0.23804 | -0.096131 | -0.13275 | -0.032043 | -0.10071 | 0.091553 | 0.018311 | 0.036621 | -0.086975 | 0.068664 | -0.054932 | 0.23804 | 122.4014 | 0.050354 | 122.3831 | 122.3236 | 122.1909 | 122.2183 | 122.1588 | -122.3648 | -122.2916 | 122.2961 | 122.3511 | 59.111 | 59.111
920.3125 | 122.6212 | -59.1431 | 63.1348 | -0.035324 | 0.0013394 | 0.063589 | 0.060449 | -0.00029898 | -0.0036018 | 0.00013254 | -8.6e-08 | 0.00056395 | 0.066943 | 0.061352 | -0.0054774 | 0.010292 | -0.008436 | -0.013733 | 63.0569 | -59.2575 | 63.176 | -58.9783 | -59.3582 | -59.3216 | 0.041199 | 62.9974 | -59.166 | 63.2309 | -59.0881 | -59.2209 | -59.1019 | -0.11444 | -0.07782 | 0.041198 | 0.16479 | -0.17853 | -0.21515 | -0.064087 | -0.10071 | -0.022889 | -0.13733 | 0.09613 | 0.054931 | 0.041198 | -0.07782 | 0.064087 | -0.054931 | 0.27924 | 122.4335 | 0.07782 | 122.3969 | 122.3145 | 122.1634 | 122.2 | 122.1405 | -122.3923 | -122.3007 | 122.319 | 122.374 | 59.1293 | 59.1843
921.3125 | 122.5113 | -59.1934 | 63.1668 | -0.020065 | 0.0026212 | 0.064444 | 0.060876 | -0.00029898 | -0.0029608 | 0.00077334 | -0.067139 | 0.0029137 | 0.065875 | 0.064343 | -0.0065454 | 0.010079 | -0.0011728 | -0.022888 | 63.1027 | -59.3079 | 62.9562 | -59.0652 | -59.3857 | -59.4315 | -0.036621 | 63.0798 | -59.198 | 63.1256 | -59.198 | -59.3445 | -59.2438 | -0.11444 | -0.064087 | -0.21057 | 0.12817 | -0.23804 | -0.19226 | -0.1236 | -0.07782 | -0.004578 | -0.086975 | -0.041199 | -0.004578 | -0.050354 | -0.15106 | -0.045776 | -0.14648 | 0.24261 | 122.2641 | 0 | 122.3236 | 122.4106 | 122.2778 | 122.2961 | 122.2733 | -122.4747 | -122.3648 | 122.1497 | 122.319 | 59.1705 | 59.1568
922.3125 | 122.6166 | -59.1476 | 63.1348 | -0.058212 | 0.0019802 | 0.063376 | 0.058954 | 0.0020508 | -0.0029608 | -0.0020039 | 0.021362 | 0.00099115 | 0.06502 | 0.061139 | -0.0069726 | 0.010292 | -0.0016 | 0.036621 | 63.0524 | -59.2575 | 63.208 | -58.9371 | -59.3124 | -59.3124 | 0.064087 | 63.0295 | -59.166 | 63.2126 | -59.0927 | -59.2255 | -59.1064 | -0.10986 | -0.082398 | 0.073242 | 0.21057 | -0.16479 | -0.16479 | -0.054932 | -0.054932 | -0.018311 | -0.10529 | 0.077819 | 0.054932 | 0.041199 | -0.07782 | 0.05951 | -0.059509 | 0.32043 | 122.4655 | 0.073243 | 122.3785 | 122.3099 | 122.1954 | 122.2 | 122.1771 | -122.3923 | -122.3007 | 122.3557 | 122.3602 | 59.1843 | 59.2117
923.3125 | 122.5845 | -59.1843 | 63.1073 | -0.096359 | 0.001553 | 0.062735 | 0.058526 | -0.002649 | -0.0042426 | -0.0020039 | 0.0030517 | 0.0031273 | 0.064807 | 0.059003 | -0.0052638 | 0.0094379 | -0.0045908 | -0.10986 | 63.0295 | -59.2896 | 63.1165 | -59.0469 | -59.4177 | -59.4086 | -0.059509 | 63.0203 | -59.198 | 63.1668 | -59.1705 | -59.2804 | -59.1476 | -0.10529 | -0.07782 | 0.009155 | 0.13733 | -0.2243 | -0.23346 | -0.11902 | -0.12817 | -0.013733 | -0.086975 | 0.059509 | 0.013733 | 0.036621 | -0.096131 | 0.050354 | -0.082398 | 0.24262 | 122.406 | 0.027466 | 122.3648 | 122.319 | 122.2183 | 122.2137 | 122.2046 | -122.3969 | -122.3053 | 122.3007 | 122.3511 | 59.0744 | 59.1248
924.3125 | 122.6395 | -59.1751 | 63.1073 | -0.058212 | 0.0019802 | 0.062094 | 0.058954 | -0.0011536 | -0.0038154 | -0.00050846 | 0.021362 | 0.0035547 | 0.065234 | 0.063275 | -0.0069726 | 0.010933 | -0.0020272 | -0.050354 | 63.0341 | -59.2621 | 63.1485 | -59.0057 | -59.3811 | -59.3674 | -0.013733 | 63.0112 | -59.1614 | 63.2034 | -59.1385 | -59.2346 | -59.1156 | -0.086975 | -0.073242 | 0.041199 | 0.16937 | -0.19226 | -0.20599 | -0.10529 | -0.11902 | 0.013733 | -0.096131 | 0.09613 | 0.036621 | 0.059509 | -0.059509 | 0.045776 | -0.073242 | 0.25635 | 122.4106 | 0.022888 | 122.3648 | 122.2961 | 122.1725 | 122.2092 | 122.1863 | -122.3694 | -122.2687 | 122.3236 | 122.3785 | 59.1248 | 59.1614
925.3125 | 122.5525 | -59.1751 | 63.1119 | -0.13451 | 0.0011258 | 0.063376 | 0.059595 | -0.0024354 | -0.0014654 | -0.0020039 | 0.018311 | 0.0012047 | 0.066089 | 0.056226 | -0.0061182 | 0.010079 | -0.0030954 | -0.07782 | 63.0295 | -59.2941 | 63.2675 | -58.8959 | -59.6466 | -59.4315 | -0.1236 | 63.0066 | -59.198 | 63.1485 | -59.1797 | -59.2758 | -59.166 | -0.11902 | -0.082397 | 0.15564 | 0.27924 | -0.25635 | -0.4715 | -0.13733 | -0.35248 | -0.022888 | -0.10529 | 0.036622 | -0.004577 | 0.009155 | -0.10071 | 0.032043 | -0.07782 | 0.39825 | 122.5616 | 0.018311 | 122.3465 | 122.3236 | 122.2046 | 122.2046 | 122.1817 | -122.406 | -122.3099 | 122.4426 | 122.3236 | 59.0973 | 59.0515
926.3125 | 122.4976 | -59.1843 | 63.1805 | -0.065842 | 0.0030484 | 0.060599 | 0.061517 | -0.00029898 | -0.0042426 | 0.00013254 | -0.048828 | 0.0027001 | 0.066516 | 0.060284 | -0.005691 | 0.0096515 | -0.0030954 | 0.16022 | 63.1439 | -59.2575 | 63.0707 | -59.0881 | -59.4269 | -59.4315 | -0.036621 | 63.0981 | -59.198 | 63.1165 | -59.2026 | -59.3491 | -59.1797 | -0.073242 | -0.036621 | -0.10986 | 0.09613 | -0.24719 | -0.24261 | -0.17395 | -0.16937 | -0.013733 | -0.082397 | -0.064087 | -0.018311 | 0.004578 | -0.16479 | 0.018311 | -0.15106 | 0.16937 | 122.3282 | -0.004578 | 122.3145 | 122.4014 | 122.2961 | 122.3282 | 122.2824 | -122.438 | -122.3785 | 122.2549 | 122.3007 | 59.3445 | 59.1476
927.3125 | 122.493 | -59.1797 | 63.176 | 0.0028229 | 0.0058256 | 0.062948 | 0.060235 | 0.0039734 | -0.0027472 | -0.0020039 | -0.015259 | 0.0027001 | 0.066302 | 0.060925 | -0.0071864 | 0.011574 | 0.0003226 | 0.022888 | 63.0707 | -59.2575 | 63.1531 | -59.0057 | -59.3765 | -59.3719 | -0.004578 | 63.0341 | -59.1705 | 63.1256 | -59.1934 | -59.3124 | -59.2163 | -0.07782 | -0.10529 | -0.022888 | 0.17395 | -0.19226 | -0.19684 | -0.11444 | -0.11902 | 0.009155 | -0.14191 | -0.050354 | -0.013733 | -0.036622 | -0.13275 | -0.045777 | -0.14191 | 0.25177 | 122.4106 | -0.022888 | 122.2961 | 122.3282 | 122.2046 | 122.2504 | 122.2137 | -122.4335 | -122.3465 | 122.3328 | 122.3053 | 59.2026 | 59.1751
928.3125 | 122.6212 | -59.1705 | 63.1439 | -0.081101 | 0.0028348 | 0.062735 | 0.057886 | 0.00076902 | -0.0025336 | -0.0043537 | 0.012207 | 0.0016321 | 0.064807 | 0.061139 | -0.0048364 | 0.0087969 | 0.000109 | -0.022888 | 63.0478 | -59.2484 | 63.1622 | -59.0012 | -59.3674 | -59.3536 | 0.009155 | 63.0341 | -59.1568 | 63.2172 | -59.1019 | -59.2255 | -59.1064 | -0.07782 | -0.09613 | 0.01831 | 0.16937 | -0.18311 | -0.19684 | -0.10529 | -0.11902 | 0.013733 | -0.10986 | 0.073242 | 0.068664 | 0.064087 | -0.054932 | 0.050354 | -0.068665 | 0.24719 | 122.4106 | 0.054931 | 122.374 | 122.2961 | 122.1909 | 122.2183 | 122.2046 | -122.3923 | -122.3007 | 122.3328 | 122.3877 | 59.1476 | 59.1797
929.3125 | 122.6212 | -59.1385 | 63.121 | -0.035324 | 0.003262 | 0.062521 | 0.060449 | 0.0039734 | -0.003388 | 0.00055974 | 0.0061035 | 0.0022729 | 0.067157 | 0.058575 | -0.0052638 | 0.010506 | -0.0054452 | -0.050354 | 63.0432 | -59.2575 | 63.1485 | -59.0057 | -59.3857 | -59.3399 | 0.004578 | 63.0157 | -59.1522 | 63.2034 | -59.1339 | -59.2255 | -59.1156 | -0.11902 | -0.07782 | 0.027466 | 0.13275 | -0.20142 | -0.24719 | -0.082398 | -0.12817 | -0.013733 | -0.10529 | 0.082397 | 0.004578 | 0.022888 | -0.086975 | 0.036621 | -0.073242 | 0.25177 | 122.406 | 0.018311 | 122.3557 | 122.3007 | 122.168 | 122.1817 | 122.1542 | -122.3785 | -122.2733 | 122.287 | 122.3419 | 59.0881 | 59.1431
930.3125 | 122.6395 | -59.1385 | 63.1256 | -0.027695 | 0.001553 | 0.061453 | 0.060235 | 0.00055542 | -0.0042426 | -0.0015765 | -0.012207 | 0.0016321 | 0.067157 | 0.060712 | -0.0076136 | 0.0090105 | -0.0026682 | -0.013733 | 63.0432 | -59.2575 | 63.1989 | -58.9554 | -59.3308 | -59.2987 | 0.10529 | 63.0157 | -59.1476 | 63.2538 | -59.0744 | -59.1888 | -59.0927 | -0.11902 | -0.082397 | 0.073243 | 0.18311 | -0.16022 | -0.19226 | -0.041199 | -0.073243 | -0.009155 | -0.10986 | 0.12817 | 0.064087 | 0.045777 | -0.050354 | 0.054932 | -0.041199 | 0.30212 | 122.4564 | 0.073242 | 122.4014 | 122.3007 | 122.1634 | 122.1817 | 122.1542 | -122.3831 | -122.2733 | 122.3373 | 122.3923 | 59.1248 | 59.2438
931.3125 | 122.5983 | -59.1385 | 63.1302 | -0.08873 | 0.0024076 | 0.064444 | 0.058313 | 0.0022644 | -0.0046698 | -0.00072206 | -0.0061035 | 0.0035547 | 0.066943 | 0.061352 | -0.0044092 | 0.0077289 | -0.0022408 | -0.054932 | 63.0386 | -59.2621 | 63.1439 | -59.024 | -59.4177 | -59.3674 | -0.032043 | 63.0295 | -59.1705 | 63.1714 | -59.1522 | -59.2529 | -59.1339 | -0.1236 | -0.091553 | 0.013733 | 0.11444 | -0.22888 | -0.27924 | -0.10529 | -0.15564 | -0.032043 | -0.10071 | 0.041199 | -0.013733 | 0.004578 | -0.11444 | 0.036621 | -0.082398 | 0.23804 | 122.406 | 0.01831 | 122.3419 | 122.3007 | 122.2 | 122.1771 | 122.168 | -122.3923 | -122.3007 | 122.2824 | 122.3099 | 59.0836 | 59.1064
932.3125 | 122.5891 | -59.1568 | 63.1165 | -0.081101 | 0.0036892 | 0.062094 | 0.059381 | -0.00029898 | -0.0046698 | -0.0032855 | -8.6e-08 | 0.0033411 | 0.065661 | 0.061139 | -0.0054774 | 0.01072 | -0.0043772 | -0.054932 | 63.0478 | -59.285 | 63.121 | -59.0378 | -59.4131 | -59.3903 | -0.064087 | 63.0066 | -59.1797 | 63.1851 | -59.1568 | -59.2529 | -59.1385 | -0.12817 | -0.068664 | 0.004578 | 0.11902 | -0.23346 | -0.25635 | -0.10529 | -0.12817 | -0.022888 | -0.10986 | 0.068665 | 0 | 0.01831 | -0.096131 | 0.041198 | -0.073243 | 0.24719 | 122.406 | 0.022888 | 122.3648 | 122.3328 | 122.1863 | 122.2046 | 122.1634 | -122.4014 | -122.2961 | 122.2778 | 122.3419 | 59.1019 | 59.0927
933.3125 | 122.5891 | -59.1476 | 63.1073 | -0.073471 | 0.0028348 | 0.062308 | 0.058313 | -0.0017944 | -0.0021064 | -0.0037129 | -0.01831 | 0.0012047 | 0.065448 | 0.05473 | -0.0088952 | 0.0085833 | -0.0058724 | -0.082397 | 63.0386 | -59.2667 | 63.1256 | -59.0378 | -59.4315 | -59.3903 | -0.10071 | 63.0249 | -59.1888 | 63.1668 | -59.1797 | -59.2941 | -59.1568 | -0.11902 | -0.068665 | 0.01831 | 0.10986 | -0.24262 | -0.28381 | -0.1236 | -0.16479 | -0.041199 | -0.082398 | 0.059509 | -0.032043 | -0.009155 | -0.14648 | 0.032044 | -0.10529 | 0.22888 | 122.3923 | 0.009156 | 122.3557 | 122.3053 | 122.2137 | 122.1863 | 122.1725 | -122.374 | -122.2961 | 122.2733 | 122.3145 | 59.0652 | 59.0469
934.3125 | 122.612 | -59.1339 | 63.1119 | -0.11162 | 0.0036892 | 0.06188 | 0.058954 | -0.0056396 | -0.004029 | 0.00034614 | 0.0091553 | 0.0016321 | 0.06737 | 0.059857 | -0.0048364 | 0.0085833 | -0.0026682 | -0.045776 | 63.0432 | -59.2712 | 63.1622 | -59.0012 | -59.3674 | -59.3491 | -0.018311 | 63.0157 | -59.1751 | 63.1897 | -59.1248 | -59.2529 | -59.1248 | -0.13733 | -0.068664 | 0.050354 | 0.13275 | -0.21515 | -0.23346 | -0.07782 | -0.096131 | -0.041199 | -0.09613 | 0.07782 | 0.009155 | 0.009155 | -0.11902 | 0.050354 | -0.07782 | 0.27008 | 122.4335 | 0.050354 | 122.3648 | 122.3145 | 122.1909 | 122.1771 | 122.1497 | -122.3831 | -122.287 | 122.2961 | 122.3236 | 59.0881 | 59.1156
935.3125 | 122.6028 | -59.1614 | 63.121 | -0.050583 | 0.0024076 | 0.062948 | 0.059381 | -0.00093998 | -0.0018928 | -0.0013629 | -0.01831 | 0.00099115 | 0.065875 | 0.060925 | -0.0065454 | 0.0087969 | -0.0018136 | -0.059509 | 63.0432 | -59.2529 | 63.1531 | -59.0149 | -59.3948 | -59.3491 | -0.027466 | 63.0341 | -59.1614 | 63.1943 | -59.1293 | -59.2575 | -59.1156 | -0.091553 | -0.07782 | 0.032043 | 0.14648 | -0.18768 | -0.23346 | -0.09613 | -0.14191 | 0 | -0.086975 | 0.073242 | 0.032044 | 0.045776 | -0.09613 | 0.045776 | -0.09613 | 0.23804 | 122.406 | 0.032044 | 122.3557 | 122.2961 | 122.1954 | 122.2046 | 122.1954 | -122.374 | -122.2824 | 122.3145 | 122.3557 | 59.1019 | 59.1339
936.3125 | 122.5983 | -59.1614 | 63.1073 | -0.042954 | 0.0028348 | 0.06188 | 0.060449 | -0.00072638 | -0.0010382 | -0.00050846 | -0.024414 | 0.0022729 | 0.065875 | 0.059216 | -0.0069726 | 0.0081561 | -0.0039498 | -0.054932 | 63.0295 | -59.285 | 63.1256 | -59.0332 | -59.4086 | -59.3719 | -0.041199 | 63.0066 | -59.198 | 63.1805 | -59.1476 | -59.2575 | -59.1248 | -0.1236 | -0.07782 | 0.01831 | 0.12817 | -0.21057 | -0.24719 | -0.086975 | -0.1236 | -0.036621 | -0.10071 | 0.073242 | 0.013733 | 0.036621 | -0.09613 | 0.073242 | -0.059509 | 0.25177 | 122.4106 | 0.050354 | 122.3785 | 122.3145 | 122.2046 | 122.1909 | 122.168 | -122.3923 | -122.3053 | 122.287 | 122.3419 | 59.1064 | 59.1202
937.3125 | 122.612 | -59.1064 | 63.1439 | -0.073471 | 0.0019802 | 0.063803 | 0.058099 | 0.0026916 | -0.0046698 | 0.00098694 | -0.042725 | 0.00077755 | 0.06438 | 0.061566 | -0.00505 | 0.01072 | -0.0065134 | 0.032043 | 63.0753 | -59.2346 | 63.2217 | -58.9325 | -59.3399 | -59.3216 | 0.073242 | 63.0295 | -59.1431 | 63.2355 | -59.0927 | -59.198 | -59.111 | -0.12817 | -0.068665 | 0.07782 | 0.17395 | -0.21515 | -0.23346 | -0.086975 | -0.10529 | -0.036621 | -0.11444 | 0.091553 | 0.013733 | -0.004578 | -0.091553 | 0.032043 | -0.054932 | 0.30212 | 122.4564 | 0.050354 | 122.3785 | 122.3099 | 122.1725 | 122.1817 | 122.1359 | -122.3785 | -122.287 | 122.3282 | 122.3419 | 59.1385 | 59.1797
938.3125 | 122.5616 | -59.1751 | 63.1073 | -0.11925 | 0.0017666 | 0.062094 | 0.060449 | -0.0024354 | -0.005097 | -0.0039265 | -0.033569 | 0.0012047 | 0.06502 | 0.057935 | -0.0063318 | 0.0083697 | -0.0020272 | -0.07782 | 62.9929 | -59.285 | 63.1302 | -59.024 | -59.4223 | -59.3765 | -0.086975 | 63.0066 | -59.1934 | 63.1714 | -59.1751 | -59.285 | -59.1568 | -0.10986 | -0.11444 | 0.022888 | 0.15106 | -0.20142 | -0.24719 | -0.091553 | -0.13733 | -0.01831 | -0.10071 | 0.064087 | 0 | 0.018311 | -0.10986 | 0.036621 | -0.091553 | 0.26093 | 122.4152 | 0.01831 | 122.3648 | 122.2778 | 122.2 | 122.168 | 122.1817 | -122.3923 | -122.3007 | 122.3053 | 122.3465 | 59.0973 | 59.0881
939.3125 | 122.5525 | -59.1614 | 63.1119 | -0.12688 | 0.0051846 | 0.063589 | 0.058526 | 0.00076902 | -0.0044562 | -0.0013629 | -0.024414 | 0.0022729 | 0.06502 | 0.061139 | -0.0065454 | 0.011574 | -0.0039498 | -0.050354 | 63.0203 | -59.2758 | 63.1393 | -59.0103 | -59.4223 | -59.3719 | -0.068665 | 63.002 | -59.1843 | 63.176 | -59.1797 | -59.2712 | -59.1705 | -0.11444 | -0.091552 | 0.027466 | 0.15106 | -0.21057 | -0.26093 | -0.09613 | -0.14648 | -0.022888 | -0.10986 | 0.064087 | -0.01831 | -0.009155 | -0.10986 | 0.013733 | -0.086975 | 0.2655 | 122.4152 | 0.004578 | 122.3602 | 122.2961 | 122.1863 | 122.1817 | 122.1634 | -122.3877 | -122.2961 | 122.3007 | 122.3373 | 59.111 | 59.0927
940.3125 | 122.5159 | -59.1385 | 63.1302 | -0.10399 | 0.0019802 | 0.064016 | 0.05874 | -0.0030762 | -0.0042426 | -0.0026447 | -0.0030517 | 0.0016321 | 0.066302 | 0.056226 | -0.0080408 | 0.0079425 | 0.000109 | -0.086975 | 63.0386 | -59.2621 | 63.1393 | -59.024 | -59.4223 | -59.3765 | -0.086975 | 63.0066 | -59.166 | 63.0981 | -59.2163 | -59.2712 | -59.166 | -0.1236 | -0.091553 | 0.009155 | 0.11444 | -0.23804 | -0.28381 | -0.11444 | -0.16022 | -0.027466 | -0.1236 | -0.032043 | -0.07782 | -0.027466 | -0.13275 | 0 | -0.10529 | 0.23804 | 122.4014 | -0.050354 | 122.2641 | 122.3007 | 122.1725 | 122.1771 | 122.1451 | -122.3923 | -122.2961 | 122.2778 | 122.2366 | 59.0515 | 59.0515
941.3125 | 122.5754 | -59.1431 | 63.1256 | -0.096359 | 0.0030484 | 0.06658 | 0.06109 | -0.00029898 | -0.00232 | -8.1264e-05 | -0.027466 | 0.0012047 | 0.065234 | 0.061139 | -0.0078272 | 0.010292 | -0.005018 | -0.091553 | 63.0524 | -59.2484 | 63.1256 | -59.0286 | -59.4269 | -59.3719 | -0.068665 | 63.0249 | -59.1843 | 63.1851 | -59.1385 | -59.2758 | -59.1522 | -0.10529 | -0.073242 | 0 | 0.11444 | -0.22888 | -0.28381 | -0.1236 | -0.17853 | -0.041199 | -0.10071 | 0.05951 | 0.004577 | -0.009156 | -0.13275 | 0.032043 | -0.091553 | 0.21973 | 122.374 | 0.045776 | 122.3694 | 122.3007 | 122.2092 | 122.1954 | 122.168 | -122.374 | -122.3099 | 122.2687 | 122.3282 | 59.0515 | 59.0744
942.3125 | 122.5296 | -59.1476 | 63.1577 | -0.058212 | 0.0041166 | 0.063803 | 0.059595 | 0.00012822 | -0.0027472 | -0.0022175 | -0.024414 | 0.0018457 | 0.067157 | 0.064984 | -0.005691 | 0.010506 | -0.0011728 | 0.022888 | 63.0798 | -59.2438 | 63.2126 | -58.96 | -59.3399 | -59.3308 | 0.054932 | 63.0615 | -59.1385 | 63.1943 | -59.1339 | -59.2438 | -59.1293 | -0.09613 | -0.07782 | 0.054931 | 0.18768 | -0.18311 | -0.19226 | -0.086976 | -0.096131 | 0.009155 | -0.096131 | 0.036621 | 0.013733 | 0.018311 | -0.09613 | 0.009156 | -0.10529 | 0.28381 | 122.4564 | 0.004578 | 122.3328 | 122.3236 | 122.2 | 122.2275 | 122.2092 | -122.4014 | -122.2961 | 122.3602 | 122.3419 | 59.1705 | 59.2026
943.3125 | 122.5754 | -59.1614 | 63.1165 | 0.010452 | 0.0028348 | 0.064016 | 0.059808 | 0.00012822 | -0.0038154 | -0.0024311 | -0.030517 | 0.0029137 | 0.068225 | 0.057507 | -0.0063318 | 0.0087969 | -0.0020272 | -0.054932 | 63.0341 | -59.2621 | 63.1393 | -58.9783 | -59.4131 | -59.3674 | -0.054932 | 62.9974 | -59.1934 | 63.1897 | -59.1476 | -59.2804 | -59.1522 | -0.10071 | -0.082397 | 0.022888 | 0.18311 | -0.20599 | -0.25177 | -0.10529 | -0.15106 | -0.032043 | -0.11902 | 0.073242 | 0.013733 | 0.009155 | -0.11902 | 0.041198 | -0.086976 | 0.28381 | 122.4014 | 0.045776 | 122.3831 | 122.2961 | 122.1909 | 122.1954 | 122.1588 | -122.3785 | -122.3099 | 122.3007 | 122.3511 | 59.1064 | 59.1064
944.3125 | 122.5525 | -59.1797 | 63.1348 | -0.050583 | 0.004971 | 0.06188 | 0.057458 | -0.002649 | -0.0021064 | -0.00029486 | -0.012207 | -7.6854e-05 | 0.065234 | 0.066907 | -0.005691 | 0.0085833 | -0.0003182 | -0.086975 | 63.0478 | -59.2667 | 63.1393 | -59.024 | -59.3994 | -59.3674 | -0.09613 | 63.0478 | -59.1705 | 63.089 | -59.2072 | -59.2529 | -59.1614 | -0.086976 | -0.086975 | 0.004577 | 0.15564 | -0.18768 | -0.21973 | -0.10071 | -0.13275 | 0.009155 | -0.086975 | -0.045777 | -0.027466 | 0.01831 | -0.073243 | 0.009155 | -0.082398 | 0.24262 | 122.406 | -0.036621 | 122.2595 | 122.3145 | 122.2183 | 122.2275 | 122.2275 | -122.4014 | -122.3053 | 122.319 | 122.2687 | 59.0927 | 59.0836
945.3125 | 122.5662 | -59.1476 | 63.1577 | -0.096359 | 0.0024076 | 0.063162 | 0.059808 | -0.0030762 | -0.0044562 | -0.0017903 | -0.0091553 | 0.0031273 | 0.065875 | 0.059216 | -0.0069726 | 0.010506 | 0.0009634 | -0.10071 | 63.0524 | -59.2712 | 63.1439 | -59.0149 | -59.4177 | -59.3674 | -0.091553 | 63.0157 | -59.1751 | 63.1805 | -59.1705 | -59.2712 | -59.1431 | -0.1236 | -0.10529 | -0.013733 | 0.13275 | -0.21973 | -0.27008 | -0.096131 | -0.14648 | -0.027466 | -0.14191 | 0.022888 | -0.022888 | 0.004578 | -0.1236 | 0.032044 | -0.09613 | 0.25635 | 122.4152 | 0.004578 | 122.3557 | 122.3236 | 122.1909 | 122.2 | 122.1634 | -122.4289 | -122.3328 | 122.2916 | 122.3282 | 59.0469 | 59.0561
946.3125 | 122.5845 | -59.1202 | 63.1531 | -0.012436 | 0.0036892 | 0.063803 | 0.059381 | -0.0039306 | -0.0029608 | -0.0017903 | -0.015259 | 0.0012047 | 0.066089 | 0.062848 | -0.005691 | 0.0096515 | -0.0035226 | -0.07782 | 63.0386 | -59.2438 | 63.1439 | -59.0149 | -59.4086 | -59.3719 | -0.082397 | 63.0112 | -59.1888 | 63.1897 | -59.1522 | -59.2712 | -59.1339 | -0.1236 | -0.11444 | -0.009155 | 0.10529 | -0.25177 | -0.28839 | -0.12817 | -0.16479 | -0.068665 | -0.14191 | 0.036621 | -0.032044 | -0.013733 | -0.15106 | 0.054932 | -0.082397 | 0.22888 | 122.3877 | 0.036621 | 122.3785 | 122.2824 | 122.2 | 122.1588 | 122.1313 | -122.3969 | -122.3419 | 122.2641 | 122.3099 | 59.0424 | 59.0378
947.3125 | 122.6212 | -59.111 | 63.1439 | 0.15541 | 0.0030484 | 0.065725 | 0.059381 | -0.00093998 | -0.0027472 | -0.00050846 | 0.0030517 | 0.00077755 | 0.063952 | 0.06477 | -0.0063318 | 0.0081561 | -0.0026682 | -0.13275 | 63.1027 | -59.2255 | 63.2584 | -58.8913 | -59.3445 | -59.2804 | 0.091553 | 63.0432 | -59.1293 | 63.2629 | -59.0607 | -59.166 | -59.0698 | -0.11444 | -0.041199 | 0.11444 | 0.21973 | -0.16937 | -0.23346 | -0.054932 | -0.11902 | -0.01831 | -0.10071 | 0.11902 | 0.050354 | 0.041199 | -0.054932 | 0.059509 | -0.036622 | 0.33417 | 122.4838 | 0.068664 | 122.3923 | 122.3282 | 122.1725 | 122.2137 | 122.1542 | -122.3694 | -122.2733 | 122.3694 | 122.374 | 58.9783 | 59.2026
948.3125 | 122.5708 | -59.1385 | 63.1073 | -0.058212 | 0.0026212 | 0.062094 | 0.059167 | -0.00072638 | -0.0014654 | -8.1264e-05 | -0.057983 | 0.0016321 | 0.066943 | 0.06413 | -0.0052638 | 0.010506 | -0.0009592 | -0.059509 | 63.0432 | -59.2621 | 63.1668 | -58.9737 | -59.4086 | -59.3536 | -0.064087 | 63.0203 | -59.166 | 63.1805 | -59.1568 | -59.2667 | -59.1476 | -0.1236 | -0.064087 | 0.059509 | 0.16479 | -0.21515 | -0.27008 | -0.091553 | -0.14648 | -0.027466 | -0.086975 | 0.073242 | -0.01831 | -0.009155 | -0.12817 | 0.018311 | -0.10071 | 0.28839 | 122.4289 | 0.009156 | 122.3465 | 122.3053 | 122.1863 | 122.1817 | 122.1588 | -122.3694 | -122.2733 | 122.3053 | 122.319 | 59.079 | 59.0744
949.3125 | 122.5616 | -59.1385 | 63.1119 | -0.11925 | 0.003262 | 0.063803 | 0.059595 | 0.0018372 | -0.0025336 | -0.0030719 | 0.0030517 | 0.0012047 | 0.066302 | 0.056653 | -0.006759 | 0.011147 | -0.0011728 | -0.091553 | 63.0478 | -59.2758 | 63.1485 | -59.024 | -59.3857 | -59.3582 | -0.068665 | 63.0341 | -59.1614 | 63.1348 | -59.1293 | -59.2621 | -59.1705 | -0.13733 | -0.064086 | 0.036622 | 0.11444 | -0.21973 | -0.24719 | -0.082397 | -0.10986 | -0.022888 | -0.077819 | 0.022889 | 0.009156 | -0.032043 | -0.1236 | -0.009155 | -0.10071 | 0.25177 | 122.4243 | 0.032044 | 122.2961 | 122.3236 | 122.1954 | 122.1863 | 122.1725 | -122.3877 | -122.2733 | 122.287 | 122.2733 | 59.0469 | 59.0698
950.3125 | 122.5433 | -59.1339 | 63.121 | -0.10399 | 0.0039028 | 0.064657 | 0.057886 | 0.00098262 | -0.0018928 | -0.00093566 | -0.012207 | 0.0018457 | 0.066729 | 0.060712 | -0.0063318 | 0.0098651 | -0.0052316 | -0.07782 | 63.0661 | -59.2484 | 63.1622 | -59.0195 | -59.3948 | -59.3674 | -0.082397 | 63.0386 | -59.1614 | 63.1943 | -58.9645 | -59.2941 | -59.2392 | -0.11444 | -0.054932 | 0.041198 | 0.11444 | -0.23346 | -0.26093 | -0.11902 | -0.14648 | -0.027466 | -0.082398 | 0.073242 | 0.16937 | -0.10529 | -0.16022 | -0.07782 | -0.13275 | 0.22888 | 122.4106 | 0.19684 | 122.3557 | 122.3145 | 122.2 | 122.2 | 122.1725 | -122.3694 | -122.2824 | 122.2961 | 122.3282 | 59.0561 | 59.0515
951.3125 | 122.5616 | -59.1431 | 63.1668 | -0.073471 | 0.0045438 | 0.062521 | 0.060663 | -0.00072638 | -0.0036018 | 0.00098694 | -0.036621 | 0.0014185 | 0.064593 | 0.063489 | -0.0063318 | 0.01072 | -0.0035226 | -0.091553 | 63.0615 | -59.2163 | 63.1485 | -59.0103 | -59.4131 | -59.3628 | -0.10986 | 63.0249 | -59.166 | 63.1989 | -59.1476 | -59.2667 | -59.1248 | -0.073243 | -0.10529 | -0.01831 | 0.13275 | -0.21973 | -0.27008 | -0.14648 | -0.19684 | -0.022889 | -0.14191 | 0.032044 | -0.004578 | 0.01831 | -0.1236 | 0.041199 | -0.10071 | 0.20599 | 122.3648 | 0.018311 | 122.3648 | 122.2778 | 122.1909 | 122.2046 | 122.168 | -122.3831 | -122.3328 | 122.2916 | 122.3419 | 59.0515 | 59.0332
952.3125 | 122.4884 | -59.1568 | 63.2309 | -0.035324 | 0.0036892 | 0.061239 | 0.058954 | 0.0020508 | -0.0029608 | -0.00093566 | -0.073242 | 0.0039819 | 0.06737 | 0.059644 | -0.00505 | 0.012215 | -0.0039498 | -0.018311 | 63.1348 | -59.2346 | 63.121 | -59.0149 | -59.4086 | -59.3811 | -0.050354 | 63.0981 | -59.1385 | 63.1485 | -59.1202 | -59.3262 | -59.1797 | -0.07782 | -0.09613 | -0.10986 | 0.14191 | -0.22431 | -0.25177 | -0.14648 | -0.17395 | 0.01831 | -0.13275 | -0.082397 | 0.036621 | -0.022888 | -0.16937 | -0.041198 | -0.18768 | 0.21973 | 122.3557 | 0.018311 | 122.287 | 122.3694 | 122.2366 | 122.2916 | 122.2549 | -122.4655 | -122.3694 | 122.2778 | 122.3053 | 59.1385 | 59.1064
953.3125 | 122.58 | -59.1293 | 63.121 | -0.096359 | 0.0039028 | 0.064657 | 0.063226 | -0.00072638 | -0.00232 | -0.0032855 | -8.6e-08 | -0.00050405 | 0.065661 | 0.068188 | -0.006759 | 0.01072 | -0.0037362 | -0.036621 | 63.0386 | -59.2163 | 63.208 | -58.9554 | -59.5139 | -59.5551 | 0.086975 | 63.0341 | -59.1476 | 63.2355 | -59.0927 | -59.2392 | -59.0881 | -0.086976 | -0.082398 | 0.086975 | 0.17395 | -0.42572 | -0.38452 | -0.33874 | -0.29755 | -0.018311 | -0.086975 | 0.11444 | 0.036621 | 0.041198 | -0.10986 | 0.059509 | -0.091553 | 0.26093 | 122.4243 | 0.054932 | 122.3831 | 122.2549 | 122.1817 | 122.168 | 122.1634 | -122.3373 | -122.2687 | 122.3373 | 122.3648 | 59.0927 | 59.2163
954.3125 | 122.5479 | -59.1385 | 63.1439 | -0.11162 | 0.0019802 | 0.064657 | 0.060022 | 0.00076902 | -0.0021064 | 0.0014141 | -0.024414 | 0.0016321 | 0.065234 | 0.059857 | -0.0048364 | 0.0068743 | -0.0007456 | -0.059509 | 63.0386 | -59.23 | 63.176 | -58.9874 | -59.4086 | -59.3582 | -0.068665 | 63.0386 | -59.166 | 63.1989 | -59.1568 | -59.2667 | -59.1293 | -0.091553 | -0.10529 | 0.032043 | 0.15106 | -0.21973 | -0.27008 | -0.12817 | -0.17853 | -0.027466 | -0.10529 | 0.054932 | -0.01831 | 0.009156 | -0.12817 | 0.036622 | -0.10071 | 0.24262 | 122.406 | 0.009156 | 122.3648 | 122.2687 | 122.2046 | 122.1771 | 122.1771 | -122.374 | -122.3099 | 122.3145 | 122.3373 | 59.079 | 59.0698
955.3125 | 122.5388 | -59.1385 | 63.1256 | -0.08873 | 0.0024076 | 0.064871 | 0.058099 | -0.0028626 | -0.003388 | 0.0022687 | 0.12207 | 0.0031273 | 0.069079 | 0.060284 | -0.0061182 | 0.0092241 | -0.0011728 | -0.09613 | 63.0569 | -59.2255 | 63.1622 | -58.9874 | -59.3765 | -59.3491 | -0.2243 | 63.0936 | -59.1293 | 63.1851 | -59.1751 | -59.2529 | -59.1339 | -0.086975 | -0.068664 | 0.036621 | 0.15106 | -0.21057 | -0.23804 | -0.1236 | -0.15106 | 0.009156 | -0.032043 | 0.05951 | -0.036621 | 0.004578 | -0.11444 | -0.004578 | -0.1236 | 0.23804 | 122.3877 | -0.045777 | 122.3145 | 122.2824 | 122.2229 | 122.1954 | 122.2321 | -122.3511 | -122.2549 | 122.3007 | 122.3236 | 59.0424 | 58.9142
956.3125 | 122.5571 | -59.1385 | 63.1302 | -0.10399 | 0.003262 | 0.063162 | 0.059808 | 0.00098262 | -0.0010382 | -0.00072206 | -0.01831 | 0.0039819 | 0.06502 | 0.063916 | -0.0048364 | 0.0094379 | -0.0001046 | -0.10986 | 63.089 | -59.2209 | 63.176 | -58.9828 | -59.3811 | -59.3491 | -0.082397 | 63.0524 | -59.1156 | 63.208 | -59.1522 | -59.2621 | -59.1339 | -0.082397 | -0.041199 | 0.045776 | 0.15564 | -0.21057 | -0.24262 | -0.12817 | -0.16022 | 0.022888 | -0.07782 | 0.07782 | -0.013733 | 0.004578 | -0.1236 | -0.01831 | -0.14648 | 0.23804 | 122.3969 | -0.036621 | 122.3236 | 122.3099 | 122.168 | 122.2275 | 122.1909 | -122.3511 | -122.2458 | 122.3145 | 122.3465 | 59.0286 | 59.0561
957.3125 | 122.5433 | -59.1431 | 63.1348 | -0.065842 | 0.0045438 | 0.062521 | 0.05874 | 0.0026916 | -0.0021064 | -8.1264e-05 | -0.01831 | 0.0020593 | 0.063739 | 0.061566 | -0.0074 | 0.0096515 | -0.0030954 | -0.073242 | 63.0524 | -59.2209 | 63.1943 | -58.96 | -59.3765 | -59.3079 | -0.036621 | 63.0203 | -59.1202 | 63.2217 | -59.1385 | -59.2575 | -59.111 | -0.07782 | -0.082398 | 0.059509 | 0.1831 | -0.1648 | -0.23346 | -0.086975 | -0.15564 | 0.022888 | -0.11444 | 0.086975 | 0.004577 | 0.032043 | -0.11444 | 0.009155 | -0.13733 | 0.26093 | 122.4152 | -0.018311 | 122.3419 | 122.2733 | 122.1405 | 122.1954 | 122.1634 | -122.3557 | -122.2549 | 122.3373 | 122.3648 | 59.0698 | 59.1064
958.3125 | 122.493 | -59.1385 | 63.1805 | -0.073471 | 0.0013394 | 0.063589 | 0.059167 | -0.0028626 | -0.0016792 | -0.0020039 | -0.033569 | 0.00035035 | 0.066089 | 0.05943 | -0.0071864 | 0.0077289 | -0.0041636 | -0.091553 | 63.0569 | -59.2392 | 63.1668 | -58.992 | -59.404 | -59.3399 | -0.086975 | 63.0341 | -59.1248 | 63.1943 | -59.1339 | -59.2438 | -59.1202 | -0.10071 | -0.1236 | -0.013733 | 0.14648 | -0.20142 | -0.2655 | -0.10071 | -0.1648 | 0.013733 | -0.14648 | 0.013733 | 0.004578 | 0.018311 | -0.10529 | 0.004578 | -0.11902 | 0.24719 | 122.406 | -0.009155 | 122.319 | 122.2961 | 122.1588 | 122.1954 | 122.1725 | -122.4197 | -122.3053 | 122.3053 | 122.3328 | 59.0469 | 59.0515
959.3125 | 122.5479 | -59.1156 | 63.1393 | -0.058212 | 0.004971 | 0.062521 | 0.060022 | -0.003717 | -0.0027472 | -0.00029486 | -0.0061035 | 0.0020593 | 0.065448 | 0.057721 | -0.006759 | 0.0092241 | -0.0009592 | -0.10071 | 63.0798 | -59.2346 | 63.1577 | -58.9828 | -59.3994 | -59.3353 | -0.091553 | 63.0386 | -59.1431 | 63.2126 | -59.1385 | -59.2346 | -59.1202 | -0.11902 | -0.059509 | 0.018311 | 0.13275 | -0.21973 | -0.28381 | -0.10071 | -0.16479 | -0.027465 | -0.10071 | 0.073242 | -0.022888 | -0.004577 | -0.11902 | 0.022888 | -0.091553 | 0.25177 | 122.3923 | 0.004577 | 122.3557 | 122.3145 | 122.1817 | 122.1954 | 122.1542 | -122.374 | -122.2824 | 122.2733 | 122.3282 | 59.0149 | 59.024
960.3125 | 122.6074 | -59.1156 | 63.1439 | -0.073471 | 0.0041166 | 0.063376 | 0.060235 | -0.0024354 | -0.00232 | -0.0022175 | -0.057983 | 0.0022729 | 0.067798 | 0.062848 | -0.0086816 | 0.0096515 | -0.0003182 | -0.068665 | 63.0524 | -59.2255 | 63.2126 | -58.9371 | -59.3582 | -59.3124 | -0.036621 | 63.0386 | -59.1522 | 63.2538 | -59.1064 | -59.23 | -59.0698 | -0.10986 | -0.091553 | 0.068664 | 0.17853 | -0.19684 | -0.24261 | -0.086975 | -0.13275 | -0.036621 | -0.10529 | 0.10986 | 0.009156 | 0.045777 | -0.11444 | 0.082398 | -0.07782 | 0.28839 | 122.438 | 0.045777 | 122.406 | 122.2778 | 122.1909 | 122.168 | 122.1542 | -122.3694 | -122.2961 | 122.3282 | 122.3694 | 59.0469 | 59.079
961.3125 | 122.5388 | -59.1431 | 63.1348 | -0.096359 | 0.0006986 | 0.064444 | 0.060022 | 0.0039734 | -0.004029 | -0.0028583 | -0.039673 | 0.0016321 | 0.064593 | 0.057935 | -0.0071864 | 0.01072 | -0.0026682 | -0.09613 | 63.0753 | -59.2346 | 63.176 | -58.9691 | -59.3811 | -59.3399 | -0.086975 | 63.0432 | -59.1431 | 63.2309 | -59.1339 | -59.2392 | -59.111 | -0.091553 | -0.05951 | 0.041198 | 0.17395 | -0.19684 | -0.23804 | -0.10529 | -0.14648 | 0 | -0.091553 | 0.09613 | 0.009155 | 0.032043 | -0.096131 | 0.032043 | -0.096131 | 0.2655 | 122.4106 | 0.009155 | 122.374 | 122.3099 | 122.1863 | 122.2183 | 122.1863 | -122.3694 | -122.2778 | 122.319 | 122.374 | 59.0469 | 59.0561
962.3125 | 122.58 | -59.1019 | 63.1714 | -0.081101 | 0.0030484 | 0.064016 | 0.05874 | -0.0011536 | -0.0025336 | -0.0039265 | -0.015259 | 0.00035035 | 0.067157 | 0.059644 | -0.0063318 | 0.0092241 | -0.0003182 | -0.073242 | 63.1165 | -59.2026 | 63.1897 | -58.96 | -59.3628 | -59.3216 | -0.045776 | 63.0432 | -59.1339 | 63.2492 | -59.0881 | -59.198 | -59.0836 | -0.10071 | -0.054932 | 0.01831 | 0.14191 | -0.21973 | -0.26093 | -0.11902 | -0.16022 | -0.032043 | -0.12817 | 0.07782 | 0.013733 | 0.018311 | -0.09613 | 0.050354 | -0.064087 | 0.24262 | 122.3923 | 0.045776 | 122.3831 | 122.319 | 122.1771 | 122.2183 | 122.1451 | -122.374 | -122.3053 | 122.2916 | 122.3511 | 59.0286 | 59.0561
963.3125 | 122.5845 | -59.1248 | 63.1485 | -0.11925 | 0.0030484 | 0.063162 | 0.059167 | -0.00072638 | -0.0018928 | 0.00077334 | -0.033569 | 0.0029137 | 0.066089 | 0.065411 | -0.0054774 | 0.0094379 | -0.0060862 | -0.091553 | 63.0707 | -59.2255 | 63.1943 | -58.9279 | -59.3719 | -59.3216 | -0.032043 | 63.0295 | -59.1293 | 63.2126 | -59.1385 | -59.2438 | -59.1064 | -0.10071 | -0.07782 | 0.045776 | 0.19684 | -0.19684 | -0.24719 | -0.09613 | -0.14648 | -0.004577 | -0.11902 | 0.064086 | -0.013733 | 0.018311 | -0.11902 | 0.022888 | -0.11444 | 0.29755 | 122.4197 | -0.009156 | 122.3419 | 122.2961 | 122.1588 | 122.1954 | 122.1542 | -122.374 | -122.2778 | 122.319 | 122.3373 | 59.0332 | 59.0927
964.3125 | 122.5616 | -59.0744 | 63.1302 | -0.11925 | 0.003262 | 0.062094 | 0.061731 | 0.00076902 | -0.00232 | -0.0022175 | -0.0030517 | 0.0014185 | 0.066516 | 0.058148 | -0.0086816 | 0.0060199 | -0.0048044 | -0.11902 | 63.1119 | -59.2209 | 63.1897 | -58.9783 | -59.3719 | -59.317 | -0.073242 | 63.0569 | -59.1339 | 63.2858 | -59.2484 | -59.2438 | -59.0881 | -0.14648 | -0.018311 | 0.059509 | 0.096131 | -0.24262 | -0.29755 | -0.096131 | -0.15106 | -0.059509 | -0.073242 | 0.15564 | -0.17395 | -0.013733 | -0.16937 | 0.045776 | -0.10986 | 0.24262 | 122.4106 | -0.11444 | 122.4197 | 122.3328 | 122.1909 | 122.1863 | 122.1313 | -122.3511 | -122.2641 | 122.2641 | 122.3602 | 58.9554 | 59.0012
965.3125 | 122.525 | -59.1202 | 63.1714 | -0.11925 | 0.0039028 | 0.064657 | 0.058526 | -0.0011536 | -0.0027472 | -0.0013629 | -0.027466 | 0.0022729 | 0.06737 | 0.062207 | -0.0048364 | 0.0083697 | -0.0003182 | -0.12817 | 63.089 | -59.2026 | 63.1714 | -58.9508 | -59.3628 | -59.3216 | -0.07782 | 63.0661 | -59.1431 | 63.1943 | -58.9005 | -59.1476 | -59.1751 | -0.082398 | -0.082398 | 0 | 0.16937 | -0.20142 | -0.24262 | -0.11902 | -0.16022 | -0.022888 | -0.10529 | 0.022888 | 0.21973 | -0.054932 | -0.027466 | -0.032044 | -0.004578 | 0.25177 | 122.374 | 0.24261 | 122.3373 | 122.2916 | 122.2092 | 122.2092 | 122.1863 | -122.374 | -122.3145 | 122.2916 | 122.3145 | 58.992 | 59.0424
966.3125 | 122.6212 | -59.0973 | 63.1531 | -0.065842 | 0.0026212 | 0.063376 | 0.060022 | 0.0014098 | -0.0044562 | -0.00072206 | -0.01831 | 0.00077755 | 0.065234 | 0.060925 | -0.0063318 | 0.0081561 | -0.0011728 | -0.14648 | 63.0981 | -59.23 | 63.1714 | -58.9783 | -59.3582 | -59.3216 | -0.082397 | 63.0661 | -59.1293 | 63.2309 | -59.111 | -59.0744 | -58.9233 | -0.13275 | -0.054931 | 0.018311 | 0.11902 | -0.2243 | -0.26093 | -0.091552 | -0.12817 | -0.032043 | -0.086975 | 0.07782 | -0.013733 | 0.17395 | 0.022888 | 0.20599 | 0.054931 | 0.25177 | 122.4014 | 0.01831 | 122.3602 | 122.3282 | 122.1954 | 122.1954 | 122.1634 | -122.3831 | -122.2824 | 122.2687 | 122.3282 | 58.9508 | 59.0149
967.3125 | 122.6074 | -59.0607 | 63.1805 | -0.035324 | 0.0024076 | 0.062948 | 0.059381 | -0.0028626 | -0.0025336 | -0.00029486 | 0.0030517 | 0.0020593 | 0.064807 | 0.063702 | -0.0082544 | 0.011361 | -0.0062998 | -0.018311 | 63.1073 | -59.198 | 63.2904 | -58.873 | -59.2621 | -59.2484 | 0.07782 | 63.0707 | -59.0927 | 63.2858 | -59.0286 | -59.1522 | -59.0424 | -0.13733 | -0.073242 | 0.10986 | 0.18768 | -0.18768 | -0.20142 | -0.050354 | -0.064087 | -0.032043 | -0.10986 | 0.10529 | 0.032044 | 0.018311 | -0.091553 | 0.050354 | -0.05951 | 0.32501 | 122.4884 | 0.064087 | 122.3785 | 122.3053 | 122.1634 | 122.168 | 122.1313 | -122.3785 | -122.2733 | 122.3511 | 122.3465 | 59.0424 | 59.1385
968.3125 | 122.6624 | -59.0881 | 63.1943 | -0.08873 | 0.0028348 | 0.063803 | 0.059381 | -0.0032898 | -0.0048834 | -0.0020039 | -0.021362 | 0.0018457 | 0.066729 | 0.05943 | -0.008468 | 0.01371 | -0.0022408 | -0.14191 | 63.0844 | -59.2117 | 63.1897 | -58.9554 | -59.3536 | -59.3262 | -0.082397 | 63.0478 | -59.1385 | 63.2309 | -59.1019 | -59.1934 | -58.9508 | -0.1236 | -0.10986 | -0.004578 | 0.13275 | -0.23804 | -0.2655 | -0.11444 | -0.14191 | -0.050354 | -0.14648 | 0.036621 | -0.013733 | 0.13733 | -0.10529 | 0.18768 | -0.054931 | 0.25635 | 122.4014 | 0.036621 | 122.3694 | 122.2961 | 122.1863 | 122.1725 | 122.1359 | -122.406 | -122.3328 | 122.2778 | 122.319 | 58.9462 | 59.0057
969.3125 | 122.5525 | -59.0881 | 63.1989 | -0.042954 | 0.0036892 | 0.061026 | 0.058313 | -0.0035034 | -0.0044562 | -0.0045673 | -8.6e-08 | 0.00077755 | 0.066943 | 0.066479 | -0.0078272 | 0.0094379 | -0.0026682 | -0.16022 | 63.1302 | -59.2026 | 63.1897 | -58.9508 | -59.3445 | -59.3124 | -0.059509 | 63.0707 | -59.1202 | 63.2309 | -59.0744 | -59.198 | -59.0698 | -0.11444 | -0.068665 | -0.009156 | 0.13733 | -0.2243 | -0.25635 | -0.10986 | -0.14191 | -0.032043 | -0.12817 | 0.032043 | 0.013733 | 0.018311 | -0.10986 | 0.050354 | -0.07782 | 0.25177 | 122.3923 | 0.045776 | 122.3511 | 122.3328 | 122.1909 | 122.2183 | 122.1588 | -122.4014 | -122.319 | 122.2778 | 122.319 | 58.9279 | 59.0286
970.3125 | 122.612 | -59.0607 | 63.1851 | -0.065842 | 0.0026212 | 0.063376 | 0.058099 | -0.0013672 | -0.0016792 | -0.0030719 | 0.0030517 | 0.0027001 | 0.063739 | 0.056866 | -0.0054774 | 0.0087969 | -0.0052316 | -0.064087 | 63.1256 | -59.1705 | 63.2904 | -58.8272 | -59.2346 | -59.2209 | 0.1236 | 63.0798 | -59.0515 | 63.3041 | -58.96 | -59.1614 | -59.0515 | -0.10986 | -0.05951 | 0.10529 | 0.23346 | -0.16022 | -0.17395 | -0.050354 | -0.064087 | 0.009155 | -0.10529 | 0.11902 | 0.10071 | 0.009155 | -0.10071 | 0 | -0.10986 | 0.34332 | 122.4609 | 0.091553 | 122.3557 | 122.2961 | 122.1313 | 122.1863 | 122.1405 | -122.3557 | -122.2366 | 122.3511 | 122.3648 | 58.9966 | 59.1843
971.3125 | 122.5525 | -59.0744 | 63.2034 | -0.050583 | 0.0034756 | 0.063162 | 0.060235 | 0.0020508 | -0.003388 | -0.0037129 | -0.021362 | 0.00077755 | 0.063952 | 0.057507 | -0.006759 | 0.010292 | -0.0030954 | -0.17395 | 63.0844 | -59.2072 | 63.2034 | -58.9554 | -59.3674 | -59.2941 | -0.082397 | 63.0936 | -59.111 | 63.2401 | -59.0836 | -58.9874 | -58.873 | -0.13275 | -0.11902 | 0 | 0.11902 | -0.21973 | -0.29297 | -0.086975 | -0.16022 | -0.036621 | -0.10986 | 0.036621 | -0.009155 | 0.20142 | 0.086975 | 0.23804 | 0.1236 | 0.25177 | 122.4106 | 0.027466 | 122.3511 | 122.2916 | 122.2046 | 122.1588 | 122.168 | -122.4106 | -122.3145 | 122.2778 | 122.3145 | 58.9005 | 58.992
972.3125 | 122.5983 | -59.0607 | 63.2217 | -0.13451 | 0.003262 | 0.061667 | 0.060235 | -0.00072638 | -0.0016792 | -0.0017903 | -0.021362 | 0.0018457 | 0.067798 | 0.059644 | -0.0063318 | 0.01072 | -0.0028818 | -0.068665 | 63.1256 | -59.1705 | 63.3041 | -58.8364 | -59.2346 | -59.2209 | 0.068665 | 63.1073 | -59.0515 | 63.295 | -59.0149 | -59.1248 | -59.024 | -0.10986 | -0.096131 | 0.082397 | 0.2243 | -0.16022 | -0.17395 | -0.050354 | -0.064087 | 0.009155 | -0.11444 | 0.073242 | 0.045776 | 0.036621 | -0.064087 | 0.027466 | -0.073242 | 0.33417 | 122.4747 | 0.036621 | 122.3465 | 122.2961 | 122.1588 | 122.1863 | 122.168 | -122.3923 | -122.2733 | 122.3648 | 122.3557 | 58.992 | 59.1293
973.3125 | 122.5479 | -59.0927 | 63.1714 | -0.11162 | 0.0019802 | 0.064444 | 0.058526 | 0.0011962 | -0.0021064 | 0.0012005 | -0.030517 | 0.00056395 | 0.065234 | 0.058148 | -0.0063318 | 0.010933 | -0.0009592 | -0.1831 | 63.1073 | -59.2026 | 63.2355 | -58.8913 | -59.3216 | -59.2896 | -0.032043 | 63.0844 | -59.1202 | 63.2629 | -59.0836 | -59.2117 | -59.0652 | -0.10986 | -0.064087 | 0.064087 | 0.20142 | -0.19684 | -0.22888 | -0.086975 | -0.11902 | -0.027466 | -0.086975 | 0.091552 | 0.009155 | 0.027465 | -0.11902 | 0.054931 | -0.091553 | 0.31128 | 122.4381 | 0.036621 | 122.3831 | 122.3099 | 122.2046 | 122.2 | 122.1771 | -122.374 | -122.2916 | 122.3282 | 122.3557 | 58.9096 | 59.0607
974.3125 | 122.5433 | -59.0744 | 63.1943 | -0.081101 | 0.0034756 | 0.063162 | 0.060022 | -0.0047852 | -0.0014654 | -0.0030719 | -0.0061035 | 0.0027001 | 0.06737 | 0.060712 | -0.0046228 | 0.010079 | -0.0016 | -0.19684 | 63.1256 | -59.198 | 63.2034 | -58.9371 | -59.3399 | -59.2896 | -0.073242 | 63.1027 | -59.0836 | 63.2538 | -59.0836 | -59.1843 | -59.0469 | -0.1236 | -0.068665 | 0.009155 | 0.13733 | -0.21515 | -0.2655 | -0.091553 | -0.14191 | -0.009155 | -0.091553 | 0.059509 | -0.009155 | 0.027466 | -0.10986 | 0.036621 | -0.10071 | 0.26093 | 122.4014 | 0 | 122.3373 | 122.3236 | 122.1863 | 122.2 | 122.1771 | -122.3923 | -122.2778 | 122.2778 | 122.3282 | 58.8776 | 59.0012
975.3125 | 122.5891 | -59.079 | 63.1989 | -0.081101 | 0.0024076 | 0.063803 | 0.058526 | 0.00034182 | -0.0016792 | -0.0020039 | -0.027466 | 0.0022729 | 0.065661 | 0.061352 | -0.003982 | 0.0064471 | -0.0018136 | -0.20142 | 63.1393 | -59.1797 | 63.2034 | -58.9279 | -59.3399 | -59.2896 | -0.054932 | 63.089 | -59.1019 | 63.2492 | -59.0744 | -59.1843 | -59.0652 | -0.10071 | -0.05951 | 0.004577 | 0.15106 | -0.21057 | -0.26093 | -0.10986 | -0.16022 | -0.022889 | -0.10986 | 0.050354 | 0.004577 | 0.013732 | -0.10529 | 0.036621 | -0.082397 | 0.25177 | 122.3831 | 0.027466 | 122.3511 | 122.319 | 122.1909 | 122.2183 | 122.168 | -122.3785 | -122.3007 | 122.2824 | 122.3282 | 58.8776 | 59.024
976.3125 | 122.6761 | -59.0515 | 63.208 | -0.042954 | 0.0043302 | 0.062735 | 0.057886 | -0.00093998 | -0.00082456 | 0.00034614 | -0.0061035 | 0.0024865 | 0.066943 | 0.06477 | -0.009109 | 0.0068743 | -0.0041636 | -0.17853 | 63.1485 | -59.166 | 63.3041 | -58.7997 | -59.2072 | -59.1888 | 0.10986 | 63.1073 | -59.0469 | 63.5559 | -59.2987 | -59.404 | -59.0927 | -0.11444 | -0.059509 | 0.09613 | 0.25177 | -0.13733 | -0.15564 | -0.022888 | -0.041198 | 0.004578 | -0.10071 | 0.3479 | -0.24719 | -0.041198 | -0.35248 | -0.045776 | -0.35706 | 0.36621 | 122.4701 | -0.25177 | 122.6028 | 122.3145 | 122.1542 | 122.2 | 122.1588 | -122.374 | -122.2549 | 122.3557 | 122.6074 | 58.873 | 59.1614
977.3125 | 122.5204 | -59.0652 | 63.2721 | -0.012436 | 0.0030484 | 0.060599 | 0.058313 | -0.0011536 | -0.00061096 | -0.00093566 | -0.030517 | 0.0029137 | 0.065448 | 0.065625 | -0.0076136 | 0.01072 | -0.0037362 | -0.15564 | 63.1531 | -59.1522 | 63.2675 | -58.8684 | -59.2758 | -59.2484 | 0.036621 | 63.1485 | -59.0652 | 63.2446 | -59.0607 | -59.1934 | -59.0744 | -0.086975 | -0.11902 | -0.004578 | 0.19684 | -0.1831 | -0.21057 | -0.09613 | -0.1236 | 0 | -0.1236 | -0.027466 | 0.004578 | -0.009155 | -0.12817 | -0.009155 | -0.12817 | 0.28381 | 122.4197 | 0.004578 | 122.3099 | 122.3053 | 122.2137 | 122.2183 | 122.2137 | -122.4243 | -122.3373 | 122.3328 | 122.3099 | 58.9096 | 59.1019
978.3125 | 122.5754 | -59.0652 | 63.2217 | -0.042954 | -0.0007968 | 0.065512 | 0.059167 | 0.004187 | -0.0048834 | -0.00093566 | -0.0061035 | 0.0014185 | 0.067798 | 0.059003 | -0.0044092 | 0.0098651 | 0.0026724 | -0.09613 | 63.1439 | -59.1522 | 63.2263 | -58.905 | -59.3445 | -59.2804 | -0.082397 | 63.0936 | -59.1064 | 63.2492 | -59.0607 | -59.198 | -59.0515 | -0.086975 | -0.07782 | 0.004577 | 0.16022 | -0.21515 | -0.27923 | -0.12817 | -0.19226 | -0.041198 | -0.12817 | 0.027466 | 0.004578 | 0.013733 | -0.13275 | 0.054931 | -0.091553 | 0.24719 | 122.3785 | 0.045776 | 122.3557 | 122.2961 | 122.2 | 122.2092 | 122.1588 | -122.374 | -122.3282 | 122.2916 | 122.3145 | 58.9691 | 58.9828
979.3125 | 122.6074 | -59.0927 | 63.2172 | -0.027695 | 0.0039028 | 0.064871 | 0.059595 | -0.0039306 | -0.0010382 | -8.1264e-05 | -0.0061035 | 0.0022729 | 0.065875 | 0.063916 | -0.0078272 | 0.010079 | -0.0052316 | -0.28381 | 63.1668 | -59.1568 | 63.2492 | -58.8638 | -59.2758 | -59.2575 | -0.009155 | 63.1073 | -59.0607 | 63.2812 | -59.0195 | -59.1293 | -59.024 | -0.064087 | -0.050354 | 0.032044 | 0.22888 | -0.16479 | -0.18311 | -0.10071 | -0.11902 | 0.032043 | -0.10986 | 0.064087 | 0.073242 | 0.068664 | -0.036621 | 0.036621 | -0.068664 | 0.29297 | 122.406 | 0.041199 | 122.3419 | 122.3236 | 122.168 | 122.2595 | 122.2 | -122.374 | -122.2778 | 122.3419 | 122.374 | 58.8089 | 59.0836
980.3125 | 122.5525 | -59.0973 | 63.2172 | -0.058212 | 0.0019802 | 0.062948 | 0.058313 | 0.002478 | -0.0027472 | -0.0043537 | -0.045776 | 0.0012047 | 0.068011 | 0.062634 | -0.0054774 | 0.0090105 | -0.0056588 | -0.31128 | 63.1302 | -59.1888 | 63.3545 | -59.0927 | -59.3765 | -59.2667 | -0.041199 | 63.0981 | -59.079 | 63.2446 | -59.0744 | -59.1888 | -59.0424 | -0.091553 | -0.086975 | 0.13733 | 0.004578 | -0.16937 | -0.27924 | -0.07782 | -0.18768 | 0.018311 | -0.11902 | 0.027466 | 0.022888 | 0.054932 | -0.091553 | 0.036621 | -0.10986 | 0.096131 | 122.5433 | 0.004577 | 122.3236 | 122.319 | 122.1771 | 122.2275 | 122.1954 | -122.406 | -122.2961 | 122.4518 | 122.3419 | 58.786 | 59.0561
981.3125 | 122.5525 | -59.0515 | 63.2172 | -0.096359 | 0.0036892 | 0.060812 | 0.060449 | -0.002649 | -0.00061096 | -0.0015765 | -0.097656 | 0.0035547 | 0.066302 | 0.056226 | -0.0071864 | 0.0090105 | -0.0043772 | -0.36163 | 63.1668 | -59.1705 | 63.2217 | -58.9417 | -59.0515 | -59.198 | -0.050354 | 63.1073 | -59.0881 | 63.2629 | -59.079 | -59.1888 | -59.079 | -0.11902 | -0.050354 | 0.004578 | 0.10986 | -0.14648 | 0 | -0.027466 | 0.11902 | -0.036621 | -0.10986 | 0.045776 | -0.027465 | -0.027465 | -0.13733 | 0.009156 | -0.10071 | 0.22888 | 122.3923 | 0.009156 | 122.3511 | 122.3373 | 122.1954 | 122.2183 | 122.1588 | -122.3877 | -122.3053 | 122.2733 | 122.3145 | 58.6899 | 59.0012
982.3125 | 122.493 | -59.0561 | 63.2721 | -0.027695 | 0.0041166 | 0.060812 | 0.06109 | 0.0016236 | -0.0031744 | -0.00029486 | -0.05188 | 0.0037683 | 0.068438 | 0.061993 | -0.008468 | 0.0098651 | -0.0028818 | -0.29755 | 63.1851 | -59.1843 | 63.2355 | -58.9142 | -59.3033 | -59.2804 | -0.041199 | 63.1989 | -59.0744 | 63.2401 | -59.0927 | -59.2209 | -59.0881 | -0.12817 | -0.086975 | -0.036621 | 0.14191 | -0.22431 | -0.24719 | -0.096131 | -0.11902 | -0.018311 | -0.073242 | -0.032044 | -0.036621 | -0.032044 | -0.16479 | -0.013733 | -0.14648 | 0.27008 | 122.4197 | -0.01831 | 122.3145 | 122.3694 | 122.2733 | 122.2412 | 122.2549 | -122.4564 | -122.3465 | 122.2916 | 122.2961 | 58.7585 | 59.0149
983.3125 | 122.58 | -59.0469 | 63.2584 | -0.035324 | 0.0039028 | 0.063162 | 0.060235 | -0.004358 | -0.0016792 | -0.0017903 | 0.015259 | 0.0022729 | 0.066089 | 0.063275 | -0.005691 | 0.0090105 | -0.0041636 | -0.39368 | 63.1851 | -59.1614 | 63.2446 | -58.8776 | -59.3033 | -59.2529 | -0.045776 | 63.1393 | -59.0973 | 63.2904 | -59.0332 | -59.1476 | -59.0057 | -0.11444 | -0.073242 | -0.013733 | 0.16937 | -0.20599 | -0.25635 | -0.091553 | -0.14191 | -0.050354 | -0.11902 | 0.032043 | 0.013733 | 0.041199 | -0.10071 | 0.091553 | -0.050354 | 0.28381 | 122.406 | 0.064087 | 122.3877 | 122.3465 | 122.2366 | 122.2321 | 122.1863 | -122.4197 | -122.3557 | 122.2916 | 122.3373 | 58.6533 | 59.0012
984.3125 | 122.6257 | -59.0149 | 63.2309 | -0.073471 | 0.0011258 | 0.062094 | 0.060235 | -0.00051278 | -0.00232 | -0.00072206 | -0.0091553 | 0.00056395 | 0.068225 | 0.059857 | -0.0074 | 0.0098651 | -0.0048044 | -0.37537 | 63.1668 | -59.1431 | 63.3041 | -58.8226 | -59.2209 | -59.1888 | 0.064087 | 63.1256 | -59.0561 | 63.327 | -58.96 | -59.0652 | -58.9783 | -0.12817 | -0.064087 | 0.073242 | 0.19226 | -0.17395 | -0.20599 | -0.045777 | -0.07782 | -0.041198 | -0.10529 | 0.09613 | 0.054932 | 0.036622 | -0.050354 | 0.07782 | -0.009156 | 0.32043 | 122.4472 | 0.09613 | 122.3831 | 122.3099 | 122.1817 | 122.1817 | 122.1405 | -122.374 | -122.287 | 122.319 | 122.3419 | 58.6395 | 59.079
985.3125 | 122.612 | -59.0424 | 63.2401 | -0.042954 | 0.0028348 | 0.064657 | 0.058313 | -0.0013672 | -0.0038154 | -0.0015765 | -0.0030517 | 0.0018457 | 0.067798 | 0.051739 | -0.0054774 | 0.0092241 | -0.0018136 | -0.41199 | 63.1714 | -59.1431 | 63.2858 | -58.8226 | -59.2255 | -59.2072 | 0.050354 | 63.1577 | -59.0515 | 63.3408 | -58.9554 | -59.079 | -58.96 | -0.10071 | -0.068664 | 0.045777 | 0.21973 | -0.16479 | -0.18311 | -0.064087 | -0.082398 | -0.009156 | -0.082397 | 0.10071 | 0.086975 | 0.082397 | -0.036621 | 0.091553 | -0.027465 | 0.32043 | 122.4289 | 0.096131 | 122.3923 | 122.3145 | 122.2092 | 122.2137 | 122.2 | -122.3831 | -122.2916 | 122.3282 | 122.3831 | 58.6304 | 59.0927
986.3125 | 122.644 | -59.024 | 63.2355 | -0.065842 | 0.0024076 | 0.062735 | 0.057886 | -0.0015808 | -0.0042426 | -0.00050846 | -0.0061035 | 0.0016321 | 0.066729 | 0.06178 | -0.0044092 | 0.0096515 | 0.000109 | -0.45319 | 63.1851 | -59.1385 | 63.3133 | -58.8135 | -59.23 | -59.2072 | 0.045776 | 63.1256 | -59.0424 | 63.3636 | -58.9645 | -59.0561 | -58.9645 | -0.11444 | -0.050354 | 0.077819 | 0.21057 | -0.1831 | -0.20599 | -0.068664 | -0.091553 | -0.01831 | -0.10986 | 0.12817 | 0.059509 | 0.059509 | -0.032043 | 0.077819 | -0.013733 | 0.32501 | 122.4518 | 0.077819 | 122.406 | 122.3236 | 122.168 | 122.2092 | 122.1497 | -122.374 | -122.2778 | 122.3373 | 122.3877 | 58.5709 | 59.0698
987.3125 | 122.5891 | -59.0378 | 63.2538 | -0.0048066 | 0.0039028 | 0.063162 | 0.058954 | 0.00034182 | -0.0027472 | -0.0015765 | -0.01831 | -0.00050405 | 0.066729 | 0.060712 | -0.0069726 | 0.010292 | 0.0003226 | -0.53101 | 63.1668 | -59.1385 | 63.2675 | -58.8821 | -59.2712 | -59.2346 | -0.036621 | 63.1393 | -59.079 | 63.3041 | -59.0195 | -59.111 | -59.0103 | -0.10071 | -0.086975 | 0.013733 | 0.15564 | -0.19684 | -0.23346 | -0.09613 | -0.13275 | -0.041198 | -0.11444 | 0.050354 | 0.018311 | 0.027466 | -0.073242 | 0.068664 | -0.032044 | 0.25635 | 122.406 | 0.059509 | 122.3831 | 122.3053 | 122.2183 | 122.2046 | 122.1771 | -122.3923 | -122.3328 | 122.3053 | 122.3419 | 58.5068 | 59.0012
988.3125 | 122.6395 | -59.0149 | 63.2401 | -0.073471 | 0.0030484 | 0.064657 | 0.060449 | 0.0029052 | -0.0029608 | -0.00072206 | 0.0061035 | 0.0020593 | 0.067584 | 0.054944 | -0.0061182 | 0.0092241 | -0.003309 | -0.53101 | 63.1714 | -59.1248 | 63.3224 | -58.8181 | -59.2255 | -59.1934 | 0.059509 | 63.1439 | -59.0378 | 63.3636 | -58.9417 | -59.0607 | -58.9462 | -0.10986 | -0.068664 | 0.082398 | 0.19684 | -0.17853 | -0.21057 | -0.068664 | -0.10071 | -0.022888 | -0.09613 | 0.1236 | 0.073243 | 0.068665 | -0.045776 | 0.091553 | -0.022888 | 0.3067 | 122.4472 | 0.096131 | 122.4014 | 122.2961 | 122.1817 | 122.1863 | 122.1588 | -122.3648 | -122.2778 | 122.3373 | 122.3785 | 58.4839 | 59.0744
989.3125 | 122.6166 | -59.0149 | 63.2584 | -0.073471 | 0.001553 | 0.062094 | 0.060022 | 0.00076902 | -0.0036018 | -0.0054217 | 0.045776 | 0.0022729 | 0.068225 | 0.05943 | -0.006759 | 0.011574 | -0.0020272 | -0.52185 | 63.2034 | -59.1064 | 63.5605 | -58.4564 | -59.4772 | -59.4452 | 0.10529 | 63.1577 | -59.0378 | 63.382 | -58.9188 | -59.0515 | -58.9371 | -0.091552 | -0.054932 | 0.30212 | 0.55847 | -0.4303 | -0.46234 | -0.33874 | -0.37079 | -0.022888 | -0.10071 | 0.1236 | 0.096131 | 0.07782 | -0.036621 | 0.10071 | -0.013733 | 0.65002 | 122.6669 | 0.11902 | 122.4197 | 122.3099 | 122.1954 | 122.2183 | 122.1725 | -122.3648 | -122.2961 | 122.5754 | 122.3969 | 58.493 | 59.1202
990.3125 | 122.5616 | -59.0103 | 63.2996 | -0.050583 | 0.0034756 | 0.062948 | 0.058313 | 0.0018372 | -0.0027472 | -0.0034991 | -0.012207 | 0.0016321 | 0.066302 | 0.060925 | -0.006759 | 0.0085833 | -0.0013864 | -0.56305 | 63.1943 | -59.1019 | 63.3316 | -58.786 | -59.1934 | -59.1705 | 0.086975 | 63.1668 | -59.0149 | 63.327 | -58.9783 | -59.111 | -58.9645 | -0.091553 | -0.10529 | 0.032043 | 0.2243 | -0.16022 | -0.18311 | -0.068664 | -0.091552 | -0.004578 | -0.13275 | 0.027465 | 0.032044 | 0.045776 | -0.10071 | 0.050354 | -0.09613 | 0.31586 | 122.4335 | 0.036622 | 122.3419 | 122.2961 | 122.1817 | 122.2046 | 122.1771 | -122.4014 | -122.3145 | 122.3419 | 122.3373 | 58.4473 | 59.0973
991.3125 | 122.6212 | -59.0057 | 63.2629 | -0.08873 | 0.0034756 | 0.062094 | 0.058954 | -0.0028626 | -0.0018928 | -0.00072206 | -0.05188 | 0.0012047 | 0.066089 | 0.053448 | -0.0046228 | 0.010292 | -0.0022408 | -0.6134 | 63.2172 | -59.1156 | 63.121 | -58.9737 | -59.0927 | -59.1522 | 0.1236 | 63.1348 | -59.024 | 63.3636 | -58.9096 | -59.0286 | -58.9508 | -0.10986 | -0.045776 | -0.14191 | 0.032043 | -0.14648 | -0.086975 | -0.036621 | 0.022889 | -0.018311 | -0.12817 | 0.10071 | 0.09613 | 0.054931 | -0.022888 | 0.073242 | -0.004577 | 0.14191 | 122.2366 | 0.11444 | 122.3877 | 122.3328 | 122.1588 | 122.2229 | 122.1405 | -122.3785 | -122.287 | 122.1268 | 122.3694 | 58.3923 | 59.1293
992.3125 | 122.4838 | -59.0057 | 63.3041 | -0.0048066 | 0.0043302 | 0.064016 | 0.062158 | -0.0013672 | -0.0046698 | -0.0017903 | -0.10681 | 0.0041955 | 0.066089 | 0.063061 | -0.0054774 | 0.0098651 | -0.0009592 | -0.72784 | 63.2126 | -59.1293 | 63.2812 | -58.873 | -59.2941 | -59.2667 | -0.018311 | 63.1851 | -59.0332 | 63.2996 | -59.0332 | -59.1888 | -59.0378 | -0.1236 | -0.091553 | -0.022888 | 0.13275 | -0.26093 | -0.28839 | -0.13733 | -0.16479 | -0.027466 | -0.11902 | -0.004577 | -0.027466 | -0.032044 | -0.18311 | -0.004578 | -0.15564 | 0.25635 | 122.4106 | 0 | 122.3328 | 122.3419 | 122.2183 | 122.2183 | 122.1909 | -122.4335 | -122.3373 | 122.287 | 122.3053 | 58.2779 | 58.9874
993.3125 | 122.6624 | -58.9737 | 63.2629 | -0.096359 | 0.0030484 | 0.064444 | 0.05874 | -0.0015808 | -0.0036018 | -8.1264e-05 | 0.030518 | 0.0022729 | 0.06737 | 0.062207 | -0.0061182 | 0.0092241 | -0.0003182 | -0.7782 | 63.1805 | -59.0927 | 63.3408 | -58.754 | -59.1934 | -59.1614 | 0.091553 | 63.1714 | -59.0149 | 63.414 | -58.9142 | -59.0286 | -58.9279 | -0.11902 | -0.082397 | 0.07782 | 0.21973 | -0.18768 | -0.21973 | -0.068665 | -0.10071 | -0.041199 | -0.091552 | 0.15106 | 0.059509 | 0.045777 | -0.054931 | 0.086976 | -0.013732 | 0.33874 | 122.4335 | 0.10071 | 122.4289 | 122.2733 | 122.1863 | 122.1542 | 122.1451 | -122.3557 | -122.2778 | 122.3145 | 122.3877 | 58.1955 | 59.0652
994.3125 | 122.6166 | -58.9691 | 63.2767 | -0.035324 | 0.0019802 | 0.063589 | 0.059808 | -0.002008 | -0.00082456 | -0.0026447 | 0.015259 | 0.0018457 | 0.06737 | 0.060925 | -0.0052638 | 0.0098651 | -0.0039498 | -0.8194 | 63.2172 | -59.0881 | 63.3499 | -58.754 | -59.1751 | -59.1568 | 0.09613 | 63.1668 | -59.0195 | 63.3865 | -58.9233 | -59.024 | -58.9096 | -0.11902 | -0.059509 | 0.073243 | 0.21515 | -0.18768 | -0.20599 | -0.068664 | -0.086975 | -0.050354 | -0.10986 | 0.10986 | 0.045776 | 0.059509 | -0.054932 | 0.10986 | -0.004578 | 0.33417 | 122.4381 | 0.09613 | 122.406 | 122.3053 | 122.1863 | 122.1863 | 122.1359 | -122.3648 | -122.2961 | 122.319 | 122.3557 | 58.1497 | 59.0652
995.3125 | 122.6395 | -58.9966 | 63.3041 | -0.065842 | 0.004971 | 0.06423 | 0.058313 | 0.0020508 | -0.00018376 | -0.0015765 | 0.0030517 | 0.0022729 | 0.066516 | 0.056439 | -0.0048364 | 0.0098651 | -0.0035226 | -0.88806 | 63.2126 | -59.1019 | 63.3453 | -58.7311 | -59.1522 | -59.1248 | 0.11902 | 63.2126 | -58.9966 | 63.3957 | -58.905 | -59.0012 | -58.9096 | -0.10529 | -0.091553 | 0.041199 | 0.2655 | -0.12817 | -0.15564 | -0.022888 | -0.050354 | 0 | -0.091553 | 0.091553 | 0.091553 | 0.086975 | -0.004578 | 0.086975 | -0.004578 | 0.37079 | 122.4472 | 0.091553 | 122.3923 | 122.3145 | 122.2092 | 122.2092 | 122.2092 | -122.406 | -122.3007 | 122.3419 | 122.3923 | 58.1085 | 59.1156
996.3125 | 122.4884 | -59.0149 | 63.3499 | -0.050583 | 0.0043302 | 0.062735 | 0.062372 | -0.0024354 | -0.0025336 | -0.0034991 | -0.05188 | 0.0024865 | 0.069079 | 0.06178 | -0.0027002 | 0.0096515 | -0.003309 | -0.95673 | 63.2767 | -59.1064 | 63.2538 | -58.8593 | -59.2667 | -59.2621 | -0.032043 | 63.2446 | -59.0103 | 63.176 | -58.96 | -59.1476 | -59.0378 | -0.091552 | -0.073243 | -0.096131 | 0.15564 | -0.24719 | -0.25177 | -0.15564 | -0.16022 | 0.004578 | -0.10529 | -0.17395 | 0.054932 | -0.022888 | -0.13275 | -0.027466 | -0.13733 | 0.24719 | 122.3602 | 0.050354 | 122.1863 | 122.3831 | 122.2549 | 122.2916 | 122.2595 | -122.4564 | -122.3602 | 122.2687 | 122.1909 | 58.0582 | 58.9828
997.3125 | 122.4884 | -59.0149 | 63.2904 | -0.43968 | 0.0026212 | 0.063589 | 0.063226 | 0.00034182 | -0.0029608 | -0.00050846 | -0.11597 | 0.0020593 | 0.067798 | 0.068616 | -0.0052638 | 0.010079 | -0.0001046 | -1.0757 | 63.1805 | -59.1843 | 63.1989 | -58.9508 | -59.317 | -59.2941 | -0.18768 | 63.2492 | -59.0607 | 63.2629 | -59.0973 | -59.23 | -59.0607 | -0.16937 | -0.10986 | -0.091552 | 0.064087 | -0.27923 | -0.30212 | -0.10986 | -0.13275 | -0.045776 | -0.041198 | -0.027466 | -0.082397 | -0.045776 | -0.21515 | 0 | -0.16937 | 0.23346 | 122.3831 | -0.036621 | 122.3236 | 122.3648 | 122.3099 | 122.1954 | 122.2641 | -122.4747 | -122.3511 | 122.2137 | 122.2778 | 57.9391 | 58.8272
998.3125 | 122.6028 | -58.9691 | 63.2996 | -0.027695 | 0.0028348 | 0.065298 | 0.057031 | -0.0041444 | -0.0036018 | -0.00029486 | 0.021362 | 0.0037683 | 0.067157 | 0.066052 | -0.0078272 | 0.011574 | -0.0018136 | -1.062 | 63.2263 | -59.0515 | 63.382 | -58.7494 | -59.1614 | -59.1156 | 0.073242 | 63.2172 | -58.9737 | 63.3957 | -58.9233 | -59.0378 | -58.9096 | -0.082398 | -0.073243 | 0.082397 | 0.21973 | -0.14648 | -0.19226 | -0.064087 | -0.10986 | -0.004578 | -0.082398 | 0.09613 | 0.045776 | 0.059509 | -0.068665 | 0.064087 | -0.064087 | 0.30212 | 122.4335 | 0.050354 | 122.3694 | 122.2778 | 122.1909 | 122.1954 | 122.1863 | -122.3511 | -122.2733 | 122.3511 | 122.3648 | 57.9071 | 59.0424
999.3125 | 122.4884 | -58.9828 | 63.3408 | -0.027695 | 0.0028348 | 0.063589 | 0.059808 | 0.00098262 | -0.0038154 | 0.00013254 | -0.0091553 | 0.0020593 | 0.065661 | 0.060925 | -0.005691 | 0.0087969 | -0.0043772 | -1.1398 | 63.2492 | -59.0744 | 63.327 | -58.7769 | -59.2163 | -59.1751 | 0.013733 | 63.2629 | -58.9828 | 63.3224 | -58.9966 | -59.1248 | -59.0332 | -0.091553 | -0.091552 | -0.013733 | 0.20599 | -0.19226 | -0.23346 | -0.10071 | -0.14191 | 0 | -0.07782 | -0.01831 | -0.013733 | -0.050354 | -0.14191 | -0.050354 | -0.14191 | 0.29755 | 122.4014 | -0.013733 | 122.3053 | 122.3236 | 122.2458 | 122.2321 | 122.2458 | -122.4152 | -122.3236 | 122.3099 | 122.3053 | 57.843 | 58.9966
1000.3125 | 122.5021 | -59.0057 | 63.3682 | -0.027695 | 0.000485 | 0.063803 | 0.058526 | 0.00098262 | -0.003388 | -0.0022175 | -0.024414 | 0.00035035 | 0.068866 | 0.05708 | -0.005691 | 0.010933 | -0.0026682 | -1.2268 | 63.2904 | -59.0469 | 63.3133 | -58.7952 | -59.2117 | -59.1843 | -0.004578 | 63.2721 | -58.9874 | 63.295 | -58.9828 | -59.1339 | -59.0149 | -0.041199 | -0.07782 | -0.054932 | 0.21057 | -0.17853 | -0.20599 | -0.13733 | -0.16479 | 0.01831 | -0.09613 | -0.073242 | 0.022888 | -0.009156 | -0.12817 | -0.027466 | -0.14648 | 0.25177 | 122.3602 | 0.004578 | 122.2824 | 122.3373 | 122.2595 | 122.2961 | 122.2778 | -122.4152 | -122.3557 | 122.319 | 122.3007 | 57.7789 | 59.0012
1001.3125 | 122.5754 | -58.96 | 63.3728 | -0.065842 | 0.0019802 | 0.062521 | 0.057672 | 0.0039734 | -0.0031744 | -0.0039265 | -0.0061035 | 0.0018457 | 0.066302 | 0.056653 | -0.0054774 | 0.0083697 | -0.0048044 | -1.2909 | 63.2217 | -59.0652 | 63.3865 | -58.7173 | -59.1385 | -59.111 | 0.073242 | 63.2355 | -58.9371 | 63.3774 | -58.9142 | -59.0378 | -58.9279 | -0.10529 | -0.15106 | 0.013733 | 0.24262 | -0.15106 | -0.17853 | -0.045776 | -0.073242 | 0.022888 | -0.13733 | 0.004577 | 0.045776 | 0.032044 | -0.07782 | 0.009156 | -0.10071 | 0.3479 | 122.4518 | 0.022888 | 122.3145 | 122.287 | 122.1725 | 122.1817 | 122.1954 | -122.4381 | -122.3099 | 122.3465 | 122.3373 | 57.6691 | 59.0332
1002.3281 | 122.6624 | -58.8867 | 63.3362 | -0.020065 | 0.004971 | 0.062094 | 0.057886 | -0.0013672 | -0.00082456 | 0.00055974 | 0.033569 | 0.00035035 | 0.068652 | 0.057721 | -0.0076136 | 0.0090105 | -0.0035226 | -1.4053 | 63.2446 | -59.0195 | 63.382 | -58.6853 | -59.1293 | -59.079 | 0.10529 | 63.2034 | -58.9508 | 63.446 | -58.8593 | -58.7402 | -58.5938 | -0.13275 | -0.091553 | 0.045776 | 0.20142 | -0.19226 | -0.24261 | -0.059509 | -0.10986 | -0.064087 | -0.13275 | 0.10986 | 0.027466 | 0.29297 | 0.14648 | 0.35706 | 0.21057 | 0.33417 | 122.4014 | 0.091553 | 122.3969 | 122.2641 | 122.1542 | 122.1313 | 122.0901 | -122.3557 | -122.287 | 122.2687 | 122.3328 | 57.4814 | 58.992
1003.3125 | 122.4976 | -58.9508 | 63.4048 | -0.012436 | 0.0019802 | 0.063162 | 0.059381 | 0.00098262 | -0.004029 | 0.00055974 | -0.021362 | 0.0024865 | 0.067157 | 0.059644 | -0.0046228 | 0.0096515 | -0.0020272 | -1.4969 | 63.2904 | -59.0424 | 63.3179 | -58.8089 | -59.2346 | -59.198 | -0.045776 | 63.2767 | -58.9828 | 63.3087 | -59.0057 | -59.0195 | -58.8089 | -0.091552 | -0.11444 | -0.086975 | 0.14191 | -0.24719 | -0.28381 | -0.15564 | -0.19226 | -0.032043 | -0.12817 | -0.09613 | -0.054931 | 0.14191 | -0.068664 | 0.17395 | -0.036621 | 0.23346 | 122.3602 | -0.022888 | 122.2916 | 122.3328 | 122.2595 | 122.2412 | 122.2275 | -122.4472 | -122.3877 | 122.2687 | 122.2595 | 57.4539 | 58.905
1004.3125 | 122.5525 | -58.9371 | 63.3774 | -0.042954 | 0.003262 | 0.063162 | 0.061944 | -0.0022218 | -0.005097 | -8.1264e-05 | -0.057983 | 0.0024865 | 0.06737 | 0.065839 | -0.0065454 | 0.011147 | -0.0020272 | -1.593 | 63.3041 | -59.0836 | 63.3179 | -58.8089 | -59.2117 | -59.198 | -0.027466 | 63.2858 | -58.96 | 63.3591 | -58.9691 | -59.0927 | -58.96 | -0.14648 | -0.073242 | -0.059509 | 0.12817 | -0.26093 | -0.27466 | -0.11444 | -0.12817 | -0.022888 | -0.091552 | -0.01831 | -0.032043 | -0.022888 | -0.15564 | 0 | -0.13275 | 0.27466 | 122.4014 | -0.009155 | 122.319 | 122.3877 | 122.2458 | 122.2412 | 122.2229 | -122.4609 | -122.3373 | 122.2549 | 122.2961 | 57.3441 | 58.9096
1005.3125 | 122.4838 | -58.9737 | 63.3957 | -0.027695 | 0.0019802 | 0.062735 | 0.058526 | -8.538e-05 | -0.0036018 | -8.1264e-05 | -0.036621 | 0.0016321 | 0.067798 | 0.060284 | -0.0063318 | 0.01072 | -0.0035226 | -1.7029 | 63.3133 | -59.0561 | 63.2904 | -58.8135 | -59.2255 | -59.2072 | -0.045776 | 63.2904 | -58.9554 | 63.3316 | -58.9874 | -59.1248 | -58.9828 | -0.082397 | -0.082398 | -0.10529 | 0.16022 | -0.23346 | -0.25177 | -0.15106 | -0.16937 | 0.018311 | -0.10529 | -0.064087 | -0.013733 | -0.009155 | -0.15106 | -0.027466 | -0.16937 | 0.24261 | 122.3465 | -0.032044 | 122.287 | 122.3694 | 122.2458 | 122.287 | 122.2641 | -122.4518 | -122.3511 | 122.2641 | 122.3053 | 57.2708 | 58.9279
1006.3125 | 122.5067 | -58.9554 | 63.4094 | -0.027695 | 0.0024076 | 0.064444 | 0.061303 | -0.0015808 | -0.003388 | -0.0047809 | -0.042725 | 0.00013675 | 0.066729 | 0.064343 | -0.0065454 | 0.010079 | -0.0009592 | -1.7944 | 63.3362 | -59.0424 | 63.3041 | -58.8089 | -59.2163 | -59.2026 | -0.082397 | 63.295 | -58.992 | 63.3453 | -58.9828 | -59.1293 | -58.9737 | -0.086975 | -0.073242 | -0.10529 | 0.14648 | -0.24719 | -0.26093 | -0.16022 | -0.17395 | -0.036621 | -0.11444 | -0.064087 | -0.027466 | -0.018311 | -0.17395 | 0.01831 | -0.13733 | 0.23346 | 122.3465 | 0.009155 | 122.3373 | 122.3785 | 122.287 | 122.2916 | 122.2504 | -122.4518 | -122.4014 | 122.2595 | 122.3007 | 57.1609 | 58.873
1007.3281 | 122.6395 | -58.9142 | 63.3728 | -0.035324 | 0.0028348 | 0.062094 | 0.05874 | -0.00093998 | -0.0031744 | -0.0056355 | -0.10376 | 0.0022729 | 0.065234 | 0.060498 | -0.0069726 | 0.0096515 | -0.005018 | -1.8219 | 63.295 | -59.0149 | 63.4506 | -58.6349 | -58.6075 | -58.9279 | 0.13733 | 63.2263 | -58.9508 | 63.4323 | -58.8135 | -58.9645 | -58.8455 | -0.10071 | -0.07782 | 0.07782 | 0.27924 | -0.013732 | 0.3067 | 0.086976 | 0.40741 | -0.036621 | -0.14648 | 0.059509 | 0.10071 | 0.068665 | -0.050354 | 0.10529 | -0.013733 | 0.37994 | 122.4655 | 0.13733 | 122.3831 | 122.3099 | 122.1771 | 122.2092 | 122.1405 | -122.3877 | -122.3236 | 122.3648 | 122.3465 | 57.0923 | 59.0515
1008.3125 | 122.4792 | -58.9279 | 63.4323 | -0.0048066 | 0.0039028 | 0.063162 | 0.058099 | 0.00098262 | -0.0021064 | -0.0022175 | 0.012207 | 0.00035035 | 0.065661 | 0.062207 | -0.0071864 | 0.0077289 | -0.0020272 | -1.9226 | 63.2996 | -59.0103 | 63.3957 | -58.7173 | -59.1248 | -59.0973 | 0.018311 | 63.2812 | -58.9325 | 63.3774 | -58.9371 | -59.0698 | -58.9325 | -0.082398 | -0.13275 | -0.036621 | 0.21057 | -0.16937 | -0.19684 | -0.086975 | -0.11444 | -0.004578 | -0.15106 | -0.054932 | -0.009156 | -0.004578 | -0.14191 | 0 | -0.13733 | 0.29297 | 122.406 | -0.004578 | 122.3099 | 122.3099 | 122.2137 | 122.2275 | 122.2092 | -122.4426 | -122.3648 | 122.3236 | 122.3053 | 57.0053 | 58.9462
1009.3125 | 122.4838 | -58.9188 | 63.4277 | 0.025711 | 0.0019802 | 0.062735 | 0.060022 | -0.00051278 | -0.0044562 | -0.0039265 | -0.042725 | 0.0024865 | 0.06737 | 0.07182 | -0.0074 | 0.010506 | 0.0005362 | -2.0691 | 63.3408 | -59.0469 | 63.327 | -58.786 | -59.198 | -59.1843 | -0.073242 | 63.3179 | -58.9554 | 63.3774 | -58.9554 | -59.0652 | -58.9325 | -0.12817 | -0.086975 | -0.10071 | 0.13275 | -0.2655 | -0.27924 | -0.13733 | -0.15106 | -0.036621 | -0.10986 | -0.050354 | -0.036621 | -0.013733 | -0.14648 | 0.022888 | -0.10986 | 0.26093 | 122.374 | 0 | 122.3328 | 122.3877 | 122.2733 | 122.2595 | 122.2366 | -122.4747 | -122.3831 | 122.2458 | 122.2961 | 56.8497 | 58.8455
1010.3125 | 122.525 | -58.9096 | 63.4003 | 0.010452 | 0.003262 | 0.065085 | 0.060876 | -0.0028626 | -0.00039736 | -0.00072206 | -0.045776 | 0.0027001 | 0.068225 | 0.05943 | -0.0063318 | 0.010506 | -0.0024546 | -2.1332 | 63.3591 | -59.0103 | 63.3865 | -58.7448 | -59.166 | -59.1339 | -0.036621 | 63.3041 | -58.9325 | 63.382 | -58.9188 | -59.0607 | -58.905 | -0.10071 | -0.041199 | -0.013733 | 0.16479 | -0.2243 | -0.25635 | -0.1236 | -0.15564 | -0.022888 | -0.096131 | -0.018311 | -0.009155 | 0.004578 | -0.15106 | 0.027466 | -0.12817 | 0.2655 | 122.3969 | 0.013733 | 122.3145 | 122.3694 | 122.2366 | 122.2687 | 122.2137 | -122.4106 | -122.3328 | 122.2961 | 122.2916 | 56.7764 | 58.873
1011.3125 | 122.4472 | -58.9188 | 63.4003 | -0.042954 | 0.0013394 | 0.063376 | 0.059167 | 0.0022644 | -0.0048834 | -0.0011493 | -0.061035 | 0.0024865 | 0.067798 | 0.064984 | -0.0041956 | 0.0085833 | -0.0054452 | -2.243 | 63.3362 | -59.0103 | 63.3911 | -58.7219 | -59.1522 | -59.1385 | -0.041199 | 63.2996 | -58.9325 | 63.4003 | -58.9279 | -59.111 | -59.0378 | -0.091553 | -0.064087 | -0.009156 | 0.19684 | -0.21973 | -0.23346 | -0.12817 | -0.14191 | -0.013733 | -0.10071 | 0 | -0.009155 | -0.11902 | -0.19226 | -0.10529 | -0.17853 | 0.28839 | 122.4014 | 0.004578 | 122.3328 | 122.3465 | 122.2321 | 122.2549 | 122.2183 | -122.4106 | -122.3328 | 122.3099 | 122.319 | 56.6757 | 58.8776
1012.3125 | 122.5754 | -58.905 | 63.3774 | -0.10399 | 0.002194 | 0.06423 | 0.057458 | 0.0011962 | -0.0016792 | -0.00050846 | 0.039673 | 0.0033411 | 0.066729 | 0.057294 | -0.0052638 | 0.0079425 | -0.0039498 | -2.4124 | 63.2904 | -59.0286 | 63.3728 | -58.7128 | -59.1568 | -59.1202 | -0.12817 | 63.2721 | -58.9325 | 63.414 | -58.9142 | -59.0195 | -58.8776 | -0.1236 | -0.086975 | -0.004577 | 0.19226 | -0.21515 | -0.25177 | -0.091553 | -0.12817 | -0.027466 | -0.10529 | 0.036621 | -0.009156 | 0.027466 | -0.11444 | 0.054932 | -0.086975 | 0.31586 | 122.4014 | 0.01831 | 122.3465 | 122.319 | 122.2046 | 122.1954 | 122.1771 | -122.406 | -122.3099 | 122.2778 | 122.319 | 56.4926 | 58.7769
1013.3125 | 122.5388 | -58.8959 | 63.4506 | -0.058212 | 0.0036892 | 0.06423 | 0.059167 | 0.00012822 | -0.00061096 | 0.00055974 | -0.027466 | 0.0012047 | 0.066943 | 0.066693 | -0.0052638 | 0.0098651 | 0.000109 | -2.4673 | 63.3728 | -59.0149 | 63.3636 | -58.7357 | -59.1248 | -59.1202 | -0.073242 | 63.3408 | -58.9096 | 63.4186 | -58.9005 | -59.0286 | -58.8959 | -0.11902 | -0.07782 | -0.086976 | 0.16022 | -0.2243 | -0.22888 | -0.10529 | -0.10986 | -0.013733 | -0.10986 | -0.032044 | -0.004578 | 0 | -0.13275 | 0.013733 | -0.11902 | 0.27924 | 122.3785 | 0.009155 | 122.3282 | 122.3877 | 122.2504 | 122.2687 | 122.2366 | -122.4655 | -122.3602 | 122.2595 | 122.3145 | 56.4285 | 58.8226
1014.3125 | 122.5296 | -58.8913 | 63.4094 | -0.020065 | 0.0041166 | 0.062094 | 0.062372 | 0.00055542 | -0.0027472 | -0.0013629 | 0.054932 | 0.0020593 | 0.068011 | 0.060498 | -0.0069726 | 0.0087969 | -0.0024546 | -2.5269 | 63.382 | -59.0149 | 63.3865 | -58.6487 | -59.4177 | -59.2438 | -0.086975 | 63.327 | -58.9188 | 63.446 | -58.8867 | -59.0103 | -58.8638 | -0.1236 | -0.027466 | -0.022888 | 0.24261 | -0.35248 | -0.52643 | -0.22888 | -0.40283 | -0.027466 | -0.082398 | 0.036621 | 0.004577 | 0.027465 | -0.11902 | 0.054931 | -0.091553 | 0.36621 | 122.4014 | 0.032043 | 122.3648 | 122.3969 | 122.2458 | 122.2733 | 122.2183 | -122.4243 | -122.3282 | 122.2778 | 122.3373 | 56.3644 | 58.8043
1015.3125 | 122.5433 | -58.8684 | 63.4415 | -0.020065 | 0.0019802 | 0.063803 | 0.058954 | 0.002478 | -0.00232 | -0.0039265 | -0.027466 | 0.0018457 | 0.06502 | 0.05943 | -0.00505 | 0.01072 | 0.0039542 | -2.6138 | 63.4094 | -58.9828 | 63.3911 | -58.7082 | -59.1248 | -59.0973 | -0.086975 | 63.3636 | -58.8959 | 63.4369 | -58.8959 | -59.0286 | -58.8776 | -0.11444 | -0.032043 | -0.050354 | 0.16022 | -0.22888 | -0.25635 | -0.11444 | -0.14191 | -0.027466 | -0.07782 | -0.004577 | -0.027466 | -0.009155 | -0.16022 | 0.018311 | -0.13275 | 0.27466 | 122.374 | 0 | 122.3328 | 122.3923 | 122.2595 | 122.2778 | 122.2321 | -122.4243 | -122.3373 | 122.2595 | 122.3053 | 56.2546 | 58.7814
1016.3125 | 122.5433 | -58.8867 | 63.4094 | -0.34813 | 0.0026212 | 0.064444 | 0.060235 | 0.00034182 | -0.00232 | -0.00072206 | -0.015259 | 0.0044091 | 0.068652 | 0.057721 | -0.005691 | 0.010292 | 0.001818 | -2.6047 | 63.3636 | -58.992 | 63.4048 | -58.6533 | -59.1156 | -59.1019 | -0.10071 | 63.3316 | -58.8913 | 63.4415 | -58.9096 | -59.0195 | -58.8638 | -0.10529 | -0.045777 | -0.004578 | 0.23346 | -0.21515 | -0.22888 | -0.10986 | -0.1236 | -0.004577 | -0.07782 | 0.032043 | -0.022888 | 0.022888 | -0.13275 | 0.027465 | -0.12817 | 0.33875 | 122.3969 | -0.018311 | 122.3328 | 122.3557 | 122.2229 | 122.2504 | 122.2183 | -122.4014 | -122.3007 | 122.2916 | 122.3282 | 56.282 | 58.786
1017.3125 | 122.6257 | -58.873 | 63.3865 | -0.042954 | 0.0039028 | 0.065939 | 0.061517 | 0.0044006 | -0.0018928 | -0.00029486 | -0.064087 | 0.0014185 | 0.06438 | 0.05473 | -0.0052638 | 0.0085833 | -0.0011728 | -2.8152 | 63.3224 | -58.96 | 63.4323 | -58.6395 | -59.0927 | -59.1019 | 0.022888 | 63.2767 | -58.9005 | 63.4872 | -58.8272 | -58.9188 | -58.7906 | -0.086975 | -0.064087 | 0.045776 | 0.23346 | -0.22888 | -0.21973 | -0.14191 | -0.13275 | -0.027466 | -0.10986 | 0.10071 | 0.045777 | 0.082398 | -0.045776 | 0.10986 | -0.01831 | 0.32044 | 122.3923 | 0.073243 | 122.3877 | 122.2824 | 122.1771 | 122.1954 | 122.1497 | -122.3465 | -122.287 | 122.3053 | 122.3602 | 56.0577 | 58.8959
1018.3125 | 122.4976 | -58.8821 | 63.4506 | -0.012436 | 0.0036892 | 0.063589 | 0.059167 | -0.0032898 | -0.004029 | -0.00072206 | -0.05188 | 0.0031273 | 0.066729 | 0.06413 | -0.0063318 | 0.012215 | -0.0054452 | -2.8976 | 63.3728 | -58.9966 | 63.3636 | -58.7265 | -59.1705 | -59.1202 | -0.2243 | 63.3591 | -58.905 | 63.4094 | -58.9371 | -59.0836 | -58.9142 | -0.11444 | -0.07782 | -0.086976 | 0.15564 | -0.23804 | -0.28839 | -0.1236 | -0.17395 | -0.022888 | -0.091553 | -0.041199 | -0.054932 | -0.032044 | -0.20142 | -0.009156 | -0.17853 | 0.27008 | 122.3602 | -0.032044 | 122.3145 | 122.3694 | 122.2641 | 122.2549 | 122.2412 | -122.4472 | -122.3557 | 122.2458 | 122.2916 | 55.9845 | 58.6578
1019.3125 | 122.4564 | -58.8959 | 63.4735 | -0.035324 | 0.0013394 | 0.064444 | 0.06109 | 0.00076902 | -0.0053108 | -0.00029486 | -0.039673 | 0.0014185 | 0.066302 | 0.065198 | -0.0069726 | 0.0092241 | -0.0016 | -3.0258 | 63.382 | -59.0057 | 63.3774 | -58.7128 | -59.1751 | -59.1522 | -0.25177 | 63.3362 | -58.8867 | 63.4003 | -58.9417 | -59.1019 | -58.8959 | -0.10986 | -0.091553 | -0.096131 | 0.1831 | -0.25635 | -0.27924 | -0.14648 | -0.16937 | 0.009155 | -0.13733 | -0.073242 | -0.045776 | 0 | -0.20599 | -0.009155 | -0.21515 | 0.29297 | 122.3831 | -0.054931 | 122.287 | 122.3877 | 122.2229 | 122.2778 | 122.2321 | -122.4792 | -122.3602 | 122.2733 | 122.2961 | 55.8701 | 58.6441
1020.3125 | 122.5021 | -58.8684 | 63.4323 | -0.027695 | 0.001553 | 0.063589 | 0.060876 | 0.0044006 | -0.00232 | -0.0017903 | 0.0030517 | 0.0035547 | 0.068225 | 0.054303 | -0.0054774 | 0.0098651 | -0.0009592 | -3.1586 | 63.3774 | -59.0149 | 63.5284 | -58.461 | -59.2026 | -59.2072 | -0.34332 | 63.3408 | -58.8959 | 63.4048 | -58.9691 | -59.1293 | -58.9096 | -0.14648 | -0.054932 | 0.09613 | 0.40741 | -0.33874 | -0.33417 | -0.19226 | -0.18768 | -0.027466 | -0.091553 | -0.027466 | -0.10071 | -0.041199 | -0.26093 | -0.013733 | -0.23346 | 0.55389 | 122.5433 | -0.073242 | 122.3007 | 122.3923 | 122.2366 | 122.2458 | 122.2092 | -122.4472 | -122.3282 | 122.3969 | 122.2733 | 55.7098 | 58.5251
1021.3125 | 122.4518 | -58.8638 | 63.4552 | -0.08873 | 0.001553 | 0.067434 | 0.057886 | -0.00072638 | -0.0027472 | 0.00034614 | -0.054932 | 0.0020593 | 0.067157 | 0.057721 | -0.0078272 | 0.011361 | -0.0028818 | -3.1769 | 63.3957 | -58.9645 | 63.3591 | -58.7219 | -59.1705 | -59.1293 | -0.33417 | 63.3682 | -58.905 | 63.3865 | -58.9645 | -59.0973 | -58.9233 | -0.10071 | -0.059509 | -0.09613 | 0.14191 | -0.2655 | -0.3067 | -0.16479 | -0.20599 | -0.041198 | -0.086975 | -0.068664 | -0.10071 | -0.059509 | -0.23346 | -0.018311 | -0.19226 | 0.24262 | 122.3236 | -0.05951 | 122.2916 | 122.3602 | 122.2733 | 122.2595 | 122.2321 | -122.4197 | -122.3602 | 122.2229 | 122.2504 | 55.687 | 58.5297
1022.3125 | 122.612 | -58.8272 | 63.4186 | -0.050583 | 0.0030484 | 0.065298 | 0.059167 | -0.0013672 | -0.0031744 | -0.0015765 | 0.030518 | 0.00077755 | 0.066943 | 0.056653 | -0.006759 | 0.0092241 | -0.0062998 | -3.2135 | 63.3408 | -58.9417 | 63.4552 | -58.5846 | -59.0744 | -59.024 | -0.21057 | 63.2904 | -58.8638 | 63.5101 | -58.786 | -58.9188 | -58.7952 | -0.11444 | -0.07782 | 0.036621 | 0.24261 | -0.19684 | -0.24719 | -0.082398 | -0.13275 | -0.036622 | -0.12817 | 0.091553 | 0.041198 | 0.032043 | -0.091553 | 0.068665 | -0.054931 | 0.35706 | 122.3969 | 0.07782 | 122.374 | 122.2824 | 122.1542 | 122.168 | 122.1176 | -122.3602 | -122.2824 | 122.2824 | 122.3373 | 55.6137 | 58.6166
1023.3125 | 122.4701 | -58.8226 | 63.4827 | -0.035324 | 0.001553 | 0.063162 | 0.061731 | -8.538e-05 | -0.0016792 | -0.0017903 | -0.042725 | 0.0024865 | 0.066516 | 0.060712 | -0.0065454 | 0.0096515 | -0.0003182 | -3.3096 | 63.4186 | -58.9325 | 63.4323 | -58.6761 | -59.1064 | -59.0973 | -0.28839 | 63.4003 | -58.873 | 63.4369 | -58.8867 | -59.0286 | -58.873 | -0.10986 | -0.064087 | -0.050354 | 0.14648 | -0.27466 | -0.28381 | -0.16479 | -0.17395 | -0.050354 | -0.082397 | -0.045776 | -0.064087 | -0.050354 | -0.20599 | 0 | -0.15564 | 0.25635 | 122.3648 | -0.013733 | 122.3099 | 122.3511 | 122.2733 | 122.2412 | 122.2229 | -122.4152 | -122.3557 | 122.2549 | 122.2595 | 55.513 | 58.5342
1024.3125 | 122.4884 | -58.8638 | 63.4872 | -0.17265 | 0.0006986 | 0.063376 | 0.059381 | -0.00051278 | -0.0018928 | -0.0039265 | -0.015259 | 0.0041955 | 0.066516 | 0.057721 | -0.0069726 | 0.0090105 | -0.0011728 | -3.3508 | 63.4369 | -58.9508 | 63.3545 | -58.7311 | -59.1705 | -59.1293 | -0.42572 | 63.3865 | -58.873 | 63.414 | -58.9233 | -59.0652 | -58.8913 | -0.086975 | -0.050354 | -0.13275 | 0.13275 | -0.2655 | -0.3067 | -0.17853 | -0.21973 | -0.009155 | -0.10071 | -0.073243 | -0.059509 | -0.027465 | -0.20142 | -0.01831 | -0.19226 | 0.21973 | 122.3053 | -0.050354 | 122.287 | 122.3877 | 122.2595 | 122.3007 | 122.2504 | -122.4381 | -122.3602 | 122.2183 | 122.2778 | 55.513 | 58.4381
1025.3125 | 122.4976 | -58.8455 | 63.4689 | -0.08873 | 0.0009122 | 0.065298 | 0.060235 | -0.0024354 | -0.0036018 | -0.0020039 | -0.015259 | 0.0018457 | 0.06438 | 0.063489 | -0.0052638 | 0.0092241 | -0.0024546 | -3.4561 | 63.4369 | -58.9508 | 63.3682 | -58.7219 | -59.1843 | -59.1339 | -0.45319 | 63.3774 | -58.8913 | 63.4323 | -58.9096 | -59.0378 | -58.8821 | -0.10529 | -0.032043 | -0.10071 | 0.1236 | -0.28839 | -0.33875 | -0.1831 | -0.23346 | -0.045776 | -0.091553 | -0.036621 | -0.064087 | -0.036621 | -0.19226 | 0.009155 | -0.14649 | 0.22888 | 122.319 | -0.018311 | 122.3236 | 122.3877 | 122.2687 | 122.2824 | 122.2229 | -122.4197 | -122.3602 | 122.2137 | 122.2778 | 55.3894 | 58.3923
1026.3125 | 122.4884 | -58.8638 | 63.4598 | -0.042954 | 0.0017666 | 0.061667 | 0.05874 | 0.0016236 | -0.0027472 | 0.00098694 | -0.01831 | 0.0020593 | 0.065448 | 0.054089 | -0.0054774 | 0.010292 | -0.0013864 | -3.5065 | 63.4598 | -58.9508 | 63.3774 | -58.7128 | -59.1797 | -59.1293 | -0.47607 | 63.382 | -58.8638 | 63.4323 | -58.9005 | -59.0424 | -58.8547 | -0.086975 | 0 | -0.082398 | 0.15106 | -0.2655 | -0.31586 | -0.17853 | -0.22888 | 0 | -0.07782 | -0.027466 | -0.036621 | 0.009156 | -0.17853 | 0.009156 | -0.17853 | 0.23804 | 122.3282 | -0.036621 | 122.2961 | 122.4106 | 122.2458 | 122.3236 | 122.2458 | -122.4106 | -122.3236 | 122.2412 | 122.2961 | 55.3574 | 58.3878
1027.3125 | 122.493 | -58.8547 | 63.4827 | -0.073471 | 0.0013394 | 0.065298 | 0.060235 | 0.0029052 | -0.0053108 | -0.0017903 | -0.036621 | 0.0016321 | 0.06502 | 0.05943 | -0.0048364 | 0.0083697 | -0.0020272 | -3.5339 | 63.4506 | -58.9371 | 63.3728 | -58.7036 | -59.1614 | -59.1293 | -0.51727 | 63.414 | -58.8501 | 63.4415 | -58.8959 | -59.0378 | -58.8455 | -0.082398 | -0.032043 | -0.10986 | 0.15106 | -0.27466 | -0.3067 | -0.19226 | -0.2243 | 0.004577 | -0.068665 | -0.041199 | -0.041199 | 0.009155 | -0.18311 | 0.004578 | -0.18768 | 0.23346 | 122.3099 | -0.045776 | 122.2916 | 122.3877 | 122.2641 | 122.3053 | 122.2687 | -122.4197 | -122.3328 | 122.2275 | 122.2961 | 55.3207 | 58.3374
1028.3125 | 122.4564 | -58.8318 | 63.4827 | -0.042954 | 0.0030484 | 0.062308 | 0.061303 | 0.0022644 | -0.0025336 | -0.0013629 | -0.048828 | 0.0022729 | 0.066729 | 0.057935 | -0.0074 | 0.010933 | -0.0028818 | -3.653 | 63.4369 | -58.9096 | 63.4048 | -58.7128 | -59.1522 | -59.1156 | -0.5722 | 63.4048 | -58.8455 | 63.4277 | -58.9371 | -59.0652 | -58.8776 | -0.07782 | -0.045776 | -0.07782 | 0.11902 | -0.28381 | -0.32044 | -0.20599 | -0.24262 | -0.013733 | -0.07782 | -0.054932 | -0.10529 | -0.045776 | -0.23346 | -0.032043 | -0.21973 | 0.19684 | 122.3145 | -0.091553 | 122.2733 | 122.3465 | 122.2504 | 122.2687 | 122.2366 | -122.3923 | -122.3282 | 122.2366 | 122.2595 | 55.1788 | 58.2596
1029.3125 | 122.4609 | -58.8318 | 63.4918 | -0.042954 | 0.0028348 | 0.063803 | 0.061303 | 0.00098262 | -0.0053108 | -0.0030719 | -0.048828 | 0.0031273 | 0.066729 | 0.06477 | -0.0071864 | 0.010079 | -0.0007456 | -3.6987 | 63.4506 | -58.9233 | 63.3957 | -58.6853 | -59.1293 | -59.1019 | -0.59509 | 63.4186 | -58.8455 | 63.414 | -58.9233 | -59.0652 | -58.8821 | -0.091553 | -0.041198 | -0.09613 | 0.14648 | -0.27008 | -0.29755 | -0.17853 | -0.20599 | -0.013733 | -0.073242 | -0.07782 | -0.091553 | -0.050354 | -0.23346 | -0.036621 | -0.21973 | 0.23804 | 122.319 | -0.07782 | 122.2595 | 122.374 | 122.2641 | 122.2824 | 122.2504 | -122.4152 | -122.3373 | 122.2275 | 122.2458 | 55.1331 | 58.2367
1030.3125 | 122.5296 | -58.7952 | 63.4964 | -0.020065 | 0.0002714 | 0.062308 | 0.059381 | 0.0050414 | -0.0044562 | -0.00050846 | -8.6e-08 | 0.0014185 | 0.066729 | 0.056439 | -0.0037684 | 0.010933 | 0.0003226 | -3.8177 | 63.446 | -58.9005 | 63.4232 | -58.6487 | -59.1064 | -59.0836 | -0.60425 | 63.3957 | -58.8272 | 63.5147 | -58.8272 | -58.9645 | -58.8043 | -0.10529 | -0.050354 | -0.073242 | 0.14648 | -0.28839 | -0.31128 | -0.1831 | -0.20599 | -0.032043 | -0.10071 | 0.01831 | -0.032043 | -0.009155 | -0.16937 | 0.022888 | -0.13733 | 0.25177 | 122.3236 | 0 | 122.3419 | 122.3465 | 122.2229 | 122.2412 | 122.1909 | -122.3969 | -122.3236 | 122.2183 | 122.3099 | 54.9774 | 58.1909
1031.3125 | 122.5388 | -58.7906 | 63.4872 | -0.08873 | 0.001553 | 0.064871 | 0.060022 | 0.0016236 | -0.0042426 | -0.0024311 | -0.024414 | 0.0031273 | 0.066729 | 0.05708 | -0.0059046 | 0.0094379 | -0.0048044 | -3.8498 | 63.4644 | -58.9188 | 63.4277 | -58.6533 | -59.1156 | -59.0607 | -0.65918 | 63.4048 | -58.8226 | 63.4872 | -58.8409 | -58.9828 | -58.7906 | -0.12817 | -0.022889 | -0.05951 | 0.13733 | -0.27008 | -0.32501 | -0.14191 | -0.19684 | -0.032044 | -0.082398 | 0 | -0.050354 | 0 | -0.19226 | 0.032044 | -0.16022 | 0.2655 | 122.3465 | -0.01831 | 122.3099 | 122.3831 | 122.2275 | 122.2549 | 122.1954 | -122.406 | -122.3099 | 122.2183 | 122.2778 | 54.9408 | 58.1314
1032.3125 | 122.5159 | -58.7997 | 63.4964 | -0.10399 | 0.0019802 | 0.062948 | 0.060876 | -8.538e-05 | -0.003388 | 0.0018413 | -0.012207 | 0.0022729 | 0.06737 | 0.058789 | -0.0061182 | 0.011361 | -0.0001046 | -3.8773 | 63.4506 | -58.9005 | 63.414 | -58.6533 | -59.111 | -59.0744 | -0.71411 | 63.4094 | -58.7997 | 63.4964 | -58.8409 | -58.9874 | -58.7997 | -0.10071 | -0.045776 | -0.082398 | 0.14648 | -0.27466 | -0.31128 | -0.17395 | -0.21057 | 0 | -0.086975 | 0 | -0.041198 | 0 | -0.18768 | 0 | -0.18768 | 0.24719 | 122.3145 | -0.041198 | 122.2961 | 122.3511 | 122.2092 | 122.2504 | 122.2092 | -122.3969 | -122.2961 | 122.2137 | 122.2961 | 54.9225 | 58.0856
1033.3125 | 122.4838 | -58.786 | 63.5696 | -0.012436 | 0.0034756 | 0.063376 | 0.060663 | -0.0017944 | -0.0048834 | -0.0026447 | -0.048828 | 0.00077755 | 0.06502 | 0.061993 | -0.0080408 | 0.011574 | 0.0009634 | -3.9276 | 63.4735 | -58.8959 | 63.4048 | -58.6624 | -59.1385 | -59.1019 | -0.73242 | 63.4415 | -58.8455 | 63.4277 | -58.8181 | -58.9737 | -58.8364 | -0.10986 | -0.09613 | -0.16479 | 0.1236 | -0.31586 | -0.35248 | -0.20599 | -0.24262 | -0.059509 | -0.12817 | -0.14191 | -0.032043 | -0.050354 | -0.18768 | 0.009155 | -0.12817 | 0.23346 | 122.3007 | 0.027466 | 122.2733 | 122.3694 | 122.287 | 122.2595 | 122.2275 | -122.4655 | -122.4152 | 122.1909 | 122.2137 | 54.8584 | 58.0536
1034.3125 | 122.5113 | -58.8043 | 63.533 | -0.058212 | -0.0014376 | 0.06423 | 0.06109 | 0.002478 | -0.0048834 | -0.0034991 | -0.036621 | 0.0033411 | 0.066729 | 0.059003 | -0.0052638 | 0.0094379 | -0.0022408 | -3.9688 | 63.4827 | -58.8913 | 63.4323 | -58.6487 | -59.0973 | -59.0652 | -0.83313 | 63.4415 | -58.7997 | 63.4872 | -58.8318 | -58.9828 | -58.7997 | -0.086975 | -0.050354 | -0.10071 | 0.15564 | -0.26093 | -0.29297 | -0.17395 | -0.20599 | 0.004577 | -0.091553 | -0.045776 | -0.027466 | 0.004577 | -0.17853 | 0 | -0.18311 | 0.24261 | 122.3236 | -0.032043 | 122.287 | 122.374 | 122.2412 | 122.287 | 122.2458 | -122.4243 | -122.3328 | 122.2366 | 122.2916 | 54.8355 | 57.9712
1035.3125 | 122.5021 | -58.754 | 63.5559 | 0.19356 | 0.0017666 | 0.063376 | 0.061517 | -8.538e-05 | -0.0025336 | -0.0022175 | -0.05188 | 0.0020593 | 0.067798 | 0.057935 | -0.0071864 | 0.0096515 | -0.0009592 | -4.0512 | 63.5193 | -58.8776 | 63.4506 | -58.6624 | -59.1064 | -59.0378 | -0.90637 | 63.4552 | -58.786 | 63.501 | -58.8547 | -58.992 | -58.8181 | -0.1236 | -0.036621 | -0.10529 | 0.091552 | -0.28381 | -0.35248 | -0.16022 | -0.22888 | -0.032044 | -0.10071 | -0.054931 | -0.10071 | -0.064087 | -0.23804 | -0.032043 | -0.20599 | 0.21515 | 122.3282 | -0.068664 | 122.287 | 122.3969 | 122.2412 | 122.2733 | 122.2092 | -122.4335 | -122.3419 | 122.2046 | 122.2549 | 54.7028 | 57.8476
1036.3125 | 122.5067 | -58.7769 | 63.5422 | -0.08873 | 0.0019802 | 0.062948 | 0.062158 | 0.00034182 | -0.0053108 | -0.0026447 | -0.015259 | 0.0027001 | 0.068225 | 0.058575 | -0.00505 | 0.010506 | 0.0024588 | -4.1473 | 63.4872 | -58.8684 | 63.6246 | -58.7082 | -59.1293 | -58.992 | -0.97046 | 63.4735 | -58.754 | 63.4964 | -58.8455 | -58.9874 | -58.7814 | -0.091553 | -0.054931 | 0.082398 | 0.068664 | -0.21515 | -0.35248 | -0.1236 | -0.26093 | 0.022888 | -0.068664 | -0.045776 | -0.068665 | -0.004578 | -0.21057 | -0.027466 | -0.23346 | 0.16022 | 122.493 | -0.091553 | 122.2504 | 122.3557 | 122.2275 | 122.2641 | 122.2504 | -122.4106 | -122.2961 | 122.4014 | 122.2733 | 54.6295 | 57.8064
1037.3125 | 122.58 | -58.7311 | 63.5147 | -0.12688 | 0.0034756 | 0.064871 | 0.057458 | 0.0014098 | -0.0042426 | -8.1264e-05 | 0.064087 | 0.0020593 | 0.066943 | 0.058789 | -0.0063318 | 0.01072 | -0.0013864 | -4.1245 | 63.4598 | -58.8409 | 63.5742 | -58.4656 | -58.9828 | -58.9188 | -0.86517 | 63.4186 | -58.7311 | 63.5971 | -58.7128 | -58.8547 | -58.7082 | -0.10986 | -0.054931 | 0.05951 | 0.2655 | -0.18768 | -0.25177 | -0.07782 | -0.14191 | 0 | -0.09613 | 0.082398 | 0.01831 | 0.022888 | -0.1236 | 0.022888 | -0.1236 | 0.37537 | 122.4152 | 0.01831 | 122.3282 | 122.3007 | 122.1497 | 122.1909 | 122.1497 | -122.3557 | -122.2458 | 122.3053 | 122.3282 | 54.6066 | 57.8659
1038.3125 | 122.4976 | -58.7585 | 63.5925 | -0.035324 | 0.002194 | 0.064444 | 0.060876 | 0.0029052 | -0.0036018 | -0.0032855 | -0.036621 | 0.0020593 | 0.066516 | 0.062207 | -0.0037684 | 0.0047381 | -0.0039498 | -4.248 | 63.5147 | -58.8638 | 63.4369 | -58.6258 | -59.1019 | -59.0561 | -1.1215 | 63.4735 | -58.7769 | 63.7207 | -58.8501 | -59.0378 | -58.8272 | -0.10529 | -0.07782 | -0.15564 | 0.13275 | -0.29755 | -0.34332 | -0.19226 | -0.23804 | -0.01831 | -0.11902 | 0.12817 | -0.091553 | -0.068664 | -0.27924 | -0.050354 | -0.26093 | 0.23804 | 122.3007 | -0.073243 | 122.4976 | 122.3785 | 122.2504 | 122.2733 | 122.2321 | -122.4564 | -122.3694 | 122.1954 | 122.4792 | 54.5105 | 57.637
1039.3125 | 122.4884 | -58.7494 | 63.5468 | 0.04097 | 0.0024076 | 0.062094 | 0.05874 | 0.0018372 | -0.004029 | -0.00072206 | -0.061035 | 0.0014185 | 0.067584 | 0.05943 | -0.0082544 | 0.0098651 | -0.0035226 | -4.3304 | 63.5193 | -58.8638 | 63.4369 | -58.6121 | -59.0973 | -59.0286 | -1.1444 | 63.4827 | -58.754 | 63.533 | -58.8181 | -58.9371 | -58.7769 | -0.11444 | -0.027466 | -0.10986 | 0.13733 | -0.27923 | -0.3479 | -0.16479 | -0.23346 | -0.004577 | -0.064087 | -0.013733 | -0.068664 | -0.027465 | -0.18768 | -0.022888 | -0.18311 | 0.25177 | 122.3007 | -0.064087 | 122.287 | 122.3831 | 122.2366 | 122.2687 | 122.2321 | -122.4106 | -122.3007 | 122.1863 | 122.2824 | 54.4189 | 57.605
1040.3125 | 122.5067 | -58.7677 | 63.5788 | 0.04097 | 0.0019802 | 0.062094 | 0.062585 | 0.0018372 | -0.0014654 | -0.0013629 | -0.027466 | 0.0033411 | 0.067798 | 0.05943 | -0.0065454 | 0.0096515 | -0.0003182 | -4.1611 | 63.5422 | -58.8318 | 63.4872 | -58.5754 | -59.0744 | -59.0286 | -1.236 | 63.4781 | -58.754 | 63.5239 | -58.8043 | -58.9508 | -58.7769 | -0.064087 | -0.036621 | -0.091552 | 0.19226 | -0.26093 | -0.3067 | -0.19684 | -0.24262 | 0.013733 | -0.10071 | -0.054931 | -0.036621 | -0.009155 | -0.18311 | -0.022888 | -0.19684 | 0.25635 | 122.319 | -0.050354 | 122.2778 | 122.374 | 122.2321 | 122.3099 | 122.2458 | -122.4106 | -122.3328 | 122.2549 | 122.2916 | 54.6066 | 57.5317
1041.3125 | 122.4655 | -58.7448 | 63.5559 | -0.050583 | 0.0030484 | 0.065298 | 0.057886 | -0.0032898 | -0.0010382 | 0.00034614 | -0.054932 | 0.0014185 | 0.066089 | 0.061352 | -0.0071864 | 0.0098651 | -0.000532 | -4.3304 | 63.5056 | -58.8776 | 63.4552 | -58.5114 | -59.0469 | -59.0515 | -1.3 | 63.4964 | -58.7723 | 63.5468 | -58.7997 | -58.9417 | -58.7402 | -0.13275 | -0.050354 | -0.10071 | 0.23346 | -0.3067 | -0.30212 | -0.17395 | -0.16937 | -0.027466 | -0.059509 | -0.009155 | -0.054932 | 0.004578 | -0.19684 | 0.032044 | -0.16937 | 0.36621 | 122.3328 | -0.027466 | 122.319 | 122.3831 | 122.2687 | 122.2504 | 122.2412 | -122.4335 | -122.3282 | 122.2 | 122.2916 | 54.4144 | 57.4448
1042.3125 | 122.5754 | -58.699 | 63.5468 | -0.081101 | 0.0028348 | 0.064444 | 0.057672 | -0.003717 | -0.0012518 | -0.00072206 | 0.042725 | -7.6854e-05 | 0.066729 | 0.051739 | -0.0063318 | 0.0075153 | 0.001177 | -4.4037 | 63.5147 | -58.8043 | 63.5788 | -58.4198 | -58.9279 | -58.9096 | -1.2405 | 63.4506 | -58.7128 | 63.6292 | -58.6899 | -58.8089 | -58.6899 | -0.10529 | -0.032044 | 0.032043 | 0.27924 | -0.21057 | -0.22888 | -0.10529 | -0.1236 | -0.013733 | -0.09613 | 0.082397 | 0.009156 | 0.009156 | -0.10986 | 0.022889 | -0.09613 | 0.38452 | 122.3831 | 0.022889 | 122.3419 | 122.319 | 122.1634 | 122.2137 | 122.1497 | -122.3511 | -122.2595 | 122.2778 | 122.3282 | 54.2953 | 57.4585
1043.3125 | 122.5021 | -58.6807 | 63.6154 | 0.0028229 | 0.002194 | 0.065085 | 0.060663 | 0.0014098 | -0.004029 | -0.0022175 | -0.073242 | 0.0020593 | 0.064807 | 0.063489 | -0.006759 | 0.011147 | -0.0007456 | -4.4083 | 63.5376 | -58.7952 | 63.5742 | -58.4793 | -58.9554 | -58.9279 | -1.3184 | 63.5147 | -58.7082 | 63.6017 | -58.7311 | -58.8593 | -58.699 | -0.11444 | -0.077819 | -0.041198 | 0.20142 | -0.24719 | -0.27466 | -0.13275 | -0.16022 | -0.027466 | -0.10071 | -0.013732 | -0.050354 | -0.018311 | -0.17853 | 0.009155 | -0.15106 | 0.31586 | 122.3694 | -0.022888 | 122.3099 | 122.3328 | 122.2229 | 122.2183 | 122.1954 | -122.4106 | -122.3236 | 122.2549 | 122.2824 | 54.2725 | 57.3624
1044.3125 | 122.4564 | -58.7219 | 63.6292 | -0.12688 | 0.0045438 | 0.063162 | 0.059381 | -8.538e-05 | -0.0055244 | -0.00072206 | -0.0030517 | 0.0012047 | 0.067584 | 0.056226 | -0.0059046 | 0.010933 | -0.0016 | -4.5502 | 63.5559 | -58.8318 | 63.4872 | -58.5983 | -59.2163 | -59.3262 | -1.3092 | 63.5422 | -58.7036 | 63.5513 | -58.7677 | -58.9279 | -58.754 | -0.10986 | -0.073242 | -0.14191 | 0.1236 | -0.60425 | -0.49439 | -0.49439 | -0.38452 | 0.018311 | -0.086975 | -0.077819 | -0.045776 | -0.032043 | -0.20599 | -0.050354 | -0.2243 | 0.23346 | 122.319 | -0.064087 | 122.2549 | 122.3877 | 122.2458 | 122.2778 | 122.2641 | -122.4609 | -122.3328 | 122.2092 | 122.2733 | 54.1718 | 57.4127
1045.3125 | 122.4976 | -58.7082 | 63.588 | -0.020065 | 0.002194 | 0.06423 | 0.062372 | 0.0035462 | -0.0021064 | 0.00013254 | -0.039673 | 0.0022729 | 0.064593 | 0.06477 | -0.0046228 | 0.0096515 | -0.0001046 | -4.5868 | 63.5468 | -58.8364 | 63.5284 | -58.5251 | -59.0378 | -58.9966 | -1.6205 | 63.5101 | -58.7128 | 63.5834 | -58.7494 | -58.873 | -58.7128 | -0.12817 | -0.041199 | -0.05951 | 0.18311 | -0.28839 | -0.32959 | -0.16022 | -0.20142 | -0.004578 | -0.07782 | -0.004578 | -0.041199 | -0.004578 | -0.16479 | 0 | -0.16022 | 0.31128 | 122.3648 | -0.036621 | 122.2961 | 122.3831 | 122.2229 | 122.2549 | 122.2183 | -122.4243 | -122.3007 | 122.2366 | 122.2916 | 54.1214 | 57.0877
1046.3125 | 122.4884 | -58.699 | 63.5971 | -0.073471 | 0.0019802 | 0.064871 | 0.059808 | 0.00098262 | -0.0016792 | -0.00072206 | -0.021362 | 0.0020593 | 0.068652 | 0.054944 | -0.005691 | 0.0096515 | -0.0037362 | -4.6463 | 63.5788 | -58.8318 | 63.5239 | -58.5251 | -59.0286 | -58.9737 | -1.6983 | 63.5239 | -58.699 | 63.5834 | -58.7448 | -58.9096 | -58.7128 | -0.13275 | -0.018311 | -0.073242 | 0.17395 | -0.27466 | -0.32959 | -0.14191 | -0.19684 | 0 | -0.073242 | -0.013733 | -0.045776 | -0.013733 | -0.21057 | -0.013733 | -0.21057 | 0.3067 | 122.3557 | -0.045776 | 122.2824 | 122.4106 | 122.2229 | 122.2778 | 122.2229 | -122.4289 | -122.2961 | 122.2229 | 122.2824 | 54.0527 | 57.0007
1047.3125 | 122.5891 | -58.6761 | 63.5742 | -0.073471 | 0.0024076 | 0.066366 | 0.05874 | -8.538e-05 | -0.0027472 | -0.0011493 | -0.07019 | 0.0020593 | 0.064593 | 0.058148 | -0.010177 | 0.0092241 | -0.0062998 | -4.6371 | 63.533 | -58.7997 | 63.6429 | -58.3923 | -58.8913 | -58.8455 | -1.7303 | 63.4552 | -58.699 | 63.6978 | -58.6258 | -58.7265 | -58.5571 | -0.1236 | -0.041199 | 0.068664 | 0.28381 | -0.16937 | -0.21515 | -0.045776 | -0.091552 | -0.022889 | -0.11902 | 0.1236 | 0.050354 | 0.11902 | -0.050354 | 0.14191 | -0.027465 | 0.40741 | 122.4426 | 0.073243 | 122.3969 | 122.3328 | 122.1542 | 122.2092 | 122.1313 | -122.374 | -122.2733 | 122.319 | 122.374 | 54.039 | 56.9458
1048.3125 | 122.5479 | -58.7265 | 63.6566 | -0.11162 | 0.0043302 | 0.063162 | 0.06109 | 0.00098262 | -0.005097 | 0.00034614 | -0.076294 | 0.0024865 | 0.066729 | 0.061566 | -0.0076136 | 0.010292 | -0.005018 | -4.7241 | 63.588 | -58.8043 | 63.5239 | -58.5297 | -59.0057 | -58.9691 | -1.8951 | 63.5651 | -58.7173 | 63.5651 | -58.7677 | -59.2941 | -59.0195 | -0.07782 | -0.068664 | -0.13275 | 0.19684 | -0.24262 | -0.27924 | -0.16479 | -0.20142 | 0.009155 | -0.091553 | -0.091553 | -0.041199 | -0.29297 | -0.56763 | -0.30212 | -0.57678 | 0.27466 | 122.3282 | -0.050354 | 122.2824 | 122.3923 | 122.2824 | 122.3145 | 122.2916 | -122.4609 | -122.374 | 122.2504 | 122.2916 | 54.0024 | 56.8314
1049.3125 | 122.4838 | -58.6716 | 63.6475 | -0.020065 | 0.0047574 | 0.06188 | 0.061303 | -0.0035034 | -0.0042426 | 0.0016277 | -0.039673 | 0.00056395 | 0.062671 | 0.062848 | -0.005691 | 0.011788 | -0.0045908 | -4.8752 | 63.5834 | -58.7814 | 63.5193 | -58.5342 | -59.0103 | -58.9417 | -1.9867 | 63.5605 | -58.7082 | 63.5925 | -58.7265 | -58.8867 | -58.7128 | -0.10986 | -0.064087 | -0.12817 | 0.13733 | -0.27008 | -0.33874 | -0.16022 | -0.22888 | -0.036621 | -0.086975 | -0.054932 | -0.054931 | -0.041199 | -0.21515 | -0.004578 | -0.17853 | 0.24719 | 122.3007 | -0.01831 | 122.3007 | 122.3648 | 122.2687 | 122.2549 | 122.2321 | -122.4289 | -122.3557 | 122.1909 | 122.2641 | 53.7964 | 56.6849
1050.3125 | 122.4884 | -58.6853 | 63.652 | -0.096359 | 0.0024076 | 0.064016 | 0.06344 | -0.0022218 | -0.003388 | -0.0047809 | -0.064087 | 0.0016321 | 0.065661 | 0.060712 | -0.0069726 | 0.012642 | -0.0024546 | -4.8889 | 63.62 | -58.7769 | 63.5696 | -58.4839 | -58.9645 | -58.9737 | -2.092 | 63.588 | -58.6853 | 63.5834 | -58.7448 | -58.9005 | -58.7219 | -0.091552 | -0.032044 | -0.082398 | 0.20142 | -0.28839 | -0.27924 | -0.19684 | -0.18768 | 0 | -0.064087 | -0.068665 | -0.059509 | -0.036621 | -0.21515 | -0.036621 | -0.21515 | 0.29297 | 122.3465 | -0.059509 | 122.2687 | 122.3969 | 122.2733 | 122.3053 | 122.2733 | -122.4289 | -122.3373 | 122.2549 | 122.2687 | 53.7964 | 56.5933
1051.3125 | 122.493 | -58.6807 | 63.6566 | -0.073471 | 0.0019802 | 0.061026 | 0.057458 | -0.0015808 | -0.0065924 | -0.0024311 | -0.01831 | 0.0020593 | 0.068011 | 0.061352 | -0.0065454 | 0.0096515 | -0.0011728 | -5.1453 | 63.5559 | -58.8364 | 63.5468 | -58.4106 | -59.0332 | -58.9645 | -2.2156 | 63.5559 | -58.7036 | 63.6154 | -58.7173 | -58.8547 | -58.6853 | -0.15564 | -0.10071 | -0.10986 | 0.27008 | -0.28381 | -0.35248 | -0.12817 | -0.19684 | -0.022888 | -0.10071 | -0.041199 | -0.036621 | -0.004578 | -0.17395 | 0.01831 | -0.15106 | 0.42572 | 122.3831 | -0.013733 | 122.319 | 122.3923 | 122.2595 | 122.2366 | 122.2366 | -122.493 | -122.3602 | 122.2275 | 122.2961 | 53.5355 | 56.4651
1052.3125 | 122.5662 | -58.5983 | 63.62 | -0.10399 | 0.0019802 | 0.063376 | 0.057458 | 0.0014098 | -0.00232 | -0.0039265 | 0.064087 | -0.00029045 | 0.066089 | 0.060284 | -0.0061182 | 0.0087969 | 0.0030996 | -5.0125 | 63.5834 | -58.7311 | 63.62 | -58.374 | -58.8776 | -58.8409 | -2.2339 | 63.533 | -58.667 | 63.7344 | -58.4335 | -58.8318 | -58.6899 | -0.13275 | -0.036621 | 0 | 0.22431 | -0.24261 | -0.27923 | -0.10986 | -0.14648 | -0.068664 | -0.086975 | 0.11444 | 0.1648 | -0.091552 | -0.23346 | -0.022888 | -0.16479 | 0.35706 | 122.3511 | 0.23346 | 122.4014 | 122.3145 | 122.2 | 122.1817 | 122.1313 | -122.3511 | -122.287 | 122.2183 | 122.3328 | 53.5858 | 56.3644
1053.3125 | 122.4426 | -58.6578 | 63.6749 | -0.08873 | 0.0019802 | 0.065725 | 0.059595 | -0.0011536 | 0.00088444 | -0.0015765 | -0.033569 | 0.0024865 | 0.066729 | 0.060498 | -0.0074 | 0.010292 | -0.0020272 | -5.1132 | 63.6154 | -58.786 | 63.5696 | -58.1451 | -58.7906 | -58.9874 | -2.3849 | 63.6017 | -58.667 | 63.62 | -58.7082 | -58.8867 | -58.7082 | -0.12817 | -0.05951 | -0.10529 | 0.5127 | -0.32959 | -0.13275 | -0.20142 | -0.004577 | -0.009155 | -0.073242 | -0.054932 | -0.050354 | -0.050354 | -0.22888 | -0.041199 | -0.21973 | 0.64087 | 122.3557 | -0.041199 | 122.287 | 122.4014 | 122.2687 | 122.2733 | 122.2595 | -122.4609 | -122.3419 | 122.2275 | 122.2778 | 53.5446 | 56.2729
1054.3125 | 122.5342 | -58.6533 | 63.6795 | -0.12688 | 0.0017666 | 0.062948 | 0.061303 | -0.0011536 | -0.0031744 | -0.0039265 | -0.042725 | 0.0024865 | 0.066302 | 0.06178 | -0.0074 | 0.0094379 | 0.0003226 | -5.1773 | 63.6154 | -58.786 | 63.5788 | -58.4381 | -58.9737 | -58.9188 | -2.504 | 63.5696 | -58.6487 | 63.6566 | -58.6716 | -58.7952 | -58.6304 | -0.13275 | -0.064087 | -0.10071 | 0.21515 | -0.2655 | -0.32044 | -0.13275 | -0.18768 | 0.004577 | -0.10986 | -0.022888 | -0.018311 | 0.022888 | -0.14191 | 0.018311 | -0.14648 | 0.3479 | 122.3648 | -0.022888 | 122.3053 | 122.4014 | 122.2183 | 122.2687 | 122.2229 | -122.4655 | -122.3282 | 122.2321 | 122.3099 | 53.476 | 56.1493
1055.3125 | 122.5342 | -58.6258 | 63.6658 | -0.073471 | 0.0030484 | 0.063376 | 0.061517 | -0.0035034 | -0.0036018 | 0.0018413 | -0.024414 | 0.0022729 | 0.064593 | 0.064343 | -0.0065454 | 0.011361 | -0.0035226 | -5.2322 | 63.6429 | -58.7494 | 63.5925 | -58.4381 | -58.9508 | -58.9096 | -2.623 | 63.588 | -58.6761 | 63.6612 | -58.6578 | -58.8043 | -58.6166 | -0.1236 | -0.022888 | -0.073242 | 0.18768 | -0.28381 | -0.32501 | -0.16022 | -0.20142 | -0.050354 | -0.077819 | -0.004577 | -0.032044 | 0.009155 | -0.17853 | 0.059509 | -0.12817 | 0.31128 | 122.3419 | 0.01831 | 122.3373 | 122.3923 | 122.2641 | 122.2687 | 122.2137 | -122.4152 | -122.3419 | 122.2183 | 122.287 | 53.3936 | 56.0028
1056.3125 | 122.5021 | -58.6395 | 63.6841 | -0.11162 | 0.0024076 | 0.062948 | 0.06109 | 0.0011962 | -0.0010382 | 0.0014141 | -0.027466 | 0.0035547 | 0.066943 | 0.060712 | -0.0054774 | 0.0094379 | -0.003309 | -5.3055 | 63.652 | -58.7402 | 63.6017 | -58.4244 | -58.9233 | -58.8821 | -2.7557 | 63.588 | -58.6441 | 63.6932 | -58.6487 | -58.7997 | -58.6121 | -0.10071 | -0.032043 | -0.082397 | 0.21515 | -0.24262 | -0.28381 | -0.14191 | -0.18311 | -0.004578 | -0.09613 | 0.009155 | -0.009156 | 0.027465 | -0.16022 | 0.032043 | -0.15564 | 0.31586 | 122.3419 | -0.004578 | 122.3373 | 122.3923 | 122.2321 | 122.2916 | 122.2275 | -122.4243 | -122.3282 | 122.2412 | 122.3328 | 53.334 | 55.8838
1057.3125 | 122.4792 | -58.6212 | 63.7161 | -0.081101 | 0.0058256 | 0.063803 | 0.061944 | 0.0011962 | -0.00061096 | 0.0012005 | -0.10986 | 0.00077755 | 0.066302 | 0.059003 | -0.0041956 | 0.0083697 | -0.003309 | -5.397 | 63.652 | -58.7311 | 63.3682 | -58.6304 | -58.5022 | -58.6624 | -2.8381 | 63.6337 | -58.6029 | 63.6429 | -58.6716 | -58.8364 | -58.6487 | -0.10986 | -0.064086 | -0.3479 | -0.009155 | -0.041199 | 0.11902 | 0.068664 | 0.22888 | 0.018311 | -0.082397 | -0.073242 | -0.050354 | -0.027466 | -0.21515 | -0.045777 | -0.23346 | 0.10071 | 122.0993 | -0.068665 | 122.2458 | 122.3831 | 122.2366 | 122.2733 | 122.2549 | -122.4472 | -122.319 | 121.9894 | 122.2641 | 53.2242 | 55.7831
1058.3125 | 122.4838 | -58.6166 | 63.6795 | -0.073471 | 0.0043302 | 0.063589 | 0.059808 | -0.003717 | -0.0021064 | -0.0028583 | -0.015259 | 0.0022729 | 0.066302 | 0.057721 | -0.0059046 | 0.0098651 | 0.000109 | -5.4749 | 63.6749 | -58.7219 | 63.6154 | -58.3786 | -58.9188 | -58.873 | -2.98 | 63.6154 | -58.6258 | 63.6841 | -58.6258 | -58.7723 | -58.6121 | -0.10529 | -0.004577 | -0.064087 | 0.23804 | -0.25635 | -0.30212 | -0.15106 | -0.19684 | -0.009155 | -0.064087 | 0.004578 | -0.009155 | 0.004577 | -0.15564 | 0.013732 | -0.14648 | 0.34332 | 122.3373 | 0 | 122.3099 | 122.3969 | 122.2412 | 122.2916 | 122.2321 | -122.4014 | -122.3053 | 122.2321 | 122.3007 | 53.1418 | 55.6366
1059.3125 | 122.612 | -58.5892 | 63.6703 | -0.050583 | 0.0028348 | 0.064444 | 0.059808 | 0.0031188 | -0.0027472 | -0.0024311 | -0.0061035 | 0.0018457 | 0.064166 | 0.058362 | -0.006759 | 0.010079 | -0.0030954 | -5.5618 | 63.6063 | -58.7082 | 63.6841 | -58.3282 | -58.8455 | -58.7997 | -3.0212 | 63.5925 | -58.5983 | 63.7711 | -58.5388 | -58.6899 | -58.5068 | -0.11902 | -0.064087 | 0.013733 | 0.26093 | -0.21057 | -0.25635 | -0.091553 | -0.13733 | -0.009156 | -0.07782 | 0.10071 | 0.050354 | 0.082397 | -0.10071 | 0.091553 | -0.091552 | 0.37994 | 122.3923 | 0.05951 | 122.3694 | 122.3145 | 122.1909 | 122.1954 | 122.1817 | -122.3785 | -122.2687 | 122.2733 | 122.3602 | 53.0273 | 55.5679
1060.3125 | 122.5845 | -58.5709 | 63.6749 | 0.0028229 | 0.0024076 | 0.064444 | 0.059381 | -0.0041444 | -0.0027472 | -0.00050846 | -0.027466 | 0.0012047 | 0.066302 | 0.060712 | -0.0095362 | 0.0090105 | -0.0026682 | -5.6305 | 63.6429 | -58.7036 | 63.6932 | -58.3237 | -58.8501 | -58.8043 | -3.1174 | 63.5788 | -58.6212 | 63.7802 | -58.5388 | -58.6807 | -58.4976 | -0.13275 | -0.032044 | 0.01831 | 0.24719 | -0.23346 | -0.27924 | -0.10071 | -0.14649 | -0.050354 | -0.096131 | 0.10529 | 0.032044 | 0.073242 | -0.10986 | 0.1236 | -0.059509 | 0.37994 | 122.3969 | 0.082398 | 122.4014 | 122.3465 | 122.2 | 122.2137 | 122.1497 | -122.3785 | -122.2961 | 122.2641 | 122.3511 | 52.9404 | 55.4535
1061.3125 | 122.58 | -58.5571 | 63.6749 | -0.13451 | 0.003262 | 0.063162 | 0.057672 | 0.0031188 | -0.003388 | -0.0013629 | -0.027466 | 0.0012047 | 0.066729 | 0.055585 | -0.0080408 | 0.0092241 | -0.0009592 | -5.7266 | 63.6337 | -58.6853 | 63.6978 | -58.3008 | -58.8364 | -58.786 | -3.2501 | 63.5834 | -58.58 | 63.7802 | -58.5388 | -58.6761 | -58.4839 | -0.12817 | -0.041199 | 0.022888 | 0.25635 | -0.22888 | -0.27924 | -0.10071 | -0.15106 | -0.022888 | -0.091553 | 0.10529 | 0.018311 | 0.073242 | -0.11902 | 0.09613 | -0.09613 | 0.38452 | 122.3831 | 0.041199 | 122.3602 | 122.319 | 122.1634 | 122.1909 | 122.1405 | -122.3602 | -122.2549 | 122.2549 | 122.3373 | 52.8305 | 55.307
1062.3125 | 122.6028 | -58.5526 | 63.7436 | -0.08873 | 0.0024076 | 0.062735 | 0.058526 | -0.0030762 | -0.0010382 | -0.0037129 | 0.061035 | 0.0014185 | 0.065234 | 0.057507 | -0.0080408 | 0.0085833 | -0.0024546 | -5.7358 | 63.6887 | -58.6258 | 63.7436 | -58.255 | -58.7448 | -58.7082 | -3.2913 | 63.62 | -58.5571 | 63.7939 | -58.4702 | -58.5983 | -58.4839 | -0.073242 | -0.054931 | 0 | 0.29755 | -0.15564 | -0.19226 | -0.082398 | -0.11902 | -0.004578 | -0.1236 | 0.050354 | 0.082397 | 0.068664 | -0.045777 | 0.073242 | -0.041199 | 0.37079 | 122.3694 | 0.086975 | 122.3511 | 122.3145 | 122.1771 | 122.2412 | 122.1725 | -122.3694 | -122.3007 | 122.2961 | 122.3465 | 52.8168 | 55.2612
1063.3125 | 122.4701 | -58.5754 | 63.7436 | -0.065842 | 0.004971 | 0.062094 | 0.061944 | 0.00076902 | -0.005097 | 0.0016277 | -0.14648 | 0.0014185 | 0.062884 | 0.061352 | -0.0069726 | 0.010079 | -0.0001046 | -5.9006 | 63.7115 | -58.6853 | 63.6063 | -58.4244 | -58.9005 | -59.2117 | -3.2913 | 63.6841 | -58.5709 | 63.6932 | -58.6029 | -58.754 | -58.5846 | -0.10986 | -0.032043 | -0.13733 | 0.15106 | -0.63629 | -0.32501 | -0.52643 | -0.21515 | 0.004577 | -0.059509 | -0.050354 | -0.027466 | -0.009156 | -0.17853 | -0.013733 | -0.18311 | 0.26093 | 122.2916 | -0.032043 | 122.2641 | 122.3969 | 122.2549 | 122.287 | 122.2595 | -122.4289 | -122.3145 | 122.1817 | 122.2687 | 52.6749 | 55.2841
1064.3125 | 122.5708 | -58.5571 | 63.7024 | -0.10399 | 0.0026212 | 0.062735 | 0.061517 | -0.0024354 | -0.0010382 | 0.00034614 | -0.057983 | 0.0020593 | 0.065448 | 0.05943 | -0.0071864 | 0.0094379 | -0.0052316 | -5.9326 | 63.6612 | -58.6761 | 63.6978 | -58.2962 | -58.8226 | -58.7769 | -3.6118 | 63.6292 | -58.5571 | 63.7985 | -58.4885 | -58.6349 | -58.4656 | -0.11902 | -0.041199 | -0.004578 | 0.26093 | -0.21973 | -0.2655 | -0.10071 | -0.14648 | 0 | -0.073243 | 0.09613 | 0.068665 | 0.091553 | -0.07782 | 0.091553 | -0.07782 | 0.37994 | 122.374 | 0.068665 | 122.3557 | 122.3373 | 122.1863 | 122.2183 | 122.1863 | -122.3785 | -122.2595 | 122.2549 | 122.3557 | 52.6245 | 54.9454
1065.3125 | 122.5983 | -58.5388 | 63.7115 | -0.081101 | -0.0005832 | 0.064016 | 0.059808 | 0.0011962 | -0.0014654 | -0.00093566 | -0.030517 | 0.0024865 | 0.067798 | 0.059644 | -0.0074 | 0.0087969 | 0.001177 | -6.015 | 63.6932 | -58.667 | 63.7207 | -58.2779 | -58.8226 | -58.7723 | -3.7537 | 63.6292 | -58.5434 | 63.8123 | -58.5205 | -58.667 | -58.4885 | -0.12817 | -0.018311 | 0.009155 | 0.26093 | -0.23346 | -0.28381 | -0.10529 | -0.15564 | -0.004578 | -0.082398 | 0.10071 | 0.01831 | 0.050354 | -0.12817 | 0.054932 | -0.1236 | 0.3891 | 122.3877 | 0.022888 | 122.3557 | 122.3602 | 122.1725 | 122.2321 | 122.168 | -122.3785 | -122.2549 | 122.2595 | 122.3511 | 52.5238 | 54.7852
1066.3125 | 122.5433 | -58.5297 | 63.7299 | -0.08873 | 0.0026212 | 0.065085 | 0.058313 | -0.00029898 | -0.0029608 | -0.0013629 | -0.057983 | 0.0012047 | 0.062243 | 0.060925 | -0.0071864 | 0.010079 | -0.0048044 | -6.0516 | 63.6658 | -58.6166 | 63.7848 | -58.2001 | -58.7494 | -58.8364 | -3.5751 | 63.6475 | -58.5205 | 63.8397 | -58.4564 | -58.5846 | -58.4381 | -0.086975 | -0.064087 | 0.054932 | 0.32959 | -0.3067 | -0.21973 | -0.21973 | -0.13275 | 0.009155 | -0.082397 | 0.10986 | 0.073242 | 0.091553 | -0.054932 | 0.082398 | -0.064087 | 0.41656 | 122.4014 | 0.064087 | 122.3602 | 122.2824 | 122.168 | 122.1954 | 122.1771 | -122.3465 | -122.2504 | 122.3145 | 122.3694 | 52.478 | 54.9545
1067.3125 | 122.5937 | -58.4976 | 63.7344 | -0.073471 | 0.0034756 | 0.063376 | 0.060449 | 0.0014098 | -0.00082456 | -0.00072206 | -0.0030517 | 0.00099115 | 0.065234 | 0.058148 | -0.0059046 | 0.010506 | -0.0030954 | -6.1523 | 63.6612 | -58.6304 | 63.7802 | -58.2047 | -58.7448 | -58.6945 | -4.1656 | 63.5834 | -58.5709 | 63.8672 | -58.4427 | -58.6258 | -58.4198 | -0.13275 | -0.073242 | 0.045776 | 0.29297 | -0.19684 | -0.24719 | -0.064087 | -0.11444 | -0.073242 | -0.15106 | 0.13275 | 0.054932 | 0.07782 | -0.12817 | 0.15106 | -0.054931 | 0.42572 | 122.4106 | 0.12817 | 122.438 | 122.2916 | 122.1542 | 122.1588 | 122.081 | -122.3648 | -122.3053 | 122.2778 | 122.3648 | 52.3453 | 54.332
1068.3125 | 122.5708 | -58.5205 | 63.739 | -0.11925 | 0.0045438 | 0.062948 | 0.058954 | 0.00055542 | -0.0010382 | -0.0017903 | 0.0091553 | 0.0031273 | 0.067157 | 0.060712 | -0.0069726 | 0.0092241 | -0.0013864 | -6.2576 | 63.6795 | -58.6258 | 63.7848 | -58.1726 | -58.7357 | -58.6899 | -4.0054 | 63.6658 | -58.4976 | 63.8351 | -58.4244 | -58.5892 | -58.4473 | -0.10529 | -0.05951 | 0.045776 | 0.3479 | -0.16937 | -0.21515 | -0.064087 | -0.10986 | 0.022888 | -0.073243 | 0.09613 | 0.096131 | 0.073242 | -0.068664 | 0.050354 | -0.091552 | 0.45319 | 122.4106 | 0.073243 | 122.3328 | 122.3053 | 122.1634 | 122.2 | 122.1863 | -122.3648 | -122.2366 | 122.3053 | 122.3557 | 52.2629 | 54.5151
1069.3125 | 122.5983 | -58.4839 | 63.7619 | -0.096359 | 0.0019802 | 0.063803 | 0.057672 | -0.002649 | -0.0048834 | -0.0015765 | -0.042725 | 0.0018457 | 0.066302 | 0.056653 | -0.0052638 | 0.011147 | 0.0007498 | -6.3446 | 63.6841 | -58.6349 | 63.7985 | -58.1863 | -58.7173 | -58.6761 | -4.1428 | 63.652 | -58.5251 | 63.7665 | -58.255 | -58.3923 | -58.3557 | -0.15106 | -0.07782 | 0.036621 | 0.29755 | -0.19226 | -0.23346 | -0.041198 | -0.082397 | -0.041198 | -0.10986 | 0.004577 | 0.22888 | 0.12817 | 0.091553 | 0.16937 | 0.13275 | 0.44861 | 122.4335 | 0.27008 | 122.2916 | 122.319 | 122.1771 | 122.168 | 122.1359 | -122.3969 | -122.287 | 122.2824 | 122.2504 | 52.1393 | 54.3411
1070.3125 | 122.5708 | -58.5159 | 63.7619 | 0.0028229 | 0.0024076 | 0.065298 | 0.060876 | 0.0014098 | -0.00082456 | -0.0011493 | -0.036621 | 0.0014185 | 0.063739 | 0.058362 | -0.006759 | 0.011788 | -0.0052316 | -6.4133 | 63.6887 | -58.6166 | 63.7848 | -58.1635 | -58.7219 | -58.6945 | -4.2572 | 63.6475 | -58.5068 | 63.8763 | -58.4152 | -58.7357 | -58.58 | -0.10071 | -0.073242 | 0.022888 | 0.35248 | -0.17853 | -0.20599 | -0.07782 | -0.10529 | 0.009155 | -0.11444 | 0.11444 | 0.10071 | -0.064087 | -0.21973 | -0.073242 | -0.22888 | 0.45319 | 122.4014 | 0.091553 | 122.3831 | 122.3053 | 122.1542 | 122.2046 | 122.1634 | -122.3785 | -122.2687 | 122.3007 | 122.3923 | 52.1027 | 54.2587
1071.3125 | 122.5937 | -58.493 | 63.7573 | -0.073471 | 0.0041166 | 0.062308 | 0.061303 | -0.00093998 | -0.0027472 | -0.0026447 | -0.039673 | 0.0016321 | 0.063525 | 0.063275 | -0.0076136 | 0.010292 | -0.0001046 | -6.5414 | 63.739 | -58.5938 | 63.8123 | -58.1909 | -58.7585 | -58.6899 | -4.39 | 63.6795 | -58.5114 | 63.8855 | -58.429 | -58.5938 | -58.3923 | -0.10071 | -0.01831 | 0.054932 | 0.30212 | -0.19684 | -0.2655 | -0.09613 | -0.16479 | -0.018311 | -0.07782 | 0.12817 | 0.064087 | 0.10071 | -0.10071 | 0.11902 | -0.082397 | 0.40283 | 122.406 | 0.082398 | 122.3969 | 122.3328 | 122.1909 | 122.2321 | 122.1725 | -122.3511 | -122.2687 | 122.3053 | 122.3785 | 51.9516 | 54.1031
1072.3125 | 122.5845 | -58.4518 | 63.7985 | -0.065842 | 0.0034756 | 0.063803 | 0.061517 | -0.00072638 | -0.004029 | 0.00098694 | -0.042725 | 0.0020593 | 0.065875 | 0.060284 | -0.008468 | 0.010506 | -0.0011728 | -6.6422 | 63.7161 | -58.5846 | 63.8077 | -58.1818 | -58.7265 | -58.6945 | -4.5044 | 63.7161 | -58.5022 | 63.8901 | -58.4106 | -58.58 | -58.3969 | -0.13275 | -0.082398 | 0.009155 | 0.27008 | -0.24262 | -0.27466 | -0.10986 | -0.14191 | -0.050354 | -0.082398 | 0.091553 | 0.041198 | 0.054931 | -0.12817 | 0.10529 | -0.07782 | 0.40283 | 122.3923 | 0.091552 | 122.3923 | 122.3007 | 122.2183 | 122.168 | 122.168 | -122.3831 | -122.3007 | 122.2595 | 122.3419 | 51.8097 | 53.9474
1073.3125 | 122.5891 | -58.4381 | 63.7939 | -0.096359 | 0.0043302 | 0.063162 | 0.058526 | 0.00076902 | -0.0025336 | -0.0022175 | -0.039673 | -0.00029045 | 0.063525 | 0.062207 | -0.008468 | 0.0090105 | -0.0024546 | -6.6788 | 63.7207 | -58.5938 | 63.8077 | -58.1589 | -58.6395 | -58.6304 | -4.5456 | 63.6841 | -58.4702 | 63.9084 | -58.3786 | -58.5388 | -58.3832 | -0.15564 | -0.073242 | 0.013733 | 0.27923 | -0.19226 | -0.20142 | -0.036621 | -0.045776 | -0.032044 | -0.10986 | 0.11444 | 0.059509 | 0.054931 | -0.10071 | 0.086975 | -0.068664 | 0.43487 | 122.4014 | 0.091553 | 122.3785 | 122.3145 | 122.1542 | 122.1588 | 122.1222 | -122.3877 | -122.2641 | 122.2458 | 122.3465 | 51.7593 | 53.8925
1074.3125 | 122.6028 | -58.4381 | 63.7939 | -0.096359 | 0.0024076 | 0.064444 | 0.057245 | -0.0015808 | -0.0027472 | -0.0013629 | -0.030517 | 0.00013675 | 0.065875 | 0.063702 | -0.0059046 | 0.010292 | -0.0069406 | -6.7795 | 63.739 | -58.5754 | 63.8992 | -57.8979 | -58.5571 | -58.6624 | -4.6417 | 63.6978 | -58.4702 | 63.913 | -58.3649 | -58.5663 | -58.4015 | -0.13733 | -0.054931 | 0.10529 | 0.54016 | -0.22431 | -0.11902 | -0.086976 | 0.01831 | -0.032044 | -0.09613 | 0.11902 | 0.073242 | 0.036621 | -0.12817 | 0.068665 | -0.09613 | 0.67749 | 122.4747 | 0.10529 | 122.3831 | 122.3145 | 122.168 | 122.1771 | 122.1359 | -122.3694 | -122.2641 | 122.3373 | 122.3511 | 51.6586 | 53.7964
1075.3125 | 122.6028 | -58.4381 | 63.7985 | -0.10399 | 0.0036892 | 0.062948 | 0.059167 | 0.0020508 | -0.0029608 | -0.0022175 | 0.079346 | 0.00099115 | 0.065448 | 0.066479 | -0.0071864 | 0.0094379 | -0.0052316 | -6.8527 | 63.7573 | -58.5709 | 63.858 | -58.0948 | -58.873 | -58.8547 | -4.6555 | 63.7115 | -58.4427 | 63.913 | -58.3649 | -58.5205 | -58.3969 | -0.13275 | -0.041199 | 0.059509 | 0.34332 | -0.41656 | -0.43488 | -0.28381 | -0.30212 | -0.004578 | -0.086975 | 0.11444 | 0.073242 | 0.041198 | -0.082398 | 0.045776 | -0.07782 | 0.47607 | 122.4289 | 0.07782 | 122.3557 | 122.3282 | 122.1542 | 122.1954 | 122.1497 | -122.3694 | -122.2412 | 122.2961 | 122.3511 | 51.5854 | 53.7827
1076.3125 | 122.5662 | -58.4381 | 63.8077 | -0.081101 | 0.0034756 | 0.063376 | 0.057886 | 0.00055542 | -0.0016792 | 0.00034614 | -0.12817 | 0.00099115 | 0.064166 | 0.070325 | -0.008468 | 0.011788 | -0.0007456 | -6.9763 | 63.7253 | -58.5434 | 63.8718 | -58.1131 | -58.667 | -58.6349 | -4.6692 | 63.7161 | -58.4473 | 63.945 | -58.3466 | -58.5114 | -58.3466 | -0.10529 | -0.082397 | 0.064087 | 0.32501 | -0.19684 | -0.22888 | -0.091553 | -0.1236 | -0.009156 | -0.091553 | 0.13733 | 0.091552 | 0.091552 | -0.073243 | 0.10071 | -0.064087 | 0.4303 | 122.4152 | 0.10071 | 122.3923 | 122.2687 | 122.1634 | 122.1634 | 122.1542 | -122.3511 | -122.2549 | 122.3099 | 122.3831 | 51.4618 | 53.7689
1077.3125 | 122.5708 | -58.4106 | 63.8397 | -0.11162 | 0.0024076 | 0.064444 | 0.057458 | -0.0032898 | -0.0021064 | -0.0020039 | 0.045776 | 0.00099115 | 0.062457 | 0.059644 | -0.0069726 | 0.0090105 | -0.0016 | -7.0999 | 63.8077 | -58.5571 | 63.858 | -58.1177 | -58.6441 | -58.5938 | -4.8889 | 63.7436 | -58.4427 | 63.9313 | -58.3466 | -58.493 | -58.3557 | -0.14648 | -0.032044 | 0.01831 | 0.29297 | -0.1831 | -0.23346 | -0.036621 | -0.086975 | -0.032043 | -0.096131 | 0.091552 | 0.064087 | 0.054932 | -0.082397 | 0.086975 | -0.050354 | 0.43945 | 122.4152 | 0.09613 | 122.374 | 122.3648 | 122.1863 | 122.2183 | 122.1542 | -122.3969 | -122.2824 | 122.2687 | 122.3419 | 51.3107 | 53.5217
1078.3125 | 122.5296 | -58.4427 | 63.826 | -0.058212 | 0.0043302 | 0.06188 | 0.060235 | 0.0039734 | -0.0038154 | -0.00029486 | -0.061035 | 0.0022729 | 0.067798 | 0.070538 | -0.0076136 | 0.010079 | -0.0001046 | -7.2235 | 63.7619 | -58.5663 | 63.826 | -58.1772 | -58.7357 | -58.6899 | -5.0674 | 63.7665 | -58.4839 | 63.9038 | -58.3923 | -58.5617 | -58.4015 | -0.1236 | -0.064087 | 0 | 0.2655 | -0.24719 | -0.29297 | -0.1236 | -0.16937 | -0.041199 | -0.05951 | 0.07782 | 0.050354 | 0.041199 | -0.11902 | 0.082398 | -0.07782 | 0.3891 | 122.3923 | 0.091553 | 122.3877 | 122.3282 | 122.2504 | 122.2046 | 122.2092 | -122.3923 | -122.3099 | 122.2687 | 122.3465 | 51.2192 | 53.3752
1079.3125 | 122.5891 | -58.4198 | 63.826 | -0.073471 | 0.0026212 | 0.064016 | 0.060876 | -0.0011536 | -0.0012518 | 0.0012005 | -0.045776 | 0.0014185 | 0.068225 | 0.063702 | -0.009109 | 0.0096515 | -0.0020272 | -7.2784 | 63.8031 | -58.5297 | 63.8947 | -58.0719 | -58.6395 | -58.5983 | -5.04 | 63.7299 | -58.4473 | 63.9496 | -58.374 | -58.5068 | -58.3374 | -0.10986 | -0.022888 | 0.068664 | 0.3479 | -0.17853 | -0.21973 | -0.068665 | -0.10986 | -0.027466 | -0.096131 | 0.1236 | 0.045777 | 0.082398 | -0.086975 | 0.10986 | -0.059509 | 0.45776 | 122.4243 | 0.073243 | 122.3969 | 122.3328 | 122.1771 | 122.2229 | 122.1497 | -122.3557 | -122.2733 | 122.3145 | 122.3694 | 51.1414 | 53.3798
1080.3125 | 122.6349 | -58.3923 | 63.8351 | -0.11925 | 0.0047574 | 0.061239 | 0.059381 | 0.00034182 | -0.0018928 | -0.0032855 | -0.012207 | 0.0012047 | 0.066943 | 0.059216 | -0.0076136 | 0.010506 | -0.0035226 | -7.3746 | 63.7573 | -58.5068 | 63.9084 | -58.049 | -58.6304 | -58.5892 | -5.1224 | 63.7299 | -58.4015 | 63.9633 | -58.3328 | -58.5022 | -58.3328 | -0.11444 | -0.07782 | 0.073242 | 0.34332 | -0.19684 | -0.23804 | -0.082397 | -0.1236 | -0.009155 | -0.10529 | 0.12817 | 0.059509 | 0.059509 | -0.10986 | 0.068664 | -0.10071 | 0.45776 | 122.4152 | 0.068664 | 122.3648 | 122.2641 | 122.1313 | 122.1497 | 122.1222 | -122.3419 | -122.2366 | 122.3007 | 122.3557 | 51.0178 | 53.27
1081.3125 | 122.6074 | -58.4061 | 63.858 | -0.10399 | 0.0041166 | 0.063376 | 0.059381 | 0.0046142 | -0.007447 | -0.0011493 | -0.01831 | 0.0012047 | 0.067798 | 0.067334 | -0.0065454 | 0.0094379 | -0.0043772 | -7.489 | 63.7573 | -58.5068 | 63.9175 | -58.0399 | -58.6121 | -58.5617 | -5.1956 | 63.7573 | -58.3969 | 63.9542 | -58.3191 | -58.4885 | -58.3237 | -0.10071 | -0.10071 | 0.05951 | 0.36621 | -0.15564 | -0.20599 | -0.054932 | -0.10529 | 0.009155 | -0.10071 | 0.096131 | 0.086975 | 0.082398 | -0.082397 | 0.073243 | -0.091552 | 0.46692 | 122.4243 | 0.07782 | 122.3511 | 122.2641 | 122.1542 | 122.1634 | 122.1634 | -122.3648 | -122.2549 | 122.3236 | 122.3602 | 50.9171 | 53.2104
1082.3125 | 122.5708 | -58.3694 | 63.913 | -0.035324 | 0.0053982 | 0.064016 | 0.061303 | -0.0024354 | -0.0029608 | -0.0013629 | 0.0030517 | 0.0018457 | 0.066089 | 0.062207 | -0.006759 | 0.0085833 | -0.0041636 | -7.5439 | 63.8535 | -58.4564 | 63.9404 | -57.9987 | -58.5526 | -58.5342 | -5.191 | 63.8397 | -58.3878 | 63.9816 | -58.2825 | -58.4564 | -58.3282 | -0.086975 | -0.059509 | 0.027466 | 0.37079 | -0.16479 | -0.1831 | -0.07782 | -0.09613 | -0.01831 | -0.073242 | 0.068664 | 0.086975 | 0.041199 | -0.086975 | 0.059509 | -0.068665 | 0.45776 | 122.3969 | 0.10529 | 122.3694 | 122.3099 | 122.2275 | 122.2229 | 122.2092 | -122.3694 | -122.3007 | 122.3099 | 122.3511 | 50.8255 | 53.1784
1083.3125 | 122.5983 | -58.3694 | 63.8947 | -0.027695 | 0.0024076 | 0.064871 | 0.059808 | -0.0028626 | -0.003388 | -0.0015765 | -0.045776 | 0.0039819 | 0.066516 | 0.057935 | -0.0074 | 0.0090105 | -0.003309 | -7.7087 | 63.8031 | -58.5068 | 63.9267 | -58.0444 | -58.6075 | -58.5526 | -5.3513 | 63.7619 | -58.3969 | 64.1098 | -58.3832 | -58.4885 | -58.3191 | -0.13733 | -0.091552 | 0.032044 | 0.32501 | -0.1831 | -0.23804 | -0.045776 | -0.10071 | -0.027466 | -0.13275 | 0.21515 | -0.013733 | 0.050354 | -0.11902 | 0.07782 | -0.091552 | 0.46234 | 122.4335 | 0.013733 | 122.5067 | 122.3099 | 122.1588 | 122.1725 | 122.1313 | -122.4014 | -122.2916 | 122.2961 | 122.4792 | 50.6607 | 53.0182
1084.3125 | 122.5891 | -58.3694 | 63.8763 | -0.096359 | 0.0036892 | 0.064444 | 0.059808 | 0.0014098 | -0.0027472 | -0.00050846 | -0.073242 | 0.0020593 | 0.065448 | 0.062848 | -0.008468 | 0.0077289 | 0.0007498 | -7.8003 | 63.8306 | -58.5159 | 63.9359 | -58.0399 | -58.5983 | -58.5434 | -5.452 | 63.7756 | -58.3878 | 64.0961 | -58.3786 | -58.5159 | -58.3282 | -0.14648 | -0.045777 | 0.059509 | 0.32959 | -0.17395 | -0.22888 | -0.027466 | -0.082398 | -0.01831 | -0.10071 | 0.21973 | -0.009155 | 0.041199 | -0.14648 | 0.059509 | -0.12817 | 0.47607 | 122.4518 | 0.009155 | 122.4838 | 122.3465 | 122.1634 | 122.2 | 122.1451 | -122.3923 | -122.2641 | 122.3053 | 122.4655 | 50.5692 | 52.9175
1085.3125 | 122.5845 | -58.3694 | 63.8672 | -0.10399 | 0.0026212 | 0.064016 | 0.059808 | 0.00012822 | -0.00232 | -0.0015765 | -0.012207 | 0.00077755 | 0.066729 | 0.061993 | -0.0082544 | 0.010079 | -0.0030954 | -7.8735 | 63.8123 | -58.4976 | 63.9359 | -58.0078 | -58.5892 | -58.5251 | -5.4886 | 63.7848 | -58.3603 | 63.9954 | -58.2687 | -58.4473 | -58.2962 | -0.12817 | -0.054931 | 0.068665 | 0.36163 | -0.15564 | -0.21973 | -0.027465 | -0.091552 | 0.009155 | -0.082397 | 0.12817 | 0.10071 | 0.073242 | -0.07782 | 0.064087 | -0.086975 | 0.48981 | 122.4335 | 0.091553 | 122.3557 | 122.3099 | 122.1451 | 122.1817 | 122.1542 | -122.3648 | -122.2275 | 122.3053 | 122.3648 | 50.4959 | 52.8809
1086.3125 | 122.5616 | -58.3511 | 63.9038 | -0.081101 | 0.001553 | 0.062948 | 0.058954 | 0.00076902 | -0.0014654 | -0.00029486 | 0.0030517 | 0.0024865 | 0.062671 | 0.063489 | -0.0078272 | 0.0094379 | -0.0020272 | -7.9926 | 63.8443 | -58.4473 | 63.9175 | -58.0124 | -58.5938 | -58.548 | -5.5984 | 63.7939 | -58.3694 | 63.9587 | -58.3054 | -58.4656 | -58.3191 | -0.096131 | -0.05951 | 0.013733 | 0.33874 | -0.19684 | -0.24262 | -0.10071 | -0.14648 | -0.018311 | -0.10986 | 0.054931 | 0.045776 | 0.032043 | -0.11444 | 0.050354 | -0.09613 | 0.43488 | 122.3648 | 0.064087 | 122.3282 | 122.2916 | 122.1634 | 122.1954 | 122.1451 | -122.3511 | -122.2733 | 122.2687 | 122.3099 | 50.3586 | 52.7527
1087.3125 | 122.5479 | -58.342 | 63.9038 | -0.065842 | 0.0039028 | 0.061667 | 0.060022 | -0.002649 | -0.004029 | -0.0015765 | -0.01831 | 0.00056395 | 0.065875 | 0.061566 | -0.0063318 | 0.010079 | -0.0022408 | -8.1253 | 63.8214 | -58.4564 | 63.945 | -57.9987 | -58.6075 | -58.5388 | -5.6854 | 63.8168 | -58.3557 | 63.9771 | -58.3054 | -58.461 | -58.3145 | -0.11444 | -0.082398 | 0.041198 | 0.34332 | -0.19684 | -0.2655 | -0.082397 | -0.15106 | -0.013733 | -0.086976 | 0.073242 | 0.036621 | 0.027466 | -0.11902 | 0.041199 | -0.10529 | 0.45776 | 122.4014 | 0.050354 | 122.3328 | 122.2778 | 122.1725 | 122.1634 | 122.1588 | -122.3602 | -122.2595 | 122.287 | 122.319 | 50.2167 | 52.6566
1088.3125 | 122.5479 | -58.3374 | 63.8947 | -0.096359 | 0.0011258 | 0.06188 | 0.059595 | -0.002649 | -0.0016792 | -0.0028583 | 0.012207 | 0.0022729 | 0.065448 | 0.060284 | -0.0071864 | 0.010079 | -0.0024546 | -8.2626 | 63.8672 | -58.4564 | 63.9359 | -57.9941 | -58.5938 | -58.5114 | -5.8136 | 63.8489 | -58.342 | 63.9771 | -58.287 | -58.4564 | -58.3054 | -0.11902 | -0.027466 | 0.041199 | 0.34332 | -0.17395 | -0.25635 | -0.054932 | -0.13733 | -0.004578 | -0.045776 | 0.082398 | 0.050354 | 0.032043 | -0.11902 | 0.036621 | -0.11444 | 0.46234 | 122.3923 | 0.054932 | 122.319 | 122.3236 | 122.1909 | 122.2046 | 122.1863 | -122.3511 | -122.2366 | 122.2733 | 122.3145 | 50.0748 | 52.5238
1089.3125 | 122.5388 | -58.3328 | 63.945 | -0.096359 | 0.003262 | 0.06423 | 0.060022 | -0.0017944 | -0.0012518 | 0.00013254 | -0.033569 | 0.0033411 | 0.068225 | 0.062634 | -0.0076136 | 0.0094379 | -0.0054452 | -8.3359 | 63.8672 | -58.4473 | 63.9542 | -57.9849 | -58.5846 | -58.5159 | -5.864 | 63.8306 | -58.3466 | 63.9954 | -58.287 | -58.4427 | -58.287 | -0.11444 | -0.07782 | 0.009156 | 0.3479 | -0.1831 | -0.25177 | -0.068664 | -0.13733 | -0.013733 | -0.11444 | 0.050354 | 0.045777 | 0.045777 | -0.10986 | 0.05951 | -0.09613 | 0.46234 | 122.4014 | 0.05951 | 122.3419 | 122.3145 | 122.1771 | 122.2 | 122.1634 | -122.3923 | -122.2916 | 122.287 | 122.3282 | 49.9969 | 52.4689
1090.3125 | 122.5708 | -58.3237 | 63.9359 | -0.058212 | 0.002194 | 0.060812 | 0.058313 | -8.538e-05 | -0.00082456 | -0.00050846 | -8.6e-08 | 0.0020593 | 0.065448 | 0.060071 | -0.0065454 | 0.010079 | -0.0030954 | -8.4549 | 63.8947 | -58.4335 | 63.9542 | -58.0032 | -58.5617 | -58.5114 | -5.7404 | 63.8947 | -58.3099 | 63.9908 | -58.255 | -58.461 | -58.3054 | -0.10986 | -0.041199 | 0.018311 | 0.32043 | -0.18768 | -0.23804 | -0.07782 | -0.12817 | 0.013732 | -0.041199 | 0.054932 | 0.068664 | 0.01831 | -0.13733 | 0.004578 | -0.15106 | 0.4303 | 122.3877 | 0.054932 | 122.3007 | 122.3282 | 122.2046 | 122.2183 | 122.2183 | -122.3694 | -122.2458 | 122.2778 | 122.3145 | 49.8688 | 52.5833
1091.3125 | 122.5662 | -58.3374 | 63.9267 | -0.11925 | 0.0036892 | 0.062735 | 0.061517 | 0.00055542 | -0.0027472 | 0.0014141 | -0.030517 | 0.00013675 | 0.066089 | 0.063916 | -0.0082544 | 0.0090105 | -0.0058724 | -8.5236 | 63.8443 | -58.4381 | 64.0091 | -57.93 | -58.5388 | -58.4747 | -5.9784 | 63.8626 | -58.342 | 64.0411 | -58.2184 | -58.4106 | -58.2504 | -0.10071 | -0.082398 | 0.082397 | 0.40741 | -0.13733 | -0.20142 | -0.036621 | -0.10071 | -0.004578 | -0.064087 | 0.11444 | 0.11902 | 0.086975 | -0.073243 | 0.091553 | -0.068665 | 0.50812 | 122.4472 | 0.1236 | 122.3831 | 122.2824 | 122.2046 | 122.1817 | 122.2 | -122.3648 | -122.2687 | 122.3465 | 122.3785 | 49.8138 | 52.359
1092.3125 | 122.5571 | -58.3054 | 63.9816 | -0.065842 | 0.0026212 | 0.062948 | 0.058099 | 0.0033324 | -0.0046698 | -0.0022175 | -0.0091553 | 0.0020593 | 0.066302 | 0.057507 | -0.0082544 | 0.0092241 | -0.0030954 | -8.6472 | 63.913 | -58.4335 | 63.9771 | -57.9529 | -58.5342 | -58.4976 | -6.0974 | 63.8947 | -58.3328 | 64.0366 | -58.2001 | -58.3969 | -58.2458 | -0.12817 | -0.068664 | -0.004577 | 0.35248 | -0.19226 | -0.22888 | -0.064087 | -0.10071 | -0.027466 | -0.086975 | 0.054932 | 0.10529 | 0.059509 | -0.091553 | 0.086975 | -0.064087 | 0.48065 | 122.4106 | 0.13275 | 122.3694 | 122.3465 | 122.2275 | 122.2183 | 122.2 | -122.4152 | -122.3145 | 122.2824 | 122.3419 | 49.6582 | 52.2079
1093.3125 | 122.525 | -58.3054 | 63.9954 | -0.042954 | 0.003262 | 0.061667 | 0.060663 | -0.0013672 | -0.00232 | -0.0020039 | 0.018311 | 0.00035035 | 0.068652 | 0.060284 | -0.006759 | 0.010079 | -0.0022408 | -8.7662 | 63.8992 | -58.4015 | 63.9725 | -57.962 | -58.5388 | -58.4793 | -6.189 | 63.913 | -58.3191 | 64.0137 | -58.2733 | -58.3786 | -58.2733 | -0.09613 | -0.09613 | -0.022888 | 0.34332 | -0.17395 | -0.23346 | -0.07782 | -0.13733 | -0.013733 | -0.082397 | 0.018311 | 0.032044 | 0.032044 | -0.073242 | 0.045777 | -0.059509 | 0.43945 | 122.374 | 0.045777 | 122.3328 | 122.3007 | 122.2321 | 122.2046 | 122.2183 | -122.3969 | -122.3145 | 122.2778 | 122.319 | 49.5392 | 52.1164
1094.3125 | 122.5113 | -58.3145 | 63.9587 | -0.10399 | 0.003262 | 0.063589 | 0.061303 | 0.00098262 | -0.003388 | 0.00077334 | -0.024414 | -0.00050405 | 0.066729 | 0.060284 | -0.006759 | 0.010506 | -0.0013864 | -8.8531 | 63.9359 | -58.3923 | 63.9771 | -57.9346 | -58.5251 | -58.4885 | -6.2759 | 63.913 | -58.3008 | 64.0228 | -58.2733 | -58.3878 | -58.2413 | -0.07782 | -0.022888 | 0.018311 | 0.37994 | -0.17395 | -0.21057 | -0.09613 | -0.13275 | 0.013733 | -0.045776 | 0.064087 | 0.041199 | 0.073242 | -0.073242 | 0.059509 | -0.086975 | 0.45776 | 122.3694 | 0.027466 | 122.3236 | 122.3282 | 122.2137 | 122.2504 | 122.2275 | -122.3511 | -122.2595 | 122.2916 | 122.3373 | 49.4614 | 52.0386
1095.3125 | 122.5021 | -58.2733 | 63.9999 | -0.065842 | 0.0034756 | 0.063589 | 0.059595 | -0.002008 | -0.0018928 | -0.0028583 | -0.024414 | 0.00035035 | 0.06502 | 0.058148 | -0.0069726 | 0.0094379 | -0.0018136 | -9.0042 | 63.9267 | -58.3923 | 63.9862 | -57.9666 | -58.5159 | -58.4702 | -6.3354 | 63.9221 | -58.2825 | 64.0182 | -58.2367 | -58.3694 | -58.2504 | -0.11902 | -0.073242 | -0.013733 | 0.3067 | -0.19684 | -0.24262 | -0.07782 | -0.1236 | -0.009156 | -0.07782 | 0.018311 | 0.036621 | 0.022888 | -0.096131 | 0.032044 | -0.086975 | 0.42572 | 122.3785 | 0.045777 | 122.3007 | 122.319 | 122.2046 | 122.2 | 122.1954 | -122.3923 | -122.2824 | 122.2595 | 122.2916 | 49.2691 | 51.9379
1096.3125 | 122.5342 | -58.287 | 63.9999 | -0.042954 | 0.0028348 | 0.063589 | 0.05874 | -0.00093998 | -0.0014654 | -0.0026447 | -0.024414 | 0.0014185 | 0.065661 | 0.062634 | -0.0054774 | 0.0081561 | -0.0022408 | -9.1278 | 63.913 | -58.3878 | 64.0045 | -57.9346 | -58.5159 | -58.4702 | -6.2897 | 63.9313 | -58.2687 | 64.0228 | -58.2001 | -58.3969 | -58.255 | -0.10071 | -0.086975 | 0.004578 | 0.35248 | -0.18311 | -0.22888 | -0.082398 | -0.12817 | 0.01831 | -0.068665 | 0.022888 | 0.086975 | 0.032043 | -0.10986 | 0.013733 | -0.12817 | 0.45319 | 122.3923 | 0.068665 | 122.2916 | 122.3007 | 122.2 | 122.2 | 122.2183 | -122.3877 | -122.2687 | 122.2916 | 122.3099 | 49.1592 | 51.9974
1097.3125 | 122.5571 | -58.2596 | 64.0091 | -0.11162 | 0.001553 | 0.063589 | 0.059595 | -0.0058532 | -0.0016792 | -0.00050846 | -0.021362 | 0.00099115 | 0.063952 | 0.059644 | -0.009109 | 0.010506 | -0.0020272 | -9.2102 | 63.9542 | -58.3832 | 64.0137 | -57.9391 | -58.5068 | -58.4518 | -6.2714 | 63.9404 | -58.2642 | 64.0549 | -58.1863 | -58.4061 | -58.2687 | -0.1236 | -0.054931 | 0.004578 | 0.32043 | -0.19226 | -0.24719 | -0.068664 | -0.1236 | -0.004577 | -0.068664 | 0.045777 | 0.073243 | -0.009155 | -0.14648 | -0.004578 | -0.14191 | 0.44403 | 122.3969 | 0.07782 | 122.319 | 122.3373 | 122.2046 | 122.2137 | 122.2 | -122.3923 | -122.2733 | 122.2733 | 122.3145 | 49.0494 | 51.9882
1098.3125 | 122.4655 | -58.255 | 64.0778 | 0.048599 | 0.004971 | 0.063376 | 0.061731 | -0.00051278 | -0.004029 | -0.00050846 | -0.073242 | 0.0037683 | 0.063525 | 0.061566 | -0.0037684 | 0.0081561 | -0.0045908 | -9.494 | 64.0091 | -58.4015 | 63.9816 | -57.9803 | -58.5159 | -58.4793 | -6.5964 | 63.9725 | -58.2687 | 64.0274 | -58.2184 | -58.4061 | -58.2642 | -0.14648 | -0.068665 | -0.096131 | 0.27466 | -0.2243 | -0.26093 | -0.07782 | -0.11444 | -0.013733 | -0.10529 | -0.050354 | 0.036621 | -0.009155 | -0.15106 | 0.004578 | -0.13733 | 0.42114 | 122.3831 | 0.050354 | 122.2961 | 122.4106 | 122.2412 | 122.2641 | 122.2275 | -122.4792 | -122.3465 | 122.2366 | 122.2824 | 48.761 | 51.6586
1099.3125 | 122.5388 | -58.2642 | 64.0182 | -0.08873 | 0.0043302 | 0.06423 | 0.060022 | 0.0020508 | -0.0012518 | 0.0012005 | -0.036621 | 0.0018457 | 0.065875 | 0.062207 | -0.006759 | 0.0094379 | -0.0030954 | -9.462 | 63.9175 | -58.3603 | 64.0366 | -57.8796 | -58.5068 | -58.429 | -6.6238 | 63.9175 | -58.2596 | 64.0778 | -58.1909 | -58.3557 | -58.2047 | -0.096131 | -0.10071 | 0.01831 | 0.38452 | -0.1648 | -0.24262 | -0.068664 | -0.14648 | 0.004577 | -0.10071 | 0.059509 | 0.073242 | 0.059509 | -0.091553 | 0.054932 | -0.09613 | 0.48065 | 122.3969 | 0.068665 | 122.3373 | 122.2778 | 122.1771 | 122.1817 | 122.1817 | -122.3785 | -122.2778 | 122.3007 | 122.3419 | 48.8022 | 51.6403
1100.3125 | 122.5891 | -58.223 | 64.0228 | -0.10399 | 0.0036892 | 0.063803 | 0.05874 | -0.0013672 | -0.004029 | -0.00050846 | -0.015259 | 0.0014185 | 0.06737 | 0.05943 | -0.0069726 | 0.0094379 | -0.0022408 | -9.5581 | 63.9633 | -58.3466 | 64.0366 | -57.8751 | -58.4518 | -58.4015 | -6.6788 | 63.9404 | -58.2413 | 64.1144 | -58.1268 | -58.3008 | -58.1726 | -0.1236 | -0.059509 | 0.013733 | 0.3479 | -0.17853 | -0.22888 | -0.054931 | -0.10528 | -0.018311 | -0.082397 | 0.091553 | 0.09613 | 0.050354 | -0.07782 | 0.068665 | -0.059509 | 0.4715 | 122.3831 | 0.11444 | 122.3557 | 122.3099 | 122.1817 | 122.1863 | 122.1634 | -122.3694 | -122.2641 | 122.2595 | 122.3373 | 48.6649 | 51.5442
1101.3125 | 122.5754 | -58.2047 | 64.0594 | -0.035324 | 0.0017666 | 0.063162 | 0.060876 | -0.00072638 | -0.0031744 | 0.00013254 | -0.01831 | 0.00099115 | 0.064166 | 0.060925 | -0.0074 | 0.0081561 | -0.003309 | -9.6451 | 63.9862 | -58.342 | 64.0549 | -57.8659 | -58.4381 | -58.3969 | -6.7245 | 63.9725 | -58.2596 | 64.1144 | -58.1131 | -58.3054 | -58.168 | -0.13733 | -0.073242 | -0.004577 | 0.33874 | -0.19226 | -0.23346 | -0.054932 | -0.09613 | -0.054932 | -0.086975 | 0.054932 | 0.091553 | 0.036621 | -0.10071 | 0.091553 | -0.045776 | 0.47607 | 122.3969 | 0.14648 | 122.374 | 122.3282 | 122.2321 | 122.1909 | 122.1771 | -122.4014 | -122.319 | 122.2595 | 122.319 | 48.5596 | 51.4801
1102.3125 | 122.5616 | -58.2184 | 64.1098 | -0.042954 | 0.0013394 | 0.064016 | 0.062372 | 0.002478 | -0.0042426 | -0.0020039 | -0.094604 | 0.0020593 | 0.066089 | 0.063702 | -0.008468 | 0.0094379 | -0.0035226 | -9.7183 | 64.0411 | -58.3237 | 64.0366 | -57.9025 | -58.4564 | -58.4381 | -6.8253 | 64.0228 | -58.2184 | 64.1052 | -58.1543 | -58.3603 | -58.2047 | -0.10529 | -0.068664 | -0.073242 | 0.31586 | -0.21973 | -0.23804 | -0.11444 | -0.13275 | 0 | -0.086975 | -0.004577 | 0.064087 | 0.013733 | -0.14191 | 0.013733 | -0.14191 | 0.42114 | 122.3602 | 0.064087 | 122.3236 | 122.3648 | 122.2412 | 122.2595 | 122.2412 | -122.4335 | -122.3282 | 122.2549 | 122.3236 | 48.5001 | 51.3931
1103.3125 | 122.5159 | -58.2367 | 64.1052 | -0.058212 | 0.0028348 | 0.063589 | 0.06109 | -0.0017944 | -0.00232 | 0.00098694 | -0.07019 | 0.0029137 | 0.069507 | 0.058362 | -0.005691 | 0.01072 | -0.0037362 | -9.8694 | 64.0457 | -58.3511 | 64.0549 | -57.8705 | -58.4473 | -58.429 | -6.9031 | 64.0182 | -58.2275 | 64.1006 | -58.1314 | -58.3694 | -58.2092 | -0.11444 | -0.05951 | -0.050354 | 0.36621 | -0.19226 | -0.21057 | -0.07782 | -0.096131 | 0.009155 | -0.086975 | -0.004578 | 0.10529 | 0.027465 | -0.13275 | 0.01831 | -0.14191 | 0.48065 | 122.406 | 0.09613 | 122.3282 | 122.3969 | 122.2458 | 122.2824 | 122.2549 | -122.4564 | -122.3328 | 122.2916 | 122.3373 | 48.3673 | 51.3336
1104.3125 | 122.58 | -58.2184 | 64.0503 | -0.12688 | 0.0028348 | 0.062521 | 0.062585 | -0.00072638 | -0.0036018 | -0.0020039 | 0.0091553 | 0.0024865 | 0.068866 | 0.059857 | -0.0082544 | 0.0094379 | -0.005018 | -10.0342 | 63.9954 | -58.3328 | 64.0549 | -57.8613 | -58.4564 | -58.4061 | -6.9855 | 63.9542 | -58.2458 | 64.1006 | -58.1177 | -58.3099 | -58.1635 | -0.11444 | -0.054932 | 0.004578 | 0.35706 | -0.18768 | -0.23804 | -0.073242 | -0.1236 | -0.027466 | -0.09613 | 0.050354 | 0.10071 | 0.054932 | -0.091553 | 0.082398 | -0.064087 | 0.4715 | 122.3877 | 0.12817 | 122.3465 | 122.3282 | 122.2 | 122.2137 | 122.1725 | -122.3831 | -122.2961 | 122.2733 | 122.319 | 48.1842 | 51.2329
1105.3125 | 122.5845 | -58.1955 | 64.0778 | -0.081101 | 0.0047574 | 0.063589 | 0.059595 | 0.00034182 | -0.0025336 | 0.00077334 | 0.0030517 | 0.00056395 | 0.06737 | 0.062848 | -0.0063318 | 0.011788 | -0.0026682 | -10.1028 | 63.9771 | -58.3008 | 64.0594 | -57.8339 | -58.4564 | -58.3786 | -7.0496 | 63.9771 | -58.2184 | 64.1235 | -58.1039 | -58.2962 | -58.1589 | -0.10529 | -0.10071 | -0.018311 | 0.36163 | -0.18311 | -0.26093 | -0.07782 | -0.15564 | -0.022888 | -0.10071 | 0.045776 | 0.091553 | 0.036621 | -0.10071 | 0.059509 | -0.07782 | 0.46692 | 122.3602 | 0.11444 | 122.3419 | 122.2778 | 122.1954 | 122.1725 | 122.1725 | -122.3785 | -122.2961 | 122.2549 | 122.319 | 48.0927 | 51.1459
1106.3125 | 122.6074 | -58.1497 | 64.0915 | -0.035324 | 0.0039028 | 0.062094 | 0.058313 | 0.002478 | -0.0044562 | -0.00050846 | 0.018311 | 0.0033411 | 0.066302 | 0.055798 | -0.005691 | 0.010079 | -0.0052316 | -10.1807 | 64.0182 | -58.287 | 64.1235 | -57.7698 | -58.3694 | -58.3328 | -7.0587 | 63.9771 | -58.1955 | 64.1876 | -58.0261 | -58.2321 | -58.1177 | -0.13733 | -0.073242 | 0.032043 | 0.37994 | -0.18311 | -0.21973 | -0.045777 | -0.082398 | -0.045777 | -0.11444 | 0.09613 | 0.1236 | 0.032043 | -0.082398 | 0.07782 | -0.036621 | 0.51727 | 122.4106 | 0.16937 | 122.3831 | 122.3053 | 122.1725 | 122.168 | 122.1268 | -122.3785 | -122.287 | 122.2733 | 122.3373 | 47.9691 | 51.091
1107.3125 | 122.525 | -58.168 | 64.1464 | -0.020065 | 0.0028348 | 0.064444 | 0.061303 | -0.0015808 | -0.0031744 | -0.00050846 | -0.094604 | 0.0020593 | 0.066516 | 0.063489 | -0.0086816 | 0.012215 | -0.0028818 | -10.2859 | 64.0594 | -58.3099 | 64.1052 | -57.8064 | -58.4061 | -58.3878 | -7.2006 | 64.0137 | -58.2047 | 64.119 | -58.1131 | -58.3282 | -58.168 | -0.14191 | -0.086975 | -0.041198 | 0.36163 | -0.21973 | -0.23804 | -0.077819 | -0.09613 | -0.036621 | -0.13275 | -0.027465 | 0.054932 | 0 | -0.16022 | 0.036621 | -0.1236 | 0.50354 | 122.4152 | 0.091553 | 122.3236 | 122.3694 | 122.2183 | 122.2275 | 122.1817 | -122.4564 | -122.3511 | 122.2733 | 122.287 | 47.8821 | 50.9674
1108.3125 | 122.4884 | -58.168 | 64.1373 | -0.050583 | 0.0026212 | 0.062948 | 0.06109 | 0.0016236 | -0.0027472 | -0.0020039 | -0.076294 | 0.0031273 | 0.067157 | 0.063275 | -0.0069726 | 0.010292 | -0.0022408 | -10.4233 | 64.0915 | -58.2733 | 64.0686 | -57.843 | -58.429 | -58.4198 | -7.3563 | 64.0869 | -58.1772 | 64.1235 | -58.1085 | -58.3328 | -58.1772 | -0.10528 | -0.045776 | -0.068664 | 0.32501 | -0.25177 | -0.26093 | -0.14649 | -0.15564 | -0.009155 | -0.050354 | -0.013733 | 0.059509 | -0.009155 | -0.16479 | 0 | -0.15564 | 0.4303 | 122.3419 | 0.068664 | 122.3007 | 122.3648 | 122.2641 | 122.2595 | 122.2549 | -122.4106 | -122.3145 | 122.2366 | 122.2916 | 47.7448 | 50.8118
1109.3125 | 122.6257 | -58.1543 | 64.1006 | -0.058212 | 0.0043302 | 0.064016 | 0.057031 | 0.0037598 | -0.0018928 | 0.00013254 | 0.012207 | 0.0041955 | 0.065661 | 0.059644 | -0.0078272 | 0.0094379 | 0.0009634 | -10.4874 | 64.0549 | -58.2596 | 64.1693 | -57.7194 | -58.3237 | -58.2962 | -7.3151 | 63.9954 | -58.1543 | 64.2288 | -57.9849 | -58.168 | -58.0673 | -0.10529 | -0.045776 | 0.068665 | 0.43488 | -0.14191 | -0.16937 | -0.036621 | -0.064086 | 0 | -0.10529 | 0.12817 | 0.16937 | 0.086975 | -0.013733 | 0.086975 | -0.013733 | 0.54016 | 122.4289 | 0.16937 | 122.3831 | 122.3145 | 122.1497 | 122.2092 | 122.1497 | -122.3602 | -122.2549 | 122.3236 | 122.3831 | 47.6669 | 50.8392
1110.3125 | 122.6257 | -58.1223 | 64.119 | -0.042954 | 0.0026212 | 0.062735 | 0.05874 | 0.00098262 | -0.0025336 | -0.0030719 | 0.036621 | 0.00099115 | 0.067157 | 0.058789 | -0.0063318 | 0.0094379 | -0.0026682 | -10.5789 | 64.0732 | -58.2596 | 64.1785 | -57.6828 | -58.3282 | -58.287 | -7.3608 | 64.0045 | -58.1589 | 64.2242 | -57.9575 | -58.1497 | -58.0444 | -0.13733 | -0.045777 | 0.059509 | 0.43945 | -0.16479 | -0.20599 | -0.027465 | -0.068664 | -0.036622 | -0.11444 | 0.10528 | 0.16479 | 0.077819 | -0.027466 | 0.11444 | 0.009156 | 0.57678 | 122.4381 | 0.20142 | 122.3831 | 122.3328 | 122.1634 | 122.1954 | 122.1268 | -122.3785 | -122.2778 | 122.3007 | 122.3465 | 47.5433 | 50.7614
1111.3125 | 122.5754 | -58.1268 | 64.1693 | -0.14214 | 0.0030484 | 0.063803 | 0.059167 | -8.538e-05 | -0.0027472 | 0.00013254 | 0.027466 | 0.0022729 | 0.064807 | 0.058148 | -0.0071864 | 0.0094379 | -0.0030954 | -10.6064 | 64.0457 | -58.2458 | 64.2059 | -57.6462 | -58.3008 | -58.2779 | -7.4112 | 64.0366 | -58.1543 | 64.2288 | -57.9758 | -58.1772 | -58.0627 | -0.11902 | -0.1236 | 0.036621 | 0.48065 | -0.15106 | -0.17395 | -0.032043 | -0.054931 | -0.027466 | -0.13275 | 0.059509 | 0.15106 | 0.064087 | -0.050354 | 0.091553 | -0.022888 | 0.59967 | 122.4518 | 0.17853 | 122.3831 | 122.2916 | 122.1909 | 122.1725 | 122.1634 | -122.4152 | -122.3236 | 122.3328 | 122.3557 | 47.5204 | 50.7156
1112.3125 | 122.5067 | -58.1406 | 64.183 | 0.010452 | 0.0026212 | 0.063162 | 0.060663 | 0.00055542 | -0.0029608 | -0.0034991 | -0.064087 | 0.0033411 | 0.067798 | 0.062421 | -0.0069726 | 0.0094379 | -0.0020272 | -10.8398 | 64.1098 | -58.2687 | 64.1006 | -57.7881 | -58.3923 | -58.3649 | -7.6401 | 64.0961 | -58.1589 | 64.1647 | -58.0627 | -58.2733 | -58.1177 | -0.12817 | -0.073242 | -0.082397 | 0.35248 | -0.2243 | -0.25177 | -0.09613 | -0.1236 | -0.018311 | -0.086975 | -0.01831 | 0.07782 | 0.022888 | -0.13275 | 0.041199 | -0.11444 | 0.48065 | 122.3694 | 0.096131 | 122.3236 | 122.3785 | 122.2549 | 122.2504 | 122.2366 | -122.4518 | -122.3419 | 122.2412 | 122.3053 | 47.3007 | 50.5005
1113.3125 | 122.4884 | -58.1635 | 64.2014 | 0.0028229 | 0.0060392 | 0.065298 | 0.05874 | 0.00076902 | -0.00232 | -0.00072206 | -0.079346 | 0.0018457 | 0.066089 | 0.054089 | -0.00505 | 0.0098651 | -0.0037362 | -10.9451 | 64.1418 | -58.2733 | 64.1098 | -57.811 | -58.3923 | -58.3786 | -7.7866 | 64.1052 | -58.1589 | 64.1373 | -58.0719 | -58.3054 | -58.1635 | -0.10986 | -0.059509 | -0.091553 | 0.35248 | -0.21515 | -0.22888 | -0.10529 | -0.11902 | 0.004577 | -0.09613 | -0.064087 | 0.091553 | 0 | -0.14191 | -0.004577 | -0.14648 | 0.46234 | 122.3831 | 0.086976 | 122.2961 | 122.4152 | 122.2641 | 122.3053 | 122.2687 | -122.4747 | -122.3602 | 122.2733 | 122.3007 | 47.2183 | 50.3769
1114.3125 | 122.6028 | -58.1131 | 64.1647 | -0.042954 | 0.0030484 | 0.065298 | 0.057458 | -0.0022218 | -0.003388 | 0.00034614 | 0.039673 | 0.0035547 | 0.066089 | 0.058362 | -0.005691 | 0.0098651 | -0.0024546 | -11.0046 | 64.0915 | -58.2321 | 64.238 | -57.637 | -58.2916 | -58.255 | -7.7225 | 64.0366 | -58.1085 | 64.2288 | -57.9575 | -58.1726 | -58.0307 | -0.11902 | -0.073242 | 0.073242 | 0.47607 | -0.14191 | -0.17853 | -0.022888 | -0.059509 | 0.004577 | -0.12817 | 0.064087 | 0.15564 | 0.082397 | -0.059509 | 0.07782 | -0.064086 | 0.59509 | 122.4701 | 0.15106 | 122.3373 | 122.3236 | 122.1451 | 122.2046 | 122.1497 | -122.3969 | -122.2733 | 122.3511 | 122.3419 | 47.1085 | 50.3906
1115.3125 | 122.4884 | -58.1177 | 64.2059 | -0.012436 | 0.0019802 | 0.060812 | 0.059808 | -0.00051278 | -0.0014654 | -0.00050846 | -0.0061035 | 0.0035547 | 0.065875 | 0.055585 | -0.0071864 | 0.0096515 | -0.0035226 | -11.087 | 64.1098 | -58.2321 | 64.1876 | -57.6828 | -58.3008 | -58.2916 | -7.8598 | 64.1006 | -58.1497 | 64.1693 | -58.0353 | -58.2413 | -58.1268 | -0.11444 | -0.096131 | -0.018311 | 0.43488 | -0.17395 | -0.1831 | -0.059509 | -0.068664 | -0.032043 | -0.10529 | -0.036621 | 0.082398 | -0.009155 | -0.1236 | 0.022888 | -0.091553 | 0.54932 | 122.4197 | 0.11444 | 122.319 | 122.3419 | 122.2504 | 122.2275 | 122.2183 | -122.4381 | -122.3557 | 122.3053 | 122.287 | 47.0306 | 50.2579
1116.3125 | 122.4884 | -58.1451 | 64.2014 | -0.012436 | 0.0039028 | 0.064871 | 0.059381 | -0.00051278 | -0.0036018 | -0.0020039 | -0.0091553 | 0.0041955 | 0.068225 | 0.060284 | -0.0046228 | 0.012642 | 0.0005362 | -11.2656 | 64.1785 | -58.2321 | 64.1144 | -57.7606 | -58.3649 | -58.1726 | -8.2123 | 64.1052 | -58.1451 | 64.1418 | -58.0811 | -58.2779 | -58.1268 | -0.086975 | -0.022888 | -0.086975 | 0.38452 | -0.027465 | -0.21973 | 0.05951 | -0.13275 | 0 | -0.09613 | -0.059509 | 0.064087 | 0.018311 | -0.13275 | 0.018311 | -0.13275 | 0.4715 | 122.3465 | 0.064087 | 122.287 | 122.4106 | 122.2504 | 122.3236 | 122.2504 | -122.4335 | -122.3465 | 122.2595 | 122.287 | 46.8796 | 49.9329
1117.3125 | 122.5159 | -58.1039 | 64.2059 | -0.035324 | 0.0019802 | 0.065085 | 0.061944 | -0.0024354 | -0.00232 | -0.00072206 | -0.079346 | 0.0031273 | 0.065875 | 0.060925 | -0.0078272 | 0.012215 | -0.0054452 | -11.3434 | 64.1464 | -58.2184 | 64.1418 | -57.7194 | -58.3282 | -58.3145 | -8.0566 | 64.1052 | -58.1177 | 64.2105 | -58.0078 | -58.2367 | -58.0948 | -0.11444 | -0.05951 | -0.064087 | 0.38452 | -0.21057 | -0.2243 | -0.09613 | -0.10986 | -0.013733 | -0.10071 | 0.004577 | 0.096131 | 0.009155 | -0.13275 | 0.022888 | -0.11902 | 0.49896 | 122.3602 | 0.10986 | 122.3282 | 122.3648 | 122.2229 | 122.2504 | 122.2092 | -122.4243 | -122.3236 | 122.2458 | 122.3145 | 46.7606 | 50.0473
1118.3125 | 122.5754 | -58.049 | 64.2197 | -0.035324 | 0.0051846 | 0.061026 | 0.057886 | -0.0015808 | -0.003388 | 0.0014141 | 0.0091553 | 0.0035547 | 0.065448 | 0.062207 | -0.0082544 | 0.0092241 | -0.0030954 | -11.4578 | 64.1418 | -58.168 | 64.2517 | -57.6096 | -58.2458 | -58.2138 | -8.0612 | 64.0778 | -58.0856 | 64.2609 | -57.9346 | -58.136 | -58.0215 | -0.11902 | -0.07782 | 0.032043 | 0.43945 | -0.16479 | -0.19684 | -0.045776 | -0.07782 | -0.036621 | -0.14191 | 0.041198 | 0.11444 | 0.027466 | -0.086975 | 0.064087 | -0.050354 | 0.55847 | 122.4197 | 0.15106 | 122.3465 | 122.3099 | 122.1634 | 122.1909 | 122.1268 | -122.3877 | -122.3053 | 122.3007 | 122.3099 | 46.5912 | 49.9878
1119.3125 | 122.5525 | -58.0719 | 64.1739 | -0.027695 | 0.0028348 | 0.063589 | 0.057245 | -0.002649 | -0.0027472 | -0.0020039 | 0.057983 | 0.00035035 | 0.068011 | 0.052167 | -0.010177 | 0.010933 | -0.003309 | -11.5311 | 64.119 | -58.1772 | 64.2426 | -57.5729 | -58.2047 | -58.1818 | -8.1345 | 64.0961 | -58.0811 | 64.1144 | -58.0032 | -58.0353 | -57.9163 | -0.10529 | -0.054931 | 0.068665 | 0.49896 | -0.10986 | -0.13275 | -0.004578 | -0.027466 | -0.009156 | -0.07782 | -0.059509 | 0.068664 | 0.15564 | 0.036621 | 0.16479 | 0.045777 | 0.60425 | 122.4197 | 0.07782 | 122.1954 | 122.2961 | 122.1771 | 122.1909 | 122.168 | -122.3511 | -122.2549 | 122.3145 | 122.1863 | 46.5408 | 49.9374
1120.3125 | 122.4701 | -58.1039 | 64.2563 | 0.010452 | 0.002194 | 0.062521 | 0.061303 | 0.0016236 | -0.0070196 | 0.0012005 | -0.045776 | 0.0046227 | 0.06972 | 0.063702 | -0.0086816 | 0.012429 | -0.0013864 | -11.6867 | 64.1739 | -58.2092 | 64.1418 | -57.7423 | -58.3374 | -58.3145 | -8.4137 | 64.1464 | -58.1131 | 64.1968 | -58.0261 | -58.255 | -58.0673 | -0.10529 | -0.082398 | -0.11444 | 0.36163 | -0.21057 | -0.23346 | -0.10529 | -0.12817 | -0.009155 | -0.10986 | -0.05951 | 0.07782 | 0.036621 | -0.15106 | 0.045776 | -0.14191 | 0.46692 | 122.3511 | 0.086975 | 122.3099 | 122.3831 | 122.2595 | 122.2778 | 122.2504 | -122.4655 | -122.3694 | 122.2458 | 122.3007 | 46.4172 | 49.6902
1121.3125 | 122.5067 | -58.0673 | 64.2517 | -0.081101 | 0.0030484 | 0.060599 | 0.060663 | -0.0017944 | -0.004029 | -0.0041401 | 0.015259 | 0.0044091 | 0.066302 | 0.063702 | -0.0065454 | 0.0090105 | -0.0009592 | -11.705 | 64.1647 | -58.1451 | 64.2242 | -57.6141 | -58.2687 | -58.2413 | -8.4091 | 64.1418 | -58.0856 | 64.2014 | -57.9895 | -58.2184 | -58.0536 | -0.07782 | -0.086975 | -0.027466 | 0.45319 | -0.17395 | -0.20142 | -0.09613 | -0.1236 | -0.01831 | -0.10986 | -0.050354 | 0.07782 | 0.013733 | -0.15106 | 0.032043 | -0.13275 | 0.53101 | 122.3694 | 0.09613 | 122.287 | 122.3099 | 122.2275 | 122.2321 | 122.2092 | -122.3969 | -122.3373 | 122.2916 | 122.2687 | 46.3623 | 49.6582
1122.3125 | 122.4792 | -58.0765 | 64.2517 | -0.058212 | 0.0036892 | 0.065725 | 0.060449 | 0.0037598 | -0.004029 | -0.0024311 | -0.088501 | 0.0050501 | 0.067584 | 0.062848 | -0.0078272 | 0.0098651 | -0.005018 | -11.8744 | 64.1556 | -58.2047 | 64.183 | -57.6965 | -58.342 | -58.3282 | -8.5968 | 64.1418 | -58.1039 | 64.2105 | -58.0307 | -58.2733 | -58.0856 | -0.12817 | -0.09613 | -0.068665 | 0.37994 | -0.25177 | -0.2655 | -0.1236 | -0.13733 | -0.027466 | -0.10986 | -0.041199 | 0.045776 | -0.009155 | -0.19684 | 0.018311 | -0.16937 | 0.50812 | 122.3877 | 0.073242 | 122.3145 | 122.3602 | 122.2458 | 122.2321 | 122.2183 | -122.4564 | -122.3557 | 122.2595 | 122.287 | 46.2021 | 49.4797
1123.3125 | 122.4655 | -58.0948 | 64.2654 | -0.11162 | 0.002194 | 0.061453 | 0.059381 | 0.0029052 | -0.0018928 | -0.0022175 | 0.073242 | 0.0020593 | 0.068652 | 0.056226 | -0.0059046 | 0.010292 | -0.0016 | -12.0071 | 64.2105 | -58.168 | 64.1647 | -57.6782 | -58.3282 | -58.2962 | -8.6609 | 64.2151 | -58.0811 | 64.183 | -58.0032 | -58.255 | -58.1039 | -0.073242 | -0.054932 | -0.10071 | 0.41656 | -0.20142 | -0.23346 | -0.12817 | -0.16022 | 0.013733 | -0.050354 | -0.082398 | 0.091553 | -0.009155 | -0.16022 | -0.022888 | -0.17395 | 0.48981 | 122.3328 | 0.07782 | 122.2641 | 122.3785 | 122.2961 | 122.3053 | 122.3099 | -122.4335 | -122.3465 | 122.2595 | 122.2778 | 46.0876 | 49.4339
1124.3125 | 122.4976 | -58.0399 | 64.2563 | -0.012436 | 0.0030484 | 0.064016 | 0.057886 | 0.0011962 | -0.0055244 | -0.0026447 | 0.012207 | 0.0033411 | 0.066729 | 0.060712 | -0.0063318 | 0.0098651 | -0.000532 | -12.0026 | 64.1922 | -58.136 | 64.2471 | -57.5912 | -58.223 | -58.2047 | -8.725 | 64.151 | -58.0627 | 64.2288 | -57.9391 | -58.1955 | -58.0353 | -0.09613 | -0.064087 | -0.009156 | 0.44861 | -0.16479 | -0.1831 | -0.068665 | -0.086975 | -0.022888 | -0.10529 | -0.027466 | 0.10071 | 0.004578 | -0.15564 | 0.027466 | -0.13275 | 0.54474 | 122.3831 | 0.1236 | 122.2916 | 122.3282 | 122.2137 | 122.2321 | 122.1909 | -122.3923 | -122.319 | 122.287 | 122.2687 | 46.0373 | 49.3149
1125.3125 | 122.4884 | -58.049 | 64.2792 | -0.042954 | 0.003262 | 0.063162 | 0.060663 | -0.0024354 | -0.0044562 | -0.0028583 | -0.039673 | 0.0016321 | 0.068652 | 0.060925 | -0.0061182 | 0.010933 | -0.0007456 | -12.1902 | 64.2197 | -58.1818 | 64.1693 | -57.6782 | -58.3099 | -58.2779 | -8.8943 | 64.1739 | -58.0582 | 64.2242 | -57.9758 | -58.2092 | -58.049 | -0.13275 | -0.059509 | -0.10986 | 0.37079 | -0.22888 | -0.26093 | -0.09613 | -0.12817 | -0.009156 | -0.10529 | -0.054932 | 0.073242 | 0 | -0.16022 | 0.009156 | -0.15106 | 0.50354 | 122.3511 | 0.082398 | 122.2824 | 122.4014 | 122.2321 | 122.2687 | 122.2229 | -122.4609 | -122.3373 | 122.2183 | 122.2733 | 45.8588 | 49.1547
1126.3125 | 122.5388 | -58.0399 | 64.2929 | -0.050583 | 0.0041166 | 0.064016 | 0.060022 | 0.0018372 | -0.003388 | -0.00029486 | 0.015259 | 0.0031273 | 0.065448 | 0.061993 | -0.0037684 | 0.0098651 | -0.0016 | -12.1628 | 64.1876 | -58.1406 | 64.2563 | -57.5546 | -58.2001 | -58.1772 | -8.8943 | 64.1602 | -58.0673 | 64.2609 | -57.9163 | -58.1451 | -58.0032 | -0.10071 | -0.10529 | -0.036621 | 0.48523 | -0.13733 | -0.16022 | -0.036621 | -0.059509 | -0.027466 | -0.13275 | -0.032044 | 0.1236 | 0.036621 | -0.10529 | 0.064087 | -0.07782 | 0.58594 | 122.3969 | 0.15106 | 122.3282 | 122.3282 | 122.2275 | 122.2275 | 122.2 | -122.4335 | -122.3602 | 122.2961 | 122.3007 | 45.8771 | 49.1455
1127.3125 | 122.5204 | -58.0215 | 64.2746 | -0.012436 | 0.0041166 | 0.062521 | 0.061303 | -0.00051278 | -0.0027472 | -0.00093566 | -0.14954 | 0.0037683 | 0.06502 | 0.050671 | -0.0063318 | 0.010933 | 0.0013906 | -12.3001 | 64.1876 | -58.1543 | 64.2151 | -57.5958 | -58.2733 | -58.2458 | -8.9172 | 64.1693 | -58.0627 | 64.27 | -57.9025 | -58.1818 | -58.0032 | -0.13275 | -0.086975 | -0.059509 | 0.42572 | -0.2243 | -0.25177 | -0.091553 | -0.11902 | -0.041199 | -0.10528 | -0.004577 | 0.11902 | 0.01831 | -0.16022 | 0.059509 | -0.11902 | 0.55847 | 122.3694 | 0.16022 | 122.3328 | 122.3419 | 122.2321 | 122.2092 | 122.1909 | -122.4289 | -122.3373 | 122.2366 | 122.2916 | 45.7214 | 49.1043
1128.3125 | 122.4884 | -58.0215 | 64.3524 | -0.058212 | 0.0047574 | 0.063803 | 0.058099 | 0.00055542 | -0.0029608 | -0.0026447 | 0.015259 | 0.0027001 | 0.066516 | 0.051953 | -0.0054774 | 0.010079 | 0.0007498 | -12.3825 | 64.2334 | -58.1223 | 64.2105 | -57.6233 | -58.287 | -58.2321 | -9.1415 | 64.2059 | -58.0536 | 64.2197 | -57.9575 | -58.0765 | -57.8567 | -0.10071 | -0.11902 | -0.14191 | 0.39825 | -0.21057 | -0.2655 | -0.10986 | -0.16479 | -0.032044 | -0.14648 | -0.13275 | 0.064087 | 0.1648 | -0.054932 | 0.19684 | -0.022888 | 0.49896 | 122.3328 | 0.096131 | 122.2733 | 122.3557 | 122.2595 | 122.2549 | 122.2275 | -122.4747 | -122.406 | 122.2321 | 122.2412 | 45.639 | 48.88
1129.3125 | 122.4655 | -58.0353 | 64.2975 | -0.065842 | 0.0019802 | 0.063162 | 0.059167 | -0.003717 | -0.00061096 | -0.0017903 | 0.030518 | 0.0024865 | 0.06737 | 0.060071 | -0.0063318 | 0.0085833 | -0.0003182 | -12.4832 | 64.2654 | -58.1131 | 64.2197 | -57.6004 | -58.2413 | -58.2047 | -9.2468 | 64.2105 | -58.0215 | 64.2288 | -57.9437 | -58.1589 | -58.0444 | -0.07782 | -0.032043 | -0.077819 | 0.43487 | -0.16937 | -0.20599 | -0.091553 | -0.12817 | 0.013733 | -0.086975 | -0.068664 | 0.091552 | -0.009156 | -0.1236 | -0.022889 | -0.13733 | 0.5127 | 122.3328 | 0.077819 | 122.2504 | 122.3785 | 122.2321 | 122.3007 | 122.2458 | -122.4106 | -122.319 | 122.2549 | 122.2641 | 45.5521 | 48.7885
1130.3125 | 122.4792 | -58.0215 | 64.3524 | 0.03334 | 0.0030484 | 0.061239 | 0.059595 | -0.002008 | -0.0042426 | -0.0026447 | -0.024414 | 0.00035035 | 0.068011 | 0.056653 | -0.0071864 | 0.010292 | -0.0026682 | -12.4878 | 64.3021 | -58.0948 | 64.2014 | -57.6965 | -58.2458 | -58.2458 | -9.343 | 64.2151 | -58.0399 | 64.238 | -57.9437 | -58.1909 | -58.0307 | -0.073243 | -0.050354 | -0.15106 | 0.32501 | -0.2243 | -0.2243 | -0.15106 | -0.15106 | -0.018311 | -0.13733 | -0.11444 | 0.077819 | -0.009156 | -0.16937 | 0.009155 | -0.15106 | 0.39825 | 122.2961 | 0.09613 | 122.2778 | 122.3969 | 122.2549 | 122.3236 | 122.2366 | -122.4472 | -122.3923 | 122.2229 | 122.2595 | 45.5338 | 48.6786
1131.3125 | 122.4838 | -58.017 | 64.3204 | -0.073471 | 0.0026212 | 0.06188 | 0.058526 | -0.0039306 | -0.0048834 | -0.0028583 | -0.021362 | 0.0037683 | 0.066089 | 0.062634 | -0.0074 | 0.0083697 | -0.0020272 | -12.7441 | 64.2746 | -58.1268 | 64.1693 | -57.8339 | -58.374 | -58.2047 | -9.4437 | 64.2059 | -58.0399 | 64.2242 | -57.9529 | -58.1497 | -58.0261 | -0.10986 | -0.045777 | -0.15106 | 0.18311 | -0.18768 | -0.35706 | -0.07782 | -0.24719 | -0.022888 | -0.11444 | -0.096131 | 0.064087 | -0.009155 | -0.13275 | 0.013733 | -0.10986 | 0.29297 | 122.2961 | 0.086975 | 122.2641 | 122.4014 | 122.2458 | 122.2916 | 122.2229 | -122.4472 | -122.3602 | 122.1863 | 122.2412 | 45.2728 | 48.5733
1132.3125 | 122.4472 | -58.0536 | 64.27 | -0.081101 | 0.002194 | 0.064444 | 0.061731 | 0.0022644 | -0.0018928 | 0.00077334 | -0.085449 | 0.0041955 | 0.066516 | 0.069257 | -0.0054774 | 0.011788 | -0.000532 | -12.8769 | 64.2197 | -58.1863 | 64.1693 | -57.6599 | -58.3237 | -58.3054 | -9.6725 | 64.2105 | -58.0673 | 64.2014 | -58.017 | -58.2642 | -58.0673 | -0.13275 | -0.050354 | -0.10071 | 0.39368 | -0.25177 | -0.27008 | -0.11902 | -0.13733 | -0.013733 | -0.05951 | -0.068665 | 0.036621 | -0.013733 | -0.21057 | 0 | -0.19684 | 0.52643 | 122.3557 | 0.050354 | 122.2687 | 122.406 | 122.2778 | 122.2733 | 122.2641 | -122.4564 | -122.3373 | 122.2229 | 122.2549 | 45.1767 | 48.381
1133.3125 | 122.5067 | -57.9987 | 64.3204 | -0.012436 | 0.0036892 | 0.064444 | 0.059167 | 0.0039734 | -0.0021064 | -0.0015765 | 0.039673 | 0.0012047 | 0.067157 | 0.060071 | -0.0059046 | 0.0079425 | -0.0001046 | -12.8769 | 64.238 | -58.0902 | 64.3021 | -57.4951 | -58.1726 | -58.136 | -9.5856 | 64.2105 | -58.0032 | 64.2975 | -57.8659 | -58.1131 | -57.9575 | -0.091553 | -0.082398 | -0.018311 | 0.50354 | -0.13733 | -0.17395 | -0.045776 | -0.082397 | -0.004578 | -0.10986 | -0.022889 | 0.13275 | 0.041199 | -0.11444 | 0.045777 | -0.10986 | 0.59509 | 122.3923 | 0.13733 | 122.3007 | 122.3282 | 122.2137 | 122.2366 | 122.2092 | -122.4106 | -122.3236 | 122.3007 | 122.2961 | 45.1218 | 48.4131
1134.3125 | 122.4976 | -57.9758 | 64.325 | -0.058212 | 0.0034756 | 0.064444 | 0.057672 | -0.0011536 | -0.005097 | -0.0037129 | 0.033569 | 0.0016321 | 0.065448 | 0.060498 | -0.005691 | 0.0094379 | -0.0024546 | -12.9501 | 64.2471 | -58.0948 | 64.3204 | -57.4768 | -58.1451 | -58.1085 | -9.6725 | 64.2105 | -58.0078 | 64.3295 | -57.8339 | -58.0902 | -57.9391 | -0.11902 | -0.07782 | -0.004577 | 0.49896 | -0.13275 | -0.16937 | -0.013733 | -0.050354 | -0.032043 | -0.11444 | 0.004578 | 0.14191 | 0.036621 | -0.11444 | 0.068664 | -0.082398 | 0.61798 | 122.4152 | 0.17395 | 122.3373 | 122.3419 | 122.2183 | 122.2229 | 122.1863 | -122.4197 | -122.3328 | 122.2961 | 122.3053 | 45.0256 | 48.3032
1135.3125 | 122.5296 | -57.9941 | 64.3478 | 0.0028229 | 0.0009122 | 0.06188 | 0.062585 | 0.0011962 | -0.0027472 | -0.00072206 | -0.027466 | 0.0039819 | 0.068438 | 0.059644 | -0.009109 | 0.0081561 | -0.0026682 | -13.1241 | 64.2746 | -58.1177 | 64.2563 | -57.5821 | -58.2367 | -58.1863 | -9.8511 | 64.2609 | -58.0078 | 64.3158 | -57.8751 | -58.1406 | -57.9437 | -0.1236 | -0.073242 | -0.091552 | 0.41199 | -0.19226 | -0.24261 | -0.068664 | -0.11902 | -0.013732 | -0.086975 | -0.032043 | 0.11902 | 0.050354 | -0.14648 | 0.064086 | -0.13275 | 0.53558 | 122.374 | 0.13275 | 122.3236 | 122.3923 | 122.2687 | 122.2687 | 122.2549 | -122.4655 | -122.3557 | 122.2504 | 122.3099 | 44.87 | 48.143
1136.3125 | 122.4747 | -57.9803 | 64.3478 | 0.071487 | 0.0013394 | 0.063803 | 0.058954 | 0.00012822 | -0.004029 | -0.0015765 | -0.012207 | 0.0018457 | 0.066943 | 0.056439 | -0.003982 | 0.0098651 | 0.0003226 | -13.3209 | 64.325 | -58.1039 | 64.238 | -57.5775 | -58.2733 | -58.2047 | -9.9472 | 64.2471 | -58.0078 | 64.2654 | -57.8934 | -58.1314 | -57.9803 | -0.1236 | -0.022888 | -0.10986 | 0.40283 | -0.2243 | -0.29297 | -0.10071 | -0.16937 | -0.027465 | -0.10071 | -0.082397 | 0.086975 | 0 | -0.15106 | 0.027465 | -0.1236 | 0.52643 | 122.3419 | 0.11444 | 122.2733 | 122.4289 | 122.2549 | 122.3053 | 122.2275 | -122.4518 | -122.3557 | 122.2183 | 122.2458 | 44.6594 | 48.0331
1137.3125 | 122.5204 | -57.9712 | 64.3433 | 0.071487 | 0.0024076 | 0.062948 | 0.060663 | -0.00093998 | -0.0042426 | -0.00050846 | -0.067139 | 0.0037683 | 0.06737 | 0.059216 | -0.006759 | 0.011361 | -0.0016 | -13.298 | 64.2883 | -58.0948 | 64.2975 | -57.518 | -58.1955 | -58.1818 | -10.0433 | 64.2471 | -58.0032 | 64.3021 | -57.8659 | -58.1268 | -57.9529 | -0.1236 | -0.054932 | -0.045777 | 0.45319 | -0.21057 | -0.22431 | -0.086975 | -0.10071 | -0.032044 | -0.096131 | -0.041199 | 0.10528 | 0.01831 | -0.15564 | 0.050354 | -0.1236 | 0.57678 | 122.3923 | 0.13733 | 122.3053 | 122.3831 | 122.2504 | 122.2595 | 122.2183 | -122.4381 | -122.3465 | 122.2687 | 122.2733 | 44.6732 | 47.9279
1138.3125 | 122.4701 | -57.9895 | 64.3707 | -0.012436 | 0.0028348 | 0.06188 | 0.058526 | 0.00012822 | -0.0036018 | 0.00055974 | 0.033569 | 0.0014185 | 0.068866 | 0.060925 | -0.00505 | 0.0094379 | 0.001177 | -13.4033 | 64.3158 | -58.0719 | 64.4028 | -57.4036 | -58.4976 | -58.3557 | -10.1807 | 64.2654 | -57.9987 | 64.2975 | -57.8934 | -58.1268 | -57.9803 | -0.082397 | -0.054932 | 0.032043 | 0.58594 | -0.36621 | -0.50812 | -0.28381 | -0.42572 | -0.009155 | -0.10529 | -0.073243 | 0.09613 | 0.009155 | -0.13733 | 0.01831 | -0.12817 | 0.66833 | 122.4747 | 0.10529 | 122.2961 | 122.3877 | 122.2641 | 122.3053 | 122.2549 | -122.4426 | -122.3694 | 122.3923 | 122.287 | 44.5862 | 47.8088
1139.3125 | 122.493 | -57.9803 | 64.3616 | -0.027695 | 0.003262 | 0.063803 | 0.056177 | -0.003717 | -0.0027472 | 0.00013254 | 0.039673 | 0.0018457 | 0.066302 | 0.061566 | -0.0059046 | 0.01072 | -0.0048044 | -13.4125 | 64.2792 | -58.0582 | 64.3295 | -57.4677 | -58.1314 | -58.1223 | -10.2127 | 64.2563 | -57.9575 | 64.3158 | -57.8522 | -58.0673 | -57.9391 | -0.07782 | -0.082397 | -0.032043 | 0.5127 | -0.14191 | -0.15106 | -0.064086 | -0.073242 | 0.022889 | -0.10528 | -0.045776 | 0.12817 | 0.041199 | -0.086975 | 0.01831 | -0.10986 | 0.59052 | 122.3877 | 0.10529 | 122.2733 | 122.3373 | 122.2137 | 122.2595 | 122.2366 | -122.4197 | -122.319 | 122.3099 | 122.2961 | 44.5679 | 47.7676
1140.3125 | 122.438 | -57.9803 | 64.3341 | -0.035324 | 0.003262 | 0.063589 | 0.060663 | -0.00029898 | -0.0025336 | -0.0013629 | -0.054932 | 0.0039819 | 0.066729 | 0.053448 | -0.0069726 | 0.010506 | -0.0020272 | -13.5956 | 64.27 | -58.1268 | 64.238 | -57.5958 | -58.255 | -58.2413 | -10.4828 | 64.2746 | -58.0032 | 64.2746 | -57.9575 | -58.2092 | -58.0078 | -0.14648 | -0.064086 | -0.09613 | 0.38452 | -0.26093 | -0.27466 | -0.11444 | -0.12817 | -0.022888 | -0.059509 | -0.059509 | 0.022889 | -0.027465 | -0.22888 | -0.004577 | -0.20599 | 0.53101 | 122.3648 | 0.045777 | 122.2778 | 122.3969 | 122.2778 | 122.2504 | 122.2549 | -122.4609 | -122.3373 | 122.2183 | 122.2549 | 44.3848 | 47.4976
1141.3125 | 122.5113 | -57.93 | 64.3707 | -0.012436 | 0.002194 | 0.064016 | 0.059595 | -8.538e-05 | -0.0036018 | 0.00034614 | 0.048828 | 0.0031273 | 0.066729 | 0.064557 | -0.0061182 | 0.01072 | -0.0054452 | -13.6276 | 64.3021 | -58.0215 | 64.3524 | -57.4265 | -58.1085 | -58.0673 | -10.405 | 64.2654 | -57.9208 | 64.3433 | -57.811 | -58.0536 | -57.9071 | -0.091552 | -0.068665 | -0.018311 | 0.50354 | -0.13733 | -0.17853 | -0.045777 | -0.086976 | 0.009156 | -0.10529 | -0.027466 | 0.11902 | 0.022889 | -0.1236 | 0.013733 | -0.13275 | 0.59509 | 122.374 | 0.10986 | 122.2641 | 122.3236 | 122.1863 | 122.2321 | 122.1954 | -122.3923 | -122.2916 | 122.2824 | 122.2733 | 44.3024 | 47.525
1142.3125 | 122.4609 | -57.9666 | 64.3341 | -0.035324 | 0.0028348 | 0.065512 | 0.061731 | -8.538e-05 | -0.0031744 | -0.0022175 | -0.045776 | 0.0041955 | 0.066302 | 0.064984 | -0.0069726 | 0.011147 | -0.0030954 | -13.7787 | 64.3066 | -58.0811 | 64.2609 | -57.5775 | -58.2596 | -58.2138 | -10.6796 | 64.2883 | -57.9803 | 64.2746 | -57.9346 | -58.1863 | -57.9803 | -0.11444 | -0.027465 | -0.073242 | 0.3891 | -0.24719 | -0.29297 | -0.13275 | -0.17853 | -0.013733 | -0.045776 | -0.059509 | 0.032044 | -0.013733 | -0.21973 | 0 | -0.20599 | 0.50354 | 122.3419 | 0.045777 | 122.2549 | 122.3877 | 122.2687 | 122.2733 | 122.2549 | -122.4152 | -122.3145 | 122.2275 | 122.2412 | 44.1879 | 47.287
1143.3125 | 122.4701 | -57.962 | 64.3845 | -0.0048066 | 0.0039028 | 0.061453 | 0.059595 | -0.002008 | -0.0016792 | -0.0013629 | 0.027466 | 0.00035035 | 0.065234 | 0.061352 | -0.00505 | 0.01072 | -0.0001046 | -13.8611 | 64.3295 | -58.0307 | 64.2975 | -57.4997 | -58.1772 | -58.1589 | -10.6934 | 64.2883 | -57.9575 | 64.2517 | -57.9849 | -58.0673 | -57.8705 | -0.068665 | -0.054931 | -0.086975 | 0.46234 | -0.19684 | -0.21515 | -0.12817 | -0.14648 | 0.004578 | -0.09613 | -0.13275 | -0.022888 | 0.091553 | -0.10529 | 0.086975 | -0.10986 | 0.53101 | 122.3282 | -0.027466 | 122.2092 | 122.3602 | 122.2458 | 122.2916 | 122.2504 | -122.4152 | -122.3419 | 122.2595 | 122.2137 | 44.101 | 47.2687
1144.3125 | 122.5067 | -57.9483 | 64.3982 | -0.073471 | 0.0036892 | 0.063589 | 0.058526 | -0.00072638 | -0.0021064 | -0.0013629 | -0.0061035 | 0.0024865 | 0.067798 | 0.060925 | -0.0061182 | 0.011147 | 0.0003226 | -13.9389 | 64.357 | -58.0444 | 64.2883 | -57.5134 | -58.1863 | -58.136 | -10.8582 | 64.3066 | -57.9437 | 64.3341 | -57.8384 | -58.0765 | -57.9117 | -0.096131 | -0.041198 | -0.10986 | 0.43488 | -0.18768 | -0.23804 | -0.091552 | -0.14191 | 0.004577 | -0.091552 | -0.064087 | 0.10986 | 0.036621 | -0.12817 | 0.032044 | -0.13275 | 0.53101 | 122.3328 | 0.10529 | 122.2778 | 122.4014 | 122.2504 | 122.3053 | 122.2549 | -122.4426 | -122.3419 | 122.2366 | 122.2824 | 44.0094 | 47.0901
1145.3125 | 122.4838 | -57.9483 | 64.3845 | -0.042954 | 0.001553 | 0.065298 | 0.060663 | -0.00072638 | -0.0031744 | 0.0018413 | -0.057983 | 0.0031273 | 0.064166 | 0.058789 | -0.005691 | 0.0098651 | -0.0011728 | -14.0533 | 64.3341 | -58.1039 | 64.2838 | -57.5317 | -58.2321 | -58.1726 | -11.0504 | 64.2883 | -57.9666 | 64.3021 | -57.8979 | -58.136 | -57.9758 | -0.15564 | -0.050354 | -0.10071 | 0.41657 | -0.2243 | -0.28381 | -0.068664 | -0.12817 | -0.018311 | -0.09613 | -0.082397 | 0.050354 | -0.027466 | -0.18768 | -0.009155 | -0.16937 | 0.57221 | 122.3877 | 0.068665 | 122.2687 | 122.438 | 122.2549 | 122.2824 | 122.2366 | -122.4884 | -122.3511 | 122.2321 | 122.2504 | 43.895 | 46.8979
1146.3125 | 122.5021 | -57.9117 | 64.4257 | -0.020065 | 0.0026212 | 0.064871 | 0.060876 | 0.002478 | -0.00232 | -0.0011493 | 0.0030517 | 0.0027001 | 0.067798 | 0.062207 | -0.0065454 | 0.011147 | -0.0020272 | -14.1495 | 64.3524 | -58.0627 | 64.3112 | -57.486 | -58.1726 | -58.1406 | -11.1237 | 64.325 | -57.9391 | 64.3295 | -57.8201 | -58.0811 | -57.9025 | -0.15106 | -0.073242 | -0.11444 | 0.42572 | -0.22888 | -0.26093 | -0.07782 | -0.10986 | -0.027466 | -0.10071 | -0.09613 | 0.091553 | 0.009155 | -0.16937 | 0.036621 | -0.14191 | 0.57678 | 122.374 | 0.11902 | 122.2687 | 122.4152 | 122.2641 | 122.2641 | 122.2366 | -122.4884 | -122.3648 | 122.2229 | 122.2412 | 43.7622 | 46.788
1147.3125 | 122.5159 | -57.9391 | 64.3616 | -0.035324 | 0.0041166 | 0.063803 | 0.060663 | 0.00034182 | -0.0016792 | -0.0041401 | -0.039673 | 0.0044091 | 0.067157 | 0.06178 | -0.0063318 | 0.0098651 | -0.0016 | -14.2776 | 64.3295 | -58.0856 | 64.2517 | -57.5134 | -58.2275 | -58.1635 | -11.3022 | 64.2838 | -57.962 | 64.3387 | -57.843 | -58.1223 | -57.9163 | -0.14648 | -0.032043 | -0.10986 | 0.42572 | -0.2243 | -0.28839 | -0.07782 | -0.14191 | -0.022888 | -0.07782 | -0.022888 | 0.09613 | 0.022888 | -0.1831 | 0.045776 | -0.16022 | 0.5722 | 122.3373 | 0.11902 | 122.3007 | 122.4152 | 122.2458 | 122.2687 | 122.2229 | -122.4472 | -122.3236 | 122.1909 | 122.2778 | 43.6615 | 46.637
1148.3125 | 122.5021 | -57.9163 | 64.4257 | -0.035324 | 0.0017666 | 0.062094 | 0.058526 | -0.0017944 | -0.005738 | -0.0058491 | -0.01831 | 0.0020593 | 0.06737 | 0.06413 | -0.0063318 | 0.0081561 | 0.0016044 | -14.3234 | 64.389 | -58.017 | 64.2975 | -57.4677 | -58.1497 | -58.1268 | -11.3388 | 64.3158 | -57.9254 | 64.3524 | -57.7972 | -58.049 | -57.8979 | -0.10071 | -0.036621 | -0.12817 | 0.44861 | -0.21057 | -0.23346 | -0.10986 | -0.13275 | -0.009155 | -0.10986 | -0.073242 | 0.11902 | 0.018311 | -0.13275 | 0.027466 | -0.1236 | 0.54932 | 122.3145 | 0.12817 | 122.2778 | 122.406 | 122.2412 | 122.3053 | 122.2321 | -122.4426 | -122.3511 | 122.2137 | 122.2687 | 43.5928 | 46.5775
1149.3125 | 122.5113 | -57.8934 | 64.4302 | -0.020065 | 0.0045438 | 0.065085 | 0.058099 | -0.00072638 | -0.0010382 | -8.1264e-05 | -0.036621 | 0.0024865 | 0.066089 | 0.061139 | -0.0088952 | 0.01072 | -0.0026682 | -14.4287 | 64.3616 | -58.0124 | 64.3341 | -57.4402 | -58.1223 | -58.1131 | -11.412 | 64.325 | -57.93 | 64.4028 | -57.7515 | -58.017 | -57.8705 | -0.11902 | -0.068665 | -0.096131 | 0.45319 | -0.21973 | -0.22888 | -0.10071 | -0.10986 | -0.036621 | -0.10529 | -0.027466 | 0.14191 | 0.022889 | -0.1236 | 0.05951 | -0.086975 | 0.5722 | 122.3465 | 0.17853 | 122.3328 | 122.374 | 122.2549 | 122.2549 | 122.2183 | -122.4426 | -122.3602 | 122.2275 | 122.2961 | 43.4647 | 46.4813
1150.3125 | 122.6028 | -57.9071 | 64.3845 | -0.058212 | 0.0034756 | 0.06423 | 0.059595 | 0.002478 | -0.0018928 | -0.0022175 | 0.033569 | 0.0018457 | 0.067157 | 0.057935 | -0.0071864 | 0.010292 | -0.0024546 | -14.5157 | 64.2838 | -57.9758 | 64.4989 | -57.193 | -58.1177 | -58.0673 | -11.4899 | 64.2838 | -57.9025 | 64.4531 | -57.7103 | -57.9895 | -57.8018 | -0.068665 | -0.10071 | 0.11444 | 0.71411 | -0.16022 | -0.21057 | -0.091553 | -0.14191 | 0.004577 | -0.10071 | 0.068665 | 0.19684 | 0.10528 | -0.082398 | 0.10071 | -0.086975 | 0.78278 | 122.4747 | 0.19226 | 122.3557 | 122.2595 | 122.1863 | 122.1909 | 122.1909 | -122.3602 | -122.287 | 122.406 | 122.3602 | 43.3914 | 46.4172
1151.3125 | 122.4655 | -57.8888 | 64.444 | -0.08873 | 0.0039028 | 0.063162 | 0.061731 | -0.0011536 | -0.0016792 | -0.0015765 | -0.027466 | 0.0022729 | 0.065875 | 0.063702 | -0.0063318 | 0.0094379 | -0.0018136 | -14.74 | 64.3707 | -58.0078 | 64.325 | -57.431 | -58.1406 | -58.0994 | -11.6867 | 64.325 | -57.9254 | 64.3799 | -57.7835 | -58.0353 | -57.8796 | -0.11902 | -0.073242 | -0.11902 | 0.45776 | -0.21057 | -0.25177 | -0.091553 | -0.13275 | -0.036621 | -0.11902 | -0.064087 | 0.10529 | 0.009155 | -0.14648 | 0.045776 | -0.10986 | 0.57678 | 122.3328 | 0.14191 | 122.3053 | 122.3785 | 122.2504 | 122.2595 | 122.2137 | -122.4518 | -122.3694 | 122.2137 | 122.2687 | 43.1488 | 46.2021
1152.3125 | 122.438 | -57.8796 | 64.4348 | -0.065842 | 0.0034756 | 0.063803 | 0.061731 | -0.00072638 | -0.00039736 | 0.00013254 | -0.042725 | 0.0022729 | 0.068011 | 0.061139 | -0.0048364 | 0.010292 | -0.0035226 | -14.6988 | 64.3662 | -58.0353 | 64.3616 | -57.3898 | -58.0902 | -58.0673 | -11.7462 | 64.325 | -57.9163 | 64.4211 | -57.724 | -58.0124 | -57.9529 | -0.15564 | -0.068664 | -0.073242 | 0.48981 | -0.18768 | -0.21057 | -0.032044 | -0.054932 | -0.036621 | -0.10986 | -0.013732 | 0.15564 | -0.073242 | -0.13275 | -0.036621 | -0.09613 | 0.64545 | 122.3969 | 0.19226 | 122.3373 | 122.4014 | 122.2412 | 122.2458 | 122.2046 | -122.4701 | -122.3511 | 122.2412 | 122.3007 | 43.1808 | 46.1334
1153.3125 | 122.5067 | -57.9025 | 64.4394 | -0.073471 | 0.0017666 | 0.063803 | 0.060022 | -0.00051278 | -0.0042426 | -0.0030719 | -0.033569 | 0.0046227 | 0.064593 | 0.058575 | -0.0059046 | 0.0081561 | 0.0007498 | -14.8224 | 64.4028 | -57.9758 | 64.3341 | -57.431 | -58.1039 | -58.0902 | -11.9385 | 64.3616 | -57.8842 | 64.4119 | -57.724 | -57.9941 | -57.8476 | -0.073242 | -0.036621 | -0.10529 | 0.4715 | -0.18768 | -0.20142 | -0.11444 | -0.12817 | 0.018311 | -0.07782 | -0.027466 | 0.17853 | 0.054932 | -0.091553 | 0.036621 | -0.10986 | 0.54474 | 122.3099 | 0.16022 | 122.2961 | 122.3785 | 122.2458 | 122.3053 | 122.2641 | -122.4152 | -122.3236 | 122.2366 | 122.3145 | 43.0801 | 45.9641
1154.3125 | 122.4976 | -57.8659 | 64.4897 | -0.035324 | 0.000485 | 0.063803 | 0.058313 | -0.002008 | -0.0031744 | -0.0015765 | -0.021362 | 0.0037683 | 0.066089 | 0.056653 | -0.0071864 | 0.011147 | -0.0026682 | -14.9277 | 64.4073 | -57.962 | 64.357 | -57.4173 | -58.1085 | -58.0673 | -12.0163 | 64.3478 | -57.8842 | 64.3982 | -57.7377 | -57.9987 | -57.8476 | -0.09613 | -0.082397 | -0.13275 | 0.44861 | -0.20142 | -0.24262 | -0.10529 | -0.14649 | -0.01831 | -0.14191 | -0.091553 | 0.12817 | 0.018311 | -0.13275 | 0.036621 | -0.11444 | 0.54474 | 122.319 | 0.14648 | 122.2824 | 122.3694 | 122.2321 | 122.2733 | 122.2137 | -122.4518 | -122.374 | 122.2229 | 122.2641 | 42.9382 | 45.8496
1155.3281 | 122.5754 | -57.811 | 64.4211 | -0.012436 | 0.002194 | 0.062521 | 0.058954 | 0.0016236 | -0.00018376 | -0.0026447 | 0.11292 | 0.0020593 | 0.066729 | 0.05473 | -0.0074 | 0.0092241 | -0.0030954 | -14.9826 | 64.3845 | -57.93 | 64.4989 | -57.1838 | -58.0719 | -57.9941 | -11.9751 | 64.3204 | -57.8384 | 64.5081 | -57.6141 | -57.8842 | -57.7698 | -0.11902 | -0.036622 | 0.077819 | 0.62714 | -0.18311 | -0.26093 | -0.064087 | -0.14191 | -0.027466 | -0.10071 | 0.086975 | 0.19684 | 0.041199 | -0.073242 | 0.068665 | -0.045776 | 0.74616 | 122.4289 | 0.2243 | 122.3465 | 122.3145 | 122.1588 | 122.1954 | 122.1313 | -122.3511 | -122.2595 | 122.3099 | 122.319 | 42.8284 | 45.8359
1156.3125 | 122.5159 | -57.8476 | 64.476 | -0.058212 | 0.0019802 | 0.063803 | 0.060022 | 0.0031188 | -0.0027472 | 0.00077334 | -0.033569 | 0.0033411 | 0.066089 | 0.060498 | -0.0082544 | 0.01072 | -0.0030954 | -15.1245 | 64.4073 | -57.9849 | 64.3982 | -57.3669 | -58.0765 | -58.0399 | -12.1719 | 64.3616 | -57.8522 | 64.4394 | -57.7194 | -57.9712 | -57.8201 | -0.13733 | -0.068664 | -0.07782 | 0.48065 | -0.19226 | -0.22888 | -0.054932 | -0.091553 | -0.004578 | -0.11444 | -0.036621 | 0.12817 | 0.027466 | -0.1236 | 0.032044 | -0.11902 | 0.61798 | 122.3831 | 0.13275 | 122.2916 | 122.3923 | 122.2137 | 122.2549 | 122.2092 | -122.4609 | -122.3282 | 122.2458 | 122.287 | 42.7231 | 45.6757
1157.3125 | 122.4609 | -57.8888 | 64.4531 | -0.065842 | 0.0019802 | 0.064871 | 0.060663 | 0.00034182 | -0.0048834 | -0.0045673 | -0.045776 | 0.0016321 | 0.06502 | 0.062634 | -0.0061182 | 0.0096515 | -0.0028818 | -15.2802 | 64.389 | -57.9941 | 64.3295 | -57.4493 | -58.1635 | -58.1085 | -12.4237 | 64.3707 | -57.9071 | 64.3799 | -57.7789 | -58.0948 | -57.8979 | -0.10529 | -0.064087 | -0.1236 | 0.43945 | -0.21973 | -0.27466 | -0.11444 | -0.16937 | -0.01831 | -0.082397 | -0.073242 | 0.10986 | -0.009155 | -0.20599 | 0.009155 | -0.18768 | 0.54474 | 122.3236 | 0.12817 | 122.287 | 122.3831 | 122.2778 | 122.2778 | 122.2595 | -122.4472 | -122.3602 | 122.2183 | 122.2687 | 42.6086 | 45.4651
1158.3125 | 122.5021 | -57.8659 | 64.4989 | -0.058212 | 0.0030484 | 0.065085 | 0.059595 | 0.0018372 | -0.0036018 | -0.0049945 | 0.0091553 | 0.0024865 | 0.066516 | 0.05238 | -0.005691 | 0.0079425 | -0.0020272 | -15.3397 | 64.4073 | -57.9712 | 64.3616 | -57.3853 | -58.0948 | -58.0536 | -12.4512 | 64.3936 | -57.8842 | 64.389 | -57.7148 | -58.0032 | -57.8522 | -0.10528 | -0.091552 | -0.13733 | 0.48065 | -0.18768 | -0.22888 | -0.082398 | -0.1236 | -0.01831 | -0.10529 | -0.10986 | 0.15106 | 0.013733 | -0.13733 | 0.032043 | -0.11902 | 0.58594 | 122.3328 | 0.16937 | 122.2733 | 122.3785 | 122.2778 | 122.2733 | 122.2595 | -122.4701 | -122.3831 | 122.2275 | 122.2549 | 42.5262 | 45.4147
1159.3125 | 122.525 | -57.8201 | 64.4897 | -0.027695 | 0.0041166 | 0.062521 | 0.059808 | 0.0029052 | -0.00232 | 0.0014141 | -0.015259 | 0.0016321 | 0.066516 | 0.06178 | -0.0061182 | 0.010506 | -0.0045908 | -15.477 | 64.4257 | -57.962 | 64.3982 | -57.3761 | -58.0673 | -58.0444 | -12.5381 | 64.3799 | -57.8522 | 64.444 | -57.6874 | -57.9575 | -57.8018 | -0.14191 | -0.064087 | -0.091553 | 0.44403 | -0.22431 | -0.24719 | -0.082398 | -0.10529 | -0.032044 | -0.10986 | -0.045776 | 0.13275 | 0.01831 | -0.13733 | 0.050354 | -0.10529 | 0.58594 | 122.3602 | 0.16479 | 122.2961 | 122.3877 | 122.2321 | 122.2458 | 122.2 | -122.4518 | -122.3419 | 122.2183 | 122.2641 | 42.3431 | 45.282
1160.3281 | 122.5113 | -57.843 | 64.4669 | 0.010452 | 0.001553 | 0.063162 | 0.06109 | -0.00051278 | -0.0025336 | -0.0015765 | -0.012207 | 0.0027001 | 0.067157 | 0.061352 | -0.006759 | 0.010079 | -0.0011728 | -15.5548 | 64.4119 | -57.9391 | 64.4028 | -57.3441 | -58.0765 | -58.0307 | -12.6617 | 64.389 | -57.8293 | 64.4531 | -57.692 | -57.9666 | -57.7972 | -0.09613 | -0.054932 | -0.064087 | 0.49896 | -0.18768 | -0.23346 | -0.091553 | -0.13733 | 0.013733 | -0.07782 | -0.013733 | 0.15106 | 0.045777 | -0.1236 | 0.032044 | -0.13733 | 0.59509 | 122.3419 | 0.13733 | 122.2824 | 122.3511 | 122.2183 | 122.2549 | 122.2321 | -122.406 | -122.2961 | 122.2458 | 122.2961 | 42.2882 | 45.1813
1161.3125 | 122.4884 | -57.843 | 64.4989 | -0.020065 | 0.0024076 | 0.064016 | 0.060235 | -8.538e-05 | -0.0036018 | -0.0037129 | 0.030518 | 0.0031273 | 0.066302 | 0.057294 | -0.0044092 | 0.0083697 | -0.0035226 | -15.6647 | 64.4394 | -57.9483 | 64.3021 | -57.2937 | -58.0536 | -58.0719 | -12.8128 | 64.4073 | -57.8613 | 64.4257 | -57.7194 | -57.9895 | -57.8567 | -0.10529 | -0.059509 | -0.19684 | 0.54932 | -0.22888 | -0.21057 | -0.1236 | -0.10529 | -0.01831 | -0.091552 | -0.073242 | 0.1236 | -0.013732 | -0.14648 | 0.004578 | -0.12817 | 0.6546 | 122.2504 | 0.14191 | 122.287 | 122.3877 | 122.2687 | 122.2824 | 122.2504 | -122.4472 | -122.3602 | 122.1451 | 122.2687 | 42.1783 | 45.0302
1162.3125 | 122.4976 | -57.8339 | 64.4485 | -0.065842 | 0.0030484 | 0.068289 | 0.060235 | 0.0014098 | -0.003388 | -0.0011493 | -0.048828 | 0.0018457 | 0.066729 | 0.062421 | -0.0082544 | 0.010079 | -0.0026682 | -15.8615 | 64.3845 | -57.9666 | 64.4623 | -57.3166 | -58.0353 | -57.9941 | -12.8769 | 64.3662 | -57.8567 | 64.4531 | -57.692 | -57.962 | -57.8018 | -0.13275 | -0.064087 | 0.013733 | 0.51727 | -0.16022 | -0.20142 | -0.027466 | -0.068664 | -0.022888 | -0.082397 | 0.004578 | 0.14191 | 0.032043 | -0.12817 | 0.054931 | -0.10529 | 0.65002 | 122.4289 | 0.16479 | 122.3099 | 122.3511 | 122.2229 | 122.2183 | 122.2 | -122.4152 | -122.3053 | 122.2961 | 122.287 | 41.9724 | 44.957
1163.3281 | 122.58 | -57.8384 | 64.4623 | -0.027695 | 0.0045438 | 0.064444 | 0.058954 | 0.00098262 | -0.0046698 | -0.0024311 | 0.073242 | 0.0027001 | 0.066516 | 0.058148 | -0.0071864 | 0.010506 | -0.0039498 | -15.8798 | 64.4028 | -57.9346 | 64.4165 | -57.2845 | -58.0399 | -57.9803 | -13.0325 | 64.3478 | -57.8705 | 64.4989 | -57.6416 | -57.9117 | -57.7606 | -0.09613 | -0.059509 | -0.045776 | 0.55389 | -0.14191 | -0.20142 | -0.045777 | -0.10529 | -0.032043 | -0.11444 | 0.036621 | 0.19684 | 0.07782 | -0.073242 | 0.10986 | -0.041199 | 0.65002 | 122.3511 | 0.22888 | 122.3694 | 122.3373 | 122.2183 | 122.2412 | 122.1863 | -122.3969 | -122.3328 | 122.2549 | 122.3373 | 41.9586 | 44.8059
1164.3125 | 122.5021 | -57.8293 | 64.4989 | -0.065842 | 0.0017666 | 0.062948 | 0.061517 | 0.002478 | -0.0029608 | -0.0024311 | -0.054932 | 0.0018457 | 0.064807 | 0.062207 | -0.008468 | 0.0085833 | 0.0016044 | -15.9622 | 64.4165 | -57.9529 | 64.4394 | -57.2983 | -58.0719 | -58.0261 | -13.1561 | 64.4211 | -57.843 | 64.4531 | -57.7011 | -57.9666 | -57.8156 | -0.1236 | -0.082397 | -0.059509 | 0.53101 | -0.19684 | -0.24261 | -0.073242 | -0.11902 | -0.013733 | -0.077819 | -0.045776 | 0.12817 | 0.013733 | -0.13733 | 0.027466 | -0.1236 | 0.6546 | 122.3923 | 0.14191 | 122.2961 | 122.3694 | 122.2641 | 122.2458 | 122.2504 | -122.4518 | -122.3419 | 122.2687 | 122.2824 | 41.8671 | 44.6732
1165.3281 | 122.4609 | -57.8339 | 64.5264 | -0.10399 | 0.002194 | 0.062308 | 0.060235 | -0.00051278 | -0.004029 | -0.0054217 | 0.021362 | 0.0031273 | 0.06438 | 0.058148 | -0.0052638 | 0.0066607 | -0.0018136 | -16.1179 | 64.4714 | -57.9391 | 64.4073 | -57.3212 | -58.0444 | -58.017 | -13.1424 | 64.4531 | -57.8018 | 64.4531 | -57.7332 | -57.9529 | -57.8201 | -0.10529 | -0.054931 | -0.11902 | 0.5127 | -0.18311 | -0.21057 | -0.07782 | -0.10529 | 0.032043 | -0.073242 | -0.073242 | 0.10071 | 0.013733 | -0.11902 | -0.01831 | -0.15106 | 0.61798 | 122.3465 | 0.068665 | 122.2549 | 122.4106 | 122.2549 | 122.3053 | 122.287 | -122.4655 | -122.3282 | 122.2412 | 122.287 | 41.716 | 44.6915
1166.3125 | 122.5479 | -57.8201 | 64.5172 | 0.048599 | 0.0028348 | 0.064444 | 0.060876 | 0.0061096 | -0.0031744 | -0.0024311 | -0.054932 | 0.0016321 | 0.065661 | 0.054089 | -0.009109 | 0.01072 | -0.0039498 | -16.1636 | 64.4531 | -57.9208 | 64.4394 | -57.2708 | -58.0215 | -57.9941 | -13.3484 | 64.4119 | -57.8339 | 64.4852 | -57.6279 | -58.1451 | -57.962 | -0.10071 | -0.064087 | -0.07782 | 0.54932 | -0.17395 | -0.20142 | -0.073243 | -0.10071 | -0.013733 | -0.10529 | -0.032044 | 0.19226 | -0.14191 | -0.32501 | -0.12817 | -0.31128 | 0.65002 | 122.3602 | 0.20599 | 122.319 | 122.374 | 122.2458 | 122.2733 | 122.2321 | -122.438 | -122.3511 | 122.2595 | 122.3053 | 41.6565 | 44.4717
1167.3125 | 122.493 | -57.8064 | 64.4806 | 0.10963 | 0.0041166 | 0.065298 | 0.061731 | 0.0018372 | -0.004029 | -0.00072206 | -0.039673 | 0.0029137 | 0.065234 | 0.058148 | -0.0082544 | 0.0098651 | -0.0013864 | -16.301 | 64.4348 | -57.93 | 64.4714 | -57.2708 | -58.0124 | -57.9987 | -13.4949 | 64.4028 | -57.8247 | 64.4852 | -57.6599 | -57.9483 | -57.7789 | -0.1236 | -0.045777 | -0.009155 | 0.53558 | -0.19226 | -0.20599 | -0.068664 | -0.082397 | -0.018311 | -0.07782 | 0.004577 | 0.14648 | 0.027465 | -0.14191 | 0.045776 | -0.1236 | 0.65918 | 122.4014 | 0.16479 | 122.3099 | 122.3648 | 122.2275 | 122.2412 | 122.2092 | -122.4106 | -122.3053 | 122.2778 | 122.2916 | 41.5054 | 44.3115
1168.3125 | 122.4884 | -57.7927 | 64.5172 | -0.012436 | 0.0019802 | 0.062521 | 0.058954 | 0.00034182 | -0.003388 | -0.00072206 | 0.0061035 | 0.0018457 | 0.065875 | 0.059003 | -0.0071864 | 0.0094379 | 0.000109 | -16.4703 | 64.4852 | -57.9071 | 64.4302 | -57.3257 | -58.0353 | -58.0124 | -13.6597 | 64.4531 | -57.8156 | 64.4623 | -57.6508 | -57.9391 | -57.7927 | -0.11444 | -0.032044 | -0.086975 | 0.46692 | -0.21973 | -0.24261 | -0.10529 | -0.12817 | -0.022888 | -0.064087 | -0.054932 | 0.14191 | 0 | -0.14648 | 0.022888 | -0.1236 | 0.58136 | 122.3373 | 0.16479 | 122.2778 | 122.3923 | 122.2687 | 122.2778 | 122.2458 | -122.4243 | -122.3328 | 122.2229 | 122.2549 | 41.3223 | 44.133
1169.3125 | 122.525 | -57.7927 | 64.5401 | -0.012436 | 0.0026212 | 0.062735 | 0.059381 | -0.0045716 | -0.0038154 | -0.0015765 | -0.015259 | 0.0031273 | 0.06737 | 0.062848 | -0.0054774 | 0.0098651 | -0.0011728 | -16.5253 | 64.4714 | -57.9117 | 64.4623 | -57.2571 | -58.0078 | -57.9666 | -13.7146 | 64.4348 | -57.7835 | 64.4989 | -57.6233 | -57.9254 | -57.7423 | -0.11902 | -0.068664 | -0.07782 | 0.53558 | -0.17395 | -0.21515 | -0.054932 | -0.09613 | 0.009156 | -0.10529 | -0.041199 | 0.16937 | 0.050354 | -0.13275 | 0.041198 | -0.14191 | 0.6546 | 122.374 | 0.16022 | 122.2824 | 122.3831 | 122.2183 | 122.2641 | 122.2275 | -122.4518 | -122.3236 | 122.2549 | 122.2916 | 41.2674 | 44.0781
1170.3281 | 122.4426 | -57.7972 | 64.5081 | 0.0028229 | 0.0039028 | 0.063589 | 0.06109 | 0.00076902 | -0.0036018 | -0.00029486 | -0.061035 | 0.0029137 | 0.066729 | 0.06178 | -0.0074 | 0.010292 | -0.0048044 | -16.6489 | 64.4394 | -57.93 | 64.4394 | -57.2662 | -58.0353 | -58.017 | -13.8794 | 64.4119 | -57.8201 | 64.4714 | -57.6828 | -57.962 | -57.7927 | -0.13275 | -0.068665 | -0.068665 | 0.53101 | -0.21973 | -0.23804 | -0.086975 | -0.10528 | -0.022888 | -0.096131 | -0.036621 | 0.11444 | 0.004577 | -0.16479 | 0.027465 | -0.14191 | 0.66376 | 122.3694 | 0.13733 | 122.2916 | 122.3694 | 122.2321 | 122.2366 | 122.2092 | -122.4381 | -122.3282 | 122.2366 | 122.2687 | 41.1484 | 43.9178
1171.3125 | 122.5296 | -57.8064 | 64.5126 | -0.073471 | 0.002194 | 0.063803 | 0.059381 | 0.0022644 | -0.0025336 | -0.0020039 | -0.0061035 | 0.0027001 | 0.066302 | 0.056866 | -0.0086816 | 0.01072 | -0.0028818 | -16.745 | 64.5264 | -57.8888 | 64.4394 | -57.2662 | -57.9941 | -57.9895 | -13.9618 | 64.4623 | -57.7789 | 64.4943 | -57.6141 | -57.8979 | -57.7377 | -0.082398 | 0.013733 | -0.073242 | 0.54016 | -0.18311 | -0.18768 | -0.10071 | -0.10529 | 0.027465 | -0.050354 | -0.01831 | 0.19226 | 0.068664 | -0.091553 | 0.041199 | -0.11902 | 0.62256 | 122.3282 | 0.16479 | 122.2733 | 122.4152 | 122.2412 | 122.3328 | 122.2687 | -122.4014 | -122.2916 | 122.2458 | 122.3007 | 41.0614 | 43.8446
1172.3125 | 122.5021 | -57.7972 | 64.5035 | -0.050583 | 0.0028348 | 0.062735 | 0.05874 | -0.00093998 | -0.0014654 | -0.0024311 | -0.045776 | 0.0016321 | 0.066302 | 0.063061 | -0.006759 | 0.010506 | -0.0011728 | -16.9418 | 64.4073 | -57.9254 | 64.3799 | -57.3212 | -58.0902 | -58.0399 | -14.1632 | 64.3936 | -57.8476 | 64.4531 | -57.6874 | -57.9803 | -57.7881 | -0.12817 | -0.09613 | -0.1236 | 0.47607 | -0.24262 | -0.29297 | -0.11444 | -0.16479 | -0.050354 | -0.10986 | -0.050354 | 0.10986 | 0.009155 | -0.18311 | 0.059509 | -0.13275 | 0.60425 | 122.3053 | 0.16022 | 122.3007 | 122.3328 | 122.2412 | 122.2046 | 122.1909 | -122.4289 | -122.3511 | 122.1771 | 122.2504 | 40.8554 | 43.634
1173.3125 | 122.5021 | -57.7744 | 64.5584 | -0.035324 | 0.0047574 | 0.062521 | 0.060663 | -0.00072638 | -0.0046698 | 0.00034614 | -0.0091553 | 0.0020593 | 0.066943 | 0.058362 | -0.0069726 | 0.010079 | -0.0043772 | -17.038 | 64.5126 | -57.8888 | 64.444 | -57.2662 | -57.9987 | -57.9712 | -14.2044 | 64.4623 | -57.7789 | 64.5126 | -57.6141 | -57.8934 | -57.7423 | -0.11444 | -0.045777 | -0.11444 | 0.50812 | -0.19684 | -0.2243 | -0.082397 | -0.10986 | -0.004578 | -0.096131 | -0.045777 | 0.16022 | 0.032043 | -0.11902 | 0.036621 | -0.11444 | 0.62256 | 122.3328 | 0.16479 | 122.2916 | 122.4014 | 122.2412 | 122.287 | 122.2366 | -122.4472 | -122.3373 | 122.2183 | 122.287 | 40.7364 | 43.5699
1174.3125 | 122.4609 | -57.7881 | 64.5447 | -0.020065 | 0.0045438 | 0.062094 | 0.058954 | -0.0011536 | -0.003388 | -0.0015765 | -0.076294 | 0.0041955 | 0.067584 | 0.06178 | -0.0054774 | 0.011361 | -0.0060862 | -17.1707 | 64.5126 | -57.8705 | 64.4257 | -57.1838 | -57.7057 | -58.0353 | -14.2502 | 64.4485 | -57.8018 | 64.4623 | -57.6096 | -57.9208 | -57.7652 | -0.082397 | -0.032044 | -0.11902 | 0.60425 | -0.24719 | 0.082398 | -0.16479 | 0.16479 | -0.013733 | -0.096131 | -0.082398 | 0.17853 | 0.022888 | -0.13275 | 0.036621 | -0.11902 | 0.68664 | 122.2961 | 0.19226 | 122.2641 | 122.3831 | 122.2504 | 122.3007 | 122.2366 | -122.4152 | -122.3465 | 122.2137 | 122.2504 | 40.6174 | 43.5379
1175.3281 | 122.4655 | -57.756 | 64.563 | -0.050583 | 0.001553 | 0.065085 | 0.061517 | -0.0011536 | -0.0055244 | -0.0037129 | 0.0091553 | 0.0035547 | 0.065661 | 0.053021 | -0.005691 | 0.0079425 | -0.0016 | -17.2852 | 64.5401 | -57.8567 | 64.4852 | -57.2617 | -58.0124 | -57.9529 | -14.4287 | 64.4714 | -57.7835 | 64.4806 | -57.6416 | -57.9254 | -57.7606 | -0.10071 | -0.022888 | -0.07782 | 0.49438 | -0.19684 | -0.25635 | -0.096131 | -0.15564 | -0.027466 | -0.091552 | -0.082397 | 0.11444 | -0.004578 | -0.16937 | 0.022888 | -0.14191 | 0.59509 | 122.3419 | 0.14191 | 122.2641 | 122.3969 | 122.2549 | 122.2961 | 122.2275 | -122.4197 | -122.3465 | 122.2412 | 122.2366 | 40.4709 | 43.3273
1176.3125 | 122.5067 | -57.7606 | 64.5721 | -0.042954 | 0.004971 | 0.064444 | 0.059167 | 0.0018372 | -0.00061096 | -0.0015765 | -0.024414 | 0.0022729 | 0.066516 | 0.057507 | -0.0082544 | 0.010933 | -0.0001046 | -17.363 | 64.5081 | -57.8613 | 64.4714 | -57.2113 | -57.9529 | -57.93 | -14.4608 | 64.4806 | -57.7652 | 64.5401 | -57.5821 | -57.8796 | -57.7011 | -0.10071 | -0.064087 | -0.10071 | 0.54932 | -0.16937 | -0.19226 | -0.068665 | -0.091553 | -0.004578 | -0.091553 | -0.032044 | 0.17853 | 0.059509 | -0.11902 | 0.064087 | -0.11444 | 0.65002 | 122.3328 | 0.18311 | 122.3053 | 122.3694 | 122.2458 | 122.2687 | 122.2412 | -122.4335 | -122.3373 | 122.2321 | 122.3007 | 40.3976 | 43.2999
1177.3125 | 122.5159 | -57.7744 | 64.5264 | -0.081101 | 0.0024076 | 0.064871 | 0.060449 | -0.00072638 | -0.0018928 | -0.0034991 | -0.039673 | 0.0029137 | 0.066943 | 0.052594 | -0.005691 | 0.01072 | 0.0013906 | -17.5735 | 64.4669 | -57.8888 | 64.4257 | -57.2662 | -58.0536 | -58.0124 | -14.6667 | 64.4348 | -57.8064 | 64.5172 | -57.637 | -57.9346 | -57.7469 | -0.11444 | -0.059509 | -0.10071 | 0.50812 | -0.23804 | -0.27924 | -0.1236 | -0.1648 | -0.032043 | -0.091553 | -0.009155 | 0.13733 | 0.027466 | -0.16022 | 0.059509 | -0.12817 | 0.62256 | 122.3145 | 0.16937 | 122.3236 | 122.3557 | 122.2412 | 122.2412 | 122.2092 | -122.4152 | -122.3328 | 122.2 | 122.2916 | 40.2008 | 43.1076
1178.3125 | 122.5113 | -57.7469 | 64.563 | -0.042954 | 0.0039028 | 0.064657 | 0.059595 | 0.00034182 | -0.0038154 | 0.00077334 | -0.0091553 | 0.0037683 | 0.066943 | 0.061566 | -0.0078272 | 0.0098651 | -0.0037362 | -17.6514 | 64.5447 | -57.8522 | 64.476 | -57.2113 | -57.9666 | -57.9483 | -14.7034 | 64.4852 | -57.7744 | 64.5447 | -57.5592 | -57.8751 | -57.7194 | -0.10529 | -0.01831 | -0.086975 | 0.53558 | -0.20142 | -0.21973 | -0.09613 | -0.11444 | -0.027466 | -0.07782 | -0.01831 | 0.18768 | 0.027466 | -0.12817 | 0.054932 | -0.10071 | 0.64087 | 122.3282 | 0.21515 | 122.319 | 122.3969 | 122.2595 | 122.2916 | 122.2321 | -122.4152 | -122.3373 | 122.2229 | 122.2916 | 40.0955 | 43.0435
1179.3125 | 122.5113 | -57.7515 | 64.5676 | -0.042954 | 0.0030484 | 0.066366 | 0.059808 | -0.0015808 | -0.0010382 | 0.0018413 | 0.0091553 | 0.0037683 | 0.066729 | 0.063702 | -0.0088952 | 0.011361 | -0.0041636 | -17.7795 | 64.5264 | -57.8339 | 64.476 | -57.2113 | -57.9575 | -57.9437 | -14.7903 | 64.4897 | -57.7423 | 64.5447 | -57.5546 | -57.8705 | -57.7057 | -0.082397 | -0.041199 | -0.091553 | 0.54016 | -0.19226 | -0.20599 | -0.10986 | -0.1236 | 0.009155 | -0.07782 | -0.022888 | 0.19684 | 0.045777 | -0.11902 | 0.036622 | -0.12817 | 0.62256 | 122.3099 | 0.18768 | 122.287 | 122.3602 | 122.2321 | 122.2778 | 122.2412 | -122.4014 | -122.3099 | 122.2275 | 122.2961 | 39.9719 | 42.9611
1180.3125 | 122.5891 | -57.724 | 64.5264 | -0.08873 | 0.0019802 | 0.063589 | 0.060663 | 0.0050414 | -0.0021064 | -0.0024311 | 0.015259 | -0.00029045 | 0.066729 | 0.060284 | -0.0080408 | 0.0081561 | -0.005018 | -17.8711 | 64.4302 | -57.8705 | 64.5447 | -57.1472 | -57.9391 | -57.8705 | -14.8499 | 64.4119 | -57.756 | 64.6271 | -57.5867 | -57.811 | -57.6279 | -0.14648 | -0.09613 | 0.018311 | 0.57678 | -0.14648 | -0.21515 | 0 | -0.068665 | -0.032043 | -0.11444 | 0.10071 | 0.13733 | 0.09613 | -0.086975 | 0.12817 | -0.054932 | 0.72327 | 122.4152 | 0.16937 | 122.3831 | 122.3007 | 122.168 | 122.1542 | 122.1359 | -122.3969 | -122.2824 | 122.2687 | 122.3511 | 39.8529 | 42.8741
1181.3125 | 122.4792 | -57.7286 | 64.5996 | -0.035324 | 0.0045438 | 0.065512 | 0.057672 | -0.0011536 | -0.0025336 | -0.0020039 | 0.054932 | 0.0016321 | 0.066089 | 0.055371 | -0.006759 | 0.01072 | -0.000532 | -17.9901 | 64.5081 | -57.7972 | 64.5493 | -57.1014 | -57.8751 | -57.8522 | -14.9139 | 64.4531 | -57.7148 | 64.5584 | -57.5546 | -57.8293 | -57.7011 | -0.068664 | -0.091552 | -0.050354 | 0.62714 | -0.1236 | -0.14648 | -0.054932 | -0.07782 | 0.013733 | -0.14648 | -0.041198 | 0.17395 | 0.027466 | -0.10071 | 0.013733 | -0.11444 | 0.6958 | 122.3465 | 0.16022 | 122.2733 | 122.3053 | 122.168 | 122.2366 | 122.1817 | -122.3969 | -122.3145 | 122.2778 | 122.287 | 39.7385 | 42.8146
1182.3125 | 122.5891 | -57.7286 | 64.5401 | -0.26421 | 0.0034756 | 0.062735 | 0.061944 | -0.0011536 | -0.0038154 | 0.00055974 | -8.6e-08 | 0.00077755 | 0.06737 | 0.061566 | -0.006759 | 0.0096515 | -0.0009592 | -18.0176 | 64.4348 | -57.8339 | 64.563 | -57.0786 | -57.8842 | -57.8613 | -14.9963 | 64.4485 | -57.756 | 64.6042 | -57.5043 | -57.8064 | -57.6324 | -0.10529 | -0.10529 | 0.022888 | 0.65002 | -0.13275 | -0.15564 | -0.027466 | -0.050354 | -0.027465 | -0.091553 | 0.064087 | 0.22431 | 0.096131 | -0.077819 | 0.1236 | -0.050354 | 0.75531 | 122.3969 | 0.25177 | 122.3602 | 122.2687 | 122.2046 | 122.1634 | 122.1771 | -122.374 | -122.2961 | 122.2916 | 122.3328 | 39.711 | 42.7322
1183.3125 | 122.4609 | -57.724 | 64.6133 | 0.0028229 | 0.0039028 | 0.061667 | 0.060235 | -8.538e-05 | -0.00039736 | -0.0034991 | -0.024414 | 0.0033411 | 0.065661 | 0.062421 | -0.0076136 | 0.0090105 | -0.0013864 | -18.3517 | 64.5721 | -57.8384 | 64.5035 | -57.1793 | -57.9666 | -57.9163 | -15.2115 | 64.5264 | -57.7423 | 64.5355 | -57.5684 | -57.8796 | -57.7148 | -0.11444 | -0.041198 | -0.10986 | 0.54474 | -0.19226 | -0.24262 | -0.07782 | -0.12817 | -0.018311 | -0.086975 | -0.07782 | 0.15564 | 0.009155 | -0.15564 | 0.027466 | -0.13733 | 0.65918 | 122.3419 | 0.17395 | 122.2778 | 122.4106 | 122.2687 | 122.2961 | 122.2504 | -122.4518 | -122.3557 | 122.2275 | 122.2595 | 39.3723 | 42.5125
1184.3125 | 122.4701 | -57.7286 | 64.5813 | -0.027695 | 0.0047574 | 0.065725 | 0.062158 | 0.0026916 | -0.003388 | -0.00072206 | -0.076294 | 0.0035547 | 0.065875 | 0.060498 | -0.0048364 | 0.012215 | -0.0003182 | -18.5303 | 64.5355 | -57.8705 | 64.4302 | -57.2617 | -58.0444 | -57.9987 | -15.3854 | 64.4989 | -57.7789 | 64.4897 | -57.2983 | -57.8567 | -57.7835 | -0.14191 | -0.045777 | -0.15106 | 0.46692 | -0.27008 | -0.31586 | -0.12817 | -0.17395 | -0.050354 | -0.082398 | -0.091553 | 0.4303 | -0.054931 | -0.12817 | -0.004577 | -0.077819 | 0.60883 | 122.3007 | 0.48065 | 122.2687 | 122.406 | 122.2778 | 122.2641 | 122.2275 | -122.4518 | -122.3602 | 122.1588 | 122.2183 | 39.1983 | 42.3431
1185.3125 | 122.5525 | -57.6965 | 64.5126 | -0.042954 | 0.0028348 | 0.06658 | 0.060235 | 0.0035462 | -0.0012518 | 0.0020551 | -0.0061035 | 0.0018457 | 0.065661 | 0.063061 | -0.0048364 | 0.01072 | -0.0028818 | -18.6218 | 64.4852 | -57.8567 | 64.5584 | -57.1014 | -57.9117 | -57.8567 | -15.303 | 64.4302 | -57.7469 | 64.5264 | -57.2937 | -57.6416 | -57.5729 | -0.16022 | -0.027466 | 0.045777 | 0.59509 | -0.16022 | -0.21515 | 0 | -0.054932 | -0.050354 | -0.082397 | 0.013733 | 0.40283 | 0.1236 | 0.054931 | 0.17395 | 0.10529 | 0.75531 | 122.4152 | 0.45319 | 122.2733 | 122.3419 | 122.1771 | 122.1817 | 122.1268 | -122.3694 | -122.2595 | 122.2549 | 122.2229 | 39.0747 | 42.3935
1186.3125 | 122.4609 | -57.7194 | 64.6133 | 0.0028229 | 0.0030484 | 0.066153 | 0.060876 | -0.003717 | -0.003388 | 0.00013254 | -0.030517 | 0.0020593 | 0.066943 | 0.060498 | -0.0065454 | 0.010079 | 0.0003226 | -18.8004 | 64.5859 | -57.8247 | 64.5126 | -57.1609 | -57.93 | -57.8979 | -15.4495 | 64.5172 | -57.7469 | 64.5538 | -57.5546 | -57.8522 | -57.7011 | -0.10529 | -0.027466 | -0.10071 | 0.55847 | -0.17853 | -0.21057 | -0.073242 | -0.10529 | -0.027466 | -0.09613 | -0.059509 | 0.16479 | 0.01831 | -0.13275 | 0.045776 | -0.10529 | 0.66376 | 122.3373 | 0.19226 | 122.3007 | 122.4106 | 122.2641 | 122.3053 | 122.2366 | -122.438 | -122.3602 | 122.2321 | 122.2733 | 38.9191 | 42.2699
1187.3125 | 122.4472 | -57.7332 | 64.6133 | -0.058212 | 0.0034756 | 0.065298 | 0.061517 | 0.00076902 | -0.0031744 | -8.1264e-05 | -0.061035 | 0.0018457 | 0.06502 | 0.058789 | -0.0088952 | 0.010079 | -0.0035226 | -18.9377 | 64.5355 | -57.8522 | 64.5081 | -57.1701 | -57.9666 | -57.93 | -15.5823 | 64.5264 | -57.7423 | 64.5538 | -57.5729 | -57.9117 | -57.7103 | -0.11902 | -0.07782 | -0.10529 | 0.56305 | -0.19684 | -0.23346 | -0.07782 | -0.11444 | -0.009156 | -0.086975 | -0.059509 | 0.16022 | 0.022888 | -0.17853 | 0.032044 | -0.16937 | 0.68207 | 122.3602 | 0.16937 | 122.2961 | 122.3877 | 122.2687 | 122.2687 | 122.2595 | -122.4655 | -122.3557 | 122.2412 | 122.287 | 38.7955 | 42.1509
1188.3125 | 122.4609 | -57.692 | 64.6271 | -0.035324 | 0.0034756 | 0.061026 | 0.059381 | -0.003717 | -0.0016792 | 0.00098694 | -0.030517 | 0.0020593 | 0.065448 | 0.058148 | -0.0052638 | 0.011147 | -0.0030954 | -19.0979 | 64.5721 | -57.8156 | 64.5309 | -57.1335 | -57.9163 | -57.8796 | -15.6189 | 64.5264 | -57.6965 | 64.5859 | -57.4814 | -57.8156 | -57.6508 | -0.1236 | -0.054931 | -0.09613 | 0.55847 | -0.18768 | -0.2243 | -0.064087 | -0.10071 | -0.004577 | -0.10071 | -0.041199 | 0.21057 | 0.041199 | -0.1236 | 0.045776 | -0.11902 | 0.68207 | 122.3465 | 0.21515 | 122.2824 | 122.3877 | 122.2229 | 122.2641 | 122.2183 | -122.4426 | -122.3236 | 122.2229 | 122.2778 | 38.5941 | 42.0731
1189.3125 | 122.525 | -57.6874 | 64.5538 | -0.073471 | 0.0047574 | 0.065298 | 0.058313 | -0.00072638 | -0.0018928 | -0.0015765 | 0.027466 | 0.0016321 | 0.067157 | 0.056439 | -0.005691 | 0.0085833 | -0.0003182 | -19.249 | 64.5172 | -57.7927 | 64.5538 | -57.0877 | -57.8888 | -57.8384 | -15.7562 | 64.476 | -57.7148 | 64.5905 | -57.3074 | -57.7881 | -57.7469 | -0.10529 | -0.036621 | 0 | 0.59967 | -0.15106 | -0.20142 | -0.045776 | -0.09613 | -0.027466 | -0.07782 | 0.036621 | 0.37994 | -0.059509 | -0.10071 | -0.032043 | -0.073242 | 0.70496 | 122.3465 | 0.40741 | 122.3053 | 122.3099 | 122.1909 | 122.2046 | 122.1634 | -122.3465 | -122.2687 | 122.2412 | 122.2778 | 38.4384 | 41.9312
1190.3125 | 122.5983 | -57.6874 | 64.5355 | -0.042954 | 0.0039028 | 0.063162 | 0.061517 | 0.00098262 | -0.00232 | -0.0037129 | -0.0061035 | 0.0027001 | 0.066302 | 0.060498 | -0.0061182 | 0.0092241 | 0.002886 | -19.3726 | 64.5264 | -57.7927 | 64.5767 | -57.074 | -57.9025 | -57.843 | -15.8066 | 64.4531 | -57.692 | 64.65 | -57.4539 | -57.7698 | -57.5867 | -0.10529 | -0.009155 | 0.041199 | 0.6134 | -0.15564 | -0.21515 | -0.050354 | -0.10986 | -0.004578 | -0.082397 | 0.11444 | 0.23346 | 0.10071 | -0.082397 | 0.10529 | -0.077819 | 0.71869 | 122.3694 | 0.23804 | 122.3419 | 122.319 | 122.1451 | 122.2137 | 122.1405 | -122.3282 | -122.2275 | 122.2641 | 122.3373 | 38.3148 | 41.8808
1191.3125 | 122.4609 | -57.6965 | 64.6271 | -0.0048066 | 0.0017666 | 0.062521 | 0.059808 | -0.00029898 | -0.0029608 | -0.00072206 | -0.015259 | 0.0029137 | 0.065875 | 0.060925 | -0.0088952 | 0.01072 | -0.0052316 | -19.5099 | 64.5767 | -57.7606 | 64.5355 | -57.0877 | -57.8796 | -57.8522 | -15.9622 | 64.5676 | -57.692 | 64.6362 | -57.2937 | -57.9895 | -57.843 | -0.064087 | -0.050354 | -0.091553 | 0.60883 | -0.15564 | -0.18311 | -0.091553 | -0.11902 | 0.004577 | -0.059509 | 0.009155 | 0.40283 | -0.14648 | -0.29297 | -0.15106 | -0.29755 | 0.67291 | 122.2961 | 0.39825 | 122.3282 | 122.3373 | 122.2595 | 122.2733 | 122.2641 | -122.3877 | -122.319 | 122.2321 | 122.3328 | 38.1866 | 41.7343
1192.3125 | 122.4609 | -57.6782 | 64.6683 | 0.0028229 | 0.0017666 | 0.066153 | 0.059167 | 0.00012822 | -0.0046698 | -0.00050846 | -0.033569 | 0.0020593 | 0.066302 | 0.066052 | -0.0063318 | 0.0090105 | -0.0020272 | -19.7159 | 64.6042 | -57.7744 | 64.5309 | -57.1198 | -57.8888 | -57.8613 | -16.0767 | 64.5676 | -57.7057 | 64.5905 | -57.518 | -57.8156 | -57.6691 | -0.09613 | -0.064087 | -0.13733 | 0.55847 | -0.1831 | -0.21057 | -0.086975 | -0.11444 | -0.027465 | -0.10071 | -0.07782 | 0.16022 | 0.009156 | -0.13733 | 0.036621 | -0.10986 | 0.6546 | 122.3053 | 0.18768 | 122.2961 | 122.3785 | 122.2733 | 122.2824 | 122.2458 | -122.4426 | -122.374 | 122.2092 | 122.2687 | 37.9623 | 41.6016
1193.3125 | 122.5754 | -57.6736 | 64.5859 | -0.10399 | 0.0045438 | 0.06658 | 0.060235 | 0.00012822 | -0.0031744 | -0.00072206 | 0.039673 | 0.0012047 | 0.06502 | 0.063061 | -0.0052638 | 0.010506 | -0.0037362 | -19.7891 | 64.5081 | -57.7972 | 64.6317 | -57.0053 | -58.0353 | -57.9895 | -16.008 | 64.4852 | -57.6508 | 64.6912 | -57.4219 | -57.7286 | -57.5775 | -0.1236 | -0.077819 | 0.045777 | 0.66833 | -0.31586 | -0.36163 | -0.19226 | -0.23804 | 0.022888 | -0.10071 | 0.10529 | 0.25177 | 0.09613 | -0.054932 | 0.073242 | -0.07782 | 0.79193 | 122.4289 | 0.22888 | 122.3419 | 122.3053 | 122.1359 | 122.1817 | 122.1588 | -122.3831 | -122.2366 | 122.3053 | 122.3648 | 37.8845 | 41.6656
1194.3125 | 122.493 | -57.7148 | 64.6271 | -0.11162 | 0.0045438 | 0.063589 | 0.062585 | -0.0015808 | -0.003388 | -0.0015765 | -0.073242 | 0.0022729 | 0.065661 | 0.063702 | -0.0071864 | 0.010933 | -0.0018136 | -20.0317 | 64.5859 | -57.8247 | 64.5218 | -57.1106 | -57.9666 | -57.8979 | -16.3055 | 64.5309 | -57.7011 | 64.5859 | -57.5455 | -57.8613 | -57.6599 | -0.10986 | -0.041199 | -0.10529 | 0.60425 | -0.1831 | -0.25177 | -0.073242 | -0.14191 | 0.013733 | -0.09613 | -0.041199 | 0.16937 | 0.054932 | -0.14648 | 0.041199 | -0.16022 | 0.71411 | 122.3465 | 0.15564 | 122.287 | 122.4106 | 122.2321 | 122.3007 | 122.2458 | -122.4518 | -122.3282 | 122.2366 | 122.3007 | 37.6831 | 41.4093
1195.3125 | 122.58 | -57.6462 | 64.65 | -0.073471 | 0.002194 | 0.067007 | 0.055963 | -0.0011536 | -0.00232 | -0.0017903 | 0.033569 | 0.0024865 | 0.066516 | 0.062634 | -0.0048364 | 0.0083697 | -0.0048044 | -20.0592 | 64.5996 | -57.7103 | 64.6774 | -56.9183 | -57.7423 | -57.724 | -16.2186 | 64.5355 | -57.6279 | 64.7186 | -57.3578 | -57.6691 | -57.5455 | -0.064087 | -0.050354 | 0.027466 | 0.72784 | -0.07782 | -0.096131 | -0.013733 | -0.032044 | 0.01831 | -0.11444 | 0.068665 | 0.28839 | 0.10071 | -0.022888 | 0.082398 | -0.041198 | 0.79193 | 122.3877 | 0.27008 | 122.3465 | 122.3099 | 122.1634 | 122.2458 | 122.1817 | -122.3602 | -122.2778 | 122.3236 | 122.3648 | 37.587 | 41.4276
1196.3125 | 122.4609 | -57.6645 | 64.6545 | 0.03334 | 0.0017666 | 0.064444 | 0.061303 | -0.00093998 | 2.9842e-05 | -0.00029486 | -0.076294 | 0.00099115 | 0.066089 | 0.065839 | -0.0080408 | 0.010292 | 0.0037406 | -20.2148 | 64.6179 | -57.7698 | 64.5355 | -57.1014 | -57.9575 | -57.8934 | -16.539 | 64.5584 | -57.7194 | 64.5859 | -57.518 | -57.8522 | -57.6691 | -0.10529 | -0.036621 | -0.11902 | 0.56305 | -0.22888 | -0.29297 | -0.1236 | -0.18768 | -0.054931 | -0.09613 | -0.068665 | 0.14648 | -0.004577 | -0.18768 | 0.050354 | -0.13275 | 0.66834 | 122.3053 | 0.20142 | 122.3053 | 122.3877 | 122.2778 | 122.2824 | 122.2229 | -122.4243 | -122.374 | 122.2 | 122.2504 | 37.4496 | 41.1255
1197.3125 | 122.4518 | -57.6462 | 64.682 | -0.035324 | 0.0039028 | 0.065939 | 0.058954 | -0.0047852 | -0.0012518 | -0.0013629 | -0.033569 | 0.0039819 | 0.068652 | 0.062207 | -0.0061182 | 0.010079 | -0.0013864 | -20.4666 | 64.6729 | -57.7652 | 64.5721 | -57.0602 | -57.8293 | -57.8247 | -16.5298 | 64.6179 | -57.6508 | 64.6271 | -57.4539 | -57.7698 | -57.6096 | -0.11902 | -0.009155 | -0.10986 | 0.58594 | -0.17853 | -0.18311 | -0.059509 | -0.064087 | -0.004578 | -0.064087 | -0.054932 | 0.19226 | 0.036621 | -0.1236 | 0.041199 | -0.11902 | 0.70496 | 122.3373 | 0.19684 | 122.2778 | 122.4381 | 122.2687 | 122.319 | 122.2641 | -122.4472 | -122.3328 | 122.2183 | 122.2733 | 37.1796 | 41.1163
1198.3125 | 122.5067 | -57.6141 | 64.6683 | -0.073471 | 0.0041166 | 0.06423 | 0.061303 | 0.0020508 | -0.004029 | -0.00029486 | -0.15869 | 0.0027001 | 0.065234 | 0.063061 | -0.0093226 | 0.012429 | -0.0020272 | -20.6451 | 64.6271 | -57.7515 | 64.6362 | -56.9733 | -57.8201 | -57.7835 | -16.507 | 64.5996 | -57.6508 | 64.6774 | -57.3807 | -57.7286 | -57.5775 | -0.13733 | -0.041199 | -0.032044 | 0.64087 | -0.16937 | -0.20599 | -0.032043 | -0.068664 | -0.036621 | -0.068665 | 0.009155 | 0.23346 | 0.036621 | -0.11444 | 0.073242 | -0.07782 | 0.7782 | 122.3877 | 0.27008 | 122.3282 | 122.3785 | 122.2504 | 122.2412 | 122.2137 | -122.4197 | -122.319 | 122.2504 | 122.2916 | 36.969 | 41.1072
1199.3125 | 122.5983 | -57.6187 | 64.6362 | -0.096359 | 0.0019802 | 0.065512 | 0.059808 | 0.0052552 | -0.004029 | -0.00029486 | -0.033569 | 0.0014185 | 0.066302 | 0.066479 | -0.0071864 | 0.01072 | -0.0009592 | -20.8511 | 64.5859 | -57.7606 | 64.6179 | -56.9733 | -57.8339 | -57.7789 | -16.7358 | 64.5355 | -57.6645 | 64.7095 | -57.3715 | -57.6965 | -57.5089 | -0.14191 | -0.050354 | -0.01831 | 0.64545 | -0.16022 | -0.21515 | -0.018311 | -0.073242 | -0.045777 | -0.10071 | 0.073243 | 0.24719 | 0.10986 | -0.07782 | 0.15564 | -0.032043 | 0.78735 | 122.3785 | 0.29297 | 122.374 | 122.3465 | 122.2 | 122.2046 | 122.1542 | -122.3969 | -122.3007 | 122.2366 | 122.3282 | 36.7676 | 40.8829
1200.3125 | 122.4838 | -57.6096 | 64.7049 | 0.048599 | 0.0028348 | 0.064871 | 0.060876 | -0.00029898 | -0.0053108 | 0.0016277 | -0.0030517 | 0.0031273 | 0.065448 | 0.063916 | -0.006759 | 0.010292 | -0.0041636 | -21.0617 | 64.6683 | -57.7286 | 64.5996 | -57.0099 | -57.8293 | -57.7835 | -16.9052 | 64.6545 | -57.6462 | 64.6317 | -57.431 | -57.7377 | -57.6004 | -0.11902 | -0.036621 | -0.10529 | 0.59967 | -0.17395 | -0.21973 | -0.054931 | -0.10071 | -0.036621 | -0.050354 | -0.073242 | 0.17853 | 0.009155 | -0.12817 | 0.045776 | -0.091553 | 0.71869 | 122.3282 | 0.21515 | 122.2778 | 122.3969 | 122.3007 | 122.2778 | 122.2641 | -122.4335 | -122.3511 | 122.2092 | 122.2412 | 36.5479 | 40.7043
1201.3125 | 122.5113 | -57.6096 | 64.7141 | -0.035324 | 0.0009122 | 0.064871 | 0.060876 | 0.0011962 | -0.0053108 | -0.0017903 | -0.01831 | 0.0020593 | 0.069079 | 0.062207 | -0.0063318 | 0.0096515 | -0.0011728 | -21.199 | 64.65 | -57.7423 | 64.6088 | -56.987 | -57.7972 | -57.7698 | -16.9647 | 64.6271 | -57.6233 | 64.6683 | -57.3898 | -57.7194 | -57.5455 | -0.13275 | -0.064087 | -0.10528 | 0.62256 | -0.16022 | -0.18768 | -0.027465 | -0.054931 | -0.013733 | -0.086975 | -0.045776 | 0.21973 | 0.064087 | -0.10986 | 0.07782 | -0.09613 | 0.75531 | 122.3511 | 0.23346 | 122.2916 | 122.3923 | 122.2504 | 122.2595 | 122.2366 | -122.4564 | -122.3373 | 122.2183 | 122.2778 | 36.4105 | 40.6448
1202.3125 | 122.4426 | -57.6324 | 64.682 | -0.08873 | 0.0030484 | 0.066153 | 0.061517 | 0.0048278 | -0.0029608 | -0.00029486 | -0.061035 | 0.00099115 | 0.068011 | 0.062848 | -0.0076136 | 0.0092241 | -0.0041636 | -21.373 | 64.6317 | -57.724 | 64.6179 | -56.987 | -57.8476 | -57.8201 | -17.0334 | 64.6042 | -57.6141 | 64.6271 | -57.4631 | -57.7972 | -57.6096 | -0.091553 | -0.050354 | -0.064087 | 0.64545 | -0.18768 | -0.21515 | -0.09613 | -0.1236 | 0.01831 | -0.07782 | -0.054932 | 0.16937 | 0.022888 | -0.16479 | 0.004578 | -0.1831 | 0.737 | 122.3419 | 0.15106 | 122.2412 | 122.3557 | 122.2183 | 122.2641 | 122.2366 | -122.406 | -122.2961 | 122.2504 | 122.2595 | 36.2595 | 40.5991
1203.3125 | 122.4701 | -57.605 | 64.7598 | -0.050583 | 0.0028348 | 0.065085 | 0.060235 | -0.00029898 | -0.005097 | -0.0028583 | 0.027466 | 0.00099115 | 0.066302 | 0.058789 | -0.0061182 | 0.0098651 | -0.0026682 | -21.5424 | 64.6591 | -57.6782 | 64.6454 | -56.9275 | -57.7469 | -57.7286 | -17.0975 | 64.6454 | -57.6004 | 64.6637 | -57.3807 | -57.724 | -57.5912 | -0.073243 | -0.10071 | -0.11444 | 0.67749 | -0.1236 | -0.14191 | -0.050354 | -0.068664 | 0.004577 | -0.11444 | -0.096131 | 0.2243 | 0.013732 | -0.11902 | 0.009155 | -0.1236 | 0.75073 | 122.3236 | 0.21973 | 122.2641 | 122.3373 | 122.2458 | 122.2641 | 122.2504 | -122.4381 | -122.3602 | 122.2504 | 122.2687 | 36.0626 | 40.5075
1204.3125 | 122.5296 | -57.5684 | 64.7461 | 0.0028229 | 0.002194 | 0.06423 | 0.059167 | 0.0033324 | -0.00232 | -0.0011493 | -0.027466 | 0.0024865 | 0.066302 | 0.062848 | -0.006759 | 0.01072 | -0.0048044 | -21.7346 | 64.6957 | -57.7194 | 64.6545 | -56.9504 | -57.756 | -57.7698 | -17.1753 | 64.6317 | -57.5775 | 64.7186 | -57.3532 | -57.6965 | -57.5409 | -0.15106 | -0.050354 | -0.091553 | 0.61798 | -0.20142 | -0.18768 | -0.050354 | -0.036621 | -0.009156 | -0.11444 | -0.027466 | 0.21515 | 0.027465 | -0.12817 | 0.036621 | -0.11902 | 0.76904 | 122.374 | 0.22431 | 122.2961 | 122.4152 | 122.2092 | 122.2641 | 122.2 | -122.4655 | -122.3236 | 122.2229 | 122.287 | 35.8337 | 40.3931
1205.3125 | 122.4976 | -57.5867 | 64.7049 | -0.027695 | 0.0053982 | 0.064871 | 0.060022 | 0.0020508 | -0.003388 | -0.0015765 | -0.036621 | 0.0020593 | 0.068225 | 0.056226 | -0.006759 | 0.0096515 | -0.0001046 | -21.8948 | 64.682 | -57.692 | 64.682 | -56.8954 | -57.7744 | -57.7423 | -17.3264 | 64.6317 | -57.605 | 64.7049 | -57.3669 | -57.7148 | -57.5363 | -0.10529 | -0.022888 | -0.022888 | 0.69122 | -0.15564 | -0.18768 | -0.050354 | -0.082397 | -0.01831 | -0.073242 | 0 | 0.21973 | 0.050354 | -0.12817 | 0.068664 | -0.10986 | 0.79651 | 122.374 | 0.23804 | 122.3099 | 122.374 | 122.2366 | 122.2687 | 122.2183 | -122.3969 | -122.3099 | 122.2687 | 122.2916 | 35.6918 | 40.2603
1206.3125 | 122.4518 | -57.5775 | 64.7644 | 0.102 | 0.0036892 | 0.064016 | 0.058954 | -0.0015808 | -0.0021064 | -0.00093566 | 0.012207 | 0.0029137 | 0.064593 | 0.054303 | -0.0065454 | 0.010079 | -0.0024546 | -22.3022 | 64.7095 | -57.6828 | 64.6317 | -56.9229 | -57.7606 | -57.7194 | -17.4637 | 64.6683 | -57.5912 | 64.6866 | -57.3669 | -57.6874 | -57.5455 | -0.10529 | -0.054931 | -0.13275 | 0.6546 | -0.14191 | -0.18311 | -0.036621 | -0.07782 | -0.013733 | -0.09613 | -0.07782 | 0.21057 | 0.032044 | -0.10986 | 0.045777 | -0.09613 | 0.75989 | 122.3145 | 0.22431 | 122.2778 | 122.3923 | 122.2595 | 122.287 | 122.2458 | -122.4472 | -122.3557 | 122.2092 | 122.2641 | 35.2753 | 40.1138
1207.3125 | 122.4976 | -57.5317 | 64.769 | -0.042954 | 0.0039028 | 0.063589 | 0.060449 | -0.0013672 | -0.0014654 | -0.0026447 | -0.027466 | 0.0022729 | 0.065234 | 0.060925 | -0.009109 | 0.011574 | -0.0043772 | -22.316 | 64.7232 | -57.6645 | 64.6774 | -56.9046 | -57.7423 | -57.7194 | -17.4957 | 64.6637 | -57.5684 | 64.7369 | -57.3257 | -57.6782 | -57.4997 | -0.13275 | -0.045776 | -0.091553 | 0.62714 | -0.18768 | -0.21057 | -0.054931 | -0.07782 | -0.036621 | -0.10529 | -0.032044 | 0.20599 | 0.032043 | -0.14649 | 0.068664 | -0.10986 | 0.75989 | 122.3419 | 0.24261 | 122.3053 | 122.3877 | 122.2321 | 122.2549 | 122.1954 | -122.4335 | -122.3373 | 122.2092 | 122.2687 | 35.2158 | 40.036
1208.3125 | 122.5983 | -57.55 | 64.7141 | -0.050583 | 0.0036892 | 0.065939 | 0.057245 | 0.0029052 | -0.00082456 | -8.1264e-05 | 0.0061035 | 0.0016321 | 0.065875 | 0.05943 | -0.0071864 | 0.011361 | -0.0054452 | -22.4808 | 64.6454 | -57.6736 | 64.6912 | -56.6345 | -57.5089 | -57.6553 | -17.5186 | 64.595 | -57.5546 | 64.8056 | -57.2571 | -57.6096 | -57.4448 | -0.1236 | -0.068664 | -0.022888 | 0.91553 | -0.10529 | 0.041199 | 0.018311 | 0.16479 | -0.004577 | -0.11902 | 0.091553 | 0.29297 | 0.10529 | -0.059509 | 0.10986 | -0.054932 | 1.0391 | 122.3648 | 0.29755 | 122.3602 | 122.319 | 122.1497 | 122.1954 | 122.1451 | -122.3877 | -122.2687 | 122.2412 | 122.3557 | 35.0693 | 40.0314
1209.3125 | 122.5021 | -57.5455 | 64.7919 | -0.050583 | 0.003262 | 0.063803 | 0.060449 | 0.0016236 | -0.0027472 | -0.00050846 | -0.015259 | 0.0033411 | 0.068438 | 0.063702 | -0.0093226 | 0.011147 | 0.0016044 | -22.6913 | 64.7186 | -57.6462 | 64.6912 | -56.8954 | -57.7103 | -57.6965 | -17.688 | 64.6729 | -57.5684 | 64.7369 | -57.3029 | -57.6599 | -57.4768 | -0.10071 | -0.073242 | -0.10071 | 0.65002 | -0.15106 | -0.16479 | -0.050354 | -0.064087 | -0.022888 | -0.11902 | -0.054932 | 0.24262 | 0.068664 | -0.11444 | 0.091552 | -0.091553 | 0.75073 | 122.3373 | 0.2655 | 122.3053 | 122.3648 | 122.2412 | 122.2641 | 122.2183 | -122.438 | -122.3602 | 122.2366 | 122.2824 | 34.8541 | 39.8575
1210.3125 | 122.4838 | -57.5272 | 64.7736 | -0.058212 | 0.004971 | 0.063803 | 0.063012 | -0.00051278 | -0.003388 | 0.0022687 | -0.01831 | 0.0039819 | 0.066729 | 0.058362 | -0.010391 | 0.0090105 | 0.0003226 | -22.9797 | 64.7415 | -57.6645 | 64.7095 | -56.8542 | -57.7148 | -57.6874 | -17.7612 | 64.6912 | -57.5409 | 64.7552 | -57.2983 | -57.6645 | -57.4814 | -0.13733 | -0.032044 | -0.064087 | 0.67291 | -0.16022 | -0.18768 | -0.022888 | -0.050354 | -0.013733 | -0.082398 | -0.018311 | 0.22888 | 0.045777 | -0.13733 | 0.05951 | -0.1236 | 0.81024 | 122.374 | 0.24262 | 122.2961 | 122.406 | 122.2321 | 122.2687 | 122.2183 | -122.4381 | -122.3145 | 122.2366 | 122.2824 | 34.5474 | 39.7659
1211.3125 | 122.4976 | -57.5592 | 64.7141 | -0.027695 | 0.003262 | 0.065085 | 0.061731 | 0.0016236 | -0.0042426 | -0.0028583 | -0.039673 | 0.0056909 | 0.064166 | 0.06712 | -0.0080408 | 0.0094379 | -0.0045908 | -23.2086 | 64.7003 | -57.6782 | 64.65 | -56.8954 | -57.7835 | -57.7286 | -17.9123 | 64.6637 | -57.5684 | 64.7461 | -57.3395 | -57.6828 | -57.518 | -0.11902 | -0.013733 | -0.064087 | 0.66376 | -0.16937 | -0.2243 | -0.050354 | -0.10528 | -0.009155 | -0.050354 | 0.032044 | 0.21973 | 0.041199 | -0.1236 | 0.050354 | -0.11444 | 0.78278 | 122.3282 | 0.22888 | 122.3145 | 122.3785 | 122.2321 | 122.2595 | 122.2229 | -122.3923 | -122.2824 | 122.2092 | 122.3053 | 34.3506 | 39.6469
1212.3125 | 122.5159 | -57.5409 | 64.7827 | -0.042954 | 0.0064664 | 0.065085 | 0.062585 | -0.00093998 | -0.0027472 | -0.00072206 | 0.021362 | 0.0031273 | 0.068652 | 0.062634 | -0.008468 | 0.011574 | -0.0037362 | -23.3139 | 64.7095 | -57.6508 | 64.7232 | -56.8039 | -57.8064 | -57.7972 | -17.9169 | 64.7003 | -57.518 | 64.7873 | -57.2708 | -57.6096 | -57.4631 | -0.10986 | -0.073242 | -0.059509 | 0.737 | -0.25635 | -0.2655 | -0.14648 | -0.15564 | 0.022889 | -0.082398 | 0.004577 | 0.27008 | 0.07782 | -0.068664 | 0.054931 | -0.091553 | 0.84686 | 122.374 | 0.24719 | 122.3053 | 122.3602 | 122.2183 | 122.2504 | 122.2412 | -122.4335 | -122.3007 | 122.2641 | 122.3282 | 34.227 | 39.624
1213.3125 | 122.5479 | -57.5134 | 64.7827 | -0.065842 | 0.0039028 | 0.065725 | 0.06109 | -0.0022218 | -0.0036018 | -8.1264e-05 | -0.021362 | 0.0035547 | 0.067798 | 0.060071 | -0.0080408 | 0.012429 | -0.0018136 | -23.465 | 64.7461 | -57.6324 | 64.6591 | -56.9962 | -57.6828 | -57.5409 | -18.0084 | 64.7095 | -57.5363 | 64.7964 | -57.2708 | -57.6279 | -57.4448 | -0.11902 | -0.036621 | -0.1236 | 0.51727 | -0.027466 | -0.16937 | 0.091552 | -0.050354 | -0.022888 | -0.073242 | 0.013733 | 0.24262 | 0.068665 | -0.11444 | 0.091553 | -0.091553 | 0.63629 | 122.2916 | 0.2655 | 122.3328 | 122.3785 | 122.2458 | 122.2595 | 122.2229 | -122.4152 | -122.319 | 122.1725 | 122.3099 | 34.0485 | 39.505
1214.3281 | 122.5891 | -57.4997 | 64.7827 | -0.11925 | 0.002194 | 0.06423 | 0.060235 | 0.002478 | -0.0027472 | -8.1264e-05 | -0.033569 | 0.0016321 | 0.06737 | 0.058575 | -0.0080408 | 0.0096515 | 0.0007498 | -23.735 | 64.7369 | -57.6553 | 64.7186 | -56.8268 | -57.7194 | -57.692 | -18.2098 | 64.6683 | -57.5363 | 64.8056 | -57.2388 | -57.6141 | -57.4127 | -0.15564 | -0.045777 | -0.064087 | 0.67291 | -0.19226 | -0.21973 | -0.036622 | -0.064087 | -0.036621 | -0.11444 | 0.022888 | 0.26093 | 0.086975 | -0.11444 | 0.1236 | -0.07782 | 0.82855 | 122.374 | 0.29755 | 122.3419 | 122.3923 | 122.2046 | 122.2366 | 122.168 | -122.438 | -122.319 | 122.2183 | 122.3053 | 33.7646 | 39.2899
1215.3125 | 122.5204 | -57.4585 | 64.8331 | -0.027695 | 0.0036892 | 0.062948 | 0.060876 | 0.00055542 | -0.0012518 | 0.0018413 | -0.01831 | 0.0044091 | 0.064593 | 0.06413 | -0.0065454 | 0.010933 | 0.0013906 | -23.8403 | 64.7644 | -57.6141 | 64.7461 | -56.7627 | -57.6508 | -57.6233 | -18.2007 | 64.7369 | -57.4951 | 64.801 | -57.2388 | -57.605 | -57.431 | -0.15564 | -0.068665 | -0.086975 | 0.6958 | -0.1648 | -0.19226 | -0.009155 | -0.036621 | -0.036621 | -0.096131 | -0.032044 | 0.21973 | 0.027466 | -0.14648 | 0.064087 | -0.10986 | 0.85144 | 122.3602 | 0.25635 | 122.2961 | 122.3785 | 122.2321 | 122.2229 | 122.1954 | -122.4472 | -122.3282 | 122.2046 | 122.2595 | 33.6182 | 39.2578
1216.3125 | 122.5067 | -57.4951 | 64.8102 | -0.050583 | 0.0043302 | 0.063376 | 0.060449 | 0.00034182 | -0.0029608 | -8.1264e-05 | -0.015259 | 0.0014185 | 0.068225 | 0.056439 | -0.006759 | 0.010933 | -0.0009592 | -24.0005 | 64.7552 | -57.6187 | 64.7552 | -56.7627 | -57.637 | -57.6096 | -18.306 | 64.7324 | -57.4814 | 64.8148 | -57.2342 | -57.6096 | -57.4265 | -0.1236 | -0.054932 | -0.054932 | 0.73242 | -0.11444 | -0.14191 | 0.009155 | -0.018311 | 0.013733 | -0.07782 | 0.004577 | 0.26093 | 0.068664 | -0.11444 | 0.054931 | -0.12817 | 0.85602 | 122.374 | 0.24719 | 122.2961 | 122.374 | 122.2137 | 122.2504 | 122.2275 | -122.4289 | -122.2916 | 122.2504 | 122.3099 | 33.4946 | 39.1891
1217.3125 | 122.5754 | -57.4814 | 64.7507 | -0.11925 | 0.0034756 | 0.065512 | 0.061303 | 0.00034182 | -0.0016792 | -0.0032855 | 0.021362 | 0.0014185 | 0.065661 | 0.059644 | -0.0078272 | 0.0098651 | 0.000109 | -24.1287 | 64.6866 | -57.5912 | 64.7873 | -56.7078 | -57.637 | -57.5867 | -18.4113 | 64.65 | -57.5089 | 64.8376 | -57.2021 | -57.5638 | -57.399 | -0.10986 | -0.064087 | 0.036621 | 0.77362 | -0.10529 | -0.15564 | 0.004578 | -0.045776 | -0.027466 | -0.10071 | 0.086975 | 0.27924 | 0.082397 | -0.082398 | 0.10986 | -0.054932 | 0.88348 | 122.3785 | 0.3067 | 122.3465 | 122.2778 | 122.1588 | 122.168 | 122.1313 | -122.3419 | -122.2595 | 122.2687 | 122.319 | 33.3527 | 39.0701
1218.3125 | 122.3282 | -57.5684 | 64.7049 | -0.10399 | 0.0043302 | 0.06423 | 0.062372 | 0.00098262 | -0.0029608 | -0.00050846 | -0.064087 | 0.0029137 | 0.06502 | 0.059644 | -0.008468 | 0.01072 | -0.0007456 | -24.2569 | 64.7324 | -57.6462 | 64.6637 | -56.8726 | -57.7835 | -57.7377 | -18.7546 | 64.7003 | -57.5638 | 64.7003 | -57.3669 | -57.8064 | -57.7057 | -0.07782 | 0.027466 | -0.041199 | 0.6958 | -0.16937 | -0.21515 | -0.091553 | -0.13733 | 0.004577 | -0.004578 | -0.004578 | 0.20142 | -0.13733 | -0.23804 | -0.14191 | -0.24261 | 0.77362 | 122.3099 | 0.19684 | 122.2641 | 122.3785 | 122.2641 | 122.3007 | 122.2687 | -122.3511 | -122.2687 | 122.2321 | 122.2687 | 33.3115 | 38.8138
1219.3125 | 122.4655 | -57.5363 | 64.769 | -0.012436 | 0.0034756 | 0.065085 | 0.061517 | 0.0018372 | -0.00232 | -0.0024311 | -0.039673 | 0.0020593 | 0.06502 | 0.059003 | -0.0080408 | 0.0085833 | -0.0018136 | -24.4354 | 64.7461 | -57.6233 | 64.6591 | -56.8726 | -57.7789 | -57.6965 | -18.7866 | 64.7003 | -57.5684 | 64.7278 | -57.3303 | -57.6874 | -57.5089 | -0.086975 | -0.022888 | -0.10986 | 0.66376 | -0.16022 | -0.24262 | -0.073242 | -0.15564 | -0.032043 | -0.068665 | -0.041199 | 0.20599 | 0.027466 | -0.15106 | 0.059509 | -0.11902 | 0.75073 | 122.2824 | 0.23804 | 122.2961 | 122.3694 | 122.2687 | 122.2824 | 122.2366 | -122.3923 | -122.3373 | 122.1954 | 122.2641 | 33.1009 | 38.7497
1220.3125 | 122.5845 | -57.5043 | 64.7507 | -0.10399 | 0.0043302 | 0.064657 | 0.060449 | 0.0065368 | -0.0027472 | -0.00050846 | -0.0030517 | 0.00056395 | 0.064807 | 0.057721 | -0.009109 | 0.010933 | -0.0009592 | -24.4263 | 64.7003 | -57.6462 | 64.769 | -56.7352 | -57.6691 | -57.6004 | -18.8004 | 64.6179 | -57.5455 | 64.8376 | -57.2525 | -57.55 | -57.3898 | -0.14191 | -0.050354 | 0.018311 | 0.76904 | -0.096131 | -0.16479 | 0.045776 | -0.022888 | -0.041199 | -0.13275 | 0.086975 | 0.25177 | 0.11444 | -0.045777 | 0.15564 | -0.004578 | 0.91095 | 122.4152 | 0.29297 | 122.3831 | 122.3465 | 122.1634 | 122.2046 | 122.1222 | -122.3969 | -122.2961 | 122.2733 | 122.3419 | 33.078 | 38.7039
1221.3125 | 122.493 | -57.5546 | 64.7736 | -0.065842 | 0.0019802 | 0.065512 | 0.062799 | 0.0029052 | -0.004029 | 0.0014141 | -0.057983 | 0.0041955 | 0.066729 | 0.064557 | -0.0065454 | 0.01072 | -0.0011728 | -24.5316 | 64.7186 | -57.6553 | 64.7095 | -56.8085 | -57.7286 | -57.6828 | -18.9835 | 64.6729 | -57.5546 | 64.7232 | -57.3257 | -57.6874 | -57.4951 | -0.10071 | -0.054932 | -0.064087 | 0.74615 | -0.12817 | -0.17395 | -0.027466 | -0.073243 | 0 | -0.10071 | -0.050354 | 0.22888 | 0.059509 | -0.13275 | 0.059509 | -0.13275 | 0.84686 | 122.3648 | 0.22888 | 122.2778 | 122.374 | 122.2275 | 122.2733 | 122.2275 | -122.4289 | -122.3282 | 122.2641 | 122.2778 | 33.0231 | 38.5712
1222.3125 | 122.5754 | -57.5089 | 64.8376 | -0.042954 | 0.002194 | 0.064016 | 0.061731 | -0.0011536 | -0.003388 | -0.0030719 | -0.067139 | 0.0024865 | 0.067798 | 0.059003 | -0.0069726 | 0.01072 | 0.0009634 | -24.6368 | 64.7186 | -57.6462 | 64.6454 | -56.8634 | -57.7744 | -57.7103 | -19.249 | 64.7186 | -57.55 | 64.7507 | -57.6462 | -58.0124 | -57.6096 | -0.13733 | -0.11902 | -0.19226 | 0.64545 | -0.20142 | -0.2655 | -0.064087 | -0.12817 | -0.041199 | -0.11902 | -0.086975 | -0.13733 | -0.10071 | -0.50354 | -0.059509 | -0.46234 | 0.78278 | 122.2916 | -0.09613 | 122.3007 | 122.3648 | 122.2687 | 122.2275 | 122.2275 | -122.4838 | -122.3877 | 122.1542 | 122.2595 | 32.872 | 38.2599
1223.3125 | 122.5937 | -57.4951 | 64.7644 | -0.11162 | 0.0024076 | 0.063803 | 0.059808 | 0.00034182 | -0.0025336 | -0.00093566 | 0.064087 | 0.00035035 | 0.066729 | 0.052594 | -0.0069726 | 0.010292 | -0.0022408 | -24.7192 | 64.7232 | -57.5958 | 64.7461 | -56.7261 | -57.6187 | -57.6004 | -19.1986 | 64.65 | -57.5043 | 64.8285 | -57.1976 | -57.5226 | -57.4036 | -0.10071 | -0.041198 | -0.01831 | 0.76904 | -0.10529 | -0.1236 | -0.004578 | -0.022888 | -0.009155 | -0.11444 | 0.064087 | 0.29755 | 0.091553 | -0.027466 | 0.10071 | -0.018311 | 0.86975 | 122.3419 | 0.3067 | 122.3328 | 122.319 | 122.1542 | 122.2183 | 122.1451 | -122.3602 | -122.2687 | 122.2412 | 122.3236 | 32.7759 | 38.2965
1224.3125 | 122.5067 | -57.4905 | 64.7919 | 0.102 | 0.0034756 | 0.065512 | 0.059167 | -0.0028626 | -0.0036018 | -0.00029486 | -0.057983 | 0.0041955 | 0.065448 | 0.06178 | -0.008468 | 0.010933 | -0.0013864 | -24.8154 | 64.7278 | -57.6233 | 64.7598 | -56.7352 | -57.637 | -57.6187 | -19.3497 | 64.7232 | -57.5317 | 64.7736 | -57.2479 | -57.6141 | -57.4402 | -0.13275 | -0.064087 | -0.032043 | 0.75531 | -0.12817 | -0.14648 | 0.004578 | -0.013733 | -0.041198 | -0.068664 | -0.01831 | 0.24262 | 0.050354 | -0.1236 | 0.091552 | -0.082398 | 0.88806 | 122.3831 | 0.28381 | 122.3053 | 122.3511 | 122.2549 | 122.2183 | 122.2137 | -122.4152 | -122.3236 | 122.2504 | 122.2641 | 32.6752 | 38.1409
1225.3125 | 122.4655 | -57.5043 | 64.7781 | -0.10399 | 0.0034756 | 0.064444 | 0.060022 | -0.00029898 | -0.0014654 | -0.0020039 | -0.073242 | 0.0014185 | 0.066302 | 0.066266 | -0.0076136 | 0.0083697 | -0.0030954 | -24.9435 | 64.7415 | -57.6324 | 64.7232 | -56.7627 | -57.7103 | -57.6553 | -19.5786 | 64.7369 | -57.5409 | 64.7598 | -57.2937 | -57.6691 | -57.486 | -0.12817 | -0.036621 | -0.054931 | 0.74158 | -0.15106 | -0.20599 | -0.022888 | -0.07782 | -0.036622 | -0.041199 | -0.01831 | 0.21057 | 0.01831 | -0.16479 | 0.054932 | -0.12817 | 0.86975 | 122.3557 | 0.24719 | 122.3007 | 122.374 | 122.2778 | 122.2458 | 122.2412 | -122.4106 | -122.319 | 122.2275 | 122.2641 | 32.5607 | 37.9257
1226.3125 | 122.5662 | -57.5226 | 64.6912 | -0.08873 | 0.0058256 | 0.064657 | 0.057031 | 0.0014098 | -0.004029 | -0.00093566 | 0.039673 | 0.0029137 | 0.063098 | 0.05943 | -0.0063318 | 0.011574 | 0.0007498 | -25.1495 | 64.6545 | -57.6324 | 64.7507 | -56.694 | -57.6691 | -57.5912 | -19.6426 | 64.6271 | -57.5317 | 64.8056 | -57.2342 | -57.5958 | -57.431 | -0.10986 | -0.036621 | 0.059509 | 0.82855 | -0.068665 | -0.14648 | 0.041198 | -0.036621 | -0.009155 | -0.064087 | 0.11444 | 0.28839 | 0.091553 | -0.073242 | 0.10071 | -0.064087 | 0.93841 | 122.3831 | 0.29755 | 122.3373 | 122.287 | 122.1588 | 122.1771 | 122.1497 | -122.3236 | -122.2229 | 122.2733 | 122.3282 | 32.373 | 37.8799
1227.3125 | 122.4564 | -57.5775 | 64.7324 | -0.081101 | 0.0051846 | 0.065725 | 0.060876 | 0.002478 | -0.00061096 | 0.0024823 | -0.079346 | 0.0029137 | 0.066516 | 0.058575 | -0.0088952 | 0.010292 | -0.0028818 | -25.383 | 64.6912 | -57.6874 | 64.6362 | -56.8176 | -57.7698 | -57.7332 | -19.8807 | 64.6591 | -57.5912 | 64.6774 | -57.3486 | -57.724 | -57.5226 | -0.10986 | -0.041199 | -0.096131 | 0.75989 | -0.15564 | -0.19226 | -0.045776 | -0.082397 | -0.013733 | -0.073242 | -0.054932 | 0.22888 | 0.054932 | -0.14648 | 0.068665 | -0.13275 | 0.86975 | 122.3236 | 0.24262 | 122.2687 | 122.3785 | 122.2504 | 122.2687 | 122.2366 | -122.4197 | -122.3236 | 122.2137 | 122.2549 | 32.1945 | 37.6968
1228.3125 | 122.4197 | -57.5958 | 64.7278 | -0.10399 | 0.0051846 | 0.063376 | 0.062372 | -0.0013672 | -0.0025336 | 0.00077334 | -0.1709 | 0.0024865 | 0.065234 | 0.066907 | -0.0071864 | 0.0090105 | 0.0016044 | -25.5478 | 64.6729 | -57.7194 | 64.5813 | -56.9046 | -57.8293 | -57.8567 | -19.7845 | 64.6637 | -57.5729 | 64.6683 | -57.3486 | -57.7148 | -57.5546 | -0.1236 | -0.054931 | -0.14648 | 0.69122 | -0.26093 | -0.23346 | -0.13733 | -0.10986 | 0.022888 | -0.064087 | -0.059509 | 0.24719 | 0.041199 | -0.11902 | 0.018311 | -0.14191 | 0.81482 | 122.3007 | 0.2243 | 122.2412 | 122.3923 | 122.2366 | 122.2687 | 122.2595 | -122.4472 | -122.3007 | 122.1771 | 122.2641 | 32.048 | 37.8113
1229.3125 | 122.493 | -57.5775 | 64.7049 | -0.12688 | 0.0028348 | 0.064016 | 0.061303 | 0.002478 | -0.0027472 | 0.0016277 | -0.030517 | 0.0039819 | 0.067157 | 0.06178 | -0.0076136 | 0.0096515 | -0.0024546 | -25.6531 | 64.6912 | -57.7011 | 64.6225 | -56.8314 | -57.7835 | -57.7377 | -20.1553 | 64.6408 | -57.5867 | 64.7095 | -57.3349 | -57.6965 | -57.518 | -0.1236 | -0.013733 | -0.082397 | 0.74616 | -0.16022 | -0.20599 | -0.036621 | -0.082397 | -0.009155 | -0.064087 | 0.004578 | 0.24262 | 0.05951 | -0.11902 | 0.068665 | -0.10986 | 0.86975 | 122.3236 | 0.25177 | 122.2961 | 122.3923 | 122.2275 | 122.2687 | 122.2183 | -122.406 | -122.2916 | 122.2 | 122.287 | 31.9244 | 37.4222
1230.3125 | 122.4747 | -57.5592 | 64.7186 | -0.073471 | 0.0026212 | 0.064657 | 0.062372 | -0.0013672 | -0.0014654 | 0.0029095 | -0.042725 | 0.0027001 | 0.063739 | 0.057935 | -0.0059046 | 0.0098651 | -0.0024546 | -25.7767 | 64.6866 | -57.6874 | 64.6317 | -56.8222 | -57.7652 | -57.724 | -20.2881 | 64.6729 | -57.5958 | 64.7095 | -57.3257 | -57.6965 | -57.518 | -0.12817 | -0.032044 | -0.086975 | 0.737 | -0.16479 | -0.20599 | -0.036621 | -0.07782 | -0.036621 | -0.045776 | -0.009155 | 0.23346 | 0.041199 | -0.13733 | 0.07782 | -0.10071 | 0.86517 | 122.319 | 0.27008 | 122.3053 | 122.374 | 122.2687 | 122.2458 | 122.2321 | -122.406 | -122.3145 | 122.1909 | 122.2687 | 31.7825 | 37.2711
1231.3125 | 122.5891 | -57.4951 | 64.7552 | -0.058212 | 0.003262 | 0.064016 | 0.058954 | -0.003717 | 0.00045724 | 0.0039777 | 0.20142 | 0.00035035 | 0.065875 | 0.060071 | -0.0080408 | 0.0096515 | -0.0009592 | -25.7492 | 64.6957 | -57.6004 | 64.801 | -56.5796 | -57.5638 | -57.518 | -20.2469 | 64.7003 | -57.5272 | 64.8102 | -57.1198 | -57.5455 | -57.4081 | -0.10529 | -0.059509 | 0.045776 | 0.91553 | -0.022888 | -0.068665 | 0.082398 | 0.036621 | -0.032044 | -0.054932 | 0.054932 | 0.37537 | 0.086975 | -0.050354 | 0.11902 | -0.01831 | 1.0208 | 122.4014 | 0.40741 | 122.3373 | 122.2961 | 122.2275 | 122.1909 | 122.1954 | -122.3557 | -122.2824 | 122.2961 | 122.3053 | 31.7459 | 37.2482
1232.3125 | 122.4564 | -57.5546 | 64.7552 | -0.27184 | 0.004971 | 0.065085 | 0.061517 | 0.00098262 | -0.0018928 | -0.0020039 | -0.064087 | 0.0016321 | 0.065661 | 0.062634 | -0.0071864 | 0.010292 | -0.0056588 | -25.7355 | 64.682 | -57.6874 | 64.6088 | -56.8314 | -57.7423 | -57.7194 | -20.5627 | 64.6729 | -57.5684 | 64.7049 | -57.3303 | -57.7103 | -57.5363 | -0.13275 | -0.073242 | -0.14648 | 0.72327 | -0.16479 | -0.18768 | -0.032043 | -0.054932 | -0.013733 | -0.082397 | -0.050354 | 0.2243 | 0.01831 | -0.15564 | 0.032043 | -0.14191 | 0.85602 | 122.2961 | 0.23804 | 122.2733 | 122.3694 | 122.2412 | 122.2366 | 122.2275 | -122.4426 | -122.3236 | 122.1634 | 122.2595 | 31.8192 | 36.9919
1233.3125 | 122.5388 | -57.5409 | 64.7324 | -0.065842 | 0.003262 | 0.065085 | 0.06109 | -0.0024354 | -0.00082456 | -0.0015765 | -0.045776 | 0.0027001 | 0.067157 | 0.062421 | -0.0069726 | 0.010079 | -0.0037362 | -26.1108 | 64.7095 | -57.6599 | 64.65 | -56.7581 | -57.7377 | -57.692 | -20.6589 | 64.65 | -57.5684 | 64.7552 | -57.2571 | -57.6416 | -57.4448 | -0.11902 | -0.022888 | -0.082398 | 0.78278 | -0.15106 | -0.19684 | -0.032044 | -0.07782 | -0.027465 | -0.082398 | 0.022888 | 0.28381 | 0.096131 | -0.10071 | 0.1236 | -0.073243 | 0.90179 | 122.3099 | 0.31128 | 122.3236 | 122.3694 | 122.2183 | 122.2504 | 122.1909 | -122.3923 | -122.3007 | 122.1909 | 122.2961 | 31.4301 | 36.882
1234.3125 | 122.5754 | -57.4951 | 64.7507 | -0.058212 | 0.003262 | 0.067221 | 0.059808 | -0.00029898 | 0.00024344 | 0.00098694 | 0.027466 | -0.00029045 | 0.065448 | 0.057721 | -0.0078272 | 0.0098651 | -0.0003182 | -25.9415 | 64.7278 | -57.5958 | 64.5584 | -56.6895 | -57.4219 | -57.55 | -20.5902 | 64.6271 | -57.5272 | 64.8285 | -57.1014 | -57.4905 | -57.3898 | -0.10071 | -0.022888 | -0.19226 | 0.80566 | -0.054932 | 0.073242 | 0.045776 | 0.17395 | -0.032044 | -0.1236 | 0.07782 | 0.39368 | 0.10529 | 0.004577 | 0.13733 | 0.036621 | 0.90637 | 122.1542 | 0.42572 | 122.3557 | 122.3236 | 122.1542 | 122.2229 | 122.1222 | -122.3465 | -122.2778 | 122.0535 | 122.3236 | 31.5537 | 36.9049
1235.3125 | 122.4792 | -57.5546 | 64.7552 | -0.058212 | 0.0034756 | 0.065298 | 0.063653 | 0.0031188 | -0.0029608 | 0.00034614 | -0.073242 | 0.0031273 | 0.068866 | 0.059003 | -0.0076136 | 0.010506 | -0.0013864 | -26.1566 | 64.7278 | -57.6828 | 64.6545 | -56.7902 | -57.7789 | -57.7103 | -20.9747 | 64.6957 | -57.5867 | 64.7186 | -57.3166 | -57.6965 | -57.5089 | -0.12817 | -0.027466 | -0.10071 | 0.76447 | -0.15564 | -0.22431 | -0.027466 | -0.096131 | -0.032044 | -0.059509 | -0.036621 | 0.23804 | 0.045776 | -0.14191 | 0.07782 | -0.10986 | 0.89264 | 122.3373 | 0.27008 | 122.3053 | 122.4106 | 122.2824 | 122.2824 | 122.2504 | -122.438 | -122.3419 | 122.2092 | 122.2733 | 31.398 | 36.5799
1236.3125 | 122.5891 | -57.5317 | 64.6957 | -0.081101 | 0.0041166 | 0.064657 | 0.06109 | -0.00072638 | -0.0031744 | 0.00055974 | 0.0091553 | 0.0020593 | 0.06737 | 0.059857 | -0.0080408 | 0.0096515 | -0.0018136 | -26.1246 | 64.6591 | -57.6324 | 64.7736 | -56.6071 | -57.6324 | -57.5775 | -21.0205 | 64.6545 | -57.5363 | 64.8148 | -57.193 | -57.5821 | -57.4127 | -0.10071 | -0.036621 | 0.07782 | 0.92468 | -0.045777 | -0.10071 | 0.054931 | 0 | -0.004578 | -0.041199 | 0.11902 | 0.33874 | 0.11902 | -0.050354 | 0.1236 | -0.045776 | 1.0254 | 122.406 | 0.34332 | 122.3511 | 122.2916 | 122.1909 | 122.1909 | 122.1863 | -122.3282 | -122.2321 | 122.3053 | 122.3465 | 31.4072 | 36.5112
1237.3125 | 122.5754 | -57.5272 | 64.7324 | -0.08873 | 0.0043302 | 0.065085 | 0.061731 | 0.0020508 | -0.0036018 | 0.00034614 | -0.045776 | 0.00056395 | 0.06502 | 0.057721 | -0.0076136 | 0.0098651 | -0.0030954 | -26.2619 | 64.7003 | -57.6462 | 64.6866 | -56.6895 | -57.6965 | -57.6508 | -21.2494 | 64.6545 | -57.5592 | 64.7919 | -57.2021 | -57.5912 | -57.4265 | -0.11902 | -0.032044 | -0.045777 | 0.83771 | -0.1236 | -0.16937 | -0.004578 | -0.050354 | -0.032043 | -0.07782 | 0.059509 | 0.32501 | 0.10071 | -0.064087 | 0.13275 | -0.032044 | 0.95673 | 122.3328 | 0.35706 | 122.3511 | 122.3465 | 122.2137 | 122.2275 | 122.1817 | -122.3785 | -122.2916 | 122.2137 | 122.319 | 31.2653 | 36.2778
1238.3125 | 122.6074 | -57.5317 | 64.6774 | -0.11162 | 0.0062528 | 0.065725 | 0.059167 | 0.0035462 | 0.0015252 | -0.0028583 | -0.027466 | 0.0018457 | 0.068011 | 0.060071 | -0.006759 | 0.010079 | -0.0003182 | -26.3031 | 64.6362 | -57.6324 | 64.7232 | -56.4331 | -57.4814 | -57.6324 | -21.4783 | 64.6179 | -57.5867 | 64.801 | -57.1838 | -57.5958 | -57.4356 | -0.10071 | -0.041199 | 0.045777 | 1.0986 | -0.10071 | 0.050354 | 0 | 0.15106 | -0.054932 | -0.059509 | 0.1236 | 0.3479 | 0.09613 | -0.064087 | 0.15106 | -0.009155 | 1.1993 | 122.3557 | 0.40283 | 122.3877 | 122.2687 | 122.2046 | 122.168 | 122.1497 | -122.3099 | -122.2641 | 122.2549 | 122.3328 | 31.2286 | 36.0535
1239.3125 | 122.5479 | -57.5134 | 64.6957 | -0.08873 | 0.004971 | 0.064657 | 0.061517 | -0.00051278 | -0.0014654 | 0.00098694 | -0.0030517 | 0.00056395 | 0.065661 | 0.061139 | -0.0074 | 0.010506 | -0.0022408 | -26.413 | 64.6362 | -57.6645 | 64.7369 | -56.5842 | -57.637 | -57.605 | -21.5652 | 64.6042 | -57.55 | 64.7644 | -57.225 | -57.5821 | -57.431 | -0.15106 | -0.05951 | 0.041198 | 0.92926 | -0.091552 | -0.1236 | 0.05951 | 0.027466 | -0.036621 | -0.091553 | 0.068664 | 0.28839 | 0.082398 | -0.068664 | 0.11902 | -0.032043 | 1.0803 | 122.4014 | 0.32501 | 122.3145 | 122.3007 | 122.1542 | 122.1497 | 122.1176 | -122.3602 | -122.2458 | 122.2504 | 122.2778 | 31.1005 | 35.9482
1240.3125 | 122.5983 | -57.5409 | 64.7003 | -0.12688 | 0.0079618 | 0.067648 | 0.060235 | 0.00055542 | -0.0014654 | -0.00050846 | -0.01831 | 0.00099115 | 0.069293 | 0.058148 | -0.0069726 | 0.010933 | -0.0013864 | -26.6922 | 64.5767 | -57.6691 | 64.7827 | -56.5796 | -57.6736 | -57.5867 | -21.7117 | 64.6088 | -57.55 | 64.8239 | -57.193 | -57.5775 | -57.4173 | -0.12817 | -0.1236 | 0.082398 | 0.9613 | -0.045776 | -0.13275 | 0.082397 | -0.004578 | -0.009155 | -0.091552 | 0.1236 | 0.3479 | 0.1236 | -0.036621 | 0.13275 | -0.027466 | 1.0895 | 122.4518 | 0.35706 | 122.374 | 122.2458 | 122.1588 | 122.1176 | 122.1497 | -122.3694 | -122.2504 | 122.3236 | 122.3648 | 30.8487 | 35.8292
1241.3125 | 122.612 | -57.5043 | 64.7736 | -0.065842 | 0.004971 | 0.064444 | 0.05874 | 0.0029052 | -0.0042426 | -0.0013629 | 0.015259 | 0.0018457 | 0.062671 | 0.056866 | -0.0080408 | 0.0098651 | -0.0001046 | -26.5366 | 64.6957 | -57.6141 | 64.7919 | -56.5292 | -57.55 | -57.5226 | -21.8079 | 64.6454 | -57.4997 | 64.8102 | -57.1289 | -57.5272 | -57.3898 | -0.10986 | -0.07782 | 0.01831 | 0.97504 | -0.018311 | -0.045777 | 0.091553 | 0.064087 | 0.004577 | -0.12817 | 0.036621 | 0.37537 | 0.11444 | -0.022889 | 0.10986 | -0.027466 | 1.0849 | 122.406 | 0.37079 | 122.3099 | 122.3099 | 122.1451 | 122.2 | 122.1497 | -122.3877 | -122.2733 | 122.2961 | 122.3145 | 30.9677 | 35.6964
1242.3125 | 122.5479 | -57.5409 | 64.7415 | -0.058212 | 0.0045438 | 0.064016 | 0.061303 | -0.0035034 | -0.00232 | -0.00072206 | -0.0030517 | 0.0044091 | 0.068438 | 0.059216 | -0.0076136 | 0.010933 | -0.0045908 | -26.6876 | 64.6591 | -57.6416 | 64.7552 | -56.5567 | -57.6462 | -57.5684 | -22.0367 | 64.6179 | -57.55 | 64.7827 | -57.1884 | -57.5775 | -57.4219 | -0.10071 | -0.082397 | 0.013733 | 0.98419 | -0.027465 | -0.10528 | 0.073243 | -0.004577 | -0.009155 | -0.1236 | 0.041199 | 0.35248 | 0.11902 | -0.036621 | 0.12817 | -0.027466 | 1.0849 | 122.3969 | 0.36163 | 122.3328 | 122.3007 | 122.168 | 122.2 | 122.1588 | -122.3831 | -122.2916 | 122.2961 | 122.3236 | 30.8533 | 35.5042
1243.3125 | 122.5021 | -57.5226 | 64.7324 | -0.10399 | 0.0053982 | 0.062094 | 0.060235 | 0.0020508 | -0.0044562 | -0.0028583 | 0.0030517 | 0.0039819 | 0.065234 | 0.059644 | -0.006759 | 0.0085833 | -0.0048044 | -26.7242 | 64.6774 | -57.6279 | 64.7186 | -56.5933 | -57.637 | -57.5958 | -22.0139 | 64.6774 | -57.5043 | 64.769 | -57.1793 | -57.605 | -57.4493 | -0.10529 | -0.054932 | -0.013733 | 0.92926 | -0.073242 | -0.11444 | 0.032044 | -0.009155 | 0.018311 | -0.054932 | 0.036621 | 0.34332 | 0.073242 | -0.082397 | 0.054931 | -0.10071 | 1.0345 | 122.3465 | 0.32501 | 122.2733 | 122.3053 | 122.1817 | 122.2 | 122.2 | -122.3602 | -122.2366 | 122.2412 | 122.2916 | 30.7983 | 35.5087
1244.3125 | 122.5388 | -57.4997 | 64.7827 | -0.065842 | 0.0041166 | 0.064657 | 0.059595 | 0.00076902 | -0.0014654 | -0.0026447 | -0.024414 | 0.0018457 | 0.063739 | 0.059216 | -0.0074 | 0.0098651 | -0.0048044 | -26.6739 | 64.7095 | -57.5867 | 64.8102 | -56.4835 | -57.5409 | -57.518 | -22.2839 | 64.6957 | -57.5317 | 64.8285 | -57.1198 | -57.5317 | -57.3898 | -0.086975 | -0.073242 | 0.027466 | 1.0162 | -0.01831 | -0.041199 | 0.068665 | 0.045776 | -0.032043 | -0.086975 | 0.045776 | 0.37994 | 0.10986 | -0.032043 | 0.14191 | 0 | 1.1032 | 122.3969 | 0.41199 | 122.3602 | 122.2961 | 122.2275 | 122.2092 | 122.1954 | -122.3694 | -122.3145 | 122.3099 | 122.3282 | 30.8258 | 35.2158
1245.3125 | 122.58 | -57.5226 | 64.7186 | -0.19554 | 0.0036892 | 0.065725 | 0.063012 | 0.0039734 | -0.0029608 | -0.0013629 | -0.054932 | 0.0033411 | 0.066302 | 0.057721 | -0.0093226 | 0.01072 | -0.0022408 | -26.7151 | 64.65 | -57.6508 | 64.7781 | -56.5247 | -57.6187 | -57.5867 | -22.403 | 64.6408 | -57.5821 | 64.7827 | -57.1426 | -57.55 | -57.3898 | -0.12817 | -0.068665 | 0.059509 | 0.99792 | -0.064087 | -0.09613 | 0.064087 | 0.032044 | -0.059509 | -0.07782 | 0.064087 | 0.37994 | 0.13275 | -0.027466 | 0.19226 | 0.032043 | 1.1261 | 122.4289 | 0.43945 | 122.3648 | 122.3007 | 122.2229 | 122.1725 | 122.1634 | -122.3694 | -122.3007 | 122.3007 | 122.3053 | 30.8075 | 35.1196
1246.3125 | 122.5845 | -57.4722 | 64.7736 | 0.23933 | 0.0047574 | 0.067648 | 0.058954 | 0.0011962 | -0.0053108 | -0.00050846 | 0.015259 | 0.0012047 | 0.065234 | 0.060071 | -0.0052638 | 0.0096515 | -0.0030954 | -26.9806 | 64.6957 | -57.605 | 64.8376 | -56.4468 | -57.5775 | -57.4905 | -22.4899 | 64.682 | -57.5043 | 64.8697 | -57.0831 | -57.4814 | -57.3441 | -0.13275 | -0.07782 | 0.064086 | 1.0254 | -0.018311 | -0.10529 | 0.11444 | 0.027465 | -0.032043 | -0.091553 | 0.09613 | 0.3891 | 0.12817 | -0.009155 | 0.16022 | 0.022888 | 1.1581 | 122.4426 | 0.42114 | 122.374 | 122.3007 | 122.1863 | 122.168 | 122.1542 | -122.3785 | -122.2778 | 122.3099 | 122.3419 | 30.4916 | 34.9823
1247.3125 | 122.5616 | -57.4905 | 64.7369 | -0.073471 | 0.0051846 | 0.063162 | 0.06344 | -0.0028626 | -0.0010382 | 0.0018413 | -0.01831 | 0.0016321 | 0.062884 | 0.060071 | -0.0069726 | 0.0090105 | 0.0005362 | -26.77 | 64.6637 | -57.6141 | 64.7827 | -56.4697 | -57.5958 | -57.5363 | -22.7142 | 64.6408 | -57.5272 | 64.8239 | -57.1381 | -57.55 | -57.3898 | -0.1236 | -0.073242 | 0.045777 | 1.0208 | -0.045776 | -0.10528 | 0.07782 | 0.018311 | -0.036621 | -0.09613 | 0.086976 | 0.35248 | 0.10071 | -0.059509 | 0.13733 | -0.022888 | 1.1444 | 122.3969 | 0.3891 | 122.3511 | 122.2778 | 122.168 | 122.1542 | 122.1313 | -122.3511 | -122.2641 | 122.2733 | 122.3145 | 30.7205 | 34.7763
1248.3125 | 122.525 | -57.5089 | 64.7507 | -0.11925 | 0.0047574 | 0.063376 | 0.060235 | -0.00072638 | -0.0014654 | -0.0022175 | 0.0030517 | 0.0012047 | 0.066089 | 0.060284 | -0.0063318 | 0.010292 | 0.001177 | -26.8158 | 64.6912 | -57.6187 | 64.7278 | -56.4926 | -57.637 | -57.5867 | -22.9202 | 64.6774 | -57.5272 | 64.7964 | -57.1472 | -57.5729 | -57.4219 | -0.10986 | -0.059509 | -0.022888 | 1.0162 | -0.07782 | -0.12817 | 0.032043 | -0.018311 | -0.018311 | -0.073242 | 0.045777 | 0.36163 | 0.086975 | -0.064087 | 0.10529 | -0.045776 | 1.1261 | 122.3465 | 0.37994 | 122.3236 | 122.3099 | 122.2046 | 122.2 | 122.1863 | -122.3694 | -122.2778 | 122.2366 | 122.3053 | 30.6931 | 34.5886
1249.3125 | 122.4976 | -57.5043 | 64.7827 | -0.08873 | 0.0041166 | 0.06658 | 0.061944 | -0.0011536 | 2.9842e-05 | 0.0012005 | -0.0061035 | 0.0037683 | 0.068225 | 0.063275 | -0.0082544 | 0.0096515 | -0.0018136 | -26.8295 | 64.7141 | -57.6233 | 64.7278 | -56.4972 | -57.6141 | -57.5546 | -23.0988 | 64.6637 | -57.5089 | 64.7964 | -57.1472 | -57.5546 | -57.399 | -0.11902 | -0.068665 | -0.054932 | 1.0071 | -0.050354 | -0.10986 | 0.068665 | 0.009155 | -0.004578 | -0.11902 | 0.013733 | 0.35706 | 0.10529 | -0.050354 | 0.10986 | -0.045776 | 1.1261 | 122.3511 | 0.36163 | 122.3053 | 122.3373 | 122.1725 | 122.2183 | 122.168 | -122.406 | -122.2916 | 122.2321 | 122.3007 | 30.6747 | 34.4055
1250.3125 | 122.5342 | -57.5043 | 64.7644 | -0.035324 | 0.0043302 | 0.067007 | 0.059167 | -0.002649 | -0.0016792 | -0.0022175 | 0.033569 | 0.0024865 | 0.067584 | 0.058575 | -0.0054774 | 0.0092241 | -0.0030954 | -26.8204 | 64.7141 | -57.6096 | 64.7598 | -56.4606 | -57.5912 | -57.55 | -23.2361 | 64.682 | -57.5089 | 64.8056 | -57.1198 | -57.5226 | -57.3807 | -0.10529 | -0.050354 | -0.004577 | 1.0437 | -0.045777 | -0.086976 | 0.059509 | 0.01831 | -0.004578 | -0.082397 | 0.041199 | 0.38452 | 0.1236 | -0.018311 | 0.12817 | -0.013733 | 1.149 | 122.3694 | 0.3891 | 122.3145 | 122.3236 | 122.1909 | 122.2183 | 122.1863 | -122.374 | -122.2733 | 122.2641 | 122.3099 | 30.6839 | 34.2682
1251.3125 | 122.4609 | -57.4951 | 64.8285 | -0.050583 | 0.0071072 | 0.064444 | 0.059808 | -0.0062806 | -0.0038154 | 0.00055974 | -0.021362 | 0.0027001 | 0.065875 | 0.05943 | -0.0065454 | 0.010933 | -0.0043772 | -26.651 | 64.7552 | -57.5867 | 64.7598 | -56.4331 | -57.5684 | -57.5317 | -23.4055 | 64.7644 | -57.4768 | 64.7736 | -57.1609 | -57.5775 | -57.4356 | -0.091553 | -0.073242 | -0.068664 | 1.062 | -0.036621 | -0.073242 | 0.054932 | 0.018311 | 0.01831 | -0.064087 | -0.054931 | 0.33417 | 0.059509 | -0.082398 | 0.041199 | -0.10071 | 1.1536 | 122.3465 | 0.31586 | 122.2504 | 122.3419 | 122.2412 | 122.2504 | 122.2595 | -122.4152 | -122.3053 | 122.2549 | 122.2687 | 30.8441 | 34.0897
1252.3125 | 122.5159 | -57.5043 | 64.7827 | -0.081101 | 0.003262 | 0.065725 | 0.05874 | -8.538e-05 | -0.0014654 | 0.0012005 | -0.033569 | 0.00099115 | 0.065661 | 0.061139 | -0.0071864 | 0.010933 | -0.0028818 | -26.6876 | 64.7003 | -57.605 | 64.7552 | -56.4239 | -57.5958 | -57.5363 | -23.4741 | 64.7186 | -57.4905 | 64.7919 | -57.1472 | -57.5409 | -57.399 | -0.10071 | -0.082398 | -0.027466 | 1.0803 | -0.032044 | -0.091553 | 0.068664 | 0.009155 | 0.013732 | -0.064087 | 0.009155 | 0.35706 | 0.10529 | -0.036622 | 0.091553 | -0.050354 | 1.181 | 122.3602 | 0.34332 | 122.2824 | 122.3053 | 122.2092 | 122.2046 | 122.2229 | -122.3877 | -122.2733 | 122.2595 | 122.2961 | 30.8166 | 34.0302
1253.3125 | 122.5845 | -57.4768 | 64.7644 | -0.081101 | 0.004971 | 0.065939 | 0.059595 | 0.00034182 | -0.0025336 | 0.0012005 | -0.0091553 | 0.0029137 | 0.065661 | 0.057294 | -0.006759 | 0.0094379 | -0.0003182 | -26.6281 | 64.7278 | -57.6004 | 64.7736 | -56.3965 | -57.5729 | -57.5134 | -23.6526 | 64.6912 | -57.5089 | 64.8331 | -57.0923 | -57.4814 | -57.3395 | -0.1236 | -0.036621 | 0.009156 | 1.0803 | -0.036621 | -0.09613 | 0.086975 | 0.027466 | -0.032043 | -0.073242 | 0.068665 | 0.38452 | 0.13733 | -0.004577 | 0.16937 | 0.027466 | 1.2039 | 122.374 | 0.41657 | 122.3419 | 122.3282 | 122.2 | 122.2046 | 122.168 | -122.3648 | -122.2733 | 122.2504 | 122.3099 | 30.8487 | 33.8242
1254.3125 | 122.4747 | -57.5134 | 64.8148 | -0.0048066 | 0.0053982 | 0.063376 | 0.062799 | -0.0035034 | -0.0038154 | -0.0015765 | -0.05188 | 0.0024865 | 0.066089 | 0.060071 | -0.0082544 | 0.01072 | 0.0013906 | -26.5045 | 64.7736 | -57.6416 | 64.7278 | -56.4468 | -57.637 | -57.5821 | -23.8815 | 64.7461 | -57.4997 | 64.7552 | -57.1747 | -57.5912 | -57.4356 | -0.12817 | -0.041198 | -0.086975 | 1.0666 | -0.068664 | -0.1236 | 0.05951 | 0.004578 | 0.013733 | -0.068664 | -0.059509 | 0.33874 | 0.07782 | -0.07782 | 0.064087 | -0.091553 | 1.1948 | 122.3694 | 0.32501 | 122.2549 | 122.4152 | 122.2458 | 122.287 | 122.2595 | -122.4564 | -122.3145 | 122.2412 | 122.2687 | 31.0089 | 33.6319
1255.3125 | 122.5388 | -57.4814 | 64.7598 | -0.12688 | 0.0043302 | 0.066366 | 0.059808 | 0.0016236 | -0.00061096 | -0.0022175 | 0.0030517 | 0.00013675 | 0.066943 | 0.061566 | -0.0078272 | 0.0079425 | -0.0018136 | -26.326 | 64.7003 | -57.637 | 64.6774 | -56.3965 | -57.5729 | -57.5684 | -24.0646 | 64.682 | -57.5317 | 64.7964 | -57.1243 | -57.55 | -57.399 | -0.15564 | -0.05951 | -0.082398 | 1.0849 | -0.086975 | -0.091553 | 0.068665 | 0.064087 | -0.050354 | -0.07782 | 0.036621 | 0.35705 | 0.082397 | -0.068665 | 0.13275 | -0.018311 | 1.2405 | 122.3145 | 0.40741 | 122.3282 | 122.3373 | 122.2137 | 122.1817 | 122.1634 | -122.3969 | -122.2916 | 122.1588 | 122.2778 | 31.1554 | 33.4167
1256.3125 | 122.5113 | -57.4905 | 64.8148 | -0.058212 | 0.0047574 | 0.065939 | 0.060235 | -0.00072638 | -0.0027472 | -0.0024311 | -0.01831 | 0.00035035 | 0.066729 | 0.060925 | -0.0063318 | 0.0096515 | 0.0009634 | -26.1063 | 64.7186 | -57.5821 | 64.7964 | -56.3141 | -57.518 | -57.5043 | -24.0921 | 64.7095 | -57.486 | 64.8102 | -57.1014 | -57.518 | -57.3898 | -0.091552 | -0.09613 | -0.01831 | 1.1765 | -0.013732 | -0.027465 | 0.07782 | 0.064087 | 0.004578 | -0.10528 | -0.004577 | 0.3891 | 0.10071 | -0.027465 | 0.09613 | -0.032043 | 1.268 | 122.3785 | 0.38452 | 122.2961 | 122.3007 | 122.1954 | 122.2092 | 122.2 | -122.3969 | -122.3007 | 122.287 | 122.3007 | 31.3843 | 33.3984
1257.3125 | 122.6074 | -57.4631 | 64.7736 | -0.050583 | 0.0045438 | 0.063376 | 0.058954 | -0.0045716 | -0.0018928 | 0.0012005 | -0.0061035 | 0.0020593 | 0.065234 | 0.057507 | -0.0074 | 0.011147 | 0.0016044 | -25.9506 | 64.6957 | -57.6141 | 64.7827 | -56.3141 | -57.5409 | -57.518 | -24.2661 | 64.6454 | -57.4997 | 64.8514 | -57.0694 | -57.5043 | -57.3395 | -0.15106 | -0.07782 | 0.009155 | 1.149 | -0.054931 | -0.07782 | 0.096131 | 0.073242 | -0.036621 | -0.12817 | 0.077819 | 0.39368 | 0.1236 | -0.041198 | 0.16022 | -0.004577 | 1.3 | 122.3969 | 0.4303 | 122.3511 | 122.3099 | 122.1451 | 122.1588 | 122.1085 | -122.3877 | -122.2733 | 122.2458 | 122.3145 | 31.5125 | 33.197
1258.3125 | 122.5937 | -57.4768 | 64.7644 | -0.042954 | 0.0051846 | 0.06423 | 0.058954 | -0.0017944 | -0.0014654 | -0.0017903 | 0.012207 | 0.0016321 | 0.064807 | 0.056653 | -0.0074 | 0.0098651 | -0.0048044 | -25.7355 | 64.7278 | -57.6324 | 64.7827 | -56.2775 | -57.5272 | -57.486 | -24.4125 | 64.6729 | -57.5272 | 64.8514 | -57.0786 | -57.4768 | -57.3441 | -0.15564 | -0.036621 | 0.018311 | 1.1993 | -0.009155 | -0.050354 | 0.14648 | 0.10529 | -0.050354 | -0.091552 | 0.086975 | 0.39825 | 0.13275 | 0 | 0.18311 | 0.050354 | 1.355 | 122.4152 | 0.44861 | 122.3785 | 122.3602 | 122.2 | 122.2046 | 122.1497 | -122.3969 | -122.2916 | 122.2595 | 122.3282 | 31.7413 | 33.0643
1259.3125 | 122.4701 | -57.5226 | 64.8239 | -0.035324 | 0.0034756 | 0.062521 | 0.060663 | 0.0018372 | -0.0029608 | -0.0020039 | -0.091553 | 0.0041955 | 0.066302 | 0.059857 | -0.0088952 | 0.01371 | -0.0037362 | -25.5981 | 64.7644 | -57.6187 | 64.7186 | -56.3461 | -57.6141 | -57.5775 | -24.678 | 64.7186 | -57.518 | 64.7644 | -57.1609 | -57.6004 | -57.4219 | -0.09613 | -0.05951 | -0.10529 | 1.1765 | -0.054932 | -0.091553 | 0.041198 | 0.004577 | 0.004578 | -0.10529 | -0.05951 | 0.36163 | 0.10071 | -0.07782 | 0.09613 | -0.082398 | 1.2726 | 122.3373 | 0.35706 | 122.2824 | 122.3831 | 122.2366 | 122.287 | 122.2412 | -122.4426 | -122.3419 | 122.2412 | 122.287 | 31.9244 | 32.8445
1260.3125 | 122.6074 | -57.4814 | 64.7781 | -0.050583 | 0.0026212 | 0.066153 | 0.05874 | -0.00029898 | -0.0025336 | -0.00072206 | -0.0061035 | 0.0014185 | 0.063952 | 0.059857 | -0.0059046 | 0.0098651 | -0.0018136 | -25.3647 | 64.7369 | -57.5912 | 64.856 | -56.1401 | -57.4585 | -57.4356 | -24.6506 | 64.6774 | -57.4951 | 64.888 | -56.9962 | -57.5317 | -57.3669 | -0.10986 | -0.041199 | 0.07782 | 1.3412 | 0.045776 | 0.022888 | 0.15564 | 0.13275 | -0.013733 | -0.10071 | 0.10986 | 0.48523 | 0.11444 | -0.050354 | 0.12817 | -0.036621 | 1.4511 | 122.4472 | 0.49896 | 122.3831 | 122.3282 | 122.1725 | 122.2183 | 122.1588 | -122.3694 | -122.2733 | 122.3373 | 122.3694 | 32.1167 | 32.8308
1261.3125 | 122.4884 | -57.5272 | 64.8102 | -0.027695 | 0.0019802 | 0.065298 | 0.06344 | -0.00029898 | -0.0018928 | -0.00050846 | -0.085449 | 0.0031273 | 0.068011 | 0.063702 | -0.0076136 | 0.0096515 | -0.003309 | -25.1862 | 64.7461 | -57.6324 | 64.7232 | -56.2866 | -57.6233 | -57.5729 | -24.9481 | 64.7461 | -57.5409 | 64.7598 | -57.1518 | -57.5867 | -57.4265 | -0.10529 | -0.064087 | -0.086975 | 1.2405 | -0.045776 | -0.09613 | 0.059509 | 0.009155 | -0.013733 | -0.064087 | -0.050354 | 0.37537 | 0.10071 | -0.059509 | 0.11444 | -0.045776 | 1.3458 | 122.3557 | 0.3891 | 122.3007 | 122.3785 | 122.287 | 122.2733 | 122.2733 | -122.4426 | -122.3511 | 122.2504 | 122.287 | 32.341 | 32.579
1262.3125 | 122.5708 | -57.5043 | 64.7781 | -0.020065 | 0.0056118 | 0.065939 | 0.060449 | 0.00055542 | -0.0012518 | 0.0014141 | -0.012207 | 0.0029137 | 0.065234 | 0.056653 | -0.0080408 | 0.011147 | -0.0020272 | -24.852 | 64.7003 | -57.605 | 64.8102 | -56.1676 | -57.4997 | -57.4722 | -25.09 | 64.6591 | -57.5089 | 64.8376 | -57.0602 | -57.4814 | -57.3441 | -0.10071 | -0.07782 | 0.032044 | 1.3367 | 0.032043 | 0.004577 | 0.13275 | 0.10528 | -0.004578 | -0.11902 | 0.059509 | 0.44403 | 0.16022 | 0.022888 | 0.1648 | 0.027466 | 1.4374 | 122.4152 | 0.44861 | 122.3465 | 122.3053 | 122.168 | 122.2046 | 122.1634 | -122.3831 | -122.287 | 122.3145 | 122.3419 | 32.6523 | 32.4142
1263.3125 | 122.4838 | -57.5226 | 64.7964 | -0.035324 | 0.0056118 | 0.064871 | 0.059595 | -0.0015808 | -0.00232 | -0.0013629 | -0.012207 | 0.0039819 | 0.065661 | 0.06178 | -0.0052638 | 0.0092241 | -0.0030954 | -24.7192 | 64.7095 | -57.637 | 64.7324 | -56.218 | -57.5684 | -57.5272 | -25.3143 | 64.6957 | -57.5317 | 64.7507 | -57.1655 | -57.5729 | -57.431 | -0.11444 | -0.086975 | -0.064087 | 1.3046 | -0.004578 | -0.045776 | 0.10986 | 0.068665 | -0.009155 | -0.10071 | -0.045777 | 0.35706 | 0.091553 | -0.050354 | 0.10071 | -0.041199 | 1.4191 | 122.3694 | 0.36621 | 122.2824 | 122.3465 | 122.2275 | 122.2321 | 122.2183 | -122.4335 | -122.3282 | 122.2549 | 122.2733 | 32.8033 | 32.2083
1264.3125 | 122.4609 | -57.5226 | 64.8102 | -0.035324 | 0.0062528 | 0.065298 | 0.062158 | 0.00076902 | -0.00061096 | -0.0026447 | -0.033569 | 0.0031273 | 0.066302 | 0.05943 | -0.0046228 | 0.0090105 | -0.000532 | -24.4812 | 64.7186 | -57.6141 | 64.7278 | -56.2134 | -57.5638 | -57.5272 | -25.5203 | 64.6866 | -57.5363 | 64.7324 | -57.1289 | -57.5912 | -57.4539 | -0.091553 | -0.091553 | -0.082398 | 1.3092 | -0.004578 | -0.041199 | 0.086975 | 0.050354 | -0.013733 | -0.1236 | -0.07782 | 0.39368 | 0.068665 | -0.068665 | 0.082398 | -0.054932 | 1.4008 | 122.3419 | 0.40741 | 122.2687 | 122.3328 | 122.2229 | 122.2412 | 122.2092 | -122.4243 | -122.3465 | 122.2504 | 122.2549 | 33.0414 | 32.0023
1265.3125 | 122.5937 | -57.4722 | 64.7736 | -0.050583 | 0.0043302 | 0.065512 | 0.06109 | 0.00034182 | -0.0014654 | 0.0048321 | -0.073242 | 0.0016321 | 0.065448 | 0.059857 | -0.0088952 | 0.0096515 | -0.0026682 | -24.2981 | 64.6683 | -57.5958 | 64.769 | -55.687 | -57.2937 | -57.7286 | -25.4929 | 64.6225 | -57.5272 | 64.8331 | -57.0236 | -57.4768 | -57.3624 | -0.1236 | -0.10529 | -0.004578 | 1.7853 | -0.25635 | 0.17853 | -0.13275 | 0.30212 | -0.054932 | -0.15106 | 0.059509 | 0.44861 | 0.10986 | -0.004578 | 0.16479 | 0.050354 | 1.9089 | 122.3648 | 0.50354 | 122.3602 | 122.2641 | 122.1497 | 122.1405 | 122.0947 | -122.3694 | -122.3007 | 122.2412 | 122.3053 | 33.1741 | 31.9794
1266.3125 | 122.4884 | -57.5592 | 64.7736 | 0.018082 | 0.0051846 | 0.064444 | 0.062372 | 0.0026916 | -0.00082456 | 0.0022687 | -0.10071 | 0.0024865 | 0.067157 | 0.066693 | -0.0076136 | 0.010079 | -0.005018 | -24.1333 | 64.6957 | -57.6736 | 64.7324 | -56.1493 | -57.6004 | -57.5867 | -25.8316 | 64.682 | -57.55 | 64.7644 | -57.1518 | -57.6096 | -57.4356 | -0.11444 | -0.07782 | -0.041199 | 1.4099 | -0.027466 | -0.041199 | 0.086975 | 0.073242 | 0.009155 | -0.091553 | -0.009156 | 0.40741 | 0.1236 | -0.050354 | 0.11444 | -0.059509 | 1.5244 | 122.406 | 0.39825 | 122.3145 | 122.3694 | 122.2321 | 122.2549 | 122.2412 | -122.4472 | -122.3236 | 122.2916 | 122.3236 | 33.4259 | 31.7276
1267.3125 | 122.4838 | -57.5363 | 64.7919 | -0.027695 | 0.0051846 | 0.064016 | 0.062585 | -0.0011536 | -0.0031744 | 0.00055974 | 0.018311 | 0.0044091 | 0.066089 | 0.058575 | -0.0069726 | 0.0098651 | -0.0003182 | -23.8541 | 64.7141 | -57.6462 | 64.6866 | -56.1264 | -57.5958 | -57.5638 | -25.9735 | 64.6683 | -57.5363 | 64.7232 | -57.1381 | -57.6096 | -57.4677 | -0.10986 | -0.07782 | -0.10529 | 1.4099 | -0.027466 | -0.059509 | 0.082397 | 0.050354 | 0 | -0.1236 | -0.068664 | 0.39825 | 0.068665 | -0.073242 | 0.068665 | -0.073242 | 1.5198 | 122.3328 | 0.39825 | 122.2595 | 122.3602 | 122.2046 | 122.2504 | 122.2046 | -122.438 | -122.3282 | 122.2229 | 122.2595 | 33.6823 | 31.5628
1268.3125 | 122.4564 | -57.55 | 64.7781 | -0.17265 | 0.0056118 | 0.062735 | 0.064081 | -0.0017944 | -0.0018928 | -0.00072206 | -0.045776 | 0.0041955 | 0.066089 | 0.062207 | -0.0082544 | 0.0098651 | -0.0009592 | -23.5886 | 64.7186 | -57.6828 | 64.6591 | -56.1493 | -57.5867 | -57.5912 | -26.2207 | 64.6912 | -57.5729 | 64.7095 | -57.1655 | -57.6279 | -57.4722 | -0.13275 | -0.059509 | -0.11902 | 1.4008 | -0.041199 | -0.036621 | 0.091552 | 0.09613 | -0.022888 | -0.086975 | -0.068664 | 0.38452 | 0.07782 | -0.07782 | 0.10071 | -0.054932 | 1.5335 | 122.3419 | 0.40741 | 122.2824 | 122.4014 | 122.2641 | 122.2687 | 122.2412 | -122.4609 | -122.3511 | 122.2092 | 122.2595 | 33.9615 | 31.3293
1269.3125 | 122.4701 | -57.5729 | 64.8102 | -0.10399 | 0.0024076 | 0.066153 | 0.061517 | 0.0052552 | -0.0010382 | -0.0043537 | -0.01831 | 0.0029137 | 0.067157 | 0.059216 | -0.0086816 | 0.011147 | 0.001177 | -23.2635 | 64.7049 | -57.6416 | 64.6774 | -56.0898 | -57.5638 | -57.5546 | -26.3443 | 64.6729 | -57.5729 | 64.6957 | -57.1518 | -57.6324 | -57.486 | -0.068665 | -0.10529 | -0.13275 | 1.4832 | 0.018311 | 0.009155 | 0.086976 | 0.07782 | 0 | -0.13733 | -0.11444 | 0.42114 | 0.086975 | -0.059509 | 0.086975 | -0.059509 | 1.5518 | 122.319 | 0.42114 | 122.2687 | 122.3465 | 122.2458 | 122.2778 | 122.2458 | -122.4518 | -122.3831 | 122.2504 | 122.2687 | 34.3094 | 31.2286
1270.3125 | 122.525 | -57.518 | 64.8148 | -0.020065 | 0.0043302 | 0.06658 | 0.060663 | 0.0022644 | 0.00024344 | -0.0011493 | -0.021362 | 0.0035547 | 0.068438 | 0.060712 | -0.0065454 | 0.010079 | 0.001818 | -22.9568 | 64.6912 | -57.6736 | 64.6683 | -56.0715 | -57.6004 | -57.5867 | -26.5274 | 64.6683 | -57.5729 | 64.6912 | -57.1381 | -57.6553 | -57.4356 | -0.15564 | -0.1236 | -0.14648 | 1.4465 | -0.068665 | -0.082398 | 0.086975 | 0.073242 | -0.054932 | -0.14648 | -0.1236 | 0.37994 | 0.082397 | -0.13733 | 0.13733 | -0.082397 | 1.6022 | 122.3419 | 0.43488 | 122.2641 | 122.3648 | 122.2412 | 122.2092 | 122.1863 | -122.4884 | -122.3877 | 122.1863 | 122.2092 | 34.5612 | 30.9906
1271.3125 | 122.4609 | -57.6004 | 64.7461 | -0.050583 | 0.0045438 | 0.065725 | 0.062372 | -8.538e-05 | -0.0021064 | 0.0073955 | -0.091553 | 0.0037683 | 0.064593 | 0.061566 | -0.0061182 | 0.012001 | -0.0048044 | -22.7829 | 64.6683 | -57.7469 | 64.4394 | -56.5018 | -57.5272 | -57.3532 | -26.7792 | 64.6591 | -57.6096 | 64.682 | -57.2388 | -57.692 | -57.4905 | -0.14648 | -0.07782 | -0.3067 | 1.0986 | 0.24719 | 0.073242 | 0.39368 | 0.21973 | -0.009155 | -0.086975 | -0.064087 | 0.36163 | 0.10986 | -0.091553 | 0.11902 | -0.082398 | 1.2451 | 122.1863 | 0.37079 | 122.2916 | 122.4152 | 122.2687 | 122.2687 | 122.2595 | -122.493 | -122.3557 | 122.0398 | 122.2824 | 34.8175 | 30.8212
1272.3125 | 122.4243 | -57.5912 | 64.7232 | -0.065842 | 0.0039028 | 0.064657 | 0.061303 | -0.00072638 | -0.0014654 | -0.0017903 | 0.021362 | 0.0024865 | 0.066516 | 0.061352 | -0.0044092 | 0.011147 | -0.003309 | -22.4716 | 64.7232 | -57.6645 | 64.6408 | -56.0623 | -57.6004 | -57.5684 | -26.8616 | 64.6591 | -57.5684 | 64.7324 | -56.9046 | -57.7927 | -57.6096 | -0.073242 | 0 | -0.082398 | 1.5289 | 0.022889 | -0.009155 | 0.096131 | 0.064087 | 0.022889 | -0.064087 | 0.009155 | 0.68665 | -0.01831 | -0.20142 | -0.041199 | -0.22431 | 1.6022 | 122.3053 | 0.66376 | 122.3007 | 122.3877 | 122.2275 | 122.3145 | 122.2504 | -122.3877 | -122.2916 | 122.2321 | 122.3236 | 35.1196 | 30.7297
1273.3125 | 122.4564 | -57.5729 | 64.7415 | -0.012436 | 0.0060392 | 0.06423 | 0.060022 | -0.00029898 | -0.0027472 | -0.0047809 | -0.033569 | 0.0035547 | 0.068438 | 0.066907 | -0.0046228 | 0.010292 | -0.0024546 | -22.2107 | 64.7186 | -57.6736 | 64.6362 | -56.0303 | -57.6141 | -57.5821 | -27.0309 | 64.6729 | -57.5867 | 64.7141 | -57.1655 | -57.637 | -57.4677 | -0.10071 | -0.022888 | -0.10529 | 1.5427 | -0.009155 | -0.041199 | 0.091553 | 0.059509 | -0.013733 | -0.068664 | -0.027466 | 0.40741 | 0.10529 | -0.064087 | 0.11902 | -0.050354 | 1.6434 | 122.3099 | 0.42114 | 122.3007 | 122.3923 | 122.2595 | 122.2916 | 122.2458 | -122.4152 | -122.3282 | 122.2092 | 122.287 | 35.3622 | 30.542
1274.3125 | 122.4747 | -57.5729 | 64.769 | -0.058212 | 0.0047574 | 0.06423 | 0.060663 | 0.004187 | -0.0014654 | -0.0020039 | 0.0061035 | 0.0046227 | 0.068652 | 0.056226 | -0.0063318 | 0.010079 | -0.0018136 | -21.8445 | 64.7003 | -57.6645 | 64.65 | -55.9845 | -57.605 | -57.5821 | -27.1683 | 64.6774 | -57.5775 | 64.5767 | -57.0648 | -57.6096 | -57.4539 | -0.091553 | -0.068665 | -0.11902 | 1.5884 | -0.009155 | -0.032043 | 0.082398 | 0.05951 | -0.004578 | -0.091553 | -0.19226 | 0.50812 | 0.11902 | -0.036621 | 0.1236 | -0.032043 | 1.68 | 122.3145 | 0.5127 | 122.1542 | 122.3648 | 122.2549 | 122.2733 | 122.2504 | -122.4335 | -122.3465 | 122.2229 | 122.1497 | 35.7285 | 30.4047
1275.3125 | 122.4472 | -57.5729 | 64.7781 | -0.027695 | 0.0056118 | 0.065298 | 0.063012 | -0.00029898 | -0.0055244 | 0.0012005 | -0.054932 | 0.0016321 | 0.067798 | 0.065839 | -0.0086816 | 0.0087969 | -0.0009592 | -21.6476 | 64.6866 | -57.7148 | 64.6408 | -55.9845 | -57.6187 | -57.5775 | -27.3148 | 64.7049 | -57.5729 | 64.7003 | -57.1472 | -57.6141 | -57.4722 | -0.14191 | -0.091553 | -0.13733 | 1.5884 | -0.004578 | -0.045776 | 0.13733 | 0.096131 | 0 | -0.073242 | -0.07782 | 0.42572 | 0.10071 | -0.041199 | 0.10071 | -0.041199 | 1.7303 | 122.3557 | 0.42572 | 122.2733 | 122.4014 | 122.2778 | 122.2595 | 122.2778 | -122.493 | -122.3511 | 122.2137 | 122.2733 | 35.9253 | 30.2582
1276.3125 | 122.4838 | -57.6004 | 64.7415 | -0.0048066 | 0.0068936 | 0.066794 | 0.062158 | 0.0033324 | -0.0021064 | -8.1264e-05 | -0.07019 | 0.0044091 | 0.066729 | 0.063702 | -0.008468 | 0.011574 | -0.0026682 | -21.3684 | 64.6774 | -57.6874 | 64.6454 | -55.9433 | -57.6141 | -57.5912 | -27.4429 | 64.6133 | -57.605 | 64.6957 | -57.1518 | -57.6508 | -57.4677 | -0.086975 | -0.064087 | -0.09613 | 1.6571 | 0.009155 | -0.013733 | 0.09613 | 0.073242 | -0.004577 | -0.12817 | -0.045776 | 0.44861 | 0.13275 | -0.050354 | 0.13733 | -0.045777 | 1.7441 | 122.3328 | 0.45319 | 122.3007 | 122.3648 | 122.2183 | 122.2778 | 122.2137 | -122.4289 | -122.3465 | 122.2458 | 122.2961 | 36.232 | 30.1575
1277.3125 | 122.5113 | -57.5592 | 64.7507 | -0.020065 | 0.0058256 | 0.064444 | 0.058313 | 0.00098262 | -0.0016792 | -0.0026447 | 0.018311 | 0.0024865 | 0.068225 | 0.056439 | -0.006759 | 0.012215 | -0.0009592 | -21.1441 | 64.6591 | -57.6553 | 64.7003 | -55.838 | -57.5134 | -57.5134 | -27.5711 | 64.6317 | -57.5729 | 64.7003 | -57.0969 | -57.5821 | -57.4493 | -0.09613 | -0.091552 | -0.050354 | 1.7212 | 0.045776 | 0.045776 | 0.14191 | 0.14191 | -0.013733 | -0.11902 | -0.050354 | 0.46234 | 0.10986 | -0.022888 | 0.1236 | -0.009155 | 1.8173 | 122.3557 | 0.47607 | 122.2733 | 122.3145 | 122.2046 | 122.2183 | 122.1909 | -122.406 | -122.3236 | 122.2595 | 122.2595 | 36.4151 | 29.9881
1278.3125 | 122.493 | -57.5775 | 64.7552 | -0.027695 | 0.0073208 | 0.065298 | 0.062372 | 0.0014098 | -0.0010382 | -0.0017903 | -0.039673 | 0.0063317 | 0.06972 | 0.061566 | -0.005691 | 0.011574 | -0.0007456 | -20.9061 | 64.7049 | -57.7057 | 64.6317 | -55.9158 | -57.605 | -57.5867 | -27.8229 | 64.6545 | -57.5912 | 64.682 | -57.1198 | -57.6508 | -57.4677 | -0.12817 | -0.050354 | -0.1236 | 1.6617 | -0.009155 | -0.027465 | 0.11902 | 0.10071 | -0.013733 | -0.10071 | -0.073242 | 0.45776 | 0.10986 | -0.073242 | 0.1236 | -0.059509 | 1.7899 | 122.3373 | 0.4715 | 122.2733 | 122.4106 | 122.2458 | 122.2824 | 122.2321 | -122.4609 | -122.3465 | 122.2092 | 122.2595 | 36.6714 | 29.7546
1279.3125 | 122.4792 | -57.5775 | 64.7369 | -0.027695 | 0.0060392 | 0.065298 | 0.058526 | 0.0011962 | -0.004029 | -0.00093566 | -0.085449 | 0.0035547 | 0.068652 | 0.06178 | -0.005691 | 0.0085833 | -0.0022408 | -20.6497 | 64.6912 | -57.7057 | 64.6179 | -55.806 | -57.2845 | -57.5867 | -27.9236 | 64.6454 | -57.6141 | 64.6637 | -57.106 | -57.637 | -57.4768 | -0.12817 | -0.045776 | -0.11902 | 1.7715 | -0.009155 | 0.29297 | 0.11902 | 0.42114 | -0.036621 | -0.091552 | -0.073242 | 0.4715 | 0.10071 | -0.059509 | 0.13733 | -0.022888 | 1.8997 | 122.3236 | 0.50812 | 122.2778 | 122.3969 | 122.2595 | 122.2687 | 122.2229 | -122.4426 | -122.3511 | 122.1954 | 122.2412 | 36.9278 | 29.6539
1280.3125 | 122.5342 | -57.6187 | 64.6729 | -0.08873 | 0.0045438 | 0.066366 | 0.063012 | 0.0031188 | -0.0029608 | 0.0012005 | -0.064087 | 0.0029137 | 0.066729 | 0.06413 | -0.0080408 | 0.010292 | -0.0020272 | -20.2789 | 64.6179 | -57.7377 | 64.5996 | -55.8655 | -57.6462 | -57.6187 | -28.1158 | 64.5905 | -57.6416 | 64.6866 | -57.1198 | -57.6462 | -57.4493 | -0.11902 | -0.054932 | -0.073243 | 1.7532 | 0 | -0.027466 | 0.11902 | 0.091553 | -0.022889 | -0.082398 | 0.013732 | 0.49896 | 0.16937 | -0.027466 | 0.19226 | -0.004577 | 1.8723 | 122.3373 | 0.52185 | 122.3282 | 122.3557 | 122.2321 | 122.2366 | 122.2092 | -122.4106 | -122.3145 | 122.2183 | 122.3053 | 37.3398 | 29.5029
1281.3125 | 122.4289 | -57.5912 | 64.6957 | -0.027695 | 0.00668 | 0.067434 | 0.061303 | 0.00076902 | -0.0010382 | 0.0020551 | -0.076294 | 0.0029137 | 0.067584 | 0.064343 | -0.0069726 | 0.01072 | -0.0018136 | -19.78 | 64.6729 | -57.7103 | 64.6225 | -55.7877 | -57.6416 | -57.5867 | -28.2623 | 64.6088 | -57.6233 | 64.6591 | -57.1381 | -57.6645 | -57.4768 | -0.11902 | -0.022888 | -0.073242 | 1.8036 | 0.004578 | -0.050354 | 0.1236 | 0.068664 | -0.032043 | -0.086975 | -0.036621 | 0.45319 | 0.11444 | -0.073242 | 0.14648 | -0.041199 | 1.9226 | 122.3328 | 0.48523 | 122.2824 | 122.3831 | 122.2321 | 122.2641 | 122.2 | -122.406 | -122.319 | 122.2137 | 122.2504 | 37.8113 | 29.3289
1282.3125 | 122.4655 | -57.5775 | 64.7369 | -0.050583 | 0.00668 | 0.06658 | 0.061303 | 0.0011962 | -0.0036018 | 0.00055974 | 0.0091553 | 0.0052637 | 0.068652 | 0.060284 | -0.0074 | 0.010506 | -0.0022408 | -19.455 | 64.682 | -57.6965 | 64.5172 | -55.7281 | -57.5821 | -57.6141 | -28.4088 | 64.6317 | -57.5867 | 64.6454 | -57.1152 | -57.637 | -57.4951 | -0.11902 | -0.054931 | -0.21973 | 1.8494 | -0.036621 | -0.004577 | 0.082397 | 0.11444 | -0.009155 | -0.10528 | -0.091552 | 0.46234 | 0.082398 | -0.059509 | 0.091553 | -0.050354 | 1.9684 | 122.2137 | 0.4715 | 122.2321 | 122.3785 | 122.2183 | 122.2595 | 122.2092 | -122.4335 | -122.3236 | 122.0947 | 122.2229 | 38.1226 | 29.1687
1283.3281 | 122.5067 | -57.6233 | 64.6957 | -0.073471 | 0.004971 | 0.066153 | 0.061731 | -0.0022218 | 0.00024344 | -0.00072206 | 0.057983 | 0.0012047 | 0.065234 | 0.051739 | -0.008468 | 0.010506 | -0.0022408 | -18.9331 | 64.5859 | -57.6965 | 64.6362 | -55.7098 | -57.5958 | -57.5317 | -28.4775 | 64.5538 | -57.6187 | 64.7003 | -57.0969 | -57.5958 | -57.4265 | -0.073242 | -0.10986 | -0.05951 | 1.9135 | 0.091553 | 0.027466 | 0.1648 | 0.10071 | 0.004578 | -0.14191 | 0.004577 | 0.52643 | 0.19684 | 0.027466 | 0.19226 | 0.022888 | 1.9867 | 122.3328 | 0.52185 | 122.319 | 122.2824 | 122.1725 | 122.2092 | 122.1771 | -122.3923 | -122.3145 | 122.2595 | 122.3236 | 38.6902 | 29.1458
1284.3125 | 122.5113 | -57.6096 | 64.7278 | -0.0048066 | 0.0064664 | 0.067434 | 0.061517 | 0.00034182 | -0.0025336 | 0.00034614 | -0.024414 | 0.0035547 | 0.066302 | 0.07182 | -0.0074 | 0.011361 | -0.003309 | -18.4296 | 64.6454 | -57.724 | 64.6088 | -55.7465 | -57.6096 | -57.5821 | -28.6835 | 64.6408 | -57.6096 | 64.6866 | -57.0969 | -57.6187 | -57.4677 | -0.11444 | -0.082397 | -0.11902 | 1.8631 | 0.027466 | 0 | 0.14191 | 0.11444 | 0 | -0.086975 | -0.041199 | 0.5127 | 0.14191 | -0.009155 | 0.14191 | -0.009155 | 1.9775 | 122.3328 | 0.5127 | 122.2961 | 122.3694 | 122.2504 | 122.2549 | 122.2504 | -122.4518 | -122.3373 | 122.2183 | 122.2961 | 39.18 | 28.9261
1285.3125 | 122.5708 | -57.605 | 64.6545 | -0.12688 | 0.00668 | 0.067434 | 0.060022 | 0.0022644 | -0.0021064 | -0.0028583 | 0.082398 | 0.00077755 | 0.068652 | 0.057935 | -0.0078272 | 0.011788 | -0.0026682 | -17.9581 | 64.5767 | -57.7286 | 64.6591 | -55.632 | -57.7515 | -57.7515 | -28.6285 | 64.563 | -57.6233 | 64.7324 | -57.0419 | -57.5912 | -57.4127 | -0.1236 | -0.07782 | 0.004578 | 1.973 | -0.14649 | -0.14649 | -0.022888 | -0.022888 | -0.018311 | -0.091553 | 0.07782 | 0.56305 | 0.19226 | 0.013732 | 0.21057 | 0.032043 | 2.0966 | 122.3877 | 0.58136 | 122.3557 | 122.3053 | 122.1863 | 122.1817 | 122.168 | -122.3831 | -122.2778 | 122.2641 | 122.3373 | 39.6469 | 28.9764
1286.3125 | 122.4609 | -57.6462 | 64.6637 | -0.050583 | 0.0053982 | 0.064871 | 0.063226 | -0.00029898 | -0.004029 | -0.00093566 | -0.054932 | 0.0024865 | 0.067584 | 0.056866 | -0.0078272 | 0.01072 | -0.000532 | -17.6147 | 64.6179 | -57.7423 | 64.5584 | -55.7419 | -57.6828 | -57.6324 | -28.9993 | 64.5813 | -57.6599 | 64.6179 | -57.1426 | -57.7148 | -57.518 | -0.096131 | -0.045776 | -0.10528 | 1.9043 | 0.013733 | -0.036621 | 0.10986 | 0.05951 | -0.013733 | -0.082397 | -0.045776 | 0.50354 | 0.12817 | -0.068665 | 0.14191 | -0.054932 | 2.0004 | 122.3007 | 0.51727 | 122.2778 | 122.3602 | 122.2412 | 122.2641 | 122.2275 | -122.406 | -122.3236 | 122.2046 | 122.2641 | 40.0314 | 28.6468
1287.3125 | 122.5525 | -57.6279 | 64.7003 | -0.0048066 | 0.0056118 | 0.06658 | 0.062372 | -8.538e-05 | -0.0010382 | -0.0024311 | -0.036621 | 0.0063317 | 0.066302 | 0.059857 | -0.0063318 | 0.012215 | -0.0060862 | -17.1112 | 64.6317 | -57.7377 | 64.6133 | -55.6183 | -57.5821 | -57.55 | -28.9948 | 64.5905 | -57.6279 | 64.7369 | -57.193 | -57.811 | -57.5729 | -0.10986 | -0.068664 | -0.086975 | 2.0096 | 0.07782 | 0.045777 | 0.18768 | 0.15564 | 0 | -0.10986 | 0.036621 | 0.43488 | 0.054932 | -0.18311 | 0.054932 | -0.18311 | 2.1194 | 122.3511 | 0.43488 | 122.3648 | 122.3694 | 122.2183 | 122.2595 | 122.2183 | -122.438 | -122.3282 | 122.2412 | 122.3648 | 40.5167 | 28.6331
1288.3125 | 122.5204 | -57.6233 | 64.6637 | -0.020065 | 0.0073208 | 0.067648 | 0.061944 | 0.00076902 | -0.0027472 | 0.0024823 | -0.067139 | 0.0046227 | 0.067157 | 0.066052 | -0.0074 | 0.011147 | -0.0009592 | -16.6809 | 64.6271 | -57.7332 | 64.6133 | -55.6 | -57.6004 | -57.5684 | -29.1275 | 64.5905 | -57.6324 | 64.6591 | -57.0969 | -57.6508 | -57.4585 | -0.10986 | -0.036621 | -0.050354 | 2.0233 | 0.054932 | 0.022888 | 0.16479 | 0.13275 | -0.009155 | -0.073242 | -0.004577 | 0.52643 | 0.1648 | -0.027466 | 0.17395 | -0.018311 | 2.1332 | 122.3465 | 0.53558 | 122.2916 | 122.3602 | 122.2229 | 122.2504 | 122.2137 | -122.3969 | -122.2961 | 122.2366 | 122.2824 | 40.9424 | 28.4958
1289.3125 | 122.4701 | -57.6416 | 64.6729 | -0.042954 | 0.0086026 | 0.065939 | 0.062585 | 0.0050414 | -0.0027472 | 0.0031231 | -0.21667 | 0.0059045 | 0.065234 | 0.056226 | -0.0063318 | 0.01072 | -0.0026682 | -16.3788 | 64.6088 | -57.7744 | 64.5218 | -55.7053 | -57.7011 | -57.6782 | -29.393 | 64.5355 | -57.7057 | 64.6271 | -57.1838 | -57.7011 | -57.4905 | -0.13275 | -0.064087 | -0.15106 | 1.9363 | -0.036621 | -0.059509 | 0.09613 | 0.073242 | -0.064086 | -0.13733 | -0.045777 | 0.45776 | 0.15106 | -0.059509 | 0.21515 | 0.004577 | 2.0691 | 122.2961 | 0.52185 | 122.3328 | 122.3831 | 122.2412 | 122.2504 | 122.1771 | -122.4472 | -122.3785 | 122.1634 | 122.2687 | 41.2628 | 28.2486
1290.3125 | 122.5662 | -57.6004 | 64.6271 | -0.11162 | 0.0068936 | 0.066153 | 0.062372 | 0.0018372 | -0.0012518 | -0.00050846 | 0.036621 | 0.0033411 | 0.064593 | 0.058575 | -0.0065454 | 0.012642 | 0.002886 | -15.9027 | 64.5859 | -57.7286 | 64.6454 | -55.4581 | -57.55 | -57.5272 | -29.2603 | 64.5126 | -57.6553 | 64.7049 | -57.0053 | -57.6004 | -57.4219 | -0.12817 | -0.041199 | 0.018311 | 2.1423 | 0.073242 | 0.050354 | 0.20142 | 0.17853 | -0.054931 | -0.11444 | 0.07782 | 0.59509 | 0.17853 | 0 | 0.23346 | 0.054931 | 2.2705 | 122.374 | 0.65002 | 122.3602 | 122.3145 | 122.168 | 122.1863 | 122.113 | -122.3557 | -122.2824 | 122.2458 | 122.3053 | 41.6977 | 28.3401
1291.3125 | 122.4472 | -57.6599 | 64.6591 | -0.058212 | 0.0056118 | 0.067648 | 0.065149 | -8.538e-05 | -0.0048834 | 0.0037639 | -0.24414 | 0.0041955 | 0.062243 | 0.059003 | -0.011032 | 0.012856 | -0.000532 | -15.5823 | 64.5996 | -57.7789 | 64.4989 | -55.632 | -57.7057 | -57.6874 | -29.2419 | 64.5584 | -57.6599 | 64.5905 | -57.1289 | -57.7103 | -57.5226 | -0.11902 | -0.05951 | -0.16022 | 2.0279 | -0.027466 | -0.045776 | 0.091553 | 0.073243 | 0 | -0.10071 | -0.068665 | 0.53101 | 0.13733 | -0.050354 | 0.13733 | -0.050354 | 2.1469 | 122.2778 | 0.53101 | 122.2504 | 122.3785 | 122.2183 | 122.2595 | 122.2183 | -122.4381 | -122.319 | 122.1588 | 122.2504 | 42.0776 | 28.418
1292.3125 | 122.5159 | -57.6233 | 64.6683 | -0.050583 | 0.0045438 | 0.065298 | 0.061944 | -0.00093998 | -0.0016792 | -0.00093566 | -0.021362 | 0.0016321 | 0.067157 | 0.058148 | -0.006759 | 0.011788 | -0.0018136 | -15.1474 | 64.6317 | -57.7332 | 64.5767 | -55.5176 | -57.5684 | -57.5729 | -29.5029 | 64.6042 | -57.6599 | 64.6545 | -57.0282 | -57.6141 | -57.4448 | -0.10986 | -0.036621 | -0.091553 | 2.1057 | 0.050354 | 0.054932 | 0.16022 | 0.16479 | -0.036621 | -0.064087 | -0.013733 | 0.59509 | 0.17853 | 0.009155 | 0.21515 | 0.045776 | 2.2156 | 122.3099 | 0.63171 | 122.3145 | 122.3648 | 122.2641 | 122.2549 | 122.2275 | -122.4014 | -122.3282 | 122.2 | 122.2778 | 42.4759 | 28.1204
1293.3125 | 122.4655 | -57.6645 | 64.6545 | -0.020065 | 0.0092434 | 0.067862 | 0.06344 | 0.002478 | -0.00082456 | 0.0012005 | -0.067139 | 0.0031273 | 0.066089 | 0.064557 | -0.009109 | 0.011147 | -0.0016 | -14.8178 | 64.5813 | -57.756 | 64.5447 | -55.5038 | -57.6324 | -57.5958 | -29.5807 | 64.5859 | -57.6599 | 64.595 | -57.106 | -57.7148 | -57.5043 | -0.091552 | -0.073242 | -0.10986 | 2.1606 | 0.068665 | 0.032044 | 0.16022 | 0.1236 | 0.004578 | -0.068665 | -0.059509 | 0.55847 | 0.16022 | -0.050354 | 0.15564 | -0.054932 | 2.2522 | 122.3007 | 0.55389 | 122.2549 | 122.3373 | 122.2458 | 122.2458 | 122.2504 | -122.4106 | -122.3145 | 122.2092 | 122.2595 | 42.8467 | 28.0838
1294.3125 | 122.5113 | -57.6553 | 64.6408 | -0.096359 | 0.0056118 | 0.065939 | 0.062372 | 0.0014098 | -0.0027472 | 0.0014141 | -0.033569 | 0.0027001 | 0.066516 | 0.06178 | -0.0065454 | 0.010933 | 0.0003226 | -14.4424 | 64.5584 | -57.7881 | 64.5081 | -55.4993 | -57.6691 | -57.6279 | -29.6768 | 64.5355 | -57.6828 | 64.6133 | -57.0831 | -57.692 | -57.5134 | -0.13275 | -0.082397 | -0.13275 | 2.1561 | 0.027465 | -0.013733 | 0.16022 | 0.11902 | -0.027466 | -0.10529 | -0.027466 | 0.5722 | 0.14191 | -0.036622 | 0.16937 | -0.009156 | 2.2888 | 122.2961 | 0.59967 | 122.2961 | 122.3465 | 122.2183 | 122.2137 | 122.1909 | -122.4289 | -122.3236 | 122.1634 | 122.2687 | 43.2129 | 27.9785
1295.3125 | 122.5525 | -57.6233 | 64.5813 | -0.042954 | 0.0073208 | 0.06658 | 0.059808 | 0.00055542 | -0.0031744 | 0.00077334 | -0.0030517 | 0.0012047 | 0.067584 | 0.061352 | -0.0074 | 0.010292 | -0.0001046 | -14.1266 | 64.5401 | -57.7469 | 64.6133 | -55.3986 | -57.5043 | -57.4677 | -29.5441 | 64.5126 | -57.6645 | 64.6774 | -56.9458 | -57.5729 | -57.4219 | -0.1236 | -0.041199 | 0.032043 | 2.2247 | 0.15564 | 0.11902 | 0.27924 | 0.24262 | -0.041199 | -0.068665 | 0.09613 | 0.67749 | 0.20142 | 0.050354 | 0.24262 | 0.091553 | 2.3483 | 122.3602 | 0.71869 | 122.3419 | 122.287 | 122.1771 | 122.1634 | 122.1359 | -122.3282 | -122.2458 | 122.2366 | 122.3007 | 43.4967 | 28.0792
1296.3125 | 122.5113 | -57.6645 | 64.6042 | -0.027695 | 0.0064664 | 0.065512 | 0.062585 | 0.00098262 | -0.00039736 | 0.0012005 | -0.054932 | 0.0027001 | 0.066943 | 0.064343 | -0.0054774 | 0.011361 | -0.0020272 | -13.8245 | 64.595 | -57.811 | 64.4943 | -55.4489 | -57.6645 | -57.6324 | -29.7729 | 64.5493 | -57.7148 | 64.5996 | -57.0648 | -57.6965 | -57.5272 | -0.14648 | -0.009155 | -0.10986 | 2.2156 | 0.032044 | 0 | 0.17853 | 0.14648 | -0.050354 | -0.054932 | -0.004578 | 0.59967 | 0.13733 | -0.032043 | 0.18768 | 0.018311 | 2.3621 | 122.3053 | 0.65002 | 122.3145 | 122.406 | 122.2641 | 122.2595 | 122.2137 | -122.4152 | -122.319 | 122.1588 | 122.2641 | 43.84 | 27.8915
1297.3125 | 122.5204 | -57.6462 | 64.65 | -0.065842 | 0.0090298 | 0.065939 | 0.063012 | 0.00098262 | -0.00018376 | 0.00034614 | -0.05188 | 0.0029137 | 0.070147 | 0.063061 | -0.0080408 | 0.010292 | -0.0001046 | -13.4445 | 64.5767 | -57.7698 | 64.5813 | -55.3482 | -57.5821 | -57.5592 | -29.6814 | 64.5584 | -57.6599 | 64.6454 | -56.9733 | -57.6279 | -57.4448 | -0.1236 | -0.073242 | -0.068664 | 2.298 | 0.086975 | 0.064087 | 0.21057 | 0.18768 | -0.013733 | -0.091552 | -0.004577 | 0.67291 | 0.20142 | 0.01831 | 0.21515 | 0.032043 | 2.4216 | 122.3511 | 0.68664 | 122.3053 | 122.3465 | 122.2183 | 122.2229 | 122.2046 | -122.4197 | -122.3099 | 122.2275 | 122.2916 | 44.2017 | 27.9648
1298.3125 | 122.4655 | -57.6599 | 64.6271 | -0.027695 | 0.0071072 | 0.066366 | 0.062158 | 0.00055542 | -0.0018928 | 0.0016277 | -0.042725 | 0.0020593 | 0.066943 | 0.063061 | -0.0074 | 0.011147 | -0.0026682 | -13.2248 | 64.5676 | -57.7652 | 64.5721 | -55.3253 | -57.5958 | -57.5775 | -29.6814 | 64.5584 | -57.6828 | 64.6042 | -56.9962 | -57.6874 | -57.4997 | -0.10529 | -0.059509 | -0.054931 | 2.3346 | 0.082397 | 0.064087 | 0.18768 | 0.16937 | -0.022888 | -0.068664 | -0.022888 | 0.66376 | 0.16022 | -0.027466 | 0.1831 | -0.004578 | 2.4399 | 122.3373 | 0.68664 | 122.287 | 122.3328 | 122.2412 | 122.2275 | 122.2183 | -122.3923 | -122.3099 | 122.2321 | 122.2641 | 44.4351 | 27.9785
1299.3125 | 122.5708 | -57.6828 | 64.5584 | -0.10399 | 0.0088162 | 0.066794 | 0.06109 | 0.00034182 | -0.00082456 | 0.0024823 | -0.01831 | 0.0041955 | 0.068011 | 0.063275 | -0.0069726 | 0.0094379 | -0.0056588 | -12.9501 | 64.5218 | -57.7744 | 64.5584 | -55.307 | -57.6233 | -57.55 | -29.6219 | 64.5264 | -57.692 | 64.6637 | -56.9412 | -57.6187 | -57.4173 | -0.091553 | -0.036621 | 0 | 2.3758 | 0.13275 | 0.059509 | 0.2243 | 0.15106 | -0.009156 | -0.032044 | 0.10528 | 0.74158 | 0.2655 | 0.064087 | 0.27466 | 0.073243 | 2.4673 | 122.3328 | 0.75073 | 122.3557 | 122.2961 | 122.2183 | 122.2046 | 122.2092 | -122.3328 | -122.2504 | 122.2412 | 122.3465 | 44.7327 | 28.0609
1300.3125 | 122.4426 | -57.6828 | 64.6179 | -0.058212 | 0.0045438 | 0.065085 | 0.063867 | -0.00072638 | -0.00061096 | 0.00098694 | -0.045776 | 0.0035547 | 0.06737 | 0.067975 | -0.0076136 | 0.012856 | -0.0020272 | -12.7029 | 64.5584 | -57.8201 | 64.5126 | -55.3116 | -57.6508 | -57.6233 | -29.7043 | 64.5584 | -57.7057 | 64.5584 | -57.0374 | -57.7423 | -57.5363 | -0.13733 | -0.059509 | -0.10529 | 2.3712 | 0.059509 | 0.032043 | 0.19684 | 0.16937 | -0.022888 | -0.059509 | -0.059509 | 0.64545 | 0.14648 | -0.05951 | 0.16937 | -0.036622 | 2.5085 | 122.3328 | 0.66833 | 122.2641 | 122.3785 | 122.2641 | 122.2412 | 122.2412 | -122.438 | -122.3236 | 122.1954 | 122.2412 | 44.9799 | 27.9785
1301.3125 | 122.438 | -57.6965 | 64.6225 | -0.08873 | 0.0086026 | 0.06658 | 0.062372 | 0.002478 | -0.00082456 | 0.00055974 | -0.024414 | 0.0022729 | 0.066302 | 0.063916 | -0.0063318 | 0.01072 | -0.0013864 | -12.4832 | 64.5721 | -57.843 | 64.4577 | -55.3802 | -57.8064 | -57.9758 | -29.4983 | 64.5676 | -57.7057 | 64.5493 | -57.0099 | -57.7469 | -57.5638 | -0.14648 | -0.050354 | -0.16479 | 2.3163 | -0.27924 | -0.10986 | -0.13275 | 0.036622 | -0.009155 | -0.054932 | -0.073243 | 0.68665 | 0.13275 | -0.050354 | 0.14191 | -0.041199 | 2.4628 | 122.3007 | 0.6958 | 122.2549 | 122.4152 | 122.2733 | 122.2687 | 122.2641 | -122.4655 | -122.3282 | 122.1542 | 122.2458 | 45.2133 | 28.1982
1302.3125 | 122.4426 | -57.7148 | 64.5996 | -0.020065 | 0.0073208 | 0.06423 | 0.063226 | 0.0029052 | -0.0014654 | -0.0015765 | -0.027466 | 0.0046227 | 0.06737 | 0.065198 | -0.008468 | 0.01072 | 0.0009634 | -12.291 | 64.5767 | -57.811 | 64.5035 | -55.275 | -57.6462 | -57.6004 | -29.5807 | 64.5218 | -57.6828 | 64.5676 | -56.9824 | -57.724 | -57.5363 | -0.09613 | -0.022888 | -0.09613 | 2.4399 | 0.11444 | 0.068665 | 0.21057 | 0.1648 | 0.032044 | -0.077819 | -0.032043 | 0.73242 | 0.17853 | -0.009155 | 0.14648 | -0.041199 | 2.536 | 122.3145 | 0.70038 | 122.2504 | 122.3877 | 122.2046 | 122.2916 | 122.2366 | -122.4106 | -122.2824 | 122.2183 | 122.2824 | 45.4239 | 28.1342
1303.3125 | 122.4838 | -57.7011 | 64.6317 | -0.073471 | 0.0081754 | 0.064871 | 0.061944 | 0.0016236 | -0.0025336 | 0.0024823 | -0.01831 | 0.0050501 | 0.069079 | 0.060284 | -0.0071864 | 0.010079 | 0.0016044 | -12.0804 | 64.5447 | -57.8339 | 64.4943 | -55.2612 | -57.6645 | -57.6233 | -29.5029 | 64.5264 | -57.7103 | 64.5493 | -56.9962 | -57.7286 | -57.5363 | -0.13275 | -0.086975 | -0.13733 | 2.4399 | 0.07782 | 0.036621 | 0.21057 | 0.16937 | -0.009155 | -0.10529 | -0.082398 | 0.70496 | 0.16479 | -0.027466 | 0.17395 | -0.018311 | 2.5726 | 122.3282 | 0.71411 | 122.2595 | 122.3785 | 122.2366 | 122.2458 | 122.2275 | -122.4655 | -122.3419 | 122.1954 | 122.2504 | 45.6207 | 28.1982
1304.3125 | 122.5662 | -57.6828 | 64.5584 | -0.096359 | 0.0060392 | 0.067221 | 0.060449 | 0.00098262 | -0.00082456 | 0.00034614 | -0.027466 | 0.0027001 | 0.06737 | 0.055585 | -0.0059046 | 0.012429 | -0.0054452 | -11.9522 | 64.5218 | -57.8293 | 64.4989 | -55.2246 | -57.6462 | -57.6004 | -29.3655 | 64.4623 | -57.7057 | 64.6225 | -56.9 | -57.6553 | -57.4539 | -0.14648 | -0.036621 | -0.05951 | 2.4582 | 0.082397 | 0.036621 | 0.22888 | 0.18311 | -0.022888 | -0.096131 | 0.064087 | 0.78278 | 0.22888 | 0.027466 | 0.25177 | 0.050354 | 2.6047 | 122.3282 | 0.80566 | 122.3282 | 122.3511 | 122.168 | 122.2046 | 122.1451 | -122.3877 | -122.2641 | 122.1817 | 122.3053 | 45.7306 | 28.3173
1305.3125 | 122.5113 | -57.7057 | 64.5813 | -0.058212 | 0.0071072 | 0.068716 | 0.062799 | 0.0020508 | -0.00082456 | 0.00055974 | -0.054932 | 0.0029137 | 0.069079 | 0.062421 | -0.0078272 | 0.012429 | -0.0001046 | -11.6409 | 64.5493 | -57.7881 | 64.5355 | -55.1514 | -57.605 | -57.5867 | -29.2557 | 64.4989 | -57.7103 | 64.5905 | -56.8954 | -57.692 | -57.5089 | -0.082398 | -0.032044 | -0.045777 | 2.5543 | 0.11902 | 0.10071 | 0.20142 | 0.18311 | -0.004578 | -0.082398 | 0.009155 | 0.81024 | 0.19684 | 0.013732 | 0.20142 | 0.01831 | 2.6367 | 122.3236 | 0.81482 | 122.3007 | 122.3373 | 122.2092 | 122.2549 | 122.2046 | -122.3694 | -122.2916 | 122.2412 | 122.2961 | 46.0648 | 28.45
1306.3125 | 122.5525 | -57.7194 | 64.5172 | -0.065842 | 0.009457 | 0.065939 | 0.061731 | 0.00034182 | 0.002166 | 0.0026959 | -0.033569 | 0.0033411 | 0.067157 | 0.063489 | -0.0078272 | 0.010933 | -0.0020272 | -11.499 | 64.5264 | -57.8705 | 64.4669 | -55.188 | -57.6599 | -57.6096 | -29.2099 | 64.4623 | -57.7652 | 64.5859 | -56.9 | -57.692 | -57.4814 | -0.15106 | 0.009155 | -0.050354 | 2.5314 | 0.10986 | 0.059509 | 0.26093 | 0.21057 | -0.045777 | -0.054932 | 0.068664 | 0.8194 | 0.23804 | 0.027465 | 0.28381 | 0.073242 | 2.6825 | 122.3373 | 0.86517 | 122.3511 | 122.3969 | 122.2275 | 122.2458 | 122.1817 | -122.3877 | -122.2824 | 122.1863 | 122.3053 | 46.2204 | 28.5095
1307.3125 | 122.4976 | -57.7286 | 64.5721 | -0.012436 | 0.0079618 | 0.067221 | 0.061303 | -0.0011536 | -0.00082456 | -8.1264e-05 | -0.039673 | 0.0054773 | 0.067798 | 0.05943 | -0.0086816 | 0.011574 | -0.0039498 | -11.3068 | 64.5401 | -57.8201 | 64.5172 | -55.1056 | -57.6004 | -57.5821 | -28.9993 | 64.4714 | -57.7423 | 64.5767 | -56.8771 | -57.692 | -57.5089 | -0.091552 | -0.032044 | -0.054932 | 2.623 | 0.14648 | 0.12817 | 0.23804 | 0.21973 | -0.013733 | -0.10071 | 0.004577 | 0.85144 | 0.21973 | 0.036621 | 0.23346 | 0.050354 | 2.7145 | 122.3373 | 0.86517 | 122.319 | 122.3602 | 122.2137 | 122.2687 | 122.2 | -122.3923 | -122.3145 | 122.2458 | 122.3053 | 46.4218 | 28.7292
1308.3125 | 122.4976 | -57.7515 | 64.5721 | -0.065842 | 0.0081754 | 0.067007 | 0.062585 | -0.00072638 | -0.00061096 | 0.0016277 | -0.024414 | 0.0059045 | 0.066729 | 0.053235 | -0.0041956 | 0.011788 | 0.0024588 | -11.2289 | 64.5081 | -57.8522 | 64.4394 | -55.22 | -57.7286 | -57.6736 | -28.9581 | 64.4485 | -57.7515 | 64.4897 | -56.9412 | -57.7698 | -57.5638 | -0.10071 | -0.064087 | -0.13275 | 2.5314 | 0.07782 | 0.022888 | 0.17853 | 0.1236 | 0 | -0.1236 | -0.082398 | 0.81024 | 0.18768 | -0.01831 | 0.18768 | -0.01831 | 2.6321 | 122.2916 | 0.81024 | 122.2412 | 122.3602 | 122.2 | 122.2595 | 122.2 | -122.4243 | -122.3236 | 122.1909 | 122.2412 | 46.5225 | 28.7933
1309.3125 | 122.525 | -57.6874 | 64.5172 | -0.096359 | 0.0073208 | 0.069143 | 0.060449 | 0.00012822 | -0.0029608 | 0.0018413 | -0.012207 | 0.0037683 | 0.068225 | 0.053876 | -0.0074 | 0.013497 | -0.0020272 | -11.0092 | 64.4531 | -57.8567 | 64.5172 | -55.0827 | -57.5958 | -57.55 | -28.6423 | 64.4028 | -57.7286 | 64.5126 | -56.6254 | -57.4356 | -57.3532 | -0.16937 | -0.064087 | 0 | 2.6047 | 0.13733 | 0.091553 | 0.3067 | 0.26093 | -0.041199 | -0.11444 | -0.004578 | 1.062 | 0.33417 | 0.25177 | 0.37537 | 0.29297 | 2.774 | 122.374 | 1.1032 | 122.2412 | 122.3099 | 122.1313 | 122.1405 | 122.0901 | -122.374 | -122.2458 | 122.2046 | 122.2 | 46.6782 | 29.0451
1310.3125 | 122.4838 | -57.7194 | 64.5538 | -0.08873 | 0.0092434 | 0.066366 | 0.061517 | -0.00029898 | 0.00088444 | 0.0014141 | -0.048828 | 0.0044091 | 0.065448 | 0.06413 | -0.009109 | 0.010506 | -0.0003182 | -10.849 | 64.5355 | -57.843 | 64.4714 | -55.0919 | -57.6416 | -57.605 | -28.569 | 64.4943 | -57.7469 | 64.5309 | -56.8542 | -57.7286 | -57.5363 | -0.1236 | -0.018311 | -0.082397 | 2.6276 | 0.11444 | 0.077819 | 0.23804 | 0.20142 | -0.027466 | -0.059509 | -0.022888 | 0.86517 | 0.1831 | -0.009156 | 0.21057 | 0.01831 | 2.7512 | 122.3145 | 0.89264 | 122.2778 | 122.3785 | 122.2412 | 122.2549 | 122.2137 | -122.3969 | -122.3007 | 122.1909 | 122.2504 | 46.8704 | 29.1504
1311.3125 | 122.4426 | -57.724 | 64.5676 | -0.08873 | 0.0088162 | 0.06658 | 0.063012 | 0.00034182 | -0.00061096 | 0.00098694 | -0.048828 | 0.0050501 | 0.068866 | 0.060284 | -0.0082544 | 0.01072 | -0.0022408 | -10.7574 | 64.5035 | -57.8751 | 64.4394 | -55.1239 | -57.6828 | -57.6599 | -28.5141 | 64.4806 | -57.7469 | 64.476 | -56.9138 | -57.7744 | -57.5729 | -0.15106 | -0.064087 | -0.12817 | 2.6001 | 0.064087 | 0.041199 | 0.21515 | 0.19226 | -0.022888 | -0.086975 | -0.091553 | 0.81024 | 0.15106 | -0.050354 | 0.17395 | -0.027466 | 2.7512 | 122.3145 | 0.83313 | 122.2229 | 122.3785 | 122.2275 | 122.2275 | 122.2046 | -122.4426 | -122.3145 | 122.1634 | 122.2 | 46.9666 | 29.2099
1312.3125 | 122.4701 | -57.7744 | 64.5401 | -0.08873 | 0.0075344 | 0.068289 | 0.061731 | -0.0015808 | -0.0021064 | 0.0041913 | -0.01831 | 0.0052637 | 0.069293 | 0.053021 | -0.005691 | 0.01307 | -0.0024546 | -10.9131 | 64.4348 | -57.9346 | 64.4531 | -55.069 | -57.7652 | -57.6553 | -28.2944 | 64.4714 | -57.7789 | 64.4897 | -56.8359 | -57.7698 | -57.5638 | -0.16022 | -0.10529 | -0.086975 | 2.7054 | 0.11902 | 0.009155 | 0.27924 | 0.16937 | -0.004578 | -0.068664 | -0.050354 | 0.93842 | 0.21057 | 0.004578 | 0.21515 | 0.009156 | 2.8656 | 122.3877 | 0.94299 | 122.2687 | 122.3694 | 122.2504 | 122.2092 | 122.2458 | -122.4747 | -122.319 | 122.2275 | 122.2641 | 46.8613 | 29.48
1313.3125 | 122.5662 | -57.7103 | 64.5218 | -0.058212 | 0.0073208 | 0.067007 | 0.062372 | -0.00093998 | 0.00024344 | 0.0022687 | -0.015259 | 0.0035547 | 0.064593 | 0.063916 | -0.0065454 | 0.012215 | -0.0007456 | -10.5743 | 64.4989 | -57.8476 | 64.4989 | -55.0003 | -57.605 | -57.5775 | -27.919 | 64.4028 | -57.7744 | 64.5996 | -56.6849 | -57.6553 | -57.4448 | -0.13733 | -0.022889 | -0.022889 | 2.71 | 0.13275 | 0.10529 | 0.27008 | 0.24262 | -0.064087 | -0.11902 | 0.077819 | 1.0254 | 0.2655 | 0.054932 | 0.32959 | 0.11902 | 2.8473 | 122.3465 | 1.0895 | 122.374 | 122.3465 | 122.1771 | 122.2092 | 122.113 | -122.3694 | -122.2961 | 122.2092 | 122.3099 | 47.1359 | 29.7913
1314.3125 | 122.438 | -57.7515 | 64.5493 | -0.073471 | 0.008389 | 0.068075 | 0.062799 | -0.0028626 | -0.00039736 | 0.0024823 | -0.045776 | 0.0037683 | 0.066729 | 0.070538 | -0.0080408 | 0.013283 | -0.0024546 | -10.4919 | 64.5035 | -57.8613 | 64.4577 | -55.069 | -57.692 | -57.6416 | -27.8229 | 64.4897 | -57.7698 | 64.4989 | -56.781 | -57.7744 | -57.5546 | -0.10986 | -0.045776 | -0.091552 | 2.6825 | 0.10986 | 0.059509 | 0.21973 | 0.16937 | -0.01831 | -0.059509 | -0.050354 | 0.97046 | 0.19684 | -0.022888 | 0.21515 | -0.004578 | 2.7924 | 122.319 | 0.98877 | 122.2687 | 122.3648 | 122.2595 | 122.2549 | 122.2412 | -122.4106 | -122.319 | 122.2092 | 122.2504 | 47.2595 | 29.9286
1315.3125 | 122.4792 | -57.7515 | 64.5172 | -0.10399 | 0.0060392 | 0.066794 | 0.061731 | -0.0013672 | -0.0010382 | -0.0011493 | -0.030517 | 0.0069727 | 0.067798 | 0.056226 | -0.0082544 | 0.010933 | 0.0013906 | -10.4553 | 64.4989 | -57.8567 | 64.4302 | -55.0461 | -57.692 | -57.6508 | -27.4567 | 64.4531 | -57.7789 | 64.5081 | -56.7398 | -57.7332 | -57.518 | -0.10528 | -0.018311 | -0.086975 | 2.7054 | 0.10071 | 0.059509 | 0.20599 | 0.16479 | -0.027466 | -0.064087 | -0.009155 | 1.0117 | 0.23346 | 0.018311 | 0.26093 | 0.045777 | 2.8107 | 122.287 | 1.0391 | 122.287 | 122.3557 | 122.2321 | 122.2504 | 122.2046 | -122.374 | -122.2961 | 122.1817 | 122.2595 | 47.2961 | 30.2948
1316.3125 | 122.58 | -57.7286 | 64.5035 | -0.08873 | 0.0092434 | 0.068716 | 0.059808 | -0.00029898 | -0.0027472 | -0.0028583 | 0.024414 | 0.0039819 | 0.063525 | 0.061993 | -0.0086816 | 0.011147 | -0.0007456 | -10.2768 | 64.4394 | -57.8705 | 64.4669 | -54.9225 | -57.5134 | -57.518 | -26.9897 | 64.3936 | -57.7377 | 64.6088 | -56.6162 | -57.6096 | -57.4265 | -0.14191 | -0.064087 | -0.036621 | 2.8061 | 0.21057 | 0.21515 | 0.35248 | 0.35706 | -0.009155 | -0.10986 | 0.10529 | 1.1124 | 0.30212 | 0.11902 | 0.31128 | 0.12817 | 2.948 | 122.3373 | 1.1215 | 122.3465 | 122.3099 | 122.1313 | 122.168 | 122.1222 | -122.374 | -122.2412 | 122.1954 | 122.3373 | 47.4518 | 30.7388
1317.3125 | 122.4289 | -57.7744 | 64.5676 | -0.096359 | 0.0092434 | 0.064871 | 0.063653 | 0.004187 | -0.0025336 | 0.0022687 | -0.061035 | 0.0052637 | 0.068011 | 0.056439 | -0.0086816 | 0.010506 | -0.0009592 | -10.2631 | 64.5081 | -57.8751 | 64.444 | -54.9957 | -57.6553 | -57.637 | -26.8616 | 64.4897 | -57.7698 | 64.4897 | -56.7215 | -57.7606 | -57.5409 | -0.10071 | -0.059509 | -0.1236 | 2.7786 | 0.13733 | 0.11902 | 0.23804 | 0.21973 | 0.004578 | -0.07782 | -0.07782 | 1.0529 | 0.23346 | 0.013733 | 0.22888 | 0.009155 | 2.8793 | 122.319 | 1.0483 | 122.2595 | 122.3831 | 122.2595 | 122.2824 | 122.2641 | -122.4426 | -122.3373 | 122.2183 | 122.2641 | 47.5113 | 30.9128
1318.3125 | 122.4564 | -57.7789 | 64.5447 | -0.081101 | 0.011166 | 0.067221 | 0.064081 | 0.0029052 | 2.9842e-05 | 0.0031231 | 0.027466 | 0.0029137 | 0.064807 | 0.062634 | -0.009109 | 0.012642 | -0.0037362 | -10.2722 | 64.4897 | -57.9071 | 64.389 | -55.0735 | -57.9483 | -57.962 | -26.3763 | 64.4852 | -57.7881 | 64.4577 | -56.7078 | -57.7789 | -57.5729 | -0.12817 | -0.054932 | -0.15564 | 2.7054 | -0.1831 | -0.16937 | -0.054932 | -0.041199 | -0.009155 | -0.05951 | -0.086975 | 1.0712 | 0.20599 | 0 | 0.21515 | 0.009155 | 2.8336 | 122.2961 | 1.0803 | 122.2458 | 122.3969 | 122.2733 | 122.2687 | 122.2641 | -122.4518 | -122.3328 | 122.168 | 122.2366 | 47.5067 | 31.4026
1319.3125 | 122.5525 | -57.7332 | 64.5218 | -0.11925 | 0.0081754 | 0.066153 | 0.062158 | -0.00093998 | 0.0023798 | 0.0012005 | 0.030518 | 0.0024865 | 0.067157 | 0.056439 | -0.0082544 | 0.011147 | 0.0007498 | -10.1807 | 64.476 | -57.8522 | 64.4669 | -54.9042 | -57.6141 | -57.5546 | -25.9872 | 64.4211 | -57.7652 | 64.5447 | -56.5933 | -57.6462 | -57.4722 | -0.11902 | -0.045777 | -0.054932 | 2.829 | 0.17853 | 0.11902 | 0.29755 | 0.23804 | -0.032044 | -0.10071 | 0.022888 | 1.1398 | 0.26093 | 0.086975 | 0.29297 | 0.11902 | 2.948 | 122.319 | 1.1719 | 122.3099 | 122.3282 | 122.1863 | 122.2092 | 122.1542 | -122.374 | -122.287 | 122.2 | 122.2778 | 47.5525 | 31.7459
1320.3125 | 122.4976 | -57.7698 | 64.5081 | -0.065842 | 0.0088162 | 0.067007 | 0.062158 | 0.002478 | -0.0031744 | 0.0022687 | -0.042725 | 0.0048363 | 0.066943 | 0.063702 | -0.0076136 | 0.01371 | -0.0018136 | -10.1852 | 64.4852 | -57.8979 | 64.4073 | -54.9911 | -57.7011 | -57.6553 | -25.621 | 64.4348 | -57.7835 | 64.5035 | -56.6345 | -57.7377 | -57.5134 | -0.12817 | -0.022889 | -0.10071 | 2.7786 | 0.11444 | 0.068664 | 0.24261 | 0.19684 | -0.013733 | -0.073243 | -0.004578 | 1.1353 | 0.25635 | 0.032043 | 0.27008 | 0.045776 | 2.9068 | 122.3053 | 1.149 | 122.287 | 122.3831 | 122.2183 | 122.2549 | 122.2046 | -122.406 | -122.2916 | 122.1771 | 122.2733 | 47.5845 | 32.1487
1321.3125 | 122.5708 | -57.7377 | 64.5218 | -0.096359 | 0.0071072 | 0.067434 | 0.063867 | 0.0018372 | 0.0013116 | 0.0029095 | 0.0091553 | 0.0035547 | 0.069507 | 0.059003 | -0.0065454 | 0.010933 | 0.001177 | -10.0983 | 64.4577 | -57.8751 | 64.4852 | -54.895 | -57.637 | -57.5912 | -25.2365 | 64.4119 | -57.7835 | 64.5676 | -56.4835 | -57.6599 | -57.4448 | -0.13733 | -0.064087 | -0.036622 | 2.8427 | 0.14648 | 0.10071 | 0.28381 | 0.23804 | -0.045776 | -0.10986 | 0.045776 | 1.2543 | 0.29297 | 0.07782 | 0.33874 | 0.1236 | 2.98 | 122.3602 | 1.3 | 122.3511 | 122.3328 | 122.1954 | 122.1954 | 122.1497 | -122.3969 | -122.3053 | 122.2229 | 122.3053 | 47.6395 | 32.5012
1322.3125 | 122.58 | -57.7606 | 64.4897 | -0.081101 | 0.0075344 | 0.068503 | 0.061731 | 0.00034182 | -0.0014654 | 0.0024823 | -0.0091553 | 0.0033411 | 0.065234 | 0.059644 | -0.0078272 | 0.01072 | 0.0009634 | -9.9655 | 64.4073 | -57.8979 | 64.4943 | -54.8538 | -57.518 | -57.5134 | -24.939 | 64.4119 | -57.7515 | 64.5813 | -56.4377 | -57.6233 | -57.4402 | -0.13733 | -0.082397 | 0.004578 | 2.9068 | 0.24719 | 0.24262 | 0.38452 | 0.37994 | 0.009155 | -0.07782 | 0.091553 | 1.3229 | 0.32043 | 0.13733 | 0.31128 | 0.12817 | 3.0441 | 122.3923 | 1.3138 | 122.3328 | 122.3053 | 122.1634 | 122.168 | 122.1725 | -122.3877 | -122.2412 | 122.2549 | 122.3419 | 47.7951 | 32.8217
1323.3125 | 122.4701 | -57.7652 | 64.5126 | -0.065842 | 0.0073208 | 0.064871 | 0.064081 | 0.0020508 | -0.00039736 | -0.00029486 | -0.021362 | 0.0052637 | 0.06972 | 0.062207 | -0.0074 | 0.010079 | 0.002886 | -10.0479 | 64.4714 | -57.8979 | 64.3982 | -54.9316 | -57.7011 | -57.6416 | -24.8108 | 64.4348 | -57.7972 | 64.4989 | -56.5338 | -57.7377 | -57.5272 | -0.13275 | -0.041198 | -0.11444 | 2.8336 | 0.1236 | 0.064087 | 0.25635 | 0.19684 | -0.032043 | -0.07782 | -0.013733 | 1.2314 | 0.23804 | 0.027466 | 0.27008 | 0.059509 | 2.9663 | 122.2961 | 1.2634 | 122.2961 | 122.3694 | 122.2321 | 122.2366 | 122.2 | -122.4106 | -122.3099 | 122.1634 | 122.2641 | 47.7173 | 32.9544
1324.3125 | 122.5296 | -57.7469 | 64.4943 | -0.14214 | 0.009457 | 0.066794 | 0.060235 | -0.003717 | -0.00018376 | -0.0026447 | 0.036621 | 0.0031273 | 0.066943 | 0.053235 | -0.0082544 | 0.012001 | -0.0028818 | -10.0571 | 64.444 | -57.8751 | 64.4669 | -54.8538 | -57.5912 | -57.5363 | -24.5178 | 64.4165 | -57.7835 | 64.5309 | -56.4102 | -57.6096 | -57.4539 | -0.12817 | -0.050354 | -0.027466 | 2.8931 | 0.21057 | 0.15564 | 0.33875 | 0.28381 | -0.036621 | -0.07782 | 0.036621 | 1.3367 | 0.29297 | 0.13733 | 0.32959 | 0.17395 | 3.0212 | 122.3419 | 1.3733 | 122.3145 | 122.319 | 122.2 | 122.1909 | 122.1634 | -122.3694 | -122.2778 | 122.2137 | 122.2778 | 47.6898 | 33.2291
1325.3125 | 122.4518 | -57.7789 | 64.5081 | -0.073471 | 0.0092434 | 0.067434 | 0.063867 | -0.003717 | -0.0010382 | 0.0031231 | -0.088501 | 0.0054773 | 0.065448 | 0.058148 | -0.0082544 | 0.012215 | -0.0013864 | -10.0433 | 64.4531 | -57.9025 | 64.2288 | -55.2292 | -57.5317 | -57.3624 | -24.2294 | 64.4485 | -57.7789 | 64.4485 | -56.5292 | -57.7606 | -57.5363 | -0.1236 | -0.054932 | -0.27924 | 2.5497 | 0.41656 | 0.24719 | 0.54016 | 0.37079 | 0 | -0.05951 | -0.05951 | 1.2497 | 0.24262 | 0.018311 | 0.24262 | 0.018311 | 2.6733 | 122.1313 | 1.2497 | 122.2275 | 122.3557 | 122.2275 | 122.2321 | 122.2275 | -122.4106 | -122.287 | 122.0078 | 122.2275 | 47.7356 | 33.5495
1326.3125 | 122.4884 | -57.7789 | 64.4852 | -0.10399 | 0.0079618 | 0.066794 | 0.060876 | 0.0031188 | -0.0012518 | -0.00029486 | -0.05188 | 0.0071863 | 0.068438 | 0.056866 | -0.0063318 | 0.010933 | -0.0003182 | -9.9747 | 64.4531 | -57.9071 | 64.3936 | -54.8813 | -57.692 | -57.637 | -23.8358 | 64.4073 | -57.811 | 64.5035 | -56.4239 | -57.7148 | -57.518 | -0.12817 | -0.032043 | -0.091552 | 2.8976 | 0.14191 | 0.086975 | 0.27008 | 0.21515 | -0.032043 | -0.077819 | 0.018311 | 1.355 | 0.26093 | 0.064087 | 0.29297 | 0.09613 | 3.0258 | 122.3007 | 1.387 | 122.3145 | 122.3602 | 122.2183 | 122.2321 | 122.1863 | -122.3923 | -122.2961 | 122.1725 | 122.2824 | 47.8043 | 33.9432
1327.3125 | 122.5204 | -57.7744 | 64.4897 | -0.13451 | 0.0090298 | 0.066794 | 0.064508 | -0.0022218 | 0.00024344 | 0.0033367 | -0.048828 | 0.0056909 | 0.066302 | 0.060071 | -0.0071864 | 0.010933 | 0.0022452 | -10.0021 | 64.4714 | -57.9025 | 64.4211 | -54.8767 | -57.6828 | -57.6462 | -23.5016 | 64.4348 | -57.8156 | 64.4897 | -56.3828 | -57.7148 | -57.4997 | -0.12817 | -0.01831 | -0.068664 | 2.8976 | 0.12817 | 0.091553 | 0.25635 | 0.21973 | -0.041199 | -0.054932 | 0 | 1.3916 | 0.27466 | 0.059509 | 0.31586 | 0.10071 | 3.0258 | 122.3236 | 1.4328 | 122.3053 | 122.374 | 122.2504 | 122.2458 | 122.2092 | -122.3923 | -122.3053 | 122.1954 | 122.2641 | 47.7722 | 34.2728
1328.3125 | 122.5525 | -57.7423 | 64.4669 | -0.042954 | 0.0075344 | 0.068716 | 0.062585 | -0.0013672 | -0.00061096 | 0.0024823 | -0.039673 | 0.0024865 | 0.06502 | 0.063061 | -0.008468 | 0.012001 | -0.0011728 | -9.9792 | 64.4348 | -57.8796 | 64.4897 | -54.7531 | -57.6187 | -57.5638 | -23.1262 | 64.3936 | -57.7698 | 64.5767 | -56.2637 | -57.6187 | -57.4173 | -0.13733 | -0.032044 | 0.022888 | 2.9892 | 0.17853 | 0.1236 | 0.31586 | 0.26093 | -0.027465 | -0.073242 | 0.10986 | 1.4786 | 0.32501 | 0.1236 | 0.35248 | 0.15106 | 3.1265 | 122.3694 | 1.506 | 122.3465 | 122.3145 | 122.1634 | 122.1771 | 122.1359 | -122.3465 | -122.2366 | 122.2321 | 122.319 | 47.7631 | 34.6161
1329.3125 | 122.525 | -57.7698 | 64.4714 | -0.096359 | 0.0077482 | 0.065939 | 0.061944 | -0.0039306 | -0.00082456 | 0.0031231 | 0.024414 | 0.0037683 | 0.067157 | 0.063489 | -0.0095362 | 0.010079 | 0.0005362 | -9.8145 | 64.4577 | -57.8751 | 64.4485 | -54.7668 | -57.5958 | -57.55 | -22.8516 | 64.389 | -57.7744 | 64.5859 | -56.4011 | -57.637 | -57.4356 | -0.10529 | -0.013733 | -0.022889 | 3.0029 | 0.21973 | 0.17395 | 0.32501 | 0.27924 | -0.004578 | -0.082398 | 0.11444 | 1.3687 | 0.33417 | 0.13275 | 0.33874 | 0.13733 | 3.1082 | 122.3236 | 1.3733 | 122.3602 | 122.3328 | 122.1634 | 122.2275 | 122.1588 | -122.3465 | -122.2458 | 122.2183 | 122.3557 | 47.9553 | 34.9182
1330.3125 | 122.5113 | -57.8156 | 64.4531 | -0.10399 | 0.0086026 | 0.068503 | 0.063653 | -0.00029898 | 2.9842e-05 | -0.0030719 | -0.045776 | 0.0044091 | 0.068225 | 0.059644 | -0.0078272 | 0.010933 | 0.001177 | -9.8465 | 64.4073 | -57.9849 | 64.3753 | -54.8813 | -57.7194 | -57.6508 | -22.554 | 64.3753 | -57.8293 | 64.4531 | -56.3095 | -57.7194 | -57.5089 | -0.16937 | -0.045776 | -0.07782 | 2.9343 | 0.16479 | 0.096131 | 0.33417 | 0.2655 | -0.013733 | -0.07782 | 0 | 1.506 | 0.3067 | 0.096131 | 0.32043 | 0.10986 | 3.1036 | 122.3602 | 1.5198 | 122.2824 | 122.3923 | 122.2046 | 122.2229 | 122.1909 | -122.438 | -122.2824 | 122.1909 | 122.2687 | 47.9691 | 35.2615
1331.3125 | 122.5525 | -57.7835 | 64.4211 | -0.058212 | 0.0096708 | 0.066794 | 0.061944 | 0.0037598 | -0.0018928 | 0.0014141 | -0.024414 | 0.0052637 | 0.068866 | 0.061139 | -0.0088952 | 0.012001 | -0.003309 | -9.8145 | 64.389 | -57.9025 | 64.4806 | -54.7302 | -57.6096 | -57.5546 | -21.9315 | 64.357 | -57.811 | 64.5355 | -56.1859 | -57.6233 | -57.4493 | -0.11902 | -0.032044 | 0.059509 | 3.0533 | 0.22888 | 0.17395 | 0.3479 | 0.29297 | -0.027466 | -0.064087 | 0.11444 | 1.5976 | 0.33417 | 0.16022 | 0.36163 | 0.18768 | 3.1723 | 122.3831 | 1.6251 | 122.3465 | 122.2916 | 122.168 | 122.1725 | 122.1405 | -122.3236 | -122.2321 | 122.2641 | 122.319 | 47.9691 | 35.852
1332.3125 | 122.644 | -57.8156 | 64.4348 | -0.10399 | 0.0088162 | 0.067434 | 0.059595 | 0.002478 | -0.00018376 | 0.0037639 | -0.021362 | 0.0054773 | 0.070147 | 0.062634 | -0.0086816 | 0.012856 | 0.0005362 | -9.8648 | 64.3433 | -57.9163 | 64.4669 | -54.7394 | -57.6187 | -57.5867 | -21.405 | 64.357 | -57.8384 | 64.6133 | -56.2866 | -57.8751 | -57.4448 | -0.10071 | -0.091552 | 0.032044 | 3.0762 | 0.22888 | 0.19684 | 0.32959 | 0.29755 | -0.022888 | -0.077819 | 0.17853 | 1.5289 | 0.37079 | -0.059509 | 0.39368 | -0.036621 | 3.1769 | 122.3831 | 1.5518 | 122.4518 | 122.2595 | 122.1954 | 122.1588 | 122.1725 | -122.3511 | -122.2733 | 122.2824 | 122.4289 | 47.9507 | 36.4105
1333.3125 | 122.525 | -57.8064 | 64.4165 | -0.027695 | 0.010739 | 0.067648 | 0.062585 | 0.0029052 | -0.00039736 | 0.0046185 | -0.012207 | 0.0052637 | 0.068225 | 0.05943 | -0.009109 | 0.011147 | -0.0009592 | -9.9289 | 64.3707 | -57.9117 | 64.4211 | -54.7256 | -57.6416 | -57.5684 | -20.9839 | 64.3524 | -57.8201 | 64.4806 | -56.1493 | -57.6508 | -57.4814 | -0.10529 | -0.045776 | 0.004578 | 3.0807 | 0.23804 | 0.16479 | 0.34332 | 0.27008 | -0.013733 | -0.064087 | 0.064087 | 1.6571 | 0.32501 | 0.15564 | 0.33875 | 0.16937 | 3.186 | 122.3328 | 1.6708 | 122.3007 | 122.2824 | 122.1725 | 122.1771 | 122.1588 | -122.3282 | -122.2366 | 122.2275 | 122.287 | 47.8775 | 36.8225
1334.3125 | 122.5204 | -57.7881 | 64.4302 | -0.081101 | 0.0092434 | 0.068503 | 0.062158 | -0.00051278 | 0.00024344 | 0.00034614 | 0.0030517 | 0.0046227 | 0.068225 | 0.060925 | -0.009109 | 0.010079 | -0.0016 | -9.9838 | 64.3524 | -57.9208 | 64.4302 | -54.7302 | -57.6279 | -57.5821 | -20.5994 | 64.3662 | -57.7881 | 64.4989 | -56.1218 | -57.6508 | -57.486 | -0.13275 | -0.07782 | 0 | 3.0579 | 0.20599 | 0.16022 | 0.33874 | 0.29297 | 0 | -0.064087 | 0.068664 | 1.6663 | 0.30212 | 0.13733 | 0.30212 | 0.13733 | 3.1906 | 122.3511 | 1.6663 | 122.287 | 122.2733 | 122.1542 | 122.1405 | 122.1542 | -122.3511 | -122.2183 | 122.2183 | 122.287 | 47.8043 | 37.1887
1335.3125 | 122.5479 | -57.7972 | 64.4211 | -0.065842 | 0.0090298 | 0.065725 | 0.064721 | -0.0013672 | -0.00018376 | 0.0018413 | -0.045776 | 0.0050501 | 0.067798 | 0.063489 | -0.0074 | 0.013497 | -0.0016 | -9.9976 | 64.357 | -57.9575 | 64.4531 | -54.7211 | -57.6141 | -57.5684 | -20.1691 | 64.3524 | -57.8293 | 64.4394 | -55.8746 | -57.4722 | -57.3807 | -0.16022 | -0.064087 | 0.032043 | 3.0762 | 0.22888 | 0.1831 | 0.3891 | 0.34332 | -0.032044 | -0.068665 | 0.01831 | 1.9226 | 0.41656 | 0.32501 | 0.44861 | 0.35706 | 3.2364 | 122.4106 | 1.9547 | 122.2687 | 122.3145 | 122.1817 | 122.1542 | 122.1497 | -122.3785 | -122.2504 | 122.2504 | 122.2366 | 47.7997 | 37.6282
1336.3125 | 122.525 | -57.8247 | 64.4211 | -0.058212 | 0.0098844 | 0.066153 | 0.062372 | 0.0016236 | 0.00067084 | 0.00034614 | 0.05188 | 0.0065453 | 0.065875 | 0.061352 | -0.0065454 | 0.010506 | -0.0009592 | -9.9609 | 64.3982 | -57.9208 | 64.4028 | -54.7394 | -57.6279 | -57.4631 | -19.9219 | 64.3387 | -57.8293 | 64.4577 | -56.0715 | -57.6782 | -57.486 | -0.09613 | -0.022889 | -0.018311 | 3.0853 | 0.36163 | 0.19684 | 0.45776 | 0.29297 | -0.004578 | -0.082398 | 0.036621 | 1.7532 | 0.33874 | 0.14648 | 0.34332 | 0.15106 | 3.1815 | 122.3236 | 1.7578 | 122.287 | 122.319 | 122.168 | 122.2229 | 122.1634 | -122.3419 | -122.2504 | 122.2275 | 122.2824 | 47.8638 | 37.9028
1337.3125 | 122.5983 | -57.7881 | 64.4211 | -0.073471 | 0.0051846 | 0.068503 | 0.064294 | 0.0020508 | 0.00045724 | 0.0014141 | -0.036621 | 0.0052637 | 0.068652 | 0.065839 | -0.0095362 | 0.0096515 | -0.0026682 | -9.9792 | 64.3662 | -57.9437 | 64.4577 | -54.6844 | -57.6187 | -57.5684 | -19.368 | 64.3478 | -57.8567 | 64.65 | -55.9341 | -57.692 | -57.4722 | -0.15564 | -0.054932 | 0.036621 | 3.1036 | 0.21973 | 0.16937 | 0.37537 | 0.32501 | -0.068664 | -0.073243 | 0.22888 | 1.8539 | 0.31586 | 0.09613 | 0.38452 | 0.16479 | 3.2593 | 122.4014 | 1.9226 | 122.5067 | 122.3099 | 122.2046 | 122.1542 | 122.1359 | -122.3648 | -122.2778 | 122.2458 | 122.438 | 47.8088 | 38.4201
1338.3125 | 122.5479 | -57.7835 | 64.4073 | -0.058212 | 0.008389 | 0.068503 | 0.063012 | 0.0035462 | 0.00045724 | 0.00055974 | -0.039673 | 0.0046227 | 0.067584 | 0.058148 | -0.0093226 | 0.010079 | -0.0001046 | -10.0113 | 64.3707 | -57.9483 | 64.4623 | -54.6341 | -57.6096 | -57.5546 | -18.9697 | 64.3341 | -57.8293 | 64.5081 | -55.9433 | -57.6187 | -57.4448 | -0.1648 | -0.036621 | 0.054931 | 3.1494 | 0.22888 | 0.17395 | 0.39368 | 0.33875 | -0.045777 | -0.073243 | 0.10071 | 1.8402 | 0.33874 | 0.16479 | 0.38452 | 0.21057 | 3.3142 | 122.4106 | 1.886 | 122.3373 | 122.319 | 122.1634 | 122.1542 | 122.1176 | -122.3557 | -122.2366 | 122.2458 | 122.2916 | 47.7722 | 38.8138
1339.3125 | 122.5479 | -57.7927 | 64.4485 | -0.10399 | 0.0096708 | 0.065725 | 0.062585 | 0.00098262 | -0.00039736 | -0.00072206 | 0.012207 | 0.0031273 | 0.068225 | 0.059216 | -0.0088952 | 0.011147 | 0.0013906 | -10.0891 | 64.4073 | -57.9071 | 64.4257 | -54.6616 | -57.605 | -57.5775 | -18.6172 | 64.3616 | -57.8384 | 64.5035 | -55.9067 | -57.6004 | -57.4585 | -0.11444 | -0.041198 | -0.022888 | 3.1311 | 0.21515 | 0.18768 | 0.32959 | 0.30212 | -0.045776 | -0.086975 | 0.054932 | 1.886 | 0.33417 | 0.19226 | 0.37994 | 0.23804 | 3.2455 | 122.3328 | 1.9318 | 122.3419 | 122.3145 | 122.2 | 122.2 | 122.1542 | -122.3557 | -122.287 | 122.2183 | 122.2961 | 47.7036 | 39.1754
1340.3125 | 122.5388 | -57.8018 | 64.4257 | -0.08873 | 0.0079618 | 0.068716 | 0.063012 | -0.0032898 | -0.0010382 | 0.0016277 | -0.030517 | 0.0054773 | 0.065448 | 0.059857 | -0.0069726 | 0.011788 | -0.0013864 | -10.1028 | 64.3662 | -57.9346 | 64.4348 | -54.6249 | -57.605 | -57.5546 | -18.2098 | 64.3341 | -57.8522 | 64.4897 | -55.9067 | -57.6324 | -57.4585 | -0.13275 | -0.059509 | 0.009155 | 3.1769 | 0.24719 | 0.19684 | 0.37994 | 0.32959 | -0.050354 | -0.091553 | 0.064087 | 1.8951 | 0.34332 | 0.16937 | 0.39368 | 0.21973 | 3.3096 | 122.3694 | 1.9455 | 122.3419 | 122.3007 | 122.1863 | 122.168 | 122.1359 | -122.3602 | -122.2778 | 122.2366 | 122.2916 | 47.699 | 39.592
1341.3125 | 122.5388 | -57.8201 | 64.4348 | -0.15739 | 0.0096708 | 0.067007 | 0.062585 | 0.0029052 | 0.00024344 | 0.0026959 | -0.015259 | 0.0071863 | 0.069507 | 0.060498 | -0.0082544 | 0.013497 | 0.0013906 | -10.1257 | 64.3845 | -57.9254 | 64.4531 | -54.6112 | -57.5958 | -57.55 | -17.8391 | 64.3341 | -57.8476 | 64.5035 | -55.8655 | -57.6279 | -57.4493 | -0.10529 | -0.050354 | 0.018311 | 3.2089 | 0.27008 | 0.2243 | 0.37537 | 0.32959 | -0.027466 | -0.10071 | 0.068665 | 1.9547 | 0.37079 | 0.19226 | 0.39825 | 0.21973 | 3.3142 | 122.3785 | 1.9821 | 122.3511 | 122.3099 | 122.1817 | 122.2046 | 122.1542 | -122.3602 | -122.2824 | 122.2733 | 122.3236 | 47.6944 | 39.9811
1342.3125 | 122.5296 | -57.8156 | 64.444 | -0.11162 | 0.008389 | 0.066794 | 0.062158 | 0.00098262 | -0.0029608 | 0.00077334 | 0.0030517 | 0.0063317 | 0.068438 | 0.058575 | -0.0082544 | 0.012215 | -0.0018136 | -10.1578 | 64.3753 | -57.9391 | 64.4119 | -54.6524 | -57.6508 | -57.5912 | -17.5003 | 64.3478 | -57.8476 | 64.476 | -55.8426 | -57.6233 | -57.4493 | -0.1236 | -0.068665 | -0.032044 | 3.1631 | 0.2243 | 0.16479 | 0.3479 | 0.28839 | -0.032043 | -0.096131 | 0.032043 | 1.973 | 0.36621 | 0.19226 | 0.39825 | 0.2243 | 3.2867 | 122.3511 | 2.005 | 122.3236 | 122.3145 | 122.1954 | 122.1909 | 122.1634 | -122.3831 | -122.2916 | 122.2275 | 122.2916 | 47.6578 | 40.3152
1343.3125 | 122.5159 | -57.8156 | 64.4806 | -0.020065 | 0.011166 | 0.066794 | 0.059595 | -0.0052124 | -0.0012518 | 0.0029095 | -0.027466 | 0.0061181 | 0.068438 | 0.066907 | -0.0069726 | 0.010079 | -0.0011728 | -10.144 | 64.3982 | -57.9117 | 64.476 | -54.5746 | -57.5455 | -57.5226 | -17.1066 | 64.3936 | -57.8247 | 64.5035 | -55.7831 | -57.6187 | -57.4448 | -0.09613 | -0.082398 | -0.004578 | 3.241 | 0.29297 | 0.27008 | 0.3891 | 0.36621 | -0.009155 | -0.086975 | 0.022888 | 2.0325 | 0.37079 | 0.19684 | 0.37994 | 0.20599 | 3.3371 | 122.3877 | 2.0416 | 122.3282 | 122.3099 | 122.2183 | 122.2137 | 122.2092 | -122.3923 | -122.3053 | 122.2916 | 122.319 | 47.6715 | 40.7089
1344.3125 | 122.5113 | -57.8201 | 64.444 | -0.096359 | 0.012448 | 0.066366 | 0.061517 | 0.0031188 | -0.0010382 | 0.00098694 | -0.039673 | 0.0067589 | 0.065875 | 0.066693 | -0.0048364 | 0.012429 | -0.0018136 | -10.2539 | 64.357 | -57.9529 | 64.4073 | -54.5975 | -57.6141 | -57.5638 | -16.7908 | 64.3433 | -57.8339 | 64.4714 | -55.7693 | -57.6141 | -57.4631 | -0.13275 | -0.086975 | -0.036621 | 3.2227 | 0.25635 | 0.20599 | 0.3891 | 0.33874 | -0.013733 | -0.10071 | 0.027466 | 2.0508 | 0.35706 | 0.20599 | 0.37079 | 0.21973 | 3.3554 | 122.3602 | 2.0645 | 122.3053 | 122.3099 | 122.1771 | 122.1771 | 122.1634 | -122.3969 | -122.2778 | 122.2275 | 122.2916 | 47.5662 | 41.0294
1345.3125 | 122.5296 | -57.7927 | 64.4394 | -0.08873 | 0.0075344 | 0.067648 | 0.06344 | -0.003717 | -0.0014654 | -0.0017903 | -0.012207 | 0.0048363 | 0.066729 | 0.063061 | -0.0065454 | 0.012215 | -0.0039498 | -10.2859 | 64.3524 | -57.9391 | 64.4302 | -54.57 | -57.6096 | -57.5455 | -16.4658 | 64.3478 | -57.8339 | 64.4852 | -55.7373 | -57.6233 | -57.4677 | -0.14648 | -0.086975 | -0.009155 | 3.2227 | 0.24719 | 0.18311 | 0.39368 | 0.32959 | -0.041198 | -0.091553 | 0.045776 | 2.0554 | 0.32501 | 0.16937 | 0.36621 | 0.21057 | 3.3691 | 122.3694 | 2.0966 | 122.319 | 122.2916 | 122.1817 | 122.1451 | 122.1405 | -122.3785 | -122.2733 | 122.2229 | 122.2778 | 47.5067 | 41.3269
1346.3125 | 122.5021 | -57.8018 | 64.4257 | -0.12688 | 0.0068936 | 0.066794 | 0.061731 | 0.00034182 | -0.00232 | 0.00098694 | -0.0061035 | 0.0071863 | 0.067798 | 0.05943 | -0.0078272 | 0.012215 | -0.0001046 | -10.3271 | 64.3662 | -57.9254 | 64.4165 | -54.57 | -57.5958 | -57.5455 | -16.246 | 64.3616 | -57.8293 | 64.4852 | -55.7556 | -57.5912 | -57.431 | -0.1236 | -0.059509 | -0.009155 | 3.2318 | 0.25635 | 0.20599 | 0.37994 | 0.32959 | -0.027466 | -0.064087 | 0.059509 | 2.0462 | 0.37079 | 0.21057 | 0.39825 | 0.23804 | 3.3554 | 122.3419 | 2.0737 | 122.3145 | 122.2916 | 122.1909 | 122.168 | 122.1634 | -122.3511 | -122.2549 | 122.2183 | 122.287 | 47.4747 | 41.5558
1347.3125 | 122.5616 | -57.811 | 64.4348 | -0.081101 | 0.009457 | 0.069571 | 0.065149 | 0.0029052 | -0.00039736 | 0.0069683 | -0.085449 | 0.0065453 | 0.066943 | 0.063275 | -0.0086816 | 0.012856 | -0.0007456 | -10.3638 | 64.3753 | -57.9712 | 64.444 | -54.5609 | -57.6141 | -57.5592 | -15.9119 | 64.3158 | -57.8339 | 64.5309 | -55.6686 | -57.5912 | -57.399 | -0.16022 | -0.059509 | 0.009156 | 3.2501 | 0.25177 | 0.19684 | 0.41199 | 0.35705 | -0.022888 | -0.11902 | 0.096131 | 2.1423 | 0.41199 | 0.21973 | 0.43488 | 0.24261 | 3.4103 | 122.4152 | 2.1652 | 122.3648 | 122.3465 | 122.1497 | 122.1863 | 122.1268 | -122.406 | -122.2687 | 122.2549 | 122.3419 | 47.4472 | 41.8991
1348.3125 | 122.5616 | -57.8247 | 64.4073 | -0.096359 | 0.008389 | 0.068503 | 0.059167 | -0.00093998 | 0.002166 | -0.00072206 | -0.064087 | 0.0084679 | 0.067157 | 0.060284 | -0.0082544 | 0.01371 | 0.0020316 | -10.4599 | 64.325 | -57.9575 | 64.4669 | -54.451 | -57.5867 | -57.5317 | -15.5869 | 64.3387 | -57.8293 | 64.5309 | -55.5954 | -57.5592 | -57.3944 | -0.13275 | -0.082398 | 0.059509 | 3.3737 | 0.29297 | 0.23804 | 0.42572 | 0.37079 | -0.004578 | -0.068665 | 0.1236 | 2.2293 | 0.4303 | 0.2655 | 0.43488 | 0.27008 | 3.5065 | 122.4243 | 2.2339 | 122.3602 | 122.2824 | 122.168 | 122.1497 | 122.1634 | -122.3648 | -122.2366 | 122.2916 | 122.3557 | 47.3648 | 42.2379
1349.3125 | 122.5662 | -57.7881 | 64.4485 | -0.073471 | 0.0086026 | 0.06658 | 0.061303 | 0.00098262 | 0.00045724 | -0.00029486 | 0.012207 | 0.0059045 | 0.067584 | 0.066693 | -0.0082544 | 0.010292 | 0.0022452 | -10.3821 | 64.4257 | -57.9254 | 64.4531 | -54.4876 | -57.5409 | -57.5089 | -15.3717 | 64.3753 | -57.8156 | 64.5355 | -55.5405 | -57.5272 | -57.3898 | -0.13733 | -0.022888 | 0.004578 | 3.3005 | 0.27924 | 0.24719 | 0.41656 | 0.38452 | -0.027466 | -0.073242 | 0.086975 | 2.2476 | 0.39825 | 0.26093 | 0.42572 | 0.28839 | 3.4378 | 122.3785 | 2.2751 | 122.3511 | 122.3511 | 122.1909 | 122.2137 | 122.1634 | -122.374 | -122.2641 | 122.2412 | 122.3236 | 47.406 | 42.4164
1350.3125 | 122.5662 | -57.8156 | 64.4073 | -0.096359 | 0.0068936 | 0.066366 | 0.063226 | 0.0014098 | 0.00067084 | 0.0041913 | -0.15259 | 0.0050501 | 0.064593 | 0.060071 | -0.0076136 | 0.010933 | -0.0041636 | -10.3958 | 64.3707 | -57.9437 | 64.4485 | -54.4785 | -57.5638 | -57.5455 | -14.946 | 64.3158 | -57.8247 | 64.563 | -55.5405 | -57.5455 | -57.3898 | -0.12817 | -0.036621 | 0.041198 | 3.3371 | 0.27008 | 0.25177 | 0.39825 | 0.37994 | -0.009155 | -0.091553 | 0.15564 | 2.2751 | 0.42572 | 0.27008 | 0.43487 | 0.27924 | 3.4653 | 122.3923 | 2.2842 | 122.3877 | 122.3145 | 122.1405 | 122.1863 | 122.1313 | -122.3511 | -122.2321 | 122.2641 | 122.3785 | 47.4197 | 42.8696
1351.3125 | 122.5616 | -57.7927 | 64.4623 | -0.10399 | 0.008389 | 0.065939 | 0.060663 | -0.0030762 | 2.9842e-05 | 0.0048321 | -0.015259 | 0.0050501 | 0.065448 | 0.05943 | -0.0076136 | 0.0096515 | 0.000109 | -10.4462 | 64.4119 | -57.9117 | 64.444 | -54.4785 | -57.5455 | -57.5317 | -14.9094 | 64.3707 | -57.8156 | 64.5309 | -55.4947 | -57.5226 | -57.3898 | -0.11902 | -0.050354 | -0.01831 | 3.3142 | 0.26093 | 0.24719 | 0.37994 | 0.36621 | -0.022888 | -0.091552 | 0.068665 | 2.298 | 0.40283 | 0.27008 | 0.42572 | 0.29297 | 3.4332 | 122.3557 | 2.3209 | 122.3465 | 122.3236 | 122.1863 | 122.2046 | 122.1634 | -122.374 | -122.2778 | 122.2366 | 122.3236 | 47.3465 | 42.8833
1352.3125 | 122.5525 | -57.8064 | 64.4119 | -0.13451 | 0.0098844 | 0.067221 | 0.063867 | 0.0018372 | 0.00024344 | 0.0022687 | -0.061035 | 0.0080407 | 0.068011 | 0.063489 | -0.008468 | 0.012001 | -0.0022408 | -10.4416 | 64.3662 | -57.9575 | 64.4577 | -54.4418 | -57.5546 | -57.518 | -14.6576 | 64.3478 | -57.8247 | 64.5309 | -55.4947 | -57.5455 | -57.3944 | -0.15106 | -0.045776 | 0.045777 | 3.3646 | 0.28839 | 0.25177 | 0.43945 | 0.40283 | -0.018311 | -0.064087 | 0.11902 | 2.3117 | 0.41199 | 0.26093 | 0.4303 | 0.27924 | 3.5156 | 122.4152 | 2.33 | 122.3557 | 122.3236 | 122.1725 | 122.1725 | 122.1542 | -122.3694 | -122.2366 | 122.2641 | 122.3373 | 47.3648 | 43.1488
1353.3125 | 122.5296 | -57.8156 | 64.4302 | -0.14214 | 0.0092434 | 0.06893 | 0.063653 | -0.0022218 | 0.00067084 | 0.00034614 | -0.045776 | 0.0093225 | 0.068652 | 0.059857 | -0.0059046 | 0.013497 | 0.0022452 | -10.5194 | 64.357 | -57.9437 | 64.444 | -54.4144 | -57.5729 | -57.5317 | -14.4791 | 64.3524 | -57.8156 | 64.5081 | -55.481 | -57.5729 | -57.4127 | -0.12817 | -0.073242 | 0.013733 | 3.4012 | 0.28381 | 0.24261 | 0.41199 | 0.37079 | 0 | -0.07782 | 0.07782 | 2.3346 | 0.40283 | 0.24261 | 0.40283 | 0.24261 | 3.5294 | 122.3877 | 2.3346 | 122.3236 | 122.3007 | 122.168 | 122.1725 | 122.168 | -122.374 | -122.2458 | 122.2595 | 122.3236 | 47.2961 | 43.3365
1354.3125 | 122.5891 | -57.7835 | 64.4257 | -0.10399 | 0.0092434 | 0.067862 | 0.061944 | 0.00076902 | -0.00039736 | 0.0029095 | -0.015259 | 0.0050501 | 0.070575 | 0.062848 | -0.0061182 | 0.013497 | 0.0007498 | -10.5423 | 64.3936 | -57.9208 | 64.4119 | -54.4556 | -57.5729 | -57.5363 | -14.3784 | 64.3707 | -57.8156 | 64.4897 | -55.4764 | -57.4219 | -57.2845 | -0.13733 | -0.032043 | -0.013733 | 3.3279 | 0.24719 | 0.21057 | 0.38452 | 0.3479 | -0.032044 | -0.054931 | 0.064087 | 2.3071 | 0.49896 | 0.36163 | 0.53101 | 0.39368 | 3.4653 | 122.3328 | 2.3392 | 122.3053 | 122.3145 | 122.1863 | 122.1771 | 122.1542 | -122.3465 | -122.2412 | 122.1954 | 122.2733 | 47.2412 | 43.4052
1355.3125 | 122.5662 | -57.811 | 64.3982 | -0.14214 | 0.012021 | 0.068716 | 0.063226 | -0.0015808 | 0.00024344 | 0.0012005 | -0.07019 | 0.0050501 | 0.067157 | 0.064343 | -0.0093226 | 0.012856 | -0.0013864 | -10.5423 | 64.3662 | -57.9208 | 64.5767 | -54.4556 | -57.6004 | -57.486 | -14.1357 | 64.325 | -57.811 | 64.5264 | -55.4077 | -57.5317 | -57.3807 | -0.10986 | -0.032043 | 0.17853 | 3.3554 | 0.32501 | 0.21057 | 0.43487 | 0.32043 | 0 | -0.073242 | 0.12817 | 2.4033 | 0.4303 | 0.27924 | 0.4303 | 0.27924 | 3.4653 | 122.4976 | 2.4033 | 122.3373 | 122.287 | 122.1359 | 122.1771 | 122.1359 | -122.319 | -122.2092 | 122.3877 | 122.3373 | 47.2687 | 43.6752
1356.3125 | 122.5479 | -57.7698 | 64.476 | -0.081101 | 0.0090298 | 0.066153 | 0.065149 | -0.0024354 | 2.9842e-05 | 0.0044049 | 0.0061035 | 0.0076135 | 0.067157 | 0.062207 | -0.006759 | 0.012215 | 0.000109 | -10.6842 | 64.4348 | -57.8842 | 64.4714 | -54.3732 | -57.4997 | -57.4722 | -13.9389 | 64.3936 | -57.7972 | 64.5584 | -55.3528 | -57.4768 | -57.3441 | -0.11444 | -0.041199 | -0.004577 | 3.3966 | 0.29755 | 0.27008 | 0.41199 | 0.38452 | -0.027466 | -0.082397 | 0.082398 | 2.417 | 0.42572 | 0.29297 | 0.45319 | 0.32043 | 3.511 | 122.3557 | 2.4445 | 122.3557 | 122.319 | 122.1909 | 122.2046 | 122.1634 | -122.3602 | -122.2733 | 122.2412 | 122.3282 | 47.0856 | 43.8309
1357.3125 | 122.5067 | -57.8018 | 64.4394 | -0.11925 | 0.010098 | 0.068289 | 0.062799 | -0.0049988 | 2.9842e-05 | 0.0018413 | -0.05188 | 0.0080407 | 0.066089 | 0.067334 | -0.0076136 | 0.01371 | -0.0062998 | -10.675 | 64.3982 | -57.9117 | 64.4348 | -54.3869 | -57.5638 | -57.518 | -13.8153 | 64.3616 | -57.8293 | 64.4943 | -55.4031 | -57.5546 | -57.3853 | -0.10986 | -0.041199 | -0.004578 | 3.4149 | 0.28381 | 0.23804 | 0.39368 | 0.3479 | -0.027466 | -0.07782 | 0.054932 | 2.3987 | 0.41656 | 0.24719 | 0.44403 | 0.27466 | 3.5248 | 122.3465 | 2.4261 | 122.3236 | 122.3099 | 122.1909 | 122.2 | 122.1634 | -122.3511 | -122.2687 | 122.2366 | 122.2961 | 47.1268 | 43.9865
1358.3125 | 122.525 | -57.7972 | 64.4577 | -0.065842 | 0.009457 | 0.06893 | 0.062799 | -0.00072638 | -0.00232 | -0.0011493 | -0.021362 | 0.0088953 | 0.068438 | 0.06178 | -0.0088952 | 0.010506 | -0.0007456 | -10.7391 | 64.4028 | -57.9208 | 64.5859 | -54.5197 | -57.6416 | -57.5043 | -13.6551 | 64.3616 | -57.811 | 64.4943 | -55.3665 | -57.5409 | -57.3807 | -0.1236 | -0.054932 | 0.12817 | 3.2776 | 0.29297 | 0.15564 | 0.41656 | 0.27923 | -0.013733 | -0.096131 | 0.036621 | 2.4307 | 0.41656 | 0.25635 | 0.4303 | 0.27008 | 3.4012 | 122.5067 | 2.4445 | 122.3053 | 122.3236 | 122.1725 | 122.2 | 122.1588 | -122.3785 | -122.2687 | 122.3831 | 122.2916 | 47.0581 | 44.1422
1359.3125 | 122.5342 | -57.7789 | 64.4806 | -0.081101 | 0.0098844 | 0.068075 | 0.061303 | -0.0032898 | -0.00061096 | -0.00029486 | 0.0061035 | 0.0054773 | 0.069293 | 0.063275 | -0.0078272 | 0.011788 | -0.0011728 | -10.849 | 64.444 | -57.8934 | 64.4669 | -54.3503 | -57.4905 | -57.4585 | -13.5361 | 64.4028 | -57.7881 | 64.5493 | -55.275 | -57.4677 | -57.3303 | -0.11444 | -0.036621 | -0.013733 | 3.4286 | 0.32044 | 0.28839 | 0.43488 | 0.40283 | -0.009155 | -0.07782 | 0.068664 | 2.504 | 0.44861 | 0.31128 | 0.45776 | 0.32044 | 3.5431 | 122.3602 | 2.5131 | 122.3373 | 122.3373 | 122.1909 | 122.2229 | 122.1817 | -122.374 | -122.2687 | 122.2458 | 122.3282 | 46.9299 | 44.2429
1360.3125 | 122.5433 | -57.7698 | 64.4623 | -0.08873 | 0.0098844 | 0.068503 | 0.06344 | -0.00051278 | -0.00018376 | 0.0012005 | -0.048828 | 0.0080407 | 0.071216 | 0.060284 | -0.0080408 | 0.011788 | 0.0009634 | -10.8948 | 64.4211 | -57.8842 | 64.4714 | -54.3182 | -57.5226 | -57.486 | -13.4125 | 64.3662 | -57.811 | 64.5218 | -55.3116 | -57.518 | -57.3624 | -0.11444 | -0.041198 | 0.009156 | 3.4515 | 0.28381 | 0.24719 | 0.39825 | 0.36163 | -0.041199 | -0.09613 | 0.05951 | 2.4582 | 0.40741 | 0.25177 | 0.44861 | 0.29297 | 3.566 | 122.3557 | 2.4994 | 122.3328 | 122.3053 | 122.1771 | 122.1909 | 122.1359 | -122.3465 | -122.2733 | 122.2412 | 122.2916 | 46.875 | 44.3573
1361.3125 | 122.5708 | -57.7332 | 64.4989 | -0.058212 | 0.010312 | 0.067434 | 0.062585 | 0.00055542 | -0.00018376 | 0.00077334 | -0.0030517 | 0.0080407 | 0.068866 | 0.063275 | -0.009109 | 0.012215 | 0.0024588 | -10.9497 | 64.4714 | -57.8384 | 64.5309 | -54.2816 | -57.431 | -57.4173 | -13.1927 | 64.4028 | -57.7469 | 64.6179 | -55.1559 | -57.3853 | -57.2708 | -0.10529 | -0.027465 | 0.032044 | 3.4515 | 0.31586 | 0.30212 | 0.42114 | 0.40741 | -0.013733 | -0.09613 | 0.11902 | 2.5772 | 0.46234 | 0.3479 | 0.47607 | 0.36163 | 3.5568 | 122.3694 | 2.5909 | 122.3648 | 122.3099 | 122.1497 | 122.2046 | 122.1359 | -122.3373 | -122.2458 | 122.2641 | 122.3511 | 46.7834 | 44.5404
1362.3125 | 122.5571 | -57.7698 | 64.476 | -0.14214 | 0.010098 | 0.069143 | 0.063653 | 0.0048278 | 2.9842e-05 | 0.0016277 | -0.10376 | 0.0073999 | 0.067798 | 0.057721 | -0.0097498 | 0.01307 | -0.0011728 | -11.0458 | 64.4165 | -57.8659 | 64.5081 | -54.2862 | -57.4722 | -57.4585 | -13.0966 | 64.3845 | -57.7789 | 64.6729 | -55.2841 | -57.4631 | -57.2845 | -0.096131 | -0.059509 | 0.032044 | 3.4836 | 0.31128 | 0.29755 | 0.40741 | 0.39368 | -0.009156 | -0.091553 | 0.19684 | 2.4857 | 0.48523 | 0.3067 | 0.49439 | 0.31586 | 3.5797 | 122.374 | 2.4948 | 122.4518 | 122.2824 | 122.1634 | 122.1863 | 122.1542 | -122.3419 | -122.2549 | 122.2778 | 122.4426 | 46.7239 | 44.6732
1363.3125 | 122.5525 | -57.756 | 64.4531 | -0.081101 | 0.01138 | 0.069143 | 0.062372 | -0.00051278 | -0.00018376 | 0.00055974 | -0.061035 | 0.0071863 | 0.069079 | 0.060925 | -0.0086816 | 0.01307 | 0.000109 | -10.9817 | 64.4028 | -57.8979 | 64.4943 | -54.2587 | -57.4905 | -57.4493 | -13.0188 | 64.3936 | -57.8064 | 64.5584 | -55.1971 | -57.4677 | -57.3349 | -0.14191 | -0.050354 | 0.041199 | 3.4973 | 0.3067 | 0.2655 | 0.44861 | 0.40741 | -0.050354 | -0.059509 | 0.10529 | 2.5589 | 0.42114 | 0.28839 | 0.4715 | 0.33875 | 3.6392 | 122.3923 | 2.6093 | 122.3648 | 122.3007 | 122.2 | 122.1588 | 122.1497 | -122.3511 | -122.2595 | 122.2504 | 122.3145 | 46.7743 | 44.7372
1364.3125 | 122.5479 | -57.7377 | 64.5081 | 0.11726 | 0.008389 | 0.065725 | 0.06344 | 0.00012822 | -0.00039736 | 0.0033367 | -0.0061035 | 0.0065453 | 0.068438 | 0.062207 | -0.010818 | 0.012429 | -0.0043772 | -10.968 | 64.5172 | -57.811 | 64.5447 | -54.1489 | -57.4127 | -57.4173 | -12.8357 | 64.4302 | -57.7606 | 64.6133 | -55.0873 | -57.4081 | -57.2754 | -0.073242 | 0.009155 | 0.036621 | 3.5889 | 0.32044 | 0.32501 | 0.39368 | 0.39825 | -0.022888 | -0.07782 | 0.10529 | 2.6505 | 0.46234 | 0.32959 | 0.48523 | 0.35248 | 3.6621 | 122.3557 | 2.6733 | 122.374 | 122.3282 | 122.1909 | 122.2549 | 122.168 | -122.319 | -122.2687 | 122.2824 | 122.3511 | 46.7697 | 44.902
1365.3125 | 122.5204 | -57.7332 | 64.5081 | -0.08873 | 0.0098844 | 0.06893 | 0.062799 | 0.0022644 | 0.00067084 | 0.0031231 | -0.042725 | 0.0084679 | 0.069934 | 0.060071 | -0.0063318 | 0.012429 | 0.0024588 | -11.1786 | 64.444 | -57.8659 | 64.4806 | -54.2358 | -57.4768 | -57.4493 | -12.8403 | 64.4302 | -57.7698 | 64.5493 | -55.1468 | -57.4493 | -57.3166 | -0.13275 | -0.064087 | -0.027466 | 3.4973 | 0.28381 | 0.25635 | 0.41657 | 0.3891 | -0.036621 | -0.07782 | 0.041198 | 2.5864 | 0.41656 | 0.28381 | 0.45319 | 0.32043 | 3.6301 | 122.3465 | 2.623 | 122.319 | 122.3099 | 122.2 | 122.1771 | 122.1634 | -122.374 | -122.2778 | 122.2137 | 122.2824 | 46.5546 | 44.8929
1366.3281 | 122.4838 | -57.7332 | 64.5447 | -0.042954 | 0.0081754 | 0.065725 | 0.063867 | 0.00076902 | -0.00061096 | 0.00034614 | -0.042725 | 0.0082543 | 0.066516 | 0.072675 | -0.0097498 | 0.014778 | -0.0035226 | -11.2152 | 64.4943 | -57.8613 | 64.4943 | -54.1946 | -57.7148 | -57.5226 | -12.767 | 64.5126 | -57.7469 | 64.5813 | -55.1193 | -57.4768 | -57.3303 | -0.12817 | -0.050354 | -0.050354 | 3.5385 | 0.21057 | 0.01831 | 0.33875 | 0.14648 | -0.013733 | -0.032044 | 0.036621 | 2.6138 | 0.40283 | 0.25635 | 0.41656 | 0.27008 | 3.6667 | 122.3557 | 2.6276 | 122.3282 | 122.3557 | 122.2595 | 122.2275 | 122.2458 | -122.406 | -122.2916 | 122.2275 | 122.3145 | 46.5179 | 44.9661
1367.3125 | 122.5204 | -57.7194 | 64.5355 | -0.035324 | 0.0098844 | 0.066366 | 0.062799 | 0.0031188 | -0.00039736 | 0.0039777 | 0.015259 | 0.0071863 | 0.070575 | 0.060071 | -0.0071864 | 0.011788 | -0.0022408 | -11.3159 | 64.4623 | -57.8567 | 64.4852 | -54.2175 | -57.4402 | -57.4356 | -12.6892 | 64.4211 | -57.7652 | 64.5859 | -55.0644 | -57.4219 | -57.2891 | -0.13733 | -0.073242 | -0.050354 | 3.5019 | 0.28381 | 0.27923 | 0.42114 | 0.41656 | -0.045777 | -0.11444 | 0.050354 | 2.655 | 0.4303 | 0.29755 | 0.47607 | 0.34332 | 3.6392 | 122.3419 | 2.7008 | 122.3511 | 122.319 | 122.1863 | 122.1817 | 122.1405 | -122.3923 | -122.3007 | 122.2046 | 122.3053 | 46.4035 | 45.0302
1368.3125 | 122.5708 | -57.6691 | 64.5264 | -0.081101 | 0.010312 | 0.067434 | 0.062158 | -0.0045716 | 0.00045724 | 0.0016277 | 0.012207 | 0.0084679 | 0.068866 | 0.064557 | -0.008468 | 0.013497 | -0.0018136 | -11.3113 | 64.4852 | -57.8384 | 64.5447 | -54.1306 | -57.3761 | -57.3486 | -12.5427 | 64.4577 | -57.7332 | 64.6179 | -54.982 | -57.3486 | -57.2296 | -0.16937 | -0.041199 | 0.018311 | 3.5385 | 0.32043 | 0.29297 | 0.48981 | 0.46234 | -0.064087 | -0.068664 | 0.091553 | 2.6871 | 0.43945 | 0.32043 | 0.50354 | 0.38452 | 3.7079 | 122.3831 | 2.7512 | 122.3511 | 122.3236 | 122.1909 | 122.1542 | 122.1268 | -122.3648 | -122.2595 | 122.2137 | 122.287 | 46.3577 | 45.1263
1369.3125 | 122.5342 | -57.6782 | 64.5584 | -0.058212 | 0.0081754 | 0.069143 | 0.060876 | -0.0022218 | -0.00061096 | 0.00055974 | -0.015259 | 0.0067589 | 0.068438 | 0.061993 | -0.0095362 | 0.010933 | 0.0003226 | -11.3342 | 64.4806 | -57.8064 | 64.5905 | -54.0665 | -57.3441 | -57.3212 | -12.4603 | 64.4623 | -57.724 | 64.6179 | -54.9637 | -57.3669 | -57.2342 | -0.12817 | -0.07782 | 0.032043 | 3.6118 | 0.35706 | 0.33417 | 0.48523 | 0.46234 | -0.045776 | -0.096131 | 0.059509 | 2.7145 | 0.44403 | 0.31128 | 0.48981 | 0.35706 | 3.7399 | 122.3969 | 2.7603 | 122.3419 | 122.287 | 122.1863 | 122.1588 | 122.1405 | -122.3648 | -122.2824 | 122.2687 | 122.2961 | 46.344 | 45.2179
1370.3125 | 122.5067 | -57.7148 | 64.5493 | -0.081101 | 0.0079618 | 0.067434 | 0.061517 | 0.0016236 | -0.00082456 | 0.0012005 | -0.079346 | 0.0069727 | 0.069293 | 0.063061 | -0.0071864 | 0.010292 | -0.0018136 | -11.4395 | 64.476 | -57.8201 | 64.5172 | -54.1397 | -57.3029 | -57.2479 | -12.5061 | 64.4577 | -57.7652 | 64.563 | -55.0095 | -57.4219 | -57.2617 | -0.10529 | -0.073242 | -0.032043 | 3.5751 | 0.46692 | 0.41199 | 0.5722 | 0.51727 | -0.050354 | -0.091552 | 0.013733 | 2.7054 | 0.45319 | 0.29297 | 0.50354 | 0.34332 | 3.6804 | 122.3373 | 2.7557 | 122.3282 | 122.2961 | 122.2229 | 122.1909 | 122.1725 | -122.3694 | -122.3145 | 122.2321 | 122.2778 | 46.2753 | 45.2087
1371.3125 | 122.5113 | -57.7057 | 64.5264 | -0.058212 | 0.01138 | 0.066794 | 0.064721 | 0.00012822 | -0.0016792 | 0.0029095 | -0.091553 | 0.0067589 | 0.069507 | 0.063916 | -0.009109 | 0.01371 | 0.0009634 | -11.5219 | 64.476 | -57.8659 | 64.5172 | -54.1672 | -57.4677 | -57.4356 | -12.3779 | 64.4577 | -57.7606 | 64.6179 | -54.9866 | -57.4173 | -57.2479 | -0.16022 | -0.050354 | -0.009155 | 3.5385 | 0.27008 | 0.23804 | 0.4303 | 0.39826 | -0.054932 | -0.068664 | 0.091553 | 2.7191 | 0.45776 | 0.28839 | 0.5127 | 0.34332 | 3.6987 | 122.3831 | 2.774 | 122.3785 | 122.3419 | 122.2183 | 122.1817 | 122.1634 | -122.3923 | -122.287 | 122.2229 | 122.3236 | 46.1838 | 45.3278
1372.3125 | 122.5616 | -57.6965 | 64.5538 | -0.11925 | 0.0090298 | 0.06893 | 0.062372 | -0.00051278 | 0.0017388 | 0.0039777 | 0.0091553 | 0.0076135 | 0.069293 | 0.061566 | -0.0078272 | 0.01307 | -0.0001046 | -11.5173 | 64.5218 | -57.8064 | 64.5538 | -54.0619 | -57.3486 | -57.3486 | -12.2635 | 64.4714 | -57.7011 | 64.6454 | -54.8996 | -57.3212 | -57.2113 | -0.10986 | -0.032043 | 0 | 3.6346 | 0.3479 | 0.3479 | 0.45776 | 0.45776 | -0.004578 | -0.082397 | 0.091553 | 2.7969 | 0.48523 | 0.37537 | 0.48981 | 0.37994 | 3.7445 | 122.3602 | 2.8015 | 122.3465 | 122.3282 | 122.1725 | 122.2183 | 122.168 | -122.3602 | -122.2549 | 122.2504 | 122.3419 | 46.1792 | 45.433
1373.3125 | 122.525 | -57.6462 | 64.5721 | -0.11925 | 0.0096708 | 0.069571 | 0.06109 | -0.0013672 | -0.0025336 | 0.0035503 | 0.018311 | 0.0076135 | 0.066943 | 0.059857 | -0.0099634 | 0.015419 | 0.0013906 | -11.5494 | 64.5126 | -57.7835 | 64.6271 | -53.952 | -57.2617 | -57.2479 | -12.1399 | 64.4669 | -57.6828 | 64.5126 | -54.9133 | -57.1838 | -57.1243 | -0.13733 | -0.05951 | 0.054931 | 3.6942 | 0.39825 | 0.38452 | 0.53558 | 0.52185 | -0.036621 | -0.10529 | -0.05951 | 2.7328 | 0.52185 | 0.46234 | 0.55847 | 0.49896 | 3.8315 | 122.4106 | 2.7695 | 122.1954 | 122.2961 | 122.1497 | 122.1588 | 122.113 | -122.3557 | -122.2549 | 122.2733 | 122.1588 | 46.0968 | 45.5063
1374.3125 | 122.5342 | -57.6462 | 64.6179 | -0.073471 | 0.010312 | 0.067434 | 0.062799 | 0.00098262 | 0.00045724 | 0.0012005 | -0.012207 | 0.0082543 | 0.068011 | 0.06477 | -0.0080408 | 0.012429 | 0.0022452 | -11.5997 | 64.5264 | -57.7927 | 64.6179 | -53.9658 | -57.2983 | -57.2983 | -12.149 | 64.4989 | -57.6874 | 64.6545 | -54.8355 | -57.312 | -57.1884 | -0.14649 | -0.091553 | 0 | 3.6804 | 0.3479 | 0.3479 | 0.49439 | 0.49439 | -0.041199 | -0.11902 | 0.036621 | 2.8107 | 0.45776 | 0.33417 | 0.49896 | 0.37537 | 3.8269 | 122.4106 | 2.8519 | 122.3419 | 122.319 | 122.1863 | 122.1725 | 122.1451 | -122.4106 | -122.3053 | 122.2641 | 122.3007 | 46.0464 | 45.4971
1375.3125 | 122.4564 | -57.6965 | 64.65 | -0.050583 | 0.0081754 | 0.069784 | 0.061517 | 0.0011962 | 0.0015252 | 0.0018413 | -0.039673 | 0.0091089 | 0.070147 | 0.061139 | -0.008468 | 0.015206 | 0.0007498 | -11.6455 | 64.5721 | -57.7927 | 64.5538 | -54.0436 | -57.3715 | -57.3395 | -12.1628 | 64.5355 | -57.6736 | 64.5676 | -54.9133 | -57.4036 | -57.28 | -0.096131 | -0.077819 | -0.09613 | 3.653 | 0.35706 | 0.32501 | 0.45319 | 0.42114 | 0.022888 | -0.11444 | -0.082397 | 2.7832 | 0.41657 | 0.29297 | 0.39368 | 0.27008 | 3.7491 | 122.3465 | 2.7603 | 122.2412 | 122.3648 | 122.2092 | 122.2687 | 122.2321 | -122.4426 | -122.3236 | 122.2504 | 122.2641 | 46.051 | 45.5338
1376.3281 | 122.4747 | -57.7103 | 64.5996 | -0.08873 | 0.0096708 | 0.069143 | 0.065576 | -0.00051278 | -0.00039736 | 0.0024823 | -0.10681 | 0.0084679 | 0.068438 | 0.062634 | -0.008468 | 0.014351 | -0.0001046 | -11.7737 | 64.5172 | -57.8201 | 64.476 | -54.1031 | -57.4585 | -57.4265 | -12.2086 | 64.5126 | -57.7148 | 64.5721 | -54.9316 | -57.4448 | -57.2754 | -0.10986 | -0.082397 | -0.1236 | 3.6072 | 0.28381 | 0.25177 | 0.39368 | 0.36163 | -0.004578 | -0.086975 | -0.027465 | 2.7786 | 0.43487 | 0.2655 | 0.43945 | 0.27008 | 3.717 | 122.2961 | 2.7832 | 122.287 | 122.3373 | 122.2275 | 122.2275 | 122.2229 | -122.4197 | -122.3145 | 122.1863 | 122.2824 | 45.9366 | 45.5017
1377.3125 | 122.58 | -57.6187 | 64.6042 | -0.058212 | 0.0047574 | 0.062521 | 0.061303 | -0.002008 | 0.00045724 | 0.0018413 | 0.0091553 | 0.0071863 | 0.068652 | 0.060498 | -0.0061182 | 0.011574 | 0.0003226 | -11.4853 | 64.6133 | -57.7194 | 64.5859 | -53.8834 | -57.2159 | -57.2433 | -11.998 | 64.5126 | -57.6736 | 64.6957 | -54.7302 | -57.2571 | -57.1472 | -0.10071 | 0.009155 | -0.018311 | 3.7354 | 0.37537 | 0.40283 | 0.47607 | 0.50354 | -0.054932 | -0.091553 | 0.091553 | 2.8885 | 0.4715 | 0.36163 | 0.52643 | 0.41656 | 3.8361 | 122.3053 | 2.9434 | 122.3694 | 122.3328 | 122.1863 | 122.2321 | 122.1313 | -122.3236 | -122.2778 | 122.2046 | 122.3145 | 46.1334 | 45.6207
1378.3125 | 122.3969 | -57.6645 | 64.6454 | -0.058212 | 0.010312 | 0.067221 | 0.06344 | 0.0029052 | 0.002807 | 0.0020551 | -0.048828 | 0.0076135 | 0.070147 | 0.063702 | -0.0071864 | 0.01371 | -0.0003182 | -11.8286 | 64.595 | -57.7606 | 64.5447 | -53.9795 | -57.3395 | -57.3395 | -12.1033 | 64.5721 | -57.6965 | 64.563 | -54.5929 | -57.4768 | -57.3715 | -0.09613 | -0.050354 | -0.10071 | 3.685 | 0.32501 | 0.32501 | 0.42114 | 0.42114 | -0.032043 | -0.073242 | -0.082398 | 3.0716 | 0.29297 | 0.18768 | 0.32501 | 0.21973 | 3.7811 | 122.3053 | 3.1036 | 122.2595 | 122.3557 | 122.2687 | 122.2595 | 122.2366 | -122.406 | -122.3419 | 122.2092 | 122.2275 | 45.8359 | 45.5612
1379.3125 | 122.4197 | -57.6782 | 64.6683 | -0.096359 | 0.0098844 | 0.065725 | 0.062585 | 0.00055542 | -0.0010382 | 0.0024823 | -0.030517 | 0.010604 | 0.069079 | 0.061352 | -0.0082544 | 0.012642 | 0.000109 | -11.879 | 64.6179 | -57.7698 | 64.5355 | -53.9795 | -57.3486 | -57.3349 | -12.0758 | 64.5676 | -57.692 | 64.5172 | -54.9088 | -57.2937 | -57.193 | -0.091552 | -0.050354 | -0.13275 | 3.6987 | 0.34332 | 0.32959 | 0.43488 | 0.42114 | -0.013733 | -0.10071 | -0.15106 | 2.7695 | 0.48523 | 0.38452 | 0.49896 | 0.39825 | 3.7903 | 122.3053 | 2.7832 | 122.2092 | 122.3877 | 122.2595 | 122.2961 | 122.2458 | -122.438 | -122.3602 | 122.2137 | 122.1954 | 45.7993 | 45.6024
1380.3125 | 122.5708 | -57.637 | 64.65 | -0.065842 | 0.010525 | 0.067862 | 0.059808 | 0.0016236 | 0.00067084 | 0.0037639 | 0.0061035 | 0.0067589 | 0.071643 | 0.061139 | -0.005691 | 0.013497 | -0.0009592 | -11.8561 | 64.5493 | -57.7286 | 64.6729 | -53.8239 | -57.225 | -57.2205 | -11.9476 | 64.5447 | -57.6553 | 64.7003 | -54.6844 | -57.2525 | -57.1243 | -0.091553 | -0.10071 | 0.022889 | 3.8132 | 0.41656 | 0.41199 | 0.50812 | 0.50354 | -0.01831 | -0.10528 | 0.050354 | 2.9526 | 0.51269 | 0.38452 | 0.53101 | 0.40283 | 3.9047 | 122.4014 | 2.9709 | 122.3557 | 122.2778 | 122.2 | 122.1863 | 122.1817 | -122.3785 | -122.3053 | 122.3099 | 122.3373 | 45.7809 | 45.6894
1381.3281 | 122.5342 | -57.6279 | 64.6317 | -0.12688 | 0.0096708 | 0.067007 | 0.061731 | 0.0031188 | 0.001098 | 0.00013254 | 0.012207 | 0.0069727 | 0.068652 | 0.051526 | -0.0074 | 0.01307 | 0.0043814 | -11.9888 | 64.5401 | -57.756 | 64.5767 | -53.9108 | -57.2937 | -57.2845 | -11.8469 | 64.5493 | -57.6416 | 64.6408 | -54.7211 | -57.3166 | -57.1976 | -0.12817 | -0.091553 | -0.054932 | 3.717 | 0.34332 | 0.33417 | 0.4715 | 0.46234 | -0.013733 | -0.082398 | 0.009155 | 2.9068 | 0.4303 | 0.31128 | 0.44403 | 0.32501 | 3.8452 | 122.3328 | 2.9205 | 122.2824 | 122.2961 | 122.1909 | 122.168 | 122.1771 | -122.3877 | -122.2733 | 122.2046 | 122.2687 | 45.639 | 45.7809
1382.3125 | 122.4609 | -57.6508 | 64.7049 | 0.010452 | 0.012661 | 0.068503 | 0.064294 | 0.00055542 | -0.003388 | 0.00055974 | 0.012207 | 0.0088953 | 0.071856 | 0.067761 | -0.0088952 | 0.013497 | 0.0016044 | -12.0392 | 64.6454 | -57.7606 | 64.7369 | -53.9108 | -57.6141 | -57.431 | -12.1307 | 64.5905 | -57.6508 | 64.6179 | -54.7531 | -57.3624 | -57.2159 | -0.10986 | -0.059509 | 0.032043 | 3.7399 | 0.21973 | 0.036621 | 0.32959 | 0.14648 | 0 | -0.11444 | -0.086975 | 2.8976 | 0.43488 | 0.28839 | 0.43488 | 0.28839 | 3.8498 | 122.4976 | 2.8976 | 122.2687 | 122.406 | 122.2412 | 122.2961 | 122.2412 | -122.4655 | -122.3557 | 122.3877 | 122.2687 | 45.6116 | 45.52
1383.3125 | 122.4655 | -57.6416 | 64.6545 | 0.03334 | 0.010312 | 0.067434 | 0.066217 | 0.0029052 | 0.0019524 | 0.0024823 | -0.033569 | 0.010177 | 0.070361 | 0.063702 | -0.0063318 | 0.013924 | -0.0024546 | -12.0987 | 64.6088 | -57.7515 | 64.5859 | -53.8513 | -57.3669 | -57.3349 | -12.085 | 64.6133 | -57.6279 | 64.6271 | -54.7348 | -57.3624 | -57.2021 | -0.10986 | -0.045776 | -0.068665 | 3.7903 | 0.3067 | 0.27466 | 0.41657 | 0.38452 | 0.013733 | -0.041199 | -0.027466 | 2.9068 | 0.43945 | 0.27924 | 0.42572 | 0.2655 | 3.9001 | 122.3373 | 2.8931 | 122.2549 | 122.3602 | 122.2412 | 122.2504 | 122.2549 | -122.406 | -122.2824 | 122.2275 | 122.2687 | 45.5429 | 45.5566
1384.3125 | 122.493 | -57.6187 | 64.6683 | 0.0028229 | 0.008389 | 0.068289 | 0.064721 | 0.004187 | -0.00039736 | 0.0022687 | -0.079346 | 0.0091089 | 0.06972 | 0.068188 | -0.0088952 | 0.012856 | 0.001177 | -12.1216 | 64.6271 | -57.7652 | 64.5721 | -53.8696 | -57.28 | -57.2937 | -12.0621 | 64.6133 | -57.6324 | 64.6454 | -54.689 | -57.2937 | -57.1747 | -0.14648 | -0.041199 | -0.09613 | 3.7491 | 0.32501 | 0.33875 | 0.4715 | 0.48523 | -0.013733 | -0.054932 | -0.022888 | 2.9297 | 0.44403 | 0.32501 | 0.45776 | 0.33875 | 3.8956 | 122.3373 | 2.9434 | 122.2778 | 122.3923 | 122.2458 | 122.2458 | 122.2321 | -122.4335 | -122.3007 | 122.1909 | 122.2641 | 45.4971 | 45.5566
1385.3125 | 122.4609 | -57.6324 | 64.7141 | -0.073471 | 0.010525 | 0.06658 | 0.062372 | 0.0039734 | 2.9842e-05 | 0.0018413 | -0.012207 | 0.0088953 | 0.071216 | 0.065839 | -0.00505 | 0.012001 | -0.0018136 | -12.117 | 64.6454 | -57.7148 | 64.5996 | -53.8101 | -57.2617 | -57.2525 | -12.0621 | 64.6225 | -57.6233 | 64.6088 | -54.6661 | -57.3029 | -57.1747 | -0.082398 | -0.068664 | -0.11444 | 3.8223 | 0.37994 | 0.37079 | 0.46234 | 0.45319 | 0.009155 | -0.091552 | -0.10528 | 2.9663 | 0.45776 | 0.32959 | 0.44861 | 0.32044 | 3.9047 | 122.3145 | 2.9572 | 122.2321 | 122.3602 | 122.2458 | 122.2778 | 122.2549 | -122.4289 | -122.3373 | 122.2321 | 122.2412 | 45.5154 | 45.5704
1386.3125 | 122.4838 | -57.637 | 64.6729 | -0.035324 | 0.010952 | 0.068289 | 0.065149 | 0.00076902 | 0.0017388 | 0.0024823 | -0.091553 | 0.0091089 | 0.066943 | 0.058148 | -0.0082544 | 0.013924 | 0.0037406 | -12.1765 | 64.6179 | -57.7332 | 64.6042 | -53.8055 | -57.2708 | -57.2662 | -12.0392 | 64.5996 | -57.6416 | 64.6683 | -54.6341 | -57.3257 | -57.1426 | -0.09613 | -0.054932 | -0.068665 | 3.8315 | 0.37079 | 0.36621 | 0.46692 | 0.46234 | -0.004578 | -0.073243 | -0.004578 | 3.0029 | 0.49438 | 0.31128 | 0.49896 | 0.31586 | 3.9276 | 122.3373 | 3.0075 | 122.3099 | 122.3511 | 122.2412 | 122.2549 | 122.2366 | -122.406 | -122.3145 | 122.2412 | 122.3053 | 45.4605 | 45.5978
1387.3125 | 122.3557 | -57.5729 | 64.7141 | -0.020065 | 0.010952 | 0.068289 | 0.061731 | 0.0018372 | -0.00018376 | 0.0024823 | -0.0091553 | 0.0097497 | 0.068438 | 0.062848 | -0.0078272 | 0.012642 | 0.001818 | -12.2177 | 64.6545 | -57.7194 | 64.595 | -53.7918 | -57.2479 | -57.2479 | -12.1033 | 64.6317 | -57.6324 | 64.5584 | -54.4968 | -57.0648 | -57.1518 | -0.14648 | -0.059509 | -0.11902 | 3.7811 | 0.32501 | 0.32501 | 0.4715 | 0.4715 | -0.059509 | -0.082397 | -0.15564 | 3.0762 | 0.42114 | 0.50812 | 0.48065 | 0.56763 | 3.9276 | 122.3145 | 3.1357 | 122.1909 | 122.374 | 122.2641 | 122.2275 | 122.2046 | -122.4335 | -122.3465 | 122.168 | 122.1313 | 45.3552 | 45.4697
1388.3125 | 122.4472 | -57.6187 | 64.7095 | -0.058212 | 0.01138 | 0.066366 | 0.06344 | 0.00055542 | 0.001098 | -0.0013629 | -0.012207 | 0.0088953 | 0.069079 | 0.06413 | -0.0059046 | 0.012429 | -0.0003182 | -12.2726 | 64.6774 | -57.7332 | 64.5767 | -53.8193 | -57.2525 | -57.2525 | -12.085 | 64.6179 | -57.6141 | 64.6271 | -54.6066 | -57.2937 | -57.1472 | -0.11444 | -0.032044 | -0.13275 | 3.7994 | 0.36621 | 0.36621 | 0.48065 | 0.48065 | 0.004577 | -0.091553 | -0.082398 | 3.0121 | 0.4715 | 0.32501 | 0.46692 | 0.32044 | 3.9139 | 122.3099 | 3.0075 | 122.2412 | 122.4106 | 122.2321 | 122.2961 | 122.2366 | -122.4426 | -122.3236 | 122.1954 | 122.2458 | 45.3461 | 45.5338
1389.3125 | 122.4792 | -57.5821 | 64.7003 | -0.035324 | 0.010098 | 0.070212 | 0.063226 | 0.0033324 | 0.00067084 | 0.00013254 | -0.054932 | 0.0095361 | 0.069293 | 0.057294 | -0.0071864 | 0.014992 | 0.0026724 | -12.2818 | 64.6729 | -57.7011 | 64.6179 | -53.7598 | -57.2021 | -57.2479 | -12.0483 | 64.6317 | -57.6096 | 64.6866 | -54.5471 | -57.2617 | -57.106 | -0.11902 | -0.027465 | -0.082397 | 3.8223 | 0.33417 | 0.37994 | 0.45319 | 0.49896 | -0.027466 | -0.068664 | -0.013733 | 3.035 | 0.47607 | 0.32043 | 0.50354 | 0.3479 | 3.9413 | 122.319 | 3.0624 | 122.2961 | 122.374 | 122.2412 | 122.2549 | 122.2137 | -122.4014 | -122.3099 | 122.2 | 122.2687 | 45.3003 | 45.5338
1390.3125 | 122.493 | -57.5867 | 64.7186 | -0.058212 | 0.010952 | 0.06658 | 0.062372 | 0.0016236 | 0.00045724 | 0.00034614 | -0.042725 | 0.0078271 | 0.071429 | 0.066266 | -0.0086816 | 0.013497 | 0.001177 | -12.3322 | 64.6683 | -57.7148 | 64.6271 | -53.7323 | -57.2159 | -57.225 | -12.0621 | 64.6179 | -57.6233 | 64.6866 | -54.5242 | -57.2479 | -57.0923 | -0.12817 | -0.050354 | -0.091553 | 3.8544 | 0.36163 | 0.37079 | 0.48981 | 0.49896 | -0.036621 | -0.10071 | -0.032044 | 3.0624 | 0.49439 | 0.33874 | 0.53101 | 0.37537 | 3.9825 | 122.3419 | 3.0991 | 122.3099 | 122.3831 | 122.2412 | 122.2549 | 122.2046 | -122.4335 | -122.3419 | 122.2137 | 122.2733 | 45.2545 | 45.5246
1391.3125 | 122.4884 | -57.6004 | 64.6729 | -0.11925 | 0.012875 | 0.068289 | 0.063226 | -0.00072638 | -0.0012518 | 0.0012005 | -0.030517 | 0.0093225 | 0.071856 | 0.063702 | -0.0054774 | 0.01371 | 0.0016044 | -12.4466 | 64.6271 | -57.7423 | 64.5584 | -53.7643 | -57.2708 | -57.28 | -12.1399 | 64.5767 | -57.6279 | 64.682 | -54.5563 | -57.3029 | -57.1152 | -0.14191 | -0.045777 | -0.11444 | 3.8361 | 0.32044 | 0.32959 | 0.46234 | 0.4715 | -0.027466 | -0.096131 | 0.009155 | 3.0441 | 0.48523 | 0.29755 | 0.5127 | 0.32501 | 3.978 | 122.3007 | 3.0716 | 122.3099 | 122.3694 | 122.2046 | 122.2275 | 122.1771 | -122.4152 | -122.3007 | 122.1588 | 122.2824 | 45.1538 | 45.4605
1392.3125 | 122.4609 | -57.5638 | 64.7507 | -0.012436 | 0.011166 | 0.068075 | 0.06109 | 0.002478 | 0.00024344 | 0.0020551 | -0.0061035 | 0.0078271 | 0.071643 | 0.062848 | -0.0069726 | 0.014992 | 0.0037406 | -12.4466 | 64.6912 | -57.692 | 64.6133 | -53.6819 | -57.1976 | -57.1976 | -12.1994 | 64.6454 | -57.5638 | 64.7003 | -54.5288 | -57.2845 | -57.1381 | -0.12817 | -0.059509 | -0.13733 | 3.8818 | 0.36621 | 0.36621 | 0.49438 | 0.49438 | 0 | -0.10528 | -0.050354 | 3.035 | 0.42572 | 0.27924 | 0.42572 | 0.27924 | 4.01 | 122.3053 | 3.035 | 122.2641 | 122.3831 | 122.2092 | 122.2549 | 122.2092 | -122.4426 | -122.3145 | 122.1771 | 122.2641 | 45.1172 | 45.3644
1393.3125 | 122.4564 | -57.5729 | 64.7369 | -0.042954 | 0.012875 | 0.067007 | 0.065362 | 0.0026916 | 0.0013116 | 0.0052593 | -0.01831 | 0.0088953 | 0.070361 | 0.064557 | -0.0059046 | 0.014565 | 0.0026724 | -12.4878 | 64.7003 | -57.6874 | 64.6133 | -53.6774 | -57.2067 | -57.225 | -12.2406 | 64.6591 | -57.5821 | 64.6774 | -54.5151 | -57.2342 | -57.1014 | -0.11444 | -0.036621 | -0.1236 | 3.8956 | 0.3479 | 0.36621 | 0.46234 | 0.48065 | -0.009155 | -0.077819 | -0.059509 | 3.0579 | 0.4715 | 0.33875 | 0.48065 | 0.3479 | 4.01 | 122.3007 | 3.067 | 122.2595 | 122.3877 | 122.2412 | 122.2733 | 122.2321 | -122.4243 | -122.319 | 122.1863 | 122.2504 | 45.0851 | 45.3323
1394.3125 | 122.4976 | -57.5363 | 64.7552 | -0.020065 | 0.012234 | 0.070212 | 0.063653 | -0.00051278 | -0.00082456 | 0.0022687 | -0.036621 | 0.0091089 | 0.071429 | 0.059216 | -0.0071864 | 0.013924 | 0.0005362 | -12.4695 | 64.682 | -57.7057 | 64.6729 | -53.6362 | -57.1518 | -57.1793 | -12.2269 | 64.6545 | -57.5729 | 64.7186 | -54.4464 | -57.2296 | -57.0648 | -0.16937 | -0.073242 | -0.082397 | 3.9001 | 0.35706 | 0.38452 | 0.52643 | 0.55389 | -0.036621 | -0.10071 | -0.036621 | 3.0899 | 0.4715 | 0.3067 | 0.50812 | 0.34332 | 4.0695 | 122.3785 | 3.1265 | 122.2916 | 122.3877 | 122.2275 | 122.2183 | 122.1909 | -122.4609 | -122.3282 | 122.2092 | 122.2549 | 45.0668 | 45.3094
1395.3125 | 122.4609 | -57.5684 | 64.7552 | 0.010452 | 0.012234 | 0.067007 | 0.063867 | 0.00098262 | -0.00061096 | 0.0016277 | -0.012207 | 0.0097497 | 0.072497 | 0.055585 | -0.0074 | 0.014138 | 0.0003226 | -12.5473 | 64.7232 | -57.6691 | 64.6179 | -53.6407 | -57.1701 | -57.1884 | -12.3001 | 64.6729 | -57.5729 | 64.6957 | -54.4601 | -57.2067 | -57.0786 | -0.10071 | -0.032043 | -0.13733 | 3.9276 | 0.37994 | 0.39825 | 0.48065 | 0.49896 | -0.004578 | -0.082397 | -0.059509 | 3.1082 | 0.48981 | 0.36163 | 0.49439 | 0.36621 | 4.0283 | 122.287 | 3.1128 | 122.2687 | 122.3923 | 122.2458 | 122.2916 | 122.2412 | -122.4243 | -122.3282 | 122.1863 | 122.2641 | 45.0211 | 45.2682
1396.3125 | 122.4426 | -57.5775 | 64.7324 | -0.027695 | 0.012234 | 0.070639 | 0.066003 | 0.002478 | 0.002807 | 0.0050457 | -0.054932 | 0.010391 | 0.069507 | 0.060071 | -0.0059046 | 0.014565 | 0.0050222 | -12.6389 | 64.7049 | -57.6874 | 64.5721 | -53.6774 | -57.2479 | -57.225 | -12.3505 | 64.6454 | -57.5958 | 64.6683 | -54.4922 | -57.2708 | -57.0969 | -0.10986 | -0.027466 | -0.16022 | 3.9001 | 0.35248 | 0.32959 | 0.46234 | 0.43945 | -0.01831 | -0.086975 | -0.064087 | 3.0853 | 0.48065 | 0.3067 | 0.49896 | 0.32501 | 4.01 | 122.2595 | 3.1036 | 122.2641 | 122.3923 | 122.2412 | 122.2824 | 122.2229 | -122.4197 | -122.3282 | 122.1497 | 122.2458 | 44.9387 | 45.2271
1397.3125 | 122.4564 | -57.5592 | 64.7415 | -0.035324 | 0.010525 | 0.066153 | 0.063867 | 0.0022644 | 2.9842e-05 | 0.0014141 | 0.0030517 | 0.0091089 | 0.072497 | 0.061566 | -0.008468 | 0.012642 | -0.0011728 | -12.6526 | 64.7141 | -57.6782 | 64.6133 | -53.6087 | -57.1747 | -57.1838 | -12.3734 | 64.6729 | -57.5775 | 64.7003 | -54.4235 | -57.2296 | -57.0648 | -0.11902 | -0.027466 | -0.12817 | 3.9505 | 0.37537 | 0.38452 | 0.49439 | 0.50354 | -0.018311 | -0.068664 | -0.041199 | 3.1357 | 0.49439 | 0.32959 | 0.5127 | 0.3479 | 4.0695 | 122.2916 | 3.154 | 122.2778 | 122.3923 | 122.2504 | 122.2733 | 122.2321 | -122.4197 | -122.319 | 122.1725 | 122.2595 | 44.9066 | 45.1859
1398.3125 | 122.4838 | -57.5455 | 64.7644 | -0.27184 | 0.012875 | 0.066366 | 0.064081 | -8.538e-05 | 0.00024344 | 0.0033367 | -0.045776 | 0.0091089 | 0.069934 | 0.060498 | -0.005691 | 0.014351 | 0.001177 | -12.6846 | 64.6729 | -57.6645 | 64.6729 | -53.5034 | -57.1106 | -57.1426 | -12.3459 | 64.6408 | -57.5775 | 64.7369 | -54.3823 | -57.2021 | -57.0465 | -0.11902 | -0.091552 | -0.091552 | 4.0421 | 0.40283 | 0.43487 | 0.52185 | 0.55389 | -0.032044 | -0.1236 | -0.027466 | 3.1631 | 0.49896 | 0.34332 | 0.53101 | 0.37537 | 4.1611 | 122.3373 | 3.1952 | 122.3145 | 122.3373 | 122.2183 | 122.2183 | 122.1863 | -122.4289 | -122.3419 | 122.2183 | 122.2824 | 44.8608 | 45.1996
1399.3125 | 122.5754 | -57.4951 | 64.7095 | -0.11925 | 0.0096708 | 0.068503 | 0.062158 | 0.0031188 | 0.002166 | 0.0024823 | 0.015259 | 0.0082543 | 0.06972 | 0.055585 | -0.0069726 | 0.01307 | -0.0001046 | -12.7487 | 64.6225 | -57.6553 | 64.7095 | -53.4714 | -57.1014 | -57.0969 | -12.5702 | 64.5493 | -57.6096 | 64.7964 | -54.3137 | -57.1335 | -56.9595 | -0.16022 | -0.086975 | 0 | 4.0237 | 0.39825 | 0.39368 | 0.55847 | 0.55389 | -0.11444 | -0.16022 | 0.086975 | 3.1815 | 0.53558 | 0.36163 | 0.65002 | 0.47607 | 4.184 | 122.3648 | 3.2959 | 122.406 | 122.2778 | 122.1588 | 122.1176 | 122.0444 | -122.3648 | -122.319 | 122.2046 | 122.2916 | 44.7464 | 44.9249
1400.3125 | 122.493 | -57.5455 | 64.7873 | -0.081101 | 0.010952 | 0.067862 | 0.06109 | 0.00055542 | 0.00088444 | 0.0039777 | -0.030517 | 0.0076135 | 0.067584 | 0.057294 | -0.0074 | 0.013283 | 0.0024588 | -12.8036 | 64.7324 | -57.637 | 64.6408 | -53.54 | -57.1289 | -57.1335 | -12.4924 | 64.6912 | -57.5592 | 64.7141 | -54.3457 | -57.1793 | -57.0236 | -0.091553 | -0.054931 | -0.14648 | 4.0054 | 0.41199 | 0.41656 | 0.50354 | 0.50812 | -0.013733 | -0.09613 | -0.073242 | 3.1998 | 0.52185 | 0.36621 | 0.53558 | 0.37994 | 4.097 | 122.2778 | 3.2135 | 122.2733 | 122.3694 | 122.2504 | 122.2778 | 122.2366 | -122.4243 | -122.3465 | 122.1863 | 122.2595 | 44.7418 | 45.0531
1401.3125 | 122.4884 | -57.5226 | 64.7598 | 0.010452 | 0.010525 | 0.068503 | 0.064721 | 0.00012822 | 0.00067084 | 0.0048321 | -0.027466 | 0.0084679 | 0.070361 | 0.065625 | -0.0088952 | 0.014138 | 0.0003226 | -12.822 | 64.7369 | -57.6462 | 64.7049 | -53.4164 | -57.0831 | -57.0923 | -12.4649 | 64.6912 | -57.55 | 64.7507 | -54.3137 | -57.1655 | -57.0145 | -0.1236 | -0.022889 | -0.054932 | 4.1061 | 0.4303 | 0.43945 | 0.55389 | 0.56305 | -0.027466 | -0.068665 | -0.009156 | 3.2089 | 0.50812 | 0.35706 | 0.53558 | 0.38452 | 4.2297 | 122.3511 | 3.2364 | 122.3007 | 122.3831 | 122.2412 | 122.2595 | 122.2137 | -122.406 | -122.3099 | 122.2275 | 122.2733 | 44.7006 | 45.0577
1402.3125 | 122.4747 | -57.4905 | 64.7827 | -0.10399 | 0.011593 | 0.069143 | 0.064935 | 0.0020508 | -0.0010382 | 0.0016277 | -0.024414 | 0.0097497 | 0.070147 | 0.060712 | -0.0061182 | 0.014992 | 0.0022452 | -12.8815 | 64.7369 | -57.6141 | 64.7232 | -53.3844 | -57.074 | -57.0969 | -12.5244 | 64.7095 | -57.5226 | 64.7552 | -54.3045 | -57.1655 | -56.987 | -0.1236 | -0.045777 | -0.059509 | 4.1061 | 0.39368 | 0.41657 | 0.51727 | 0.54016 | -0.032043 | -0.073242 | -0.027466 | 3.186 | 0.50354 | 0.32501 | 0.53558 | 0.35706 | 4.2297 | 122.3373 | 3.2181 | 122.2778 | 122.3511 | 122.2321 | 122.2275 | 122.2 | -122.3969 | -122.3053 | 122.2137 | 122.2458 | 44.6091 | 44.9661
1403.3125 | 122.4518 | -57.5134 | 64.8148 | -0.073471 | 0.011807 | 0.068075 | 0.065149 | 0.0054688 | -0.00018376 | 0.0020551 | -0.042725 | 0.010177 | 0.068866 | 0.071393 | -0.008468 | 0.012215 | -0.0043772 | -12.9501 | 64.7369 | -57.6324 | 64.6683 | -53.4256 | -57.1243 | -57.1243 | -12.6389 | 64.7369 | -57.5134 | 64.7232 | -54.3503 | -57.2021 | -57.0328 | -0.11902 | -0.07782 | -0.14648 | 4.0878 | 0.3891 | 0.3891 | 0.50812 | 0.50812 | 0 | -0.07782 | -0.091552 | 3.1631 | 0.48065 | 0.31128 | 0.48065 | 0.31128 | 4.2068 | 122.3007 | 3.1631 | 122.2366 | 122.3694 | 122.2504 | 122.2504 | 122.2504 | -122.4472 | -122.3282 | 122.1817 | 122.2366 | 44.5633 | 44.8746
1404.3125 | 122.5571 | -57.4585 | 64.7507 | -0.065842 | 0.013302 | 0.069998 | 0.062158 | 0.00012822 | 0.002807 | 0.0020551 | 0.061035 | 0.0088953 | 0.069293 | 0.061139 | -0.0080408 | 0.012215 | 0.003527 | -12.9822 | 64.7095 | -57.6004 | 64.7736 | -53.2883 | -57.0099 | -57.0007 | -12.4832 | 64.6591 | -57.4814 | 64.8376 | -54.1946 | -57.0419 | -56.8863 | -0.14191 | -0.041198 | 0.022889 | 4.1702 | 0.45776 | 0.44861 | 0.59967 | 0.59052 | -0.022888 | -0.091552 | 0.086975 | 3.2639 | 0.5722 | 0.41656 | 0.59509 | 0.43945 | 4.3121 | 122.374 | 3.2867 | 122.319 | 122.3099 | 122.1405 | 122.168 | 122.1176 | -122.3511 | -122.2321 | 122.2321 | 122.2961 | 44.4763 | 44.9753
1405.3125 | 122.4426 | -57.4722 | 64.8102 | -0.065842 | 0.010952 | 0.068289 | 0.064721 | 0.00076902 | 0.00045724 | 0.0020551 | -0.045776 | 0.011886 | 0.069293 | 0.06413 | -0.010391 | 0.014992 | 0.0003226 | -13.06 | 64.7827 | -57.6141 | 64.7415 | -53.3249 | -57.0648 | -57.0602 | -12.6068 | 64.7232 | -57.4677 | 64.7736 | -54.2496 | -57.1381 | -56.9595 | -0.14191 | -0.027466 | -0.068665 | 4.1473 | 0.41199 | 0.40741 | 0.55389 | 0.54932 | 0.004578 | -0.086975 | -0.036621 | 3.2227 | 0.5127 | 0.33417 | 0.50812 | 0.32959 | 4.2892 | 122.3557 | 3.2181 | 122.2412 | 122.3969 | 122.1909 | 122.2549 | 122.1954 | -122.4243 | -122.2778 | 122.2137 | 122.2458 | 44.4122 | 44.8654
1406.3125 | 122.4518 | -57.4677 | 64.8331 | -0.027695 | 0.011166 | 0.070425 | 0.066217 | 0.00076902 | 0.001098 | 0.0014141 | -0.061035 | 0.011032 | 0.069079 | 0.068188 | -0.0093226 | 0.015206 | 0.0016044 | -13.0966 | 64.7644 | -57.6233 | 64.7461 | -53.3066 | -57.0419 | -57.0648 | -12.6663 | 64.7598 | -57.486 | 64.7736 | -54.2313 | -57.1198 | -56.9595 | -0.15564 | -0.068665 | -0.086975 | 4.1611 | 0.40283 | 0.42572 | 0.55847 | 0.58136 | -0.018311 | -0.073242 | -0.059509 | 3.2364 | 0.50812 | 0.3479 | 0.52643 | 0.36621 | 4.3167 | 122.3694 | 3.2547 | 122.2595 | 122.3877 | 122.2458 | 122.2321 | 122.2275 | -122.4564 | -122.319 | 122.2137 | 122.2412 | 44.371 | 44.8013
1407.3125 | 122.4701 | -57.4585 | 64.8422 | -0.027695 | 0.012875 | 0.069784 | 0.064294 | -8.538e-05 | 0.002166 | 0.0054729 | -0.042725 | 0.012741 | 0.070788 | 0.06712 | -0.0069726 | 0.016487 | 0.0024588 | -13.1287 | 64.8056 | -57.5546 | 64.7736 | -53.2196 | -56.9778 | -57.0007 | -12.6572 | 64.7736 | -57.4768 | 64.8285 | -54.1443 | -57.0694 | -56.9046 | -0.09613 | -0.036621 | -0.068664 | 4.2389 | 0.45776 | 0.48065 | 0.55389 | 0.57678 | -0.018311 | -0.068664 | -0.013733 | 3.3142 | 0.55389 | 0.3891 | 0.57221 | 0.40741 | 4.335 | 122.3282 | 3.3325 | 122.3053 | 122.3602 | 122.2504 | 122.2641 | 122.2321 | -122.3969 | -122.319 | 122.2321 | 122.287 | 44.3298 | 44.8013
1408.3125 | 122.4472 | -57.4539 | 64.8514 | -0.065842 | 0.013516 | 0.069784 | 0.064081 | 0.0033324 | 0.0032342 | 0.00055974 | -0.039673 | 0.0099633 | 0.069079 | 0.064343 | -0.0082544 | 0.01371 | 0.0016044 | -13.1927 | 64.801 | -57.5638 | 64.7461 | -53.2425 | -57.0236 | -57.0328 | -12.7625 | 64.769 | -57.4677 | 64.7781 | -54.1946 | -57.1152 | -56.9366 | -0.10986 | -0.050354 | -0.10528 | 4.2114 | 0.42114 | 0.4303 | 0.53101 | 0.54016 | -0.013733 | -0.082397 | -0.073242 | 3.2593 | 0.51727 | 0.33875 | 0.531 | 0.35248 | 4.3213 | 122.3099 | 3.273 | 122.2458 | 122.3648 | 122.2366 | 122.2549 | 122.2229 | -122.4152 | -122.319 | 122.2 | 122.2321 | 44.2612 | 44.6915
1409.3125 | 122.525 | -57.4036 | 64.8285 | -0.096359 | 0.01373 | 0.069357 | 0.063226 | 0.00076902 | 0.0013116 | 0.0018413 | 0.073242 | 0.0078271 | 0.069507 | 0.066052 | -0.0071864 | 0.012429 | 0.003527 | -13.2065 | 64.7552 | -57.4997 | 64.8193 | -53.1006 | -56.8863 | -56.9092 | -12.6846 | 64.7415 | -57.431 | 64.888 | -54.0665 | -56.9687 | -56.8359 | -0.096131 | -0.073242 | -0.009155 | 4.303 | 0.49438 | 0.51727 | 0.59052 | 0.6134 | -0.027466 | -0.086975 | 0.059509 | 3.3371 | 0.56763 | 0.43488 | 0.59509 | 0.46234 | 4.3991 | 122.319 | 3.3646 | 122.319 | 122.2549 | 122.1725 | 122.1588 | 122.1451 | -122.3282 | -122.2595 | 122.2229 | 122.2916 | 44.1971 | 44.7189
1410.3125 | 122.4564 | -57.4081 | 64.8651 | -0.042954 | 0.011593 | 0.069357 | 0.065149 | 0.0011962 | 0.0034478 | 0.0041913 | -0.039673 | 0.011886 | 0.070361 | 0.067975 | -0.0088952 | 0.015419 | 0.001818 | -13.2751 | 64.8331 | -57.5043 | 64.7964 | -53.1509 | -56.955 | -56.9595 | -12.7991 | 64.8056 | -57.4127 | 64.8422 | -54.071 | -57.019 | -56.8863 | -0.09613 | -0.032043 | -0.068664 | 4.2572 | 0.44861 | 0.45319 | 0.54474 | 0.54932 | -0.004578 | -0.059509 | -0.022888 | 3.3371 | 0.52185 | 0.3891 | 0.52643 | 0.39368 | 4.3533 | 122.3007 | 3.3417 | 122.2549 | 122.3373 | 122.2183 | 122.2412 | 122.2137 | -122.3694 | -122.2778 | 122.2046 | 122.2504 | 44.133 | 44.6091
1411.3125 | 122.4564 | -57.4173 | 64.9017 | -0.027695 | 0.013302 | 0.071493 | 0.066644 | -0.002649 | 0.0015252 | 0.0020551 | -0.057983 | 0.0082543 | 0.069079 | 0.063061 | -0.0074 | 0.015847 | 0.001177 | -13.4995 | 64.7552 | -57.5317 | 64.7644 | -53.2288 | -56.9778 | -56.9824 | -12.9181 | 64.7964 | -57.4127 | 64.8239 | -54.1214 | -57.0786 | -56.8909 | -0.11444 | -0.14648 | -0.13733 | 4.1885 | 0.43487 | 0.43945 | 0.54932 | 0.55389 | 0.004577 | -0.10528 | -0.077819 | 3.2959 | 0.52643 | 0.33874 | 0.52185 | 0.33417 | 4.303 | 122.2961 | 3.2913 | 122.2366 | 122.287 | 122.2092 | 122.1725 | 122.2137 | -122.4335 | -122.3145 | 122.1817 | 122.2412 | 43.9178 | 44.4992
1412.3125 | 122.4564 | -57.3898 | 64.8697 | 0.17067 | 0.012021 | 0.069784 | 0.066217 | 0.00055542 | 0.002166 | 0.0033367 | -0.048828 | 0.010604 | 0.069293 | 0.06178 | -0.0080408 | 0.013924 | 0.0003226 | -13.5132 | 64.856 | -57.5409 | 64.7644 | -53.1692 | -57.0053 | -56.9916 | -12.9822 | 64.7964 | -57.4127 | 64.8376 | -54.0939 | -57.0557 | -56.868 | -0.15106 | -0.013733 | -0.10529 | 4.2206 | 0.39825 | 0.38452 | 0.54932 | 0.53558 | -0.022888 | -0.073242 | -0.032044 | 3.2959 | 0.52185 | 0.33417 | 0.54474 | 0.35706 | 4.3716 | 122.3053 | 3.3188 | 122.2504 | 122.3969 | 122.2092 | 122.2458 | 122.1863 | -122.4106 | -122.2824 | 122.1542 | 122.2275 | 43.8766 | 44.4077
1413.3125 | 122.4564 | -57.3944 | 64.8743 | -0.027695 | 0.010098 | 0.070212 | 0.066217 | 0.0026916 | 0.0015252 | 0.0024823 | -0.01831 | 0.0088953 | 0.069934 | 0.065411 | -0.0074 | 0.014778 | 0.0009634 | -13.4857 | 64.8605 | -57.4997 | 64.7598 | -53.1326 | -56.9824 | -56.9733 | -12.9913 | 64.8285 | -57.4173 | 64.8468 | -54.0619 | -57.0419 | -56.8588 | -0.10529 | -0.013733 | -0.11444 | 4.2618 | 0.42114 | 0.41199 | 0.52643 | 0.51727 | -0.022888 | -0.045777 | -0.027466 | 3.3325 | 0.53558 | 0.35248 | 0.55847 | 0.37537 | 4.3671 | 122.2595 | 3.3554 | 122.2641 | 122.3602 | 122.2458 | 122.2549 | 122.2229 | -122.374 | -122.2916 | 122.1542 | 122.2412 | 43.9087 | 44.4031
1414.3125 | 122.5159 | -57.3257 | 64.8697 | -0.10399 | 0.010525 | 0.06893 | 0.062799 | -0.00072638 | 0.0013116 | 0.0046185 | 0.033569 | 0.0091089 | 0.070575 | 0.061139 | -0.009109 | 0.011147 | 0.0005362 | -13.4308 | 64.8148 | -57.4356 | 64.9017 | -52.9312 | -56.8222 | -56.8359 | -12.886 | 64.7736 | -57.3349 | 64.9658 | -53.9062 | -56.8771 | -56.749 | -0.10986 | -0.054932 | 0.032043 | 4.3945 | 0.48981 | 0.50354 | 0.59967 | 0.6134 | -0.009155 | -0.09613 | 0.09613 | 3.4195 | 0.57678 | 0.44861 | 0.58594 | 0.45776 | 4.5044 | 122.3373 | 3.4286 | 122.3007 | 122.2504 | 122.1085 | 122.1405 | 122.0993 | -122.3053 | -122.2046 | 122.2275 | 122.2916 | 43.895 | 44.4397
1415.3125 | 122.4426 | -57.3807 | 64.9063 | -0.081101 | 0.012234 | 0.068503 | 0.064508 | -0.00093998 | 0.00088444 | 0.00034614 | -0.05188 | 0.011245 | 0.070361 | 0.067334 | -0.0074 | 0.013497 | 0.0005362 | -13.559 | 64.8651 | -57.4997 | 64.7873 | -53.0411 | -56.9321 | -56.9458 | -13.0508 | 64.8102 | -57.399 | 64.888 | -53.9932 | -56.9962 | -56.8268 | -0.11902 | -0.041199 | -0.11902 | 4.3396 | 0.43487 | 0.44861 | 0.55389 | 0.56763 | -0.018311 | -0.09613 | -0.018311 | 3.3875 | 0.55389 | 0.38452 | 0.5722 | 0.40283 | 4.4586 | 122.287 | 3.4058 | 122.287 | 122.3648 | 122.2092 | 122.2458 | 122.1909 | -122.406 | -122.3053 | 122.168 | 122.2687 | 43.8217 | 44.3298
1416.3125 | 122.5342 | -57.3441 | 64.8788 | -0.15739 | 0.013516 | 0.070212 | 0.061303 | 0.00098262 | 0.0013116 | 0.0039777 | 0.054932 | 0.0093225 | 0.068866 | 0.062207 | -0.0074 | 0.01307 | 0.0016044 | -13.5544 | 64.8468 | -57.4631 | 64.9109 | -52.8946 | -56.7993 | -56.7947 | -12.9913 | 64.8193 | -57.3761 | 64.9612 | -53.8651 | -56.868 | -56.7307 | -0.11902 | -0.032043 | 0.032044 | 4.4495 | 0.54932 | 0.54474 | 0.66833 | 0.66376 | -0.032044 | -0.059509 | 0.082398 | 3.479 | 0.6134 | 0.47607 | 0.64545 | 0.50812 | 4.5685 | 122.374 | 3.511 | 122.3373 | 122.3099 | 122.1954 | 122.1909 | 122.1634 | -122.3419 | -122.2549 | 122.2549 | 122.3053 | 43.7897 | 44.3527
1417.3125 | 122.5433 | -57.3395 | 64.8743 | -0.30235 | 0.014798 | 0.068503 | 0.063867 | 0.00055542 | 0.0015252 | 0.0035503 | 0.0061035 | 0.0095361 | 0.066943 | 0.063702 | -0.010818 | 0.012429 | -0.0024546 | -13.4995 | 64.8239 | -57.4402 | 64.9063 | -52.858 | -56.781 | -56.8268 | -13.0188 | 64.7873 | -57.3486 | 64.9658 | -53.8513 | -56.868 | -56.7215 | -0.10071 | -0.050354 | 0.032043 | 4.4815 | 0.5127 | 0.55847 | 0.6134 | 0.65918 | -0.009155 | -0.086976 | 0.091552 | 3.4882 | 0.61798 | 0.4715 | 0.62714 | 0.48065 | 4.5822 | 122.3465 | 3.4973 | 122.3145 | 122.2641 | 122.1359 | 122.1634 | 122.1268 | -122.3145 | -122.2229 | 122.2458 | 122.3053 | 43.84 | 44.3207
1418.3125 | 122.5479 | -57.3029 | 64.9155 | -0.020065 | 0.011807 | 0.069784 | 0.06344 | -0.00051278 | 0.0023798 | 0.0031231 | 0.0030517 | 0.0086815 | 0.068866 | 0.064557 | -0.008468 | 0.012215 | 0.0016044 | -13.7054 | 64.8422 | -57.4265 | 64.9155 | -52.8534 | -56.7581 | -56.7764 | -13.0737 | 64.8102 | -57.3486 | 64.9979 | -53.8101 | -56.8542 | -56.694 | -0.1236 | -0.073242 | 0 | 4.4495 | 0.52643 | 0.54474 | 0.65002 | 0.66833 | -0.045777 | -0.10528 | 0.082398 | 3.4927 | 0.60882 | 0.44861 | 0.6546 | 0.49439 | 4.5731 | 122.3419 | 3.5385 | 122.3465 | 122.2687 | 122.1588 | 122.1451 | 122.113 | -122.3419 | -122.2641 | 122.2183 | 122.3007 | 43.5974 | 44.2291
1419.3125 | 122.525 | -57.3349 | 64.9155 | -0.081101 | 0.011807 | 0.069998 | 0.063226 | -0.002649 | 0.00067084 | 0.0014141 | 0.021362 | 0.0093225 | 0.071429 | 0.059857 | -0.0099634 | 0.012642 | -0.0007456 | -13.7238 | 64.8468 | -57.4402 | 64.9017 | -52.8259 | -56.8085 | -56.7947 | -13.1516 | 64.8148 | -57.3257 | 64.9475 | -53.8376 | -56.8588 | -56.7307 | -0.10529 | -0.068664 | -0.013733 | 4.509 | 0.54016 | 0.52643 | 0.64545 | 0.63171 | 0.009155 | -0.10071 | 0.032044 | 3.4973 | 0.60425 | 0.47607 | 0.59509 | 0.46692 | 4.6143 | 122.3419 | 3.4882 | 122.2733 | 122.287 | 122.1405 | 122.1817 | 122.1497 | -122.3557 | -122.2412 | 122.2366 | 122.2824 | 43.6111 | 44.1833
1420.3125 | 122.5342 | -57.2891 | 64.9292 | -0.11925 | 0.011593 | 0.070212 | 0.06579 | 0.00055542 | 0.003875 | 0.0041913 | -0.057983 | 0.011886 | 0.068438 | 0.063916 | -0.0071864 | 0.01371 | 0.0009634 | -13.8153 | 64.92 | -57.4631 | 64.8651 | -52.8671 | -56.8405 | -56.8497 | -13.2568 | 64.8926 | -57.3532 | 64.9887 | -53.8239 | -56.8863 | -56.7352 | -0.17395 | -0.009155 | -0.064087 | 4.422 | 0.43945 | 0.44861 | 0.6134 | 0.62256 | -0.064086 | -0.036621 | 0.059509 | 3.4653 | 0.5539 | 0.40283 | 0.61798 | 0.46692 | 4.5959 | 122.3282 | 3.5294 | 122.3419 | 122.3831 | 122.2458 | 122.2092 | 122.1817 | -122.3923 | -122.2824 | 122.1542 | 122.2778 | 43.4738 | 44.0323
1421.3125 | 122.5754 | -57.3029 | 64.9063 | -0.11162 | 0.013516 | 0.067648 | 0.066003 | -0.0022218 | 0.0036614 | 0.0033367 | -0.027466 | 0.011459 | 0.070147 | 0.064984 | -0.0097498 | 0.012429 | 0.0033134 | -13.7924 | 64.8697 | -57.4127 | 64.9475 | -52.7618 | -56.7307 | -56.7581 | -13.4079 | 64.7919 | -57.3578 | 65.0436 | -53.7552 | -56.7993 | -56.6483 | -0.10986 | -0.036621 | 0.041199 | 4.541 | 0.54474 | 0.5722 | 0.6546 | 0.68207 | -0.054932 | -0.11444 | 0.13733 | 3.5477 | 0.6546 | 0.50354 | 0.70953 | 0.55847 | 4.6509 | 122.3602 | 3.6026 | 122.4014 | 122.2824 | 122.1497 | 122.1725 | 122.0947 | -122.319 | -122.2641 | 122.2504 | 122.3465 | 43.5104 | 43.895
1422.3125 | 122.5662 | -57.2617 | 64.9292 | -0.096359 | 0.011593 | 0.070639 | 0.065149 | 0.004187 | 0.001098 | 0.0039777 | -0.042725 | 0.0080407 | 0.070575 | 0.061139 | -0.0080408 | 0.012642 | 0.0007498 | -13.8931 | 64.8926 | -57.431 | 64.9017 | -52.8076 | -56.7993 | -56.7947 | -13.3255 | 64.8697 | -57.3349 | 65.0116 | -53.7598 | -56.8268 | -56.6528 | -0.16937 | -0.036621 | -0.027466 | 4.454 | 0.46692 | 0.46234 | 0.63629 | 0.63171 | -0.073242 | -0.059509 | 0.082398 | 3.5019 | 0.60883 | 0.43488 | 0.68207 | 0.50812 | 4.6234 | 122.3328 | 3.5751 | 122.3465 | 122.3236 | 122.2046 | 122.1542 | 122.1313 | -122.3602 | -122.2641 | 122.1634 | 122.2733 | 43.3685 | 43.9362
1423.3125 | 122.5342 | -57.2617 | 64.9292 | -0.10399 | 0.01373 | 0.071066 | 0.063653 | -0.00051278 | -0.0010382 | -0.00029486 | -0.0091553 | 0.011032 | 0.068011 | 0.061566 | -0.0078272 | 0.015847 | -0.0003182 | -13.8657 | 64.9063 | -57.3761 | 64.975 | -52.6749 | -56.694 | -56.694 | -13.2889 | 64.8605 | -57.2845 | 65.0299 | -53.6774 | -56.7993 | -56.6437 | -0.11444 | -0.022888 | 0.045777 | 4.5868 | 0.56763 | 0.56763 | 0.68207 | 0.68207 | -0.022888 | -0.068664 | 0.10071 | 3.5843 | 0.61798 | 0.46234 | 0.64087 | 0.48523 | 4.7012 | 122.3511 | 3.6072 | 122.3145 | 122.2824 | 122.1451 | 122.168 | 122.1222 | -122.3053 | -122.2137 | 122.2366 | 122.2916 | 43.396 | 43.9728
1424.3125 | 122.4335 | -57.2571 | 65.0574 | -0.012436 | 0.012875 | 0.06658 | 0.065149 | -8.538e-05 | 0.00045724 | 0.0029095 | -0.14343 | 0.011245 | 0.070147 | 0.059216 | -0.0093226 | 0.013924 | 0.001177 | -13.9343 | 65.0208 | -57.3441 | 64.9246 | -52.739 | -56.4148 | -56.7078 | -13.3987 | 64.9887 | -57.2845 | 64.9841 | -53.6911 | -56.8268 | -56.6986 | -0.086975 | -0.036621 | -0.13275 | 4.5181 | 0.54932 | 0.84229 | 0.63629 | 0.92926 | -0.027466 | -0.068665 | -0.073242 | 3.566 | 0.55847 | 0.4303 | 0.58594 | 0.45776 | 4.6051 | 122.2687 | 3.5934 | 122.2687 | 122.3648 | 122.2733 | 122.2778 | 122.2458 | -122.4014 | -122.3419 | 122.1817 | 122.2412 | 43.3228 | 43.8583
1425.3125 | 122.5021 | -57.2525 | 64.9292 | -0.081101 | 0.013943 | 0.070852 | 0.066003 | -0.00029898 | 0.0013116 | 0.0044049 | -0.01831 | 0.0086815 | 0.06972 | 0.061352 | -0.0082544 | 0.014778 | 0.003527 | -13.9755 | 64.9475 | -57.3898 | 64.975 | -52.6245 | -56.6528 | -56.6986 | -13.3759 | 64.8926 | -57.2525 | 65.0894 | -53.6133 | -56.7398 | -56.5521 | -0.13733 | 0.018311 | 0.045777 | 4.628 | 0.55389 | 0.59967 | 0.69122 | 0.737 | 0 | -0.036621 | 0.16022 | 3.6392 | 0.70038 | 0.5127 | 0.70038 | 0.5127 | 4.7653 | 122.3648 | 3.6392 | 122.3419 | 122.3373 | 122.1451 | 122.2 | 122.1451 | -122.319 | -122.1817 | 122.2275 | 122.3419 | 43.277 | 43.8766
1426.3125 | 122.5159 | -57.2296 | 65.0024 | -0.050583 | 0.012448 | 0.069143 | 0.065149 | 0.002478 | -0.00018376 | 0.0033367 | -0.0061035 | 0.0093225 | 0.069079 | 0.05708 | -0.006759 | 0.012429 | 0.0050222 | -13.9938 | 64.9521 | -57.3532 | 64.9796 | -52.5833 | -56.6803 | -56.6803 | -13.4811 | 64.8834 | -57.2525 | 65.0482 | -53.627 | -56.749 | -56.6254 | -0.1236 | -0.050354 | -0.022888 | 4.6463 | 0.54932 | 0.54932 | 0.67291 | 0.67291 | -0.022888 | -0.11902 | 0.045777 | 3.6026 | 0.60425 | 0.48065 | 0.62714 | 0.50354 | 4.7699 | 122.3328 | 3.6255 | 122.3007 | 122.3053 | 122.1359 | 122.1817 | 122.113 | -122.3557 | -122.2549 | 122.2092 | 122.2778 | 43.2358 | 43.7485
1427.3125 | 122.5296 | -57.2021 | 64.9979 | -0.11925 | 0.013302 | 0.069784 | 0.064721 | 0.0026916 | 0.0023798 | 0.0039777 | -0.021362 | 0.010177 | 0.067157 | 0.06178 | -0.0080408 | 0.014351 | 0.001177 | -14.035 | 64.9521 | -57.3532 | 65.0345 | -52.5238 | -56.6299 | -56.6483 | -13.472 | 64.9246 | -57.225 | 65.1077 | -53.5721 | -56.7123 | -56.5796 | -0.15106 | -0.045777 | 0.036621 | 4.6783 | 0.55389 | 0.5722 | 0.70496 | 0.72327 | -0.022889 | -0.073242 | 0.10986 | 3.6301 | 0.62256 | 0.48981 | 0.64545 | 0.5127 | 4.8294 | 122.3877 | 3.653 | 122.3328 | 122.3053 | 122.1497 | 122.1542 | 122.1268 | -122.3511 | -122.2229 | 122.2366 | 122.3099 | 43.1671 | 43.7302
1428.3125 | 122.5113 | -57.2113 | 65.0208 | -0.081101 | 0.013089 | 0.069571 | 0.064081 | -0.0011536 | -0.00018376 | 0.0044049 | -0.012207 | 0.0078271 | 0.072497 | 0.060712 | -0.0082544 | 0.015847 | -0.000532 | -14.1129 | 64.9567 | -57.3349 | 65.007 | -52.5467 | -56.6345 | -56.6528 | -13.5864 | 64.9521 | -57.2479 | 65.0574 | -53.5629 | -56.7307 | -56.5887 | -0.1236 | -0.064087 | -0.013733 | 4.6646 | 0.55847 | 0.57678 | 0.68207 | 0.70038 | -0.036621 | -0.068665 | 0.036621 | 3.6484 | 0.62256 | 0.48065 | 0.65918 | 0.51727 | 4.7882 | 122.3419 | 3.685 | 122.3053 | 122.2916 | 122.2 | 122.168 | 122.1634 | -122.3557 | -122.2687 | 122.2183 | 122.2687 | 43.0984 | 43.6249
1429.3125 | 122.5433 | -57.1518 | 65.0528 | 0.018082 | 0.011593 | 0.069143 | 0.064721 | 0.0033324 | 0.00088444 | 0.0031231 | 0.012207 | 0.0082543 | 0.069507 | 0.060284 | -0.0076136 | 0.014351 | -0.000532 | -14.0808 | 65.007 | -57.2983 | 65.094 | -52.4277 | -56.5292 | -56.5704 | -13.5178 | 64.9658 | -57.2205 | 65.1352 | -53.4622 | -56.6391 | -56.5384 | -0.14648 | -0.045776 | 0.041199 | 4.7241 | 0.58136 | 0.62256 | 0.72784 | 0.76904 | -0.068665 | -0.086975 | 0.082398 | 3.6896 | 0.6134 | 0.5127 | 0.68207 | 0.58136 | 4.8706 | 122.3923 | 3.7582 | 122.3557 | 122.3053 | 122.1863 | 122.1588 | 122.1176 | -122.3511 | -122.2733 | 122.2458 | 122.287 | 43.071 | 43.634
1430.3125 | 122.5067 | -57.2067 | 65.0162 | -0.12688 | 0.012661 | 0.070212 | 0.063867 | -0.0015808 | 0.0013116 | 0.0037639 | 0.0061035 | 0.0088953 | 0.069934 | 0.059644 | -0.0082544 | 0.015847 | 0.0003226 | -14.2044 | 64.9979 | -57.3166 | 65.0024 | -52.5009 | -56.6391 | -56.6483 | -13.678 | 64.9429 | -57.2296 | 65.062 | -53.5995 | -56.4926 | -56.4331 | -0.10986 | -0.01831 | -0.013733 | 4.7058 | 0.55847 | 0.56763 | 0.66833 | 0.67749 | -0.022888 | -0.073242 | 0.045777 | 3.6072 | 0.77362 | 0.71411 | 0.79651 | 0.737 | 4.8157 | 122.319 | 3.6301 | 122.2916 | 122.3145 | 122.1725 | 122.2046 | 122.1497 | -122.3328 | -122.2458 | 122.2092 | 122.2687 | 43.0023 | 43.5287
1431.3125 | 122.5067 | -57.1976 | 65.0528 | -0.11925 | 0.011807 | 0.07128 | 0.063012 | -8.538e-05 | 0.0036614 | 0.00098694 | -0.0061035 | 0.011032 | 0.06972 | 0.058789 | -0.0093226 | 0.015633 | 0.0020316 | -14.2502 | 64.975 | -57.3074 | 65.0116 | -52.4643 | -56.5659 | -56.6162 | -13.6917 | 64.9475 | -57.2159 | 65.0208 | -53.508 | -56.6666 | -56.5613 | -0.10986 | -0.077819 | -0.041198 | 4.7333 | 0.58136 | 0.63171 | 0.69122 | 0.74158 | -0.01831 | -0.10529 | -0.032043 | 3.6896 | 0.63629 | 0.53101 | 0.6546 | 0.54932 | 4.8431 | 122.319 | 3.7079 | 122.2366 | 122.2824 | 122.1634 | 122.1725 | 122.1451 | -122.3602 | -122.2687 | 122.2092 | 122.2183 | 42.9474 | 43.5059
1432.3125 | 122.5204 | -57.2159 | 65.0528 | -0.12688 | 0.014157 | 0.07128 | 0.064294 | -0.00051278 | 0.00067084 | 0.0037639 | 0.10681 | 0.011245 | 0.071643 | 0.061352 | -0.0088952 | 0.014565 | 0.0007498 | -14.2776 | 65.0208 | -57.2891 | 65.0253 | -52.4231 | -56.5613 | -56.5887 | -13.829 | 64.9658 | -57.225 | 65.094 | -53.4988 | -56.694 | -56.543 | -0.073243 | -0.032043 | -0.027465 | 4.7928 | 0.62714 | 0.6546 | 0.70038 | 0.72785 | -0.009156 | -0.086975 | 0.041199 | 3.717 | 0.67291 | 0.52185 | 0.68207 | 0.53101 | 4.866 | 122.3145 | 3.7262 | 122.319 | 122.3099 | 122.1909 | 122.2366 | 122.1817 | -122.3419 | -122.2778 | 122.2412 | 122.3099 | 42.9382 | 43.3868
1433.3125 | 122.5616 | -57.1655 | 65.0757 | -0.10399 | 0.010739 | 0.068503 | 0.064935 | 0.00076902 | 0.0015252 | 0.0046185 | -0.0030517 | 0.0095361 | 0.071002 | 0.064984 | -0.0082544 | 0.012215 | -0.0009592 | -14.3051 | 65.0208 | -57.2845 | 65.0528 | -52.3636 | -56.5201 | -56.5475 | -13.6871 | 64.9979 | -57.2113 | 65.1306 | -53.3707 | -56.6116 | -56.5063 | -0.11902 | -0.054932 | -0.022889 | 4.8019 | 0.61798 | 0.64545 | 0.737 | 0.76447 | -0.045777 | -0.07782 | 0.054931 | 3.7949 | 0.65918 | 0.55389 | 0.70496 | 0.59967 | 4.921 | 122.3373 | 3.8406 | 122.3419 | 122.3053 | 122.2092 | 122.1863 | 122.1634 | -122.3602 | -122.287 | 122.2183 | 122.2961 | 42.8604 | 43.4784
1434.3125 | 122.5342 | -57.1335 | 65.094 | -0.13451 | 0.014798 | 0.070852 | 0.064508 | 0.0018372 | 0.0017388 | 0.0014141 | -0.0030517 | 0.0093225 | 0.068652 | 0.069043 | -0.0082544 | 0.014778 | 0.0022452 | -14.2868 | 65.0208 | -57.2845 | 65.1123 | -52.272 | -56.4377 | -56.5109 | -13.678 | 64.9704 | -57.1609 | 65.1672 | -53.334 | -56.5842 | -56.4789 | -0.15106 | -0.073242 | 0.018311 | 4.8615 | 0.62256 | 0.6958 | 0.77362 | 0.84686 | -0.027466 | -0.1236 | 0.073242 | 3.7994 | 0.6546 | 0.54932 | 0.68207 | 0.57678 | 5.0125 | 122.3969 | 3.8269 | 122.3282 | 122.3053 | 122.1313 | 122.1542 | 122.1039 | -122.3785 | -122.2549 | 122.2458 | 122.3007 | 42.8467 | 43.4555
1435.3125 | 122.525 | -57.1426 | 65.1215 | -0.050583 | 0.011593 | 0.070212 | 0.065149 | -0.0015808 | 0.0030206 | 0.0054729 | -0.01831 | 0.012954 | 0.069507 | 0.061352 | -0.0069726 | 0.01307 | -0.0020272 | -14.3967 | 65.0345 | -57.3029 | 65.0528 | -52.3178 | -56.5247 | -56.5613 | -13.797 | 64.9796 | -57.1701 | 65.1306 | -53.3661 | -56.6162 | -56.4972 | -0.16022 | -0.086975 | -0.068665 | 4.8248 | 0.58136 | 0.61798 | 0.74158 | 0.7782 | -0.027466 | -0.14191 | 0.009155 | 3.7766 | 0.64545 | 0.52643 | 0.67291 | 0.55389 | 4.985 | 122.3557 | 3.804 | 122.3007 | 122.3373 | 122.1497 | 122.1771 | 122.1222 | -122.4243 | -122.2916 | 122.1954 | 122.2733 | 42.746 | 43.3456
1436.3125 | 122.5433 | -57.1152 | 65.1031 | -0.050583 | 0.013943 | 0.068716 | 0.06344 | 0.0018372 | 0.0025934 | 0.0022687 | 0.0091553 | 0.010177 | 0.067798 | 0.068402 | -0.0076136 | 0.014138 | -0.0022408 | -14.3692 | 65.0482 | -57.2342 | 65.1031 | -52.2491 | -56.4514 | -56.488 | -13.7878 | 65.0436 | -57.1655 | 65.1901 | -53.2883 | -56.5201 | -56.4331 | -0.11902 | -0.054931 | 0 | 4.866 | 0.62714 | 0.66376 | 0.74616 | 0.78278 | -0.050354 | -0.059509 | 0.086976 | 3.8269 | 0.68207 | 0.59509 | 0.73242 | 0.64545 | 4.985 | 122.3373 | 3.8773 | 122.3557 | 122.2824 | 122.2092 | 122.1634 | 122.1588 | -122.3373 | -122.2687 | 122.2183 | 122.3053 | 42.746 | 43.3273
1437.3125 | 122.58 | -57.1289 | 65.1031 | -0.065842 | 0.01373 | 0.069571 | 0.064721 | 0.00098262 | 0.002166 | 0.0041913 | -0.015259 | 0.0097497 | 0.069293 | 0.068188 | -0.006759 | 0.015206 | 0.0020316 | -14.4104 | 65.0665 | -57.2388 | 65.1352 | -52.1805 | -56.4148 | -56.4743 | -13.8199 | 65.0482 | -57.1564 | 65.2176 | -53.2379 | -56.5201 | -56.4056 | -0.10986 | -0.036621 | 0.032044 | 4.9484 | 0.6546 | 0.71411 | 0.76447 | 0.82398 | -0.027466 | -0.054931 | 0.11444 | 3.891 | 0.72327 | 0.60883 | 0.75073 | 0.63629 | 5.0583 | 122.374 | 3.9185 | 122.374 | 122.3053 | 122.2046 | 122.1954 | 122.1771 | -122.3419 | -122.2595 | 122.2641 | 122.3465 | 42.7185 | 43.309
1438.3125 | 122.5571 | -57.0877 | 65.126 | 0.018082 | 0.013302 | 0.070212 | 0.067499 | 0.0011962 | 0.0043024 | 0.0016277 | -0.024414 | 0.010177 | 0.070361 | 0.058148 | -0.009109 | 0.01307 | 0.005236 | -14.4012 | 65.062 | -57.2708 | 65.1489 | -52.1255 | -56.4011 | -56.4468 | -13.8428 | 65.0162 | -57.1152 | 65.2451 | -53.2013 | -56.5018 | -56.3919 | -0.1831 | -0.064087 | 0.022888 | 4.9622 | 0.64087 | 0.68665 | 0.82397 | 0.86975 | -0.027465 | -0.10986 | 0.11902 | 3.8864 | 0.6958 | 0.58594 | 0.72327 | 0.6134 | 5.1453 | 122.4197 | 3.9139 | 122.3602 | 122.3328 | 122.1313 | 122.1497 | 122.1039 | -122.3969 | -122.2412 | 122.2366 | 122.3328 | 42.6865 | 43.2449
1439.3125 | 122.4564 | -57.1518 | 65.1947 | -0.0048066 | 0.011593 | 0.069357 | 0.064508 | 0.00055542 | -0.00039736 | 0.0026959 | -0.07019 | 0.010391 | 0.071216 | 0.062634 | -0.0069726 | 0.01371 | 0.002886 | -14.5065 | 65.1123 | -57.2342 | 65.0848 | -52.1942 | -56.4514 | -56.5247 | -14.0396 | 65.0986 | -57.1518 | 65.2634 | -53.3295 | -56.8359 | -56.6574 | -0.082398 | -0.082397 | -0.10986 | 4.9576 | 0.62714 | 0.70038 | 0.70953 | 0.78278 | 0 | -0.09613 | 0.068665 | 3.8223 | 0.49438 | 0.31586 | 0.49438 | 0.31586 | 5.04 | 122.319 | 3.8223 | 122.4152 | 122.3465 | 122.2504 | 122.2641 | 122.2504 | -122.4289 | -122.3465 | 122.2366 | 122.4152 | 42.6453 | 43.1122
1440.3125 | 122.5067 | -57.0694 | 65.1489 | -0.065842 | 0.014584 | 0.070425 | 0.065362 | 0.0048278 | 0.0053704 | 0.0014141 | -0.033569 | 0.0097497 | 0.069934 | 0.061993 | -0.0080408 | 0.013283 | 0.002886 | -14.4882 | 65.0757 | -57.2296 | 65.1901 | -52.0203 | -56.3416 | -56.4148 | -13.9297 | 65.062 | -57.0969 | 65.2359 | -53.1555 | -56.4697 | -56.4148 | -0.16022 | -0.073242 | 0.041199 | 5.0491 | 0.6546 | 0.72784 | 0.81482 | 0.88806 | -0.027466 | -0.086975 | 0.086975 | 3.9139 | 0.6546 | 0.59967 | 0.68207 | 0.62714 | 5.2094 | 122.4197 | 3.9413 | 122.3328 | 122.3053 | 122.1588 | 122.1451 | 122.1313 | -122.3785 | -122.2458 | 122.2595 | 122.3053 | 42.5812 | 43.1396
1441.3125 | 122.5388 | -57.0557 | 65.1627 | -0.073471 | 0.013302 | 0.069571 | 0.065362 | -0.0022218 | 0.0030206 | 0.0033367 | -0.030517 | 0.010177 | 0.069079 | 0.060284 | -0.0065454 | 0.014778 | 0.001818 | -14.5294 | 65.1169 | -57.1564 | 65.2084 | -52.034 | -56.3461 | -56.3919 | -13.9938 | 65.0528 | -57.0923 | 65.2496 | -53.1555 | -56.4835 | -56.3782 | -0.10071 | -0.045777 | 0.045776 | 5.0217 | 0.66376 | 0.70953 | 0.76446 | 0.81024 | -0.036621 | -0.10986 | 0.086975 | 3.9001 | 0.67749 | 0.5722 | 0.71411 | 0.60883 | 5.1224 | 122.3648 | 3.9368 | 122.3419 | 122.2733 | 122.1451 | 122.1725 | 122.1085 | -122.319 | -122.2549 | 122.2641 | 122.3053 | 42.5262 | 43.0618
1442.3125 | 122.493 | -57.0465 | 65.1901 | -0.050583 | 0.015439 | 0.068716 | 0.064294 | 0.0018372 | 0.0017388 | 0.0069683 | -0.036621 | 0.0088953 | 0.069293 | 0.059644 | -0.0078272 | 0.014351 | 0.006304 | -14.5248 | 65.1306 | -57.1701 | 65.2313 | -51.9745 | -56.3095 | -56.3644 | -14.003 | 65.1077 | -57.0557 | 65.2679 | -53.1189 | -56.4468 | -56.3599 | -0.1236 | -0.05951 | 0.041198 | 5.072 | 0.68207 | 0.737 | 0.80566 | 0.8606 | -0.009155 | -0.082398 | 0.077819 | 3.9276 | 0.68665 | 0.59967 | 0.6958 | 0.60883 | 5.1956 | 122.4014 | 3.9368 | 122.3236 | 122.3007 | 122.1634 | 122.1771 | 122.1542 | -122.3602 | -122.2458 | 122.2778 | 122.3145 | 42.5217 | 43.0435
1443.3125 | 122.5616 | -57.0328 | 65.2039 | -0.065842 | 0.015225 | 0.070425 | 0.06344 | -0.0030762 | -0.0014654 | 0.0022687 | -0.012207 | 0.012313 | 0.072711 | 0.061139 | -0.0078272 | 0.013924 | 0.0039542 | -14.5157 | 65.1215 | -57.1655 | 65.2313 | -52.2491 | -56.456 | -56.282 | -14.0717 | 65.0757 | -57.0831 | 65.2679 | -53.0548 | -56.4011 | -56.3278 | -0.13275 | -0.082397 | 0.027466 | 4.7836 | 0.75073 | 0.57678 | 0.88348 | 0.70953 | -0.050354 | -0.12817 | 0.064087 | 3.978 | 0.70496 | 0.63171 | 0.75531 | 0.68207 | 4.9164 | 122.3969 | 4.0283 | 122.3511 | 122.287 | 122.1588 | 122.1542 | 122.1085 | -122.3694 | -122.287 | 122.2641 | 122.3007 | 42.5171 | 42.9611
1444.3125 | 122.4152 | -57.0786 | 65.2359 | -0.096359 | 0.015866 | 0.071921 | 0.068353 | 0.004187 | 0.0019524 | 0.0063275 | -0.14343 | 0.011886 | 0.06972 | 0.065625 | -0.008468 | 0.014138 | 0.0009634 | -14.6118 | 65.1398 | -57.1976 | 65.126 | -52.0477 | -56.4423 | -56.488 | -14.2502 | 65.1489 | -57.0923 | 65.1672 | -53.2104 | -56.6071 | -56.4468 | -0.11902 | -0.09613 | -0.10986 | 5.0308 | 0.59052 | 0.63629 | 0.70953 | 0.75531 | -0.013733 | -0.086975 | -0.068665 | 3.8681 | 0.63171 | 0.4715 | 0.64545 | 0.48523 | 5.1498 | 122.3236 | 3.8818 | 122.2595 | 122.3373 | 122.2412 | 122.2183 | 122.2275 | -122.4335 | -122.3282 | 122.2046 | 122.2458 | 42.4667 | 42.8284
1445.3125 | 122.5571 | -56.9916 | 65.213 | 0.094376 | 0.013089 | 0.071921 | 0.065362 | 0.00076902 | 0.00024344 | 0.0046185 | 0.012207 | 0.0086815 | 0.069293 | 0.065198 | -0.0086816 | 0.010933 | 0.0016044 | -14.8041 | 65.181 | -57.1701 | 65.2634 | -51.8509 | -56.25 | -56.2775 | -14.1174 | 65.1123 | -57.0236 | 65.3091 | -52.9907 | -56.3873 | -56.2958 | -0.17853 | -0.032044 | 0.050354 | 5.1407 | 0.71411 | 0.74158 | 0.89264 | 0.9201 | -0.032044 | -0.10071 | 0.09613 | 4.0009 | 0.6958 | 0.60425 | 0.72785 | 0.63629 | 5.3192 | 122.4335 | 4.0329 | 122.3328 | 122.3511 | 122.1359 | 122.1725 | 122.1039 | -122.3831 | -122.2366 | 122.2549 | 122.3007 | 42.1875 | 42.8741
1446.3125 | 122.4792 | -56.9916 | 65.2588 | -0.08873 | 0.01373 | 0.068716 | 0.064721 | -0.00051278 | 0.0023798 | 0.0022687 | -0.036621 | 0.0097497 | 0.070788 | 0.060498 | -0.0071864 | 0.011788 | 0.0024588 | -14.5981 | 65.1993 | -57.1243 | 65.2267 | -51.8417 | -56.2454 | -56.3232 | -14.2273 | 65.1352 | -57.0099 | 65.2588 | -53.0228 | -56.4239 | -56.3278 | -0.13275 | -0.059509 | -0.032043 | 5.1498 | 0.66833 | 0.74616 | 0.80109 | 0.87891 | -0.018311 | -0.1236 | 0 | 3.9688 | 0.66376 | 0.56763 | 0.68207 | 0.58594 | 5.2826 | 122.3511 | 3.9871 | 122.2687 | 122.3236 | 122.1451 | 122.1909 | 122.1268 | -122.3831 | -122.2687 | 122.2183 | 122.2504 | 42.3935 | 42.7643
1447.3125 | 122.4655 | -57.0053 | 65.2817 | -0.073471 | 0.015439 | 0.070425 | 0.066217 | 0.00076902 | 0.004516 | 0.0041913 | -0.024414 | 0.010391 | 0.071429 | 0.06178 | -0.0059046 | 0.014138 | 0.0037406 | -14.6072 | 65.1901 | -57.1152 | 65.2542 | -51.828 | -56.2042 | -56.3004 | -14.2685 | 65.1764 | -57.0053 | 65.2679 | -53.009 | -56.4377 | -56.3278 | -0.10986 | -0.091552 | -0.027466 | 5.1773 | 0.70496 | 0.80109 | 0.81482 | 0.91095 | 0 | -0.10528 | -0.013733 | 3.9963 | 0.67749 | 0.56763 | 0.67749 | 0.56763 | 5.2872 | 122.3694 | 3.9963 | 122.2733 | 122.3053 | 122.1817 | 122.1954 | 122.1817 | -122.3969 | -122.287 | 122.2595 | 122.2733 | 42.3981 | 42.7368
1448.3125 | 122.4335 | -57.0145 | 65.3046 | -0.042954 | 0.013943 | 0.069143 | 0.065149 | 0.0044006 | 0.003875 | 0.0012005 | -0.039673 | 0.010818 | 0.070575 | 0.067975 | -0.0078272 | 0.015419 | 0.0060904 | -14.6942 | 65.2451 | -57.1243 | 65.1764 | -51.8738 | -56.3095 | -56.3644 | -14.241 | 65.2451 | -56.9595 | 65.2451 | -53.0457 | -56.4468 | -56.3507 | -0.10986 | -0.059509 | -0.12817 | 5.1407 | 0.65002 | 0.70496 | 0.75989 | 0.81482 | 0.054931 | -0.059509 | -0.059509 | 3.9688 | 0.66376 | 0.56763 | 0.60883 | 0.5127 | 5.2506 | 122.3007 | 3.9139 | 122.2046 | 122.3694 | 122.2046 | 122.2595 | 122.2595 | -122.4289 | -122.2641 | 122.1909 | 122.2595 | 42.3203 | 42.7734
1449.3125 | 122.4655 | -57.0145 | 65.2771 | -0.11925 | 0.014798 | 0.06893 | 0.06878 | -0.00051278 | 0.0023798 | 0.0037639 | -0.10681 | 0.0121 | 0.070575 | 0.071606 | -0.009109 | 0.016701 | 0.001177 | -14.6713 | 65.2222 | -57.1426 | 65.3 | -51.796 | -56.2637 | -56.3187 | -14.4196 | 65.1947 | -57.019 | 65.2725 | -52.9633 | -56.4468 | -56.3278 | -0.12817 | -0.054932 | 0.022888 | 5.2185 | 0.6958 | 0.75073 | 0.82397 | 0.87891 | -0.004578 | -0.082398 | -0.004578 | 4.0512 | 0.68664 | 0.56763 | 0.69122 | 0.57221 | 5.3467 | 122.4426 | 4.0558 | 122.2916 | 122.3648 | 122.2137 | 122.2366 | 122.2092 | -122.4197 | -122.2961 | 122.3145 | 122.287 | 42.3431 | 42.5949
1450.3125 | 122.438 | -56.9778 | 65.2908 | -0.050583 | 0.012234 | 0.072561 | 0.064935 | -0.0022218 | 0.002166 | 0.0029095 | -0.012207 | 0.011032 | 0.072497 | 0.062207 | -0.0080408 | 0.014565 | 0.0030996 | -14.6988 | 65.2222 | -57.0831 | 65.2313 | -51.7273 | -56.1905 | -56.2866 | -14.502 | 65.2313 | -57.0053 | 65.2588 | -52.9312 | -56.3919 | -56.2912 | -0.10529 | -0.068665 | -0.05951 | 5.2505 | 0.69122 | 0.78735 | 0.79651 | 0.89264 | -0.027466 | -0.05951 | -0.032044 | 4.0466 | 0.68664 | 0.58594 | 0.71411 | 0.6134 | 5.3558 | 122.3145 | 4.0741 | 122.2641 | 122.3053 | 122.2366 | 122.2 | 122.2092 | -122.374 | -122.2961 | 122.2092 | 122.2366 | 42.2791 | 42.4759
1451.3125 | 122.4701 | -56.9733 | 65.3549 | -0.058212 | 0.01437 | 0.069571 | 0.064935 | -0.0024354 | 0.0025934 | 0.0031231 | -0.082397 | 0.011672 | 0.070361 | 0.06413 | -0.008468 | 0.015206 | 0.0058768 | -14.7675 | 65.2725 | -57.1152 | 65.1947 | -51.7822 | -56.2637 | -56.3278 | -14.6118 | 65.2222 | -57.0099 | 65.2725 | -52.9312 | -56.4148 | -56.2912 | -0.14191 | -0.082397 | -0.16022 | 5.191 | 0.64545 | 0.70953 | 0.78735 | 0.85144 | -0.036621 | -0.13275 | -0.082397 | 4.0421 | 0.68207 | 0.55847 | 0.71869 | 0.59509 | 5.3329 | 122.3099 | 4.0787 | 122.2824 | 122.3877 | 122.2321 | 122.2458 | 122.1954 | -122.4701 | -122.3648 | 122.168 | 122.2458 | 42.2058 | 42.3615
1452.3125 | 122.5754 | -56.9595 | 65.2359 | -0.10399 | 0.01373 | 0.071707 | 0.067712 | 0.0029052 | 0.002807 | 0.0048321 | -0.036621 | 0.011459 | 0.070361 | 0.055371 | -0.008468 | 0.015419 | 0.0024588 | -14.7812 | 65.1993 | -57.106 | 65.2679 | -51.6769 | -56.2088 | -56.25 | -14.566 | 65.1169 | -57.0328 | 65.3 | -52.8168 | -56.3324 | -56.218 | -0.14648 | -0.036621 | 0.032043 | 5.2826 | 0.70953 | 0.75073 | 0.85602 | 0.89722 | -0.073242 | -0.11902 | 0.064087 | 4.1428 | 0.74158 | 0.62714 | 0.81482 | 0.70038 | 5.4291 | 122.374 | 4.216 | 122.3328 | 122.3053 | 122.1497 | 122.1588 | 122.0764 | -122.3419 | -122.2687 | 122.2275 | 122.2595 | 42.1783 | 42.3935
1453.3125 | 122.4197 | -56.9687 | 65.3046 | -0.073471 | 0.013089 | 0.068503 | 0.065576 | -0.002649 | 0.0049432 | 0.0050457 | -0.015259 | 0.012741 | 0.070147 | 0.062421 | -0.0074 | 0.015419 | 0.0007498 | -14.7903 | 65.2863 | -57.074 | 65.2496 | -51.6678 | -56.1813 | -56.2592 | -14.6255 | 65.2451 | -56.9687 | 65.2634 | -52.8671 | -56.3873 | -56.2866 | -0.10529 | -0.01831 | -0.054931 | 5.3009 | 0.70953 | 0.78735 | 0.81482 | 0.89264 | 0 | -0.059509 | -0.041198 | 4.1016 | 0.68207 | 0.58136 | 0.68207 | 0.58136 | 5.4062 | 122.3236 | 4.1016 | 122.2321 | 122.3602 | 122.2137 | 122.2549 | 122.2137 | -122.3785 | -122.2733 | 122.2183 | 122.2321 | 42.1783 | 42.3431
1454.3125 | 122.5433 | -56.9595 | 65.332 | -0.027695 | 0.01672 | 0.071493 | 0.067071 | -0.00093998 | 0.0017388 | 0.0048321 | -0.082397 | 0.013595 | 0.070361 | 0.070752 | -0.0093226 | 0.015847 | 0.0009634 | -14.8041 | 65.2817 | -57.0694 | 65.2588 | -51.6266 | -56.1722 | -56.2729 | -14.6622 | 65.2405 | -56.987 | 65.3183 | -52.9083 | -56.5338 | -56.3873 | -0.10986 | -0.050354 | -0.073242 | 5.3329 | 0.68665 | 0.78735 | 0.79651 | 0.89722 | -0.027466 | -0.091552 | -0.013733 | 4.0512 | 0.5722 | 0.42572 | 0.59967 | 0.45319 | 5.4428 | 122.3282 | 4.0787 | 122.3053 | 122.3511 | 122.2275 | 122.2412 | 122.2 | -122.4014 | -122.319 | 122.2183 | 122.2778 | 42.1555 | 42.2974
1455.3125 | 122.4609 | -56.9275 | 65.3366 | -0.027695 | 0.01373 | 0.070212 | 0.067926 | -0.0011536 | 0.003875 | 0.0035503 | -0.042725 | 0.010818 | 0.071002 | 0.070111 | -0.008468 | 0.015419 | 0.0041678 | -14.8407 | 65.3091 | -57.074 | 65.2451 | -51.6403 | -56.1722 | -56.2546 | -14.74 | 65.2817 | -56.955 | 65.3229 | -52.7939 | -56.337 | -56.2271 | -0.14648 | -0.027466 | -0.091553 | 5.2872 | 0.67291 | 0.75531 | 0.8194 | 0.90179 | -0.027466 | -0.054932 | -0.013733 | 4.1336 | 0.70038 | 0.59051 | 0.72784 | 0.61798 | 5.4337 | 122.319 | 4.1611 | 122.2778 | 122.3831 | 122.2366 | 122.2366 | 122.2092 | -122.4106 | -122.2916 | 122.1725 | 122.2504 | 42.0868 | 42.1875
1456.3125 | 122.4792 | -56.9138 | 65.3458 | -0.073471 | 0.015225 | 0.071921 | 0.068353 | 0.0011962 | 0.0034478 | 0.0039777 | -0.039673 | 0.014022 | 0.070788 | 0.06477 | -0.0093226 | 0.015206 | 0.0030996 | -14.8361 | 65.3046 | -57.0419 | 65.2679 | -51.5762 | -56.1172 | -56.2363 | -14.7766 | 65.2771 | -56.9321 | 65.3412 | -52.7573 | -56.3187 | -56.1859 | -0.12817 | -0.041199 | -0.07782 | 5.3375 | 0.67749 | 0.79651 | 0.80566 | 0.92468 | -0.018311 | -0.068664 | -0.004577 | 4.1565 | 0.72784 | 0.59509 | 0.74616 | 0.6134 | 5.4657 | 122.3099 | 4.1748 | 122.2733 | 122.3465 | 122.2092 | 122.2183 | 122.1909 | -122.3877 | -122.2778 | 122.1817 | 122.2549 | 42.0776 | 42.1371
1457.3125 | 122.4701 | -56.9275 | 65.3229 | -0.11925 | 0.015011 | 0.07128 | 0.067499 | 0.0011962 | 0.0023798 | 0.0063275 | -0.048828 | 0.012527 | 0.071643 | 0.062207 | -0.0074 | 0.014778 | 0.000109 | -14.8911 | 65.2771 | -57.0923 | 65.2084 | -51.6037 | -56.2088 | -56.2683 | -14.8682 | 65.2496 | -56.9687 | 65.3046 | -52.7939 | -56.369 | -56.218 | -0.16479 | -0.045776 | -0.11444 | 5.3238 | 0.65918 | 0.71869 | 0.82397 | 0.88348 | -0.041199 | -0.073242 | -0.018311 | 4.1336 | 0.70953 | 0.55847 | 0.75073 | 0.59967 | 5.4886 | 122.3007 | 4.1748 | 122.2733 | 122.3694 | 122.2183 | 122.2046 | 122.1771 | -122.4152 | -122.2916 | 122.1359 | 122.2321 | 42.0364 | 42.0593
1458.3125 | 122.4701 | -56.9 | 65.3595 | -0.058212 | 0.013302 | 0.069571 | 0.065576 | 0.0011962 | 0.0017388 | 0.0048321 | -0.067139 | 0.011032 | 0.071216 | 0.058789 | -0.0086816 | 0.013924 | 0.001177 | -14.8636 | 65.3503 | -57.0374 | 65.2817 | -51.5167 | -56.0761 | -56.1859 | -14.8544 | 65.3091 | -56.9138 | 65.3503 | -52.6886 | -56.2775 | -56.1676 | -0.13733 | -0.009155 | -0.07782 | 5.3833 | 0.71411 | 0.82397 | 0.85144 | 0.9613 | -0.013733 | -0.050354 | -0.009155 | 4.2114 | 0.73242 | 0.62256 | 0.74615 | 0.63629 | 5.5206 | 122.319 | 4.2252 | 122.2641 | 122.3877 | 122.2229 | 122.2504 | 122.2092 | -122.3969 | -122.2733 | 122.1817 | 122.2504 | 42.0364 | 42.0456
1459.3125 | 122.4152 | -56.9275 | 65.3458 | -0.081101 | 0.014798 | 0.074484 | 0.06579 | 0.002478 | 0.0034478 | 0.0069683 | -0.094604 | 0.011672 | 0.07207 | 0.063275 | -0.0082544 | 0.016701 | 0.0016044 | -14.9094 | 65.3229 | -57.074 | 65.2451 | -51.5442 | -56.1722 | -56.2546 | -15.0055 | 65.2771 | -56.955 | 65.2817 | -52.771 | -56.3965 | -56.2363 | -0.14648 | -0.022888 | -0.10071 | 5.3833 | 0.67291 | 0.75531 | 0.8194 | 0.90179 | -0.027466 | -0.068664 | -0.064087 | 4.1565 | 0.69122 | 0.53101 | 0.71869 | 0.55847 | 5.5298 | 122.319 | 4.184 | 122.2366 | 122.3969 | 122.2321 | 122.2504 | 122.2046 | -122.4197 | -122.3007 | 122.1725 | 122.2092 | 42.0181 | 41.922
1460.3125 | 122.4747 | -56.8634 | 65.3824 | -0.08873 | 0.014157 | 0.071707 | 0.063867 | 0.00034182 | 0.005584 | 0.0065411 | -0.039673 | 0.011672 | 0.071643 | 0.064557 | -0.008468 | 0.014565 | -0.000532 | -14.8773 | 65.3687 | -57.0007 | 65.3046 | -51.4114 | -56.0394 | -56.1401 | -14.9368 | 65.3 | -56.8954 | 65.3778 | -52.6245 | -56.2546 | -56.1356 | -0.13733 | -0.013733 | -0.07782 | 5.452 | 0.72327 | 0.82397 | 0.86059 | 0.9613 | -0.032044 | -0.082397 | -0.004577 | 4.2389 | 0.72784 | 0.60882 | 0.75989 | 0.64087 | 5.5893 | 122.3053 | 4.2709 | 122.2733 | 122.3694 | 122.1954 | 122.2321 | 122.1634 | -122.3831 | -122.2778 | 122.168 | 122.2412 | 41.9861 | 41.9266
1461.3125 | 122.4747 | -56.8726 | 65.4282 | -0.11925 | 0.013516 | 0.074698 | 0.066217 | -0.00051278 | 0.0057976 | 0.0061139 | -0.05188 | 0.013595 | 0.070788 | 0.070752 | -0.006759 | 0.018196 | 0.002886 | -14.9918 | 65.3046 | -57.019 | 65.3687 | -51.3519 | -56.0165 | -56.1127 | -14.9414 | 65.3366 | -56.8863 | 65.4053 | -52.5925 | -56.2363 | -56.1127 | -0.14648 | -0.1236 | -0.05951 | 5.5206 | 0.75989 | 0.85602 | 0.90637 | 1.0025 | -0.013733 | -0.091553 | -0.022889 | 4.2801 | 0.75989 | 0.63629 | 0.77362 | 0.65002 | 5.6671 | 122.3877 | 4.2938 | 122.2916 | 122.3236 | 122.2229 | 122.1771 | 122.2092 | -122.4472 | -122.3145 | 122.2412 | 122.2778 | 41.8808 | 41.9312
1462.3125 | 122.4976 | -56.8726 | 65.3549 | -0.08873 | 0.013516 | 0.072775 | 0.06344 | -0.0011536 | 0.0030206 | 0.0039777 | 0.067139 | 0.012527 | 0.071216 | 0.053448 | -0.0080408 | 0.012215 | 0.0022452 | -14.8956 | 65.3366 | -56.9824 | 65.4007 | -51.1597 | -56.131 | -56.1951 | -15.0833 | 65.2634 | -56.9046 | 65.387 | -52.5787 | -56.1951 | -56.0898 | -0.10986 | -0.01831 | 0.045777 | 5.7129 | 0.67749 | 0.74158 | 0.78735 | 0.85144 | -0.032043 | -0.091552 | 0.032044 | 4.2938 | 0.78278 | 0.67749 | 0.81482 | 0.70953 | 5.8228 | 122.3831 | 4.3259 | 122.2916 | 122.319 | 122.168 | 122.2092 | 122.1359 | -122.3373 | -122.2595 | 122.2733 | 122.2595 | 41.9769 | 41.7892
1463.3125 | 122.4335 | -56.8451 | 65.3961 | -0.042954 | 0.016507 | 0.070639 | 0.064935 | 0.0011962 | 0.0025934 | 0.0022687 | -0.045776 | 0.010604 | 0.072284 | 0.064984 | -0.0074 | 0.015847 | 0.0071586 | -14.9094 | 65.3687 | -56.9733 | 65.3503 | -51.2741 | -55.9891 | -56.0898 | -15.0467 | 65.3732 | -56.8542 | 65.4327 | -52.5192 | -56.2088 | -56.0989 | -0.12817 | -0.027466 | -0.045776 | 5.571 | 0.75531 | 0.85602 | 0.88348 | 0.98419 | -0.009155 | -0.022888 | 0.036621 | 4.3259 | 0.74616 | 0.63629 | 0.75531 | 0.64545 | 5.6992 | 122.3236 | 4.335 | 122.287 | 122.3419 | 122.2275 | 122.2137 | 122.2183 | -122.3694 | -122.2504 | 122.1954 | 122.2778 | 41.9357 | 41.7984
1464.3125 | 122.4472 | -56.8359 | 65.4419 | -0.042954 | 0.016293 | 0.07128 | 0.066858 | -0.0024354 | 0.006225 | 0.0050457 | -0.054932 | 0.013168 | 0.072284 | 0.061566 | -0.0080408 | 0.016274 | 0.004595 | -14.9048 | 65.387 | -56.955 | 65.3778 | -51.2421 | -55.9021 | -56.0806 | -15.1291 | 65.3458 | -56.868 | 65.419 | -52.478 | -56.3416 | -56.1951 | -0.11902 | -0.054932 | -0.064087 | 5.5939 | 0.75531 | 0.93384 | 0.87433 | 1.0529 | -0.032044 | -0.096131 | -0.022889 | 4.3579 | 0.64087 | 0.49438 | 0.67291 | 0.52643 | 5.7129 | 122.3328 | 4.39 | 122.287 | 122.3419 | 122.2137 | 122.2229 | 122.1817 | -122.3969 | -122.3099 | 122.2137 | 122.2549 | 41.9312 | 41.7068
1465.3125 | 122.4335 | -56.868 | 65.4465 | -0.058212 | 0.015439 | 0.071493 | 0.067499 | 0.0033324 | 0.0023798 | 0.0026959 | -0.05188 | 0.012313 | 0.070575 | 0.061566 | -0.009109 | 0.016915 | 0.0009634 | -14.978 | 65.4007 | -56.9733 | 65.332 | -51.265 | -56.0532 | -56.1264 | -15.2527 | 65.3412 | -56.8726 | 65.3778 | -52.5513 | -56.2592 | -56.1172 | -0.10529 | -0.045776 | -0.11444 | 5.603 | 0.74158 | 0.81482 | 0.84686 | 0.9201 | -0.004578 | -0.10528 | -0.068664 | 4.3167 | 0.75073 | 0.60883 | 0.75531 | 0.6134 | 5.7083 | 122.3053 | 4.3213 | 122.2504 | 122.374 | 122.2137 | 122.2687 | 122.2092 | -122.4197 | -122.319 | 122.2 | 122.2458 | 41.89 | 41.6153
1466.3125 | 122.4518 | -56.8314 | 65.4327 | -0.050583 | 0.014798 | 0.070852 | 0.067499 | 0.0052552 | 0.0047296 | 0.0063275 | -0.048828 | 0.0121 | 0.07207 | 0.065839 | -0.0076136 | 0.016701 | 0.0003226 | -14.9414 | 65.3732 | -56.9412 | 65.3549 | -51.21 | -55.9708 | -56.0715 | -15.2527 | 65.3412 | -56.8588 | 65.4144 | -52.4643 | -56.1996 | -56.0486 | -0.10986 | -0.059509 | -0.07782 | 5.6213 | 0.75989 | 0.8606 | 0.86975 | 0.97046 | -0.027466 | -0.091552 | -0.01831 | 4.3671 | 0.78278 | 0.63171 | 0.81024 | 0.65918 | 5.7312 | 122.2961 | 4.3945 | 122.2733 | 122.3145 | 122.2 | 122.2046 | 122.1725 | -122.374 | -122.2916 | 122.1863 | 122.2458 | 41.89 | 41.5787
1467.3125 | 122.4747 | -56.8268 | 65.4327 | -0.073471 | 0.015652 | 0.070639 | 0.067712 | -0.00093998 | -0.00018376 | 0.0063275 | -0.015259 | 0.013809 | 0.070788 | 0.06477 | -0.0061182 | 0.016915 | 0.005236 | -15.0467 | 65.3915 | -56.9778 | 65.3091 | -51.2238 | -56.0394 | -56.1035 | -15.358 | 65.3458 | -56.8771 | 65.4099 | -52.4689 | -56.2042 | -56.0806 | -0.15106 | -0.041198 | -0.1236 | 5.603 | 0.72327 | 0.78735 | 0.87433 | 0.93841 | -0.050354 | -0.086975 | -0.022888 | 4.3579 | 0.74616 | 0.62256 | 0.79651 | 0.67291 | 5.7541 | 122.287 | 4.4083 | 122.287 | 122.3694 | 122.2229 | 122.2183 | 122.1725 | -122.4106 | -122.3099 | 122.1359 | 122.2366 | 41.7801 | 41.4688
1468.3125 | 122.4564 | -56.8451 | 65.4465 | -0.081101 | 0.015439 | 0.07128 | 0.066858 | 0.0050414 | 0.0047296 | 0.0044049 | -0.021362 | 0.014663 | 0.071429 | 0.067334 | -0.0086816 | 0.014138 | 0.0005362 | -15.0192 | 65.3915 | -56.9504 | 65.3595 | -51.1505 | -55.957 | -56.0577 | -15.3625 | 65.3778 | -56.8497 | 65.3961 | -52.4368 | -56.2042 | -56.0577 | -0.10529 | -0.054931 | -0.086975 | 5.6946 | 0.78735 | 0.88806 | 0.89264 | 0.99335 | -0.004577 | -0.068664 | -0.050354 | 4.4083 | 0.78735 | 0.64087 | 0.79193 | 0.64545 | 5.7999 | 122.3099 | 4.4128 | 122.2458 | 122.3419 | 122.2275 | 122.2366 | 122.2229 | -122.3969 | -122.2961 | 122.2046 | 122.2412 | 41.8259 | 41.4825
1469.3125 | 122.5708 | -56.8039 | 65.3915 | -0.058212 | 0.017361 | 0.072989 | 0.064935 | -0.00029898 | 0.0036614 | 0.0035503 | 0.012207 | 0.013168 | 0.071002 | 0.061139 | -0.0074 | 0.015206 | 0.0048086 | -15.0238 | 65.3641 | -56.8954 | 65.4144 | -51.0544 | -55.8929 | -55.9708 | -15.3305 | 65.3 | -56.8268 | 65.4922 | -52.327 | -56.0852 | -55.9616 | -0.091553 | -0.027466 | 0.022888 | 5.7495 | 0.83313 | 0.91095 | 0.92468 | 1.0025 | -0.022888 | -0.091553 | 0.10071 | 4.4769 | 0.84228 | 0.71869 | 0.86517 | 0.74158 | 5.8411 | 122.3099 | 4.4998 | 122.319 | 122.2595 | 122.1268 | 122.168 | 122.1039 | -122.287 | -122.2183 | 122.2183 | 122.2961 | 41.7801 | 41.4734
1470.3125 | 122.4518 | -56.8314 | 65.4694 | -0.042954 | 0.015652 | 0.071921 | 0.067499 | 0.0039734 | 0.002807 | 0.0061139 | -0.045776 | 0.013809 | 0.07207 | 0.06413 | -0.0093226 | 0.017769 | 0.0069448 | -15.0513 | 65.4053 | -56.9366 | 65.3961 | -51.091 | -55.9433 | -56.0303 | -15.4861 | 65.387 | -56.813 | 65.4282 | -52.3773 | -56.1951 | -56.0349 | -0.10529 | -0.064087 | -0.073242 | 5.7404 | 0.80109 | 0.88806 | 0.90637 | 0.99335 | 0.018311 | -0.082397 | -0.041198 | 4.454 | 0.79651 | 0.63629 | 0.7782 | 0.61798 | 5.8456 | 122.3328 | 4.4357 | 122.2412 | 122.3419 | 122.2 | 122.2366 | 122.2183 | -122.406 | -122.2824 | 122.2275 | 122.2595 | 41.7801 | 41.3452
1471.3125 | 122.4472 | -56.8222 | 65.4648 | -0.11162 | 0.01672 | 0.073202 | 0.066858 | 0.0033324 | 0.0043024 | 0.0071819 | -0.05188 | 0.012741 | 0.072925 | 0.065198 | -0.0069726 | 0.014565 | 0.000109 | -15.0787 | 65.419 | -56.9366 | 65.3687 | -51.059 | -55.9433 | -56.0349 | -15.5273 | 65.4099 | -56.8222 | 65.419 | -52.3636 | -56.1859 | -56.0257 | -0.11444 | -0.045777 | -0.096131 | 5.7632 | 0.78735 | 0.87891 | 0.90179 | 0.99335 | 0 | -0.054932 | -0.045777 | 4.4586 | 0.79651 | 0.63629 | 0.79651 | 0.63629 | 5.8777 | 122.3053 | 4.4586 | 122.2412 | 122.3557 | 122.2321 | 122.2412 | 122.2321 | -122.4014 | -122.287 | 122.1909 | 122.2412 | 41.7435 | 41.2949
1472.3125 | 122.4335 | -56.7993 | 65.4785 | -0.073471 | 0.015011 | 0.072775 | 0.067926 | -0.00051278 | 0.0068658 | 0.0063275 | -0.036621 | 0.013168 | 0.07207 | 0.067975 | -0.0074 | 0.016487 | 0.001177 | -15.1428 | 65.4327 | -56.9229 | 65.3412 | -51.0498 | -55.9433 | -56.0303 | -15.6281 | 65.4007 | -56.8222 | 65.4282 | -52.327 | -56.1722 | -56.0211 | -0.1236 | -0.045777 | -0.13733 | 5.7495 | 0.76904 | 0.85602 | 0.89264 | 0.97962 | -0.022889 | -0.07782 | -0.050354 | 4.4724 | 0.7782 | 0.62714 | 0.80109 | 0.65002 | 5.8731 | 122.2641 | 4.4952 | 122.2504 | 122.3557 | 122.2229 | 122.2321 | 122.2 | -122.4014 | -122.3007 | 122.1405 | 122.2275 | 41.6565 | 41.1713
1473.3125 | 122.438 | -56.7902 | 65.4877 | -0.081101 | 0.017361 | 0.071707 | 0.067071 | -0.0013672 | 0.004516 | 0.0069683 | -0.061035 | 0.013168 | 0.070361 | 0.06413 | -0.0078272 | 0.018624 | 0.0033134 | -15.184 | 65.451 | -56.9504 | 65.3275 | -51.0727 | -55.9662 | -56.0532 | -15.9027 | 65.3503 | -56.8634 | 65.4053 | -52.24 | -56.1768 | -56.0486 | -0.16022 | -0.036621 | -0.16022 | 5.7175 | 0.737 | 0.82397 | 0.89722 | 0.98419 | -0.073242 | -0.13733 | -0.082398 | 4.5502 | 0.74158 | 0.6134 | 0.81482 | 0.68664 | 5.8777 | 122.2778 | 4.6234 | 122.2687 | 122.4014 | 122.2137 | 122.2412 | 122.1405 | -122.438 | -122.3511 | 122.1176 | 122.1954 | 41.6061 | 40.8875
1474.3125 | 122.4838 | -56.7673 | 65.4648 | -0.13451 | 0.014157 | 0.070639 | 0.067285 | -8.538e-05 | 0.0049432 | 0.0031231 | -0.0091553 | 0.014236 | 0.073138 | 0.066693 | -0.0071864 | 0.015206 | 0.0043814 | -15.2069 | 65.4419 | -56.9275 | 65.3503 | -50.9903 | -55.9433 | -56.012 | -15.6967 | 65.4053 | -56.8405 | 65.4282 | -52.2766 | -56.1172 | -55.9799 | -0.16022 | -0.022888 | -0.11444 | 5.777 | 0.75531 | 0.82398 | 0.91553 | 0.98419 | -0.073242 | -0.05951 | -0.036621 | 4.4907 | 0.78735 | 0.65002 | 0.8606 | 0.72327 | 5.9372 | 122.2778 | 4.5639 | 122.2687 | 122.3694 | 122.2458 | 122.2092 | 122.1725 | -122.3923 | -122.3053 | 122.1176 | 122.1954 | 41.5604 | 41.0706
1475.3125 | 122.4426 | -56.7947 | 65.5106 | -0.073471 | 0.016507 | 0.070425 | 0.069208 | -0.0028626 | 0.002807 | 0.0063275 | -0.054932 | 0.012527 | 0.071216 | 0.06477 | -0.009109 | 0.015633 | 0.001177 | -15.2573 | 65.4602 | -56.8909 | 65.4785 | -51.0773 | -55.8792 | -55.9204 | -15.7425 | 65.4282 | -56.7947 | 65.4419 | -52.2537 | -56.1356 | -55.9799 | -0.09613 | -0.050354 | -0.032043 | 5.7175 | 0.87433 | 0.91553 | 0.97046 | 1.0117 | 0 | -0.082397 | -0.068664 | 4.541 | 0.81482 | 0.65918 | 0.81482 | 0.65918 | 5.8136 | 122.3694 | 4.541 | 122.2366 | 122.3511 | 122.2229 | 122.2549 | 122.2229 | -122.4014 | -122.3053 | 122.2733 | 122.2366 | 41.5375 | 41.0522
1476.3125 | 122.4838 | -56.7627 | 65.4877 | -0.10399 | 0.015439 | 0.071707 | 0.066644 | 0.0033324 | 0.0047296 | 0.0054729 | -0.012207 | 0.014663 | 0.070575 | 0.062848 | -0.0078272 | 0.014565 | 0.0007498 | -15.271 | 65.4648 | -56.8909 | 65.3732 | -50.8987 | -55.8609 | -55.9479 | -15.7471 | 65.4282 | -56.7993 | 65.4785 | -52.1484 | -56.0532 | -55.9296 | -0.12817 | -0.022888 | -0.11444 | 5.864 | 0.81482 | 0.90179 | 0.94299 | 1.03 | -0.036621 | -0.059509 | -0.009155 | 4.6143 | 0.83313 | 0.70953 | 0.86975 | 0.74615 | 5.9921 | 122.2641 | 4.6509 | 122.2778 | 122.3557 | 122.2275 | 122.2275 | 122.1909 | -122.3785 | -122.287 | 122.1359 | 122.2412 | 41.4917 | 41.0156
1477.3125 | 122.4564 | -56.781 | 65.4877 | -0.17265 | 0.016079 | 0.069143 | 0.067712 | -0.00029898 | 0.0032342 | 0.0071819 | -0.033569 | 0.013595 | 0.071216 | 0.064557 | -0.0082544 | 0.017769 | 0.0007498 | -15.2298 | 65.4739 | -56.8954 | 65.3503 | -50.8896 | -55.8975 | -55.9891 | -15.8386 | 65.4236 | -56.7993 | 65.4327 | -52.1851 | -56.1264 | -55.9753 | -0.11444 | -0.013733 | -0.13733 | 5.8914 | 0.79193 | 0.88348 | 0.90637 | 0.99792 | -0.01831 | -0.064087 | -0.054932 | 4.5959 | 0.80566 | 0.6546 | 0.82397 | 0.67291 | 6.0059 | 122.2458 | 4.6143 | 122.2321 | 122.3694 | 122.2229 | 122.2549 | 122.2046 | -122.3831 | -122.287 | 122.1313 | 122.2137 | 41.5512 | 40.9424
1478.3125 | 122.5159 | -56.7581 | 65.4739 | -0.11162 | 0.017148 | 0.071066 | 0.065149 | 0.0011962 | 0.003875 | 0.0048321 | -0.015259 | 0.0121 | 0.071856 | 0.065839 | -0.0069726 | 0.015206 | 0.001818 | -15.3442 | 65.4419 | -56.8954 | 65.3915 | -50.8438 | -55.838 | -55.9387 | -15.8295 | 65.3915 | -56.8085 | 65.4968 | -52.0752 | -56.0028 | -55.8838 | -0.13733 | -0.032043 | -0.082397 | 5.9143 | 0.8194 | 0.92011 | 0.95673 | 1.0574 | -0.050354 | -0.082397 | 0.022888 | 4.6829 | 0.87433 | 0.75531 | 0.92468 | 0.80566 | 6.0516 | 122.287 | 4.7333 | 122.3053 | 122.3373 | 122.2 | 122.2 | 122.1497 | -122.3694 | -122.2824 | 122.1497 | 122.2549 | 41.4139 | 40.9287
1479.3125 | 122.5891 | -56.7215 | 65.4831 | -0.058212 | 0.014584 | 0.07128 | 0.063012 | -0.0039306 | 0.0030206 | 0.0059003 | 0.073242 | 0.014236 | 0.071429 | 0.066907 | -0.0076136 | 0.014992 | -0.0018136 | -15.2893 | 65.4556 | -56.8497 | 65.5014 | -50.6332 | -55.6686 | -55.7877 | -15.683 | 65.4144 | -56.7307 | 65.5792 | -51.9287 | -55.8609 | -55.806 | -0.12817 | -0.027466 | 0.018311 | 6.0883 | 0.93384 | 1.0529 | 1.062 | 1.181 | -0.009155 | -0.068664 | 0.096131 | 4.7928 | 0.91553 | 0.8606 | 0.92468 | 0.86975 | 6.2164 | 122.3511 | 4.8019 | 122.3099 | 122.3053 | 122.1451 | 122.1771 | 122.1359 | -122.3328 | -122.2137 | 122.2229 | 122.3007 | 41.4322 | 41.0385
1480.3125 | 122.4609 | -56.7947 | 65.4968 | -0.073471 | 0.015652 | 0.07128 | 0.067926 | -0.0011536 | 0.0032342 | 0.0050457 | -0.033569 | 0.012527 | 0.070575 | 0.066907 | -0.0078272 | 0.016487 | 0.0060904 | -15.4037 | 65.4465 | -56.9046 | 65.3824 | -50.8026 | -55.8563 | -55.9296 | -15.9439 | 65.4327 | -56.8039 | 65.4602 | -52.0981 | -56.0623 | -55.9341 | -0.10986 | -0.050354 | -0.11444 | 5.9921 | 0.86517 | 0.93842 | 0.97504 | 1.0483 | -0.009155 | -0.064087 | -0.036621 | 4.6967 | 0.8606 | 0.73242 | 0.86975 | 0.74158 | 6.102 | 122.287 | 4.7058 | 122.2641 | 122.3511 | 122.2366 | 122.2412 | 122.2275 | -122.4014 | -122.3007 | 122.1771 | 122.2549 | 41.391 | 40.8508
1481.3125 | 122.5296 | -56.7169 | 65.4739 | -0.11925 | 0.016293 | 0.072561 | 0.067926 | -0.00029898 | 0.0025934 | 0.0069683 | -0.0061035 | 0.0121 | 0.070788 | 0.068188 | -0.010177 | 0.01606 | 0.0020316 | -15.3625 | 65.4053 | -56.8726 | 65.5426 | -50.7202 | -55.719 | -55.7922 | -15.834 | 65.387 | -56.7398 | 65.5701 | -51.9562 | -55.925 | -55.8014 | -0.15564 | -0.068665 | 0.068665 | 5.9967 | 0.92468 | 0.99792 | 1.0803 | 1.1536 | -0.022888 | -0.086975 | 0.09613 | 4.7607 | 0.91553 | 0.79193 | 0.93841 | 0.81482 | 6.1523 | 122.4152 | 4.7836 | 122.3099 | 122.2778 | 122.1268 | 122.1222 | 122.1039 | -122.3465 | -122.2137 | 122.2595 | 122.287 | 41.3544 | 40.8829
1482.3125 | 122.5342 | -56.6986 | 65.4922 | -0.17265 | 0.019497 | 0.074057 | 0.066003 | 0.0022644 | 0.0040888 | 0.0082501 | 0.012207 | 0.014236 | 0.071856 | 0.065411 | -0.008468 | 0.014565 | 0.0054496 | -15.5914 | 65.387 | -56.8451 | 65.538 | -50.5646 | -55.719 | -55.7693 | -15.8936 | 65.387 | -56.7581 | 65.5838 | -51.9058 | -55.9113 | -55.7968 | -0.14648 | -0.10529 | 0.045776 | 6.134 | 0.92926 | 0.97961 | 1.0757 | 1.1261 | -0.05951 | -0.10529 | 0.091552 | 4.7928 | 0.90179 | 0.78735 | 0.9613 | 0.84686 | 6.2805 | 122.3831 | 4.8523 | 122.3419 | 122.2321 | 122.1451 | 122.0856 | 122.0856 | -122.3373 | -122.2504 | 122.2366 | 122.2824 | 41.1072 | 40.8051
1483.3125 | 122.5479 | -56.7078 | 65.4785 | -0.10399 | 0.018002 | 0.072775 | 0.06878 | -0.00072638 | 0.0051568 | 0.0071819 | -0.030517 | 0.012741 | 0.070361 | 0.064343 | -0.0088952 | 0.01371 | 0.0039542 | -15.4449 | 65.4373 | -56.8634 | 65.4694 | -50.6058 | -55.7236 | -55.8289 | -15.9439 | 65.4099 | -56.7444 | 65.5701 | -51.8921 | -55.9067 | -55.7785 | -0.15564 | -0.041199 | -0.009156 | 6.102 | 0.87891 | 0.98419 | 1.0345 | 1.1398 | -0.036621 | -0.068665 | 0.091552 | 4.8157 | 0.92926 | 0.80109 | 0.96588 | 0.83771 | 6.2576 | 122.3328 | 4.8523 | 122.3145 | 122.3007 | 122.1542 | 122.1451 | 122.1176 | -122.3419 | -122.2229 | 122.1771 | 122.2778 | 41.2628 | 40.7639
1484.3125 | 122.5113 | -56.7215 | 65.4694 | -0.12688 | 0.017361 | 0.071707 | 0.066858 | -0.00029898 | 0.004516 | 0.0056867 | 0.024414 | 0.011886 | 0.071002 | 0.064984 | -0.008468 | 0.014351 | 0.0020316 | -15.4358 | 65.4099 | -56.8359 | 65.4922 | -50.5417 | -55.687 | -55.7877 | -15.9622 | 65.4053 | -56.7627 | 65.5426 | -51.8921 | -55.9204 | -55.8197 | -0.11444 | -0.059509 | 0.022889 | 6.1798 | 0.93384 | 1.0345 | 1.0483 | 1.149 | -0.041198 | -0.064087 | 0.073243 | 4.8294 | 0.90179 | 0.80109 | 0.94299 | 0.84229 | 6.2942 | 122.3282 | 4.8706 | 122.3053 | 122.2458 | 122.168 | 122.1313 | 122.1268 | -122.3053 | -122.2321 | 122.2137 | 122.2641 | 41.2857 | 40.7593
1485.3125 | 122.5479 | -56.7078 | 65.5106 | 0.018082 | 0.017575 | 0.072775 | 0.066217 | 0.00055542 | 0.004516 | 0.0054729 | -0.012207 | 0.012954 | 0.070147 | 0.06413 | -0.009109 | 0.016915 | 0.001818 | -15.477 | 65.4648 | -56.8222 | 65.5334 | -50.528 | -55.6961 | -55.751 | -15.9851 | 65.419 | -56.7261 | 65.593 | -51.796 | -55.8701 | -55.751 | -0.11444 | -0.045776 | 0.022888 | 6.1798 | 0.95673 | 1.0117 | 1.0712 | 1.1261 | -0.01831 | -0.091553 | 0.082398 | 4.9118 | 0.95673 | 0.83771 | 0.97504 | 0.85602 | 6.2943 | 122.3557 | 4.9301 | 122.319 | 122.287 | 122.1451 | 122.1725 | 122.1268 | -122.3328 | -122.2366 | 122.2412 | 122.3007 | 41.2308 | 40.7227
1486.3125 | 122.5571 | -56.6711 | 65.506 | -0.20317 | 0.019284 | 0.073416 | 0.067499 | -0.00093998 | 0.0047296 | 0.0022687 | -0.030517 | 0.012954 | 0.071643 | 0.065839 | -0.0086816 | 0.016487 | 0.002886 | -15.3854 | 65.4694 | -56.8176 | 65.5243 | -50.441 | -55.6091 | -55.7327 | -16.0034 | 65.4144 | -56.7123 | 65.6433 | -51.7593 | -55.8197 | -55.7465 | -0.14648 | -0.036621 | 0.018311 | 6.2302 | 0.93842 | 1.062 | 1.0849 | 1.2085 | -0.041198 | -0.091552 | 0.13733 | 4.9118 | 0.92468 | 0.85144 | 0.96588 | 0.89264 | 6.3766 | 122.3419 | 4.953 | 122.3557 | 122.287 | 122.1268 | 122.1405 | 122.0856 | -122.3236 | -122.2183 | 122.1954 | 122.3145 | 41.2857 | 40.6677
1487.3125 | 122.5571 | -56.7444 | 65.4556 | -0.13451 | 0.018643 | 0.072989 | 0.066858 | -0.0011536 | 0.003875 | 0.0050457 | -0.045776 | 0.014236 | 0.073352 | 0.063275 | -0.0086816 | 0.017128 | 0.0022452 | -15.4861 | 65.451 | -56.8588 | 65.506 | -50.4913 | -55.6412 | -55.7648 | -16.0721 | 65.419 | -56.7352 | 65.5975 | -51.7639 | -55.8609 | -55.7236 | -0.11444 | -0.004577 | 0.050354 | 6.2531 | 0.97961 | 1.1032 | 1.0941 | 1.2177 | 0.009156 | -0.036621 | 0.14191 | 4.9805 | 1.0208 | 0.88348 | 1.0117 | 0.87433 | 6.3675 | 122.3648 | 4.9713 | 122.3328 | 122.3099 | 122.1542 | 122.1954 | 122.1634 | -122.3145 | -122.1909 | 122.2504 | 122.3419 | 41.2582 | 40.6723
1488.3125 | 122.5571 | -56.6483 | 65.5472 | -0.096359 | 0.018643 | 0.072989 | 0.068994 | 0.00055542 | 0.0057976 | 0.0071819 | -8.6e-08 | 0.013168 | 0.070147 | 0.059216 | -0.008468 | 0.015419 | 0.0048086 | -15.4449 | 65.4739 | -56.7902 | 65.5655 | -50.3769 | -55.6 | -55.7007 | -16.0584 | 65.4602 | -56.6757 | 65.625 | -51.6861 | -55.8334 | -55.719 | -0.14191 | -0.073242 | 0.018311 | 6.2714 | 0.94757 | 1.0483 | 1.0895 | 1.1902 | -0.027466 | -0.086975 | 0.07782 | 4.9622 | 0.92926 | 0.81482 | 0.95673 | 0.84228 | 6.4133 | 122.3557 | 4.9896 | 122.3007 | 122.2641 | 122.1359 | 122.1222 | 122.1085 | -122.3373 | -122.2229 | 122.2137 | 122.2733 | 41.2033 | 40.5899
1489.3125 | 122.5021 | -56.6437 | 65.5701 | -0.10399 | 0.018002 | 0.071493 | 0.067712 | -0.0041444 | 0.0049432 | 0.0048321 | -0.0030517 | 0.012313 | 0.072925 | 0.068616 | -0.0078272 | 0.017556 | 0.0022452 | -15.5045 | 65.4922 | -56.7764 | 65.5472 | -50.3448 | -55.6137 | -55.7098 | -16.1179 | 65.451 | -56.694 | 65.6021 | -51.6998 | -55.806 | -55.7236 | -0.13275 | -0.077819 | -0.022888 | 6.2988 | 0.93384 | 1.03 | 1.0666 | 1.1627 | -0.050354 | -0.11902 | 0.032044 | 4.9438 | 0.9201 | 0.83771 | 0.97046 | 0.88806 | 6.4316 | 122.3236 | 4.9942 | 122.2961 | 122.2687 | 122.1451 | 122.1359 | 122.0947 | -122.3465 | -122.2641 | 122.1909 | 122.2458 | 41.1392 | 40.5258
1490.3125 | 122.493 | -56.6483 | 65.5609 | -0.11925 | 0.020779 | 0.071707 | 0.06878 | 0.00098262 | 0.0034478 | 0.0080365 | -0.042725 | 0.012313 | 0.071856 | 0.062634 | -0.009109 | 0.015206 | 0.0065176 | -15.4999 | 65.4922 | -56.7627 | 65.5472 | -50.3128 | -55.5771 | -55.6824 | -16.1316 | 65.4739 | -56.6757 | 65.6113 | -51.6586 | -55.8197 | -55.7053 | -0.11444 | -0.068664 | -0.013733 | 6.3354 | 0.96588 | 1.0712 | 1.0803 | 1.1856 | -0.027466 | -0.086975 | 0.050354 | 4.9896 | 0.94299 | 0.82855 | 0.97046 | 0.85602 | 6.4499 | 122.3099 | 5.0171 | 122.287 | 122.2549 | 122.1497 | 122.1405 | 122.1222 | -122.3236 | -122.2366 | 122.1954 | 122.2595 | 41.1484 | 40.5167
1491.3125 | 122.5525 | -56.6208 | 65.5838 | -0.10399 | 0.016293 | 0.071066 | 0.064721 | -0.0011536 | 0.0057976 | 0.0061139 | -0.024414 | 0.013168 | 0.070361 | 0.067548 | -0.0099634 | 0.016274 | 0.0022452 | -15.5136 | 65.5151 | -56.7719 | 65.6113 | -50.2258 | -55.545 | -55.6366 | -16.1133 | 65.4922 | -56.6437 | 65.6799 | -51.5762 | -55.751 | -55.6412 | -0.15106 | -0.068664 | 0.027466 | 6.395 | 0.98419 | 1.0757 | 1.1353 | 1.2268 | -0.022888 | -0.091552 | 0.096131 | 5.0446 | 0.97962 | 0.86975 | 1.0025 | 0.89264 | 6.546 | 122.3831 | 5.0674 | 122.3236 | 122.287 | 122.1359 | 122.1359 | 122.113 | -122.3557 | -122.2275 | 122.2321 | 122.3007 | 41.1072 | 40.5075
1492.3125 | 122.4747 | -56.6574 | 65.5792 | -0.096359 | 0.018429 | 0.071921 | 0.066003 | -0.0030762 | 0.0034478 | 0.0078229 | -0.030517 | 0.012954 | 0.072497 | 0.062848 | -0.0080408 | 0.015206 | 0.003527 | -15.5365 | 65.5289 | -56.7764 | 65.5563 | -50.2487 | -55.5725 | -55.6686 | -16.1819 | 65.4556 | -56.6711 | 65.6158 | -51.5945 | -55.7739 | -55.6824 | -0.11902 | -0.050354 | -0.022889 | 6.4087 | 0.98877 | 1.0849 | 1.1078 | 1.2039 | -0.013733 | -0.1236 | 0.036621 | 5.0629 | 0.97504 | 0.88348 | 0.98877 | 0.89722 | 6.5277 | 122.3328 | 5.0766 | 122.287 | 122.3053 | 122.1268 | 122.1863 | 122.113 | -122.3557 | -122.2504 | 122.2137 | 122.2733 | 41.1209 | 40.4755
1493.3125 | 122.5388 | -56.6437 | 65.5518 | -0.13451 | 0.017575 | 0.071707 | 0.068994 | 0.0029052 | 0.0049432 | 0.0046185 | -0.024414 | 0.013381 | 0.071216 | 0.065198 | -0.010391 | 0.017128 | 0.0065176 | -15.477 | 65.506 | -56.7673 | 65.5975 | -50.1984 | -55.5542 | -55.6458 | -16.1728 | 65.4922 | -56.662 | 65.6754 | -51.5259 | -55.7419 | -55.6503 | -0.1236 | -0.045777 | 0.045776 | 6.4453 | 0.99792 | 1.0895 | 1.1215 | 1.2131 | -0.01831 | -0.059509 | 0.1236 | 5.1178 | 0.99335 | 0.90179 | 1.0117 | 0.92011 | 6.5689 | 122.3648 | 5.1361 | 122.3373 | 122.2733 | 122.1542 | 122.1497 | 122.1359 | -122.319 | -122.2137 | 122.2412 | 122.319 | 41.1667 | 40.4709
1494.3125 | 122.493 | -56.6162 | 65.625 | -0.12688 | 0.018429 | 0.071066 | 0.067712 | 0.0052552 | 0.0043024 | 0.0059003 | -0.033569 | 0.012741 | 0.070361 | 0.074383 | -0.0093226 | 0.015633 | 0.0037406 | -15.5457 | 65.5289 | -56.7352 | 65.5975 | -50.1526 | -55.5084 | -55.6183 | -16.2048 | 65.5243 | -56.6345 | 65.6433 | -51.4984 | -55.7419 | -55.6641 | -0.11902 | -0.09613 | -0.027466 | 6.4636 | 0.99793 | 1.1078 | 1.1169 | 1.2268 | -0.01831 | -0.10071 | 0.018311 | 5.1178 | 0.95215 | 0.87433 | 0.97046 | 0.89264 | 6.5826 | 122.3328 | 5.1361 | 122.2778 | 122.2641 | 122.1588 | 122.1451 | 122.1405 | -122.3602 | -122.2595 | 122.2137 | 122.2595 | 41.0706 | 40.4114
1495.3125 | 122.5113 | -56.6162 | 65.6113 | -0.08873 | 0.018643 | 0.07128 | 0.068139 | 0.0018372 | 0.0023798 | 0.0029095 | -0.012207 | 0.013809 | 0.073779 | 0.058789 | -0.0082544 | 0.01606 | 0.0013906 | -15.564 | 65.5472 | -56.7398 | 65.5792 | -50.1251 | -55.5176 | -55.6 | -16.2598 | 65.5243 | -56.6162 | 65.6662 | -51.4938 | -55.751 | -55.6595 | -0.1236 | -0.064087 | -0.032043 | 6.4911 | 1.0162 | 1.0986 | 1.1398 | 1.2222 | 0 | -0.086975 | 0.054932 | 5.1224 | 0.95673 | 0.86517 | 0.95673 | 0.86517 | 6.6147 | 122.319 | 5.1224 | 122.2824 | 122.287 | 122.1405 | 122.1634 | 122.1405 | -122.3511 | -122.2275 | 122.1954 | 122.2824 | 41.0522 | 40.3564
1496.3125 | 122.4884 | -56.5521 | 65.6708 | -0.058212 | 0.018002 | 0.071921 | 0.067499 | -0.0030762 | 0.0066522 | 0.0024823 | -0.01831 | 0.013168 | 0.069507 | 0.061352 | -0.0086816 | 0.016274 | 0.0016044 | -15.5228 | 65.6204 | -56.6849 | 65.7166 | -49.9146 | -55.5862 | -55.6458 | -16.2872 | 65.5838 | -56.5887 | 65.6937 | -51.4023 | -55.6595 | -55.5817 | -0.13275 | -0.050354 | 0.045777 | 6.6376 | 0.90637 | 0.96588 | 1.0391 | 1.0986 | -0.036621 | -0.086975 | 0.022889 | 5.1498 | 0.97046 | 0.89264 | 1.0071 | 0.92926 | 6.7703 | 122.4014 | 5.1865 | 122.2824 | 122.3053 | 122.1725 | 122.1725 | 122.1359 | -122.3557 | -122.2595 | 122.2687 | 122.2458 | 41.0294 | 40.2649
1497.3125 | 122.4792 | -56.5659 | 65.6525 | -0.11925 | 0.018857 | 0.072775 | 0.067712 | -0.00051278 | 0.005584 | 0.0056867 | -0.0091553 | 0.014236 | 0.06972 | 0.06178 | -0.0069726 | 0.015206 | 0.001818 | -15.5777 | 65.6021 | -56.7078 | 65.7303 | -49.91 | -55.6229 | -55.6458 | -16.3422 | 65.5609 | -56.5842 | 65.6799 | -51.3931 | -55.687 | -55.5908 | -0.14191 | -0.050354 | 0.07782 | 6.6559 | 0.9201 | 0.94299 | 1.062 | 1.0849 | -0.01831 | -0.091553 | 0.027466 | 5.1727 | 0.97504 | 0.87891 | 0.99335 | 0.89722 | 6.7978 | 122.4381 | 5.191 | 122.2641 | 122.3099 | 122.1451 | 122.168 | 122.1268 | -122.3602 | -122.2366 | 122.2961 | 122.2458 | 40.9882 | 40.2237
1498.3125 | 122.4976 | -56.5521 | 65.6616 | -0.11925 | 0.019284 | 0.071921 | 0.068139 | 0.0018372 | 0.0040888 | 0.0050457 | -0.042725 | 0.015304 | 0.070147 | 0.069043 | -0.0082544 | 0.014992 | 0.002886 | -15.5731 | 65.593 | -56.6528 | 65.6433 | -49.9924 | -55.4306 | -55.545 | -16.2918 | 65.5975 | -56.5613 | 65.7257 | -51.3474 | -55.6503 | -55.5679 | -0.10071 | -0.068664 | -0.01831 | 6.5598 | 1.0071 | 1.1215 | 1.1078 | 1.2222 | -0.009155 | -0.064087 | 0.064087 | 5.2048 | 0.98419 | 0.90179 | 0.99335 | 0.91095 | 6.6605 | 122.2961 | 5.2139 | 122.287 | 122.2458 | 122.1588 | 122.1451 | 122.1497 | -122.3145 | -122.2229 | 122.1954 | 122.2778 | 40.979 | 40.2603
1499.3125 | 122.5067 | -56.5155 | 65.7394 | -0.042954 | 0.020993 | 0.070425 | 0.065576 | -0.00093998 | 0.0025934 | 0.0069683 | -0.021362 | 0.015304 | 0.071002 | 0.068616 | -0.010177 | 0.017556 | 0.0033134 | -15.5045 | 65.6479 | -56.6299 | 65.7303 | -49.8962 | -55.3162 | -55.4626 | -16.2506 | 65.6525 | -56.5201 | 65.7532 | -51.2512 | -55.5679 | -55.5084 | -0.11444 | -0.091553 | -0.009155 | 6.6193 | 1.0529 | 1.1993 | 1.1673 | 1.3138 | -0.004578 | -0.086975 | 0.013733 | 5.2643 | 1.0071 | 0.94757 | 1.0117 | 0.95215 | 6.7337 | 122.3602 | 5.2689 | 122.2733 | 122.2778 | 122.1725 | 122.1634 | 122.168 | -122.3694 | -122.2595 | 122.2458 | 122.2687 | 41.011 | 40.2649
1500.3125 | 122.4747 | -56.543 | 65.6845 | -0.11162 | 0.018643 | 0.071066 | 0.068139 | 0.0014098 | 0.0053704 | 0.0059003 | -0.030517 | 0.014663 | 0.072925 | 0.066479 | -0.008468 | 0.015847 | 0.0026724 | -15.5823 | 65.6296 | -56.6849 | 65.6479 | -49.9283 | -55.4123 | -55.5267 | -16.3193 | 65.6113 | -56.5796 | 65.712 | -51.2924 | -55.6458 | -55.5496 | -0.14191 | -0.054931 | -0.036621 | 6.6147 | 1.0162 | 1.1307 | 1.1581 | 1.2726 | -0.036621 | -0.073242 | 0.027466 | 5.2505 | 0.99335 | 0.89722 | 1.03 | 0.93384 | 6.7566 | 122.3328 | 5.2872 | 122.2916 | 122.3145 | 122.1909 | 122.1725 | 122.1542 | -122.3694 | -122.2641 | 122.1909 | 122.2549 | 40.9607 | 40.2237
1501.3125 | 122.5021 | -56.5063 | 65.7394 | -0.14977 | 0.01907 | 0.073202 | 0.06878 | -0.00072638 | 0.0081476 | 0.0061139 | -0.0091553 | 0.016158 | 0.069934 | 0.061352 | -0.0071864 | 0.01606 | 0.0037406 | -15.5685 | 65.6754 | -56.6437 | 65.8264 | -49.9237 | -55.4855 | -55.4855 | -16.3239 | 65.657 | -56.5201 | 65.7394 | -51.1963 | -55.5634 | -55.4901 | -0.13733 | -0.064087 | 0.086975 | 6.5826 | 1.0208 | 1.0208 | 1.1581 | 1.1581 | -0.013733 | -0.082398 | 0 | 5.3101 | 1.0162 | 0.94299 | 1.03 | 0.95673 | 6.72 | 122.4701 | 5.3238 | 122.2595 | 122.319 | 122.1771 | 122.1817 | 122.1634 | -122.3831 | -122.2595 | 122.3328 | 122.2458 | 40.9378 | 40.1825
1502.3125 | 122.5342 | -56.4972 | 65.7074 | -0.042954 | 0.019711 | 0.072775 | 0.066217 | -0.0011536 | 0.004516 | 0.0046185 | -0.015259 | 0.013381 | 0.06972 | 0.071179 | -0.0095362 | 0.016274 | 0.0030996 | -15.564 | 65.6799 | -56.6345 | 65.6845 | -49.8413 | -55.3391 | -55.4398 | -16.3559 | 65.6113 | -56.5338 | 65.7761 | -51.1276 | -55.545 | -55.4581 | -0.13733 | -0.027465 | -0.022888 | 6.6559 | 1.0574 | 1.1581 | 1.1948 | 1.2955 | -0.036621 | -0.09613 | 0.068665 | 5.3696 | 1.0391 | 0.95215 | 1.0757 | 0.98877 | 6.7932 | 122.319 | 5.4062 | 122.3099 | 122.3145 | 122.1451 | 122.1771 | 122.1085 | -122.3419 | -122.2412 | 122.1817 | 122.2733 | 40.9332 | 40.1413
1503.3125 | 122.493 | -56.488 | 65.7074 | -0.12688 | 0.019284 | 0.071921 | 0.066003 | -0.0011536 | 0.007934 | 0.0039777 | -0.012207 | 0.014022 | 0.071002 | 0.060071 | -0.009109 | 0.017769 | 0.002886 | -15.596 | 65.6525 | -56.6528 | 65.625 | -49.823 | -55.3482 | -55.4901 | -16.4383 | 65.6433 | -56.5567 | 65.7623 | -51.1505 | -55.5588 | -55.4855 | -0.16479 | -0.054931 | -0.082397 | 6.665 | 0.99792 | 1.1398 | 1.1627 | 1.3046 | -0.068665 | -0.064086 | 0.054932 | 5.3375 | 1.0025 | 0.92926 | 1.0712 | 0.99793 | 6.8298 | 122.2778 | 5.4062 | 122.319 | 122.3053 | 122.2 | 122.1405 | 122.1313 | -122.3602 | -122.2641 | 122.113 | 122.2504 | 40.892 | 40.0497
1504.3125 | 122.4884 | -56.4972 | 65.7532 | -0.10399 | 0.018857 | 0.070852 | 0.067499 | -0.0058532 | 0.0064386 | 0.0059003 | -0.07019 | 0.012313 | 0.072497 | 0.068829 | -0.0054774 | 0.018837 | 0.006304 | -15.5228 | 65.7028 | -56.6116 | 65.744 | -49.7498 | -55.275 | -55.3894 | -16.3696 | 65.6662 | -56.4926 | 65.7578 | -51.1047 | -55.5405 | -55.481 | -0.11444 | -0.050354 | -0.009155 | 6.7474 | 1.1078 | 1.2222 | 1.2222 | 1.3367 | 0.004577 | -0.086975 | 0.004577 | 5.3925 | 1.0162 | 0.95673 | 1.0117 | 0.95215 | 6.8619 | 122.3557 | 5.3879 | 122.2504 | 122.3145 | 122.1588 | 122.2 | 122.1634 | -122.3648 | -122.2458 | 122.2412 | 122.2549 | 40.9744 | 40.1276
1505.3125 | 122.5067 | -56.4331 | 65.7806 | -0.027695 | 0.018643 | 0.072775 | 0.067285 | -0.0035034 | 0.0066522 | 0.0067547 | -0.05188 | 0.014663 | 0.072284 | 0.064343 | -0.0061182 | 0.016487 | 0.0039542 | -15.6097 | 65.7257 | -56.5704 | 65.7349 | -49.7406 | -55.2612 | -55.3665 | -16.3513 | 65.6982 | -56.4651 | 65.8173 | -51.0223 | -55.4626 | -55.4169 | -0.13733 | -0.054932 | -0.045777 | 6.6925 | 1.0666 | 1.1719 | 1.2039 | 1.3092 | -0.032044 | -0.082398 | 0.036621 | 5.4108 | 1.0162 | 0.97046 | 1.0483 | 1.0025 | 6.8298 | 122.3053 | 5.4428 | 122.2824 | 122.2961 | 122.1634 | 122.1588 | 122.1313 | -122.3511 | -122.2458 | 122.168 | 122.2504 | 40.8234 | 40.0818
1506.3125 | 122.4243 | -56.3919 | 65.744 | -0.096359 | 0.018429 | 0.070425 | 0.067926 | -0.0032898 | 0.006225 | 0.0095319 | -0.027466 | 0.015304 | 0.07207 | 0.066479 | -0.0063318 | 0.014992 | 0.0016044 | -15.4907 | 65.7349 | -56.5338 | 65.8447 | -49.5392 | -55.1331 | -55.2841 | -16.2598 | 65.712 | -56.4102 | 65.7257 | -50.5966 | -55.1697 | -55.3436 | -0.14191 | -0.009156 | 0.10071 | 6.8527 | 1.1078 | 1.2589 | 1.2497 | 1.4008 | -0.01831 | -0.032044 | -0.018311 | 5.7953 | 1.0483 | 1.2222 | 1.0666 | 1.2405 | 6.9946 | 122.3785 | 5.8136 | 122.1359 | 122.2687 | 122.1222 | 122.1268 | 122.1039 | -122.2778 | -122.1542 | 122.2366 | 122.1176 | 40.9012 | 40.1321
1507.3125 | 122.5159 | -56.4194 | 65.8173 | -0.073471 | 0.020565 | 0.074698 | 0.068994 | 0.00076902 | 0.0049432 | 0.0041913 | -0.027466 | 0.014663 | 0.074206 | 0.065411 | -0.0088952 | 0.018196 | 0.0013906 | -15.5548 | 65.7211 | -56.5521 | 65.7623 | -49.6353 | -55.2246 | -55.3574 | -16.4108 | 65.7211 | -56.4468 | 65.8401 | -50.9308 | -55.4352 | -55.3802 | -0.13275 | -0.096131 | -0.054932 | 6.7841 | 1.062 | 1.1948 | 1.1948 | 1.3275 | -0.027465 | -0.096131 | 0.022888 | 5.4886 | 1.0391 | 0.98419 | 1.0666 | 1.0117 | 6.9168 | 122.3145 | 5.5161 | 122.287 | 122.2733 | 122.168 | 122.1405 | 122.1405 | -122.3694 | -122.2641 | 122.1817 | 122.2595 | 40.8646 | 40.0085
1508.3125 | 122.5342 | -56.369 | 65.7852 | -0.042954 | 0.017788 | 0.072134 | 0.067285 | -0.0028626 | 0.004516 | 0.0031231 | -0.030517 | 0.01445 | 0.072497 | 0.063275 | -0.0080408 | 0.016701 | 0.002886 | -15.5228 | 65.7715 | -56.543 | 65.8081 | -49.5438 | -55.1559 | -55.2841 | -16.3605 | 65.7532 | -56.4194 | 65.8813 | -50.8255 | -55.3619 | -55.3207 | -0.17395 | -0.013733 | 0.022888 | 6.8253 | 1.0849 | 1.2131 | 1.2589 | 1.387 | -0.050354 | -0.032043 | 0.096131 | 5.5435 | 1.0483 | 1.0071 | 1.0986 | 1.0574 | 6.9992 | 122.3511 | 5.5939 | 122.3007 | 122.3145 | 122.1725 | 122.1405 | 122.1222 | -122.3282 | -122.2046 | 122.1771 | 122.2504 | 40.8463 | 40.0085
1509.3125 | 122.4472 | -56.3416 | 65.9225 | -0.096359 | 0.01907 | 0.073202 | 0.068139 | -0.00072638 | 0.0047296 | 0.0086773 | -0.05188 | 0.015731 | 0.071429 | 0.066266 | -0.0088952 | 0.016274 | 0.003527 | -15.4541 | 65.863 | -56.4926 | 65.8676 | -49.4659 | -55.1102 | -55.2383 | -16.3696 | 65.831 | -56.3736 | 65.8676 | -50.8163 | -55.3574 | -55.3345 | -0.15106 | -0.059509 | -0.054931 | 6.8756 | 1.1032 | 1.2314 | 1.2543 | 1.3824 | -0.032043 | -0.091552 | -0.054931 | 5.5252 | 1.0071 | 0.98419 | 1.0391 | 1.0162 | 7.0267 | 122.3602 | 5.5573 | 122.2412 | 122.3557 | 122.2046 | 122.2046 | 122.1725 | -122.4152 | -122.2961 | 122.2092 | 122.2092 | 40.8875 | 39.9719
1510.3125 | 122.5388 | -56.3141 | 65.8813 | -0.073471 | 0.019497 | 0.072775 | 0.066644 | 0.00034182 | 0.0064386 | 0.0056867 | -0.030517 | 0.01445 | 0.072284 | 0.06477 | -0.0082544 | 0.01841 | 0.006304 | -15.4678 | 65.8264 | -56.4468 | 65.8813 | -49.4064 | -55.0735 | -55.1697 | -16.3193 | 65.7898 | -56.3599 | 65.9683 | -50.6973 | -55.2704 | -55.2246 | -0.13275 | -0.054932 | 0 | 6.9077 | 1.1444 | 1.2405 | 1.2772 | 1.3733 | -0.045776 | -0.091553 | 0.086975 | 5.6168 | 1.0895 | 1.0437 | 1.1353 | 1.0895 | 7.0404 | 122.3282 | 5.6625 | 122.3282 | 122.2733 | 122.1497 | 122.1405 | 122.1039 | -122.3282 | -122.2412 | 122.1954 | 122.2824 | 40.8463 | 39.9948
1511.3125 | 122.5388 | -56.3278 | 65.8905 | -0.073471 | 0.018643 | 0.07128 | 0.06878 | -0.0013672 | 0.0060114 | 0.0076093 | -0.027466 | 0.014236 | 0.072925 | 0.06477 | -0.0086816 | 0.016487 | 0.0048086 | -15.4816 | 65.831 | -56.4606 | 65.8951 | -49.3744 | -55.0095 | -55.1697 | -16.3147 | 65.8127 | -56.3461 | 65.9729 | -50.6653 | -55.2658 | -55.2155 | -0.13275 | -0.059509 | 0.004578 | 6.9534 | 1.1581 | 1.3184 | 1.2909 | 1.4511 | -0.01831 | -0.07782 | 0.082397 | 5.6625 | 1.1124 | 1.062 | 1.1307 | 1.0803 | 7.0862 | 122.3557 | 5.6808 | 122.319 | 122.2916 | 122.1588 | 122.1588 | 122.1405 | -122.3511 | -122.2366 | 122.2229 | 122.3007 | 40.8463 | 40.0131
1512.3125 | 122.5342 | -56.2912 | 65.8997 | -0.11162 | 0.019711 | 0.07128 | 0.068567 | 0.00012822 | 0.005584 | 0.0048321 | -0.036621 | 0.015304 | 0.072284 | 0.06477 | -0.009109 | 0.018624 | 0.001177 | -15.4816 | 65.8539 | -56.4239 | 65.9134 | -49.3149 | -55.0323 | -55.1514 | -16.3239 | 65.8081 | -56.3278 | 65.9866 | -50.6241 | -55.22 | -55.1926 | -0.13275 | -0.045776 | 0.013733 | 6.9763 | 1.1398 | 1.2588 | 1.2726 | 1.3916 | -0.036621 | -0.091553 | 0.086975 | 5.6671 | 1.0986 | 1.0712 | 1.1353 | 1.1078 | 7.1091 | 122.3373 | 5.7037 | 122.3145 | 122.2778 | 122.1359 | 122.1451 | 122.0993 | -122.3236 | -122.2275 | 122.2046 | 122.2778 | 40.8096 | 39.9673
1513.3125 | 122.5021 | -56.2683 | 65.9637 | -0.042954 | 0.020779 | 0.072348 | 0.071557 | 0.0014098 | 0.0057976 | 0.0088909 | -0.036621 | 0.017227 | 0.069934 | 0.06947 | -0.0076136 | 0.017128 | 0.0037406 | -15.4083 | 65.8813 | -56.4102 | 65.9729 | -49.2416 | -54.9774 | -55.1056 | -16.3147 | 65.8585 | -56.3049 | 66.0095 | -50.5737 | -55.2155 | -55.1834 | -0.14191 | -0.082397 | 0.009155 | 7.0267 | 1.1627 | 1.2909 | 1.3046 | 1.4328 | -0.036621 | -0.10529 | 0.045776 | 5.6946 | 1.0849 | 1.0529 | 1.1215 | 1.0895 | 7.1686 | 122.3831 | 5.7312 | 122.3145 | 122.2916 | 122.1634 | 122.1497 | 122.1268 | -122.374 | -122.2687 | 122.2412 | 122.2778 | 40.86 | 39.9536
1514.3125 | 122.5616 | -56.2683 | 65.9683 | -0.096359 | 0.018216 | 0.071493 | 0.069635 | 0.0016236 | 0.0081476 | 0.0069683 | 0.030518 | 0.018081 | 0.073565 | 0.065625 | -0.0082544 | 0.01841 | 0.001177 | -15.4175 | 65.8905 | -56.3644 | 66.0095 | -49.1638 | -54.9362 | -54.7531 | -16.5619 | 65.8401 | -56.3049 | 66.037 | -50.5142 | -55.1605 | -55.1102 | -0.09613 | -0.07782 | 0.041198 | 7.1045 | 1.5152 | 1.3321 | 1.6113 | 1.4282 | -0.036621 | -0.12817 | 0.068664 | 5.7541 | 1.1581 | 1.1078 | 1.1948 | 1.1444 | 7.2006 | 122.374 | 5.7907 | 122.3419 | 122.2549 | 122.1451 | 122.1588 | 122.1085 | -122.3328 | -122.2733 | 122.2778 | 122.3053 | 40.8508 | 39.7064
1515.3125 | 122.5662 | -56.2454 | 65.9592 | -0.058212 | 0.019497 | 0.072775 | 0.066858 | -0.0035034 | 0.007934 | 0.0044049 | 0.12512 | 0.015945 | 0.072284 | 0.06477 | -0.0052638 | 0.018624 | 0.0026724 | -15.4083 | 65.8859 | -56.3644 | 66.0233 | -49.1089 | -54.9133 | -55.0323 | -16.3605 | 65.9042 | -56.282 | 66.0095 | -50.4456 | -55.1651 | -55.1376 | -0.11902 | -0.073242 | 0.064087 | 7.1365 | 1.2131 | 1.3321 | 1.3321 | 1.4511 | -0.036621 | -0.054931 | 0.050354 | 5.7999 | 1.1078 | 1.0803 | 1.1444 | 1.1169 | 7.2556 | 122.3877 | 5.8365 | 122.2916 | 122.2504 | 122.1863 | 122.1313 | 122.1497 | -122.3236 | -122.2412 | 122.2687 | 122.2549 | 40.8371 | 39.8849
1516.3125 | 122.5296 | -56.25 | 65.9866 | -0.096359 | 0.019711 | 0.072134 | 0.070276 | 0.0029052 | 0.006225 | 0.0046185 | -0.033569 | 0.015304 | 0.072711 | 0.063489 | -0.0078272 | 0.017556 | 0.0030996 | -15.4083 | 65.9088 | -56.3553 | 66.0141 | -49.118 | -54.9179 | -55.0415 | -16.3422 | 65.863 | -56.2637 | 66.0278 | -50.4456 | -55.1239 | -55.101 | -0.10529 | -0.07782 | 0.027466 | 7.132 | 1.2085 | 1.3321 | 1.3138 | 1.4374 | -0.013733 | -0.1236 | 0.041199 | 5.8044 | 1.149 | 1.1261 | 1.1627 | 1.1398 | 7.2372 | 122.3694 | 5.8182 | 122.2916 | 122.2641 | 122.1268 | 122.1588 | 122.113 | -122.3419 | -122.2504 | 122.2641 | 122.2778 | 40.8417 | 39.9078
1517.3125 | 122.5479 | -56.2363 | 65.9546 | -0.08873 | 0.019284 | 0.071707 | 0.068353 | -0.002649 | 0.0047296 | 0.0071819 | -0.012207 | 0.014663 | 0.072284 | 0.067975 | -0.0061182 | 0.017769 | 0.000109 | -15.4175 | 65.9088 | -56.3416 | 66.0233 | -49.0356 | -54.863 | -55.0095 | -16.3101 | 65.8951 | -56.2225 | 66.1011 | -50.3632 | -55.1788 | -55.1376 | -0.10529 | -0.045777 | 0.068664 | 7.2006 | 1.2268 | 1.3733 | 1.3321 | 1.4786 | 0.013733 | -0.059509 | 0.14648 | 5.8731 | 1.0986 | 1.0574 | 1.0849 | 1.0437 | 7.3059 | 122.3648 | 5.8594 | 122.3236 | 122.2504 | 122.1176 | 122.1451 | 122.1313 | -122.2961 | -122.1771 | 122.2595 | 122.3373 | 40.8188 | 39.9261
1518.3125 | 122.5296 | -56.2408 | 65.9683 | -0.027695 | 0.020352 | 0.074057 | 0.067712 | 0.00034182 | 0.0053704 | 0.0086773 | -0.027466 | 0.015731 | 0.073779 | 0.062421 | -0.0076136 | 0.01841 | 0.0037406 | -15.4678 | 65.8951 | -56.3553 | 66.0324 | -49.0631 | -54.8813 | -55.014 | -16.3651 | 65.8997 | -56.2454 | 66.0553 | -50.3769 | -55.0919 | -55.0781 | -0.11444 | -0.073242 | 0.064087 | 7.1777 | 1.2268 | 1.3596 | 1.3412 | 1.474 | -0.004577 | -0.068665 | 0.086975 | 5.864 | 1.1627 | 1.149 | 1.1673 | 1.1536 | 7.2922 | 122.3877 | 5.8685 | 122.3007 | 122.2504 | 122.1451 | 122.1359 | 122.1405 | -122.3236 | -122.2137 | 122.2733 | 122.2961 | 40.773 | 39.8758
1519.3125 | 122.4609 | -56.2683 | 66.0095 | -0.050583 | 0.022274 | 0.072989 | 0.070917 | 0.00055542 | 0.0057976 | 0.0086773 | -0.11902 | 0.017013 | 0.073352 | 0.073529 | -0.008468 | 0.018837 | 0.0050222 | -15.4495 | 65.9683 | -56.3782 | 65.9363 | -49.118 | -54.9545 | -55.1147 | -16.4795 | 65.9409 | -56.2683 | 66.0187 | -50.4181 | -55.188 | -55.1468 | -0.10986 | -0.041198 | -0.073242 | 7.1503 | 1.1536 | 1.3138 | 1.2634 | 1.4236 | 0 | -0.068664 | 0.009156 | 5.8502 | 1.1215 | 1.0803 | 1.1215 | 1.0803 | 7.2601 | 122.3145 | 5.8502 | 122.287 | 122.3465 | 122.2092 | 122.2366 | 122.2092 | -122.3877 | -122.2778 | 122.2046 | 122.287 | 40.8188 | 39.7888
1520.3125 | 122.525 | -56.2042 | 65.9912 | -0.058212 | 0.020565 | 0.072561 | 0.06643 | -0.0024354 | 0.0075066 | 0.0052593 | -0.0061035 | 0.017227 | 0.072711 | 0.061566 | -0.0097498 | 0.018624 | 0.001818 | -15.3809 | 65.95 | -56.3187 | 66.037 | -48.9532 | -54.8401 | -54.9728 | -16.3696 | 65.9363 | -56.218 | 66.0736 | -50.2762 | -55.0644 | -55.0598 | -0.11444 | -0.041199 | 0.045776 | 7.251 | 1.2314 | 1.3641 | 1.3458 | 1.4786 | -0.013733 | -0.054932 | 0.082397 | 5.928 | 1.1444 | 1.1398 | 1.1581 | 1.1536 | 7.3654 | 122.3557 | 5.9418 | 122.2916 | 122.2687 | 122.1542 | 122.1542 | 122.1405 | -122.3099 | -122.2092 | 122.2412 | 122.2778 | 40.8234 | 39.8346
1521.3125 | 122.5342 | -56.1813 | 66.0187 | -0.15739 | 0.023556 | 0.072775 | 0.070276 | 0.0046142 | 0.0068658 | 0.0059003 | 0.012207 | 0.015304 | 0.072711 | 0.072461 | -0.0074 | 0.016274 | -0.0013864 | -15.3946 | 65.9409 | -56.3232 | 66.0278 | -48.9075 | -54.8035 | -54.9637 | -16.3559 | 65.9271 | -56.2317 | 66.0873 | -50.2396 | -55.0461 | -55.0186 | -0.14191 | -0.07782 | 0.009155 | 7.2739 | 1.2177 | 1.3779 | 1.3596 | 1.5198 | -0.050354 | -0.091553 | 0.068664 | 5.9418 | 1.1627 | 1.1353 | 1.2131 | 1.1856 | 7.4158 | 122.3511 | 5.9921 | 122.319 | 122.2641 | 122.1588 | 122.1222 | 122.1085 | -122.3419 | -122.2504 | 122.2092 | 122.2687 | 40.7867 | 39.8254
1522.3125 | 122.525 | -56.1768 | 66.0461 | -0.30235 | 0.019925 | 0.07427 | 0.069421 | -0.00072638 | 0.0047296 | 0.0073955 | -0.024414 | 0.015731 | 0.072925 | 0.066479 | -0.0071864 | 0.017769 | 0.001818 | -15.303 | 65.95 | -56.3004 | 66.0553 | -48.8525 | -54.7714 | -54.9316 | -16.3513 | 65.9409 | -56.1905 | 66.0873 | -50.1755 | -55.014 | -55.0049 | -0.1236 | -0.096131 | 0.009155 | 7.3242 | 1.2451 | 1.4053 | 1.3687 | 1.5289 | -0.013733 | -0.10529 | 0.041198 | 6.0013 | 1.1719 | 1.1627 | 1.1856 | 1.1765 | 7.4478 | 122.3557 | 6.015 | 122.2778 | 122.2504 | 122.1313 | 122.1268 | 122.1176 | -122.3465 | -122.2366 | 122.2321 | 122.2641 | 40.8737 | 39.8254
1523.3125 | 122.4747 | -56.2042 | 66.0645 | -0.042954 | 0.024624 | 0.074484 | 0.067712 | 0.00076902 | 0.0036614 | 0.0069683 | -0.045776 | 0.017867 | 0.071856 | 0.062634 | -0.0078272 | 0.019478 | 0.0056632 | -15.3809 | 65.9821 | -56.282 | 66.0324 | -48.8663 | -54.8126 | -54.9591 | -16.4291 | 65.95 | -56.218 | 66.0736 | -50.2258 | -55.0644 | -55.0369 | -0.077819 | -0.082397 | -0.032043 | 7.338 | 1.2451 | 1.3916 | 1.3229 | 1.4694 | -0.013733 | -0.11444 | 0.009155 | 5.9784 | 1.1673 | 1.1398 | 1.181 | 1.1536 | 7.4158 | 122.3145 | 5.9921 | 122.2916 | 122.2641 | 122.168 | 122.1863 | 122.1542 | -122.3465 | -122.2824 | 122.2366 | 122.2778 | 40.8234 | 39.7751
1524.3125 | 122.5433 | -56.1768 | 66.0461 | -0.11162 | 0.021206 | 0.072775 | 0.071344 | -0.00072638 | 0.0043024 | 0.0088909 | 0.012207 | 0.016372 | 0.072925 | 0.069257 | -0.0086816 | 0.017128 | 0.0024588 | -15.4404 | 66.0187 | -56.2592 | 66.1377 | -48.8571 | -54.7806 | -54.863 | -16.3605 | 65.9821 | -56.1539 | 66.1331 | -50.1068 | -54.9637 | -54.9545 | -0.082397 | -0.027466 | 0.091552 | 7.3196 | 1.3138 | 1.3962 | 1.3962 | 1.4786 | 0.022888 | -0.064087 | 0.086975 | 6.0699 | 1.2222 | 1.2131 | 1.1993 | 1.1902 | 7.402 | 122.3969 | 6.0471 | 122.287 | 122.2778 | 122.1359 | 122.1954 | 122.1588 | -122.3053 | -122.2 | 122.3145 | 122.3099 | 40.7364 | 39.8163
1525.3125 | 122.493 | -56.1813 | 66.0645 | -0.08873 | 0.023343 | 0.074698 | 0.067712 | -0.00093998 | 0.007293 | 0.0056867 | -0.0061035 | 0.016799 | 0.072284 | 0.07182 | -0.0080408 | 0.01841 | 0.0009634 | -15.3763 | 65.9866 | -56.3004 | 66.0507 | -48.8205 | -54.7806 | -54.9362 | -16.42 | 65.9592 | -56.1996 | 66.0828 | -50.1389 | -55.0415 | -55.0003 | -0.11902 | -0.07782 | -0.013733 | 7.3608 | 1.2451 | 1.4008 | 1.3641 | 1.5198 | -0.018311 | -0.10529 | 0.018311 | 6.0425 | 1.181 | 1.1398 | 1.1993 | 1.1581 | 7.4799 | 122.3511 | 6.0608 | 122.2824 | 122.287 | 122.1588 | 122.168 | 122.1405 | -122.3648 | -122.2641 | 122.2321 | 122.2641 | 40.8051 | 39.7614
1526.3125 | 122.5159 | -56.1493 | 66.0736 | -0.11162 | 0.020565 | 0.07363 | 0.067712 | 0.00034182 | 0.006225 | 0.0073955 | -0.045776 | 0.016158 | 0.073138 | 0.072461 | -0.008468 | 0.018196 | 0.0043814 | -15.3442 | 65.9866 | -56.2775 | 66.0873 | -48.7473 | -54.7394 | -54.9042 | -16.4154 | 65.9775 | -56.1768 | 66.1057 | -50.0839 | -54.982 | -54.9774 | -0.12817 | -0.086975 | 0.013733 | 7.402 | 1.2451 | 1.4099 | 1.3733 | 1.5381 | -0.027466 | -0.09613 | 0.032044 | 6.0654 | 1.1719 | 1.1673 | 1.1993 | 1.1948 | 7.5302 | 122.3648 | 6.0928 | 122.2824 | 122.2641 | 122.1542 | 122.1359 | 122.1268 | -122.3511 | -122.2504 | 122.2366 | 122.2549 | 40.8051 | 39.7339
1527.3125 | 122.493 | -56.0989 | 66.124 | -0.073471 | 0.020993 | 0.074057 | 0.070703 | 0.00012822 | 0.0051568 | 0.0099591 | -0.027466 | 0.017227 | 0.072711 | 0.065839 | -0.0086816 | 0.017983 | 0.005236 | -15.3305 | 66.0645 | -56.2134 | 66.1377 | -48.6649 | -54.6799 | -54.8218 | -16.3834 | 66.0553 | -56.1356 | 66.1606 | -49.9832 | -54.9271 | -54.895 | -0.11444 | -0.059509 | 0.013733 | 7.4341 | 1.2772 | 1.4191 | 1.3916 | 1.5335 | -0.036621 | -0.068664 | 0.036621 | 6.1157 | 1.2039 | 1.1719 | 1.2405 | 1.2085 | 7.5485 | 122.3511 | 6.1523 | 122.2961 | 122.2778 | 122.1909 | 122.1634 | 122.1542 | -122.3373 | -122.2595 | 122.2366 | 122.2595 | 40.7684 | 39.7156
1528.3125 | 122.5067 | -56.131 | 66.1377 | -0.10399 | 0.021634 | 0.072989 | 0.068994 | -0.00072638 | 0.0077202 | 0.0059003 | -0.015259 | 0.016799 | 0.07207 | 0.06712 | -0.008468 | 0.016274 | 0.001177 | -15.3259 | 66.0461 | -56.2088 | 66.1469 | -48.6511 | -54.6844 | -54.8309 | -16.3696 | 66.0324 | -56.1264 | 66.1606 | -49.9649 | -54.9362 | -54.895 | -0.07782 | -0.091552 | 0.009156 | 7.4799 | 1.3 | 1.4465 | 1.3779 | 1.5244 | 0.004577 | -0.10528 | 0.022888 | 6.1661 | 1.236 | 1.1948 | 1.2314 | 1.1902 | 7.5577 | 122.3557 | 6.1615 | 122.287 | 122.2549 | 122.1588 | 122.1771 | 122.1634 | -122.3465 | -122.2641 | 122.2778 | 122.2916 | 40.8051 | 39.7614
1529.3125 | 122.4289 | -56.1447 | 66.1331 | -0.11162 | 0.021206 | 0.076834 | 0.071344 | 0.002478 | 0.0060114 | 0.0106 | -0.11597 | 0.019363 | 0.072497 | 0.075665 | -0.0074 | 0.020974 | 0.0043814 | -15.3488 | 66.0782 | -56.2637 | 66.0782 | -48.6877 | -54.7531 | -54.9088 | -16.4703 | 66.0553 | -56.1539 | 66.1285 | -49.9649 | -55.0095 | -54.9454 | -0.11902 | -0.054932 | -0.054932 | 7.457 | 1.236 | 1.3916 | 1.355 | 1.5106 | -0.009156 | -0.07782 | -0.004578 | 6.1798 | 1.1993 | 1.1353 | 1.2085 | 1.1444 | 7.576 | 122.3419 | 6.189 | 122.2824 | 122.3419 | 122.2092 | 122.2229 | 122.2 | -122.3969 | -122.287 | 122.2229 | 122.2733 | 40.7959 | 39.6744
1530.3125 | 122.4976 | -56.0944 | 66.1285 | -0.073471 | 0.021206 | 0.072775 | 0.067071 | -0.0017944 | 0.0083612 | 0.0065411 | 0.0091553 | 0.017654 | 0.073993 | 0.06712 | -0.0088952 | 0.018624 | 0.0050222 | -15.3168 | 66.1102 | -56.1905 | 66.1606 | -48.5504 | -54.6158 | -54.7668 | -16.3513 | 66.0553 | -56.1035 | 66.2018 | -49.8779 | -54.8859 | -54.8584 | -0.096131 | -0.018311 | 0.032043 | 7.5439 | 1.3275 | 1.4786 | 1.4236 | 1.5747 | -0.009156 | -0.073242 | 0.073242 | 6.2164 | 1.236 | 1.2085 | 1.2451 | 1.2177 | 7.6401 | 122.3511 | 6.2256 | 122.3053 | 122.3007 | 122.1588 | 122.2046 | 122.1497 | -122.319 | -122.2321 | 122.2549 | 122.2961 | 40.7776 | 39.743
1531.3125 | 122.406 | -56.0806 | 66.2155 | -0.10399 | 0.020565 | 0.07427 | 0.068139 | -0.0013672 | 0.0049432 | 0.0084637 | -0.0061035 | 0.016586 | 0.073352 | 0.066266 | -0.0082544 | 0.019905 | 0.0073722 | -15.3214 | 66.1469 | -56.1951 | 66.1057 | -48.587 | -54.6844 | -54.8264 | -16.4978 | 66.1285 | -56.0852 | 66.124 | -49.8779 | -54.9316 | -54.9225 | -0.11444 | -0.068664 | -0.10986 | 7.4936 | 1.2543 | 1.3962 | 1.3687 | 1.5106 | -0.004578 | -0.086975 | -0.091553 | 6.2027 | 1.1581 | 1.149 | 1.1627 | 1.1536 | 7.608 | 122.3007 | 6.2073 | 122.2092 | 122.3419 | 122.2137 | 122.2275 | 122.2092 | -122.4106 | -122.3007 | 122.1863 | 122.2046 | 40.7593 | 39.5828
1532.3125 | 122.493 | -56.0761 | 66.1606 | -0.10399 | 0.02142 | 0.073416 | 0.069421 | 0.00055542 | 0.0083612 | 0.0086773 | 0.018311 | 0.015731 | 0.073779 | 0.066266 | -0.0076136 | 0.016487 | 0.0060904 | -15.3122 | 66.1011 | -56.1676 | 66.1743 | -48.4817 | -54.5975 | -54.7531 | -16.4474 | 66.0461 | -56.0761 | 66.188 | -49.7726 | -54.8721 | -54.8584 | -0.091553 | -0.059509 | 0.013733 | 7.5943 | 1.3229 | 1.4786 | 1.4145 | 1.5701 | 0 | -0.11444 | 0.027466 | 6.3034 | 1.2177 | 1.2039 | 1.2177 | 1.2039 | 7.6859 | 122.3419 | 6.3034 | 122.2641 | 122.2687 | 122.1222 | 122.1771 | 122.1222 | -122.3282 | -122.2366 | 122.2504 | 122.2641 | 40.7639 | 39.6286
1533.3125 | 122.4289 | -56.0623 | 66.2384 | -0.08873 | 0.021634 | 0.071921 | 0.068567 | -0.0035034 | 0.0049432 | 0.0084637 | -0.039673 | 0.018081 | 0.072711 | 0.06413 | -0.008468 | 0.016915 | 0.002886 | -15.3214 | 66.1606 | -56.1676 | 66.1102 | -48.5046 | -54.6387 | -54.7714 | -16.5344 | 66.1331 | -56.0623 | 66.1606 | -49.791 | -54.9133 | -54.8859 | -0.10529 | -0.07782 | -0.12817 | 7.5577 | 1.2909 | 1.4236 | 1.3962 | 1.5289 | 0 | -0.10529 | -0.07782 | 6.2714 | 1.1765 | 1.149 | 1.1765 | 1.149 | 7.663 | 122.2778 | 6.2714 | 122.2229 | 122.3282 | 122.1954 | 122.2229 | 122.1954 | -122.406 | -122.3007 | 122.1725 | 122.2229 | 40.741 | 39.5279
1534.3125 | 122.4197 | -56.0623 | 66.2201 | -0.10399 | 0.023129 | 0.07427 | 0.073266 | 0.0016236 | 0.0085748 | 0.0084637 | -0.14343 | 0.018508 | 0.07207 | 0.06477 | -0.008468 | 0.020974 | 0.0084402 | -15.3854 | 66.1652 | -56.2088 | 66.0553 | -48.6099 | -54.7485 | -54.8813 | -16.5482 | 66.1377 | -56.1081 | 66.0919 | -49.7955 | -54.9042 | -54.8859 | -0.14648 | -0.054932 | -0.1648 | 7.4524 | 1.181 | 1.3138 | 1.3275 | 1.4603 | -0.045776 | -0.082398 | -0.12817 | 6.2668 | 1.1765 | 1.1581 | 1.2222 | 1.2039 | 7.5989 | 122.2641 | 6.3126 | 122.2 | 122.374 | 122.2458 | 122.2275 | 122.2 | -122.4289 | -122.3282 | 122.1176 | 122.1542 | 40.6769 | 39.5142
1535.3125 | 122.4655 | -55.9982 | 66.2292 | -0.10399 | 0.020779 | 0.072989 | 0.067926 | -0.0011536 | 0.0060114 | 0.0078229 | -8.6e-08 | 0.01744 | 0.073138 | 0.06413 | -0.008468 | 0.017128 | 0.0054496 | -15.2618 | 66.1697 | -56.1035 | 66.2247 | -48.3398 | -54.5151 | -54.6753 | -16.4566 | 66.1423 | -56.012 | 66.243 | -49.6719 | -54.7806 | -54.7623 | -0.10529 | -0.059509 | -0.004578 | 7.6584 | 1.3229 | 1.4832 | 1.4282 | 1.5884 | -0.013733 | -0.086975 | 0.013733 | 6.3263 | 1.236 | 1.2177 | 1.2497 | 1.2314 | 7.7637 | 122.3282 | 6.34 | 122.2549 | 122.2733 | 122.1542 | 122.168 | 122.1405 | -122.3328 | -122.2412 | 122.2229 | 122.2412 | 40.7364 | 39.5416
1536.3125 | 122.4014 | -55.9525 | 66.2933 | -0.11162 | 0.02142 | 0.072989 | 0.070917 | -8.538e-05 | 0.0066522 | 0.0056867 | -0.0091553 | 0.018936 | 0.074634 | 0.063916 | -0.0065454 | 0.017556 | 0.0058768 | -15.2435 | 66.2567 | -56.0806 | 66.1835 | -48.349 | -54.4876 | -54.6478 | -16.5207 | 66.2338 | -55.9753 | 66.2292 | -49.6216 | -54.8126 | -54.7943 | -0.12817 | -0.036621 | -0.10986 | 7.6035 | 1.3046 | 1.4648 | 1.4328 | 1.593 | -0.022888 | -0.059509 | -0.064087 | 6.3309 | 1.1581 | 1.1398 | 1.181 | 1.1627 | 7.7316 | 122.2641 | 6.3538 | 122.2046 | 122.3373 | 122.2092 | 122.2092 | 122.1863 | -122.374 | -122.2687 | 122.1359 | 122.1817 | 40.7089 | 39.4318
1537.3125 | 122.4838 | -55.9937 | 66.2979 | -0.096359 | 0.022702 | 0.074057 | 0.070917 | 0.0018372 | 0.0043024 | 0.0093181 | -0.061035 | 0.019363 | 0.074206 | 0.068616 | -0.0093226 | 0.018624 | 0.0054496 | -15.2802 | 66.2476 | -56.1218 | 66.1697 | -48.3765 | -54.5609 | -54.7165 | -16.5573 | 66.1972 | -56.0165 | 66.2384 | -49.6262 | -54.7943 | -54.7668 | -0.12817 | -0.050354 | -0.12817 | 7.6172 | 1.2772 | 1.4328 | 1.4053 | 1.561 | -0.022889 | -0.10071 | -0.05951 | 6.3675 | 1.2268 | 1.1993 | 1.2497 | 1.2222 | 7.7454 | 122.2916 | 6.3904 | 122.2549 | 122.3694 | 122.2137 | 122.2412 | 122.1909 | -122.4197 | -122.3145 | 122.1634 | 122.2321 | 40.7135 | 39.4363
1538.3125 | 122.3877 | -55.9937 | 66.3254 | -0.073471 | 0.020779 | 0.072989 | 0.069421 | -0.0011536 | 0.0077202 | 0.010814 | -0.015259 | 0.019576 | 0.072711 | 0.065198 | -0.0065454 | 0.017128 | 0.0084402 | -15.2023 | 66.2476 | -56.0669 | 66.2018 | -48.262 | -54.4968 | -54.6661 | -16.539 | 66.2155 | -55.9753 | 66.2476 | -49.5621 | -54.808 | -54.7668 | -0.073243 | -0.077819 | -0.1236 | 7.7316 | 1.3275 | 1.4969 | 1.4008 | 1.5701 | 0.01831 | -0.10986 | -0.077819 | 6.4316 | 1.2268 | 1.1856 | 1.2085 | 1.1673 | 7.8049 | 122.2687 | 6.4133 | 122.2229 | 122.3145 | 122.1909 | 122.2412 | 122.2092 | -122.3923 | -122.3007 | 122.1954 | 122.2412 | 40.7913 | 39.4547
1539.3125 | 122.4426 | -55.9525 | 66.3528 | -0.08873 | 0.020993 | 0.073416 | 0.070703 | 0.0039734 | 0.007293 | 0.0067547 | -0.012207 | 0.018508 | 0.075702 | 0.067548 | -0.0086816 | 0.018196 | 0.0065176 | -15.2023 | 66.2888 | -56.0486 | 66.1926 | -48.2712 | -54.5197 | -54.6844 | -16.5848 | 66.2613 | -55.9662 | 66.2567 | -49.5529 | -54.7668 | -54.7348 | -0.09613 | -0.064087 | -0.16022 | 7.6813 | 1.268 | 1.4328 | 1.3641 | 1.5289 | -0.013733 | -0.091552 | -0.09613 | 6.3995 | 1.2177 | 1.1856 | 1.2314 | 1.1993 | 7.7774 | 122.2412 | 6.4133 | 122.2229 | 122.3373 | 122.2275 | 122.2412 | 122.2137 | -122.4014 | -122.319 | 122.1451 | 122.2092 | 40.7501 | 39.3677
1540.3125 | 122.3923 | -55.9799 | 66.3116 | -0.012436 | 0.021634 | 0.075339 | 0.070489 | 0.00076902 | 0.0068658 | 0.012309 | -0.048828 | 0.019363 | 0.074847 | 0.063916 | -0.0076136 | 0.018624 | 0.0058768 | -15.2618 | 66.2659 | -56.0852 | 66.1789 | -48.2803 | -54.538 | -54.6661 | -16.6809 | 66.2292 | -55.9937 | 66.243 | -49.5255 | -54.7989 | -54.7394 | -0.10529 | -0.045777 | -0.13275 | 7.6996 | 1.3138 | 1.442 | 1.4191 | 1.5472 | -0.013733 | -0.082398 | -0.068665 | 6.4545 | 1.2405 | 1.181 | 1.2543 | 1.1948 | 7.8049 | 122.2641 | 6.4682 | 122.2366 | 122.3511 | 122.2229 | 122.2458 | 122.2092 | -122.3969 | -122.3053 | 122.1588 | 122.2229 | 40.7181 | 39.299
1541.3125 | 122.4426 | -55.9341 | 66.3574 | -0.042954 | 0.023343 | 0.071066 | 0.070489 | -0.00093998 | 0.0064386 | 0.0073955 | -0.01831 | 0.018508 | 0.073993 | 0.066052 | -0.0080408 | 0.019905 | 0.0037406 | -15.2252 | 66.3162 | -56.0715 | 66.2201 | -48.1979 | -54.4601 | -54.6204 | -16.6168 | 66.2796 | -55.925 | 66.2796 | -49.4568 | -54.7302 | -54.6936 | -0.13733 | -0.041199 | -0.13733 | 7.7362 | 1.3138 | 1.474 | 1.4511 | 1.6113 | 0.009155 | -0.07782 | -0.07782 | 6.4774 | 1.2405 | 1.2039 | 1.2314 | 1.1948 | 7.8735 | 122.2916 | 6.4682 | 122.2046 | 122.3877 | 122.2046 | 122.2504 | 122.2137 | -122.4289 | -122.2824 | 122.1542 | 122.2137 | 40.7089 | 39.3173
1542.3125 | 122.4518 | -55.9158 | 66.3849 | -0.14977 | 0.020779 | 0.072775 | 0.071344 | 0.00012822 | 0.007293 | 0.010814 | 0.0091553 | 0.019576 | 0.075061 | 0.068829 | -0.0069726 | 0.016701 | 0.004595 | -15.1886 | 66.2888 | -56.0486 | 66.2064 | -48.143 | -54.4693 | -54.6158 | -16.6489 | 66.2567 | -55.9525 | 66.2704 | -49.4476 | -54.7256 | -54.5883 | -0.13275 | -0.096131 | -0.17853 | 7.7728 | 1.3 | 1.4465 | 1.4328 | 1.5793 | -0.036621 | -0.12817 | -0.11444 | 6.4682 | 1.3275 | 1.1902 | 1.3641 | 1.2268 | 7.9056 | 122.2549 | 6.5048 | 122.2229 | 122.3373 | 122.2092 | 122.2046 | 122.1725 | -122.4335 | -122.3373 | 122.1222 | 122.1863 | 40.7272 | 39.267
1543.3125 | 122.4106 | -55.9616 | 66.3666 | -0.08873 | 0.020993 | 0.072348 | 0.07348 | -0.0024354 | 0.0070794 | 0.011027 | -0.027466 | 0.018722 | 0.074634 | 0.070966 | -0.008468 | 0.020119 | 0.0056632 | -15.2161 | 66.2842 | -56.0761 | 66.2109 | -48.143 | -54.4601 | -54.6112 | -16.658 | 66.2659 | -55.9341 | 66.275 | -49.3744 | -54.7028 | -54.689 | -0.11444 | -0.082397 | -0.15564 | 7.8186 | 1.3504 | 1.5015 | 1.4648 | 1.6159 | 0.027466 | -0.10071 | -0.091553 | 6.5872 | 1.2726 | 1.2589 | 1.2451 | 1.2314 | 7.933 | 122.287 | 6.5598 | 122.2092 | 122.3602 | 122.2 | 122.2458 | 122.2275 | -122.4426 | -122.3007 | 122.1725 | 122.2366 | 40.7455 | 39.3036
1544.3125 | 122.3969 | -55.9753 | 66.2979 | -0.096359 | 0.023343 | 0.073416 | 0.075403 | 0.0022644 | 0.007934 | 0.0084637 | -0.057983 | 0.018722 | 0.075702 | 0.070111 | -0.008468 | 0.019692 | 0.0039542 | -15.2664 | 66.2704 | -56.1035 | 66.3712 | -48.0377 | -54.6524 | -54.6616 | -16.7633 | 66.2338 | -55.9753 | 66.2659 | -49.4522 | -54.808 | -54.7211 | -0.12817 | -0.027466 | 0.073242 | 7.9376 | 1.3138 | 1.3229 | 1.442 | 1.4511 | 0 | -0.064087 | -0.032044 | 6.5231 | 1.2543 | 1.1673 | 1.2543 | 1.1673 | 8.0658 | 122.4747 | 6.5231 | 122.2412 | 122.374 | 122.2092 | 122.2458 | 122.2092 | -122.4014 | -122.2733 | 122.3465 | 122.2412 | 40.7089 | 39.212
1545.3125 | 122.4518 | -55.8792 | 66.4169 | -0.050583 | 0.024838 | 0.074698 | 0.069421 | 0.00098262 | 0.007293 | 0.010173 | -0.030517 | 0.020858 | 0.074206 | 0.073315 | -0.0069726 | 0.017556 | 0.0030996 | -15.1474 | 66.3666 | -55.9753 | 66.275 | -47.9919 | -54.364 | -54.5242 | -16.6214 | 66.3391 | -55.8975 | 66.3574 | -49.2691 | -54.6295 | -54.5837 | -0.096131 | -0.050354 | -0.14191 | 7.8873 | 1.355 | 1.5152 | 1.4511 | 1.6113 | -0.018311 | -0.07782 | -0.059509 | 6.6101 | 1.2955 | 1.2497 | 1.3138 | 1.268 | 7.9834 | 122.2504 | 6.6284 | 122.2549 | 122.3419 | 122.2366 | 122.2458 | 122.2183 | -122.3923 | -122.3145 | 122.1542 | 122.2366 | 40.7318 | 39.2578
1546.3125 | 122.4426 | -55.8609 | 66.4124 | -0.065842 | 0.023129 | 0.072775 | 0.070917 | -0.00093998 | 0.0066522 | 0.0086773 | -0.048828 | 0.019576 | 0.075061 | 0.068402 | -0.0069726 | 0.019265 | 0.0056632 | -15.1154 | 66.3666 | -55.9845 | 66.3162 | -47.937 | -54.3274 | -54.5013 | -16.5756 | 66.33 | -55.8563 | 66.3803 | -49.2188 | -54.5929 | -54.5654 | -0.1236 | -0.045777 | -0.096131 | 7.9239 | 1.3596 | 1.5335 | 1.4832 | 1.6571 | 0.004578 | -0.082398 | -0.032044 | 6.6422 | 1.2955 | 1.268 | 1.2909 | 1.2634 | 8.0475 | 122.3007 | 6.6376 | 122.2366 | 122.3511 | 122.1863 | 122.2275 | 122.1909 | -122.3969 | -122.2687 | 122.1771 | 122.2412 | 40.7455 | 39.2853
1547.3125 | 122.4289 | -55.8746 | 66.4032 | -0.073471 | 0.022915 | 0.072561 | 0.070917 | 0.0026916 | 0.0070794 | 0.0054729 | -0.042725 | 0.019149 | 0.076342 | 0.065625 | -0.0082544 | 0.020333 | 0.008013 | -15.1566 | 66.3803 | -55.9937 | 66.2613 | -47.9874 | -54.3594 | -54.5471 | -16.6809 | 66.3254 | -55.9021 | 66.3208 | -49.2645 | -54.6204 | -54.5929 | -0.11902 | -0.022888 | -0.14191 | 7.8873 | 1.3275 | 1.5152 | 1.4465 | 1.6342 | -0.027466 | -0.07782 | -0.082397 | 6.6101 | 1.2817 | 1.2543 | 1.3092 | 1.2817 | 8.0063 | 122.2549 | 6.6376 | 122.2229 | 122.374 | 122.2275 | 122.2549 | 122.2 | -122.3969 | -122.3053 | 122.1359 | 122.1954 | 40.7181 | 39.1937
1548.3125 | 122.4289 | -55.8517 | 66.3986 | -0.081101 | 0.023556 | 0.075552 | 0.071344 | 0.0048278 | 0.0066522 | 0.0082501 | -0.054932 | 0.018295 | 0.07677 | 0.060925 | -0.0071864 | 0.017983 | 0.0058768 | -15.1062 | 66.3849 | -55.9891 | 66.3071 | -47.8912 | -54.3365 | -54.5151 | -16.6443 | 66.3208 | -55.8563 | 66.3666 | -49.205 | -54.6112 | -54.5792 | -0.13733 | -0.013733 | -0.091553 | 7.9605 | 1.3367 | 1.5152 | 1.474 | 1.6525 | -0.004577 | -0.07782 | -0.032044 | 6.6467 | 1.2726 | 1.2405 | 1.2772 | 1.2451 | 8.0978 | 122.2961 | 6.6513 | 122.2229 | 122.374 | 122.1771 | 122.2366 | 122.1725 | -122.3877 | -122.2549 | 122.1588 | 122.2183 | 40.7455 | 39.2075
1549.3125 | 122.4243 | -55.8655 | 66.3757 | -0.081101 | 0.022274 | 0.073202 | 0.069421 | -0.00072638 | 0.0068658 | 0.0091045 | -0.039673 | 0.021285 | 0.074634 | 0.063275 | -0.0069726 | 0.017556 | 0.0058768 | -15.0879 | 66.3483 | -55.9982 | 66.3025 | -47.8867 | -54.3182 | -54.4876 | -16.6443 | 66.3025 | -55.8655 | 66.3666 | -49.173 | -54.5837 | -54.5517 | -0.13275 | -0.027465 | -0.073242 | 7.9788 | 1.3779 | 1.5472 | 1.5106 | 1.68 | 0 | -0.073242 | -0.009155 | 6.6925 | 1.3138 | 1.2817 | 1.3138 | 1.2817 | 8.1116 | 122.3007 | 6.6925 | 122.2321 | 122.3465 | 122.168 | 122.2137 | 122.168 | -122.374 | -122.2412 | 122.168 | 122.2321 | 40.7776 | 39.2212
1550.3125 | 122.4426 | -55.806 | 66.4398 | -0.08873 | 0.024411 | 0.074911 | 0.070276 | 0.0033324 | 0.0092156 | 0.0078229 | -0.021362 | 0.020217 | 0.075061 | 0.073956 | -0.0088952 | 0.021187 | 0.0058768 | -15.0284 | 66.4215 | -55.925 | 66.362 | -47.7631 | -54.245 | -54.4189 | -16.6122 | 66.3895 | -55.8289 | 66.4307 | -49.0265 | -54.5197 | -54.4785 | -0.11902 | -0.01831 | -0.077819 | 8.0429 | 1.387 | 1.561 | 1.506 | 1.68 | -0.022888 | -0.050354 | -0.009155 | 6.7795 | 1.3275 | 1.2863 | 1.3504 | 1.3092 | 8.1619 | 122.287 | 6.8024 | 122.2595 | 122.3465 | 122.2183 | 122.2275 | 122.1954 | -122.3648 | -122.2687 | 122.168 | 122.2366 | 40.7776 | 39.1937
1551.3125 | 122.4518 | -55.8105 | 66.4307 | -0.035324 | 0.024197 | 0.075766 | 0.069421 | 0.0026916 | 0.005584 | 0.0080365 | -0.048828 | 0.020858 | 0.076342 | 0.070325 | -0.008468 | 0.020333 | 0.0037406 | -14.9963 | 66.4307 | -55.9433 | 66.3712 | -47.7402 | -54.2358 | -54.4144 | -16.6122 | 66.362 | -55.8334 | 66.4261 | -49.0494 | -54.5471 | -54.4876 | -0.13275 | 0 | -0.059509 | 8.0704 | 1.3962 | 1.5747 | 1.5289 | 1.7075 | -0.022888 | -0.068664 | -0.004578 | 6.7612 | 1.3229 | 1.2634 | 1.3458 | 1.2863 | 8.2031 | 122.3145 | 6.7841 | 122.2595 | 122.374 | 122.1954 | 122.2412 | 122.1725 | -122.374 | -122.2641 | 122.1817 | 122.2366 | 40.8142 | 39.1983
1552.3125 | 122.4609 | -55.8151 | 66.4398 | -0.050583 | 0.023556 | 0.074698 | 0.069848 | -8.538e-05 | 0.010711 | 0.0097455 | -0.024414 | 0.020858 | 0.074847 | 0.065411 | -0.0078272 | 0.017556 | 0.0054496 | -14.9963 | 66.4307 | -55.9296 | 66.3574 | -47.7081 | -54.2084 | -54.4052 | -16.6214 | 66.3574 | -55.8197 | 66.4261 | -49.0082 | -54.5059 | -54.4693 | -0.11444 | -0.009155 | -0.082397 | 8.107 | 1.4099 | 1.6068 | 1.5244 | 1.7212 | -0.004577 | -0.082397 | -0.013733 | 6.8069 | 1.3458 | 1.3092 | 1.3504 | 1.3138 | 8.2214 | 122.287 | 6.8115 | 122.2458 | 122.3602 | 122.1771 | 122.2458 | 122.1725 | -122.3694 | -122.2595 | 122.1725 | 122.2412 | 40.8188 | 39.1937
1553.3125 | 122.4884 | -55.7785 | 66.4307 | -0.08873 | 0.023129 | 0.07662 | 0.069848 | 0.0018372 | 0.007934 | 0.0078229 | 0.067139 | 0.019576 | 0.075702 | 0.06477 | -0.0080408 | 0.016915 | 0.0071586 | -15.0284 | 66.3803 | -55.8838 | 66.3208 | -47.8088 | -54.1992 | -54.3869 | -16.6489 | 66.3116 | -55.8243 | 66.4215 | -48.9532 | -54.451 | -54.4327 | -0.10529 | -0.050354 | -0.10986 | 7.9697 | 1.3916 | 1.5793 | 1.4969 | 1.6846 | -0.045777 | -0.11902 | -0.009155 | 6.8253 | 1.3458 | 1.3275 | 1.3916 | 1.3733 | 8.075 | 122.2046 | 6.871 | 122.2458 | 122.2641 | 122.1359 | 122.1588 | 122.0901 | -122.3145 | -122.2549 | 122.0993 | 122.2 | 40.7501 | 39.1296
1554.3125 | 122.493 | -55.7831 | 66.4169 | -0.10399 | 0.023129 | 0.076834 | 0.070917 | 0.00098262 | 0.0083612 | 0.0069683 | -0.036621 | 0.017867 | 0.075915 | 0.065625 | -0.0099634 | 0.020974 | 0.0088676 | -15.0558 | 66.3986 | -55.9204 | 66.3437 | -47.7081 | -54.2496 | -54.3961 | -16.658 | 66.3757 | -55.8014 | 66.4764 | -48.9349 | -54.4647 | -54.4052 | -0.13733 | -0.01831 | -0.073242 | 8.075 | 1.387 | 1.5335 | 1.5244 | 1.6708 | -0.018311 | -0.041199 | 0.059509 | 6.8481 | 1.3779 | 1.3184 | 1.3962 | 1.3367 | 8.2123 | 122.2641 | 6.8665 | 122.2778 | 122.319 | 122.1771 | 122.1817 | 122.1588 | -122.3373 | -122.2183 | 122.1268 | 122.2595 | 40.7272 | 39.1251
1555.3125 | 122.438 | -55.751 | 66.4627 | -0.073471 | 0.024624 | 0.074057 | 0.071771 | -0.0028626 | 0.006225 | 0.0091045 | -0.067139 | 0.019363 | 0.076556 | 0.066693 | -0.0076136 | 0.020119 | 0.0058768 | -14.9689 | 66.4398 | -55.8792 | 66.3986 | -47.5845 | -54.1672 | -54.3457 | -16.6168 | 66.4261 | -55.7739 | 66.4581 | -48.8892 | -54.4556 | -54.4189 | -0.12817 | -0.022889 | -0.064087 | 8.1665 | 1.4053 | 1.5839 | 1.5335 | 1.712 | -0.022888 | -0.036622 | -0.004578 | 6.8619 | 1.3321 | 1.2955 | 1.355 | 1.3184 | 8.2947 | 122.2778 | 6.8848 | 122.2321 | 122.319 | 122.2 | 122.1909 | 122.1771 | -122.3419 | -122.2366 | 122.1497 | 122.2092 | 40.7822 | 39.1342
1556.3125 | 122.4701 | -55.751 | 66.4902 | -0.042954 | 0.024838 | 0.075125 | 0.072412 | 0.0037598 | 0.009643 | 0.0073955 | -0.076294 | 0.023208 | 0.075488 | 0.066693 | -0.0088952 | 0.019051 | 0.0050222 | -14.9872 | 66.4536 | -55.8746 | 66.4032 | -47.5479 | -54.158 | -54.3411 | -16.6626 | 66.4169 | -55.7831 | 66.481 | -48.8434 | -54.4281 | -54.4006 | -0.1236 | -0.036621 | -0.086975 | 8.2031 | 1.4099 | 1.593 | 1.5335 | 1.7166 | -0.032043 | -0.073242 | -0.009155 | 6.9077 | 1.3504 | 1.3229 | 1.3824 | 1.355 | 8.3267 | 122.2778 | 6.9397 | 122.2641 | 122.3282 | 122.2 | 122.2046 | 122.168 | -122.3648 | -122.2733 | 122.1542 | 122.2321 | 40.7639 | 39.0884
1557.3125 | 122.4289 | -55.7053 | 66.5359 | 0.048599 | 0.024624 | 0.074057 | 0.071771 | -8.538e-05 | 0.0066522 | 0.0093181 | -0.030517 | 0.020431 | 0.075702 | 0.072034 | -0.0080408 | 0.019051 | 0.0050222 | -14.9002 | 66.4993 | -55.8197 | 66.4719 | -47.4884 | -54.0939 | -54.2816 | -16.6031 | 66.4627 | -55.7419 | 66.5314 | -48.7793 | -54.3686 | -54.3274 | -0.11444 | -0.036621 | -0.064087 | 8.2169 | 1.4236 | 1.6113 | 1.5381 | 1.7258 | -0.036621 | -0.073242 | -0.004578 | 6.926 | 1.3779 | 1.3367 | 1.4145 | 1.3733 | 8.3313 | 122.2916 | 6.9626 | 122.2733 | 122.319 | 122.2046 | 122.2046 | 122.168 | -122.3557 | -122.2778 | 122.1771 | 122.2366 | 40.8051 | 39.1022
1558.3125 | 122.5067 | -55.7785 | 66.4398 | -0.096359 | 0.022061 | 0.074484 | 0.069848 | -0.00029898 | 0.0083612 | 0.0093181 | 0.054932 | 0.018936 | 0.076342 | 0.064557 | -0.0065454 | 0.019905 | 0.008013 | -15.0192 | 66.394 | -55.8792 | 66.4124 | -47.4838 | -54.1214 | -54.2999 | -16.6763 | 66.3437 | -55.7877 | 66.4627 | -48.7885 | -54.3777 | -54.364 | -0.10071 | -0.045776 | -0.027465 | 8.2947 | 1.4786 | 1.6571 | 1.5793 | 1.7578 | -0.009156 | -0.09613 | 0.022889 | 6.9901 | 1.4145 | 1.4008 | 1.4236 | 1.4099 | 8.3954 | 122.2916 | 6.9992 | 122.2504 | 122.2733 | 122.1313 | 122.1725 | 122.1222 | -122.319 | -122.2275 | 122.1909 | 122.2412 | 40.7593 | 39.1022
1559.3125 | 122.5021 | -55.7419 | 66.4627 | -0.14214 | 0.022702 | 0.078116 | 0.070276 | 0.002478 | 0.0087884 | 0.0088909 | 0.021362 | 0.019363 | 0.075274 | 0.064557 | -0.009109 | 0.019478 | 0.004595 | -14.9231 | 66.4169 | -55.8472 | 66.449 | -47.4243 | -54.0894 | -54.2404 | -16.6077 | 66.3574 | -55.7785 | 66.5314 | -48.7015 | -54.332 | -54.3228 | -0.10529 | -0.045777 | -0.013733 | 8.3176 | 1.5015 | 1.6525 | 1.6068 | 1.7578 | -0.036621 | -0.10529 | 0.068664 | 7.0404 | 1.4191 | 1.4099 | 1.4557 | 1.4465 | 8.4229 | 122.2961 | 7.077 | 122.3099 | 122.2641 | 122.1359 | 122.1588 | 122.0993 | -122.3099 | -122.2412 | 122.1909 | 122.2733 | 40.8188 | 39.1342
1560.3125 | 122.4472 | -55.6778 | 66.5771 | -0.20317 | 0.024197 | 0.074484 | 0.071985 | 0.0054688 | 0.0083612 | 0.0099591 | -0.091553 | 0.020858 | 0.073138 | 0.070325 | -0.0065454 | 0.02076 | 0.0071586 | -14.7446 | 66.5268 | -55.7968 | 66.5085 | -47.3465 | -54.0344 | -54.2313 | -16.6077 | 66.4948 | -55.6732 | 66.568 | -48.6557 | -54.3182 | -54.2953 | -0.11902 | -0.050354 | -0.068664 | 8.3313 | 1.4465 | 1.6434 | 1.5656 | 1.7624 | 0.004577 | -0.082397 | -0.009155 | 7.0221 | 1.3824 | 1.3596 | 1.3779 | 1.355 | 8.4503 | 122.3053 | 7.0175 | 122.2412 | 122.3236 | 122.168 | 122.2046 | 122.1725 | -122.374 | -122.2504 | 122.1863 | 122.2458 | 40.9332 | 39.0701
1561.3125 | 122.4152 | -55.7236 | 66.5176 | -0.065842 | 0.023556 | 0.076407 | 0.072626 | 0.0016236 | 0.0094292 | 0.011455 | -0.057983 | 0.021926 | 0.076556 | 0.065198 | -0.0088952 | 0.019692 | 0.003527 | -14.9414 | 66.4581 | -55.8792 | 66.394 | -47.4426 | -54.1168 | -54.2953 | -16.7541 | 66.4307 | -55.7785 | 66.4581 | -48.7381 | -54.3961 | -54.3732 | -0.15564 | -0.059509 | -0.1236 | 8.2809 | 1.4282 | 1.6068 | 1.5839 | 1.7624 | -0.054931 | -0.086975 | -0.059509 | 6.9855 | 1.3504 | 1.3275 | 1.4053 | 1.3824 | 8.4366 | 122.2733 | 7.0404 | 122.2366 | 122.3373 | 122.2092 | 122.1817 | 122.1542 | -122.3969 | -122.2961 | 122.1176 | 122.1817 | 40.7822 | 38.9694
1562.3125 | 122.2549 | -55.7236 | 66.4902 | -0.10399 | 0.027615 | 0.07363 | 0.071985 | -0.0015808 | 0.0092156 | 0.0106 | -0.042725 | 0.019363 | 0.074634 | 0.065839 | -0.0071864 | 0.018624 | 0.0073722 | -14.8911 | 66.5085 | -55.8151 | 66.4169 | -47.438 | -54.1214 | -54.2862 | -16.7862 | 66.4993 | -55.7327 | 66.4673 | -48.7152 | -54.4098 | -54.2633 | -0.091553 | 0.018311 | -0.073242 | 8.2855 | 1.4374 | 1.6022 | 1.5289 | 1.6937 | -0.009155 | 0.009156 | -0.022888 | 7.0084 | 1.4603 | 1.3138 | 1.4694 | 1.3229 | 8.3771 | 122.2321 | 7.0175 | 122.2 | 122.3236 | 122.2321 | 122.2321 | 122.2229 | -122.3053 | -122.2229 | 122.1405 | 122.1909 | 40.8325 | 38.9374
1563.3125 | 122.4792 | -55.6961 | 66.5405 | -0.11162 | 0.024838 | 0.07662 | 0.070062 | -0.0015808 | 0.0081476 | 0.0091045 | 0.015259 | 0.01979 | 0.075274 | 0.061139 | -0.008468 | 0.017128 | 0.0071586 | -14.9002 | 66.4856 | -55.7739 | 66.5085 | -47.2687 | -54.007 | -54.1763 | -16.6672 | 66.4169 | -55.719 | 66.5543 | -48.5596 | -54.2587 | -54.245 | -0.07782 | -0.054931 | -0.032043 | 8.4274 | 1.5198 | 1.6891 | 1.5976 | 1.767 | -0.022888 | -0.1236 | 0.013733 | 7.1365 | 1.4511 | 1.4374 | 1.474 | 1.4603 | 8.5052 | 122.2824 | 7.1594 | 122.2733 | 122.2595 | 122.1359 | 122.1817 | 122.113 | -122.3145 | -122.2595 | 122.2046 | 122.2504 | 40.7959 | 39.0289
1564.3125 | 122.4014 | -55.7007 | 66.5863 | -0.08873 | 0.024411 | 0.074911 | 0.072626 | 0.00055542 | 0.0098566 | 0.0091045 | -0.067139 | 0.022781 | 0.073352 | 0.069897 | -0.0093226 | 0.019905 | 0.0060904 | -14.8773 | 66.5405 | -55.7785 | 66.4764 | -47.2916 | -54.0115 | -54.2038 | -16.7267 | 66.5085 | -55.6732 | 66.5588 | -48.5641 | -54.2953 | -54.2633 | -0.077819 | -0.045777 | -0.10986 | 8.4091 | 1.4969 | 1.6891 | 1.5747 | 1.767 | 0.027466 | -0.07782 | -0.027466 | 7.1365 | 1.4374 | 1.4053 | 1.4099 | 1.3779 | 8.4869 | 122.2549 | 7.1091 | 122.2321 | 122.319 | 122.1817 | 122.2412 | 122.2092 | -122.3648 | -122.2595 | 122.1771 | 122.2595 | 40.8234 | 38.974
1565.3125 | 122.3648 | -55.687 | 66.6092 | -0.10399 | 0.024197 | 0.075339 | 0.070917 | 0.0033324 | 0.0085748 | 0.0078229 | -0.064087 | 0.021713 | 0.075702 | 0.06712 | -0.0082544 | 0.02076 | 0.0058768 | -14.8224 | 66.5817 | -55.7831 | 66.4764 | -47.287 | -54.0253 | -54.213 | -16.7633 | 66.5588 | -55.6732 | 66.5314 | -48.5596 | -54.3457 | -54.2542 | -0.09613 | -0.027466 | -0.13275 | 8.4 | 1.474 | 1.6617 | 1.5701 | 1.7578 | 0.013733 | -0.050354 | -0.07782 | 7.1274 | 1.4328 | 1.3412 | 1.4191 | 1.3275 | 8.4961 | 122.2595 | 7.1136 | 122.2046 | 122.3648 | 122.2321 | 122.2687 | 122.2458 | -122.3923 | -122.2824 | 122.1634 | 122.2183 | 40.8646 | 38.9236
1566.3125 | 122.3602 | -55.6183 | 66.6687 | -0.027695 | 0.02377 | 0.075125 | 0.072839 | 0.0048278 | 0.009002 | 0.010386 | -0.054932 | 0.019363 | 0.074847 | 0.072675 | -0.0095362 | 0.020974 | 0.0056632 | -14.8132 | 66.6367 | -55.7053 | 66.5176 | -47.2 | -53.9795 | -54.1489 | -16.7587 | 66.5909 | -55.632 | 66.5771 | -48.4863 | -54.2633 | -54.2175 | -0.086975 | -0.032043 | -0.15106 | 8.4183 | 1.4694 | 1.6388 | 1.5564 | 1.7258 | -0.013733 | -0.07782 | -0.091553 | 7.132 | 1.4008 | 1.355 | 1.4145 | 1.3687 | 8.5052 | 122.2229 | 7.1457 | 122.2092 | 122.3419 | 122.2229 | 122.2549 | 122.2092 | -122.374 | -122.3007 | 122.1359 | 122.1954 | 40.8051 | 38.8596
1567.3125 | 122.374 | -55.5771 | 66.6779 | -0.058212 | 0.026333 | 0.076193 | 0.073266 | 0.0011962 | 0.010284 | 0.0099591 | -0.07019 | 0.019363 | 0.076556 | 0.073102 | -0.0078272 | 0.021187 | 0.008013 | -14.7995 | 66.6321 | -55.7281 | 66.5268 | -47.1725 | -53.9566 | -54.1397 | -16.7221 | 66.5955 | -55.5817 | 66.5909 | -48.4451 | -54.245 | -54.2038 | -0.15106 | -0.045776 | -0.15106 | 8.4045 | 1.4374 | 1.6205 | 1.5884 | 1.7715 | -0.004578 | -0.082397 | -0.086975 | 7.132 | 1.3733 | 1.3321 | 1.3779 | 1.3367 | 8.5556 | 122.2549 | 7.1365 | 122.1725 | 122.3602 | 122.1771 | 122.2092 | 122.1725 | -122.406 | -122.2595 | 122.1039 | 122.168 | 40.7776 | 38.855
1568.3125 | 122.5433 | -55.5496 | 66.6458 | -0.11925 | 0.024838 | 0.072775 | 0.069635 | 0.0046142 | 0.0081476 | 0.010173 | 0.018311 | 0.02214 | 0.075061 | 0.067548 | -0.0076136 | 0.020333 | 0.0088676 | -14.7217 | 66.5451 | -55.6824 | 66.6504 | -46.9803 | -53.8376 | -54.0115 | -16.5894 | 66.5451 | -55.5817 | 66.7282 | -48.2483 | -54.0802 | -54.0619 | -0.13275 | -0.10071 | 0.004578 | 8.5693 | 1.5381 | 1.712 | 1.6708 | 1.8448 | -0.032043 | -0.10071 | 0.082397 | 7.3013 | 1.4877 | 1.4694 | 1.5198 | 1.5015 | 8.7021 | 122.3328 | 7.3334 | 122.3099 | 122.2275 | 122.1268 | 122.0947 | 122.0947 | -122.3282 | -122.2275 | 122.2 | 122.2778 | 40.8279 | 38.9603
1569.3125 | 122.4838 | -55.5725 | 66.6504 | -0.12688 | 0.025265 | 0.076407 | 0.070489 | -0.0013672 | 0.01007 | 0.0059003 | 0.057983 | 0.021926 | 0.076556 | 0.061993 | -0.0044092 | 0.021614 | 0.0048086 | -14.7491 | 66.5817 | -55.6778 | 66.5817 | -47.0261 | -53.8559 | -54.0344 | -16.6626 | 66.5451 | -55.5771 | 66.6641 | -48.2803 | -54.1031 | -54.0939 | -0.10529 | -0.068665 | -0.068665 | 8.5464 | 1.5381 | 1.7166 | 1.6434 | 1.8219 | -0.004577 | -0.10529 | 0.013733 | 7.2922 | 1.4786 | 1.4694 | 1.4832 | 1.474 | 8.6517 | 122.2595 | 7.2968 | 122.2412 | 122.2595 | 122.1222 | 122.1542 | 122.1176 | -122.3282 | -122.2275 | 122.1542 | 122.2366 | 40.8234 | 38.9099
1570.3125 | 122.438 | -55.5176 | 66.7282 | -0.12688 | 0.027188 | 0.075979 | 0.070489 | -8.538e-05 | 0.0077202 | 0.0095319 | -0.073242 | 0.021072 | 0.076342 | 0.074383 | -0.0088952 | 0.019265 | 0.0069448 | -14.653 | 66.6779 | -55.6686 | 66.6321 | -46.9666 | -53.8239 | -54.0253 | -16.6534 | 66.6641 | -55.5359 | 66.687 | -48.2574 | -54.0939 | -54.0756 | -0.15106 | -0.050354 | -0.09613 | 8.551 | 1.4923 | 1.6937 | 1.6434 | 1.8448 | -0.018311 | -0.064086 | -0.041198 | 7.2601 | 1.442 | 1.4236 | 1.4603 | 1.442 | 8.7021 | 122.3007 | 7.2784 | 122.2229 | 122.3465 | 122.2 | 122.1954 | 122.1817 | -122.3969 | -122.2641 | 122.1497 | 122.2046 | 40.8646 | 38.8641
1571.3125 | 122.4243 | -55.4672 | 66.7694 | 0.018082 | 0.024838 | 0.075979 | 0.075403 | 0.0018372 | 0.009002 | 0.0095319 | -0.067139 | 0.023208 | 0.076342 | 0.066052 | -0.0088952 | 0.021828 | 0.0075858 | -14.5432 | 66.806 | -55.5725 | 66.6595 | -46.9345 | -53.8239 | -53.9749 | -16.6397 | 66.7236 | -55.4993 | 66.7374 | -48.1796 | -54.071 | -54.0161 | -0.10529 | 0.036621 | -0.10986 | 8.5327 | 1.4923 | 1.6434 | 1.5976 | 1.7487 | -0.032044 | -0.045776 | -0.032043 | 7.2876 | 1.4511 | 1.3962 | 1.4832 | 1.4282 | 8.638 | 122.2321 | 7.3196 | 122.2366 | 122.3785 | 122.2229 | 122.2733 | 122.1909 | -122.3419 | -122.2687 | 122.1268 | 122.2046 | 40.9241 | 38.8275
1572.3125 | 122.4152 | -55.5267 | 66.7099 | 0.11726 | 0.023983 | 0.074911 | 0.07113 | -0.00029898 | 0.0092156 | 0.0099591 | -0.088501 | 0.020217 | 0.077624 | 0.070752 | -0.009109 | 0.022255 | 0.0075858 | -14.7583 | 66.7099 | -55.6137 | 66.5909 | -46.9711 | -53.8513 | -54.0344 | -16.7267 | 66.6595 | -55.545 | 66.687 | -48.2208 | -54.1077 | -54.0619 | -0.086975 | 0 | -0.11902 | 8.5556 | 1.4923 | 1.6754 | 1.5793 | 1.7624 | -0.018311 | -0.050354 | -0.022888 | 7.3059 | 1.4648 | 1.4191 | 1.4832 | 1.4374 | 8.6426 | 122.2046 | 7.3242 | 122.2321 | 122.3236 | 122.2046 | 122.2366 | 122.1863 | -122.3236 | -122.2549 | 122.1176 | 122.2137 | 40.7684 | 38.8
1573.3125 | 122.4106 | -55.4535 | 66.7419 | -0.10399 | 0.026761 | 0.078543 | 0.074121 | 0.002478 | 0.011566 | 0.011241 | -0.057983 | 0.022781 | 0.075488 | 0.072247 | -0.0080408 | 0.021614 | 0.0086538 | -14.5706 | 66.7694 | -55.5725 | 66.655 | -46.875 | -53.7827 | -53.9703 | -16.6992 | 66.7511 | -55.4764 | 66.7236 | -48.1339 | -54.0436 | -54.0207 | -0.11902 | 0.027466 | -0.086975 | 8.5785 | 1.4832 | 1.6708 | 1.6022 | 1.7899 | -0.022888 | 0.009156 | -0.01831 | 7.3196 | 1.4328 | 1.4099 | 1.4557 | 1.4328 | 8.6975 | 122.2275 | 7.3425 | 122.2 | 122.3419 | 122.2275 | 122.2229 | 122.2046 | -122.3145 | -122.2183 | 122.1085 | 122.1771 | 40.8829 | 38.7543
1574.3125 | 122.4564 | -55.4352 | 66.7465 | -0.11162 | 0.026333 | 0.076193 | 0.069421 | -0.0024354 | 0.0094292 | 0.010814 | 0.024414 | 0.019576 | 0.075915 | 0.066693 | -0.0078272 | 0.021187 | 0.0056632 | -14.5844 | 66.6916 | -55.5634 | 66.7099 | -46.7194 | -53.7003 | -53.8834 | -16.5665 | 66.6779 | -55.4581 | 66.8015 | -48.024 | -53.9474 | -53.9337 | -0.12817 | -0.054932 | -0.036621 | 8.7158 | 1.5518 | 1.7349 | 1.68 | 1.8631 | -0.022888 | -0.068665 | 0.054932 | 7.4112 | 1.5015 | 1.4877 | 1.5244 | 1.5106 | 8.844 | 122.2733 | 7.4341 | 122.2595 | 122.2549 | 122.1359 | 122.1268 | 122.113 | -122.3099 | -122.2046 | 122.1451 | 122.2366 | 40.8508 | 38.8687
1575.3125 | 122.4243 | -55.3619 | 66.8701 | -0.10399 | 0.025479 | 0.07662 | 0.073053 | 0.002478 | 0.0098566 | 0.012523 | -0.045776 | 0.020431 | 0.074847 | 0.070538 | -0.0095362 | 0.019265 | 0.0069448 | -14.534 | 66.8106 | -55.5313 | 66.7191 | -46.7743 | -53.7094 | -53.8651 | -16.6168 | 66.8015 | -55.4123 | 66.8152 | -48.0103 | -53.9612 | -53.9154 | -0.16937 | -0.059509 | -0.15106 | 8.5876 | 1.4969 | 1.6525 | 1.6663 | 1.8219 | -0.050354 | -0.068664 | -0.054931 | 7.3517 | 1.4465 | 1.4008 | 1.4969 | 1.4511 | 8.757 | 122.2504 | 7.402 | 122.2275 | 122.3419 | 122.2137 | 122.1725 | 122.1634 | -122.4014 | -122.2824 | 122.081 | 122.1771 | 40.8279 | 38.7451
1576.3125 | 122.493 | -55.3711 | 66.8427 | -0.11162 | 0.025692 | 0.073416 | 0.070276 | 0.0016236 | 0.0070794 | 0.0084637 | -0.036621 | 0.020431 | 0.075488 | 0.07182 | -0.009109 | 0.019905 | 0.0058768 | -14.5203 | 66.8152 | -55.513 | 66.7419 | -46.6736 | -53.6636 | -53.8284 | -16.5985 | 66.7557 | -55.4031 | 66.8747 | -47.905 | -53.8742 | -53.8422 | -0.14191 | -0.027465 | -0.10071 | 8.6975 | 1.5427 | 1.7075 | 1.6846 | 1.8494 | -0.032043 | -0.086975 | 0.032044 | 7.4661 | 1.5289 | 1.4969 | 1.561 | 1.5289 | 8.8394 | 122.2549 | 7.4982 | 122.2778 | 122.3282 | 122.1588 | 122.1863 | 122.1268 | -122.3557 | -122.2458 | 122.113 | 122.2458 | 40.8508 | 38.7726
1577.3125 | 122.3923 | -55.3299 | 66.9205 | -0.11925 | 0.026761 | 0.075125 | 0.074121 | -0.0013672 | 0.010284 | 0.011668 | -0.079346 | 0.022354 | 0.075702 | 0.071393 | -0.0061182 | 0.024605 | 0.0075858 | -14.5203 | 66.8884 | -55.4672 | 66.7648 | -46.6827 | -53.6728 | -53.8376 | -16.6946 | 66.861 | -55.3802 | 66.9067 | -47.6486 | -53.9291 | -53.9246 | -0.13733 | -0.032043 | -0.15564 | 8.6472 | 1.4923 | 1.6571 | 1.6296 | 1.7944 | -0.050354 | -0.059509 | -0.013733 | 7.6813 | 1.4053 | 1.4008 | 1.4557 | 1.4511 | 8.7845 | 122.2321 | 7.7316 | 122.287 | 122.3557 | 122.2412 | 122.2183 | 122.1909 | -122.3877 | -122.3007 | 122.0947 | 122.2366 | 40.8096 | 38.6353
1578.3125 | 122.4976 | -55.3757 | 66.7831 | -0.12688 | 0.026547 | 0.076407 | 0.071771 | 0.0029052 | 0.009002 | 0.010173 | -0.024414 | 0.02214 | 0.073565 | 0.068188 | -0.0082544 | 0.020333 | 0.0056632 | -14.5432 | 66.774 | -55.5267 | 66.7282 | -46.6415 | -53.6407 | -53.8376 | -16.6214 | 66.7419 | -55.4214 | 66.8655 | -47.8592 | -53.8422 | -53.8422 | -0.15106 | -0.009155 | -0.054932 | 8.7341 | 1.5381 | 1.7349 | 1.6891 | 1.886 | -0.045777 | -0.041199 | 0.082398 | 7.5165 | 1.5335 | 1.5335 | 1.5793 | 1.5793 | 8.8852 | 122.2549 | 7.5623 | 122.287 | 122.3007 | 122.1634 | 122.1497 | 122.1176 | -122.3099 | -122.2046 | 122.1039 | 122.2412 | 40.8325 | 38.7543
1579.3125 | 122.4701 | -55.2475 | 66.9388 | -0.16502 | 0.024624 | 0.077688 | 0.069208 | 0.0044006 | 0.0092156 | 0.0082501 | 0.0091553 | 0.023208 | 0.075488 | 0.065839 | -0.0086816 | 0.019905 | 0.0067312 | -14.3829 | 66.8884 | -55.3802 | 66.893 | -46.4355 | -53.4897 | -53.6728 | -16.507 | 66.8564 | -55.2704 | 66.9571 | -47.7173 | -53.7094 | -53.7323 | -0.13275 | -0.050354 | -0.045777 | 8.812 | 1.5747 | 1.7578 | 1.7075 | 1.8906 | -0.022888 | -0.082398 | 0.01831 | 7.5302 | 1.5152 | 1.5381 | 1.5381 | 1.561 | 8.9447 | 122.2733 | 7.5531 | 122.2275 | 122.2687 | 122.1268 | 122.1359 | 122.1039 | -122.319 | -122.2092 | 122.1405 | 122.2046 | 40.8646 | 38.7405
1580.3125 | 122.4106 | -55.3894 | 66.861 | -0.11162 | 0.026333 | 0.076193 | 0.07348 | -0.0039306 | 0.011138 | 0.0065411 | -0.10071 | 0.020645 | 0.075702 | 0.065839 | -0.0071864 | 0.022896 | 0.0071586 | -14.4516 | 66.8564 | -55.4855 | 66.7419 | -46.6141 | -53.6591 | -53.8239 | -16.6855 | 66.7969 | -55.3848 | 66.8198 | -47.85 | -53.8788 | -53.8422 | -0.096131 | -0.004578 | -0.11902 | 8.7753 | 1.5656 | 1.7303 | 1.6617 | 1.8265 | 0.004577 | -0.064087 | -0.041199 | 7.5394 | 1.5472 | 1.5106 | 1.5427 | 1.506 | 8.8715 | 122.2275 | 7.5348 | 122.2046 | 122.3419 | 122.1817 | 122.2458 | 122.1863 | -122.3465 | -122.2458 | 122.1313 | 122.2092 | 40.9378 | 38.7039
1581.3125 | 122.4152 | -55.2887 | 66.9571 | -0.12688 | 0.028256 | 0.074911 | 0.074548 | -0.00093998 | 0.0098566 | 0.011027 | -0.054932 | 0.021926 | 0.074847 | 0.073315 | -0.0095362 | 0.021401 | 0.011858 | -14.3875 | 66.8976 | -55.4123 | 66.8152 | -46.5042 | -53.5492 | -53.7506 | -16.5939 | 66.8793 | -55.3024 | 66.9159 | -47.731 | -53.8055 | -53.7689 | -0.1236 | -0.059509 | -0.14191 | 8.7845 | 1.5381 | 1.7395 | 1.6617 | 1.8631 | -0.013733 | -0.07782 | -0.041198 | 7.5577 | 1.5198 | 1.4832 | 1.5335 | 1.4969 | 8.9081 | 122.2275 | 7.5714 | 122.2183 | 122.3099 | 122.1817 | 122.1863 | 122.168 | -122.3694 | -122.2595 | 122.1039 | 122.2046 | 40.9012 | 38.6948
1582.3125 | 122.525 | -55.2292 | 66.9525 | -0.08873 | 0.026974 | 0.078756 | 0.071985 | 0.0014098 | 0.010925 | 0.0073955 | -0.042725 | 0.023422 | 0.075061 | 0.068402 | -0.0095362 | 0.021401 | 0.0056632 | -14.3417 | 66.9296 | -55.3711 | 66.9022 | -46.3806 | -53.4485 | -53.6545 | -16.4841 | 66.8838 | -55.2887 | 67.0212 | -47.5891 | -53.6545 | -53.6316 | -0.14191 | -0.022889 | -0.050354 | 8.8486 | 1.5747 | 1.7807 | 1.7166 | 1.9226 | -0.059509 | -0.068665 | 0.068664 | 7.6401 | 1.5976 | 1.5747 | 1.6571 | 1.6342 | 8.9905 | 122.2733 | 7.6996 | 122.3099 | 122.3007 | 122.1725 | 122.1588 | 122.113 | -122.3236 | -122.2412 | 122.1313 | 122.2504 | 40.8875 | 38.7451
1583.3125 | 122.5159 | -55.2612 | 66.9342 | -0.13451 | 0.027401 | 0.075339 | 0.071985 | -0.00029898 | 0.010284 | 0.010386 | -0.07019 | 0.024703 | 0.076556 | 0.076306 | -0.0099634 | 0.022042 | 0.011645 | -14.3463 | 66.9067 | -55.394 | 66.8793 | -46.3623 | -53.476 | -53.6636 | -16.5298 | 66.861 | -55.2841 | 67.0029 | -47.5708 | -53.6636 | -53.6499 | -0.13275 | -0.027466 | -0.054932 | 8.8989 | 1.5976 | 1.7853 | 1.7303 | 1.918 | -0.022889 | -0.073242 | 0.068665 | 7.6904 | 1.6113 | 1.5976 | 1.6342 | 1.6205 | 9.0317 | 122.2733 | 7.7133 | 122.287 | 122.3007 | 122.1451 | 122.168 | 122.1222 | -122.3282 | -122.2183 | 122.1405 | 122.2641 | 40.9149 | 38.7314
1584.3125 | 122.4426 | -55.22 | 66.9754 | -0.11925 | 0.025906 | 0.075766 | 0.070062 | 0.0011962 | 0.01007 | 0.0099591 | 0.018311 | 0.022567 | 0.076129 | 0.06477 | -0.008468 | 0.018624 | 0.0084402 | -14.2548 | 66.9434 | -55.3162 | 66.9205 | -46.2799 | -53.3936 | -53.5904 | -16.4978 | 66.8747 | -55.2338 | 67.0258 | -47.5159 | -53.6316 | -53.6407 | -0.09613 | -0.032044 | -0.054932 | 8.9401 | 1.6296 | 1.8265 | 1.7258 | 1.9226 | -0.013733 | -0.10071 | 0.050354 | 7.7042 | 1.5793 | 1.5884 | 1.593 | 1.6022 | 9.0363 | 122.2366 | 7.7179 | 122.2595 | 122.2595 | 122.1085 | 122.1634 | 122.0947 | -122.2916 | -122.2092 | 122.1405 | 122.2458 | 40.9653 | 38.7222
1585.3125 | 122.5113 | -55.0735 | 67.1173 | -0.11925 | 0.027615 | 0.078116 | 0.073266 | 0.0037598 | 0.010284 | 0.0095319 | -0.057983 | 0.024063 | 0.074634 | 0.072888 | -0.0086816 | 0.020974 | 0.0039542 | -14.1907 | 67.0624 | -55.2338 | 67.0624 | -46.1288 | -53.2883 | -53.4988 | -16.3376 | 67.0212 | -55.1239 | 67.1631 | -47.3282 | -53.4988 | -53.4714 | -0.16022 | -0.054932 | -0.054932 | 8.9447 | 1.5747 | 1.7853 | 1.7349 | 1.9455 | -0.050354 | -0.096131 | 0.045776 | 7.7454 | 1.6022 | 1.5747 | 1.6525 | 1.6251 | 9.1049 | 122.2961 | 7.7957 | 122.287 | 122.2961 | 122.1451 | 122.1359 | 122.0947 | -122.3511 | -122.2412 | 122.1359 | 122.2366 | 40.8829 | 38.736
1586.3125 | 122.5296 | -54.982 | 67.1585 | -0.11162 | 0.02847 | 0.075552 | 0.072198 | 0.0056824 | 0.011566 | 0.010814 | -0.0030517 | 0.023422 | 0.072284 | 0.069043 | -0.0095362 | 0.023964 | 0.0090812 | -14.0579 | 67.1265 | -55.1239 | 67.2638 | -45.7397 | -53.1097 | -53.4073 | -16.2369 | 67.0944 | -55.0186 | 67.3004 | -47.2 | -53.3569 | -53.3432 | -0.14191 | -0.032043 | 0.10529 | 9.2422 | 1.5747 | 1.8723 | 1.7166 | 2.0142 | -0.036621 | -0.064087 | 0.14191 | 7.782 | 1.6388 | 1.6251 | 1.6754 | 1.6617 | 9.3842 | 122.3877 | 7.8186 | 122.319 | 122.2504 | 122.113 | 122.1085 | 122.0764 | -122.2824 | -122.1771 | 122.2458 | 122.2824 | 40.9241 | 38.7451
1587.3125 | 122.5067 | -54.9911 | 67.2043 | -0.073471 | 0.023556 | 0.077261 | 0.072626 | -0.00051278 | 0.010711 | 0.011027 | -0.042725 | 0.022567 | 0.076129 | 0.069257 | -0.0099634 | 0.022255 | 0.008013 | -14.1083 | 67.1768 | -55.1102 | 67.1722 | -45.9824 | -53.1647 | -53.3661 | -16.2781 | 67.1219 | -55.0186 | 67.2821 | -47.1725 | -53.3661 | -53.3478 | -0.11902 | -0.027466 | -0.032044 | 9.0088 | 1.6251 | 1.8265 | 1.7441 | 1.9455 | -0.027466 | -0.082398 | 0.077819 | 7.8186 | 1.6434 | 1.6251 | 1.6708 | 1.6525 | 9.1278 | 122.2824 | 7.8461 | 122.3007 | 122.287 | 122.1405 | 122.168 | 122.113 | -122.3145 | -122.2229 | 122.1634 | 122.2733 | 40.8829 | 38.7131
1588.3125 | 122.5159 | -54.9728 | 67.2134 | -0.14977 | 0.02612 | 0.075125 | 0.070703 | 0.0026916 | 0.011352 | 0.0080365 | -0.024414 | 0.022994 | 0.074847 | 0.067548 | -0.0086816 | 0.021187 | 0.0095084 | -14.035 | 67.1585 | -55.0735 | 67.3187 | -45.6757 | -53.1418 | -53.3524 | -16.2277 | 67.1173 | -54.9866 | 67.305 | -47.1497 | -53.3249 | -53.3386 | -0.10071 | -0.054932 | 0.10529 | 9.2972 | 1.6205 | 1.8311 | 1.7212 | 1.9318 | -0.013733 | -0.09613 | 0.091553 | 7.8232 | 1.6342 | 1.6479 | 1.6479 | 1.6617 | 9.3979 | 122.3923 | 7.8369 | 122.2916 | 122.2321 | 122.1039 | 122.1313 | 122.0901 | -122.287 | -122.2 | 122.2916 | 122.2778 | 40.9378 | 38.7451
1589.3125 | 122.5159 | -54.9088 | 67.2775 | -0.15739 | 0.028256 | 0.076834 | 0.070917 | 0.0020508 | 0.009643 | 0.0088909 | -0.0091553 | 0.023635 | 0.070361 | 0.075238 | -0.008468 | 0.019478 | 0.004595 | -14.0213 | 67.2226 | -55.014 | 67.4194 | -45.639 | -53.1281 | -53.2745 | -16.1682 | 67.186 | -54.9316 | 67.3691 | -47.0581 | -53.2516 | -53.2562 | -0.10529 | -0.054932 | 0.14191 | 9.2697 | 1.6342 | 1.7807 | 1.7395 | 1.886 | -0.022889 | -0.091553 | 0.091553 | 7.8506 | 1.6525 | 1.6571 | 1.6754 | 1.68 | 9.375 | 122.4335 | 7.8735 | 122.3007 | 122.2366 | 122.1176 | 122.1313 | 122.0947 | -122.2916 | -122.2092 | 122.3282 | 122.2778 | 40.8875 | 38.7405
1590.3125 | 122.5113 | -54.9225 | 67.2775 | -0.12688 | 0.027615 | 0.077261 | 0.072839 | -0.0011536 | 0.010925 | 0.011882 | -0.01831 | 0.02214 | 0.073779 | 0.075452 | -0.011245 | 0.023323 | 0.0067312 | -13.9435 | 67.2226 | -55.0049 | 67.4011 | -45.6436 | -53.1281 | -53.2608 | -16.1774 | 67.1448 | -54.9225 | 67.3737 | -47.0352 | -53.2288 | -53.2379 | -0.082398 | -0.054932 | 0.1236 | 9.2789 | 1.6617 | 1.7944 | 1.7441 | 1.8768 | 0 | -0.13275 | 0.09613 | 7.8873 | 1.6846 | 1.6937 | 1.6846 | 1.6937 | 9.3613 | 122.406 | 7.8873 | 122.2961 | 122.2275 | 122.0673 | 122.1451 | 122.0673 | -122.2824 | -122.2 | 122.3236 | 122.2961 | 40.979 | 38.7451
1591.3125 | 122.5204 | -54.895 | 67.2546 | -0.08873 | 0.028256 | 0.077261 | 0.074121 | -0.0030762 | 0.009002 | 0.0099591 | -0.05188 | 0.022567 | 0.07442 | 0.073102 | -0.0097498 | 0.021401 | 0.0067312 | -13.9206 | 67.2043 | -55.0232 | 67.3691 | -45.8359 | -53.0502 | -53.183 | -16.1362 | 67.186 | -54.9362 | 67.3553 | -46.9849 | -53.1921 | -53.2242 | -0.12817 | -0.050354 | 0.11444 | 9.0591 | 1.712 | 1.8448 | 1.8402 | 1.973 | -0.041198 | -0.068665 | 0.10071 | 7.9102 | 1.6708 | 1.7029 | 1.712 | 1.7441 | 9.1873 | 122.3923 | 7.9514 | 122.2916 | 122.2275 | 122.1222 | 122.0993 | 122.081 | -122.2778 | -122.1909 | 122.2641 | 122.2504 | 40.9744 | 38.7589
1592.3125 | 122.4838 | -54.8401 | 67.3553 | -0.096359 | 0.028256 | 0.078756 | 0.071344 | 0.0037598 | 0.0094292 | 0.010173 | -0.015259 | 0.022354 | 0.075702 | 0.070538 | -0.009109 | 0.021187 | 0.0077994 | -13.8382 | 67.3004 | -54.9362 | 67.3553 | -45.6207 | -52.9449 | -53.1143 | -16.0629 | 67.2501 | -54.8492 | 67.4149 | -46.9025 | -53.1601 | -53.1738 | -0.09613 | -0.054932 | 0 | 9.2194 | 1.7258 | 1.8951 | 1.8219 | 1.9913 | -0.009155 | -0.10529 | 0.059509 | 7.9376 | 1.6663 | 1.68 | 1.6754 | 1.6891 | 9.3155 | 122.2916 | 7.9468 | 122.2641 | 122.2366 | 122.0993 | 122.1405 | 122.0901 | -122.2916 | -122.2046 | 122.1954 | 122.2549 | 41.0019 | 38.7772
1593.3125 | 122.5159 | -54.808 | 67.392 | -0.12688 | 0.028042 | 0.077475 | 0.073053 | 0.0022644 | 0.0077202 | 0.013591 | -0.05188 | 0.02214 | 0.074847 | 0.066266 | -0.0093226 | 0.019692 | 0.0054496 | -13.7604 | 67.337 | -54.9271 | 67.5156 | -45.5704 | -53.009 | -53.1006 | -16.0263 | 67.305 | -54.8172 | 67.4652 | -46.8475 | -53.1097 | -53.1281 | -0.11902 | -0.054932 | 0.1236 | 9.2377 | 1.7075 | 1.799 | 1.8265 | 1.918 | -0.009156 | -0.086975 | 0.073242 | 7.9605 | 1.68 | 1.6983 | 1.6891 | 1.7075 | 9.3567 | 122.4426 | 7.9697 | 122.2824 | 122.2641 | 122.1222 | 122.1451 | 122.113 | -122.319 | -122.2092 | 122.3236 | 122.2733 | 41.0477 | 38.7817
1594.3125 | 122.4152 | -54.6753 | 67.5339 | -0.058212 | 0.028256 | 0.076193 | 0.071344 | -0.007135 | 0.007934 | 0.0095319 | 0.027466 | 0.022354 | 0.07442 | 0.06712 | -0.0095362 | 0.021187 | 0.0033134 | -13.6185 | 67.4789 | -54.7485 | 67.5751 | -45.3461 | -52.684 | -52.8992 | -15.8066 | 67.4469 | -54.6524 | 67.5842 | -46.3257 | -52.8534 | -53.0777 | -0.073242 | -0.054932 | 0.041198 | 9.3292 | 1.7761 | 1.9913 | 1.8494 | 2.0645 | 0.022888 | -0.086976 | 0.050354 | 8.3496 | 1.5976 | 1.8219 | 1.5747 | 1.799 | 9.4025 | 122.3236 | 8.3267 | 122.2366 | 122.2275 | 122.0993 | 122.1542 | 122.1222 | -122.2824 | -122.1863 | 122.2504 | 122.2595 | 41.0568 | 38.8687
1595.3125 | 122.5113 | -54.5517 | 67.6254 | -0.14977 | 0.027829 | 0.077688 | 0.073694 | 0.0020508 | 0.011138 | 0.010814 | -0.048828 | 0.022567 | 0.074206 | 0.072247 | -0.010604 | 0.021401 | 0.0071586 | -13.4995 | 67.5568 | -54.6936 | 67.6941 | -45.3873 | -52.6703 | -52.8122 | -15.802 | 67.5201 | -54.57 | 67.717 | -46.5363 | -52.858 | -52.8717 | -0.14191 | -0.068664 | 0.068665 | 9.1644 | 1.7395 | 1.8814 | 1.8814 | 2.0233 | -0.01831 | -0.10528 | 0.091553 | 8.0154 | 1.68 | 1.6937 | 1.6983 | 1.712 | 9.3063 | 122.3877 | 8.0338 | 122.287 | 122.2504 | 122.0901 | 122.1085 | 122.0718 | -122.319 | -122.1954 | 122.2458 | 122.2687 | 41.0522 | 38.7497
1596.3125 | 122.4701 | -54.4373 | 67.7307 | -0.12688 | 0.027188 | 0.074911 | 0.070703 | -0.0028626 | 0.0094292 | 0.014232 | -0.015259 | 0.022567 | 0.076342 | 0.073315 | -0.0071864 | 0.02076 | 0.0075858 | -13.472 | 67.6941 | -54.5654 | 67.6941 | -45.1813 | -52.565 | -52.7664 | -15.7837 | 67.6666 | -54.4693 | 67.7673 | -46.4493 | -52.7344 | -52.7847 | -0.12817 | -0.036621 | -0.036621 | 9.256 | 1.6708 | 1.8723 | 1.799 | 2.0004 | -0.032043 | -0.064087 | 0.036621 | 7.988 | 1.6525 | 1.7029 | 1.6846 | 1.7349 | 9.3842 | 122.2595 | 8.02 | 122.2366 | 122.2595 | 122.1359 | 122.1313 | 122.1039 | -122.2961 | -122.2 | 122.1313 | 122.2046 | 40.9653 | 38.6536
1597.3125 | 122.5113 | -54.5242 | 67.6712 | -0.13451 | 0.028897 | 0.07897 | 0.071771 | -0.0017944 | 0.0083612 | 0.011668 | -0.07019 | 0.023208 | 0.07442 | 0.078442 | -0.010177 | 0.02076 | 0.0082266 | -13.4354 | 67.5888 | -54.6341 | 67.6392 | -45.2499 | -52.5284 | -52.7847 | -15.77 | 67.5568 | -54.5471 | 67.7628 | -46.4355 | -52.7985 | -52.8122 | -0.10986 | -0.082398 | -0.032044 | 9.2743 | 1.7395 | 1.9958 | 1.8494 | 2.1057 | -0.022888 | -0.11444 | 0.091552 | 8.0887 | 1.712 | 1.7258 | 1.7349 | 1.7487 | 9.3842 | 122.2733 | 8.1116 | 122.3099 | 122.2229 | 122.1039 | 122.113 | 122.081 | -122.3053 | -122.2183 | 122.1634 | 122.287 | 41.0889 | 38.7543
1598.3125 | 122.4884 | -54.6249 | 67.511 | -0.08873 | 0.028042 | 0.076193 | 0.073266 | 0.00098262 | 0.011138 | 0.012523 | -0.057983 | 0.022781 | 0.074847 | 0.068616 | -0.0093226 | 0.022042 | 0.0069448 | -13.5544 | 67.4881 | -54.776 | 67.5385 | -45.282 | -52.7298 | -52.9221 | -15.9164 | 67.4606 | -54.6753 | 67.6117 | -46.5591 | -52.9449 | -52.9633 | -0.15106 | -0.022888 | 0.027466 | 9.343 | 1.7029 | 1.8951 | 1.8539 | 2.0462 | -0.050354 | -0.050354 | 0.10071 | 8.0658 | 1.6617 | 1.68 | 1.712 | 1.7303 | 9.494 | 122.3145 | 8.1162 | 122.287 | 122.2641 | 122.1359 | 122.113 | 122.0856 | -122.287 | -122.1863 | 122.1634 | 122.2366 | 41.0706 | 38.7085
1599.3125 | 122.4747 | -54.7073 | 67.5018 | 0.079117 | 0.028683 | 0.077047 | 0.073053 | -0.0024354 | 0.011352 | 0.010173 | -0.021362 | 0.022994 | 0.075061 | 0.063489 | -0.0076136 | 0.022469 | 0.0073722 | -13.7833 | 67.4423 | -54.8218 | 67.4286 | -45.3964 | -52.7985 | -52.977 | -16.0263 | 67.424 | -54.7165 | 67.5339 | -46.5912 | -52.9678 | -52.9907 | -0.11444 | -0.059509 | -0.073242 | 9.3109 | 1.7303 | 1.9089 | 1.8448 | 2.0233 | -0.009156 | -0.07782 | 0.032044 | 8.1161 | 1.7166 | 1.7395 | 1.7258 | 1.7487 | 9.4254 | 122.2504 | 8.1253 | 122.2504 | 122.2641 | 122.1405 | 122.1497 | 122.1313 | -122.3236 | -122.2183 | 122.1359 | 122.2412 | 40.9241 | 38.681
1600.3125 | 122.4564 | -54.6844 | 67.5018 | -0.12688 | 0.02911 | 0.07662 | 0.073907 | -0.00072638 | 0.010711 | 0.0106 | -0.045776 | 0.022567 | 0.073993 | 0.074597 | -0.009109 | 0.022042 | 0.0071586 | -13.5361 | 67.4515 | -54.7852 | 67.511 | -45.2316 | -52.7435 | -52.9541 | -15.8981 | 67.4149 | -54.7073 | 67.5705 | -46.5317 | -52.9495 | -52.9724 | -0.10071 | -0.050354 | 0.009155 | 9.4528 | 1.7303 | 1.9409 | 1.8311 | 2.0416 | -0.022888 | -0.086975 | 0.068665 | 8.1528 | 1.712 | 1.7349 | 1.7349 | 1.7578 | 9.5535 | 122.2961 | 8.1757 | 122.2778 | 122.2366 | 122.1222 | 122.1359 | 122.0993 | -122.287 | -122.2092 | 122.1954 | 122.2549 | 41.1484 | 38.7863
1601.3125 | 122.4792 | -54.6661 | 67.5064 | -0.14214 | 0.028042 | 0.078543 | 0.072198 | 0.0016236 | 0.0068658 | 0.0088909 | -0.042725 | 0.023208 | 0.07677 | 0.070966 | -0.0074 | 0.021828 | 0.0095084 | -13.5361 | 67.4469 | -54.7577 | 67.5247 | -45.2133 | -52.7069 | -52.9358 | -15.9027 | 67.4286 | -54.6753 | 67.6071 | -46.4859 | -52.9266 | -52.9312 | -0.091552 | -0.05951 | 0.01831 | 9.4528 | 1.7303 | 1.9592 | 1.8219 | 2.0508 | -0.009155 | -0.07782 | 0.10071 | 8.1802 | 1.7349 | 1.7395 | 1.7441 | 1.7487 | 9.5444 | 122.2824 | 8.1894 | 122.2824 | 122.2046 | 122.1039 | 122.113 | 122.0947 | -122.2641 | -122.1817 | 122.1909 | 122.2733 | 41.1301 | 38.7634
1602.3125 | 122.4655 | -54.5563 | 67.6254 | -0.14214 | 0.028897 | 0.07662 | 0.073053 | 0.0014098 | 0.010497 | 0.0095319 | -0.039673 | 0.024917 | 0.075488 | 0.06712 | -0.0080408 | 0.023537 | 0.0069448 | -13.4537 | 67.5934 | -54.6661 | 67.6117 | -45.1309 | -52.6428 | -52.8397 | -15.8844 | 67.5751 | -54.5929 | 67.6804 | -46.3577 | -52.8305 | -52.8397 | -0.10986 | -0.032043 | -0.013733 | 9.4254 | 1.7166 | 1.9135 | 1.8265 | 2.0233 | -0.036622 | -0.050354 | 0.054932 | 8.1985 | 1.7166 | 1.7258 | 1.7532 | 1.7624 | 9.5352 | 122.2778 | 8.2352 | 122.2733 | 122.2595 | 122.168 | 122.1497 | 122.1313 | -122.2916 | -122.2183 | 122.168 | 122.2366 | 41.1026 | 38.6719
1603.3125 | 122.4518 | -54.5883 | 67.6163 | -0.13451 | 0.029538 | 0.075766 | 0.069848 | -0.0045716 | 0.013702 | 0.0084637 | -0.0030517 | 0.023422 | 0.07677 | 0.068829 | -0.0076136 | 0.021828 | 0.010363 | -13.4583 | 67.5476 | -54.7211 | 67.5064 | -45.1584 | -52.684 | -52.9129 | -15.9714 | 67.5339 | -54.6204 | 67.6254 | -46.3943 | -52.858 | -52.8717 | -0.13275 | -0.068665 | -0.10986 | 9.4299 | 1.6754 | 1.9043 | 1.8082 | 2.037 | -0.032043 | -0.082397 | 0.009155 | 8.194 | 1.7166 | 1.7303 | 1.7487 | 1.7624 | 9.5627 | 122.2275 | 8.226 | 122.2458 | 122.2687 | 122.1542 | 122.1359 | 122.1222 | -122.3373 | -122.2366 | 122.0947 | 122.2137 | 41.1301 | 38.6169
1604.3125 | 122.5067 | -54.538 | 67.6895 | 0.018082 | 0.030392 | 0.079825 | 0.071985 | 0.0031188 | 0.009643 | 0.0097455 | -0.024414 | 0.023635 | 0.075915 | 0.063702 | -0.0086816 | 0.022683 | 0.0082266 | -13.5223 | 67.6025 | -54.6753 | 67.6941 | -45.0073 | -52.4918 | -52.739 | -15.7745 | 67.6163 | -54.5288 | 67.749 | -46.2341 | -52.7023 | -52.7618 | -0.13733 | -0.086975 | 0.004578 | 9.5306 | 1.799 | 2.0462 | 1.9363 | 2.1835 | 0.009155 | -0.073242 | 0.059509 | 8.3038 | 1.7761 | 1.8356 | 1.767 | 1.8265 | 9.668 | 122.3694 | 8.2947 | 122.2778 | 122.2778 | 122.1451 | 122.1405 | 122.1542 | -122.3648 | -122.2183 | 122.2321 | 122.287 | 41.0156 | 38.7634
1605.3125 | 122.493 | -54.5746 | 67.6209 | -0.096359 | 0.02847 | 0.078543 | 0.073907 | 0.0026916 | 0.011138 | 0.0093181 | -0.07019 | 0.02449 | 0.075061 | 0.068402 | -0.0082544 | 0.024392 | 0.0088676 | -13.3347 | 67.5522 | -54.6799 | 67.6254 | -45.0256 | -52.6062 | -52.8305 | -15.8203 | 67.5247 | -54.6112 | 67.6895 | -46.2708 | -52.7847 | -52.8168 | -0.10529 | -0.068665 | 0.004577 | 9.5489 | 1.7441 | 1.9684 | 1.8494 | 2.0737 | -0.036621 | -0.096131 | 0.068664 | 8.3038 | 1.7578 | 1.7899 | 1.7944 | 1.8265 | 9.6542 | 122.3053 | 8.3405 | 122.3007 | 122.2321 | 122.1359 | 122.1268 | 122.0993 | -122.3007 | -122.2321 | 122.2 | 122.2641 | 41.2399 | 38.7543
1606.3125 | 122.4701 | -54.4968 | 67.6895 | -0.16502 | 0.026761 | 0.078116 | 0.072839 | -0.0047852 | 0.011352 | 0.0080365 | -0.036621 | 0.023635 | 0.077197 | 0.070966 | -0.0097498 | 0.02311 | 0.0090812 | -13.3072 | 67.6712 | -54.6112 | 67.5705 | -45.1035 | -52.5284 | -52.7618 | -15.8386 | 67.6209 | -54.5425 | 67.7261 | -46.2204 | -52.739 | -52.7664 | -0.11444 | -0.01831 | -0.11902 | 9.3933 | 1.7349 | 1.9684 | 1.8494 | 2.0828 | -0.045777 | -0.068664 | 0.036621 | 8.2764 | 1.7303 | 1.7578 | 1.7761 | 1.8036 | 9.5078 | 122.1817 | 8.3221 | 122.2687 | 122.2824 | 122.1634 | 122.168 | 122.1176 | -122.3007 | -122.2321 | 122.0673 | 122.2229 | 41.1896 | 38.6581
1607.3125 | 122.4838 | -54.4601 | 67.7399 | -0.14214 | 0.02911 | 0.078116 | 0.070276 | -0.0062806 | 0.0087884 | 0.010173 | -0.064087 | 0.025131 | 0.078479 | 0.072461 | -0.0082544 | 0.021828 | 0.008013 | -13.1927 | 67.6575 | -54.6066 | 67.6895 | -44.902 | -52.5192 | -52.7252 | -15.7654 | 67.6437 | -54.4876 | 67.749 | -46.1609 | -52.7206 | -52.7664 | -0.14648 | -0.082397 | -0.050354 | 9.5581 | 1.7349 | 1.9409 | 1.8814 | 2.0874 | -0.027466 | -0.09613 | 0.009155 | 8.2993 | 1.6937 | 1.7395 | 1.7212 | 1.767 | 9.7046 | 122.2961 | 8.3267 | 122.2366 | 122.2641 | 122.1313 | 122.1176 | 122.1039 | -122.3465 | -122.2275 | 122.1497 | 122.2092 | 41.2674 | 38.6948
1608.3125 | 122.4747 | -54.4418 | 67.7399 | -0.11162 | 0.028256 | 0.077047 | 0.071557 | -0.0028626 | 0.0066522 | 0.011241 | -0.039673 | 0.022781 | 0.075915 | 0.073102 | -0.0097498 | 0.023323 | 0.010363 | -13.1744 | 67.6941 | -54.5746 | 67.7353 | -45.0806 | -52.5421 | -52.7023 | -15.7974 | 67.6437 | -54.5105 | 67.7719 | -46.1243 | -52.6978 | -52.7252 | -0.13275 | -0.045776 | -0.004577 | 9.3613 | 1.7395 | 1.8997 | 1.8723 | 2.0325 | -0.068665 | -0.09613 | 0.032044 | 8.3176 | 1.7166 | 1.7441 | 1.7853 | 1.8127 | 9.494 | 122.3099 | 8.3862 | 122.2824 | 122.2687 | 122.1542 | 122.1359 | 122.0856 | -122.3145 | -122.2504 | 122.1771 | 122.2137 | 41.2674 | 38.6444
1609.3125 | 122.3145 | -54.4281 | 67.8223 | -0.08873 | 0.027829 | 0.075979 | 0.072839 | -0.00051278 | 0.0083612 | 0.012095 | -0.085449 | 0.025131 | 0.075915 | 0.073102 | -0.0095362 | 0.021614 | 0.0048086 | -13.1744 | 67.7582 | -54.5563 | 67.6804 | -44.8975 | -52.4597 | -52.7115 | -15.8569 | 67.7444 | -54.451 | 67.7444 | -46.1517 | -52.4689 | -52.5833 | -0.12817 | -0.064087 | -0.14191 | 9.5306 | 1.7166 | 1.9684 | 1.8448 | 2.0966 | -0.022888 | -0.07782 | -0.07782 | 8.2764 | 1.8448 | 1.9592 | 1.8677 | 1.9821 | 9.6588 | 122.2366 | 8.2993 | 122.1954 | 122.3145 | 122.1954 | 122.1863 | 122.1725 | -122.3785 | -122.2733 | 122.1085 | 122.1725 | 41.2537 | 38.5712
1610.3125 | 122.4747 | -54.3823 | 67.8452 | -0.11925 | 0.028897 | 0.074698 | 0.070703 | -0.0017944 | 0.01242 | 0.012523 | -0.033569 | 0.024703 | 0.075915 | 0.073102 | -0.0071864 | 0.021828 | 0.0058768 | -13.092 | 67.7994 | -54.483 | 67.6987 | -44.7968 | -52.3819 | -52.6337 | -15.7562 | 67.7673 | -54.3961 | 67.8589 | -45.9732 | -52.5696 | -52.5925 | -0.10071 | -0.045777 | -0.14648 | 9.5856 | 1.7487 | 2.0004 | 1.8494 | 2.1011 | -0.013733 | -0.07782 | 0.013733 | 8.4091 | 1.7899 | 1.8127 | 1.8036 | 1.8265 | 9.6863 | 122.1817 | 8.4229 | 122.2549 | 122.2824 | 122.1634 | 122.1817 | 122.1497 | -122.3282 | -122.2412 | 122.081 | 122.2412 | 41.2903 | 38.6261
1611.3125 | 122.4747 | -54.3457 | 67.8452 | -0.10399 | 0.027829 | 0.076834 | 0.071985 | -0.0017944 | 0.01242 | 0.011027 | -0.024414 | 0.025558 | 0.075915 | 0.071179 | -0.0080408 | 0.021828 | 0.0075858 | -13.0737 | 67.7948 | -54.483 | 67.7444 | -44.696 | -52.3956 | -52.6428 | -15.8157 | 67.7765 | -54.3777 | 67.8589 | -45.9549 | -52.5696 | -52.5833 | -0.13733 | -0.050354 | -0.10071 | 9.6497 | 1.7029 | 1.9501 | 1.8402 | 2.0874 | -0.032044 | -0.068665 | 0.013733 | 8.3908 | 1.7624 | 1.7761 | 1.7944 | 1.8082 | 9.787 | 122.2275 | 8.4229 | 122.2366 | 122.2778 | 122.1542 | 122.1405 | 122.1222 | -122.3282 | -122.2229 | 122.0901 | 122.2046 | 41.272 | 38.53
1612.3125 | 122.4564 | -54.245 | 67.9642 | -0.12688 | 0.02911 | 0.077688 | 0.073694 | 0.004187 | 0.011138 | 0.012523 | -0.033569 | 0.024063 | 0.075488 | 0.069897 | -0.008468 | 0.019692 | 0.009722 | -13.0096 | 67.8955 | -54.364 | 67.9047 | -44.6228 | -52.2766 | -52.4689 | -15.6738 | 67.8726 | -54.2816 | 67.9779 | -45.8176 | -52.4414 | -52.4734 | -0.11902 | -0.068664 | -0.059509 | 9.6222 | 1.7761 | 1.9684 | 1.8951 | 2.0874 | -0.036621 | -0.091552 | 0.013733 | 8.4274 | 1.7715 | 1.8036 | 1.8082 | 1.8402 | 9.7412 | 122.2687 | 8.4641 | 122.2595 | 122.2595 | 122.1542 | 122.1405 | 122.1176 | -122.3282 | -122.2458 | 122.1497 | 122.2229 | 41.2354 | 38.5712
1613.3125 | 122.5204 | -54.2175 | 68.0008 | -0.10399 | 0.029324 | 0.077047 | 0.07348 | -8.538e-05 | 0.01007 | 0.0093181 | -0.0030517 | 0.02449 | 0.077197 | 0.067761 | -0.0082544 | 0.022683 | 0.008013 | -12.9776 | 67.923 | -54.3732 | 67.9504 | -44.545 | -52.1988 | -52.4414 | -15.6326 | 67.9001 | -54.2542 | 68.0374 | -45.7169 | -52.359 | -52.4048 | -0.15564 | -0.077819 | -0.050354 | 9.6725 | 1.7761 | 2.0187 | 1.9318 | 2.1744 | -0.036621 | -0.10071 | 0.036622 | 8.5007 | 1.8127 | 1.8585 | 1.8494 | 1.8951 | 9.8282 | 122.3236 | 8.5373 | 122.2916 | 122.2961 | 122.1542 | 122.1405 | 122.1176 | -122.374 | -122.2549 | 122.168 | 122.2549 | 41.2399 | 38.5849
1614.3125 | 122.5067 | -54.3228 | 67.8818 | -0.073471 | 0.030179 | 0.076193 | 0.072412 | -0.0017944 | 0.0094292 | 0.011241 | -0.036621 | 0.02449 | 0.076129 | 0.068616 | -0.009109 | 0.023323 | 0.011004 | -13.0875 | 67.8314 | -54.4556 | 67.836 | -44.6045 | -52.3041 | -52.5375 | -15.7608 | 67.7856 | -54.3365 | 67.955 | -45.7993 | -52.4643 | -52.5055 | -0.13275 | -0.050354 | -0.045776 | 9.7183 | 1.7853 | 2.0187 | 1.918 | 2.1515 | -0.013733 | -0.09613 | 0.073242 | 8.5236 | 1.8173 | 1.8585 | 1.8311 | 1.8723 | 9.8511 | 122.2916 | 8.5373 | 122.2916 | 122.287 | 122.1222 | 122.1542 | 122.1085 | -122.3373 | -122.2183 | 122.1588 | 122.2778 | 41.2354 | 38.562
1615.3125 | 122.493 | -54.3228 | 67.8909 | -0.11925 | 0.028256 | 0.077475 | 0.072412 | -0.00093998 | 0.01007 | 0.011882 | -0.0091553 | 0.023849 | 0.076983 | 0.068616 | -0.0086816 | 0.023323 | 0.012713 | -13.028 | 67.8314 | -54.4144 | 67.8589 | -44.5541 | -52.272 | -52.5055 | -15.7471 | 67.8177 | -54.3182 | 67.9596 | -45.7489 | -52.446 | -52.4826 | -0.091553 | -0.059509 | -0.032043 | 9.7687 | 1.8173 | 2.0508 | 1.9089 | 2.1423 | 0.004578 | -0.073242 | 0.068665 | 8.5739 | 1.8402 | 1.8768 | 1.8356 | 1.8723 | 9.8602 | 122.2733 | 8.5693 | 122.2778 | 122.2458 | 122.1359 | 122.1542 | 122.1405 | -122.3053 | -122.2092 | 122.1817 | 122.2824 | 41.2949 | 38.5757
1616.3125 | 122.5067 | -54.2404 | 67.9504 | -0.11925 | 0.02911 | 0.077688 | 0.072839 | -0.00072638 | 0.01007 | 0.0080365 | -0.012207 | 0.025131 | 0.076983 | 0.067975 | -0.0074 | 0.021187 | 0.0082266 | -12.9547 | 67.9001 | -54.3686 | 67.9276 | -44.4855 | -52.2125 | -52.4414 | -15.6967 | 67.8589 | -54.2404 | 68.0145 | -45.6711 | -52.3499 | -52.4094 | -0.12817 | -0.050354 | -0.022888 | 9.7549 | 1.799 | 2.0279 | 1.9272 | 2.1561 | 0 | -0.091552 | 0.064087 | 8.5693 | 1.8311 | 1.8906 | 1.8311 | 1.8906 | 9.8831 | 122.2961 | 8.5693 | 122.2549 | 122.2687 | 122.0993 | 122.1405 | 122.0993 | -122.319 | -122.1909 | 122.168 | 122.2549 | 41.2857 | 38.5437
1617.3125 | 122.5342 | -54.2404 | 67.9642 | -0.081101 | 0.031247 | 0.078756 | 0.072198 | 0.0046142 | 0.011138 | 0.0093181 | -0.024414 | 0.025985 | 0.075488 | 0.064557 | -0.0086816 | 0.023323 | 0.0082266 | -12.973 | 67.8909 | -54.3594 | 67.9184 | -44.4763 | -52.2079 | -52.4323 | -15.715 | 67.8452 | -54.2542 | 68.0145 | -45.6207 | -52.3407 | -52.4094 | -0.11902 | -0.073242 | -0.045776 | 9.7641 | 1.8082 | 2.0325 | 1.9272 | 2.1515 | -0.013733 | -0.11902 | 0.050354 | 8.6197 | 1.8311 | 1.8997 | 1.8448 | 1.9135 | 9.8831 | 122.2778 | 8.6334 | 122.2687 | 122.2504 | 122.0993 | 122.1313 | 122.0856 | -122.3236 | -122.2183 | 122.1588 | 122.2549 | 41.2674 | 38.5254
1618.3125 | 122.5067 | -54.1306 | 68.0603 | -0.14977 | 0.02911 | 0.077902 | 0.073053 | 0.0044006 | 0.01242 | 0.013804 | -0.015259 | 0.02449 | 0.077197 | 0.06712 | -0.0095362 | 0.022896 | 0.011217 | -12.8677 | 68.0054 | -54.2725 | 68.0466 | -44.3527 | -52.0798 | -52.3224 | -15.5869 | 67.9688 | -54.1626 | 68.1473 | -45.4926 | -52.2308 | -52.272 | -0.14191 | -0.054932 | -0.013733 | 9.7778 | 1.8082 | 2.0508 | 1.9501 | 2.1927 | -0.032044 | -0.091553 | 0.086975 | 8.638 | 1.8585 | 1.8997 | 1.8906 | 1.9318 | 9.9197 | 122.319 | 8.67 | 122.3099 | 122.2778 | 122.1313 | 122.1359 | 122.0993 | -122.3328 | -122.2229 | 122.1771 | 122.2778 | 41.2628 | 38.5437
1619.3125 | 122.3877 | -54.126 | 68.1244 | -0.050583 | 0.030179 | 0.078116 | 0.073907 | -0.00072638 | 0.0077202 | 0.0095319 | -0.088501 | 0.026199 | 0.077197 | 0.077801 | -0.011032 | 0.023537 | 0.010363 | -12.8586 | 68.0832 | -54.2862 | 68.0786 | -44.5633 | -52.3224 | -52.3819 | -15.7516 | 68.0786 | -54.1718 | 68.0603 | -45.575 | -52.3087 | -52.3727 | -0.16022 | -0.041199 | -0.045777 | 9.5627 | 1.7441 | 1.8036 | 1.9043 | 1.9638 | -0.045776 | -0.045777 | -0.064087 | 8.551 | 1.7532 | 1.8173 | 1.799 | 1.8631 | 9.7229 | 122.3648 | 8.5968 | 122.2321 | 122.3694 | 122.2504 | 122.2092 | 122.2046 | -122.4106 | -122.2961 | 122.2046 | 122.1863 | 41.2674 | 38.3743
1620.3125 | 122.5479 | -54.1168 | 68.042 | -0.13451 | 0.029324 | 0.078756 | 0.07113 | 0.00098262 | 0.009002 | 0.011241 | -0.01831 | 0.025558 | 0.075274 | 0.076947 | -0.0071864 | 0.022896 | 0.0060904 | -12.8357 | 67.9733 | -54.2679 | 68.0328 | -44.3161 | -52.0798 | -52.3178 | -15.6509 | 67.9596 | -54.158 | 68.1427 | -45.4285 | -52.2171 | -52.2766 | -0.15106 | -0.068664 | -0.009155 | 9.8007 | 1.799 | 2.037 | 1.9501 | 2.1881 | -0.041199 | -0.082397 | 0.10071 | 8.6884 | 1.8402 | 1.8997 | 1.8814 | 1.9409 | 9.9518 | 122.3007 | 8.7296 | 122.3007 | 122.2412 | 122.1176 | 122.0901 | 122.0764 | -122.3099 | -122.2 | 122.1497 | 122.2595 | 41.2811 | 38.4659
1621.3125 | 122.5296 | -54.0985 | 68.0923 | -0.081101 | 0.029324 | 0.077688 | 0.071985 | 0.00076902 | 0.004516 | 0.0078229 | 0.012207 | 0.02684 | 0.077197 | 0.066907 | -0.0088952 | 0.023323 | 0.0075858 | -12.7487 | 68.0603 | -54.2175 | 68.367 | -44.2886 | -52.4048 | -52.3315 | -15.6235 | 67.9916 | -54.0985 | 68.1839 | -45.3552 | -52.1347 | -52.2217 | -0.11902 | -0.032043 | 0.27466 | 9.8099 | 1.767 | 1.6937 | 1.886 | 1.8127 | 0 | -0.10071 | 0.091553 | 8.7433 | 1.8768 | 1.9638 | 1.8768 | 1.9638 | 9.9289 | 122.5845 | 8.7433 | 122.2824 | 122.2778 | 122.0901 | 122.1588 | 122.0901 | -122.3099 | -122.1909 | 122.4655 | 122.2824 | 41.3498 | 38.475
1622.3125 | 122.5159 | -54.0253 | 68.1656 | -0.065842 | 0.029538 | 0.078329 | 0.073266 | -0.0024354 | 0.011566 | 0.0084637 | -0.027466 | 0.025772 | 0.076556 | 0.071179 | -0.0076136 | 0.022469 | 0.0086538 | -12.7396 | 68.1107 | -54.1443 | 68.1747 | -44.1193 | -51.9424 | -52.1896 | -15.4861 | 68.074 | -54.039 | 68.248 | -45.2591 | -52.0706 | -52.1301 | -0.11902 | -0.054931 | 0.009156 | 9.906 | 1.8356 | 2.0828 | 1.9547 | 2.2018 | -0.013732 | -0.091552 | 0.082398 | 8.7662 | 1.8951 | 1.9547 | 1.9089 | 1.9684 | 10.025 | 122.319 | 8.7799 | 122.287 | 122.2549 | 122.113 | 122.1359 | 122.0993 | -122.3099 | -122.2046 | 122.2 | 122.2733 | 41.2857 | 38.5391
1623.3125 | 122.4609 | -54.0115 | 68.2205 | -0.10399 | 0.029965 | 0.077047 | 0.073907 | 0.002478 | 0.010925 | 0.010386 | -0.05188 | 0.026199 | 0.07677 | 0.063916 | -0.010391 | 0.023323 | 0.0088676 | -12.7075 | 68.129 | -54.126 | 68.1885 | -44.0826 | -51.9196 | -52.1851 | -15.5457 | 68.129 | -54.0344 | 68.2205 | -45.2866 | -52.1118 | -52.153 | -0.11444 | -0.091553 | -0.032043 | 9.9289 | 1.8265 | 2.092 | 1.9409 | 2.2064 | -0.022888 | -0.091553 | 0 | 8.725 | 1.8585 | 1.8997 | 1.8814 | 1.9226 | 10.0433 | 122.3145 | 8.7479 | 122.2549 | 122.2549 | 122.1634 | 122.1405 | 122.1405 | -122.3465 | -122.2549 | 122.2 | 122.2321 | 41.304 | 38.4659
1624.3125 | 122.4518 | -54.0482 | 68.1473 | -0.12688 | 0.029751 | 0.077047 | 0.072839 | -0.00051278 | 0.009643 | 0.011027 | -0.064087 | 0.028121 | 0.075915 | 0.074811 | -0.009109 | 0.022042 | 0.0077994 | -12.7441 | 68.1107 | -54.158 | 68.1473 | -44.1559 | -51.9516 | -52.2217 | -15.5914 | 68.0832 | -54.0665 | 68.1564 | -45.3049 | -52.121 | -52.1942 | -0.10986 | -0.036621 | 0 | 9.8923 | 1.8265 | 2.0966 | 1.9363 | 2.2064 | -0.01831 | -0.064087 | 0.009155 | 8.7433 | 1.8539 | 1.9272 | 1.8723 | 1.9455 | 10.0021 | 122.3053 | 8.7616 | 122.2229 | 122.2687 | 122.1497 | 122.1588 | 122.1313 | -122.3053 | -122.2137 | 122.1954 | 122.2046 | 41.304 | 38.4567
1625.3125 | 122.4884 | -53.9795 | 68.1885 | -0.020065 | 0.028897 | 0.078543 | 0.071985 | -0.0013672 | 0.01242 | 0.0097455 | -0.036621 | 0.025558 | 0.078906 | 0.068829 | -0.008468 | 0.024178 | 0.009722 | -12.7716 | 68.1198 | -54.1077 | 68.2434 | -44.0231 | -51.8646 | -52.1439 | -15.4678 | 68.1335 | -54.0115 | 68.2846 | -45.1538 | -52.0294 | -52.0981 | -0.12817 | -0.068665 | 0.054931 | 9.9564 | 1.8356 | 2.1149 | 1.9638 | 2.243 | -0.032044 | -0.054932 | 0.09613 | 8.8257 | 1.8814 | 1.9501 | 1.9135 | 1.9821 | 10.0845 | 122.3511 | 8.8577 | 122.2961 | 122.2275 | 122.1451 | 122.0993 | 122.113 | -122.2961 | -122.2 | 122.2229 | 122.2641 | 41.2079 | 38.5117
1626.3125 | 122.5021 | -53.9841 | 68.2434 | -0.11925 | 0.030179 | 0.078543 | 0.071344 | 0.00076902 | 0.011352 | 0.0091045 | -0.021362 | 0.024703 | 0.077838 | 0.065839 | -0.0071864 | 0.023323 | 0.008013 | -12.6892 | 68.1747 | -54.0985 | 68.2571 | -43.9819 | -51.8509 | -52.121 | -15.4495 | 68.1656 | -53.9566 | 68.2983 | -45.1355 | -51.9882 | -52.066 | -0.11444 | -0.068664 | 0.013733 | 10.0021 | 1.8631 | 2.1332 | 1.9775 | 2.2476 | 0.027466 | -0.07782 | 0.054932 | 8.8486 | 1.918 | 1.9959 | 1.8906 | 1.9684 | 10.1166 | 122.3557 | 8.8211 | 122.2549 | 122.2733 | 122.1222 | 122.1588 | 122.1497 | -122.3419 | -122.2 | 122.2412 | 122.2824 | 41.2949 | 38.5345
1627.3125 | 122.493 | -53.9246 | 68.2892 | -0.08873 | 0.029965 | 0.077688 | 0.072839 | -0.002008 | 0.010925 | 0.012523 | -0.030517 | 0.027267 | 0.076983 | 0.06712 | -0.0088952 | 0.023537 | 0.011004 | -12.6389 | 68.2159 | -54.0344 | 68.2892 | -43.9453 | -51.7868 | -52.0569 | -15.4083 | 68.2022 | -53.952 | 68.335 | -45.0577 | -51.947 | -52.0203 | -0.10986 | -0.073243 | 0 | 9.9792 | 1.8677 | 2.1378 | 1.9775 | 2.2476 | -0.027465 | -0.086976 | 0.045776 | 8.8669 | 1.9043 | 1.9775 | 1.9318 | 2.005 | 10.0891 | 122.3236 | 8.8943 | 122.287 | 122.2504 | 122.1542 | 122.1405 | 122.1268 | -122.3236 | -122.2412 | 122.2137 | 122.2595 | 41.2857 | 38.5162
1628.3125 | 122.4106 | -53.9108 | 68.335 | -0.042954 | 0.029538 | 0.077475 | 0.072626 | -0.0022218 | 0.011352 | 0.011668 | -0.05188 | 0.02684 | 0.078479 | 0.077161 | -0.0095362 | 0.023964 | 0.0099356 | -12.6755 | 68.2343 | -54.0298 | 68.2526 | -43.9774 | -51.8417 | -52.1072 | -15.509 | 68.2297 | -53.9337 | 68.2526 | -45.1355 | -51.9882 | -52.0706 | -0.11902 | -0.10071 | -0.082398 | 9.9335 | 1.8036 | 2.0691 | 1.9226 | 2.1881 | -0.022888 | -0.10529 | -0.082398 | 8.7753 | 1.8402 | 1.9226 | 1.8631 | 1.9455 | 10.0525 | 122.2824 | 8.7982 | 122.1863 | 122.2641 | 122.1634 | 122.1451 | 122.1405 | -122.3648 | -122.2687 | 122.1634 | 122.1634 | 41.2354 | 38.4018
1629.3125 | 122.4335 | -53.9291 | 68.3075 | -0.17265 | 0.030179 | 0.075766 | 0.077112 | 0.0026916 | 0.009643 | 0.012095 | -0.12512 | 0.02684 | 0.076342 | 0.070325 | -0.0099634 | 0.024392 | 0.0086538 | -12.5519 | 68.2709 | -54.0573 | 68.248 | -43.9911 | -51.8738 | -52.1484 | -15.509 | 68.2343 | -53.9154 | 68.3029 | -45.0897 | -52.0294 | -52.0798 | -0.12817 | -0.036621 | -0.059509 | 9.938 | 1.7807 | 2.0554 | 1.9089 | 2.1835 | 0.013733 | -0.073242 | -0.004578 | 8.8394 | 1.8494 | 1.8997 | 1.8356 | 1.886 | 10.0662 | 122.3053 | 8.8257 | 122.2183 | 122.3282 | 122.1497 | 122.2 | 122.1634 | -122.3648 | -122.2229 | 122.1771 | 122.2321 | 41.3773 | 38.4201
1630.3125 | 122.438 | -53.8513 | 68.3533 | -0.081101 | 0.03146 | 0.080038 | 0.071771 | 0.0026916 | 0.011138 | 0.011668 | -0.01831 | 0.025985 | 0.077411 | 0.075238 | -0.0059046 | 0.023964 | 0.0095084 | -12.5656 | 68.2892 | -53.9795 | 68.3395 | -43.8492 | -51.7364 | -52.0065 | -15.4633 | 68.2755 | -53.8925 | 68.399 | -44.9524 | -51.8692 | -51.9516 | -0.12817 | -0.064086 | -0.013732 | 10.0021 | 1.8448 | 2.1149 | 1.973 | 2.243 | -0.041199 | -0.077819 | 0.045777 | 8.8989 | 1.8997 | 1.9821 | 1.9409 | 2.0233 | 10.1303 | 122.319 | 8.9401 | 122.2916 | 122.2687 | 122.168 | 122.1405 | 122.1268 | -122.3328 | -122.2458 | 122.1909 | 122.2504 | 41.2857 | 38.3881
1631.3125 | 122.3969 | -53.8925 | 68.3533 | -0.17265 | 0.029965 | 0.07662 | 0.073694 | -8.538e-05 | 0.011779 | 0.0097455 | -0.067139 | 0.025772 | 0.079547 | 0.07652 | -0.0065454 | 0.023751 | 0.010363 | -12.6663 | 68.3304 | -54.0115 | 68.2297 | -43.9728 | -51.8143 | -52.1164 | -15.564 | 68.3212 | -53.9017 | 68.3075 | -45.0165 | -51.9836 | -52.0386 | -0.11902 | -0.022888 | -0.1236 | 9.9197 | 1.7761 | 2.0782 | 1.8951 | 2.1973 | -0.009155 | -0.032043 | -0.045776 | 8.876 | 1.8539 | 1.9089 | 1.8631 | 1.918 | 10.0388 | 122.2412 | 8.8852 | 122.2092 | 122.3419 | 122.2229 | 122.2229 | 122.2137 | -122.3648 | -122.2549 | 122.1222 | 122.2 | 41.2262 | 38.3286
1632.3125 | 122.4518 | -53.7781 | 68.3945 | -0.042954 | 0.028897 | 0.07897 | 0.070062 | 0.00055542 | 0.0094292 | 0.0088909 | 0.018311 | 0.027481 | 0.078265 | 0.065411 | -0.0059046 | 0.021401 | 0.010149 | -12.5931 | 68.3441 | -53.9291 | 68.3716 | -43.8126 | -51.6769 | -51.9699 | -15.4037 | 68.3258 | -53.833 | 68.399 | -44.8471 | -51.8372 | -51.915 | -0.15106 | -0.050354 | -0.022888 | 9.9655 | 1.8082 | 2.1011 | 1.9592 | 2.2522 | -0.054932 | -0.068664 | 0.004578 | 8.931 | 1.8631 | 1.9409 | 1.918 | 1.9958 | 10.1166 | 122.3007 | 8.9859 | 122.2321 | 122.2733 | 122.1588 | 122.1222 | 122.1039 | -122.3236 | -122.2275 | 122.1497 | 122.1771 | 41.185 | 38.3743
1633.3125 | 122.3785 | -53.7231 | 68.5226 | -0.10399 | 0.030392 | 0.077475 | 0.074334 | 0.0014098 | 0.011138 | 0.011882 | -0.057983 | 0.030258 | 0.076556 | 0.064343 | -0.0093226 | 0.023537 | 0.013567 | -12.5565 | 68.4677 | -53.8284 | 68.3853 | -43.7988 | -51.6861 | -51.9562 | -15.4266 | 68.4586 | -53.7643 | 68.3899 | -44.9249 | -51.7273 | -51.8188 | -0.10528 | -0.054932 | -0.13733 | 9.9243 | 1.767 | 2.037 | 1.8723 | 2.1423 | -0.041198 | -0.064087 | -0.13275 | 8.7982 | 1.9043 | 1.9959 | 1.9455 | 2.037 | 10.0296 | 122.2137 | 8.8394 | 122.1542 | 122.2961 | 122.2229 | 122.1909 | 122.1817 | -122.3511 | -122.287 | 122.1085 | 122.113 | 41.1667 | 38.2965
1634.3125 | 122.4197 | -53.8284 | 68.4357 | -0.050583 | 0.030819 | 0.077047 | 0.073053 | -0.003717 | 0.011352 | 0.011027 | -0.061035 | 0.027694 | 0.080829 | 0.075238 | -0.006759 | 0.024819 | 0.0082266 | -12.7029 | 68.3899 | -53.952 | 68.2617 | -43.9087 | -51.7639 | -52.0523 | -15.5045 | 68.367 | -53.8467 | 68.3624 | -44.8792 | -51.8967 | -51.9653 | -0.1236 | -0.045776 | -0.17395 | 9.9197 | 1.7761 | 2.0645 | 1.8997 | 2.1881 | -0.018311 | -0.068665 | -0.073242 | 8.9493 | 1.8631 | 1.9318 | 1.8814 | 1.9501 | 10.0433 | 122.2137 | 8.9676 | 122.2092 | 122.3419 | 122.2137 | 122.2183 | 122.1954 | -122.3877 | -122.2824 | 122.0901 | 122.1909 | 41.1255 | 38.324
1635.3125 | 122.4014 | -53.7552 | 68.4814 | -0.11162 | 0.030606 | 0.077688 | 0.070703 | -0.00093998 | 0.011352 | 0.012736 | -0.05188 | 0.027694 | 0.079547 | 0.071606 | -0.008468 | 0.02311 | 0.010149 | -12.6572 | 68.4586 | -53.8651 | 68.3487 | -44.0414 | -51.796 | -51.9241 | -15.4495 | 68.4174 | -53.7827 | 68.4174 | -44.783 | -51.8188 | -51.8829 | -0.10986 | -0.022888 | -0.13275 | 9.7137 | 1.8311 | 1.9592 | 1.9409 | 2.0691 | -0.027466 | -0.064087 | -0.064087 | 8.9722 | 1.8723 | 1.9363 | 1.8997 | 1.9638 | 9.8236 | 122.2137 | 8.9996 | 122.2 | 122.3236 | 122.2 | 122.2137 | 122.1725 | -122.3465 | -122.2641 | 122.1039 | 122.1725 | 41.098 | 38.3057
1636.3125 | 122.4197 | -53.8376 | 68.399 | -0.081101 | 0.029965 | 0.078543 | 0.074121 | 0.0029052 | 0.010925 | 0.0095319 | -0.048828 | 0.028762 | 0.078051 | 0.072675 | -0.0099634 | 0.024819 | 0.0077994 | -12.5885 | 68.3807 | -53.9612 | 68.2617 | -43.9865 | -51.8051 | -52.0889 | -15.4816 | 68.3487 | -53.8605 | 68.3533 | -44.8517 | -51.915 | -51.9608 | -0.1236 | -0.018311 | -0.13733 | 9.8511 | 1.7487 | 2.0325 | 1.8723 | 2.1561 | -0.022889 | -0.050354 | -0.045777 | 8.9859 | 1.8768 | 1.9226 | 1.8997 | 1.9455 | 9.9747 | 122.2229 | 9.0088 | 122.2137 | 122.3419 | 122.2092 | 122.2183 | 122.1863 | -122.3602 | -122.2595 | 122.0993 | 122.1909 | 41.2491 | 38.356
1637.3125 | 122.4243 | -53.8971 | 68.3166 | -0.096359 | 0.028683 | 0.078116 | 0.074548 | -0.00029898 | 0.011352 | 0.014232 | -0.054932 | 0.027694 | 0.080401 | 0.072888 | -0.0074 | 0.022896 | 0.008013 | -12.7487 | 68.2663 | -54.0802 | 68.1702 | -44.0552 | -51.8921 | -52.1667 | -15.5273 | 68.2205 | -53.9429 | 68.2571 | -44.9203 | -51.9699 | -52.0477 | -0.1831 | -0.050354 | -0.14648 | 9.8419 | 1.7303 | 2.005 | 1.9135 | 2.1881 | -0.045776 | -0.09613 | -0.059509 | 8.9767 | 1.8494 | 1.9272 | 1.8951 | 1.973 | 10.025 | 122.2504 | 9.0225 | 122.2 | 122.3465 | 122.1634 | 122.1634 | 122.1176 | -122.3969 | -122.2595 | 122.0673 | 122.1542 | 41.1484 | 38.3698
1638.3125 | 122.4243 | -53.7277 | 68.4952 | -0.10399 | 0.029538 | 0.077688 | 0.073907 | -0.00051278 | 0.013488 | 0.011882 | -0.097656 | 0.026412 | 0.079974 | 0.070111 | -0.0082544 | 0.025246 | 0.011217 | -12.4969 | 68.4402 | -53.8696 | 68.3899 | -43.84 | -51.7044 | -51.9791 | -15.3168 | 68.4128 | -53.7735 | 68.4814 | -44.6732 | -51.7502 | -51.8417 | -0.14191 | -0.054931 | -0.10528 | 9.8877 | 1.7487 | 2.0233 | 1.8906 | 2.1652 | -0.045777 | -0.082397 | -0.013733 | 9.0546 | 1.886 | 1.9775 | 1.9318 | 2.0233 | 10.0296 | 122.2595 | 9.1003 | 122.2549 | 122.3099 | 122.1863 | 122.168 | 122.1405 | -122.3648 | -122.2687 | 122.1176 | 122.2092 | 41.2308 | 38.4109
1639.3125 | 122.438 | -53.7689 | 68.4448 | -0.10399 | 0.031033 | 0.079397 | 0.074121 | -0.0017944 | 0.010284 | 0.011882 | -0.05188 | 0.028762 | 0.077411 | 0.075024 | -0.0065454 | 0.023537 | 0.010576 | -12.561 | 68.399 | -53.8971 | 68.3212 | -43.8904 | -51.7776 | -52.0294 | -15.3763 | 68.3716 | -53.7918 | 68.4357 | -44.7418 | -51.8326 | -51.8646 | -0.12817 | -0.045776 | -0.1236 | 9.8785 | 1.7395 | 1.9913 | 1.8677 | 2.1194 | -0.022888 | -0.073242 | -0.009155 | 9.0271 | 1.9043 | 1.9363 | 1.9272 | 1.9592 | 10.0067 | 122.2183 | 9.05 | 122.2275 | 122.2961 | 122.1634 | 122.168 | 122.1405 | -122.3419 | -122.2366 | 122.0901 | 122.2046 | 41.2079 | 38.3926
1640.3125 | 122.4014 | -53.7323 | 68.5135 | -0.10399 | 0.02847 | 0.077047 | 0.073266 | -0.00029898 | 0.010925 | 0.010173 | -0.01831 | 0.029403 | 0.078906 | 0.071606 | -0.0052638 | 0.024178 | 0.0090812 | -12.4649 | 68.4769 | -53.8605 | 68.3578 | -43.8309 | -51.7273 | -51.9974 | -15.3625 | 68.4402 | -53.7643 | 68.4402 | -44.6823 | -51.7868 | -51.8509 | -0.12817 | -0.036621 | -0.15564 | 9.9014 | 1.7349 | 2.005 | 1.8631 | 2.1332 | -0.032043 | -0.073242 | -0.073242 | 9.05 | 1.8814 | 1.9455 | 1.9135 | 1.9775 | 10.0296 | 122.2183 | 9.082 | 122.2046 | 122.3373 | 122.2046 | 122.2092 | 122.1725 | -122.374 | -122.2778 | 122.0901 | 122.1725 | 41.2674 | 38.3698
1641.3125 | 122.406 | -53.7781 | 68.486 | -0.12688 | 0.029538 | 0.078329 | 0.072626 | -0.00051278 | 0.01242 | 0.011668 | -0.061035 | 0.027694 | 0.078692 | 0.071393 | -0.0078272 | 0.024819 | 0.0099356 | -12.5061 | 68.4311 | -53.9017 | 68.3807 | -43.7897 | -51.7181 | -51.9928 | -15.2985 | 68.3853 | -53.7872 | 68.4494 | -44.6548 | -51.7776 | -51.8463 | -0.1236 | -0.054932 | -0.10529 | 9.9884 | 1.7853 | 2.0599 | 1.9089 | 2.1835 | -0.009155 | -0.10071 | -0.036621 | 9.1232 | 1.9318 | 2.0004 | 1.9409 | 2.0096 | 10.112 | 122.2824 | 9.1324 | 122.2366 | 122.3328 | 122.1725 | 122.2092 | 122.1634 | -122.3877 | -122.2733 | 122.1588 | 122.2275 | 41.272 | 38.4796
1642.3125 | 122.4152 | -53.5812 | 68.6371 | -0.08873 | 0.030179 | 0.078543 | 0.072839 | -0.0015808 | 0.011993 | 0.0095319 | -0.048828 | 0.027267 | 0.077197 | 0.075665 | -0.0080408 | 0.025032 | 0.0043814 | -12.3047 | 68.6325 | -53.6911 | 68.5638 | -43.634 | -51.5121 | -51.796 | -15.0833 | 68.5776 | -53.5858 | 68.6417 | -44.4168 | -51.6083 | -51.6495 | -0.10986 | -0.004578 | -0.073242 | 9.9472 | 1.7853 | 2.0691 | 1.8951 | 2.179 | -0.004577 | -0.059509 | 0.004578 | 9.1644 | 1.9318 | 1.973 | 1.9363 | 1.9775 | 10.0571 | 122.2549 | 9.169 | 122.2275 | 122.3236 | 122.1634 | 122.2137 | 122.1588 | -122.3282 | -122.2229 | 122.1451 | 122.2229 | 41.2766 | 38.4979
1643.3125 | 122.3328 | -53.6911 | 68.5364 | -0.065842 | 0.029538 | 0.080465 | 0.07113 | -0.00093998 | 0.010284 | 0.011241 | -0.048828 | 0.028762 | 0.079333 | 0.076306 | -0.011032 | 0.02546 | 0.008013 | -12.4512 | 68.5318 | -53.7827 | 68.454 | -43.7347 | -51.6037 | -51.8967 | -15.184 | 68.4723 | -53.6865 | 68.5181 | -44.5221 | -51.6769 | -51.6953 | -0.091553 | -0.004578 | -0.082398 | 9.9564 | 1.7944 | 2.0874 | 1.886 | 2.179 | 0.004578 | -0.064087 | -0.018311 | 9.169 | 1.9959 | 2.0142 | 1.9913 | 2.0096 | 10.0479 | 122.2366 | 9.1644 | 122.2046 | 122.3145 | 122.1588 | 122.2229 | 122.1634 | -122.319 | -122.2229 | 122.1451 | 122.2092 | 41.2399 | 38.5071
1644.3125 | 122.4655 | -53.4805 | 68.6783 | -0.10399 | 0.03146 | 0.07662 | 0.071344 | -0.00029898 | 0.010925 | 0.0095319 | 0.070191 | 0.026626 | 0.077838 | 0.063061 | -0.0088952 | 0.020546 | 0.01314 | -12.2314 | 68.6874 | -53.54 | 68.6142 | -43.5516 | -51.4526 | -51.6953 | -14.9826 | 68.6462 | -53.476 | 68.7378 | -44.2886 | -51.4297 | -51.5213 | -0.059509 | 0.009155 | -0.064087 | 9.9289 | 1.7853 | 2.0279 | 1.8448 | 2.0874 | 0.004578 | -0.032044 | 0.059509 | 9.1919 | 1.9592 | 2.0508 | 1.9547 | 2.0462 | 9.9884 | 122.1542 | 9.1873 | 122.2137 | 122.2275 | 122.1222 | 122.168 | 122.1268 | -122.2183 | -122.1542 | 122.0947 | 122.2183 | 41.2491 | 38.4979
1645.3125 | 122.3877 | -53.5721 | 68.6508 | -0.096359 | 0.030606 | 0.078329 | 0.074334 | 0.002478 | 0.009643 | 0.0093181 | -0.061035 | 0.029617 | 0.07976 | 0.069043 | -0.0076136 | 0.025673 | 0.0099356 | -12.3871 | 68.6005 | -53.7094 | 68.5547 | -43.6386 | -51.5488 | -51.8143 | -15.0833 | 68.5501 | -53.6087 | 68.605 | -44.4077 | -51.6083 | -51.6678 | -0.13733 | -0.050354 | -0.096131 | 9.9335 | 1.7578 | 2.0233 | 1.8951 | 2.1606 | -0.036621 | -0.10071 | -0.045776 | 9.1644 | 1.9043 | 1.9638 | 1.9409 | 2.0004 | 10.0708 | 122.2641 | 9.2011 | 122.2137 | 122.3099 | 122.1588 | 122.1725 | 122.1222 | -122.3602 | -122.2595 | 122.1268 | 122.1771 | 41.185 | 38.4888
1646.3125 | 122.3785 | -53.5126 | 68.7286 | -0.073471 | 0.029324 | 0.078116 | 0.075403 | -0.00029898 | 0.011352 | 0.014872 | -0.054932 | 0.027908 | 0.078265 | 0.077588 | -0.008468 | 0.025887 | 0.0099356 | -12.4741 | 68.6646 | -53.6362 | 68.6325 | -43.5425 | -51.4709 | -51.7456 | -15.0055 | 68.6508 | -53.5126 | 68.692 | -44.3207 | -51.5259 | -51.5671 | -0.1236 | -0.064087 | -0.096131 | 9.9701 | 1.767 | 2.0416 | 1.8906 | 2.1652 | 0 | -0.07782 | -0.036621 | 9.1919 | 1.9455 | 1.9867 | 1.9455 | 1.9867 | 10.0937 | 122.2687 | 9.1919 | 122.2046 | 122.3007 | 122.1634 | 122.1771 | 122.1634 | -122.3648 | -122.2412 | 122.1451 | 122.2046 | 41.0385 | 38.5071
1647.3125 | 122.3785 | -53.5217 | 68.7286 | -0.096359 | 0.030606 | 0.078116 | 0.071985 | -0.0017944 | 0.010284 | 0.010173 | -0.042725 | 0.028762 | 0.078692 | 0.07182 | -0.0069726 | 0.025673 | 0.0099356 | -12.4741 | 68.6508 | -53.6224 | 68.6234 | -43.5745 | -51.4801 | -51.741 | -14.9826 | 68.6508 | -53.508 | 68.7012 | -44.3024 | -51.5121 | -51.5762 | -0.10071 | -0.07782 | -0.10529 | 9.9472 | 1.7807 | 2.0416 | 1.8814 | 2.1423 | 0.013733 | -0.07782 | -0.027466 | 9.2194 | 1.9455 | 2.0096 | 1.9318 | 1.9958 | 10.0479 | 122.2458 | 9.2056 | 122.2092 | 122.2733 | 122.1588 | 122.1725 | 122.1725 | -122.3511 | -122.2366 | 122.1451 | 122.2229 | 41.0477 | 38.5391
1648.3125 | 122.3694 | -53.6499 | 68.6325 | -0.17265 | 0.028683 | 0.07897 | 0.072626 | 0.00076902 | 0.011138 | 0.011027 | -0.076294 | 0.02983 | 0.078479 | 0.077588 | -0.0074 | 0.023751 | 0.0090812 | -12.6709 | 68.5547 | -53.7735 | 68.454 | -43.7668 | -51.6357 | -51.9196 | -15.2161 | 68.5226 | -53.6591 | 68.5226 | -44.4168 | -51.6861 | -51.7319 | -0.1236 | -0.07782 | -0.17853 | 9.8831 | 1.7303 | 2.0142 | 1.8539 | 2.1378 | -0.009156 | -0.10986 | -0.10986 | 9.2331 | 1.918 | 1.9638 | 1.9272 | 1.973 | 10.0067 | 122.2275 | 9.2422 | 122.1817 | 122.3282 | 122.1817 | 122.2046 | 122.1725 | -122.406 | -122.2916 | 122.1039 | 122.1725 | 40.979 | 38.4338
1649.3281 | 122.4655 | -53.4164 | 68.7286 | -0.11925 | 0.027401 | 0.078329 | 0.068994 | -0.0047852 | 0.009643 | 0.011668 | 0.091553 | 0.027267 | 0.075702 | 0.075452 | -0.0099634 | 0.022896 | 0.012713 | -12.4283 | 68.7012 | -53.5217 | 68.7698 | -43.3685 | -51.2878 | -51.535 | -14.5844 | 68.7241 | -53.421 | 68.8065 | -44.0918 | -51.2878 | -51.4252 | -0.10529 | -0.027466 | 0.041198 | 10.0479 | 1.8814 | 2.1286 | 1.9867 | 2.2339 | -0.004578 | -0.004578 | 0.07782 | 9.3246 | 1.9913 | 2.1286 | 1.9959 | 2.1332 | 10.1532 | 122.2916 | 9.3292 | 122.2275 | 122.2229 | 122.1451 | 122.1176 | 122.1405 | -122.2504 | -122.1497 | 122.1863 | 122.2229 | 40.9882 | 38.8321
1650.3125 | 122.438 | -53.3844 | 68.8202 | -0.050583 | 0.028897 | 0.078329 | 0.073266 | 0.00012822 | 0.009643 | 0.010173 | -0.067139 | 0.027694 | 0.078906 | 0.063702 | -0.0097498 | 0.023323 | 0.011431 | -12.4924 | 68.8065 | -53.508 | 68.7103 | -43.4784 | -51.3794 | -51.622 | -14.9139 | 68.7195 | -53.4119 | 68.7836 | -44.1193 | -51.3977 | -51.4801 | -0.1236 | -0.013732 | -0.10986 | 9.906 | 1.7624 | 2.005 | 1.886 | 2.1286 | -0.027466 | -0.10071 | -0.036621 | 9.2651 | 1.9043 | 1.9867 | 1.9318 | 2.0142 | 10.0296 | 122.2183 | 9.2926 | 122.1954 | 122.3145 | 122.1313 | 122.1909 | 122.1039 | -122.3282 | -122.2321 | 122.0947 | 122.168 | 40.892 | 38.4705
1651.3125 | 122.3557 | -53.4668 | 68.7836 | -0.08873 | 0.031888 | 0.078543 | 0.073053 | 0.0046142 | 0.0075066 | 0.0088909 | -0.079346 | 0.030258 | 0.079333 | 0.069257 | -0.0093226 | 0.024392 | 0.01079 | -12.616 | 68.7332 | -53.595 | 68.6279 | -43.6203 | -51.5076 | -51.7181 | -15.0558 | 68.692 | -53.4897 | 68.6966 | -44.22 | -51.4938 | -51.5579 | -0.12817 | -0.050354 | -0.15564 | 9.8465 | 1.7487 | 1.9592 | 1.8768 | 2.0874 | -0.022888 | -0.091552 | -0.086975 | 9.2468 | 1.9089 | 1.973 | 1.9318 | 1.9959 | 9.9747 | 122.2229 | 9.2697 | 122.1863 | 122.3282 | 122.1817 | 122.2 | 122.1588 | -122.3785 | -122.2733 | 122.0947 | 122.1634 | 40.8508 | 38.4109
1652.3125 | 122.3785 | -53.3157 | 68.9255 | -0.12688 | 0.029324 | 0.080038 | 0.072198 | 0.0033324 | 0.010925 | 0.012736 | -0.061035 | 0.027908 | 0.07976 | 0.073956 | -0.008468 | 0.024178 | 0.011858 | -12.529 | 68.8889 | -53.4439 | 68.7744 | -43.4601 | -51.3245 | -51.5625 | -14.9002 | 68.8477 | -53.3569 | 68.8248 | -44.046 | -51.3565 | -51.4114 | -0.12817 | -0.036621 | -0.15106 | 9.8557 | 1.7532 | 1.9913 | 1.8814 | 2.1194 | -0.041199 | -0.07782 | -0.10071 | 9.2697 | 1.9043 | 1.9592 | 1.9455 | 2.0004 | 9.9838 | 122.2183 | 9.3109 | 122.1817 | 122.3328 | 122.2046 | 122.2046 | 122.1634 | -122.3694 | -122.2824 | 122.0901 | 122.1405 | 40.7867 | 38.4155
1653.3125 | 122.3694 | -53.3798 | 68.8522 | -0.11925 | 0.030819 | 0.078329 | 0.074762 | 0.00055542 | 0.009002 | 0.012309 | -0.10376 | 0.028976 | 0.077411 | 0.07652 | -0.009109 | 0.025032 | 0.0090812 | -12.6663 | 68.8385 | -53.5034 | 68.4952 | -43.483 | -50.9857 | -51.5396 | -14.8819 | 68.8019 | -53.3981 | 68.7836 | -44.0643 | -51.4069 | -51.4435 | -0.1236 | -0.013733 | -0.35706 | 9.8969 | 1.8402 | 2.3941 | 1.9638 | 2.5177 | -0.01831 | -0.050354 | -0.068665 | 9.3155 | 1.9363 | 1.973 | 1.9547 | 1.9913 | 10.0204 | 121.9986 | 9.3338 | 122.1817 | 122.3419 | 122.2 | 122.2183 | 122.1817 | -122.3557 | -122.2504 | 121.875 | 122.1634 | 40.7135 | 38.4979
1654.3125 | 122.5067 | -53.2562 | 68.9255 | -0.12688 | 0.030179 | 0.078116 | 0.070062 | -0.002649 | 0.011352 | 0.010386 | 0.061035 | 0.027481 | 0.078051 | 0.067761 | -0.0082544 | 0.021614 | 0.0075858 | -12.6984 | 68.866 | -53.3981 | 68.8339 | -43.364 | -51.2283 | -51.4618 | -14.7858 | 68.8293 | -53.2928 | 68.9346 | -43.8492 | -51.1826 | -51.2787 | -0.14191 | -0.059509 | -0.091553 | 9.8923 | 1.7944 | 2.0279 | 1.9363 | 2.1698 | -0.036621 | -0.09613 | 0.009155 | 9.407 | 1.9775 | 2.0737 | 2.0142 | 2.1103 | 10.0342 | 122.2321 | 9.4437 | 122.2275 | 122.2641 | 122.1222 | 122.1222 | 122.0856 | -122.3236 | -122.2183 | 122.0901 | 122.1909 | 40.5579 | 38.4705
1655.3125 | 122.3602 | -53.3112 | 68.9209 | -0.14977 | 0.031247 | 0.078329 | 0.074975 | 0.0046142 | 0.0083612 | 0.011241 | -0.073242 | 0.02983 | 0.078265 | 0.067334 | -0.0097498 | 0.025246 | 0.013567 | -12.9089 | 68.8797 | -53.4531 | 68.7698 | -43.4967 | -51.3565 | -51.59 | -14.8544 | 68.8339 | -53.334 | 68.8202 | -43.9682 | -51.3657 | -51.3977 | -0.14191 | -0.041198 | -0.15106 | 9.8145 | 1.7212 | 1.9547 | 1.8631 | 2.0966 | -0.022888 | -0.086975 | -0.10071 | 9.343 | 1.9135 | 1.9455 | 1.9363 | 1.9684 | 9.9564 | 122.2229 | 9.3658 | 122.1542 | 122.3328 | 122.168 | 122.1909 | 122.1451 | -122.374 | -122.2549 | 122.081 | 122.1313 | 40.4022 | 38.4567
1656.3125 | 122.3923 | -53.2974 | 68.9438 | -0.12688 | 0.030819 | 0.077261 | 0.073694 | 0.00076902 | 0.010497 | 0.0078229 | -0.045776 | 0.030044 | 0.080615 | 0.075879 | -0.0093226 | 0.022896 | 0.0099356 | -12.9822 | 68.9072 | -53.421 | 68.6691 | -43.1946 | -51.0956 | -51.5762 | -14.8544 | 68.8843 | -53.3066 | 68.8843 | -43.9316 | -51.3153 | -51.3611 | -0.1236 | -0.036621 | -0.27466 | 10.1028 | 1.7212 | 2.2018 | 1.8448 | 2.3254 | -0.009156 | -0.05951 | -0.05951 | 9.3658 | 1.9363 | 1.9821 | 1.9455 | 1.9913 | 10.2264 | 122.0901 | 9.375 | 122.1909 | 122.3282 | 122.1909 | 122.2046 | 122.1817 | -122.3648 | -122.2504 | 121.9666 | 122.1817 | 40.3152 | 38.443
1657.3125 | 122.3648 | -53.3432 | 68.9026 | -0.14977 | 0.028042 | 0.079184 | 0.075616 | 0.00055542 | 0.006225 | 0.011455 | -0.036621 | 0.028335 | 0.080615 | 0.07182 | -0.008468 | 0.023537 | 0.0082266 | -13.0829 | 68.8614 | -53.4576 | 68.9621 | -43.5333 | -51.4847 | -51.5396 | -14.9277 | 68.8477 | -53.3569 | 68.8477 | -43.959 | -51.3611 | -51.4069 | -0.11444 | -0.041199 | 0.059509 | 9.8099 | 1.8036 | 1.8585 | 1.918 | 1.973 | -0.013733 | -0.054932 | -0.054932 | 9.3842 | 1.9363 | 1.9821 | 1.9501 | 1.9959 | 9.9243 | 122.4197 | 9.3979 | 122.2046 | 122.319 | 122.2046 | 122.2046 | 122.1909 | -122.3602 | -122.2595 | 122.3053 | 122.1909 | 40.2603 | 38.4155
1658.3125 | 122.4335 | -53.1967 | 69.0079 | -0.10399 | 0.029324 | 0.077261 | 0.074548 | -0.00051278 | 0.010925 | 0.012309 | -0.057983 | 0.027908 | 0.078692 | 0.069684 | -0.0069726 | 0.023323 | 0.016131 | -12.8632 | 68.9987 | -53.3432 | 68.8797 | -43.3319 | -51.2421 | -51.4389 | -14.7583 | 68.9255 | -53.215 | 69.0033 | -43.7531 | -51.1505 | -51.2421 | -0.14648 | -0.009156 | -0.12817 | 9.8648 | 1.7578 | 1.9547 | 1.9043 | 2.1011 | -0.018311 | -0.082398 | -0.004578 | 9.4437 | 1.9547 | 2.0462 | 1.973 | 2.0645 | 10.0113 | 122.2229 | 9.462 | 122.2183 | 122.3419 | 122.1405 | 122.1954 | 122.1222 | -122.3511 | -122.2229 | 122.0764 | 122.2 | 40.3336 | 38.4384
1659.3281 | 122.3831 | -53.0594 | 69.1956 | -0.096359 | 0.029751 | 0.075766 | 0.070703 | 0.0031188 | 0.0087884 | 0.0091045 | 0.027466 | 0.02684 | 0.079974 | 0.069043 | -0.008468 | 0.023964 | 0.0090812 | -12.7487 | 69.136 | -53.1555 | 69.072 | -43.1488 | -51.004 | -51.2146 | -14.5798 | 69.1132 | -53.0777 | 69.1177 | -43.5654 | -50.9903 | -51.1002 | -0.096131 | -0.05951 | -0.1236 | 9.9106 | 1.8448 | 2.0554 | 1.9409 | 2.1515 | -0.018311 | -0.082398 | -0.07782 | 9.494 | 1.9592 | 2.0691 | 1.9775 | 2.0874 | 10.0067 | 122.2275 | 9.5123 | 122.1954 | 122.2916 | 122.1909 | 122.1954 | 122.1725 | -122.3511 | -122.2733 | 122.1313 | 122.1771 | 40.3107 | 38.4796
1660.3125 | 122.2229 | -52.9404 | 69.2642 | -0.11162 | 0.030606 | 0.080252 | 0.074762 | 0.0035462 | 0.010284 | 0.0093181 | -0.073242 | 0.028762 | 0.080401 | 0.070538 | -0.0069726 | 0.025246 | 0.0088676 | -12.8906 | 69.2459 | -53.0594 | 69.1269 | -43.1396 | -51.004 | -51.1871 | -14.6027 | 69.2276 | -52.9678 | 69.223 | -43.515 | -50.9491 | -50.9766 | -0.11902 | -0.01831 | -0.13733 | 9.8007 | 1.7532 | 1.9363 | 1.8723 | 2.0554 | -0.027465 | -0.036621 | -0.041199 | 9.4254 | 1.9638 | 1.9913 | 1.9913 | 2.0187 | 9.9197 | 122.1863 | 9.4528 | 122.1909 | 122.3053 | 122.1954 | 122.1863 | 122.168 | -122.3236 | -122.2321 | 122.0673 | 122.1634 | 40.0497 | 38.3377
1661.3125 | 122.4518 | -53.0136 | 69.1772 | -0.14977 | 0.030392 | 0.080252 | 0.072626 | 0.0035462 | 0.010497 | 0.0091045 | -0.045776 | 0.028762 | 0.080188 | 0.071179 | -0.010391 | 0.025673 | 0.0095084 | -12.9044 | 69.1635 | -53.1281 | 69.104 | -43.1488 | -51.0269 | -51.2054 | -14.6164 | 69.1086 | -53.0273 | 69.2322 | -43.4647 | -50.9079 | -50.9674 | -0.11444 | -0.013733 | -0.073242 | 9.8648 | 1.8082 | 1.9867 | 1.9226 | 2.1011 | -0.013733 | -0.068664 | 0.054932 | 9.5489 | 2.0462 | 2.1057 | 2.0599 | 2.1194 | 9.9792 | 122.2321 | 9.5627 | 122.2595 | 122.2916 | 122.1359 | 122.1771 | 122.1222 | -122.3053 | -122.2046 | 122.1176 | 122.2458 | 40.1093 | 38.3972
1662.3125 | 122.4884 | -52.977 | 69.1681 | -0.12688 | 0.029965 | 0.077902 | 0.073907 | 0.0029052 | 0.011138 | 0.012523 | -0.033569 | 0.029403 | 0.07976 | 0.075024 | -0.009109 | 0.024392 | 0.0071586 | -12.9181 | 69.1177 | -53.1464 | 69.0994 | -43.1442 | -51.0132 | -51.178 | -14.6072 | 69.0903 | -53.0136 | 69.2551 | -43.4372 | -50.8987 | -50.972 | -0.16937 | -0.050354 | -0.068665 | 9.8328 | 1.799 | 1.9638 | 1.9684 | 2.1332 | -0.036621 | -0.07782 | 0.086975 | 9.5398 | 2.005 | 2.0782 | 2.0416 | 2.1149 | 10.0021 | 122.2458 | 9.5764 | 122.2687 | 122.2641 | 122.1039 | 122.0947 | 122.0673 | -122.3145 | -122.1817 | 122.0764 | 122.2321 | 40.0589 | 38.3698
1663.3125 | 122.4197 | -53.0365 | 69.1589 | -0.12688 | 0.027829 | 0.078543 | 0.072198 | -0.00051278 | 0.011566 | 0.012095 | -0.039673 | 0.028549 | 0.081256 | 0.072888 | -0.0088952 | 0.02311 | 0.014635 | -13.0692 | 69.1544 | -53.1509 | 69.0537 | -43.2037 | -51.091 | -51.2466 | -14.6896 | 69.1132 | -53.0457 | 69.1681 | -43.4921 | -50.9674 | -51.0498 | -0.11444 | -0.004578 | -0.10529 | 9.8328 | 1.7899 | 1.9455 | 1.9043 | 2.0599 | -0.009155 | -0.045777 | 0.009155 | 9.5444 | 1.9867 | 2.0691 | 1.9958 | 2.0782 | 9.9472 | 122.2046 | 9.5535 | 122.2137 | 122.3053 | 122.1588 | 122.1909 | 122.1497 | -122.3099 | -122.2046 | 122.0901 | 122.2046 | 39.9673 | 38.3469
1664.3125 | 122.4426 | -52.9083 | 69.2688 | -0.20317 | 0.029751 | 0.078116 | 0.071985 | -0.00029898 | 0.013274 | 0.014232 | -0.0030517 | 0.028335 | 0.07976 | 0.066266 | -0.0095362 | 0.025246 | 0.0099356 | -12.8906 | 69.2139 | -53.0228 | 69.223 | -42.9932 | -50.9216 | -51.0727 | -14.5844 | 69.1818 | -52.9312 | 69.2963 | -43.3502 | -50.8255 | -50.9171 | -0.11444 | -0.054932 | -0.045777 | 9.9152 | 1.8356 | 1.9867 | 1.9501 | 2.1011 | -0.022888 | -0.086975 | 0.027466 | 9.5581 | 1.9913 | 2.0828 | 2.0142 | 2.1057 | 10.0296 | 122.2458 | 9.581 | 122.2275 | 122.2366 | 122.113 | 122.1222 | 122.0901 | -122.2916 | -122.2 | 122.1313 | 122.2046 | 40.0177 | 38.324
1665.3125 | 122.4609 | -52.8763 | 69.2871 | -0.11925 | 0.03146 | 0.077475 | 0.071985 | 0.00034182 | 0.0087884 | 0.0095319 | 0.057983 | 0.028549 | 0.081469 | 0.070752 | -0.0097498 | 0.025032 | 0.011004 | -12.9501 | 69.2276 | -52.9953 | 69.2917 | -42.9703 | -51.0361 | -51.2283 | -14.3692 | 69.1864 | -52.8992 | 69.3558 | -43.277 | -50.7751 | -50.8255 | -0.11902 | -0.059509 | 0.004578 | 9.906 | 1.6479 | 1.8402 | 1.767 | 1.9592 | -0.022888 | -0.10071 | 0.068665 | 9.5993 | 2.0508 | 2.1011 | 2.0737 | 2.124 | 10.025 | 122.287 | 9.6222 | 122.2549 | 122.2229 | 122.0856 | 122.1039 | 122.0627 | -122.2824 | -122.1863 | 122.168 | 122.2321 | 39.9261 | 38.5071
1666.3125 | 122.4792 | -52.8168 | 69.3375 | -0.17265 | 0.032101 | 0.077047 | 0.070917 | -0.00051278 | 0.010497 | 0.0091045 | -0.0030517 | 0.030685 | 0.076556 | 0.065198 | -0.009109 | 0.025887 | 0.0039542 | -13.0188 | 69.2871 | -52.9541 | 69.3237 | -42.8925 | -50.8163 | -50.9491 | -14.447 | 69.2413 | -52.8671 | 69.3741 | -43.2404 | -50.7202 | -50.8072 | -0.13733 | -0.050354 | -0.013733 | 9.9243 | 1.8677 | 2.0004 | 2.005 | 2.1378 | -0.050354 | -0.09613 | 0.036621 | 9.5764 | 2.0096 | 2.0966 | 2.0599 | 2.1469 | 10.0616 | 122.2778 | 9.6268 | 122.2412 | 122.2412 | 122.1085 | 122.1039 | 122.0581 | -122.2916 | -122.2046 | 122.1405 | 122.1909 | 39.798 | 38.3698
1667.3125 | 122.4609 | -52.7847 | 69.3466 | -0.14214 | 0.031247 | 0.079184 | 0.071985 | 0.0016236 | 0.010711 | 0.0095319 | -0.061035 | 0.028762 | 0.076129 | 0.073315 | -0.0095362 | 0.025032 | 0.012926 | -13.0234 | 69.3237 | -52.8992 | 69.342 | -42.8604 | -50.766 | -50.9216 | -14.4516 | 69.2734 | -52.7985 | 69.4565 | -43.1808 | -50.647 | -50.7248 | -0.11444 | -0.022889 | -0.004578 | 9.9243 | 1.8631 | 2.0187 | 1.9775 | 2.1332 | -0.013733 | -0.073243 | 0.10986 | 9.6039 | 2.0599 | 2.1378 | 2.0737 | 2.1515 | 10.0388 | 122.2412 | 9.6176 | 122.2549 | 122.2229 | 122.0718 | 122.1085 | 122.0581 | -122.2458 | -122.1451 | 122.1268 | 122.2412 | 39.7614 | 38.3331
1668.3125 | 122.4701 | -52.7161 | 69.5206 | -0.16502 | 0.028256 | 0.078116 | 0.072198 | 0.005896 | 0.012634 | 0.010386 | 0.012207 | 0.031326 | 0.078906 | 0.070966 | -0.0080408 | 0.024605 | 0.0082266 | -12.9456 | 69.4244 | -52.8076 | 69.4427 | -42.746 | -50.7065 | -50.8209 | -14.3875 | 69.3832 | -52.7344 | 69.5023 | -43.1122 | -50.5829 | -50.679 | -0.091553 | -0.096131 | -0.07782 | 9.9701 | 1.8951 | 2.0096 | 1.9867 | 2.1011 | -0.018311 | -0.13733 | -0.018311 | 9.6039 | 2.037 | 2.1332 | 2.0554 | 2.1515 | 10.0616 | 122.2504 | 9.6222 | 122.2366 | 122.2321 | 122.1176 | 122.1405 | 122.0993 | -122.3282 | -122.2549 | 122.1588 | 122.2183 | 39.7705 | 38.3286
1669.3125 | 122.5067 | -52.6749 | 69.4977 | -0.27184 | 0.029538 | 0.075766 | 0.072198 | -0.002649 | 0.0087884 | 0.011027 | 0.033569 | 0.02919 | 0.078265 | 0.06947 | -0.009109 | 0.023751 | 0.01079 | -12.9181 | 69.4336 | -52.8351 | 69.4931 | -42.6453 | -50.6104 | -50.7614 | -14.328 | 69.3924 | -52.7023 | 69.548 | -43.0389 | -50.5005 | -50.6241 | -0.16022 | -0.064087 | -0.004578 | 10.0296 | 1.9135 | 2.0645 | 2.0737 | 2.2247 | -0.027466 | -0.10529 | 0.050354 | 9.6359 | 2.0508 | 2.1744 | 2.0782 | 2.2018 | 10.1898 | 122.3282 | 9.6634 | 122.2504 | 122.2687 | 122.0947 | 122.1085 | 122.0673 | -122.3328 | -122.2 | 122.168 | 122.2229 | 39.7568 | 38.3469
1670.3125 | 122.4564 | -52.7115 | 69.4473 | -0.13451 | 0.029965 | 0.077047 | 0.072839 | -0.00029898 | 0.010711 | 0.012736 | -0.036621 | 0.028976 | 0.07677 | 0.064343 | -0.010818 | 0.023964 | 0.010149 | -13.0508 | 69.3787 | -52.8351 | 69.4107 | -42.7322 | -50.7111 | -50.8163 | -14.4653 | 69.3649 | -52.7573 | 69.4839 | -43.1351 | -50.5829 | -50.6927 | -0.1236 | -0.068665 | -0.036621 | 9.9792 | 1.8951 | 2.0004 | 2.0187 | 2.124 | -0.045776 | -0.082398 | 0.036621 | 9.5764 | 2.0187 | 2.1286 | 2.0645 | 2.1744 | 10.1028 | 122.2458 | 9.6222 | 122.2412 | 122.2137 | 122.1222 | 122.0901 | 122.0764 | -122.2824 | -122.2046 | 122.1222 | 122.1954 | 39.6606 | 38.2462
1671.3125 | 122.4335 | -52.6108 | 69.5709 | -0.11162 | 0.028897 | 0.07897 | 0.072412 | -8.538e-05 | 0.011993 | 0.012095 | -0.0091553 | 0.02983 | 0.079547 | 0.072675 | -0.010177 | 0.023323 | 0.0092948 | -12.9913 | 69.4839 | -52.7573 | 69.5297 | -42.6178 | -50.6058 | -50.7339 | -14.4653 | 69.4565 | -52.6428 | 69.5938 | -43.0801 | -50.5005 | -50.6012 | -0.14648 | -0.086975 | -0.041199 | 9.993 | 1.8768 | 2.005 | 2.0233 | 2.1515 | -0.032043 | -0.11444 | 0.022888 | 9.5306 | 2.0096 | 2.1103 | 2.0416 | 2.1423 | 10.1395 | 122.287 | 9.5627 | 122.2366 | 122.2412 | 122.0993 | 122.0947 | 122.0673 | -122.3282 | -122.2137 | 122.1405 | 122.2046 | 39.6194 | 38.1454
1672.3125 | 122.4426 | -52.7161 | 69.4885 | -0.10399 | 0.028683 | 0.080893 | 0.072198 | 0.00076902 | 0.01242 | 0.012523 | 0.088501 | 0.02919 | 0.077411 | 0.070966 | -0.011032 | 0.025246 | 0.013781 | -13.1378 | 69.4199 | -52.7985 | 69.4153 | -42.691 | -50.6973 | -50.798 | -14.7766 | 69.3878 | -52.7206 | 69.5023 | -43.1808 | -50.6149 | -50.6973 | -0.082398 | -0.068664 | -0.073242 | 10.025 | 1.918 | 2.0187 | 2.0004 | 2.1011 | -0.004578 | -0.10071 | 0.013733 | 9.5352 | 2.0187 | 2.1011 | 2.0233 | 2.1057 | 10.1074 | 122.2137 | 9.5398 | 122.2229 | 122.2183 | 122.1085 | 122.1359 | 122.1039 | -122.287 | -122.2092 | 122.1313 | 122.2183 | 39.5782 | 37.9395
1673.3125 | 122.4609 | -52.7023 | 69.4748 | -0.10399 | 0.029538 | 0.07662 | 0.072412 | 0.00076902 | 0.0081476 | 0.012523 | 0.0030517 | 0.02919 | 0.078479 | 0.068402 | -0.0076136 | 0.023964 | 0.0067312 | -13.2294 | 69.4244 | -52.8168 | 69.4336 | -42.6086 | -50.6927 | -50.7706 | -14.7263 | 69.3832 | -52.7481 | 69.5251 | -43.19 | -50.5371 | -50.6607 | -0.11444 | -0.050354 | -0.041198 | 10.0937 | 1.9318 | 2.0096 | 2.0462 | 2.124 | -0.045776 | -0.091552 | 0.050354 | 9.5123 | 2.0416 | 2.1652 | 2.0874 | 2.211 | 10.2081 | 122.2504 | 9.5581 | 122.2733 | 122.2412 | 122.1313 | 122.1268 | 122.0856 | -122.2916 | -122.2229 | 122.1359 | 122.2275 | 39.473 | 37.9761
1674.3125 | 122.5204 | -52.4872 | 69.635 | -0.12688 | 0.030606 | 0.077688 | 0.071344 | -0.00093998 | 0.0092156 | 0.011241 | 0.0061035 | 0.027908 | 0.077411 | 0.072461 | -0.009109 | 0.02311 | 0.012499 | -12.9913 | 69.5801 | -52.6428 | 69.6533 | -42.2791 | -50.4593 | -50.5692 | -14.502 | 69.5755 | -52.5467 | 69.7311 | -42.9611 | -50.322 | -50.4776 | -0.15564 | -0.054932 | 0.01831 | 10.2081 | 1.918 | 2.0279 | 2.0737 | 2.1835 | -0.059509 | -0.05951 | 0.09613 | 9.5261 | 2.0096 | 2.1652 | 2.0691 | 2.2247 | 10.3638 | 122.2961 | 9.5856 | 122.2778 | 122.2229 | 122.1222 | 122.0673 | 122.0627 | -122.2778 | -122.1817 | 122.1405 | 122.2183 | 39.4959 | 37.9852
1675.3125 | 122.4609 | -52.5787 | 69.6213 | -0.13451 | 0.030819 | 0.080038 | 0.071344 | -0.0030762 | 0.011352 | 0.017009 | -0.027466 | 0.027267 | 0.075915 | 0.072247 | -0.0093226 | 0.022255 | 0.011431 | -13.1699 | 69.5572 | -52.6886 | 69.5206 | -42.3386 | -50.5554 | -50.6378 | -14.653 | 69.5297 | -52.6016 | 69.6442 | -43.0756 | -50.4227 | -50.56 | -0.10986 | -0.064087 | -0.10071 | 10.2402 | 1.9409 | 2.0233 | 2.0508 | 2.1332 | -0.022889 | -0.091553 | 0.022888 | 9.5032 | 2.0187 | 2.1561 | 2.0416 | 2.179 | 10.35 | 122.2092 | 9.5261 | 122.2458 | 122.2458 | 122.1313 | 122.1359 | 122.1085 | -122.3099 | -122.2229 | 122.0993 | 122.2229 | 39.4089 | 37.9257
1676.3125 | 122.4701 | -52.565 | 69.5984 | -0.12688 | 0.030819 | 0.077902 | 0.070917 | -0.00051278 | 0.010711 | 0.011668 | -0.0091553 | 0.02684 | 0.078906 | 0.066693 | -0.0097498 | 0.026101 | 0.0088676 | -13.1882 | 69.5572 | -52.652 | 69.6487 | -42.1783 | -50.4456 | -50.5463 | -14.7217 | 69.5435 | -52.5742 | 69.5068 | -42.9611 | -50.2991 | -50.4913 | -0.086976 | -0.041199 | 0.050354 | 10.3867 | 2.0187 | 2.1194 | 2.1057 | 2.2064 | -0.009156 | -0.054932 | -0.091553 | 9.6039 | 2.0737 | 2.2659 | 2.0828 | 2.2751 | 10.4736 | 122.3007 | 9.613 | 122.081 | 122.2092 | 122.1176 | 122.1222 | 122.1085 | -122.2504 | -122.1725 | 122.2137 | 122.0718 | 39.3768 | 37.8433
1677.3125 | 122.4609 | -52.684 | 69.4977 | -0.11925 | 0.030819 | 0.077688 | 0.073907 | 0.00076902 | 0.01007 | 0.010814 | -0.030517 | 0.02983 | 0.078906 | 0.07182 | -0.0088952 | 0.023751 | 0.010576 | -13.4766 | 69.4519 | -52.8259 | 69.4611 | -42.4438 | -50.679 | -50.7477 | -15.097 | 69.4473 | -52.7161 | 69.5435 | -43.19 | -50.5051 | -50.5966 | -0.14191 | -0.045777 | -0.036621 | 10.2402 | 1.9363 | 2.005 | 2.0782 | 2.1469 | -0.032043 | -0.050354 | 0.045776 | 9.494 | 2.0874 | 2.179 | 2.1194 | 2.211 | 10.3821 | 122.287 | 9.5261 | 122.2595 | 122.2778 | 122.1634 | 122.1359 | 122.1313 | -122.3236 | -122.2137 | 122.1451 | 122.2275 | 39.2075 | 37.587
1678.3125 | 122.4701 | -52.5375 | 69.5892 | -0.081101 | 0.029538 | 0.077902 | 0.072412 | -0.00029898 | 0.012206 | 0.0095319 | -0.036621 | 0.030258 | 0.075702 | 0.072675 | -0.0095362 | 0.024178 | 0.010363 | -13.2935 | 69.5755 | -52.6749 | 69.603 | -42.2333 | -50.5417 | -50.5783 | -14.9734 | 69.5343 | -52.5879 | 69.6945 | -43.0389 | -50.3723 | -50.4959 | -0.13733 | -0.013733 | 0.013733 | 10.3043 | 1.9592 | 1.9958 | 2.0966 | 2.1332 | -0.050354 | -0.054931 | 0.10529 | 9.4986 | 2.0416 | 2.1652 | 2.092 | 2.2156 | 10.4416 | 122.2778 | 9.549 | 122.2824 | 122.2504 | 122.1222 | 122.113 | 122.0718 | -122.2641 | -122.1771 | 122.1405 | 122.2321 | 39.2441 | 37.5641
1679.3125 | 122.3465 | -54.7577 | 67.6712 | -0.13451 | 0.088284 | 0.077902 | 0.069635 | -0.0013672 | 0.010497 | 0.073832 | -0.073242 | 0.030258 | 0.077411 | 0.073743 | -0.0078272 | 0.025887 | 0.011645 | -15.4312 | 66.9983 | -55.3207 | 66.8106 | -39.4684 | -53.5858 | 18.306 | -17.5415 | 67.1585 | -55.0186 | 66.9342 | -45.7672 | -53.0136 | -52.6154 | -0.56305 | -0.67291 | -0.8606 | 15.2893 | 73.0637 | 1.1719 | 73.6267 | 1.7349 | -0.26093 | -0.5127 | -0.737 | 8.9905 | 2.1423 | 1.7441 | 2.4033 | 2.005 | 15.8524 | 122.1313 | 9.2514 | 121.9528 | 122.319 | 122.1771 | 121.756 | 121.9162 | -122.9919 | -122.6898 | 121.5683 | 121.6919 | 39.3265 | 37.2162
1680.3125 | 122.4518 | -51.7593 | 70.4819 | -0.14977 | 0.069272 | 0.07662 | 0.070917 | -0.0015808 | 0.012847 | 0.056102 | -0.027466 | 0.025772 | 0.077197 | 0.072247 | -0.008468 | 0.022683 | 0.0092948 | -12.7396 | 70.5185 | -51.796 | 68.9667 | -40.8829 | -51.0269 | -32.579 | -14.8361 | 69.6487 | -52.3819 | 70.3812 | -42.3203 | -49.5529 | -49.5483 | -0.036621 | 0.036621 | -1.5152 | 10.8765 | 19.1803 | 0.73242 | 19.2169 | 0.76904 | -0.62256 | -0.83313 | -0.10071 | 9.4391 | 2.211 | 2.2064 | 2.8336 | 2.829 | 10.9131 | 120.7626 | 10.0616 | 122.7631 | 122.3145 | 122.0306 | 122.2778 | 121.4081 | -122.2778 | -122.8638 | 120.726 | 122.1405 | 39.0198 | 36.9232
1681.3125 | 122.5067 | -61.0977 | 61.0153 | -0.14214 | 0.12375 | 0.086447 | 0.060022 | -0.0011536 | -0.0044562 | 0.10032 | -8.6e-08 | 0.029617 | 0.077411 | 0.073102 | -0.010391 | 0.025032 | 0.010149 | 9.9884 | 60.9879 | -61.2122 | 61.0428 | -41.7114 | 38.942 | 60.6995 | -23.5107 | 60.9329 | -61.1618 | 61.1252 | -51.5076 | -58.8409 | -59.0103 | -0.11444 | -0.027466 | 0.027466 | 19.3863 | 121.7972 | 100.0397 | 121.9116 | 100.1541 | -0.064087 | -0.082398 | 0.10986 | 9.5901 | 2.0874 | 2.2568 | 2.1515 | 2.3209 | 19.5007 | 122.2549 | 9.6542 | 122.287 | 122.2 | 122.0947 | 122.0856 | 122.0306 | -122.2275 | -122.1771 | 122.1405 | 122.2229 | 71.0861 | 37.587
1682.3125 | 122.5204 | -61.0382 | 61.0886 | -0.15739 | 0.1246 | 0.084097 | 0.06109 | 0.0014098 | -0.0027472 | 0.10075 | -0.030517 | 0.029617 | 0.077411 | 0.076092 | -0.010177 | 0.022042 | 0.010363 | 10.0388 | 61.0291 | -61.1664 | 61.116 | -41.5604 | 38.9465 | 61.1893 | -23.4467 | 61.0016 | -61.0931 | 61.2122 | -51.4755 | -58.8043 | -58.9325 | -0.12817 | -0.059509 | 0.027466 | 19.4778 | 122.2275 | 99.9847 | 122.3557 | 100.1129 | -0.054932 | -0.086975 | 0.1236 | 9.5627 | 2.1057 | 2.2339 | 2.1606 | 2.2888 | 19.606 | 122.2824 | 9.6176 | 122.3053 | 122.1954 | 122.0947 | 122.0673 | 122.0398 | -122.2549 | -122.1817 | 122.1542 | 122.2504 | 71.077 | 37.5916
1683.3125 | 122.5021 | -61.1481 | 60.9879 | -0.20317 | 0.12353 | 0.083456 | 0.059808 | -0.0035034 | -0.005097 | 0.10331 | -0.0030517 | 0.027267 | 0.076129 | 0.066479 | -0.0074 | 0.025673 | 0.010363 | 9.9106 | 60.9146 | -61.3037 | 60.9741 | -41.6794 | 38.9511 | 61.0611 | -23.7076 | 60.9009 | -61.1938 | 61.0794 | -51.6174 | -58.9417 | -59.0561 | -0.15564 | -0.073242 | -0.013733 | 19.4687 | 122.2092 | 100.0992 | 122.3648 | 100.2548 | -0.045777 | -0.086975 | 0.091553 | 9.5306 | 2.092 | 2.2064 | 2.1378 | 2.2522 | 19.6243 | 122.2778 | 9.5764 | 122.2733 | 122.2183 | 122.0947 | 122.0627 | 122.049 | -122.2916 | -122.1817 | 122.1222 | 122.2275 | 71.0587 | 37.4405
1684.3125 | 122.4884 | -60.9879 | 61.1389 | -0.20317 | 0.12268 | 0.084311 | 0.063012 | 0.0018372 | -0.00232 | 0.10096 | -0.0091553 | 0.02919 | 0.077197 | 0.070966 | -0.009109 | 0.023964 | 0.010576 | 10.025 | 61.0794 | -61.1389 | 61.1526 | -41.5329 | 39.0335 | 61.2396 | -23.616 | 61.0565 | -61.0428 | 61.2579 | -51.4801 | -58.7723 | -58.8821 | -0.15106 | -0.059509 | 0.013733 | 19.455 | 122.2275 | 100.0214 | 122.3785 | 100.1724 | -0.054932 | -0.082397 | 0.11902 | 9.5078 | 2.1057 | 2.2156 | 2.1606 | 2.2705 | 19.606 | 122.2916 | 9.5627 | 122.3007 | 122.2183 | 122.0993 | 122.0673 | 122.0444 | -122.2778 | -122.1817 | 122.1405 | 122.2458 | 71.0129 | 37.3718
1685.3125 | 122.612 | -61.203 | 60.9924 | -0.17265 | 0.12033 | 0.084097 | 0.063867 | -0.0015808 | -0.0038154 | 0.10331 | -0.012207 | 0.027908 | 0.07976 | 0.06947 | -0.0099634 | 0.022469 | 0.010576 | 9.7687 | 60.8734 | -61.3541 | 60.9421 | -41.7297 | 38.9145 | 61.0245 | -23.9227 | 60.8185 | -61.2167 | 61.0382 | -51.6953 | -58.9783 | -59.2575 | -0.15106 | -0.11902 | -0.050354 | 19.4733 | 122.2275 | 100.1175 | 122.3785 | 100.2686 | -0.013733 | -0.17395 | 0.045776 | 9.5078 | 1.9455 | 2.2247 | 1.9592 | 2.2385 | 19.6243 | 122.2961 | 9.5215 | 122.2549 | 122.2275 | 122.0352 | 122.0764 | 122.0215 | -122.3465 | -122.2092 | 122.1451 | 122.2412 | 70.9717 | 37.2803
1686.3125 | 122.3877 | -61.1389 | 61.0291 | -0.16502 | 0.11712 | 0.085806 | 0.06878 | 0.0014098 | -0.004029 | 0.10203 | -0.036621 | 0.028121 | 0.078692 | 0.07182 | -0.0086816 | 0.022469 | 0.0069448 | 9.8328 | 60.965 | -61.2808 | 60.9833 | -41.6794 | 38.9328 | 61.0519 | -24.0463 | 60.9375 | -61.1755 | 61.0382 | -51.7273 | -58.9874 | -59.1019 | -0.14191 | -0.064087 | -0.045777 | 19.4595 | 122.1909 | 100.0717 | 122.3328 | 100.2136 | -0.036621 | -0.091553 | 0.009155 | 9.4116 | 2.037 | 2.1515 | 2.0737 | 2.1881 | 19.6014 | 122.2641 | 9.4482 | 122.2137 | 122.2458 | 122.113 | 122.1039 | 122.0764 | -122.3099 | -122.2046 | 122.1222 | 122.1771 | 70.9717 | 37.0926
1687.3125 | 122.4335 | -61.4319 | 60.6812 | -0.20317 | 0.11413 | 0.084738 | 0.068994 | -0.0024354 | -0.0042426 | 0.10203 | -0.015259 | 0.027694 | 0.078265 | 0.06947 | -0.012313 | 0.024178 | 0.006304 | 9.5581 | 60.6674 | -61.5326 | 60.759 | -41.8579 | 38.7863 | 60.8322 | -24.2935 | 60.6445 | -61.4227 | 60.8597 | -51.6403 | -59.4589 | -59.523 | -0.10071 | -0.013733 | 0.07782 | 19.574 | 122.2641 | 100.2182 | 122.3648 | 100.3189 | 0.009156 | -0.036621 | 0.17853 | 9.7916 | 1.9089 | 1.973 | 1.8997 | 1.9638 | 19.6747 | 122.2916 | 9.7824 | 122.2824 | 122.2 | 122.0673 | 122.0993 | 122.0764 | -122.2137 | -122.1039 | 122.1909 | 122.2916 | 70.99 | 37.1384
1688.3125 | 122.4426 | -61.3174 | 60.8185 | -0.21843 | 0.11136 | 0.08367 | 0.071344 | 0.0016236 | -0.0038154 | 0.10139 | -0.01831 | 0.028762 | 0.078906 | 0.069684 | -0.009109 | 0.025246 | 0.0095084 | 9.5993 | 60.7773 | -61.4456 | 60.8322 | -41.8671 | 38.8092 | 60.8963 | -24.3484 | 60.7636 | -61.3358 | 60.8917 | -51.8509 | -59.1202 | -59.2117 | -0.12817 | -0.041198 | 0.013733 | 19.4504 | 122.2137 | 100.1266 | 122.3419 | 100.2548 | -0.01831 | -0.054931 | 0.073243 | 9.4666 | 2.1057 | 2.1973 | 2.124 | 2.2156 | 19.5786 | 122.2778 | 9.4849 | 122.2275 | 122.2229 | 122.0993 | 122.0947 | 122.081 | -122.2641 | -122.1542 | 122.1497 | 122.2092 | 70.9167 | 36.969
1689.3125 | 122.3877 | -61.4777 | 60.6903 | -0.16502 | 0.11306 | 0.084952 | 0.074975 | 0.0022644 | -0.004029 | 0.10374 | -0.15259 | 0.028335 | 0.078265 | 0.07887 | -0.0078272 | 0.026314 | 0.009722 | 9.407 | 60.6079 | -61.6241 | 60.6216 | -41.9952 | 38.6215 | 60.6857 | -24.6094 | 60.6354 | -61.5417 | 60.6857 | -52.0844 | -59.3857 | -59.4498 | -0.14649 | -0.082398 | -0.068665 | 19.4824 | 122.1634 | 100.0992 | 122.3099 | 100.2457 | -0.064087 | -0.054932 | -0.004578 | 9.3933 | 2.0279 | 2.092 | 2.092 | 2.1561 | 19.6289 | 122.2458 | 9.4574 | 122.2275 | 122.2321 | 122.1771 | 122.0856 | 122.113 | -122.3145 | -122.2321 | 122.0993 | 122.1634 | 70.8847 | 36.8683
1690.3125 | 122.4609 | -61.4182 | 60.7224 | -0.2108 | 0.10986 | 0.08602 | 0.073266 | -0.0013672 | -0.005097 | 0.099681 | -0.015259 | 0.028335 | 0.080188 | 0.075452 | -0.0082544 | 0.024178 | 0.0092948 | 9.3658 | 60.6766 | -61.5372 | 60.7178 | -41.8808 | 38.7039 | 60.8093 | -24.4308 | 60.6262 | -61.4456 | 60.791 | -51.947 | -59.2209 | -59.3308 | -0.11902 | -0.045776 | -0.004578 | 19.5374 | 122.2275 | 100.1221 | 122.3465 | 100.2411 | -0.027466 | -0.09613 | 0.068665 | 9.4711 | 2.0874 | 2.1973 | 2.1149 | 2.2247 | 19.6564 | 122.2549 | 9.4986 | 122.2366 | 122.2137 | 122.0718 | 122.0947 | 122.0444 | -122.2595 | -122.168 | 122.1359 | 122.2092 | 70.784 | 36.9873
1691.3125 | 122.4335 | -61.9446 | 60.2234 | -0.15739 | 0.1152 | 0.090933 | 0.07583 | 0.00076902 | -0.0046698 | 0.10438 | -0.021362 | 0.027053 | 0.078051 | 0.073956 | -0.006759 | 0.022683 | 0.009722 | 8.9493 | 60.1501 | -62.0316 | 60.26 | -34.6848 | 38.2462 | 60.2646 | -24.9435 | 60.1501 | -61.9537 | 60.2371 | -52.5192 | -59.7748 | -59.8343 | -0.086975 | -0.073243 | 0.036621 | 27.2598 | 122.2092 | 100.1907 | 122.2961 | 100.2777 | -0.009155 | -0.073243 | 0.013733 | 9.4254 | 2.1103 | 2.1698 | 2.1194 | 2.179 | 27.3468 | 122.2916 | 9.4345 | 122.1909 | 122.1817 | 122.1039 | 122.0947 | 122.0947 | -122.2549 | -122.1771 | 122.2046 | 122.1817 | 70.8939 | 37.001
1692.3125 | 122.4426 | -65.6479 | 56.4926 | -0.24132 | 0.15387 | 0.14626 | 0.093988 | -0.004358 | -0.0063788 | 0.098826 | -0.024414 | 0.026626 | 0.080829 | 0.074597 | -0.0080408 | 0.024392 | 0.013994 | 7.0541 | 56.4102 | -65.7898 | 56.4926 | 53.4576 | 35.5911 | 56.5475 | -28.6377 | 56.3965 | -65.6754 | 56.5292 | -56.1768 | -63.4506 | -63.5422 | -0.14191 | -0.082398 | 0 | 119.1055 | 122.1954 | 101.239 | 122.3373 | 101.3809 | -0.027466 | -0.096131 | 0.036621 | 9.4711 | 2.1057 | 2.1973 | 2.1332 | 2.2247 | 119.2474 | 122.2824 | 9.4986 | 122.2046 | 122.2 | 122.0718 | 122.0581 | 122.0444 | -122.2824 | -122.168 | 122.1405 | 122.1771 | 72.702 | 37.0102
1693.3125 | 122.3557 | -65.744 | 56.4468 | -0.33287 | 0.15216 | 0.14605 | 0.098688 | -0.0015808 | -0.0048834 | 0.10118 | -0.073242 | 0.02919 | 0.078479 | 0.071393 | -0.0059046 | 0.025887 | 0.0092948 | 6.9168 | 56.4011 | -65.8859 | 56.3187 | 54.7577 | 35.4492 | 56.3919 | -28.9627 | 56.3919 | -65.7532 | 56.3828 | -56.337 | -63.6246 | -63.6887 | -0.14191 | -0.045776 | -0.12817 | 120.5017 | 122.1359 | 101.1932 | 122.2778 | 101.3351 | -0.009155 | -0.054931 | -0.064087 | 9.407 | 2.0554 | 2.1194 | 2.0645 | 2.1286 | 120.6436 | 122.2046 | 9.4162 | 122.1359 | 122.287 | 122.1451 | 122.1451 | 122.1359 | -122.3328 | -122.2 | 122.0627 | 122.1268 | 72.6608 | 36.7813
1694.3125 | 122.3419 | -65.9088 | 56.282 | -0.26421 | 0.14938 | 0.14861 | 0.10018 | -0.00051278 | -0.0027472 | 0.10118 | -0.045776 | 0.030898 | 0.081042 | 0.078229 | -0.0076136 | 0.025246 | 0.0075858 | 6.6513 | 56.2225 | -66.0416 | 56.1996 | 55.7144 | 35.0464 | 56.4651 | -29.3747 | 56.218 | -65.9042 | 56.2317 | -56.5704 | -63.8535 | -63.8489 | -0.13275 | -0.059509 | -0.082397 | 121.6232 | 122.374 | 100.9552 | 122.5067 | 101.088 | 0.004577 | -0.064086 | -0.050354 | 9.3384 | 2.0599 | 2.0554 | 2.0554 | 2.0508 | 121.756 | 122.2412 | 9.3338 | 122.1359 | 122.2641 | 122.1222 | 122.1313 | 122.1268 | -122.3236 | -122.1863 | 122.1085 | 122.1405 | 72.5601 | 36.5341
1695.3125 | 122.3694 | -65.8035 | 56.3507 | -0.23369 | 0.14831 | 0.1484 | 0.10061 | 0.0020508 | -0.004029 | 0.10823 | -0.021362 | 0.02919 | 0.079333 | 0.072461 | -0.0076136 | 0.02546 | 0.012926 | 6.7703 | 56.2592 | -65.9134 | 56.3141 | 56.3736 | 35.3897 | 56.3736 | -29.2374 | 56.2775 | -65.8173 | 56.3507 | -56.3644 | -63.6475 | -63.7253 | -0.10986 | -0.091553 | -0.036621 | 122.1771 | 122.1771 | 101.1932 | 122.287 | 101.3031 | -0.013733 | -0.073242 | 0 | 9.4391 | 2.0782 | 2.1561 | 2.092 | 2.1698 | 122.287 | 122.2275 | 9.4528 | 122.168 | 122.1725 | 122.0947 | 122.0627 | 122.081 | -122.2641 | -122.168 | 122.1176 | 122.1542 | 72.5739 | 36.5662
1696.3125 | 122.3602 | -65.9225 | 56.25 | -0.23369 | 0.14447 | 0.14626 | 0.10296 | 0.0033324 | -0.005738 | 0.09904 | -0.076294 | 0.030044 | 0.079333 | 0.075238 | -0.0071864 | 0.026528 | 0.0095084 | 6.4774 | 56.1951 | -66.037 | 56.0989 | 56.1493 | 35.0739 | 56.1996 | -29.48 | 56.1768 | -65.9683 | 56.2042 | -56.5613 | -63.8168 | -63.8763 | -0.11444 | -0.054932 | -0.15106 | 122.0718 | 122.1222 | 100.9964 | 122.2366 | 101.1108 | -0.045777 | -0.073242 | -0.045776 | 9.3613 | 2.0462 | 2.1057 | 2.092 | 2.1515 | 122.1863 | 122.1359 | 9.407 | 122.1725 | 122.2321 | 122.1451 | 122.1176 | 122.0993 | -122.287 | -122.2183 | 122.0215 | 122.1268 | 72.3999 | 36.4426
1697.3125 | 122.3145 | -65.8813 | 56.3141 | -0.20317 | 0.14575 | 0.14818 | 0.10146 | 0.0014098 | -0.00039736 | 0.10246 | -0.057983 | 0.02684 | 0.078906 | 0.068616 | -0.006759 | 0.025032 | 0.0075858 | 6.6055 | 56.2958 | -65.9592 | 56.0577 | 56.2775 | 35.257 | 56.2729 | -29.5303 | 56.2866 | -65.863 | 56.2683 | -56.4789 | -63.7482 | -63.7939 | -0.077819 | -0.018311 | -0.25635 | 122.1588 | 122.1542 | 101.1383 | 122.2321 | 101.2161 | 0.018311 | -0.027466 | -0.045776 | 9.4025 | 2.0874 | 2.1332 | 2.0691 | 2.1149 | 122.2366 | 122.0169 | 9.3842 | 122.1313 | 122.2549 | 122.1497 | 122.1771 | 122.168 | -122.2733 | -122.1771 | 121.9391 | 122.1497 | 72.4869 | 36.351
1698.3125 | 122.3694 | -65.9454 | 56.2088 | -0.22606 | 0.14447 | 0.14776 | 0.10531 | 0.0022644 | -0.003388 | 0.10374 | -0.073242 | 0.029403 | 0.080401 | 0.074383 | -0.0082544 | 0.024392 | 0.011217 | 6.4362 | 56.1768 | -66.0645 | 56.0898 | 56.1493 | 35.0098 | 56.1722 | -29.7501 | 56.1676 | -65.9775 | 56.1951 | -56.575 | -63.8168 | -63.8535 | -0.11902 | -0.032043 | -0.11902 | 122.0947 | 122.1176 | 100.9552 | 122.2366 | 101.0742 | -0.032043 | -0.041198 | -0.013733 | 9.3704 | 2.092 | 2.1286 | 2.124 | 2.1606 | 122.2137 | 122.1542 | 9.4025 | 122.1725 | 122.2412 | 122.1451 | 122.1222 | 122.113 | -122.2733 | -122.1863 | 122.0352 | 122.1405 | 72.3816 | 36.1954
1699.3125 | 122.3145 | -65.9958 | 56.1813 | -0.25658 | 0.14383 | 0.14797 | 0.10638 | 0.0035462 | -0.0025336 | 0.10331 | -0.097656 | 0.030258 | 0.078906 | 0.072034 | -0.0069726 | 0.025032 | 0.012499 | 6.2119 | 56.131 | -66.1194 | 56.044 | 56.0761 | 34.7717 | 56.1081 | -29.8828 | 56.0989 | -66.0278 | 56.1401 | -56.7169 | -63.9542 | -63.9496 | -0.1236 | -0.050354 | -0.13733 | 122.0718 | 122.1039 | 100.7675 | 122.2275 | 100.8911 | -0.032043 | -0.082397 | -0.041198 | 9.2789 | 2.0462 | 2.0416 | 2.0782 | 2.0737 | 122.1954 | 122.1634 | 9.3109 | 122.168 | 122.2504 | 122.1268 | 122.1268 | 122.0947 | -122.3007 | -122.2092 | 122.0398 | 122.1359 | 72.2076 | 36.113
1700.3125 | 122.3602 | -65.8905 | 56.2271 | -0.22606 | 0.14361 | 0.14776 | 0.10702 | 0.0046142 | -0.0046698 | 0.10545 | -0.061035 | 0.029617 | 0.078692 | 0.071179 | -0.008468 | 0.025673 | 0.014635 | 6.3583 | 56.2088 | -66.0233 | 56.1539 | 56.2317 | 34.9411 | 56.2317 | -29.6997 | 56.218 | -65.8997 | 56.2729 | -56.4697 | -63.7482 | -63.7756 | -0.13275 | -0.018311 | -0.073242 | 122.1222 | 122.1222 | 100.8316 | 122.2549 | 100.9644 | -0.009155 | -0.009155 | 0.045776 | 9.4208 | 2.1149 | 2.1423 | 2.124 | 2.1515 | 122.2549 | 122.1771 | 9.4299 | 122.1725 | 122.2321 | 122.1176 | 122.0993 | 122.1085 | -122.2504 | -122.1268 | 122.0444 | 122.1634 | 72.2488 | 36.1908
1701.3125 | 122.3602 | -66.0095 | 56.1493 | -0.27184 | 0.14212 | 0.14733 | 0.10681 | -0.0015808 | -0.0044562 | 0.098826 | -0.048828 | 0.031753 | 0.078906 | 0.068616 | -0.0080408 | 0.02546 | 0.011645 | 6.1386 | 56.1172 | -66.1102 | 56.0577 | 56.131 | 34.6939 | 56.131 | -29.8599 | 56.0852 | -66.0461 | 56.1539 | -56.5887 | -63.8992 | -63.9175 | -0.10071 | -0.032043 | -0.091553 | 122.1405 | 122.1405 | 100.7034 | 122.2412 | 100.8041 | -0.036622 | -0.064087 | 0.004578 | 9.4208 | 2.092 | 2.1103 | 2.1286 | 2.1469 | 122.2412 | 122.168 | 9.4574 | 122.2 | 122.2275 | 122.1313 | 122.1268 | 122.0947 | -122.2595 | -122.1954 | 122.0673 | 122.1634 | 72.1481 | 36.1496
1702.3125 | 122.3282 | -66.0278 | 56.1264 | -0.24132 | 0.14084 | 0.14455 | 0.10424 | -0.0022218 | -0.0059516 | 0.09904 | -0.045776 | 0.02919 | 0.078906 | 0.072888 | -0.0071864 | 0.023964 | 0.006304 | 6.0791 | 56.0761 | -66.1423 | 55.9891 | 56.0577 | 34.6436 | 56.0761 | -30.0476 | 56.0532 | -66.0553 | 56.0806 | -56.6071 | -63.945 | -63.9175 | -0.11444 | -0.050354 | -0.13733 | 122.0856 | 122.1039 | 100.6714 | 122.2183 | 100.7858 | -0.027466 | -0.073242 | -0.045777 | 9.4208 | 2.1103 | 2.0828 | 2.1378 | 2.1103 | 122.2 | 122.1313 | 9.4482 | 122.1359 | 122.2183 | 122.1085 | 122.1039 | 122.081 | -122.2687 | -122.1817 | 122.0169 | 122.1085 | 72.1069 | 35.9802
1703.3125 | 122.3969 | -66.0461 | 56.0898 | -0.24132 | 0.14041 | 0.14712 | 0.10809 | -0.00051278 | -0.0061652 | 0.1016 | -0.061035 | 0.027694 | 0.080829 | 0.077588 | -0.0093226 | 0.026101 | 0.0075858 | 5.9784 | 56.0257 | -66.188 | 55.9937 | 56.0898 | 34.639 | 56.0623 | -30.0613 | 56.0074 | -66.0965 | 56.1081 | -56.7261 | -64.0411 | -63.9084 | -0.14191 | -0.064087 | -0.096131 | 122.1359 | 122.1085 | 100.6851 | 122.2504 | 100.827 | -0.050354 | -0.082398 | 0.01831 | 9.3201 | 2.1378 | 2.005 | 2.1881 | 2.0554 | 122.2778 | 122.1817 | 9.3704 | 122.2046 | 122.2137 | 122.1039 | 122.0718 | 122.0535 | -122.2778 | -122.1863 | 122.0398 | 122.1542 | 72.0245 | 35.9848
1704.3125 | 122.3282 | -65.95 | 56.2088 | -0.30235 | 0.1387 | 0.14818 | 0.10745 | 0.00012822 | -0.0031744 | 0.10374 | -0.073242 | 0.028335 | 0.080615 | 0.073315 | -0.0063318 | 0.023751 | 0.013354 | 5.8731 | 56.163 | -66.0599 | 56.1264 | 56.2042 | 34.5703 | 56.1859 | -30.0018 | 56.131 | -65.95 | 56.1859 | -56.4514 | -63.8718 | -63.8077 | -0.10986 | -0.045776 | -0.082397 | 122.1542 | 122.1359 | 100.5203 | 122.2458 | 100.6302 | 0 | -0.07782 | -0.022888 | 9.4986 | 2.1423 | 2.0782 | 2.1423 | 2.0782 | 122.2641 | 122.1863 | 9.4986 | 122.1359 | 122.2229 | 122.081 | 122.113 | 122.081 | -122.2687 | -122.1588 | 122.0764 | 122.1359 | 71.8231 | 35.9482
1705.3125 | 122.3648 | -66.0416 | 56.0898 | -0.26421 | 0.14105 | 0.1469 | 0.10894 | 0.0016236 | -0.0063788 | 0.10118 | -0.024414 | 0.029403 | 0.079974 | 0.072888 | -0.0097498 | 0.024819 | 0.012072 | 5.6808 | 56.0486 | -66.1743 | 56.0577 | 55.9662 | 34.2819 | 56.1905 | -30.1117 | 56.0394 | -66.0828 | 56.1127 | -56.4651 | -63.9542 | -63.9038 | -0.13275 | -0.041199 | -0.032044 | 122.0078 | 122.2321 | 100.3235 | 122.3648 | 100.4562 | -0.041199 | -0.050354 | 0.022888 | 9.5764 | 2.1378 | 2.0874 | 2.179 | 2.1286 | 122.1405 | 122.2321 | 9.6176 | 122.1954 | 122.2229 | 122.1222 | 122.0901 | 122.081 | -122.2641 | -122.1725 | 122.0993 | 122.1542 | 71.7224 | 35.9299
1706.3125 | 122.319 | -65.9958 | 56.1722 | -0.27184 | 0.14019 | 0.14882 | 0.10894 | 0.0029052 | -0.0044562 | 0.10054 | -0.054932 | 0.033035 | 0.078906 | 0.075879 | -0.0076136 | 0.023964 | 0.014635 | 5.5206 | 56.1035 | -66.1148 | 56.0623 | 56.1218 | 34.1034 | 56.1127 | -30.1437 | 56.1127 | -66.0004 | 56.1356 | -56.4148 | -63.9587 | -63.8535 | -0.11902 | -0.068664 | -0.10986 | 122.1176 | 122.1085 | 100.0992 | 122.2275 | 100.2182 | -0.004577 | -0.059509 | -0.036621 | 9.581 | 2.1423 | 2.037 | 2.1469 | 2.0416 | 122.2366 | 122.1771 | 9.5856 | 122.1359 | 122.2183 | 122.113 | 122.0993 | 122.1085 | -122.287 | -122.1725 | 122.0581 | 122.1313 | 71.5164 | 35.8521
1707.3125 | 122.3053 | -66.156 | 55.9845 | -0.22606 | 0.14254 | 0.14754 | 0.10851 | 0.0020508 | -0.0038154 | 0.1031 | -0.057983 | 0.030044 | 0.080829 | 0.074597 | -0.0078272 | 0.022683 | 0.011217 | 5.3558 | 55.9433 | -66.2659 | 55.8838 | 55.9479 | 33.9706 | 55.925 | -30.3452 | 55.925 | -66.1926 | 55.9387 | -56.5338 | -64.1418 | -63.9999 | -0.10986 | -0.041199 | -0.10071 | 122.1039 | 122.081 | 100.1266 | 122.1909 | 100.2365 | -0.036621 | -0.059509 | -0.045776 | 9.6222 | 2.1561 | 2.0142 | 2.1927 | 2.0508 | 122.2137 | 122.1497 | 9.6588 | 122.1313 | 122.2092 | 122.1176 | 122.0993 | 122.081 | -122.2504 | -122.1771 | 122.0398 | 122.0947 | 71.5118 | 35.8109
1708.3125 | 122.3053 | -66.037 | 56.1081 | -0.23369 | 0.14126 | 0.14925 | 0.1098 | -0.0013672 | -0.0044562 | 0.10331 | -0.048828 | 0.029617 | 0.084247 | 0.072034 | -0.009109 | 0.023751 | 0.0067312 | 5.2734 | 56.0532 | -66.1743 | 55.9113 | 55.9616 | 33.8562 | 56.0028 | -30.6061 | 55.9891 | -66.1285 | 56.0669 | -56.4194 | -64.0732 | -63.9267 | -0.13733 | -0.054931 | -0.19684 | 121.9986 | 122.0398 | 99.8932 | 122.1771 | 100.0305 | -0.091553 | -0.11902 | -0.041198 | 9.6176 | 2.1103 | 1.9638 | 2.2018 | 2.0554 | 122.1359 | 122.0856 | 9.7092 | 122.1954 | 122.2275 | 122.1176 | 122.0901 | 122.0261 | -122.2824 | -122.2366 | 121.9482 | 122.1039 | 71.3104 | 35.4309
1709.3125 | 122.4243 | -65.918 | 56.1493 | -0.24132 | 0.14084 | 0.14754 | 0.10851 | 0.0014098 | -0.0031744 | 0.10054 | -0.0061035 | 0.028549 | 0.07976 | 0.069897 | -0.0069726 | 0.024392 | 0.012285 | 5.452 | 56.1172 | -66.0782 | 56.1401 | 56.2042 | 34.0668 | 56.1676 | -30.13 | 56.0806 | -65.9683 | 56.2363 | -56.1768 | -63.8535 | -63.6932 | -0.16022 | -0.032043 | -0.009155 | 122.1222 | 122.0856 | 99.9847 | 122.2458 | 100.145 | -0.050354 | -0.068665 | 0.086975 | 9.7412 | 2.2247 | 2.0645 | 2.2751 | 2.1149 | 122.2824 | 122.2183 | 9.7916 | 122.2046 | 122.1954 | 122.0489 | 122.0352 | 121.9986 | -122.2275 | -122.1176 | 122.0581 | 122.1542 | 71.3699 | 35.788
1710.3125 | 122.2687 | -66.1285 | 56.0211 | -0.25658 | 0.14254 | 0.14583 | 0.10937 | 0.00098262 | -0.003388 | 0.10374 | -0.07019 | 0.028976 | 0.076983 | 0.071393 | -0.0069726 | 0.025673 | 0.012285 | 5.1956 | 55.9662 | -66.2704 | 55.8792 | 55.9204 | 33.7326 | 55.9525 | -30.3497 | 55.9662 | -66.1514 | 55.9433 | -56.4285 | -64.1739 | -63.9816 | -0.14191 | -0.054931 | -0.14191 | 122.0489 | 122.081 | 99.8611 | 122.2229 | 100.0031 | -0.022888 | -0.054931 | -0.07782 | 9.7 | 2.1469 | 1.9547 | 2.1698 | 1.9775 | 122.1909 | 122.1497 | 9.7229 | 122.0947 | 122.2366 | 122.1176 | 122.0947 | 122.0947 | -122.2916 | -122.1725 | 122.0078 | 122.0718 | 71.3242 | 35.7788
1711.3125 | 122.3419 | -66.1057 | 56.0623 | -0.27946 | 0.14233 | 0.14797 | 0.10659 | -0.0015808 | -0.0048834 | 0.10224 | -0.067139 | 0.031967 | 0.079547 | 0.073102 | -0.0078272 | 0.023323 | 0.015917 | 5.1865 | 55.9845 | -66.2521 | 55.8655 | 55.9067 | 33.8287 | 55.9296 | -30.3314 | 55.957 | -66.1514 | 55.9296 | -56.6071 | -63.8672 | -63.7299 | -0.14648 | -0.07782 | -0.19684 | 122.0123 | 122.0352 | 99.9344 | 122.1817 | 100.0809 | -0.045776 | -0.10529 | -0.13275 | 9.4986 | 2.3758 | 2.2385 | 2.4216 | 2.2842 | 122.1588 | 122.1176 | 9.5444 | 122.081 | 122.2366 | 122.1085 | 122.0901 | 122.0627 | -122.3145 | -122.2137 | 121.9711 | 122.0352 | 71.2921 | 35.7742
1712.3125 | 122.2778 | -59.1797 | 62.9974 | 0.071487 | 0.0060392 | -0.0066929 | -0.094 | 0.0014098 | -0.005097 | 0.00077334 | -0.054932 | 0.030471 | 0.076129 | 0.074597 | -0.0076136 | 0.025887 | 0.011645 | -1.0254 | -0.80109 | -1.0986 | -1.0757 | -1.0025 | -1.1032 | -1.03 | -23.5016 | 62.9517 | -59.1202 | 62.9883 | -49.2737 | -57.1381 | -56.9458 | 58.0811 | -63.7985 | -64.0732 | 58.1772 | 58.1497 | 58.0765 | 0.068665 | -0.004577 | 0.059509 | -0.045777 | -0.009156 | 9.906 | 2.2339 | 2.0416 | 2.1744 | 1.9821 | 0.096131 | 0.022888 | 9.8465 | 122.1085 | 0.29755 | 122.0718 | 58.3786 | 122.1313 | -64.0961 | -122.1176 | 58.1039 | 122.168 | 58.1543 | 35.6781
1713.3125 | 122.3328 | -59.1202 | 63.0295 | 0.018082 | 0.008389 | -0.0037021 | -0.09635 | 0.00055542 | -0.0036018 | -0.0060627 | -0.057983 | 0.031112 | 0.077411 | 0.073956 | -0.0076136 | 0.023751 | 0.012499 | -1.0986 | -0.89722 | -1.1719 | -1.1627 | -1.0757 | -1.181 | -1.0941 | -23.4283 | 62.9608 | -59.1156 | 63.0432 | -49.1867 | -57.1106 | -56.9183 | 57.9483 | -63.9267 | -64.1922 | 58.0444 | 58.0261 | 57.9391 | 0.07782 | -0.009155 | 0.004577 | -0.068665 | 0.013733 | 9.9335 | 2.2018 | 2.0096 | 2.1973 | 2.005 | 0.09613 | 0.009155 | 9.9289 | 122.1588 | 0.27466 | 122.0764 | 58.223 | 122.081 | -64.2014 | -122.1451 | 57.9575 | 122.1634 | 58.0215 | 35.6918
1714.3125 | 122.374 | -59.0927 | 63.0615 | 0.048599 | 0.0062528 | -0.0045567 | -0.098914 | -0.004358 | -0.0029608 | -0.0041401 | 0.088501 | 0.026626 | 0.07976 | 0.066907 | -0.009109 | 0.023537 | 0.011004 | -1.1124 | -0.94299 | -1.1856 | -1.1581 | -1.0529 | -1.149 | -1.0757 | -23.2544 | 63.0112 | -59.0515 | 63.0844 | -49.086 | -57.074 | -56.8634 | 57.9071 | -64.0045 | -64.2197 | 58.0399 | 58.017 | 57.9437 | 0.10986 | 0.036621 | 0.041198 | -0.050354 | 0.022889 | 10.0067 | 2.2293 | 2.0187 | 2.1881 | 1.9775 | 0.13275 | 0.027466 | 9.9655 | 122.1359 | 0.24262 | 122.0627 | 58.1497 | 122.1039 | -64.2471 | -122.113 | 57.9346 | 122.1771 | 57.9803 | 35.8383
1715.3125 | 122.3328 | -59.1339 | 63.089 | 0.071487 | 0.00668 | -0.0075473 | -0.093146 | 0.00098262 | -0.0044562 | -0.0013629 | -0.064087 | 0.030685 | 0.07976 | 0.06947 | -0.0097498 | 0.023537 | 0.016131 | -1.1444 | -0.95673 | -1.2589 | -1.2314 | -1.1536 | -1.2543 | -1.1719 | -23.4055 | 62.9929 | -59.1385 | 63.0386 | -49.0952 | -57.1518 | -56.9183 | 57.8751 | -64.0457 | -64.3204 | 57.9803 | 57.962 | 57.8796 | 0.086975 | 0.004578 | -0.004578 | -0.09613 | -0.050354 | 10.0388 | 2.2156 | 1.9821 | 2.2202 | 1.9867 | 0.10529 | 0.027466 | 10.0433 | 122.1771 | 0.30212 | 122.1313 | 58.1772 | 122.1268 | -64.3478 | -122.2275 | 57.9025 | 122.1725 | 57.9895 | 35.7285
1716.3125 | 122.4289 | -59.0561 | 63.0707 | 0.010452 | 0.0071072 | -0.0047703 | -0.095709 | 0.0022644 | -0.0044562 | -0.0020039 | -0.027466 | 0.029403 | 0.077838 | 0.072034 | -0.009109 | 0.021828 | 0.012072 | -1.1307 | -1.0025 | -1.2451 | -1.1765 | -1.0757 | -1.1993 | -1.1078 | -23.2819 | 63.0066 | -59.0881 | 63.1439 | -48.9487 | -57.0374 | -56.8039 | 57.811 | -64.0732 | -64.2471 | 57.9803 | 57.9483 | 57.8568 | 0.13733 | 0.045776 | -0.032044 | -0.064087 | 0.073242 | 10.1074 | 2.2522 | 2.0187 | 2.2842 | 2.0508 | 0.16937 | 0.068664 | 10.1395 | 122.2321 | 0.24262 | 122.0947 | 58.0536 | 122.0627 | -64.3158 | -122.1588 | 57.8796 | 122.2 | 57.9254 | 35.7742
1717.3125 | 122.4655 | -59.0012 | 63.1119 | 0.12489 | 0.0077482 | -0.0041293 | -0.095282 | -0.0011536 | -0.0014654 | -0.0015765 | -0.0061035 | 0.02919 | 0.077197 | 0.068616 | -0.0078272 | 0.022042 | 0.013354 | -1.1719 | -1.0941 | -1.3092 | -1.1719 | -1.0666 | -1.2131 | -1.1444 | -23.085 | 63.0249 | -59.0378 | 63.176 | -48.7885 | -56.9229 | -56.7352 | 57.692 | -64.2059 | -64.2838 | 57.9346 | 57.8568 | 57.7881 | 0.1648 | 0.09613 | -0.036621 | -0.086975 | 0.064087 | 10.2127 | 2.2659 | 2.0782 | 2.3026 | 2.1149 | 0.24262 | 0.13733 | 10.2493 | 122.2137 | 0.21515 | 122.0627 | 57.9071 | 122.0261 | -64.4211 | -122.1497 | 57.8293 | 122.1771 | 57.8293 | 35.9161
1718.3125 | 122.4518 | -58.9783 | 63.1485 | 0.056229 | 0.0077482 | -0.0054111 | -0.096564 | -0.00072638 | -0.0027472 | -0.00072206 | -0.0061035 | 0.028976 | 0.079333 | 0.073102 | -0.0097498 | 0.022896 | 0.014208 | -1.1902 | -1.0941 | -1.2772 | -1.1948 | -1.0849 | -1.2268 | -1.1444 | -23.1583 | 63.0478 | -59.0149 | 63.2217 | -48.7381 | -56.9641 | -56.7123 | 57.7011 | -64.2426 | -64.3433 | 57.8934 | 57.8339 | 57.7515 | 0.13275 | 0.050354 | -0.036622 | -0.10071 | 0.073242 | 10.2402 | 2.2659 | 2.0142 | 2.3026 | 2.0508 | 0.19226 | 0.082398 | 10.2768 | 122.2366 | 0.18311 | 122.0627 | 57.8842 | 122.0261 | -64.4257 | -122.1634 | 57.7835 | 122.2 | 57.7881 | 35.82
1719.3125 | 122.3923 | -59.0012 | 63.1714 | 0.086746 | 0.0075344 | -0.0058383 | -0.096778 | -0.0049988 | -0.0065924 | -0.0028583 | 0.024414 | 0.028549 | 0.079974 | 0.068829 | -0.011245 | 0.022683 | 0.012926 | -1.1444 | -1.0345 | -1.236 | -1.1581 | -1.0437 | -1.1444 | -1.1169 | -23.1949 | 63.1027 | -59.0103 | 63.176 | -48.6511 | -56.9916 | -56.7261 | 57.7652 | -64.2059 | -64.3295 | 57.9575 | 57.8842 | 57.8568 | 0.11902 | 0.091553 | -0.009155 | -0.068665 | 0.004577 | 10.35 | 2.2751 | 2.0096 | 2.2842 | 2.0187 | 0.19226 | 0.07782 | 10.3592 | 122.1863 | 0.20142 | 122.113 | 57.9666 | 122.1039 | -64.4073 | -122.1817 | 57.843 | 122.1771 | 57.8568 | 35.8063
1720.3125 | 122.4197 | -58.9645 | 63.1531 | 0.048599 | 0.0077482 | -0.0056247 | -0.097632 | -0.00093998 | -0.0031744 | -0.0034991 | -0.021362 | 0.030044 | 0.079974 | 0.066266 | -0.0082544 | 0.023964 | 0.011645 | -1.2039 | -1.0941 | -1.3092 | -1.2222 | -1.0895 | -1.2405 | -1.1673 | -23.1354 | 63.0753 | -59.0195 | 63.2217 | -48.5962 | -56.987 | -56.7078 | 57.6553 | -64.2471 | -64.3753 | 57.8751 | 57.7972 | 57.724 | 0.14191 | 0.068664 | -0.054931 | -0.07782 | 0.068665 | 10.3683 | 2.2568 | 1.9775 | 2.3117 | 2.0325 | 0.21973 | 0.086975 | 10.4233 | 122.2412 | 0.21515 | 122.0947 | 57.8705 | 122.0398 | -64.4623 | -122.1725 | 57.7423 | 122.1863 | 57.7606 | 35.8292
1721.3125 | 122.4747 | -58.96 | 63.1622 | -0.0048066 | 0.0081754 | -0.0047703 | -0.095282 | -0.00029898 | -0.0055244 | -0.0013629 | 0.012207 | 0.02983 | 0.079333 | 0.068402 | -0.008468 | 0.021828 | 0.015917 | -1.2405 | -1.0941 | -1.3 | -1.2451 | -1.1627 | -1.268 | -1.1993 | -23.2132 | 63.1073 | -59.0149 | 63.1989 | -48.5733 | -56.8634 | -56.5613 | 57.6599 | -64.2563 | -64.4073 | 57.7972 | 57.7606 | 57.692 | 0.10071 | 0.032044 | -0.054932 | -0.054931 | 0.036622 | 10.3867 | 2.3987 | 2.0966 | 2.4536 | 2.1515 | 0.13733 | 0.054932 | 10.4416 | 122.2137 | 0.20599 | 122.1222 | 57.8659 | 122.0673 | -64.4623 | -122.1771 | 57.7148 | 122.1588 | 57.7194 | 35.7468
1722.3125 | 122.4609 | -58.9417 | 63.1805 | 0.071487 | 0.010098 | -0.0043429 | -0.095069 | 0.00098262 | -0.004029 | -0.0037129 | -0.045776 | 0.028549 | 0.077197 | 0.066266 | -0.010818 | 0.024819 | 0.0069448 | -1.2314 | -1.1765 | -1.3412 | -1.2268 | -1.1444 | -1.2726 | -1.2039 | -23.0347 | 63.1027 | -58.9554 | 63.2767 | -48.4222 | -56.9504 | -56.6254 | 57.6004 | -64.357 | -64.4073 | 57.7972 | 57.7377 | 57.6691 | 0.13733 | 0.068665 | -0.013733 | -0.07782 | 0.09613 | 10.5194 | 2.3163 | 1.9913 | 2.33 | 2.005 | 0.19684 | 0.11444 | 10.5331 | 122.2321 | 0.1648 | 122.0581 | 57.7652 | 122.0444 | -64.5218 | -122.1359 | 57.7148 | 122.2183 | 57.7103 | 35.907
1723.3125 | 122.4747 | -59.7107 | 62.5351 | -0.042954 | 0.011166 | -0.0041293 | -0.095496 | 0.0022644 | -0.0038154 | -0.0011493 | -0.054932 | 0.068283 | 0.080615 | 0.073102 | -0.0071864 | 0.020974 | 0.053301 | -1.3962 | -1.236 | -1.3962 | -1.2817 | -0.96588 | -0.97961 | -0.8606 | -23.378 | 62.3383 | -59.7061 | 62.439 | -45.4834 | -57.5638 | 0.34332 | 58.3145 | -63.7711 | -63.8168 | 58.7448 | 58.8501 | 58.7311 | 0.53558 | 0.41657 | 0.004577 | -0.19684 | -0.09613 | 14.2273 | 60.054 | 2.1469 | 60.0494 | 2.1423 | 0.4303 | 0.11444 | 14.2227 | 122.1451 | 0.16022 | 122.0444 | 58.4747 | 122.0489 | -63.9313 | -122.2412 | 58.429 | 122.1497 | 58.3145 | 36.3327
1724.3125 | 122.5708 | -60.5576 | 61.5555 | 0.094376 | 0.0079618 | -0.0060519 | -0.095282 | 0.0039734 | -0.005738 | -0.0015765 | -0.31128 | 0.79695 | 0.082751 | 0.055798 | -0.012527 | 0.020119 | 0.77684 | -0.54932 | -0.48523 | -0.67291 | -0.5722 | -0.45319 | -0.5722 | -0.49439 | -23.8632 | 61.3541 | -60.5438 | 61.5372 | -41.391 | -58.342 | 61.5601 | 59.8846 | -62.0407 | -62.1277 | 60.1044 | 60.0632 | 59.9854 | 0.17853 | 0.10071 | 0.013733 | -0.20142 | -0.018311 | 19.1666 | 122.1176 | 2.2156 | 122.1039 | 2.2018 | 0.21973 | 0.10071 | 19.1528 | 122.081 | 0.18768 | 121.8979 | 60.0723 | 121.9116 | -62.2284 | -122.0993 | 59.9854 | 122.0947 | 60.0082 | 36.6943
1725.3125 | 122.4243 | -60.6125 | 61.5051 | 0.048599 | 0.0090298 | -0.0058383 | -0.095709 | -0.0013672 | -0.0038154 | -0.0032855 | -0.30518 | 0.79332 | 0.086169 | 0.061993 | -0.011459 | 0.020974 | 0.77001 | -0.60425 | -0.49439 | -0.70496 | -0.64545 | -0.56763 | -0.67291 | -0.60425 | -23.9044 | 61.3449 | -60.553 | 61.4502 | -41.3498 | -58.3878 | 61.5097 | 59.9075 | -61.9995 | -62.1506 | 60.0449 | 60.0082 | 59.9396 | 0.10071 | 0.032043 | 0.059509 | -0.16022 | -0.054932 | 19.2627 | 122.1222 | 2.2247 | 122.0627 | 2.1652 | 0.13733 | 0.059509 | 19.2032 | 122.0032 | 0.21057 | 121.8979 | 60.1181 | 121.9574 | -62.2101 | -122.0581 | 59.967 | 122.0627 | 60.0082 | 36.7081
1726.3125 | 122.3465 | -60.5988 | 61.4868 | 0.0028229 | 0.0079618 | -0.0073337 | -0.094855 | -0.0024354 | -0.0021064 | -0.0011493 | -0.32349 | 0.79268 | 0.082324 | 0.062848 | -0.011886 | 0.021614 | 0.77022 | -0.59509 | -0.48981 | -0.70953 | -0.63629 | -0.55847 | -0.67291 | -0.59509 | -24.0326 | 61.3174 | -60.5576 | 61.4502 | -41.2857 | -58.4885 | 61.4182 | 59.8892 | -61.9766 | -62.1231 | 60.0403 | 60.0037 | 59.9258 | 0.11444 | 0.036621 | 0.041199 | -0.16937 | -0.036621 | 19.313 | 122.0169 | 2.1103 | 121.9757 | 2.0691 | 0.15106 | 0.073242 | 19.2719 | 122.0078 | 0.21973 | 121.875 | 60.1089 | 121.9162 | -62.1963 | -122.0444 | 59.9625 | 122.0489 | 60.0037 | 36.5662
1727.3125 | 122.3785 | -60.5713 | 61.4731 | 0.010452 | 0.0081754 | -0.0064793 | -0.095282 | -0.0041444 | -0.004029 | -0.0022175 | -0.32959 | 0.78926 | 0.084887 | 0.066693 | -0.012954 | 0.022042 | 0.76595 | -0.60425 | -0.48065 | -0.70038 | -0.63171 | -0.54474 | -0.64087 | -0.5722 | -23.9319 | 61.3495 | -60.5301 | 61.4731 | -41.0568 | -58.4198 | 61.4502 | 59.8709 | -61.9537 | -62.1048 | 60.0266 | 59.9991 | 59.9304 | 0.12817 | 0.059509 | 0.041199 | -0.1236 | 0 | 19.5145 | 122.0215 | 2.1515 | 121.9803 | 2.1103 | 0.15564 | 0.068664 | 19.4733 | 122.0032 | 0.21973 | 121.8796 | 60.0906 | 121.9208 | -62.1735 | -122.0032 | 59.9396 | 122.0444 | 59.967 | 36.6394
1728.3125 | 122.3419 | -60.5621 | 61.4639 | 0.071487 | 0.008389 | -0.0054111 | -0.094855 | 0.0011962 | -0.0018928 | -0.0032855 | -0.32043 | 0.7852 | 0.083819 | 0.065625 | -0.0121 | 0.019905 | 0.76552 | -0.5722 | -0.49439 | -0.69122 | -0.62256 | -0.50812 | -0.6134 | -0.55389 | -23.9273 | 61.3449 | -60.5164 | 61.4822 | -40.892 | -58.3923 | 61.4502 | 59.8709 | -61.9583 | -62.0865 | 60.054 | 60.0082 | 59.9487 | 0.13733 | 0.07782 | 0.045777 | -0.11902 | 0.018311 | 19.6701 | 122.0123 | 2.1698 | 121.9666 | 2.124 | 0.18311 | 0.068664 | 19.6243 | 121.9986 | 0.19684 | 121.8613 | 60.0677 | 121.907 | -62.1552 | -121.9803 | 59.9396 | 122.0444 | 59.9899 | 36.6348
1729.3125 | 122.2687 | -60.5301 | 61.5097 | 0.14778 | 0.00668 | -0.0056247 | -0.094 | -0.0015808 | -0.0046698 | -0.0024311 | -0.4364 | 0.78349 | 0.086596 | 0.065411 | -0.013168 | 0.024178 | 0.75997 | -0.59052 | -0.44403 | -0.73242 | -0.65918 | -0.59509 | -0.67291 | -0.62714 | -24.0097 | 61.3953 | -60.5118 | 61.4548 | -40.8005 | -58.429 | 61.409 | 59.7977 | -61.9537 | -62.1689 | 59.935 | 59.903 | 59.8572 | 0.10529 | 0.059509 | 0.01831 | -0.11444 | -0.054932 | 19.7296 | 121.9391 | 2.1011 | 121.9208 | 2.0828 | 0.13733 | 0.073242 | 19.7113 | 121.9666 | 0.28839 | 121.907 | 60.0861 | 121.9254 | -62.2421 | -122.0215 | 59.8709 | 121.9849 | 59.9396 | 36.5204
1730.3125 | 122.3007 | -60.5484 | 61.496 | 0.079117 | 0.0079618 | -0.0079745 | -0.094855 | 0.0046142 | -0.0036018 | -0.0020039 | -0.31433 | 0.77965 | 0.085315 | 0.064343 | -0.0121 | 0.02311 | 0.76082 | -0.59967 | -0.51727 | -0.72327 | -0.6546 | -0.54932 | -0.66834 | -0.59052 | -23.9594 | 61.322 | -60.5026 | 61.4502 | -40.5396 | -58.3374 | 61.4273 | 59.8251 | -62.0132 | -62.1506 | 59.9991 | 59.9579 | 59.8801 | 0.13275 | 0.054932 | 0.045776 | -0.17395 | -0.045777 | 20.0088 | 121.9757 | 2.211 | 121.9299 | 2.1652 | 0.17395 | 0.068665 | 19.9631 | 121.9528 | 0.20599 | 121.8246 | 60.0311 | 121.8704 | -62.2192 | -121.9986 | 59.8938 | 121.9986 | 59.9487 | 36.5891
1731.3125 | 122.3465 | -61.9492 | 60.022 | 0.10963 | 0.0088162 | -0.0071201 | -0.096564 | -8.538e-05 | -0.0055244 | -0.0017903 | -0.35095 | 0.83989 | 0.14406 | 0.057935 | -0.011886 | 0.022255 | 0.75698 | 0.21973 | 0.23804 | 0.045776 | 0.14648 | 0.23346 | 0.12817 | 0.1831 | -23.5062 | 59.8846 | -61.9308 | 60.0677 | 58.4473 | -59.6603 | 59.9945 | 61.9949 | -59.7839 | -59.8755 | 62.1826 | 62.1323 | 62.0773 | 0.13733 | 0.082398 | 0.018311 | -0.13733 | 0.045776 | 120.3964 | 121.9437 | 2.2888 | 121.9254 | 2.2705 | 0.18768 | 0.10071 | 120.3781 | 121.9986 | 0.19226 | 121.8155 | 62.1872 | 121.8338 | -59.9762 | -121.9528 | 62.0956 | 122.0169 | 62.1689 | 38.443
1732.3125 | 122.3007 | -61.9904 | 59.9991 | 0.094376 | 0.0068936 | -0.0071201 | -0.097205 | 0.00012822 | -0.0042426 | -0.0037129 | -0.33569 | 0.83775 | 0.14449 | 0.058362 | -0.011245 | 0.023323 | 0.74928 | 0.41199 | 0.23804 | 0.032043 | 0.10986 | 0.21515 | 0.20142 | 0.20142 | -23.5107 | 59.8572 | -61.94 | 60.0311 | 60.0311 | -59.6375 | 59.9808 | 62.0224 | -59.761 | -59.8892 | 62.2055 | 62.1918 | 62.1918 | 0.16937 | 0.16937 | 0.050354 | -0.14191 | 0.032044 | 122.0215 | 121.9711 | 2.3529 | 121.9208 | 2.3026 | 0.18311 | 0.07782 | 121.9711 | 121.9711 | 0.20599 | 121.7972 | 62.2284 | 121.8475 | -59.967 | -121.9391 | 62.1002 | 122.0215 | 62.4023 | 38.4796
1733.3125 | 122.3465 | -61.9858 | 59.9945 | 0.071487 | 0.0060392 | -0.0054111 | -0.095282 | 0.002478 | -0.005097 | 0.0012005 | -0.3418 | 0.83412 | 0.14727 | 0.056866 | -0.011245 | 0.02311 | 0.75377 | 0.21973 | 0.21973 | 0.050354 | 0.15564 | 0.2655 | 0.16022 | 0.21515 | -23.5474 | 59.8114 | -61.9675 | 60.0174 | 60.0677 | -59.6146 | 59.9854 | 62.0361 | -59.7748 | -59.8389 | 62.2513 | 62.2009 | 62.146 | 0.16479 | 0.10986 | 0.018311 | -0.18311 | 0.022888 | 122.0535 | 121.9711 | 2.3712 | 121.9528 | 2.3529 | 0.21515 | 0.10529 | 122.0352 | 121.9849 | 0.16937 | 121.7789 | 62.2055 | 121.7972 | -59.9442 | -121.962 | 62.1414 | 122.0032 | 62.2055 | 38.4384
1734.3125 | 122.3053 | -61.9812 | 59.9945 | 0.04097 | 0.0096708 | -0.0062655 | -0.096778 | -8.538e-05 | -0.0042426 | -0.0026447 | -0.36011 | 0.83156 | 0.14556 | 0.063489 | -0.012954 | 0.022683 | 0.74736 | 0.2243 | 0.21057 | 0.022888 | 0.14648 | 0.24719 | 0.16937 | 0.19226 | -23.584 | 59.8618 | -61.9629 | 60.0128 | 60.0632 | -59.5917 | 59.9716 | 62.0041 | -59.7839 | -59.848 | 62.2284 | 62.1735 | 62.1506 | 0.16937 | 0.14649 | 0.01831 | -0.13275 | 0.01831 | 122.0444 | 121.9528 | 2.3895 | 121.9345 | 2.3712 | 0.2243 | 0.1236 | 122.0261 | 121.9757 | 0.18768 | 121.8246 | 62.1918 | 121.843 | -59.9716 | -121.9574 | 62.1277 | 121.994 | 62.2055 | 38.3972
1735.3125 | 122.1542 | -62.0361 | 60.0357 | 0.11726 | 0.0071072 | -0.0049839 | -0.092078 | 0.005896 | -0.003388 | -0.0024311 | -0.47302 | 0.83241 | 0.14556 | 0.06413 | -0.012313 | 0.026314 | 0.74309 | 0.16479 | 0.28381 | 0 | 0.045776 | 0.091553 | -0.032043 | 0.045776 | -23.9319 | 59.8572 | -61.9812 | 59.8663 | 59.8663 | -59.7885 | 59.8206 | 62.0361 | -59.7519 | -59.9899 | 62.1277 | 62.0819 | 62.0041 | 0.045776 | -0.032043 | 0.054932 | -0.17853 | -0.16937 | 121.9025 | 121.8567 | 2.2476 | 121.8018 | 2.1927 | 0.091553 | 0.045776 | 121.8475 | 121.8475 | 0.28381 | 121.8384 | 62.3199 | 121.8933 | -60.0357 | -122.0169 | 62.0819 | 121.9025 | 62.2009 | 38.1042
1736.3125 | 122.319 | -61.9537 | 59.9854 | 0.04097 | 0.0053982 | -0.0043429 | -0.095282 | -0.0015808 | -0.0059516 | -0.0030719 | -0.32654 | 0.826 | 0.14492 | 0.061566 | -0.008468 | 0.023751 | 0.73989 | 0.21973 | 0.21973 | 0.041199 | 0.13733 | 0.27008 | 0.13733 | 0.20142 | -23.79 | 59.8709 | -61.8942 | 60.0632 | 60.0906 | -59.5963 | 59.9442 | 61.9949 | -59.7656 | -59.848 | 62.2238 | 62.1552 | 62.0911 | 0.16022 | 0.09613 | 0.059509 | -0.11444 | 0.077819 | 122.0444 | 121.8979 | 2.3575 | 121.8384 | 2.298 | 0.22888 | 0.09613 | 121.9849 | 121.9574 | 0.17853 | 121.7651 | 62.1735 | 121.8246 | -59.9442 | -121.8796 | 62.0911 | 122.0169 | 62.1735 | 38.1638
1737.3125 | 122.3373 | -62.1414 | 59.8022 | 0.063858 | 0.010098 | -0.0075473 | -0.096778 | -0.0022218 | -0.005738 | -0.0030719 | -0.18311 | 0.82451 | 0.14897 | 0.073529 | -0.012741 | 0.034218 | 0.74159 | 0.1831 | 0.19684 | 0.009155 | 0.20599 | 0.35248 | 0.15564 | 0.16479 | -18.5898 | 59.6695 | -62.1506 | 59.9213 | 59.8251 | -52.803 | 59.7565 | 62.1506 | -59.6054 | -59.5963 | 62.4939 | 62.3062 | 62.2971 | 0.15564 | 0.14649 | -0.009156 | -0.13275 | 0.11902 | 121.9666 | 121.8979 | 9.3384 | 121.907 | 9.3475 | 0.34332 | 0.19684 | 121.9757 | 122.0718 | 0.18768 | 121.8201 | 62.3383 | 121.8109 | -59.7931 | -121.9528 | 62.3474 | 122.0627 | 62.3245 | 43.5516
1738.3125 | 122.2458 | -61.7935 | 60.1273 | 0.071487 | 0.0088162 | -0.0045567 | -0.095069 | -0.0011536 | -0.004029 | -0.0024311 | -0.36316 | 0.81831 | 0.14855 | 0.0966 | -0.011886 | 0.059212 | 0.7386 | 0.041199 | 0.14648 | -0.045776 | 0.58594 | 0.63171 | 0.48523 | 0.58136 | -4.1245 | 58.7311 | -62.97 | 60.4294 | 60.5484 | -78.2822 | 60.3149 | 61.7477 | -59.9808 | -59.5413 | 62.4252 | 62.3749 | 62.2787 | 0.62714 | 0.53101 | -1.1765 | -1.3962 | 0.30212 | 122.3419 | 122.1085 | -16.4886 | 123.2849 | -15.3122 | 0.67749 | 0.63171 | 123.5184 | 123.3994 | 0.19226 | 121.7011 | 61.94 | 120.5246 | -60.173 | -123.0972 | 62.3795 | 122.2229 | 61.8347 | 57.6691
1739.3125 | 122.1863 | -62.0819 | 59.9304 | 0.079117 | 0.0056118 | -0.0054111 | -0.091223 | -0.00029898 | -0.0063788 | 0.00055974 | -0.46692 | 0.82536 | 0.14684 | 0.11326 | -0.010604 | 0.071602 | 0.7401 | 0.45776 | 0.54474 | 0.27924 | 0.21057 | 0.1236 | -0.041199 | -0.054932 | -31.2332 | 60.2097 | -61.6425 | 59.3903 | 60.1364 | -79.6646 | 60.0082 | 62.3611 | -59.3857 | -59.7198 | 62.2055 | 62.027 | 62.0407 | -0.33417 | -0.32043 | 0.43945 | 0.27924 | -0.54016 | 122.2183 | 122.0901 | -17.5827 | 121.6507 | -18.0222 | -0.15564 | -0.068665 | 121.7789 | 121.0327 | 0.2655 | 121.8521 | 62.6266 | 122.2916 | -59.6512 | -121.5729 | 62.2925 | 121.4722 | 62.5397 | 30.8487
1740.3125 | 122.2504 | -60.9009 | 61.1343 | 0.086746 | 0.0075344 | -0.0062655 | -0.094855 | 0.00076902 | -0.0029608 | -0.0017903 | -0.054932 | -0.0015723 | -0.010388 | 0.0013245 | -0.00505 | 0.011574 | -0.000532 | 0.027466 | 0.14191 | -0.09613 | -0.018311 | 0.068665 | -0.059509 | 0.018311 | 0.027466 | 0.18768 | -0.09613 | 0.13275 | 0.27924 | 0.004578 | 0.068665 | 60.8047 | -60.9924 | -61.1526 | 60.9695 | 60.9192 | 60.8414 | 0.11444 | 0.036621 | 60.8047 | -60.9467 | -61.0016 | 61.1801 | 60.9695 | 60.9055 | 0.16479 | 0.10071 | 0.16479 | 0.077819 | 0.37537 | 0.22888 | 0.23804 | 0.28381 | 61.0428 | 61.0886 | -61.2305 | -61.2305 | 60.8826 | 61.0336 | 60.9283 | 60.9283
1741.3125 | 122.1497 | -60.9238 | 61.1435 | 0.12489 | 0.0092434 | -0.0058383 | -0.096137 | 0.00012822 | -0.0036018 | -0.0028583 | 0.015259 | -0.0034949 | -0.010816 | 0.0015381 | -0.0088952 | 0.0081561 | -0.003309 | -0.004578 | 0.16937 | -0.082397 | -0.064087 | 0.041199 | -0.050354 | -0.004578 | 0.009155 | 0.24261 | -0.064087 | -0.009155 | 0.10986 | 0.37994 | 0.42572 | 60.8414 | -60.9741 | -61.2076 | 60.965 | 60.9192 | 60.8734 | 0.077819 | 0.032043 | 60.8597 | -60.9009 | -61.1526 | 61.0336 | 61.3495 | 61.3037 | 0.48981 | 0.44403 | 0.1236 | 0.01831 | 0.17395 | 0.054932 | 0.25177 | 0.3067 | 61.0931 | 61.1664 | -61.2259 | -61.2076 | 60.8597 | 60.9146 | 60.9192 | 60.9329
1742.3125 | 122.2137 | -60.9512 | 61.1481 | 0.071487 | 0.0081754 | -0.0039157 | -0.094855 | 0.0011962 | -0.004029 | -0.0039265 | 0.012207 | -0.0019995 | -0.0091068 | -0.0040161 | -0.0069726 | 0.013283 | 0.0013906 | -0.004578 | 0.16937 | -0.082397 | -0.068665 | 0.032043 | -0.064087 | 0.013733 | -0.009155 | 0.23804 | -0.07782 | -0.28839 | 0.009155 | 0.11444 | 0.13733 | 60.8688 | -60.9787 | -61.2167 | 60.9833 | 60.965 | 60.8871 | 0.09613 | 0.01831 | 60.8734 | -60.91 | -61.4365 | 60.9604 | 61.0886 | 61.0657 | 0.21515 | 0.19226 | 0.11444 | 0.013732 | 0.086975 | -0.21057 | 0.25177 | 0.31586 | 61.1206 | 61.1893 | -61.2305 | -61.2259 | 60.8826 | 60.6628 | 60.9467 | 60.9421
1743.3125 | 122.287 | -60.9146 | 61.1618 | 0.071487 | 0.0096708 | -0.0066929 | -0.094 | -0.0028626 | -0.0053108 | -8.1264e-05 | 0.057983 | -0.0022131 | -0.0065432 | -0.0065795 | -0.0080408 | 0.010292 | 0.0005362 | 0.059509 | 0.13275 | -0.068665 | 0.018311 | 0.11902 | 0.018311 | 0.086975 | 0.068665 | 0.21515 | -0.045776 | 0.027466 | 0.13733 | 0.054932 | 0.10071 | 60.8459 | -61.0291 | -61.1435 | 61.0336 | 61.0016 | 60.9329 | 0.15564 | 0.086976 | 60.8688 | -60.9467 | -61.1343 | 61.0519 | 61.0153 | 60.9695 | 0.14648 | 0.10071 | 0.18768 | 0.086976 | 0.18311 | 0.073242 | 0.20142 | 0.26093 | 61.0474 | 61.1298 | -61.2305 | -61.2076 | 60.9329 | 60.9421 | 60.9741 | 60.9833
1744.3125 | 122.3007 | -60.9421 | 61.1618 | 0.025711 | 0.008389 | -0.0058383 | -0.095282 | 0.00012822 | -0.0031744 | -0.0028583 | -0.042725 | -0.0019995 | -0.010602 | 0.0043153 | -0.0074 | 0.012001 | -0.000532 | 0.009155 | 0.15564 | -0.09613 | -0.041199 | 0.054932 | -0.045776 | 0.018311 | 0.004578 | 0.1831 | -0.082397 | 0.022888 | 0.10071 | -0.013733 | 0.068665 | 60.8459 | -61.0062 | -61.203 | 60.997 | 60.9604 | 60.8963 | 0.11444 | 0.050354 | 60.8597 | -60.9787 | -61.1389 | 61.0428 | 61.0107 | 60.9283 | 0.15106 | 0.068664 | 0.15106 | 0.054931 | 0.18311 | 0.10528 | 0.25177 | 0.2655 | 61.0977 | 61.1252 | -61.2579 | -61.2442 | 60.9009 | 60.965 | 60.9512 | 60.9467
1745.3281 | 122.3923 | -60.9421 | 61.1252 | 0.010452 | 0.0079618 | -0.0032749 | -0.095069 | -0.0015808 | -0.0025336 | -0.00029486 | 0.0061035 | -0.0015723 | -0.0099612 | -0.0023071 | -0.0078272 | 0.01072 | -0.0009592 | 0.018311 | 0.10529 | -0.082397 | 0.032043 | 0.12817 | -0.013733 | 0.045776 | 0.013733 | 0.07782 | -0.15106 | -0.013733 | 0.10071 | 0.009155 | 0.073242 | 60.8597 | -61.0199 | -61.0931 | 61.0703 | 60.9879 | 60.9283 | 0.12817 | 0.068664 | 60.791 | -61.0474 | -61.1389 | 61.0428 | 61.0153 | 60.9512 | 0.2243 | 0.16022 | 0.21057 | 0.11444 | 0.25177 | 0.13733 | 0.18768 | 0.22888 | 61.0474 | 61.0199 | -61.2076 | -61.2762 | 60.9741 | 60.9283 | 60.9604 | 60.9558
1746.3125 | 122.3099 | -60.9787 | 61.1847 | 0.094376 | 0.0053982 | -0.0062655 | -0.092291 | 0.0014098 | -0.0076606 | -0.0049945 | -0.015259 | 0.00035035 | -0.008893 | -0.0059387 | -0.0093226 | 0.012215 | 0.0016044 | -0.018311 | 0.15564 | -0.086975 | -0.050354 | 0.018311 | -0.059509 | -0.009155 | -0.013733 | 0.22888 | -0.09613 | 0.009155 | 0.10986 | 0.013733 | 0.073242 | 60.8917 | -61.0291 | -61.235 | 60.997 | 60.9695 | 60.9192 | 0.07782 | 0.027466 | 60.8826 | -60.9558 | -61.1755 | 61.0886 | 61.0519 | 60.9924 | 0.16937 | 0.10986 | 0.10529 | 0.036621 | 0.20599 | 0.10528 | 0.24261 | 0.32501 | 61.1343 | 61.2076 | -61.2717 | -61.2808 | 60.9283 | 60.9879 | 60.9604 | 60.965
1747.3125 | 122.3511 | -60.9421 | 61.203 | 0.056229 | 0.0086026 | -0.0030613 | -0.094 | -0.00029898 | -0.005097 | -0.0013629 | -0.0030517 | -0.0017859 | -0.010602 | -0.0020935 | -0.0082544 | 0.012429 | -0.0011728 | -0.018311 | 0.16022 | -0.10529 | -0.059509 | 0.018311 | -0.059509 | -0.013733 | -0.009155 | 0.21973 | -0.068665 | 0.018311 | 0.10529 | 0.018311 | 0.09613 | 60.8368 | -61.0428 | -61.2625 | 60.9604 | 60.9283 | 60.8826 | 0.091553 | 0.045777 | 60.8734 | -60.9833 | -61.1847 | 61.0474 | 61.0382 | 60.9604 | 0.16479 | 0.086976 | 0.1236 | 0.045777 | 0.17395 | 0.086976 | 0.2655 | 0.28839 | 61.1023 | 61.1618 | -61.3083 | -61.2717 | 60.8826 | 60.9604 | 60.9238 | 60.9329
1748.3125 | 122.3694 | -60.9467 | 61.1847 | 0.04097 | 0.0075344 | -0.0054111 | -0.094855 | 0.0067504 | -0.0055244 | -0.00029486 | -0.15259 | -0.00093145 | -0.012097 | 4.2656e-05 | -0.010604 | 0.012215 | 0.0016044 | 0.009155 | 0.16479 | -0.07782 | -0.027466 | 0.059509 | -0.059509 | 0 | 0.24261 | 0.16937 | -0.10071 | 0.009155 | 0.13275 | -0.004578 | 0.068665 | 60.8688 | -61.0199 | -61.2122 | 61.0062 | 60.9467 | 60.8871 | 0.07782 | 0.018311 | 60.8459 | -61.0153 | -61.1755 | 61.0794 | 61.0153 | 60.9421 | 0.16937 | 0.09613 | 0.13733 | 0.050354 | 0.23346 | 0.10986 | 0.24261 | 0.27008 | 61.1114 | 61.116 | -61.2625 | -61.2854 | 60.9192 | 60.9558 | 60.9558 | 61.1893
1749.3125 | 122.3145 | -60.9787 | 61.2122 | 0.048599 | 0.0068936 | -0.0054111 | -0.092932 | -0.002008 | -0.0038154 | -0.0013629 | -0.036621 | -0.0011451 | -0.0091068 | -0.0023071 | -0.0088952 | 0.0098651 | -0.0013864 | -0.009155 | 0.14191 | -0.091553 | -0.054932 | 0.050354 | -0.082397 | -0.022888 | -0.050354 | 0.15106 | -0.1236 | -0.059509 | 0.022888 | -0.07782 | 0.022888 | 60.8871 | -61.0703 | -61.2671 | 61.0291 | 60.9558 | 60.8963 | 0.068665 | 0.009156 | 60.8551 | -61.0611 | -61.2717 | 61.0016 | 61.0016 | 60.9009 | 0.14648 | 0.045776 | 0.14191 | 0.036621 | 0.14648 | 0.064087 | 0.23346 | 0.27466 | 61.1206 | 61.1298 | -61.3037 | -61.3358 | 60.9238 | 60.9192 | 60.9695 | 60.9283
1750.3125 | 122.3557 | -60.9695 | 61.2122 | 0.11726 | 0.0062528 | -0.0043429 | -0.095496 | 0.0039734 | -0.0048834 | -0.0013629 | 0.021362 | -0.0022131 | -0.011457 | -0.0027343 | -0.0071864 | 0.012429 | 0.0024588 | 0 | 0.15564 | -0.07782 | -0.054932 | 0.050354 | -0.045776 | -0.004578 | 0.009155 | 0.21515 | -0.068665 | 0.018311 | 0.10071 | -0.022888 | 0.073242 | 60.8917 | -61.0565 | -61.2671 | 61.0199 | 60.965 | 60.9238 | 0.073242 | 0.032044 | 60.9009 | -60.997 | -61.1938 | 61.0703 | 61.0428 | 60.9467 | 0.14191 | 0.045777 | 0.12817 | 0.022888 | 0.16937 | 0.086976 | 0.23346 | 0.28381 | 61.1252 | 61.1847 | -61.29 | -61.2808 | 60.9146 | 60.9879 | 60.9695 | 60.9787
1751.3125 | 122.3831 | -60.9741 | 61.1984 | 0.079117 | 0.0081754 | -0.0058383 | -0.093573 | 0.0035462 | -0.0063788 | -0.0028583 | 0.018311 | -0.00093145 | -0.0099612 | -0.0048705 | -0.008468 | 0.014138 | 0.0033134 | 0.004578 | 0.16937 | -0.10071 | -0.036621 | 0.064087 | -0.022888 | 0.027466 | 0.013733 | 0.1831 | -0.068665 | 0 | 0.10529 | 0.004578 | 0.064087 | 60.8734 | -61.0291 | -61.235 | 61.0382 | 61.0016 | 60.9512 | 0.12817 | 0.07782 | 60.9055 | -61.0153 | -61.1984 | 61.0794 | 61.0382 | 60.9787 | 0.13275 | 0.073243 | 0.1648 | 0.064087 | 0.17395 | 0.068665 | 0.27008 | 0.25177 | 61.1435 | 61.1572 | -61.2991 | -61.2671 | 60.9375 | 60.9741 | 60.9787 | 60.9879
1752.3125 | 122.3785 | -60.9787 | 61.1984 | 0.056229 | 0.0088162 | -0.0045567 | -0.093573 | 0.00076902 | -0.0048834 | -0.0026447 | -0.021362 | -0.0022131 | -0.0084658 | -0.0023071 | -0.0076136 | 0.011788 | 0.0024588 | 0.022888 | 0.1831 | -0.059509 | -0.027466 | 0.073242 | -0.036621 | 0.004578 | -0.018311 | 0.16479 | -0.10986 | -0.018311 | 0.059509 | -0.036621 | 0.050354 | 60.9192 | -61.0153 | -61.2259 | 61.0519 | 60.9833 | 60.9421 | 0.064087 | 0.022888 | 60.8688 | -61.0336 | -61.2167 | 61.0382 | 61.0291 | 60.9421 | 0.16022 | 0.073242 | 0.13275 | 0.032043 | 0.16937 | 0.091552 | 0.24261 | 0.27466 | 61.1618 | 61.1435 | -61.2579 | -61.3083 | 60.9512 | 60.9604 | 61.0016 | 60.9604
1753.3125 | 122.3373 | -60.9879 | 61.2213 | 0.079117 | 0.0086026 | -0.0051975 | -0.091437 | 0.00076902 | -0.0055244 | -0.00029486 | -0.015259 | -0.00050405 | -0.0082522 | -0.0057251 | -0.0099634 | 0.012429 | 0.0024588 | -0.041199 | 0.13275 | -0.10529 | -0.09613 | -0.004578 | -0.09613 | -0.041199 | -0.10071 | 0.14191 | -0.11444 | -0.09613 | -0.013733 | -0.09613 | 0 | 60.8826 | -61.0886 | -61.3174 | 60.9833 | 60.9467 | 60.8917 | 0.064087 | 0.009156 | 60.8734 | -61.0794 | -61.3174 | 60.9741 | 60.9879 | 60.8917 | 0.11444 | 0.018311 | 0.10071 | 0.009156 | 0.10071 | 0.018311 | 0.23804 | 0.25635 | 61.1206 | 61.1298 | -61.3266 | -61.3358 | 60.8917 | 60.8917 | 60.9467 | 60.8871
1754.3125 | 122.3282 | -61.0153 | 61.1801 | 0.086746 | 0.0064664 | -0.0049839 | -0.093787 | -0.0015808 | -0.0038154 | -0.0017903 | -0.021362 | -0.0011451 | -0.0086794 | -0.00059814 | -0.0093226 | 0.01072 | -0.0013864 | -0.036621 | 0.13733 | -0.10071 | -0.11444 | -0.013733 | -0.13275 | -0.059509 | -0.13275 | 0.14191 | -0.12817 | -0.09613 | -0.018311 | -0.12817 | -0.027466 | 60.9146 | -61.0428 | -61.2946 | 61.0016 | 60.9558 | 60.8826 | 0.041199 | -0.032043 | 60.8871 | -61.0382 | -61.2762 | 60.997 | 60.9879 | 60.8871 | 0.10071 | 0 | 0.086975 | -0.013733 | 0.10986 | 0.032044 | 0.23804 | 0.27008 | 61.1526 | 61.1572 | -61.2808 | -61.3083 | 60.9009 | 60.9192 | 60.9787 | 60.8826
1755.3125 | 122.3602 | -61.0016 | 61.1893 | 0.063858 | 0.0068936 | -0.0056247 | -0.094214 | 0.0031188 | -0.0046698 | -0.0017903 | -0.015259 | -0.00071785 | -0.0080386 | -0.00081174 | -0.0080408 | 0.0098651 | 0.0007498 | -0.013733 | 0.13275 | -0.09613 | -0.050354 | 0.027466 | -0.064087 | -0.004578 | -0.036621 | 0.15564 | -0.10986 | -0.054932 | 0.032043 | -0.068665 | 0.027466 | 60.9055 | -61.0565 | -61.2396 | 61.0291 | 60.997 | 60.9375 | 0.091552 | 0.032043 | 60.8917 | -61.0336 | -61.2442 | 61.0336 | 61.0291 | 60.9329 | 0.13733 | 0.041198 | 0.1236 | 0.045776 | 0.14191 | 0.054931 | 0.22888 | 0.2655 | 61.1343 | 61.1572 | -61.2854 | -61.2991 | 60.9512 | 60.9467 | 60.9879 | 60.965
1756.3125 | 122.3831 | -61.0016 | 61.203 | 0.071487 | 0.0075344 | -0.0056247 | -0.09336 | 0.002478 | -0.0061652 | -0.0032855 | -0.0061035 | -0.0015723 | -0.0097476 | 0.0023927 | -0.0093226 | 0.0094379 | 0.001818 | -0.018311 | 0.13275 | -0.091553 | -0.064087 | 0.032043 | -0.086975 | -0.027466 | -0.041199 | 0.14191 | -0.11444 | -0.064087 | 0.013733 | -0.073242 | 0.013733 | 60.91 | -61.0703 | -61.2671 | 61.0336 | 60.9741 | 60.9146 | 0.064087 | 0.004578 | 60.8871 | -61.0611 | -61.2671 | 61.0153 | 61.0153 | 60.9283 | 0.12817 | 0.041199 | 0.1236 | 0.027466 | 0.12817 | 0.050354 | 0.2243 | 0.25635 | 61.1343 | 61.1435 | -61.2946 | -61.3174 | 60.9375 | 60.9375 | 60.9833 | 60.9604
1757.3125 | 122.3923 | -60.9833 | 61.1801 | 0.15541 | 0.0060392 | -0.0058383 | -0.095069 | 0.0039734 | -0.005738 | -8.1264e-05 | 0.018311 | -0.0022131 | -0.010816 | -0.0040161 | -0.010391 | 0.012001 | 0.002886 | -0.013733 | 0.1831 | -0.050354 | -0.027466 | 0.068665 | -0.041199 | 0.009155 | -0.004578 | 0.16937 | -0.10071 | -0.022888 | 0.054932 | -0.027466 | 0.059509 | 60.9329 | -60.997 | -61.2076 | 61.0519 | 60.9924 | 60.9421 | 0.059509 | 0.009155 | 60.8826 | -61.0107 | -61.203 | 61.0382 | 61.0428 | 60.9558 | 0.16022 | 0.073242 | 0.11902 | 0.022888 | 0.15564 | 0.07782 | 0.23346 | 0.27008 | 61.1664 | 61.1526 | -61.2305 | -61.2808 | 60.9558 | 60.9604 | 60.9695 | 60.9787
1758.3125 | 122.374 | -61.0153 | 61.1893 | 0.018082 | 0.00668 | -0.0051975 | -0.095923 | 0.0035462 | -0.003388 | -8.1264e-05 | 0.015259 | 0.00035035 | -0.0099612 | -0.0087157 | -0.0086816 | 0.011788 | 0.0009634 | -0.022888 | 0.14191 | -0.091553 | -0.091553 | 0.013733 | -0.11444 | -0.050354 | -0.082397 | 0.14648 | -0.13733 | -0.091553 | 0 | -0.09613 | 0.004578 | 60.9238 | -61.0474 | -61.2808 | 61.0291 | 60.965 | 60.9009 | 0.041199 | -0.022888 | 60.878 | -61.0428 | -61.2808 | 61.0153 | 61.0199 | 60.9192 | 0.14191 | 0.041199 | 0.10529 | 0 | 0.13733 | 0.045776 | 0.23346 | 0.28381 | 61.1572 | 61.1618 | -61.2808 | -61.3266 | 60.9238 | 60.9238 | 60.9924 | 60.9329
1759.3125 | 122.3785 | -61.0291 | 61.2167 | 0.010452 | 0.00668 | -0.0049839 | -0.093146 | 0.0050414 | -0.0038154 | -0.0022175 | 0.12512 | -0.00050405 | -0.0093204 | -0.0029479 | -0.0086816 | 0.012856 | 0.0024588 | -0.07782 | 0.12817 | -0.11444 | -0.11444 | -0.09613 | -0.46234 | 0.073242 | -0.29755 | 0.082397 | -0.15564 | -0.073242 | -0.068665 | -0.15106 | -0.022888 | 60.9146 | -61.0886 | -61.3312 | 60.9329 | 61.1023 | 60.5667 | 0.18768 | -0.3479 | 60.8734 | -61.1343 | -61.29 | 60.9604 | 61.0062 | 60.878 | 0.13275 | 0.004578 | 0.018311 | 0 | 0.086975 | 0.082398 | 0.24262 | 0.23804 | 61.1572 | 61.1114 | -61.3312 | -61.3724 | 60.9146 | 60.9558 | 60.9512 | 60.7315
1760.3125 | 122.3831 | -61.0428 | 61.2076 | 0.071487 | 0.0081754 | -0.0037021 | -0.094641 | -0.0017944 | -0.0046698 | -0.00050846 | 0.015259 | -0.0026405 | -0.0084658 | -0.0091431 | -0.0078272 | 0.010292 | -0.000532 | -0.059509 | 0.13275 | -0.12817 | -0.20599 | -0.050354 | -0.027466 | -0.045776 | -0.11444 | 0.15106 | -0.12817 | -0.10071 | -0.032043 | -0.11444 | -0.009155 | 60.9146 | -61.0748 | -61.4136 | 60.9924 | 60.997 | 61.0153 | 0.082398 | 0.10071 | 60.9146 | -61.0565 | -61.3083 | 61.0107 | 61.0336 | 60.9283 | 0.11902 | 0.013733 | 0.07782 | -0.07782 | 0.096131 | 0.027466 | 0.26093 | 0.27924 | 61.1755 | 61.1938 | -61.3358 | -61.3358 | 60.8368 | 60.9421 | 60.9833 | 60.9283
1761.3125 | 122.3602 | -61.0291 | 61.1938 | 0.079117 | 0.0068936 | -0.0034885 | -0.092719 | 0.0044006 | -0.0038154 | -0.00029486 | 0.033569 | -0.0011451 | -0.0099612 | -0.0029479 | -0.0093226 | 0.012429 | -0.0003182 | -0.059509 | 0.13733 | -0.10071 | -0.11444 | -0.036621 | -0.15106 | -0.064087 | -0.14191 | 0.14191 | -0.15106 | -0.13275 | -0.068665 | -0.14191 | -0.032043 | 60.9283 | -61.0565 | -61.3083 | 60.9924 | 60.965 | 60.878 | 0.036621 | -0.050354 | 60.878 | -61.0519 | -61.3266 | 60.9604 | 60.997 | 60.8871 | 0.11902 | 0.009155 | 0.064087 | -0.013733 | 0.082397 | 0.018311 | 0.23804 | 0.29297 | 61.1664 | 61.171 | -61.2946 | -61.3449 | 60.9146 | 60.8963 | 60.9695 | 60.8871
1762.3125 | 122.4106 | -61.0199 | 61.1984 | 0.025711 | 0.0062528 | -0.0051975 | -0.095282 | 0.0014098 | -0.0053108 | -0.0020039 | 0.027466 | -0.0013587 | -0.0099612 | -0.0085021 | -0.0080408 | 0.011361 | -0.0001046 | -0.041199 | 0.15564 | -0.11902 | -0.11902 | -0.032043 | -0.12817 | -0.050354 | -0.13275 | 0.11444 | -0.16479 | -0.091553 | -0.018311 | -0.11444 | -0.009155 | 60.9009 | -61.0428 | -61.3174 | 60.9879 | 60.9695 | 60.8917 | 0.068665 | -0.009155 | 60.8551 | -61.084 | -61.29 | 61.0016 | 61.0107 | 60.9055 | 0.15564 | 0.050354 | 0.086976 | 0 | 0.14648 | 0.073242 | 0.27466 | 0.27924 | 61.1755 | 61.1343 | -61.3174 | -61.3632 | 60.9009 | 60.9283 | 60.9787 | 60.8871
1763.3125 | 122.3785 | -61.0519 | 61.2259 | 0.10963 | 0.0077482 | -0.0045567 | -0.093573 | -0.0011536 | -0.0055244 | -0.00093566 | 0.012207 | -0.0028541 | -0.0069704 | -0.0072205 | -0.0088952 | 0.010506 | -0.0030954 | -0.07782 | 0.13733 | -0.11902 | -0.14191 | -0.059509 | -0.16479 | -0.10071 | -0.24719 | 0.086975 | -0.1831 | -0.15106 | 0.086975 | -0.086975 | -0.045776 | 60.9329 | -61.0886 | -61.3678 | 60.9924 | 60.9512 | 60.8871 | 0.018311 | -0.045776 | 60.8688 | -61.1389 | -61.377 | 61.1389 | 61.0062 | 60.965 | 0.13733 | 0.09613 | 0.05951 | -0.022888 | 0.27008 | 0.032043 | 0.25635 | 0.27008 | 61.1893 | 61.1389 | -61.3449 | -61.409 | 60.91 | 60.9009 | 60.9741 | 60.8047
1764.3125 | 122.438 | -60.9879 | 61.171 | 0.025711 | 0.0075344 | -0.0045567 | -0.096991 | 0.00012822 | -0.0038154 | -0.0011493 | 0.094605 | -0.0017859 | -0.0093204 | -0.0042297 | -0.0086816 | 0.01072 | 0.001177 | -0.027466 | 0.11444 | -0.068665 | -0.032043 | 0.059509 | -0.045776 | 0.027466 | -0.045776 | 0.09613 | -0.1236 | -0.027466 | 0.082397 | 0.004578 | 0.073242 | 60.9192 | -61.0565 | -61.203 | 61.0474 | 61.0153 | 60.9421 | 0.096131 | 0.022889 | 60.8643 | -61.0748 | -61.1984 | 61.0703 | 61.0611 | 60.9924 | 0.19684 | 0.12817 | 0.12817 | 0.036622 | 0.20599 | 0.09613 | 0.18311 | 0.21973 | 61.1023 | 61.084 | -61.2396 | -61.2946 | 60.9558 | 60.9604 | 60.9604 | 60.9421
1765.3125 | 122.4472 | -61.0153 | 61.203 | 0.010452 | 0.0075344 | -0.0058383 | -0.09336 | -8.538e-05 | -0.0036018 | 0.0016277 | 0.033569 | -0.0015723 | -0.01167 | -0.0059387 | -0.0088952 | 0.012001 | -0.0003182 | -0.073242 | 0.11444 | -0.11444 | -0.10529 | -0.018311 | -0.13275 | -0.045776 | -0.10529 | 0.10529 | -0.14648 | -0.073242 | 0.009155 | -0.09613 | 0.004578 | 60.9009 | -61.0886 | -61.3083 | 60.997 | 60.9695 | 60.8826 | 0.068665 | -0.01831 | 60.8688 | -61.0977 | -61.2762 | 61.0245 | 61.0199 | 60.9192 | 0.15106 | 0.050354 | 0.09613 | 0.009155 | 0.15564 | 0.073242 | 0.22888 | 0.25177 | 61.1298 | 61.1206 | -61.3174 | -61.3495 | 60.91 | 60.9421 | 60.9421 | 60.91
1766.3125 | 122.438 | -61.0199 | 61.1893 | 0.063858 | 0.0068936 | -0.0064793 | -0.093573 | 0.0037598 | -0.003388 | -0.0049945 | -8.6e-08 | -0.0015723 | -0.010388 | -0.0048705 | -0.0080408 | 0.0098651 | 0.0007498 | -0.059509 | 0.12817 | -0.10986 | -0.09613 | -0.009155 | -0.10986 | -0.036621 | -0.091553 | 0.09613 | -0.14191 | -0.073242 | 0 | -0.10071 | -0.004578 | 60.91 | -61.0611 | -61.2854 | 61.0107 | 60.9833 | 60.91 | 0.073242 | 0 | 60.878 | -61.0931 | -61.2625 | 61.0199 | 61.0153 | 60.9192 | 0.13733 | 0.041199 | 0.10071 | 0.013733 | 0.14191 | 0.068665 | 0.23804 | 0.23804 | 61.1481 | 61.116 | -61.2991 | -61.3312 | 60.9238 | 60.9467 | 60.9604 | 60.9283
1767.3125 | 122.4747 | -61.0199 | 61.1984 | 0.056229 | 0.0056118 | -0.0041293 | -0.093146 | -0.00029898 | -0.0042426 | -0.0013629 | 0.0030517 | -0.00050405 | -0.010175 | -0.0033751 | -0.0095362 | 0.010506 | -0.0011728 | -0.064087 | 0.11902 | -0.10986 | -0.091553 | -0.009155 | -0.10986 | -0.032043 | -0.086975 | 0.10071 | -0.15106 | -0.064087 | 0.013733 | -0.054932 | 0.045776 | 60.91 | -61.0794 | -61.29 | 61.0107 | 60.9879 | 60.91 | 0.07782 | 0 | 60.8688 | -61.0977 | -61.2625 | 61.0336 | 61.0657 | 60.965 | 0.19684 | 0.09613 | 0.10071 | 0.01831 | 0.16479 | 0.086975 | 0.22888 | 0.25177 | 61.1389 | 61.1206 | -61.3083 | -61.3495 | 60.9283 | 60.9558 | 60.9558 | 60.9329
1768.3125 | 122.4838 | -61.0016 | 61.1847 | 0.079117 | 0.0075344 | -0.0058383 | -0.092719 | 0.0037598 | -0.0038154 | -0.0017903 | 0.012207 | -0.0022131 | -0.011029 | -0.00059814 | -0.010177 | 0.010933 | 0.001818 | -0.059509 | 0.1236 | -0.09613 | -0.073242 | 0 | -0.10071 | -0.018311 | -0.086975 | 0.10071 | -0.14648 | -0.050354 | 0.032043 | -0.068665 | 0.050354 | 60.9055 | -61.0611 | -61.2579 | 61.0016 | 60.9833 | 60.9009 | 0.077819 | -0.004578 | 60.8551 | -61.084 | -61.235 | 61.0336 | 61.0519 | 60.9329 | 0.19684 | 0.077819 | 0.09613 | 0.022888 | 0.17853 | 0.09613 | 0.21973 | 0.24719 | 61.1252 | 61.1023 | -61.2808 | -61.3312 | 60.9283 | 60.9512 | 60.9421 | 60.9146
1769.3125 | 122.5204 | -61.0016 | 61.1847 | 0.079117 | 0.008389 | -0.0088291 | -0.097205 | -0.0045716 | -0.005738 | -0.0015765 | 0.11597 | -0.0043495 | -0.01167 | -0.0093567 | -0.0097498 | 0.0087969 | 0.0003226 | -0.013733 | 0.13275 | -0.059509 | -0.013733 | 0.09613 | 0.004578 | 0.086975 | 0.022888 | 0.1236 | -0.086975 | 0.018311 | 0.13275 | 0.07782 | 0.1236 | 60.9421 | -61.0519 | -61.1984 | 61.0977 | 61.0886 | 61.0062 | 0.14648 | 0.064087 | 60.9146 | -61.0611 | -61.1664 | 61.1343 | 61.1252 | 61.0794 | 0.21057 | 0.16479 | 0.15564 | 0.045776 | 0.21973 | 0.10529 | 0.19226 | 0.21057 | 61.1343 | 61.1252 | -61.2442 | -61.2717 | 60.9879 | 61.0199 | 60.9879 | 61.0245
1770.3125 | 122.5021 | -61.0199 | 61.1847 | 0.086746 | 0.0053982 | -0.0056247 | -0.092078 | 0.0026916 | -0.004029 | -0.0020039 | 0.021362 | -0.0013587 | -0.012311 | -0.0065795 | -0.010391 | 0.011147 | -0.0020272 | -0.041199 | 0.10986 | -0.09613 | -0.059509 | 0.041199 | -0.073242 | -0.009155 | -0.050354 | 0.07782 | -0.14648 | -0.018311 | 0.068665 | -0.036621 | 0.068665 | 60.9238 | -61.0748 | -61.2442 | 61.0611 | 61.0107 | 60.9467 | 0.086975 | 0.022888 | 60.8734 | -61.1069 | -61.203 | 61.0886 | 61.0886 | 60.9833 | 0.21515 | 0.10986 | 0.13733 | 0.036621 | 0.21515 | 0.12817 | 0.20599 | 0.2243 | 61.1298 | 61.0977 | -61.2808 | -61.3312 | 60.9604 | 61.0016 | 60.9787 | 60.9695
1771.3125 | 122.5204 | -61.0016 | 61.203 | 0.048599 | 0.0077482 | -0.0041293 | -0.09336 | -0.0011536 | -0.0061652 | -0.00029486 | -0.015259 | -0.0030677 | -0.011029 | -0.0052979 | -0.0088952 | 0.0087969 | -0.0026682 | -0.054932 | 0.11444 | -0.10529 | -0.022888 | 0.054932 | -0.064087 | 0.004578 | -0.027466 | 0.07782 | -0.14648 | -0.036621 | 0.059509 | -0.022888 | 0.073242 | 60.8963 | -61.0886 | -61.2259 | 61.0565 | 61.0062 | 60.9375 | 0.10986 | 0.041199 | 60.8551 | -61.1252 | -61.2396 | 61.0611 | 61.0748 | 60.9787 | 0.21973 | 0.1236 | 0.16022 | 0.082398 | 0.20599 | 0.10986 | 0.21973 | 0.2243 | 61.116 | 61.0794 | -61.3083 | -61.3495 | 60.9787 | 60.965 | 60.9467 | 60.9741
1772.3125 | 122.5204 | -61.0199 | 61.2167 | 0.048599 | 0.0051846 | -0.0043429 | -0.094855 | 0.0016236 | -0.0038154 | -0.0030719 | 0.030518 | -0.0013587 | -0.012097 | -0.0042297 | -0.0095362 | 0.011788 | -0.0024546 | 0.045776 | 0.041199 | -0.11444 | 0.013733 | 0.1236 | -0.032043 | 0.036621 | 0.004578 | 0.086975 | -0.12817 | 0.004578 | 0.09613 | 0.013733 | 0.064087 | 60.9055 | -61.1755 | -61.203 | 61.1435 | 61.0565 | 60.9879 | 0.15106 | 0.082398 | 60.8917 | -61.1298 | -61.2122 | 61.116 | 61.084 | 61.0336 | 0.19226 | 0.14191 | 0.23804 | 0.12817 | 0.2243 | 0.13275 | 0.15564 | 0.21515 | 61.0611 | 61.1069 | -61.3312 | -61.3449 | 61.0336 | 61.0245 | 61.0657 | 61.0245
1773.3125 | 122.5296 | -61.0062 | 61.1664 | 0.048599 | 0.0077482 | -0.0043429 | -0.093573 | -0.00051278 | -0.0065924 | -0.00093566 | 0.024414 | -0.0013587 | -0.0093204 | -0.0065795 | -0.0097498 | 0.010292 | 0.0033134 | -0.004578 | 0.050354 | -0.086975 | 0.009155 | 0.09613 | -0.045776 | 0.050354 | 0 | 0.082397 | -0.1236 | 0 | 0.091553 | 0.004578 | 0.059509 | 60.9192 | -61.116 | -61.1572 | 61.1023 | 61.0565 | 60.9604 | 0.13733 | 0.041199 | 60.8826 | -61.084 | -61.1664 | 61.0977 | 61.0657 | 61.0107 | 0.1831 | 0.12817 | 0.1831 | 0.09613 | 0.21515 | 0.1236 | 0.13733 | 0.20599 | 61.0565 | 61.0886 | -61.2534 | -61.29 | 61.0153 | 61.0062 | 61.0016 | 61.0062
1774.3125 | 122.4976 | -61.0291 | 61.1938 | 0.025711 | 0.0073208 | -0.0069065 | -0.097205 | 0.0014098 | -0.00232 | -0.0028583 | 0.091553 | -0.0026405 | -0.011243 | -0.0059387 | -0.0088952 | 0.0087969 | -0.0009592 | -0.032043 | 0.10986 | -0.073242 | -0.018311 | 0.068665 | -0.032043 | 0.041199 | -0.20599 | 0.1236 | -0.09613 | -0.045776 | 0.068665 | 0.013733 | 0.068665 | 60.9558 | -61.084 | -61.2122 | 61.0977 | 61.0703 | 60.997 | 0.11444 | 0.041199 | 60.9329 | -61.0703 | -61.2396 | 61.0977 | 61.0977 | 61.0428 | 0.16479 | 0.10986 | 0.14191 | 0.054931 | 0.16479 | 0.050354 | 0.18311 | 0.21973 | 61.1389 | 61.1526 | -61.2671 | -61.29 | 61.0107 | 60.9833 | 60.997 | 60.8231
1775.3125 | 122.493 | -61.0107 | 61.2122 | 0.04097 | 0.0092434 | -0.0043429 | -0.094855 | -0.0013672 | -0.0042426 | 0.00013254 | 0.057983 | 0.00013675 | -0.0097476 | -0.0023071 | -0.009109 | 0.01072 | -0.0028818 | -0.004578 | 0.091553 | -0.045776 | 0 | 0.086975 | -0.036621 | 0.036621 | -0.022888 | 0.09613 | -0.13275 | -0.022888 | 0.064087 | -0.009155 | 0.045776 | 60.965 | -61.1206 | -61.2122 | 61.0977 | 61.0474 | 60.9741 | 0.082397 | 0.009155 | 60.878 | -61.116 | -61.235 | 61.0748 | 61.0565 | 61.0016 | 0.17853 | 0.1236 | 0.13275 | 0.045776 | 0.19684 | 0.10986 | 0.13733 | 0.22888 | 61.1023 | 61.1069 | -61.2579 | -61.3449 | 61.0107 | 60.9879 | 61.0062 | 60.9879
1776.3125 | 122.4976 | -61.0016 | 61.1847 | 0.03334 | 0.0060392 | -0.0060519 | -0.093573 | -0.0030762 | -0.005738 | -0.00050846 | 0.057983 | -0.00050405 | -0.0099612 | -0.010638 | -0.010604 | 0.0092241 | 0.001818 | -0.013733 | 0.10986 | -0.064087 | -0.004578 | 0.082397 | -0.032043 | 0.045776 | -0.018311 | 0.09613 | -0.10986 | -0.009155 | 0.07782 | 0.009155 | 0.064087 | 60.9375 | -61.0748 | -61.1893 | 61.084 | 61.0474 | 60.9695 | 0.10986 | 0.032044 | 60.8917 | -61.0886 | -61.1938 | 61.0794 | 61.0657 | 61.0107 | 0.17395 | 0.11902 | 0.14648 | 0.059509 | 0.18768 | 0.10071 | 0.17395 | 0.20599 | 61.1114 | 61.0977 | -61.2488 | -61.2946 | 60.997 | 60.9924 | 60.9879 | 60.9833
1777.3125 | 122.5067 | -61.0199 | 61.1664 | 0.0028229 | 0.0098844 | -0.0054111 | -0.092505 | 0.00098262 | -0.0042426 | -0.0011493 | 0.036621 | -0.0019995 | -0.010816 | -0.0016663 | -0.0099634 | 0.010506 | -0.0028818 | 0 | 0.10529 | -0.086975 | 0.041199 | 0.1236 | -0.022888 | 0.059509 | 0.032043 | 0.073242 | -0.12817 | 0 | 0.068665 | -0.013733 | 0.045776 | 60.9329 | -61.0611 | -61.1252 | 61.1435 | 61.0794 | 60.997 | 0.14648 | 0.064087 | 60.8917 | -61.0931 | -61.1664 | 61.0886 | 61.0657 | 61.0062 | 0.17395 | 0.11444 | 0.21057 | 0.12817 | 0.19684 | 0.12817 | 0.19226 | 0.20142 | 61.1252 | 61.0931 | -61.2534 | -61.2946 | 61.0611 | 61.0199 | 61.0199 | 61.0519
1778.3125 | 122.5021 | -61.0062 | 61.203 | 0.03334 | 0.0092434 | -0.0047703 | -0.094428 | -0.00029898 | -0.003388 | -0.0043537 | 0.012207 | -0.0026405 | -0.011029 | -0.0046569 | -0.0086816 | 0.0098651 | 0.0007498 | 0 | 0.10071 | -0.068665 | 0.022888 | 0.13733 | -0.032043 | 0.045776 | 0.009155 | 0.086975 | -0.12817 | -0.018311 | 0.064087 | -0.009155 | 0.064087 | 60.9375 | -61.1023 | -61.1801 | 61.1435 | 61.0519 | 60.9741 | 0.11444 | 0.036622 | 60.878 | -61.116 | -61.2213 | 61.0703 | 61.0703 | 60.997 | 0.19226 | 0.11902 | 0.20599 | 0.091553 | 0.19226 | 0.10986 | 0.16937 | 0.21515 | 61.1069 | 61.0931 | -61.2717 | -61.3312 | 61.0291 | 60.9879 | 61.0062 | 61.0153
1779.3125 | 122.5433 | -61.0245 | 61.203 | 0.056229 | 0.0058256 | -0.0073337 | -0.094641 | 0.00012822 | -0.0059516 | -0.00093566 | 0.045776 | -0.0026405 | -0.0099612 | -0.0014525 | -0.0082544 | 0.010292 | -0.0011728 | 0.022888 | 0.11902 | -0.064087 | 0.054932 | 0.13275 | 0.013733 | 0.1236 | 0.10071 | 0.14191 | -0.064087 | 0.068665 | 0.19226 | 0.12817 | 0.14648 | 60.9604 | -61.084 | -61.1481 | 61.1572 | 61.1481 | 61.0382 | 0.18768 | 0.07782 | 60.9604 | -61.0611 | -61.1343 | 61.2167 | 61.171 | 61.1526 | 0.21057 | 0.19226 | 0.19684 | 0.11902 | 0.25635 | 0.13275 | 0.18311 | 0.20599 | 61.1435 | 61.1664 | -61.2671 | -61.2671 | 61.0794 | 61.0931 | 61.0474 | 61.1252
1780.3125 | 122.4884 | -61.0382 | 61.2305 | 0.10963 | 0.0075344 | -0.0069065 | -0.096991 | 0.002478 | -0.004029 | 0.00013254 | -0.01831 | -0.0019995 | -0.012738 | -0.00059814 | -0.0095362 | 0.0085833 | -0.0026682 | -0.027466 | 0.11902 | -0.082397 | -0.004578 | 0.07782 | -0.027466 | 0.032043 | -0.13275 | 0.13733 | -0.11444 | -0.041199 | 0.073242 | 0.004578 | 0.068665 | 60.9558 | -61.1114 | -61.235 | 61.116 | 61.0703 | 61.0107 | 0.11444 | 0.054931 | 60.9238 | -61.0931 | -61.2717 | 61.1114 | 61.1069 | 61.0428 | 0.18311 | 0.11902 | 0.16022 | 0.077819 | 0.18768 | 0.073242 | 0.20142 | 0.25177 | 61.1572 | 61.1755 | -61.3129 | -61.3449 | 61.0336 | 60.997 | 61.0107 | 60.9055
1781.3125 | 122.5067 | -61.0199 | 61.1984 | 0.03334 | 0.0077482 | -0.0064793 | -0.095709 | 0.002478 | -0.0031744 | 0.00013254 | 0.048828 | -0.00071785 | -0.012525 | -0.0052979 | -0.0071864 | 0.010079 | -0.0018136 | -0.013733 | 0.11444 | -0.068665 | -0.082397 | 0.082397 | -0.082397 | -0.018311 | -0.059509 | 0.09613 | -0.11444 | -0.013733 | 0.082397 | 0.018311 | 0.082397 | 60.9512 | -61.084 | -61.2808 | 61.1023 | 61.0016 | 60.9375 | 0.050354 | -0.013732 | 60.9055 | -61.1023 | -61.2122 | 61.1023 | 61.1023 | 61.0382 | 0.19684 | 0.13275 | 0.15106 | -0.013732 | 0.19684 | 0.10071 | 0.18311 | 0.21057 | 61.1343 | 61.116 | -61.2671 | -61.3129 | 60.9375 | 61.0062 | 61.0062 | 60.9604
1782.3125 | 122.5067 | -61.0107 | 61.2213 | 0.048599 | 0.0079618 | -0.0056247 | -0.094214 | -0.00072638 | -0.0048834 | -0.00072206 | 0.030518 | -0.0022131 | -0.013379 | -0.0014525 | -0.008468 | 0.0092241 | -0.0043772 | -0.004578 | 0.14191 | -0.068665 | 0.018311 | 0.10986 | 0.004578 | 0.091553 | 0.050354 | 0.12817 | -0.086975 | 0.050354 | 0.15564 | 0.09613 | 0.11444 | 60.9421 | -61.0794 | -61.203 | 61.1206 | 61.1023 | 61.0153 | 0.16022 | 0.073243 | 60.9238 | -61.0931 | -61.171 | 61.1664 | 61.1252 | 61.1069 | 0.20142 | 0.1831 | 0.17853 | 0.086976 | 0.24261 | 0.13733 | 0.21057 | 0.21515 | 61.1526 | 61.1389 | -61.29 | -61.3083 | 61.0291 | 61.0611 | 61.0062 | 61.0611
1783.3125 | 122.5525 | -61.0107 | 61.2259 | 0.048599 | 0.0077482 | -0.0064793 | -0.095923 | -0.00093998 | -0.005738 | -0.0020039 | 0.033569 | -0.0019995 | -0.011884 | 4.2656e-05 | -0.0095362 | 0.010933 | 0.0007498 | 0.022888 | 0.11902 | -0.059509 | 0.032043 | 0.1236 | 0.018311 | 0.082397 | 0.064087 | 0.15564 | -0.068665 | 0.059509 | 0.16022 | 0.10529 | 0.12817 | 60.9512 | -61.1069 | -61.1938 | 61.1343 | 61.0931 | 61.0291 | 0.14191 | 0.07782 | 60.9421 | -61.0703 | -61.1664 | 61.171 | 61.1389 | 61.116 | 0.19684 | 0.17395 | 0.1831 | 0.091552 | 0.22888 | 0.12817 | 0.17853 | 0.22431 | 61.1298 | 61.1664 | -61.2854 | -61.2946 | 61.0428 | 61.0703 | 61.0336 | 61.0748
1784.3125 | 122.4243 | -61.0474 | 61.2488 | 0.12489 | 0.00668 | -0.0071201 | -0.095282 | -0.0058532 | -0.005738 | 0.0046185 | -0.07019 | -0.0019995 | -0.0093204 | -0.0040161 | -0.010177 | 0.011574 | -0.0016 | -0.032043 | 0.16479 | -0.09613 | -0.19684 | -0.07782 | 0.054932 | 0.032043 | 0.004578 | 0.2243 | -0.068665 | -0.027466 | 0.073242 | -0.004578 | 0.068665 | 60.9512 | -61.084 | -61.4456 | 60.9695 | 61.0794 | 61.1023 | 0.12817 | 0.15106 | 60.9787 | -61.0245 | -61.2762 | 61.1206 | 61.116 | 61.0428 | 0.13733 | 0.064087 | 0.01831 | -0.10071 | 0.14191 | 0.041199 | 0.26092 | 0.29297 | 61.2122 | 61.2717 | -61.3449 | -61.3174 | 60.8505 | 61.0199 | 61.0153 | 61.0519
1785.3125 | 122.525 | -61.0382 | 61.2122 | 0.048599 | 0.0039028 | -0.0071201 | -0.095069 | -0.00029898 | -0.0042426 | -0.00050846 | 0.012207 | -0.0019995 | -0.011457 | -0.010425 | -0.010177 | 0.010506 | -0.0009592 | -0.013733 | 0.10986 | -0.068665 | -0.004578 | 0.086975 | -0.009155 | 0.050354 | 0.018311 | 0.13275 | -0.091553 | 0.041199 | 0.14191 | 0.068665 | 0.10071 | 60.9695 | -61.1023 | -61.2167 | 61.1252 | 61.0886 | 61.0291 | 0.11902 | 0.05951 | 60.9467 | -61.0794 | -61.171 | 61.1801 | 61.1389 | 61.1069 | 0.19226 | 0.16022 | 0.15564 | 0.064087 | 0.23346 | 0.13275 | 0.17853 | 0.2243 | 61.1481 | 61.171 | -61.2808 | -61.3037 | 61.0336 | 61.0794 | 61.0245 | 61.0565
1786.3125 | 122.5388 | -60.997 | 61.2122 | 0.102 | 0.008389 | -0.0049839 | -0.094428 | -0.0035034 | -0.0059516 | -0.0034991 | 0.0030517 | -0.0015723 | -0.010175 | -0.0018799 | -0.011459 | 0.011361 | -0.0024546 | 0.1831 | 0.11902 | -0.054932 | 0.004578 | 0.16022 | 0.073242 | 0.07782 | 0.15106 | 0.1236 | -0.073242 | 0.082397 | 0.21057 | 0.11444 | 0.15564 | 60.9421 | -61.0931 | -61.2076 | 61.1572 | 61.0748 | 61.0703 | 0.13275 | 0.12817 | 60.9238 | -61.0886 | -61.1298 | 61.2076 | 61.1526 | 61.1114 | 0.22888 | 0.18768 | 0.21515 | 0.05951 | 0.28381 | 0.15564 | 0.17395 | 0.19684 | 61.116 | 61.1206 | -61.2671 | -61.2854 | 61.0016 | 61.0794 | 61.1801 | 61.1481
1787.3125 | 122.5708 | -61.0107 | 61.2167 | 0.079117 | 0.0079618 | -0.0079745 | -0.096137 | -0.00093998 | -0.005738 | -0.0030719 | 0.024414 | -0.0030677 | -0.012097 | -0.0012389 | -0.0086816 | 0.0098651 | -0.0041636 | -0.009155 | 0.082397 | -0.059509 | 0.07782 | 0.15564 | 0.045776 | 0.13275 | 0.13275 | 0.14191 | -0.059509 | 0.073242 | 0.20142 | 0.12817 | 0.15564 | 60.9512 | -61.1343 | -61.1389 | 61.1664 | 61.1435 | 61.0565 | 0.19226 | 0.10528 | 60.9512 | -61.0748 | -61.1435 | 61.2122 | 61.1664 | 61.1389 | 0.21515 | 0.18768 | 0.21515 | 0.13733 | 0.26093 | 0.13275 | 0.14191 | 0.20142 | 61.0931 | 61.1526 | -61.2762 | -61.2762 | 61.0886 | 61.084 | 61.0016 | 61.1435
1788.3125 | 122.5296 | -61.0107 | 61.2396 | 0.063858 | 0.0056118 | -0.0062655 | -0.094214 | -0.0022218 | -0.005738 | -0.0024311 | 0.030518 | -0.0011451 | -0.0082522 | -0.0042297 | -0.0093226 | 0.0092241 | -0.0013864 | 0.041199 | 0.091553 | -0.041199 | 0.082397 | 0.16479 | 0.041199 | 0.091553 | 0.13733 | 0.15564 | -0.045776 | 0.082397 | 0.20599 | 0.11902 | 0.15564 | 60.9695 | -61.1481 | -61.1572 | 61.1755 | 61.1023 | 61.0519 | 0.13275 | 0.082398 | 60.965 | -61.084 | -61.1572 | 61.2167 | 61.1664 | 61.1298 | 0.20142 | 0.16479 | 0.20599 | 0.1236 | 0.25177 | 0.12817 | 0.13275 | 0.20142 | 61.1023 | 61.1664 | -61.2808 | -61.2854 | 61.0931 | 61.0931 | 61.0519 | 61.1481
1789.3125 | 122.438 | -61.0382 | 61.2442 | 0.11726 | 0.0064664 | -0.0064793 | -0.092291 | -0.00029898 | -0.004029 | -0.0013629 | -0.094604 | -0.0017859 | -0.01167 | 0.0023927 | -0.010177 | 0.011788 | -0.0022408 | -0.009155 | 0.11902 | -0.082397 | -0.041199 | 0.018311 | -0.09613 | -0.022888 | -0.041199 | 0.14191 | -0.10071 | -0.050354 | 0.013733 | -0.086975 | 0.004578 | 60.9558 | -61.1252 | -61.2854 | 61.0565 | 61.0153 | 60.9421 | 0.059509 | -0.013733 | 60.9375 | -61.1023 | -61.2946 | 61.0519 | 61.0428 | 60.9512 | 0.10529 | 0.013733 | 0.10071 | 0.041198 | 0.11444 | 0.050354 | 0.20142 | 0.24262 | 61.1572 | 61.1801 | -61.3266 | -61.3449 | 60.997 | 60.9879 | 61.0291 | 60.997
1790.3125 | 122.4426 | -61.0291 | 61.2762 | 0.094376 | 0.0075344 | -0.0056247 | -0.094428 | -8.538e-05 | -0.0046698 | 0.00055974 | -0.0061035 | -0.00050405 | -0.009534 | -0.0038025 | -0.0078272 | 0.012001 | -0.0018136 | 0.013733 | 0.15106 | -0.064087 | -0.041199 | 0.041199 | -0.032043 | 0.036621 | -0.018311 | 0.21515 | -0.054932 | 0 | 0.10071 | 0.018311 | 0.068665 | 60.965 | -61.1252 | -61.3174 | 61.0703 | 61.0657 | 60.997 | 0.10071 | 0.032044 | 60.9741 | -61.0611 | -61.2762 | 61.1298 | 61.0977 | 61.0474 | 0.1236 | 0.073243 | 0.10529 | 0.022888 | 0.15564 | 0.054932 | 0.21515 | 0.27008 | 61.1801 | 61.2442 | -61.3403 | -61.3312 | 60.9879 | 61.0291 | 61.0428 | 61.0107
1791.3125 | 122.493 | -61.0336 | 61.2534 | 0.079117 | 0.0086026 | -0.0047703 | -0.097846 | -0.00051278 | -0.0031744 | -0.0020039 | 0.0091553 | -0.00071785 | -0.010602 | -0.0040161 | -0.0086816 | 0.012642 | 0.000109 | 0.036621 | 0.1236 | -0.036621 | 0.032043 | 0.12817 | 0.036621 | 0.073242 | 0.082397 | 0.16937 | -0.032043 | 0.050354 | 0.17395 | 0.064087 | 0.11902 | 60.997 | -61.1298 | -61.2213 | 61.1618 | 61.1069 | 61.0703 | 0.10986 | 0.073242 | 61.0016 | -61.084 | -61.203 | 61.2076 | 61.1526 | 61.0977 | 0.15106 | 0.09613 | 0.1648 | 0.068664 | 0.20599 | 0.082397 | 0.16022 | 0.20142 | 61.1572 | 61.203 | -61.29 | -61.2854 | 61.0657 | 61.084 | 61.0703 | 61.116
1792.3125 | 122.4747 | -61.0062 | 61.2579 | 0.102 | 0.008389 | -0.0041293 | -0.094855 | 0.00076902 | -0.0053108 | -0.0015765 | 0.027466 | -0.00050405 | -0.0091068 | 4.2656e-05 | -0.009109 | 0.010079 | 0.001177 | 0.032043 | 0.1236 | -0.054932 | 0.022888 | 0.11444 | 0.013733 | 0.064087 | 0.068665 | 0.1831 | -0.041199 | 0.032043 | 0.13275 | 0.054932 | 0.09613 | 60.9512 | -61.1343 | -61.235 | 61.1206 | 61.0703 | 61.0199 | 0.11902 | 0.068665 | 60.965 | -61.0748 | -61.2259 | 61.1389 | 61.1023 | 61.0611 | 0.13733 | 0.096131 | 0.16937 | 0.07782 | 0.17395 | 0.073242 | 0.17853 | 0.2243 | 61.1298 | 61.1893 | -61.3129 | -61.2991 | 61.0291 | 61.0382 | 61.0382 | 61.0748
1793.3125 | 122.4472 | -61.0428 | 61.2671 | 0.094376 | 0.0058256 | -0.0058383 | -0.093787 | 0.0026916 | -0.0018928 | -0.0028583 | -0.0061035 | -0.00093145 | -0.011457 | -0.0082885 | -0.006759 | 0.0090105 | 0.0003226 | -0.018311 | 0.17853 | -0.068665 | -0.15106 | 0.073242 | 0.004578 | -0.018311 | -0.004578 | 0.21973 | -0.054932 | -0.013733 | 0.082397 | 0.009155 | 0.059509 | 60.9741 | -61.0886 | -61.4182 | 61.116 | 61.0245 | 61.0474 | 0.050354 | 0.073243 | 60.9879 | -61.0474 | -61.2808 | 61.1252 | 61.1023 | 61.0519 | 0.11444 | 0.064087 | 0.14191 | -0.082397 | 0.13733 | 0.041199 | 0.24719 | 0.27466 | 61.2213 | 61.2625 | -61.3358 | -61.322 | 60.8917 | 61.0291 | 61.0245 | 61.0382
1794.3125 | 122.4426 | -61.0474 | 61.2762 | 0.010452 | 0.0073208 | -0.0077609 | -0.093573 | -0.003717 | -0.0046698 | -0.0041401 | -0.030517 | 0.00013675 | -0.010388 | -0.0025207 | -0.006759 | 0.011361 | 0.001177 | 0 | 0.20599 | -0.050354 | -0.082397 | 0.018311 | -0.059509 | 0.018311 | 0.004578 | 0.20599 | -0.07782 | -0.009155 | 0.091553 | 0 | 0.07782 | 60.997 | -61.0703 | -61.3586 | 61.0657 | 61.0657 | 60.9879 | 0.068665 | -0.009155 | 60.9695 | -61.0703 | -61.2854 | 61.1389 | 61.1252 | 61.0474 | 0.15564 | 0.07782 | 0.068665 | -0.032043 | 0.16937 | 0.068665 | 0.25635 | 0.28381 | 61.2534 | 61.2534 | -61.3266 | -61.3541 | 60.965 | 61.0382 | 61.0474 | 61.0519
1795.3125 | 122.4518 | -61.0474 | 61.2717 | 0.079117 | 0.0068936 | -0.0066929 | -0.092932 | -0.00093998 | -0.005738 | -0.0039265 | -0.01831 | 0.00077755 | -0.010175 | -0.0044433 | -0.0082544 | 0.011147 | 0.0005362 | -0.027466 | 0.16479 | -0.07782 | -0.054932 | 0.018311 | -0.07782 | 0.009155 | -0.027466 | 0.19684 | -0.064087 | -0.013733 | 0.07782 | -0.009155 | 0.068665 | 60.9695 | -61.1069 | -61.3266 | 61.0657 | 61.0565 | 60.9695 | 0.086975 | 0 | 60.9833 | -61.0748 | -61.2854 | 61.1252 | 61.116 | 61.0382 | 0.13275 | 0.054932 | 0.096131 | 0.022888 | 0.14191 | 0.050354 | 0.24261 | 0.26093 | 61.2122 | 61.2442 | -61.3495 | -61.3358 | 60.9924 | 61.0336 | 61.0199 | 61.0199
1796.3125 | 122.4747 | -61.0474 | 61.2808 | 0.13252 | 0.0058256 | -0.0066929 | -0.09336 | -0.00072638 | -0.005738 | -0.00093566 | -0.036621 | -0.00071785 | -0.0099612 | -0.0082885 | -0.0093226 | 0.011788 | -0.0011728 | -0.018311 | 0.17395 | -0.086975 | -0.068665 | 0.018311 | -0.07782 | 0 | -0.022888 | 0.21515 | -0.064087 | -0.009155 | 0.10071 | -0.009155 | 0.054932 | 60.9604 | -61.1069 | -61.3495 | 61.0657 | 61.0474 | 60.9695 | 0.086975 | 0.009155 | 60.9833 | -61.0657 | -61.29 | 61.1481 | 61.1023 | 61.0382 | 0.11902 | 0.054932 | 0.10529 | 0.01831 | 0.1648 | 0.054932 | 0.26092 | 0.27924 | 61.2213 | 61.2625 | -61.3678 | -61.3449 | 60.9787 | 61.0382 | 61.0291 | 61.0245
1797.3125 | 122.4747 | -61.0336 | 61.2671 | 0.102 | 0.0060392 | -0.0060519 | -0.095282 | -0.0015808 | -0.0072334 | -0.00029486 | -0.015259 | -0.00093145 | -0.0084658 | -0.0050841 | -0.006759 | 0.012856 | -0.0007456 | -0.013733 | 0.16022 | -0.064087 | -0.054932 | 0.032043 | -0.059509 | -0.013733 | -0.027466 | 0.20599 | -0.07782 | -0.004578 | 0.091553 | 0.004578 | 0.07782 | 60.9695 | -61.1069 | -61.322 | 61.0657 | 61.0199 | 60.9741 | 0.050354 | 0.004578 | 60.9558 | -61.0611 | -61.2717 | 61.1252 | 61.1115 | 61.0382 | 0.15564 | 0.082398 | 0.09613 | 0.009155 | 0.16937 | 0.073242 | 0.2243 | 0.28381 | 61.1938 | 61.2396 | -61.3312 | -61.3449 | 60.9787 | 61.0291 | 61.0199 | 61.0062
1798.3125 | 122.4792 | -61.0382 | 61.29 | 0.086746 | 0.0079618 | -0.0056247 | -0.094428 | -0.0013672 | -0.005738 | -0.0034991 | -0.015259 | -0.0019995 | -0.011884 | -0.0033751 | -0.008468 | 0.01072 | -0.0026682 | -0.027466 | 0.16937 | -0.086975 | -0.054932 | 0.013733 | -0.068665 | -0.004578 | -0.013733 | 0.21515 | -0.091553 | 0.004578 | 0.091553 | 0.032043 | 0.10071 | 60.9512 | -61.1206 | -61.3449 | 61.0519 | 61.0336 | 60.9695 | 0.082397 | 0.01831 | 60.9467 | -61.0748 | -61.2854 | 61.1298 | 61.1389 | 61.0703 | 0.19226 | 0.1236 | 0.10071 | 0.032043 | 0.18311 | 0.096131 | 0.25635 | 0.3067 | 61.2076 | 61.2534 | -61.377 | -61.3815 | 60.9833 | 61.0428 | 61.0107 | 61.0245
1799.3125 | 122.5067 | -61.0611 | 61.2671 | 0.094376 | 0.0062528 | -0.0043429 | -0.09336 | 0.0033324 | -0.0031744 | -0.0017903 | -0.039673 | -0.00071785 | -0.0084658 | -0.0040161 | -0.0080408 | 0.012001 | -0.0056588 | 0.027466 | 0.1236 | -0.086975 | -0.032043 | 0.073242 | -0.041199 | 0.018311 | 0.027466 | 0.16022 | -0.09613 | -0.11444 | -0.1236 | 0.20599 | 0.24719 | 60.9741 | -61.1435 | -61.2991 | 61.1343 | 61.0794 | 61.0199 | 0.10529 | 0.045776 | 60.965 | -61.1069 | -61.3815 | 60.9375 | 61.3083 | 61.2671 | 0.34332 | 0.30212 | 0.16022 | 0.054932 | -0.027466 | -0.018311 | 0.21057 | 0.25635 | 61.1847 | 61.2213 | -61.3541 | -61.3632 | 61.0291 | 60.9467 | 61.0886 | 61.0886
1800.3125 | 122.493 | -61.0474 | 61.2808 | 0.094376 | 0.0056118 | -0.0064793 | -0.094428 | 0.00098262 | -0.0044562 | -0.0015765 | -0.0091553 | -0.0017859 | -0.009534 | -0.0082885 | -0.0071864 | 0.010292 | -0.0013864 | 0 | 0.14648 | -0.082397 | -0.054932 | 0.022888 | -0.059509 | 0.009155 | 0 | 0.1831 | -0.064087 | 0.013733 | 0.10529 | 0.004578 | 0.09613 | 60.965 | -61.1343 | -61.3358 | 61.0703 | 61.0565 | 60.9879 | 0.091552 | 0.022888 | 60.9833 | -61.0977 | -61.2671 | 61.1526 | 61.1435 | 61.0519 | 0.16022 | 0.068665 | 0.10528 | 0.027465 | 0.16937 | 0.07782 | 0.22888 | 0.24719 | 61.1938 | 61.2305 | -61.3632 | -61.3449 | 60.9924 | 61.0611 | 61.0474 | 61.0474
1801.3125 | 122.4884 | -61.0565 | 61.29 | 0.079117 | 0.0068936 | -0.0045567 | -0.09336 | 0.00012822 | -0.004029 | -0.00072206 | -0.024414 | -0.00029045 | -0.011243 | -0.0014525 | -0.0095362 | 0.012429 | -0.0022408 | 0 | 0.10529 | -0.082397 | -0.036621 | 0.050354 | -0.068665 | -0.009155 | -0.032043 | 0.14648 | -0.091553 | -0.032043 | 0.054932 | -0.064087 | 0.036621 | 60.9741 | -61.1847 | -61.3266 | 61.1069 | 61.0474 | 60.9879 | 0.073242 | 0.013732 | 60.965 | -61.1435 | -61.322 | 61.1115 | 61.0931 | 60.9924 | 0.12817 | 0.027466 | 0.13275 | 0.045776 | 0.14649 | 0.05951 | 0.18768 | 0.23804 | 61.1618 | 61.203 | -61.3724 | -61.3815 | 61.0199 | 61.0245 | 61.0565 | 61.0245
1802.3125 | 122.5021 | -61.0565 | 61.2488 | 0.056229 | 0.0096708 | -0.0066929 | -0.092291 | 0.0014098 | -0.005738 | -0.0060627 | -8.6e-08 | -0.0015723 | -0.010175 | 0.00047006 | -0.0080408 | 0.010292 | 0.001818 | 0.009155 | 0.14648 | -0.082397 | 0.091553 | 0.19226 | -0.050354 | 0.022888 | 0.009155 | 0.16937 | -0.073242 | 0 | 0.086975 | -0.004578 | 0.068665 | 60.9741 | -61.1023 | -61.1572 | 61.2488 | 61.0794 | 61.0062 | 0.10528 | 0.032043 | 60.9833 | -61.0794 | -61.2488 | 61.1435 | 61.1252 | 61.0519 | 0.14191 | 0.068664 | 0.27466 | 0.17395 | 0.16022 | 0.073242 | 0.22888 | 0.24261 | 61.203 | 61.2259 | -61.3312 | -61.322 | 61.1481 | 61.0565 | 61.0657 | 61.0657
1803.3125 | 122.5067 | -61.0611 | 61.2488 | 0.102 | 0.0086026 | -0.0051975 | -0.094214 | 0.0022644 | -0.003388 | 0.00034614 | -0.015259 | -0.0019995 | -0.0071842 | -0.0046569 | -0.010177 | 0.010933 | -0.0009592 | 0.07782 | 0.10071 | -0.07782 | -0.027466 | 0.11444 | -0.054932 | 0.013733 | 0.013733 | 0.17853 | -0.082397 | -0.013733 | 0.082397 | -0.022888 | 0.064087 | 60.9833 | -61.1481 | -61.2762 | 61.1755 | 61.0748 | 61.0062 | 0.091553 | 0.022888 | 60.9787 | -61.0703 | -61.2625 | 61.1435 | 61.1252 | 61.0382 | 0.14648 | 0.059509 | 0.19226 | 0.050354 | 0.16479 | 0.068664 | 0.17853 | 0.26092 | 61.1618 | 61.2396 | -61.3266 | -61.3312 | 61.0336 | 61.0474 | 61.1389 | 61.0748
1804.3125 | 122.5433 | -61.0611 | 61.2213 | 0.079117 | 0.0081754 | -0.0034885 | -0.095496 | 0.0022644 | -0.0046698 | -0.0032855 | 0.0030517 | -0.0026405 | -0.007825 | -0.011066 | -0.009109 | 0.0098651 | 0.0007498 | -0.054932 | 0.13275 | -0.082397 | -0.082397 | 0.013733 | -0.10986 | -0.009155 | -0.064087 | 0.09613 | -0.13275 | -0.032043 | 0.041199 | -0.059509 | 0.045776 | 60.9787 | -61.0886 | -61.3037 | 61.0748 | 61.0519 | 60.9512 | 0.073242 | -0.027466 | 60.9283 | -61.1252 | -61.2534 | 61.1023 | 61.1069 | 61.0016 | 0.17853 | 0.073242 | 0.09613 | 0 | 0.17395 | 0.10071 | 0.21515 | 0.22888 | 61.1938 | 61.1572 | -61.3037 | -61.3541 | 60.9787 | 61.0291 | 61.0062 | 60.997
1805.3125 | 122.493 | -61.0565 | 61.2717 | 0.063858 | 0.0081754 | -0.0054111 | -0.094428 | 0.0011962 | -0.0061652 | -0.0015765 | -0.0091553 | -0.0013587 | -0.009534 | -0.0027343 | -0.0086816 | 0.012215 | -0.0003182 | 0.032043 | 0.19226 | -0.045776 | -0.018311 | 0.091553 | -0.059509 | 0.009155 | 0.013733 | 0.15564 | -0.068665 | -0.022888 | 0.064087 | -0.022888 | 0.064087 | 61.0107 | -61.0794 | -61.29 | 61.1481 | 61.0657 | 60.997 | 0.054931 | -0.013733 | 60.9879 | -61.116 | -61.2946 | 61.1206 | 61.1206 | 61.0336 | 0.13275 | 0.045777 | 0.13733 | 0.027465 | 0.13275 | 0.045777 | 0.23804 | 0.22431 | 61.2488 | 61.2122 | -61.3174 | -61.3403 | 61.0382 | 61.0336 | 61.0886 | 61.0703
1806.3125 | 122.5021 | -61.0519 | 61.2671 | 0.15541 | 0.0071072 | -0.0062655 | -0.094214 | 0.0020508 | -0.0036018 | -0.0011493 | -0.01831 | -0.0019995 | -0.010816 | -0.0020935 | -0.008468 | 0.011147 | -0.0024546 | 0.018311 | 0.1831 | -0.013733 | -0.027466 | 0.07782 | -0.041199 | 0.013733 | 0.013733 | 0.14648 | -0.082397 | -0.009155 | 0.073242 | -0.032043 | 0.054932 | 61.0382 | -61.084 | -61.2946 | 61.1298 | 61.0657 | 61.0107 | 0.027466 | -0.027466 | 60.9695 | -61.1206 | -61.2762 | 61.1252 | 61.1069 | 61.0199 | 0.13733 | 0.050354 | 0.091553 | -0.013733 | 0.15564 | 0.073242 | 0.19684 | 0.22888 | 61.235 | 61.1984 | -61.2808 | -61.3495 | 61.0245 | 61.0428 | 61.0703 | 61.0657
1807.3125 | 122.4564 | -61.0748 | 61.2762 | 0.10963 | 0.0056118 | -0.0049839 | -0.092078 | 0.0014098 | -0.0042426 | -0.0011493 | -0.0091553 | -0.00093145 | -0.011884 | -0.0014525 | -0.0088952 | 0.012856 | 0.0003226 | -0.032043 | 0.11902 | -0.09613 | -0.068665 | 0.022888 | -0.10071 | -0.032043 | -0.073242 | 0.15564 | -0.11902 | -0.064087 | 0.004578 | -0.10071 | 0 | 60.9787 | -61.1572 | -61.3449 | 61.0977 | 61.0428 | 60.9741 | 0.064087 | -0.004578 | 60.9558 | -61.1206 | -61.3403 | 61.0794 | 61.0748 | 60.9741 | 0.11902 | 0.018311 | 0.11902 | 0.027465 | 0.1236 | 0.054932 | 0.21515 | 0.27466 | 61.1938 | 61.2305 | -61.3724 | -61.3953 | 61.0062 | 61.0107 | 61.0428 | 61.0016
1808.3125 | 122.5067 | -61.0519 | 61.2579 | 0.063858 | 0.0088162 | -0.0071201 | -0.095282 | 0.002478 | -0.0042426 | -0.0039265 | 0.0091553 | -0.00029045 | -0.010175 | -0.00059814 | -0.0086816 | 0.010079 | 0.0020316 | 0 | 0.16022 | -0.059509 | -0.027466 | 0.082397 | -0.045776 | 0.018311 | -0.004578 | 0.16937 | -0.091553 | -0.018311 | 0.064087 | -0.045776 | 0.050354 | 60.9924 | -61.0977 | -61.2854 | 61.1343 | 61.0703 | 61.0062 | 0.07782 | 0.013733 | 60.9604 | -61.0886 | -61.2762 | 61.116 | 61.1023 | 61.0062 | 0.14191 | 0.045777 | 0.14191 | 0.032043 | 0.15564 | 0.073242 | 0.21973 | 0.26093 | 61.2122 | 61.2213 | -61.3174 | -61.3495 | 61.0245 | 61.0336 | 61.0519 | 61.0474
1809.3125 | 122.5662 | -61.0199 | 61.2305 | 0.025711 | 0.0073208 | -0.0032749 | -0.096778 | 0.00012822 | -0.0027472 | -0.0069171 | 0.091553 | -0.0017859 | -0.0084658 | -0.0087157 | -0.0080408 | 0.0098651 | 0.003527 | 0.004578 | 0.09613 | -0.050354 | 0.009155 | 0.1236 | -0.013733 | 0.073242 | 0.032043 | 0.073242 | -0.11444 | -0.018311 | 0.09613 | -0.004578 | 0.045776 | 60.9695 | -61.1343 | -61.2213 | 61.1435 | 61.0931 | 61.0062 | 0.1236 | 0.036621 | 60.9055 | -61.1572 | -61.2488 | 61.116 | 61.0657 | 61.0153 | 0.16022 | 0.10986 | 0.17395 | 0.059509 | 0.21057 | 0.09613 | 0.14648 | 0.18768 | 61.116 | 61.0931 | -61.2808 | -61.3449 | 61.0291 | 61.0016 | 61.0245 | 61.0519
1810.3125 | 122.4701 | -61.084 | 61.2579 | 0.079117 | 0.0060392 | -0.0054111 | -0.091864 | 0.0018372 | -0.0059516 | -0.00072206 | -0.036621 | 0.00099115 | -0.0093204 | -0.0023071 | -0.009109 | 0.011788 | 0.0009634 | -0.068665 | 0.1236 | -0.10071 | -0.1831 | -0.24719 | 0.1236 | 0.2243 | -0.10529 | 0.10986 | -0.11444 | -0.10071 | -0.059509 | -0.11902 | 0 | 60.9833 | -61.1343 | -61.441 | 60.8368 | 61.3083 | 61.2076 | 0.32501 | 0.2243 | 60.9695 | -61.1481 | -61.3586 | 61.0245 | 61.084 | 60.965 | 0.11444 | -0.004578 | -0.14648 | -0.082397 | 0.054932 | 0.013733 | 0.2243 | 0.2243 | 61.2076 | 61.1938 | -61.3586 | -61.3724 | 60.9009 | 60.9833 | 61.0153 | 60.9787
1811.3125 | 122.4609 | -61.0748 | 61.2808 | 0.056229 | 0.0071072 | -0.0062655 | -0.093146 | -0.0011536 | -0.0018928 | -0.0041401 | -0.01831 | -0.0013587 | -0.0097476 | -0.0087157 | -0.0095362 | 0.011788 | 0.0041678 | -0.022888 | 0.11902 | -0.09613 | -0.086975 | -0.018311 | -0.10071 | -0.045776 | -0.10529 | 0.13733 | -0.1236 | -0.11902 | -0.041199 | -0.1236 | 0 | 60.9787 | -61.1618 | -61.3678 | 61.0565 | 61.0291 | 60.9741 | 0.050354 | -0.004578 | 60.9512 | -61.1435 | -61.3998 | 61.0336 | 61.0748 | 60.9512 | 0.1236 | 0 | 0.077819 | 0.009155 | 0.082397 | 0.004577 | 0.21515 | 0.26093 | 61.1938 | 61.2122 | -61.377 | -61.4044 | 60.9879 | 60.9558 | 61.0519 | 60.9695
1812.3125 | 122.4518 | -61.0611 | 61.2625 | 0.079117 | 0.0075344 | -0.0049839 | -0.096137 | 0.00055542 | -0.0038154 | 0.0016277 | -0.024414 | 0.0012047 | -0.0091068 | 0.00047006 | -0.010391 | 0.014138 | -0.0028818 | -0.041199 | 0.1236 | -0.091553 | -0.091553 | -0.022888 | -0.11902 | -0.054932 | -0.10986 | 0.13733 | -0.11902 | -0.10071 | -0.022888 | -0.13275 | -0.045776 | 60.9695 | -61.1389 | -61.3541 | 61.0382 | 61.0062 | 60.9421 | 0.036621 | -0.027466 | 60.9421 | -61.1252 | -61.3632 | 61.0382 | 61.0153 | 60.9283 | 0.073243 | -0.013732 | 0.068665 | 0 | 0.096131 | 0.018311 | 0.21515 | 0.25635 | 61.1847 | 61.1984 | -61.3541 | -61.3815 | 60.9695 | 60.9604 | 61.0199 | 60.9512
1813.3125 | 122.4564 | -61.084 | 61.2762 | 0.048599 | 0.0081754 | -0.0045567 | -0.092719 | 0.0011962 | -0.0048834 | -0.0022175 | -0.01831 | -0.0013587 | -0.008893 | 0.0013245 | -0.0093226 | 0.012642 | -0.0007456 | -0.027466 | 0.15106 | -0.091553 | -0.10529 | -0.027466 | -0.11444 | -0.036621 | -0.1236 | 0.12817 | -0.1236 | -0.09613 | -0.032043 | -0.13275 | -0.036621 | 60.9924 | -61.1252 | -61.3815 | 61.0565 | 61.0474 | 60.9695 | 0.054932 | -0.022888 | 60.9604 | -61.1481 | -61.3724 | 61.0519 | 61.0474 | 60.9512 | 0.086975 | -0.009155 | 0.064087 | -0.013733 | 0.091553 | 0.027466 | 0.24261 | 0.25177 | 61.235 | 61.2122 | -61.3678 | -61.3998 | 60.9787 | 60.9879 | 61.0565 | 60.9604
1814.3125 | 122.5983 | -61.0245 | 61.235 | 0.04097 | 0.00668 | -0.0041293 | -0.095069 | 0.0018372 | -0.005097 | -0.0013629 | 0.048828 | -7.6854e-05 | -0.010175 | -0.0052979 | -0.0076136 | 0.012429 | -0.0009592 | -0.018311 | 0.09613 | -0.07782 | -0.004578 | 0.086975 | -0.045776 | 0.054932 | -0.013733 | 0.054932 | -0.12817 | 0 | 0.10071 | -0.009155 | 0.07782 | 60.9467 | -61.1389 | -61.2396 | 61.1115 | 61.0794 | 60.9787 | 0.13275 | 0.032044 | 60.8963 | -61.1801 | -61.235 | 61.1252 | 61.1023 | 61.0153 | 0.20599 | 0.11902 | 0.16479 | 0.073242 | 0.22888 | 0.12817 | 0.17395 | 0.18311 | 61.1206 | 61.0794 | -61.3129 | -61.3632 | 61.0199 | 61.0245 | 61.0062 | 61.0107
1815.3125 | 122.4655 | -61.0748 | 61.2534 | 0.086746 | 0.0068936 | -0.0054111 | -0.096991 | -8.538e-05 | -0.0027472 | -0.00050846 | -0.0061035 | 0.00056395 | -0.0071842 | 0.00025626 | -0.0088952 | 0.010933 | 0.001177 | 0.073242 | 0.13275 | -0.09613 | -0.13733 | 0.036621 | -0.10071 | -0.068665 | -0.10986 | 0.12817 | -0.10986 | -0.10529 | -0.013733 | -0.11444 | 0 | 60.9787 | -61.1206 | -61.3907 | 61.1114 | 61.0062 | 60.9741 | 0.027465 | -0.004578 | 60.965 | -61.1252 | -61.3586 | 61.0611 | 61.0748 | 60.9604 | 0.10986 | -0.004578 | 0.13275 | -0.041199 | 0.09613 | 0.004577 | 0.22888 | 0.23804 | 61.2076 | 61.203 | -61.3495 | -61.3632 | 60.9375 | 60.9695 | 61.1481 | 60.965
1816.3125 | 122.612 | -61.0382 | 61.2579 | 0.04097 | 0.0090298 | -0.0058383 | -0.097205 | -0.0011536 | -0.0029608 | -0.0013629 | 0.13733 | -0.00093145 | -0.0073978 | -0.0091431 | -0.0088952 | 0.010079 | 0.0005362 | 0.032043 | 0.11902 | -0.041199 | 0.036621 | 0.19226 | 0.045776 | 0.32044 | -0.30212 | 0.19226 | -0.018311 | 0.091553 | 0.16937 | 0.12817 | 0.16022 | 60.997 | -61.1389 | -61.2213 | 61.2305 | 61.3586 | 61.084 | 0.36163 | 0.086975 | 61.0199 | -61.0657 | -61.1664 | 61.2076 | 61.1984 | 61.1664 | 0.17853 | 0.14649 | 0.23346 | 0.07782 | 0.18768 | 0.10986 | 0.16022 | 0.21057 | 61.1572 | 61.2305 | -61.2991 | -61.2762 | 61.0748 | 61.1298 | 61.0703 | 60.7361
1817.3125 | 122.5342 | -61.0657 | 61.2534 | 0.056229 | 0.0064664 | -0.0045567 | -0.094428 | 0.0014098 | -0.0044562 | -0.0013629 | 0.0030517 | -0.0017859 | -0.012311 | -0.0055115 | -0.0097498 | 0.012642 | -0.0030954 | -0.059509 | 0.12817 | -0.10529 | -0.086975 | 0.004578 | -0.10071 | -0.009155 | -0.064087 | 0.10071 | -0.13733 | -0.054932 | 0.004578 | -0.07782 | 0.022888 | 60.9604 | -61.1252 | -61.3403 | 61.0703 | 61.0565 | 60.965 | 0.096131 | 0.004578 | 60.9283 | -61.1526 | -61.3083 | 61.0703 | 61.0886 | 60.9879 | 0.16022 | 0.059509 | 0.10986 | 0.018311 | 0.14191 | 0.082397 | 0.23346 | 0.23804 | 61.1938 | 61.1664 | -61.3586 | -61.3907 | 60.9787 | 61.0107 | 61.0062 | 61.0016
1818.3125 | 122.4655 | -61.0703 | 61.2534 | -0.020065 | 0.0051846 | -0.0069065 | -0.091437 | 0.0039734 | -0.0038154 | -0.0015765 | -0.0091553 | -0.0015723 | -0.008893 | -0.00081174 | -0.008468 | 0.011574 | -0.0024546 | 0.10071 | 0.12817 | -0.09613 | -0.10986 | -0.009155 | -0.13733 | -0.068665 | -0.13275 | 0.14648 | -0.12817 | -0.09613 | -0.027466 | -0.1236 | -0.004578 | 60.9741 | -61.1252 | -61.3632 | 61.0611 | 61.0016 | 60.9329 | 0.027465 | -0.041199 | 60.9421 | -61.1069 | -61.3495 | 61.0428 | 61.0657 | 60.9467 | 0.1236 | 0.004578 | 0.086975 | -0.013733 | 0.10071 | 0.032044 | 0.2243 | 0.27466 | 61.1984 | 61.2167 | -61.3495 | -61.3815 | 60.9604 | 60.9741 | 61.171 | 60.9375
1819.3125 | 122.6166 | -61.0199 | 61.2213 | 0.03334 | 0.0079618 | -0.0062655 | -0.096137 | -0.0013672 | -0.0048834 | -0.0032855 | 0.13428 | -0.0028541 | -0.01167 | -0.010852 | -0.010177 | 0.0094379 | 0.005236 | 0.022888 | 0.1236 | -0.032043 | 0.027466 | 0.15106 | 0.054932 | 0.11444 | 0.091553 | 0.13275 | -0.059509 | 0.07782 | 0.20142 | 0.1236 | 0.17853 | 60.9879 | -61.0977 | -61.1938 | 61.171 | 61.1343 | 61.0748 | 0.14648 | 0.086975 | 60.9604 | -61.0886 | -61.1435 | 61.2213 | 61.1984 | 61.1435 | 0.23804 | 0.1831 | 0.18311 | 0.059509 | 0.26093 | 0.13733 | 0.15564 | 0.19226 | 61.1435 | 61.1526 | -61.2534 | -61.2808 | 61.0474 | 61.0977 | 61.0428 | 61.1114
1820.3125 | 122.4838 | -61.0657 | 61.2671 | 0.102 | 0.0077482 | -0.0075473 | -0.092078 | 0.0011962 | -0.0061652 | 0.00077334 | -0.012207 | -0.00093145 | -0.01167 | -0.0027343 | -0.0088952 | 0.010079 | 0.0013906 | -0.032043 | 0.16479 | -0.082397 | -0.10986 | -0.041199 | -0.10986 | -0.045776 | -0.11444 | 0.11902 | -0.13733 | -0.086975 | -0.041199 | -0.12817 | 0 | 60.9833 | -61.1023 | -61.377 | 61.0245 | 61.0199 | 60.9558 | 0.036621 | -0.027466 | 60.9283 | -61.1481 | -61.3541 | 61.0245 | 61.0657 | 60.9375 | 0.13733 | 0.009155 | 0.041198 | -0.027466 | 0.09613 | 0.050354 | 0.24719 | 0.25635 | 61.2305 | 61.1847 | -61.3495 | -61.4044 | 60.9558 | 60.9787 | 61.0336 | 60.9512
1821.3125 | 122.5708 | -61.0428 | 61.2259 | 0.056229 | 0.0068936 | -0.0037021 | -0.095923 | -0.0015808 | -0.005097 | -0.0015765 | 0.10681 | -0.0030677 | -0.010816 | -0.0018799 | -0.0099634 | 0.011147 | -0.0054452 | -0.013733 | 0.1236 | -0.054932 | -0.018311 | 0.082397 | -0.013733 | 0.07782 | 0.027466 | 0.13275 | -0.073242 | 0.018311 | 0.14191 | 0.054932 | 0.10529 | 60.9879 | -61.1023 | -61.2442 | 61.1252 | 61.1206 | 61.0291 | 0.13275 | 0.041199 | 60.9695 | -61.0931 | -61.2076 | 61.1847 | 61.1481 | 61.0977 | 0.17853 | 0.12817 | 0.13733 | 0.036621 | 0.21515 | 0.091553 | 0.17853 | 0.20599 | 61.1664 | 61.1755 | -61.2808 | -61.2991 | 61.0245 | 61.0611 | 61.0291 | 61.0703
1822.3125 | 122.5479 | -61.0703 | 61.2213 | 0.056229 | 0.00668 | -0.0066929 | -0.092505 | 0.0033324 | -0.0016792 | -0.0013629 | -0.0091553 | -0.0013587 | -0.010388 | -0.0072205 | -0.011886 | 0.010292 | 0.0009634 | -0.059509 | 0.11444 | -0.09613 | -0.064087 | 0.004578 | -0.10986 | -0.022888 | -0.07782 | 0.10071 | -0.15564 | -0.041199 | 0.032043 | -0.041199 | 0.036621 | 60.9741 | -61.1069 | -61.2854 | 61.0748 | 61.0474 | 60.9604 | 0.073242 | -0.013733 | 60.9146 | -61.1206 | -61.2625 | 61.1023 | 61.1069 | 61.0291 | 0.19226 | 0.11444 | 0.10071 | 0.032043 | 0.18768 | 0.11444 | 0.21057 | 0.25635 | 61.1847 | 61.171 | -61.3174 | -61.377 | 61.0062 | 61.0291 | 61.0107 | 60.9924
1823.3125 | 122.4884 | -61.0931 | 61.2671 | 0.14778 | 0.0071072 | -0.0064793 | -0.092291 | -0.002649 | -0.003388 | -0.00093566 | -0.045776 | -0.0011451 | -0.012097 | -0.0035889 | -0.0074 | 0.010506 | -0.0003182 | -0.11444 | 0.13275 | -0.091553 | -0.091553 | -0.045776 | -0.13733 | -0.045776 | -0.10071 | 0.12817 | -0.13733 | -0.09613 | -0.036621 | -0.10986 | 0 | 61.0016 | -61.1343 | -61.3586 | 61.0474 | 61.0474 | 60.9558 | 0.045777 | -0.045776 | 60.9558 | -61.1389 | -61.3632 | 61.0565 | 61.0931 | 60.9833 | 0.13733 | 0.027466 | 0.045777 | 0 | 0.10071 | 0.041199 | 0.2243 | 0.2655 | 61.2259 | 61.2213 | -61.3586 | -61.4044 | 61.0016 | 60.997 | 60.9787 | 60.9924
1824.3125 | 122.5662 | -61.0519 | 61.2305 | 0.048599 | 0.0092434 | -0.0073337 | -0.097418 | -0.0032898 | -0.003388 | -0.0020039 | 0.073242 | -0.0034949 | -0.010175 | -0.0061523 | -0.0093226 | 0.0077289 | -0.0011728 | -0.032043 | 0.11444 | -0.059509 | -0.013733 | 0.073242 | -0.022888 | 0.036621 | 0.1831 | 0.11902 | -0.10529 | -0.018311 | 0.07782 | -0.045776 | 0.041199 | 60.9924 | -61.116 | -61.2442 | 61.1252 | 61.0886 | 61.0291 | 0.09613 | 0.036621 | 60.9467 | -61.1114 | -61.2488 | 61.1298 | 61.0931 | 61.0062 | 0.14649 | 0.05951 | 0.13275 | 0.045776 | 0.18311 | 0.086975 | 0.17395 | 0.22431 | 61.1664 | 61.171 | -61.29 | -61.3358 | 61.0382 | 61.0336 | 61.0199 | 61.235
1825.3125 | 122.6578 | -61.0291 | 61.2396 | 0.0028229 | 0.00668 | -0.0041293 | -0.094428 | 0.00076902 | -0.0029608 | 0.0014141 | 0.015259 | -0.0013587 | -0.0093204 | -0.0033751 | -0.0086816 | 0.010933 | -0.0048044 | 0.004578 | 0.09613 | -0.073242 | 0.018311 | 0.10071 | -0.032043 | 0.050354 | 0.004578 | 0.068665 | -0.12817 | 0.032043 | -0.27008 | -0.25635 | 0.10529 | 60.9558 | -61.1435 | -61.2213 | 61.1298 | 61.0794 | 60.997 | 0.1236 | 0.041199 | 60.9009 | -61.171 | -61.2076 | 60.759 | 61.1343 | 60.7727 | 0.23346 | -0.12817 | 0.17395 | 0.091553 | -0.14191 | 0.16022 | 0.16937 | 0.19684 | 61.1252 | 61.0977 | -61.3129 | -61.3678 | 61.0474 | 61.0611 | 61.0336 | 61.0336
1826.3125 | 122.5662 | -61.0245 | 61.2579 | 0.025711 | 0.0081754 | -0.0077609 | -0.095709 | -0.0030762 | -0.0044562 | -0.0037129 | 0.067139 | -0.0022131 | -0.013593 | -0.0065795 | -0.009109 | 0.010292 | -0.0039498 | 0.027466 | 0.12817 | -0.018311 | 0.045776 | 0.16022 | 0.045776 | 0.10529 | 0.11444 | 0.1831 | -0.032043 | 0.050354 | 0.1831 | 0.10529 | 0.14648 | 61.0062 | -61.1298 | -61.2122 | 61.1847 | 61.1298 | 61.0703 | 0.1236 | 0.064087 | 60.9924 | -61.0748 | -61.2076 | 61.2076 | 61.171 | 61.1298 | 0.17853 | 0.13733 | 0.17853 | 0.064087 | 0.21515 | 0.082397 | 0.14649 | 0.21515 | 61.1526 | 61.2076 | -61.2762 | -61.29 | 61.0703 | 61.0748 | 61.0519 | 61.1389
1827.3125 | 122.5616 | -61.0474 | 61.2488 | 0.079117 | 0.0073208 | -0.0045567 | -0.092505 | 0.0026916 | -0.0036018 | 0.00034614 | -0.030517 | 0.00077755 | -0.0099612 | 0.0013245 | -0.0076136 | 0.010292 | -0.000532 | -0.045776 | 0.13275 | -0.10529 | -0.07782 | 0.004578 | -0.11444 | -0.032043 | -0.07782 | 0.082397 | -0.14648 | -0.036621 | 0.013733 | -0.073242 | 0.027466 | 60.9421 | -61.116 | -61.3266 | 61.0519 | 61.0153 | 60.9329 | 0.073243 | -0.009155 | 60.9009 | -61.1664 | -61.2854 | 61.0611 | 61.0748 | 60.9741 | 0.17395 | 0.073242 | 0.10986 | 0.027466 | 0.16022 | 0.10986 | 0.23804 | 0.22888 | 61.1801 | 61.1298 | -61.3541 | -61.3953 | 60.9695 | 61.0107 | 61.0016 | 60.9695
1828.3125 | 122.6349 | -61.0565 | 61.1801 | 0.063858 | 0.0081754 | -0.0062655 | -0.094641 | -0.0011536 | -0.0059516 | -0.00050846 | -0.024414 | -0.0017859 | -0.0091068 | -0.0031615 | -0.010391 | 0.0096515 | 0.0024588 | -0.018311 | 0.10529 | -0.059509 | 0 | 0.082397 | 0 | 0.050354 | 0.018311 | 0.064087 | -0.1236 | 0.018311 | 0.10529 | 0.013733 | 0.086975 | 60.997 | -61.0748 | -61.1801 | 61.1389 | 61.1069 | 61.0565 | 0.10986 | 0.059509 | 60.9329 | -61.116 | -61.1618 | 61.1618 | 61.1435 | 61.0703 | 0.21057 | 0.13733 | 0.14191 | 0.059509 | 0.22888 | 0.14191 | 0.16479 | 0.18768 | 61.1618 | 61.1206 | -61.2396 | -61.3037 | 61.0565 | 61.0748 | 61.0382 | 61.0748
1829.3125 | 122.5754 | -61.0703 | 61.2167 | 0.048599 | 0.0092434 | -0.0054111 | -0.094214 | -0.0024354 | -0.0053108 | -0.0034991 | 0.042725 | -0.0022131 | -0.010175 | -0.0063659 | -0.0088952 | 0.010079 | 0.0007498 | 0.013733 | 0.09613 | -0.050354 | 0.013733 | 0.12817 | -0.013733 | 0.050354 | 0.004578 | 0.082397 | -0.13275 | 0 | 0.07782 | 0.018311 | 0.068665 | 61.0199 | -61.1206 | -61.203 | 61.1984 | 61.1206 | 61.0565 | 0.10071 | 0.036621 | 60.9375 | -61.1343 | -61.2167 | 61.1481 | 61.1389 | 61.0886 | 0.20142 | 0.15106 | 0.17853 | 0.064087 | 0.21057 | 0.13275 | 0.14648 | 0.21515 | 61.1664 | 61.1526 | -61.2671 | -61.3495 | 61.084 | 61.0703 | 61.084 | 61.0748
1830.3125 | 122.6212 | -61.0474 | 61.2076 | 0.102 | 0.0073208 | -0.0058383 | -0.094641 | 0.0016236 | -0.0046698 | -0.0017903 | -0.0091553 | -0.0019995 | -0.010816 | -0.0035889 | -0.0099634 | 0.012642 | -0.0039498 | -0.018311 | 0.10071 | -0.068665 | -0.004578 | 0.10071 | -0.07782 | 0.036621 | 0.004578 | 0.064087 | -0.14648 | 0.022888 | 0.091553 | -0.004578 | 0.073242 | 60.9787 | -61.1069 | -61.2122 | 61.1481 | 61.084 | 60.9695 | 0.10529 | -0.009155 | 60.9009 | -61.1435 | -61.1847 | 61.1389 | 61.1206 | 61.0428 | 0.21973 | 0.14191 | 0.16937 | 0.064087 | 0.23804 | 0.16937 | 0.16937 | 0.21057 | 61.1481 | 61.1114 | -61.2762 | -61.3541 | 61.0428 | 61.0703 | 61.0291 | 61.0519

## Thermal Data
Fire Time | North 25 C | Conduit Top | Conduit Bottom | TC Cable
-0.7458 | 22.4956 | 21.1028 | 21.2629 | 21.0649
0.2542 | 24.3871 | 21.1132 | 21.2759 | 21.0642
1.2542 | 26.9658 | 21.1299 | 21.2815 | 21.0626
2.2542 | 30.0797 | 21.1325 | 21.2953 | 21.0634
3.2542 | 33.6442 | 21.1464 | 21.3096 | 21.0618
4.2542 | 37.5622 | 21.1678 | 21.3276 | 21.0626
5.2542 | 41.8074 | 21.1807 | 21.3557 | 21.0622
6.2542 | 46.3604 | 21.1948 | 21.378 | 21.0581
7.2542 | 51.076 | 21.2307 | 21.4008 | 21.0606
8.2542 | 56.0483 | 21.2623 | 21.4547 | 21.063
9.2542 | 61.1753 | 21.2948 | 21.5151 | 21.0595
10.2542 | 66.4241 | 21.3419 | 21.5606 | 21.0592
11.2542 | 71.7672 | 21.3872 | 21.5938 | 21.0685
12.2542 | 77.2085 | 21.448 | 21.6337 | 21.0609
13.2542 | 82.8228 | 21.5106 | 21.6871 | 21.0643
14.2542 | 88.5378 | 21.5798 | 21.7292 | 21.0617
15.2542 | 94.3137 | 21.6555 | 21.7895 | 21.0618
16.2542 | 100.1356 | 21.7182 | 21.871 | 21.0618
17.2542 | 106.0228 | 21.8088 | 21.9791 | 21.0612
18.2542 | 111.8693 | 21.9083 | 22.0333 | 21.0573
19.2542 | 117.7865 | 22.0321 | 22.1303 | 21.0674
20.2542 | 123.7827 | 22.1377 | 22.2448 | 21.0691
21.2542 | 129.8749 | 22.2461 | 22.3251 | 21.0675
22.2542 | 135.9625 | 22.3722 | 22.434 | 21.0667
23.2542 | 142.0486 | 22.5 | 22.6113 | 21.0671
24.2542 | 148.0567 | 22.6651 | 22.8204 | 21.0705
25.2542 | 154.1337 | 22.8368 | 22.9654 | 21.0732
26.2542 | 160.166 | 22.9492 | 23.1163 | 21.0673
27.2542 | 166.1903 | 23.0688 | 23.2849 | 21.0611
28.2542 | 172.1426 | 23.2814 | 23.4735 | 21.0721
29.2542 | 178.1241 | 23.4488 | 23.6942 | 21.0619
30.2542 | 184.211 | 23.693 | 23.8365 | 21.0705
31.2542 | 190.2092 | 23.9549 | 24.0099 | 21.0699
32.2542 | 196.1057 | 24.147 | 24.2214 | 21.0627
33.2542 | 202.0352 | 24.3376 | 24.5001 | 21.0674
34.2542 | 208.0411 | 24.5025 | 24.747 | 21.0721
35.2542 | 213.9745 | 24.7365 | 24.9884 | 21.0691
36.2542 | 219.9898 | 25.0404 | 25.0477 | 21.0708
37.2542 | 225.9028 | 25.338 | 25.1918 | 21.0677
38.2542 | 231.9587 | 25.6346 | 25.4098 | 21.0636
39.2542 | 237.9788 | 25.8833 | 25.7648 | 21.0733
40.2542 | 243.8684 | 26.1369 | 25.9515 | 21.0751
41.2542 | 249.7437 | 26.4352 | 26.3638 | 21.0705
42.2542 | 255.6568 | 26.7829 | 26.7968 | 21.0758
43.2542 | 261.5711 | 27.1001 | 26.9439 | 21.0753
44.2542 | 267.5251 | 27.3998 | 27.1201 | 21.0827
45.2542 | 273.2783 | 27.7448 | 27.475 | 21.0771
46.2542 | 279.0163 | 28.1226 | 27.7202 | 21.0825
47.2542 | 284.7668 | 28.489 | 28.1549 | 21.0864
48.2542 | 290.4592 | 28.8533 | 28.6945 | 21.0846
49.2542 | 296.2382 | 29.2664 | 29.0248 | 21.0856
50.2542 | 301.9852 | 29.6797 | 29.4741 | 21.0884
51.2542 | 307.6966 | 30.1117 | 29.9355 | 21.0908
52.2542 | 313.3538 | 30.5647 | 30.2145 | 21.0884
53.2542 | 319.0332 | 31.0082 | 30.6605 | 21.0945
54.2542 | 324.6346 | 31.5044 | 31.1832 | 21.0926
55.2542 | 330.2823 | 31.9845 | 31.8603 | 21.1021
56.2542 | 335.7923 | 32.5063 | 32.435 | 21.1028
57.2542 | 341.2637 | 33.0203 | 33.0511 | 21.102
58.2542 | 346.8084 | 33.5305 | 33.3408 | 21.1091
59.2542 | 352.3295 | 34.1046 | 33.7667 | 21.1122
60.2542 | 357.6691 | 34.6666 | 34.174 | 21.1162
61.2542 | 363.0805 | 35.2597 | 34.9367 | 21.1245
62.2542 | 368.5277 | 35.8662 | 35.4048 | 21.1298
63.2542 | 373.9064 | 36.4746 | 36.055 | 21.1369
64.2542 | 379.1733 | 37.143 | 36.8824 | 21.1402
65.301 | 384.5829 | 37.8225 | 37.2735 | 21.1412
66.2542 | 389.6485 | 38.5115 | 38.0234 | 21.136
67.2542 | 394.9223 | 39.1842 | 38.8275 | 21.146
68.2542 | 400.2319 | 39.8991 | 39.2493 | 21.1603
69.2542 | 405.4459 | 40.6319 | 39.9748 | 21.1644
70.2542 | 410.4937 | 41.3763 | 40.8478 | 21.1715
71.2542 | 415.5574 | 42.0908 | 41.6585 | 21.1744
72.2542 | 420.6916 | 42.8021 | 42.386 | 21.1848
73.2542 | 425.6532 | 43.6651 | 42.9774 | 21.1914
74.2542 | 430.6352 | 44.4798 | 43.8821 | 21.1965
75.2542 | 435.7165 | 45.2881 | 44.3573 | 21.2041
76.2542 | 440.7493 | 46.1287 | 44.9227 | 21.2117
77.2542 | 445.768 | 47.0398 | 45.6089 | 21.2257
78.2542 | 450.7207 | 47.9676 | 46.7074 | 21.2415
79.2542 | 455.5602 | 48.8976 | 48.071 | 21.2434
80.2542 | 460.3788 | 49.8203 | 48.8584 | 21.251
81.2542 | 465.2447 | 50.8261 | 49.504 | 21.2572
82.2542 | 470.1157 | 51.7922 | 50.0221 | 21.2725
83.2542 | 474.8766 | 52.82 | 50.819 | 21.2806
84.2542 | 479.1095 | 53.8134 | 51.9903 | 21.2959
85.2542 | 482.8992 | 54.7477 | 53.1579 | 21.3046
86.2542 | 486.2378 | 55.8472 | 53.9165 | 21.3183
87.2698 | 489.4805 | 56.9505 | 54.5479 | 21.33
88.2542 | 492.4248 | 57.899 | 55.3836 | 21.3506
89.2542 | 495.2692 | 58.9215 | 56.6665 | 21.3584
90.2542 | 498.0558 | 59.9718 | 58.132 | 21.3737
91.2542 | 500.7977 | 61.0857 | 59.1146 | 21.3894
92.2542 | 503.6053 | 62.0794 | 60.1152 | 21.4079
93.2542 | 506.1165 | 63.0813 | 60.7805 | 21.4364
94.2542 | 508.5611 | 64.1491 | 61.5345 | 21.4513
95.2542 | 510.9724 | 65.2649 | 62.7657 | 21.4754
96.2542 | 513.0329 | 66.4104 | 64.1084 | 21.495
97.2542 | 514.9643 | 67.3972 | 65.042 | 21.5178
98.2542 | 516.5509 | 68.4027 | 66.0426 | 21.5375
99.2542 | 517.7559 | 69.4759 | 67.0956 | 21.5704
100.2542 | 518.9342 | 70.5618 | 67.8125 | 21.5911
101.2542 | 519.9191 | 71.6346 | 69.2227 | 21.6071
102.2542 | 520.582 | 72.6783 | 70.2927 | 21.6369
103.2542 | 521.1215 | 73.6464 | 71.1279 | 21.663
104.2542 | 521.7043 | 74.7367 | 71.8682 | 21.6991
105.2542 | 522.1272 | 76.0748 | 73.144 | 21.724
106.2542 | 522.2451 | 76.9936 | 73.8852 | 21.7643
107.2542 | 522.3144 | 77.973 | 74.6878 | 21.7898
108.2542 | 522.2166 | 78.8926 | 75.853 | 21.8256
109.2542 | 522.1556 | 79.9221 | 77.0614 | 21.8681
110.2542 | 522.2025 | 80.9378 | 78.3314 | 21.8969
111.2542 | 522.24 | 81.931 | 79.0322 | 21.9348
112.2542 | 522.3174 | 82.9147 | 79.7641 | 21.9769
113.2542 | 522.3263 | 83.8802 | 80.3857 | 22.0195
114.2542 | 522.4581 | 84.8207 | 81.3858 | 22.0687
115.2542 | 522.6588 | 85.8742 | 82.3424 | 22.1028
116.2542 | 522.7305 | 86.8994 | 83.4114 | 22.1572
117.2542 | 522.7791 | 87.9271 | 84.31 | 22.2111
118.2542 | 522.9556 | 88.9401 | 85.3865 | 22.2624
119.2542 | 523.1101 | 89.9643 | 86.1268 | 22.3064
120.2542 | 523.3352 | 90.9153 | 87.0313 | 22.3611
121.2542 | 523.3733 | 91.8859 | 87.9788 | 22.4164
122.2542 | 523.5282 | 92.9107 | 88.9816 | 22.4739
123.2542 | 523.7317 | 93.8359 | 89.6776 | 22.5294
124.2542 | 523.9061 | 94.9234 | 90.5367 | 22.5894
125.2542 | 524.0665 | 95.9238 | 91.5015 | 22.6418
126.2542 | 524.2913 | 96.9824 | 92.4169 | 22.6985
127.2542 | 524.4053 | 97.9639 | 93.3413 | 22.7665
128.2542 | 524.542 | 98.8452 | 94.1963 | 22.8338
129.2542 | 524.6605 | 99.8816 | 95.1347 | 22.908
130.2542 | 524.7195 | 100.8588 | 96.1511 | 22.9819
131.2542 | 524.8831 | 101.8822 | 97.4913 | 23.0545
132.2542 | 525.0141 | 102.9863 | 98.2961 | 23.1378
133.2542 | 525.1727 | 103.9169 | 99.1013 | 23.2186
134.2542 | 525.4006 | 104.879 | 100.3132 | 23.3019
135.2542 | 525.6 | 105.8298 | 101.2678 | 23.3787
136.2542 | 525.84 | 106.6743 | 102.2462 | 23.4619
137.2542 | 526.0241 | 107.7993 | 103.1417 | 23.5503
138.2542 | 526.1865 | 108.7861 | 104.1446 | 23.6448
139.2542 | 526.199 | 109.6748 | 105.0548 | 23.7355
140.2542 | 526.267 | 110.656 | 105.8196 | 23.8314
141.2542 | 526.3343 | 111.6238 | 106.7338 | 23.9249
142.2542 | 526.5322 | 112.6299 | 107.4225 | 24.0364
143.2542 | 526.7532 | 113.5771 | 108.2597 | 24.1316
144.2542 | 526.8574 | 114.5567 | 109.3902 | 24.2407
145.2542 | 526.9859 | 115.5317 | 110.3664 | 24.3511
146.2542 | 527.0893 | 116.4303 | 111.1385 | 24.462
147.2542 | 527.1809 | 117.4417 | 112.2254 | 24.5716
148.2542 | 527.3087 | 118.3773 | 112.9922 | 24.6914
149.2542 | 527.3296 | 119.3762 | 113.7241 | 24.8079
150.2542 | 527.5164 | 120.3694 | 114.989 | 24.9294
151.2542 | 527.5835 | 121.3313 | 115.9044 | 25.0517
152.2542 | 527.5854 | 122.2192 | 116.649 | 25.1834
153.2542 | 527.5549 | 123.1595 | 117.4119 | 25.3075
154.2542 | 527.563 | 124.1441 | 118.4688 | 25.4365
155.2542 | 527.5262 | 125.1388 | 119.7072 | 25.5826
156.2542 | 527.6407 | 126.0204 | 120.469 | 25.7151
157.2542 | 527.6626 | 126.9588 | 121.1422 | 25.8577
158.2542 | 527.6181 | 127.955 | 122.0491 | 25.9998
159.2542 | 527.7274 | 128.9047 | 122.8676 | 26.1363
160.2542 | 527.6883 | 129.7897 | 123.7481 | 26.2889
161.2542 | 527.6918 | 130.7475 | 124.7534 | 26.4373
162.2542 | 527.7848 | 131.7114 | 125.5999 | 26.599
163.2542 | 527.7689 | 132.608 | 126.3643 | 26.7538
164.2542 | 527.7634 | 133.5011 | 127.516 | 26.9168
165.2542 | 527.6768 | 134.3949 | 128.217 | 27.0794
166.2542 | 527.6825 | 135.3146 | 129.1147 | 27.2474
167.2542 | 527.7628 | 136.2049 | 129.8331 | 27.4125
168.2542 | 527.9104 | 137.139 | 130.7491 | 27.5929
169.2542 | 527.9421 | 138.0159 | 131.6987 | 27.7694
170.2542 | 527.8948 | 138.8928 | 132.4548 | 27.9451
171.2542 | 527.8564 | 139.8422 | 133.3019 | 28.1219
172.2542 | 527.789 | 140.7282 | 134.124 | 28.3072
173.2542 | 527.8498 | 141.6128 | 135.0398 | 28.4998
174.2542 | 527.9037 | 142.4571 | 135.8917 | 28.6891
175.2542 | 527.9276 | 143.2547 | 136.9973 | 28.8847
176.2542 | 527.9817 | 144.1759 | 137.8071 | 29.0768
177.2542 | 528.1207 | 145.0476 | 138.5346 | 29.2871
178.2542 | 528.2971 | 145.927 | 139.4311 | 29.489
179.2542 | 528.4115 | 146.7496 | 140.3871 | 29.6986
180.2542 | 528.3669 | 147.6083 | 141.2893 | 29.9094
181.2542 | 528.3085 | 148.5442 | 142.1162 | 30.1264
182.2542 | 528.3023 | 149.3851 | 143.0439 | 30.3524
183.2542 | 528.4207 | 150.2032 | 143.7209 | 30.5735
184.2542 | 528.4567 | 151.0264 | 144.6236 | 30.8001
185.2542 | 528.5055 | 151.9297 | 145.4108 | 31.0329
186.2542 | 528.4789 | 152.8612 | 146.1787 | 31.2725
187.2542 | 528.4152 | 153.7429 | 147.0912 | 31.5177
188.2542 | 528.4536 | 154.5742 | 147.8579 | 31.7624
189.2542 | 528.424 | 155.4275 | 148.6494 | 32.0146
190.2542 | 528.3967 | 156.24 | 149.4903 | 32.2727
191.2542 | 528.2348 | 157.0242 | 150.4612 | 32.5344
192.2542 | 528.1305 | 157.9215 | 151.3041 | 32.7969
193.2542 | 528.1007 | 158.7503 | 152.0584 | 33.0749
194.2542 | 528.0548 | 159.5699 | 152.8925 | 33.3364
195.2542 | 528.0129 | 160.4011 | 153.567 | 33.6215
196.2542 | 528.0403 | 161.2371 | 154.2483 | 33.9083
197.2542 | 527.972 | 162.1212 | 155.1077 | 34.1929
198.2542 | 527.801 | 162.9497 | 155.9035 | 34.4943
199.2542 | 527.8158 | 163.7088 | 156.6253 | 34.784
200.2542 | 527.8238 | 164.5162 | 157.4626 | 35.0854
201.2542 | 527.8125 | 165.3202 | 158.2028 | 35.3941
202.2542 | 527.9507 | 166.1318 | 159.0385 | 35.703
203.2542 | 528.012 | 166.9907 | 159.762 | 36.0188
204.2542 | 528.0633 | 167.8043 | 160.4117 | 36.3356
205.2542 | 528.0592 | 168.5802 | 161.1967 | 36.6504
206.2542 | 528.1112 | 169.4492 | 161.8615 | 36.9707
207.2542 | 528.2194 | 170.2569 | 162.5951 | 37.3134
208.2542 | 528.326 | 171.0394 | 163.3927 | 37.6401
209.2542 | 528.3777 | 171.8465 | 164.1666 | 37.9661
210.2542 | 528.3923 | 172.5817 | 164.8684 | 38.3081
211.2542 | 528.3666 | 173.4121 | 165.5828 | 38.6479
212.2542 | 528.4377 | 174.2706 | 166.3321 | 38.9866
213.2542 | 528.4276 | 175.2146 | 167.1222 | 39.3294
214.2542 | 528.4421 | 175.86 | 167.9364 | 39.6778
215.2542 | 528.4575 | 176.5777 | 168.6452 | 40.023
216.2542 | 528.4493 | 177.3545 | 169.4431 | 40.3869
217.2542 | 528.3508 | 178.0826 | 170.1649 | 40.7303
218.2542 | 528.4591 | 178.9172 | 171.0061 | 41.0868
219.2542 | 528.4031 | 179.6866 | 171.869 | 41.4432
220.2542 | 528.3126 | 180.4983 | 172.5179 | 41.7951
221.2542 | 528.1004 | 181.2701 | 173.1999 | 42.1422
222.2542 | 528.027 | 182.0335 | 173.928 | 42.4857
223.2542 | 528.0148 | 182.7966 | 174.6775 | 42.8357
224.2542 | 528.0115 | 183.5753 | 175.3438 | 43.1818
225.2542 | 528.0495 | 184.3631 | 176.062 | 43.5255
226.2542 | 528.1596 | 185.0923 | 176.7771 | 43.8682
227.2542 | 528.271 | 185.8486 | 177.6339 | 44.2205
228.2542 | 528.1402 | 186.6331 | 178.404 | 44.5628
229.2542 | 528.1094 | 187.372 | 179.0378 | 44.9095
230.2542 | 528.1391 | 188.1192 | 179.6515 | 45.2449
231.2542 | 528.1167 | 188.8628 | 180.4098 | 45.5947
232.2542 | 528.1327 | 189.6307 | 181.1866 | 45.9306
233.2542 | 528.1725 | 190.37 | 181.8442 | 46.2717
234.2542 | 528.1344 | 191.1031 | 182.5333 | 46.6059
235.2542 | 528.1567 | 191.8446 | 183.2475 | 46.9592
236.2542 | 528.2312 | 192.6108 | 183.9767 | 47.2918
237.2542 | 528.3943 | 193.372 | 184.6393 | 47.6171
238.2542 | 528.2702 | 194.1462 | 185.3214 | 47.9463
239.2542 | 528.2063 | 194.8962 | 186.088 | 48.2788
240.2542 | 528.229 | 195.6715 | 186.8268 | 48.5977
241.2542 | 528.1459 | 196.4165 | 187.5665 | 48.925
242.2542 | 528.0409 | 197.0985 | 188.2416 | 49.2352
243.2542 | 528.0907 | 197.7775 | 188.9963 | 49.5492
244.2542 | 528.1633 | 198.5147 | 189.7592 | 49.8602
245.2542 | 528.2694 | 199.2337 | 190.386 | 50.173
246.2542 | 528.1713 | 199.9862 | 191.0319 | 50.4796
247.2542 | 528.0941 | 200.7063 | 191.716 | 50.7818
248.2542 | 528.216 | 201.4636 | 192.4042 | 51.0813
249.2542 | 528.3463 | 202.1692 | 193.2028 | 51.3786
250.2542 | 528.3467 | 202.8882 | 193.8766 | 51.6633
251.2542 | 528.4361 | 203.6219 | 194.586 | 51.9726
252.2542 | 528.2724 | 204.3186 | 195.2498 | 52.2601
253.2542 | 528.1772 | 205.0171 | 195.94 | 52.553
254.2542 | 528.1266 | 205.7702 | 196.61 | 52.8422
255.2542 | 528.1 | 206.4792 | 197.3068 | 53.1301
256.2542 | 528.1088 | 207.1618 | 198.0292 | 53.4167
257.2542 | 528.0705 | 207.8836 | 198.7361 | 53.7068
258.2542 | 528.0851 | 208.5773 | 199.4002 | 53.9978
259.2542 | 528.0043 | 209.2448 | 200.0849 | 54.2934
260.2542 | 527.9104 | 209.8654 | 200.777 | 54.5838
261.2542 | 527.7115 | 210.5632 | 201.4464 | 54.8721
262.2542 | 527.5993 | 211.2732 | 202.0741 | 55.171
263.2542 | 527.5331 | 211.9646 | 202.7751 | 55.4563
264.2542 | 527.461 | 212.6461 | 203.4454 | 55.7473
265.2542 | 527.4294 | 213.2734 | 204.1063 | 56.0335
266.2542 | 527.3566 | 213.9047 | 204.7737 | 56.3323
267.2542 | 527.3151 | 214.6028 | 205.4155 | 56.6178
268.2542 | 527.313 | 215.2927 | 206.0735 | 56.9017
269.2542 | 527.2922 | 215.9659 | 206.7647 | 57.1863
270.2542 | 527.4211 | 216.6285 | 207.4246 | 57.4694
271.2542 | 527.4148 | 217.2698 | 208.0966 | 57.7458
272.2542 | 527.4569 | 218.0054 | 208.75 | 58.0256
273.2542 | 527.496 | 218.72 | 209.3965 | 58.3049
274.2542 | 527.6223 | 219.4007 | 210.0652 | 58.5786
275.2542 | 527.6274 | 220.0776 | 210.7349 | 58.8582
276.2542 | 527.6153 | 220.7681 | 211.4095 | 59.1271
277.2542 | 527.6477 | 221.4437 | 212.0641 | 59.4019
278.2542 | 527.7305 | 222.1064 | 212.7899 | 59.6678
279.2542 | 527.5715 | 222.7816 | 213.4038 | 59.9245
280.2542 | 527.4804 | 223.4001 | 213.9944 | 60.1853
281.2542 | 527.385 | 224.1135 | 214.6329 | 60.4522
282.2542 | 527.3475 | 224.8133 | 215.2605 | 60.7177
283.2542 | 527.4009 | 225.5169 | 215.8572 | 60.9666
284.2542 | 527.4166 | 226.188 | 216.5013 | 61.2125
285.2542 | 527.4804 | 226.8796 | 217.1408 | 61.4714
286.2542 | 527.3769 | 227.6002 | 217.8046 | 61.7147
287.2542 | 527.336 | 228.2362 | 218.4121 | 61.9662
288.2542 | 527.3372 | 228.9276 | 219.1307 | 62.2162
289.2542 | 527.3744 | 229.5882 | 219.7517 | 62.455
290.2542 | 527.2742 | 230.2501 | 220.4402 | 62.7012
291.2542 | 527.2766 | 230.9016 | 221.0138 | 62.9384
292.2542 | 527.4729 | 231.5176 | 221.6235 | 63.1722
293.2542 | 527.6025 | 232.188 | 222.2124 | 63.4117
294.2542 | 527.6706 | 232.8935 | 222.9036 | 63.6443
295.2542 | 527.7947 | 233.602 | 223.4967 | 63.8766
296.2542 | 527.7929 | 234.2944 | 224.1218 | 64.1051
297.2542 | 527.8041 | 234.9879 | 224.7562 | 64.3363
298.2542 | 527.6928 | 235.6447 | 225.422 | 64.5707
299.2542 | 527.7383 | 236.3125 | 226.0306 | 64.7927
300.2542 | 527.8133 | 237.0158 | 226.6115 | 65.0208
301.2542 | 527.8662 | 237.7046 | 227.2351 | 65.2568
302.2542 | 527.888 | 238.3861 | 227.8167 | 65.475
303.2542 | 527.8505 | 238.9964 | 228.4014 | 65.7151
304.2542 | 527.853 | 239.7058 | 229.0303 | 65.9342
305.2542 | 527.7824 | 240.3485 | 229.6611 | 66.1478
306.2542 | 527.8284 | 241.0212 | 230.3041 | 66.3687
307.2542 | 527.7281 | 241.7034 | 230.8649 | 66.5799
308.2542 | 527.6477 | 242.3826 | 231.4634 | 66.7969
309.2542 | 527.7085 | 243.0498 | 232.0585 | 67.0037
310.2542 | 527.7487 | 243.6866 | 232.6309 | 67.2147
311.2542 | 527.6131 | 244.3771 | 233.1863 | 67.4265
312.2542 | 527.5065 | 245.0359 | 233.8553 | 67.6355
313.2542 | 527.5407 | 245.7054 | 234.5478 | 67.832
314.2542 | 527.6994 | 246.36 | 235.1233 | 68.043
315.2542 | 527.7119 | 246.9796 | 235.7104 | 68.2443
316.2542 | 527.6684 | 247.6059 | 236.2807 | 68.4525
317.2542 | 527.6852 | 248.2825 | 236.8879 | 68.6509
318.2542 | 527.7093 | 248.9544 | 237.4169 | 68.8534
319.2542 | 527.7096 | 249.7814 | 237.9627 | 69.0542
320.2542 | 527.7851 | 250.3573 | 238.6406 | 69.2515
321.2542 | 527.8467 | 250.9674 | 239.1951 | 69.4395
322.2542 | 527.8937 | 251.5893 | 239.7765 | 69.6272
323.2542 | 527.8994 | 252.2168 | 240.3548 | 69.818
324.2542 | 527.9367 | 252.8852 | 240.9032 | 70.0063
325.2542 | 527.7909 | 253.5089 | 241.4605 | 70.178
326.2542 | 527.744 | 254.1431 | 242.0947 | 70.3537
327.2542 | 527.7617 | 254.7935 | 242.7035 | 70.5403
328.2542 | 527.6885 | 255.4509 | 243.3183 | 70.7171
329.2542 | 527.6576 | 256.0857 | 243.9424 | 70.8906
330.2542 | 527.7124 | 256.6989 | 244.409 | 71.0595
331.2542 | 527.6049 | 257.2937 | 245.0287 | 71.2359
332.2542 | 527.5202 | 257.9329 | 245.53 | 71.4083
333.2542 | 527.6013 | 258.5437 | 246.0051 | 71.5709
334.2542 | 527.5552 | 259.1594 | 246.631 | 71.7414
335.2542 | 527.5168 | 259.8088 | 247.0742 | 71.9053
336.2542 | 527.378 | 260.4279 | 247.6795 | 72.0619
337.2542 | 527.2585 | 261.0759 | 248.3273 | 72.2234
338.2542 | 527.2242 | 261.6984 | 248.9167 | 72.3724
339.2542 | 527.1838 | 262.3201 | 249.4738 | 72.5313
340.2542 | 527.1886 | 262.923 | 249.8856 | 72.6822
341.2542 | 527.1177 | 263.5434 | 250.5075 | 72.8358
342.2542 | 527.0897 | 264.1101 | 250.9987 | 72.978
343.2542 | 527.0672 | 264.7382 | 251.5741 | 73.131
344.2542 | 527.0431 | 265.3431 | 252.2716 | 73.2799
345.2542 | 527.0372 | 265.957 | 252.7753 | 73.4288
346.2542 | 526.9958 | 266.5721 | 253.2256 | 73.5707
347.2542 | 526.9942 | 267.1747 | 253.7916 | 73.7174
348.2542 | 526.975 | 267.7913 | 254.4224 | 73.8598
349.2542 | 526.9281 | 268.4029 | 255.004 | 73.988
350.2542 | 527.0199 | 268.9887 | 255.4968 | 74.1278
351.2542 | 526.9612 | 269.589 | 256.0274 | 74.261
352.2542 | 527.0514 | 270.1591 | 256.5896 | 74.3936
353.2542 | 527.0303 | 270.7305 | 257.0903 | 74.5227
354.2542 | 526.9945 | 271.3463 | 257.5219 | 74.6527
355.2542 | 527.0637 | 271.9084 | 258.029 | 74.775
356.2542 | 527.0497 | 272.4798 | 258.6858 | 74.8997
357.2542 | 527.0454 | 273.0526 | 259.2891 | 75.034
358.2542 | 527.0643 | 273.6211 | 259.8742 | 75.1524
359.2542 | 527.035 | 274.199 | 260.4112 | 75.2679
360.2542 | 526.9892 | 274.7994 | 260.934 | 75.3959
361.2542 | 526.9051 | 275.4084 | 261.4351 | 75.508
362.2542 | 526.9722 | 275.9984 | 261.8704 | 75.6231
363.2542 | 526.9434 | 276.5675 | 262.4231 | 75.7478
364.2542 | 526.924 | 277.1281 | 262.9648 | 75.8659
365.2542 | 526.9324 | 277.7144 | 263.4907 | 75.9721
366.2542 | 527.0507 | 278.2789 | 263.9837 | 76.0843
367.2542 | 527.163 | 278.8594 | 264.6087 | 76.2025
368.2542 | 527.2264 | 279.4371 | 265.2519 | 76.2997
369.2542 | 527.2101 | 279.9828 | 265.8743 | 76.4036
370.2542 | 527.3152 | 280.5511 | 266.243 | 76.5172
371.2542 | 527.4262 | 281.1492 | 266.8069 | 76.6201
372.2542 | 527.4754 | 281.7405 | 267.2767 | 76.7231
373.2542 | 527.4416 | 282.31 | 267.7797 | 76.8252
374.2542 | 527.4162 | 282.8455 | 268.3426 | 76.9281
375.2542 | 527.5425 | 283.414 | 268.8271 | 77.029
376.2542 | 527.5944 | 283.9964 | 269.3597 | 77.1337
377.2542 | 527.6377 | 284.5648 | 269.9771 | 77.2344
378.2698 | 527.618 | 285.1153 | 270.3982 | 77.3388
379.2542 | 527.584 | 285.6888 | 270.8686 | 77.4388
380.2542 | 527.5785 | 286.2547 | 271.3642 | 77.5536
381.2542 | 527.6416 | 286.8045 | 271.8628 | 77.6579
382.2542 | 527.5889 | 287.3602 | 272.2596 | 77.7577
383.2542 | 527.4916 | 287.9136 | 272.7098 | 77.8661
384.2542 | 527.4368 | 288.5244 | 273.2042 | 77.9759
385.2542 | 527.3668 | 289.0803 | 273.8539 | 78.0849
386.2542 | 527.4466 | 289.6508 | 274.3226 | 78.1999
387.2542 | 527.4733 | 290.1792 | 274.7837 | 78.3081
388.2542 | 527.4864 | 290.7303 | 275.2794 | 78.4199
389.2542 | 527.5878 | 291.2672 | 275.8046 | 78.5366
390.2542 | 527.5348 | 291.8296 | 276.226 | 78.6545
391.2542 | 527.4922 | 292.3767 | 276.9015 | 78.7794
392.2542 | 527.4259 | 292.9324 | 277.2702 | 78.9016
393.2542 | 527.3778 | 293.4987 | 277.8413 | 79.0308
394.2542 | 527.3197 | 294.0367 | 278.1744 | 79.1597
395.2542 | 527.3095 | 294.5681 | 278.5993 | 79.2935
396.2542 | 527.4664 | 295.1098 | 279.1398 | 79.4428
397.2542 | 527.5125 | 295.6762 | 279.6895 | 79.5773
398.2542 | 527.5893 | 296.2365 | 280.1978 | 79.7184
399.2542 | 527.7444 | 296.779 | 280.8478 | 79.8706
400.2542 | 527.8332 | 297.3121 | 281.304 | 80.0215
401.2542 | 527.9224 | 297.8426 | 281.7021 | 80.1708
402.2542 | 528.0699 | 298.3852 | 282.2036 | 80.3301
403.2542 | 528.1322 | 298.9112 | 282.6864 | 80.4864
404.2542 | 528.1685 | 299.4775 | 283.1518 | 80.646
405.2542 | 528.1938 | 300.014 | 283.5124 | 80.8103
406.2542 | 528.2807 | 300.5556 | 283.9887 | 80.9786
407.2542 | 528.2802 | 301.0918 | 284.4252 | 81.1459
408.2542 | 528.2472 | 301.6403 | 285.0956 | 81.3126
409.2542 | 528.2102 | 302.1603 | 285.505 | 81.4949
410.2542 | 528.1755 | 302.6922 | 285.8627 | 81.6786
411.2542 | 528.1577 | 303.239 | 286.3978 | 81.8573
412.2542 | 528.0797 | 303.7649 | 286.9703 | 82.0459
413.2542 | 528.0031 | 304.3006 | 287.585 | 82.2458
414.2542 | 527.9744 | 304.8057 | 287.9267 | 82.4465
415.2542 | 527.8848 | 305.3345 | 288.2765 | 82.6533
416.2542 | 527.792 | 305.8692 | 288.7945 | 82.8691
417.2542 | 527.6882 | 306.401 | 289.286 | 83.0776
418.2542 | 527.6212 | 306.9205 | 289.6507 | 83.2877
419.2542 | 527.6023 | 307.4394 | 290.2292 | 83.5057
420.2542 | 527.6149 | 307.9509 | 290.6574 | 83.7113
421.2542 | 527.6733 | 308.445 | 291.0177 | 83.9415
422.2542 | 527.7013 | 308.9365 | 291.5855 | 84.1565
423.2542 | 527.7003 | 309.4889 | 291.8828 | 84.3755
424.2542 | 527.6846 | 309.997 | 292.2501 | 84.5907
425.2542 | 527.7774 | 310.5151 | 292.6986 | 84.8125
426.2542 | 527.7449 | 311.0386 | 293.2757 | 85.0264
427.2542 | 527.8213 | 311.5296 | 293.6584 | 85.2411
428.2542 | 527.8589 | 312.0627 | 294.0454 | 85.4593
429.2542 | 527.8552 | 312.5578 | 294.5853 | 85.6823
430.2542 | 527.7549 | 313.0838 | 294.9187 | 85.9129
431.2542 | 527.78 | 313.5978 | 295.5735 | 86.1465
432.2542 | 527.6769 | 314.1319 | 296.0938 | 86.3753
433.2542 | 527.5675 | 314.6466 | 296.6848 | 86.606
434.2542 | 527.496 | 315.1422 | 297.2037 | 86.8437
435.2542 | 527.4965 | 315.6569 | 297.4481 | 87.0857
436.2542 | 527.5616 | 316.1444 | 297.6916 | 87.3208
437.2542 | 527.5995 | 316.6478 | 298.1361 | 87.5657
438.2542 | 527.5013 | 317.1487 | 298.452 | 87.8018
439.2542 | 527.4988 | 317.6625 | 299.0269 | 88.0496
440.2542 | 527.3537 | 318.1602 | 299.6507 | 88.2868
441.2542 | 527.3567 | 318.6575 | 300.0925 | 88.5315
442.2542 | 527.3853 | 319.1632 | 300.3784 | 88.7857
443.2542 | 527.3076 | 319.6403 | 300.9868 | 89.0317
444.2542 | 527.2436 | 320.1435 | 301.1879 | 89.2898
445.2542 | 527.1958 | 320.639 | 301.537 | 89.556
446.2542 | 527.1445 | 321.0931 | 302.0384 | 89.816
447.2542 | 527.0465 | 321.5799 | 302.5027 | 90.088
448.2542 | 526.9608 | 322.0794 | 302.901 | 90.36
449.2542 | 526.8569 | 322.5509 | 303.4444 | 90.6359
450.2542 | 526.8168 | 323.0429 | 303.8527 | 90.9072
451.2542 | 526.8264 | 323.5392 | 304.1186 | 91.1782
452.2542 | 526.8679 | 324.0277 | 304.4707 | 91.454
453.2542 | 526.9494 | 324.5056 | 305.0706 | 91.7273
454.2542 | 527.0767 | 324.9838 | 305.3067 | 92.0156
455.2542 | 527.1567 | 325.4496 | 305.7664 | 92.2965
456.2542 | 527.2876 | 325.9492 | 306.0197 | 92.587
457.2542 | 527.3785 | 326.4143 | 306.3881 | 92.886
458.2542 | 527.4173 | 326.9103 | 306.9301 | 93.1828
459.2542 | 527.3371 | 327.3747 | 307.3647 | 93.4904
460.2542 | 527.4088 | 327.8586 | 307.9405 | 93.8003
461.2542 | 527.4804 | 328.3416 | 308.3516 | 94.1165
462.2542 | 527.4016 | 328.8181 | 308.6038 | 94.4221
463.2542 | 527.4045 | 329.273 | 308.9819 | 94.726
464.2542 | 527.4431 | 329.7637 | 309.4824 | 95.038
465.2542 | 527.5092 | 330.217 | 309.8662 | 95.3495
466.2542 | 527.5294 | 330.7126 | 310.2998 | 95.6516
467.2542 | 527.4806 | 331.1546 | 310.6615 | 95.9713
468.2542 | 527.3959 | 331.615 | 311.018 | 96.2861
469.2542 | 527.3439 | 332.0943 | 311.4851 | 96.6089
470.2542 | 527.2885 | 332.5731 | 311.8724 | 96.9243
471.2542 | 527.3082 | 333.0317 | 312.3388 | 97.251
472.2542 | 527.3574 | 333.5122 | 312.6416 | 97.5758
473.2542 | 527.2777 | 333.951 | 313.1453 | 97.8991
474.2542 | 527.1812 | 334.4263 | 313.5067 | 98.2321
475.2542 | 527.2123 | 334.8874 | 313.9946 | 98.5593
476.2542 | 527.1971 | 335.3465 | 314.3643 | 98.8865
477.2542 | 527.0845 | 335.7999 | 314.6414 | 99.2044
478.2542 | 527.038 | 336.2351 | 315.1106 | 99.5327
479.2542 | 527.0444 | 336.6846 | 315.5806 | 99.8424
480.2542 | 527.055 | 337.1232 | 316.0126 | 100.16
481.2542 | 527.0292 | 337.5785 | 316.3324 | 100.4766
482.2542 | 527.0178 | 338.022 | 316.5772 | 100.7902
483.2542 | 527.0788 | 338.4733 | 316.9212 | 101.101
484.2542 | 527.1056 | 338.9129 | 317.2097 | 101.414
485.2542 | 527.0516 | 339.3537 | 317.5811 | 101.7283
486.2542 | 526.9998 | 339.7909 | 318.1924 | 102.0247
487.2542 | 526.9293 | 340.2641 | 318.6062 | 102.3337
488.2542 | 526.8829 | 340.6712 | 319.0415 | 102.6497
489.2542 | 526.8049 | 341.0756 | 319.4135 | 102.9525
490.2542 | 526.7225 | 341.5626 | 319.9181 | 103.2634
491.2542 | 526.6852 | 341.9951 | 320.1553 | 103.5617
492.2542 | 526.6898 | 342.4468 | 320.3524 | 103.8733
493.2542 | 526.6985 | 342.8741 | 320.7252 | 104.1694
494.2542 | 526.5802 | 343.2961 | 320.981 | 104.4713
495.2542 | 526.568 | 343.7294 | 321.5603 | 104.7669
496.2542 | 526.5589 | 344.1542 | 322.0951 | 105.0677
497.2542 | 526.6497 | 344.5779 | 322.2122 | 105.3658
498.2542 | 526.6615 | 345.0193 | 322.457 | 105.6622
499.2542 | 526.5986 | 345.469 | 322.824 | 105.9513
500.2542 | 526.5349 | 345.8593 | 323.1756 | 106.2392
501.2542 | 526.5481 | 346.2914 | 323.5875 | 106.5432
502.2542 | 526.4683 | 346.7069 | 323.8455 | 106.8342
503.2542 | 526.4641 | 347.1458 | 324.3061 | 107.1241
504.2542 | 526.521 | 347.5763 | 324.4345 | 107.406
505.2542 | 526.4845 | 347.9773 | 324.8183 | 107.695
506.2542 | 526.482 | 348.3576 | 325.1126 | 107.9825
507.2542 | 526.5105 | 348.7398 | 325.6584 | 108.2634
508.2542 | 526.431 | 349.1817 | 326.2953 | 108.5438
509.2542 | 526.307 | 349.5996 | 326.4991 | 108.8283
510.2542 | 526.252 | 350.024 | 326.7372 | 109.1106
511.2542 | 526.1855 | 350.4516 | 327.1112 | 109.3993
512.2542 | 526.1561 | 350.8549 | 327.3944 | 109.6866
513.2542 | 526.2273 | 351.2927 | 327.8752 | 109.9709
514.2542 | 526.2932 | 351.6855 | 328.2603 | 110.2631
515.2542 | 526.3022 | 352.1021 | 328.4257 | 110.556
516.2542 | 526.3275 | 352.5018 | 328.9649 | 110.8486
517.2542 | 526.3302 | 352.9102 | 329.3507 | 111.1467
518.2542 | 526.3463 | 353.3354 | 329.9521 | 111.4442
519.2542 | 526.3187 | 353.7371 | 330.11 | 111.7446
520.2542 | 526.2044 | 354.1406 | 330.5117 | 112.0507
521.2542 | 526.1037 | 354.5273 | 330.708 | 112.3734
522.2542 | 526.0982 | 354.9008 | 331.0151 | 112.6871
523.2542 | 526.1158 | 355.2973 | 331.4118 | 113.03
524.2542 | 526.1715 | 355.7208 | 331.8985 | 113.3628
525.2542 | 526.167 | 356.0965 | 332.0468 | 113.6981
526.2542 | 526.2354 | 356.4837 | 332.5824 | 114.0439
527.2542 | 526.2756 | 356.8956 | 333.0584 | 114.3935
528.2542 | 526.4642 | 357.3061 | 333.1758 | 114.7451
529.2542 | 526.6118 | 357.7011 | 333.6581 | 115.1069
530.2542 | 526.6676 | 358.1129 | 333.926 | 115.4779
531.2542 | 526.6567 | 358.5143 | 334.0667 | 115.8502
532.2542 | 526.7251 | 358.8911 | 334.4178 | 116.2247
533.2542 | 526.805 | 359.2676 | 334.7275 | 116.6085
534.2542 | 526.8101 | 359.6482 | 335.216 | 116.9961
535.2542 | 526.8492 | 360.0151 | 335.4451 | 117.3862
536.2542 | 526.9038 | 360.4031 | 335.8484 | 117.7729
537.2542 | 527.0176 | 360.7794 | 336.1585 | 118.1723
538.2542 | 527.1076 | 361.1939 | 336.5401 | 118.554
539.2542 | 527.2007 | 361.5456 | 337.0359 | 118.9557
540.2542 | 527.2931 | 361.954 | 337.4474 | 119.3441
541.2542 | 527.2947 | 362.3726 | 337.5417 | 119.7452
542.2542 | 527.3765 | 362.729 | 337.8549 | 120.1379
543.2542 | 527.3899 | 363.1221 | 338.1911 | 120.5316
544.2542 | 527.3792 | 363.5017 | 338.3281 | 120.9165
545.2542 | 527.4209 | 363.8601 | 338.6927 | 121.3114
546.2542 | 527.534 | 364.2516 | 339.3257 | 121.7042
547.2542 | 527.6212 | 364.6053 | 339.5854 | 122.1002
548.2542 | 527.6722 | 365.0091 | 340.0799 | 122.4946
549.2542 | 527.5784 | 365.3902 | 340.2668 | 122.8868
550.2542 | 527.5228 | 365.7381 | 340.3527 | 123.2699
551.2542 | 527.512 | 366.1338 | 340.7943 | 123.6578
552.2542 | 527.5235 | 366.4773 | 341.4466 | 124.0448
553.2542 | 527.5495 | 366.8552 | 341.791 | 124.4297
554.2542 | 527.5766 | 367.2409 | 341.8589 | 124.8251
555.2542 | 527.5706 | 367.6225 | 341.989 | 125.2118
556.2542 | 527.5053 | 367.9879 | 342.2355 | 125.5977
557.2542 | 527.5184 | 368.3435 | 342.7399 | 125.9868
558.2542 | 527.5333 | 368.7232 | 343.0919 | 126.3774
559.2542 | 527.4327 | 369.0551 | 343.5902 | 126.7698
560.2542 | 527.421 | 369.3722 | 343.7437 | 127.1643
561.2542 | 527.376 | 369.7637 | 344.2489 | 127.5557
562.2542 | 527.2864 | 370.1591 | 344.7352 | 127.9585
563.2542 | 527.2921 | 370.5259 | 344.8088 | 128.3581
564.2542 | 527.3878 | 370.8387 | 345.2141 | 128.7619
565.2542 | 527.5049 | 371.2334 | 345.4517 | 129.1694
566.2542 | 527.5151 | 371.6097 | 345.8525 | 129.5798
567.2542 | 527.4455 | 371.9695 | 346.1528 | 129.9962
568.2542 | 527.4502 | 372.328 | 346.4685 | 130.4157
569.2542 | 527.4068 | 372.6733 | 346.9141 | 130.8319
570.2542 | 527.326 | 373.0114 | 347.1325 | 131.2584
571.2542 | 527.2648 | 373.3767 | 347.335 | 131.6916
572.2542 | 527.2196 | 373.722 | 347.6472 | 132.1291
573.2542 | 527.2236 | 374.0389 | 347.9719 | 132.561
574.2542 | 527.216 | 374.3902 | 348.1542 | 133.004
575.2542 | 527.2593 | 374.7492 | 348.5059 | 133.4377
576.2542 | 527.2747 | 375.1206 | 348.958 | 133.8785
577.2542 | 527.2267 | 375.4597 | 349.2517 | 134.3231
578.2542 | 527.1712 | 375.7864 | 349.7538 | 134.7594
579.2542 | 527.0873 | 376.1292 | 350.0744 | 135.199
580.2542 | 527.1017 | 376.4718 | 350.4481 | 135.6461
581.2542 | 527.2283 | 376.8384 | 350.6388 | 136.0976
582.2542 | 527.303 | 377.1822 | 350.8491 | 136.5552
583.2542 | 527.3232 | 377.5383 | 351.2025 | 136.9961
584.2542 | 527.3711 | 377.8867 | 351.5137 | 137.446
585.2542 | 527.359 | 378.2074 | 351.9675 | 137.9064
586.2542 | 527.328 | 378.521 | 352.0863 | 138.3598
587.2542 | 527.4186 | 378.8671 | 352.4906 | 138.8197
588.2542 | 527.4945 | 379.183 | 352.6941 | 139.2818
589.2542 | 527.4377 | 379.5304 | 352.8633 | 139.7403
590.2542 | 527.4756 | 379.8881 | 353.1987 | 140.2044
591.2542 | 527.4249 | 380.242 | 353.6154 | 140.6704
592.2542 | 527.4331 | 380.5451 | 354.1782 | 141.136
593.2542 | 527.4023 | 380.8873 | 354.5749 | 141.6157
594.2542 | 527.3942 | 381.2128 | 354.7832 | 142.0865
595.2542 | 527.4326 | 381.5385 | 354.9914 | 142.5555
596.2542 | 527.4922 | 381.8644 | 355.132 | 143.0151
597.2542 | 527.4795 | 382.2137 | 355.3098 | 143.4855
598.2542 | 527.4768 | 382.5417 | 355.5683 | 143.9603
599.2542 | 527.4433 | 382.8605 | 355.746 | 144.4308
600.2542 | 527.3509 | 383.1461 | 355.9669 | 144.9034
601.2542 | 527.3852 | 383.4792 | 356.454 | 145.3811
602.2542 | 527.3832 | 383.8223 | 356.7703 | 145.853
603.2542 | 527.4694 | 384.1309 | 356.9589 | 146.3268
604.2542 | 527.5503 | 384.454 | 357.2359 | 146.7952
605.2542 | 527.6691 | 384.7645 | 357.7687 | 147.2741
606.2542 | 527.7594 | 385.0586 | 357.7494 | 147.7561
607.2542 | 527.7854 | 385.3823 | 358.1172 | 148.2303
608.2542 | 527.7673 | 385.724 | 358.7511 | 148.7026
609.2542 | 527.7778 | 386.0398 | 358.8289 | 149.1837
610.2542 | 527.8612 | 386.3532 | 359.0638 | 149.6638
611.2542 | 527.8233 | 386.6566 | 359.5408 | 150.139
612.2542 | 527.7507 | 386.9204 | 359.9805 | 150.6246
613.2542 | 527.819 | 387.2581 | 360.2506 | 151.1015
614.2542 | 527.9115 | 387.5899 | 360.6347 | 151.5997
615.2542 | 527.9203 | 387.902 | 360.9405 | 152.0827
616.2542 | 528.0103 | 388.2129 | 361.1642 | 152.5598
617.2542 | 527.9884 | 388.5283 | 361.3993 | 153.0499
618.2542 | 527.9558 | 388.8128 | 361.7654 | 153.5342
619.2542 | 527.9104 | 389.1047 | 362.2362 | 154.0179
620.2542 | 527.8411 | 389.4425 | 362.3415 | 154.4986
621.2542 | 527.7969 | 389.7807 | 362.5115 | 154.9914
622.2542 | 527.7107 | 390.117 | 362.6034 | 155.4719
623.2542 | 527.7164 | 390.4196 | 362.7149 | 155.9622
624.2542 | 527.6474 | 390.6862 | 363.1026 | 156.4495
625.2542 | 527.6211 | 390.9411 | 363.4568 | 156.9318
626.2542 | 527.6365 | 391.2708 | 363.6881 | 157.4229
627.2542 | 527.6455 | 391.5917 | 364.185 | 157.9137
628.2542 | 527.615 | 391.903 | 364.2736 | 158.4024
629.2542 | 527.5454 | 392.2072 | 364.6726 | 158.8909
630.2542 | 527.4428 | 392.4923 | 365.1291 | 159.3759
631.2542 | 527.3191 | 392.7936 | 365.1793 | 159.8647
632.2542 | 527.3026 | 393.0953 | 365.5172 | 160.3606
633.2542 | 527.3117 | 393.3855 | 365.556 | 160.8545
634.2542 | 527.2284 | 393.663 | 365.6536 | 161.3516
635.2542 | 527.2241 | 393.9591 | 366.1372 | 161.8452
636.2542 | 527.2723 | 394.2523 | 366.3652 | 162.3369
637.2542 | 527.2492 | 394.5249 | 366.5624 | 162.8281
638.2542 | 527.28 | 394.7597 | 367.0757 | 163.3215
639.2542 | 527.284 | 395.0512 | 367.2472 | 163.8133
640.2542 | 527.2698 | 395.3412 | 367.5185 | 164.3016
641.2542 | 527.2537 | 395.6844 | 367.9587 | 164.7989
642.2542 | 527.1606 | 395.9181 | 367.9866 | 165.2953
643.2542 | 527.1024 | 396.2253 | 368.4574 | 165.7814
644.2542 | 527.0491 | 396.5351 | 369.021 | 166.2737
645.2542 | 527.0363 | 396.8121 | 369.3137 | 166.7616
646.2542 | 526.9423 | 397.1173 | 369.6604 | 167.2624
647.2542 | 526.9398 | 397.4395 | 369.615 | 167.7503
648.2542 | 526.943 | 397.7225 | 369.5712 | 168.244
649.2542 | 526.8233 | 397.9619 | 369.8344 | 168.7366
650.2542 | 526.7938 | 398.2397 | 370.2537 | 169.2266
651.2542 | 526.8327 | 398.5567 | 370.7659 | 169.7296
652.2542 | 526.8847 | 398.8523 | 370.9153 | 170.2185
653.2542 | 526.9284 | 399.0847 | 371.0256 | 170.7216
654.2542 | 526.9359 | 399.3452 | 371.0978 | 171.2112
655.2542 | 526.9213 | 399.6353 | 371.578 | 171.7064
656.2542 | 526.8937 | 399.9122 | 371.7651 | 172.2024
657.2542 | 526.7874 | 400.1724 | 372.2241 | 172.6955
658.2542 | 526.7567 | 400.4499 | 372.4849 | 173.1954
659.2542 | 526.7298 | 400.7199 | 372.6194 | 173.6834
660.2542 | 526.7492 | 400.9897 | 373.1307 | 174.1795
661.2542 | 526.7048 | 401.2664 | 373.3345 | 174.6706
662.2542 | 526.7135 | 401.514 | 373.2614 | 175.1735
663.2542 | 526.6881 | 401.8085 | 373.7612 | 175.6627
664.2542 | 526.7283 | 402.0718 | 374.0869 | 176.1564
665.2542 | 526.7584 | 402.3469 | 374.3372 | 176.6465
666.2542 | 526.8997 | 402.6223 | 374.4312 | 177.152
667.2542 | 527.0484 | 402.8715 | 374.6205 | 177.6377
668.2542 | 527.0407 | 403.1167 | 374.9765 | 178.1399
669.2542 | 527.0333 | 403.3874 | 375.3281 | 178.6283
670.2542 | 527.0884 | 403.6377 | 375.3583 | 179.1329
671.2542 | 527.1396 | 403.892 | 375.5136 | 179.6221
672.2542 | 527.2284 | 404.1474 | 376.0172 | 180.1117
673.2542 | 527.2348 | 404.4021 | 376.1334 | 180.6167
674.2542 | 527.3564 | 404.6518 | 376.3228 | 181.1127
675.2542 | 527.4522 | 404.9242 | 376.4948 | 181.594
676.2542 | 527.4319 | 405.173 | 376.7495 | 182.0972
677.2542 | 527.4424 | 405.4443 | 376.9297 | 182.5812
678.2542 | 527.4197 | 405.6729 | 377.0065 | 183.075
679.2542 | 527.4671 | 405.9188 | 377.1696 | 183.5647
680.2542 | 527.3878 | 406.146 | 377.5373 | 184.0525
681.2542 | 527.2828 | 406.3945 | 377.7981 | 184.5395
682.2542 | 527.2829 | 406.5923 | 378.2859 | 185.0363
683.2542 | 527.2805 | 406.8561 | 378.3304 | 185.522
684.2542 | 527.2631 | 407.097 | 378.5294 | 186.011
685.2542 | 527.112 | 407.3286 | 378.7539 | 186.5028
686.2542 | 527.0224 | 407.5582 | 379.263 | 186.987
687.2542 | 527.042 | 407.8298 | 379.6218 | 187.4708
688.2542 | 527.0545 | 408.0716 | 379.8016 | 187.9667
689.2542 | 527.0733 | 408.3147 | 379.7613 | 188.4506
690.2542 | 527.1411 | 408.5417 | 380.0615 | 188.9367
691.2542 | 527.225 | 408.794 | 380.3866 | 189.4218
692.2542 | 527.2696 | 409.0601 | 380.9662 | 189.9019
693.2542 | 527.2583 | 409.284 | 381.3761 | 190.4025
694.2542 | 527.2862 | 409.4945 | 381.5313 | 190.8761
695.2542 | 527.2914 | 409.7375 | 381.8908 | 191.3554
696.2542 | 527.3047 | 409.9636 | 381.8417 | 191.8426
697.2542 | 527.3722 | 410.2173 | 382.1786 | 192.3163
698.2542 | 527.466 | 410.4486 | 382.1515 | 192.8045
699.2542 | 527.5102 | 410.6789 | 382.4039 | 193.281
700.2542 | 527.5384 | 410.917 | 382.879 | 193.7606
701.2542 | 527.489 | 411.1567 | 382.9958 | 194.2392
702.2542 | 527.473 | 411.4242 | 383.4563 | 194.7244
703.2542 | 527.5058 | 411.6099 | 383.6154 | 195.2043
704.2542 | 527.479 | 411.8457 | 383.8528 | 195.6764
705.2542 | 527.5244 | 412.0953 | 384.3094 | 196.1481
706.2542 | 527.5783 | 412.3663 | 384.7969 | 196.6314
707.2542 | 527.5595 | 412.602 | 384.854 | 197.1116
708.2542 | 527.577 | 412.8307 | 385.2275 | 197.5861
709.2542 | 527.6267 | 413.0668 | 384.9294 | 198.0734
710.2542 | 527.6368 | 413.3107 | 384.9704 | 198.5493
711.2542 | 527.6109 | 413.537 | 385.489 | 199.0224
712.2542 | 527.5997 | 413.7771 | 385.9447 | 199.501
713.2542 | 527.5776 | 413.9944 | 386.2169 | 199.9717
714.2542 | 527.4699 | 414.2384 | 386.4647 | 200.4704
715.2542 | 527.4901 | 414.473 | 386.5727 | 200.9491
716.2542 | 527.5159 | 414.7072 | 386.5108 | 201.4228
717.2542 | 527.6293 | 414.9208 | 386.4434 | 201.8929
718.2542 | 527.6281 | 415.1248 | 386.8948 | 202.3537
719.2542 | 527.6617 | 415.3556 | 387.249 | 202.8264
720.2542 | 527.7497 | 415.5199 | 387.5326 | 203.2937
721.2542 | 527.7079 | 415.7484 | 387.6496 | 203.766
722.2542 | 527.6058 | 415.9984 | 388.1728 | 204.226
723.2542 | 527.6326 | 416.2353 | 388.6081 | 204.6873
724.2542 | 527.6562 | 416.4585 | 388.3746 | 205.1581
725.2542 | 527.7299 | 416.6994 | 388.3318 | 205.6221
726.2542 | 527.8525 | 416.9285 | 388.4856 | 206.0753
727.2542 | 527.9491 | 417.1129 | 389.0057 | 206.5385
728.2542 | 527.977 | 417.3585 | 389.5916 | 207.0055
729.2542 | 527.9727 | 417.5801 | 389.8784 | 207.4628
730.2542 | 527.9836 | 417.8079 | 390.077 | 207.921
731.2542 | 528.0142 | 417.9711 | 390.398 | 208.383
732.2542 | 528.0119 | 418.2048 | 390.5454 | 208.8478
733.2542 | 527.9892 | 418.4399 | 390.4886 | 209.3004
734.2542 | 527.9302 | 418.6538 | 390.6703 | 209.7516
735.2542 | 527.8067 | 418.8912 | 390.6901 | 210.2178
736.2542 | 527.7621 | 419.1057 | 390.98 | 210.6892
737.2542 | 527.7754 | 419.3036 | 390.9356 | 211.1419
738.2542 | 527.7719 | 419.5101 | 391.2437 | 211.6072
739.2542 | 527.756 | 419.7234 | 391.654 | 212.0706
740.2542 | 527.6538 | 419.9252 | 391.9836 | 212.5367
741.2542 | 527.6419 | 420.128 | 392.3526 | 213.0042
742.2542 | 527.6449 | 420.3101 | 392.6869 | 213.4692
743.2542 | 527.5969 | 420.5206 | 392.632 | 213.9287
744.2542 | 527.6818 | 420.7093 | 392.8757 | 214.3933
745.2542 | 527.7633 | 420.9242 | 392.8637 | 214.8551
746.2542 | 527.7793 | 421.1191 | 392.9126 | 215.3114
747.2542 | 527.8424 | 421.3178 | 393.1973 | 215.7758
748.2542 | 527.8589 | 421.5399 | 393.6829 | 216.2397
749.2542 | 527.7925 | 421.7475 | 394.1217 | 216.7027
750.2542 | 527.7424 | 421.9302 | 394.2622 | 217.1504
751.2542 | 527.6648 | 422.116 | 394.4683 | 217.6178
752.2542 | 527.5997 | 422.3422 | 394.2422 | 218.0677
753.2542 | 527.562 | 422.5314 | 394.6804 | 218.5098
754.2542 | 527.6323 | 422.7214 | 394.7087 | 218.9628
755.2542 | 527.5798 | 422.9228 | 394.695 | 219.412
756.2542 | 527.5429 | 423.1322 | 395.0783 | 219.8663
757.2542 | 527.623 | 423.3308 | 395.4576 | 220.2811
758.2542 | 527.7574 | 423.5304 | 395.6391 | 220.7092
759.2542 | 527.8475 | 423.7125 | 395.7669 | 221.1462
760.2542 | 527.8529 | 423.9027 | 396.1937 | 221.5771
761.2542 | 527.9281 | 424.1215 | 396.547 | 222.0027
762.2542 | 527.98 | 424.3063 | 396.5542 | 222.4384
763.2542 | 527.9636 | 424.4746 | 396.4442 | 222.8615
764.2542 | 527.9858 | 424.6814 | 396.604 | 223.2999
765.2542 | 528.0392 | 424.8728 | 396.6276 | 223.7223
766.2542 | 528.144 | 425.0759 | 397.0525 | 224.1616
767.2542 | 528.1299 | 425.2579 | 397.4867 | 224.5924
768.2542 | 528.0302 | 425.4317 | 397.7311 | 225.026
769.2542 | 527.9777 | 425.6495 | 397.6553 | 225.4597
770.2542 | 527.9713 | 425.7857 | 397.8791 | 225.8947
771.2542 | 527.9655 | 425.9974 | 397.9777 | 226.3278
772.2542 | 527.8973 | 426.1964 | 398.1753 | 226.7643
773.2542 | 527.8475 | 426.3939 | 398.0871 | 227.1952
774.2542 | 527.8333 | 426.599 | 398.6532 | 227.629
775.2542 | 527.773 | 426.7913 | 399.0653 | 228.0634
776.2542 | 527.7224 | 426.9696 | 399.1005 | 228.5028
777.2542 | 527.7011 | 427.162 | 399.6256 | 228.93
778.2542 | 527.7238 | 427.3407 | 400.1143 | 229.3661
779.2542 | 527.7656 | 427.5209 | 400.1297 | 229.7893
780.2542 | 527.7897 | 427.691 | 400.1064 | 230.2238
781.2542 | 527.7633 | 427.8867 | 400.3764 | 230.6432
782.2542 | 527.7576 | 428.0263 | 400.3857 | 231.062
783.2542 | 527.7833 | 428.1685 | 400.7504 | 231.4814
784.2542 | 527.7338 | 428.3951 | 401.2127 | 231.8941
785.2542 | 527.724 | 428.5828 | 401.3727 | 232.3112
786.2542 | 527.7808 | 428.7914 | 401.6923 | 232.7189
787.2542 | 527.7912 | 428.9758 | 401.8779 | 233.1197
788.2542 | 527.8143 | 429.1699 | 401.5415 | 233.5205
789.2542 | 527.8313 | 429.3238 | 401.6979 | 233.9244
790.2542 | 527.7761 | 429.4786 | 402.1332 | 234.3183
791.2542 | 527.7941 | 429.6708 | 402.1929 | 234.7039
792.2542 | 527.8119 | 429.8654 | 402.1351 | 235.0862
793.2542 | 527.7691 | 430.058 | 402.2924 | 235.4769
794.2542 | 527.7584 | 430.1751 | 402.9575 | 235.8748
795.2542 | 527.6887 | 430.3966 | 403.0436 | 236.2856
796.2542 | 527.5935 | 430.6002 | 403.6713 | 236.7162
797.2542 | 527.5436 | 430.7886 | 403.6507 | 237.148
798.2542 | 527.4802 | 430.9616 | 403.6159 | 237.5721
799.2542 | 527.4077 | 431.1279 | 404.1476 | 237.9907
800.2542 | 527.3416 | 431.3046 | 404.2243 | 238.4218
801.2542 | 527.407 | 431.489 | 404.6128 | 238.847
802.2542 | 527.4454 | 431.6655 | 404.6348 | 239.2662
803.2542 | 527.3847 | 431.8476 | 404.4697 | 239.6764
804.2542 | 527.3603 | 432.0121 | 404.8074 | 240.0817
805.2542 | 527.2753 | 432.16 | 405.2336 | 240.4915
806.2542 | 527.244 | 432.3349 | 405.7495 | 240.8972
807.2542 | 527.2174 | 432.5158 | 405.9056 | 241.2981
808.2542 | 527.206 | 432.7027 | 405.9884 | 241.7085
809.2542 | 527.2448 | 432.8893 | 406.2264 | 242.1025
810.2542 | 527.278 | 433.0564 | 406.3474 | 242.4977
811.2542 | 527.2803 | 433.2291 | 406.186 | 242.8963
812.2542 | 527.2667 | 433.3523 | 406.3883 | 243.2968
813.2542 | 527.286 | 433.5541 | 406.3425 | 243.6944
814.2542 | 527.2336 | 433.7144 | 406.8344 | 244.087
815.2542 | 527.2184 | 433.9075 | 407.3082 | 244.4881
816.2542 | 527.1363 | 434.063 | 407.3284 | 244.8914
817.2542 | 527.0074 | 434.24 | 407.4865 | 245.2806
818.2542 | 527.0173 | 434.3911 | 407.5932 | 245.6481
819.2542 | 527.0574 | 434.5463 | 408.1734 | 246.0076
820.2542 | 527.0776 | 434.7223 | 408.1873 | 246.3703
821.2542 | 527.0622 | 434.8634 | 408.6535 | 246.733
822.2542 | 527.0506 | 435.0379 | 408.7002 | 247.0999
823.2542 | 527.0055 | 435.1989 | 408.9769 | 247.468
824.2542 | 526.8936 | 435.3784 | 409.3588 | 247.8386
825.2542 | 526.7446 | 435.5482 | 409.368 | 248.2113
826.2542 | 526.6834 | 435.7148 | 409.3232 | 248.5799
827.2542 | 526.6628 | 435.8851 | 409.7995 | 248.9839
828.2542 | 526.5941 | 436.0567 | 409.8005 | 249.3485
829.2542 | 526.5836 | 436.2193 | 409.6622 | 249.7216
830.2542 | 526.4505 | 436.3736 | 409.9363 | 250.0755
831.2542 | 526.4841 | 436.5359 | 410.3095 | 250.4223
832.2542 | 526.4891 | 436.7024 | 410.192 | 250.7716
833.2542 | 526.3794 | 436.8364 | 410.6334 | 251.133
834.2542 | 526.3287 | 437.0125 | 410.9606 | 251.4669
835.2542 | 526.3034 | 437.1632 | 411.0305 | 251.7667
836.2542 | 526.3227 | 437.3265 | 411.2056 | 252.1481
837.2542 | 526.3878 | 437.4763 | 411.4073 | 252.5157
838.2542 | 526.3792 | 437.6116 | 411.5912 | 252.8857
839.2542 | 526.3693 | 437.7896 | 411.8263 | 253.2254
840.2542 | 526.4322 | 437.9419 | 411.8302 | 253.6156
841.2542 | 526.4277 | 438.0908 | 412.0612 | 254.0035
842.2542 | 526.4926 | 438.2481 | 412.0226 | 254.3423
843.2542 | 526.5252 | 438.4047 | 411.9484 | 254.7061
844.2542 | 526.4675 | 438.5627 | 412.3887 | 255.0511
845.2542 | 526.5329 | 438.7093 | 412.5386 | 255.4354
846.2542 | 526.6345 | 438.804 | 412.4736 | 255.7822
847.2542 | 526.7753 | 438.9862 | 412.8904 | 256.1271
848.2542 | 526.7893 | 439.181 | 413.0726 | 256.4923
849.2542 | 526.8762 | 439.3433 | 413.3887 | 256.8429
850.2542 | 526.9417 | 439.4994 | 413.4902 | 257.1762
851.2542 | 527.0031 | 439.6453 | 413.6636 | 257.49
852.2542 | 527.0064 | 439.8069 | 413.7298 | 257.7732
853.2542 | 527.0583 | 439.9515 | 414.0365 | 258.021
854.2542 | 527.1205 | 440.1253 | 414.0283 | 258.2396
855.2542 | 527.1592 | 440.2649 | 414.179 | 258.4519
856.2542 | 527.2074 | 440.4541 | 414.4685 | 258.6803
857.2542 | 527.2741 | 440.5994 | 414.5568 | 258.9975
858.2542 | 527.267 | 440.7268 | 414.6473 | 259.3178
859.2542 | 527.2492 | 440.904 | 414.9264 | 259.5738
860.2542 | 527.252 | 441.0712 | 415.2143 | 259.7748
861.2542 | 527.315 | 441.2327 | 415.355 | 259.9981
862.2542 | 527.2645 | 441.3746 | 415.8559 | 260.1717
863.2542 | 527.1004 | 441.5466 | 415.5927 | 260.4399
864.2542 | 527.0352 | 441.6669 | 415.8961 | 260.7343
865.2542 | 526.9913 | 441.8341 | 416.1887 | 260.9463
866.2542 | 527.0152 | 441.9783 | 416.6432 | 261.1634
867.2542 | 527.0854 | 442.1334 | 416.8729 | 261.3658
868.2542 | 527.1585 | 442.2879 | 416.8599 | 261.6058
869.2542 | 527.208 | 442.4184 | 417.0099 | 261.8126
870.2542 | 527.2615 | 442.5644 | 416.75 | 261.9847
871.2542 | 527.287 | 442.7165 | 417.022 | 262.1899
872.2542 | 527.2851 | 442.8483 | 417.2706 | 262.3243
873.2542 | 527.2088 | 443.0052 | 417.369 | 262.5304
874.2542 | 527.2118 | 443.1256 | 417.9034 | 262.7589
875.2542 | 527.281 | 443.2798 | 418.0171 | 262.9749
876.2542 | 527.2759 | 443.4082 | 418.1092 | 263.1987
877.2542 | 527.3042 | 443.5998 | 417.8585 | 263.4632
878.2542 | 527.3981 | 443.7464 | 417.9673 | 263.7418
879.2542 | 527.4183 | 443.9074 | 418.3093 | 263.98
880.2542 | 527.4454 | 444.0605 | 418.7819 | 264.2064
881.2542 | 527.4912 | 444.2063 | 418.9549 | 264.4294
882.2542 | 527.5237 | 444.3523 | 419.126 | 264.6269
883.2542 | 527.6162 | 444.4869 | 419.0512 | 264.8533
884.2542 | 527.6121 | 444.6454 | 419.1203 | 265.0635
885.2542 | 527.554 | 444.8113 | 418.9481 | 265.2892
886.2542 | 527.5671 | 444.9695 | 418.8976 | 265.5307
887.2542 | 527.5837 | 445.1208 | 419.2335 | 265.7962
888.2542 | 527.624 | 445.2584 | 419.2349 | 266.0405
889.2542 | 527.6712 | 445.4051 | 419.3959 | 266.2784
890.2542 | 527.6448 | 445.5249 | 420.0263 | 266.4681
891.2542 | 527.6898 | 445.6194 | 420.0018 | 266.6355
892.2542 | 527.6994 | 445.7257 | 420.065 | 266.8585
893.2542 | 527.6308 | 445.8799 | 420.4451 | 267.0873
894.2542 | 527.6052 | 446.0657 | 420.5781 | 267.3144
895.2542 | 527.6258 | 446.2226 | 420.9924 | 267.4784
896.2542 | 527.6225 | 446.3736 | 420.865 | 267.6282
897.2542 | 527.705 | 446.5164 | 420.9177 | 267.9292
898.2542 | 527.7141 | 446.6702 | 421.1795 | 268.1584
899.2542 | 527.7816 | 446.807 | 421.5131 | 268.4277
900.2542 | 527.7905 | 446.9418 | 421.4846 | 268.7215
901.2542 | 527.7857 | 447.0331 | 421.5601 | 268.9296
902.2542 | 527.7653 | 447.2274 | 421.8311 | 269.1655
903.2542 | 527.7041 | 447.3709 | 421.9624 | 269.4031
904.2542 | 527.7206 | 447.5165 | 421.9235 | 269.7214
905.2542 | 527.6933 | 447.6508 | 422.2153 | 270.0101
906.2542 | 527.5549 | 447.7857 | 422.6924 | 270.2681
907.2542 | 527.4182 | 447.9247 | 422.7981 | 270.4628
908.2542 | 527.3843 | 448.0659 | 423.1587 | 270.6774
909.2542 | 527.4805 | 448.1803 | 423.3671 | 270.906
910.2542 | 527.4959 | 448.3031 | 423.5296 | 271.1036
911.2542 | 527.5396 | 448.4635 | 423.4779 | 271.3745
912.2542 | 527.6029 | 448.6171 | 423.5686 | 271.6046
913.2542 | 527.6527 | 448.7225 | 423.7981 | 271.8213
914.2542 | 527.6987 | 448.8843 | 423.8043 | 271.9832
915.2542 | 527.6846 | 449.0422 | 423.7073 | 272.1528
916.2542 | 527.7067 | 449.1577 | 423.4728 | 272.3405
917.2542 | 527.7979 | 449.2962 | 423.4319 | 272.5155
918.2542 | 527.9296 | 449.4233 | 423.7196 | 272.7353
919.2542 | 527.9119 | 449.5614 | 424.0146 | 272.9458
920.2542 | 527.9593 | 449.7179 | 424.2118 | 273.105
921.2542 | 528.044 | 449.8527 | 424.72 | 273.2725
922.2542 | 528.116 | 449.9973 | 424.9248 | 273.5359
923.2542 | 528.1435 | 450.0921 | 425.0788 | 273.8734
924.2542 | 528.1692 | 450.1654 | 424.9909 | 274.1507
925.2542 | 528.1058 | 450.3431 | 425.0294 | 274.3235
926.2542 | 528.0772 | 450.4858 | 424.8395 | 274.51
927.2542 | 528.2068 | 450.5953 | 425.091 | 274.7296
928.2542 | 528.1344 | 450.7092 | 425.3026 | 274.913
929.2542 | 528.0603 | 450.8575 | 425.5883 | 275.103
930.2542 | 528.0072 | 450.9762 | 425.7041 | 275.2973
931.2542 | 527.9251 | 451.1191 | 425.5442 | 275.5043
932.2542 | 527.8806 | 451.2711 | 425.8969 | 275.7384
933.2542 | 527.8722 | 451.3594 | 425.9271 | 275.9596
934.2542 | 527.8048 | 451.4647 | 426.2636 | 276.1809
935.2542 | 527.7138 | 451.6024 | 426.7941 | 276.4114
936.2542 | 527.631 | 451.7469 | 427.0605 | 276.681
937.2542 | 527.5124 | 451.91 | 427.3819 | 276.9086
938.2542 | 527.3226 | 452.0483 | 427.3097 | 277.2769
939.2542 | 527.3246 | 452.1467 | 427.2377 | 277.6375
940.2542 | 527.39 | 452.2787 | 427.11 | 277.9399
941.2542 | 527.3462 | 452.4186 | 426.9714 | 278.2545
942.2542 | 527.2801 | 452.5185 | 427.1823 | 278.496
943.2542 | 527.1555 | 452.6348 | 427.5298 | 278.7718
944.2542 | 527.1088 | 452.7504 | 427.3814 | 279.0499
945.2542 | 527.1311 | 452.8276 | 427.5976 | 279.3694
946.2542 | 527.1218 | 452.9506 | 427.7799 | 279.6194
947.2542 | 527.0926 | 453.1113 | 427.8626 | 279.8262
948.2542 | 527.0869 | 453.2353 | 427.8321 | 280.0589
949.2542 | 527.0574 | 453.3869 | 428.3006 | 280.3202
950.2542 | 527.0335 | 453.5318 | 428.2844 | 280.5666
951.2542 | 527.0336 | 453.5968 | 428.617 | 280.8451
952.2542 | 527.0031 | 453.7464 | 428.6451 | 281.0951
953.2542 | 527.0281 | 453.8863 | 428.7587 | 281.3647
954.2542 | 527.058 | 454.0329 | 429.1333 | 281.5936
955.2542 | 527.1273 | 454.1459 | 429.2186 | 281.8673
956.2542 | 527.1285 | 454.2472 | 429.1845 | 282.1387
957.2542 | 527.2254 | 454.3646 | 429.1605 | 282.4124
958.2542 | 527.3275 | 454.4886 | 429.4477 | 282.6546
959.2542 | 527.3518 | 454.5975 | 429.8493 | 282.9163
960.2542 | 527.3233 | 454.7084 | 430.0977 | 283.1806
961.2542 | 527.2677 | 454.8413 | 429.9631 | 283.4741
962.2542 | 527.2494 | 454.9716 | 430.3065 | 283.7158
963.2542 | 527.2568 | 455.077 | 430.3394 | 283.9624
964.2542 | 527.2571 | 455.1778 | 430.3572 | 284.1741
965.2542 | 527.2116 | 455.3044 | 430.5848 | 284.3124
966.2542 | 527.2456 | 455.4178 | 430.4544 | 284.4114
967.2542 | 527.2979 | 455.5571 | 430.7871 | 284.5102
968.2542 | 527.3099 | 455.6761 | 430.7574 | 284.6774
969.2542 | 527.4397 | 455.8002 | 430.815 | 284.8996
970.2542 | 527.4372 | 455.8936 | 431.0901 | 285.0596
971.2542 | 527.4744 | 456.0266 | 431.1264 | 285.2708
972.2542 | 527.4972 | 456.1493 | 431.0763 | 285.5137
973.2542 | 527.4984 | 456.2573 | 431.4931 | 285.7095
974.2542 | 527.4913 | 456.3722 | 431.8955 | 285.8948
975.2542 | 527.5445 | 456.4974 | 431.7545 | 286.1002
976.2542 | 527.5927 | 456.6105 | 431.5899 | 286.2959
977.2542 | 527.5431 | 456.6972 | 431.6641 | 286.5097
978.2542 | 527.6448 | 456.7815 | 431.3158 | 286.7093
979.2542 | 527.729 | 456.8711 | 431.4299 | 286.932
980.2542 | 527.7232 | 457.0007 | 431.8211 | 287.1301
981.2542 | 527.7194 | 457.1143 | 431.8085 | 287.329
982.2542 | 527.7128 | 457.2092 | 431.7238 | 287.5458
983.2542 | 527.6872 | 457.3272 | 431.8398 | 287.7607
984.2542 | 527.7063 | 457.4584 | 432.0133 | 287.9589
985.2542 | 527.7551 | 457.5475 | 432.5861 | 288.1483
986.2542 | 527.7106 | 457.6818 | 432.625 | 288.3623
987.2542 | 527.6584 | 457.6894 | 432.6333 | 288.5655
988.2542 | 527.6493 | 457.8106 | 432.6128 | 288.778
989.2542 | 527.703 | 457.9241 | 432.778 | 288.9824
990.2542 | 527.6911 | 458.0755 | 433.1278 | 289.2146
991.2542 | 527.656 | 458.1867 | 433.1179 | 289.4383
992.2542 | 527.6519 | 458.2796 | 433.1388 | 289.6403
993.2542 | 527.6655 | 458.4096 | 432.8768 | 289.8986
994.2542 | 527.6789 | 458.5087 | 432.7955 | 290.1579
995.2542 | 527.6487 | 458.613 | 432.9978 | 290.3662
996.2542 | 527.5452 | 458.7026 | 433.697 | 290.6363
997.2542 | 527.5319 | 458.8261 | 433.4519 | 290.8554
998.2542 | 527.6119 | 458.9452 | 433.2817 | 291.0842
999.2542 | 527.6888 | 459.0381 | 433.5849 | 291.3159
1000.2542 | 527.6976 | 459.0687 | 433.9245 | 291.3925
1001.2542 | 527.5909 | 459.2148 | 433.8471 | 291.7083
1002.2542 | 527.5913 | 459.3318 | 434.2894 | 291.951
1003.2542 | 527.5786 | 459.4438 | 434.6237 | 292.2092
1004.2542 | 527.6325 | 459.5529 | 434.742 | 292.4733
1005.2542 | 527.6325 | 459.5768 | 434.7392 | 292.7467
1006.2542 | 527.6398 | 459.6987 | 434.5433 | 292.9886
1007.2542 | 527.6649 | 459.8433 | 434.4284 | 293.1878
1008.2542 | 527.6205 | 459.9483 | 434.3928 | 293.3973
1009.2542 | 527.6553 | 460.0047 | 434.7166 | 293.665
1010.2542 | 527.6091 | 460.1395 | 435.0904 | 293.9297
1011.2542 | 527.5081 | 460.2445 | 435.0712 | 294.1422
1012.2542 | 527.4565 | 460.3736 | 435.1034 | 294.3554
1013.2542 | 527.3968 | 460.4382 | 435.3032 | 294.5775
1014.2542 | 527.413 | 460.5195 | 435.1881 | 294.8704
1015.2542 | 527.4217 | 460.6291 | 435.5868 | 295.1373
1016.2542 | 527.3786 | 460.735 | 435.7886 | 295.4278
1017.2542 | 527.335 | 460.8665 | 435.6908 | 295.6666
1018.2542 | 527.3794 | 460.9698 | 435.5208 | 295.9694
1019.2542 | 527.4245 | 461.0711 | 435.4419 | 296.2557
1020.2542 | 527.3901 | 461.2056 | 436.0791 | 296.5068
1021.2542 | 527.5172 | 461.3141 | 436.0982 | 296.8525
1022.2542 | 527.6049 | 461.3802 | 435.8556 | 297.1578
1023.2542 | 527.6221 | 461.4662 | 435.9983 | 297.4011
1024.2542 | 527.5511 | 461.5825 | 436.7442 | 297.7
1025.2542 | 527.596 | 461.7031 | 437.0127 | 297.9947
1026.2542 | 527.5558 | 461.7798 | 436.9666 | 298.2499
1027.2542 | 527.4749 | 461.8828 | 437.3655 | 298.5274
1028.2542 | 527.4884 | 462.0077 | 437.2602 | 298.8047
1029.2542 | 527.4889 | 462.0958 | 437.22 | 299.1391
1030.2542 | 527.5148 | 462.205 | 437.2684 | 299.3933
1031.2542 | 527.5006 | 462.2904 | 437.5778 | 299.7602
1032.2542 | 527.4966 | 462.3916 | 437.8999 | 300.0019
1033.2542 | 527.5325 | 462.463 | 437.9165 | 300.3364
1034.2542 | 527.5067 | 462.5579 | 438.25 | 300.5845
1035.2542 | 527.5308 | 462.6688 | 438.2437 | 300.7798
1036.2542 | 527.5332 | 462.7672 | 438.2919 | 301.078
1037.2542 | 527.5478 | 462.8602 | 438.331 | 301.2698
1038.2542 | 527.5758 | 462.9573 | 438.3496 | 301.4475
1039.2542 | 527.5646 | 462.9745 | 438.4371 | 301.695
1040.2542 | 527.4683 | 463.1193 | 438.8278 | 301.9769
1041.2542 | 527.4765 | 463.2654 | 438.7401 | 302.2641
1042.2542 | 527.4835 | 463.3639 | 438.5892 | 302.6552
1043.2542 | 527.5658 | 463.4751 | 438.4645 | 302.8809
1044.2542 | 527.6052 | 463.5728 | 438.6912 | 303.0352
1045.2542 | 527.6045 | 463.6433 | 438.5032 | 303.2475
1046.2542 | 527.6528 | 463.7487 | 438.499 | 303.4848
1047.2542 | 527.6952 | 463.8634 | 438.9445 | 303.6862
1048.2542 | 527.6046 | 463.9662 | 438.8862 | 303.9317
1049.2542 | 527.573 | 464.0397 | 439.0956 | 304.152
1050.2542 | 527.5542 | 464.1298 | 438.9543 | 304.2667
1051.2542 | 527.485 | 464.2091 | 438.8218 | 304.3647
1052.2542 | 527.4444 | 464.3288 | 439.4358 | 304.4936
1053.2542 | 527.3562 | 464.4396 | 439.8998 | 304.6656
1054.2542 | 527.2503 | 464.5121 | 439.7451 | 304.9922
1055.2542 | 527.1263 | 464.6039 | 440.1206 | 305.3598
1056.2542 | 527.0767 | 464.7072 | 440.4468 | 305.6265
1057.2542 | 527.1054 | 464.7517 | 440.5091 | 305.8709
1058.2542 | 527.1563 | 464.8613 | 440.6754 | 306.0776
1059.2542 | 527.1619 | 464.9774 | 440.7069 | 306.3035
1060.2542 | 527.1581 | 465.0716 | 440.4378 | 306.5521
1061.2542 | 527.1654 | 465.0646 | 440.4991 | 306.7339
1062.2542 | 527.2055 | 465.1829 | 440.5899 | 306.9322
1063.2542 | 527.1716 | 465.2676 | 440.4517 | 307.1155
1064.2542 | 527.1157 | 465.3892 | 440.2957 | 307.3571
1065.2542 | 527.1617 | 465.4609 | 440.3329 | 307.6385
1066.2542 | 527.2119 | 465.5373 | 440.6044 | 307.8716
1067.2542 | 527.2262 | 465.6245 | 440.3614 | 308.0955
1068.2542 | 527.2261 | 465.7222 | 440.8162 | 308.2917
1069.2542 | 527.2876 | 465.8027 | 441.3026 | 308.5218
1070.2542 | 527.3189 | 465.8941 | 441.271 | 308.736
1071.2542 | 527.2688 | 465.8031 | 441.3666 | 308.9807
1072.2542 | 527.2671 | 465.9801 | 441.2986 | 309.1661
1073.2542 | 527.2361 | 466.0974 | 441.3174 | 309.4
1074.2542 | 527.1344 | 466.1954 | 441.7849 | 309.6834
1075.2542 | 526.9897 | 466.3169 | 442.0089 | 309.9258
1076.2542 | 526.9217 | 466.4008 | 441.9772 | 310.1836
1077.2542 | 526.9491 | 466.5003 | 442.1785 | 310.4451
1078.2542 | 527.0037 | 466.5785 | 442.4466 | 310.6888
1079.2542 | 527.0047 | 466.6258 | 442.1206 | 310.9541
1080.2542 | 526.9698 | 466.6906 | 441.7005 | 311.1817
1081.2542 | 527.0011 | 466.7615 | 441.9072 | 311.3712
1082.2542 | 527.0823 | 466.8706 | 441.9585 | 311.684
1083.2542 | 527.0208 | 466.9916 | 442.3312 | 311.999
1084.2542 | 527.0684 | 467.07 | 442.6981 | 312.1997
1085.2542 | 527.1321 | 467.1626 | 442.9488 | 312.4208
1086.2542 | 527.206 | 467.2104 | 442.8038 | 312.6416
1087.2542 | 527.2029 | 467.2751 | 442.9196 | 312.8741
1088.2542 | 527.2599 | 467.3922 | 443.237 | 313.1296
1089.2542 | 527.2699 | 467.4653 | 443.0502 | 313.4083
1090.2542 | 527.2468 | 467.569 | 443.218 | 313.6549
1091.2542 | 527.3032 | 467.6666 | 443.4936 | 313.9386
1092.2542 | 527.303 | 467.7739 | 443.5601 | 314.2502
1093.2542 | 527.3048 | 467.8534 | 443.6171 | 314.5353
1094.2542 | 527.3983 | 467.8998 | 443.3517 | 314.8049
1095.2542 | 527.4904 | 467.9981 | 443.5586 | 315.1353
1096.2542 | 527.533 | 468.0814 | 443.3999 | 315.3973
1097.2542 | 527.5628 | 468.1397 | 443.6981 | 315.6558
1098.2542 | 527.6212 | 468.2143 | 443.6252 | 315.9228
1099.2542 | 527.6524 | 468.3078 | 443.8976 | 316.2108
1100.2542 | 527.7 | 468.4087 | 444.2688 | 316.492
1101.2542 | 527.73 | 468.4988 | 444.4697 | 316.7636
1102.2542 | 527.75 | 468.5389 | 444.3076 | 317.0489
1103.2542 | 527.6864 | 468.6135 | 444.4055 | 317.2648
1104.2542 | 527.6605 | 468.7135 | 444.3831 | 317.5241
1105.2542 | 527.6648 | 468.8083 | 444.4124 | 317.7568
1106.2542 | 527.6975 | 468.8952 | 444.2259 | 317.9851
1107.2542 | 527.6412 | 468.956 | 444.2771 | 318.3232
1108.2542 | 527.5734 | 469.0288 | 444.5258 | 318.5843
1109.2542 | 527.6052 | 469.1412 | 444.4756 | 318.7886
1110.2542 | 527.6335 | 469.2149 | 444.1111 | 319.0547
1111.2542 | 527.6344 | 469.2756 | 444.4347 | 319.3139
1112.2542 | 527.5814 | 469.3361 | 444.648 | 319.5754
1113.2542 | 527.5668 | 469.4044 | 444.8694 | 319.9015
1114.2542 | 527.515 | 469.5162 | 444.9544 | 320.1412
1115.2542 | 527.5226 | 469.5991 | 444.9556 | 320.3644
1116.2542 | 527.4037 | 469.6847 | 444.8166 | 320.6315
1117.2542 | 527.3064 | 469.6987 | 445.1314 | 320.898
1118.2542 | 527.3003 | 469.7521 | 445.0712 | 321.1565
1119.2542 | 527.2945 | 469.8423 | 445.4562 | 321.4597
1120.2542 | 527.2237 | 469.9485 | 445.5211 | 321.7962
1121.2542 | 527.2323 | 469.9971 | 445.4875 | 322.09
1122.2542 | 527.363 | 470.1014 | 445.3077 | 322.3558
1123.2542 | 527.4567 | 470.1815 | 445.464 | 322.641
1124.2542 | 527.5457 | 470.2202 | 445.4336 | 322.8911
1125.2542 | 527.5368 | 470.2897 | 445.9337 | 323.3203
1126.2542 | 527.4393 | 470.3885 | 446.0679 | 323.5819
1127.2542 | 527.3975 | 470.4857 | 446.0939 | 323.8916
1128.2542 | 527.3499 | 470.5508 | 446.2163 | 324.2364
1129.2542 | 527.4136 | 470.6271 | 446.318 | 324.6367
1130.2542 | 527.3975 | 470.6856 | 446.481 | 324.9836
1131.2542 | 527.3901 | 470.7653 | 446.5098 | 325.2839
1132.2542 | 527.4067 | 470.8499 | 446.6401 | 325.5299
1133.2542 | 527.2718 | 470.9198 | 446.5684 | 325.7884
1134.2542 | 527.3866 | 470.9875 | 446.8673 | 326.1054
1135.2542 | 527.447 | 471.0706 | 446.7676 | 326.443
1136.2542 | 527.3723 | 471.1194 | 446.9951 | 326.788
1137.2542 | 527.3892 | 471.2229 | 446.88 | 327.0508
1138.2542 | 527.3609 | 471.3203 | 447.0105 | 327.3906
1139.2542 | 527.3211 | 471.3869 | 446.9076 | 327.7484
1140.2542 | 527.1825 | 471.4117 | 447.0894 | 328.0309
1141.2542 | 527.1361 | 471.4551 | 447.4205 | 328.3794
1142.2542 | 527.1438 | 471.5584 | 447.5836 | 328.7863
1143.2542 | 527.1377 | 471.6073 | 447.3441 | 329.147
1144.2542 | 527.1256 | 471.7033 | 447.3645 | 329.4649
1145.2542 | 527.0907 | 471.7896 | 447.7415 | 329.7309
1146.2542 | 527.061 | 471.863 | 447.8346 | 329.9933
1147.2542 | 526.9975 | 471.9432 | 447.5652 | 330.277
1148.2542 | 526.9177 | 471.9899 | 447.3363 | 330.5995
1149.2542 | 526.8682 | 472.0377 | 447.6571 | 330.922
1150.2542 | 526.8974 | 472.1072 | 447.274 | 331.1924
1151.2542 | 526.897 | 472.1456 | 447.8007 | 331.4949
1152.2542 | 526.8534 | 472.2527 | 447.9268 | 331.8143
1153.2542 | 526.8233 | 472.3219 | 448.2136 | 332.1143
1154.2542 | 526.761 | 472.3863 | 448.2138 | 332.3762
1155.2542 | 526.6973 | 472.4259 | 448.1058 | 332.7176
1156.2542 | 526.6947 | 472.4694 | 448.2341 | 332.9691
1157.2542 | 526.7754 | 472.5789 | 448.603 | 333.2564
1158.2542 | 526.7502 | 472.6402 | 448.3481 | 333.5459
1159.2542 | 526.6512 | 472.6823 | 448.6972 | 333.8135
1160.2542 | 526.7146 | 472.7639 | 448.4866 | 334.1112
1161.2542 | 526.7312 | 472.8324 | 448.3637 | 334.3982
1162.2542 | 526.7333 | 472.8999 | 448.3483 | 334.7256
1163.2542 | 526.6771 | 472.9656 | 448.8496 | 334.9853
1164.2542 | 526.6409 | 473.0528 | 449.0146 | 335.2482
1165.2542 | 526.7033 | 473.1187 | 448.7084 | 335.5092
1166.2542 | 526.6672 | 473.1778 | 448.8549 | 335.7958
1167.2542 | 526.7028 | 473.2365 | 449.2595 | 336.0653
1168.2542 | 526.7416 | 473.2991 | 449.4482 | 336.3921
1169.2542 | 526.7267 | 473.3454 | 449.2577 | 336.7074
1170.2542 | 526.6802 | 473.3643 | 449.3109 | 337.0399
1171.2542 | 526.6516 | 473.4283 | 449.5972 | 337.3074
1172.2542 | 526.6076 | 473.5174 | 449.7934 | 337.5797
1173.2542 | 526.6066 | 473.5907 | 449.6882 | 337.8461
1174.2542 | 526.5404 | 473.6562 | 449.9964 | 338.0894
1175.2542 | 526.5225 | 473.6735 | 450.1383 | 338.3989
1176.2542 | 526.6038 | 473.7389 | 449.8978 | 338.6872
1177.2542 | 526.6515 | 473.7843 | 450.2765 | 338.9706
1178.2542 | 526.6542 | 473.815 | 450.2515 | 339.2895
1179.2542 | 526.6187 | 473.8902 | 450.3114 | 339.6363
1180.2542 | 526.5931 | 473.9871 | 450.0145 | 340.0168
1181.2542 | 526.6594 | 474.0246 | 450.2514 | 340.2968
1182.2542 | 526.6732 | 474.1204 | 450.0872 | 340.6588
1183.2542 | 526.7198 | 474.2004 | 450.2391 | 341.0348
1184.2542 | 526.7845 | 474.2598 | 450.13 | 341.3224
1185.2542 | 526.6943 | 474.3134 | 450.4303 | 341.619
1186.2542 | 526.6699 | 474.3769 | 450.3609 | 341.9673
1187.2542 | 526.6713 | 474.438 | 450.448 | 342.2004
1188.2542 | 526.722 | 474.5115 | 450.8231 | 342.4829
1189.2542 | 526.753 | 474.5952 | 450.8571 | 342.7811
1190.2542 | 526.8602 | 474.6114 | 450.8782 | 343.0646
1191.2542 | 526.834 | 474.639 | 450.7576 | 343.3497
1192.2542 | 526.9289 | 474.6922 | 450.5615 | 343.6386
1193.2542 | 527.0703 | 474.7674 | 450.9566 | 343.9547
1194.2542 | 527.123 | 474.8743 | 450.8683 | 344.2275
1195.2542 | 527.175 | 474.9463 | 450.8878 | 344.4967
1196.2542 | 527.2128 | 474.9946 | 451.1066 | 344.8003
1197.2542 | 527.2158 | 475.0551 | 451.4062 | 345.0993
1198.2542 | 527.1476 | 475.124 | 451.219 | 345.3846
1199.2542 | 527.0822 | 475.1583 | 451.228 | 345.6479
1200.2542 | 527.1181 | 475.2265 | 451.0053 | 345.918
1201.2542 | 527.0323 | 475.191 | 451.292 | 346.1555
1202.2542 | 526.9031 | 475.2625 | 451.757 | 346.3983
1203.2542 | 526.7822 | 475.3304 | 451.8087 | 346.6979
1204.2542 | 526.7499 | 475.3822 | 451.4728 | 346.9509
1205.2542 | 526.7064 | 475.4355 | 451.8434 | 347.2052
1206.2542 | 526.596 | 475.4967 | 451.82 | 347.4853
1207.2542 | 526.6451 | 475.5736 | 451.3874 | 347.7874
1208.2542 | 526.7599 | 475.64 | 451.6518 | 348.0622
1209.2542 | 526.8276 | 475.7275 | 451.8265 | 348.3042
1210.2542 | 526.7377 | 475.7674 | 451.9075 | 348.5596
1211.2542 | 526.6894 | 475.8113 | 452.0952 | 348.8406
1212.2542 | 526.6583 | 475.8691 | 452.0587 | 349.1125
1213.2542 | 526.5975 | 475.8479 | 452.3484 | 349.441
1214.2542 | 526.5718 | 475.9321 | 452.6355 | 349.6744
1215.2542 | 526.5608 | 476.0308 | 452.8132 | 349.9527
1216.2542 | 526.5142 | 476.0949 | 452.4276 | 350.2354
1217.2542 | 526.4779 | 476.1407 | 452.1868 | 350.5113
1218.2542 | 526.504 | 476.1985 | 452.4149 | 350.7821
1219.2542 | 526.5398 | 476.2524 | 452.2142 | 351.0806
1220.2542 | 526.5128 | 476.3368 | 452.6523 | 351.3519
1221.2542 | 526.4914 | 476.3842 | 452.9669 | 351.6267
1222.2542 | 526.4633 | 476.3855 | 453.0118 | 351.9031
1223.2542 | 526.4514 | 476.4645 | 453.2792 | 352.1726
1224.2542 | 526.4398 | 476.5556 | 453.2509 | 352.4562
1225.2542 | 526.4147 | 476.5927 | 453.2711 | 352.7298
1226.2542 | 526.3584 | 476.637 | 453.6244 | 353.0054
1227.2542 | 526.3962 | 476.6861 | 453.3114 | 353.2851
1228.2542 | 526.4354 | 476.681 | 453.3752 | 353.5618
1229.2542 | 526.4985 | 476.7586 | 453.2894 | 353.8385
1230.2542 | 526.6174 | 476.821 | 453.5289 | 354.1463
1231.2542 | 526.7594 | 476.9064 | 453.7186 | 354.4511
1232.2542 | 526.8541 | 476.9739 | 453.4468 | 354.7648
1233.2542 | 526.765 | 477.0057 | 453.3439 | 355.4176
1234.2542 | 526.7541 | 477.0644 | 453.4293 | 355.6616
1235.2542 | 526.7652 | 477.14 | 453.91 | 355.9033
1236.2542 | 526.814 | 477.1845 | 454.0111 | 356.1475
1237.2542 | 526.8843 | 477.2605 | 454.0296 | 356.3427
1238.2542 | 526.9489 | 477.2991 | 453.6565 | 356.5173
1239.2542 | 526.9169 | 477.3765 | 453.3133 | 356.7023
1240.2542 | 526.9496 | 477.3972 | 453.2262 | 356.956
1241.2542 | 526.8282 | 477.4825 | 453.4422 | 357.1809
1242.2542 | 526.9108 | 477.5141 | 453.581 | 357.4163
1243.2542 | 526.8936 | 477.5515 | 453.4766 | 357.6385
1244.2542 | 526.9338 | 477.6144 | 453.8418 | 357.8813
1245.2542 | 527.0538 | 477.6304 | 454.0536 | 358.1303
1246.2542 | 527.1342 | 477.7141 | 454.2164 | 358.3873
1247.2542 | 527.1388 | 477.7591 | 454.3366 | 358.6125
1248.2542 | 527.1059 | 477.809 | 454.5687 | 358.8
1249.2542 | 527.0964 | 477.8798 | 454.4525 | 359.0991
1250.2542 | 527.0094 | 477.9052 | 454.7682 | 359.2728
1251.2542 | 526.9007 | 477.9331 | 454.971 | 359.5103
1252.2542 | 526.8529 | 478.0312 | 454.78 | 359.7558
1253.2542 | 526.9168 | 478.0852 | 454.6678 | 359.9776
1254.2542 | 526.8609 | 478.1378 | 454.8502 | 360.2087
1255.2542 | 526.7633 | 478.2051 | 454.6272 | 360.4436
1256.2542 | 526.7179 | 478.2712 | 454.6657 | 360.6788
1257.2542 | 526.6776 | 478.3248 | 454.8899 | 360.9265
1258.2542 | 526.7206 | 478.3419 | 455.1532 | 361.154
1259.2542 | 526.7052 | 478.3988 | 455.1421 | 361.3914
1260.2542 | 526.7129 | 478.4505 | 455.2274 | 361.643
1261.2542 | 526.7606 | 478.4599 | 455.0812 | 361.8923
1262.2542 | 526.7583 | 478.511 | 455.2745 | 362.1432
1263.2542 | 526.7782 | 478.5851 | 455.2034 | 362.38
1264.2542 | 526.8193 | 478.6056 | 455.3645 | 362.629
1265.2542 | 526.8967 | 478.6629 | 455.1543 | 362.8686
1266.2542 | 526.8631 | 478.7189 | 455.2231 | 363.1068
1267.2542 | 526.8457 | 478.7855 | 455.2823 | 363.3206
1268.2542 | 526.7952 | 478.824 | 455.1065 | 363.568
1269.2542 | 526.8518 | 478.8712 | 455.411 | 363.8166
1270.2542 | 526.7728 | 478.9424 | 455.6578 | 364.0664
1271.2542 | 526.7569 | 478.9673 | 455.8902 | 364.3249
1272.2542 | 526.7193 | 479.0245 | 455.7332 | 364.5678
1273.2542 | 526.7672 | 479.0436 | 455.9725 | 364.8384
1274.2542 | 526.8959 | 479.1124 | 456.0699 | 365.1016
1275.2542 | 526.9614 | 479.1702 | 456.1417 | 365.3501
1276.2542 | 527.0181 | 479.1819 | 455.8244 | 365.6131
1277.2542 | 527.0945 | 479.2701 | 455.8832 | 365.8673
1278.2542 | 527.1539 | 479.3337 | 456.0304 | 366.1279
1279.2542 | 527.2871 | 479.3863 | 456.2532 | 366.4081
1280.2542 | 527.3878 | 479.4305 | 456.2354 | 366.6688
1281.2542 | 527.4604 | 479.4463 | 455.9753 | 366.9377
1282.2542 | 527.5773 | 479.5211 | 456.3519 | 367.192
1283.2542 | 527.6466 | 479.5561 | 456.1388 | 367.4212
1284.2542 | 527.5901 | 479.595 | 456.191 | 367.6793
1285.2542 | 527.4927 | 479.648 | 456.5423 | 367.9402
1286.2542 | 527.4983 | 479.7114 | 456.2232 | 368.2147
1287.2542 | 527.4788 | 479.6939 | 456.2773 | 368.4629
1288.2542 | 527.5585 | 479.7791 | 456.7524 | 368.7051
1289.2542 | 527.5922 | 479.844 | 456.7526 | 368.9567
1290.2542 | 527.6918 | 479.876 | 456.653 | 369.2097
1291.2542 | 527.6864 | 479.936 | 456.3284 | 369.4264
1292.2542 | 527.6458 | 479.9639 | 456.1533 | 369.656
1293.2542 | 527.6449 | 480.0319 | 456.3622 | 369.9114
1294.2542 | 527.5873 | 480.0816 | 456.591 | 370.1492
1295.2542 | 527.492 | 480.1231 | 457.0771 | 370.3678
1296.2542 | 527.4737 | 480.1605 | 457.0046 | 370.5771
1297.2542 | 527.3995 | 480.2235 | 457.3247 | 370.7597
1298.2542 | 527.2686 | 480.2774 | 457.2989 | 370.9344
1299.2542 | 527.3087 | 480.3397 | 457.3152 | 371.1238
1300.2542 | 527.3215 | 480.3437 | 457.0046 | 371.3373
1301.2542 | 527.2484 | 480.4131 | 457.456 | 371.5253
1302.2542 | 527.2038 | 480.4561 | 457.4005 | 371.72
1303.2542 | 527.2187 | 480.5199 | 457.2438 | 371.9237
1304.2542 | 527.1923 | 480.563 | 457.4142 | 372.1261
1305.2542 | 527.1904 | 480.6261 | 457.3785 | 372.3233
1306.2542 | 527.1919 | 480.6721 | 457.74 | 372.5049
1307.2542 | 527.2581 | 480.7159 | 457.4007 | 372.6992
1308.2542 | 527.3778 | 480.748 | 457.3572 | 372.8846
1309.2542 | 527.4226 | 480.7787 | 457.7858 | 373.0772
1310.2542 | 527.4591 | 480.8256 | 457.7133 | 373.2615
1311.2542 | 527.5016 | 480.8704 | 457.5679 | 373.437
1312.2542 | 527.5009 | 480.9085 | 458.0668 | 373.6213
1313.2542 | 527.5616 | 480.9572 | 458.1381 | 373.798
1314.2542 | 527.5558 | 481.0156 | 458.0014 | 373.9773
1315.2542 | 527.5923 | 481.0756 | 458.148 | 374.1608
1316.2542 | 527.7039 | 481.1229 | 458.1797 | 374.3313
1317.2542 | 527.7166 | 481.1283 | 457.8921 | 374.5017
1318.2542 | 527.7774 | 481.1412 | 457.9385 | 374.6867
1319.2542 | 527.7913 | 481.2267 | 458.3151 | 374.8753
1320.2542 | 527.8766 | 481.2759 | 458.2787 | 375.0384
1321.2542 | 527.8977 | 481.329 | 458.2524 | 375.2094
1322.2542 | 527.8291 | 481.3538 | 458.5787 | 375.4148
1323.2542 | 527.7819 | 481.3695 | 458.4123 | 375.6239
1324.2542 | 527.7537 | 481.4393 | 458.256 | 375.8285
1325.2542 | 527.6942 | 481.4315 | 458.3582 | 376.0184
1326.2542 | 527.6784 | 481.4918 | 458.679 | 376.174
1327.2542 | 527.6107 | 481.5693 | 458.3832 | 376.354
1328.2542 | 527.5227 | 481.5838 | 458.6854 | 376.5426
1329.2542 | 527.5017 | 481.6507 | 458.7927 | 376.7175
1330.2542 | 527.5173 | 481.6727 | 458.7727 | 376.8761
1331.2542 | 527.4929 | 481.7224 | 458.8478 | 377.0607
1332.2542 | 527.4643 | 481.7971 | 458.6077 | 377.2644
1333.2542 | 527.4536 | 481.7998 | 458.463 | 377.4282
1334.2542 | 527.4627 | 481.8578 | 458.6344 | 377.6088
1335.2542 | 527.3991 | 481.9031 | 458.577 | 377.7543
1336.2542 | 527.4299 | 481.9477 | 458.6823 | 377.92
1337.2542 | 527.4122 | 482.0269 | 458.3233 | 378.0974
1338.2542 | 527.4756 | 482.0165 | 458.9023 | 378.2647
1339.2542 | 527.4489 | 482.0437 | 458.715 | 378.4186
1340.2542 | 527.3458 | 482.1104 | 458.7526 | 378.5636
1341.2542 | 527.3958 | 482.1188 | 458.7789 | 378.7217
1342.2542 | 527.4151 | 482.1798 | 458.9392 | 378.8878
1343.2542 | 527.3585 | 482.2255 | 459.0567 | 379.0372
1344.2542 | 527.3745 | 482.2736 | 459.262 | 379.1871
1345.2542 | 527.3528 | 482.2608 | 459.3243 | 379.3246
1346.2542 | 527.3406 | 482.3244 | 459.3498 | 379.4464
1347.2542 | 527.3365 | 482.3426 | 459.1019 | 379.5664
1348.2542 | 527.3221 | 482.3022 | 458.9937 | 379.6963
1349.2542 | 527.3546 | 482.3619 | 459.0779 | 379.8391
1350.2542 | 527.3112 | 482.4235 | 459.4253 | 379.9993
1351.2542 | 527.302 | 482.4917 | 459.3294 | 380.1682
1352.2542 | 527.2552 | 482.5453 | 459.6965 | 380.3302
1353.2542 | 527.2387 | 482.6134 | 460.143 | 380.4627
1354.2542 | 527.202 | 482.6397 | 460.1306 | 380.6101
1355.2542 | 527.165 | 482.6598 | 460.2945 | 380.7439
1356.2542 | 527.1395 | 482.6672 | 460.3227 | 380.8827
1357.2542 | 527.2056 | 482.7296 | 460.0879 | 381.0241
1358.2542 | 527.2523 | 482.7836 | 460.1904 | 381.1616
1359.2542 | 527.2739 | 482.8395 | 460.3449 | 381.3264
1360.2542 | 527.3582 | 482.833 | 460.4248 | 381.4719
1361.2542 | 527.3938 | 482.826 | 460.2227 | 381.6149
1362.2542 | 527.3086 | 482.8126 | 460.0023 | 381.7713
1363.2542 | 527.3403 | 482.9235 | 460.3631 | 381.8944
1364.2542 | 527.3284 | 482.9946 | 460.3618 | 382.036
1365.2542 | 527.2908 | 483.0459 | 460.5564 | 382.1837
1366.2542 | 527.2134 | 483.0987 | 460.4082 | 382.334
1367.2542 | 527.171 | 483.1032 | 460.5208 | 382.4651
1368.2542 | 527.1325 | 483.1557 | 460.4428 | 382.6142
1369.2542 | 527.0801 | 483.1884 | 460.9062 | 382.7612
1370.2542 | 527.0858 | 483.2356 | 461.0861 | 382.9113
1371.2542 | 526.9596 | 483.2647 | 461.0935 | 383.0671
1372.2542 | 526.7874 | 483.3183 | 461.2046 | 383.2173
1373.2542 | 526.7068 | 483.3765 | 461.1542 | 383.3518
1374.2542 | 526.7043 | 483.406 | 461.3888 | 383.5177
1375.2542 | 526.7278 | 483.4536 | 461.5677 | 383.6701
1376.2542 | 526.7356 | 483.4688 | 461.6726 | 383.817
1377.2542 | 526.6511 | 483.5418 | 461.5076 | 383.9634
1378.2542 | 526.6512 | 483.5732 | 461.1006 | 384.1252
1379.2542 | 526.7059 | 483.5841 | 461.0354 | 384.2688
1380.2542 | 526.7588 | 483.6088 | 461.5363 | 384.421
1381.2542 | 526.7489 | 483.6627 | 461.5863 | 384.5695
1382.2542 | 526.8731 | 483.6863 | 461.5956 | 384.7253
1383.2542 | 526.8402 | 483.7246 | 461.973 | 384.875
1384.2542 | 526.8814 | 483.7677 | 461.7366 | 385.0329
1385.2542 | 526.9013 | 483.809 | 461.337 | 385.162
1386.2542 | 526.8916 | 483.8304 | 461.3555 | 385.3044
1387.2542 | 526.949 | 483.874 | 461.6798 | 385.447
1388.2542 | 527.0054 | 483.9268 | 461.8704 | 385.6031
1389.2542 | 527.0004 | 483.9661 | 461.8126 | 385.752
1390.2542 | 527.007 | 483.9948 | 461.5148 | 385.908
1391.2542 | 527.0206 | 484.0115 | 461.4864 | 386.0571
1392.2542 | 527.031 | 484.0498 | 461.5014 | 386.2055
1393.2542 | 527.0935 | 484.1081 | 461.9554 | 386.3594
1394.2542 | 527.0905 | 484.1648 | 461.8857 | 386.5045
1395.2542 | 527.0611 | 484.1709 | 461.9526 | 386.6599
1396.2542 | 527.019 | 484.2339 | 461.9423 | 386.7992
1397.2542 | 527.0237 | 484.2372 | 462.2725 | 386.9465
1398.2542 | 526.9778 | 484.2426 | 462.3688 | 387.1001
1399.2542 | 526.9684 | 484.3097 | 462.3138 | 387.2441
1400.2542 | 527.0099 | 484.3667 | 462.7119 | 387.3805
1401.2542 | 526.9729 | 484.3725 | 462.6531 | 387.5197
1402.2542 | 527.0208 | 484.3852 | 462.8553 | 387.6618
1403.2542 | 527.1022 | 484.401 | 462.6017 | 387.7987
1404.2542 | 527.1688 | 484.437 | 462.3947 | 387.9433
1405.2542 | 527.1664 | 484.5214 | 462.2418 | 388.0841
1406.2542 | 527.1515 | 484.5667 | 462.4136 | 388.2284
1407.2542 | 527.2079 | 484.6247 | 462.426 | 388.378
1408.2542 | 527.2303 | 484.6546 | 462.4263 | 388.5067
1409.2542 | 527.2826 | 484.7081 | 462.6029 | 388.6278
1410.2542 | 527.2554 | 484.7481 | 462.7196 | 388.7743
1411.2542 | 527.2665 | 484.7712 | 462.8004 | 388.9858
1412.2542 | 527.2904 | 484.7385 | 462.6623 | 389.1253
1413.2542 | 527.3943 | 484.7799 | 462.6907 | 389.2649
1414.2542 | 527.3822 | 484.8458 | 462.8047 | 389.4287
1415.2542 | 527.3476 | 484.8699 | 462.486 | 389.5628
1416.2542 | 527.3217 | 484.8641 | 462.7234 | 389.6962
1417.2542 | 527.3428 | 484.9261 | 462.9333 | 389.8549
1418.2542 | 527.3448 | 484.9629 | 463.2126 | 389.9964
1419.2542 | 527.3317 | 484.9449 | 462.996 | 390.1159
1420.2542 | 527.2617 | 485.0028 | 463.0711 | 390.2736
1421.2542 | 527.3011 | 485.0529 | 462.8038 | 390.411
1422.2542 | 527.3346 | 485.0958 | 462.88 | 390.5474
1423.2542 | 527.3491 | 485.1466 | 463.3105 | 390.6946
1424.2542 | 527.2807 | 485.1858 | 463.5927 | 390.8349
1425.2542 | 527.2447 | 485.2303 | 463.7838 | 390.9764
1426.2542 | 527.2377 | 485.2611 | 463.8066 | 391.1166
1427.2542 | 527.2308 | 485.3178 | 464.0312 | 391.277
1428.2542 | 527.193 | 485.3512 | 463.5923 | 391.4143
1429.2542 | 527.22 | 485.3401 | 463.776 | 391.5617
1430.2542 | 527.2256 | 485.3846 | 463.8574 | 391.7035
1431.2542 | 527.2842 | 485.4121 | 464.012 | 391.8553
1432.2542 | 527.2565 | 485.4563 | 463.9004 | 391.996
1433.2542 | 527.1874 | 485.4503 | 463.9795 | 392.1329
1434.2542 | 527.1012 | 485.5137 | 463.9783 | 392.2863
1435.2542 | 527.1073 | 485.522 | 464.2356 | 392.434
1436.2542 | 527.1097 | 485.5881 | 464.4607 | 392.5833
1437.2542 | 527.1607 | 485.6138 | 464.3488 | 392.7378
1438.2542 | 527.1881 | 485.6334 | 463.9932 | 392.8783
1439.2542 | 527.1822 | 485.6505 | 464.3552 | 393.0243
1440.2542 | 527.147 | 485.7145 | 464.0017 | 393.1697
1441.2542 | 527.193 | 485.7213 | 463.9141 | 393.3221
1442.2542 | 527.1721 | 485.7779 | 463.5694 | 393.4702
1443.2542 | 527.1574 | 485.7535 | 463.6453 | 393.6201
1444.2542 | 527.1777 | 485.8001 | 464.3447 | 393.7618
1445.2542 | 527.2186 | 485.8386 | 464.4186 | 393.9024
1446.2542 | 527.2621 | 485.8707 | 463.821 | 394.0502
1447.2542 | 527.2467 | 485.926 | 463.7989 | 394.1971
1448.2542 | 527.1872 | 485.9584 | 464.2799 | 394.3391
1449.2542 | 527.112 | 486.0071 | 464.074 | 394.4809
1450.2542 | 527.1279 | 486.0521 | 463.8791 | 394.6276
1451.2542 | 527.1422 | 486.0855 | 464.3834 | 394.7819
1452.2542 | 527.0414 | 486.099 | 464.7641 | 394.9334
1453.2542 | 526.991 | 486.1208 | 464.9285 | 395.0809
1454.2542 | 526.9469 | 486.1508 | 465.0583 | 395.229
1455.2542 | 526.9094 | 486.2043 | 465.0494 | 395.3721
1456.2542 | 526.8929 | 486.2303 | 464.555 | 395.5171
1457.2542 | 526.8625 | 486.2549 | 464.2619 | 395.6631
1458.2542 | 526.8523 | 486.2821 | 464.6786 | 395.813
1459.2542 | 526.9276 | 486.2961 | 464.6742 | 395.9592
1460.2542 | 527.0288 | 486.3331 | 464.8737 | 396.1015
1461.2542 | 527.0629 | 486.3549 | 464.7435 | 396.2379
1462.2542 | 527.0778 | 486.3834 | 464.8375 | 396.3857
1463.2542 | 527.0988 | 486.4206 | 464.6814 | 396.532
1464.2542 | 527.0404 | 486.4419 | 464.5829 | 396.6785
1465.2542 | 527.0043 | 486.4868 | 464.8647 | 396.8208
1466.2542 | 527.0205 | 486.4999 | 464.8082 | 396.9699
1467.2542 | 526.913 | 486.553 | 464.8769 | 397.1223
1468.2542 | 526.9724 | 486.5987 | 464.7477 | 397.273
1469.2542 | 527.045 | 486.5851 | 465.1164 | 397.4119
1470.2542 | 527.1174 | 486.6084 | 465.1914 | 397.5692
1471.2542 | 527.1122 | 486.6362 | 465.4529 | 397.7276
1472.2542 | 527.0783 | 486.7157 | 465.5438 | 397.8657
1473.2542 | 527.0224 | 486.732 | 465.6059 | 398.0157
1474.2542 | 526.9942 | 486.7716 | 465.0669 | 398.1718
1475.2542 | 526.9731 | 486.7614 | 465.1858 | 398.3121
1476.2542 | 526.9211 | 486.8272 | 465.5844 | 398.465
1477.2542 | 527.005 | 486.872 | 465.6724 | 398.6067
1478.2542 | 526.9893 | 486.8958 | 465.3468 | 398.7651
1479.2542 | 526.9726 | 486.9419 | 465.3184 | 398.9018
1480.2542 | 526.9413 | 486.9449 | 465.3682 | 399.0527
1481.2542 | 526.9583 | 486.9823 | 465.6025 | 399.2174
1482.2542 | 526.8871 | 486.9983 | 465.455 | 399.3625
1483.2542 | 526.9056 | 487.0304 | 465.6455 | 399.4957
1484.2542 | 526.8757 | 487.0453 | 465.9374 | 399.6513
1485.2542 | 526.8563 | 487.0907 | 465.3702 | 399.7983
1486.2542 | 526.8685 | 487.1204 | 465.6907 | 399.953
1487.2542 | 526.8218 | 487.184 | 466.0996 | 400.0997
1488.2542 | 526.8959 | 487.2282 | 466.1485 | 400.2533
1489.2542 | 526.941 | 487.2466 | 466.0683 | 400.4067
1490.2542 | 526.9536 | 487.2579 | 465.7769 | 400.5597
1491.2542 | 526.978 | 487.2824 | 466.1719 | 400.7029
1492.2542 | 527.0234 | 487.3115 | 465.8667 | 400.8499
1493.2542 | 527.0743 | 487.3471 | 465.8689 | 400.9929
1494.2542 | 527.0976 | 487.3878 | 465.6162 | 401.1396
1495.2542 | 527.1262 | 487.3891 | 465.7598 | 401.288
1496.2542 | 527.0907 | 487.4354 | 466.2206 | 401.4183
1497.2542 | 527.0966 | 487.4782 | 466.2454 | 401.5613
1498.2542 | 527.0648 | 487.4882 | 465.9969 | 401.7134
1499.2542 | 527.1448 | 487.5138 | 465.9882 | 401.8506
1500.2542 | 527.1681 | 487.5159 | 466.1639 | 401.9942
1501.2542 | 527.1224 | 487.5712 | 466.2102 | 402.1382
1502.2542 | 527.1688 | 487.5981 | 466.0656 | 402.273
1503.2542 | 527.173 | 487.6239 | 465.7481 | 402.41
1504.2542 | 527.1888 | 487.6543 | 465.9919 | 402.5459
1505.2542 | 527.1693 | 487.695 | 466.4853 | 402.682
1506.2542 | 527.1557 | 487.7304 | 466.8456 | 402.8177
1507.2542 | 527.1194 | 487.7868 | 466.8538 | 402.9603
1508.2542 | 527.1346 | 487.8057 | 466.7468 | 403.1073
1509.2542 | 527.2358 | 487.817 | 466.75 | 403.2359
1510.2542 | 527.2007 | 487.844 | 466.9973 | 403.3699
1511.2542 | 527.2298 | 487.8861 | 466.9342 | 403.5072
1512.2542 | 527.2816 | 487.9278 | 467.0567 | 403.644
1513.2542 | 527.3047 | 487.9577 | 467.2308 | 403.776
1514.2542 | 527.2808 | 487.9977 | 467.4136 | 403.9064
1515.2542 | 527.333 | 488.0397 | 467.3126 | 404.0422
1516.2542 | 527.4069 | 488.0606 | 467.3458 | 404.1773
1517.2542 | 527.4602 | 488.0842 | 467.3395 | 404.3025
1518.2542 | 527.506 | 488.1206 | 467.1152 | 404.4507
1519.2542 | 527.4804 | 488.0981 | 466.9545 | 404.5816
1520.2542 | 527.4326 | 488.1313 | 467.4239 | 404.718
1521.2542 | 527.4714 | 488.1819 | 467.6692 | 404.8514
1522.2542 | 527.4035 | 488.1949 | 467.334 | 404.9862
1523.2542 | 527.3627 | 488.2039 | 466.9153 | 405.1203
1524.2542 | 527.4022 | 488.2649 | 467.1632 | 405.2597
1525.2542 | 527.4394 | 488.2949 | 467.5392 | 405.394
1526.2542 | 527.4428 | 488.3356 | 467.5827 | 405.5341
1527.2542 | 527.4791 | 488.3849 | 467.626 | 405.6878
1528.2542 | 527.5084 | 488.4223 | 467.6071 | 405.8194
1529.2542 | 527.526 | 488.4571 | 467.2481 | 405.9624
1530.2542 | 527.5338 | 488.4945 | 467.3558 | 406.0953
1531.2542 | 527.5232 | 488.4916 | 467.5345 | 406.2342
1532.2542 | 527.527 | 488.5309 | 467.8045 | 406.3781
1533.2542 | 527.6272 | 488.5504 | 467.4537 | 406.5137
1534.2542 | 527.5886 | 488.5773 | 467.0516 | 406.6408
1535.2542 | 527.5617 | 488.605 | 467.2361 | 406.7883
1536.2542 | 527.5441 | 488.6349 | 467.5377 | 406.9309
1537.2542 | 527.519 | 488.6632 | 467.4192 | 407.0643
1538.2542 | 527.4108 | 488.6784 | 467.7887 | 407.209
1539.2542 | 527.3377 | 488.7273 | 467.8833 | 407.3528
1540.2542 | 527.3048 | 488.7496 | 467.4546 | 407.489
1541.2542 | 527.2904 | 488.7172 | 467.0882 | 407.6245
1542.2542 | 527.2204 | 488.7149 | 467.323 | 407.7642
1543.2542 | 527.0542 | 488.7704 | 467.3187 | 407.8914
1544.2542 | 527.039 | 488.8181 | 467.3386 | 408.0281
1545.2542 | 526.9864 | 488.823 | 467.0047 | 408.1655
1546.2542 | 526.8763 | 488.8124 | 466.7646 | 408.3135
1547.2542 | 526.7973 | 488.8726 | 466.9217 | 408.4556
1548.2542 | 526.7044 | 488.9041 | 466.8543 | 408.5938
1549.2542 | 526.687 | 488.9138 | 467.1012 | 408.7396
1550.2542 | 526.7145 | 488.9699 | 467.2218 | 408.8731
1551.2542 | 526.6958 | 489.0045 | 467.4724 | 409.0083
1552.2542 | 526.6805 | 489.032 | 467.4412 | 409.1455
1553.2542 | 526.5054 | 489.0434 | 467.6129 | 409.2731
1554.2542 | 526.4149 | 489.0726 | 467.584 | 409.4115
1555.2542 | 526.3767 | 489.0809 | 467.2259 | 409.5584
1556.2542 | 526.3906 | 489.1022 | 467.4127 | 409.6983
1557.2542 | 526.4731 | 489.1265 | 467.3568 | 409.8342
1558.2542 | 526.4982 | 488.9936 | 467.495 | 409.9674
1559.2542 | 526.5733 | 489.0013 | 467.5215 | 410.1214
1560.2542 | 526.6816 | 489.0936 | 467.5635 | 410.2488
1561.2542 | 526.6369 | 489.1651 | 467.8412 | 410.397
1562.2542 | 526.61 | 489.1951 | 467.9209 | 410.5362
1563.2542 | 526.6062 | 489.2649 | 467.4164 | 410.649
1564.2542 | 526.5755 | 489.3146 | 467.5344 | 410.7982
1565.2542 | 526.5932 | 489.2724 | 467.9761 | 410.9336
1566.2542 | 526.4996 | 489.3186 | 467.635 | 411.0658
1567.2542 | 526.5078 | 489.3515 | 467.8817 | 411.1955
1568.2542 | 526.5113 | 489.4001 | 468.2444 | 411.3258
1569.2542 | 526.5433 | 489.4235 | 467.9823 | 411.4711
1570.2542 | 526.5587 | 489.4481 | 467.9194 | 411.6096
1571.2542 | 526.5742 | 489.4737 | 467.8925 | 411.7491
1572.2542 | 526.5689 | 489.4535 | 467.7189 | 411.8832
1573.2542 | 526.5205 | 489.4992 | 468.1573 | 412.0059
1574.2542 | 526.5287 | 489.5003 | 468.138 | 412.145
1575.2542 | 526.617 | 489.5557 | 468.2427 | 412.2766
1576.2542 | 526.7048 | 489.5862 | 468.2644 | 412.4143
1577.2542 | 526.7177 | 489.6192 | 468.567 | 412.5428
1578.2542 | 526.7292 | 489.651 | 468.3514 | 412.6717
1579.2542 | 526.5134 | 489.6849 | 468.267 | 412.7987
1580.2542 | 526.4845 | 489.7128 | 468.4081 | 412.9347
1581.2542 | 526.5133 | 489.7124 | 468.6513 | 413.0643
1582.2542 | 526.5561 | 489.7646 | 468.4963 | 413.2118
1583.2542 | 526.5311 | 489.8062 | 468.4943 | 413.3459
1584.2542 | 526.5676 | 489.8174 | 468.6514 | 413.479
1585.2542 | 526.5408 | 489.8388 | 468.3327 | 413.6274
1586.2542 | 526.5178 | 489.8581 | 468.1252 | 413.7591
1587.2542 | 526.4194 | 489.8972 | 468.3152 | 413.9019
1588.2542 | 526.4112 | 489.9222 | 467.9842 | 414.0477
1589.2542 | 526.4745 | 489.9509 | 468.2685 | 414.1799
1590.2542 | 526.4805 | 489.9552 | 468.3556 | 414.3172
1591.2542 | 526.4052 | 489.9716 | 468.2849 | 414.4544
1592.2542 | 526.4869 | 490.0003 | 468.458 | 414.5853
1593.2542 | 526.6028 | 490.0223 | 468.8396 | 414.7144
1594.2542 | 526.6514 | 490.0514 | 469.0791 | 414.8392
1595.2542 | 526.6475 | 490.0927 | 468.9484 | 414.9826
1596.2542 | 526.6132 | 490.132 | 468.8994 | 415.1176
1597.2542 | 526.5516 | 490.1176 | 468.6714 | 415.242
1598.2542 | 526.5341 | 490.1417 | 468.7191 | 415.3748
1599.2542 | 526.4909 | 490.1776 | 469.0602 | 415.5108
1600.2542 | 526.3883 | 490.1698 | 468.6411 | 415.6416
1601.2542 | 526.3354 | 490.1769 | 468.8264 | 415.7718
1602.2542 | 526.2741 | 490.1857 | 468.831 | 415.9112
1603.2542 | 526.1846 | 490.202 | 469.0494 | 416.041
1604.2542 | 526.1896 | 490.223 | 468.8919 | 416.1732
1605.2542 | 526.1944 | 490.2428 | 468.7631 | 416.2988
1606.2542 | 526.2875 | 490.2744 | 468.4854 | 416.4226
1607.2542 | 526.4073 | 490.2836 | 468.9749 | 416.5635
1608.2542 | 526.4422 | 490.2646 | 468.8004 | 416.696
1609.2542 | 526.4296 | 490.2785 | 468.5566 | 416.8194
1610.2542 | 526.4162 | 490.3274 | 469.0414 | 416.9435
1611.2542 | 526.3971 | 490.3771 | 469.349 | 417.0688
1612.2542 | 526.3871 | 490.4074 | 468.998 | 417.2032
1613.2542 | 526.5084 | 490.4085 | 468.9455 | 417.3323
1614.2542 | 526.4573 | 490.4596 | 468.8211 | 417.4603
1615.2542 | 526.3985 | 490.4769 | 468.7664 | 417.5969
1616.2542 | 526.4988 | 490.4785 | 468.669 | 417.7347
1617.2542 | 526.5652 | 490.4969 | 469.1427 | 417.8722
1618.2542 | 526.5627 | 490.5441 | 468.8146 | 417.9921
1619.2542 | 526.5729 | 490.5468 | 468.8786 | 418.1199
1620.2542 | 526.6643 | 490.573 | 469.2268 | 418.2466
1621.2542 | 526.6961 | 490.5914 | 469.3861 | 418.371
1622.2542 | 526.7234 | 490.5916 | 469.2075 | 418.503
1623.2542 | 526.8194 | 490.5891 | 469.1 | 418.6386
1624.2542 | 526.8437 | 490.6399 | 469.4739 | 418.76
1625.2542 | 526.799 | 490.6565 | 469.3875 | 418.8783
1626.2542 | 526.8278 | 490.7069 | 469.0635 | 418.9835
1627.2542 | 526.9276 | 490.6919 | 468.8107 | 419.1216
1628.2542 | 526.9582 | 490.712 | 468.8515 | 419.2319
1629.2542 | 526.9386 | 490.749 | 469.221 | 419.3482
1630.2542 | 526.9297 | 490.7832 | 469.3049 | 419.477
1631.2542 | 526.889 | 490.7904 | 469.1226 | 419.5912
1632.2542 | 526.9085 | 490.7652 | 469.4644 | 419.5961
1633.2542 | 526.8634 | 490.7427 | 469.2874 | 419.6813
1634.2542 | 526.8704 | 490.7102 | 468.8178 | 419.7839
1635.2542 | 526.8387 | 490.5748 | 468.6156 | 419.8947
1636.2542 | 526.8669 | 490.5627 | 468.8341 | 420.0087
1637.2542 | 526.9294 | 490.6098 | 469.3728 | 420.1101
1638.2542 | 526.9917 | 490.6284 | 469.4794 | 420.2135
1639.2542 | 527.023 | 490.6509 | 469.7485 | 420.3276
1640.2542 | 527.0887 | 490.6551 | 469.9939 | 420.414
1641.2542 | 527.1262 | 490.6895 | 469.8907 | 420.5196
1642.2542 | 527.2243 | 490.7115 | 469.8993 | 420.6417
1643.2542 | 527.2714 | 490.7372 | 469.9412 | 420.7554
1644.2542 | 527.3185 | 490.6748 | 470.0956 | 420.8688
1645.2542 | 527.4372 | 490.71 | 470.2913 | 420.9844
1646.2542 | 527.4892 | 490.7513 | 470.2072 | 421.0982
1647.2542 | 527.5274 | 490.7773 | 470.2777 | 421.2347
1648.2542 | 527.542 | 490.8701 | 470.394 | 421.3424
1649.2542 | 527.5607 | 490.9214 | 470.4991 | 421.4153
1650.2542 | 527.6267 | 490.9746 | 470.247 | 421.5269
1651.2542 | 527.6556 | 490.9974 | 470.3181 | 421.6124
1652.2542 | 527.7603 | 490.9956 | 470.429 | 421.7455
1653.2542 | 527.807 | 491.0126 | 470.2968 | 421.8502
1654.2542 | 527.8364 | 491.0124 | 470.3336 | 421.9649
1655.2542 | 527.8125 | 491.0216 | 469.9604 | 422.1121
1656.2542 | 527.8511 | 490.95 | 470.0578 | 422.2204
1657.2542 | 527.8619 | 490.9514 | 470.1589 | 422.3609
1658.2542 | 527.7944 | 491.0602 | 470.341 | 422.4426
1659.2542 | 527.8516 | 491.0117 | 470.4429 | 422.5343
1660.2542 | 527.9067 | 491.0261 | 470.4857 | 422.6081
1661.2542 | 527.9713 | 491.0386 | 470.6659 | 422.6684
1662.2542 | 528.0335 | 491.0489 | 470.6284 | 422.7798
1663.2542 | 528.0802 | 491.037 | 470.7411 | 422.906
1664.2542 | 528.0943 | 491.054 | 470.8185 | 423.0142
1665.2542 | 528.0662 | 491.0594 | 470.9133 | 423.1039
1666.2542 | 528.0025 | 491.1445 | 471.0667 | 423.2283
1667.2542 | 527.9387 | 491.1852 | 470.824 | 423.3408
1668.2542 | 527.8829 | 491.1796 | 470.9078 | 423.4273
1669.2542 | 527.8467 | 491.2278 | 470.9124 | 423.4966
1670.2542 | 527.8311 | 491.2253 | 471.0905 | 423.6207
1671.2542 | 527.7555 | 491.2371 | 471.2909 | 423.7449
1672.2542 | 527.705 | 491.2776 | 471.3792 | 423.8094
1673.2542 | 527.6551 | 491.3558 | 471.254 | 423.877
1674.2542 | 527.6373 | 491.3671 | 471.1836 | 423.9315
1675.2542 | 527.5793 | 491.2665 | 470.9414 | 423.9948
1676.2542 | 527.48 | 491.2671 | 470.9815 | 424.3257
1677.2542 | 527.4952 | 491.2736 | 471.2219 | 424.4504
1678.2542 | 527.4912 | 491.3317 | 471.416 | 424.5798
1679.2542 | 527.4831 | 491.3649 | 471.2808 | 424.6779
1680.2542 | 527.5502 | 491.3255 | 471.1594 | 424.7727
1681.2542 | 527.571 | 491.3383 | 471.3378 | 424.8647
1682.2542 | 527.5932 | 491.3782 | 471.4167 | 424.9621
1683.2542 | 527.6006 | 491.3876 | 471.5146 | 425.0433
1684.2542 | 527.5722 | 491.4535 | 471.627 | 425.135
1685.2542 | 527.5251 | 491.4657 | 471.5491 | 425.2146
1686.2542 | 527.4651 | 491.4778 | 471.5927 | 425.3118
1687.2542 | 527.4953 | 491.4283 | 471.7272 | 425.5507
1688.2542 | 527.5549 | 491.4644 | 471.7406 | 425.6824
1689.2542 | 527.655 | 491.4369 | 471.4428 | 425.7799
1690.2542 | 527.6893 | 491.4262 | 471.6395 | 425.8794
1691.2542 | 527.657 | 491.5201 | 471.6566 | 425.9569
1692.2542 | 527.7722 | 491.5571 | 471.4397 | 426.0469
1693.2542 | 527.7997 | 491.4876 | 471.6829 | 426.1619
1694.2542 | 527.8051 | 491.5444 | 471.55 | 426.257
1695.2542 | 527.7552 | 491.5842 | 471.6342 | 426.363
1696.2542 | 527.7772 | 491.6268 | 471.7363 | 426.4433
1697.2542 | 527.8131 | 491.619 | 471.8622 | 426.5139
1698.2542 | 527.7719 | 491.6794 | 471.8167 | 426.5968
1699.2542 | 527.7723 | 491.6949 | 471.7413 | 426.6876
1700.2542 | 527.8047 | 491.6608 | 471.8009 | 426.8581
1701.2542 | 527.8375 | 491.734 | 471.601 | 426.898
1702.2542 | 527.8181 | 491.7499 | 471.7932 | 426.9447
1703.2542 | 527.7831 | 491.7638 | 471.4152 | 426.9834
1704.2542 | 527.7542 | 491.7825 | 471.6186 | 427.0523
1705.2542 | 527.7435 | 491.7872 | 471.5518 | 427.1399
1706.2542 | 527.7048 | 491.8178 | 471.3512 | 427.2006
1707.2542 | 527.6821 | 491.7951 | 471.3252 | 427.1424
1708.2542 | 527.6389 | 491.812 | 471.3936 | 427.1617
1709.2542 | 527.647 | 491.8295 | 471.7194 | 427.2217
1710.2542 | 527.55 | 491.9222 | 471.9924 | 427.3021
1711.2542 | 527.4705 | 491.9308 | 472.0014 | 427.377
1712.2542 | 527.4235 | 491.8745 | 471.7688 | 427.4344
1713.2542 | 527.4062 | 491.8489 | 471.4176 | 427.4978
1714.2542 | 527.3454 | 491.8257 | 471.3317 | 427.6356
1715.2542 | 527.2982 | 491.9106 | 471.7562 | 427.7508
1716.2542 | 527.2464 | 491.9127 | 471.8598 | 427.8578
1717.2542 | 527.2395 | 491.9365 | 471.9396 | 427.9472
1718.2542 | 527.2386 | 491.9587 | 471.7918 | 427.9778
1719.2542 | 527.2247 | 492.0075 | 472.057 | 428.0685
1720.2542 | 527.1912 | 492.0226 | 471.5278 | 428.44
1721.2542 | 527.1717 | 491.9911 | 471.8077 | 428.5142
1722.2542 | 527.1133 | 492.0475 | 472.0059 | 428.5335
1723.2542 | 527.0819 | 492.0596 | 472.1485 | 428.6716
1724.2542 | 527.0345 | 492.1094 | 471.7974 | 428.6953
1725.2542 | 526.9511 | 492.1091 | 471.5261 | 428.8107
1726.2542 | 526.8977 | 492.1448 | 471.7929 | 429.1332
1727.2542 | 526.8399 | 492.1743 | 471.9886 | 429.2287
1728.2542 | 526.7305 | 492.0823 | 471.7038 | 429.3317
1729.2542 | 526.6865 | 492.0714 | 471.9784 | 429.3782
1730.2542 | 526.6917 | 492.1208 | 472.1759 | 429.433
1731.2542 | 526.7673 | 492.1644 | 472.246 | 429.5076
1732.2542 | 526.7803 | 492.1378 | 472.2354 | 429.5669
1733.2542 | 526.7676 | 492.2155 | 472.3002 | 429.7604
1734.2542 | 526.8208 | 492.2158 | 472.2203 | 429.8395
1735.2542 | 526.8665 | 492.1919 | 471.7271 | 429.6758
1736.2542 | 526.9554 | 492.1434 | 471.4947 | 429.7516
1737.2542 | 527.0285 | 492.1409 | 471.7588 | 429.8073
1738.2542 | 527.0443 | 492.1997 | 471.8618 | 429.8554
1739.2542 | 527.0912 | 492.1799 | 472.2033 | 429.9055
1740.2542 | 527.0788 | 492.2882 | 472.3194 | 429.968
1741.2542 | 527.1073 | 492.2941 | 472.4923 | 430.0586
1742.2542 | 527.1389 | 492.2963 | 472.3073 | 430.1208
1743.2542 | 527.1798 | 492.3781 | 472.3672 | 430.1771
1744.2542 | 527.196 | 492.4139 | 472.5309 | 430.2407
1745.2542 | 527.2309 | 492.3913 | 472.4128 | 430.2788
1746.2542 | 527.2729 | 492.4043 | 472.5069 | 430.3368
1747.2542 | 527.2547 | 492.4068 | 472.5326 | 430.4325
1748.2542 | 527.24 | 492.4349 | 472.602 | 430.5352
1749.2542 | 527.2752 | 492.4383 | 472.446 | 430.6012
1750.2542 | 527.3025 | 492.4213 | 472.4427 | 430.6633
1751.2542 | 527.3216 | 492.468 | 472.6633 | 430.7943
1752.2542 | 527.3447 | 492.5398 | 472.7694 | 430.8547
1753.2542 | 527.3638 | 492.5843 | 472.7006 | 430.9169
1754.2542 | 527.3844 | 492.4952 | 472.4833 | 430.9888
1755.2542 | 527.4665 | 492.5063 | 472.7618 | 431.1019
1756.2542 | 527.4106 | 492.5612 | 472.5193 | 431.1843
1757.2542 | 527.3395 | 492.5617 | 472.7657 | 431.2235
1758.2542 | 527.3533 | 492.5623 | 472.7359 | 431.2245
1759.2542 | 527.2795 | 492.5554 | 472.7206 | 431.2433
1760.2542 | 527.2281 | 492.4761 | 472.7929 | 431.2845
1761.2542 | 527.2073 | 492.5515 | 472.5222 | 431.3372
1762.2542 | 527.2564 | 492.4672 | 472.4018 | 431.3887
1763.2542 | 527.2431 | 492.5391 | 472.3181 | 431.4641
1764.2542 | 527.19 | 492.583 | 472.0879 | 431.5706
1765.2542 | 527.1739 | 492.5633 | 472.0666 | 431.6475
1766.2542 | 527.162 | 492.6021 | 472.3314 | 431.7387
1767.2542 | 527.1285 | 492.6249 | 472.1699 | 431.7765
1768.2542 | 527.0879 | 492.6405 | 472.1051 | 431.7581
1769.2542 | 527.126 | 492.7006 | 472.2812 | 431.7791
1770.2542 | 527.0808 | 492.7037 | 472.078 | 431.8446
1771.2542 | 527.0684 | 492.7142 | 472.075 | 431.9064
1772.2542 | 527.0597 | 492.728 | 472.1399 | 431.9758
1773.2542 | 527.0646 | 492.7489 | 472.3981 | 432.0057
1774.2542 | 527.0258 | 492.6415 | 472.5796 | 432.0063
1775.2542 | 527.1318 | 492.5683 | 472.8379 | 432.0788
1776.2542 | 527.2425 | 492.653 | 472.9708 | 432.1042
1777.2542 | 527.2492 | 492.736 | 472.4053 | 432.1961
1778.2542 | 527.2661 | 492.7687 | 472.4226 | 432.2503
1779.2542 | 527.3 | 492.7544 | 472.4063 | 432.2706
1780.2542 | 527.3442 | 492.7519 | 472.7164 | 432.2517
1781.2542 | 527.3616 | 492.7942 | 472.8806 | 432.2833
1782.2542 | 527.3696 | 492.7978 | 473.0652 | 432.3707
1783.2542 | 527.3673 | 492.8776 | 473.1178 | 432.4163
1784.2542 | 527.2859 | 492.8921 | 473.1213 | 432.4005
1785.2542 | 527.2422 | 492.8811 | 473.1186 | 432.4489
1786.2542 | 527.2564 | 492.8468 | 473.1918 | 432.4938
1787.2542 | 527.2663 | 492.8983 | 473.2663 | 432.5637
1788.2542 | 527.3381 | 492.9491 | 473.2725 | 432.6003
1789.2542 | 527.3659 | 492.9516 | 473.0685 | 432.651
1790.2542 | 527.3816 | 492.9587 | 472.8762 | 432.5501
1791.2542 | 527.4408 | 492.926 | 473.0947 | 432.4762
1792.2542 | 527.4919 | 492.934 | 472.9107 | 432.5247
1793.2542 | 527.5068 | 492.9561 | 473.0564 | 432.6044
1794.2542 | 527.5052 | 492.9733 | 472.6243 | 432.5259
1795.2542 | 527.5154 | 492.9755 | 472.4341 | 432.5198
1796.2542 | 527.583 | 493.0028 | 472.8688 | 432.6727
1797.2542 | 527.5793 | 493.0334 | 473.1543 | 432.7293
1798.2542 | 527.5922 | 493.0635 | 473.0322 | 432.8063
1799.2542 | 527.6006 | 493.1202 | 473.1883 | 432.9112
1800.2542 | 527.6247 | 493.1126 | 473.2671 | 432.8598
1801.2542 | 527.5869 | 493.1609 | 473.3281 | 432.6702
1802.2542 | 527.5574 | 493.1671 | 473.5043 | 432.6385
1803.2542 | 527.6056 | 493.097 | 473.582 | 432.7529
1804.2542 | 527.6425 | 493.0732 | 473.0253 | 432.8695
1805.2542 | 527.7209 | 493.1175 | 472.9146 | 433.0047
1806.2542 | 527.7879 | 493.0951 | 473.1108 | 433.1009
1807.2542 | 527.8253 | 493.157 | 472.9623 | 433.1293
1808.2542 | 527.8019 | 493.1748 | 473.0531 | 433.1938
1809.2542 | 527.785 | 493.1231 | 472.851 | 433.3321
1810.2542 | 527.7411 | 493.1041 | 472.8927 | 433.4566
1811.2542 | 527.696 | 493.161 | 472.9827 | 433.5082
1812.2542 | 527.682 | 493.178 | 473.0458 | 433.5285
1813.2542 | 527.6388 | 493.255 | 473.1883 | 433.5309
1814.2542 | 527.5853 | 493.2671 | 473.2392 | 433.4596
1815.2542 | 527.5586 | 493.2875 | 473.1448 | 433.4581
1816.2542 | 527.5276 | 493.3082 | 472.8979 | 433.6208
1817.2542 | 527.4948 | 493.243 | 472.7139 | 433.6571
1818.2542 | 527.4428 | 493.2913 | 472.4878 | 433.7356
1819.2542 | 527.4427 | 493.3383 | 472.708 | 433.8879
1820.2542 | 527.4438 | 493.2413 | 472.594 | 434.0371
1821.2542 | 527.4632 | 493.153 | 473.014 | 434.1582
1822.2542 | 527.5717 | 493.1673 | 473.1105 | 434.169
1823.2542 | 527.5592 | 493.2789 | 473.2291 | 434.2749
1824.2542 | 527.5442 | 493.2989 | 473.1961 | 434.1825
1825.2542 | 527.5569 | 493.3839 | 473.2593 | 434.2245
1826.2542 | 527.5187 | 493.4093 | 473.1146 | 434.3012
1827.2542 | 527.4086 | 493.3456 | 472.9964 | 434.4896
1828.2542 | 527.1532 | 493.39 | 473.2277 | 434.6028
1829.2542 | 526.8127 | 493.366 | 473.4737 | 434.7466
1830.2542 | 526.3257 | 493.36 | 473.5798 | 434.9163