## Worksheet 1
METHOD FOR PREDICTING TEMPERATURE IN A ROOM FIRE WITH
NATURAL VENTILATION
The following calculations estimate the hot gas layer temperature in enclosure fire.
Parameters should be specified ONLY IN THE RED INPUT PARAMETER BOXES.
All subsequent values are calculated by the spreadsheet, and based on values specified in the
input parameters.
INPUT PARAMETERS
COMPARTMENT INFORMATION
| Compartment Width (wc) |  |  |  | 15 | feet | 4.572 | m
| Compartment Length (lc) |  |  |  | 15 | feet | 4.572 | m
| Compartment Height (hc) |  |  |  | 10 | feet | 3.048 | m
| Vent Width (wv) |  |  |  | 4 | feet | 1.2192 | m
| Vent Height (hv) |  |  |  | 6 | feet | 1.8288 | m
| Interior Lining Thickness (d) |  |  |  | 1 | feet | 0.3048 | m
AMBIENT CONDITIONS
| Ambient Air Temperature (T0) |  |  |  | 77 | °F | 25 | °C
[7 empty] | 298 | K
| Specific Heat of Air (cp) |  |  |  | 1 | kJ/kg-K
| Ambient air Density (r0) |  |  |  | 1.18 | kg/m3
THERMAL PROPERTIES OF ENCLOSING SURFACES
| Interior Lining Thermal Inertia (krc) |  |  |  | 2 | (kW/m2-°C)2-sec
| Interior Lining Thermal Conductivity (k) |  |  |  | 0.0014 | kW/m-K
| Interior Lining Specific Heat (cp) |  |  |  | 0.88 | kJ/kg-K
| Interior Lining Density (r) |  |  |  | 2000 | kg/m3
INTERIOR LINING TYPICAL CONSTRUCTION PROPERTIES for common materials:
| Matetial |  | k | r | cp | krc
|  |  | (kW/m-°C) | (kg/m3) | (kJ/kg-K) | (kW/m2-°C)2-sec
| Concrete |  | 1.0 x 10-3 | 2000 | 0.88 | 2.0
| Gypsum Board |  | 5.0 x 10-4 | 1440 | 0.84 | 0.60
| Steel |  | 5.0 x 10-3 | 1600 | 0.46 | 150
| Wood |  | 1.5 x 10-4 | 420 | 2.72 | 0.30
Reference Quintiere, James. Principles of Fire Behavior. (Page 187)
FIRE SPECIFICATIONS
| Fire Heat Release Rate (Q) |  |  |  | 500 | kW
| Time After Ignition (t) |  |  |  | 100 | sec
METHOD OF McCAFFREY, QUINTIERE, AND HARKLEROAD (MQH)
Reference SFPE Handbook of Fire Protection Engineering 2nd Edition (Page 3-139)
DTg = 6.85[Q2/(A0(hv)1/2) (AThk)]1/3
| Where | DTg = upper layer gas temperature rise above ambient (Tg-T0) (K)
Q = heat release rate of the fire (kW)
A0 = area of ventilation opening (m2)
hv = height of ventilation opening (m)
hk = heat trensfer coefficient (kW/m2-K)
AT = total area of the compartment enclosing surface boundaries (m2)
Area of Ventilation Opening Calculation
| A0 = | (wv)(hv)
| A0 = | 2.2297 | m2
Thermal Penetration Time Calculation
| tp = | (rcp/k)(d/2)2
| Where | r = interior construction density (kg/m3)
cp = interior construction heat capacity (kJ/Kg-K)
k = interior construction thermal conductivity (kW/m-K)
d = interior construction thickness (m)
| tp = | 29198.0983 | sec, which is over 8 hours, so the conduction will be transient for a
long time
Heat Transfer Coefficient Calculation
| hk = | (krc/t)1/2 | for t < tp
| Where | krc = interior construction thermal inertia (kW/m2-°C)2-sec
(a thermal property of material responsible for the rate of temperature rise)
t = time after ignition (sec)
| hk = | 0.14142 | kW/m2-°C
Area of Compartment Enclosing Surface Boundaries
| AT = | [2(wcxlc) + 2(hcxwc) + 2(hcxlc)] - A0
| AT = | 95.3185 | m2
Compartment Hot Gas Layer Temperature With Natural Ventilation
DTg = 6.85[Q2/(A0(hv)1/2) (AThk)]1/3
| DTg = | 125.5062 | K
| DTg = | Tg-T0
| Tg = | DTg+T0
| Tg= | 423.5062 | K
| Tg= | 150.5062 | °C | 302.9111 | °F | ANSWER
NOTE
The above calculations are based on principles developed in the Society of Fire
Protection Engineers (SFPE) Handbook of Fire Protection Engineering, 2nd Edition 1995.
Calculations are based on certain assumptions and has inherent limitations. The results
of such calculations may or may not have reasonable predictive capabilities for a
given situation, and should only be interpreted by an informed user.

## Temperature-FV
CHAPTER 2. PREDICTING HOT GAS LAYER TEMPERATURE
|  |  | IN A ROOM FIRE | [5 empty] | Version 1805.1
|  | WITH FORCED VENTILATION | [6 empty] | (English Units)
COMPARTMENT WITH THERMALLY THICK/THIN BOUNDARIES
The following calculations estimate the hot gas layer temperature and smoke layer height in enclosure fire.
Parameters in YELLOW CELLS are Entered by the User.
Parameters in GREEN CELLS are Automatically Selected from the DROP DOWN MENU for the Material Selected.
All subsequent output values are calculated by the spreadsheet and based on values specified in the input parameters. This spreadsheet is protected
and secure to avoid errors due to a wrong entry in a cell(s). The chapter in the NUREG should be read before an analysis is made.
Project / Inspection Title:
INPUT PARAMETERS
COMPARTMENT INFORMATION
| Compartment Width (wc) |  |  |  | 50 | ft | 15.24 | m
| Compartment Length (lc) |  |  |  | 40 | ft | 12.192 | m
| Compartment Height (hc) |  |  |  | 12 | ft | 3.6576 | m
| Interior Lining Thickness (d) |  |  |  | 1.5 | in | 0.0381 | m |  | STOP - d > 1 inch
AMBIENT CONDITIONS
| Ambient Air Temperature (Ta) |  |  |  | 77 | °F | 25 | °C
[7 empty] | 298 | K
| Specific Heat of Air (ca) |  |  |  | 1 | kJ/kg-K
| Ambient Air Density (ra) |  |  |  | 1.1846 | kg/m3
THERMAL PROPERTIES OF COMPARTMENT ENCLOSING SURFACES
| Interior Lining Thermal Inertia (krc) |  |  |  | 0.18 | (kW/m2-K)2-sec
| Interior Lining Thermal Conductivity (k) |  |  |  | 0.00017 | kW/m-K
| Interior Lining Specific Heat (cp) |  |  |  | 1.1 | kJ/kg-K
| Interior Lining Density (r) |  |  |  | 960 | kg/m3
Note: Air density will automatically correct with Ambient Air Temperature (Ta) Input
THERMAL PROPERTIES FOR COMMON INTERIOR LINING MATERIALS
| Material |  | krc | k | c | r | Select Material
|  |  | (kW/m2-K)2-sec | (kW/m-K) | (kJ/kg-K) | (kg/m3)
| Aluminum (pure) |  | 500 | 0.206 | 0.895 | 2710 | Scroll to desired material then
| Steel (0.5% Carbon) |  | 197 | 0.054 | 0.465 | 7850 | Click on selection
| Concrete |  | 2.9 | 0.0016 | 0.75 | 2400
| Brick |  | 1.7 | 0.0008 | 0.8 | 2600
| Glass, Plate |  | 1.6 | 0.00076 | 0.8 | 2710
| Brick/Concrete Block |  | 1.2 | 0.00073 | 0.84 | 1900
| Gypsum Board |  | 0.18 | 0.00017 | 1.1 | 960
| Plywood |  | 0.16 | 0.00012 | 2.5 | 540
| Fiber Insulation Board |  | 0.16 | 0.00053 | 1.25 | 240
| Chipboard |  | 0.15 | 0.00015 | 1.25 | 800
| Aerated Concrete |  | 0.12 | 0.00026 | 0.96 | 500
| Plasterboard |  | 0.12 | 0.00016 | 0.84 | 950
| Calcium Silicate Board |  | 0.098 | 0.00013 | 1.12 | 700
| Alumina Silicate Block |  | 0.036 | 0.00014 | 1 | 260
| Glass Fiber Insulation |  | 0.0018 | 3.7e-05 | 0.8 | 60
| Expanded Polystyrene |  | 0.001 | 3.4e-05 | 1.5 | 20
| User Specified Value |  | Enter Value | Enter Value | Enter Value | Enter Value
Reference: Klote, J., J. Milke, Principles of Smoke Management, 2002 Page 270.
COMPARTMENT MASS VENTILATION FLOW RATE
| Forced Ventilation Flow Rate (m) |  |  |  | 6000 | cfm | 2.8317 | m3/sec
[7 empty] | 3.3543 | kg/sec
FIRE SPECIFICATIONS
| Fire Heat Release Rate (Q) |  |  |  | 1500 | kW
Calculate
METHOD OF FOOTE, PAGNI, AND ALVARES (FPA)
Reference: SFPE Handbook of Fire Protection Engineering, 3rd Edition, 2002, Page 3-177.
DTg/Ta = 0.63(Q/(mcaTa))0.72(hkAT/(mca))-0.36
Where
| DTg = | Tg - Ta = upper layer gas temperature rise above ambient (K)
| Ta = | ambient air temperature (K)
| Q = | heat release rate of the fire (kW)
| m = | compartment mass ventilation flow rate (kg/sec)
| ca = | specific heat of air (kJ/kg-K)
| hk = | convective heat transfer coefficient (kW/m2-K)
| AT = | total area of the compartment enclosing surface boundaries (m2)
Thermal Penetration Time Calculation
|  | tp = | (rcp/k) (d/2)2
Where
|  | tp = | thermal penetration time (sec)
|  | r = | interior lining density (kg/m3)
|  | cp = | interior lining specific heat (kJ/kg-K)
|  | k = | interior lining thermal conductivity (kW/m-K)
|  | d = | interior lining thickness (m)
|  | tp = | 2254.2649 | sec
Heat Transfer Coefficient Calculation
|  | hk = | √(krc/t) | for t < tp | or (k/d) | for t > tp
Where
|  | hk = | heat transfer coefficient (kW/m2-K)
|  | krc = | interior construction thermal inertia (kW/m2-K)2-sec
(a thermal property of material responsible for the rate of temperature rise)
|  | t = | time after ignition (sec)
See table below for results
Area of Compartment Enclosing Surface Boundaries
|  | AT = | 2 (wc x lc) + 2 (hc x wc) + 2 (hc x lc)
Where
|  | AT = | total area of the compartment enclosing surface boundaries (m2)
|  | wc = | compartment width (m)
|  | lc = | compartment length (m)
|  | hc = | compartment height (m)
|  | AT = | 572.2827 | m2
Compartment Hot Gas Layer Temperature With Forced Ventilation
DTg/Ta = 0.63(Q/(mcpTa))0.72(hkAT/(mcp))-0.36
|  | DTg = | Tg - Ta
|  | Tg = | DTg + Ta
| Time After Ignition (t) |  | hk | DTg/Ta | DTg | Tg | Tg | Tg
| (min) | (sec) | (kW/m2-K) |  | (K) | (K) | (°C) | (°F)
| 0 | 0 | - | - | - | 298 | 25 | 77
| 1 | 60 | 0.054772 | 0.37744 | 112.4781 | 410.4781 | 137.4781 | 279.4606
| 2 | 120 | 0.03873 | 0.4276 | 127.4246 | 425.4246 | 152.4246 | 306.3643
| 3 | 180 | 0.031623 | 0.45997 | 137.0723 | 435.0723 | 162.0723 | 323.7302
| 4 | 240 | 0.027386 | 0.48442 | 144.3573 | 442.3573 | 169.3573 | 336.8431
| 5 | 300 | 0.024495 | 0.50427 | 150.2735 | 448.2735 | 175.2735 | 347.4924
| 10 | 600 | 0.017321 | 0.57128 | 170.2425 | 468.2425 | 195.2425 | 383.4365
| 15 | 900 | 0.014142 | 0.61454 | 183.1321 | 481.1321 | 208.1321 | 406.6377
| 20 | 1200 | 0.012247 | 0.6472 | 192.865 | 490.865 | 217.865 | 424.1569
| 25 | 1500 | 0.010954 | 0.67372 | 200.7692 | 498.7692 | 225.7692 | 438.3846
| 30 | 1800 | 0.01 | 0.6962 | 207.4674 | 505.4674 | 232.4674 | 450.4412
| 35 | 2100 | 0.0092582 | 0.71579 | 213.3046 | 511.3046 | 238.3046 | 460.9482
| 40 | 2400 | 0.0044619 | 0.9309 | 277.4094 | 575.4094 | 302.4094 | 576.3369
| 45 | 2700 | 0.0044619 | 0.9309 | 277.4094 | 575.4094 | 302.4094 | 576.3369
| 50 | 3000 | 0.0044619 | 0.9309 | 277.4094 | 575.4094 | 302.4094 | 576.3369
| 55 | 3300 | 0.0044619 | 0.9309 | 277.4094 | 575.4094 | 302.4094 | 576.3369
| 60 | 3600 | 0.0044619 | 0.9309 | 277.4094 | 575.4094 | 302.4094 | 576.3369
METHOD OF DEAL AND BEYLER
Reference: SFPE Handbook of Fire Protection Engineering, 3rd Edition, 2002, Page 3-178.
Thermal Penetration Time Calculation
|  |  | tp = | (rcp/k) (d/2)2
Where
tp = thermal penetration time (sec)
r = interior lining density (kg/m3)
cp = interior lining heat capacity (kJ/kg-K)
k = interior lining thermal conductivity (kW/m-K)
d = interior lining thickness (m)
|  |  | tp = | 2254.2649 | sec
Heat Transfer Coefficient Calculation
|  |  | hk = | 0.4 √(krc / t) | for t < tp | or 0.4(k/d) | for t > tp
Where
|  |  | hk = | heat transfer coefficient (kW/m2-K)
|  |  | krc = | interior construction thermal inertia (kW/m2-K)2-sec
(a thermal property of material responsible for the rate of temperature rise)
|  |  | d = | thickness of interior lining (m)
See table below for results
Area of Compartment Enclosing Surface Boundaries
|  |  | AT = | 2(w c x lc) + 2(h c x wc) + 2(hc x lc)
|  |  | AT = | 572.2827 | m2
Compartment Hot Gas Layer Temperature With Forced Ventilation
|  |  | DTg = | Q / (mca + hkAT)
Where
|  |  | DTg = | Tg - Ta = upper layer gas temperature rise above ambient (K)
|  |  | Ta = | ambient air temperature (K)
|  |  | Q = | heat release rate of the fire (kW)
|  |  | m = | compartment mass ventilation flow rate (kg/sec)
|  |  | ca = | specific heat of air (kJ/kg-K)
|  |  | hk = | convective heat transfer coefficient (kW/m2-K)
|  |  | AT = | total area of the compartment enclosing surface boundaries (m2)
| Time After Ignition (t) |  | hk | DTg | Tg | Tg | Tg
| (min) | (sec) | (kW/m2-K) | (K) | (K) | (°C) | (°F)
| 0 | 0 | - | - | 298 | 25 | 77
| 1 | 60 | 0.021909 | 94.3848 | 392.3848 | 119.3848 | 246.8926
| 2 | 120 | 0.015492 | 122.7488 | 420.7488 | 147.7488 | 297.9479
| 3 | 180 | 0.012649 | 141.6006 | 439.6006 | 166.6006 | 331.881
| 4 | 240 | 0.010954 | 155.8708 | 453.8708 | 180.8708 | 357.5674
| 5 | 300 | 0.009798 | 167.3824 | 465.3824 | 192.3824 | 378.2884
| 10 | 600 | 0.0069282 | 204.9404 | 502.9404 | 229.9404 | 445.8927
| 15 | 900 | 0.0056569 | 227.5613 | 525.5613 | 252.5613 | 486.6103
| 20 | 1200 | 0.004899 | 243.589 | 541.589 | 268.589 | 515.4603
| 25 | 1500 | 0.0043818 | 255.8885 | 553.8885 | 280.8885 | 537.5993
| 30 | 1800 | 0.004 | 265.7952 | 563.7952 | 290.7952 | 555.4314
| 35 | 2100 | 0.0037033 | 274.0409 | 572.0409 | 299.0409 | 570.2737
| 40 | 2400 | 0.0017848 | 342.8016 | 640.8016 | 367.8016 | 694.0429
| 45 | 2700 | 0.0017848 | 342.8016 | 640.8016 | 367.8016 | 694.0429
| 50 | 3000 | 0.0017848 | 342.8016 | 640.8016 | 367.8016 | 694.0429
| 55 | 3300 | 0.0017848 | 342.8016 | 640.8016 | 367.8016 | 694.0429
| 60 | 3600 | 0.0017848 | 342.8016 | 640.8016 | 367.8016 | 694.0429
Summary of Results
NOTE:
The above calculations are based on principles developed in the SFPE Handbook of Fire Protection Engineering, 3rd Edition, 2002. Calculations are based on certain assumptions and have inherent limitations. The results of such calculations may or may not have reasonable predictive capabilities for a given situation and should only be interpreted by an informed user. Although each calculation in the spreadsheet has been verified with the results of hand calculation, there is no absolute guarantee of the accuracy of these calculations. Any questions, comments, concerns and suggestions or to report an error(s) in the spreadsheets, please send an email to David.Stroup@nrc.gov or Naeem.Iqbal@nrc.gov.
Prepared by: |  |  |  | Date: |  | Organization:
Checked by: |  |  |  | Date: |  | Organization:
Additional Information:
Revision Log | Description of Revision | [6 empty] | Date
1805.0 | Original issue with final text. | [6 empty] | December 2004
1805.1 | Deleted extraneous variable in Cell C94. Under Deal & Beyler Method, added tp calculation in Cells starting B148, added hk formula for t > tp in Cell E158 and changed equation for results table for hk in Cells starting D184. Revised e-mail addresses, corrected editorial errors, revised print pagination and print layout. | [6 empty] | March 2011
Note on F30: This default value (1.00) is the most appropriate value for the majority of analyses. You may change this value for your specific application. If you change this value please ensure that it is appropriate.