## Wall_Flame_Height (4.9-1)
CHAPTER 4
|  |  | ESTIMATING WALL FIRE |  |  |  |  | Version 1805.1
|  |  | FLAME HEIGHT |  |  |  |  | (English Units)
The following calculations estimate the wall fire flame height.
Parameters in YELLOW CELLS are Entered by the User.
Parameters in GREEN CELLS are Automatically Selected from the DROP DOWN MENU for the Fuel Type Selected.
All subsequent output values are calculated by the spreadsheet and based on values specified in the input parameters. This spreadsheet is protected and
secure to avoid errors due to a wrong entry in a cell(s). The chapter in the NUREG should be read before an analysis is made.
Project / Inspection Title:
INPUT PARAMETERS
| Fuel Spill Volume (V) |  |  |  | 2 | gallons |  |  | 0.0075708 | m3
| Fuel Spill Area or Dike Area (Adike) |  |  |  | 9 | ft2 |  |  | 0.83613 | m2
| Mass Burning Rate of Fuel (m") |  |  |  | 0.039 | kg/m2-sec
| Effective Heat of Combustion of Fuel (DHc,eff) |  |  |  | 46000 | kJ/kg
| Empirical Constant (kb) |  |  |  | 0.7 | m-1
Calculate
THERMAL PROPERTIES FOR
BURNING RATE DATA FOR LIQUID HYDROCARBON FUELS
Fuel |  | Mass Burning Rate |  | Heat of Combustion |  | Empirical Constant |  | Select Fuel Type
|  | m" (kg/m2-sec) |  | DHc,eff (kJ/kg) |  | kb (m-1)
Acetone |  | 0.041 |  | 25800 |  | 1.9 |  | Scroll to desired fuel type then
Benzene |  | 0.085 |  | 40100 |  | 2.7 |  | Click on selection
Benzene |  | 0.048 |  | 44700 |  | 3.6
Butane |  | 0.078 |  | 45700 |  | 2.7
Crude Oil |  | 0.034 |  | 42600 |  | 2.8
Diesel |  | 0.045 |  | 44400 |  | 2.1
Diethy Ether |  | 0.085 |  | 34200 |  | 0.7
Dioxane |  | 0.018 |  | 26200 |  | 5.4
Ethanol |  | 0.015 |  | 26800 |  | 100
Fuel Oil, Heavy |  | 0.035 |  | 39700 |  | 1.7
Gasoline |  | 0.055 |  | 43700 |  | 2.1
Heptane |  | 0.101 |  | 44600 |  | 1.1
Hexane |  | 0.074 |  | 44700 |  | 1.9
JP-4 |  | 0.051 |  | 43500 |  | 3.6
JP-5 |  | 0.054 |  | 43000 |  | 1.6
Kerosene |  | 0.039 |  | 43200 |  | 3.5
Lube Oil |  | 0.039 |  | 46000 |  | 0.7
Methanol |  | 0.017 |  | 20000 |  | 100
Silicon Transformer Fluid (561) |  | 0.005 |  | 28100 |  | 100
Transformer Oil, Hydrocarbon |  | 0.039 |  | 46000 |  | 0.7
Xylene |  | 0.09 |  | 40800 |  | 1.4
User Specified Value |  | Enter Value |  | Enter Value |  | Enter Value
Reference: SFPE Handbook of Fire Protection Engineering, 3rd Edition, Page 3-26.
Heat Release Rate Calculation
Reference: SFPE Handbook of Fire Protection Engineering, 3rd Edition, 2002, Page 3-25.
Q = |  |  | m"DHc,eff (1 - e-kb D) Adike
Where,
Q = |  |  |  | pool fire heat release rate (kW)
m" = |  |  |  | mass burning rate of fuel per unit surface area (kg/m2-sec)
DHc,eff = |  |  |  | effective heat of combustion of fuel (kJ/kg)
Adike = |  |  |  | surface area of pool fire (area involved in vaporization) (m2)
kb = |  |  |  | empirical constant (m-1)
D = |  |  |  | diameter of pool fire (diameter involved in vaporization, circular pool is assumed) (m)
NOTE: Liquids with relatively high flash point, like transformer oil, require localized
heating to achieve ignition.
Pool Fire Diameter Calculation
Adike = |  |  |  | pD2/4
D = |  |  |  | √(4Adike/p)
Where,
Adike = |  |  |  | surface area of pool fire (m2)
D = |  |  |  | pool fire diameter (m)
D = |  |  |  | 1.0318 |  | m
Heat Release Rate Calculation
Q = |  |  | m"DHc,eff (1 - e-kb D) Adike
Q = |  |  | 771.5211 |  | kW |  | 731.2631 |  | Btu/sec
Heat Release Rate Per Unit Length of Fire Calculation
Q' = |  |  | Q/L
Where,
Q' = |  |  |  | heat release rate per unit length (kW/m)
Q = |  |  |  | fire heat release rate of the fire (kW)
L = |  |  |  | length of the fire source (m)
Fire Source Length Calculation
L x W = |  |  |  | Adike
L x W = |  |  |  | 0.83613 |  | m2
L = |  |  |  | 0.9144 |  | m
Heat Release Rate Per Unit Length of Fire Calculation
Q' = |  |  | Q/L
Q' = |  |  | 843.7458 |  | kW/m
ESTIMATING WALL FIRE FLAME HEIGHT
Reference: NFPA Fire Protection Handbook, 19th Edition, 2003, Page 3-134.
Hf(wall) = |  |  | 0.034 Q' 2/3
Where,
Hf(wall) = |  |  | wall fire flame height (m)
Q' = |  |  | rate of heat release per unit length of the fire (kW/m)
Hf(wall) = |  |  | 0.034 Q' 2/3
Answer | Hf(wall) = |  | 9.9603 |  | ft |  | 3.0359 |  | m
NOTE:
The above calculations are based on principles developed in the SFPE Handbook of Fire Protection Engineering, 3rd Edition, 2002, and NFPA Fire Protection Handbook, 19th Edition, 2003. Calculations are based on certain assumptions and have inherent limitations. The results of such calculations may or may not have reasonable predictive capabilities for a given situation and should only be interpreted by an informed user. Although each calculation in the spreadsheet has been verified with the results of hand calculation, there is no absolute guarantee of the accuracy of these calculations. Any questions, comments, concerns and suggestions or to report an error(s) in the spreadsheet, please send an email to David.Stroup@nrc.gov or Naeem.Iqbal@nrc.gov.
Prepared by: |  |  |  | Date: |  | Organization:
Checked by: |  |  |  | Date: |  | Organization:
Additional Information:
Revision Log | Description of Revision | [7 empty] | Date
1805.0 | Original issue with final text. | [7 empty] | December 2004
1805.1 | Revised e-mail addresses, corrected editorial errors, revised print pagination and print layout. | [7 empty] | March 2011

## Wall_Line_Flame_Height (4.9-2)
CHAPTER 4
|  |  | ESTIMATING LINE FIRE |  |  |  |  | Version 1805.1
|  |  | FLAME HEIGHT AGAINST THE WALL |  |  |  |  | (English Units)
The following calculations estimate the line fire flame height against the wall.
Parameters in YELLOW CELLS are Entered by the User.
Parameters in GREEN CELLS are Automatically Selected from the DROP DOWN MENU for the Fuel Type Selected.
All subsequent output values are calculated by the spreadsheet and based on values specified in the input parameters. This spreadsheet is protected and
secure to avoid errors due to a wrong entry in a cell(s). The chapter in the NUREG should be read before an analysis is made.
Project / Inspection Title:
INPUT PARAMETERS
| Fuel Spill Volume (V) |  |  |  | 15 | gallons |  |  | 0.056781 | m3
| Fuel Spill Area or Dike Area (Adike) |  |  |  | 30 | ft2 |  |  | 2.7871 | m2
| Mass Burning Rate of Fuel (m") |  |  |  | 0.045 | kg/m2-sec
| Effective Heat of Combustion of Fuel (DHc,eff) |  |  |  | 44400 | kJ/kg
| Empirical Constant (kb) |  |  |  | 2.1 | m-1
Calculate
THERMAL PROPERTIES FOR
BURNING RATE DATA FOR LIQUID HYDROCARBON FUELS
Fuel |  | Mass Burning Rate |  | Heat of Combustion |  | Empirical Constant |  | Select Fuel Type
|  | m" (kg/m2-sec) |  | DHc,eff (kJ/kg) |  | kb (m-1)
Acetone |  | 0.041 |  | 25800 |  | 1.9 |  | Scroll to desired fuel type then
Benzene |  | 0.085 |  | 40100 |  | 2.7 |  | Click on selection
Benzene |  | 0.048 |  | 44700 |  | 3.6
Butane |  | 0.078 |  | 45700 |  | 2.7
Crude Oil |  | 0.034 |  | 42600 |  | 2.8
Diesel |  | 0.045 |  | 44400 |  | 2.1
Diethy Ether |  | 0.085 |  | 34200 |  | 0.7
Dioxane |  | 0.018 |  | 26200 |  | 5.4
Ethanol |  | 0.015 |  | 26800 |  | 100
Fuel Oil, Heavy |  | 0.035 |  | 39700 |  | 1.7
Gasoline |  | 0.055 |  | 43700 |  | 2.1
Heptane |  | 0.101 |  | 44600 |  | 1.1
Hexane |  | 0.074 |  | 44700 |  | 1.9
JP-4 |  | 0.051 |  | 43500 |  | 3.6
JP-5 |  | 0.054 |  | 43000 |  | 1.6
Kerosene |  | 0.039 |  | 43200 |  | 3.5
Lube Oil |  | 0.039 |  | 46000 |  | 0.7
Methanol |  | 0.017 |  | 20000 |  | 100
Silicon Transformer Fluid (561) |  | 0.005 |  | 28100 |  | 100
Transformer Oil, Hydrocarbon |  | 0.039 |  | 46000 |  | 0.7
Xylene |  | 0.09 |  | 40800 |  | 1.4
User Specified Value |  | Enter Value |  | Enter Value |  | Enter Value
Reference: SFPE Handbook of Fire Protection Engineering, 3rd Edition, Page 3-26.
Heat Release Rate Calculation
Reference: SFPE Handbook of Fire Protection Engineering, 3rd Edition, 2002, Page 3-25.
Q = |  |  | m"DHc,eff (1 - e-kb D) Adike
Where,
Q = |  |  |  | pool fire heat release rate (kW)
m" = |  |  |  | mass burning rate of fuel per unit surface area (kg/m2-sec)
DHc,eff = |  |  |  | effective heat of combustion of fuel (kJ/kg)
Adike = |  |  |  | surface area of pool fire (area involved in vaporization) (m2)
kb = |  |  |  | empirical constant (m-1)
D = |  |  |  | diameter of pool fire (diameter involved in vaporization, circular pool is assumed) (m)
NOTE: Liquids with relatively high flash point, like transformer oil, require localized
heating to achieve ignition.
Pool Fire Diameter Calculation
Adike = |  |  |  | pD2/4
D = |  |  |  | √(4Adike/p)
Where,
Adike = |  |  |  | surface area of pool fire (m2)
D = |  |  |  | pool fire diameter (m)
D = |  |  |  | 1.8838 |  | m
Heat Release Rate Calculation
Q = |  |  | m"DHc,eff (1 - e-kb D) Adike
Q = |  |  | 5462.0216 |  | kW |  | 5177.0133 |  | Btu/sec
Heat Release Rate Per Unit Length of Fire Calculation
Q' = |  |  | Q/L
Where,
Q' = |  |  |  | heat release rate per unit length (kW/m)
Q = |  |  |  | fire heat release rate of the fire (kW)
L = |  |  |  | length of the fire source (m)
Fire Source Length Calculation
L x W = |  |  |  | Adike
L x W = |  |  |  | 2.7871 |  | m2
L = |  |  |  | 1.6695 |  | m
Heat Release Rate Per Unit Length of Fire Calculation
Q' = |  |  | Q/L
Q' = |  |  | 3271.7328 |  | kW/m
ESTIMATING LINE WALL FIRE FLAME HEIGHT
Reference: NFPA Fire Protection Handbook, 19th Edition, 2003, Page 3-134.
Hf(wall line) = |  |  | 0.017 Q' 2/3
Where,
Hf(wall line) = |  |  | wall fire flame height (m)
Q' = |  |  | rate of heat release per unit length of the fire (kW/m)
Hf(wall line) = |  |  | 0.017 Q' 2/3
Answer | Hf(wall line) = |  | 12.2919 |  | ft |  | 3.7466 |  | m
NOTE:
The above calculations are based on principles developed in the SFPE Handbook of Fire Protection Engineering, 3rd Edition, 2002, and NFPA Fire Protection Handbook, 19th Edition, 2003. Calculations are based on certain assumptions and have inherent limitations. The results of such calculations may or may not have reasonable predictive capabilities for a given situation and should only be interpreted by an informed user. Although each calculation in the spreadsheet has been verified with the results of hand calculation, there is no absolute guarantee of the accuracy of these calculations. Any questions, comments, concerns and suggestions, or to report an error(s) in the spreadsheet, please send an email to David.Stroup@nrc.gov or Naeem.Iqbal@nrc.gov.
Prepared by: |  |  |  | Date: |  | Organization:
Checked by: |  |  |  | Date: |  | Organization:
Additional Information:
Revision Log | Description of Revision | [7 empty] | Date
1805.0 | Original issue with final text. | [7 empty] | December 2004
1805.1 | Revised e-mail addresses, corrected editorial errors, revised print pagination and print layout. | [7 empty] | March 2011

## Corner_Flame_Height (4.9-3)
CHAPTER 4
|  |  | ESTIMATING CORNER FIRE |  |  |  |  | Version 1805.1
|  |  | FLAME HEIGHT |  |  |  |  | (English Units)
The following calculations estimate the corner fire flame height.
Parameters in YELLOW CELLS are Entered by the User.
Parameters in GREEN CELLS are Automatically Selected from the DROP DOWN MENU for the Fuel Type Selected.
All subsequent output values are calculated by the spreadsheet and based on values specified in the input parameters. This spreadsheet is protected and
secure to avoid errors due to a wrong entry in a cell(s). The chapter in the NUREG should be read before an analysis is made.
Project / Inspection Title:
INPUT PARAMETERS
| Fuel Spill Volume (V) |  |  |  | 5 | gallons |  |  | 0.018925 | m3
| Fuel Spill Area or Dike Area (Adike) |  |  |  | 10 | ft2 |  |  | 0.92903 | m2
| Mass Burning Rate of Fuel (m") |  |  |  | 0.005 | kg/m2-sec
| Effective Heat of Combustion of Fuel (DHc,eff) |  |  |  | 28100 | kJ/kg
| Empirical Constant (kb) |  |  |  | 100 | m-1
Calculate
THERMAL PROPERTIES FOR
BURNING RATE DATA FOR LIQUID HYDROCARBON FUELS
Fuel |  | Mass Burning Rate |  | Heat of Combustion |  | Empirical Constant |  | Select Fuel Type
|  | m" (kg/m2-sec) |  | DHc,eff (kJ/kg) |  | kb (m-1)
Acetone |  | 0.041 |  | 25800 |  | 1.9 |  | Scroll to desired fuel type then
Benzene |  | 0.085 |  | 40100 |  | 2.7 |  | Click on selection
Benzene |  | 0.048 |  | 44700 |  | 3.6
Butane |  | 0.078 |  | 45700 |  | 2.7
Crude Oil |  | 0.034 |  | 42600 |  | 2.8
Diesel |  | 0.045 |  | 44400 |  | 2.1
Diethy Ether |  | 0.085 |  | 34200 |  | 0.7
Dioxane |  | 0.018 |  | 26200 |  | 5.4
Ethanol |  | 0.015 |  | 26800 |  | 100
Fuel Oil, Heavy |  | 0.035 |  | 39700 |  | 1.7
Gasoline |  | 0.055 |  | 43700 |  | 2.1
Heptane |  | 0.101 |  | 44600 |  | 1.1
Hexane |  | 0.074 |  | 44700 |  | 1.9
JP-4 |  | 0.051 |  | 43500 |  | 3.6
JP-5 |  | 0.054 |  | 43000 |  | 1.6
Kerosene |  | 0.039 |  | 43200 |  | 3.5
Lube Oil |  | 0.039 |  | 46000 |  | 0.7
Methanol |  | 0.017 |  | 20000 |  | 100
Silicon Transformer Fluid (561) |  | 0.005 |  | 28100 |  | 100
Transformer Oil, Hydrocarbon |  | 0.039 |  | 46000 |  | 0.7
Xylene |  | 0.09 |  | 40800 |  | 1.4
User Specified Value |  | Enter Value |  | Enter Value |  | Enter Value
Reference: SFPE Handbook of Fire Protection Engineering, 3rd Edition, Page 3-26.
Heat Release Rate Calculation
Reference: SFPE Handbook of Fire Protection Engineering, 3rd Edition, 2002, Page 3-25.
Q = |  |  | m"DHc,eff (1 - e-kb D) Adike
Where,
Q = |  |  |  | pool fire heat release rate (kW)
m" = |  |  |  | mass burning rate of fuel per unit surface area (kg/m2-sec)
DHc,eff = |  |  |  | effective heat of combustion of fuel (kJ/kg)
Adike = |  |  |  | surface area of pool fire (area involved in vaporization) (m2)
kb = |  |  |  | empirical constant (m-1)
D = |  |  |  | diameter of pool fire (diameter involved in vaporization, circular pool is assumed) (m)
NOTE: Liquids with relatively high flash point, like transformer oil, require localized
heating to achieve ignition.
Pool Fire Diameter Calculation
Adike = |  |  |  | pD2/4
D = |  |  |  | √(4Adike/p)
Where,
Adike = |  |  |  | surface area of pool fire (m2)
D = |  |  |  | pool fire diameter (m)
D = |  |  |  | 1.0876 |  | m
Heat Release Rate Calculation
Q = |  |  | m"DHc,eff (1 - e-kb D) Adike
Q = |  |  | 130.5288 |  | kW |  | 123.7178 |  | Btu/sec
ESTIMATING CORNER FIRE FLAME HEIGHT
Reference: Hesemi and Tokunaga, "Modeling of Turbulent Diffusion Flames and Fire Plumes for the Analysis of Fire Growth," Proceeding of the
21th National Heat Transfer Conference, American Society of Mechanical Engineers (ASME), 1983.
Hf(corner) = |  |  | 0.075 Q3/5
Where,
Q = |  |  | heat release rate of the fire (kW)
Hf(corner) = |  |  | 0.075 Q3/5
Answer | Hf(corner) = |  | 4.5758 |  | ft |  | 1.3947 |  | m
NOTE:
The above calculations are based on principles developed in the SFPE Handbook of Fire Protection Engineering, 3rd Edition, 2002, and Hesemi and Tokunage, 1983. Calculations are based on certain assumptions and have inherent limitations. The results of such calculations may or may not have reasonable predictive capabilities for a given situation and should only be interpreted by an informed user. Although each calculation in the spreadsheet has been verified with the results of hand calculation, there is no absolute guarantee of the accuracy of these calculations. Any questions, comments, concerns and suggestions or to report an error(s) in the spreadsheet, please send an email to David.Stroup@nrc.gov or Naeem.Iqbal@nrc.gov.
Prepared by: |  |  |  | Date: |  | Organization:
Checked by: |  |  |  | Date: |  | Organization:
Additional Information:
Revision Log | Description of Revision | [7 empty] | Date
1805.0 | Original issue with final text. | [7 empty] | December 2004
1805.1 | Revised e-mail addresses, corrected editorial errors, revised print pagination and print layout. | [7 empty] | March 2011