## Point Source
CHAPTER 5
ESTIMATING RADIANT HEAT FLUX FROM FIRE
| TO A TARGET FUEL AT GROUND LEVEL | [7 empty] | Version 1805.1
| UNDER WIND-FREE CONDITIONS | [7 empty] | (SI Units)
POINT SOURCE RADIATION MODEL
The following calculations estimate the full-scale cable tray heat release rate.
Parameters in YELLOW CELLS are Entered by the User.
Parameters in GREEN CELLS are Automatically Selected from the DROP DOWN MENU for the Cable Type Selected.
All subsequent output values are calculated by the spreadsheet and based on values specified in the input parameters. This spreadsheet is protected
and secure to avoid errors due to a wrong entry in a cell(s). The chapter in the NUREG should be read before an analysis is made.
Project / Inspection Title:
INPUT PARAMETERS
| Mass Burning Rate of Fuel (m") |  |  |  | 0.101 | kg/m2-sec
| Effective Heat of Combustion of Fuel (DHc,eff) |  |  | FALSE | 44600 | kJ/kg
| Empirical Constant (kb) |  |  |  | 1.1 | m-1
| Heat Release Rate (Q) |  |  |  | 527713.1175 | kW
| Fuel Area or Dike Area (Adike) |  |  |  | 117.15 | m2 | 117.15 | m2
| Distance between Fire and Target (L) |  |  |  | 29.87 | m | 29.87 | m
| Radiative Fraction (cr) |  |  |  | 0.3
OPTIONAL CALCULATION FOR GIVEN HEAT RELEASE RATE
| Select "User Specified Value" from Fuel Type Menu and Enter Your HRR here → |  |  |  |  | kW
Calculate
THERMAL PROPERTIES DATA
BURNING RATE DATA FOR FUELS
| Fuel | Mass Burning Rate | Heat of Combustion |  | Empirical Constant | Select Fuel Type
|  | m" (kg/m2-sec) | DHc,eff (kJ/kg) |  | kb (m-1)
| Methanol | 0.017 | 20000 |  | 100 | Scroll to desired fuel type then
| Ethanol | 0.015 | 26800 |  | 100 | Click on selection
| Butane | 0.078 | 45700 |  | 2.7
| Benzene | 0.085 | 40100 |  | 2.7
| Hexane | 0.074 | 44700 |  | 1.9
| Heptane | 0.101 | 44600 |  | 1.1
| Xylene | 0.09 | 40800 |  | 1.4
| Acetone | 0.041 | 25800 |  | 1.9
| Dioxane | 0.018 | 26200 |  | 5.4
| Diethy Ether | 0.085 | 34200 |  | 0.7
| Benzine | 0.048 | 44700 |  | 3.6
| Gasoline | 0.055 | 43700 |  | 2.1
| Kerosine | 0.039 | 43200 |  | 3.5
| Diesel | 0.045 | 44400 |  | 2.1
| JP-4 | 0.051 | 43500 |  | 3.6
| JP-5 | 0.054 | 43000 |  | 1.6
| Transformer Oil, Hydrocarbon | 0.039 | 46000 |  | 0.7
| 561 Silicon Transformer Fluid | 0.005 | 28100 |  | 100
| Fuel Oil, Heavy | 0.035 | 39700 |  | 1.7
| Crude Oil | 0.0335 | 42600 |  | 2.8
| Lube Oil | 0.039 | 46000 |  | 0.7
| Douglas Fir Plywood | 0.01082 | 10900 |  | 100
| User Specified Value | Enter Value | Enter Value |  | Enter Value
Reference: SFPE Handbook of Fire Protection Engineering, 3rd Edition, 2002, Page 3-26.
ESTIMATING RADIATIVE HEAT FLUX TO A TARGET FUEL
Reference: SFPE Handbook of Fire Protection Engineering, 3rd Edition, 2002, Page 3-272.
POINT SOURCE RADIATION MODEL
| q" = | Q cr / 4 p R2
Where
| q" = | incident radiative heat flux on the target (kW/m2)
| Q = | pool fire heat release rate (kW)
| cr = | radiative fraction
| R = | distance from center of the pool fire to edge of the target (m)
Pool Fire Diameter Calculation
Adike = pD2/4
D = √(4Adike/p)
Where
|  |  | Adike = | surface area of pool fire (m2)
|  |  | D = | pool fire diamter (m)
|  |  | D = | 12.2131 | m
Heat Release Rate Calculation
Q = m"DHc,eff (1 - e-kb D) Af
Where
|  |  | Q = | pool fire heat release rate (kW)
|  |  | m" = | mass burning rate of fuel per unit surface area (kg/m2-sec)
|  |  | DHc = | effective heat of combustion of fuel (kJ/kg)
|  |  | Af = | surface area of pool fire (area involved in vaporization) (m2)
|  |  | kb = | empirical constant (m-1)
|  |  | D = | diameter of pool fire (diameter involved in vaporization, circular pool is assumed) (m)
|  |  | Q = | 527713.1175 | kW
Distance from Center of the Fire to Edge of the Target Calculation
R = L+D/2
Where
|  |  | R = | distance from center of the pool fire to edge of the target (m)
|  |  | L = | distance between pool fire and target (m)
|  |  | D = | pool fire diameter (m)
|  |  | R = | 35.9766 | m
RADIATIVE HEAT FLUX CALCULATION
q" = Q cr / 4 p R2
Answer | q" = | 9.7335 | kW/m2 | 0.85709 | Btu/ft2-sec
NOTE:
The above calculations are based on principles developed in the SFPE Handbook of Fire Protection Engineering, 3rd Edition, 2002. Calculations are based on certain assumptions and have inherent limitations. The results of such calculations may or may not have reasonable predictive capabilities for a given situation and should only be interpreted by an informed user. Although each calculation in the spreadsheet has been verified with the results of hand calculation, there is no absolute guarantee of the accuracy of these calculations. Any questions, comments, concerns and suggestions or to report an error(s) in the spreadsheets, please send an email to David.Stroup@nrc.gov or Naeem.Iqbal@nrc.gov.
Prepared by: |  |  |  | Date: |  | Organization:
Checked by: |  |  |  | Date: |  | Organization:
Additional Information:
Revision Log | Description of Revision |  |  |  | Date
1805.0 | Original issue with final text. |  |  |  | December 2004
1805.1 | Revised e-mail addresses, corrected editorial errors, revised print pagination and print layout. |  |  |  | March 2011
Note on F27: This default value (0.30) is the most appropriate value for the majority of analyses. You may change this value for your specific application. If you change this value please ensure that it is appropriate.

## Solid Flame 1
CHAPTER 5
ESTIMATING RADIANT HEAT FLUX FROM FIRE
| TO A TARGET FUEL AT GROUND LEVEL | [7 empty] | Version 1805.1
| UNDER WIND-FREE CONDITIONS | [7 empty] | (SI Units)
SOLID FLAME RADIATION MODEL
The following calculations estimate the full-scale cable tray heat release rate.
Parameters in YELLOW CELLS are Entered by the User.
Parameters in GREEN CELLS are Automatically Selected from the DROP DOWN MENU for the Cable Type Selected.
All subsequent output values are calculated by the spreadsheet and based on values specified in the input parameters. This spreadsheet is protected
and secure to avoid errors due to a wrong entry in a cell(s). The chapter in the NUREG should be read before an analysis is made.
Project / Inspection Title:
INPUT PARAMETERS
| Mass Burning Rate of Fuel (m") |  |  |  | 0.051 | kg/m2-sec
| Effective Heat of Combustion of Fuel (DHc,eff) |  |  | FALSE | 43500 | kJ/kg
| Empirical Constant (kb) |  |  |  | 3.6 | m-1
| Heat Release Rate (Q) |  |  |  | 1818.5159 | kW
| Fuel Area or Dike Area (Adike) |  |  |  | 0.84 | m2 | 0.84 | m2
| Distance between Fire and Target (L) |  |  |  | 3.048 | m | 3.048 | m
OPTIONAL CALCULATION FOR GIVEN HEAT RELEASE RATE
| Select "User Specified Value" from Fuel Type Menu and Enter Your HRR here → |  |  |  |  | kW
Calculate
THERMAL PROPERTIES DATA
BURNING RATE DATA FOR FUELS
| Fuel | Mass Burning Rate | Heat of Combustion |  | Empirical Constant | Select Fuel Type
|  | m" (kg/m2-sec) | DHc,eff (kJ/kg) |  | kb (m-1)
| Methanol | 0.017 | 20000 |  | 100 | Scroll to desired fuel type then
| Ethanol | 0.015 | 26800 |  | 100 | Click on selection
| Butane | 0.078 | 45700 |  | 2.7
| Benzene | 0.085 | 40100 |  | 2.7
| Hexane | 0.074 | 44700 |  | 1.9
| Heptane | 0.101 | 44600 |  | 1.1
| Xylene | 0.09 | 40800 |  | 1.4
| Acetone | 0.041 | 25800 |  | 1.9
| Dioxane | 0.018 | 26200 |  | 5.4
| Diethy Ether | 0.085 | 34200 |  | 0.7
| Benzine | 0.048 | 44700 |  | 3.6
| Gasoline | 0.055 | 43700 |  | 2.1
| Kerosine | 0.039 | 43200 |  | 3.5
| Diesel | 0.045 | 44400 |  | 2.1
| JP-4 | 0.051 | 43500 |  | 3.6
| JP-5 | 0.054 | 43000 |  | 1.6
| Transformer Oil, Hydrocarbon | 0.039 | 46000 |  | 0.7
| 561 Silicon Transformer Fluid | 0.005 | 28100 |  | 100
| Fuel Oil, Heavy | 0.035 | 39700 |  | 1.7
| Crude Oil | 0.0335 | 42600 |  | 2.8
| Lube Oil | 0.039 | 46000 |  | 0.7
| Douglas Fir Plywood | 0.01082 | 10900 |  | 100
| User Specified Value | Enter Value | Enter Value |  | Enter Value
Reference: SFPE Handbook of Fire Protection Engineering, 3rd Edition, 2002, Page 3-26.
ESTIMATING RADIATIVE HEAT FLUX TO A TARGET FUEL
Reference: SFPE Handbook of Fire Protection Engineering, 3rd Edition, 2002, Page 3-276.
SOLID FLAME RADIATION MODEL
q" = EF1->2
Where
| q" = | incident radiative heat flux on the target (kW/m2)
| E = | emissive power of the pool fire flame (kW/m2)
| F1->2 = | view factor between target and the flame
Pool Fire Diameter Calculation
Adike = pD2/4
D = √(4Adike/p)
Where
|  | Adike = | surface area of pool fire (m2)
|  | D = | pool fire diamter (m)
|  | D = | 1.0342 | m
Emissive Power Calculation
|  | E = | 58 (10-0.00823 D)
Where
|  | E = | emissive power of the pool fire flame (kW/m2)
|  | D = | diameter of the pool fire (m)
|  | E = | 56.8744 | kW/m2
View Factor Calculation
|  | F1->2,H = | (B-1/S)/p(B2-1)1/2 tan-1 ((B+1) (S-1)/(B-1)(S+1))1/2-(A-1/S)/(p(A2-1)1/2) tan-1 ((A+1)(S-1)/(A-1)(S+1))1/2
|  | F1->2,V = | 1/(pS) tan-1(h/(S2-1)1/2)-(h/pS) tan-1 ((S-1)/(S+1))1/2 + Ah/pS(A2-1)1/2 tan-1 ((A+1)(S-1)/(A-1)(S+1))1/2
|  | A = | (h2+S2+1)/2S
|  | B = | (1+S2)/2S
|  | S = | 2R/D
|  | h = | 2Hf/D
|  | F1->2,max = | √(F21->2,H + F21->2,V)
Where
|  | F1->2,H = | horizontal view factor
|  | F1->2,V = | vertical view factor
|  | F1->2,max = | maximum view factor
|  | R = | distance from center of the pool fire to edge of the target (m)
|  | Hf = | height of the pool fire flame (m)
|  | D = | pool fire diameter (m)
Distance from Center of the Pool Fire to Edge of the Target Calculation
R = L + D/2
Where
|  | R = | distance from center of the pool fire to edge of the target (m)
|  | L = | distance between pool fire and target (m)
|  | D = | pool fire diameter (m)
|  | R = L+D/2 = | 3.5651 | m
Heat Release Rate Calculation
Q = m"DHc,eff (1 - e-kb D) Adike
Where
|  | Q = | pool fire heat release rate (kW)
|  | m" = | mass burning rate of fuel per unit surface area (kg/m2-sec)
|  | DHc = | effective heat of combustion of fuel (kJ/kg)
|  | Adike = | surface area of pool fire (area involved in vaporization) (m2)
|  | kb = | empirical constant (m-1)
|  | D = | diameter of pool fire (diameter involved in vaporization, circular pool is assumed) (m)
|  | Q = | 1818.5159 | kW
Pool Fire Flame Height Calculation
Hf = 0.235 Q2/5-1.02 D
Where
|  | Hf = | flame height (m)
|  | Q = | heat release rate of fire (kW)
|  | D = | fire diameter (m)
|  | Hf = | 3.6762 | m
| S = 2R/D = | 6.8945
| h = 2Hf/D = | 7.1093
| A = (h2+S2+1)/2S = | 7.1852
| B = (1+S2)/2S = | 3.5198
|  |  |  | FH1 | FH2 | FH3 | FH4 | F1->2,H
| F1->2,H = | 0.026741 |  | 0.31831 | 0.85818 | 0.31496 | 0.7824 | 0.026741
| F1->2,V = | 0.062644 |  | FV1 | FV2 | FV3 | FV4 | F1->2,V
| F1->2, max = √(F21->2,H + F21->2,V) = | 0.068113 |  | 0.037215 | 0.23391 | 0.33146 | 0.7824 | 0.062644
RADIATIVE HEAT FLUX CALCULATION
q" = EF1->2
Answer | q" = | 3.8739 | kW/m2 | 0.34112 | Btu/ft2-sec
NOTE:
The above calculations are based on principles developed in the SFPE Handbook of Fire Protection Engineering, 3rd Edition, 2002. Calculations are based on certain assumptions and have inherent limitations. The results of such calculations may or may not have reasonable predictive capabilities for a given situation and should only be interpreted by an informed user. Although each calculation in the spreadsheet has been verified with the results of hand calculation, there is no absolute guarantee of the accuracy of these calculations. Any questions, comments, concerns and suggestions or to report an error(s) in the spreadsheets, please send an email to David.Stroup@nrc.gov or Naeem.Iqbal@nrc.gov.
Prepared by: |  |  |  | Date: |  | Organization:
Checked by: |  |  |  | Date: |  | Organization:
Additional Information:
Revision Log | Description of Revision |  |  |  |  | Date
1805.0 | Original issue with final text. |  |  |  |  | December 2004
1805.1 | Rervised e-mail addresses, corrected editorial errors, revised print pagination and print layout. |  |  |  |  | March 2011

## Solid Flame 2
CHAPTER 5
ESTIMATING RADIANT HEAT FLUX FROM FIRE
| TO A TARGET FUEL ABOVE GROUND LEVEL | [7 empty] | Version 1805.1
| UNDER WIND-FREE CONDITIONS | [7 empty] | (SI Units)
SOLID FLAME RADIATION MODEL
The following calculations estimate the full-scale cable tray heat release rate.
Parameters in YELLOW CELLS are Entered by the User.
Parameters in GREEN CELLS are Automatically Selected from the DROP DOWN MENU for the Cable Type Selected.
All subsequent output values are calculated by the spreadsheet and based on values specified in the input parameters. This spreadsheet is protected
and secure to avoid errors due to a wrong entry in a cell(s). The chapter in the NUREG should be read before an analysis is made.
Project / Inspection Title:
INPUT PARAMETERS
| Mass Burning Rate of Fuel (m") |  |  |  | 0.054 | kg/m2-sec
| Effective Heat of Combustion of Fuel (DHc,eff) |  |  | FALSE | 43000 | kJ/kg
| Empirical Constant (kb) |  |  |  | 1.6 | m-1
| Heat Release Rate (Q) |  |  |  | 1690.2625 | kW
| Fuel Area or Dike Area (Adike) |  |  |  | 0.89 | m2 | 0.89 | m2
| Distance between Fire and Target (L) |  |  |  | 3.048 | m | 3.048 | m
| Vertical Distance of Target from Ground (H1 = Hf1) |  |  |  | 2.4384 | m | 2.4384 | m
OPTIONAL CALCULATION FOR GIVEN HEAT RELEASE RATE
| Select "User Specified Value" from Fuel Type Menu and Enter Your HRR here → |  |  |  |  | kW
Calculate
THERMAL PROPERTIES DATA
BURNING RATE DATA FOR FUELS
| Fuel | Mass Burning Rate | Heat of Combustion |  | Empirical Constant | Select Fuel Type
|  | m" (kg/m2-sec) | DHc,eff (kJ/kg) |  | kb (m-1)
| Methanol | 0.017 | 20000 |  | 100 | Scroll to desired fuel type then
| Ethanol | 0.015 | 26800 |  | 100 | Click on selection
| Butane | 0.078 | 45700 |  | 2.7
| Benzene | 0.085 | 40100 |  | 2.7
| Hexane | 0.074 | 44700 |  | 1.9
| Heptane | 0.101 | 44600 |  | 1.1
| Xylene | 0.09 | 40800 |  | 1.4
| Acetone | 0.041 | 25800 |  | 1.9
| Dioxane | 0.018 | 26200 |  | 5.4
| Diethy Ether | 0.085 | 34200 |  | 0.7
| Benzine | 0.048 | 44700 |  | 3.6
| Gasoline | 0.055 | 43700 |  | 2.1
| Kerosine | 0.039 | 43200 |  | 3.5
| Diesel | 0.045 | 44400 |  | 2.1
| JP-4 | 0.051 | 43500 |  | 3.6
| JP-5 | 0.054 | 43000 |  | 1.6
| Transformer Oil, Hydrocarbon | 0.039 | 46000 |  | 0.7
| 561 Silicon Transformer Fluid | 0.005 | 28100 |  | 100
| Fuel Oil, Heavy | 0.035 | 39700 |  | 1.7
| Crude Oil | 0.0335 | 42600 |  | 2.8
| Lube Oil | 0.039 | 46000 |  | 0.7
| Douglas Fir Plywood | 0.01082 | 10900 |  | 100
| User Specified Value | Enter Value | Enter Value |  | Enter Value
Reference: SFPE Handbook of Fire Protection Engineering, 3rd Edition, 2002, Page 3-26.
ESTIMATING RADIATIVE HEAT FLUX TO A TARGET FUEL
Reference: SFPE Handbook of Fire Protection Engineering, 3rd Edition, 2002, Page 3-276.
SOLID FLAME RADIATION MODEL
q" = EF1->2
Where
| q" = | incident radiative heat flux on the target (kW/m2)
| E = | emissive power of the pool fire flame (kW/m2)
| F1->2 = | view factor between target and the flame
Pool Fire Diameter Calculation
Adike = pD2/4
D = √(4Adike/p)
Where
|  | Adike = | surface area of pool fire (m2)
|  | D = | pool fire diameter (m)
|  | D = | 1.0645 | m
Emissive Power Calculation
E = 58 (10-0.00823 D)
Where
|  | E = | emissive power of the pool fire flame (kW/m2)
|  | D = | diameter of the pool fire (m)
|  | E = | 56.8417 | (kW/m2)
View Factor Calculation
|  | F1->2,V1 = | 1/(pS)tan-1(h1/(S2-1)1/2)-(h1/pS)tan-1((S-1)/(S+1))1/2+A1h1/pS(A12-1)1/2tan-1((A1+1)(S-1)/(A1-1)(S+1))1/2
|  | F1->2,V2 = | 1/(pS)tan-1(h2/(S2-1)1/2)-(h2/pS)tan-1((S-1)/(S+1))1/2+A2h2/pS(A22-1)1/2tan-1((A2+1)(S-1)/(A2-1)(S+1))1/2
|  | A1 = | (h12+S2+1)/2S
|  | A2 = | (h22+S2+1)/2S
|  | B = | (1+S2)/2S
|  | S = | 2R/D
|  | h1 = | 2Hf1/D
|  | h2 = | 2Hf2/D
|  | F1->2,V= | F1->2,V1 + F1->2,V2
Where
|  | F1->2,V = | total vertical view factor
|  | R = | distance from center of the pool fire to edge of the target (m)
|  | Hf = | height of the pool fire flame (m)
|  | D = | pool fire diameter (m)
Distance from Center of the Pool Fire to Edge of the Target Calculation
R = L + D/2
Where
|  | R = | distance from center of the pool fire to edge of the target (m)
|  | L = | distance between pool fire and target (m)
|  | D = | pool fire diameter (m)
|  | R = L+D/2 = | 3.5803 | m
Heat Release Rate Calculation
Q = m"DHc,eff (1 - e-kb D) Adike
Where
|  | Q = | pool fire heat release rate (kW)
|  | m" = | mass burning rate of fuel per unit surface area (kg/m2-sec)
|  | DHc = | effective heat of combustion of fuel (kJ/kg)
|  | Adike = | surface area of pool fire (area involved in vaporization) (m2)
|  | kb = | empirical constant (m-1)
|  | D = | diameter of pool fire (diameter involved in vaporization, circular pool is assumed) (m)
|  | Q = | 1690.2625 | kW
Pool Fire Flame Height Calculation
Hf = 0.235 Q2/5-1.02 D
Where
|  | Hf = | flame height (m)
|  | Q = | heat release rate of fire (kW)
|  | D = | fire diameter (m)
|  | Hf = | 3.5088 | m
| S = 2R/D = |  | 6.7266
| h1 = 2Hf1/D = |  | 4.5813
| h2 = 2Hf2/D = | 2(Hf-Hf1)/D = | 2.0111
| A1 = (h12+S2+1)/2S = |  | 4.9977
| A2 = (h22+S2+1)/2S = |  | 3.7383
| B = (1+S2)/2S = |  | 3.4376
|  |  |  | FV1 | FV2 | FV3 | FV4 | F1->2,V1
| F1->2,V1 = | 0.054097 |  | 0.028541 | 0.1541 | 0.22127 | 0.81191 | 0.054097
| F1->2,V2 = | 0.029949 |  | FV1 | FV2 | FV3 | FV4 | F1->2,V2
| F1->2, V = F1->2,V1 + F1->2,V2 = | 0.084047 |  | 0.013894 | 0.067646 | 0.09877 | 0.84744 | 0.029949
RADIATIVE HEAT FLUX CALCULATION
q" = EF1->2
Answer | q" = | 4.7774 | kW/m2 | 0.42067 | Btu/ft2-sec
NOTE:
The above calculations are based on principles developed in the SFPE Handbook of Fire Protection Engineering, 3rd Edition, 2002. Calculations are based on certain assumptions and have inherent limitations. The results of such calculations may or may not have reasonable predictive capabilities for a given situation and should only be interpreted by an informed user. Although each calculation in the spreadsheet has been verified with the results of hand calculation, there is no absolute guarantee of the accuracy of these calculations. Any questions, comments, concerns and suggestions or to report an error(s) in the spreadsheets, please send an email to David.Stroup@nrc.gov or Naeem.Iqbal@nrc.gov.
Prepared by: |  |  |  | Date: |  | Organization:
Checked by: |  |  |  | Date: |  | Organization:
Additional Information:
Revision Log | Description of Revision |  |  |  |  | Date
1805.0 | Original issue with final text. |  |  |  |  | December 2004
1805.1 | Revised e-mail addresses, corrected editorial errors, revised print pagination and print layout. |  |  |  |  | March 2011