## Solid Flame 1
CHAPTER 5
ESTIMATING RADIANT HEAT FLUX FROM FIRE TO A TARGET FUEL
| AT GROUND LEVEL IN PRESCENCE OF WIND (TILTED FLAME) | [7 empty] | Version 1805.1
| SOLID FLAME RADIATION MODEL | [7 empty] | (SI Units)
The following calculations estimate the full-scale cable tray heat release rate.
Parameters in YELLOW CELLS are Entered by the User.
Parameters in GREEN CELLS are Automatically Selected from the DROP DOWN MENU for the Cable Type Selected.
All subsequent output values are calculated by the spreadsheet and based on values specified in the input parameters. This spreadsheet is protected
and secure to avoid errors due to a wrong entry in a cell(s). The chapter in the NUREG should be read before an analysis is made.
Project / Inspection Title:
INPUT PARAMETERS
| Mass Burning Rate of Fuel (m") |  |  |  | 0.017 | kg/m2-sec
| Effective Heat of Combustion of Fuel (DHc,eff) |  |  |  | 20000 | kJ/kg
| Empirical Constant (kb) |  |  |  | 100 | m-1
| Fuel Area or Dike Area (Adike) |  |  |  | 0.836 | m2 | 0.836 | m2
| Distance between Fire and Target (L) |  |  |  | 3.048 | m | 3.048 | m
| Wind Speed or Velocity (uw) |  |  |  | 3.56 | m/sec | 3.56 | m/sec
| Ambient Air Temperature (Ta) |  |  |  | 25 | °C | 25 | °C
[7 empty] | 298 | K
| Gravitational Acceleration (g) |  |  |  | 9.81 | m/sec2
| Ambient Air Density (ra) |  |  |  | 1.1846 | kg/m3
Calculate
Note: Air density will automatically correct with Ambient Air Temperature (Ta) Input
THERMAL PROPERTIES DATA
BURNING RATE DATA FOR FUELS
| Fuel | Mass Burning Rate | Heat of Combustion | Empirical Constant | Select Fuel Type
|  | m" (kg/m2-sec) | DHc,eff (kJ/kg) | kb (m-1)
| Methanol | 0.017 | 20000 | 100 | Scroll to desired fuel type then
| Ethanol | 0.015 | 26800 | 100 | Click on selection
| Butane | 0.078 | 45700 | 2.7
| Benzene | 0.085 | 40100 | 2.7
| Hexane | 0.074 | 44700 | 1.9
| Heptane | 0.101 | 44600 | 1.1
| Xylene | 0.09 | 40800 | 1.4
| Acetone | 0.041 | 25800 | 1.9
| Dioxane | 0.018 | 26200 | 5.4
| Diethy Ether | 0.085 | 34200 | 0.7
| Benzine | 0.048 | 44700 | 3.6
| Gasoline | 0.055 | 43700 | 2.1
| Kerosine | 0.039 | 43200 | 3.5
| Diesel | 0.045 | 44400 | 2.1
| JP-4 | 0.051 | 43500 | 3.6
| JP-5 | 0.054 | 43000 | 1.6
| Transformer Oil, Hydrocarbon | 0.039 | 46000 | 0.7
| 561 Silicon Transformer Fluid | 0.005 | 28100 | 100
| Fuel Oil, Heavy | 0.035 | 39700 | 1.7
| Crude Oil | 0.0335 | 42600 | 2.8
| Lube Oil | 0.039 | 46000 | 0.7
| Douglas Fir Plywood | 0.01082 | 10900 | 100
| User Specified Value | Enter Value | Enter Value | Enter Value
Reference: SFPE Handbook of Fire Protection Engineering, 3rd Edition, 2002, Page 3-26.
ESTIMATING RADIATIVE HEAT FLUX TO A TARGET FUEL IN PRESENCE OF WIND
Reference: SFPE Handbook of Fire Protection Engineering, 3rd Edition, 1995, Page 3-276.
SOLID FLAME RADIATION MODEL IN PRESENCE OF WIND
q" = EF1->2
Where
| q" = | incident radiative heat flux on the target (kW/m2)
| E = | emissive power of the pool fire flame (kW/m2)
| F1->2 = | view factor between target and the flame in presence of wind
Pool Fire Diameter Calculation
Adike = pD2/4
D = √(4 Adike/p)
Where
|  | Adike = | surface area of pool fire (m2)
|  | D = | pool fire diameter (m)
|  | D = | 1.0317 | m
Pool Fire Radius Calculation
r = D/2
Where
|  | r = | pool fire radius (m)
|  | D = | pool fire diameter (m)
|  | r = | 0.51586 | m
Flame Emissive Power Calculation
E = 58 (10-0.00823 D)
Where
|  | E = | emissive power of the pool fire flame (kW/m2)
|  | D = | diameter of the pool fire (m)
|  | E = | 56.877 | kW/m2
View Factor Calculation in Presence of Wind
|  | p F1->2,H = | tan-1(b+1/b-1)0.5-(a2 + (b + 1)2 - 2 (b + 1 +ab Sin q)/(AB)0.5 tan-1 (A/B)0.5((b - 1)/(b + 1))0.5 + Sinq/(C)0.5 (tan-1 ((ab - (b2 - 1)Sinq)/ ((b2 - 1) (C))0.5)+ tan-1 (( Sinq (b2-1))/(b2-1)0.5/ (C)0.5)
|  | p F1->2,V = | (a Cosq/(b - a Sinq)) (a2 + (b + 1)2 - 2b (1 + a Sinq))/ (AB)0.5 (tan-1 (A/B)0.5 ((b - 1)/(b + 1))0.5+ Cosq/(C)0.5((tan-1 (ab-(b2-1) Sinq)/((b2-1) (C))0.5+ tan-1 (b2-1) Sinq/((b2-1)0.5 (C)0.5)))-(aCosq)/(b-a Sinq)(tan-1(b-1/b + 1)0.5
a = Hf/r
b = R/r
A = a2 + (b +1)2 - 2a (b + 1) sinq
B = a2 + (b - 1)2 - 2a (b - 1) sinq
C = 1 + (b2 - 1) Cos2q
F1->2,max = √(F21->2,H + F21->2,V)
Where
|  | F1->2,H = | horizontal view factor
|  | F1->2,V = | vertical view factor
|  | F1->2,max = | maximum view factor
|  | R = | distance from center of the pool fire to edge of the target (m)
|  | Hf = | height of the pool fire flame (m)
|  | r = | pool fire radius (m)
|  | q = | flame tilt or angle of deflection (radians)
Distance from Center of the Pool Fire to Edge of the Target Calculation
R = L+r
Where
|  | R = | distance from center of the pool fire to edge of the target (m)
|  | L = | Distance between fire and target
|  | r = | pool fire radius (m)
|  | R= | 3.5639 | m
Heat Release Rate Calculation
Q = m"DHc,eff (1 - e-kb D) Adike
Where
|  | Q = | pool fire heat release rate (kW)
|  | m" = | mass burning rate of fuel per unit surface area (kg/m2-sec)
|  | DHc = | effective heat of combustion of fuel (kJ/kg)
|  | Adike = | surface area of pool fire (area involved in vaporization) (m2)
|  | kb = | empirical constant (m-1)
|  | D = | diameter of pool fire (diameter involved in vaporization, circular pool is assumed) (m)
|  | Q = | 284.24 | kW
Pool Fire Flame Height Calculation
Hf = 55 D (m"/ra (√g D)) 0.67 (u*)-0.21
Where
|  | Hf = | nondimensional wind velocity
|  | m" = | mass burning rate of fuel (kg/m2-sec)
|  | D = | pool fire diameter (m)
|  | ra = | ambient air density (kg/m3)
|  | g = | gravitational acceleration (m/sec2)
|  | u* = | nondimensional wind velocity
|  | Hf = | 1.0182 | m
Nondimensional Wind Velocity Calculation
u* = uw/(g m" D/ra)1/3
Where
|  | u* = | nondimensional wind velocity
|  | uw = | wind velocity (m/sec)
|  | g = | gravitational acceleration (m/sec2)
|  | m" = | mass burning rate of fuel (kg/m2-sec)
|  | D = | pool fire diameter (m)
|  | ra = | ambient air density (kg/m3)
|  | u* = | 6.7724
Flame Tilt or Angle of Deflection Calculation
|  | COS q = 1 | for u* ≤ 1
|  | COS q = 1 / √(u*) | for u* ≥ 1
Since u* ≥ 1
|  | q= | ACOS(1/(u*)^0.5) = | 1.1764 | Rad | 67.4021 | degree
|  |  |  | 1.1764 | Rad | 67.4021 | degree
|  |  |  | 0 | Rad | 0 | degree
|  | a = Hf/r = | 1.9738
|  | b = R/r = | 6.9086
|  | A = a2 + (b +1)2 - 2a (b + 1) sinq = | 37.6192
|  | B = a2 + (b - 1)2 - 2a (b - 1) sinq = | 17.2737
|  | C = 1 + (b2 - 1) Cos2q = | 7.8999
F1->2,H
0.0018117
[5 empty] | FH1 | FH2 | FH3 | FH4 | FH5 | FH6 | FV7 | F1->2,V
|  | F1->2,H = | 0.0018117 |  | 0.85803 | 0.99823 | 0.90591 | 0.32847 | -0.99359 | 1.1518 | 0.10628 | 0.01935
|  | F1->2,V = | 0.01935 |  | FV1 | FV2 | FV3 | FV4 | FV5 | FV6
|  | F1->2, max = √(F21->2,H + F21->2,V) = | 0.019435 |  | 0.14912 | 1.0767 | 0.90591 | 0.13672 | -0.99359 | 1.1518
RADIATIVE HEAT FLUX CALCULATION IN PRESCENCE OF WIND
q" = EF1->2
Answer | q" = | 1.1054 | kW/m2 | 0.097336 | FH1: Btu/ft2-sec
NOTE: | bar: FH1 to FH6
The above calculations are based on principles developed in the SFPE Handbook of Fire Protection Engineering, 3rd Edition, 2002. Calculations are based on certain assumptions and have inherent limitations. The results of such calculations may or may not have reasonable predictive capabilities for a given situation and should only be interpreted by an informed user. Although each calculation in the spreadsheet has been verified with the results of hand calculation, there is no absolute guarantee of the accuracy of these calculations. Any questions, comments, concerns and suggestions or to report an error(s) in the spreadsheets, please send an email to David.Stroup@nrc.gov or Naeem.Iqbal@nrc.gov. | bar: FH1 to FH6
Prepared by: |  |  |  | Date: | FH2: Organization:
Checked by: |  |  |  | Date: | FH2: Organization:
Additional Information:
Revision Log | Description of Revision |  |  |  | FH1: Date
1805.0 | Original issue with final text. |  |  |  | FH1: December 2004
1805.1 | Corrected typo in Cell C85. Corrected programming errors in Cells G156 and M158. Revised e-mail address, corrected editorial errors, revised print pagination and print layout. |  |  |  | FH1: March 2011
Note on F27: This default value (9.81) is the most appropriate value for the majority of analyses. You may change this value for your specific application. If you change this value please ensure that it is appropriate.

## Solid Flame 2
CHAPTER 5
ESTIMATING RADIANT HEAT FLUX FROM FIRE TO A TARGET FUEL
| ABOVE GROUND LEVEL IN PRESCENCE OF WIND (TILTED FLAME) | [7 empty] | Version 1805.1
| SOLID FLAME RADIATION MODEL | [7 empty] | (SI Units)
The following calculations estimate the full-scale cable tray heat release rate.
Parameters in YELLOW CELLS are Entered by the User.
Parameters in GREEN CELLS are Automatically Selected from the DROP DOWN MENU for the Cable Type Selected.
All subsequent output values are calculated by the spreadsheet and based on values specified in the input parameters. This spreadsheet is protected
and secure to avoid errors due to a wrong entry in a cell(s). The chapter in the NUREG should be read before an analysis is made.
Project / Inspection Title:
INPUT PARAMETERS
| Mass Burning Rate of Fuel (m") |  |  |  | 0.005 | kg/m2-sec
| Effective Heat of Combustion of Fuel (DHc,eff) |  |  |  | 28100 | kJ/kg
| Empirical Constant (kb) |  |  |  | 100 | m-1
| Fuel Area or Dike Area (Adike) |  |  |  | 1.86 | m2 | 1.86 | m2
| Distance between Fire and Target (L) |  |  |  | 9.144 | m | 9.144 | m
| Vertical Distance of Target from Ground Level (H1 = Hf1) |  |  |  | 3.048 | m | 3.048 | m
| Wind Speed or Velocity (uw) |  |  |  | 3.56 | m/sec | 3.56 | m/sec
| Ambient Air Temperature (Ta) |  |  |  | 25 | °C | 25 | °C
[7 empty] | 298 | K
| Gravitational Acceleration (g) |  |  |  | 9.81 | m/sec2
| Ambient Air Density (ra) |  |  |  | 1.1846 | kg/m3
Calculate
Note: Air density will automatically correct with Ambient Air Temperature (Ta) Input
THERMAL PROPERTIES DATA
BURNING RATE DATA FOR FUELS
| Fuel | Mass Burning Rate | Heat of Combustion | Empirical Constant | Select Fuel Type
|  | m" (kg/m2-sec) | DHc,eff (kJ/kg) | kb (m-1)
| Methanol | 0.017 | 20000 | 100 | Scroll to desired fuel type then
| Ethanol | 0.015 | 26800 | 100 | Click on selection
| Butane | 0.078 | 45700 | 2.7
| Benzene | 0.085 | 40100 | 2.7
| Hexane | 0.074 | 44700 | 1.9
| Heptane | 0.101 | 44600 | 1.1
| Xylene | 0.09 | 40800 | 1.4
| Acetone | 0.041 | 25800 | 1.9
| Dioxane | 0.018 | 26200 | 5.4
| Diethy Ether | 0.085 | 34200 | 0.7
| Benzine | 0.048 | 44700 | 3.6
| Gasoline | 0.055 | 43700 | 2.1
| Kerosine | 0.039 | 43200 | 3.5
| Diesel | 0.045 | 44400 | 2.1
| JP-4 | 0.051 | 43500 | 3.6
| JP-5 | 0.054 | 43000 | 1.6
| Transformer Oil, Hydrocarbon | 0.039 | 46000 | 0.7
| 561 Silicon Transformer Fluid | 0.005 | 28100 | 100
| Fuel Oil, Heavy | 0.035 | 39700 | 1.7
| Crude Oil | 0.0335 | 42600 | 2.8
| Lube Oil | 0.039 | 46000 | 0.7
| Douglas Fir Plywood | 0.01082 | 10900 | 100
| User Specified Value | Enter Value | Enter Value | Enter Value
Reference: SFPE Handbook of Fire Protection Engineering, 3rd Edition, 2002, Page 3-26.
ESTIMATING RADIATIVE HEAT FLUX TO A TARGET FUEL IN PRESENCE OF WIND
Reference: SFPE Handbook of Fire Protection Engineering, 3rd Edition, 1995, Page 3-272.
SOLID FLAME RADIATION MODEL IN PRESENCE OF WIND
q" = EF1->2
Where
| q" = | incident radiative heat flux on the target (kW/m2)
| E = | emissive power of the pool fire flame (kW/m2)
| F1->2 = | view factor between target and the flame in presence of wind
Pool Fire Diameter Calculation
Adike = pD2/4
D = √(4 Adike/p)
Where
|  | Adike = | surface area of pool fire (m2)
|  | D = | pool fire diameter (m)
|  | D = | 1.5389 | m
Pool Fire Radius Calculation
|  | r = | D/2
|  | r = | 0.76945 | m
Flame Emissive Power Calculation
E = 58 (10-0.00823 D)
Where
|  | E = | emissive power of the pool fire flame (kW/m2)
|  | D = | diameter of the pool fire (m)
|  | E = | 56.333 | (kW/m2)
View Factor Calculation in Presence of Wind
|  | p F1->2,V1 = | (a1 Cosq/(b - a1 Sinq)) (a12 + (b + 1)2 - 2b (1 + a1 Sinq))/ (A1B1)0.5 (tan-1 (A1/B1)0.5 ((b - 1)/(b + 1))0.5 + Cosq/(C)0.5((tan-1 (a1b -(b2-1) Sinq)/((b2 - 1) (C))0.5+ tan-1 (b2-1) Sinq/((b2 - 1)0.5 (C)0.5)) - (a1 Cosq)/(b - a1 Sinq) (tan-1 (b - 1/b + 1)0.5
|  | p F1->2,V2 = | (a2 Cosq/(b - a2 Sinq)) (a22 + (b + 1)2 - 2b (1 + a2 Sinq))/ (A2B2)0.5 (tan-1 (A2/B2)0.5 ((b - 1)/(b + 1))0.5 + Cosq/(C)0.5((tan-1(a2b - (b2-1) Sinq)/((b2 - 1) (C))0.5 + tan-1 (b2-1) Sinq/((b2 - 1)0.5 (C)0.5)) - (a2 Cosq)/(b - a2 Sinq) (tan-1 (b - 1/b + 1)0.5
|  | A1 = | a12 + (b +1)2 - 2a1 (b + 1) sinq
|  | A2 = | a22 + (b +1)2 - 2a2 (b + 1) sinq
|  | B1 = | a12 + (b - 1)2 - 2a1 (b - 1) sinq
|  | B2 = | a22 + (b - 1)2 - 2a2 (b - 1) sinq
|  | C = | 1 + (b2 - 1) Cos2q
|  | a1 = | 2Hf1/r = 2H1/r
|  | a2 = | 2Hf2/r = 2 (Hf - Hf1)/r
|  | b = | R/r
F1->2,V = F1->2,V1 + F1->2,V2
Where
|  | F1->2,V = | total vertical view factor in presence of wind
|  | R = | distance from center of the pool fire to edge of the target (m)
|  | Hf = | height of the pool fire flame (m)
|  | r = | pool fire radius (m)
|  | q = | flame tilt or angle of deflection (radians)
Distance from Center of the Pool Fire to Edge of the Target Calculation
R = L+ r
Where
|  | R= | distance from center of the pool fire to edge of the target (m)
|  | L= | Distance between Fire and Target
|  | r= | pool fire radius (m)
|  | R= | 9.9135 | m
Heat Release Rate Calculation
Q = m"DHc,eff (1 - e-kb D) Adike
Where
|  | Q = | pool fire heat release rate (kW)
|  | m" = | mass burning rate of fuel per unit surface area (kg/m2-sec)
|  | DHc = | effective heat of combustion of fuel (kJ/kg)
|  | Adike = | surface area of pool fire (area involved in vaporization) (m2)
|  | kb = | empirical constant (m-1)
|  | D = | diameter of pool fire (diameter involved in vaporization, circular pool is assumed) (m)
|  | Q = | 261.33 | kW
Pool Fire Flame Height Calculation
Hf = 55 D (m"/ra √(g D))0.67 (u*)-0.21
Where
|  | Hf = | flame height (m)
|  | m" = | mass burning rate of fuel (kg/m2-sec)
|  | D = | pool fire diameter (m)
|  | ra = | ambient air density (kg/m3)
|  | g = | gravitational acceleration (m/sec2)
|  | u* = | nondimensional wind velocity
|  | Hf = | 0.55229 | m
Nondimensional Wind Velocity Calculation
u* = uw/(g m" D/ra)1/3
Where
|  | u* = | nondimensional wind velocity
|  | uw = | wind velocity (m/sec)
|  | g = | gravitational acceleration (m/sec2)
|  | m" = | mass burning rate of fuel (kg/m2-sec)
|  | D = | pool fire diameter (m)
|  | ra = | ambient air density (kg/m3)
|  | u* = | 8.9129
Flame Tilt or Angle of Deflection Calculation
|  | COS q = 1 | for u* ≤ 1
|  | COS q = 1 / (√u*) | for u* ≥ 1
Since u* ≥ 1
|  | q = | ACOS(1/(u*)^0.5) = | 1.2292 | Rad | 70.43 | degree
|  |  |  | 1.2292 | Rad | 70.43 | degree
|  |  |  | 0 | Rad | 0 | degree
|  | A1 = a12 + (b +1)2 - 2a1 (b + 1) sinq = |  | 48.2447
|  | A2 = a22 + (b +1)2 - 2a2 (b + 1) sinq = |  | 404.5621
|  | B1 = a12 + (b - 1)2 - 2a1 (b - 1) sinq = |  | 26.569
|  | B2 = a22 + (b - 1)2 - 2a2 (b - 1) sinq = |  | 328.578 | [6 empty] | F1->2,V1
|  | C = 1 + (b2 - 1) Cos2q = |  | 19.5116 | [6 empty] | 0.040599
|  | a1 = 2Hf1/r = 2H1/r = |  | 7.9225 | [6 empty] | F1->2,V2
|  | a2 = 2Hf2/r = 2 (Hf - Hf1)/r = |  | -6.487 | [6 empty] | -0.0048712
|  | b = R/r = |  | 12.8838
|  | F1->2,V1 | 0.040599 | FV1 | FV2 | FV3 | FV4 | FV5 | FV6 | FV7
|  | F1->2,V2 | -0.0048712 | 0.48971 | 1.0448 | 0.89476 | 0.075831 | -0.75499 | 1.2208 | 0.36559
|  | F1->2 = F1->2,V1 + F1->2,V2 = | 0.035727 | FV1 | FV2 | FV3 | FV4 | FV5 | FV6 | FV7
|  |  |  | -0.11439 | 1.0054 | 0.79852 | 0.075831 | -1.3377 | 1.2208 | -0.085394
RADIATIVE HEAT FLUX CALCULATIONS IN PRESCENCE OF WIND
q" = EF1->2
Answer | q" = | 2.0126 | 0.035727: kW/m2; FV1: 0.17722; FV2: Btu/ft2-sec
NOTE:
The above calculations are based on principles developed in the SFPE Handbook of Fire Protection Engineering, 3rd Edition, 2002. Calculations are based on certain assumptions and have inherent limitations. The results of such calculations may or may not have reasonable predictive capabilities for a given situation and should only be interpreted by an informed user. Although each calculation in the spreadsheet has been verified with the results of hand calculation, there is no absolute guarantee of the accuracy of these calculations. Any questions, comments, concerns and suggestions or to report an error(s) in the spreadsheets, please send an email to David.Stroup@nrc.gov or Naeem.Iqbal@nrc.gov.
Prepared by: |  |  | FV1: Date:; FV3: Organization:
Checked by: |  |  | FV1: Date:; FV3: Organization:
Additional Information:
Revision Log | Description of Revision |  | FV2: Date
1805.0 | Original issue with final text. |  | FV2: December 2004
1805.1 | Revised e-mail addresses, corrected editorial errors, revised print pagination and print layout |  | FV2: March 2011
Note on F29: This default value (9.81) is the most appropriate value for the majority of analyses. You may change this value for your specific application. If you change this value please ensure that it is appropriate.