## Fireball_Heat_Flux-Calculations
CHAPTER 5
|  | ESTIMATING THERMAL RADIATION FROM | [6 empty] | Version 1805.1
|  | HYDROCARBON FIREBALLS | [6 empty] | (SI Units)
The following calculations estimate the thermal heat flux from hydrocarbon fuel vapors received by an object.
Parameters in YELLOW CELLS are Entered by the User.
Parameters in GREEN CELLS are Automatically Selected from the DROP DOWN MENU for the Fuel Type Selected.
All subsequent output values are calculated by the spreadsheet and based on values specified in the input parameters. This spreadsheet is protected
and secure to avoid errors due to a wrong entry in a cell(s). The chapter in the NUREG should be read before an analysis is made.
Project / Inspection Title:
INPUT PARAMETERS
| Mass of Fuel Vapor (mF) |  |  |  | 4.54 | kg |  |  | 4.54 | kg
| Distance at Ground Level from the Origin (L) |  |  |  | 91.44 | m |  |  | 91.44 | m
| Fuel Vapor Density (rF) |  |  |  | 1.6 | kg/m3
Calculate
THERMAL PROPERTIES FOR
Vapor Densities of Hydrocarbon Fuels at Normal
Temperature and Pressure
|  | Fuel |  |  | Fuel Vapor Density ( rF ) |  |  | Select Fuel Type
(kg/m3)
|  | Acetone |  |  | 2 |  |  | Scroll to desired fuel type then
|  | Acetylene |  |  | 0.9 |  |  | Click on selection
|  | Benzene |  |  | 2.8
|  | Butane |  |  | 2
|  | Carbon Monoxide |  |  | 1
|  | Cyclohexane |  |  | 29
|  | Ethanol |  |  | 1.5
|  | Ethane |  |  | 1
|  | Ethylene |  |  | 1
|  | Gasoline |  |  | 3.49
|  | Heptane |  |  | 3.5
|  | Hexane |  |  | 3
|  | Hydrogen |  |  | 0.1
|  | Methane |  |  | 0.6
|  | Methanol |  |  | 1.1
|  | Octene |  |  | 3.9
|  | Propane |  |  | 1.6
|  | Propylene |  |  | 1.5
|  | Styrene |  |  | 3.6
|  | Toluene |  |  | 3.1
|  | Xylene |  |  | 3.7
|  | User Specified Value |  |  | Enter Value
Reference: NFPA 325, Fire Hazard Properties of Flammable Liquids, Gases, and Volatile Solids, 1994 Edition.
ESTIMATING THERMAL RADIATION FROM HYDROCARBON FIREBALLS
METHOD OF HASEGAWA AND SATO
Reference: SFPE Handbook of Fire Protection Engineering, 3rd Edition, 2002, Page 3-306.
q"r = |  |  | 828 (mF)0.771/ R2
Where,
q"r = |  |  |  | thermal radiation from fireball (kW/m2)
mF = |  |  |  | mass of fuel vapor (kg)
R = |  |  |  | distance from the center of the fireball to the target (m)
Volume of the Fireball Fuel Calculation
VF = mF/rF
Where,
VF = |  |  |  | volume of fuel vapor (m3)
mF = |  |  |  | mass of fuel vapor (kg)
rF = |  |  |  | fuel vapor density (kg/m3)
VF = |  |  |  | 2.8375 |  | m3
Fireball Flame Height Calculation
Zp = 12.73 (VF)1/3
Where,
Zp = |  |  |  | height of the maximum visible flame (m)
VF = |  |  |  | volume of fuel vapor (m3)
Zp = |  |  |  | 18.0222 |  | m
Distance from the Center of the Fireball to the Target Calculation
R = √(Zp2 + L2)
Where,
R = |  |  |  | distance from center of the fireball to the target (m)
Zp = |  |  |  | height of the maximum visible flame (m)
L = |  |  |  | distance at ground level from the origin (m)
R = |  |  |  | 93.1991 |  | m
MAXIMUM HEAT FLUX ON TARGET
q"r = 828 (mF)0.771/ R2
Answer | q"r = | 0.30605 |  | kW/m2 |  |  | 0.02695 |  | Btu/ft2-sec
DIAMETER OF THE FIREBALL
D = 5.8 (mF)1/3
Where,
D = |  |  |  |  | maximum fireball diameter (m)
mF = |  |  |  |  | mass of fuel vapor (kg)
Answer | D = | 9.6039 |  | m |  |  | 31.5088 |  | ft
DURATION OF THE FIREBALL
tp = 2.8 (VF)1/6
Where,
tp = |  |  |  |  | time of the fireball (sec)
VF = |  |  |  |  | volume of fuel vapor (m3)
Answer | tp = | 3.3316 |  | sec |  |  | 0.055526 |  | min
NOTE:
The above calculations are based on principles developed in the SFPE Handbook of Fire Protection Engineering, 3rd Edition, 2002. Calculations are based on certain assumptions and have inherent limitations. The results of such calculations may or may not have reasonable predictive capabilities for a given situation and should only be interpreted by an informed user. Although each calculation in the spreadsheet has been verified with the results of hand calculation, there is no absolute guarantee of the accuracy of these calculations. Any questions, comments, concerns and suggestions or to report an error(s) in the spreadsheets, please send an email to David.Stroup@nrc.gov or Naeem.Iqbal@nrc.gov.
Prepared by: |  |  |  | Date: |  | Organization:
Checked by: |  |  |  | Date: |  | Organization:
Additional Information:
Revision Log | Description of Revision | [7 empty] | Date
1805.0 | Original issue with final text. | [7 empty] | December 2004
1805.1 | Revised e-mail addresses, corrected editorial errors, revised print pagination and print layout. | [7 empty] | March 2011