## Plume-Calculations (9.11-1)
CHAPTER 9
ESTIMATING CENTERLINE TEMPERATURE
|  | OF A | [5 empty] | Version 1805.1
|  | BUOYANT FIRE PLUME | [5 empty] | (English Units)
The following calculations estimate the centerline plume temperature in a compartment fire.
Parameters in YELLOW CELLS are Entered by the User.
All subsequent output values are calculated by the spreadsheet and based on values specified in the input parameters. This spreadsheet is protected
and secure to avoid errors due to a wrong entry in a cell(s). The chapter in the NUREG should be read before an analysis is made.
Project / Inspection Title:
INPUT PARAMETERS
| Heat Release Rate of the Fire (Q) |  |  |  | 1420 | kW
| Elevation Above the Fire Source (z) |  |  |  | 20 | ft |  | 6.096 | m
| Area of Combustible Fuel (Ac) |  |  |  | 10 | ft2 |  | 0.92903 | m2
| Ambient Air Temperature (Ta) |  |  |  | 77 | °F |  | 25 | °C
[8 empty] | 298 | °K
Calculate
AMBIENT CONDITIONS
| Specific Heat of Air (ca) |  |  |  | 1 | kJ/kg-K
| Ambient Air Density (ra) |  |  |  | 1.1846 | kg/m3
| Acceleration of Gravity (g) |  |  |  | 9.81 | m/sec2
| Convective Heat Release Fraction (cc) |  |  |  | 0.7
NOTE: Ambient Air Density (ra) will automatically correct with Ambient Air Temperature (Ta) Input
ESTIMATING PLUME CENTERLINE TEMPERATURE
Reference: SFPE Handbook of Fire Protection Engineering, 3rd Edition, 2002, Page 2-6.
Tp(centerline) - Ta = |  |  |  | 9.1 (Ta/g ca2 ra2)1/3 Qc2/3 (z - z0)-5/3
Where,
Tp(centerline) = |  |  |  | plume centerline temperature (°C)
Qc = |  |  |  | convective portion of the heat release rate (kW)
Ta = |  |  |  | ambient air temperature (K)
g = |  |  |  | acceleration of gravity (m/sec2)
ca = |  |  |  | specific heat of air (kJ/kg-K)
ra = |  |  |  | ambient air density (kg/m3)
z = |  |  |  | distance from the top of the fuel package to the ceiling (m)
z0 = |  |  |  | hypothetical virtual origin of the fire (m)
Convective Heat Release Rate Calculation
Qc = |  |  |  | cc Q
Where,
Qc = |  |  |  | convective portion of the heat release rate (kW)
Q = |  |  |  | heat release rate of the fire (kW)
cc = |  |  |  | convective heat release fraction
Qc = |  |  |  | 994 |  | kW
Fire Diameter Calculation
Ac = |  |  |  | pD2/4
D = |  |  |  | √(4 Ac/p)
Where,
Ac = |  |  |  | area of combustible fuel (m2)
D = |  |  |  | fire diameter (m)
D = |  |  |  | 1.0876 |  | m
Hypothetical Virtual Origin Calculation
z0/D = |  |  |  | -1.02 + 0.083 (Q2/5)/D
Where,
z0 = |  |  |  | virtual origin of the fire (m)
Q = |  |  |  | heat release rate of fire (kW)
D = |  |  |  | fire diameter (m)
z0/D = |  |  |  | 0.37163
z0 = |  |  |  | 0.40418 |  | m
Mean Flame Height Calculation
L = |  |  |  | -1.02D + 0.235 (Q2/5)
Where,
L = |  |  |  | mean flame height (m)
Q = |  |  |  | heat release rate of fire (kW)
D = |  |  |  | fire diameter (m)
L = |  |  |  | 3.18 |  | m
ESTIMATING PLUME CENTERLINE TEMPERATURE
Tp(centerline) - Ta = |  |  |  | 9.1 (Ta/g ca2 ra2)1/3 Qc2/3 (z - z0)-5/3
Tp(centerline) - Ta = |  |  |  | 139.2166 |  | °K
Tp(centerline) = |  |  |  | 9.1 (Ta/g ca2 ra2)1/3 Qc2/3 (z - z0)-5/3 + Ta
Tp(centerline) = |  |  |  | 437.2166 |  | °K
ESTIMATED PLUME CENTERLINE TEMPERATURE
Answer | Tp(centerline) = |  | 327.5899 |  | °F |  | 164.2166 | °C
NOTE:
The above calculations are based on principles developed in the SFPE Handbook of Fire Protection Engineering, 3rd Edition, 2002. Calculations are based on certain assumptions and have inherent limitations. The results of such calculations may or may not have reasonable predictive capabilities for a given situation and should only be interpreted by an informed user. Although each calculation in the spreadsheet has been verified with the results of hand calculation, there is no absolute guarantee of the accuracy of these calculations. Any questions, comments, concerns and suggestions or to report an error(s) in the spreadsheets, please send an email to David.Stroup@nrc.gov or Naeem.Iqbal@nrc.gov.
Prepared by: |  |  |  | Date: |  | Organization:
Checked by: |  |  |  | Date: |  | Organization:
Additional Information:
Revision Log | Description of Revision | [7 empty] | Date
1805.0 | Original issue with final text. | [7 empty] | December 2004
1805.1 | Corrected subscripts, revised e-mail addresses, corrected editorial errors, added flame height calculation, revised print pagination and print layout. | [7 empty] | March 2011
Note on F33: This default value (1.00) is the most appropriate value for the majority of analyses. You may change this value for your specific application. If you change this value please ensure that it is appropriate.
Note on F35: This default value (9.81) is the most appropriate value for the majority of analyses. You may change this value for your specific application. If you change this value please ensure that it is appropriate.
Note on F36: This default value (0.70) is the most appropriate value for the majority of analyses. You may change this value for your specific application. If you change this value please ensure that it is appropriate.