## Compartment-Pressure
CHAPTER 14
ESTIMATING PRESSURE RISE
|  | DUE TO A FIRE IN A | [5 empty] | Version 1805.1
|  | CLOSED COMPARTMENT | [5 empty] | (SI Units)
The following calculations estimate the pressure rise in a compartment due to fire and combustion.
Parameters in YELLOW CELLS are Entered by the User.
All subsequent output values are calculated by the spreadsheet and based on values specified in the input parameters. This spreadsheet is protected and
secure to avoid errors due to a wrong entry in a cell(s). The chapter in the NUREG should be read before an analysis is made.
Project / Inspection Title:
INPUT PARAMETERS
COMPARTMENT INFORMATION
| Compartment Width (wc) |  |  |  | 3.05 | m |  | 3.05 | m
| Compartment Length (lc) |  |  |  | 2.74 | m |  | 2.74 | m
| Compartment Height (hc) |  |  |  | 2.44 | m |  | 2.44 | m
| Fire Heat Release Rate (Q) |  |  |  | 75 | kW
| Time after Ignition (t) |  |  |  | 15 | sec
| Ambient Air Temperature (Ta) |  |  |  | 25 | °C |  | 25 | °C
[8 empty] | 298 | °K
Calculate
AMBIENT CONDITIONS
| Initial Atmospheric Pressure (Pa) |  |  |  | 101.35 | kPa |  | 101.35 | kPa
| Specific Heat of Air at Constant Volume (cv) |  |  |  | 0.71 | kJ/kg-K
| Ambient Air Density (ra) |  |  |  | 1.1846 | kg/m3
NOTE:
Values of Specific Heat of Air at Constant Volume (cv) range from 0.71 to 0.85 kJ/kg-k
Ambient Air Density (ra) will automatically correct with Ambient Air Temperature (Ta) Input
METHOD OF KARLSSON AND QUINTIERE
Reference: Karlsson and Quintiere, Enclosure Fire Dynamics, 1999, Page 192.
(P - Pa) / Pa = |  |  |  | Q t / (V ra cv Ta)
Where,
P = |  |  |  | compartment pressure due to fire and combustion (kPa)
Pa = |  |  |  | initial atmospheric pressure (kPa)
Q = |  |  |  | heat release rate of the fire (kW)
t = |  |  |  | time after ignition (sec)
V = |  |  |  | compartment volume (m3)
ra = |  |  |  | ambient density (kg/m3)
cv = |  |  |  | specific heat of air at constant volume (kJ/kg-K)
Ta = |  |  |  | ambient air temperature (K)
Compartment Volume Calculation
V = |  |  |  | wc x lc x hc
Where,
V = |  |  |  | volume of the compartment (m3)
wc = |  |  |  | compartment width (m)
lc = |  |  |  | compartment length (m)
hc = |  |  |  | compartment height (m)
V = |  |  |  | 20.3911 |  | m3 | 720.1042 | ft3
Pressure Rise in Compartment
(P - Pa) / Pa = |  |  |  | Q t / (V ra cv Ta)
(P-Pa)/Pa = |  |  |  | 0.22013 |  | atm
Multiplying by the atmospheric pressure (Pa) = 101 kPa
Gives a pressure difference equal to:
Answer | 22.3102 |  | kPa |  | 3.2358 |  | psi
This example shows that in a very short time the pressure in a closed compartment rises to quite a large value.
Most buildings have leaks of some sort. The above example indicates that even though a fire compartment may be closed, the pressure rise is very rapid and would presumably lead to sufficient leaks to prevent any further pressure rise from occurring. We will use this conclusion when dealing with pressure rises in enclosures with small leaks.
NOTE:
The above calculations are based on principles developed in the Enclosure Fire Dynamics. Calculations are based on certain assumptions and have inherent limitations. The results of such calculations may or may not have reasonable predictive capabilities for a given situation and should only be interpreted by an informed user. Although each calculation in the spreadsheet has been verified with the results of hand calculation, there is no absolute guarantee of the accuracy of these calculations. Any questions, comments, concerns and suggestions or to report an error(s) in the spreadsheet, please send an email to David.Stroup@nrc.gov or Naeem.Iqbal@nrc.gov.
Prepared by: |  |  |  | Date: |  | Organization:
Checked by: |  |  |  | Date: |  | Organization:
Additional Information:
Revision Log | Description of Revision | [6 empty] | Date
1805.0 | Original issue with final text. | [6 empty] | December 2004
1805.1 | Revised e-mail addresses, corrected editorial errors, revised print pagination and print layout. | [6 empty] | March 2011
Note on F39: This default value (101.35) is the most appropriate value for the majority of analyses. You may change this value for your specific application. If you change this value please ensure that it is appropriate.
Note on F40: This default value (0.71) is the most appropriate value for the majority of analyses. You may change this value for your specific application. If you change this value please ensure that it is appropriate.