## Beam
CHAPTER 17
ESTIMATING THE THICKNESS OF FIRE PROTECTION
| SPRAY-APPLIED COATING | [7 empty] | Version 1805.1
| FOR STRUCTURAL STEEL BEAMS | [7 empty] | (SI Units)
(SUBSTITUTION CORRELATION)
The following calculations estimate the full-scale cable tray heat release rate.
Parameters in YELLOW CELLS are Entered by the User.
Parameters in GREEN CELLS are Automatically Selected from the DROP DOWN MENU for the Cable Type Selected.
All subsequent output values are calculated by the spreadsheet and based on values specified in the input parameters. This spreadsheet is protected
and secure to avoid errors due to a wrong entry in a cell(s). The chapter in the NUREG should be read before an analysis is made.
Project / Inspection Title:
INPUT PARAMETERS
| Rated Design Thickness of Beam Insulation (T2) |  |  |  | 3.66 | cm | 1.4409 | in
Known Insulation Rating
| Weight of the Beam (W2) |  |  |  | 19 | lb/ft
| Heated Perimeter of Beam (D2) |  |  |  | 24.85 | in
Unknown Insulation Rating
| Weight of the Beam (W1) |  |  |  | 15 | lb/ft
| Heated Perimeter of Beam (D1) |  |  |  | 31.52 | in
SECTIONAL FACTORS FOR STEEL BEAMS | [8 empty] | 0.65
| Beam Size | Beam Wt. | Heated | W/D
|  | W (lb/ft) | Perimeter D (in)
| W36 x 300 | 300 | 121.56 | 2.47
| W36 x 135 | 135 | 105.75 | 1.28
| W33 x 201 | 201 | 113.17 | 1.78
| W33 x 118 | 118 | 99.06 | 1.19
| W30 x 173 | 173 | 104.53 | 1.66
| W30 x 99 | 99 | 89.61 | 1.1
| W27 x 146 | 146 | 95.45 | 1.53
| W27 x 84 | 84 | 82.38 | 1.02
| W24 x 104 | 104 | 85.37 | 1.22
| W24 x 68 | 68 | 73.53 | 0.92
| W21 x 101 | 101 | 78.59 | 1.29
| W21 x 62 | 62 | 65.9 | 0.94
| W21 x 44 | 44 | 60.12 | 0.73
| W18 x 106 | 106 | 69.88 | 1.52
| W18 x 76 | 76 | 68.68 | 1.11
| W18 x 50 | 50 | 57.76 | 0.87
| W18 x 35 | 35 | 52.8 | 0.66
| W16 x 77 | 77 | 63.02 | 1.22
| W16 x 57 | 57 | 53.36 | 1.07
| W16 x 40 | 40 | 52.4 | 0.76
| W16 x 31 | 31 | 47.79 | 0.65
| W16 x 26 | 26 | 47.38 | 0.55
| W14 x 370 | 70 | 81.96 | 0.85
| W14 x 145 | 145 | 74.7 | 1.94
| W14 x 82 | 82 | 57.99 | 1.41
| W14 x 68 | 68 | 57.36 | 1.19
| W14 x 53 | 53 | 51.28 | 1.03
| W14 x 43 | 43 | 50.7 | 0.85
| W14 x 38 | 38 | 47.89 | 0.79
| W14 x 30 | 30 | 47.33 | 0.63
| W14 x 26 | 26 | 42.39 | 0.61
| W14 x 22 | 22 | 42.02 | 0.52
| W12 x 96 | 96 | 60.8 | 1.58
| W12 x 72 | 72 | 59.76 | 1.2
| W12 x 50 | 50 | 47.88 | 1.04
| W12 x 40 | 40 | 47.31 | 0.85
| W12 x 35 | 35 | 44.08 | 0.79
| W12 x 30 | 30 | 43.72 | 0.69
| W12 x 26 | 26 | 43.45 | 0.6
| W12 x 22 | 22 | 36.19 | 0.61
| W12 x 16 | 16 | 35.51 | 0.45
| W10 x 112 | 112 | 52.46 | 2.14
| W10 x 68 | 68 | 50.25 | 1.35
| W10 x 54 | 54 | 49.53 | 1.09
| W10 x 45 | 45 | 43.56 | 1.03
| W10 x 39 | 39 | 43.17 | 0.9
| W10 x 33 | 33 | 42.76 | 0.77
| W10 x 30 | 30 | 37.77 | 0.79
| W10 x 22 | 22 | 37.11 | 0.59
| W10 x 19 | 19 | 32.04 | 0.59
| W10 x 15 | 15 | 31.52 | 0.48
| W8 x 58 | 58 | 41.14 | 1.41
| W8 x 48 | 48 | 40.53 | 1.18
| W8 x 40 | 40 | 39.99 | 1
| W8 x 35 | 35 | 39.68 | 0.88
| W8 x 31 | 31 | 39.42 | 0.79
| W8 x 28 | 28 | 35.16 | 0.8
| W8 x 24 | 24 | 34.86 | 0.69
| W8 x 21 | 21 | 31.87 | 0.66
| W8 x 18 | 18 | 31.57 | 0.57
| W8 x 15 | 15 | 27.78 | 0.54
| W8 x 13 | 13 | 27.52 | 0.47
| W6 x 25 | 25 | 30.36 | 0.82
| W6 x 20 | 20 | 29.94 | 0.67
| W6 x 16 | 16 | 24.13 | 0.66
| W6 x 12 | 12 | 23.6 | 0.51
| W6 x 9 | 9 | 23.28 | 0.39
| W5 x 19 | 19 | 24.85 | 0.76
| W5 x 16 | 16 | 24.54 | 0.65
| W4 x 13 | 13 | 19.94 | 0.65
| User Specified Value | Enter Value | Enter Value
Select the Beam with known |  |  |  |  | Select the Beam with unknown
rating for insulation thickness |  |  |  |  | rating for insulation thickness
| Subscript 2 |  |  |  | Subscript 1
| (Rated Beam) |  |  | Calculate | (Substitute Beam)
ESTIMATING THICKNESS OF FIRE PROTECTION INSULATION ON UNRATED BEAM
Reference: UL Fire Resistance Directory, Volume 1, 1995, Page 19.
T1 = ((W2/D2 + 0.6)T2)/(W1/D1 + 0.6)
Where
T1 = calculated thickness of fire protection insulation on unrated beam (in)
T2 = design thickness of insulation on rated beam (in)
W1 = weight of beam with unknown insulation rating (lb/ft)
W2 = weight of design rated beam (lb/ft)
D1 = heated perimeter of unrated beam (in)
D2 = heated perimeter of the rated beam (in)
REQUIRED EQUIVALENT THICKNESS OF FIRE PROTECTION INSULATION ON UNRATED BEAM
T1 = ((W2/D2 + 0.6)T2)/(W1/D1 + 0.6)
Answer | T1 = |  | 4.6421 | cm |  | 1.8276 | in
Beams with a larger W/D ratio can always be substituted for the structural member listed with a specific fire
resistive covering without changing the thickness of the covering.
NOTE:
The above calculations are based on principles developed in the SFPE Handbook of Fire Protection Engineering, 3rd Edition, 2002. Calculations are based on certain assumptions and have inherent limitations. The results of such calculations may or may not have reasonable predictive capabilities for a given situation and should only be interpreted by an informed user. Although each calculation in the spreadsheet has been verified with the results of hand calculation, there is no absolute guarantee of the accuracy of these calculations. Any questions, comments, concerns and suggestions or to report an error(s) in the spreadsheets, please send an email to David.Stroup@nrc.gov or Naeem.Iqbal@nrc.gov.
Prepared by: |  |  |  | Date: |  | Organization:
Checked by: |  |  |  | Date: |  | Organization:
Additional Information:
Revision Log | Description of Revision |  |  |  |  | Date
1805.0 | Original issue with final text. |  |  |  |  | December 2004
1805.1 | Revised e-mail addresses, corrected editorial errors, revised print pagination |  |  |  |  | March 2011
and print layout.

## Column
CHAPTER 17
ESTIMATING THE THICKNESS OF FIRE PROTECTION
| SPRAY-APPLIED COATING | [7 empty] | Version 1805.1
| FOR STRUCTURAL STEEL COLUMNS | [7 empty] | (SI Units)
(SUBSTITUTION CORRELATION)
The following calculations estimate the full-scale cable tray heat release rate.
Parameters in YELLOW CELLS are Entered by the User.
Parameters in GREEN CELLS are Automatically Selected from the DROP DOWN MENU for the Cable Type Selected.
All subsequent output values are calculated by the spreadsheet and based on values specified in the input parameters. This spreadsheet is protected
and secure to avoid errors due to a wrong entry in a cell(s). The chapter in the NUREG should be read before an analysis is made.
Project / Inspection Title:
INPUT PARAMETERS
| Thickness of Coating Used on the Rated Steel Column Section (X1) |  |  |  | 3.66 | cm | 1.4409 | in
Known Insulation Rating
| Weight Per Foot of the Rated Steel Column Section (W1) |  |  |  | 16 | lb/ft
| Heated Perimeter of the Rated Steel Column Section at Interface with Coating (D1) |  |  |  | 28.16 | in
Unknown Insulation Rating
| Weight Per Foot of Smaller Wide Flange Steel Column Section (W2) |  |  |  | 19 | lb/ft
| Heated Perimeter of the Unrated Steel Section at Interface with Coating (D2) |  |  |  | 36.06 | in
SECTIONAL FACTORS FOR STEEL COLUMNS
| Column Size | Column Wt. | Heated | W/D
|  | W (lb/ft) | Perimeter D (in)
| W36 x 300 | 300 | 138.21 | 2.17
| W36 x 135 | 135 | 117.7 | 1.15
| W33 x 201 | 201 | 128.91 | 1.56
| W33 x 118 | 118 | 110.54 | 1.07
| W30 x 173 | 173 | 119.51 | 1.45
| W30 x 99 | 99 | 100.06 | 0.99
| W27 x 146 | 146 | 109.41 | 1.33
| W27 x 84 | 84 | 92.34 | 0.91
| W24 x 104 | 104 | 98.12 | 1.06
| W24 x 68 | 68 | 82.49 | 0.82
| W21 x 101 | 101 | 90.88 | 1.11
| W21 x 62 | 62 | 74.14 | 0.84
| W21 x 44 | 44 | 66.62 | 0.66
| W18 x 106 | 106 | 81.08 | 1.31
| W18 x 76 | 76 | 79.71 | 0.95
| W18 x 50 | 50 | 65.25 | 0.77
| W18 x 35 | 35 | 58.8 | 0.6
| W16 x 77 | 77 | 73.31 | 1.05
| W16 x 57 | 57 | 60.48 | 0.94
| W16 x 40 | 40 | 59.39 | 0.67
| W16 x 31 | 31 | 53.31 | 0.58
| W16 x 26 | 26 | 52.88 | 0.49
| W14 x 370 | 70 | 98.43 | 0.71
| W14 x 145 | 145 | 90.2 | 1.61
| W14 x 82 | 82 | 68.12 | 1.2
| W14 x 68 | 68 | 67.39 | 1.01
| W14 x 53 | 53 | 59.34 | 0.89
| W14 x 43 | 43 | 58.69 | 0.73
| W14 x 38 | 38 | 54.66 | 0.7
| W14 x 30 | 30 | 54.06 | 0.55
| W14 x 26 | 26 | 47.41 | 0.55
| W14 x 22 | 22 | 47.02 | 0.47
| W12 x 96 | 96 | 72.96 | 1.32
| W12 x 72 | 72 | 71.8 | 1
| W12 x 50 | 50 | 55.96 | 0.89
| W12 x 40 | 40 | 55.31 | 0.72
| W12 x 35 | 35 | 50.64 | 0.69
| W12 x 30 | 30 | 50.24 | 0.6
| W12 x 26 | 26 | 49.94 | 0.52
| W12 x 22 | 22 | 40.22 | 0.55
| W12 x 16 | 16 | 39.5 | 0.41
| W10 x 112 | 112 | 62.87 | 1.78
| W10 x 68 | 68 | 60.38 | 1.13
| W10 x 54 | 54 | 59.56 | 0.91
| W10 x 45 | 45 | 51.58 | 0.87
| W10 x 39 | 39 | 51.15 | 0.76
| W10 x 33 | 33 | 50.72 | 0.65
| W10 x 30 | 30 | 43.58 | 0.69
| W10 x 22 | 22 | 42.86 | 0.51
| W10 x 19 | 19 | 36.06 | 0.53
| W10 x 15 | 15 | 35.52 | 0.42
| W8 x 58 | 58 | 49.36 | 1.18
| W8 x 48 | 48 | 48.64 | 0.99
| W8 x 40 | 40 | 48.06 | 0.83
| W8 x 35 | 35 | 47.7 | 0.73
| W8 x 31 | 31 | 47.41 | 0.65
| W8 x 28 | 28 | 41.69 | 0.67
| W8 x 24 | 24 | 41.35 | 0.58
| W8 x 21 | 21 | 37.14 | 0.57
| W8 x 18 | 18 | 36.82 | 0.49
| W8 x 15 | 15 | 31.79 | 0.47
| W8 x 13 | 13 | 31.52 | 0.41
| W6 x 25 | 25 | 36.44 | 0.69
| W6 x 20 | 20 | 35.96 | 0.56
| W6 x 16 | 16 | 28.16 | 0.57
| W6 x 12 | 12 | 27.6 | 0.43
| W6 x 9 | 9 | 27.22 | 0.33
| W5 x 19 | 19 | 29.88 | 0.64
| W5 x 16 | 16 | 29.54 | 0.54
| W4 x 13 | 13 | 24 | 0.54
| User Specified Value | Enter Value | Enter Value
Select the Column with known |  |  |  | Select the Column with unknown
rating for insulation thickness |  |  |  | rating for insulation thickness
| Subscript 1 |  |  | Subscript 2
| (Rated Column) |  | Calculate | (Substitute Column)
ESTIMATING THICKNESS OF FIRE PROTECTION INSULATION ON UNRATED COLUMN
Reference: UL Fire Resistance Directory, Volume 1, 1995, Page 19.
X2 = 1.25 (X1) (W1/D1) (D2/W2)
Where
X2 = thickness of coating for smaller wide flange section (in)
X1 = thickness of coating used on the rated steel section (in)
W2 = weight per foot of smaller wide flange section (lb/ft)
W1 = weight per foot of the rated steel section (lb/ft)
D2 = heated perimeter of smaller steel (unrated) section at interface with coating (in)
D1 = heated perimeter of the rated steel section at interface with coating(in)
REQUIRED EQUIVALENT THICKNESS OF FIRE PROTECTION INSULATION ON UNRATED COLUMN
X2 = 1.25 (X1) (W1/D1) (D2/W2)
Answer | X2 = |  | 4.9334 | cm | 1.9423 | in
NOTE:
The above calculations are based on principles developed in the SFPE Handbook of Fire Protection Engineering, 3rd Edition, 2002. Calculations are based on certain assumptions and have inherent limitations. The results of such calculations may or may not have reasonable predictive capabilities for a given situation and should only be interpreted by an informed user. Although each calculation in the spreadsheet has been verified with the results of hand calculation, there is no absolute guarantee of the accuracy of these calculations. Any questions, comments, concerns and suggestions or to report an error(s) in the spreadsheets, please send an email to David.Stroup@nrc.gov or Naeem.Iqbal@nrc.gov.
Prepared by: |  |  |  | Date: |  | Organization:
Checked by: |  |  |  | Date: |  | Organization:
Additional Information:
Revision Log | Description of Revision |  |  |  | Date
1805.0 | Original issue with final text. |  |  |  | December 2004
1805.1 | Revised e-mail addresses, corrected editorial errors, revised print pagination and print layout. |  |  |  | March 2011

## Data
SECTIONAL FACTORS FOR STEEL MEMBERS
BEAMS |  |  |  | COLUMNS
Beam Size | Beam Wt. | Heated | W/D | Column Size | Column Wt. | Heated | W/D
| W (lb/ft) | Perimeter D (in) | (lb/ft-in) |  | W (lb/ft) | Perimeter D (in) | (lb/ft-in)
W36 x 300 | 300 | 121.56 | 2.47 | W36 x 300 | 300 | 138.21 | 2.17
W36 x 135 | 135 | 105.75 | 1.28 | W36 x 135 | 135 | 117.7 | 1.15
W33 x 201 | 201 | 113.17 | 1.78 | W33 x 201 | 201 | 128.91 | 1.56
W33 x 118 | 118 | 99.06 | 1.19 | W33 x 118 | 118 | 110.54 | 1.07
W30 x 173 | 173 | 104.53 | 1.66 | W30 x 173 | 173 | 119.51 | 1.45
W30 x 99 | 99 | 89.61 | 1.1 | W30 x 99 | 99 | 100.06 | 0.99
W27 x 146 | 146 | 95.45 | 1.53 | W27 x 146 | 146 | 109.41 | 1.33
W27 x 84 | 84 | 82.38 | 1.02 | W27 x 84 | 84 | 92.34 | 0.91
W24 x 104 | 104 | 85.37 | 1.22 | W24 x 104 | 104 | 98.12 | 1.06
W24 x 68 | 68 | 73.53 | 0.92 | W24 x 68 | 68 | 82.49 | 0.82
W21 x 101 | 101 | 78.59 | 1.29 | W21 x 101 | 101 | 90.88 | 1.11
W21 x 62 | 62 | 65.9 | 0.94 | W21 x 62 | 62 | 74.14 | 0.84
W21 x 44 | 44 | 60.12 | 0.73 | W21 x 44 | 44 | 66.62 | 0.66
W18 x 106 | 106 | 69.88 | 1.52 | W18 x 106 | 106 | 81.08 | 1.31
W18 x 76 | 76 | 68.68 | 1.11 | W18 x 76 | 76 | 79.71 | 0.95
W18 x 50 | 50 | 57.76 | 0.87 | W18 x 50 | 50 | 65.25 | 0.77
W18 x 35 | 35 | 52.8 | 0.66 | W18 x 35 | 35 | 58.8 | 0.6
W16 x 77 | 77 | 63.02 | 1.22 | W16 x 77 | 77 | 73.31 | 1.05
W16 x 57 | 57 | 53.36 | 1.07 | W16 x 57 | 57 | 60.48 | 0.94
W16 x 40 | 40 | 52.4 | 0.76 | W16 x 40 | 40 | 59.39 | 0.67
W16 x 31 | 31 | 47.79 | 0.65 | W16 x 31 | 31 | 53.31 | 0.58
W16 x 26 | 26 | 47.38 | 0.55 | W16 x 26 | 26 | 52.88 | 0.49
W14 x 370 | 70 | 81.96 | 0.85 | W14 x 370 | 70 | 98.43 | 0.71
W14 x 145 | 145 | 74.7 | 1.94 | W14 x 145 | 145 | 90.2 | 1.61
W14 x 82 | 82 | 57.99 | 1.41 | W14 x 82 | 82 | 68.12 | 1.2
W14 x 68 | 68 | 57.36 | 1.19 | W14 x 68 | 68 | 67.39 | 1.01
W14 x 53 | 53 | 51.28 | 1.03 | W14 x 53 | 53 | 59.34 | 0.89
W14 x 43 | 43 | 50.7 | 0.85 | W14 x 43 | 43 | 58.69 | 0.73
W14 x 38 | 38 | 47.89 | 0.79 | W14 x 38 | 38 | 54.66 | 0.7
W14 x 30 | 30 | 47.33 | 0.63 | W14 x 30 | 30 | 54.06 | 0.55
W14 x 26 | 26 | 42.39 | 0.61 | W14 x 26 | 26 | 47.41 | 0.55
W14 x 22 | 22 | 42.02 | 0.52 | W14 x 22 | 22 | 47.02 | 0.47
W12 x 96 | 96 | 60.8 | 1.58 | W12 x 96 | 96 | 72.96 | 1.32
W12 x 72 | 72 | 59.76 | 1.2 | W12 x 72 | 72 | 71.8 | 1
W12 x 50 | 50 | 47.88 | 1.04 | W12 x 50 | 50 | 55.96 | 0.89
W12 x 40 | 40 | 47.31 | 0.85 | W12 x 40 | 40 | 55.31 | 0.72
W12 x 35 | 35 | 44.08 | 0.79 | W12 x 35 | 35 | 50.64 | 0.69
W12 x 30 | 30 | 43.72 | 0.69 | W12 x 30 | 30 | 50.24 | 0.6
W12 x 26 | 26 | 43.45 | 0.6 | W12 x 26 | 26 | 49.94 | 0.52
W12 x 22 | 22 | 36.19 | 0.61 | W12 x 22 | 22 | 40.22 | 0.55
W12 x 16 | 16 | 35.51 | 0.45 | W12 x 16 | 16 | 39.5 | 0.41
W10 x 112 | 112 | 52.46 | 2.14 | W10 x 112 | 112 | 62.87 | 1.78
W10 x 68 | 68 | 50.25 | 1.35 | W10 x 68 | 68 | 60.38 | 1.13
W10 x 54 | 54 | 49.53 | 1.09 | W10 x 54 | 54 | 59.56 | 0.91
W10 x 45 | 45 | 43.56 | 1.03 | W10 x 45 | 45 | 51.58 | 0.87
W10 x 39 | 39 | 43.17 | 0.9 | W10 x 39 | 39 | 51.15 | 0.76
W10 x 33 | 33 | 42.76 | 0.77 | W10 x 33 | 33 | 50.72 | 0.65
W10 x 30 | 30 | 37.77 | 0.79 | W10 x 30 | 30 | 43.58 | 0.69
W10 x 22 | 22 | 37.11 | 0.59 | W10 x 22 | 22 | 42.86 | 0.51
W10 x 19 | 19 | 32.04 | 0.59 | W10 x 19 | 19 | 36.06 | 0.53
W10 x 15 | 15 | 31.52 | 0.48 | W10 x 15 | 15 | 35.52 | 0.42
W8 x 58 | 58 | 41.14 | 1.41 | W8 x 58 | 58 | 49.36 | 1.18
W8 x 48 | 48 | 40.53 | 1.18 | W8 x 48 | 48 | 48.64 | 0.99
W8 x 40 | 40 | 39.99 | 1 | W8 x 40 | 40 | 48.06 | 0.83
W8 x 35 | 35 | 39.68 | 0.88 | W8 x 35 | 35 | 47.7 | 0.73
W8 x 31 | 31 | 39.42 | 0.79 | W8 x 31 | 31 | 47.41 | 0.65
W8 x 28 | 28 | 35.16 | 0.8 | W8 x 28 | 28 | 41.69 | 0.67
W8 x 24 | 24 | 34.86 | 0.69 | W8 x 24 | 24 | 41.35 | 0.58
W8 x 21 | 21 | 31.87 | 0.66 | W8 x 21 | 21 | 37.14 | 0.57
W8 x 18 | 18 | 31.57 | 0.57 | W8 x 18 | 18 | 36.82 | 0.49
W8 x 15 | 15 | 27.78 | 0.54 | W8 x 15 | 15 | 31.79 | 0.47
W8 x 13 | 13 | 27.52 | 0.47 | W8 x 13 | 13 | 31.52 | 0.41
W6 x 25 | 25 | 30.36 | 0.82 | W6 x 25 | 25 | 36.44 | 0.69
W6 x 20 | 20 | 29.94 | 0.67 | W6 x 20 | 20 | 35.96 | 0.56
W6 x 16 | 16 | 24.13 | 0.66 | W6 x 16 | 16 | 28.16 | 0.57
W6 x 12 | 12 | 23.6 | 0.51 | W6 x 12 | 12 | 27.6 | 0.43
W6 x 9 | 9 | 23.28 | 0.39 | W6 x 9 | 9 | 27.22 | 0.33
W5 x 19 | 19 | 24.85 | 0.76 | W5 x 19 | 19 | 29.88 | 0.64
W5 x 16 | 16 | 24.54 | 0.65 | W5 x 16 | 16 | 29.54 | 0.54
W4 x 13 | 13 | 19.94 | 0.65 | W4 x 13 | 13 | 24 | 0.54
User Specified Value | Enter Value | Enter Value |  | User Specified Value | Enter Value | Enter Value