## Beam
CHAPTER 17
ESTIMATING FIRE RESISTANCE TIME OF STEEL BEAMS
|  | PROTECTED BY FIRE PROTECTION INSULATION | [6 empty] | Version 1805.1
|  | (QUASI-STEADY-STATE APPROACH) | [6 empty] | (SI Units)
The following calculations estimate the full-scale cable tray heat release rate.
Parameters in YELLOW CELLS are Entered by the User.
Parameters in GREEN CELLS are Automatically Selected from the DROP DOWN MENU for the Cable Type Selected.
All subsequent output values are calculated by the spreadsheet and based on values specified in the input parameters. This spreadsheet is protected
and secure to avoid errors due to a wrong entry in a cell(s). The chapter in the NUREG should be read before an analysis is made.
Project / Inspection Title:
INPUT PARAMETERS
| Ratio of Weight of Steel Section per Linear Foot and Heated Perimeter (W/D) | [5 empty] | 23.9671 | lb/ft2
| Thickness of Spray-Applied Protection on Steel Beam (h) |  |  |  |  | h ≥ 1/6 cm | 1.3 | cm | 0.042651 | ft
| Density of Spray-Applied Material (ri) | [5 empty] | 22 | lb/ft3
| Thermal Conductivity of Spray-Applied Material (ki) | [5 empty] | 0.06936 | Btu/ft-hr-°F | 1.9267e-05 | Btu/ft-sec-°F
| Specific Heat of Spray-Applied Material (ci) | [5 empty] | 0.2868 | Btu/lb-°F
| Ambient Air Temperature (Ta) | [5 empty] | 25 | °C | 77
| Specific Heat of Steel (cs) | [5 empty] | 0.132 | Btu/lb-°F
Calculate
SECTIONAL FACTORS FOR STEEL BEAMS
| Structural Shape | W/D Ratio
| W Shapes | (lb/ft2)
| 36x300 | 29.6162
| 36x280 | 27.756
| 36x260 | 25.8943
| 36x245 | 24.4816
| 36x230 | 23.0596
| 36x210 | 23.2773
| 36x194 | 21.5965
| 36x182 | 20.3286
| 36x170 | 19.053
| 36x160 | 17.991
| 36x150 | 16.9213
| 36x135 | 15.3191
| 33x241 | 25.3063
| 33x221 | 23.3194
| 33x201 | 21.314
| 33x152 | 18.1664
| 33x141 | 16.9208
| 33x130 | 15.6705
| 33x118 | 14.2944
| 30x211 | 23.9671
| 30x191 | 21.8161
| 30x173 | 19.8613
| 30x132 | 17.4018
| 30x124 | 16.403
| 30x116 | 15.4025
| 30x108 | 14.4008
| 30x99 | 13.2574
| 27x178 | 22.1519
| 27x161 | 20.1418
| 27x146 | 18.3561
| 27x114 | 16.3539
| 27x102 | 14.7124
| 27x94 | 13.6183
| 27x84 | 12.236
| 24x162 | 22.2286
| 24x146 | 20.1657
| 24x131 | 18.2124
| 24x117 | 16.3598
| 24x104 | 14.6187
| 24x94 | 15.0832
| 24x84 | 13.563
| 24x76 | 12.336
| 24x68 | 11.0983
| 24x62 | 10.9832
| 24x55 | 9.7974
| 21x147 | 21.9923
| 21x132 | 19.8795
| 21x122 | 18.4546
| 21x111 | 16.8736
| 21x101 | 15.4218
| 21x93 | 16.5726
| 21x83 | 14.889
| 21x73 | 13.1819
| 21x68 | 12.3244
| 21x62 | 11.2898
| 21x57 | 11.2205
| 21x50 | 9.919
| 21x44 | 8.7824
| 18x119 | 20.2769
| 18x106 | 18.2026
| 18x97 | 16.7374
| 18x86 | 14.937
| 18x76 | 13.2799
| 18x71 | 14.4763
| 18x65 | 13.3174
| 18x60 | 12.3499
| 18x55 | 11.3734
| 18x50 | 10.3887
| 18x46 | 10.3024
| 18x40 | 9.02
| 18x35 | 7.9545
| 16x100 | 18.7368
| 16x89 | 16.807
| 16x77 | 14.6632
| 16x67 | 12.8486
| 16x57 | 12.8186
| 16x50 | 11.3272
| 16x45 | 10.2515
| 16x40 | 9.1612
| 16x36 | 8.2941
| 16x31 | 7.7849
| 16x26 | 6.5851
| 14x730 | 94.836
| 14x665 | 88.1086
| 14x605 | 81.6694
| 14x550 | 75.5841
| 14x500 | 69.8893
| 14x455 | 64.6039
| 14x426 | 61.0935
| 14x398 | 57.6742
| 14x370 | 54.1761
| 14x342 | 50.7293
| 14x311 | 46.5859
| 14x283 | 42.8626
| 14x257 | 39.3392
| 14x233 | 36.0263
| 14x211 | 32.9344
| 14x193 | 30.3499
| 14x176 | 27.8886
| 14x159 | 25.2923
| 14x145 | 23.2932
| 14x132 | 21.9375
| 14x120 | 20.0585
| 14x109 | 18.318
| 14x99 | 16.7218
| 14x90 | 15.2715
| 14x82 | 16.9684
| 14x74 | 15.4033
| 14x68 | 14.2272
| 14x61 | 12.8387
| 14x53 | 12.4025
| 14x48 | 11.2963
| 14x43 | 10.1785
| 14x38 | 9.5218
| 14x34 | 8.5669
| 14x30 | 7.6062
| 14x26 | 7.3611
| 14x22 | 6.2827
| 12x336 | 57.3991
| 12x305 | 52.9705
| 12x279 | 49.1919
| 12x252 | 45.104
| 12x230 | 41.6824
| 12x210 | 38.5144
| 12x190 | 35.2668
| 12x170 | 31.9499
| 12x152 | 28.8973
| 12x136 | 26.1371
| 12x120 | 23.3085
| 12x106 | 20.7775
| 12x96 | 18.9474
| 12x87 | 17.2833
| 12x79 | 15.7842
| 12x72 | 14.4578
| 12x65 | 13.1181
| 12x58 | 12.9633
| 12x53 | 11.9068
| 12x50 | 12.5313
| 12x45 | 11.3481
| 12x40 | 10.1469
| 12x35 | 9.5281
| 12x30 | 8.2342
| 12x26 | 7.1807
| 12x22 | 7.2948
| 12x19 | 6.3572
| 12x16 | 5.4069
| 12x14 | 4.7552
| 10x112 | 25.622
| 10x100 | 23.1392
| 10x88 | 20.5988
| 10x77 | 18.2213
| 10x68 | 16.2388
| 10x60 | 14.4462
| 10x54 | 13.083
| 10x49 | 11.9318
| 10x45 | 12.3967
| 10x39 | 10.8421
| 10x33 | 9.261
| 10x30 | 9.5314
| 10x26 | 8.3311
| 10x22 | 7.114
| 10x19 | 7.1161
| 10x17 | 6.4212
| 10x15 | 5.7107
| 10x12 | 4.6095
| 8x67 | 19.2806
| 8x58 | 16.9178
| 8x48 | 14.2117
| 8x40 | 12.003
| 8x35 | 10.5823
| 8x31 | 9.438
| 8x28 | 9.5577
| 8x24 | 8.2628
| 8x21 | 7.9071
| 8x18 | 6.8419
| 8x15 | 6.4806
| 8x13 | 5.6686
| 8x10 | 4.4021
| 6x25 | 9.8814
| 6x20 | 8.016
| 6x15 | 6.1038
| 6x16 | 7.9569
| 6x12 | 6.1017
| 6x9 | 4.6392
| 5x19 | 9.1751
| 5x16 | 7.824
| 4x13 | 7.82
| User Specified Value | Enter Value
Select Beam
Scroll to desired beam size then Click on selection
THERMAL PROPERTIES OF SPRAY-APPLIED INSULATION MATERIALS
Insulation Material |  | Density | Thermal | Specific Heat |  | Select Insulation Type
Spray-Applied |  | ρi | Conductivity ki | ci
|  | (lb/ft3) | (Btu/ft-hr-°F) | (Btu/lb-°F) |  | Scroll to desired material then Click on selection
Sprayed mineral fiber |  | 19 | 0.06936 | 0.2868
Perlite or vermiculite |  | 22 | 0.06936 | 0.2868
High density perlite or vermiculite |  | 35 | 0.06936 | 0.2868
User Specified Value |  | Enter Value | Enter Value | Enter Value
Reference: Buchanan, A. H., Structural Design for Fire Safety, 2001, Page 179.
ESTIMATING FIRE RESISTANCE TIME USING QUASI-STEADY-STATE APPROACH
Reference: "Analytical Methods for Determining Fire Resistance of Steel Members,"
"SFPE Handbook of Fire Protection Engineering, 3rd Edition, 2002, Page 4-209.
Temperature Rise in Steel Beam
DTs = (ki /(cs h W/D + 1/2 ci ri h2)) (Tf - Ts) Dt
Where
DTs = temperature rise in steel (°F)
ki = thermal conductivity of spray-applied material (Btu/ft-sec-°F)
ri = density of spray-applied material (lb/ft3)
ci = specific heat of spray-applied material (Btu/lb-°F)
cs = specific heat of steel (Btu/lb-°F)
h = thickness of spray-applied protection on steel beam (in)
W/D = ratio of weight of steel section per linear foot and heated perimeter (lb/ft2)
Tf = fire exposure temperature (°F)
Ts = steel temperature (°F)
Dt = time step (sec)
cs W/D > 2 ci ri h
Where
cs = specific heat of steel (Btu/lb-°F)
W/D = ratio of weight of steel section per linear foot and heated perimeter (lb/ft2)
ri = density of spray-applied material (lb/ft3)
ci = specific heat of spray-applied material (BTU/lb-°F)
h = thickness of spray-applied protection on steel beam (in)
|  |  | 3.1637 | > | 0.53822
The Maximum Allowable Time Step
Dt = 15.9 W/D
|  |  | Dt = | 381.0762 | sec
|  |  | Dt = | 6.3513 | minutes
For ASTM-E-119 exposure, Tf at any time, t, is given by the following expression
Tf = C1 LOG (0.133 t + 1) + Ta
Where
Tf = fire exposure temperature (°F)
C1 = constant = 620
t = time step (sec)
Ta = ambient air temperature (°F)
DTs1 = (ki /(cs h W/D + 1/2 ci ri h2)) ((C1 LOG (0.133 t1 + 1)+Ta) - Ts0) Dt
Where
|  | t1 = Dt/2 |  |  | Caution! This equation is only valid up to 1000 °F (538 °C) where
|  | Ts0 = initial steel temperature (°F) |  |  | carbon steel structural members begin to fail. Predicted
temperatures above 1000 °F (538 °C) are not accurate or valid.
DTs2 = (ki /(cs h W/D + 1/2 ci ri h2)) ((C1 LOG (0.133 t2 + 1)+Ta) - Ts) Dt
Where
t2 = t1 + Dt/2
Ts = Ts0 + DTs from previous row
Answer
Time | Time | DTs | Ts |  |  | Time | Time | DTs | Ts
(min) | (sec) | (°F) | (°C) |  |  | (min) | (sec) | (°F) | (°C)
6.3513 | 381.0762 | 50.7562 | 53.1979 |  |  | 336.6174 | 20197.041 | 112.2861 | 2932.1681 | Failure of Beam
12.7025 | 762.1525 | 63.715 | 88.5951 |  |  | 342.9686 | 20578.1173 | 112.5479 | 2994.6947 | Failure of Beam
19.0538 | 1143.2287 | 70.4178 | 127.7161 |  |  | 349.3199 | 20959.1935 | 112.8049 | 3057.3641 | Failure of Beam
25.4051 | 1524.305 | 74.9501 | 169.355 |  |  | 355.6712 | 21340.2698 | 113.0572 | 3120.1737 | Failure of Beam
31.7564 | 1905.3812 | 78.3673 | 212.8924 |  |  | 362.0224 | 21721.346 | 113.3051 | 3183.121 | Failure of Beam
38.1076 | 2286.4575 | 81.1098 | 257.9534 |  |  | 368.3737 | 22102.4223 | 113.5485 | 3246.2035 | Failure of Beam
44.4589 | 2667.5337 | 83.4001 | 304.2868 |  |  | 374.725 | 22483.4985 | 113.7878 | 3309.4189 | Failure of Beam
50.8102 | 3048.61 | 85.3662 | 351.7124 |  |  | 381.0762 | 22864.5748 | 114.023 | 3372.7651 | Failure of Beam
57.1614 | 3429.6862 | 87.0885 | 400.0949 |  |  | 387.4275 | 23245.651 | 114.2544 | 3436.2397 | Failure of Beam
63.5127 | 3810.7625 | 88.6208 | 449.3287 |  |  | 393.7788 | 23626.7272 | 114.4819 | 3499.8408 | Failure of Beam
69.864 | 4191.8387 | 90.0009 | 499.3291 |  |  | 400.1301 | 24007.8035 | 114.7057 | 3563.5662 | Failure of Beam
76.2152 | 4572.915 | 91.2562 | 550.0271 | Failure of Beam |  | 406.4813 | 24388.8797 | 114.9261 | 3627.414 | Failure of Beam
82.5665 | 4953.9912 | 92.4076 | 601.3646 | Failure of Beam |  | 412.8326 | 24769.956 | 115.1429 | 3691.3823 | Failure of Beam
88.9178 | 5335.0674 | 93.4708 | 653.2928 | Failure of Beam |  | 419.1839 | 25151.0322 | 115.3565 | 3755.4692 | Failure of Beam
95.2691 | 5716.1437 | 94.4584 | 705.7697 | Failure of Beam |  | 425.5351 | 25532.1085 | 115.5668 | 3819.673 | Failure of Beam
101.6203 | 6097.2199 | 95.3805 | 758.7589 | Failure of Beam |  | 431.8864 | 25913.1847 | 115.774 | 3883.9918 | Failure of Beam
107.9716 | 6478.2962 | 96.2452 | 812.2285 | Failure of Beam |  | 438.2377 | 26294.261 | 115.9781 | 3948.4241 | Failure of Beam
114.3229 | 6859.3724 | 97.0593 | 866.1503 | Failure of Beam |  | 444.589 | 26675.3372 | 116.1793 | 4012.9681 | Failure of Beam
120.6741 | 7240.4487 | 97.8283 | 920.4994 | Failure of Beam |  | 450.9402 | 27056.4135 | 116.3776 | 4077.6224 | Failure of Beam
127.0254 | 7621.5249 | 98.5569 | 975.2532 | Failure of Beam |  | 457.2915 | 27437.4897 | 116.5731 | 4142.3852 | Failure of Beam
133.3767 | 8002.6012 | 99.2493 | 1030.3917 | Failure of Beam |  | 463.6428 | 27818.566 | 116.7659 | 4207.2551 | Failure of Beam
139.728 | 8383.6774 | 99.9088 | 1085.8966 | Failure of Beam |  | 469.994 | 28199.6422 | 116.956 | 4272.2307 | Failure of Beam
146.0792 | 8764.7537 | 100.5384 | 1141.7512 | Failure of Beam |  | 476.3453 | 28580.7184 | 117.1436 | 4337.3105 | Failure of Beam
152.4305 | 9145.8299 | 101.1407 | 1197.9405 | Failure of Beam |  | 482.6966 | 28961.7947 | 117.3287 | 4402.4931 | Failure of Beam
158.7818 | 9526.9061 | 101.718 | 1254.4505 | Failure of Beam |  | 489.0478 | 29342.8709 | 117.5114 | 4467.7772 | Failure of Beam
165.133 | 9907.9824 | 102.2722 | 1311.2684 | Failure of Beam |  | 495.3991 | 29723.9472 | 117.6917 | 4533.1615 | Failure of Beam
171.4843 | 10289.0586 | 102.8052 | 1368.3824 | Failure of Beam |  | 501.7504 | 30105.0234 | 117.8697 | 4598.6446 | Failure of Beam
177.8356 | 10670.1349 | 103.3185 | 1425.7816 | Failure of Beam |  | 508.1017 | 30486.0997 | 118.0454 | 4664.2254 | Failure of Beam
184.1869 | 11051.2111 | 103.8135 | 1483.4558 | Failure of Beam |  | 514.4529 | 30867.1759 | 118.2189 | 4729.9026 | Failure of Beam
190.5381 | 11432.2874 | 104.2915 | 1541.3955 | Failure of Beam |  | 520.8042 | 31248.2522 | 118.3903 | 4795.675 | Failure of Beam
196.8894 | 11813.3636 | 104.7536 | 1599.592 | Failure of Beam |  | 527.1555 | 31629.3284 | 118.5596 | 4861.5414 | Failure of Beam
203.2407 | 12194.4399 | 105.2008 | 1658.0369 | Failure of Beam |  | 533.5067 | 32010.4047 | 118.7269 | 4927.5008 | Failure of Beam
209.5919 | 12575.5161 | 105.6341 | 1716.7225 | Failure of Beam |  | 539.858 | 32391.4809 | 118.8922 | 4993.5521 | Failure of Beam
215.9432 | 12956.5924 | 106.0543 | 1775.6416 | Failure of Beam |  | 546.2093 | 32772.5571 | 119.0555 | 5059.694 | Failure of Beam
222.2945 | 13337.6686 | 106.4621 | 1834.7872 | Failure of Beam |  | 552.5606 | 33153.6334 | 119.217 | 5125.9257 | Failure of Beam
228.6457 | 13718.7449 | 106.8583 | 1894.153 | Failure of Beam |  | 558.9118 | 33534.7096 | 119.3765 | 5192.246 | Failure of Beam
234.997 | 14099.8211 | 107.2436 | 1953.7327 | Failure of Beam |  | 565.2631 | 33915.7859 | 119.5343 | 5258.6539 | Failure of Beam
241.3483 | 14480.8973 | 107.6184 | 2013.5207 | Failure of Beam |  | 571.6144 | 34296.8621 | 119.6903 | 5325.1485 | Failure of Beam
247.6996 | 14861.9736 | 107.9834 | 2073.5115 | Failure of Beam |  | 577.9656 | 34677.9384 | 119.8446 | 5391.7289 | Failure of Beam
254.0508 | 15243.0498 | 108.339 | 2133.6999 | Failure of Beam |  | 584.3169 | 35059.0146 | 119.9972 | 5458.394 | Failure of Beam
260.4021 | 15624.1261 | 108.6858 | 2194.0809 | Failure of Beam |  | 590.6682 | 35440.0909 | 120.1481 | 5525.1429 | Failure of Beam
266.7534 | 16005.2023 | 109.0241 | 2254.6498 | Failure of Beam |  | 597.0195 | 35821.1671 | 120.2974 | 5591.9748 | Failure of Beam
273.1046 | 16386.2786 | 109.3544 | 2315.4023 | Failure of Beam |  | 603.3707 | 36202.2434 | 120.4451 | 5658.8887 | Failure of Beam
279.4559 | 16767.3548 | 109.677 | 2376.334 | Failure of Beam |  | 609.722 | 36583.3196 | 120.5913 | 5725.8839 | Failure of Beam
285.8072 | 17148.4311 | 109.9923 | 2437.4408 | Failure of Beam |  | 616.0733 | 36964.3959 | 120.7359 | 5792.9594 | Failure of Beam
292.1585 | 17529.5073 | 110.3006 | 2498.719 | Failure of Beam |  | 622.4245 | 37345.4721 | 120.879 | 5860.1144 | Failure of Beam
298.5097 | 17910.5836 | 110.6022 | 2560.1647 | Failure of Beam |  | 628.7758 | 37726.5483 | 121.0207 | 5927.3481 | Failure of Beam
304.861 | 18291.6598 | 110.8974 | 2621.7743 | Failure of Beam |  | 635.1271 | 38107.6246 | 121.161 | 5994.6598 | Failure of Beam
311.2123 | 18672.736 | 111.1865 | 2683.5446 | Failure of Beam |  | 641.4783 | 38488.7008 | 121.2998 | 6062.0486 | Failure of Beam
317.5635 | 19053.8123 | 111.4697 | 2745.4722 | Failure of Beam |  | 647.8296 | 38869.7771 | 121.4373 | 6129.5137 | Failure of Beam
323.9148 | 19434.8885 | 111.7472 | 2807.554 | Failure of Beam |  | 654.1809 | 39250.8533 | 121.5734 | 6197.0545 | Failure of Beam
330.2661 | 19815.9648 | 112.0193 | 2869.7869 | Failure of Beam |  | 660.5322 | 39631.9296 | 121.7083 | 6264.6702 | Failure of Beam
NOTE:
The above calculations are based on principles developed in the SFPE Handbook of Fire Protection Engineering, 3rd Edition, 2002. Calculations are based on certain assumptions and have inherent limitations. The results of such calculations may or may not have reasonable predictive capabilities for a given situation and should only be interpreted by an informed user. Although each calculation in the spreadsheet has been verified with the results of hand calculation, there is no absolute guarantee of the accuracy of these calculations. Any questions, comments, concerns and suggestions or to report an error(s) in the spreadsheets, please send an email to David.Stroup@nrc.gov or Naeem.Iqbal@nrc.gov.
Prepared by: |  |  |  | Date: |  | Organization:
Checked by: |  |  |  | Date: |  | Organization:
Additional Information:
Revision Log | Description of Revision |  |  |  |  | Date
1805.0 | Original issue with final text. |  |  |  |  | December 2004
1805.1 | Revised e-mail addresses, corrected editorial errors, revised print pagination and |  |  |  |  | March 2011
print layout.
Note on H27: This default value (0.132) is the most appropriate value for the majority of analyses. You may change this value for your specific application. If you change this value please ensure that it is appropriate.

## Column
CHAPTER 17
ESTIMATING FIRE RESISTANCE TIME OF STEEL COLUMNS
| PROTECTED BY FIRE PROTECTION INSULATION | [7 empty] | Version 1805.1
| (QUASI-STEADY-STATE APPROACH) | [7 empty] | (SI Units)
The following calculations estimate the full-scale cable tray heat release rate.
Parameters in YELLOW CELLS are Entered by the User.
Parameters in GREEN CELLS are Automatically Selected from the DROP DOWN MENU for the Cable Type Selected.
All subsequent output values are calculated by the spreadsheet and based on values specified in the input parameters. This spreadsheet is protected
and secure to avoid errors due to a wrong entry in a cell(s). The chapter in the NUREG should be read before an analysis is made.
Project / Inspection Title:
INPUT PARAMETERS
| Ratio of Weight of Steel Section per Linear Foot and Heated Perimeter (W/D) | [6 empty] | 13.7638 | lb/ft2
| Thickness of Spray-Applied Protection on Steel Column (h) |  |  |  |  | h ≥ 1/6 cm |  | 1.3 | cm | 0.042651 | ft
| Density of Spray-Applied Material (ri) | [6 empty] | 22 | lb/ft3
| Thermal Conductivity of Spray-Applied Material (ki) | [6 empty] | 0.06936 | Btu/ft-hr-°F | 1.9267e-05 | Btu/lb-sec-°F
| Specific Heat of Spray-Applied Material (ci) | [6 empty] | 0.2868 | Btu/lb-°F
| Ambient Air Temperature (Ta) | [6 empty] | 25 | °C | 77
| Specific Heat of Steel (cs) | [6 empty] | 0.132 | Btu/lb-°F
Calculate
SECTIONAL FACTORS FOR STEEL COLUMNS
| Structural Shape | W/D Ratio
| W Shapes | (lb/ft2)
| 36x300 | 26.0473
| 36x280 | 24.4097
| 36x260 | 22.7671
| 36x245 | 21.5227
| 36x230 | 20.2703
| 36x210 | 20.9233
| 36x194 | 19.4146
| 36x182 | 18.2746
| 36x170 | 17.1285
| 36x160 | 16.1725
| 36x150 | 15.2091
| 36x135 | 13.7638
| 33x241 | 22.2222
| 33x221 | 20.474
| 33x201 | 18.7107
| 33x152 | 16.2901
| 33x141 | 15.1708
| 33x130 | 14.0465
| 33x118 | 12.8098
| 30x211 | 20.9689
| 30x191 | 19.0841
| 30x173 | 17.3709
| 30x132 | 15.5952
| 30x124 | 14.6992
| 30x116 | 13.7999
| 30x108 | 12.8994
| 30x99 | 11.8729
| 27x178 | 19.3286
| 27x161 | 17.5732
| 27x146 | 16.0132
| 27x114 | 14.5967
| 27x102 | 13.1316
| 27x94 | 12.1526
| 27x84 | 10.9162
| 24x162 | 19.3606
| 24x146 | 17.5586
| 24x131 | 15.8516
| 24x117 | 14.2365
| 24x104 | 12.7191
| 24x94 | 13.4526
| 24x84 | 12.095
| 24x76 | 10.9986
| 24x68 | 9.8921
| 24x62 | 9.9492
| 24x55 | 8.8745
| 21x147 | 19.025
| 21x132 | 17.195
| 21x122 | 15.9616
| 21x111 | 14.5925
| 21x101 | 13.3363
| 21x93 | 14.7307
| 21x83 | 13.2359
| 21x73 | 11.7191
| 21x68 | 10.956
| 21x62 | 10.0351
| 21x57 | 10.1318
| 21x50 | 8.9526
| 21x44 | 7.9255
| 18x119 | 17.4807
| 18x106 | 15.6882
| 18x97 | 14.4256
| 18x86 | 12.871
| 18x76 | 11.4415
| 18x71 | 12.814
| 18x65 | 11.7896
| 18x60 | 10.9339
| 18x55 | 10.0671
| 18x50 | 9.1954
| 18x46 | 9.2555
| 18x40 | 8.104
| 18x35 | 7.1429
| 16x100 | 16.1139
| 16x89 | 14.45
| 16x77 | 12.604
| 16x67 | 11.0424
| 16x57 | 11.3095
| 16x50 | 9.9933
| 16x45 | 9.0437
| 16x40 | 8.0822
| 16x36 | 7.3134
| 16x31 | 6.9781
| 16x26 | 5.9002
| 14x730 | 79.4486
| 14x665 | 73.7387
| 14x605 | 68.2908
| 14x550 | 63.1458
| 14x500 | 58.3317
| 14x455 | 53.8727
| 14x426 | 50.9316
| 14x398 | 48.0483
| 14x370 | 45.1082
| 14x342 | 42.1962
| 14x311 | 38.7378
| 14x283 | 35.6199
| 14x257 | 32.673
| 14x233 | 29.9037
| 14x211 | 27.3198
| 14x193 | 25.1684
| 14x176 | 23.1123
| 14x159 | 20.9454
| 14x145 | 19.2905
| 14x132 | 18.2216
| 14x120 | 16.6551
| 14x109 | 15.2075
| 14x99 | 13.8769
| 14x90 | 12.6701
| 14x82 | 14.4451
| 14x74 | 13.1128
| 14x68 | 12.1086
| 14x61 | 10.9237
| 14x53 | 10.7179
| 14x48 | 9.7594
| 14x43 | 8.792
| 14x38 | 8.3425
| 14x34 | 7.5041
| 14x30 | 6.6593
| 14x26 | 6.5809
| 14x22 | 5.6146
| 12x336 | 48.2124
| 12x305 | 44.4552
| 12x279 | 41.2315
| 12x252 | 37.7764
| 12x230 | 34.8881
| 12x210 | 32.2168
| 12x190 | 29.4878
| 12x170 | 26.6946
| 12x152 | 24.127
| 12x136 | 21.8065
| 12x120 | 19.4332
| 12x106 | 17.3203
| 12x96 | 15.7895
| 12x87 | 14.394
| 12x79 | 13.1411
| 12x72 | 12.0334
| 12x65 | 10.9152
| 12x58 | 10.9262
| 12x53 | 10.03
| 12x50 | 10.7219
| 12x45 | 9.707
| 12x40 | 8.6784
| 12x35 | 8.2938
| 12x30 | 7.1656
| 12x26 | 6.2475
| 12x22 | 6.5639
| 12x19 | 5.7186
| 12x16 | 4.8608
| 12x14 | 4.2748
| 10x112 | 21.3774
| 10x100 | 19.2926
| 10x88 | 17.1624
| 10x77 | 15.1724
| 10x68 | 13.5144
| 10x60 | 12.016
| 10x54 | 10.8798
| 10x49 | 9.919
| 10x45 | 10.4692
| 10x39 | 9.1496
| 10x33 | 7.8076
| 10x30 | 8.2607
| 10x26 | 7.2189
| 10x22 | 6.1596
| 10x19 | 6.3228
| 10x17 | 5.7015
| 10x15 | 5.0676
| 10x12 | 4.0909
| 8x67 | 16.0864
| 8x58 | 14.1005
| 8x48 | 11.8421
| 8x40 | 9.9875
| 8x35 | 8.8028
| 8x31 | 7.8464
| 8x28 | 8.0595
| 8x24 | 6.9649
| 8x21 | 6.7851
| 8x18 | 5.8664
| 8x15 | 5.6622
| 8x13 | 4.9492
| 8x10 | 3.8462
| 6x25 | 8.2327
| 6x20 | 6.6741
| 6x15 | 5.0733
| 6x16 | 6.8182
| 6x12 | 5.2174
| 6x9 | 3.9677
| 5x19 | 7.6305
| 5x16 | 6.4997
| 4x13 | 6.5
| User Specified Value | Enter Value
Select Column
Scroll to desired column size then Click on selection
THERMAL PROPERTIES OF SPRAY-APPLIED INSULATION MATERIALS
Insulation Material |  | Density | Thermal | Specific Heat |  | Select Insulation Type
Spray-Applied |  | ρi | Conductivity ki | ci
|  | (lb/ft3) | (Btu/ft-hr-°F) | (Btu/lb-°F) |  | Scroll to desired material then Click on selection
Sprayed mineral fiber |  | 19 | 0.06936 | 0.2868
Perlite or vermiculite |  | 22 | 0.06936 | 0.2868
High density perlite or vermiculite |  | 35 | 0.06936 | 0.2868
User Specified Value |  | Enter Value | Enter Value | Enter Value
Reference: Buchanan, A. H., Structural Design for Fire Safety, 2001, Page 182.
ESTIMATING FIRE RESISTANCE TIME USING QUASI-STEADY-STATE APPROACH
Reference: "Analytical Methods for Determining Fire Resistance of Steel Members,"
"SFPE Handbook of Fire Protection Engineering, 3rd Edition, 2002, Page 4-209.
Temperature Rise in Steel Column
DTs = (ki /(cs h W/D + 1/2 ci ri h2)) (Tf - Ts) Dt
Where
DTs = temperature rise in steel (°F)
ki = thermal conductivity of spray-applied material (Btu/ft-sec-°F)
ri = density of spray-applied material (lb/ft3)
ci = specific heat of spray-applied material (Btu/lb-°F)
cs = specific heat of steel (Btu/lb-°F)
h = thickness of spray-applied protection on steel beam (in)
W/D = ratio of weight of steel section per linear foot and heated perimeter (lb/ft2)
Tf = fire exposure temperature (°F)
Ts = steel temperature (°F)
Dt = time step (sec)
cs W/D > 2 ci ri h
Where
cs = specific heat of steel (Btu/lb-°F)
W/D = ratio of weight of steel section per linear foot and heated perimeter (lb/ft2)
ri = density of spray-applied material (lb/ft3)
ci = specific heat of spray-applied material (ci)
h = thickness of spray-applied protection on steel column (in)
|  |  | 1.8168 | > | 0.53822
The Maximum Allowable Time Step
Dt = 15.9 W/D
|  |  | Dt = | 218.8445 | sec
|  |  | Dt = | 3.6474 | minutes
For ASTM-E-119 exposure, Tf at any time, t, is given by the following expression
Tf = C1 LOG (0.133 t + 1) + T0
Where
Tf = fire exposure temperature (°F)
C1 = constant = 620
t = time step (sec)
Ta = ambient air temperature (°F)
DTs1 = (ki /(cs h W/D + 1/2 ci ri h2)) ((C1 LOG (0.133 t1 + 1)+Ta) - Ts0) Dt
| Where |  |  |  |  | Caution! This equation is only valid up to 1000 °F (538 °C) where
|  | t1 = Dt/2 |  |  |  | carbon steel structural members begin to fail. Predicted
|  | Ts0 = initial steel temperature (°F) |  |  |  | temperatures above 1000 °F (538 °C) are not accurate or valid.
DTs2 = (ki /(cs h W/D + 1/2 ci ri h2)) ((C1 LOG (0.133 t2 + 1)+Ta) - Ts) Dt
Where
t2 = t1 + Dt/2
Ts = Ts0 + DTs from previous row
Answer
Time | Time | DTs | Ts |  |  | Time | Time | DTs | Ts
(min) | (sec) | (°F) | (°C) |  |  | (min) | (sec) | (°F) | (°C)
3.6474 | 218.8445 | 43.0366 | 48.9092 |  |  | 222.4919 | 13349.5157 | 106.5509 | 3222.8701 | Failure of Column
7.2948 | 437.689 | 56.1491 | 80.1032 |  |  | 226.1393 | 13568.3602 | 106.7783 | 3329.6485 | Failure of Column
10.9422 | 656.5336 | 62.7881 | 114.9855 |  |  | 229.7867 | 13787.2048 | 107.0022 | 3436.6506 | Failure of Column
14.5896 | 875.3781 | 67.2998 | 152.3743 |  |  | 233.4342 | 14006.0493 | 107.2224 | 3543.873 | Failure of Column
18.237 | 1094.2226 | 70.7047 | 191.6546 |  |  | 237.0816 | 14224.8938 | 107.4392 | 3651.3123 | Failure of Column
21.8845 | 1313.0671 | 73.4393 | 232.4543 |  |  | 240.729 | 14443.7383 | 107.6527 | 3758.965 | Failure of Column
25.5319 | 1531.9116 | 75.7241 | 274.5232 |  |  | 244.3764 | 14662.5828 | 107.863 | 3866.828 | Failure of Column
29.1793 | 1750.7562 | 77.6861 | 317.6822 |  |  | 248.0238 | 14881.4274 | 108.0701 | 3974.8981 | Failure of Column
32.8267 | 1969.6007 | 79.4053 | 361.7962 |  |  | 251.6712 | 15100.2719 | 108.2742 | 4083.1723 | Failure of Column
36.4741 | 2188.4452 | 80.9352 | 406.7602 |  |  | 255.3186 | 15319.1164 | 108.4753 | 4191.6477 | Failure of Column
40.1215 | 2407.2897 | 82.3132 | 452.4898 |  |  | 258.966 | 15537.9609 | 108.6736 | 4300.3213 | Failure of Column
43.7689 | 2626.1342 | 83.567 | 498.9158 |  |  | 262.6134 | 15756.8054 | 108.8691 | 4409.1904 | Failure of Column
47.4163 | 2844.9788 | 84.7169 | 545.9808 | Failure of Column |  | 266.2608 | 15975.65 | 109.0618 | 4518.2522 | Failure of Column
51.0637 | 3063.8233 | 85.7789 | 593.6358 | Failure of Column |  | 269.9082 | 16194.4945 | 109.252 | 4627.5042 | Failure of Column
54.7111 | 3282.6678 | 86.7655 | 641.8388 | Failure of Column |  | 273.5556 | 16413.339 | 109.4395 | 4736.9437 | Failure of Column
58.3585 | 3501.5123 | 87.6867 | 690.5537 | Failure of Column |  | 277.2031 | 16632.1835 | 109.6246 | 4846.5683 | Failure of Column
62.0059 | 3720.3568 | 88.5507 | 739.7485 | Failure of Column |  | 280.8505 | 16851.028 | 109.8072 | 4956.3755 | Failure of Column
65.6534 | 3939.2014 | 89.364 | 789.3952 | Failure of Column |  | 284.4979 | 17069.8726 | 109.9875 | 5066.3629 | Failure of Column
69.3008 | 4158.0459 | 90.1324 | 839.4687 | Failure of Column |  | 288.1453 | 17288.7171 | 110.1654 | 5176.5283 | Failure of Column
72.9482 | 4376.8904 | 90.8605 | 889.9468 | Failure of Column |  | 291.7927 | 17507.5616 | 110.3411 | 5286.8694 | Failure of Column
76.5956 | 4595.7349 | 91.5523 | 940.8092 | Failure of Column |  | 295.4401 | 17726.4061 | 110.5146 | 5397.3841 | Failure of Column
80.243 | 4814.5794 | 92.2113 | 992.0377 | Failure of Column |  | 299.0875 | 17945.2506 | 110.686 | 5508.07 | Failure of Column
83.8904 | 5033.424 | 92.8405 | 1043.6158 | Failure of Column |  | 302.7349 | 18164.0952 | 110.8553 | 5618.9253 | Failure of Column
87.5378 | 5252.2685 | 93.4425 | 1095.5282 | Failure of Column |  | 306.3823 | 18382.9397 | 111.0225 | 5729.9478 | Failure of Column
91.1852 | 5471.113 | 94.0194 | 1147.7612 | Failure of Column |  | 310.0297 | 18601.7842 | 111.1877 | 5841.1355 | Failure of Column
94.8326 | 5689.9575 | 94.5733 | 1200.302 | Failure of Column |  | 313.6771 | 18820.6287 | 111.3511 | 5952.4866 | Failure of Column
98.48 | 5908.802 | 95.106 | 1253.1387 | Failure of Column |  | 317.3246 | 19039.4732 | 111.5125 | 6063.9991 | Failure of Column
102.1274 | 6127.6466 | 95.6191 | 1306.2603 | Failure of Column |  | 320.972 | 19258.3178 | 111.672 | 6175.6711 | Failure of Column
105.7749 | 6346.4911 | 96.1138 | 1359.6569 | Failure of Column |  | 324.6194 | 19477.1623 | 111.8298 | 6287.5009 | Failure of Column
109.4223 | 6565.3356 | 96.5916 | 1413.3189 | Failure of Column |  | 328.2668 | 19696.0068 | 111.9858 | 6399.4866 | Failure of Column
113.0697 | 6784.1801 | 97.0534 | 1467.2375 | Failure of Column |  | 331.9142 | 19914.8513 | 112.14 | 6511.6266 | Failure of Column
116.7171 | 7003.0246 | 97.5004 | 1521.4044 | Failure of Column |  | 335.5616 | 20133.6958 | 112.2926 | 6623.9192 | Failure of Column
120.3645 | 7221.8692 | 97.9335 | 1575.8119 | Failure of Column |  | 339.209 | 20352.5404 | 112.4434 | 6736.3626 | Failure of Column
124.0119 | 7440.7137 | 98.3535 | 1630.4527 | Failure of Column |  | 342.8564 | 20571.3849 | 112.5927 | 6848.9554 | Failure of Column
127.6593 | 7659.5582 | 98.7612 | 1685.3201 | Failure of Column |  | 346.5038 | 20790.2294 | 112.7404 | 6961.6958 | Failure of Column
131.3067 | 7878.4027 | 99.1572 | 1740.4074 | Failure of Column |  | 350.1512 | 21009.0739 | 112.8865 | 7074.5823 | Failure of Column
134.9541 | 8097.2472 | 99.5423 | 1795.7087 | Failure of Column |  | 353.7986 | 21227.9184 | 113.0312 | 7187.6135 | Failure of Column
138.6015 | 8316.0918 | 99.917 | 1851.2181 | Failure of Column |  | 357.446 | 21446.763 | 113.1743 | 7300.7877 | Failure of Column
142.2489 | 8534.9363 | 100.2818 | 1906.9302 | Failure of Column |  | 361.0935 | 21665.6075 | 113.3159 | 7414.1037 | Failure of Column
145.8963 | 8753.7808 | 100.6373 | 1962.8399 | Failure of Column |  | 364.7409 | 21884.452 | 113.4562 | 7527.5599 | Failure of Column
149.5438 | 8972.6253 | 100.984 | 2018.9421 | Failure of Column |  | 368.3883 | 22103.2965 | 113.595 | 7641.1549 | Failure of Column
153.1912 | 9191.4698 | 101.3222 | 2075.2322 | Failure of Column |  | 372.0357 | 22322.141 | 113.7325 | 7754.8873 | Failure of Column
156.8386 | 9410.3144 | 101.6524 | 2131.7057 | Failure of Column |  | 375.6831 | 22540.9856 | 113.8686 | 7868.7559 | Failure of Column
160.486 | 9629.1589 | 101.9749 | 2188.3584 | Failure of Column |  | 379.3305 | 22759.8301 | 114.0034 | 7982.7593 | Failure of Column
164.1334 | 9848.0034 | 102.2901 | 2245.1862 | Failure of Column |  | 382.9779 | 22978.6746 | 114.1369 | 8096.8962 | Failure of Column
167.7808 | 10066.8479 | 102.5983 | 2302.1853 | Failure of Column |  | 386.6253 | 23197.5191 | 114.2691 | 8211.1653 | Failure of Column
171.4282 | 10285.6924 | 102.8998 | 2359.3518 | Failure of Column |  | 390.2727 | 23416.3636 | 114.4001 | 8325.5654 | Failure of Column
175.0756 | 10504.537 | 103.1949 | 2416.6823 | Failure of Column |  | 393.9201 | 23635.2082 | 114.5298 | 8440.0952 | Failure of Column
178.723 | 10723.3815 | 103.4838 | 2474.1733 | Failure of Column |  | 397.5675 | 23854.0527 | 114.6584 | 8554.7536 | Failure of Column
182.3704 | 10942.226 | 103.7669 | 2531.8216 | Failure of Column |  | 401.215 | 24072.8972 | 114.7858 | 8669.5394 | Failure of Column
186.0178 | 11161.0705 | 104.0444 | 2589.624 | Failure of Column |  | 404.8624 | 24291.7417 | 114.912 | 8784.4514 | Failure of Column
189.6653 | 11379.915 | 104.3164 | 2647.5776 | Failure of Column |  | 408.5098 | 24510.5862 | 115.0371 | 8899.4885 | Failure of Column
193.3127 | 11598.7596 | 104.5831 | 2705.6793 | Failure of Column |  | 412.1572 | 24729.4308 | 115.1611 | 9014.6496 | Failure of Column
196.9601 | 11817.6041 | 104.8449 | 2763.9265 | Failure of Column |  | 415.8046 | 24948.2753 | 115.2839 | 9129.9335 | Failure of Column
200.6075 | 12036.4486 | 105.1018 | 2822.3164 | Failure of Column |  | 419.452 | 25167.1198 | 115.4057 | 9245.3392 | Failure of Column
204.2549 | 12255.2931 | 105.3541 | 2880.8464 | Failure of Column |  | 423.0994 | 25385.9643 | 115.5265 | 9360.8657 | Failure of Column
207.9023 | 12474.1376 | 105.6018 | 2939.5141 | Failure of Column |  | 426.7468 | 25604.8088 | 115.6462 | 9476.5119 | Failure of Column
211.5497 | 12692.9822 | 105.8452 | 2998.317 | Failure of Column |  | 430.3942 | 25823.6534 | 115.7648 | 9592.2767 | Failure of Column
215.1971 | 12911.8267 | 106.0844 | 3057.2528 | Failure of Column |  | 434.0416 | 26042.4979 | 115.8825 | 9708.1592 | Failure of Column
218.8445 | 13130.6712 | 106.3196 | 3116.3192 | Failure of Column |  | 437.689 | 26261.3424 | 115.9992 | 9824.1584 | Failure of Column
The Failure Temperature for Steel Columns is Assumed at 1000 °F (538 °C)
NOTE:
The above calculations are based on principles developed in the SFPE Handbook of Fire Protection Engineering, 3rd Edition, 2002. Calculations are based on certain assumptions and have inherent limitations. The results of such calculations may or may not have reasonable predictive capabilities for a given situation and should only be interpreted by an informed user. Although each calculation in the spreadsheet has been verified with the results of hand calculation, there is no absolute guarantee of the accuracy of these calculations. Any questions, comments, concerns and suggestions or to report an error(s) in the spreadsheets, please send an email to David.Stroup@nrc.gov or Naeem.Iqbal@nrc.gov.
Prepared by: |  |  |  | Date: |  | Organization:
Checked by: |  |  |  | Date: |  | Organization:
Additional Information:
Revision Log | Description of Revision |  |  |  |  | Date
1805.0 | Original issue with final text. |  |  |  |  | December 2004
1805.1 | Revised e-mail addresses, corrected editorial errors, revised print pagination |  |  |  |  | March 2011
and print layout.
Note on I27: This default value (0.132) is the most appropriate value for the majority of analyses. You may change this value for your specific application. If you change this value please ensure that it is appropriate.

## Data
SECTIONAL FACTORS FOR STEEL MEMBERS
| BEAMS |  | COLUMNS
| Structural Shape | W/D Ratio | Structural Shape | W/D Ratio
| W Shapes | (lb/ft2) | W Shapes | (lb/ft2)
| 36x300 | 29.6162 | 36x300 | 26.0473
| 36x280 | 27.756 | 36x280 | 24.4097
| 36x260 | 25.8943 | 36x260 | 22.7671
| 36x245 | 24.4816 | 36x245 | 21.5227
| 36x230 | 23.0596 | 36x230 | 20.2703
| 36x210 | 23.2773 | 36x210 | 20.9233
| 36x194 | 21.5965 | 36x194 | 19.4146
| 36x182 | 20.3286 | 36x182 | 18.2746
| 36x170 | 19.053 | 36x170 | 17.1285
| 36x160 | 17.991 | 36x160 | 16.1725
| 36x150 | 16.9213 | 36x150 | 15.2091
| 36x135 | 15.3191 | 36x135 | 13.7638
| 33x241 | 25.3063 | 33x241 | 22.2222
| 33x221 | 23.3194 | 33x221 | 20.474
| 33x201 | 21.314 | 33x201 | 18.7107
| 33x152 | 18.1664 | 33x152 | 16.2901
| 33x141 | 16.9208 | 33x141 | 15.1708
| 33x130 | 15.6705 | 33x130 | 14.0465
| 33x118 | 14.2944 | 33x118 | 12.8098
| 30x211 | 23.9671 | 30x211 | 20.9689
| 30x191 | 21.8161 | 30x191 | 19.0841
| 30x173 | 19.8613 | 30x173 | 17.3709
| 30x132 | 17.4018 | 30x132 | 15.5952
| 30x124 | 16.403 | 30x124 | 14.6992
| 30x116 | 15.4025 | 30x116 | 13.7999
| 30x108 | 14.4008 | 30x108 | 12.8994
| 30x99 | 13.2574 | 30x99 | 11.8729
| 27x178 | 22.1519 | 27x178 | 19.3286
| 27x161 | 20.1418 | 27x161 | 17.5732
| 27x146 | 18.3561 | 27x146 | 16.0132
| 27x114 | 16.3539 | 27x114 | 14.5967
| 27x102 | 14.7124 | 27x102 | 13.1316
| 27x94 | 13.6183 | 27x94 | 12.1526
| 27x84 | 12.236 | 27x84 | 10.9162
| 24x162 | 22.2286 | 24x162 | 19.3606
| 24x146 | 20.1657 | 24x146 | 17.5586
| 24x131 | 18.2124 | 24x131 | 15.8516
| 24x117 | 16.3598 | 24x117 | 14.2365
| 24x104 | 14.6187 | 24x104 | 12.7191
| 24x94 | 15.0832 | 24x94 | 13.4526
| 24x84 | 13.563 | 24x84 | 12.095
| 24x76 | 12.336 | 24x76 | 10.9986
| 24x68 | 11.0983 | 24x68 | 9.8921
| 24x62 | 10.9832 | 24x62 | 9.9492
| 24x55 | 9.7974 | 24x55 | 8.8745
| 21x147 | 21.9923 | 21x147 | 19.025
| 21x132 | 19.8795 | 21x132 | 17.195
| 21x122 | 18.4546 | 21x122 | 15.9616
| 21x111 | 16.8736 | 21x111 | 14.5925
| 21x101 | 15.4218 | 21x101 | 13.3363
| 21x93 | 16.5726 | 21x93 | 14.7307
| 21x83 | 14.889 | 21x83 | 13.2359
| 21x73 | 13.1819 | 21x73 | 11.7191
| 21x68 | 12.3244 | 21x68 | 10.956
| 21x62 | 11.2898 | 21x62 | 10.0351
| 21x57 | 11.2205 | 21x57 | 10.1318
| 21x50 | 9.919 | 21x50 | 8.9526
| 21x44 | 8.7824 | 21x44 | 7.9255
| 18x119 | 20.2769 | 18x119 | 17.4807
| 18x106 | 18.2026 | 18x106 | 15.6882
| 18x97 | 16.7374 | 18x97 | 14.4256
| 18x86 | 14.937 | 18x86 | 12.871
| 18x76 | 13.2799 | 18x76 | 11.4415
| 18x71 | 14.4763 | 18x71 | 12.814
| 18x65 | 13.3174 | 18x65 | 11.7896
| 18x60 | 12.3499 | 18x60 | 10.9339
| 18x55 | 11.3734 | 18x55 | 10.0671
| 18x50 | 10.3887 | 18x50 | 9.1954
| 18x46 | 10.3024 | 18x46 | 9.2555
| 18x40 | 9.02 | 18x40 | 8.104
| 18x35 | 7.9545 | 18x35 | 7.1429
| 16x100 | 18.7368 | 16x100 | 16.1139
| 16x89 | 16.807 | 16x89 | 14.45
| 16x77 | 14.6632 | 16x77 | 12.604
| 16x67 | 12.8486 | 16x67 | 11.0424
| 16x57 | 12.8186 | 16x57 | 11.3095
| 16x50 | 11.3272 | 16x50 | 9.9933
| 16x45 | 10.2515 | 16x45 | 9.0437
| 16x40 | 9.1612 | 16x40 | 8.0822
| 16x36 | 8.2941 | 16x36 | 7.3134
| 16x31 | 7.7849 | 16x31 | 6.9781
| 16x26 | 6.5851 | 16x26 | 5.9002
| 14x730 | 94.836 | 14x730 | 79.4486
| 14x665 | 88.1086 | 14x665 | 73.7387
| 14x605 | 81.6694 | 14x605 | 68.2908
| 14x550 | 75.5841 | 14x550 | 63.1458
| 14x500 | 69.8893 | 14x500 | 58.3317
| 14x455 | 64.6039 | 14x455 | 53.8727
| 14x426 | 61.0935 | 14x426 | 50.9316
| 14x398 | 57.6742 | 14x398 | 48.0483
| 14x370 | 54.1761 | 14x370 | 45.1082
| 14x342 | 50.7293 | 14x342 | 42.1962
| 14x311 | 46.5859 | 14x311 | 38.7378
| 14x283 | 42.8626 | 14x283 | 35.6199
| 14x257 | 39.3392 | 14x257 | 32.673
| 14x233 | 36.0263 | 14x233 | 29.9037
| 14x211 | 32.9344 | 14x211 | 27.3198
| 14x193 | 30.3499 | 14x193 | 25.1684
| 14x176 | 27.8886 | 14x176 | 23.1123
| 14x159 | 25.2923 | 14x159 | 20.9454
| 14x145 | 23.2932 | 14x145 | 19.2905
| 14x132 | 21.9375 | 14x132 | 18.2216
| 14x120 | 20.0585 | 14x120 | 16.6551
| 14x109 | 18.318 | 14x109 | 15.2075
| 14x99 | 16.7218 | 14x99 | 13.8769
| 14x90 | 15.2715 | 14x90 | 12.6701
| 14x82 | 16.9684 | 14x82 | 14.4451
| 14x74 | 15.4033 | 14x74 | 13.1128
| 14x68 | 14.2272 | 14x68 | 12.1086
| 14x61 | 12.8387 | 14x61 | 10.9237
| 14x53 | 12.4025 | 14x53 | 10.7179
| 14x48 | 11.2963 | 14x48 | 9.7594
| 14x43 | 10.1785 | 14x43 | 8.792
| 14x38 | 9.5218 | 14x38 | 8.3425
| 14x34 | 8.5669 | 14x34 | 7.5041
| 14x30 | 7.6062 | 14x30 | 6.6593
| 14x26 | 7.3611 | 14x26 | 6.5809
| 14x22 | 6.2827 | 14x22 | 5.6146
| 12x336 | 57.3991 | 12x336 | 48.2124
| 12x305 | 52.9705 | 12x305 | 44.4552
| 12x279 | 49.1919 | 12x279 | 41.2315
| 12x252 | 45.104 | 12x252 | 37.7764
| 12x230 | 41.6824 | 12x230 | 34.8881
| 12x210 | 38.5144 | 12x210 | 32.2168
| 12x190 | 35.2668 | 12x190 | 29.4878
| 12x170 | 31.9499 | 12x170 | 26.6946
| 12x152 | 28.8973 | 12x152 | 24.127
| 12x136 | 26.1371 | 12x136 | 21.8065
| 12x120 | 23.3085 | 12x120 | 19.4332
| 12x106 | 20.7775 | 12x106 | 17.3203
| 12x96 | 18.9474 | 12x96 | 15.7895
| 12x87 | 17.2833 | 12x87 | 14.394
| 12x79 | 15.7842 | 12x79 | 13.1411
| 12x72 | 14.4578 | 12x72 | 12.0334
| 12x65 | 13.1181 | 12x65 | 10.9152
| 12x58 | 12.9633 | 12x58 | 10.9262
| 12x53 | 11.9068 | 12x53 | 10.03
| 12x50 | 12.5313 | 12x50 | 10.7219
| 12x45 | 11.3481 | 12x45 | 9.707
| 12x40 | 10.1469 | 12x40 | 8.6784
| 12x35 | 9.5281 | 12x35 | 8.2938
| 12x30 | 8.2342 | 12x30 | 7.1656
| 12x26 | 7.1807 | 12x26 | 6.2475
| 12x22 | 7.2948 | 12x22 | 6.5639
| 12x19 | 6.3572 | 12x19 | 5.7186
| 12x16 | 5.4069 | 12x16 | 4.8608
| 12x14 | 4.7552 | 12x14 | 4.2748
| 10x112 | 25.622 | 10x112 | 21.3774
| 10x100 | 23.1392 | 10x100 | 19.2926
| 10x88 | 20.5988 | 10x88 | 17.1624
| 10x77 | 18.2213 | 10x77 | 15.1724
| 10x68 | 16.2388 | 10x68 | 13.5144
| 10x60 | 14.4462 | 10x60 | 12.016
| 10x54 | 13.083 | 10x54 | 10.8798
| 10x49 | 11.9318 | 10x49 | 9.919
| 10x45 | 12.3967 | 10x45 | 10.4692
| 10x39 | 10.8421 | 10x39 | 9.1496
| 10x33 | 9.261 | 10x33 | 7.8076
| 10x30 | 9.5314 | 10x30 | 8.2607
| 10x26 | 8.3311 | 10x26 | 7.2189
| 10x22 | 7.114 | 10x22 | 6.1596
| 10x19 | 7.1161 | 10x19 | 6.3228
| 10x17 | 6.4212 | 10x17 | 5.7015
| 10x15 | 5.7107 | 10x15 | 5.0676
| 10x12 | 4.6095 | 10x12 | 4.0909
| 8x67 | 19.2806 | 8x67 | 16.0864
| 8x58 | 16.9178 | 8x58 | 14.1005
| 8x48 | 14.2117 | 8x48 | 11.8421
| 8x40 | 12.003 | 8x40 | 9.9875
| 8x35 | 10.5823 | 8x35 | 8.8028
| 8x31 | 9.438 | 8x31 | 7.8464
| 8x28 | 9.5577 | 8x28 | 8.0595
| 8x24 | 8.2628 | 8x24 | 6.9649
| 8x21 | 7.9071 | 8x21 | 6.7851
| 8x18 | 6.8419 | 8x18 | 5.8664
| 8x15 | 6.4806 | 8x15 | 5.6622
| 8x13 | 5.6686 | 8x13 | 4.9492
| 8x10 | 4.4021 | 8x10 | 3.8462
| 6x25 | 9.8814 | 6x25 | 8.2327
| 6x20 | 8.016 | 6x20 | 6.6741
| 6x15 | 6.1038 | 6x15 | 5.0733
| 6x16 | 7.9569 | 6x16 | 6.8182
| 6x12 | 6.1017 | 6x12 | 5.2174
| 6x9 | 4.6392 | 6x9 | 3.9677
| 5x19 | 9.1751 | 5x19 | 7.6305
| 5x16 | 7.824 | 5x16 | 6.4997
| 4x13 | 7.82 | 4x13 | 6.5
| User Specified Value | Enter Value | User Specified Value | Enter Value