## Sheet1
NRC Significant Enforcement Actions
Action Number |  | Type | Issue Date | Summary
EA-12-152 | Wolf Creek Nuclear Operating Corporation (Wolf Creek) | Reactor | 2012-09-21 | On September 21, 2012, the NRC issued a Notice of Violation to Wolf Creek Nuclear Operating Corporation (Wolf Creek) for a violation of Technical Specification 5.4.1(a) and Regulatory Guide 1.33, Appendix A, Section 9.a, associated with a Yellow Significance Determination Process finding. The finding involved Wolf Creek’s failure to implement maintenance that affected safety-related equipment in accordance with written procedures. Specifically, although required by a work order, Wolf Creek failed to install insulating sleeves on two splices associated with a startup transformer protective relay circuit. The startup transformer subsequently experienced a trip and lockout during a plant trip because the two uninsulated wires touched and provided a false high phase differential signal to the protective relaying circuit. The protective lockout caused prolonged loss of offsite power to all Train B equipment and all non-safety related buses.
EA-12-133 | Tennessee Valley Authority (Browns Ferry Nuclear Plant) | Reactor | 2012-08-13 | On August 13, 2012, the NRC issued a Notice of Violation to Tennessee Valley Authority (TVA) for a violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," associated with a White Significance Determination Process finding involving TVA’s failure to accomplish the requirements contained in procedure NPG-SPP-09.3 “Plant Modifications and Engineering Change Control,” which required that an evaluation of training needs be completed to support implementation of procedures developed in response to design changes. Specifically, on September 13, 2011, TVA issued several Safe Shutdown Instructions in support of Design Change Notice 69957, which installed a new three-hour fire barrier in the Intake Tunnel Structure, without performing an evaluation of training needs. As a result, the Safe Shutdown Instructions could not be satisfactorily performed by plant operators and staff.
EA-12-093 | NextEra Energy Seaboork, LLC (Seabrook Station) | Reactor | 2012-08-07 | On August 7, 2012, the NRC issued a Notice of Violation to NextEra Energy Seabrook, LLC. (Seabrook) for a violation of 10 CFR 50.54(q)(2), associated with a White Significance Determination Process finding involving Seabrook’s failure to identify an performance weakness during the post-exercise critique. Specifically, Seabrook did not identify as a weakness that an incorrect initial Protective Action Recommendation (PAR) had been developed and communicated to the state response organizations. The initial PAR was incorrect for the exercise actual condition (i.e., no release in progress).
EA-12-106 | NextEra Energy Seaboork, LLC (Point Beach Nuclear Plant, Units 1 and 2) | Reactor | 2012-07-24 | On July 24, 2012, the NRC issued a Notice of Violation to NextEra Energy Point Beach, LLC for a violation of 10 CFR 50.47(b)(10) associated with a White Significance Determination Process finding involving the failure of Point Beach personnel to develop and have in place guidelines for the choice of protective actions during an emergency that were consistent with Federal guidance. Specifically, an apparent logic error in a Point Beach emergency planning implementing procedure required the emergency director to revisit the question of impediments to evacuation after a prior decision to evacuate affected downwind sectors had been implemented by local authorities, resulting in a contradictory recommendation for sheltering being given during an exercise.
EA-12-021 | Tennessee Valley Authority Watts Bar, Unit 2 | Reactor | 2012-06-18 | On June 18, 2012, the NRC issued a Confirmatory Order (Effective Immediately) to Tennessee Valley Authority (TVA) to formalize commitments made as a result of an ADR mediation session. The commitments were made by TVA as part of a settlement agreement between TVA and the NRC regarding an apparent violation of NRC requirements by TVA. The agreement resolves the apparent violation involving two subcontractor employees at Watts Bar Unit 2 who deliberately falsified work order packages for primary containment penetrations which caused TVA to be in apparent violation of 10 CFR Part 50, Appendix B, Criterion V, Instructions, Procedures and Drawings, and 10 CFR 50.9, Completeness and Accuracy of Information, which was identified during an NRC Office of Investigations (OI) investigation. TVA agreed to a number of corrective actions as part of this Confirmatory Order, including but not limited to: (1) a prompt cessation of all containment electrical penetration work activities and the initiation of an internal review of the incident; (2) a root cause and extent of condition review; (3) procedural revisions and training related to the importance of 10 CFR 50.9 and procedural compliance; and (4) various site specific (Watts Bar Unit 2) and fleet wide communications which discuss expectations for assuring work activities are performed and documented in a complete and accurate manner. In consideration of these corrective actions and commitments, the NRC agreed to refrain from proposing a civil penalty and issuing a Notice of Violation or other enforcement action in this matter.
EA-12-071 | Tennessee Valley Authority Browns Ferry Nuclear Plant | Reactor | 2012-05-18 | On May 18, 2012, an immediately effective Confirmatory Order was issued to the Tennessee Valley Authority (TVA), confirming TVA’s commitment to submit a license amendment request to transition the three units at the Browns Ferry plant to the National Fire Protection Association Standard 805. TVA had originally planned to submit its application to transition Browns Ferry on March 4, 2012. However, TVA requested a delay to ensure it could submit a high-quality application. Based on TVA’s commitment to maintain acceptable compensatory measures, and a review of TVA’s status and planned key activities, including the intended NFPA 805 modifications, the NRC determined that TVA provided adequate justification for its commitment to submit a license application by March 29, 2013. The NRC has therefore extended TVA’s enforcement discretion until March 29, 2013.
EA-12-033 | Virginia Electric and Power Company (North Anna Power Station, Units 1 & 2) | Reactor | 2012-05-12 | On May 10, 2012, the NRC issued a Notice of Violation to Virginia Electric and Power Company for a violation of Technical Specification 5.4.1.a, “Procedures,” associated with a White Significance Determination Process finding involving Virginia Electric and Power Company’s failure to establish and maintain maintenance procedures appropriate to the circumstances for the safety-related emergency diesel generators (EDGs). Specifically, maintenance procedure 0-MCM-0701-27 did not provide adequate guidance for installation of the jacket water cooling inlet jumper gasket, which resulted in a faulty gasket installation on the Unit 2 “H” (2H) EDG in May 2010. As a result, the 2H EDG failed to perform its safety function when called upon on August 23, 2011.
EA-12-075 | Pacific Gas and Electric Company (Diablo Canyon Power Plant) | Reactor | 2012-05-04 | On May 4, 2012, the NRC issued a Notice of Violation to Pacific Gas and Electric Company (PG&E) for a violation of 10 CFR 50.9, “Completeness and Accuracy of Information,” associated with a Severity Level III violation involving PG&E’s failure to provide information to the Commission that was complete and accurate in all material respects, related to its NRC Generic Letter 2003-01 response. Specifically, in a letter dated April 22, 2005, PG&E stated that: (1) test results confirmed that no unfiltered control room in-leakage existed; and (2) tracer gas in-leakage testing was performed in the alignment that results in the greatest consequence to the control room operator. This information was inaccurate because control room ventilation testing conducted prior to PG&E’s response to Generic Letter 2003-01 indicated that the unfiltered in-leakage was greater than the value assumed in the design basis radiological analyses, and the system test was not performed in an alignment that resulted in the greatest consequence to the control room operator.
EA-12-023 | Omaha Public Power District (Fort Calhoun Station) | Reactor | 2012-04-10 | On April 10, 2012, the NRC issued a Red Significance Determination Process finding and a Notice of Violations for three violations to Omaha Public Power District as a result of inspections at the Fort Calhoun Station. The Red finding was based on deficient modification and maintenance of the safety-related 480 Vac electrical distribution system that resulted in a catastrophic switchgear fire. There were three violations associated with the Red finding: (1) 10 CFR Part 50, Appendix B, Criterion III, “Design Control” associated with modifications to safety-related breakers, (2) 10 CFR Part 50, Appendix B, Criterion XVI, “Corrective Action” associated with inadequate electrical maintenance, and (3) License Condition 3.D, “Fire Protection Program” associated with train separation. At the time of the event the plant was in cold shutdown for a planned refueling outage.
EA-12-001 | Florida Power and Light (Turkey Point Nuclear Plant, Units 3 & 4) | Reactor | 2012-04-09 | On April 9, 2012, the NRC issued a Notice of Violation associated with a White Significance Determination Process (SDP) finding and a Severity Level III violation with a Proposed Imposition of Civil Penalty in the amount of $140,000 to Florida Power and Light Company (FPL). The White Finding was issued for the failure of Turkey Point personnel to maintain the effectiveness of their emergency plan, as required by 10 CFR 50.54(q) and 10 CFR 50.47(b), and the Severity Level III violation and Civil Penalty were issued for FPL’s failure to make an eight hour report, as required by 10 CFR 50.72(b)(3)(xiii). Specifically, from December 4, 2010, to July 13, 2011, and from October 10 to October 28, 2011, FPL failed to follow and maintain the effectiveness of its emergency plan when portions of the Technical Support Center (TSC) ventilation system were removed from service for maintenance, without compensatory measures. FPL failed to report this condition as required from December 4, 2010, to July 13, 2011.
EA-11-243 | Entergy Nuclear Operations, Inc. (Palisades Nuclear Plant) | Reactor | 2012-02-14 | On February 14, 2012, the NRC issued a Notice of Violation to Palisades Nuclear Plant for a violation of 10 CFR Part 50, Appendix B, Criterion V “Instructions, Procedures, and Drawings” that was categorized as a Yellow Significance Determination Process finding. The licensee failed to ensure that the work performed on Electrical Bus D11-2 was prescribed by documented instructions or procedures of a type appropriate to the circumstances and accomplished in accordance with the instructions or procedures. Specifically, on September 25, 2011, the work order instructions did not provide critical steps and also lacked proper step progression. The work order instructions also included action steps to, “Insulate or support load side bus bars to ensure they do not fault,” which were not implemented. Finally, the electricians performing work in the field attempted to remove a positive horizontal bus bar in Bus D11-2, which was not a prescribed step in the work order instructions. As a result, these performance deficiencies caused an electrical fault which caused the loss of the left train 125-Volt DC safety-related system and loss of both preferred AC sources associated with the left train DC system.
EA-11-241 | Entergy Nuclear Operations, Inc. (Palisades Nuclear Plant) | Reactor | 2012-02-14 | On February 14, 2012, the NRC issued a Notice of Violation to Palisades Nuclear Plant for violations of 10 CFR Part 50, Appendix B, Criterion III “Design Control” and Criterion XVI “Corrective Action” that were categorized as one White Significance Determination Process finding. Specifically, in December 2007, the licensee failed to verify the adequacy of the safety related service water pump (SWP) coupling design to confirm that the coupling material was adequate for the environment and working conditions for which it would be subjected. As a result, the licensee failed to identify and evaluate a new failure mechanism which was introduced into the system in the form of intergranular stress corrosion cracking (IGSCC). In addition, on August 9, 2011, the licensee failed to preclude repetition of a significant condition adverse to quality when a coupling on a SWP failed due to IGSCC.
EA-10-090 EA-10-248 EA-11-106 | Entergy Nuclear Operations, Inc. (James A. FitzPatrick Nuclear Power Plant) | Reactor | 2012-01-26 | On January 26, 2012, the NRC issued a Confirmatory Order (Effective Immediately) to Entergy Nuclear Operations, Inc (licensee). to confirm commitments made as a result of an ADR mediation session held on November, 9, 2011. During three investigations, the NRC discovered information associated with violations, the majority of which were willful, related to the adherence to site procedures related to radiation protection (RP). Specifically, technicians willfully failed to (1) test required individuals for respirator fit, as required by 10 CFR 20.1703; (2) maintain accurate documentation of completed respirator fit tests, as required by 10 CFR 50.9; (3) perform and/or accurately document independent verification of Drywell Continuous Atmospheric Monitoring System (DWCAM) valve positions after the valves were manipulated, as required by technical specifications (TS) and 10 CFR 50.9; (4) document a personal contamination event as required by TS; (5) perform a contamination survey prior to removing an item from a radiologically controlled area, as required by TS; and (6) perform daily radiological surveys of the reactor building 326 foot elevation airlock, as required by 10 CFR 20.1501(a). Entergy agreed to take a number of actions as part of this Confirmatory Order, including but not limited to: (1) committing to maintain the safety culture monitoring processes as described in NEI 09-07 “Fostering a Strong Nuclear Safety Culture,” or similar processes; (2) assessing Entergy’s procedure for implementing the safety culture processes described in the NEI guidance to determine if potential enhancements should be provided to NEI that would improve licensees’ ability to detect weaknesses in safety culture (if such enhancements could have prevented such violations as were the subject of this action); (3) conducting an assessment of the RP departments at each Entergy nuclear power plant to ensure activities are being conducted in accordance with NRC regulations; (4) preparing and presenting case studies at each Entergy nuclear power plant; and (5) delivering a presentation to industry representatives in each NRC geographical region which will discuss these events, including lessons learned and corrective actions. In addition, Entergy took several corrective actions prior to the ADR mediation session. In recognition of Entergy’s proposed extensive corrective actions, in addition to corrective actions already taken, the NRC issued a Notice of Violation, associated with the violations discussed above, with no civil penalty assessed.
EA-11-214 | Entergy Nuclear Operations, Inc. (Palisades Nuclear Plant) | Reactor | 2012-01-25 | On January 25, 2012, an immediately effective Confirmatory Order was issued to Entergy Nuclear Operations, Inc. (Entergy), to confirm commitments made as a result of an Alternative Dispute Resolution (ADR) mediation session held on December 12, 2011. This enforcement action is based on a Technical Specification apparent violation. An at-the-controls reactor operator left the at-the-controls area of the Control Room without providing a turnover to a qualified individual and without obtaining permission from the Control Room Supervisor. Although the operator left the Control Room, another qualified individual resumed the at-the-controls responsibility. During the ADR session, Entergy agreed to take the following actions: 1) development of a case study as related to the events that gave rise to the Confirmatory Order and present it to Entergy licensed reactor operators fleet wide, 2) a senior Entergy nuclear executive will send a letter fleet wide to each Entergy licensed reactor operator re-emphasizing the responsibilities of their position and associated safety responsibilities and obligations to the public, 3) a presentation at the appropriate industry forum(s) based on the facts and lessons learned from this event, 4) a review of the three Entergy procedures that are applicable to this event and address any relevant observations, findings, or recommendations in their Corrective Action Program, 5) conduct a safety culture assessment of the Palisades Operations Department, 6) perform a review of the planning for the next refueling outage, focusing on stressful or complex work evolutions to ensure that they are properly planned, and 7) inform the NRC, in writing, their plan to monitor and manage the reactor operator associated with event. In consideration of these commitments, and other corrective actions already completed by Entergy, the NRC agreed to refrain from proposing a civil penalty and issuing a Notice of Violation.
EA-11-252 | Tennessee Valley Authority (Browns Ferry Nuclear Plant) | Reactor | 2012-01-23 | On January 23, 2012, the NRC issued a Notice of Violation to Tennessee Valley Authority (TVA) for a violation of 10 CFR 50.9, “Completeness and Accuracy of Information,” associated with a Severity Level III violation involving TVA’s failure to provide information to the Commission that was complete and accurate in all material respects, related to its NRC Generic Letter 89-10, “Safety-Related Motor-Operated Valve Testing and Surveillance” testing program. Specifically, in a letter dated January 6, 1997, TVA stated that “Closure of valves FCV-74-52 and FCV-74-66 is not required by plant procedures to operate the residual heat removal (RHR) system in the suppression pool cooling mode. Therefore, these valves have no ‘redundant’ safety function and will not be included in the GL 89-10 program.” In a letter dated May 5, 2004, TVA stated that valves FCV-74-52 and FCV-74-66, “are not in the GL 89-10 program, since the valves are normally in their safety position.” This information was inaccurate because the FCV-74-52 and FCV-74-66 valves do have a safety function to shut to operate the RHR system in the suppression pool cooling mode and should therefore have been included in Browns Ferry’s GL 89-10 MOV monitoring program.
EA-11-159 | Entergy Operations, Inc. (River Bend Station) | Reactor | 2012-01-05 | On January 5, 2012, the NRC issued a Notice of Violation and Proposed Civil Penalty in the amount of $140,000 to Entergy Operations, Inc. (Entergy) for a Severity Level III violation as a result of an investigation at the River Bend Station. An investigation conducted by the NRC Office of Investigations determined that on multiple occasions multiple reactor operators willfully failed to follow an Entergy procedure that prohibited internet access in the “At-the-Controls” area of the control room, except as specifically authorized by the Operations Manager. These reactor operators put Entergy in violation of the River Bend Station Technical Specifications.
EA-11-227 | Entergy Nuclear Operations, Inc. (Palisades Nuclear Plant) | Reactor | 2012-01-03 | On January 3, 2012, the NRC issued a Notice of Violation to Entergy Nuclear Operations, Inc. for a violation of Title 10 of the Code of Federal Regulations, Part 50, Appendix B, Criterion V, “Instructions, Procedures, and Drawings,” associated with a White Significance Determination Process finding involving Entergy’s failure to prescribe maintenance on the safety-related turbine driven auxiliary feedwater pump, an activity affecting quality, by documented instructions of a type appropriate to the circumstances, as well as a failure to accomplish the maintenance in accordance with their procedure. Specifically, on October 17, 2010, procedure FWS-M-6, “Auxiliary Feedwater Turbine Maintenance,” failed to prescribe inspections of wear conditions on the knife edge and latch plate, or to replace the trip spring, although these inspections and replacements had been identified as necessary by the turbine vendor. Palisades’ personnel also failed to perform a step in the surveillance procedure which required lubricating a pin and instead greased the knife edge of the mechanical overspeed/manual trip mechanism. These deficiencies resulted in the turbine driven auxiliary feedwater pump being inoperable from October 29, 2010 to May 11, 2011.
EA-11-251 | Carolina Power and Light Company (Brunswick Steam Electric Plant, Units 1 and 2) | Reactor | 2011-12-27 | On December 27, 2011, the NRC issued a Notice of Violation to Carolina Power and Light Company for a violation of Title 10 of the Code of Federal Regulations, Part 50, Appendix B, Criterion XVI, “Corrective Action,” associated with a White Significance Determination Process finding involving the failure of Brunswick personnel to promptly identify and correct a condition adverse to quality involving the external flood barrier for the emergency diesel generator fuel oil tank rooms as of April 20, 2011. Specifically, the entrance enclosures which house the emergency diesel generator fuel oil tanks had several openings, unsealed pinholes, and a narrow gap along the perimeter of the base walls, which would allow water intrusion into the emergency diesel generator fuel oil tank rooms during a design basis external event (hurricane).
EA-11-208 | Progress Energy (Crystal River Nuclear Plant, Unit 3) | Reactor | 2011-12-20 | On December 20, 2011, the NRC issued a Notice of Violation to Progress Energy for a violation of 10 CFR 50.54(q) associated with a White Significance Determination Process finding involving the failure of Crystal River personnel to maintain in effect a standard emergency classification scheme which included facility effluent parameters. Specifically, for several years prior to June 2011, the General Emergency classification contained effluent radiation monitors threshold values greater than that which the instruments could accurately measure. During an actual emergency, these monitors would have been relied upon to determine initial offsite response measures, to assess the impact of the release of radioactive materials, and to provide criteria for determining the need for notification and participation of local and State agencies.
EA-11-221 | Exelon Generation Company, LLC (Limerick Generating Station) | Reactor | 2011-12-08 | On December 8, 2011, the NRC issued a White Significance Determination Process finding and a Notice of Violations for two violations to Exelon Generation Company, LLC. as a result of inspections at the Limerick Generating Station, Unit 2. The White finding was based on the failure to ensure that sufficient technical guidance was contained in an operating procedure. This failure resulted in two valves failing to fully shut, which rendered two reactor systems inoperable for greater than the Technical Specification allowed outage time. The two violations are based on the Licensee’s failure to: 1) establish adequate procedures; and, 2) exceeding Technical Specifications for two reactor systems.
EA-11-226 | Duke Energy Carolinas, LLC (Oconee Nuclear Station, Units 1 and 2) | Reactor | 2011-12-06 | On December 6, 2011, the NRC issued a Notice of Violation to Duke Energy Carolinas, LLC for a violation of Title 10 of the Code of Federal Regulations, Part 50, Appendix B, Criterion III, “Design Control,” associated with a Yellow Significance Determination Process finding involving Duke Energy’s failure to perform a review for suitability of application of equipment essential to safety-related functions of structures, systems, and components. Specifically, Oconee personnel failed to maintain the Standby Shutdown Facility pressurizer heater breakers and associated electrical components in accordance with the licensing and design basis of the plant, which resulted in the Standby Shutdown Facility being inoperable from 1983, until June 1, 2011.
EA-11-174 | Entergy Nuclear Operations, Inc. (Pilgrim Nuclear Power Station) | Reactor | 2011-11-21 | On November 21, 2011, the NRC issued a Notice of Violation to Entergy Nuclear Operations, Inc. for a violation of Technical Specification 5.4, “Procedures,” associated with a White Significance Determination Process finding involving multiple examples of Entergy’s failure to conduct safety-related activities as described in written procedures prior to and during a reactor startup operation. Specifically, on May 10, 2011, Pilgrim personnel failed to implement conduct of operations and reactivity control standards and procedures during a reactor startup which resulted in a reactor scram.
EA-11-142 | Entergy Operations, Inc. (Waterford Steam Electric Station) | Reactor | 2011-11-17 | On November 17, 2011, the NRC issued a White finding to Entergy Operations, Inc. as a result of inspections at the Waterford Steam Electric Station Unit 3. The White finding involved the failure to use effective engineering controls to prevent leakage from reactor coolant pump seals to surrounding areas. This failure resulted in high levels of contamination which caused unexpected and unintended radiation doses to plant workers during outage activities. There were no NRC violations associated with the finding.
EA-11-148 | First Energy Nuclear Operating Company (Perry Nuclear Power Plant) | Reactor | 2011-08-25 | On August 25, 2011, the NRC issued a Notice of Violation to First Energy Nuclear Operating Company for three violations associated with a White Significance Determination Process finding involving work activity during the retraction of a stuck source range monitor (SRM) from the reactor vessel. The first violation involved the failure to perform an evaluation of the potential radiological hazards associated with the work activity, as required by 10 CFR 20.1501. The second violation involved the failure to perform a complete radiological characterization of the SRM, as required by Technical Specification (T.S.) 5.7.1.b. The third violation involved the failure to establish a procedure that addressed the control of highly radioactive materials removed from the reactor vessel, as well as, the failure to implement a procedure to ensure that the licensee’s ALARA plan contained steps to ensure that the ambient radiation field in the work areas were being controlled and that the workers actions were in accordance with ALARA considerations, as required by T.S. 5.4.1.
EA-11-096 | Entergy Operations, Inc (River Bend Station) | Reactor | 2011-08-24 | On August 24, 2011, the NRC issued a Confirmatory Order (effective immediately) to Entergy Nuclear Operations Inc. and Entergy Operations Inc. (collectively Entergy) to formalize commitments made as a result of an ADR mediation session held on July 18, 2011 in Washington DC. By letter dated May 20, 2011, the NRC identified an apparent violation of 10 CFR 50.7 to Entergy Operations Inc. based on the NRC’s Office of Investigations, March 17, 2011 report (OI Case No. 4-2010-053). Specifically, the NRC had reached a preliminary conclusion that an employee at the River Bend Station was rated lower in his/her 2008 annual performance appraisal based in part on the employee questioning the qualifications necessary to perform certain work activities in compliance with applicable plant procedure(s). Prior to the issuance of the NRC’s May 20, 2011 letter but following a separate NRC inquiry, Entergy conducted its own internal investigation of the circumstances giving rise to the apparent violation. The NRC recognized that as a result of its investigation, Entergy took several specific actions at the River Bend Station and several fleet-wide actions. The fleet-wide actions included conducting supervisory and Employee Concerns Program personnel training on 10 CFR 50.7; reviewing all closed internal retaliation type cases in 2008 and 2009; reviewing all 2009 appraisals for employees with overall “improvement required” rating; and revising several quality-affecting procedures. As a result of the settlement agreement from the ADR mediation session, Entergy agreed to take a number of additional fleet-wide actions. A summary of those fleet-wide actions are: (1) reorganizing the quality control organization’s reporting structure; (2) reinforcing the company’s commitment to a safety conscious work environment through a written communication from a senior Entergy nuclear executive; (3) reviewing and, as necessary, revising the existing general employee training on 10 CFR 50.7 to include insights from the circumstances giving rise to this matter; (4) reviewing and, as necessary, revising training to new supervisors for 10 CFR 50.7 to include insights from the circumstances giving rise to this matter; and (5) conducting an effectiveness review of the Employee Concerns Program enhancements and training that were implemented relating to the underlying matter. Entergy also agreed to conduct a plant wide safety culture survey at the River Bend Station prior to December 31, 2012.
EA-11-110 | Northern States Power Company (Prairie Island Nuclear Generating Plant) | Reactor | 2011-08-17 | On August 17, 2011, the NRC issued a Notice of Violation to Northern States Power Company for a violation associated with a White Significance Determination Process finding. The violation involved the failure to maintain the direct current electrical power subsystems operable in Modes 1 through 4, as required by Technical Specification 3.8.4. Specifically, from December 21, 1994 to approximately October 22, 2010, all battery chargers in Unit 1 were susceptible to a common mode failure under design basis accident conditions. Under those conditions, the battery chargers would stop providing an output, or “lock-up,” when their alternating current input voltage dropped below their nameplate minimum voltage at the battery charger motor control center.
EA-11-047 | Dominion Nuclear Connecticut, Inc. (Millstone Power Station, Unit 2) | Reactor | 2011-08-08 | On August 8, 2011, the NRC issued a White Significance Determination Process finding and Notice of Violation (NOV) for two violations to Dominion Nuclear Connecticut, Inc. as a result of inspections at the Millstone Power Station Unit 2. The finding was based on multiple human performance errors, and the NOV was based on two violations which involved the licensee’s failure to meet its Technical Specifications requirements. Together these failures caused and exacerbated the February 12, 2011, unanticipated eight percent reactor power increase during the main turbine control valve testing.
EA-11-083 | Southern California Edison Company (San Onofre Nuclear Generating Station) | Reactor | 2011-08-04 | On August 4, 2011, the NRC issued a Notice of Violation to SONGS for a Severity Level III violation involving the failure to certify that the qualifications and status of a senior operator licensee were current and valid and that the senior operator licensee had completed a minimum of 40 hours of shift functions under the direction of an operator or senior operator, as required by 10 CFR 55.53(e) and (f). Specifically, on October 21 and October 27, 2010, the licensee did not certify that qualifications of the senior operator licensee were current and valid and scheduled the senior operator to perform licensed activities (core alterations) as refueling senior operator supervisor while his license was INACTIVE. Additionally, the senior operator was not medically qualified in accordance with ANSI 3.4 (1996) to perform licensed duties.
EA-11-025 | Omaha Public Power District (Fort Calhoun Station) | Reactor | 2011-07-18 | On July 18, 2011, the NRC issued a violation of 10 CFR 50, Appendix B, Criterion XVI, associated with a White Significance Determination Process finding involving the failure to assure that the cause of a significant condition adverse to quality was determined and corrective actions taken to preclude repetition. Specifically, between November 3, 2008 and June 14, 2010, the licensee failed to preclude shading coils from repetitively becoming loose material in the M2 reactor trip contactor. The licensee failed to identify that the loose parts in the trip contactor represented a potential failure of the contactor if they became an obstruction; and therefore, failed to preclude repetition of this significant condition adverse to quality, that subsequently resulted in the contactor failing.
EA-11-024 | Nebraska Public Power District (Cooper Nuclear Station) | Reactor | 2011-06-10 | On June 10, 2011, the NRC issued a violation of 10 CFR 50, Appendix B, Criterion XVI and Criterion V, associated with a White Significance Determination Process finding involving the failure to establish measures to assure a condition adverse to quality was corrected and ensure the activities affecting quality were prescribed by documented procedures appropriate to the circumstances. Specifically, Violation 05000298/2008008-1, dated June 13, 2008, identified a condition adverse to quality in that two procedures would not work as written. While correcting that violation, the licensee failed to perform sufficient evaluation of the circuits to identify and correct a problem with three motor-operated valves needed to establish core cooling. Failure to correct the condition adverse to quality resulted in inadequate procedures in that they contained steps that were inappropriate to the circumstances because they would not work as written to reposition the three motor-operated valves.
EA-11-018 | Tennessee Valley Authority (Browns Ferry Nuclear Plant) | Reactor | 2011-05-09 | On May 9, 2011, the NRC issued a violation of Technical Specifications associated with a Red Significance Determination Process finding involving the failure to implement an IST program in accordance with the American Society of Mechanical Engineers (ASME), Code for Operation and Maintenance of Nuclear Power Plants (OM Code), 1995 Edition, 1996 Addenda, Section ISTC 4.1. This failure precluded the timely identification that the RHR loop II subsystem was unable to fulfill its safety function due to a failure of LPCI Outboard Injection Valve 1-FCV-74-66. Specifically, TVA’s IST program was not able to verify operability and functionality of valves susceptible to stem and disc separations as required by the ASME OM Code. Because the LPCI Outboard Injection Valve was inoperable from March 13, 2009 to October 23, 2010, the Technical Specification allowed outage time of 7 days was exceeded.
EA-11-014 | Exelon Generation Company, LLC (Byron Station Unit 2) | Reactor | 2011-03-14 | On March 14, 2011, the NRC issued a violation of 10 CFR Part 50, Appendix B, Criterion V, associated with a White Significance Determination Process finding involving the failure to provide appropriate quantitative or qualitative acceptance criteria related to maintenance on the 2A emergency diesel generator. Specifically, on January 17, 2010, a work order package did not contain a final torque verification to ensure that the 2A diesel generator upper lube oil cooler spool piece connections were torqued to the required values. As a result, the spool piece flange connection to the upper lube oil cooler did not meet the minimum torque ranges, and, subsequently, during routine testing on November 17, 2010, the flange connection on the 2A diesel generator upper lube oil cooler failed. Because the 2A diesel generator was inoperable since January 17, 2010, and because the licensee was not aware of the inoperability, the Technical Specification allowed outage time of 14 days was also exceeded.
EA-10-257 | Carolina Power and Light Company (H.B. Robinson Steam Electric Plant) | Reactor | 2011-01-31 | On January 31, 2011, the NRC issued a Notice of Violation to Carolina Power and Light Company for two violations associated with two White Significance Determination Process findings. The first violation involved the failure to adequately implement requirements, as required by Technical Specifications 5.8.1, “Procedures,” of multiple procedures during an uncontrolled cooldown of the Reactor Coolant System (RCS) and subsequent safety injection. Specifically, on March 28, 2010, following a reactor trip, the licensee: (1) failed to take required procedural actions to stop an uncontrolled cooldown that resulted in a safety injection; (2) failed to identify a loss of component cooling water flow to the thermal barrier heat exchangers coincident with a failure to identify a loss of charging pump suction that resulted in inadequate seal injection flow; (3) re-energized electrically faulted equipment that damaged surrounding equipment and resulted in electrical ground alarms, which required an Alert emergency declaration. The second violation involved failure to adequately design and implement operator training based on learning objectives as required by 10 CFR 55.59(c)4. Specifically, prior to March 28, 2010, training lesson material failed to identify the basis of a procedural action involving reactor coolant pump seal cooling, as required by a systems approach to training, as defined in 10 CFR 55.4.
EA-10-192 | Carolina Power and Light Company (Brunswick Steam Electric Plant) | Reactor | 2010-12-21 | On December 21, 2010, the NRC issued a violation of 10 CFR 50.54(q) associated with a White Significance Determination Process finding involving the failure to follow and maintain in effect Emergency Plans which required activation of the Operations Support Center (OSC), Technical Support Center (TSC), and Emergency Operations Facility (EOF) within 60 to 75 minutes following the declaration of an Alert or higher emergency classification. Specifically, on June 6, 2010, the licensee failed to activate the OSC, TSC, and EOF until approximately two and one-half hours after an Alert was declared.
EA-10-207 | PPL Susquehanna, LLC (Susquehanna Steam Electric Plant) | Reactor | 2010-12-16 | On December 16, 2010, the NRC issued a White finding to PPL Susquehanna, LLC as a result of inspections at the Susquehanna Steam Electric Plant Unit 1 and 2. The White finding involved inadequate procedures related to the maintenance and operation of the main condenser waterboxes and circulating water system, which resulted in an internal flooding event, a manual scram, and a loss of the normal reactor heat sink. There were no NRC violations associated with the finding.
EA-10-205 | Carolina Power and Light Company (H. B. Robinson Steam Electric Plant) | Reactor | 2010-12-07 | On December 7, 2010, the NRC issued a White finding with associated violation and Notice of Violation (NOV) for a Severity Level III violation to Carolina Power and Light Company (doing business as Progress Energy Carolinas Inc (PEC)) as a result of inspections at the H.B. Robinson Steam Electric Plant Unit 2. The White finding involved the failure to identify and correct a problem associated with the “B” Emergency Diesel Generator (EDG) output breaker in 2008. Again in 2009, a similar malfunction caused the EDG to be declared inoperable for a period greater than Technical Specifications. A 10 CFR 50.9, “Completeness and Accuracy of Information,” NOV for a Severity Level III violation was also assessed for submitting materially inaccurate information. PEC provided information which stated that the breaker was tested in accordance with a maintenance procedure. However, the NRC determined that they had not conducted full testing in accordance with the procedure, and only completed the instructions for returning the breaker to service.
EA-10-234 | Kansas State University (Research Reactor Facility) | Reactor | 2010-11-22 | On November 22, 2010, the NRC issued a Notice of Violation to Kansas State University for a severity level III violation involving 10 CFR 20.1101(a). Specifically, on or prior to September 22, 2010, the licensee did not implement a radiation protection program commensurate with the scope and extent of licensed activities that was sufficient to ensure compliance with the provisions of the regulations in Part 20. Examples include: (1) On or prior to September 22, 2010, the licensee did not make surveys as required by 10 CFR 20.1501 when the licensee failed to determine the magnitude and extent of radiation levels that would be caused by irradiating oil samples on September 21, 2010 that subsequently resulted, on September 22, 2010, in an unexpected high shallow-dose equivalent of 12.5 rem to the skin of the extremities (hands) of the operator handling the experiment and an unexpected change in the restricted area dose rates that exceeded 50 rem per hour on September 22, 2010; (2) On September 22, 2010, the licensee failed to supply and require the use of extremity monitoring devices to personnel who were likely to receive in 1 year, from sources external to the body, a dose in excess of 10 percent of the limits in 20.1201(a) in that, a person handling oil samples and a sample holder, which read in excess of 50 rem per hour, was not wearing, and had not been issued, extremity monitoring; (3) On or prior to September 22, 2010, the licensee did not have an adequate procedure as required by Technical Specification Section 6.3 to assure the safety of personnel within the Laboratory for conducting sample irradiations, in that, Experiment Procedure 1, “Isotope Production,” did not require extremity dosimetry – finger rings – for those handling samples, it did not have a maximum sample withdrawal rate, and it did not specify threshold exposure/dose rates (hold points) to clearly indicate at what dose rate a sample should not be withdrawn from the pool.
EA-10-084 | Omaha Public Power District (Fort Calhoun Station) | Reactor | 2010-10-06 | On October 6, 2010, the NRC issued a Notice of Violation to Omaha Public Power District for a violation of Technical Specification 5.8.1.a, “Procedures,” at Fort Calhoun Station. This violation, which is associated with a Yellow Significance Determination Process finding, involved the licensee’s failure to develop an adequate procedure for protecting vital facilities and equipment from external flooding events to the level described in the Updated Final Safety Analysis Report. Specifically, the inspectors identified that the licensee’s strategy of using sandbags stacked on top of floodgates would not be effective in protecting the auxiliary building, intake structure, and turbine building basement because the tops of the floodgates were too small to support the necessary number of sandbags. This could have resulted in flooding impacting multiple, redundant trains of equipment required for safe shutdown of the plant.
EA-10-094 | Duke Energy Carolinas, LLC (Oconee Nuclear Station) | Reactor | 2010-08-12 | On August 12, 2010, the NRC issued a Yellow and a White finding with associated violations and a Notice of Violation (NOV) for a Severity Level III violation to Duke Energy Carolinas, LLC. (Duke) as a result of inspections at the Oconee Nuclear Station Units 1, 2 and 3. The Yellow finding involved the failure to ensure the Standby Shutdown Facility (SSF) Reactor Coolant Makeup (RCM) subsystem for all three units remained operable as required by Technical Specifications. The White finding involved the failure to identify and correct Unit 2 and Unit 3 SSF RCM letdown line degradation in a timely manner after degradation was identified on Unit 1, as required by 10 CFR 50, Appendix B, Criterion XVI, “Corrective Action.” A 10 CFR 50.9, “Completeness and Accuracy of Information,” NOV for a Severity Level III violation was also assessed to Duke for submitting materially inaccurate information. Duke provided information which described an alternate flow path that could be used to control pressurizer level during an SSF event. However, it was discovered that this flow path was not available due to a closed manual valve inside containment.
EA-10-080 | Calvert Cliffs Nuclear Power Plant, LLC (Calvert Cliffs Nuclear Power Plant) | Reactor | 2010-08-03 | On August 3, 2010, the NRC issued a White Significance Determination finding with an associated violation to Calvert Cliffs Nuclear Power Plant (Calvert Cliffs). This White finding involved the licensee’s failure to develop and implement scheduled preventive maintenance for Agastat E7000 series time delay relays, as required by Technical Specification 5.4.1. Specifically, subsequent to the approval of Engineering Change Package No. ES200100067, issued in March 2001, the licensee did not replace the relays within the vendor recommended 10-year lifetime, nor establish a performance monitoring program. Consequently, on February 18, 2010, an Agastat E7000 series time delay relay that had a lifetime in excess of 10 years, used in the 2B emergency diesel generator (EDG) protective logic, timed out early and failed to support a demand fast start and run of the 2B EDG. This resulted in the EDG becoming inoperable with the resultant loss of alternating current to the 24 safeguards bus during the dual unit trip that occurred on February 18, 2010.
EA-10-037 | Florida Power and Light Company (Turkey Point Nuclear Plant Unit 3) | Reactor | 2010-06-21 | On June 21, 2010, the NRC issued a White finding with two associated violations to Florida Power and Light Company (FP&L) as a result of inspections at Turkey Point Nuclear Plant Unit 3. This White finding involves the licensee’s failure to adequately address degradation of Boraflex, a fixed neutron absorber material used in the Turkey Point Unit 3 spent fuel pool. Boraflex degradation resulted in a reduction in the Boron‑10 areal density of the spent fuel storage racks such that, when considering the biases and uncertainties identified in Chapter 9 of the Updated Final Safety Analysis Report, the effective neutron multiplication factor would not have been maintained less than 1.0 if the spent fuel pool had been flooded with unborated water. The NRC identified that FP&L had violated 10 CFR 50, Appendix B, Criterion XVI, “Corrective Action,” which requires that conditions adverse to quality be promptly identified and corrected, and Technical Specification 5.5.1.1.a, which requires that the spent fuel storage racks be maintained with an effective neutron multiplication factor less than 1.0 if flooded with unborated water, when considering the biases and uncertainties described in the Updated Final Safety Analysis Report. The NRC also issued FP&L a Severity Level III Notice of Violation with a proposed $70,000 civil penalty for failure to comply with 10 CFR 50.73, which requires, in part, that licensees report any condition prohibited by the plant’s Technical Specifications. As discussed, Boraflex degradation led to a condition prohibited by Turkey Point Unit 3 Technical Specifications, but this condition was not reported to the NRC as required by 10 CFR 50.73.
EA-09-252 | Duke Energy Carolinas, LLC (William B. McGuire Nuclear Station) | Reactor | 2010-06-02 | On June 2, 2010, an immediately effective Confirmatory Order was issued to Duke Energy Carolinas, LLC. (Duke Energy), to confirm commitments made as a result of an Alternative Dispute Resolution mediation session held on March 29, 2010. This enforcement action is based on two violations of NRC requirements at the McGuire Nuclear Station, which included a contract employee introducing and using marijuana inside the Protected Area and a contract employee failing to immediately report the event to Duke Energy management. Duke Energy agreed to take the following actions: (1) develop a summary of lessons learned from the facts and circumstances surrounding the apparent violations and communicate this summary to its fleet wide employees; (2) perform a self-assessment of the adequacy of the programs and processes in place to detect and deter the introduction of illegal drugs and alcohol into the Protected Area of Duke Energy’s nuclear stations and implement appropriate enhancements in accordance with Duke Energy’s corrective action program; and (3) prior to December 31, 2010, perform an effectiveness review of the corrective actions identified in (1) and (2) above. This is in addition to several other corrective actions already completed by Duke Energy. In consideration of these commitments, and the corrective actions already completed by Duke Energy, the NRC agreed that the non-compliances will be characterized as a violation of 10 CFR Part 26, with a significance of Severity Level IV.
EA-10-009 | Southern Nuclear Operating Company, Inc. (Edwin I. Hatch Nuclear Plant) | Reactor | 2010-05-12 | On May 12, 2010, a Notice of Violation (NOV) was issued to Southern Nuclear Operating Company, Inc. for a violation associated with a White Significance Determination Finding as a result of inspections at the Edwin I. Hatch Nuclear Plant. The White finding involved the licensee’s failure to meet Technical Specifications. From 1988 to 2009 the licensee failed to establish and perform preventative maintenance activities on components having a specific lifetime. This resulted in a capacitor failure on a circuit card, during a surveillance test of an emergency diesel generator (EDG) and caused the EDG to be declared inoperable.
EA-09-332 | FirstEnergy Nuclear Operating Company (Davis-Besse Nuclear Power Station) | Reactor | 2010-04-30 | On April 30, 2010, a Notice of Violation (NOV) was issued to FirstEnergy Nuclear Operating Company for a Severity Level III problem for the failure to implement: (1) 10 CFR 50.71 “Maintenance of records, making of reports” and (2) 10 CFR 50, Appendix B, Criterion III, “Design control.” In July 1999, the licensee submitted a license amendment request to eliminate as found testing criteria by using the past data for double O ring data and was approved by the NRC. However, the licensee staff did not update this fact in their updated final safety analysis report. The licensee also changed from the double O ring design to a flat gasket design which did not have the same reliable history as the double O ring and failed to translate this fact into the licensing basis at time of installation.
EA-09-307 | Tennessee Valley Authority (Browns Ferry Nuclear Plant) | Reactor | 2010-04-19 | On April 19, 2010, a Notice of Violations was issued to Tennessee Valley Authority (TVA) for violations associated with Yellow and White Significance Determination Findings as a result of inspections at the Browns Ferry Nuclear Plant. The Yellow finding involved the licensee’s failure to meet the requirements of 10 CFR 50, Appendix R, III.G, fire protection of safe shutdown capability. There were multiple examples of the licensee not providing fire protection features capable of limiting fire damage and failing to ensure one train of systems or components was free of fire damage by approved methods. Compensatory measures are currently in place and long term corrective actions will be implemented. The White finding involved the licensee’s failure to meet the requirements of a Technical Specification. This involved the inappropriate revision to a procedure which could have delayed proper operator response to a major disabling fire event. The procedure has been revised to prevent such an issue from occurring.
EA-09-321 | Florida Power & Light Company (St. Lucie Nuclear Plant) | Reactor | 2010-04-19 | On April 19, 2010, a Notice of Violation was issued to Florida Power & Light Company for a violation associated with a Yellow Significance Determination Finding as a result of inspections at the St. Lucie Nuclear Plant. The Yellow finding involved the licensee’s failure to meet the requirements of 10 CFR 50, Appendix B, Criterion XVI, “Corrective Action.” In 2008, the licensee experienced an air in-leakage event into the closed cooling water (CCW) system which affected the system’s ability to supply adequate cooling to essential equipment. Their troubleshooting and corrective actions failed to identify the source of the air in-leakage, which resulted in a similar event in 2009.
EA-09-259 | Exelon Generation Company, LLC (Braidwood Nuclear Power Station) | Reactor | 2010-02-25 | On February 25, 2010, a Notice of Violation was issued to Exelon Generation Company, LLC, for a violation associated with a White Significance Determination Finding as a result of inspections at the Braidwood Nuclear Power Station. This finding involved a violation of 10 CFR Part 50, Appendix B, Criterion III, “Design Control,” which requires, in part, that measures be established for the selection and review for suitability of application of materials, parts, equipment, and processes that are essential to the safety-related functions of the structures, systems, and components. Specifically, on June 24, 2009, a safety-related valve failed to stroke full open during a surveillance testing procedure. Following the test failure, the licensee determined that water entered the valve actuator through conduit penetration and caused corrosion to the valve internals, which caused the valve not to fully open.
EA-09-283 | FirstEnergy Nuclear Operating Company (Davis-Besse Nuclear Power Station) | Reactor | 2010-02-25 | On February 25, 2010, a Notice of Violation was issued to FirstEnergy Nuclear Operating Company for a violation associated with a White Significance Determination Finding as a result of inspections at the Davis-Besse Nuclear Power Station. This finding involved a violation of 10 CFR 50.54(q) which requires, in part, that a holder of an operating license shall follow emergency plans which meet the standards in 10 CFR 50.47(b). 10 CFR 50.47(b) requires, in part, that the licensee have a standard emergency classification and action level scheme in use. The Davis-Besse Emergency Plan requires, in part, that the Shift Manager shall verify the indication of an off-normal event and classify the situation. Specifically, on June 25, 2009, the Shift Manager failed to verify the indications of an off-normal event or reported sighting, assess the information available from valid indications or reports of an explosion, and classify the situation as an Alert in accordance with the Emergency Action Level Conditions during an actual event.
EA-09-248 | PPL Susquehanna, LLC (Susquehanna Steam Electric Station) | Reactor | 2010-01-28 | On January 28, 2010, a Notice of Violation for a Severity Level III violation was issued to PPL Susquehanna, LLC. This finding involved a violation of 10 CFR Part 55.21 which requires, in part, that the licensed operator receives a medical examination by a physician every two years and meets the requirements of 10 CFR 55.33(a)(1). 10 CFR 55.33(a)(1) states, in part, the medical condition of the applicant will not adversely affect the performance of assigned duties or cause operational errors endangering public health and safety. 10 CFR 55.33(b) states, in part, if an applicant’s general medical condition does not meet the minimum standards under 10 CFR 55.33(a)(1), the Commission may approve the application and include conditions in the license to accommodate the medical defect. 10 CFR 55.23 requires, in part, that a facility licensee shall certify the medical fitness of an applicant. PPL certified that it used the guidance of ANSI/ANS 3.4 1983 which describes the health requirements. Contrary to the above, in 2009, a PPL operator did not meet a certain medical prerequisite for performing NRC-licensed operator activities. Specifically, on three separate occasions, the licensed operator performed duties, even though a change in his license condition existed, as found by a medical examination.
EA-09-269 | Entergy Nuclear Operations, Inc. (Palisades Nuclear Plant) EA-09-269 | Reactor | 2010-01-20 | On January 20, 2010, a Notice of Violation was issued to Entergy Nuclear Operations, Inc. for a violation associated with a White Significance Determination Finding as a result of inspections at the Palisades Nuclear Plant. This White finding involved the licensee’s failure to meet the requirements of Technical Specification (TS) for fuel storage in the spent fuel pool (SFP). Specifically, the Region I spent fuel pool storage rack neutron absorber had deteriorated over the life of the plant and was less than required by TS. Corrective actions are currently in place for additional controls of the spent fuel pool.
EA-09-018 | Entergy Operations, Inc. (Waterford Steam Electric Station) | Reactor | 2010-01-14 | On January 14, 2010, the NRC issued a Notice of Violation to Entergy Operations, Inc. for a violation of Technical Specification 6.8.1.a, "Procedures and Programs," at Waterford Steam Electric Station Unit 3. The violation, which is associated with a White Significance Determination Process finding, involved the failure to properly follow all procedural steps during replacement of the safety-related Train B 125 Vdc battery in May 2008. Specifically, following replacement of the battery, the licensee did not: (1) adequately torque all of the affected intercell connections, (2) obtain the required quality control inspector verification that all affected connections were properly tightened, (3) ensure that all the necessary intercell resistance checks were performed, and (4) obtain quality control verification that the intercell resistance checks met Technical Specification limits. As a result, an intercell connection on the battery loosened over time and on September 2, 2008, the battery was found to be inoperable during testing.
EA-09-009; EA-09-203 | Tennessee Valley Authority (Browns Ferry Nuclear Plant) | Reactor | 2009-12-22 | On December 22, 2009, a Confirmatory Order (effective immediately) was issued to the Tennessee Valley Authority (TVA) to confirm commitments made as a result of an Alternative Dispute Resolution (ADR) mediation session held on December 4, 2009. At issue were two apparent violations of the NRC’s employee protection regulation (10CFR50.7) identified during two separate investigations conducted by the NRC Office of Investigations at the Browns Ferry Nuclear Plant (BFN). The NRC acknowledged that TVA, prior to the ADR session, had taken numerous actions which address the issues underlying the apparent violations. As part of the agreement, TVA agreed to take a number of additional actions. These actions include, implementing a process to review proposed adverse employment actions before they are taken to ensure compliance with 10CFR50.7 and to ensure the action could not negatively impact the Safety Conscious Work Environment (SCWE), issuing a fleet-wide written communication from TVA’s executive management communicating TVA’s policy and management expectations regarding the employee’s right to raise concerns without fear of retaliation, performing two additional independent safety culture surveys before the end of calendar year 2013, and modifying contractor in-process training and new supervisor training to improve awareness of TVA’s policy on SCWE. In recognition of these commitments, and the other actions already completed by TVA, the NRC agreed to refrain from issuing a civil penalty or Notice of Violation for these apparent violations.
EA-09-007, EA-09-059 | Exelon Generating Company, LLC (Peach Bottom Atomic Power Station) | Reactor | 2009-12-01 | On December 1, 2009, an immediately effective Confirmatory Order was issued to Exelon Generating Company, LLC (Exelon) to confirm commitments made as a result of an Alternative Dispute Resolution mediation session held on September 3, 2009. This enforcement action is based on two violations of NRC requirements at Exelon’s Peach Bottom Atomic Power Station (Peach Bottom), including the deliberate failure of a former reactor operator to report an arrest in a timely manner and the deliberate failure of a former maintenance supervisor to provide complete and accurate information on a personal history questionnaire. Exelon agreed to take the following actions: (1) provide additional training on deliberate misconduct at Peach Bottom and other Exelon sites, for both employees and supervisors; (2) perform an assessment to verify the effectiveness of the deliberate misconduct training; (3) conduct training with licensed operators on the special obligations associated with holding an NRC license; (4) perform an assessment of Peach Bottom employee conduct, including trending; (5) conduct additional Exelon fleet-wide training on the Behavioral Observation Program, fitness for duty requirements, and the Employee Assistance Program; (6) submit a lessons-learned article to two professional organizations requesting publication in their respective newsletters; and (7) discuss with the Institute of Nuclear Power Operations the possibility of incorporating training on deliberate misconduct into its supervisor and operator development programs. In consideration of these commitments, and other actions already completed by Exelon, the NRC agreed to refrain from issuing a civil penalty or Notice of Violation for these violations.
EA-09-262 | Constellation Energy (Nine Mile Point Nuclear Station Unit 2) | Reactor | 2009-11-24 | On November 24, 2009, the NRC issued a parallel White finding to Constellation Energy as a result of inspections at Nine Mile Point Nuclear Station Unit 2. This parallel White finding was identified during a supplemental inspection to review the licensee’s evaluation of the circumstances that led to the Mitigating Systems Performance Index for the cooling water system crossing the Green to White threshold. The performance indicator crossed the threshold because of service water pump unavailability for maintenance and reliability challenges caused by a November 4, 2008 event where the licensee failed to properly control diving operations while cleaning the intake bays. The inspectors identified significant weaknesses in Constellation’s causal analysis for the November 4, 2008 event. Specifically, Constellation failed to identify that the initial work controls put into place for the diving evolution, and subsequent changes made to the work scope, were inadequate and directly contributed to the event. In addition, Constellation failed to identify that governing diving procedures were not followed during the event. Based on these NRC-identified weaknesses, a parallel White inspection finding was opened to allow for the NRC’s continued review of Constellation’s actions to address the significant weaknesses identified during the supplemental inspection.
EA-09-145 | NextEra Energy Seaboork, LLC (Seabrook Station) | Reactor | 2009-11-12 | On November 12, 2009, the NRC issued a Notice of Violation to NextEra Energy Seabrook, LLC, for a violation of 10 CFR 50, Appendix B, Criterion III, “Design Control,” at Seabrook Station. The violation, which is associated with a White Significance Determination Process finding, involved the failure to assure that the design basis of the B emergency diesel generator (EDG) was correctly translated into work instructions and that measures were established for the selection of suitable parts and materials. Specifically, a design change to a flange on a jacket water cooling line to the B EDG turbocharger did not (1) control welding stresses, verify flange alignment, or evaluate vibration effects, (2) address suitability of gasket material, or (3) consider flange performance history. This resulted in failure of the flange during operation of the B EDG, leading to rapid loss of jacket cooling water and inoperability of the EDG.
EA-09-249 | Constellation Energy (R.E. Ginna Nuclear Power Plant) | Reactor | 2009-11-12 | On November 12, 2009, the NRC issued a Notice of Violation to Constellation Energy for a violation of 10 CFR 50, Appendix B, Criterion XVI, “Corrective Action,” at the R.E. Ginna Nuclear Power Plant. The violation, which is associated with a White Significance Determination Process finding, involved the failure to identify the cause of a significant condition adverse to quality. Specifically, after identifying corrosion on the turbine-driven auxiliary feedwater pump governor control valve stem on April 11, 2005, the licensee did not take adequate measures to identify the cause or prevent recurrence. This led to additional corrosion and binding of the governor control valve, and resulted in failure of the turbine-driven auxiliary feedwater pump on July 2, 2009.
EA-09-193 | Northern States Power Company (Prairie Island Nuclear Generating Plant) | Reactor | 2009-10-27 | On October 27, 2009, the NRC issued a Notice of Violation for a Severity Level III violation to Northern States Power Company, Minnesota. The licensee violated 10 CFR 50.9 which requires, in part, that information provided to the Commission by an applicant shall be complete and accurate in all material respects. Specifically, on May 11, 2007, the licensee failed to report a medical condition, as required by 10 CFR 55.23 “Certification,” of a senior reactor operator (SRO) on a license renewal form. This resulted in the NRC renewing the SRO’s license without a restriction for the medical condition.
EA-09-172 | Exelon Generation Company, LLC (Dresden Nuclear Power Station Unit 3) | Reactor | 2009-10-26 | On October 26, 2009, a Notice of Violation was issued to Exelon Generation Company, LLC for a violations associated with a White Significance Determination Finding as a result of inspections at the Dresden Nuclear Power Station Unit 3. The White finding involved multiple violations including: (a) 10 CFR 50.54(j), in which non-licensed operators, during a maintenance activity, manipulated the control rod drive system hydraulic control unit insert riser isolation valves and the withdraw riser isolation valves, an action which affected the reactivity of the reactor in that the valve manipulations caused three control rods, D-7, E-7, and E-6 to move out of the core to positions 06, 18, and 16, respectively; (b) Technical Specification 3.1.1, in which the reactor was in Mode 4, the shutdown margin was not ≥ 0.38 ∆k/k and the licensee failed to initiate immediate actions to insert control rods; (c) Technical Specification 5.4.1, in which maintenance that affected the performance of the control rods, which are safety‑related equipment, was performed in accordance with a written procedure that was not appropriate to the circumstances; (d) Technical Specification 5.4.1, in which the control room operators failed to implement a section of a procedure in that they did not aggressively investigate annunciators and alarms and did not accept the alarms as correct until demonstrated otherwise; and (e) Technical Specification 5.4.1, in which the licensee failed to implement its written procedure which addressed the inability to drive control rods.
EA-09-167 | Northern States Power Company (Prairie Island Nuclear Generating Plant) | Reactor | 2009-09-03 | On September 3, 2009, a Notice of Violation was issued to Northern States Power Company - Minnesota for a violation associated with a White Significance Determination Finding involving a violation of 10 CFR Part 50, Appendix B, Criterion III, “Design Control” which requires, in part, that measures be established to assure that the design basis for safety related functions of structures, systems, and components are correctly translated into specifications, drawings, procedures, and instructions. Contrary to this requirement, Prairie Island Nuclear Generating Plant failed to implement design control measures to ensure that the design basis for the component cooling water system was correctly translated into specifications, drawings, procedures, and instructions. Specifically, the licensee failed to ensure that the safety-related function of the component cooling water system was maintained following a high energy line break, seismic, or tornado events in the turbine building.
EA-09-103 | Southern Nuclear Operating Company, Inc. (Joseph M. Farley Nuclear Plant) | Reactor | 2009-07-10 | On July 10, 2009, the NRC issued a Notice of Violation to Southern Nuclear Operating Company, Inc. (SNC) for a violation of 10 CFR 50.54(q) which states, in part, that the licensee shall follow and maintain emergency response plans which must meet planning standards in 10 CFR 50.47(b). 10 CFR 50.47(b) requires, in part, that the licensee establish a means to provide early notification and clear instruction to the populace within the plume exposure pathway Emergency Planning Zone (EPZ). SNC emergency plan identifies both tone alert radios (TARs) and sirens as the means by which it provides alert and notification to the populace within the plume exposure pathway. This violation is associated with a White Significance Determination Process finding. Specifically, in January 2008, the licensee identified that approximately 109 TARs had not been provided to residences that were outside the limits of the sirens but within the 10 mile EPZ of Farley Nuclear Plant. The licensee’s subsequent review identified additional residences within the 10 mile EPZ which were required to have TARs in accordance with the Farley emergency plan, but were not provided TARs.
EA-09-012 | Nuclear Management Company, LLC (Point Beach Nuclear Generating Plant) | Reactor | 2009-06-29 | On June 26, 2009, the NRC issued a Notice of Violation to NextEra Energy Point Beach, LLC for a Severity Level III problem involving the failure to implement: (1) 10 CFR 50.74(c) which requires that each licensee notify the appropriate NRC Regional Administrator within 30 days of a permanent disability or illness, as described in 10 CFR 55.25, of a licensed operator or a senior licensed operator; (2) 10 CFR 50.9 which requires, in part, that information provided to the Commission by an applicant for a license or by a licensee or information required by statute or by the Commission’s regulations, Orders, or license conditions to be maintained by the applicant or the licensee shall be complete and accurate in all material respects; and (3) 10 CFR 55.23 requires, in part, that to certify the medical fitness of the applicant, an authorized representative of the facility licensee shall complete and sign NRC Form‑396, "Certification of Medical Examination by Facility Licensee." Specifically, the licensee was informed in February 1993 that the non-licensed operator was taking prescribed medication for hypertension, a permanent disability or illness. The non-licensed operator applied for an NRC operating license in May 1999. The NRC issued the operator a reactor operator license August 27, 1999 and a senior reactor operator license on February 22, 2002, with no restrictions. The licensee did not inform the NRC of the operator’s medical condition until October 20, 2008. Also, the licensee submitted an NRC Form 396 for renewal of a senior reactor operator’s license and the NRC Form 396 certified that the applicant met the medical requirements of ANSI/ANS 3.4 1996 with no restrictions. However, in February 1993, the operator was prescribed medication to adequately compensate for a disqualifying medical condition. The certification by the senior licensee facility representative was material to the NRC because the NRC relied upon this certification to renew the senior reactor operator’s license pursuant to 10 CFR Part 55 when the license should have been modified with a restriction that the senior reactor operator was required to take medication as prescribed to maintain his qualification.
EA-09-054 | Southern Nuclear Operating Company, Inc. (Edwin I. Hatch Nuclear Plant) | Reactor | 2009-06-09 | On June 9, 2009, a Notice of Violation was issued to Southern Nuclear Operating Company, Inc. for a violation associated with a White Significance Determination Finding involving a violation of 10 CFR Part 50, Appendix B, Criterion XVI, “Corrective Actions.” Specifically, since 1988 the licensee had observed cracks in the glands of the emergency diesel generator (EDG) couplings, but did not recognize the cracking was an indication of coupling deterioration. This fact was not documented during routine maintenance inspections, therefore there was no condition report written to identify and correct the condition. Consequently, the 1B EDG coupling developed higher than normal vibration on July 12, 2008, during a routine surveillance test which prompted the licensee to declare the 1B EDG inoperable.
EA-09-045 | Constellation Energy (R. E. Ginna Nuclear Power Plant) | Reactor | 2009-06-08 | On June 8, 2009, the NRC issued a Notice of Violation to Constellation Energy for a violation of Technical Specification 5.4.1.a, “Procedures” at the R.E. Ginna Nuclear Power Plant. The violation, which is associated with a White Significance Determination Process finding, involved the failure to implement a Technical Specification-required procedure. Specifically, in March 2008, the licensee did not implement steps for cleaning and lubricating the turbine-driven auxiliary feedwater pump’s governor linkage assembly, as required. Failure to conduct this preventative maintenance led to the turbine-driven auxiliary feedwater pump being declared inoperable when the governor linkage became stuck, preventing the pump from obtaining the required discharge pressure and flow during surveillance testing in December 2008.
EA-09-083 | Florida Power and Light Energy (Duane Arnold Energy Center) | Reactor | 2009-06-06 | On June 6, 2009 a Notice of Violation was issued to Florida Power and Light Energy Duane Arnold, LLC for a violation associated with a White Significance Determination Finding involving a violation of 10 CFR Part 50, Appendix B, Criterion XVI, “Corrective Actions.” Specifically, the licensee initially identified and corrected a condition adverse to quality regarding overspeed trip alarms on the Train B emergency diesel generator (B EDG), a safety‑related component covered under 10 CFR Part 50, Appendix B, in February and March 2008. However, when spurious overspeed trip alarms began recurring in June 2008, the licensee did not perform any additional evaluation to identify the cause for the new condition adverse to quality and did not correct the recurring spurious overspeed trip alarms. This allowed the overspeed switch degradation to continue, resulting in the failure of the B EDG during the monthly surveillance test conducted in November 2008.
EA-09-010 | Northern States Power Company (Monticello Nuclear Generating Plant) | Reactor | 2009-05-27 | On May 27, 2009, a Notice of Violation was issued for a Severity Level III problem involving incomplete and inaccurate information in the renewal application for a Senior Reactor Operator’s (SRO) license. Specifically, on September 11, 2008, Monticello Nuclear Generating Plant submitted NRC Form 396 for renewal of an SRO license certifying that the individual met the medical requirements. The NRC renewed the SRO license based on NRC Form 396, which only requested a corrective lenses license restriction. Later in November 2008, the NRC received a license restriction change request for the same SRO to add a “Must Take Medication as Prescribed to Maintain Medical Qualifications” license restriction. During the review of the licensing action, the NRC discovered that the SRO both started taking medication and notified the Monticello medical staff in July 2004. The licensee failed to notify the NRC of this change in medical condition. This is a violation of 10 CFR 50.74(c), which requires the licensee to notify the appropriate Regional Administrator within 30 days of a permanent disability or illness of a licensed operator. As a result of the inaccurate information contained in the renewal request, the NRC renewed the SRO license. This is a violation of both 10 CFR 50.9 and 10 CFR 55.23. Title 10 CFR 50.9, states, in part, “Information provided to the Commission…shall be complete and accurate in all material respects” and 10 CFR 55.23, states, in part, that to certify the medical fitness of the applicant, an authorized representative of the facility licensee shall complete and sign NRC Form 396, “Certification of Medical Examination by Facility Licensee.”
EA-08-349 | Northern States Power Company (Prairie Island Nuclear Generating Plant) | Reactor | 2009-05-06 | On May 6, 2009, a Notice of Violation was issued to Northern States Power Company for a violation associated with a White Significance Determination Process finding at Prairie Island. Specifically, the licensee failed to meet the requirements of 49 CFR 173.441(a), which requires shipments of radioactive material to be packaged such that under conditions normally incident to transportation, dose rates on all external surfaces of the package are less than 200 mrem per hour, and 49 CFR 172.704, which requires training for personnel involved in packaging and shipping radioactive materials. Specifically, on October 31, 2008, a shipment of radioactive material sent from Prairie Island to a Westinghouse facility in Pennsylvania was found to have a dose rate on an external surface in excess of 200 mrem per hour. Subsequent investigation identified that a number of the personnel involved in preparing this shipment had not been properly trained, as required.
EA-08-351 | Constellation Generation Group, LLC (Calvert Cliffs Nuclear Power Plant) | Reactor | 2009-04-03 | On April 3, 2009, a Notice of Violation was issued to Constellation Energy for a violation associated with a White Significance Determination Process finding at Calvert Cliffs. Specifically, the licensee failed to maintain in effect Emergency Plans that met the requirements of 10 CFR 50.47(b)(4) and 10 CFR 50, Appendix E. An emergency action level table used by operators to assess the functionality of the containment barrier during an accident contained an inaccurate threshold for identifying a potential loss of the containment barrier. This error could have adversely impacted the licensee’s ability to accurately classify an emergency condition.
EA-08-324 | Duke Power Company, LLC (Oconee Nuclear Station) | Reactor | 2009-02-19 | On February 19, 2009, Duke Power Company, LLC was issued a White Significance Determination Finding which involved the performance of a maintenance procedure that was inadequate. Specifically, the maintenance procedure failed to identify and electrically isolate all main generator automatic voltage regulator trip outputs to the main generator lockout relay. This deficiency caused a main generator lockout which resulted in a loss of power event to the site which ultimately led to a loss of reactor coolant inventory while the reactor was shutdown.
EA-08-322 | Entergy Nuclear Operations, Inc. (Palisades Nuclear Plant) | Reactor | 2009-01-30 | On January 30, 2009, a Notice of Violation was issued for a violation associated with a White Significance Determination finding involving a violation of 10 CFR 20.1501 which requires the performance of surveys (evaluations) necessary for the licensee to comply with the regulations in Part 20. The violation involved the failure to evaluate radiological hazards and assess dose to workers that handled tools used for reconstituting failed fuel during work on the refueling floor in October 2007, as required by 10 CFR 20.1501 to demonstrate compliance with the dose limits of 20.1201.
EA-08-272 | Northern States Power Company (Prairie Island Nuclear Generating Plant) | Reactor | 2009-01-27 | On January 27, 2009, a Notice of Violation was issued to Northern States Power Company for a violation of Technical Specifications associated with a White Significance Determination finding at Prairie Island Nuclear Generating Plant. Specifically, the licensee failed to adequately control the position of a normally open pressure switch block valve for the Unit 1 turbine-driven auxiliary feedwater pump. The valve was inadvertently left closed, causing the turbine-driven auxiliary feedwater pump to fail to operate as required following a July 31, 2008, Unit 1 reactor trip. The pump was subsequently determined to have been inoperable for 138 days, a time period that significantly exceeded that allowed by the Technical Specifications.
EA-08-298 | Exelon Generation Company, LLC (Peach Bottom Atomic Power Station) | Reactor | 2009-01-06 | On January 6, 2009, a Notice of Violation and Proposed Imposition of Civil Penalty in the amount of $65,000 was issued for a Severity Level III problem involving inattentive security officers at Exelon’s Peach Bottom Atomic Power Station. An investigation conducted by the NRC Office of Investigations determined that multiple security officers at Peach Bottom were deliberately inattentive on multiple occasions. In addition, multiple security officers deliberately failed to report observations of inattentiveness to their supervision. These security officers put Exelon in violation of 10 CFR 73.55, which requires armed responders to maintain continuous communication with each alarm station and be available to immediately respond to threats, and Peach Bottom License Condition 2.C(3), which requires, in part, reporting of aberrant behavior.
EA-08-211 | Tennessee Valley Authority (Sequoyah Nuclear Plant) | Reactor | 2009-01-05 | On January 5, 2009 a Confirmatory Order (effective immediately) was issued to Tennessee Valley Authority to confirm commitments made as a result of an Alternative Dispute Resolution (ADR) settlement agreement, regarding violation of site security procedures caused by the deliberate actions of one contract security supervisor at the Sequoyah Nuclear Plant, who falsified an inventory form to conceal the supervisor’s failure to verify inventory as required by licensee procedures.
EA-12-142 | The Christ Hospital, Cincinnati, OH | Materials | 2012-08-28 | On August 28, 2012, the NRC issued a Notice of Violation to The Christ Hospital, for a Severity Level III violation involving the failure to file NRC Form 241 “Report of Proposed Activities in Non-Agreement States,” at least three days prior to engaging in licensed activities within NRC jurisdiction, as required by 10 CFR 150.20 (b). Specifically, on multiple occasions between January 2009 and March 8, 2012, The Christ Hospital - Mobile, a licensee of the State of Ohio, possessed and used syringes containing technetium-99m at a temporary job site in Indiana, a non-Agreement State, without first filing a Form-241 with the NRC, at least three days before engaging in such activity.
EA-12-108 | L.E. Gregg Associates, Lexington, KY | Materials | 2012-07-27 | On July 27, 2012, the NRC issued a Notice of Violation to L.E. Gregg Associates for a Severity Level III violation. The violation involved a failure to file NRC Form 241 “Report of Proposed Activities in Non-Agreement States,” at least three days prior to engaging in licensed activities within NRC jurisdiction, as required by 10 CFR 150.20(b). Specifically, on December 12-16, 2011, January 5-7, 2012, and February 21-24, 2012, L.E. Gregg Associates, which only holds a Kentucky (Agreement State) license, used and stored a portable nuclear gauge at temporary jobsites in West Virginia (non-Agreement State), without obtaining a specific license issued by the NRC or filing NRC Form-241, at least three days before engaging in such activity.
EA-12-088 | Gamma Irradiator Services | Materials | 2012-07-11 | On July 11, 2012, the NRC issued a Notice of Violation to Gamma Irradiator Services (GIS) for a Severity Level III violation. The violation involved the failure to limit licensed activities to Category 1 self-shielded irradiators, as required by Condition 9 of GIS’s NRC license No. 37-30850-01. Specifically, on May 2, 2003, February 25, 2005, June 15, 2007, and May 19, 2009, GIS performed maintenance activities on a JL Shepherd Model 81-22 irradiator, which is not a self-shielded (Category I) irradiator but, rather, a panoramic (Category II) irradiator.
EA-12-031 | U. S. Air Force - Wright Patterson Medical Center | Materials | 2012-06-29 | On June 29, 2012, the NRC issued a Notice Violation and Proposed Imposition of a Civil Penalty in the amount of $8,500 to the United States Air Force (USAF) for a Severity Level (SL) III problem. The SL III problem involved two violations: 1) the USAF’s failure to conduct a semiannual physical inventory of all sealed sources in their possession, as required by 10 CFR 35.67(g); and 2) the USAF’s failure to secure from unauthorized removal or access licensed materials that are stored in controlled or unrestricted areas, as required by 10 CFR 20.1801. Specifically, between November 2, 2004 and September 30, 2011, the USAF did not include a sealed source, which was believed to be in storage, in its semiannual physical inventory. The USAF believed the source was located in the low-level radioactive waste storage room, which is a controlled area; however, sometime between November 2, 2004, when the last physical inventory occurred, and September 30th 2011, the source was lost.
EA-12-077 | American Radiolabeled Chemicals - St. Louis, Missouri | Materials | 2012-06-25 | On June 25, 2012, the NRC issued a Notice of Violation to American Radiolabeled Chemicals for a Severity Level III violation involving the failure to implement 10 CFR 20.1801. Specifically, on April 2, 2012 the licensee failed to secure from unauthorized removal or limit access to licensed material stored in a controlled area.
EA-12-068 | neo-pet, LLC - Cleveland, OH | Materials | 2012-06-13 | On June 13, 2012, the NRC issued a Notice of Violation to neo-pet, LLC, a licensee of the State of Ohio, for a Severity Level III violation involving 10 CFR 150.20. Specifically, on multiple occasions between April 6, 2010, and March 6, 2012, neo-pet, LLC, possessed and used doses of fluorine-18 in Indiana, a Non-Agreement State, without filing an NRC Form 241 at least three days prior to engaging in licensed activities in areas of exclusive Federal jurisdiction.
EA-10-102 | Texas Gamma Ray, LLC -Pasadena, Texas | Materials | 2012-05-15 | On May 15, 2012, the NRC issued a Confirmatory Order (Effective Immediately) to Texas Gamma Ray, LLC (TGR) to formalize commitments made as a result of an ADR mediation session held on April 23, 2012. The commitments were made as part of a settlement agreement between TGR and the NRC regarding apparent violations of NRC requirements. The agreement resolves the apparent violations involving TGR’s failure to: (1) meet two NRC security requirements; and (2) store radioactive material only at a location authorized by its license. Specifically, radioactive material was stored at a facility in Rock Springs, Wyoming, which was not an approved storage location. TGR agreed to a number of corrective actions, including paying a civil penalty of $7,000, retrieving the licensed material from Wyoming and transferring it to a site in Texas authorized for storage, revising internal procedures, requiring the RSO’s approval for storing licensed material, and training all radiographers on the new procedures.
EA-11-276 | Advanced Material Services, LLC | Materials | 2012-04-17 | On April 17, 2012, the NRC issued a Notice of Violation to Advanced Material Services, LLC (AMS) for a Severity Level III violation. The violation involved a failure to file NRC Form 241 “Report of Proposed Activities in Non-Agreement States,” at least three days prior to engaging in licensed activities within NRC jurisdiction, as required by 10 CFR 150.20(b). Specifically, between May 12 and June 26, 2008, AMS, which only holds an Alabama (Agreement State) license, used a portable nuclear gauge, at temporary jobsites within the State of Connecticut (non-Agreement state), without obtaining a specific license issued by the NRC or filing NRC Form-241, at least three days before engaging in such activity.
EA-11-270 | Morpho Detection, Inc. | Materials | 2012-04-10 | On April 10, 2012, the NRC issued a Notice of Violation to Morpho Detection, Inc. (MDI), for a Severity Level III problem. The violations involved the licensee’s failure to: 1) file NRC Form 241 “Report of Proposed Activities in Non-Agreement States,” at least three days prior to engaging in licensed activities within NRC jurisdiction, as required by 10 CFR 150.20(b); and 2) store and use the byproduct material under a Agreement State license for a period of less than 180 days in a calendar year, as required by 10 CFR 150.20(b)(4). Specifically, between 2007 and 2011, on multiple occasions, MDI, a Massachusetts Agreement State license, engaged in activities in non-agreement states without obtaining a specific license issued by the NRC or filing NRC Form-241 as required. In addition, the material was stored and used in non-agreement states for periods greater than 180 days in any calendar year.
EA-12-014 | Department of the Army (Redstone Arsenal, AL) | Materials | 2012-04-05 | On April 5, 2012, the NRC issued a Notice of Violation to the Department of the Army (Army), for a Severity Level III violation. The violation involved Army’s failure to provide a radiation monitor that was equipped with personnel access door locks to prevent access to the radiation room of the panoramic irradiator at the Redstone Arsenal facility, when radiation levels were high, as required by 10 CFR 150.20(b). Specifically, from September 24, 1996 to February 17, 2012, the Army’s radiation room personnel access door was not integrated with the radiation monitor to prevent the door from opening when radiation levels were high.
EA-11-242 | InstroTek, Inc. | Materials | 2012-03-30 | On March 30, 2012, the NRC issued a Notice of Violation to InstroTek/CPN International (CPN) for a Severity Level III problem. The violations involved licensee’s failure to: 1) obtain a specific license to export byproduct materials to embargoed destinations as required by 10 CFR110.5; and 2) submit annual reports of americium exports as required by 10 CFR110.23(b) (currently 110.54(b)). Specifically, on November 20, 2008, and May 5, 2010, CPN exported americium-241 and cesium-137 byproduct materials subject to NRC licensing jurisdiction, to embargoed destinations (Iraq and Sudan), without a specific license as required. Also between 2000 and 2009, CPN exported americium and failed to file the required annual reports.
EA-11-138 | Humboldt Scientific, Inc. | Materials | 2012-03-08 | On March 8, 2012, the NRC issued a Notice of Violation to Humboldt Scientific, Inc. (HSI) for a Severity Level III problem. The violations involved a failure to obtain appropriate license authorization to export byproduct materials to embargoed destinations and a failure to submit annual reports of americium exports in accordance with 10 CFR 110.54(b). Specifically, on May 6, 2005, May 7, 2008, June 26, 2008, and July 31, 2008, HSI exported americium-241 and cesium-137 byproduct materials subject to NRC licensing jurisdiction, to embargoed destinations of Iraq and Sudan respectively, without a specific license as required by 10 CFR 110.5 and HSI failed to make annual reports of americium exports for calendar years 2000-2009, during which years americium exports were performed.
EA-11-233 | Dakota Panel - Rapid City, South Dakota | Materials | 2012-02-07 | On February 7, 2012, the NRC issued a Notice of Violation to Dakota Panel for a Severity Level III violation involving the licensee's failure to identifying an individual as the Radiation Safety Officer (RSO) on its license, as required by License Condition 12. Specifically, from January 2010 until September 23, 2011, the licensee failed to have an individual named on its license in the RSO position or any qualified individual as RSO.
EA-09-328 | Roxar Flow Measurement, Inc. | Materials | 2012-02-02 | On February 2, 2012, the NRC issued a Notice of Violation to Roxar Flow Measurement, Inc., for a Severity Level III violation involving the failure to only transfer byproduct material to persons authorized to receive such byproduct material in accordance with 10 CFR 30.41(a) and (b)(5). Specifically, on numerous occasions between September 2003 and August 2007, the licensee transferred fixed gauges containing byproduct material to persons not authorized to receive byproduct material under the terms of a specific license or a general license issued by the Commission or an Agreement State.
EA-11-098 | S&R Engineering S.E. | Materials | 2012-01-13 | On January 13, 2012, the NRC issued a Notice of Violation and Proposed Imposition of a Civil Penalty in the amount of $14,000 to S&R Engineering (S&R) for a Severity Level (SL) III problem and two SL III violations. The SL III problem involved two violations: 1) S&R’s failure to comply with or respond to an NRC Order, as required by 10 CFR 2.202(b); and 2) S&R provided information to the NRC that was not complete and accurate in all material respects as required by 10 CFR 30.9(a). Specifically, as of January 13, 2012, S&R has not submitted an answer to the order (which was required by November 28, 2009), has not paid the license fee, and has not disposed of or transferred its licensed nuclear material to an authorized recipient. On August 3, 2010, the S&R president informed the NRC that S&R had transferred its portable moisture density gauge containing radioactive sources to another NRC licensee when S&R still possessed the gauge. The two additional SL III violations involved S&R’s failure to afford the NRC an opportunity to inspect materials, activities, and records under the regulations as required by 10 CFR 19.14(a) and S&R’s failure to use a minimum of two independent controls that form tangible barriers to secure portable gauge from unauthorized removal, when the portable gauge was not under S&R’s direct control and constant surveillance as required by 10 CFR 30.34(i). Specifically, on August 3, 2010, S&R provided the NRC inaccurate information about the location of its licensed material, thereby preventing inspection of S&R’s licensed activities and the gauge has been stored inside of its shipping case, which was located in an unlocked closet of the locked S&R office, providing only one barrier.
EA-11-222 | Universal Product Concepts, Inc. | Materials | 2012-01-09 | On January 9, 2012, the NRC issued a Notice of Violation and Proposed Imposition of a Civil Penalty in the amount of $7,000.00, to Universal Product Concepts, Inc. (UPC) for a Severity Level III problem. The violations involved a willful transfer of smoke detectors containing byproduct material (americium-241) without the NRC license as required by 10 CFR 30.3(a) and an import of material into United States without having the required license for possession of the material as required by 10 CFR 110.5. Specifically, from May to July 2010, UPC imported and transferred approximately 19,423 smoke detectors containing byproduct material without the required NRC licenses authorizing such imports and transfers.
EA-11-228 | Regents of the University of Michigan | Materials | 2012-01-06 | On January 6, 2012, the NRC issued a Notice of Violation to the Regents of the University of Michigan for a Severity Level III violation involving the failure to develop, implement, and maintain written procedures to provide high confidence that each administration was in accordance with the written directive as required by 10 CFR 35.41(a). In accordance with 10 CFR 35.41(b)(2), the procedures required by 10 CFR 35.41(a) must address verifying that the administration is in accordance with the treatment plan, if applicable, and the written directive. Specifically, on March 9, 2011, the licensee administered a yttrium-90 TheraSphere™ liver treatment, but the licensee’s procedures did not require verifying that the administration of byproduct material was in accordance with the applicable treatment plan and written directive.
EA-11-219 | Lincoln University of Missouri | Materials | 2011-12-19 | On December 19, 2011, the NRC issued a Notice of Violation to Lincoln University of Missouri for a Severity Level III problem involving multiple violations of license conditions and NRC regulations. Specifically, the licensee failed to: (1) ensure that the individual named on the NRC license fulfilled the responsibilities of the RSO between May 2009 and August 18, 2011; (2) conduct a physical inventory every 6 months to account for all sources and/or devices received and possessed under the license between May 2009 and August 8, 2011; (3) notify the NRC in writing within 60 days of no longer conducting principal activities for a period of 24 months; (4) maintain records of receipt of radioactive materials for as long as the material was possessed as well as maintain disposal records until termination of the NRC license; and (5) comply with the applicable requirements for performing leak tests and inventories of generally licensed devices.
EA-11-086 | International Cyclotron, Inc. | Materials | 2011-12-19 | On December 19, 2011, the NRC issued a Notice of Violation and Proposed Imposition of a Civil Penalty in the amount of $7000, and an Order suspending licensed activities within 60 days, to International Cyclotron, Inc. (ICI), for a Severity Level III violation of 10 CFR 30.35. The violation involved ICI’s failure to provide a decommissioning funding plan. Specifically, on August 20, 2009, ICI was issued an NRC license authorizing the possession and use of unsealed byproduct material of applicable quantities set forth in Appendix B to 10 CFR Part 30 and ICI has not provided a decommissioning funding plan that contains a signed original of the financial instrument obtained to provide financial assurance for decommissioning, as required by 10 CFR 30.35. Further, based on ICI’s failure to fully and timely respond to repeat NRC requests for information, and to compel ICI to comply with NRC regulations, the NRC issued an Order Suspending Licensed Activities (Order). According to this Order, if ICI does not submit to the NRC an acceptable financial assurance instrument within 60 days of the date of the Order, ICI is required to suspend all activities authorized under its License. This Order will remain in effect until ICI submits a financial assurance instrument and the NRC informs ICI that the instrument is accepted.
EA-11-146 | Cardinal Health PET Manufacturing Services, Inc. | Materials | 2011-11-09 | On November 9, 2011, the NRC issued a Notice of Violation to Cardinal Health PET Manufacturing Services, Inc., for a Severity Level III violation involving the failure to monitor the occupational exposure to an adult who was likely to receive, in one year from sources external to the body, an extremity dose in excess of 5 rem as required by 10 CFR 20.1502(a)(1). Specifically, on June 16, 2010, a Cardinal Health PET Manufacturing Services employee removed his extremity (ring) dosimetry on two separate occasions prior to handling a chemical cartridge containing approximately 4 curies of fluorine-18.
EA-11-209 | Warner Brothers, LLC | Materials | 2011-11-08 | On November 8, 2011, the NRC issued a Notice of Violation to Warner Brothers, LLC for a Severity Level III violation involving the failure to file NRC Form 241 “Report of Proposed Activities in Non-Agreement States,” at least three days prior to engaging in licensed activities within NRC jurisdiction, as required by 10 CFR 150.20. Specifically, on December 6, 2006, and July 7, 2008, Warner Brothers LLC, which only holds a Massachusetts license, used a portable gauge containing a sealed source, at temporary jobsites within the State of Connecticut, without obtaining a specific license issued by the NRC or filing NRC Form-241 with the NRC, as required.
EA-11-061 | Escanaba Paper Company | Materials | 2011-10-17 | On October 17, 2011, the NRC issued a Notice of Violation to Escanaba Paper Company for a Severity Level III violation involving the failure to ensure that only persons specifically licensed by the U.S. Nuclear Regulatory Commission (NRC) or an Agreement State perform services involving the dismantling and non-routine maintenance or repair of components related to the radiological safety of the gauge. Specifically, on May 9, 2011, the licensee performed non-routine maintenance on a fixed level gauge by using a rod to change the position of the shutter contrary to NRC License No. 21-17630-01, Condition 17.B. The licensee was not specifically licensed by the NRC or an Agreement State to perform this service.
EA-11-071 | Construction Testing and Engineering, Inc. | Materials | 2011-09-26 | On September 26, 2011, the NRC issued a Notice of Violation (Notice) and Proposed Imposition of Civil Penalty in the amount of $1,750 to Construction Testing and Engineering, Inc. (CTE), for a Severity Level III violation. The violation involved the failure to maintain a minimum of two independent physical controls that formed a tangible barrier to secure a portable gauge from unauthorized removal during a period when the gauge was not under direct control or surveillance. Specifically, on October 26, 2010, CTE stored a portable gauge in its locked transport container, inside of the trunk of a vehicle at a temporary jobsite. The gauge was secured with only a single independent physical control (the lock to the trunk). The vehicle was stolen on that date and the gauge inside was removed from the storage location by defeating only one barrier. Additionally, the Notice issued a Severity Level III violation involving the failure to file NRC Form 241 “Report of Proposed Activities in Non-Agreement States,” at least three days prior to engaging in licensed activities within NRC jurisdiction, as required by 10 CFR 150.20. Specifically, between September 14, 2010, and October 26, 2010, CTE, which held a Virginia license, engaged in activities involving the use of a portable gauge containing sealed sources at a temporary site in District of Columbia, an area of exclusive federal jurisdiction without obtaining a specific license issued by the NRC or filing NRC Form-241 with the NRC, as required.
EA-11-179 | Associated Specialities, Inc. | Materials | 2011-09-21 | On September 21, 2011, the NRC issued a Notice of Violation to Associated Specialists, Inc. (ASI), for a Severity Level III problem. The violations involved the licensee’s failure to: (1) limit operation with a temporary radiation safety officer (RSO) to a period of 60 days, in accordance with 10 CFR 35.24(c); and (2) ensure that its authorized user (AU) provided adequate supervision to licensee staff who were involved in the receipt, possession, use, transfer or preparation of byproduct material, in accordance with 10 CFR 35.27. Specifically, after ASI’s RSO left the company on June 8, 2010, the AU functioned as the temporary RSO until October 13, 2010, a period greater than 60 days. And from August 16, 2009 until April 19, 2011, the AU had limited oversight of the program, such that ASI personnel under the supervision of the AU had not spoken to him and had not received instructions associated with ASI’s written radiation protection procedures, NRC regulations, ASI’s license conditions, and the requirement that supervised individuals follow the instructions of the supervising authorized user for medical uses of byproduct material.
EA-11-163 | William Beaumont Hospital | Materials | 2011-09-02 | On September 2, 2011, the NRC issued a Notice of Violation to William Beaumont Hospital for a Severity Level III violation involving the failure to develop written procedures to provide high confidence that each administration was in accordance with the written directive as required by 10 CFR 35.41(a). Specifically, as of May 5, 2011, the licensee’s written procedures for yttrium-90 treatments did not specify how personnel should administer a treatment using a fine bore catheter and a high concentration of microspheres in order to prevent blockage within the catheter.
EA-11-165 | Crittenton Hospital | Materials | 2011-09-02 | On September 2, 2011, the NRC issued a Notice of Violation to Crittenton Hospital for a Severity Level III violation involving the failure to develop written procedures to provide high confidence that each administration was in accordance with the written directive as required by 10 CFR 35.41(a). Specifically, between September 2009 and January 2011, the licensee failed to address in its written procedure the need to verify that the step size used in the treatment plan was correctly translated into the high dose rate (HDR) remote afterloader unit. As a result, the device’s control unit default step size of 2.5 mm was used instead of the 5 mm used in the treatment planning system.
EA-11-145 | Carmeuse Lime, Inc. | Materials | 2011-09-02 | On September 2, 2011, a Notice of Violation was issued to Carmeuse Lime, Inc., for a Severity Level III Problem involving three violations. The first violation involved the failure to have the individual specifically authorized by Condition 12.A of the license fulfill the duties and responsibilities as the Radiation Safety Officer (RSO). Specifically, the individual left the company in 2007, and the licensee failed to appoint a new RSO and amend its license. The second violation involved the failure to conduct a physical inventory every six months, or at other intervals approved by the NRC, to account for all sealed sources and/or devices received and possessed under the license as required by Condition 15 of the license. The third violation involved the failure to test each gauge for the proper operation of the on-off mechanism (shutter) and indicator, if any, at intervals not to exceed six months or at intervals specified in the certificate of registration as required by Condition 16.B of the license.
EA-10-161 | Professional Service Industries, Inc. | Materials | 2011-08-18 | On August 18, 2011, the NRC issued an Immediately Effective Confirmatory Order to Professional Service Industries, Inc., confirming commitments reached as part of an alternative dispute resolution (ADR) mediation settlement agreement. The NRC identified eight apparent safety violations as well as apparent security-related violations involving the performance of industrial radiography in the Rock Springs, Wyoming, area. In addition, the NRC indicated that willfulness on the part of an office manager and a radiographer appeared to have been a factor in two of the apparent violations. PSI made no admission that they deliberately violated any NRC requirement. As part of the agreement, PSI agreed to take several corrective actions involving increased management oversight and individual accountability including, but not limited to: (1) developing and implementing a disciplinary program managed by the corporate staff that provides a graded approach for radiation safety and security infractions; (2) enhanced routine and refresher training for staff; (3) annual safety culture training for Radiation Safety Officers; (4) enhanced annual audits of the Radiation Safety Program; and (5) advance notification if PSI will be working in NRC jurisdiction under reciprocity. PSI also agreed that a Confirmatory Order with a Notice of Violation and $15,000 civil penalty would be issued in order to avoid further action by the NRC. Prior to any enforcement action by the NRC, the licensee voluntarily terminated its NRC license for radiography but maintains Agreement State licenses for radiography and an NRC license for other non-radiographic, regulated activities.
EA-10-129 | Department of the Army - U.S. Army Installation Management Command | Materials | 2011-08-01 | On August 1, 2011, the NRC issued a Notice of Violation to the Department of the Army (Army) for a Severity Level III violation involving the failure to implement 10 CFR 40.3, "License Requirements." Specifically, from April 1978, when NRC license SUB-459 expired, to the present, the Army continued to possess depleted uranium (DU) associated with the Davy Crockett weapons system in the form of spent fragments of spotting rounds (obtained from 1962 to 1968, and expended prior to 1968) at firing ranges located at the Army's two installations in Hawaii, Schofield Barracks and Pohakuloa Training Area. In addition to the two installations in Hawaii, the Army has also identified the presence of spent DU spotting rounds at other Army installations across the United States.
EA-11-109 | Liberty Hospital | Materials | 2011-07-22 | On July 22, 2011, the NRC issued a Notice of Violation to Liberty Hospital for a Severity Level III violation involving the failure to develop written procedures to provide high confidence that each administration was in accordance with the written directive as required by 10 CFR 35.41(a). Specifically, as of October 6, 2010, the licensee’s procedure did not require the position of the prostate to be verified prior to seed placement. As a result, the prostate received 16.9 Gray (Gy) as opposed to the prescribed dose of 125 Gy.
EA-10-258 | Bozeman Deaconess Hospital | Materials | 2011-07-08 | On July 8, 2011, a Confirmatory Order (effective immediately) was issued to Bozeman Deaconess Hospital (BDH) to confirm commitments made as a result of an Alternative Dispute Resolution (ADR) settlement agreement. During inspection and investigation, NRC identified two willful violations. The violations involved the failures to secure licensed materials from unauthorized removal or access as required by 10 CFR 20.1801 and to control and maintain constant surveillance of licensed material as required by 10 CFR 20.1802. In response to these violations, the licensee requested ADR. BDH agreed to take a number of actions as part of this Confirmatory Order: providing training to hospital staff and managers involved in NRC licensed activities by an independent third-party organization; modifying the internal requirements for new worker training and for its annual refresher training; developing and implementing a procedure that allows hospital employees and contractors to raise radiation safety concerns to hospital management; and paying a civil penalty in the amount of $3,500.
EA-11-022 | Luzenac America, Inc. | Materials | 2011-07-07 | On July 7, 2011, the NRC issued a Notice of Violation and Proposed Imposition of Civil Penalty in the amount of $8,500 to Luzenac America, Inc., for a Severity Level III violation involving the failure to transfer a device containing byproduct material to a licensee authorized to receive it, as required by 10 CFR 31.5(c)(8)(i). Specifically, as of December 2, 2010, Luzenac transferred a fixed nuclear gauge containing byproduct material to a recycling company that was not authorized to receive it.
EA-11-115 | Charleston Radiation Therapy Consultants, PLLC | Materials | 2011-06-30 | On June 30, 2011, the NRC issued a Notice of Violation to Charleston Radiation Therapy Consultants, PLLC (CRTC) for a Severity Level III violation involving the failure to meet the physical presence requirements of 10 CFR 35.615(f)(2) during high dose radiation (HDR) treatments. Specifically, on an indeterminate number of occasions on and prior to April 28, 2011, neither a CRTC authorized user (AU), nor a physician under the supervision of an AU, was physically present during continuation of patient treatments involving the HDR unit.
EA-11-088 | Henry Ford Macomb Hospital | Materials | 2011-06-24 | On June 24, 2011, the NRC issued a Notice of Violation to Henry Ford Macomb Hospital for a Severity Level III violation involving the failure to develop, implement, and maintain written procedures to provide high confidence that each administration is in accordance with the written directive as required by 10 CFR 35.41(a). Specifically, as of December 9, 2010, the licensee’s procedure did not include steps to verify that the transfer tube assembly used at the time of the administration was the same length as the one identified in the treatment plan implementing the written directive. This resulted in four patients receiving radiation doses to areas not included within the planned treatment area.
EA-11-100 | Owensby and Kritikos, Inc. | Materials | 2011-06-08 | On June 8, 2011, the NRC issued a Notice of Violation to the Owensby and Kritikos, Inc., for a Severity Level III violation involving the licensee’s failure to control and maintain constant surveillance of the licensed material in an unrestricted area as required by 10 CFR 20.1801 and 20.1802. Specifically, during inspection on July 29, 2010, the radiography camera was found on the floor of the unlocked darkroom and no radiography personnel were maintaining constant surveillance over the material.
EA-11-094 | Mercy Hospital | Materials | 2011-06-08 | On June 8, 2011, the NRC issued a Notice of Violation to Mercy Hospital for a Severity Level III violation involving the failure to develop, implement, and maintain written procedures to provide high confidence that each administration is in accordance with the written directive as required by 10 CFR 35.41(a). Specifically, between June 18, 2008 and February 23, 2011, the licensee performed approximately 200 high dose-rate (HDR) remote afterloader administrations requiring written directives, and failed to develop written procedures to provide high confidence that each administration was in accordance with the written directive.
EA-10-231 | Alaska Industrial X-Ray, Inc. | Materials | 2011-06-07 | On June 7, 2011, a Confirmatory Order (effective immediately) was issued to Alaska Industrial X-Ray Inc. (AIX) to confirm commitments made as a result of an Alternative Dispute Resolution (ADR) settlement agreement. During inspection and investigation, NRC identified a deliberate violation associated with two conditions of the Order Modifying License (EA-08-196): (1) failure to have an independent consultant or contractor perform field audits and submit the audit reports to AIX, and the NRC, as required by Condition 1 of the Order, from August 2008 through March 2010 and (2) failure to have an independent consultant or a contractor evaluate the effectiveness of AIX’s radiation safety program, as required by Condition 3 of the Order, from September 2008 through October 2010. In response to these violations, the licensee requested ADR. As part of the agreement, AIX agreed to take a number of actions including training for all AIX employees engaged in licensed activities on what is meant by willfulness, conducting an annual review of its radiation safety and compliance program by an independent auditor, conducting quarterly audits of AIX radiographers as they perform radiography, and paying a civil penalty in the amount of $1,000.
EA-11-037 | Providence Hospital | Materials | 2011-05-17 | On May 17, 2011, the NRC issued a Notice of Violation to Providence Hospital for a Severity Level III violation involving the failure to develop written procedures to provide high confidence that each administration was in accordance with the written directive as required by 10 CFR 35.41(a). Specifically, as of August 30, 2010, the licensee’s brachytherapy procedure did not provide high confidence that the needles would be inserted to the right depth as the licensee did not require the use of available means such as biological or needle markers.
EA-11-009 | Del Valle Group | Materials | 2011-05-11 | On May 11, 2011, the NRC issued a Notice of Violation to Del Valle Group (DVG) for a Severity Level III violation involving the failure to obtain authorization in a specific NRC license to own and possess three portable moisture density gauges, as required by 10 CFR 30.3(a). Specifically, from November 30, 2008 through October 28, 2010, DVG owned and/or possessed byproduct material (discrete radium-226 sources contained in three portable moisture density gauges) without authorization in a specific or general license issued in accordance with NRC regulations.
EA-11-016 | Community Hospitals of Indiana | Materials | 2011-04-20 | On April 20, 2011, the NRC issued a Notice of Violation to the Community Hospitals of Indiana for a Severity Level III violation involving the failure to fully implement procedures to provide high confidence that a brachytherapy treatment was in accordance with the written directive as required by 10 CFR 35.41(a). Specifically, on September 30, 2010, an authorized medical physicist missed a step in the procedure that established the starting position for the high dose remote afterloader brachytherapy treatment. The failure to implement this step resulted in a medical event.
EA-11-027 | West Virginia University Hospitals, Inc. | Materials | 2011-03-25 | On March 25, 2011, the NRC issued a Notice of Violation to West Virginia University Hospitals Inc. (WVUH) for a Severity Level III violation involving the failure to notify the NRC Operations Center by telephone no later than the next calendar day after discovery of the medical event as required by 10 CFR 35.3045(c). Specifically, WVUH did not notify the NRC until July 7, 2010, after discovering that a dose administered on January 20, 2010 differed from the prescribed dose.
EA-11-010 | Oakwood Hospital - Annapolis Center | Materials | 2011-03-04 | On March 4, 2011, the NRC issued a Notice of Violation to Oakwood Hospital – Annapolis Center for a Severity Level III problem involving: (1) the licensee’s usage of a dose that differed from the prescribed dose by more than 20 percent which is contrary to 10 CFR 35.63(d); and (2) the failure to verify that the assayed dosage was within 10 percent of the prescribed activity as required by License Condition 15.A. Specifically, the licensee administered approximately 124.5 millicuries of sodium pertechnetate technetium-99m (Tc-99m) to a patient instead of the prescribed dosage of 10 millicuries of Tc-99m tetrofosmin, a difference in excess of 20 percent. The licensee failed to verify that it had the correct syringe which resulted in the incorrect radiopharmaceutical and dosage being administered to the patient.
EA-10-100 | Mattingly Testing Services, Inc. | Materials | 2011-02-22 | On February 22, 2011, the NRC ASLB Hearing Board issued a Memorandum and Order accepting a Settlement and Dismissing the Hearing Proceeding in the matters of Mattingly Testing Services, Inc., (MTS) Order Revoking License (EA-10-100) and Mark M. Ficek Order Prohibiting Engagement in NRC-licensed Activities (IA-10-028) that were both issued on September 2, 2010. Specifically, the NRC staff and two parties, employees of MTS, who had requested a hearing on the September 2 Orders had agreed to a settlement on February 4, 2011, in lieu of continuing the hearing proceeding. The Settlement Agreement was forwarded to the ASLB and approved. The February 22, 2011 Board Order superseded the September 2, 2010 Order Revoking License issued to MTS and the Order Prohibiting Engagement in NRC-licensed Activities issued to Mark M. Ficek. The Order and Settlement included the following terms and conditions: (1) the MTS license remains revoked and parties agree that it will not be reinstated; (2) Mr. Ficek is prohibited from engaging in NRC-licensed activities until September 2, 2017 (the settlement further defines NRC-licensed activities); (3) for a three year period after September 2, 2017, Mr. Ficek is required to notify NRC of employment involving NRC-licensed activities; (4) Mr. Ficek is allowed non-controlling ownership in an NRC licensee, subject to conditions specified in the settlement prohibiting Mr. Ficek’s engagement in licensed activities; (5) Mr. Ficek is allowed to own and/or sell the radiographic exposure devices that were listed on the former MTS license, subject to conditions specified in the settlement; and, (6) that all parties agree that all further procedural steps before the ASLB and any right to challenge or contest the validity of the Board Order entered into in accordance with the Settlement Agreement, and all rights to seek judicial review or otherwise contest the validity of the Board Order are expressly waived.
EA-11-008 | Bristol Hospital, Inc. | Materials | 2011-02-17 | On February 17, 2011, the NRC issued a Notice of Violation to Bristol Hospital, Inc. for a Severity Level III violation involving the failure to notify the NRC Operations Center of two medical events, in accordance with 10 CFR 35.3045(c), which requires a report within the next calendar day of discovery. Specifically, on January 12, 2010, Bristol Hospital experienced two medical events involving patients receiving less than the intended prescribed dose during two different permanent prostrate brachytherapy seed implants. The administered doses differed from the prescribed doses by 50 rem to an organ or tissue, and the total doses differed by greater than 20 percent from the prescribed doses. As of March 1, 2010, Bristol Hospital personnel had information available to determine that these medical events had occurred on January 12, 2010, and should have therefore reported the events by March 2, 2010. However, the licensee did not verbally report the events to the NRC until June 2, 1010 following NRC questioning of the circumstances during an inspection.
EA-10-272 | Carro & Carro Enterprises, Inc. | Materials | 2011-02-11 | On February 11, 2011, the NRC issued a Notice of Violation to Carro & Carro Enterprises, Inc. (CCE) for a severity level III violation involved CCE’s failure to obtain authorization in a specific NRC license to own and possess the portable moisture density gauge, which contained byproduct material. Specifically, from November 30, 2008, through June 28, 2009, CCE owned and/or possessed byproduct material, a discrete radium-226 source contained in a portable moisture density gauge, without authorization in a specific or general license issued in accordance with NRC regulations.
EA-10-077 | Superior Well Services, Ltd. | Materials | 2011-02-08 | On February 8, 2011, the NRC issued an Immediately Effective Confirmatory Order to the Superior Well Services, Ltd. (SWS) to confirm commitments made as a result of an Alternate Dispute Resolution (ADR) mediation session held on January 4, 2011. The licensee requested ADR following the NRC’s October 21, 2010, Notice of Violation and Proposed civil penalty of $34,000, for five violations that were categorized into two severity level (SL) III problems. The first SL III problem involved three violations related to the temporary loss of two radioactive well logging sources. The second SL III problem involved two violations related to the deliberate failure to conduct radiological surveys and the creation of inaccurate survey records. As part of the agreement, SWS took number of actions addressing all of the violations, to ensure that the corrective actions are effective, and to ensure that lessons learned from these events are extended to the well logging industry. In addition, SWS took several corrective actions prior to the ADR mediation session. In recognition of SWS’s proposed extensive corrective actions, in addition to corrective actions already taken, the NRC agreed to reduce the civil penalty originally proposed to $17,000.
EA-10-182 | Sanford Medical Center | Materials | 2010-12-10 | On December 10, 2010, the NRC issued a Notice of Violation to Sanford Medical Center for a Severity Level III violation involving the failure to secure the high dose-rate remote (HDR) afterloader brachytherapy unit in accordance with License Condition 19.A and Section 3.3.1.1 of Standard Operating Procedure, NM-X2, “Radiation Safety Procedures for the Nucletron Microselectron HDR, Version 2.” Specifically, on June 15 through July 29, 2010, the licensee failed to secure the HDR afterloader unit from unauthorized removal or access from its storage area when the unit was not in use because a mechanical locking mechanism failed to function as designed, leaving the unit unsecured.
EA-10-041 | AREVA NP, Inc. | Materials | 2010-12-02 | On December 2, 2010, the NRC issued a Notice of Violation and a Confirmatory Order to AREVA NP, Inc., as a result of an Alternate Dispute Resolution settlement for a violation of 10 CFR 71.5(a) and 49 CFR 172.204(a) involving inaccurate transportation records for several export shipments of special nuclear material (SNM). Specifically, on December 9, 2009, and March 11 and 18, 2009, an AREVA employee deliberately altered (falsified) the reference and date stamp on three documents entitled “Approval to Transit a UK [United Kingdom] Port” associated with the export of SNM from the United States to Germany by Areva NP, Inc.
EA-10-171 | St. Francis Hospital and Medical Center | Materials | 2010-11-10 | On November 10, 2010, the NRC issued a Notice of Violation to St. Francis Hospital and Medical Center (St. Francis) for a Severity Level III violation involving the failure to meet the physical presence requirements of 10 CFR 35.615(f)(2) during high dose radiation (HDR) treatments. Specifically, on July 1, 2010 and other occasions prior to that date, a St. Francis authorized medical physicist was not physically present during initiation and continuation of patient treatments involving the HDR unit.
EA-10-140 | Walter Reed Army Medical Center | Materials | 2010-10-25 | On October 25, 2010, the NRC issued a Notice of Violation to the Walter Reed Army Medical Center (WRAMC), for a Severity Level III problem. The violations involved the licensee’s failure to control and maintain constant surveillance of the licensed material in an unrestricted area as required by 10 CFR 20.1802 and failure to conduct operations so that the dose in any unrestricted area from external sources did not exceed 0.002 rem (0.02 millisievert) in any one hour. Specifically, between May 1 and 3, 2010, WRAMC did not control and maintain constant surveillance of packages containing licensed radioactive materials, which were improperly stored by WRAMC personnel in an unrestricted area under a counter in the concierge workstation, resulting in a dose greater than 0.002 rem in any one hour within the first floor lobby of the WRAMC.
EA-10-077 | Superior Well Services, Ltd. | Materials | 2010-10-21 | On October 21, 2010, the NRC issued a Notice of Violation and Proposed Imposition of Civil Penalty in the amount of $34,000 to the Superior Well Services, Ltd. (SWS), for two Severity Level III problems. The violations involved the licensee’s failure to: (1) secure a shipment of radioactive materials on a public highway to prevent shifting during normal transportation conditions in accordance with 10 CFR 71.5(a); control and maintain constant surveillance of the licensed material in an unrestricted area as required by 10 CFR 20.1802; and notify the NRC of the missing licensed material in accordance with 10 CFR 20.2201(a); (2) conduct required radiological surveys of vehicles before transporting licensed material in accordance with10 CFR 39.67, and the deliberate falsification of survey records for the vehicles. Specifically, on September 20, 2008, while transporting licensed material on a public highway, SWS did not secure a shipment of radioactive materials, and failed to control and maintain constant surveillance of the licensed material for at least ninety minutes, until SWS located and retrieved the sources, and also failed to notify the NRC of the missing licensed material until July 23, 2009, ten months after identifying the event. In addition, on an unspecified number of occasions prior to July 22, 2010, before transporting licensed materials, SWS did not make radiation surveys of the position occupied by each individual in the vehicle and of the exterior of the vehicle used to transport the licensed materials and recorded survey results that were obtained by copying from previous survey records.
EA-10-135 | Analytical Bio-Chemistry Laboratories, Inc. | Materials | 2010-10-13 | On October 13, 2010, the NRC issued a Notice of Violation to Analytical Bio-Chemistry Laboratories, Inc., for a Severity Level III problem involving two violations. The first violation involves the failure to notify the NRC in writing within 60 days of the decision to permanently cease principal activities in any separate building that contains residual radioactivity and is unsuitable for release as required by 10 CFR 30.36(d)(2). Specifically, as of February 2010, the licensee decided to permanently cease principal activities in two buildings that contained residual radioactivity, and the NRC was not notified until June 30, 2010, and July 14, 2010. The second violation involves the failure to submit a decommissioning plan and receive NRC approval of procedures used in aggressive remediation activities as required by 10 CFR 30.36(g). Specifically, on June 22, 2010, the licensee demolished and removed contaminated countertops, floors, and fume hoods with associated ventilation ducts. These types of activities involved techniques not routinely applied during cleanup or maintenance operations such that there was the potential for health and safety impacts to the workers.
EA-10-174 | McConnell Dowell (American Samoa), Ltd. | Materials | 2010-10-06 | On October 6, 2010, the NRC issued a Notice of Violation to McConnell Dowell (American Samoa), Ltd., for a Severity Level III violation involving the receipt, possession, and usage of byproduct material without authorization from a specific or general license as required by 10 CFR 30.3(a). Specifically, as early as 2008 to July 25, 2010, the licensee received, possessed and used two portable nuclear gauges in American Samoa, an area of exclusive Federal jurisdiction, without a specific license issued by the U.S. Nuclear Regulatory Commission.
EA-10-100 | Mattingly Testing Services, Inc. | Materials | 2010-09-02 | On September 2, 2010, the NRC issued an Order Revoking License (Immediately Effective) to Mattingly Testing Services, Inc., for multiple violations of NRC requirements. Specifically, (1) on various dates beginning on May 3, 2009, the licensee, in part deliberately, failed to implement specified actions required by Confirmatory Order (EA-08-271) involving: (i) conducting an assessment of the radiation safety program, (ii) providing initial safety training to the licensee staff, (iii) ensuring that an independent consultant’s recommended program improvements were provided within 30 days of completing the required reviews, (iv) providing the independent consultant’s 2009 annual audit results to the NRC, (v) conducting the initial field audit of radiography operations by the independent consultant by May 3, 2009, and (vi) submitting a required license amendment request by May 3, 2009; (2) from May 13, 2006 through September 9, 2009, the licensee deliberately failed to establish and maintain a prearranged response plan with the Local Law Enforcement Agency (LLEA) in accordance with Increased Controls Order (EA-05-090), Attachment B, Section IC-2(b); (3) on March 6, 2007, the licensee president deliberately failed to provide complete and accurate information to an NRC inspector in accordance 10 CFR 30.9, regarding the licensee’s effort to establish a prearranged response plan with the LLEA; (4) on October 22, 2009, while under oath, the licensee president deliberately failed to provide complete and accurate information to an NRC investigator in accordance with 10 CFR 30.9 regarding the licensee’s effort to establish a prearranged response plan with the LLEA; (5) on July 4, 16, and August 29-30, 2009, the licensee failed to maintain a dependable means to detect, assess, and respond to unauthorized access to radioactive materials in accordance with Increased Controls Order (EA-05-090) Appendix B, Section IC-2(c); (6) on June 22, 2009, the licensee failed to properly secure a radiographic exposure device for transport with proper blocking and bracing to prevent loss during transit in accordance with 10 CFR 20.1802, 10 CFR 34.35(d), and 10 CFR 71.5 that led to the device being lost in the public domain; and, (7) on June 22, 2009, the licensee willfully failed to immediately notify the NRC about the lost radiographic exposure device in accordance with 10 CFR 20.2201.
EA-10-085 | St. Louis Testing Laboratories, Inc. | Materials | 2010-08-31 | On August 31, 2010, the NRC issued a Notice of Violation to St. Louis Testing Laboratories, Inc., for a Severity Level III violation involving the failure to ensure each individual who acts as a radiographer or a radiographer's assistant wears a direct reading dosimeter, an operating alarm rate meter, and a personal dosimeter at all times during radiographic operations as required by 10 CFR 34.47(a). Specifically, on October 22, 2009, a radiographer inadvertently left his personal dosimeter in a tool bag inside a permanent radiographic cell while performing radiographic shots.
EA-10-138 | Universal Engineering Sciences, Inc. | Materials | 2010-08-27 | On August 27, 2010, the NRC issued a Notice of Violation to Universal Engineering Sciences, Inc. (UES), for a Severity Level III violation involving the failure to file NRC Form 241 “Report of Proposed Activities in Non-Agreement States,” at least three days prior to engaging in licensed activities within NRC jurisdiction, as required by 10 CFR 150.20. Specifically, UES used portable gauges containing sealed sources, at numerous areas of exclusive federal jurisdiction within the States of Florida and Georgia, without obtaining a specific license issued by the NRC or filing NRC Form-241 with the NRC, as required.
EA-09-258 | Basin Electric Power Cooperative | Materials | 2010-08-26 | On August 26, 2010, the NRC issued a Notice of Violation and Proposed Imposition of Civil Penalty in the amount of $24,700 to Basin Electric Power Cooperative. The violations involved: (1) Severity Level (SL) II violation of 10 CFR 20.1301(a)(1) for failure to limit radiation exposure to members of the public to less than 100 millirem in a year, resulting in six members of the public received doses in excess of 100 millirem; (2) SL III violation of 10 CFR 20.1902(e) for failure to conspicuously post caution signs with the words “CAUTION, RADIOACTIVE MATERIAL(S)” or “DANGER RADIOACTIVE MATERIAL(S)” in areas where nuclear gauges were used; (3) SL III violation of 10 CFR 30.50(b)(4) for failure to notify the NRC within 24 hours after the discovery of an unplanned fire on March 8, 2007, that damaged the integrity of a licensed device; and (4) SL III violation of License Condition 21 of Amendment 10 to NRC Materials License 33‑18224‑01 for failure to close and lock the nuclear gauge shutters after plant operations had stopped and prior to allowing welders to begin work, resulting in welders exposed to the direct radiation beam from these nuclear gauges.
EA-10-113 | Chicago Testing Laboratory, Inc. | Materials | 2010-08-24 | On August 24, 2010, the NRC issued a Notice of Violation to Chicago Testing Laboratory, Inc., for a Severity Level III violation involving the possession and usage of byproduct material without authorization from a specific or general license. Specifically, on multiple occasions between July 6, 2006, and August 30, 2009, Chicago Testing Laboratory, Inc., an Agreement State licensee, possessed and used devices containing sealed sources in a non-Agreement State, and was not authorized in either a specific or general license.
EA-10-141 | Christiana Care Health Services | Materials | 2010-08-24 | On August 24, 2010, the NRC issued a Notice of Violation to the Christiana Care Health Services (CCHS), for a Severity Level III violation involving the failure to develop and maintain written procedures to provide high confidence that each administration requiring a written directive was performed in accordance with the written directive as required by 10 CFR 35.41. Specifically, CCHS’s written procedures for high dose rate remote afterloader (HDR) treatments did not: (i) include a quality assurance process to test and evaluate proper functioning of all measurement tools used to determine treatment parameters; and, (ii) specify how personnel should respond when unknown and questionable treatment distances were encountered during HDR simulation measurements. As a result of these procedural inadequacies, a medical event occurred, in which the patient received a dose to unintended tissue and did not receive the prescribed dose to the intended tissue during an HDR treatment conducted between January 18 and January 22, 2010.
EA-10-081 | Department of Veteran Affairs | Materials | 2010-08-23 | On August 23, 2010, the NRC issued a Notice of Violation (Notice) and Proposed Imposition of Civil Penalty in the amount of $39,000 to the Department of Veteran Affairs (VA) for two Severity Level III violations involving: (1) the failure to implement 10 CFR 35.41(a)(2) and 10 CFR 35.41(b)(2) requirements for verifying medical treatments, and (2) the failure to implement 10 CFR 35.3045(c) requirements to report a medical event. Additionally, the Notice issued a Severity Level III violation for three examples of both 10 CFR 35.41(a)(2) and 35.41(b)(2) violations involving five patients at the VA Boston Healthcare System during 2005, which is also beyond the statute of limitations time period such that a civil penalty was not assessed. Specifically, for the first set of violations assessed a civil penalty, several facilities are identified and involve multiple examples of the licensee’s failure to verify that the administration of permanent prostate brachytherapy implants was in accordance with the written directives: (i) the VA Sierra Nevada Health Care System in Reno, Nevada, between September 29, 2005 and October 12, 2008; (ii) the G.V. (Sonny) Montgomery VA Medical Center in Jackson, Mississippi, between May 2007 and February 2008; and, (iii) the VA Boston Healthcare System in Boston, Massachusetts on September 27, 2005. Further, the Notice identifies that the second violation assessed a civil penalty occurred on October 10, 2008, at the VA New York Harbor Healthcare System in Brooklyn, New York, where the licensee failed to make a timely medical event report regarding a permanent prostate brachytherapy implant when the data available at the time indicated otherwise, with the actual treatment dose less than 69 percent of the prescribed dose.
EA-10-066 | Bryan LGH Medical Center (EA-10-066) | Materials | 2010-08-18 | On August 18, 2010, the NRC issued a Notice of Violation to Bryan LGH Medical Center dba Bryan LGH Heart Institute (Bryan Heart), for a Severity Level III violation involving the failure to file NRC Form 241 “Report of Proposed Activities in Non-Agreement States,” at least three days prior to engaging in licensed activities within NRC jurisdiction, as required by 10 CFR 150.20. Specifically, as of December 16, 2009, Bryan Heart, a holder of Nebraska State license, provided mobile nuclear medicine services at a temporary job site in the State of Missouri, a non-Agreement State, without filing a reciprocity submittal for calendar year 2009 with the NRC.
EA-10-110 | Southern Earth Sciences, Inc. | Materials | 2010-07-19 | On July 19, 2010, the NRC issued a Notice of Violation to Southern Earth Sciences, Inc (SES), for a Severity Level III violation involving the failure to file NRC Form 241 “Report of Proposed Activities in Non-Agreement States,” at least three days prior to engaging in licensed activities within NRC jurisdiction, as required by 10 CFR 150.20. Specifically, between January 2008 and April 2009, SES, a holder of a Florida license, stored or used portable gauges in an area of exclusive federal jurisdiction without a specific license issued by the NRC, nor had SES filed a Form-241 with the NRC.
EA-10-069 | Laboratory Testing Services, LLC (EA-10-069) | Materials | 2010-07-06 | On July 6, 2010, the NRC issued a Notice of Violation to Laboratory Testing Services, LLC (LTS) for a Severity Level III problem involving three violations. The first violation involved a failure to confine possession and use of byproduct material to the location authorized by the license, as required by 10 CFR 30.34(c). Specifically, the licensee possessed and used portable gauges at a location not authorized by the license. The second violation involved a failure to have an individual named on the license as a Radiation Safety Officer (RSO), as required by the license. Specially, the RSO named in the license left the company in June 2008, and the licensee failed to have an RSO approved by the NRC. The third violation involved a failure to obtain written consent from the NRC before transferring ownership of LTS to HAKS Material Testing Company (HAKS), as required by 10 CFR 30.34(b). Specifically, on January 14, 2010, LTS transferred ownership control of the license to HAKS without the Commission’s written consent.
EA-10-062 | Earth Engineers, Inc. | Materials | 2010-06-28 | On June 28, 2010, the NRC issued a Notice of Violation to Earth Engineers, Inc., d.b.a. Heynen Engineers (EEI) for a Severity Level III problem involving two violations. The first violation involved a failure to comply with the conditions of the NRC Order Revoking License, issued on June 4, 2009. Specifically, the licensee did not pay fees within 30 days or transfer the licensed material to an authorized recipient within 60 days from the date of the Order. The second violation involved a failure to afford the NRC an opportunity to inspect the EEI facility, as required by 10 CFR 19.14(a). Specifically, on October 7, 2009, the licensee did not provide access to the nuclear portable gauge to inspect the condition of the gauge; and, between November 2, 2009 and January 27, 2010, the NRC made several attempts to contact the licensee, but the licensee did not provide access to the EEI facility.
EA-10-068 | Anthony & Edward Consultants (EA-10-068) | Materials | 2010-06-25 | On June 25, 2010, the NRC issued a Notice of Violation to Anthony & Edwards Consultants (A&E) for a Severity Level III problem invovling three violations. The first violation invovled a failure to comply with the conditions of the NRC Order Revoking License, issued on July 28, 2009. Specifically, the licensee did not pay fees within 30 days or transfer the licensed material to an authorized recipient within 60 days from the date of the Order. The second violation involved a failure to afford the NRC an opportunity to inspect the A&E facility, as required by 10 CFR 19.14(a). Specifically between February 18, 2009 and September 17, 2009, the NRC made several attempts to contact the licensee to visit the facility and to schedule an inspection of licensed activities, but the licensee did not respond to these requests. And the third violation involved a failure to confine storage of licensed material to a location specified on the license, as required by 10 CFR 30.34(c). Specifically, from September 5, 2008 through at least September 30, 2009, the licensee stored the licensed material at a location not authorized by the license.
EA-10-044 | ArcelorMittal USA, Inc. | Materials | 2010-06-02 | On June 2, 2010, the NRC issued a Notice of Violation to ArcelorMittal USA, Inc., for a Severity Level III violation involving the failure to ensure that only persons who have completed the licensee’s training program, the gauge manufacturer’s training course, or those persons specifically authorized by the Commission or an Agreement State remove gauges from service as required by license condition, Item 9. Specifically, on November 20, 2009, two individuals removed a gauge from service and neither individual had completed the licensee’s training program or the gauge manufacturer’s training course. In addition, on April 15, 2009, two other individuals removed a gauge from service, and one of those two individuals was not trained. None of the three individuals was authorized by the Commission or an Agreement State to remove gauges from service.
EA-10-023 | Department of Veterans Affairs | Materials | 2010-06-02 | On June 2, 2010, the NRC issued a Notice of Violation and Proposed Imposition of Civil Penalty in the amount of $14,000 to the Department of Veterans Affairs for two Severity Level III violations identified as a result of a medical event that occurred at the San Diego Healthcare System facility. The medical event resulted when iodine-131 was injected into the wrong port of the gastrostomy feeding tube (g-tube) resulting in an underdose to the patient’s thyroid and an unintended dose to the patient’s stomach. Specifically, the licensee’s written procedures did not include directions for administering byproduct material through a g-tube to ensure that the administered dose was in accordance with the written directive as required by 10 CFR 35.41(a)(2). Additionally, two nuclear medicine technologists had not been instructed on administering byproduct material through a g-tube prior to performing the administration in order to ensure that the administered dose was in accordance with the written directive. The second Severity Level III violation involved the licensee’s failure to notify the NRC Operations Center no later than the next calendar day after discovery of a medical event as required by 10 CFR 35.3045(c). Specifically, on September 23, 2009, the licensee had sufficient information, based on patient survey data and the image from the nuclear medicine department, to report the medical event and did not notify the NRC until September 26, 2009.
EA-10-063 | Yale-New Haven Hospital | Materials | 2010-05-21 | On May 21, 2010, the NRC issued a Notice of Violation to Yale-New Haven Hospital (YNHH) for a Severity Level III violation involving the failure to develop and maintain written procedures to provide high confidence that each administration requiring a written directive was performed in accordance with the written directive as required by 10 CFR 35.41. Specifically, YNHH’s written procedures did not require a physical verification of the automatic position system coordinates against the electronic coordinates prior to initiation of gamma stereotactic radiosurgery (GSR) treatment and did not specify how hospital personnel should respond to unexpected GSR treatment console errors. These procedural inadequacies resulted in a medical event, when YNHH personnel did not verify that the automatic position system coordinates were in accordance with the written directive, during the treatment of a patient undergoing GSR on August 5, 2009.
EA-10-025 | SSM St. Clare Health Center | Materials | 2010-04-19 | On April 19, 2010, the NRC issued a Notice of Violation to SSM St. Clare Health Center for a Severity Level III violation involving the failure to implement written procedures to provide high confidence that each administration was in accordance with the written directive as required by Title 10 of the Code of Federal Regulations (CFR), Section 35.41. Specifically, between November 19, 2008, and September 23, 2009, the licensee failed to follow its procedures which required the preparation of final computerized treatment plans for two patients whose prostates had been implanted with radioactive seeds. The seeds were implanted on October 22, 2008, and their computed tomography (CT) studies were performed on November 19, 2008. However, the licensee still had not prepared the final treatment plans for these patients at the time of the inspection.
EA-08-184 | CAN USA, Inc. | Materials | 2010-04-16 | On April 16, 2010, the NRC issued a Confirmatory Order (effective immediately) to CAN USA, Inc. to formalize commitments made as a result of an ADR mediation session. The commitments were made by CAN USA, Inc. as part of a settlement agreement between CAN USA, Inc. and the NRC regarding apparent willful violations of NRC requirements by a radiographer and radiographer’s assistant. The agreement resolves the apparent violations involving the CAN USA failures, which were identified during NRC inspection and investigation by the NRC Office of Investigations, and include the following areas: (1) failure to have a radiographer and at least one other individual qualified pursuant to 34.43(c); (2) failure to have a radiographer supervise and maintain direct observation of the assistant during use of a radiographic device; and (3) failure to control and maintain constant surveillance of licensed material that is in a controlled or unrestricted area and not in storage. CAN USA, Inc. agreed to a number of corrective actions, including the following: new and specific changes to operating procedures; activities related to training on new and/or revised operating procedures; interim training until the procedures are completed; unannounced audits; additional oversight of radiography crews; and specific written agreements with clients that address radiographic operations. In consideration of these commitments, the NRC agreed to limit the civil penalty amount to $7,000 and not to pursue any further enforcement action in connection with the inspection.
EA-09-038 | U.S. Department of Veterans Affairs | Materials | 2010-03-17 | On March 17, 2010, the NRC issued a Notice of Violation and Proposed Imposition of Civil Penalty in the amount of $227,500 to the U.S. Department of Veterans Affairs for violations related to activities at the Philadelphia Veterans Affairs Medical Center (PVAMC). The following areas of violation were identified: (1) Severity Level II violations of 10 CFR 35.41(a)(2) for failure to develop, implement, and maintain written procedures to provide high confidence that each administration is in accordance with the written directive, resulting in a total of 74 prostate brachytherapy treatments where the administered radiation dose was not in accordance with the written directive; (2) a Severity Level II violation of 10 CFR 35.41(b)(2) for failure to have procedures that addressed verifying that the administration was in accordance with the applicable treatment plan and written directive , resulting the licensee administering at least 16 prostate brachytherapy treatments without performing post-treatment verifications until a prolonged period of time had passed; (3) a separate Severity Level III violation of 10 CFR 35.41(b)(2) related to the the licensee’s failure to identify that the treatment plan for a brachytherapy treatment differed from the written directive, resulting in the wrong seeds being ordered and administered; (4) a Severity Level III problem involving violations of 10 CFR 35.27(a)(1) and 19.12(a)(4) for failing to instruct individuals about procedures, 10 CFR Part 35 and licensing requirements, and prompt reporting of conditions that resulted in to two medical physicists not being instructed in the requirements for identifying and reporting medical events (10 CFR 35.2 and 35.3045) and an authorized user physician not being instructed of his responsibility to report to the licensee any condition that may lead to or cause a violation; (5) a Severity Level III violation of 10 CFR 35.3045(c) for failure to report to the NRC Operations Center no later than the next calendar day when they had information that medical events occurred; and (6) two Severity Level IV violations.
EA-10-014 | City of South Bend, Indiana | Materials | 2010-03-10 | On March 10, 2010, a Notice of Violation was issued to the City of South Bend for a Severity Level III violation involving Condition 11.B of the facility's license which authorized a specifically named individual to fulfill the responsibilities of the Radiation Protection Officer. Specifically, as of January 19, 2010, the named individual was no longer employed by the company. The licensee failed to appoint a new Radiation Protection Officer and had not amended the license.
EA-09-082 | Troxler Electronic Laboratories, Inc. | Materials | 2010-03-09 | On March 9, 2010, the NRC issued a Notice of Violation for a Severity Level III violation involving the failure to implement 10 CFR 110.20(a)(2) and 10 CFR 110.41(a)(9). Specifically, on November 21, 2008, Troxler Electronic Laboratories, Inc., failed to apply for a specific license and exported byproduct material listed in Appendix L (a moisture density gauge containing Am-241) to an embargoed country listed in 10 CFR 110.28 (Iraq). Further, this failure to apply for a specific export license prevented an Executive Branch review of the export activity as required by 10 CFR 110.41(a)(9).
EA-09-142 | National Institute of Standards and Technology | Materials | 2010-03-01 | On March 1, 2010, the NRC issued an Immediately Effective Confirmatory Order to the U.S. Department of Commerce’s National Institute of Standards and Technology (NIST or licensee) to confirm commitments made as a result of an Alternate Dispute Resolution mediation session held on January 5, 2010. This enforcement action is based on ten apparent violations of NRC requirements at NIST’s facility in Boulder, Colorado, which were identified during NRC inspection and investigation activities conducted in response to a June 9, 2008 plutonium spill. The apparent violations involved the licensee’s failure to conduct the radiation safety program at NIST-Boulder in accordance with NRC requirements and the conditions of the NIST-Boulder license. The licensee agreed to take the following actions: (1) complete an independent assessment of the radiation safety program at NIST-Boulder; (2) submit copies of the required annual radiation safety audit to the NRC; (3) develop and implement a procedure for training new employees on radiation safety policies and procedures; (4) upgrade initial and refresher training for employees who work with radioactive materials, including a review of lessons learned from the plutonium spill and the associated apparent violations; (5) submit a license amendment request for deletion of the radionuclides on the NIST-Boulder license that NIST no longer plans to use; (6) develop a formal radiation hazards analysis process; (7) revise the NIST Ionizing Radiation Safety Committee charter to require additional review of NRC submittals; (8) revise the NIST radiation safety program policy to indicate that all individuals interacting with the NRC are required to provide complete and accurate information; (9) develop a clearly defined process for acquiring radioactive materials; and (10) pay a civil penalty of $10,000. In consideration of these commitments, and other actions already completed by NIST, the NRC agreed not to pursue any additional enforcement actions for the apparent violations or count this matter as previous enforcement for the purposes of assessing potential future enforcement actions in accordance with Section VI.C of the Enforcement Policy.
EA-09-289 | Gamma Knife Center of the Pacific | Materials | 2010-02-23 | On February 23, 2010, the NRC issued a Notice of Violation for a SLIII violation to Gamma Knife Center of the Pacific for a failure to implement 10 CFR 35.41(b). Specifically, as of July 2, 2009, the licensee failed to develop, implement, and maintain written procedures to provide high confidence that each medical administration is in accordance with the written directive in that the procedures did not require explicit verification that the administration was in accordance with the treatment plan and written directive. Consequently, the treatment plan and written directive were not followed to ensure that the collimator was used in the treatment of a patient.
EA-09-312 | Kanawha Scales & Systems, Inc. | Materials | 2010-02-18 | On February 18, 2010, the NRC issued a Notice of Violation to Kanawha Scales & Systems, Inc., a licensee of the State of Ohio, for a Severity Level III violation involving 10 CFR 150.20. Specifically, on November 2, 2009, Kanawha Scales & Systems, Inc., used sealed sources in a non-agreement state without filing an NRC Form 241 at least three days prior to engaging in licensed activities in areas of exclusive Federal jurisdiction.
EA-09-335 | Nanticoke Memorial Hospital | Materials | 2010-02-02 | On February 2, 2010, the NRC issued a Notice of Violation to Nanticoke Memorial Hospital for a Severity Level III violation involving the failure to notify the NRC Operations Center by telephone no later than the next calendar day after discovery of the medical event as required by 10 CFR 35.3045(c). Specifically, Nanticoke Memorial Hospital became aware that a medical event had occurred on June 26, 2009, but the NRC was not notified until July 15, 2009.
EA-09-290 | Great Falls Clinic | Materials | 2010-01-21 | On January 21, 2010, the NRC issued a Notice of Violation to Great Falls Clinic for violations associated with a Severity Level III problem involving the failure to: (1) secure from unauthorized removal or access licensed materials that are stored in controlled or unrestricted areas, in violation of 10 CFR 20.1801 and (2) secure the unit, console, console keys and the treatment room when not in use or unattended, in violation of 10 CFR 35.610 (a)(1). Specifically, the licensee stored a high dose-rate remote afterloader unit in a designated controlled area and did not secure the radioactive material from unauthorized removal or access. The console and unit were found in the unattended and not secured, designated controlled area. The console was found with its key inserted.
EA-09-040 | CJW Medical Center - Johnston-Willis Campus | Materials | 2010-01-21 | On January 21, 2010, the NRC issued a Notice of Violation to CJW Medical Center - Johnston-Willis Campus for a violation of 10 CFR 35.41(a)(2) associated with a Severity Level III violation involving the failure to develop, implement, and maintain written procedures to provide high confidence that each administration is in accordance with written directives. Specifically, as of December 16, 2008, the licensee's procedures did not require verification of the treatment site nor resolution of any inconsistencies in the written directive prior to administration of the dose. This resulted in a patient receiving treatment to the left trigeminal nerve instead of to the originally-intended site (right trigeminal nerve).
EA-09-147 | Beta Gamma Nuclear Radiology, Inc. | Materials | 2010-01-21 | On January 21, 2010, the NRC issued a Notice of Violation (NOV) and Immediately Effective Confirmatory Order to Beta Gamma Nuclear Radiology, Inc., (BGNR) to confirm commitments made as a result of an Alternative Dispute Resolution (ADR) mediation session held on October 27, 2009. This enforcement action is based on a violation of 10 CFR 30.9 which requires, in part, that information provided to the Commission by a licensee, or information required by the Commission's regulations to be maintained by the licensee shall be complete and accurate in all material respects. Contrary to this requirement, in a May 5, 2008 response contesting a Severity Level IV Notice of Violation, BGNR maintained, and provided to the NRC, information that was not complete and accurate in all material respects. Specifically, the BGNR response stated that three written directives, administered on September 14, 2005, and February 19 and 26, 2008, were written prior to the administrations, when in fact, the written directives were signed and dated after the administrations. The written directives were required to be maintained by 10 CFR 35.40(a), and were therefore, material to the NRC. BGNR agreed to: (1) perform quarterly comprehensive radiation safety audits and (2) authorize a new RSO for a two year period. In recognition of these commitments, the NRC agreed to issue to BGNR a civil penalty in the amount of $5,000 and also issue an NOV containing a SL III violation of 10 CFR 30.9.
EA-09-266 | Allegiance Health | Materials | 2010-01-06 | On January 6, 2010, the NRC issued a Notice of Violation to Allegiance Health for a Severity Level III violation involving the failure to develop written procedures to provide high confidence that the administration was in accordance with the written directive as required by Title 10 of the Code of Federal Regulations (CFR), Section 35.41. Specifically, on April 16, 2009, the licensee’s procedures did not contain any steps to ensure that no changes had occurred in the patients’ prostate volume between the time the treatment plan was prepared and the administration of the treatment and no other method was provided to ensure that the administration was in accordance with the written directive.
EA-09-221 | Cardinal Health | Materials | 2009-12-30 | On December 30, 2009, the NRC issued a Notice of Violation to Cardinal Health for a Severity Level III violation involving the failure of an employee to wear finger dosimetry while compounding radiopharmaceuticals as required by Condition 24 of the license. Specifically, on several occasions between January and May 17, 2007, a licensee employee responsible for dispensing radioactive sources deliberately failed to wear finger dosimetry while compounding iodine-131 doses.
EA-09-260 | Niles Steel Tank Company | Materials | 2009-12-09 | On December 9, 2009, the NRC issued a Notice of Violation to Niles Steel Tank Company for a Severity Level III violation involving the failure to secure from unauthorized removal or access licensed material stored in controlled or restricted areas as required by 10 CFR 20.1801. Specifically, between August 24, 2009, and September 9, 2009, the licensee stored a radiography camera in a permanent radiographic installation and a member of the public had access to the area.
EA-09-187 | Wal-Mart Stores, Inc. | Materials | 2009-10-28 | On October 28, 2009, the NRC issued a Notice of Violation to Wal-Mart, Inc. (Wal-Mart) for a Severity Level III problem involving the failure to: (1) appoint an individual responsible for having knowledge of appropriate regulations and requirements to comply with the general license; (2) properly transfer and dispose of generally licensed devices; and (3) transfer generally licensed devices to another general licensee only if the devices remain in use at a particular location. Specifically, between October 2000 and January 2008, Wal-Mart did not appoint a radiation safety officer or other responsible individual to manage its general license program relative to tritium exit signs, improperly transferred or disposed of up to 2,462 tritium exit signs, and also transferred 517 tritium exit signs from various Wal-Mart facilities to other Wal-Mart facilities, which were not authorized in a specific or general license.
EA-09-084 | Hematite Decommissioning Project | Materials | 2009-10-23 | On October 23, 2009, the NRC issued a Notice of Violation and Proposed Imposition of Civil Penalty in the amount of $16,250 to Westinghouse Electric Company - Hematite Decommissioning Project for a Severity Level III violation involving the failure to implement 10 CFR 70.24 (a) requirements. Specifically, in March 2006, the licensee failed to maintain a criticality accident monitoring system which will energize clearly audible alarm signals when it removed the system from service without prior NRC authorization. In addition, the Notice of Violation included a second Severity Level III violation for which a civil penalty was not proposed, involving the failure to implement 10 CFR 70.9 (a) requirements. Specifically, on March 17, 2006, the licensee provided inaccurate information to the Commission when it informed the NRC that the Process buildings contained less than 250 grams of uranium-235, when in fact, as later determined in November 2008, the Process buildings contained an estimated 2,638 grams of uranium-235. This information was material to the NRC since it was used in part as the basis for granting a license amendment on June 30, 2006, revising the possession limits such that the criticality monitoring system could be disabled.
EA-09-212 | Virtua Health System - West Jersey Hospital | Materials | 2009-10-21 | On October 21, 2009, the NRC issued a Notice of Violation to Virtua Health System - West Jersey Hospital (Virtua) for a Severity Level III violation involving the failure to develop, implement, and maintain written procedures to provide high confidence that each administration is in accordance with the written directive, as required by 10 CFR 35.41(a)(2). Specifically, during patient setup on January 19, 2009, Virtua staff raised questions concerning the visualization and positioning of seeds in the prostate and there were no procedures to ensure resolution of the questions. As a result, all seeds were implanted outside the prostate.
EA-09-253 | Langan Engineering & Environmental Services, Inc. | Materials | 2009-10-13 | On October 13, 2009, the NRC issued a Notice of Violation to Langan Engineering & Environmental Services, Inc. for a Severity Level III violation involving the failure to control and maintain constant surveillance of licensed material as required by 10 CFR 20.1802. Specifically, on June 29, 2009, the licensee’s authorized user left unattended a portable moisture/density gauge in an unrestricted area for a short period of time. During the time that the licensee did not maintain control and constant surveillance of the gauge, it was damaged by construction equipment that was operating in the unrestricted area.
EA-09-188 | Department of Commerce - National Oceanic and Atmospheric Administration | Materials | 2009-10-01 | On October 1, 2009, a Notice of Violation was issued to the Department of Commerce, National Oceanic and Atmospheric Administration (NOAA) for two Severity Level III violations involving (1) failure to secure from unauthorized removal or access licensed materials that are stored in controlled or unrestricted areas, pursuant to 10 CFR, 20.1801, and (2) failure to confine possession and use of byproduct materials to the locations and purposes authorized on the license, pursuant to 10 CFR 30.34(c). Specifically, NOAA stored licensed materials in two different unrestricted areas and a controlled area during two different time periods, without securing the materials from unauthorized removal or access. Additionally, from 1993 until 2008, NOAA used licensed material in custom-made, unregistered devices in violation of its license condition requiring NOAA to use only such devices when the device has been registered with either the NRC or an NRC Agreement State.
EA-09-114 | Earth Exploration, Inc. | Materials | 2009-10-01 | On October 1, 2009, the NRC issued an Immediately Effective Confirmatory Order to Earth Exploration, Inc. to confirm commitments made as a result of an Alternative Dispute Resolution (ADR) mediation session held on August 25, 2009. The parties agreed to engage in ADR following NRC’s July 21, 2009, letter wherein seven apparent violations were identified based on information developed during an investigation. The violations involved the failure to: (1) perform annual reviews of the radiation protection program; (2) perform leak testing of sealed sources; (3) perform physical inventories every six months of sealed sources; (4) ensure that dosimetry provided to gauge users was processed and evaluated; (5) ensure through the Radiation Safety Officer that required tests and conditions of the NRC license are performed; (6) secure, on multiple occasions, portable gauges using two independent physical barriers; and (7) lock a gauge or gauge case when in storage. The NRC preliminarily determined that the first five violations were due to the deliberate actions of the Radiation Safety Officer. As part of the agreement, Earth Exploration, Inc., acknowledged the technical violations and agreed to take a number of actions including, but not limited to, retaining a qualified consultant to audit the radiation safety program on an annual basis for a period of five years, receiving training on radiation safety program management, and developing a plan to inform other organizations of the lessons learned and the importance of developing the necessary infrastructure and communication paths to identify and resolve competing priorities. In recognition of these and other actions, the NRC agreed to not categorize the violations as deliberate and to not pursue any further enforcement action against Earth Exploration, Inc., for these violations.
EA-09-182 | Ohio Valley Medical Center | Materials | 2009-09-17 | On September 17, 2009, the NRC issued a Notice of Violation to Ohio Valley Medical Center for a Severity Level III violation involving the failure to meet the physical presence requirements of 10 CFR 35.615(f)(2) during high dose radiation (HDR) treatments. Specifically, on June 17, 2009 and other occasions prior to that date, neither an authorized user (AU), nor a physician under the supervision of an AU and trained in the operation and emergency response for the unit, were physically present during continuation of HDR treatments.
EA-09-181 | Mercy Health Services | Materials | 2009-09-15 | On September 15, 2009, the NRC issued a Notice of Violation to Mercy Health Services for a Severity Level III problem involving: (1) the failure to conduct surveys to ensure compliance with the regulations in 10 CFR Part 20 as required by 10 CFR 20.1501 and (2) the discharge of licensed material into the sanitary sewer system that exceeded the concentration limits listed in 10 CFR Part 20 Appendix B Table 3 in violation of 10 CFR 20.2003. Specifically, in May 2008, the licensee disposed of iodine-125 into the sanitary sewer system without evaluating the radioactivity of the iodine waste or evaluating the average monthly volume of water released into the sewer system. The licensee released 2.29E-5 microcurie per milliliter of iodine-125 into the sewer which exceeded the 2E-5 microcurie per milliliter limit.
EA-09-030 | Advex Corporation | Materials | 2009-07-02 | On July 2, 2009, the NRC issued a Notice of Violation for two Severity Level III violations to Advex Corporation (Advex). The first violation involved the failure to wear an alarming ratemeter while performing radiography by an assistant radiographer, as described in Condition 19 of the Advex’s license. Specifically, on January 22, 2008, an assistant radiographer worked in a restricted area (permanent radiography vault) and did not wear an alarm ratemeter. The second violation involved the deliberate failure of the lead radiographer and the assistant radiographer to follow the Operating & Emergency (O&E) Procedure and 10 CFR 34.47(d) requirements, when the assistant radiographer had an off-scale pocket dosimeter. Specifically, on January 22, 2008, neither individual notified the RSO after the radiographers realized the assistant radiographer’s dosimeter was off-scale. The assistant did not remove himself from the restricted area and he was allowed to continue working with and around radioactive material although he was not authorized to return to work by the RSO, as required by the O&E procedure and 10 CFR 34.47(d).
EA-09-020 | Allwest Geosciences, Inc. | Materials | 2009-06-08 | On June 8, 2009, the NRC issued a Notice of Violation to Allwest Geoscience, Inc. for a Severity Level III failure to implement 10 CFR 150.20. Specifically, from November 2008 through January 2009, the Agreement State licensee conducted portable gauge operations at a Federal facility considered an area of exclusive Federal jurisdiction that is regulated by NRC and is located within an Agreement State, without first filing a reciprocity submittal for calendar years 2008 and 2009.
EA-08-332 | S&M Testing Laboratory | Materials | 2009-06-08 | On June 8, 2009, the NRC issued an Order Imposing Civil Monetary Penalty to S&M Testing Laboratory (S&M). Following the NRC’s March 23, 2009, Notice of Violation and Proposed Imposition of a Civil Penalty in the amount of $16,250, the licensee has failed to respond to the Notice and the proposed civil penalties. The Notice of Violation and proposed civil penalty was issued to the licensee for the deliberate failure to confine possession of byproduct material to only those locations authorized by the NRC license; the deliberate failure to provide the NRC an opportunity to inspect byproduct material and the premises where the byproduct material was stored, as required by 10 CFR 30.52(a); and the failure to utilize a minimum of two independent physical controls that form tangible barriers to secure portable gauges from unauthorized removal whenever the gauges were not under the control and constant surveillance of the licensee, as required by 10 CFR 30.34(i). Accordingly, NRC concluded that the violation remains valid and issued an order imposing Civil Monetary Penalty in the amount of $16,250.
EA-09-067 | Central Indiana Cancer Centers | Materials | 2009-05-27 | On May 27, 2009, the NRC issued a Notice of Violation to Central Indiana Cancer Centers for a Severity Level III violation involving the failure to implement 10 CFR 20.1802. Specifically, as of February 18, 2009, on several occasions while transporting a High Dose Rate Afterloader unit, the licensee left the unit in an unlocked vehicle for several minutes while retrieving other associated equipment. During these periods, the licensee did not control or maintain constant surveillance over the licensed material.
EA-09-039 | Department of the Army - Walter Reed Army Medical Center | Materials | 2009-05-22 | On May 22, 2009, the NRC issued a Notice of Violation to Walter Reed Medical Center (WRAMC) for a SL III problem involving: (1) the failure to control radioactive material not in storage as required by 10 CFR 20.1802 and (2) a failure to provide adequate radiation safety instruction to a medical student, who provided care to a brachytherapy patient; and a Severity Level III violation involving a failure to provide event notification as required, in a timely manner. Specifically, on November 14, 2008, the licensee lost control of the brachytherapy sources for approximately 5.5 hours when a medical student, who had not been trained on the safe handling and shielding of brachytherapy sources, inadvertently removed three ribbons containing iridium-192 from a patient’s bandage and improperly disposed of the sources. Consequently the sources were improperly transported to the trash compactor, an uncontrolled area, on the WRAMC loading dock. In addition, the WRAMC did not notify the NRC until November 19, 2008, five days after this event.
EA-09-019 | Northwest Inspection, Inc. | Materials | 2009-05-20 | On May 20, 2009, the NRC issued a Notice of Violation for a SLIII violation to Northwest Inspection, Inc., for a violation of 10 CFR 150.20. Specifically, during six time periods in 2008, the Agreement State licensee engaged in activities in NRC jurisdiction and did not file (1) a submittal containing NRC Form 241, “Report of Proposed Activities in Non-Agreement States,” (2) a copy of its Agreement State specific license, and (3) the appropriate fee with the Regional Administrator for the Region in which the Agreement State that issued the license is located.
EA-09-047 | Department of Air Force | Materials | 2009-05-18 | On May 18, 2009, the NRC issued a Notice of Violation to the Department of the Air Force for a Severity Level III failure to implement 10 CFR 35.3047. Specifically, as of August 14, 2008, the licensee failed to notify by telephone the NRC Operations Center no later than the next calendar day after discovery of a dose to an embryo/fetus that is greater than a 5 rem (50 millisievert) dose equivalent that results from an administration of byproduct material to a pregnant individual unless specifically approved by an authorized user physician. On August 13, 2008, the licensee discovered that an embryo/fetus had received a dose of approximately 31.5 rem (50 millisievert) as a result of a sodium iodine-131administration to a pregnant individual and did not notify the NRC Operations Center until September 5, 2008.
EA-09-071 | Memorial Hospital of Sweetwater County | Materials | 2009-05-14 | On May 14, 2009, the NRC issued a Notice of Violation to Memorial Hospital of Sweetwater County for a Severity Level III violation involving the failure to implement 10 CFR 20.1801. Specifically, on February 12, 2009, the licensee stored radioactive materials in a hospital hot lab, a designated controlled area, and did not secure the materials therein from unauthorized removal or access by failing to lock the hot lab door.
EA-09-034 | KAM Engineering Services, P.C. | Materials | 2009-05-06 | On May 6, 2009, the NRC issued a Notice of Violation to KAM Engineering Services (KAM-ES), for two Severity Level III violations. The first violation involved the failure to file NRC Form 241 “Report of Proposed Activities in Non-Agreement States,” at least three days prior to engaging in licensed activities within NRC jurisdiction. Specifically, from March 1, 2008 until January 21, 2009, KAM-ES, a holder of a North Carolina license, stored or used portable gauges in an area of exclusive federal jurisdiction without a specific license issued by the NRC and did not file Form-241 with the NRC. The second violation involved a failure to utilize a minimum of two independent physical controls that form tangible barriers to secure portable gauges from unauthorized removal whenever the gauges were not under the control and constant surveillance of the licensee, as required by 10 CFR 30.34(i). Specifically, KAM-ES periodically stored two portable gauges in a trailer-type container, and the trailer only had a single lock on the door to secure gauges from unauthorized removal, whenever they were not under the control and constant surveillance of KAM-ES.
EA-08-332 | S&M Testing Laboratory | Materials | 2009-03-23 | On March 23, 2009, a Notice of Violation and Proposed Imposition of Civil Penalty in the amount of $16,250 was issued to S&M Testing Laboratory for three Severity Level III violations. The first violation involved a deliberate failure to confine possession of byproduct material to only those locations authorized by the NRC license. Specifically from May 1, 2007, through September 23, 2008, S&M Testing stored portable gauges at a location in Gurabo, Puerto Rico (PR) which was not an authorized storage location on the license. The second violation involved a deliberate failure to provide the NRC an opportunity to inspect byproduct material and the premises where the byproduct material was stored, as required by 10 CFR 30.52(a). Specifically, from May 1, 2007 through August 6, 2008, S&M Testing failed to respond to NRC letters and telephone calls that requested information regarding its licensed activities and storage of licensed material. The third violation involved a failure to utilize a minimum of two independent physical controls that form tangible barriers to secure portable gauges from unauthorized removal whenever the gauges were not under the control and constant surveillance of the licensee, as required by 10 CFR 30.34(i). Specifically, between May 1, 2007, and September 23, 2008, the portable gauges were stored in locked metal boxes located in an unrestricted area, but the keys to the boxes were left in another unrestricted area and during this period the gauges were not under the control and constant surveillance of S&M Testing.
EA-08-158 | Quality Inspection Services, Inc. | Materials | 2009-03-10 | On March 10, 2009, a Confirmatory Order (effective immediately) was issued to Quality Inspection Services, Inc. (QISI) to confirm commitments made as a result of an Alternative Dispute Resolution (ADR) settlement agreement. The licensee requested ADR following the NRC’s September 15, 2008, Notice of Violation and Proposed civil penalty of $6,500, for a willful violation of 10 CFR 34.71, involving the failure to maintain utilization logs of radiographic activities and three other related violations. As part of the agreement, QISI agreed to take a number of actions including revising the existing Operations and Emergency (O&E) Manual, adding a radiation safety component to the existing Newsletter, developing a video recording that can be used for a presentation at a national industry conference, increasing audits of the radiographers working areas, and an inquiry of all radiographers during the next two annual radiation safety program reviews. In recognition of QISI’s proposed extensive corrective actions, in addition to corrective actions already taken, the NRC agreed to reduce the civil penalty originally proposed to $500.
EA-08-271 | Mattingly Testing Services, Inc. | Materials | 2009-03-06 | On March 6, 2009, the NRC issued an immediately effective Confirmatory Order to Mattingly Testing Services, Inc. that issued commitments resulting from an Alternative Dispute Resolution settlement agreement with the licensee to address nine apparent violations and corrective actions. The nine apparent violations are summarized as follows: (1) failure to wear required dosimetry during radiographic operations by a radiographer’s assistant; (2) failure to secure a radiographic exposure device containing radioactive material with a minimum of two independent physical controls; (3) failure to notify NRC within 24 hours after discovery of an event; (4) failure to use pocket dosimetry that is calibrated; (5) failure to have a required functional alarm system; (6) failure to provide complete and accurate information to the Commission; (7) failure to provide supervision of an assistant radiographer by a radiographer during use of radiographic equipment; (8) failure to remove damaged equipment from service; and (9) failure to assure that an individual acting as an assistant radiographer had completed a practical examination on the use of radiographic equipment. As part of the settlement, NRC agreed not to pursue any further enforcement action in connection with the apparent violations and will not count this matter as previous enforcement for the purposes of assessing potential future enforcement action.
EA-08-261 | Schlumberger Technology Corporation | Materials | 2009-02-24 | On February 24, 2009, a Confirmatory Order (effective immediately) was issued to Schlumberger Technology Corporation (Schlumberger) to confirm commitments made as a result of an Alternative Dispute Resolution (ADR) settlement agreement. NRC identified two violations during inspection and investigation involving: (1) a willful failure to maintain required records complete and accurate as required by 10 CFR 30.9, and (2) failure to maintain control over licensed material as required by 10 CFR 20.1802. In response to these violations, the licensee requested ADR. As part of the agreement, Schlumberger agreed to take a number of actions including developing and implementing an enhanced accountability and security program for licensed materials, conducting additional line management reviews of the radiation safety program, and paying a civil penalty in the base amount of $3250. In recognition of these and other actions, as well as those actions already completed, the NRC agreed not to pursue further enforcement action against Schlumberger for the violations.
EA-08-329 | St. John Macomb-Oakland Hospital | Materials | 2009-02-18 | On February 18, 2009, a Notice of Violation (NOV) was issued for a Severity Level III violation. The NOV involved a violation of Condition 11.B of the facility's license, which authorized a specifically named individual to fulfill the responsibilities of the Radiation Safety Officer (RSO) for the brachytherapy activities. Specifically, as of November 2007, the authorized individual was no longer employed by the consulting firm retained by the licensee and did not fulfill the RSO responsibilities. The licensee failed to appoint a new RSO following the previous RSO's departure from the consulting firm.
EA-08-237 | Sabia, Inc. | Materials | 2009-01-29 | On January 29, 2009, the NRC issued a Notice of Violation and Imposition of Civil Penalty in the amount of $13,000 to Sabia, Inc. for a Severity Level III violation of 10 CFR 20.1101. Specifically, between February 25 and 29, 2008, the licensee conducted gauge dismantlement activities and failed to develop, document, and implement a radiation protection program commensurate with the scope and extent of this licensed activity. This failure created a substantial potential for exposures or releases in excess of the applicable NRC regulatory limits when its activities resulted in contamination of its workers and the facility. In addition, the licensee failed to have a radiation protection program for the gauge dismantlement activities that was sufficient to ensure that occupational doses were as low as is reasonably achievable (ALARA), resulting in worker doses that were not ALARA.
EA-08-303 | Huntington Testing & Technology, Inc. | Materials | 2009-01-22 | On January 22, 2009, a Notice of Violation (NOV) was issued for a Severity Level III problem. The violations involved the failure to comply with license condition and to provide event notification as required, in a timely manner. Specifically, on August 20, 2008, the licensee had an event where a radiography camera was disabled and failed to function as designed. The lead radiographer and the field Radiation Safety Officer, who were not trained or authorized by the NRC license, conducted source retrieval activities and shielded-down a source. In addition, the licensee did not notify the NRC until September 3, 2008, two weeks after this event.
EA-08-286 | Cal Testing Services, Inc. | Materials | 2009-01-05 | On January 5, 2009, a Notice of Violation (NOV) and Proposed Imposition of Civil Penalty in the amount of $6,500 was issued to Cal Testing Services, Inc. This action is based on a Severity Level III violation of NRC License Condition 20 involving the failure of the licensee to conduct its program in accordance with the statements, representations, and procedures contained in an application (with attachments) provided to the NRC. Specifically, the licensee failed to connect the control cable to the source assembly before cranking the source out of the radiographic exposure device, as required by the licensee’s procedures. This event resulted in a disconnected source event.
IA-12-043 | Mr. Rodger T Devlin | Individual | 2012-09-20 | On September 20, 2012, the NRC issued a Notice of Violation to Mr. Rodger T Devlin, formerly a licensed reactor operator at the Limerick Generating Station, for a Severity Level III violation involving 10 CFR 55.53(j). On July 14, 2012, Mr. Devlin participated in the Exelon Generation Company random fitness for duty testing program and subsequently tested positive for alcohol while working on shift as a reactor operator.
IA-12-037 | Peter E. Reynolds | Individual | 2012-09-11 | On September 11, 2012, the NRC issued a Notice of Violation to Mr. Peter E. Reynolds, a licensed reactor operator at the Browns Ferry Nuclear Plant, for a Severity Level III violation involving 10 CFR 55.53(j) which prohibits the licensee from performing activities authorized by a license issued under 10 CFR Part 55 while under the influence of alcohol. On May 17, 2012, Mr. Reynolds participated in the Tennessee Valley Authority’s random fitness for duty testing program and subsequently tested positive for alcohol. Specifically, Mr. Reynolds’ breath test sample was 0.024 percent breath alcohol content (BAC), and the confirmatory test sample was 0.030 percent BAC. A positive test result was determined by Tennessee Valley Authority because Mr. Reynolds met or exceeded the administrative level of 0.02 percent BAC and was in work status more than 2 hours prior to the time the initial test was concluded.
IA-11-036 | Jaime Sánchez | Individual | 2012-05-17 | On May 17, 2012, the NRC issued a Severity Level III Notice of Violation and an Order prohibiting involvement in NRC-licensed activities to Mr. Jaime Sánchez, President, S&R Engineering, S.E. (S&R). This enforcement action is based on Mr. Sánchez’s deliberate violation of 10 CFR 30.10(a)(2): he provided information to the NRC that he knew was inaccurate in some respect material to the NRC. Specifically, on August 3, 2010, Mr. Sánchez stated to the NRC that S&R’s licensed portable nuclear gauge had been transferred to another licensee and that S&R no longer possessed licensed material, when, in fact, S&R still possessed the gauge. In addition, as the President of S&R, he failed to respond to NRC correspondence and communication attempts, and failed to address or correct the misinformation that he provided on August 3, 2010. The Order prohibits Mr. Sánchez from engaging in all NRC-licensed activities for a period of five years, and requires him to notify the NRC, following completion of the five year prohibition, of his first employment involving NRC-licensed activities.
IA-12-003 | Jay T. Barnes | Individual | 2012-04-12 | On April 12, 2012, the NRC issued a Notice of Violation to Mr. Jay T. Barnes, formerly a security shift supervisor at Northern States Power Company’s Prairie Island Nuclear Generating Plant (Prairie Island), for a violation of 10 CFR 50.5(a)(2) associated with a Severity Level III violation involving his deliberate submittal to a licensee information that he knew to be incomplete or inaccurate in some respect material to the NRC. Specifically, while employed as a security shift supervisor at Prairie Island, Mr. Barnes deliberately submitted a urine sample to Northern States Power Company that he knew was not his own taken at the time of testing during a random drug screen on July 23, 2010. The accuracy of fitness-for-duty test results is material to the NRC.
IA-11-061 | Edward G. Johnson | Individual | 2012-01-25 | On January 25, 2012, an immediately effective Confirmatory Order was issued to Mr. Edward G. Johnson, to confirm commitments made as a result of an Alternative Dispute Resolution (ADR) mediation session held on December 20, 2011. As part of the ADR agreement, Mr. Johnson agreed to: 1) participate in the Entergy Remediation Plan specifically designed for him, in which he will be required to: develop a presentation and provide it to senior Palisades leadership and operations personnel on the event; interview with senior Entergy management to assess his eligibility and readiness to resume licensed duties; successfully complete 40 hours of “under instruction” watches on each shift; and, participate in a simulator scenario and associated training that include handling stressful situations and conflict management, and 2) author an article in which he will discuss the incident and lessons learned, and submit it to the Communicator (the publication for the Professional Reactor Operator Society). Accordingly, the NRC agreed not to pursue additional enforcement action against Mr. Johnson.
IA-11-041 | Eric L. Stone | Individual | 2012-01-05 | On January 5, 2012, the NRC issued a Notice of Violation to Mr. Eric L. Stone, a licensed operator at the River Bend Station for a Severity Level III violation involving 10 CFR 50.5, Deliberate misconduct. Mr. Stone deliberately violated an Entergy Nuclear Fleet Procedure which prohibits internet access in the At-the-Controls area of the Control Room, except as specifically authorized by the Operations Manager and caused the River Bend Station to be in violation of Technical Specifications. Specifically, Mr. Stone accessed the internet, a significant number of times for non-work-related purposes, while standing watch as the reactor operator “At-the-Controls” in the “At-the-Controls” area of the control room.
IA-11-045 | Scott Motes | Individual | 2012-01-05 | On January 5, 2012, the NRC issued a Notice of Violation to Mr. Scott Motes, a licensed operator at the River Bend Station for a Severity Level IV violation involving 10 CFR 50.5, Deliberate misconduct. Mr. Motes deliberately violated an Entergy Nuclear Fleet Procedure which prohibits internet access in the At-the-Controls area of the Control Room, except as specifically authorized by the Operations Manager and caused the River Bend Station to be in violation of Technical Specifications. Specifically, Mr. Motes accessed the internet, for non-work-related purposes, while standing watch as the reactor operator “At-the-Controls” in the “At-the-Controls” area of the control room.
IA-11-040 | Anthony K. Linton | Individual | 2012-01-05 | On January 5, 2012, the NRC issued a Notice of Violation to Mr. Anthony K. Linton, a licensed operator at the River Bend Station for a Severity Level III violation involving 10 CFR 50.5, Deliberate misconduct. Mr. Linton deliberately violated an Entergy Nuclear Fleet Procedure which prohibits internet access in the At-the-Controls area of the Control Room, except as specifically authorized by the Operations Manager and caused the River Bend Station to be in violation of Technical Specifications. Specifically, Mr. Linton accessed the internet, a significant number of times for non-work-related purposes, while standing watch as the reactor operator “At-the-Controls” in the “At-the-Controls” area of the control room.
IA-11-032 | Francis Guilbeau | Individual | 2012-01-05 | On January 5, 2012, the NRC issued Mr. Francis Guilbeau an Order prohibiting involvement in NRC-licensed activities for a period of one year. As a former radiographer employed by Accurate NDE & Inspection, LLC (Accurate NDE), working in NRC jurisdiction, this individual engaged in deliberate misconduct while performing radiographic operations on March 14 and March 15, 2010. Specifically, he deliberately failed to follow Accurate NDE operating procedures by attempting to retrieve a disconnected source without first contacting and obtaining authorization from the Radiation Safety Officer that, in turn, placed Accurate NDE in violation of its Louisiana State license and 10 CFR 150.20(b)(5). Additionally, the individual deliberately provided inaccurate information on a daily radiation report involving a dose exposure for another radiographer. These actions constituted two separate violations of NRC’s rule prohibiting deliberate misconduct, 10 CFR 30.10.
IA-11-044 | Tommy S. Edwards | Individual | 2012-01-05 | On January 5, 2012, the NRC issued a Notice of Violation to Mr. Tommy S. Edwards, a licensed operator at the River Bend Station for a Severity Level IV violation involving 10 CFR 50.5, Deliberate misconduct. Mr. Edwards deliberately violated an Entergy Nuclear Fleet Procedure which prohibits internet access in the At-the-Controls area of the Control Room, except as specifically authorized by the Operations Manager and caused the River Bend Station to be in violation of Technical Specifications. Specifically, Mr. Edwards accessed the internet, for non-work-related purposes, while standing watch as the reactor operator “At-the-Controls” in the “At-the-Controls” area of the control room.
IA-11-047 | Terry J. Douglas | Individual | 2012-01-05 | On January 5, 2012, the NRC issued a Notice of Violation to Mr. Terry J. Douglas, a licensed operator at the River Bend Station for a Severity Level IV violation involving 10 CFR 50.5, Deliberate misconduct. Mr. Douglas deliberately violated an Entergy Nuclear Fleet Procedure which prohibits internet access in the At-the-Controls area of the Control Room, except as specifically authorized by the Operations Manager and caused the River Bend Station to be in violation of Technical Specifications. Specifically, Mr. Douglas accessed the internet, for non-work-related purposes, while standing watch as the reactor operator “At-the-Controls” in the “At-the-Controls” area of the control room.
IA-11-039 | Jeffery W. Coykendall | Individual | 2012-01-05 | On January 5, 2012, the NRC issued a Notice of Violation to Mr. Jeffery W. Coykendall, a licensed operator at the River Bend Station for a Severity Level III violation involving 10 CFR 50.5, Deliberate misconduct. Mr. Coykendall deliberately violated an Entergy Nuclear Fleet Procedure which prohibits internet access in the At-the-Controls area of the Control Room, except as specifically authorized by the Operations Manager and caused the River Bend Station to be in violation of Technical Specifications. Specifically, Mr. Coykendall accessed the internet, for non-work-related purposes, while standing watch as the reactor operator “At-the-Controls” in the “At-the-Controls” area of the control room.
IA-11-046 | Louis F. Brown, III | Individual | 2012-01-05 | On January 5, 2012, the NRC issued a Notice of Violation to Mr. Louis F. Brown, III, a licensed operator at the River Bend Station for a Severity Level IV violation involving 10 CFR 50.5, Deliberate misconduct. Mr. Brown deliberately violated an Entergy Nuclear Fleet Procedure which prohibits internet access in the At-the-Controls area of the Control Room, except as specifically authorized by the Operations Manager and caused the River Bend Station to be in violation of Technical Specifications. Specifically, Mr. Brown accessed the internet, for non-work-related purposes, while standing watch as the reactor operator “At-the-Controls” in the “At-the-Controls” area of the control room.
IA-11-043 | Terry N. Blanchard | Individual | 2012-01-05 | On January 5, 2012, the NRC issued a Notice of Violation to Mr. Terry N. Blanchard, a licensed operator at the River Bend Station for a Severity Level IV violation involving 10 CFR 50.5, Deliberate misconduct. Mr. Blanchard deliberately violated an Entergy Nuclear Fleet Procedure which prohibits internet access in the At-the-Controls area of the Control Room, except as specifically authorized by the Operations Manager and caused the River Bend Station to be in violation of Technical Specifications. Specifically, Mr. Blanchard accessed the internet, for non-work-related purposes, while standing watch as the reactor operator “At-the-Controls” in the “At-the-Controls” area of the control room.
IA-11-042 | Steve L. Bibb | Individual | 2012-01-05 | On January 5, 2012, the NRC issued a Notice of Violation to Mr. Steve L. Bibb, a licensed operator at the River Bend Station for a Severity Level IV violation involving 10 CFR 50.5, Deliberate misconduct. Mr. Bibb deliberately violated an Entergy Nuclear Fleet Procedure which prohibits internet access in the At-the-Controls area of the Control Room, except as specifically authorized by the Operations Manager and caused the River Bend Station to be in violation of Technical Specifications. Specifically, Mr. Bibb accessed the internet, for non-work-related purposes, while standing watch as the reactor operator “At-the-Controls” in the “At-the-Controls” area of the control room.
IA-11-037 | Christopher A. Moore | Individual | 2011-11-09 | On November 9, 2011, the NRC issued a Notice of Violation to Christopher A. Moore, former Radiation Safety Officer at Cardinal Health PET Manufacturing Services, Inc., in St. Louis, Missouri, for a Severity Level III violation involving 10 CFR 30.10, “Deliberate Misconduct.” Specifically, on June 16, 2010, Mr. Moore caused Cardinal Health PET Manufacturing Services, Inc., an applicant for an NRC license, to be in violation of 10 CFR 20.1502(a)(1) which requires that a licensee (in this case, an applicant) monitor the occupational exposure to adults likely to receive, in one year from sources external to the body, a dose in excess of 10 percent of the limits in 10 CFR 20.1201(a). The nature of Mr. Moore’s position made him subject to 10 CFR 20.1502(a)(1). However, Mr. Moore deliberately removed his extremity (ring) dosimetry on two separate occasions prior to handling a chemical cartridge containing approximately 4 curies of fluorine-18.
IA-11-056 | Craig M. Rice | Individual | 2011-09-21 | On September 21, 2011, the NRC issued a Notice of Violation to Mr. Craig M. Rice, formerly a licensed reactor operator at the Fermi Power Plant, Unit 2, for a Severity Level III violation involving 10 CFR 55.53(j). On April 25, 2011, Mr. Rice participated in the Detroit Edison Company random fitness for duty testing program and subsequently tested positive for an illegal substance.
IA-10-010 | Gregory Desobry | Individual | 2011-02-23 | On February 23, 2011, the NRC issued an Order requiring notification of future involvement in NRC licensed or Agreement State regulated activities to Mr. Gregory Desobry in order to provide the NRC with an opportunity to verify the effectiveness of corrective actions that Mr. Desobry had taken in response to his involvement in the medical events that occurred at the VA Philadelphia Medical Center from February 2002 through June 2008 and the resulting identified violations (EA-09-038). Specifically, the Order requires Mr. Desobry to make a one-time notification to the NRC within 20 days of his accepting employment as a medical physicist in NRC licensed or Agreement State regulated activities. The Order noted that Mr. Desobry provided a description of the corrective actions he had taken in a June 28, 2010, reply to a Demand for Information that the NRC issued on May 24, 2010. The Order will be effective 20 days after it is published in the Federal Register.
IA-09-035 | Gary Kao | Individual | 2011-02-23 | On February 23, 2011, the NRC issued an Order prohibiting involvement in NRC licensed activities to Dr. Gary Kao in order to provide the NRC with reasonable assurance that the protection of public health and safety will not be compromised until such time that Dr. Kao provides NRC with sufficient information relative to the corrective actions he has taken to address his part in the medical events that occurred at the VA Philadelphia Medical Center from February 2002 through June 2008, and resulting identified violations (EA-09-038). Specifically, the Order prohibits Dr. Kao’s involvement in any NRC licensed activity until rescinded by the NRC, contingent upon Dr. Kao’s completing specialized training, demonstrating the ability to correctly identify and report medical events, and providing other documentation to the NRC supporting completion of the requirements specified in the Order. The Order noted that Dr. Kao voluntarily stopped performing brachytherapy treatments and committed to take all necessary and appropriate steps to ensure that he was current on all applicable requirements should he perform brachytherapy treatments in the future. The Order will be effective 20 days after it is published in the Federal Register.
IA-10-028 | Mark M. Ficek | Individual | 2011-02-22 | On February 22, 2011, the NRC ASLB Hearing Board issued a Memorandum and Order accepting a Settlement and Dismissing the Hearing Proceeding in the matters of Mattingly Testing Services, Inc., (MTS) Order Revoking License (EA-10-100) and Mark M. Ficek Order Prohibiting Engagement in NRC-licensed Activities (IA-10-028) that were both issued on September 2, 2010. Specifically, the NRC staff and two parties, employees of MTS, who had requested a hearing on the September 2 Orders had agreed to a settlement on February 4, 2011, in lieu of continuing the hearing proceeding. The Settlement Agreement was forwarded to the ASLB and approved. The February 22, 2011 Board Order superseded the September 2, 2010 Order Revoking License issued to MTS and the Order Prohibiting Engagement in NRC-licensed Activities issued to Mark M. Ficek. The Order and Settlement included the following terms and conditions: (1) the MTS license remains revoked and parties agree that it will not be reinstated; (2) Mr. Ficek is prohibited from engaging in NRC-licensed activities until September 2, 2017 (the settlement further defines NRC-licensed activities); (3) for a three year period after September 2, 2017, Mr. Ficek is required to notify NRC of employment involving NRC-licensed activities; (4) Mr. Ficek is allowed non-controlling ownership in an NRC licensee, subject to conditions specified in the settlement prohibiting Mr. Ficek’s engagement in licensed activities; (5) Mr. Ficek is allowed to own and/or sell the radiographic exposure devices that were listed on the former MTS license, subject to conditions specified in the settlement; and, (6) that all parties agree that all further procedural steps before the ASLB and any right to challenge or contest the validity of the Board Order entered into in accordance with the Settlement Agreement, and all rights to seek judicial review or otherwise contest the validity of the Board Order are expressly waived.
IA-10-028 | Mark M. Ficek | Individual | 2010-09-02 | On September 2, 2010, the NRC issued an Order (Immediately Effective) Prohibiting Involvement in NRC Activities to Mr. Mark M. Ficek for multiple deliberate violations of NRC requirements and a violation of Confirmatory Order (IA-08-055). The Order specified that Mr. Ficek is prohibited involvement from all NRC-licensed activities for a period of 7 years, and that Mr. Ficek is required to notify the NRC upon initial involvement in NRC-licensed activities for an additional two years after the 7 year prohibition period expires. Specifically, the NRC found that Mr. Ficek, president of Mattingly Testing Services, Inc., (1) deliberately failed to implement the requirements of Confirmatory Order (EA-08-271), which dispositioned a number of willful violations through alternative dispute resolution in 2009, including conducting an assessment of the licensee’s safety programs and providing safety training to the licensee’s staff; (2) deliberately failed to establish and maintain a prearranged response plan with the Local Law Enforcement Agency (LLEA), as required by Increased Controls Order (EA-05-090), Appendix B, Section IC-2(b); (3) deliberately provided material false information to an NRC inspector during a site visit on March 6, 2007, in violation of 10 CFR 30.10(a)(2), regarding the licensee’s effort to establish a prearranged response plan with the LLEA; (4) deliberately provided material false information to an NRC investigator while under oath on October 22, 2009, in violation of 10 CFR 30.10(a)(2), regarding the licensee’s effort to establish a prearranged response plan with the LLEA; and, (5) violated the provisions of Confirmatory Order (IA-08-055) Section V.1 which specified that Mr. Ficek was prohibited for 2 years from the date of the Order (March 6, 2009) from engaging in NRC-licensed activities since during the 2 year period Mr. Ficek (i) directed the activities of an NRC-required independent consultant, (ii) assumed the duties of the Radiation Safety Officer to determine the reporting requirements of an event involving a lost radiographic exposure device, (iii) applied, on behalf of the licensee, for reciprocity to use radioactive materials in an Agreement State pursuant to Mattingly’s NRC license, and (iv) continued to answer employees’ questions about radiation safety issue and to purchase radiographic exposure devices.
IA-09-075 | Mary K. Files | Individual | 2010-06-02 | On June 2, 2010, an Order was issued to Ms. Mary K Files, a contractor working at McGuire Nuclear Station, prohibiting her from involvement in NRC-licensed activities for a period of five years from the date the Order was issued. This enforcement action is based on Ms. Files deliberate failure to adhere to Duke Energy Carolinas, LLC, fitness-for-duty requirements. Specifically, on October 20, 2008, Ms. Files introduced and used marijuana inside the Protected Area at McGuire Nuclear Station.
IA-09-025 | Daniel Culver | Individual | 2009-12-01 | On December 1, 2009, an Order was issued to Mr. Daniel Culver, a former maintenance supervisor at Peach Bottom Atomic Power Station (Peach Bottom), prohibiting him from involvement in NRC-licensed activities for a period of three years from the date the Order was issued. This enforcement action is based on Mr. Culver’s deliberate failure to provide complete and accurate information on a personnel history questionnaire used to obtain unescorted access authorization at Peach Bottom. Specifically, Mr. Culver provided inaccurate information regarding his rank in the military, his history of misconduct in the military, and the nature of his military discharge. Mr. Culver also listed a peer, who was also a personal friend, as a former supervisor on his application for employment, even though this individual was not Mr. Culver’s supervisor at the time he submitted his application. This represents a violation of 10 CFR 50.5(a)(2), which, in part, prohibits licensee employees from deliberately submitting to a licensee information that the person knows to be incomplete or inaccurate in some respect material to the NRC.
IA-09-012 | Dr. Cedric Fernando | Individual | 2009-11-23 | On November 23, 2009, an immediately effective Confirmatory Order was issued to Dr. Cedric Fernando, the medical review officer (MRO) for Nuclear Fuel Services, Inc. (NFS), to confirm commitments made as a result of an Alternative Dispute Resolution mediation session held on May 15, 2009. This enforcement action is based on two apparent deliberate violations of NRC requirements involving Dr. Fernando’s certification that two security officers had been given a hearing examination when, in fact, they had not. Dr. Fernando agreed to: (1) ensure that an independent assessment is conducted to identify causes of this event, (2) implement lessons learned and corrective actions based on the results of the assessment, (3) participate in periodic meetings with a physician engaged in NRC-regulated activities to review issues relevant to compliance with NRC regulations, (4) take a course addressing best practices for administrative office procedures and record keeping, and (5) communicate lessons learned and experiences of this incident to an appropriate audience. In consideration of these commitments, the NRC agreed not to pursue additional enforcement action against Dr. Fernando for the apparent violations associated with this incident.
IA-08-036 | Dr. Cedric Fernando | Individual | 2009-11-23 | On November 23, 2009, an immediately effective Confirmatory Order was issued to Dr. Cedric Fernando, the medical review officer (MRO) for Nuclear Fuel Services, Inc. (NFS), to confirm commitments made as a result of an Alternative Dispute Resolution mediation session held on May 15, 2009. This enforcement action is based on three apparent deliberate violations of NRC fitness for duty (FFD) requirements related to a March 2006 incident involving a senior executive at NFS who consumed alcohol less than five hours before a scheduled working tour. Dr. Fernando agreed to: (1) ensure that an independent assessment by a certified MRO into the FFD incident discussed above is conducted, (2) implement lessons learned and corrective actions based on the results of the assessment, (3) participate in periodic meetings with an MRO engaged in NRC-regulated activities to review issues relevant to compliance with NRC regulations, (4) attend an MRO symposium, and (5) solicit information from an MRO certification program on improvements to the MRO referral process. In consideration of these commitments, the NRC agreed not to pursue additional enforcement action against Dr. Fernando for the apparent violations associated with this incident.
IA-09-021 | Douglas Poling | Individual | 2009-09-16 | On September 16, 2009, the NRC issued a Confirmatory Order (Effective Immediately) to Douglas Poling to formalize commitments made as a result of an Alternate Dispute Resolution mediation session. The commitments were made by Mr. Poling as part of a settlement agreement between Mr. Poling and the NRC regarding apparent violations of NRC requirements by Mr. Poling as President, Chief Executive Officer, and Radiation Safety Officer of Magna Chek, Inc. The agreement resolves the apparent violations involving Mr. Poling’s failure to provide the NRC with information that was complete and accurate in all material respects pursuant to 10 CFR 30.10, as well as deliberate failure to comply with an NRC Order. Mr. Poling agreed to a number of corrective actions, including: (1) he will not be involved in any NRC-licensed activities for a period of five years from the date of the Order; (2) he will provide a copy of the Order to each NRC Agreement State within which he plans to conduct activities involving radioactive materials; (3) he will not be involved in any decisions, financial or otherwise, regarding Magna Chek activities involving radioactive materials for a period of five years; (4) he will step down as Radiation Safety Officer; and (5) he will provide all copies of keys and relative documents to the Magna Chek Chief Financial Officer within one day. In consideration of these commitments, the NRC agrees to refrain from further enforcement action in connection with the subject violations, as provided to Mr. Poling.
IA-09-026 | Michael Hackett | Individual | 2009-07-28 | On July 28, 2009, the NRC issued a Confirmatory Order to Mr. Michael Hackett, Radiation Safety Officer for the Department of Veterans Affairs Medical Center, Lexington, Kentucky (VAMC Lexington). The Order is a result of an Alternative Dispute Resolution (ADR) session on June 26, 2009. ADR was requested by Mr. Hackett after an NRC investigation determined that Mr. Hackett’s actions caused VAMC Lexington to be in apparent violation by not implementing portions of the radiation safety program including: (1) failing to hold periodic Radiation Safety Committee meetings; (2) not performing annual program reviews; (3) and not performing required hazardous material training. The Order specifies that Mr. Hackett made no admission that he violated any NRC requirements and confirms commitments from Mr. Hackett for additional actions on his part to provide both the NRC and the National Health Physics Program (NHPP) for the Department of Veterans Affairs the minutes from quarterly Radiation Safety Committee meetings, annual program review results, and specific information following completion of the next training on transportation and receipt of radioactive material. Additionally, Mr. Hackett will (1) inform the NRC of his specific plans if he is assigned and has accepted responsibility for additional collateral duties, (2) inform NHPP and the NRC if he is unable to perform his duties, (3) submit to NRC an article with specific information for submittal and consideration for publication by NHPP, and (4)inform NRC if he leaves his position before the terms of the Order are completed. In consideration of these commitments from Mr. Hackett, the NRC agrees not to pursue any further enforcement action in connection with the apparent violations.
IA-08-072 | Jennifer O'Neill-Torres | Individual | 2009-03-23 | On March 23, 2009, an Order was issued to Ms. Jennifer O’Neil-Torres, the Radiation Safety Officer (RSO), President, and an owner of S&M Testing Laboratory, prohibiting her from involvement in NRC-licensed activities for a period of five years from the date the Order was issued. The Order was issued based on her engagement in deliberate misconduct, which caused the licensee to be in violation of 10 CFR 30.34(c) & 10 CFR 30.52(a). Specifically, as a RSO/President/owner, Ms. O’Neill-Torres deliberately failed to obtain NRC approval via an amendment to S&M Testing’s NRC license to authorize storage of licensed gauges at an alternate location prior to moving all gauges from authorized storage location to an unauthorized storage location and failed to provide the NRC an opportunity to inspect the gauges, failed to respond to repeated contact attempts by the NRC, and refused to provide an NRC inspector information regarding the licensed gauges including their location and conditions of storage. In this case, she not only deliberately failed to respond to repeated NRC correspondence and communication attempts, but also failed to address or correct the violations.
EA-11-254 | ABSG Consulting, Inc. | Non-Licensee | 2012-04-17 | On April 17, 2012, the NRC issued an Immediately Effective Confirmatory Order to ABSG Consulting Inc. (ABSG), confirming commitments reached as part of an alternative dispute resolution (ADR) mediation session. By letter dated January 17, 2012, the NRC identified an apparent violation of 10 CFR 50.7 to ABSG based on the NRC’s Office of Investigations, October 5, 2011 report (OI Case No. 1 2010-050). Specifically, the NRC had reached a preliminary conclusion that a former ABSG employee was terminated, in part, for participating in a Commission proceeding before the NRC Atomic Safety and Licensing Board Panel prior to his employment with ABSG. ABSG conducted its own internal investigation of the circumstances leading to the termination of the employment of the individual. The NRC recognizes that although ABSG did not admit to any apparent retaliation, ABSG nonetheless took several actions to reinforce its anti-retaliation policies. In addition, as part of the ADR settlement agreement, ABSG agreed to take several corrective actions involving increased management oversight and individual accountability including, but not limited to: (1) reinforcing through a written communication from the President ABSG the Company’s policy regarding employees’ right to raise concerns; (2) developing anti-retaliation training for all ABSG U.S. Nuclear Utilities Market Sector employees which shall include those items identified in 10 CFR 50.7, define key terms, and provide examples of discriminatory practices; (3) publishing, as part of its on-line newsletter, an article concerning the protections afforded by 10 CFR 50.7; and (4) establishing a process to conduct a secondary review of all proposed adverse actions (including written reprimand or above, but excluding reductions-in-force and other ordinary layoffs) for any of its U.S. Nuclear Utilities Market Sector employees who have engaged in protected activities. In consideration of these commitments, and other corrective actions already completed by ABSG, the NRC agreed to refrain from proposing a civil penalty and issuing a Notice of Violation.
EA-10-054 | Stone & Webster Construction, Inc. | Non-Licensee | 2010-09-10 | On September 10, 2010, a Confirmatory Order (effective immediately) was issued against Stone & Webster Construction, Inc. (S&W) to confirm commitments made as a result of an Alternative Dispute Resolution (ADR) mediation session held on August 24, 2010. By letter dated June 2, 2010, the NRC identified an apparent violation of 10 CFR 50.7 based on the United States Department of Labor (DOL) Administrative Review Board’s (ARB) September 24, 2009 Final Decision and Order of Remand (ARB Case No. 06-041). That ARB decision reversed a January 9, 2006 DOL Administrative Law Judge’s (ALJ) recommended decision where the ALJ issued a Proposed Decision and Order (ALJ Case No. 2005-ERA-6), concluding that S&W had not retaliated against a former painter foreman at the Browns Ferry Nuclear Power Plant. As part of the settlement agreement, S&W agreed to take a number of actions, including: (1) issuing a written communication from a senior S&W Power executive to reiterate, among others, the company’s policy on Safety Conscious Work Environment (SCWE) at all S&W nuclear construction and maintenance sites; (2) ensuring that an Executive Review Board reviews certain proposed adverse actions for compliance with applicable employee protection requirements and to assess and mitigate the potential chilling effect at all S&W nuclear maintenance sites; (3) revising the company’s SpeakUp program brochure to explicitly identify safety concerns as within the scope of the program; (4) conducting SCWE surveys of its employees, including craft, at all of its nuclear maintenance sites; (5) ensuring that SCWE training is provided to all of its nuclear maintenance supervisors and above; and (6) collecting, reviewing and assessing data collected through the company’s various programs for SCWE trends. In exchange for these actions, the NRC agreed not to pursue further action relating to this matter.
EA-08-301 | Wackenhut Nuclear Services | Non-Licensee | 2009-01-06 | On January 6, 2009, a Severity Level III Notice of Violation was issued to Wackenhut Nuclear Services (WNS) involving 10 CFR 50.5, which prohibits any contractor of a licensee from engaging in deliberate misconduct that causes a licensee to be in violation of any NRC regulation or condition of a license issued by the Commission. An investigation conducted by the NRC Office of Investigations determined that multiple security officers employed by WNS were deliberately inattentive on multiple occasions at Exelon’s Peach Bottom Atomic Power Station. In addition, multiple security officers deliberately failed to report observations of inattentiveness to their supervision. These security officers put Exelon in violation of 10 CFR 73.55, which requires armed responders to maintain continuous communication with each alarm station and be available to immediately respond to threats, and Peach Bottom License Condition 2.C(3), which requires, in part, reporting of aberrant behavior.
EA-12-013 | Global Nuclear Fuels - Americas, LLC | Fuel Cycle Facilities | 2012-04-23 | On April 23, 2012, a Notice of Violation was issued to Global Nuclear Fuels – Americas, LLC for a Severity Level III violation involving a significant delay in the Criticality Warning System (CWS) activation process which resulted in the failure of the CWS to be able to initiate an immediate evacuation of the facility, had an evacuation been required while special nuclear material operations were being conducted, as required by Safety Condition S-1 of its license. Specifically, between May 3 and July 17, 2011, the CWS exhibited a three minute delay before the alarm horns would sound. No actual consequences resulted from this violation because there were no incidents requiring an evacuation during this time period.
EA-11-095 | Global Nuclear Fuels - Americas, LLC | Fuel Cycle Facilities | 2011-11-14 | On November 14, 2011, the NRC issued a Notice of Violation and Proposed Imposition of Civil Penalty in the amount of $17,500 to Global Nuclear Fuel-Americas, LLC for a Severity Level (SL) III problem involving the failure to maintain the double contingency principle as it was compromised during the operation of the sinter test grinder and the risk of a high consequence event (criticality accident) increased. The NRC determined that five violations of NRC requirements directly related to the root causes that allowed the event occurred. Specifically, (1) on March 1, 2011, the licensee failed to ensure that a process design incorporated sufficient margins of safety to require at least two unlikely, independent, and concurrent changes in process conditions before a criticality accident was possible; (2) on March 1, 2011, the licensee failed to apply sufficient controls to the extent needed to reduce the likelihood of occurrence of a criticality, high consequence event, in the sinter test grinder HEPA filter enclosure so that, upon implementation of such controls, the event was highly unlikely; (3) on February 4, 2009, the licensee failed to verify as part of the change process that the controls selected and installed for the sinter test grinder HEPA enclosure would limit the UO2 holdup to less than 25 kgs by controlling a differential pressure across the ventilation housing to 4-inches of water or less; (4) on February 18, 2009, the licensee failed to conduct a criticality safety analysis (CSA) on the Sinter Test Grinder; and (5) on August 1, 2010, and January 23, 2011, the licensee failed to notify HVAC and the area manager and request a clean out of the effected Sinter Test Grinder Primary HEPA Filter housing transition when the survey results for the transition exceeded the action limit of 0.5 mr/hr above background.
EA-11-056 | United States Enrichment Corporation Paducah Facility | Fuel Cycle Facilities | 2011-08-17 | On August 17, 2011, the NRC issued a Confirmatory Order (effective immediately) to the United States Enrichment Corporation (USEC), to confirm commitments made as a result of an Alternative Dispute Resolution (ADR) settlement agreement. During an investigation NRC identified a violation involving an incident in which an operator deliberately violated applicable radiation protection procedures. Specifically, the violation involved the failure to adhere to the requirements of a USEC Paducah procedure that requires personnel to perform a whole body frisk when exiting from areas controlled for removable contamination. In response, the USEC requested ADR in an attempt to resolve the enforcement matter. USEC agreed to take a number of actions as part of this Confirmatory Order. These actions included a prompt investigation into the incident, the conduct of multiple staff briefings by USEC-Paducah management, procedural reviews and revisions as warranted, appropriate retraining and communication of lessons learned to staff, a review of the circumstances that took place during the routine operational activities that resulted in the existence of contaminated material, and disciplinary action for the employee involved in the incident. In addition, USEC committed to enhancing new employee orientation and General Employee Training at Paducah to ensure that personnel clearly understand the consequences of deliberate acts of non-compliance with regulations or procedures, and expanding its independent, Safety Conscious Work Environment assessment to include an assessment of the safety culture components of decision making and work practices. In recognition of USEC’s proposed extensive corrective actions, in addition to corrective actions already taken, the NRC agreed to not issue a Notice of Violation, and refrain from proposing a civil penalty for this matter.
EA-10-153 | Westinghouse Electric Company - Commerical Nuclear Fuel Division | Fuel Cycle Facilities | 2011-02-25 | On February 25, 2011, a Notice of Violation was issued to Westinghouse Electric Company, Commercial Nuclear Fuel Division, for a Severity Level III problem which existed on and before July 23, 2010, involving three violations associated with the Integral Fuel Burnable Absorber (IFBA) Filter Press used in the waste water handling system. Specifically, the violations involved (1) the failure to establish double contingency for the IFBA filter press to protect against an inadvertent criticality as required by License Condition 6.1.1, (2) the failure to designate items relied on for safety (IROFS) to limit the risk of a high consequence event as required by 10CFR70.61(e), and (3) the failure to designate the passive engineered controls of the IFBA filter press as an IROFS as required by the license and license application based on the conclusion that the accident scenario was not credible. In addition, two Severity Level IV violations were issued involving the failure to establish adequate operating procedures for the filter press and the failure to make a change to facility equipment in accordance with approved procedures.
EA-10-096 | GE-Hitachi Nuclear Energy Americas | Fuel Cycle Facilities | 2010-12-16 | On December 16, 2010, the NRC issued a Notice of Violation to GE-Hitachi Nuclear Energy Americas for two Severity Level III violations involving the failure to implement Special Nuclear License SNM-960, Condition S-9 and 10 CFR 20.1501. Specifically, on February 16, 2010, one worker identified contamination on his wrist at 240-260 corrected counts per minute, but failed to log the personnel contamination as required by licensee procedure; and on February 16, 2010, the licensee did not make or cause to be made surveys that were reasonable under the circumstances to evaluate the concentrations or quantities of radioactive material.
EA-10-076 | Nuclear Fuel Services, Inc. | Fuel Cycle Facilities | 2010-11-16 | On November 16, 2010, a Confirmatory Order (effective immediately) and a Notice of Violation (NOV) were issued to Nuclear Fuel Services, Inc. (NFS) to confirm commitments made as a result of an Alternative Dispute Resolution (ADR) mediation sessions held on October 4, 2010. This enforcement action is based on the failure of NFS to provide complete and accurate information to the NRC, as required by 10CFR70.9(a), on two occasions. Specifically, (1) on November 25, 2008, NFS submitted a response to a previously issued NOV stating that all fire dampers in Procedure NFS-GH-22 were inspected in September 2008 and all passed the inspection, when 12 of the fire dampers had not been inspected; and (2) in August 2009, during an inspection to verify the corrective actions as documented in the response to the previously issued NOV, a former NFS employee created and provided a document to an NRC inspector that indicated that all but one of the dampers had been fully inspected in 2008, when in fact more than one of the dampers had not been fully inspected. The NRC concluded that these actions were willful and associated with the same former employee. As a result of the ADR agreement, the licensee agreed to a number of actions, including: (1) issuance of a NOV as part of the Confirmatory Order; (2) conducting an effectiveness review within one year of each corrective action to the NOV; (3) performing an assessment of the effectiveness of its corrective actions by an independent group to assure adequacy and accuracy of information submitted to the NRC; (4) developing and implementing an appropriate safety culture improvement plan and conducting periodic integrated safety culture assessments; and (5) assessing its current corrective action program (CAP) against NQA-1-2008 and submitting a license amendment request within nine months incorporating the CAP into its license. In recognition of these actions, the NRC agreed to refrain from proposing a civil penalty for this matter.
EA-10-124 | Westinghouse Electic Company | Fuel Cycle Facilities | 2010-11-03 | On November 3, 2010, a Notice of Violation and Proposed Imposition of a Civil Penalty in the amount of $17,500 was issued to Westinghouse Electric Company, Commercial Nuclear Fuel Division, for a Severity Level III problem involving two violations associated with a spill of uranium bearing ammoniated waste water inside the plant on January 25, 2010. Specifically, the violations involved (1) the failure to identify in the Integrated Safety Analysis (ISA) that a spill in the quarantine tank system could lead to an intermediate consequence event as required by 10CFR70.62(c)(1), and (2) the failure to designate items relied on for safety (IROFS) to limit the risk of an intermediate consequence event resulting from an overflow of the quarantine system as required by 10CFR70.61(e). In addition, two Severity Level IV violations involving failure to follow license condition requirements, and a Severity Level IV problem involving three violations associated with failure to follow Site Emergency Plan requirements were issued.
EA-08-204 | Babcock and Wilcox | Fuel Cycle Facilities | 2010-10-12 | On October 12, 2010, the Atomic Safety and Licensing Board (Board) issued an Order approving a settlement agreement between Babcock and Wilcox Nuclear Operations Group, Inc. (B&W NOG) (formerly BWX Technologies (BWXT), Inc) and the NRC related to the failure by B&W NOG to adequately neutralize a spill of hydrofluoric acid (HF) which, on April 28, 2008, resulted in an operator receiving an ocular exposure requiring onsite and offsite emergency medical treatment. The original enforcement action associated with this incident, which was retracted and reissued on February 23, 2010, was issued on October 20, 2008 (ML082960026). In accordance with the Board Order, the NRC agreed (1) to withdraw the Order imposing a monetary civil penalty in the amount of $32,500 issued on June 15, 2010 (ML101580256); and, (2) to recategorize the violation issued on February 23, 2010 (ML100540701) from a Severity Level III violation to a violation with no severity level. In accordance with the Board Order, B&W agreed to (1) not challenge the existence of a violation of NRC requirements related to the HF spill and withdraw its request for a hearing; (2) pay a settlement fee of $32,500 in lieu of the withdrawn civil penalty; (3) perform one quarterly emergency drill within a twelve-month period related to a chemical exposure event; and, (4) give a presentation addressing lessons learned at the 2011 Fuel Cycle Information Exchange.
EA-10-086 | Nuclear Fuel Services, Inc. | Fuel Cycle Facilities | 2010-09-02 | On September 2, 2010, a Notice of Violation, Exercise of Enforcement Discretion, and Proposed Imposition of a Civil Penalty in the amount of $140,000 was issued to Nuclear Fuel Services, Inc. (NFS). This action was based on a Severity Level III problem involving three violations associated with an event which occurred on October 13, 2009. The three violations involved (1) the failure to have adequate engineered or administrative controls for operations of the bowl cleaning station in violation of 10 CFR 70.61(b); (2) the failure to comply with multiple facility operating procedures regarding the facility system change process; and (3) the failure to maintain records necessary to support NFS’s determination that specific facility changes did not require prior NRC approval in violation of 10 CFR 70.72. Specifically, during routine facility operations in the uranium-aluminum line of the Blended Low-enriched Uranium Preparation Facility, nitric acid was added into the bowl cleaning stations which contained small particles of high-enriched uranium scrap material, and the resultant solution produced an unexpectedly high exothermic chemical reaction deforming some of the process piping. The temperatures from the reaction created excess nitrogen compound gases which resulted in the evacuation of the building. Although the failure to have adequate engineered or administrative controls for operations of the bowl cleaning station did not result in any actual personnel exposure consequences in this case, a more significant event could have resulted in a high consequence occupational exposure under different circumstances. In recognition of particularly poor licensee performance and previous escalated enforcement history, the NRC exercised enforcement discretion and doubled the $70,000 Civil Penalty derived from the normal civil penalty assessment process.
EA-09-268 | Global Nuclear Fuels - Americas, LLC | Fuel Cycle Facilities | 2010-06-09 | On June 9, 2010, a Notice of Violation and Exercise of Enforcement Discretion (Notice) was issued to Global Nuclear Fuels – Americas, LLC (GNF-A). This action was based on a Severity Level III problem involving three violations of regulatory requirements. Specifically, the licensee failed to (1) identify credible accident scenarios as required by the license; (2) characterize criticality accident scenarios in the integrated safety analysis (ISA) as high consequence events as required by the license; and (3) designate engineered or administrative controls as items relied on for safety (IROFS) when necessary to comply with the performance requirements of 10 CFR 70.61(b) – (d), as required by 10 CFR 70.61(e). Because, in part, the NRC staff and the licensee did not share a common understanding of GNF-A’s application of its ISA methodology to scenario evaluation and IROFS identification during the ISA summary review and related inspection activities, the NRC concluded that enforcement discretion to forego proposing a civil penalty was appropriate in this case. No actual consequences resulted from these violations because there were no incidents and no existing safety controls were identified as degraded.
EA-09-272 | AREVA NP, Inc. | Fuel Cycle Facilities | 2010-04-26 | On April 26, 2010, a Confirmatory Order (effective immediately) was issued to AREVA NP – Richland, Inc. (AREVA) to formalize commitments reached as part of an alternative dispute resolution (ADR) mediation session involving a violation of a facility procedure by an employee who willfully defeated the function of an Item Relied On For Safety (IROFS) on April 21, 2009. Specifically, an electronic eye sensor known as the vacuum wand interlock was deliberately bypassed by an employee and made to work by using tape. As a result, IROFS 1111 was not available and reliable as required by 10 CFR 70.61(e). Although the vacuum wand interlock was disabled, sufficient system IROFS remained in service to perform the intended safety function for identified accident scenarios and protect the health and safety of the public. As part of the settlement agreement, AREVA agreed to take a number of actions in addition to those already completed. These additional actions include: (1) incorporating lessons learned from this incident, including enhanced safety conscious work environment (SCWE) training, into General Employee training for new employees and annual refresher training for all Richland employees; (2) implementing a management observation program for the purpose of reinforcing task performance standards and work practices; (3) performing a survey to determine the results of efforts to increase supervisor availability in the work area; and (4) developing a presentation on the incident and lessons learned with regard to work practices for a future industry forum. In recognition of these actions, the NRC agreed to refrain from proposing a civil penalty and issuing a Notice of Violation or other enforcement action.
EA-09-263 | Babcock and Wilcox | Fuel Cycle Facilities | 2010-01-11 | On January 11, 2010, a Notice of Violation and Proposed Imposition of a Civil Penalty in the amount of $35,000 was issued, to Babcock and Wilcox Nuclear Operations Group, Inc. (B&W -NOG). This action was based on a Severity Level III violation involving the failure of the licensee to declare an Alert in a timely manner as required by Appendix G to their Emergency Plan. Specifically, on July 15, 2009, the licensee failed to declare an Alert for more than 2 hours even though employees were cognizant that during that time, critically controls associated with a band saw reservoir did not exist and that the lost controls could not be immediately reestablished. Although the failure to declare an Alert in a timely manner did not result in any actual consequences in this case, the potential consequences of an untimely emergency declaration could have been significant under different circumstances. In addition, a Severity Level III problem associated with three procedural violations was identified as a result of this incident. The three violations involved the failure of the licensee (1) to ensure that the band saw’s built-in coolant reservoir was disabled and not usable prior to operation of the band saw, (2) to establish controls on the band saw cutting fluid reservoir to prevent process changes which would make a criticality accident possible such as accumulation of cutting fluid or fissile material in the reservoir, and (3) to evaluate an accident scenario or establish appropriate controls preventing the accumulation of high enriched uranium and moderator in the band saw cutting fluid reservoir, an unfavorable geometry vessel. In accordance with the Enforcement Policy, a civil penalty was not proposed for these violations.
EA-09-117 | Shaw AREVA MOX Services | Fuel Cycle Facilities | 2009-11-24 | On November 24, 2009, an immediately effective Confirmatory Order was issued to Shaw AREVA MOX Services (MOX Services) to confirm commitments made as a result of an Alternative Dispute Resolution mediation session held on October 8, 2009. This enforcement action is based on an apparent deliberate violation of 10 CFR 70.9, “Completeness and accuracy of information.” Specifically, a senior structural engineer directed or allowed a junior engineer to sign the senior structural engineer’s signature on travelers, which are used as part of MOX Services process to signify that field drawings match design drawings. MOX Services agreed to take a number of corrective actions, including: (1) periodic quality assurance assessments and surveillances of vendor submittals, including drawings, to ensure design requirements are properly implemented; (2) periodic training for all MOX Services project personnel, including onsite contractors, on the definition of and consequences associated with material false statements, as well as the obligations of the signer of project records; (3) periodic safety conscious work environment surveys through the life of construction. In consideration of these commitments, and additional corrective actions previously taken by MOX Services in response to this issue, the NRC agreed to refrain from issuing a civil penalty or Notice of Violation for this apparent violation.
EA-08-321 | Nuclear Fuel Services, Inc. | Fuel Cycle Facilities | 2009-11-23 | On November 23, 2009, an immediately effective Confirmatory Order was issued to Nuclear Fuel Services, Inc. (NFS) to confirm commitments made as a result of an Alternative Dispute Resolution mediation session held on September 16, 2009. This enforcement action is based on two apparent violations of NRC requirements involving a primary physician who apparently deliberately certified that two security officers had been given a hearing examination when, in fact, they had not. NFS agreed to take the following actions to preclude recurrence of these violations: (1) complete an assessment of why this issue was not entered into the corrective action program and why a root cause analysis was not completed, (2) complete an extent of condition review, (3) benchmark other licensee’s oversight of primary physicians to identify best practices, (4) ensure the primary physician participates in periodic meetings with a physician engaged in NRC-regulated activities to review issues relevant to compliance with NRC regulations, (5) ensure the primary physician initiates an evaluation of procedures and processes with a physician engaged in NRC-regulated activities, (6) establish standards for primary physicians and other contract medical specialists, and (7) enhance selected administrative procedures. In consideration of these commitments, the NRC agreed to refrain from issuing a civil penalty or Notice of Violation for these apparent violations.
EA-08-103 | Nuclear Fuel Services, Inc. | Fuel Cycle Facilities | 2009-11-23 | On November 23, 2009, an immediately effective Confirmatory Order was issued to Nuclear Fuel Services, Inc. (NFS) to confirm commitments made as a result of an Alternative Dispute Resolution mediation session held on September 15, 2009. This enforcement action is based on seven apparent violations, some apparently committed deliberately, of NRC fitness for duty (FFD) requirements related to a March 2006 incident involving a senior executive at NFS who consumed alcohol less than five hours before a scheduled working tour. NFS agreed to take actions to strengthen the FFD program, including: (1) establishment of an oversight board for behavioral observation program (BOP), FFD, and other issues; (2) enhancements to the employee concerns program; (3) changes to the FFD training program to include a discussion of case studies, including this incident, and issue reporting; (4) improvements to procedures and processes associated with FFD and BOP; (5) improved procedural guidance for, and assessment of, the medical review officer; and (6) changes to the process for responding to NRC requests for information to ensure completeness and accuracy of information. In consideration of these commitments, the NRC agreed to refrain from issuing a civil penalty or Notice of Violation for these apparent violations.
EA-08-344 | United States Enrichment Corporation - Paducah Facility | Fuel Cycle Facilities | 2009-08-18 | On August 18, 2009, an effective immediately Confirmatory Order was issued to United States Enrichment Corporation (USEC) to confirm commitments made as a result of an Alternative Dispute Resolution (ADR) mediation session held on July 2, 2009. The parties agreed to engage in ADR following NRC’s February 25, 2009, letter to USEC wherein four apparent violations were identified based on information developed during an investigation at the USEC-Paducah facility, involving violations of station procedures which occurred during and subsequent to an incident in January 2008. Specifically, the violations involved: (1) failing to disconnect equipment during movement of a Uranium Hexaflouride (UF6) cylinder causing damage to the manifold; (2) deliberately attempting to conceal the damage; (3) deliberately falsifying documents indicating the equipment was properly disconnected; and (4) deliberately denying knowledge of the procedure violations. As part of the agreement, USEC agreed to take a number of actions including actions to address the willful actions of USEC employees, procedural use, recurring training for Operations and Maintenance supervisors to reinforce conduct of principles and procedural compliance, and subsequent effectiveness reviews of corrective actions. In addition, USEC committed to conducting a review of this incident and a limited number of other significant events, to determine if weaknesses in any of the 13 safety culture components, as identified in NRC Regulatory Information Summary 2006-13, caused or significantly contributed to the event. In recognition of these actions, the NRC agreed to refrain from proposing a civil penalty and issuing a Notice of Violation or other enforcement action for the matters discussed in the NRC letter to USEC dated February 6, 2009.
EA-08-280 | United States Enrichment Corporation - Paducah Facility | Fuel Cycle Facilities | 2009-08-18 | On August 18, 2009, an immediately effective Confirmatory Order was issued to United States Enrichment Corporation (USEC) to confirm commitments made as a result of an Alternative Dispute Resolution (ADR) mediation session held on July 1, 2009. The parties agreed to engage in ADR following NRC’s February 6, 2009, letter to USEC wherein an apparent violation of 10 CFR 95.39(b)(3) was identified based on information developed during an investigation at the licensee’s Paducah facility. As part of the agreement, USEC agreed to take a number of actions including revising procedures and related training, continuation of recurring training for Operations and Maintenance supervisors to reinforce conduct of principles and procedure compliance, conducting interactive informational training sessions with employees to identify critical job tasks and tools to prevent and protect against causing adverse events when performing critical tasks, and communicating the facts of the violation and lessons learned to employees at all USEC facilities. In recognition of these actions, the NRC agreed to refrain from proposing a civil penalty and issuing a Notice of Violation or other enforcement action for the matters discussed in the February 6, 2009, letter.
EA-06-140 | USEC, Inc. and its Subsidiary, United States Enrichment Corporation | Fuel Cycle Facilities | 2009-08-13 | On August 13, 2009, a Confirmatory Order (effective immediately) was issued to USEC Inc. and its subsidiary the United States Enrichment Corporation to confirm commitments made as a result of an Alternative Dispute Resolution (ADR) settlement agreement, regarding an apparent violation of 10 CFR 76.7, "Employee protection." The action is based on the United States Department of Labor Administrative Review Board’s (ARB’s) August 19, 2008, Final Decision and Order (ARB Case Nos. 06-055, 06-058, and 06-119) affirming a DOL Administrative Law Judge’s finding. As part of the settlement agreement, USEC agreed to take a number of actions that, among others, included: a third party independent assessment of the safety conscious work environment (SCWE) at the Paducah site; and providing SCWE training (including case studies) to Paducah and Portsmouth Gaseous Diffusion Plants, American Centrifuge Plant, American Centrifuge Lead Cascade Facility, and designated USEC Headquarters managers and employees.
EA-08-244 | Westinghouse Electric Company, LLC | Fuel Cycle Facilities | 2009-08-06 | On August 6, 2009, the NRC issued a Confirmatory Order (Effective Immediately) to Westinghouse Electric Company, LLC (WEC) – Commercial Nuclear Fuel Division to formalize commitments made as a result of an ADR mediation session. The commitments were made by WEC as part of a settlement agreement between WEC and the NRC regarding apparent violations of NRC requirements by a former contract foreman. The agreement resolves the apparent violations involving WEC’s maintaining inaccurate records associated with employee training and testing of a ventilation system filter, an Item Relied On For Safety, which was identified during an NRC Office of Investigations (OI) investigation. WEC agreed to a number of corrective actions, including procedural revisions, improved management oversight of contractor activities, a review of the causes of the falsification issues, and incorporation of lessons learned into employee initial and annual refresher training. In consideration of these commitments, the NRC agreed to refrain from further enforcement action in this matter.
EA-08-330 | United States Enrichment Corporation | Fuel Cycle Facilities | 2009-03-04 | On March 4, 2009, a Notice of Violation (NOV) was issued to United States Enrichment Corporation for a Severity Level III violation. Specifically, on September 8, 2008, the licensee moved a cylinder containing liquid uranium hexafluoride to a storage pad with mobile equipment (straddle carrier) instead of an approved crane in violation of Technical Safety Requirement 2.1.3.14 of their license. In this case, no adverse affects to the public or environment resulted from this unauthorized moved.