## Sheet1
Findings from Fire Inspections
Site | Region | Event Date | Item Type | Title | Report Number and/or Comments | Year First Observed | Report Type
ANO | 4 | 2007-10-19 | NCV (Green ) | (PIM) FAILURE TO MAINTAIN ADEQUATE FIRE BRIGADE STAFFING DURING ALTERNATE SHUTDOWN | 2007006 | 2007 | Triennial
ANO | 4 | 2001-08-03 | Violation (White ) | (PIM) The Acceptability of the Use of Manual Actions in Lieu of Providing Protection for Cables Associated with Equipment Necessary for Achieving and Maintaining Hot Shutdown. | Open in TR 2001006 and discussed in IR 2003012 and closed in Supplemental Inspection Report 200511. | 2001 | Triennial
ANO | 4 | 2000-09-30 | NCV (Green ) | (PIM) INOPERABILITY OF UNIT 2 FIRE DOOR 269 | 2000016 | 2000 | Annual/Quarterly
ANO | 4 | 2001-03-31 | NCV (Green ) | (PIM) INDIVIDUAL WITHOUT REQUIRED TRAINING PERFORMED FIRE WATCH PATROLS | 2000013 | 2001 | Annual/Quarterly
ANO | 4 | 2001-10-22 | NCV (Green ) | (PIM) FAILURE TO ENSURE THAT ONE TRAIN OF BWST OUTLET VALVES WAS FREE OF FIRE DAMAGE. | 2001007 | 2001 | Annual/Quarterly
ANO | 4 | 2001-12-21 | Finding (Green ) | (PIM) FIRE BRIGADE DRILL HOSE SELECTION ISSUE AND PREFIRE PLAN ISSUE. | 2001008 | 2001 | Annual/Quarterly
ANO | 4 | 2002-09-21 | NCV (Green ) | (PIM) FAILURE TO HAVE ADEQUATE PROCEDURAL CONTROLS FOR THE USE OF FIRE RETARDANT TREATED WOOD | 2002004 | 2002 | Annual/Quarterly
ANO | 4 | 2004-06-23 | NCV (Green ) | (PIM) FAILURE TO PROVIDE ADEQUATE COMPENSATORY MEASURES FOR A LOSS OF FIRE WATER TO THE INTAKE STRUCTURE | 2004003 | 2004 | Annual/Quarterly
ANO | 4 | 2004-09-23 | NCV (Green ) | (PIM) FAILURE TO PERFORM REQUIRED HYDROSTATIC TESTING OF PRESSURIZED FIRE EXTINGUISHERS | 2004004 | 2004 | Annual/Quarterly
ANO | 4 | 2006-03-24 | NCV (Green ) | (PIM) FAILURE TO ENSURE FIRE DOORS WERE LATCHED | 2006002 | 2006 | Annual/Quarterly
ANO | 4 | 2006-12-31 | NCV (Green ) | (PIM) FIRE DURING HOT WORK ACTIVITIES ON THE CONTAINMENT SUMP STRAINER | 2006005 | 2006 | Annual/Quarterly
ANO | 4 | 2007-12-31 | NCV (Green ) | (PIM) Failure to Maintain Fire Barrier for Emergency Feedwater Pump A | 2007005 | 2007 | Annual/Quarterly
BF | 2 | 2001-09-22 | NCV (Green ) | (PIM) Error in Analysis of RHR System Results in Failure to Meet Appendix R, Criterion III.L.2.B | Open in TR 2000008 as URI and closed in IR 2001003 as NCV. This finding corresponds to the year 2000. This finding appeared in the quarterly/annual findings. | 2000 | Triennial
BF | 2 | 2003-10-03 | NCV (Green ) | (PIM) Changes Made to the Fire Protection Program Regarding Compensatory Fire Watch Implementation Without NRC Approval | 2003007 | 2003 | Triennial
BF | 2 | 2006-09-15 | NCV (Green ) | (PIM) Safe Shutdown Instruction Directs Operators to Connect 4 KV SD BD "A" to a Potentially Fire-Induced Fault in FA 8 | 2006014 | 2006 | Triennial
BF | 2 | 2006-09-15 | NCV (Green ) | (PIM) Cellular Phone Communications Unreliable for Alternate Shutdown in FA16 | 2006014 | 2006 | Triennial
BF | 2 | 2010-01-20 | NCV (Green ) | Deficiencies with Emergency Lighting Units | 2009007 | 2009 | Triennial
BF | 2 | 2010-01-21 | NCV (Green ) | Failure to Establish Adequate Compensatory Measures for an Out-of-Service Hose Station | 2009007 | 2009 | Triennial
BF | 2 | 2009-06-05 | Violation (Yellow ) | Violation of 10 CFR Part 50, Appendix R, Section III.G | Open in TR 2006014 as URI, apparent violation in 2009009 and Yellow Violation in the final determination report 2010007 | 2006 | Triennial
BF | 2 | 2009-06-06 | Violation (White ) | The licensee failed to establish, implement, and maintain an adequate procedure for combating a plant fire event. | Open in TR 2006014 as URI, apparent violation in 2009009 and Yellow Violation in the final determination report 2010008 | 2006 | Triennial
BF | 2 | 2001-09-22 | NCV (Green ) | (PIM) Inadequate Fire Damper Maintenance Procedure Results in Inoperable Emergency Diesel Generators | 2001003. This finding appeared in the triennial search but it was a licensee identified violation during a quarterly inspection report. | 2001 | Annual/Quarterly
BF | 2 | 2001-09-22 | NCV (Green ) | (PIM) ERROR IN ANALYSIS OF RHR SYSTEM RESULTS IN FAILURE TO MEET APPENDIX R, CRITERION III.L.2.B | 2001003 | 2001 | Annual/Quarterly
BF | 2 | 2006-06-30 | NCV (Green ) | (PIM) Failure to Implement Required Fire Watches | 2006003 | 2006 | Annual/Quarterly
BRAI | 3 | 2000-11-30 | NCV (N/A ) | (PIM) Molded Case Circuit Breakers Not Periodically Inspected and Tested | 2000006 | 2000 | Triennial
BRAI | 3 | 2000-11-30 | NCV (N/A ) | (PIM) Instrumentation Not Available for Determining RCP Seal Temperature | 2000006 | 2000 | Triennial
BRAI | 3 | 2000-11-30 | NCV (N/A ) | (PIM) ESW Suction Valves Not Protected from Fire Induced Spurious Actuations | 2000006 | 2000 | Triennial
BRAI | 3 | 2003-07-11 | NCV (Green ) | (PIM) Failure to assess and address Coordination Calculation Conclusions/Recommendations | 2003005 | 2003 | Triennial
BRAI | 3 | 2003-07-11 | NCV (Green ) | (PIM) MOLDED CASE CIRCUIT BREAKERS NOT PERIODICALLY CYCLED/EXERCISED | 2003005 | 2003 | Triennial
BRAI | 3 | 2006-06-30 | NCV (Green ) | (PIM) Failure to Adequately Control Transient Combustibles | 2006009 | 2006 | Triennial
BRAI | 3 | 2006-06-30 | NCV (Green ) | (PIM) Inadequate Pre-Fire Plan | 2006009 | 2006 | Triennial
BRAI | 3 | 2006-06-30 | NCV (Green ) | (PIM) Failure to Take Effective Corrective Action | 2006009 | 2006 | Triennial
BRAI | 3 | 2009-03-06 | Finding (Green ) | (PIM) Failure to Perform Validation for Safe Shutdown Manual Actions | 2009003 | 2009 | Triennial
BRAI | 3 | 2009-03-06 | NCV (Green ) | (PIM) Failure to Take Effective Corrective actions to Maintain Capability of foam Suppression Systems | 2009003 | 2009 | Triennial
BRAI | 3 | 2002-02-18 | NCV (Green ) | (PIM) FAILURE TO FOLLOW EQUIPMENT CONTROL PROCEDURE | 2002002 | 2002 | Annual/Quarterly
BRAI | 3 | 2002-09-30 | NCV (Green ) | (PIM) FAILURE TO ESTABLISH COMPENSATORY FIREWATCHES FOR TWO REMOVED FIRE RATED BARRIERS | 2002007 | 2002 | Annual/Quarterly
BRAI | 3 | 2005-03-31 | Finding (Green ) | (PIM) POOR CONTROL OF COMBUSTIBLE MATERIAL AND TEMPORARY POWER SOURCES | 2005002 | 2005 | Annual/Quarterly
BRAI | 3 | 2006-06-30 | NCV (Green ) | (PIM) FAILURE TO MAINTAIN FIRE BARRIER IN ACCORDANCE WITH FIRE PROTECTION PROGRAM | 2006003 | 2006 | Annual/Quarterly
BRAI | 3 | 2006-09-30 | NCV (Green ) | (PIM) FAILURE TO MAINTAIN ELECTRICALLY SUPERVISED FIRE DOORS IN ACCORDANCE WITH THE FIRE PROTECTION PROGRAM | 2006004 | 2006 | Annual/Quarterly
BRAI | 3 | 2006-12-31 | NCV (Green ) | (PIM) TRANSIENT COMBUSTIBLES STAGED DIRECTLY BENEATH SAFETY RELATED HORIZONTAL CABLE TRAYS | 2006005 | 2006 | Annual/Quarterly
BRAI | 3 | 2008-09-30 | NCV (Green ) | (PIM) FAILURE TO COMPLY WITH THE SPACING STANDARD FOR SPRINKLER SYSTEMS IN ACCORDANCE WITH THE LICENSEE FIRE PROTECTION PROGRAM REQUIREMENTS | 2008004 | 2008 | Annual/Quarterly
BRAI | 3 | 2008-09-30 | NCV (SL-IV ) | (PIM) FAILURE TO PROPERLY EVALUATE REMOVAL OF CARBON DIOXIDE FIRE SUPPRESSION FOR THE UPPER CABLE SPREADING ROOM CARBON DIOXIDE FIRE SUPPRESSION | 2008004 | 2008 | Annual/Quarterly
BRAI | 3 | 2009-06-30 | NCV (Green ) | (PIM) ISOLATION OF LOWER CABLE SPREADING ROOM CARBON DIOXIDE FIRE SUPPRESSION | First discussed in 2008004 and closed in 2009004 | 2008 | Annual/Quarterly
BRAI | 3 | 2009-09-30 | NCV (Green ) | (PIM) FAILURE TO PROVIDE CONTINUOUS MONITORING OF A FIRE DOOR | 2009004 | 2009 | Annual/Quarterly
BRAI | 3 | 2009-09-30 | NCV (Green ) | (PIM) FAILURE OF FIRE PROTECTION VALVE STROKE PROCEDURE RESULTS IN TRIP OF B TRAIN OF MAIN CONTROL ROOM VENTILATION | 2009004 | 2009 | Annual/Quarterly
BRU | 2 | 2004-11-19 | NCV (Green ) | (PIM) Inadequate Implementation of the Fire Protection Program For ERFBS Fire Barrier Protection of Circuits In Fire Area DG-8 | 2004010 | 2004 | Triennial
BRU | 2 | 2002-09-28 | NCV (Green ) | (PIM) FAILURE TO HAVE INSTALLLED FIXED FIRE SUPPRESSION SYSTEMS THAT ARE CAPABLE OF MINIMIZING FIRE DAMAGE TO SAFE SHUTDOWN CABLING DURING FLOOR LEVEL TRANSIENT COMBUSTIBLE FIRES IN THE UNIT 1 AND 2 CSRs | 2002003 | 2002 | Annual/Quarterly
BRU | 2 | 2009-12-31 | NCV (Green ) | (PIM) Failure To Identify and Correct Degraded Fire Protection Sprinklers | 2009005 | 2009 | Annual/Quarterly
BRU | 2 | 2009-12-31 | NCV (Green ) | (PIM) Failure To Adequately Implement Design Control Measures For The Fire Protection Program | 2009005 | 2009 | Annual/Quarterly
BV | 1 | 2001-06-08 | NCV (Green ) | (PIM) INADEQUATE PROCEDURE FOR SAFE SHUTDOWN FROM OUTSIDE OF THE CONTROL ROOM COULD RESULT IN DAMAGE TO EMERGENCY DIESEL GENERATOR | 2001005 | 2001 | Triennial
BV | 1 | 2001-03-31 | NCV (Green ) | (PIM) FAILURE TO PROPERLY CONTROL COMBUSTIBLE MATERIALS IN ACCORDANCE WITH THE FIRE PROTECTION PROGRAM | 2001002 | 2001 | Annual/Quarterly
BV | 1 | 2001-03-31 | NCV (Green ) | (PIM) FAILURE TO ESTABLISH THE COMPENSATORY MEASURES FOR AN INOPERABLE FIRE DOOR IN THE UNIT 2 EMERGENCY SWITCH GEAR | 2001002 | 2001 | Annual/Quarterly
BV | 1 | 2007-08-07 | NCV (Green ) | (PIM) POST-FIRE SAFE SHUTDOWN CAPABILITY DEGRADED DUE TO AMMONIA GAS HAZARD | 2007004 | 2007 | Annual/Quarterly
BYRO | 3 | 2007-06-30 | NCV (Green ) | (PIM) ALTERNATIVE SHUTDOWN USING THE REMOTE SHUTDOWN PANEL. | Open in TR 2004005 as URI and was closed in IR 2007003 as NCV. This finding corresponds to the year 2004. | 2004 | Triennial
BYRO | 3 | 2007-03-31 | NCV (Green ) | (PIM) ADEQUACY OF SAFE SHUTDOWN PROCEDURES TO ADDRESS DRAINING OF THE RWST. | It was an URI from TR 2004005 and was closed in IR 2007002. This finding corresponds to the year 2004. | 2004 | Triennial
BYRO | 3 | 2004-07-09 | NCV (Green ) | (PIM) Failure to Install Fire Detector in Accordance With NFPA 72E | 2004005 | 2004 | Triennial
BYRO | 3 | 2004-07-09 | NCV (Green ) | (PIM) Faulted Pressurizer PORV Power Source Restoration Directions Inadequate | 2004005 | 2004 | Triennial
BYRO | 3 | 2004-07-09 | NCV (Green ) | (PIM) Design Control of Fire Loading Calculations | 2004005 | 2004 | Triennial
BYRO | 3 | 2005-06-30 | NCV (Green ) | (PIM) Insufficient Fire Seal Material in Penetration Between Emergency Diesel Generator Rooms and Associated Switchgear Rooms | 2005004 | 2005 | Annual/Quarterly
BYRO | 3 | 2006-09-30 | NCV (Green ) | (PIM) FAILURE TO MAINTAIN FIRE BARRIERS IN ACCORDANCE WITH FIRE PROTECTION PROGRAM. | 2006004 | 2006 | Annual/Quarterly
BYRO | 3 | 2007-06-30 | NCV (Green ) | (PIM) FAILURE TO FIRE PROOF STRUCTURAL STEEL BEAMS TO ACHIEVE A 3-HOUR FIRE RATING. | 2007003 | 2007 | Annual/Quarterly
BYRO | 3 | 2008-06-30 | NCV (Green ) | (PIM) FIRE SUPPRESSION SPRINKLER OBSTRUCTION IN THE DIESEL OIL STORAGE TANK ROOM | 2008003 | 2008 | Annual/Quarterly
BYRO | 3 | 2008-09-30 | NCV (Green ) | (PIM) ISOLATING CARBON DIOXIDE FIRE SUPPRESSION SYSTEM IN UPPER CABLE SPREADING ROOMS WITHOUT PRIOR NRC APPROVAL | 2008004 | 2008 | Annual/Quarterly
CALL | 4 | 2000-08-22 | NCV (Green ) | (PIM) Three examples of making a change to the fire protection program, without prior Commission approval, that adversely affected the ability to achieve and maintain safe shutdown. | 2000013 | 2000 | Triennial
CALL | 4 | 2000-08-09 | NCV (Green ) | (PIM) Failure to maintain in effect a 3-hour rated fire barrier between redundant trains of equipment necessary to achieve and maintain safe shutdown. | 2000013 | 2000 | Triennial
CALL | 4 | 2004-03-24 | NCV (Green ) | (PIM) Inadequate smoke alarm response procedure for control room supply. | Open in TR 2003007 as URI and closed in IR 2004002 as NCV. | 2003 | Triennial
CALL | 4 | 2003-10-21 | NCV (Green ) | (PIM) Failure to Take Required Compensatory Measures When CREVIS Operation Rendered ESF Switchgear Room Halon System Inoperable | 2003007 | 2003 | Triennial
CALL | 4 | 2009-02-27 | NCV (Green ) | (PIM) Failure to Correct Problems with Fire Protection Impairment Permits | 2009006 | 2009 | Triennial
CALL | 4 | 2002-06-25 | NCV (Green ) | (PIM) Unsecured fire door. | 2002002 | 2002 | Annual/Quarterly
CALL | 4 | 2004-12-31 | NCV (Green ) | (PIM) Failure to Establish Required Fire Watch. | 2004005 | 2004 | Annual/Quarterly
CALL | 4 | 2004-12-31 | NCV (Green ) | (PIM) Failure to Maintain the Integrity of an Auxiliary Building Fire Door | 2004005 | 2004 | Annual/Quarterly
CALL | 4 | 2005-03-24 | NCV (Green ) | (PIM) Unplanned loss of water fire suppression due to an inadequate testing procedure. | 2005002 | 2005 | Annual/Quarterly
CALL | 4 | 2005-03-24 | NCV (Green ) | (PIM) Failure to maintain the minimum number of fire brigade members on site. | 2005002 | 2005 | Annual/Quarterly
CALL | 4 | 2005-06-23 | NCV (Green ) | (PIM) Failure to maintain the integrity of a three-hour auxiliary building fire door. | 2005003 | 2005 | Annual/Quarterly
CALL | 4 | 2005-12-31 | NCV (Green ) | (PIM) Failure to adequately implement continuous compensatory fire watches. | 2006005 | 2006 | Annual/Quarterly
CALL | 4 | 2006-12-31 | NCV (Green ) | (PIM) Failure to Identify a Degraded Fire Barrier | 2006005 | 2006 | Annual/Quarterly
CALV | 1 | 2001-09-14 | NCV (Green ) | (PIM) Inadequate abnormal operating procedures for post-fire safe shutdown. (Section 1RO5.07) | 2001007 | 2001 | Triennial
CALV | 1 | 2001-09-14 | NCV (Green ) | (PIM) Failure to account for steam generator inventory losses due to blow down flow. (Section 1RO5.07). | 2001007 | 2001 | Triennial
CALV | 1 | 2001-09-14 | NCV (Green ) | (PIM) 22 Saltwater air compressor Appendix R hand switch fuses shunted. LER 50-318/2001-001 (Section 4OA3.1) | 2001007 | 2001 | Triennial
CALV | 1 | 2004-02-28 | NCV (Green ) | Inadequate Combustible Material Control in Unit 1 69’ West Electrical Room | 2004003 | 2004 | Triennial
CALV | 1 | 2004-02-28 | NCV (Green ) | Failure to Provide Protection in Accordance with 10 CFR Part 50, Appendix R, Section III.G.2. | 2004003 | 2004 | Triennial
CALV | 1 | 2004-02-28 | Finding (Green) | Inadequate Breaker Coordination | 2004003 | 2004 | Triennial
CALV | 1 | 2000-05-13 | Finding (Green ) | (PIM) Degraded Protect wire fire detection system | 2000004 | 2000 | Annual/Quarterly
CALV | 1 | 2000-05-13 | Finding (N/A ) | (PIM) Protect wire degradation - cross-cutting issue, PI&R | 2000004 | 2000 | Annual/Quarterly
CAT | 2 | 2006-03-31 | NCV (Green ) | (PIM) Derating Selected Emergency Lighting Units Required for Post-Fire Safe Shutdown | Open in TR 2004007 as Uri and closed in IR 2006002 as NCV. | 2004 | Triennial
CAT | 2 | 2007-08-03 | NCV (Green ) | (PIM) Degraded Fire Barrier Penetration Seal | 2007007 | 2007 | Triennial
CAT | 2 | 2007-08-03 | NCV (Green ) | (PIM) ELU Replacement Batteries Not Tested After Installation | 2007007 | 2007 | Triennial
CAT | 2 | 2004-03-27 | NCV (Green ) | (PIM) Seal Not Installed in a Cable Conduit Penetrating a Fire Barrier | 2004003 | 2004 | Annual/Quarterly
CAT | 2 | 2005-03-31 | NCV (Green ) | (PIM) Insufficient Fire Drill Oversight to Ensure Fire Brigade Performance Deficiencies are Identified | 2005002 | 2005 | Annual/Quarterly
CAT | 2 | 2009-09-30 | NCV (Green ) | (PIM) Failure to perform required hourly fire watch patrols | 2009007 | 2009 | Annual/Quarterly
CLIN | 3 | 2004-09-30 | NCV (Green ) | (PIM) PORTABLE FIRE EXTINGUISHER MISSING FROM ITS DESIGNATED STORAGE. | 2004006 | 2004 | Annual/Quarterly
CLIN | 3 | 2005-03-31 | NCV (Green ) | (PIM) FAILURE TO ESTABLISH ADEQUATE COMPENSATORY ACTIONS (HOURLY FIRE WATCH) ACCORDING TO FIRE PROTECTION PROGRAM PROCEDURES. | 2005003 | 2005 | Annual/Quarterly
CLIN | 3 | 2007-12-31 | NCV (Green ) | (PIM) Failure to implement fire protection program in accordance with program requirements | 2007005 | 2007 | Annual/Quarterly
CLIN | 3 | 2008-03-31 | NCV (Green ) | (PIM) FAILURE TO FOLLOW APPROVED FIRE PROTECTION PROGRAM PROCEDURES CONCERNING CONTROL OF TRANSIENT COMBUSTIBLE MATERIAL. | 2008002 | 2008 | Annual/Quarterly
CLIN | 3 | 2008-12-31 | NCV (Green ) | (PIM) FAILURE TO CONTROL TRANSIENT COMBUSTIBLE MATERIALS IN ACCORDANCE WITH FIRE PROTECTION PROGRAM. | 2008005 | 2008 | Annual/Quarterly
CNS | 4 | 2001-04-06 | NCV (Green ) | Failure to provide 20 feet separation between redundant service water equipment. | 2001003 The ROP website did not have this finding; it was obtained by opening the triennial report. | 2001 | Triennial
CNS | 4 | 2001-04-07 | NCV (Green ) | Failure to provide adequate emergency lighting to perform operator actions for safe shutdown. | 2001003 The ROP website did not have this finding; it was obtained by opening the triennial report. | 2001 | Triennial
CNS | 4 | 2001-04-08 | NCV (Green ) | Failure to install detectors as documented in the safety evaluation report which was not in accordance with 10 CFR 50.48(b). | 2001003 The ROP website did not have this finding; it was obtained by opening the triennial report. | 2001 | Triennial
CNS | 4 | 2001-04-09 | NCV (Green ) | Failure to perform calculations to ensure that the locations and conditions of fire areas did not require as much water as is discharged by nominal 1/2-inch orifice sprinkler, as required by NFPA 13 Code requirements | 2001003 The ROP website did not have this finding; it was obtained by opening the triennial report. | 2001 | Triennial
CNS | 4 | 2004-07-02 | NCV (Green ) | (PIM) Failure to ensure redundant safe shutdown systems located in the same fire area are free of fire damage. | 2004008 | 2004 | Triennial
CNS | 4 | 2004-07-02 | NCV (Green ) | (PIM) Three examples of a NCV of Technical Specification 5.4.1.d for failure to provide adequate instructions in Emergency Procedure 5.4 Fire-S/D, "Fire Induced Shutdown From Outside Control. | 2004008 | 2004 | Triennial
CNS | 4 | 2008-03-18 | Violation (White ) | (PIM) Failure to ensure that some steps contained in emergency procedures would work as written | Open in TR 2007008 as URI, then became an AV in the follow-up inspection 2008007 and was declared a White Violation in IR 2008008 | 2007 | Triennial
CNS | 4 | 2000-04-01 | NCV (Green ) | (PIM) APPENDIX R LIGHTING INADEQUATE | 2000004 | 2000 | Annual/Quarterly
CNS | 4 | 2002-01-03 | NCV (Green ) | (PIM) Failure to follow procedure resulting in a fire | 2001007 | 2002 | Annual/Quarterly
CNS | 4 | 2002-10-05 | NCV (Green ) | (PIM) NCV of License Condition 2.C.(4) for failure to maintain operability of a fire suppression system. | 2002003 | 2002 | Annual/Quarterly
CNS | 4 | 2003-04-03 | NCV (Green ) | (PIM) Failure to implement the procedural requirements of Administrative Procedure 0.39 "Fire Watches," Revision 27, affected the mitigating systems cornerstone. | 2003004 | 2003 | Annual/Quarterly
CNS | 4 | 2004-12-31 | NCV (Green ) | (PIM) Failure to Implement the Station Fire Watch Procedure | 2004005 | 2004 | Annual/Quarterly
CNS | 4 | 2006-06-24 | NCV (Green ) | (PIM) Failures to Properly Control Combustibles in the Plant | 2006003 | 2006 | Annual/Quarterly
CNS | 4 | 2009-09-23 | NCV (Green ) | (PIM) Failure to Follow Scaffold Procedure Threatens Fire Protection Equipment | 2009004 | 2009 | Annual/Quarterly
COOK | 3 | 2003-04-11 | NCV (Green ) | (PIM) Failure to Ensure Alternative Shutdown Capability Could Accommodate Post-Fire Conditions Where Off-Site Power is Not Available | 2003005 | 2003 | Triennial
COOK | 3 | 2003-04-11 | NCV (Green ) | (PIM) Failure to Ensure Control Room Ventilation Would be Free of Fire Damage | 2003005 | 2003 | Triennial
COOK | 3 | 2003-04-11 | NCV (Green ) | (PIM) Failure to Provide Adequate Emergency Lighting | 2003005 | 2003 | Triennial
COOK | 3 | 2003-04-11 | NCV (Green ) | (PIM) Inadequate Carbon Dioxide Concentrations | 2003005 | 2003 | Triennial
COOK | 3 | 2001-12-29 | NCV (N/A ) | (PIM) Failure to Ensure That Breaker Coordination and Selective Tripping was Provided at the 4.16 kV System | This was a combined inspection were they looked the FP Safe Shutdown Analysis. Inspection repot 2001019 | 2001 | Annual/Quarterly
COOK | 3 | 2001-12-29 | NCV (N/A ) | (PIM) Failure to Ensure That Breaker Coordination and Selective Tripping was Provided at the 4.16 kV System | 2001019. Found in the triennial search. | 2001 | Annual/Quarterly
CP | 4 | 2002-02-08 | NCV (Green ) | (PIM) Failure to establish and maintain adequate procedures covering activities associated with fire protection program implementation | Open in TR 2002003 as URI and closed in an IR 2002006. | 2002 | Triennial
CP | 4 | 2006-06-23 | NCV (Green ) | (PIM) Operators Unable to Meet Some Critical Action Times During Alternate Shutdown Walkthrough | Open in TR 2005008 as URI and closed as NCV in IR 2006003. | 2005 | Triennial
CP | 4 | 2009-09-19 | NCV (Green ) | (PIM) Inadequate Postfire Safe Shutdown Procedure | Open in TR 2008006 as URI and closed as NCV in IR 2009004. | 2008 | Triennial
CP | 4 | 2009-09-19 | NCV (Green ) | (PIM) Failure to Assure That One Train of Equipment is Free From Fire Damage | Open in TR 2008006 and closed as NCV in IR 2009004. This NCV came from the analysis of the URI "Unapproved Local Manual Actions for Hot Shutdown". | 2008 | Triennial
CP | 4 | 2009-09-19 | NCV (Green ) | (PIM) Inadequate Alternative Shutdown Procedure | Open in TR 2008006 and closed as NCV in IR 2009004. | 2008 | Triennial
CP | 4 | 2008-05-22 | NCV (Green ) | (PIM) Inadequate Fire Suppression Systems | 2008006 | 2008 | Triennial
CP | 4 | 2008-05-22 | NCV (Green ) | (PIM) Inadequate Post-Fire Safe Shutdown Procedures | 2008006 | 2008 | Triennial
CP | 4 | 2008-06-22 | NCV (Green ) | (PIM) Inadequate Fire Protection Compensatory Actions During Refueling Outage. | 2008003. Found in the triennial search. | 2008 | Annual/Quarterly
CP | 4 | 2008-06-22 | NCV (Green ) | (PIM) Failure to Expeditiously Restore Fire Hose Stations in Containment to Service | 2008003. Found in the triennial search. | 2008 | Annual/Quarterly
CP | 4 | 2008-09-21 | NCV (Green ) | (PIM) "Failure to Ensure Roll-up Fire Doors Complied With Fire Code" | 2008004. Found in the triennial search. | 2008 | Annual/Quarterly
CP | 4 | 2008-09-21 | NCV (Green ) | (PIM) "Failure to Control Transient Combustibles" | 2008004 | 2008 | Annual/Quarterly
CP | 4 | 2009-09-19 | NCV (Green ) | (PIM) Failure to Seal Electrical Enclosure | 2009004 | 2009 | Annual/Quarterly
CR | 2 | 2002-07-12 | NCV (Green) | (Non-PIM) Failure to Protect One Train of Safe Shutdown Equipment From Fire Damage in Accordance with Appendix R, Section III.G.2 (Three Examples). | Open in 2002005 (Triennial) and closed in an Integrated report 2003005. It was consider a Green Non-cited violation under 2003005. It was declared as a Quarterly Inspection finding. | 2002 | Triennial
CR | 2 | 2005-09-07 | Violation (White ) | (PIM) Unprotected Post-Fire Safe Shutdown Cables and Related Non-feasible Local Manual Operator Action | Open in TR 2004009 as URI, then became an AV in IR 2005007 and was declared a White Violation in IR 2005011. | 2004 | Triennial
CR | 2 | 2000-12-30 | NCV (Green ) | (PIM) Failure to Implement Fire Protection Plan Requirements When Two Cable Spreading Room Fire Dampers Were Not Operable. | 2000004 | 2000 | Annual/Quarterly
CR | 2 | 2001-03-31 | NCV (Green ) | (PIM) Failure to Implement Fire Protection Requirements for Inoperable Fire Damper. | 2000005 | 2001 | Annual/Quarterly
DAVI | 3 | 2004-09-17 | NCV (SL-IV ) | (PIM) Incomplete Information Provided to NRC in Licensing Submittal | 2004009 | 2004 | Triennial
DAVI | 3 | 2005-06-30 | NCV (Green ) | (PIM) INOPERABILITY OF EMERGENCY BATTERY PACKS AND ASSOCIATED LIGHTING CREDITED WITH LICENSEE COMPLIANCE TO 10 CFR 50, APPENDIX R, SECTION III.J | 2005007 | 2005 | Annual/Quarterly
DAVI | 3 | 2006-06-30 | NCV (Green ) | (PIM) FIRE PROTECTION, TRANSIENT COMBUSTIBLES ON THE DRY FUEL STORAGE PAD | 2006003 | 2006 | Annual/Quarterly
DIAB | 4 | 2000-04-07 | Finding (Green ) | (PIM) Degraded 1-hour fire-rated ceiling in Fire Area 4A and degraded 2-hour fire-rated barrier between Fire Areas 4A and 4B. | 2000003 | 2000 | Triennial
DIAB | 4 | 2003-03-18 | NCV (Green ) | (PIM) Two examples of a violation of Technical Specification 5.4.1.d for inadequate fire protection implementation procedure | 2003002 | 2003 | Triennial
DIAB | 4 | 2009-07-24 | NCV (Green ) | (PIM) Safe Shutdown Procedure Not Consistent with Safe Shutdown Analysis | 2009008 | 2009 | Triennial
DIAB | 4 | 2003-09-27 | NCV (Green ) | (PIM) Two Examples of a Violation of Technical Specification 5.4.1.d for Inadequate Fire Protection Implementation | 2003007 | 2003 | Annual/Quarterly
DIAB | 4 | 2003-12-31 | NCV (TBD ) | (PIM) Failure to Adequately Train Operations Responders in Support of the Fire Brigade | 2003008 | 2003 | Annual/Quarterly
DIAB | 4 | 2005-03-31 | NCV (Green ) | (PIM) Failure to correct fire program violation concerning qualifications of Operations Responders in support of the fire brigade | 2005002 | 2005 | Annual/Quarterly
DIAB | 4 | 2006-08-23 | NCV (Green ) | (PIM) Failure to Promptly Identify that the Correct Equipment Necessary for Implementing EOP for Inadequate Core Cooling Was Not Pre-staged | 2006004 | 2006 | Annual/Quarterly
DIAB | 4 | 2008-02-17 | NCV (Green ) | (PIM) Failure to Maintain the Integrity of an Auxiliary Building Fire Door | 2008002 | 2008 | Annual/Quarterly
DIAB | 4 | 2008-09-30 | NCV (Green ) | (PIM) Failure to Perform a Safety Assessment for Following Discovery of Explosive Gas in the Auxiliary and Containment Buildings | 2008004 | 2008 | Annual/Quarterly
DIAB | 4 | 2009-09-25 | NCV (Green ) | (PIM) Failure to Identify and Correct a Degraded Fire Barrier | 2009004 | 2009 | Annual/Quarterly
DRES | 3 | 2002-05-10 | NCV (Green ) | (PIM) Reactor Water Level Could Drop Below Top of Active Fuel in the Event of Fire | 2002006 | 2002 | Triennial
DRES | 3 | 2007-12-18 | NCV (Green ) | Failure to Perform a 10 CFR 50.59 Evaluation for Exceeding Continuous Rating on the EDG. | Open in TR 2002006, discussed in 2005009 and closed in 2008007. The URI became two NCV in 2008007. This finding did not appear in the Dynamic website search. | 2002 | Triennial
DRES | 3 | 2007-12-18 | NCV (Green ) | Failure to Meet the EDG Power Factor Testing Requirements | Open in TR 2002006, discussed in 2005009 and closed in 2008007. The URI became two NCV in 2008007. This finding did not appear in the Dynamic website search. | 2002 | Triennial
DRES | 3 | 2005-04-01 | NCV (Green ) | (PIM) Safe Shutdown Procedure Failed to Specify Correct Number of Turns for Opening Valve | 2005002 | 2005 | Triennial
DRES | 3 | 2008-02-15 | NCV (Green ) | (PIM) Failure to Perform Periodic Trip Tests on Thermal Overload Heaters. | 2008006 | 2008 | Triennial
DRES | 3 | 2001-01-04 | NCV (Green ) | (PIM) Failure of the fire marshall to properly evaluate fire drill | 2000021 | 2001 | Annual/Quarterly
DRES | 3 | 2001-11-13 | NCV (N/A ) | (PIM) Failure to have a fire extinguisher readily available, as required by station procedures, while performing hot work activities | 2001019 | 2001 | Annual/Quarterly
DRES | 3 | 2002-09-30 | NCV (Green ) | (PIM) The licensee failed to follow the procedure for ensuring timely fire watch response. | 2002012 | 2002 | Annual/Quarterly
DRES | 3 | 2003-09-30 | NCV (Green ) | (PIM) Failure to Meet Technical Specification 5.4.1, Fire Protection Program Implementation for Hot Work Activities | 2003007 | 2003 | Annual/Quarterly
DRES | 3 | 2006-06-29 | NCV (Green ) | (PIM) Failure to Identify an Inoperable 3-hour Fire Barrier Wall in the Unit 2 EDG Day Tank Room | 2006007 | 2006 | Annual/Quarterly
DRES | 3 | 2006-12-31 | NCV (Green ) | (PIM) Licensee’s Failure to Develop a Pre-fire Plan for Fire Zone 8.2.6.A, Elevation 534' | 2006011 | 2006 | Annual/Quarterly
DRES | 3 | 2007-06-12 | NCV (Green ) | (PIM) Failure to Restore Fire Brigade Equipment to a Ready Status in a Timely Manner after the Performance of a Fire Drill | 2007003 | 2007 | Annual/Quarterly
DRES | 3 | 2008-06-30 | NCV (Green ) | (PIM) Fire Doors Failed Their Periodic Functional Test | 2008003 | 2008 | Annual/Quarterly
DRES | 3 | 2009-03-31 | NCV (Green ) | (PIM) Failure to Develop a Pre Fire Plan for Fire Zone 18.6 | 2009002 | 2009 | Annual/Quarterly
DUAN | 3 | 2003-03-07 | NCV (Green ) | (PIM) Lack of Demonstrated Reactor Water Level Instrumentation | 2003002 | 2003 | Triennial
DUAN | 3 | 2003-02-14 | NCV (Green ) | (PIM) Inadequate Circuit Breaker Coordination for Instrument Power Supply | 2003002 | 2003 | Triennial
DUAN | 3 | 2003-02-14 | NCV (Green ) | (PIM) Inadequate Corrective Action for Potential for Smoke to Enter Control Room | 2003002 | 2003 | Triennial
DUAN | 3 | 2009-10-06 | NonCited Violation (Green ) | (PIM) Failure to Identify and Address an Adverse Trend in Performing Required Fire Watches | 2009006 | 2009 | Triennial
DUAN | 3 | 2000-07-10 | Finding (Green ) | (PIM) DURING A WALKDOWN OF THE REACTOR BUILDING, THE INSPECTORS IDENTIFIED THAT SEVERAL PORTABLE FIRE EXTINGUISHERS WERE MISSING FROM THEIR ASSIGNED LOCATION. | 2000003 | 2000 | Annual/Quarterly
DUAN | 3 | 2005-09-30 | NCV (Green ) | (PIM) FAILURE TO MEET TRAVEL DISTANCE REQUIREMENTS FOR FIRE EXTINGUISHERS IN THE REACTOR BUILDING. | 2005004 | 2005 | Annual/Quarterly
DUAN | 3 | 2005-12-31 | NCV (Green ) | (PIM) FAILURE TO IDENTIFY AND CONTROL TRANSIENT COMBUSTIBLES IN THE SOUTHEAST CORNER ROOM OF THE REACTOR BUILDING. | 2005005 | 2005 | Annual/Quarterly
FAR | 2 | 2002-09-13 | NCV (Green ) | (PIM) Failure to Obtain NRC Approval Prior to Implementing Changes to the Approved Fire Protection Program | 2002006 | 2002 | Triennial
FAR | 2 | 2002-09-13 | NCV (Green ) | (PIM) Failure to Revise Procedure AOP-29.0 Promptly | 2002006 | 2002 | Triennial
FAR | 2 | 2002-09-13 | NCV (Green ) | (PIM) Failure to Maintain and Implement Fire Protection Program Transformer Fluid Confinement Features Required by the Listing Agency | 2002006 | 2002 | Triennial
FAR | 2 | 2008-04-04 | NonCited Violation (Green ) | (PIM) Fire Procedure Credits Unreliable Indication | Open in TR 2005006 as URI and closed in TR 2008006 as NCV. | 2005 | Triennial
FAR | 2 | 2005-05-23 | NCV (Green ) | (PIM) Unapproved Local Manual Operator Actions for Post-Fire Safe Shutdown | 2005006 | 2005 | Triennial
FAR | 2 | 2006-12-31 | NCV (Green ) | (Non-PIM) Fire Procedure Failed to Ensure that AC Power Would Be Available | Open in TR 2005007 and closed in IR 2006005. This finding did not appear in any search from the Dynamic Website. It was taken from the report. | 2005 | Triennial
FAR | 2 | 2008-04-04 | NCV (Green ) | (PIM) Areas Where OMAs Are Performed Did Not Have ELUs Installed | 2008006 | 2008 | Triennial
FAR | 2 | 2008-04-04 | NCV (Green ) | (PIM) ELU Test Failures Were Not Documented In CRs As Required By Procedure | 2008006 | 2008 | Triennial
FCS | 4 | 2000-03-10 | NCV (Green ) | (PIM) Failure to Ensure One Train of Systems Required for Safe Shutdown is Free of Fire Damage | Open in TR 2000001 as an Apparent Violation and it was closed as NCV in the TR 2005008. | 2000 | Triennial
FCS | 4 | 2000-03-11 | NCV (Green ) | Failure to maintain in effect all provisions of the NRC-approved fire protection program in Fire Area 32 | 2000001. This NCV was taken from the inspection report and not from the website. | 2000 | Triennial
FCS | 4 | 2003-01-17 | NCV (Green ) | (PIM) Failure to Assure that at Least One Train of Charging Pumps Was Free of Fire Damage | 2003002 | 2003 | Triennial
FCS | 4 | 2006-09-30 | NCV (Green ) | (PIM) Failure to Implement reasonable and Feasible Manual Actions | Open in TR 2005008 and closed in an IR 2006004. This URI became a NCV in that report. | 2005 | Triennial
FCS | 4 | 2006-09-30 | NCV (Green ) | (PIM) Inadequate Alternate Shutdown Procedure | Open in TR 2005008 and closed in an IR 2006004. This URI became a NCV in that report. | 2005 | Triennial
FCS | 4 | 2005-11-10 | NCV (Green ) | (PIM) Failure to Take Prompt Corrective Action for Fire Protection Program Deficiencies | 2005008 | 2005 | Triennial
FCS | 4 | 2008-08-15 | NCV (Green ) | (PIM) Untimely Corrective Actions for Degraded Fire Protection Water Supply System | 2008009 | 2008 | Triennial
FCS | 4 | 2008-08-15 | NCV (Green ) | (PIM) Inadequate Corrective Actions Related to Revising a Post-fire Safe Shutdown Procedure | 2008009 | 2008 | Triennial
FCS | 4 | 2004-06-30 | NCV (Green ) | (PIM) Failing to Ensure that Fire Barriers Protecting Safety-Related Areas Were Functional | 2004003 | 2004 | Annual/Quarterly
FCS | 4 | 2004-06-30 | NCV (Green ) | (PIM) Failure to Provide Fire Protection Features for Components Important to Achieve and Maintain Cold Shutdown | 2004003 | 2004 | Annual/Quarterly
FCS | 4 | 2004-06-30 | NCV (Green ) | (PIM) Failure to Provide Compensatory Measures When Blocking a Fire Hose Station | 2004003 | 2004 | Annual/Quarterly
FCS | 4 | 2005-03-31 | NCV (Green ) | (PIM) Failure to Control Transient Combustible Materials that Exceeded the Fire Load limit for an Area | 2005002 | 2005 | Annual/Quarterly
FCS | 4 | 2005-03-31 | NCV (Green ) | (PIM) Failure to ensure that fire barriers protecting safety-related areas were functional | 2005002 | 2005 | Annual/Quarterly
FCS | 4 | 2006-06-30 | NCV (Green ) | (PIM) Nonfunctional Fire Barrier Separating Corridor 23 (Fire Area 20.1) and Room 61 (Fire Area 20.4) | 2006003 | 2006 | Annual/Quarterly
FERM | 3 | 2002-12-06 | NCV (Green ) | (PIM) Failure to Have Adequate Procedures for Alternative Shutdown in Effect | 2002008 | 2002 | Triennial
FERM | 3 | 2002-12-06 | NCV (Green ) | (PIM) Failure to Take Prompt Corrective Actions to Correct Identified Deficiencies in Alternative Shutdown Procedure | 2002008 | 2002 | Triennial
FERM | 3 | 2006-09-30 | NCV (Green ) | (PIM) Temperatures in Dedicated Shutdown Panel Area - Balance of Plant Switchgear Room | Open in TR 2005006 and closed as NCV in IR 2006004 | 2005 | Triennial
FERM | 3 | 2005-07-15 | NCV (Green ) | (PIM) Failure to Have Separation Between Redundant Safe Shutdown Cables (Section 1R05.2) | 2005006 | 2005 | Triennial
FERM | 3 | 2005-07-15 | NCV (Green ) | (PIM) Failure to Ensure that Adequate Electrical Coordination Existed in Post -Fire Alternate Shutdown Circuits (Section 1R05.3) | 2005006 | 2005 | Triennial
FERM | 3 | 2005-07-15 | NCV (Green ) | (PIM) Failure to Install Smoke Detectors in Accordance with NFPA 72-E (Section 1R05.10) | 2005006 | 2005 | Triennial
FERM | 3 | 2005-07-15 | NCV (Green ) | (PIM) Failure to Implement Adequate Corrective Actions in a Timely Manner (Section 4OA2) | 2005006 | 2005 | Triennial
FERM | 3 | 2008-05-08 | NCV (Green ) | (PIM) Failure to Ensure Air Supply Tubing for Safe Shutdown Valves Free of Fire Damage | 2008006 | 2008 | Triennial
FERM | 3 | 2008-05-08 | NCV (Green ) | (PIM) High Pressure Coolant Injection Room Sprinkler System Failed to Protect Against Hazard | 2008006 | 2008 | Triennial
FERM | 3 | 2008-05-08 | NCV (Green ) | (PIM) Reactor Core Isolation Cooling Room Sprinkler System Improperly Installed | 2008006 | 2008 | Triennial
FERM | 3 | 2008-05-08 | NCV (Green ) | (PIM) Lack of Basis for Diesel Fire Pump Temperature De-Rating | 2008006 | 2008 | Triennial
FERM | 3 | 2008-05-08 | NCV (Green ) | (PIM) Alternate Shutdown Procedure Failed to Identify Time-Critical Steps | 2008006 | 2008 | Triennial
FERM | 3 | 2006-06-30 | NCV (Green ) | (PIM) Improper Storage of Chemicals Affecting Fire Fighting Response | 2006003 | 2006 | Annual/Quarterly
FERM | 3 | 2006-06-30 | NCV (Green ) | (PIM) Unauthorized Transient Combustibles in Safety-Related Areas | 2006003 | 2006 | Annual/Quarterly
FERM | 3 | 2007-06-30 | Finding (Green ) | (PIM) Failure to Control Transient Combustibles | 2007004 | 2007 | Annual/Quarterly
FERM | 3 | 2008-09-30 | NCV (Green ) | (PIM) Failure to Install Smoke Detectors in the Reactor Building, First Floor, Beam Pockets. | 2008004 | 2008 | Annual/Quarterly
FITZ | 1 | 2008-05-16 | NCV (Green ) | (PIM) Inadequate Procedure Guidance to Address Spurious Failures of the RCIC and LPCI Systems | 2008006 | 2008 | Triennial
FITZ | 1 | 2004-09-30 | NCV (Green ) | (PIM) Transient Combustible Control Requirements for the Screenwell Not Met | 2004004 | 2004 | Annual/Quarterly
GG | 4 | 2002-09-17 | NCV (Green ) | (PIM) Inadequate alternative shutdown procedure | 2002007 | 2002 | Triennial
GG | 4 | 2002-09-18 | NCV (Green ) | Failure to protect radio repeaters | 2002007. Check because this finding is included in the annual findings. I found this finding in the triennial report not in the website. | 2002 | Triennial
GG | 4 | 2006-04-11 | NCV (Green ) | (PIM) Inadequate Alternative Shutdown Procedure for Locally Starting and Loading an EDG | Open in TR 2005008 as URI and closed in IR 2006002 as NCV. | 2005 | Triennial
GG | 4 | 2005-05-12 | Finding (Green ) | (PIM) Inadequate Fire Drill Critique | 2005008 | 2005 | Triennial
GG | 4 | 2005-05-12 | Finding (Green ) | (PIM) No Procedures for Implementing Two Repairs Needed to Achieve Cold Shutdown Following A CR Fire | 2005008 | 2005 | Triennial
GG | 4 | 2005-05-12 | NCV (Green ) | (PIM) Alternative Shutdown Procedure Did Not Implement Safe Shutdown Analysis Assumption to Isolate Containment in a Timely Manner | 2005008 | 2005 | Triennial
GG | 4 | 2008-04-18 | NCV (Green ) | (PIM) Failure to Evaluate Fire Wrap Testing Discrepancies | 2008006 | 2008 | Triennial
GG | 4 | 2008-04-18 | NCV (Green ) | (PIM) Fire Brigade Members Assigned Responsibilities That Conflicted with Fire Brigade Responsibilities. | 2008006 | 2008 | Triennial
GG | 4 | 2008-04-18 | NCV (Green ) | (PIM) Plant Modification Blocked Access for Manual Firefighting. | 2008006 | 2008 | Triennial
GG | 4 | 2008-04-18 | NCV (Green ) | (PIM) Failure to Ensure That Potential Damage to Motor-Operated Valve Circuits Would Not Prevent Safe Shutdown. | 2008006 | 2008 | Triennial
GG | 4 | 2000-06-29 | Finding (Green ) | (PIM) Increased Risk of Loss of Instrument Air System Due to Fire | 2000006 | 2000 | Annual/Quarterly
GG | 4 | 2006-09-30 | NCV (Green ) | (PIM) Failure to Control Loose Items in Safety Related Areas | 2006004 | 2006 | Annual/Quarterly
GG | 4 | 2008-03-22 | NCV (Green ) | (PIM) Failure to Implement an Adequate Compensatory Fire Watch per Station Fire Protection Procedures. | 2008002 | 2008 | Annual/Quarterly
GG | 4 | 2008-06-21 | NCV (Green ) | (PIM) Inadequate Fireproofing on Fire Barrier Protecting the Safeguards Switchgear Room | 2008003 | 2008 | Annual/Quarterly
GG | 4 | 2008-12-31 | Finding (Green ) | (PIM) Inadequate Fire Drill Critique | 2008005 | 2008 | Annual/Quarterly
GINN | 1 | 2000-11-17 | NCV (Green ) | (PIM) Failure to ensure that the alternate shutdown capability for the screen house was electrically and physically independent of the area. | 2000009 | 2000 | Triennial
GINN | 1 | 2004-09-30 | NCV (Green ) | (PIM) Non-Rated Cable Tunnel Hatch | Open in TR 2003013 as URI and closed in IR 2004004 as a NCV. | 2003 | Triennial
GINN | 1 | 2006-06-23 | NCV (Green ) | (PIM) Missed Fire Brigade Training | 2006007 | 2006 | Triennial
GINN | 1 | 2000-12-30 | NCV (Green ) | (PIM) Failure to adequately establish a continuous fire watch. | 2000010 | 2000 | Annual/Quarterly
GINN | 1 | 2002-05-18 | NCV (Green ) | (PIM) Failure to formally control and evaluate a compensatory fire protection measure installed to provide a temporary water supply to the containment fire hose reels. | 2002003 | 2002 | Annual/Quarterly
GINN | 1 | 2002-09-28 | NCV (Green ) | (PIM) A natural gas supply isolation valve to the screen house had been covered by several inches of gravel and asphalt pavement and could not be operated during a fire. | 2002005 | 2002 | Annual/Quarterly
GINN | 1 | 2002-12-28 | Finding (Green ) | (PIM) Failure to implement all aspects of the fire attack strategy | 2002006 | 2002 | Annual/Quarterly
GINN | 1 | 2003-03-29 | NCV (Green ) | (PIM) Intermittent control room roof leakage not identified and repaired | 2003003 | 2003 | Annual/Quarterly
GINN | 1 | 2005-12-31 | NCV (Green ) | (PIM) Failure to Maintain Fire Protection Procedures as Required by Technical Specification 5.4.1 | 2005005 | 2005 | Annual/Quarterly
GINN | 1 | 2006-03-31 | NCV (Green ) | (PIM) INADEQUATE CONTROL OF TRANSIENT COMBUSTIBLE MATERIAL | 2006002 | 2006 | Annual/Quarterly
HAR | 2 | 2003-10-31 | NCV (Green ) | (PIM) INADEQUATE IMPLEMENTATION OF THE FIRE PROTECTION PROGRAM FOR SAFE SHUTDOWN | This NCV was declared in an in-office review of the significance of the triennial fire protection inspection findings of TR 2002011. The inspection report number is 2003007. | 2002 | Triennial
HAR | 2 | 2003-10-31 | NCV (Green ) | (PIM) INADEQUATE CORRECTIVE ACTION FOR A PREVIOUS WHITE FIRE PROTECTION FINDING | This NCV was declared in an in-office review of the significance of the triennial fire protection inspection findings of TR 2002011. The inspection report number is 2003007. | 2002 | Triennial
HAR | 2 | 2008-11-07 | NCV (Green ) | (PIM) Sprinkler System in Cable Spreading Room A Does Not Meet Licensee’s Fire Protection Program Requirements | 2008008 | 2008 | Triennial
HAR | 2 | 2002-09-06 | Violation (White ) | (Non-PIM) FAILURE TO IMPLEMENT AND MAINTAIN NRC APPROVED FIRE PROTECTION PROGRAM SAFE SHUTDOWN SYSTEM SEPARATION REQUIREMENTS | Open in TR 1999013 as URI, then became an AV in open item IR 2000009 and was declared a White Violation in supplemental report 2002008. The violation was officially closed in the report 2003007. | 1999 | Triennial
HAR | 2 | 2000-04-01 | NCV (Green ) | (PIM) Fire protection wrap/penetration seal interface problems | This NCV was found in the integrated report 2000001. This NCV should be a finding under quarterly procedure. | 2000 | Annual/Quarterly
HAR | 2 | 2001-09-29 | NCV (Green ) | (PIM) INADEQUATE FUSE COORDINATION FOR PORV BLOCK VALVES | 2001004 | 2001 | Annual/Quarterly
HAR | 2 | 2001-12-29 | NCV (Green ) | (PIM) TWO EXAMPLES OF FAILURE TO IMPLEMENT THE FIRE PROTECTION PROGRAM IN B CABLE SPREADING ROOM TUNNEL | 2001005 | 2001 | Annual/Quarterly
HAR | 2 | 2003-04-05 | NCV (Green ) | (PIM) INADEQUATE ROVING CONTINUOUS FIRE WATCHES | 2003002 | 2003 | Annual/Quarterly
HAT | 2 | 2005-06-30 | NCV (Green ) | (PIM) Untimely and Unapproved Manual Operators Actions for Post-Fire SSD | Open in TR 2003006 as URI and closed in IR 2005003 as NCV. | 2003 | Triennial
HAT | 2 | 2003-07-25 | NCV (Green ) | (Non-PIM) Inadequate Procedure for Local Manual Operator Action for Post-Fire Safe Shutdown Equipment | 2003006 | 2003 | Triennial
HAT | 2 | 2003-07-25 | NCV (Green ) | (PIM) Unapproved Manual Operator Actions for Post-Fire Safe Shutdown | 2003006 | 2003 | Triennial
HAT | 2 | 2003-07-25 | NCV (Green ) | (PIM) Inadequate Emergency Lighting for Operation of Post-Fire SSD Equipment | 2003006 | 2003 | Triennial
HAT | 2 | 2001-06-30 | NCV (Green ) | (PIM) Inadequate Separation of Residual Heat Removal Service Water (RHRSW) Cables. | 2001003 | 2001 | Annual/Quarterly
HOPE | 1 | 2001-01-26 | Finding (Green ) | (PIM) SHUTDOWN OUTSIDE CONTROL ROOM PROCEDURE COULD NOT BE PERFORMED AS WRITTEN | 2001002 | 2001 | Triennial
HOPE | 1 | 2001-03-31 | NCV (Green ) | (PIM) FAILURE TO PROVIDE A THREE-HOUR RATED FIRE BARRIER TO ENSURE APPENDIX R SEPARATION BETWEEN TWO SHUTDOWN TRAINS. | 2001004 | 2001 | Annual/Quarterly
HOPE | 1 | 2001-12-29 | NCV (Green ) | (PIM) PSEG NUCLEAR DID NOT IDENTIFY AND ADMINISTRATIVELY CONTROL TRANSIENT COMBUSTIBLES MATERIALS IN THE HPCI PUMP AND TURBINE ROOM | 2001011 | 2001 | Annual/Quarterly
HOPE | 1 | 2001-12-29 | NCV (Green ) | (PIM) PSEG NUCLEAR DID NOT PROPERLY IMPLEMENT FIRE PROTECTION PROGRAM REQUIREMENTS FOR AN INOPERABLE FIRE DOOR | 2001011 | 2001 | Annual/Quarterly
HOPE | 1 | 2002-09-30 | NCV (Green ) | (PIM) PSEG NUCLEAR DID NOT IDENTIFY AND ADMINISTRATIVELY CONTROL TRANSIENT COMBUSTIBLES MATERIALS IN THE HPCI PUMP AND TURBINE ROOM | 2002006 | 2002 | Annual/Quarterly
HOPE | 1 | 2004-03-30 | NCV (Green ) | (PIM) IMPROPER CONTROL OF TRANSIENT COMBUSTIBLES IN CORE SPRAY ROOM | 2004002 | 2004 | Annual/Quarterly
HOPE | 1 | 2004-09-30 | NCV (Green ) | (PIM) INADEQUATE CONTROL OF TRANSIENT COMBUSTIBLE MATERIAL | 2004004 | 2004 | Annual/Quarterly
INP3 | 1 | 2002-02-21 | NCV (Green ) | (PIM) INADEQUATE PROCEDURE FOR TRANSITION TO COLD SHUTDOWN DURING SHUTDOWN FROM OUTSIDE THE CONTROL ROOM | 2001012 | 2002 | Triennial
INP3 | 1 | 2008-02-08 | NCV (Green ) | (PIM) Inadequate Procedure Guidance to Diagnose and Align RCP Seal Cooling | 2008007 | 2008 | Triennial
INP3 | 1 | 2008-02-08 | NCV (Green ) | (PIM) Inadequate Procedure Guidance to Isolate Steam Generator Blow down Flow | 2008007 | 2008 | Triennial
INP3 | 1 | 2008-02-08 | NCV (Green ) | (PIM) Inadequate Procedure Directions to De-energize PORV and Letdown Valve Circuits | 2008007 | 2008 | Triennial
INP3 | 1 | 2004-03-31 | NCV (Green ) | (PIM) INADEQUATE IMPLEMENTATION OF FIRE PROTECTION PROCEDURES | 2004002 | 2004 | Annual/Quarterly
INPT | 1 | 2001-04-13 | NCV (Green ) | (PIM) Failure to have adequate length of fire hose staged for manual fire fighting in the central control room | 2000004 | 2001 | Triennial
INPT | 1 | 2001-04-13 | NCV (Green ) | (PIM) Failure to provide adequate isolation of circuits from the central control room | 2000004 | 2001 | Triennial
INPT | 1 | 2000-09-30 | NCV (Green ) | (PIM) A minor fire inside containment occurred due to a failure to properly evaluate and control transient combustibles during a grinding evolution | 2000011 | 2000 | Annual/Quarterly
INPT | 1 | 2000-09-30 | NCV (Green ) | (PIM) Inadequate fire fighting strategy instruction existed to align fire suppression water to containment | 2000011 | 2000 | Annual/Quarterly
INPT | 1 | 2000-09-30 | NCV (Green ) | (PIM) During implementation of a plant modification, workers failed to perform a work area walkdown, pre-job brief, and review of removal drawings | 2000011 | 2000 | Annual/Quarterly
INPT | 1 | 2001-07-07 | NCV (N/A ) | (PIM) FIRE PROTECTION DESIGN BASIS COMBUSTIBLE LOADING | 2001006 | 2001 | Annual/Quarterly
INPT | 1 | 2004-03-31 | NCV (Green ) | (PIM) NON-CITED VIOLATION OF TS 5.4.1.d FOR THE FAILURE TO PERFORM A TRANSIENT COMBUSTIBLE EVALUATION FOR 330 GALLONS OF OIL TEMPORARILY STORED IN FIRE ZONE 6A | 2004002 | 2004 | Annual/Quarterly
INPT | 1 | 2004-07-20 | NCV (Green ) | (PIM) Failure to implement appropriate design controls for electrical cable and raceway installations. | 2004009 | 2004 | Annual/Quarterly
INPT | 1 | 2005-04-02 | NCV (Green ) | (PIM) FAILURE TO IMPLEMENT ADEQUATE INTERIM COMPENSATORY MEASURES FOR FIRE BARRIER IMPAIRMENTS | 2005002 | 2005 | Annual/Quarterly
INPT | 1 | 2006-01-29 | NCV (Green ) | (PIM) DEGRADED RESIDUAL HEAT REMOVAL PUMP FIRE DOOR | 2006002 | 2006 | Annual/Quarterly
INPT | 1 | 2006-06-30 | NCV (Green ) | (PIM) FAILURE TO IDENTIFY DEGRADED RESIDUAL HEAT REMOVAL PUMP CELL FIRE DOOR | 2006003 | 2006 | Annual/Quarterly
INPT | 1 | 2007-10-03 | NCV (Green ) | (PIM) Degraded 12 Fire Main Booster Pump Cell Fire Door | 2007004 | 2007 | Annual/Quarterly
INPT | 1 | 2007-12-31 | NCV (Green ) | (PIM) FAILURE TO IDENTIFY DEGRADED FIRE BARRIER IN EDG BUILDING | 2007005 | 2007 | Annual/Quarterly
INPT | 1 | 2009-03-31 | NCV (Green ) | (PIM) Failure to Identify Damaged Components in EDG Ventilation Motor Control Center #2 | 2009002 | 2009 | Annual/Quarterly
INPT | 1 | 2009-03-31 | NCV (Green ) | (PIM) Failure to Identify and Promptly Correct Degraded 480 Volt Switchgear Room Fire Door | 2009002 | 2009 | Annual/Quarterly
KEWA | 3 | 2002-10-02 | NCV (Green ) | Inappropriate Placement of Diesel Generator Room Heat Detectors | Open in TR 2001002 as URI and closed in this follow-up fire protection inspection 2002006. This NCV should be a triennial finding because they are closing an URI but it did not appeared in the Dynamic Website at all. | 2001 | Triennial
KEWA | 3 | 2001-08-09 | NCV (Green ) | (PIM) NON-RATED FIRE BARRIER | Open in TR 2001002 as an Apparent Violation and closed in IR 2001011 as NCV. | 2001 | Triennial
KEWA | 3 | 2001-03-12 | NCV (Green ) | (PIM) INADEQUATE SMOKE DETECTOR COVERAGE IN FIRE ZONE TU-95B. | 2001002 | 2001 | Triennial
KEWA | 3 | 2006-12-14 | NCV (Green ) | (PIM) Failure to Provide Suppression for Safe Shutdown Equipment in Appendix R, III.G.3 Area | Open in TR 2004005 as URI and closed in the inspection report 2006016 as NCV. | 2004 | Triennial
KEWA | 3 | 2004-07-30 | NCV (Green ) | (PIM) Failure to Meet the Fire Protection Program Requirements for Hose Lengths to Maintain an Acceptable Water Pressure and Flow at Hose Stations | 2004005 | 2004 | Triennial
KEWA | 3 | 2004-07-31 | NCV (Green ) | Failure to Maintain Acceptable (Quality Related) Pre-Fire Strategies | 2004005 This NCV was taken from the triennial inspection report. This NCV appeared in the quarterly/annual findings search when it is suppose to be a triennial finding. | 2004 | Triennial
KEWA | 3 | 2004-07-30 | NCV (Green ) | (PIM) Failure to Meet the NFPA Code Requirements for Extinguisher Placement | 2004005 | 2004 | Triennial
KEWA | 3 | 2004-07-30 | NCV (Green ) | (PIM) Transient Combustibles Not Adequately Controlled Within Fire Area AX-32 | 2004005 | 2004 | Triennial
KEWA | 3 | 2004-07-30 | NCV (Green ) | (PIM) Transient Combustibles Not Adequately Controlled Within Fire Area AX-24 | 2004005 | 2004 | Triennial
KEWA | 3 | 2004-07-30 | NCV (Green ) | (PIM) Failure to Repair the Deluge System Heat Detectors in a Timely Manner | 2004005 | 2004 | Triennial
KEWA | 3 | 2008-09-11 | Finding (N/A ) | (Non-PIM) Failure to Provide Fire Detection and Fixed Fire Suppression in an Appendix R III.G.3 Area | 2008008 | 2008 | Triennial
KEWA | 3 | 2008-09-11 | Finding (N/A ) | (Non-PIM) Post-fire Shutdown Procedures Failed to Ensure Time-Critical Operator Actions were Performed in an Expeditious Manner | 2008008 | 2008 | Triennial
KEWA | 3 | 2008-09-11 | Finding (N/A ) | (Non-PIM) Failure to Protect Pressurize PORV Control Cable for a Fire Scenario | 2008008 | 2008 | Triennial
KEWA | 3 | 2000-05-22 | Finding (Green ) | (PIM) FIRE EXTINGUISHERS NOT LOCATED IN ALL AREAS OF CONTAINMENT BUILDING AT BEGINNING OF REFUELING OUTAGE. | 2000007 | 2000 | Annual/Quarterly
KEWA | 3 | 2001-02-13 | NCV (Green ) | (PIM) Failure to Test Fire Door in Accordance with Fire Plan | Inspection report 2001004 This NCV should be in the annual/quarterly finding. | 2001 | Annual/Quarterly
KEWA | 3 | 2001-03-31 | NCV (Green ) | (PIM) FIRE DOOR FUSIBLE LINKS. | 2001006 | 2001 | Annual/Quarterly
KEWA | 3 | 2002-09-30 | NCV (Green ) | (PIM) Failure to Provide Appendix R Barriers Between Dedicated and Alternate Fire Zones | 2002005 | 2002 | Annual/Quarterly
KEWA | 3 | 2004-12-31 | NCV (Green ) | (PIM) Inadequate Control Of Combustible Materials | 2004009 | 2004 | Annual/Quarterly
KEWA | 3 | 2004-12-31 | NCV (Green ) | (PIM) Inadequate Corrective Action to Preclude Storage of Oxygen Cylinders Next to Flammable Gas Cylinders | 2004009 | 2004 | Annual/Quarterly
KEWA | 3 | 2006-12-31 | NCV (Green ) | (PIM) Inadequate Pre-Fire Strategy Identified in Cable Spreading Room | 2006005 | 2006 | Annual/Quarterly
LASA | 3 | 2007-06-30 | NCV (Green ) | (PIM) Licensee Relied on Operator Manual Actions for Post-fire SSD. | Open in TR 2005006 as an URI and closed in IR 2007003 as NCV. | 2005 | Triennial
LASA | 3 | 2005-09-02 | NCV (Green ) | (PIM) Procedures Fail To Ensure Fire Doors Are Operable | 2005006 | 2005 | Triennial
LASA | 3 | 2008-11-17 | NCV (Green ) | (PIM) Unauthorized Transient Combustibles | 2008007 | 2008 | Triennial
LASA | 3 | 2008-11-17 | NCV (Green ) | (PIM) Failure to provide a sprinkler system for Fire Zone 4F3 | 2008007 | 2008 | Triennial
LASA | 3 | 2000-09-30 | Finding (Green ) | (PIM) The inspectors completed the assessment of an issue identified involving two holes between the U1, Div 1 and U1, Div 2 Essential Switchgear Rooms. | 2000013 | 2000 | Annual/Quarterly
LASA | 3 | 2000-09-30 | NCV (Green ) | (Non-PIM) 3-Hour Fire Barrier Degradation | 2000013 | 2000 | Annual/Quarterly
LASA | 3 | 2002-09-30 | NCV (Green ) | (PIM) Essential Switchgear Room Degraded Fire Barriers | 2002005 | 2002 | Annual/Quarterly
LASA | 3 | 2005-03-31 | NCV (Green ) | (PIM) Failure to Properly Implement Procedure Requirements for Hot Work and Ignition Control Results in a Fire in the 2B RHR Corner Room | 2005002 | 2005 | Annual/Quarterly
LASA | 3 | 2005-06-30 | NCV (Green ) | (PIM) Failure to Properly Implement Fire Protection Procedure Requirements for Hot Work and Ignition Control Issues. | 2005003 | 2005 | Annual/Quarterly
LASA | 3 | 2006-09-30 | NCV (Green ) | (PIM) Failure to Promptly Repair a Degraded Condition Associated with the 2B EDG Day Tank Room Structure | 2006005 | 2006 | Annual/Quarterly
LASA | 3 | 2009-06-24 | NCV (Green ) | (PIM) Failure to implement a fire protection program procedure for combustible controls | 2009003 | 2009 | Annual/Quarterly
LIM | 1 | 2007-08-09 | NCV (Green ) | (PIM) Inadequate Fire safe Shutdown Procedure for Securing HPCI | 2007006 | 2007 | Triennial
MCG | 2 | 2004-03-13 | NCV (Green ) | (PIM) Standby Shutdown Facility was Not Independent of Cables in Fire Areas 2 and 14 | Open in TR 2000009 as URI and closed in an IR 2004003 as NCV. Not found in the ROP website; obtained from the triennial inspection report. | 2000 | Triennial
MCG | 2 | 2004-09-11 | NCV (Green ) | (PIM) Inadequate Separation and Protection of Cables Associated With Redundant Trains of Instrumentation Located in the Same Fire Area | Open in TR 2003007 as URI and closed in an IR 2004004 as NCV. | 2003 | Triennial
MCG | 2 | 2004-03-13 | NCV (Green ) | (PIM) Failure to Include Valve 2CA0007A in the Fire Protection Safe Shutdown Analysis for Control Room Fire | Open in TR 2003007 as URI and closed in an IR 2004003 as NCV. | 2003 | Triennial
MCG | 2 | 2009-05-14 | NCV (Green ) | (PIM) Failure to Take Adequate Corrective Action for Appendix R Emergency Lighting Credited for Operator Action | 2009007 | 2009 | Triennial
MCG | 2 | 2009-05-14 | NCV (Green ) | (PIM) Pertinent Fire Brigade Information and Guidance Not Identified in Fire Fighting Strategies | 2009007 | 2009 | Triennial
MCG | 2 | 2004-03-13 | NCV (Green ) | (PIM) Failure to have pre-fire plans for the Unit 1 and 2 interior and exterior doghouses | 2004003 | 2004 | Annual/Quarterly
MCG | 2 | 2004-03-13 | NCV (SL-IV ) | (PIM) Failure to update the UFSAR - (two examples) | 2004003 | 2004 | Annual/Quarterly
MCG | 2 | 2004-03-13 | NCV (Green ) | (PIM) Failure to have a rated 3-hour barrier around the SSF power system | 2004003 | 2004 | Annual/Quarterly
MCG | 2 | 2004-06-12 | NCV (Green ) | (PIM) Failure to update fire strategy plans when a modification removed numerous extinguishers. | 2004004 | 2004 | Annual/Quarterly
MCG | 2 | 2005-06-30 | NCV (Green ) | (PIM) Failure to Have Adequate Procedures to Implement Fire Mitigation Actions For Containment | 2005003 | 2005 | Annual/Quarterly
MCG | 2 | 2005-06-30 | NCV (Green ) | (PIM) Failure to Have Adequate Procedures to Implement SLC Test Requirements for Fire Protection Sprinklers | 2005003 | 2005 | Annual/Quarterly
MCG | 2 | 2006-03-31 | NCV (Green ) | (PIM) Failure to Take Adequate Corrective Action for Repetitive Fire Strategy Plan Deficiencies | 2006002 | 2006 | Annual/Quarterly
MCG | 2 | 2009-06-30 | NCV (Green ) | (PIM) Failure to Adequately Implement Design Control Measures For Fire Protection | 2009003 | 2009 | Annual/Quarterly
MILL | 1 | 2001-11-02 | Finding (Green ) | (PIM) INSUFFICIENT COMPENSATORY MEASURES FOR REMOVAL OF CABLE SPREADING ROOM CO2 SUPPRESSION SYSTEM | 2001012 | 2001 | Triennial
MILL | 1 | 2007-10-05 | NCV (Green ) | (PIM) Auxiliary Building Fire Safe Shutdown Procedure Lacked RCP Seal Thermal Shock Precautions | 2007007 | 2007 | Triennial
MILL | 1 | 2007-10-05 | NCV (Green ) | (PIM) Auxiliary Shutdown Panel Reactor Head Vent Valves Not Isolated from Effects of a Control Room Fire | 2007007 | 2007 | Triennial
MILL | 1 | 2007-10-05 | NCV (Green ) | (PIM) Emergency Light Unit High Failure Rate | 2007007 | 2007 | Triennial
MILL | 1 | 2008-12-05 | NCV (Green ) | (PIM) NCV 05000336/2008008-01, Failure to Ensure Equipment Necessary For Fire Safe Shutdown Available. | 2008008 | 2008 | Triennial
MILL | 1 | 2008-12-05 | NCV (Green ) | (PIM) NCV 05000336/2008008-02, Failure to Ensure Timely Manual Action Consistent with the Post-Fire Safe Shutdown Analysis. | 2008008 | 2008 | Triennial
MILL | 1 | 2008-06-30 | NCV (Green ) | (PIM) Fire Protection Deficiency Resulting in Potential Loss of All Charging Pumps | Open in TR 2007007 as URI and closed in IR 2008003 as NCV. | 2008 | Triennial
MILL | 1 | 2000-07-01 | NCV (Green ) | (PIM) FAILURE TO MAINTAIN FIRE FIGHTING STRATEGIES | 2000008 | 2000 | Annual/Quarterly
MILL | 1 | 2001-08-11 | Finding (Green ) | (PIM) LICENSEE'S ON-SITE FIRE BRIGADE TEAM RECEIVED A FAILING GRADE FOLLOWING AN UNANNOUNCED FIRE DRILL DUE TO DEGRADATION OF A FIRE PROTECTION DEFENCE-IN-DEPTH FEATURE | 2001006 | 2001 | Annual/Quarterly
MILL | 1 | 2002-06-29 | NCV (Green ) | (PIM) FAILURE TO MAINTAIN FIRE BARRIER REQUIREMENTS DESCRIBED IN THE PLANT FIRE HAZARDS ANALYSIS | 2002004 | 2002 | Annual/Quarterly
MILL | 1 | 2005-06-30 | NCV (Green ) | (PIM) FAILURE TO EVALUATE EXCEEDING SPECIFIED FIRE LOADING LIMIT FOR MAIN STEAM VALVE ENCLOSURE | 2005003 | 2005 | Annual/Quarterly
MONT | 3 | 2002-06-21 | NCV (Green ) | (PIM) Failure to Meet the Separation Criteria for Redundant Cabling and Equipment in Fire Zone 12A, Intake Structure Pump Room | 2002011 | 2002 | Triennial
MONT | 3 | 2002-06-21 | NCV (Green ) | (PIM) Procedures C.4-b-8.5.A, "Plant Fire," C.4-C, "Shutdown Outside the Control Room," and Other Related Procedures Associated with Responding to a Plant Fire Were Not Appropriate to the Circumstances. | 2002011 | 2002 | Triennial
MONT | 3 | 2002-06-21 | NCV (Green ) | (PIM) Failure to Maintain Full Area Detector Coverage in Zones 23A, 14A, 13B, 19A, and 19B. | 2002011 | 2002 | Triennial
MONT | 3 | 2002-06-21 | NCV (Green ) | (PIM) Failure to maintain Complete Sprinkler Coverage in Fire Zones 13A and 13B. | 2002011 | 2002 | Triennial
MONT | 3 | 2002-06-21 | NCV (Green ) | (PIM) Failure to Enter Conditions Adverse to Quality into the Corrective Action Program and to Correct Conditions Adverse to Quality. | 2002011 | 2002 | Triennial
MONT | 3 | 2002-06-21 | NCV (SL-IV ) | (PIM) Failure to Perform Written Safety Evaluations and Summit a Summary to the NRC for Changes Made to the FPP, FHA, and SSA from 1984 to 2001. | 2002011 | 2002 | Triennial
MONT | 3 | 2005-11-04 | NCV (Green ) | (PIM) FAILURE TO ADDRESS SIGNIFICANT OBSTRUCTION OF SPRINKLER HEADS. | 2005013 | 2005 | Triennial
MONT | 3 | 2008-04-18 | NCV (Green ) | (PIM) Uncontrolled Transient Combustibles. | 2008006 | 2008 | Triennial
MONT | 3 | 2008-04-18 | NCV (Green ) | (PIM) SHUTDOWN PANEL REQUIREMENTS REMOVED FROM IMPROVED TECHNICAL SPECIFICATIONS. | 2008006 | 2008 | Triennial
MONT | 3 | 2001-05-30 | NCV (Green ) | (PIM) FIRE PROTECTION ADMINISTRATIVE CONTROLS. | 2001005 | 2001 | Annual/Quarterly
MONT | 3 | 2004-03-20 | NCV (Green ) | (PIM) FAILURE TO FOLLOW FIRE PROTECTION PROGRAM PROCEDURES WHICH REQUIRE THAT CHANGES MADE TO THE FIRE PROTECTION PROGRAM BE EVALUATED FOR IMPACTS TO SAFE-SHUTDOWN CAPABILITIES. | 2004002 | 2004 | Annual/Quarterly
MONT | 3 | 2004-03-20 | NCV (Green ) | (PIM) FAILURE TO TAKE PROMPT AND ADEQUATE CORRECTIVE ACTIONS TO CORRECT PRE-FIRE STRATEGIES. | 2004002 | 2004 | Annual/Quarterly
MONT | 3 | 2006-06-30 | Finding (Green ) | (PIM) IMPROPER LOOSE MATERIAL STORAGE ADJACENT TO LPCI COMPONENTS. | 2006003 | 2006 | Annual/Quarterly
MONT | 3 | 2006-12-31 | NCV (Green ) | (PIM) LICENSEE ANNOUNCED FIRE DRILL IMPLEMENTATION PRACTICE INCONSISTENT WITH THE REQUIREMENTS OF APPENDIX R. | 2006005 | 2006 | Annual/Quarterly
NA | 2 | 2000-07-01 | NCV (Green ) | (PIM) INADEQUATE PROCEDURE FOR ALTERNATIVE SHUTDOWN FOR A CONTROL ROOM FIRE | NCV from IR 2000003 due to continue investigation of the 2 NCV from TR 2000007. | 2000 | Triennial
NA | 2 | 4/31/2000 | NCV (Green ) | Failure to analyze for the affect on the post-fire safe shutdown capability of fire-induced failures of the main feedwater system. | Open in TR 2000007 as URI and closed in IR 2000006 as a NCV in 2000006. This finding did not show up in the triennial findings neither in the annual/quarterly findings when you do the search in the ROP Web Site. | 2000 | Triennial
NA | 2 | 4/31/2001 | NCV (Green ) | Inadequate procedural guidance for implementing alternate shutdown for a fire in the emergency switchgear room. | Open in TR 2000007 as URI and closed in IR 2000006 as a NCV in 2000006. This finding did not show up in the triennial findings neither in the annual/quarterly findings when you do the search in the ROP Web Site. | 2000 | Triennial
NA | 2 | 2000-04-28 | NCV (N/A ) | (PIM) FAILURE TO ANALYZE NON-SAFETY CIRCUITS WHICH COULD PRODUCE TRANSIENTS DUE TO POTENTIAL FIRE INDUCED SPURIOUS OPERATION | 2000007 | 2000 | Triennial
NA | 2 | 2000-04-28 | NCV (Green ) | (PIM) INADEQUATE PROCEDURE GUIDANCE FOR IMPLEMENTING ALTERNATE SHUTDOWN FOR A FIRE IN THE MAIN CONTROL ROOM | 2000007 | 2000 | Triennial
NA | 2 | 2004-12-31 | NCV (Green ) | (PIM) Fire Response Procedures Not Adequate to Maintain Reactor Coolant Level Within the Level Indication of the Pressurizer (Section 4OA5) | Open in TR 2003006 as URI and closed in IR 2004006 as NCV. This finding appeared in the annual/quarterly findings search. | 2003 | Triennial
NA | 2 | 2004-06-26 | NCV (Green ) | (PIM) Alternate Shutdown Panel Ventilation System Not Independent From Impacts of a Main Control Room Fire | Open in TR 2003006 as URI and closed in IR 2004003 as NCV. | 2003 | Triennial
NA | 2 | 2003-05-23 | NCV (Green ) | (PIM) Failure to Demonstrate the Fire Resistance Rating of 3-Hour Duct Wrap | 2003006 | 2003 | Triennial
NA | 2 | 2006-02-10 | NCV (Green ) | (PIM) Carbon Dioxide System for Unit 2 Cable Vault and Tunnel Area Has Degraded Manual Mode | 2005008 | 2006 | Triennial
NA | 2 | 2009-11-12 | NCV (Green ) | (PIM) Failure to Adequately Address the Potential for CO2 Over-pressurization within the Unit 2 Cable Vault & Tunnel | 2009008 | 2009 | Triennial
NA | 2 | 2009-11-12 | NCV (Green ) | (PIM) Inadequate Procedure for Powering Credited Components for Fire in Cable Vault & Tunnel. | 2009008 | 2009 | Triennial
NA | 2 | 2006-12-31 | NCV (Green ) | (PIM) Failure to Identify Unsatisfactory Performance of a Fire Brigade Crew | 2006005 | 2006 | Annual/Quarterly
NA | 2 | 2008-01-30 | NCV (Green ) | (PIM) Failure to Adequately Install an Oil Collection System on a Reactor Coolant Pump Motor | 2008002 | 2008 | Annual/Quarterly
NA | 2 | 2008-12-31 | NCV (Green ) | (PIM) Reactor Coolant Pump Motor Oil Collection System Installation and Design Problems | 2008005 | 2008 | Annual/Quarterly
NMP | 1 | 2003-06-20 | NCV (Green ) | (PIM) Failure to Promptly Correct Fire Protection Deficiency. | 2003007 | 2003 | Triennial
NMP | 1 | 2009-06-19 | NCV (Green ) | Failure to Implement Fire Brigade Training Program Procedure | 2009006 | 2009 | Triennial
NMP | 1 | 2001-02-10 | NCV (Green ) | (PIM) INADEQUATE CORRECTIVE ACTIONS ASSOCIATED WITH FIRE DAMPERS. | 2000011 | 2000 | Annual/Quarterly
NMP | 1 | 2001-02-10 | NCV (Green ) | (PIM) FAILURE TO FOLLOW PROCEDURE ASSOCIATED WITH FIRE DAMPER SURVEILLANCE TEST. | 2000011 | 2000 | Annual/Quarterly
NMP | 1 | 2003-12-31 | NCV (Green ) | (PIM) Degraded Penetration Fire Seal not Identified in a Timely Manner. | 2003006 | 2003 | Annual/Quarterly
NMP | 1 | 2004-03-31 | NCV (Green ) | (PIM) Barrier Breach Permits Cleared while Associated Fire Doors were Still Inoperable | 2004002 | 2004 | Annual/Quarterly
OC | 1 | 2005-11-04 | NCV (Green ) | (PIM) Failure to Provide Protection in Accordance with 10 CFR Part 50, Appendix R, Section III.G.2. | Open in TR 2002011 as URI and closed in TR 2005008 as NCV. | 2002 | Triennial
OC | 1 | 2008-06-27 | NCV (Green ) | (PIM) Failure to Review the Impact of Site Staffing Changes to the Fire Protection Program | 2008008 | 2008 | Triennial
OC | 1 | 2000-11-18 | Finding (N/A ) | (PIM) Personnel Performance During Non-routine Plant Evolutions and Events | 2000008 | 2000 | Annual/Quarterly
OC | 1 | 2000-11-18 | NCV (Green ) | (PIM) Fire Protection | 2000008 | 2000 | Annual/Quarterly
OC | 1 | 2001-03-16 | NCV (Green ) | (PIM) Fire Protection | 2001003 | 2001 | Annual/Quarterly
OC | 1 | 2001-08-11 | NCV (Green ) | (PIM) Routine Fire Protection Walkdowns | 2001007 | 2001 | Annual/Quarterly
OC | 1 | 2006-09-30 | NCV (Green ) | (PIM) Fire Protection Plan Requirements Not Implemented | 2006004 | 2006 | Annual/Quarterly
OC | 1 | 2007-03-31 | NCV (Green ) | (PIM) Improper Identification of an Inoperable Fire Barrier Door | 2007002 | 2007 | Annual/Quarterly
OCO | 2 | 2004-02-27 | NCV (Green ) | (PIM) Inadequate Maintenance of Fire Safe Shutdown Procedures | Open in TR 2002003 as URI and closed in TR in 2004010 as NCV. | 2002 | Triennial
OCO | 2 | 2004-07-20 | Violation (White ) | (PIM) Failure to Meet Licensing Basis for Staffing the SSF in the Event of a Confirmed Fire | Open in TR 2002003 as URI and closed in TR in 2004012 as Apparent Violation. The apparent Violation was discussed in 2004013 in which was declared as a white finding. | 2002 | Triennial
OCO | 2 | 2000-09-30 | NCV (Green ) | (PIM) Failure to Evaluate Flammable Material Use in the Unit 2 East Penetration Room | 2000006 | 2000 | Annual/Quarterly
OCO | 2 | 2003-04-05 | NCV (Green ) | (PIM) Failure to Evaluate Combustible Material in the KHU Complex | 2003002 | 2003 | Annual/Quarterly
PALI | 3 | 2001-07-27 | NCV (Green ) | (PIM) Smoke Detectors Inadequate - Southern Portions of Cable | Triennial Report 2001008. Check because this finding is included in the annual findings. I found this finding in the triennial report not in the website. | 2001 | Triennial
PALI | 3 | 2001-07-27 | NCV (Green ) | (PIM) Smoke Detectors Inadequate - 1-D Switchgear Room | Triennial Report 2001008. Check because this finding is included in the annual findings. I found this finding in the triennial report not in the website. | 2001 | Triennial
PALI | 3 | 2001-07-27 | Violation (White ) | (PIM) Smoke Detectors Inadequate - Northwest Portion of Cable Spreading Room | Open in TR 2001008 as Apparent Violation, discussed in 2002008 and closed in IR as White Violation. | 2001 | Triennial
PALI | 3 | 2008-03-31 | NCV (Green ) | (PIM) Failure to Ensure Fire Door Was Closed | 2008002 | 2008 | Annual/Quarterly
PALO | 4 | 2007-08-17 | NCV (Green ) | (PIM) Inadequate procedure for safe shutdown from outside the control room | 2007008 | 2007 | Triennial
PALO | 4 | 2006-03-31 | NCV (Green ) | (PIM) INADEQUATE DIESEL FIRE PUMP BATTERY SURVEILLANCE | 2006002 | 2006 | Annual/Quarterly
PALO | 4 | 2009-06-30 | NCV (Green ) | (PIM) Inoperable Fire Barrier Door for Emergency Diesel Generator Train B | 2009003 | 2009 | Annual/Quarterly
PB | 1 | 2003-04-25 | NCV (Green ) | (PIM) Failure To Provide Cable Protection in Accordance With 10 CFR Part 50, Appendix R, Section III.G.2 | 2003009 | 2003 | Triennial
PB | 1 | 2008-03-31 | NCV (Green ) | (PIM) Failure to Identify and Document Fire Brigade Deficiencies | 2008002 | 2008 | Annual/Quarterly
PERR | 3 | 2000-11-02 | NCV (N/A ) | (PIM) Failure to update procedures ONI-054 in a timely manner to include information used to alert operators about potential fire impacts upon RHR valves. | 2000010 | 2000 | Triennial
PERR | 3 | 2000-11-02 | NCV (Green ) | (PIM) Failure to address extended inoperability of the control room sub floor CO2 system. | 2000010 | 2000 | Triennial
PERR | 3 | 2006-12-15 | NCV (Green ) | (PIM) Failure to provide full electrical isolation in the design of the post-fire safe shutdown control logic circuitry | 2006006 | 2006 | Triennial
PERR | 3 | 2006-12-15 | NCV (Green ) | (PIM) Failure to evaluate the floor drain capacity in the division 1 and 2 cable spreading rooms | 2006006 | 2006 | Triennial
PERR | 3 | 2009-06-26 | NCV (Green ) | (PIM) Failure to Maintain Procedures for Post Fire Operation of Control Room HVAC Fans and Control of Remote Shutdown Room Toolbox Inventory. | 2009007 | 2009 | Triennial
PERR | 3 | 2009-06-26 | NCV (Green ) | (PIM) Failure to Assure That Systems Structures and Components Necessary to Achieve And Maintain Hot Shutdown Conditions Were Free of Fire Damage Without Repair Actions. | 2009007 | 2009 | Triennial
PERR | 3 | 2009-06-26 | NCV (Green ) | (PIM) Failure to Provide Required Electrical Isolation for Post Fire Safe Shutdown Electrical Circuits | 2009007 | 2009 | Triennial
PERR | 3 | 2003-03-31 | Finding (Green ) | (PIM) FAILURE TO PROMPTLY IDENTIFY AND CORRECT DEGRADED FIRE BARRIER | 2003003 | 2003 | Annual/Quarterly
PERR | 3 | 2003-09-30 | Finding (Green ) | (PIM) FAILURE TO MAINTAIN FIRE BARRIERS | 2003006 | 2003 | Annual/Quarterly
PERR | 3 | 2004-12-31 | Finding (Green ) | (PIM) FAILURE TO PROMPTLY IDENTIFY A DEGRADED FIRE BARRIER | 2004015 | 2004 | Annual/Quarterly
PERR | 3 | 2005-09-30 | NCV (Green ) | (PIM) FAILURE TO EVALUATE INTERFERENCE WITH THE DESIGN RATTLE SPACE BETWEEN SAFETY CLASS BUILDINGS | 2005009 | 2005 | Annual/Quarterly
PERR | 3 | 2007-06-30 | NCV (Green ) | (PIM) IMPROPER STORAGE OF COMBUSTIBLE MATERIAL | 2007003 | 2007 | Annual/Quarterly
PERR | 3 | 2008-09-30 | NCV (Green ) | (PIM) Impaired Fire Barrier for Safety-Related Building | 2008004 | 2008 | Annual/Quarterly
PILG | 1 | 2000-08-18 | NCV (Green ) | (PIM) Emergency Lighting Units were not installed to support manual operation | 2000004 | 2000 | Triennial
PILG | 1 | 2000-08-18 | NCV (Green ) | (PIM) Emergency diesel generator watt-meter cables in the cable spreading room were neither protected nor isolated | 2000004 | 2000 | Triennial
PILG | 1 | 2003-07-31 | NCV (Green ) | (PIM) Failure to Provide Instrumentation for Diagnosing and Verifying Manual Actions. | 2003005 | 2003 | Triennial
PILG | 1 | 2009-10-01 | NCV (Green ) | (PIM) Failure to establish adequate procedures to prevent adverse impact due to spurious valve closure caused by fire damage. | 2009007 | 2009 | Triennial
POIN | 3 | 2001-09-28 | Finding (N/A ) | (PIM) HUMAN PERFORMANCE CROSS-CUTTING ISSUE DUE TO WEAKNESSES IN FIRE PROTECTION ENGINEERING AREA | 2001012 | 2001 | Triennial
POIN | 3 | 2001-09-28 | NCV (N/A ) | (PIM) Emergency Lighting Inadequate in Façade Area | 2001012 | 2001 | Triennial
POIN | 3 | 2001-09-28 | NCV (Green ) | (PIM) Auxiliary Feedwater Pump Room Halon System Inadequate for Deep-Seated Fire Hazard | 2001012 | 2001 | Triennial
POIN | 3 | 2001-09-28 | NCV (N/A ) | (PIM) INSUFFICIENT APPENDIX R FUEL OIL SUPPLY | 2001012 | 2001 | Triennial
POIN | 3 | 2001-09-28 | NCV (Green ) | (PIM) POSSIBLE SPURIOUS OPENING OF POWER-OPERATED RELIEF VALVE DURING FIRES | 2001012 | 2001 | Triennial
POIN | 3 | 2004-11-19 | NCV (Green ) | (PIM) Failure to Ensure That a Safe Shutdown Procedure Directed Alignment of Instrumentation to a Direct Current Bus with a Battery Charger | 2004010 | 2004 | Triennial
POIN | 3 | 2007-07-13 | Finding (N/A ) | (PIM) Failure to Meet Separation Requirements for Redundant Trains | 2007006 | 2007 | Triennial
POIN | 3 | 2007-07-13 | NonCited Violation (Green ) | (PIM) Failure to Promptly Correct Non-Compliant Sprinkler Heads in the EDG Rooms | 2007006 | 2007 | Triennial
POIN | 3 | 2003-12-31 | NCV (Green ) | (PIM) Inadequate Corrective Actions for Control of Transient Combustibles | 2003009 | 2003 | Annual/Quarterly
POIN | 3 | 2004-03-31 | NCV (Green ) | (PIM) Sprinkler Head Locations Not in Accordance with Fire Code | 2004002 | 2004 | Annual/Quarterly
POIN | 3 | 2004-06-30 | NCV (Green ) | (PIM) Loss of Transient Combustible Control in the Containment and Turbine Buildings During a Unit 1 Refueling Outage | 2004003 | 2004 | Annual/Quarterly
POIN | 3 | 2008-06-30 | NCV (Green ) | (PIM) Failure to Address Sprinkler Head Obstructions in 'B' Train EDG Rooms | 2008003 | 2008 | Annual/Quarterly
PRAI | 3 | 2004-06-30 | NCV (Green ) | (PIM) CYCLING OF SAFETY INJECTION PUMPS FOR FIRE SCENARIOS | Open in TR 2004002 as URI and closed in an IR 2004005 as NCV. | 2004 | Triennial
PRAI | 3 | 2004-03-05 | NCV (Green ) | (PIM) TRANSIENT COMBUSTIBLES INVALIDATED EXEMPTION FOR LACK OF A FIRE SUPPRESSION SYSTEM | 2004002 | 2004 | Triennial
PRAI | 3 | 2006-08-18 | NCV (Green ) | (PIM) No Fire-Rated Damper in Return Ventilation Duct | 2006009 | 2006 | Triennial
PRAI | 3 | 2006-08-18 | NCV (Green ) | (PIM) Surveillance Did Not Include TS Requirements | 2006009 | 2006 | Triennial
PRAI | 3 | 2006-08-18 | NCV (Green ) | (PIM) Lack of Smoke Detectors | 2006009 | 2006 | Triennial
PRAI | 3 | 2009-04-24 | Finding (Green ) | (PIM) Failure to Ensure Fire door Would Consistently Close | 2009007 | 2009 | Triennial
PRAI | 3 | 2009-04-24 | Finding (N/A ) | (Non-PIM) Unanalyzed Condition Due to Manual Actions That Do Not Comply with 10 CFR 50, Appendix R | 2009007 | 2009 | Triennial
PRAI | 3 | 2009-04-24 | NCV (Green ) | (PIM) Combustible Materials Present Within Safety Related Fire Area | 2009007 | 2009 | Triennial
PRAI | 3 | 2005-06-30 | NCV (Green ) | (PIM) INADEQUATE CONTROL OF TRANSIENT COMBUSTIBLES | 2005004 | 2005 | Annual/Quarterly
QUAD | 3 | 2000-12-15 | NCV (Green ) | (PIM) Failure to Seal Tops of Electrical Cabinets | 2000016 | 2000 | Triennial
QUAD | 3 | 2000-12-15 | NCV (Green ) | (PIM) Failure to Provide Fire Stops in Cable Trays | 2000016 | 2000 | Triennial
QUAD | 3 | 2000-12-15 | NCV (N/A ) | (PIM) Technical Errors in Appendix R Safe Shutdown Procedures | 2000016 | 2000 | Triennial
QUAD | 3 | 2006-06-29 | NCV (Green ) | (PIM) SSMP Credited as a Redundant System for an Appendix R III.G.2 Fire Area | 2006002 | 2006 | Triennial
QUAD | 3 | 2006-06-29 | NCV (Green ) | (PIM) Failure To Ensure One Redundant Train of RHRSW Free of Fire Damage | 2006002 | 2006 | Triennial
QUAD | 3 | 2006-06-29 | NCV (Green ) | (PIM) Procedure Included Unapproved Fuse Repair for Appendix R | 2006002 | 2006 | Triennial
QUAD | 3 | 2006-06-29 | NCV (Green ) | (PIM) Failure to Maintain Acceptable Pre-Fire Plans | 2006002 | 2006 | Triennial
QUAD | 3 | 2006-06-29 | NCV (Green ) | (PIM) Failure to Have a Calculation for Hose Stations That Did Not Meet Code Requirements to Ensure Adequate Water Pressure and Flow Rate | 2006002 | 2006 | Triennial
QUAD | 3 | 2006-06-29 | NCV (Green ) | (PIM) Failure to Meet NFPA Code Requirements for Class A Fire Extinguishers | 2006002 | 2006 | Triennial
QUAD | 3 | 2009-09-10 | NCV (Green ) | (PIM) Failure to Evaluate Lack of Water Spray System Piping | 2009006 | 2009 | Triennial
QUAD | 3 | 2009-09-10 | NCV (Green ) | (PIM) Failure to Provide Adequate Electrical Coordination for Control Circuit | 2009006 | 2009 | Triennial
QUAD | 3 | 2000-09-30 | NCV (Green ) | (PIM) Degraded condition of fire door 128 | 2000014 | 2000 | Annual/Quarterly
QUAD | 3 | 2003-03-31 | NCV (Green ) | (PIM) FAILURE TO MAINTAIN ADEQUATE SPATIAL SEPARATION OF FLAMMABLES FROM THE DIESEL DRIVEN FIRE PUMPS | 2003003 | 2003 | Annual/Quarterly
RBS | 4 | 2004-02-13 | Finding (Green ) | (PIM) Untimely corrective actions for degraded fire protection feature | 2004007 | 2004 | Triennial
RBS | 4 | 2004-02-13 | NCV (Green ) | (PIM) Inadequate procedures for ventilation and smoke control associated with a fire | 2004007 | 2004 | Triennial
RBS | 4 | 2000-11-11 | NCV (Green ) | (PIM) Failure to adequately assess and conduct fire drills | 2000014 | 2000 | Annual/Quarterly
RBS | 4 | 2001-03-31 | NCV (Green ) | (PIM) Failure To Maintain A Fire Barrier Between Two Fire Areas Which Contain Redundant Safe Shutdown Equipment | 2000016 | 2001 | Annual/Quarterly
RBS | 4 | 2001-08-01 | NCV (Green ) | (PIM) Failure to maintain fire barrier requirements described in the plant fire hazards analysis. | 2001003 | 2001 | Annual/Quarterly
RBS | 4 | 2005-06-30 | NCV (Green ) | (PIM) Failure to inspect portable fire extinguishers within the required frequency | 2005003 | 2005 | Annual/Quarterly
ROB | 2 | 2004-09-03 | NCV (Green ) | (PIM) UNAPPROVED LOCAL MANUAL OPERATOR ACTIONS INSTEAD OF REQUIRED PHYSICAL PROTECTION OR SEPARATION OF CABLES TO PRECLUDE FIRE DAMAGE | 2004006 | 2004 | Triennial
ROB | 2 | 2004-09-03 | NCV (Green ) | (PIM) INOPERABLE FIRE BARRIER PENETRATION SEAL | 2004006 | 2004 | Triennial
SALM | 1 | 2000-02-07 | NCV (Green ) | (PIM) PSEG FAILED TO ENSURE THE CO2 SYSTEMS FOR THE UNITS 1 & 2 4,160 VAC ELECTRIC PENETRATION ROOMS REACHED AND MAINTAINED THE REQUIRED CO2 CONCENTRATION 50% | 1999010 | 2000 | Triennial
SALM | 1 | 2000-02-07 | NCV (Green ) | (PIM) PSEG FAILED TO ENSURE THAT ONE TRAIN OF EQUIPMENT NECESSARY TO ACHIEVE HOT SHUTDOWN FORM THE EMERGENCY CONTROL STATION IS FREE OF FIRE DAMAGE | 1999010 | 2000 | Triennial
SALM | 1 | 2000-02-07 | NCV (Green ) | (PIM) PSEG IDENTIFIED A CONDITION IN WHICH A FIRE COULD DAMAGE CABLES SUCH THAT THE POWER OPERATED RELIEF VALVE WOULD OPEN AND THE ASSOCIATED BLOCK VALVE COULD NOT BE CLOSED. | 1999010 | 2000 | Triennial
SALM | 1 | 2006-03-31 | NCV (Green ) | (PIM) FAILURE TO COMPLY WITH STATION COLD SHUTDOWN REPAIR PROCEDURES | 2006007 | 2006 | Triennial
SALM | 1 | 2009-02-13 | NCV (Green ) | (PIM) FAILURE TO EVALUATE SPURIOUS OPERATION OF SAFETY INJECTION SIGNAL | 2009006 | 2009 | Triennial
SALM | 1 | 2000-02-07 | Violation (White ) | (PIM) THE CARBON DIOXIDE TESTS FOR THE UNITS 1 & 2 4,160 VAC SWITCHGEAR ROOMS DID NOT REACH OR MAINTAIN THE REQUIRED CO2 CONCENTRATION OF 50% | 1999010 | 2000 | Triennial
SALM | 1 | 2001-11-10 | NCV (Green ) | (PIM) PSEG NUCLEAR FAILED TO PROPERLY CONTROL TRANSIENT COMBUSTIBLE MATERIALS WITHIN THE UNIT 1 SPENT FUEL POOL | 2001010 | 2001 | Annual/Quarterly
SALM | 1 | 2002-09-30 | NCV (Green ) | (PIM) PSEG NUCLEAR FAILED TO PROPERLY MAINTAIN ROOM ISOLATION BARRIERS AND IMPROPERLY IMPLEMENTED A MODIFICATION TO THE SWITCHGEAR PENETRATION AREA VENTILATION SYSTEM | Opened in 2002007 and discussed in 2002009 | 2002 | Annual/Quarterly
SALM | 1 | 2008-12-30 | NCV (Green ) | (PIM) IMPROPER CONTROL OF TRANSIENT COMBUSTIBLE MATERIAL | 2008005 | 2008 | Annual/Quarterly
SANO | 4 | 2004-10-07 | Finding (Green ) | (PIM) INADEQUATE PROGRAM TO PROVIDE TRAINING FOR OPERATORS ASSIGNED DUTIES AS FIRE TECHNICAL ADVISORS | 2004008 | 2004 | Triennial
SANO | 4 | 2007-06-15 | NCV (Green ) | (PIM) Fire Separation in Fire Area 2/3-AC-50-29 Did Not Comply With Deviation Request. | 2007008 | 2007 | Triennial
SANO | 4 | 2000-04-08 | NCV (Green ) | (PIM) Failure to follow procedure for transient combustible material in battery rooms. | 2000007 | 2000 | Annual/Quarterly
SANO | 4 | 2009-06-02 | NCV (Green ) | (PIM) Failure to Evaluate the Impact of Temporary Scaffolding on Installed Fire Protection Systems | 2009003 | 2009 | Annual/Quarterly
SEAB | 1 | 2005-07-29 | Finding (Green ) | (PIM) Time Critical Operator Actions Not Included in the Safe Shutdown Analysis | 2005008 | 2005 | Triennial
SEQ | 2 | 2002-03-29 | NCV (Green ) | (PIM) INADEQUATE PROTECTION OF SAFE SHUTDOWN (SSD) COMPONENTS | 2002003 | 2002 | Triennial
SEQ | 2 | 2002-03-29 | NCV (Green ) | (PIM) INADEQUATE PROCEDURE GUIDANCE FOR PLANT FIRES | 2002003 | 2002 | Triennial
SEQ | 2 | 2002-03-29 | NCV (Green ) | (PIM) INADEQUATE EMERGENCY LIGHTING FOR REFUELING WATER STORAGE TANK (RWST) SUCTION VALVES | 2002003 | 2002 | Triennial
SEQ | 2 | 2002-03-29 | NCV (Green ) | (PIM) INADEQUATE PROTECTION FOR VOLUME CONTROL TANK (VCT) SUCTION VALVES | 2002003 | 2002 | Triennial
SEQ | 2 | 2008-06-27 | NCV (Green ) | (PIM) Sprinklers too far below Ceiling in Cable Spreading Room | Open in TR 2005011 as a URI and closed in TR 2008006 as a NCV. | 2005 | Triennial
SEQ | 2 | 2008-06-27 | NCV (Green ) | (PIM) Fire Detectors in 480 V Shutdown Board Room 2B2 Not Installed According to NFPA Code | 2008006 | 2008 | Triennial
SEQ | 2 | 2003-12-27 | NCV (Green ) | (PIM) Failure to Implement Timely and Appropriate Fire Protection Compensatory Measures | 2003006 | 2003 | Annual/Quarterly
SEQ | 2 | 2004-03-27 | NCV (Green ) | (PIM) Inappropriate Change to the Approved Fire Protection Program | 2004002 | 2004 | Annual/Quarterly
SEQ | 2 | 2006-03-31 | NCV (Green ) | (PIM) Inadequate Procedure Results in Blocked Sprinkler Head Without Compensatory Actions | 2006002 | 2006 | Annual/Quarterly
SEQ | 2 | 2008-03-31 | NCV (Green ) | (PIM) Inadequate Tagging Procedure | 2008002 | 2008 | Annual/Quarterly
STL | 2 | 2003-03-28 | NCV (Green ) | (PIM) Cables in Containment Fail to Meet 10 CFR 50, Appendix R, Criterion III.G.2 Requirements | 2003002 | 2003 | Triennial
STL | 2 | 2003-10-31 | NCV (Green ) | Failure to Evaluate the Combustible Loading of Oil-Filled Transformers in the FHA and the Effect on SSD Capability in the Event of a Fire in Unit 2 | Open in TR 2003002 as URI and closed in IR 2003013 as NCV. This NCV appeared under the quarterly findings list. | 2003 | Triennial
STL | 2 | 2006-10-20 | NCV (Green ) | (PIM) Failure to Test the Sound Powered Phones in Accordance With Surveillance Procedures | 2006010 | 2006 | Triennial
STL | 2 | 2009-04-30 | NCV (Green ) | (PIM) Failure to Correct Conditions Adverse to Quality | 2009007 | 2009 | Triennial
STL | 2 | 2001-06-30 | NCV (Green ) | (PIM) Inoperable Cable Spreading Room Smoke Detector | 2001003. The finding was obtained in a IR but appeared under the triennial website search | 2001 | Annual/Quarterly
STL | 2 | 2001-06-30 | NCV (Green ) | (PIM) Fire Detection Electrical Monitoring System Not in Accordance with Requirements | 2001003. The finding was obtained in an IR but appeared under the triennial website search. | 2001 | Annual/Quarterly
STL | 2 | 2001-06-30 | NCV (Green ) | (PIM) Inadequate Testing of Sprinkler System | 2001003. The finding was obtained in a IR but appeared under the triennial website search | 2001 | Annual/Quarterly
STL | 2 | 2001-09-29 | NCV (Green ) | (PIM) Failure to Maintain Control of Fire Alarm Computer Design Features Required by the NRC Approved Fire Protection Program | 2001004 | 2001 | Annual/Quarterly
STL | 2 | 2001-09-29 | NCV (Green ) | (PIM) Inadequate Implementation of Interim Corrective Actions to Compensate for a Degraded Fire Alarm Computer | 2001004 | 2001 | Annual/Quarterly
STL | 2 | 2008-09-30 | NCV (Green ) | (PIM) Failure to Identify and Correct an Open and Degraded Missile Shield Door | 2008004 | 2008 | Annual/Quarterly
STP | 4 | 2004-07-07 | Finding (Green ) | (PIM) Fire safe shutdown analysis did not account for the impact of reactor coolant seal leakage. | IR 2004003. This finding was found when they were doing the review of two URIs of TR 2002003 but it is not consider part of those 2 URIs. | 2004 | Triennial
STP | 4 | 2005-07-14 | NCV (Green ) | (PIM) Failure to ensure redundant safe shutdown systems located in the same fire area are free of fire damage | 2005006 | 2005 | Triennial
STP | 4 | 2006-04-07 | NCV (Green ) | (Non-PIM) Hot Sticking Motor-operated Valves | Open in TR 2005006 as URI and closed in IR 2006002 as NCV. This NCV appeared under the annual/quarterly findings list. | 2005 | Triennial
STP | 4 | 2006-04-08 | NCV (Green ) | (Non-PIM) Thermal Hydraulic Analysis Inconsistencies | Open in TR 2005006 as URI and closed in IR 2006002 as NCV. This NCV appeared under the annual/quarterly findings list. | 2005 | Triennial
STP | 4 | 2009-07-04 | NCV (Green ) | (PIM) Failure to Ensure a Reliable Fire Suppression Water Supply System | Open in TR 2008008 as URI and closed as NCV in IR 2009003. | 2008 | Triennial
STP | 4 | 2009-07-04 | NCV (Green ) | (PIM) Potential Loss of Centrifugal Charging Pump Suction Due to Fire Damage | Open in TR 2008008 as URI and closed as NCV in IR 2009003. | 2008 | Triennial
SUM | 2 | 2001-11-28 | NCV (Green ) | (PIM) Emergency Lighting Installation Deficiencies for Performing Alternative Shutdown Actions | 2001009 | 2001 | Triennial
SUM | 2 | 2005-08-26 | NCV (Green ) | (PIM) Failure to Prevent Spurious Operation of Charging Pump Suction From Volume Control Tank Valves LCV-115C and LCV-115E | Open in TR 2004007as URI and closed in IR 2005009 as NCV. | 2004 | Triennial
SUM | 2 | 2005-08-26 | NCV (Green ) | (PIM) Fire Emergency Procedure Implementation Not Timely To Maintain Pressurizer Level In Indicating Range | Open in TR 2004007as URI and closed in IR 2005009 as NCV. | 2004 | Triennial
SUM | 2 | 2005-08-26 | NCV (Green ) | (PIM) Post-Fire Operator Actions For Reactor Coolant Pump Seal Cooling Were Not Adequate | Open in TR 2004007as URI and closed in IR 2005009 as NCV. | 2004 | Triennial
SUM | 2 | 2004-06-25 | NCV (Green ) | (PIM) Failure to Provide Portable Smoke Ejectors Capable of Operation During a Loss of Offsite Electrical Power | 2004007 | 2004 | Triennial
SUR | 2 | 2004-02-02 | Violation (White ) | (PIM) Alternative Shutdown Capability and Response Procedures Not Adequate to Ensure Safe Shutdown of Unit 1 and 2 | Open in TR 2003007as URI; discussed in the inspection report 2003008 as an Apparent Violation; declared a white violation in the report 2004008, and closed in inspection report 2004011. | 2003 | Triennial
SUR | 2 | 2004-01-07 | NCV (Green ) | (PIM) Fire Response Procedures 1-FCA-3.00 And 0-FCA-14.00 Not Adequate To Ensure Safe Shutdown Of Unit 1. | Open in TR 2003007 as URI and closed in the inspection report 2003008 as NCV. The 2003008 inspection report was an in-office examination of 3 open URIs. | 2003 | Triennial
SUR | 2 | 2004-01-07 | NCV (Green ) | (PIM) Alternate Shutdown Panel Ventilation System Not Independent From Impacts Of A Main Control Room Fire. | Open in TR 2003007 as URI and closed in the inspection report 2003008 as NCV. The 2003008 inspection report was an in-office examination of 3 open URIs. | 2003 | Triennial
SUR | 2 | 2003-02-14 | NCV (Green ) | (PIM) Failure to Adequately Test Diesel Driven Fire Pump Automatic Start Features | 2003007 | 2003 | Triennial
SUR | 2 | 2003-02-14 | NCV (Green ) | (PIM) Inadequate Control of Diesel Driven Fire Pump Fuel Oil Isolation Valve | 2003007 | 2003 | Triennial
SUR | 2 | 2003-02-14 | NCV (Green ) | (Non-PIM) Emergency Diesel Generator No. 3 Bus-tie Breakers Control Circuit Design Deficiency | Open in TR 2003007 as URI and closed in 200304 as NCV. This NCV did not appear in the triennial findings neither in the annual/quarterly findings. I change the denomination from URI to NCV. | 2003 | Triennial
SUR | 2 | 2007-12-31 | NCV (Green ) | (PIM) Carbon Dioxide Suppression System Degraded in Two Fire Areas in Unit 1 and Three Fire Areas in Unit 2 | Open in TR 2006009 as URI and closed in IR 2007005 as NCV. | 2006 | Triennial
SUR | 2 | 2006-06-30 | NCV (Green ) | (PIM) Removal of Damper Motor Operators From CO2 System in Normal Switchgear Rooms | 2006009 | 2006 | Triennial
SUR | 2 | 2006-06-30 | NCV (Green ) | (PIM) Inadequate Procedure for Post-Fire Safe Shutdown During a Fire in Mechanical Equipment Room 3 | 2006009 | 2006 | Triennial
SUR | 2 | 2009-06-26 | NCV (Green ) | (PIM) Failure to Establish Maintenance for Backup Battery for the Halon 1301 System in ESGRs | 2009007 | 2009 | Triennial
SUR | 2 | 2003-04-05 | NCV (Green ) | (PIM) Failure to Properly Evaluate and Approve the Storage of Flammable Materials in the Vicinity of Safety-related Equipment | 2003002 | 2003 | Annual/Quarterly
SUR | 2 | 2007-12-31 | NCV (Green ) | (PIM) Temporary Fire Suppression Capacity Not Equivalent to Unit 1 Containment Fire Hose Stations | 2007005 | 2007 | Annual/Quarterly
SUR | 2 | 2009-09-30 | NCV (Green ) | (PIM) Inadequate Compensatory Measures for the Impairment of Fire Detection Systems | 2009004 | 2009 | Annual/Quarterly
SUSQ | 1 | 2002-08-30 | NCV (Green ) | (PIM) Inadequate Fire Barrier Surveillance | 2002008 | 2002 | Triennial
SUSQ | 1 | 2002-08-30 | NCV (Green ) | (PIM) Inadequate UCSR Under-Floor CO2 Suppression System | 2002008 | 2002 | Triennial
SUSQ | 1 | 2002-08-30 | NCV (Green ) | (PIM) Inadequate UCSR and LCSR Pre-Action Sprinkler System | 2002008 | 2002 | Triennial
SUSQ | 1 | 2005-12-02 | Finding (Green ) | (PIM) Fire Brigade Drill Program Not Consistent With Regulatory Guidance and Industry Standards | 2005009 | 2005 | Triennial
SUSQ | 1 | 2008-11-07 | NCV (Green ) | (PIM) Failure to Establish Adequate Procedures for Operation of the Plant Following Evacuation of the Control Room due to a Fire | 2008009 | 2008 | Triennial
SUSQ | 1 | 2009-09-30 | NCV (Green ) | (PIM) Failure to Implement and Maintain the Fire Protection Program with Respect to the use and Storage of Combustibles in the Control Structure | 2009004 | 2009 | Annual/Quarterly
SUSQ | 1 | 2009-12-31 | NCV (Green ) | (PIM) Insufficient Fire Drill Oversight to Ensure Fire Brigade Performance Deficiencies are Identified | 2009005 | 2009 | Annual/Quarterly
TMI | 1 | 2002-10-25 | NCV (Green ) | (PIM) Inadequate Control of Transient Combustibles | 2002011 | 2002 | Triennial
TMI | 1 | 2005-12-16 | NCV (Green ) | (PIM) Failure to Implement Hot Work Procedural Requirements | 2005012 | 2005 | Triennial
TMI | 1 | 2009-12-31 | NCV (Green ) | (PIM) Potential CO2 Migration Outside the Relay Room Fire Area | Open in TR 2008009 as URI and closed in IR 2009005 as NCV. | 2008 | Triennial
TMI | 1 | 2008-09-12 | NCV (Green ) | (PIM) Inappropriate Use of Elevators by Fire Brigade Members | 2008009 | 2008 | Triennial
TMI | 1 | 2000-12-30 | NCV (Green ) | (PIM) Failure to Implement Compensatory Measures for an Inoperable Battery Room Fire Door | 2000008 | 2000 | Annual/Quarterly
TMI | 1 | 2005-03-31 | NCV (Green ) | (PIM) Failure to Maintain Fire Barriers for the 'A' and 'B' Makeup Pump Rooms | 2005002 | 2005 | Annual/Quarterly
TP | 2 | 2004-02-13 | NCV (Green ) | (PIM) Failure to Install Full Area Fire Detection and Fixed Suppression Systems in the Unit 3 and 4 Mechanical Equipment Room | 2004007 | 2004 | Triennial
TP | 2 | 2007-12-31 | NCV (Green ) | (PIM) Failure to implement the fire protection program: unapproved transient combustibles in the cable spreading room | 2007005 | 2007 | Annual/Quarterly
TP | 2 | 2008-06-30 | Finding (Green ) | (PIM) Maintenance causes smoke and fumes to enter the control room causing fire alarms. | 2008003 | 2008 | Annual/Quarterly
VOG | 2 | 2004-08-26 | NCV (Green ) | (PIM) Inadequate Fire Protection Pre-fire Plan to Ensure Adequate Environmental Conditions for Operators to Access Required Equipment | 2004007 | 2004 | Triennial
VOG | 2 | 2007-11-30 | NCV (Green ) | (PIM) Failure to Adequately Control Transient Combustibles | 2007007 | 2007 | Triennial
VOG | 2 | 2007-11-30 | NCV (Green ) | (PIM) Safe Shutdown Procedure 18068-2 Not Consistent With Analysis | 2007007 | 2007 | Triennial
VOG | 2 | 2007-11-30 | NCV (Green ) | (PIM) Emergency Lighting Units Not Installed as Required by the Fire Protection Program | 2007007 | 2007 | Triennial
VY | 1 | 2004-12-17 | NCV (Green ) | (PIM) Failure to Provide Isolation of Normal Control Power Source for RCIC Steam Supply Line Isolation Valve | 2004010 | 2004 | Triennial
VY | 1 | 2000-07-01 | NCV (Green ) | (PIM) Violation of FSAR Cable Separation Criteria | 2000005 | 2000 | Annual/Quarterly
VY | 1 | 2000-12-30 | NCV (N/A ) | (PIM) Failure to use self-contained breathing apparatus during fire brigade drills | 2000010 | 2000 | Annual/Quarterly
VY | 1 | 2003-06-28 | NCV (Green ) | (PIM) Failure to Take Effective Corrective Actions Regarding Safety-Related Electrical Cable Separation | 2003005 | 2003 | Annual/Quarterly
WAT | 4 | 2000-09-29 | NCV (Green ) | Failure to Isolate Neutral Wire during Transfer to the Alternative Shutdown Panel per 10 CFR Part 50 Appendix R, Section III.L.3 | Open in TR 2000007 as an URI and closed in IR 2004005 as NCV. This NCV did not appear in any findings list. | 2000 | Triennial
WAT | 4 | 2000-09-28 | NCV (Green ) | (PIM) Failure to demonstrate the ratings of 3-hour fire barriers. | 2000007 | 2000 | Triennial
WAT | 4 | 2000-09-27 | NCV (Green ) | (PIM) Failure to initiate condition reports for emergency lighting battery test failures. | 2000007 | 2000 | Triennial
WAT | 4 | 2000-09-18 | NCV (Green ) | (PIM) Failure to maintain in effect a 1-hour rated fire barrier between redundant trains of equipment necessary to achieve and maintain safe shutdown. | 2000007 | 2000 | Triennial
WAT | 4 | 2003-08-19 | NCV (Green ) | (PIM) Failure to test certain emergency diesel generator "B" mini-sequencer contacts. | 2003011 | 2003 | Triennial
WAT | 4 | 2003-08-19 | NCV (Green ) | (PIM) Inadequate emergency lighting for supporting operator actions. | 2003011 | 2003 | Triennial
WAT | 4 | 2003-08-19 | NCV (Green ) | (PIM) Inadequate corrective actions for deficiencies associated with the emergency lighting system. | 2003011 | 2003 | Triennial
WAT | 4 | 2009-05-22 | Finding (N/A ) | (PIM) Failure to provide area wide sprinkler coverage as required in an Appendix R, Section III.G.2.c fire area. | 2009006 | 2009 | Triennial
WAT | 4 | 2009-05-22 | Finding (N/A ) | (PIM) Failure to ensure post-fire safe shutdown valves could be operated. | 2009006 | 2009 | Triennial
WAT | 4 | 2009-05-22 | NCV (Green ) | (PIM) Failure to identify conditions adverse to fire protection. | 2009006 | 2009 | Triennial
WAT | 4 | 2000-07-01 | NCV (Green ) | (PIM) Failure to ensure fire extinguishers remained within their current hydrostatic test dates | 2000005 | 2000 | Annual/Quarterly
WAT | 4 | 2007-12-31 | NCV (Green ) | (PIM) Failure to Follow Procedure Review Process | 2007005 | 2007 | Annual/Quarterly
WB | 2 | 2004-04-16 | NCV (Green ) | (PIM) Inadequate Evaluation Process for Design Changes Which Could Affect Safe Shutdown in the Event of a Fire. | 2004006 | 2004 | Triennial
WB | 2 | 2008-12-31 | NCV (Green ) | (PIM) Carbon Dioxide System in Fire Area 48 Failed to Meet Design Criterion | Open in TR 2007007 as URI and closed in IR 2008005 as NCV. | 2007 | Triennial
WB | 2 | 2007-12-31 | NCV (Green ) | (PIM) Fire Protection Program Did Not Demonstrate Eight-Hour Emergency Light Unit Battery Capacity | Open in TR 2007007 as URI and closed in IR 2007005 as NCV. | 2007 | Triennial
WB | 2 | 2007-06-15 | NCV (Green ) | (PIM) Safe Shutdown Procedure for Portions of FA 8 Not Consistent With Underlying Analysis | 2007007 | 2007 | Triennial
WB | 2 | 2007-06-15 | NCV (Green ) | (PIM) Feeder Cables for Vital Inverter not Protected with One-Hour Fire Barrier | 2007007 | 2007 | Triennial
WB | 2 | 2007-06-15 | NCV (Green ) | (PIM) Failure to Provide Emergency Light at Location of Local Operator Action Important to Safe Shutdown | 2007007 | 2007 | Triennial
WB | 2 | 2002-06-15 | NCV (Green ) | (PIM) FAILURE TO CONTROL TRANSIENT COMBUSTIBLES | 2002002 | 2002 | Annual/Quarterly
WB | 2 | 2003-12-27 | NCV (Green ) | (PIM) Inadequate Operability Evaluation Results in Exceeding the OR Time Limit for Returning Electric Driven Fire Pumps to Operable Status | 2003005 | 2003 | Annual/Quarterly
WB | 2 | 2003-12-27 | NCV (Green ) | (PIM) Seal Not Installed in a Cable Conduit Penetrating a Fire Barrier | 2003005 | 2003 | Annual/Quarterly
WB | 2 | 2004-09-25 | NCV (Green ) | (PIM) Failure to Identify Unsatisfactory Performance of a Fire Brigade Crew | 2004004 | 2004 | Annual/Quarterly
WB | 2 | 2006-10-31 | NCV (Green ) | (PIM) Fire Header Inoperable Due to Failure to Follow Procedure | 2006004 | 2006 | Annual/Quarterly
WC | 4 | 2002-10-11 | NCV (Green ) | (PIM) Inadequate Alternative Shutdown Procedure | 2002008 | 2002 | Triennial
WC | 4 | 2008-10-24 | NCV (Green ) | (PIM) Failure to Evaluate Changes to the Approved Fire Protection Program | Open in TR 2005008 as URI and closed in TR 2008010 as NCV. | 2005 | Triennial
WC | 4 | 2005-12-29 | NCV (Green ) | (PIM) Failure to Ensure Redundant Safe Shutdown Systems Located in the Same Fire Area Are Free of Fire Damage | 2005008 The ROP website had it as an apparent violation but the report stated that is a green NCV. | 2005 | Triennial
WC | 4 | 2005-12-29 | NCV (Green ) | (PIM) Failure to Provide Adequate Post-Fire Shutdown Procedures | 2005008 | 2005 | Triennial
WC | 4 | 12/29//2009 | NCV (Green ) | (PIM) Operator Actions Disable Circuit Breaker Coordination and Could Initiate Secondary Fires | Open in TR 2008010 as URI, and closed in IR 2009005 as NCV. | 2008 | Triennial
WC | 4 | 2009-09-30 | NCV (SL-IV ) | (PIM) Changes to the Approved Fire Protection Program Without Prior Staff Approval | Open in TR 2008010 as URI and closed in IR 2009004 as NCV. | 2008 | Triennial
WC | 4 | 2008-10-24 | NCV (Green ) | (PIM) Failure to Ensure a Fire Pump Would Automatically Start for One Fire Area | 2008010 | 2008 | Triennial
WC | 4 | 2008-10-24 | NCV (Green ) | (PIM) Operator Actions Affect the Ability to Operate Post Fire Safe Shutdown Equipment | 2008010 | 2008 | Triennial
WC | 4 | 2001-03-31 | NCV (Green ) | (PIM) Three hour rated fire door partially open between vital switchgear rooms | 2000011 | 2000 | Annual/Quarterly
WC | 4 | 2002-03-23 | NCV (N/A ) | (PIM) Fire Protection | 2001006 | 2001 | Annual/Quarterly
WC | 4 | 2006-04-07 | NCV (Green ) | (PIM) Failure to provide adequate fire detection in the diesel generator rooms | 2006002 | 2006 | Annual/Quarterly
WC | 4 | 2007-04-07 | NCV (Green ) | (PIM) Failure to implement fire protection impairment control permit requirements and compensatory measures | 2007002 | 2007 | Annual/Quarterly
WC | 4 | 2007-10-06 | NCV (Green ) | (PIM) Failure to implement transient combustible material control permit requirements | 2007004 | 2007 | Annual/Quarterly
WC | 4 | 2008-04-07 | NCV (Green ) | (PIM) Failure to implement fire protection impairment control permit requirements and compensatory measures | 2008002 | 2008 | Annual/Quarterly
WC | 4 | 2008-06-28 | NCV (Green ) | (PIM) Failure to implement transient combustible control permit requirements for a propane tank | 2008003 | 2008 | Annual/Quarterly
WC | 4 | 2009-03-31 | NCV (Green ) | (PIM) Degraded fire barrier for auxiliary feedwater | 2009002 | 2009 | Annual/Quarterly
WC | 4 | 2009-03-31 | NCV (Green ) | (PIM) Failure to implement foreign material exclusion control procedure for spent fuel pool | 2009002 | 2009 | Annual/Quarterly
WC | 4 | 2009-08-12 | NCV (Green ) | (PIM) Failure to Log Foreign Material in Spent Fuel Pool After Extent of Condition Evaluation | 2009004 | 2009 | Annual/Quarterly
WNP | 4 | 2000-05-05 | NCV (Green ) | (PIM) Detectors found not installed in accordance with the fire code. | 2000007 | 2000 | Triennial
WNP | 4 | 2000-05-05 | NCV (Green ) | (PIM) A degraded 1-hour rated Darmatt raceway fire barrier found with an unsealed annular gap through the post-fire safe shutdown barrier envelope. | 2000007 | 2000 | Triennial
WNP | 4 | 2004-04-06 | NCV (Green ) | (PIM) Failure to have adequate procedures in effect for alternative shutdown | Open in TR 2003002 as URI and closed in IR 2004002 as NCV. | 2003 | Triennial
WNP | 4 | 2004-04-06 | NCV (Green ) | (PIM) Inadequate corrective action for a condition affecting safe shutdown | Open in TR 2003002 as URI and closed in IR 2004002 as NCV. | 2003 | Triennial
WNP | 4 | 2003-04-22 | NCV (Green ) | (PIM) Unapproved use of manual actions to protect safe shutdown equipment from the effects of a fire | 2003002 | 2003 | Triennial
WNP | 4 | 2008-09-30 | NCV (Green ) | (PIM) Failure to assure that Division 2 instrument sensing lines remained free of fire damage | Open in TR 2006008 as URI and closed in IR 2008002 as NCV. | 2006 | Triennial
WNP | 4 | 2006-07-13 | NCV (Green ) | (PIM) Failure to Ensure Redundant Safe Shutdown Systems Located In the Same Fire Area Are Free of Fire Damage | 2006008 | 2006 | Triennial
WNP | 4 | 2001-03-31 | NCV (SL-IV ) | (PIM) Failure to obtain NRC approval prior to changing fire protection program (Closes URI 0012-02) | 2001002 | 2001 | Annual/Quarterly
WNP | 4 | 2002-12-28 | NCV (Green ) | (PIM) Man-lift inappropriately stored in control room | 2002004 | 2002 | Annual/Quarterly
WNP | 4 | 2007-12-31 | NCV (SL-IV ) | (PIM) Willful Failure to Complete Fire Watch Rounds and Falsification of Logs (EA 07-282) | 2007005 | 2007 | Annual/Quarterly