NRC INSPECTION MANUAL	DQASIP

INSPECTION PROCEDURE 70400

PREOPERATIONAL TEST RESULT EVALUATION

PROGRAM APPLICABILITY:  2513

70400-01	INSPECTION OBJECTIVES

01.01	Assure that the licensee is performing an adequate evaluation of test results.

01.02	Assure that all test data are either within previously established acceptance criteria, or that deviations are properly dispositioned.

01.03	Evaluate the adequacy of the licensee's methods for correcting deficiencies and for retesting, if necessary.

01.04	Evaluate the adequacy of the licensee's administrative practices in maintaining proper test discipline concerning test execution, test alteration, and test records.

01.05	Verify that the licensee is following his procedures for review, evaluation, and acceptance of test results.

70400-02	INSPECTION REQUIREMENTS

02.01	Review all test changes.

a.	Verify that each change was approved in accordance with pertinent administrative procedures.

b.	Verify that the procedure is annotated to identify test changes.

c.	Verify that the test change has been completed if it entails specific actions.

d.	Verify that none changed the basic objectives of the test.

02.02	Review all test deficiencies.

a.	Verify that each has been resolved, that the resolution has been accepted by appropriate management, and that retest requirements have been completed.

b.	Verify that any system or process changes necessitated by a test deficiency have been properly documented and reviewed.

02.03	Review the test summary and evaluation.

a.	Verify that the cognizant engineering function has evaluated the test results and has signified that the testing demonstrated that the system met design requirements.

b.	Verify that the licensee specifically compared test results with established acceptance criteria.

02.04	Review the "as-run" copy of test procedure.

a.	Verify that data sheets have been completed (10 percent sample).

b.	Verify that all data are recorded where required and are within acceptance tolerances (10 percent sample).

c.	Verify that test deficiencies identified in 02.02a and 02.02b are noted and had received appropriate review and evaluation.

d.	Verify that individual test steps and data sheets have been properly initialed and dated.

02.05	Review the QA inspection records.

a.	Verify that a QA review of the test package has been completed and documented to confirm the adequacy of the test package contents, and to indicate independent review of the test records and data package contents.

b.	Verify that independent audit by QA personnel was performed during test performance as required by administrative procedures.

02.06	Verify that the test results have been approved.

a.	Verify that those personnel charged with responsibility for review and acceptance of test results have documented their review and acceptance of the data package and the evaluation.

b.	If the offsite review committee has audited the test package, verify that the records reflect this audit and that their comments are included and corrective action has been taken.

70400-03	INSPECTION GUIDANCE

03.01	All changes, including deletions, to the test program should be reviewed for conformance to the requirements established in the FSAR and Regulatory Guide 1.68.  If a change results in failure to satisfy FSAR commitments, or eliminates testing identified in Regulatory Guide 1.68, the change should be identified as a test exception in the licensee readiness report resulting from IP 94300.

03.02	In some cases, the test data will not be within the written predicted acceptance criteria.  In this case, the inspector must ascertain that further licensee actions will be or have been taken.  These actions may require plant design changes, evaluation by a manufacturer of the error between the design and predicted plant performance, or restriction of plant operations because of the difference between plant or system performance and predicted acceptance criteria.  The inspector must determine that for each of the above types of actions licensee followup corrective actions have been correctly performed; i.e., licensing approval if required; subsequent testing for each design change, and FSAR change if required.

03.03	The inspector should make his own technical analysis and use his own judgment to assure that the licensee's analysis has been performed correctly.  He should specifically confirm that all test results have been compared with acceptance criteria.

03.04-03.05  Test data packages are assembled by licensees.  The inspector should review the data package to assure that the package is complete (as defined in licensee procedures).  The inspector must also ascertain that the licensee has verified that the acceptance criteria of the procedure have been met.

03.06	Normally, the test results are reviewed by the Plant Superintendent, the NSSS Site Manager, and the A/E Site Manager, or their designees.

Frequently, test review committees will also have examined the results in accordance with FSAR commitments or administrative requirements.

03.07	Accounting.  Inspection effort in utilizing this Inspection Procedure will be recorded on the 766 system by the specific system inspection procedure number.

END

The digits following the "03" numbers in this section refer to the equivalent digits following the "02" numbers in Section 70400-02, "Inspection Requirements."  For example, Section 03.01 offers guidance for Inspection Requirement 02.01.