## IS Test Matrix
Intermediate Scale Test Matrix - Revision F (12-06-06)
|  | Comments: 1) All tests were conducted as open burns with a Propene (Propylene) gas sand burner 2) Colors identify test conditions grouped into the same test run | [14 empty] | ACTUAL TEST CONDITIONS
Burn Test # | Rev. E Test # | Loc. | Cable Insulation Material | [8 empty] | Number of Conductors |  |  |  | Conductor Size (AWG) |  |  |  |  | Cable Bundle Size |  |  |  |  | Water Spary Optionsl | Raceway Type
|  |  | Thermoset | [5 empty] | Thermoplastic
|  |  | XLPE | EPR | Silicone | XLPO | TS/TP | Vita-Link | PE | PVC | Tefzel | 3 | 2 | 7 | 12 | 8 | 12 | 14 | 16 | 18 | 1 | 3 | 6 | 12 | Load Tr | * | 12" Tray | 2.5" Cnd | Air Drop
Prelim 1 | Prelim 1 | A | X | [8 empty] | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | A | X | [10 empty] | X |  |  | X |  |  |  | X | [5 empty] | X
Prelim 2 | Prelim 2 | A | X | [8 empty] | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | A | X | [10 empty] | X |  |  | X |  |  |  | X | [5 empty] | X
Prelim 3 | Prelim 3 | A | [7 empty] | X |  | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | A | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [5 empty] | X
Prelim 4 | Prelim 4 | A | [7 empty] | X |  | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | A | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [5 empty] | X
1 | 15 | A | X | [9 empty] | X | X | X |  | X |  | X | X |  |  |  |  | X |  | X
|  | B | X | [10 empty] | X |  |  | X | [6 empty] | X |  |  | X
|  | D | X | [10 empty] | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | E | X | [10 empty] | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | [10 empty] | X |  |  | X | [6 empty] | X |  |  | X
2 | 1 | A | X | [10 empty] | X |  |  | X | [6 empty] | X |  |  | X
|  | C | X | [10 empty] | X |  |  | X | [5 empty] | X |  |  |  | X
|  | A | X | [5 empty] | X |  |  |  |  | X |  |  | X | [6 empty] | X |  |  | X
|  | C | X | [5 empty] | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
| 11 | C - A | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [7 empty] | X
|  | E | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [5 empty] | X
|  | G | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [5 empty] | X
3 | 2 | A | X | X | [9 empty] | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X | [9 empty] | X |  |  | X | [5 empty] | X |  |  |  | X
| 3 | A |  | X |  |  |  |  | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C |  | X |  |  |  |  | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
| 10 | E | [7 empty] | X |  | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | [7 empty] | X |  | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
4 | 5 | A | X | X |  | X | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X |  | X | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
| 6 | A | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
| 9 | C - A | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [7 empty] | X
|  | E | X | [8 empty] | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | [8 empty] | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
5 | 4 | A | X | X | X | X |  |  | X |  | X |  |  | X |  |  | X | [6 empty] | X |  | X | X
|  | C | X | X | X | X |  |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
| 7 | A | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | X | [5 empty] | X |  | X | X
|  | C | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | X |  |  |  |  | X |  |  | X | X
|  | C - A | X | [10 empty] | X |  |  | X |  |  |  | X | [7 empty] | X
|  | E |  | X | [9 empty] | X |  |  | X |  |  |  | X | [5 empty] | X
|  | G |  | X | [9 empty] | X |  |  | X |  |  |  | X | [5 empty] | X
6 | 12 | A | X | X | X | X |  |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | C | X | X | X | X |  |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | E | X | [5 empty] | X |  | X |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
| 13 | C - A | X | [5 empty] | X |  | X |  |  | X |  |  | X |  |  |  |  | X | [6 empty] | X
|  | A |  | X | X | X | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | C |  | X | X | X | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | G |  |  |  |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  |  |  | X
7 | 14 | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | A | X | X |  | X | X |  |  | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C |  | X |  | X | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | E | X | [5 empty] | X | X |  |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G |  | X |  | X | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
8 | 16 | A | X | [5 empty] | X | X |  |  | X | X | X |  | X |  | X | X |  |  | X |  |  |  | X
|  | A | X | [5 empty] | X | X |  |  | X | X | X |  | X |  | X | X |  |  | X |  |  |  | X
|  | C | X | [5 empty] | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | E | X | [5 empty] | X |  |  |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | [5 empty] | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
9 | 19 | A | X | X | X |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | A | X | X | X |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | C | X | X | X |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | E | X | [5 empty] | X |  | X |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | X | X |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
10 | 20 | A | X | X | X | X | X |  |  |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | A | X | X | X | X | X |  |  |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | C | X | X | X | X | X |  |  | X |  |  |  | X | X |  | X |  |  | X |  |  | X |  |  | X | X
|  | E |  |  |  |  | X |  | X |  | X |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | X |  |  | X |  | X | X | X |  | X | X |  |  | X |  | X |  |  |  | X |  |  |  | X
11 | 21 | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X |  | X | X |  |  | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | E |  |  |  |  | X |  | X | X |  |  |  | X |  |  | X |  |  |  |  | X | [6 empty] | X
|  | G | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
12 | 24 | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X |  | X | X |  |  | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | E |  |  |  |  | X |  | X | X |  |  |  | X |  |  | X |  |  |  |  | X | [6 empty] | X
|  | G | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
13 | 25 | A | X | X |  | X | X | X | X |  | X |  |  | X |  |  | X | [7 empty] | X | X | X
|  | C | X | X |  | X | X | X | X |  | X |  |  | X |  |  | X | [7 empty] | X | X | X
|  | E | X | X | [9 empty] | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | F | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | F | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | G | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | G | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
14 | 27 | A | X | X |  | X | X |  | X | X | X |  |  | X |  |  | X | [7 empty] | X |  | X
|  | C | X | X |  | X | X |  | X | X | X |  |  | X |  |  | X | [7 empty] | X |  | X
|  | E |  |  |  |  | X |  | X | X |  |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | F | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | F | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | G | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | G | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X

## Shorting Summary
Shorting Sequence for Open Burn Test 8, Location A, IRMS #1
Test conditions: Cable: Bundle of 6 XLPE (7/C, 12 AWG), PE (7/C, 12 AWG), XLPE (12/C, 18 AWG), XLPE (2/C, 16 AWG), PVC (12/C, 18 AWG), & PVC (2/C, 16 AWG) control and instrument cables (Items 10, 15, 13, 7, 6, & 4). Cable specimens present: Six lengths of cable were monitored for electrical performance (A, B, C, D, E, & F [See Elect. Conn. Map]), a second bundle of 6 cables was monitored for temperature response. Raceway: 12" B-Line Series 2 tray (part number 248P09-12-144) located at position A in the Test Cell chamber with chamber end walls open and un-heated. Exposure conditions: Gas burner flow rate set to a nominal 150 kW heat release rate and increased to ~300 kW during the test. Electrical repsonse monitoring: IRMS system using 12 channels - two for each cable (see electrical connection map), cable tray was grounded. Thermal response monitoring: Four cable bundle temperatures (see thermocouple map) and the cable tray rung temperature. Gas burner initiated: Following 219 seconds of baseline data monitoring. Special Note: This test was run with the bunker door open and a fan in the exhaust stack pulling the smoke/air mixture out from inside the bunker. The forced air blower was off.
DAQ Time | Burner Time | Event | Interpretation
219 | 0 | Ignited Gas Burner
322-325 | 103-106 | Conductors E9 & E10 both short to ground at less than 100 ohms (7 & 11) | Cable E shorts to ground
343-345 | 124-126 | Conductors F11 & F12 both short to ground at less than 100 ohms (2 & 4) | Cable F shorts to ground
354 | 135 | Conductors E9 & E10 short together at less than 100 ohms (13) | Cable E shorted internally
368 | 149 | Conductors F11 & F12 short together at less than 100 ohms (20) | Cable F shorted internally
456-465 | 237-246 | Conductors C5 & C6 both short to ground at less than 100 ohms (12 & 6) | Cable C shorts to ground
477 | 258 | Conductors C5 & C6 short together at less than 100 ohms (11) | Cable C shorted internally
489-495 | 270-276 | Conductors D7 & D8 both short to ground at less than 100 ohms (6 & 7) | Cable D shorts to ground
513 | 294 | Conductors D7 & D8 short together at less than 100 ohms (4) | Cable D shorted internally
611-627 | 392-408 | Conductors B3 & B4 both short to ground at less than 1000 ohms (133 & 166) | Cable B shorts to ground
740 | 521 | Conductors A1 & A2 short together at less than 100 ohms (90) | Cable A shorted internally
746-768 | 527-549 | Conductors A1 & A2 both short to ground (164 & 32) | Cable A shorts to ground
796 | 577 | The existing ground fault on conductor B3 decreases to less than 100 ohms (7)
799 | 580 | Conductors B3 & B4 short together at less than 100 ohms (63) | Cable B shorted internally
811 | 592 | The existing ground fault on conductor B4 decreases to less than 100 ohms (8)
930 | 711 | The existing ground fault on conductor A1 decreases to less than 100 ohms (3)
2257 | 2038 | Gas burner is shut off
Additional Observations
Observation 1 | No cable to cable interactions took place during this test.

## Thermocouple Map
Thermocouple map for TC's on and within the cable
|  |  |  | Cable A = | XLPE (7/C) | (Item #10)
|  |  |  | Cable B = | PE (7/C) | (Item #15)
|  |  |  | Cable C = | XLPE (12/C) | (Item #13)
|  |  |  | Cable D = | XLPE (2/C) | (Item #7)
|  |  |  | Cable E = | PVC (12/C) | (Item #6)
|  |  |  | Cable F = | PVC (2/C) | (Item #4)
Translation to data file names used in "PenTemps" WorkSheet:
| Map Name |  | Location
| A1 | = | Center of bundle, under jacket
| A2 | = | Air above bundle
| A3 | = | Air below bundle
| A4 | = | Intra-bundle, center

## Elect Conn Map
Electrical connection map within the cables
|  |  |  | Cable A = | XLPE (7/C) | (Item #10)
|  |  |  | Cable B = | PE (7/C) | (Item #15)
|  |  |  | Cable C = | XLPE (12/C) | (Item #13)
|  |  |  | Cable D = | XLPE (2/C) | (Item #7)
|  |  |  | Cable E = | PVC (12/C) | (Item #6)
|  |  |  | Cable F = | PVC (2/C) | (Item #4)
Cable tray rung below D-E-F
Cable Bundle Arrangement
Cable 7-Conductor Arrangement
| Lt Blue = | Even conductor set
| Lt Red = | Odd conductor set
| Gray = | Center conductor (not connected)
IRMS Electrical Connections

## C-C Individuals
Conductor to Conductor Resistances
Open Burn Test 8 |  |  | 2006-11-10 | 13:06
Mix | 7-C | Tray A | IRMS | 1
0 | 150 kW
Burner Time | A1-A2 | Burner Time | A1-B3 | Burner Time | A1-B4 | Burner Time | A1-C5 | Burner Time | A1-C6 | Burner Time | A2-B3 | Burner Time | A2-B4 | Burner Time | A2-C5 | Burner Time | A2-C6 | Burner Time | B3-B4 | Burner Time | B3-C5 | Burner Time | B3-C6 | Burner Time | B3-D7 | Burner Time | B3-D8 | Burner Time | B3-E9 | Burner Time | B3-E10 | Burner Time | B4-C5 | Burner Time | B4-C6 | Burner Time | B4-D7 | Burner Time | B4-D8 | Burner Time | B4-E9 | Burner Time | B4-E10 | Burner Time | C5-C6 | Burner Time | C5-E9 | Burner Time | C5-E10 | Burner Time | C5-F11 | Burner Time | C5-F12 | Burner Time | C6-E9 | Burner Time | C6-E10 | Burner Time | C6-F11 | Burner Time | C6-F12 | Burner Time | D7-D8 | Burner Time | D7-E9 | Burner Time | D7-E10 | Burner Time | D8-E9 | Burner Time | D8-E10 | Burner Time | E9-E10 | Burner Time | E9-F11 | Burner Time | E9-F12 | Burner Time | E10-F11 | Burner Time | E10-F12 | Burner Time | F11-F12
-218.5 | 260337.9994 | -215.5 | 260037.9994 | -212.5 | 258037.9994 | -210 | 256637.9994 | -207 | 258837.9994 | -187.5 | 263137.9994 | -184.5 | 259137.9994 | -181.5 | 260337.9994 | -180 | 256837.9994 | -159.5 | 257937.9994 | -156.5 | 262337.9994 | -153.5 | 257937.9994 | -151 | 254037.9994 | -148.5 | 262237.9994 | -145.5 | 262437.9994 | -142.5 | 259937.9994 | -134 | 523775.9997 | -131.5 | 260537.9994 | -128.5 | 261037.9994 | -125.5 | 262337.9994 | -123 | 259937.9994 | -120 | 262937.9994 | -112 | 258237.9994 | -103.5 | 257137.9994 | -100.5 | 260137.9994 | -97.5 | 263537.9994 | -95 | 259837.9994 | -86.5 | 258237.9994 | -84 | 261037.9994 | -81 | 261937.9994 | -78 | 261637.9994 | -75.5 | 262637.9994 | -72.5 | 261037.9994 | -69.5 | 262337.9994 | -61.5 | 263537.9994 | -58.5 | 261537.9994 | -50.5 | 262437.9994 | -47.5 | 259037.9994 | -44.5 | 262137.9994 | -42 | 258737.9994 | -39 | 263337.9994 | -36 | 253737.9994
-33.5 | 260337.9994 | -30.5 | 260037.9994 | -27.5 | 258037.9994 | -25 | 256637.9994 | -22.5 | 517775.9997 | -2.5 | 263137.9994 | 0.5 | 259137.9994 | 3 | 260337.9994 | 6 | 256837.9994 | 25.5 | 257937.9994 | 28.5 | 262337.9994 | 31 | 257937.9994 | 33.5 | 254037.9994 | 36.5 | 262237.9994 | 39.5 | 262437.9994 | 42 | 259937.9994 | 50.5 | 261837.9994 | 53.5 | 260537.9994 | 56 | 261037.9994 | 59 | 262337.9994 | 61.5 | 259937.9994 | 64.5 | 262937.9994 | 73 | 258237.9994 | 81.5 | 257137.9994 | 84 | 260137.9994 | 87 | 263537.9994 | 90 | 259837.9994 | 98.5 | 258237.9994 | 101 | 261037.9994 | 104 | 261937.9994 | 106.5 | 261637.9994 | 109.5 | 262637.9994 | 112.5 | 261037.9994 | 115 | 262337.9994 | 123.5 | 263537.9994 | 126.5 | 261537.9994 | 134.5 | 12.8434 | 137.5 | 26.6056 | 140 | 5.4959 | 143 | 9.4259 | 145.5 | 13.1341 | 148.5 | 20.1776
151.5 | 130118.9988 | 154 | 260037.9994 | 157 | 258037.9994 | 160 | 256637.9994 | 162.5 | 258837.9994 | 182.5 | 263137.9994 | 185 | 259137.9994 | 187.5 | 260337.9994 | 190.5 | 256837.9994 | 210 | 257937.9994 | 213 | 262337.9994 | 215.5 | 257937.9994 | 218.5 | 254037.9994 | 221.5 | 262237.9994 | 224 | 262437.9994 | 227 | 259937.9994 | 235.5 | 130868.9988 | 238 | 260537.9994 | 241 | 261037.9994 | 244 | 262337.9994 | 246.5 | 259937.9994 | 249.5 | 262937.9994 | 257.5 | 11.3942 | 266 | 10.1438 | 269 | 23.481 | 271.5 | 81.1864 | 274.5 | 198.5926 | 283 | 4.9172 | 285.5 | 5.757 | 288.5 | 21.8975 | 291.5 | 5.3803 | 294 | 4.2989 | 297 | 15.3173 | 299.5 | 29.6019 | 308 | 12.2703 | 311 | 30.1948 | 319.5 | 31.3862 | 322.5 | 27.5033 | 325 | 27.942 | 327.5 | 4.3276 | 330.5 | 6.5666 | 333.5 | 0.29832
336 | 260337.9994 | 339 | 260037.9994 | 342 | 258037.9994 | 344.5 | 256637.9994 | 347.5 | 258837.9994 | 367 | 263137.9994 | 369.5 | 259137.9994 | 372.5 | 260337.9994 | 375.5 | 256837.9994 | 395 | 128918.9988 | 397.5 | 262337.9994 | 400.5 | 257937.9994 | 403.5 | 126968.9988 | 406 | 405.1514 | 409 | 662.9818 | 411.5 | 132.5372 | 420 | 1229.5142 | 423 | 439.3283 | 425.5 | 6117.5458 | 428.5 | 176.8411 | 431.5 | 165.0183 | 434 | 237.6201 | 442.5 | 1.0593 | 451 | 26.6236 | 453.5 | 2.908 | 456.5 | 18.6026 | 459.5 | 5.6657 | 467.5 | 6.7239 | 470.5 | 30.8811 | 473.5 | 27.4594 | 476 | 9.7515 | 479 | 16.9951 | 481.5 | 2.2968 | 484.5 | 28.1048 | 493 | 28.3738 | 495.5 | 22.7703 | 504 | 17.0669 | 507 | 12.7719 | 509.5 | 1.8579 | 512.5 | 0.93335 | 515.5 | 1.0577 | 518 | 11.1901
521 | 90.029 | 523.5 | 803.0811 | 526.5 | 304.2155 | 529.5 | 190.8787 | 532 | 163.3542 | 551.5 | 32.4207 | 554.5 | 52.2722 | 557.5 | 30.864 | 560 | 48.7711 | 579.5 | 63.0515 | 582.5 | 33.8822 | 585.5 | 17.5314 | 588 | 16.2827 | 591 | 6.7002 | 593.5 | 5.8403 | 596.5 | 36.359 | 605 | 11.5866 | 607.5 | 14.8313 | 610.5 | 32.7264 | 613.5 | 18.2768 | 616 | 13.7845 | 619 | 32.7995 | 627.5 | 19.071 | 635.5 | 9580.9237 | 638.5 | 21.694 | 641.5 | 27.2258 | 644 | 6.0251 | 652.5 | 13.5466 | 655.5 | 11.835 | 658 | 33.2575 | 661 | 2.4095 | 663.5 | 0.46214 | 666.5 | 10.0723 | 669.5 | 12.5489 | 677.5 | 29.7388 | 680.5 | 26.3139 | 689 | 26.8158 | 691.5 | 17.5398 | 694.5 | 18.4064 | 697.5 | 2.051 | 700 | 1.7522 | 703 | 13.5622
705.5 | 6962.7129 | 708.5 | 23.9181 | 711.5 | 1.8128 | 714 | 30.7431 | 717 | 5.9718 | 736.5 | 19.0297 | 739.5 | 6.6877 | 742 | 4.6737 | 745 | 26.7313 | 764.5 | 15.1435 | 767.5 | 0.87071 | 770 | 0.92648 | 773 | 7.4603 | 775.5 | 15.5892 | 778.5 | 21.9569 | 781.5 | 21.4237 | 789.5 | 2.489 | 792.5 | 25.6389 | 795.5 | 0.28257 | 798 | 16.5377 | 801 | 15.9928 | 803.5 | 21.0882 | 812 | 6258.7287 | 820.5 | 23.7991 | 823.5 | 8.0772 | 826 | 20.5079 | 829 | 33.8575 | 837.5 | 10.5225 | 840 | 6.4309 | 843 | 15.4028 | 845.5 | 32.2059 | 848.5 | 5.8776 | 851.5 | 0.1992 | 854 | 3.6624 | 862.5 | 0.97432 | 865.5 | 0.518 | 873.5 | 9.234 | 876.5 | 24.046 | 879.5 | 11.2239 | 882 | 7.8609 | 885 | 0.54133 | 887.5 | 6.5349
890.5 | 2.438 | 893.5 | 15.2924 | 896 | 15.4553 | 899 | 0.67435 | 901.5 | 8.3258 | 921.5 | 15.3586 | 924 | 0.93678 | 927 | 17.8596 | 929.5 | 7.6185 | 949.5 | 2.918 | 952 | 27.7198 | 955 | 2.1096 | 957.5 | 1.0029 | 960.5 | 11.8086 | 963.5 | 19.1553 | 966 | 11.5067 | 974.5 | 13.9026 | 977.5 | 2.56 | 980 | 9.1634 | 983 | 0.46634 | 985.5 | 7.1132 | 988.5 | 29.3098 | 997 | 1466.8157 | 1005.5 | 29.2413 | 1008 | 4.6799 | 1011 | 3.7154 | 1013.5 | 2.7876 | 1022 | 12.4702 | 1025 | 2.9714 | 1027.5 | 25.0166 | 1030.5 | 3.2966 | 1033.5 | 0.96667 | 1036 | 27.1447 | 1039 | 6.6962 | 1047.5 | 1.7484 | 1050 | 0.72059 | 1058.5 | 0.22389 | 1061.5 | 18.2608 | 1064 | 22.344 | 1066.5 | 12.4874 | 1069.5 | 0.13232 | 1072.5 | 6.2101
1075.5 | 1.3541 | 1078 | 9.2146 | 1081 | 27.5231 | 1083.5 | 4.7016 | 1086.5 | 0.93421 | 1106 | 25.0415 | 1109 | 9.1654 | 1111.5 | 21.4368 | 1114.5 | 18.8716 | 1134 | 0.92648 | 1137 | 12.4488 | 1139.5 | 6.782 | 1143 | 12.0869 | 1145.5 | 13.7197 | 1148 | 31.3862 | 1151 | 16.2074 | 1159.5 | 15.8868 | 1162 | 13.3304 | 1165 | 29.2821 | 1167.5 | 4.6987 | 1170.5 | 17.1829 | 1173.5 | 31.301 | 1181.5 | 8.3544 | 1190 | 4.0235 | 1192.5 | 26.3854 | 1195.5 | 20.9648 | 1198.5 | 35.6495 | 1206.5 | 32.6756 | 1209.5 | 12.636 | 1212.5 | 27.0141 | 1215 | 13.8659 | 1218 | 25.6628 | 1220.5 | 0.63696 | 1223.5 | 6.0223 | 1232 | 29.0203 | 1235 | 0.9573 | 1243.5 | 19.0994 | 1246 | 0.69722 | 1249 | 14.9151 | 1251.5 | 22.4504 | 1254.5 | 15.5522 | 1257.5 | 10.2877
1260 | 7.7887 | 1263 | 21.0042 | 1265.5 | 21.1107 | 1268.5 | 17.3748 | 1271.5 | 0.61545 | 1291 | 13.249 | 1293.5 | 25.4557 | 1296.5 | 3.4154 | 1299 | 26.9891 | 1318.5 | 25.9363 | 1321.5 | 21.1546 | 1324.5 | 11.4819 | 1327.5 | 25.7839 | 1330 | 25.2844 | 1332.5 | 8.7164 | 1335.5 | 2.1942 | 1344 | 2.2798 | 1346.5 | 19.9144 | 1349.5 | 0.15922 | 1352.5 | 27.6558 | 1355.5 | 0.94363 | 1358 | 2.7577 | 1366.5 | 1976.6176 | 1374.5 | 9.7046 | 1377.5 | 23.0595 | 1380.5 | 36.1393 | 1383 | 18.9104 | 1391.5 | 38.5127 | 1394.5 | 19.5785 | 1397 | 30.2624 | 1400 | 13.4054 | 1402.5 | 24.7405 | 1405.5 | 13.807 | 1408.5 | 23.09 | 1416.5 | 12.8189 | 1419.5 | 21.1277 | 1428 | 18.5434 | 1430.5 | 9.2662 | 1433.5 | 10.882 | 1436.5 | 11.9825 | 1439.5 | 23.4445 | 1442 | 22.45
1444.5 | 1.4367 | 1447.5 | 6.4698 | 1450.5 | 24.9181 | 1453 | 27.2128 | 1456 | 10.5369 | 1475.5 | 16.3621 | 1478.5 | 5.1098 | 1481 | 26.9915 | 1484 | 1.6258 | 1503.5 | 4.4397 | 1506.5 | 18.8306 | 1509 | 18.8746 | 1512 | 21.2094 | 1514.5 | 23.6408 | 1517.5 | 24.0375 | 1520.5 | 4.8623 | 1528.5 | 12.8339 | 1531.5 | 29.2297 | 1534.5 | 12.1341 | 1537.5 | 27.0831 | 1540 | 13.527 | 1543 | 14.6969 | 1551 | 4.2987 | 1559.5 | 22.7637 | 1562.5 | 11.0989 | 1565 | 22.4733 | 1568 | 0.4203 | 1576.5 | 18.003 | 1579 | 15.2646 | 1582 | 32.0846 | 1584.5 | 10.0393 | 1587.5 | 12.9304 | 1590.5 | 4.7833 | 1593 | 10.8216 | 1601.5 | 1.0139 | 1604.5 | 7.1379 | 1612.5 | 0.96497 | 1615.5 | 6.2814 | 1618.5 | 8.1245 | 1621 | 9.8603 | 1624 | 17.0946 | 1626.5 | 8.8146
1629.5 | 0.94705 | 1632.5 | 5.7481 | 1635 | 11.127 | 1638 | 9.0537 | 1640.5 | 8.7517 | 1660.5 | 23.2307 | 1663 | 22.7014 | 1666 | 8.1614 | 1668.5 | 0.91701 | 1688.5 | 5.1052 | 1691 | 0.96412 | 1694 | 1.1886 | 1696.5 | 4.6498 | 1699.5 | 26.2785 | 1702.5 | 28.0255 | 1705 | 24.2972 | 1713.5 | 0.95986 | 1716.5 | 25.452 | 1719 | 5.9359 | 1722 | 6.246 | 1724.5 | 2.2362 | 1727.5 | 23.4939 | 1736 | 22.5702 | 1744.5 | 0.91959 | 1747 | 8.4521 | 1750 | 20.1108 | 1752.5 | 14.5192 | 1761 | 26.211 | 1764 | 28.6271 | 1766.5 | 6.0818 | 1769.5 | 18.0127 | 1772.5 | 0.13795 | 1775 | 1.383 | 1778 | 18.3871 | 1786.5 | 6.3795 | 1789 | 4.7675 | 1797.5 | 3.2339 | 1800.5 | 15.9615 | 1803 | 0.92318 | 1806 | 13.2017 | 1808.5 | 11.5919 | 1811.5 | 24.4292
1814.5 | 7.7887 | 1817 | 10.031 | 1820 | 25.859 | 1822.5 | 22.102 | 1825.5 | 19.6926 | 1845 | 9.0101 | 1848 | 25.3307 | 1850.5 | 6.4581 | 1853.5 | 24.2696 | 1873 | 7.5697 | 1876 | 23.869 | 1878.5 | 20.2479 | 1881.5 | 0.0052769 | 1884.5 | 3.8794 | 1887 | 18.5987 | 1890 | 23.024 | 1898.5 | 3.5902 | 1901 | 8.2456 | 1904 | 9.64 | 1906.5 | 18.775 | 1909.5 | 7.1592 | 1912.5 | 5.0289 | 1920.5 | 3.0394 | 1929 | 7.046 | 1932 | 6.7388 | 1934.5 | 10.0788 | 1937.5 | 5.4869 | 1946 | 12.2168 | 1948.5 | 18.2353 | 1951.5 | 7.1668 | 1954.5 | 3.0416 | 1957 | 17.2653 | 1960 | 1.6306 | 1962.5 | 7.1956 | 1971 | 4.9222 | 1974 | 25.4405 | 1982.5 | 28.8011 | 1985 | 17.4296 | 1988 | 21.6994 | 1990.5 | 3.5869 | 1993.5 | 0.026969 | 1996.5 | 10.5369
1999 | 10.9886 | 2002 | 6.5152 | 2004.5 | 12.4328 | 2007.5 | 0.055207 | 2010.5 | 14.9654 | 2030 | 13.249 | 2032.5 | 2.4221 | 2035.5 | 4.0192 | 2038.5 | 20.9517 | 2058 | 16.7066 | 2060.5 | 18.2768 | 2063.5 | 6.782 | 2066.5 | 4.8748 | 2069 | 26.4666 | 2072 | 9.6611 | 2074.5 | 13.2194 | 2083 | 10.0764 | 2086 | 0.94876 | 2088.5 | 18.0695 | 2091.5 | 14.7433 | 2094.5 | 26.9858 | 2097 | 0.097481 | 2105.5 | 24.2107 | 2114 | 9.9482 | 2116.5 | 5.3874 | 2119.5 | 3.3331 | 2122.5 | 15.3086 | 2130.5 | 1.0179 | 2133.5 | 3.0138 | 2136.5 | 27.8434 | 2139 | 11.5496 | 2142 | 3.8683 | 2144.5 | 19.7485 | 2147.5 | 2.1443 | 2156 | 18.9901 | 2158.5 | 32.6367 | 2167 | 179.2177 | 2170 | 155.7359 | 2172.5 | 238.036 | 2175.5 | 346.4025 | 2178.5 | 460.2668 | 2181 | 70.5057
2184 | 44.8394 | 2186.5 | 194.5044 | 2189.5 | 212.469 | 2192.5 | 156.0715 | 2195 | 183.1717 | 2214.5 | 166.3264 | 2217.5 | 82.6172 | 2220.5 | 313.88 | 2223 | 57.8667 | 2242.5 | 97.4537 | 2245.5 | 4119.9744 | 2248.5 | 5.5534 | 2251 | 22.1709 | 2254 | 17.7372 | 2256.5 | 31.5892 | 2259.5 | 2.4046 | 2268 | 15.8868 | 2270.5 | 18.729 | 2273.5 | 22.771 | 2276 | 23.7486 | 2279 | 29.9898 | 2282 | 287.7562 | 2290.5 | 41.9218 | 2298.5 | 14.7276 | 2301.5 | 53.6773 | 2304 | 61.4654 | 2307 | 105.7974 | 2315.5 | 25.714 | 2318.5 | 90.7872 | 2321 | 69.013 | 2323.5 | 91.8978 | 2326.5 | 3.4828 | 2329.5 | 11.8615 | 2332.5 | 76.3016 | 2340.5 | 86.1255 | 2343.5 | 79.3401 | 2352 | 34.6361 | 2354.5 | 56.3758 | 2357.5 | 199.2723 | 2360.5 | 77.0453 | 2363 | 139.361 | 2366 | 16.0413
2368.5 | 15.4411 | 2371.5 | 53.5087 | 2374 | 26.5689 | 2377 | 13.5676 | 2379.5 | 38.8105 | 2399.5 | 19.4119 | 2402.5 | 27.3691 | 2405 | 35.3014 | 2408 | 14.9846 | 2427.5 | 74.6752 | 2430.5 | 92.3596 | 2433 | 68.1617 | 2436 | 230.2051 | 2438.5 | 316.3602 | 2441.5 | 57.9051 | 2444.5 | 54.1051 | 2452.5 | 106.8416 | 2455.5 | 80.4619 | 2458 | 75.5041 | 2461 | 468.6465 | 2463.5 | 67.9137 | 2466.5 | 35.0425 | 2475 | 38.6972 | 2483.5 | 36.27 | 2486.5 | 80.8139 | 2489 | 33.8146 | 2491.5 | 58.1573 | 2500.5 | 69.675 | 2503 | 15.632 | 2506 | 84.7044 | 2508.5 | 27.1626 | 2511.5 | 70.1423 | 2514.5 | 236.9164 | 2517 | 177.248 | 2525.5 | 191.0157 | 2528.5 | 351.478 | 2536.5 | 13.8402 | 2539.5 | 82.8517 | 2542 | 161.0456 | 2545 | 115.9637 | 2548 | 128.8995 | 2550.5 | 73.5676
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!

## C-G Min
Minimum Conductor to Ground Resistances
Open Burn Test 8 |  |  | 2006-11-10 | 13:06
Mix | 7-C | Tray A | IRMS | 1
0 | 150 kW
Burner Time | A1-G |  | Burner Time | A2-G | Burner Time | B3-G | Burner Time | B4-G | Burner Time | C5-G | Burner Time | C6-G | Burner Time | D7-G | Burner Time | D8-G | Burner Time | E9-G | Burner Time | E10-G | Burner Time | F11-G | Burner Time | F12-G
-212.7 | 256638 |  | -190.4 | 256838 | -162.2222 | 254038 | -146.5556 | 257938 | -132.2778 | 256638 | -123.7222 | 256838 | -99.4 | 254038 | -93.9 | 261538 | -81.6667 | 257138 | -78.5 | 258738 | -60.8 | 253738 | -58.5 | 253738
-27.8 | 256638 |  | -5.3 | 256838 | 22.6111 | 254038 | 38.1667 | 258038 | 52.5 | 256638 | 61.2222 | 256838 | 85.3 | 254038 | 91 | 261538 | 103.2222 | 6.9922 | 106.2222 | 10.8514 | 124 | 1.6646 | 126.1 | 3.5934
157 | 130119 |  | 179.4 | 256838 | 207.3333 | 254038 | 222.9444 | 130869 | 237.1667 | 11.5516 | 245.8333 | 6.3995 | 270 | 5.8147 | 275.7 | 6.6848 | 287.9444 | 1.0712 | 291 | 1.4584 | 308.7 | 0.63612 | 311 | 0.77965
341.8 | 256638 |  | 364.1 | 130119 | 392.1111 | 133.2179 | 407.6667 | 165.6159 | 421.9444 | 2.5965 | 430.7222 | 4.8423 | 454.8 | 0.64871 | 460.4 | 24.0578 | 472.6667 | 0.6381 | 475.7222 | 0.63686 | 493.5 | 7.2607 | 495.7 | 3.4469
526.5 | 163.9531 |  | 548.9 | 32.068 | 576.8333 | 7.3336 | 592.4444 | 8.4713 | 606.8333 | 4.6496 | 615.5 | 2.5701 | 639.6 | 1.6959 | 645.2 | 12.3503 | 657.3889 | 1.1821 | 660.6667 | 2.3549 | 678.3 | 0.62903 | 680.5 | 3.4785
711.3 | 3.3379 |  | 733.7 | 6.1712 | 761.7222 | 0.63885 | 777.2778 | 1.8479 | 791.5556 | 7.9104 | 800.2778 | 5.0643 | 824.5 | 1.3734 | 830 | 0.62519 | 842.3333 | 5.4921 | 845.3889 | 0.63121 | 863 | 0.90027 | 865.3 | 4.5804
896.1 | 0.87937 |  | 918.5 | 0.63587 | 946.5556 | 2.5163 | 962.0556 | 2.0365 | 976.3889 | 4.309 | 985.0556 | 3.1769 | 1009.2 | 0.62735 | 1014.9 | 2.2823 | 1027.1111 | 0.63121 | 1030.1111 | 0.82136 | 1047.8 | 7.6497 | 1050 | 10.5085
1080.9 | 0.63661 |  | 1103.3 | 4.9307 | 1131.3333 | 0.63885 | 1146.8889 | 3.505 | 1161.0556 | 4.8913 | 1169.7222 | 1.7979 | 1194 | 0.9424 | 1199.6 | 0.63 | 1211.7778 | 0.87116 | 1214.9444 | 0.6339 | 1232.6 | 3.2422 | 1234.9 | 0.64948
1265.7 | 0.95049 |  | 1288 | 4.9307 | 1316 | 3.7248 | 1331.5 | 0.6339 | 1345.8333 | 4.973 | 1354.5556 | 1.9191 | 1378.7 | 13.292 | 1384.2 | 14.2279 | 1396.4444 | 10.355 | 1399.7222 | 0.63341 | 1417.3 | 0.676 | 1419.6 | 0.62855
1450.3 | 2.9806 |  | 1472.7 | 3.1465 | 1500.7222 | 2.6269 | 1516.3889 | 13.5383 | 1530.5556 | 0.6421 | 1539.2778 | 2.211 | 1563.5 | 0.63121 | 1569.1 | 0.62831 | 1581.3333 | 0.62783 | 1584.4444 | 2.2751 | 1602 | 3.037 | 1604.3 | 3.6997
1635.1 | 0.63292 |  | 1657.5 | 0.6416 | 1685.5556 | 0.62807 | 1701.0556 | 0.62927 | 1715.3889 | 0.64085 | 1724.0556 | 0.6381 | 1748.2 | 1.4432 | 1753.9 | 4.6821 | 1766.1111 | 0.66718 | 1769.1667 | 0.62807 | 1786.9 | 0.62519 | 1789 | 0.62976
1819.9 | 9.2441 |  | 1842.3 | 3.8015 | 1870.2778 | 0.63366 | 1885.8889 | 0.6386 | 1900.1111 | 1.5264 | 1908.8333 | 1.5081 | 1933 | 0.78657 | 1938.6 | 0.62807 | 1950.8889 | 3.5997 | 1954 | 0.62663 | 1971.6 | 4.1901 | 1974 | 0.62567
2004.7 | 1.5979 |  | 2027.1 | 3.9447 | 2055.1111 | 0.62615 | 2070.6111 | 0.63243 | 2084.9444 | 0.63292 | 2093.7222 | 1.2763 | 2117.8 | 0.88845 | 2123.4 | 15.9991 | 2135.6667 | 4.7273 | 2138.7222 | 2.6486 | 2156.5 | 7.8715 | 2158.7 | 13.3327
2189.5 | 16.7056 |  | 2211.9 | 11.9532 | 2239.8333 | 3.9321 | 2255.3889 | 17.2507 | 2269.7778 | 8.5801 | 2278.4444 | 12.7815 | 2302.6 | 14.9881 | 2308.1 | 18.7502 | 2320.3889 | 7.1146 | 2323.6667 | 31.3893 | 2341.2 | 71.6657 | 2343.4 | 106.913
2374.1 | 44.5753 |  | 2396.7 | 37.6392 | 2424.7222 | 83.8285 | 2440.1111 | 97.9825 | 2454.5 | 34.2253 | 2463.2222 | 42.554 | 2487.4 | 63.572 | 2493 | 127.443 | 2505.2222 | 43.1801 | 2508.3889 | 20.3949 | 2526 | 164.7678 | 2528.1 | 117.0315
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!

## F11-F12
Open Burn Test 8 |  |  | 2006-11-10 | 13:06 |  |  | Vs = |  | 154.9683 |  | R = | 100
Mix | 7-C | Tray A | IRMS | 1
0 | 150 kW |  | Bundle | Ch. 11 & 12 | Cable F | Odd -Even
Time-131 | N11 | N12 | Time-132 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R11-G | R12-G | R11-12
39031.543 | 1 | 0 | 39031.543 | 1 | 0 |  | -36 | 183 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253738 | 253738 | 253737.9994
39031.5452 | 2090 | 0 | 39031.5452 | 2155 | 0 |  | 148.5 | 367.5 | 127.5946 | 0 | 131.5629 | 0 | 1.2759 | 0 | 1.3156 | 0 | 1.2759 | 1.3156 | 21.4536 | 17.7903 | 20.1776
39031.5473 | 2493 | 0 | 39031.5473 | 2236 | 0 |  | 333.5 | 552.5 | 152.1978 | 0 | 136.5079 | 0 | 1.522 | 0 | 1.3651 | 0 | 1.522 | 1.3651 | 1.8203 | 13.5233 | 0.29832
39031.5494 | 2255 | 0 | 39031.5494 | 2295 | 0 |  | 518 | 737 | 137.6679 | 0 | 140.1099 | 0 | 1.3767 | 0 | 1.4011 | 0 | 1.3767 | 1.4011 | 12.5667 | 10.6048 | 11.1901
39031.5516 | 2209 | 0 | 39031.5516 | 2061 | 0 |  | 703 | 922 | 134.8596 | 0 | 125.8242 | 0 | 1.3486 | 0 | 1.2582 | 0 | 1.3486 | 1.2582 | 14.9108 | 23.1625 | 13.5622
39031.5537 | 2351 | 0 | 39031.5537 | 2284 | 0 |  | 887.5 | 1106.5 | 143.5287 | 0 | 139.4383 | 0 | 1.4353 | 0 | 1.3944 | 0 | 1.4353 | 1.3944 | 7.9702 | 11.1375 | 6.5349
39031.5558 | 2358 | 0 | 39031.5559 | 2297 | 0 |  | 1072.5 | 1291.5 | 143.956 | 0 | 140.232 | 0 | 1.4396 | 0 | 1.4023 | 0 | 1.4396 | 1.4023 | 7.6497 | 10.5085 | 6.2101
39031.558 | 2273 | 0 | 39031.558 | 2522 | 0 |  | 1257.5 | 1476.5 | 138.7668 | 0 | 153.9683 | 0 | 1.3877 | 0 | 1.5397 | 0 | 1.3877 | 1.5397 | 11.6753 | 0.64948 | 10.2877
39031.5601 | 2052 | 0 | 39031.5601 | 2048 | 0 |  | 1442 | 1661 | 125.2747 | 0 | 125.0305 | 0 | 1.2527 | 0 | 1.2503 | 0 | 1.2527 | 1.2503 | 23.7027 | 23.9443 | 22.45
39031.5623 | 2303 | 0 | 39031.5623 | 2027 | 0 |  | 1626.5 | 1845.5 | 140.5983 | 0 | 123.7485 | 0 | 1.406 | 0 | 1.2375 | 0 | 1.406 | 1.2375 | 10.2206 | 25.2284 | 8.8146
39031.5644 | 2020 | 0 | 39031.5644 | 2096 | 0 |  | 1811.5 | 2030.5 | 123.3211 | 0 | 127.9609 | 0 | 1.2332 | 0 | 1.2796 | 0 | 1.2332 | 1.2796 | 25.6624 | 21.1059 | 24.4292
39031.5665 | 2268 | 0 | 39031.5666 | 2497 | 0 |  | 1996.5 | 2215.5 | 138.4615 | 0 | 152.442 | 0 | 1.3846 | 0 | 1.5244 | 0 | 1.3846 | 1.5244 | 11.9215 | 1.6572 | 10.5369
39031.5687 | 2228 | 60 | 39031.5687 | 2182 | 61 |  | 2181 | 2400 | 136.0195 | 3.663 | 133.2112 | 3.7241 | 1.3602 | 0.03663 | 1.3321 | 0.037241 | 1.3236 | 1.2949 | 16.5723 | 20.3307 | 70.5057
39031.5708 | 1831 | 572 | 39031.5708 | 1844 | 632 |  | 2366 | 2585 | 111.7827 | 34.9206 | 112.5763 | 38.5836 | 1.1178 | 0.34921 | 1.1258 | 0.38584 | 0.76862 | 0.73993 | 71.6657 | 210.3369 | 16.0413
39031.573 | 1084 | 832 | 39031.573 | 1328 | 703 |  | 2550.5 | 2769.5 | 66.1783 | 50.7937 | 81.0745 | 42.9182 | 0.66178 | 0.50794 | 0.81074 | 0.42918 | 0.15385 | 0.38156 | 546.764 | 5943.8109 | 73.5676

## E10-F12
Open Burn Test 8 |  |  | 2006-11-10 | 13:06 |  |  | Vs = |  | 160.8291 |  | R = | 100
Mix | 7-C | Tray A | IRMS | 1
0 | 150 kW |  | Bundle | Ch. 10 & 12 | Cable E | Even - | Cable F |  | Even
Time-129 | N11 | N12 | Time-130 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R10-G | R12-G | R10-12
39031.543 | 1 | 0 | 39031.543 | 1 | 0 |  | -39 | 180 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263338 | 263338 | 263337.9994
39031.5451 | 2300 | 0 | 39031.5451 | 2543 | 0 |  | 145.5 | 364.5 | 140.4151 | 0 | 155.2503 | 0 | 1.4042 | 0 | 1.5525 | 0 | 1.4042 | 1.5525 | 14.5383 | 3.5934 | 13.1341
39031.5473 | 2438 | 0 | 39031.5473 | 2614 | 0 |  | 330.5 | 549.5 | 148.84 | 0 | 159.5849 | 0 | 1.4884 | 0 | 1.5958 | 0 | 1.4884 | 1.5958 | 8.055 | 0.77965 | 6.5666
39031.5494 | 2567 | 0 | 39031.5494 | 2345 | 0 |  | 515.5 | 734.5 | 156.7155 | 0 | 143.1624 | 0 | 1.5672 | 0 | 1.4316 | 0 | 1.5672 | 1.4316 | 2.6249 | 12.3403 | 1.0577
39031.5515 | 2550 | 0 | 39031.5516 | 2423 | 0 |  | 700 | 919 | 155.6777 | 0 | 147.9243 | 0 | 1.5568 | 0 | 1.4792 | 0 | 1.5568 | 1.4792 | 3.309 | 8.7239 | 1.7522
39031.5537 | 2607 | 0 | 39031.5537 | 2519 | 0 |  | 885 | 1104 | 159.1575 | 0 | 153.7851 | 0 | 1.5916 | 0 | 1.5379 | 0 | 1.5916 | 1.5379 | 1.0502 | 4.5804 | 0.54133
39031.5558 | 2590 | 0 | 39031.5558 | 2031 | 0 |  | 1069.5 | 1288.5 | 158.1197 | 0 | 123.9927 | 0 | 1.5812 | 0 | 1.2399 | 0 | 1.5812 | 1.2399 | 1.7135 | 29.7085 | 0.13232
39031.558 | 2253 | 0 | 39031.558 | 2172 | 0 |  | 1254.5 | 1473.5 | 137.5458 | 0 | 132.6007 | 0 | 1.3755 | 0 | 1.326 | 0 | 1.3755 | 1.326 | 16.9277 | 21.2882 | 15.5522
39031.5601 | 2112 | 0 | 39031.5601 | 2553 | 0 |  | 1439.5 | 1658.5 | 128.9377 | 0 | 155.8608 | 0 | 1.2894 | 0 | 1.5586 | 0 | 1.2894 | 1.5586 | 24.7339 | 3.1876 | 23.4445
39031.5622 | 2224 | 0 | 39031.5622 | 2137 | 0 |  | 1624 | 1843 | 135.7753 | 0 | 130.464 | 0 | 1.3578 | 0 | 1.3046 | 0 | 1.3578 | 1.3046 | 18.4523 | 23.2747 | 17.0946
39031.5644 | 2331 | 0 | 39031.5644 | 2080 | 0 |  | 1808.5 | 2027.5 | 142.3077 | 0 | 126.9841 | 0 | 1.4231 | 0 | 1.2698 | 0 | 1.4231 | 1.2698 | 13.015 | 26.6529 | 11.5919
39031.5665 | 2594 | 0 | 39031.5665 | 2618 | 0 |  | 1993.5 | 2212.5 | 158.3639 | 0 | 159.8291 | 0 | 1.5836 | 0 | 1.5983 | 0 | 1.5836 | 1.5983 | 1.5567 | 0.62567 | 0.026969
39031.5686 | 2169 | 26 | 39031.5687 | 1957 | 27 |  | 2178.5 | 2397.5 | 132.4176 | 1.5873 | 119.475 | 1.6484 | 1.3242 | 0.015873 | 1.1947 | 0.016484 | 1.3083 | 1.1783 | 22.4438 | 37.4305 | 460.2668
39031.5708 | 1507 | 421 | 39031.5708 | 1346 | 574 |  | 2363 | 2582 | 92.0024 | 25.7021 | 82.1734 | 35.0427 | 0.92002 | 0.25702 | 0.82173 | 0.35043 | 0.663 | 0.47131 | 112.7234 | 490.2714 | 139.361
39031.5729 | 1262 | 562 | 39031.5729 | 954 | 740 |  | 2548 | 2767 | 77.0452 | 34.3101 | 58.2418 | 45.177 | 0.77045 | 0.3431 | 0.58242 | 0.45177 | 0.42735 | 0.13065 | 179.0003 | 842.6883 | 128.8995

## E10-F11
Open Burn Test 8 |  |  | 2006-11-10 | 13:06 |  |  | Vs = |  | 158.0208 |  | R = | 100
Mix | 7-C | Tray A | IRMS | 1
0 | 150 kW |  | Bundle | Ch. 10 & 11 | Cable E | Even - | Cable F |  | Odd
Time-127 | N11 | N12 | Time-128 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R10-G | R11-G | R10-11
39031.5429 | 1 | 0 | 39031.543 | 1 | 0 |  | -42 | 177 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258738 | 258738 | 258737.9994
39031.5451 | 2335 | 0 | 39031.5451 | 2546 | 0 |  | 143 | 362 | 142.5519 | 0 | 155.4335 | 0 | 1.4255 | 0 | 1.5543 | 0 | 1.4255 | 1.5543 | 10.8514 | 1.6646 | 9.4259
39031.5472 | 2446 | 0 | 39031.5472 | 2209 | 0 |  | 327.5 | 546.5 | 149.3284 | 0 | 134.8596 | 0 | 1.4933 | 0 | 1.3486 | 0 | 1.4933 | 1.3486 | 5.8209 | 17.1743 | 4.3276
39031.5494 | 2572 | 0 | 39031.5494 | 2041 | 0 |  | 512.5 | 731.5 | 157.0208 | 0 | 124.6032 | 0 | 1.5702 | 0 | 1.246 | 0 | 1.5702 | 1.246 | 0.63686 | 26.8192 | 0.93335
39031.5515 | 2499 | 0 | 39031.5515 | 2034 | 0 |  | 697.5 | 916.5 | 152.5641 | 0 | 124.1758 | 0 | 1.5256 | 0 | 1.2418 | 0 | 1.5256 | 1.2418 | 3.5766 | 27.2557 | 2.051
39031.5536 | 2368 | 0 | 39031.5537 | 2111 | 0 |  | 882 | 1101 | 144.5665 | 0 | 128.8767 | 0 | 1.4457 | 0 | 1.2888 | 0 | 1.4457 | 1.2888 | 9.3066 | 22.6139 | 7.8609
39031.5558 | 2273 | 0 | 39031.5558 | 2286 | 0 |  | 1066.5 | 1285.5 | 138.7668 | 0 | 139.5604 | 0 | 1.3877 | 0 | 1.3956 | 0 | 1.3877 | 1.3956 | 13.8751 | 13.2275 | 12.4874
39031.5579 | 2092 | 0 | 39031.5579 | 2072 | 0 |  | 1251.5 | 1470.5 | 127.7167 | 0 | 126.4957 | 0 | 1.2772 | 0 | 1.265 | 0 | 1.2772 | 1.265 | 23.7275 | 24.9218 | 22.4504
39031.5601 | 2283 | 0 | 39031.5601 | 2571 | 0 |  | 1436.5 | 1655.5 | 139.3773 | 0 | 156.9597 | 0 | 1.3938 | 0 | 1.5696 | 0 | 1.3938 | 1.5696 | 13.3763 | 0.676 | 11.9825
39031.5622 | 2326 | 0 | 39031.5622 | 2385 | 0 |  | 1621 | 1840 | 142.0024 | 0 | 145.6044 | 0 | 1.42 | 0 | 1.456 | 0 | 1.42 | 1.456 | 11.2803 | 8.5275 | 9.8603
39031.5643 | 2259 | 0 | 39031.5644 | 2481 | 0 |  | 1806 | 2025 | 137.9121 | 0 | 151.4652 | 0 | 1.3791 | 0 | 1.5147 | 0 | 1.3791 | 1.5147 | 14.5808 | 4.3281 | 13.2017
39031.5665 | 2463 | 0 | 39031.5665 | 2336 | 0 |  | 1990.5 | 2209.5 | 150.3663 | 0 | 142.6129 | 0 | 1.5037 | 0 | 1.4261 | 0 | 1.5037 | 1.4261 | 5.0905 | 10.8039 | 3.5869
39031.5686 | 2148 | 27 | 39031.5686 | 2037 | 27 |  | 2175.5 | 2394.5 | 131.1355 | 1.6484 | 124.359 | 1.6484 | 1.3114 | 0.016484 | 1.2436 | 0.016484 | 1.2949 | 1.2271 | 21.7079 | 29.2413 | 346.4025
39031.5708 | 1790 | 326 | 39031.5708 | 1737 | 399 |  | 2360.5 | 2579.5 | 109.2796 | 19.9023 | 106.044 | 24.359 | 1.0928 | 0.19902 | 1.0604 | 0.24359 | 0.89377 | 0.81685 | 67.8387 | 113.5416 | 77.0453
39031.5729 | 1298 | 582 | 39031.5729 | 1015 | 693 |  | 2545 | 2764 | 79.243 | 35.5311 | 61.9658 | 42.3077 | 0.79243 | 0.35531 | 0.61966 | 0.42308 | 0.43712 | 0.19658 | 173.2371 | 2016.3837 | 115.9637

## E9-F12
Open Burn Test 8 |  |  | 2006-11-10 | 13:06 |  |  | Vs = |  | 160.0965 |  | R = | 100
Mix | 7-C | Tray A | IRMS | 1
0 | 150 kW |  | Bundle | Ch. 9 & 12 | Cable E | Odd - | Cable F |  | Even
Time-125 | N11 | N12 | Time-126 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R9-G | R12-G | R9-12
39031.5429 | 1 | 0 | 39031.5429 | 1 | 0 |  | -44.5 | 174.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262138 | 262138 | 262137.9994
39031.545 | 2451 | 0 | 39031.5451 | 2215 | 0 |  | 140 | 359 | 149.6337 | 0 | 135.2259 | 0 | 1.4963 | 0 | 1.3523 | 0 | 1.4963 | 1.3523 | 6.9922 | 18.3919 | 5.4959
39031.5472 | 2030 | 0 | 39031.5472 | 2583 | 0 |  | 325 | 544 | 123.9316 | 0 | 157.6923 | 0 | 1.2393 | 0 | 1.5769 | 0 | 1.2393 | 1.5769 | 29.1813 | 1.5246 | 27.942
39031.5493 | 2536 | 0 | 39031.5493 | 2535 | 0 |  | 509.5 | 728.5 | 154.823 | 0 | 154.7619 | 0 | 1.5482 | 0 | 1.5476 | 0 | 1.5482 | 1.5476 | 3.4062 | 3.4469 | 1.8579
39031.5515 | 2190 | 0 | 39031.5515 | 2240 | 0 |  | 694.5 | 913.5 | 133.6996 | 0 | 136.7521 | 0 | 1.337 | 0 | 1.3675 | 0 | 1.337 | 1.3675 | 19.7434 | 17.0705 | 18.4064
39031.5536 | 2328 | 0 | 39031.5536 | 2118 | 0 |  | 879.5 | 1098.5 | 142.1245 | 0 | 129.304 | 0 | 1.4212 | 0 | 1.293 | 0 | 1.4212 | 1.293 | 12.6452 | 23.814 | 11.2239
39031.5557 | 2121 | 0 | 39031.5558 | 2046 | 0 |  | 1064 | 1283 | 129.4872 | 0 | 124.9084 | 0 | 1.2949 | 0 | 1.2491 | 0 | 1.2949 | 1.2491 | 23.6388 | 28.1711 | 22.344
39031.5579 | 2255 | 0 | 39031.5579 | 2535 | 0 |  | 1249 | 1468 | 137.6679 | 0 | 154.7619 | 0 | 1.3767 | 0 | 1.5476 | 0 | 1.3767 | 1.5476 | 16.2918 | 3.4469 | 14.9151
39031.56 | 2335 | 0 | 39031.56 | 2606 | 0 |  | 1433.5 | 1652.5 | 142.5519 | 0 | 159.0965 | 0 | 1.4255 | 0 | 1.591 | 0 | 1.4255 | 1.591 | 12.3075 | 0.62855 | 10.882
39031.5622 | 2393 | 0 | 39031.5622 | 2072 | 0 |  | 1618.5 | 1837.5 | 146.0928 | 0 | 126.4957 | 0 | 1.4609 | 0 | 1.265 | 0 | 1.4609 | 1.265 | 9.5855 | 26.5627 | 8.1245
39031.5643 | 2605 | 0 | 39031.5643 | 2595 | 0 |  | 1803 | 2022 | 159.0354 | 0 | 158.4249 | 0 | 1.5904 | 0 | 1.5842 | 0 | 1.5904 | 1.5842 | 0.66718 | 1.0551 | 0.92318
39031.5664 | 2132 | 0 | 39031.5665 | 2021 | 0 |  | 1988 | 2207 | 130.1587 | 0 | 123.3822 | 0 | 1.3016 | 0 | 1.2338 | 0 | 1.3016 | 1.2338 | 23.0009 | 29.7566 | 21.6994
39031.5686 | 2134 | 23 | 39031.5686 | 2332 | 31 |  | 2172.5 | 2391.5 | 130.2808 | 1.4042 | 142.3687 | 1.8926 | 1.3028 | 0.014042 | 1.4237 | 0.018926 | 1.2888 | 1.4048 | 25.1938 | 13.3327 | 238.036
39031.5707 | 1809 | 229 | 39031.5707 | 1715 | 510 |  | 2357.5 | 2576.5 | 110.4396 | 13.9805 | 104.7009 | 31.1355 | 1.1044 | 0.1398 | 1.047 | 0.31136 | 0.96459 | 0.73565 | 53.6621 | 356.3816 | 199.2723
39031.5728 | 1214 | 529 | 39031.5729 | 1091 | 761 |  | 2542 | 2761 | 74.1148 | 32.2955 | 66.6056 | 46.4591 | 0.74115 | 0.32295 | 0.66606 | 0.46459 | 0.41819 | 0.20147 | 200.6113 | 3103.6949 | 161.0456

## E9-F11
Open Burn Test 8 |  |  | 2006-11-10 | 13:06 |  |  | Vs = |  | 158.2039 |  | R = | 100
Mix | 7-C | Tray A | IRMS | 1
0 | 150 kW |  | Bundle | Ch. 9 & 11 | Cable E | Odd - | Cable F |  | Odd
Time-123 | N11 | N12 | Time-124 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R9-G | R11-G | R9-11
39031.5429 | 1 | 0 | 39031.5429 | 1 | 0 |  | -47.5 | 171.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259038 | 259038 | 259037.9994
39031.545 | 2027 | 0 | 39031.545 | 2488 | 0 |  | 137.5 | 356.5 | 123.7485 | 0 | 151.8926 | 0 | 1.2375 | 0 | 1.5189 | 0 | 1.2375 | 1.5189 | 27.8431 | 4.1551 | 26.6056
39031.5472 | 2013 | 0 | 39031.5472 | 2575 | 0 |  | 322.5 | 541.5 | 122.8938 | 0 | 157.2039 | 0 | 1.2289 | 0 | 1.572 | 0 | 1.2289 | 1.572 | 28.7322 | 0.63612 | 27.5033
39031.5493 | 2270 | 0 | 39031.5493 | 2079 | 0 |  | 507 | 726 | 138.5836 | 0 | 126.9231 | 0 | 1.3858 | 0 | 1.2692 | 0 | 1.3858 | 1.2692 | 14.1577 | 24.6455 | 12.7719
39031.5514 | 2180 | 0 | 39031.5514 | 2276 | 0 |  | 691.5 | 910.5 | 133.0891 | 0 | 138.9499 | 0 | 1.3309 | 0 | 1.3895 | 0 | 1.3309 | 1.3895 | 18.8706 | 13.8568 | 17.5398
39031.5536 | 2068 | 0 | 39031.5536 | 2462 | 0 |  | 876.5 | 1095.5 | 126.2515 | 0 | 150.3053 | 0 | 1.2625 | 0 | 1.5031 | 0 | 1.2625 | 1.5031 | 25.3085 | 5.2551 | 24.046
39031.5557 | 2167 | 0 | 39031.5557 | 1982 | 0 |  | 1061.5 | 1280.5 | 132.2955 | 0 | 121.0012 | 0 | 1.323 | 0 | 1.21 | 0 | 1.323 | 1.21 | 19.5838 | 30.7457 | 18.2608
39031.5578 | 2569 | 0 | 39031.5579 | 2510 | 0 |  | 1246 | 1465 | 156.8376 | 0 | 153.2357 | 0 | 1.5684 | 0 | 1.5324 | 0 | 1.5684 | 1.5324 | 0.87116 | 3.2422 | 0.69722
39031.56 | 2341 | 0 | 39031.56 | 2033 | 0 |  | 1430.5 | 1649.5 | 142.9182 | 0 | 124.1148 | 0 | 1.4292 | 0 | 1.2411 | 0 | 1.4292 | 1.2411 | 10.6954 | 27.4658 | 9.2662
39031.5621 | 2405 | 0 | 39031.5621 | 2515 | 0 |  | 1615.5 | 1834.5 | 146.8254 | 0 | 153.5409 | 0 | 1.4683 | 0 | 1.5354 | 0 | 1.4683 | 1.5354 | 7.7497 | 3.037 | 6.2814
39031.5643 | 2209 | 0 | 39031.5643 | 2286 | 0 |  | 1800.5 | 2019.5 | 134.8596 | 0 | 139.5604 | 0 | 1.3486 | 0 | 1.3956 | 0 | 1.3486 | 1.3956 | 17.3101 | 13.3587 | 15.9615
39031.5664 | 2182 | 0 | 39031.5664 | 2337 | 0 |  | 1985 | 2204 | 133.2112 | 0 | 142.674 | 0 | 1.3321 | 0 | 1.4267 | 0 | 1.3321 | 1.4267 | 18.7617 | 10.8849 | 17.4296
39031.5685 | 2161 | 28 | 39031.5686 | 2327 | 28 |  | 2170 | 2389 | 131.9292 | 1.7094 | 142.0635 | 1.7094 | 1.3193 | 0.017094 | 1.4206 | 0.017094 | 1.3022 | 1.4035 | 22.6203 | 12.1542 | 155.7359
39031.5707 | 1930 | 373 | 39031.5707 | 1658 | 417 |  | 2354.5 | 2573.5 | 117.8266 | 22.7717 | 101.221 | 25.4579 | 1.1783 | 0.22772 | 1.0122 | 0.25458 | 0.95055 | 0.75763 | 46.6263 | 269.2526 | 56.3758
39031.5728 | 1269 | 697 | 39031.5728 | 915 | 714 |  | 2539.5 | 2758.5 | 77.4725 | 42.5519 | 55.8608 | 43.5897 | 0.77473 | 0.42552 | 0.55861 | 0.4359 | 0.34921 | 0.12271 | 209.9621 | 1205.4961 | 82.8517

## E9-E10
Open Burn Test 8 |  |  | 2006-11-10 | 13:06 |  |  | Vs = |  | 160.2796 |  | R = | 100
Mix | 7-C | Tray A | IRMS | 1
0 | 150 kW |  | Bundle | Ch. 9 & 10 | Cable E | Odd -Even
Time-121 | N11 | N12 | Time-122 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R9-G | R10-G | R9-10
39031.5428 | 1 | 0 | 39031.5429 | 1 | 0 |  | -50.5 | 168.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262438 | 262438 | 262437.9994
39031.545 | 2298 | 0 | 39031.545 | 2161 | 0 |  | 134.5 | 353.5 | 140.293 | 0 | 131.9292 | 0 | 1.4029 | 0 | 1.3193 | 0 | 1.4029 | 1.3193 | 14.2463 | 21.4891 | 12.8434
39031.5471 | 1980 | 0 | 39031.5471 | 2157 | 0 |  | 319.5 | 538.5 | 120.8791 | 0 | 131.685 | 0 | 1.2088 | 0 | 1.3168 | 0 | 1.2088 | 1.3168 | 32.5949 | 21.7144 | 31.3862
39031.5493 | 2217 | 0 | 39031.5493 | 2346 | 0 |  | 504 | 723 | 135.348 | 0 | 143.2234 | 0 | 1.3535 | 0 | 1.4322 | 0 | 1.3535 | 1.4322 | 18.4204 | 11.9088 | 17.0669
39031.5514 | 2050 | 0 | 39031.5514 | 2285 | 0 |  | 689 | 908 | 125.1526 | 0 | 139.4994 | 0 | 1.2515 | 0 | 1.395 | 0 | 1.2515 | 1.395 | 28.0673 | 14.8963 | 26.8158
39031.5535 | 2372 | 0 | 39031.5536 | 2166 | 0 |  | 873.5 | 1092.5 | 144.8107 | 0 | 132.2344 | 0 | 1.4481 | 0 | 1.3223 | 0 | 1.4481 | 1.3223 | 10.6821 | 21.2087 | 9.234
39031.5557 | 2579 | 0 | 39031.5557 | 2506 | 0 |  | 1058.5 | 1277.5 | 157.4481 | 0 | 152.9915 | 0 | 1.5745 | 0 | 1.5299 | 0 | 1.5745 | 1.5299 | 1.7984 | 4.7638 | 0.22389
39031.5578 | 2180 | 0 | 39031.5578 | 2102 | 0 |  | 1243.5 | 1462.5 | 133.0891 | 0 | 128.3272 | 0 | 1.3309 | 0 | 1.2833 | 0 | 1.3309 | 1.2833 | 20.4303 | 24.8991 | 19.0994
39031.56 | 2190 | 0 | 39031.56 | 2450 | 0 |  | 1428 | 1647 | 133.6996 | 0 | 149.5726 | 0 | 1.337 | 0 | 1.4957 | 0 | 1.337 | 1.4957 | 19.8804 | 7.1584 | 18.5434
39031.5621 | 2609 | 0 | 39031.5621 | 2481 | 0 |  | 1612.5 | 1831.5 | 159.2796 | 0 | 151.4652 | 0 | 1.5928 | 0 | 1.5147 | 0 | 1.5928 | 1.5147 | 0.62783 | 5.8194 | 0.96497
39031.5642 | 2506 | 0 | 39031.5642 | 2029 | 0 |  | 1797.5 | 2016.5 | 152.9915 | 0 | 123.8706 | 0 | 1.5299 | 0 | 1.2387 | 0 | 1.5299 | 1.2387 | 4.7638 | 29.3928 | 3.2339
39031.5664 | 2019 | 0 | 39031.5664 | 2412 | 0 |  | 1982.5 | 2201.5 | 123.2601 | 0 | 147.2527 | 0 | 1.2326 | 0 | 1.4725 | 0 | 1.2326 | 1.4725 | 30.0337 | 8.8466 | 28.8011
39031.5685 | 2220 | 37 | 39031.5685 | 2199 | 43 |  | 2167 | 2386 | 135.5311 | 2.2589 | 134.2491 | 2.6252 | 1.3553 | 0.022589 | 1.3425 | 0.026252 | 1.3327 | 1.3162 | 20.1236 | 21.9521 | 179.2177
39031.5706 | 1752 | 450 | 39031.5707 | 1925 | 450 |  | 2352 | 2571 | 106.9597 | 27.4725 | 117.5214 | 27.4725 | 1.0696 | 0.27473 | 1.1752 | 0.27473 | 0.79487 | 0.90049 | 164.9029 | 58.2625 | 34.6361
39031.5728 | 1445 | 989 | 39031.5728 | 1321 | 673 |  | 2536.5 | 2755.5 | 88.2173 | 60.3785 | 80.6471 | 41.0867 | 0.88217 | 0.60379 | 0.80647 | 0.41087 | 0.27839 | 0.3956 | 1897.0643 | 251.1564 | 13.8402

## D8-E10
Open Burn Test 8 |  |  | 2006-11-10 | 13:06 |  |  | Vs = |  | 159.7302 |  | R = | 100
Mix | 7-C | Tray A | IRMS | 1
0 | 150 kW |  | Bundle | Ch. 8 & 10 | Cable D | Even - | Cable E |  | Even
Time-115 | N11 | N12 | Time-116 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R8-G | R10-G | R8-10
39031.5428 | 1 | 0 | 39031.5428 | 1 | 0 |  | -58.5 | 160.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261538 | 261538 | 261537.9994
39031.5449 | 1 | 0 | 39031.5449 | 2274 | 0 |  | 126.5 | 345.5 | 0.06105 | 0 | 138.8278 | 0 | 0.0006105 | 0 | 1.3883 | 0 | 0.0006105 | 1.3883 | 261538 | 15.0563 | 261537.9994
39031.547 | 1991 | 0 | 39031.547 | 2109 | 0 |  | 311 | 530 | 121.5507 | 0 | 128.7546 | 0 | 1.2155 | 0 | 1.2875 | 0 | 1.2155 | 1.2875 | 31.4103 | 24.0578 | 30.1948
39031.5492 | 2109 | 0 | 39031.5492 | 2067 | 0 |  | 495.5 | 714.5 | 128.7546 | 0 | 126.1905 | 0 | 1.2875 | 0 | 1.2619 | 0 | 1.2875 | 1.2619 | 24.0578 | 26.5786 | 22.7703
39031.5513 | 2051 | 0 | 39031.5513 | 2503 | 0 |  | 680.5 | 899.5 | 125.2137 | 0 | 152.8083 | 0 | 1.2521 | 0 | 1.5281 | 0 | 1.2521 | 1.5281 | 27.5661 | 4.5298 | 26.3139
39031.5534 | 2563 | 0 | 39031.5535 | 2452 | 0 |  | 865.5 | 1084.5 | 156.4713 | 0 | 149.6947 | 0 | 1.5647 | 0 | 1.4969 | 0 | 1.5647 | 1.4969 | 2.0827 | 6.7039 | 0.518
39031.5556 | 2558 | 0 | 39031.5556 | 2009 | 0 |  | 1050 | 1269 | 156.1661 | 0 | 122.6496 | 0 | 1.5617 | 0 | 1.2265 | 0 | 1.5617 | 1.2265 | 2.2823 | 30.233 | 0.72059
39031.5577 | 2600 | 0 | 39031.5577 | 2029 | 0 |  | 1235 | 1454 | 158.7302 | 0 | 123.8706 | 0 | 1.5873 | 0 | 1.2387 | 0 | 1.5873 | 1.2387 | 0.63 | 28.9492 | 0.9573
39031.5599 | 2137 | 0 | 39031.5599 | 2149 | 0 |  | 1419.5 | 1638.5 | 130.464 | 0 | 131.1966 | 0 | 1.3046 | 0 | 1.312 | 0 | 1.3046 | 1.312 | 22.4324 | 21.7487 | 21.1277
39031.562 | 2409 | 0 | 39031.562 | 2013 | 0 |  | 1604.5 | 1823.5 | 147.0696 | 0 | 122.8938 | 0 | 1.4707 | 0 | 1.2289 | 0 | 1.4707 | 1.2289 | 8.6086 | 29.9742 | 7.1379
39031.5641 | 2462 | 0 | 39031.5642 | 2222 | 0 |  | 1789 | 2008 | 150.3053 | 0 | 135.6532 | 0 | 1.5031 | 0 | 1.3565 | 0 | 1.5031 | 1.3565 | 6.2705 | 17.7489 | 4.7675
39031.5663 | 2065 | 0 | 39031.5663 | 2221 | 0 |  | 1974 | 2193 | 126.0684 | 0 | 135.5922 | 0 | 1.2607 | 0 | 1.3559 | 0 | 1.2607 | 1.3559 | 26.7012 | 17.8019 | 25.4405
39031.5684 | 1955 | 0 | 39031.5684 | 2359 | 1 |  | 2158.5 | 2377.5 | 119.3529 | 0 | 144.0171 | 0.06105 | 1.1935 | 0 | 1.4402 | 0.0006105 | 1.1935 | 1.4396 | 33.8302 | 10.9576 | 32.6367
39031.5706 | 1334 | 431 | 39031.5706 | 1975 | 305 |  | 2343.5 | 2562.5 | 81.4408 | 26.3126 | 120.5739 | 18.6203 | 0.81441 | 0.26313 | 1.2057 | 0.1862 | 0.55128 | 1.0195 | 491.4786 | 67.1259 | 79.3401
39031.5727 | 1007 | 74 | 39031.5727 | 2175 | 8 |  | 2528.5 | 2747.5 | 61.4774 | 4.5177 | 132.7839 | 0.4884 | 0.61477 | 0.045177 | 1.3278 | 0.004884 | 0.5696 | 1.323 | 282.2658 | 20.3949 | 351.478

## D8-E9
Open Burn Test 8 |  |  | 2006-11-10 | 13:06 |  |  | Vs = |  | 160.9512 |  | R = | 100
Mix | 7-C | Tray A | IRMS | 1
0 | 150 kW |  | Bundle | Ch. 8 & 9 | Cable D | Even - | Cable E |  | Odd
Time-113 | N11 | N12 | Time-114 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R8-G | R9-G | R8-9
39031.5427 | 1 | 0 | 39031.5427 | 1 | 0 |  | -61.5 | 157.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263538 | 263538 | 263537.9994
39031.5449 | 1 | 0 | 39031.5449 | 1 | 0 |  | 123.5 | 342.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263538 | 263538 | 263537.9994
39031.547 | 2319 | 0 | 39031.547 | 2219 | 0 |  | 308 | 527 | 141.5751 | 0 | 135.4701 | 0 | 1.4158 | 0 | 1.3547 | 0 | 1.4158 | 1.3547 | 13.6861 | 18.8094 | 12.2703
39031.5491 | 2034 | 0 | 39031.5492 | 1984 | 0 |  | 493 | 712 | 124.1758 | 0 | 121.1233 | 0 | 1.2418 | 0 | 1.2112 | 0 | 1.2418 | 1.2112 | 29.6155 | 32.8821 | 28.3738
39031.5513 | 2013 | 0 | 39031.5513 | 2226 | 0 |  | 677.5 | 896.5 | 122.8938 | 0 | 135.8974 | 0 | 1.2289 | 0 | 1.359 | 0 | 1.2289 | 1.359 | 30.9677 | 18.4358 | 29.7388
39031.5534 | 2620 | 0 | 39031.5534 | 2090 | 0 |  | 862.5 | 1081.5 | 159.9512 | 0 | 127.5946 | 0 | 1.5995 | 0 | 1.2759 | 0 | 1.5995 | 1.2759 | 0.62519 | 26.1426 | 0.97432
39031.5556 | 2552 | 0 | 39031.5556 | 2060 | 0 |  | 1047.5 | 1266.5 | 155.7998 | 0 | 125.7631 | 0 | 1.558 | 0 | 1.2576 | 0 | 1.558 | 1.2576 | 3.3064 | 27.9796 | 1.7484
39031.5577 | 2024 | 0 | 39031.5577 | 2310 | 0 |  | 1232 | 1451 | 123.5653 | 0 | 141.0256 | 0 | 1.2357 | 0 | 1.4103 | 0 | 1.2357 | 1.4103 | 30.2559 | 14.129 | 29.0203
39031.5598 | 2308 | 0 | 39031.5598 | 2389 | 0 |  | 1416.5 | 1635.5 | 140.9035 | 0 | 145.8486 | 0 | 1.409 | 0 | 1.4585 | 0 | 1.409 | 1.4585 | 14.2279 | 10.355 | 12.8189
39031.562 | 2570 | 0 | 39031.562 | 2078 | 0 |  | 1601.5 | 1820.5 | 156.8987 | 0 | 126.862 | 0 | 1.569 | 0 | 1.2686 | 0 | 1.569 | 1.2686 | 2.5829 | 26.871 | 1.0139
39031.5641 | 2444 | 0 | 39031.5641 | 2491 | 0 |  | 1786.5 | 2005.5 | 149.2063 | 0 | 152.0757 | 0 | 1.4921 | 0 | 1.5208 | 0 | 1.4921 | 1.5208 | 7.8715 | 5.8362 | 6.3795
39031.5662 | 2477 | 0 | 39031.5663 | 2445 | 0 |  | 1971 | 2190 | 151.221 | 0 | 149.2674 | 0 | 1.5122 | 0 | 1.4927 | 0 | 1.5122 | 1.4927 | 6.4344 | 7.8274 | 4.9222
39031.5684 | 2191 | 0 | 39031.5684 | 2495 | 0 |  | 2156 | 2375 | 133.7607 | 0 | 152.3199 | 0 | 1.3376 | 0 | 1.5232 | 0 | 1.3376 | 1.5232 | 20.3277 | 5.6665 | 18.9901
39031.5705 | 1754 | 307 | 39031.5705 | 1716 | 284 |  | 2340.5 | 2559.5 | 107.0818 | 18.7424 | 104.7619 | 17.3382 | 1.0708 | 0.18742 | 1.0476 | 0.17338 | 0.88339 | 0.87424 | 81.2558 | 85.0246 | 86.1255
39031.5727 | 1154 | 322 | 39031.5727 | 1289 | 69 |  | 2525.5 | 2744.5 | 70.4518 | 19.6581 | 78.6935 | 4.2125 | 0.70452 | 0.19658 | 0.78694 | 0.042125 | 0.50794 | 0.74481 | 271.2394 | 112.7929 | 191.0157

## D7-E10
Open Burn Test 8 |  |  | 2006-11-10 | 13:06 |  |  | Vs = |  | 160.2186 |  | R = | 100
Mix | 7-C | Tray A | IRMS | 1
0 | 150 kW |  | Bundle | Ch. 7 & 10 | Cable D | Odd - | Cable E |  | Even
Time-107 | N11 | N12 | Time-108 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R7-G | R10-G | R7-10
39031.5426 | 1 | 0 | 39031.5426 | 1 | 0 |  | -69.5 | 149.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262338 | 262338 | 262337.9994
39031.5448 | 1 | 0 | 39031.5448 | 1 | 0 |  | 115 | 334 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262338 | 262338 | 262337.9994
39031.5469 | 2006 | 0 | 39031.5469 | 2475 | 0 |  | 299.5 | 518.5 | 122.4664 | 0 | 151.0989 | 0 | 1.2247 | 0 | 1.511 | 0 | 1.2247 | 1.511 | 30.8265 | 6.0356 | 29.6019
39031.549 | 2029 | 0 | 39031.5491 | 2280 | 0 |  | 484.5 | 703.5 | 123.8706 | 0 | 139.1941 | 0 | 1.2387 | 0 | 1.3919 | 0 | 1.2387 | 1.3919 | 29.3435 | 15.1044 | 28.1048
39031.5512 | 2303 | 0 | 39031.5512 | 2564 | 0 |  | 669.5 | 888.5 | 140.5983 | 0 | 156.5324 | 0 | 1.406 | 0 | 1.5653 | 0 | 1.406 | 1.5653 | 13.9548 | 2.3549 | 12.5489
39031.5533 | 2495 | 0 | 39031.5533 | 2195 | 0 |  | 854 | 1073 | 152.3199 | 0 | 134.0049 | 0 | 1.5232 | 0 | 1.34 | 0 | 1.5232 | 1.34 | 5.1856 | 19.5617 | 3.6624
39031.5555 | 2426 | 0 | 39031.5555 | 2603 | 0 |  | 1039 | 1258 | 148.1074 | 0 | 158.9133 | 0 | 1.4811 | 0 | 1.5891 | 0 | 1.4811 | 1.5891 | 8.1772 | 0.82136 | 6.6962
39031.5576 | 2441 | 0 | 39031.5576 | 2089 | 0 |  | 1223.5 | 1442.5 | 149.0232 | 0 | 127.5336 | 0 | 1.4902 | 0 | 1.2753 | 0 | 1.4902 | 1.2753 | 7.5125 | 25.6285 | 6.0223
39031.5597 | 2110 | 0 | 39031.5597 | 2031 | 0 |  | 1408.5 | 1627.5 | 128.8156 | 0 | 123.9927 | 0 | 1.2882 | 0 | 1.2399 | 0 | 1.2882 | 1.2399 | 24.3782 | 29.2161 | 23.09
39031.5619 | 2338 | 0 | 39031.5619 | 2566 | 0 |  | 1593 | 1812 | 142.735 | 0 | 156.6545 | 0 | 1.4274 | 0 | 1.5665 | 0 | 1.4274 | 1.5665 | 12.2489 | 2.2751 | 10.8216
39031.564 | 2192 | 0 | 39031.564 | 2608 | 0 |  | 1778 | 1997 | 133.8217 | 0 | 159.2186 | 0 | 1.3382 | 0 | 1.5922 | 0 | 1.3382 | 1.5922 | 19.7254 | 0.62807 | 18.3871
39031.5661 | 2415 | 0 | 39031.5662 | 2155 | 0 |  | 1962.5 | 2181.5 | 147.4359 | 0 | 131.5629 | 0 | 1.4744 | 0 | 1.3156 | 0 | 1.4744 | 1.3156 | 8.67 | 21.781 | 7.1956
39031.5683 | 2531 | 0 | 39031.5683 | 1954 | 0 |  | 2147.5 | 2366.5 | 154.5177 | 0 | 119.2918 | 0 | 1.5452 | 0 | 1.1929 | 0 | 1.5452 | 1.1929 | 3.6895 | 34.3081 | 2.1443
39031.5704 | 1518 | 349 | 39031.5704 | 1837 | 261 |  | 2332.5 | 2551.5 | 92.674 | 21.3065 | 112.149 | 15.9341 | 0.92674 | 0.21306 | 1.1215 | 0.15934 | 0.71368 | 0.96215 | 210.5841 | 54.2251 | 76.3016
39031.5726 | 945 | 346 | 39031.5726 | 1465 | 93 |  | 2517 | 2736 | 57.6923 | 21.1233 | 89.4383 | 5.6777 | 0.57692 | 0.21123 | 0.89438 | 0.056777 | 0.36569 | 0.83761 | 871.3556 | 85.1654 | 177.248

## D7-E9
Open Burn Test 8 |  |  | 2006-11-10 | 13:06 |  |  | Vs = |  | 159.4249 |  | R = | 100
Mix | 7-C | Tray A | IRMS | 1
0 | 150 kW |  | Bundle | Ch. 7 & 9 | Cable D | Odd - | Cable E |  | Odd
Time-105 | N11 | N12 | Time-106 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R7-G | R9-G | R7-9
39031.5426 | 1 | 0 | 39031.5426 | 1 | 0 |  | -72.5 | 146.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261038 | 261038 | 261037.9994
39031.5447 | 1 | 0 | 39031.5447 | 1 | 0 |  | 112.5 | 331.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261038 | 261038 | 261037.9994
39031.5469 | 2238 | 0 | 39031.5469 | 1991 | 0 |  | 297 | 516 | 136.63 | 0 | 121.5507 | 0 | 1.3663 | 0 | 1.2155 | 0 | 1.3663 | 1.2155 | 16.6836 | 31.1592 | 15.3173
39031.549 | 2515 | 0 | 39031.549 | 2237 | 0 |  | 481.5 | 700.5 | 153.5409 | 0 | 136.569 | 0 | 1.5354 | 0 | 1.3657 | 0 | 1.5354 | 1.3657 | 3.8322 | 16.7358 | 2.2968
39031.5511 | 2342 | 0 | 39031.5512 | 2176 | 0 |  | 666.5 | 885.5 | 142.9792 | 0 | 132.8449 | 0 | 1.4298 | 0 | 1.3284 | 0 | 1.4298 | 1.3284 | 11.5021 | 20.0083 | 10.0723
39031.5533 | 2576 | 0 | 39031.5533 | 2143 | 0 |  | 851.5 | 1070.5 | 157.265 | 0 | 130.8303 | 0 | 1.5726 | 0 | 1.3083 | 0 | 1.5726 | 1.3083 | 1.3734 | 21.8563 | 0.1992
39031.5554 | 2034 | 0 | 39031.5554 | 2595 | 0 |  | 1036 | 1255 | 124.1758 | 0 | 158.4249 | 0 | 1.2418 | 0 | 1.5842 | 0 | 1.2418 | 1.5842 | 28.3864 | 0.63121 | 27.1447
39031.5576 | 2587 | 0 | 39031.5576 | 2230 | 0 |  | 1220.5 | 1439.5 | 157.9365 | 0 | 136.1416 | 0 | 1.5794 | 0 | 1.3614 | 0 | 1.5794 | 1.3614 | 0.9424 | 17.1022 | 0.63696
39031.5597 | 2267 | 0 | 39031.5597 | 2301 | 0 |  | 1405.5 | 1624.5 | 138.4005 | 0 | 140.4762 | 0 | 1.384 | 0 | 1.4048 | 0 | 1.384 | 1.4048 | 15.191 | 13.4889 | 13.807
39031.5618 | 2457 | 0 | 39031.5619 | 2077 | 0 |  | 1590.5 | 1809.5 | 150 | 0 | 126.801 | 0 | 1.5 | 0 | 1.268 | 0 | 1.5 | 1.268 | 6.2833 | 25.7285 | 4.7833
39031.564 | 2537 | 0 | 39031.564 | 2391 | 0 |  | 1775 | 1994 | 154.884 | 0 | 145.9707 | 0 | 1.5488 | 0 | 1.4597 | 0 | 1.5488 | 1.4597 | 2.9318 | 9.2171 | 1.383
39031.5661 | 2531 | 0 | 39031.5661 | 2145 | 0 |  | 1960 | 2179 | 154.5177 | 0 | 130.9524 | 0 | 1.5452 | 0 | 1.3095 | 0 | 1.5452 | 1.3095 | 3.1758 | 21.7427 | 1.6306
39031.5683 | 2157 | 0 | 39031.5683 | 2227 | 0 |  | 2144.5 | 2363.5 | 131.685 | 0 | 135.9585 | 0 | 1.3168 | 0 | 1.3596 | 0 | 1.3168 | 1.3596 | 21.0654 | 17.26 | 19.7485
39031.5704 | 1951 | 517 | 39031.5704 | 1777 | 311 |  | 2329.5 | 2548.5 | 119.1087 | 31.5629 | 108.486 | 18.9866 | 1.1911 | 0.31563 | 1.0849 | 0.18987 | 0.87546 | 0.89499 | 88.9739 | 74.7345 | 11.8615
39031.5725 | 1283 | 150 | 39031.5725 | 1844 | 42 |  | 2514.5 | 2733.5 | 78.3272 | 9.1575 | 112.5763 | 2.5641 | 0.78327 | 0.091575 | 1.1258 | 0.025641 | 0.6917 | 1.1001 | 169.0873 | 43.1801 | 236.9164

## D7-D8
Open Burn Test 8 |  |  | 2006-11-10 | 13:06 |  |  | Vs = |  | 160.4017 |  | R = | 100
Mix | 7-C | Tray A | IRMS | 1
0 | 150 kW |  | Bundle | Ch. 7 & 8 | Cable D | Odd -Even
Time-103 | N11 | N12 | Time-104 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R7-G | R8-G | R7-8
39031.5426 | 1 | 0 | 39031.5426 | 1 | 0 |  | -75.5 | 143.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262638 | 262638 | 262637.9994
39031.5447 | 1 | 0 | 39031.5447 | 1 | 0 |  | 109.5 | 328.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262638 | 262638 | 262637.9994
39031.5468 | 2483 | 0 | 39031.5469 | 2086 | 0 |  | 294 | 513 | 151.5873 | 0 | 127.3504 | 0 | 1.5159 | 0 | 1.2735 | 0 | 1.5159 | 1.2735 | 5.8147 | 25.953 | 4.2989
39031.549 | 2220 | 0 | 39031.549 | 2100 | 0 |  | 479 | 698 | 135.5311 | 0 | 128.2051 | 0 | 1.3553 | 0 | 1.2821 | 0 | 1.3553 | 1.2821 | 18.3505 | 25.1133 | 16.9951
39031.5511 | 2575 | 0 | 39031.5511 | 2141 | 0 |  | 663.5 | 882.5 | 157.2039 | 0 | 130.7082 | 0 | 1.572 | 0 | 1.3071 | 0 | 1.572 | 1.3071 | 2.0342 | 22.7174 | 0.46214
39031.5533 | 2447 | 0 | 39031.5533 | 2262 | 0 |  | 848.5 | 1067.5 | 149.3895 | 0 | 138.0952 | 0 | 1.4939 | 0 | 1.381 | 0 | 1.4939 | 1.381 | 7.3715 | 16.153 | 5.8776
39031.5554 | 2611 | 0 | 39031.5554 | 2559 | 0 |  | 1033.5 | 1252.5 | 159.4017 | 0 | 156.2271 | 0 | 1.594 | 0 | 1.5623 | 0 | 1.594 | 1.5623 | 0.62735 | 2.6721 | 0.96667
39031.5575 | 2070 | 0 | 39031.5575 | 2326 | 0 |  | 1218 | 1437 | 126.3736 | 0 | 142.0024 | 0 | 1.2637 | 0 | 1.42 | 0 | 1.2637 | 1.42 | 26.9266 | 12.957 | 25.6628
39031.5597 | 2085 | 0 | 39031.5597 | 2255 | 0 |  | 1402.5 | 1621.5 | 127.2894 | 0 | 137.6679 | 0 | 1.2729 | 0 | 1.3767 | 0 | 1.2729 | 1.3767 | 26.0134 | 16.5135 | 24.7405
39031.5618 | 2298 | 0 | 39031.5618 | 2558 | 0 |  | 1587.5 | 1806.5 | 140.293 | 0 | 156.1661 | 0 | 1.4029 | 0 | 1.5617 | 0 | 1.4029 | 1.5617 | 14.3333 | 2.7123 | 12.9304
39031.5639 | 2590 | 0 | 39031.564 | 2391 | 0 |  | 1772.5 | 1991.5 | 158.1197 | 0 | 145.9707 | 0 | 1.5812 | 0 | 1.4597 | 0 | 1.5812 | 1.4597 | 1.4432 | 9.8862 | 0.13795
39031.5661 | 2215 | 0 | 39031.5661 | 2219 | 0 |  | 1957 | 2176 | 135.2259 | 0 | 135.4701 | 0 | 1.3523 | 0 | 1.3547 | 0 | 1.3523 | 1.3547 | 18.6176 | 18.4038 | 17.2653
39031.5682 | 2493 | 0 | 39031.5682 | 2265 | 0 |  | 2142 | 2361 | 152.1978 | 0 | 138.2784 | 0 | 1.522 | 0 | 1.3828 | 0 | 1.522 | 1.3828 | 5.3903 | 15.9991 | 3.8683
39031.5704 | 2199 | 388 | 39031.5704 | 1353 | 553 |  | 2326.5 | 2545.5 | 134.2491 | 23.6874 | 82.6007 | 33.7607 | 1.3425 | 0.23687 | 0.82601 | 0.33761 | 1.1056 | 0.4884 | 16.5885 | 50.2983 | 3.4828
39031.5725 | 1098 | 894 | 39031.5725 | 1009 | 903 |  | 2511.5 | 2730.5 | 67.033 | 54.5788 | 61.5995 | 55.1282 | 0.67033 | 0.54579 | 0.616 | 0.55128 | 0.12454 | 0.064713 | 708.5551 | 7547.5479 | 70.1423

## Raw IRMS Data
Time | DL1.V2000:B | DL1.V2001:B | DL1.V1500:B | Open Burn Test 8 |  |  | 2006-11-10 | 13:06
39031.5409 | 1 | 0 | 1 | Mix | 7-C | Tray A | IRMS | 1
39031.543 | 1 | 0 | 1 |  | 150 kW |  | Bundle
39031.5452 | 2 | 0 | 1
39031.5473 | 1 | 0 | 1
39031.5495 | 1161 | 723 | 1
39031.5516 | 2050 | 2 | 1
39031.5537 | 2505 | 0 | 1
39031.5559 | 2531 | 0 | 1
39031.558 | 2384 | 0 | 1
39031.5602 | 2529 | 0 | 1
39031.5623 | 2588 | 0 | 1
39031.5644 | 2384 | 0 | 1
39031.5666 | 2317 | 0 | 1
39031.5687 | 2308 | 57 | 1
39031.5708 | 1905 | 574 | 1
1
39031.5409 | 1 | 0 | 2
39031.5431 | 1 | 0 | 2
39031.5452 | 1 | 0 | 2
39031.5473 | 2 | 0 | 2
39031.5495 | 1227 | 864 | 2
39031.5516 | 1949 | 1 | 2
39031.5537 | 2040 | 0 | 2
39031.5559 | 2482 | 0 | 2
39031.558 | 2106 | 0 | 2
39031.5602 | 2273 | 0 | 2
39031.5623 | 2398 | 0 | 2
39031.5644 | 2509 | 0 | 2
39031.5666 | 2195 | 0 | 2
39031.5687 | 2383 | 76 | 2
39031.5709 | 1513 | 606 | 2
2
39031.5409 | 1 | 0 | 3
39031.5431 | 1 | 0 | 3
39031.5452 | 1 | 0 | 3
39031.5473 | 1 | 0 | 3
39031.5495 | 288 | 0 | 3
39031.5516 | 2078 | 0 | 3
39031.5538 | 2230 | 0 | 3
39031.5559 | 2351 | 0 | 3
39031.558 | 2127 | 0 | 3
39031.5602 | 2410 | 0 | 3
39031.5623 | 2426 | 0 | 3
39031.5645 | 2334 | 0 | 3
39031.5666 | 2409 | 0 | 3
39031.5687 | 2068 | 55 | 3
39031.5709 | 1425 | 547 | 3
3
39031.5409 | 1 | 0 | 4
39031.5431 | 1 | 0 | 4
39031.5452 | 1 | 0 | 4
39031.5474 | 1 | 0 | 4
39031.5495 | 1812 | 0 | 4
39031.5516 | 2357 | 0 | 4
39031.5538 | 2303 | 0 | 4
39031.5559 | 2581 | 0 | 4
39031.5581 | 2091 | 0 | 4
39031.5602 | 2454 | 0 | 4
39031.5623 | 2090 | 0 | 4
39031.5645 | 2585 | 0 | 4
39031.5666 | 2572 | 0 | 4
39031.5687 | 2071 | 52 | 4
39031.5709 | 1675 | 503 | 4
4
39031.541 | 1 | 0 | 5
39031.5431 | 1 | 0 | 5
39031.5452 | 1 | 0 | 5
39031.5474 | 1 | 0 | 5
39031.5495 | 638 | 0 | 5
39031.5517 | 2498 | 0 | 5
39031.5538 | 2210 | 0 | 5
39031.5559 | 2005 | 0 | 5
39031.5581 | 2109 | 0 | 5
39031.5602 | 2046 | 0 | 5
39031.5623 | 2294 | 0 | 5
39031.5645 | 2031 | 0 | 5
39031.5666 | 2268 | 0 | 5
39031.5688 | 2145 | 54 | 5
39031.5709 | 1832 | 534 | 5
5
39031.541 | 1 | 0 | 6
39031.5431 | 1 | 0 | 6
39031.5453 | 1 | 0 | 6
39031.5474 | 1 | 0 | 6
39031.5495 | 1741 | 0 | 6
39031.5517 | 2110 | 0 | 6
39031.5538 | 2037 | 0 | 6
39031.556 | 2196 | 0 | 6
39031.5581 | 2408 | 0 | 6
39031.5602 | 2199 | 0 | 6
39031.5624 | 2423 | 0 | 6
39031.5645 | 2565 | 0 | 6
39031.5666 | 2030 | 0 | 6
39031.5688 | 1896 | 54 | 6
39031.5709 | 1502 | 399 | 6
6
39031.541 | 1 | 0 | 7
39031.5431 | 1 | 0 | 7
39031.5453 | 1 | 0 | 7
39031.5474 | 1 | 0 | 7
39031.5496 | 881 | 0 | 7
39031.5517 | 1946 | 0 | 7
39031.5538 | 2545 | 0 | 7
39031.556 | 2418 | 0 | 7
39031.5581 | 2163 | 0 | 7
39031.5602 | 1999 | 0 | 7
39031.5624 | 2324 | 0 | 7
39031.5645 | 2081 | 0 | 7
39031.5667 | 2527 | 0 | 7
39031.5688 | 1869 | 44 | 7
39031.5709 | 1881 | 448 | 7
7
39031.541 | 1 | 0 | 8
39031.5432 | 1 | 0 | 8
39031.5453 | 1 | 0 | 8
39031.5474 | 2010 | 0 | 8
39031.5496 | 2188 | 0 | 8
39031.5517 | 2028 | 0 | 8
39031.5539 | 1927 | 0 | 8
39031.556 | 2112 | 0 | 8
39031.5581 | 1938 | 0 | 8
39031.5603 | 2551 | 0 | 8
39031.5624 | 2105 | 0 | 8
39031.5645 | 2194 | 0 | 8
39031.5667 | 2520 | 0 | 8
39031.5688 | 2317 | 59 | 8
39031.571 | 2047 | 291 | 8
8
39031.541 | 1 | 0 | 9
39031.5432 | 0 | 0 | 9
39031.5453 | 1 | 0 | 9
39031.5475 | 1 | 0 | 9
39031.5496 | 981 | 0 | 9
39031.5517 | 2410 | 0 | 9
39031.5539 | 2359 | 0 | 9
39031.556 | 2573 | 0 | 9
39031.5581 | 2565 | 0 | 9
39031.5603 | 2313 | 0 | 9
39031.5624 | 2350 | 0 | 9
39031.5646 | 2140 | 0 | 9
39031.5667 | 2226 | 0 | 9
39031.5688 | 2117 | 56 | 9
39031.571 | 1577 | 504 | 9
9
39031.5411 | 1 | 0 | 10
39031.5432 | 1 | 0 | 10
39031.5453 | 1 | 0 | 10
39031.5475 | 1927 | 0 | 10
39031.5496 | 2104 | 0 | 10
39031.5517 | 2043 | 0 | 10
39031.5539 | 2199 | 0 | 10
39031.556 | 2523 | 0 | 10
39031.5582 | 2384 | 0 | 10
39031.5603 | 2527 | 0 | 10
39031.5624 | 2559 | 0 | 10
39031.5646 | 2226 | 0 | 10
39031.5667 | 2388 | 0 | 10
39031.5689 | 2018 | 54 | 10
39031.571 | 1791 | 407 | 10
10
39031.5411 | 1 | 0 | 11
39031.5432 | 1 | 0 | 11
39031.5453 | 1 | 0 | 11
39031.5475 | 1 | 0 | 11
39031.5496 | 937 | 0 | 11
39031.5518 | 2257 | 0 | 11
39031.5539 | 2473 | 0 | 11
39031.556 | 2356 | 0 | 11
39031.5582 | 2255 | 0 | 11
39031.5603 | 2114 | 0 | 11
39031.5625 | 2055 | 0 | 11
39031.5646 | 2444 | 0 | 11
39031.5667 | 2604 | 0 | 11
39031.5689 | 1855 | 42 | 11
39031.571 | 1419 | 300 | 11
11
39031.5411 | 1 | 0 | 12
39031.5432 | 1 | 0 | 12
39031.5454 | 93 | 0 | 12
39031.5475 | 2006 | 0 | 12
39031.5496 | 1996 | 0 | 12
39031.5518 | 2133 | 0 | 12
39031.5539 | 2457 | 0 | 12
39031.5561 | 2270 | 0 | 12
39031.5582 | 2497 | 0 | 12
39031.5603 | 2394 | 0 | 12
39031.5625 | 2597 | 0 | 12
39031.5646 | 2578 | 0 | 12
39031.5667 | 2053 | 0 | 12
39031.5689 | 2007 | 40 | 12
39031.571 | 1655 | 316 | 12
12
39031.5411 | 1 | 0 | 13
39031.5432 | 1 | 0 | 13
39031.5454 | 1 | 0 | 13
39031.5475 | 2 | 0 | 13
39031.5497 | 1537 | 0 | 13
39031.5539 | 2435 | 0 | 13
39031.5561 | 2028 | 0 | 13
39031.5582 | 2567 | 0 | 13
39031.5603 | 2026 | 0 | 13
39031.5625 | 2546 | 0 | 13
39031.5646 | 2386 | 0 | 13
39031.5668 | 2600 | 0 | 13
39031.5689 | 2191 | 60 | 13
39031.571 | 1278 | 354 | 13
13
39031.5411 | 1 | 0 | 14
39031.5433 | 1 | 0 | 14
39031.5454 | 332 | 0 | 14
39031.5475 | 2563 | 0 | 14
39031.5497 | 2251 | 0 | 14
39031.5518 | 2528 | 0 | 14
39031.5539 | 2600 | 0 | 14
39031.5561 | 2181 | 0 | 14
39031.5582 | 2090 | 0 | 14
39031.5604 | 2282 | 0 | 14
39031.5625 | 2534 | 0 | 14
39031.5646 | 2105 | 0 | 14
39031.5668 | 2555 | 0 | 14
39031.5689 | 2020 | 58 | 14
39031.5711 | 1365 | 346 | 14
14
39031.5411 | 1 | 0 | 15
39031.5433 | 1 | 0 | 15
39031.5454 | 1 | 0 | 15
39031.5475 | 2 | 0 | 15
39031.5497 | 1724 | 0 | 15
39031.5518 | 2042 | 0 | 15
39031.554 | 2103 | 0 | 15
39031.5561 | 2519 | 0 | 15
39031.5582 | 2198 | 0 | 15
39031.5604 | 2370 | 0 | 15
39031.5625 | 2017 | 0 | 15
39031.5647 | 2071 | 0 | 15
39031.5668 | 2159 | 0 | 15
39031.5689 | 2311 | 81 | 15
39031.5711 | 1342 | 619 | 15
15
39031.5411 | 1 | 0 | 16
39031.5433 | 1 | 0 | 16
39031.5454 | 2409 | 0 | 16
39031.5476 | 2069 | 0 | 16
39031.5497 | 2334 | 0 | 16
39031.5518 | 2538 | 0 | 16
39031.554 | 2609 | 0 | 16
39031.5561 | 2330 | 0 | 16
39031.5583 | 2026 | 0 | 16
39031.5604 | 2215 | 0 | 16
39031.5625 | 2121 | 0 | 16
39031.5647 | 2272 | 0 | 16
39031.5668 | 2382 | 0 | 16
39031.5689 | 1910 | 66 | 16
39031.5711 | 2014 | 457 | 16
16
39031.5412 | 1 | 0 | 17
39031.5433 | 1 | 0 | 17
39031.5454 | 1 | 0 | 17
39031.5476 | 2 | 0 | 17
39031.5497 | 1448 | 0 | 17
39031.5519 | 2031 | 0 | 17
39031.554 | 2145 | 0 | 17
39031.5561 | 2033 | 0 | 17
39031.5583 | 2303 | 0 | 17
39031.5604 | 2065 | 0 | 17
39031.5625 | 2071 | 0 | 17
39031.5647 | 2093 | 0 | 17
39031.5668 | 2383 | 0 | 17
39031.569 | 1832 | 69 | 17
39031.5711 | 1573 | 617 | 17
17
39031.5412 | 1 | 0 | 18
39031.5433 | 1 | 0 | 18
39031.5455 | 2086 | 0 | 18
39031.5476 | 2126 | 0 | 18
39031.5497 | 2576 | 0 | 18
39031.5519 | 2397 | 0 | 18
39031.554 | 2264 | 0 | 18
39031.5561 | 2024 | 0 | 18
39031.5583 | 2092 | 0 | 18
39031.5604 | 2611 | 0 | 18
39031.5626 | 2185 | 0 | 18
39031.5647 | 2302 | 0 | 18
39031.5668 | 2611 | 0 | 18
39031.569 | 2201 | 83 | 18
39031.5711 | 1849 | 482 | 18
18
39031.5412 | 1 | 0 | 19
39031.5433 | 1 | 0 | 19
39031.5455 | 1 | 0 | 19
39031.5476 | 1 | 0 | 19
39031.5497 | 1552 | 0 | 19
39031.5519 | 2543 | 0 | 19
39031.554 | 2067 | 0 | 19
39031.5562 | 2029 | 0 | 19
39031.5583 | 2405 | 0 | 19
39031.5604 | 2130 | 0 | 19
39031.5626 | 2010 | 0 | 19
39031.5647 | 2591 | 0 | 19
39031.5669 | 2538 | 0 | 19
39031.569 | 1887 | 63 | 19
39031.5711 | 1437 | 383 | 19
19
39031.5412 | 1 | 0 | 20
39031.5433 | 1 | 0 | 20
39031.5455 | 2588 | 0 | 20
39031.5476 | 2564 | 0 | 20
39031.5498 | 2016 | 0 | 20
39031.5519 | 2362 | 0 | 20
39031.554 | 1992 | 0 | 20
39031.5562 | 2531 | 0 | 20
39031.5583 | 2090 | 0 | 20
39031.5605 | 2295 | 0 | 20
39031.5626 | 2215 | 0 | 20
39031.5647 | 2032 | 0 | 20
39031.5669 | 2162 | 0 | 20
39031.569 | 1844 | 61 | 20
39031.5712 | 1526 | 492 | 20
20
39031.5412 | 1 | 0 | 21
39031.5434 | 1 | 0 | 21
39031.5455 | 1 | 0 | 21
39031.5476 | 2 | 0 | 21
39031.5498 | 2029 | 0 | 21
39031.5519 | 2543 | 0 | 21
39031.5541 | 2563 | 0 | 21
39031.5562 | 2562 | 0 | 21
39031.5583 | 2046 | 0 | 21
39031.5605 | 2032 | 0 | 21
39031.5626 | 2106 | 0 | 21
39031.5648 | 2315 | 0 | 21
39031.5669 | 2495 | 0 | 21
39031.569 | 1853 | 68 | 21
39031.5712 | 1456 | 440 | 21
21
39031.5413 | 1 | 0 | 22
39031.5434 | 1 | 0 | 22
39031.5455 | 2588 | 0 | 22
39031.5477 | 2594 | 0 | 22
39031.5498 | 2110 | 0 | 22
39031.5519 | 2060 | 0 | 22
39031.5541 | 1989 | 0 | 22
39031.5562 | 2298 | 0 | 22
39031.5584 | 2542 | 0 | 22
39031.5605 | 2268 | 0 | 22
39031.5626 | 2380 | 0 | 22
39031.5648 | 2030 | 0 | 22
39031.5669 | 2406 | 0 | 22
39031.5691 | 1956 | 67 | 22
39031.5712 | 1799 | 733 | 22
22
39031.5413 | 1 | 0 | 23
39031.5434 | 1 | 0 | 23
39031.5455 | 1 | 0 | 23
39031.5477 | 1 | 0 | 23
39031.5498 | 1970 | 0 | 23
39031.552 | 2187 | 0 | 23
39031.5541 | 2255 | 0 | 23
39031.5562 | 2084 | 0 | 23
39031.5584 | 2296 | 0 | 23
39031.5605 | 2236 | 0 | 23
39031.5627 | 2114 | 0 | 23
39031.5648 | 2383 | 0 | 23
39031.5669 | 2296 | 0 | 23
39031.5691 | 1853 | 84 | 23
39031.5712 | 1797 | 632 | 23
23
39031.5413 | 1 | 0 | 24
39031.5434 | 1 | 0 | 24
39031.5456 | 1 | 0 | 24
39031.5477 | 1 | 0 | 24
39031.5498 | 1849 | 0 | 24
39031.552 | 2309 | 0 | 24
39031.5541 | 2003 | 0 | 24
39031.5563 | 2348 | 0 | 24
39031.5584 | 2487 | 0 | 24
39031.5605 | 2565 | 0 | 24
39031.5627 | 2396 | 0 | 24
39031.5648 | 2584 | 0 | 24
39031.5669 | 2616 | 0 | 24
39031.5691 | 2160 | 99 | 24
39031.5712 | 1699 | 572 | 24
24
39031.5413 | 1 | 0 | 25
39031.5434 | 1 | 0 | 25
39031.5456 | 1 | 0 | 25
39031.5477 | 1 | 0 | 25
39031.5498 | 1691 | 0 | 25
39031.552 | 2397 | 0 | 25
39031.5541 | 2576 | 0 | 25
39031.5563 | 2344 | 0 | 25
39031.5584 | 2046 | 0 | 25
39031.5605 | 2432 | 0 | 25
39031.5627 | 2091 | 0 | 25
39031.5648 | 2048 | 0 | 25
39031.567 | 2494 | 0 | 25
39031.5691 | 2243 | 108 | 25
39031.5712 | 1817 | 570 | 25
25
39031.5413 | 1 | 0 | 26
39031.5434 | 1 | 0 | 26
39031.5456 | 1 | 0 | 26
39031.5477 | 1 | 0 | 26
39031.5499 | 1715 | 0 | 26
39031.552 | 2052 | 0 | 26
39031.5541 | 2401 | 0 | 26
39031.5563 | 2285 | 0 | 26
39031.5584 | 2542 | 0 | 26
39031.5606 | 2072 | 0 | 26
39031.5627 | 2126 | 0 | 26
39031.5648 | 2240 | 0 | 26
39031.567 | 2549 | 0 | 26
39031.5691 | 1858 | 92 | 26
39031.5713 | 1601 | 674 | 26
26
39031.5413 | 1 | 0 | 27
39031.5435 | 1 | 0 | 27
39031.5456 | 1 | 0 | 27
39031.5477 | 1 | 0 | 27
39031.5499 | 1972 | 0 | 27
39031.552 | 2453 | 0 | 27
39031.5542 | 2185 | 0 | 27
39031.5563 | 2122 | 0 | 27
39031.5584 | 2482 | 0 | 27
39031.5606 | 2031 | 0 | 27
39031.5627 | 2376 | 0 | 27
39031.5648 | 2413 | 0 | 27
39031.567 | 2468 | 0 | 27
39031.5691 | 1778 | 83 | 27
39031.5713 | 1637 | 538 | 27
27
39031.5413 | 1 | 0 | 28
39031.5435 | 1 | 0 | 28
39031.5456 | 498 | 0 | 28
39031.5478 | 2170 | 0 | 28
39031.5499 | 2486 | 0 | 28
39031.552 | 2396 | 0 | 28
39031.5542 | 2023 | 0 | 28
39031.5563 | 2084 | 0 | 28
39031.5584 | 2481 | 0 | 28
39031.5606 | 2462 | 0 | 28
39031.5627 | 2432 | 0 | 28
39031.5649 | 2184 | 0 | 28
39031.567 | 2588 | 0 | 28
39031.5691 | 1775 | 83 | 28
39031.5713 | 1745 | 461 | 28
28
39031.5414 | 1 | 0 | 29
39031.5435 | 1 | 0 | 29
39031.5456 | 1 | 0 | 29
39031.5478 | 1 | 0 | 29
39031.5499 | 1715 | 0 | 29
39031.552 | 2008 | 0 | 29
39031.5542 | 2356 | 0 | 29
39031.5563 | 2138 | 0 | 29
39031.5585 | 2004 | 0 | 29
39031.5606 | 2491 | 0 | 29
39031.5627 | 2553 | 0 | 29
39031.5649 | 2047 | 0 | 29
39031.567 | 2102 | 0 | 29
39031.5692 | 2158 | 104 | 29
39031.5713 | 1650 | 616 | 29
29
39031.5435 | 1 | 0 | 30
39031.5456 | 374 | 0 | 30
39031.5478 | 2358 | 0 | 30
39031.5499 | 2505 | 0 | 30
39031.5521 | 2432 | 0 | 30
39031.5542 | 2342 | 0 | 30
39031.5563 | 2524 | 0 | 30
39031.5585 | 2521 | 0 | 30
39031.5606 | 2430 | 0 | 30
39031.5628 | 2022 | 0 | 30
39031.5649 | 2294 | 0 | 30
39031.567 | 2537 | 0 | 30
39031.5692 | 2174 | 111 | 30
39031.5713 | 2043 | 560 | 30
30
39031.5414 | 1 | 0 | 31
39031.5435 | 1 | 0 | 31
39031.5457 | 1 | 0 | 31
39031.5478 | 2 | 0 | 31
39031.5499 | 2076 | 0 | 31
39031.5521 | 2473 | 0 | 31
39031.5542 | 2224 | 0 | 31
39031.5564 | 2558 | 0 | 31
39031.5585 | 2320 | 0 | 31
39031.5606 | 2380 | 0 | 31
39031.5628 | 2498 | 0 | 31
39031.5649 | 2499 | 0 | 31
39031.567 | 2532 | 0 | 31
39031.5692 | 1909 | 91 | 31
39031.5713 | 1553 | 266 | 31
31
39031.5414 | 1 | 0 | 32
39031.5435 | 1 | 0 | 32
39031.5457 | 1280 | 0 | 32
39031.5478 | 2024 | 0 | 32
39031.55 | 2214 | 0 | 32
39031.5521 | 2254 | 0 | 32
39031.5542 | 2082 | 0 | 32
39031.5564 | 2542 | 0 | 32
39031.5585 | 2216 | 0 | 32
39031.5606 | 2605 | 0 | 32
39031.5628 | 2049 | 0 | 32
39031.5649 | 2317 | 0 | 32
39031.5692 | 2163 | 100 | 32
39031.5713 | 1642 | 345 | 32
32
39031.5414 | 1 | 0 | 33
39031.5436 | 1 | 0 | 33
39031.5457 | 1 | 0 | 33
39031.5478 | 1 | 0 | 33
39031.55 | 2008 | 0 | 33
39031.5521 | 2190 | 0 | 33
39031.5543 | 2397 | 0 | 33
39031.5564 | 2098 | 0 | 33
39031.5585 | 2115 | 0 | 33
39031.5607 | 2035 | 0 | 33
39031.5628 | 2306 | 0 | 33
39031.5649 | 2596 | 0 | 33
39031.5671 | 2144 | 0 | 33
39031.5692 | 1858 | 96 | 33
39031.5714 | 1514 | 351 | 33
33
39031.5414 | 1 | 0 | 34
39031.5436 | 1 | 0 | 34
39031.5457 | 2104 | 0 | 34
39031.5479 | 2575 | 0 | 34
39031.55 | 2551 | 0 | 34
39031.5521 | 2119 | 0 | 34
39031.5543 | 2580 | 0 | 34
39031.5564 | 2382 | 0 | 34
39031.5585 | 2129 | 0 | 34
39031.5607 | 2418 | 0 | 34
39031.5628 | 2463 | 0 | 34
39031.565 | 2043 | 0 | 34
39031.5671 | 2013 | 0 | 34
39031.5692 | 1860 | 109 | 34
39031.5714 | 1196 | 297 | 34
34
39031.5415 | 1 | 0 | 35
39031.5436 | 1 | 0 | 35
39031.5457 | 1 | 0 | 35
39031.5479 | 1 | 0 | 35
39031.55 | 1983 | 0 | 35
39031.5522 | 2119 | 0 | 35
39031.5543 | 2092 | 0 | 35
39031.5564 | 2354 | 0 | 35
39031.5586 | 2493 | 0 | 35
39031.5607 | 2389 | 0 | 35
39031.5628 | 2597 | 0 | 35
39031.565 | 2129 | 0 | 35
39031.5671 | 2570 | 0 | 35
39031.5693 | 2062 | 137 | 35
39031.5714 | 1436 | 705 | 35
35
39031.5415 | 1 | 0 | 36
39031.5436 | 1 | 0 | 36
39031.5458 | 2528 | 0 | 36
39031.5479 | 2179 | 0 | 36
39031.55 | 2227 | 0 | 36
39031.5522 | 2131 | 0 | 36
39031.5543 | 2154 | 0 | 36
39031.5564 | 2329 | 0 | 36
39031.5586 | 2520 | 0 | 36
39031.5607 | 2540 | 0 | 36
39031.5629 | 2044 | 0 | 36
39031.565 | 2080 | 0 | 36
39031.5671 | 2458 | 0 | 36
39031.5693 | 1944 | 133 | 36
39031.5714 | 1639 | 680 | 36
36
39031.5415 | 1 | 0 | 37
39031.5436 | 1 | 0 | 37
39031.5458 | 1 | 0 | 37
39031.5479 | 1 | 0 | 37
39031.55 | 2051 | 0 | 37
39031.5522 | 2174 | 0 | 37
39031.5543 | 2116 | 0 | 37
39031.5565 | 2069 | 0 | 37
39031.5586 | 2455 | 0 | 37
39031.5607 | 2357 | 0 | 37
39031.5629 | 2595 | 0 | 37
39031.565 | 2488 | 0 | 37
39031.5672 | 2570 | 0 | 37
39031.5693 | 2069 | 159 | 37
39031.5714 | 1131 | 654 | 37
37
39031.5415 | 1 | 0 | 38
39031.5436 | 1 | 0 | 38
39031.5458 | 2335 | 0 | 38
39031.5479 | 2558 | 0 | 38
39031.5501 | 2250 | 0 | 38
39031.5522 | 2184 | 0 | 38
39031.5543 | 2602 | 0 | 38
39031.5565 | 2022 | 0 | 38
39031.5586 | 2070 | 0 | 38
39031.5608 | 2559 | 0 | 38
39031.5629 | 2040 | 0 | 38
39031.565 | 2435 | 0 | 38
39031.5672 | 2123 | 0 | 38
39031.5693 | 2208 | 179 | 38
39031.5714 | 1485 | 566 | 38
38
39031.5415 | 1 | 0 | 39
39031.5437 | 1 | 0 | 39
39031.5458 | 1 | 0 | 39
39031.5479 | 1 | 0 | 39
39031.5501 | 2220 | 0 | 39
39031.5522 | 2205 | 0 | 39
39031.5544 | 2500 | 0 | 39
39031.5565 | 2468 | 0 | 39
39031.5586 | 2079 | 0 | 39
39031.5608 | 2311 | 0 | 39
39031.5629 | 2180 | 0 | 39
39031.565 | 2046 | 0 | 39
39031.5672 | 2559 | 0 | 39
39031.5693 | 1719 | 231 | 39
39031.5715 | 1249 | 644 | 39
39
39031.5415 | 1 | 0 | 40
39031.5437 | 1 | 0 | 40
39031.5458 | 2519 | 0 | 40
39031.548 | 2566 | 0 | 40
39031.5501 | 2148 | 0 | 40
39031.5522 | 2515 | 0 | 40
39031.5544 | 2514 | 0 | 40
39031.5565 | 2089 | 0 | 40
39031.5586 | 2049 | 0 | 40
39031.5608 | 2030 | 0 | 40
39031.5629 | 2382 | 0 | 40
39031.5651 | 2323 | 0 | 40
39031.5672 | 2363 | 0 | 40
39031.5693 | 1862 | 109 | 40
39031.5715 | 1120 | 642 | 40
40
39031.5416 | 1 | 0 | 41
39031.5437 | 1 | 0 | 41
39031.5458 | 1 | 0 | 41
39031.548 | 2 | 0 | 41
39031.5501 | 1839 | 0 | 41
39031.5522 | 2332 | 0 | 41
39031.5544 | 2455 | 0 | 41
39031.5565 | 2566 | 0 | 41
39031.5587 | 2548 | 0 | 41
39031.5608 | 2517 | 0 | 41
39031.5629 | 2558 | 0 | 41
39031.5651 | 2171 | 0 | 41
39031.5672 | 2253 | 0 | 41
39031.5694 | 1703 | 189 | 41
39031.5715 | 1198 | 559 | 41
41
39031.5416 | 1 | 0 | 42
39031.5437 | 1 | 0 | 42
39031.5458 | 2284 | 0 | 42
39031.548 | 2395 | 0 | 42
39031.5501 | 2269 | 0 | 42
39031.5523 | 2475 | 0 | 42
39031.5544 | 2446 | 0 | 42
39031.5565 | 2047 | 0 | 42
39031.5587 | 2110 | 0 | 42
39031.5608 | 2481 | 1 | 42
39031.563 | 2451 | 0 | 42
39031.5651 | 2598 | 0 | 42
39031.5672 | 2011 | 0 | 42
39031.5694 | 1878 | 63 | 42
39031.5715 | 1261 | 529 | 42
42
39031.5416 | 1 | 0 | 43
39031.5437 | 1 | 0 | 43
39031.5459 | 1 | 0 | 43
39031.548 | 2 | 0 | 43
39031.5501 | 2163 | 46 | 43
39031.5523 | 2215 | 0 | 43
39031.5544 | 2471 | 0 | 43
39031.5566 | 2564 | 0 | 43
39031.5587 | 2029 | 0 | 43
39031.5608 | 2436 | 0 | 43
39031.563 | 2421 | 0 | 43
39031.5651 | 2367 | 0 | 43
39031.5672 | 2186 | 0 | 43
39031.5694 | 1661 | 304 | 43
39031.5715 | 1469 | 617 | 43
43
39031.5416 | 1 | 0 | 44
39031.5437 | 0 | 0 | 44
39031.5459 | 1 | 0 | 44
39031.548 | 89 | 0 | 44
39031.5502 | 2396 | 46 | 44
39031.5523 | 2076 | 0 | 44
39031.5544 | 2117 | 0 | 44
39031.5566 | 2493 | 0 | 44
39031.5587 | 2504 | 0 | 44
39031.5608 | 2020 | 0 | 44
39031.563 | 2048 | 0 | 44
39031.5651 | 2504 | 0 | 44
39031.5673 | 2554 | 0 | 44
39031.5694 | 1680 | 335 | 44
39031.5715 | 1374 | 745 | 44
44
39031.5416 | 1 | 0 | 45
39031.5438 | 1 | 0 | 45
39031.5459 | 1 | 0 | 45
39031.548 | 1 | 0 | 45
39031.5502 | 1943 | 0 | 45
39031.5523 | 2562 | 0 | 45
39031.5544 | 2035 | 0 | 45
39031.5566 | 2305 | 0 | 45
39031.5587 | 2143 | 0 | 45
39031.5609 | 2184 | 0 | 45
39031.563 | 2608 | 0 | 45
39031.5651 | 2097 | 0 | 45
39031.5673 | 2194 | 0 | 45
39031.5694 | 2102 | 1 | 45
39031.5716 | 1202 | 707 | 45
45
39031.5416 | 1 | 0 | 46
39031.5438 | 1 | 0 | 46
39031.5459 | 47 | 0 | 46
39031.548 | 2304 | 0 | 46
39031.5502 | 2027 | 0 | 46
39031.5523 | 2432 | 0 | 46
39031.5545 | 2096 | 0 | 46
39031.5566 | 2502 | 0 | 46
39031.5587 | 2049 | 0 | 46
39031.5609 | 2538 | 0 | 46
39031.563 | 2382 | 0 | 46
39031.5652 | 2539 | 0 | 46
39031.5673 | 2105 | 0 | 46
39031.5694 | 2417 | 0 | 46
39031.5716 | 1669 | 604 | 46
46
39031.5417 | 1 | 0 | 47
39031.5438 | 1 | 0 | 47
39031.5459 | 1 | 0 | 47
39031.5481 | 1 | 0 | 47
39031.5502 | 2171 | 0 | 47
39031.5523 | 2564 | 0 | 47
39031.5545 | 2490 | 0 | 47
39031.5566 | 2384 | 0 | 47
39031.5588 | 2286 | 0 | 47
39031.5609 | 2147 | 0 | 47
39031.563 | 2512 | 0 | 47
39031.5652 | 2123 | 0 | 47
39031.5673 | 2384 | 0 | 47
39031.5695 | 2411 | 0 | 47
39031.5716 | 1150 | 677 | 47
47
39031.5417 | 1 | 0 | 48
39031.5438 | 1 | 0 | 48
39031.5459 | 45 | 0 | 48
39031.5481 | 2294 | 0 | 48
39031.5502 | 2477 | 0 | 48
39031.5524 | 2456 | 0 | 48
39031.5545 | 2029 | 0 | 48
39031.5566 | 2121 | 0 | 48
39031.5588 | 2510 | 0 | 48
39031.5609 | 2323 | 0 | 48
39031.5631 | 2453 | 0 | 48
39031.5652 | 2245 | 0 | 48
39031.5673 | 2528 | 0 | 48
39031.5695 | 1899 | 0 | 48
39031.5716 | 1419 | 548 | 48
48
39031.5417 | 1 | 0 | 49
39031.5438 | 1 | 0 | 49
39031.546 | 1 | 0 | 49
39031.5481 | 2 | 0 | 49
39031.5502 | 2161 | 0 | 49
39031.5524 | 2334 | 0 | 49
39031.5545 | 2479 | 0 | 49
39031.5588 | 2001 | 0 | 49
39031.5609 | 2075 | 0 | 49
39031.5631 | 2395 | 0 | 49
39031.5652 | 2503 | 0 | 49
39031.5673 | 2390 | 0 | 49
39031.5695 | 2059 | 0 | 49
39031.5716 | 1466 | 240 | 49
49
39031.5417 | 1 | 0 | 50
39031.5438 | 1 | 0 | 50
39031.546 | 2260 | 0 | 50
39031.5481 | 2525 | 0 | 50
39031.5503 | 2499 | 0 | 50
39031.5524 | 2064 | 0 | 50
39031.5545 | 2501 | 0 | 50
39031.5567 | 2054 | 0 | 50
39031.5588 | 2147 | 0 | 50
39031.5609 | 2179 | 0 | 50
39031.5631 | 2430 | 0 | 50
39031.5652 | 2215 | 0 | 50
39031.5674 | 2519 | 0 | 50
39031.5695 | 1885 | 0 | 50
39031.5716 | 1221 | 269 | 50
50
39031.5417 | 1 | 0 | 51
39031.5439 | 1 | 0 | 51
39031.546 | 1 | 0 | 51
39031.5481 | 519 | 0 | 51
39031.5503 | 2425 | 0 | 51
39031.5524 | 2243 | 0 | 51
39031.5545 | 2317 | 0 | 51
39031.5567 | 2279 | 0 | 51
39031.5588 | 2073 | 0 | 51
39031.561 | 2100 | 0 | 51
39031.5631 | 2057 | 0 | 51
39031.5652 | 2489 | 0 | 51
39031.5674 | 2054 | 0 | 51
39031.5695 | 2203 | 0 | 51
39031.5717 | 1354 | 191 | 51
51
39031.5417 | 1 | 0 | 52
39031.5439 | 1 | 0 | 52
39031.546 | 2459 | 0 | 52
39031.5481 | 1991 | 0 | 52
39031.5503 | 2335 | 0 | 52
39031.5524 | 2063 | 0 | 52
39031.5546 | 2553 | 0 | 52
39031.5567 | 2390 | 0 | 52
39031.5588 | 2287 | 0 | 52
39031.561 | 2607 | 0 | 52
39031.5631 | 2197 | 0 | 52
39031.5653 | 2177 | 0 | 52
39031.5674 | 2165 | 0 | 52
39031.5695 | 1952 | 0 | 52
39031.5717 | 1364 | 209 | 52
52
39031.5417 | 1 | 0 | 53
39031.5439 | 1 | 0 | 53
39031.546 | 1 | 0 | 53
39031.5482 | 344 | 0 | 53
39031.5503 | 2446 | 0 | 53
39031.5524 | 2130 | 0 | 53
39031.5546 | 2179 | 0 | 53
39031.5567 | 1980 | 0 | 53
39031.5589 | 2383 | 0 | 53
39031.561 | 2095 | 0 | 53
39031.5631 | 2031 | 0 | 53
39031.5653 | 2189 | 0 | 53
39031.5674 | 2363 | 0 | 53
39031.5695 | 1977 | 0 | 53
39031.5717 | 1723 | 528 | 53
53
39031.5418 | 1 | 0 | 54
39031.5439 | 1 | 0 | 54
39031.546 | 2228 | 0 | 54
39031.5482 | 1997 | 0 | 54
39031.5503 | 2062 | 0 | 54
39031.5525 | 2051 | 0 | 54
39031.5546 | 2011 | 0 | 54
39031.5567 | 2602 | 0 | 54
39031.5589 | 2187 | 0 | 54
39031.561 | 2609 | 0 | 54
39031.5631 | 2602 | 0 | 54
39031.5653 | 2293 | 0 | 54
39031.5674 | 2210 | 0 | 54
39031.5696 | 2451 | 0 | 54
39031.5717 | 1529 | 585 | 54
54
39031.5418 | 1 | 0 | 55
39031.5439 | 1 | 0 | 55
39031.5461 | 1 | 0 | 55
39031.5482 | 1115 | 0 | 55
39031.5503 | 1891 | 0 | 55
39031.5525 | 2119 | 0 | 55
39031.5546 | 2303 | 0 | 55
39031.5567 | 2212 | 0 | 55
39031.5589 | 2507 | 0 | 55
39031.561 | 2445 | 0 | 55
39031.5632 | 2071 | 0 | 55
39031.5653 | 2092 | 0 | 55
39031.5674 | 2269 | 0 | 55
39031.5696 | 2502 | 0 | 55
39031.5717 | 1263 | 687 | 55
55
39031.5418 | 1 | 0 | 56
39031.5439 | 1 | 0 | 56
39031.5461 | 2563 | 0 | 56
39031.5482 | 2380 | 0 | 56
39031.5503 | 2127 | 0 | 56
39031.5525 | 2162 | 0 | 56
39031.5546 | 2575 | 0 | 56
39031.5568 | 2584 | 0 | 56
39031.5589 | 2550 | 0 | 56
39031.561 | 2164 | 0 | 56
39031.5632 | 2484 | 0 | 56
39031.5653 | 2050 | 0 | 56
39031.5675 | 2107 | 0 | 56
39031.5696 | 1947 | 0 | 56
39031.5717 | 1413 | 500 | 56
56
39031.5418 | 1 | 0 | 57
39031.5439 | 1 | 0 | 57
39031.5461 | 2 | 0 | 57
39031.5482 | 1563 | 0 | 57
39031.5504 | 2027 | 0 | 57
39031.5525 | 2413 | 0 | 57
39031.5546 | 2216 | 0 | 57
39031.5568 | 2270 | 0 | 57
39031.5589 | 2522 | 0 | 57
39031.5611 | 2225 | 0 | 57
39031.5632 | 2239 | 0 | 57
39031.5653 | 2464 | 0 | 57
39031.5675 | 2294 | 0 | 57
39031.5696 | 2307 | 0 | 57
39031.5717 | 1354 | 684 | 57
57
39031.5418 | 1 | 0 | 58
39031.544 | 1 | 0 | 58
39031.5461 | 2101 | 0 | 58
39031.5482 | 2111 | 0 | 58
39031.5504 | 2089 | 0 | 58
39031.5525 | 2594 | 0 | 58
39031.5547 | 2114 | 0 | 58
39031.5568 | 2075 | 0 | 58
39031.5589 | 2300 | 0 | 58
39031.5611 | 2440 | 0 | 58
39031.5632 | 2025 | 0 | 58
39031.5653 | 2394 | 0 | 58
39031.5675 | 2442 | 0 | 58
39031.5696 | 1887 | 0 | 58
39031.5718 | 1281 | 637 | 58
58
39031.5418 | 1 | 0 | 59
39031.544 | 1 | 0 | 59
39031.5461 | 1 | 0 | 59
39031.5483 | 1383 | 0 | 59
39031.5504 | 2260 | 0 | 59
39031.5525 | 2249 | 0 | 59
39031.5547 | 2174 | 0 | 59
39031.5568 | 2228 | 0 | 59
39031.559 | 2583 | 0 | 59
39031.5611 | 2562 | 0 | 59
39031.5632 | 2474 | 0 | 59
39031.5654 | 2107 | 0 | 59
39031.5675 | 2208 | 0 | 59
39031.5696 | 2210 | 0 | 59
39031.5718 | 1410 | 613 | 59
59
39031.5419 | 1 | 0 | 60
39031.544 | 1 | 0 | 60
39031.5461 | 2221 | 0 | 60
39031.5483 | 2608 | 0 | 60
39031.5504 | 2171 | 0 | 60
39031.5526 | 2169 | 0 | 60
39031.5547 | 2490 | 0 | 60
39031.5568 | 2084 | 0 | 60
39031.559 | 2447 | 0 | 60
39031.5611 | 2101 | 0 | 60
39031.5632 | 2197 | 0 | 60
39031.5654 | 2229 | 0 | 60
39031.5675 | 2449 | 0 | 60
39031.5697 | 2374 | 1 | 60
39031.5718 | 1363 | 674 | 60
60
39031.5419 | 0 | 0 | 61
39031.544 | 1 | 0 | 61
39031.5462 | 2 | 0 | 61
39031.5483 | 197 | 0 | 61
39031.5504 | 2318 | 0 | 61
39031.5526 | 2518 | 0 | 61
39031.5547 | 2272 | 0 | 61
39031.5569 | 2234 | 0 | 61
39031.559 | 2523 | 0 | 61
39031.5611 | 2293 | 0 | 61
39031.5633 | 2603 | 0 | 61
39031.5654 | 2492 | 0 | 61
39031.5675 | 2349 | 0 | 61
39031.5697 | 2234 | 0 | 61
39031.5718 | 1057 | 681 | 61
61
39031.5419 | 1 | 0 | 62
39031.544 | 1 | 0 | 62
39031.5462 | 299 | 0 | 62
39031.5483 | 1982 | 0 | 62
39031.5505 | 2503 | 0 | 62
39031.5526 | 2053 | 0 | 62
39031.5547 | 2004 | 0 | 62
39031.5569 | 2449 | 0 | 62
39031.559 | 2167 | 0 | 62
39031.5611 | 2037 | 0 | 62
39031.5633 | 2182 | 0 | 62
39031.5654 | 2580 | 0 | 62
39031.5676 | 1984 | 0 | 62
39031.5697 | 2003 | 0 | 62
39031.5718 | 1634 | 506 | 62
62
39031.5419 | 1 | 0 | 63
39031.5441 | 1 | 0 | 63
39031.5462 | 1 | 0 | 63
39031.5483 | 483 | 0 | 63
39031.5505 | 2243 | 0 | 63
39031.5526 | 2054 | 0 | 63
39031.5547 | 2504 | 0 | 63
39031.5569 | 2272 | 0 | 63
39031.559 | 2150 | 0 | 63
39031.5612 | 1998 | 0 | 63
39031.5633 | 2057 | 0 | 63
39031.5654 | 2376 | 0 | 63
39031.5676 | 2590 | 0 | 63
39031.5697 | 2171 | 0 | 63
39031.5719 | 1187 | 481 | 63
63
39031.5419 | 1 | 0 | 64
39031.5441 | 1 | 0 | 64
39031.5462 | 854 | 0 | 64
39031.5483 | 2486 | 0 | 64
39031.5505 | 2511 | 0 | 64
39031.5526 | 2094 | 0 | 64
39031.5548 | 2418 | 0 | 64
39031.5569 | 2487 | 0 | 64
39031.559 | 2208 | 0 | 64
39031.5612 | 2550 | 0 | 64
39031.5633 | 2142 | 0 | 64
39031.5655 | 2309 | 0 | 64
39031.5676 | 2442 | 0 | 64
39031.5697 | 2311 | 0 | 64
39031.5719 | 1743 | 445 | 64
64
39031.5419 | 1 | 0 | 65
39031.5441 | 1 | 0 | 65
39031.5462 | 1 | 0 | 65
39031.5484 | 42 | 0 | 65
39031.5505 | 1950 | 0 | 65
39031.5526 | 2564 | 0 | 65
39031.5548 | 2361 | 0 | 65
39031.5569 | 2001 | 0 | 65
39031.5591 | 2575 | 0 | 65
39031.5612 | 2300 | 0 | 65
39031.5633 | 2431 | 0 | 65
39031.5655 | 2351 | 0 | 65
39031.5676 | 2187 | 0 | 65
39031.5697 | 2105 | 0 | 65
39031.5719 | 1449 | 395 | 65
65
39031.542 | 1 | 0 | 66
39031.5441 | 1 | 0 | 66
39031.5462 | 2051 | 0 | 66
39031.5484 | 2153 | 0 | 66
39031.5505 | 2080 | 0 | 66
39031.5527 | 2514 | 0 | 66
39031.5548 | 2578 | 0 | 66
39031.5569 | 2347 | 0 | 66
39031.5591 | 2305 | 0 | 66
39031.5612 | 2595 | 0 | 66
39031.5633 | 2195 | 0 | 66
39031.5655 | 2591 | 0 | 66
39031.5676 | 2085 | 0 | 66
39031.5698 | 2271 | 0 | 66
39031.5719 | 1693 | 181 | 66
66
39031.542 | 1 | 0 | 67
39031.5441 | 1 | 0 | 67
39031.5462 | 1 | 0 | 67
39031.5484 | 946 | 0 | 67
39031.5505 | 2194 | 0 | 67
39031.5527 | 2226 | 0 | 67
39031.5548 | 2572 | 0 | 67
39031.5569 | 2471 | 0 | 67
39031.5591 | 2036 | 0 | 67
39031.5612 | 2045 | 0 | 67
39031.5634 | 2436 | 0 | 67
39031.5655 | 2185 | 0 | 67
39031.5676 | 2260 | 0 | 67
39031.5698 | 2099 | 0 | 67
39031.5719 | 1433 | 174 | 67
67
39031.542 | 1 | 0 | 68
39031.5441 | 1 | 0 | 68
39031.5463 | 2147 | 0 | 68
39031.5484 | 2051 | 0 | 68
39031.5505 | 2151 | 0 | 68
39031.5527 | 2400 | 0 | 68
39031.5548 | 2563 | 0 | 68
39031.557 | 2281 | 0 | 68
39031.5591 | 2024 | 0 | 68
39031.5612 | 2091 | 0 | 68
39031.5634 | 2507 | 0 | 68
39031.5655 | 2608 | 0 | 68
39031.5677 | 2090 | 0 | 68
39031.5698 | 2210 | 0 | 68
39031.5719 | 1010 | 302 | 68
68
39031.542 | 1 | 0 | 69
39031.5441 | 1 | 0 | 69
39031.5463 | 1 | 0 | 69
39031.5484 | 979 | 0 | 69
39031.5506 | 2258 | 0 | 69
39031.5527 | 2216 | 0 | 69
39031.5548 | 2395 | 0 | 69
39031.557 | 2194 | 0 | 69
39031.5591 | 2584 | 0 | 69
39031.5612 | 2263 | 0 | 69
39031.5634 | 2506 | 0 | 69
39031.5655 | 2394 | 0 | 69
39031.5677 | 2028 | 0 | 69
39031.5698 | 1982 | 0 | 69
39031.5719 | 1172 | 728 | 69
69
39031.542 | 1 | 0 | 70
39031.5442 | 1 | 0 | 70
39031.5463 | 2530 | 0 | 70
39031.5484 | 2421 | 0 | 70
39031.5506 | 2570 | 0 | 70
39031.5527 | 2465 | 0 | 70
39031.5548 | 2552 | 0 | 70
39031.557 | 2067 | 0 | 70
39031.5591 | 2350 | 0 | 70
39031.5613 | 2045 | 0 | 70
39031.5634 | 2287 | 0 | 70
39031.5655 | 2333 | 0 | 70
39031.5677 | 2483 | 0 | 70
39031.5698 | 1951 | 0 | 70
39031.572 | 1724 | 608 | 70
70
39031.542 | 1 | 0 | 71
39031.5442 | 1 | 0 | 71
39031.5463 | 1 | 0 | 71
39031.5484 | 778 | 0 | 71
39031.5506 | 1963 | 0 | 71
39031.5527 | 2149 | 0 | 71
39031.5549 | 2015 | 0 | 71
39031.557 | 1985 | 0 | 71
39031.5591 | 2522 | 0 | 71
39031.5613 | 2266 | 0 | 71
39031.5634 | 2108 | 0 | 71
39031.5656 | 2469 | 0 | 71
39031.5677 | 2587 | 0 | 71
39031.5698 | 1939 | 53 | 71
39031.572 | 1408 | 868 | 71
71
39031.5421 | 1 | 0 | 72
39031.5442 | 1 | 0 | 72
39031.5463 | 2100 | 0 | 72
39031.5485 | 1982 | 0 | 72
39031.5506 | 2065 | 0 | 72
39031.5527 | 2075 | 0 | 72
39031.5549 | 2183 | 0 | 72
39031.557 | 2407 | 0 | 72
39031.5592 | 2028 | 0 | 72
39031.5613 | 2189 | 0 | 72
39031.5634 | 2173 | 0 | 72
39031.5656 | 2614 | 0 | 72
39031.5677 | 2117 | 0 | 72
39031.5699 | 2240 | 286 | 72
39031.572 | 1529 | 504 | 72
72
39031.5421 | 0 | 0 | 73
39031.5442 | 1 | 0 | 73
39031.5464 | 1 | 0 | 73
39031.5485 | 814 | 0 | 73
39031.5506 | 2467 | 0 | 73
39031.5528 | 2052 | 0 | 73
39031.5549 | 2082 | 0 | 73
39031.557 | 2349 | 0 | 73
39031.5592 | 2505 | 0 | 73
39031.5613 | 2305 | 0 | 73
39031.5635 | 2399 | 0 | 73
39031.5656 | 2409 | 0 | 73
39031.5677 | 2498 | 0 | 73
39031.5699 | 2017 | 363 | 73
39031.572 | 1245 | 779 | 73
73
39031.5421 | 1 | 0 | 74
39031.5442 | 26 | 0 | 74
39031.5464 | 2311 | 0 | 74
39031.5485 | 2387 | 0 | 74
39031.5506 | 2300 | 0 | 74
39031.5528 | 2559 | 0 | 74
39031.5549 | 2201 | 0 | 74
39031.5571 | 2555 | 0 | 74
39031.5592 | 2608 | 0 | 74
39031.5613 | 2048 | 0 | 74
39031.5635 | 2562 | 0 | 74
39031.5656 | 2407 | 0 | 74
39031.5678 | 2051 | 0 | 74
39031.5699 | 1698 | 324 | 74
39031.572 | 1240 | 616 | 74
74
39031.5421 | 1 | 0 | 75
39031.5442 | 1 | 0 | 75
39031.5464 | 1 | 0 | 75
39031.5485 | 1376 | 0 | 75
39031.5507 | 2495 | 0 | 75
39031.5528 | 2257 | 0 | 75
39031.5549 | 2476 | 0 | 75
39031.5571 | 1977 | 0 | 75
39031.5592 | 2527 | 0 | 75
39031.5614 | 2291 | 0 | 75
39031.5635 | 2406 | 0 | 75
39031.5656 | 2533 | 0 | 75
39031.5678 | 2319 | 0 | 75
39031.5699 | 1581 | 324 | 75
39031.572 | 1471 | 649 | 75
75
39031.5421 | 1 | 0 | 76
39031.5443 | 609 | 0 | 76
39031.5464 | 2356 | 0 | 76
39031.5485 | 2055 | 0 | 76
39031.5507 | 2285 | 0 | 76
39031.5528 | 2157 | 0 | 76
39031.555 | 2361 | 0 | 76
39031.5571 | 2198 | 0 | 76
39031.5592 | 2295 | 0 | 76
39031.5614 | 2505 | 0 | 76
39031.5635 | 2192 | 0 | 76
39031.5656 | 2594 | 0 | 76
39031.5678 | 2082 | 0 | 76
39031.5699 | 1629 | 355 | 76
39031.5721 | 1333 | 964 | 76
76
39031.5421 | 1 | 0 | 77
39031.5443 | 1 | 0 | 77
39031.5464 | 1529 | 900 | 77
39031.5486 | 2518 | 0 | 77
39031.5507 | 2146 | 0 | 77
39031.5528 | 2255 | 1 | 77
39031.555 | 2106 | 1 | 77
39031.5571 | 2353 | 0 | 77
39031.5592 | 2048 | 1 | 77
39031.5614 | 2442 | 0 | 77
39031.5635 | 2086 | 0 | 77
39031.5657 | 2471 | 0 | 77
39031.5678 | 2059 | 0 | 77
39031.5699 | 1588 | 346 | 77
39031.5721 | 1385 | 722 | 77
77
39031.5422 | 1 | 0 | 78
39031.5443 | 1 | 0 | 78
39031.5464 | 1454 | 758 | 78
39031.5486 | 1976 | 0 | 78
39031.5507 | 2042 | 0 | 78
39031.5528 | 2091 | 1 | 78
39031.555 | 2504 | 1 | 78
39031.5571 | 2450 | 0 | 78
39031.5593 | 2488 | 1 | 78
39031.5614 | 2195 | 0 | 78
39031.5635 | 2567 | 0 | 78
39031.5657 | 2545 | 0 | 78
39031.5678 | 1993 | 0 | 78
39031.57 | 2110 | 372 | 78
39031.5721 | 1513 | 672 | 78
78
39031.5422 | 1 | 0 | 79
39031.5443 | 1 | 0 | 79
39031.5464 | 1581 | 0 | 79
39031.5486 | 2109 | 0 | 79
39031.5507 | 2143 | 0 | 79
39031.5529 | 2217 | 0 | 79
39031.555 | 2019 | 0 | 79
39031.5571 | 1950 | 0 | 79
39031.5593 | 2387 | 0 | 79
39031.5614 | 2545 | 0 | 79
39031.5636 | 2279 | 0 | 79
39031.5657 | 2528 | 0 | 79
39031.5678 | 2222 | 0 | 79
39031.57 | 1950 | 266 | 79
39031.5721 | 1382 | 186 | 79
79
39031.5422 | 1 | 0 | 80
39031.5443 | 1 | 0 | 80
39031.5465 | 2244 | 0 | 80
39031.5486 | 2323 | 0 | 80
39031.5507 | 2405 | 0 | 80
39031.5529 | 2222 | 0 | 80
39031.555 | 2246 | 0 | 80
39031.5572 | 2312 | 0 | 80
39031.5593 | 2279 | 0 | 80
39031.5614 | 2466 | 0 | 80
39031.5636 | 2221 | 0 | 80
39031.5657 | 2571 | 0 | 80
39031.5678 | 2550 | 0 | 80
39031.57 | 1790 | 168 | 80
39031.5721 | 1127 | 247 | 80
80
39031.5422 | 0 | 0 | 81
39031.5443 | 1 | 0 | 81
39031.5465 | 2017 | 0 | 81
39031.5486 | 1961 | 0 | 81
39031.5508 | 1996 | 0 | 81
39031.5529 | 2467 | 0 | 81
39031.555 | 2199 | 0 | 81
39031.5572 | 2117 | 0 | 81
39031.5593 | 2219 | 0 | 81
39031.5614 | 2116 | 0 | 81
39031.5636 | 2084 | 0 | 81
39031.5657 | 2467 | 0 | 81
39031.5679 | 1982 | 0 | 81
39031.57 | 1985 | 102 | 81
39031.5721 | 1622 | 114 | 81
81
39031.5422 | 1 | 0 | 82
39031.5444 | 1 | 0 | 82
39031.5465 | 2205 | 0 | 82
39031.5486 | 2013 | 0 | 82
39031.5508 | 2242 | 0 | 82
39031.5529 | 2144 | 0 | 82
39031.555 | 2347 | 0 | 82
39031.5572 | 2599 | 0 | 82
39031.5593 | 2165 | 0 | 82
39031.5615 | 2118 | 0 | 82
39031.5636 | 2142 | 0 | 82
39031.5657 | 2204 | 0 | 82
39031.5679 | 2587 | 0 | 82
39031.57 | 1934 | 210 | 82
39031.5722 | 960 | 173 | 82
82
39031.5422 | 1 | 0 | 83
39031.5444 | 1 | 0 | 83
39031.5465 | 2306 | 0 | 83
39031.5486 | 2012 | 0 | 83
39031.5508 | 2130 | 1 | 83
39031.5529 | 2057 | 0 | 83
39031.5551 | 1972 | 0 | 83
39031.5572 | 2438 | 0 | 83
39031.5593 | 2315 | 0 | 83
39031.5615 | 2074 | 0 | 83
39031.5636 | 2556 | 0 | 83
39031.5658 | 2371 | 0 | 83
39031.5679 | 2310 | 0 | 83
39031.57 | 1990 | 417 | 83
39031.5722 | 1535 | 576 | 83
83
39031.5422 | 1 | 0 | 84
39031.5444 | 1 | 0 | 84
39031.5465 | 2218 | 0 | 84
39031.5487 | 2258 | 0 | 84
39031.5508 | 2014 | 0 | 84
39031.5529 | 2341 | 0 | 84
39031.5551 | 2428 | 0 | 84
39031.5572 | 2369 | 0 | 84
39031.5594 | 2285 | 0 | 84
39031.5615 | 2403 | 0 | 84
39031.5636 | 2168 | 0 | 84
39031.5658 | 2483 | 0 | 84
39031.5679 | 2107 | 0 | 84
39031.57 | 1826 | 226 | 84
39031.5722 | 1579 | 302 | 84
84
39031.5423 | 1 | 0 | 85
39031.5444 | 1 | 0 | 85
39031.5465 | 2086 | 0 | 85
39031.5487 | 2492 | 0 | 85
39031.5508 | 2116 | 0 | 85
39031.553 | 2376 | 0 | 85
39031.5551 | 2451 | 0 | 85
39031.5572 | 2039 | 0 | 85
39031.5594 | 2093 | 0 | 85
39031.5615 | 2313 | 0 | 85
39031.5636 | 2368 | 0 | 85
39031.5658 | 2405 | 0 | 85
39031.5679 | 2435 | 0 | 85
39031.5701 | 1850 | 286 | 85
39031.5722 | 1342 | 533 | 85
85
39031.5423 | 1 | 0 | 86
39031.5444 | 1 | 0 | 86
39031.5466 | 2340 | 0 | 86
39031.5487 | 2326 | 0 | 86
39031.5508 | 2169 | 0 | 86
39031.553 | 2085 | 0 | 86
39031.5551 | 2104 | 0 | 86
39031.5572 | 2320 | 0 | 86
39031.5594 | 2586 | 0 | 86
39031.5615 | 2422 | 0 | 86
39031.5637 | 2108 | 0 | 86
39031.5658 | 2540 | 0 | 86
39031.5679 | 2314 | 0 | 86
39031.5701 | 2015 | 355 | 86
39031.5722 | 1534 | 591 | 86
86
39031.5423 | 1 | 0 | 87
39031.5444 | 1 | 0 | 87
39031.5466 | 1448 | 0 | 87
39031.5487 | 2198 | 0 | 87
39031.5509 | 2052 | 0 | 87
39031.553 | 2164 | 0 | 87
39031.5551 | 2505 | 0 | 87
39031.5573 | 2156 | 0 | 87
39031.5594 | 1920 | 0 | 87
39031.5615 | 2130 | 0 | 87
39031.5637 | 2171 | 0 | 87
39031.5658 | 2364 | 0 | 87
39031.568 | 2514 | 0 | 87
39031.5701 | 2083 | 302 | 87
39031.5722 | 1840 | 516 | 87
87
39031.5423 | 1 | 0 | 88
39031.5445 | 1792 | 0 | 88
39031.5466 | 2575 | 0 | 88
39031.5487 | 2277 | 0 | 88
39031.5509 | 2422 | 0 | 88
39031.553 | 2425 | 0 | 88
39031.5552 | 2445 | 0 | 88
39031.5573 | 2454 | 0 | 88
39031.5594 | 2481 | 0 | 88
39031.5616 | 2274 | 0 | 88
39031.5637 | 2620 | 0 | 88
39031.5658 | 2201 | 0 | 88
39031.568 | 2444 | 0 | 88
39031.5701 | 1825 | 382 | 88
39031.5723 | 998 | 652 | 88
88
39031.5423 | 1 | 0 | 89
39031.5445 | 1 | 0 | 89
39031.5466 | 869 | 0 | 89
39031.5488 | 2426 | 0 | 89
39031.5509 | 2418 | 0 | 89
39031.553 | 1925 | 0 | 89
39031.5552 | 2492 | 0 | 89
39031.5573 | 1900 | 0 | 89
39031.5594 | 2162 | 0 | 89
39031.5616 | 2549 | 0 | 89
39031.5637 | 2243 | 0 | 89
39031.5659 | 2430 | 0 | 89
39031.568 | 2228 | 0 | 89
39031.5701 | 1975 | 292 | 89
39031.5723 | 1800 | 399 | 89
89
39031.5423 | 1 | 0 | 90
39031.5445 | 1540 | 0 | 90
39031.5466 | 2124 | 0 | 90
39031.5488 | 2021 | 0 | 90
39031.5509 | 2512 | 0 | 90
39031.553 | 2080 | 0 | 90
39031.5552 | 1992 | 0 | 90
39031.5573 | 2491 | 0 | 90
39031.5595 | 2583 | 0 | 90
39031.5616 | 2210 | 0 | 90
39031.5637 | 2116 | 0 | 90
39031.5659 | 2131 | 0 | 90
39031.568 | 1989 | 0 | 90
39031.5702 | 1676 | 468 | 90
39031.5723 | 1005 | 694 | 90
90
39031.5424 | 1 | 0 | 91
39031.5445 | 1 | 0 | 91
39031.5466 | 2141 | 0 | 91
39031.5488 | 2435 | 0 | 91
39031.5509 | 2318 | 0 | 91
39031.5531 | 2092 | 0 | 91
39031.5552 | 2511 | 0 | 91
39031.5573 | 2278 | 0 | 91
39031.5595 | 1929 | 0 | 91
39031.5616 | 2106 | 0 | 91
39031.5638 | 2050 | 0 | 91
39031.5659 | 2350 | 0 | 91
39031.568 | 2144 | 0 | 91
39031.5702 | 1503 | 360 | 91
39031.5723 | 1733 | 131 | 91
91
39031.5424 | 1 | 0 | 92
39031.5445 | 1 | 0 | 92
39031.5467 | 2013 | 0 | 92
39031.5488 | 2187 | 0 | 92
39031.5509 | 2359 | 0 | 92
39031.5531 | 2182 | 0 | 92
39031.5552 | 2153 | 0 | 92
39031.5573 | 2043 | 0 | 92
39031.5595 | 2243 | 0 | 92
39031.5616 | 2042 | 0 | 92
39031.5638 | 2450 | 0 | 92
39031.5659 | 2612 | 0 | 92
39031.568 | 2088 | 0 | 92
39031.5702 | 1552 | 192 | 92
39031.5723 | 1438 | 69 | 92
92
39031.5424 | 1 | 0 | 93
39031.5445 | 1 | 0 | 93
39031.5467 | 2127 | 0 | 93
39031.5488 | 2470 | 0 | 93
39031.5509 | 2469 | 0 | 93
39031.5531 | 2482 | 0 | 93
39031.5552 | 2149 | 0 | 93
39031.5574 | 2448 | 0 | 93
39031.5595 | 2290 | 0 | 93
39031.5616 | 2268 | 0 | 93
39031.5638 | 2438 | 0 | 93
39031.5659 | 2576 | 0 | 93
39031.5681 | 2215 | 0 | 93
39031.5702 | 1798 | 173 | 93
39031.5723 | 1583 | 133 | 93
93
39031.5424 | 1 | 0 | 94
39031.5445 | 1 | 0 | 94
39031.5467 | 2473 | 0 | 94
39031.5488 | 2535 | 0 | 94
39031.551 | 2436 | 0 | 94
39031.5531 | 2598 | 0 | 94
39031.5552 | 2393 | 0 | 94
39031.5574 | 2150 | 0 | 94
39031.5595 | 2567 | 0 | 94
39031.5617 | 2535 | 0 | 94
39031.5638 | 2271 | 0 | 94
39031.5659 | 2187 | 0 | 94
39031.5681 | 2470 | 0 | 94
39031.5702 | 1676 | 321 | 94
39031.5723 | 954 | 225 | 94
94
39031.5424 | 1 | 0 | 95
39031.5446 | 1 | 0 | 95
39031.5467 | 2428 | 0 | 95
39031.5488 | 2388 | 0 | 95
39031.551 | 2248 | 0 | 95
39031.5531 | 2308 | 0 | 95
39031.5553 | 2269 | 0 | 95
39031.5574 | 1930 | 0 | 95
39031.5595 | 1850 | 0 | 95
39031.5617 | 2165 | 0 | 95
39031.5638 | 2027 | 0 | 95
39031.5659 | 2274 | 0 | 95
39031.5681 | 2519 | 0 | 95
39031.5702 | 2040 | 393 | 95
39031.5724 | 1372 | 609 | 95
95
39031.5424 | 1 | 0 | 96
39031.5446 | 1 | 0 | 96
39031.5467 | 2556 | 0 | 96
39031.5489 | 2567 | 0 | 96
39031.551 | 2097 | 0 | 96
39031.5531 | 2334 | 0 | 96
39031.5553 | 2372 | 0 | 96
39031.5574 | 2194 | 0 | 96
39031.5595 | 2138 | 0 | 96
39031.5617 | 2156 | 0 | 96
39031.5638 | 2180 | 0 | 96
39031.566 | 2214 | 0 | 96
39031.5681 | 2107 | 0 | 96
39031.5702 | 1574 | 294 | 96
39031.5724 | 1857 | 588 | 96
96
39031.5425 | 1 | 0 | 97
39031.5446 | 1 | 0 | 97
39031.5467 | 2435 | 0 | 97
39031.5489 | 1977 | 0 | 97
39031.551 | 2306 | 0 | 97
39031.5531 | 2420 | 0 | 97
39031.5553 | 2499 | 0 | 97
39031.5574 | 2290 | 0 | 97
39031.5596 | 2160 | 0 | 97
39031.5617 | 2239 | 0 | 97
39031.5638 | 2011 | 0 | 97
39031.566 | 2184 | 0 | 97
39031.5681 | 2498 | 0 | 97
39031.5703 | 1964 | 227 | 97
39031.5724 | 1783 | 680 | 97
97
39031.5425 | 1 | 0 | 98
39031.5446 | 1 | 0 | 98
39031.5467 | 2083 | 0 | 98
39031.5489 | 2561 | 0 | 98
39031.551 | 2094 | 0 | 98
39031.5532 | 2595 | 0 | 98
39031.5553 | 2508 | 0 | 98
39031.5574 | 2245 | 0 | 98
39031.5596 | 2141 | 0 | 98
39031.5617 | 2506 | 0 | 98
39031.5639 | 2341 | 0 | 98
39031.566 | 2180 | 0 | 98
39031.5681 | 2544 | 0 | 98
39031.5703 | 2047 | 440 | 98
39031.5724 | 1446 | 718 | 98
98
39031.5425 | 1 | 0 | 99
39031.5446 | 1 | 0 | 99
39031.5468 | 2127 | 0 | 99
39031.5489 | 2036 | 0 | 99
39031.551 | 1949 | 0 | 99
39031.5532 | 2244 | 0 | 99
39031.5553 | 2075 | 0 | 99
39031.5575 | 2043 | 0 | 99
39031.5596 | 1993 | 0 | 99
39031.5617 | 1966 | 0 | 99
39031.5639 | 2436 | 0 | 99
39031.566 | 2412 | 0 | 99
39031.5682 | 2030 | 0 | 99
39031.5703 | 2145 | 269 | 99
39031.5724 | 1449 | 587 | 99
99
39031.5425 | 1 | 0 | 100
39031.5447 | 2536 | 0 | 100
39031.5468 | 2388 | 0 | 100
39031.5489 | 2443 | 0 | 100
39031.5511 | 2604 | 0 | 100
39031.5532 | 2597 | 0 | 100
39031.5553 | 2063 | 0 | 100
39031.5575 | 2106 | 0 | 100
39031.5596 | 2557 | 0 | 100
39031.5618 | 2063 | 0 | 100
39031.5639 | 2565 | 0 | 100
39031.566 | 2515 | 0 | 100
39031.5682 | 2322 | 0 | 100
39031.5703 | 1571 | 337 | 100
39031.5725 | 1075 | 738 | 100
100
39031.5425 | 1 | 0 | 101
39031.5447 | 1 | 0 | 101
39031.5468 | 2449 | 0 | 101
39031.5489 | 2354 | 0 | 101
39031.5511 | 2518 | 0 | 101
39031.5532 | 1962 | 0 | 101
39031.5554 | 2497 | 0 | 101
39031.5575 | 2271 | 0 | 101
39031.5596 | 2280 | 0 | 101
39031.5618 | 2348 | 0 | 101
39031.5639 | 2193 | 0 | 101
39031.5661 | 2503 | 0 | 101
39031.5682 | 2317 | 0 | 101
39031.5703 | 1631 | 355 | 101
39031.5725 | 1858 | 505 | 101
101
39031.5425 | 1 | 0 | 102
39031.5447 | 2010 | 0 | 102
39031.5468 | 2564 | 0 | 102
39031.549 | 2095 | 0 | 102
39031.5511 | 2252 | 0 | 102
39031.5532 | 2271 | 0 | 102
39031.5554 | 2102 | 0 | 102
39031.5575 | 2213 | 0 | 102
39031.5597 | 2292 | 0 | 102
39031.5618 | 2524 | 0 | 102
39031.5639 | 2601 | 0 | 102
39031.5661 | 2452 | 0 | 102
39031.5682 | 2263 | 0 | 102
39031.5703 | 1720 | 450 | 102
39031.5725 | 1344 | 726 | 102
102
39031.5426 | 1 | 0 | 103
39031.5447 | 1 | 0 | 103
39031.5468 | 2483 | 0 | 103
39031.549 | 2220 | 0 | 103
39031.5511 | 2575 | 0 | 103
39031.5533 | 2447 | 0 | 103
39031.5554 | 2611 | 0 | 103
39031.5575 | 2070 | 0 | 103
39031.5597 | 2085 | 0 | 103
39031.5618 | 2298 | 0 | 103
39031.5639 | 2590 | 0 | 103
39031.5661 | 2215 | 0 | 103
39031.5682 | 2493 | 0 | 103
39031.5704 | 2199 | 388 | 103
39031.5725 | 1098 | 894 | 103
103
39031.5426 | 1 | 0 | 104
39031.5447 | 1 | 0 | 104
39031.5469 | 2086 | 0 | 104
39031.549 | 2100 | 0 | 104
39031.5511 | 2141 | 0 | 104
39031.5533 | 2262 | 0 | 104
39031.5554 | 2559 | 0 | 104
39031.5575 | 2326 | 0 | 104
39031.5597 | 2255 | 0 | 104
39031.5618 | 2558 | 0 | 104
39031.564 | 2391 | 0 | 104
39031.5661 | 2219 | 0 | 104
39031.5682 | 2265 | 0 | 104
39031.5704 | 1353 | 553 | 104
39031.5725 | 1009 | 903 | 104
104
39031.5426 | 1 | 0 | 105
39031.5447 | 1 | 0 | 105
39031.5469 | 2238 | 0 | 105
39031.549 | 2515 | 0 | 105
39031.5511 | 2342 | 0 | 105
39031.5533 | 2576 | 0 | 105
39031.5554 | 2034 | 0 | 105
39031.5576 | 2587 | 0 | 105
39031.5597 | 2267 | 0 | 105
39031.5618 | 2457 | 0 | 105
39031.564 | 2537 | 0 | 105
39031.5661 | 2531 | 0 | 105
39031.5683 | 2157 | 0 | 105
39031.5704 | 1951 | 517 | 105
39031.5725 | 1283 | 150 | 105
105
39031.5426 | 1 | 0 | 106
39031.5447 | 1 | 0 | 106
39031.5469 | 1991 | 0 | 106
39031.549 | 2237 | 0 | 106
39031.5512 | 2176 | 0 | 106
39031.5533 | 2143 | 0 | 106
39031.5554 | 2595 | 0 | 106
39031.5576 | 2230 | 0 | 106
39031.5597 | 2301 | 0 | 106
39031.5619 | 2077 | 0 | 106
39031.564 | 2391 | 0 | 106
39031.5661 | 2145 | 0 | 106
39031.5683 | 2227 | 0 | 106
39031.5704 | 1777 | 311 | 106
39031.5725 | 1844 | 42 | 106
106
39031.5426 | 1 | 0 | 107
39031.5448 | 1 | 0 | 107
39031.5469 | 2006 | 0 | 107
39031.549 | 2029 | 0 | 107
39031.5512 | 2303 | 0 | 107
39031.5533 | 2495 | 0 | 107
39031.5555 | 2426 | 0 | 107
39031.5576 | 2441 | 0 | 107
39031.5597 | 2110 | 0 | 107
39031.5619 | 2338 | 0 | 107
39031.564 | 2192 | 0 | 107
39031.5661 | 2415 | 0 | 107
39031.5683 | 2531 | 0 | 107
39031.5704 | 1518 | 349 | 107
39031.5726 | 945 | 346 | 107
107
39031.5426 | 1 | 0 | 108
39031.5448 | 1 | 0 | 108
39031.5469 | 2475 | 0 | 108
39031.5491 | 2280 | 0 | 108
39031.5512 | 2564 | 0 | 108
39031.5533 | 2195 | 0 | 108
39031.5555 | 2603 | 0 | 108
39031.5576 | 2089 | 0 | 108
39031.5597 | 2031 | 0 | 108
39031.5619 | 2566 | 0 | 108
39031.564 | 2608 | 0 | 108
39031.5662 | 2155 | 0 | 108
39031.5683 | 1954 | 0 | 108
39031.5704 | 1837 | 261 | 108
39031.5726 | 1465 | 93 | 108
108
39031.5427 | 1 | 0 | 109
39031.5448 | 1 | 0 | 109
39031.5469 | 1991 | 0 | 109
39031.5491 | 2495 | 0 | 109
39031.5512 | 2049 | 0 | 109
39031.5533 | 2390 | 0 | 109
39031.5555 | 2147 | 0 | 109
39031.5576 | 2430 | 0 | 109
39031.5598 | 2427 | 0 | 109
39031.5619 | 2314 | 0 | 109
39031.564 | 2605 | 0 | 109
39031.5662 | 2423 | 0 | 109
39031.5683 | 2349 | 0 | 109
39031.5705 | 1672 | 334 | 109
39031.5726 | 1269 | 53 | 109
109
39031.5427 | 1 | 0 | 110
39031.5448 | 2312 | 0 | 110
39031.5469 | 2257 | 0 | 110
39031.5491 | 2086 | 0 | 110
39031.5512 | 2520 | 0 | 110
39031.5534 | 2305 | 0 | 110
39031.5555 | 2198 | 0 | 110
39031.5576 | 2004 | 0 | 110
39031.5598 | 2034 | 0 | 110
39031.5619 | 2330 | 0 | 110
39031.5641 | 2453 | 0 | 110
39031.5662 | 2051 | 0 | 110
39031.5683 | 2425 | 0 | 110
39031.5705 | 1677 | 237 | 110
39031.5726 | 1174 | 121 | 110
110
39031.5427 | 1 | 0 | 111
39031.5448 | 1 | 0 | 111
39031.547 | 2388 | 0 | 111
39031.5491 | 2338 | 0 | 111
39031.5512 | 2451 | 0 | 111
39031.5534 | 2107 | 0 | 111
39031.5555 | 2157 | 0 | 111
39031.5577 | 2600 | 0 | 111
39031.5598 | 2605 | 0 | 111
39031.5619 | 2025 | 0 | 111
39031.5641 | 2223 | 0 | 111
39031.5662 | 2144 | 0 | 111
39031.5683 | 2306 | 0 | 111
39031.5705 | 1544 | 440 | 111
39031.5726 | 1358 | 76 | 111
111
39031.5427 | 1 | 0 | 112
39031.5448 | 2388 | 0 | 112
39031.547 | 2013 | 0 | 112
39031.5491 | 2451 | 0 | 112
39031.5513 | 2595 | 0 | 112
39031.5534 | 2410 | 0 | 112
39031.5555 | 2293 | 0 | 112
39031.5577 | 2492 | 0 | 112
39031.5598 | 2108 | 0 | 112
39031.5619 | 2365 | 0 | 112
39031.5641 | 2534 | 0 | 112
39031.5662 | 2045 | 0 | 112
39031.5684 | 2050 | 0 | 112
39031.5705 | 1632 | 250 | 112
39031.5726 | 1170 | 53 | 112
112
39031.5427 | 1 | 0 | 113
39031.5449 | 1 | 0 | 113
39031.547 | 2319 | 0 | 113
39031.5491 | 2034 | 0 | 113
39031.5513 | 2013 | 0 | 113
39031.5534 | 2620 | 0 | 113
39031.5556 | 2552 | 0 | 113
39031.5577 | 2024 | 0 | 113
39031.5598 | 2308 | 0 | 113
39031.562 | 2570 | 0 | 113
39031.5641 | 2444 | 0 | 113
39031.5662 | 2477 | 0 | 113
39031.5684 | 2191 | 0 | 113
39031.5705 | 1754 | 307 | 113
39031.5727 | 1154 | 322 | 113
113
39031.5427 | 1 | 0 | 114
39031.5449 | 1 | 0 | 114
39031.547 | 2219 | 0 | 114
39031.5492 | 1984 | 0 | 114
39031.5513 | 2226 | 0 | 114
39031.5534 | 2090 | 0 | 114
39031.5556 | 2060 | 0 | 114
39031.5577 | 2310 | 0 | 114
39031.5598 | 2389 | 0 | 114
39031.562 | 2078 | 0 | 114
39031.5641 | 2491 | 0 | 114
39031.5663 | 2445 | 0 | 114
39031.5684 | 2495 | 0 | 114
39031.5705 | 1716 | 284 | 114
39031.5727 | 1289 | 69 | 114
114
39031.5428 | 1 | 0 | 115
39031.5449 | 1 | 0 | 115
39031.547 | 1991 | 0 | 115
39031.5492 | 2109 | 0 | 115
39031.5513 | 2051 | 0 | 115
39031.5534 | 2563 | 0 | 115
39031.5556 | 2558 | 0 | 115
39031.5577 | 2600 | 0 | 115
39031.5599 | 2137 | 0 | 115
39031.562 | 2409 | 0 | 115
39031.5641 | 2462 | 0 | 115
39031.5663 | 2065 | 0 | 115
39031.5684 | 1955 | 0 | 115
39031.5706 | 1334 | 431 | 115
39031.5727 | 1007 | 74 | 115
115
39031.5428 | 1 | 0 | 116
39031.5449 | 2274 | 0 | 116
39031.547 | 2109 | 0 | 116
39031.5492 | 2067 | 0 | 116
39031.5513 | 2503 | 0 | 116
39031.5535 | 2452 | 0 | 116
39031.5556 | 2009 | 0 | 116
39031.5577 | 2029 | 0 | 116
39031.5599 | 2149 | 0 | 116
39031.562 | 2013 | 0 | 116
39031.5642 | 2222 | 0 | 116
39031.5663 | 2221 | 0 | 116
39031.5684 | 2359 | 1 | 116
39031.5706 | 1975 | 305 | 116
39031.5727 | 2175 | 8 | 116
116
39031.5428 | 1 | 0 | 117
39031.5449 | 2 | 0 | 117
39031.5471 | 2393 | 0 | 117
39031.5492 | 2226 | 0 | 117
39031.5513 | 2467 | 0 | 117
39031.5535 | 2234 | 0 | 117
39031.5556 | 2158 | 0 | 117
39031.5578 | 2176 | 0 | 117
39031.5599 | 2257 | 0 | 117
39031.562 | 2591 | 0 | 117
39031.5642 | 2061 | 0 | 117
39031.5663 | 2450 | 0 | 117
39031.5684 | 2190 | 0 | 117
39031.5706 | 1565 | 174 | 117
39031.5727 | 1180 | 0 | 117
117
39031.5428 | 1 | 0 | 118
39031.5449 | 2467 | 0 | 118
39031.5471 | 2448 | 0 | 118
39031.5492 | 2407 | 0 | 118
39031.5514 | 2243 | 0 | 118
39031.5535 | 2377 | 0 | 118
39031.5556 | 2025 | 0 | 118
39031.5578 | 2134 | 0 | 118
39031.5599 | 2427 | 0 | 118
39031.562 | 2427 | 0 | 118
39031.5642 | 2228 | 0 | 118
39031.5663 | 2202 | 0 | 118
39031.5685 | 1990 | 1 | 118
39031.5706 | 1818 | 308 | 118
39031.5727 | 1866 | 0 | 118
118
39031.5428 | 1 | 0 | 119
39031.545 | 1 | 0 | 119
39031.5471 | 2391 | 0 | 119
39031.5492 | 2109 | 0 | 119
39031.5514 | 2110 | 0 | 119
39031.5535 | 2022 | 0 | 119
39031.5556 | 2609 | 0 | 119
39031.5578 | 2067 | 0 | 119
39031.5599 | 2169 | 0 | 119
39031.5621 | 2389 | 0 | 119
39031.5642 | 2177 | 0 | 119
39031.5663 | 2464 | 0 | 119
39031.5685 | 1949 | 0 | 119
39031.5706 | 1330 | 364 | 119
39031.5728 | 1099 | 59 | 119
119
39031.5428 | 1 | 0 | 120
39031.545 | 2128 | 0 | 120
39031.5471 | 2216 | 0 | 120
39031.5492 | 2022 | 0 | 120
39031.5514 | 2567 | 0 | 120
39031.5535 | 2140 | 0 | 120
39031.5557 | 2018 | 0 | 120
39031.5578 | 2547 | 0 | 120
39031.5599 | 2541 | 0 | 120
39031.5621 | 2568 | 0 | 120
39031.5642 | 2258 | 0 | 120
39031.5664 | 2435 | 0 | 120
39031.5685 | 2291 | 9 | 120
39031.5706 | 1728 | 324 | 120
39031.5728 | 1209 | 70 | 120
120
39031.5428 | 1 | 0 | 121
39031.545 | 2298 | 0 | 121
39031.5471 | 1980 | 0 | 121
39031.5493 | 2217 | 0 | 121
39031.5514 | 2050 | 0 | 121
39031.5535 | 2372 | 0 | 121
39031.5557 | 2579 | 0 | 121
39031.5578 | 2180 | 0 | 121
39031.56 | 2190 | 0 | 121
39031.5621 | 2609 | 0 | 121
39031.5642 | 2506 | 0 | 121
39031.5664 | 2019 | 0 | 121
39031.5685 | 2220 | 37 | 121
39031.5706 | 1752 | 450 | 121
39031.5728 | 1445 | 989 | 121
121
39031.5429 | 1 | 0 | 122
39031.545 | 2161 | 0 | 122
39031.5471 | 2157 | 0 | 122
39031.5493 | 2346 | 0 | 122
39031.5514 | 2285 | 0 | 122
39031.5536 | 2166 | 0 | 122
39031.5557 | 2506 | 0 | 122
39031.5578 | 2102 | 0 | 122
39031.56 | 2450 | 0 | 122
39031.5621 | 2481 | 0 | 122
39031.5642 | 2029 | 0 | 122
39031.5664 | 2412 | 0 | 122
39031.5685 | 2199 | 43 | 122
39031.5707 | 1925 | 450 | 122
39031.5728 | 1321 | 673 | 122
122
39031.5429 | 1 | 0 | 123
39031.545 | 2027 | 0 | 123
39031.5472 | 2013 | 0 | 123
39031.5493 | 2270 | 0 | 123
39031.5514 | 2180 | 0 | 123
39031.5536 | 2068 | 0 | 123
39031.5557 | 2167 | 0 | 123
39031.5578 | 2569 | 0 | 123
39031.56 | 2341 | 0 | 123
39031.5621 | 2405 | 0 | 123
39031.5643 | 2209 | 0 | 123
39031.5664 | 2182 | 0 | 123
39031.5685 | 2161 | 28 | 123
39031.5707 | 1930 | 373 | 123
39031.5728 | 1269 | 697 | 123
123
39031.5429 | 1 | 0 | 124
39031.545 | 2488 | 0 | 124
39031.5472 | 2575 | 0 | 124
39031.5493 | 2079 | 0 | 124
39031.5514 | 2276 | 0 | 124
39031.5536 | 2462 | 0 | 124
39031.5557 | 1982 | 0 | 124
39031.5579 | 2510 | 0 | 124
39031.56 | 2033 | 0 | 124
39031.5621 | 2515 | 0 | 124
39031.5643 | 2286 | 0 | 124
39031.5664 | 2337 | 0 | 124
39031.5686 | 2327 | 28 | 124
39031.5707 | 1658 | 417 | 124
39031.5728 | 915 | 714 | 124
124
39031.5429 | 1 | 0 | 125
39031.545 | 2451 | 0 | 125
39031.5472 | 2030 | 0 | 125
39031.5493 | 2536 | 0 | 125
39031.5515 | 2190 | 0 | 125
39031.5536 | 2328 | 0 | 125
39031.5557 | 2121 | 0 | 125
39031.5579 | 2255 | 0 | 125
39031.56 | 2335 | 0 | 125
39031.5622 | 2393 | 0 | 125
39031.5643 | 2605 | 0 | 125
39031.5664 | 2132 | 0 | 125
39031.5686 | 2134 | 23 | 125
39031.5707 | 1809 | 229 | 125
39031.5728 | 1214 | 529 | 125
125
39031.5429 | 1 | 0 | 126
39031.5451 | 2215 | 0 | 126
39031.5472 | 2583 | 0 | 126
39031.5493 | 2535 | 0 | 126
39031.5515 | 2240 | 0 | 126
39031.5536 | 2118 | 0 | 126
39031.5558 | 2046 | 0 | 126
39031.5579 | 2535 | 0 | 126
39031.56 | 2606 | 0 | 126
39031.5622 | 2072 | 0 | 126
39031.5643 | 2595 | 0 | 126
39031.5665 | 2021 | 0 | 126
39031.5686 | 2332 | 31 | 126
39031.5707 | 1715 | 510 | 126
39031.5729 | 1091 | 761 | 126
126
39031.5429 | 1 | 0 | 127
39031.5451 | 2335 | 0 | 127
39031.5472 | 2446 | 0 | 127
39031.5494 | 2572 | 0 | 127
39031.5515 | 2499 | 0 | 127
39031.5536 | 2368 | 0 | 127
39031.5558 | 2273 | 0 | 127
39031.5579 | 2092 | 0 | 127
39031.5601 | 2283 | 0 | 127
39031.5622 | 2326 | 0 | 127
39031.5643 | 2259 | 0 | 127
39031.5665 | 2463 | 0 | 127
39031.5686 | 2148 | 27 | 127
39031.5708 | 1790 | 326 | 127
39031.5729 | 1298 | 582 | 127
127
39031.543 | 1 | 0 | 128
39031.5451 | 2546 | 0 | 128
39031.5472 | 2209 | 0 | 128
39031.5494 | 2041 | 0 | 128
39031.5515 | 2034 | 0 | 128
39031.5537 | 2111 | 0 | 128
39031.5558 | 2286 | 0 | 128
39031.5579 | 2072 | 0 | 128
39031.5601 | 2571 | 0 | 128
39031.5622 | 2385 | 0 | 128
39031.5644 | 2481 | 0 | 128
39031.5665 | 2336 | 0 | 128
39031.5686 | 2037 | 27 | 128
39031.5708 | 1737 | 399 | 128
39031.5729 | 1015 | 693 | 128
128
39031.543 | 1 | 0 | 129
39031.5451 | 2300 | 0 | 129
39031.5473 | 2438 | 0 | 129
39031.5494 | 2567 | 0 | 129
39031.5515 | 2550 | 0 | 129
39031.5537 | 2607 | 0 | 129
39031.5558 | 2590 | 0 | 129
39031.558 | 2253 | 0 | 129
39031.5601 | 2112 | 0 | 129
39031.5622 | 2224 | 0 | 129
39031.5644 | 2331 | 0 | 129
39031.5665 | 2594 | 0 | 129
39031.5686 | 2169 | 26 | 129
39031.5708 | 1507 | 421 | 129
39031.5729 | 1262 | 562 | 129
129
39031.543 | 1 | 0 | 130
39031.5451 | 2543 | 0 | 130
39031.5473 | 2614 | 0 | 130
39031.5494 | 2345 | 0 | 130
39031.5516 | 2423 | 0 | 130
39031.5537 | 2519 | 0 | 130
39031.5558 | 2031 | 0 | 130
39031.558 | 2172 | 0 | 130
39031.5601 | 2553 | 0 | 130
39031.5622 | 2137 | 0 | 130
39031.5644 | 2080 | 0 | 130
39031.5665 | 2618 | 0 | 130
39031.5687 | 1957 | 27 | 130
39031.5708 | 1346 | 574 | 130
39031.5729 | 954 | 740 | 130
130
39031.543 | 1 | 0 | 131
39031.5452 | 2090 | 0 | 131
39031.5473 | 2493 | 0 | 131
39031.5494 | 2255 | 0 | 131
39031.5516 | 2209 | 0 | 131
39031.5537 | 2351 | 0 | 131
39031.5558 | 2358 | 0 | 131
39031.558 | 2273 | 0 | 131
39031.5601 | 2052 | 0 | 131
39031.5623 | 2303 | 0 | 131
39031.5644 | 2020 | 0 | 131
39031.5665 | 2268 | 0 | 131
39031.5687 | 2228 | 60 | 131
39031.5708 | 1831 | 572 | 131
39031.573 | 1084 | 832 | 131
131
39031.543 | 1 | 0 | 132
39031.5452 | 2155 | 0 | 132
39031.5473 | 2236 | 0 | 132
39031.5494 | 2295 | 0 | 132
39031.5516 | 2061 | 0 | 132
39031.5537 | 2284 | 0 | 132
39031.5559 | 2297 | 0 | 132
39031.558 | 2522 | 0 | 132
39031.5601 | 2048 | 0 | 132
39031.5623 | 2027 | 0 | 132
39031.5644 | 2096 | 0 | 132
39031.5666 | 2497 | 0 | 132
39031.5687 | 2182 | 61 | 132
39031.5708 | 1844 | 632 | 132
39031.573 | 1328 | 703 | 132
132

## C6-F12
Open Burn Test 8 |  |  | 2006-11-10 | 13:06 |  |  | Vs = |  | 159.7912 |  | R = | 100
Mix | 7-C | Tray A | IRMS | 1
0 | 150 kW |  | Bundle | Ch. 6 & 12 | Cable C | Even - | Cable F |  | Even
Time-101 | N11 | N12 | Time-102 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R12-G | R6-12
39031.5425 | 1 | 0 | 39031.5425 | 1 | 0 |  | -78 | 141 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261638 | 261638 | 261637.9994
39031.5447 | 1 | 0 | 39031.5447 | 2010 | 0 |  | 106.5 | 325.5 | 0.06105 | 0 | 122.7106 | 0 | 0.0006105 | 0 | 1.2271 | 0 | 0.0006105 | 1.2271 | 261638 | 30.2179 | 261637.9994
39031.5468 | 2449 | 0 | 39031.5468 | 2564 | 0 |  | 291.5 | 510.5 | 149.5116 | 0 | 156.5324 | 0 | 1.4951 | 0 | 1.5653 | 0 | 1.4951 | 1.5653 | 6.8755 | 2.0819 | 5.3803
39031.5489 | 2354 | 0 | 39031.549 | 2095 | 0 |  | 476 | 695 | 143.7118 | 0 | 127.8999 | 0 | 1.4371 | 0 | 1.279 | 0 | 1.4371 | 1.279 | 11.1886 | 24.9346 | 9.7515
39031.5511 | 2518 | 0 | 39031.5511 | 2252 | 0 |  | 661 | 880 | 153.7241 | 0 | 137.4847 | 0 | 1.5372 | 0 | 1.3748 | 0 | 1.5372 | 1.3748 | 3.9468 | 16.2247 | 2.4095
39031.5532 | 1962 | 0 | 39031.5532 | 2271 | 0 |  | 845.5 | 1064.5 | 119.7802 | 0 | 138.6447 | 0 | 1.1978 | 0 | 1.3864 | 0 | 1.1978 | 1.3864 | 33.4037 | 15.2523 | 32.2059
39031.5554 | 2497 | 0 | 39031.5554 | 2102 | 0 |  | 1030.5 | 1249.5 | 152.442 | 0 | 128.3272 | 0 | 1.5244 | 0 | 1.2833 | 0 | 1.5244 | 1.2833 | 4.821 | 24.5186 | 3.2966
39031.5575 | 2271 | 0 | 39031.5575 | 2213 | 0 |  | 1215 | 1434 | 138.6447 | 0 | 135.1038 | 0 | 1.3864 | 0 | 1.351 | 0 | 1.3864 | 1.351 | 15.2523 | 18.2729 | 13.8659
39031.5596 | 2280 | 0 | 39031.5597 | 2292 | 0 |  | 1400 | 1619 | 139.1941 | 0 | 139.9267 | 0 | 1.3919 | 0 | 1.3993 | 0 | 1.3919 | 1.3993 | 14.7974 | 14.1963 | 13.4054
39031.5618 | 2348 | 0 | 39031.5618 | 2524 | 0 |  | 1584.5 | 1803.5 | 143.3455 | 0 | 154.0904 | 0 | 1.4335 | 0 | 1.5409 | 0 | 1.4335 | 1.5409 | 11.4727 | 3.6997 | 10.0393
39031.5639 | 2193 | 0 | 39031.5639 | 2601 | 0 |  | 1769.5 | 1988.5 | 133.8828 | 0 | 158.7912 | 0 | 1.3388 | 0 | 1.5879 | 0 | 1.3388 | 1.5879 | 19.3516 | 0.62976 | 18.0127
39031.5661 | 2503 | 0 | 39031.5661 | 2452 | 0 |  | 1954.5 | 2173.5 | 152.8083 | 0 | 149.6947 | 0 | 1.5281 | 0 | 1.4969 | 0 | 1.5281 | 1.4969 | 4.5697 | 6.7447 | 3.0416
39031.5682 | 2317 | 0 | 39031.5682 | 2263 | 0 |  | 2139 | 2358 | 141.453 | 0 | 138.1563 | 0 | 1.4145 | 0 | 1.3816 | 0 | 1.4145 | 1.3816 | 12.9642 | 15.6597 | 11.5496
39031.5703 | 1631 | 355 | 39031.5703 | 1720 | 450 |  | 2323.5 | 2542.5 | 99.5726 | 21.6728 | 105.0061 | 27.4725 | 0.99573 | 0.21673 | 1.0501 | 0.27473 | 0.779 | 0.77534 | 104.4945 | 106.913 | 91.8978
39031.5725 | 1858 | 505 | 39031.5725 | 1344 | 726 |  | 2508.5 | 2727.5 | 113.431 | 30.8303 | 82.0513 | 44.3223 | 1.1343 | 0.3083 | 0.82051 | 0.44322 | 0.82601 | 0.37729 | 42.554 | 117.0315 | 27.1626

## C6-F11
Open Burn Test 8 |  |  | 2006-11-10 | 13:06 |  |  | Vs = |  | 159.9744 |  | R = | 100
Mix | 7-C | Tray A | IRMS | 1
0 | 150 kW |  | Bundle | Ch. 6 & 11 | Cable C | Even - | Cable F |  | Odd
Time-99 | N11 | N12 | Time-100 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R11-G | R6-11
39031.5425 | 1 | 0 | 39031.5425 | 1 | 0 |  | -81 | 138 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261938 | 261938 | 261937.9994
39031.5446 | 1 | 0 | 39031.5447 | 2536 | 0 |  | 104 | 323 | 0.06105 | 0 | 154.823 | 0 | 0.0006105 | 0 | 1.5482 | 0 | 0.0006105 | 1.5482 | 261938 | 3.3273 | 261937.9994
39031.5468 | 2127 | 0 | 39031.5468 | 2388 | 0 |  | 288.5 | 507.5 | 129.8535 | 0 | 145.7875 | 0 | 1.2985 | 0 | 1.4579 | 0 | 1.2985 | 1.4579 | 23.1961 | 9.7312 | 21.8975
39031.5489 | 2036 | 0 | 39031.5489 | 2443 | 0 |  | 473.5 | 692.5 | 124.2979 | 0 | 149.1453 | 0 | 1.243 | 0 | 1.4915 | 0 | 1.243 | 1.4915 | 28.7024 | 7.2607 | 27.4594
39031.551 | 1949 | 0 | 39031.5511 | 2604 | 0 |  | 658 | 877 | 118.9866 | 0 | 158.9744 | 0 | 1.1899 | 0 | 1.5897 | 0 | 1.1899 | 1.5897 | 34.4474 | 0.62903 | 33.2575
39031.5532 | 2244 | 0 | 39031.5532 | 2597 | 0 |  | 843 | 1062 | 136.9963 | 0 | 158.547 | 0 | 1.37 | 0 | 1.5855 | 0 | 1.37 | 1.5855 | 16.7727 | 0.90027 | 15.4028
39031.5553 | 2075 | 0 | 39031.5553 | 2063 | 0 |  | 1027.5 | 1246.5 | 126.6789 | 0 | 125.9463 | 0 | 1.2668 | 0 | 1.2595 | 0 | 1.2668 | 1.2595 | 26.2834 | 27.0179 | 25.0166
39031.5575 | 2043 | 0 | 39031.5575 | 2106 | 0 |  | 1212.5 | 1431.5 | 124.7253 | 0 | 128.5714 | 0 | 1.2473 | 0 | 1.2857 | 0 | 1.2473 | 1.2857 | 28.2614 | 24.4245 | 27.0141
39031.5596 | 1993 | 0 | 39031.5596 | 2557 | 0 |  | 1397 | 1616 | 121.6728 | 0 | 156.105 | 0 | 1.2167 | 0 | 1.5611 | 0 | 1.2167 | 1.5611 | 31.4792 | 2.4787 | 30.2624
39031.5617 | 1966 | 0 | 39031.5618 | 2063 | 0 |  | 1582 | 1801 | 120.0244 | 0 | 125.9463 | 0 | 1.2002 | 0 | 1.2595 | 0 | 1.2002 | 1.2595 | 33.2848 | 27.0179 | 32.0846
39031.5639 | 2436 | 0 | 39031.5639 | 2565 | 0 |  | 1766.5 | 1985.5 | 148.7179 | 0 | 156.5934 | 0 | 1.4872 | 0 | 1.5659 | 0 | 1.4872 | 1.5659 | 7.569 | 2.1591 | 6.0818
39031.566 | 2412 | 0 | 39031.566 | 2515 | 0 |  | 1951.5 | 2170.5 | 147.2527 | 0 | 153.5409 | 0 | 1.4725 | 0 | 1.5354 | 0 | 1.4725 | 1.5354 | 8.6393 | 4.1901 | 7.1668
39031.5682 | 2030 | 0 | 39031.5682 | 2322 | 0 |  | 2136.5 | 2355.5 | 123.9316 | 0 | 141.7582 | 0 | 1.2393 | 0 | 1.4176 | 0 | 1.2393 | 1.4176 | 29.0828 | 12.8501 | 27.8434
39031.5703 | 2145 | 269 | 39031.5703 | 1571 | 337 |  | 2321 | 2540 | 130.9524 | 16.4225 | 95.9096 | 20.5739 | 1.3095 | 0.16422 | 0.9591 | 0.20574 | 1.1453 | 0.75336 | 24.9406 | 895.3141 | 69.013
39031.5724 | 1449 | 587 | 39031.5725 | 1075 | 738 |  | 2506 | 2725 | 88.4615 | 35.8364 | 65.6288 | 45.0549 | 0.88462 | 0.35836 | 0.65629 | 0.45055 | 0.52625 | 0.20574 | 121.3985 | 570.4291 | 84.7044

## C6-E10
Open Burn Test 8 |  |  | 2006-11-10 | 13:06 |  |  | Vs = |  | 159.4249 |  | R = | 100
Mix | 7-C | Tray A | IRMS | 1
0 | 150 kW |  | Bundle | Ch. 6 & 10 | Cable C | Even - | Cable E |  | Even
Time-97 | N11 | N12 | Time-98 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R10-G | R6-10
39031.5425 | 1 | 0 | 39031.5425 | 1 | 0 |  | -84 | 135 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261038 | 261038 | 261037.9994
39031.5446 | 1 | 0 | 39031.5446 | 1 | 0 |  | 101 | 320 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261038 | 261038 | 261037.9994
39031.5467 | 2435 | 0 | 39031.5467 | 2083 | 0 |  | 285.5 | 504.5 | 148.6569 | 0 | 127.1673 | 0 | 1.4866 | 0 | 1.2717 | 0 | 1.4866 | 1.2717 | 7.2435 | 25.3663 | 5.757
39031.5489 | 1977 | 0 | 39031.5489 | 2561 | 0 |  | 470.5 | 689.5 | 120.696 | 0 | 156.3492 | 0 | 1.207 | 0 | 1.5635 | 0 | 1.207 | 1.5635 | 32.088 | 1.9672 | 30.8811
39031.551 | 2306 | 0 | 39031.551 | 2094 | 0 |  | 655.5 | 874.5 | 140.7814 | 0 | 127.8388 | 0 | 1.4078 | 0 | 1.2784 | 0 | 1.4078 | 1.2784 | 13.2428 | 24.7077 | 11.835
39031.5531 | 2420 | 0 | 39031.5532 | 2595 | 0 |  | 840 | 1059 | 147.7411 | 0 | 158.4249 | 0 | 1.4774 | 0 | 1.5842 | 0 | 1.4774 | 1.5842 | 7.9083 | 0.63121 | 6.4309
39031.5553 | 2499 | 0 | 39031.5553 | 2508 | 0 |  | 1025 | 1244 | 152.5641 | 0 | 153.1136 | 0 | 1.5256 | 0 | 1.5311 | 0 | 1.5256 | 1.5311 | 4.497 | 4.122 | 2.9714
39031.5574 | 2290 | 0 | 39031.5574 | 2245 | 0 |  | 1209.5 | 1428.5 | 139.8046 | 0 | 137.0574 | 0 | 1.398 | 0 | 1.3706 | 0 | 1.398 | 1.3706 | 14.0341 | 16.3198 | 12.636
39031.5596 | 2160 | 0 | 39031.5596 | 2141 | 0 |  | 1394.5 | 1613.5 | 131.8681 | 0 | 130.7082 | 0 | 1.3187 | 0 | 1.3071 | 0 | 1.3187 | 1.3071 | 20.8972 | 21.9701 | 19.5785
39031.5617 | 2239 | 0 | 39031.5617 | 2506 | 0 |  | 1579 | 1798 | 136.6911 | 0 | 152.9915 | 0 | 1.3669 | 0 | 1.5299 | 0 | 1.3669 | 1.5299 | 16.6315 | 4.2051 | 15.2646
39031.5638 | 2011 | 0 | 39031.5639 | 2341 | 0 |  | 1764 | 1983 | 122.7717 | 0 | 142.9182 | 0 | 1.2277 | 0 | 1.4292 | 0 | 1.2277 | 1.4292 | 29.8548 | 11.5498 | 28.6271
39031.566 | 2184 | 0 | 39031.566 | 2180 | 0 |  | 1948.5 | 2167.5 | 133.3333 | 0 | 133.0891 | 0 | 1.3333 | 0 | 1.3309 | 0 | 1.3333 | 1.3309 | 19.5687 | 19.7881 | 18.2353
39031.5681 | 2498 | 0 | 39031.5681 | 2544 | 0 |  | 2133.5 | 2352.5 | 152.5031 | 0 | 155.3114 | 0 | 1.525 | 0 | 1.5531 | 0 | 1.525 | 1.5531 | 4.5388 | 2.6486 | 3.0138
39031.5703 | 1964 | 227 | 39031.5703 | 2047 | 440 |  | 2318.5 | 2537.5 | 119.9023 | 13.8584 | 124.9695 | 26.862 | 1.199 | 0.13858 | 1.2497 | 0.26862 | 1.0604 | 0.98107 | 43.131 | 96.1706 | 90.7872
39031.5724 | 1783 | 680 | 39031.5724 | 1446 | 718 |  | 2503 | 2722 | 108.8523 | 41.514 | 88.2784 | 43.8339 | 1.0885 | 0.41514 | 0.88278 | 0.43834 | 0.67338 | 0.44444 | 60.3686 | 252.5962 | 15.632

## C6-E9
Open Burn Test 8 |  |  | 2006-11-10 | 13:06 |  |  | Vs = |  | 157.7155 |  | R = | 100
Mix | 7-C | Tray A | IRMS | 1
0 | 150 kW |  | Bundle | Ch. 6 & 9 | Cable C | Even - | Cable E |  | Odd
Time-95 | N11 | N12 | Time-96 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R9-G | R6-9
39031.5424 | 1 | 0 | 39031.5424 | 1 | 0 |  | -86.5 | 132.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258238 | 258238 | 258237.9994
39031.5446 | 1 | 0 | 39031.5446 | 1 | 0 |  | 98.5 | 317.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258238 | 258238 | 258237.9994
39031.5467 | 2428 | 0 | 39031.5467 | 2556 | 0 |  | 283 | 502 | 148.2295 | 0 | 156.044 | 0 | 1.4823 | 0 | 1.5604 | 0 | 1.4823 | 1.5604 | 6.3995 | 1.0712 | 4.9172
39031.5488 | 2388 | 0 | 39031.5489 | 2567 | 0 |  | 467.5 | 686.5 | 145.7875 | 0 | 156.7155 | 0 | 1.4579 | 0 | 1.5672 | 0 | 1.4579 | 1.5672 | 8.1817 | 0.6381 | 6.7239
39031.551 | 2248 | 0 | 39031.551 | 2097 | 0 |  | 652.5 | 871.5 | 137.2405 | 0 | 128.022 | 0 | 1.3724 | 0 | 1.2802 | 0 | 1.3724 | 1.2802 | 14.919 | 23.1941 | 13.5466
39031.5531 | 2308 | 0 | 39031.5531 | 2334 | 0 |  | 837.5 | 1056.5 | 140.9035 | 0 | 142.4908 | 0 | 1.409 | 0 | 1.4249 | 0 | 1.409 | 1.4249 | 11.9315 | 10.6847 | 10.5225
39031.5553 | 2269 | 0 | 39031.5553 | 2372 | 0 |  | 1022 | 1241 | 138.5226 | 0 | 144.8107 | 0 | 1.3852 | 0 | 1.4481 | 0 | 1.3852 | 1.4481 | 13.8554 | 8.9115 | 12.4702
39031.5574 | 1930 | 0 | 39031.5574 | 2194 | 0 |  | 1206.5 | 1425.5 | 117.8266 | 0 | 133.9438 | 0 | 1.1783 | 0 | 1.3394 | 0 | 1.1783 | 1.3394 | 33.8539 | 17.7475 | 32.6756
39031.5595 | 1850 | 0 | 39031.5595 | 2138 | 0 |  | 1391.5 | 1610.5 | 112.9426 | 0 | 130.525 | 0 | 1.1294 | 0 | 1.3053 | 0 | 1.1294 | 1.3053 | 39.6422 | 20.8316 | 38.5127
39031.5617 | 2165 | 0 | 39031.5617 | 2156 | 0 |  | 1576.5 | 1795.5 | 132.1734 | 0 | 131.6239 | 0 | 1.3217 | 0 | 1.3162 | 0 | 1.3217 | 1.3162 | 19.3247 | 19.8228 | 18.003
39031.5638 | 2027 | 0 | 39031.5638 | 2180 | 0 |  | 1761 | 1980 | 123.7485 | 0 | 133.0891 | 0 | 1.2375 | 0 | 1.3309 | 0 | 1.2375 | 1.3309 | 27.4484 | 18.5037 | 26.211
39031.5659 | 2274 | 0 | 39031.566 | 2214 | 0 |  | 1946 | 2165 | 138.8278 | 0 | 135.1648 | 0 | 1.3883 | 0 | 1.3516 | 0 | 1.3883 | 1.3516 | 13.6051 | 16.6838 | 12.2168
39031.5681 | 2519 | 0 | 39031.5681 | 2107 | 0 |  | 2130.5 | 2349.5 | 153.7851 | 0 | 128.6325 | 0 | 1.5379 | 0 | 1.2863 | 0 | 1.5379 | 1.2863 | 2.5558 | 22.6094 | 1.0179
39031.5702 | 2040 | 393 | 39031.5702 | 1574 | 294 |  | 2315.5 | 2534.5 | 124.5421 | 23.9927 | 96.0928 | 17.9487 | 1.2454 | 0.23993 | 0.96093 | 0.17949 | 1.0055 | 0.78144 | 37.341 | 204.883 | 25.714
39031.5724 | 1372 | 609 | 39031.5724 | 1857 | 588 |  | 2500.5 | 2719.5 | 83.7607 | 37.1795 | 113.37 | 35.8974 | 0.83761 | 0.37179 | 1.1337 | 0.35897 | 0.46581 | 0.77473 | 238.7222 | 238.3033 | 69.675

## C5-F12
Open Burn Test 8 |  |  | 2006-11-10 | 13:06 |  |  | Vs = |  | 158.6923 |  | R = | 100
Mix | 7-C | Tray A | IRMS | 1
0 | 150 kW |  | Bundle | Ch. 5 & 12 | Cable C | Odd - | Cable F |  | Even
Time-89 | N11 | N12 | Time-90 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R12-G | R5-12
39031.5423 | 1 | 0 | 39031.5423 | 1 | 0 |  | -95 | 124 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259838 | 259838 | 259837.9994
39031.5445 | 1 | 0 | 39031.5445 | 1540 | 0 |  | 90 | 309 | 0.06105 | 0 | 94.0171 | 0 | 0.0006105 | 0 | 0.94017 | 0 | 0.0006105 | 0.94017 | 259838 | 68.7909 | 259837.9994
39031.5466 | 869 | 0 | 39031.5466 | 2124 | 0 |  | 274.5 | 493.5 | 53.0525 | 0 | 129.6703 | 0 | 0.53053 | 0 | 1.2967 | 0 | 0.53053 | 1.2967 | 199.1231 | 22.3814 | 198.5926
39031.5488 | 2426 | 0 | 39031.5488 | 2021 | 0 |  | 459.5 | 678.5 | 148.1074 | 0 | 123.3822 | 0 | 1.4811 | 0 | 1.2338 | 0 | 1.4811 | 1.2338 | 7.1467 | 28.6185 | 5.6657
39031.5509 | 2418 | 0 | 39031.5509 | 2512 | 0 |  | 644 | 863 | 147.619 | 0 | 153.3578 | 0 | 1.4762 | 0 | 1.5336 | 0 | 1.4762 | 1.5336 | 7.5012 | 3.4785 | 6.0251
39031.553 | 1925 | 0 | 39031.553 | 2080 | 0 |  | 829 | 1048 | 117.5214 | 0 | 126.9841 | 0 | 1.1752 | 0 | 1.2698 | 0 | 1.1752 | 1.2698 | 35.0327 | 24.9702 | 33.8575
39031.5552 | 2492 | 0 | 39031.5552 | 1992 | 0 |  | 1013.5 | 1232.5 | 152.1368 | 0 | 121.6117 | 0 | 1.5214 | 0 | 1.2161 | 0 | 1.5214 | 1.2161 | 4.309 | 30.491 | 2.7876
39031.5573 | 1900 | 0 | 39031.5573 | 2491 | 0 |  | 1198.5 | 1417.5 | 115.9951 | 0 | 152.0757 | 0 | 1.16 | 0 | 1.5208 | 0 | 1.16 | 1.5208 | 36.8095 | 4.3509 | 35.6495
39031.5594 | 2162 | 0 | 39031.5595 | 2583 | 0 |  | 1383 | 1602 | 131.9902 | 0 | 157.6923 | 0 | 1.3199 | 0 | 1.5769 | 0 | 1.3199 | 1.5769 | 20.2303 | 0.63415 | 18.9104
39031.5616 | 2549 | 0 | 39031.5616 | 2210 | 0 |  | 1568 | 1787 | 155.6166 | 0 | 134.9206 | 0 | 1.5562 | 0 | 1.3492 | 0 | 1.5562 | 1.3492 | 1.9765 | 17.619 | 0.4203
39031.5637 | 2243 | 0 | 39031.5637 | 2116 | 0 |  | 1752.5 | 1971.5 | 136.9353 | 0 | 129.1819 | 0 | 1.3694 | 0 | 1.2918 | 0 | 1.3694 | 1.2918 | 15.8885 | 22.844 | 14.5192
39031.5659 | 2430 | 0 | 39031.5659 | 2131 | 0 |  | 1937.5 | 2156.5 | 148.3516 | 0 | 130.0977 | 0 | 1.4835 | 0 | 1.301 | 0 | 1.4835 | 1.301 | 6.9704 | 21.9794 | 5.4869
39031.568 | 2228 | 0 | 39031.568 | 1989 | 0 |  | 2122.5 | 2341.5 | 136.0195 | 0 | 121.4286 | 0 | 1.3602 | 0 | 1.2143 | 0 | 1.3602 | 1.2143 | 16.6688 | 30.6878 | 15.3086
39031.5701 | 1975 | 292 | 39031.5702 | 1676 | 468 |  | 2307 | 2526 | 120.5739 | 17.8266 | 102.3199 | 28.5714 | 1.2057 | 0.17827 | 1.0232 | 0.28571 | 1.0275 | 0.73748 | 36.6169 | 1317.2956 | 105.7974
39031.5723 | 1800 | 399 | 39031.5723 | 1005 | 694 |  | 2491.5 | 2710.5 | 109.8901 | 24.359 | 61.3553 | 42.3687 | 1.0989 | 0.24359 | 0.61355 | 0.42369 | 0.85531 | 0.18987 | 47.2882 | 137.851 | 58.1573

## C5-F11
Open Burn Test 8 |  |  | 2006-11-10 | 13:06 |  |  | Vs = |  | 160.9512 |  | R = | 100
Mix | 7-C | Tray A | IRMS | 1
0 | 150 kW |  | Bundle | Ch. 5 & 11 | Cable C | Odd - | Cable F |  | Odd
Time-87 | N11 | N12 | Time-88 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R11-G | R5-11
39031.5423 | 1 | 0 | 39031.5423 | 1 | 0 |  | -97.5 | 121.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263538 | 263538 | 263537.9994
39031.5444 | 1 | 0 | 39031.5445 | 1792 | 0 |  | 87 | 306 | 0.06105 | 0 | 109.4017 | 0 | 0.0006105 | 0 | 1.094 | 0 | 0.0006105 | 1.094 | 263538 | 47.1194 | 263537.9994
39031.5466 | 1448 | 0 | 39031.5466 | 2575 | 0 |  | 271.5 | 490.5 | 88.4005 | 0 | 157.2039 | 0 | 0.884 | 0 | 1.572 | 0 | 0.884 | 1.572 | 82.0704 | 2.3837 | 81.1864
39031.5487 | 2198 | 0 | 39031.5487 | 2277 | 0 |  | 456.5 | 675.5 | 134.188 | 0 | 139.011 | 0 | 1.3419 | 0 | 1.3901 | 0 | 1.3419 | 1.3901 | 19.9445 | 15.783 | 18.6026
39031.5509 | 2052 | 0 | 39031.5509 | 2422 | 0 |  | 641.5 | 860.5 | 125.2747 | 0 | 147.8632 | 0 | 1.2527 | 0 | 1.4786 | 0 | 1.2527 | 1.4786 | 28.4786 | 8.8514 | 27.2258
39031.553 | 2164 | 0 | 39031.553 | 2425 | 0 |  | 826 | 1045 | 132.1123 | 0 | 148.0464 | 0 | 1.3211 | 0 | 1.4805 | 0 | 1.3211 | 1.4805 | 21.829 | 8.7167 | 20.5079
39031.5551 | 2505 | 0 | 39031.5552 | 2445 | 0 |  | 1011 | 1230 | 152.9304 | 0 | 149.2674 | 0 | 1.5293 | 0 | 1.4927 | 0 | 1.5293 | 1.4927 | 5.2447 | 7.8274 | 3.7154
39031.5573 | 2156 | 0 | 39031.5573 | 2454 | 0 |  | 1195.5 | 1414.5 | 131.6239 | 0 | 149.8168 | 0 | 1.3162 | 0 | 1.4982 | 0 | 1.3162 | 1.4982 | 22.2811 | 7.4319 | 20.9648
39031.5594 | 1920 | 0 | 39031.5594 | 2481 | 0 |  | 1380.5 | 1599.5 | 117.2161 | 0 | 151.4652 | 0 | 1.1722 | 0 | 1.5147 | 0 | 1.1722 | 1.5147 | 37.3115 | 6.2628 | 36.1393
39031.5615 | 2130 | 0 | 39031.5616 | 2274 | 0 |  | 1565 | 1784 | 130.0366 | 0 | 138.8278 | 0 | 1.3004 | 0 | 1.3883 | 0 | 1.3004 | 1.3883 | 23.7737 | 15.9358 | 22.4733
39031.5637 | 2171 | 0 | 39031.5637 | 2620 | 0 |  | 1750 | 1969 | 132.5397 | 0 | 159.9512 | 0 | 1.3254 | 0 | 1.5995 | 0 | 1.3254 | 1.5995 | 21.4362 | 0.62519 | 20.1108
39031.5658 | 2364 | 0 | 39031.5658 | 2201 | 0 |  | 1934.5 | 2153.5 | 144.3223 | 0 | 134.3712 | 0 | 1.4432 | 0 | 1.3437 | 0 | 1.4432 | 1.3437 | 11.522 | 19.781 | 10.0788
39031.568 | 2514 | 0 | 39031.568 | 2444 | 0 |  | 2119.5 | 2338.5 | 153.4799 | 0 | 149.2063 | 0 | 1.5348 | 0 | 1.4921 | 0 | 1.5348 | 1.4921 | 4.8679 | 7.8715 | 3.3331
39031.5701 | 2083 | 302 | 39031.5701 | 1825 | 382 |  | 2304 | 2523 | 127.1673 | 18.4371 | 111.4164 | 23.3211 | 1.2717 | 0.18437 | 1.1142 | 0.23321 | 1.0873 | 0.88095 | 33.0569 | 282.3002 | 61.4654
39031.5722 | 1840 | 516 | 39031.5723 | 998 | 652 |  | 2489 | 2708 | 112.3321 | 31.5018 | 60.928 | 39.8046 | 1.1233 | 0.31502 | 0.60928 | 0.39805 | 0.8083 | 0.21123 | 48.6438 | 164.7678 | 33.8146

## C5-E10
Open Burn Test 8 |  |  | 2006-11-10 | 13:06 |  |  | Vs = |  | 158.8755 |  | R = | 100
Mix | 7-C | Tray A | IRMS | 1
0 | 150 kW |  | Bundle | Ch. 5 & 10 | Cable C | Odd - | Cable E |  | Even
Time-85 | N11 | N12 | Time-86 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R10-G | R5-10
39031.5423 | 1 | 0 | 39031.5423 | 1 | 0 |  | -100.5 | 118.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260138 | 260138 | 260137.9994
39031.5444 | 1 | 0 | 39031.5444 | 1 | 0 |  | 84 | 303 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260138 | 260138 | 260137.9994
39031.5465 | 2086 | 0 | 39031.5466 | 2340 | 0 |  | 269 | 488 | 127.3504 | 0 | 142.8571 | 0 | 1.2735 | 0 | 1.4286 | 0 | 1.2735 | 1.4286 | 24.7546 | 11.2128 | 23.481
39031.5487 | 2492 | 0 | 39031.5487 | 2326 | 0 |  | 453.5 | 672.5 | 152.1368 | 0 | 142.0024 | 0 | 1.5214 | 0 | 1.42 | 0 | 1.5214 | 1.42 | 4.4294 | 11.8822 | 2.908
39031.5508 | 2116 | 0 | 39031.5508 | 2169 | 0 |  | 638.5 | 857.5 | 129.1819 | 0 | 132.4176 | 0 | 1.2918 | 0 | 1.3242 | 0 | 1.2918 | 1.3242 | 22.9858 | 19.9806 | 21.694
39031.553 | 2376 | 0 | 39031.553 | 2085 | 0 |  | 823.5 | 1042.5 | 145.0549 | 0 | 127.2894 | 0 | 1.4505 | 0 | 1.2729 | 0 | 1.4505 | 1.2729 | 9.5278 | 24.8144 | 8.0772
39031.5551 | 2451 | 0 | 39031.5551 | 2104 | 0 |  | 1008 | 1227 | 149.6337 | 0 | 128.4493 | 0 | 1.4963 | 0 | 1.2845 | 0 | 1.4963 | 1.2845 | 6.1763 | 23.6873 | 4.6799
39031.5572 | 2039 | 0 | 39031.5572 | 2320 | 0 |  | 1192.5 | 1411.5 | 124.4811 | 0 | 141.6361 | 0 | 1.2448 | 0 | 1.4164 | 0 | 1.2448 | 1.4164 | 27.6302 | 12.1716 | 26.3854
39031.5594 | 2093 | 0 | 39031.5594 | 2586 | 0 |  | 1377.5 | 1596.5 | 127.7778 | 0 | 157.8755 | 0 | 1.2778 | 0 | 1.5788 | 0 | 1.2778 | 1.5788 | 24.3373 | 0.63341 | 23.0595
39031.5615 | 2313 | 0 | 39031.5615 | 2422 | 0 |  | 1562.5 | 1781.5 | 141.2088 | 0 | 147.8632 | 0 | 1.4121 | 0 | 1.4786 | 0 | 1.4121 | 1.4786 | 12.511 | 7.4476 | 11.0989
39031.5636 | 2368 | 0 | 39031.5637 | 2108 | 0 |  | 1747 | 1966 | 144.5665 | 0 | 128.6935 | 0 | 1.4457 | 0 | 1.2869 | 0 | 1.4457 | 1.2869 | 9.8978 | 23.4526 | 8.4521
39031.5658 | 2405 | 0 | 39031.5658 | 2540 | 0 |  | 1932 | 2151 | 146.8254 | 0 | 155.0672 | 0 | 1.4683 | 0 | 1.5507 | 0 | 1.4683 | 1.5507 | 8.2071 | 2.4559 | 6.7388
39031.5679 | 2435 | 0 | 39031.5679 | 2314 | 0 |  | 2116.5 | 2335.5 | 148.6569 | 0 | 141.2698 | 0 | 1.4866 | 0 | 1.4127 | 0 | 1.4866 | 1.4127 | 6.8739 | 12.4624 | 5.3874
39031.5701 | 1850 | 286 | 39031.5701 | 2015 | 355 |  | 2301.5 | 2520.5 | 112.9426 | 17.4603 | 123.0159 | 21.6728 | 1.1294 | 0.1746 | 1.2302 | 0.21673 | 0.95482 | 1.0134 | 76.6842 | 49.0685 | 53.6773
39031.5722 | 1342 | 533 | 39031.5722 | 1534 | 591 |  | 2486.5 | 2705.5 | 81.9292 | 32.5397 | 93.6508 | 36.0806 | 0.81929 | 0.3254 | 0.93651 | 0.36081 | 0.49389 | 0.5757 | 285.1978 | 145.2046 | 80.8139

## C5-E9
Open Burn Test 8 |  |  | 2006-11-10 | 13:06 |  |  | Vs = |  | 157.044 |  | R = | 100
Mix | 7-C | Tray A | IRMS | 1
0 | 150 kW |  | Bundle | Ch. 5 & 9 | Cable C | Odd - | Cable E |  | Odd
Time-83 | N11 | N12 | Time-84 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R9-G | R5-9
39031.5422 | 1 | 0 | 39031.5422 | 1 | 0 |  | -103.5 | 115.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257138 | 257138 | 257137.9994
39031.5444 | 1 | 0 | 39031.5444 | 1 | 0 |  | 81.5 | 300.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257138 | 257138 | 257137.9994
39031.5465 | 2306 | 0 | 39031.5465 | 2218 | 0 |  | 266 | 485 | 140.7814 | 0 | 135.409 | 0 | 1.4078 | 0 | 1.3541 | 0 | 1.4078 | 1.3541 | 11.5516 | 15.9775 | 10.1438
39031.5486 | 2012 | 0 | 39031.5487 | 2258 | 0 |  | 451 | 670 | 122.8327 | 0 | 137.851 | 0 | 1.2283 | 0 | 1.3785 | 0 | 1.2283 | 1.3785 | 27.8519 | 13.9229 | 26.6236
39031.5508 | 2130 | 1 | 39031.5508 | 2014 | 0 |  | 635.5 | 854.5 | 130.0366 | 0.06105 | 122.9548 | 0 | 1.3004 | 0.0006105 | 1.2295 | 0 | 1.2998 | 1.2295 | 20.814 | 27.7249 | 9580.9237
39031.5529 | 2057 | 0 | 39031.5529 | 2341 | 0 |  | 820.5 | 1039.5 | 125.58 | 0 | 142.9182 | 0 | 1.2558 | 0 | 1.4292 | 0 | 1.2558 | 1.4292 | 25.0549 | 9.8838 | 23.7991
39031.5551 | 1972 | 0 | 39031.5551 | 2428 | 0 |  | 1005.5 | 1224.5 | 120.3907 | 0 | 148.2295 | 0 | 1.2039 | 0 | 1.4823 | 0 | 1.2039 | 1.4823 | 30.4452 | 5.9465 | 29.2413
39031.5572 | 2438 | 0 | 39031.5572 | 2369 | 0 |  | 1190 | 1409 | 148.84 | 0 | 144.6276 | 0 | 1.4884 | 0 | 1.4463 | 0 | 1.4884 | 1.4463 | 5.5119 | 8.5851 | 4.0235
39031.5593 | 2315 | 0 | 39031.5594 | 2285 | 0 |  | 1374.5 | 1593.5 | 141.3309 | 0 | 139.4994 | 0 | 1.4133 | 0 | 1.395 | 0 | 1.4133 | 1.395 | 11.1179 | 12.5768 | 9.7046
39031.5615 | 2074 | 0 | 39031.5615 | 2403 | 0 |  | 1559.5 | 1778.5 | 126.6178 | 0 | 146.7033 | 0 | 1.2662 | 0 | 1.467 | 0 | 1.2662 | 1.467 | 24.0299 | 7.0487 | 22.7637
39031.5636 | 2556 | 0 | 39031.5636 | 2168 | 0 |  | 1744.5 | 1963.5 | 156.044 | 0 | 132.3565 | 0 | 1.5604 | 0 | 1.3236 | 0 | 1.5604 | 1.3236 | 0.64085 | 18.6522 | 0.91959
39031.5658 | 2371 | 0 | 39031.5658 | 2483 | 0 |  | 1929 | 2148 | 144.7497 | 0 | 151.5873 | 0 | 1.4475 | 0 | 1.5159 | 0 | 1.4475 | 1.5159 | 8.4935 | 3.5997 | 7.046
39031.5679 | 2310 | 0 | 39031.5679 | 2107 | 0 |  | 2114 | 2333 | 141.0256 | 0 | 128.6325 | 0 | 1.4103 | 0 | 1.2863 | 0 | 1.4103 | 1.2863 | 11.3584 | 22.0873 | 9.9482
39031.57 | 1990 | 417 | 39031.57 | 1826 | 226 |  | 2298.5 | 2517.5 | 121.4896 | 25.4579 | 111.4774 | 13.7973 | 1.2149 | 0.25458 | 1.1148 | 0.13797 | 0.96032 | 0.9768 | 67.166 | 59.0715 | 14.7276
39031.5722 | 1535 | 576 | 39031.5722 | 1579 | 302 |  | 2483.5 | 2702.5 | 93.7118 | 35.1648 | 96.398 | 18.4371 | 0.93712 | 0.35165 | 0.96398 | 0.18437 | 0.58547 | 0.77961 | 394.5476 | 82.7502 | 36.27

## C5-C6
Open Burn Test 8 |  |  | 2006-11-10 | 13:06 |  |  | Vs = |  | 157.7155 |  | R = | 100
Mix | 7-C | Tray A | IRMS | 1
0 | 150 kW |  | Bundle | Ch. 5 & 6 | Cable C | Odd-Even
Time-77 | N11 | N12 | Time-78 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R6-G | R5-6
39031.5421 | 1 | 0 | 39031.5422 | 1 | 0 |  | -112 | 107 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258238 | 258238 | 258237.9994
39031.5443 | 1 | 0 | 39031.5443 | 1 | 0 |  | 73 | 292 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258238 | 258238 | 258237.9994
39031.5464 | 1529 | 900 | 39031.5464 | 1454 | 758 |  | 257.5 | 476.5 | 93.3455 | 54.9451 | 88.7668 | 46.2759 | 0.93346 | 0.54945 | 0.88767 | 0.46276 | 0.384 | 0.42491 | 605.6151 | 197.846 | 11.3942
39031.5486 | 2518 | 0 | 39031.5486 | 1976 | 0 |  | 442.5 | 661.5 | 153.7241 | 0 | 120.6349 | 0 | 1.5372 | 0 | 1.2063 | 0 | 1.5372 | 1.2063 | 2.5965 | 30.7379 | 1.0593
39031.5507 | 2146 | 0 | 39031.5507 | 2042 | 0 |  | 627.5 | 846.5 | 131.0134 | 0 | 124.6642 | 0 | 1.3101 | 0 | 1.2466 | 0 | 1.3101 | 1.2466 | 20.3812 | 26.5122 | 19.071
39031.5528 | 2255 | 1 | 39031.5528 | 2091 | 1 |  | 812 | 1031 | 137.6679 | 0.06105 | 127.6557 | 0.06105 | 1.3767 | 0.0006105 | 1.2766 | 0.0006105 | 1.3761 | 1.2759 | 14.5962 | 23.6363 | 6258.7287
39031.555 | 2106 | 1 | 39031.555 | 2504 | 1 |  | 997 | 1216 | 128.5714 | 0.06105 | 152.8694 | 0.06105 | 1.2857 | 0.0006105 | 1.5287 | 0.0006105 | 1.2851 | 1.5281 | 23.0227 | 3.1769 | 1466.8157
39031.5571 | 2353 | 0 | 39031.5571 | 2450 | 0 |  | 1181.5 | 1400.5 | 143.6508 | 0 | 149.5726 | 0 | 1.4365 | 0 | 1.4957 | 0 | 1.4365 | 1.4957 | 9.7909 | 5.4441 | 8.3544
39031.5592 | 2048 | 1 | 39031.5593 | 2488 | 1 |  | 1366.5 | 1585.5 | 125.0305 | 0.06105 | 151.8926 | 0.06105 | 1.2503 | 0.0006105 | 1.5189 | 0.0006105 | 1.2497 | 1.5183 | 26.4913 | 3.841 | 1976.6176
39031.5614 | 2442 | 0 | 39031.5614 | 2195 | 0 |  | 1551 | 1770 | 149.0842 | 0 | 134.0049 | 0 | 1.4908 | 0 | 1.34 | 0 | 1.4908 | 1.34 | 5.7895 | 17.6938 | 4.2987
39031.5635 | 2086 | 0 | 39031.5635 | 2567 | 0 |  | 1736 | 1955 | 127.3504 | 0 | 156.7155 | 0 | 1.2735 | 0 | 1.5672 | 0 | 1.2735 | 1.5672 | 23.8437 | 0.6381 | 22.5702
39031.5657 | 2471 | 0 | 39031.5657 | 2545 | 0 |  | 1920.5 | 2139.5 | 150.8547 | 0 | 155.3724 | 0 | 1.5085 | 0 | 1.5537 | 0 | 1.5085 | 1.5537 | 4.548 | 1.5081 | 3.0394
39031.5678 | 2059 | 0 | 39031.5678 | 1993 | 0 |  | 2105.5 | 2324.5 | 125.7021 | 0 | 121.6728 | 0 | 1.257 | 0 | 1.2167 | 0 | 1.257 | 1.2167 | 25.4677 | 29.6227 | 24.2107
39031.5699 | 1588 | 346 | 39031.57 | 2110 | 372 |  | 2290.5 | 2509.5 | 96.9475 | 21.1233 | 128.8156 | 22.7106 | 0.96947 | 0.21123 | 1.2882 | 0.22711 | 0.75824 | 1.0611 | 2553.9147 | 28.7608 | 41.9218
39031.5721 | 1385 | 722 | 39031.5721 | 1513 | 672 |  | 2475 | 2694 | 84.5543 | 44.0781 | 92.3687 | 41.0256 | 0.84554 | 0.44078 | 0.92369 | 0.41026 | 0.40476 | 0.51343 | 778.3901 | 141.8346 | 38.6972

## B4-E10
Open Burn Test 8 |  |  | 2006-11-10 | 13:06 |  |  | Vs = |  | 160.5849 |  | R = | 100
Mix | 7-C | Tray A | IRMS | 1
0 | 150 kW |  | Bundle | Ch. 4 & 10 | Cable B | Even - | Cable E |  | Even
Time-71 | N11 | N12 | Time-72 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R10-G | R4-10
39031.542 | 1 | 0 | 39031.5421 | 1 | 0 |  | -120 | 99 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262938 | 262938 | 262937.9994
39031.5442 | 1 | 0 | 39031.5442 | 1 | 0 |  | 64.5 | 283.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262938 | 262938 | 262937.9994
39031.5463 | 1 | 0 | 39031.5463 | 2100 | 0 |  | 249.5 | 468.5 | 0.06105 | 0 | 128.2051 | 0 | 0.0006105 | 0 | 1.2821 | 0 | 0.0006105 | 1.2821 | 262938 | 25.2562 | 262937.9994
39031.5484 | 778 | 0 | 39031.5485 | 1982 | 0 |  | 434 | 653 | 47.4969 | 0 | 121.0012 | 0 | 0.47497 | 0 | 1.21 | 0 | 0.47497 | 1.21 | 238.0951 | 32.7134 | 237.6201
39031.5506 | 1963 | 0 | 39031.5506 | 2065 | 0 |  | 619 | 838 | 119.8413 | 0 | 126.0684 | 0 | 1.1984 | 0 | 1.2607 | 0 | 1.1984 | 1.2607 | 33.998 | 27.3792 | 32.7995
39031.5527 | 2149 | 0 | 39031.5527 | 2075 | 0 |  | 803.5 | 1022.5 | 131.1966 | 0 | 126.6789 | 0 | 1.312 | 0 | 1.2668 | 0 | 1.312 | 1.2668 | 22.4002 | 26.7653 | 21.0882
39031.5549 | 2015 | 0 | 39031.5549 | 2183 | 0 |  | 988.5 | 1207.5 | 123.0159 | 0 | 133.2723 | 0 | 1.2302 | 0 | 1.3327 | 0 | 1.2302 | 1.3327 | 30.54 | 20.4938 | 29.3098
39031.557 | 1985 | 0 | 39031.557 | 2407 | 0 |  | 1173.5 | 1392.5 | 121.1844 | 0 | 146.9475 | 0 | 1.2118 | 0 | 1.4695 | 0 | 1.2118 | 1.4695 | 32.5128 | 9.2804 | 31.301
39031.5591 | 2522 | 0 | 39031.5592 | 2028 | 0 |  | 1358 | 1577 | 153.9683 | 0 | 123.8095 | 0 | 1.5397 | 0 | 1.2381 | 0 | 1.5397 | 1.2381 | 4.2974 | 29.7032 | 2.7577
39031.5613 | 2266 | 0 | 39031.5613 | 2189 | 0 |  | 1543 | 1762 | 138.3394 | 0 | 133.6386 | 0 | 1.3834 | 0 | 1.3364 | 0 | 1.3834 | 1.3364 | 16.0803 | 20.1635 | 14.6969
39031.5634 | 2108 | 0 | 39031.5634 | 2173 | 0 |  | 1727.5 | 1946.5 | 128.6935 | 0 | 132.6618 | 0 | 1.2869 | 0 | 1.3266 | 0 | 1.2869 | 1.3266 | 24.7808 | 21.0483 | 23.4939
39031.5656 | 2469 | 0 | 39031.5656 | 2614 | 0 |  | 1912.5 | 2131.5 | 150.7326 | 0 | 159.5849 | 0 | 1.5073 | 0 | 1.5958 | 0 | 1.5073 | 1.5958 | 6.5362 | 0.62663 | 5.0289
39031.5677 | 2587 | 0 | 39031.5677 | 2117 | 0 |  | 2097 | 2316 | 157.9365 | 0 | 129.243 | 0 | 1.5794 | 0 | 1.2924 | 0 | 1.5794 | 1.2924 | 1.6768 | 24.2504 | 0.097481
39031.5698 | 1939 | 53 | 39031.5699 | 2240 | 286 |  | 2282 | 2501 | 118.3761 | 3.2357 | 136.7521 | 17.4603 | 1.1838 | 0.032357 | 1.3675 | 0.1746 | 1.1514 | 1.1929 | 40.2632 | 31.3893 | 287.7562
39031.572 | 1408 | 868 | 39031.572 | 1529 | 504 |  | 2466.5 | 2685.5 | 85.9585 | 52.9915 | 93.3455 | 30.7692 | 0.85958 | 0.52991 | 0.93346 | 0.30769 | 0.32967 | 0.62576 | 308.1262 | 605.782 | 35.0425

## B4-E9
Open Burn Test 8 |  |  | 2006-11-10 | 13:06 |  |  | Vs = |  | 158.7534 |  | R = | 100
Mix | 7-C | Tray A | IRMS | 1
0 | 150 kW |  | Bundle | Ch. 4 & 9 | Cable B | Even - | Cable E |  | Odd
Time-69 | N11 | N12 | Time-70 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R9-G | R4-9
39031.542 | 1 | 0 | 39031.542 | 1 | 0 |  | -123 | 96 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259938 | 259938 | 259937.9994
39031.5441 | 1 | 0 | 39031.5442 | 1 | 0 |  | 61.5 | 280.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259938 | 259938 | 259937.9994
39031.5463 | 1 | 0 | 39031.5463 | 2530 | 0 |  | 246.5 | 465.5 | 0.06105 | 0 | 154.4567 | 0 | 0.0006105 | 0 | 1.5446 | 0 | 0.0006105 | 1.5446 | 259938 | 2.7818 | 259937.9994
39031.5484 | 979 | 0 | 39031.5484 | 2421 | 0 |  | 431.5 | 650.5 | 59.768 | 0 | 147.8022 | 0 | 0.59768 | 0 | 1.478 | 0 | 0.59768 | 1.478 | 165.6159 | 7.4093 | 165.0183
39031.5506 | 2258 | 0 | 39031.5506 | 2570 | 0 |  | 616 | 835 | 137.851 | 0 | 156.8987 | 0 | 1.3785 | 0 | 1.569 | 0 | 1.3785 | 1.569 | 15.163 | 1.1821 | 13.7845
39031.5527 | 2216 | 0 | 39031.5527 | 2465 | 0 |  | 801 | 1020 | 135.2869 | 0 | 150.4884 | 0 | 1.3529 | 0 | 1.5049 | 0 | 1.3529 | 1.5049 | 17.3457 | 5.4921 | 15.9928
39031.5548 | 2395 | 0 | 39031.5548 | 2552 | 0 |  | 985.5 | 1204.5 | 146.2149 | 0 | 155.7998 | 0 | 1.4621 | 0 | 1.558 | 0 | 1.4621 | 1.558 | 8.5754 | 1.8958 | 7.1132
39031.557 | 2194 | 0 | 39031.557 | 2067 | 0 |  | 1170.5 | 1389.5 | 133.9438 | 0 | 126.1905 | 0 | 1.3394 | 0 | 1.2619 | 0 | 1.3394 | 1.2619 | 18.5223 | 25.8045 | 17.1829
39031.5591 | 2584 | 0 | 39031.5591 | 2350 | 0 |  | 1355.5 | 1574.5 | 157.7534 | 0 | 143.4676 | 0 | 1.5775 | 0 | 1.4347 | 0 | 1.5775 | 1.4347 | 0.6339 | 10.6545 | 0.94363
39031.5612 | 2263 | 0 | 39031.5613 | 2045 | 0 |  | 1540 | 1759 | 138.1563 | 0 | 124.8474 | 0 | 1.3816 | 0 | 1.2485 | 0 | 1.3816 | 1.2485 | 14.9085 | 27.1579 | 13.527
39031.5634 | 2506 | 0 | 39031.5634 | 2287 | 0 |  | 1724.5 | 1943.5 | 152.9915 | 0 | 139.6215 | 0 | 1.5299 | 0 | 1.3962 | 0 | 1.5299 | 1.3962 | 3.7662 | 13.7027 | 2.2362
39031.5655 | 2394 | 0 | 39031.5655 | 2333 | 0 |  | 1909.5 | 2128.5 | 146.1538 | 0 | 142.4298 | 0 | 1.4615 | 0 | 1.4243 | 0 | 1.4615 | 1.4243 | 8.6207 | 11.4608 | 7.1592
39031.5677 | 2028 | 0 | 39031.5677 | 2483 | 0 |  | 2094.5 | 2313.5 | 123.8095 | 0 | 151.5873 | 0 | 1.2381 | 0 | 1.5159 | 0 | 1.2381 | 1.5159 | 28.2239 | 4.7273 | 26.9858
39031.5698 | 1982 | 0 | 39031.5698 | 1951 | 0 |  | 2279 | 2498 | 121.0012 | 0 | 119.1087 | 0 | 1.21 | 0 | 1.1911 | 0 | 1.21 | 1.1911 | 31.1998 | 33.2845 | 29.9898
39031.5719 | 1172 | 728 | 39031.572 | 1724 | 608 |  | 2463.5 | 2682.5 | 71.5507 | 44.4444 | 105.2503 | 37.1184 | 0.71551 | 0.44444 | 1.0525 | 0.37118 | 0.27106 | 0.68132 | 191.1439 | 240.0423 | 67.9137

## B4-D8
Open Burn Test 8 |  |  | 2006-11-10 | 13:06 |  |  | Vs = |  | 160.2186 |  | R = | 100
Mix | 7-C | Tray A | IRMS | 1
0 | 150 kW |  | Bundle | Ch. 4 & 8 | Cable B | Even - | Cable D |  | Even
Time-67 | N11 | N12 | Time-68 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R8-G | R4-8
39031.542 | 1 | 0 | 39031.542 | 1 | 0 |  | -125.5 | 93.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262338 | 262338 | 262337.9994
39031.5441 | 1 | 0 | 39031.5441 | 1 | 0 |  | 59 | 278 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262338 | 262338 | 262337.9994
39031.5462 | 1 | 0 | 39031.5463 | 2147 | 0 |  | 244 | 463 | 0.06105 | 0 | 131.0745 | 0 | 0.0006105 | 0 | 1.3107 | 0 | 0.0006105 | 1.3107 | 262338 | 22.2347 | 262337.9994
39031.5484 | 946 | 0 | 39031.5484 | 2051 | 0 |  | 428.5 | 647.5 | 57.7534 | 0 | 125.2137 | 0 | 0.57753 | 0 | 1.2521 | 0 | 0.57753 | 1.2521 | 177.4186 | 27.9561 | 176.8411
39031.5505 | 2194 | 0 | 39031.5505 | 2151 | 0 |  | 613.5 | 832.5 | 133.9438 | 0 | 131.3187 | 0 | 1.3394 | 0 | 1.3132 | 0 | 1.3394 | 1.3132 | 19.6162 | 22.0074 | 18.2768
39031.5527 | 2226 | 0 | 39031.5527 | 2400 | 0 |  | 798 | 1017 | 135.8974 | 0 | 146.5201 | 0 | 1.359 | 0 | 1.4652 | 0 | 1.359 | 1.4652 | 17.8967 | 9.3492 | 16.5377
39031.5548 | 2572 | 0 | 39031.5548 | 2563 | 0 |  | 983 | 1202 | 157.0208 | 0 | 156.4713 | 0 | 1.5702 | 0 | 1.5647 | 0 | 1.5702 | 1.5647 | 2.0365 | 2.3948 | 0.46634
39031.5569 | 2471 | 0 | 39031.557 | 2281 | 0 |  | 1167.5 | 1386.5 | 150.8547 | 0 | 139.2552 | 0 | 1.5085 | 0 | 1.3926 | 0 | 1.5085 | 1.3926 | 6.2072 | 15.0539 | 4.6987
39031.5591 | 2036 | 0 | 39031.5591 | 2024 | 0 |  | 1352.5 | 1571.5 | 124.2979 | 0 | 123.5653 | 0 | 1.243 | 0 | 1.2357 | 0 | 1.243 | 1.2357 | 28.8988 | 29.663 | 27.6558
39031.5612 | 2045 | 0 | 39031.5612 | 2091 | 0 |  | 1537.5 | 1756.5 | 124.8474 | 0 | 127.6557 | 0 | 1.2485 | 0 | 1.2766 | 0 | 1.2485 | 1.2766 | 28.3315 | 25.5084 | 27.0831
39031.5634 | 2436 | 0 | 39031.5634 | 2507 | 0 |  | 1722 | 1941 | 148.7179 | 0 | 153.0525 | 0 | 1.4872 | 0 | 1.5305 | 0 | 1.4872 | 1.5305 | 7.7332 | 4.6821 | 6.246
39031.5655 | 2185 | 0 | 39031.5655 | 2608 | 0 |  | 1906.5 | 2125.5 | 133.3944 | 0 | 159.2186 | 0 | 1.3339 | 0 | 1.5922 | 0 | 1.3339 | 1.5922 | 20.1089 | 0.62807 | 18.775
39031.5676 | 2260 | 0 | 39031.5677 | 2090 | 0 |  | 2091.5 | 2310.5 | 137.9731 | 0 | 127.5946 | 0 | 1.3797 | 0 | 1.2759 | 0 | 1.3797 | 1.2759 | 16.123 | 25.5684 | 14.7433
39031.5698 | 2099 | 0 | 39031.5698 | 2210 | 0 |  | 2276 | 2495 | 128.1441 | 0 | 134.9206 | 0 | 1.2814 | 0 | 1.3492 | 0 | 1.2814 | 1.3492 | 25.03 | 18.7502 | 23.7486
39031.5719 | 1433 | 174 | 39031.5719 | 1010 | 302 |  | 2461 | 2680 | 87.4847 | 10.6227 | 61.6606 | 18.4371 | 0.87485 | 0.10623 | 0.61661 | 0.18437 | 0.76862 | 0.43223 | 97.9825 | 403.8154 | 468.6465

## B4-D7
Open Burn Test 8 |  |  | 2006-11-10 | 13:06 |  |  | Vs = |  | 159.4249 |  | R = | 100
Mix | 7-C | Tray A | IRMS | 1
0 | 150 kW |  | Bundle | Ch. 4 & 7 | Cable B | Even - | Cable D |  | Odd
Time-65 | N11 | N12 | Time-66 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R7-G | R4-7
39031.5419 | 1 | 0 | 39031.542 | 1 | 0 |  | -128.5 | 90.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261038 | 261038 | 261037.9994
39031.5441 | 1 | 0 | 39031.5441 | 1 | 0 |  | 56 | 275 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261038 | 261038 | 261037.9994
39031.5462 | 1 | 0 | 39031.5462 | 2051 | 0 |  | 241 | 460 | 0.06105 | 0 | 125.2137 | 0 | 0.0006105 | 0 | 1.2521 | 0 | 0.0006105 | 1.2521 | 261038 | 27.3223 | 261037.9994
39031.5484 | 42 | 0 | 39031.5484 | 2153 | 0 |  | 425.5 | 644.5 | 2.5641 | 0 | 131.4408 | 0 | 0.025641 | 0 | 1.3144 | 0 | 0.025641 | 1.3144 | 6117.5714 | 21.2903 | 6117.5458
39031.5505 | 1950 | 0 | 39031.5505 | 2080 | 0 |  | 610.5 | 829.5 | 119.0476 | 0 | 126.9841 | 0 | 1.1905 | 0 | 1.2698 | 0 | 1.1905 | 1.2698 | 33.9169 | 25.5471 | 32.7264
39031.5526 | 2564 | 0 | 39031.5527 | 2514 | 0 |  | 795.5 | 1014.5 | 156.5324 | 0 | 153.4799 | 0 | 1.5653 | 0 | 1.5348 | 0 | 1.5653 | 1.5348 | 1.8479 | 3.8735 | 0.28257
39031.5548 | 2361 | 0 | 39031.5548 | 2578 | 0 |  | 980 | 1199 | 144.1392 | 0 | 157.3871 | 0 | 1.4414 | 0 | 1.5739 | 0 | 1.4414 | 1.5739 | 10.6048 | 1.2948 | 9.1634
39031.5569 | 2001 | 0 | 39031.5569 | 2347 | 0 |  | 1165 | 1384 | 122.1612 | 0 | 143.2845 | 0 | 1.2216 | 0 | 1.4328 | 0 | 1.2216 | 1.4328 | 30.5037 | 11.2646 | 29.2821
39031.5591 | 2575 | 0 | 39031.5591 | 2305 | 0 |  | 1349.5 | 1568.5 | 157.2039 | 0 | 140.7204 | 0 | 1.572 | 0 | 1.4072 | 0 | 1.572 | 1.4072 | 1.4128 | 13.292 | 0.15922
39031.5612 | 2300 | 0 | 39031.5612 | 2595 | 0 |  | 1534.5 | 1753.5 | 140.4151 | 0 | 158.4249 | 0 | 1.4042 | 0 | 1.5842 | 0 | 1.4042 | 1.5842 | 13.5383 | 0.63121 | 12.1341
39031.5633 | 2431 | 0 | 39031.5633 | 2195 | 0 |  | 1719 | 1938 | 148.4127 | 0 | 134.0049 | 0 | 1.4841 | 0 | 1.34 | 0 | 1.4841 | 1.34 | 7.42 | 18.9695 | 5.9359
39031.5655 | 2351 | 0 | 39031.5655 | 2591 | 0 |  | 1904 | 2123 | 143.5287 | 0 | 158.1807 | 0 | 1.4353 | 0 | 1.5818 | 0 | 1.4353 | 1.5818 | 11.0753 | 0.78657 | 9.64
39031.5676 | 2187 | 0 | 39031.5676 | 2085 | 0 |  | 2088.5 | 2307.5 | 133.5165 | 0 | 127.2894 | 0 | 1.3352 | 0 | 1.2729 | 0 | 1.3352 | 1.2729 | 19.4047 | 25.246 | 18.0695
39031.5697 | 2105 | 0 | 39031.5698 | 2271 | 0 |  | 2273.5 | 2492.5 | 128.5104 | 0 | 138.6447 | 0 | 1.2851 | 0 | 1.3864 | 0 | 1.2851 | 1.3864 | 24.0561 | 14.9881 | 22.771
39031.5719 | 1449 | 395 | 39031.5719 | 1693 | 181 |  | 2458 | 2677 | 88.4615 | 24.1148 | 103.3578 | 11.0501 | 0.88462 | 0.24115 | 1.0336 | 0.1105 | 0.64347 | 0.92308 | 268.6604 | 63.572 | 75.5041

## B4-C6
Open Burn Test 8 |  |  | 2006-11-10 | 13:06 |  |  | Vs = |  | 159.1197 |  | R = | 100
Mix | 7-C | Tray A | IRMS | 1
0 | 150 kW |  | Bundle | Ch. 4 & 6 | Cable B | Even - | Cable C |  | Even
Time-63 | N11 | N12 | Time-64 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R6-G | R4-6
39031.5419 | 1 | 0 | 39031.5419 | 1 | 0 |  | -131.5 | 87.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260538 | 260538 | 260537.9994
39031.5441 | 1 | 0 | 39031.5441 | 1 | 0 |  | 53.5 | 272.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260538 | 260538 | 260537.9994
39031.5462 | 1 | 0 | 39031.5462 | 854 | 0 |  | 238 | 457 | 0.06105 | 0 | 52.1368 | 0 | 0.0006105 | 0 | 0.52137 | 0 | 0.0006105 | 0.52137 | 260538 | 205.1967 | 260537.9994
39031.5483 | 483 | 0 | 39031.5483 | 2486 | 0 |  | 423 | 642 | 29.4872 | 0 | 151.7705 | 0 | 0.29487 | 0 | 1.5177 | 0 | 0.29487 | 1.5177 | 439.6232 | 4.8423 | 439.3283
39031.5505 | 2243 | 0 | 39031.5505 | 2511 | 0 |  | 607.5 | 826.5 | 136.9353 | 0 | 153.2967 | 0 | 1.3694 | 0 | 1.533 | 0 | 1.3694 | 1.533 | 16.2006 | 3.7985 | 14.8313
39031.5526 | 2054 | 0 | 39031.5526 | 2094 | 0 |  | 792.5 | 1011.5 | 125.3968 | 0 | 127.8388 | 0 | 1.254 | 0 | 1.2784 | 0 | 1.254 | 1.2784 | 26.8929 | 24.469 | 25.6389
39031.5547 | 2504 | 0 | 39031.5548 | 2418 | 0 |  | 977.5 | 1196.5 | 152.8694 | 0 | 147.619 | 0 | 1.5287 | 0 | 1.4762 | 0 | 1.5287 | 1.4762 | 4.0887 | 7.7907 | 2.56
39031.5569 | 2272 | 0 | 39031.5569 | 2487 | 0 |  | 1162 | 1381 | 138.7057 | 0 | 151.8315 | 0 | 1.3871 | 0 | 1.5183 | 0 | 1.3871 | 1.5183 | 14.7174 | 4.8002 | 13.3304
39031.559 | 2150 | 0 | 39031.559 | 2208 | 0 |  | 1346.5 | 1565.5 | 131.2576 | 0 | 134.7985 | 0 | 1.3126 | 0 | 1.348 | 0 | 1.3126 | 1.348 | 21.227 | 18.0426 | 19.9144
39031.5612 | 1998 | 0 | 39031.5612 | 2550 | 0 |  | 1531.5 | 1750.5 | 121.978 | 0 | 155.6777 | 0 | 1.2198 | 0 | 1.5568 | 0 | 1.2198 | 1.5568 | 30.4494 | 2.211 | 29.2297
39031.5633 | 2057 | 0 | 39031.5633 | 2142 | 0 |  | 1716.5 | 1935.5 | 125.58 | 0 | 130.7692 | 0 | 1.2558 | 0 | 1.3077 | 0 | 1.2558 | 1.3077 | 26.7078 | 21.6797 | 25.452
39031.5654 | 2376 | 0 | 39031.5655 | 2309 | 0 |  | 1901 | 2120 | 145.0549 | 0 | 140.9646 | 0 | 1.4505 | 0 | 1.4096 | 0 | 1.4505 | 1.4096 | 9.6961 | 12.8792 | 8.2456
39031.5676 | 2590 | 0 | 39031.5676 | 2442 | 0 |  | 2086 | 2305 | 158.1197 | 0 | 149.0842 | 0 | 1.5812 | 0 | 1.4908 | 0 | 1.5812 | 1.4908 | 0.63243 | 6.7314 | 0.94876
39031.5697 | 2171 | 0 | 39031.5697 | 2311 | 0 |  | 2270.5 | 2489.5 | 132.5397 | 0 | 141.0867 | 0 | 1.3254 | 0 | 1.4109 | 0 | 1.3254 | 1.4109 | 20.0544 | 12.7815 | 18.729
39031.5719 | 1187 | 481 | 39031.5719 | 1743 | 445 |  | 2455.5 | 2674.5 | 72.4664 | 29.3651 | 106.4103 | 27.1673 | 0.72466 | 0.29365 | 1.0641 | 0.27167 | 0.43101 | 0.79243 | 6837.7397 | 70.1942 | 80.4619

## B4-C5
Open Burn Test 8 |  |  | 2006-11-10 | 13:06 |  |  | Vs = |  | 159.9133 |  | R = | 100
Mix | 7-C | Tray A | IRMS | 1
0 | 150 kW |  | Bundle | Ch. 4 & 5 | Cable B | Even - | Cable C |  | Odd
Time-61 | N11 | N12 | Time-62 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R5-G | R4-5
39031.5419 | 0 | 0 | 39031.5419 | 1 | 0 |  | -134 | 85 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 523776 | 261838 | 523775.9997
39031.544 | 1 | 0 | 39031.544 | 1 | 0 |  | 50.5 | 269.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261838 | 261838 | 261837.9994
39031.5462 | 2 | 0 | 39031.5462 | 299 | 0 |  | 235.5 | 454.5 | 0.1221 | 0 | 18.254 | 0 | 0.001221 | 0 | 0.18254 | 0 | 0.001221 | 0.18254 | 130869 | 776.0468 | 130868.9988
39031.5483 | 197 | 0 | 39031.5483 | 1982 | 0 |  | 420 | 639 | 12.0269 | 0 | 121.0012 | 0 | 0.12027 | 0 | 1.21 | 0 | 0.12027 | 1.21 | 1229.6345 | 32.1584 | 1229.5142
39031.5504 | 2318 | 0 | 39031.5505 | 2503 | 0 |  | 605 | 824 | 141.514 | 0 | 152.8083 | 0 | 1.4151 | 0 | 1.5281 | 0 | 1.4151 | 1.5281 | 13.0017 | 4.6496 | 11.5866
39031.5526 | 2518 | 0 | 39031.5526 | 2053 | 0 |  | 789.5 | 1008.5 | 153.7241 | 0 | 125.3358 | 0 | 1.5372 | 0 | 1.2534 | 0 | 1.5372 | 1.2534 | 4.0262 | 27.5879 | 2.489
39031.5547 | 2272 | 0 | 39031.5547 | 2004 | 0 |  | 974.5 | 1193.5 | 138.7057 | 0 | 122.3443 | 0 | 1.3871 | 0 | 1.2234 | 0 | 1.3871 | 1.2234 | 15.2896 | 30.7076 | 13.9026
39031.5569 | 2234 | 0 | 39031.5569 | 2449 | 0 |  | 1159.5 | 1378.5 | 136.3858 | 0 | 149.5116 | 0 | 1.3639 | 0 | 1.4951 | 0 | 1.3639 | 1.4951 | 17.2507 | 6.9571 | 15.8868
39031.559 | 2523 | 0 | 39031.559 | 2167 | 0 |  | 1344 | 1563 | 154.0293 | 0 | 132.2955 | 0 | 1.5403 | 0 | 1.323 | 0 | 1.5403 | 1.323 | 3.8201 | 20.8759 | 2.2798
39031.5611 | 2293 | 0 | 39031.5611 | 2037 | 0 |  | 1528.5 | 1747.5 | 139.9878 | 0 | 124.359 | 0 | 1.3999 | 0 | 1.2436 | 0 | 1.3999 | 1.2436 | 14.2338 | 28.5901 | 12.8339
39031.5633 | 2603 | 0 | 39031.5633 | 2182 | 0 |  | 1713.5 | 1932.5 | 158.9133 | 0 | 133.2112 | 0 | 1.5891 | 0 | 1.3321 | 0 | 1.5891 | 1.3321 | 0.62927 | 20.0449 | 0.95986
39031.5654 | 2492 | 0 | 39031.5654 | 2580 | 0 |  | 1898.5 | 2117.5 | 152.1368 | 0 | 157.5092 | 0 | 1.5214 | 0 | 1.5751 | 0 | 1.5214 | 1.5751 | 5.1116 | 1.5264 | 3.5902
39031.5675 | 2349 | 0 | 39031.5676 | 1984 | 0 |  | 2083 | 2302 | 143.4066 | 0 | 121.1233 | 0 | 1.4341 | 0 | 1.2112 | 0 | 1.4341 | 1.2112 | 11.5104 | 32.0252 | 10.0764
39031.5697 | 2234 | 0 | 39031.5697 | 2003 | 0 |  | 2268 | 2487 | 136.3858 | 0 | 122.2833 | 0 | 1.3639 | 0 | 1.2228 | 0 | 1.3639 | 1.2228 | 17.2507 | 30.7728 | 15.8868
39031.5718 | 1057 | 681 | 39031.5718 | 1634 | 506 |  | 2452.5 | 2671.5 | 64.5299 | 41.5751 | 99.7558 | 30.8913 | 0.6453 | 0.41575 | 0.99756 | 0.30891 | 0.22955 | 0.68864 | 300.492 | 473.1119 | 106.8416

## B3-E10
Open Burn Test 8 |  |  | 2006-11-10 | 13:06 |  |  | Vs = |  | 158.7534 |  | R = | 100
Mix | 7-C | Tray A | IRMS | 1
0 | 150 kW |  | Bundle | Ch. 3 & 10 | Ch. 3 & 9 | Cable B | Odd - |  | Cable E | Even
Time-55 | N11 | N12 | Time-56 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R10-G | R3-10
39031.5418 | 1 | 0 | 39031.5418 | 1 | 0 |  | -142.5 | 76.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259938 | 259938 | 259937.9994
39031.5439 | 1 | 0 | 39031.5439 | 1 | 0 |  | 42 | 261 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259938 | 259938 | 259937.9994
39031.5461 | 1 | 0 | 39031.5461 | 2563 | 0 |  | 227 | 446 | 0.06105 | 0 | 156.4713 | 0 | 0.0006105 | 0 | 1.5647 | 0 | 0.0006105 | 1.5647 | 259938 | 1.4584 | 259937.9994
39031.5482 | 1115 | 0 | 39031.5482 | 2380 | 0 |  | 411.5 | 630.5 | 68.0708 | 0 | 145.2991 | 0 | 0.68071 | 0 | 1.453 | 0 | 0.68071 | 1.453 | 133.2179 | 9.2597 | 132.5372
39031.5503 | 1891 | 0 | 39031.5503 | 2127 | 0 |  | 596.5 | 815.5 | 115.4457 | 0 | 129.8535 | 0 | 1.1545 | 0 | 1.2985 | 0 | 1.1545 | 1.2985 | 37.5135 | 22.2558 | 36.359
39031.5525 | 2119 | 0 | 39031.5525 | 2162 | 0 |  | 781.5 | 1000.5 | 129.3651 | 0 | 131.9902 | 0 | 1.2937 | 0 | 1.3199 | 0 | 1.2937 | 1.3199 | 22.7173 | 20.2766 | 21.4237
39031.5546 | 2303 | 0 | 39031.5546 | 2575 | 0 |  | 966 | 1185 | 140.5983 | 0 | 157.2039 | 0 | 1.406 | 0 | 1.572 | 0 | 1.406 | 1.572 | 12.9127 | 0.98563 | 11.5067
39031.5567 | 2212 | 0 | 39031.5568 | 2584 | 0 |  | 1151 | 1370 | 135.0427 | 0 | 157.7534 | 0 | 1.3504 | 0 | 1.5775 | 0 | 1.3504 | 1.5775 | 17.5579 | 0.6339 | 16.2074
39031.5589 | 2507 | 0 | 39031.5589 | 2550 | 0 |  | 1335.5 | 1554.5 | 153.0525 | 0 | 155.6777 | 0 | 1.5305 | 0 | 1.5568 | 0 | 1.5305 | 1.5568 | 3.7248 | 1.9757 | 2.1942
39031.561 | 2445 | 0 | 39031.561 | 2164 | 0 |  | 1520.5 | 1739.5 | 149.2674 | 0 | 132.1123 | 0 | 1.4927 | 0 | 1.3211 | 0 | 1.4927 | 1.3211 | 6.355 | 20.1654 | 4.8623
39031.5632 | 2071 | 0 | 39031.5632 | 2484 | 0 |  | 1705 | 1924 | 126.4347 | 0 | 151.6484 | 0 | 1.2643 | 0 | 1.5165 | 0 | 1.2643 | 1.5165 | 25.5616 | 4.6852 | 24.2972
39031.5653 | 2092 | 0 | 39031.5653 | 2050 | 0 |  | 1890 | 2109 | 127.7167 | 0 | 125.1526 | 0 | 1.2772 | 0 | 1.2515 | 0 | 1.2772 | 1.2515 | 24.3011 | 26.8478 | 23.024
39031.5674 | 2269 | 0 | 39031.5675 | 2107 | 0 |  | 2074.5 | 2293.5 | 138.5226 | 0 | 128.6325 | 0 | 1.3852 | 0 | 1.2863 | 0 | 1.3852 | 1.2863 | 14.6047 | 23.4162 | 13.2194
39031.5696 | 2502 | 0 | 39031.5696 | 1947 | 0 |  | 2259.5 | 2478.5 | 152.7473 | 0 | 118.8645 | 0 | 1.5275 | 0 | 1.1886 | 0 | 1.5275 | 1.1886 | 3.9321 | 33.5583 | 2.4046
39031.5717 | 1263 | 687 | 39031.5717 | 1413 | 500 |  | 2444.5 | 2663.5 | 77.1062 | 41.9414 | 86.2637 | 30.525 | 0.77106 | 0.41941 | 0.86264 | 0.30525 | 0.35165 | 0.55739 | 2194.8517 | 133.3806 | 54.1051

## B3-E9
Open Burn Test 8 |  |  | 2006-11-10 | 13:06 |  |  | Vs = |  | 160.2796 |  | R = | 100
Mix | 7-C | Tray A | IRMS | 1
0 | 150 kW |  | Bundle | Ch. 3 & 9 | Cable B | Odd - | Cable E |  | Odd
Time-53 | N11 | N12 | Time-54 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R9-G | R3-9
39031.5417 | 1 | 0 | 39031.5418 | 1 | 0 |  | -145.5 | 73.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262438 | 262438 | 262437.9994
39031.5439 | 1 | 0 | 39031.5439 | 1 | 0 |  | 39.5 | 258.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262438 | 262438 | 262437.9994
39031.546 | 1 | 0 | 39031.546 | 2228 | 0 |  | 224 | 443 | 0.06105 | 0 | 136.0195 | 0 | 0.0006105 | 0 | 1.3602 | 0 | 0.0006105 | 1.3602 | 262438 | 17.8357 | 262437.9994
39031.5482 | 344 | 0 | 39031.5482 | 1997 | 0 |  | 409 | 628 | 21.0012 | 0 | 121.917 | 0 | 0.21001 | 0 | 1.2192 | 0 | 0.21001 | 1.2192 | 663.1919 | 31.4662 | 662.9818
39031.5503 | 2446 | 0 | 39031.5503 | 2062 | 0 |  | 593.5 | 812.5 | 149.3284 | 0 | 125.8852 | 0 | 1.4933 | 0 | 1.2589 | 0 | 1.4933 | 1.2589 | 7.3336 | 27.322 | 5.8403
39031.5524 | 2130 | 0 | 39031.5525 | 2051 | 0 |  | 778.5 | 997.5 | 130.0366 | 0 | 125.2137 | 0 | 1.3004 | 0 | 1.2521 | 0 | 1.3004 | 1.2521 | 23.2573 | 28.0049 | 21.9569
39031.5546 | 2179 | 0 | 39031.5546 | 2011 | 0 |  | 963.5 | 1182.5 | 133.0281 | 0 | 122.7717 | 0 | 1.3303 | 0 | 1.2277 | 0 | 1.3303 | 1.2277 | 20.4855 | 30.551 | 19.1553
39031.5567 | 1980 | 0 | 39031.5567 | 2602 | 0 |  | 1148 | 1367 | 120.8791 | 0 | 158.8523 | 0 | 1.2088 | 0 | 1.5885 | 0 | 1.2088 | 1.5885 | 32.5949 | 0.89854 | 31.3862
39031.5589 | 2383 | 0 | 39031.5589 | 2187 | 0 |  | 1332.5 | 1551.5 | 145.4823 | 0 | 133.5165 | 0 | 1.4548 | 0 | 1.3352 | 0 | 1.4548 | 1.3352 | 10.1712 | 20.0448 | 8.7164
39031.561 | 2095 | 0 | 39031.561 | 2609 | 0 |  | 1517.5 | 1736.5 | 127.8999 | 0 | 159.2796 | 0 | 1.279 | 0 | 1.5928 | 0 | 1.279 | 1.5928 | 25.3165 | 0.62783 | 24.0375
39031.5631 | 2031 | 0 | 39031.5631 | 2602 | 0 |  | 1702.5 | 1921.5 | 123.9927 | 0 | 158.8523 | 0 | 1.2399 | 0 | 1.5885 | 0 | 1.2399 | 1.5885 | 29.2654 | 0.89854 | 28.0255
39031.5653 | 2189 | 0 | 39031.5653 | 2293 | 0 |  | 1887 | 2106 | 133.6386 | 0 | 139.9878 | 0 | 1.3364 | 0 | 1.3999 | 0 | 1.3364 | 1.3999 | 19.9351 | 14.4954 | 18.5987
39031.5674 | 2363 | 0 | 39031.5674 | 2210 | 0 |  | 2072 | 2291 | 144.2613 | 0 | 134.9206 | 0 | 1.4426 | 0 | 1.3492 | 0 | 1.4426 | 1.3492 | 11.1037 | 18.7955 | 9.6611
39031.5695 | 1977 | 0 | 39031.5696 | 2451 | 0 |  | 2256.5 | 2475.5 | 120.696 | 0 | 149.6337 | 0 | 1.207 | 0 | 1.4963 | 0 | 1.207 | 1.4963 | 32.7962 | 7.1146 | 31.5892
39031.5717 | 1723 | 528 | 39031.5717 | 1529 | 585 |  | 2441.5 | 2660.5 | 105.1893 | 32.2344 | 93.3455 | 35.7143 | 1.0519 | 0.32234 | 0.93346 | 0.35714 | 0.72955 | 0.57631 | 83.8285 | 445.4171 | 57.9051

## B3-D8
Open Burn Test 8 |  |  | 2006-11-10 | 13:06 |  |  | Vs = |  | 160.1575 |  | R = | 100
Mix | 7-C | Tray A | IRMS | 1
0 | 150 kW |  | Bundle | Ch. 3 & 8 | Cable B | Odd - | Cable D |  | Even
Time-51 | N11 | N12 | Time-52 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R8-G | R3-8
39031.5417 | 1 | 0 | 39031.5417 | 1 | 0 |  | -148.5 | 70.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262238 | 262238 | 262237.9994
39031.5439 | 1 | 0 | 39031.5439 | 1 | 0 |  | 36.5 | 255.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262238 | 262238 | 262237.9994
39031.546 | 1 | 0 | 39031.546 | 2459 | 0 |  | 221.5 | 440.5 | 0.06105 | 0 | 150.1221 | 0 | 0.0006105 | 0 | 1.5012 | 0 | 0.0006105 | 1.5012 | 262238 | 6.6848 | 262237.9994
39031.5481 | 519 | 0 | 39031.5481 | 1991 | 0 |  | 406 | 625 | 31.685 | 0 | 121.5507 | 0 | 0.31685 | 0 | 1.2155 | 0 | 0.31685 | 1.2155 | 405.4682 | 31.7619 | 405.1514
39031.5503 | 2425 | 0 | 39031.5503 | 2335 | 0 |  | 591 | 810 | 148.0464 | 0 | 142.5519 | 0 | 1.4805 | 0 | 1.4255 | 0 | 1.4805 | 1.4255 | 8.1806 | 12.3503 | 6.7002
39031.5524 | 2243 | 0 | 39031.5524 | 2063 | 0 |  | 775.5 | 994.5 | 136.9353 | 0 | 125.9463 | 0 | 1.3694 | 0 | 1.2595 | 0 | 1.3694 | 1.2595 | 16.9585 | 27.1634 | 15.5892
39031.5545 | 2317 | 0 | 39031.5546 | 2553 | 0 |  | 960.5 | 1179.5 | 141.453 | 0 | 155.8608 | 0 | 1.4145 | 0 | 1.5586 | 0 | 1.4145 | 1.5586 | 13.2231 | 2.7568 | 11.8086
39031.5567 | 2279 | 0 | 39031.5567 | 2390 | 0 |  | 1145.5 | 1364.5 | 139.1331 | 0 | 145.9096 | 0 | 1.3913 | 0 | 1.4591 | 0 | 1.3913 | 1.4591 | 15.111 | 9.7649 | 13.7197
39031.5588 | 2073 | 0 | 39031.5588 | 2287 | 0 |  | 1330 | 1549 | 126.5568 | 0 | 139.6215 | 0 | 1.2656 | 0 | 1.3962 | 0 | 1.2656 | 1.3962 | 26.5499 | 14.7084 | 25.2844
39031.561 | 2100 | 0 | 39031.561 | 2607 | 0 |  | 1514.5 | 1733.5 | 128.2051 | 0 | 159.1575 | 0 | 1.2821 | 0 | 1.5916 | 0 | 1.2821 | 1.5916 | 24.9229 | 0.62831 | 23.6408
39031.5631 | 2057 | 0 | 39031.5631 | 2197 | 0 |  | 1699.5 | 1918.5 | 125.58 | 0 | 134.127 | 0 | 1.2558 | 0 | 1.3413 | 0 | 1.2558 | 1.3413 | 27.5343 | 19.4074 | 26.2785
39031.5652 | 2489 | 0 | 39031.5653 | 2177 | 0 |  | 1884.5 | 2103.5 | 151.9536 | 0 | 132.906 | 0 | 1.5195 | 0 | 1.3291 | 0 | 1.5195 | 1.3291 | 5.399 | 20.5044 | 3.8794
39031.5674 | 2054 | 0 | 39031.5674 | 2165 | 0 |  | 2069 | 2288 | 125.3968 | 0 | 132.1734 | 0 | 1.254 | 0 | 1.3217 | 0 | 1.254 | 1.3217 | 27.7205 | 21.1723 | 26.4666
39031.5695 | 2203 | 0 | 39031.5695 | 1952 | 0 |  | 2254 | 2473 | 134.4933 | 0 | 119.1697 | 0 | 1.3449 | 0 | 1.1917 | 0 | 1.3449 | 1.1917 | 19.0822 | 34.3945 | 17.7372
39031.5717 | 1354 | 191 | 39031.5717 | 1364 | 209 |  | 2438.5 | 2657.5 | 82.6618 | 11.6606 | 83.2723 | 12.7595 | 0.82662 | 0.11661 | 0.83272 | 0.12759 | 0.71001 | 0.70513 | 125.293 | 127.443 | 316.3602

## B3-D7
Open Burn Test 8 |  |  | 2006-11-10 | 13:06 |  |  | Vs = |  | 155.1514 |  | R = | 100
Mix | 7-C | Tray A | IRMS | 1
0 | 150 kW |  | Bundle | Ch. 3 & 7 | Cable B | Odd - | Cable D |  | Odd
Time-49 | N11 | N12 | Time-50 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R7-G | R3-7
39031.5417 | 1 | 0 | 39031.5417 | 1 | 0 |  | -151 | 68 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254038 | 254038 | 254037.9994
39031.5438 | 1 | 0 | 39031.5438 | 1 | 0 |  | 33.5 | 252.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254038 | 254038 | 254037.9994
39031.546 | 1 | 0 | 39031.546 | 2260 | 0 |  | 218.5 | 437.5 | 0.06105 | 0 | 137.9731 | 0 | 0.0006105 | 0 | 1.3797 | 0 | 0.0006105 | 1.3797 | 254038 | 12.4504 | 254037.9994
39031.5481 | 2 | 0 | 39031.5481 | 2525 | 0 |  | 403.5 | 622.5 | 0.1221 | 0 | 154.1514 | 0 | 0.001221 | 0 | 1.5415 | 0 | 0.001221 | 1.5415 | 126969 | 0.64871 | 126968.9988
39031.5502 | 2161 | 0 | 39031.5503 | 2499 | 0 |  | 588 | 807 | 131.9292 | 0 | 152.5641 | 0 | 1.3193 | 0 | 1.5256 | 0 | 1.3193 | 1.5256 | 17.602 | 1.6959 | 16.2827
39031.5524 | 2334 | 0 | 39031.5524 | 2064 | 0 |  | 773 | 992 | 142.4908 | 0 | 126.0073 | 0 | 1.4249 | 0 | 1.2601 | 0 | 1.4249 | 1.2601 | 8.8852 | 23.1289 | 7.4603
39031.5545 | 2479 | 0 | 39031.5545 | 2501 | 0 |  | 957.5 | 1176.5 | 151.3431 | 0 | 152.6862 | 0 | 1.5134 | 0 | 1.5269 | 0 | 1.5134 | 1.5269 | 2.5163 | 1.6146 | 1.0029
| 2240 | 0 | 39031.5567 | 2054 | 0 |  | 1143 | 1362 | 136.7521 | 0 | 125.3968 | 0 | 1.3675 | 0 | 1.254 | 0 | 1.3675 | 1.254 | 13.4545 | 23.7283 | 12.0869
39031.5588 | 2001 | 0 | 39031.5588 | 2147 | 0 |  | 1327.5 | 1546.5 | 122.1612 | 0 | 131.0745 | 0 | 1.2216 | 0 | 1.3107 | 0 | 1.2216 | 1.3107 | 27.0055 | 18.3689 | 25.7839
39031.5609 | 2075 | 0 | 39031.5609 | 2179 | 0 |  | 1512 | 1731 | 126.6789 | 0 | 133.0281 | 0 | 1.2668 | 0 | 1.3303 | 0 | 1.2668 | 1.3303 | 22.4761 | 16.6306 | 21.2094
39031.5631 | 2395 | 0 | 39031.5631 | 2430 | 0 |  | 1696.5 | 1915.5 | 146.2149 | 0 | 148.3516 | 0 | 1.4621 | 0 | 1.4835 | 0 | 1.4621 | 1.4835 | 6.1119 | 4.5835 | 4.6498
39031.5652 | 2503 | 0 | 39031.5652 | 2215 | 0 |  | 1881.5 | 2100.5 | 152.8083 | 0 | 135.2259 | 0 | 1.5281 | 0 | 1.3523 | 0 | 1.5281 | 1.3523 | 1.5334 | 14.735 | 0.0052769
39031.5673 | 2390 | 0 | 39031.5674 | 2519 | 0 |  | 2066.5 | 2285.5 | 145.9096 | 0 | 153.7851 | 0 | 1.4591 | 0 | 1.5379 | 0 | 1.4591 | 1.5379 | 6.3339 | 0.88845 | 4.8748
39031.5695 | 2059 | 0 | 39031.5695 | 1885 | 0 |  | 2251 | 2470 | 125.7021 | 0 | 115.0794 | 0 | 1.257 | 0 | 1.1508 | 0 | 1.257 | 1.1508 | 23.4279 | 34.8212 | 22.1709
39031.5716 | 1466 | 240 | 39031.5716 | 1221 | 269 |  | 2436 | 2655 | 89.4994 | 14.652 | 74.5421 | 16.4225 | 0.89499 | 0.14652 | 0.74542 | 0.16422 | 0.74847 | 0.5812 | 97.4858 | 195.3045 | 230.2051

## B3-C6
Open Burn Test 8 |  |  | 2006-11-10 | 13:06 |  |  | Vs = |  | 157.5324 |  | R = | 100
Mix | 7-C | Tray A | IRMS | 1
0 | 150 kW |  | Bundle | Ch. 3 & 6 | Cable B | Odd - | Cable C |  | Even
Time-47 | N11 | N12 | Time-48 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R6-G | R3-6
39031.5417 | 1 | 0 | 39031.5417 | 1 | 0 |  | -153.5 | 65.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257938 | 257938 | 257937.9994
39031.5438 | 1 | 0 | 39031.5438 | 1 | 0 |  | 31 | 250 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257938 | 257938 | 257937.9994
39031.5459 | 1 | 0 | 39031.5459 | 45 | 0 |  | 215.5 | 434.5 | 0.06105 | 0 | 2.7473 | 0 | 0.0006105 | 0 | 0.027473 | 0 | 0.0006105 | 0.027473 | 257938 | 5634.1778 | 257937.9994
39031.5481 | 1 | 0 | 39031.5481 | 2294 | 0 |  | 400.5 | 619.5 | 0.06105 | 0 | 140.0488 | 0 | 0.0006105 | 0 | 1.4005 | 0 | 0.0006105 | 1.4005 | 257938 | 12.4839 | 257937.9994
39031.5502 | 2171 | 0 | 39031.5502 | 2477 | 0 |  | 585.5 | 804.5 | 132.5397 | 0 | 151.221 | 0 | 1.3254 | 0 | 1.5122 | 0 | 1.3254 | 1.5122 | 18.8567 | 4.1736 | 17.5314
39031.5523 | 2564 | 0 | 39031.5524 | 2456 | 0 |  | 770 | 989 | 156.5324 | 0 | 149.9389 | 0 | 1.5653 | 0 | 1.4994 | 0 | 1.5653 | 1.4994 | 0.63885 | 5.0643 | 0.92648
39031.5545 | 2490 | 0 | 39031.5545 | 2029 | 0 |  | 955 | 1174 | 152.0147 | 0 | 123.8706 | 0 | 1.5201 | 0 | 1.2387 | 0 | 1.5201 | 1.2387 | 3.6297 | 27.175 | 2.1096
39031.5566 | 2384 | 0 | 39031.5566 | 2121 | 0 |  | 1139.5 | 1358.5 | 145.5433 | 0 | 129.4872 | 0 | 1.4554 | 0 | 1.2949 | 0 | 1.4554 | 1.2949 | 8.2374 | 21.6587 | 6.782
39031.5588 | 2286 | 0 | 39031.5588 | 2510 | 0 |  | 1324.5 | 1543.5 | 139.5604 | 0 | 153.2357 | 0 | 1.3956 | 0 | 1.5324 | 0 | 1.3956 | 1.5324 | 12.8775 | 2.804 | 11.4819
39031.5609 | 2147 | 0 | 39031.5609 | 2323 | 0 |  | 1509 | 1728 | 131.0745 | 0 | 141.8193 | 0 | 1.3107 | 0 | 1.4182 | 0 | 1.3107 | 1.4182 | 20.1854 | 11.0796 | 18.8746
39031.563 | 2512 | 0 | 39031.5631 | 2453 | 0 |  | 1694 | 1913 | 153.3578 | 0 | 149.7558 | 0 | 1.5336 | 0 | 1.4976 | 0 | 1.5336 | 1.4976 | 2.7221 | 5.1928 | 1.1886
39031.5652 | 2123 | 0 | 39031.5652 | 2245 | 0 |  | 1878.5 | 2097.5 | 129.6093 | 0 | 137.0574 | 0 | 1.2961 | 0 | 1.3706 | 0 | 1.2961 | 1.3706 | 21.544 | 14.939 | 20.2479
39031.5673 | 2384 | 0 | 39031.5673 | 2528 | 0 |  | 2063.5 | 2282.5 | 145.5433 | 0 | 154.3346 | 0 | 1.4554 | 0 | 1.5433 | 0 | 1.4554 | 1.5433 | 8.2374 | 2.072 | 6.782
39031.5695 | 2411 | 0 | 39031.5695 | 1899 | 0 |  | 2248.5 | 2467.5 | 147.1917 | 0 | 115.9341 | 0 | 1.4719 | 0 | 1.1593 | 0 | 1.4719 | 1.1593 | 7.0253 | 35.881 | 5.5534
39031.5716 | 1150 | 677 | 39031.5716 | 1419 | 548 |  | 2433 | 2652 | 70.2076 | 41.3309 | 86.63 | 33.4554 | 0.70208 | 0.41331 | 0.8663 | 0.33455 | 0.28877 | 0.53175 | 3198.8159 | 158.0727 | 68.1617

## B3-C5
Open Burn Test 8 |  |  | 2006-11-10 | 13:06 |  |  | Vs = |  | 160.2186 |  | R = | 100
Mix | 7-C | Tray A | IRMS | 1
0 | 150 kW |  | Bundle | Ch. 3 & 5 | Cable B | Odd - | Cable C |  | Odd
Time-45 | N11 | N12 | Time-46 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R5-G | R3-5
39031.5416 | 1 | 0 | 39031.5416 | 1 | 0 |  | -156.5 | 62.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262338 | 262338 | 262337.9994
39031.5438 | 1 | 0 | 39031.5438 | 1 | 0 |  | 28.5 | 247.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262338 | 262338 | 262337.9994
39031.5459 | 1 | 0 | 39031.5459 | 47 | 0 |  | 213 | 432 | 0.06105 | 0 | 2.8694 | 0 | 0.0006105 | 0 | 0.028694 | 0 | 0.0006105 | 0.028694 | 262338 | 5483.7872 | 262337.9994
39031.548 | 1 | 0 | 39031.548 | 2304 | 0 |  | 397.5 | 616.5 | 0.06105 | 0 | 140.6593 | 0 | 0.0006105 | 0 | 1.4066 | 0 | 0.0006105 | 1.4066 | 262338 | 13.9054 | 262337.9994
39031.5502 | 1943 | 0 | 39031.5502 | 2027 | 0 |  | 582.5 | 801.5 | 118.6203 | 0 | 123.7485 | 0 | 1.1862 | 0 | 1.2375 | 0 | 1.1862 | 1.2375 | 35.0685 | 29.4711 | 33.8822
39031.5523 | 2562 | 0 | 39031.5523 | 2432 | 0 |  | 767.5 | 986.5 | 156.4103 | 0 | 148.4737 | 0 | 1.5641 | 0 | 1.4847 | 0 | 1.5641 | 1.4847 | 2.4348 | 7.9104 | 0.87071
39031.5544 | 2035 | 0 | 39031.5545 | 2096 | 0 |  | 952 | 1171 | 124.2369 | 0 | 127.9609 | 0 | 1.2424 | 0 | 1.2796 | 0 | 1.2424 | 1.2796 | 28.9622 | 25.209 | 27.7198
39031.5566 | 2305 | 0 | 39031.5566 | 2502 | 0 |  | 1137 | 1356 | 140.7204 | 0 | 152.7473 | 0 | 1.4072 | 0 | 1.5275 | 0 | 1.4072 | 1.5275 | 13.856 | 4.8913 | 12.4488
39031.5587 | 2143 | 0 | 39031.5587 | 2049 | 0 |  | 1321.5 | 1540.5 | 130.8303 | 0 | 125.0916 | 0 | 1.3083 | 0 | 1.2509 | 0 | 1.3083 | 1.2509 | 22.4629 | 28.081 | 21.1546
39031.5609 | 2184 | 0 | 39031.5609 | 2538 | 0 |  | 1506.5 | 1725.5 | 133.3333 | 0 | 154.9451 | 0 | 1.3333 | 0 | 1.5495 | 0 | 1.3333 | 1.5495 | 20.1639 | 3.4035 | 18.8306
39031.563 | 2608 | 0 | 39031.563 | 2382 | 0 |  | 1691 | 1910 | 159.2186 | 0 | 145.4212 | 0 | 1.5922 | 0 | 1.4542 | 0 | 1.5922 | 1.4542 | 0.62807 | 10.1755 | 0.96412
39031.5651 | 2097 | 0 | 39031.5652 | 2539 | 0 |  | 1876 | 2095 | 128.022 | 0 | 155.0061 | 0 | 1.2802 | 0 | 1.5501 | 0 | 1.2802 | 1.5501 | 25.1493 | 3.3627 | 23.869
39031.5673 | 2194 | 0 | 39031.5673 | 2105 | 0 |  | 2060.5 | 2279.5 | 133.9438 | 0 | 128.5104 | 0 | 1.3394 | 0 | 1.2851 | 0 | 1.3394 | 1.2851 | 19.6162 | 24.6736 | 18.2768
39031.5694 | 2102 | 1 | 39031.5694 | 2417 | 0 |  | 2245.5 | 2464.5 | 128.3272 | 0.06105 | 147.558 | 0 | 1.2833 | 0.0006105 | 1.4756 | 0 | 1.2827 | 1.4756 | 25.0021 | 8.5801 | 4119.9744
39031.5716 | 1202 | 707 | 39031.5716 | 1669 | 604 |  | 2430.5 | 2649.5 | 73.3822 | 43.1624 | 101.8926 | 36.8742 | 0.73382 | 0.43162 | 1.0189 | 0.36874 | 0.3022 | 0.65018 | 332.7664 | 1046.4922 | 92.3596

## B3-B4
Open Burn Test 8 |  |  | 2006-11-10 | 13:06 |  |  | Vs = |  | 157.5324 |  | R = | 100
Mix | 7-C | Tray A | IRMS | 1
0 | 150 kW |  | Bundle | Ch. 3 & 4 | Cable B | Odd -Even
Time-43 | N11 | N12 | Time-44 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R4-G | R3-4
39031.5416 | 1 | 0 | 39031.5416 | 1 | 0 |  | -159.5 | 59.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257938 | 257938 | 257937.9994
39031.5437 | 1 | 0 | 39031.5437 | 0 | 0 |  | 25.5 | 244.5 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 257938 | 515976 | 257937.9994
39031.5459 | 1 | 0 | 39031.5459 | 1 | 0 |  | 210 | 429 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257938 | 257938 | 257937.9994
39031.548 | 2 | 0 | 39031.548 | 89 | 0 |  | 395 | 614 | 0.1221 | 0 | 5.4335 | 0 | 0.001221 | 0 | 0.054335 | 0 | 0.001221 | 0.054335 | 128919 | 2799.3034 | 128918.9988
39031.5501 | 2163 | 46 | 39031.5502 | 2396 | 46 |  | 579.5 | 798.5 | 132.0513 | 2.8083 | 146.2759 | 2.8083 | 1.3205 | 0.028083 | 1.4628 | 0.028083 | 1.2924 | 1.4347 | 26.5173 | 8.4713 | 63.0515
39031.5523 | 2215 | 0 | 39031.5523 | 2076 | 0 |  | 764.5 | 983.5 | 135.2259 | 0 | 126.7399 | 0 | 1.3523 | 0 | 1.2674 | 0 | 1.3523 | 1.2674 | 16.4957 | 24.2958 | 15.1435
39031.5544 | 2471 | 0 | 39031.5544 | 2117 | 0 |  | 949.5 | 1168.5 | 150.8547 | 0 | 129.243 | 0 | 1.5085 | 0 | 1.2924 | 0 | 1.5085 | 1.2924 | 4.4265 | 21.8885 | 2.918
39031.5566 | 2564 | 0 | 39031.5566 | 2493 | 0 |  | 1134 | 1353 | 156.5324 | 0 | 152.1978 | 0 | 1.5653 | 0 | 1.522 | 0 | 1.5653 | 1.522 | 0.63885 | 3.505 | 0.92648
39031.5587 | 2029 | 0 | 39031.5587 | 2504 | 0 |  | 1318.5 | 1537.5 | 123.8706 | 0 | 152.8694 | 0 | 1.2387 | 0 | 1.5287 | 0 | 1.2387 | 1.5287 | 27.175 | 3.0503 | 25.9363
39031.5608 | 2436 | 0 | 39031.5608 | 2020 | 0 |  | 1503.5 | 1722.5 | 148.7179 | 0 | 123.3211 | 0 | 1.4872 | 0 | 1.2332 | 0 | 1.4872 | 1.2332 | 5.9269 | 27.7416 | 4.4397
39031.563 | 2421 | 0 | 39031.563 | 2048 | 0 |  | 1688.5 | 1907.5 | 147.8022 | 0 | 125.0305 | 0 | 1.478 | 0 | 1.2503 | 0 | 1.478 | 1.2503 | 6.5832 | 25.9951 | 5.1052
39031.5651 | 2367 | 0 | 39031.5651 | 2504 | 0 |  | 1873 | 2092 | 144.5055 | 0 | 152.8694 | 0 | 1.4451 | 0 | 1.5287 | 0 | 1.4451 | 1.5287 | 9.0148 | 3.0503 | 7.5697
39031.5672 | 2186 | 0 | 39031.5673 | 2554 | 0 |  | 2058 | 2277 | 133.4554 | 0 | 155.9219 | 0 | 1.3346 | 0 | 1.5592 | 0 | 1.3346 | 1.5592 | 18.0412 | 1.0329 | 16.7066
39031.5694 | 1661 | 304 | 39031.5694 | 1680 | 335 |  | 2242.5 | 2461.5 | 101.4042 | 18.5592 | 102.5641 | 20.4518 | 1.014 | 0.18559 | 1.0256 | 0.20452 | 0.82845 | 0.82112 | 89.3 | 92.8361 | 97.4537
39031.5715 | 1469 | 617 | 39031.5715 | 1374 | 745 |  | 2427.5 | 2646.5 | 89.6825 | 37.6679 | 83.8828 | 45.4823 | 0.89683 | 0.37668 | 0.83883 | 0.45482 | 0.52015 | 0.384 | 137.7244 | 1369.883 | 74.6752

## A2-C6
Open Burn Test 8 |  |  | 2006-11-10 | 13:06 |  |  | Vs = |  | 156.8608 |  | R = | 100
Mix | 7-C | Tray A | IRMS | 1
0 | 150 kW |  | Bundle | Ch. 2 & 6 | Cable A | Even - | Cable C |  | Even
Time-29 | N11 | N12 | Time-30 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R6-G | R2-6
39031.5414 | 1 | 0 |  | 1 | 0 |  | -180 | 39 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256838 | 256838 | 256837.9994
39031.5435 | 1 | 0 | 39031.5435 | 1 | 0 |  | 6 | 225 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256838 | 256838 | 256837.9994
39031.5456 | 1 | 0 | 39031.5456 | 374 | 0 |  | 190.5 | 409.5 | 0.06105 | 0 | 22.8327 | 0 | 0.0006105 | 0 | 0.22833 | 0 | 0.0006105 | 0.22833 | 256838 | 587 | 256837.9994
39031.5478 | 1 | 0 | 39031.5478 | 2358 | 0 |  | 375.5 | 594.5 | 0.06105 | 0 | 143.956 | 0 | 0.0006105 | 0 | 1.4396 | 0 | 0.0006105 | 1.4396 | 256838 | 8.9644 | 256837.9994
39031.5499 | 1715 | 0 | 39031.5499 | 2505 | 0 |  | 560 | 779 | 104.7009 | 0 | 152.9304 | 0 | 1.047 | 0 | 1.5293 | 0 | 1.047 | 1.5293 | 49.8181 | 2.5701 | 48.7711
39031.552 | 2008 | 0 | 39031.5521 | 2432 | 0 |  | 745 | 964 | 122.5885 | 0 | 148.4737 | 0 | 1.2259 | 0 | 1.4847 | 0 | 1.2259 | 1.4847 | 27.9572 | 5.6488 | 26.7313
39031.5542 | 2356 | 0 | 39031.5542 | 2342 | 0 |  | 929.5 | 1148.5 | 143.8339 | 0 | 142.9792 | 0 | 1.4383 | 0 | 1.4298 | 0 | 1.4383 | 1.4298 | 9.0569 | 9.7088 | 7.6185
39031.5563 | 2138 | 0 | 39031.5563 | 2524 | 0 |  | 1114.5 | 1333.5 | 130.525 | 0 | 154.0904 | 0 | 1.3053 | 0 | 1.5409 | 0 | 1.3053 | 1.5409 | 20.1768 | 1.7979 | 18.8716
39031.5585 | 2004 | 0 | 39031.5585 | 2521 | 0 |  | 1299 | 1518 | 122.3443 | 0 | 153.9072 | 0 | 1.2234 | 0 | 1.5391 | 0 | 1.2234 | 1.5391 | 28.2126 | 1.9191 | 26.9891
39031.5606 | 2491 | 0 | 39031.5606 | 2430 | 0 |  | 1484 | 1703 | 152.0757 | 0 | 148.3516 | 0 | 1.5208 | 0 | 1.4835 | 0 | 1.5208 | 1.4835 | 3.1465 | 5.7358 | 1.6258
39031.5627 | 2553 | 0 | 39031.5628 | 2022 | 0 |  | 1668.5 | 1887.5 | 155.8608 | 0 | 123.4432 | 0 | 1.5586 | 0 | 1.2344 | 0 | 1.5586 | 1.2344 | 0.6416 | 27.0712 | 0.91701
39031.5649 | 2047 | 0 | 39031.5649 | 2294 | 0 |  | 1853.5 | 2072.5 | 124.9695 | 0 | 140.0488 | 0 | 1.2497 | 0 | 1.4005 | 0 | 1.2497 | 1.4005 | 25.5193 | 12.0044 | 24.2696
39031.567 | 2102 | 0 | 39031.567 | 2537 | 0 |  | 2038.5 | 2257.5 | 128.3272 | 0 | 154.884 | 0 | 1.2833 | 0 | 1.5488 | 0 | 1.2833 | 1.5488 | 22.235 | 1.2763 | 20.9517
39031.5692 | 2158 | 104 | 39031.5692 | 2174 | 111 |  | 2223 | 2442 | 131.746 | 6.3492 | 132.7228 | 6.7766 | 1.3175 | 0.063492 | 1.3272 | 0.067766 | 1.254 | 1.2595 | 25.2875 | 24.3453 | 57.8667
39031.5713 | 1650 | 616 | 39031.5713 | 2043 | 560 |  | 2408 | 2627 | 100.7326 | 37.6068 | 124.7253 | 34.188 | 1.0073 | 0.37607 | 1.2473 | 0.34188 | 0.63126 | 0.90537 | 37.6392 | 43.731 | 14.9846

## A2-C5
Open Burn Test 8 |  |  | 2006-11-10 | 13:06 |  |  | Vs = |  | 158.9976 |  | R = | 100
Mix | 7-C | Tray A | IRMS | 1
0 | 150 kW |  | Bundle | Ch. 2 & 5 | Cable A | Even - | Cable C |  | Odd
Time-27 | N11 | N12 | Time-28 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R5-G | R2-5
39031.5413 | 1 | 0 | 39031.5413 | 1 | 0 |  | -181.5 | 37.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260338 | 260338 | 260337.9994
39031.5435 | 1 | 0 | 39031.5435 | 1 | 0 |  | 3 | 222 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260338 | 260338 | 260337.9994
39031.5456 | 1 | 0 | 39031.5456 | 498 | 0 |  | 187.5 | 406.5 | 0.06105 | 0 | 30.4029 | 0 | 0.0006105 | 0 | 0.30403 | 0 | 0.0006105 | 0.30403 | 260338 | 422.9679 | 260337.9994
39031.5477 | 1 | 0 | 39031.5478 | 2170 | 0 |  | 372.5 | 591.5 | 0.06105 | 0 | 132.4786 | 0 | 0.0006105 | 0 | 1.3248 | 0 | 0.0006105 | 1.3248 | 260338 | 20.0175 | 260337.9994
39031.5499 | 1972 | 0 | 39031.5499 | 2486 | 0 |  | 557.5 | 776.5 | 120.3907 | 0 | 151.7705 | 0 | 1.2039 | 0 | 1.5177 | 0 | 1.2039 | 1.5177 | 32.068 | 4.7619 | 30.864
39031.552 | 2453 | 0 | 39031.552 | 2396 | 0 |  | 742 | 961 | 149.7558 | 0 | 146.2759 | 0 | 1.4976 | 0 | 1.4628 | 0 | 1.4976 | 1.4628 | 6.1712 | 8.697 | 4.6737
39031.5542 | 2185 | 0 | 39031.5542 | 2023 | 0 |  | 927 | 1146 | 133.3944 | 0 | 123.5043 | 0 | 1.3339 | 0 | 1.235 | 0 | 1.3339 | 1.235 | 19.1936 | 28.7385 | 17.8596
39031.5563 | 2122 | 0 | 39031.5563 | 2084 | 0 |  | 1111.5 | 1330.5 | 129.5482 | 0 | 127.2283 | 0 | 1.2955 | 0 | 1.2723 | 0 | 1.2955 | 1.2723 | 22.7323 | 24.9702 | 21.4368
39031.5584 | 2482 | 0 | 39031.5584 | 2481 | 0 |  | 1296.5 | 1515.5 | 151.5263 | 0 | 151.4652 | 0 | 1.5153 | 0 | 1.5147 | 0 | 1.5153 | 1.5147 | 4.9307 | 4.973 | 3.4154
39031.5606 | 2031 | 0 | 39031.5606 | 2462 | 0 |  | 1481 | 1700 | 123.9927 | 0 | 150.3053 | 0 | 1.2399 | 0 | 1.5031 | 0 | 1.2399 | 1.5031 | 28.2314 | 5.7831 | 26.9915
39031.5627 | 2376 | 0 | 39031.5627 | 2432 | 0 |  | 1666 | 1885 | 145.0549 | 0 | 148.4737 | 0 | 1.4505 | 0 | 1.4847 | 0 | 1.4505 | 1.4847 | 9.612 | 7.088 | 8.1614
39031.5648 | 2413 | 0 | 39031.5649 | 2184 | 0 |  | 1850.5 | 2069.5 | 147.3138 | 0 | 133.3333 | 0 | 1.4731 | 0 | 1.3333 | 0 | 1.4731 | 1.3333 | 7.9312 | 19.2482 | 6.4581
39031.567 | 2468 | 0 | 39031.567 | 2588 | 0 |  | 2035.5 | 2254.5 | 150.6716 | 0 | 157.9976 | 0 | 1.5067 | 0 | 1.58 | 0 | 1.5067 | 1.58 | 5.5259 | 0.63292 | 4.0192
39031.5691 | 1778 | 83 | 39031.5691 | 1775 | 83 |  | 2220.5 | 2439.5 | 108.547 | 5.0672 | 108.3639 | 5.0672 | 1.0855 | 0.050672 | 1.0836 | 0.050672 | 1.0348 | 1.033 | 53.6205 | 53.9536 | 313.88
39031.5713 | 1637 | 538 | 39031.5713 | 1745 | 461 |  | 2405 | 2624 | 99.9389 | 32.8449 | 106.5324 | 28.1441 | 0.99939 | 0.32845 | 1.0653 | 0.28144 | 0.67094 | 0.78388 | 229.9589 | 79.313 | 35.3014

## A2-B4
Open Burn Test 8 |  |  | 2006-11-10 | 13:06 |  |  | Vs = |  | 158.265 |  | R = | 100
Mix | 7-C | Tray A | IRMS | 1
0 | 150 kW |  | Bundle | Ch. 2 & 4 | Cable A | Even - | Cable B |  | Even
Time-25 | N11 | N12 | Time-26 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R4-G | R2-4
39031.5413 | 1 | 0 | 39031.5413 | 1 | 0 |  | -184.5 | 34.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259138 | 259138 | 259137.9994
39031.5434 | 1 | 0 | 39031.5434 | 1 | 0 |  | 0.5 | 219.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259138 | 259138 | 259137.9994
39031.5456 | 1 | 0 | 39031.5456 | 1 | 0 |  | 185 | 404 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259138 | 259138 | 259137.9994
39031.5477 | 1 | 0 | 39031.5477 | 1 | 0 |  | 369.5 | 588.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259138 | 259138 | 259137.9994
39031.5498 | 1691 | 0 | 39031.5499 | 1715 | 0 |  | 554.5 | 773.5 | 103.2357 | 0 | 104.7009 | 0 | 1.0324 | 0 | 1.047 | 0 | 1.0324 | 1.047 | 53.3046 | 51.1592 | 52.2722
39031.552 | 2397 | 0 | 39031.552 | 2052 | 0 |  | 739.5 | 958.5 | 146.337 | 0 | 125.2747 | 0 | 1.4634 | 0 | 1.2527 | 0 | 1.4634 | 1.2527 | 8.151 | 26.3343 | 6.6877
39031.5541 | 2576 | 0 | 39031.5541 | 2401 | 0 |  | 924 | 1143 | 157.265 | 0 | 146.5812 | 0 | 1.5726 | 0 | 1.4658 | 0 | 1.5726 | 1.4658 | 0.63587 | 7.9708 | 0.93678
39031.5563 | 2344 | 0 | 39031.5563 | 2285 | 0 |  | 1109 | 1328 | 143.1013 | 0 | 139.4994 | 0 | 1.431 | 0 | 1.395 | 0 | 1.431 | 1.395 | 10.5964 | 13.4521 | 9.1654
39031.5584 | 2046 | 0 | 39031.5584 | 2542 | 0 |  | 1293.5 | 1512.5 | 124.9084 | 0 | 155.1893 | 0 | 1.2491 | 0 | 1.5519 | 0 | 1.2491 | 1.5519 | 26.7048 | 1.9819 | 25.4557
39031.5605 | 2432 | 0 | 39031.5606 | 2072 | 0 |  | 1478.5 | 1697.5 | 148.4737 | 0 | 126.4957 | 0 | 1.4847 | 0 | 1.265 | 0 | 1.4847 | 1.265 | 6.5946 | 25.1149 | 5.1098
39031.5627 | 2091 | 0 | 39031.5627 | 2126 | 0 |  | 1663 | 1882 | 127.6557 | 0 | 129.7924 | 0 | 1.2766 | 0 | 1.2979 | 0 | 1.2766 | 1.2979 | 23.978 | 21.937 | 22.7014
39031.5648 | 2048 | 0 | 39031.5648 | 2240 | 0 |  | 1848 | 2067 | 125.0305 | 0 | 136.7521 | 0 | 1.2503 | 0 | 1.3675 | 0 | 1.2503 | 1.3675 | 26.5811 | 15.7312 | 25.3307
39031.567 | 2494 | 0 | 39031.567 | 2549 | 0 |  | 2032.5 | 2251.5 | 152.2589 | 0 | 155.6166 | 0 | 1.5226 | 0 | 1.5562 | 0 | 1.5226 | 1.5562 | 3.9447 | 1.7018 | 2.4221
39031.5691 | 2243 | 108 | 39031.5691 | 1858 | 92 |  | 2217.5 | 2436.5 | 136.9353 | 6.5934 | 113.431 | 5.6166 | 1.3694 | 0.065934 | 1.1343 | 0.056166 | 1.3034 | 1.0781 | 17.9093 | 58.6425 | 82.6172
39031.5712 | 1817 | 570 | 39031.5713 | 1601 | 674 |  | 2402.5 | 2621.5 | 110.928 | 34.7985 | 97.7411 | 41.1477 | 1.1093 | 0.34799 | 0.97741 | 0.41148 | 0.76129 | 0.56593 | 54.3209 | 315.9522 | 27.3691

## A2-B3
Open Burn Test 8 |  |  | 2006-11-10 | 13:06 |  |  | Vs = |  | 160.707 |  | R = | 100
Mix | 7-C | Tray A | IRMS | 1
0 | 150 kW |  | Bundle | Ch. 2 & 3 | Cable A | Even - | Cable B |  | Odd
Time-23 | N11 | N12 | Time-24 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R3-G | R2-3
39031.5413 | 1 | 0 | 39031.5413 | 1 | 0 |  | -187.5 | 31.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263138 | 263138 | 263137.9994
39031.5434 | 1 | 0 | 39031.5434 | 1 | 0 |  | -2.5 | 216.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263138 | 263138 | 263137.9994
39031.5455 | 1 | 0 | 39031.5456 | 1 | 0 |  | 182.5 | 401.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263138 | 263138 | 263137.9994
39031.5477 | 1 | 0 | 39031.5477 | 1 | 0 |  | 367 | 586 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263138 | 263138 | 263137.9994
39031.5498 | 1970 | 0 | 39031.5498 | 1849 | 0 |  | 551.5 | 770.5 | 120.2686 | 0 | 112.8816 | 0 | 1.2027 | 0 | 1.1288 | 0 | 1.2027 | 1.1288 | 33.6234 | 42.3678 | 32.4207
39031.552 | 2187 | 0 | 39031.552 | 2309 | 0 |  | 736.5 | 955.5 | 133.5165 | 0 | 140.9646 | 0 | 1.3352 | 0 | 1.4096 | 0 | 1.3352 | 1.4096 | 20.3649 | 14.0052 | 19.0297
39031.5541 | 2255 | 0 | 39031.5541 | 2003 | 0 |  | 921.5 | 1140.5 | 137.6679 | 0 | 122.2833 | 0 | 1.3767 | 0 | 1.2228 | 0 | 1.3767 | 1.2228 | 16.7353 | 31.4219 | 15.3586
39031.5562 | 2084 | 0 | 39031.5563 | 2348 | 0 |  | 1106 | 1325 | 127.2283 | 0 | 143.3455 | 0 | 1.2723 | 0 | 1.4335 | 0 | 1.2723 | 1.4335 | 26.3138 | 12.1116 | 25.0415
39031.5584 | 2296 | 0 | 39031.5584 | 2487 | 0 |  | 1291 | 1510 | 140.1709 | 0 | 151.8315 | 0 | 1.4017 | 0 | 1.5183 | 0 | 1.4017 | 1.5183 | 14.6507 | 5.8456 | 13.249
39031.5605 | 2236 | 0 | 39031.5605 | 2565 | 0 |  | 1475.5 | 1694.5 | 136.5079 | 0 | 156.5934 | 0 | 1.3651 | 0 | 1.5659 | 0 | 1.3651 | 1.5659 | 17.7272 | 2.6269 | 16.3621
39031.5627 | 2114 | 0 | 39031.5627 | 2396 | 0 |  | 1660.5 | 1879.5 | 129.0598 | 0 | 146.2759 | 0 | 1.2906 | 0 | 1.4628 | 0 | 1.2906 | 1.4628 | 24.5213 | 9.8656 | 23.2307
39031.5648 | 2383 | 0 | 39031.5648 | 2584 | 0 |  | 1845 | 2064 | 145.4823 | 0 | 157.7534 | 0 | 1.4548 | 0 | 1.5775 | 0 | 1.4548 | 1.5775 | 10.465 | 1.8723 | 9.0101
39031.5669 | 2296 | 0 | 39031.5669 | 2616 | 0 |  | 2030 | 2249 | 140.1709 | 0 | 159.707 | 0 | 1.4017 | 0 | 1.5971 | 0 | 1.4017 | 1.5971 | 14.6507 | 0.62615 | 13.249
39031.5691 | 1853 | 84 | 39031.5691 | 2160 | 99 |  | 2214.5 | 2433.5 | 113.1258 | 5.1282 | 131.8681 | 6.044 | 1.1313 | 0.051282 | 1.3187 | 0.06044 | 1.08 | 1.2582 | 54.3153 | 25.1436 | 166.3264
39031.5712 | 1797 | 632 | 39031.5712 | 1699 | 572 |  | 2399.5 | 2618.5 | 109.707 | 38.5836 | 103.7241 | 34.9206 | 1.0971 | 0.38584 | 1.0372 | 0.34921 | 0.71123 | 0.68803 | 111.4894 | 152.0295 | 19.4119

## A1-C6
Open Burn Test 8 |  |  | 2006-11-10 | 13:06 |  |  | Vs = |  | 158.0818 |  | R = | 100
Mix | 7-C | Tray A | IRMS | 1
0 | 150 kW |  | Bundle | Ch. 1 & 6 | Cable A | Odd - | Cable C |  | Even
Time-9 | N11 | N12 | Time-10 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R6-G | R1-6
39031.541 | 1 | 0 | 39031.5411 | 1 | 0 |  | -207 | 12 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258838 | 258838 | 258837.9994
39031.5432 | 0 | 0 | 39031.5432 | 1 | 0 |  | -22.5 | 196.5 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 517776 | 258838 | 517775.9997
39031.5453 | 1 | 0 | 39031.5453 | 1 | 0 |  | 162.5 | 381.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258838 | 258838 | 258837.9994
39031.5475 | 1 | 0 | 39031.5475 | 1927 | 0 |  | 347.5 | 566.5 | 0.06105 | 0 | 117.6435 | 0 | 0.0006105 | 0 | 1.1764 | 0 | 0.0006105 | 1.1764 | 258838 | 34.3736 | 258837.9994
39031.5496 | 981 | 0 | 39031.5496 | 2104 | 0 |  | 532 | 751 | 59.8901 | 0 | 128.4493 | 0 | 0.5989 | 0 | 1.2845 | 0 | 0.5989 | 1.2845 | 163.9531 | 23.0694 | 163.3542
39031.5517 | 2410 | 0 | 39031.5517 | 2043 | 0 |  | 717 | 936 | 147.1306 | 0 | 124.7253 | 0 | 1.4713 | 0 | 1.2473 | 0 | 1.4713 | 1.2473 | 7.4432 | 26.744 | 5.9718
39031.5539 | 2359 | 0 | 39031.5539 | 2199 | 0 |  | 901.5 | 1120.5 | 144.0171 | 0 | 134.2491 | 0 | 1.4402 | 0 | 1.3425 | 0 | 1.4402 | 1.3425 | 9.766 | 17.7526 | 8.3258
39031.556 | 2573 | 0 | 39031.556 | 2523 | 0 |  | 1086.5 | 1305.5 | 157.0818 | 0 | 154.0293 | 0 | 1.5708 | 0 | 1.5403 | 0 | 1.5708 | 1.5403 | 0.63661 | 2.631 | 0.93421
39031.5581 | 2565 | 0 | 39031.5582 | 2384 | 0 |  | 1271.5 | 1490.5 | 156.5934 | 0 | 145.5433 | 0 | 1.5659 | 0 | 1.4554 | 0 | 1.5659 | 1.4554 | 0.95049 | 8.6149 | 0.61545
39031.5603 | 2313 | 0 | 39031.5603 | 2527 | 0 |  | 1456 | 1675 | 141.2088 | 0 | 154.2735 | 0 | 1.4121 | 0 | 1.5427 | 0 | 1.4121 | 1.5427 | 11.949 | 2.4685 | 10.5369
39031.5624 | 2350 | 0 | 39031.5624 | 2559 | 0 |  | 1640.5 | 1859.5 | 143.4676 | 0 | 156.2271 | 0 | 1.4347 | 0 | 1.5623 | 0 | 1.4347 | 1.5623 | 10.1864 | 1.1872 | 8.7517
39031.5646 | 2140 | 0 | 39031.5646 | 2226 | 0 |  | 1825.5 | 2044.5 | 130.6471 | 0 | 135.8974 | 0 | 1.3065 | 0 | 1.359 | 0 | 1.3065 | 1.359 | 20.9991 | 16.3243 | 19.6926
39031.5667 | 2226 | 0 | 39031.5667 | 2388 | 0 |  | 2010.5 | 2229.5 | 135.8974 | 0 | 145.7875 | 0 | 1.359 | 0 | 1.4579 | 0 | 1.359 | 1.4579 | 16.3243 | 8.433 | 14.9654
39031.5688 | 2117 | 56 | 39031.5689 | 2018 | 54 |  | 2195 | 2414 | 129.243 | 3.4188 | 123.199 | 3.2967 | 1.2924 | 0.034188 | 1.232 | 0.032967 | 1.2582 | 1.199 | 24.9978 | 32.688 | 183.1717
39031.571 | 1577 | 504 | 39031.571 | 1791 | 407 |  | 2379.5 | 2598.5 | 96.2759 | 30.7692 | 109.3407 | 24.8474 | 0.96276 | 0.30769 | 1.0934 | 0.24847 | 0.65507 | 0.84493 | 379.031 | 62.5385 | 38.8105

## A1-C5
Open Burn Test 8 |  |  | 2006-11-10 | 13:06 |  |  | Vs = |  | 156.7387 |  | R = | 100
Mix | 7-C | Tray A | IRMS | 1
0 | 150 kW |  | Bundle | Ch. 1 & 5 | Cable A | Odd - | Cable C |  | Odd
Time-7 | N11 | N12 | Time-8 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R5-G | R1-5
39031.541 | 1 | 0 | 39031.541 | 1 | 0 |  | -210 | 9 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256638 | 256638 | 256637.9994
39031.5431 | 1 | 0 | 39031.5432 | 1 | 0 |  | -25 | 194 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256638 | 256638 | 256637.9994
39031.5453 | 1 | 0 | 39031.5453 | 1 | 0 |  | 160 | 379 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256638 | 256638 | 256637.9994
39031.5474 | 1 | 0 | 39031.5474 | 2010 | 0 |  | 344.5 | 563.5 | 0.06105 | 0 | 122.7106 | 0 | 0.0006105 | 0 | 1.2271 | 0 | 0.0006105 | 1.2271 | 256638 | 27.7303 | 256637.9994
39031.5496 | 881 | 0 | 39031.5496 | 2188 | 0 |  | 529.5 | 748.5 | 53.7851 | 0 | 133.5775 | 0 | 0.53785 | 0 | 1.3358 | 0 | 0.53785 | 1.3358 | 191.4166 | 17.3391 | 190.8787
39031.5517 | 1946 | 0 | 39031.5517 | 2028 | 0 |  | 714 | 933 | 118.8034 | 0 | 123.8095 | 0 | 1.188 | 0 | 1.2381 | 0 | 1.188 | 1.2381 | 31.9311 | 26.5966 | 30.7431
39031.5538 | 2545 | 0 | 39031.5539 | 1927 | 0 |  | 899 | 1118 | 155.3724 | 0 | 117.6435 | 0 | 1.5537 | 0 | 1.1764 | 0 | 1.5537 | 1.1764 | 0.87937 | 33.232 | 0.67435
39031.556 | 2418 | 0 | 39031.556 | 2112 | 0 |  | 1083.5 | 1302.5 | 147.619 | 0 | 128.9377 | 0 | 1.4762 | 0 | 1.2894 | 0 | 1.4762 | 1.2894 | 6.1778 | 21.5616 | 4.7016
39031.5581 | 2163 | 0 | 39031.5581 | 1938 | 0 |  | 1268.5 | 1487.5 | 132.0513 | 0 | 118.315 | 0 | 1.3205 | 0 | 1.1832 | 0 | 1.3205 | 1.1832 | 18.6953 | 32.4757 | 17.3748
39031.5602 | 1999 | 0 | 39031.5603 | 2551 | 0 |  | 1453 | 1672 | 122.0391 | 0 | 155.7387 | 0 | 1.2204 | 0 | 1.5574 | 0 | 1.2204 | 1.5574 | 28.4332 | 0.6421 | 27.2128
39031.5624 | 2324 | 0 | 39031.5624 | 2105 | 0 |  | 1638 | 1857 | 141.8803 | 0 | 128.5104 | 0 | 1.4188 | 0 | 1.2851 | 0 | 1.4188 | 1.2851 | 10.4725 | 21.9658 | 9.0537
39031.5645 | 2081 | 0 | 39031.5645 | 2194 | 0 |  | 1822.5 | 2041.5 | 127.0452 | 0 | 133.9438 | 0 | 1.2705 | 0 | 1.3394 | 0 | 1.2705 | 1.3394 | 23.3724 | 17.0182 | 22.102
39031.5667 | 2527 | 0 | 39031.5667 | 2520 | 0 |  | 2007.5 | 2226.5 | 154.2735 | 0 | 153.8462 | 0 | 1.5427 | 0 | 1.5385 | 0 | 1.5427 | 1.5385 | 1.5979 | 1.8802 | 0.055207
39031.5688 | 1869 | 44 | 39031.5688 | 2317 | 59 |  | 2192.5 | 2411.5 | 114.1026 | 2.6862 | 141.453 | 3.602 | 1.141 | 0.026862 | 1.4145 | 0.03602 | 1.1142 | 1.3785 | 48.1735 | 11.7245 | 156.0715
39031.5709 | 1881 | 448 | 39031.571 | 2047 | 291 |  | 2377 | 2596 | 114.8352 | 27.3504 | 124.9695 | 17.7656 | 1.1484 | 0.2735 | 1.2497 | 0.17766 | 0.87485 | 1.072 | 553.4194 | 34.2253 | 13.5676

## A1-B4
Open Burn Test 8 |  |  | 2006-11-10 | 13:06 |  |  | Vs = |  | 157.5934 |  | R = | 100
Mix | 7-C | Tray A | IRMS | 1
0 | 150 kW |  | Bundle | Ch. 1 & 4 | Cable A | Odd - | Cable B |  | Even
Time-5 | N11 | N12 | Time-6 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R4-G | R1-4
39031.541 | 1 | 0 | 39031.541 | 1 | 0 |  | -212.5 | 6.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258038 | 258038 | 258037.9994
39031.5431 | 1 | 0 | 39031.5431 | 1 | 0 |  | -27.5 | 191.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258038 | 258038 | 258037.9994
39031.5452 | 1 | 0 | 39031.5453 | 1 | 0 |  | 157 | 376 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258038 | 258038 | 258037.9994
39031.5474 | 1 | 0 | 39031.5474 | 1 | 0 |  | 342 | 561 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258038 | 258038 | 258037.9994
39031.5495 | 638 | 0 | 39031.5495 | 1741 | 0 |  | 526.5 | 745.5 | 38.9499 | 0 | 106.2882 | 0 | 0.3895 | 0 | 1.0629 | 0 | 0.3895 | 1.0629 | 304.605 | 48.27 | 304.2155
39031.5517 | 2498 | 0 | 39031.5517 | 2110 | 0 |  | 711.5 | 930.5 | 152.5031 | 0 | 128.8156 | 0 | 1.525 | 0 | 1.2882 | 0 | 1.525 | 1.2882 | 3.3379 | 22.3403 | 1.8128
39031.5538 | 2210 | 0 | 39031.5538 | 2037 | 0 |  | 896 | 1115 | 134.9206 | 0 | 124.359 | 0 | 1.3492 | 0 | 1.2436 | 0 | 1.3492 | 1.2436 | 16.8045 | 26.7246 | 15.4553
39031.5559 | 2005 | 0 | 39031.556 | 2196 | 0 |  | 1081 | 1300 | 122.4054 | 0 | 134.0659 | 0 | 1.2241 | 0 | 1.3407 | 0 | 1.2241 | 1.3407 | 28.7471 | 17.5492 | 27.5231
39031.5581 | 2109 | 0 | 39031.5581 | 2408 | 0 |  | 1265.5 | 1484.5 | 128.7546 | 0 | 147.0085 | 0 | 1.2875 | 0 | 1.4701 | 0 | 1.2875 | 1.4701 | 22.3983 | 7.2002 | 21.1107
39031.5602 | 2046 | 0 | 39031.5602 | 2199 | 0 |  | 1450.5 | 1669.5 | 124.9084 | 0 | 134.2491 | 0 | 1.2491 | 0 | 1.3425 | 0 | 1.2491 | 1.3425 | 26.1672 | 17.3888 | 24.9181
39031.5623 | 2294 | 0 | 39031.5624 | 2423 | 0 |  | 1635 | 1854 | 140.0488 | 0 | 147.9243 | 0 | 1.4005 | 0 | 1.4792 | 0 | 1.4005 | 1.4792 | 12.5275 | 6.5365 | 11.127
39031.5645 | 2031 | 0 | 39031.5645 | 2565 | 0 |  | 1820 | 2039 | 123.9927 | 0 | 156.5934 | 0 | 1.2399 | 0 | 1.5659 | 0 | 1.2399 | 1.5659 | 27.099 | 0.6386 | 25.859
39031.5666 | 2268 | 0 | 39031.5666 | 2030 | 0 |  | 2004.5 | 2223.5 | 138.4615 | 0 | 123.9316 | 0 | 1.3846 | 0 | 1.2393 | 0 | 1.3846 | 1.2393 | 13.8175 | 27.1616 | 12.4328
39031.5688 | 2145 | 54 | 39031.5688 | 1896 | 54 |  | 2189.5 | 2408.5 | 130.9524 | 3.2967 | 115.7509 | 3.2967 | 1.3095 | 0.032967 | 1.1575 | 0.032967 | 1.2766 | 1.1245 | 22.2073 | 42.8674 | 212.469
39031.5709 | 1832 | 534 | 39031.5709 | 1502 | 399 |  | 2374 | 2593 | 111.8437 | 32.6007 | 91.6972 | 24.359 | 1.1184 | 0.32601 | 0.91697 | 0.24359 | 0.79243 | 0.67338 | 73.3714 | 193.0253 | 26.5689

## A1-B3
Open Burn Test 8 |  |  | 2006-11-10 | 13:06 |  |  | Vs = |  | 158.8144 |  | R = | 100
Mix | 7-C | Tray A | IRMS | 1
0 | 150 kW |  | Bundle | Ch. 1 & 3 | Cable A | Odd - | Cable B |  | Odd
Time-3 | N11 | N12 | Time-4 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R3-G | R1-3
39031.5409 | 1 | 0 | 39031.5409 | 1 | 0 |  | -215.5 | 3.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260038 | 260038 | 260037.9994
39031.5431 | 1 | 0 | 39031.5431 | 1 | 0 |  | -30.5 | 188.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260038 | 260038 | 260037.9994
39031.5452 | 1 | 0 | 39031.5452 | 1 | 0 |  | 154 | 373 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260038 | 260038 | 260037.9994
39031.5473 | 1 | 0 | 39031.5474 | 1 | 0 |  | 339 | 558 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260038 | 260038 | 260037.9994
39031.5495 | 288 | 0 | 39031.5495 | 1812 | 0 |  | 523.5 | 742.5 | 17.5824 | 0 | 110.6227 | 0 | 0.17582 | 0 | 1.1062 | 0 | 0.17582 | 1.1062 | 803.2569 | 43.564 | 803.0811
39031.5516 | 2078 | 0 | 39031.5516 | 2357 | 0 |  | 708.5 | 927.5 | 126.862 | 0 | 143.895 | 0 | 1.2686 | 0 | 1.4389 | 0 | 1.2686 | 1.4389 | 25.1867 | 10.3683 | 23.9181
39031.5538 | 2230 | 0 | 39031.5538 | 2303 | 0 |  | 893.5 | 1112.5 | 136.1416 | 0 | 140.5983 | 0 | 1.3614 | 0 | 1.406 | 0 | 1.3614 | 1.406 | 16.6538 | 12.9561 | 15.2924
39031.5559 | 2351 | 0 | 39031.5559 | 2581 | 0 |  | 1078 | 1297 | 143.5287 | 0 | 157.5702 | 0 | 1.4353 | 0 | 1.5757 | 0 | 1.4353 | 1.5757 | 10.6499 | 0.78962 | 9.2146
39031.558 | 2127 | 0 | 39031.5581 | 2091 | 0 |  | 1263 | 1482 | 129.8535 | 0 | 127.6557 | 0 | 1.2985 | 0 | 1.2766 | 0 | 1.2985 | 1.2766 | 22.3028 | 24.4084 | 21.0042
39031.5602 | 2410 | 0 | 39031.5602 | 2454 | 0 |  | 1447.5 | 1666.5 | 147.1306 | 0 | 149.8168 | 0 | 1.4713 | 0 | 1.4982 | 0 | 1.4713 | 1.4982 | 7.9411 | 6.0057 | 6.4698
39031.5623 | 2426 | 0 | 39031.5623 | 2090 | 0 |  | 1632.5 | 1851.5 | 148.1074 | 0 | 127.5946 | 0 | 1.4811 | 0 | 1.2759 | 0 | 1.4811 | 1.2759 | 7.2292 | 24.4679 | 5.7481
39031.5645 | 2334 | 0 | 39031.5645 | 2585 | 0 |  | 1817 | 2036 | 142.4908 | 0 | 157.8144 | 0 | 1.4249 | 0 | 1.5781 | 0 | 1.4249 | 1.5781 | 11.4559 | 0.63366 | 10.031
39031.5666 | 2409 | 0 | 39031.5666 | 2572 | 0 |  | 2002 | 2221 | 147.0696 | 0 | 157.0208 | 0 | 1.4707 | 0 | 1.5702 | 0 | 1.4707 | 1.5702 | 7.9859 | 1.1423 | 6.5152
39031.5687 | 2068 | 55 | 39031.5687 | 2071 | 52 |  | 2186.5 | 2405.5 | 126.2515 | 3.3578 | 126.4347 | 3.1746 | 1.2625 | 0.033578 | 1.2643 | 0.031746 | 1.2289 | 1.2326 | 29.2736 | 28.8036 | 194.5044
39031.5709 | 1425 | 547 | 39031.5709 | 1675 | 503 |  | 2371.5 | 2590.5 | 86.9963 | 33.3944 | 102.2589 | 30.7082 | 0.86996 | 0.33394 | 1.0226 | 0.30708 | 0.53602 | 0.71551 | 472.8611 | 86.9329 | 53.5087

## A1-A2
Open Burn Test 8 |  |  | 2006-11-10 | 13:06 |  |  | Vs = |  | 158.9976 |  | R = | 100
Mix | 7-C | Tray A | IRMS | 1
0 | 150 kW |  | Bundle | Ch. 1 & 2 | Cable A | Odd-Even
Time-1 | N11 | N12 | Time-2 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R2-G | R1-2
39031.5409 | 1 | 0 | 39031.5409 | 1 | 0 |  | -218.5 | 0.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260338 | 260338 | 260337.9994
39031.543 | 1 | 0 | 39031.5431 | 1 | 0 |  | -33.5 | 185.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260338 | 260338 | 260337.9994
39031.5452 | 2 | 0 | 39031.5452 | 1 | 0 |  | 151.5 | 370.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 130119 | 260338 | 130118.9988
39031.5473 | 1 | 0 | 39031.5473 | 2 | 0 |  | 336 | 555 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 260338 | 130119 | 260337.9994
39031.5495 | 1161 | 723 | 39031.5495 | 1227 | 864 |  | 521 | 740 | 70.8791 | 44.1392 | 74.9084 | 52.7473 | 0.70879 | 0.44139 | 0.74908 | 0.52747 | 0.2674 | 0.22161 | 400.0109 | 936.9559 | 90.029
39031.5516 | 2050 | 2 | 39031.5516 | 1949 | 1 |  | 705.5 | 924.5 | 125.1526 | 0.1221 | 118.9866 | 0.06105 | 1.2515 | 0.001221 | 1.1899 | 0.0006105 | 1.2503 | 1.1893 | 27.148 | 33.7075 | 6962.7129
39031.5537 | 2505 | 0 | 39031.5537 | 2040 | 0 |  | 890.5 | 1109.5 | 152.9304 | 0 | 124.5421 | 0 | 1.5293 | 0 | 1.2454 | 0 | 1.5293 | 1.2454 | 3.9673 | 27.6657 | 2.438
39031.5559 | 2531 | 0 | 39031.5559 | 2482 | 0 |  | 1075.5 | 1294.5 | 154.5177 | 0 | 151.5263 | 0 | 1.5452 | 0 | 1.5153 | 0 | 1.5452 | 1.5153 | 2.8992 | 4.9307 | 1.3541
39031.558 | 2384 | 0 | 39031.558 | 2106 | 0 |  | 1260 | 1479 | 145.5433 | 0 | 128.5714 | 0 | 1.4554 | 0 | 1.2857 | 0 | 1.4554 | 1.2857 | 9.2441 | 23.6648 | 7.7887
39031.5602 | 2529 | 0 | 39031.5602 | 2273 | 0 |  | 1444.5 | 1663.5 | 154.3956 | 0 | 138.7668 | 0 | 1.544 | 0 | 1.3877 | 0 | 1.544 | 1.3877 | 2.9806 | 14.579 | 1.4367
39031.5623 | 2588 | 0 | 39031.5623 | 2398 | 0 |  | 1629.5 | 1848.5 | 157.9976 | 0 | 146.398 | 0 | 1.58 | 0 | 1.464 | 0 | 1.58 | 1.464 | 0.63292 | 8.6063 | 0.94705
39031.5644 | 2384 | 0 | 39031.5644 | 2509 | 0 |  | 1814.5 | 2033.5 | 145.5433 | 0 | 153.1746 | 0 | 1.4554 | 0 | 1.5317 | 0 | 1.4554 | 1.5317 | 9.2441 | 3.8015 | 7.7887
39031.5666 | 2317 | 0 | 39031.5666 | 2195 | 0 |  | 1999 | 2218 | 141.453 | 0 | 134.0049 | 0 | 1.4145 | 0 | 1.34 | 0 | 1.4145 | 1.34 | 12.4031 | 18.6506 | 10.9886
39031.5687 | 2308 | 57 | 39031.5687 | 2383 | 76 |  | 2184 | 2403 | 140.9035 | 3.4799 | 145.4823 | 4.6398 | 1.409 | 0.034799 | 1.4548 | 0.046398 | 1.3742 | 1.4084 | 16.7056 | 11.9532 | 44.8394
39031.5708 | 1905 | 574 | 39031.5709 | 1513 | 606 |  | 2368.5 | 2587.5 | 116.3004 | 35.0427 | 92.3687 | 36.9963 | 1.163 | 0.35043 | 0.92369 | 0.36996 | 0.81258 | 0.55372 | 44.5753 | 241.1898 | 15.4411

## Temps
DAQ Time | Burner Time | Bundle center | Air above bundle | Air below bundle | Intra-bundle | TRAY A
0 | -219 | 15.1 | 14.7 | 14.9 | 15.3 | 16.2
1 | -218 | 15 | 14.7 | 14.9 | 15.3 | 16.2
2 | -217 | 15 | 14.7 | 14.9 | 15.3 | 16.2
3 | -216 | 15.1 | 14.7 | 14.9 | 15.3 | 16.2
4 | -215 | 15 | 14.7 | 14.9 | 15.3 | 16.2
5 | -214 | 15 | 14.7 | 14.9 | 15.3 | 16.2
6.1 | -212.9 | 15 | 14.7 | 14.9 | 15.3 | 16.2
7.1 | -211.9 | 15.1 | 14.7 | 14.9 | 15.3 | 16.2
8.1 | -210.9 | 15.1 | 14.7 | 14.9 | 15.3 | 16.2
9.1 | -209.9 | 15.1 | 14.7 | 14.9 | 15.3 | 16.2
10.1 | -208.9 | 15.1 | 14.7 | 14.9 | 15.3 | 16.2
11.1 | -207.9 | 15.1 | 14.7 | 14.9 | 15.3 | 16.2
12.1 | -206.9 | 15 | 14.7 | 14.9 | 15.3 | 16.2
13.1 | -205.9 | 15.1 | 14.7 | 14.9 | 15.3 | 16.2
14.1 | -204.9 | 15.1 | 14.7 | 14.9 | 15.3 | 16.2
15.1 | -203.9 | 15.1 | 14.7 | 14.9 | 15.3 | 16.2
16.1 | -202.9 | 15.1 | 14.7 | 14.9 | 15.3 | 16.2
17.1 | -201.9 | 15 | 14.7 | 14.9 | 15.3 | 16.2
18.1 | -200.9 | 15 | 14.7 | 14.9 | 15.3 | 16.2
19.1 | -199.9 | 15.1 | 14.7 | 14.9 | 15.3 | 16.2
20.1 | -198.9 | 15 | 14.7 | 14.9 | 15.3 | 16.2
21.1 | -197.9 | 15 | 14.7 | 14.9 | 15.3 | 16.2
22.1 | -196.9 | 15 | 14.7 | 14.9 | 15.3 | 16.2
23.1 | -195.9 | 15 | 14.7 | 14.9 | 15.3 | 16.2
24.1 | -194.9 | 15 | 14.7 | 14.9 | 15.3 | 16.2
25.1 | -193.9 | 15 | 14.7 | 14.9 | 15.3 | 16.2
26.1 | -192.9 | 15 | 14.7 | 14.9 | 15.3 | 16.2
27.1 | -191.9 | 15 | 14.7 | 14.9 | 15.3 | 16.2
28.1 | -190.9 | 15.1 | 14.7 | 14.9 | 15.3 | 16.2
29.1 | -189.9 | 15.1 | 14.7 | 14.9 | 15.3 | 16.2
30.1 | -188.9 | 15 | 14.7 | 14.9 | 15.3 | 16.2
31.1 | -187.9 | 15 | 14.7 | 14.9 | 15.3 | 16.2
32.1 | -186.9 | 15.1 | 14.7 | 14.9 | 15.3 | 16.2
33.1 | -185.9 | 15 | 14.8 | 14.9 | 15.3 | 16.2
34.1 | -184.9 | 15 | 14.7 | 14.9 | 15.3 | 16.2
35.1 | -183.9 | 15 | 14.7 | 14.9 | 15.3 | 16.2
36.1 | -182.9 | 15.1 | 14.7 | 14.9 | 15.3 | 16.2
37.1 | -181.9 | 15 | 14.7 | 14.9 | 15.3 | 16.2
38.1 | -180.9 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2
39.1 | -179.9 | 15.1 | 14.7 | 14.9 | 15.3 | 16.2
40.1 | -178.9 | 15.1 | 14.7 | 14.9 | 15.3 | 16.2
41.1 | -177.9 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2
42.1 | -176.9 | 15 | 14.7 | 14.9 | 15.3 | 16.2
43.1 | -175.9 | 15 | 14.8 | 14.9 | 15.3 | 16.2
44.1 | -174.9 | 15.1 | 14.7 | 14.9 | 15.3 | 16.2
45.1 | -173.9 | 15 | 14.8 | 14.9 | 15.3 | 16.2
46.2 | -172.8 | 15 | 14.7 | 14.9 | 15.3 | 16.2
47.2 | -171.8 | 15.1 | 14.7 | 14.9 | 15.3 | 16.2
48.2 | -170.8 | 15.1 | 14.7 | 14.9 | 15.3 | 16.2
49.2 | -169.8 | 15 | 14.7 | 14.9 | 15.3 | 16.2
50.2 | -168.8 | 15.1 | 14.7 | 14.9 | 15.3 | 16.2
51.2 | -167.8 | 15.1 | 14.7 | 14.9 | 15.3 | 16.2
52.2 | -166.8 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2
53.2 | -165.8 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2
54.2 | -164.8 | 15.1 | 14.7 | 14.9 | 15.3 | 16.2
55.2 | -163.8 | 15.1 | 14.7 | 14.9 | 15.3 | 16.2
56.2 | -162.8 | 15 | 14.7 | 14.9 | 15.3 | 16.2
57.2 | -161.8 | 15 | 14.7 | 14.9 | 15.3 | 16.2
58.2 | -160.8 | 15 | 14.7 | 14.9 | 15.3 | 16.2
59.2 | -159.8 | 15 | 14.7 | 14.9 | 15.3 | 16.2
60.2 | -158.8 | 15.1 | 14.7 | 14.9 | 15.3 | 16.2
61.2 | -157.8 | 15 | 14.7 | 14.9 | 15.3 | 16.2
62.2 | -156.8 | 15 | 14.7 | 14.9 | 15.3 | 16.2
63.2 | -155.8 | 15 | 14.7 | 14.9 | 15.3 | 16.2
64.2 | -154.8 | 15.1 | 14.7 | 14.9 | 15.3 | 16.2
65.2 | -153.8 | 15 | 14.7 | 14.9 | 15.3 | 16.2
66.2 | -152.8 | 15.1 | 14.7 | 14.9 | 15.3 | 16.2
67.2 | -151.8 | 15 | 14.7 | 14.9 | 15.3 | 16.2
68.2 | -150.8 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2
69.2 | -149.8 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2
70.2 | -148.8 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2
71.2 | -147.8 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2
72.2 | -146.8 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2
73.2 | -145.8 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2
74.2 | -144.8 | 15 | 14.8 | 14.9 | 15.3 | 16.2
75.2 | -143.8 | 15 | 14.8 | 14.9 | 15.3 | 16.2
76.2 | -142.8 | 15.1 | 14.7 | 14.9 | 15.3 | 16.2
77.2 | -141.8 | 15 | 14.7 | 14.9 | 15.3 | 16.2
78.2 | -140.8 | 15.1 | 14.7 | 14.9 | 15.3 | 16.2
79.2 | -139.8 | 15 | 14.7 | 14.9 | 15.3 | 16.2
80.2 | -138.8 | 15.1 | 14.7 | 14.9 | 15.3 | 16.2
81.2 | -137.8 | 15 | 14.7 | 14.9 | 15.3 | 16.2
82.2 | -136.8 | 15.1 | 14.7 | 14.9 | 15.3 | 16.2
83.3 | -135.7 | 15 | 14.7 | 14.9 | 15.3 | 16.2
84.3 | -134.7 | 15.1 | 14.7 | 14.9 | 15.3 | 16.2
85.3 | -133.7 | 15 | 14.7 | 14.9 | 15.3 | 16.2
86.3 | -132.7 | 15 | 14.7 | 14.9 | 15.3 | 16.2
87.3 | -131.7 | 15 | 14.7 | 14.9 | 15.3 | 16.2
88.3 | -130.7 | 15.1 | 14.7 | 14.9 | 15.3 | 16.2
89.3 | -129.7 | 15 | 14.7 | 14.9 | 15.3 | 16.2
90.3 | -128.7 | 15.1 | 14.7 | 14.9 | 15.3 | 16.2
91.3 | -127.7 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2
92.3 | -126.7 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2
93.3 | -125.7 | 15 | 14.8 | 14.9 | 15.3 | 16.2
94.3 | -124.7 | 15 | 14.7 | 14.9 | 15.3 | 16.2
95.3 | -123.7 | 15 | 14.7 | 14.9 | 15.3 | 16.2
96.3 | -122.7 | 15 | 14.8 | 14.9 | 15.3 | 16.2
97.3 | -121.7 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2
98.3 | -120.7 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2
99.3 | -119.7 | 15 | 14.8 | 14.9 | 15.3 | 16.2
100.3 | -118.7 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2
101.3 | -117.7 | 15 | 14.8 | 14.9 | 15.3 | 16.2
102.3 | -116.7 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2
103.3 | -115.7 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2
104.3 | -114.7 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2
105.3 | -113.7 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2
106.3 | -112.7 | 15 | 14.8 | 14.9 | 15.3 | 16.2
107.3 | -111.7 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2
108.3 | -110.7 | 15 | 14.8 | 14.9 | 15.3 | 16.2
109.3 | -109.7 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2
110.3 | -108.7 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2
111.3 | -107.7 | 15 | 14.8 | 14.9 | 15.3 | 16.2
112.3 | -106.7 | 15 | 14.8 | 14.9 | 15.3 | 16.2
113.3 | -105.7 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2
114.3 | -104.7 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2
115.3 | -103.7 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2
116.3 | -102.7 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2
117.3 | -101.7 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2
118.3 | -100.7 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2
119.3 | -99.7 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2
120.3 | -98.7 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2
121.3 | -97.7 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2
122.3 | -96.7 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2
123.3 | -95.7 | 15 | 14.8 | 14.9 | 15.3 | 16.2
124.3 | -94.7 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2
125.3 | -93.7 | 15 | 14.8 | 14.9 | 15.3 | 16.2
126.3 | -92.7 | 15 | 14.8 | 14.9 | 15.3 | 16.2
127.3 | -91.7 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2
128.3 | -90.7 | 15 | 14.8 | 14.9 | 15.3 | 16.2
129.3 | -89.7 | 15 | 14.8 | 14.9 | 15.3 | 16.2
130.3 | -88.7 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2
131.3 | -87.7 | 15 | 14.8 | 14.9 | 15.3 | 16.2
132.3 | -86.7 | 15 | 14.8 | 14.9 | 15.3 | 16.2
133.3 | -85.7 | 15 | 14.8 | 14.9 | 15.3 | 16.2
134.3 | -84.7 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2
135.3 | -83.7 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2
136.3 | -82.7 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2
137.3 | -81.7 | 15 | 14.8 | 14.9 | 15.3 | 16.2
138.3 | -80.7 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2
139.3 | -79.7 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2
140.3 | -78.7 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2
141.3 | -77.7 | 15 | 14.8 | 14.9 | 15.3 | 16.2
142.3 | -76.7 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2
143.3 | -75.7 | 15 | 14.8 | 14.9 | 15.3 | 16.2
144.3 | -74.7 | 15 | 14.8 | 14.9 | 15.3 | 16.2
145.3 | -73.7 | 15 | 14.8 | 14.9 | 15.3 | 16.2
146.3 | -72.7 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2
147.3 | -71.7 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2
148.3 | -70.7 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2
149.3 | -69.7 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2
150.3 | -68.7 | 15 | 14.8 | 14.9 | 15.3 | 16.2
151.3 | -67.7 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2
152.3 | -66.7 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2
153.3 | -65.7 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2
154.3 | -64.7 | 15.1 | 14.8 | 15 | 15.3 | 16.2
155.3 | -63.7 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2
156.3 | -62.7 | 15.1 | 14.8 | 15 | 15.3 | 16.2
157.3 | -61.7 | 15.1 | 14.8 | 15 | 15.3 | 16.2
158.3 | -60.7 | 15.1 | 14.8 | 15 | 15.3 | 16.2
159.3 | -59.7 | 15.1 | 14.8 | 15 | 15.3 | 16.2
160.3 | -58.7 | 15 | 14.8 | 15 | 15.3 | 16.2
161.3 | -57.7 | 15 | 14.8 | 15 | 15.3 | 16.2
162.3 | -56.7 | 15.1 | 14.8 | 15 | 15.3 | 16.2
163.3 | -55.7 | 15.1 | 14.8 | 15 | 15.3 | 16.2
164.3 | -54.7 | 15.1 | 14.8 | 15 | 15.3 | 16.2
165.3 | -53.7 | 15.1 | 14.8 | 15 | 15.3 | 16.2
166.3 | -52.7 | 15.1 | 14.8 | 15 | 15.3 | 16.2
167.3 | -51.7 | 15.1 | 14.8 | 15 | 15.3 | 16.2
168.3 | -50.7 | 15 | 14.8 | 15 | 15.3 | 16.2
169.3 | -49.7 | 15.1 | 14.8 | 15 | 15.3 | 16.2
170.3 | -48.7 | 15.1 | 14.8 | 15 | 15.3 | 16.2
171.3 | -47.7 | 15.1 | 14.8 | 15 | 15.3 | 16.2
172.3 | -46.7 | 15 | 14.8 | 15 | 15.3 | 16.2
173.3 | -45.7 | 15.1 | 14.8 | 15 | 15.3 | 16.2
174.3 | -44.7 | 15.1 | 14.8 | 15 | 15.3 | 16.2
175.3 | -43.7 | 15.1 | 14.8 | 15 | 15.3 | 16.2
176.3 | -42.7 | 15.1 | 14.8 | 15 | 15.3 | 16.2
177.3 | -41.7 | 15.1 | 14.8 | 15 | 15.3 | 16.2
178.3 | -40.7 | 15.1 | 14.8 | 15 | 15.3 | 16.2
179.3 | -39.7 | 15.1 | 14.8 | 15 | 15.3 | 16.2
180.3 | -38.7 | 15.1 | 14.8 | 15 | 15.3 | 16.2
181.3 | -37.7 | 15.1 | 14.8 | 15 | 15.3 | 16.2
182.3 | -36.7 | 15.1 | 14.8 | 15 | 15.3 | 16.2
183.3 | -35.7 | 15.1 | 14.8 | 15 | 15.3 | 16.2
184.3 | -34.7 | 15.1 | 14.8 | 15 | 15.3 | 16.2
185.3 | -33.7 | 15.1 | 14.8 | 15 | 15.3 | 16.3
186.3 | -32.7 | 15.1 | 14.8 | 15 | 15.3 | 16.2
187.3 | -31.7 | 15.1 | 14.8 | 15 | 15.3 | 16.2
188.3 | -30.7 | 15.1 | 14.8 | 15 | 15.3 | 16.2
189.3 | -29.7 | 15.1 | 14.8 | 15 | 15.3 | 16.2
190.3 | -28.7 | 15.1 | 14.8 | 15 | 15.3 | 16.2
191.3 | -27.7 | 15.1 | 14.8 | 15 | 15.3 | 16.2
192.3 | -26.7 | 15.1 | 14.8 | 15 | 15.3 | 16.2
193.3 | -25.7 | 15.1 | 14.8 | 15 | 15.3 | 16.2
194.3 | -24.7 | 15.1 | 14.8 | 15 | 15.3 | 16.2
195.3 | -23.7 | 15.1 | 14.8 | 15 | 15.3 | 16.2
196.3 | -22.7 | 15.1 | 14.8 | 15 | 15.3 | 16.3
197.3 | -21.7 | 15.1 | 14.8 | 15 | 15.3 | 16.3
198.3 | -20.7 | 15.1 | 14.8 | 15 | 15.3 | 16.2
199.3 | -19.7 | 15.1 | 14.8 | 15 | 15.3 | 16.3
200.3 | -18.7 | 15.1 | 14.8 | 15 | 15.3 | 16.2
201.3 | -17.7 | 15.1 | 14.8 | 15 | 15.3 | 16.3
202.3 | -16.7 | 15.1 | 14.8 | 15 | 15.3 | 16.3
203.3 | -15.7 | 15.1 | 14.8 | 15 | 15.3 | 16.3
204.3 | -14.7 | 15.1 | 14.8 | 15 | 15.3 | 16.3
205.3 | -13.7 | 15.1 | 14.8 | 15 | 15.3 | 16.3
206.3 | -12.7 | 15.1 | 14.8 | 15 | 15.3 | 16.3
207.3 | -11.7 | 15.1 | 14.8 | 15 | 15.3 | 16.3
208.3 | -10.7 | 15.1 | 14.8 | 15 | 15.3 | 16.3
209.3 | -9.7 | 15.1 | 14.8 | 15 | 15.3 | 16.3
210.3 | -8.7 | 15.1 | 14.8 | 15 | 15.3 | 16.3
211.3 | -7.7 | 15.1 | 14.8 | 15 | 15.3 | 16.3
212.3 | -6.7 | 15.1 | 14.8 | 15 | 15.3 | 16.3
213.3 | -5.7 | 15.1 | 14.8 | 15 | 15.3 | 16.3
214.3 | -4.7 | 15.1 | 14.8 | 15 | 15.3 | 16.3
215.3 | -3.7 | 15.1 | 14.8 | 15 | 15.3 | 16.3
216.3 | -2.7 | 15.1 | 14.8 | 15 | 15.3 | 16.3
217.3 | -1.7 | 15.1 | 14.8 | 15 | 15.3 | 16.3
218.3 | -0.7 | 15.1 | 14.8 | 15 | 15.3 | 16.3
219.3 | 0.3 | 15.1 | 14.8 | 15 | 15.3 | 16.3
220.3 | 1.3 | 15.1 | 14.8 | 15 | 15.3 | 16.3
221.3 | 2.3 | 15.1 | 14.8 | 15 | 15.3 | 16.3
222.3 | 3.3 | 15.1 | 14.8 | 15 | 15.3 | 16.3
223.3 | 4.3 | 15.1 | 14.8 | 15 | 15.3 | 16.3
224.3 | 5.3 | 15.1 | 14.8 | 15.1 | 15.3 | 16.3
225.3 | 6.3 | 15.1 | 14.9 | 15.6 | 15.3 | 16.4
226.3 | 7.3 | 15.1 | 15.8 | 19.5 | 15.3 | 16.7
227.3 | 8.3 | 15.1 | 18.1 | 23.9 | 15.3 | 17
228.3 | 9.3 | 15.1 | 21.2 | 32.3 | 15.3 | 17.9
229.3 | 10.3 | 15.1 | 26.6 | 49.3 | 15.4 | 19.4
230.3 | 11.3 | 15.1 | 33.6 | 69 | 15.4 | 20.9
231.3 | 12.3 | 15.1 | 39.7 | 83.4 | 15.5 | 22.1
232.3 | 13.3 | 15.1 | 48.2 | 102 | 15.5 | 24.8
233.3 | 14.3 | 15.1 | 59.9 | 133.3 | 15.6 | 27.3
234.3 | 15.3 | 15.1 | 82.6 | 192.5 | 15.7 | 30.4
235.3 | 16.3 | 15.2 | 120.1 | 254.8 | 15.8 | 34.5
236.3 | 17.3 | 15.3 | 143.8 | 285.5 | 15.9 | 39.7
237.3 | 18.3 | 15.4 | 170.2 | 333 | 15.9 | 45.4
238.3 | 19.3 | 15.5 | 196.6 | 362.1 | 16 | 48.5
239.3 | 20.3 | 15.7 | 217.5 | 380.5 | 16.1 | 52.3
240.3 | 21.3 | 15.9 | 237.3 | 400.3 | 16.2 | 56.3
241.3 | 22.3 | 16.1 | 245.7 | 416.8 | 16.3 | 62.2
242.3 | 23.3 | 16.4 | 265.6 | 451.2 | 16.4 | 69.6
243.3 | 24.3 | 16.6 | 284.3 | 472.3 | 16.4 | 74.5
244.3 | 25.3 | 16.9 | 306.3 | 496.4 | 17.1 | 79.1
245.3 | 26.3 | 17.3 | 330.5 | 515.4 | 18.4 | 83.2
246.3 | 27.3 | 17.7 | 343 | 523.3 | 19.7 | 87.7
247.3 | 28.3 | 18.2 | 349.3 | 534.1 | 20.9 | 91.8
248.3 | 29.3 | 18.7 | 362.3 | 546 | 21.9 | 96.3
249.3 | 30.3 | 19.3 | 367.3 | 548.8 | 23 | 97.9
250.3 | 31.3 | 19.9 | 389.9 | 559.3 | 25.2 | 99.5
251.3 | 32.3 | 20.6 | 400.4 | 564.8 | 27 | 101.7
252.3 | 33.3 | 21.4 | 410.1 | 575.6 | 28.7 | 104.3
253.3 | 34.3 | 22.2 | 411.5 | 577.7 | 29.9 | 106.2
254.3 | 35.3 | 23.2 | 426.9 | 589.2 | 31.2 | 109.8
255.3 | 36.3 | 24.2 | 441.2 | 603.6 | 33.2 | 113.7
256.3 | 37.3 | 25.3 | 452.5 | 607.2 | 35.6 | 116.3
257.3 | 38.3 | 26.5 | 452.7 | 605 | 36.9 | 118.2
258.3 | 39.3 | 27.7 | 447.3 | 595.9 | 37.9 | 119.9
259.3 | 40.3 | 29.1 | 448.9 | 598 | 38.8 | 122.8
260.3 | 41.3 | 30.8 | 453.9 | 598.1 | 40.4 | 125.7
261.3 | 42.3 | 32 | 466.9 | 602.9 | 43 | 128.8
262.3 | 43.3 | 33.4 | 481.2 | 614.2 | 44.8 | 131.5
263.3 | 44.3 | 35 | 487.5 | 611.4 | 46.4 | 132.5
264.3 | 45.3 | 36.8 | 480.6 | 598.7 | 46 | 134.3
265.3 | 46.3 | 38.6 | 484.3 | 609 | 47.1 | 136.3
266.3 | 47.3 | 40.5 | 474.4 | 608.9 | 47.8 | 139.4
267.3 | 48.3 | 42.5 | 472.4 | 612.3 | 48.8 | 143
268.3 | 49.3 | 44.7 | 469.1 | 611.1 | 49.6 | 147.4
269.3 | 50.3 | 46.9 | 467.9 | 612.2 | 51.3 | 152.6
270.3 | 51.3 | 48.6 | 466.1 | 609.8 | 54.4 | 154.7
271.3 | 52.3 | 50.5 | 476.6 | 610.3 | 57.2 | 156.8
272.3 | 53.3 | 52.3 | 484.1 | 622.7 | 60.4 | 159.4
273.3 | 54.3 | 54.2 | 486.5 | 621.7 | 63.9 | 162.9
274.3 | 55.3 | 56.2 | 495.6 | 624.4 | 67.9 | 166.2
275.3 | 56.3 | 58.7 | 502.7 | 628 | 73.1 | 169.7
276.3 | 57.3 | 62.3 | 505.3 | 626.7 | 78.8 | 170.5
277.3 | 58.3 | 63.9 | 507.8 | 627.9 | 82.5 | 171.8
278.3 | 59.3 | 65.7 | 498 | 610.6 | 84.1 | 173.5
279.3 | 60.3 | 67.7 | 492.4 | 607.1 | 88.4 | 177
280.3 | 61.3 | 69.7 | 495.1 | 608 | 91.8 | 180
281.3 | 62.3 | 71.7 | 490.8 | 603.6 | 95.9 | 181.9
282.3 | 63.3 | 73.9 | 484.2 | 601.8 | 101.3 | 183.3
283.3 | 64.3 | 76.1 | 481.4 | 592.1 | 105.5 | 184.1
284.3 | 65.3 | 78.2 | 477 | 588.3 | 109.8 | 185.2
285.3 | 66.3 | 80.5 | 474 | 593.2 | 113.2 | 187.7
286.3 | 67.3 | 82.5 | 470.1 | 595 | 115.9 | 191.3
287.3 | 68.3 | 84.4 | 476.4 | 599.8 | 118.7 | 193.8
288.3 | 69.3 | 86.7 | 474.5 | 594.8 | 122.2 | 197.4
289.3 | 70.3 | 88.8 | 482.2 | 602.7 | 127.8 | 203.2
290.3 | 71.3 | 90.5 | 489.3 | 604.6 | 134.1 | 205.5
291.3 | 72.3 | 92.3 | 493.3 | 603.2 | 138.7 | 207.1
292.3 | 73.3 | 94.5 | 499.1 | 599.4 | 143.4 | 208.5
293.3 | 74.3 | 97.3 | 502.7 | 591.8 | 146.9 | 209.9
294.3 | 75.3 | 100.5 | 510.9 | 597 | 153.9 | 211.6
295.3 | 76.3 | 104 | 519.8 | 601 | 161.6 | 213.5
296.3 | 77.3 | 107.5 | 522.1 | 592.3 | 164.8 | 215.7
297.3 | 78.3 | 111.3 | 520.4 | 576.5 | 166.3 | 215.3
298.3 | 79.3 | 115.7 | 507.4 | 562.4 | 166.5 | 215.6
299.3 | 80.3 | 119.5 | 503 | 561.9 | 167.5 | 215.7
300.3 | 81.3 | 122.9 | 510.8 | 573.4 | 169.7 | 218.7
301.3 | 82.3 | 125.7 | 525.3 | 578.6 | 174.3 | 221.9
302.3 | 83.3 | 128.2 | 527.4 | 569.8 | 172.7 | 222.3
303.3 | 84.3 | 131.1 | 526.4 | 565.2 | 172.8 | 223.4
304.3 | 85.3 | 134.8 | 538 | 578.6 | 177.9 | 226.6
305.3 | 86.3 | 138.2 | 527 | 556.7 | 177.9 | 227.5
306.3 | 87.3 | 141.5 | 535.3 | 561 | 184.1 | 227.7
307.3 | 88.3 | 145 | 540.3 | 567.7 | 185.5 | 231.6
308.3 | 89.3 | 148.5 | 545.5 | 571.8 | 186.9 | 233.4
309.3 | 90.3 | 152.4 | 546.7 | 584.7 | 191.7 | 236.9
310.3 | 91.3 | 156.3 | 544.5 | 578.1 | 197.8 | 237.6
311.3 | 92.3 | 160.1 | 574.5 | 592.7 | 208.2 | 240.8
312.3 | 93.3 | 163.4 | 588.7 | 608 | 211.3 | 244.5
313.3 | 94.3 | 166.3 | 610.4 | 618.4 | 214.4 | 249
314.3 | 95.3 | 168.9 | 639.8 | 633 | 221 | 253.4
315.3 | 96.3 | 171.3 | 664.6 | 632.5 | 218.3 | 259.6
316.3 | 97.3 | 173.5 | 672.8 | 636.5 | 216.1 | 261.1
317.3 | 98.3 | 175.8 | 683.4 | 631.3 | 216.9 | 263.4
318.3 | 99.3 | 178.4 | 692.9 | 642.1 | 218.5 | 268.8
319.3 | 100.3 | 180.9 | 700.5 | 649.6 | 221.7 | 274.1
320.3 | 101.3 | 183.3 | 712.3 | 649.4 | 226.2 | 276.3
321.3 | 102.3 | 185.8 | 711.1 | 630.8 | 227 | 276.5
322.3 | 103.3 | 188 | 712.3 | 626.7 | 227.4 | 276.8
323.3 | 104.3 | 190 | 720.7 | 633 | 226.5 | 280.2
324.3 | 105.3 | 192.1 | 716.7 | 628.3 | 225.9 | 281.2
325.3 | 106.3 | 194.1 | 725.6 | 636.7 | 229.6 | 283
326.3 | 107.3 | 196.2 | 741.1 | 635.7 | 232.3 | 285
327.3 | 108.3 | 198.3 | 745.8 | 644.8 | 237.1 | 287.8
328.3 | 109.3 | 200.7 | 756.2 | 652.7 | 238.2 | 293.4
329.3 | 110.3 | 202.7 | 762.7 | 647.4 | 238.3 | 294.7
330.3 | 111.3 | 204.6 | 764.5 | 632.4 | 233.9 | 295.2
331.3 | 112.3 | 206.5 | 761.6 | 628.1 | 232.9 | 295.3
332.3 | 113.3 | 208 | 756.5 | 632.5 | 232.4 | 298.7
333.3 | 114.3 | 209.9 | 756.5 | 645.1 | 231.8 | 307.1
334.3 | 115.3 | 212 | 761 | 654.1 | 235.9 | 314.8
335.3 | 116.3 | 214.4 | 765.1 | 658.1 | 238.6 | 317.9
336.3 | 117.3 | 217.5 | 765 | 648.6 | 243.5 | 317.4
337.3 | 118.3 | 220.3 | 771.2 | 653.6 | 251.4 | 319.9
338.3 | 119.3 | 223.2 | 772.5 | 658.4 | 255.7 | 324.2
339.3 | 120.3 | 226 | 770.8 | 654.8 | 257.4 | 326.9
340.3 | 121.3 | 228.4 | 754.6 | 636.6 | 258.3 | 324.6
341.3 | 122.3 | 230.7 | 740.2 | 617 | 257.2 | 324
342.3 | 123.3 | 233.1 | 731.6 | 614.3 | 258.7 | 325.4
343.3 | 124.3 | 235.2 | 730.5 | 615 | 263.6 | 326.5
344.3 | 125.3 | 236.9 | 735.7 | 613.9 | 268.3 | 329.1
345.3 | 126.3 | 238.8 | 737.5 | 626.1 | 273.4 | 330.7
346.3 | 127.3 | 240.9 | 734.8 | 620.4 | 276.1 | 330.5
347.3 | 128.3 | 243.4 | 721.2 | 608.6 | 278.1 | 331.3
348.3 | 129.3 | 245.4 | 714.8 | 602.9 | 278.8 | 331.6
349.3 | 130.3 | 247.7 | 713.8 | 598.7 | 279.7 | 332
350.3 | 131.3 | 249.9 | 715.8 | 592.8 | 281 | 332.1
351.3 | 132.3 | 252 | 721.1 | 592.4 | 282.8 | 333.6
352.3 | 133.3 | 253.9 | 727 | 592.2 | 284.8 | 334.4
353.3 | 134.3 | 255.6 | 726.4 | 588.3 | 289.3 | 334.6
354.3 | 135.3 | 257.6 | 719.2 | 585 | 292.5 | 335.9
355.3 | 136.3 | 259.7 | 719.2 | 579.9 | 293.5 | 334.8
356.3 | 137.3 | 262 | 710.5 | 565.2 | 294.6 | 334.8
357.3 | 138.3 | 263.9 | 702.7 | 567.9 | 296.3 | 334.7
358.3 | 139.3 | 265.6 | 703.7 | 588.1 | 299.8 | 339.2
359.3 | 140.3 | 267.4 | 701.3 | 590 | 300.9 | 340.3
360.3 | 141.3 | 269.2 | 688.5 | 577.3 | 302.5 | 340.2
361.3 | 142.3 | 270.7 | 679.2 | 564.8 | 301.6 | 339.4
362.3 | 143.3 | 271.8 | 661.6 | 561.6 | 301 | 339.4
363.3 | 144.3 | 272.8 | 659.1 | 564.7 | 299.6 | 341.5
364.3 | 145.3 | 273.7 | 640.8 | 545 | 299.4 | 340.4
365.3 | 146.3 | 274.4 | 623.4 | 534.8 | 299.7 | 340
366.3 | 147.3 | 274.9 | 605.7 | 532.2 | 299.3 | 340.5
367.3 | 148.3 | 275.4 | 601 | 532.6 | 300.4 | 341.5
368.3 | 149.3 | 275.9 | 589.3 | 539.7 | 301.4 | 341.8
369.3 | 150.3 | 276.4 | 577.7 | 542.5 | 301.4 | 342.5
370.3 | 151.3 | 277 | 566.3 | 541.6 | 301 | 342.5
371.3 | 152.3 | 277.8 | 559.6 | 554.9 | 300.9 | 344.9
372.3 | 153.3 | 278.7 | 556.3 | 554.4 | 302.1 | 345
373.3 | 154.3 | 279.5 | 568.4 | 559.8 | 306.9 | 346.1
374.3 | 155.3 | 280.6 | 574.2 | 565.1 | 307.9 | 347.9
375.3 | 156.3 | 281.7 | 580.3 | 555.8 | 309.1 | 348.2
376.3 | 157.3 | 282.9 | 579.7 | 553.2 | 309.7 | 348.4
377.3 | 158.3 | 284.3 | 576.4 | 548.9 | 309.8 | 348.4
378.3 | 159.3 | 285.6 | 575.9 | 544.4 | 310.3 | 348.1
379.3 | 160.3 | 286.8 | 572.9 | 538.9 | 309.9 | 348.4
380.3 | 161.3 | 288 | 571.6 | 533.7 | 310.5 | 348.5
381.3 | 162.3 | 289.4 | 558.4 | 530.7 | 310.5 | 347.5
382.3 | 163.3 | 290.8 | 555.8 | 528.4 | 311.2 | 347.3
383.3 | 164.3 | 292.2 | 556 | 530.9 | 312.1 | 348
384.3 | 165.3 | 293.6 | 560.4 | 529.2 | 313.3 | 347.9
385.3 | 166.3 | 295.1 | 559.2 | 529 | 313.3 | 348.1
386.3 | 167.3 | 296.6 | 544.1 | 511.1 | 311.8 | 346.6
387.3 | 168.3 | 297.9 | 529.4 | 501.3 | 309.8 | 345.9
388.3 | 169.3 | 299 | 520 | 504.1 | 309.1 | 347.4
389.3 | 170.3 | 299.9 | 516.3 | 507.8 | 308.5 | 347.9
390.3 | 171.3 | 300.9 | 522.8 | 517.3 | 308.5 | 349.5
391.3 | 172.3 | 302 | 519.9 | 510.6 | 308.8 | 349.7
392.3 | 173.3 | 303.3 | 522.7 | 505.8 | 309.7 | 349
393.3 | 174.3 | 304.8 | 530.7 | 518.6 | 310.6 | 349.8
394.3 | 175.3 | 306.7 | 543 | 531.6 | 311.4 | 352.2
395.3 | 176.3 | 308.9 | 569.9 | 557 | 312.3 | 356
396.3 | 177.3 | 311.1 | 589.1 | 570.1 | 312 | 358.2
397.3 | 178.3 | 313.2 | 584.5 | 560.8 | 310.6 | 357.9
398.3 | 179.3 | 314.7 | 575 | 548.9 | 309.7 | 358
399.3 | 180.3 | 316.1 | 567 | 550.7 | 309.2 | 358.8
400.3 | 181.3 | 317.2 | 561.2 | 555.2 | 308.9 | 359.2
401.3 | 182.3 | 318.3 | 576.5 | 579.8 | 309.6 | 362.8
402.3 | 183.3 | 319.7 | 572.2 | 581.1 | 309.9 | 362.8
403.3 | 184.3 | 321 | 582.6 | 587.6 | 310.3 | 363.7
404.3 | 185.3 | 322.3 | 598 | 601.4 | 310.7 | 365.6
405.3 | 186.3 | 323.5 | 615.6 | 614.7 | 311.2 | 367.3
406.3 | 187.3 | 324.9 | 631.4 | 627.2 | 311.8 | 370
407.3 | 188.3 | 326.5 | 653.5 | 643.2 | 313 | 372.5
408.3 | 189.3 | 328.3 | 672.1 | 648.5 | 314.5 | 374.8
409.3 | 190.3 | 329.9 | 683.4 | 647.3 | 315.3 | 374.8
410.3 | 191.3 | 331.6 | 700.4 | 660.3 | 316.6 | 378.2
411.3 | 192.3 | 333.2 | 712.5 | 664.4 | 317.9 | 380
412.3 | 193.3 | 334.9 | 721.3 | 681.6 | 319.3 | 381.7
413.3 | 194.3 | 336.7 | 735.3 | 683.6 | 321 | 385.5
414.3 | 195.3 | 338.3 | 735.9 | 664.4 | 322.2 | 385.7
415.3 | 196.3 | 339.9 | 734.7 | 655.3 | 323.4 | 385.4
416.3 | 197.3 | 341.2 | 734.4 | 648.9 | 324.5 | 385.1
417.3 | 198.3 | 342.7 | 737 | 647.6 | 326.1 | 385.9
418.3 | 199.3 | 344.2 | 733.1 | 635.8 | 327.7 | 386.1
419.3 | 200.3 | 345.7 | 723.5 | 626.7 | 329.1 | 385.6
420.3 | 201.3 | 347.1 | 722 | 621.5 | 330.5 | 385.8
421.3 | 202.3 | 348.5 | 728.6 | 624.8 | 332.5 | 387.2
422.3 | 203.3 | 349.9 | 736.9 | 639.4 | 335.2 | 389.5
423.3 | 204.3 | 351.6 | 744.4 | 644.6 | 336.7 | 392.2
424.3 | 205.3 | 353.2 | 752.3 | 648.9 | 338 | 395.6
425.3 | 206.3 | 355 | 755.6 | 642.1 | 340.2 | 396.4
426.3 | 207.3 | 356.7 | 743.6 | 633.3 | 342.1 | 395.8
427.3 | 208.3 | 358.3 | 742.3 | 638.6 | 343.7 | 398.2
428.3 | 209.3 | 359.7 | 744.6 | 634.1 | 344.4 | 397.9
429.3 | 210.3 | 361 | 752.8 | 638.9 | 345.4 | 399.9
430.3 | 211.3 | 361.9 | 751.6 | 619.7 | 346.4 | 399.2
431.3 | 212.3 | 362.9 | 744.1 | 613.2 | 346.8 | 398.2
432.3 | 213.3 | 363.8 | 737 | 619.6 | 348.6 | 397.8
433.3 | 214.3 | 364.9 | 736.7 | 616.2 | 351 | 399.5
434.3 | 215.3 | 366.3 | 735.8 | 610.1 | 353.5 | 400.4
435.3 | 216.3 | 367.7 | 728.8 | 602 | 354.3 | 399.5
436.3 | 217.3 | 369 | 728.2 | 600.4 | 357.1 | 400.8
437.3 | 218.3 | 370.4 | 731.1 | 604.8 | 360.2 | 401.8
438.3 | 219.3 | 372.2 | 727.5 | 614.3 | 364.7 | 402.2
439.3 | 220.3 | 374.3 | 729.6 | 610.6 | 367.8 | 401.6
440.3 | 221.3 | 376.3 | 732.5 | 609.1 | 369.9 | 403.9
441.3 | 222.3 | 378.1 | 720.9 | 599 | 371.3 | 403.4
442.3 | 223.3 | 379.6 | 720.7 | 587.4 | 372.7 | 402.7
443.3 | 224.3 | 380.9 | 708.1 | 584.9 | 375.5 | 403.5
444.3 | 225.3 | 382.5 | 702.1 | 578.6 | 378.2 | 403.9
445.3 | 226.3 | 384.1 | 702.1 | 575.9 | 380.6 | 404.9
446.3 | 227.3 | 385.8 | 688.3 | 572.8 | 382.7 | 404.7
447.3 | 228.3 | 387.7 | 680.2 | 567.7 | 385.1 | 404.6
448.3 | 229.3 | 389.5 | 665.1 | 565.1 | 386.1 | 403.7
449.3 | 230.3 | 391.1 | 654.2 | 549.1 | 386.3 | 402.2
450.3 | 231.3 | 392.2 | 646.7 | 538.8 | 385.9 | 401.5
451.3 | 232.3 | 393.2 | 631.2 | 545.9 | 388.2 | 401.4
452.3 | 233.3 | 394.6 | 625.1 | 550.7 | 392.1 | 402.9
453.3 | 234.3 | 396.4 | 622.4 | 547.6 | 395.1 | 403
454.3 | 235.3 | 398.4 | 624.2 | 554.1 | 398.9 | 403.8
455.3 | 236.3 | 400.6 | 616.9 | 542.3 | 402.1 | 402.5
456.3 | 237.3 | 402.7 | 615.7 | 537.4 | 404.9 | 402.3
457.3 | 238.3 | 404.7 | 616.8 | 538.5 | 407.7 | 402.6
458.3 | 239.3 | 406.6 | 606 | 537.5 | 409.6 | 401.9
459.3 | 240.3 | 408.5 | 611.1 | 548 | 412.5 | 404.7
460.3 | 241.3 | 410.6 | 615.1 | 560.3 | 416.3 | 406.8
461.3 | 242.3 | 413.2 | 628.2 | 578.5 | 420.6 | 408.3
462.3 | 243.3 | 416.3 | 637.5 | 584 | 424.6 | 409.9
463.3 | 244.3 | 419.6 | 643.7 | 601.4 | 429.3 | 411.6
464.3 | 245.3 | 423.1 | 654.1 | 604.8 | 433.9 | 413.2
465.3 | 246.3 | 426.7 | 656.6 | 607.1 | 438.2 | 413
466.3 | 247.3 | 430.4 | 652.3 | 605.9 | 440.4 | 413
467.3 | 248.3 | 433.7 | 661 | 620.2 | 443.4 | 414.7
468.3 | 249.3 | 436.8 | 668.7 | 619.8 | 446.4 | 416.4
469.3 | 250.3 | 440.1 | 680.3 | 620.3 | 450.1 | 419
470.3 | 251.3 | 443.5 | 690.7 | 614.8 | 454.9 | 419
471.3 | 252.3 | 447.3 | 683.3 | 602.5 | 458.4 | 418.2
472.3 | 253.3 | 451.1 | 679.8 | 590 | 461.4 | 416.8
473.3 | 254.3 | 454.8 | 673.7 | 587.7 | 465.4 | 417.3
474.3 | 255.3 | 458.3 | 666.5 | 579.2 | 469 | 417.5
475.3 | 256.3 | 461.1 | 657.8 | 575.6 | 472.6 | 416.5
476.3 | 257.3 | 464.2 | 653.9 | 569.9 | 475.9 | 416
477.3 | 258.3 | 467.4 | 646.2 | 567.6 | 478.4 | 415.7
478.3 | 259.3 | 470.2 | 650.2 | 574.1 | 482.2 | 417.4
479.3 | 260.3 | 473.4 | 652.3 | 554.9 | 485.7 | 415.5
480.3 | 261.3 | 476.2 | 648.2 | 545.2 | 488.4 | 414
481.3 | 262.3 | 478.5 | 643.3 | 548.2 | 492.1 | 414.4
482.3 | 263.3 | 480.9 | 650.7 | 553 | 497.4 | 415
483.3 | 264.3 | 484.2 | 642.2 | 559.3 | 502.3 | 415.8
484.3 | 265.3 | 487.7 | 639 | 546.8 | 506.7 | 414.5
485.3 | 266.3 | 490.2 | 632.7 | 550.3 | 510.9 | 414.2
486.3 | 267.3 | 492.3 | 624.7 | 534.7 | 514.9 | 412.8
487.3 | 268.3 | 494.3 | 614.2 | 519.1 | 517.2 | 412.1
488.3 | 269.3 | 496.1 | 599.3 | 502.1 | 519.5 | 410.5
489.3 | 270.3 | 497.4 | 591.2 | 502.6 | 521 | 410
490.3 | 271.3 | 498.7 | 589.7 | 505.6 | 524.2 | 409.8
491.3 | 272.3 | 500.4 | 601.5 | 517.5 | 527.4 | 410.3
492.3 | 273.3 | 502.7 | 598.2 | 515.1 | 532.6 | 410.8
493.3 | 274.3 | 505.4 | 598.4 | 516.7 | 537.1 | 410.2
494.3 | 275.3 | 508.2 | 607.1 | 533 | 543.4 | 411.9
495.3 | 276.3 | 512.4 | 619.2 | 542.1 | 549.1 | 413.7
496.3 | 277.3 | 516.7 | 622.3 | 543.5 | 554.5 | 413.5
497.3 | 278.3 | 520.4 | 622.7 | 537 | 560.1 | 414.3
498.3 | 279.3 | 523.5 | 617.7 | 525.2 | 565.7 | 412.9
499.3 | 280.3 | 526.4 | 606.2 | 523 | 569.6 | 411.8
500.3 | 281.3 | 528.5 | 610.2 | 542.1 | 574.3 | 413.1
501.3 | 282.3 | 531.2 | 626.4 | 561.6 | 579.3 | 415.7
502.3 | 283.3 | 534.7 | 632.6 | 584.7 | 585.1 | 418.8
503.3 | 284.3 | 539.1 | 644.2 | 595.4 | 591.1 | 420.4
504.3 | 285.3 | 543.8 | 652.2 | 589.6 | 596.6 | 420.9
505.3 | 286.3 | 548.3 | 654.7 | 577.9 | 600.2 | 420.1
506.3 | 287.3 | 552.1 | 660.3 | 579.1 | 604.1 | 420.8
507.3 | 288.3 | 555.6 | 653.5 | 568.9 | 608.7 | 420.1
508.3 | 289.3 | 558.8 | 647.1 | 556.5 | 612 | 419.8
509.3 | 290.3 | 561.8 | 640.7 | 547.7 | 614.8 | 419.7
510.3 | 291.3 | 564.3 | 643.7 | 544.5 | 617.2 | 420.3
511.3 | 292.3 | 566.7 | 644.7 | 549.6 | 620.1 | 420.6
512.3 | 293.3 | 569.4 | 646.6 | 549.7 | 622.9 | 420.5
513.3 | 294.3 | 572.1 | 649.7 | 543.3 | 624.5 | 421.5
514.3 | 295.3 | 575.5 | 647.6 | 542.9 | 626.4 | 421.3
515.3 | 296.3 | 578.4 | 636.5 | 535.1 | 628.4 | 420.8
516.3 | 297.3 | 580.9 | 627.8 | 530.3 | 629.9 | 419.6
517.3 | 298.3 | 583.1 | 620.2 | 542.5 | 633.3 | 420.8
518.3 | 299.3 | 586 | 629.5 | 566 | 637.6 | 422.8
519.3 | 300.3 | 590.3 | 647.5 | 577.7 | 642.7 | 426.3
520.3 | 301.3 | 594.7 | 641.2 | 563.3 | 647.9 | 425.3
521.3 | 302.3 | 598.9 | 632.6 | 547.3 | 652.2 | 423.7
522.3 | 303.3 | 602.7 | 626 | 539.6 | 656.3 | 421.9
523.3 | 304.3 | 606 | 633.6 | 556.9 | 662.2 | 423.9
524.3 | 305.3 | 609.8 | 645.5 | 562.8 | 667.2 | 426.3
525.3 | 306.3 | 613.3 | 650.1 | 561.8 | 672 | 427.1
526.3 | 307.3 | 616.8 | 649.2 | 558.6 | 676.4 | 427.4
527.3 | 308.3 | 620.5 | 643.7 | 547.8 | 680 | 426.3
528.3 | 309.3 | 624.4 | 639.2 | 535.6 | 682.1 | 425.2
529.3 | 310.3 | 627.9 | 635.9 | 514.9 | 682.8 | 424.3
530.3 | 311.3 | 630.7 | 632.4 | 503.9 | 683.8 | 423
531.3 | 312.3 | 633.1 | 630.3 | 508.9 | 686.1 | 422.9
532.3 | 313.3 | 635.9 | 623.9 | 502.4 | 687.7 | 422
533.3 | 314.3 | 638.4 | 621.7 | 505.4 | 690.1 | 422
534.3 | 315.3 | 640.8 | 625.2 | 508 | 693.5 | 421.6
535.3 | 316.3 | 643.1 | 629.1 | 501.7 | 696.6 | 420.7
536.3 | 317.3 | 645.2 | 639.7 | 504.3 | 700.3 | 421.8
537.3 | 318.3 | 647.3 | 631.5 | 489.7 | 703.5 | 420
538.3 | 319.3 | 649.6 | 628.1 | 486 | 705.8 | 419.5
539.3 | 320.3 | 651.8 | 617.7 | 480.5 | 707.9 | 419.1
540.3 | 321.3 | 654.1 | 604.8 | 465.7 | 709.7 | 417.6
541.3 | 322.3 | 656.5 | 599.1 | 460.9 | 711.6 | 417.2
542.3 | 323.3 | 658.6 | 594.5 | 466.4 | 714.7 | 417.6
543.3 | 324.3 | 661.1 | 588.9 | 473.9 | 717.9 | 417.6
544.3 | 325.3 | 663.6 | 603 | 489.9 | 722.6 | 420
545.3 | 326.3 | 666.7 | 619.8 | 510.9 | 727.2 | 422.3
546.3 | 327.3 | 670.1 | 633.2 | 526.5 | 730.9 | 424.1
547.3 | 328.3 | 673.4 | 645.9 | 547.9 | 735.6 | 426.6
548.3 | 329.3 | 677 | 660.5 | 561.4 | 739.1 | 430
549.3 | 330.3 | 680.4 | 666.3 | 556.9 | 742.8 | 429.1
550.3 | 331.3 | 683.8 | 672.9 | 555.7 | 746.6 | 429.7
551.3 | 332.3 | 687.2 | 687.8 | 568.6 | 750.5 | 433.6
552.3 | 333.3 | 690.3 | 696.4 | 569.8 | 754.7 | 433.7
553.3 | 334.3 | 693.5 | 699.1 | 564.7 | 757.2 | 433
554.3 | 335.3 | 696.7 | 694.8 | 550.6 | 758.9 | 432.6
555.3 | 336.3 | 699.9 | 691 | 543.5 | 759 | 431.4
556.3 | 337.3 | 702.7 | 703.5 | 545.9 | 759.2 | 431.7
557.3 | 338.3 | 705.7 | 708.6 | 542.4 | 758.5 | 432.3
558.3 | 339.3 | 708.2 | 712.7 | 558.5 | 761.3 | 433.1
559.3 | 340.3 | 710.5 | 727.7 | 574 | 762 | 436
560.3 | 341.3 | 712.8 | 737 | 582 | 765.8 | 438.1
561.3 | 342.3 | 715.4 | 741.7 | 586.6 | 769 | 440.5
562.3 | 343.3 | 718 | 747.6 | 600.1 | 773.1 | 442.6
563.3 | 344.3 | 721 | 758.3 | 603.1 | 774.6 | 444
564.3 | 345.3 | 724.1 | 763.6 | 593.9 | 775.5 | 443.6
565.3 | 346.3 | 727.1 | 758.8 | 578.8 | 775.8 | 442.1
566.3 | 347.3 | 730.2 | 746.2 | 561.4 | 774.8 | 441.1
567.3 | 348.3 | 733 | 740.5 | 546.5 | 773 | 440.4
568.3 | 349.3 | 735.5 | 738.1 | 545.4 | 771.2 | 441.4
569.3 | 350.3 | 737.8 | 741.9 | 536.2 | 769.4 | 441.2
570.3 | 351.3 | 739.8 | 735.7 | 523.1 | 768.3 | 439.8
571.3 | 352.3 | 741.4 | 737.1 | 506.2 | 766.5 | 438
572.3 | 353.3 | 742.7 | 732.7 | 494.4 | 765.5 | 437.1
573.3 | 354.3 | 744.3 | 724.5 | 486.2 | 763.1 | 436.6
574.3 | 355.3 | 746.2 | 708.6 | 470 | 762 | 434.8
575.3 | 356.3 | 747.5 | 697.2 | 459.3 | 760 | 432.8
576.3 | 357.3 | 748.4 | 695.4 | 453.7 | 758.1 | 432
577.3 | 358.3 | 749.3 | 692.4 | 450.3 | 756.3 | 431.3
578.3 | 359.3 | 750.1 | 691.1 | 454 | 753.7 | 431.1
579.3 | 360.3 | 751.2 | 684.5 | 449.8 | 752.7 | 430.3
580.3 | 361.3 | 752.3 | 675.9 | 443.2 | 750.9 | 429.3
581.3 | 362.3 | 753.2 | 671 | 438.7 | 751.3 | 428.8
582.3 | 363.3 | 754.7 | 659.3 | 429.2 | 749.7 | 427.5
583.3 | 364.3 | 755.6 | 646.8 | 419.7 | 748.9 | 426.4
584.3 | 365.3 | 756.2 | 637.8 | 413.2 | 747.1 | 426.2
585.3 | 366.3 | 756.9 | 630.1 | 415.9 | 745.3 | 426.4
586.3 | 367.3 | 758.1 | 622.1 | 409.2 | 742.2 | 426.6
587.3 | 368.3 | 759 | 617.4 | 406 | 739.9 | 425.9
588.3 | 369.3 | 759.6 | 614.6 | 403.8 | 738.7 | 425.4
589.3 | 370.3 | 760.2 | 617.5 | 404.5 | 735.5 | 424.7
590.3 | 371.3 | 760.8 | 615.8 | 400.6 | 735.1 | 424
591.3 | 372.3 | 761.4 | 620.4 | 406.8 | 732.7 | 423.1
592.3 | 373.3 | 761.9 | 625.3 | 410.4 | 730.2 | 422.6
593.3 | 374.3 | 762.6 | 622.8 | 416.1 | 727.9 | 422.4
594.3 | 375.3 | 763.5 | 618 | 413.3 | 727.2 | 422
595.3 | 376.3 | 764.5 | 615.2 | 414.8 | 727.7 | 421.4
596.3 | 377.3 | 765.7 | 609.5 | 412.7 | 723.7 | 420.8
597.3 | 378.3 | 766.4 | 601.4 | 411.6 | 722.9 | 420.5
598.3 | 379.3 | 767.3 | 596.9 | 413.6 | 722.5 | 420.5
599.3 | 380.3 | 768.3 | 593.9 | 411.7 | 720.9 | 419.3
600.3 | 381.3 | 768.7 | 597.5 | 419.7 | 718.8 | 419.2
601.3 | 382.3 | 769.3 | 607.2 | 429.9 | 717.8 | 420.2
602.3 | 383.3 | 770.4 | 615.2 | 440.9 | 715.6 | 420.8
603.3 | 384.3 | 771.3 | 621.9 | 461.9 | 719.7 | 422.5
604.3 | 385.3 | 772.7 | 625.3 | 472.7 | 723.3 | 423.1
605.3 | 386.3 | 773.8 | 626.8 | 484.4 | 722 | 423.8
606.3 | 387.3 | 774.8 | 646.2 | 507.2 | 723.9 | 427.5
607.3 | 388.3 | 776.2 | 656.5 | 522.9 | 731.8 | 428.8
608.3 | 389.3 | 778.5 | 663 | 526 | 731.1 | 429.5
609.3 | 390.3 | 780.5 | 664.1 | 528 | 728.3 | 429.6
610.3 | 391.3 | 781.8 | 670.6 | 539.8 | 729 | 430.5
611.3 | 392.3 | 783 | 674.6 | 541.3 | 725.3 | 430.4
612.3 | 393.3 | 783.3 | 681.6 | 554.2 | 727.7 | 430.5
613.3 | 394.3 | 784.4 | 681.8 | 547.1 | 728.6 | 430.8
614.3 | 395.3 | 785.3 | 684.2 | 535.3 | 727.4 | 429.6
615.3 | 396.3 | 785.6 | 677.5 | 517.2 | 724.9 | 428.1
616.3 | 397.3 | 785.6 | 667.9 | 502.1 | 724.2 | 427.2
617.3 | 398.3 | 785.7 | 667.1 | 509.4 | 728.9 | 427.9
618.3 | 399.3 | 787 | 674.6 | 516.2 | 734.1 | 428.6
619.3 | 400.3 | 789.1 | 677.2 | 508.9 | 736.8 | 428.5
620.3 | 401.3 | 790.4 | 684.3 | 516.6 | 735.2 | 429.2
621.3 | 402.3 | 791.1 | 685.1 | 510.8 | 734.2 | 428.3
622.3 | 403.3 | 791.2 | 679.8 | 503.1 | 731.6 | 427.8
623.3 | 404.3 | 790.7 | 675.9 | 496.2 | 728.5 | 426.9
624.3 | 405.3 | 790.2 | 672.1 | 489.3 | 726 | 427.4
625.3 | 406.3 | 789.5 | 658.3 | 473 | 723.9 | 425.6
626.3 | 407.3 | 788.3 | 644.9 | 461.5 | 722.2 | 424.8
627.3 | 408.3 | 787.2 | 643.5 | 461.8 | 718.1 | 424.8
628.3 | 409.3 | 786.3 | 649.2 | 466.6 | 714.3 | 425.4
629.3 | 410.3 | 785.6 | 656.1 | 481 | 716.3 | 427.7
630.3 | 411.3 | 785.6 | 659.1 | 479.3 | 716.8 | 427.9
631.3 | 412.3 | 785.6 | 665 | 481.4 | 716.1 | 428
632.3 | 413.3 | 785.2 | 671.9 | 486.8 | 713.8 | 428.3
633.3 | 414.3 | 784.7 | 680.5 | 496.5 | 712.4 | 428.6
634.3 | 415.3 | 784.4 | 685.6 | 496.3 | 710.3 | 428.9
635.3 | 416.3 | 784.4 | 691.2 | 501.5 | 709 | 429.5
636.3 | 417.3 | 784.5 | 693.1 | 502.7 | 707.8 | 430.4
637.3 | 418.3 | 785.1 | 698.7 | 508.2 | 712.8 | 431.1
638.3 | 419.3 | 785.5 | 703.4 | 510.9 | 716.3 | 430.7
639.3 | 420.3 | 785.8 | 710.3 | 527.3 | 720.1 | 433.4
640.3 | 421.3 | 786.8 | 719.7 | 544.1 | 722.1 | 438.8
641.3 | 422.3 | 787.9 | 725.1 | 552.6 | 722.6 | 440.3
642.3 | 423.3 | 788.5 | 723.1 | 550.8 | 720.9 | 440
643.3 | 424.3 | 788.6 | 728.8 | 560.9 | 725.4 | 442
644.3 | 425.3 | 789.5 | 732 | 567.3 | 728.2 | 443.9
645.3 | 426.3 | 790.6 | 737.1 | 568.4 | 726.9 | 444.3
646.3 | 427.3 | 791.3 | 737.8 | 567.1 | 727.8 | 444.1
647.3 | 428.3 | 791.7 | 734 | 560.1 | 724.2 | 444.4
648.3 | 429.3 | 791.5 | 733.3 | 547.1 | 722.1 | 445.1
649.3 | 430.3 | 791.5 | 727 | 542.7 | 721 | 445.4
650.3 | 431.3 | 791.2 | 727.6 | 535.5 | 720.9 | 445.9
651.3 | 432.3 | 791 | 728.7 | 540.5 | 720.4 | 447
652.3 | 433.3 | 791.1 | 729.3 | 537.5 | 719.7 | 446.8
653.3 | 434.3 | 791.8 | 731 | 540.9 | 721.3 | 447.9
654.3 | 435.3 | 792.1 | 730.9 | 530.4 | 723.1 | 448.4
655.3 | 436.3 | 791.8 | 729.6 | 522.5 | 722.4 | 447.8
656.3 | 437.3 | 791.3 | 729.8 | 508.8 | 721.2 | 447.9
657.3 | 438.3 | 791 | 732.2 | 505.2 | 721 | 449.5
658.3 | 439.3 | 790.3 | 727.3 | 498.8 | 716.9 | 449.5
659.3 | 440.3 | 789.6 | 726.3 | 492.3 | 715.7 | 449.3
660.3 | 441.3 | 788.4 | 718.9 | 485.9 | 713.1 | 449
661.3 | 442.3 | 787.7 | 723.8 | 488.1 | 713.2 | 450.8
662.3 | 443.3 | 786.9 | 724.3 | 488.3 | 711.6 | 451.3
663.3 | 444.3 | 786.2 | 723.4 | 478.6 | 711.1 | 450.7
664.3 | 445.3 | 785.6 | 722.3 | 478.1 | 709.5 | 451.7
665.3 | 446.3 | 785.1 | 724.6 | 483.6 | 707.7 | 452.2
666.3 | 447.3 | 785.3 | 730.3 | 509.2 | 712 | 455
667.3 | 448.3 | 786.3 | 737.6 | 522.4 | 714.9 | 456.6
668.3 | 449.3 | 787.1 | 742.9 | 554.6 | 720.7 | 459.4
669.3 | 450.3 | 788.2 | 748.7 | 560.1 | 726.2 | 460.5
670.3 | 451.3 | 789.3 | 753.9 | 566.4 | 725.3 | 462.5
671.3 | 452.3 | 789.9 | 755.4 | 553.1 | 725.1 | 462.2
672.3 | 453.3 | 790.4 | 753.8 | 549.8 | 724 | 463
673.3 | 454.3 | 790.9 | 757.4 | 560.4 | 724.6 | 465.4
674.3 | 455.3 | 790.9 | 760.7 | 559 | 723.9 | 466.2
675.3 | 456.3 | 790.7 | 762.4 | 549.8 | 721.6 | 466.2
676.3 | 457.3 | 790.1 | 759.2 | 554.5 | 721.4 | 467.1
677.3 | 458.3 | 790.3 | 760.8 | 557.2 | 725.2 | 470.1
678.3 | 459.3 | 790.9 | 761.8 | 553.1 | 724 | 470.1
679.3 | 460.3 | 790.9 | 758.5 | 543.4 | 721.6 | 470.7
680.3 | 461.3 | 790.2 | 756.1 | 536.8 | 720.3 | 471.8
681.3 | 462.3 | 789.5 | 757.3 | 526.5 | 719.1 | 473.3
682.3 | 463.3 | 788.8 | 753.1 | 522.2 | 718.3 | 474.1
683.3 | 464.3 | 788 | 750.4 | 522.3 | 715.8 | 476.1
684.3 | 465.3 | 787.2 | 750.7 | 520.4 | 714.7 | 478.1
685.3 | 466.3 | 786.6 | 749 | 505.9 | 714.3 | 478.8
686.3 | 467.3 | 785.4 | 737.4 | 490.3 | 713.2 | 479.5
687.3 | 468.3 | 783.6 | 731.1 | 489.6 | 709.7 | 480.2
688.3 | 469.3 | 781 | 726.9 | 480.1 | 704.6 | 481.1
689.3 | 470.3 | 778.1 | 723.2 | 468 | 702.6 | 482.7
690.3 | 471.3 | 775.9 | 705.4 | 456.1 | 700.3 | 484.7
691.3 | 472.3 | 773.4 | 674.8 | 440.8 | 697.8 | 484.7
692.3 | 473.3 | 770.6 | 665.3 | 431.9 | 694.5 | 485
693.3 | 474.3 | 768 | 661.4 | 425.7 | 689.3 | 485
694.3 | 475.3 | 765.7 | 664.2 | 421.3 | 686.6 | 486.6
695.3 | 476.3 | 763.7 | 661.2 | 412.5 | 682.8 | 488.2
696.3 | 477.3 | 761.3 | 648.3 | 410.6 | 678.2 | 487.4
697.3 | 478.3 | 758.5 | 651.1 | 403.6 | 674.5 | 487.1
698.3 | 479.3 | 755.8 | 649.3 | 402.9 | 671.8 | 487.7
699.3 | 480.3 | 753.6 | 647.5 | 399.6 | 669.7 | 488.3
700.3 | 481.3 | 751.6 | 632.9 | 393.3 | 668.3 | 488.4
701.3 | 482.3 | 749.9 | 630.6 | 392.7 | 666.7 | 489.3
702.3 | 483.3 | 748.9 | 636.4 | 420.6 | 666.6 | 492.6
703.3 | 484.3 | 748.6 | 646.5 | 451.9 | 668.9 | 496.4
704.3 | 485.3 | 748.2 | 647.1 | 454.9 | 668.6 | 498.6
705.3 | 486.3 | 746.9 | 635.4 | 446.6 | 666.3 | 497.3
706.3 | 487.3 | 746.4 | 646.2 | 443.6 | 669 | 498.4
707.3 | 488.3 | 746.2 | 638.1 | 433.4 | 667.8 | 498.2
708.3 | 489.3 | 744.8 | 628.5 | 428 | 664.9 | 497.4
709.3 | 490.3 | 743.7 | 633.9 | 425.7 | 662.7 | 497.4
710.3 | 491.3 | 742.8 | 629.7 | 425.9 | 660.8 | 497.1
711.3 | 492.3 | 742.3 | 636.9 | 443.4 | 659.2 | 498
712.3 | 493.3 | 741.2 | 633.6 | 440.8 | 657.7 | 497.7
713.3 | 494.3 | 739.4 | 633.5 | 444.8 | 654.9 | 497.1
714.3 | 495.3 | 737.5 | 627.8 | 438 | 651.8 | 497
715.3 | 496.3 | 735.2 | 626 | 441.1 | 647.6 | 497.8
716.3 | 497.3 | 733.2 | 627.2 | 456.5 | 645.1 | 499.3
717.3 | 498.3 | 731.2 | 623.1 | 450 | 640.8 | 499
718.3 | 499.3 | 729.5 | 614.2 | 448.7 | 638.7 | 499.3
719.3 | 500.3 | 727.3 | 595.8 | 438.7 | 636.1 | 498.5
720.3 | 501.3 | 725.1 | 581.8 | 437.4 | 632.9 | 498
721.3 | 502.3 | 724 | 578.8 | 436.4 | 632.1 | 498.5
722.3 | 503.3 | 722.9 | 580.9 | 435.2 | 630.5 | 499.1
723.3 | 504.3 | 722 | 578.3 | 436.3 | 629.6 | 499.1
724.3 | 505.3 | 721.8 | 585.3 | 446.5 | 629.7 | 500.1
725.3 | 506.3 | 721.7 | 591.3 | 465.5 | 629.7 | 502.6
726.3 | 507.3 | 721.5 | 597.8 | 471.8 | 630.1 | 503.3
727.3 | 508.3 | 722 | 602.5 | 466.9 | 632.7 | 503.1
728.3 | 509.3 | 722.3 | 611.1 | 461.4 | 633.8 | 503.3
729.3 | 510.3 | 721.8 | 605.4 | 457.5 | 631.5 | 503.2
730.3 | 511.3 | 721.4 | 610.3 | 477.3 | 632.1 | 505.1
731.3 | 512.3 | 721.2 | 613.7 | 493 | 631.5 | 507.3
732.3 | 513.3 | 720.7 | 613.2 | 513.2 | 631.7 | 510.7
733.3 | 514.3 | 720.8 | 620.1 | 534 | 635.2 | 512.1
734.3 | 515.3 | 721.7 | 624.4 | 543.8 | 636.4 | 512.2
735.3 | 516.3 | 722.6 | 628.2 | 552.1 | 638.3 | 513.5
736.3 | 517.3 | 724.3 | 635.7 | 563.7 | 644.4 | 514.5
737.3 | 518.3 | 726.1 | 642.8 | 564.3 | 645.4 | 517.1
738.3 | 519.3 | 727 | 645.5 | 553.2 | 644.4 | 515.7
739.3 | 520.3 | 726.4 | 640.7 | 536.6 | 643.6 | 514.9
740.3 | 521.3 | 726 | 632.9 | 535.6 | 642.8 | 516.3
741.3 | 522.3 | 725.8 | 633.1 | 535.7 | 643.5 | 519.1
742.3 | 523.3 | 725 | 628.9 | 529.8 | 641.4 | 520
743.3 | 524.3 | 723.7 | 629.6 | 519 | 640.5 | 520.5
744.3 | 525.3 | 722.5 | 628.2 | 514.4 | 639.2 | 520.3
745.3 | 526.3 | 723.3 | 638 | 515.8 | 644 | 522.2
746.3 | 527.3 | 726.9 | 658.8 | 531.1 | 653.7 | 526.4
747.3 | 528.3 | 730.6 | 665.6 | 546.5 | 655.9 | 527.8
748.3 | 529.3 | 732.3 | 667.3 | 552.4 | 655.5 | 528.9
749.3 | 530.3 | 733.3 | 674.7 | 566.7 | 658.7 | 530.3
750.3 | 531.3 | 734.3 | 674.2 | 575.1 | 662 | 530.9
751.3 | 532.3 | 734.5 | 669.7 | 574.2 | 662.1 | 533.4
752.3 | 533.3 | 734.8 | 671.8 | 598 | 667.1 | 538.2
753.3 | 534.3 | 736.2 | 675.5 | 600.8 | 670.8 | 541.1
754.3 | 535.3 | 736.1 | 670.4 | 590.5 | 667.8 | 539.8
755.3 | 536.3 | 735.4 | 673.6 | 596.8 | 669.2 | 542.4
756.3 | 537.3 | 736.1 | 686.2 | 606 | 671.2 | 544.1
757.3 | 538.3 | 737.3 | 688.8 | 617 | 674.9 | 545.8
758.3 | 539.3 | 739.3 | 699.7 | 621.6 | 678.1 | 546.2
759.3 | 540.3 | 741.1 | 698.3 | 606.8 | 678.9 | 545.8
760.3 | 541.3 | 741.6 | 690.5 | 587.4 | 677 | 544.8
761.3 | 542.3 | 739.9 | 674.7 | 565.4 | 673.6 | 543.6
762.3 | 543.3 | 737 | 651.3 | 545.5 | 669.5 | 542.4
763.3 | 544.3 | 734.5 | 647.9 | 532.3 | 665.8 | 541.9
764.3 | 545.3 | 731.9 | 642 | 522.9 | 661.4 | 541.3
765.3 | 546.3 | 729.4 | 645.4 | 516.2 | 657.6 | 541.4
766.3 | 547.3 | 726.8 | 638.5 | 508.9 | 654.1 | 540.2
767.3 | 548.3 | 725.1 | 637 | 512.5 | 652.8 | 540.4
768.3 | 549.3 | 723.3 | 630.7 | 507 | 649.5 | 540.5
769.3 | 550.3 | 720.6 | 625.1 | 494 | 645 | 539.2
770.3 | 551.3 | 717 | 618.8 | 483.3 | 641.3 | 539.2
771.3 | 552.3 | 714 | 614.6 | 482.7 | 637.5 | 539.7
772.3 | 553.3 | 712.3 | 608.3 | 478.6 | 635.7 | 538.8
773.3 | 554.3 | 711.4 | 610.7 | 489.7 | 634.9 | 539.4
774.3 | 555.3 | 711.8 | 614.3 | 505 | 637.3 | 540.7
775.3 | 556.3 | 712.4 | 617 | 515.3 | 637.4 | 542.6
776.3 | 557.3 | 711.6 | 613.4 | 507.2 | 633.9 | 541.2
777.3 | 558.3 | 709.9 | 611.5 | 495.5 | 631.2 | 539.4
778.3 | 559.3 | 708.1 | 609.1 | 502 | 630.1 | 540.6
779.3 | 560.3 | 707.1 | 613.2 | 506.8 | 630.6 | 541.5
780.3 | 561.3 | 705.3 | 609.8 | 499.7 | 629.1 | 539.7
781.3 | 562.3 | 703.2 | 608 | 499.7 | 628 | 539.1
782.3 | 563.3 | 701.6 | 608.5 | 503 | 626.3 | 538.6
783.3 | 564.3 | 701.6 | 612.4 | 514.7 | 627.7 | 540.5
784.3 | 565.3 | 701.5 | 610.2 | 525.1 | 626.8 | 540.9
785.3 | 566.3 | 702.2 | 611.9 | 536.7 | 630.4 | 542.5
786.3 | 567.3 | 703.5 | 611.8 | 529.1 | 632.7 | 541.9
787.3 | 568.3 | 703.3 | 612.5 | 522.2 | 632.1 | 539.9
788.3 | 569.3 | 701.8 | 606.7 | 520.9 | 629.1 | 539.2
789.3 | 570.3 | 698.9 | 597.4 | 512.5 | 626 | 537.7
790.3 | 571.3 | 696.1 | 591.2 | 507 | 624.3 | 537.5
791.3 | 572.3 | 694.4 | 589.1 | 503.1 | 623.8 | 537.5
792.3 | 573.3 | 693 | 586.3 | 497.3 | 625.1 | 536.7
793.3 | 574.3 | 691.5 | 581.2 | 499.6 | 623.1 | 536.7
794.3 | 575.3 | 690.8 | 583.3 | 503.9 | 622.2 | 536.7
795.3 | 576.3 | 692.3 | 598 | 525.1 | 627.1 | 538.3
796.3 | 577.3 | 696 | 612.2 | 534.1 | 632.4 | 539.1
797.3 | 578.3 | 698.6 | 616.1 | 535.2 | 633.8 | 538.5
798.3 | 579.3 | 701.7 | 629.1 | 545.7 | 636.3 | 538.4
799.3 | 580.3 | 706 | 638.6 | 566.6 | 645.8 | 540.8
800.3 | 581.3 | 710.4 | 637.5 | 580.1 | 654.3 | 541
801.3 | 582.3 | 715.3 | 640.8 | 577.8 | 660.8 | 540.4
802.3 | 583.3 | 718.3 | 638.5 | 582.2 | 664 | 540.3
803.3 | 584.3 | 719.1 | 631.4 | 584.9 | 664.1 | 540.4
804.3 | 585.3 | 720.8 | 632.6 | 588.5 | 666 | 540.3
805.3 | 586.3 | 722.2 | 628.4 | 595.3 | 667.1 | 541
806.3 | 587.3 | 723.2 | 632.2 | 601.9 | 668.9 | 541.5
807.3 | 588.3 | 723.9 | 637.3 | 602.1 | 669.5 | 541.3
808.3 | 589.3 | 726.8 | 649 | 604.6 | 674.9 | 542.6
809.3 | 590.3 | 730.1 | 653.2 | 601.1 | 678 | 542.3
810.3 | 591.3 | 731.9 | 650.5 | 596.4 | 679 | 541.8
811.3 | 592.3 | 730.7 | 634.3 | 582.5 | 674.6 | 539.9
812.3 | 593.3 | 727.4 | 621 | 567.3 | 671.2 | 538.9
813.3 | 594.3 | 724.7 | 610.8 | 561.8 | 668.4 | 538.5
814.3 | 595.3 | 724.1 | 611.7 | 575.5 | 668.9 | 540.3
815.3 | 596.3 | 723.5 | 608.6 | 566.1 | 667.8 | 539.4
816.3 | 597.3 | 723.1 | 609.8 | 560.4 | 666.8 | 539
817.3 | 598.3 | 724.2 | 614.9 | 554.1 | 668.5 | 539
818.3 | 599.3 | 725.6 | 615.6 | 548.9 | 670 | 538.9
819.3 | 600.3 | 727.8 | 621.3 | 552.1 | 672.1 | 538.5
820.3 | 601.3 | 730.8 | 630.6 | 558.7 | 675.9 | 539.1
821.3 | 602.3 | 734.1 | 639.7 | 571.7 | 680.2 | 540.3
822.3 | 603.3 | 737 | 640.1 | 572.6 | 681.2 | 541.8
823.3 | 604.3 | 737.7 | 635.6 | 573.6 | 679.7 | 540.4
824.3 | 605.3 | 738.3 | 632.4 | 567.2 | 681.3 | 540.1
825.3 | 606.3 | 738.9 | 632 | 565.5 | 681.7 | 540.5
826.3 | 607.3 | 740.1 | 643.6 | 585.9 | 687.4 | 543.9
827.3 | 608.3 | 742.7 | 654.2 | 604.7 | 692.5 | 546.6
828.3 | 609.3 | 746.2 | 670.4 | 628.3 | 698.7 | 548.6
829.3 | 610.3 | 749.9 | 678.7 | 630.6 | 706.7 | 549.7
830.3 | 611.3 | 751.8 | 676.1 | 631 | 706.1 | 549.3
831.3 | 612.3 | 752.7 | 674.8 | 633.4 | 705.8 | 550.2
832.3 | 613.3 | 752.3 | 669.6 | 618.4 | 702.9 | 548.9
833.3 | 614.3 | 752.3 | 671.1 | 610.4 | 702.4 | 548
834.3 | 615.3 | 752.4 | 669.7 | 611.1 | 702.9 | 549.8
835.3 | 616.3 | 752.2 | 668.4 | 601.4 | 702.7 | 549.3
836.3 | 617.3 | 752.9 | 674.7 | 595.1 | 706.1 | 549.3
837.3 | 618.3 | 754.4 | 677.5 | 596.7 | 710.3 | 550.2
838.3 | 619.3 | 754.9 | 671.7 | 599.8 | 711.5 | 550.8
839.3 | 620.3 | 754.5 | 670 | 603.1 | 710.6 | 550.8
840.3 | 621.3 | 754.6 | 669.5 | 617.9 | 711.8 | 552.7
841.3 | 622.3 | 757.1 | 674.5 | 627 | 716.7 | 555.2
842.3 | 623.3 | 759.2 | 680.4 | 620.8 | 718.5 | 555.5
843.3 | 624.3 | 759.1 | 675.8 | 602.6 | 716.2 | 554.2
844.3 | 625.3 | 755.4 | 661.6 | 581.9 | 710.9 | 553.1
845.3 | 626.3 | 751.3 | 649.6 | 568.8 | 704.9 | 551.7
846.3 | 627.3 | 747.6 | 639.5 | 551.5 | 698.8 | 550.3
847.3 | 628.3 | 745.6 | 635.7 | 543.1 | 696.9 | 550.4
848.3 | 629.3 | 745.4 | 643.6 | 560 | 694.1 | 551.6
849.3 | 630.3 | 746.4 | 657.8 | 579.7 | 695.2 | 552.5
850.3 | 631.3 | 751.5 | 676 | 589 | 700.5 | 554.4
851.3 | 632.3 | 753.4 | 680.6 | 599.6 | 701.9 | 555.6
852.3 | 633.3 | 756.4 | 690.3 | 612 | 708.4 | 556.7
853.3 | 634.3 | 759.2 | 703.3 | 622.9 | 713 | 557.3
854.3 | 635.3 | 762.9 | 717.8 | 623.8 | 716.2 | 557.9
855.3 | 636.3 | 764.4 | 724.6 | 634.6 | 717 | 558
856.3 | 637.3 | 765.9 | 727.1 | 664.6 | 716.7 | 560.5
857.3 | 638.3 | 767 | 725.1 | 667.1 | 716.6 | 561.9
858.3 | 639.3 | 767.1 | 720.4 | 657.6 | 716.2 | 560.4
859.3 | 640.3 | 767.9 | 719.5 | 662.8 | 717.4 | 564.7
860.3 | 641.3 | 765.8 | 713.8 | 656.9 | 714.8 | 565.2
861.3 | 642.3 | 764.4 | 713.8 | 659.3 | 715.6 | 564.7
862.3 | 643.3 | 765.4 | 719.4 | 674.4 | 718.1 | 567.5
863.3 | 644.3 | 765.7 | 722.9 | 667.2 | 717.6 | 567.6
864.3 | 645.3 | 763.9 | 718 | 644.8 | 714.5 | 565.8
865.3 | 646.3 | 763 | 715.7 | 627.4 | 713.2 | 565
866.3 | 647.3 | 763.2 | 719.2 | 622.3 | 712.6 | 564.8
867.3 | 648.3 | 763 | 722.2 | 624.7 | 713.5 | 566.3
868.3 | 649.3 | 765.9 | 728.6 | 630.5 | 718.1 | 568.3
869.3 | 650.3 | 766.6 | 726.4 | 635.1 | 721 | 569.4
870.3 | 651.3 | 765.8 | 725.9 | 632.1 | 721.8 | 571.4
871.3 | 652.3 | 762.7 | 712.6 | 634.9 | 720.9 | 570.3
872.3 | 653.3 | 759 | 699.9 | 621 | 718.3 | 570.6
873.3 | 654.3 | 755.7 | 693 | 608.8 | 715.2 | 570
874.3 | 655.3 | 754.8 | 689.9 | 598 | 713.4 | 568.9
875.3 | 656.3 | 755.1 | 698 | 600.6 | 711 | 568.8
876.3 | 657.3 | 752.1 | 696.2 | 599.4 | 705.5 | 567.1
877.3 | 658.3 | 751.6 | 697.7 | 602.9 | 703.8 | 569.3
878.3 | 659.3 | 754.6 | 711.1 | 622.5 | 707.6 | 571.5
879.3 | 660.3 | 756.7 | 709.1 | 621.5 | 712.5 | 573.6
880.3 | 661.3 | 757.4 | 713.7 | 623.3 | 712.6 | 573.8
881.3 | 662.3 | 754 | 700.3 | 601.3 | 708.7 | 571.8
882.3 | 663.3 | 750.1 | 695.5 | 591.4 | 703.7 | 570.8
883.3 | 664.3 | 746.9 | 694.4 | 592.9 | 698 | 571.6
884.3 | 665.3 | 742.9 | 683.8 | 588.5 | 693.7 | 570.6
885.3 | 666.3 | 742.7 | 685.3 | 599.7 | 693 | 571.3
886.3 | 667.3 | 741.2 | 679.2 | 604.8 | 692.1 | 571.4
887.3 | 668.3 | 738.1 | 672.3 | 589.7 | 688.6 | 570.9
888.3 | 669.3 | 734.9 | 666.9 | 577.8 | 684 | 570.2
889.3 | 670.3 | 730.8 | 660.9 | 569 | 679.8 | 568.8
890.3 | 671.3 | 726.9 | 656.7 | 563.4 | 675.9 | 568.1
891.3 | 672.3 | 723.1 | 655.2 | 549.3 | 672.5 | 567.1
892.3 | 673.3 | 718.9 | 651.6 | 542.1 | 667.8 | 565.8
893.3 | 674.3 | 714.9 | 644.2 | 540.5 | 664.9 | 564.2
894.3 | 675.3 | 710.2 | 630.8 | 526.3 | 660.5 | 562.3
895.3 | 676.3 | 704.9 | 609.9 | 508.6 | 656.3 | 560.5
896.3 | 677.3 | 700 | 594.7 | 495.7 | 652.6 | 559
897.3 | 678.3 | 696.9 | 592.5 | 495.3 | 650.1 | 558.6
898.3 | 679.3 | 695.4 | 595.5 | 490.9 | 648.6 | 557.4
899.3 | 680.3 | 694.6 | 601.5 | 495.1 | 648.7 | 557.3
900.3 | 681.3 | 691.6 | 602.4 | 487.4 | 645.5 | 555.2
901.3 | 682.3 | 689.4 | 597 | 487.5 | 643.4 | 553.4
902.3 | 683.3 | 688.2 | 602 | 500.2 | 641.7 | 553.9
903.3 | 684.3 | 687.1 | 609.8 | 509.9 | 641.4 | 555.4
904.3 | 685.3 | 687.1 | 614.2 | 518.1 | 641 | 555.5
905.3 | 686.3 | 686.8 | 624.8 | 526.3 | 639.6 | 555
906.3 | 687.3 | 686 | 627.2 | 533.2 | 637.8 | 555.5
907.3 | 688.3 | 684.5 | 627.4 | 534.9 | 636.2 | 555.1
908.3 | 689.3 | 686.6 | 642.9 | 552.5 | 639.5 | 557.2
909.3 | 690.3 | 691.1 | 653.3 | 569.1 | 647.2 | 557.8
910.3 | 691.3 | 697.9 | 668.5 | 573.7 | 655.5 | 558.9
911.3 | 692.3 | 703.4 | 674.1 | 600.7 | 662.9 | 562.1
912.3 | 693.3 | 709.3 | 679.7 | 621.1 | 672 | 564.1
913.3 | 694.3 | 712.7 | 683.7 | 633.8 | 675.6 | 565.9
914.3 | 695.3 | 714.7 | 686.7 | 641.5 | 676.5 | 567.4
915.3 | 696.3 | 714.7 | 680.4 | 625.4 | 676.7 | 567.1
916.3 | 697.3 | 712 | 669.9 | 606 | 673.6 | 564.9
917.3 | 698.3 | 709.1 | 660.8 | 590.3 | 671.3 | 564
918.3 | 699.3 | 704.9 | 638.9 | 570.7 | 668 | 561.5
919.3 | 700.3 | 701.5 | 626.1 | 560.3 | 664.1 | 560.2
920.3 | 701.3 | 697.9 | 611.8 | 543.6 | 660.2 | 559
921.3 | 702.3 | 693.2 | 596.8 | 527 | 655.4 | 557.3
922.3 | 703.3 | 689.4 | 594.1 | 520.6 | 650.4 | 556.2
923.3 | 704.3 | 686.7 | 591.3 | 530.3 | 646.8 | 556.1
924.3 | 705.3 | 688.3 | 601.5 | 552.4 | 648.2 | 559.3
925.3 | 706.3 | 690.7 | 610.2 | 571.6 | 651.1 | 560.4
926.3 | 707.3 | 693.3 | 614.4 | 590.6 | 657.8 | 564
927.3 | 708.3 | 696.2 | 622.6 | 601.4 | 660 | 565.6
928.3 | 709.3 | 697.3 | 628.7 | 613.8 | 660.5 | 567.5
929.3 | 710.3 | 698.3 | 629.2 | 605.9 | 663 | 568
930.3 | 711.3 | 698 | 630 | 599.9 | 663.2 | 567.1
931.3 | 712.3 | 697.2 | 631.2 | 597.4 | 662.5 | 566.7
932.3 | 713.3 | 698.8 | 639.7 | 611 | 665.1 | 567.5
933.3 | 714.3 | 702.2 | 646.2 | 614 | 669.9 | 568.4
934.3 | 715.3 | 702.1 | 642.5 | 615.5 | 670.8 | 568.7
935.3 | 716.3 | 702.5 | 643.3 | 628 | 672 | 569.8
936.3 | 717.3 | 705.2 | 652.4 | 639.9 | 674.9 | 570.6
937.3 | 718.3 | 707 | 650.5 | 630.7 | 676.1 | 570.1
938.3 | 719.3 | 709.7 | 649.7 | 633.8 | 679.1 | 571.2
939.3 | 720.3 | 708.5 | 642 | 632.1 | 678.2 | 570.7
940.3 | 721.3 | 705.1 | 620.4 | 612.9 | 674.8 | 568.1
941.3 | 722.3 | 702.9 | 613.5 | 595.2 | 672.3 | 566
942.3 | 723.3 | 700.1 | 605.4 | 573.6 | 668.8 | 563.8
943.3 | 724.3 | 696.9 | 599.7 | 560.8 | 665.6 | 562.2
944.3 | 725.3 | 694 | 593.1 | 553.6 | 662.1 | 560.8
945.3 | 726.3 | 695.7 | 600.7 | 555 | 662.5 | 560.9
946.3 | 727.3 | 699.3 | 618.4 | 569.4 | 665.1 | 561.8
947.3 | 728.3 | 702.2 | 626.3 | 594 | 668.3 | 565.1
948.3 | 729.3 | 703.9 | 625.7 | 595.6 | 671.6 | 564.5
949.3 | 730.3 | 707.1 | 632.2 | 614.4 | 674.7 | 566.3
950.3 | 731.3 | 710.5 | 640 | 628.5 | 679.1 | 568.3
951.3 | 732.3 | 713.3 | 642.1 | 624.2 | 682.9 | 566.4
952.3 | 733.3 | 713.9 | 641.5 | 616.1 | 683.1 | 565.5
953.3 | 734.3 | 712.1 | 642.6 | 615 | 680.1 | 564.3
954.3 | 735.3 | 709.5 | 636.7 | 615.3 | 676.2 | 564.2
955.3 | 736.3 | 709.1 | 640.6 | 614.1 | 674 | 564.6
956.3 | 737.3 | 713 | 651.3 | 633.3 | 677.1 | 568.2
957.3 | 738.3 | 719.3 | 671.7 | 643.5 | 683.9 | 569.3
958.3 | 739.3 | 724 | 672.1 | 641.8 | 689.3 | 570.3
959.3 | 740.3 | 724.3 | 668.4 | 635 | 689.7 | 569.6
960.3 | 741.3 | 723.9 | 663.9 | 628.8 | 689.8 | 569.2
961.3 | 742.3 | 725 | 668.1 | 633.4 | 691.6 | 570.1
962.3 | 743.3 | 726.2 | 664.5 | 641 | 694.7 | 569.5
963.3 | 744.3 | 724.4 | 653.3 | 636.7 | 693.3 | 569.6
964.3 | 745.3 | 724.8 | 656.5 | 632.5 | 693 | 569.5
965.3 | 746.3 | 723.2 | 657.2 | 625.5 | 689.5 | 569.5
966.3 | 747.3 | 721.5 | 645.8 | 605 | 685.7 | 567.5
967.3 | 748.3 | 719.2 | 639.4 | 594.4 | 683.1 | 565.5
968.3 | 749.3 | 715.3 | 631.1 | 578.5 | 679.7 | 563.3
969.3 | 750.3 | 714.1 | 634.7 | 577 | 678.3 | 563.3
970.3 | 751.3 | 710.4 | 623.1 | 564.2 | 673.4 | 562
971.3 | 752.3 | 708.1 | 623.1 | 569.5 | 670.3 | 562
972.3 | 753.3 | 703.8 | 616.7 | 555.4 | 665.4 | 559.9
973.3 | 754.3 | 702.7 | 621.7 | 550.6 | 661.8 | 559
974.3 | 755.3 | 704 | 623 | 540.3 | 661.4 | 557.8
975.3 | 756.3 | 705.4 | 626.2 | 544.7 | 662.2 | 557.7
976.3 | 757.3 | 708.3 | 635.6 | 547.8 | 665.6 | 557.8
977.3 | 758.3 | 711.2 | 652.4 | 559.2 | 667.3 | 558.5
978.3 | 759.3 | 713 | 654.9 | 572.4 | 670.3 | 559.9
979.3 | 760.3 | 714.2 | 651.8 | 588.1 | 673.7 | 560.1
980.3 | 761.3 | 719.7 | 662.5 | 593.2 | 682 | 560.8
981.3 | 762.3 | 723.3 | 663.3 | 613.2 | 688.9 | 562
982.3 | 763.3 | 725.5 | 661.4 | 611.4 | 692.8 | 562.6
983.3 | 764.3 | 724.7 | 660.4 | 614 | 692.3 | 560.7
984.3 | 765.3 | 722.7 | 653.9 | 601.7 | 689.9 | 560
985.3 | 766.3 | 718.6 | 639.3 | 582.2 | 684.6 | 557.6
986.3 | 767.3 | 714.8 | 633.5 | 573.8 | 679.1 | 556.5
987.3 | 768.3 | 714.6 | 633.7 | 576.5 | 678.5 | 557.1
988.3 | 769.3 | 714.6 | 632.3 | 569.3 | 677 | 556.3
989.3 | 770.3 | 713.5 | 632.2 | 564.2 | 674 | 555
990.3 | 771.3 | 718.3 | 650.4 | 596.3 | 679.7 | 558.5
991.3 | 772.3 | 727.2 | 666.5 | 630.4 | 693.1 | 563.1
992.3 | 773.3 | 734.2 | 683.4 | 660 | 703.3 | 567.2
993.3 | 774.3 | 741.3 | 702.9 | 695.2 | 715 | 572.1
994.3 | 775.3 | 746.8 | 710.3 | 716.9 | 723.3 | 576.6
995.3 | 776.3 | 750.3 | 700.7 | 720.4 | 731.4 | 578.1
996.3 | 777.3 | 750.8 | 695.4 | 711.4 | 733.6 | 578.6
997.3 | 778.3 | 750.5 | 701.5 | 707.6 | 732.1 | 580.4
998.3 | 779.3 | 748.9 | 699.6 | 705.8 | 730.1 | 580.2
999.3 | 780.3 | 752.2 | 709.9 | 711.3 | 733.7 | 582.3
1000.3 | 781.3 | 754.4 | 713.7 | 708.2 | 734 | 583.6
1001.3 | 782.3 | 757.8 | 718.8 | 708.7 | 737 | 585.6
1002.3 | 783.3 | 756 | 697.3 | 686.5 | 734.6 | 583
1003.3 | 784.3 | 751.7 | 682.3 | 659.5 | 729.7 | 581.1
1004.3 | 785.3 | 746.5 | 662.2 | 640.9 | 724 | 578.8
1005.3 | 786.3 | 744.5 | 654.5 | 625.9 | 720.7 | 577.1
1006.3 | 787.3 | 744.7 | 654.8 | 624.4 | 722.3 | 577.5
1007.3 | 788.3 | 746.5 | 665.2 | 630.2 | 725 | 577.7
1008.3 | 789.3 | 748.2 | 672.8 | 634.5 | 724.2 | 577.3
1009.3 | 790.3 | 748.7 | 675.2 | 637.4 | 723.9 | 577
1010.3 | 791.3 | 748.2 | 665.7 | 625.5 | 722 | 575.5
1011.3 | 792.3 | 748 | 657.7 | 622.1 | 720.6 | 574.4
1012.3 | 793.3 | 746.8 | 660.3 | 616.8 | 719.6 | 573.8
1013.3 | 794.3 | 745.3 | 662.8 | 610.1 | 718.7 | 572.1
1014.3 | 795.3 | 741.5 | 650.3 | 598.7 | 713.6 | 571.3
1015.3 | 796.3 | 736.6 | 634.1 | 580.1 | 706.5 | 568.5
1016.3 | 797.3 | 732.5 | 626.3 | 570.5 | 700.2 | 567.2
1017.3 | 798.3 | 731.2 | 631.3 | 563.8 | 698.1 | 566.7
1018.3 | 799.3 | 727.7 | 615.9 | 554 | 692.7 | 564.3
1019.3 | 800.3 | 723.1 | 601 | 543 | 685.5 | 562.1
1020.3 | 801.3 | 723.4 | 611.4 | 552 | 685.3 | 562.5
1021.3 | 802.3 | 721.6 | 613.5 | 566.2 | 683.8 | 563.4
1022.3 | 803.3 | 720.9 | 616.2 | 579.8 | 682.8 | 562.6
1023.3 | 804.3 | 719.9 | 619.2 | 585.5 | 679.9 | 563.3
1024.3 | 805.3 | 717.7 | 612.2 | 576.5 | 676.2 | 562.3
1025.3 | 806.3 | 717 | 610.1 | 574.9 | 674.9 | 563
1026.3 | 807.3 | 713.3 | 600.1 | 568.6 | 670 | 561.4
1027.3 | 808.3 | 712.4 | 602 | 571.2 | 668.1 | 561.5
1028.3 | 809.3 | 714.7 | 619.2 | 582.8 | 669.9 | 561.6
1029.3 | 810.3 | 718.1 | 629.4 | 607.1 | 675.6 | 565.1
1030.3 | 811.3 | 722 | 645.8 | 644.8 | 682.3 | 568.6
1031.3 | 812.3 | 722.7 | 634.7 | 642.4 | 686.7 | 572.9
1032.3 | 813.3 | 722.6 | 630.7 | 640.5 | 687.2 | 572.1
1033.3 | 814.3 | 720.7 | 618.5 | 639.8 | 684.8 | 570.9
1034.3 | 815.3 | 719.2 | 614.1 | 635.5 | 682.9 | 570.4
1035.3 | 816.3 | 718.6 | 623.1 | 626.2 | 682.6 | 569.7
1036.3 | 817.3 | 717.5 | 627.1 | 631.1 | 681.1 | 569.8
1037.3 | 818.3 | 717.3 | 635.1 | 638.8 | 681 | 570
1038.3 | 819.3 | 717.5 | 631 | 635.7 | 681.5 | 570.9
1039.3 | 820.3 | 714 | 618.9 | 622.6 | 678.1 | 568.6
1040.3 | 821.3 | 714.3 | 631.4 | 619.7 | 678.4 | 568
1041.3 | 822.3 | 713 | 615.2 | 606.2 | 677.1 | 567
1042.3 | 823.3 | 710.7 | 604.3 | 601.2 | 675.2 | 565.5
1043.3 | 824.3 | 709.1 | 592.1 | 590.8 | 673.6 | 565.2
1044.3 | 825.3 | 704.2 | 575.1 | 568.6 | 668.5 | 562.2
1045.3 | 826.3 | 699.6 | 566.6 | 555.4 | 662.7 | 560.1
1046.3 | 827.3 | 695.1 | 551.9 | 539.3 | 657.1 | 558
1047.3 | 828.3 | 690.2 | 547.7 | 538.3 | 650.5 | 556.5
1048.3 | 829.3 | 689.4 | 552 | 550.1 | 648.3 | 557
1049.3 | 830.3 | 691.1 | 558.3 | 570.7 | 649.8 | 558.6
1050.3 | 831.3 | 691.5 | 558.8 | 573.1 | 650.1 | 559.1
1051.3 | 832.3 | 689.7 | 549.6 | 561.3 | 649 | 557.3
1052.3 | 833.3 | 688.7 | 553.2 | 564.4 | 648.7 | 557.4
1053.3 | 834.3 | 688.1 | 555.8 | 568.8 | 649.5 | 556.5
1054.3 | 835.3 | 686.5 | 556.8 | 563 | 648.9 | 555.7
1055.3 | 836.3 | 683.4 | 549.1 | 545 | 644.8 | 553.2
1056.3 | 837.3 | 680.4 | 537.1 | 535.2 | 639.8 | 551.7
1057.3 | 838.3 | 677.8 | 532.9 | 525.2 | 636.4 | 551.1
1058.3 | 839.3 | 675.5 | 532.7 | 524.4 | 635 | 550.3
1059.3 | 840.3 | 674.3 | 537.3 | 525.1 | 633.3 | 549.3
1060.3 | 841.3 | 674.9 | 549.6 | 536.3 | 634.2 | 549.8
1061.3 | 842.3 | 676.1 | 562.8 | 551.6 | 634.7 | 549.7
1062.3 | 843.3 | 678.2 | 571.8 | 557.4 | 637.7 | 550.5
1063.3 | 844.3 | 679.9 | 586.7 | 558.2 | 639.8 | 549
1064.3 | 845.3 | 681.8 | 594.8 | 567.6 | 640.9 | 549
1065.3 | 846.3 | 682.7 | 603.2 | 589.9 | 641.9 | 550.8
1066.3 | 847.3 | 681.8 | 600.2 | 577.7 | 641 | 548.9
1067.3 | 848.3 | 680.4 | 604.2 | 573 | 640.4 | 548.3
1068.3 | 849.3 | 678.2 | 593.8 | 568.8 | 637 | 547.2
1069.3 | 850.3 | 676.3 | 586.3 | 562.3 | 634.1 | 546.1
1070.3 | 851.3 | 676.1 | 591.8 | 572.4 | 633.8 | 547.2
1071.3 | 852.3 | 675.8 | 597.9 | 576.9 | 635 | 546.5
1072.3 | 853.3 | 679.2 | 618.9 | 597.1 | 640.7 | 549.4
1073.3 | 854.3 | 680.2 | 611.2 | 599.3 | 643.4 | 549.9
1074.3 | 855.3 | 676.1 | 590.2 | 582.1 | 640.9 | 547
1075.3 | 856.3 | 673.6 | 582.4 | 574.2 | 638.7 | 545.8
1076.3 | 857.3 | 673.1 | 583.8 | 571.8 | 637.7 | 545.8
1077.3 | 858.3 | 677.1 | 600.7 | 581.6 | 640.7 | 547
1078.3 | 859.3 | 679.9 | 613.8 | 592.4 | 641.8 | 548.1
1079.3 | 860.3 | 684.5 | 641.1 | 598.3 | 646.1 | 549.1
1080.3 | 861.3 | 690.5 | 659.8 | 615.8 | 653.2 | 549.8
1081.3 | 862.3 | 697.2 | 673.6 | 625.3 | 663.4 | 552.3
1082.3 | 863.3 | 700.9 | 681.1 | 628.5 | 670.8 | 553.4
1083.3 | 864.3 | 703.6 | 678.2 | 649 | 676.9 | 556
1084.3 | 865.3 | 704.4 | 671.6 | 667.1 | 679.3 | 559.1
1085.3 | 866.3 | 703.8 | 663.5 | 664.2 | 679.2 | 559.4
1086.3 | 867.3 | 702.9 | 648 | 672.7 | 678.5 | 561.5
1087.3 | 868.3 | 705.2 | 659 | 678.3 | 682.2 | 562.4
1088.3 | 869.3 | 704.5 | 649.2 | 663.2 | 680.6 | 560.3
1089.3 | 870.3 | 703.5 | 653.6 | 660.5 | 677.7 | 559.7
1090.3 | 871.3 | 702.7 | 647.2 | 651.2 | 676.7 | 559.1
1091.3 | 872.3 | 701 | 638.4 | 646 | 673.8 | 558.4
1092.3 | 873.3 | 700.3 | 635.1 | 648.1 | 672.3 | 559.5
1093.3 | 874.3 | 700.1 | 626.2 | 652.7 | 670.9 | 560.4
1094.3 | 875.3 | 701.2 | 630.4 | 663.8 | 671.6 | 563.5
1095.3 | 876.3 | 701.1 | 628.2 | 646.4 | 673.4 | 562.1
1096.3 | 877.3 | 697.7 | 606.7 | 628.6 | 670.5 | 559.2
1097.3 | 878.3 | 694.5 | 597.1 | 615.9 | 667.2 | 557.8
1098.3 | 879.3 | 693.1 | 595.4 | 618.8 | 663 | 557
1099.3 | 880.3 | 691 | 580.3 | 609.1 | 659.6 | 555.7
1100.3 | 881.3 | 686.2 | 561.1 | 583.4 | 654.5 | 553.1
1101.3 | 882.3 | 679.2 | 536.7 | 560.4 | 648.4 | 550.5
1102.3 | 883.3 | 672.4 | 514.5 | 540.8 | 642.1 | 547.9
1103.3 | 884.3 | 665.7 | 497.8 | 522 | 635.4 | 545.6
1104.3 | 885.3 | 661.7 | 495.3 | 519.2 | 627.7 | 544.8
1105.3 | 886.3 | 659.8 | 495.1 | 511.8 | 622.5 | 543.7
1106.3 | 887.3 | 657.2 | 486.1 | 501.3 | 619.2 | 541.9
1107.3 | 888.3 | 659.4 | 512.5 | 520 | 620.9 | 542.3
1108.3 | 889.3 | 663.6 | 539.2 | 541.3 | 627 | 544.5
1109.3 | 890.3 | 667.1 | 556 | 567.1 | 632.8 | 546.4
1110.3 | 891.3 | 667.5 | 553.9 | 572.9 | 635.6 | 547.1
1111.3 | 892.3 | 670 | 563 | 598.4 | 643.6 | 548.9
1112.3 | 893.3 | 674.5 | 584.5 | 626.1 | 651.7 | 552.4
1113.3 | 894.3 | 675.2 | 581.1 | 625.9 | 653.1 | 551.2
1114.3 | 895.3 | 676.6 | 590.7 | 636.9 | 655.7 | 554.5
1115.3 | 896.3 | 674.3 | 577.9 | 635.9 | 653.1 | 553.6
1116.3 | 897.3 | 673 | 579.4 | 624.8 | 651 | 553.3
1117.3 | 898.3 | 671.9 | 575.1 | 613.7 | 648.2 | 552.4
1118.3 | 899.3 | 668.9 | 569.1 | 606.2 | 642.3 | 550.8
1119.3 | 900.3 | 669.3 | 578.5 | 609.2 | 641.1 | 550.1
1120.3 | 901.3 | 670.5 | 592.5 | 624.5 | 641.4 | 552
1121.3 | 902.3 | 670 | 586.1 | 619.2 | 639.7 | 551.4
1122.3 | 903.3 | 669.1 | 589.3 | 621 | 638 | 550.1
1123.3 | 904.3 | 672 | 606 | 635.4 | 640.7 | 552.6
1124.3 | 905.3 | 673.7 | 599.1 | 639 | 643.6 | 553
1125.3 | 906.3 | 673.8 | 599.9 | 615.8 | 643.7 | 551
1126.3 | 907.3 | 672.1 | 589.8 | 600.5 | 641.5 | 548.6
1127.3 | 908.3 | 671.3 | 584.9 | 596.7 | 642.3 | 548.1
1128.3 | 909.3 | 670.5 | 582.1 | 605 | 643.4 | 549.4
1129.3 | 910.3 | 671.1 | 583 | 607.8 | 643.8 | 551.9
1130.3 | 911.3 | 669.3 | 573.2 | 594.9 | 642 | 549.9
1131.3 | 912.3 | 666.5 | 566.5 | 583.6 | 638.1 | 548.4
1132.3 | 913.3 | 661.8 | 542.4 | 564.3 | 633.9 | 545.7
1133.3 | 914.3 | 661.2 | 548.8 | 567.5 | 632.3 | 545.3
1134.3 | 915.3 | 658.7 | 543.8 | 557.7 | 628.5 | 543.9
1135.3 | 916.3 | 656.2 | 542.2 | 560.1 | 625.2 | 543
1136.3 | 917.3 | 655.7 | 548.6 | 564.1 | 623.5 | 543.4
1137.3 | 918.3 | 656.9 | 554.5 | 576.3 | 624.6 | 544.5
1138.3 | 919.3 | 661.5 | 570.8 | 588.2 | 628.9 | 545.4
1139.3 | 920.3 | 662.9 | 583.2 | 590.6 | 628.4 | 545.5
1140.3 | 921.3 | 664.4 | 600.5 | 598.5 | 628.1 | 546.1
1141.3 | 922.3 | 664 | 601.7 | 597.5 | 627.1 | 546.7
1142.3 | 923.3 | 666.3 | 601 | 609.9 | 631 | 548.4
1143.3 | 924.3 | 670.5 | 608.1 | 616.7 | 637.3 | 548.8
1144.3 | 925.3 | 674.6 | 608.7 | 623 | 643.6 | 548.9
1145.3 | 926.3 | 675.1 | 596.9 | 617.2 | 646.3 | 547.4
1146.3 | 927.3 | 672.9 | 579.1 | 603.5 | 644.6 | 546.2
1147.3 | 928.3 | 669 | 562.6 | 582.8 | 640.2 | 543.8
1148.3 | 929.3 | 665.5 | 548.6 | 572.9 | 635.6 | 542
1149.3 | 930.3 | 663.8 | 540.4 | 565.4 | 632.2 | 540.5
1150.3 | 931.3 | 665.1 | 552.3 | 568.3 | 631.6 | 540.1
1151.3 | 932.3 | 665.1 | 545.6 | 565.4 | 630.7 | 538.6
1152.3 | 933.3 | 665.2 | 558.2 | 566.2 | 630.7 | 538.3
1153.3 | 934.3 | 666 | 586 | 583.5 | 631.4 | 539.9
1154.3 | 935.3 | 669.6 | 609.6 | 611.8 | 637 | 543.8
1155.3 | 936.3 | 674.4 | 627.7 | 637.3 | 646.8 | 546.6
1156.3 | 937.3 | 682.1 | 657.2 | 674.6 | 660.8 | 553
1157.3 | 938.3 | 684.8 | 660.6 | 680.4 | 663.3 | 556.2
1158.3 | 939.3 | 686.4 | 660.7 | 684.1 | 665.8 | 555.7
1159.3 | 940.3 | 685.7 | 640.8 | 668 | 664.2 | 554.9
1160.3 | 941.3 | 684.3 | 631.4 | 658.2 | 660.8 | 553.4
1161.3 | 942.3 | 681.5 | 612.3 | 650.1 | 655.1 | 552.3
1162.3 | 943.3 | 679.1 | 608.4 | 641.3 | 649.1 | 550.1
1163.3 | 944.3 | 680.3 | 623.5 | 631.4 | 649.2 | 550.8
1164.3 | 945.3 | 678.7 | 609.5 | 624.2 | 646.4 | 550
1165.3 | 946.3 | 678.1 | 609.6 | 625.9 | 643 | 549.9
1166.3 | 947.3 | 677.4 | 615.6 | 623.2 | 640.9 | 549.9
1167.3 | 948.3 | 678.1 | 630.9 | 637.7 | 640.3 | 550.6
1168.3 | 949.3 | 679.5 | 644.9 | 645.5 | 641.3 | 550.3
1169.3 | 950.3 | 678 | 633.4 | 627.8 | 637.1 | 548.4
1170.3 | 951.3 | 674.7 | 610.1 | 613.6 | 632.9 | 546.5
1171.3 | 952.3 | 669.8 | 584.2 | 593.7 | 627.9 | 544.3
1172.3 | 953.3 | 663.6 | 558.1 | 573.9 | 621.4 | 541.9
1173.3 | 954.3 | 659.8 | 546 | 573.4 | 616.8 | 541.6
1174.3 | 955.3 | 657.6 | 547.4 | 573.3 | 613.1 | 541.1
1175.3 | 956.3 | 657 | 549.7 | 568.9 | 611.1 | 539.2
1176.3 | 957.3 | 659.4 | 574.8 | 580.2 | 612.4 | 539.7
1177.3 | 958.3 | 662.3 | 571.5 | 581.2 | 616.9 | 540.2
1178.3 | 959.3 | 661.7 | 562.2 | 578.4 | 618.1 | 539.4
1179.3 | 960.3 | 662.5 | 563.7 | 570.3 | 619.7 | 539.7
1180.3 | 961.3 | 661.7 | 556.3 | 562 | 619.8 | 539
1181.3 | 962.3 | 660.1 | 554 | 566.2 | 619.4 | 537.8
1182.3 | 963.3 | 664.8 | 575.4 | 593.4 | 626.7 | 540.8
1183.3 | 964.3 | 665.8 | 586.5 | 598.9 | 626.9 | 541.7
1184.3 | 965.3 | 668.1 | 617.7 | 608.1 | 629.2 | 541.8
1185.3 | 966.3 | 670.5 | 626.7 | 618.4 | 631.7 | 542
1186.3 | 967.3 | 674.8 | 638.2 | 634.6 | 637.8 | 545.9
1187.3 | 968.3 | 675.6 | 630.8 | 632 | 637.7 | 545.1
1188.3 | 969.3 | 679.4 | 645.6 | 652.1 | 643.6 | 547.6
1189.3 | 970.3 | 684.8 | 660.2 | 672.5 | 653.5 | 550.5
1190.3 | 971.3 | 688.8 | 658.2 | 678.5 | 660.4 | 552.8
1191.3 | 972.3 | 690.6 | 655.4 | 685.6 | 664.4 | 553.8
1192.3 | 973.3 | 690.8 | 658.4 | 690.1 | 666.6 | 555.4
1193.3 | 974.3 | 691.5 | 659 | 695.3 | 668 | 557.1
1194.3 | 975.3 | 692.9 | 666.4 | 701.4 | 668.8 | 559.1
1195.3 | 976.3 | 694.9 | 673.8 | 709.3 | 671 | 562.1
1196.3 | 977.3 | 699.4 | 677.6 | 708.2 | 678.8 | 563.6
1197.3 | 978.3 | 700.3 | 668.6 | 701.4 | 679.1 | 563.1
1198.3 | 979.3 | 703.5 | 690.9 | 698.8 | 681.6 | 565
1199.3 | 980.3 | 702.9 | 671.8 | 689.5 | 681.4 | 565.4
1200.3 | 981.3 | 702.9 | 671 | 681.5 | 681.9 | 564.1
1201.3 | 982.3 | 705.5 | 675.9 | 682.7 | 688 | 565.4
1202.3 | 983.3 | 708.8 | 677.4 | 687.9 | 694.2 | 567.7
1203.3 | 984.3 | 710.2 | 694.1 | 689.6 | 696.4 | 567.9
1204.3 | 985.3 | 714.2 | 708 | 705.4 | 702.1 | 570.1
1205.3 | 986.3 | 716.8 | 711.8 | 703.8 | 704.4 | 571.9
1206.3 | 987.3 | 716.2 | 696 | 693.9 | 702.2 | 571.9
1207.3 | 988.3 | 716.6 | 689.9 | 684.6 | 701.7 | 571.2
1208.3 | 989.3 | 719 | 698.7 | 685 | 704.3 | 571.3
1209.3 | 990.3 | 719.5 | 687.8 | 672.1 | 702.8 | 569.9
1210.3 | 991.3 | 719.5 | 690.6 | 657.6 | 701.3 | 568.3
1211.3 | 992.3 | 719.3 | 696.6 | 660.1 | 700.7 | 567.4
1212.3 | 993.3 | 718.5 | 690.9 | 652.9 | 698.1 | 566.9
1213.3 | 994.3 | 716.2 | 679.7 | 649.9 | 694.1 | 564.7
1214.3 | 995.3 | 715.1 | 664.5 | 652.5 | 690.5 | 564.3
1215.3 | 996.3 | 714.4 | 649.5 | 652.4 | 688.4 | 564.5
1216.3 | 997.3 | 717.2 | 665.7 | 666 | 691.9 | 566.3
1217.3 | 998.3 | 720.5 | 675.2 | 676.5 | 695.9 | 568.1
1218.3 | 999.3 | 722.3 | 682.9 | 681.6 | 698 | 569.3
1219.3 | 1000.3 | 722 | 664.9 | 678.3 | 698.4 | 568.7
1220.3 | 1001.3 | 721.9 | 661.6 | 687.3 | 699.2 | 570.3
1221.3 | 1002.3 | 724.1 | 672.2 | 702.6 | 702.3 | 571.4
1222.3 | 1003.3 | 724.5 | 656.2 | 686.4 | 703.2 | 570
1223.3 | 1004.3 | 721.7 | 644 | 676.2 | 699.9 | 569.9
1224.3 | 1005.3 | 716.3 | 617.5 | 661.6 | 692.8 | 566.8
1225.3 | 1006.3 | 711.9 | 621.1 | 651.8 | 685.7 | 564.4
1226.3 | 1007.3 | 711.8 | 618.5 | 640.9 | 682.9 | 563.7
1227.3 | 1008.3 | 709.4 | 609.4 | 632.6 | 678.9 | 562.1
1228.3 | 1009.3 | 710.4 | 619.6 | 635.2 | 678.7 | 562.4
1229.3 | 1010.3 | 713.9 | 648.6 | 652.8 | 682.3 | 562.6
1230.3 | 1011.3 | 718.4 | 670.7 | 673.3 | 688.1 | 567.4
1231.3 | 1012.3 | 720.7 | 690.8 | 695.9 | 690.7 | 571.4
1232.3 | 1013.3 | 721.2 | 686.1 | 704.7 | 691.9 | 574.4
1233.3 | 1014.3 | 724 | 685.5 | 712.3 | 697.5 | 576
1234.3 | 1015.3 | 723.6 | 691.2 | 714.1 | 697.3 | 576.1
1235.3 | 1016.3 | 725.7 | 691.8 | 720.8 | 701.2 | 576.4
1236.3 | 1017.3 | 727.1 | 692.2 | 721.2 | 703.5 | 579
1237.3 | 1018.3 | 725.4 | 679.9 | 721.1 | 701.5 | 578.8
1238.3 | 1019.3 | 726.3 | 679.1 | 727.8 | 704.3 | 579.7
1239.3 | 1020.3 | 727.5 | 681.2 | 729.6 | 706.2 | 581
1240.3 | 1021.3 | 730 | 692.8 | 728.6 | 709 | 581.6
1241.3 | 1022.3 | 733 | 690 | 729.1 | 713.3 | 585.6
1242.3 | 1023.3 | 733.5 | 687 | 723.5 | 714.9 | 585.3
1243.3 | 1024.3 | 734.9 | 679.9 | 722 | 718.9 | 585
1244.3 | 1025.3 | 736.4 | 675.1 | 710.4 | 723.3 | 584.7
1245.3 | 1026.3 | 735.2 | 653.8 | 695.5 | 724.6 | 582.6
1246.3 | 1027.3 | 731.9 | 646.4 | 680 | 719.6 | 579.9
1247.3 | 1028.3 | 730.3 | 642.4 | 673 | 715.1 | 578.3
1248.3 | 1029.3 | 729.1 | 636.1 | 671.3 | 712.5 | 576.9
1249.3 | 1030.3 | 728.5 | 651 | 686.6 | 710.6 | 577.4
1250.3 | 1031.3 | 731.9 | 677.3 | 705 | 712.5 | 582.4
1251.3 | 1032.3 | 737.8 | 699.8 | 720 | 721.6 | 585.1
1252.3 | 1033.3 | 740.3 | 696.5 | 705.4 | 724 | 583.8
1253.3 | 1034.3 | 740.7 | 703.4 | 694.4 | 725.8 | 582.2
1254.3 | 1035.3 | 746.2 | 707 | 694.6 | 734.6 | 583.7
1255.3 | 1036.3 | 750.9 | 717.5 | 694.6 | 742.1 | 583.9
1256.3 | 1037.3 | 755.5 | 718 | 696.2 | 749.5 | 584.4
1257.3 | 1038.3 | 757.4 | 711.1 | 701.1 | 753 | 585.4
1258.3 | 1039.3 | 757.7 | 709.8 | 718.1 | 751.8 | 588.6
1259.3 | 1040.3 | 758.6 | 700.4 | 725.9 | 753.3 | 591.6
1260.3 | 1041.3 | 759.3 | 700.6 | 726.4 | 753.6 | 591.2
1261.3 | 1042.3 | 758.2 | 702.1 | 730.3 | 751.8 | 590.5
1262.3 | 1043.3 | 758.7 | 695.6 | 729 | 753.7 | 591
1263.3 | 1044.3 | 757.7 | 683.3 | 722.7 | 752.4 | 590.2
1264.3 | 1045.3 | 754.1 | 682 | 714 | 745.3 | 588.2
1265.3 | 1046.3 | 755.8 | 695 | 719.9 | 746.8 | 588.9
1266.3 | 1047.3 | 757.8 | 698.5 | 724.9 | 749.5 | 590
1267.3 | 1048.3 | 759.9 | 704.2 | 736 | 752.5 | 592.3
1268.3 | 1049.3 | 760.6 | 704.2 | 739.6 | 753.2 | 593.2
1269.3 | 1050.3 | 760.6 | 714.5 | 751.2 | 753.5 | 597.2
1270.3 | 1051.3 | 763.4 | 728.2 | 750.1 | 756.4 | 596.9
1271.3 | 1052.3 | 765.1 | 724.8 | 751.8 | 757.6 | 599.1
1272.3 | 1053.3 | 764.9 | 702.7 | 744.4 | 756.6 | 600
1273.3 | 1054.3 | 765.1 | 711.4 | 740.9 | 756.9 | 600.3
1274.3 | 1055.3 | 766 | 707.7 | 735 | 759.9 | 600.1
1275.3 | 1056.3 | 766.3 | 704.6 | 723.6 | 757.8 | 597.6
1276.3 | 1057.3 | 767.5 | 704.3 | 720.2 | 757.9 | 596.7
1277.3 | 1058.3 | 768.7 | 701.7 | 731.5 | 761.3 | 597.4
1278.3 | 1059.3 | 772.1 | 715.6 | 743.1 | 768 | 602
1279.3 | 1060.3 | 774.6 | 728.9 | 745 | 772.5 | 604.4
1280.3 | 1061.3 | 772.1 | 715 | 728.8 | 767.9 | 603.2
1281.3 | 1062.3 | 767.4 | 685.5 | 713.3 | 759.8 | 600.2
1282.3 | 1063.3 | 761.4 | 656.6 | 694.4 | 749.9 | 596.7
1283.3 | 1064.3 | 755.4 | 649.7 | 689.7 | 739.7 | 594.4
1284.3 | 1065.3 | 750.9 | 634.9 | 682.7 | 732.3 | 593
1285.3 | 1066.3 | 746.4 | 623.4 | 668.9 | 724.1 | 590.1
1286.3 | 1067.3 | 745 | 635.4 | 669.6 | 720.2 | 589.7
1287.3 | 1068.3 | 745.5 | 637.6 | 671.5 | 720 | 589.9
1288.3 | 1069.3 | 748 | 658.1 | 679.5 | 725.1 | 590.5
1289.3 | 1070.3 | 749.8 | 659.6 | 683.1 | 729 | 591.4
1290.3 | 1071.3 | 750.2 | 663.1 | 693.9 | 730.6 | 592
1291.3 | 1072.3 | 749.8 | 667.4 | 709.1 | 732.2 | 593.9
1292.3 | 1073.3 | 751.2 | 685.8 | 724.4 | 735.3 | 600.3
1293.3 | 1074.3 | 754.3 | 693.4 | 725.4 | 740.2 | 603.6
1294.3 | 1075.3 | 752.5 | 687.2 | 706.4 | 736.4 | 601.1
1295.3 | 1076.3 | 748.9 | 677.1 | 694.1 | 729.5 | 599.8
1296.3 | 1077.3 | 747.7 | 679.3 | 693.4 | 725.1 | 599.5
1297.3 | 1078.3 | 748 | 680.7 | 704.7 | 722.2 | 600.4
1298.3 | 1079.3 | 749.6 | 674.5 | 713.4 | 726.7 | 602.1
1299.3 | 1080.3 | 746.9 | 657.7 | 708.1 | 724 | 600.2
1300.3 | 1081.3 | 743 | 645.3 | 700.3 | 718.1 | 598.6
1301.3 | 1082.3 | 740.1 | 624.7 | 685.9 | 712 | 596.5
1302.3 | 1083.3 | 733.5 | 604.4 | 670.3 | 703.2 | 592.5
1303.3 | 1084.3 | 730.6 | 604.1 | 671.7 | 699.5 | 592.4
1304.3 | 1085.3 | 728.8 | 604.1 | 672.6 | 695.5 | 592.2
1305.3 | 1086.3 | 729.8 | 618.7 | 675.7 | 695.8 | 592.9
1306.3 | 1087.3 | 730 | 609.8 | 665.8 | 697.3 | 591.2
1307.3 | 1088.3 | 729.8 | 608 | 658.7 | 698.1 | 589.9
1308.3 | 1089.3 | 728.8 | 599.2 | 670.5 | 698.8 | 590.1
1309.3 | 1090.3 | 730.7 | 613.5 | 685.4 | 702.7 | 592.2
1310.3 | 1091.3 | 728.7 | 608.6 | 676.2 | 699.8 | 590.1
1311.3 | 1092.3 | 726.8 | 615.7 | 687.4 | 696.3 | 589.8
1312.3 | 1093.3 | 726.4 | 622.6 | 681.7 | 694.2 | 590
1313.3 | 1094.3 | 723.6 | 611.8 | 675.8 | 690.3 | 587.7
1314.3 | 1095.3 | 722.8 | 620.5 | 676.2 | 690.2 | 587.9
1315.3 | 1096.3 | 720.7 | 613 | 669.9 | 688 | 586
1316.3 | 1097.3 | 718.7 | 615.3 | 658.5 | 684.3 | 583.7
1317.3 | 1098.3 | 717.2 | 609.2 | 649.5 | 681.7 | 582.1
1318.3 | 1099.3 | 717.5 | 616.7 | 653.5 | 683.8 | 582.2
1319.3 | 1100.3 | 717 | 613.6 | 654.1 | 684.1 | 581.5
1320.3 | 1101.3 | 715 | 602 | 640.4 | 680.8 | 579.3
1321.3 | 1102.3 | 711 | 589.7 | 632.6 | 675.1 | 576.9
1322.3 | 1103.3 | 708.8 | 585.1 | 635.6 | 671.6 | 575.5
1323.3 | 1104.3 | 707.6 | 582.7 | 635.3 | 670.1 | 574.1
1324.3 | 1105.3 | 708.5 | 605.7 | 638.4 | 671.3 | 574.7
1325.3 | 1106.3 | 705.6 | 593.8 | 628.6 | 667.5 | 572
1326.3 | 1107.3 | 704.3 | 595.4 | 624.9 | 667.3 | 571.2
1327.3 | 1108.3 | 700.9 | 578.7 | 625.4 | 664.6 | 569.5
1328.3 | 1109.3 | 698.2 | 567.8 | 622 | 662.7 | 569.5
1329.3 | 1110.3 | 693.6 | 558.9 | 615.1 | 658.5 | 567.6
1330.3 | 1111.3 | 690.1 | 550.1 | 612.7 | 654.7 | 566.2
1331.3 | 1112.3 | 686.8 | 536.8 | 607.2 | 649.5 | 564.1
1332.3 | 1113.3 | 684.7 | 542.7 | 619.2 | 645.7 | 563.4
1333.3 | 1114.3 | 684.6 | 546.2 | 638.5 | 647.3 | 566
1334.3 | 1115.3 | 686.1 | 561.9 | 642 | 651.6 | 567.4
1335.3 | 1116.3 | 688.9 | 573.6 | 648.1 | 656.9 | 567.6
1336.3 | 1117.3 | 690.3 | 577.9 | 653.2 | 659.6 | 568.6
1337.3 | 1118.3 | 690 | 570.8 | 649 | 658.7 | 567.4
1338.3 | 1119.3 | 692.4 | 594.4 | 648 | 662 | 568.2
1339.3 | 1120.3 | 695 | 606.4 | 644.5 | 664.2 | 566.4
1340.3 | 1121.3 | 695.3 | 599.5 | 643.1 | 663.8 | 565.8
1341.3 | 1122.3 | 695.6 | 605.1 | 641.4 | 663.8 | 565.3
1342.3 | 1123.3 | 693.7 | 594.6 | 634.3 | 660.3 | 563.3
1343.3 | 1124.3 | 690.4 | 586.4 | 623.1 | 656.3 | 561.1
1344.3 | 1125.3 | 688.2 | 583 | 623.4 | 652.9 | 561.3
1345.3 | 1126.3 | 686.7 | 580 | 631.2 | 650.1 | 560.6
1346.3 | 1127.3 | 685.9 | 578.7 | 638.4 | 647.8 | 561
1347.3 | 1128.3 | 682.7 | 562.7 | 625.8 | 642.9 | 559
1348.3 | 1129.3 | 678.5 | 549.7 | 610.3 | 638.8 | 556.9
1349.3 | 1130.3 | 673.3 | 534.1 | 597 | 633.5 | 554.4
1350.3 | 1131.3 | 668.8 | 517.9 | 589.3 | 628.4 | 552.1
1351.3 | 1132.3 | 669.8 | 536.9 | 599.9 | 630.7 | 552.1
1352.3 | 1133.3 | 672.5 | 558.5 | 616.3 | 633.9 | 554.9
1353.3 | 1134.3 | 674.3 | 562.1 | 626.2 | 637.5 | 554.8
1354.3 | 1135.3 | 680.8 | 587 | 649.6 | 650.7 | 559.2
1355.3 | 1136.3 | 683.6 | 599.9 | 660.4 | 654.7 | 562.7
1356.3 | 1137.3 | 685.1 | 603.7 | 659.7 | 657.4 | 564
1357.3 | 1138.3 | 683.1 | 596.1 | 660.2 | 654.5 | 563.6
1358.3 | 1139.3 | 683 | 601.9 | 658.4 | 656.3 | 563.1
1359.3 | 1140.3 | 681.7 | 588.5 | 649.6 | 653 | 562.2
1360.3 | 1141.3 | 680.7 | 587 | 638 | 652.7 | 560
1361.3 | 1142.3 | 680.1 | 591.3 | 639.5 | 650.9 | 558.6
1362.3 | 1143.3 | 679.8 | 583 | 636.2 | 650.9 | 558.2
1363.3 | 1144.3 | 678.6 | 570 | 633.6 | 649.2 | 557
1364.3 | 1145.3 | 679.7 | 595.3 | 647.5 | 651.3 | 558.2
1365.3 | 1146.3 | 680.9 | 597.7 | 656.3 | 652.8 | 561.9
1366.3 | 1147.3 | 679.8 | 580.5 | 645.2 | 652.4 | 560.6
1367.3 | 1148.3 | 677.1 | 564.1 | 634.1 | 649.3 | 558.4
1368.3 | 1149.3 | 676.7 | 568.4 | 631.7 | 649.2 | 558.8
1369.3 | 1150.3 | 678.3 | 579.8 | 637.1 | 651.7 | 559.3
1370.3 | 1151.3 | 677.5 | 572.4 | 633.1 | 648.7 | 557.6
1371.3 | 1152.3 | 676.9 | 571.7 | 635.1 | 645.7 | 556.9
1372.3 | 1153.3 | 676 | 574.6 | 636.4 | 644.6 | 557
1373.3 | 1154.3 | 676.1 | 575.5 | 632.3 | 645.2 | 555.5
1374.3 | 1155.3 | 675.5 | 581.3 | 632.3 | 645.4 | 555.4
1375.3 | 1156.3 | 676.7 | 589.2 | 635.7 | 648.5 | 554.9
1376.3 | 1157.3 | 680.7 | 602.4 | 650.7 | 654 | 557.5
1377.3 | 1158.3 | 683.1 | 611.3 | 662.7 | 656.8 | 559.8
1378.3 | 1159.3 | 686 | 629.5 | 679.9 | 662.7 | 566.1
1379.3 | 1160.3 | 689.6 | 637.8 | 680.4 | 669.2 | 565.9
1380.3 | 1161.3 | 688.7 | 628.5 | 679.4 | 668.9 | 565.9
1381.3 | 1162.3 | 686.5 | 615.7 | 670.9 | 666.4 | 564.9
1382.3 | 1163.3 | 686.8 | 612.9 | 679.9 | 668.1 | 566.3
1383.3 | 1164.3 | 690.1 | 615.7 | 685.2 | 676.6 | 567.4
1384.3 | 1165.3 | 693.4 | 616.1 | 685.1 | 684 | 567.9
1385.3 | 1166.3 | 696.1 | 617 | 684.1 | 687.8 | 567.7
1386.3 | 1167.3 | 697.3 | 630.6 | 686.9 | 688.9 | 568.4
1387.3 | 1168.3 | 696.9 | 619.6 | 678.3 | 690 | 566.6
1388.3 | 1169.3 | 691.8 | 590.7 | 655.8 | 682.2 | 562.2
1389.3 | 1170.3 | 687 | 577.5 | 641.5 | 673.7 | 559.7
1390.3 | 1171.3 | 682.6 | 565.3 | 631.4 | 667.1 | 558.1
1391.3 | 1172.3 | 681.2 | 581.2 | 634 | 665.1 | 558.2
1392.3 | 1173.3 | 678.7 | 574.9 | 630.1 | 661.1 | 557.1
1393.3 | 1174.3 | 678.3 | 573 | 631.3 | 660.1 | 555.9
1394.3 | 1175.3 | 678.5 | 570.2 | 621.5 | 660.5 | 554.4
1395.3 | 1176.3 | 679 | 582.4 | 621 | 657.9 | 553.7
1396.3 | 1177.3 | 678.9 | 591.4 | 619.6 | 655.3 | 553.3
1397.3 | 1178.3 | 676.6 | 585.6 | 611.6 | 651.2 | 552.1
1398.3 | 1179.3 | 673 | 576.1 | 608.1 | 646.1 | 550.3
1399.3 | 1180.3 | 669.5 | 559.8 | 601.8 | 641.4 | 548.3
1400.3 | 1181.3 | 666.1 | 554.2 | 592.5 | 637 | 546.4
1401.3 | 1182.3 | 663.8 | 549.6 | 583.7 | 633.8 | 544.9
1402.3 | 1183.3 | 663.3 | 550.8 | 580.8 | 631.7 | 544.1
1403.3 | 1184.3 | 663.4 | 553.7 | 593.1 | 630.8 | 544.5
1404.3 | 1185.3 | 666.1 | 563.2 | 603.4 | 633.3 | 546.3
1405.3 | 1186.3 | 668.9 | 583.2 | 604.3 | 635.5 | 546.4
1406.3 | 1187.3 | 671.6 | 599.9 | 607.2 | 637.8 | 546.5
1407.3 | 1188.3 | 671.8 | 596.2 | 613.5 | 639 | 546.3
1408.3 | 1189.3 | 673.3 | 595.8 | 620.6 | 644.2 | 547.8
1409.3 | 1190.3 | 672.5 | 585.6 | 605.8 | 644.2 | 545.7
1410.3 | 1191.3 | 670.2 | 574.9 | 601.2 | 642.4 | 544.9
1411.3 | 1192.3 | 668 | 559.8 | 598.7 | 640.9 | 543.9
1412.3 | 1193.3 | 667.4 | 551.7 | 597.4 | 640.1 | 542.7
1413.3 | 1194.3 | 668.3 | 556.7 | 588.8 | 641.3 | 541.5
1414.3 | 1195.3 | 667.2 | 559.7 | 585.5 | 640 | 540.3
1415.3 | 1196.3 | 664.4 | 548.5 | 576.7 | 637.5 | 538.2
1416.3 | 1197.3 | 661.2 | 533.2 | 571.6 | 633.6 | 537.1
1417.3 | 1198.3 | 658.4 | 525 | 566.6 | 630.6 | 536
1418.3 | 1199.3 | 658.1 | 532.9 | 566.8 | 629.7 | 535.6
1419.3 | 1200.3 | 661.4 | 551.4 | 579.6 | 633.8 | 537.1
1420.3 | 1201.3 | 665.7 | 563.8 | 586.4 | 639.6 | 537.5
1421.3 | 1202.3 | 668.7 | 576.1 | 588.8 | 645.2 | 538.2
1422.3 | 1203.3 | 670.2 | 585 | 593.2 | 645.2 | 538.3
1423.3 | 1204.3 | 674.3 | 611.1 | 592.3 | 648 | 539.4
1424.3 | 1205.3 | 679.9 | 623.6 | 609.8 | 657.4 | 541.3
1425.3 | 1206.3 | 683.9 | 635.1 | 622.3 | 665 | 542.1
1426.3 | 1207.3 | 686.9 | 643.6 | 629.4 | 671.9 | 542.5
1427.3 | 1208.3 | 687.3 | 639.7 | 633.5 | 673.3 | 542.3
1428.3 | 1209.3 | 687.6 | 631.3 | 633.1 | 673.6 | 541.5
1429.3 | 1210.3 | 687.3 | 632.3 | 633.7 | 672.5 | 540.6
1430.3 | 1211.3 | 683.1 | 612 | 620.6 | 667 | 538.2
1431.3 | 1212.3 | 680.5 | 603.5 | 617.8 | 664.1 | 536.7
1432.3 | 1213.3 | 679.5 | 603.7 | 619.2 | 663 | 536.1
1433.3 | 1214.3 | 680.9 | 615.6 | 633.8 | 665.7 | 539.3
1434.3 | 1215.3 | 686.2 | 634.7 | 655 | 674.4 | 542.5
1435.3 | 1216.3 | 692.7 | 657.3 | 660.8 | 684.9 | 543.9
1436.3 | 1217.3 | 696.4 | 644.8 | 654.1 | 689.7 | 544.7
1437.3 | 1218.3 | 697.9 | 646 | 653.4 | 693.2 | 545.6
1438.3 | 1219.3 | 702 | 661.1 | 658.5 | 698.9 | 547.3
1439.3 | 1220.3 | 708.8 | 683.9 | 672.4 | 706.9 | 550.3
1440.3 | 1221.3 | 712.5 | 700.3 | 682.9 | 711 | 552.5
1441.3 | 1222.3 | 719.7 | 716 | 698.9 | 720.8 | 555.9
1442.3 | 1223.3 | 728 | 727 | 721.8 | 733.7 | 560.2
1443.3 | 1224.3 | 733 | 714.1 | 732.6 | 742.5 | 563.9
1444.3 | 1225.3 | 738.4 | 717.1 | 747.4 | 751.8 | 570.8
1445.3 | 1226.3 | 744.1 | 731.1 | 747.7 | 760.6 | 574
1446.3 | 1227.3 | 747 | 734.4 | 749.5 | 765.7 | 575.6
1447.3 | 1228.3 | 749.4 | 732.3 | 749.3 | 767.7 | 577.1
1448.3 | 1229.3 | 749.6 | 717.5 | 731.9 | 767.2 | 575.5
1449.3 | 1230.3 | 748.6 | 702.4 | 717.3 | 766.9 | 574.6
1450.3 | 1231.3 | 745.9 | 679.6 | 706.4 | 763.2 | 573.3
1451.3 | 1232.3 | 744.3 | 672.1 | 699.7 | 761.7 | 572.3
1452.3 | 1233.3 | 747.7 | 678.7 | 713.8 | 762.4 | 575.2
1453.3 | 1234.3 | 749.1 | 673.8 | 713.7 | 761.5 | 575.2
1454.3 | 1235.3 | 748.4 | 673.9 | 707.6 | 758.6 | 574.3
1455.3 | 1236.3 | 747.2 | 658.6 | 694.4 | 755 | 572.9
1456.3 | 1237.3 | 745 | 654.2 | 690.3 | 751.1 | 571.1
1457.3 | 1238.3 | 742.6 | 652.9 | 681.3 | 746.4 | 569.9
1458.3 | 1239.3 | 741.5 | 652.2 | 681.6 | 745.7 | 569.4
1459.3 | 1240.3 | 742.9 | 668.6 | 674.9 | 746.7 | 569.7
1460.3 | 1241.3 | 743.2 | 668.3 | 665.8 | 744.7 | 569
1461.3 | 1242.3 | 740.2 | 659.7 | 654 | 739 | 567.2
1462.3 | 1243.3 | 738.4 | 663.8 | 649.4 | 735.9 | 565.8
1463.3 | 1244.3 | 738.1 | 649 | 636.1 | 736.6 | 564
1464.3 | 1245.3 | 733.9 | 635.2 | 630.5 | 732.3 | 563
1465.3 | 1246.3 | 730.1 | 620.4 | 616.5 | 726.2 | 561.5
1466.3 | 1247.3 | 727.3 | 615.4 | 609 | 721.3 | 560.4
1467.3 | 1248.3 | 723.5 | 601.4 | 603.7 | 715.3 | 560.2
1468.3 | 1249.3 | 720.2 | 597.1 | 618.5 | 712 | 560
1469.3 | 1250.3 | 718.6 | 614.6 | 630.7 | 709.2 | 561.6
1470.3 | 1251.3 | 722.8 | 627.3 | 632.9 | 714 | 562.9
1471.3 | 1252.3 | 726.5 | 635.6 | 639.8 | 716.7 | 564.5
1472.3 | 1253.3 | 732.5 | 669.2 | 660.8 | 725.2 | 568.1
1473.3 | 1254.3 | 740.6 | 684.9 | 671.8 | 738.2 | 570.5
1474.3 | 1255.3 | 746.9 | 707.3 | 671.9 | 743.7 | 571.2
1475.3 | 1256.3 | 748 | 716.5 | 660.6 | 742.1 | 570.5
1476.3 | 1257.3 | 749.2 | 731.3 | 673.8 | 743.2 | 570
1477.3 | 1258.3 | 754 | 753.1 | 710.3 | 749.1 | 578.7
1478.3 | 1259.3 | 757.2 | 754 | 718.4 | 752.4 | 581.1
1479.3 | 1260.3 | 760.4 | 754.4 | 730.4 | 757.6 | 584
1480.3 | 1261.3 | 762.3 | 741.3 | 714.1 | 761.4 | 583.8
1481.3 | 1262.3 | 761.8 | 733 | 696.7 | 761.9 | 582.6
1482.3 | 1263.3 | 759.9 | 726 | 683.6 | 760.1 | 581.1
1483.3 | 1264.3 | 758.6 | 715.4 | 676.2 | 755.3 | 580.8
1484.3 | 1265.3 | 755.5 | 714.6 | 665.1 | 748.2 | 578.7
1485.3 | 1266.3 | 755 | 726 | 671.7 | 745.1 | 579.4
1486.3 | 1267.3 | 756 | 728.4 | 680.8 | 744 | 582.2
1487.3 | 1268.3 | 756.8 | 729.2 | 692.6 | 742.5 | 582.9
1488.3 | 1269.3 | 757.7 | 739.4 | 701.7 | 740.1 | 585
1489.3 | 1270.3 | 759.4 | 752.2 | 707.8 | 741.1 | 586
1490.3 | 1271.3 | 761.7 | 762.9 | 722.7 | 744.9 | 588.1
1491.3 | 1272.3 | 765.4 | 768.6 | 728.1 | 750.3 | 589.5
1492.3 | 1273.3 | 772.1 | 772.8 | 748.7 | 761.2 | 594.3
1493.3 | 1274.3 | 779.2 | 784.1 | 764.2 | 769.8 | 597.6
1494.3 | 1275.3 | 781.8 | 776.8 | 762.9 | 772.6 | 598.6
1495.3 | 1276.3 | 785.1 | 792.8 | 771 | 778.3 | 600.1
1496.3 | 1277.3 | 784.7 | 794.8 | 767.9 | 776.3 | 603.8
1497.3 | 1278.3 | 784.5 | 791.9 | 770.2 | 773.1 | 606.2
1498.3 | 1279.3 | 785.2 | 773.2 | 761.9 | 774.1 | 605.4
1499.3 | 1280.3 | 781.3 | 747.7 | 732.4 | 768.8 | 602.6
1500.3 | 1281.3 | 776.6 | 726.3 | 708.4 | 763.8 | 599.4
1501.3 | 1282.3 | 778.7 | 734.4 | 714.1 | 766.3 | 599.9
1502.3 | 1283.3 | 783 | 761.7 | 736 | 770.3 | 606
1503.3 | 1284.3 | 786.8 | 776.1 | 749.4 | 775.2 | 612.9
1504.3 | 1285.3 | 789.8 | 785.7 | 760.8 | 779.4 | 616.9
1505.3 | 1286.3 | 788 | 772.5 | 758.9 | 775.8 | 618.1
1506.3 | 1287.3 | 789.4 | 777.3 | 771.1 | 780.8 | 621.9
1507.3 | 1288.3 | 792.9 | 791.7 | 781.9 | 786.2 | 627.7
1508.3 | 1289.3 | 793.5 | 798.8 | 777 | 784 | 631.5
1509.3 | 1290.3 | 798.4 | 812.7 | 778.7 | 786.2 | 634.7
1510.3 | 1291.3 | 805 | 833.2 | 773.5 | 794.4 | 637.2
1511.3 | 1292.3 | 809.7 | 817.4 | 759.9 | 801.6 | 635.2
1512.3 | 1293.3 | 810.4 | 802.7 | 750.9 | 801.3 | 634.3
1513.3 | 1294.3 | 811.4 | 782 | 738.5 | 802.6 | 633.6
1514.3 | 1295.3 | 807.1 | 753.2 | 722.2 | 795.5 | 630.5
1515.3 | 1296.3 | 801.6 | 726.3 | 718.7 | 788 | 627.5
1516.3 | 1297.3 | 796.5 | 707.7 | 717.5 | 781.6 | 626.6
1517.3 | 1298.3 | 793 | 697.4 | 717.4 | 777.7 | 625.8
1518.3 | 1299.3 | 786.8 | 681.2 | 689.1 | 770.8 | 622.4
1519.3 | 1300.3 | 781.6 | 663.4 | 674.4 | 766 | 619.4
1520.3 | 1301.3 | 779.5 | 673.5 | 663.4 | 765.7 | 617.5
1521.3 | 1302.3 | 778.9 | 679.1 | 670.9 | 764.9 | 617.1
1522.3 | 1303.3 | 782.9 | 711.4 | 698.2 | 769.6 | 621.4
1523.3 | 1304.3 | 784.8 | 731.1 | 721.5 | 772 | 624.2
1524.3 | 1305.3 | 786.7 | 744.4 | 740.1 | 775.9 | 626.4
1525.3 | 1306.3 | 788 | 753.7 | 748.2 | 776.5 | 626.5
1526.3 | 1307.3 | 789.4 | 747.3 | 736.7 | 778.1 | 626.4
1527.3 | 1308.3 | 790.9 | 744.9 | 740.8 | 778.6 | 626.5
1528.3 | 1309.3 | 794.2 | 753 | 738 | 781.2 | 627.9
1529.3 | 1310.3 | 791.4 | 740.2 | 721.1 | 776.7 | 625.9
1530.3 | 1311.3 | 788.7 | 744.7 | 717.1 | 770.3 | 624.3
1531.3 | 1312.3 | 788.9 | 747.7 | 732.4 | 769.8 | 626.9
1532.3 | 1313.3 | 790.4 | 747.6 | 740.2 | 773.5 | 629.3
1533.3 | 1314.3 | 788.6 | 725.1 | 730.9 | 770 | 627
1534.3 | 1315.3 | 785.2 | 714.8 | 714 | 766.3 | 624.9
1535.3 | 1316.3 | 783.1 | 703.8 | 707.5 | 764.5 | 624.4
1536.3 | 1317.3 | 783.1 | 706.1 | 698.8 | 765.1 | 623.4
1537.3 | 1318.3 | 778.1 | 682.7 | 684.5 | 759.2 | 620.7
1538.3 | 1319.3 | 773.3 | 660.3 | 667.9 | 754.6 | 619.1
1539.3 | 1320.3 | 768.4 | 635.4 | 655.6 | 748.8 | 617.1
1540.3 | 1321.3 | 765.4 | 628.3 | 656 | 743.5 | 615.2
1541.3 | 1322.3 | 763.7 | 628.4 | 656.5 | 742.2 | 614.8
1542.3 | 1323.3 | 765.1 | 647 | 659 | 744.9 | 613.8
1543.3 | 1324.3 | 765.7 | 654 | 645.4 | 745.4 | 611.4
1544.3 | 1325.3 | 766.8 | 666.7 | 651.3 | 748.2 | 610.8
1545.3 | 1326.3 | 765.4 | 672.4 | 647.5 | 746.8 | 609.7
1546.3 | 1327.3 | 765.5 | 685.7 | 661.9 | 746.8 | 610
1547.3 | 1328.3 | 767 | 678.9 | 666.4 | 750.9 | 609.8
1548.3 | 1329.3 | 766.2 | 670.8 | 665.7 | 752.5 | 609.6
1549.3 | 1330.3 | 766.2 | 671.6 | 676 | 753.1 | 609.4
1550.3 | 1331.3 | 768.4 | 674.6 | 677.9 | 757.5 | 611.5
1551.3 | 1332.3 | 766.6 | 663.8 | 668.2 | 756.9 | 608.7
1552.3 | 1333.3 | 763.4 | 659.6 | 649.3 | 752.9 | 605.7
1553.3 | 1334.3 | 756.6 | 638 | 633 | 745.7 | 603
1554.3 | 1335.3 | 752.3 | 624.5 | 623.8 | 741.4 | 600.9
1555.3 | 1336.3 | 750.1 | 622.8 | 616.6 | 739.6 | 599.1
1556.3 | 1337.3 | 745.2 | 612.8 | 611.2 | 734.2 | 597.1
1557.3 | 1338.3 | 741 | 609.2 | 610 | 728.5 | 594.9
1558.3 | 1339.3 | 738.2 | 607.1 | 618.3 | 727.3 | 594.7
1559.3 | 1340.3 | 738.9 | 615.4 | 617.3 | 729.4 | 593.1
1560.3 | 1341.3 | 736.8 | 613.4 | 615.7 | 727.6 | 591.1
1561.3 | 1342.3 | 735 | 609.1 | 617.7 | 725.7 | 590.7
1562.3 | 1343.3 | 735 | 613.6 | 627 | 725.3 | 589.8
1563.3 | 1344.3 | 739.8 | 632.5 | 632 | 732.4 | 590.8
1564.3 | 1345.3 | 741.5 | 647.2 | 640.9 | 733.3 | 590.5
1565.3 | 1346.3 | 742.5 | 643.6 | 637.8 | 733.7 | 589.7
1566.3 | 1347.3 | 742.8 | 663.5 | 640.8 | 732.1 | 588.6
1567.3 | 1348.3 | 746 | 668.7 | 652.7 | 737.9 | 590.2
1568.3 | 1349.3 | 748.9 | 665.8 | 669 | 742 | 591.5
1569.3 | 1350.3 | 754.3 | 688.8 | 686.1 | 749.1 | 594.7
1570.3 | 1351.3 | 757.8 | 691.4 | 692.2 | 754.6 | 595.6
1571.3 | 1352.3 | 757.9 | 682.1 | 691.5 | 756.1 | 594.8
1572.3 | 1353.3 | 760.8 | 693 | 707.9 | 760.7 | 598.4
1573.3 | 1354.3 | 761.8 | 693.7 | 707.4 | 761 | 600.1
1574.3 | 1355.3 | 762.2 | 692.6 | 712.2 | 761.4 | 600.6
1575.3 | 1356.3 | 765 | 692.9 | 725.8 | 767 | 603.2
1576.3 | 1357.3 | 769 | 702.5 | 730.2 | 773.1 | 605.3
1577.3 | 1358.3 | 771.5 | 709.6 | 736.4 | 773.7 | 606.5
1578.3 | 1359.3 | 775.3 | 727.9 | 744.3 | 779.9 | 612
1579.3 | 1360.3 | 777.9 | 725.9 | 742.9 | 782.5 | 614.4
1580.3 | 1361.3 | 779 | 725.2 | 736.7 | 782.4 | 614.2
1581.3 | 1362.3 | 782.4 | 732.9 | 747.6 | 787.2 | 615.5
1582.3 | 1363.3 | 786.7 | 732.5 | 757.4 | 791.4 | 617.8
1583.3 | 1364.3 | 788 | 724.5 | 755.1 | 791.3 | 618.7
1584.3 | 1365.3 | 787.7 | 714.6 | 751.7 | 789.3 | 618.1
1585.3 | 1366.3 | 786.6 | 721 | 746.1 | 787.7 | 617.8
1586.3 | 1367.3 | 784.7 | 715.8 | 741.5 | 783.7 | 618
1587.3 | 1368.3 | 783.3 | 711.8 | 725.6 | 782.8 | 615.7
1588.3 | 1369.3 | 782.5 | 705 | 727.3 | 781.1 | 616
1589.3 | 1370.3 | 780.7 | 693.1 | 722.5 | 778.4 | 613.9
1590.3 | 1371.3 | 781.9 | 703.2 | 727.5 | 780.4 | 614.2
1591.3 | 1372.3 | 781.7 | 697.3 | 721.9 | 780.1 | 613.6
1592.3 | 1373.3 | 780.8 | 701.3 | 711.3 | 776.7 | 612.7
1593.3 | 1374.3 | 779.1 | 715.7 | 704.2 | 772 | 611.7
1594.3 | 1375.3 | 777.9 | 698.6 | 697.6 | 769.6 | 611.2
1595.3 | 1376.3 | 778.8 | 699.2 | 693.4 | 769.4 | 611.4
1596.3 | 1377.3 | 777.9 | 698 | 689.5 | 766.3 | 609.5
1597.3 | 1378.3 | 779.1 | 707 | 703.7 | 767.4 | 611.6
1598.3 | 1379.3 | 778.3 | 700.9 | 701.4 | 766.5 | 611.7
1599.3 | 1380.3 | 776.6 | 705.9 | 702.7 | 765.6 | 610.6
1600.3 | 1381.3 | 774.9 | 694.2 | 696.1 | 766.5 | 608.7
1601.3 | 1382.3 | 775 | 695.5 | 693.1 | 767.4 | 607.5
1602.3 | 1383.3 | 772.9 | 700.1 | 686.2 | 762.3 | 605.1
1603.3 | 1384.3 | 772.2 | 712 | 681.7 | 759.8 | 604.7
1604.3 | 1385.3 | 769.5 | 707.5 | 676.4 | 756.5 | 603.5
1605.3 | 1386.3 | 770.2 | 703.1 | 678 | 757.1 | 602.4
1606.3 | 1387.3 | 770.1 | 714.4 | 676.2 | 755.4 | 601.4
1607.3 | 1388.3 | 770.4 | 708.9 | 676.7 | 755.2 | 600.2
1608.3 | 1389.3 | 767.6 | 692.6 | 669.8 | 751.2 | 599.2
1609.3 | 1390.3 | 770 | 709.5 | 682 | 756.3 | 600
1610.3 | 1391.3 | 771.9 | 722.5 | 691.1 | 760.3 | 601.1
1611.3 | 1392.3 | 773.1 | 732.1 | 688.1 | 759.2 | 600.7
1612.3 | 1393.3 | 775.3 | 732 | 699.7 | 762.9 | 602.1
1613.3 | 1394.3 | 781.5 | 742.2 | 720.5 | 775.8 | 605.9
1614.3 | 1395.3 | 788.6 | 771.1 | 744.7 | 783 | 610.2
1615.3 | 1396.3 | 795.6 | 784.9 | 750.2 | 789.2 | 613.6
1616.3 | 1397.3 | 799.8 | 779.8 | 748 | 794.7 | 616.5
1617.3 | 1398.3 | 800.8 | 773 | 755.5 | 797.8 | 617.6
1618.3 | 1399.3 | 803.7 | 771 | 766.4 | 802.1 | 621.5
1619.3 | 1400.3 | 806.8 | 775.4 | 774.4 | 808.1 | 624.9
1620.3 | 1401.3 | 806.4 | 757.4 | 763.6 | 808.4 | 625.6
1621.3 | 1402.3 | 804.6 | 743.2 | 750.1 | 805.8 | 624.1
1622.3 | 1403.3 | 803 | 740.2 | 752.4 | 803 | 625
1623.3 | 1404.3 | 802.8 | 737.9 | 753.4 | 800.4 | 625.3
1624.3 | 1405.3 | 804 | 762 | 769.6 | 801.6 | 628.1
1625.3 | 1406.3 | 805.4 | 773.7 | 772.4 | 801.3 | 630.1
1626.3 | 1407.3 | 806.9 | 770.5 | 763.3 | 804.1 | 631.2
1627.3 | 1408.3 | 805.3 | 754.1 | 753.8 | 802.7 | 629.2
1628.3 | 1409.3 | 805.5 | 765.2 | 755.8 | 803.6 | 629.6
1629.3 | 1410.3 | 805.2 | 759.6 | 751.2 | 804.1 | 629.2
1630.3 | 1411.3 | 803.4 | 747.6 | 741.4 | 800.5 | 627
1631.3 | 1412.3 | 799.8 | 739.4 | 727.6 | 794.8 | 624.8
1632.3 | 1413.3 | 800.6 | 747.2 | 737.3 | 797.8 | 625.3
1633.3 | 1414.3 | 806.1 | 782 | 752.8 | 804.6 | 629.5
1634.3 | 1415.3 | 812.7 | 803.9 | 769.2 | 810.5 | 635
1635.3 | 1416.3 | 817.2 | 812.1 | 782.5 | 812.9 | 639.2
1636.3 | 1417.3 | 819.9 | 820.7 | 781.7 | 817.3 | 642
1637.3 | 1418.3 | 818 | 809.2 | 766.8 | 816.2 | 640.6
1638.3 | 1419.3 | 817.3 | 806.3 | 756.6 | 815.6 | 639.4
1639.3 | 1420.3 | 817 | 790.5 | 745.5 | 812.7 | 638.6
1640.3 | 1421.3 | 816.3 | 780.5 | 739 | 811.5 | 637.4
1641.3 | 1422.3 | 813.9 | 760.2 | 720 | 808.1 | 634.5
1642.3 | 1423.3 | 806.6 | 726.4 | 707.5 | 795.9 | 630.8
1643.3 | 1424.3 | 799.1 | 703.9 | 686.8 | 785.8 | 627.2
1644.3 | 1425.3 | 793.4 | 692.3 | 678 | 777.9 | 624.9
1645.3 | 1426.3 | 789.5 | 674.7 | 678.5 | 774.5 | 623.6
1646.3 | 1427.3 | 786.1 | 664.5 | 673.9 | 769.2 | 622.9
1647.3 | 1428.3 | 779.3 | 662.4 | 657.3 | 759.8 | 619.5
1648.3 | 1429.3 | 774.6 | 661.5 | 655.7 | 753.9 | 618.6
1649.3 | 1430.3 | 771.7 | 655.6 | 646.6 | 751.4 | 616.5
1650.3 | 1431.3 | 768.8 | 653.9 | 648 | 747.9 | 615.1
1651.3 | 1432.3 | 768.4 | 660 | 649.6 | 749.3 | 614.8
1652.3 | 1433.3 | 766.2 | 666.1 | 653.8 | 744.9 | 612.4
1653.3 | 1434.3 | 769.8 | 695.5 | 681.2 | 747.9 | 614.2
1654.3 | 1435.3 | 773.2 | 730.1 | 703.6 | 751 | 617.8
1655.3 | 1436.3 | 778.8 | 745.5 | 716.3 | 759.1 | 619.8
1656.3 | 1437.3 | 780.2 | 760.2 | 720.9 | 758.9 | 620.8
1657.3 | 1438.3 | 782.2 | 754.3 | 730.6 | 762.4 | 622.5
1658.3 | 1439.3 | 779.9 | 733.6 | 710.5 | 760.4 | 622.1
1659.3 | 1440.3 | 778 | 706.3 | 694 | 759.9 | 619.9
1660.3 | 1441.3 | 775.4 | 703 | 684.3 | 756.1 | 616.8
1661.3 | 1442.3 | 770.4 | 690.5 | 664.9 | 750.6 | 613.3
1662.3 | 1443.3 | 766.8 | 682.5 | 659.5 | 746.3 | 611.3
1663.3 | 1444.3 | 766.7 | 703.9 | 672.4 | 744.8 | 611.7
1664.3 | 1445.3 | 770.7 | 727.3 | 691.3 | 749.7 | 614.3
1665.3 | 1446.3 | 770.4 | 710.6 | 677.1 | 748.6 | 612.4
1666.3 | 1447.3 | 764.4 | 689.3 | 659.1 | 742.5 | 608.8
1667.3 | 1448.3 | 758.8 | 678.2 | 643.1 | 736.3 | 606.8
1668.3 | 1449.3 | 751.9 | 649 | 620.8 | 729.5 | 603.4
1669.3 | 1450.3 | 743.5 | 623.7 | 605.9 | 719.5 | 599.7
1670.3 | 1451.3 | 737.5 | 623.5 | 606.5 | 710.8 | 597.5
1671.3 | 1452.3 | 738.7 | 653.7 | 626.4 | 711.8 | 598.3
1672.3 | 1453.3 | 739.6 | 662.1 | 634.7 | 710.9 | 598.5
1673.3 | 1454.3 | 739.8 | 677.4 | 654.5 | 710.3 | 600.1
1674.3 | 1455.3 | 743.1 | 700.3 | 674.1 | 716.5 | 603.6
1675.3 | 1456.3 | 745.9 | 711.9 | 690.5 | 719.8 | 604.8
1676.3 | 1457.3 | 745.4 | 700.9 | 684.8 | 719.8 | 602.5
1677.3 | 1458.3 | 742.8 | 698.5 | 674.6 | 715.4 | 601.3
1678.3 | 1459.3 | 741 | 691.5 | 664.3 | 713.7 | 599
1679.3 | 1460.3 | 737.1 | 670.8 | 649 | 710.5 | 596.8
1680.3 | 1461.3 | 737.1 | 664.7 | 654.9 | 711.3 | 595.5
1681.3 | 1462.3 | 737.9 | 666.3 | 656.2 | 711.3 | 594.5
1682.3 | 1463.3 | 737 | 657.6 | 648 | 711.8 | 593.5
1683.3 | 1464.3 | 740.9 | 678.6 | 662.1 | 718.9 | 595.2
1684.3 | 1465.3 | 745.7 | 699.2 | 684.2 | 727.4 | 598.9
1685.3 | 1466.3 | 749.4 | 698.2 | 702.6 | 735.2 | 601.4
1686.3 | 1467.3 | 749.2 | 682.3 | 707.9 | 734 | 602.5
1687.3 | 1468.3 | 748.1 | 675.9 | 696.6 | 738.4 | 601.8
1688.3 | 1469.3 | 748.4 | 670.5 | 698.5 | 740.6 | 602.1
1689.3 | 1470.3 | 746.5 | 675.2 | 693.3 | 736.4 | 600.7
1690.3 | 1471.3 | 744 | 676.7 | 680.3 | 732.3 | 598.8
1691.3 | 1472.3 | 740.4 | 677.4 | 669.9 | 725.5 | 596
1692.3 | 1473.3 | 743.2 | 691.3 | 683.4 | 728.5 | 598.4
1693.3 | 1474.3 | 749.2 | 709 | 690 | 734.7 | 599.3
1694.3 | 1475.3 | 752.3 | 708.8 | 694.6 | 737 | 600.3
1695.3 | 1476.3 | 754.1 | 696.2 | 697.5 | 739.8 | 600.8
1696.3 | 1477.3 | 756.1 | 705.3 | 690 | 742.4 | 600.2
1697.3 | 1478.3 | 757.7 | 714.9 | 688.8 | 743.3 | 600.3
1698.3 | 1479.3 | 753.6 | 695.3 | 676.3 | 738.4 | 598
1699.3 | 1480.3 | 749.8 | 679.8 | 663.1 | 735.6 | 595.5
1700.3 | 1481.3 | 743.9 | 657.7 | 646.3 | 729.4 | 593.4
1701.3 | 1482.3 | 741.5 | 654.6 | 652.4 | 726.6 | 593.1
1702.3 | 1483.3 | 739.7 | 669.9 | 659.3 | 722.9 | 592.4
1703.3 | 1484.3 | 737.9 | 678.5 | 663.4 | 721.1 | 592.6
1704.3 | 1485.3 | 735.4 | 674.9 | 659.1 | 717.4 | 591.1
1705.3 | 1486.3 | 733.8 | 667.7 | 654.3 | 714.2 | 589.7
1706.3 | 1487.3 | 734.3 | 658.8 | 657.1 | 712.8 | 589.5
1707.3 | 1488.3 | 738.2 | 671.5 | 669.6 | 715.4 | 590.6
1708.3 | 1489.3 | 737.5 | 666.8 | 651.3 | 714.7 | 588.8
1709.3 | 1490.3 | 736.8 | 673.7 | 641.2 | 714.8 | 587.9
1710.3 | 1491.3 | 738.1 | 695.9 | 645.9 | 712.5 | 588.9
1711.3 | 1492.3 | 737.6 | 691.2 | 649.4 | 710.9 | 587.5
1712.3 | 1493.3 | 736.8 | 694.3 | 658.6 | 705.5 | 588
1713.3 | 1494.3 | 736.1 | 688.7 | 653.6 | 705.1 | 587.2
1714.3 | 1495.3 | 737.4 | 679.3 | 647.2 | 709.2 | 586.5
1715.3 | 1496.3 | 738.2 | 676.3 | 635.3 | 711.2 | 584.9
1716.3 | 1497.3 | 736.8 | 680 | 628.7 | 709.8 | 583.3
1717.3 | 1498.3 | 735.5 | 670.2 | 622.3 | 708.6 | 582.8
1718.3 | 1499.3 | 735.7 | 675.1 | 627.9 | 710.2 | 583.5
1719.3 | 1500.3 | 732.6 | 667.8 | 620.9 | 708.3 | 581
1720.3 | 1501.3 | 728.8 | 657.8 | 610.9 | 704.8 | 578.7
1721.3 | 1502.3 | 724.7 | 645.9 | 596.8 | 699.8 | 576.3
1722.3 | 1503.3 | 718.5 | 625.7 | 582.9 | 694.5 | 573.9
1723.3 | 1504.3 | 715.4 | 616 | 573.9 | 692.8 | 572.8
1724.3 | 1505.3 | 711.5 | 625.9 | 575.4 | 687.9 | 570.6
1725.3 | 1506.3 | 711.7 | 613.4 | 586.4 | 689.8 | 570.5
1726.3 | 1507.3 | 710.3 | 609.3 | 589.7 | 689.9 | 569.4
1727.3 | 1508.3 | 711.7 | 625 | 603.1 | 691.5 | 570.4
1728.3 | 1509.3 | 708.5 | 607.2 | 590.7 | 689.6 | 568.1
1729.3 | 1510.3 | 704.9 | 594.7 | 579.7 | 686.1 | 565.6
1730.3 | 1511.3 | 701.4 | 589.5 | 576.9 | 681.4 | 564.1
1731.3 | 1512.3 | 701.9 | 586.6 | 584 | 681.6 | 564.9
1732.3 | 1513.3 | 700.9 | 599.2 | 584.2 | 678.7 | 564.7
1733.3 | 1514.3 | 697.3 | 585.5 | 573.2 | 673.8 | 563
1734.3 | 1515.3 | 690.5 | 561.1 | 561.8 | 668.3 | 560
1735.3 | 1516.3 | 685.4 | 552.4 | 568.2 | 661.4 | 558.6
1736.3 | 1517.3 | 684.6 | 569.5 | 579.8 | 661.4 | 559.1
1737.3 | 1518.3 | 686.3 | 589.7 | 589.4 | 664.2 | 558.3
1738.3 | 1519.3 | 694.2 | 634.2 | 622.1 | 676.3 | 561
1739.3 | 1520.3 | 699.4 | 660.6 | 632.9 | 682.8 | 564.3
1740.3 | 1521.3 | 701.7 | 670.4 | 634 | 680.7 | 564.1
1741.3 | 1522.3 | 701.9 | 678.4 | 620.6 | 677.6 | 561.9
1742.3 | 1523.3 | 700.6 | 688.2 | 607.9 | 673.9 | 559.9
1743.3 | 1524.3 | 702.9 | 708.6 | 616.1 | 674.9 | 560
1744.3 | 1525.3 | 710 | 732 | 627 | 683.7 | 561.5
1745.3 | 1526.3 | 712.8 | 733.6 | 631.8 | 683 | 561.8
1746.3 | 1527.3 | 711.9 | 720 | 623.4 | 680.9 | 561.7
1747.3 | 1528.3 | 706.7 | 685.9 | 603.8 | 676.8 | 559.8
1748.3 | 1529.3 | 700.8 | 655.7 | 594.5 | 670.8 | 557.9
1749.3 | 1530.3 | 701.6 | 653.6 | 592.5 | 672.4 | 558.6
1750.3 | 1531.3 | 705.1 | 657.2 | 603.5 | 675.4 | 559.9
1751.3 | 1532.3 | 708.8 | 661.3 | 607.6 | 679.3 | 560.7
1752.3 | 1533.3 | 706.2 | 647.3 | 597.6 | 676.3 | 558.7
1753.3 | 1534.3 | 704.1 | 658 | 601 | 671 | 558.7
1754.3 | 1535.3 | 699.2 | 635.5 | 589.8 | 668.9 | 556.3
1755.3 | 1536.3 | 698.9 | 636.2 | 590.1 | 667.7 | 555
1756.3 | 1537.3 | 704.4 | 663.6 | 618.2 | 675.6 | 557.3
1757.3 | 1538.3 | 712.1 | 687.9 | 651.7 | 689.4 | 561.3
1758.3 | 1539.3 | 719 | 687.1 | 665.8 | 701.5 | 564
1759.3 | 1540.3 | 718.7 | 659.8 | 652 | 699.9 | 561.3
1760.3 | 1541.3 | 717.2 | 646.8 | 651.8 | 698.8 | 559.9
1761.3 | 1542.3 | 715.3 | 642 | 652.9 | 697.8 | 559.3
1762.3 | 1543.3 | 715.9 | 655.3 | 665.2 | 701.6 | 560.9
1763.3 | 1544.3 | 718 | 661.3 | 666.7 | 704.3 | 559.9
1764.3 | 1545.3 | 717.8 | 656.9 | 669.9 | 702.7 | 559.6
1765.3 | 1546.3 | 718.7 | 660.5 | 651 | 703.1 | 559.2
1766.3 | 1547.3 | 715.1 | 639.9 | 633.1 | 698 | 557
1767.3 | 1548.3 | 710.2 | 612.1 | 617.6 | 692.2 | 555.5
1768.3 | 1549.3 | 705.6 | 595 | 602.9 | 685.8 | 553.4
1769.3 | 1550.3 | 706.1 | 601.3 | 606.7 | 684.1 | 552.8
1770.3 | 1551.3 | 709.3 | 600.6 | 599.3 | 690.1 | 551.9
1771.3 | 1552.3 | 706.6 | 595.8 | 590.3 | 688.2 | 550.7
1772.3 | 1553.3 | 703.9 | 584.8 | 597.1 | 684.6 | 550.3
1773.3 | 1554.3 | 705 | 590.8 | 597.9 | 686.7 | 549.5
1774.3 | 1555.3 | 703.4 | 585 | 586.9 | 684.7 | 548.5
1775.3 | 1556.3 | 701.4 | 587.9 | 578.2 | 682.3 | 547
1776.3 | 1557.3 | 697.1 | 578.3 | 570.6 | 678.1 | 545.2
1777.3 | 1558.3 | 693.7 | 574.8 | 561 | 673.7 | 543.2
1778.3 | 1559.3 | 691.2 | 566.9 | 549.9 | 670.7 | 541.3
1779.3 | 1560.3 | 687.9 | 566.8 | 552 | 666.8 | 540.1
1780.3 | 1561.3 | 688.1 | 594.5 | 570.7 | 665.1 | 540.8
1781.3 | 1562.3 | 692.6 | 632.9 | 607.7 | 667.8 | 544.2
1782.3 | 1563.3 | 696.6 | 641 | 627.2 | 669.8 | 547.4
1783.3 | 1564.3 | 697.9 | 635.5 | 618.7 | 671.6 | 547
1784.3 | 1565.3 | 696.5 | 631.1 | 604.4 | 669.4 | 545.4
1785.3 | 1566.3 | 693.7 | 623.9 | 596.4 | 666.1 | 544.5
1786.3 | 1567.3 | 694.1 | 623.8 | 612.8 | 664.5 | 545.8
1787.3 | 1568.3 | 698.3 | 624.2 | 627 | 668.7 | 549.1
1788.3 | 1569.3 | 699.3 | 629.8 | 628.4 | 670.7 | 547.8
1789.3 | 1570.3 | 697.2 | 624.2 | 615.1 | 667.7 | 546.4
1790.3 | 1571.3 | 692.7 | 616.5 | 600.9 | 664.6 | 544.5
1791.3 | 1572.3 | 693.3 | 627.9 | 605 | 665.6 | 544.8
1792.3 | 1573.3 | 697.8 | 631.6 | 604.5 | 670.6 | 544.8
1793.3 | 1574.3 | 700.5 | 649.2 | 604.1 | 673.5 | 545.1
1794.3 | 1575.3 | 702.1 | 651.2 | 611.8 | 676.3 | 545.5
1795.3 | 1576.3 | 700.7 | 645.4 | 611 | 674.2 | 545.1
1796.3 | 1577.3 | 697 | 633.4 | 602.8 | 670.4 | 543.3
1797.3 | 1578.3 | 696.6 | 627.5 | 615.4 | 669.4 | 544.2
1798.3 | 1579.3 | 698.7 | 643 | 630.1 | 673 | 546.2
1799.3 | 1580.3 | 702.7 | 656.7 | 648.1 | 677.8 | 548.4
1800.3 | 1581.3 | 706.7 | 659.9 | 659.8 | 685.5 | 549.6
1801.3 | 1582.3 | 707.7 | 662.2 | 652 | 684.7 | 549.7
1802.3 | 1583.3 | 708.4 | 667.5 | 649.9 | 684.2 | 550
1803.3 | 1584.3 | 714.9 | 698.6 | 652.2 | 693.7 | 550.9
1804.3 | 1585.3 | 716.7 | 704.1 | 640.3 | 693.2 | 549.7
1805.3 | 1586.3 | 715.6 | 698.9 | 632.6 | 690.7 | 548.2
1806.3 | 1587.3 | 717 | 702.8 | 644 | 693 | 549.2
1807.3 | 1588.3 | 719.4 | 698.8 | 662.7 | 696.4 | 551.7
1808.3 | 1589.3 | 722.8 | 713.2 | 667.8 | 698.6 | 551.6
1809.3 | 1590.3 | 720.7 | 707 | 666.9 | 696 | 553.6
1810.3 | 1591.3 | 721.5 | 689.8 | 671.1 | 701.3 | 554.9
1811.3 | 1592.3 | 723.1 | 673.9 | 670.5 | 708.5 | 555.2
1812.3 | 1593.3 | 725.4 | 682.1 | 667.3 | 713.4 | 554.3
1813.3 | 1594.3 | 729.6 | 695.8 | 653.5 | 721.7 | 554.6
1814.3 | 1595.3 | 731.4 | 689.2 | 645 | 722.6 | 554.6
1815.3 | 1596.3 | 729.1 | 677.6 | 642.8 | 720.5 | 554.2
1816.3 | 1597.3 | 726.1 | 665.2 | 639.6 | 717.7 | 554.1
1817.3 | 1598.3 | 727.1 | 659.5 | 660 | 720.1 | 555.9
1818.3 | 1599.3 | 728.7 | 646.5 | 668.4 | 724 | 556.9
1819.3 | 1600.3 | 727.7 | 638.9 | 656.4 | 724.1 | 554.6
1820.3 | 1601.3 | 729.5 | 624.6 | 645.8 | 727.4 | 553.7
1821.3 | 1602.3 | 731.7 | 631.9 | 648.4 | 729.8 | 555.2
1822.3 | 1603.3 | 734.8 | 634.3 | 649.3 | 734.4 | 554.2
1823.3 | 1604.3 | 737.2 | 652.2 | 653.1 | 736.6 | 553.3
1824.3 | 1605.3 | 742.4 | 689 | 651.2 | 742.1 | 554
1825.3 | 1606.3 | 744 | 688.8 | 652.2 | 740.1 | 553.9
1826.3 | 1607.3 | 741.8 | 680.6 | 658.9 | 733.5 | 553.7
1827.3 | 1608.3 | 743.9 | 682.5 | 662.7 | 737.7 | 555.8
1828.3 | 1609.3 | 745.1 | 689.8 | 662 | 737.3 | 555.8
1829.3 | 1610.3 | 744.4 | 696.5 | 669.5 | 732.4 | 556.3
1830.3 | 1611.3 | 749.3 | 715.9 | 676 | 738 | 558.9
1831.3 | 1612.3 | 754.1 | 718.2 | 695.5 | 741.6 | 562.6
1832.3 | 1613.3 | 761.7 | 745.4 | 711.4 | 747.2 | 567.2
1833.3 | 1614.3 | 766.8 | 750.6 | 721.4 | 755.2 | 569.7
1834.3 | 1615.3 | 772.3 | 757.1 | 720.3 | 763.1 | 571.7
1835.3 | 1616.3 | 777.7 | 762.9 | 735.5 | 768.8 | 576
1836.3 | 1617.3 | 785.4 | 777.7 | 753.8 | 776.4 | 581.7
1837.3 | 1618.3 | 791.9 | 785.7 | 758.5 | 783 | 587.9
1838.3 | 1619.3 | 797.6 | 802.3 | 765.4 | 789.6 | 592.8
1839.3 | 1620.3 | 802.1 | 799.4 | 766 | 793.2 | 595.3
1840.3 | 1621.3 | 806.7 | 815.5 | 770.6 | 798.9 | 597.3
1841.3 | 1622.3 | 813.8 | 832.9 | 779 | 807.6 | 601.6
1842.3 | 1623.3 | 816.6 | 845.7 | 782.4 | 806.1 | 605.2
1843.3 | 1624.3 | 821.5 | 838.6 | 794.1 | 813.1 | 609.3
1844.3 | 1625.3 | 826.9 | 833.8 | 799.3 | 819 | 612.5
1845.3 | 1626.3 | 828.3 | 824 | 794.9 | 817.8 | 615.5
1846.3 | 1627.3 | 828.9 | 808.8 | 790.6 | 821.7 | 616.3
1847.3 | 1628.3 | 829.2 | 799.4 | 786.9 | 826.3 | 619.3
1848.3 | 1629.3 | 829.9 | 780.3 | 773.2 | 828.7 | 617.4
1849.3 | 1630.3 | 825.4 | 752.3 | 757.3 | 826.3 | 615.8
1850.3 | 1631.3 | 823.7 | 751.2 | 747.1 | 826.3 | 614.6
1851.3 | 1632.3 | 821 | 726.3 | 723.5 | 822.4 | 611.6
1852.3 | 1633.3 | 818.7 | 722.7 | 717.2 | 817.9 | 609.9
1853.3 | 1634.3 | 818.5 | 740 | 726.1 | 814.6 | 610.6
1854.3 | 1635.3 | 824.4 | 775.1 | 752 | 822.5 | 616.9
1855.3 | 1636.3 | 831.7 | 782.9 | 767.7 | 833.4 | 620.4
1856.3 | 1637.3 | 837.5 | 789.9 | 777 | 841.4 | 621.4
1857.3 | 1638.3 | 840.8 | 781.3 | 762.8 | 843.5 | 621
1858.3 | 1639.3 | 842.1 | 786.7 | 757.3 | 843.9 | 619.8
1859.3 | 1640.3 | 844.1 | 786.9 | 755.2 | 846.3 | 620
1860.3 | 1641.3 | 848.7 | 804.7 | 774.5 | 851.3 | 622.6
1861.3 | 1642.3 | 851.4 | 796.7 | 768.1 | 854.1 | 623
1862.3 | 1643.3 | 851 | 791.5 | 763.2 | 845.7 | 623.9
1863.3 | 1644.3 | 851.4 | 806.4 | 770.1 | 841.6 | 625
1864.3 | 1645.3 | 852.3 | 808.7 | 765.2 | 842.2 | 625.9
1865.3 | 1646.3 | 854.6 | 814.4 | 758.5 | 843.8 | 625.9
1866.3 | 1647.3 | 854.8 | 805.5 | 745.5 | 843.2 | 624.8
1867.3 | 1648.3 | 852.3 | 781.8 | 746.5 | 837.3 | 624
1868.3 | 1649.3 | 849.8 | 774.7 | 737.3 | 832.6 | 622.3
1869.3 | 1650.3 | 842.9 | 751.9 | 706.7 | 823.1 | 618.6
1870.3 | 1651.3 | 835.6 | 736.2 | 685.4 | 811 | 615.2
1871.3 | 1652.3 | 836.4 | 738.8 | 691.1 | 811.5 | 614.2
1872.3 | 1653.3 | 838.5 | 753.1 | 694.5 | 814.9 | 615
1873.3 | 1654.3 | 841.5 | 757.2 | 694.2 | 820.8 | 613.9
1874.3 | 1655.3 | 845.5 | 783.3 | 712.6 | 825.2 | 617.3
1875.3 | 1656.3 | 848.3 | 802.2 | 730.4 | 826.7 | 618.1
1876.3 | 1657.3 | 847.6 | 782.6 | 724.2 | 823 | 618.2
1877.3 | 1658.3 | 841.4 | 760.8 | 703.6 | 815.7 | 615.5
1878.3 | 1659.3 | 835.4 | 749.7 | 695.7 | 809.4 | 614.3
1879.3 | 1660.3 | 828.2 | 727.6 | 685.7 | 797.5 | 612.2
1880.3 | 1661.3 | 825.4 | 731.1 | 682.3 | 793 | 611.5
1881.3 | 1662.3 | 826.6 | 751.1 | 691.3 | 791.4 | 613.8
1882.3 | 1663.3 | 825.6 | 746 | 685.9 | 791.4 | 612.2
1883.3 | 1664.3 | 825.2 | 755.2 | 700.6 | 795.5 | 612.6
1884.3 | 1665.3 | 830 | 780.2 | 711.9 | 804.4 | 614.1
1885.3 | 1666.3 | 834.5 | 791.3 | 739.4 | 813.1 | 618.5
1886.3 | 1667.3 | 839.3 | 798.4 | 764.5 | 823.4 | 623.2
1887.3 | 1668.3 | 844.1 | 789.3 | 773.8 | 834.1 | 626.3
1888.3 | 1669.3 | 848.3 | 796.8 | 788.2 | 844.1 | 630.6
1889.3 | 1670.3 | 852.9 | 821.1 | 797.6 | 850.9 | 633.5
1890.3 | 1671.3 | 859.8 | 836.7 | 805.5 | 865.6 | 638.7
1891.3 | 1672.3 | 863.4 | 842 | 798.9 | 864.4 | 640.1
1892.3 | 1673.3 | 866.9 | 843 | 803.1 | 861.5 | 642.3
1893.3 | 1674.3 | 871.1 | 853.1 | 811.8 | 865.3 | 646.8
1894.3 | 1675.3 | 875.8 | 868.4 | 809.7 | 872 | 649.5
1895.3 | 1676.3 | 879.9 | 869.4 | 805.7 | 873.3 | 651.9
1896.3 | 1677.3 | 883.3 | 876.6 | 810.4 | 877.8 | 654
1897.4 | 1678.4 | 885.7 | 869.3 | 805.5 | 880.4 | 655.5
1898.4 | 1679.4 | 889.8 | 866.5 | 792 | 887.3 | 655.1
1899.4 | 1680.4 | 893.4 | 877.3 | 788.4 | 891 | 654.7
1900.4 | 1681.4 | 896.5 | 888.8 | 796.8 | 890 | 657.1
1901.4 | 1682.4 | 899.8 | 897.1 | 805 | 895 | 661.2
1902.4 | 1683.4 | 899.3 | 881.1 | 794 | 888.8 | 662
1903.4 | 1684.4 | 894.1 | 856.6 | 779.7 | 876.3 | 658.7
1904.4 | 1685.4 | 891.7 | 834.4 | 777.2 | 872.9 | 660.5
1905.4 | 1686.4 | 891.3 | 828.4 | 783.7 | 872.9 | 662.1
1906.4 | 1687.4 | 894.8 | 841.2 | 779.8 | 880.4 | 663.2
1907.4 | 1688.4 | 898.2 | 850.6 | 783.5 | 887.1 | 665.2
1908.4 | 1689.4 | 898.3 | 843.3 | 780.2 | 885.1 | 663.4
1909.4 | 1690.4 | 894.8 | 839 | 774.8 | 877.1 | 663.3
1910.4 | 1691.4 | 893 | 844.3 | 770.9 | 870.8 | 661.9
1911.4 | 1692.4 | 892.9 | 834.7 | 756.3 | 869.7 | 658.4
1912.4 | 1693.4 | 893 | 826.1 | 752.6 | 868.1 | 658.1
1913.4 | 1694.4 | 891.7 | 815.6 | 738.2 | 866.2 | 654.6
1914.4 | 1695.4 | 890.7 | 816.8 | 728.8 | 864.6 | 652.6
1915.4 | 1696.4 | 891.4 | 823.7 | 727 | 861.2 | 651.3
1916.4 | 1697.4 | 890.7 | 818.8 | 722.9 | 858.3 | 649.3
1917.4 | 1698.4 | 889.8 | 825.9 | 723.4 | 853.9 | 648.7
1918.4 | 1699.4 | 891.9 | 837.8 | 737.1 | 859.5 | 649.3
1919.4 | 1700.4 | 894.2 | 837.8 | 741.9 | 868 | 649.8
1920.4 | 1701.4 | 896 | 838.9 | 752.7 | 871 | 650.4
1921.4 | 1702.4 | 898.5 | 818.7 | 766.1 | 876.8 | 652.5
1922.4 | 1703.4 | 898.7 | 825.1 | 772.8 | 876.9 | 655
1923.4 | 1704.4 | 898.3 | 838.7 | 786.8 | 877.9 | 658.5
1924.4 | 1705.4 | 902.7 | 845.3 | 797.3 | 886.3 | 660.7
1925.4 | 1706.4 | 906.5 | 840.8 | 808.8 | 896.1 | 664.6
1926.4 | 1707.4 | 910.6 | 850.5 | 820.2 | 905.8 | 667.1
1927.4 | 1708.4 | 913.5 | 867.5 | 828.3 | 913.6 | 672
1928.4 | 1709.4 | 915.9 | 879.6 | 829 | 913.5 | 677.1
1929.4 | 1710.4 | 918 | 881.7 | 825.3 | 913.5 | 679
1930.4 | 1711.4 | 919.4 | 867 | 822.5 | 917.8 | 681.6
1931.4 | 1712.4 | 921.1 | 875.9 | 824.8 | 917.8 | 684.5
1932.4 | 1713.4 | 922.9 | 879.6 | 827.5 | 920.6 | 687.1
1933.4 | 1714.4 | 925.2 | 873.2 | 820.2 | 926 | 687.2
1934.4 | 1715.4 | 927.6 | 866.1 | 810.8 | 927.6 | 686
1935.4 | 1716.4 | 928.8 | 874.6 | 805.8 | 938.2 | 687.3
1936.4 | 1717.4 | 929.1 | 868.3 | 794.1 | 933.5 | 686.2
1937.4 | 1718.4 | 929.3 | 876.8 | 794.3 | 921.3 | 687.2
1938.4 | 1719.4 | 926.8 | 874.9 | 794.1 | 909.9 | 686.5
1939.4 | 1720.4 | 926.5 | 879.8 | 804.5 | 907.9 | 687.4
1940.4 | 1721.4 | 929.4 | 883.7 | 810.7 | 918 | 688.4
1941.4 | 1722.4 | 931.8 | 889 | 809.8 | 925.1 | 688.8
1942.4 | 1723.4 | 933.7 | 901.3 | 820.4 | 934 | 693
1943.4 | 1724.4 | 934.6 | 897.8 | 825.6 | 939.5 | 695.1
1944.4 | 1725.4 | 936.7 | 887.6 | 826.5 | 937.2 | 696.1
1945.4 | 1726.4 | 938.9 | 890.6 | 832.4 | 940.9 | 698.4
1946.4 | 1727.4 | 941.4 | 896.2 | 840.3 | 949.1 | 701.4
1947.4 | 1728.4 | 940.6 | 877.5 | 822.2 | 943.1 | 699.9
1948.4 | 1729.4 | 938.5 | 855.8 | 816.2 | 932.7 | 701.3
1949.4 | 1730.4 | 934.1 | 855.1 | 815.5 | 919.7 | 702.4
1950.4 | 1731.4 | 932.5 | 874.4 | 827.5 | 914 | 706.2
1951.4 | 1732.4 | 927.4 | 866 | 828.8 | 902.8 | 708.7
1952.4 | 1733.4 | 923.7 | 863.3 | 827.2 | 896.3 | 713.1
1953.4 | 1734.4 | 920.7 | 864.3 | 827.9 | 892.6 | 712.4
1954.4 | 1735.4 | 918.8 | 865.6 | 836 | 887.6 | 713.1
1955.4 | 1736.4 | 918.5 | 861.5 | 834.8 | 890.1 | 714.2
1956.4 | 1737.4 | 918.3 | 856.9 | 831.6 | 895.3 | 714.2
1957.4 | 1738.4 | 912.3 | 843 | 799.1 | 881.3 | 710.1
1958.4 | 1739.4 | 904.4 | 823.3 | 787.9 | 863.8 | 707.9
1959.4 | 1740.4 | 901.8 | 820.8 | 794.3 | 865.1 | 707.9
1960.4 | 1741.4 | 901.9 | 822.1 | 779.1 | 869.9 | 707
1961.4 | 1742.4 | 900.7 | 807.5 | 777.9 | 872 | 705.6
1962.4 | 1743.4 | 897.4 | 788.5 | 777.3 | 867.8 | 705.7
1963.4 | 1744.4 | 892.1 | 789.1 | 782 | 864.1 | 705.9
1964.4 | 1745.4 | 891.2 | 797.3 | 790.2 | 868.4 | 707.2
1965.4 | 1746.4 | 891.6 | 815.6 | 798.4 | 868.9 | 709
1966.4 | 1747.4 | 892.4 | 816.3 | 800.9 | 869.8 | 710.2
1967.4 | 1748.4 | 896.8 | 828.9 | 808.1 | 881.8 | 711.4
1968.4 | 1749.4 | 900.6 | 818.9 | 806.4 | 892 | 711.1
1969.4 | 1750.4 | 903.1 | 843.5 | 815.4 | 896.5 | 714.6
1970.4 | 1751.4 | 905.5 | 845.7 | 818.6 | 902.5 | 717.1
1971.4 | 1752.4 | 905.7 | 846.6 | 817 | 899 | 717.6
1972.4 | 1753.4 | 905.2 | 845 | 823.8 | 895.9 | 717
1973.4 | 1754.4 | 907.8 | 856 | 834.7 | 900.5 | 719.3
1974.4 | 1755.4 | 911 | 860.7 | 845.5 | 906.7 | 722.8
1975.4 | 1756.4 | 912 | 870.6 | 848.5 | 905.4 | 724.6
1976.4 | 1757.4 | 912 | 880.9 | 840.5 | 903.1 | 723.2
1977.4 | 1758.4 | 912.6 | 878.5 | 834.3 | 903.5 | 722.2
1978.4 | 1759.4 | 916.1 | 885.7 | 838.9 | 911.2 | 723.5
1979.4 | 1760.4 | 919 | 886.4 | 843 | 916.2 | 725.4
1980.4 | 1761.4 | 922.3 | 878.3 | 842.4 | 922.7 | 726.4
1981.4 | 1762.4 | 923.7 | 874.4 | 844.9 | 924.1 | 727.7
1982.4 | 1763.4 | 925.6 | 885.3 | 852.2 | 930.1 | 730.6
1983.4 | 1764.4 | 927.7 | 884.5 | 855.5 | 937.7 | 733.7
1984.4 | 1765.4 | 928.9 | 889.3 | 855.8 | 940.8 | 738.5
1985.4 | 1766.4 | 929.9 | 875.8 | 855.9 | 943.5 | 740.7
1986.4 | 1767.4 | 931 | 887.8 | 853.4 | 942.2 | 743.5
1987.4 | 1768.4 | 930.8 | 887.2 | 843.7 | 934.2 | 744.4
1988.4 | 1769.4 | 931.5 | 883 | 847.6 | 937.4 | 747.9
1989.4 | 1770.4 | 931.5 | 875.2 | 853.6 | 941.8 | 750.6
1990.4 | 1771.4 | 931.9 | 854.7 | 854.6 | 943.9 | 752.3
1991.4 | 1772.4 | 932.1 | 851.6 | 854.2 | 942.3 | 754
1992.4 | 1773.4 | 931.5 | 845.6 | 848.9 | 940.3 | 753.9
1993.4 | 1774.4 | 932.7 | 852.3 | 848.9 | 946 | 755.7
1994.4 | 1775.4 | 933.1 | 847.9 | 843.2 | 948.7 | 755
1995.4 | 1776.4 | 933.3 | 859.2 | 843.2 | 948 | 756.6
1996.4 | 1777.4 | 934.3 | 867.9 | 842.8 | 948.8 | 758.9
1997.4 | 1778.4 | 932.4 | 861.1 | 833.8 | 941.2 | 758.6
1998.4 | 1779.4 | 929.8 | 859.4 | 826.2 | 932.3 | 757.3
1999.4 | 1780.4 | 923.7 | 842.6 | 811.6 | 918.5 | 754.6
2000.4 | 1781.4 | 922 | 835.9 | 800 | 914.1 | 751.5
2001.4 | 1782.4 | 923.5 | 841.8 | 794.4 | 918.5 | 750.8
2002.4 | 1783.4 | 922 | 837 | 796.5 | 914.4 | 750.9
2003.4 | 1784.4 | 921 | 833.6 | 797.4 | 912.2 | 750.9
2004.4 | 1785.4 | 922.4 | 845.4 | 800.1 | 918.6 | 750.5
2005.4 | 1786.4 | 922.6 | 850.6 | 801.7 | 919.1 | 750
2006.4 | 1787.4 | 920.5 | 847.2 | 812.2 | 913.2 | 749.4
2007.4 | 1788.4 | 920.2 | 851.9 | 824.5 | 911.4 | 750.5
2008.4 | 1789.4 | 919.8 | 827 | 804.1 | 911.1 | 746.2
2009.4 | 1790.4 | 919 | 826.8 | 799.1 | 912.7 | 745.5
2010.4 | 1791.4 | 916.9 | 824.6 | 775.7 | 909 | 743.4
2011.4 | 1792.4 | 908.4 | 798.8 | 746.3 | 890.5 | 738.9
2012.4 | 1793.4 | 898.3 | 765.7 | 718.7 | 870.9 | 734.1
2013.4 | 1794.4 | 886.4 | 740.8 | 694.1 | 847.4 | 729
2014.4 | 1795.4 | 882.1 | 749 | 703.2 | 837.4 | 728.2
2015.4 | 1796.4 | 879.3 | 768.5 | 715.2 | 834.5 | 726.6
2016.4 | 1797.4 | 872.5 | 753 | 705.5 | 826.2 | 723.3
2017.4 | 1798.4 | 869 | 764.4 | 712.5 | 825.3 | 722.5
2018.4 | 1799.4 | 868.4 | 791.6 | 720.6 | 827.9 | 722
2019.4 | 1800.4 | 865.2 | 776.7 | 707.2 | 825.2 | 718.9
2020.4 | 1801.4 | 863.6 | 758.3 | 702.7 | 827.8 | 715.5
2021.4 | 1802.4 | 860.5 | 740.5 | 687 | 826.2 | 710.8
2022.4 | 1803.4 | 856.5 | 725.1 | 681.2 | 822 | 708.5
2023.4 | 1804.4 | 852.8 | 714 | 671.8 | 814.5 | 705.6
2024.4 | 1805.4 | 845.6 | 697.4 | 660.1 | 802.5 | 701.4
2025.4 | 1806.4 | 838.3 | 692.1 | 647.3 | 791.2 | 698.2
2026.4 | 1807.4 | 832.8 | 687.9 | 649.2 | 784.7 | 696
2027.4 | 1808.4 | 834.1 | 708.3 | 670.2 | 790.4 | 696.7
2028.4 | 1809.4 | 838.6 | 739.3 | 698 | 801.6 | 698
2029.4 | 1810.4 | 843.8 | 767 | 731.8 | 812.9 | 701.3
2030.4 | 1811.4 | 844.6 | 774.9 | 742.9 | 809.5 | 703.5
2031.4 | 1812.4 | 847.3 | 773.7 | 768.8 | 816.7 | 705.8
2032.4 | 1813.4 | 853.1 | 790.6 | 785 | 832.2 | 708.8
2033.4 | 1814.4 | 857 | 797 | 790.1 | 839.2 | 711.7
2034.4 | 1815.4 | 862.1 | 794.9 | 805.9 | 854 | 714.3
2035.4 | 1816.4 | 864 | 806.2 | 808.6 | 856.6 | 715.7
2036.4 | 1817.4 | 862.9 | 804.7 | 812.2 | 849.2 | 715.7
2037.4 | 1818.4 | 865.4 | 816.1 | 809.5 | 853.9 | 716.1
2038.4 | 1819.4 | 868.1 | 818.3 | 793.5 | 860.8 | 715.9
2039.4 | 1820.4 | 871.4 | 819.8 | 789.7 | 868.6 | 715.6
2040.4 | 1821.4 | 874.6 | 821 | 797.6 | 875.7 | 717.2
2041.4 | 1822.4 | 877.3 | 816.6 | 790.6 | 880.2 | 716.6
2042.4 | 1823.4 | 879.3 | 809.4 | 787.6 | 880.1 | 716.5
2043.4 | 1824.4 | 882.9 | 818.2 | 787.9 | 884.8 | 717.1
2044.4 | 1825.4 | 887 | 834.3 | 798 | 894.6 | 718.9
2045.4 | 1826.4 | 889 | 831.3 | 799.7 | 894.6 | 718.6
2046.4 | 1827.4 | 891.4 | 833 | 805.3 | 896.7 | 719.1
2047.4 | 1828.4 | 894.9 | 846.6 | 817.4 | 904.9 | 722.4
2048.4 | 1829.4 | 898.8 | 855.2 | 828 | 915 | 725.7
2049.4 | 1830.4 | 901.9 | 869.9 | 837.5 | 920.4 | 729.7
2050.4 | 1831.4 | 904.3 | 873.1 | 844.4 | 925.5 | 733.2
2051.4 | 1832.4 | 906.8 | 872.1 | 851.7 | 933.5 | 736
2052.4 | 1833.4 | 908.6 | 861.7 | 848.2 | 935.8 | 739.6
2053.4 | 1834.4 | 910 | 848.9 | 833.2 | 932.6 | 740
2054.4 | 1835.4 | 911.6 | 844.6 | 833.7 | 934.7 | 739.4
2055.4 | 1836.4 | 913 | 846 | 842.1 | 937 | 741.7
2056.4 | 1837.4 | 913.7 | 848.5 | 850.7 | 940.3 | 746.3
2057.4 | 1838.4 | 914.8 | 841.5 | 833.2 | 938.3 | 745.2
2058.4 | 1839.4 | 915.4 | 831.7 | 813.7 | 936.6 | 743
2059.4 | 1840.4 | 916.2 | 819.5 | 811.6 | 938.5 | 741.6
2060.4 | 1841.4 | 917.7 | 823.1 | 819.5 | 943.7 | 743.6
2061.4 | 1842.4 | 917.5 | 815.7 | 814.2 | 944.1 | 743.9
2062.4 | 1843.4 | 915.3 | 807.2 | 789 | 935.2 | 740.7
2063.4 | 1844.4 | 910.6 | 790.4 | 784 | 921.6 | 739.8
2064.4 | 1845.4 | 905.6 | 778.6 | 762.8 | 913.9 | 736.1
2065.4 | 1846.4 | 901.6 | 781.5 | 763.5 | 906.6 | 734.2
2066.4 | 1847.4 | 898.5 | 781.5 | 767.1 | 901.1 | 732.7
2067.4 | 1848.4 | 898.6 | 781 | 777.3 | 903.2 | 733.7
2068.4 | 1849.4 | 897.2 | 786.5 | 768.9 | 902.6 | 732.4
2069.4 | 1850.4 | 894.6 | 779.9 | 758 | 897.3 | 728.9
2070.4 | 1851.4 | 895.9 | 786.5 | 766.5 | 900.6 | 729.2
2071.4 | 1852.4 | 895.8 | 796.1 | 780.4 | 899.5 | 729.9
2072.4 | 1853.4 | 896.8 | 794.9 | 800.5 | 904.3 | 731.4
2073.4 | 1854.4 | 896.2 | 795.2 | 805.4 | 904.3 | 732.4
2074.4 | 1855.4 | 895.4 | 785.6 | 801.9 | 904.4 | 731.7
2075.4 | 1856.4 | 893.6 | 782.8 | 802.6 | 899.8 | 730.4
2076.4 | 1857.4 | 891 | 791.5 | 811.7 | 895 | 730.8
2077.4 | 1858.4 | 893.9 | 794.5 | 814.3 | 905.2 | 732.4
2078.4 | 1859.4 | 895.1 | 792.8 | 802.2 | 910.7 | 730.8
2079.4 | 1860.4 | 892.3 | 784.9 | 802.3 | 904.4 | 730.9
2080.4 | 1861.4 | 891.2 | 785.2 | 792 | 905.1 | 729.4
2081.4 | 1862.4 | 892.1 | 779.7 | 779.8 | 907 | 729.2
2082.4 | 1863.4 | 888.4 | 770.4 | 765.3 | 898.7 | 725.6
2083.4 | 1864.4 | 887.3 | 774.7 | 764.8 | 895 | 724.5
2084.4 | 1865.4 | 885.1 | 781.4 | 768.3 | 886.8 | 724.4
2085.4 | 1866.4 | 882.3 | 786.6 | 762.5 | 879 | 721.2
2086.4 | 1867.4 | 881.6 | 791.6 | 775.4 | 878.1 | 720
2087.4 | 1868.4 | 884.3 | 806.6 | 779.6 | 885 | 720.5
2088.4 | 1869.4 | 885.5 | 815.8 | 794.1 | 888.5 | 721.3
2089.4 | 1870.4 | 887.2 | 821.4 | 806.3 | 894.3 | 723.4
2090.4 | 1871.4 | 887.9 | 820.1 | 791.8 | 897.2 | 723
2091.4 | 1872.4 | 887.2 | 819.4 | 778 | 893.6 | 720.1
2092.4 | 1873.4 | 881.9 | 796.9 | 762.6 | 877.1 | 717.6
2093.4 | 1874.4 | 878.2 | 784.6 | 758.1 | 870.6 | 715.7
2094.4 | 1875.4 | 878.8 | 783.2 | 767.9 | 875.6 | 717.5
2095.4 | 1876.4 | 877.5 | 763.1 | 747.3 | 876.9 | 715.4
2096.4 | 1877.4 | 872.9 | 743.3 | 723.1 | 870.8 | 711
2097.4 | 1878.4 | 865.4 | 719.7 | 689.9 | 855.6 | 706.8
2098.4 | 1879.4 | 853.5 | 697.2 | 662.9 | 828.9 | 701.6
2099.4 | 1880.4 | 841.2 | 667.9 | 637.8 | 807.1 | 696.9
2100.4 | 1881.4 | 829.1 | 638.1 | 614 | 789.5 | 692.1
2101.4 | 1882.4 | 821.7 | 629 | 608.7 | 782.5 | 688.5
2102.4 | 1883.4 | 817.6 | 636.7 | 609.7 | 779.7 | 686.4
2103.4 | 1884.4 | 818.6 | 672.8 | 636.1 | 786.3 | 686.5
2104.4 | 1885.4 | 820.4 | 694.2 | 642.5 | 792 | 685.1
2105.4 | 1886.4 | 823.4 | 725.1 | 672.4 | 800.9 | 686.2
2106.4 | 1887.4 | 827.5 | 756.3 | 697.1 | 809.3 | 686.7
2107.4 | 1888.4 | 831.9 | 767.6 | 715.7 | 822 | 687.4
2108.4 | 1889.4 | 837.4 | 792.6 | 745.1 | 836.1 | 690
2109.4 | 1890.4 | 842.4 | 804.3 | 755 | 846.5 | 692.8
2110.4 | 1891.4 | 843.6 | 803.6 | 768.1 | 843.1 | 693.3
2111.4 | 1892.4 | 843.8 | 783.9 | 771.3 | 840.1 | 694
2112.4 | 1893.4 | 845.3 | 769.4 | 768.9 | 841.2 | 694
2113.4 | 1894.4 | 845.8 | 768.9 | 750.3 | 844.4 | 692.4
2114.4 | 1895.4 | 846.4 | 766.6 | 741.2 | 848.7 | 689.7
2115.4 | 1896.4 | 842.4 | 736.5 | 726.7 | 839.2 | 686.7
2116.4 | 1897.4 | 835.1 | 708.2 | 703.8 | 822.5 | 683.7
2117.4 | 1898.4 | 829.3 | 680.8 | 678.8 | 816.8 | 679.8
2118.4 | 1899.4 | 821 | 656.5 | 652.9 | 805.1 | 675.4
2119.4 | 1900.4 | 813 | 647.9 | 633.8 | 788.8 | 671.5
2120.4 | 1901.4 | 806 | 640.6 | 622.3 | 775.6 | 668.1
2121.4 | 1902.4 | 804.2 | 645.3 | 614 | 776.8 | 666.3
2122.4 | 1903.4 | 803 | 649.4 | 604 | 780.4 | 663.9
2123.4 | 1904.4 | 801.2 | 646 | 603.8 | 777.4 | 661.6
2124.4 | 1905.4 | 798.5 | 641.6 | 602 | 772.3 | 659.2
2125.4 | 1906.4 | 797.3 | 655.1 | 606.4 | 770.8 | 657.5
2126.4 | 1907.4 | 800 | 682.5 | 635.3 | 779.5 | 658.3
2127.4 | 1908.4 | 805.8 | 700 | 653.1 | 792.9 | 660
2128.4 | 1909.4 | 806.4 | 702.7 | 666.8 | 791.1 | 659.6
2129.4 | 1910.4 | 808 | 712.5 | 690.4 | 795 | 661.1
2130.4 | 1911.4 | 812.8 | 732.3 | 729.5 | 806.8 | 663.2
2131.4 | 1912.4 | 816.5 | 743.4 | 727.8 | 815.8 | 662.7
2132.4 | 1913.4 | 818.9 | 735.6 | 719.3 | 821.7 | 662.4
2133.4 | 1914.4 | 824.1 | 751.1 | 725.3 | 830.8 | 663
2134.4 | 1915.4 | 827.6 | 773.1 | 735.8 | 839.2 | 664.4
2135.4 | 1916.4 | 829.2 | 768.5 | 726.8 | 841.6 | 662
2136.4 | 1917.4 | 830.8 | 765.6 | 728.2 | 841.6 | 661.7
2137.4 | 1918.4 | 831.9 | 757.1 | 725.6 | 840.6 | 660.5
2138.4 | 1919.4 | 834.8 | 769.6 | 729.2 | 847.2 | 661.7
2139.4 | 1920.4 | 835.4 | 766.9 | 739.1 | 841.5 | 662.9
2140.4 | 1921.4 | 837.1 | 768.1 | 755.5 | 841.7 | 666.2
2141.4 | 1922.4 | 837.2 | 755.9 | 756 | 839 | 667.1
2142.4 | 1923.4 | 838.3 | 760.1 | 758.2 | 840 | 668.1
2143.4 | 1924.4 | 839.6 | 762.6 | 760.4 | 841.6 | 669.5
2144.4 | 1925.4 | 838.9 | 760.7 | 768.9 | 842.1 | 668.9
2145.4 | 1926.4 | 842.3 | 761.1 | 765.4 | 854.5 | 669.7
2146.4 | 1927.4 | 846.3 | 772.6 | 763.8 | 862.2 | 670
2147.4 | 1928.4 | 850.8 | 775.9 | 779.4 | 872.4 | 673.7
2148.4 | 1929.4 | 853.1 | 778.5 | 783.1 | 874.7 | 675.1
2149.4 | 1930.4 | 856.2 | 785.9 | 789.9 | 877.5 | 678
2150.4 | 1931.4 | 859.8 | 794 | 783.8 | 883.9 | 679.2
2151.4 | 1932.4 | 861.4 | 785.1 | 772 | 883.7 | 679.1
2152.4 | 1933.4 | 860.5 | 767.9 | 752.3 | 878.5 | 677.1
2153.4 | 1934.4 | 860.6 | 758.4 | 752.4 | 874 | 677.1
2154.4 | 1935.4 | 862.6 | 780.7 | 747.8 | 875.9 | 677.4
2155.4 | 1936.4 | 863.4 | 789.4 | 754.6 | 876 | 678.2
2156.4 | 1937.4 | 866.9 | 804.3 | 765.6 | 879.4 | 680.1
2157.4 | 1938.4 | 870.6 | 811 | 764.5 | 887 | 679.5
2158.4 | 1939.4 | 873.1 | 812.9 | 755.6 | 892.9 | 678.4
2159.4 | 1940.4 | 874.3 | 807.4 | 760.9 | 896.2 | 678.9
2160.4 | 1941.4 | 878.8 | 815.5 | 769.2 | 906.2 | 680.1
2161.4 | 1942.4 | 882.8 | 819.5 | 780.6 | 912.1 | 681.1
2162.4 | 1943.4 | 883.7 | 810.4 | 786.5 | 911.7 | 681.9
2163.4 | 1944.4 | 885.1 | 811.8 | 793 | 908.1 | 683.6
2164.4 | 1945.4 | 888.5 | 823.1 | 794.6 | 911.1 | 685.4
2165.4 | 1946.4 | 890.5 | 813.3 | 803.9 | 916 | 686.4
2166.4 | 1947.4 | 892.7 | 816.6 | 811.4 | 920.8 | 688.6
2167.4 | 1948.4 | 894.4 | 819.3 | 819.1 | 922.8 | 690.7
2168.4 | 1949.4 | 897.2 | 834.8 | 818.9 | 928.7 | 692.2
2169.4 | 1950.4 | 899.1 | 829 | 812.2 | 926.2 | 692.3
2170.4 | 1951.4 | 900.2 | 832.8 | 814.6 | 923.3 | 694.5
2171.4 | 1952.4 | 901.8 | 828.9 | 825 | 926.5 | 697.6
2172.4 | 1953.4 | 903.4 | 838.1 | 839.2 | 934.2 | 700.3
2173.4 | 1954.4 | 904.7 | 849.3 | 842.4 | 932.9 | 701.5
2174.4 | 1955.4 | 903.3 | 850.4 | 816.2 | 920.4 | 700.7
2175.4 | 1956.4 | 897.9 | 842.7 | 786.3 | 903 | 697.8
2176.4 | 1957.4 | 891.4 | 843 | 780.7 | 881.8 | 696.6
2177.4 | 1958.4 | 890.6 | 852.7 | 794.4 | 878.9 | 700.8
2178.4 | 1959.4 | 892.1 | 853.3 | 802.7 | 883.7 | 705
2179.4 | 1960.4 | 891.8 | 853.8 | 796.8 | 882.9 | 707.9
2180.4 | 1961.4 | 890.6 | 850.2 | 783.1 | 878.3 | 705.3
2181.4 | 1962.4 | 889.1 | 849.4 | 776.4 | 875.4 | 702.1
2182.4 | 1963.4 | 889.3 | 852.2 | 782.7 | 877.2 | 703
2183.4 | 1964.4 | 891.1 | 853.8 | 802.6 | 886.7 | 706.7
2184.4 | 1965.4 | 892.4 | 856.6 | 819.5 | 899.5 | 711.2
2185.4 | 1966.4 | 893.3 | 863.1 | 835.8 | 905.9 | 716.3
2186.4 | 1967.4 | 894.1 | 861.8 | 840.1 | 911.2 | 720.1
2187.4 | 1968.4 | 894.9 | 858.6 | 841.3 | 914.2 | 723.7
2188.4 | 1969.4 | 894.4 | 859.2 | 845.1 | 917.1 | 728
2189.4 | 1970.4 | 894.7 | 853.8 | 842.9 | 921 | 733
2190.4 | 1971.4 | 895.1 | 844.5 | 847.7 | 922.1 | 736.4
2191.4 | 1972.4 | 896.9 | 842.6 | 851.7 | 918.1 | 741.9
2192.4 | 1973.4 | 898.3 | 842.2 | 854.7 | 918.1 | 745.5
2193.4 | 1974.4 | 899.2 | 836.9 | 843.4 | 919.2 | 746.6
2194.4 | 1975.4 | 900 | 836.5 | 841.7 | 914.7 | 748.5
2195.4 | 1976.4 | 900.6 | 845 | 845.1 | 910.6 | 749.8
2196.4 | 1977.4 | 900.7 | 848.6 | 841 | 906.6 | 751.1
2197.4 | 1978.4 | 901.6 | 851.7 | 849.3 | 906.4 | 754.3
2198.4 | 1979.4 | 902.3 | 853.2 | 849 | 909.7 | 757.6
2199.4 | 1980.4 | 902.1 | 849.2 | 852.2 | 911 | 759.8
2200.4 | 1981.4 | 900.5 | 836 | 849.5 | 910.5 | 759.5
2201.4 | 1982.4 | 899.9 | 834.3 | 846.7 | 910 | 760.6
2202.4 | 1983.4 | 900.5 | 833.6 | 848.8 | 916.1 | 761.3
2203.4 | 1984.4 | 901 | 839.5 | 838.1 | 921.2 | 759.3
2204.4 | 1985.4 | 902.3 | 841.1 | 826.1 | 924.4 | 758.6
2205.4 | 1986.4 | 903.5 | 851.4 | 830.3 | 923.6 | 758.5
2206.4 | 1987.4 | 904.3 | 855.4 | 833.3 | 924.2 | 759.1
2207.4 | 1988.4 | 902.1 | 837 | 812.8 | 918.5 | 756.3
2208.4 | 1989.4 | 900 | 829 | 795.8 | 915.7 | 752.8
2209.4 | 1990.4 | 900.3 | 823.6 | 801.2 | 919 | 752.3
2210.4 | 1991.4 | 901.1 | 828 | 807.2 | 919.7 | 751.3
2211.4 | 1992.4 | 900.7 | 818 | 803.6 | 920.4 | 750
2212.4 | 1993.4 | 898 | 801.2 | 799.1 | 912.1 | 749
2213.4 | 1994.4 | 893.6 | 797.2 | 786.8 | 902.3 | 745.2
2214.4 | 1995.4 | 889.3 | 793.1 | 774.2 | 897.8 | 742.3
2215.4 | 1996.4 | 889.2 | 791.1 | 765.6 | 902.9 | 740.9
2216.4 | 1997.4 | 890.1 | 791.4 | 759.7 | 905.5 | 739.2
2217.4 | 1998.4 | 889.5 | 790.2 | 763.9 | 902.4 | 738
2218.4 | 1999.4 | 887.1 | 783.6 | 762.1 | 899.6 | 736.5
2219.4 | 2000.4 | 885.9 | 777.7 | 767.6 | 899 | 735.8
2220.4 | 2001.4 | 883.4 | 781.7 | 765.3 | 893.4 | 733.5
2221.4 | 2002.4 | 878.2 | 763.7 | 746.8 | 880.7 | 729.9
2222.4 | 2003.4 | 873.7 | 758.7 | 743.4 | 873.9 | 728
2223.4 | 2004.4 | 876.2 | 765.8 | 748.1 | 887.8 | 727.6
2224.4 | 2005.4 | 877.3 | 761.4 | 750.6 | 893.7 | 726.6
2225.4 | 2006.4 | 876.5 | 759.3 | 758.2 | 892.5 | 725
2226.4 | 2007.4 | 875.1 | 749.6 | 763.8 | 889.4 | 724.2
2227.4 | 2008.4 | 869 | 737.8 | 746.8 | 872.7 | 720.1
2228.4 | 2009.4 | 865.1 | 742.7 | 741 | 862.1 | 717.1
2229.4 | 2010.4 | 867.3 | 766 | 752 | 876.5 | 718.5
2230.4 | 2011.4 | 871.1 | 778 | 764.4 | 893.2 | 719.4
2231.4 | 2012.4 | 874.7 | 778.1 | 773.9 | 900.9 | 722.2
2232.4 | 2013.4 | 875.9 | 781.2 | 768.3 | 900.3 | 723.1
2233.4 | 2014.4 | 874.3 | 768.6 | 759.6 | 895.1 | 721.1
2234.4 | 2015.4 | 876.5 | 780.6 | 756.9 | 901.3 | 721.3
2235.4 | 2016.4 | 878.1 | 781.4 | 750.9 | 901.8 | 720.8
2236.4 | 2017.4 | 876.7 | 776.2 | 735.1 | 895.3 | 718.2
2237.4 | 2018.4 | 875.2 | 781.9 | 744.1 | 894.8 | 717
2238.4 | 2019.4 | 874.1 | 784.5 | 760 | 895.4 | 717.5
2239.4 | 2020.4 | 875.3 | 785.9 | 762.2 | 898.3 | 718.2
2240.4 | 2021.4 | 877 | 780.9 | 760.6 | 906.5 | 716.5
2241.4 | 2022.4 | 879.5 | 790.2 | 777.3 | 911.5 | 718.6
2242.4 | 2023.4 | 881.6 | 805.1 | 789.3 | 914 | 720.2
2243.4 | 2024.4 | 884.1 | 814.8 | 805.5 | 919.3 | 724.2
2244.4 | 2025.4 | 886.1 | 826.5 | 797.2 | 917.4 | 725.1
2245.4 | 2026.4 | 886.4 | 829.9 | 797.4 | 909 | 725.7
2246.4 | 2027.4 | 886.4 | 838.8 | 811.9 | 909.5 | 731.3
2247.4 | 2028.4 | 887.4 | 831.3 | 813 | 916.6 | 733.3
2248.4 | 2029.4 | 886.7 | 817.6 | 814.3 | 916.2 | 734.4
2249.4 | 2030.4 | 886.3 | 814.5 | 812.6 | 914.9 | 735.7
2250.4 | 2031.4 | 888.3 | 825.8 | 822.2 | 917 | 738.2
2251.4 | 2032.4 | 889.4 | 834.2 | 826.8 | 921.7 | 738.9
2252.4 | 2033.4 | 891.3 | 834.4 | 826.4 | 923.5 | 738.8
2253.4 | 2034.4 | 890.8 | 824 | 826.3 | 922.2 | 740.2
2254.4 | 2035.4 | 887.9 | 819.8 | 826.8 | 914.5 | 740.6
2255.4 | 2036.4 | 889.3 | 834.1 | 833.4 | 926.1 | 742.7
2256.4 | 2037.4 | 890.2 | 817.3 | 821.4 | 922.1 | 742.8
2257.4 | 2038.4 | 889.3 | 806.5 | 813.9 | 910.5 | 742.4
2258.4 | 2039.4 | 880 | 756.1 | 770.6 | 883.4 | 736.7
2259.4 | 2040.4 | 864.5 | 702.1 | 709.9 | 839.3 | 727.3
2260.4 | 2041.4 | 848.6 | 659.6 | 660.2 | 803 | 719.4
2261.4 | 2042.4 | 833.5 | 622.9 | 619.2 | 768.4 | 711.5
2262.4 | 2043.4 | 819.3 | 591.3 | 583.6 | 739.2 | 704.1
2263.4 | 2044.4 | 805.6 | 566.7 | 553.9 | 716.1 | 697.4
2264.4 | 2045.4 | 792.5 | 542.8 | 526.8 | 692.4 | 690.8
2265.4 | 2046.4 | 779.5 | 524.4 | 507.1 | 674 | 684.6
2266.4 | 2047.4 | 766.9 | 508.9 | 488.6 | 656.7 | 678.5
2267.4 | 2048.4 | 754.6 | 493.3 | 468.6 | 636 | 672.4
2268.4 | 2049.4 | 742.8 | 478.5 | 453.5 | 619.1 | 667
2269.4 | 2050.4 | 731.2 | 465.1 | 436.5 | 602.6 | 661.9
2270.4 | 2051.4 | 720.1 | 451.1 | 420.3 | 584.1 | 656.2
2271.4 | 2052.4 | 709.2 | 437.3 | 404.4 | 565.3 | 650.6
2272.4 | 2053.4 | 699.2 | 427.6 | 391.9 | 553.5 | 644.9
2273.4 | 2054.4 | 689.5 | 422.1 | 382.2 | 545.8 | 640.2
2274.4 | 2055.4 | 680.4 | 414.1 | 372.4 | 537 | 634.9
2275.4 | 2056.4 | 672 | 406.4 | 365 | 532.6 | 630.3
2276.4 | 2057.4 | 664.1 | 399.6 | 357.2 | 528.2 | 626.3
2277.4 | 2058.4 | 656.2 | 393.5 | 349.1 | 522.2 | 621.9
2278.4 | 2059.4 | 648.4 | 385.9 | 340.3 | 515.7 | 617.6
2279.4 | 2060.4 | 641.2 | 381.7 | 332.8 | 511.9 | 613.3
2280.4 | 2061.4 | 634.5 | 375.3 | 325.3 | 510.8 | 608.9
2281.4 | 2062.4 | 628 | 370.8 | 318.4 | 508.5 | 605.2
2282.4 | 2063.4 | 621.7 | 364 | 313.1 | 504.3 | 601.3
2283.4 | 2064.4 | 615.1 | 358.7 | 307.9 | 498.2 | 597.5
2284.4 | 2065.4 | 608.3 | 353.6 | 303.1 | 490.6 | 593.9
2285.4 | 2066.4 | 601.5 | 348.9 | 297.3 | 480 | 590.1
2286.4 | 2067.4 | 595.1 | 343 | 291.7 | 473 | 586.6
2287.4 | 2068.4 | 589.1 | 337.9 | 286.1 | 468.4 | 583
2288.4 | 2069.4 | 583.5 | 333.4 | 281.5 | 463.5 | 579.7
2289.4 | 2070.4 | 577.9 | 328.3 | 276.8 | 456.8 | 576.3
2290.4 | 2071.4 | 572.5 | 322.4 | 272.2 | 451.6 | 572.8
2291.4 | 2072.4 | 566.6 | 317.3 | 267 | 443.7 | 569.5
2292.4 | 2073.4 | 561.2 | 313.1 | 262.4 | 437.3 | 566.1
2293.4 | 2074.4 | 556.1 | 308.1 | 258.4 | 432.6 | 563
2294.4 | 2075.4 | 551.2 | 303 | 254.1 | 428.3 | 559.8
2295.4 | 2076.4 | 546.1 | 298.3 | 250 | 421 | 556.6
2296.4 | 2077.4 | 541.1 | 293.5 | 246 | 413.6 | 553
2297.4 | 2078.4 | 536.3 | 287.4 | 242.1 | 405.1 | 549.6
2298.4 | 2079.4 | 531.6 | 283.2 | 238.4 | 397.7 | 546.3
2299.4 | 2080.4 | 527.1 | 279.8 | 234.8 | 393.2 | 542.8
2300.4 | 2081.4 | 522.8 | 277.4 | 231.9 | 390.3 | 539.5
2301.4 | 2082.4 | 518.9 | 273.1 | 229 | 388.7 | 536.8
2302.4 | 2083.4 | 515.1 | 269.7 | 226.2 | 387.7 | 534
2303.4 | 2084.4 | 511.3 | 266 | 223.4 | 386.3 | 531.6
2304.4 | 2085.4 | 507.5 | 262.5 | 220.8 | 385 | 528.9
2305.4 | 2086.4 | 503.9 | 259.5 | 218.3 | 383.1 | 526.3
2306.4 | 2087.4 | 500.1 | 257.4 | 214.7 | 379.7 | 523.5
2307.4 | 2088.4 | 496.6 | 254.1 | 211.1 | 376.4 | 520.6
2308.4 | 2089.4 | 493.1 | 250.2 | 208 | 372.2 | 518
2309.4 | 2090.4 | 489.2 | 246.9 | 205.3 | 367.8 | 515.3
2310.4 | 2091.4 | 485.5 | 242.9 | 202.7 | 363.7 | 512.9
2311.4 | 2092.4 | 481.5 | 243.2 | 200.1 | 359.3 | 509.9
2312.4 | 2093.4 | 477.5 | 241.3 | 198.2 | 355.4 | 507.4
2313.4 | 2094.4 | 474.2 | 237.8 | 196.1 | 353.5 | 505
2314.4 | 2095.4 | 470.6 | 235.5 | 193.5 | 348.6 | 502.7
2315.4 | 2096.4 | 467.3 | 230.7 | 190.7 | 342.9 | 500.1
2316.4 | 2097.4 | 464.2 | 229.6 | 187.9 | 339.4 | 497.8
2317.4 | 2098.4 | 461.3 | 225.8 | 185.3 | 336.8 | 495.5
2318.4 | 2099.4 | 458.4 | 223.7 | 182.7 | 334.9 | 493.3
2319.4 | 2100.4 | 455.8 | 221.4 | 180.4 | 334.7 | 490.6
2320.4 | 2101.4 | 453.4 | 218.5 | 177.5 | 334 | 488.1
2321.4 | 2102.4 | 450.9 | 216.7 | 176.1 | 332.3 | 485.9
2322.4 | 2103.4 | 448.2 | 218.2 | 174.1 | 330.3 | 483.6
2323.4 | 2104.4 | 445.2 | 217.5 | 172.9 | 328 | 481.2
2324.4 | 2105.4 | 442.4 | 216.4 | 171 | 326.3 | 478.8
2325.4 | 2106.4 | 440 | 213.4 | 169.3 | 325.1 | 476.5
2326.4 | 2107.4 | 437.4 | 210.8 | 168.1 | 322.9 | 474.2
2327.4 | 2108.4 | 435 | 209.8 | 166.9 | 321.4 | 472
2328.4 | 2109.4 | 432.4 | 209.8 | 164.7 | 319.8 | 469.7
2329.4 | 2110.4 | 429.9 | 208.8 | 163.1 | 318.3 | 467.3
2330.4 | 2111.4 | 427.4 | 206.7 | 161.7 | 317.5 | 464.9
2331.4 | 2112.4 | 425 | 203.8 | 159.8 | 315.9 | 462.9
2332.4 | 2113.4 | 422.8 | 200.7 | 158.2 | 314.9 | 460.8
2333.4 | 2114.4 | 420.5 | 198.3 | 157 | 312.5 | 458.9
2334.4 | 2115.4 | 417.8 | 195.5 | 155.4 | 307.5 | 457.1
2335.4 | 2116.4 | 415.1 | 194.1 | 153.8 | 303.8 | 455
2336.4 | 2117.4 | 412.6 | 192.1 | 152.8 | 301.4 | 453.1
2337.4 | 2118.4 | 410.1 | 190.8 | 151.6 | 299.1 | 451.2
2338.4 | 2119.4 | 407.6 | 189.7 | 150.1 | 296.8 | 449.4
2339.4 | 2120.4 | 405.6 | 190.7 | 148.4 | 295.6 | 447.5
2340.4 | 2121.4 | 403.3 | 190.3 | 146.9 | 293.9 | 445.7
2341.4 | 2122.4 | 401.2 | 188.6 | 145.8 | 293 | 443.8
2342.4 | 2123.4 | 399.2 | 186.6 | 144.7 | 293.1 | 442
2343.4 | 2124.4 | 397.1 | 184.9 | 143.9 | 292.4 | 440.1
2344.4 | 2125.4 | 395 | 184.4 | 143.5 | 291.3 | 438.4
2345.4 | 2126.4 | 392.9 | 183.3 | 142.6 | 289.8 | 436.7
2346.4 | 2127.4 | 390.8 | 185.2 | 142 | 287.9 | 434.9
2347.4 | 2128.4 | 388.8 | 186.3 | 141.6 | 286.7 | 433.2
2348.4 | 2129.4 | 386.8 | 185.7 | 140.8 | 285.8 | 431.6
2349.4 | 2130.4 | 384.9 | 183.4 | 139.6 | 284.9 | 429.9
2350.4 | 2131.4 | 383 | 183.8 | 139.2 | 283 | 428.2
2351.4 | 2132.4 | 380.9 | 181.3 | 138.4 | 280.7 | 426.2
2352.4 | 2133.4 | 378.9 | 181.2 | 137.6 | 278.8 | 424.4
2353.4 | 2134.4 | 377.2 | 181.2 | 137 | 276.9 | 422.7
2354.4 | 2135.4 | 375.4 | 179.1 | 135.9 | 275.7 | 420.9
2355.4 | 2136.4 | 373.5 | 177.4 | 134.6 | 273 | 419.1
2356.4 | 2137.4 | 371.5 | 174.9 | 133.4 | 269.2 | 416.9
2357.4 | 2138.4 | 369.7 | 174 | 132.3 | 266.9 | 414.9
2358.4 | 2139.4 | 368 | 173.4 | 131 | 265.9 | 413.2
2359.4 | 2140.4 | 366.5 | 173.2 | 130.1 | 265 | 411.3
2360.4 | 2141.4 | 364.7 | 170.8 | 129.2 | 263.9 | 410
2361.4 | 2142.4 | 362.6 | 170 | 127.8 | 260.3 | 408.7
2362.4 | 2143.4 | 360.5 | 167.5 | 126.7 | 257.5 | 406.9
2363.4 | 2144.4 | 358.7 | 164.9 | 125.9 | 254.9 | 405.2
2364.4 | 2145.4 | 356.8 | 163.4 | 125 | 252.9 | 403.5
2365.4 | 2146.4 | 355.1 | 162.9 | 124 | 251.7 | 402
2366.4 | 2147.4 | 353.5 | 162.1 | 123.1 | 251.1 | 400.6
2367.4 | 2148.4 | 352.1 | 162.5 | 122 | 251.2 | 398.8
2368.4 | 2149.4 | 350.5 | 163.5 | 121 | 250.5 | 397.1
2369.4 | 2150.4 | 348.9 | 163.3 | 120.3 | 249.2 | 395.6
2370.4 | 2151.4 | 347.5 | 161.9 | 119.2 | 248.6 | 393.8
2371.4 | 2152.4 | 346.2 | 159.9 | 118.3 | 248.1 | 392.1
2372.4 | 2153.4 | 344.9 | 158.1 | 117.2 | 247.5 | 390.2
2373.4 | 2154.4 | 343.4 | 156.9 | 116.4 | 246.1 | 388.3
2374.4 | 2155.4 | 341.7 | 156.1 | 115.8 | 243.4 | 386.7
2375.4 | 2156.4 | 340 | 154.9 | 115.1 | 240.3 | 385.1
2376.4 | 2157.4 | 338.4 | 153.7 | 114.6 | 237.4 | 383.8
2377.4 | 2158.4 | 336.9 | 153.3 | 114.1 | 235.8 | 382.2
2378.4 | 2159.4 | 335.3 | 154.6 | 113.1 | 234.4 | 380.7
2379.4 | 2160.4 | 333.6 | 156.4 | 112.2 | 232.5 | 379.2
2380.4 | 2161.4 | 332.1 | 154.7 | 111.3 | 231.1 | 377.8
2381.4 | 2162.4 | 330.9 | 154 | 110.7 | 230.3 | 376.2
2382.4 | 2163.4 | 329.2 | 153.6 | 110.2 | 229.6 | 374.6
2383.4 | 2164.4 | 327.8 | 152.9 | 109.6 | 229.6 | 373.2
2384.4 | 2165.4 | 326.6 | 153.2 | 109 | 230 | 371.8
2385.4 | 2166.4 | 325.2 | 151.4 | 108.6 | 230.2 | 370.6
2386.4 | 2167.4 | 323.9 | 150.5 | 108.1 | 229.7 | 369.5
2387.4 | 2168.4 | 322.6 | 149.7 | 107.5 | 228.6 | 368.4
2388.4 | 2169.4 | 321.2 | 148.9 | 107.2 | 227 | 367.1
2389.4 | 2170.4 | 319.9 | 149.7 | 106.9 | 225.5 | 365.7
2390.4 | 2171.4 | 318.5 | 149.7 | 106.5 | 224 | 364.1
2391.4 | 2172.4 | 317 | 148.8 | 106.2 | 222.7 | 362.6
2392.4 | 2173.4 | 315.4 | 146.6 | 105.1 | 219.8 | 361.2
2393.4 | 2174.4 | 313.9 | 145.2 | 104.5 | 216.5 | 359.6
2394.4 | 2175.4 | 312.5 | 144.7 | 103.9 | 213.2 | 357.6
2395.4 | 2176.4 | 311.2 | 143.4 | 103.4 | 210 | 355.9
2396.4 | 2177.4 | 309.9 | 142.4 | 102.9 | 207.9 | 354.3
2397.4 | 2178.4 | 308.5 | 141.3 | 102.5 | 206.3 | 352.8
2398.4 | 2179.4 | 306.9 | 140.5 | 101.8 | 204.8 | 351.4
2399.4 | 2180.4 | 305.1 | 139.8 | 101 | 202.8 | 350.1
2400.4 | 2181.4 | 303.8 | 139.1 | 100.5 | 200.7 | 348.8
2401.4 | 2182.4 | 302.5 | 137.9 | 99.5 | 199 | 347.7
2402.4 | 2183.4 | 301.3 | 138.2 | 99 | 198.7 | 346.5
2403.4 | 2184.4 | 300.1 | 137.7 | 98.5 | 198.4 | 345.4
2404.4 | 2185.4 | 298.9 | 137.5 | 98.2 | 198.2 | 344.6
2405.4 | 2186.4 | 297.7 | 137 | 97.9 | 197.7 | 343.5
2406.4 | 2187.4 | 296.6 | 136.6 | 97.7 | 197.7 | 342.3
2407.4 | 2188.4 | 295.3 | 136.3 | 96.9 | 197.4 | 341.1
2408.4 | 2189.4 | 293.9 | 135.3 | 96.2 | 195.9 | 339.8
2409.4 | 2190.4 | 292.6 | 134.8 | 95.6 | 194.1 | 338.6
2410.4 | 2191.4 | 291.4 | 134.9 | 95.2 | 192.5 | 337.3
2411.4 | 2192.4 | 290.3 | 133.5 | 94.4 | 191 | 336
2412.4 | 2193.4 | 289 | 132.3 | 94 | 188.8 | 334.9
2413.4 | 2194.4 | 287.8 | 131.2 | 93.6 | 187.4 | 333.8
2414.4 | 2195.4 | 286.6 | 130.1 | 93.1 | 186.1 | 332.4
2415.4 | 2196.4 | 285.4 | 129.4 | 93 | 184.4 | 331.2
2416.4 | 2197.4 | 284.1 | 128.8 | 92.6 | 182.8 | 329.9
2417.4 | 2198.4 | 283 | 128.9 | 92.3 | 181.8 | 328.7
2418.4 | 2199.4 | 281.8 | 127.7 | 91.7 | 180.7 | 327.6
2419.4 | 2200.4 | 280.6 | 127.1 | 91.3 | 179.9 | 326.4
2420.4 | 2201.4 | 279.5 | 126.3 | 91.1 | 179.6 | 325.2
2421.4 | 2202.4 | 278.3 | 125.8 | 90.6 | 179.4 | 324.1
2422.4 | 2203.4 | 277.2 | 125 | 90.5 | 178.7 | 323.2
2423.4 | 2204.4 | 276.1 | 124 | 90.2 | 177.7 | 322.2
2424.4 | 2205.4 | 275 | 124.7 | 89.8 | 176.8 | 321
2425.4 | 2206.4 | 274.1 | 123.6 | 89.4 | 176.1 | 320
2426.4 | 2207.4 | 273.1 | 121.8 | 89 | 175.6 | 318.6
2427.4 | 2208.4 | 271.7 | 120.9 | 88.6 | 175 | 317.1
2428.4 | 2209.4 | 270.4 | 119.8 | 88.3 | 173 | 316
2429.4 | 2210.4 | 269.2 | 119.2 | 87.5 | 171.4 | 314.7
2430.4 | 2211.4 | 268.2 | 118.5 | 87.1 | 170.7 | 313.6
2431.4 | 2212.4 | 267 | 117.7 | 86.6 | 169.2 | 312.5
2432.4 | 2213.4 | 265.9 | 117.3 | 86.1 | 168.1 | 311.4
2433.4 | 2214.4 | 264.8 | 116.9 | 85.8 | 167.1 | 310.2
2434.4 | 2215.4 | 263.6 | 116 | 85.4 | 165.2 | 309.1
2435.4 | 2216.4 | 262.6 | 115.4 | 85.1 | 164 | 308
2436.4 | 2217.4 | 261.5 | 114.8 | 84.8 | 162.2 | 306.7
2437.4 | 2218.4 | 260.5 | 113.7 | 84.5 | 160.4 | 305.3
2438.4 | 2219.4 | 259.5 | 113 | 84 | 159.2 | 304
2439.4 | 2220.4 | 258.5 | 111.6 | 83.3 | 157.8 | 302.6
2440.4 | 2221.4 | 257.4 | 110.4 | 82.8 | 156.4 | 301.4
2441.4 | 2222.4 | 256.3 | 109.6 | 82.7 | 155.5 | 300.3
2442.4 | 2223.4 | 255.4 | 108.9 | 81.9 | 156.1 | 299
2443.4 | 2224.4 | 254.5 | 108.9 | 81.9 | 156.6 | 298.1
2444.4 | 2225.4 | 253.5 | 107.8 | 81.7 | 156.9 | 297.1
2445.4 | 2226.4 | 252.5 | 107.8 | 81.1 | 156.4 | 296.1
2446.4 | 2227.4 | 251.6 | 107.2 | 80.4 | 155.5 | 295
2447.4 | 2228.4 | 250.7 | 106 | 80.1 | 155 | 294
2448.4 | 2229.4 | 249.9 | 105.5 | 79.8 | 154.5 | 293
2449.4 | 2230.4 | 249 | 104.9 | 79.4 | 154.3 | 292
2450.4 | 2231.4 | 248.2 | 103.9 | 79.3 | 154.7 | 290.9
2451.4 | 2232.4 | 247.3 | 103 | 79.2 | 154.8 | 289.9
2452.4 | 2233.4 | 246.1 | 101.7 | 79.1 | 153.8 | 289
2453.4 | 2234.4 | 245 | 100.9 | 78.6 | 152.9 | 288
2454.4 | 2235.4 | 244.1 | 101.2 | 77.9 | 152.7 | 287.1
2455.4 | 2236.4 | 243.2 | 100.7 | 77.7 | 152.7 | 286.2
2456.4 | 2237.4 | 242.5 | 99.5 | 77.6 | 152.7 | 285.2
2457.4 | 2238.4 | 241.5 | 98.7 | 77.6 | 153 | 284.4
2458.4 | 2239.4 | 240.7 | 98.4 | 77.4 | 152.5 | 283.6
2459.4 | 2240.4 | 239.7 | 97.8 | 77.2 | 151.8 | 282.7
2460.4 | 2241.4 | 238.9 | 97.1 | 76.9 | 151 | 281.3
2461.4 | 2242.4 | 237.9 | 96.6 | 76.7 | 150.6 | 280.2
2462.4 | 2243.4 | 236.7 | 96.1 | 76 | 150.1 | 279.2
2463.4 | 2244.4 | 235.6 | 95.6 | 75.5 | 148.8 | 278.2
2464.4 | 2245.4 | 234.8 | 94.9 | 75.1 | 147.8 | 277.2
2465.4 | 2246.4 | 234 | 94.5 | 75 | 146.8 | 276.2
2466.4 | 2247.4 | 233.2 | 94.2 | 74.9 | 146 | 275.3
2467.4 | 2248.4 | 232.4 | 93.3 | 74.5 | 145.4 | 274.3
2468.4 | 2249.4 | 231.7 | 92.4 | 74 | 144.2 | 273.4
2469.4 | 2250.4 | 230.9 | 91.5 | 74.5 | 142.8 | 272.6
2470.4 | 2251.4 | 230 | 91.8 | 74 | 141.8 | 271.8
2471.4 | 2252.4 | 229.2 | 91.6 | 73.4 | 140.9 | 270.8
2472.4 | 2253.4 | 228.4 | 91.3 | 73.2 | 140 | 269.9
2473.4 | 2254.4 | 227.3 | 91.2 | 72.8 | 139.1 | 269
2474.4 | 2255.4 | 226.5 | 91.3 | 72.4 | 138.3 | 268
2475.4 | 2256.4 | 225.7 | 91.7 | 72 | 138.3 | 267.2
2476.4 | 2257.4 | 225.1 | 90.9 | 72.1 | 138.1 | 266.5
2477.4 | 2258.4 | 224.4 | 90.7 | 72 | 138.4 | 265.8
2478.4 | 2259.4 | 223.8 | 90.7 | 71.6 | 138.6 | 264.9
2479.4 | 2260.4 | 223.2 | 90.2 | 71.4 | 138.6 | 264.1
2480.4 | 2261.4 | 222.5 | 89.4 | 71.5 | 138.8 | 263.3
2481.4 | 2262.4 | 221.8 | 88.9 | 71.5 | 139 | 262.4
2482.4 | 2263.4 | 221.1 | 88.9 | 71.5 | 138.9 | 261.5
2483.4 | 2264.4 | 220.2 | 89.5 | 71.5 | 138.4 | 260.6
2484.4 | 2265.4 | 219.3 | 89.2 | 71.4 | 137.7 | 259.8
2485.4 | 2266.4 | 218.8 | 88.2 | 71.1 | 137.4 | 258.9
2486.4 | 2267.4 | 218.2 | 87.6 | 70.7 | 137.1 | 258
2487.4 | 2268.4 | 217.6 | 86.5 | 70.2 | 137 | 257.3
2488.4 | 2269.4 | 217 | 85.7 | 70.1 | 137.1 | 256.5
2489.4 | 2270.4 | 216.3 | 85.1 | 69.7 | 136.7 | 255.5
2490.4 | 2271.4 | 215.4 | 84.3 | 69.4 | 136 | 254.7
2491.4 | 2272.4 | 214.8 | 83.7 | 69.2 | 135.8 | 253.9
2492.4 | 2273.4 | 214.3 | 83.2 | 69.4 | 135.5 | 253.2
2493.4 | 2274.4 | 213.7 | 82.8 | 69.4 | 134.9 | 252.5
2494.4 | 2275.4 | 213 | 83.1 | 69.5 | 134.1 | 251.5
2495.4 | 2276.4 | 212.1 | 83.3 | 69.1 | 133.2 | 250.9
2496.4 | 2277.4 | 211.4 | 82.6 | 69.1 | 132.5 | 250.2
2497.4 | 2278.4 | 210.7 | 82 | 68.7 | 131.8 | 249.3
2498.4 | 2279.4 | 210.1 | 81.6 | 68.8 | 131.3 | 248.6
2499.4 | 2280.4 | 209.5 | 81.2 | 69 | 130.9 | 247.8
2500.4 | 2281.4 | 209 | 81 | 68.7 | 130.6 | 247.1
2501.4 | 2282.4 | 208.4 | 81.4 | 68.4 | 130.7 | 246.3
2502.4 | 2283.4 | 207.8 | 81.3 | 68.1 | 130.4 | 245.4
2503.4 | 2284.4 | 207.3 | 80.4 | 67.7 | 130.4 | 244.5
2504.4 | 2285.4 | 206.7 | 80 | 67.5 | 130.1 | 243.7
2505.4 | 2286.4 | 206 | 78.9 | 67.5 | 129.5 | 242.9
2506.4 | 2287.4 | 205.5 | 78 | 67.4 | 129.6 | 242.2
2507.4 | 2288.4 | 205 | 77.4 | 67.1 | 129.9 | 241.4
2508.4 | 2289.4 | 204.4 | 76.8 | 67 | 129.9 | 240.6
2509.4 | 2290.4 | 203.9 | 76.7 | 66.9 | 130 | 239.9
2510.4 | 2291.4 | 203.1 | 76.3 | 66.7 | 130 | 239.3
2511.4 | 2292.4 | 202.6 | 76 | 66.8 | 130.3 | 238.5
2512.4 | 2293.4 | 202.1 | 76.1 | 66.8 | 130.4 | 237.7
2513.4 | 2294.4 | 201.5 | 75.6 | 66.5 | 130.1 | 236.9
2514.4 | 2295.4 | 201 | 74.8 | 66.4 | 129.7 | 236.1
2515.4 | 2296.4 | 200.5 | 74.5 | 66.4 | 129 | 235.3
2516.4 | 2297.4 | 199.8 | 74.2 | 66.5 | 128.4 | 234.7
2517.4 | 2298.4 | 199.1 | 73.8 | 66.7 | 127.4 | 234.1
2518.4 | 2299.4 | 198.4 | 74.2 | 66.6 | 126.1 | 233.3
2519.4 | 2300.4 | 197.6 | 74.3 | 66.7 | 124.7 | 232.5
2520.4 | 2301.4 | 196.6 | 74.6 | 66.5 | 123.2 | 231.9
2521.4 | 2302.4 | 195.6 | 74 | 66.2 | 121.6 | 231.1
2522.4 | 2303.4 | 195 | 73.4 | 66.1 | 121 | 230.4
2523.4 | 2304.4 | 194.4 | 73.2 | 66 | 120.9 | 229.9
2524.4 | 2305.4 | 193.7 | 72.8 | 65.7 | 120.4 | 229.2
2525.4 | 2306.4 | 193.1 | 72.6 | 65.6 | 120.2 | 228.4
2526.4 | 2307.4 | 192.4 | 72.2 | 65.4 | 119.9 | 227.8
2527.4 | 2308.4 | 191.9 | 71.9 | 65.1 | 120 | 227.1
2528.4 | 2309.4 | 191.4 | 71.6 | 64.9 | 119.9 | 226.4
2529.4 | 2310.4 | 190.8 | 71 | 64.6 | 119.7 | 225.7
2530.4 | 2311.4 | 190.3 | 70.6 | 64.5 | 119.5 | 225.2
2531.4 | 2312.4 | 189.7 | 70 | 64.4 | 118.6 | 224.4
2532.4 | 2313.4 | 189 | 69.7 | 64.4 | 117.4 | 223.4
2533.4 | 2314.4 | 188.5 | 69.3 | 64.3 | 116.3 | 222.8
2534.4 | 2315.4 | 187.9 | 69.1 | 64.3 | 115.7 | 222
2535.4 | 2316.4 | 187.4 | 68.7 | 64.4 | 115.1 | 221.2
2536.4 | 2317.4 | 186.8 | 68.3 | 64.5 | 114.6 | 220.5
2537.4 | 2318.4 | 186.2 | 68.2 | 64.2 | 114.1 | 219.9
2538.4 | 2319.4 | 185.5 | 68 | 64 | 113.1 | 219.2
2539.4 | 2320.4 | 184.8 | 67.9 | 64 | 112.4 | 218.6
2540.4 | 2321.4 | 184.3 | 67.7 | 64.1 | 112.5 | 218
2541.4 | 2322.4 | 183.9 | 67.5 | 63.9 | 112.8 | 217.3
2542.4 | 2323.4 | 183.4 | 67.5 | 63.8 | 112.9 | 216.7
2543.4 | 2324.4 | 182.8 | 67.4 | 63.8 | 113 | 216.1
2544.4 | 2325.4 | 182.2 | 66.8 | 63.5 | 112.6 | 215.6
2545.4 | 2326.4 | 181.7 | 66.5 | 63.5 | 111.8 | 214.9
2546.4 | 2327.4 | 181 | 66.4 | 63.4 | 111.3 | 214.3
2547.4 | 2328.4 | 180.4 | 66.6 | 63.2 | 111.1 | 213.7
2548.4 | 2329.4 | 179.9 | 66.3 | 62.9 | 110.7 | 213.1
2549.4 | 2330.4 | 179.5 | 66 | 62.9 | 110.4 | 212.5
2550.4 | 2331.4 | 178.9 | 65.5 | 62.7 | 110.2 | 211.7
2551.4 | 2332.4 | 178.5 | 65.3 | 62.4 | 110.3 | 211.1
2552.4 | 2333.4 | 178.2 | 65.3 | 62.3 | 110.5 | 210.5
2553.4 | 2334.4 | 177.7 | 65.2 | 62.2 | 110.8 | 209.9
2554.4 | 2335.4 | 177.2 | 65.1 | 62.3 | 110.9 | 209.3
2555.4 | 2336.4 | 176.8 | 64.8 | 62.4 | 110.7 | 208.7
2556.4 | 2337.4 | 176.5 | 64.5 | 62.5 | 110.4 | 208
2557.4 | 2338.4 | 175.8 | 64.2 | 62.1 | 110.2 | 207.3
2558.4 | 2339.4 | 175 | 63.9 | 61.8 | 110.4 | 206.5
2559.4 | 2340.4 | 174.5 | 63.4 | 61.7 | 110.1 | 205.8
2560.4 | 2341.4 | 173.9 | 63.3 | 61.4 | 109.4 | 205.2
2561.4 | 2342.4 | 173.4 | 63.1 | 61.3 | 108.8 | 204.6
2562.4 | 2343.4 | 172.8 | 62.6 | 61.1 | 108 | 204.1
2563.4 | 2344.4 | 172.4 | 62.2 | 61.1 | 107.3 | 203.5
2564.4 | 2345.4 | 172.1 | 61.9 | 61.2 | 106.9 | 202.7
2565.4 | 2346.4 | 171.5 | 61.6 | 60.9 | 106.4 | 202.2
2566.4 | 2347.4 | 171 | 61.5 | 60.9 | 105.9 | 201.7
2567.4 | 2348.4 | 170.4 | 62.2 | 60.8 | 105.2 | 201.1
2568.4 | 2349.4 | 169.9 | 61.9 | 60.5 | 104.6 | 200.6
2569.4 | 2350.4 | 169.5 | 61.5 | 60.4 | 104.1 | 199.8
2570.4 | 2351.4 | 169 | 61.1 | 60.4 | 103.6 | 199.2
2571.4 | 2352.4 | 168.6 | 60.8 | 60.2 | 103.2 | 198.6
2572.4 | 2353.4 | 168.1 | 60.8 | 60 | 102.6 | 197.9
2573.4 | 2354.4 | 167.6 | 61.4 | 59.8 | 101.8 | 197.3
2574.4 | 2355.4 | 167.1 | 61.7 | 59.6 | 101.2 | 196.6
2575.4 | 2356.4 | 166.7 | 61.3 | 59.8 | 101.1 | 196.1
2576.4 | 2357.4 | 166.2 | 61.5 | 59.7 | 101.4 | 195.7
2577.4 | 2358.4 | 165.8 | 61.6 | 59.5 | 101.7 | 195.2
2578.4 | 2359.4 | 165.5 | 61.2 | 59.5 | 101.9 | 194.6
2579.4 | 2360.4 | 165.1 | 61 | 59.4 | 101.6 | 194.1
2580.4 | 2361.4 | 164.5 | 60.8 | 59.2 | 101.5 | 193.6
2581.4 | 2362.4 | 164 | 60.9 | 59 | 101.3 | 193.1
2582.4 | 2363.4 | 163.5 | 60.6 | 59 | 100.9 | 192.6
2583.4 | 2364.4 | 163 | 60.2 | 58.9 | 100.7 | 192
2584.4 | 2365.4 | 162.5 | 60.2 | 58.6 | 100.5 | 191.4
2585.4 | 2366.4 | 161.9 | 60 | 58.4 | 100 | 190.8
2586.4 | 2367.4 | 161.4 | 59.7 | 58.2 | 99.8 | 190.3
2587.4 | 2368.4 | 160.9 | 59.7 | 58.2 | 100.1 | 189.8
2588.4 | 2369.4 | 160.3 | 59.9 | 58.1 | 100.6 | 189.4
2589.4 | 2370.4 | 159.9 | 59.6 | 57.9 | 100.9 | 188.9
2590.4 | 2371.4 | 159.5 | 59.3 | 57.9 | 101.1 | 188.4
2591.4 | 2372.4 | 158.9 | 59.3 | 57.8 | 101.1 | 188
2592.4 | 2373.4 | 158.3 | 59.3 | 57.7 | 100.8 | 187.4
2593.4 | 2374.4 | 158 | 59.2 | 57.8 | 100.5 | 186.9
2594.4 | 2375.4 | 157.6 | 59.8 | 57.6 | 100.4 | 186.4
2595.4 | 2376.4 | 157.1 | 60.5 | 57.4 | 100.5 | 185.9
2596.4 | 2377.4 | 156.6 | 60.3 | 57.3 | 100.2 | 185.3
2597.4 | 2378.4 | 156.1 | 59.8 | 57.3 | 100.2 | 184.7
2598.4 | 2379.4 | 155.7 | 59.6 | 57.2 | 99.8 | 184.2
2599.4 | 2380.4 | 155.4 | 59.2 | 57.2 | 99.1 | 183.5
2600.4 | 2381.4 | 155 | 59 | 56.9 | 98.9 | 183
2601.4 | 2382.4 | 154.7 | 58.7 | 56.7 | 98.2 | 182.4
2602.4 | 2383.4 | 154.2 | 58.3 | 56.7 | 97.8 | 182
2603.4 | 2384.4 | 153.9 | 58.3 | 56.7 | 97.4 | 181.5
2604.4 | 2385.4 | 153.4 | 58.4 | 56.5 | 97.1 | 181.2
2605.4 | 2386.4 | 153 | 58.1 | 56.4 | 97.1 | 180.7
2606.4 | 2387.4 | 152.7 | 58 | 56.3 | 97.3 | 180.3
2607.4 | 2388.4 | 152.5 | 57.9 | 56.2 | 97.5 | 179.9
2608.4 | 2389.4 | 152.2 | 58.1 | 56 | 97.7 | 179.4
2609.4 | 2390.4 | 152 | 58 | 55.9 | 97.9 | 179
2610.4 | 2391.4 | 151.7 | 57.8 | 55.8 | 97.7 | 178.5
2611.4 | 2392.4 | 151.4 | 57.7 | 55.8 | 97.1 | 178
2612.4 | 2393.4 | 151.1 | 57.4 | 55.8 | 96.2 | 177.3
2613.4 | 2394.4 | 150.7 | 57.2 | 55.6 | 95.4 | 176.8
2614.4 | 2395.4 | 150.2 | 57.1 | 55.5 | 94.5 | 176.4
2615.4 | 2396.4 | 149.8 | 56.8 | 55.5 | 94 | 175.9
2616.4 | 2397.4 | 149.5 | 56.7 | 55.3 | 94 | 175.4
2617.4 | 2398.4 | 149.3 | 56.8 | 54.9 | 94.4 | 174.8
2618.4 | 2399.4 | 148.9 | 56.7 | 54.7 | 94.6 | 174.4
2619.4 | 2400.4 | 148.6 | 56.4 | 54.7 | 94.5 | 173.9
2620.4 | 2401.4 | 148.2 | 56.1 | 54.5 | 94.1 | 173.4
2621.4 | 2402.4 | 147.9 | 55.9 | 54.5 | 93.6 | 172.8
2622.4 | 2403.4 | 147.5 | 55.7 | 54.4 | 92.7 | 172.4
2623.4 | 2404.4 | 147.1 | 55.7 | 54.6 | 91.7 | 172.1
2624.4 | 2405.4 | 146.6 | 55.6 | 54.5 | 90.9 | 171.4
2625.4 | 2406.4 | 146.2 | 55.4 | 54.6 | 90.6 | 171
2626.4 | 2407.4 | 145.8 | 55.4 | 54.5 | 90.3 | 170.5
2627.4 | 2408.4 | 145.3 | 55.7 | 54.3 | 90 | 170
2628.4 | 2409.4 | 144.7 | 56.4 | 54 | 90 | 169.7
2629.4 | 2410.4 | 144.2 | 57.1 | 53.8 | 89.8 | 169.3
2630.4 | 2411.4 | 143.8 | 57.3 | 53.9 | 90 | 168.8
2631.4 | 2412.4 | 143.5 | 56.9 | 53.7 | 90.1 | 168.4
2632.4 | 2413.4 | 143.2 | 56.6 | 53.2 | 90.5 | 167.9
2633.4 | 2414.4 | 143 | 56.2 | 53 | 90.6 | 167.5
2634.4 | 2415.4 | 142.7 | 55.9 | 52.7 | 90.9 | 167.1
2635.4 | 2416.4 | 142.5 | 55.6 | 52.6 | 91.2 | 166.7
2636.4 | 2417.4 | 142.3 | 55.5 | 52.6 | 91.4 | 166.2
2637.4 | 2418.4 | 142.1 | 55.6 | 52.5 | 91.7 | 165.8
2638.4 | 2419.4 | 141.8 | 55.7 | 52.7 | 91.8 | 165.5
2639.4 | 2420.4 | 141.5 | 55.8 | 52.8 | 91.9 | 165.2
2640.4 | 2421.4 | 141.2 | 56 | 52.8 | 92 | 164.9
2641.4 | 2422.4 | 140.9 | 55.8 | 52.6 | 92 | 164.5
2642.4 | 2423.4 | 140.5 | 55.6 | 52.6 | 92 | 164.1
2643.4 | 2424.4 | 140.1 | 55.6 | 52.6 | 91.6 | 163.8
2644.4 | 2425.4 | 139.8 | 55.2 | 52.3 | 91.3 | 163.4
2645.4 | 2426.4 | 139.6 | 54.9 | 52.2 | 91.1 | 163.1
2646.4 | 2427.4 | 139.2 | 54.7 | 52.1 | 91.2 | 162.7
2647.4 | 2428.4 | 138.9 | 54.9 | 52.1 | 91.3 | 162.3
2648.4 | 2429.4 | 138.5 | 55 | 52 | 91.2 | 162.1
2649.4 | 2430.4 | 138.2 | 55.3 | 51.9 | 91.1 | 161.8
2650.4 | 2431.4 | 137.9 | 55.7 | 51.5 | 91.1 | 161.4
2651.4 | 2432.4 | 137.6 | 55.5 | 51.4 | 91.1 | 161
2652.4 | 2433.4 | 137.4 | 55.2 | 51.1 | 90.9 | 160.6
2653.4 | 2434.4 | 137.1 | 54.9 | 51 | 90.8 | 160.2
2654.4 | 2435.4 | 137 | 54.6 | 50.8 | 90.8 | 159.8
2655.4 | 2436.4 | 136.7 | 54.2 | 50.6 | 90.7 | 159.3
2656.4 | 2437.4 | 136.5 | 54.3 | 50.5 | 91 | 159
2657.4 | 2438.4 | 136.2 | 54 | 50.5 | 90.9 | 158.6
2658.4 | 2439.4 | 135.9 | 54 | 50.4 | 90.7 | 158.2
2659.4 | 2440.4 | 135.7 | 53.8 | 50.2 | 90.7 | 157.7
2660.4 | 2441.4 | 135.5 | 53.3 | 49.9 | 90.9 | 157.2
2661.4 | 2442.4 | 135.3 | 53 | 49.6 | 91.3 | 156.8
2662.4 | 2443.4 | 135.1 | 52.8 | 49.4 | 91.2 | 156.4
2663.4 | 2444.4 | 134.9 | 52.6 | 49.2 | 91 | 156
2664.4 | 2445.4 | 134.6 | 52.3 | 48.8 | 90.6 | 155.6
2665.4 | 2446.4 | 134.3 | 52 | 48.5 | 90.1 | 155.3
2666.4 | 2447.4 | 134.1 | 51.6 | 48.3 | 89.7 | 154.9
2667.4 | 2448.4 | 133.8 | 51.3 | 47.9 | 89.4 | 154.5
2668.4 | 2449.4 | 133.4 | 51.3 | 47.9 | 89.2 | 154.2
2669.4 | 2450.4 | 133.1 | 51.3 | 47.7 | 88.9 | 153.8

## Test Facts
Last row in IRMS data sheets: | 20
Time when Penlight power was initiated: | 219