## IS Test Matrix
Intermediate Scale Test Matrix - Revision F (12-06-06)
|  | Comments: 1) All tests were conducted as open burns with a Propene (Propylene) gas sand burner 2) Colors identify test conditions grouped into the same test run | [14 empty] | ACTUAL TEST CONDITIONS
Burn Test # | Rev. E Test # | Loc. | Cable Insulation Material | [8 empty] | Number of Conductors |  |  |  | Conductor Size (AWG) |  |  |  |  | Cable Bundle Size |  |  |  |  | Water Spary Optionsl | Raceway Type
|  |  | Thermoset | [5 empty] | Thermoplastic
|  |  | XLPE | EPR | Silicone | XLPO | TS/TP | Vita-Link | PE | PVC | Tefzel | 3 | 2 | 7 | 12 | 8 | 12 | 14 | 16 | 18 | 1 | 3 | 6 | 12 | Load Tr | * | 12" Tray | 2.5" Cnd | Air Drop
Prelim 1 | Prelim 1 | A | X | [8 empty] | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | A | X | [10 empty] | X |  |  | X |  |  |  | X | [5 empty] | X
Prelim 2 | Prelim 2 | A | X | [8 empty] | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | A | X | [10 empty] | X |  |  | X |  |  |  | X | [5 empty] | X
Prelim 3 | Prelim 3 | A | [7 empty] | X |  | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | A | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [5 empty] | X
Prelim 4 | Prelim 4 | A | [7 empty] | X |  | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | A | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [5 empty] | X
1 | 15 | A | X | [9 empty] | X | X | X |  | X |  | X | X |  |  |  |  | X |  | X
|  | B | X | [10 empty] | X |  |  | X | [6 empty] | X |  |  | X
|  | D | X | [10 empty] | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | E | X | [10 empty] | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | [10 empty] | X |  |  | X | [6 empty] | X |  |  | X
2 | 1 | A | X | [10 empty] | X |  |  | X | [6 empty] | X |  |  | X
|  | C | X | [10 empty] | X |  |  | X | [5 empty] | X |  |  |  | X
|  | A | X | [5 empty] | X |  |  |  |  | X |  |  | X | [6 empty] | X |  |  | X
|  | C | X | [5 empty] | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
| 11 | C - A | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [7 empty] | X
|  | E | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [5 empty] | X
|  | G | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [5 empty] | X
3 | 2 | A | X | X | [9 empty] | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X | [9 empty] | X |  |  | X | [5 empty] | X |  |  |  | X
| 3 | A |  | X |  |  |  |  | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C |  | X |  |  |  |  | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
| 10 | E | [7 empty] | X |  | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | [7 empty] | X |  | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
4 | 5 | A | X | X |  | X | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X |  | X | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
| 6 | A | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
| 9 | C - A | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [7 empty] | X
|  | E | X | [8 empty] | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | [8 empty] | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
5 | 4 | A | X | X | X | X |  |  | X |  | X |  |  | X |  |  | X | [6 empty] | X |  | X | X
|  | C | X | X | X | X |  |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
| 7 | A | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | X | [5 empty] | X |  | X | X
|  | C | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | X |  |  |  |  | X |  |  | X | X
|  | C - A | X | [10 empty] | X |  |  | X |  |  |  | X | [7 empty] | X
|  | E |  | X | [9 empty] | X |  |  | X |  |  |  | X | [5 empty] | X
|  | G |  | X | [9 empty] | X |  |  | X |  |  |  | X | [5 empty] | X
6 | 12 | A | X | X | X | X |  |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | C | X | X | X | X |  |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | E | X | [5 empty] | X |  | X |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
| 13 | C - A | X | [5 empty] | X |  | X |  |  | X |  |  | X |  |  |  |  | X | [6 empty] | X
|  | A |  | X | X | X | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | C |  | X | X | X | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | G |  |  |  |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  |  |  | X
7 | 14 | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | A | X | X |  | X | X |  |  | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C |  | X |  | X | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | E | X | [5 empty] | X | X |  |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G |  | X |  | X | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
8 | 16 | A | X | [5 empty] | X | X |  |  | X | X | X |  | X |  | X | X |  |  | X |  |  |  | X
|  | A | X | [5 empty] | X | X |  |  | X | X | X |  | X |  | X | X |  |  | X |  |  |  | X
|  | C | X | [5 empty] | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | E | X | [5 empty] | X |  |  |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | [5 empty] | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
9 | 19 | A | X | X | X |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | A | X | X | X |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | C | X | X | X |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | E | X | [5 empty] | X |  | X |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | X | X |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
10 | 20 | A | X | X | X | X | X |  |  |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | A | X | X | X | X | X |  |  |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | C | X | X | X | X | X |  |  | X |  |  |  | X | X |  | X |  |  | X |  |  | X |  |  | X | X
|  | E |  |  |  |  | X |  | X |  | X |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | X |  |  | X |  | X | X | X |  | X | X |  |  | X |  | X |  |  |  | X |  |  |  | X
11 | 21 | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X |  | X | X |  |  | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | E |  |  |  |  | X |  | X | X |  |  |  | X |  |  | X |  |  |  |  | X | [6 empty] | X
|  | G | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
12 | 24 | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X |  | X | X |  |  | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | E |  |  |  |  | X |  | X | X |  |  |  | X |  |  | X |  |  |  |  | X | [6 empty] | X
|  | G | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
13 | 25 | A | X | X |  | X | X | X | X |  | X |  |  | X |  |  | X | [7 empty] | X | X | X
|  | C | X | X |  | X | X | X | X |  | X |  |  | X |  |  | X | [7 empty] | X | X | X
|  | E | X | X | [9 empty] | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | F | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | F | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | G | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | G | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
14 | 27 | A | X | X |  | X | X |  | X | X | X |  |  | X |  |  | X | [7 empty] | X |  | X
|  | C | X | X |  | X | X |  | X | X | X |  |  | X |  |  | X | [7 empty] | X |  | X
|  | E |  |  |  |  | X |  | X | X |  |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | F | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | F | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | G | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | G | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X

## Shorting Summary
Shorting Sequence for Open Burn Test 11, Location A, IRMS #1
Test conditions: Cable: Bundle of 6, 7-conductor, 12 AWG, XLPE, EPR, PE, PVC, TS/TP & XLPO control cables (Items 10, 2, 15, 1, 3 & 8). Cable specimens present: Three lengths of cable were monitored for electrical performance (A, B & C [See Elect. Conn. Map]), a second bundle of 6 cables was monitored for temperature response. Raceway: 12" B-Line Series 2 tray (part number 248P09-12-144) located at position A in the Test Cell chamber with chamber end walls open and un-heated. Exposure conditions: Initial gas burner flow rate set to a nominal 250 kW heat release rate and increased to 300 kW during the test run. Electrical repsonse monitoring: IRMS system using 6 channels - two for each cable (see electrical connection map), cable tray was grounded. Thermal response monitoring: Two cable bundle temperatures (see thermocouple map), air temperatures above and below the cable bundle, and the cable tray rung temperature. Gas burner initiated: Following 207 seconds of baseline data monitoring.
DAQ Time | Burner Time | Event | Interpretation
207 | 0 | Ignited Gas Burner
399-402 | 192-195 | Conductors B3 & B4 both short to ground at less than 1000 ohms (744 & 186) | Cable B shorted to ground
404 | 197 | Conductors B3 & B4 short together at less than 1000 ohms (543) | Cable B shorts internally
441-444 | 234-237 | The existing ground faults on conductors B3 & B4 decrease to less than 100 ohms (83 & 58)
462 | 255 | Conductors A1 & A2 short together at less than 1000 ohms (674) | Cable A shorts internally
468-477 | 261-270 | Conductors A1& A2 both short to ground at less than 1000 ohms (458 & 341) | Cable A shorted to ground
488-491 | 281-284 | Conductors C5 & C6 both short to ground at less than 1000 ohms (119 & 142) | Cable C shorted to ground
505 | 298 | The existing internal fault between conductors A1 & A2 decreases to less than 100 ohms (38)
510-519 | 303-312 | The existing ground faults on conductors A1 & A2 decrease to less than 100 ohms (32 & 27)
530 | 323 | The existing internal fault between conductors B3 & B4 decreases to less than 100 ohms (3)
530-533 | 323-326 | The existing ground faults on conductors C5 & C6 decrease to less than 100 ohms (24 & 67)
544 | 337 | Conductors C5 & C6 short together at less than 100 ohms (82) | Cable C shorts internally
1148 | 941 | Extinguished Gas Burner
Additional Observations
Observation 1 | There was no evidence of cable-to-cable interactions prior to internal cable shorting or shorting to ground.

## Thermocouple Map
Thermocouple map for TC's on and within the cable
|  |  |  | Cable A = | XLPE | (Item #10)
|  |  |  | Cable B = | EPR | (Item #2)
|  |  |  | Cable C = | PE | (Item #15)
|  |  |  | Cable D = | PVC | (Item #1)
|  |  |  | Cable E = | TS/TP | (Item #3)
|  |  |  | Cable F = | XLPO | (Item #8)
Translation to data file names used in "Temperatures" WorkSheet:
| Map Name |  | Location
| A1 | = | Center of bundle, under jacket
| A2 | = | Air above bundle
| A3 | = | Air below bundle
| A4 | = | Intra-bundle, center

## Elect Conn Map
Electrical connection map within the cables
|  |  |  | Cable A = | XLPE | (Item #10)
|  |  |  | Cable B = | EPR | (Item #2)
|  |  |  | Cable C = | PE | (Item #15)
Tray rung under D-E-F
Cable Bundle Arrangement
Cable 7-Conductor Arrangement
| Lt Blue = | Even conductor set
| Lt Red = | Odd conductor set
| Gray = | Center conductor (not connected)
IRMS Electrical Connections

## C-C Individuals
Conductor to Conductor Resistances
Open Burn Test 11 |  |  | 2006-11-20 | 12:58
Mixed | 7-C | Tray A | IRMS | 1
0 | 250 kW
Burner Time | A1-A2 | Burner Time | A1-B3 | Burner Time | A1-B4 | Burner Time | A1-C5 | Burner Time | A1-C6 | Burner Time | A2-B3 | Burner Time | A2-B4 | Burner Time | A2-C5 | Burner Time | A2-C6 | Burner Time | B3-B4 | Burner Time | B3-C5 | Burner Time | B3-C6 | Burner Time | B4-C5 | Burner Time | B4-C6 | Burner Time | C5-C6
-206.5 | 259537.9994 | -203.5 | 257137.9994 | -201 | 258337.9994 | -198 | 259837.9994 | -195 | 259737.9994 | -192.5 | 259137.9994 | -189.5 | 259837.9994 | -187 | 261237.9994 | -184 | 262537.9994 | -181.5 | 253937.9994 | -178.5 | 262737.9994 | -175.5 | 262537.9994 | -173 | 257237.9994 | -170 | 262737.9994 | -167.5 | 262637.9994
-164.5 | 259537.9994 | -161.5 | 257137.9994 | -159 | 258337.9994 | -156 | 259837.9994 | -153.5 | 259737.9994 | -150.5 | 259137.9994 | -147.5 | 259837.9994 | -145 | 261237.9994 | -142 | 262537.9994 | -139.5 | 253937.9994 | -136.5 | 262737.9994 | -133.5 | 262537.9994 | -131 | 257237.9994 | -128 | 262737.9994 | -125.5 | 262637.9994
-122.5 | 259537.9994 | -119.5 | 257137.9994 | -117 | 258337.9994 | -114 | 259837.9994 | -111.5 | 259737.9994 | -108.5 | 259137.9994 | -105.5 | 259837.9994 | -103 | 261237.9994 | -100 | 262537.9994 | -97.5 | 253937.9994 | -94.5 | 262737.9994 | -91.5 | 262537.9994 | -89 | 257237.9994 | -86 | 262737.9994 | -83.5 | 262637.9994
-80.5 | 259537.9994 | -77.5 | 257137.9994 | -75 | 258337.9994 | -72 | 259837.9994 | -69.5 | 259737.9994 | -66.5 | 259137.9994 | -63.5 | 259837.9994 | -61 | 261237.9994 | -58 | 262537.9994 | -55.5 | 253937.9994 | -52.5 | 262737.9994 | -49.5 | 262537.9994 | -47 | 257237.9994 | -44 | 262737.9994 | -41 | 262637.9994
-38.5 | 259537.9994 | -35.5 | 257137.9994 | -33 | 258337.9994 | -30 | 259837.9994 | -27.5 | 259737.9994 | -24.5 | 259137.9994 | -21.5 | 259837.9994 | -19 | 261237.9994 | -16 | 262537.9994 | -13.5 | 253937.9994 | -10.5 | 262737.9994 | -7.5 | 262537.9994 | -4.5 | 257237.9994 | -2 | 262737.9994 | 0.5 | 262637.9994
3.5 | 259537.9994 | 6.5 | 257137.9994 | 9 | 258337.9994 | 12 | 259837.9994 | 15 | 259737.9994 | 17.5 | 259137.9994 | 20.5 | 259837.9994 | 23 | 261237.9994 | 26 | 262537.9994 | 28.5 | 253937.9994 | 31.5 | 262737.9994 | 35 | 262537.9994 | 37 | 257237.9994 | 40 | 262737.9994 | 42.5 | 262637.9994
45.5 | 259537.9994 | 48.5 | 257137.9994 | 51 | 258337.9994 | 54 | 259837.9994 | 56.5 | 259737.9994 | 59.5 | 259137.9994 | 62.5 | 259837.9994 | 65 | 261237.9994 | 68 | 262537.9994 | 70.5 | 253937.9994 | 73.5 | 262737.9994 | 76.5 | 262537.9994 | 79 | 257237.9994 | 82 | 262737.9994 | 84.5 | 262637.9994
87.5 | 259537.9994 | 90.5 | 257137.9994 | 93 | 258337.9994 | 96 | 259837.9994 | 98.5 | 259737.9994 | 101.5 | 259137.9994 | 104.5 | 259837.9994 | 107 | 261237.9994 | 110 | 262537.9994 | 112.5 | 253937.9994 | 115.5 | 262737.9994 | 118.5 | 262537.9994 | 121 | 257237.9994 | 124 | 262737.9994 | 126.5 | 262637.9994
129.5 | 259537.9994 | 132.5 | 257137.9994 | 135 | 258337.9994 | 138 | 259837.9994 | 140.5 | 259737.9994 | 143.5 | 259137.9994 | 146.5 | 259837.9994 | 149 | 261237.9994 | 152 | 262537.9994 | 154.5 | 253937.9994 | 157.5 | 262737.9994 | 160.5 | 262537.9994 | 163 | 257237.9994 | 166 | 262737.9994 | 168.5 | 262637.9994
171.5 | 259537.9994 | 174.5 | 257137.9994 | 177 | 258337.9994 | 180 | 259837.9994 | 182.5 | 259737.9994 | 185.5 | 259137.9994 | 188.5 | 259837.9994 | 191 | 261237.9994 | 194 | 262537.9994 | 196.5 | 542.7162 | 199.5 | 248743.3265 | 202.5 | 231249.9175 | 205 | 199960.2664 | 208 | 170773.0025 | 210.5 | 262637.9994
213.5 | 259537.9994 | 216.5 | 257137.9994 | 219 | 258337.9994 | 222 | 259837.9994 | 224.5 | 259737.9994 | 227.5 | 259137.9994 | 230.5 | 259837.9994 | 233 | 261237.9994 | 236 | 262537.9994 | 238.5 | 137.122 | 241.5 | 158977.492 | 244.5 | 118792.7522 | 247 | 94164.7594 | 250 | 120891.9876 | 252.5 | 11842.6229
255.5 | 673.5162 | 258.5 | 552.6478 | 261 | 457.8988 | 264 | 796.1609 | 266.5 | 220952.9324 | 269.5 | 828.9981 | 272.5 | 646.7358 | 275 | 340.3429 | 278 | 392.4288 | 280.5 | 245.461 | 283.5 | 41.2555 | 286.5 | 13.647 | 289 | 33842.5108 | 292 | 53275.3508 | 294.5 | 1516.3592
297.5 | 37.5869 | 300.5 | 102.4167 | 303 | 73.3617 | 306 | 58.6732 | 308.5 | 30.8978 | 311.5 | 30.5252 | 314.5 | 37.7129 | 317 | 35.5879 | 320 | 25.5526 | 322.5 | 2.6243 | 325.5 | 22.6859 | 328.5 | 6.1936 | 331 | 24.403 | 334 | 3.2263 | 336.5 | 81.6339
339.5 | 70.2351 | 342.5 | 38.0698 | 345 | 23.1 | 348 | 13.3289 | 350.5 | 6.1642 | 353.5 | 11.6065 | 356.5 | 9.3683 | 359 | 21.2191 | 362 | 28.0747 | 364.5 | 5.4678 | 367.5 | 15.0767 | 370.5 | 2.809 | 373 | 29.7612 | 376 | 17.8548 | 378.5 | 2.2628
381.5 | 21.9401 | 384.5 | 2.1685 | 387 | 5.4944 | 390 | 13.3801 | 392.5 | 0.17845 | 395.5 | 16.7094 | 398.5 | 18.1284 | 401 | 2.8395 | 404 | 28.2034 | 406.5 | 26.4424 | 409.5 | 26.7729 | 412.5 | 25.4908 | 415 | 1.5345 | 418 | 19.9117 | 420.5 | 7.3655
423.5 | 29.9884 | 426.5 | 10.7346 | 429 | 0.97501 | 432 | 26.3014 | 434.5 | 2.4089 | 437.5 | 0.14568 | 440.5 | 3.5145 | 443 | 15.0908 | 446 | 13.698 | 448.5 | 16.1815 | 451.5 | 0.70261 | 455 | 11.8886 | 457 | 26.0346 | 460 | 11.8759 | 462.5 | 21.0637
465.5 | 13.4015 | 468.5 | 16.1775 | 471 | 0.0063763 | 474 | 6.7509 | 476.5 | 26.4422 | 479.5 | 6.4595 | 482.5 | 6.523 | 485 | 23.4046 | 488 | 0.5038 | 490.5 | 5.1948 | 493.5 | 25.8973 | 496.5 | 0.90817 | 499 | 3.2799 | 502 | 10.1708 | 504.5 | 11.537
507.5 | 16.5116 | 510 | 15.1547 | 513 | 28.4561 | 515.5 | 11.3642 | 518.5 | 22.272 | 521.5 | 20.4654 | 524.5 | 24.864 | 527 | 18.1057 | 530 | 0.4233 | 532.5 | 4.1163 | 535.5 | 9.2187 | 538.5 | 4.8669 | 541 | 27.2535 | 544 | 26.2711 | 546.5 | 4.2125
549.5 | 14.229 | 552.5 | 0.49901 | 555 | 12.0084 | 558 | 29.2088 | 560.5 | 7.3982 | 563.5 | 19.7756 | 566.5 | 17.5758 | 569 | 2.8818 | 571.5 | 16.9501 | 574.5 | 25.4782 | 577.5 | 15.9709 | 580.5 | 15.0403 | 583 | 24.2792 | 586 | 31.8768 | 588.5 | 13.5379
591.5 | 26.1542 | 594.5 | 20.3925 | 597 | 7.0882 | 600 | 0.82393 | 602.5 | 16.7651 | 605.5 | 14.3637 | 608.5 | 0.86357 | 611 | 22.1549 | 614 | 26.4243 | 616.5 | 0.89193 | 619.5 | 20.8228 | 622.5 | 7.1417 | 625 | 2.3788 | 627.5 | 31.2002 | 630.5 | 9.413
633.5 | 25.7139 | 636 | 21.5669 | 639 | 26.1968 | 642 | 5.1753 | 644.5 | 20.9213 | 647.5 | 21.6912 | 650.5 | 0.94278 | 653 | 9.6294 | 655.5 | 7.6907 | 658.5 | 8.035 | 661.5 | 26.71 | 664.5 | 19.8194 | 667 | 14.7744 | 670 | 1.5991 | 672.5 | 3.5689
675.5 | 28.6636 | 678.5 | 13.4709 | 681 | 22.6182 | 684 | 24.1877 | 686.5 | 19.6561 | 689.5 | 0.93678 | 692.5 | 16.4315 | 695 | 20.469 | 698 | 0.10252 | 700.5 | 22.8529 | 703.5 | 11.3345 | 706.5 | 29.6357 | 709 | 26.0982 | 711.5 | 15.1812 | 714.5 | 10.6102
717.5 | 11.2835 | 720 | 24.6646 | 723 | 25.252 | 725.5 | 15.097 | 728.5 | 13.5928 | 731.5 | 3.1458 | 734.5 | 27.0642 | 737 | 9.4384 | 740 | 30.6971 | 742.5 | 11.2788 | 745.5 | 21.6893 | 748.5 | 1.9742 | 751 | 4.1964 | 754 | 31.0657 | 756.5 | 11.1449
759.5 | 6.4893 | 762 | 27.7887 | 765 | 12.616 | 767.5 | 4.9097 | 770.5 | 0.14412 | 773.5 | 24.4012 | 776 | 7.5326 | 779 | 28.2715 | 782 | 19.6502 | 784.5 | 0.92064 | 787.5 | 1.9702 | 790.5 | 17.004 | 793 | 1.1588 | 795.5 | 20.1382 | 798.5 | 0.96667
801.5 | 0.94021 | 804 | 11.9854 | 807 | 14.7935 | 809.5 | 26.1752 | 812.5 | 17.0372 | 815.5 | 21.2214 | 818 | 0.54556 | 821 | 4.7769 | 824 | 30.9651 | 826.5 | 11.2282 | 829.5 | 12.4223 | 832.5 | 20.6726 | 835 | 23.4192 | 838 | 31.8088 | 840.5 | 4.1262
843.5 | 3.9117 | 846 | 1.8726 | 849 | 0.77047 | 852 | 19.2487 | 854.5 | 16.6566 | 857.5 | 28.9894 | 860.5 | 7.7647 | 863 | 30.3108 | 865.5 | 19.0336 | 868.5 | 4.7429 | 871.5 | 19.1811 | 874 | 22.6507 | 877 | 8.1181 | 879.5 | 20.9377 | 882.5 | 0.49473
885.5 | 14.5423 | 888 | 18.0524 | 891 | 0.92992 | 894 | 15.9477 | 896.5 | 23.7737 | 899.5 | 28.2673 | 902 | 13.9469 | 905 | 20.6988 | 907.5 | 10.0858 | 910.5 | 28.4146 | 913.5 | 12.9739 | 916 | 7.875 | 919 | 10.9766 | 921.5 | 31.6731 | 924.5 | 0.50239
927.5 | 24.9659 | 930 | 24.4162 | 932 | 22.8586 | 935.5 | 13.9987 | 938.5 | 9.7095 | 941.5 | 27.4884 | 944 | 8.5608 | 947 | 27.8839 | 950 | 3.2313 | 952.5 | 10.7753 | 955.5 | 27.5967 | 958 | 12.5355 | 961 | 31.2574 | 963.5 | 28.5603 | 966.5 | 5.567
969.5 | 13.1453 | 972.5 | 29.4419 | 975 | 28.4561 | 978 | 16.0549 | 980.5 | 10.8277 | 983.5 | 20.2346 | 986 | 10.9692 | 989 | 18.1609 | 991.5 | 10.3744 | 994.5 | 21.941 | 997.5 | 34.865 | 1000 | 18.5337 | 1003 | 2.8919 | 1005.5 | 9.9313 | 1008.5 | 22.5207
1011.5 | 6.5804 | 1014 | 15.4758 | 1017 | 27.2845 | 1020 | 13.5342 | 1022.5 | 15.1579 | 1025.5 | 26.2739 | 1028 | 10.1389 | 1031 | 30.1774 | 1033.5 | 3.7425 | 1036.5 | 228.1741 | 1039.5 | 48.0093 | 1042.5 | 63.2752 | 1045 | 48.9163 | 1047.5 | 56.179 | 1050.5 | 11.5862
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!

## C-G Min
Average Conductor to Ground Resistances
Open Burn Test 11 |  |  | 2006-11-20 | 12:58
Mixed | 7-C | Tray A | IRMS | 1
0 | 250 kW
Burner Time | A1-G |  | Burner Time | A2-G | Burner Time | B3-G | Burner Time | B4-G | Burner Time | C5-G | Burner Time | C6-G
-200.8 | 257138 |  | -191.9 | 259138 | -186.3 | 253938 | -183 | 253938 | -180.8 | 257238 | -178.4 | 259738
-158.9 | 257138 |  | -149.9 | 259138 | -144.3 | 253938 | -141 | 253938 | -138.8 | 257238 | -136.5 | 259738
-116.9 | 257138 |  | -107.9 | 259138 | -102.3 | 253938 | -99 | 253938 | -96.8 | 257238 | -94.5 | 259738
-74.9 | 257138 |  | -65.9 | 259138 | -60.3 | 253938 | -57 | 253938 | -54.7 | 257238 | -52.4 | 259738
-32.9 | 257138 |  | -23.9 | 259138 | -18.3 | 253938 | -14.9 | 253938 | -12.7 | 257238 | -10.5 | 259738
9.2 | 257138 |  | 18.1 | 259138 | 23.8 | 253938 | 27 | 253938 | 29.2 | 257238 | 31.7 | 259738
51.1 | 257138 |  | 60.1 | 259138 | 65.7 | 253938 | 69 | 253938 | 71.2 | 257238 | 73.5 | 259738
93.1 | 257138 |  | 102.1 | 259138 | 107.7 | 253938 | 111 | 253938 | 113.2 | 257238 | 115.5 | 259738
135.1 | 257138 |  | 144.1 | 259138 | 149.7 | 253938 | 153 | 253938 | 155.2 | 257238 | 157.5 | 259738
177.1 | 257138 |  | 186.1 | 259138 | 191.7 | 744.1745 | 195 | 186.207 | 197.2 | 257237.9999 | 199.5 | 259738
219.1 | 257138 |  | 228.1 | 259138 | 233.7 | 82.8259 | 237 | 57.9116 | 239.2 | 11842.6364 | 241.5 | 52447.6
261.1 | 458.1814 |  | 270.1 | 340.7049 | 275.7 | 15.0407 | 279 | 22.3236 | 281.2 | 118.8493 | 283.5 | 141.6173
303.1 | 32.0986 |  | 312.1 | 26.817 | 317.7 | 4.1139 | 321 | 4.7581 | 323.2 | 23.8989 | 325.5 | 67.0833
345.1 | 7.6379 |  | 354.1 | 10.8005 | 359.7 | 4.3456 | 363 | 3.3095 | 365.2 | 3.808 | 367.5 | 3.8065
387.1 | 1.7377 |  | 396.1 | 3.98 | 401.7 | 10.2671 | 405 | 3.0589 | 407.2 | 2.5396 | 409.5 | 5.5195
429.1 | 2.5141 |  | 438.1 | 1.7018 | 443.8 | 2.2716 | 447 | 6.6163 | 449.2 | 3.0737 | 451.6 | 0.66565
471.1 | 1.5473 |  | 480.1 | 2.0746 | 485.7 | 2.4729 | 489 | 4.7793 | 491.2 | 8.5659 | 493.5 | 4.7312
512.9 | 12.7714 |  | 522.1 | 1.9953 | 527.6 | 1.9572 | 531 | 6.7069 | 533.1 | 4.577 | 535.5 | 0.63439
555.1 | 2.0381 |  | 564 | 4.4099 | 569.7 | 16.1461 | 573 | 1.9077 | 575.2 | 0.64059 | 577.4 | 0.66565
597.1 | 0.75116 |  | 606.1 | 0.71213 | 611.7 | 0.64085 | 614.9 | 3.891 | 617.2 | 7.5902 | 619.4 | 0.6659
639 | 6.6631 |  | 648 | 0.63415 | 653.6 | 0.99647 | 657 | 1.2291 | 659.2 | 5.0952 | 661.4 | 0.62711
681.1 | 14.8384 |  | 690.1 | 0.63587 | 695.7 | 12.7576 | 698.9 | 16.1519 | 701.2 | 12.0418 | 703.4 | 2.593
722.9 | 12.6901 |  | 732.1 | 4.6581 | 737.6 | 3.5231 | 741 | 3.7677 | 743.1 | 2.4453 | 745.5 | 0.62759
764.9 | 1.42 |  | 774 | 8.9887 | 779.6 | 2.4347 | 782.8 | 2.6887 | 785.1 | 0.62735 | 787.4 | 7.237
806.9 | 0.63488 |  | 816 | 1.0253 | 821.6 | 12.6055 | 824.9 | 5.6574 | 827.1 | 0.62711 | 829.5 | 7.1088
849 | 0.79485 |  | 858 | 9.2176 | 863.5 | 6.2032 | 866.9 | 9.5521 | 869.2 | 1.092 | 871.2 | 4.8579
891 | 0.63785 |  | 899.9 | 11.5236 | 905.5 | 5.5985 | 908.8 | 6.532 | 911.2 | 0.63073 | 913.2 | 0.85912
932.7 | 11.1369 |  | 942 | 4.7619 | 947.5 | 2.9364 | 950.6 | 1.4986 | 953.1 | 3.6022 | 955.3 | 0.62759
975.1 | 12.241 |  | 983.9 | 1.739 | 989.6 | 11.7887 | 992.8 | 4.3968 | 995.2 | 1.8354 | 997.2 | 1.7188
1017 | 8.0474 |  | 1025.9 | 5.2657 | 1031.6 | 9.5432 | 1034.8 | 23.0185 | 1037.2 | 4.2253 | 1039.3 | 2.872
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!

## C5-C6
Open Burn Test 11 |  |  | 2006-11-20 | 12:58 |  |  | Vs = |  | 160.4017 |  | R = | 100
Mixed | 7-C | Tray A | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 5 & 6 | Cable C | Odd-Even
Time-29 | N11 | N12 | Time-30 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R6-G | R5-6
39041.5361 | 1 | 0 | 39041.5361 | 1 | 0 |  | -167.5 | 39.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262638 | 262638 | 262637.9994
39041.5366 | 1 | 0 | 39041.5366 | 1 | 0 |  | -125.5 | 81.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262638 | 262638 | 262637.9994
39041.537 | 1 | 0 | 39041.5371 | 1 | 0 |  | -83.5 | 123.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262638 | 262638 | 262637.9994
39041.5375 | 1 | 0 | 39041.5376 | 1 | 0 |  | -41 | 166 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262638 | 262638 | 262637.9994
39041.538 | 1 | 0 | 39041.538 | 1 | 0 |  | 0.5 | 207.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262638 | 262638 | 262637.9994
39041.5385 | 1 | 0 | 39041.5385 | 1 | 0 |  | 42.5 | 249.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262638 | 262638 | 262637.9994
39041.539 | 1 | 0 | 39041.539 | 1 | 0 |  | 84.5 | 291.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262638 | 262638 | 262637.9994
39041.5395 | 1 | 0 | 39041.5395 | 1 | 0 |  | 126.5 | 333.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262638 | 262638 | 262637.9994
39041.54 | 1 | 0 | 39041.54 | 1 | 0 |  | 168.5 | 375.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262638 | 262638 | 262637.9994
39041.5405 | 1 | 0 | 39041.5405 | 1 | 0 |  | 210.5 | 417.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262638 | 262638 | 262637.9994
39041.5409 | 22 | 0 | 39041.5409 | 20 | 15 |  | 252.5 | 459.5 | 1.3431 | 0 | 1.221 | 0.91575 | 0.013431 | 0 | 0.01221 | 0.0091575 | 0.013431 | 0.0030525 | 11842.6364 | 52447.6 | 11842.6229
39041.5414 | 352 | 134 | 39041.5414 | 154 | 19 |  | 294.5 | 501.5 | 21.4896 | 8.1807 | 9.4017 | 1.16 | 0.2149 | 0.081807 | 0.094017 | 0.0116 | 0.13309 | 0.082418 | 1079.4971 | 1856.3355 | 1516.3592
39041.5419 | 1954 | 222 | 39041.5419 | 1690 | 95 |  | 336.5 | 543.5 | 119.2918 | 13.5531 | 103.1746 | 5.7998 | 1.1929 | 0.13553 | 1.0317 | 0.057998 | 1.0574 | 0.97375 | 48.0619 | 67.0833 | 81.6339
39041.5424 | 2531 | 0 | 39041.5424 | 2423 | 0 |  | 378.5 | 585.5 | 154.5177 | 0 | 147.9243 | 0 | 1.5452 | 0 | 1.4792 | 0 | 1.5452 | 1.4792 | 3.808 | 8.435 | 2.2628
39041.5429 | 2414 | 0 | 39041.5429 | 2133 | 0 |  | 420.5 | 627.5 | 147.3748 | 0 | 130.2198 | 0 | 1.4737 | 0 | 1.3022 | 0 | 1.4737 | 1.3022 | 8.8393 | 23.1777 | 7.3655
39041.5434 | 2147 | 0 | 39041.5434 | 2493 | 0 |  | 462.5 | 669.5 | 131.0745 | 0 | 152.1978 | 0 | 1.3107 | 0 | 1.522 | 0 | 1.3107 | 1.522 | 22.3745 | 5.3903 | 21.0637
39041.5439 | 2326 | 0 | 39041.5439 | 2176 | 0 |  | 504.5 | 711.5 | 142.0024 | 0 | 132.8449 | 0 | 1.42 | 0 | 1.3284 | 0 | 1.42 | 1.3284 | 12.957 | 20.7436 | 11.537
39041.5443 | 2485 | 0 | 39041.5444 | 2491 | 0 |  | 546.5 | 753.5 | 151.7094 | 0 | 152.0757 | 0 | 1.5171 | 0 | 1.5208 | 0 | 1.5171 | 1.5208 | 5.7296 | 5.4749 | 4.2125
39041.5448 | 2286 | 0 | 39041.5448 | 2149 | 0 |  | 588.5 | 795.5 | 139.5604 | 0 | 131.1966 | 0 | 1.3956 | 0 | 1.312 | 0 | 1.3956 | 1.312 | 14.9335 | 22.2606 | 13.5379
39041.5453 | 2370 | 0 | 39041.5453 | 2610 | 0 |  | 630.5 | 837.5 | 144.6886 | 0 | 159.3407 | 0 | 1.4469 | 0 | 1.5934 | 0 | 1.4469 | 1.5934 | 10.8599 | 0.6659 | 9.413
39041.5458 | 2500 | 0 | 39041.5458 | 2039 | 0 |  | 672.5 | 879.5 | 152.6252 | 0 | 124.4811 | 0 | 1.5263 | 0 | 1.2448 | 0 | 1.5263 | 1.2448 | 5.0952 | 28.8563 | 3.5689
39041.5463 | 2345 | 0 | 39041.5463 | 2254 | 0 |  | 714.5 | 921.5 | 143.1624 | 0 | 137.6068 | 0 | 1.4316 | 0 | 1.3761 | 0 | 1.4316 | 1.3761 | 12.0418 | 16.5652 | 10.6102
39041.5468 | 2334 | 0 | 39041.5468 | 2526 | 0 |  | 756.5 | 963.5 | 142.4908 | 0 | 154.2125 | 0 | 1.4249 | 0 | 1.5421 | 0 | 1.4249 | 1.5421 | 12.5698 | 4.0135 | 11.1449
39041.5473 | 2611 | 0 | 39041.5473 | 2064 | 0 |  | 798.5 | 1005.5 | 159.4017 | 0 | 126.0073 | 0 | 1.594 | 0 | 1.2601 | 0 | 1.594 | 1.2601 | 0.62735 | 27.2955 | 0.96667
39041.5477 | 2487 | 0 | 39041.5478 | 2453 | 0 |  | 840.5 | 1047.5 | 151.8315 | 0 | 149.7558 | 0 | 1.5183 | 0 | 1.4976 | 0 | 1.5183 | 1.4976 | 5.6446 | 7.1088 | 4.1262
39041.5482 | 2599 | 0 | 39041.5482 | 2408 | 0 |  | 882.5 | 1089.5 | 158.6691 | 0 | 147.0085 | 0 | 1.5867 | 0 | 1.4701 | 0 | 1.5867 | 1.4701 | 1.092 | 9.1105 | 0.49473
39041.5487 | 2574 | 0 | 39041.5487 | 2605 | 0 |  | 924.5 | 1131.5 | 157.1429 | 0 | 159.0354 | 0 | 1.5714 | 0 | 1.5904 | 0 | 1.5714 | 1.5904 | 2.0738 | 0.85912 | 0.50239
39041.5492 | 2454 | 0 | 39041.5492 | 2590 | 0 |  | 966.5 | 1173.5 | 149.8168 | 0 | 158.1197 | 0 | 1.4982 | 0 | 1.5812 | 0 | 1.4982 | 1.5812 | 7.0652 | 1.4432 | 5.567
39041.5497 | 2122 | 0 | 39041.5497 | 2238 | 0 |  | 1008.5 | 1215.5 | 129.5482 | 0 | 136.63 | 0 | 1.2955 | 0 | 1.3663 | 0 | 1.2955 | 1.3663 | 23.8162 | 17.3986 | 22.5207
39041.5502 | 2325 | 0 | 39041.5502 | 2394 | 0 |  | 1050.5 | 1257.5 | 141.9414 | 0 | 146.1538 | 0 | 1.4194 | 0 | 1.4615 | 0 | 1.4194 | 1.4615 | 13.0056 | 9.7485 | 11.5862

## B4-C6
Open Burn Test 11 |  |  | 2006-11-20 | 12:58 |  |  | Vs = |  | 160.4628 |  | R = | 100
Mixed | 7-C | Tray A | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 4 & 6 | Cable B | Even - | Cable C |  | Even
Time-27 | N11 | N12 | Time-28 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R6-G | R4-6
39041.536 | 1 | 0 | 39041.5361 | 1 | 0 |  | -170 | 37 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262738 | 262738 | 262737.9994
39041.5365 | 1 | 0 | 39041.5366 | 1 | 0 |  | -128 | 79 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262738 | 262738 | 262737.9994
39041.537 | 1 | 0 | 39041.537 | 1 | 0 |  | -86 | 121 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262738 | 262738 | 262737.9994
39041.5375 | 1 | 0 | 39041.5375 | 1 | 0 |  | -44 | 163 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262738 | 262738 | 262737.9994
39041.538 | 1 | 0 | 39041.538 | 1 | 0 |  | -2 | 205 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262738 | 262738 | 262737.9994
39041.5385 | 1 | 0 | 39041.5385 | 1 | 0 |  | 40 | 247 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262738 | 262738 | 262737.9994
39041.539 | 1 | 0 | 39041.539 | 1 | 0 |  | 82 | 289 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262738 | 262738 | 262737.9994
39041.5394 | 1 | 0 | 39041.5395 | 1 | 0 |  | 124 | 331 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262738 | 262738 | 262737.9994
39041.5399 | 1 | 0 | 39041.54 | 1 | 0 |  | 166 | 373 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262738 | 262738 | 262737.9994
39041.5404 | 919 | 1 | 39041.5404 | 1 | 0 |  | 208 | 415 | 56.105 | 0.06105 | 0.06105 | 0 | 0.56105 | 0.0006105 | 0.0006105 | 0 | 0.56044 | 0.0006105 | 186.207 | 262737.9999 | 170773.0025
39041.5409 | 1418 | 1 | 39041.5409 | 1 | 0 |  | 250 | 457 | 86.569 | 0.06105 | 0.06105 | 0 | 0.86569 | 0.0006105 | 0.0006105 | 0 | 0.86508 | 0.0006105 | 85.4185 | 262738.0001 | 120891.9876
39041.5414 | 2093 | 1 | 39041.5414 | 8 | 0 |  | 292 | 499 | 127.7778 | 0.06105 | 0.4884 | 0 | 1.2778 | 0.0006105 | 0.004884 | 0 | 1.2772 | 0.004884 | 25.5918 | 32754.75 | 53275.3508
39041.5419 | 2509 | 0 | 39041.5419 | 1298 | 0 |  | 334 | 541 | 153.1746 | 0 | 79.243 | 0 | 1.5317 | 0 | 0.79243 | 0 | 1.5317 | 0.79243 | 4.7581 | 102.4946 | 3.2263
39041.5424 | 2205 | 0 | 39041.5424 | 2532 | 0 |  | 376 | 583 | 134.6154 | 0 | 154.5788 | 0 | 1.3462 | 0 | 1.5458 | 0 | 1.3462 | 1.5458 | 19.2009 | 3.8065 | 17.8548
39041.5428 | 2168 | 0 | 39041.5429 | 2001 | 0 |  | 418 | 625 | 132.3565 | 0 | 122.1612 | 0 | 1.3236 | 0 | 1.2216 | 0 | 1.3236 | 1.2216 | 21.2352 | 31.3533 | 19.9117
39041.5433 | 2320 | 0 | 39041.5434 | 2611 | 0 |  | 460 | 667 | 141.6361 | 0 | 159.4017 | 0 | 1.4164 | 0 | 1.594 | 0 | 1.4164 | 1.594 | 13.2922 | 0.66565 | 11.8759
39041.5438 | 2355 | 0 | 39041.5438 | 2241 | 0 |  | 502 | 709 | 143.7729 | 0 | 136.8132 | 0 | 1.4377 | 0 | 1.3681 | 0 | 1.4377 | 1.3681 | 11.6085 | 17.286 | 10.1708
39041.5443 | 2061 | 0 | 39041.5443 | 2139 | 0 |  | 544 | 751 | 125.8242 | 0 | 130.5861 | 0 | 1.2582 | 0 | 1.3059 | 0 | 1.2582 | 1.3059 | 27.5294 | 22.8789 | 26.2711
39041.5448 | 1975 | 0 | 39041.5448 | 2611 | 0 |  | 586 | 793 | 120.5739 | 0 | 159.4017 | 0 | 1.2057 | 0 | 1.594 | 0 | 1.2057 | 1.594 | 33.0825 | 0.66565 | 31.8768
39041.5453 | 1985 | 0 | 39041.5453 | 2416 | 0 |  | 627.5 | 834.5 | 121.1844 | 0 | 147.4969 | 0 | 1.2118 | 0 | 1.475 | 0 | 1.2118 | 1.475 | 32.4121 | 8.7906 | 31.2002
39041.5458 | 2548 | 0 | 39041.5458 | 2612 | 0 |  | 670 | 877 | 155.5556 | 0 | 159.4628 | 0 | 1.5556 | 0 | 1.5946 | 0 | 1.5556 | 1.5946 | 3.1546 | 0.62711 | 1.5991
39041.5462 | 2255 | 0 | 39041.5463 | 2168 | 0 |  | 711.5 | 918.5 | 137.6679 | 0 | 132.3565 | 0 | 1.3767 | 0 | 1.3236 | 0 | 1.3767 | 1.3236 | 16.5579 | 21.2352 | 15.1812
39041.5467 | 1987 | 0 | 39041.5468 | 2251 | 0 |  | 754 | 961 | 121.3065 | 0 | 137.4237 | 0 | 1.2131 | 0 | 1.3742 | 0 | 1.2131 | 1.3742 | 32.2788 | 16.765 | 31.0657
39041.5472 | 2164 | 0 | 39041.5472 | 2451 | 0 |  | 795.5 | 1002.5 | 132.1123 | 0 | 149.6337 | 0 | 1.3211 | 0 | 1.4963 | 0 | 1.3211 | 1.4963 | 21.4593 | 7.237 | 20.1382
39041.5477 | 1976 | 0 | 39041.5477 | 2055 | 0 |  | 838 | 1045 | 120.6349 | 0 | 125.4579 | 0 | 1.2063 | 0 | 1.2546 | 0 | 1.2063 | 1.2546 | 33.0152 | 27.9017 | 31.8088
39041.5482 | 2150 | 0 | 39041.5482 | 2050 | 0 |  | 879.5 | 1086.5 | 131.2576 | 0 | 125.1526 | 0 | 1.3126 | 0 | 1.2515 | 0 | 1.3126 | 1.2515 | 22.2502 | 28.2137 | 20.9377
39041.5487 | 1978 | 0 | 39041.5487 | 2243 | 0 |  | 921.5 | 1128.5 | 120.757 | 0 | 136.9353 | 0 | 1.2076 | 0 | 1.3694 | 0 | 1.2076 | 1.3694 | 32.8807 | 17.1815 | 31.6731
39041.5492 | 2025 | 0 | 39041.5492 | 2484 | 0 |  | 963.5 | 1170.5 | 123.6264 | 0 | 151.6484 | 0 | 1.2363 | 0 | 1.5165 | 0 | 1.2363 | 1.5165 | 29.7965 | 5.8124 | 28.5603
39041.5497 | 2360 | 0 | 39041.5497 | 2111 | 0 |  | 1005.5 | 1212.5 | 144.0781 | 0 | 128.8767 | 0 | 1.4408 | 0 | 1.2888 | 0 | 1.4408 | 1.2888 | 11.372 | 24.5088 | 9.9313
39041.5501 | 1672 | 0 | 39041.5502 | 2555 | 0 |  | 1047.5 | 1254.5 | 102.0757 | 0 | 155.9829 | 0 | 1.0208 | 0 | 1.5598 | 0 | 1.0208 | 1.5598 | 57.1998 | 2.872 | 56.179

## B4-C5
Open Burn Test 11 |  |  | 2006-11-20 | 12:58 |  |  | Vs = |  | 157.105 |  | R = | 100
Mixed | 7-C | Tray A | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 4 & 5 | Cable B | Even - | Cable C |  | Odd
Time-25 | N11 | N12 | Time-26 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R5-G | R4-5
39041.536 | 1 | 0 | 39041.536 | 1 | 0 |  | -173 | 34 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257238 | 257238 | 257237.9994
39041.5365 | 1 | 0 | 39041.5365 | 1 | 0 |  | -131 | 76 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257238 | 257238 | 257237.9994
39041.537 | 1 | 0 | 39041.537 | 1 | 0 |  | -89 | 118 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257238 | 257238 | 257237.9994
39041.5375 | 1 | 0 | 39041.5375 | 1 | 0 |  | -47 | 160 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257238 | 257238 | 257237.9994
39041.538 | 1 | 0 | 39041.538 | 1 | 0 |  | -4.5 | 202.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257238 | 257238 | 257237.9994
39041.5384 | 1 | 0 | 39041.5385 | 1 | 0 |  | 37 | 244 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257238 | 257238 | 257237.9994
39041.5389 | 1 | 0 | 39041.5389 | 1 | 0 |  | 79 | 286 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257238 | 257238 | 257237.9994
39041.5394 | 1 | 0 | 39041.5394 | 1 | 0 |  | 121 | 328 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257238 | 257238 | 257237.9994
39041.5399 | 1 | 0 | 39041.5399 | 1 | 0 |  | 163 | 370 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257238 | 257238 | 257237.9994
39041.5404 | 572 | 1 | 39041.5404 | 1 | 0 |  | 205 | 412 | 34.9206 | 0.06105 | 0.06105 | 0 | 0.34921 | 0.0006105 | 0.0006105 | 0 | 0.3486 | 0.0006105 | 350.5046 | 257237.9999 | 199960.2664
39041.5409 | 1630 | 1 | 39041.5409 | 2 | 0 |  | 247 | 454 | 99.5116 | 0.06105 | 0.1221 | 0 | 0.99512 | 0.0006105 | 0.001221 | 0 | 0.99451 | 0.001221 | 57.9116 | 128569 | 94164.7594
39041.5414 | 2104 | 1 | 39041.5414 | 714 | 0 |  | 289 | 496 | 128.4493 | 0.06105 | 43.5897 | 0 | 1.2845 | 0.0006105 | 0.4359 | 0 | 1.2839 | 0.4359 | 22.3236 | 260.4174 | 33842.5108
39041.5418 | 2048 | 0 | 39041.5419 | 2077 | 0 |  | 331 | 538 | 125.0305 | 0 | 126.801 | 0 | 1.2503 | 0 | 1.268 | 0 | 1.2503 | 1.268 | 25.6533 | 23.8989 | 24.403
39041.5423 | 1965 | 0 | 39041.5423 | 2386 | 0 |  | 373 | 580 | 119.9634 | 0 | 145.6654 | 0 | 1.1996 | 0 | 1.4567 | 0 | 1.1996 | 1.4567 | 30.9608 | 7.8533 | 29.7612
39041.5428 | 2497 | 0 | 39041.5428 | 2481 | 0 |  | 415 | 622 | 152.442 | 0 | 151.4652 | 0 | 1.5244 | 0 | 1.5147 | 0 | 1.5244 | 1.5147 | 3.0589 | 3.7235 | 1.5345
39041.5433 | 2022 | 0 | 39041.5433 | 2270 | 0 |  | 457 | 664 | 123.4432 | 0 | 138.5836 | 0 | 1.2344 | 0 | 1.3858 | 0 | 1.2344 | 1.3858 | 27.269 | 13.3648 | 26.0346
39041.5438 | 2456 | 0 | 39041.5438 | 2089 | 0 |  | 499 | 706 | 149.9389 | 0 | 127.5336 | 0 | 1.4994 | 0 | 1.2753 | 0 | 1.4994 | 1.2753 | 4.7793 | 23.1872 | 3.2799
39041.5443 | 2003 | 0 | 39041.5443 | 2293 | 0 |  | 541 | 748 | 122.2833 | 0 | 139.9878 | 0 | 1.2228 | 0 | 1.3999 | 0 | 1.2228 | 1.3999 | 28.4763 | 12.2276 | 27.2535
39041.5448 | 2050 | 0 | 39041.5448 | 2557 | 0 |  | 583 | 790 | 125.1526 | 0 | 156.105 | 0 | 1.2515 | 0 | 1.5611 | 0 | 1.2515 | 1.5611 | 25.5307 | 0.64059 | 24.2792
39041.5452 | 2477 | 0 | 39041.5453 | 2069 | 0 |  | 625 | 832 | 151.221 | 0 | 126.3126 | 0 | 1.5122 | 0 | 1.2631 | 0 | 1.5122 | 1.2631 | 3.891 | 24.378 | 2.3788
39041.5457 | 2216 | 0 | 39041.5458 | 2440 | 0 |  | 667 | 874 | 135.2869 | 0 | 148.9621 | 0 | 1.3529 | 0 | 1.4896 | 0 | 1.3529 | 1.4896 | 16.1273 | 5.4664 | 14.7744
39041.5462 | 2021 | 0 | 39041.5462 | 2126 | 0 |  | 709 | 916 | 123.3822 | 0 | 129.7924 | 0 | 1.2338 | 0 | 1.2979 | 0 | 1.2338 | 1.2979 | 27.332 | 21.0433 | 26.0982
39041.5467 | 2435 | 0 | 39041.5467 | 2119 | 0 |  | 751 | 958 | 148.6569 | 0 | 129.3651 | 0 | 1.4866 | 0 | 1.2937 | 0 | 1.4866 | 1.2937 | 5.683 | 21.4431 | 4.1964
39041.5472 | 2506 | 0 | 39041.5472 | 2394 | 0 |  | 793 | 1000 | 152.9915 | 0 | 146.1538 | 0 | 1.5299 | 0 | 1.4615 | 0 | 1.5299 | 1.4615 | 2.6887 | 7.4929 | 1.1588
39041.5477 | 2064 | 0 | 39041.5477 | 2014 | 0 |  | 835 | 1042 | 126.0073 | 0 | 122.9548 | 0 | 1.2601 | 0 | 1.2295 | 0 | 1.2601 | 1.2295 | 24.6793 | 27.7746 | 23.4192
39041.5482 | 2349 | 0 | 39041.5482 | 2036 | 0 |  | 877 | 1084 | 143.4066 | 0 | 124.2979 | 0 | 1.4341 | 0 | 1.243 | 0 | 1.4341 | 1.243 | 9.5521 | 26.3939 | 8.1181
39041.5486 | 2290 | 0 | 39041.5487 | 2181 | 0 |  | 919 | 1126 | 139.8046 | 0 | 133.1502 | 0 | 1.398 | 0 | 1.3315 | 0 | 1.398 | 1.3315 | 12.3747 | 17.9908 | 10.9766
39041.5491 | 1943 | 0 | 39041.5492 | 2069 | 0 |  | 961 | 1168 | 118.6203 | 0 | 126.3126 | 0 | 1.1862 | 0 | 1.2631 | 0 | 1.1862 | 1.2631 | 32.4436 | 24.378 | 31.2574
39041.5496 | 2465 | 0 | 39041.5496 | 2527 | 0 |  | 1003 | 1210 | 150.4884 | 0 | 154.2735 | 0 | 1.5049 | 0 | 1.5427 | 0 | 1.5049 | 1.5427 | 4.3968 | 1.8354 | 2.8919
39041.5501 | 1716 | 0 | 39041.5501 | 2332 | 0 |  | 1045 | 1252 | 104.7619 | 0 | 142.3687 | 0 | 1.0476 | 0 | 1.4237 | 0 | 1.0476 | 1.4237 | 49.9639 | 10.3508 | 48.9163

## B3-C6
Open Burn Test 11 |  |  | 2006-11-20 | 12:58 |  |  | Vs = |  | 160.3407 |  | R = | 100
Mixed | 7-C | Tray A | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 3 & 6 | Cable B | Odd - | Cable C |  | Even
Time-23 | N11 | N12 | Time-24 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R6-G | R3-6
39041.536 | 1 | 0 | 39041.536 | 1 | 0 |  | -175.5 | 31.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262538 | 262538 | 262537.9994
39041.5365 | 1 | 0 | 39041.5365 | 1 | 0 |  | -133.5 | 73.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262538 | 262538 | 262537.9994
39041.537 | 1 | 0 | 39041.537 | 1 | 0 |  | -91.5 | 115.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262538 | 262538 | 262537.9994
39041.5374 | 1 | 0 | 39041.5375 | 1 | 0 |  | -49.5 | 157.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262538 | 262538 | 262537.9994
39041.5379 | 1 | 0 | 39041.5379 | 1 | 0 |  | -7.5 | 199.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262538 | 262538 | 262537.9994
| 1 | 0 | 39041.5384 | 1 | 0 |  | 35 | 242 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262538 | 262538 | 262537.9994
39041.5389 | 1 | 0 | 39041.5389 | 1 | 0 |  | 76.5 | 283.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262538 | 262538 | 262537.9994
39041.5394 | 1 | 0 | 39041.5394 | 1 | 0 |  | 118.5 | 325.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262538 | 262538 | 262537.9994
39041.5399 | 1 | 0 | 39041.5399 | 1 | 0 |  | 160.5 | 367.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262538 | 262538 | 262537.9994
39041.5404 | 312 | 1 | 39041.5404 | 1 | 0 |  | 202.5 | 409.5 | 19.0476 | 0.06105 | 0.06105 | 0 | 0.19048 | 0.0006105 | 0.0006105 | 0 | 0.18987 | 0.0006105 | 744.1745 | 262538 | 231249.9175
39041.5408 | 1437 | 1 | 39041.5409 | 1 | 0 |  | 244.5 | 451.5 | 87.7289 | 0.06105 | 0.06105 | 0 | 0.87729 | 0.0006105 | 0.0006105 | 0 | 0.87668 | 0.0006105 | 82.8259 | 262538.0001 | 118792.7522
39041.5413 | 2283 | 0 | 39041.5413 | 1087 | 0 |  | 286.5 | 493.5 | 139.3773 | 0 | 66.3614 | 0 | 1.3938 | 0 | 0.66361 | 0 | 1.3938 | 0.66361 | 15.0407 | 141.6173 | 13.647
39041.5418 | 2439 | 0 | 39041.5418 | 971 | 0 |  | 328.5 | 535.5 | 148.9011 | 0 | 59.2796 | 0 | 1.489 | 0 | 0.5928 | 0 | 1.489 | 0.5928 | 7.6827 | 170.482 | 6.1936
39041.5423 | 2517 | 0 | 39041.5423 | 2517 | 0 |  | 370.5 | 577.5 | 153.663 | 0 | 153.663 | 0 | 1.5366 | 0 | 1.5366 | 0 | 1.5366 | 1.5366 | 4.3456 | 4.3456 | 2.809
39041.5428 | 2072 | 0 | 39041.5428 | 2284 | 0 |  | 412.5 | 619.5 | 126.4957 | 0 | 139.4383 | 0 | 1.265 | 0 | 1.3944 | 0 | 1.265 | 1.3944 | 26.7558 | 14.9904 | 25.4908
| 2318 | 0 | 39041.5433 | 2188 | 0 |  | 455 | 662 | 141.514 | 0 | 133.5775 | 0 | 1.4151 | 0 | 1.3358 | 0 | 1.4151 | 1.3358 | 13.3037 | 20.0356 | 11.8886
39041.5438 | 2563 | 0 | 39041.5438 | 2428 | 0 |  | 496.5 | 703.5 | 156.4713 | 0 | 148.2295 | 0 | 1.5647 | 0 | 1.4823 | 0 | 1.5647 | 1.4823 | 2.4729 | 8.1705 | 0.90817
39041.5442 | 2469 | 0 | 39041.5443 | 2063 | 0 |  | 538.5 | 745.5 | 150.7326 | 0 | 125.9463 | 0 | 1.5073 | 0 | 1.2595 | 0 | 1.5073 | 1.2595 | 6.3742 | 27.3088 | 4.8669
39041.5447 | 2256 | 0 | 39041.5447 | 2060 | 0 |  | 580.5 | 787.5 | 137.7289 | 0 | 125.7631 | 0 | 1.3773 | 0 | 1.2576 | 0 | 1.3773 | 1.2576 | 16.4176 | 27.4942 | 15.0403
39041.5452 | 2418 | 0 | 39041.5452 | 2403 | 0 |  | 622.5 | 829.5 | 147.619 | 0 | 146.7033 | 0 | 1.4762 | 0 | 1.467 | 0 | 1.4762 | 1.467 | 8.6179 | 9.2959 | 7.1417
39041.5457 | 2168 | 0 | 39041.5457 | 2344 | 0 |  | 664.5 | 871.5 | 132.3565 | 0 | 143.1013 | 0 | 1.3236 | 0 | 1.431 | 0 | 1.3236 | 1.431 | 21.143 | 12.0469 | 19.8194
39041.5462 | 2007 | 0 | 39041.5462 | 2560 | 0 |  | 706.5 | 913.5 | 122.5275 | 0 | 156.2882 | 0 | 1.2253 | 0 | 1.5629 | 0 | 1.2253 | 1.5629 | 30.861 | 2.593 | 29.6357
39041.5467 | 2537 | 0 | 39041.5467 | 2610 | 0 |  | 748.5 | 955.5 | 154.884 | 0 | 159.3407 | 0 | 1.5488 | 0 | 1.5934 | 0 | 1.5488 | 1.5934 | 3.5231 | 0.62759 | 1.9742
39041.5472 | 2219 | 0 | 39041.5472 | 2327 | 0 |  | 790.5 | 997.5 | 135.4701 | 0 | 142.0635 | 0 | 1.3547 | 0 | 1.4206 | 0 | 1.3547 | 1.4206 | 18.3587 | 12.8655 | 17.004
39041.5477 | 2153 | 0 | 39041.5477 | 2253 | 0 |  | 832.5 | 1039.5 | 131.4408 | 0 | 137.5458 | 0 | 1.3144 | 0 | 1.3755 | 0 | 1.3144 | 1.3755 | 21.987 | 16.5726 | 20.6726
39041.5481 | 2119 | 0 | 39041.5481 | 2254 | 0 |  | 874 | 1081 | 129.3651 | 0 | 137.6068 | 0 | 1.2937 | 0 | 1.3761 | 0 | 1.2937 | 1.3761 | 23.9443 | 16.5209 | 22.6507
39041.5486 | 2402 | 0 | 39041.5486 | 2318 | 0 |  | 916 | 1123 | 146.6422 | 0 | 141.514 | 0 | 1.4664 | 0 | 1.4151 | 0 | 1.4664 | 1.4151 | 9.3414 | 13.3037 | 7.875
39041.5491 | 2305 | 0 | 39041.5491 | 2607 | 0 |  | 958 | 1165 | 140.7204 | 0 | 159.1575 | 0 | 1.4072 | 0 | 1.5916 | 0 | 1.4072 | 1.5916 | 13.9427 | 0.74338 | 12.5355
39041.5496 | 2191 | 0 | 39041.5496 | 2187 | 0 |  | 1000 | 1207 | 133.7607 | 0 | 133.5165 | 0 | 1.3376 | 0 | 1.3352 | 0 | 1.3376 | 1.3352 | 19.8713 | 20.0905 | 18.5337
39041.5501 | 1599 | 0 | 39041.5501 | 2031 | 0 |  | 1042.5 | 1249.5 | 97.619 | 0 | 123.9927 | 0 | 0.97619 | 0 | 1.2399 | 0 | 0.97619 | 1.2399 | 64.2514 | 29.3146 | 63.2752

## B3-C5
Open Burn Test 11 |  |  | 2006-11-20 | 12:58 |  |  | Vs = |  | 160.4628 |  | R = | 100
Mixed | 7-C | Tray A | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 3 & 5 | Cable B | Odd - | Cable C |  | Odd
Time-21 | N11 | N12 | Time-22 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R5-G | R3-5
39041.5359 | 1 | 0 | 39041.536 | 1 | 0 |  | -178.5 | 28.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262738 | 262738 | 262737.9994
39041.5364 | 1 | 0 | 39041.5364 | 1 | 0 |  | -136.5 | 70.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262738 | 262738 | 262737.9994
39041.5369 | 1 | 0 | 39041.5369 | 1 | 0 |  | -94.5 | 112.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262738 | 262738 | 262737.9994
39041.5374 | 1 | 0 | 39041.5374 | 1 | 0 |  | -52.5 | 154.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262738 | 262738 | 262737.9994
39041.5379 | 1 | 0 | 39041.5379 | 1 | 0 |  | -10.5 | 196.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262738 | 262738 | 262737.9994
39041.5384 | 1 | 0 | 39041.5384 | 1 | 0 |  | 31.5 | 238.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262738 | 262738 | 262737.9994
39041.5389 | 1 | 0 | 39041.5389 | 1 | 0 |  | 73.5 | 280.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262738 | 262738 | 262737.9994
39041.5394 | 1 | 0 | 39041.5394 | 1 | 0 |  | 115.5 | 322.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262738 | 262738 | 262737.9994
39041.5398 | 1 | 0 | 39041.5398 | 1 | 0 |  | 157.5 | 364.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262738 | 262738 | 262737.9994
39041.5403 | 139 | 1 | 39041.5403 | 1 | 0 |  | 199.5 | 406.5 | 8.486 | 0.06105 | 0.06105 | 0 | 0.08486 | 0.0006105 | 0.0006105 | 0 | 0.084249 | 0.0006105 | 1803.9035 | 262738 | 248743.3265
39041.5408 | 1037 | 1 | 39041.5408 | 1 | 0 |  | 241.5 | 448.5 | 63.3089 | 0.06105 | 0.06105 | 0 | 0.63309 | 0.0006105 | 0.0006105 | 0 | 0.63248 | 0.0006105 | 153.6082 | 262737.9999 | 158977.492
39041.5413 | 1846 | 0 | 39041.5413 | 1201 | 0 |  | 283.5 | 490.5 | 112.6984 | 0 | 73.3211 | 0 | 1.127 | 0 | 0.73321 | 0 | 1.127 | 0.73321 | 42.3824 | 118.8493 | 41.2555
39041.5418 | 2120 | 0 | 39041.5418 | 1917 | 0 |  | 325.5 | 532.5 | 129.4261 | 0 | 117.033 | 0 | 1.2943 | 0 | 1.1703 | 0 | 1.2943 | 1.1703 | 23.9802 | 37.109 | 22.6859
39041.5423 | 2257 | 0 | 39041.5423 | 1823 | 0 |  | 367.5 | 574.5 | 137.79 | 0 | 111.2943 | 0 | 1.3779 | 0 | 1.1129 | 0 | 1.3779 | 1.1129 | 16.4546 | 44.1788 | 15.0767
39041.5428 | 2053 | 0 | 39041.5428 | 2398 | 0 |  | 409.5 | 616.5 | 125.3358 | 0 | 146.398 | 0 | 1.2534 | 0 | 1.464 | 0 | 1.2534 | 1.464 | 28.0263 | 9.6072 | 26.7729
39041.5432 | 2570 | 0 | 39041.5433 | 2550 | 0 |  | 451.5 | 658.5 | 156.8987 | 0 | 155.6777 | 0 | 1.569 | 0 | 1.5568 | 0 | 1.569 | 1.5568 | 2.2716 | 3.0737 | 0.70261
39041.5437 | 2067 | 0 | 39041.5437 | 2421 | 0 |  | 493.5 | 700.5 | 126.1905 | 0 | 147.8022 | 0 | 1.2619 | 0 | 1.478 | 0 | 1.2619 | 1.478 | 27.1592 | 8.5659 | 25.8973
39041.5442 | 2375 | 0 | 39041.5442 | 2212 | 0 |  | 535.5 | 742.5 | 144.9939 | 0 | 135.0427 | 0 | 1.4499 | 0 | 1.3504 | 0 | 1.4499 | 1.3504 | 10.6686 | 18.8237 | 9.2187
39041.5447 | 2240 | 0 | 39041.5447 | 2013 | 0 |  | 577.5 | 784.5 | 136.7521 | 0 | 122.8938 | 0 | 1.3675 | 0 | 1.2289 | 0 | 1.3675 | 1.2289 | 17.3384 | 30.5703 | 15.9709
39041.5452 | 2152 | 0 | 39041.5452 | 2082 | 0 |  | 619.5 | 826.5 | 131.3797 | 0 | 127.1062 | 0 | 1.3138 | 0 | 1.2711 | 0 | 1.3138 | 1.2711 | 22.1366 | 26.243 | 20.8228
39041.5457 | 2054 | 0 | 39041.5457 | 2038 | 0 |  | 661.5 | 868.5 | 125.3968 | 0 | 124.42 | 0 | 1.254 | 0 | 1.2442 | 0 | 1.254 | 1.2442 | 27.964 | 28.9686 | 26.71
39041.5462 | 2331 | 0 | 39041.5462 | 2044 | 0 |  | 703.5 | 910.5 | 142.3077 | 0 | 124.7863 | 0 | 1.4231 | 0 | 1.2479 | 0 | 1.4231 | 1.2479 | 12.7576 | 28.59 | 11.3345
39041.5466 | 2137 | 0 | 39041.5467 | 2300 | 0 |  | 745.5 | 952.5 | 130.464 | 0 | 140.4151 | 0 | 1.3046 | 0 | 1.4042 | 0 | 1.3046 | 1.4042 | 22.9939 | 14.2774 | 21.6893
39041.5471 | 2539 | 0 | 39041.5471 | 2257 | 0 |  | 787.5 | 994.5 | 155.0061 | 0 | 137.79 | 0 | 1.5501 | 0 | 1.3779 | 0 | 1.5501 | 1.3779 | 3.5203 | 16.4546 | 1.9702
39041.5476 | 2309 | 0 | 39041.5476 | 2612 | 0 |  | 829.5 | 1036.5 | 140.9646 | 0 | 159.4628 | 0 | 1.4096 | 0 | 1.5946 | 0 | 1.4096 | 1.5946 | 13.832 | 0.62711 | 12.4223
39041.5481 | 2181 | 0 | 39041.5481 | 2164 | 0 |  | 871.5 | 1078.5 | 133.1502 | 0 | 132.1123 | 0 | 1.3315 | 0 | 1.3211 | 0 | 1.3315 | 1.3211 | 20.5126 | 21.4593 | 19.1811
39041.5486 | 2298 | 0 | 39041.5486 | 2471 | 0 |  | 913.5 | 1120.5 | 140.293 | 0 | 150.8547 | 0 | 1.4029 | 0 | 1.5085 | 0 | 1.4029 | 1.5085 | 14.3768 | 6.3691 | 12.9739
39041.5491 | 2040 | 0 | 39041.5491 | 2063 | 0 |  | 955.5 | 1162.5 | 124.5421 | 0 | 125.9463 | 0 | 1.2454 | 0 | 1.2595 | 0 | 1.2454 | 1.2595 | 28.8422 | 27.4057 | 27.5967
39041.5496 | 1932 | 0 | 39041.5496 | 2094 | 0 |  | 997.5 | 1204.5 | 117.9487 | 0 | 127.8388 | 0 | 1.1795 | 0 | 1.2784 | 0 | 1.1795 | 1.2784 | 36.0445 | 25.5196 | 34.865
39041.55 | 1763 | 0 | 39041.5501 | 2376 | 0 |  | 1039.5 | 1246.5 | 107.6313 | 0 | 145.0549 | 0 | 1.0763 | 0 | 1.4505 | 0 | 1.0763 | 1.4505 | 49.0856 | 10.6221 | 48.0093

## B3-B4
Open Burn Test 11 |  |  | 2006-11-20 | 12:58 |  |  | Vs = |  | 155.0904 |  | R = | 100
Mixed | 7-C | Tray A | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 3 & 4 | Cable B | Odd -Even
Time-19 | N11 | N12 | Time-20 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R4-G | R3-4
39041.5359 | 1 | 0 | 39041.5359 | 1 | 0 |  | -181.5 | 25.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253938 | 253938 | 253937.9994
39041.5364 | 1 | 0 | 39041.5364 | 1 | 0 |  | -139.5 | 67.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253938 | 253938 | 253937.9994
39041.5369 | 1 | 0 | 39041.5369 | 1 | 0 |  | -97.5 | 109.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253938 | 253938 | 253937.9994
39041.5374 | 1 | 0 | 39041.5374 | 1 | 0 |  | -55.5 | 151.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253938 | 253938 | 253937.9994
39041.5379 | 1 | 0 | 39041.5379 | 1 | 0 |  | -13.5 | 193.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253938 | 253938 | 253937.9994
39041.5383 | 1 | 0 | 39041.5384 | 1 | 0 |  | 28.5 | 235.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253938 | 253938 | 253937.9994
39041.5388 | 1 | 0 | 39041.5388 | 1 | 0 |  | 70.5 | 277.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253938 | 253938 | 253937.9994
39041.5393 | 1 | 0 | 39041.5393 | 1 | 0 |  | 112.5 | 319.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253938 | 253938 | 253937.9994
39041.5398 | 1 | 0 | 39041.5398 | 1 | 0 |  | 154.5 | 361.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253938 | 253938 | 253937.9994
39041.5403 | 433 | 326 | 39041.5403 | 451 | 416 |  | 196.5 | 403.5 | 26.4347 | 19.9023 | 27.5336 | 25.3968 | 0.26435 | 0.19902 | 0.27534 | 0.25397 | 0.065324 | 0.021368 | 2011.5145 | 14591.5949 | 542.7162
39041.5408 | 1372 | 378 | 39041.5408 | 1473 | 543 |  | 238.5 | 445.5 | 83.7607 | 23.0769 | 89.9267 | 33.1502 | 0.83761 | 0.23077 | 0.89927 | 0.3315 | 0.60684 | 0.56777 | 146.8564 | 190.5182 | 137.122
39041.5413 | 2002 | 38 | 39041.5413 | 2100 | 41 |  | 280.5 | 487.5 | 122.2222 | 2.3199 | 128.2051 | 2.5031 | 1.2222 | 0.023199 | 1.2821 | 0.025031 | 1.199 | 1.257 | 29.9408 | 22.9118 | 245.461
39041.5417 | 2440 | 0 | 39041.5418 | 2260 | 1 |  | 322.5 | 529.5 | 148.9621 | 0 | 137.9731 | 0.06105 | 1.4896 | 0 | 1.3797 | 0.0006105 | 1.4896 | 1.3791 | 4.1139 | 12.456 | 2.6243
39041.5422 | 2376 | 0 | 39041.5422 | 2459 | 0 |  | 364.5 | 571.5 | 145.0549 | 0 | 150.1221 | 0 | 1.4505 | 0 | 1.5012 | 0 | 1.4505 | 1.5012 | 6.9184 | 3.3095 | 5.4678
39041.5427 | 1990 | 0 | 39041.5427 | 2104 | 0 |  | 406.5 | 613.5 | 121.4896 | 0 | 128.4493 | 0 | 1.2149 | 0 | 1.2845 | 0 | 1.2149 | 1.2845 | 27.6573 | 20.7405 | 26.4424
39041.5432 | 2162 | 0 | 39041.5432 | 2090 | 0 |  | 448.5 | 655.5 | 131.9902 | 0 | 127.5946 | 0 | 1.3199 | 0 | 1.2759 | 0 | 1.3199 | 1.2759 | 17.5014 | 21.5493 | 16.1815
39041.5437 | 2382 | 0 | 39041.5437 | 2012 | 0 |  | 490.5 | 697.5 | 145.4212 | 0 | 122.8327 | 0 | 1.4542 | 0 | 1.2283 | 0 | 1.4542 | 1.2283 | 6.649 | 26.2614 | 5.1948
39041.5442 | 2406 | 0 | 39041.5442 | 2371 | 0 |  | 532.5 | 739.5 | 146.8864 | 0 | 144.7497 | 0 | 1.4689 | 0 | 1.4475 | 0 | 1.4689 | 1.4475 | 5.5852 | 7.1438 | 4.1163
39041.5447 | 2005 | 0 | 39041.5447 | 2375 | 0 |  | 574.5 | 781.5 | 122.4054 | 0 | 144.9939 | 0 | 1.2241 | 0 | 1.4499 | 0 | 1.2241 | 1.4499 | 26.7022 | 6.9634 | 25.4782
39041.5452 | 2524 | 0 | 39041.5452 | 2092 | 0 |  | 616.5 | 823.5 | 154.0904 | 0 | 127.7167 | 0 | 1.5409 | 0 | 1.2772 | 0 | 1.5409 | 1.2772 | 0.64897 | 21.4331 | 0.89193
39041.5456 | 2321 | 0 | 39041.5456 | 2272 | 0 |  | 658.5 | 865.5 | 141.6972 | 0 | 138.7057 | 0 | 1.417 | 0 | 1.3871 | 0 | 1.417 | 1.3871 | 9.452 | 11.8125 | 8.035
39041.5461 | 2047 | 0 | 39041.5461 | 1958 | 0 |  | 700.5 | 907.5 | 124.9695 | 0 | 119.536 | 0 | 1.2497 | 0 | 1.1954 | 0 | 1.2497 | 1.1954 | 24.1026 | 29.7436 | 22.8529
39041.5466 | 2255 | 0 | 39041.5466 | 2054 | 0 |  | 742.5 | 949.5 | 137.6679 | 0 | 125.3968 | 0 | 1.3767 | 0 | 1.254 | 0 | 1.3767 | 1.254 | 12.6554 | 23.6796 | 11.2788
39041.5471 | 2480 | 0 | 39041.5471 | 1972 | 0 |  | 784.5 | 991.5 | 151.4042 | 0 | 120.3907 | 0 | 1.514 | 0 | 1.2039 | 0 | 1.514 | 1.2039 | 2.4347 | 28.8225 | 0.92064
39041.5476 | 2256 | 0 | 39041.5476 | 2247 | 0 |  | 826.5 | 1033.5 | 137.7289 | 0 | 137.1795 | 0 | 1.3773 | 0 | 1.3718 | 0 | 1.3773 | 1.3718 | 12.6055 | 13.0565 | 11.2282
39041.5481 | 2392 | 0 | 39041.5481 | 2138 | 0 |  | 868.5 | 1075.5 | 146.0317 | 0 | 130.525 | 0 | 1.4603 | 0 | 1.3053 | 0 | 1.4603 | 1.3053 | 6.2032 | 18.8204 | 4.7429
39041.5486 | 1960 | 0 | 39041.5486 | 2111 | 0 |  | 910.5 | 1117.5 | 119.6581 | 0 | 128.8767 | 0 | 1.1966 | 0 | 1.2888 | 0 | 1.1966 | 1.2888 | 29.6112 | 20.3401 | 28.4146
39041.549 | 2265 | 0 | 39041.5491 | 2137 | 0 |  | 952.5 | 1159.5 | 138.2784 | 0 | 130.464 | 0 | 1.3828 | 0 | 1.3046 | 0 | 1.3828 | 1.3046 | 12.1581 | 18.876 | 10.7753
39041.5495 | 2062 | 0 | 39041.5495 | 2400 | 1 |  | 994.5 | 1201.5 | 125.8852 | 0 | 146.5201 | 0.06105 | 1.2589 | 0 | 1.4652 | 0.0006105 | 1.2589 | 1.4646 | 23.1998 | 5.8933 | 21.941
39041.55 | 2325 | 60 | 39041.55 | 1718 | 140 |  | 1036.5 | 1243.5 | 141.9414 | 3.663 | 104.884 | 8.547 | 1.4194 | 0.03663 | 1.0488 | 0.08547 | 1.3828 | 0.96337 | 9.5432 | 741.0051 | 228.1741

## A2-C6
Open Burn Test 11 |  |  | 2006-11-20 | 12:58 |  |  | Vs = |  | 160.3407 |  | R = | 100
Mixed | 7-C | Tray A | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 2 & 6 | Cable A | Even - | Cable C |  | Even
Time-17 | N11 | N12 | Time-18 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R6-G | R2-6
39041.5359 | 1 | 0 | 39041.5359 | 1 | 0 |  | -184 | 23 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262538 | 262538 | 262537.9994
39041.5364 | 1 | 0 | 39041.5364 | 1 | 0 |  | -142 | 65 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262538 | 262538 | 262537.9994
39041.5369 | 1 | 0 | 39041.5369 | 1 | 0 |  | -100 | 107 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262538 | 262538 | 262537.9994
39041.5373 | 1 | 0 | 39041.5374 | 1 | 0 |  | -58 | 149 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262538 | 262538 | 262537.9994
39041.5378 | 1 | 0 | 39041.5378 | 1 | 0 |  | -16 | 191 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262538 | 262538 | 262537.9994
39041.5383 | 1 | 0 | 39041.5383 | 1 | 0 |  | 26 | 233 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262538 | 262538 | 262537.9994
39041.5388 | 1 | 0 | 39041.5388 | 1 | 0 |  | 68 | 275 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262538 | 262538 | 262537.9994
39041.5393 | 1 | 0 | 39041.5393 | 1 | 0 |  | 110 | 317 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262538 | 262538 | 262537.9994
39041.5398 | 1 | 0 | 39041.5398 | 1 | 0 |  | 152 | 359 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262538 | 262538 | 262537.9994
39041.5403 | 1 | 0 | 39041.5403 | 1 | 0 |  | 194 | 401 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262538 | 262538 | 262537.9994
39041.5407 | 1 | 0 | 39041.5408 | 1 | 0 |  | 236 | 443 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262538 | 262538 | 262537.9994
39041.5412 | 533 | 0 | 39041.5413 | 274 | 0 |  | 278 | 485 | 32.5397 | 0 | 16.7277 | 0 | 0.3254 | 0 | 0.16728 | 0 | 0.3254 | 0.16728 | 392.7542 | 858.5328 | 392.4288
39041.5417 | 2071 | 0 | 39041.5417 | 336 | 0 |  | 320 | 527 | 126.4347 | 0 | 20.5128 | 0 | 1.2643 | 0 | 0.20513 | 0 | 1.2643 | 0.20513 | 26.817 | 681.6607 | 25.5526
39041.5422 | 2031 | 0 | 39041.5422 | 2221 | 0 |  | 362 | 569 | 123.9927 | 0 | 135.5922 | 0 | 1.2399 | 0 | 1.3559 | 0 | 1.2399 | 1.3559 | 29.3146 | 18.2521 | 28.0747
39041.5427 | 2029 | 0 | 39041.5427 | 2489 | 0 |  | 404 | 611 | 123.8706 | 0 | 151.9536 | 0 | 1.2387 | 0 | 1.5195 | 0 | 1.2387 | 1.5195 | 29.4421 | 5.5195 | 28.2034
39041.5432 | 2282 | 0 | 39041.5432 | 2107 | 0 |  | 446 | 653 | 139.3162 | 0 | 128.6325 | 0 | 1.3932 | 0 | 1.2863 | 0 | 1.3932 | 1.2863 | 15.0911 | 24.6502 | 13.698
39041.5437 | 2573 | 0 | 39041.5437 | 2279 | 0 |  | 488 | 695 | 157.0818 | 0 | 139.1331 | 0 | 1.5708 | 0 | 1.3913 | 0 | 1.5708 | 1.3913 | 2.0746 | 15.2427 | 0.5038
39041.5441 | 2575 | 0 | 39041.5442 | 2199 | 0 |  | 530 | 737 | 157.2039 | 0 | 134.2491 | 0 | 1.572 | 0 | 1.3425 | 0 | 1.572 | 1.3425 | 1.9953 | 19.4352 | 0.4233
39041.5446 | 2220 | 0 | 39041.5446 | 2480 | 0 |  | 571.5 | 778.5 | 135.5311 | 0 | 151.4042 | 0 | 1.3553 | 0 | 1.514 | 0 | 1.3553 | 1.514 | 18.3054 | 5.9024 | 16.9501
39041.5451 | 2057 | 0 | 39041.5451 | 2209 | 0 |  | 614 | 821 | 125.58 | 0 | 134.8596 | 0 | 1.2558 | 0 | 1.3486 | 0 | 1.2558 | 1.3486 | 27.6801 | 18.8945 | 26.4243
39041.5456 | 2406 | 0 | 39041.5456 | 2066 | 0 |  | 655.5 | 862.5 | 146.8864 | 0 | 126.1294 | 0 | 1.4689 | 0 | 1.2613 | 0 | 1.4689 | 1.2613 | 9.1596 | 27.1239 | 7.6907
39041.5461 | 2583 | 0 | 39041.5461 | 2490 | 0 |  | 698 | 905 | 157.6923 | 0 | 152.0147 | 0 | 1.5769 | 0 | 1.5201 | 0 | 1.5769 | 1.5201 | 1.6794 | 5.4771 | 0.10252
39041.5466 | 1991 | 0 | 39041.5466 | 2278 | 0 |  | 740 | 947 | 121.5507 | 0 | 139.072 | 0 | 1.2155 | 0 | 1.3907 | 0 | 1.2155 | 1.3907 | 31.9126 | 15.2932 | 30.6971
39041.5471 | 2171 | 0 | 39041.5471 | 2366 | 0 |  | 782 | 989 | 132.5397 | 0 | 144.4444 | 0 | 1.3254 | 0 | 1.4444 | 0 | 1.3254 | 1.4444 | 20.9756 | 11.0051 | 19.6502
39041.5475 | 1987 | 0 | 39041.5476 | 2406 | 0 |  | 824 | 1031 | 121.3065 | 0 | 146.8864 | 0 | 1.2131 | 0 | 1.4689 | 0 | 1.2131 | 1.4689 | 32.1782 | 9.1596 | 30.9651
39041.548 | 2182 | 0 | 39041.548 | 2321 | 0 |  | 865.5 | 1072.5 | 133.2112 | 0 | 141.6972 | 0 | 1.3321 | 0 | 1.417 | 0 | 1.3321 | 1.417 | 20.3657 | 13.1573 | 19.0336
39041.5485 | 2355 | 0 | 39041.5485 | 2158 | 0 |  | 907.5 | 1114.5 | 143.7729 | 0 | 131.746 | 0 | 1.4377 | 0 | 1.3175 | 0 | 1.4377 | 1.3175 | 11.5236 | 21.7044 | 10.0858
39041.549 | 2507 | 0 | 39041.549 | 2610 | 0 |  | 950 | 1157 | 153.0525 | 0 | 159.3407 | 0 | 1.5305 | 0 | 1.5934 | 0 | 1.5305 | 1.5934 | 4.7619 | 0.62759 | 3.2313
39041.5495 | 2349 | 0 | 39041.5495 | 2582 | 0 |  | 991.5 | 1198.5 | 143.4066 | 0 | 157.6313 | 0 | 1.4341 | 0 | 1.5763 | 0 | 1.4341 | 1.5763 | 11.8084 | 1.7188 | 10.3744
39041.55 | 2495 | 0 | 39041.55 | 2112 | 0 |  | 1033.5 | 1240.5 | 152.3199 | 0 | 128.9377 | 0 | 1.5232 | 0 | 1.2894 | 0 | 1.5232 | 1.2894 | 5.2657 | 24.3551 | 3.7425

## A2-C5
Open Burn Test 11 |  |  | 2006-11-20 | 12:58 |  |  | Vs = |  | 159.547 |  | R = | 100
Mixed | 7-C | Tray A | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 2 & 5 | Cable A | Even - | Cable C |  | Odd
Time-15 | N11 | N12 | Time-16 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R5-G | R2-5
39041.5358 | 1 | 0 | 39041.5359 | 1 | 0 |  | -187 | 20 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261238 | 261238 | 261237.9994
39041.5363 | 1 | 0 | 39041.5364 | 1 | 0 |  | -145 | 62 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261238 | 261238 | 261237.9994
39041.5368 | 1 | 0 | 39041.5368 | 1 | 0 |  | -103 | 104 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261238 | 261238 | 261237.9994
39041.5373 | 1 | 0 | 39041.5373 | 1 | 0 |  | -61 | 146 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261238 | 261238 | 261237.9994
39041.5378 | 1 | 0 | 39041.5378 | 1 | 0 |  | -19 | 188 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261238 | 261238 | 261237.9994
39041.5383 | 1 | 0 | 39041.5383 | 1 | 0 |  | 23 | 230 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261238 | 261238 | 261237.9994
39041.5388 | 1 | 0 | 39041.5388 | 1 | 0 |  | 65 | 272 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261238 | 261238 | 261237.9994
39041.5392 | 1 | 0 | 39041.5393 | 1 | 0 |  | 107 | 314 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261238 | 261238 | 261237.9994
39041.5397 | 1 | 0 | 39041.5398 | 1 | 0 |  | 149 | 356 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261238 | 261238 | 261237.9994
39041.5402 | 1 | 0 | 39041.5402 | 1 | 0 |  | 191 | 398 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261238 | 261238 | 261237.9994
39041.5407 | 1 | 0 | 39041.5407 | 1 | 0 |  | 233 | 440 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261238 | 261238 | 261237.9994
39041.5412 | 593 | 0 | 39041.5412 | 213 | 0 |  | 275 | 482 | 36.2027 | 0 | 13.0037 | 0 | 0.36203 | 0 | 0.13004 | 0 | 0.36203 | 0.13004 | 340.7049 | 1126.939 | 340.3429
39041.5417 | 1911 | 0 | 39041.5417 | 1622 | 0 |  | 317 | 524 | 116.6667 | 0 | 99.0232 | 0 | 1.1667 | 0 | 0.99023 | 0 | 1.1667 | 0.99023 | 36.7546 | 61.1208 | 35.5879
39041.5422 | 2133 | 0 | 39041.5422 | 2185 | 0 |  | 359 | 566 | 130.2198 | 0 | 133.3944 | 0 | 1.3022 | 0 | 1.3339 | 0 | 1.3022 | 1.3339 | 22.5213 | 19.6055 | 21.2191
39041.5427 | 2504 | 0 | 39041.5427 | 2379 | 0 |  | 401 | 608 | 152.8694 | 0 | 145.2381 | 0 | 1.5287 | 0 | 1.4524 | 0 | 1.5287 | 1.4524 | 4.3682 | 9.852 | 2.8395
39041.5431 | 2244 | 0 | 39041.5432 | 2245 | 0 |  | 443 | 650 | 136.9963 | 0 | 137.0574 | 0 | 1.37 | 0 | 1.3706 | 0 | 1.37 | 1.3706 | 16.4608 | 16.4089 | 15.0908
39041.5436 | 2096 | 0 | 39041.5436 | 2255 | 0 |  | 485 | 692 | 127.9609 | 0 | 137.6679 | 0 | 1.2796 | 0 | 1.3767 | 0 | 1.2796 | 1.3767 | 24.6842 | 15.8927 | 23.4046
39041.5441 | 2188 | 0 | 39041.5441 | 2499 | 0 |  | 527 | 734 | 133.5775 | 0 | 152.5641 | 0 | 1.3358 | 0 | 1.5256 | 0 | 1.3358 | 1.5256 | 19.4415 | 4.577 | 18.1057
39041.5446 | 2503 | 0 | 39041.5446 | 2015 | 0 |  | 569 | 776 | 152.8083 | 0 | 123.0159 | 0 | 1.5281 | 0 | 1.2302 | 0 | 1.5281 | 1.2302 | 4.4099 | 29.6963 | 2.8818
39041.5451 | 2117 | 0 | 39041.5451 | 2073 | 0 |  | 611 | 818 | 129.243 | 0 | 126.5568 | 0 | 1.2924 | 0 | 1.2656 | 0 | 1.2924 | 1.2656 | 23.4473 | 26.0675 | 22.1549
39041.5456 | 2353 | 0 | 39041.5456 | 2261 | 0 |  | 653 | 860 | 143.6508 | 0 | 138.0342 | 0 | 1.4365 | 0 | 1.3803 | 0 | 1.4365 | 1.3803 | 11.0659 | 15.5851 | 9.6294
39041.5461 | 2146 | 0 | 39041.5461 | 2066 | 0 |  | 695 | 902 | 131.0134 | 0 | 126.1294 | 0 | 1.3101 | 0 | 1.2613 | 0 | 1.3101 | 1.2613 | 21.7791 | 26.4947 | 20.469
39041.5465 | 2357 | 0 | 39041.5466 | 2551 | 0 |  | 737 | 944 | 143.895 | 0 | 155.7387 | 0 | 1.4389 | 0 | 1.5574 | 0 | 1.4389 | 1.5574 | 10.8774 | 2.4453 | 9.4384
39041.547 | 2018 | 0 | 39041.547 | 2465 | 0 |  | 779 | 986 | 123.199 | 0 | 150.4884 | 0 | 1.232 | 0 | 1.5049 | 0 | 1.232 | 1.5049 | 29.5035 | 6.0195 | 28.2715
39041.5475 | 2459 | 0 | 39041.5475 | 2587 | 0 |  | 821 | 1028 | 150.1221 | 0 | 157.9365 | 0 | 1.5012 | 0 | 1.5794 | 0 | 1.5012 | 1.5794 | 6.2782 | 1.0197 | 4.7769
39041.548 | 1987 | 0 | 39041.548 | 2178 | 0 |  | 863 | 1070 | 121.3065 | 0 | 132.967 | 0 | 1.2131 | 0 | 1.3297 | 0 | 1.2131 | 1.3297 | 31.5239 | 19.9899 | 30.3108
39041.5485 | 2142 | 0 | 39041.5485 | 2597 | 0 |  | 905 | 1112 | 130.7692 | 0 | 158.547 | 0 | 1.3077 | 0 | 1.5855 | 0 | 1.3077 | 1.5855 | 22.0065 | 0.63073 | 20.6988
39041.549 | 2024 | 0 | 39041.549 | 2079 | 0 |  | 947 | 1154 | 123.5653 | 0 | 126.9231 | 0 | 1.2357 | 0 | 1.2692 | 0 | 1.2357 | 1.2692 | 29.1196 | 25.7037 | 27.8839
39041.5495 | 2187 | 0 | 39041.5495 | 2522 | 0 |  | 989 | 1196 | 133.5165 | 0 | 153.9683 | 0 | 1.3352 | 0 | 1.5397 | 0 | 1.3352 | 1.5397 | 19.4961 | 3.6233 | 18.1609
39041.5499 | 1989 | 0 | 39041.55 | 2326 | 0 |  | 1031 | 1238 | 121.4286 | 0 | 142.0024 | 0 | 1.2143 | 0 | 1.42 | 0 | 1.2143 | 1.42 | 31.3917 | 12.3551 | 30.1774

## A2-B4
Open Burn Test 11 |  |  | 2006-11-20 | 12:58 |  |  | Vs = |  | 158.6923 |  | R = | 100
Mixed | 7-C | Tray A | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 2 & 4 | Cable A | Even - | Cable B |  | Even
Time-13 | N11 | N12 | Time-14 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R4-G | R2-4
39041.5358 | 1 | 0 | 39041.5358 | 1 | 0 |  | -189.5 | 17.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259838 | 259838 | 259837.9994
39041.5363 | 1 | 0 | 39041.5363 | 1 | 0 |  | -147.5 | 59.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259838 | 259838 | 259837.9994
39041.5368 | 1 | 0 | 39041.5368 | 1 | 0 |  | -105.5 | 101.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259838 | 259838 | 259837.9994
39041.5373 | 1 | 0 | 39041.5373 | 1 | 0 |  | -63.5 | 143.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259838 | 259838 | 259837.9994
39041.5378 | 1 | 0 | 39041.5378 | 1 | 0 |  | -21.5 | 185.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259838 | 259838 | 259837.9994
39041.5383 | 1 | 0 | 39041.5383 | 1 | 0 |  | 20.5 | 227.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259838 | 259838 | 259837.9994
39041.5387 | 1 | 0 | 39041.5387 | 1 | 0 |  | 62.5 | 269.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259838 | 259838 | 259837.9994
39041.5392 | 1 | 0 | 39041.5392 | 1 | 0 |  | 104.5 | 311.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259838 | 259838 | 259837.9994
39041.5397 | 1 | 0 | 39041.5397 | 1 | 0 |  | 146.5 | 353.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259838 | 259838 | 259837.9994
39041.5402 | 1 | 0 | 39041.5402 | 1 | 0 |  | 188.5 | 395.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259838 | 259838 | 259837.9994
39041.5407 | 1 | 0 | 39041.5407 | 1 | 0 |  | 230.5 | 437.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259838 | 259838 | 259837.9994
39041.5412 | 348 | 0 | 39041.5412 | 492 | 0 |  | 272.5 | 479.5 | 21.2454 | 0 | 30.0366 | 0 | 0.21245 | 0 | 0.30037 | 0 | 0.21245 | 0.30037 | 646.9483 | 428.3293 | 646.7358
39041.5417 | 1872 | 0 | 39041.5417 | 1932 | 0 |  | 314.5 | 521.5 | 114.2857 | 0 | 117.9487 | 0 | 1.1429 | 0 | 1.1795 | 0 | 1.1429 | 1.1795 | 38.8558 | 34.5435 | 37.7129
39041.5421 | 2346 | 0 | 39041.5422 | 2203 | 0 |  | 356.5 | 563.5 | 143.2234 | 0 | 134.4933 | 0 | 1.4322 | 0 | 1.3449 | 0 | 1.4322 | 1.3449 | 10.8005 | 17.9927 | 9.3683
39041.5426 | 2176 | 0 | 39041.5426 | 2061 | 0 |  | 398.5 | 605.5 | 132.8449 | 0 | 125.8242 | 0 | 1.3284 | 0 | 1.2582 | 0 | 1.3284 | 1.2582 | 19.4568 | 26.1223 | 18.1284
39041.5431 | 2475 | 0 | 39041.5431 | 2318 | 0 |  | 440.5 | 647.5 | 151.0989 | 0 | 141.514 | 0 | 1.511 | 0 | 1.4151 | 0 | 1.511 | 1.4151 | 5.0255 | 12.1389 | 3.5145
39041.5436 | 2407 | 0 | 39041.5436 | 2367 | 0 |  | 482.5 | 689.5 | 146.9475 | 0 | 144.5055 | 0 | 1.4695 | 0 | 1.4451 | 0 | 1.4695 | 1.4451 | 7.9925 | 9.8175 | 6.523
39041.5441 | 2061 | 0 | 39041.5441 | 2436 | 0 |  | 524.5 | 731.5 | 125.8242 | 0 | 148.7179 | 0 | 1.2582 | 0 | 1.4872 | 0 | 1.2582 | 1.4872 | 26.1223 | 6.7069 | 24.864
39041.5446 | 2186 | 0 | 39041.5446 | 2086 | 0 |  | 566.5 | 773.5 | 133.4554 | 0 | 127.3504 | 0 | 1.3346 | 0 | 1.2735 | 0 | 1.3346 | 1.2735 | 18.9103 | 24.6107 | 17.5758
39041.5451 | 2581 | 0 | 39041.5451 | 2489 | 0 |  | 608.5 | 815.5 | 157.5702 | 0 | 151.9536 | 0 | 1.5757 | 0 | 1.5195 | 0 | 1.5757 | 1.5195 | 0.71213 | 4.4347 | 0.86357
39041.5455 | 2583 | 0 | 39041.5456 | 2429 | 0 |  | 650.5 | 857.5 | 157.6923 | 0 | 148.2906 | 0 | 1.5769 | 0 | 1.4829 | 0 | 1.5769 | 1.4829 | 0.63415 | 7.0144 | 0.94278
39041.546 | 2207 | 0 | 39041.546 | 2072 | 0 |  | 692.5 | 899.5 | 134.7375 | 0 | 126.4957 | 0 | 1.3474 | 0 | 1.265 | 0 | 1.3474 | 1.265 | 17.7789 | 25.4527 | 16.4315
39041.5465 | 2026 | 0 | 39041.5465 | 2505 | 0 |  | 734.5 | 941.5 | 123.6874 | 0 | 152.9304 | 0 | 1.2369 | 0 | 1.5293 | 0 | 1.2369 | 1.5293 | 28.3011 | 3.7677 | 27.0642
39041.547 | 2385 | 0 | 39041.547 | 2258 | 0 |  | 776 | 983 | 145.6044 | 0 | 137.851 | 0 | 1.456 | 0 | 1.3785 | 0 | 1.456 | 1.3785 | 8.9887 | 15.1187 | 7.5326
39041.5475 | 2573 | 0 | 39041.5475 | 2101 | 0 |  | 818 | 1025 | 157.0818 | 0 | 128.2662 | 0 | 1.5708 | 0 | 1.2827 | 0 | 1.5708 | 1.2827 | 1.0253 | 23.7211 | 0.54556
39041.548 | 2380 | 0 | 39041.548 | 2120 | 0 |  | 860.5 | 1067.5 | 145.2991 | 0 | 129.4261 | 0 | 1.453 | 0 | 1.2943 | 0 | 1.453 | 1.2943 | 9.2176 | 22.6123 | 7.7647
39041.5484 | 2254 | 0 | 39041.5485 | 2440 | 0 |  | 902 | 1109 | 137.6068 | 0 | 148.9621 | 0 | 1.3761 | 0 | 1.4896 | 0 | 1.3761 | 1.4896 | 15.323 | 6.532 | 13.9469
39041.5489 | 2363 | 0 | 39041.549 | 2561 | 0 |  | 944 | 1151 | 144.2613 | 0 | 156.3492 | 0 | 1.4426 | 0 | 1.5635 | 0 | 1.4426 | 1.5635 | 10.0034 | 1.4986 | 8.5608
39041.5494 | 2313 | 0 | 39041.5494 | 1971 | 0 |  | 986 | 1193 | 141.2088 | 0 | 120.3297 | 0 | 1.4121 | 0 | 1.2033 | 0 | 1.4121 | 1.2033 | 12.3813 | 31.8813 | 10.9692
39041.5499 | 2330 | 0 | 39041.5499 | 2113 | 0 |  | 1028 | 1235 | 142.2466 | 0 | 128.9988 | 0 | 1.4225 | 0 | 1.29 | 0 | 1.4225 | 1.29 | 11.5614 | 23.0185 | 10.1389

## A2-B3
Open Burn Test 11 |  |  | 2006-11-20 | 12:58 |  |  | Vs = |  | 158.265 |  | R = | 100
Mixed | 7-C | Tray A | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 2 & 3 | Cable A | Even - | Cable B |  | Odd
Time-11 | N11 | N12 | Time-12 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R3-G | R2-3
39041.5358 | 1 | 0 | 39041.5358 | 1 | 0 |  | -192.5 | 14.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259138 | 259138 | 259137.9994
39041.5363 | 1 | 0 | 39041.5363 | 1 | 0 |  | -150.5 | 56.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259138 | 259138 | 259137.9994
39041.5368 | 1 | 0 | 39041.5368 | 1 | 0 |  | -108.5 | 98.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259138 | 259138 | 259137.9994
39041.5372 | 1 | 0 | 39041.5373 | 1 | 0 |  | -66.5 | 140.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259138 | 259138 | 259137.9994
39041.5377 | 1 | 0 | 39041.5377 | 1 | 0 |  | -24.5 | 182.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259138 | 259138 | 259137.9994
39041.5382 | 1 | 0 | 39041.5382 | 1 | 0 |  | 17.5 | 224.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259138 | 259138 | 259137.9994
39041.5387 | 1 | 0 | 39041.5387 | 1 | 0 |  | 59.5 | 266.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259138 | 259138 | 259137.9994
39041.5392 | 1 | 0 | 39041.5392 | 1 | 0 |  | 101.5 | 308.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259138 | 259138 | 259137.9994
39041.5397 | 1 | 0 | 39041.5397 | 1 | 0 |  | 143.5 | 350.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259138 | 259138 | 259137.9994
39041.5402 | 1 | 0 | 39041.5402 | 1 | 0 |  | 185.5 | 392.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259138 | 259138 | 259137.9994
39041.5406 | 1 | 0 | 39041.5407 | 1220 | 0 |  | 227.5 | 434.5 | 0.06105 | 0 | 74.4811 | 0 | 0.0006105 | 0 | 0.74481 | 0 | 0.0006105 | 0.74481 | 259138 | 112.4902 | 259137.9994
39041.5411 | 279 | 0 | 39041.5411 | 1781 | 0 |  | 269.5 | 476.5 | 17.033 | 0 | 108.7302 | 0 | 0.17033 | 0 | 1.0873 | 0 | 0.17033 | 1.0873 | 829.1685 | 45.5576 | 828.9981
39041.5416 | 1968 | 0 | 39041.5416 | 1971 | 0 |  | 311.5 | 518.5 | 120.1465 | 0 | 120.3297 | 0 | 1.2015 | 0 | 1.2033 | 0 | 1.2015 | 1.2033 | 31.7266 | 31.5261 | 30.5252
39041.5421 | 2294 | 0 | 39041.5421 | 2025 | 0 |  | 353.5 | 560.5 | 140.0488 | 0 | 123.6264 | 0 | 1.4005 | 0 | 1.2363 | 0 | 1.4005 | 1.2363 | 13.007 | 28.0188 | 11.6065
39041.5426 | 2196 | 0 | 39041.5426 | 2351 | 0 |  | 395.5 | 602.5 | 134.0659 | 0 | 143.5287 | 0 | 1.3407 | 0 | 1.4353 | 0 | 1.3407 | 1.4353 | 18.0501 | 10.2671 | 16.7094
39041.5431 | 2549 | 0 | 39041.5431 | 2076 | 0 |  | 437.5 | 644.5 | 155.6166 | 0 | 126.7399 | 0 | 1.5562 | 0 | 1.2674 | 0 | 1.5562 | 1.2674 | 1.7018 | 24.8738 | 0.14568
39041.5436 | 2402 | 0 | 39041.5436 | 2206 | 0 |  | 479.5 | 686.5 | 146.6422 | 0 | 134.6764 | 0 | 1.4664 | 0 | 1.3468 | 0 | 1.4664 | 1.3468 | 7.9259 | 17.515 | 6.4595
39041.5441 | 2129 | 0 | 39041.5441 | 2171 | 0 |  | 521.5 | 728.5 | 129.9756 | 0 | 132.5397 | 0 | 1.2998 | 0 | 1.3254 | 0 | 1.2998 | 1.3254 | 21.7651 | 19.4095 | 20.4654
39041.5445 | 2141 | 0 | 39041.5445 | 2232 | 0 |  | 563.5 | 770.5 | 130.7082 | 0 | 136.2637 | 0 | 1.3071 | 0 | 1.3626 | 0 | 1.3071 | 1.3626 | 21.0827 | 16.1461 | 19.7756
39041.545 | 2240 | 0 | 39041.545 | 2415 | 0 |  | 605.5 | 812.5 | 136.7521 | 0 | 147.4359 | 0 | 1.3675 | 0 | 1.4744 | 0 | 1.3675 | 1.4744 | 15.7312 | 7.3449 | 14.3637
39041.5455 | 2108 | 0 | 39041.5455 | 2257 | 0 |  | 647.5 | 854.5 | 128.6935 | 0 | 137.79 | 0 | 1.2869 | 0 | 1.3779 | 0 | 1.2869 | 1.3779 | 22.9782 | 14.8595 | 21.6912
39041.546 | 2576 | 0 | 39041.546 | 1980 | 0 |  | 689.5 | 896.5 | 157.265 | 0 | 120.8791 | 0 | 1.5726 | 0 | 1.2088 | 0 | 1.5726 | 1.2088 | 0.63587 | 30.9283 | 0.93678
39041.5465 | 2477 | 0 | 39041.5465 | 2465 | 0 |  | 731.5 | 938.5 | 151.221 | 0 | 150.4884 | 0 | 1.5122 | 0 | 1.5049 | 0 | 1.5122 | 1.5049 | 4.6581 | 5.1675 | 3.1458
39041.547 | 2063 | 0 | 39041.547 | 2325 | 0 |  | 773.5 | 980.5 | 125.9463 | 0 | 141.9414 | 0 | 1.2595 | 0 | 1.4194 | 0 | 1.2595 | 1.4194 | 25.6607 | 11.5002 | 24.4012
39041.5475 | 2116 | 0 | 39041.5475 | 2049 | 0 |  | 815.5 | 1022.5 | 129.1819 | 0 | 125.0916 | 0 | 1.2918 | 0 | 1.2509 | 0 | 1.2918 | 1.2509 | 22.5132 | 26.5193 | 21.2214
39041.5479 | 1991 | 0 | 39041.548 | 2372 | 0 |  | 857.5 | 1064.5 | 121.5507 | 0 | 144.8107 | 0 | 1.2155 | 0 | 1.4481 | 0 | 1.2155 | 1.4481 | 30.2049 | 9.2909 | 28.9894
39041.5484 | 2002 | 0 | 39041.5484 | 2015 | 0 |  | 899.5 | 1106.5 | 122.2222 | 0 | 123.0159 | 0 | 1.2222 | 0 | 1.2302 | 0 | 1.2222 | 1.2302 | 29.4895 | 28.6541 | 28.2673
39041.5489 | 2014 | 0 | 39041.5489 | 2250 | 0 |  | 941.5 | 1148.5 | 122.9548 | 0 | 137.3626 | 0 | 1.2295 | 0 | 1.3736 | 0 | 1.2295 | 1.3736 | 28.718 | 15.2169 | 27.4884
39041.5494 | 2133 | 0 | 39041.5494 | 2319 | 0 |  | 983.5 | 1190.5 | 130.2198 | 0 | 141.5751 | 0 | 1.3022 | 0 | 1.4158 | 0 | 1.3022 | 1.4158 | 21.5368 | 11.7887 | 20.2346
39041.5499 | 2033 | 0 | 39041.5499 | 2027 | 0 |  | 1025.5 | 1232.5 | 124.1148 | 0 | 123.7485 | 0 | 1.2411 | 0 | 1.2375 | 0 | 1.2411 | 1.2375 | 27.515 | 27.8925 | 26.2739

## A1-C6
Open Burn Test 11 |  |  | 2006-11-20 | 12:58 |  |  | Vs = |  | 158.6313 |  | R = | 100
Mixed | 7-C | Tray A | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 1 & 6 | Cable A | Odd - | Cable C |  | Even
Time-9 | N11 | N12 | Time-10 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R6-G | R1-6
39041.5358 | 1 | 0 | 39041.5358 | 1 | 0 |  | -195 | 12 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259738 | 259738 | 259737.9994
39041.5362 | 1 | 0 | 39041.5362 | 1 | 0 |  | -153.5 | 53.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259738 | 259738 | 259737.9994
39041.5367 | 1 | 0 | 39041.5367 | 1 | 0 |  | -111.5 | 95.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259738 | 259738 | 259737.9994
39041.5372 | 1 | 0 | 39041.5372 | 1 | 0 |  | -69.5 | 137.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259738 | 259738 | 259737.9994
39041.5377 | 1 | 0 | 39041.5377 | 1 | 0 |  | -27.5 | 179.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259738 | 259738 | 259737.9994
39041.5382 | 1 | 0 | 39041.5382 | 1 | 0 |  | 15 | 222 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259738 | 259738 | 259737.9994
39041.5387 | 1 | 0 | 39041.5387 | 1 | 0 |  | 56.5 | 263.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259738 | 259738 | 259737.9994
39041.5392 | 1 | 0 | 39041.5392 | 1 | 0 |  | 98.5 | 305.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259738 | 259738 | 259737.9994
39041.5396 | 1 | 0 | 39041.5397 | 1 | 0 |  | 140.5 | 347.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259738 | 259738 | 259737.9994
39041.5401 | 1 | 0 | 39041.5401 | 1 | 0 |  | 182.5 | 389.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259738 | 259738 | 259737.9994
39041.5406 | 1 | 0 | 39041.5406 | 1 | 0 |  | 224.5 | 431.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259738 | 259738 | 259737.9994
39041.5411 | 387 | 1 | 39041.5411 | 1 | 0 |  | 266.5 | 473.5 | 23.6264 | 0.06105 | 0.06105 | 0 | 0.23626 | 0.0006105 | 0.0006105 | 0 | 0.23565 | 0.0006105 | 572.8969 | 259738 | 220952.9324
39041.5416 | 1967 | 0 | 39041.5416 | 297 | 0 |  | 308.5 | 515.5 | 120.0855 | 0 | 18.1319 | 0 | 1.2009 | 0 | 0.18132 | 0 | 1.2009 | 0.18132 | 32.0986 | 774.8754 | 30.8978
39041.5421 | 2414 | 0 | 39041.5421 | 1744 | 0 |  | 350.5 | 557.5 | 147.3748 | 0 | 106.4713 | 0 | 1.4737 | 0 | 1.0647 | 0 | 1.4737 | 1.0647 | 7.6379 | 48.9897 | 6.1642
39041.5426 | 2554 | 0 | 39041.5426 | 2022 | 0 |  | 392.5 | 599.5 | 155.9219 | 0 | 123.4432 | 0 | 1.5592 | 0 | 1.2344 | 0 | 1.5592 | 1.2344 | 1.7377 | 28.5054 | 0.17845
39041.543 | 2500 | 0 | 39041.5431 | 2007 | 0 |  | 434.5 | 641.5 | 152.6252 | 0 | 122.5275 | 0 | 1.5263 | 0 | 1.2253 | 0 | 1.5263 | 1.2253 | 3.9352 | 29.4659 | 2.4089
39041.5435 | 2035 | 0 | 39041.5435 | 2481 | 0 |  | 476.5 | 683.5 | 124.2369 | 0 | 151.4652 | 0 | 1.2424 | 0 | 1.5147 | 0 | 1.2424 | 1.5147 | 27.6845 | 4.7312 | 26.4422
39041.544 | 2103 | 0 | 39041.544 | 2582 | 0 |  | 518.5 | 725.5 | 128.3883 | 0 | 157.6313 | 0 | 1.2839 | 0 | 1.5763 | 0 | 1.2839 | 1.5763 | 23.5559 | 0.63439 | 22.272
39041.5445 | 2387 | 0 | 39041.5445 | 2188 | 0 |  | 560.5 | 767.5 | 145.7265 | 0 | 133.5775 | 0 | 1.4573 | 0 | 1.3358 | 0 | 1.4573 | 1.3358 | 8.8555 | 18.7559 | 7.3982
39041.545 | 2200 | 0 | 39041.545 | 2359 | 0 |  | 602.5 | 809.5 | 134.3101 | 0 | 144.0171 | 0 | 1.3431 | 0 | 1.4402 | 0 | 1.3431 | 1.4402 | 18.1082 | 10.1475 | 16.7651
39041.5455 | 2126 | 0 | 39041.5455 | 2414 | 0 |  | 644.5 | 851.5 | 129.7924 | 0 | 147.3748 | 0 | 1.2979 | 0 | 1.4737 | 0 | 1.2979 | 1.4737 | 22.2192 | 7.6379 | 20.9213
39041.546 | 2148 | 0 | 39041.546 | 2486 | 0 |  | 686.5 | 893.5 | 131.1355 | 0 | 151.7705 | 0 | 1.3114 | 0 | 1.5177 | 0 | 1.3114 | 1.5177 | 20.9674 | 4.5205 | 19.6561
39041.5464 | 2260 | 0 | 39041.5465 | 2548 | 0 |  | 728.5 | 935.5 | 137.9731 | 0 | 155.5556 | 0 | 1.3797 | 0 | 1.5556 | 0 | 1.3797 | 1.5556 | 14.9726 | 1.9772 | 13.5928
39041.5469 | 2562 | 0 | 39041.5469 | 2239 | 0 |  | 770.5 | 977.5 | 156.4103 | 0 | 136.6911 | 0 | 1.5641 | 0 | 1.3669 | 0 | 1.5641 | 1.3669 | 1.42 | 16.0509 | 0.14412
39041.5474 | 2195 | 0 | 39041.5474 | 2165 | 0 |  | 812.5 | 1019.5 | 134.0049 | 0 | 132.1734 | 0 | 1.34 | 0 | 1.3217 | 0 | 1.34 | 1.3217 | 18.3772 | 20.0176 | 17.0372
39041.5479 | 2202 | 0 | 39041.5479 | 2478 | 0 |  | 854.5 | 1061.5 | 134.4322 | 0 | 151.2821 | 0 | 1.3443 | 0 | 1.5128 | 0 | 1.3443 | 1.5128 | 18.0009 | 4.8579 | 16.6566
39041.5484 | 2078 | 0 | 39041.5484 | 2569 | 0 |  | 896.5 | 1103.5 | 126.862 | 0 | 156.8376 | 0 | 1.2686 | 0 | 1.5684 | 0 | 1.2686 | 1.5684 | 25.0423 | 1.1436 | 23.7737
39041.5489 | 2338 | 0 | 39041.5489 | 2485 | 0 |  | 938.5 | 1145.5 | 142.735 | 0 | 151.7094 | 0 | 1.4274 | 0 | 1.5171 | 0 | 1.4274 | 1.5171 | 11.1369 | 4.5626 | 9.7095
39041.5494 | 2315 | 0 | 39041.5494 | 2552 | 0 |  | 980.5 | 1187.5 | 141.3309 | 0 | 155.7998 | 0 | 1.4133 | 0 | 1.558 | 0 | 1.4133 | 1.558 | 12.241 | 1.8174 | 10.8277
39041.5498 | 2230 | 0 | 39041.5499 | 2211 | 0 |  | 1022.5 | 1229.5 | 136.1416 | 0 | 134.9817 | 0 | 1.3614 | 0 | 1.3498 | 0 | 1.3614 | 1.3498 | 16.5193 | 17.5206 | 15.1579

## A1-C5
Open Burn Test 11 |  |  | 2006-11-20 | 12:58 |  |  | Vs = |  | 158.6923 |  | R = | 100
Mixed | 7-C | Tray A | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 1 & 5 | Cable A | Odd - | Cable C |  | Odd
Time-7 | N11 | N12 | Time-8 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R5-G | R1-5
39041.5357 | 1 | 0 | 39041.5357 | 1 | 0 |  | -198 | 9 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259838 | 259838 | 259837.9994
39041.5362 | 1 | 0 | 39041.5362 | 1 | 0 |  | -156 | 51 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259838 | 259838 | 259837.9994
39041.5367 | 1 | 0 | 39041.5367 | 1 | 0 |  | -114 | 93 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259838 | 259838 | 259837.9994
39041.5372 | 1 | 0 | 39041.5372 | 1 | 0 |  | -72 | 135 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259838 | 259838 | 259837.9994
39041.5377 | 1 | 0 | 39041.5377 | 1 | 0 |  | -30 | 177 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259838 | 259838 | 259837.9994
39041.5381 | 1 | 0 | 39041.5382 | 1 | 0 |  | 12 | 219 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259838 | 259838 | 259837.9994
39041.5386 | 1 | 0 | 39041.5387 | 1 | 0 |  | 54 | 261 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259838 | 259838 | 259837.9994
39041.5391 | 1 | 0 | 39041.5391 | 1 | 0 |  | 96 | 303 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259838 | 259838 | 259837.9994
39041.5396 | 1 | 0 | 39041.5396 | 1 | 0 |  | 138 | 345 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259838 | 259838 | 259837.9994
39041.5401 | 1 | 0 | 39041.5401 | 1 | 0 |  | 180 | 387 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259838 | 259838 | 259837.9994
39041.5406 | 1 | 0 | 39041.5406 | 1 | 0 |  | 222 | 429 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259838 | 259838 | 259837.9994
39041.5411 | 290 | 0 | 39041.5411 | 135 | 0 |  | 264 | 471 | 17.7045 | 0 | 8.2418 | 0 | 0.17705 | 0 | 0.082418 | 0 | 0.17705 | 0.082418 | 796.3379 | 1825.4667 | 796.1609
39041.5416 | 1628 | 0 | 39041.5416 | 1503 | 0 |  | 306 | 513 | 99.3895 | 0 | 91.7582 | 0 | 0.99389 | 0 | 0.91758 | 0 | 0.99389 | 0.91758 | 59.6671 | 72.9461 | 58.6732
39041.542 | 2266 | 0 | 39041.5421 | 1631 | 0 |  | 348 | 555 | 138.3394 | 0 | 99.5726 | 0 | 1.3834 | 0 | 0.99573 | 0 | 1.3834 | 0.99573 | 14.7123 | 59.3734 | 13.3289
39041.5425 | 2265 | 0 | 39041.5425 | 2535 | 0 |  | 390 | 597 | 138.2784 | 0 | 154.7619 | 0 | 1.3828 | 0 | 1.5476 | 0 | 1.3828 | 1.5476 | 14.7629 | 2.5396 | 13.3801
39041.543 | 2038 | 0 | 39041.543 | 2300 | 0 |  | 432 | 639 | 124.42 | 0 | 140.4151 | 0 | 1.2442 | 0 | 1.4042 | 0 | 1.2442 | 1.4042 | 27.5456 | 13.0165 | 26.3014
39041.5435 | 2402 | 0 | 39041.5435 | 2058 | 0 |  | 474 | 681 | 146.6422 | 0 | 125.641 | 0 | 1.4664 | 0 | 1.2564 | 0 | 1.4664 | 1.2564 | 8.2173 | 26.3061 | 6.7509
39041.544 | 2305 | 0 | 39041.544 | 2098 | 0 |  | 515.5 | 722.5 | 140.7204 | 0 | 128.083 | 0 | 1.4072 | 0 | 1.2808 | 0 | 1.4072 | 1.2808 | 12.7714 | 23.898 | 11.3642
39041.5445 | 1993 | 0 | 39041.5445 | 2174 | 0 |  | 558 | 765 | 121.6728 | 0 | 132.7228 | 0 | 1.2167 | 0 | 1.3272 | 0 | 1.2167 | 1.3272 | 30.4255 | 19.5667 | 29.2088
39041.545 | 2580 | 0 | 39041.545 | 2416 | 0 |  | 600 | 807 | 157.5092 | 0 | 147.4969 | 0 | 1.5751 | 0 | 1.475 | 0 | 1.5751 | 1.475 | 0.75116 | 7.5902 | 0.82393
39041.5454 | 2437 | 0 | 39041.5455 | 2335 | 0 |  | 642 | 849 | 148.779 | 0 | 142.5519 | 0 | 1.4878 | 0 | 1.4255 | 0 | 1.4878 | 1.4255 | 6.6631 | 11.3225 | 5.1753
39041.5459 | 2072 | 0 | 39041.5459 | 2116 | 0 |  | 684 | 891 | 126.4957 | 0 | 129.1819 | 0 | 1.265 | 0 | 1.2918 | 0 | 1.265 | 1.2918 | 25.4527 | 22.844 | 24.1877
39041.5464 | 2232 | 0 | 39041.5464 | 2051 | 0 |  | 725.5 | 932.5 | 136.2637 | 0 | 125.2137 | 0 | 1.3626 | 0 | 1.2521 | 0 | 1.3626 | 1.2521 | 16.4597 | 26.7372 | 15.097
39041.5469 | 2443 | 0 | 39041.5469 | 2583 | 0 |  | 767.5 | 974.5 | 149.1453 | 0 | 157.6923 | 0 | 1.4915 | 0 | 1.5769 | 0 | 1.4915 | 1.5769 | 6.4011 | 0.63415 | 4.9097
39041.5474 | 2040 | 0 | 39041.5474 | 2571 | 0 |  | 809.5 | 1016.5 | 124.5421 | 0 | 156.9597 | 0 | 1.2454 | 0 | 1.5696 | 0 | 1.2454 | 1.5696 | 27.4206 | 1.1039 | 26.1752
39041.5479 | 2156 | 0 | 39041.5479 | 2056 | 0 |  | 852 | 1059 | 131.6239 | 0 | 125.5189 | 0 | 1.3162 | 0 | 1.2552 | 0 | 1.3162 | 1.2552 | 20.5649 | 26.429 | 19.2487
39041.5484 | 2216 | 0 | 39041.5484 | 2230 | 0 |  | 894 | 1101 | 135.2869 | 0 | 136.1416 | 0 | 1.3529 | 0 | 1.3614 | 0 | 1.3529 | 1.3614 | 17.3005 | 16.5641 | 15.9477
39041.5488 | 2253 | 0 | 39041.5489 | 2509 | 0 |  | 935.5 | 1142.5 | 137.5458 | 0 | 153.1746 | 0 | 1.3755 | 0 | 1.5317 | 0 | 1.3755 | 1.5317 | 15.3742 | 3.6022 | 13.9987
39041.5493 | 2214 | 0 | 39041.5494 | 2212 | 0 |  | 978 | 1185 | 135.1648 | 0 | 135.0427 | 0 | 1.3516 | 0 | 1.3504 | 0 | 1.3516 | 1.3504 | 17.4065 | 17.5127 | 16.0549
39041.5498 | 2262 | 0 | 39041.5498 | 2494 | 0 |  | 1020 | 1227 | 138.0952 | 0 | 152.2589 | 0 | 1.381 | 0 | 1.5226 | 0 | 1.381 | 1.5226 | 14.9151 | 4.2253 | 13.5342

## A1-B4
Open Burn Test 11 |  |  | 2006-11-20 | 12:58 |  |  | Vs = |  | 157.7766 |  | R = | 100
Mixed | 7-C | Tray A | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 1 & 4 | Cable A | Odd - | Cable B |  | Even
Time-5 | N11 | N12 | Time-6 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R4-G | R1-4
39041.5357 | 1 | 0 | 39041.5357 | 1 | 0 |  | -201 | 6 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258338 | 258338 | 258337.9994
39041.5362 | 1 | 0 | 39041.5362 | 1 | 0 |  | -159 | 48 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258338 | 258338 | 258337.9994
39041.5367 | 1 | 0 | 39041.5367 | 1 | 0 |  | -117 | 90 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258338 | 258338 | 258337.9994
39041.5371 | 1 | 0 | 39041.5372 | 1 | 0 |  | -75 | 132 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258338 | 258338 | 258337.9994
39041.5376 | 1 | 0 | 39041.5377 | 1 | 0 |  | -33 | 174 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258338 | 258338 | 258337.9994
39041.5381 | 1 | 0 | 39041.5381 | 1 | 0 |  | 9 | 216 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258338 | 258338 | 258337.9994
39041.5386 | 1 | 0 | 39041.5386 | 1 | 0 |  | 51 | 258 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258338 | 258338 | 258337.9994
39041.5391 | 1 | 0 | 39041.5391 | 1 | 0 |  | 93 | 300 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258338 | 258338 | 258337.9994
39041.5396 | 1 | 0 | 39041.5396 | 1 | 0 |  | 135 | 342 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258338 | 258338 | 258337.9994
39041.5401 | 1 | 0 | 39041.5401 | 1 | 0 |  | 177 | 384 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258338 | 258338 | 258337.9994
39041.5405 | 1 | 0 | 39041.5406 | 691 | 0 |  | 219 | 426 | 0.06105 | 0 | 42.1856 | 0 | 0.0006105 | 0 | 0.42186 | 0 | 0.0006105 | 0.42186 | 258338 | 274.0058 | 258337.9994
39041.541 | 463 | 0 | 39041.5411 | 1560 | 0 |  | 261 | 468 | 28.2662 | 0 | 95.2381 | 0 | 0.28266 | 0 | 0.95238 | 0 | 0.28266 | 0.95238 | 458.1814 | 65.6654 | 457.8988
39041.5415 | 1483 | 0 | 39041.5415 | 1879 | 0 |  | 303 | 510 | 90.5372 | 0 | 114.7131 | 0 | 0.90537 | 0 | 1.1471 | 0 | 0.90537 | 1.1471 | 74.267 | 37.5402 | 73.3617
39041.542 | 2078 | 0 | 39041.542 | 2366 | 0 |  | 345 | 552 | 126.862 | 0 | 144.4444 | 0 | 1.2686 | 0 | 1.4444 | 0 | 1.2686 | 1.4444 | 24.3686 | 9.2299 | 23.1
39041.5425 | 2416 | 0 | 39041.5425 | 2018 | 0 |  | 387 | 594 | 147.4969 | 0 | 123.199 | 0 | 1.475 | 0 | 1.232 | 0 | 1.475 | 1.232 | 6.9694 | 28.0664 | 5.4944
39041.543 | 2521 | 0 | 39041.543 | 2424 | 0 |  | 429 | 636 | 153.9072 | 0 | 147.9853 | 0 | 1.5391 | 0 | 1.4799 | 0 | 1.5391 | 1.4799 | 2.5141 | 6.6163 | 0.97501
39041.5435 | 2545 | 0 | 39041.5435 | 2161 | 0 |  | 471 | 678 | 155.3724 | 0 | 131.9292 | 0 | 1.5537 | 0 | 1.3193 | 0 | 1.5537 | 1.3193 | 1.5473 | 19.5919 | 0.0063763
39041.5439 | 1993 | 0 | 39041.544 | 2044 | 0 |  | 513 | 720 | 121.6728 | 0 | 124.7863 | 0 | 1.2167 | 0 | 1.2479 | 0 | 1.2167 | 1.2479 | 29.6729 | 26.4374 | 28.4561
39041.5444 | 2279 | 0 | 39041.5445 | 2536 | 0 |  | 555 | 762 | 139.1331 | 0 | 154.823 | 0 | 1.3913 | 0 | 1.5482 | 0 | 1.3913 | 1.5482 | 13.3997 | 1.9077 | 12.0084
39041.5449 | 2381 | 0 | 39041.5449 | 2005 | 0 |  | 597 | 804 | 145.3602 | 0 | 122.4054 | 0 | 1.4536 | 0 | 1.2241 | 0 | 1.4536 | 1.2241 | 8.5418 | 28.8968 | 7.0882
39041.5454 | 2028 | 0 | 39041.5454 | 2553 | 0 |  | 639 | 846 | 123.8095 | 0 | 155.8608 | 0 | 1.2381 | 0 | 1.5586 | 0 | 1.2381 | 1.5586 | 27.4349 | 1.2291 | 26.1968
39041.5459 | 2086 | 0 | 39041.5459 | 2225 | 0 |  | 681 | 888 | 127.3504 | 0 | 135.8364 | 0 | 1.2735 | 0 | 1.3584 | 0 | 1.2735 | 1.3584 | 23.8917 | 16.1519 | 22.6182
39041.5464 | 2043 | 0 | 39041.5464 | 2432 | 0 |  | 723 | 930 | 124.7253 | 0 | 148.4737 | 0 | 1.2473 | 0 | 1.4847 | 0 | 1.2473 | 1.4847 | 26.4993 | 6.2656 | 25.252
39041.5469 | 2267 | 0 | 39041.5469 | 2091 | 0 |  | 765 | 972 | 138.4005 | 0 | 127.6557 | 0 | 1.384 | 0 | 1.2766 | 0 | 1.384 | 1.2766 | 14 | 23.5954 | 12.616
39041.5473 | 2225 | 0 | 39041.5474 | 2446 | 0 |  | 807 | 1014 | 135.8364 | 0 | 149.3284 | 0 | 1.3584 | 0 | 1.4933 | 0 | 1.3584 | 1.4933 | 16.1519 | 5.6574 | 14.7935
39041.5478 | 2564 | 0 | 39041.5479 | 2293 | 0 |  | 849 | 1056 | 156.5324 | 0 | 139.9878 | 0 | 1.5653 | 0 | 1.3999 | 0 | 1.5653 | 1.3999 | 0.79485 | 12.7074 | 0.77047
39041.5483 | 2568 | 0 | 39041.5483 | 2424 | 0 |  | 891 | 1098 | 156.7766 | 0 | 147.9853 | 0 | 1.5678 | 0 | 1.4799 | 0 | 1.5678 | 1.4799 | 0.63785 | 6.6163 | 0.92992
39041.5488 | 2082 | 0 |  | 2437 | 0 |  | 932 | 1139 | 127.1062 | 0 | 148.779 | 0 | 1.2711 | 0 | 1.4878 | 0 | 1.2711 | 1.4878 | 24.1297 | 6.0476 | 22.8586
39041.5493 | 1993 | 0 | 39041.5493 | 2450 | 0 |  | 975 | 1182 | 121.6728 | 0 | 149.5726 | 0 | 1.2167 | 0 | 1.4957 | 0 | 1.2167 | 1.4957 | 29.6729 | 5.4849 | 28.4561
39041.5498 | 2011 | 0 | 39041.5498 | 1974 | 0 |  | 1017 | 1224 | 122.7717 | 0 | 120.5128 | 0 | 1.2277 | 0 | 1.2051 | 0 | 1.2277 | 1.2051 | 28.5122 | 30.921 | 27.2845

## A1-B3
Open Burn Test 11 |  |  | 2006-11-20 | 12:58 |  |  | Vs = |  | 157.044 |  | R = | 100
Mixed | 7-C | Tray A | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 1 & 3 | Cable A | Odd - | Cable B |  | Odd
Time-3 | N11 | N12 | Time-4 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R3-G | R1-3
39041.5357 | 1 | 0 | 39041.5357 | 1 | 0 |  | -203.5 | 3.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257138 | 257138 | 257137.9994
39041.5361 | 1 | 0 | 39041.5362 | 1 | 0 |  | -161.5 | 45.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257138 | 257138 | 257137.9994
39041.5366 | 1 | 0 | 39041.5366 | 1 | 0 |  | -119.5 | 87.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257138 | 257138 | 257137.9994
39041.5371 | 1 | 0 | 39041.5371 | 1 | 0 |  | -77.5 | 129.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257138 | 257138 | 257137.9994
39041.5376 | 1 | 0 | 39041.5376 | 1 | 0 |  | -35.5 | 171.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257138 | 257138 | 257137.9994
39041.5381 | 1 | 0 | 39041.5381 | 1 | 0 |  | 6.5 | 213.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257138 | 257138 | 257137.9994
39041.5386 | 1 | 0 | 39041.5386 | 1 | 0 |  | 48.5 | 255.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257138 | 257138 | 257137.9994
39041.5391 | 1 | 0 | 39041.5391 | 1 | 0 |  | 90.5 | 297.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257138 | 257138 | 257137.9994
39041.5395 | 1 | 0 | 39041.5396 | 1 | 0 |  | 132.5 | 339.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257138 | 257138 | 257137.9994
39041.54 | 1 | 0 | 39041.54 | 1 | 0 |  | 174.5 | 381.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257138 | 257138 | 257137.9994
39041.5405 | 1 | 0 | 39041.5405 | 450 | 0 |  | 216.5 | 423.5 | 0.06105 | 0 | 27.4725 | 0 | 0.0006105 | 0 | 0.27473 | 0 | 0.0006105 | 0.27473 | 257138 | 471.64 | 257137.9994
39041.541 | 394 | 0 | 39041.541 | 1331 | 0 |  | 258.5 | 465.5 | 24.0537 | 0 | 81.2576 | 0 | 0.24054 | 0 | 0.81258 | 0 | 0.24054 | 0.81258 | 552.8883 | 93.2667 | 552.6478
39041.5415 | 1266 | 0 | 39041.5415 | 2175 | 0 |  | 300.5 | 507.5 | 77.2894 | 0 | 132.7839 | 0 | 0.77289 | 0 | 1.3278 | 0 | 0.77289 | 1.3278 | 103.1896 | 18.2703 | 102.4167
39041.542 | 1848 | 0 | 39041.542 | 2305 | 0 |  | 342.5 | 549.5 | 112.8205 | 0 | 140.7204 | 0 | 1.1282 | 0 | 1.4072 | 0 | 1.1282 | 1.4072 | 39.1981 | 11.6 | 38.0698
39041.5425 | 2481 | 0 | 39041.5425 | 2131 | 0 |  | 384.5 | 591.5 | 151.4652 | 0 | 130.0977 | 0 | 1.5147 | 0 | 1.301 | 0 | 1.5147 | 1.301 | 3.6832 | 20.7123 | 2.1685
39041.543 | 2294 | 0 | 39041.543 | 2247 | 0 |  | 426.5 | 633.5 | 140.0488 | 0 | 137.1795 | 0 | 1.4005 | 0 | 1.3718 | 0 | 1.4005 | 1.3718 | 12.1351 | 14.4806 | 10.7346
39041.5434 | 2189 | 0 | 39041.5434 | 2146 | 0 |  | 468.5 | 675.5 | 133.6386 | 0 | 131.0134 | 0 | 1.3364 | 0 | 1.3101 | 0 | 1.3364 | 1.3101 | 17.5139 | 19.8686 | 16.1775
39041.5439 | 2208 | 0 | 39041.5439 | 2523 | 0 |  | 510 | 717 | 134.7985 | 0 | 154.0293 | 0 | 1.348 | 0 | 1.5403 | 0 | 1.348 | 1.5403 | 16.5027 | 1.9572 | 15.1547
39041.5444 | 2521 | 0 | 39041.5444 | 2205 | 0 |  | 552.5 | 759.5 | 153.9072 | 0 | 134.6154 | 0 | 1.5391 | 0 | 1.3462 | 0 | 1.5391 | 1.3462 | 2.0381 | 16.6612 | 0.49901
39041.5449 | 2114 | 0 | 39041.5449 | 2556 | 0 |  | 594.5 | 801.5 | 129.0598 | 0 | 156.044 | 0 | 1.2906 | 0 | 1.5604 | 0 | 1.2906 | 1.5604 | 21.6831 | 0.64085 | 20.3925
39041.5454 | 2094 | 0 | 39041.5454 | 2547 | 0 |  | 636 | 843 | 127.8388 | 0 | 155.4945 | 0 | 1.2784 | 0 | 1.5549 | 0 | 1.2784 | 1.5549 | 22.8453 | 0.99647 | 21.5669
39041.5459 | 2240 | 0 | 39041.5459 | 1984 | 0 |  | 678.5 | 885.5 | 136.7521 | 0 | 121.1233 | 0 | 1.3675 | 0 | 1.2112 | 0 | 1.3675 | 1.2112 | 14.8384 | 29.6562 | 13.4709
39041.5463 | 2043 | 0 | 39041.5464 | 2291 | 0 |  | 720 | 927 | 124.7253 | 0 | 139.8657 | 0 | 1.2473 | 0 | 1.3987 | 0 | 1.2473 | 1.3987 | 25.9119 | 12.282 | 24.6646
39041.5468 | 1994 | 0 | 39041.5469 | 2200 | 0 |  | 762 | 969 | 121.7338 | 0 | 134.3101 | 0 | 1.2173 | 0 | 1.3431 | 0 | 1.2173 | 1.3431 | 29.006 | 16.9264 | 27.7887
39041.5473 | 2269 | 0 | 39041.5473 | 2152 | 0 |  | 804 | 1011 | 138.5226 | 0 | 131.3797 | 0 | 1.3852 | 0 | 1.3138 | 0 | 1.3852 | 1.3138 | 13.3706 | 19.5344 | 11.9854
39041.5478 | 2488 | 0 | 39041.5478 | 2384 | 0 |  | 846 | 1053 | 151.8926 | 0 | 145.5433 | 0 | 1.5189 | 0 | 1.4554 | 0 | 1.5189 | 1.4554 | 3.3915 | 7.9018 | 1.8726
39041.5483 | 2155 | 0 | 39041.5483 | 2436 | 0 |  | 888 | 1095 | 131.5629 | 0 | 148.7179 | 0 | 1.3156 | 0 | 1.4872 | 0 | 1.3156 | 1.4872 | 19.368 | 5.5985 | 18.0524
39041.5488 | 2047 | 0 | 39041.5488 | 2499 | 0 |  | 930 | 1137 | 124.9695 | 0 | 152.5641 | 0 | 1.2497 | 0 | 1.5256 | 0 | 1.2497 | 1.5256 | 25.6659 | 2.9364 | 24.4162
39041.5493 | 1969 | 0 | 39041.5493 | 1980 | 0 |  | 972.5 | 1179.5 | 120.2076 | 0 | 120.8791 | 0 | 1.2021 | 0 | 1.2088 | 0 | 1.2021 | 1.2088 | 30.644 | 29.9182 | 29.4419
39041.5497 | 2202 | 0 | 39041.5498 | 2342 | 0 |  | 1014 | 1221 | 134.4322 | 0 | 142.9792 | 0 | 1.3443 | 0 | 1.4298 | 0 | 1.3443 | 1.4298 | 16.8202 | 9.8369 | 15.4758

## A1-A2
Open Burn Test 11 |  |  | 2006-11-20 | 12:58 |  |  | Vs = |  | 158.5092 |  | R = | 100
Mixed | 7-C | Tray A | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 1 & 2 | Cable A | Odd-Even
Time-1 | N11 | N12 | Time-2 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R2-G | R1-2
39041.5356 | 1 | 0 | 39041.5356 | 1 | 0 |  | -206.5 | 0.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259538 | 259538 | 259537.9994
39041.5361 | 1 | 0 | 39041.5361 | 1 | 0 |  | -164.5 | 42.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259538 | 259538 | 259537.9994
39041.5366 | 1 | 0 | 39041.5366 | 1 | 0 |  | -122.5 | 84.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259538 | 259538 | 259537.9994
39041.5371 | 1 | 0 | 39041.5371 | 1 | 0 |  | -80.5 | 126.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259538 | 259538 | 259537.9994
39041.5376 | 1 | 0 | 39041.5376 | 1 | 0 |  | -38.5 | 168.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259538 | 259538 | 259537.9994
39041.5381 | 1 | 0 | 39041.5381 | 1 | 0 |  | 3.5 | 210.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259538 | 259538 | 259537.9994
39041.5385 | 1 | 0 | 39041.5386 | 1 | 0 |  | 45.5 | 252.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259538 | 259538 | 259537.9994
39041.539 | 1 | 0 | 39041.539 | 1 | 0 |  | 87.5 | 294.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259538 | 259538 | 259537.9994
39041.5395 | 1 | 0 | 39041.5395 | 1 | 0 |  | 129.5 | 336.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259538 | 259538 | 259537.9994
39041.54 | 1 | 0 | 39041.54 | 1 | 0 |  | 171.5 | 378.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259538 | 259538 | 259537.9994
39041.5405 | 1 | 0 | 39041.5405 | 1 | 0 |  | 213.5 | 420.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259538 | 259538 | 259537.9994
39041.541 | 412 | 256 | 39041.541 | 916 | 678 |  | 255.5 | 462.5 | 25.1526 | 15.6288 | 55.9219 | 41.3919 | 0.25153 | 0.15629 | 0.55922 | 0.41392 | 0.095238 | 0.1453 | 1737.9843 | 844.4575 | 673.5162
39041.5415 | 1629 | 599 | 39041.5415 | 1563 | 542 |  | 297.5 | 504.5 | 99.4505 | 36.569 | 95.4212 | 33.0891 | 0.99451 | 0.36569 | 0.95421 | 0.33089 | 0.62882 | 0.62332 | 149.0746 | 157.1863 | 37.5869
39041.5419 | 2296 | 74 | 39041.542 | 2115 | 66 |  | 339.5 | 546.5 | 140.1709 | 4.5177 | 129.1209 | 4.0293 | 1.4017 | 0.045177 | 1.2912 | 0.040293 | 1.3565 | 1.2509 | 15.2193 | 29.8006 | 70.2351
39041.5424 | 2107 | 0 | 39041.5424 | 2497 | 0 |  | 381.5 | 588.5 | 128.6325 | 0 | 152.442 | 0 | 1.2863 | 0 | 1.5244 | 0 | 1.2863 | 1.5244 | 23.2264 | 3.98 | 21.9401
39041.5429 | 1979 | 0 | 39041.5429 | 2130 | 0 |  | 423.5 | 630.5 | 120.8181 | 0 | 130.0366 | 0 | 1.2082 | 0 | 1.3004 | 0 | 1.2082 | 1.3004 | 31.1966 | 21.8958 | 29.9884
39041.5434 | 2262 | 0 | 39041.5434 | 2317 | 0 |  | 465.5 | 672.5 | 138.0952 | 0 | 141.453 | 0 | 1.381 | 0 | 1.4145 | 0 | 1.381 | 1.4145 | 14.7825 | 12.0578 | 13.4015
39041.5439 | 2203 | 0 | 39041.5439 | 2140 | 0 |  | 507.5 | 714.5 | 134.4933 | 0 | 130.6471 | 0 | 1.3449 | 0 | 1.3065 | 0 | 1.3449 | 1.3065 | 17.8566 | 21.3262 | 16.5116
39041.5444 | 2246 | 0 | 39041.5444 | 2307 | 0 |  | 549.5 | 756.5 | 137.1184 | 0 | 140.8425 | 0 | 1.3712 | 0 | 1.4084 | 0 | 1.3712 | 1.4084 | 15.6002 | 12.5436 | 14.229
39041.5449 | 2038 | 0 | 39041.5449 | 2553 | 0 |  | 591.5 | 798.5 | 124.42 | 0 | 155.8608 | 0 | 1.2442 | 0 | 1.5586 | 0 | 1.2442 | 1.5586 | 27.3984 | 1.6992 | 26.1542
39041.5453 | 2045 | 0 | 39041.5454 | 2102 | 0 |  | 633.5 | 840.5 | 124.8474 | 0 | 128.3272 | 0 | 1.2485 | 0 | 1.2833 | 0 | 1.2485 | 1.2833 | 26.9623 | 23.5195 | 25.7139
39041.5458 | 1999 | 0 | 39041.5458 | 2259 | 0 |  | 675.5 | 882.5 | 122.0391 | 0 | 137.9121 | 0 | 1.2204 | 0 | 1.3791 | 0 | 1.2204 | 1.3791 | 29.8839 | 14.9349 | 28.6636
39041.5463 | 2304 | 0 | 39041.5463 | 2319 | 0 |  | 717.5 | 924.5 | 140.6593 | 0 | 141.5751 | 0 | 1.4066 | 0 | 1.4158 | 0 | 1.4066 | 1.4158 | 12.6901 | 11.9612 | 11.2835
39041.5468 | 2405 | 0 | 39041.5468 | 2055 | 0 |  | 759.5 | 966.5 | 146.8254 | 0 | 125.4579 | 0 | 1.4683 | 0 | 1.2546 | 0 | 1.4683 | 1.2546 | 7.9576 | 26.3445 | 6.4893
39041.5473 | 2580 | 0 | 39041.5473 | 2484 | 0 |  | 801.5 | 1008.5 | 157.5092 | 0 | 151.6484 | 0 | 1.5751 | 0 | 1.5165 | 0 | 1.5751 | 1.5165 | 0.63488 | 4.5242 | 0.94021
39041.5478 | 2463 | 0 | 39041.5478 | 2245 | 0 |  | 843.5 | 1050.5 | 150.3663 | 0 | 137.0574 | 0 | 1.5037 | 0 | 1.3706 | 0 | 1.5037 | 1.3706 | 5.4153 | 15.6517 | 3.9117
39041.5483 | 2240 | 0 | 39041.5483 | 2080 | 0 |  | 885.5 | 1092.5 | 136.7521 | 0 | 126.9841 | 0 | 1.3675 | 0 | 1.2698 | 0 | 1.3675 | 1.2698 | 15.9098 | 24.826 | 14.5423
39041.5488 | 2057 | 0 | 39041.5488 | 2322 | 0 |  | 927.5 | 1134.5 | 125.58 | 0 | 141.7582 | 0 | 1.2558 | 0 | 1.4176 | 0 | 1.2558 | 1.4176 | 26.2217 | 11.8165 | 24.9659
39041.5492 | 2267 | 0 | 39041.5492 | 2552 | 0 |  | 969.5 | 1176.5 | 138.4005 | 0 | 155.7998 | 0 | 1.384 | 0 | 1.558 | 0 | 1.384 | 1.558 | 14.5293 | 1.739 | 13.1453
39041.5497 | 2403 | 0 | 39041.5497 | 2142 | 0 |  | 1011.5 | 1218.5 | 146.7033 | 0 | 130.7692 | 0 | 1.467 | 0 | 1.3077 | 0 | 1.467 | 1.3077 | 8.0474 | 21.2129 | 6.5804

## Raw IRMS Data
Time | DL1.V2000:B | DL1.V2001:B | DL1.V1500:B | Open Burn Test 11 |  |  | 2006-11-20 | 12:58
39041.5356 | 1 | 0 | 1 | Mixed | 7-C | Tray A | IRMS | 1
39041.5361 | 1 | 0 | 1 |  | 250 kW |  | Bundle
39041.5366 | 1 | 0 | 1
39041.5371 | 1 | 0 | 1
39041.5376 | 1 | 0 | 1
39041.5381 | 1 | 0 | 1
39041.5385 | 1 | 0 | 1
39041.539 | 1 | 0 | 1
39041.5395 | 1 | 0 | 1
39041.54 | 1 | 0 | 1
39041.5405 | 1 | 0 | 1
39041.541 | 412 | 256 | 1
39041.5415 | 1629 | 599 | 1
39041.5419 | 2296 | 74 | 1
39041.5424 | 2107 | 0 | 1
39041.5429 | 1979 | 0 | 1
39041.5434 | 2262 | 0 | 1
39041.5439 | 2203 | 0 | 1
39041.5444 | 2246 | 0 | 1
39041.5449 | 2038 | 0 | 1
39041.5453 | 2045 | 0 | 1
39041.5458 | 1999 | 0 | 1
39041.5463 | 2304 | 0 | 1
39041.5468 | 2405 | 0 | 1
39041.5473 | 2580 | 0 | 1
39041.5478 | 2463 | 0 | 1
39041.5483 | 2240 | 0 | 1
39041.5488 | 2057 | 0 | 1
39041.5492 | 2267 | 0 | 1
39041.5497 | 2403 | 0 | 1
1
39041.5356 | 1 | 0 | 2
39041.5361 | 1 | 0 | 2
39041.5366 | 1 | 0 | 2
39041.5371 | 1 | 0 | 2
39041.5376 | 1 | 0 | 2
39041.5381 | 1 | 0 | 2
39041.5386 | 1 | 0 | 2
39041.539 | 1 | 0 | 2
39041.5395 | 1 | 0 | 2
39041.54 | 1 | 0 | 2
39041.5405 | 1 | 0 | 2
39041.541 | 916 | 678 | 2
39041.5415 | 1563 | 542 | 2
39041.542 | 2115 | 66 | 2
39041.5424 | 2497 | 0 | 2
39041.5429 | 2130 | 0 | 2
39041.5434 | 2317 | 0 | 2
39041.5439 | 2140 | 0 | 2
39041.5444 | 2307 | 0 | 2
39041.5449 | 2553 | 0 | 2
39041.5454 | 2102 | 0 | 2
39041.5458 | 2259 | 0 | 2
39041.5463 | 2319 | 0 | 2
39041.5468 | 2055 | 0 | 2
39041.5473 | 2484 | 0 | 2
39041.5478 | 2245 | 0 | 2
39041.5483 | 2080 | 0 | 2
39041.5488 | 2322 | 0 | 2
39041.5492 | 2552 | 0 | 2
39041.5497 | 2142 | 0 | 2
2
39041.5357 | 1 | 0 | 3
39041.5361 | 1 | 0 | 3
39041.5366 | 1 | 0 | 3
39041.5371 | 1 | 0 | 3
39041.5376 | 1 | 0 | 3
39041.5381 | 1 | 0 | 3
39041.5386 | 1 | 0 | 3
39041.5391 | 1 | 0 | 3
39041.5395 | 1 | 0 | 3
39041.54 | 1 | 0 | 3
39041.5405 | 1 | 0 | 3
39041.541 | 394 | 0 | 3
39041.5415 | 1266 | 0 | 3
39041.542 | 1848 | 0 | 3
39041.5425 | 2481 | 0 | 3
39041.543 | 2294 | 0 | 3
39041.5434 | 2189 | 0 | 3
39041.5439 | 2208 | 0 | 3
39041.5444 | 2521 | 0 | 3
39041.5449 | 2114 | 0 | 3
39041.5454 | 2094 | 0 | 3
39041.5459 | 2240 | 0 | 3
39041.5463 | 2043 | 0 | 3
39041.5468 | 1994 | 0 | 3
39041.5473 | 2269 | 0 | 3
39041.5478 | 2488 | 0 | 3
39041.5483 | 2155 | 0 | 3
39041.5488 | 2047 | 0 | 3
39041.5493 | 1969 | 0 | 3
39041.5497 | 2202 | 0 | 3
3
39041.5357 | 1 | 0 | 4
39041.5362 | 1 | 0 | 4
39041.5366 | 1 | 0 | 4
39041.5371 | 1 | 0 | 4
39041.5376 | 1 | 0 | 4
39041.5381 | 1 | 0 | 4
39041.5386 | 1 | 0 | 4
39041.5391 | 1 | 0 | 4
39041.5396 | 1 | 0 | 4
39041.54 | 1 | 0 | 4
39041.5405 | 450 | 0 | 4
39041.541 | 1331 | 0 | 4
39041.5415 | 2175 | 0 | 4
39041.542 | 2305 | 0 | 4
39041.5425 | 2131 | 0 | 4
39041.543 | 2247 | 0 | 4
39041.5434 | 2146 | 0 | 4
39041.5439 | 2523 | 0 | 4
39041.5444 | 2205 | 0 | 4
39041.5449 | 2556 | 0 | 4
39041.5454 | 2547 | 0 | 4
39041.5459 | 1984 | 0 | 4
39041.5464 | 2291 | 0 | 4
39041.5469 | 2200 | 0 | 4
39041.5473 | 2152 | 0 | 4
39041.5478 | 2384 | 0 | 4
39041.5483 | 2436 | 0 | 4
39041.5488 | 2499 | 0 | 4
39041.5493 | 1980 | 0 | 4
39041.5498 | 2342 | 0 | 4
4
39041.5357 | 1 | 0 | 5
39041.5362 | 1 | 0 | 5
39041.5367 | 1 | 0 | 5
39041.5371 | 1 | 0 | 5
39041.5376 | 1 | 0 | 5
39041.5381 | 1 | 0 | 5
39041.5386 | 1 | 0 | 5
39041.5391 | 1 | 0 | 5
39041.5396 | 1 | 0 | 5
39041.5401 | 1 | 0 | 5
39041.5405 | 1 | 0 | 5
39041.541 | 463 | 0 | 5
39041.5415 | 1483 | 0 | 5
39041.542 | 2078 | 0 | 5
39041.5425 | 2416 | 0 | 5
39041.543 | 2521 | 0 | 5
39041.5435 | 2545 | 0 | 5
39041.5439 | 1993 | 0 | 5
39041.5444 | 2279 | 0 | 5
39041.5449 | 2381 | 0 | 5
39041.5454 | 2028 | 0 | 5
39041.5459 | 2086 | 0 | 5
39041.5464 | 2043 | 0 | 5
39041.5469 | 2267 | 0 | 5
39041.5473 | 2225 | 0 | 5
39041.5478 | 2564 | 0 | 5
39041.5483 | 2568 | 0 | 5
39041.5488 | 2082 | 0 | 5
39041.5493 | 1993 | 0 | 5
39041.5498 | 2011 | 0 | 5
5
39041.5357 | 1 | 0 | 6
39041.5362 | 1 | 0 | 6
39041.5367 | 1 | 0 | 6
39041.5372 | 1 | 0 | 6
39041.5377 | 1 | 0 | 6
39041.5381 | 1 | 0 | 6
39041.5386 | 1 | 0 | 6
39041.5391 | 1 | 0 | 6
39041.5396 | 1 | 0 | 6
39041.5401 | 1 | 0 | 6
39041.5406 | 691 | 0 | 6
39041.5411 | 1560 | 0 | 6
39041.5415 | 1879 | 0 | 6
39041.542 | 2366 | 0 | 6
39041.5425 | 2018 | 0 | 6
39041.543 | 2424 | 0 | 6
39041.5435 | 2161 | 0 | 6
39041.544 | 2044 | 0 | 6
39041.5445 | 2536 | 0 | 6
39041.5449 | 2005 | 0 | 6
39041.5454 | 2553 | 0 | 6
39041.5459 | 2225 | 0 | 6
39041.5464 | 2432 | 0 | 6
39041.5469 | 2091 | 0 | 6
39041.5474 | 2446 | 0 | 6
39041.5479 | 2293 | 0 | 6
39041.5483 | 2424 | 0 | 6
39041.5493 | 2450 | 0 | 6
39041.5498 | 1974 | 0 | 6
6
39041.5357 | 1 | 0 | 7
39041.5362 | 1 | 0 | 7
39041.5367 | 1 | 0 | 7
39041.5372 | 1 | 0 | 7
39041.5377 | 1 | 0 | 7
39041.5381 | 1 | 0 | 7
39041.5386 | 1 | 0 | 7
39041.5391 | 1 | 0 | 7
39041.5396 | 1 | 0 | 7
39041.5401 | 1 | 0 | 7
39041.5406 | 1 | 0 | 7
39041.5411 | 290 | 0 | 7
39041.5416 | 1628 | 0 | 7
39041.542 | 2266 | 0 | 7
39041.5425 | 2265 | 0 | 7
39041.543 | 2038 | 0 | 7
39041.5435 | 2402 | 0 | 7
39041.544 | 2305 | 0 | 7
39041.5445 | 1993 | 0 | 7
39041.545 | 2580 | 0 | 7
39041.5454 | 2437 | 0 | 7
39041.5459 | 2072 | 0 | 7
39041.5464 | 2232 | 0 | 7
39041.5469 | 2443 | 0 | 7
39041.5474 | 2040 | 0 | 7
39041.5479 | 2156 | 0 | 7
39041.5484 | 2216 | 0 | 7
39041.5488 | 2253 | 0 | 7
39041.5493 | 2214 | 0 | 7
39041.5498 | 2262 | 0 | 7
7
39041.5357 | 1 | 0 | 8
39041.5362 | 1 | 0 | 8
39041.5367 | 1 | 0 | 8
39041.5372 | 1 | 0 | 8
39041.5377 | 1 | 0 | 8
39041.5382 | 1 | 0 | 8
39041.5387 | 1 | 0 | 8
39041.5391 | 1 | 0 | 8
39041.5396 | 1 | 0 | 8
39041.5401 | 1 | 0 | 8
39041.5406 | 1 | 0 | 8
39041.5411 | 135 | 0 | 8
39041.5416 | 1503 | 0 | 8
39041.5421 | 1631 | 0 | 8
39041.5425 | 2535 | 0 | 8
39041.543 | 2300 | 0 | 8
39041.5435 | 2058 | 0 | 8
39041.544 | 2098 | 0 | 8
39041.5445 | 2174 | 0 | 8
39041.545 | 2416 | 0 | 8
39041.5455 | 2335 | 0 | 8
39041.5459 | 2116 | 0 | 8
39041.5464 | 2051 | 0 | 8
39041.5469 | 2583 | 0 | 8
39041.5474 | 2571 | 0 | 8
39041.5479 | 2056 | 0 | 8
39041.5484 | 2230 | 0 | 8
39041.5489 | 2509 | 0 | 8
39041.5494 | 2212 | 0 | 8
39041.5498 | 2494 | 0 | 8
8
39041.5358 | 1 | 0 | 9
39041.5362 | 1 | 0 | 9
39041.5367 | 1 | 0 | 9
39041.5372 | 1 | 0 | 9
39041.5377 | 1 | 0 | 9
39041.5382 | 1 | 0 | 9
39041.5387 | 1 | 0 | 9
39041.5392 | 1 | 0 | 9
39041.5396 | 1 | 0 | 9
39041.5401 | 1 | 0 | 9
39041.5406 | 1 | 0 | 9
39041.5411 | 387 | 0 | 9
39041.5416 | 1967 | 0 | 9
39041.5421 | 2414 | 0 | 9
39041.5426 | 2554 | 0 | 9
39041.543 | 2500 | 0 | 9
39041.5435 | 2035 | 0 | 9
39041.544 | 2103 | 0 | 9
39041.5445 | 2387 | 0 | 9
39041.545 | 2200 | 0 | 9
39041.5455 | 2126 | 0 | 9
39041.546 | 2148 | 0 | 9
39041.5464 | 2260 | 0 | 9
39041.5469 | 2562 | 0 | 9
39041.5474 | 2195 | 0 | 9
39041.5479 | 2202 | 0 | 9
39041.5484 | 2078 | 0 | 9
39041.5489 | 2338 | 0 | 9
39041.5494 | 2315 | 0 | 9
39041.5498 | 2230 | 0 | 9
9
39041.5358 | 1 | 0 | 10
39041.5362 | 1 | 0 | 10
39041.5367 | 1 | 0 | 10
39041.5372 | 1 | 0 | 10
39041.5377 | 1 | 0 | 10
39041.5382 | 1 | 0 | 10
39041.5387 | 1 | 0 | 10
39041.5392 | 1 | 0 | 10
39041.5397 | 1 | 0 | 10
39041.5401 | 1 | 0 | 10
39041.5406 | 1 | 0 | 10
39041.5411 | 1 | 0 | 10
39041.5416 | 297 | 0 | 10
39041.5421 | 1744 | 0 | 10
39041.5426 | 2022 | 0 | 10
39041.5431 | 2007 | 0 | 10
39041.5435 | 2481 | 0 | 10
39041.544 | 2582 | 0 | 10
39041.5445 | 2188 | 0 | 10
39041.545 | 2359 | 0 | 10
39041.5455 | 2414 | 0 | 10
39041.546 | 2486 | 0 | 10
39041.5465 | 2548 | 0 | 10
39041.5469 | 2239 | 0 | 10
39041.5474 | 2165 | 0 | 10
39041.5479 | 2478 | 0 | 10
39041.5484 | 2569 | 0 | 10
39041.5489 | 2485 | 0 | 10
39041.5494 | 2552 | 0 | 10
39041.5499 | 2211 | 0 | 10
10
39041.5358 | 1 | 0 | 11
39041.5363 | 1 | 0 | 11
39041.5368 | 1 | 0 | 11
39041.5372 | 1 | 0 | 11
39041.5377 | 1 | 0 | 11
39041.5382 | 1 | 0 | 11
39041.5387 | 1 | 0 | 11
39041.5392 | 1 | 0 | 11
39041.5397 | 1 | 0 | 11
39041.5402 | 1 | 0 | 11
39041.5406 | 1 | 0 | 11
39041.5411 | 279 | 0 | 11
39041.5416 | 1968 | 0 | 11
39041.5421 | 2294 | 0 | 11
39041.5426 | 2196 | 0 | 11
39041.5431 | 2549 | 0 | 11
39041.5436 | 2402 | 0 | 11
39041.5441 | 2129 | 0 | 11
39041.5445 | 2141 | 0 | 11
39041.545 | 2240 | 0 | 11
39041.5455 | 2108 | 0 | 11
39041.546 | 2576 | 0 | 11
39041.5465 | 2477 | 0 | 11
39041.547 | 2063 | 0 | 11
39041.5475 | 2116 | 0 | 11
39041.5479 | 1991 | 0 | 11
39041.5484 | 2002 | 0 | 11
39041.5489 | 2014 | 0 | 11
39041.5494 | 2133 | 0 | 11
39041.5499 | 2033 | 0 | 11
11
39041.5358 | 1 | 0 | 12
39041.5363 | 1 | 0 | 12
39041.5368 | 1 | 0 | 12
39041.5373 | 1 | 0 | 12
39041.5377 | 1 | 0 | 12
39041.5382 | 1 | 0 | 12
39041.5387 | 1 | 0 | 12
39041.5392 | 1 | 0 | 12
39041.5397 | 1 | 0 | 12
39041.5402 | 1 | 0 | 12
39041.5407 | 1220 | 0 | 12
39041.5411 | 1781 | 0 | 12
39041.5416 | 1971 | 0 | 12
39041.5421 | 2025 | 0 | 12
39041.5426 | 2351 | 0 | 12
39041.5431 | 2076 | 0 | 12
39041.5436 | 2206 | 0 | 12
39041.5441 | 2171 | 0 | 12
39041.5445 | 2232 | 0 | 12
39041.545 | 2415 | 0 | 12
39041.5455 | 2257 | 0 | 12
39041.546 | 1980 | 0 | 12
39041.5465 | 2465 | 0 | 12
39041.547 | 2325 | 0 | 12
39041.5475 | 2049 | 0 | 12
39041.548 | 2372 | 0 | 12
39041.5484 | 2015 | 0 | 12
39041.5489 | 2250 | 0 | 12
39041.5494 | 2319 | 0 | 12
39041.5499 | 2027 | 0 | 12
12
39041.5358 | 1 | 0 | 13
39041.5363 | 1 | 0 | 13
39041.5368 | 1 | 0 | 13
39041.5373 | 1 | 0 | 13
39041.5378 | 1 | 0 | 13
39041.5383 | 1 | 0 | 13
39041.5387 | 0 | 0 | 13
39041.5392 | 1 | 0 | 13
39041.5397 | 1 | 0 | 13
39041.5402 | 1 | 0 | 13
39041.5407 | 1 | 0 | 13
39041.5412 | 348 | 0 | 13
39041.5417 | 1872 | 0 | 13
39041.5421 | 2346 | 0 | 13
39041.5426 | 2176 | 0 | 13
39041.5431 | 2475 | 0 | 13
39041.5436 | 2407 | 0 | 13
39041.5441 | 2061 | 0 | 13
39041.5446 | 2186 | 0 | 13
39041.5451 | 2581 | 0 | 13
39041.5455 | 2583 | 0 | 13
39041.546 | 2207 | 0 | 13
39041.5465 | 2026 | 0 | 13
39041.547 | 2385 | 0 | 13
39041.5475 | 2573 | 0 | 13
39041.548 | 2380 | 0 | 13
39041.5484 | 2254 | 0 | 13
39041.5489 | 2363 | 0 | 13
39041.5494 | 2313 | 0 | 13
39041.5499 | 2330 | 0 | 13
13
39041.5358 | 1 | 0 | 14
39041.5363 | 1 | 0 | 14
39041.5368 | 1 | 0 | 14
39041.5373 | 1 | 0 | 14
39041.5378 | 1 | 0 | 14
39041.5383 | 1 | 0 | 14
39041.5387 | 1 | 0 | 14
39041.5392 | 1 | 0 | 14
39041.5397 | 1 | 0 | 14
39041.5402 | 1 | 0 | 14
39041.5407 | 1 | 0 | 14
39041.5412 | 492 | 0 | 14
39041.5417 | 1932 | 0 | 14
39041.5422 | 2203 | 0 | 14
39041.5426 | 2061 | 0 | 14
39041.5431 | 2318 | 0 | 14
39041.5436 | 2367 | 0 | 14
39041.5441 | 2436 | 0 | 14
39041.5446 | 2086 | 0 | 14
39041.5451 | 2489 | 0 | 14
39041.5456 | 2429 | 0 | 14
39041.546 | 2072 | 0 | 14
39041.5465 | 2505 | 0 | 14
39041.547 | 2258 | 0 | 14
39041.5475 | 2101 | 0 | 14
39041.548 | 2120 | 0 | 14
39041.5485 | 2440 | 0 | 14
39041.549 | 2561 | 0 | 14
39041.5494 | 1971 | 0 | 14
39041.5499 | 2113 | 0 | 14
14
39041.5358 | 1 | 0 | 15
39041.5363 | 1 | 0 | 15
39041.5368 | 1 | 0 | 15
39041.5373 | 1 | 0 | 15
39041.5378 | 1 | 0 | 15
39041.5383 | 1 | 0 | 15
39041.5388 | 1 | 0 | 15
39041.5392 | 1 | 0 | 15
39041.5397 | 1 | 0 | 15
39041.5402 | 1 | 0 | 15
39041.5407 | 1 | 0 | 15
39041.5412 | 593 | 0 | 15
39041.5417 | 1911 | 0 | 15
39041.5422 | 2133 | 0 | 15
39041.5427 | 2504 | 0 | 15
39041.5431 | 2244 | 0 | 15
39041.5436 | 2096 | 0 | 15
39041.5441 | 2188 | 0 | 15
39041.5446 | 2503 | 0 | 15
39041.5451 | 2117 | 0 | 15
39041.5456 | 2353 | 0 | 15
39041.5461 | 2146 | 0 | 15
39041.5465 | 2357 | 0 | 15
39041.547 | 2018 | 0 | 15
39041.5475 | 2459 | 0 | 15
39041.548 | 1987 | 0 | 15
39041.5485 | 2142 | 0 | 15
39041.549 | 2024 | 0 | 15
39041.5495 | 2187 | 0 | 15
39041.5499 | 1989 | 0 | 15
15
39041.5359 | 1 | 0 | 16
39041.5364 | 1 | 0 | 16
39041.5368 | 1 | 0 | 16
39041.5373 | 1 | 0 | 16
39041.5378 | 0 | 0 | 16
39041.5383 | 1 | 0 | 16
39041.5388 | 1 | 0 | 16
39041.5393 | 1 | 0 | 16
39041.5398 | 1 | 0 | 16
39041.5402 | 1 | 0 | 16
39041.5407 | 1 | 0 | 16
39041.5412 | 213 | 0 | 16
39041.5417 | 1622 | 0 | 16
39041.5422 | 2185 | 0 | 16
39041.5427 | 2379 | 0 | 16
39041.5432 | 2245 | 0 | 16
39041.5436 | 2255 | 0 | 16
39041.5441 | 2499 | 0 | 16
39041.5446 | 2015 | 0 | 16
39041.5451 | 2073 | 0 | 16
39041.5456 | 2261 | 0 | 16
39041.5461 | 2066 | 0 | 16
39041.5466 | 2551 | 0 | 16
39041.547 | 2465 | 0 | 16
39041.5475 | 2587 | 0 | 16
39041.548 | 2178 | 0 | 16
39041.5485 | 2597 | 0 | 16
39041.549 | 2079 | 0 | 16
39041.5495 | 2522 | 0 | 16
39041.55 | 2326 | 0 | 16
16
39041.5359 | 1 | 0 | 17
39041.5364 | 1 | 0 | 17
39041.5369 | 1 | 0 | 17
39041.5373 | 1 | 0 | 17
39041.5378 | 1 | 0 | 17
39041.5383 | 1 | 0 | 17
39041.5388 | 1 | 0 | 17
39041.5393 | 1 | 0 | 17
39041.5398 | 1 | 0 | 17
39041.5403 | 1 | 0 | 17
39041.5407 | 1 | 0 | 17
39041.5412 | 533 | 0 | 17
39041.5417 | 2071 | 0 | 17
39041.5422 | 2031 | 0 | 17
39041.5427 | 2029 | 0 | 17
39041.5432 | 2282 | 0 | 17
39041.5437 | 2573 | 0 | 17
39041.5441 | 2575 | 0 | 17
39041.5446 | 2220 | 0 | 17
39041.5451 | 2057 | 0 | 17
39041.5456 | 2406 | 0 | 17
39041.5461 | 2583 | 0 | 17
39041.5466 | 1991 | 0 | 17
39041.5471 | 2171 | 0 | 17
39041.5475 | 1987 | 0 | 17
39041.548 | 2182 | 0 | 17
39041.5485 | 2355 | 0 | 17
39041.549 | 2507 | 0 | 17
39041.5495 | 2349 | 0 | 17
39041.55 | 2495 | 0 | 17
17
39041.5359 | 1 | 0 | 18
39041.5364 | 1 | 0 | 18
39041.5369 | 1 | 0 | 18
39041.5374 | 1 | 0 | 18
39041.5378 | 1 | 0 | 18
39041.5383 | 1 | 0 | 18
39041.5388 | 1 | 0 | 18
39041.5393 | 1 | 0 | 18
39041.5398 | 1 | 0 | 18
39041.5403 | 1 | 0 | 18
39041.5408 | 1 | 0 | 18
39041.5413 | 274 | 0 | 18
39041.5417 | 336 | 0 | 18
39041.5422 | 2221 | 0 | 18
39041.5427 | 2489 | 0 | 18
39041.5432 | 2107 | 0 | 18
39041.5437 | 2279 | 0 | 18
39041.5442 | 2199 | 0 | 18
39041.5446 | 2480 | 0 | 18
39041.5451 | 2209 | 0 | 18
39041.5456 | 2066 | 0 | 18
39041.5461 | 2490 | 0 | 18
39041.5466 | 2278 | 0 | 18
39041.5471 | 2366 | 0 | 18
39041.5476 | 2406 | 0 | 18
39041.548 | 2321 | 0 | 18
39041.5485 | 2158 | 0 | 18
39041.549 | 2610 | 0 | 18
39041.5495 | 2582 | 0 | 18
39041.55 | 2112 | 0 | 18
18
39041.5359 | 1 | 0 | 19
39041.5364 | 1 | 0 | 19
39041.5369 | 1 | 0 | 19
39041.5374 | 1 | 0 | 19
39041.5379 | 1 | 0 | 19
39041.5383 | 1 | 0 | 19
39041.5388 | 1 | 0 | 19
39041.5393 | 1 | 0 | 19
39041.5398 | 1 | 0 | 19
39041.5403 | 433 | 326 | 19
39041.5408 | 1372 | 378 | 19
39041.5413 | 2002 | 38 | 19
39041.5417 | 2440 | 0 | 19
39041.5422 | 2376 | 0 | 19
39041.5427 | 1990 | 0 | 19
39041.5432 | 2162 | 0 | 19
39041.5437 | 2382 | 0 | 19
39041.5442 | 2406 | 0 | 19
39041.5447 | 2005 | 0 | 19
39041.5452 | 2524 | 0 | 19
39041.5456 | 2321 | 0 | 19
39041.5461 | 2047 | 0 | 19
39041.5466 | 2255 | 0 | 19
39041.5471 | 2480 | 0 | 19
39041.5476 | 2256 | 0 | 19
39041.5481 | 2392 | 0 | 19
39041.5486 | 1960 | 0 | 19
39041.549 | 2265 | 0 | 19
39041.5495 | 2062 | 0 | 19
39041.55 | 2325 | 60 | 19
19
39041.5359 | 1 | 0 | 20
39041.5364 | 1 | 0 | 20
39041.5369 | 1 | 0 | 20
39041.5374 | 1 | 0 | 20
39041.5379 | 1 | 0 | 20
39041.5384 | 1 | 0 | 20
39041.5388 | 1 | 0 | 20
39041.5393 | 1 | 0 | 20
39041.5398 | 1 | 0 | 20
39041.5403 | 451 | 416 | 20
39041.5408 | 1473 | 543 | 20
39041.5413 | 2100 | 41 | 20
39041.5418 | 2260 | 1 | 20
39041.5422 | 2459 | 0 | 20
39041.5427 | 2104 | 0 | 20
39041.5432 | 2090 | 0 | 20
39041.5437 | 2012 | 0 | 20
39041.5442 | 2371 | 0 | 20
39041.5447 | 2375 | 0 | 20
39041.5452 | 2092 | 0 | 20
39041.5456 | 2272 | 0 | 20
39041.5461 | 1958 | 0 | 20
39041.5466 | 2054 | 0 | 20
39041.5471 | 1972 | 0 | 20
39041.5476 | 2247 | 0 | 20
39041.5481 | 2138 | 0 | 20
39041.5486 | 2111 | 0 | 20
39041.5491 | 2137 | 0 | 20
39041.5495 | 2400 | 1 | 20
39041.55 | 1718 | 140 | 20
20
39041.5359 | 1 | 0 | 21
39041.5364 | 1 | 0 | 21
39041.5369 | 1 | 0 | 21
39041.5374 | 1 | 0 | 21
39041.5379 | 1 | 0 | 21
39041.5384 | 1 | 0 | 21
39041.5389 | 1 | 0 | 21
39041.5394 | 1 | 0 | 21
39041.5398 | 1 | 0 | 21
39041.5403 | 139 | 0 | 21
39041.5408 | 1037 | 0 | 21
39041.5413 | 1846 | 0 | 21
39041.5418 | 2120 | 0 | 21
39041.5423 | 2257 | 0 | 21
39041.5428 | 2053 | 0 | 21
39041.5432 | 2570 | 0 | 21
39041.5437 | 2067 | 0 | 21
39041.5442 | 2375 | 0 | 21
39041.5447 | 2240 | 0 | 21
39041.5452 | 2152 | 0 | 21
39041.5457 | 2054 | 0 | 21
39041.5462 | 2331 | 0 | 21
39041.5466 | 2137 | 0 | 21
39041.5471 | 2539 | 0 | 21
39041.5476 | 2309 | 0 | 21
39041.5481 | 2181 | 0 | 21
39041.5486 | 2298 | 0 | 21
39041.5491 | 2040 | 0 | 21
39041.5496 | 1932 | 0 | 21
39041.55 | 1763 | 0 | 21
21
39041.536 | 1 | 0 | 22
39041.5364 | 1 | 0 | 22
39041.5369 | 1 | 0 | 22
39041.5374 | 1 | 0 | 22
39041.5379 | 1 | 0 | 22
39041.5384 | 0 | 0 | 22
39041.5389 | 1 | 0 | 22
39041.5394 | 1 | 0 | 22
39041.5398 | 1 | 0 | 22
39041.5403 | 1 | 0 | 22
39041.5408 | 1 | 0 | 22
39041.5413 | 1201 | 0 | 22
39041.5418 | 1917 | 0 | 22
39041.5423 | 1823 | 0 | 22
39041.5428 | 2398 | 0 | 22
39041.5433 | 2550 | 0 | 22
39041.5437 | 2421 | 0 | 22
39041.5442 | 2212 | 0 | 22
39041.5447 | 2013 | 0 | 22
39041.5452 | 2082 | 0 | 22
39041.5457 | 2038 | 0 | 22
39041.5462 | 2044 | 0 | 22
39041.5467 | 2300 | 0 | 22
39041.5471 | 2257 | 0 | 22
39041.5476 | 2612 | 0 | 22
39041.5481 | 2164 | 0 | 22
39041.5486 | 2471 | 0 | 22
39041.5491 | 2063 | 0 | 22
39041.5496 | 2094 | 0 | 22
39041.5501 | 2376 | 0 | 22
22
39041.536 | 1 | 0 | 23
39041.5365 | 1 | 0 | 23
39041.537 | 1 | 0 | 23
39041.5374 | 1 | 0 | 23
39041.5379 | 1 | 0 | 23
39041.5389 | 1 | 0 | 23
39041.5394 | 1 | 0 | 23
39041.5399 | 1 | 0 | 23
39041.5404 | 312 | 0 | 23
39041.5408 | 1437 | 0 | 23
39041.5413 | 2283 | 0 | 23
39041.5418 | 2439 | 0 | 23
39041.5423 | 2517 | 0 | 23
39041.5428 | 2072 | 0 | 23
39041.5438 | 2563 | 0 | 23
39041.5442 | 2469 | 0 | 23
39041.5447 | 2256 | 0 | 23
39041.5452 | 2418 | 0 | 23
39041.5457 | 2168 | 0 | 23
39041.5462 | 2007 | 0 | 23
39041.5467 | 2537 | 0 | 23
39041.5472 | 2219 | 0 | 23
39041.5477 | 2153 | 0 | 23
39041.5481 | 2119 | 0 | 23
39041.5486 | 2402 | 0 | 23
39041.5491 | 2305 | 0 | 23
39041.5496 | 2191 | 0 | 23
39041.5501 | 1599 | 0 | 23
23
39041.536 | 1 | 0 | 24
39041.5365 | 1 | 0 | 24
39041.537 | 1 | 0 | 24
39041.5375 | 1 | 0 | 24
39041.5379 | 1 | 0 | 24
39041.5384 | 1 | 0 | 24
39041.5389 | 1 | 0 | 24
39041.5394 | 1 | 0 | 24
39041.5399 | 1 | 0 | 24
39041.5404 | 1 | 0 | 24
39041.5409 | 1 | 0 | 24
39041.5413 | 1087 | 0 | 24
39041.5418 | 971 | 0 | 24
39041.5423 | 2517 | 0 | 24
39041.5428 | 2284 | 0 | 24
39041.5433 | 2188 | 0 | 24
39041.5438 | 2428 | 0 | 24
39041.5443 | 2063 | 0 | 24
39041.5447 | 2060 | 0 | 24
39041.5452 | 2403 | 0 | 24
39041.5457 | 2344 | 0 | 24
39041.5462 | 2560 | 0 | 24
39041.5467 | 2610 | 0 | 24
39041.5472 | 2327 | 0 | 24
39041.5477 | 2253 | 0 | 24
39041.5481 | 2254 | 0 | 24
39041.5486 | 2318 | 0 | 24
39041.5491 | 2607 | 0 | 24
39041.5496 | 2187 | 0 | 24
39041.5501 | 2031 | 0 | 24
24
39041.536 | 1 | 0 | 25
39041.5365 | 1 | 0 | 25
39041.537 | 1 | 0 | 25
39041.5375 | 1 | 0 | 25
39041.538 | 1 | 0 | 25
39041.5384 | 1 | 0 | 25
39041.5389 | 1 | 0 | 25
39041.5394 | 1 | 0 | 25
39041.5399 | 1 | 0 | 25
39041.5404 | 572 | 0 | 25
39041.5409 | 1630 | 0 | 25
39041.5414 | 2104 | 0 | 25
39041.5418 | 2048 | 0 | 25
39041.5423 | 1965 | 0 | 25
39041.5428 | 2497 | 0 | 25
39041.5433 | 2022 | 0 | 25
39041.5438 | 2456 | 0 | 25
39041.5443 | 2003 | 0 | 25
39041.5448 | 2050 | 0 | 25
39041.5452 | 2477 | 0 | 25
39041.5457 | 2216 | 0 | 25
39041.5462 | 2021 | 0 | 25
39041.5467 | 2435 | 0 | 25
39041.5472 | 2506 | 0 | 25
39041.5477 | 2064 | 0 | 25
39041.5482 | 2349 | 0 | 25
39041.5486 | 2290 | 0 | 25
39041.5491 | 1943 | 0 | 25
39041.5496 | 2465 | 0 | 25
39041.5501 | 1716 | 0 | 25
25
39041.536 | 1 | 0 | 26
39041.5365 | 1 | 0 | 26
39041.537 | 1 | 0 | 26
39041.5375 | 1 | 0 | 26
39041.538 | 1 | 0 | 26
39041.5385 | 1 | 0 | 26
39041.5389 | 1 | 0 | 26
39041.5394 | 1 | 0 | 26
39041.5399 | 1 | 0 | 26
39041.5404 | 1 | 0 | 26
39041.5409 | 2 | 0 | 26
39041.5414 | 714 | 0 | 26
39041.5419 | 2077 | 0 | 26
39041.5423 | 2386 | 0 | 26
39041.5428 | 2481 | 0 | 26
39041.5433 | 2270 | 0 | 26
39041.5438 | 2089 | 0 | 26
39041.5443 | 2293 | 0 | 26
39041.5448 | 2557 | 0 | 26
39041.5453 | 2069 | 0 | 26
39041.5458 | 2440 | 0 | 26
39041.5462 | 2126 | 0 | 26
39041.5467 | 2119 | 0 | 26
39041.5472 | 2394 | 0 | 26
39041.5477 | 2014 | 0 | 26
39041.5482 | 2036 | 0 | 26
39041.5487 | 2181 | 0 | 26
39041.5492 | 2069 | 0 | 26
39041.5496 | 2527 | 0 | 26
39041.5501 | 2332 | 0 | 26
26
39041.536 | 1 | 0 | 27
39041.5365 | 1 | 0 | 27
39041.537 | 1 | 0 | 27
39041.5375 | 1 | 0 | 27
39041.538 | 1 | 0 | 27
39041.5385 | 1 | 0 | 27
39041.539 | 1 | 0 | 27
39041.5394 | 1 | 0 | 27
39041.5399 | 1 | 0 | 27
39041.5404 | 919 | 0 | 27
39041.5409 | 1418 | 0 | 27
39041.5414 | 2093 | 0 | 27
39041.5419 | 2509 | 0 | 27
39041.5424 | 2205 | 0 | 27
39041.5428 | 2168 | 0 | 27
39041.5433 | 2320 | 0 | 27
39041.5438 | 2355 | 0 | 27
39041.5443 | 2061 | 0 | 27
39041.5448 | 1975 | 0 | 27
39041.5453 | 1985 | 0 | 27
39041.5458 | 2548 | 0 | 27
39041.5462 | 2255 | 0 | 27
39041.5467 | 1987 | 0 | 27
39041.5472 | 2164 | 0 | 27
39041.5477 | 1976 | 0 | 27
39041.5482 | 2150 | 0 | 27
39041.5487 | 1978 | 0 | 27
39041.5492 | 2025 | 0 | 27
39041.5497 | 2360 | 0 | 27
39041.5501 | 1672 | 0 | 27
27
39041.5361 | 1 | 0 | 28
39041.5366 | 1 | 0 | 28
39041.537 | 1 | 0 | 28
39041.5375 | 1 | 0 | 28
39041.538 | 1 | 0 | 28
39041.5385 | 1 | 0 | 28
39041.539 | 1 | 0 | 28
39041.5395 | 1 | 0 | 28
39041.54 | 1 | 0 | 28
39041.5404 | 1 | 0 | 28
39041.5409 | 1 | 0 | 28
39041.5414 | 8 | 0 | 28
39041.5419 | 1298 | 0 | 28
39041.5424 | 2532 | 0 | 28
39041.5429 | 2001 | 0 | 28
39041.5434 | 2611 | 0 | 28
39041.5438 | 2241 | 0 | 28
39041.5443 | 2139 | 0 | 28
39041.5448 | 2611 | 0 | 28
39041.5453 | 2416 | 0 | 28
39041.5458 | 2612 | 0 | 28
39041.5463 | 2168 | 0 | 28
39041.5468 | 2251 | 0 | 28
39041.5472 | 2451 | 0 | 28
39041.5477 | 2055 | 0 | 28
39041.5482 | 2050 | 0 | 28
39041.5487 | 2243 | 0 | 28
39041.5492 | 2484 | 0 | 28
39041.5497 | 2111 | 0 | 28
39041.5502 | 2555 | 0 | 28
28
39041.5361 | 1 | 0 | 29
39041.5366 | 1 | 0 | 29
39041.537 | 1 | 0 | 29
39041.5375 | 1 | 0 | 29
39041.538 | 1 | 0 | 29
39041.5385 | 1 | 0 | 29
39041.539 | 1 | 0 | 29
39041.5395 | 1 | 0 | 29
39041.54 | 1 | 0 | 29
39041.5405 | 1 | 0 | 29
39041.5409 | 22 | 0 | 29
39041.5414 | 352 | 134 | 29
39041.5419 | 1954 | 222 | 29
39041.5424 | 2531 | 0 | 29
39041.5429 | 2414 | 0 | 29
39041.5434 | 2147 | 0 | 29
39041.5439 | 2326 | 0 | 29
39041.5443 | 2485 | 0 | 29
39041.5448 | 2286 | 0 | 29
39041.5453 | 2370 | 0 | 29
39041.5458 | 2500 | 0 | 29
39041.5463 | 2345 | 0 | 29
39041.5468 | 2334 | 0 | 29
39041.5473 | 2611 | 0 | 29
39041.5477 | 2487 | 0 | 29
39041.5482 | 2599 | 0 | 29
39041.5487 | 2574 | 0 | 29
39041.5492 | 2454 | 0 | 29
39041.5497 | 2122 | 0 | 29
39041.5502 | 2325 | 0 | 29
29
39041.5361 | 1 | 0 | 30
39041.5366 | 1 | 0 | 30
39041.5371 | 1 | 0 | 30
39041.5376 | 1 | 0 | 30
39041.538 | 1 | 0 | 30
39041.5385 | 1 | 0 | 30
39041.539 | 1 | 0 | 30
39041.5395 | 1 | 0 | 30
39041.54 | 1 | 0 | 30
39041.5405 | 1 | 0 | 30
39041.5409 | 20 | 15 | 30
39041.5414 | 154 | 19 | 30
39041.5419 | 1690 | 95 | 30
39041.5424 | 2423 | 0 | 30
39041.5429 | 2133 | 0 | 30
39041.5434 | 2493 | 0 | 30
39041.5439 | 2176 | 0 | 30
39041.5444 | 2491 | 0 | 30
39041.5448 | 2149 | 0 | 30
39041.5453 | 2610 | 0 | 30
39041.5458 | 2039 | 0 | 30
39041.5463 | 2254 | 0 | 30
39041.5468 | 2526 | 0 | 30
39041.5473 | 2064 | 0 | 30
39041.5478 | 2453 | 0 | 30
39041.5482 | 2408 | 0 | 30
39041.5487 | 2605 | 0 | 30
39041.5492 | 2590 | 0 | 30
39041.5497 | 2238 | 0 | 30
39041.5502 | 2394 | 0 | 30
30

## Temperatures
DAQ Time | Burner Time | Bundle center | Air above bundle | Air below bundle | Intra-bundle | TRAY A
0 | -207 | 15.8 | 15.8 | 15.9 | 16 | 18
1 | -206 | 15.8 | 15.8 | 15.9 | 16 | 18.1
2 | -205 | 15.8 | 15.8 | 15.9 | 16 | 18.1
3 | -204 | 15.8 | 15.8 | 15.9 | 16 | 18.1
4 | -203 | 15.8 | 15.8 | 15.9 | 16 | 18.1
5 | -202 | 15.8 | 15.8 | 15.9 | 16 | 18
6 | -201 | 15.8 | 15.8 | 15.9 | 16 | 18.1
7 | -200 | 15.8 | 15.8 | 15.9 | 16 | 18.1
8 | -199 | 15.8 | 15.8 | 15.9 | 16 | 18.1
9 | -198 | 15.8 | 15.8 | 15.9 | 16 | 18.1
10 | -197 | 15.8 | 15.8 | 15.9 | 16 | 18.1
11 | -196 | 15.8 | 15.8 | 15.9 | 16 | 18.1
12 | -195 | 15.8 | 15.8 | 15.9 | 16 | 18.1
13 | -194 | 15.8 | 15.7 | 15.9 | 16 | 18.1
14 | -193 | 15.8 | 15.8 | 15.9 | 16 | 18.1
15 | -192 | 15.8 | 15.8 | 15.9 | 16 | 18.1
16 | -191 | 15.8 | 15.8 | 15.9 | 16 | 18.1
17 | -190 | 15.8 | 15.8 | 15.9 | 16 | 18.1
18 | -189 | 15.8 | 15.8 | 15.9 | 16 | 18.1
19 | -188 | 15.8 | 15.8 | 15.9 | 16 | 18.1
20 | -187 | 15.8 | 15.8 | 15.9 | 16 | 18.1
21 | -186 | 15.8 | 15.8 | 15.9 | 16 | 18.1
22 | -185 | 15.8 | 15.8 | 15.9 | 16 | 18.1
23 | -184 | 15.8 | 15.8 | 15.9 | 16 | 18.1
24 | -183 | 15.8 | 15.8 | 15.9 | 16 | 18.1
25 | -182 | 15.8 | 15.8 | 15.9 | 16 | 18.1
26 | -181 | 15.8 | 15.8 | 15.9 | 16 | 18.1
27 | -180 | 15.8 | 15.8 | 15.9 | 16 | 18.1
28 | -179 | 15.8 | 15.8 | 15.9 | 16 | 18.1
29 | -178 | 15.8 | 15.8 | 15.9 | 16 | 18.1
30 | -177 | 15.8 | 15.8 | 15.9 | 16 | 18.1
31 | -176 | 15.8 | 15.8 | 15.9 | 16 | 18.1
32 | -175 | 15.8 | 15.7 | 15.9 | 16 | 18.1
33 | -174 | 15.8 | 15.8 | 15.9 | 16 | 18.1
34 | -173 | 15.8 | 15.8 | 15.9 | 16 | 18.1
35 | -172 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1
36 | -171 | 15.8 | 15.8 | 15.9 | 16 | 18.1
37 | -170 | 15.8 | 15.8 | 15.9 | 16 | 18.1
38 | -169 | 15.8 | 15.8 | 15.9 | 16 | 18.1
39 | -168 | 15.8 | 15.8 | 15.9 | 16 | 18.1
40 | -167 | 15.8 | 15.8 | 15.9 | 16 | 18.1
41 | -166 | 15.8 | 15.8 | 15.9 | 16 | 18.1
42 | -165 | 15.8 | 15.8 | 15.9 | 16 | 18.1
43 | -164 | 15.8 | 15.8 | 15.9 | 16 | 18.1
44 | -163 | 15.8 | 15.8 | 15.9 | 16 | 18.1
45 | -162 | 15.8 | 15.8 | 15.9 | 16 | 18.1
46 | -161 | 15.8 | 15.8 | 15.9 | 16 | 18.1
47 | -160 | 15.8 | 15.8 | 15.9 | 16 | 18.1
48 | -159 | 15.8 | 15.8 | 15.9 | 16 | 18.1
49 | -158 | 15.8 | 15.8 | 15.9 | 16 | 18.1
50 | -157 | 15.8 | 15.8 | 15.9 | 16 | 18.1
51 | -156 | 15.8 | 15.8 | 15.9 | 16 | 18.1
52 | -155 | 15.8 | 15.8 | 15.9 | 16 | 18.1
53 | -154 | 15.8 | 15.8 | 15.9 | 16 | 18.1
54 | -153 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1
55 | -152 | 15.8 | 15.8 | 15.9 | 16 | 18.1
56 | -151 | 15.8 | 15.8 | 15.9 | 16 | 18.1
57 | -150 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1
58 | -149 | 15.8 | 15.8 | 15.9 | 16 | 18.1
59 | -148 | 15.8 | 15.8 | 15.9 | 16 | 18.1
60 | -147 | 15.8 | 15.8 | 15.9 | 16 | 18.1
61 | -146 | 15.8 | 15.8 | 15.9 | 16 | 18.1
62 | -145 | 15.8 | 15.8 | 15.9 | 16 | 18.1
63 | -144 | 15.8 | 15.8 | 15.9 | 16 | 18.1
64 | -143 | 15.8 | 15.8 | 15.9 | 16 | 18.1
65 | -142 | 15.8 | 15.8 | 15.9 | 16 | 18.1
66 | -141 | 15.8 | 15.8 | 15.9 | 16 | 18.1
67 | -140 | 15.8 | 15.8 | 15.9 | 16 | 18.1
68 | -139 | 15.8 | 15.8 | 15.9 | 16 | 18.1
69 | -138 | 15.8 | 15.8 | 15.9 | 16 | 18.1
70 | -137 | 15.8 | 15.8 | 15.9 | 16 | 18.1
71 | -136 | 15.8 | 15.8 | 15.9 | 16 | 18.1
72 | -135 | 15.8 | 15.8 | 15.9 | 16 | 18.1
73 | -134 | 15.8 | 15.8 | 15.9 | 16 | 18.1
74 | -133 | 15.8 | 15.8 | 15.9 | 16 | 18.1
75 | -132 | 15.8 | 15.8 | 15.9 | 16 | 18.1
76 | -131 | 15.8 | 15.8 | 15.9 | 16 | 18.1
77 | -130 | 15.8 | 15.8 | 15.9 | 16 | 18.1
78 | -129 | 15.8 | 15.8 | 15.9 | 16 | 18.1
79 | -128 | 15.8 | 15.8 | 15.9 | 16 | 18.1
80 | -127 | 15.8 | 15.8 | 15.9 | 16 | 18.1
81 | -126 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1
82 | -125 | 15.8 | 15.8 | 15.9 | 16 | 18.1
83 | -124 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1
84 | -123 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1
85 | -122 | 15.8 | 15.8 | 15.9 | 16 | 18.1
86 | -121 | 15.8 | 15.8 | 15.9 | 16 | 18.1
87 | -120 | 15.8 | 15.8 | 15.9 | 16 | 18.1
88 | -119 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1
89 | -118 | 15.8 | 15.8 | 15.9 | 16 | 18.1
90 | -117 | 15.8 | 15.8 | 15.9 | 16 | 18.1
91 | -116 | 15.8 | 15.8 | 15.9 | 16 | 18.1
92 | -115 | 15.8 | 15.8 | 15.9 | 16 | 18.1
93 | -114 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1
94 | -113 | 15.8 | 15.8 | 15.9 | 16 | 18.1
95 | -112 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1
96 | -111 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1
97 | -110 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1
98 | -109 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1
99 | -108 | 15.8 | 15.8 | 15.9 | 16 | 18.1
100 | -107 | 15.8 | 15.8 | 15.9 | 16 | 18.1
101 | -106 | 15.8 | 15.8 | 15.9 | 16 | 18.1
102 | -105 | 15.8 | 15.8 | 15.9 | 16 | 18.1
103 | -104 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1
104 | -103 | 15.8 | 15.8 | 15.9 | 16 | 18.1
105 | -102 | 15.8 | 15.8 | 15.9 | 16 | 18.1
106 | -101 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1
107 | -100 | 15.8 | 15.8 | 15.9 | 16 | 18.1
108 | -99 | 15.8 | 15.8 | 15.9 | 16 | 18.1
109 | -98 | 15.8 | 15.8 | 15.9 | 16 | 18.1
110 | -97 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1
111 | -96 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1
112 | -95 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1
113 | -94 | 15.8 | 15.8 | 15.9 | 16 | 18.1
114 | -93 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1
115 | -92 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1
116 | -91 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1
117 | -90 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1
118 | -89 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1
119 | -88 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1
120 | -87 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1
121 | -86 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1
122 | -85 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1
123 | -84 | 15.8 | 15.8 | 15.9 | 16 | 18.1
124 | -83 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1
125 | -82 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1
126 | -81 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1
127 | -80 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1
128 | -79 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1
129 | -78 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1
130 | -77 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1
131 | -76 | 15.8 | 15.8 | 15.9 | 16 | 18.1
132 | -75 | 15.8 | 15.8 | 15.9 | 16 | 18.1
133 | -74 | 15.8 | 15.8 | 15.9 | 16 | 18.1
134 | -73 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1
135 | -72 | 15.8 | 15.8 | 15.9 | 16 | 18.1
136 | -71 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1
137 | -70 | 15.8 | 15.8 | 15.9 | 16 | 18.1
138 | -69 | 15.8 | 15.8 | 15.9 | 16 | 18.1
139 | -68 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1
140 | -67 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1
141 | -66 | 15.8 | 15.8 | 15.9 | 16 | 18.1
142 | -65 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1
143 | -64 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1
144 | -63 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1
145 | -62 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1
146 | -61 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1
147 | -60 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1
148 | -59 | 15.8 | 15.8 | 15.9 | 16 | 18.1
149 | -58 | 15.8 | 15.8 | 15.9 | 16 | 18.1
150 | -57 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1
151 | -56 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1
152 | -55 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1
153 | -54 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1
154 | -53 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1
155 | -52 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1
156 | -51 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1
157 | -50 | 15.8 | 15.8 | 15.9 | 16 | 18.1
158 | -49 | 15.8 | 15.8 | 15.9 | 16 | 18.1
159 | -48 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1
160 | -47 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1
161 | -46 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1
162 | -45 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1
163 | -44 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1
164 | -43 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1
165 | -42 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1
166 | -41 | 15.8 | 15.8 | 15.9 | 16 | 18.1
167 | -40 | 15.8 | 15.8 | 15.9 | 16 | 18.1
168 | -39 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1
169 | -38 | 15.8 | 15.7 | 15.9 | 16.1 | 18.1
170 | -37 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1
171 | -36 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1
172 | -35 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1
173 | -34 | 15.8 | 15.7 | 15.9 | 16.1 | 18.1
174 | -33 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1
175 | -32 | 15.8 | 15.8 | 15.8 | 16.1 | 18.1
176 | -31 | 15.8 | 15.8 | 15.8 | 16.1 | 18.1
177 | -30 | 15.8 | 15.7 | 15.8 | 16 | 18.1
178 | -29 | 15.8 | 15.7 | 15.8 | 16.1 | 18.1
179 | -28 | 15.8 | 15.7 | 15.8 | 16 | 18.1
180 | -27 | 15.8 | 15.7 | 15.8 | 16.1 | 18.1
181 | -26 | 15.8 | 15.7 | 15.8 | 16 | 18.1
182 | -25 | 15.8 | 15.7 | 15.8 | 16.1 | 18.1
183 | -24 | 15.8 | 15.8 | 15.8 | 16.1 | 18.1
184 | -23 | 15.8 | 15.7 | 15.8 | 16.1 | 18.1
185 | -22 | 15.8 | 15.7 | 15.8 | 16 | 18.1
186 | -21 | 15.8 | 15.7 | 15.8 | 16.1 | 18.1
187 | -20 | 15.8 | 15.8 | 15.8 | 16.1 | 18.1
188 | -19 | 15.8 | 15.7 | 15.8 | 16.1 | 18.1
189 | -18 | 15.8 | 15.7 | 15.8 | 16.1 | 18.1
190 | -17 | 15.8 | 15.8 | 15.8 | 16.1 | 18.1
191 | -16 | 15.8 | 15.7 | 15.8 | 16 | 18.1
192 | -15 | 15.8 | 15.7 | 15.8 | 16 | 18.1
193 | -14 | 15.8 | 15.7 | 15.9 | 16.1 | 18.1
194 | -13 | 15.8 | 15.7 | 15.9 | 16.1 | 18.1
195 | -12 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1
196 | -11 | 15.8 | 15.8 | 15.9 | 16 | 18.1
197 | -10 | 15.8 | 15.8 | 16 | 16.1 | 18.1
198 | -9 | 15.8 | 15.8 | 16.1 | 16 | 18.1
199 | -8 | 15.8 | 15.8 | 16.1 | 16.1 | 18.1
200 | -7 | 15.8 | 15.8 | 16.1 | 16.1 | 18.1
201 | -6 | 15.8 | 15.8 | 16.1 | 16.1 | 18.1
202 | -5 | 15.8 | 15.8 | 16.1 | 16.1 | 18.1
203 | -4 | 15.8 | 15.8 | 16.1 | 16.1 | 18.1
204 | -3 | 15.8 | 15.8 | 16.1 | 16.1 | 18.2
205 | -2 | 15.8 | 15.9 | 16.1 | 16 | 18.2
206 | -1 | 15.8 | 15.9 | 16.1 | 16 | 18.2
207 | 0 | 15.8 | 15.9 | 16.1 | 16.1 | 18.2
208 | 1 | 15.8 | 15.9 | 16.1 | 16.1 | 18.2
209 | 2 | 15.8 | 16 | 16.1 | 16.1 | 18.3
210 | 3 | 15.8 | 16.1 | 16.5 | 16.1 | 18.4
211 | 4 | 15.8 | 19.6 | 30.1 | 16.1 | 22
212 | 5 | 15.8 | 39.9 | 97.1 | 16.3 | 33.4
213 | 6 | 15.8 | 80.6 | 177.3 | 16.6 | 61
214 | 7 | 15.8 | 133.9 | 268.9 | 17.3 | 87.9
215 | 8 | 15.8 | 198.1 | 337.7 | 18.3 | 119.4
216 | 9 | 15.8 | 278.4 | 405.5 | 19.6 | 149.2
217 | 10 | 15.9 | 345.1 | 458.9 | 20.9 | 178
218 | 11 | 15.9 | 412 | 509.7 | 22.3 | 211.5
219 | 12 | 16 | 467.6 | 551.8 | 24 | 239.3
220 | 13 | 16.1 | 528.6 | 592 | 25.8 | 269
221 | 14 | 16.2 | 582.2 | 633.8 | 28.2 | 303.6
222 | 15 | 16.3 | 628.3 | 671.7 | 31.1 | 335.2
223 | 16 | 16.5 | 664.5 | 702.6 | 33.3 | 366.1
224 | 17 | 16.7 | 698.1 | 730.9 | 36.9 | 389.5
225 | 18 | 16.9 | 731.1 | 749.7 | 39.7 | 410.6
226 | 19 | 17.2 | 757.3 | 763.5 | 41.7 | 428.7
227 | 20 | 17.5 | 775.6 | 775.3 | 44 | 444.3
228 | 21 | 17.9 | 792.3 | 790.4 | 46.5 | 462.9
229 | 22 | 18.2 | 805.9 | 794.7 | 48.8 | 475.7
230 | 23 | 18.7 | 826.4 | 795.5 | 49.3 | 486.7
231 | 24 | 19.1 | 839 | 792.4 | 50.4 | 497.6
232 | 25 | 19.6 | 849.4 | 782.1 | 52.4 | 509.6
233 | 26 | 20.1 | 857.3 | 771.8 | 54.2 | 518
234 | 27 | 20.6 | 866 | 769.7 | 56.3 | 526.7
235 | 28 | 21.2 | 876.5 | 765.4 | 59.3 | 539.2
236 | 29 | 21.8 | 885.2 | 757.7 | 61.7 | 553.1
237 | 30 | 22.4 | 890.4 | 778.4 | 64.3 | 560.6
238 | 31 | 23 | 893.8 | 794 | 66.2 | 564
239 | 32 | 23.7 | 897.2 | 797.1 | 68.6 | 570.9
240 | 33 | 24.4 | 897.7 | 796.6 | 70.4 | 576.7
241 | 34 | 25.1 | 898.2 | 795.8 | 72.4 | 577.7
242 | 35 | 25.9 | 899.7 | 799 | 73.9 | 578.8
243 | 36 | 26.6 | 904 | 807.2 | 76.9 | 580.5
244 | 37 | 27.5 | 910 | 804.8 | 79.7 | 589.1
245 | 38 | 28.3 | 913.8 | 812 | 83.1 | 594.3
246 | 39 | 29.1 | 911.8 | 827.9 | 87.1 | 601.2
247 | 40 | 30 | 912.1 | 827.7 | 90.7 | 604.4
248 | 41 | 30.9 | 910 | 837.2 | 94.2 | 605.2
249 | 42 | 31.8 | 908.9 | 836.7 | 97.3 | 605.5
250 | 43 | 32.8 | 910.5 | 837 | 99.7 | 608.4
251 | 44 | 33.8 | 913.7 | 830.5 | 101.7 | 613
252 | 45 | 34.7 | 914.6 | 826.4 | 103.1 | 617.4
253 | 46 | 35.7 | 910.2 | 836.9 | 105 | 617.4
254 | 47 | 36.7 | 901.8 | 830.7 | 105.5 | 616
255 | 48 | 37.7 | 901.3 | 826.5 | 106.7 | 612.5
256 | 49 | 38.7 | 907.1 | 822.7 | 108.5 | 615.2
257 | 50 | 39.6 | 915.9 | 825.8 | 109.3 | 620.9
258 | 51 | 40.6 | 918.1 | 818.8 | 110.4 | 626
259 | 52 | 41.6 | 914.4 | 812.3 | 110.7 | 621.6
260 | 53 | 42.6 | 912.5 | 813.9 | 112.7 | 619.2
261 | 54 | 43.7 | 918.3 | 823.8 | 115.4 | 626.2
262 | 55 | 44.8 | 916.7 | 820.5 | 120 | 635.7
263 | 56 | 45.9 | 919.1 | 824.3 | 124.7 | 644.2
264 | 57 | 47 | 919.5 | 827.8 | 130.4 | 650.4
265 | 58 | 48.2 | 913.4 | 827.3 | 137.5 | 654.9
266 | 59 | 49.3 | 914.8 | 829.3 | 143.2 | 656.2
267 | 60 | 50.5 | 917.8 | 812.6 | 148.1 | 663.9
268 | 61 | 51.9 | 913.4 | 806 | 152.9 | 667.9
269 | 62 | 53.4 | 915.2 | 794.6 | 156.9 | 669.8
270 | 63 | 54.9 | 917.8 | 779.6 | 162.8 | 673
271 | 64 | 56.3 | 920.7 | 784.6 | 171.7 | 684
272 | 65 | 57.9 | 919.4 | 797.7 | 178.8 | 691.6
273 | 66 | 59.3 | 916.2 | 809.9 | 187.9 | 701.6
274 | 67 | 60.9 | 922.2 | 820.2 | 193.1 | 703.2
275 | 68 | 62.6 | 925.3 | 818 | 196.4 | 704.9
276 | 69 | 64.7 | 916 | 802.7 | 199.2 | 699
277 | 70 | 67 | 907.2 | 784.2 | 203 | 695.8
278 | 71 | 68.8 | 899.4 | 770.1 | 206.2 | 698.9
279 | 72 | 70.6 | 906.2 | 778.7 | 211.6 | 707.9
280 | 73 | 72.5 | 916.2 | 791 | 217.9 | 714.5
281 | 74 | 74.6 | 920.3 | 807.8 | 223.2 | 717.4
282 | 75 | 76.2 | 925.5 | 813.3 | 226 | 722.3
283 | 76 | 77.8 | 927 | 818.6 | 226.8 | 719.8
284 | 77 | 79.5 | 922.9 | 824.2 | 232.4 | 719.9
285 | 78 | 81.2 | 922.7 | 824.1 | 239.7 | 721
286 | 79 | 82.9 | 920.9 | 824.5 | 245.3 | 717
287 | 80 | 84.7 | 912.9 | 827.2 | 249.6 | 710.8
288 | 81 | 86.5 | 909.5 | 841.5 | 256 | 711
289 | 82 | 88.4 | 910.3 | 850.5 | 262.3 | 712.2
290 | 83 | 90.3 | 912.2 | 849.1 | 267.8 | 711.2
291 | 84 | 92.3 | 911 | 848 | 272.2 | 709.2
292 | 85 | 94.4 | 907.3 | 837.8 | 275.5 | 711
293 | 86 | 96.6 | 910.6 | 830.5 | 280.5 | 715.4
294 | 87 | 99 | 904.8 | 824 | 286.2 | 724.5
295 | 88 | 101.3 | 904 | 824.9 | 292.5 | 729.4
296 | 89 | 103.7 | 903.8 | 819.8 | 294.5 | 738.2
297 | 90 | 106.1 | 902.5 | 816.6 | 297 | 738.3
298 | 91 | 108.5 | 899.6 | 808.8 | 299.3 | 735.3
299 | 92 | 111 | 891.8 | 797.6 | 299.4 | 734.4
300 | 93 | 113.6 | 896.2 | 810.2 | 299.7 | 738.2
301 | 94 | 116.2 | 893.5 | 826.5 | 299.4 | 733.2
302 | 95 | 118.8 | 885.5 | 822 | 299.4 | 723.8
303 | 96 | 121.5 | 881.3 | 828.1 | 297.8 | 722.4
304 | 97 | 124.1 | 888.6 | 825.9 | 297.2 | 727.4
305 | 98 | 126.7 | 891.6 | 831.5 | 296.6 | 735.8
306 | 99 | 129.2 | 892.9 | 835.6 | 295 | 738.9
307 | 100 | 131.7 | 893.4 | 830.6 | 292.8 | 731.8
308 | 101 | 134.2 | 885.2 | 816.4 | 291.5 | 728.4
309 | 102 | 136.7 | 882.1 | 825.9 | 290.8 | 728.7
310 | 103 | 139.1 | 883.2 | 825.2 | 290.3 | 728.9
311 | 104 | 141.5 | 880.6 | 825.2 | 289.7 | 729.7
312 | 105 | 143.9 | 875.3 | 830.3 | 289.6 | 723.4
313 | 106 | 146.3 | 876 | 806.1 | 290 | 725.7
314 | 107 | 148.7 | 879.6 | 804.1 | 289.2 | 730.6
315 | 108 | 150.9 | 880.6 | 807.6 | 286.6 | 740.1
316 | 109 | 153.2 | 880.1 | 823.1 | 284.8 | 739
317 | 110 | 155.4 | 874.2 | 828.5 | 285 | 732.6
318 | 111 | 157.5 | 860.1 | 822.9 | 283.7 | 725.3
319 | 112 | 159.6 | 854.1 | 819.2 | 283.4 | 730.2
320 | 113 | 161.6 | 851.4 | 808.8 | 283.5 | 736.4
321 | 114 | 163.6 | 850.7 | 797.3 | 283.5 | 739.4
322 | 115 | 165.6 | 851.5 | 797.7 | 283.3 | 742.3
323 | 116 | 167.5 | 850.4 | 815.2 | 281.2 | 747.2
324 | 117 | 169.3 | 855.5 | 832 | 278.6 | 748.4
325 | 118 | 171.1 | 856 | 828.6 | 275.8 | 743.1
326 | 119 | 172.9 | 853 | 816.7 | 273.4 | 743.5
327 | 120 | 174.7 | 851 | 819.4 | 270.9 | 742.6
328 | 121 | 176.4 | 842.6 | 823.4 | 268.3 | 739.4
329 | 122 | 178 | 829.4 | 824.9 | 265.4 | 731.7
330 | 123 | 179.6 | 816.6 | 817.1 | 262.6 | 724
331 | 124 | 181.2 | 797.8 | 814.2 | 259.9 | 716.6
332 | 125 | 182.7 | 776.9 | 800.9 | 257.5 | 714.1
333 | 126 | 184.2 | 775.1 | 810.7 | 255.4 | 720
334 | 127 | 185.7 | 778.9 | 822.6 | 253.1 | 726.9
335 | 128 | 187.1 | 781.4 | 823.7 | 250.4 | 727.8
336 | 129 | 188.4 | 782.3 | 812.5 | 247.7 | 713.6
337 | 130 | 189.7 | 774.8 | 803.7 | 245.1 | 704.9
338 | 131 | 190.9 | 763.5 | 792.5 | 242.6 | 700.2
339 | 132 | 192.1 | 765.4 | 805.5 | 240.3 | 699.5
340 | 133 | 193.2 | 760.9 | 807.6 | 238.2 | 703
341 | 134 | 194.2 | 749.8 | 795.1 | 236.2 | 702.7
342 | 135 | 195 | 724.2 | 792.9 | 234.2 | 698.9
343 | 136 | 195.8 | 715.3 | 805.7 | 232.2 | 698.9
344 | 137 | 196.5 | 704.6 | 799.5 | 230.3 | 695.7
345 | 138 | 197.1 | 685.2 | 777.7 | 228.3 | 688.9
346 | 139 | 197.6 | 668.1 | 757.2 | 226.1 | 680
347 | 140 | 197.8 | 655.5 | 754.3 | 223.9 | 669.5
348 | 141 | 198 | 650.2 | 766.7 | 221.7 | 664.7
349 | 142 | 198.1 | 660.5 | 770.2 | 219.7 | 672.2
350 | 143 | 198 | 657.4 | 764.2 | 218.1 | 672.4
351 | 144 | 197.8 | 667.5 | 775.8 | 216.7 | 680
352 | 145 | 197.7 | 683.9 | 785.8 | 215.6 | 686.5
353 | 146 | 197.5 | 698.8 | 796.4 | 214.8 | 692.5
354 | 147 | 197.4 | 712.1 | 808.9 | 214.1 | 702
355 | 148 | 197.3 | 728 | 800.2 | 213.6 | 705.7
356 | 149 | 197.2 | 740.4 | 803.8 | 213.2 | 707.3
357 | 150 | 197.2 | 752.8 | 816.9 | 212.7 | 713.4
358 | 151 | 197.2 | 767.8 | 820.8 | 212.1 | 710.6
359 | 152 | 197.4 | 785.5 | 826 | 211.6 | 710.4
360 | 153 | 197.6 | 796.1 | 837.2 | 211.2 | 712.5
361 | 154 | 197.8 | 796.3 | 847.8 | 210.9 | 718.2
362 | 155 | 198.1 | 799.1 | 853 | 210.9 | 723.3
363 | 156 | 198.5 | 807.8 | 857.4 | 210.9 | 727.2
364 | 157 | 198.9 | 810.1 | 866 | 210.8 | 725.1
365 | 158 | 199.4 | 802.5 | 862.3 | 210.6 | 721.6
366 | 159 | 199.9 | 805.6 | 848.6 | 210.2 | 716.9
367 | 160 | 200.5 | 810.2 | 840.9 | 209.9 | 708.2
368 | 161 | 201.2 | 808.3 | 822.9 | 209.6 | 700.3
369 | 162 | 201.8 | 802.5 | 822 | 209.4 | 699.6
370 | 163 | 202.5 | 804.7 | 824 | 209.4 | 704.3
371 | 164 | 203.2 | 796.6 | 813.6 | 209.4 | 697.1
372 | 165 | 204 | 795 | 818.5 | 209.3 | 694.3
373 | 166 | 204.7 | 789.9 | 804.2 | 209.3 | 687.8
374 | 167 | 205.5 | 794.2 | 787.6 | 209.2 | 686.6
375 | 168 | 206.4 | 797.9 | 798.2 | 209.2 | 687
376 | 169 | 207.1 | 796.3 | 793.5 | 209.2 | 691.4
377 | 170 | 208 | 796 | 796 | 209.1 | 692.3
378 | 171 | 208.8 | 793.3 | 793.9 | 209.1 | 694.3
379 | 172 | 209.7 | 793.2 | 803.7 | 209 | 699.1
380 | 173 | 210.6 | 793.7 | 801.4 | 209 | 701.2
381 | 174 | 211.4 | 797.1 | 802.6 | 209 | 707.1
382 | 175 | 212.2 | 798.3 | 807 | 209.2 | 715.2
383 | 176 | 213 | 800 | 804.5 | 209.5 | 720.8
384 | 177 | 214 | 805.8 | 811.6 | 209.8 | 728.9
385 | 178 | 214.8 | 814.3 | 823.7 | 210.1 | 736
386 | 179 | 215.7 | 817.2 | 833.8 | 210.4 | 738.9
387 | 180 | 216.6 | 818.3 | 807.3 | 210.7 | 738.9
388 | 181 | 217.6 | 821 | 808.5 | 211.1 | 737.1
389 | 182 | 218.5 | 822.8 | 818.3 | 211.4 | 735.4
390 | 183 | 219.4 | 824.1 | 820.2 | 211.7 | 732.4
391 | 184 | 220.4 | 823.4 | 832.1 | 212 | 728.6
392 | 185 | 221.3 | 819.4 | 832.5 | 212.2 | 733.5
393 | 186 | 222.2 | 820.4 | 827 | 212.5 | 737.6
394 | 187 | 223.1 | 821.3 | 835.7 | 213 | 741.5
395 | 188 | 224.1 | 820.7 | 831.3 | 213.4 | 736
396 | 189 | 225 | 820.5 | 846.4 | 213.8 | 739.2
397 | 190 | 226 | 818.5 | 847.9 | 214.1 | 739.4
398 | 191 | 226.9 | 820.6 | 853.3 | 214.4 | 741.5
399 | 192 | 227.8 | 820.9 | 836.4 | 214.6 | 737.2
400 | 193 | 228.8 | 818.2 | 811 | 214.8 | 727.6
401 | 194 | 229.8 | 814.7 | 827.5 | 215 | 725.3
402 | 195 | 230.8 | 811.1 | 829.3 | 215.2 | 724.1
403 | 196 | 231.9 | 813 | 825.5 | 215.3 | 722.5
404 | 197 | 233 | 815.3 | 822.4 | 215.6 | 726.1
405 | 198 | 234.1 | 818.7 | 812.5 | 215.9 | 726.7
406 | 199 | 235.2 | 818.7 | 814.8 | 216.2 | 721.6
407 | 200 | 236.3 | 815.3 | 811.7 | 216.5 | 721.3
408 | 201 | 237.4 | 810.9 | 830.8 | 216.9 | 728.1
409 | 202 | 238.5 | 805.8 | 823.7 | 217.2 | 727.4
410 | 203 | 239.5 | 796.3 | 813.3 | 217.5 | 719.9
411 | 204 | 240.5 | 790.5 | 795.3 | 217.6 | 711.5
412 | 205 | 241.5 | 792.6 | 783.8 | 217.8 | 705.1
413 | 206 | 242.4 | 792.2 | 791.8 | 217.9 | 704.3
414 | 207 | 243.4 | 796 | 810.4 | 218.2 | 705.9
415 | 208 | 244.3 | 795.7 | 821.8 | 218.6 | 708.4
416 | 209 | 245.2 | 798.2 | 823.8 | 218.9 | 710.7
417 | 210 | 246 | 797.4 | 831.6 | 219.4 | 714.5
418 | 211 | 246.9 | 801.7 | 834.1 | 220.1 | 716.3
419 | 212 | 247.7 | 803.6 | 825.2 | 220.8 | 714.1
420 | 213 | 248.5 | 805.3 | 807.8 | 221.5 | 705.3
421 | 214 | 249.3 | 804.3 | 793.8 | 222.2 | 699.9
422 | 215 | 250.1 | 807.3 | 804 | 222.9 | 698.4
423 | 216 | 250.8 | 806.4 | 808.6 | 223.7 | 703.4
424 | 217 | 251.4 | 803.9 | 789.9 | 224.4 | 704.2
425 | 218 | 252.1 | 805.1 | 775.5 | 225.2 | 699.3
426 | 219 | 252.6 | 804 | 794.1 | 225.8 | 701.1
427 | 220 | 253.2 | 801.1 | 802.8 | 226.4 | 706.2
428 | 221 | 253.8 | 801.6 | 813.9 | 227.1 | 706.7
429 | 222 | 254.6 | 801.9 | 824.7 | 227.7 | 710.2
430 | 223 | 255.4 | 797.8 | 822.2 | 228.4 | 715
431 | 224 | 256.4 | 795.5 | 822.8 | 229.1 | 711.4
432 | 225 | 257.5 | 791.5 | 833.7 | 229.7 | 712.1
433 | 226 | 258.6 | 794.2 | 845.2 | 230.4 | 717.5
434 | 227 | 259.7 | 793.9 | 843.7 | 231.1 | 718.8
435 | 228 | 260.9 | 795.9 | 840.3 | 231.8 | 716.2
436 | 229 | 262.2 | 798.8 | 839.9 | 232.5 | 717.6
437 | 230 | 263.6 | 794.7 | 844.5 | 233.3 | 722.2
438 | 231 | 265 | 790.4 | 842.8 | 234.1 | 726.4
439 | 232 | 266.3 | 785.1 | 841.4 | 234.8 | 732.3
440 | 233 | 267.6 | 783.3 | 834.2 | 235.5 | 734.5
441 | 234 | 268.9 | 784.8 | 828.6 | 236.1 | 736.3
442 | 235 | 270.1 | 782.2 | 831.6 | 236.7 | 741.9
443 | 236 | 271.4 | 780 | 841.9 | 237.4 | 745
444 | 237 | 272.9 | 781 | 853.4 | 238.1 | 741.8
445 | 238 | 274.2 | 779.7 | 851.9 | 238.9 | 739.5
446 | 239 | 275.6 | 779.9 | 850.1 | 239.7 | 737.9
447 | 240 | 276.9 | 779.6 | 846.1 | 240.5 | 737.3
448 | 241 | 278.3 | 775.6 | 856.3 | 241.3 | 745.5
449 | 242 | 279.7 | 773.2 | 862.3 | 242.2 | 753.7
450 | 243 | 281.2 | 774.1 | 865.4 | 243.1 | 759.8
451 | 244 | 282.7 | 774.8 | 855.7 | 243.9 | 762.7
452 | 245 | 284.2 | 774.1 | 850.9 | 244.8 | 770.3
453 | 246 | 285.9 | 771.2 | 862.7 | 245.7 | 775.1
454 | 247 | 287.5 | 769.3 | 864.2 | 246.7 | 778.3
455 | 248 | 289 | 766.4 | 863.2 | 247.6 | 782.9
456 | 249 | 290.5 | 765.6 | 862.8 | 248.6 | 785.9
457 | 250 | 292 | 766 | 873.7 | 249.7 | 787.6
458 | 251 | 293.5 | 768.3 | 875.9 | 250.8 | 784.6
459 | 252 | 295 | 770.8 | 869.3 | 251.9 | 783
460 | 253 | 296.6 | 771.9 | 859.1 | 252.9 | 783.4
461 | 254 | 298.1 | 772.6 | 855.9 | 254.1 | 779
462 | 255 | 299.8 | 769.9 | 856 | 255.2 | 782.6
463 | 256 | 301.5 | 771.5 | 855.8 | 256.3 | 786.9
464 | 257 | 303.3 | 772.3 | 862.7 | 257.5 | 789.1
465 | 258 | 305.1 | 773.4 | 863.9 | 258.8 | 786.7
466 | 259 | 307 | 773.5 | 860.4 | 260.2 | 786.1
467 | 260 | 308.9 | 775.1 | 864.3 | 261.5 | 785.8
468 | 261 | 311.1 | 773.4 | 864.3 | 263 | 784.8
469 | 262 | 313.3 | 771.2 | 855 | 264.6 | 782.1
470 | 263 | 315.7 | 770.7 | 853.1 | 266 | 785.1
471 | 264 | 318.1 | 770.2 | 857.8 | 267.5 | 788
472 | 265 | 320.5 | 769.2 | 843.6 | 269 | 779.6
473 | 266 | 323.2 | 766.1 | 833 | 270.5 | 769.9
474 | 267 | 325.8 | 762.7 | 827.4 | 271.9 | 765.1
475 | 268 | 328.3 | 762.5 | 830.5 | 273.5 | 761.5
476 | 269 | 330.7 | 761 | 831.2 | 274.9 | 762.9
477 | 270 | 333.1 | 759.5 | 833.3 | 276.4 | 763.2
478 | 271 | 335.4 | 759 | 822.5 | 277.7 | 767.2
479 | 272 | 337.7 | 755.5 | 816.1 | 279.1 | 777
480 | 273 | 339.7 | 751.2 | 806 | 280.6 | 783.2
481 | 274 | 341.5 | 749 | 807.1 | 281.9 | 787.7
482 | 275 | 343 | 747.1 | 824.3 | 283.4 | 787.9
483 | 276 | 344.4 | 745.7 | 832.2 | 285 | 787.5
484 | 277 | 345.6 | 746 | 835.3 | 286.4 | 781.3
485 | 278 | 346.8 | 746.7 | 839.2 | 287.8 | 777.7
486 | 279 | 348.1 | 746.6 | 842 | 289.2 | 774.2
487 | 280 | 349.5 | 746.3 | 827.7 | 290.7 | 769.1
488 | 281 | 350.7 | 747.3 | 816.1 | 292.2 | 765
489 | 282 | 351.7 | 747.4 | 812.4 | 293.6 | 762.2
490 | 283 | 352.3 | 747.9 | 813.9 | 295 | 762.5
491 | 284 | 352.7 | 746.5 | 822.5 | 296.4 | 762.4
492 | 285 | 352.9 | 745.1 | 825.6 | 298 | 763.4
493 | 286 | 353 | 745.7 | 834.6 | 299.7 | 766.3
494 | 287 | 352.9 | 744.9 | 836.2 | 301.3 | 769.9
495 | 288 | 352.8 | 745.9 | 835.9 | 303.3 | 773
496 | 289 | 352.6 | 746.6 | 832.9 | 305.2 | 772.7
497 | 290 | 352.4 | 748.8 | 835.3 | 307.2 | 772.2
498 | 291 | 351.8 | 748.6 | 838.7 | 309.3 | 777.1
499 | 292 | 351 | 747.3 | 836.1 | 311.2 | 777.8
500 | 293 | 350.2 | 746.7 | 838.3 | 313.3 | 778.5
501 | 294 | 349.7 | 747.6 | 831.5 | 315.2 | 783.7
502 | 295 | 349.4 | 749.3 | 812 | 317.3 | 791.9
503 | 296 | 349.3 | 749.8 | 804.1 | 319.5 | 794.5
504 | 297 | 349.5 | 748.9 | 809.4 | 321.5 | 798.6
505 | 298 | 349.9 | 748.3 | 810.7 | 323.8 | 803.5
506 | 299 | 353.6 | 747.8 | 806.2 | 325.4 | 806.1
507 | 300 | 356.4 | 747.3 | 800.7 | 327.6 | 807.8
508 | 301 | 357.9 | 746.2 | 791.4 | 329.3 | 809.7
509 | 302 | 359.2 | 746.2 | 792.3 | 331.4 | 813.8
510 | 303 | 360.6 | 747.3 | 797.8 | 332.9 | 815.7
511 | 304 | 362.3 | 749.5 | 813.4 | 334.8 | 814.9
512 | 305 | 364.3 | 749.6 | 821.8 | 337 | 813.8
513 | 306 | 367 | 749.6 | 827.8 | 339.2 | 813.3
514 | 307 | 369.5 | 749.9 | 827.2 | 341 | 817
515 | 308 | 372.3 | 751.5 | 829.3 | 343.5 | 820.6
516 | 309 | 376.1 | 750.6 | 837.1 | 345.6 | 822.4
517 | 310 | 381.2 | 752 | 838.4 | 348 | 819.5
518 | 311 | 386.3 | 754.3 | 836.7 | 351.1 | 814.6
519 | 312 | 390.1 | 268.8 | 841 | 357.8 | 815.6
520 | 313 | 392.8 | 65.2 | 838.2 | 358.2 | 815.2
521 | 314 | 396.6 | 74.8 | 841.5 | 360.1 | 816.7
522 | 315 | 401.1 | 86.7 | 842.7 | 363.3 | 820.4
523 | 316 | 405.1 | 498.5 | 841.7 | 366.8 | 822.2
524 | 317 | 410 | 764.8 | 839.5 | 370.2 | 821.7
525 | 318 | 414.6 | 767.7 | 833.7 | 374.1 | 823.7
526 | 319 | 419 | 767.8 | 831.8 | 378.2 | 826.4
527 | 320 | 424.1 | 768.2 | 834.7 | 382.1 | 827.1
528 | 321 | 428.9 | 768.4 | 837.7 | 386.4 | 825.5
529 | 322 | 433.4 | 767.8 | 831.1 | 390.4 | 827.7
530 | 323 | 437.5 | 767.9 | 826 | 394.6 | 831.2
531 | 324 | 441.9 | 766.8 | 822.5 | 398.4 | 833.6
532 | 325 | 446.4 | 765.8 | 820.2 | 402.5 | 835
533 | 326 | 450.1 | 766.6 | 803.4 | 406.3 | 836
534 | 327 | 454.5 | 768 | 798.2 | 410.7 | 835.8
535 | 328 | 459.3 | 767.5 | 806.7 | 414.4 | 839.7
536 | 329 | 464.2 | 768.1 | 811.1 | 419.1 | 840.1
537 | 330 | 468.8 | 769 | 809.4 | 423.5 | 840.5
538 | 331 | 473.3 | 769.4 | 805.7 | 428 | 841.8
539 | 332 | 477.9 | 767.9 | 807.7 | 432.6 | 844.3
540 | 333 | 482.3 | 765.2 | 805.7 | 437 | 845
541 | 334 | 486.8 | 761.9 | 795.9 | 440.9 | 845.3
542 | 335 | 490.9 | 758.4 | 781.8 | 444.4 | 846.3
543 | 336 | 495.4 | 754.9 | 768.7 | 447.8 | 845
544 | 337 | 499.5 | 750.7 | 749.1 | 450.9 | 837.4
545 | 338 | 503.7 | 747.7 | 742.8 | 454.2 | 836.4
546 | 339 | 507.5 | 745.1 | 736.9 | 456.9 | 836.7
547 | 340 | 511.8 | 743.4 | 737.9 | 459.8 | 837.5
548 | 341 | 515.8 | 742.4 | 732.9 | 462.8 | 839
549 | 342 | 519.9 | 742 | 728.5 | 465.7 | 839.2
550 | 343 | 523.9 | 741.2 | 732.2 | 468.7 | 842
551 | 344 | 528.3 | 741.2 | 741.6 | 472.2 | 845.1
552 | 345 | 532.8 | 741.1 | 751.6 | 475.1 | 848.1
553 | 346 | 536.9 | 741.8 | 751.6 | 478.2 | 847.5
554 | 347 | 541.1 | 743.6 | 741.2 | 481.6 | 842.5
555 | 348 | 545.1 | 743.8 | 733.2 | 484.4 | 844.2
556 | 349 | 549.5 | 744.1 | 733.9 | 486.9 | 846.9
557 | 350 | 554 | 744.9 | 740.6 | 489.8 | 848.4
558 | 351 | 558.4 | 745 | 740.1 | 493.1 | 846.6
559 | 352 | 562.7 | 745 | 737.1 | 495.8 | 846
560 | 353 | 567.1 | 744.6 | 742.1 | 498.8 | 850.1
561 | 354 | 572 | 743.9 | 743.7 | 501.7 | 853.6
562 | 355 | 577 | 744.4 | 732.7 | 505.4 | 854.6
563 | 356 | 582.6 | 744.8 | 728.2 | 508.7 | 853.7
564 | 357 | 588 | 744 | 722 | 512 | 849.9
565 | 358 | 593.6 | 742.6 | 722.6 | 514.9 | 851.3
566 | 359 | 599.1 | 742.5 | 729 | 517.7 | 852
567 | 360 | 604.5 | 742.5 | 713.2 | 520.1 | 850.2
568 | 361 | 610 | 741.4 | 701 | 522.7 | 850.4
569 | 362 | 615.5 | 741 | 719.2 | 525 | 852.9
570 | 363 | 620.7 | 741.1 | 734.4 | 527.5 | 859
571 | 364 | 625.3 | 741.6 | 728.9 | 529.9 | 857.3
572 | 365 | 629.7 | 742.1 | 715.8 | 532.1 | 852
573 | 366 | 634.1 | 742.9 | 707.8 | 534.1 | 851.6
574 | 367 | 638.8 | 742.8 | 711.2 | 536.1 | 854.2
575 | 368 | 643.7 | 742.8 | 718.7 | 538.6 | 857.2
576 | 369 | 648.6 | 743 | 730.9 | 541.2 | 859.1
577 | 370 | 653.1 | 743.3 | 743.1 | 543.8 | 858.9
578 | 371 | 657.2 | 743 | 758.5 | 547.1 | 855.3
579 | 372 | 661.4 | 742.9 | 771.4 | 550.1 | 850.6
580 | 373 | 665.4 | 742.9 | 787.6 | 553.7 | 847.1
581 | 374 | 669.6 | 743.8 | 792.9 | 557.6 | 853.1
582 | 375 | 673.3 | 744.2 | 799.3 | 561.3 | 859.8
583 | 376 | 676.3 | 745.3 | 797.2 | 565.4 | 860.6
584 | 377 | 679.7 | 746.8 | 799.1 | 569.1 | 862.9
585 | 378 | 683.3 | 747.1 | 811 | 573.3 | 864.5
586 | 379 | 687.1 | 748.6 | 820.2 | 577.6 | 865.6
587 | 380 | 690.7 | 749.9 | 826.8 | 581.3 | 867.8
588 | 381 | 694.3 | 753 | 834.3 | 585.4 | 867
589 | 382 | 697.4 | 754 | 824.6 | 589.5 | 868.6
590 | 383 | 700.9 | 753.8 | 819.4 | 592.7 | 870
591 | 384 | 704 | 754.4 | 818.8 | 596.3 | 868.6
592 | 385 | 707.2 | 755.3 | 814.9 | 599.3 | 869.5
593 | 386 | 710.5 | 756 | 810.4 | 602.7 | 870.2
594 | 387 | 713.8 | 756.1 | 814.4 | 606 | 874.1
595 | 388 | 717.2 | 756.5 | 819.9 | 609.6 | 875.9
596 | 389 | 720.2 | 756.8 | 827.2 | 613.9 | 881.8
597 | 390 | 722.8 | 757.5 | 829.4 | 618.7 | 882.1
598 | 391 | 725.7 | 757.8 | 836.5 | 623.3 | 881.8
599 | 392 | 728.6 | 758.1 | 836.5 | 627.8 | 884.1
600 | 393 | 731.3 | 758.9 | 835.3 | 631.8 | 886.2
601 | 394 | 734 | 759.7 | 835.5 | 635.8 | 887.5
602 | 395 | 736.5 | 759.9 | 836.4 | 639.4 | 887.2
603 | 396 | 739 | 760.3 | 836.2 | 642.8 | 884.2
604 | 397 | 741.8 | 761.5 | 836.7 | 645.7 | 883.2
605 | 398 | 744.4 | 761.3 | 841.1 | 648.5 | 884
606 | 399 | 746.8 | 760.2 | 840.5 | 651 | 886.4
607 | 400 | 748.5 | 760.3 | 833.7 | 653.9 | 889.4
608 | 401 | 750.3 | 761.7 | 833.5 | 655.9 | 891.4
609 | 402 | 751.9 | 764.9 | 829.7 | 657.8 | 891.7
610 | 403 | 754.3 | 766.7 | 825.6 | 659.9 | 889.6
611 | 404 | 757.1 | 768.2 | 824.8 | 662.4 | 887.7
612 | 405 | 759.6 | 769 | 822.9 | 665.2 | 887.2
613 | 406 | 761.8 | 769.8 | 820.7 | 668 | 887.5
614 | 407 | 764 | 770.4 | 824.4 | 670.6 | 890.4
615 | 408 | 766.5 | 770.3 | 829.3 | 674 | 890.4
616 | 409 | 768.6 | 769.5 | 836 | 677.3 | 891.6
617 | 410 | 770.9 | 770 | 839.5 | 680.7 | 892.9
618 | 411 | 773.3 | 770.3 | 843.5 | 683.9 | 892.4
619 | 412 | 775.8 | 770.3 | 843.9 | 687.1 | 897.4
620 | 413 | 778.5 | 770.2 | 847.1 | 690.6 | 898.6
621 | 414 | 780.9 | 770.2 | 845.4 | 693.7 | 895.9
622 | 415 | 782.8 | 770.8 | 849.1 | 696.7 | 899.2
623 | 416 | 784.2 | 771 | 847.5 | 699.9 | 900.4
624 | 417 | 785.8 | 772.1 | 844.7 | 702.3 | 901.9
625 | 418 | 787.8 | 773.2 | 843.7 | 705.1 | 900.9
626 | 419 | 789.7 | 774.4 | 847.2 | 708 | 901.2
627 | 420 | 791.5 | 775.5 | 849.9 | 711.7 | 899.5
628 | 421 | 793.7 | 777.1 | 849.6 | 715.1 | 900.7
629 | 422 | 795.7 | 777.5 | 853.5 | 718.8 | 901.7
630 | 423 | 798 | 777.8 | 854.2 | 722.9 | 899.1
631 | 424 | 800.7 | 778.6 | 853.3 | 726.8 | 900.2
632 | 425 | 803.2 | 779.5 | 852.6 | 730.8 | 895.2
633 | 426 | 805.4 | 780.6 | 850.4 | 734.7 | 896.4
634 | 427 | 807.5 | 781.2 | 850.6 | 738.8 | 893.8
635 | 428 | 809.6 | 781.5 | 845.9 | 742.4 | 889.9
636 | 429 | 811.3 | 781.6 | 845.4 | 746 | 890.8
637 | 430 | 813.1 | 781.6 | 843.7 | 749.8 | 895.7
638 | 431 | 815.1 | 781.5 | 844.8 | 753.9 | 898.8
639 | 432 | 817.2 | 781.7 | 851.6 | 758.5 | 897.8
640 | 433 | 819.3 | 782.7 | 852.7 | 762.5 | 896.6
641 | 434 | 820.8 | 783 | 858.6 | 766.3 | 899.5
642 | 435 | 822.6 | 782.7 | 862.2 | 769.9 | 902.6
643 | 436 | 824.3 | 783 | 864.8 | 773.4 | 903.3
644 | 437 | 825.9 | 783.6 | 865 | 776.6 | 902
645 | 438 | 827.6 | 784.5 | 863.5 | 780 | 904.6
646 | 439 | 829.5 | 784.9 | 862.7 | 783.4 | 905.2
647 | 440 | 831.7 | 784.8 | 863.7 | 786.4 | 907.3
648 | 441 | 833.4 | 785.3 | 863.6 | 789.5 | 905.7
649 | 442 | 835 | 785.3 | 864.7 | 792.4 | 905.9
650 | 443 | 836.5 | 785.2 | 865.7 | 795.6 | 906.8
651 | 444 | 838.3 | 786.5 | 865.3 | 798.9 | 908.7
652 | 445 | 840 | 787.2 | 866.4 | 802.2 | 909.7
653 | 446 | 841.7 | 787.3 | 866.2 | 805.1 | 906.6
654 | 447 | 843 | 788.1 | 865.9 | 807.8 | 906.3
655 | 448 | 844.4 | 788.9 | 866.3 | 810.6 | 906.1
656 | 449 | 845.5 | 788.9 | 866.6 | 812.9 | 905.5
657 | 450 | 846.5 | 789 | 867.8 | 815.2 | 903.2
658 | 451 | 847.7 | 788.7 | 871 | 817.7 | 906
659 | 452 | 848.7 | 789 | 871.4 | 819.7 | 904.5
660 | 453 | 849.8 | 788.9 | 872.2 | 821.5 | 902.1
661 | 454 | 851.2 | 789.7 | 872.3 | 823.6 | 902.8
662 | 455 | 852.3 | 790.3 | 874.1 | 825.7 | 900.3
663 | 456 | 852.7 | 789.6 | 871.2 | 826.9 | 896.5
664 | 457 | 853.5 | 790 | 868.8 | 828.1 | 894.6
665 | 458 | 854.3 | 789.8 | 865.8 | 828.9 | 894.4
666 | 459 | 854.9 | 789.9 | 866.9 | 830 | 892.6
667 | 460 | 855.7 | 789.9 | 867.3 | 831.2 | 891.5
668 | 461 | 857.4 | 790.2 | 868.4 | 832.7 | 889.9
669 | 462 | 858.6 | 790.4 | 870 | 834.2 | 885.6
670 | 463 | 859.6 | 790.2 | 870.6 | 835.3 | 886.5
671 | 464 | 860.4 | 789.2 | 871.4 | 836.4 | 883.2
672 | 465 | 860.7 | 789.2 | 870.8 | 837 | 882.2
673 | 466 | 860.7 | 790 | 871.5 | 837.6 | 886
674 | 467 | 860.5 | 790.5 | 870.1 | 838.1 | 888.8
675 | 468 | 860.7 | 791.5 | 869.5 | 838.6 | 889.9
676 | 469 | 860.8 | 793 | 869.4 | 839.2 | 892.2
677 | 470 | 861.6 | 795.6 | 870.6 | 840.3 | 895.5
678 | 471 | 863 | 797.2 | 871.4 | 841.9 | 895.2
679 | 472 | 863.8 | 797.9 | 871.9 | 843.9 | 894.8
680 | 473 | 863.8 | 798.2 | 870.3 | 844.8 | 893.2
681 | 474 | 864.4 | 798.7 | 870.3 | 845 | 894.3
682 | 475 | 865.6 | 798.7 | 870.9 | 845.8 | 891.3
683 | 476 | 866 | 799.5 | 870.6 | 847.1 | 890
684 | 477 | 865.7 | 801.4 | 870.8 | 848.1 | 892.1
685 | 478 | 866.1 | 803.1 | 871.9 | 849.5 | 892.7
686 | 479 | 866.2 | 803.7 | 873 | 850.6 | 892.5
687 | 480 | 866.2 | 804.2 | 873.3 | 851.8 | 896.6
688 | 481 | 866.2 | 804.6 | 872.3 | 852.9 | 899.3
689 | 482 | 866.4 | 803.9 | 869 | 853.1 | 902.3
690 | 483 | 866.9 | 803.7 | 868.7 | 853.9 | 909.8
691 | 484 | 867.1 | 804.4 | 868.1 | 854.9 | 909.7
692 | 485 | 867.4 | 803.8 | 868.3 | 855.7 | 905.9
693 | 486 | 867.9 | 804.8 | 869.2 | 856.7 | 903.1
694 | 487 | 868.1 | 806.4 | 869.4 | 857.7 | 905.3
695 | 488 | 868.5 | 806.2 | 868.8 | 858.6 | 908.8
696 | 489 | 868.5 | 807.1 | 867.4 | 859.2 | 914.2
697 | 490 | 869.1 | 808.4 | 867.2 | 860.3 | 917.8
698 | 491 | 869.5 | 808.1 | 866.1 | 861.3 | 925.4
699 | 492 | 870.2 | 808.4 | 864.9 | 861.6 | 925.9
700 | 493 | 871.1 | 809.4 | 866.2 | 862.3 | 922.7
701 | 494 | 872 | 810.9 | 866.2 | 863.5 | 925.1
702 | 495 | 872.6 | 812 | 867 | 864.4 | 924.3
703 | 496 | 872.8 | 812.9 | 865.8 | 865.3 | 918.8
704 | 497 | 873.1 | 813.6 | 864.7 | 866.1 | 914.8
705 | 498 | 873.5 | 813.3 | 867.1 | 866.9 | 917.2
706 | 499 | 873.3 | 812.7 | 867.7 | 868.2 | 913.6
707 | 500 | 873.3 | 813.6 | 868.6 | 870.1 | 912.5
708 | 501 | 873.2 | 813.5 | 869.1 | 871 | 916.4
709 | 502 | 872.9 | 813.3 | 870 | 872 | 921.6
710 | 503 | 872.8 | 814 | 869.7 | 873 | 918.3
711 | 504 | 872.7 | 815.4 | 868.3 | 873.7 | 918.7
712 | 505 | 872.8 | 816 | 869.9 | 874.6 | 922.1
713 | 506 | 872.8 | 814.9 | 869.7 | 875 | 921.8
714 | 507 | 872.6 | 813.4 | 870.7 | 875.2 | 920.1
715 | 508 | 872.7 | 813.2 | 870.8 | 875.3 | 920.6
716 | 509 | 872.7 | 813.3 | 869 | 875.5 | 919.9
717 | 510 | 872.6 | 813.7 | 867 | 875.8 | 913.2
718 | 511 | 872.3 | 814.9 | 865.3 | 876 | 911.9
719 | 512 | 871.9 | 816.1 | 864.3 | 875.9 | 913
720 | 513 | 871.8 | 816.1 | 863.3 | 875.8 | 914.1
721 | 514 | 871.8 | 816 | 866.1 | 876.1 | 919.8
722 | 515 | 871.3 | 815.3 | 867.8 | 875.9 | 917.9
723 | 516 | 870.4 | 815.5 | 867.6 | 875.8 | 923.3
724 | 517 | 870.3 | 817.1 | 868.5 | 876 | 923.2
725 | 518 | 869.7 | 817.9 | 868.7 | 875.8 | 922.4
726 | 519 | 869.2 | 818.9 | 868.8 | 875.8 | 918.5
727 | 520 | 869.4 | 820.4 | 870.8 | 876 | 921
728 | 521 | 869.1 | 820.7 | 871.7 | 876.1 | 930.1
729 | 522 | 868.5 | 821.4 | 871.9 | 876 | 930.6
730 | 523 | 867.6 | 820.3 | 870 | 875.7 | 930.1
731 | 524 | 867.5 | 819.3 | 868.8 | 875.6 | 928.5
732 | 525 | 867.5 | 817.2 | 870.2 | 875.8 | 921.9
733 | 526 | 867.8 | 815.2 | 870 | 876 | 914.6
734 | 527 | 868.4 | 814.9 | 873 | 876.9 | 908.5
735 | 528 | 868.9 | 814.3 | 874.8 | 877.7 | 904.2
736 | 529 | 869.5 | 813.8 | 876.6 | 878.3 | 906.2
737 | 530 | 869.5 | 813.5 | 875.9 | 878.3 | 906.4
738 | 531 | 869.5 | 812.3 | 874.5 | 878.3 | 907.6
739 | 532 | 869.5 | 811.7 | 872.6 | 878.3 | 906.3
740 | 533 | 869.7 | 810.7 | 871.8 | 878.4 | 899.6
741 | 534 | 870 | 808.4 | 870.2 | 878.6 | 891.3
742 | 535 | 870.8 | 807.7 | 869.2 | 879.1 | 892
743 | 536 | 871.2 | 807.3 | 868.7 | 879.3 | 893
744 | 537 | 871 | 807.5 | 870.7 | 879.1 | 899.7
745 | 538 | 870.9 | 808.2 | 872.8 | 878.8 | 904.6
746 | 539 | 870.5 | 807.1 | 875.2 | 878.4 | 903.2
747 | 540 | 870.1 | 806.2 | 873.7 | 878 | 897.9
748 | 541 | 869.8 | 805.8 | 874.5 | 877.4 | 893.4
749 | 542 | 869.7 | 805.7 | 876.2 | 877.1 | 893.2
750 | 543 | 869.6 | 807.7 | 876.4 | 877 | 897.5
751 | 544 | 869.4 | 809.2 | 877.6 | 876.9 | 899.9
752 | 545 | 868.8 | 809.6 | 875.8 | 876.5 | 903
753 | 546 | 868.3 | 808.5 | 876.2 | 876 | 901.4
754 | 547 | 868.1 | 807.8 | 873.2 | 875.4 | 897
755 | 548 | 868.5 | 804.5 | 869.1 | 875.3 | 886.1
756 | 549 | 868.7 | 802.1 | 869.5 | 875.1 | 877
757 | 550 | 868.7 | 802.2 | 871.6 | 875.1 | 882.1
758 | 551 | 868.9 | 801.8 | 872.1 | 875.1 | 881.7
759 | 552 | 868.7 | 800.9 | 870.7 | 874.9 | 877.7
760 | 553 | 869 | 800.2 | 871.4 | 875.2 | 879.6
761 | 554 | 869 | 799.8 | 871.7 | 875.2 | 880.5
762 | 555 | 869.5 | 800.2 | 869.2 | 875.5 | 877.6
763 | 556 | 870.2 | 799.6 | 872 | 876.2 | 874.3
764 | 557 | 870.7 | 799.6 | 872.2 | 876.8 | 874.4
765 | 558 | 871.3 | 799 | 873.4 | 877.5 | 868.8
766 | 559 | 872 | 798.3 | 871.4 | 877.9 | 863.5
767 | 560 | 872.9 | 796.9 | 868.3 | 878.2 | 853.8
768 | 561 | 873.3 | 795.9 | 866.6 | 878.5 | 847.7
769 | 562 | 873.6 | 796.2 | 866.3 | 878.6 | 848
770 | 563 | 873 | 798.2 | 867.2 | 878.5 | 854.5
771 | 564 | 872.7 | 800 | 868.4 | 878.2 | 860.1
772 | 565 | 872.5 | 801 | 866.3 | 878 | 858.9
773 | 566 | 872.4 | 801.2 | 864.9 | 877.8 | 855.3
774 | 567 | 872.4 | 801.8 | 866.6 | 877.8 | 854.2
775 | 568 | 873.1 | 802.5 | 869.1 | 878.3 | 850.7
776 | 569 | 873.4 | 804.1 | 870.8 | 878.6 | 856.9
777 | 570 | 873.5 | 806.2 | 869.7 | 878.8 | 861.8
778 | 571 | 873.8 | 807.1 | 870.5 | 879 | 864.5
779 | 572 | 874.1 | 807 | 869.7 | 879.4 | 862.3
780 | 573 | 874.7 | 808.4 | 868.1 | 880 | 860.7
781 | 574 | 876 | 808.8 | 864.3 | 880.6 | 857.6
782 | 575 | 876.8 | 807.6 | 862.3 | 880.8 | 853.4
783 | 576 | 877.4 | 807.5 | 863.8 | 881.5 | 848.5
784 | 577 | 877.9 | 806.1 | 866.3 | 882.5 | 847.2
785 | 578 | 877.7 | 808.1 | 868.4 | 882.8 | 853.5
786 | 579 | 877.8 | 809 | 872.4 | 883.1 | 859.6
787 | 580 | 878.2 | 810.7 | 874.8 | 883.6 | 865.4
788 | 581 | 878.1 | 811 | 873.2 | 883.7 | 869.9
789 | 582 | 878.1 | 811.1 | 868.9 | 883.8 | 873.5
790 | 583 | 877.9 | 812.7 | 868.3 | 883.8 | 876.7
791 | 584 | 877.9 | 813.9 | 868.6 | 884 | 887.2
792 | 585 | 878.6 | 812.9 | 867.1 | 884.4 | 893.2
793 | 586 | 879.3 | 812.5 | 869.5 | 884.8 | 890.5
794 | 587 | 879.6 | 813.4 | 867.4 | 884.8 | 889.8
795 | 588 | 879.9 | 815.4 | 868.7 | 885.3 | 898.1
796 | 589 | 880.1 | 817.1 | 870.5 | 885.6 | 904.4
797 | 590 | 880.5 | 818.2 | 871.6 | 885.9 | 910.7
798 | 591 | 880.7 | 818.1 | 871.5 | 886 | 909.8
799 | 592 | 880.8 | 818.5 | 873 | 886.2 | 906.9
800 | 593 | 881.5 | 819.2 | 876.1 | 886.6 | 904.1
801 | 594 | 882.6 | 818.6 | 875.9 | 887 | 898.9
802 | 595 | 883.6 | 815.9 | 874.2 | 887.2 | 885.9
803 | 596 | 884.9 | 814.8 | 876.1 | 887.9 | 877.3
804 | 597 | 885.2 | 815.8 | 876.4 | 888.3 | 881.3
805 | 598 | 885 | 816.8 | 875 | 888.3 | 882.8
806 | 599 | 885.1 | 818.5 | 877 | 888.6 | 888.1
807 | 600 | 885.5 | 819.3 | 878.4 | 888.8 | 888
808 | 601 | 885.6 | 819.2 | 878.5 | 888.6 | 889.3
809 | 602 | 885.9 | 819.5 | 876.9 | 888.6 | 893.4
810 | 603 | 886.5 | 819.5 | 877.5 | 888.8 | 899
811 | 604 | 887.3 | 820.9 | 877.3 | 889.2 | 900.4
812 | 605 | 887.8 | 822.6 | 875.7 | 889.4 | 898.3
813 | 606 | 888.3 | 823.3 | 876.4 | 889.5 | 902.5
814 | 607 | 888.9 | 823.6 | 875 | 889.7 | 896.8
815 | 608 | 889.6 | 823.7 | 872.9 | 889.9 | 897.8
816 | 609 | 890.6 | 822.7 | 870.4 | 890.3 | 897.2
817 | 610 | 891.9 | 820.2 | 866.6 | 890.6 | 904.7
818 | 611 | 892.7 | 818.2 | 865.1 | 890.9 | 906.4
819 | 612 | 893.4 | 816.9 | 861.1 | 891.3 | 908.9
820 | 613 | 893.9 | 815.9 | 857.5 | 891.6 | 907.9
821 | 614 | 894.9 | 813.3 | 851.4 | 891.7 | 906.8
822 | 615 | 895.5 | 810.3 | 847.3 | 891.9 | 900.6
823 | 616 | 895.9 | 807.7 | 846.2 | 892.2 | 891.2
824 | 617 | 896 | 806.1 | 850.7 | 892.4 | 885.9
825 | 618 | 896.1 | 804.5 | 851.9 | 892.4 | 872.2
826 | 619 | 896 | 802.1 | 851.7 | 892.3 | 866.5
827 | 620 | 896.9 | 801.6 | 854.4 | 892.6 | 871
828 | 621 | 896.9 | 802.7 | 858.1 | 892.7 | 878.5
829 | 622 | 896.9 | 803 | 855.3 | 892.9 | 880.3
830 | 623 | 897 | 803.5 | 856.9 | 892.9 | 884.8
831 | 624 | 896.4 | 803.7 | 853.3 | 892.7 | 880.1
832 | 625 | 897.1 | 804.3 | 853.9 | 892.7 | 883.6
833 | 626 | 896.4 | 804 | 856.6 | 892.4 | 885.7
834 | 627 | 896.1 | 804 | 862.3 | 892 | 888.1
835 | 628 | 895 | 804.5 | 864.8 | 891.6 | 885
836 | 629 | 895.2 | 804.2 | 862.4 | 891.4 | 877
837 | 630 | 895.9 | 803.1 | 862.2 | 891.3 | 872.7
838 | 631 | 895.9 | 803.7 | 862 | 891.3 | 873.9
839 | 632 | 895.5 | 804.7 | 863.3 | 891.1 | 875.1
840 | 633 | 894.8 | 806 | 863.3 | 890.7 | 880.3
841 | 634 | 894 | 808 | 863.9 | 890.3 | 888.8
842 | 635 | 893.4 | 810.1 | 863.6 | 889.9 | 897.8
843 | 636 | 892.9 | 811.4 | 866.3 | 889.6 | 901.2
844 | 637 | 892.4 | 810.9 | 862.9 | 889.3 | 903.1
845 | 638 | 893.3 | 811.2 | 864.6 | 889.7 | 902.6
846 | 639 | 893.3 | 812.3 | 867.3 | 889.7 | 905.7
847 | 640 | 892.6 | 812.9 | 869.3 | 889.8 | 896.9
848 | 641 | 893 | 813.6 | 869.7 | 890.1 | 895.6
849 | 642 | 893.2 | 815.1 | 870.6 | 890.4 | 899.2
850 | 643 | 892.9 | 815.4 | 871.5 | 890 | 904.3
851 | 644 | 892.5 | 814.8 | 871.9 | 889.9 | 901
852 | 645 | 892.5 | 816 | 871 | 889.9 | 887.7
853 | 646 | 893.2 | 817 | 870.7 | 890.3 | 890
854 | 647 | 893.1 | 817.9 | 870.1 | 890.6 | 895
855 | 648 | 893.4 | 820.1 | 870.3 | 891.4 | 895
856 | 649 | 893.6 | 821 | 870.2 | 891.2 | 897.7
857 | 650 | 892.9 | 821.8 | 869.1 | 891.5 | 898.2
858 | 651 | 893.3 | 823.5 | 870.2 | 892.1 | 897.5
859 | 652 | 893.2 | 824.2 | 869.7 | 891.9 | 898.2
860 | 653 | 893.7 | 824.9 | 867.4 | 892.1 | 896.8
861 | 654 | 894.2 | 825.7 | 868.9 | 892.5 | 905.7
862 | 655 | 894.6 | 826.5 | 870.9 | 892.6 | 914.7
863 | 656 | 894.9 | 826.6 | 873.7 | 892.8 | 921.9
864 | 657 | 895.1 | 826.1 | 872.7 | 892.9 | 920.4
865 | 658 | 895.2 | 826.4 | 874 | 892.8 | 919.1
866 | 659 | 895.5 | 827.3 | 874.4 | 893.9 | 919.1
867 | 660 | 896 | 827.7 | 874.4 | 894.4 | 919.1
868 | 661 | 896.9 | 828.7 | 872.5 | 895.2 | 921.8
869 | 662 | 897.5 | 828.6 | 871.6 | 895.6 | 920.8
870 | 663 | 898 | 829.3 | 870.9 | 896.1 | 916.7
871 | 664 | 898.2 | 828.9 | 872.6 | 896.3 | 915.1
872 | 665 | 898.8 | 828.3 | 871.7 | 896.5 | 913.6
873 | 666 | 899.3 | 828.6 | 872 | 896.9 | 922.9
874 | 667 | 899.9 | 828.7 | 867 | 897.1 | 922.2
875 | 668 | 900.4 | 829.3 | 867.5 | 897.1 | 922
876 | 669 | 901.1 | 830.6 | 871.6 | 897.6 | 927.7
877 | 670 | 901.7 | 828.8 | 869 | 897.6 | 919.2
878 | 671 | 903.1 | 825.2 | 860.8 | 898.2 | 907
879 | 672 | 903.9 | 821.1 | 859.4 | 898.7 | 897.7
880 | 673 | 904.3 | 818.7 | 863 | 898.9 | 893.1
881 | 674 | 904.5 | 816.1 | 863.5 | 898.8 | 885.3
882 | 675 | 905 | 814.6 | 864.8 | 899.3 | 885.3
883 | 676 | 904.9 | 813.5 | 865.1 | 899.1 | 889.1
884 | 677 | 904.6 | 814 | 866.3 | 898.9 | 893.3
885 | 678 | 904.1 | 815 | 867.2 | 898.7 | 896.8
886 | 679 | 903.5 | 815.6 | 866.2 | 898.2 | 894.9
887 | 680 | 903.1 | 815.3 | 861.2 | 897.1 | 901.1
888 | 681 | 903.3 | 813.3 | 859 | 896.9 | 899.3
889 | 682 | 903.8 | 812.1 | 858.3 | 897.1 | 890.6
890 | 683 | 904 | 811.2 | 858.7 | 897.4 | 887.7
891 | 684 | 904.1 | 811.3 | 859.6 | 897.4 | 888.1
892 | 685 | 904.1 | 811.6 | 857.5 | 897.1 | 892.6
893 | 686 | 904.1 | 811.1 | 861.1 | 897.3 | 898.1
894 | 687 | 904 | 810.2 | 861.4 | 896.7 | 894.6
895 | 688 | 903.3 | 809.9 | 862.6 | 896.3 | 892.7
896 | 689 | 902.9 | 810.3 | 862.9 | 896 | 889.5
897 | 690 | 903 | 810.9 | 861.2 | 896 | 886.1
898 | 691 | 902.7 | 811.6 | 862.5 | 895.7 | 884
899 | 692 | 902.5 | 811.3 | 865.6 | 895.7 | 880.4
900 | 693 | 902.1 | 811.1 | 866.3 | 895.3 | 873
901 | 694 | 902.2 | 809.2 | 865.4 | 895.2 | 863.8
902 | 695 | 902.3 | 806.8 | 859.5 | 895.1 | 860
903 | 696 | 902.6 | 805 | 857.1 | 895.4 | 855.1
904 | 697 | 902.9 | 804.4 | 858.2 | 895.9 | 855.1
905 | 698 | 903.2 | 806 | 858.2 | 896.2 | 857.2
906 | 699 | 903.2 | 806.7 | 859.8 | 896.3 | 855.8
907 | 700 | 903 | 807.1 | 859.4 | 896 | 857.3
908 | 701 | 902.9 | 808.2 | 859.5 | 895.7 | 860.4
909 | 702 | 903.2 | 807.1 | 856.8 | 895.4 | 860.3
910 | 703 | 903.3 | 805.5 | 855.1 | 895.5 | 857.3
911 | 704 | 903.3 | 804.4 | 851.8 | 894.9 | 853.2
912 | 705 | 903.2 | 802.9 | 844.6 | 894.7 | 835.4
913 | 706 | 903.3 | 801.3 | 842 | 895 | 825.5
914 | 707 | 903.5 | 800.8 | 845.1 | 895 | 822.9
915 | 708 | 903.6 | 800.1 | 846.2 | 894.8 | 823.5
916 | 709 | 903.2 | 801 | 848.6 | 894.5 | 822
917 | 710 | 902.8 | 801.5 | 851.3 | 894.2 | 821
918 | 711 | 902.4 | 803.4 | 853 | 894.1 | 824.3
919 | 712 | 901.8 | 806.2 | 852.2 | 893.9 | 831.2
920 | 713 | 901.2 | 807 | 851.7 | 893.5 | 840.4
921 | 714 | 900.6 | 809.9 | 850.3 | 893.2 | 851.7
922 | 715 | 900 | 813.3 | 852.3 | 893.2 | 862.5
923 | 716 | 899.7 | 814.6 | 854.8 | 893.1 | 870.9
924 | 717 | 899.8 | 814.6 | 852.2 | 892.7 | 863.9
925 | 718 | 899.8 | 812.5 | 850 | 892.3 | 845
926 | 719 | 899.4 | 812.4 | 853 | 892.1 | 846.7
927 | 720 | 899.1 | 813.7 | 853.1 | 892.1 | 847.9
928 | 721 | 898.5 | 814.7 | 855.7 | 891.8 | 853.3
929 | 722 | 898.5 | 815.1 | 855.4 | 891.8 | 854.4
930 | 723 | 898.7 | 812.7 | 851.7 | 891.7 | 847.3
931 | 724 | 898.7 | 811.8 | 854.2 | 891.6 | 840.9
932 | 725 | 898.5 | 811.6 | 854.5 | 891.6 | 841.5
933 | 726 | 898.4 | 812 | 855 | 891.6 | 845.4
934 | 727 | 898.2 | 813 | 854.6 | 891.6 | 850.1
935 | 728 | 898.6 | 811.9 | 848.8 | 891.6 | 850.9
936 | 729 | 898.8 | 811.1 | 846.6 | 891.8 | 849.2
937 | 730 | 898.6 | 811.5 | 848.2 | 892 | 851.3
938 | 731 | 898.4 | 812.5 | 848.2 | 891.8 | 857.7
939 | 732 | 898.1 | 813.8 | 844.4 | 891.7 | 866
940 | 733 | 898.2 | 813.9 | 842.9 | 891.9 | 866.7
941 | 734 | 898.4 | 812.9 | 840.6 | 891.9 | 862.4
942 | 735 | 898 | 811.7 | 839 | 891.6 | 858.5
943 | 736 | 897.1 | 813 | 844.4 | 891.2 | 861.6
944 | 737 | 896.3 | 813.8 | 847.1 | 890.6 | 864.5
945 | 738 | 895.7 | 815.3 | 848.2 | 890.3 | 867.1
946 | 739 | 895.5 | 816.8 | 847.4 | 890.1 | 871.3
947 | 740 | 895.4 | 816.5 | 846 | 890.2 | 867.2
948 | 741 | 894.9 | 816.2 | 849 | 890.1 | 858.8
949 | 742 | 894.5 | 816 | 848.6 | 889.7 | 854.9
950 | 743 | 894.4 | 815.4 | 849 | 889.2 | 847.2
951 | 744 | 894.1 | 813.5 | 847.7 | 888.8 | 836.5
952 | 745 | 894.6 | 812.2 | 844.9 | 888.9 | 829.1
953 | 746 | 894.4 | 812.2 | 845.7 | 889.2 | 825.6
954 | 747 | 894.4 | 812.7 | 847.7 | 889.2 | 824.2
955 | 748 | 894.6 | 813.6 | 848.3 | 889.5 | 824.4
956 | 749 | 894.6 | 813.5 | 848.8 | 890.2 | 821.9
957 | 750 | 894.1 | 815.2 | 850.6 | 890.1 | 830.7
958 | 751 | 893.2 | 816.9 | 850.9 | 889.3 | 842
959 | 752 | 892 | 817.9 | 850.9 | 888.4 | 848.2
960 | 753 | 890.7 | 820.3 | 849.5 | 887.3 | 853.4
961 | 754 | 889.7 | 822.8 | 845.2 | 887 | 864.4
962 | 755 | 888.8 | 824.1 | 842.4 | 886.9 | 871.9
963 | 756 | 888.2 | 826.6 | 847.4 | 886.7 | 874.1
964 | 757 | 888.2 | 828.7 | 849.9 | 886.8 | 876.7
965 | 758 | 888.2 | 830.1 | 851.8 | 887.2 | 875.5
966 | 759 | 888.2 | 832 | 853.4 | 887.6 | 875.8
967 | 760 | 888.3 | 832.3 | 854.1 | 887.7 | 877.7
968 | 761 | 888.6 | 832.1 | 852.5 | 887.9 | 879.4
969 | 762 | 889.1 | 833.3 | 851.7 | 888.3 | 884.4
970 | 763 | 889.6 | 833.6 | 852.8 | 888.9 | 882.8
971 | 764 | 890.1 | 833.8 | 852.7 | 889.5 | 884.9
972 | 765 | 890.5 | 834.6 | 855.3 | 889.9 | 884.4
973 | 766 | 891 | 836 | 858.5 | 890.6 | 887.5
974 | 767 | 891.4 | 835.2 | 862 | 890.7 | 887.2
975 | 768 | 891.5 | 834.1 | 862.9 | 890.5 | 882.8
976 | 769 | 891.7 | 834.3 | 862.9 | 890.4 | 890.1
977 | 770 | 892.2 | 833.7 | 863.7 | 891.1 | 890.4
978 | 771 | 892.5 | 833.5 | 864.3 | 891.2 | 891.3
979 | 772 | 893.1 | 833.3 | 863.5 | 891.5 | 893.4
980 | 773 | 894 | 831.9 | 865.9 | 892.4 | 886.5
981 | 774 | 895 | 830.1 | 865.4 | 893.1 | 871.6
982 | 775 | 896.1 | 827.8 | 860.8 | 893.3 | 858.8
983 | 776 | 896.8 | 826.4 | 863 | 894 | 852.9
984 | 777 | 897.6 | 825.4 | 864.6 | 894.2 | 852.5
985 | 778 | 897.8 | 825 | 865.3 | 894.5 | 857.3
986 | 779 | 898.2 | 824.2 | 864.3 | 894.1 | 863.1
987 | 780 | 898.4 | 824.2 | 863.1 | 894 | 870
988 | 781 | 898.7 | 825.7 | 862.4 | 894.4 | 874.8
989 | 782 | 899 | 826.9 | 862 | 894.3 | 877.4
990 | 783 | 899.1 | 827.8 | 861.4 | 894.9 | 880.4
991 | 784 | 899.2 | 828.8 | 861.2 | 894.8 | 878.5
992 | 785 | 899.2 | 830.6 | 861.5 | 894.6 | 885.2
993 | 786 | 899.1 | 829.7 | 861.5 | 894.1 | 888.2
994 | 787 | 899 | 828.6 | 863.6 | 893.6 | 889.6
995 | 788 | 898.9 | 827.3 | 864.2 | 893.5 | 888.5
996 | 789 | 898.7 | 827.6 | 864.5 | 893.2 | 883.1
997 | 790 | 898.4 | 828 | 862.9 | 892.7 | 880.3
998 | 791 | 898.3 | 829.7 | 861.2 | 892.7 | 883.4
999 | 792 | 898.6 | 830.5 | 862.2 | 893 | 888.1
1000 | 793 | 898.9 | 830.8 | 862.5 | 893.5 | 896.5
1001 | 794 | 899.3 | 831.7 | 861.3 | 894 | 898.2
1002 | 795 | 899.6 | 832.4 | 859.7 | 894.2 | 893.5
1003 | 796 | 899.9 | 832.8 | 856.8 | 894.3 | 899.1
1004 | 797 | 900.2 | 832.1 | 849.2 | 894.7 | 900.1
1005 | 798 | 900.1 | 831.2 | 843.3 | 894.7 | 894.7
1006 | 799 | 900.1 | 832.4 | 843.6 | 894.8 | 890.9
1007 | 800 | 900.2 | 834.4 | 847.9 | 894.7 | 895.3
1008 | 801 | 900.3 | 835.6 | 849.9 | 894.6 | 895.3
1009 | 802 | 900.2 | 834.4 | 846.5 | 894.3 | 894.9
1010 | 803 | 900.2 | 834 | 846.9 | 894.2 | 898.4
1011 | 804 | 900.3 | 832.7 | 847.6 | 894.1 | 900.3
1012 | 805 | 900.2 | 832.5 | 850.3 | 894.2 | 900.2
1013 | 806 | 899.8 | 832.2 | 853 | 894 | 899.5
1014 | 807 | 899.3 | 833.8 | 857.8 | 893.6 | 901.6
1015 | 808 | 899.3 | 835.7 | 860.6 | 893.8 | 906.2
1016 | 809 | 899.3 | 836.3 | 859.4 | 894.2 | 906.2
1017 | 810 | 899.3 | 837.8 | 858.7 | 894.2 | 905.4
1018 | 811 | 899.6 | 838 | 857.5 | 894.3 | 904
1019 | 812 | 899.8 | 835.6 | 853.6 | 894.4 | 900.2
1020 | 813 | 900.3 | 834.6 | 844.8 | 894.8 | 887.7
1021 | 814 | 900.2 | 833.4 | 836 | 894.9 | 876
1022 | 815 | 900.1 | 833.4 | 834.3 | 894.8 | 873.5
1023 | 816 | 899.7 | 834.6 | 833.7 | 894.2 | 877.7
1024 | 817 | 899.1 | 836.6 | 834.7 | 893.5 | 881.8
1025 | 818 | 898.4 | 837.2 | 835.5 | 892.5 | 885.6
1026 | 819 | 897.9 | 838.9 | 835.4 | 891.7 | 888.1
1027 | 820 | 897.5 | 840.8 | 837.5 | 891.3 | 891.8
1028 | 821 | 897.3 | 841.2 | 839.6 | 890.8 | 892.1
1029 | 822 | 897.3 | 842.4 | 837.9 | 890.5 | 893.2
1030 | 823 | 897.3 | 843.7 | 842.3 | 890.4 | 898.8
1031 | 824 | 897.2 | 844.9 | 847.4 | 890.3 | 899.2
1032 | 825 | 897 | 845.7 | 850.9 | 890 | 905.5
1033 | 826 | 896.9 | 844.9 | 848.8 | 889.6 | 896.5
1034 | 827 | 897.1 | 844 | 844.5 | 889.5 | 889.1
1035 | 828 | 897.2 | 844.4 | 835.5 | 890.1 | 886.5
1036 | 829 | 897 | 845.7 | 835.1 | 889.9 | 888.7
1037 | 830 | 896.9 | 846.5 | 832.1 | 889.8 | 891.4
1038 | 831 | 897.2 | 847.5 | 830.1 | 890.4 | 891.1
1039 | 832 | 896.8 | 848.5 | 828.4 | 890.2 | 889
1040 | 833 | 896.2 | 850.9 | 827.6 | 889.7 | 890.7
1041 | 834 | 895.8 | 853.3 | 824.6 | 888.8 | 894.4
1042 | 835 | 895.4 | 856.6 | 821.9 | 888.3 | 899.8
1043 | 836 | 894.8 | 859 | 824.9 | 888.1 | 907.3
1044 | 837 | 895.2 | 860.2 | 825.9 | 888.5 | 909.9
1045 | 838 | 895.5 | 856 | 815.2 | 888.7 | 891.1
1046 | 839 | 895.1 | 852.7 | 810.5 | 888.9 | 875.5
1047 | 840 | 894.5 | 852.2 | 811.4 | 888.5 | 876.3
1048 | 841 | 894.2 | 852 | 805.5 | 888.1 | 873.5
1049 | 842 | 893.9 | 850.6 | 801.2 | 888.1 | 869
1050 | 843 | 894 | 847.6 | 799.5 | 888.3 | 857.6
1051 | 844 | 893.1 | 845.5 | 803.8 | 887.9 | 848.9
1052 | 845 | 891.9 | 845.9 | 804.2 | 886.6 | 851.6
1053 | 846 | 891.6 | 846.1 | 796.2 | 886.1 | 853.9
1054 | 847 | 891.2 | 843.8 | 788.2 | 885.9 | 848.6
1055 | 848 | 890.7 | 838.9 | 776.8 | 885.6 | 836.3
1056 | 849 | 890 | 832 | 769 | 885 | 821.9
1057 | 850 | 887.8 | 824.1 | 756.6 | 882.9 | 805.1
1058 | 851 | 886.3 | 816.7 | 748.1 | 881.1 | 788.2
1059 | 852 | 884.7 | 813.3 | 745.2 | 879.9 | 784.5
1060 | 853 | 882.5 | 813.4 | 748.8 | 878.4 | 790.5
1061 | 854 | 880.7 | 811.7 | 748.2 | 877.1 | 785.5
1062 | 855 | 879.1 | 811.1 | 751.4 | 876 | 783.8
1063 | 856 | 877.6 | 811.3 | 759.2 | 875.2 | 780.3
1064 | 857 | 876.6 | 814.3 | 762.4 | 874.6 | 784
1065 | 858 | 875.5 | 816.5 | 761.2 | 873.5 | 789.3
1066 | 859 | 874.4 | 813.2 | 754.7 | 872.4 | 782.3
1067 | 860 | 873.1 | 811.6 | 759 | 871.4 | 774.3
1068 | 861 | 872.2 | 811.9 | 758.2 | 870.5 | 773.8
1069 | 862 | 871.2 | 812.6 | 760.4 | 869.7 | 772.4
1070 | 863 | 869.6 | 817.6 | 772.3 | 868.7 | 779.6
1071 | 864 | 868.2 | 820.9 | 782.9 | 867 | 786.7
1072 | 865 | 867.5 | 821.8 | 783.4 | 865.8 | 791.3
1073 | 866 | 867 | 825.1 | 788.3 | 865.2 | 799.8
1074 | 867 | 866.3 | 829.9 | 796 | 864.4 | 808.5
1075 | 868 | 865.2 | 833.9 | 801.7 | 863.1 | 815.1
1076 | 869 | 865.1 | 839.2 | 797.5 | 862.2 | 823.2
1077 | 870 | 864.3 | 843.4 | 801.4 | 861.5 | 833.5
1078 | 871 | 865 | 845 | 805.4 | 861.7 | 837.3
1079 | 872 | 865.5 | 844.8 | 805.8 | 861.8 | 836.2
1080 | 873 | 865.2 | 846.5 | 812 | 861.7 | 839.9
1081 | 874 | 864.5 | 848.1 | 810.9 | 860.4 | 847.9
1082 | 875 | 864.7 | 850.3 | 807.7 | 860.1 | 852.7
1083 | 876 | 864.6 | 851.1 | 809.4 | 860 | 853.3
1084 | 877 | 864.4 | 851.2 | 812 | 859.2 | 854.3
1085 | 878 | 864.5 | 852.7 | 803.8 | 859.3 | 856
1086 | 879 | 864.6 | 855.4 | 801.4 | 859.4 | 861.3
1087 | 880 | 865.5 | 858 | 793.5 | 859.8 | 867.6
1088 | 881 | 865.7 | 858.4 | 789.1 | 859.6 | 864.2
1089 | 882 | 866.5 | 858.8 | 781.5 | 860 | 867.9
1090 | 883 | 866.7 | 853.6 | 776.1 | 860.2 | 876.9
1091 | 884 | 866.6 | 850.9 | 782.1 | 860.6 | 875.7
1092 | 885 | 866.4 | 853.1 | 792.1 | 860.7 | 879.7
1093 | 886 | 866.5 | 856.2 | 803.1 | 860.5 | 884.9
1094 | 887 | 867.1 | 856.6 | 810.6 | 860.8 | 884.8
1095 | 888 | 867.7 | 857.6 | 807.3 | 861 | 882.3
1096 | 889 | 867.2 | 859.3 | 814.4 | 860.5 | 883
1097 | 890 | 868 | 862.2 | 821.1 | 860.9 | 879.6
1098 | 891 | 869 | 861.8 | 823.7 | 861.1 | 875
1099 | 892 | 869.7 | 859.1 | 827.2 | 861.4 | 867.3
1100 | 893 | 869.6 | 859.4 | 833.9 | 861 | 865.4
1101 | 894 | 870.1 | 862.4 | 832.9 | 861.4 | 864.3
1102 | 895 | 871 | 861.9 | 825.9 | 861.8 | 858.4
1103 | 896 | 871.5 | 857.7 | 814.7 | 862.1 | 850.5
1104 | 897 | 871.7 | 853.1 | 807.7 | 862.1 | 845.3
1105 | 898 | 871.9 | 851.2 | 811.1 | 862.1 | 839
1106 | 899 | 871.8 | 852.7 | 813 | 862 | 839.4
1107 | 900 | 872.1 | 855.1 | 806.1 | 862.3 | 844
1108 | 901 | 872 | 852.9 | 798 | 862.5 | 843
1109 | 902 | 872 | 846.3 | 786.8 | 862.8 | 829.2
1110 | 903 | 871.8 | 840.6 | 780.8 | 863.1 | 816
1111 | 904 | 871.4 | 835.9 | 776.9 | 863.1 | 809.4
1112 | 905 | 871.2 | 833.4 | 774.5 | 863 | 807.5
1113 | 906 | 870.7 | 832.1 | 770.8 | 863 | 808.7
1114 | 907 | 870.4 | 829.4 | 771.8 | 863.1 | 805.5
1115 | 908 | 869.9 | 827.7 | 776 | 862.9 | 801.4
1116 | 909 | 869.5 | 827.5 | 777.6 | 862.6 | 800.8
1117 | 910 | 869 | 829.1 | 784.2 | 862.3 | 803.5
1118 | 911 | 868.8 | 831.6 | 783.1 | 862 | 806.2
1119 | 912 | 868.7 | 835.2 | 786 | 861.9 | 808.8
1120 | 913 | 868.3 | 836.8 | 788.6 | 861.2 | 811.6
1121 | 914 | 868 | 840.8 | 791.9 | 860.8 | 817.3
1122 | 915 | 867.7 | 844 | 796.9 | 860.4 | 829.1
1123 | 916 | 867.1 | 847.1 | 797.5 | 859.6 | 836.5
1124 | 917 | 866.9 | 848 | 801 | 858.9 | 843.1
1125 | 918 | 866.8 | 847.3 | 809.4 | 858.9 | 844.3
1126 | 919 | 866.8 | 846.6 | 805.8 | 858.8 | 841.5
1127 | 920 | 866.7 | 845 | 801.7 | 858.9 | 841.3
1128 | 921 | 866.7 | 841.7 | 794.4 | 859.3 | 833.7
1129 | 922 | 866.6 | 837.6 | 788 | 859.8 | 829.1
1130 | 923 | 866.7 | 833.2 | 778.8 | 860.4 | 821.4
1131 | 924 | 866.3 | 827.4 | 773.7 | 860.5 | 809.2
1132 | 925 | 865.9 | 823.1 | 768.6 | 860.5 | 804.2
1133 | 926 | 865.8 | 822.5 | 768 | 861 | 807.5
1134 | 927 | 865.7 | 821.5 | 769.6 | 860.9 | 806.4
1135 | 928 | 865.5 | 822.5 | 777.1 | 861 | 810.4
1136 | 929 | 865.7 | 829.3 | 785.2 | 860.8 | 819.4
1137 | 930 | 865.3 | 834.6 | 789.3 | 860 | 828.4
1138 | 931 | 864.7 | 838.5 | 793.6 | 858.7 | 838.6
1139 | 932 | 864.6 | 841 | 792.4 | 858.3 | 847.6
1140 | 933 | 865.4 | 840.7 | 786.8 | 858.3 | 852.5
1141 | 934 | 865 | 836.4 | 784.1 | 858.4 | 843.8
1142 | 935 | 864.8 | 835.9 | 789.2 | 858.7 | 843.1
1143 | 936 | 865 | 834.5 | 791 | 859.4 | 840.7
1144 | 937 | 865.1 | 832.7 | 791.9 | 859.9 | 834.2
1145 | 938 | 865.1 | 829.6 | 790.6 | 860 | 827.8
1146 | 939 | 865.1 | 827.3 | 792.6 | 859.5 | 822.1
1147 | 940 | 864.8 | 820.3 | 789.1 | 859.3 | 805.1
1148 | 941 | 864.6 | 814.3 | 783.8 | 859.3 | 797.2
1149 | 942 | 864 | 808.1 | 769.8 | 859.3 | 786.9
1150 | 943 | 862.7 | 796.1 | 744.4 | 858.8 | 769.4
1151 | 944 | 861 | 782 | 717.7 | 857.6 | 752.6
1152 | 945 | 858.9 | 769.1 | 694.3 | 855.6 | 737.3
1153 | 946 | 856.8 | 755.3 | 674.8 | 853.4 | 725.4
1154 | 947 | 854.2 | 739.4 | 657 | 850.6 | 715
1155 | 948 | 851.5 | 727.4 | 640 | 847.4 | 705.5
1156 | 949 | 848.6 | 716.6 | 625.4 | 844.2 | 697.4
1157 | 950 | 845.4 | 703.3 | 611.8 | 840.7 | 689.9
1158 | 951 | 842.1 | 687.8 | 599.9 | 837.1 | 682.9
1159 | 952 | 838.6 | 680 | 587.9 | 833.7 | 676.6
1160 | 953 | 835.1 | 674.7 | 576.2 | 831 | 669.4
1161 | 954 | 831.8 | 670.1 | 565.3 | 828.4 | 663.2
1162 | 955 | 828.7 | 661.7 | 555.5 | 825.6 | 658.1
1163 | 956 | 825.2 | 655.5 | 546.2 | 822.5 | 653.3
1164 | 957 | 821.7 | 652.8 | 536.6 | 819.6 | 647.7
1165 | 958 | 818.2 | 651.1 | 526.4 | 816.8 | 651.4
1166 | 959 | 814.7 | 649.8 | 517.2 | 814.5 | 649.7
1167 | 960 | 811.5 | 647.6 | 508.8 | 812.3 | 645.4
1168 | 961 | 808.5 | 644.8 | 501.4 | 810.2 | 640.9
1169 | 962 | 805.4 | 642.2 | 494.4 | 807.7 | 636.7
1170 | 963 | 802 | 640.9 | 486.9 | 805 | 631.7
1171 | 964 | 798.8 | 639.9 | 479.5 | 802.5 | 625.6
1172 | 965 | 795.5 | 638 | 472.4 | 800.3 | 619.5
1173 | 966 | 792.1 | 635.9 | 465.6 | 798 | 613.9
1174 | 967 | 789 | 633.4 | 459.1 | 795.6 | 608.2
1175 | 968 | 786.3 | 630.5 | 453.2 | 793.3 | 602.4
1176 | 969 | 783.7 | 624.9 | 447.5 | 791.2 | 596.9
1177 | 970 | 781.2 | 615.9 | 442.5 | 788.6 | 590.4
1178 | 971 | 778.5 | 609.9 | 437.4 | 785.3 | 582.1
1179 | 972 | 775.5 | 607.3 | 433 | 782 | 573.6
1180 | 973 | 772.4 | 607.8 | 428.5 | 778.9 | 568.1
1181 | 974 | 769.3 | 608 | 424 | 776.1 | 563.9
1182 | 975 | 766.1 | 607.5 | 419.3 | 773.4 | 559.8
1183 | 976 | 763 | 606.8 | 414.6 | 771 | 556.5
1184 | 977 | 760.1 | 605.6 | 409.8 | 768.5 | 553.6
1185 | 978 | 757.3 | 604.4 | 405.3 | 765.9 | 549.7
1186 | 979 | 754.5 | 603.3 | 400.8 | 763 | 544.1
1187 | 980 | 751.6 | 601.4 | 397 | 760.4 | 540.6
1188 | 981 | 748.8 | 599.7 | 393 | 757.8 | 536
1189 | 982 | 746 | 593.7 | 388.7 | 755.2 | 531.4
1190 | 983 | 743.2 | 591.2 | 384.1 | 753.1 | 528.4
1191 | 984 | 740.4 | 590.6 | 379.9 | 751 | 524.7
1192 | 985 | 737.7 | 588.6 | 375.8 | 749.1 | 520.4
1193 | 986 | 734.9 | 587.4 | 372.4 | 747.1 | 517.3
1194 | 987 | 732.4 | 585.6 | 368 | 745.1 | 513.9
1195 | 988 | 729.8 | 585.1 | 364.2 | 743.2 | 510.7
1196 | 989 | 727.3 | 584 | 360.6 | 741.1 | 507.9
1197 | 990 | 724.7 | 581.6 | 357 | 739 | 505.4
1198 | 991 | 722.1 | 580 | 353.8 | 736.9 | 503.4
1199 | 992 | 719.5 | 576.8 | 350.1 | 734.9 | 501.8
1200 | 993 | 716.8 | 573.8 | 346.8 | 732.7 | 500
1201 | 994 | 714.1 | 573.2 | 343.2 | 730.7 | 497.8
1202 | 995 | 711.5 | 572.3 | 339.5 | 728.8 | 495.2
1203 | 996 | 708.9 | 571.5 | 336.2 | 727.1 | 492.4
1204 | 997 | 706.5 | 570.8 | 333 | 725.7 | 488.9
1205 | 998 | 704.2 | 569 | 329.6 | 724.2 | 486
1206 | 999 | 701.9 | 562.6 | 326.9 | 722.7 | 483.2
1207 | 1000 | 699.6 | 555 | 324 | 721.5 | 480.1
1208 | 1001 | 697.3 | 552.1 | 321.2 | 719.9 | 479
1209 | 1002 | 694.8 | 552.3 | 318.1 | 718.1 | 478.6
1210 | 1003 | 692.3 | 549.5 | 314.9 | 716.5 | 477.2
1211 | 1004 | 690 | 548.4 | 311.9 | 715 | 475.1
1212 | 1005 | 688 | 547 | 309.2 | 713.5 | 472.6
1213 | 1006 | 686.1 | 545.2 | 306.9 | 711.8 | 470.1
1214 | 1007 | 683.9 | 533.3 | 304.4 | 709.9 | 467.5
1215 | 1008 | 681.8 | 530.6 | 301.8 | 708.6 | 464.7
1216 | 1009 | 679.7 | 531.9 | 299.5 | 707 | 462.8
1217 | 1010 | 677.5 | 533.1 | 297 | 705.2 | 460.1
1218 | 1011 | 675.3 | 531.2 | 295 | 703.5 | 458.2
1219 | 1012 | 673.2 | 519 | 293.1 | 701.7 | 457.3
1220 | 1013 | 671.1 | 509.8 | 291 | 699.9 | 456
1221 | 1014 | 669 | 512.5 | 288.2 | 697.9 | 453.3
1222 | 1015 | 666.7 | 515 | 285.7 | 696 | 451.5
1223 | 1016 | 664.6 | 517.4 | 283.4 | 694.4 | 450.5
1224 | 1017 | 662.7 | 517.7 | 281.1 | 692.6 | 449.7
1225 | 1018 | 660.7 | 518.2 | 278.4 | 690.9 | 447.7
1226 | 1019 | 658.7 | 518 | 276.2 | 689.2 | 445.5
1227 | 1020 | 656.6 | 518.3 | 274.1 | 687.3 | 444.3
1228 | 1021 | 654.4 | 515.4 | 272.3 | 685.4 | 443.1
1229 | 1022 | 652.5 | 511.1 | 270.6 | 683.6 | 442
1230 | 1023 | 650.7 | 509.4 | 268.8 | 681.8 | 441
1231 | 1024 | 648.8 | 499.6 | 266.8 | 679.9 | 439.3
1232 | 1025 | 646.9 | 494.5 | 264.8 | 678.1 | 438.2
1233 | 1026 | 644.9 | 491.5 | 262.9 | 676.1 | 437.3
1234 | 1027 | 642.9 | 488 | 261 | 674.2 | 436.1
1235 | 1028 | 640.9 | 485.5 | 258.7 | 672.2 | 434.5
1236 | 1029 | 638.9 | 482.7 | 256.3 | 670.4 | 433
1237 | 1030 | 636.8 | 480.3 | 253.5 | 668.6 | 431.6
1238 | 1031 | 634.9 | 482.9 | 250.6 | 666.9 | 430.5
1239 | 1032 | 632.9 | 483.9 | 248.2 | 665.2 | 428.9
1240 | 1033 | 631.1 | 485.6 | 246.5 | 663.5 | 426.1
1241 | 1034 | 629.1 | 484.4 | 244.2 | 661.8 | 423.5
1242 | 1035 | 627.3 | 484.3 | 241.9 | 660.3 | 421.3
1243 | 1036 | 625.6 | 483.4 | 239.7 | 659 | 418.6
1244 | 1037 | 623.7 | 482.9 | 237.4 | 657.5 | 416.3
1245 | 1038 | 621.8 | 485.3 | 235.4 | 656.2 | 414.9
1246 | 1039 | 620.2 | 485.6 | 233.1 | 654.8 | 412.8
1247 | 1040 | 618.4 | 483.4 | 231 | 653.5 | 411
1248 | 1041 | 616.7 | 485.9 | 228.7 | 652.2 | 409.4
1249 | 1042 | 615.1 | 487 | 226.5 | 650.7 | 408.2
1250 | 1043 | 613.6 | 486.4 | 224.6 | 649.7 | 406.9
1251 | 1044 | 612.3 | 480.9 | 222.9 | 648.7 | 405.7
1252 | 1045 | 611 | 480.5 | 221 | 647.4 | 404.4
1253 | 1046 | 609.5 | 480.3 | 218.8 | 646.2 | 402.8
1254 | 1047 | 607.9 | 479.8 | 216.8 | 644.8 | 400.8
1255 | 1048 | 606.4 | 476.9 | 215 | 643.5 | 399.3
1256 | 1049 | 605.1 | 476.8 | 213.1 | 642.3 | 397.7
1257 | 1050 | 603.7 | 475.3 | 211.6 | 641.1 | 396
1258 | 1051 | 602.3 | 476.5 | 209.5 | 640 | 394.2
1259 | 1052 | 601.1 | 476.1 | 207.9 | 638.9 | 393
1260 | 1053 | 599.9 | 474 | 206.4 | 637.8 | 392.1
1261 | 1054 | 598.7 | 471.3 | 205.2 | 636.5 | 389.7
1262 | 1055 | 597.2 | 471.4 | 204.6 | 635.1 | 386.7
1263 | 1056 | 595.9 | 469.9 | 204.4 | 633.7 | 383.9
1264 | 1057 | 594.5 | 466.5 | 203 | 632.4 | 380.1
1265 | 1058 | 592.8 | 466.8 | 201.4 | 631 | 377.7
1266 | 1059 | 591 | 465.5 | 199.8 | 629.6 | 376.3
1267 | 1060 | 589.4 | 463.6 | 198.1 | 628.3 | 375.4
1268 | 1061 | 587.9 | 463.5 | 196.5 | 627 | 374.1
1269 | 1062 | 586.5 | 465.1 | 195.4 | 625.7 | 372.9
1270 | 1063 | 585.1 | 466.3 | 194.1 | 624.5 | 370.8
1271 | 1064 | 583.4 | 465.7 | 192.6 | 623.2 | 369.5
1272 | 1065 | 581.9 | 464.8 | 191 | 621.9 | 368.2
1273 | 1066 | 580.6 | 464.5 | 189.6 | 620.9 | 367.2
1274 | 1067 | 579.3 | 456.4 | 188.2 | 619.8 | 365.8
1275 | 1068 | 578.1 | 446.9 | 186.9 | 618.6 | 364.7
1276 | 1069 | 576.7 | 447.2 | 185.6 | 617.3 | 364.2
1277 | 1070 | 575.5 | 447.4 | 184.3 | 615.9 | 362.1
1278 | 1071 | 574.4 | 441.2 | 182.8 | 614.5 | 359.8
1279 | 1072 | 573 | 433.1 | 181.5 | 613.1 | 357.3
1280 | 1073 | 571.5 | 434.1 | 180.5 | 611.6 | 356.2
1281 | 1074 | 570.1 | 435.1 | 179.4 | 610.3 | 354.7
1282 | 1075 | 568.8 | 429.3 | 178.1 | 608.7 | 353.3
1283 | 1076 | 567.4 | 425.6 | 176.9 | 607.1 | 351.5
1284 | 1077 | 565.7 | 425.8 | 175.7 | 605.5 | 349
1285 | 1078 | 563.9 | 427.7 | 174.5 | 604 | 348
1286 | 1079 | 562.5 | 429.4 | 173.5 | 602.9 | 346.2
1287 | 1080 | 561.1 | 430.4 | 172.9 | 601.6 | 344.8
1288 | 1081 | 559.5 | 432.1 | 171.8 | 600.1 | 343.4
1289 | 1082 | 558.3 | 432.4 | 171.1 | 598.8 | 341.8
1290 | 1083 | 556.9 | 431.5 | 170.2 | 597.4 | 340.2
1291 | 1084 | 555.3 | 432.4 | 169.3 | 596 | 338.8
1292 | 1085 | 553.8 | 432.5 | 168.5 | 594.6 | 337.2
1293 | 1086 | 552.3 | 433.7 | 167.6 | 593.2 | 336.9
1294 | 1087 | 551.1 | 434.2 | 167 | 592.1 | 337.2
1295 | 1088 | 549.8 | 433.3 | 166.4 | 590.9 | 337.7
1296 | 1089 | 548.5 | 432.6 | 165.5 | 589.4 | 337.5
1297 | 1090 | 547.3 | 426.5 | 164.7 | 588.3 | 336.1
1298 | 1091 | 546 | 421.4 | 164 | 587.2 | 334.8
1299 | 1092 | 544.5 | 422.1 | 163.3 | 586.1 | 334.2
1300 | 1093 | 542.9 | 424.5 | 163 | 584.6 | 333.6
1301 | 1094 | 541.5 | 425.3 | 162.4 | 583.4 | 332.9
1302 | 1095 | 540.1 | 425.5 | 161.6 | 582.4 | 331.8
1303 | 1096 | 539 | 424.6 | 160.9 | 581 | 330.4
1304 | 1097 | 537.9 | 424.4 | 160 | 579.8 | 327.6
1305 | 1098 | 536.7 | 422.3 | 159.1 | 578.6 | 325.7
1306 | 1099 | 535.4 | 420.5 | 158.3 | 577.4 | 324.9
1307 | 1100 | 534.3 | 418 | 157.5 | 576.2 | 323.7
1308 | 1101 | 533.1 | 418.1 | 156.6 | 575 | 322.4
1309 | 1102 | 532.1 | 418.5 | 155.8 | 573.8 | 321.6
1310 | 1103 | 531.1 | 417.3 | 154.8 | 572.6 | 320.4
1311 | 1104 | 530.1 | 411.7 | 153.8 | 571.4 | 318
1312 | 1105 | 528.6 | 409.1 | 153 | 570.1 | 316.7
1313 | 1106 | 527.3 | 411.8 | 152.1 | 568.8 | 316.6
1314 | 1107 | 526.4 | 412.9 | 151.2 | 567.5 | 316.4
1315 | 1108 | 525.5 | 411.3 | 150.5 | 566.4 | 315.8
1316 | 1109 | 524.5 | 408.5 | 149.8 | 565.1 | 315.6
1317 | 1110 | 523.3 | 408.6 | 148.9 | 563.8 | 314.9
1318 | 1111 | 522.1 | 407.5 | 148 | 562.5 | 313.8
1319 | 1112 | 520.7 | 402.1 | 147.3 | 561.1 | 312.3
1320 | 1113 | 519.7 | 401.9 | 146.4 | 559.9 | 310.9
1321 | 1114 | 518.6 | 397.7 | 145.4 | 558.7 | 308.7
1322 | 1115 | 517.5 | 392.6 | 144.5 | 557.5 | 307.2
1323 | 1116 | 516.1 | 392.8 | 143.7 | 556.2 | 306.3
1324 | 1117 | 514.6 | 394.2 | 142.9 | 554.9 | 305.6
1325 | 1118 | 513.2 | 394 | 141.9 | 553.5 | 304.7
1326 | 1119 | 511.8 | 390.3 | 140.9 | 552.3 | 303.9
1327 | 1120 | 510.5 | 392.9 | 140 | 551.1 | 303.4

## Test Facts
Last row in IRMS data sheets: | 35
Time when gas burner was ignited: | 207