## IS Test Matrix
Intermediate Scale Test Matrix - Revision F (12-06-06)
|  | Comments: 1) All tests were conducted as open burns with a Propene (Propylene) gas sand burner 2) Colors identify test conditions grouped into the same test run | [14 empty] | ACTUAL TEST CONDITIONS
Burn Test # | Rev. E Test # | Loc. | Cable Insulation Material | [8 empty] | Number of Conductors |  |  |  | Conductor Size (AWG) |  |  |  |  | Cable Bundle Size |  |  |  |  | Water Spary Optionsl | Raceway Type
|  |  | Thermoset | [5 empty] | Thermoplastic
|  |  | XLPE | EPR | Silicone | XLPO | TS/TP | Vita-Link | PE | PVC | Tefzel | 3 | 2 | 7 | 12 | 8 | 12 | 14 | 16 | 18 | 1 | 3 | 6 | 12 | Load Tr | * | 12" Tray | 2.5" Cnd | Air Drop
Prelim 1 | Prelim 1 | A | X | [8 empty] | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | A | X | [10 empty] | X |  |  | X |  |  |  | X | [5 empty] | X
Prelim 2 | Prelim 2 | A | X | [8 empty] | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | A | X | [10 empty] | X |  |  | X |  |  |  | X | [5 empty] | X
Prelim 3 | Prelim 3 | A | [7 empty] | X |  | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | A | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [5 empty] | X
Prelim 4 | Prelim 4 | A | [7 empty] | X |  | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | A | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [5 empty] | X
1 | 15 | A | X | [9 empty] | X | X | X |  | X |  | X | X |  |  |  |  | X |  | X
|  | B | X | [10 empty] | X |  |  | X | [6 empty] | X |  |  | X
|  | D | X | [10 empty] | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | E | X | [10 empty] | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | [10 empty] | X |  |  | X | [6 empty] | X |  |  | X
2 | 1 | A | X | [10 empty] | X |  |  | X | [6 empty] | X |  |  | X
|  | C | X | [10 empty] | X |  |  | X | [5 empty] | X |  |  |  | X
|  | A | X | [5 empty] | X |  |  |  |  | X |  |  | X | [6 empty] | X |  |  | X
|  | C | X | [5 empty] | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
| 11 | C - A | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [7 empty] | X
|  | E | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [5 empty] | X
|  | G | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [5 empty] | X
3 | 2 | A | X | X | [9 empty] | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X | [9 empty] | X |  |  | X | [5 empty] | X |  |  |  | X
| 3 | A |  | X |  |  |  |  | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C |  | X |  |  |  |  | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
| 10 | E | [7 empty] | X |  | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | [7 empty] | X |  | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
4 | 5 | A | X | X |  | X | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X |  | X | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
| 6 | A | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
| 9 | C - A | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [7 empty] | X
|  | E | X | [8 empty] | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | [8 empty] | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
5 | 4 | A | X | X | X | X |  |  | X |  | X |  |  | X |  |  | X | [6 empty] | X |  | X | X
|  | C | X | X | X | X |  |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
| 7 | A | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | X | [5 empty] | X |  | X | X
|  | C | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | X |  |  |  |  | X |  |  | X | X
|  | C - A | X | [10 empty] | X |  |  | X |  |  |  | X | [7 empty] | X
|  | E |  | X | [9 empty] | X |  |  | X |  |  |  | X | [5 empty] | X
|  | G |  | X | [9 empty] | X |  |  | X |  |  |  | X | [5 empty] | X
6 | 12 | A | X | X | X | X |  |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | C | X | X | X | X |  |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | E | X | [5 empty] | X |  | X |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
| 13 | C - A | X | [5 empty] | X |  | X |  |  | X |  |  | X |  |  |  |  | X | [6 empty] | X
|  | A |  | X | X | X | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | C |  | X | X | X | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | G |  |  |  |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  |  |  | X
7 | 14 | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | A | X | X |  | X | X |  |  | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C |  | X |  | X | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | E | X | [5 empty] | X | X |  |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G |  | X |  | X | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
8 | 16 | A | X | [5 empty] | X | X |  |  | X | X | X |  | X |  | X | X |  |  | X |  |  |  | X
|  | A | X | [5 empty] | X | X |  |  | X | X | X |  | X |  | X | X |  |  | X |  |  |  | X
|  | C | X | [5 empty] | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | E | X | [5 empty] | X |  |  |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | [5 empty] | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
9 | 19 | A | X | X | X |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | A | X | X | X |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | C | X | X | X |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | E | X | [5 empty] | X |  | X |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | X | X |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
10 | 20 | A | X | X | X | X | X |  |  |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | A | X | X | X | X | X |  |  |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | C | X | X | X | X | X |  |  | X |  |  |  | X | X |  | X |  |  | X |  |  | X |  |  | X | X
|  | E |  |  |  |  | X |  | X |  | X |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | X |  |  | X |  | X | X | X |  | X | X |  |  | X |  | X |  |  |  | X |  |  |  | X
11 | 21 | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X |  | X | X |  |  | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | E |  |  |  |  | X |  | X | X |  |  |  | X |  |  | X |  |  |  |  | X | [6 empty] | X
|  | G | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
12 | 24 | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X |  | X | X |  |  | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | E |  |  |  |  | X |  | X | X |  |  |  | X |  |  | X |  |  |  |  | X | [6 empty] | X
|  | G | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
13 | 25 | A | X | X |  | X | X | X | X |  | X |  |  | X |  |  | X | [7 empty] | X | X | X
|  | C | X | X |  | X | X | X | X |  | X |  |  | X |  |  | X | [7 empty] | X | X | X
|  | E | X | X | [9 empty] | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | F | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | F | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | G | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | G | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
14 | 27 | A | X | X |  | X | X |  | X | X | X |  |  | X |  |  | X | [7 empty] | X |  | X
|  | C | X | X |  | X | X |  | X | X | X |  |  | X |  |  | X | [7 empty] | X |  | X
|  | E |  |  |  |  | X |  | X | X |  |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | F | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | F | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | G | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | G | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X

## Shorting Summary
Shorting Sequence for Open Burn Test 12, Location A, IRMS #1
Test conditions: Cable: Bundle of 6, 7-conductor, 12 AWG, XLPE, EPR, PE, PVC, TS/TP & XLPO control cables (Items 10, 2, 15, 1, 3 & 8). Cable specimens present: Three lengths of cable were monitored for electrical performance (A, B & C [See Elect. Conn. Map]), a second bundle of 6 cables was monitored for temperature response. Raceway: 12" B-Line Series 2 tray (part number 248P09-12-144) located at position A in the Test Cell chamber with chamber end walls open and un-heated. Exposure conditions: Initial gas burner flow rate set to a nominal 250 kW heat release rate and increased to 300 kW during the test run. Electrical repsonse monitoring: IRMS system using 6 channels - two for each cable (see electrical connection map), cable tray was grounded. Thermal response monitoring: Two cable bundle temperatures (see thermocouple map), air temperatures above and below the cable bundle, and the cable tray rung temperature. Gas burner initiated: Following 190 seconds of baseline data monitoring. Special Note: This test run was intended to be a repeat of Test #11
DAQ Time | Burner Time | Event | Interpretation
190 | 0 | Ignited Gas Burner
320 | 130 | Conductor C5 shorts to ground at less than 1000 ohms (463)
362 | 172 | The existing ground fault on conductor C5 decreases to less than 100 ohms (80)
364 | 174 | Conductor C6 shorts to ground at less than 100 ohms (88) | Cable C shorted to ground
376 | 186 | Conductors C5 & C6 short together at less than 100 ohms (63) | Cable C shorts internally
463 | 273 | Conductors A1 & A2 short together at less than 1000 ohms (110) | Cable A shorts internally
468-477 | 278-287 | Conductors A1 & A2 both short to ground at less than 100 ohms (79 & 17) | Cable A shorted to ground
483-486 | 293-296 | Conductors B3 & B4 both short to ground (799 & 20) | Cable B shorted to ground
488 | 298 | Conductors B3 & B4 short together at less than 100 ohms (76) | Cable B shorts internally
505 | 315 | The existing internal fault between conductors A1 & A2 decreases to less than 100 ohms (69)
524 | 334 | The existing ground fault on conductor B3 decreases to less than 100 ohms (17)
1323 | 1133 | Extinguished Gas Burner
Additional Observations
Observation 1 | There was no evidence of cable-to-cable interactions prior to internal cable shorting or shorting to ground.

## Thermocouple Map
Thermocouple map for TC's on and within the cable
|  |  |  | Cable A = | XLPE | (Item #10)
|  |  |  | Cable B = | EPR | (Item #2)
|  |  |  | Cable C = | PE | (Item #15)
|  |  |  | Cable D = | PVC | (Item #1)
|  |  |  | Cable E = | TS/TP | (Item #3)
|  |  |  | Cable F = | XLPO | (Item #8)
Translation to data file names used in "Temperatures" WorkSheet:
| Map Name |  | Location
| A1 | = | Center of bundle, under jacket
| A2 | = | Air above bundle
| A3 | = | Air below bundle
| A4 | = | Intra-bundle, center

## Elect Conn Map
Electrical connection map within the cables
|  |  |  | Cable A = | XLPE | (Item #10)
|  |  |  | Cable B = | EPR | (Item #2)
|  |  |  | Cable C = | PE | (Item #15)
Tray rung under D-E-F
Cable Bundle Arrangement
Cable 7-Conductor Arrangement
| Lt Blue = | Even conductor set
| Lt Red = | Odd conductor set
| Gray = | Center conductor (not connected)
IRMS Electrical Connections

## C-C Individuals
Conductor to Conductor Resistances
Open Burn Test 12 |  |  | 2006-11-22 | 13:02
Mixed | 7-C | Tray A | IRMS | 1
0 | 250 kW
Burner Time | A1-A2 | Burner Time | A1-B3 | Burner Time | A1-B4 | Burner Time | A1-C5 | Burner Time | A1-C6 | Burner Time | A2-B3 | Burner Time | A2-B4 | Burner Time | A2-C5 | Burner Time | A2-C6 | Burner Time | B3-B4 | Burner Time | B3-C5 | Burner Time | B3-C6 | Burner Time | B4-C5 | Burner Time | B4-C6 | Burner Time | C5-C6
-189.5 | 265337.9994 | -187 | 264437.9994 | -184 | 264537.9994 | -181.5 | 266737.9994 | -178.5 | 264037.9994 | -175.5 | 262237.9994 | -173 | 265837.9994 | -170 | 267137.9994 | -167.5 | 266837.9994 | -164.5 | 262437.9994 | -161.5 | 266937.9994 | -159 | 265037.9994 | -156 | 266937.9994 | -153.5 | 265137.9994 | -150.5 | 266237.9994
-147.5 | 265337.9994 | -145 | 264437.9994 | -142 | 264537.9994 | -139.5 | 266737.9994 | -136.5 | 264037.9994 | -133.5 | 262237.9994 | -131 | 265837.9994 | -128 | 267137.9994 | -125.5 | 266837.9994 | -122.5 | 262437.9994 | -119.5 | 266937.9994 | -117 | 265037.9994 | -114 | 266937.9994 | -111.5 | 265137.9994 | -108.5 | 266237.9994
-105.5 | 265337.9994 | -103 | 264437.9994 | -100 | 264537.9994 | -97.5 | 266737.9994 | -94.5 | 264037.9994 | -91.5 | 262237.9994 | -89 | 265837.9994 | -86 | 267137.9994 | -83.5 | 266837.9994 | -80.5 | 262437.9994 | -77.5 | 266937.9994 | -75 | 265037.9994 | -72 | 266937.9994 | -69.5 | 265137.9994 | -66.5 | 266237.9994
-63.5 | 265337.9994 | -61 | 264437.9994 | -58 | 264537.9994 | -55.5 | 266737.9994 | -52.5 | 264037.9994 | -49.5 | 262237.9994 | -47 | 265837.9994 | -44 | 267137.9994 | -41.5 | 266837.9994 | -38.5 | 262437.9994 | -35.5 | 266937.9994 | -33 | 265037.9994 | -30 | 266937.9994 | -27.5 | 265137.9994 | -24.5 | 266237.9994
-21.5 | 265337.9994 | -19 | 264437.9994 | -17 | 264537.9994 | -13.5 | 266737.9994 | -10.5 | 264037.9994 | -7.5 | 262237.9994 | -5 | 265837.9994 | -2 | 267137.9994 | 0.5 | 266837.9994 | 3.5 | 262437.9994 | 6.5 | 266937.9994 | 9 | 265037.9994 | 12 | 266937.9994 | 14.5 | 265137.9994 | 17.5 | 266237.9994
20.5 | 265337.9994 | 23 | 264437.9994 | 26 | 264537.9994 | 28.5 | 266737.9994 | 31.5 | 264037.9994 | 34.5 | 262237.9994 | 37 | 265837.9994 | 40 | 267137.9994 | 42.5 | 266837.9994 | 45.5 | 262437.9994 | 48.5 | 266937.9994 | 51 | 265037.9994 | 54 | 266937.9994 | 56.5 | 265137.9994 | 59.5 | 266237.9994
62.5 | 265337.9994 | 65 | 264437.9994 | 68 | 264537.9994 | 70.5 | 266737.9994 | 73.5 | 264037.9994 | 76.5 | 262237.9994 | 79 | 265837.9994 | 82 | 267137.9994 | 84.5 | 266837.9994 | 87.5 | 262437.9994 | 90.5 | 266937.9994 | 93 | 265037.9994 | 96 | 266937.9994 | 98.5 | 265137.9994 | 101.5 | 266237.9994
104.5 | 265337.9994 | 107 | 264437.9994 | 110 | 264537.9994 | 112.5 | 266737.9994 | 115.5 | 264037.9994 | 118.5 | 262237.9994 | 121 | 265837.9994 | 124 | 267137.9994 | 126.5 | 266837.9994 | 129.5 | 262437.9994 | 132.5 | 266937.9994 | 135 | 265037.9994 | 138 | 266937.9994 | 140.5 | 265137.9994 | 143.5 | 218755.8345
146.5 | 265337.9994 | 149 | 264437.9994 | 152 | 264537.9994 | 154.5 | 266737.9994 | 157.5 | 264037.9994 | 160.5 | 262237.9994 | 163 | 265837.9994 | 165 | 267137.9994 | 168.5 | 266837.9994 | 171.5 | 262437.9994 | 174.5 | 266937.9994 | 177 | 265037.9994 | 179 | 266937.9994 | 182.5 | 265137.9994 | 185.5 | 63.1122
188.5 | 265337.9994 | 191 | 264437.9994 | 194 | 264537.9994 | 196.5 | 266737.9994 | 199.5 | 264037.9994 | 202.5 | 262237.9994 | 205 | 265837.9994 | 208 | 267137.9994 | 210.5 | 266837.9994 | 213.5 | 262437.9994 | 216.5 | 266937.9994 | 219 | 265037.9994 | 222 | 266937.9994 | 224.5 | 265137.9994 | 227.5 | 609.3982
230.5 | 132618.9988 | 233 | 264437.9994 | 236 | 264537.9994 | 238.5 | 266737.9994 | 241.5 | 131968.9988 | 244.5 | 65484.4976 | 247 | 26493.7939 | 250 | 2164.6568 | 252.5 | 1527.5706 | 255.5 | 262437.9994 | 258.5 | 266937.9994 | 261 | 132468.9988 | 264 | 2419.1617 | 266.5 | 132518.9988 | 269.5 | 0.25364
272.5 | 110.2052 | 275 | 129142.4319 | 278 | 147600.0909 | 280.5 | 115.1338 | 283.5 | 77.8108 | 286.5 | 85772.5592 | 289 | 43.8051 | 292 | 15.5064 | 294.5 | 17.9629 | 297.5 | 76.0671 | 300.5 | 798.9365 | 303 | 5925.8368 | 306 | 17702.5242 | 308.5 | 52947.5969 | 311.5 | 5.8364
314.5 | 69.2568 | 317 | 32.6692 | 320 | 23.2382 | 322.5 | 24.3332 | 325.5 | 37.6391 | 328 | 39.2217 | 331 | 15.559 | 334 | 18.043 | 336.5 | 9.5715 | 339.5 | 83.4717 | 342.5 | 72.6878 | 345 | 89.3484 | 348 | 54.2046 | 350.5 | 59.4494 | 353.5 | 3.8119
356.5 | 11720.5805 | 359 | 5.9454 | 362 | 2.1403 | 364.5 | 3.5037 | 367.5 | 31.5851 | 370.5 | 12.4554 | 373 | 27.712 | 376 | 21.6545 | 378.5 | 4.0916 | 381.5 | 86.696 | 384.5 | 19.0418 | 387 | 49.486 | 389.5 | 17.0437 | 392.5 | 43.0278 | 395.5 | 0.72612
398.5 | 0.14657 | 401 | 18.791 | 403.5 | 21.6593 | 406.5 | 10.9508 | 409.5 | 9.9561 | 412.5 | 5.7586 | 415 | 0.17973 | 418 | 24.8215 | 420.5 | 5.8588 | 423.5 | 20.6954 | 426 | 35.1175 | 429 | 62.6764 | 432 | 32.5004 | 434.5 | 45.9264 | 437.5 | 14.1407
440.5 | 17.3997 | 443 | 3.0159 | 446 | 11.6646 | 448.5 | 14.4085 | 451.5 | 7.762 | 454.5 | 9.9584 | 457 | 11.8769 | 459.5 | 20.6332 | 462.5 | 27.378 | 466 | 28.3475 | 468.5 | 7.0055 | 471 | 4.443 | 473.5 | 23.0665 | 476.5 | 6.3185 | 479.5 | 25.1199
482.5 | 0.14657 | 485 | 0.31668 | 488 | 0.9828 | 490.5 | 0.20758 | 493.5 | 6.6738 | 496.5 | 10.4879 | 499 | 9.0623 | 502 | 1.5995 | 504.5 | 0.14747 | 507.5 | 17.9375 | 510.5 | 18.1156 | 513 | 3.7598 | 516 | 4.5144 | 518.5 | 15.8248 | 521.5 | 22.6821
524.5 | 26.7798 | 527 | 11.6219 | 530 | 0.99778 | 532.5 | 16.6373 | 535.5 | 6.8087 | 538.5 | 4.4842 | 541 | 7.9104 | 544 | 26.8368 | 546.5 | 0.49884 | 549.5 | 2105.821 | 552.5 | 26.1854 | 555 | 6.9932 | 557.5 | 20.8802 | 560.5 | 15.4591 | 563.5 | 24.878
566.5 | 8.9941 | 569 | 14.7882 | 572 | 26.7056 | 574.5 | 19.3368 | 577.5 | 2.3576 | 580.5 | 20.5905 | 583 | 26.0902 | 585.5 | 29.6241 | 588.5 | 13.7939 | 591.5 | 11.2058 | 594 | 18.4953 | 597 | 25.2175 | 600 | 12.7891 | 602.5 | 16.2455 | 605.5 | 21.8707
608 | 1.3484 | 611 | 16.9971 | 613.5 | 0.16006 | 616.5 | 16.5318 | 619.5 | 0.40259 | 622.5 | 3.9224 | 625 | 17.1407 | 627.5 | 29.0443 | 630.5 | 8.8738 | 633.5 | 13312.1141 | 636 | 45.6131 | 639 | 23.8305 | 642 | 40.2115 | 644.5 | 37.1179 | 647.5 | 16.9988
650 | 7.7958 | 653 | 4.6335 | 655.5 | 21.5438 | 658.5 | 4.4777 | 661.5 | 23.3585 | 664.5 | 1.6083 | 667 | 20.2643 | 670 | 0.55813 | 672.5 | 17.2655 | 675.5 | 34.8929 | 678 | 13.636 | 681 | 38.9067 | 683.5 | 47.0069 | 686.5 | 49.1132 | 689.5 | 10.2635
692.5 | 21.397 | 695 | 24.8705 | 697.5 | 5.0206 | 700.5 | 8.2348 | 703.5 | 22.4732 | 706 | 8.0736 | 709 | 22.7878 | 712 | 3.2842 | 714.5 | 25.344 | 717.5 | 14.8949 | 720 | 36.5357 | 723 | 19.1742 | 725.5 | 44.006 | 728.5 | 52.1714 | 731.5 | 1.3731
734 | 18.0482 | 737 | 11.9653 | 740 | 11.1772 | 742.5 | 27.3925 | 745.5 | 10.2903 | 748 | 13.7708 | 751 | 17.1407 | 753.5 | 3.4933 | 756.5 | 19.1065 | 759.5 | 12.7428 | 762 | 29.3325 | 765 | 13.9748 | 767.5 | 2.3779 | 770.5 | 21.707 | 773.5 | 4.8794
776.5 | 21.2252 | 779 | 0.98196 | 781.5 | 1.6068 | 784.5 | 13.9524 | 787.5 | 1.1679 | 790 | 11.7097 | 793 | 10.6196 | 796 | 17.2921 | 798.5 | 29.6065 | 801.5 | 1.5635 | 804.5 | 7.4994 | 807 | 7.5813 | 809.5 | 7.095 | 812.5 | 25.9396 | 815.5 | 0.89042
818 | 14.6676 | 821 | 24.6884 | 823.5 | 17.7967 | 826.5 | 24.393 | 829.5 | 6.6289 | 832 | 1.0757 | 835 | 0.057091 | 837.5 | 0.50194 | 840.5 | 13.5929 | 843.5 | 0.96497 | 846 | 21.5053 | 849 | 13.6201 | 852 | 5.724 | 854.5 | 18.9984 | 857.5 | 0.33642
860 | 0.20868 | 863 | 20.4687 | 865.5 | 26.5184 | 868.5 | 7.5531 | 871.5 | 20.625 | 874 | 0.96327 | 877 | 2.8573 | 879.5 | 20.1287 | 882.5 | 20.4963 | 886 | 0.25491 | 888.5 | 3.2474 | 891 | 0.11076 | 893.5 | 7.8613 | 896.5 | 16.14 | 899.5 | 0.80371
902 | 20.4297 | 905 | 13.5618 | 907.5 | 26.956 | 910.5 | 6.568 | 913.5 | 26.2148 | 916 | 0.18641 | 919 | 13.0123 | 922 | 19.7947 | 924.5 | 18.3417 | 927.5 | 0.46494 | 930.5 | 0.95941 | 933 | 0.086971 | 935.5 | 28.6909 | 938.5 | 6.8992 | 941.5 | 0.99718
944 | 22.4378 | 947 | 10.941 | 949.5 | 28.2228 | 952.5 | 10.5208 | 955.5 | 19.8895 | 958 | 10.6332 | 961 | 7.2754 | 963.5 | 29.8185 | 966.5 | 7.0543 | 969.5 | 23.1374 | 972 | 2.2548 | 975 | 18.5679 | 977.5 | 2.7902 | 980.5 | 1.2303 | 983.5 | 10.2635
986 | 11.1779 | 989 | 28.4943 | 991.5 | 9.1743 | 994.5 | 28.4025 | 997.5 | 4.2148 | 1000 | 2.313 | 1003 | 4.419 | 1005.5 | 29.7536 | 1008.5 | 29.5418 | 1011.5 | 1.0724 | 1014 | 5.3323 | 1017 | 1.8836 | 1019.5 | 22.4838 | 1022.5 | 3.2506 | 1025.5 | 5.9682
1028 | 1.7143 | 1031 | 23.4878 | 1033.5 | 10.9834 | 1036.5 | 0.22462 | 1039.5 | 14.9745 | 1042.5 | 9.0553 | 1045 | 0.021731 | 1047.5 | 0.95623 | 1050.5 | 0.52274 | 1053.5 | 0.96497 | 1056.5 | 24.7872 | 1059 | 28.5315 | 1061.5 | 13.5357 | 1064.5 | 26.4344 | 1067.5 | 15.5268
1070 | 0.98958 | 1073 | 17.6433 | 1075.5 | 22.8251 | 1078.5 | 18.5688 | 1081.5 | 5.5184 | 1084 | 13.6686 | 1087 | 6.4695 | 1089.5 | 28.8522 | 1092.5 | 22.2637 | 1095.5 | 7.4198 | 1098 | 28.1821 | 1101 | 9.4303 | 1103.5 | 21.7342 | 1106.5 | 2.9991 | 1109.5 | 27.2765
1112 | 23.972 | 1115 | 10.5555 | 1117.5 | 2.0579 | 1120.5 | 10.0468 | 1123.5 | 0.97856 | 1126 | 25.9039 | 1129 | 29.1809 | 1131.5 | 24.8817 | 1134.5 | 24.2012 | 1137.5 | 26.9998 | 1140 | 61.1305 | 1143 | 46.2 | 1145.5 | 8.8227 | 1148.5 | 10.7075 | 1151.5 | 2.1464
1154 | 19.1997 | 1157 | 21.0381 | 1159.5 | 18.6711 | 1162.5 | 20.4506 | 1165.5 | 10.3382 | 1168 | 1.1981 | 1171 | 14.1194 | 1173.5 | 10.8319 | 1176.5 | 0.36428 | 1179.5 | 7.5573 | 1182 | 25.3308 | 1185 | 30.4179 | 1187.5 | 21.5053 | 1190.5 | 5.0445 | 1193.5 | 10.4537
1196 | 1.7551 | 1199 | 3.7336 | 1201.5 | 14.7289 | 1204.5 | 28.0852 | 1207.5 | 24.3771 | 1210 | 0.5484 | 1213 | 0.6167 | 1215.5 | 2.0055 | 1218.5 | 26.5691 | 1221.5 | 4.8264 | 1224 | 9.3328 | 1227 | 8.0837 | 1229.5 | 20.3174 | 1232.5 | 22.2863 | 1235.5 | 28.4778
1238 | 9.9807 | 1241 | 25.2973 | 1243.5 | 10.8385 | 1246.5 | 14.4085 | 1249.5 | 13.5396 | 1252 | 27.8628 | 1255 | 5.2823 | 1257.5 | 28.5332 | 1260.5 | 22.4954 | 1263.5 | 1504.2536 | 1266 | 8.7765 | 1269 | 63.084 | 1271.5 | 48.5114 | 1274.5 | 60.8286 | 1277.5 | 2.7235
1280 | 100.3585 | 1283 | 26.0355 | 1285.5 | 26.4561 | 1288.5 | 17.1677 | 1291.5 | 22.8259 | 1294 | 23.5207 | 1297 | 28.0921 | 1299.5 | 2077.8882 | 1302.5 | 1030.5001 | 1305.5 | 31.8155 | 1308 | 18.3323 | 1311 | 36.4867 | 1313.5 | 34.2802 | 1316.5 | 33.5049 | 1319.5 | 65.5498
1322 | 48.3186 | 1325 | 87.1567 | 1327.5 | 143.6952 | 1330.5 | 74.563 | 1333.5 | 84.9563 | 1336 | 183.3515 | 1339 | 241.3477 | 1341.5 | 56.0021 | 1344.5 | 55.5612 | 1347.5 | 93.1766 | 1350 | 56.1364 | 1353 | 71.5652 | 1355.5 | 79.7729 | 1358.5 | 104.3444 | 1361.5 | 22.9742
1364 | 47.3321 | 1367 | 122.5154 | 1369.5 | 70.7906 | 1372.5 | 142.6826 | 1375.5 | 83.1656 | 1378 | 88.9812 | 1381 | 61.9559 | 1383.5 | 88.9296 | 1386.5 | 141.034 | 1389.5 | 170.5374 | 1392 | 6.7379 | 1395 | 5.1783 | 1397.5 | 109.159 | 1400.5 | 80.5288 | 1403.5 | 43.4118
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!

## C-G Min
Average Conductor to Ground Resistances
Open Burn Test 12 |  |  | 2006-11-22 | 13:02
Mixed | 7-C | Tray A | IRMS | 1
0 | 250 kW
Burner Time | A1-G |  | Burner Time | A2-G | Burner Time | B3-G | Burner Time | B4-G | Burner Time | C5-G | Burner Time | C6-G
-184.1 | 264038 |  | -175.1 | 262238 | -169.5 | 262238 | -166.2 | 262438 | -163.9 | 266238 | -161.8 | 133069
-142.1 | 264038 |  | -133.1 | 262238 | -127.5 | 262238 | -124.2 | 262438 | -121.9 | 266238 | -119.8 | 264038
-100.1 | 264038 |  | -91.1 | 262238 | -85.5 | 262238 | -82.2 | 262438 | -79.9 | 266238 | -77.8 | 264038
-58.1 | 264038 |  | -49.1 | 262238 | -43.5 | 262238 | -40.2 | 262438 | -37.9 | 266238 | -35.8 | 264038
-16.3 | 264038 |  | -7.1 | 262238 | -1.5 | 262238 | 1.6 | 262438 | 4.1 | 266238 | 6.2 | 264038
25.9 | 264038 |  | 34.9 | 262238 | 40.5 | 262238 | 43.8 | 262438 | 46.1 | 266238 | 48.2 | 264038
67.9 | 264038 |  | 76.9 | 262238 | 82.5 | 262238 | 85.8 | 262438 | 88.1 | 266238 | 90.2 | 264038
109.9 | 264038 |  | 118.9 | 262238 | 124.5 | 262238 | 127.8 | 262438 | 130.1 | 462.8714 | 132.2 | 264038
151.9 | 264038 |  | 160.7 | 262238 | 166.5 | 262238 | 169.6 | 262438 | 171.7 | 80.2959 | 174.2 | 87.8456
193.9 | 264038 |  | 202.9 | 262238 | 208.5 | 262238 | 211.8 | 262438 | 214.1 | 15.7512 | 216.2 | 21.0603
235.9 | 131969 |  | 244.9 | 1527.6707 | 250.5 | 132469 | 253.8 | 1444.3412 | 256.1 | 1.8501 | 258.2 | 7.075
277.9 | 78.7131 |  | 286.9 | 16.902 | 292.5 | 799.1178 | 295.8 | 19.6841 | 298.1 | 4.1116 | 300.2 | 13.6955
319.9 | 24.5355 |  | 328.8 | 11.0391 | 334.4 | 17.1961 | 337.8 | 30.7463 | 340.1 | 5.3552 | 342.2 | 3.6652
361.9 | 3.6983 |  | 370.9 | 5.6343 | 376.5 | 19.5162 | 379.7 | 16.632 | 382 | 0.88561 | 384.2 | 0.8836
403.8 | 1.7394 |  | 412.9 | 1.775 | 418.4 | 36.3134 | 421.7 | 22.9487 | 424 | 7.6766 | 426.2 | 1.3965
445.9 | 4.5605 |  | 454.8 | 11.3962 | 460.6 | 2.276 | 463.8 | 3.1167 | 465.9 | 0.65511 | 468.2 | 9.3286
487.9 | 0.62281 |  | 496.9 | 1.4588 | 502.5 | 5.2971 | 505.8 | 5.7828 | 508.1 | 0.61718 | 510.2 | 2.0547
529.9 | 2.5729 |  | 538.9 | 1.1129 | 544.5 | 6.1238 | 547.7 | 1.5806 | 550 | 16.1399 | 552.2 | 5.0864
571.9 | 3.9095 |  | 580.8 | 15.2085 | 586.4 | 2.8776 | 589.8 | 4.5968 | 591.9 | 0.73104 | 594.2 | 0.61741
613.7 | 1.4327 |  | 622.7 | 5.4413 | 628.4 | 11.3844 | 631.7 | 0.61975 | 633.9 | 0.99773 | 636.2 | 1.6238
655.7 | 6.0143 |  | 664.8 | 2.1552 | 670.4 | 15.053 | 673.6 | 13.7946 | 675.9 | 11.719 | 678.2 | 2.3699
697.8 | 6.537 |  | 706.8 | 3.203 | 712.3 | 17.8518 | 715.6 | 16.5806 | 717.9 | 2.9525 | 720.2 | 7.006
739.8 | 11.7335 |  | 748.6 | 5.0464 | 754.3 | 6.4683 | 757.7 | 2.4339 | 759.8 | 6.4075 | 762.2 | 2.1968
781.8 | 0.62305 |  | 790.8 | 1.1963 | 796.4 | 3.1178 | 799.6 | 4.6176 | 802 | 2.4771 | 804.2 | 0.6214
823.7 | 8.1203 |  | 832.6 | 1.1116 | 838.3 | 0.62783 | 841.7 | 4.8893 | 843.9 | 1.2692 | 846.2 | 5.1473
865.7 | 1.3896 |  | 874.6 | 0.62831 | 880.5 | 1.3269 | 883.7 | 9.3522 | 885.9 | 0.80924 | 888.2 | 3.8355
907.7 | 8.0753 |  | 916.7 | 1.7603 | 922.4 | 1.5077 | 925.6 | 6.3658 | 928 | 0.61881 | 930.2 | 0.62163
949.7 | 11.9757 |  | 958.6 | 8.5555 | 964.3 | 1.642 | 967.6 | 1.2097 | 969.8 | 0.61672 | 972.2 | 9.1325
991.7 | 5.7398 |  | 1000.6 | 3.8551 | 1006.3 | 2.6341 | 1009.6 | 1.5806 | 1011.8 | 0.61718 | 1014.2 | 6.8243
1033.7 | 1.3822 |  | 1042.7 | 1.6194 | 1048.5 | 0.62783 | 1051.6 | 14.9539 | 1053.9 | 0.76906 | 1056.2 | 5.1765
1075.7 | 0.62092 |  | 1084.6 | 7.9732 | 1090.3 | 5.4413 | 1093.6 | 1.736 | 1095.8 | 2.1552 | 1098.2 | 0.69332
1117.7 | 0.624 |  | 1126.6 | 2.8033 | 1132.3 | 2.3958 | 1135.6 | 1.1941 | 1137.8 | 3.7142 | 1140.2 | 12.9508
1159.7 | 11.7808 |  | 1168.6 | 1.9626 | 1174.3 | 9.0274 | 1177.6 | 6.5641 | 1179.8 | 8.8174 | 1182.2 | 2.8267
1201.7 | 3.3235 |  | 1210.6 | 2.1168 | 1216.3 | 6.3337 | 1219.6 | 10.6231 | 1221.8 | 11.6749 | 1224.2 | 10.7961
1243.7 | 11.4349 |  | 1252.6 | 5.1656 | 1258.3 | 10.2552 | 1261.6 | 9.445 | 1263.8 | 4.2827 | 1266.2 | 1.2411
1285.7 | 8.675 |  | 1294.6 | 8.9967 | 1300.3 | 11.843 | 1303.6 | 29.0382 | 1305.8 | 18.8732 | 1308.2 | 8.3865
1327.7 | 77.4726 |  | 1336.6 | 114.2378 | 1342.3 | 13.7632 | 1345.6 | 66.5437 | 1347.8 | 192.4841 | 1350.2 | 195.0738
1369.7 | 71.7313 |  | 1378.6 | 62.9522 | 1384.3 | 6.6954 | 1387.6 | 11.6145 | 1389.8 | 118.7043 | 1392.2 | 49.3735
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!

## C5-C6
Open Burn Test 12 |  |  | 2006-11-22 | 13:02 |  |  | Vs = |  | 162.5995 |  | R = | 100
Mixed | 7-C | Tray A | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 5 & 6 | Cable C | Odd-Even
Time-29 | N11 | N12 | Time-30 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R6-G | R5-6
39043.5393 | 1 | 0 | 39043.5393 | 2 | 0 |  | -150.5 | 39.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 266238 | 133069 | 266237.9994
39043.5398 | 1 | 0 | 39043.5398 | 1 | 0 |  | -108.5 | 81.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 266238 | 266238 | 266237.9994
39043.5403 | 1 | 0 | 39043.5403 | 1 | 0 |  | -66.5 | 123.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 266238 | 266238 | 266237.9994
39043.5408 | 1 | 0 | 39043.5408 | 1 | 0 |  | -24.5 | 165.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 266238 | 266238 | 266237.9994
39043.5413 | 1 | 0 | 39043.5413 | 1 | 0 |  | 17.5 | 207.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 266238 | 266238 | 266237.9994
39043.5418 | 1 | 0 | 39043.5418 | 1 | 0 |  | 59.5 | 249.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 266238 | 266238 | 266237.9994
39043.5422 | 1 | 0 | 39043.5423 | 1 | 0 |  | 101.5 | 291.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 266238 | 266238 | 266237.9994
39043.5427 | 474 | 1 | 39043.5427 | 1 | 0 |  | 143.5 | 333.5 | 28.9377 | 0.06105 | 0.06105 | 0 | 0.28938 | 0.0006105 | 0.0006105 | 0 | 0.28877 | 0.0006105 | 462.8714 | 266238 | 218755.8345
39043.5432 | 1414 | 662 | 39043.5432 | 1273 | 511 |  | 185.5 | 375.5 | 86.3248 | 40.4151 | 77.7167 | 31.1966 | 0.86325 | 0.40415 | 0.77717 | 0.31197 | 0.4591 | 0.4652 | 258.5058 | 246.3791 | 63.1122
39043.5437 | 1890 | 39 | 39043.5437 | 1927 | 118 |  | 227.5 | 417.5 | 115.3846 | 2.381 | 117.6435 | 7.2039 | 1.1538 | 0.02381 | 1.1764 | 0.072039 | 1.13 | 1.1044 | 43.7064 | 47.8474 | 609.3982
39043.5442 | 2615 | 0 | 39043.5442 | 2176 | 0 |  | 269.5 | 459.5 | 159.6459 | 0 | 132.8449 | 0 | 1.5965 | 0 | 1.3284 | 0 | 1.5965 | 1.3284 | 1.8501 | 22.398 | 0.25364
39043.5447 | 2481 | 0 | 39043.5447 | 2077 | 0 |  | 311.5 | 501.5 | 151.4652 | 0 | 126.801 | 0 | 1.5147 | 0 | 1.268 | 0 | 1.5147 | 1.268 | 7.3511 | 28.2321 | 5.8364
39043.5452 | 2528 | 0 | 39043.5452 | 2226 | 0 |  | 353.5 | 543.5 | 154.3346 | 0 | 135.8974 | 0 | 1.5433 | 0 | 1.359 | 0 | 1.5433 | 1.359 | 5.3552 | 19.6487 | 3.8119
39043.5456 | 2640 | 0 | 39043.5457 | 2139 | 0 |  | 395.5 | 585.5 | 161.1722 | 0 | 130.5861 | 0 | 1.6117 | 0 | 1.3059 | 0 | 1.6117 | 1.3059 | 0.88561 | 24.5152 | 0.72612
39043.5461 | 2305 | 0 | 39043.5461 | 2334 | 0 |  | 437.5 | 627.5 | 140.7204 | 0 | 142.4908 | 0 | 1.4072 | 0 | 1.4249 | 0 | 1.4072 | 1.4249 | 15.5479 | 14.1123 | 14.1407
39043.5466 | 2107 | 0 | 39043.5466 | 2430 | 0 |  | 479.5 | 669.5 | 128.6325 | 0 | 148.3516 | 0 | 1.2863 | 0 | 1.4835 | 0 | 1.2863 | 1.4835 | 26.4063 | 9.6041 | 25.1199
39043.5471 | 2148 | 0 | 39043.5471 | 2586 | 0 |  | 521.5 | 711.5 | 131.1355 | 0 | 157.8755 | 0 | 1.3114 | 0 | 1.5788 | 0 | 1.3114 | 1.5788 | 23.9935 | 2.9923 | 22.6821
39043.5476 | 2111 | 0 | 39043.5476 | 2076 | 0 |  | 563.5 | 753.5 | 128.8767 | 0 | 126.7399 | 0 | 1.2888 | 0 | 1.2674 | 0 | 1.2888 | 1.2674 | 26.1667 | 28.2938 | 24.878
39043.5481 | 2162 | 0 | 39043.5481 | 2302 | 0 |  | 605.5 | 795.5 | 131.9902 | 0 | 140.5372 | 0 | 1.3199 | 0 | 1.4054 | 0 | 1.3199 | 1.4054 | 23.1906 | 15.6985 | 21.8707
39043.5486 | 2250 | 0 | 39043.5486 | 2159 | 0 |  | 647.5 | 837.5 | 137.3626 | 0 | 131.8071 | 0 | 1.3736 | 0 | 1.3181 | 0 | 1.3736 | 1.3181 | 18.3724 | 23.3617 | 16.9988
39043.5491 | 2384 | 0 | 39043.5491 | 2515 | 0 |  | 689.5 | 879.5 | 145.5433 | 0 | 153.5409 | 0 | 1.4554 | 0 | 1.5354 | 0 | 1.4554 | 1.5354 | 11.719 | 5.8998 | 10.2635
39043.5495 | 2587 | 0 | 39043.5495 | 2489 | 0 |  | 731.5 | 921.5 | 157.9365 | 0 | 151.9536 | 0 | 1.5794 | 0 | 1.5195 | 0 | 1.5794 | 1.5195 | 2.9525 | 7.006 | 1.3731
39043.55 | 2503 | 0 | 39043.55 | 2359 | 0 |  | 773.5 | 963.5 | 152.8083 | 0 | 144.0171 | 0 | 1.5281 | 0 | 1.4402 | 0 | 1.5281 | 1.4402 | 6.4075 | 12.9029 | 4.8794
39043.5505 | 2599 | 0 | 39043.5505 | 2643 | 0 |  | 815.5 | 1005.5 | 158.6691 | 0 | 161.3553 | 0 | 1.5867 | 0 | 1.6136 | 0 | 1.5867 | 1.6136 | 2.4771 | 0.77109 | 0.89042
39043.551 | 2630 | 0 | 39043.551 | 2533 | 0 |  | 857.5 | 1047.5 | 160.5617 | 0 | 154.6398 | 0 | 1.6056 | 0 | 1.5464 | 0 | 1.6056 | 1.5464 | 1.2692 | 5.1473 | 0.33642
39043.5515 | 2642 | 0 | 39043.5515 | 2565 | 0 |  | 899.5 | 1089.5 | 161.2943 | 0 | 156.5934 | 0 | 1.6129 | 0 | 1.5659 | 0 | 1.6129 | 1.5659 | 0.80924 | 3.8355 | 0.80371
39043.552 | 2647 | 0 | 39043.552 | 2597 | 0 |  | 941.5 | 1131.5 | 161.5995 | 0 | 158.547 | 0 | 1.616 | 0 | 1.5855 | 0 | 1.616 | 1.5855 | 0.61881 | 2.556 | 0.99718
39043.5525 | 2384 | 0 | 39043.5525 | 2062 | 0 |  | 983.5 | 1173.5 | 145.5433 | 0 | 125.8852 | 0 | 1.4554 | 0 | 1.2589 | 0 | 1.4554 | 1.2589 | 11.719 | 29.1649 | 10.2635
39043.5529 | 2478 | 0 | 39043.553 | 2384 | 0 |  | 1025.5 | 1215.5 | 151.2821 | 0 | 145.5433 | 0 | 1.5128 | 0 | 1.4554 | 0 | 1.5128 | 1.4554 | 7.481 | 11.719 | 5.9682
39043.5534 | 2278 | 0 | 39043.5534 | 2516 | 0 |  | 1067.5 | 1257.5 | 139.072 | 0 | 153.602 | 0 | 1.3907 | 0 | 1.536 | 0 | 1.3907 | 1.536 | 16.9175 | 5.8577 | 15.5268
39043.5539 | 2072 | 0 | 39043.5539 | 2239 | 0 |  | 1109.5 | 1299.5 | 126.4957 | 0 | 136.6911 | 0 | 1.265 | 0 | 1.3669 | 0 | 1.265 | 1.3669 | 28.5415 | 18.954 | 27.2765
39043.5544 | 2568 | 0 | 39043.5544 | 2358 | 0 |  | 1151.5 | 1341.5 | 156.7766 | 0 | 143.956 | 0 | 1.5678 | 0 | 1.4396 | 0 | 1.5678 | 1.4396 | 3.7142 | 12.9508 | 2.1464
39043.5549 | 2380 | 0 | 39043.5549 | 2342 | 0 |  | 1193.5 | 1383.5 | 145.2991 | 0 | 142.9792 | 0 | 1.453 | 0 | 1.4298 | 0 | 1.453 | 1.4298 | 11.9067 | 13.7225 | 10.4537
39043.5554 | 2053 | 0 | 39043.5554 | 2355 | 0 |  | 1235.5 | 1425.5 | 125.3358 | 0 | 143.7729 | 0 | 1.2534 | 0 | 1.4377 | 0 | 1.2534 | 1.4377 | 29.7311 | 13.0947 | 28.4778
39043.5559 | 2554 | 0 | 39043.5559 | 2246 | 0 |  | 1277.5 | 1467.5 | 155.9219 | 0 | 137.1184 | 0 | 1.5592 | 0 | 1.3712 | 0 | 1.5592 | 1.3712 | 4.2827 | 18.5833 | 2.7235
39043.5563 | 1426 | 634 | 39043.5564 | 1412 | 601 |  | 1319.5 | 1509.5 | 87.0574 | 38.7057 | 86.2027 | 36.6911 | 0.87057 | 0.38706 | 0.86203 | 0.36691 | 0.48352 | 0.49512 | 244.7792 | 221.2981 | 65.5498
39043.5568 | 1487 | 873 | 39043.5568 | 1532 | 834 |  | 1361.5 | 1551.5 | 90.7814 | 53.2967 | 93.5287 | 50.9158 | 0.90781 | 0.53297 | 0.93529 | 0.50916 | 0.37485 | 0.42613 | 706.6315 | 195.0738 | 22.9742
39043.5573 | 1167 | 1031 | 39043.5573 | 1298 | 1002 |  | 1403.5 | 1593.5 | 71.2454 | 62.9426 | 79.243 | 61.1722 | 0.71245 | 0.62943 | 0.79243 | 0.61172 | 0.083028 | 0.18071 | 845.3539 | 2513.8824 | 43.4118

## B4-C6
Open Burn Test 12 |  |  | 2006-11-22 | 13:02 |  |  | Vs = |  | 161.928 |  | R = | 100
Mixed | 7-C | Tray A | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 4 & 6 | Cable B | Even - | Cable C |  | Even
Time-27 | N11 | N12 | Time-28 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R6-G | R4-6
39043.5393 | 1 | 0 | 39043.5393 | 1 | 0 |  | -153.5 | 36.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265138 | 265138 | 265137.9994
39043.5398 | 1 | 0 | 39043.5398 | 1 | 0 |  | -111.5 | 78.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265138 | 265138 | 265137.9994
39043.5403 | 1 | 0 | 39043.5403 | 1 | 0 |  | -69.5 | 120.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265138 | 265138 | 265137.9994
39043.5408 | 1 | 0 | 39043.5408 | 1 | 0 |  | -27.5 | 162.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265138 | 265138 | 265137.9994
39043.5412 | 1 | 0 | 39043.5413 | 1 | 0 |  | 14.5 | 204.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265138 | 265138 | 265137.9994
39043.5417 | 1 | 0 | 39043.5417 | 1 | 0 |  | 56.5 | 246.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265138 | 265138 | 265137.9994
39043.5422 | 1 | 0 | 39043.5422 | 1 | 0 |  | 98.5 | 288.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265138 | 265138 | 265137.9994
39043.5427 | 1 | 0 | 39043.5427 | 1 | 0 |  | 140.5 | 330.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265138 | 265138 | 265137.9994
39043.5432 | 1 | 0 | 39043.5432 | 1412 | 0 |  | 182.5 | 372.5 | 0.06105 | 0 | 86.2027 | 0 | 0.0006105 | 0 | 0.86203 | 0 | 0.0006105 | 0.86203 | 265138 | 87.8456 | 265137.9994
39043.5437 | 1 | 0 | 39043.5437 | 2150 | 0 |  | 224.5 | 414.5 | 0.06105 | 0 | 131.2576 | 0 | 0.0006105 | 0 | 1.3126 | 0 | 0.0006105 | 1.3126 | 265138 | 23.3665 | 265137.9994
39043.5442 | 2 | 0 | 39043.5442 | 2225 | 0 |  | 266.5 | 456.5 | 0.1221 | 0 | 135.8364 | 0 | 0.001221 | 0 | 1.3584 | 0 | 0.001221 | 1.3584 | 132519 | 19.2081 | 132518.9988
39043.5446 | 5 | 0 | 39043.5447 | 2092 | 0 |  | 308.5 | 498.5 | 0.30525 | 0 | 127.7167 | 0 | 0.0030525 | 0 | 1.2772 | 0 | 0.0030525 | 1.2772 | 52947.6 | 26.7868 | 52947.5969
39043.5451 | 1653 | 0 | 39043.5451 | 2328 | 0 |  | 350.5 | 540.5 | 100.9158 | 0 | 142.1245 | 0 | 1.0092 | 0 | 1.4212 | 0 | 1.0092 | 1.4212 | 60.4586 | 13.9338 | 59.4494
39043.5456 | 1840 | 0 | 39043.5456 | 2116 | 0 |  | 392.5 | 582.5 | 112.3321 | 0 | 129.1819 | 0 | 1.1233 | 0 | 1.2918 | 0 | 1.1233 | 1.2918 | 44.1511 | 25.3488 | 43.0278
39043.5461 | 1804 | 0 | 39043.5461 | 2514 | 0 |  | 434.5 | 624.5 | 110.1343 | 0 | 153.4799 | 0 | 1.1013 | 0 | 1.5348 | 0 | 1.1013 | 1.5348 | 47.0277 | 5.5044 | 45.9264
39043.5466 | 2460 | 0 | 39043.5466 | 2096 | 0 |  | 476.5 | 666.5 | 150.1832 | 0 | 127.9609 | 0 | 1.5018 | 0 | 1.2796 | 0 | 1.5018 | 1.2796 | 7.8203 | 26.5448 | 6.3185
39043.5471 | 2263 | 0 | 39043.5471 | 2185 | 0 |  | 518.5 | 708.5 | 138.1563 | 0 | 133.3944 | 0 | 1.3816 | 0 | 1.3339 | 0 | 1.3816 | 1.3339 | 17.2064 | 21.3904 | 15.8248
39043.5476 | 2270 | 0 | 39043.5476 | 2524 | 0 |  | 560.5 | 750.5 | 138.5836 | 0 | 154.0904 | 0 | 1.3858 | 0 | 1.5409 | 0 | 1.3858 | 1.5409 | 16.8449 | 5.0864 | 15.4591
39043.548 | 2255 | 0 | 39043.5481 | 2617 | 0 |  | 602.5 | 792.5 | 137.6679 | 0 | 159.768 | 0 | 1.3767 | 0 | 1.5977 | 0 | 1.3767 | 1.5977 | 17.6222 | 1.3519 | 16.2455
39043.5485 | 1918 | 0 | 39043.5485 | 2610 | 0 |  | 644.5 | 834.5 | 117.094 | 0 | 159.3407 | 0 | 1.1709 | 0 | 1.5934 | 0 | 1.1709 | 1.5934 | 38.2888 | 1.6238 | 37.1179
39043.549 | 1766 | 0 | 39043.549 | 2559 | 0 |  | 686.5 | 876.5 | 107.8144 | 0 | 156.2271 | 0 | 1.0781 | 0 | 1.5623 | 0 | 1.0781 | 1.5623 | 50.1914 | 3.6491 | 49.1132
39043.5495 | 1731 | 0 | 39043.5495 | 2477 | 0 |  | 728.5 | 918.5 | 105.6777 | 0 | 151.221 | 0 | 1.0568 | 0 | 1.5122 | 0 | 1.0568 | 1.5122 | 53.2282 | 7.0803 | 52.1714
39043.55 | 2156 | 0 | 39043.55 | 2476 | 0 |  | 770.5 | 960.5 | 131.6239 | 0 | 151.16 | 0 | 1.3162 | 0 | 1.5116 | 0 | 1.3162 | 1.5116 | 23.0232 | 7.1236 | 21.707
39043.5505 | 2085 | 0 | 39043.5505 | 2636 | 0 |  | 812.5 | 1002.5 | 127.2894 | 0 | 160.928 | 0 | 1.2729 | 0 | 1.6093 | 0 | 1.2729 | 1.6093 | 27.2125 | 0.6214 | 25.9396
39043.551 | 2204 | 0 | 39043.551 | 2436 | 0 |  | 854.5 | 1044.5 | 134.5543 | 0 | 148.7179 | 0 | 1.3455 | 0 | 1.4872 | 0 | 1.3455 | 1.4872 | 20.3439 | 8.8826 | 18.9984
39043.5514 | 2257 | 0 | 39043.5515 | 2067 | 0 |  | 896.5 | 1086.5 | 137.79 | 0 | 126.1905 | 0 | 1.3779 | 0 | 1.2619 | 0 | 1.3779 | 1.2619 | 17.5179 | 28.3203 | 16.14
39043.5519 | 2447 | 0 | 39043.5519 | 2063 | 0 |  | 938.5 | 1128.5 | 149.3895 | 0 | 125.9463 | 0 | 1.4939 | 0 | 1.2595 | 0 | 1.4939 | 1.2595 | 8.3931 | 28.5691 | 6.8992
39043.5524 | 2580 | 0 | 39043.5524 | 2408 | 0 |  | 980.5 | 1170.5 | 157.5092 | 0 | 147.0085 | 0 | 1.5751 | 0 | 1.4701 | 0 | 1.5751 | 1.4701 | 2.8054 | 10.1487 | 1.2303
39043.5529 | 2531 | 0 | 39043.5529 | 2287 | 0 |  | 1022.5 | 1212.5 | 154.5177 | 0 | 139.6215 | 0 | 1.5452 | 0 | 1.3962 | 0 | 1.5452 | 1.3962 | 4.7957 | 15.9764 | 3.2506
39043.5534 | 2077 | 0 | 39043.5534 | 2135 | 0 |  | 1064.5 | 1254.5 | 126.801 | 0 | 130.3419 | 0 | 1.268 | 0 | 1.3034 | 0 | 1.268 | 1.3034 | 27.7025 | 24.2333 | 26.4344
39043.5539 | 2537 | 0 | 39043.5539 | 2159 | 0 |  | 1106.5 | 1296.5 | 154.884 | 0 | 131.8071 | 0 | 1.5488 | 0 | 1.3181 | 0 | 1.5488 | 1.3181 | 4.5479 | 22.8522 | 2.9991
39043.5544 | 2365 | 0 | 39043.5544 | 2165 | 0 |  | 1148.5 | 1338.5 | 144.3834 | 0 | 132.1734 | 0 | 1.4438 | 0 | 1.3217 | 0 | 1.4438 | 1.3217 | 12.1514 | 22.5118 | 10.7075
39043.5548 | 2489 | 0 | 39043.5549 | 2092 | 0 |  | 1190.5 | 1380.5 | 151.9536 | 0 | 127.7167 | 0 | 1.5195 | 0 | 1.2772 | 0 | 1.5195 | 1.2772 | 6.5641 | 26.7868 | 5.0445
39043.5553 | 2146 | 0 | 39043.5553 | 2156 | 0 |  | 1232.5 | 1422.5 | 131.0134 | 0 | 131.6239 | 0 | 1.3101 | 0 | 1.3162 | 0 | 1.3101 | 1.3162 | 23.5965 | 23.0232 | 22.2863
39043.5558 | 1639 | 0 | 39043.5558 | 2303 | 0 |  | 1274.5 | 1464.5 | 100.0611 | 0 | 140.5983 | 0 | 1.0006 | 0 | 1.406 | 0 | 1.0006 | 1.406 | 61.8292 | 15.1706 | 60.8286
39043.5563 | 1969 | 0 | 39043.5563 | 1683 | 0 |  | 1316.5 | 1506.5 | 120.2076 | 0 | 102.7473 | 0 | 1.2021 | 0 | 1.0275 | 0 | 1.2021 | 1.0275 | 34.707 | 57.5983 | 33.5049
39043.5568 | 1293 | 0 | 39043.5568 | 829 | 0 |  | 1358.5 | 1548.5 | 78.9377 | 0 | 50.6105 | 0 | 0.78938 | 0 | 0.50611 | 0 | 0.78938 | 0.50611 | 105.1338 | 219.9493 | 104.3444
39043.5573 | 1462 | 0 | 39043.5573 | 503 | 0 |  | 1400.5 | 1590.5 | 89.2552 | 0 | 30.7082 | 0 | 0.89255 | 0 | 0.30708 | 0 | 0.89255 | 0.30708 | 81.4213 | 427.3121 | 80.5288

## B4-C5
Open Burn Test 12 |  |  | 2006-11-22 | 13:02 |  |  | Vs = |  | 163.0269 |  | R = | 100
Mixed | 7-C | Tray A | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 4 & 5 | Cable B | Even - | Cable C |  | Odd
Time-25 | N11 | N12 | Time-26 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R5-G | R4-5
39043.5393 | 1 | 0 | 39043.5393 | 1 | 0 |  | -156 | 34 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 266938 | 266938 | 266937.9994
39043.5397 | 1 | 0 | 39043.5398 | 1 | 0 |  | -114 | 76 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 266938 | 266938 | 266937.9994
39043.5402 | 1 | 0 | 39043.5403 | 1 | 0 |  | -72 | 118 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 266938 | 266938 | 266937.9994
39043.5407 | 1 | 0 | 39043.5407 | 1 | 0 |  | -30 | 160 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 266938 | 266938 | 266937.9994
39043.5412 | 1 | 0 | 39043.5412 | 1 | 0 |  | 12 | 202 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 266938 | 266938 | 266937.9994
39043.5417 | 1 | 0 | 39043.5417 | 1 | 0 |  | 54 | 244 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 266938 | 266938 | 266937.9994
39043.5422 | 1 | 0 | 39043.5422 | 1 | 0 |  | 96 | 286 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 266938 | 266938 | 266937.9994
39043.5427 | 1 | 0 | 39043.5427 | 1 | 0 |  | 138 | 328 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 266938 | 266938 | 266937.9994
39043.5431 | 1 | 0 |  | 615 | 0 |  | 179 | 369 | 0.06105 | 0 | 37.5458 | 0 | 0.0006105 | 0 | 0.37546 | 0 | 0.0006105 | 0.37546 | 266938 | 334.2081 | 266937.9994
39043.5436 | 1 | 0 | 39043.5437 | 2266 | 0 |  | 222 | 412 | 0.06105 | 0 | 138.3394 | 0 | 0.0006105 | 0 | 1.3834 | 0 | 0.0006105 | 1.3834 | 266938 | 17.8455 | 266937.9994
39043.5441 | 106 | 0 | 39043.5441 | 2478 | 0 |  | 264 | 454 | 6.4713 | 0 | 151.2821 | 0 | 0.064713 | 0 | 1.5128 | 0 | 0.064713 | 1.5128 | 2419.2264 | 7.7635 | 2419.1617
39043.5446 | 15 | 0 | 39043.5446 | 2213 | 0 |  | 306 | 496 | 0.91575 | 0 | 135.1038 | 0 | 0.0091575 | 0 | 1.351 | 0 | 0.0091575 | 1.351 | 17702.5333 | 20.6679 | 17702.5242
39043.5451 | 1720 | 0 | 39043.5451 | 2342 | 0 |  | 348 | 538 | 105.0061 | 0 | 142.9792 | 0 | 1.0501 | 0 | 1.4298 | 0 | 1.0501 | 1.4298 | 55.2547 | 14.0213 | 54.2046
39043.5456 | 2255 | 0 | 39043.5456 | 2382 | 0 |  | 389.5 | 579.5 | 137.6679 | 0 | 145.4212 | 0 | 1.3767 | 0 | 1.4542 | 0 | 1.3767 | 1.4542 | 18.4204 | 12.1066 | 17.0437
39043.5461 | 1997 | 0 | 39043.5461 | 2480 | 0 |  | 432 | 622 | 121.917 | 0 | 151.4042 | 0 | 1.2192 | 0 | 1.514 | 0 | 1.2192 | 1.514 | 33.7196 | 7.6766 | 32.5004
39043.5466 | 2147 | 0 | 39043.5466 | 2653 | 0 |  | 473.5 | 663.5 | 131.0745 | 0 | 161.9658 | 0 | 1.3107 | 0 | 1.6197 | 0 | 1.3107 | 1.6197 | 24.3773 | 0.65511 | 23.0665
39043.547 | 2518 | 0 | 39043.5471 | 2654 | 0 |  | 516 | 706 | 153.7241 | 0 | 162.0269 | 0 | 1.5372 | 0 | 1.6203 | 0 | 1.5372 | 1.6203 | 6.0516 | 0.61718 | 4.5144
39043.5475 | 2185 | 0 | 39043.5475 | 2066 | 0 |  | 557.5 | 747.5 | 133.3944 | 0 | 126.1294 | 0 | 1.3339 | 0 | 1.2613 | 0 | 1.3339 | 1.2613 | 22.2142 | 29.2536 | 20.8802
39043.548 | 2338 | 0 | 39043.548 | 2282 | 0 |  | 600 | 790 | 142.735 | 0 | 139.3162 | 0 | 1.4274 | 0 | 1.3932 | 0 | 1.4274 | 1.3932 | 14.2164 | 17.0193 | 12.7891
39043.5485 | 1889 | 0 | 39043.5485 | 2374 | 0 |  | 642 | 832 | 115.3236 | 0 | 144.9328 | 0 | 1.1532 | 0 | 1.4493 | 0 | 1.1532 | 1.4493 | 41.3647 | 12.4844 | 40.2115
39043.549 | 1803 | 0 | 39043.549 | 2163 | 0 |  | 683.5 | 873.5 | 110.0733 | 0 | 132.0513 | 0 | 1.1007 | 0 | 1.3205 | 0 | 1.1007 | 1.3205 | 48.1076 | 23.4572 | 47.0069
39043.5495 | 1840 | 0 | 39043.5495 | 2074 | 0 |  | 725.5 | 915.5 | 112.3321 | 0 | 126.6178 | 0 | 1.1233 | 0 | 1.2662 | 0 | 1.1233 | 1.2662 | 45.1293 | 28.7551 | 44.006
39043.55 | 2569 | 0 | 39043.55 | 2367 | 0 |  | 767.5 | 957.5 | 156.8376 | 0 | 144.5055 | 0 | 1.5684 | 0 | 1.4451 | 0 | 1.5684 | 1.4451 | 3.9463 | 12.8171 | 2.3779
39043.5504 | 2459 | 0 | 39043.5505 | 2257 | 0 |  | 809.5 | 999.5 | 150.1221 | 0 | 137.79 | 0 | 1.5012 | 0 | 1.3779 | 0 | 1.5012 | 1.3779 | 8.5962 | 18.3155 | 7.095
39043.5509 | 2490 | 0 | 39043.5509 | 2537 | 0 |  | 852 | 1042 | 152.0147 | 0 | 154.884 | 0 | 1.5201 | 0 | 1.5488 | 0 | 1.5201 | 1.5488 | 7.2442 | 5.2574 | 5.724
39043.5514 | 2442 | 0 | 39043.5514 | 2068 | 0 |  | 893.5 | 1083.5 | 149.0842 | 0 | 126.2515 | 0 | 1.4908 | 0 | 1.2625 | 0 | 1.4908 | 1.2625 | 9.3522 | 29.1286 | 7.8613
39043.5519 | 2055 | 0 | 39043.5519 | 2345 | 0 |  | 935.5 | 1125.5 | 125.4579 | 0 | 143.1624 | 0 | 1.2546 | 0 | 1.4316 | 0 | 1.2546 | 1.4316 | 29.9455 | 13.8755 | 28.6909
39043.5524 | 2559 | 0 | 39043.5524 | 2143 | 0 |  | 977.5 | 1167.5 | 156.2271 | 0 | 130.8303 | 0 | 1.5623 | 0 | 1.3083 | 0 | 1.5623 | 1.3083 | 4.3525 | 24.6094 | 2.7902
39043.5529 | 2157 | 0 | 39043.5529 | 2398 | 0 |  | 1019.5 | 1209.5 | 131.685 | 0 | 146.398 | 0 | 1.3168 | 0 | 1.464 | 0 | 1.3168 | 1.464 | 23.8006 | 11.3586 | 22.4838
39043.5534 | 2323 | 0 | 39043.5534 | 2650 | 0 |  | 1061.5 | 1251.5 | 141.8193 | 0 | 161.7827 | 0 | 1.4182 | 0 | 1.6178 | 0 | 1.4182 | 1.6178 | 14.9539 | 0.76906 | 13.5357
39043.5538 | 2170 | 0 | 39043.5539 | 2225 | 0 |  | 1103.5 | 1293.5 | 132.4786 | 0 | 135.8364 | 0 | 1.3248 | 0 | 1.3584 | 0 | 1.3248 | 1.3584 | 23.059 | 20.0171 | 21.7342
39043.5543 | 2421 | 0 | 39043.5543 | 2432 | 0 |  | 1145.5 | 1335.5 | 147.8022 | 0 | 148.4737 | 0 | 1.478 | 0 | 1.4847 | 0 | 1.478 | 1.4847 | 10.3007 | 9.8018 | 8.8227
39043.5548 | 2174 | 0 | 39043.5548 | 2454 | 0 |  | 1187.5 | 1377.5 | 132.7228 | 0 | 149.8168 | 0 | 1.3272 | 0 | 1.4982 | 0 | 1.3272 | 1.4982 | 22.8326 | 8.8174 | 21.5053
39043.5553 | 2195 | 0 | 39043.5553 | 2182 | 0 |  | 1229.5 | 1419.5 | 134.0049 | 0 | 133.2112 | 0 | 1.34 | 0 | 1.3321 | 0 | 1.34 | 1.3321 | 21.6574 | 22.3822 | 20.3174
39043.5558 | 1785 | 0 | 39043.5558 | 2060 | 0 |  | 1271.5 | 1461.5 | 108.9744 | 0 | 125.7631 | 0 | 1.0897 | 0 | 1.2576 | 0 | 1.0897 | 1.2576 | 49.6011 | 29.6301 | 48.5114
39043.5563 | 1971 | 0 | 39043.5563 | 1888 | 0 |  | 1313.5 | 1503.5 | 120.3297 | 0 | 115.2625 | 0 | 1.2033 | 0 | 1.1526 | 0 | 1.2033 | 1.1526 | 35.4835 | 41.4396 | 34.2802
39043.5568 | 1478 | 0 | 39043.5568 | 659 | 0 |  | 1355.5 | 1545.5 | 90.232 | 0 | 40.232 | 0 | 0.90232 | 0 | 0.40232 | 0 | 0.90232 | 0.40232 | 80.6752 | 305.217 | 79.7729
39043.5572 | 1272 | 0 | 39043.5573 | 1221 | 0 |  | 1397.5 | 1587.5 | 77.6557 | 0 | 74.5421 | 0 | 0.77656 | 0 | 0.74542 | 0 | 0.77656 | 0.74542 | 109.9355 | 118.7043 | 109.159

## B3-C6
Open Burn Test 12 |  |  | 2006-11-22 | 13:02 |  |  | Vs = |  | 161.8669 |  | R = | 100
Mixed | 7-C | Tray A | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 3 & 6 | Cable B | Odd - | Cable C |  | Even
Time-23 | N11 | N12 | Time-24 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R6-G | R3-6
39043.5392 | 1 | 0 | 39043.5392 | 1 | 0 |  | -159 | 31 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265038 | 265038 | 265037.9994
39043.5397 | 1 | 0 | 39043.5397 | 1 | 0 |  | -117 | 73 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265038 | 265038 | 265037.9994
39043.5402 | 1 | 0 | 39043.5402 | 1 | 0 |  | -75 | 115 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265038 | 265038 | 265037.9994
39043.5407 | 1 | 0 | 39043.5407 | 1 | 0 |  | -33 | 157 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265038 | 265038 | 265037.9994
39043.5412 | 1 | 0 | 39043.5412 | 1 | 0 |  | 9 | 199 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265038 | 265038 | 265037.9994
39043.5417 | 1 | 0 | 39043.5417 | 1 | 0 |  | 51 | 241 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265038 | 265038 | 265037.9994
39043.5421 | 1 | 0 | 39043.5422 | 1 | 0 |  | 93 | 283 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265038 | 265038 | 265037.9994
39043.5426 | 1 | 0 | 39043.5427 | 1 | 0 |  | 135 | 325 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265038 | 265038 | 265037.9994
39043.5431 | 1 | 0 | 39043.5431 | 645 | 0 |  | 177 | 367 | 0.06105 | 0 | 39.3773 | 0 | 0.0006105 | 0 | 0.39377 | 0 | 0.0006105 | 0.39377 | 265038 | 311.0667 | 265037.9994
39043.5436 | 1 | 0 | 39043.5436 | 1941 | 0 |  | 219 | 409 | 0.06105 | 0 | 118.4982 | 0 | 0.0006105 | 0 | 1.185 | 0 | 0.0006105 | 1.185 | 265038 | 36.5987 | 265037.9994
39043.5441 | 2 | 0 | 39043.5441 | 2132 | 0 |  | 261 | 451 | 0.1221 | 0 | 130.1587 | 0 | 0.001221 | 0 | 1.3016 | 0 | 0.001221 | 1.3016 | 132469 | 24.3612 | 132468.9988
39043.5446 | 44 | 0 | 39043.5446 | 2332 | 0 |  | 303 | 493 | 2.6862 | 0 | 142.3687 | 0 | 0.026862 | 0 | 1.4237 | 0 | 0.026862 | 1.4237 | 5925.8636 | 13.6955 | 5925.8368
39043.5451 | 1394 | 0 | 39043.5451 | 2436 | 0 |  | 345 | 535 | 85.1038 | 0 | 148.7179 | 0 | 0.85104 | 0 | 1.4872 | 0 | 0.85104 | 1.4872 | 90.1994 | 8.8415 | 89.3484
39043.5455 | 1761 | 0 | 39043.5456 | 2531 | 0 |  | 387 | 577 | 107.5092 | 0 | 154.5177 | 0 | 1.0751 | 0 | 1.5452 | 0 | 1.0751 | 1.5452 | 50.561 | 4.7562 | 49.486
39043.546 | 1620 | 0 | 39043.5461 | 2367 | 0 |  | 429 | 619 | 98.9011 | 0 | 144.5055 | 0 | 0.98901 | 0 | 1.4451 | 0 | 0.98901 | 1.4451 | 63.6654 | 12.0144 | 62.6764
39043.5465 | 2502 | 0 | 39043.5465 | 2410 | 0 |  | 471 | 661 | 152.7473 | 0 | 147.1306 | 0 | 1.5275 | 0 | 1.4713 | 0 | 1.5275 | 1.4713 | 5.9704 | 10.0158 | 4.443
39043.547 | 2518 | 0 | 39043.547 | 2598 | 0 |  | 513 | 703 | 153.7241 | 0 | 158.6081 | 0 | 1.5372 | 0 | 1.5861 | 0 | 1.5372 | 1.5861 | 5.2971 | 2.0547 | 3.7598
39043.5475 | 2444 | 0 | 39043.5475 | 2476 | 0 |  | 555 | 745 | 149.2063 | 0 | 151.16 | 0 | 1.4921 | 0 | 1.5116 | 0 | 1.4921 | 1.5116 | 8.4853 | 7.0832 | 6.9932
39043.548 | 2096 | 0 | 39043.548 | 2190 | 0 |  | 597 | 787 | 127.9609 | 0 | 133.6996 | 0 | 1.2796 | 0 | 1.337 | 0 | 1.2796 | 1.337 | 26.4971 | 21.0676 | 25.2175
39043.5485 | 2119 | 0 | 39043.5485 | 2278 | 0 |  | 639 | 829 | 129.3651 | 0 | 139.072 | 0 | 1.2937 | 0 | 1.3907 | 0 | 1.2937 | 1.3907 | 25.1241 | 16.3907 | 23.8305
39043.5489 | 1893 | 0 | 39043.549 | 2590 | 0 |  | 681 | 871 | 115.5678 | 0 | 158.1197 | 0 | 1.1557 | 0 | 1.5812 | 0 | 1.1557 | 1.5812 | 40.0623 | 2.3699 | 38.9067
39043.5494 | 2200 | 0 | 39043.5495 | 2261 | 0 |  | 723 | 913 | 134.3101 | 0 | 138.0342 | 0 | 1.3431 | 0 | 1.3803 | 0 | 1.3431 | 1.3803 | 20.5173 | 17.2658 | 19.1742
39043.5499 | 2298 | 0 | 39043.5499 | 2368 | 0 |  | 765 | 955 | 140.293 | 0 | 144.5665 | 0 | 1.4029 | 0 | 1.4457 | 0 | 1.4029 | 1.4457 | 15.3777 | 11.9671 | 13.9748
39043.5504 | 2431 | 0 | 39043.5504 | 2559 | 0 |  | 807 | 997 | 148.4127 | 0 | 156.2271 | 0 | 1.4841 | 0 | 1.5623 | 0 | 1.4841 | 1.5623 | 9.0654 | 3.61 | 7.5813
39043.5509 | 2305 | 0 | 39043.5509 | 2148 | 0 |  | 849 | 1039 | 140.7204 | 0 | 131.1355 | 0 | 1.4072 | 0 | 1.3114 | 0 | 1.4072 | 1.3114 | 15.0273 | 23.4348 | 13.6201
39043.5514 | 2607 | 0 | 39043.5514 | 2407 | 0 |  | 891 | 1081 | 159.1575 | 0 | 146.9475 | 0 | 1.5916 | 0 | 1.4695 | 0 | 1.5916 | 1.4695 | 1.7023 | 10.1529 | 0.11076
39043.5519 | 2612 | 0 | 39043.5519 | 2635 | 0 |  | 933 | 1123 | 159.4628 | 0 | 160.8669 | 0 | 1.5946 | 0 | 1.6087 | 0 | 1.5946 | 1.6087 | 1.5077 | 0.62163 | 0.086971
39043.5523 | 2211 | 0 | 39043.5524 | 2068 | 0 |  | 975 | 1165 | 134.9817 | 0 | 126.2515 | 0 | 1.3498 | 0 | 1.2625 | 0 | 1.3498 | 1.2625 | 19.9177 | 28.2099 | 18.5679
39043.5528 | 2563 | 0 | 39043.5529 | 2482 | 0 |  | 1017 | 1207 | 156.4713 | 0 | 151.5263 | 0 | 1.5647 | 0 | 1.5153 | 0 | 1.5647 | 1.5153 | 3.4483 | 6.8243 | 1.8836
39043.5533 | 2043 | 0 | 39043.5533 | 2289 | 0 |  | 1059 | 1249 | 124.7253 | 0 | 139.7436 | 0 | 1.2473 | 0 | 1.3974 | 0 | 1.2473 | 1.3974 | 29.7788 | 15.8314 | 28.5315
39043.5538 | 2391 | 0 | 39043.5538 | 2282 | 0 |  | 1101 | 1291 | 145.9707 | 0 | 139.3162 | 0 | 1.4597 | 0 | 1.3932 | 0 | 1.4597 | 1.3932 | 10.89 | 16.1867 | 9.4303
39043.5543 | 1800 | 0 | 39043.5543 | 2047 | 0 |  | 1143 | 1333 | 109.8901 | 0 | 124.9695 | 0 | 1.0989 | 0 | 1.2497 | 0 | 1.0989 | 1.2497 | 47.2989 | 29.5252 | 46.2
39043.5548 | 2014 | 0 | 39043.5548 | 2502 | 0 |  | 1185 | 1375 | 122.9548 | 0 | 152.7473 | 0 | 1.2295 | 0 | 1.5275 | 0 | 1.2295 | 1.5275 | 31.6475 | 5.9704 | 30.4179
39043.5553 | 2420 | 0 | 39043.5553 | 2071 | 0 |  | 1227 | 1417 | 147.7411 | 0 | 126.4347 | 0 | 1.4774 | 0 | 1.2643 | 0 | 1.4774 | 1.2643 | 9.5612 | 28.0241 | 8.0837
39043.5558 | 1616 | 0 | 39043.5558 | 2152 | 0 |  | 1269 | 1459 | 98.6569 | 0 | 131.3797 | 0 | 0.98657 | 0 | 1.3138 | 0 | 0.98657 | 1.3138 | 64.0705 | 23.2054 | 63.084
39043.5562 | 1926 | 0 | 39043.5563 | 1859 | 0 |  | 1311 | 1501 | 117.5824 | 0 | 113.4921 | 0 | 1.1758 | 0 | 1.1349 | 0 | 1.1758 | 1.1349 | 37.6625 | 42.624 | 36.4867
39043.5567 | 1537 | 0 | 39043.5567 | 694 | 0 |  | 1353 | 1543 | 93.8339 | 0 | 42.3687 | 0 | 0.93834 | 0 | 0.42369 | 0 | 0.93834 | 0.42369 | 72.5036 | 282.0432 | 71.5652
39043.5572 | 2485 | 0 | 39043.5572 | 1775 | 0 |  | 1395 | 1585 | 151.7094 | 0 | 108.3639 | 0 | 1.5171 | 0 | 1.0836 | 0 | 1.5171 | 1.0836 | 6.6954 | 49.3735 | 5.1783

## B3-C5
Open Burn Test 12 |  |  | 2006-11-22 | 13:02 |  |  | Vs = |  | 163.0269 |  | R = | 100
Mixed | 7-C | Tray A | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 3 & 5 | Cable B | Odd - | Cable C |  | Odd
Time-21 | N11 | N12 | Time-22 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R5-G | R3-5
39043.5392 | 1 | 0 | 39043.5392 | 1 | 0 |  | -161.5 | 28.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 266938 | 266938 | 266937.9994
39043.5397 | 1 | 0 | 39043.5397 | 1 | 0 |  | -119.5 | 70.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 266938 | 266938 | 266937.9994
39043.5402 | 1 | 0 | 39043.5402 | 1 | 0 |  | -77.5 | 112.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 266938 | 266938 | 266937.9994
39043.5407 | 1 | 0 | 39043.5407 | 1 | 0 |  | -35.5 | 154.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 266938 | 266938 | 266937.9994
39043.5411 | 1 | 0 | 39043.5412 | 1 | 0 |  | 6.5 | 196.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 266938 | 266938 | 266937.9994
39043.5416 | 1 | 0 | 39043.5416 | 1 | 0 |  | 48.5 | 238.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 266938 | 266938 | 266937.9994
39043.5421 | 1 | 0 | 39043.5421 | 1 | 0 |  | 90.5 | 280.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 266938 | 266938 | 266937.9994
39043.5426 | 1 | 0 | 39043.5426 | 1 | 0 |  | 132.5 | 322.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 266938 | 266938 | 266937.9994
39043.5431 | 1 | 0 | 39043.5431 | 626 | 0 |  | 174.5 | 364.5 | 0.06105 | 0 | 38.2173 | 0 | 0.0006105 | 0 | 0.38217 | 0 | 0.0006105 | 0.38217 | 266938 | 326.5783 | 266937.9994
39043.5436 | 1 | 0 | 39043.5436 | 2307 | 0 |  | 216.5 | 406.5 | 0.06105 | 0 | 140.8425 | 0 | 0.0006105 | 0 | 1.4084 | 0 | 0.0006105 | 1.4084 | 266938 | 15.7512 | 266937.9994
39043.5441 | 1 | 0 | 39043.5441 | 2451 | 0 |  | 258.5 | 448.5 | 0.06105 | 0 | 149.6337 | 0 | 0.0006105 | 0 | 1.4963 | 0 | 0.0006105 | 1.4963 | 266938 | 8.9506 | 266937.9994
39043.5445 | 297 | 0 | 39043.5446 | 2261 | 0 |  | 300.5 | 490.5 | 18.1319 | 0 | 138.0342 | 0 | 0.18132 | 0 | 1.3803 | 0 | 0.18132 | 1.3803 | 799.1178 | 18.1061 | 798.9365
39043.545 | 1538 | 0 | 39043.545 | 2086 | 0 |  | 342.5 | 532.5 | 93.895 | 0 | 127.3504 | 0 | 0.93895 | 0 | 1.2735 | 0 | 0.93895 | 1.2735 | 73.6268 | 28.0144 | 72.6878
39043.5455 | 2218 | 0 | 39043.5455 | 2395 | 0 |  | 384.5 | 574.5 | 135.409 | 0 | 146.2149 | 0 | 1.3541 | 0 | 1.4621 | 0 | 1.3541 | 1.4621 | 20.3959 | 11.4981 | 19.0418
39043.546 | 1959 | 0 | 39043.546 | 2173 | 0 |  | 426 | 616 | 119.5971 | 0 | 132.6618 | 0 | 1.196 | 0 | 1.3266 | 0 | 1.196 | 1.3266 | 36.3134 | 22.8891 | 35.1175
39043.5465 | 2461 | 0 | 39043.5465 | 2428 | 0 |  | 468.5 | 658.5 | 150.2442 | 0 | 148.2295 | 0 | 1.5024 | 0 | 1.4823 | 0 | 1.5024 | 1.4823 | 8.5079 | 9.9827 | 7.0055
39043.547 | 2235 | 0 | 39043.547 | 2093 | 0 |  | 510.5 | 700.5 | 136.4469 | 0 | 127.7778 | 0 | 1.3645 | 0 | 1.2778 | 0 | 1.3645 | 1.2778 | 19.4801 | 27.5862 | 18.1156
39043.5475 | 2095 | 0 | 39043.5475 | 2048 | 0 |  | 552.5 | 742.5 | 127.8999 | 0 | 125.0305 | 0 | 1.279 | 0 | 1.2503 | 0 | 1.279 | 1.2503 | 27.4644 | 30.3896 | 26.1854
39043.5479 | 2228 | 0 | 39043.548 | 2651 | 0 |  | 594 | 784 | 136.0195 | 0 | 161.8437 | 0 | 1.3602 | 0 | 1.6184 | 0 | 1.3602 | 1.6184 | 19.8555 | 0.73104 | 18.4953
39043.5484 | 1820 | 0 | 39043.5484 | 2644 | 0 |  | 636 | 826 | 111.1111 | 0 | 161.4164 | 0 | 1.1111 | 0 | 1.6142 | 0 | 1.1111 | 1.6142 | 46.7242 | 0.99773 | 45.6131
39043.5489 | 2321 | 0 | 39043.5489 | 2252 | 0 |  | 678 | 868 | 141.6972 | 0 | 137.4847 | 0 | 1.417 | 0 | 1.3748 | 0 | 1.417 | 1.3748 | 15.053 | 18.5782 | 13.636
39043.5494 | 1939 | 0 | 39043.5494 | 2118 | 0 |  | 720 | 910 | 118.3761 | 0 | 129.304 | 0 | 1.1838 | 0 | 1.293 | 0 | 1.1838 | 1.293 | 37.7194 | 26.0803 | 36.5357
39043.5499 | 2045 | 0 | 39043.5499 | 2282 | 0 |  | 762 | 952 | 124.8474 | 0 | 139.3162 | 0 | 1.2485 | 0 | 1.3932 | 0 | 1.2485 | 1.3932 | 30.5809 | 17.0193 | 29.3325
39043.5504 | 2450 | 0 | 39043.5504 | 2576 | 0 |  | 804.5 | 994.5 | 149.5726 | 0 | 157.265 | 0 | 1.4957 | 0 | 1.5726 | 0 | 1.4957 | 1.5726 | 8.9951 | 3.6638 | 7.4994
39043.5509 | 2174 | 0 | 39043.5509 | 2492 | 0 |  | 846 | 1036 | 132.7228 | 0 | 152.1368 | 0 | 1.3272 | 0 | 1.5214 | 0 | 1.3272 | 1.5214 | 22.8326 | 7.1581 | 21.5053
39043.5514 | 2548 | 0 | 39043.5514 | 2336 | 0 |  | 888.5 | 1078.5 | 155.5556 | 0 | 142.6129 | 0 | 1.5556 | 0 | 1.4261 | 0 | 1.5556 | 1.4261 | 4.803 | 14.3142 | 3.2474
39043.5518 | 2604 | 0 | 39043.5519 | 2373 | 0 |  | 930.5 | 1120.5 | 158.9744 | 0 | 144.8718 | 0 | 1.5897 | 0 | 1.4487 | 0 | 1.5897 | 1.4487 | 2.5492 | 12.5318 | 0.95941
39043.5523 | 2572 | 0 | 39043.5523 | 2512 | 0 |  | 972 | 1162 | 157.0208 | 0 | 153.3578 | 0 | 1.5702 | 0 | 1.5336 | 0 | 1.5702 | 1.5336 | 3.825 | 6.3049 | 2.2548
39043.5528 | 2499 | 0 | 39043.5528 | 2654 | 0 |  | 1014 | 1204 | 152.5641 | 0 | 162.0269 | 0 | 1.5256 | 0 | 1.6203 | 0 | 1.5256 | 1.6203 | 6.8579 | 0.61718 | 5.3323
39043.5533 | 2118 | 0 | 39043.5533 | 2194 | 0 |  | 1056.5 | 1246.5 | 129.304 | 0 | 133.9438 | 0 | 1.293 | 0 | 1.3394 | 0 | 1.293 | 1.3394 | 26.0803 | 21.7129 | 24.7872
39043.5538 | 2063 | 0 | 39043.5538 | 2267 | 0 |  | 1098 | 1288 | 125.9463 | 0 | 138.4005 | 0 | 1.2595 | 0 | 1.384 | 0 | 1.2595 | 1.384 | 29.4416 | 17.7936 | 28.1821
39043.5543 | 1647 | 0 | 39043.5543 | 2053 | 0 |  | 1140 | 1330 | 100.5495 | 0 | 125.3358 | 0 | 1.0055 | 0 | 1.2534 | 0 | 1.0055 | 1.2534 | 62.136 | 30.0721 | 61.1305
39043.5547 | 2109 | 0 | 39043.5548 | 2208 | 0 |  | 1182 | 1372 | 128.7546 | 0 | 134.7985 | 0 | 1.2875 | 0 | 1.348 | 0 | 1.2875 | 1.348 | 26.6183 | 20.9411 | 25.3308
39043.5552 | 2410 | 0 | 39043.5553 | 2312 | 0 |  | 1224 | 1414 | 147.1306 | 0 | 141.1477 | 0 | 1.4713 | 0 | 1.4115 | 0 | 1.4713 | 1.4115 | 10.8041 | 15.5009 | 9.3328
39043.5557 | 2422 | 0 | 39043.5557 | 2497 | 0 |  | 1266 | 1456 | 147.8632 | 0 | 152.442 | 0 | 1.4786 | 0 | 1.5244 | 0 | 1.4786 | 1.5244 | 10.2552 | 6.9435 | 8.7765
39043.5562 | 2231 | 0 | 39043.5562 | 1872 | 0 |  | 1308 | 1498 | 136.2027 | 0 | 114.2857 | 0 | 1.362 | 0 | 1.1429 | 0 | 1.362 | 1.1429 | 19.6943 | 42.6485 | 18.3323
39043.5567 | 1699 | 0 | 39043.5567 | 913 | 0 |  | 1350 | 1540 | 103.7241 | 0 | 55.7387 | 0 | 1.0372 | 0 | 0.55739 | 0 | 1.0372 | 0.55739 | 57.1736 | 192.4841 | 56.1364
39043.5572 | 2467 | 0 | 39043.5572 | 1024 | 0 |  | 1392 | 1582 | 150.6105 | 0 | 62.5153 | 0 | 1.5061 | 0 | 0.62515 | 0 | 1.5061 | 0.62515 | 8.244 | 160.7793 | 6.7379

## B3-B4
Open Burn Test 12 |  |  | 2006-11-22 | 13:02 |  |  | Vs = |  | 160.2796 |  | R = | 100
Mixed | 7-C | Tray A | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 3 & 4 | Cable B | Odd -Even
Time-19 | N11 | N12 | Time-20 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R4-G | R3-4
39043.5392 | 1 | 0 | 39043.5392 | 1 | 0 |  | -164.5 | 25.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262438 | 262438 | 262437.9994
39043.5397 | 1 | 0 | 39043.5397 | 1 | 0 |  | -122.5 | 67.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262438 | 262438 | 262437.9994
39043.5401 | 1 | 0 | 39043.5402 | 1 | 0 |  | -80.5 | 109.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262438 | 262438 | 262437.9994
39043.5406 | 1 | 0 | 39043.5406 | 1 | 0 |  | -38.5 | 151.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262438 | 262438 | 262437.9994
39043.5411 | 1 | 0 | 39043.5411 | 1 | 0 |  | 3.5 | 193.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262438 | 262438 | 262437.9994
39043.5416 | 1 | 0 | 39043.5416 | 1 | 0 |  | 45.5 | 235.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262438 | 262438 | 262437.9994
39043.5421 | 1 | 0 | 39043.5421 | 1 | 0 |  | 87.5 | 277.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262438 | 262438 | 262437.9994
39043.5426 | 1 | 0 | 39043.5426 | 1 | 0 |  | 129.5 | 319.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262438 | 262438 | 262437.9994
39043.5431 | 1 | 0 | 39043.5431 | 1 | 0 |  | 171.5 | 361.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262438 | 262438 | 262437.9994
39043.5435 | 1 | 0 | 39043.5436 | 1 | 0 |  | 213.5 | 403.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262438 | 262438 | 262437.9994
39043.544 | 1 | 0 | 39043.544 | 170 | 0 |  | 255.5 | 445.5 | 0.06105 | 0 | 10.3785 | 0 | 0.0006105 | 0 | 0.10379 | 0 | 0.0006105 | 0.10379 | 262438 | 1444.3412 | 262437.9994
39043.5445 | 988 | 920 | 39043.5445 | 1265 | 1198 |  | 297.5 | 487.5 | 60.3175 | 56.1661 | 77.2283 | 73.138 | 0.60317 | 0.56166 | 0.77228 | 0.73138 | 0.041514 | 0.040904 | 3645.7748 | 3984.7049 | 76.0671
39043.545 | 2236 | 137 | 39043.545 | 1513 | 419 |  | 339.5 | 529.5 | 136.5079 | 8.3639 | 92.3687 | 25.58 | 1.3651 | 0.083639 | 0.92369 | 0.2558 | 1.2814 | 0.66789 | 17.1961 | 82.8525 | 83.4717
39043.5455 | 1750 | 373 | 39043.5455 | 1193 | 707 |  | 381.5 | 571.5 | 106.8376 | 22.7717 | 72.8327 | 43.1624 | 1.0684 | 0.22772 | 0.72833 | 0.43162 | 0.84066 | 0.2967 | 55.2823 | 180.6528 | 86.696
39043.546 | 1850 | 393 | 39043.546 | 2138 | 333 |  | 423.5 | 613.5 | 112.9426 | 23.9927 | 130.525 | 20.3297 | 1.1294 | 0.23993 | 1.3053 | 0.2033 | 0.8895 | 1.102 | 33041.1824 | 27.0167 | 20.6954
| 2026 | 0 | 39043.5465 | 2528 | 0 |  | 466 | 656 | 123.6874 | 0 | 154.3346 | 0 | 1.2369 | 0 | 1.5433 | 0 | 1.2369 | 1.5433 | 29.5844 | 3.8521 | 28.3475
39043.5469 | 2201 | 0 | 39043.547 | 2474 | 0 |  | 507.5 | 697.5 | 134.3712 | 0 | 151.0379 | 0 | 1.3437 | 0 | 1.5104 | 0 | 1.3437 | 1.5104 | 19.2812 | 6.1188 | 17.9375
39043.5474 | 2129 | 1 | 39043.5474 | 2514 | 1 |  | 549.5 | 739.5 | 129.9756 | 0.06105 | 153.4799 | 0.06105 | 1.2998 | 0.0006105 | 1.5348 | 0.0006105 | 1.2991 | 1.5342 | 23.5757 | 4.4396 | 2105.821
39043.5479 | 2331 | 0 | 39043.5479 | 2510 | 0 |  | 591.5 | 781.5 | 142.3077 | 0 | 153.2357 | 0 | 1.4231 | 0 | 1.5324 | 0 | 1.4231 | 1.5324 | 12.6289 | 4.5968 | 11.2058
39043.5484 | 2015 | 2 | 39043.5484 | 1965 | 260 |  | 633.5 | 823.5 | 123.0159 | 0.1221 | 119.9634 | 15.873 | 1.2302 | 0.001221 | 1.1996 | 0.15873 | 1.2289 | 1.0409 | 30.3607 | 77.8173 | 13312.1141
39043.5489 | 1967 | 344 | 39043.5489 | 2039 | 416 |  | 675.5 | 865.5 | 120.0855 | 21.0012 | 124.4811 | 25.3968 | 1.2009 | 0.21001 | 1.2448 | 0.25397 | 0.99084 | 0.99084 | 61.7609 | 61.7609 | 34.8929
39043.5494 | 1350 | 743 | 39043.5494 | 2058 | 608 |  | 717.5 | 907.5 | 82.4176 | 45.3602 | 125.641 | 37.1184 | 0.82418 | 0.4536 | 1.2564 | 0.37118 | 0.37057 | 0.88523 | 37.0941 | 26.243 | 14.8949
39043.5499 | 2300 | 0 | 39043.5499 | 2563 | 0 |  | 759.5 | 949.5 | 140.4151 | 0 | 156.4713 | 0 | 1.4042 | 0 | 1.5647 | 0 | 1.4042 | 1.5647 | 14.147 | 2.4339 | 12.7428
39043.5503 | 2546 | 0 | 39043.5504 | 2225 | 0 |  | 801.5 | 991.5 | 155.4335 | 0 | 135.8364 | 0 | 1.5543 | 0 | 1.3584 | 0 | 1.5543 | 1.3584 | 3.1178 | 17.9946 | 1.5635
39043.5508 | 2609 | 0 | 39043.5508 | 2503 | 0 |  | 843.5 | 1033.5 | 159.2796 | 0 | 152.8083 | 0 | 1.5928 | 0 | 1.5281 | 0 | 1.5928 | 1.5281 | 0.62783 | 4.8893 | 0.96497
| 2591 | 0 | 39043.5513 | 2018 | 0 |  | 886 | 1076 | 158.1807 | 0 | 123.199 | 0 | 1.5818 | 0 | 1.232 | 0 | 1.5818 | 1.232 | 1.3269 | 30.0981 | 0.25491
39043.5518 | 2573 | 0 | 39043.5518 | 2356 | 0 |  | 927.5 | 1117.5 | 157.0818 | 0 | 143.8339 | 0 | 1.5708 | 0 | 1.4383 | 0 | 1.5708 | 1.4383 | 2.0358 | 11.4338 | 0.46494
39043.5523 | 2110 | 0 | 39043.5523 | 2594 | 0 |  | 969.5 | 1159.5 | 128.8156 | 0 | 158.3639 | 0 | 1.2882 | 0 | 1.5836 | 0 | 1.2882 | 1.5836 | 24.4256 | 1.2097 | 23.1374
39043.5528 | 2558 | 0 | 39043.5528 | 2294 | 0 |  | 1011.5 | 1201.5 | 156.1661 | 0 | 140.0488 | 0 | 1.5617 | 0 | 1.4005 | 0 | 1.5617 | 1.4005 | 2.6341 | 14.4455 | 1.0724
39043.5533 | 2609 | 0 | 39043.5533 | 2107 | 0 |  | 1053.5 | 1243.5 | 159.2796 | 0 | 128.6325 | 0 | 1.5928 | 0 | 1.2863 | 0 | 1.5928 | 1.2863 | 0.62783 | 24.6028 | 0.96497
39043.5537 | 2411 | 0 | 39043.5538 | 2287 | 0 |  | 1095.5 | 1285.5 | 147.1917 | 0 | 139.6215 | 0 | 1.4719 | 0 | 1.3962 | 0 | 1.4719 | 1.3962 | 8.8917 | 14.7958 | 7.4198
39043.5542 | 2182 | 222 | 39043.5542 | 2249 | 482 |  | 1137.5 | 1327.5 | 133.2112 | 13.5531 | 137.3016 | 29.4261 | 1.3321 | 0.13553 | 1.373 | 0.29426 | 1.1966 | 1.0788 | 17.3335 | 37.128 | 26.9998
39043.5547 | 2408 | 0 | 39043.5547 | 2249 | 0 |  | 1179.5 | 1369.5 | 147.0085 | 0 | 137.3016 | 0 | 1.4701 | 0 | 1.373 | 0 | 1.4701 | 1.373 | 9.0274 | 16.7354 | 7.5573
39043.5552 | 2469 | 0 | 39043.5552 | 2145 | 0 |  | 1221.5 | 1411.5 | 150.7326 | 0 | 130.9524 | 0 | 1.5073 | 0 | 1.3095 | 0 | 1.5073 | 1.3095 | 6.3337 | 22.3953 | 4.8264
39043.5557 | 2057 | 29 | 39043.5557 | 1987 | 403 |  | 1263.5 | 1453.5 | 125.58 | 1.7705 | 121.3065 | 24.6032 | 1.2558 | 0.017705 | 1.2131 | 0.24603 | 1.2381 | 0.96703 | 28.1217 | 422.9264 | 1504.2536
39043.5562 | 2314 | 129 | 39043.5562 | 1752 | 504 |  | 1305.5 | 1495.5 | 141.2698 | 7.8755 | 106.9597 | 30.7692 | 1.4127 | 0.078755 | 1.0696 | 0.30769 | 1.3339 | 0.7619 | 11.843 | 29.0382 | 31.8155
39043.5567 | 1050 | 740 | 39043.5567 | 1299 | 928 |  | 1347.5 | 1537.5 | 64.1026 | 45.177 | 79.304 | 56.6545 | 0.64103 | 0.45177 | 0.79304 | 0.56654 | 0.18926 | 0.2265 | 1026.6797 | 472.6748 | 93.1766
39043.5572 | 1855 | 265 | 39043.5572 | 1378 | 407 |  | 1389.5 | 1579.5 | 113.2479 | 16.1783 | 84.127 | 24.8474 | 1.1325 | 0.16178 | 0.84127 | 0.24847 | 0.9707 | 0.5928 | 49.426 | 845.4169 | 170.5374

## A2-C6
Open Burn Test 12 |  |  | 2006-11-22 | 13:02 |  |  | Vs = |  | 162.9658 |  | R = | 100
Mixed | 7-C | Tray A | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 2 & 6 | Cable A | Even - | Cable C |  | Even
Time-17 | N11 | N12 | Time-18 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R6-G | R2-6
39043.5391 | 1 | 0 | 39043.5391 | 1 | 0 |  | -167.5 | 22.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 266838 | 266838 | 266837.9994
39043.5396 | 1 | 0 | 39043.5396 | 1 | 0 |  | -125.5 | 64.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 266838 | 266838 | 266837.9994
39043.5401 | 1 | 0 | 39043.5401 | 1 | 0 |  | -83.5 | 106.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 266838 | 266838 | 266837.9994
39043.5406 | 1 | 0 | 39043.5406 | 1 | 0 |  | -41.5 | 148.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 266838 | 266838 | 266837.9994
39043.5411 | 1 | 0 | 39043.5411 | 1 | 0 |  | 0.5 | 190.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 266838 | 266838 | 266837.9994
39043.5416 | 1 | 0 | 39043.5416 | 1 | 0 |  | 42.5 | 232.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 266838 | 266838 | 266837.9994
39043.542 | 1 | 0 | 39043.5421 | 1 | 0 |  | 84.5 | 274.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 266838 | 266838 | 266837.9994
39043.5425 | 1 | 0 | 39043.5425 | 1 | 0 |  | 126.5 | 316.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 266838 | 266838 | 266837.9994
39043.543 | 1 | 0 | 39043.543 | 727 | 0 |  | 168.5 | 358.5 | 0.06105 | 0 | 44.3834 | 0 | 0.0006105 | 0 | 0.44383 | 0 | 0.0006105 | 0.44383 | 266838 | 267.1774 | 266837.9994
39043.5435 | 1 | 0 | 39043.5435 | 2205 | 0 |  | 210.5 | 400.5 | 0.06105 | 0 | 134.6154 | 0 | 0.0006105 | 0 | 1.3462 | 0 | 0.0006105 | 1.3462 | 266838 | 21.0603 | 266837.9994
39043.544 | 164 | 0 | 39043.544 | 2493 | 0 |  | 252.5 | 442.5 | 10.0122 | 0 | 152.1978 | 0 | 0.10012 | 0 | 1.522 | 0 | 0.10012 | 1.522 | 1527.6707 | 7.075 | 1527.5706
39043.5445 | 2237 | 0 | 39043.5445 | 2182 | 0 |  | 294.5 | 484.5 | 136.569 | 0 | 133.2112 | 0 | 1.3657 | 0 | 1.3321 | 0 | 1.3657 | 1.3321 | 19.3286 | 22.3364 | 17.9629
39043.545 | 2404 | 0 | 39043.545 | 2575 | 0 |  | 336.5 | 526.5 | 146.7643 | 0 | 157.2039 | 0 | 1.4676 | 0 | 1.572 | 0 | 1.4676 | 1.572 | 11.0391 | 3.6652 | 9.5715
39043.5455 | 2527 | 0 | 39043.5455 | 2646 | 0 |  | 378.5 | 568.5 | 154.2735 | 0 | 161.5385 | 0 | 1.5427 | 0 | 1.6154 | 0 | 1.5427 | 1.6154 | 5.6343 | 0.8836 | 4.0916
39043.5459 | 2486 | 0 | 39043.5459 | 2164 | 0 |  | 420.5 | 610.5 | 151.7705 | 0 | 132.1123 | 0 | 1.5177 | 0 | 1.3211 | 0 | 1.5177 | 1.3211 | 7.3765 | 23.354 | 5.8588
39043.5464 | 2075 | 0 | 39043.5464 | 2121 | 0 |  | 462.5 | 652.5 | 126.6789 | 0 | 129.4872 | 0 | 1.2668 | 0 | 1.2949 | 0 | 1.2668 | 1.2949 | 28.6448 | 25.8548 | 27.378
39043.5469 | 2631 | 0 | 39043.5469 | 2603 | 0 |  | 504.5 | 694.5 | 160.6227 | 0 | 158.9133 | 0 | 1.6062 | 0 | 1.5891 | 0 | 1.6062 | 1.5891 | 1.4588 | 2.5501 | 0.14747
39043.5474 | 2640 | 0 | 39043.5474 | 2423 | 0 |  | 546.5 | 736.5 | 161.1722 | 0 | 147.9243 | 0 | 1.6117 | 0 | 1.4792 | 0 | 1.6117 | 1.4792 | 1.1129 | 10.1684 | 0.49884
39043.5479 | 2317 | 0 | 39043.5479 | 2653 | 0 |  | 588.5 | 778.5 | 141.453 | 0 | 161.9658 | 0 | 1.4145 | 0 | 1.6197 | 0 | 1.4145 | 1.6197 | 15.2085 | 0.61741 | 13.7939
39043.5484 | 2419 | 0 | 39043.5484 | 2224 | 0 |  | 630.5 | 820.5 | 147.6801 | 0 | 135.7753 | 0 | 1.4768 | 0 | 1.3578 | 0 | 1.4768 | 1.3578 | 10.3506 | 20.0261 | 8.8738
39043.5489 | 2250 | 0 | 39043.5489 | 2106 | 0 |  | 672.5 | 862.5 | 137.3626 | 0 | 128.5714 | 0 | 1.3736 | 0 | 1.2857 | 0 | 1.3736 | 1.2857 | 18.6391 | 26.7512 | 17.2655
39043.5493 | 2108 | 0 | 39043.5494 | 2265 | 0 |  | 714.5 | 904.5 | 128.6935 | 0 | 138.2784 | 0 | 1.2869 | 0 | 1.3828 | 0 | 1.2869 | 1.3828 | 26.6309 | 17.8534 | 25.344
39043.5498 | 2216 | 0 | 39043.5498 | 2612 | 0 |  | 756.5 | 946.5 | 135.2869 | 0 | 159.4628 | 0 | 1.3529 | 0 | 1.5946 | 0 | 1.3529 | 1.5946 | 20.4594 | 2.1968 | 19.1065
39043.5503 | 2040 | 0 | 39043.5503 | 2502 | 0 |  | 798.5 | 988.5 | 124.5421 | 0 | 152.7473 | 0 | 1.2454 | 0 | 1.5275 | 0 | 1.2454 | 1.5275 | 30.852 | 6.6898 | 29.6065
39043.5508 | 2321 | 0 | 39043.5508 | 2153 | 0 |  | 840.5 | 1030.5 | 141.6972 | 0 | 131.4408 | 0 | 1.417 | 0 | 1.3144 | 0 | 1.417 | 1.3144 | 15.0099 | 23.9842 | 13.5929
39043.5513 | 2191 | 0 | 39043.5513 | 2476 | 0 |  | 882.5 | 1072.5 | 133.7607 | 0 | 151.16 | 0 | 1.3376 | 0 | 1.5116 | 0 | 1.3376 | 1.5116 | 21.8339 | 7.8102 | 20.4963
39043.5518 | 2230 | 0 | 39043.5518 | 2499 | 0 |  | 924.5 | 1114.5 | 136.1416 | 0 | 152.5641 | 0 | 1.3614 | 0 | 1.5256 | 0 | 1.3614 | 1.5256 | 19.7031 | 6.8179 | 18.3417
39043.5523 | 2459 | 0 | 39043.5523 | 2446 | 0 |  | 966.5 | 1156.5 | 150.1221 | 0 | 149.3284 | 0 | 1.5012 | 0 | 1.4933 | 0 | 1.5012 | 1.4933 | 8.5555 | 9.1325 | 7.0543
39043.5527 | 2041 | 0 | 39043.5528 | 2387 | 0 |  | 1008.5 | 1198.5 | 124.6032 | 0 | 145.7265 | 0 | 1.246 | 0 | 1.4573 | 0 | 1.246 | 1.4573 | 30.7878 | 11.8299 | 29.5418
39043.5532 | 2614 | 0 | 39043.5532 | 2538 | 0 |  | 1050.5 | 1240.5 | 159.5849 | 0 | 154.9451 | 0 | 1.5958 | 0 | 1.5495 | 0 | 1.5958 | 1.5495 | 2.1186 | 5.1765 | 0.52274
39043.5537 | 2160 | 0 | 39043.5537 | 2651 | 0 |  | 1092.5 | 1282.5 | 131.8681 | 0 | 161.8437 | 0 | 1.3187 | 0 | 1.6184 | 0 | 1.3187 | 1.6184 | 23.5824 | 0.69332 | 22.2637
39043.5542 | 2127 | 0 | 39043.5542 | 2357 | 0 |  | 1134.5 | 1324.5 | 129.8535 | 0 | 143.895 | 0 | 1.2985 | 0 | 1.4389 | 0 | 1.2985 | 1.4389 | 25.4998 | 13.2533 | 24.2012
39043.5547 | 2618 | 0 | 39043.5547 | 2596 | 0 |  | 1176.5 | 1366.5 | 159.8291 | 0 | 158.486 | 0 | 1.5983 | 0 | 1.5849 | 0 | 1.5983 | 1.5849 | 1.9626 | 2.8267 | 0.36428
39043.5552 | 2088 | 0 | 39043.5552 | 2034 | 0 |  | 1218.5 | 1408.5 | 127.4725 | 0 | 124.1758 | 0 | 1.2747 | 0 | 1.2418 | 0 | 1.2747 | 1.2418 | 27.8439 | 31.238 | 26.5691
39043.5557 | 2156 | 0 | 39043.5557 | 2131 | 0 |  | 1260.5 | 1450.5 | 131.6239 | 0 | 130.0977 | 0 | 1.3162 | 0 | 1.301 | 0 | 1.3162 | 1.301 | 23.8117 | 25.2642 | 22.4954
39043.5561 | 1994 | 19 | 39043.5562 | 1918 | 39 |  | 1302.5 | 1492.5 | 121.7338 | 1.16 | 117.094 | 2.381 | 1.2173 | 0.0116 | 1.1709 | 0.02381 | 1.2057 | 1.1471 | 34.9883 | 42.5101 | 1030.5001
39043.5566 | 1354 | 767 | 39043.5566 | 1410 | 820 |  | 1344.5 | 1534.5 | 82.6618 | 46.8254 | 86.0806 | 50.0611 | 0.82662 | 0.46825 | 0.86081 | 0.50061 | 0.35836 | 0.3602 | 358.399 | 348.661 | 55.5612
39043.5571 | 1201 | 579 | 39043.5571 | 1060 | 825 |  | 1386.5 | 1576.5 | 73.3211 | 35.348 | 64.7131 | 50.3663 | 0.73321 | 0.35348 | 0.64713 | 0.50366 | 0.37973 | 0.14347 | 217.9853 | 1121.7864 | 141.034

## A2-C5
Open Burn Test 12 |  |  | 2006-11-22 | 13:02 |  |  | Vs = |  | 163.149 |  | R = | 100
Mixed | 7-C | Tray A | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 2 & 5 | Cable A | Even - | Cable C |  | Odd
Time-15 | N11 | N12 | Time-16 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R5-G | R2-5
39043.5391 | 1 | 0 | 39043.5391 | 1 | 0 |  | -170 | 20 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 267138 | 267138 | 267137.9994
39043.5396 | 1 | 0 | 39043.5396 | 1 | 0 |  | -128 | 62 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 267138 | 267138 | 267137.9994
39043.5401 | 1 | 0 | 39043.5401 | 1 | 0 |  | -86 | 104 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 267138 | 267138 | 267137.9994
39043.5406 | 1 | 0 | 39043.5406 | 1 | 0 |  | -44 | 146 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 267138 | 267138 | 267137.9994
39043.541 | 1 | 0 | 39043.5411 | 1 | 0 |  | -2 | 188 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 267138 | 267138 | 267137.9994
39043.5415 | 1 | 0 | 39043.5416 | 1 | 0 |  | 40 | 230 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 267138 | 267138 | 267137.9994
39043.542 | 1 | 0 | 39043.542 | 1 | 0 |  | 82 | 272 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 267138 | 267138 | 267137.9994
39043.5425 | 1 | 0 | 39043.5425 | 1 | 0 |  | 124 | 314 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 267138 | 267138 | 267137.9994
39043.543 | 1 | 0 |  | 336 | 0 |  | 165 | 355 | 0.06105 | 0 | 20.5128 | 0 | 0.0006105 | 0 | 0.20513 | 0 | 0.0006105 | 0.20513 | 267138 | 695.3512 | 267137.9994
39043.5435 | 1 | 0 | 39043.5435 | 1237 | 0 |  | 208 | 398 | 0.06105 | 0 | 75.5189 | 0 | 0.0006105 | 0 | 0.75519 | 0 | 0.0006105 | 0.75519 | 267138 | 116.0372 | 267137.9994
39043.544 | 118 | 0 | 39043.544 | 2556 | 0 |  | 250 | 440 | 7.2039 | 0 | 156.044 | 0 | 0.072039 | 0 | 1.5604 | 0 | 0.072039 | 1.5604 | 2164.7288 | 4.5532 | 2164.6568
39043.5444 | 2286 | 0 | 39043.5445 | 2044 | 0 |  | 292 | 482 | 139.5604 | 0 | 124.7863 | 0 | 1.3956 | 0 | 1.2479 | 0 | 1.3956 | 1.2479 | 16.902 | 30.7427 | 15.5064
39043.5449 | 2238 | 0 | 39043.545 | 2169 | 0 |  | 334 | 524 | 136.63 | 0 | 132.4176 | 0 | 1.3663 | 0 | 1.3242 | 0 | 1.3663 | 1.3242 | 19.4093 | 23.2079 | 18.043
39043.5454 | 2173 | 0 | 39043.5454 | 2648 | 0 |  | 376 | 566 | 132.6618 | 0 | 161.6606 | 0 | 1.3266 | 0 | 1.6166 | 0 | 1.3266 | 1.6166 | 22.9811 | 0.92069 | 21.6545
39043.5459 | 2119 | 0 | 39043.5459 | 2281 | 0 |  | 418 | 608 | 129.3651 | 0 | 139.2552 | 0 | 1.2937 | 0 | 1.3926 | 0 | 1.2937 | 1.3926 | 26.1151 | 17.1583 | 24.8215
39043.5464 | 2191 | 0 | 39043.5464 | 2352 | 0 |  | 459.5 | 649.5 | 133.7607 | 0 | 143.5897 | 0 | 1.3376 | 0 | 1.4359 | 0 | 1.3376 | 1.4359 | 21.9708 | 13.6216 | 20.6332
39043.5469 | 2590 | 0 | 39043.5469 | 2130 | 0 |  | 502 | 692 | 158.1197 | 0 | 130.0366 | 0 | 1.5812 | 0 | 1.3004 | 0 | 1.5812 | 1.3004 | 3.1807 | 25.4638 | 1.5995
39043.5474 | 2086 | 0 | 39043.5474 | 2301 | 0 |  | 544 | 734 | 127.3504 | 0 | 140.4762 | 0 | 1.2735 | 0 | 1.4048 | 0 | 1.2735 | 1.4048 | 28.1103 | 16.1399 | 26.8368
39043.5478 | 2042 | 0 | 39043.5479 | 2072 | 0 |  | 585.5 | 775.5 | 124.6642 | 0 | 126.4957 | 0 | 1.2466 | 0 | 1.265 | 0 | 1.2466 | 1.265 | 30.8707 | 28.9759 | 29.6241
39043.5483 | 2051 | 0 | 39043.5483 | 2135 | 0 |  | 627.5 | 817.5 | 125.2137 | 0 | 130.3419 | 0 | 1.2521 | 0 | 1.3034 | 0 | 1.2521 | 1.3034 | 30.2964 | 25.17 | 29.0443
39043.5488 | 2616 | 0 | 39043.5488 | 2108 | 0 |  | 670 | 860 | 159.707 | 0 | 128.6935 | 0 | 1.5971 | 0 | 1.2869 | 0 | 1.5971 | 1.2869 | 2.1552 | 26.7732 | 0.55813
39043.5493 | 2549 | 0 | 39043.5493 | 2402 | 0 |  | 712 | 902 | 155.6166 | 0 | 146.6422 | 0 | 1.5562 | 0 | 1.4664 | 0 | 1.5562 | 1.4664 | 4.8403 | 11.2565 | 3.2842
39043.5498 | 2544 | 0 | 39043.5498 | 2124 | 0 |  | 753.5 | 943.5 | 155.3114 | 0 | 129.6703 | 0 | 1.5531 | 0 | 1.2967 | 0 | 1.5531 | 1.2967 | 5.0464 | 25.8183 | 3.4933
39043.5503 | 2252 | 0 | 39043.5503 | 2408 | 0 |  | 796 | 986 | 137.4847 | 0 | 147.0085 | 0 | 1.3748 | 0 | 1.4701 | 0 | 1.3748 | 1.4701 | 18.667 | 10.9792 | 17.2921
39043.5508 | 2643 | 0 | 39043.5508 | 2435 | 0 |  | 837.5 | 1027.5 | 161.3553 | 0 | 148.6569 | 0 | 1.6136 | 0 | 1.4866 | 0 | 1.6136 | 1.4866 | 1.1116 | 9.7487 | 0.50194
39043.5512 | 2200 | 0 | 39043.5513 | 2369 | 0 |  | 879.5 | 1069.5 | 134.3101 | 0 | 144.6276 | 0 | 1.3431 | 0 | 1.4463 | 0 | 1.3431 | 1.4463 | 21.4718 | 12.8062 | 20.1287
39043.5517 | 2206 | 0 | 39043.5518 | 2600 | 0 |  | 922 | 1112 | 134.6764 | 0 | 158.7302 | 0 | 1.3468 | 0 | 1.5873 | 0 | 1.3468 | 1.5873 | 21.1414 | 2.7838 | 19.7947
39043.5522 | 2039 | 0 | 39043.5522 | 2656 | 0 |  | 963.5 | 1153.5 | 124.4811 | 0 | 162.149 | 0 | 1.2448 | 0 | 1.6215 | 0 | 1.2448 | 1.6215 | 31.0633 | 0.61672 | 29.8185
39043.5527 | 2040 | 0 | 39043.5527 | 2581 | 0 |  | 1005.5 | 1195.5 | 124.5421 | 0 | 157.5702 | 0 | 1.2454 | 0 | 1.5757 | 0 | 1.2454 | 1.5757 | 30.999 | 3.5405 | 29.7536
39043.5532 | 2606 | 0 | 39043.5532 | 2210 | 0 |  | 1047.5 | 1237.5 | 159.0965 | 0 | 134.9206 | 0 | 1.591 | 0 | 1.3492 | 0 | 1.591 | 1.3492 | 2.5472 | 20.9222 | 0.95623
39043.5537 | 2054 | 0 | 39043.5537 | 2616 | 0 |  | 1089.5 | 1279.5 | 125.3968 | 0 | 159.707 | 0 | 1.254 | 0 | 1.5971 | 0 | 1.254 | 1.5971 | 30.1061 | 2.1552 | 28.8522
39043.5542 | 2118 | 0 | 39043.5542 | 2302 | 0 |  | 1131.5 | 1321.5 | 129.304 | 0 | 140.5372 | 0 | 1.293 | 0 | 1.4054 | 0 | 1.293 | 1.4054 | 26.1747 | 16.0895 | 24.8817
39043.5547 | 2380 | 0 | 39043.5547 | 2136 | 0 |  | 1173.5 | 1363.5 | 145.2991 | 0 | 130.4029 | 0 | 1.453 | 0 | 1.304 | 0 | 1.453 | 1.304 | 12.2849 | 25.1114 | 10.8319
39043.5551 | 2580 | 0 | 39043.5552 | 2393 | 0 |  | 1215.5 | 1405.5 | 157.5092 | 0 | 146.0928 | 0 | 1.5751 | 0 | 1.4609 | 0 | 1.5751 | 1.4609 | 3.5806 | 11.6749 | 2.0055
39043.5556 | 2059 | 0 | 39043.5556 | 2392 | 0 |  | 1257.5 | 1447.5 | 125.7021 | 0 | 146.0317 | 0 | 1.257 | 0 | 1.4603 | 0 | 1.257 | 1.4603 | 29.7902 | 11.7216 | 28.5332
39043.5561 | 2013 | 5 | 39043.5561 | 2250 | 3 |  | 1299.5 | 1489.5 | 122.8938 | 0.30525 | 137.3626 | 0.18315 | 1.2289 | 0.0030525 | 1.3736 | 0.0018315 | 1.2259 | 1.3718 | 33.2767 | 18.8732 | 2077.8882
39043.5566 | 1428 | 723 | 39043.5566 | 1323 | 668 |  | 1341.5 | 1531.5 | 87.1795 | 44.1392 | 80.7692 | 40.7814 | 0.87179 | 0.44139 | 0.80769 | 0.40781 | 0.4304 | 0.39988 | 250.3784 | 347.5958 | 56.0021
39043.5571 | 1636 | 511 | 39043.5571 | 1202 | 662 |  | 1383.5 | 1573.5 | 99.8779 | 31.1966 | 73.3822 | 40.4151 | 0.99878 | 0.31197 | 0.73382 | 0.40415 | 0.68681 | 0.32967 | 86.0222 | 640.4969 | 88.9296

## A2-B4
Open Burn Test 12 |  |  | 2006-11-22 | 13:02 |  |  | Vs = |  | 162.3553 |  | R = | 100
Mixed | 7-C | Tray A | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 2 & 4 | Cable A | Even - | Cable B |  | Even
Time-13 | N11 | N12 | Time-14 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R4-G | R2-4
39043.5391 | 1 | 0 | 39043.5391 | 1 | 0 |  | -173 | 17 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265838 | 265838 | 265837.9994
39043.5395 | 1 | 0 | 39043.5396 | 1 | 0 |  | -131 | 59 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265838 | 265838 | 265837.9994
39043.54 | 1 | 0 | 39043.5401 | 1 | 0 |  | -89 | 101 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265838 | 265838 | 265837.9994
39043.5405 | 1 | 0 | 39043.5405 | 1 | 0 |  | -47 | 143 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265838 | 265838 | 265837.9994
39043.541 | 1 | 0 | 39043.541 | 1 | 0 |  | -5 | 185 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265838 | 265838 | 265837.9994
39043.5415 | 1 | 0 | 39043.5415 | 1 | 0 |  | 37 | 227 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265838 | 265838 | 265837.9994
39043.542 | 1 | 0 | 39043.542 | 1 | 0 |  | 79 | 269 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265838 | 265838 | 265837.9994
39043.5425 | 1 | 0 | 39043.5425 | 1 | 0 |  | 121 | 311 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265838 | 265838 | 265837.9994
39043.543 | 1 | 0 | 39043.543 | 1 | 0 |  | 163 | 353 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265838 | 265838 | 265837.9994
39043.5434 | 1 | 0 | 39043.5435 | 1 | 0 |  | 205 | 395 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265838 | 265838 | 265837.9994
39043.5439 | 10 | 0 | 39043.5439 | 165 | 0 |  | 247 | 437 | 0.6105 | 0 | 10.0733 | 0 | 0.006105 | 0 | 0.10073 | 0 | 0.006105 | 0.10073 | 26493.8 | 1511.7455 | 26493.7939
39043.5444 | 1835 | 0 | 39043.5444 | 2222 | 0 |  | 289 | 479 | 112.0269 | 0 | 135.6532 | 0 | 1.1203 | 0 | 1.3565 | 0 | 1.1203 | 1.3565 | 44.9253 | 19.6841 | 43.8051
39043.5449 | 2274 | 0 | 39043.5449 | 2034 | 0 |  | 331 | 521 | 138.8278 | 0 | 124.1758 | 0 | 1.3883 | 0 | 1.2418 | 0 | 1.3883 | 1.2418 | 16.9472 | 30.7463 | 15.559
39043.5454 | 2062 | 0 | 39043.5454 | 2149 | 0 |  | 373 | 563 | 125.8852 | 0 | 131.1966 | 0 | 1.2589 | 0 | 1.312 | 0 | 1.2589 | 1.312 | 28.9709 | 23.7497 | 27.712
39043.5459 | 2613 | 0 | 39043.5459 | 2163 | 0 |  | 415 | 605 | 159.5238 | 0 | 132.0513 | 0 | 1.5952 | 0 | 1.3205 | 0 | 1.5952 | 1.3205 | 1.775 | 22.9487 | 0.17973
39043.5464 | 2347 | 0 | 39043.5464 | 2579 | 0 |  | 457 | 647 | 143.2845 | 0 | 157.4481 | 0 | 1.4328 | 0 | 1.5745 | 0 | 1.4328 | 1.5745 | 13.3098 | 3.1167 | 11.8769
39043.5468 | 2406 | 0 | 39043.5469 | 2514 | 0 |  | 499 | 689 | 146.8864 | 0 | 153.4799 | 0 | 1.4689 | 0 | 1.5348 | 0 | 1.4689 | 1.5348 | 10.5312 | 5.7828 | 9.0623
39043.5473 | 2431 | 0 | 39043.5473 | 2618 | 0 |  | 541 | 731 | 148.4127 | 0 | 159.8291 | 0 | 1.4841 | 0 | 1.5983 | 0 | 1.4841 | 1.5983 | 9.3945 | 1.5806 | 7.9104
39043.5478 | 2088 | 0 | 39043.5478 | 2069 | 0 |  | 583 | 773 | 127.4725 | 0 | 126.3126 | 0 | 1.2747 | 0 | 1.2631 | 0 | 1.2747 | 1.2631 | 27.3649 | 28.5346 | 26.0902
39043.5483 | 2244 | 0 | 39043.5483 | 2643 | 0 |  | 625 | 815 | 136.9963 | 0 | 161.3553 | 0 | 1.37 | 0 | 1.6136 | 0 | 1.37 | 1.6136 | 18.5107 | 0.61975 | 17.1407
39043.5488 | 2187 | 0 | 39043.5488 | 2337 | 0 |  | 667 | 857 | 133.5165 | 0 | 142.674 | 0 | 1.3352 | 0 | 1.4267 | 0 | 1.3352 | 1.4267 | 21.5995 | 13.7946 | 20.2643
39043.5493 | 2143 | 0 | 39043.5493 | 2080 | 0 |  | 709 | 899 | 130.8303 | 0 | 126.9841 | 0 | 1.3083 | 0 | 1.2698 | 0 | 1.3083 | 1.2698 | 24.0961 | 27.8548 | 22.7878
39043.5498 | 2244 | 0 | 39043.5498 | 2214 | 0 |  | 751 | 941 | 136.9963 | 0 | 135.1648 | 0 | 1.37 | 0 | 1.3516 | 0 | 1.37 | 1.3516 | 18.5107 | 20.1165 | 17.1407
39043.5502 | 2373 | 0 | 39043.5503 | 2542 | 0 |  | 793 | 983 | 144.8718 | 0 | 155.1893 | 0 | 1.4487 | 0 | 1.5519 | 0 | 1.4487 | 1.5519 | 12.0683 | 4.6176 | 10.6196
39043.5507 | 2619 | 0 | 39043.5508 | 2056 | 0 |  | 835 | 1025 | 159.8901 | 0 | 125.5189 | 0 | 1.5989 | 0 | 1.2552 | 0 | 1.5989 | 1.2552 | 1.5418 | 29.3473 | 0.057091
39043.5512 | 2547 | 0 | 39043.5512 | 2073 | 0 |  | 877 | 1067 | 155.4945 | 0 | 126.5568 | 0 | 1.5549 | 0 | 1.2656 | 0 | 1.5549 | 1.2656 | 4.4122 | 28.2865 | 2.8573
39043.5517 | 2324 | 0 | 39043.5517 | 2117 | 0 |  | 919 | 1109 | 141.8803 | 0 | 129.243 | 0 | 1.4188 | 0 | 1.2924 | 0 | 1.4188 | 1.2924 | 14.4312 | 25.6202 | 13.0123
39043.5522 | 2445 | 0 | 39043.5522 | 2607 | 0 |  | 961 | 1151 | 149.2674 | 0 | 159.1575 | 0 | 1.4927 | 0 | 1.5916 | 0 | 1.4927 | 1.5916 | 8.7681 | 2.0092 | 7.2754
39043.5527 | 2510 | 0 | 39043.5527 | 2618 | 0 |  | 1003 | 1193 | 153.2357 | 0 | 159.8291 | 0 | 1.5324 | 0 | 1.5983 | 0 | 1.5324 | 1.5983 | 5.9514 | 1.5806 | 4.419
39043.5532 | 2617 | 0 | 39043.5532 | 2285 | 0 |  | 1045 | 1235 | 159.768 | 0 | 139.4994 | 0 | 1.5977 | 0 | 1.395 | 0 | 1.5977 | 1.395 | 1.6194 | 16.3842 | 0.021731
39043.5536 | 2463 | 0 | 39043.5537 | 2614 | 0 |  | 1087 | 1277 | 150.3663 | 0 | 159.5849 | 0 | 1.5037 | 0 | 1.5958 | 0 | 1.5037 | 1.5958 | 7.9732 | 1.736 | 6.4695
39043.5541 | 2039 | 0 | 39043.5542 | 2628 | 0 |  | 1129 | 1319 | 124.4811 | 0 | 160.4396 | 0 | 1.2448 | 0 | 1.6044 | 0 | 1.2448 | 1.6044 | 30.4257 | 1.1941 | 29.1809
39043.5546 | 2302 | 0 | 39043.5546 | 2073 | 0 |  | 1171 | 1361 | 140.5372 | 0 | 126.5568 | 0 | 1.4054 | 0 | 1.2656 | 0 | 1.4054 | 1.2656 | 15.5248 | 28.2865 | 14.1194
39043.5551 | 2602 | 0 | 39043.5551 | 2404 | 0 |  | 1213 | 1403 | 158.8523 | 0 | 146.7643 | 0 | 1.5885 | 0 | 1.4676 | 0 | 1.5885 | 1.4676 | 2.2052 | 10.6231 | 0.6167
39043.5556 | 2490 | 0 | 39043.5556 | 2223 | 0 |  | 1255 | 1445 | 152.0147 | 0 | 135.7143 | 0 | 1.5201 | 0 | 1.3571 | 0 | 1.5201 | 1.3571 | 6.8024 | 19.6302 | 5.2823
39043.5561 | 2056 | 0 | 39043.5561 | 1862 | 0 |  | 1297 | 1487 | 125.5189 | 0 | 113.6752 | 0 | 1.2552 | 0 | 1.1368 | 0 | 1.2552 | 1.1368 | 29.3473 | 42.8238 | 28.0921
39043.5566 | 778 | 0 | 39043.5566 | 989 | 0 |  | 1339 | 1529 | 47.4969 | 0 | 60.3785 | 0 | 0.47497 | 0 | 0.60379 | 0 | 0.47497 | 0.60379 | 241.8226 | 168.8959 | 241.3477
39043.557 | 1632 | 0 | 39043.5571 | 1307 | 0 |  | 1381 | 1571 | 99.6337 | 0 | 79.7924 | 0 | 0.99634 | 0 | 0.79792 | 0 | 0.99634 | 0.79792 | 62.9522 | 103.4721 | 61.9559

## A2-B3
Open Burn Test 12 |  |  | 2006-11-22 | 13:02 |  |  | Vs = |  | 160.1575 |  | R = | 100
Mixed | 7-C | Tray A | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 2 & 3 | Cable A | Even - | Cable B |  | Odd
Time-11 | N11 | N12 | Time-12 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R3-G | R2-3
39043.539 | 1 | 0 | 39043.5391 | 1 | 0 |  | -175.5 | 14.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262238 | 262238 | 262237.9994
39043.5395 | 1 | 0 | 39043.5395 | 1 | 0 |  | -133.5 | 56.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262238 | 262238 | 262237.9994
39043.54 | 1 | 0 | 39043.54 | 1 | 0 |  | -91.5 | 98.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262238 | 262238 | 262237.9994
39043.5405 | 1 | 0 | 39043.5405 | 1 | 0 |  | -49.5 | 140.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262238 | 262238 | 262237.9994
39043.541 | 1 | 0 | 39043.541 | 1 | 0 |  | -7.5 | 182.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262238 | 262238 | 262237.9994
39043.5415 | 1 | 0 | 39043.5415 | 1 | 0 |  | 34.5 | 224.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262238 | 262238 | 262237.9994
39043.542 | 1 | 0 | 39043.542 | 1 | 0 |  | 76.5 | 266.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262238 | 262238 | 262237.9994
39043.5424 | 1 | 0 | 39043.5425 | 1 | 0 |  | 118.5 | 308.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262238 | 262238 | 262237.9994
39043.5429 | 1 | 0 | 39043.5429 | 1 | 0 |  | 160.5 | 350.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262238 | 262238 | 262237.9994
39043.5434 | 1 | 0 | 39043.5434 | 1 | 0 |  | 202.5 | 392.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262238 | 262238 | 262237.9994
39043.5439 | 4 | 0 | 39043.5439 | 1 | 0 |  | 244.5 | 434.5 | 0.2442 | 0 | 0.06105 | 0 | 0.002442 | 0 | 0.0006105 | 0 | 0.002442 | 0.0006105 | 65484.5 | 262238 | 65484.4976
39043.5444 | 1764 | 1 | 39043.5444 | 2 | 0 |  | 286.5 | 476.5 | 107.6923 | 0.06105 | 0.1221 | 0 | 1.0769 | 0.0006105 | 0.001221 | 0 | 1.0763 | 0.001221 | 48.7453 | 131069 | 85772.5592
39043.5449 | 1869 | 0 | 39043.5449 | 1150 | 0 |  | 328 | 518 | 114.1026 | 0 | 70.2076 | 0 | 1.141 | 0 | 0.70208 | 0 | 1.141 | 0.70208 | 40.3628 | 128.12 | 39.2217
39043.5454 | 2304 | 0 | 39043.5454 | 2195 | 0 |  | 370.5 | 560.5 | 140.6593 | 0 | 134.0049 | 0 | 1.4066 | 0 | 1.34 | 0 | 1.4066 | 1.34 | 13.862 | 19.5162 | 12.4554
39043.5458 | 2446 | 0 | 39043.5459 | 1829 | 0 |  | 412.5 | 602.5 | 149.3284 | 0 | 111.6606 | 0 | 1.4933 | 0 | 1.1166 | 0 | 1.4933 | 1.1166 | 7.2518 | 43.4325 | 5.7586
39043.5463 | 2355 | 0 | 39043.5463 | 2565 | 0 |  | 454.5 | 644.5 | 143.7729 | 0 | 156.5934 | 0 | 1.4377 | 0 | 1.5659 | 0 | 1.4377 | 1.5659 | 11.3962 | 2.276 | 9.9584
39043.5468 | 2344 | 0 | 39043.5468 | 2394 | 0 |  | 496.5 | 686.5 | 143.1013 | 0 | 146.1538 | 0 | 1.431 | 0 | 1.4615 | 0 | 1.431 | 1.4615 | 11.9189 | 9.5815 | 10.4879
39043.5473 | 2475 | 0 | 39043.5473 | 2472 | 0 |  | 538.5 | 728.5 | 151.0989 | 0 | 150.9158 | 0 | 1.511 | 0 | 1.5092 | 0 | 1.511 | 1.5092 | 5.9952 | 6.1238 | 4.4842
39043.5478 | 2152 | 0 | 39043.5478 | 2550 | 0 |  | 580.5 | 770.5 | 131.3797 | 0 | 155.6777 | 0 | 1.3138 | 0 | 1.5568 | 0 | 1.3138 | 1.5568 | 21.9043 | 2.8776 | 20.5905
39043.5483 | 2488 | 0 | 39043.5483 | 2096 | 0 |  | 622.5 | 812.5 | 151.8926 | 0 | 127.9609 | 0 | 1.5189 | 0 | 1.2796 | 0 | 1.5189 | 1.2796 | 5.4413 | 25.1613 | 3.9224
39043.5488 | 2543 | 0 | 39043.5488 | 1988 | 0 |  | 664.5 | 854.5 | 155.2503 | 0 | 121.3675 | 0 | 1.5525 | 0 | 1.2137 | 0 | 1.5525 | 1.2137 | 3.1608 | 31.9608 | 1.6083
39043.5492 | 2395 | 0 | 39043.5493 | 2226 | 0 |  | 706 | 896 | 146.2149 | 0 | 135.8974 | 0 | 1.4621 | 0 | 1.359 | 0 | 1.4621 | 1.359 | 9.5357 | 17.8518 | 8.0736
39043.5497 | 2278 | 0 | 39043.5497 | 2464 | 0 |  | 748 | 938 | 139.072 | 0 | 150.4274 | 0 | 1.3907 | 0 | 1.5043 | 0 | 1.3907 | 1.5043 | 15.1615 | 6.4683 | 13.7708
39043.5502 | 2319 | 0 | 39043.5502 | 2038 | 0 |  | 790 | 980 | 141.5751 | 0 | 124.42 | 0 | 1.4158 | 0 | 1.2442 | 0 | 1.4158 | 1.2442 | 13.1255 | 28.7233 | 11.7097
39043.5507 | 2556 | 0 | 39043.5507 | 2403 | 0 |  | 832 | 1022 | 156.044 | 0 | 146.7033 | 0 | 1.5604 | 0 | 1.467 | 0 | 1.5604 | 1.467 | 2.6362 | 9.171 | 1.0757
39043.5512 | 2607 | 0 | 39043.5512 | 2431 | 0 |  | 874 | 1064 | 159.1575 | 0 | 148.4127 | 0 | 1.5916 | 0 | 1.4841 | 0 | 1.5916 | 1.4841 | 0.62831 | 7.9136 | 0.96327
39043.5517 | 2578 | 0 | 39043.5517 | 2367 | 0 |  | 916 | 1106 | 157.3871 | 0 | 144.5055 | 0 | 1.5739 | 0 | 1.4451 | 0 | 1.5739 | 1.4451 | 1.7603 | 10.8314 | 0.18641
39043.5522 | 2341 | 0 | 39043.5522 | 2581 | 0 |  | 958 | 1148 | 142.9182 | 0 | 157.5702 | 0 | 1.4292 | 0 | 1.5757 | 0 | 1.4292 | 1.5757 | 12.0624 | 1.642 | 10.6332
39043.5526 | 2526 | 0 | 39043.5527 | 2366 | 0 |  | 1000 | 1190 | 154.2125 | 0 | 144.4444 | 0 | 1.5421 | 0 | 1.4444 | 0 | 1.5421 | 1.4444 | 3.8551 | 10.8783 | 2.313
39043.5531 | 2374 | 0 | 39043.5531 | 2371 | 0 |  | 1042.5 | 1232.5 | 144.9328 | 0 | 144.7497 | 0 | 1.4493 | 0 | 1.4475 | 0 | 1.4493 | 1.4475 | 10.5046 | 10.6445 | 9.0553
39043.5536 | 2280 | 0 | 39043.5536 | 2488 | 0 |  | 1084 | 1274 | 139.1941 | 0 | 151.8926 | 0 | 1.3919 | 0 | 1.5189 | 0 | 1.3919 | 1.5189 | 15.0605 | 5.4413 | 13.6686
39043.5541 | 2063 | 0 | 39043.5541 | 2562 | 0 |  | 1126 | 1316 | 125.9463 | 0 | 156.4103 | 0 | 1.2595 | 0 | 1.5641 | 0 | 1.2595 | 1.5641 | 27.1634 | 2.3958 | 25.9039
39043.5546 | 2553 | 0 | 39043.5546 | 2373 | 0 |  | 1168 | 1358 | 155.8608 | 0 | 144.8718 | 0 | 1.5586 | 0 | 1.4487 | 0 | 1.5586 | 1.4487 | 2.7568 | 10.5512 | 1.1981
39043.5551 | 2569 | 0 | 39043.5551 | 2264 | 0 |  | 1210 | 1400 | 156.8376 | 0 | 138.2173 | 0 | 1.5684 | 0 | 1.3822 | 0 | 1.5684 | 1.3822 | 2.1168 | 15.8737 | 0.5484
39043.5556 | 2032 | 0 | 39043.5556 | 2073 | 0 |  | 1252 | 1442 | 124.0537 | 0 | 126.5568 | 0 | 1.2405 | 0 | 1.2656 | 0 | 1.2405 | 1.2656 | 29.1033 | 26.5499 | 27.8628
39043.556 | 2102 | 0 | 39043.5561 | 1982 | 0 |  | 1294 | 1484 | 128.3272 | 0 | 121.0012 | 0 | 1.2833 | 0 | 1.21 | 0 | 1.2833 | 1.21 | 24.804 | 32.3602 | 23.5207
39043.5565 | 924 | 0 | 39043.5566 | 2306 | 0 |  | 1336 | 1526 | 56.4103 | 0 | 140.7814 | 0 | 0.5641 | 0 | 1.4078 | 0 | 0.5641 | 1.4078 | 183.9156 | 13.7632 | 183.3515
39043.557 | 1382 | 0 | 39043.557 | 1745 | 0 |  | 1378 | 1568 | 84.3712 | 0 | 106.5324 | 0 | 0.84371 | 0 | 1.0653 | 0 | 0.84371 | 1.0653 | 89.8249 | 50.337 | 88.9812

## A1-C6
Open Burn Test 12 |  |  | 2006-11-22 | 13:02 |  |  | Vs = |  | 161.2564 |  | R = | 100
Mixed | 7-C | Tray A | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 1 & 6 | Cable A | Odd - | Cable C |  | Even
Time-9 | N11 | N12 | Time-10 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R6-G | R1-6
39043.539 | 1 | 0 | 39043.539 | 1 | 0 |  | -178.5 | 11.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264038 | 264038 | 264037.9994
39043.5395 | 1 | 0 | 39043.5395 | 1 | 0 |  | -136.5 | 53.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264038 | 264038 | 264037.9994
39043.54 | 1 | 0 | 39043.54 | 1 | 0 |  | -94.5 | 95.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264038 | 264038 | 264037.9994
39043.5405 | 1 | 0 | 39043.5405 | 1 | 0 |  | -52.5 | 137.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264038 | 264038 | 264037.9994
39043.5409 | 1 | 0 | 39043.541 | 1 | 0 |  | -10.5 | 179.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264038 | 264038 | 264037.9994
39043.5414 | 1 | 0 | 39043.5414 | 1 | 0 |  | 31.5 | 221.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264038 | 264038 | 264037.9994
39043.5419 | 1 | 0 | 39043.5419 | 1 | 0 |  | 73.5 | 263.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264038 | 264038 | 264037.9994
39043.5424 | 1 | 0 | 39043.5424 | 1 | 0 |  | 115.5 | 305.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264038 | 264038 | 264037.9994
39043.5429 | 1 | 0 | 39043.5429 | 7 | 0 |  | 157.5 | 347.5 | 0.06105 | 0 | 0.42735 | 0 | 0.0006105 | 0 | 0.0042735 | 0 | 0.0006105 | 0.0042735 | 264038 | 37634 | 264037.9994
39043.5434 | 1 | 0 | 39043.5434 | 1674 | 0 |  | 199.5 | 389.5 | 0.06105 | 0 | 102.1978 | 0 | 0.0006105 | 0 | 1.022 | 0 | 0.0006105 | 1.022 | 264038 | 57.7885 | 264037.9994
39043.5439 | 2 | 0 | 39043.5439 | 2191 | 0 |  | 241.5 | 431.5 | 0.1221 | 0 | 133.7607 | 0 | 0.001221 | 0 | 1.3376 | 0 | 0.001221 | 1.3376 | 131969 | 20.5559 | 131968.9988
39043.5444 | 1478 | 0 | 39043.5444 | 2253 | 0 |  | 283.5 | 473.5 | 90.232 | 0 | 137.5458 | 0 | 0.90232 | 0 | 1.3755 | 0 | 0.90232 | 1.3755 | 78.7131 | 17.2383 | 77.8108
39043.5448 | 1903 | 0 | 39043.5448 | 2271 | 0 |  | 325.5 | 515.5 | 116.1783 | 0 | 138.6447 | 0 | 1.1618 | 0 | 1.3864 | 0 | 1.1618 | 1.3864 | 38.8008 | 16.3091 | 37.6391
39043.5453 | 1989 | 0 | 39043.5453 | 2117 | 0 |  | 367.5 | 557.5 | 121.4286 | 0 | 129.243 | 0 | 1.2143 | 0 | 1.2924 | 0 | 1.2143 | 1.2924 | 32.7994 | 24.77 | 31.5851
39043.5458 | 2371 | 0 | 39043.5458 | 2605 | 0 |  | 409.5 | 599.5 | 144.7497 | 0 | 159.0354 | 0 | 1.4475 | 0 | 1.5904 | 0 | 1.4475 | 1.5904 | 11.4036 | 1.3965 | 9.9561
39043.5463 | 2418 | 0 | 39043.5463 | 2416 | 0 |  | 451.5 | 641.5 | 147.619 | 0 | 147.4969 | 0 | 1.4762 | 0 | 1.475 | 0 | 1.4762 | 1.475 | 9.2382 | 9.3286 | 7.762
39043.5468 | 2442 | 0 | 39043.5468 | 2269 | 0 |  | 493.5 | 683.5 | 149.0842 | 0 | 138.5226 | 0 | 1.4908 | 0 | 1.3852 | 0 | 1.4908 | 1.3852 | 8.1646 | 16.4116 | 6.6738
39043.5473 | 2439 | 0 | 39043.5473 | 2253 | 0 |  | 535.5 | 725.5 | 148.9011 | 0 | 137.5458 | 0 | 1.489 | 0 | 1.3755 | 0 | 1.489 | 1.3755 | 8.2977 | 17.2383 | 6.8087
39043.5478 | 2542 | 0 | 39043.5478 | 2293 | 0 |  | 577.5 | 767.5 | 155.1893 | 0 | 139.9878 | 0 | 1.5519 | 0 | 1.3999 | 0 | 1.5519 | 1.3999 | 3.9095 | 15.1932 | 2.3576
39043.5482 | 2590 | 0 | 39043.5483 | 2478 | 0 |  | 619.5 | 809.5 | 158.1197 | 0 | 151.2821 | 0 | 1.5812 | 0 | 1.5128 | 0 | 1.5812 | 1.5128 | 1.9838 | 6.5932 | 0.40259
39043.5487 | 2119 | 0 | 39043.5487 | 2066 | 0 |  | 661.5 | 851.5 | 129.3651 | 0 | 126.1294 | 0 | 1.2937 | 0 | 1.2613 | 0 | 1.2937 | 1.2613 | 24.6522 | 27.85 | 23.3585
39043.5492 | 2134 | 0 | 39043.5492 | 2332 | 0 |  | 703.5 | 893.5 | 130.2808 | 0 | 142.3687 | 0 | 1.3028 | 0 | 1.4237 | 0 | 1.3028 | 1.4237 | 23.776 | 13.2667 | 22.4732
39043.5497 | 2364 | 0 | 39043.5497 | 2146 | 0 |  | 745.5 | 935.5 | 144.3223 | 0 | 131.0134 | 0 | 1.4432 | 0 | 1.3101 | 0 | 1.4432 | 1.3101 | 11.7335 | 23.0839 | 10.2903
39043.5502 | 2571 | 0 | 39043.5502 | 2048 | 0 |  | 787.5 | 977.5 | 156.9597 | 0 | 125.0305 | 0 | 1.5696 | 0 | 1.2503 | 0 | 1.5696 | 1.2503 | 2.7375 | 28.9736 | 1.1679
39043.5507 | 2443 | 0 | 39043.5507 | 2347 | 0 |  | 829.5 | 1019.5 | 149.1453 | 0 | 143.2845 | 0 | 1.4915 | 0 | 1.4328 | 0 | 1.4915 | 1.4328 | 8.1203 | 12.5428 | 6.6289
39043.5512 | 2166 | 0 | 39043.5512 | 2235 | 0 |  | 871.5 | 1061.5 | 132.2344 | 0 | 136.4469 | 0 | 1.3223 | 0 | 1.3645 | 0 | 1.3223 | 1.3645 | 21.9474 | 18.1826 | 20.625
39043.5516 | 2072 | 0 | 39043.5517 | 2368 | 0 |  | 913.5 | 1103.5 | 126.4957 | 0 | 144.5665 | 0 | 1.265 | 0 | 1.4457 | 0 | 1.265 | 1.4457 | 27.4797 | 11.5448 | 26.2148
39043.5521 | 2179 | 0 | 39043.5521 | 2236 | 0 |  | 955.5 | 1145.5 | 133.0281 | 0 | 136.5079 | 0 | 1.3303 | 0 | 1.3651 | 0 | 1.3303 | 1.3651 | 21.2198 | 18.1297 | 19.8895
39043.5526 | 2498 | 0 | 39043.5526 | 2119 | 0 |  | 997.5 | 1187.5 | 152.5031 | 0 | 129.3651 | 0 | 1.525 | 0 | 1.2937 | 0 | 1.525 | 1.2937 | 5.7398 | 24.6522 | 4.2148
39043.5531 | 2270 | 0 | 39043.5531 | 2133 | 0 |  | 1039.5 | 1229.5 | 138.5836 | 0 | 130.2198 | 0 | 1.3858 | 0 | 1.3022 | 0 | 1.3858 | 1.3022 | 16.3604 | 23.834 | 14.9745
39043.5536 | 2468 | 0 | 39043.5536 | 2162 | 0 |  | 1081.5 | 1271.5 | 150.6716 | 0 | 131.9902 | 0 | 1.5067 | 0 | 1.3199 | 0 | 1.5067 | 1.3199 | 7.0251 | 22.173 | 5.5184
39043.5541 | 2625 | 0 | 39043.5541 | 2155 | 0 |  | 1123.5 | 1313.5 | 160.2564 | 0 | 131.5629 | 0 | 1.6026 | 0 | 1.3156 | 0 | 1.6026 | 1.3156 | 0.624 | 22.5698 | 0.97856
39043.5546 | 2363 | 0 | 39043.5546 | 2169 | 0 |  | 1165.5 | 1355.5 | 144.2613 | 0 | 132.4176 | 0 | 1.4426 | 0 | 1.3242 | 0 | 1.4426 | 1.3242 | 11.7808 | 21.7787 | 10.3382
39043.555 | 2102 | 0 | 39043.5551 | 2384 | 0 |  | 1207.5 | 1397.5 | 128.3272 | 0 | 145.5433 | 0 | 1.2833 | 0 | 1.4554 | 0 | 1.2833 | 1.4554 | 25.6603 | 10.7961 | 24.3771
39043.5555 | 2298 | 0 | 39043.5555 | 2609 | 0 |  | 1249.5 | 1439.5 | 140.293 | 0 | 159.2796 | 0 | 1.4029 | 0 | 1.5928 | 0 | 1.4029 | 1.5928 | 14.9426 | 1.2411 | 13.5396
39043.556 | 2128 | 0 | 39043.556 | 2437 | 0 |  | 1291.5 | 1481.5 | 129.9145 | 0 | 148.779 | 0 | 1.2991 | 0 | 1.4878 | 0 | 1.2991 | 1.4878 | 24.125 | 8.3865 | 22.8259
39043.5565 | 1172 | 665 | 39043.5565 | 1354 | 701 |  | 1333.5 | 1523.5 | 71.5507 | 40.5983 | 82.6618 | 42.7961 | 0.71551 | 0.40598 | 0.82662 | 0.42796 | 0.30952 | 0.39866 | 652.5255 | 235.9692 | 84.9563
39043.557 | 1671 | 439 | 39043.557 | 1371 | 384 |  | 1375.5 | 1565.5 | 102.0147 | 26.801 | 83.6996 | 23.4432 | 1.0201 | 0.26801 | 0.837 | 0.23443 | 0.75214 | 0.60256 | 94.0238 | 219.5638 | 83.1656

## A1-C5
Open Burn Test 12 |  |  | 2006-11-22 | 13:02 |  |  | Vs = |  | 162.9048 |  | R = | 100
Mixed | 7-C | Tray A | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 1 & 5 | Cable A | Odd - | Cable C |  | Odd
Time-7 | N11 | N12 | Time-8 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R5-G | R1-5
39043.539 | 1 | 0 | 39043.539 | 1 | 0 |  | -181.5 | 8.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 266738 | 266738 | 266737.9994
39043.5395 | 1 | 0 | 39043.5395 | 1 | 0 |  | -139.5 | 50.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 266738 | 266738 | 266737.9994
39043.5399 | 1 | 0 | 39043.54 | 1 | 0 |  | -97.5 | 92.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 266738 | 266738 | 266737.9994
39043.5404 | 1 | 0 | 39043.5404 | 1 | 0 |  | -55.5 | 134.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 266738 | 266738 | 266737.9994
39043.5409 | 1 | 0 | 39043.5409 | 1 | 0 |  | -13.5 | 176.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 266738 | 266738 | 266737.9994
39043.5414 | 1 | 0 | 39043.5414 | 1 | 0 |  | 28.5 | 218.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 266738 | 266738 | 266737.9994
39043.5419 | 1 | 0 | 39043.5419 | 1 | 0 |  | 70.5 | 260.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 266738 | 266738 | 266737.9994
39043.5424 | 1 | 0 | 39043.5424 | 1 | 0 |  | 112.5 | 302.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 266738 | 266738 | 266737.9994
39043.5429 | 1 | 0 | 39043.5429 | 1480 | 0 |  | 154.5 | 344.5 | 0.06105 | 0 | 90.3541 | 0 | 0.0006105 | 0 | 0.90354 | 0 | 0.0006105 | 0.90354 | 266738 | 80.2959 | 266737.9994
39043.5433 | 1 | 0 | 39043.5434 | 1920 | 0 |  | 196.5 | 386.5 | 0.06105 | 0 | 117.2161 | 0 | 0.0006105 | 0 | 1.1722 | 0 | 0.0006105 | 1.1722 | 266738 | 38.9781 | 266737.9994
39043.5438 | 1 | 0 | 39043.5438 | 1916 | 0 |  | 238.5 | 428.5 | 0.06105 | 0 | 116.9719 | 0 | 0.0006105 | 0 | 1.1697 | 0 | 0.0006105 | 1.1697 | 266738 | 39.2683 | 266737.9994
39043.5443 | 1236 | 0 | 39043.5443 | 2563 | 0 |  | 280.5 | 470.5 | 75.4579 | 0 | 156.4713 | 0 | 0.75458 | 0 | 1.5647 | 0 | 0.75458 | 1.5647 | 115.8883 | 4.1116 | 115.1338
39043.5448 | 2124 | 0 | 39043.5448 | 2284 | 0 |  | 322.5 | 512.5 | 129.6703 | 0 | 139.4383 | 0 | 1.2967 | 0 | 1.3944 | 0 | 1.2967 | 1.3944 | 25.6299 | 16.8292 | 24.3332
39043.5453 | 2540 | 0 | 39043.5453 | 2195 | 0 |  | 364.5 | 554.5 | 155.0672 | 0 | 134.0049 | 0 | 1.5507 | 0 | 1.34 | 0 | 1.5507 | 1.34 | 5.0543 | 21.5663 | 3.5037
39043.5458 | 2374 | 0 | 39043.5458 | 2124 | 0 |  | 406.5 | 596.5 | 144.9328 | 0 | 129.6703 | 0 | 1.4493 | 0 | 1.2967 | 0 | 1.4493 | 1.2967 | 12.4002 | 25.6299 | 10.9508
39043.5463 | 2304 | 0 | 39043.5463 | 2080 | 0 |  | 448.5 | 638.5 | 140.6593 | 0 | 126.9841 | 0 | 1.4066 | 0 | 1.2698 | 0 | 1.4066 | 1.2698 | 15.8151 | 28.2875 | 14.4085
39043.5467 | 2621 | 0 | 39043.5468 | 2208 | 0 |  | 490.5 | 680.5 | 160.0122 | 0 | 134.7985 | 0 | 1.6001 | 0 | 1.348 | 0 | 1.6001 | 1.348 | 1.8077 | 20.8505 | 0.20758
39043.5472 | 2261 | 0 | 39043.5472 | 2209 | 0 |  | 532.5 | 722.5 | 138.0342 | 0 | 134.8596 | 0 | 1.3803 | 0 | 1.3486 | 0 | 1.3803 | 1.3486 | 18.0177 | 20.7958 | 16.6373
39043.5477 | 2211 | 0 | 39043.5477 | 2216 | 0 |  | 574.5 | 764.5 | 134.9817 | 0 | 135.2869 | 0 | 1.3498 | 0 | 1.3529 | 0 | 1.3498 | 1.3529 | 20.6866 | 20.4143 | 19.3368
39043.5482 | 2263 | 0 | 39043.5482 | 2558 | 0 |  | 616.5 | 806.5 | 138.1563 | 0 | 156.1661 | 0 | 1.3816 | 0 | 1.5617 | 0 | 1.3816 | 1.5617 | 17.9134 | 4.3151 | 16.5318
39043.5487 | 2517 | 0 | 39043.5487 | 2086 | 0 |  | 658.5 | 848.5 | 153.663 | 0 | 127.3504 | 0 | 1.5366 | 0 | 1.2735 | 0 | 1.5366 | 1.2735 | 6.0143 | 27.9185 | 4.4777
39043.5492 | 2432 | 0 | 39043.5492 | 2385 | 0 |  | 700.5 | 890.5 | 148.4737 | 0 | 145.6044 | 0 | 1.4847 | 0 | 1.456 | 0 | 1.4847 | 1.456 | 9.7196 | 11.8818 | 8.2348
39043.5497 | 2074 | 0 | 39043.5497 | 2251 | 0 |  | 742.5 | 932.5 | 126.6178 | 0 | 137.4237 | 0 | 1.2662 | 0 | 1.3742 | 0 | 1.2662 | 1.3742 | 28.6586 | 18.542 | 27.3925
39043.5502 | 2313 | 0 | 39043.5502 | 2485 | 0 |  | 784.5 | 974.5 | 141.2088 | 0 | 151.7094 | 0 | 1.4121 | 0 | 1.5171 | 0 | 1.4121 | 1.5171 | 15.3645 | 7.3795 | 13.9524
39043.5506 | 2123 | 0 | 39043.5506 | 2193 | 0 |  | 826.5 | 1016.5 | 129.6093 | 0 | 133.8828 | 0 | 1.2961 | 0 | 1.3388 | 0 | 1.2961 | 1.3388 | 25.6891 | 21.6772 | 24.393
39043.5511 | 2447 | 0 | 39043.5511 | 2488 | 0 |  | 868.5 | 1058.5 | 149.3895 | 0 | 151.8926 | 0 | 1.4939 | 0 | 1.5189 | 0 | 1.4939 | 1.5189 | 9.047 | 7.25 | 7.5531
39043.5516 | 2469 | 0 | 39043.5516 | 2378 | 0 |  | 910.5 | 1100.5 | 150.7326 | 0 | 145.177 | 0 | 1.5073 | 0 | 1.4518 | 0 | 1.5073 | 1.4518 | 8.0753 | 12.2111 | 6.568
39043.5521 | 2383 | 0 | 39043.5521 | 2652 | 0 |  | 952.5 | 1142.5 | 145.4823 | 0 | 161.9048 | 0 | 1.4548 | 0 | 1.619 | 0 | 1.4548 | 1.619 | 11.9757 | 0.61765 | 10.5208
39043.5526 | 2058 | 0 | 39043.5526 | 2305 | 0 |  | 994.5 | 1184.5 | 125.641 | 0 | 140.7204 | 0 | 1.2564 | 0 | 1.4072 | 0 | 1.2564 | 1.4072 | 29.6589 | 15.7649 | 28.4025
39043.5531 | 2632 | 0 | 39043.5531 | 2509 | 0 |  | 1036.5 | 1226.5 | 160.6838 | 0 | 153.1746 | 0 | 1.6068 | 0 | 1.5317 | 0 | 1.6068 | 1.5317 | 1.3822 | 6.3523 | 0.22462
39043.5536 | 2225 | 0 | 39043.5536 | 2091 | 0 |  | 1078.5 | 1268.5 | 135.8364 | 0 | 127.6557 | 0 | 1.3584 | 0 | 1.2766 | 0 | 1.3584 | 1.2766 | 19.9272 | 27.6126 | 18.5688
39043.554 | 2393 | 0 | 39043.5541 | 2149 | 0 |  | 1120.5 | 1310.5 | 146.0928 | 0 | 131.1966 | 0 | 1.4609 | 0 | 1.312 | 0 | 1.4609 | 1.312 | 11.5077 | 24.1685 | 10.0468
39043.5545 | 2191 | 0 | 39043.5545 | 2175 | 0 |  | 1162.5 | 1352.5 | 133.7607 | 0 | 132.7839 | 0 | 1.3376 | 0 | 1.3278 | 0 | 1.3376 | 1.3278 | 21.7882 | 22.6841 | 20.4506
39043.555 | 2063 | 0 | 39043.555 | 2156 | 0 |  | 1204.5 | 1394.5 | 125.9463 | 0 | 131.6239 | 0 | 1.2595 | 0 | 1.3162 | 0 | 1.2595 | 1.3162 | 29.3446 | 23.7653 | 28.0852
39043.5555 | 2304 | 0 | 39043.5555 | 2200 | 0 |  | 1246.5 | 1436.5 | 140.6593 | 0 | 134.3101 | 0 | 1.4066 | 0 | 1.3431 | 0 | 1.4066 | 1.3431 | 15.8151 | 21.29 | 14.4085
39043.556 | 2251 | 0 | 39043.556 | 2034 | 0 |  | 1288.5 | 1478.5 | 137.4237 | 0 | 124.1758 | 0 | 1.3742 | 0 | 1.2418 | 0 | 1.3742 | 1.2418 | 18.542 | 31.1888 | 17.1677
39043.5565 | 1752 | 492 | 39043.5565 | 1437 | 543 |  | 1330.5 | 1520.5 | 106.9597 | 30.0366 | 87.7289 | 33.1502 | 1.0696 | 0.30037 | 0.87729 | 0.3315 | 0.76923 | 0.54579 | 77.4726 | 637.6664 | 74.563
39043.557 | 1439 | 377 | 39043.557 | 1432 | 421 |  | 1372.5 | 1562.5 | 87.851 | 23.0159 | 87.4237 | 25.7021 | 0.87851 | 0.23016 | 0.87424 | 0.25702 | 0.64835 | 0.61722 | 146.0758 | 171.0558 | 142.6826

## A1-B4
Open Burn Test 12 |  |  | 2006-11-22 | 13:02 |  |  | Vs = |  | 161.5617 |  | R = | 100
Mixed | 7-C | Tray A | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 1 & 4 | Cable A | Odd - | Cable B |  | Even
Time-5 | N11 | N12 | Time-6 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R4-G | R1-4
39043.5389 | 1 | 0 | 39043.539 | 1 | 0 |  | -184 | 6 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264538 | 264538 | 264537.9994
39043.5394 | 1 | 0 | 39043.5394 | 1 | 0 |  | -142 | 48 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264538 | 264538 | 264537.9994
39043.5399 | 1 | 0 | 39043.5399 | 1 | 0 |  | -100 | 90 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264538 | 264538 | 264537.9994
39043.5404 | 1 | 0 | 39043.5404 | 1 | 0 |  | -58 | 132 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264538 | 264538 | 264537.9994
39043.5409 | 1 | 0 |  | 1 | 0 |  | -17 | 173 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264538 | 264538 | 264537.9994
39043.5414 | 1 | 0 | 39043.5414 | 1 | 0 |  | 26 | 216 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264538 | 264538 | 264537.9994
39043.5419 | 1 | 0 | 39043.5419 | 1 | 0 |  | 68 | 258 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264538 | 264538 | 264537.9994
39043.5423 | 1 | 0 | 39043.5424 | 1 | 0 |  | 110 | 300 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264538 | 264538 | 264537.9994
39043.5428 | 1 | 0 | 39043.5428 | 1 | 0 |  | 152 | 342 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264538 | 264538 | 264537.9994
39043.5433 | 1 | 0 | 39043.5433 | 1 | 0 |  | 194 | 384 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264538 | 264538 | 264537.9994
39043.5438 | 1 | 0 | 39043.5438 | 1 | 0 |  | 236 | 426 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264538 | 264538 | 264537.9994
39043.5443 | 1145 | 1 | 39043.5443 | 43 | 0 |  | 278 | 468 | 69.9023 | 0.06105 | 2.6252 | 0 | 0.69902 | 0.0006105 | 0.026252 | 0 | 0.69841 | 0.026252 | 131.2414 | 6054.3721 | 147600.0909
39043.5448 | 2125 | 0 | 39043.5448 | 346 | 0 |  | 320 | 510 | 129.7314 | 0 | 21.1233 | 0 | 1.2973 | 0 | 0.21123 | 0 | 1.2973 | 0.21123 | 24.5355 | 664.8497 | 23.2382
39043.5453 | 2552 | 0 | 39043.5453 | 2269 | 0 |  | 362 | 552 | 155.7998 | 0 | 138.5226 | 0 | 1.558 | 0 | 1.3852 | 0 | 1.558 | 1.3852 | 3.6983 | 16.632 | 2.1403
39043.5457 | 2152 | 0 | 39043.5458 | 1914 | 0 |  | 403.5 | 593.5 | 131.3797 | 0 | 116.8498 | 0 | 1.3138 | 0 | 1.1685 | 0 | 1.3138 | 1.1685 | 22.973 | 38.2644 | 21.6593
39043.5462 | 2340 | 0 | 39043.5462 | 2342 | 0 |  | 446 | 636 | 142.8571 | 0 | 142.9792 | 0 | 1.4286 | 0 | 1.4298 | 0 | 1.4286 | 1.4298 | 13.0932 | 12.9966 | 11.6646
39043.5467 | 2630 | 0 | 39043.5467 | 2010 | 0 |  | 488 | 678 | 160.5617 | 0 | 122.7106 | 0 | 1.6056 | 0 | 1.2271 | 0 | 1.6056 | 1.2271 | 0.62281 | 31.6607 | 0.9828
39043.5472 | 2580 | 0 | 39043.5472 | 2172 | 0 |  | 530 | 720 | 157.5092 | 0 | 132.6007 | 0 | 1.5751 | 0 | 1.326 | 0 | 1.5751 | 1.326 | 2.5729 | 21.8407 | 0.99778
39043.5477 | 2068 | 0 | 39043.5477 | 2514 | 0 |  | 572 | 762 | 126.2515 | 0 | 153.4799 | 0 | 1.2625 | 0 | 1.5348 | 0 | 1.2625 | 1.5348 | 27.9681 | 5.2657 | 26.7056
39043.5482 | 2609 | 0 | 39043.5482 | 2303 | 0 |  | 613.5 | 803.5 | 159.2796 | 0 | 140.5983 | 0 | 1.5928 | 0 | 1.406 | 0 | 1.5928 | 1.406 | 1.4327 | 14.9101 | 0.16006
39043.5487 | 2154 | 0 | 39043.5487 | 1828 | 0 |  | 655.5 | 845.5 | 131.5018 | 0 | 111.5995 | 0 | 1.315 | 0 | 1.116 | 0 | 1.315 | 1.116 | 22.8589 | 44.7691 | 21.5438
39043.5491 | 2484 | 0 | 39043.5492 | 2270 | 0 |  | 697.5 | 887.5 | 151.6484 | 0 | 138.5836 | 0 | 1.5165 | 0 | 1.3858 | 0 | 1.5165 | 1.3858 | 6.537 | 16.5806 | 5.0206
39043.5496 | 2350 | 0 | 39043.5497 | 1903 | 0 |  | 740 | 930 | 143.4676 | 0 | 116.1783 | 0 | 1.4347 | 0 | 1.1618 | 0 | 1.4347 | 1.1618 | 12.6119 | 39.0636 | 11.1772
39043.5501 | 2565 | 0 | 39043.5501 | 2309 | 0 |  | 781.5 | 971.5 | 156.5934 | 0 | 140.9646 | 0 | 1.5659 | 0 | 1.4096 | 0 | 1.5659 | 1.4096 | 3.1727 | 14.6115 | 1.6068
39043.5506 | 2221 | 0 | 39043.5506 | 2229 | 0 |  | 823.5 | 1013.5 | 135.5922 | 0 | 136.0806 | 0 | 1.3559 | 0 | 1.3608 | 0 | 1.3559 | 1.3608 | 19.1526 | 18.725 | 17.7967
39043.5511 | 2071 | 0 | 39043.5511 | 2067 | 0 |  | 865.5 | 1055.5 | 126.4347 | 0 | 126.1905 | 0 | 1.2643 | 0 | 1.2619 | 0 | 1.2643 | 1.2619 | 27.7827 | 28.03 | 26.5184
39043.5516 | 2064 | 0 | 39043.5516 | 2488 | 0 |  | 907.5 | 1097.5 | 126.0073 | 0 | 151.8926 | 0 | 1.2601 | 0 | 1.5189 | 0 | 1.2601 | 1.5189 | 28.2161 | 6.3658 | 26.956
39043.5521 | 2044 | 0 | 39043.5521 | 2454 | 0 |  | 949.5 | 1139.5 | 124.7863 | 0 | 149.8168 | 0 | 1.2479 | 0 | 1.4982 | 0 | 1.2479 | 1.4982 | 29.4706 | 7.8394 | 28.2228
39043.5525 | 2392 | 0 | 39043.5526 | 2505 | 0 |  | 991.5 | 1181.5 | 146.0317 | 0 | 152.9304 | 0 | 1.4603 | 0 | 1.5293 | 0 | 1.4603 | 1.5293 | 10.6346 | 5.6439 | 9.1743
39043.553 | 2354 | 0 | 39043.553 | 2132 | 0 |  | 1033.5 | 1223.5 | 143.7118 | 0 | 130.1587 | 0 | 1.4371 | 0 | 1.3016 | 0 | 1.4371 | 1.3016 | 12.4206 | 24.1266 | 10.9834
39043.5535 | 2132 | 0 | 39043.5535 | 2339 | 0 |  | 1075.5 | 1265.5 | 130.1587 | 0 | 142.7961 | 0 | 1.3016 | 0 | 1.428 | 0 | 1.3016 | 1.428 | 24.1266 | 13.1415 | 22.8251
39043.554 | 2554 | 0 | 39043.554 | 2001 | 0 |  | 1117.5 | 1307.5 | 155.9219 | 0 | 122.1612 | 0 | 1.5592 | 0 | 1.2216 | 0 | 1.5592 | 1.2216 | 3.6171 | 32.2529 | 2.0579
39043.5545 | 2205 | 0 | 39043.5545 | 2209 | 0 |  | 1159.5 | 1349.5 | 134.6154 | 0 | 134.8596 | 0 | 1.3462 | 0 | 1.3486 | 0 | 1.3462 | 1.3486 | 20.0172 | 19.7999 | 18.6711
39043.555 | 2279 | 0 | 39043.555 | 1896 | 0 |  | 1201.5 | 1391.5 | 139.1331 | 0 | 115.7509 | 0 | 1.3913 | 0 | 1.1575 | 0 | 1.3913 | 1.1575 | 16.1202 | 39.577 | 14.7289
39043.5555 | 2357 | 0 | 39043.5555 | 2418 | 0 |  | 1243.5 | 1433.5 | 143.895 | 0 | 147.619 | 0 | 1.4389 | 0 | 1.4762 | 0 | 1.4389 | 1.4762 | 12.2775 | 9.445 | 10.8385
39043.5559 | 2072 | 0 | 39043.556 | 2013 | 0 |  | 1285.5 | 1475.5 | 126.4957 | 0 | 122.8938 | 0 | 1.265 | 0 | 1.2289 | 0 | 1.265 | 1.2289 | 27.721 | 31.4645 | 26.4561
39043.5564 | 1083 | 0 | 39043.5564 | 1589 | 0 |  | 1327.5 | 1517.5 | 66.1172 | 0 | 97.0085 | 0 | 0.66117 | 0 | 0.97009 | 0 | 0.66117 | 0.97009 | 144.3564 | 66.5437 | 143.6952
39043.5569 | 1541 | 0 | 39043.5569 | 2371 | 0 |  | 1369.5 | 1559.5 | 94.0781 | 0 | 144.7497 | 0 | 0.94078 | 0 | 1.4475 | 0 | 0.94078 | 1.4475 | 71.7313 | 11.6145 | 70.7906

## A1-B3
Open Burn Test 12 |  |  | 2006-11-22 | 13:02 |  |  | Vs = |  | 161.5006 |  | R = | 100
Mixed | 7-C | Tray A | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 1 & 3 | Cable A | Odd - | Cable B |  | Odd
Time-3 | N11 | N12 | Time-4 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R3-G | R1-3
39043.5389 | 1 | 0 | 39043.5389 | 1 | 0 |  | -187 | 3 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264438 | 264438 | 264437.9994
39043.5394 | 1 | 0 | 39043.5394 | 1 | 0 |  | -145 | 45 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264438 | 264438 | 264437.9994
39043.5399 | 1 | 0 | 39043.5399 | 1 | 0 |  | -103 | 87 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264438 | 264438 | 264437.9994
39043.5404 | 1 | 0 | 39043.5404 | 1 | 0 |  | -61 | 129 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264438 | 264438 | 264437.9994
39043.5408 | 1 | 0 | 39043.5409 | 1 | 0 |  | -19 | 171 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264438 | 264438 | 264437.9994
39043.5413 | 1 | 0 | 39043.5414 | 1 | 0 |  | 23 | 213 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264438 | 264438 | 264437.9994
39043.5418 | 1 | 0 | 39043.5418 | 1 | 0 |  | 65 | 255 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264438 | 264438 | 264437.9994
39043.5423 | 1 | 0 | 39043.5423 | 1 | 0 |  | 107 | 297 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264438 | 264438 | 264437.9994
39043.5428 | 1 | 0 | 39043.5428 | 1 | 0 |  | 149 | 339 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264438 | 264438 | 264437.9994
39043.5433 | 1 | 0 | 39043.5433 | 1 | 0 |  | 191 | 381 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264438 | 264438 | 264437.9994
39043.5438 | 1 | 0 | 39043.5438 | 1 | 0 |  | 233 | 423 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264438 | 264438 | 264437.9994
39043.5442 | 1351 | 1 | 39043.5443 | 4 | 0 |  | 275 | 465 | 82.4786 | 0.06105 | 0.2442 | 0 | 0.82479 | 0.0006105 | 0.002442 | 0 | 0.82418 | 0.002442 | 95.8801 | 66034.5 | 129142.4319
39043.5447 | 1976 | 0 | 39043.5448 | 616 | 0 |  | 317 | 507 | 120.6349 | 0 | 37.6068 | 0 | 1.2063 | 0 | 0.37607 | 0 | 1.2063 | 0.37607 | 33.8755 | 329.4448 | 32.6692
39043.5452 | 2462 | 0 | 39043.5452 | 1481 | 0 |  | 359 | 549 | 150.3053 | 0 | 90.4151 | 0 | 1.5031 | 0 | 0.90415 | 0 | 1.5031 | 0.90415 | 7.4484 | 78.6212 | 5.9454
39043.5457 | 2202 | 0 | 39043.5457 | 1554 | 0 |  | 401 | 591 | 134.4322 | 0 | 94.8718 | 0 | 1.3443 | 0 | 0.94872 | 0 | 1.3443 | 0.94872 | 20.1353 | 70.2304 | 18.791
39043.5462 | 2530 | 0 | 39043.5462 | 2345 | 0 |  | 443 | 633 | 154.4567 | 0 | 143.1624 | 0 | 1.5446 | 0 | 1.4316 | 0 | 1.5446 | 1.4316 | 4.5605 | 12.8094 | 3.0159
39043.5467 | 2612 | 0 | 39043.5467 | 1972 | 0 |  | 485 | 675 | 159.4628 | 0 | 120.3907 | 0 | 1.5946 | 0 | 1.2039 | 0 | 1.5946 | 1.2039 | 1.2779 | 34.1471 | 0.31668
39043.5472 | 2340 | 0 | 39043.5472 | 2007 | 0 |  | 527 | 717 | 142.8571 | 0 | 122.5275 | 0 | 1.4286 | 0 | 1.2253 | 0 | 1.4286 | 1.2253 | 13.0504 | 31.8077 | 11.6219
39043.5477 | 2277 | 0 | 39043.5477 | 2366 | 0 |  | 569 | 759 | 139.011 | 0 | 144.4444 | 0 | 1.3901 | 0 | 1.4444 | 0 | 1.3901 | 1.4444 | 16.1783 | 11.8081 | 14.7882
39043.5481 | 2235 | 0 | 39043.5482 | 2375 | 0 |  | 611 | 801 | 136.4469 | 0 | 144.9939 | 0 | 1.3645 | 0 | 1.4499 | 0 | 1.3645 | 1.4499 | 18.3615 | 11.3844 | 16.9971
39043.5486 | 2492 | 0 | 39043.5486 | 1882 | 0 |  | 653 | 843 | 152.1368 | 0 | 114.8962 | 0 | 1.5214 | 0 | 1.149 | 0 | 1.5214 | 1.149 | 6.1549 | 40.5622 | 4.6335
39043.5491 | 2097 | 0 | 39043.5491 | 1851 | 0 |  | 695 | 885 | 128.022 | 0 | 113.0037 | 0 | 1.2802 | 0 | 1.13 | 0 | 1.2802 | 1.13 | 26.1507 | 42.9163 | 24.8705
39043.5496 | 2333 | 0 | 39043.5496 | 1728 | 0 |  | 737 | 927 | 142.4298 | 0 | 105.4945 | 0 | 1.4243 | 0 | 1.0549 | 0 | 1.4243 | 1.0549 | 13.3896 | 53.0891 | 11.9653
39043.5501 | 2629 | 0 | 39043.5501 | 2232 | 0 |  | 779 | 969 | 160.5006 | 0 | 136.2637 | 0 | 1.605 | 0 | 1.3626 | 0 | 1.605 | 1.3626 | 0.62305 | 18.5206 | 0.98196
39043.5506 | 2100 | 0 | 39043.5506 | 2245 | 0 |  | 821 | 1011 | 128.2051 | 0 | 137.0574 | 0 | 1.2821 | 0 | 1.3706 | 0 | 1.2821 | 1.3706 | 25.9705 | 17.8343 | 24.6884
39043.5511 | 2172 | 0 | 39043.5511 | 2046 | 0 |  | 863 | 1053 | 132.6007 | 0 | 124.9084 | 0 | 1.326 | 0 | 1.2491 | 0 | 1.326 | 1.2491 | 21.7947 | 29.2952 | 20.4687
39043.5515 | 2301 | 0 | 39043.5516 | 2508 | 0 |  | 905 | 1095 | 140.4762 | 0 | 153.1136 | 0 | 1.4048 | 0 | 1.5311 | 0 | 1.4048 | 1.5311 | 14.9665 | 5.4777 | 13.5618
39043.552 | 2354 | 0 | 39043.552 | 2463 | 0 |  | 947 | 1137 | 143.7118 | 0 | 150.3663 | 0 | 1.4371 | 0 | 1.5037 | 0 | 1.4371 | 1.5037 | 12.3781 | 7.4048 | 10.941
39043.5525 | 2039 | 0 | 39043.5525 | 2135 | 0 |  | 989 | 1179 | 124.4811 | 0 | 130.3419 | 0 | 1.2448 | 0 | 1.3034 | 0 | 1.2448 | 1.3034 | 29.7391 | 23.9054 | 28.4943
39043.553 | 2120 | 0 | 39043.553 | 2316 | 0 |  | 1031 | 1221 | 129.4261 | 0 | 141.3919 | 0 | 1.2943 | 0 | 1.4139 | 0 | 1.2943 | 1.4139 | 24.7821 | 14.2219 | 23.4878
39043.5535 | 2223 | 0 | 39043.5535 | 2350 | 0 |  | 1073 | 1263 | 135.7143 | 0 | 143.4676 | 0 | 1.3571 | 0 | 1.4347 | 0 | 1.3571 | 1.4347 | 19.0004 | 12.5694 | 17.6433
39043.554 | 2362 | 0 | 39043.554 | 2507 | 0 |  | 1115 | 1305 | 144.2002 | 0 | 153.0525 | 0 | 1.442 | 0 | 1.5305 | 0 | 1.442 | 1.5305 | 11.9975 | 5.5197 | 10.5555
39043.5545 | 2162 | 0 | 39043.5545 | 2147 | 0 |  | 1157 | 1347 | 131.9902 | 0 | 131.0745 | 0 | 1.3199 | 0 | 1.3107 | 0 | 1.3199 | 1.3107 | 22.358 | 23.2129 | 21.0381
39043.5549 | 2513 | 0 | 39043.555 | 2460 | 0 |  | 1199 | 1389 | 153.4188 | 0 | 150.1832 | 0 | 1.5342 | 0 | 1.5018 | 0 | 1.5342 | 1.5018 | 5.2678 | 7.5358 | 3.7336
39043.5554 | 2090 | 0 | 39043.5555 | 2329 | 0 |  | 1241 | 1431 | 127.5946 | 0 | 142.1856 | 0 | 1.2759 | 0 | 1.4219 | 0 | 1.2759 | 1.4219 | 26.5732 | 13.5844 | 25.2973
39043.5559 | 2078 | 0 | 39043.5559 | 1781 | 0 |  | 1283 | 1473 | 126.862 | 0 | 108.7302 | 0 | 1.2686 | 0 | 1.0873 | 0 | 1.2686 | 1.0873 | 27.3041 | 48.5334 | 26.0355
39043.5564 | 1407 | 0 | 39043.5564 | 2095 | 0 |  | 1325 | 1515 | 85.8974 | 0 | 127.8999 | 0 | 0.85897 | 0 | 1.279 | 0 | 0.85897 | 1.279 | 88.0156 | 26.2711 | 87.1567
39043.5569 | 1185 | 0 | 39043.5569 | 2178 | 0 |  | 1367 | 1557 | 72.3443 | 0 | 132.967 | 0 | 0.72344 | 0 | 1.3297 | 0 | 0.72344 | 1.3297 | 123.2388 | 21.4591 | 122.5154

## A1-A2
Open Burn Test 12 |  |  | 2006-11-22 | 13:02 |  |  | Vs = |  | 162.0501 |  | R = | 100
Mixed | 7-C | Tray A | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 1 & 2 | Cable A | Odd-Even
Time-1 | N11 | N12 | Time-2 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R2-G | R1-2
39043.5389 | 1 | 0 | 39043.5389 | 1 | 0 |  | -189.5 | 0.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265338 | 265338 | 265337.9994
39043.5394 | 1 | 0 | 39043.5394 | 1 | 0 |  | -147.5 | 42.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265338 | 265338 | 265337.9994
39043.5398 | 1 | 0 | 39043.5399 | 1 | 0 |  | -105.5 | 84.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265338 | 265338 | 265337.9994
39043.5403 | 1 | 0 | 39043.5403 | 1 | 0 |  | -63.5 | 126.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265338 | 265338 | 265337.9994
39043.5408 | 1 | 0 | 39043.5408 | 1 | 0 |  | -21.5 | 168.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265338 | 265338 | 265337.9994
39043.5413 | 1 | 0 | 39043.5413 | 1 | 0 |  | 20.5 | 210.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265338 | 265338 | 265337.9994
39043.5418 | 1 | 0 | 39043.5418 | 1 | 0 |  | 62.5 | 252.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265338 | 265338 | 265337.9994
39043.5423 | 1 | 0 | 39043.5423 | 1 | 0 |  | 104.5 | 294.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265338 | 265338 | 265337.9994
39043.5428 | 1 | 0 | 39043.5428 | 1 | 0 |  | 146.5 | 336.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265338 | 265338 | 265337.9994
39043.5433 | 1 | 0 | 39043.5433 | 1 | 0 |  | 188.5 | 378.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265338 | 265338 | 265337.9994
39043.5437 | 2 | 0 | 39043.5437 | 1 | 0 |  | 230.5 | 420.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 132619 | 265338 | 132618.9988
39043.5442 | 1224 | 546 | 39043.5442 | 1428 | 658 |  | 272.5 | 462.5 | 74.7253 | 33.3333 | 87.1795 | 40.1709 | 0.74725 | 0.33333 | 0.87179 | 0.40171 | 0.41392 | 0.47009 | 339.3427 | 212.8778 | 110.2052
39043.5447 | 1911 | 188 | 39043.5447 | 2139 | 183 |  | 314.5 | 504.5 | 116.6667 | 11.4774 | 130.5861 | 11.1722 | 1.1667 | 0.11477 | 1.3059 | 0.11172 | 1.0519 | 1.1941 | 67.0264 | 30.6232 | 69.2568
39043.5452 | 2040 | 1 | 39043.5452 | 2148 | 1 |  | 356.5 | 546.5 | 124.5421 | 0.06105 | 131.1355 | 0.06105 | 1.2454 | 0.0006105 | 1.3114 | 0.0006105 | 1.2448 | 1.3107 | 30.1941 | 23.6219 | 11720.5805
39043.5457 | 2609 | 0 | 39043.5457 | 2085 | 0 |  | 398.5 | 588.5 | 159.2796 | 0 | 127.2894 | 0 | 1.5928 | 0 | 1.2729 | 0 | 1.5928 | 1.2729 | 1.7394 | 27.3084 | 0.14657
39043.5462 | 2235 | 0 | 39043.5462 | 2102 | 0 |  | 440.5 | 630.5 | 136.4469 | 0 | 128.3272 | 0 | 1.3645 | 0 | 1.2833 | 0 | 1.3645 | 1.2833 | 18.7642 | 26.2788 | 17.3997
39043.5467 | 2609 | 0 | 39043.5467 | 2436 | 0 |  | 482.5 | 672.5 | 159.2796 | 0 | 148.7179 | 0 | 1.5928 | 0 | 1.4872 | 0 | 1.5928 | 1.4872 | 1.7394 | 8.9647 | 0.14657
39043.5471 | 2073 | 0 | 39043.5472 | 2549 | 0 |  | 524.5 | 714.5 | 126.5568 | 0 | 155.6166 | 0 | 1.2656 | 0 | 1.5562 | 0 | 1.2656 | 1.5562 | 28.0453 | 4.1342 | 26.7798
39043.5476 | 2403 | 0 | 39043.5476 | 2107 | 0 |  | 566.5 | 756.5 | 146.7033 | 0 | 128.6325 | 0 | 1.467 | 0 | 1.2863 | 0 | 1.467 | 1.2863 | 10.4611 | 25.9791 | 8.9941
39043.5481 | 2579 | 0 | 39043.5481 | 2103 | 0 |  | 608 | 798 | 157.4481 | 0 | 128.3883 | 0 | 1.5745 | 0 | 1.2839 | 0 | 1.5745 | 1.2839 | 2.9228 | 26.2187 | 1.3484
39043.5486 | 2429 | 0 | 39043.5486 | 2409 | 0 |  | 650 | 840 | 148.2906 | 0 | 147.0696 | 0 | 1.4829 | 0 | 1.4707 | 0 | 1.4829 | 1.4707 | 9.2787 | 10.186 | 7.7958
39043.5491 | 2163 | 0 | 39043.5491 | 2572 | 0 |  | 692.5 | 882.5 | 132.0513 | 0 | 157.0208 | 0 | 1.3205 | 0 | 1.5702 | 0 | 1.3205 | 1.5702 | 22.7175 | 3.203 | 21.397
39043.5496 | 2223 | 0 | 39043.5496 | 2180 | 0 |  | 734 | 924 | 135.7143 | 0 | 133.0891 | 0 | 1.3571 | 0 | 1.3309 | 0 | 1.3571 | 1.3309 | 19.4053 | 21.7606 | 18.0482
39043.5501 | 2166 | 0 | 39043.5501 | 2623 | 0 |  | 776.5 | 966.5 | 132.2344 | 0 | 160.1343 | 0 | 1.3223 | 0 | 1.6013 | 0 | 1.3223 | 1.6013 | 22.5476 | 1.1963 | 21.2252
39043.5505 | 2287 | 0 | 39043.5506 | 2398 | 0 |  | 818 | 1008 | 139.6215 | 0 | 146.398 | 0 | 1.3962 | 0 | 1.464 | 0 | 1.3962 | 1.464 | 16.0638 | 10.6914 | 14.6676
39043.551 | 2618 | 0 | 39043.551 | 2464 | 0 |  | 860 | 1050 | 159.8291 | 0 | 150.4274 | 0 | 1.5983 | 0 | 1.5043 | 0 | 1.5983 | 1.5043 | 1.3896 | 7.7265 | 0.20868
39043.5515 | 2180 | 0 | 39043.5515 | 2534 | 0 |  | 902 | 1092 | 133.0891 | 0 | 154.7009 | 0 | 1.3309 | 0 | 1.547 | 0 | 1.3309 | 1.547 | 21.7606 | 4.7506 | 20.4297
39043.552 | 2145 | 0 | 39043.552 | 2039 | 0 |  | 944 | 1134 | 130.9524 | 0 | 124.4811 | 0 | 1.3095 | 0 | 1.2448 | 0 | 1.3095 | 1.2448 | 23.7473 | 30.1805 | 22.4378
39043.5525 | 2357 | 0 | 39043.5525 | 2113 | 0 |  | 986 | 1176 | 143.895 | 0 | 128.9988 | 0 | 1.4389 | 0 | 1.29 | 0 | 1.4389 | 1.29 | 12.6169 | 25.6214 | 11.1779
39043.553 | 2570 | 0 | 39043.553 | 2175 | 0 |  | 1028 | 1218 | 156.8987 | 0 | 132.7839 | 0 | 1.569 | 0 | 1.3278 | 0 | 1.569 | 1.3278 | 3.2833 | 22.0405 | 1.7143
39043.5534 | 2638 | 0 | 39043.5535 | 2153 | 0 |  | 1070 | 1260 | 161.0501 | 0 | 131.4408 | 0 | 1.6105 | 0 | 1.3144 | 0 | 1.6105 | 1.3144 | 0.62092 | 23.2875 | 0.98958
39043.5539 | 2119 | 0 | 39043.554 | 2582 | 0 |  | 1112 | 1302 | 129.3651 | 0 | 157.6313 | 0 | 1.2937 | 0 | 1.5763 | 0 | 1.2937 | 1.5763 | 25.2657 | 2.8033 | 23.972
39043.5544 | 2202 | 0 | 39043.5544 | 2281 | 0 |  | 1154 | 1344 | 134.4322 | 0 | 139.2552 | 0 | 1.3443 | 0 | 1.3926 | 0 | 1.3443 | 1.3926 | 20.5441 | 16.3691 | 19.1997
39043.5549 | 2569 | 0 | 39043.5549 | 2487 | 0 |  | 1196 | 1386 | 156.8376 | 0 | 151.8315 | 0 | 1.5684 | 0 | 1.5183 | 0 | 1.5684 | 1.5183 | 3.3235 | 6.7302 | 1.7551
39043.5554 | 2382 | 0 | 39043.5554 | 2524 | 0 |  | 1238 | 1428 | 145.4212 | 0 | 154.0904 | 0 | 1.4542 | 0 | 1.5409 | 0 | 1.4542 | 1.5409 | 11.4349 | 5.1656 | 9.9807
39043.5559 | 2457 | 15 | 39043.5559 | 2457 | 21 |  | 1280 | 1470 | 150 | 0.91575 | 150 | 1.2821 | 1.5 | 0.0091575 | 1.5 | 0.012821 | 1.4908 | 1.4872 | 8.675 | 8.9967 | 100.3585
39043.5564 | 1545 | 582 | 39043.5564 | 1707 | 623 |  | 1322 | 1512 | 94.3223 | 35.5311 | 104.2125 | 38.0342 | 0.94322 | 0.35531 | 1.0421 | 0.38034 | 0.58791 | 0.66178 | 244.6067 | 114.2378 | 48.3186
39043.5569 | 1411 | 757 | 39043.5569 | 1311 | 635 |  | 1364 | 1554 | 86.1416 | 46.2149 | 80.0366 | 38.7668 | 0.86142 | 0.46215 | 0.80037 | 0.38767 | 0.39927 | 0.4127 | 324.2944 | 279.7599 | 47.3321

## Raw IRMS Data
Time | DL1.V2000:B | DL1.V2001:B | DL1.V1500:B | Open Burn Test 12 |  |  | 2006-11-22 | 13:02
39043.5389 | 1 | 0 | 1 | Mixed | 7-C | Tray A | IRMS | 1
39043.5394 | 1 | 0 | 1 |  | 250 kW |  | Bundle
39043.5398 | 1 | 0 | 1
39043.5403 | 1 | 0 | 1
39043.5408 | 1 | 0 | 1
39043.5413 | 1 | 0 | 1
39043.5418 | 1 | 0 | 1
39043.5423 | 1 | 0 | 1
39043.5428 | 1 | 0 | 1
39043.5433 | 1 | 0 | 1
39043.5437 | 2 | 0 | 1
39043.5442 | 1224 | 546 | 1
39043.5447 | 1911 | 188 | 1
39043.5452 | 2040 | 1 | 1
39043.5457 | 2609 | 0 | 1
39043.5462 | 2235 | 0 | 1
39043.5467 | 2609 | 0 | 1
39043.5471 | 2073 | 0 | 1
39043.5476 | 2403 | 0 | 1
39043.5481 | 2579 | 0 | 1
39043.5486 | 2429 | 0 | 1
39043.5491 | 2163 | 0 | 1
39043.5496 | 2223 | 0 | 1
39043.5501 | 2166 | 0 | 1
39043.5505 | 2287 | 0 | 1
39043.551 | 2618 | 0 | 1
39043.5515 | 2180 | 0 | 1
39043.552 | 2145 | 0 | 1
39043.5525 | 2357 | 0 | 1
39043.553 | 2570 | 0 | 1
39043.5534 | 2638 | 0 | 1
39043.5539 | 2119 | 0 | 1
39043.5544 | 2202 | 0 | 1
39043.5549 | 2569 | 0 | 1
39043.5554 | 2382 | 0 | 1
39043.5559 | 2457 | 15 | 1
39043.5564 | 1545 | 582 | 1
39043.5569 | 1411 | 757 | 1
1
39043.5389 | 1 | 0 | 2
39043.5394 | 1 | 0 | 2
39043.5399 | 1 | 0 | 2
39043.5403 | 1 | 0 | 2
39043.5408 | 1 | 0 | 2
39043.5413 | 1 | 0 | 2
39043.5418 | 1 | 0 | 2
39043.5423 | 1 | 0 | 2
39043.5428 | 1 | 0 | 2
39043.5433 | 1 | 0 | 2
39043.5437 | 1 | 0 | 2
39043.5442 | 1428 | 658 | 2
39043.5447 | 2139 | 183 | 2
39043.5452 | 2148 | 1 | 2
39043.5457 | 2085 | 0 | 2
39043.5462 | 2102 | 0 | 2
39043.5467 | 2436 | 0 | 2
39043.5472 | 2549 | 0 | 2
39043.5476 | 2107 | 0 | 2
39043.5481 | 2103 | 0 | 2
39043.5486 | 2409 | 0 | 2
39043.5491 | 2572 | 0 | 2
39043.5496 | 2180 | 0 | 2
39043.5501 | 2623 | 0 | 2
39043.5506 | 2398 | 0 | 2
39043.551 | 2464 | 0 | 2
39043.5515 | 2534 | 0 | 2
39043.552 | 2039 | 0 | 2
39043.5525 | 2113 | 0 | 2
39043.553 | 2175 | 0 | 2
39043.5535 | 2153 | 0 | 2
39043.554 | 2582 | 0 | 2
39043.5544 | 2281 | 0 | 2
39043.5549 | 2487 | 0 | 2
39043.5554 | 2524 | 0 | 2
39043.5559 | 2457 | 21 | 2
39043.5564 | 1707 | 623 | 2
39043.5569 | 1311 | 635 | 2
2
39043.5389 | 1 | 0 | 3
39043.5394 | 1 | 0 | 3
39043.5399 | 1 | 0 | 3
39043.5404 | 1 | 0 | 3
39043.5408 | 1 | 0 | 3
39043.5413 | 1 | 0 | 3
39043.5418 | 1 | 0 | 3
39043.5423 | 1 | 0 | 3
39043.5428 | 1 | 0 | 3
39043.5433 | 1 | 0 | 3
39043.5438 | 1 | 0 | 3
39043.5442 | 1351 | 0 | 3
39043.5447 | 1976 | 0 | 3
39043.5452 | 2462 | 0 | 3
39043.5457 | 2202 | 0 | 3
39043.5462 | 2530 | 0 | 3
39043.5467 | 2612 | 0 | 3
39043.5472 | 2340 | 0 | 3
39043.5477 | 2277 | 0 | 3
39043.5481 | 2235 | 0 | 3
39043.5486 | 2492 | 0 | 3
39043.5491 | 2097 | 0 | 3
39043.5496 | 2333 | 0 | 3
39043.5501 | 2629 | 0 | 3
39043.5506 | 2100 | 0 | 3
39043.5511 | 2172 | 0 | 3
39043.5515 | 2301 | 0 | 3
39043.552 | 2354 | 0 | 3
39043.5525 | 2039 | 0 | 3
39043.553 | 2120 | 0 | 3
39043.5535 | 2223 | 0 | 3
39043.554 | 2362 | 0 | 3
39043.5545 | 2162 | 0 | 3
39043.5549 | 2513 | 0 | 3
39043.5554 | 2090 | 0 | 3
39043.5559 | 2078 | 0 | 3
39043.5564 | 1407 | 0 | 3
39043.5569 | 1185 | 0 | 3
3
39043.5389 | 1 | 0 | 4
39043.5394 | 1 | 0 | 4
39043.5399 | 1 | 0 | 4
39043.5404 | 1 | 0 | 4
39043.5409 | 1 | 0 | 4
39043.5414 | 1 | 0 | 4
39043.5418 | 1 | 0 | 4
39043.5423 | 1 | 0 | 4
39043.5428 | 1 | 0 | 4
39043.5433 | 1 | 0 | 4
39043.5438 | 1 | 0 | 4
39043.5443 | 4 | 0 | 4
39043.5448 | 616 | 0 | 4
39043.5452 | 1481 | 0 | 4
39043.5457 | 1554 | 0 | 4
39043.5462 | 2345 | 0 | 4
39043.5467 | 1972 | 0 | 4
39043.5472 | 2007 | 0 | 4
39043.5477 | 2366 | 0 | 4
39043.5482 | 2375 | 0 | 4
39043.5486 | 1882 | 0 | 4
39043.5491 | 1851 | 0 | 4
39043.5496 | 1728 | 0 | 4
39043.5501 | 2232 | 0 | 4
39043.5506 | 2245 | 0 | 4
39043.5511 | 2046 | 0 | 4
39043.5516 | 2508 | 0 | 4
39043.552 | 2463 | 0 | 4
39043.5525 | 2135 | 0 | 4
39043.553 | 2316 | 0 | 4
39043.5535 | 2350 | 0 | 4
39043.554 | 2507 | 0 | 4
39043.5545 | 2147 | 0 | 4
39043.555 | 2460 | 0 | 4
39043.5555 | 2329 | 0 | 4
39043.5559 | 1781 | 0 | 4
39043.5564 | 2095 | 0 | 4
39043.5569 | 2178 | 0 | 4
4
39043.5389 | 1 | 0 | 5
39043.5394 | 1 | 0 | 5
39043.5399 | 1 | 0 | 5
39043.5404 | 1 | 0 | 5
39043.5409 | 1 | 0 | 5
39043.5414 | 1 | 0 | 5
39043.5419 | 1 | 0 | 5
39043.5423 | 1 | 0 | 5
39043.5428 | 1 | 0 | 5
39043.5433 | 1 | 0 | 5
39043.5438 | 1 | 0 | 5
39043.5443 | 1145 | 0 | 5
39043.5448 | 2125 | 0 | 5
39043.5453 | 2552 | 0 | 5
39043.5457 | 2152 | 0 | 5
39043.5462 | 2340 | 0 | 5
39043.5467 | 2630 | 0 | 5
39043.5472 | 2580 | 0 | 5
39043.5477 | 2068 | 0 | 5
39043.5482 | 2609 | 0 | 5
39043.5487 | 2154 | 0 | 5
39043.5491 | 2484 | 0 | 5
39043.5496 | 2350 | 0 | 5
39043.5501 | 2565 | 0 | 5
39043.5506 | 2221 | 0 | 5
39043.5511 | 2071 | 0 | 5
39043.5516 | 2064 | 0 | 5
39043.5521 | 2044 | 0 | 5
39043.5525 | 2392 | 0 | 5
39043.553 | 2354 | 0 | 5
39043.5535 | 2132 | 0 | 5
39043.554 | 2554 | 0 | 5
39043.5545 | 2205 | 0 | 5
39043.555 | 2279 | 0 | 5
39043.5555 | 2357 | 0 | 5
39043.5559 | 2072 | 0 | 5
39043.5564 | 1083 | 0 | 5
39043.5569 | 1541 | 0 | 5
5
39043.539 | 1 | 0 | 6
39043.5394 | 1 | 0 | 6
39043.5399 | 1 | 0 | 6
39043.5404 | 1 | 0 | 6
39043.5414 | 1 | 0 | 6
39043.5419 | 1 | 0 | 6
39043.5424 | 1 | 0 | 6
39043.5428 | 1 | 0 | 6
39043.5433 | 1 | 0 | 6
39043.5438 | 1 | 0 | 6
39043.5443 | 43 | 0 | 6
39043.5448 | 346 | 0 | 6
39043.5453 | 2269 | 0 | 6
39043.5458 | 1914 | 0 | 6
39043.5462 | 2342 | 0 | 6
39043.5467 | 2010 | 0 | 6
39043.5472 | 2172 | 0 | 6
39043.5477 | 2514 | 0 | 6
39043.5482 | 2303 | 0 | 6
39043.5487 | 1828 | 0 | 6
39043.5492 | 2270 | 0 | 6
39043.5497 | 1903 | 0 | 6
39043.5501 | 2309 | 0 | 6
39043.5506 | 2229 | 0 | 6
39043.5511 | 2067 | 0 | 6
39043.5516 | 2488 | 0 | 6
39043.5521 | 2454 | 0 | 6
39043.5526 | 2505 | 0 | 6
39043.553 | 2132 | 0 | 6
39043.5535 | 2339 | 0 | 6
39043.554 | 2001 | 0 | 6
39043.5545 | 2209 | 0 | 6
39043.555 | 1896 | 0 | 6
39043.5555 | 2418 | 0 | 6
39043.556 | 2013 | 0 | 6
39043.5564 | 1589 | 0 | 6
39043.5569 | 2371 | 0 | 6
6
39043.539 | 1 | 0 | 7
39043.5395 | 1 | 0 | 7
39043.5399 | 1 | 0 | 7
39043.5404 | 1 | 0 | 7
39043.5409 | 1 | 0 | 7
39043.5414 | 1 | 0 | 7
39043.5419 | 1 | 0 | 7
39043.5424 | 1 | 0 | 7
39043.5429 | 1 | 0 | 7
39043.5433 | 1 | 0 | 7
39043.5438 | 1 | 0 | 7
39043.5443 | 1236 | 0 | 7
39043.5448 | 2124 | 0 | 7
39043.5453 | 2540 | 0 | 7
39043.5458 | 2374 | 0 | 7
39043.5463 | 2304 | 0 | 7
39043.5467 | 2621 | 0 | 7
39043.5472 | 2261 | 0 | 7
39043.5477 | 2211 | 0 | 7
39043.5482 | 2263 | 0 | 7
39043.5487 | 2517 | 0 | 7
39043.5492 | 2432 | 0 | 7
39043.5497 | 2074 | 0 | 7
39043.5502 | 2313 | 0 | 7
39043.5506 | 2123 | 0 | 7
39043.5511 | 2447 | 0 | 7
39043.5516 | 2469 | 0 | 7
39043.5521 | 2383 | 0 | 7
39043.5526 | 2058 | 0 | 7
39043.5531 | 2632 | 0 | 7
39043.5536 | 2225 | 0 | 7
39043.554 | 2393 | 0 | 7
39043.5545 | 2191 | 0 | 7
39043.555 | 2063 | 0 | 7
39043.5555 | 2304 | 0 | 7
39043.556 | 2251 | 0 | 7
39043.5565 | 1752 | 492 | 7
39043.557 | 1439 | 377 | 7
7
39043.539 | 1 | 0 | 8
39043.5395 | 1 | 0 | 8
39043.54 | 1 | 0 | 8
39043.5404 | 1 | 0 | 8
39043.5409 | 1 | 0 | 8
39043.5414 | 1 | 0 | 8
39043.5419 | 1 | 0 | 8
39043.5424 | 1 | 0 | 8
39043.5429 | 1480 | 0 | 8
39043.5434 | 1920 | 0 | 8
39043.5438 | 1916 | 0 | 8
39043.5443 | 2563 | 0 | 8
39043.5448 | 2284 | 0 | 8
39043.5453 | 2195 | 0 | 8
39043.5458 | 2124 | 0 | 8
39043.5463 | 2080 | 0 | 8
39043.5468 | 2208 | 0 | 8
39043.5472 | 2209 | 0 | 8
39043.5477 | 2216 | 0 | 8
39043.5482 | 2558 | 0 | 8
39043.5487 | 2086 | 0 | 8
39043.5492 | 2385 | 0 | 8
39043.5497 | 2251 | 0 | 8
39043.5502 | 2485 | 0 | 8
39043.5506 | 2193 | 0 | 8
39043.5511 | 2488 | 0 | 8
39043.5516 | 2378 | 0 | 8
39043.5521 | 2652 | 0 | 8
39043.5526 | 2305 | 0 | 8
39043.5531 | 2509 | 0 | 8
39043.5536 | 2091 | 0 | 8
39043.5541 | 2149 | 0 | 8
39043.5545 | 2175 | 0 | 8
39043.555 | 2156 | 0 | 8
39043.5555 | 2200 | 0 | 8
39043.556 | 2034 | 0 | 8
39043.5565 | 1437 | 543 | 8
39043.557 | 1432 | 421 | 8
8
39043.539 | 1 | 0 | 9
39043.5395 | 1 | 0 | 9
39043.54 | 1 | 0 | 9
39043.5405 | 1 | 0 | 9
39043.5409 | 1 | 0 | 9
39043.5414 | 1 | 0 | 9
39043.5419 | 1 | 0 | 9
39043.5424 | 1 | 0 | 9
39043.5429 | 1 | 0 | 9
39043.5434 | 1 | 0 | 9
39043.5439 | 2 | 0 | 9
39043.5444 | 1478 | 0 | 9
39043.5448 | 1903 | 0 | 9
39043.5453 | 1989 | 0 | 9
39043.5458 | 2371 | 0 | 9
39043.5463 | 2418 | 0 | 9
39043.5468 | 2442 | 0 | 9
39043.5473 | 2439 | 0 | 9
39043.5478 | 2542 | 0 | 9
39043.5482 | 2590 | 0 | 9
39043.5487 | 2119 | 0 | 9
39043.5492 | 2134 | 0 | 9
39043.5497 | 2364 | 0 | 9
39043.5502 | 2571 | 0 | 9
39043.5507 | 2443 | 0 | 9
39043.5512 | 2166 | 0 | 9
39043.5516 | 2072 | 0 | 9
39043.5521 | 2179 | 0 | 9
39043.5526 | 2498 | 0 | 9
39043.5531 | 2270 | 0 | 9
39043.5536 | 2468 | 0 | 9
39043.5541 | 2625 | 0 | 9
39043.5546 | 2363 | 0 | 9
39043.555 | 2102 | 0 | 9
39043.5555 | 2298 | 0 | 9
39043.556 | 2128 | 0 | 9
39043.5565 | 1172 | 665 | 9
39043.557 | 1671 | 439 | 9
9
39043.539 | 1 | 0 | 10
39043.5395 | 1 | 0 | 10
39043.54 | 1 | 0 | 10
39043.5405 | 1 | 0 | 10
39043.541 | 1 | 0 | 10
39043.5414 | 1 | 0 | 10
39043.5419 | 1 | 0 | 10
39043.5424 | 1 | 0 | 10
39043.5429 | 7 | 0 | 10
39043.5434 | 1674 | 0 | 10
39043.5439 | 2191 | 0 | 10
39043.5444 | 2253 | 0 | 10
39043.5448 | 2271 | 0 | 10
39043.5453 | 2117 | 0 | 10
39043.5458 | 2605 | 0 | 10
39043.5463 | 2416 | 0 | 10
39043.5468 | 2269 | 0 | 10
39043.5473 | 2253 | 0 | 10
39043.5478 | 2293 | 0 | 10
39043.5483 | 2478 | 0 | 10
39043.5487 | 2066 | 0 | 10
39043.5492 | 2332 | 0 | 10
39043.5497 | 2146 | 0 | 10
39043.5502 | 2048 | 0 | 10
39043.5507 | 2347 | 0 | 10
39043.5512 | 2235 | 0 | 10
39043.5517 | 2368 | 0 | 10
39043.5521 | 2236 | 0 | 10
39043.5526 | 2119 | 0 | 10
39043.5531 | 2133 | 0 | 10
39043.5536 | 2162 | 0 | 10
39043.5541 | 2155 | 0 | 10
39043.5546 | 2169 | 0 | 10
39043.5551 | 2384 | 0 | 10
39043.5555 | 2609 | 0 | 10
39043.556 | 2437 | 0 | 10
39043.5565 | 1354 | 701 | 10
39043.557 | 1371 | 384 | 10
10
39043.539 | 1 | 0 | 11
39043.5395 | 1 | 0 | 11
39043.54 | 1 | 0 | 11
39043.5405 | 1 | 0 | 11
39043.541 | 1 | 0 | 11
39043.5415 | 1 | 0 | 11
39043.542 | 1 | 0 | 11
39043.5424 | 1 | 0 | 11
39043.5429 | 1 | 0 | 11
39043.5434 | 1 | 0 | 11
39043.5439 | 4 | 0 | 11
39043.5444 | 1764 | 0 | 11
39043.5449 | 1869 | 0 | 11
39043.5454 | 2304 | 0 | 11
39043.5458 | 2446 | 0 | 11
39043.5463 | 2355 | 0 | 11
39043.5468 | 2344 | 0 | 11
39043.5473 | 2475 | 0 | 11
39043.5478 | 2152 | 0 | 11
39043.5483 | 2488 | 0 | 11
39043.5488 | 2543 | 0 | 11
39043.5492 | 2395 | 0 | 11
39043.5497 | 2278 | 0 | 11
39043.5502 | 2319 | 0 | 11
39043.5507 | 2556 | 0 | 11
39043.5512 | 2607 | 0 | 11
39043.5517 | 2578 | 0 | 11
39043.5522 | 2341 | 0 | 11
39043.5526 | 2526 | 0 | 11
39043.5531 | 2374 | 0 | 11
39043.5536 | 2280 | 0 | 11
39043.5541 | 2063 | 0 | 11
39043.5546 | 2553 | 0 | 11
39043.5551 | 2569 | 0 | 11
39043.5556 | 2032 | 0 | 11
39043.556 | 2102 | 0 | 11
39043.5565 | 924 | 0 | 11
39043.557 | 1382 | 0 | 11
11
39043.5391 | 1 | 0 | 12
39043.5395 | 1 | 0 | 12
39043.54 | 1 | 0 | 12
39043.5405 | 1 | 0 | 12
39043.541 | 1 | 0 | 12
39043.5415 | 1 | 0 | 12
39043.542 | 1 | 0 | 12
39043.5425 | 1 | 0 | 12
39043.5429 | 1 | 0 | 12
39043.5434 | 1 | 0 | 12
39043.5439 | 1 | 0 | 12
39043.5444 | 2 | 0 | 12
39043.5449 | 1150 | 0 | 12
39043.5454 | 2195 | 0 | 12
39043.5459 | 1829 | 0 | 12
39043.5463 | 2565 | 0 | 12
39043.5468 | 2394 | 0 | 12
39043.5473 | 2472 | 0 | 12
39043.5478 | 2550 | 0 | 12
39043.5483 | 2096 | 0 | 12
39043.5488 | 1988 | 0 | 12
39043.5493 | 2226 | 0 | 12
39043.5497 | 2464 | 0 | 12
39043.5502 | 2038 | 0 | 12
39043.5507 | 2403 | 0 | 12
39043.5512 | 2431 | 0 | 12
39043.5517 | 2367 | 0 | 12
39043.5522 | 2581 | 0 | 12
39043.5527 | 2366 | 0 | 12
39043.5531 | 2371 | 0 | 12
39043.5536 | 2488 | 0 | 12
39043.5541 | 2562 | 0 | 12
39043.5546 | 2373 | 0 | 12
39043.5551 | 2264 | 0 | 12
39043.5556 | 2073 | 0 | 12
39043.5561 | 1982 | 0 | 12
39043.5566 | 2306 | 0 | 12
39043.557 | 1745 | 0 | 12
12
39043.5391 | 1 | 0 | 13
39043.5395 | 1 | 0 | 13
39043.54 | 1 | 0 | 13
39043.5405 | 1 | 0 | 13
39043.541 | 1 | 0 | 13
39043.5415 | 1 | 0 | 13
39043.542 | 1 | 0 | 13
39043.5425 | 1 | 0 | 13
39043.543 | 1 | 0 | 13
39043.5434 | 1 | 0 | 13
39043.5439 | 10 | 0 | 13
39043.5444 | 1835 | 0 | 13
39043.5449 | 2274 | 0 | 13
39043.5454 | 2062 | 0 | 13
39043.5459 | 2613 | 0 | 13
39043.5464 | 2347 | 0 | 13
39043.5468 | 2406 | 0 | 13
39043.5473 | 2431 | 0 | 13
39043.5478 | 2088 | 0 | 13
39043.5483 | 2244 | 0 | 13
39043.5488 | 2187 | 0 | 13
39043.5493 | 2143 | 0 | 13
39043.5498 | 2244 | 0 | 13
39043.5502 | 2373 | 0 | 13
39043.5507 | 2619 | 0 | 13
39043.5512 | 2547 | 0 | 13
39043.5517 | 2324 | 0 | 13
39043.5522 | 2445 | 0 | 13
39043.5527 | 2510 | 0 | 13
39043.5532 | 2617 | 0 | 13
39043.5536 | 2463 | 0 | 13
39043.5541 | 2039 | 0 | 13
39043.5546 | 2302 | 0 | 13
39043.5551 | 2602 | 0 | 13
39043.5556 | 2490 | 0 | 13
39043.5561 | 2056 | 0 | 13
39043.5566 | 778 | 0 | 13
39043.557 | 1632 | 0 | 13
13
39043.5391 | 1 | 0 | 14
39043.5396 | 1 | 0 | 14
39043.5401 | 1 | 0 | 14
39043.5405 | 1 | 0 | 14
39043.541 | 1 | 0 | 14
39043.5415 | 1 | 0 | 14
39043.542 | 1 | 0 | 14
39043.5425 | 1 | 0 | 14
39043.543 | 1 | 0 | 14
39043.5435 | 1 | 0 | 14
39043.5439 | 165 | 0 | 14
39043.5444 | 2222 | 0 | 14
39043.5449 | 2034 | 0 | 14
39043.5454 | 2149 | 0 | 14
39043.5459 | 2163 | 0 | 14
39043.5464 | 2579 | 0 | 14
39043.5469 | 2514 | 0 | 14
39043.5473 | 2618 | 0 | 14
39043.5478 | 2069 | 0 | 14
39043.5483 | 2643 | 0 | 14
39043.5488 | 2337 | 0 | 14
39043.5493 | 2080 | 0 | 14
39043.5498 | 2214 | 0 | 14
39043.5503 | 2542 | 0 | 14
39043.5508 | 2056 | 0 | 14
39043.5512 | 2073 | 0 | 14
39043.5517 | 2117 | 0 | 14
39043.5522 | 2607 | 0 | 14
39043.5527 | 2618 | 0 | 14
39043.5532 | 2285 | 0 | 14
39043.5537 | 2614 | 0 | 14
39043.5542 | 2628 | 0 | 14
39043.5546 | 2073 | 0 | 14
39043.5551 | 2404 | 0 | 14
39043.5556 | 2223 | 0 | 14
39043.5561 | 1862 | 0 | 14
39043.5566 | 989 | 0 | 14
39043.5571 | 1307 | 0 | 14
14
39043.5391 | 1 | 0 | 15
39043.5396 | 1 | 0 | 15
39043.5401 | 1 | 0 | 15
39043.5406 | 1 | 0 | 15
39043.541 | 1 | 0 | 15
39043.5415 | 1 | 0 | 15
39043.542 | 1 | 0 | 15
39043.5425 | 1 | 0 | 15
39043.543 | 1 | 0 | 15
39043.5435 | 1 | 0 | 15
39043.544 | 118 | 0 | 15
39043.5444 | 2286 | 0 | 15
39043.5449 | 2238 | 0 | 15
39043.5454 | 2173 | 0 | 15
39043.5459 | 2119 | 0 | 15
39043.5464 | 2191 | 0 | 15
39043.5469 | 2590 | 0 | 15
39043.5474 | 2086 | 0 | 15
39043.5478 | 2042 | 0 | 15
39043.5483 | 2051 | 0 | 15
39043.5488 | 2616 | 0 | 15
39043.5493 | 2549 | 0 | 15
39043.5498 | 2544 | 0 | 15
39043.5503 | 2252 | 0 | 15
39043.5508 | 2643 | 0 | 15
39043.5512 | 2200 | 0 | 15
39043.5517 | 2206 | 0 | 15
39043.5522 | 2039 | 0 | 15
39043.5527 | 2040 | 0 | 15
39043.5532 | 2606 | 0 | 15
39043.5537 | 2054 | 0 | 15
39043.5542 | 2118 | 0 | 15
39043.5547 | 2380 | 0 | 15
39043.5551 | 2580 | 0 | 15
39043.5556 | 2059 | 0 | 15
39043.5561 | 2013 | 5 | 15
39043.5566 | 1428 | 723 | 15
39043.5571 | 1636 | 511 | 15
15
39043.5391 | 1 | 0 | 16
39043.5396 | 1 | 0 | 16
39043.5401 | 1 | 0 | 16
39043.5406 | 1 | 0 | 16
39043.5411 | 1 | 0 | 16
39043.5416 | 1 | 0 | 16
39043.542 | 1 | 0 | 16
39043.5425 | 1 | 0 | 16
39043.5435 | 1237 | 0 | 16
39043.544 | 2556 | 0 | 16
39043.5445 | 2044 | 0 | 16
39043.545 | 2169 | 0 | 16
39043.5454 | 2648 | 0 | 16
39043.5459 | 2281 | 0 | 16
39043.5464 | 2352 | 0 | 16
39043.5469 | 2130 | 0 | 16
39043.5474 | 2301 | 0 | 16
39043.5479 | 2072 | 0 | 16
39043.5483 | 2135 | 0 | 16
39043.5488 | 2108 | 0 | 16
39043.5493 | 2402 | 0 | 16
39043.5498 | 2124 | 0 | 16
39043.5503 | 2408 | 0 | 16
39043.5508 | 2435 | 0 | 16
39043.5513 | 2369 | 0 | 16
39043.5518 | 2600 | 0 | 16
39043.5522 | 2656 | 0 | 16
39043.5527 | 2581 | 0 | 16
39043.5532 | 2210 | 0 | 16
39043.5537 | 2616 | 0 | 16
39043.5542 | 2302 | 0 | 16
39043.5547 | 2136 | 0 | 16
39043.5552 | 2393 | 0 | 16
39043.5556 | 2392 | 0 | 16
39043.5561 | 2250 | 3 | 16
39043.5566 | 1323 | 668 | 16
39043.5571 | 1202 | 662 | 16
16
39043.5391 | 1 | 0 | 17
39043.5396 | 1 | 0 | 17
39043.5401 | 1 | 0 | 17
39043.5406 | 1 | 0 | 17
39043.5411 | 1 | 0 | 17
39043.5416 | 1 | 0 | 17
39043.542 | 1 | 0 | 17
39043.5425 | 1 | 0 | 17
39043.543 | 1 | 0 | 17
39043.5435 | 1 | 0 | 17
39043.544 | 164 | 0 | 17
39043.5445 | 2237 | 0 | 17
39043.545 | 2404 | 0 | 17
39043.5455 | 2527 | 0 | 17
39043.5459 | 2486 | 0 | 17
39043.5464 | 2075 | 0 | 17
39043.5469 | 2631 | 0 | 17
39043.5474 | 2640 | 0 | 17
39043.5479 | 2317 | 0 | 17
39043.5484 | 2419 | 0 | 17
39043.5489 | 2250 | 0 | 17
39043.5493 | 2108 | 0 | 17
39043.5498 | 2216 | 0 | 17
39043.5503 | 2040 | 0 | 17
39043.5508 | 2321 | 0 | 17
39043.5513 | 2191 | 0 | 17
39043.5518 | 2230 | 0 | 17
39043.5523 | 2459 | 0 | 17
39043.5527 | 2041 | 0 | 17
39043.5532 | 2614 | 0 | 17
39043.5537 | 2160 | 0 | 17
39043.5542 | 2127 | 0 | 17
39043.5547 | 2618 | 0 | 17
39043.5552 | 2088 | 0 | 17
39043.5557 | 2156 | 0 | 17
39043.5561 | 1994 | 19 | 17
39043.5566 | 1354 | 767 | 17
39043.5571 | 1201 | 579 | 17
17
39043.5391 | 1 | 0 | 18
39043.5396 | 1 | 0 | 18
39043.5401 | 1 | 0 | 18
39043.5406 | 1 | 0 | 18
39043.5411 | 1 | 0 | 18
39043.5416 | 1 | 0 | 18
39043.5421 | 1 | 0 | 18
39043.5425 | 1 | 0 | 18
39043.543 | 727 | 0 | 18
39043.5435 | 2205 | 0 | 18
39043.544 | 2493 | 0 | 18
39043.5445 | 2182 | 0 | 18
39043.545 | 2575 | 0 | 18
39043.5455 | 2646 | 0 | 18
39043.5459 | 2164 | 0 | 18
39043.5464 | 2121 | 0 | 18
39043.5469 | 2603 | 0 | 18
39043.5474 | 2423 | 0 | 18
39043.5479 | 2653 | 0 | 18
39043.5484 | 2224 | 0 | 18
39043.5489 | 2106 | 0 | 18
39043.5494 | 2265 | 0 | 18
39043.5498 | 2612 | 0 | 18
39043.5503 | 2502 | 0 | 18
39043.5508 | 2153 | 0 | 18
39043.5513 | 2476 | 0 | 18
39043.5518 | 2499 | 0 | 18
39043.5523 | 2446 | 0 | 18
39043.5528 | 2387 | 0 | 18
39043.5532 | 2538 | 0 | 18
39043.5537 | 2651 | 0 | 18
39043.5542 | 2357 | 0 | 18
39043.5547 | 2596 | 0 | 18
39043.5552 | 2034 | 0 | 18
39043.5557 | 2131 | 0 | 18
39043.5562 | 1918 | 39 | 18
39043.5566 | 1410 | 820 | 18
39043.5571 | 1060 | 825 | 18
18
39043.5392 | 1 | 0 | 19
39043.5397 | 1 | 0 | 19
39043.5401 | 1 | 0 | 19
39043.5406 | 1 | 0 | 19
39043.5411 | 1 | 0 | 19
39043.5416 | 1 | 0 | 19
39043.5421 | 1 | 0 | 19
39043.5426 | 1 | 0 | 19
39043.5431 | 1 | 0 | 19
39043.5435 | 1 | 0 | 19
39043.544 | 1 | 0 | 19
39043.5445 | 988 | 920 | 19
39043.545 | 2236 | 137 | 19
39043.5455 | 1750 | 373 | 19
39043.546 | 1850 | 393 | 19
39043.5469 | 2201 | 0 | 19
39043.5474 | 2129 | 1 | 19
39043.5479 | 2331 | 0 | 19
39043.5484 | 2015 | 2 | 19
39043.5489 | 1967 | 344 | 19
39043.5494 | 1350 | 743 | 19
39043.5499 | 2300 | 0 | 19
39043.5503 | 2546 | 0 | 19
39043.5508 | 2609 | 0 | 19
39043.5518 | 2573 | 0 | 19
39043.5523 | 2110 | 0 | 19
39043.5528 | 2558 | 0 | 19
39043.5533 | 2609 | 0 | 19
39043.5537 | 2411 | 0 | 19
39043.5542 | 2182 | 222 | 19
39043.5547 | 2408 | 0 | 19
39043.5552 | 2469 | 0 | 19
39043.5557 | 2057 | 29 | 19
39043.5562 | 2314 | 129 | 19
39043.5567 | 1050 | 740 | 19
39043.5572 | 1855 | 265 | 19
19
39043.5392 | 1 | 0 | 20
39043.5397 | 1 | 0 | 20
39043.5402 | 1 | 0 | 20
39043.5406 | 1 | 0 | 20
39043.5411 | 1 | 0 | 20
39043.5416 | 1 | 0 | 20
39043.5421 | 1 | 0 | 20
39043.5426 | 1 | 0 | 20
39043.5431 | 1 | 0 | 20
39043.5436 | 1 | 0 | 20
39043.544 | 170 | 0 | 20
39043.5445 | 1265 | 1198 | 20
39043.545 | 1513 | 419 | 20
39043.5455 | 1193 | 707 | 20
39043.546 | 2138 | 333 | 20
39043.5465 | 2528 | 0 | 20
39043.547 | 2474 | 0 | 20
39043.5474 | 2514 | 1 | 20
39043.5479 | 2510 | 0 | 20
39043.5484 | 1965 | 260 | 20
39043.5489 | 2039 | 416 | 20
39043.5494 | 2058 | 608 | 20
39043.5499 | 2563 | 0 | 20
39043.5504 | 2225 | 0 | 20
39043.5508 | 2503 | 0 | 20
39043.5513 | 2018 | 0 | 20
39043.5518 | 2356 | 0 | 20
39043.5523 | 2594 | 0 | 20
39043.5528 | 2294 | 0 | 20
39043.5533 | 2107 | 0 | 20
39043.5538 | 2287 | 0 | 20
39043.5542 | 2249 | 482 | 20
39043.5547 | 2249 | 0 | 20
39043.5552 | 2145 | 0 | 20
39043.5557 | 1987 | 403 | 20
39043.5562 | 1752 | 504 | 20
39043.5567 | 1299 | 928 | 20
39043.5572 | 1378 | 407 | 20
20
39043.5392 | 1 | 0 | 21
39043.5397 | 1 | 0 | 21
39043.5402 | 1 | 0 | 21
39043.5407 | 1 | 0 | 21
39043.5411 | 1 | 0 | 21
39043.5416 | 1 | 0 | 21
39043.5421 | 1 | 0 | 21
39043.5426 | 1 | 0 | 21
39043.5431 | 1 | 0 | 21
39043.5436 | 1 | 0 | 21
39043.5441 | 1 | 0 | 21
39043.5445 | 297 | 0 | 21
39043.545 | 1538 | 0 | 21
39043.5455 | 2218 | 0 | 21
39043.546 | 1959 | 0 | 21
39043.5465 | 2461 | 0 | 21
39043.547 | 2235 | 0 | 21
39043.5475 | 2095 | 0 | 21
39043.5479 | 2228 | 0 | 21
39043.5484 | 1820 | 0 | 21
39043.5489 | 2321 | 0 | 21
39043.5494 | 1939 | 0 | 21
39043.5499 | 2045 | 0 | 21
39043.5504 | 2450 | 0 | 21
39043.5509 | 2174 | 0 | 21
39043.5514 | 2548 | 0 | 21
39043.5518 | 2604 | 0 | 21
39043.5523 | 2572 | 0 | 21
39043.5528 | 2499 | 0 | 21
39043.5533 | 2118 | 0 | 21
39043.5538 | 2063 | 0 | 21
39043.5543 | 1647 | 0 | 21
39043.5547 | 2109 | 0 | 21
39043.5552 | 2410 | 0 | 21
39043.5557 | 2422 | 0 | 21
39043.5562 | 2231 | 0 | 21
39043.5567 | 1699 | 0 | 21
39043.5572 | 2467 | 0 | 21
21
39043.5392 | 1 | 0 | 22
39043.5397 | 1 | 0 | 22
39043.5402 | 1 | 0 | 22
39043.5407 | 1 | 0 | 22
39043.5412 | 1 | 0 | 22
39043.5416 | 1 | 0 | 22
39043.5421 | 1 | 0 | 22
39043.5426 | 1 | 0 | 22
39043.5431 | 626 | 0 | 22
39043.5436 | 2307 | 0 | 22
39043.5441 | 2451 | 0 | 22
39043.5446 | 2261 | 0 | 22
39043.545 | 2086 | 0 | 22
39043.5455 | 2395 | 0 | 22
39043.546 | 2173 | 0 | 22
39043.5465 | 2428 | 0 | 22
39043.547 | 2093 | 0 | 22
39043.5475 | 2048 | 0 | 22
39043.548 | 2651 | 0 | 22
39043.5484 | 2644 | 0 | 22
39043.5489 | 2252 | 0 | 22
39043.5494 | 2118 | 0 | 22
39043.5499 | 2282 | 0 | 22
39043.5504 | 2576 | 0 | 22
39043.5509 | 2492 | 0 | 22
39043.5514 | 2336 | 0 | 22
39043.5519 | 2373 | 0 | 22
39043.5523 | 2512 | 0 | 22
39043.5528 | 2654 | 0 | 22
39043.5533 | 2194 | 0 | 22
39043.5538 | 2267 | 0 | 22
39043.5543 | 2053 | 0 | 22
39043.5548 | 2208 | 0 | 22
39043.5553 | 2312 | 0 | 22
39043.5557 | 2497 | 0 | 22
39043.5562 | 1872 | 0 | 22
39043.5567 | 913 | 0 | 22
39043.5572 | 1024 | 0 | 22
22
39043.5392 | 1 | 0 | 23
39043.5397 | 1 | 0 | 23
39043.5402 | 1 | 0 | 23
39043.5407 | 1 | 0 | 23
39043.5412 | 1 | 0 | 23
39043.5417 | 1 | 0 | 23
39043.5421 | 1 | 0 | 23
39043.5426 | 1 | 0 | 23
39043.5431 | 1 | 0 | 23
39043.5436 | 1 | 0 | 23
39043.5441 | 2 | 0 | 23
39043.5446 | 44 | 0 | 23
39043.5451 | 1394 | 0 | 23
39043.5455 | 1761 | 0 | 23
39043.546 | 1620 | 0 | 23
39043.5465 | 2502 | 0 | 23
39043.547 | 2518 | 0 | 23
39043.5475 | 2444 | 0 | 23
39043.548 | 2096 | 0 | 23
39043.5485 | 2119 | 0 | 23
39043.5489 | 1893 | 0 | 23
39043.5494 | 2200 | 0 | 23
39043.5499 | 2298 | 0 | 23
39043.5504 | 2431 | 0 | 23
39043.5509 | 2305 | 0 | 23
39043.5514 | 2607 | 0 | 23
39043.5519 | 2612 | 0 | 23
39043.5523 | 2211 | 0 | 23
39043.5528 | 2563 | 0 | 23
39043.5533 | 2043 | 0 | 23
39043.5538 | 2391 | 0 | 23
39043.5543 | 1800 | 0 | 23
39043.5548 | 2014 | 0 | 23
39043.5553 | 2420 | 0 | 23
39043.5558 | 1616 | 0 | 23
39043.5562 | 1926 | 0 | 23
39043.5567 | 1537 | 0 | 23
39043.5572 | 2485 | 0 | 23
23
39043.5392 | 1 | 0 | 24
39043.5397 | 1 | 0 | 24
39043.5402 | 1 | 0 | 24
39043.5407 | 1 | 0 | 24
39043.5412 | 1 | 0 | 24
39043.5417 | 1 | 0 | 24
39043.5422 | 1 | 0 | 24
39043.5427 | 1 | 0 | 24
39043.5431 | 645 | 0 | 24
39043.5436 | 1941 | 0 | 24
39043.5441 | 2132 | 0 | 24
39043.5446 | 2332 | 0 | 24
39043.5451 | 2436 | 0 | 24
39043.5456 | 2531 | 0 | 24
39043.5461 | 2367 | 0 | 24
39043.5465 | 2410 | 0 | 24
39043.547 | 2598 | 0 | 24
39043.5475 | 2476 | 0 | 24
39043.548 | 2190 | 0 | 24
39043.5485 | 2278 | 0 | 24
39043.549 | 2590 | 0 | 24
39043.5495 | 2261 | 0 | 24
39043.5499 | 2368 | 0 | 24
39043.5504 | 2559 | 0 | 24
39043.5509 | 2148 | 0 | 24
39043.5514 | 2407 | 0 | 24
39043.5519 | 2635 | 0 | 24
39043.5524 | 2068 | 0 | 24
39043.5529 | 2482 | 0 | 24
39043.5533 | 2289 | 0 | 24
39043.5538 | 2282 | 0 | 24
39043.5543 | 2047 | 0 | 24
39043.5548 | 2502 | 0 | 24
39043.5553 | 2071 | 0 | 24
39043.5558 | 2152 | 0 | 24
39043.5563 | 1859 | 0 | 24
39043.5567 | 694 | 0 | 24
39043.5572 | 1775 | 0 | 24
24
39043.5393 | 1 | 0 | 25
39043.5397 | 1 | 0 | 25
39043.5402 | 1 | 0 | 25
39043.5407 | 1 | 0 | 25
39043.5412 | 1 | 0 | 25
39043.5417 | 1 | 0 | 25
39043.5422 | 1 | 0 | 25
39043.5427 | 1 | 0 | 25
39043.5431 | 1 | 0 | 25
39043.5436 | 1 | 0 | 25
39043.5441 | 106 | 0 | 25
39043.5446 | 15 | 0 | 25
39043.5451 | 1720 | 0 | 25
39043.5456 | 2255 | 0 | 25
39043.5461 | 1997 | 0 | 25
39043.5466 | 2147 | 0 | 25
39043.547 | 2518 | 0 | 25
39043.5475 | 2185 | 0 | 25
39043.548 | 2338 | 0 | 25
39043.5485 | 1889 | 0 | 25
39043.549 | 1803 | 0 | 25
39043.5495 | 1840 | 0 | 25
39043.55 | 2569 | 0 | 25
39043.5504 | 2459 | 0 | 25
39043.5509 | 2490 | 0 | 25
39043.5514 | 2442 | 0 | 25
39043.5519 | 2055 | 0 | 25
39043.5524 | 2559 | 0 | 25
39043.5529 | 2157 | 0 | 25
39043.5534 | 2323 | 0 | 25
39043.5538 | 2170 | 0 | 25
39043.5543 | 2421 | 0 | 25
39043.5548 | 2174 | 0 | 25
39043.5553 | 2195 | 0 | 25
39043.5558 | 1785 | 0 | 25
39043.5563 | 1971 | 0 | 25
39043.5568 | 1478 | 0 | 25
39043.5572 | 1272 | 0 | 25
25
39043.5393 | 1 | 0 | 26
39043.5398 | 1 | 0 | 26
39043.5403 | 1 | 0 | 26
39043.5407 | 1 | 0 | 26
39043.5412 | 1 | 0 | 26
39043.5417 | 1 | 0 | 26
39043.5422 | 1 | 0 | 26
39043.5427 | 1 | 0 | 26
39043.5437 | 2266 | 0 | 26
39043.5441 | 2478 | 0 | 26
39043.5446 | 2213 | 0 | 26
39043.5451 | 2342 | 0 | 26
39043.5456 | 2382 | 0 | 26
39043.5461 | 2480 | 0 | 26
39043.5466 | 2653 | 0 | 26
39043.5471 | 2654 | 0 | 26
39043.5475 | 2066 | 0 | 26
39043.548 | 2282 | 0 | 26
39043.5485 | 2374 | 0 | 26
39043.549 | 2163 | 0 | 26
39043.5495 | 2074 | 0 | 26
39043.55 | 2367 | 0 | 26
39043.5505 | 2257 | 0 | 26
39043.5509 | 2537 | 0 | 26
39043.5514 | 2068 | 0 | 26
39043.5519 | 2345 | 0 | 26
39043.5524 | 2143 | 0 | 26
39043.5529 | 2398 | 0 | 26
39043.5534 | 2650 | 0 | 26
39043.5539 | 2225 | 0 | 26
39043.5543 | 2432 | 0 | 26
39043.5548 | 2454 | 0 | 26
39043.5553 | 2182 | 0 | 26
39043.5558 | 2060 | 0 | 26
39043.5563 | 1888 | 0 | 26
39043.5568 | 659 | 0 | 26
39043.5573 | 1221 | 0 | 26
26
39043.5393 | 1 | 0 | 27
39043.5398 | 1 | 0 | 27
39043.5403 | 1 | 0 | 27
39043.5408 | 1 | 0 | 27
39043.5412 | 1 | 0 | 27
39043.5417 | 1 | 0 | 27
39043.5422 | 1 | 0 | 27
39043.5427 | 1 | 0 | 27
39043.5432 | 1 | 0 | 27
39043.5437 | 1 | 0 | 27
39043.5442 | 2 | 0 | 27
39043.5446 | 5 | 0 | 27
39043.5451 | 1653 | 0 | 27
39043.5456 | 1840 | 0 | 27
39043.5461 | 1804 | 0 | 27
39043.5466 | 2460 | 0 | 27
39043.5471 | 2263 | 0 | 27
39043.5476 | 2270 | 0 | 27
39043.548 | 2255 | 0 | 27
39043.5485 | 1918 | 0 | 27
39043.549 | 1766 | 0 | 27
39043.5495 | 1731 | 0 | 27
39043.55 | 2156 | 0 | 27
39043.5505 | 2085 | 0 | 27
39043.551 | 2204 | 0 | 27
39043.5514 | 2257 | 0 | 27
39043.5519 | 2447 | 0 | 27
39043.5524 | 2580 | 0 | 27
39043.5529 | 2531 | 0 | 27
39043.5534 | 2077 | 0 | 27
39043.5539 | 2537 | 0 | 27
39043.5544 | 2365 | 0 | 27
39043.5548 | 2489 | 0 | 27
39043.5553 | 2146 | 0 | 27
39043.5558 | 1639 | 0 | 27
39043.5563 | 1969 | 0 | 27
39043.5568 | 1293 | 0 | 27
39043.5573 | 1462 | 0 | 27
27
39043.5393 | 1 | 0 | 28
39043.5398 | 1 | 0 | 28
39043.5403 | 1 | 0 | 28
39043.5408 | 1 | 0 | 28
39043.5413 | 1 | 0 | 28
39043.5417 | 1 | 0 | 28
39043.5422 | 1 | 0 | 28
39043.5427 | 1 | 0 | 28
39043.5432 | 1412 | 0 | 28
39043.5437 | 2150 | 0 | 28
39043.5442 | 2225 | 0 | 28
39043.5447 | 2092 | 0 | 28
39043.5451 | 2328 | 0 | 28
39043.5456 | 2116 | 0 | 28
39043.5461 | 2514 | 0 | 28
39043.5466 | 2096 | 0 | 28
39043.5471 | 2185 | 0 | 28
39043.5476 | 2524 | 0 | 28
39043.5481 | 2617 | 0 | 28
39043.5485 | 2610 | 0 | 28
39043.549 | 2559 | 0 | 28
39043.5495 | 2477 | 0 | 28
39043.55 | 2476 | 0 | 28
39043.5505 | 2636 | 0 | 28
39043.551 | 2436 | 0 | 28
39043.5515 | 2067 | 0 | 28
39043.5519 | 2063 | 0 | 28
39043.5524 | 2408 | 0 | 28
39043.5529 | 2287 | 0 | 28
39043.5534 | 2135 | 0 | 28
39043.5539 | 2159 | 0 | 28
39043.5544 | 2165 | 0 | 28
39043.5549 | 2092 | 0 | 28
39043.5553 | 2156 | 0 | 28
39043.5558 | 2303 | 0 | 28
39043.5563 | 1683 | 0 | 28
39043.5568 | 829 | 0 | 28
39043.5573 | 503 | 0 | 28
28
39043.5393 | 1 | 0 | 29
39043.5398 | 1 | 0 | 29
39043.5403 | 1 | 0 | 29
39043.5408 | 1 | 0 | 29
39043.5413 | 1 | 0 | 29
39043.5418 | 1 | 0 | 29
39043.5422 | 1 | 0 | 29
39043.5427 | 474 | 0 | 29
39043.5432 | 1414 | 662 | 29
39043.5437 | 1890 | 39 | 29
39043.5442 | 2615 | 0 | 29
39043.5447 | 2481 | 0 | 29
39043.5452 | 2528 | 0 | 29
39043.5456 | 2640 | 0 | 29
39043.5461 | 2305 | 0 | 29
39043.5466 | 2107 | 0 | 29
39043.5471 | 2148 | 0 | 29
39043.5476 | 2111 | 0 | 29
39043.5481 | 2162 | 0 | 29
39043.5486 | 2250 | 0 | 29
39043.5491 | 2384 | 0 | 29
39043.5495 | 2587 | 0 | 29
39043.55 | 2503 | 0 | 29
39043.5505 | 2599 | 0 | 29
39043.551 | 2630 | 0 | 29
39043.5515 | 2642 | 0 | 29
39043.552 | 2647 | 0 | 29
39043.5525 | 2384 | 0 | 29
39043.5529 | 2478 | 0 | 29
39043.5534 | 2278 | 0 | 29
39043.5539 | 2072 | 0 | 29
39043.5544 | 2568 | 0 | 29
39043.5549 | 2380 | 0 | 29
39043.5554 | 2053 | 0 | 29
39043.5559 | 2554 | 0 | 29
39043.5563 | 1426 | 634 | 29
39043.5568 | 1487 | 873 | 29
39043.5573 | 1167 | 1031 | 29
29
39043.5393 | 2 | 0 | 30
39043.5398 | 1 | 0 | 30
39043.5403 | 1 | 0 | 30
39043.5408 | 1 | 0 | 30
39043.5413 | 1 | 0 | 30
39043.5418 | 1 | 0 | 30
39043.5423 | 1 | 0 | 30
39043.5427 | 1 | 0 | 30
39043.5432 | 1273 | 511 | 30
39043.5437 | 1927 | 118 | 30
39043.5442 | 2176 | 0 | 30
39043.5447 | 2077 | 0 | 30
39043.5452 | 2226 | 0 | 30
39043.5457 | 2139 | 0 | 30
39043.5461 | 2334 | 0 | 30
39043.5466 | 2430 | 0 | 30
39043.5471 | 2586 | 0 | 30
39043.5476 | 2076 | 0 | 30
39043.5481 | 2302 | 0 | 30
39043.5486 | 2159 | 0 | 30
39043.5491 | 2515 | 0 | 30
39043.5495 | 2489 | 0 | 30
39043.55 | 2359 | 0 | 30
39043.5505 | 2643 | 0 | 30
39043.551 | 2533 | 0 | 30
39043.5515 | 2565 | 0 | 30
39043.552 | 2597 | 0 | 30
39043.5525 | 2062 | 0 | 30
39043.553 | 2384 | 0 | 30
39043.5534 | 2516 | 0 | 30
39043.5539 | 2239 | 0 | 30
39043.5544 | 2358 | 0 | 30
39043.5549 | 2342 | 0 | 30
39043.5554 | 2355 | 0 | 30
39043.5559 | 2246 | 0 | 30
39043.5564 | 1412 | 601 | 30
39043.5568 | 1532 | 834 | 30
39043.5573 | 1298 | 1002 | 30
30

## Temperatures
DAQ Time | Burner Time | Bundle center | Air above bundle | Air below bundle | Intra-bundle | TRAY A
0 | -190 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8
1 | -189 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8
2 | -188 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8
3 | -187 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8
4 | -186 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8
5 | -185 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8
6 | -184 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8
7 | -183 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8
8 | -182 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8
9 | -181 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8
10 | -180 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8
11 | -179 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8
12 | -178 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8
13 | -177 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8
14 | -176 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8
15 | -175 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8
16 | -174 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8
17 | -173 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8
18 | -172 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8
19 | -171 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8
20 | -170 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8
21 | -169 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8
22 | -168 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8
23 | -167 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8
24 | -166 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8
25 | -165 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8
26 | -164 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8
27 | -163 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8
28 | -162 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8
29 | -161 | 16.1 | 16.6 | 16.8 | 16.5 | 18.8
30 | -160 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8
31 | -159 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8
32 | -158 | 16.1 | 16.6 | 16.8 | 16.5 | 18.8
33 | -157 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8
34 | -156 | 16.1 | 16.6 | 16.8 | 16.5 | 18.8
35 | -155 | 16.1 | 16.6 | 16.8 | 16.5 | 18.8
36 | -154 | 16.1 | 16.6 | 16.8 | 16.5 | 18.8
37 | -153 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8
38 | -152 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8
39 | -151 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8
40 | -150 | 16.2 | 16.7 | 16.8 | 16.5 | 18.8
41 | -149 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8
42 | -148 | 16.1 | 16.6 | 16.8 | 16.5 | 18.8
43 | -147 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8
44 | -146 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8
45 | -145 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8
46 | -144 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8
47 | -143 | 16.2 | 16.7 | 16.8 | 16.5 | 18.8
48 | -142 | 16.2 | 16.7 | 16.8 | 16.5 | 18.8
49 | -141 | 16.2 | 16.7 | 16.8 | 16.5 | 18.8
50 | -140 | 16.2 | 16.7 | 16.8 | 16.5 | 18.8
51 | -139 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8
52 | -138 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8
53 | -137 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8
54 | -136 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8
55 | -135 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8
56 | -134 | 16.2 | 16.7 | 16.8 | 16.5 | 18.8
57 | -133 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8
58 | -132 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8
59 | -131 | 16.2 | 16.7 | 16.8 | 16.5 | 18.8
60 | -130 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8
61 | -129 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8
62 | -128 | 16.2 | 16.7 | 16.8 | 16.5 | 18.8
63 | -127 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8
64 | -126 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8
65 | -125 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8
66 | -124 | 16.2 | 16.7 | 16.8 | 16.5 | 18.8
67 | -123 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8
68 | -122 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8
69 | -121 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8
70 | -120 | 16.2 | 16.7 | 16.8 | 16.5 | 18.8
71 | -119 | 16.2 | 16.7 | 16.8 | 16.5 | 18.8
72 | -118 | 16.1 | 16.7 | 16.9 | 16.5 | 18.8
73 | -117 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8
74 | -116 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8
75 | -115 | 16.2 | 16.7 | 16.8 | 16.5 | 18.8
76 | -114 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8
77 | -113 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8
78 | -112 | 16.2 | 16.6 | 16.9 | 16.5 | 18.8
79 | -111 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8
80 | -110 | 16.2 | 16.6 | 16.9 | 16.5 | 18.8
81 | -109 | 16.2 | 16.6 | 16.9 | 16.5 | 18.8
82 | -108 | 16.2 | 16.6 | 16.9 | 16.5 | 18.8
83 | -107 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8
84 | -106 | 16.2 | 16.6 | 16.9 | 16.5 | 18.8
85 | -105 | 16.2 | 16.6 | 16.9 | 16.5 | 18.8
86 | -104 | 16.2 | 16.6 | 16.9 | 16.5 | 18.8
87 | -103 | 16.2 | 16.6 | 16.9 | 16.5 | 18.8
88 | -102 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8
89 | -101 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8
90 | -100 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8
91 | -99 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8
92 | -98 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8
93 | -97 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8
94 | -96 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8
95 | -95 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8
96 | -94 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8
97 | -93 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8
98 | -92 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8
99 | -91 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8
100 | -90 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8
101 | -89 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8
102 | -88 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8
103 | -87 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8
104 | -86 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8
105 | -85 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8
106 | -84 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8
107 | -83 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8
108 | -82 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8
109 | -81 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8
110 | -80 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8
111 | -79 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8
112 | -78 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8
113 | -77 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8
114 | -76 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8
115 | -75 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8
116 | -74 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8
117 | -73 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8
118 | -72 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8
119 | -71 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8
120 | -70 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8
121 | -69 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8
122 | -68 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8
123 | -67 | 16.2 | 16.7 | 17 | 16.5 | 18.8
124 | -66 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8
125 | -65 | 16.2 | 16.7 | 16.9 | 16.5 | 18.9
126 | -64 | 16.2 | 16.7 | 16.9 | 16.5 | 18.9
127 | -63 | 16.2 | 16.7 | 16.9 | 16.5 | 18.9
128 | -62 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8
129 | -61 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8
130 | -60 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8
131 | -59 | 16.2 | 16.7 | 16.9 | 16.5 | 18.9
132 | -58 | 16.2 | 16.7 | 16.9 | 16.5 | 18.9
133 | -57 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8
134 | -56 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8
135 | -55 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8
136 | -54 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8
137 | -53 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8
138 | -52 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8
139 | -51 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8
140 | -50 | 16.2 | 16.7 | 17 | 16.5 | 18.8
141 | -49 | 16.2 | 16.7 | 17 | 16.5 | 18.9
142 | -48 | 16.2 | 16.7 | 17 | 16.5 | 18.9
143 | -47 | 16.2 | 16.7 | 17 | 16.5 | 18.9
144 | -46 | 16.2 | 16.7 | 17 | 16.5 | 18.9
145 | -45 | 16.2 | 16.7 | 17 | 16.5 | 18.9
146 | -44 | 16.2 | 16.7 | 17 | 16.5 | 18.9
147 | -43 | 16.2 | 16.7 | 17 | 16.5 | 18.9
148 | -42 | 16.2 | 16.7 | 17 | 16.5 | 18.9
149 | -41 | 16.2 | 16.7 | 17 | 16.5 | 18.9
150 | -40 | 16.2 | 16.7 | 17 | 16.5 | 18.9
151 | -39 | 16.2 | 16.7 | 17 | 16.5 | 18.9
152 | -38 | 16.2 | 16.7 | 17 | 16.5 | 18.9
153 | -37 | 16.2 | 16.7 | 17 | 16.5 | 18.9
154 | -36 | 16.2 | 16.7 | 17 | 16.5 | 18.9
155 | -35 | 16.2 | 16.7 | 17 | 16.5 | 18.9
156 | -34 | 16.2 | 16.7 | 17 | 16.5 | 18.9
157 | -33 | 16.2 | 16.7 | 17 | 16.5 | 18.9
158 | -32 | 16.2 | 16.8 | 17 | 16.5 | 18.9
159 | -31 | 16.2 | 16.8 | 17 | 16.5 | 18.9
160 | -30 | 16.2 | 16.7 | 17 | 16.5 | 18.9
161 | -29 | 16.2 | 16.8 | 17 | 16.5 | 18.9
162 | -28 | 16.2 | 16.8 | 17 | 16.5 | 18.9
163 | -27 | 16.2 | 16.8 | 17 | 16.5 | 18.9
164 | -26 | 16.2 | 16.8 | 17 | 16.5 | 18.9
165 | -25 | 16.2 | 16.8 | 17 | 16.5 | 18.9
166 | -24 | 16.2 | 16.8 | 17 | 16.5 | 18.9
167 | -23 | 16.2 | 16.7 | 17 | 16.5 | 18.9
168 | -22 | 16.2 | 16.8 | 17 | 16.5 | 18.9
169 | -21 | 16.2 | 16.7 | 17 | 16.5 | 18.9
170 | -20 | 16.2 | 16.7 | 17 | 16.5 | 18.9
171 | -19 | 16.2 | 16.7 | 17 | 16.5 | 18.9
172 | -18 | 16.2 | 16.7 | 17 | 16.5 | 18.9
173 | -17 | 16.2 | 16.7 | 17.1 | 16.5 | 18.9
174 | -16 | 16.2 | 16.7 | 17.1 | 16.5 | 18.9
175 | -15 | 16.2 | 16.7 | 17.1 | 16.5 | 18.9
176 | -14 | 16.2 | 16.7 | 17 | 16.5 | 18.9
177 | -13 | 16.2 | 16.7 | 17 | 16.5 | 18.9
178 | -12 | 16.2 | 16.7 | 17 | 16.5 | 18.9
179 | -11 | 16.2 | 16.7 | 17 | 16.5 | 18.9
180 | -10 | 16.2 | 16.7 | 17 | 16.5 | 18.9
181 | -9 | 16.2 | 16.7 | 17 | 16.5 | 18.9
182 | -8 | 16.2 | 16.7 | 17 | 16.5 | 18.9
183 | -7 | 16.2 | 16.7 | 17 | 16.5 | 18.9
184 | -6 | 16.2 | 16.8 | 17 | 16.5 | 18.9
185 | -5 | 16.2 | 16.7 | 17 | 16.5 | 18.9
186 | -4 | 16.2 | 16.7 | 17 | 16.5 | 18.9
187 | -3 | 16.2 | 16.7 | 17 | 16.5 | 18.9
188 | -2 | 16.2 | 16.7 | 17 | 16.5 | 18.9
189 | -1 | 16.2 | 16.7 | 17 | 16.5 | 18.9
190 | 0 | 16.2 | 16.8 | 17.1 | 16.5 | 18.9
191 | 1 | 16.2 | 16.7 | 17.1 | 16.5 | 18.9
192 | 2 | 16.2 | 16.8 | 17.1 | 16.5 | 18.9
193 | 3 | 16.2 | 16.8 | 17.1 | 16.5 | 18.9
194 | 4 | 16.2 | 17.9 | 24.3 | 17.5 | 20.1
195 | 5 | 16.2 | 36.2 | 77.4 | 24.6 | 29.6
196 | 6 | 16.2 | 68.9 | 129.7 | 31.6 | 47.4
197 | 7 | 16.3 | 118.4 | 210.1 | 39.2 | 72.9
198 | 8 | 16.4 | 182.8 | 293.2 | 46.9 | 98.6
199 | 9 | 16.5 | 247 | 355.5 | 56.6 | 129.1
200 | 10 | 16.8 | 321.5 | 426.4 | 69.2 | 163.9
201 | 11 | 17.1 | 387.4 | 483.6 | 78.7 | 187.4
202 | 12 | 17.5 | 454.4 | 532.5 | 92.3 | 216.4
203 | 13 | 18 | 512.4 | 579.7 | 106.3 | 245.7
204 | 14 | 18.6 | 563 | 620.3 | 116.1 | 279.3
205 | 15 | 19.4 | 608.6 | 662.1 | 126.5 | 306
206 | 16 | 20.3 | 653.2 | 699.9 | 139.4 | 328.7
207 | 17 | 21.3 | 698.1 | 732.3 | 150.7 | 352.3
208 | 18 | 22.3 | 737 | 751.2 | 165.6 | 373.8
209 | 19 | 23.4 | 761.2 | 770.3 | 180.4 | 392.6
210 | 20 | 24.6 | 786.4 | 782.6 | 193.3 | 406.2
211 | 21 | 25.8 | 806.7 | 786.2 | 199.3 | 419.6
212 | 22 | 27 | 824.7 | 798.7 | 209.9 | 431.3
213 | 23 | 28.2 | 837.9 | 799.7 | 217.3 | 444.7
214 | 24 | 29.5 | 835.2 | 787.8 | 220.4 | 453
215 | 25 | 30.9 | 836.4 | 787.4 | 225.3 | 461.7
216 | 26 | 32.3 | 851.5 | 790.8 | 236.7 | 467.6
217 | 27 | 33.8 | 862 | 791.8 | 249.4 | 484.8
218 | 28 | 35.2 | 864.4 | 791 | 251.3 | 493.4
219 | 29 | 36.7 | 858.5 | 786 | 252.6 | 507.8
220 | 30 | 38.3 | 858.4 | 793.1 | 258.2 | 516.1
221 | 31 | 40 | 871 | 808.9 | 270.6 | 516.4
222 | 32 | 41.8 | 871.6 | 810.2 | 273.2 | 513.3
223 | 33 | 43.6 | 858.2 | 795.8 | 276.3 | 508.6
224 | 34 | 45.4 | 836.4 | 782.3 | 277.1 | 507.3
225 | 35 | 47.4 | 834.1 | 771 | 282.4 | 503.2
226 | 36 | 49.4 | 822.2 | 768.9 | 284.9 | 500.2
227 | 37 | 51.4 | 803 | 760.4 | 287.7 | 500.7
228 | 38 | 53.4 | 776.1 | 745 | 287.2 | 500.6
229 | 39 | 55.4 | 764.9 | 742.4 | 292.3 | 498.5
230 | 40 | 57.4 | 755.9 | 739 | 297.4 | 494.3
231 | 41 | 59.3 | 738.8 | 725.2 | 303.9 | 496.1
232 | 42 | 61.2 | 736.7 | 730.7 | 310.7 | 500.3
233 | 43 | 63.1 | 734.8 | 732 | 310.6 | 501.1
234 | 44 | 65 | 741.8 | 720.8 | 318 | 509.2
235 | 45 | 66.9 | 750.9 | 720.5 | 323.9 | 527.2
236 | 46 | 68.7 | 768.1 | 730.9 | 332.7 | 539.3
237 | 47 | 70.5 | 788.5 | 745 | 336.6 | 549.9
238 | 48 | 72.2 | 809.8 | 758.5 | 344.2 | 558.2
239 | 49 | 73.9 | 820.9 | 754.8 | 350.5 | 564.2
240 | 50 | 75.5 | 828 | 743.6 | 351.9 | 576.2
241 | 51 | 77.1 | 821.8 | 735 | 348.8 | 574.4
242 | 52 | 78.8 | 814.9 | 731.5 | 346.1 | 574.5
243 | 53 | 80.4 | 801.9 | 727.7 | 341.3 | 576.6
244 | 54 | 82.1 | 812.5 | 751.7 | 343.5 | 592.1
245 | 55 | 83.8 | 828.4 | 760.6 | 346.8 | 608.9
246 | 56 | 85.4 | 837.8 | 742.1 | 345.5 | 618.2
247 | 57 | 87.2 | 839.3 | 732.1 | 344.5 | 628.4
248 | 58 | 88.9 | 848.1 | 752 | 345.5 | 632.8
249 | 59 | 90.6 | 855.9 | 771.3 | 345.9 | 631
250 | 60 | 92.2 | 862.7 | 771 | 343.9 | 630.4
251 | 61 | 93.8 | 868.5 | 774.3 | 342.1 | 635.1
252 | 62 | 95.3 | 873.5 | 780.9 | 341 | 637
253 | 63 | 96.9 | 879.6 | 775.5 | 338.6 | 637.6
254 | 64 | 98.4 | 879.6 | 777.2 | 335.7 | 639.9
255 | 65 | 99.8 | 884.2 | 779.3 | 333.1 | 641.5
256 | 66 | 101.3 | 890.1 | 781.7 | 330.9 | 647.9
257 | 67 | 102.8 | 895.4 | 795.4 | 329.4 | 654.3
258 | 68 | 104.5 | 899.4 | 804 | 328.6 | 652.3
259 | 69 | 106.1 | 899 | 813.4 | 328.2 | 650.7
260 | 70 | 107.8 | 905.8 | 822.1 | 327.4 | 648.5
261 | 71 | 109.5 | 907.9 | 827.2 | 326.3 | 641.2
262 | 72 | 111.5 | 911.4 | 822.3 | 324.8 | 639
263 | 73 | 113.6 | 912.7 | 806.7 | 323.2 | 643.3
264 | 74 | 116 | 914.2 | 804.6 | 321.4 | 644.2
265 | 75 | 118.8 | 921.3 | 815.1 | 319.8 | 644.2
266 | 76 | 121.9 | 923.7 | 822.2 | 318.6 | 640.9
267 | 77 | 125.8 | 918.7 | 828.1 | 318.4 | 641.5
268 | 78 | 127.9 | 920.7 | 820.3 | 318.1 | 638.9
269 | 79 | 129.3 | 923.1 | 825 | 318 | 633.5
270 | 80 | 131.3 | 908.6 | 827.1 | 318.3 | 632.5
271 | 81 | 132.9 | 897.9 | 835.3 | 319.2 | 637.7
272 | 82 | 134.7 | 901.8 | 840.3 | 320.6 | 646.4
273 | 83 | 136.6 | 898.7 | 844.2 | 322.3 | 648.2
274 | 84 | 138.5 | 882.6 | 835.3 | 323.2 | 642.2
275 | 85 | 140.2 | 864 | 820.9 | 323.4 | 635.3
276 | 86 | 141.7 | 860.6 | 832.1 | 324.2 | 636.3
277 | 87 | 143.7 | 871 | 848.2 | 326.1 | 641.1
278 | 88 | 146.4 | 875.6 | 845.1 | 328.2 | 644.2
279 | 89 | 148.6 | 870.6 | 834.9 | 329.6 | 641
280 | 90 | 150.9 | 852.5 | 825.7 | 330.4 | 630.9
281 | 91 | 154.5 | 840.1 | 814.1 | 331.1 | 623.1
282 | 92 | 157.9 | 838.7 | 816.7 | 331.8 | 615
283 | 93 | 160.5 | 842.7 | 820.6 | 333.5 | 621.8
284 | 94 | 162.8 | 850.6 | 818.5 | 336.4 | 635.4
285 | 95 | 165 | 855.1 | 802.1 | 339 | 645.7
286 | 96 | 167.1 | 856.2 | 785 | 341.1 | 656.2
287 | 97 | 169.7 | 858.6 | 798.8 | 343.1 | 664.7
288 | 98 | 172.8 | 868.7 | 789.6 | 345.4 | 677.9
289 | 99 | 175.3 | 870.7 | 796.9 | 347.4 | 692.6
290 | 100 | 177.5 | 877.1 | 780 | 349.5 | 707
291 | 101 | 179.5 | 879.1 | 786.5 | 352.1 | 716.1
292 | 102 | 181.9 | 886.5 | 800.1 | 355.7 | 718
293 | 103 | 184.1 | 886.7 | 806 | 359.6 | 720.1
294 | 104 | 186.2 | 887.3 | 803.1 | 363.6 | 726.6
295 | 105 | 187.9 | 882.2 | 808.2 | 368.3 | 729.5
296 | 106 | 189.2 | 877.5 | 820.1 | 373.4 | 725.2
297 | 107 | 190.4 | 877.6 | 828.4 | 377.7 | 722.6
298 | 108 | 191.3 | 875.5 | 819.9 | 381.4 | 726.5
299 | 109 | 192.1 | 879.2 | 814 | 384.7 | 736.8
300 | 110 | 193.1 | 884.4 | 803.8 | 388 | 745.6
301 | 111 | 194 | 881 | 801.7 | 390.9 | 747.1
302 | 112 | 195 | 879.7 | 786.9 | 394 | 748.6
303 | 113 | 195.9 | 881.6 | 795.3 | 397.7 | 753.5
304 | 114 | 196.9 | 883.6 | 804.3 | 401.4 | 753
305 | 115 | 198 | 884.4 | 805.4 | 405.6 | 751.2
306 | 116 | 199 | 886 | 818.1 | 409.7 | 749.6
307 | 117 | 200.2 | 891.8 | 830.5 | 413.6 | 742.1
308 | 118 | 201.2 | 889.3 | 831.8 | 417.6 | 732.5
309 | 119 | 202.2 | 885.5 | 824.1 | 421.3 | 730.7
310 | 120 | 203.3 | 886.8 | 810.9 | 424.8 | 733
311 | 121 | 204.2 | 885.9 | 802.3 | 427.7 | 739.1
312 | 122 | 205.2 | 885.4 | 798.7 | 430.4 | 746.3
313 | 123 | 206.1 | 885.7 | 783.9 | 433.4 | 753.8
314 | 124 | 207.1 | 891.6 | 781.6 | 437 | 758.2
315 | 125 | 208 | 891.3 | 789.3 | 440.6 | 758.9
316 | 126 | 208.8 | 887.6 | 803.1 | 444 | 757.3
317 | 127 | 209.7 | 889.3 | 824.2 | 448.3 | 751.3
318 | 128 | 210.7 | 880.8 | 837 | 453.3 | 745.5
319 | 129 | 211.7 | 878.4 | 849.7 | 458.9 | 741.3
320 | 130 | 212.8 | 882.2 | 854.5 | 465.6 | 737.3
321 | 131 | 213.9 | 882.3 | 851.5 | 472.2 | 727
322 | 132 | 215 | 880 | 854.2 | 477.7 | 717.9
323 | 133 | 216.2 | 884.7 | 851.6 | 483.4 | 716.5
324 | 134 | 217.6 | 884.4 | 842.6 | 489.8 | 712.6
325 | 135 | 218.8 | 885.1 | 848.1 | 495.9 | 709.3
326 | 136 | 219.9 | 883.3 | 847 | 501.9 | 714.9
327 | 137 | 220.9 | 879.8 | 846.8 | 506.8 | 719.2
328 | 138 | 221.8 | 868.2 | 831.7 | 511.6 | 715.6
329 | 139 | 222.9 | 850.7 | 815.4 | 515.8 | 705.6
330 | 140 | 224.3 | 835.5 | 790.9 | 518.6 | 699.7
331 | 141 | 225.6 | 840.3 | 801.3 | 522 | 703.4
332 | 142 | 227.1 | 838.1 | 799.3 | 525.3 | 705.1
333 | 143 | 228.4 | 835.5 | 801.6 | 528.5 | 700.8
334 | 144 | 229.6 | 838.4 | 817.6 | 533.3 | 705.3
335 | 145 | 231 | 840.5 | 808.4 | 537.7 | 713.8
336 | 146 | 232.7 | 842.7 | 816.8 | 542.4 | 715.5
337 | 147 | 234.4 | 844.9 | 815 | 547.5 | 717.9
338 | 148 | 236 | 854.3 | 824.2 | 553 | 723.5
339 | 149 | 237.5 | 862.6 | 826.5 | 558 | 726.3
340 | 150 | 239.4 | 867.3 | 833.1 | 561.8 | 729.7
341 | 151 | 241.3 | 869 | 836.6 | 565.1 | 737.8
342 | 152 | 243 | 869.9 | 822.6 | 568 | 738.9
343 | 153 | 244.7 | 873.8 | 823 | 570.9 | 739.9
344 | 154 | 246.3 | 872 | 836.3 | 574 | 743.8
345 | 155 | 247.8 | 868.9 | 839 | 577.3 | 747
346 | 156 | 249.4 | 865.3 | 840.6 | 580.1 | 748.9
347 | 157 | 251.1 | 863.7 | 841.4 | 581.8 | 751.8
348 | 158 | 252.9 | 866.3 | 827.8 | 584.6 | 759.8
349 | 159 | 254.6 | 864.2 | 828.9 | 587.2 | 762.2
350 | 160 | 256.3 | 860.3 | 824.5 | 589.3 | 768.4
351 | 161 | 258.1 | 856.1 | 828.5 | 591.4 | 771.6
352 | 162 | 259.7 | 855.4 | 820.9 | 593.7 | 777
353 | 163 | 261.1 | 850.6 | 826.8 | 595.4 | 778.5
354 | 164 | 262.8 | 845.5 | 838.8 | 597.2 | 773.1
355 | 165 | 264.5 | 846.3 | 839.1 | 598.2 | 767.9
356 | 166 | 266.2 | 844.6 | 838.2 | 598.2 | 761.5
357 | 167 | 267.9 | 841.5 | 844.7 | 598.6 | 758
358 | 168 | 269.8 | 839.4 | 845 | 599.5 | 755.3
359 | 169 | 271.8 | 838.4 | 834.7 | 600.3 | 749.3
360 | 170 | 273.5 | 834.3 | 839 | 600.8 | 741
361 | 171 | 275.3 | 827.2 | 845.4 | 600.9 | 737.6
362 | 172 | 277.2 | 821.6 | 857.4 | 600.4 | 738.3
363 | 173 | 279 | 815.2 | 863 | 598.6 | 742.4
364 | 174 | 280.9 | 808.8 | 871.5 | 597 | 750.9
365 | 175 | 282.6 | 811.9 | 864.3 | 595.6 | 747.8
366 | 176 | 284.4 | 813 | 859.2 | 594.2 | 747.8
367 | 177 | 286.2 | 813 | 856.9 | 593.3 | 744
368 | 178 | 288.1 | 813.1 | 851.9 | 593 | 747.6
369 | 179 | 290 | 806.2 | 859.8 | 591.7 | 744.3
370 | 180 | 291.9 | 807.9 | 851.9 | 591.6 | 745
371 | 181 | 293.8 | 809.6 | 856.1 | 591.8 | 739.2
372 | 182 | 295.7 | 807 | 858.8 | 591.2 | 740.9
373 | 183 | 297.6 | 803.9 | 864.2 | 591.7 | 747.3
374 | 184 | 299.6 | 800.4 | 864.8 | 591.4 | 750.6
375 | 185 | 301.7 | 794 | 873 | 590.8 | 752.9
376 | 186 | 303.8 | 795.3 | 867.2 | 591.5 | 752.9
377 | 187 | 305.7 | 799.6 | 859.8 | 592 | 761.7
378 | 188 | 307.5 | 803.6 | 834.7 | 592.5 | 767.8
379 | 189 | 309.4 | 807.2 | 817.6 | 591.8 | 769.3
380 | 190 | 311.4 | 809.8 | 794.7 | 590 | 767.3
381 | 191 | 313.4 | 819.8 | 766.7 | 587.6 | 768
382 | 192 | 315.4 | 822 | 767.5 | 585.7 | 774.1
383 | 193 | 317.4 | 830.6 | 765.2 | 584.4 | 776.2
384 | 194 | 319.2 | 835.7 | 762.6 | 583.4 | 782.6
385 | 195 | 321.1 | 834.7 | 765 | 582.8 | 782
386 | 196 | 322.8 | 839.1 | 766.4 | 582.8 | 781.3
387 | 197 | 324.5 | 849.4 | 774.6 | 583.3 | 782
388 | 198 | 326 | 853.5 | 767.4 | 583.7 | 782.6
389 | 199 | 327.3 | 850 | 766.5 | 584.7 | 783.8
390 | 200 | 328.6 | 862.9 | 751.3 | 586.1 | 789.2
391 | 201 | 330 | 863 | 758.6 | 587.5 | 794.6
392 | 202 | 331.3 | 855.2 | 757.9 | 588 | 795.8
393 | 203 | 332.5 | 874.5 | 747.8 | 588.1 | 799.7
394 | 204 | 334 | 884.6 | 762.6 | 587.3 | 802.6
395 | 205 | 335.5 | 881.2 | 772.5 | 587.1 | 797.8
396 | 206 | 337 | 874.3 | 777.7 | 586.7 | 794.1
397 | 207 | 338.4 | 861.3 | 782 | 585.9 | 789.4
398 | 208 | 339.9 | 857.5 | 783.8 | 584.4 | 786.4
399 | 209 | 341.4 | 842.8 | 790.1 | 583.4 | 787.9
400 | 210 | 343 | 838.6 | 773 | 582.4 | 786
401 | 211 | 344.6 | 833.8 | 780.4 | 581.6 | 782.9
402 | 212 | 346.4 | 824.6 | 791.8 | 581.7 | 787.1
403 | 213 | 348.4 | 811.5 | 802.5 | 581.3 | 792.2
404 | 214 | 350.7 | 592.9 | 803.2 | 580.8 | 791.1
405 | 215 | 353.3 | 806.7 | 808 | 580.2 | 791.7
406 | 216 | 356.1 | 756.4 | 804 | 580.1 | 793.3
407 | 217 | 359 | 380.3 | 812.1 | 581 | 794.2
408 | 218 | 361.5 | 799.7 | 822.5 | 582 | 795.1
409 | 219 | 363.9 | 796.7 | 826.9 | 583.3 | 796.5
410 | 220 | 366.3 | 797 | 824.8 | 584.5 | 794.8
411 | 221 | 368.9 | 795.5 | 832.2 | 586.1 | 798.5
412 | 222 | 371.4 | 792.3 | 828.4 | 587.1 | 800.2
413 | 223 | 373.9 | 790.4 | 818.4 | 588.7 | 801.8
414 | 224 | 376.5 | 792.2 | 815.2 | 590.2 | 801.4
415 | 225 | 379.5 | 791.6 | 809.4 | 592.4 | 802.2
416 | 226 | 382.8 | 785.6 | 811.3 | 593.7 | 803.8
417 | 227 | 386.3 | 784.1 | 796.4 | 595.7 | 808.8
418 | 228 | 389.6 | 533.7 | 772.2 | 598 | 810.8
419 | 229 | 392.8 | 787.2 | 757.8 | 600.7 | 813.1
420 | 230 | 396.1 | 800.1 | 746.2 | 603.5 | 813.2
421 | 231 | 399.7 | 796.4 | 739.8 | 606.1 | 814.2
422 | 232 | 403.3 | 795.2 | 742.7 | 609.1 | 817
423 | 233 | 406.7 | 802.9 | 731.2 | 612 | 820.4
424 | 234 | 410.4 | 803.1 | 730.3 | 614.8 | 816.7
425 | 235 | 414.3 | 802.3 | 747.6 | 617.7 | 820
426 | 236 | 417.7 | 798.8 | 745.7 | 619.4 | 823
427 | 237 | 420.7 | 797.9 | 738.9 | 621.1 | 824.6
428 | 238 | 424.8 | 803 | 744.1 | 623.5 | 823.2
429 | 239 | 429.5 | 793.5 | 750.6 | 625 | 821.1
430 | 240 | 433.6 | 782.9 | 746.9 | 626.5 | 822.8
431 | 241 | 437.6 | 788.8 | 753.8 | 628.8 | 826
432 | 242 | 441.8 | 767.3 | 745.9 | 630.9 | 828.1
433 | 243 | 445.8 | 789.8 | 746.5 | 634.6 | 828.5
434 | 244 | 450.1 | 795.4 | 735.5 | 638.5 | 830.4
435 | 245 | 454.2 | 802.5 | 733.3 | 642.1 | 833
436 | 246 | 458.6 | 800.5 | 740.7 | 644.8 | 833.5
437 | 247 | 462.9 | 799.6 | 731.3 | 647.1 | 835
438 | 248 | 466.9 | 801.8 | 729.5 | 649.7 | 837.2
439 | 249 | 470.1 | 798.4 | 723.7 | 652.6 | 839.8
440 | 250 | 473.9 | 800.8 | 732.3 | 656.6 | 842.2
441 | 251 | 477.5 | 800.5 | 733.3 | 660.4 | 847.6
442 | 252 | 480.9 | 797.2 | 749.1 | 664.4 | 850.8
443 | 253 | 484.3 | 796.1 | 763.1 | 671.6 | 852
444 | 254 | 487.9 | 792.1 | 768.8 | 679 | 849.9
445 | 255 | 491.7 | 792 | 771.8 | 686.4 | 847.1
446 | 256 | 495.6 | 793 | 775.7 | 692.7 | 844.8
447 | 257 | 499.2 | 795.5 | 780.2 | 696.2 | 841
448 | 258 | 502.5 | 793.2 | 780.5 | 697.9 | 835.9
449 | 259 | 505.6 | 793.5 | 783.8 | 699.8 | 826.1
450 | 260 | 509 | 794.3 | 781.3 | 703.9 | 818.7
451 | 261 | 512.8 | 788 | 786 | 706.5 | 810.7
452 | 262 | 516.7 | 782.4 | 791.2 | 709.4 | 808.8
453 | 263 | 520.8 | 783.6 | 797.1 | 712.3 | 804.7
454 | 264 | 525.1 | 780.2 | 809.7 | 713.1 | 803.4
455 | 265 | 529.8 | 777 | 824.2 | 713.5 | 806.3
456 | 266 | 534.2 | 776.3 | 820.4 | 715.4 | 805.2
457 | 267 | 538.8 | 774 | 825.1 | 716.1 | 802.2
458 | 268 | 543.7 | 774.7 | 832.4 | 717.4 | 797.2
459 | 269 | 548.9 | 772.9 | 831.3 | 717.3 | 799.4
460 | 270 | 553.8 | 771 | 826.8 | 717.9 | 807.7
461 | 271 | 558.7 | 769 | 823.5 | 718.6 | 818.1
462 | 272 | 564.3 | 766.3 | 821.9 | 717.8 | 822.7
463 | 273 | 570 | 770.9 | 812.2 | 720.3 | 826.1
464 | 274 | 575.8 | 771.9 | 823.5 | 723.2 | 826
465 | 275 | 581.7 | 769.8 | 829.6 | 728.5 | 820.6
466 | 276 | 587.9 | 767.6 | 829.3 | 733.9 | 817.1
467 | 277 | 594.2 | 767.4 | 820 | 738 | 814.4
468 | 278 | 600.4 | 771 | 808.9 | 742.9 | 808.6
469 | 279 | 607.1 | 774.7 | 806.5 | 748.2 | 799.4
470 | 280 | 613.6 | 776.2 | 798 | 753 | 788.7
471 | 281 | 620.1 | 776.5 | 801.6 | 756.4 | 789.1
472 | 282 | 626.7 | 777 | 805.4 | 759.1 | 791.6
473 | 283 | 632.7 | 774 | 820 | 759.3 | 794.6
474 | 284 | 638.1 | 772.1 | 822.5 | 762.3 | 795.3
475 | 285 | 644.6 | 774.9 | 820 | 767.5 | 797.8
476 | 286 | 652.2 | 776.3 | 826.8 | 771.9 | 802.9
477 | 287 | 659.4 | 775.7 | 828.1 | 773.9 | 803.7
478 | 288 | 665.6 | 774.4 | 833.4 | 774.9 | 809.2
479 | 289 | 671.1 | 772.5 | 839.3 | 775.1 | 811.6
480 | 290 | 676.6 | 770.5 | 841.3 | 775.9 | 815.2
481 | 291 | 683.1 | 771.1 | 836.6 | 777.9 | 816.3
482 | 292 | 689.5 | 773.3 | 836.6 | 780.1 | 818.7
483 | 293 | 695.3 | 773 | 836.6 | 782.1 | 822.3
484 | 294 | 700.7 | 772.8 | 835 | 785 | 822.6
485 | 295 | 707.4 | 773.2 | 832.1 | 787.6 | 823.8
486 | 296 | 713.8 | 772.7 | 830.3 | 789.8 | 827.2
487 | 297 | 719.8 | 772.6 | 834.9 | 792.5 | 827.9
488 | 298 | 725.6 | 772.9 | 841.1 | 795.5 | 825.8
489 | 299 | 731.4 | 772.2 | 844.3 | 798.3 | 822
490 | 300 | 736.7 | 771.2 | 842.3 | 801 | 814.4
491 | 301 | 742.3 | 771.8 | 834.2 | 803.1 | 808.9
492 | 302 | 747.8 | 772.6 | 833.9 | 803.5 | 810.1
493 | 303 | 752.9 | 773.4 | 839.4 | 804.9 | 810.5
494 | 304 | 757.9 | 774.7 | 842.4 | 806.3 | 810.5
495 | 305 | 763 | 775.9 | 836.2 | 808.2 | 806.4
496 | 306 | 768.2 | 778.1 | 829.6 | 811 | 801.8
497 | 307 | 774.5 | 780 | 829.7 | 813.4 | 800.7
498 | 308 | 779.9 | 780.1 | 839.2 | 814.6 | 807.4
499 | 309 | 784.3 | 784.6 | 831.6 | 818 | 812.1
500 | 310 | 789.8 | 788.1 | 832.5 | 822.5 | 815.9
501 | 311 | 796 | 789.9 | 841.6 | 826.1 | 818.5
502 | 312 | 802.1 | 792.2 | 839.7 | 829.6 | 821.9
503 | 313 | 808 | 793.6 | 841.2 | 832.7 | 820.9
504 | 314 | 813.7 | 794.5 | 836.6 | 833.6 | 822.1
505 | 315 | 819.9 | 794.8 | 829.8 | 835.7 | 822.2
506 | 316 | 826.9 | 797.8 | 821.5 | 837.4 | 825.7
507 | 317 | 834.1 | 800.7 | 824.7 | 838.8 | 818.9
508 | 318 | 840 | 802 | 835.5 | 840.2 | 813.7
509 | 319 | 844.9 | 800.9 | 847 | 843.1 | 811.3
510 | 320 | 849.3 | 800.9 | 848 | 846.5 | 808.2
511 | 321 | 854.7 | 802.6 | 846.9 | 848.7 | 799.7
512 | 322 | 860.2 | 804.7 | 854.7 | 850.2 | 795.8
513 | 323 | 865 | 805.4 | 860.6 | 852.5 | 797.2
514 | 324 | 869.6 | 806.6 | 860.7 | 855 | 793.7
515 | 325 | 874.9 | 810.3 | 861.9 | 855.2 | 796.6
516 | 326 | 878.9 | 809.5 | 871 | 857.5 | 797.3
517 | 327 | 881.8 | 809 | 872.4 | 860.7 | 795
518 | 328 | 884.7 | 811.6 | 871.8 | 863.2 | 794.7
519 | 329 | 888.1 | 811.3 | 873.2 | 864.8 | 791.6
520 | 330 | 891.5 | 812.7 | 869.9 | 865.9 | 779.4
521 | 331 | 896.3 | 816.7 | 863.1 | 863.1 | 775.8
522 | 332 | 900.4 | 818.8 | 863.4 | 863.2 | 779.5
523 | 333 | 903.8 | 821.8 | 866.2 | 864.6 | 780.1
524 | 334 | 907 | 821.4 | 873.1 | 867.5 | 783.7
525 | 335 | 909.4 | 820.3 | 875.2 | 870.7 | 784.7
526 | 336 | 911.9 | 820.6 | 877 | 872.6 | 785.3
527 | 337 | 913.7 | 819.8 | 874.9 | 873.7 | 790.8
528 | 338 | 916.2 | 820.4 | 871.5 | 874.8 | 800.9
529 | 339 | 919.4 | 822.9 | 869 | 873.2 | 797.1
530 | 340 | 922.4 | 825.4 | 873 | 871.5 | 787.7
531 | 341 | 924.4 | 828.5 | 873.3 | 872.1 | 791.1
532 | 342 | 927.2 | 831.3 | 876.3 | 871.5 | 791.1
533 | 343 | 929.3 | 832.9 | 879 | 874.3 | 790.4
534 | 344 | 930.9 | 832.1 | 882.7 | 878 | 795.5
535 | 345 | 932.4 | 832.5 | 883.5 | 879.3 | 800.1
536 | 346 | 933.7 | 834 | 882.3 | 878.2 | 798.5
537 | 347 | 935.6 | 834.5 | 884 | 877.3 | 790.1
538 | 348 | 938.4 | 836.4 | 884.6 | 876.4 | 787.7
539 | 349 | 940.8 | 837.9 | 879.8 | 870.7 | 779
540 | 350 | 942.2 | 837.3 | 878.2 | 868.7 | 775.1
541 | 351 | 943.1 | 837.3 | 877.6 | 869.9 | 771.6
542 | 352 | 943.7 | 838.2 | 878.7 | 871 | 770.1
543 | 353 | 944.6 | 840.8 | 880 | 871.1 | 771.6
544 | 354 | 945.7 | 841.8 | 877.5 | 870.9 | 772.7
545 | 355 | 946.5 | 843.1 | 878.9 | 872.3 | 773.5
546 | 356 | 946.6 | 843.8 | 876.8 | 873.9 | 776.8
547 | 357 | 946.9 | 844 | 878.1 | 876.2 | 775
548 | 358 | 947.3 | 842.5 | 884.1 | 877.2 | 773.7
549 | 359 | 948.1 | 842.4 | 883.9 | 877 | 775.9
550 | 360 | 948.9 | 843.9 | 879.2 | 874.5 | 773.5
551 | 361 | 949.2 | 843.8 | 880.6 | 877.3 | 772.4
552 | 362 | 948.6 | 839.5 | 883.4 | 883.3 | 772.5
553 | 363 | 948.1 | 840.1 | 880.5 | 883.4 | 772.1
554 | 364 | 948.5 | 841.9 | 878.3 | 879.5 | 771.6
555 | 365 | 948.7 | 843 | 879.5 | 880 | 773.7
556 | 366 | 949 | 843.2 | 880.3 | 885.2 | 781.3
557 | 367 | 948.2 | 840.2 | 883.9 | 893.6 | 791.7
558 | 368 | 947.2 | 839 | 886.9 | 897.9 | 795.7
559 | 369 | 946.6 | 836.9 | 890.1 | 901 | 793.4
560 | 370 | 946 | 836.1 | 887.8 | 898.5 | 790.3
561 | 371 | 945.6 | 837.5 | 881.7 | 896.3 | 789.6
562 | 372 | 945.4 | 840.3 | 877.4 | 890.8 | 780.5
563 | 373 | 945.9 | 844.4 | 871.7 | 882.4 | 775
564 | 374 | 946.9 | 848.8 | 864.4 | 872.3 | 763
565 | 375 | 947.6 | 851.5 | 862.7 | 867.1 | 754.8
566 | 376 | 947.5 | 850.4 | 870.2 | 877.1 | 755.9
567 | 377 | 946.5 | 848.2 | 875 | 884.8 | 762.6
568 | 378 | 945.8 | 846 | 877.5 | 889.8 | 764.2
569 | 379 | 945.5 | 845.9 | 880 | 896.1 | 769.5
570 | 380 | 945.4 | 846.7 | 880.3 | 898 | 777.9
571 | 381 | 944.5 | 847.4 | 876.6 | 898.4 | 784.3
572 | 382 | 943.9 | 849.7 | 880.2 | 903.2 | 792
573 | 383 | 943.8 | 852 | 879.8 | 903.9 | 794.7
574 | 384 | 943.8 | 852.2 | 880.8 | 904.9 | 800.3
575 | 385 | 943.4 | 853.2 | 879.6 | 903.4 | 804.3
576 | 386 | 943 | 854.6 | 882.2 | 902.9 | 806.8
577 | 387 | 942.9 | 853.9 | 887.3 | 904.3 | 812.1
578 | 388 | 943.3 | 853.7 | 887.2 | 905.6 | 811.8
579 | 389 | 944.4 | 854.1 | 888.7 | 905.8 | 809.5
580 | 390 | 943.8 | 850.8 | 890.4 | 911.2 | 810.2
581 | 391 | 942.5 | 849.1 | 890.3 | 912.1 | 815.2
582 | 392 | 941.6 | 847.8 | 890.9 | 914.5 | 821
583 | 393 | 941 | 847.1 | 889.7 | 914.3 | 823.4
584 | 394 | 941.6 | 848.7 | 887.9 | 915.6 | 824
585 | 395 | 942.1 | 848.3 | 889.4 | 916.4 | 825.2
586 | 396 | 942 | 848.3 | 892.3 | 915.1 | 825.5
587 | 397 | 941.5 | 846 | 892.8 | 918.6 | 829.9
588 | 398 | 941.1 | 844.6 | 892.5 | 922 | 832.1
589 | 399 | 940.6 | 845.7 | 888.8 | 922.1 | 832.2
590 | 400 | 940.5 | 850.1 | 888.9 | 912.7 | 820
591 | 401 | 941.4 | 851.8 | 885.3 | 903.9 | 811.1
592 | 402 | 943.2 | 856.3 | 882.6 | 892 | 799.7
593 | 403 | 944.1 | 855.1 | 883.9 | 896.2 | 795.7
594 | 404 | 945 | 855.2 | 880.1 | 890.2 | 787
595 | 405 | 945.4 | 855.3 | 880.2 | 885.5 | 782
596 | 406 | 945.2 | 851.2 | 884.5 | 897.4 | 783.4
597 | 407 | 945.6 | 851.9 | 884.7 | 898.9 | 787.9
598 | 408 | 946.2 | 851.3 | 886.8 | 899.4 | 787
599 | 409 | 946.7 | 850.8 | 885.9 | 899.5 | 785.5
600 | 410 | 947.3 | 851.7 | 887 | 900.1 | 791.1
601 | 411 | 947.9 | 852.1 | 887.7 | 901.9 | 798.4
602 | 412 | 948.3 | 853.3 | 887.2 | 902.7 | 807.6
603 | 413 | 948.5 | 851.9 | 886.6 | 908 | 815.4
604 | 414 | 948.1 | 852.1 | 885.1 | 909.5 | 821.1
605 | 415 | 947.6 | 850.3 | 885.4 | 912.6 | 825.9
606 | 416 | 947.7 | 851 | 887.6 | 912.1 | 831.8
607 | 417 | 947.8 | 850.3 | 889.2 | 917.2 | 833.5
608 | 418 | 947.9 | 851.5 | 885.4 | 919.4 | 836.6
609 | 419 | 948.1 | 852.9 | 885.1 | 916.9 | 839.3
610 | 420 | 949 | 853.6 | 888.4 | 912.3 | 839.4
611 | 421 | 950 | 852.7 | 888 | 910.5 | 831.6
612 | 422 | 951 | 850 | 888.2 | 908 | 826.5
613 | 423 | 952.5 | 849.8 | 884.9 | 895.7 | 817.7
614 | 424 | 953.3 | 850.2 | 882.4 | 895.5 | 812.4
615 | 425 | 953.6 | 849.8 | 882.3 | 899.2 | 812.6
616 | 426 | 953.4 | 849.4 | 886.2 | 899.9 | 812.5
617 | 427 | 953.3 | 848.6 | 889.2 | 906.4 | 812
618 | 428 | 953.2 | 847.7 | 890.6 | 906.9 | 811.6
619 | 429 | 953.1 | 848.1 | 892.2 | 912.9 | 817
620 | 430 | 953 | 847.8 | 894.6 | 917.4 | 822.4
621 | 431 | 952.6 | 847.9 | 892.4 | 916.9 | 825.6
622 | 432 | 953 | 850.3 | 890.4 | 905.1 | 817
623 | 433 | 953.4 | 850.8 | 891.9 | 908.5 | 813.8
624 | 434 | 954 | 854.5 | 887.9 | 905.3 | 812.5
625 | 435 | 954.2 | 854.1 | 887.8 | 905.8 | 811.2
626 | 436 | 954 | 852.4 | 890.7 | 909 | 811.7
627 | 437 | 953.1 | 849.5 | 892.8 | 915.8 | 820.4
628 | 438 | 952.4 | 849.2 | 892.9 | 920.4 | 830.9
629 | 439 | 951.7 | 848.6 | 891.3 | 921.7 | 838.5
630 | 440 | 951.3 | 853.4 | 888.5 | 914.9 | 842.4
631 | 441 | 951.2 | 855 | 892.1 | 916.9 | 849.6
632 | 442 | 950.9 | 855.9 | 892.8 | 920.5 | 855.8
633 | 443 | 951.1 | 860 | 891.2 | 918.2 | 859.1
634 | 444 | 951.7 | 859.3 | 891 | 920 | 862.9
635 | 445 | 951.9 | 855.8 | 893 | 919.9 | 866.6
636 | 446 | 951.3 | 855.1 | 893.4 | 924.1 | 870
637 | 447 | 951.2 | 858 | 887.9 | 921.4 | 870.8
638 | 448 | 952 | 862.8 | 885.1 | 912.7 | 863.4
639 | 449 | 953.3 | 862.6 | 884.6 | 909.8 | 850.7
640 | 450 | 953.5 | 856.8 | 885.8 | 915 | 845.5
641 | 451 | 954.3 | 855.1 | 882.8 | 910.2 | 836.7
642 | 452 | 954.7 | 857.4 | 881.4 | 912 | 832.3
643 | 453 | 955.1 | 855.7 | 881.7 | 913.9 | 827.8
644 | 454 | 955.5 | 854.4 | 879.1 | 909.3 | 826.3
645 | 455 | 955.1 | 854 | 879.1 | 913.4 | 834.2
646 | 456 | 954.7 | 853 | 881.1 | 915.3 | 842.5
647 | 457 | 955.2 | 854 | 882.9 | 913 | 840.7
648 | 458 | 955.2 | 854.9 | 883.6 | 918.2 | 845
649 | 459 | 955 | 856.9 | 882 | 917 | 846.8
650 | 460 | 955.9 | 856 | 881.6 | 910.4 | 841.3
651 | 461 | 955.1 | 852.8 | 886.7 | 916.7 | 844.8
652 | 462 | 953.4 | 848.7 | 888.5 | 920 | 851.5
653 | 463 | 952.6 | 849.3 | 887.6 | 919.5 | 852.7
654 | 464 | 953 | 847.6 | 885.6 | 915.3 | 839.4
655 | 465 | 954.1 | 847.8 | 880.4 | 908 | 827.1
656 | 466 | 954.8 | 850.6 | 879.3 | 901.1 | 819.9
657 | 467 | 955 | 852 | 881.7 | 901.3 | 818.3
658 | 468 | 954 | 849.5 | 885.7 | 909.7 | 825.4
659 | 469 | 953.1 | 849.6 | 885.9 | 910.7 | 827.7
660 | 470 | 952.4 | 848.3 | 887 | 915.3 | 827.4
661 | 471 | 952 | 847.3 | 888.4 | 917.7 | 832
662 | 472 | 950.6 | 843.4 | 889.7 | 919.1 | 833.9
663 | 473 | 949.8 | 842.8 | 890.9 | 922.9 | 832.7
664 | 474 | 948.4 | 840 | 888.9 | 917.9 | 833.2
665 | 475 | 946.8 | 837.8 | 888.1 | 918.4 | 837.8
666 | 476 | 945.5 | 836.8 | 887.1 | 918.2 | 843.2
667 | 477 | 944.1 | 836.7 | 888.1 | 918.3 | 844.6
668 | 478 | 943.2 | 837.9 | 887.7 | 917.3 | 845.5
669 | 479 | 942.6 | 840.8 | 887.5 | 916.6 | 848.7
670 | 480 | 942.3 | 839.7 | 887.1 | 918 | 854.9
671 | 481 | 942.4 | 841.7 | 886.4 | 917.9 | 855.8
672 | 482 | 941.1 | 839.3 | 886.4 | 913 | 856.7
673 | 483 | 940.5 | 840.4 | 886.2 | 915.6 | 859.4
674 | 484 | 940 | 839.1 | 886.6 | 917.1 | 864.3
675 | 485 | 939.5 | 841.7 | 888.2 | 918.5 | 868.9
676 | 486 | 939.8 | 841.7 | 888.8 | 919 | 873.1
677 | 487 | 939.8 | 843.1 | 889.2 | 917.9 | 879
678 | 488 | 939.5 | 839.5 | 889.9 | 915.2 | 884.7
679 | 489 | 939.4 | 836.9 | 889.8 | 915.8 | 882.7
680 | 490 | 939.4 | 834.6 | 888.7 | 915.7 | 876.1
681 | 491 | 939.7 | 834 | 888.1 | 919.9 | 866.8
682 | 492 | 939.7 | 834.8 | 887.8 | 920.5 | 864.9
683 | 493 | 938.9 | 834.5 | 888.4 | 918.9 | 868.9
684 | 494 | 938.4 | 833 | 888.7 | 919.9 | 873.7
685 | 495 | 937.9 | 832 | 888.2 | 917.3 | 875.4
686 | 496 | 937.9 | 833.8 | 888.4 | 918.8 | 879.8
687 | 497 | 937.9 | 833.2 | 889.6 | 919.7 | 879.2
688 | 498 | 938.4 | 832.6 | 889.5 | 919.5 | 872.7
689 | 499 | 938.8 | 833.7 | 888.6 | 920 | 867
690 | 500 | 939.1 | 833.3 | 887.9 | 919.6 | 863.8
691 | 501 | 939.2 | 834 | 888 | 919.8 | 864.9
692 | 502 | 939.2 | 832.9 | 888.3 | 919.6 | 865.9
693 | 503 | 939.3 | 833.9 | 888.8 | 922.6 | 868.5
694 | 504 | 939.8 | 835.7 | 888.9 | 924.2 | 870.6
695 | 505 | 939.9 | 832.6 | 889 | 921.1 | 866.4
696 | 506 | 940.2 | 831.9 | 889.5 | 920 | 866.9
697 | 507 | 940.5 | 831.1 | 890.5 | 919.7 | 869
698 | 508 | 940.5 | 830.9 | 891.4 | 918.5 | 873.5
699 | 509 | 940 | 830 | 891.2 | 916.2 | 871.7
700 | 510 | 939.5 | 829.2 | 889.3 | 913.4 | 873.9
701 | 511 | 939.2 | 830.1 | 889.3 | 914.4 | 875.8
702 | 512 | 939.4 | 829.4 | 889.6 | 915.8 | 873.2
703 | 513 | 939.9 | 828.8 | 888.8 | 918.2 | 865.5
704 | 514 | 940.5 | 829.6 | 887.8 | 917.2 | 856.6
705 | 515 | 941.3 | 831.4 | 887.6 | 914 | 843.9
706 | 516 | 941.6 | 832.9 | 888.9 | 916.6 | 847.4
707 | 517 | 942.1 | 831.9 | 891.3 | 917.9 | 849.1
708 | 518 | 942.7 | 831.9 | 893.1 | 919.5 | 848.5
709 | 519 | 943.1 | 830 | 893.7 | 919.1 | 845.3
710 | 520 | 944.4 | 829.7 | 892.7 | 914.3 | 839.6
711 | 521 | 945 | 829.4 | 892.4 | 913.4 | 839.5
712 | 522 | 944.5 | 829.1 | 892.6 | 913.5 | 843.6
713 | 523 | 943.5 | 830.7 | 893.2 | 912.7 | 845.6
714 | 524 | 943.3 | 829.1 | 894.9 | 914.1 | 846.2
715 | 525 | 942.3 | 824.9 | 896.2 | 912.2 | 842.9
716 | 526 | 942.2 | 824 | 895.9 | 914.9 | 840.6
717 | 527 | 942.4 | 826 | 896.1 | 914.9 | 846
718 | 528 | 942.9 | 826.5 | 895.9 | 914 | 842
719 | 529 | 943.5 | 828.1 | 895.6 | 912.4 | 836.3
720 | 530 | 943.5 | 826.6 | 895.8 | 912 | 835.1
721 | 531 | 943.8 | 825.5 | 896.5 | 913.4 | 830.1
722 | 532 | 944.3 | 824.7 | 896 | 912.8 | 824.9
723 | 533 | 944.5 | 823.3 | 896.1 | 912.5 | 819.7
724 | 534 | 944.6 | 820.6 | 895.5 | 912.8 | 820.2
725 | 535 | 944.7 | 820.5 | 895.8 | 913.4 | 821.5
726 | 536 | 945.5 | 823.2 | 895 | 908.5 | 813.2
727 | 537 | 945.6 | 822.5 | 895.9 | 907.7 | 807.6
728 | 538 | 945.7 | 823.8 | 896.3 | 905.1 | 810.4
729 | 539 | 945.5 | 826.2 | 896.7 | 905.1 | 818.9
730 | 540 | 945.5 | 829.4 | 898.4 | 906.9 | 827.6
731 | 541 | 944.7 | 829.2 | 899.9 | 910.7 | 835.5
732 | 542 | 944.2 | 827.9 | 900.4 | 914.1 | 840.9
733 | 543 | 943.9 | 828 | 899.5 | 914.4 | 844.8
734 | 544 | 943.5 | 827.9 | 899.3 | 913.8 | 853.7
735 | 545 | 943.2 | 829.5 | 899.7 | 916.8 | 863.7
736 | 546 | 943.3 | 829.1 | 900 | 917.4 | 866.7
737 | 547 | 943.9 | 830.7 | 898.9 | 914.4 | 861
738 | 548 | 944.4 | 832 | 899.1 | 913.1 | 859.5
739 | 549 | 944.3 | 828.9 | 899.2 | 913.9 | 859
740 | 550 | 944 | 827.1 | 898.8 | 913.7 | 861.1
741 | 551 | 943.7 | 826.8 | 899.3 | 914.1 | 861.1
742 | 552 | 942.7 | 824.2 | 899.7 | 915.1 | 861.9
743 | 553 | 942 | 822.4 | 899 | 916.6 | 859.2
744 | 554 | 941.9 | 824.1 | 899.2 | 917 | 856.9
745 | 555 | 941.7 | 821.6 | 899.9 | 917.1 | 851.7
746 | 556 | 941.4 | 822.5 | 898.1 | 912.2 | 840
747 | 557 | 941.1 | 825.3 | 896.8 | 905.2 | 832.2
748 | 558 | 940.5 | 825.6 | 897.4 | 904.3 | 832.6
749 | 559 | 939.8 | 823.9 | 898.6 | 908.4 | 832.5
750 | 560 | 939 | 824.3 | 897.2 | 909.8 | 834.5
751 | 561 | 938.2 | 827.4 | 896.2 | 912.5 | 839
752 | 562 | 937.9 | 830.1 | 896.2 | 911.5 | 845.1
753 | 563 | 937.4 | 831.9 | 896.6 | 912.6 | 852.9
754 | 564 | 937 | 833.6 | 897 | 914.3 | 859.8
755 | 565 | 937.2 | 833.1 | 897.6 | 913.3 | 863.9
756 | 566 | 936.9 | 832.2 | 895.9 | 909.3 | 865.4
757 | 567 | 936.4 | 832.5 | 894.5 | 906.1 | 865.3
758 | 568 | 936 | 838.5 | 893.1 | 907.2 | 868.9
759 | 569 | 936.4 | 837.1 | 893.7 | 908.1 | 873.7
760 | 570 | 936 | 838.8 | 891.9 | 908.1 | 873.9
761 | 571 | 936 | 838.8 | 891.8 | 907.6 | 878.5
762 | 572 | 936.5 | 838.3 | 892.1 | 907.5 | 884
763 | 573 | 935.9 | 838.3 | 892 | 907.8 | 891.1
764 | 574 | 935.4 | 838.9 | 891 | 908.2 | 891.7
765 | 575 | 935.2 | 838.1 | 890.3 | 907.7 | 897.5
766 | 576 | 935.3 | 837.3 | 891.3 | 907.9 | 904.3
767 | 577 | 935 | 838.2 | 892.1 | 908.5 | 905.8
768 | 578 | 935.1 | 836.2 | 892.8 | 908.8 | 911.4
769 | 579 | 935.4 | 837.3 | 893.6 | 909.8 | 913.6
770 | 580 | 935.4 | 838.5 | 894.2 | 909.4 | 911.5
771 | 581 | 936.3 | 840.5 | 894.7 | 910.7 | 913
772 | 582 | 937.2 | 841.1 | 895.5 | 909.1 | 907.4
773 | 583 | 936.8 | 838.3 | 896 | 909 | 902.7
774 | 584 | 936.2 | 837.4 | 895 | 909.5 | 905.2
775 | 585 | 935.9 | 842.7 | 894 | 911.3 | 905.4
776 | 586 | 936.2 | 843.1 | 894 | 910.9 | 898.6
777 | 587 | 936.7 | 846.2 | 893.5 | 909.2 | 896.3
778 | 588 | 936.5 | 849.2 | 893.2 | 909.1 | 894.8
779 | 589 | 936.4 | 852.5 | 891.1 | 906 | 890.4
780 | 590 | 936.6 | 854.2 | 890 | 903.4 | 883.9
781 | 591 | 936.5 | 856 | 888.7 | 899.2 | 876.7
782 | 592 | 936.9 | 860 | 887.2 | 897.4 | 868
783 | 593 | 936.7 | 861.1 | 886.1 | 895.9 | 866.2
784 | 594 | 936.4 | 860.2 | 885.4 | 897.1 | 867.3
785 | 595 | 936.2 | 861.2 | 882.3 | 893.6 | 864.9
786 | 596 | 936.5 | 863.8 | 880.7 | 889.4 | 859.2
787 | 597 | 936.5 | 862.2 | 880 | 890.2 | 858.8
788 | 598 | 937.4 | 861.6 | 879.8 | 890.9 | 858
789 | 599 | 937.5 | 863.4 | 878.9 | 892.2 | 858.7
790 | 600 | 937 | 863.5 | 878.4 | 895.7 | 867.1
791 | 601 | 936.3 | 858 | 879.5 | 898.5 | 872.9
792 | 602 | 935.5 | 858.2 | 880.2 | 901.8 | 871.5
793 | 603 | 935.4 | 857.9 | 879.9 | 902.5 | 865.4
794 | 604 | 935.8 | 857.1 | 880.3 | 902.6 | 861.6
795 | 605 | 935.8 | 857.1 | 880.3 | 903.5 | 861.3
796 | 606 | 935.7 | 860.2 | 879.8 | 899.3 | 854.6
797 | 607 | 936 | 860.5 | 879.5 | 898.4 | 854.3
798 | 608 | 934.9 | 860.3 | 878.1 | 901 | 858.6
799 | 609 | 934 | 863.5 | 874.5 | 897.9 | 859.2
800 | 610 | 932.8 | 864 | 871.7 | 893.2 | 858.1
801 | 611 | 931.7 | 869.4 | 871.4 | 895 | 864.2
802 | 612 | 931.2 | 869.6 | 870.1 | 894.8 | 870.3
803 | 613 | 931.3 | 869.4 | 867.2 | 891.5 | 873.1
804 | 614 | 930.5 | 870.6 | 865.2 | 888.9 | 875.4
805 | 615 | 930.4 | 873.1 | 863.6 | 886.8 | 881.9
806 | 616 | 930.6 | 874.6 | 864.8 | 888 | 884.2
807 | 617 | 930.4 | 876.5 | 863.7 | 888.2 | 887
808 | 618 | 930.9 | 879.3 | 863.9 | 887.3 | 892.9
809 | 619 | 930.8 | 884.7 | 864.4 | 889.2 | 897.8
810 | 620 | 931.4 | 886.2 | 863.8 | 887.7 | 899.9
811 | 621 | 931.6 | 885.1 | 864.6 | 891.6 | 898.4
812 | 622 | 931.1 | 885.6 | 864.9 | 895.8 | 898.7
813 | 623 | 930.9 | 887.2 | 865 | 896.1 | 900.6
814 | 624 | 930.8 | 889.6 | 864.3 | 896.8 | 901.6
815 | 625 | 931.2 | 888.6 | 863.9 | 897 | 904.7
816 | 626 | 931.5 | 888.9 | 864.8 | 898.7 | 908.8
817 | 627 | 931.8 | 888.5 | 864.7 | 897.7 | 908
818 | 628 | 932.7 | 884 | 863.1 | 893.5 | 905.1
819 | 629 | 933.1 | 882.9 | 862.8 | 894.5 | 899.1
820 | 630 | 933.1 | 884.9 | 862.4 | 894.7 | 903.8
821 | 631 | 934.1 | 875.1 | 861.3 | 891.6 | 904.6
822 | 632 | 934 | 862.7 | 858.4 | 888.4 | 899.6
823 | 633 | 934.3 | 850.5 | 855.9 | 883 | 891.4
824 | 634 | 934.6 | 836.9 | 852.4 | 878.5 | 886.4
825 | 635 | 934 | 843.8 | 852.2 | 880.1 | 887.3
826 | 636 | 933.7 | 848.4 | 852.2 | 883.6 | 891.6
827 | 637 | 933.5 | 854.6 | 850.7 | 884 | 893.7
828 | 638 | 933.5 | 856.1 | 850.1 | 886 | 894.2
829 | 639 | 933.8 | 860.1 | 848.9 | 884.9 | 896.3
830 | 640 | 933.7 | 861.6 | 849.5 | 885 | 896.3
831 | 641 | 933 | 858.3 | 848.7 | 886.4 | 895.7
832 | 642 | 932.6 | 847.6 | 845.5 | 882.5 | 896.1
833 | 643 | 932.1 | 853.4 | 844.2 | 879.5 | 892
834 | 644 | 932.2 | 859.7 | 845.2 | 883.2 | 891.1
835 | 645 | 932.1 | 864.5 | 844.5 | 884.6 | 890.3
836 | 646 | 931.7 | 872 | 844.2 | 884.5 | 893.2
837 | 647 | 930.7 | 876.9 | 843.9 | 886 | 898.9
838 | 648 | 929.6 | 871.6 | 841.4 | 885.5 | 899.9
839 | 649 | 929 | 874.5 | 842.6 | 887.1 | 904.7
840 | 650 | 929.1 | 870.4 | 843 | 887.6 | 903.5
841 | 651 | 929.7 | 872.3 | 845.6 | 886.9 | 908.6
842 | 652 | 930.5 | 875.7 | 846.3 | 888 | 914.2
843 | 653 | 930.7 | 874.3 | 847.6 | 890.2 | 919.3
844 | 654 | 931.1 | 873.7 | 848.9 | 891.1 | 917.2
845 | 655 | 932 | 875.3 | 849.2 | 893.5 | 921.4
846 | 656 | 931.9 | 880.6 | 850.5 | 896.8 | 919.5
847 | 657 | 931.9 | 880.4 | 851.6 | 897.1 | 919.2
848 | 658 | 931.7 | 881.7 | 851.3 | 896.5 | 917.7
849 | 659 | 933.1 | 874.6 | 849.2 | 890.6 | 919.5
850 | 660 | 934.3 | 873.6 | 848.8 | 888.5 | 915.2
851 | 661 | 934.1 | 878.7 | 848.3 | 890.2 | 915.7
852 | 662 | 933.9 | 882.8 | 848.3 | 890.8 | 917.6
853 | 663 | 933.5 | 882 | 845.8 | 890.2 | 915.1
854 | 664 | 932.7 | 879.6 | 845.3 | 891.3 | 913.6
855 | 665 | 932.8 | 880.5 | 846.3 | 892.1 | 917.1
856 | 666 | 933.1 | 878 | 847.4 | 892.2 | 916.6
857 | 667 | 933.3 | 875 | 845.9 | 889.6 | 915.6
858 | 668 | 933.9 | 874.5 | 843.8 | 885.6 | 912.7
859 | 669 | 934.8 | 871.8 | 843.2 | 884.7 | 915.3
860 | 670 | 935.3 | 866 | 840.6 | 881 | 916.9
861 | 671 | 935.5 | 863.6 | 840.1 | 881.1 | 910.8
862 | 672 | 935.2 | 866.4 | 839.7 | 882 | 906.6
863 | 673 | 935.2 | 861.5 | 838.5 | 880.9 | 909.5
864 | 674 | 935.4 | 865.1 | 838.8 | 881.3 | 917.9
865 | 675 | 935.6 | 867.8 | 837.2 | 878.6 | 920.3
866 | 676 | 935.8 | 877.1 | 838.6 | 879.7 | 925.9
867 | 677 | 935.6 | 882.8 | 840.9 | 883.3 | 927.5
868 | 678 | 936 | 887.5 | 842.3 | 885.4 | 927.8
869 | 679 | 935.8 | 887.6 | 844.4 | 886.9 | 926.9
870 | 680 | 935.9 | 887 | 846.5 | 889.3 | 928.9
871 | 681 | 936.1 | 891.6 | 844.2 | 888.7 | 928.6
872 | 682 | 935.2 | 893.3 | 844 | 889.6 | 928.8
873 | 683 | 934.5 | 891.3 | 843.1 | 888.3 | 927.7
874 | 684 | 935.2 | 885.6 | 843.4 | 883.7 | 930
875 | 685 | 936.3 | 883.5 | 841.8 | 879 | 927.3
876 | 686 | 937.5 | 871.9 | 838 | 871.8 | 925.7
877 | 687 | 938.3 | 857.4 | 834.4 | 866 | 920.4
878 | 688 | 938 | 857.3 | 833.1 | 866.5 | 918.6
879 | 689 | 937.5 | 857.3 | 834 | 869 | 921.1
880 | 690 | 937.7 | 856.8 | 834.6 | 868.6 | 921.4
881 | 691 | 937.1 | 859.1 | 835.3 | 870.6 | 922.1
882 | 692 | 937 | 861.9 | 836.7 | 872.3 | 925.6
883 | 693 | 936.9 | 866.4 | 836.4 | 871.6 | 927.2
884 | 694 | 936.3 | 863.3 | 836.7 | 871.4 | 926.2
885 | 695 | 936.3 | 865.5 | 838.4 | 872.1 | 930
886 | 696 | 936.3 | 870.9 | 839.9 | 874.4 | 929.1
887 | 697 | 935.6 | 877.6 | 841.6 | 876.7 | 926.3
888 | 698 | 934.4 | 876.9 | 841.3 | 879.6 | 926
889 | 699 | 933.6 | 880.2 | 837.4 | 880.2 | 923.8
890 | 700 | 933 | 884.4 | 836.5 | 881.2 | 927.4
891 | 701 | 933 | 884.9 | 837.1 | 881.3 | 932.8
892 | 702 | 932.6 | 892 | 838.2 | 880.7 | 935.2
893 | 703 | 932.6 | 892.9 | 839.2 | 879.6 | 937.4
894 | 704 | 933.2 | 896.5 | 837.8 | 877.8 | 939.8
895 | 705 | 933.5 | 897.5 | 836.2 | 878.2 | 937.8
896 | 706 | 933.5 | 901.1 | 835.5 | 878 | 932.4
897 | 707 | 932.6 | 898.5 | 837.2 | 879.2 | 930.7
898 | 708 | 933 | 894 | 835.9 | 875.8 | 934
899 | 709 | 933.6 | 892.4 | 835.8 | 875 | 936.4
900 | 710 | 933.7 | 893.6 | 838.4 | 879.4 | 936.2
901 | 711 | 934.2 | 893.7 | 838.8 | 879 | 938
902 | 712 | 934 | 891.2 | 838.4 | 879.8 | 938.5
903 | 713 | 934.1 | 888.2 | 836.4 | 876.7 | 935.7
904 | 714 | 934 | 886.3 | 832.8 | 875.4 | 935
905 | 715 | 934.5 | 875.8 | 832 | 872.2 | 937.8
906 | 716 | 934.9 | 879.8 | 831.8 | 869.4 | 936.5
907 | 717 | 934.7 | 886.7 | 834.9 | 871.3 | 933.4
908 | 718 | 935 | 885.8 | 836.1 | 870.7 | 932.8
909 | 719 | 934.9 | 882.6 | 836 | 871.7 | 934
910 | 720 | 934.8 | 873.2 | 835.9 | 869.5 | 928.6
911 | 721 | 934.5 | 865.3 | 836.5 | 869.2 | 920.5
912 | 722 | 934.9 | 862 | 836.5 | 868.2 | 908
913 | 723 | 935.6 | 867 | 839.2 | 869.8 | 902.3
914 | 724 | 935.5 | 870.3 | 840.7 | 872.9 | 907.7
915 | 725 | 934 | 868.5 | 843 | 878.3 | 912.2
916 | 726 | 933.2 | 874.4 | 840.3 | 878.3 | 912.4
917 | 727 | 932.2 | 874.1 | 837.2 | 876.7 | 914.1
918 | 728 | 932 | 875.2 | 838.6 | 876.5 | 915.1
919 | 729 | 932.5 | 881.5 | 836.7 | 873.8 | 914.6
920 | 730 | 932.6 | 887.3 | 835.7 | 874.2 | 919.2
921 | 731 | 932.9 | 883.7 | 833.9 | 873.1 | 922.6
922 | 732 | 932.9 | 881.3 | 833.9 | 873.4 | 923.9
923 | 733 | 932.3 | 878.5 | 835.1 | 875.8 | 922.9
924 | 734 | 931.9 | 878.9 | 834.7 | 876 | 926.7
925 | 735 | 932.1 | 882.7 | 835.5 | 876.1 | 928.7
926 | 736 | 932.8 | 877.9 | 831.1 | 870.8 | 928.9
927 | 737 | 933.2 | 876.2 | 827.9 | 868.3 | 929.2
928 | 738 | 933.6 | 875.7 | 831.6 | 872 | 932.7
929 | 739 | 934 | 883.6 | 831.9 | 874.6 | 933.6
930 | 740 | 933.7 | 882.7 | 830.7 | 875.4 | 930.9
931 | 741 | 933.6 | 886.3 | 832.8 | 877.6 | 935.3
932 | 742 | 934 | 889.4 | 834.7 | 879.5 | 935.5
933 | 743 | 933.9 | 893.1 | 834.9 | 879.9 | 931.5
934 | 744 | 934.2 | 901.8 | 835.4 | 879.5 | 932.5
935 | 745 | 934.2 | 899.1 | 839.5 | 881.1 | 934.6
936 | 746 | 933.4 | 894.8 | 844.4 | 883 | 934.1
937 | 747 | 932.2 | 893.4 | 844.3 | 885.2 | 931.5
938 | 748 | 931.1 | 897.7 | 845.4 | 887.1 | 929.7
939 | 749 | 930.1 | 894.5 | 848 | 888.4 | 933.7
940 | 750 | 929.3 | 884.5 | 853.9 | 889.9 | 937.8
941 | 751 | 929.4 | 886.4 | 858.6 | 893.3 | 938
942 | 752 | 930.4 | 889.8 | 860.3 | 893.1 | 937
943 | 753 | 930.9 | 888.3 | 861.3 | 890.9 | 938.7
944 | 754 | 931.1 | 891.5 | 862.1 | 892.2 | 939.8
945 | 755 | 932.4 | 889.2 | 861.9 | 895.4 | 939.5
946 | 756 | 933.5 | 901.8 | 861.7 | 894.6 | 935.3
947 | 757 | 933.8 | 902 | 860 | 892.9 | 935.4
948 | 758 | 934.2 | 898 | 860.7 | 891.3 | 936.4
949 | 759 | 935.8 | 897.5 | 858.1 | 888.4 | 933.9
950 | 760 | 935.8 | 899.9 | 856.3 | 888.5 | 932.5
951 | 761 | 935.7 | 897 | 852.2 | 886.5 | 932.2
952 | 762 | 935.6 | 898.8 | 851.5 | 886.8 | 930.6
953 | 763 | 935.6 | 898.8 | 854.6 | 888.9 | 930.4
954 | 764 | 934.8 | 894.2 | 856.5 | 889.9 | 924.3
955 | 765 | 933.7 | 888.6 | 858.4 | 892.3 | 919
956 | 766 | 933.1 | 886.2 | 855.4 | 893 | 916.4
957 | 767 | 933.3 | 883.8 | 853.8 | 893.1 | 914.1
958 | 768 | 933.4 | 887.9 | 854.4 | 895.1 | 914.1
959 | 769 | 932.7 | 888 | 853.4 | 896.4 | 915.4
960 | 770 | 933.5 | 881.8 | 846.8 | 889.8 | 916.7
961 | 771 | 934.2 | 876.6 | 840.4 | 882.6 | 917.3
962 | 772 | 934.1 | 879.3 | 838.7 | 882.7 | 921.1
963 | 773 | 934.3 | 881.6 | 841.1 | 883.3 | 926.1
964 | 774 | 934.8 | 889.1 | 844.1 | 886.2 | 931.4
965 | 775 | 935.4 | 888.4 | 849.7 | 892.9 | 935.1
966 | 776 | 935.8 | 889.3 | 850.1 | 896.2 | 935
967 | 777 | 936.4 | 887.1 | 845.7 | 894.6 | 936.9
968 | 778 | 937.1 | 884.6 | 845.5 | 890.3 | 937.9
969 | 779 | 937.5 | 886.8 | 846.2 | 889.1 | 936.5
970 | 780 | 937.5 | 890.3 | 847.1 | 891.4 | 939.4
971 | 781 | 937.1 | 887.7 | 850.5 | 894 | 938.5
972 | 782 | 937.4 | 892.7 | 854.4 | 898.5 | 936.4
973 | 783 | 936.3 | 893.5 | 857.1 | 900.5 | 934.1
974 | 784 | 935.6 | 894.8 | 856.5 | 902.2 | 933
975 | 785 | 935.5 | 902 | 854.9 | 900.3 | 930.5
976 | 786 | 935.2 | 900 | 859 | 900.7 | 927.4
977 | 787 | 934.1 | 892 | 861.5 | 899.1 | 927.4
978 | 788 | 932.9 | 887.6 | 861.1 | 900.7 | 929.5
979 | 789 | 932 | 901 | 857.3 | 901.9 | 926
980 | 790 | 931.5 | 902.1 | 858.8 | 904.1 | 929
981 | 791 | 931.9 | 906.6 | 860.5 | 904 | 931.8
982 | 792 | 932.4 | 906.3 | 861.1 | 903.2 | 931.4
983 | 793 | 932.1 | 903.4 | 859.4 | 905.1 | 932.1
984 | 794 | 932 | 910.6 | 858.1 | 903.1 | 935.2
985 | 795 | 932.3 | 908.8 | 859 | 902.1 | 931.9
986 | 796 | 932.1 | 906 | 857.8 | 901.4 | 926.4
987 | 797 | 932.7 | 901.7 | 854.9 | 899.1 | 929.6
988 | 798 | 932.9 | 896.6 | 859.5 | 901.6 | 933.3
989 | 799 | 932.5 | 890.6 | 862.3 | 904.7 | 936.8
990 | 800 | 932.7 | 894.6 | 862.2 | 908.6 | 939.1
991 | 801 | 932.4 | 895.9 | 864.6 | 907.3 | 939.6
992 | 802 | 932.2 | 888.4 | 866.8 | 906.9 | 942.5
993 | 803 | 932.4 | 889.8 | 864.3 | 907.4 | 939.2
994 | 804 | 932.5 | 904.5 | 859.5 | 907.4 | 935.9
995 | 805 | 932.4 | 909.5 | 858 | 905.9 | 933.2
996 | 806 | 932.7 | 897.2 | 851.9 | 898.5 | 923.8
997 | 807 | 933.7 | 892.4 | 850.2 | 894.8 | 922
998 | 808 | 933.2 | 891.6 | 853.9 | 898.8 | 920.2
999 | 809 | 932.6 | 893.9 | 856.5 | 901 | 915.4
1000 | 810 | 932.3 | 899.4 | 855.6 | 902.2 | 910.1
1001 | 811 | 932.2 | 898.1 | 860.2 | 904.3 | 915.8
1002 | 812 | 931.3 | 891.9 | 864.7 | 904.8 | 919.9
1003 | 813 | 930.6 | 895.4 | 863.2 | 906.3 | 925.8
1004 | 814 | 930.3 | 902.4 | 856.2 | 907.1 | 929.5
1005 | 815 | 930.3 | 892.9 | 853.1 | 902.2 | 928.6
1006 | 816 | 930.6 | 890.5 | 854.9 | 903.2 | 926.4
1007 | 817 | 930.8 | 893.8 | 860.6 | 905.5 | 924.3
1008 | 818 | 931.6 | 894.1 | 860.8 | 906.9 | 923
1009 | 819 | 932.6 | 893.7 | 857.8 | 902.2 | 921.2
1010 | 820 | 932.9 | 894.1 | 856.3 | 904.5 | 922.5
1011 | 821 | 933.7 | 892.9 | 852 | 901.5 | 924.3
1012 | 822 | 934.2 | 894.7 | 854.1 | 899.5 | 921.9
1013 | 823 | 933.2 | 895.7 | 851.4 | 902.8 | 920.3
1014 | 824 | 932.5 | 896.8 | 849.3 | 903.6 | 921.2
1015 | 825 | 932.6 | 881.8 | 845 | 899 | 922.5
1016 | 826 | 932.6 | 882 | 847.2 | 900.3 | 919.6
1017 | 827 | 931.8 | 881.4 | 850.9 | 902.7 | 919.5
1018 | 828 | 931.3 | 881.7 | 852 | 902.5 | 917.5
1019 | 829 | 931.4 | 882.1 | 846.1 | 902.1 | 912.2
1020 | 830 | 932 | 882.8 | 845.6 | 899.8 | 915.8
1021 | 831 | 931.8 | 885.1 | 842.4 | 900.3 | 917.9
1022 | 832 | 931.2 | 885.7 | 839.3 | 900.1 | 913.2
1023 | 833 | 930.1 | 884.1 | 837.2 | 900.7 | 912.2
1024 | 834 | 930 | 888.9 | 841 | 902.5 | 920.1
1025 | 835 | 929.8 | 892.6 | 842.3 | 904.1 | 925.2
1026 | 836 | 929.3 | 895.2 | 846.5 | 907.4 | 929.4
1027 | 837 | 928.9 | 887.5 | 854 | 910.3 | 929.9
1028 | 838 | 928.4 | 889.4 | 859.7 | 911.3 | 932.2
1029 | 839 | 928.2 | 898.2 | 861.1 | 912.2 | 931.1
1030 | 840 | 928.6 | 901.6 | 855.4 | 908.9 | 931.9
1031 | 841 | 929.3 | 890.7 | 849.2 | 902.4 | 923.5
1032 | 842 | 929.6 | 890.6 | 846.8 | 899.4 | 923.1
1033 | 843 | 930.9 | 885.7 | 844.5 | 896.8 | 917
1034 | 844 | 930.8 | 880.5 | 839.4 | 893.4 | 915.8
1035 | 845 | 931.3 | 874 | 832.8 | 888 | 916.4
1036 | 846 | 931.2 | 877.9 | 833.2 | 890 | 912.8
1037 | 847 | 931.2 | 883.9 | 836.3 | 893.7 | 918.5
1038 | 848 | 931 | 884.5 | 839.7 | 896.4 | 920.7
1039 | 849 | 930.9 | 881.4 | 834.1 | 894.5 | 923.2
1040 | 850 | 931.8 | 885 | 833.4 | 892.4 | 930.1
1041 | 851 | 933.1 | 877.2 | 829.3 | 887.5 | 932
1042 | 852 | 933 | 869.7 | 826.2 | 886.8 | 925.2
1043 | 853 | 932.2 | 868.1 | 829 | 890.6 | 928.1
1044 | 854 | 932.1 | 868.5 | 829.4 | 893.5 | 930.6
1045 | 855 | 931.8 | 870.4 | 834.5 | 895 | 934.5
1046 | 856 | 931.2 | 872.5 | 838.8 | 897 | 936.6
1047 | 857 | 930.7 | 871.7 | 845.4 | 899.5 | 935.6
1048 | 858 | 930.7 | 874.3 | 847.4 | 903.8 | 932.8
1049 | 859 | 930.6 | 875.7 | 841.5 | 902.1 | 935.3
1050 | 860 | 930.3 | 875.5 | 834 | 897.4 | 933.8
1051 | 861 | 931.3 | 867.9 | 827.9 | 889.4 | 933.3
1052 | 862 | 933.3 | 870.4 | 826.1 | 884.4 | 934.7
1053 | 863 | 933.1 | 874.2 | 833 | 891 | 931.1
1054 | 864 | 931.9 | 878.2 | 833.7 | 896.3 | 924.9
1055 | 865 | 930.3 | 884.2 | 831.1 | 895.7 | 924.1
1056 | 866 | 929.4 | 883.8 | 837.4 | 897.5 | 922.8
1057 | 867 | 927.8 | 885.3 | 830.3 | 899.2 | 916.7
1058 | 868 | 927.2 | 881.7 | 828.6 | 896.6 | 927.2
1059 | 869 | 926.7 | 879.5 | 831.1 | 897 | 932.3
1060 | 870 | 926.3 | 882.6 | 828.8 | 899.3 | 929.9
1061 | 871 | 926.7 | 881.6 | 828.9 | 898.1 | 934.3
1062 | 872 | 926.4 | 877.3 | 829.5 | 897.4 | 932
1063 | 873 | 925.8 | 868.7 | 827.4 | 894.2 | 934.6
1064 | 874 | 926 | 866 | 829.2 | 894.8 | 936.3
1065 | 875 | 926.3 | 865.4 | 827.9 | 893.3 | 939.6
1066 | 876 | 926.8 | 868.8 | 824.4 | 892.3 | 938.4
1067 | 877 | 926.9 | 873 | 826.2 | 893.7 | 934.2
1068 | 878 | 926.1 | 873.8 | 834.9 | 899.9 | 937.4
1069 | 879 | 925.4 | 877 | 844.6 | 905.4 | 937.8
1070 | 880 | 925.7 | 881.5 | 851.3 | 909.9 | 937.7
1071 | 881 | 926.2 | 886.6 | 851.7 | 912.4 | 935.3
1072 | 882 | 926 | 893.6 | 849.6 | 912.9 | 936.6
1073 | 883 | 925.7 | 892.2 | 852.6 | 910.1 | 935.4
1074 | 884 | 926 | 897.8 | 855.9 | 913.1 | 937.9
1075 | 885 | 927.2 | 900.3 | 858.3 | 914.9 | 939.3
1076 | 886 | 927.4 | 902.4 | 857.9 | 915.8 | 935.7
1077 | 887 | 927.1 | 906.2 | 854.7 | 915.5 | 926.8
1078 | 888 | 927.6 | 901.4 | 850.3 | 912.9 | 930.6
1079 | 889 | 928.4 | 889.4 | 845.6 | 907.8 | 936.5
1080 | 890 | 929.9 | 884.5 | 841.7 | 901 | 933.2
1081 | 891 | 929.6 | 888.6 | 839.5 | 899.6 | 934.4
1082 | 892 | 929.6 | 891.3 | 842.7 | 902.4 | 932.8
1083 | 893 | 929.5 | 887.3 | 839.6 | 903 | 932.2
1084 | 894 | 929.5 | 887.2 | 837 | 900.9 | 927.8
1085 | 895 | 929.2 | 884.5 | 832.8 | 901.4 | 934.8
1086 | 896 | 929.7 | 873.8 | 822.8 | 894.8 | 935.2
1087 | 897 | 929.4 | 861.3 | 816.5 | 888.7 | 932.7
1088 | 898 | 928.8 | 866.3 | 818.8 | 889.3 | 931.7
1089 | 899 | 928.2 | 874.5 | 820.2 | 891.4 | 931.1
1090 | 900 | 927.1 | 880.7 | 827.3 | 895.1 | 936.5
1091 | 901 | 927.9 | 879.8 | 827.3 | 893.4 | 932.4
1092 | 902 | 927.3 | 871.7 | 820.6 | 889.4 | 925.1
1093 | 903 | 927.5 | 857.4 | 809.8 | 880.6 | 918.5
1094 | 904 | 927 | 861.1 | 809.5 | 877 | 912.5
1095 | 905 | 926.3 | 866.6 | 820.3 | 880.2 | 920.1
1096 | 906 | 926 | 864.7 | 828.7 | 878.5 | 921.2
1097 | 907 | 926.6 | 853.3 | 831 | 873.8 | 908.8
1098 | 908 | 927.7 | 836.9 | 820.4 | 867 | 877.5
1099 | 909 | 927 | 827 | 813.3 | 867.5 | 840.5
1100 | 910 | 925.9 | 822.6 | 803.9 | 866.7 | 852.7
1101 | 911 | 925.4 | 824.6 | 799.7 | 865.6 | 876.8
1102 | 912 | 925 | 824.7 | 790.5 | 863 | 885.6
1103 | 913 | 924.2 | 826.3 | 784.1 | 862.9 | 894.3
1104 | 914 | 923.8 | 829.5 | 787.9 | 864.5 | 903.9
1105 | 915 | 924 | 838.1 | 796.1 | 864.8 | 904.9
1106 | 916 | 923.5 | 855.2 | 806.7 | 869.8 | 908.8
1107 | 917 | 922.3 | 859.6 | 817.2 | 875.1 | 906.7
1108 | 918 | 920.7 | 863.9 | 822.1 | 881.1 | 903.2
1109 | 919 | 919.8 | 871.8 | 819.2 | 884.1 | 908.8
1110 | 920 | 919 | 872.3 | 827 | 890.1 | 915.8
1111 | 921 | 919.1 | 874.7 | 831.7 | 893.5 | 925.2
1112 | 922 | 918.5 | 877.5 | 831.4 | 893.7 | 932.5
1113 | 923 | 918.7 | 875.1 | 828.1 | 893.3 | 936.8
1114 | 924 | 918.7 | 877.5 | 832.8 | 893.2 | 931.7
1115 | 925 | 918.5 | 881.6 | 832.7 | 893.5 | 932.9
1116 | 926 | 918.5 | 887.2 | 831.5 | 893 | 932.9
1117 | 927 | 918.6 | 891.6 | 834.1 | 893.4 | 931.2
1118 | 928 | 920.6 | 888.8 | 836.9 | 891 | 924.9
1119 | 929 | 920.4 | 870.4 | 827 | 881.7 | 914.7
1120 | 930 | 919.5 | 866.2 | 829.9 | 883.5 | 910.5
1121 | 931 | 919.6 | 874 | 835.2 | 887.3 | 904.1
1122 | 932 | 920.8 | 872.4 | 829.2 | 884.4 | 905.7
1123 | 933 | 922.2 | 852.8 | 813 | 874.1 | 908.7
1124 | 934 | 922.3 | 839.9 | 804.2 | 870.7 | 912.1
1125 | 935 | 922.8 | 826.4 | 795.5 | 863.5 | 910.9
1126 | 936 | 922.3 | 829.3 | 800.2 | 862.6 | 910.6
1127 | 937 | 920.8 | 839.9 | 803.2 | 866.2 | 913.6
1128 | 938 | 918.8 | 855.2 | 803.7 | 874.2 | 914.2
1129 | 939 | 916.9 | 862.4 | 818.5 | 878.5 | 918.9
1130 | 940 | 915.7 | 869.6 | 826.5 | 882.3 | 926.4
1131 | 941 | 915.2 | 869.5 | 833.9 | 886 | 931.5
1132 | 942 | 913.9 | 872 | 840.3 | 891.8 | 931.9
1133 | 943 | 913.5 | 879.6 | 845.3 | 895.1 | 934.1
1134 | 944 | 913.2 | 883.1 | 853.8 | 898.6 | 936.2
1135 | 945 | 913.3 | 876 | 861.4 | 895.2 | 936
1136 | 946 | 913.2 | 873.8 | 864.9 | 898.9 | 925
1137 | 947 | 913.2 | 892.5 | 860.6 | 899.7 | 922.1
1138 | 948 | 912.8 | 894.9 | 859.2 | 901 | 912.9
1139 | 949 | 913.2 | 890.1 | 854.3 | 901.2 | 918.8
1140 | 950 | 913.1 | 892.6 | 850.5 | 898.3 | 924.6
1141 | 951 | 913 | 892.9 | 847.8 | 899.2 | 932.5
1142 | 952 | 913.5 | 893.5 | 854.3 | 900.6 | 934
1143 | 953 | 914.1 | 897.9 | 856.3 | 901.9 | 937.9
1144 | 954 | 914.4 | 907.1 | 855.9 | 901.6 | 936
1145 | 955 | 915 | 909.1 | 857.5 | 898.2 | 935.3
1146 | 956 | 914.9 | 908.7 | 860.8 | 900.3 | 936.9
1147 | 957 | 914.6 | 911.6 | 857 | 901.4 | 935.3
1148 | 958 | 914.3 | 911.6 | 857.3 | 899.5 | 931.7
1149 | 959 | 914.8 | 902 | 854 | 897.5 | 934.8
1150 | 960 | 915.7 | 897.2 | 852.9 | 891.5 | 933.7
1151 | 961 | 917.6 | 898 | 850.1 | 889.5 | 934.5
1152 | 962 | 919.2 | 898 | 844.6 | 886 | 937.8
1153 | 963 | 920.3 | 896 | 844.7 | 885.5 | 939
1154 | 964 | 919.6 | 890.6 | 847.4 | 889.4 | 936.8
1155 | 965 | 919.6 | 892 | 849.1 | 893.6 | 931.8
1156 | 966 | 919 | 893 | 844.7 | 894.5 | 931.7
1157 | 967 | 919.2 | 892.8 | 840.8 | 891.8 | 927.3
1158 | 968 | 919.3 | 884.9 | 832.8 | 884.3 | 923.4
1159 | 969 | 919.9 | 880.9 | 826.1 | 879.5 | 922.5
1160 | 970 | 920.6 | 877.3 | 824.7 | 877 | 929.5
1161 | 971 | 920.3 | 881.5 | 835.9 | 881.5 | 926.5
1162 | 972 | 919.7 | 883.7 | 841.6 | 887.4 | 928.9
1163 | 973 | 921.1 | 887.4 | 847.4 | 891.5 | 936.3
1164 | 974 | 921.7 | 881.9 | 838.6 | 891.9 | 931.5
1165 | 975 | 921.9 | 871.4 | 831.6 | 888 | 936.7
1166 | 976 | 922.5 | 872.9 | 831.9 | 885.7 | 938.2
1167 | 977 | 922.1 | 874.2 | 834.1 | 886.8 | 939.1
1168 | 978 | 922.1 | 873.6 | 831.5 | 890 | 942.2
1169 | 979 | 921.6 | 868.2 | 837.3 | 891.9 | 941.1
1170 | 980 | 921.9 | 869.4 | 834.1 | 891.2 | 945.4
1171 | 981 | 922 | 876.7 | 838 | 892.6 | 942.2
1172 | 982 | 923.3 | 884.2 | 837.7 | 890.7 | 943.6
1173 | 983 | 924 | 881.3 | 833.9 | 885.4 | 937.6
1174 | 984 | 923.5 | 877.6 | 832.5 | 883.1 | 938.6
1175 | 985 | 923.4 | 881.6 | 835.6 | 882.2 | 941
1176 | 986 | 924.2 | 883.9 | 840.7 | 881.7 | 936
1177 | 987 | 924.4 | 880.7 | 839.2 | 883.2 | 940.4
1178 | 988 | 925.4 | 872.3 | 837.1 | 879.8 | 936.6
1179 | 989 | 926.5 | 861.1 | 829.6 | 873.5 | 933.5
1180 | 990 | 926.4 | 859.9 | 830.3 | 873.8 | 934.5
1181 | 991 | 925.3 | 862 | 838.2 | 880.3 | 935.6
1182 | 992 | 924.4 | 866.9 | 845.6 | 884.5 | 930
1183 | 993 | 924.4 | 872.9 | 838.5 | 885.4 | 928
1184 | 994 | 926.1 | 861.4 | 826 | 877.2 | 927
1185 | 995 | 926.1 | 853.7 | 820.6 | 873.5 | 924.4
1186 | 996 | 926.3 | 848.5 | 824.8 | 873.4 | 923.7
1187 | 997 | 926.3 | 855.7 | 828.7 | 875.8 | 925.9
1188 | 998 | 925.8 | 870.7 | 829.7 | 878.6 | 928.1
1189 | 999 | 924.8 | 876.3 | 829.1 | 882.1 | 928.2
1190 | 1000 | 923.9 | 880.5 | 834.1 | 885.3 | 931.1
1191 | 1001 | 923.7 | 877.6 | 838.9 | 887.4 | 932
1192 | 1002 | 924.5 | 874.1 | 828.5 | 881 | 928.3
1193 | 1003 | 926 | 860.7 | 823.8 | 874.5 | 931.2
1194 | 1004 | 926 | 863.2 | 822.6 | 876.4 | 931.5
1195 | 1005 | 925.9 | 864.7 | 819.1 | 872.7 | 929.3
1196 | 1006 | 925.7 | 866.3 | 832 | 874.1 | 933.9
1197 | 1007 | 924.3 | 868.7 | 835.4 | 878 | 929.7
1198 | 1008 | 923.9 | 870.5 | 844 | 880.2 | 929.9
1199 | 1009 | 925.2 | 874.4 | 852.6 | 882 | 930.3
1200 | 1010 | 925.1 | 874.8 | 857 | 884.8 | 931.4
1201 | 1011 | 924.8 | 876.8 | 859.5 | 886.9 | 931.5
1202 | 1012 | 924.8 | 875.2 | 868 | 890.1 | 929.1
1203 | 1013 | 924.4 | 870.2 | 874.4 | 892.7 | 919.4
1204 | 1014 | 924.2 | 875.8 | 870.5 | 891.7 | 918.1
1205 | 1015 | 923.1 | 886.2 | 871.9 | 890.6 | 916
1206 | 1016 | 922.4 | 882.6 | 871 | 890.1 | 918.6
1207 | 1017 | 922.1 | 885.9 | 873.6 | 890.2 | 914.2
1208 | 1018 | 921.5 | 889.4 | 868.6 | 886.1 | 911.3
1209 | 1019 | 921.6 | 883.4 | 871.2 | 885.3 | 900.6
1210 | 1020 | 922.6 | 882.6 | 876.5 | 888.6 | 909
1211 | 1021 | 923.6 | 877.6 | 866 | 883.4 | 913.7
1212 | 1022 | 924.6 | 868.2 | 851.9 | 874.9 | 911.3
1213 | 1023 | 924.6 | 870.3 | 849.3 | 873.1 | 907.3
1214 | 1024 | 924.7 | 870.2 | 837.6 | 869.6 | 917.2
1215 | 1025 | 924.8 | 869.1 | 835.5 | 866.8 | 926.8
1216 | 1026 | 925.6 | 863.1 | 838.9 | 863.9 | 932.1
1217 | 1027 | 926.1 | 856.1 | 847.7 | 862 | 923
1218 | 1028 | 925 | 856.3 | 854.2 | 868.9 | 912.9
1219 | 1029 | 923.6 | 856.6 | 861.7 | 871.8 | 927.2
1220 | 1030 | 923 | 856.5 | 865 | 875.3 | 911.6
1221 | 1031 | 922.5 | 855.2 | 873.6 | 878 | 912
1222 | 1032 | 922.6 | 856.7 | 871.8 | 877.2 | 905.4
1223 | 1033 | 923 | 865.1 | 856 | 874.7 | 898
1224 | 1034 | 923.7 | 866.7 | 849.1 | 871.8 | 900.2
1225 | 1035 | 924 | 867.7 | 850.9 | 874.5 | 915.6
1226 | 1036 | 924.2 | 865.2 | 854.9 | 875.1 | 909.8
1227 | 1037 | 924.5 | 867.3 | 857.1 | 877.5 | 907.1
1228 | 1038 | 924.3 | 871.2 | 860.9 | 877.7 | 916.4
1229 | 1039 | 923.8 | 878.5 | 850.5 | 877.3 | 913.8
1230 | 1040 | 923.1 | 879.3 | 848.4 | 869.6 | 914.7
1231 | 1041 | 923.3 | 881.8 | 853.7 | 869.6 | 915.9
1232 | 1042 | 924.6 | 881.1 | 848.8 | 866.7 | 928
1233 | 1043 | 924.7 | 884.3 | 849.7 | 865.7 | 930.8
1234 | 1044 | 924.7 | 884.4 | 852.6 | 867.8 | 932.9
1235 | 1045 | 924.1 | 885.6 | 852 | 869.5 | 931.6
1236 | 1046 | 923.4 | 881.7 | 845.9 | 867.5 | 929.7
1237 | 1047 | 923.6 | 886.5 | 848.2 | 866.2 | 919.6
1238 | 1048 | 923.4 | 886.7 | 855.4 | 867.3 | 913.6
1239 | 1049 | 923.4 | 885.1 | 861.8 | 870.4 | 914.2
1240 | 1050 | 923.2 | 879.9 | 863.5 | 871.5 | 917.9
1241 | 1051 | 923 | 886.2 | 859.9 | 872.8 | 920.1
1242 | 1052 | 922.9 | 882 | 860 | 870.2 | 917.6
1243 | 1053 | 924.5 | 867.3 | 845.7 | 859.1 | 912.2
1244 | 1054 | 924.4 | 865.1 | 841.5 | 853.4 | 903.2
1245 | 1055 | 923.1 | 871.3 | 847.5 | 855.6 | 895.2
1246 | 1056 | 921.9 | 874.1 | 850 | 860.3 | 892.3
1247 | 1057 | 920.7 | 876.6 | 848.9 | 861.8 | 900
1248 | 1058 | 919.6 | 875 | 854.1 | 865.7 | 908.6
1249 | 1059 | 919.3 | 871.5 | 863 | 869.8 | 908.5
1250 | 1060 | 919 | 865.2 | 869.4 | 867.1 | 905.5
1251 | 1061 | 919 | 872.5 | 869.7 | 868 | 906.4
1252 | 1062 | 921.7 | 873.7 | 867.8 | 866.3 | 908.7
1253 | 1063 | 924.2 | 866.5 | 867.1 | 862 | 910.8
1254 | 1064 | 924.3 | 867.5 | 866.5 | 858.9 | 915.4
1255 | 1065 | 923.8 | 870.4 | 864.9 | 862.1 | 924.5
1256 | 1066 | 922.4 | 872.5 | 863.9 | 864.5 | 920.4
1257 | 1067 | 921.2 | 868 | 865.1 | 862.5 | 915.3
1258 | 1068 | 920.5 | 865.8 | 866.8 | 862.1 | 913.1
1259 | 1069 | 919.4 | 865.2 | 873.5 | 862.5 | 913.3
1260 | 1070 | 918.8 | 867.3 | 879.2 | 862.6 | 914.9
1261 | 1071 | 918.1 | 870 | 876.3 | 862.9 | 917.3
1262 | 1072 | 917.4 | 871 | 870.2 | 862 | 905.7
1263 | 1073 | 917.2 | 871.8 | 866.7 | 862.3 | 909.3
1264 | 1074 | 917.6 | 890.5 | 855.7 | 860.4 | 905.5
1265 | 1075 | 917.7 | 881.6 | 844.5 | 854.3 | 906.9
1266 | 1076 | 918.6 | 872.1 | 840.4 | 851.6 | 901
1267 | 1077 | 918.9 | 875.4 | 841.7 | 853 | 898.9
1268 | 1078 | 918.5 | 879.1 | 842.8 | 853.5 | 898.7
1269 | 1079 | 918.6 | 877.9 | 843.8 | 853.6 | 908.1
1270 | 1080 | 918.8 | 875.3 | 837.8 | 852.7 | 912.9
1271 | 1081 | 918.5 | 873.6 | 831.1 | 852.5 | 912.5
1272 | 1082 | 917.6 | 874.1 | 831.7 | 850.7 | 919
1273 | 1083 | 918.3 | 880.2 | 833 | 851.6 | 919.7
1274 | 1084 | 918.1 | 881.5 | 835.5 | 852.5 | 912.1
1275 | 1085 | 918.1 | 880.1 | 839.5 | 854.5 | 909.8
1276 | 1086 | 919 | 882.5 | 836.6 | 853.6 | 920.8
1277 | 1087 | 919.3 | 878.3 | 834.2 | 852.9 | 919.4
1278 | 1088 | 919 | 866.5 | 823.4 | 848.4 | 917.3
1279 | 1089 | 918.4 | 868.9 | 829.5 | 848.1 | 922.5
1280 | 1090 | 917.5 | 869.1 | 835.7 | 849.1 | 914.9
1281 | 1091 | 916.9 | 879.8 | 835 | 851.3 | 910.8
1282 | 1092 | 916 | 879 | 833.4 | 850.8 | 917.8
1283 | 1093 | 916 | 877.9 | 835.7 | 850.1 | 913.3
1284 | 1094 | 915.4 | 886.9 | 834.9 | 851.1 | 909.1
1285 | 1095 | 915.5 | 891.4 | 833.6 | 851.7 | 911.1
1286 | 1096 | 915.9 | 886.9 | 826.7 | 850.5 | 911.7
1287 | 1097 | 917.5 | 885.4 | 830 | 845 | 911.7
1288 | 1098 | 918 | 881.7 | 839.3 | 845.3 | 913.8
1289 | 1099 | 918.1 | 884.3 | 843 | 847.1 | 911.1
1290 | 1100 | 918 | 881.1 | 850.5 | 850.3 | 912.4
1291 | 1101 | 917.9 | 886.3 | 847.1 | 850.1 | 903
1292 | 1102 | 917.4 | 887.9 | 834.8 | 847.5 | 903.2
1293 | 1103 | 917.1 | 882.6 | 831.6 | 843.5 | 901.3
1294 | 1104 | 917.2 | 874.4 | 829 | 839.8 | 898.7
1295 | 1105 | 916.5 | 872.4 | 831.9 | 841.2 | 899.2
1296 | 1106 | 916.4 | 870.2 | 839.8 | 844.1 | 900.6
1297 | 1107 | 917 | 868.7 | 849 | 846.2 | 895.4
1298 | 1108 | 917.8 | 866.9 | 852.9 | 846.3 | 902.1
1299 | 1109 | 919.1 | 866.1 | 856.4 | 845 | 907.7
1300 | 1110 | 919.9 | 866.4 | 859.4 | 845.6 | 917.4
1301 | 1111 | 921.2 | 866.1 | 860.3 | 843.2 | 926.3
1302 | 1112 | 921.6 | 863.3 | 861.7 | 845 | 918
1303 | 1113 | 922.3 | 861.4 | 865.8 | 844.2 | 904.4
1304 | 1114 | 922.9 | 868 | 862 | 843.7 | 893.7
1305 | 1115 | 922.7 | 869.5 | 863.9 | 844.1 | 906
1306 | 1116 | 922.5 | 866.5 | 868.1 | 846.3 | 917
1307 | 1117 | 922.8 | 864.9 | 864.6 | 846 | 917.5
1308 | 1118 | 921.3 | 859.6 | 868.4 | 845.8 | 922.4
1309 | 1119 | 920.6 | 859.8 | 867 | 845.9 | 925.2
1310 | 1120 | 920.5 | 863 | 864.9 | 845.4 | 914.7
1311 | 1121 | 919.7 | 869 | 859.9 | 846.7 | 909.5
1312 | 1122 | 918.7 | 875 | 857.7 | 844.7 | 898.8
1313 | 1123 | 918.6 | 871 | 855.7 | 844 | 902.5
1314 | 1124 | 919.2 | 868.7 | 861 | 845.5 | 909.9
1315 | 1125 | 921 | 872.9 | 861.5 | 846.4 | 907.3
1316 | 1126 | 920.6 | 865.4 | 864.4 | 844.3 | 909.3
1317 | 1127 | 920.8 | 862.1 | 868.1 | 845.8 | 924.6
1318 | 1128 | 919.3 | 858.2 | 872 | 843.8 | 911.9
1319 | 1129 | 919.2 | 856.5 | 869.9 | 843.4 | 915
1320 | 1130 | 918.7 | 855.3 | 873 | 843.1 | 915.6
1321 | 1131 | 918.5 | 857 | 875.4 | 846.7 | 914.2
1322 | 1132 | 918.4 | 857 | 876.2 | 846.1 | 912.9
1323 | 1133 | 919.2 | 862.3 | 875 | 846.3 | 916.7
1324 | 1134 | 920.9 | 868.6 | 863.5 | 844.6 | 928.9
1325 | 1135 | 923.3 | 863.6 | 825.1 | 829.6 | 905.6
1326 | 1136 | 925.3 | 828.2 | 789.1 | 816.6 | 842.9
1327 | 1137 | 925.3 | 796.1 | 759 | 806.1 | 810.6
1328 | 1138 | 923.9 | 768.7 | 734.4 | 798.7 | 799.8
1329 | 1139 | 921.5 | 746.9 | 712.7 | 792.6 | 788.1
1330 | 1140 | 918 | 729.2 | 691.9 | 786.2 | 774.3
1331 | 1141 | 915.2 | 711.6 | 674.1 | 781.6 | 763.6
1332 | 1142 | 912.2 | 694.8 | 657.5 | 777 | 753.8
1333 | 1143 | 908.8 | 676.2 | 642.9 | 772 | 742.8
1334 | 1144 | 905.2 | 661.2 | 629.1 | 768.3 | 731.3
1335 | 1145 | 901.5 | 650.7 | 615.6 | 764.3 | 722.1
1336 | 1146 | 898.3 | 641.1 | 602.8 | 760.1 | 715.3
1337 | 1147 | 894.3 | 630.8 | 590.9 | 756.3 | 709.5
1338 | 1148 | 890 | 625.2 | 577.5 | 751.2 | 703.6
1339 | 1149 | 886 | 624.9 | 564.6 | 746.8 | 697
1340 | 1150 | 881.9 | 622.9 | 552.7 | 743.7 | 690.2
1341 | 1151 | 878.1 | 618.1 | 541.1 | 740.2 | 684.9
1342 | 1152 | 875.1 | 615.7 | 531 | 737 | 678.2
1343 | 1153 | 871.9 | 607.5 | 520.7 | 733.8 | 674.1
1344 | 1154 | 868.9 | 598.4 | 510.8 | 731 | 670.3
1345 | 1155 | 864.9 | 593 | 501.5 | 727.7 | 666.1
1346 | 1156 | 860.5 | 589.7 | 492.4 | 723.9 | 662.4
1347 | 1157 | 856.4 | 588.9 | 483.5 | 720 | 655.5
1348 | 1158 | 852.8 | 586.9 | 474.8 | 716.9 | 647.8
1349 | 1159 | 848.4 | 584.6 | 467.9 | 714.8 | 644.1
1350 | 1160 | 843 | 580.3 | 462.4 | 713.5 | 642.8
1351 | 1161 | 837.8 | 578.4 | 457.4 | 712.2 | 639.5
1352 | 1162 | 833.1 | 577.3 | 452.6 | 710 | 636.6
1353 | 1163 | 828.3 | 574.6 | 447.3 | 708.2 | 634.2
1354 | 1164 | 823.7 | 570 | 442.1 | 706.4 | 632.1
1355 | 1165 | 819.4 | 568.6 | 436.2 | 704.3 | 629.2
1356 | 1166 | 815.2 | 566.5 | 430.7 | 702.5 | 626.9
1357 | 1167 | 811.1 | 563.2 | 426.2 | 700.8 | 623.7
1358 | 1168 | 807.3 | 561.6 | 421.3 | 698.8 | 619.6
1359 | 1169 | 803.4 | 559.9 | 416.3 | 696.3 | 617.2
1360 | 1170 | 799.8 | 559 | 411.7 | 693.4 | 615.6
1361 | 1171 | 796.1 | 556.6 | 407 | 690.8 | 613
1362 | 1172 | 792.6 | 555 | 402.2 | 688.6 | 610.1
1363 | 1173 | 789.2 | 552.1 | 397.8 | 686.1 | 608
1364 | 1174 | 786 | 549.5 | 393 | 683.4 | 604.7
1365 | 1175 | 782.7 | 546 | 388.5 | 680.3 | 602.2
1366 | 1176 | 779.5 | 541.8 | 384.7 | 677.1 | 599.9
1367 | 1177 | 776.4 | 538.7 | 381.1 | 674.1 | 598.2
1368 | 1178 | 773.3 | 533.6 | 376.6 | 671 | 596.1
1369 | 1179 | 770.4 | 527.1 | 371.9 | 667.6 | 594.9
1370 | 1180 | 767.5 | 524.2 | 367.5 | 665.1 | 594
1371 | 1181 | 764.6 | 519.1 | 363.1 | 662.7 | 591.8
1372 | 1182 | 761.5 | 508.1 | 359.1 | 659.9 | 590.9
1373 | 1183 | 758.7 | 501.9 | 354.7 | 656.6 | 589
1374 | 1184 | 756.1 | 504.3 | 350 | 654 | 587.1
1375 | 1185 | 753.3 | 504.7 | 345.1 | 651.1 | 584.6
1376 | 1186 | 750.7 | 506.8 | 340.6 | 648.6 | 579.4
1377 | 1187 | 748.2 | 506.8 | 336.2 | 645.5 | 575
1378 | 1188 | 745.8 | 506.3 | 331.8 | 642.4 | 568.4
1379 | 1189 | 743.6 | 504.7 | 327.6 | 639.2 | 562.4
1380 | 1190 | 741.2 | 501.6 | 323.1 | 636.9 | 560.7
1381 | 1191 | 738.8 | 500.4 | 318.9 | 634.7 | 561.1
1382 | 1192 | 736.2 | 499.7 | 315.3 | 633.3 | 562
1383 | 1193 | 733.6 | 497.5 | 312.1 | 631.1 | 562.2
1384 | 1194 | 731.2 | 495.3 | 308.8 | 629.5 | 561.8
1385 | 1195 | 728.7 | 494.1 | 305.3 | 627.1 | 560.2
1386 | 1196 | 726.2 | 492 | 302.3 | 625.5 | 560.1
1387 | 1197 | 723.7 | 491.9 | 299.3 | 623.5 | 560
1388 | 1198 | 721.4 | 491.6 | 295.6 | 621.5 | 559.2
1389 | 1199 | 718.8 | 489.7 | 292.5 | 619.7 | 558.7
1390 | 1200 | 716.4 | 486.3 | 289.2 | 616.4 | 557.2
1391 | 1201 | 714 | 485.6 | 286.1 | 613.5 | 556.5
1392 | 1202 | 711.8 | 485 | 282.4 | 609.2 | 557.6
1393 | 1203 | 710 | 480.9 | 279.3 | 605.1 | 558.7
1394 | 1204 | 708 | 478.7 | 276.8 | 603.3 | 559.1
1395 | 1205 | 705.8 | 473.5 | 273.8 | 600.8 | 559.8
1396 | 1206 | 703.8 | 471.2 | 270.7 | 597.6 | 560
1397 | 1207 | 701.8 | 470.9 | 268 | 594.5 | 560.3
1398 | 1208 | 699.9 | 470.9 | 265.1 | 591.4 | 560.9
1399 | 1209 | 698 | 469.6 | 262.3 | 588.2 | 561.5
1400 | 1210 | 696.1 | 469.2 | 259.3 | 586 | 562.2
1401 | 1211 | 694.2 | 468.7 | 257.1 | 583.7 | 563.2
1402 | 1212 | 692.2 | 465.3 | 254.2 | 579.9 | 563.8
1403 | 1213 | 690.5 | 464.1 | 251.4 | 577.8 | 564.1
1404 | 1214 | 688.5 | 462.2 | 249.3 | 577.7 | 564
1405 | 1215 | 686.4 | 458.3 | 247.4 | 576.9 | 564.4
1406 | 1216 | 684.3 | 459.5 | 245.5 | 576.3 | 566.1
1407 | 1217 | 682.3 | 456.2 | 243.2 | 575.3 | 566.8
1408 | 1218 | 680.3 | 452.2 | 241.1 | 573.9 | 565.6
1409 | 1219 | 678.4 | 450.4 | 238.8 | 572.3 | 566.5
1410 | 1220 | 676.8 | 447.8 | 236.6 | 570.8 | 567.2
1411 | 1221 | 674.8 | 447.1 | 234.4 | 569.7 | 567.9
1412 | 1222 | 672.6 | 444.6 | 232.5 | 568.6 | 567.5
1413 | 1223 | 670.3 | 442.6 | 230.5 | 567.1 | 568.1
1414 | 1224 | 668 | 437.2 | 228 | 564.8 | 569.8
1415 | 1225 | 665.7 | 429.2 | 225.5 | 562.3 | 569.9
1416 | 1226 | 663.7 | 426.7 | 223.2 | 560.1 | 569.8
1417 | 1227 | 661.8 | 428.9 | 220.9 | 558.2 | 571
1418 | 1228 | 659.8 | 428.2 | 218.9 | 556.3 | 572.9
1419 | 1229 | 657.9 | 425.4 | 217.1 | 554.7 | 573.9
1420 | 1230 | 655.9 | 422.9 | 215.1 | 553.1 | 574.9
1421 | 1231 | 653.8 | 419.8 | 212.8 | 551.5 | 576.1
1422 | 1232 | 651.8 | 418 | 210.7 | 549.7 | 576.9
1423 | 1233 | 649.8 | 418.8 | 208.6 | 547.7 | 577.6
1424 | 1234 | 647.9 | 416.9 | 206.4 | 545.4 | 578.9
1425 | 1235 | 645.8 | 414.1 | 204.1 | 542.7 | 579.6
1426 | 1236 | 643.8 | 414.4 | 202.1 | 539.5 | 581.1
1427 | 1237 | 641.9 | 414.9 | 200.3 | 536.8 | 581.7
1428 | 1238 | 639.8 | 416.1 | 198.4 | 534.8 | 583.1
1429 | 1239 | 637.6 | 414.2 | 196.2 | 532.9 | 584.8
1430 | 1240 | 635.5 | 412.5 | 194.4 | 531.8 | 585.4
1431 | 1241 | 633.4 | 414.3 | 192.7 | 530.2 | 586.6
1432 | 1242 | 631.4 | 410.8 | 191.4 | 528.7 | 587.5
1433 | 1243 | 629.3 | 409.9 | 189.4 | 526.9 | 588.9
1434 | 1244 | 627.4 | 411.9 | 187.4 | 523.3 | 590.9
1435 | 1245 | 625.6 | 411.4 | 185.6 | 520.9 | 591.8
1436 | 1246 | 623.8 | 407.8 | 184.3 | 519.7 | 592.7
1437 | 1247 | 621.8 | 403.3 | 183.3 | 518.5 | 593.7
1438 | 1248 | 619.7 | 399.8 | 181.6 | 517.4 | 594.6
1439 | 1249 | 617.5 | 399.2 | 180.3 | 516.9 | 594.4
1440 | 1250 | 615.3 | 397.8 | 178.9 | 516.2 | 595.9
1441 | 1251 | 613 | 395.2 | 177.3 | 515.2 | 596.9
1442 | 1252 | 610.8 | 395.9 | 175.5 | 513.5 | 597.9
1443 | 1253 | 608.7 | 396.6 | 173.8 | 512 | 598.6
1444 | 1254 | 606.5 | 393.6 | 172.8 | 509.5 | 600.6
1445 | 1255 | 604.5 | 394 | 171 | 506.1 | 602.4
1446 | 1256 | 602.4 | 393.1 | 168.9 | 502.4 | 603.5
1447 | 1257 | 600.4 | 389.9 | 167.3 | 500.1 | 603.7
1448 | 1258 | 598.4 | 388 | 166 | 498.2 | 602.7
1449 | 1259 | 596.4 | 387.1 | 164.5 | 495.9 | 604.7
1450 | 1260 | 594.4 | 386.9 | 163.1 | 494.2 | 606
1451 | 1261 | 592.4 | 383.2 | 161.4 | 492 | 608.6
1452 | 1262 | 590.4 | 380.8 | 159.5 | 489 | 610.8
1453 | 1263 | 588.4 | 378.7 | 157.8 | 486.6 | 612.1
1454 | 1264 | 586.4 | 377.9 | 156.3 | 485.2 | 614.3
1455 | 1265 | 584.5 | 376.6 | 155 | 484.2 | 616.8
1456 | 1266 | 582.5 | 373 | 153.7 | 483.2 | 618.7
1457 | 1267 | 580.7 | 371.3 | 152.5 | 480.5 | 620.2
1458 | 1268 | 578.8 | 368.5 | 151.3 | 478.3 | 622.2
1459 | 1269 | 577 | 367.1 | 149.8 | 476.2 | 623.9
1460 | 1270 | 575.2 | 365.5 | 148.3 | 473.6 | 625.9
1461 | 1271 | 573.5 | 362.6 | 146.9 | 470.6 | 627.2
1462 | 1272 | 571.8 | 361.8 | 145.8 | 468.1 | 628.7
1463 | 1273 | 570.1 | 357.5 | 144.5 | 465.3 | 628.8
1464 | 1274 | 568.2 | 355.3 | 143.2 | 462 | 630.5
1465 | 1275 | 566.5 | 353.5 | 142.3 | 459.7 | 632
1466 | 1276 | 564.7 | 352.3 | 141.3 | 457.1 | 633
1467 | 1277 | 562.9 | 348.8 | 140 | 454.8 | 635
1468 | 1278 | 560.9 | 346.2 | 138.9 | 452.4 | 636
1469 | 1279 | 558.9 | 343.6 | 137.8 | 449.3 | 637.7
1470 | 1280 | 557.1 | 343.4 | 136.9 | 446.2 | 639.9
1471 | 1281 | 555.3 | 343.7 | 136.1 | 443 | 641.7
1472 | 1282 | 553.6 | 340.1 | 135.2 | 440.8 | 642.6
1473 | 1283 | 551.8 | 336.2 | 134.3 | 437.8 | 645
1474 | 1284 | 550.1 | 334.4 | 133.4 | 435.4 | 647.2
1475 | 1285 | 548.4 | 334.9 | 132.5 | 432.6 | 648.1
1476 | 1286 | 546.7 | 333.4 | 131.6 | 429.6 | 649.7
1477 | 1287 | 545 | 329.6 | 130.9 | 426.9 | 651.2
1478 | 1288 | 543.3 | 328 | 130.3 | 423.9 | 652.2
1479 | 1289 | 541.5 | 327.7 | 129.6 | 420.9 | 653.8
1480 | 1290 | 539.7 | 328 | 128.6 | 418.7 | 654.9
1481 | 1291 | 538 | 327.1 | 127.4 | 416.8 | 655.8
1482 | 1292 | 536.2 | 325.5 | 126.4 | 414.6 | 657.5
1483 | 1293 | 534.4 | 325.1 | 125.8 | 413.1 | 657.7
1484 | 1294 | 532.6 | 325.1 | 125.2 | 411.9 | 658.2
1485 | 1295 | 530.9 | 324.7 | 124.4 | 409.3 | 660.2
1486 | 1296 | 529 | 322.7 | 123.7 | 407.1 | 661.9
1487 | 1297 | 527.2 | 319.3 | 123.2 | 404.5 | 662.9
1488 | 1298 | 525.3 | 318.5 | 122.5 | 401 | 665.9
1489 | 1299 | 523.5 | 317.9 | 121.8 | 398.6 | 667.4
1490 | 1300 | 521.6 | 318.3 | 121.2 | 396.5 | 667.5
1491 | 1301 | 519.8 | 317 | 120.5 | 394.6 | 667.6
1492 | 1302 | 518 | 316.6 | 119.6 | 392.6 | 669.4
1493 | 1303 | 516.3 | 317.3 | 118.6 | 390.9 | 671.9
1494 | 1304 | 514.6 | 316 | 117.9 | 388.6 | 672.9
1495 | 1305 | 512.9 | 313.8 | 117.2 | 386.4 | 673.6
1496 | 1306 | 511.1 | 314.9 | 116.5 | 384.2 | 675.8
1497 | 1307 | 509.3 | 314.9 | 116.1 | 382.2 | 678
1498 | 1308 | 507.4 | 313 | 115.5 | 379.8 | 680.2
1499 | 1309 | 505.5 | 311.1 | 115.1 | 376.8 | 683.3
1500 | 1310 | 503.7 | 308.3 | 114.5 | 374.8 | 685.5
1501 | 1311 | 501.8 | 306.5 | 113.8 | 372.5 | 688.1
1502 | 1312 | 500.1 | 304.4 | 113.3 | 370.7 | 689.6
1503 | 1313 | 498.1 | 302.9 | 112.9 | 368.5 | 691.2
1504 | 1314 | 496.1 | 301 | 112.5 | 365.6 | 693.6
1505 | 1315 | 494.2 | 300.8 | 112.1 | 362.7 | 694.9
1506 | 1316 | 492.2 | 301.4 | 111.8 | 360.4 | 695.8
1507 | 1317 | 490.2 | 301 | 111.6 | 358.1 | 698.4
1508 | 1318 | 488.3 | 300 | 111.2 | 356.3 | 701
1509 | 1319 | 486.3 | 299.3 | 110.8 | 354.4 | 703.7
1510 | 1320 | 484.4 | 297.4 | 110.4 | 352.2 | 705.8
1511 | 1321 | 482.4 | 298.5 | 109.9 | 350.4 | 707.3
1512 | 1322 | 480.5 | 298.6 | 109.5 | 349.7 | 708
1513 | 1323 | 478.4 | 298.5 | 108.8 | 348 | 708.2
1514 | 1324 | 476.4 | 298.7 | 107.9 | 345.3 | 710.4
1515 | 1325 | 474.3 | 299.5 | 107.3 | 343.7 | 712
1516 | 1326 | 472.3 | 297.8 | 106.9 | 341.2 | 714.3
1517 | 1327 | 470.3 | 298.2 | 106.3 | 338.2 | 715.9
1518 | 1328 | 468.2 | 297.7 | 105.8 | 336.3 | 717
1519 | 1329 | 466.3 | 297.3 | 105.2 | 333.9 | 718.2
1520 | 1330 | 464.3 | 296.5 | 104.6 | 331.6 | 720.7
1521 | 1331 | 462.4 | 294.9 | 104 | 330.6 | 722.8
1522 | 1332 | 460.5 | 292.8 | 103.6 | 328.5 | 723.5
1523 | 1333 | 458.2 | 291.7 | 102.9 | 325.8 | 724.4
1524 | 1334 | 456.1 | 291.8 | 102.4 | 324.7 | 726
1525 | 1335 | 454 | 292.3 | 101.9 | 323.5 | 728.3
1526 | 1336 | 452 | 292 | 101.5 | 321.9 | 729.6
1527 | 1337 | 450.1 | 291.4 | 101.1 | 321.4 | 729.4
1528 | 1338 | 448.2 | 290.3 | 100.6 | 320.8 | 729.4
1529 | 1339 | 446.3 | 289.2 | 100.2 | 318.4 | 730.7
1530 | 1340 | 444.3 | 288.3 | 99.8 | 316.5 | 732.7
1531 | 1341 | 442.4 | 287.6 | 99.5 | 316 | 733.6
1532 | 1342 | 440.5 | 287.6 | 98.9 | 315.1 | 734.5
1533 | 1343 | 438.6 | 286.9 | 98.3 | 313 | 735.7
1534 | 1344 | 436.7 | 286.5 | 97.7 | 311.7 | 736.4
1535 | 1345 | 434.7 | 286.8 | 97.4 | 310.6 | 737.5
1536 | 1346 | 432.8 | 286.2 | 97.3 | 309.7 | 738.1
1537 | 1347 | 430.8 | 282 | 97.2 | 309 | 739.9
1538 | 1348 | 428.9 | 277.7 | 96.9 | 308.6 | 741.3
1539 | 1349 | 426.9 | 275.8 | 96.5 | 307.2 | 742.6
1540 | 1350 | 424.9 | 275.5 | 96.2 | 305.8 | 745
1541 | 1351 | 422.9 | 275.6 | 95.8 | 304.1 | 746.8
1542 | 1352 | 420.9 | 275.3 | 95.5 | 302.6 | 748.2
1543 | 1353 | 418.9 | 274.3 | 95.1 | 301.1 | 750
1544 | 1354 | 416.9 | 272.8 | 94.5 | 299.9 | 751.4
1545 | 1355 | 415 | 271.2 | 94 | 298.4 | 752.9
1546 | 1356 | 412.9 | 271.5 | 93.6 | 296.9 | 753.4
1547 | 1357 | 410.9 | 270.1 | 93.3 | 296 | 751.5
1548 | 1358 | 408.9 | 269.9 | 93 | 295.3 | 751.1
1549 | 1359 | 406.9 | 268.4 | 92.8 | 294.5 | 753.2
1550 | 1360 | 404.8 | 267.7 | 92.3 | 293.2 | 755.5
1551 | 1361 | 402.6 | 266.6 | 92 | 292.5 | 758
1552 | 1362 | 400.5 | 266.6 | 91.5 | 291.5 | 760.4
1553 | 1363 | 398.4 | 266.2 | 91.3 | 289.4 | 762.6
1554 | 1364 | 396.2 | 265.1 | 91 | 287.5 | 764.8
1555 | 1365 | 393.9 | 262 | 90.8 | 284.1 | 766.7
1556 | 1366 | 391.6 | 262.4 | 90.5 | 282.5 | 766.4
1557 | 1367 | 389.5 | 262.1 | 90.1 | 281.5 | 768.1
1558 | 1368 | 387.4 | 258.7 | 89.7 | 279.4 | 769.5
1559 | 1369 | 385.3 | 256 | 89.1 | 278.7 | 768.2
1560 | 1370 | 383.2 | 256.1 | 88.9 | 277.3 | 769
1561 | 1371 | 381 | 255.8 | 88.6 | 276.5 | 770.2
1562 | 1372 | 378.9 | 250.2 | 88.1 | 275.7 | 771.8
1563 | 1373 | 376.8 | 245.3 | 87.7 | 274.7 | 774.3
1564 | 1374 | 374.6 | 244.7 | 87.4 | 273.8 | 773
1565 | 1375 | 372.5 | 243 | 86.9 | 273.1 | 773
1566 | 1376 | 370.4 | 242.8 | 86.5 | 271.9 | 774.4
1567 | 1377 | 368.3 | 241.9 | 86.1 | 270.6 | 775.2
1568 | 1378 | 366.2 | 238.6 | 85.9 | 270 | 777
1569 | 1379 | 364.1 | 237.2 | 85.7 | 269.7 | 777.6
1570 | 1380 | 362.1 | 236.7 | 85.5 | 268.7 | 777.1
1571 | 1381 | 360 | 236.9 | 85.1 | 267.9 | 776.7
1572 | 1382 | 358 | 235.9 | 84.8 | 267.3 | 778
1573 | 1383 | 356 | 233.4 | 84.7 | 267.1 | 779.8
1574 | 1384 | 354 | 230.8 | 84.5 | 266.9 | 781.4
1575 | 1385 | 352 | 225.8 | 84.3 | 266.3 | 782.8
1576 | 1386 | 349.9 | 223 | 84.2 | 264.6 | 783.8
1577 | 1387 | 347.9 | 221.5 | 83.9 | 264.2 | 784.3
1578 | 1388 | 345.8 | 221.7 | 83.6 | 263.6 | 785.1
1579 | 1389 | 343.5 | 221.5 | 83.3 | 262 | 786.8
1580 | 1390 | 341.3 | 222.7 | 83.3 | 261.1 | 789.2
1581 | 1391 | 339.2 | 223.3 | 83.3 | 260.2 | 791.1
1582 | 1392 | 337.1 | 222.1 | 83.2 | 259.1 | 791.9
1583 | 1393 | 335 | 221 | 83 | 257.4 | 794.7
1584 | 1394 | 333 | 221.8 | 82.7 | 255.9 | 797.5
1585 | 1395 | 331 | 222.9 | 82.6 | 254.1 | 799.5
1586 | 1396 | 329.1 | 222.8 | 82.2 | 253.1 | 800.2
1587 | 1397 | 327.2 | 222.3 | 82 | 252.5 | 801.5
1588 | 1398 | 325.4 | 221.7 | 81.8 | 251.3 | 802.8
1589 | 1399 | 323.5 | 222.5 | 81.5 | 249.3 | 805.1
1590 | 1400 | 321.6 | 223.5 | 81.1 | 248.9 | 805.9
1591 | 1401 | 319.8 | 224 | 80.7 | 247.6 | 805.7
1592 | 1402 | 317.9 | 223.2 | 80.5 | 246.7 | 806.5
1593 | 1403 | 316 | 222.9 | 80.3 | 246.4 | 806.9
1594 | 1404 | 314.1 | 222.9 | 80 | 246 | 807.2
1595 | 1405 | 312.3 | 222.5 | 79.6 | 245 | 808.7
1596 | 1406 | 310.5 | 222.1 | 79.2 | 244.2 | 810.6
1597 | 1407 | 308.7 | 219.2 | 78.9 | 243.3 | 812.8
1598 | 1408 | 306.8 | 216.6 | 78.8 | 242.1 | 814.1
1599 | 1409 | 304.9 | 216.6 | 78.6 | 241.6 | 815
1600 | 1410 | 303 | 215.9 | 78.5 | 240.7 | 816.7
1601 | 1411 | 301 | 215.9 | 78.2 | 239.8 | 818.3
1602 | 1412 | 298.9 | 217.1 | 78 | 238.4 | 820
1603 | 1413 | 296.9 | 217.7 | 77.7 | 237.1 | 821.9
1604 | 1414 | 294.9 | 217.9 | 77.6 | 236.3 | 822.2
1605 | 1415 | 292.9 | 217.7 | 77.3 | 235.9 | 822.9
1606 | 1416 | 290.9 | 217.4 | 77.2 | 235.6 | 824
1607 | 1417 | 289 | 217.3 | 77 | 234.9 | 824.6
1608 | 1418 | 287.1 | 216.2 | 76.8 | 234.1 | 825.5
1609 | 1419 | 285.2 | 215 | 76.5 | 233.9 | 827.2
1610 | 1420 | 283.3 | 214.6 | 76.4 | 232.9 | 829.2
1611 | 1421 | 281.3 | 213.5 | 76.1 | 232.1 | 830.4
1612 | 1422 | 279.4 | 213.7 | 76.1 | 231.8 | 832.1
1613 | 1423 | 277.6 | 214.3 | 76.1 | 231.6 | 833.2
1614 | 1424 | 275.8 | 213.7 | 75.8 | 231.6 | 834.8
1615 | 1425 | 274.1 | 212.7 | 75.5 | 231 | 835.1
1616 | 1426 | 272.4 | 209.1 | 75.3 | 231 | 834.9
1617 | 1427 | 270.8 | 206.7 | 75.1 | 231.1 | 835.1

## Test Facts
Last row in IRMS data sheets: | 43
Time when gas burner was ignited: | 190