## IS Test Matrix
Intermediate Scale Test Matrix - Revision F (12-06-06)
|  | Comments: 1) All tests were conducted as open burns with a Propene (Propylene) gas sand burner 2) Colors identify test conditions grouped into the same test run | [14 empty] | ACTUAL TEST CONDITIONS
Burn Test # | Rev. E Test # | Loc. | Cable Insulation Material | [8 empty] | Number of Conductors |  |  |  | Conductor Size (AWG) |  |  |  |  | Cable Bundle Size |  |  |  |  | Water Spary Optionsl | Raceway Type
|  |  | Thermoset | [5 empty] | Thermoplastic
|  |  | XLPE | EPR | Silicone | XLPO | TS/TP | Vita-Link | PE | PVC | Tefzel | 3 | 2 | 7 | 12 | 8 | 12 | 14 | 16 | 18 | 1 | 3 | 6 | 12 | Load Tr | * | 12" Tray | 2.5" Cnd | Air Drop
Prelim 1 | Prelim 1 | A | X | [8 empty] | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | A | X | [10 empty] | X |  |  | X |  |  |  | X | [5 empty] | X
Prelim 2 | Prelim 2 | A | X | [8 empty] | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | A | X | [10 empty] | X |  |  | X |  |  |  | X | [5 empty] | X
Prelim 3 | Prelim 3 | A | [7 empty] | X |  | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | A | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [5 empty] | X
Prelim 4 | Prelim 4 | A | [7 empty] | X |  | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | A | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [5 empty] | X
1 | 15 | A | X | [9 empty] | X | X | X |  | X |  | X | X |  |  |  |  | X |  | X
|  | B | X | [10 empty] | X |  |  | X | [6 empty] | X |  |  | X
|  | D | X | [10 empty] | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | E | X | [10 empty] | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | [10 empty] | X |  |  | X | [6 empty] | X |  |  | X
2 | 1 | A | X | [10 empty] | X |  |  | X | [6 empty] | X |  |  | X
|  | C | X | [10 empty] | X |  |  | X | [5 empty] | X |  |  |  | X
|  | A | X | [5 empty] | X |  |  |  |  | X |  |  | X | [6 empty] | X |  |  | X
|  | C | X | [5 empty] | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
| 11 | C - A | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [7 empty] | X
|  | E | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [5 empty] | X
|  | G | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [5 empty] | X
3 | 2 | A | X | X | [9 empty] | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X | [9 empty] | X |  |  | X | [5 empty] | X |  |  |  | X
| 3 | A |  | X |  |  |  |  | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C |  | X |  |  |  |  | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
| 10 | E | [7 empty] | X |  | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | [7 empty] | X |  | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
4 | 5 | A | X | X |  | X | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X |  | X | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
| 6 | A | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
| 9 | C - A | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [7 empty] | X
|  | E | X | [8 empty] | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | [8 empty] | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
5 | 4 | A | X | X | X | X |  |  | X |  | X |  |  | X |  |  | X | [6 empty] | X |  | X | X
|  | C | X | X | X | X |  |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
| 7 | A | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | X | [5 empty] | X |  | X | X
|  | C | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | X |  |  |  |  | X |  |  | X | X
|  | C - A | X | [10 empty] | X |  |  | X |  |  |  | X | [7 empty] | X
|  | E |  | X | [9 empty] | X |  |  | X |  |  |  | X | [5 empty] | X
|  | G |  | X | [9 empty] | X |  |  | X |  |  |  | X | [5 empty] | X
6 | 12 | A | X | X | X | X |  |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | C | X | X | X | X |  |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | E | X | [5 empty] | X |  | X |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
| 13 | C - A | X | [5 empty] | X |  | X |  |  | X |  |  | X |  |  |  |  | X | [6 empty] | X
|  | A |  | X | X | X | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | C |  | X | X | X | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | G |  |  |  |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  |  |  | X
7 | 14 | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | A | X | X |  | X | X |  |  | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C |  | X |  | X | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | E | X | [5 empty] | X | X |  |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G |  | X |  | X | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
8 | 16 | A | X | [5 empty] | X | X |  |  | X | X | X |  | X |  | X | X |  |  | X |  |  |  | X
|  | A | X | [5 empty] | X | X |  |  | X | X | X |  | X |  | X | X |  |  | X |  |  |  | X
|  | C | X | [5 empty] | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | E | X | [5 empty] | X |  |  |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | [5 empty] | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
9 | 19 | A | X | X | X |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | A | X | X | X |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | C | X | X | X |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | E | X | [5 empty] | X |  | X |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | X | X |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
10 | 20 | A | X | X | X | X | X |  |  |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | A | X | X | X | X | X |  |  |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | C | X | X | X | X | X |  |  | X |  |  |  | X | X |  | X |  |  | X |  |  | X |  |  | X | X
|  | E |  |  |  |  | X |  | X |  | X |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | X |  |  | X |  | X | X | X |  | X | X |  |  | X |  | X |  |  |  | X |  |  |  | X
11 | 21 | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X |  | X | X |  |  | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | E |  |  |  |  | X |  | X | X |  |  |  | X |  |  | X |  |  |  |  | X | [6 empty] | X
|  | G | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
12 | 24 | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X |  | X | X |  |  | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | E |  |  |  |  | X |  | X | X |  |  |  | X |  |  | X |  |  |  |  | X | [6 empty] | X
|  | G | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
13 | 25 | A | X | X |  | X | X | X | X |  | X |  |  | X |  |  | X | [7 empty] | X | X | X
|  | C | X | X |  | X | X | X | X |  | X |  |  | X |  |  | X | [7 empty] | X | X | X
|  | E | X | X | [9 empty] | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | F | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | F | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | G | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | G | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
14 | 27 | A | X | X |  | X | X |  | X | X | X |  |  | X |  |  | X | [7 empty] | X |  | X
|  | C | X | X |  | X | X |  | X | X | X |  |  | X |  |  | X | [7 empty] | X |  | X
|  | E |  |  |  |  | X |  | X | X |  |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | F | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | F | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | G | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | G | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X

## Shorting Summary
Shorting Sequence for Open Burn Test 12, Location C, IRMS #2
Test conditions: Cable: Bundle of 6, 7-conductor, 12 AWG, Tefzel, XLPO, EPR, XLPE, PVC, & TS/TP control cables (Items 12, 8, 2, 10, 1 & 3). Cable specimens present: Three lengths of cable were monitored for electrical performance (A, B & C [See Elect. Conn. Map]), a second bundle of 6 cables was monitored for temperature response. Raceway: 12" B-Line Series 2 tray (part number 248P09-12-144) located at position C in the Test Cell chamber with chamber end walls open and un-heated. Exposure conditions: Gas burner flow rate set to a nominal 250 kW heat release rate, increased to 300 kW during the test run. Electrical repsonse monitoring: IRMS system using 6 channels - two for each cable (see electrical connection map), cable tray was grounded. Thermal response monitoring: Two cable bundle temperatures (see thermocouple map), air temperatures above and below the cable bundle, and the cable tray rung temperature. Gas burner initiated: Following 190 seconds of baseline data monitoring. Special Note: This test run was intended to be a repeat of Test #11.
DAQ Time | Burner Time | Event | Interpretation
190 | 0 | Ignited Gas Burner
463 | 273 | Conductors A1 & A2 short together at less than 100 ohms (61) [Erratic shorting behavior noted] | Cable A shorts internally
510-519 | 320-329 | Conductors A1 & A2 both short to ground (226 & 74) | Cable A shorted to ground
525-528 | 335-338 | Conductors B3 & B4 both short to ground (167 & 80) | Cable B shorted to ground
552-567 | 362-377 | The existing ground faults on conductors A1 & B3 decrease to less than 100 ohms (66 & 67)
572 | 382 | Conductors B3 & B4 short together at less than 1000 ohms (265) [Erratic shorting behavior noted] | Cable B shorts internally
572-574 | 382-384 | Conductors C5 & C6 both short to ground (314 & 52) | Cable C shorted to ground
586 | 396 | Conductors C5 & C6 short together at less than 1000 ohms (313) | Cable C shorts internally
614 | 424 | The existing ground fault on conductor C5 decreases to less than 100 ohms (32)
617 | 427 | The existing internal short between conductors B3 & B4 decreases to less than 100 ohms (53) [Erratic shorting behavior still occurring]
628 | 438 | The existing internal short between conductors C5 & C6 decreases to less than 100 ohms (68) but is erratic in nature
1323 | 1133 | Gas burner is shut off
Additional Observations
Observation 1 | Some erratic internal shorting behavior was noted.
Observation 2 | There was no evidence of cable-to-cable interactions prior to internal cable shorting or shorting to ground.

## Thermocouple Map
Thermocouple map for TC's on and within the cable
|  |  |  | Cable A = | TEFZEL | (Item #12)
|  |  |  | Cable B = | XLPO | (Item #8)
|  |  |  | Cable C = | EPR | (Item #2)
|  |  |  | Cable D = | XLPE | (Item #10)
|  |  |  | Cable E = | PVC | (Item #1)
|  |  |  | Cable F = | TS/TP | (Item #3)
Translation to data file names used in "Temperatures" WorkSheet:
| Map Name |  | Location
| C1 | = | Center of bundle, under jacket
| C2 | = | Air above bundle
| C3 | = | Air below bundle
| C4 | = | Intra-bundle, center

## Elect Conn Map
Electrical connection map within the cables
|  |  |  | Cable A = | TEFZEL | (Item #12)
|  |  |  | Cable B = | XLPO | (Item #8)
|  |  |  | Cable C = | EPR | (Item #2)
Tray rung under D-E-F
Cable Bundle Arrangement
Cable 7-Conductor Arrangement
| Lt Blue = | Even conductor set
| Lt Red = | Odd conductor set
| Gray = | Center conductor (not connected)
IRMS Electrical Connections

## C-C Individuals
Conductor to Conductor Resistances
Open Burn Test 12 |  |  | 2006-11-22 | 13:02
Mixed | 7-C | Tray C | IRMS | 2
0 | 250 kW
Burner Time | A1-A2 | Burner Time | A1-B3 | Burner Time | A1-B4 | Burner Time | A1-C5 | Burner Time | A1-C6 | Burner Time | A2-B3 | Burner Time | A2-B4 | Burner Time | A2-C5 | Burner Time | A2-C6 | Burner Time | B3-B4 | Burner Time | B3-C5 | Burner Time | B3-C6 | Burner Time | B4-C5 | Burner Time | B4-C6 | Burner Time | C5-C6
-189.5 | 524775.9997 | -186.5 | 522375.9997 | -184 | 517575.9997 | -181 | 524775.9997 | -178.5 | 523975.9997 | -175.5 | 517575.9997 | -172.5 | 525575.9997 | -170 | 526375.9997 | -167.5 | 520975.9997 | -164.5 | 521175.9997 | -161.5 | 518375.9997 | -159 | 516975.9997 | -156 | 518575.9997 | -153.5 | 518975.9997 | -150.5 | 517775.9997
-147.5 | 524775.9997 | -144.5 | 522375.9997 | -142 | 517575.9997 | -139.5 | 524775.9997 | -136.5 | 523975.9997 | -133.5 | 517575.9997 | -130.5 | 525575.9997 | -128 | 526375.9997 | -125 | 520975.9997 | -122.5 | 521175.9997 | -119.5 | 518375.9997 | -116.5 | 516975.9997 | -114 | 518575.9997 | -111.5 | 518975.9997 | -108.5 | 517775.9997
-105.5 | 524775.9997 | -103 | 522375.9997 | -100 | 517575.9997 | -97.5 | 524775.9997 | -94.5 | 523975.9997 | -91.5 | 517575.9997 | -89 | 525575.9997 | -86 | 526375.9997 | -83.5 | 520975.9997 | -80.5 | 521175.9997 | -77.5 | 518375.9997 | -74.5 | 516975.9997 | -72 | 518575.9997 | -69 | 518975.9997 | -66.5 | 517775.9997
-63.5 | 524775.9997 | -61 | 522375.9997 | -58 | 517575.9997 | -55.5 | 524775.9997 | -52.5 | 523975.9997 | -49.5 | 517575.9997 | -47 | 525575.9997 | -44 | 526375.9997 | -41 | 520975.9997 | -38.5 | 521175.9997 | -35.5 | 518375.9997 | -33 | 516975.9997 | -30 | 518575.9997 | -27.5 | 518975.9997 | -24.5 | 517775.9997
-21.5 | 524775.9997 | -19 | 522375.9997 | -16 | 517575.9997 | -13.5 | 524775.9997 | -10.5 | 523975.9997 | -7.5 | 517575.9997 | -4.5 | 525575.9997 | -2 | 526375.9997 | 1 | 520975.9997 | 3.5 | 521175.9997 | 6.5 | 518375.9997 | 9.5 | 516975.9997 | 12 | 518575.9997 | 15 | 518975.9997 | 17.5 | 517775.9997
20.5 | 524775.9997 | 23.5 | 522375.9997 | 26 | 517575.9997 | 29 | 524775.9997 | 31.5 | 523975.9997 | 34.5 | 517575.9997 | 37 | 525575.9997 | 40 | 526375.9997 | 43 | 520975.9997 | 45.5 | 521175.9997 | 48.5 | 518375.9997 | 51 | 516975.9997 | 54 | 518575.9997 | 57 | 518975.9997 | 59.5 | 517775.9997
62.5 | 524775.9997 | 65.5 | 522375.9997 | 68 | 517575.9997 | 70.5 | 524775.9997 | 73.5 | 523975.9997 | 76.5 | 517575.9997 | 79.5 | 525575.9997 | 82 | 526375.9997 | 85 | 520975.9997 | 87.5 | 521175.9997 | 90.5 | 518375.9997 | 93 | 516975.9997 | 96 | 518575.9997 | 99 | 518975.9997 | 101.5 | 517775.9997
104.5 | 524775.9997 | 107.5 | 522375.9997 | 110 | 517575.9997 | 113 | 524775.9997 | 115.5 | 523975.9997 | 118.5 | 517575.9997 | 121 | 525575.9997 | 124 | 526375.9997 | 126.5 | 520975.9997 | 129.5 | 521175.9997 | 132.5 | 518375.9997 | 135 | 516975.9997 | 138 | 518575.9997 | 140.5 | 518975.9997 | 143.5 | 517775.9997
146.5 | 524775.9997 | 149.5 | 522375.9997 | 152 | 517575.9997 | 155 | 524775.9997 | 157.5 | 261838.0286 | 160.5 | 517575.9997 | 163 | 525575.9997 | 166 | 526375.9997 | 168.5 | 520975.9997 | 171.5 | 521175.9997 | 174.5 | 518375.9997 | 177 | 516975.9997 | 180 | 518575.9997 | 182.5 | 518975.9997 | 185.5 | 517775.9997
188.5 | 524775.9997 | 191 | 522375.9997 | 194 | 517575.9997 | 197 | 524775.9997 | 199.5 | 523975.9997 | 202.5 | 517575.9997 | 205 | 525575.9997 | 208 | 526375.9997 | 210.5 | 520975.9997 | 213.5 | 521175.9997 | 216.5 | 518375.9997 | 219 | 516975.9997 | 222 | 518575.9997 | 224.5 | 518975.9997 | 227.5 | 517775.9997
230.5 | 524775.9997 | 233 | 522375.9997 | 236 | 517575.9997 | 238.5 | 524775.9997 | 241.5 | 523975.9997 | 244.5 | 517575.9997 | 247 | 525575.9997 | 250 | 526375.9997 | 252.5 | 520975.9997 | 255.5 | 521175.9997 | 258.5 | 518375.9997 | 261 | 516975.9997 | 264 | 518575.9997 | 266.5 | 518975.9997 | 269.5 | 517775.9997
272.5 | 61.1222 | 275 | 522375.9997 | 278 | 517575.9997 | 280.5 | 524775.9997 | 283.5 | 523975.9997 | 286.5 | 517575.9997 | 289.5 | 525575.9997 | 292 | 526375.9997 | 294.5 | 520975.9997 | 297.5 | 521175.9997 | 300.5 | 518375.9997 | 303 | 516975.9997 | 306 | 518575.9997 | 308.5 | 518975.9997 | 311.5 | 517775.9997
314.5 | 37.5067 | 317 | 255189.1484 | 320 | 216696.1325 | 322.5 | 185902.5749 | 325.5 | 181503.3604 | 328.5 | 197099.9187 | 331 | 88.9292 | 334 | 111516.8142 | 336.5 | 121614.6564 | 339.5 | 521175.9997 | 342.5 | 161906.7665 | 345 | 192100.8414 | 348 | 180103.2696 | 350.5 | 177503.7973 | 353.5 | 517775.9997
356.5 | 36.9926 | 359 | 971.8816 | 362 | 504.3493 | 364.5 | 106917.626 | 367.5 | 104418.072 | 370.5 | 1356.4443 | 373 | 359.2577 | 376 | 65125.6275 | 378.5 | 88820.951 | 381.5 | 265.1684 | 384.5 | 65.8711 | 387 | 71513.9741 | 390 | 31.1869 | 392.5 | 75.0575 | 395.5 | 313.2568
398.5 | 87.6774 | 401 | 1276.2161 | 404 | 1460.1222 | 406.5 | 35.2992 | 409.5 | 26.2578 | 412.5 | 1098.064 | 415 | 3223.344 | 418 | 32.6263 | 420.5 | 31.1179 | 423.5 | 53.4326 | 426.5 | 45.5485 | 429.5 | 54.8268 | 432 | 25.0681 | 434.5 | 52.9998 | 437.5 | 68.3065
440.5 | 291.0894 | 443 | 612.5741 | 446 | 750.0354 | 448.5 | 25.5179 | 451.5 | 41.523 | 454.5 | 580.0346 | 457 | 2691.4424 | 460 | 10.1007 | 462.5 | 28.4589 | 465.5 | 55.3312 | 468.5 | 37.4136 | 471 | 26.3096 | 474 | 13.7324 | 476.5 | 34.0039 | 479.5 | 378.5543
482.5 | 385.0666 | 485 | 921.1364 | 488 | 3056.6945 | 490.5 | 42.2915 | 493.5 | 33.957 | 496.5 | 3920.5653 | 499 | 3751.7658 | 502 | 9.7666 | 504.5 | 44.3773 | 507.5 | 155.8111 | 510.5 | 35.7899 | 513 | 7.0378 | 516 | 20.4546 | 518.5 | 28.8763 | 521.5 | 2141.9847
524.5 | 378.5328 | 527 | 6451.9559 | 530 | 1270.7502 | 532.5 | 15.7923 | 535.5 | 23.558 | 538.5 | 6349.5153 | 541 | 13596.2001 | 544 | 149.7228 | 546.5 | 262.5317 | 549.5 | 2537.6093 | 552.5 | 1.9589 | 555 | 9.3454 | 558 | 6.3192 | 560.5 | 29.2724 | 563.5 | 6208.9476
566.5 | 3377.5279 | 569 | 6.0667 | 572 | 25.0731 | 574.5 | 8.5341 | 577.5 | 28.8135 | 580.5 | 25.7617 | 583 | 9.2659 | 586 | 17.7085 | 588.5 | 5.5551 | 591.5 | 8915.3724 | 594.5 | 16.7638 | 597 | 0.0075946 | 600 | 0.26602 | 602.5 | 28.2213 | 605.5 | 11512.4564
608.5 | 4179.921 | 611 | 5483.2683 | 614 | 4.7239 | 616.5 | 32.8383 | 619.5 | 6.8935 | 622.5 | 12.8945 | 625 | 4560.1186 | 628 | 33.2469 | 630.5 | 18.5155 | 633.5 | 18.8969 | 636.5 | 10.4218 | 639 | 0.41099 | 642 | 9.5437 | 644.5 | 22.0109 | 647.5 | 1938.5363
650.5 | 473.9932 | 653 | 4473.8516 | 656 | 3510.2375 | 658.5 | 7.9764 | 661.5 | 2.5706 | 664.5 | 13050.536 | 667 | 15.2859 | 670 | 34.5053 | 672.5 | 3183.3039 | 675.5 | 14683.4001 | 678.5 | 9106.1544 | 681 | 352.7862 | 684 | 19.2029 | 686.5 | 12.1884 | 689.5 | 294.3533
692.5 | 1168.7551 | 695 | 4881.2272 | 698 | 20.1622 | 700.5 | 264.833 | 703.5 | 11408.5798 | 706.5 | 4335.5444 | 709 | 7.4069 | 712 | 1595.9893 | 714.5 | 10.7376 | 717.5 | 1742.2104 | 720.5 | 0.83889 | 723 | 27.7875 | 726 | 2510.2625 | 728.5 | 3165.7185 | 731.5 | 1876.1049
734.5 | 967.2595 | 737 | 2.1274 | 740 | 0.17279 | 742.5 | 10945.2002 | 745.5 | 6585.9541 | 748.5 | 16.6359 | 751 | 3185.8051 | 754 | 846.4889 | 756.5 | 3252.6466 | 759.5 | 276.5201 | 762.5 | 11.1099 | 765 | 15198.3958 | 768 | 15.4104 | 770.5 | 3.8711 | 773.5 | 3469.148
776.5 | 5728.4846 | 779 | 9432.8193 | 782 | 26.6487 | 784.5 | 18.7194 | 787.5 | 15706.1977 | 790.5 | 27.7423 | 793 | 32.0129 | 796 | 6.5294 | 798.5 | 4074.8008 | 801.5 | 672.7655 | 804.5 | 207.4489 | 807 | 4884.4288 | 810 | 25.3796 | 812.5 | 15.129 | 815.5 | 7.5301
818.5 | 2516.6106 | 821 | 12826.4626 | 824 | 1115.1595 | 826.5 | 20.924 | 829.5 | 15518.7661 | 832.5 | 24.0846 | 835 | 1.1897 | 838 | 3.7689 | 840.5 | 28.5894 | 843.5 | 2472.7033 | 846.5 | 26.8464 | 850 | 11968.2153 | 851.5 | 9.9782 | 854.5 | 331.3127 | 857.5 | 15.3898
860 | 38.9343 | 863 | 23.8998 | 866 | 27.8722 | 868.5 | 118.8976 | 871.5 | 23.9195 | 874.5 | 28.9865 | 877 | 7.3613 | 880 | 15.5159 | 882.5 | 14171.6458 | 885.5 | 392.3582 | 888.5 | 14.416 | 891 | 11734.983 | 894 | 18.7452 | 896.5 | 29.7375 | 899.5 | 7470.994
902.5 | 30.1711 | 905 | 29.464 | 908 | 0.93335 | 910.5 | 3908.1187 | 913.5 | 7291.922 | 916.5 | 11.8319 | 919 | 4.1234 | 922 | 1092.0089 | 924.5 | 21.3088 | 927.5 | 6387.1855 | 930.5 | 17.4204 | 933 | 12782.6766 | 936 | 27.8616 | 938.5 | 0.18232 | 941.5 | 5270.7213
944.5 | 30.3965 | 947 | 13.237 | 950 | 11.9825 | 952.5 | 0.76777 | 955.5 | 0.11009 | 958.5 | 11.2333 | 961 | 30.2644 | 964 | 301.7013 | 966.5 | 10671.3579 | 969.5 | 52.6118 | 972.5 | 6304.2372 | 975 | 7.3617 | 977.5 | 18.8014 | 980.5 | 5347.2634 | 983.5 | 1720.117
986 | 2858.0375 | 989 | 72.6381 | 992 | 23.0507 | 994.5 | 0.70859 | 997.5 | 26.0701 | 1000.5 | 199.9268 | 1003 | 7823.7304 | 1006 | 11.4571 | 1008.5 | 5.7785 | 1011.5 | 2917.5825 | 1014.5 | 25.206 | 1017 | 14.4173 | 1020 | 8.4482 | 1022.5 | 12.7445 | 1025.5 | 2198.6114
1028 | 2560.467 | 1031 | 15.6265 | 1034 | 23.6569 | 1036.5 | 4737.8422 | 1039.5 | 13.2825 | 1042.5 | 10007.3013 | 1045 | 282.5073 | 1047.5 | 10543.3207 | 1050.5 | 7404.2859 | 1053.5 | 12412.3934 | 1056 | 15.7922 | 1059 | 0.33056 | 1061.5 | 7.559 | 1064.5 | 5429.1304 | 1067.5 | 5740.9335
1070.5 | 885.3331 | 1073 | 1041.7651 | 1076 | 8263.2683 | 1078.5 | 0.96412 | 1081.5 | 29.0092 | 1084.5 | 9.2339 | 1087 | 26.71 | 1090 | 0.69667 | 1092.5 | 481.8255 | 1095.5 | 6039.6965 | 1098.5 | 7054.1543 | 1101 | 1102.4006 | 1103.5 | 31.3918 | 1106.5 | 13.3573 | 1109.5 | 929.7154
1112.5 | 8.3011 | 1115 | 599.8394 | 1118 | 21.6783 | 1120.5 | 7050.7398 | 1123.5 | 0.96071 | 1126.5 | 26.9685 | 1129 | 3.5237 | 1132 | 4553.2843 | 1134.5 | 60.4367 | 1137.5 | 1912.1604 | 1140.5 | 23.2429 | 1143 | 772.6402 | 1145.5 | 25.006 | 1148.5 | 29.1401 | 1151.5 | 2365.7943
1154 | 4426.3226 | 1157 | 5.3531 | 1160 | 17.2921 | 1162.5 | 25.9524 | 1165.5 | 9126.2048 | 1168.5 | 11.8319 | 1171 | 8.2823 | 1174 | 13.0472 | 1176.5 | 23.5644 | 1179.5 | 1203.4658 | 1182.5 | 23.0017 | 1185 | 32.6394 | 1188 | 3.6167 | 1190.5 | 4.0449 | 1193.5 | 5.9267
1196 | 28.6866 | 1199 | 8.1709 | 1201.5 | 19.6459 | 1204.5 | 22.6745 | 1207.5 | 15.9316 | 1210 | 12.7924 | 1213 | 18.4591 | 1215.5 | 23.1712 | 1218.5 | 7126.1069 | 1221.5 | 2032.6054 | 1224 | 3.9229 | 1227 | 33.3417 | 1230 | 15.4104 | 1232.5 | 34.2173 | 1235.5 | 9.8064
1238 | 9490.5374 | 1241 | 31.6095 | 1243.5 | 26.7764 | 1246.5 | 5.5775 | 1249.5 | 0.070039 | 1252 | 28.4598 | 1255 | 4.3824 | 1257.5 | 20.4938 | 1260.5 | 13.851 | 1263.5 | 53.2118 | 1266 | 22.9415 | 1269 | 28.8356 | 1272 | 0.22545 | 1274.5 | 27.5083 | 1277.5 | 111.4642
1280.5 | 3360.9593 | 1283 | 7.1546 | 1286 | 25.1354 | 1288.5 | 13.7124 | 1291.5 | 13.8952 | 1294 | 3.5004 | 1297 | 2.8464 | 1300 | 25.7804 | 1302.5 | 3.6276 | 1305.5 | 9828.4642 | 1308.5 | 7.7029 | 1311 | 0.93077 | 1314 | 7.0505 | 1316.5 | 14.2366 | 1319.5 | 270.2874
1322.5 | 595.4939 | 1325 | 9.4914 | 1328 | 12.4367 | 1330.5 | 2.6036 | 1333.5 | 11.7286 | 1336 | 10.8376 | 1339 | 26.5215 | 1341.5 | 17.5454 | 1344.5 | 31.7994 | 1347.5 | 4351.1961 | 1350 | 0.77783 | 1353 | 27.9828 | 1355.5 | 0.51011 | 1358.5 | 14.6024 | 1361.5 | 249.004
1364 | 2273.5577 | 1367 | 24.1426 | 1369.5 | 6.2021 | 1372.5 | 11.408 | 1375.5 | 22.841 | 1378 | 32.4458 | 1381 | 3.0994 | 1383.5 | 8.5424 | 1386.5 | 32.2806 | 1389.5 | 5178.3341 | 1392 | 0.81761 | 1395 | 4.3366 | 1398 | 14.6704 | 1400.5 | 0.93935 | 1403.5 | 195.7342
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!

## C-G Min
Average Conductor to Ground Resistances
Open Burn Test 12 |  |  | 2006-11-22 | 13:02
Mixed | 7-C | Tray C | IRMS | 2
0 | 250 kW
Burner Time | A1-G |  | Burner Time | A2-G | Burner Time | B3-G | Burner Time | B4-G | Burner Time | C5-G | Burner Time | C6-G
-183.9 | 517576 |  | -175 | 517576 | -169.4 | 516976 | -166.1 | 517576 | -163.8 | 517776 | -161.8 | 516976
-142 | 517576 |  | -132.9 | 517576 | -127.3 | 516976 | -124.1 | 517576 | -121.9 | 517776 | -119.6 | 516976
-100.1 | 517576 |  | -91.1 | 517576 | -85.4 | 516976 | -82.1 | 517576 | -79.9 | 517776 | -77.6 | 516976
-58.1 | 517576 |  | -49 | 517576 | -43.5 | 516976 | -40.2 | 517576 | -37.9 | 517776 | -35.7 | 516976
-16.1 | 517576 |  | -6.9 | 517576 | -1.4 | 516976 | 2 | 517576 | 4.1 | 517776 | 6.5 | 516976
26.1 | 517576 |  | 35 | 517576 | 40.6 | 516976 | 43.9 | 517576 | 46.2 | 517776 | 48.4 | 516976
68 | 517576 |  | 77.1 | 517576 | 82.6 | 516976 | 86 | 517576 | 88.1 | 517776 | 90.4 | 516976
110.1 | 517576 |  | 118.9 | 517576 | 124.6 | 516976 | 127.8 | 517576 | 130.2 | 517776 | 132.2 | 516976
152.1 | 517576 |  | 160.9 | 517576 | 166.6 | 516976 | 169.8 | 517576 | 172.2 | 517776 | 174.2 | 516976
194 | 517576 |  | 202.9 | 517576 | 208.5 | 516976 | 211.8 | 517576 | 214.2 | 517776 | 216.2 | 516976
235.9 | 517576 |  | 244.9 | 517576 | 250.5 | 516976 | 253.8 | 517576 | 256.1 | 517776 | 258.2 | 516976
277.9 | 1441.1848 |  | 287 | 2359.1159 | 292.5 | 516976 | 295.9 | 517576 | 298.1 | 517776 | 300.2 | 516976
319.9 | 226.1993 |  | 328.9 | 73.6885 | 334.5 | 166.8775 | 337.8 | 79.7798 | 340.1 | 517776 | 342.2 | 516976.0002
361.9 | 66.4155 |  | 370.9 | 32.9651 | 376.5 | 66.8198 | 379.8 | 32.3828 | 382.1 | 313.639 | 384.2 | 52.4959
403.9 | 23.0165 |  | 412.9 | 18.4864 | 418.6 | 46.6278 | 421.8 | 23.0415 | 424.1 | 31.9786 | 426.3 | 23.6571
445.9 | 10.4415 |  | 454.9 | 8.5554 | 460.5 | 26.2181 | 463.8 | 15.1079 | 466.1 | 7.788 | 468.2 | 22.0323
487.9 | 9.5835 |  | 496.9 | 11.2117 | 502.5 | 8.4927 | 505.8 | 21.7549 | 508.1 | 4.3614 | 510.2 | 13.3873
529.9 | 8.7233 |  | 538.9 | 11.3483 | 544.5 | 3.4882 | 547.8 | 6.5954 | 550.1 | 8.2393 | 552.2 | 13.5281
571.9 | 7.5496 |  | 580.9 | 7.0411 | 586.5 | 1.5467 | 589.8 | 1.821 | 592.1 | 7.0789 | 594.2 | 4.1067
613.9 | 6.2117 |  | 622.9 | 9.8574 | 628.5 | 1.1495 | 631.8 | 10.9705 | 634.1 | 4.7407 | 636.2 | 2.3323
655.9 | 3.9681 |  | 664.9 | 10.7848 | 670.5 | 4.7769 | 673.8 | 0.65601 | 676.1 | 1.2643 | 678.2 | 0.63791
697.9 | 3.2804 |  | 706.9 | 3.3999 | 712.5 | 2.3847 | 715.8 | 1.5051 | 718.1 | 3.3637 | 720.2 | 5.332
739.9 | 1.3858 |  | 748.9 | 5.5759 | 754.5 | 4.8842 | 757.8 | 1.2668 | 760.1 | 2.1544 | 762.2 | 11.0241
781.9 | 11.0355 |  | 790.9 | 8.0172 | 796.5 | 2.5421 | 799.8 | 3.2762 | 802.1 | 0.6377 | 804.2 | 3.9399
823.9 | 7.0059 |  | 832.9 | 2.7514 | 838.7 | 4.8517 | 841.7 | 3.6297 | 844 | 0.94901 | 846.4 | 3.2782
865.8 | 2.1948 |  | 874.8 | 0.62807 | 880.5 | 12.6511 | 883.8 | 0.63339 | 886.1 | 2.2353 | 888.2 | 9.8341
907.9 | 0.63686 |  | 916.9 | 1.3666 | 922.5 | 2.9712 | 925.8 | 1.7397 | 928.1 | 3.9788 | 930.2 | 13.9558
949.9 | 0.82136 |  | 958.9 | 0.62737 | 964.5 | 1.255 | 967.7 | 1.7052 | 970 | 2.7166 | 972.2 | 3.4152
991.8 | 0.63616 |  | 1000.8 | 3.299 | 1006.5 | 2.5507 | 1009.8 | 9.889 | 1012.1 | 2.8362 | 1014.2 | 1.9472
1033.8 | 14.6775 |  | 1042.7 | 5.196 | 1048.4 | 1.2287 | 1051.7 | 0.62842 | 1053.8 | 3.3232 | 1056.2 | 9.2792
1075.9 | 0.62807 |  | 1084.9 | 0.89613 | 1090.5 | 6.3426 | 1093.7 | 10.0662 | 1096 | 3.008 | 1098.2 | 2.6414
1117.9 | 0.62903 |  | 1126.9 | 0.63896 | 1132.5 | 7.1087 | 1135.7 | 5.9075 | 1138 | 6.3733 | 1140.2 | 2.0733
1159.8 | 6.8458 |  | 1168.8 | 9.0312 | 1174.5 | 4.4383 | 1177.8 | 5.1228 | 1180.1 | 7.3986 | 1182.2 | 18.2847
1201.7 | 9.6257 |  | 1210.6 | 13.5604 | 1216.3 | 5.4242 | 1219.7 | 16.7663 | 1221.9 | 8.3736 | 1224.2 | 15.5892
1243.7 | 1.6439 |  | 1252.6 | 5.8977 | 1258.3 | 17.9216 | 1261.7 | 1.781 | 1263.9 | 26.5567 | 1266.2 | 20.3113
1285.9 | 5.4479 |  | 1294.8 | 4.3836 | 1300.4 | 0.6376 | 1303.8 | 3.0737 | 1306.1 | 186.245 | 1308.2 | 36.1934
1327.9 | 4.1286 |  | 1336.7 | 12.2454 | 1342.3 | 0.75438 | 1345.7 | 2.0614 | 1347.8 | 334.3861 | 1350.2 | 21.4629
1369.7 | 7.6697 |  | 1378.6 | 4.633 | 1384.3 | 0.63686 | 1387.7 | 0.63513 | 1389.9 | 196.2677 | 1392.2 | 18.9128
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!

## C5-C6
Open Burn Test 12 |  |  | 2006-11-22 | 13:02 |  |  | Vs = |  | 158.0818 |  | R = | 100
Mixed | 7-C | Tray C | IRMS | 2
0 | 250 kW |  | Bundle | Ch. 5 & 6 | Cable C | Odd-Even
Time-29 | N11 | N12 | Time-30 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R6-G | R5-6
39043.539 | 0 | 0 | 39043.539 | 0 | 0 |  | -150.5 | 39.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517776 | 517776 | 517775.9997
39043.5395 | 0 | 0 | 39043.5395 | 0 | 0 |  | -108.5 | 81.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517776 | 517776 | 517775.9997
39043.54 | 0 | 0 | 39043.54 | 0 | 0 |  | -66.5 | 123.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517776 | 517776 | 517775.9997
39043.5405 | 0 | 0 | 39043.5405 | 0 | 0 |  | -24.5 | 165.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517776 | 517776 | 517775.9997
39043.541 | 0 | 0 | 39043.541 | 0 | 0 |  | 17.5 | 207.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517776 | 517776 | 517775.9997
39043.5415 | 0 | 0 | 39043.5415 | 0 | 0 |  | 59.5 | 249.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517776 | 517776 | 517775.9997
39043.5419 | 0 | 0 | 39043.542 | 0 | 0 |  | 101.5 | 291.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517776 | 517776 | 517775.9997
39043.5424 | 0 | 0 | 39043.5424 | 0 | 0 |  | 143.5 | 333.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517776 | 517776 | 517775.9997
39043.5429 | 0 | 0 | 39043.5429 | 0 | 0 |  | 185.5 | 375.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517776 | 517776 | 517775.9997
39043.5434 | 0 | 0 | 39043.5434 | 0 | 0 |  | 227.5 | 417.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517776 | 517776 | 517775.9997
39043.5439 | 0 | 0 | 39043.5439 | 0 | 0 |  | 269.5 | 459.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517776 | 517776 | 517775.9997
39043.5444 | 0 | 0 | 39043.5444 | 0 | 0 |  | 311.5 | 501.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517776 | 517776 | 517775.9997
39043.5449 | 0 | 0 | 39043.5449 | 0 | 0 |  | 353.5 | 543.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517776 | 517776 | 517775.9997
39043.5453 | 626 | 0 | 39043.5454 | 1698 | 0 |  | 395.5 | 585.5 | 38.2173 | 0 | 103.663 | 0 | 0.38217 | 0 | 1.0366 | 0 | 0.38217 | 1.0366 | 313.639 | 52.4959 | 313.2568
39043.5458 | 1530 | 0 | 39043.5458 | 2107 | 13 |  | 437.5 | 627.5 | 93.4066 | 0 | 128.6325 | 0.79365 | 0.93407 | 0 | 1.2863 | 0.0079365 | 0.93407 | 1.2784 | 69.2405 | 23.6571 | 68.3065
39043.5463 | 2172 | 19 | 39043.5463 | 2138 | 15 |  | 479.5 | 669.5 | 132.6007 | 1.16 | 130.525 | 0.91575 | 1.326 | 0.0116 | 1.3053 | 0.0091575 | 1.3144 | 1.2961 | 20.1949 | 22.0323 | 378.5543
39043.5468 | 1997 | 7 | 39043.5468 | 1935 | 8 |  | 521.5 | 711.5 | 121.917 | 0.42735 | 118.1319 | 0.4884 | 1.2192 | 0.0042735 | 1.1813 | 0.004884 | 1.2149 | 1.1764 | 30.0751 | 34.4338 | 2141.9847
39043.5473 | 1934 | 2 | 39043.5473 | 2098 | 1 |  | 563.5 | 753.5 | 118.0708 | 0.1221 | 128.083 | 0.06105 | 1.1807 | 0.001221 | 1.2808 | 0.0006105 | 1.1795 | 1.2802 | 34.0727 | 23.4654 | 6208.9476
39043.5478 | 2087 | 1 | 39043.5478 | 1996 | 1 |  | 605.5 | 795.5 | 127.4115 | 0.06105 | 121.8559 | 0.06105 | 1.2741 | 0.0006105 | 1.2186 | 0.0006105 | 1.2735 | 1.2179 | 24.1222 | 29.8053 | 11512.4564
39043.5483 | 2338 | 2 | 39043.5483 | 2190 | 2 |  | 647.5 | 837.5 | 142.735 | 0.1221 | 133.6996 | 0.1221 | 1.4274 | 0.001221 | 1.337 | 0.001221 | 1.4261 | 1.3358 | 10.8114 | 18.4088 | 1938.5363
39043.5488 | 2124 | 1 | 39043.5488 | 2573 | 1 |  | 689.5 | 879.5 | 129.6703 | 0.06105 | 157.0818 | 0.06105 | 1.2967 | 0.0006105 | 1.5708 | 0.0006105 | 1.2961 | 1.5702 | 23.6686 | 0.63791 | 294.3533
39043.5492 | 2342 | 1 | 39043.5492 | 2393 | 1 |  | 731.5 | 921.5 | 142.9792 | 0.06105 | 146.0928 | 0.06105 | 1.4298 | 0.0006105 | 1.4609 | 0.0006105 | 1.4292 | 1.4603 | 10.6223 | 8.2423 | 1876.1049
39043.5497 | 2239 | 1 | 39043.5497 | 2333 | 1 |  | 773.5 | 963.5 | 136.6911 | 0.06105 | 142.4298 | 0.06105 | 1.3669 | 0.0006105 | 1.4243 | 0.0006105 | 1.3663 | 1.4237 | 15.7197 | 11.0241 | 3469.148
39043.5502 | 2376 | 0 | 39043.5502 | 2103 | 0 |  | 815.5 | 1005.5 | 145.0549 | 0 | 128.3883 | 0 | 1.4505 | 0 | 1.2839 | 0 | 1.4505 | 1.2839 | 8.9806 | 23.1279 | 7.5301
39043.5507 | 2218 | 0 | 39043.5507 | 1958 | 0 |  | 857.5 | 1047.5 | 135.409 | 0 | 119.536 | 0 | 1.3541 | 0 | 1.1954 | 0 | 1.3541 | 1.1954 | 16.7439 | 32.2462 | 15.3898
39043.5512 | 2246 | 1 | 39043.5512 | 2026 | 1 |  | 899.5 | 1089.5 | 137.1184 | 0.06105 | 123.6874 | 0.06105 | 1.3712 | 0.0006105 | 1.2369 | 0.0006105 | 1.3706 | 1.2363 | 15.3198 | 27.9112 | 7470.994
39043.5517 | 2158 | 1 | 39043.5517 | 2273 | 1 |  | 941.5 | 1131.5 | 131.746 | 0.06105 | 138.7668 | 0.06105 | 1.3175 | 0.0006105 | 1.3877 | 0.0006105 | 1.3168 | 1.3871 | 20.0657 | 13.9558 | 5270.7213
39043.5522 | 2521 | 1 | 39043.5522 | 1938 | 1 |  | 983.5 | 1173.5 | 153.9072 | 0.06105 | 118.315 | 0.06105 | 1.5391 | 0.0006105 | 1.1832 | 0.0006105 | 1.5385 | 1.1825 | 2.7166 | 34.2797 | 1720.117
39043.5526 | 2339 | 1 | 39043.5527 | 2362 | 1 |  | 1025.5 | 1215.5 | 142.7961 | 0.06105 | 144.2002 | 0.06105 | 1.428 | 0.0006105 | 1.442 | 0.0006105 | 1.4274 | 1.4414 | 10.7567 | 9.6687 | 2198.6114
39043.5531 | 2004 | 1 | 39043.5531 | 2335 | 0 |  | 1067.5 | 1257.5 | 122.3443 | 0.06105 | 142.5519 | 0 | 1.2234 | 0.0006105 | 1.4255 | 0 | 1.2228 | 1.4255 | 29.3597 | 10.8942 | 5740.9335
39043.5536 | 2514 | 1 | 39043.5536 | 2270 | 1 |  | 1109.5 | 1299.5 | 153.4799 | 0.06105 | 138.5836 | 0.06105 | 1.5348 | 0.0006105 | 1.3858 | 0.0006105 | 1.5342 | 1.3852 | 3.008 | 14.2851 | 929.7154
39043.5541 | 2234 | 1 | 39043.5541 | 2417 | 1 |  | 1151.5 | 1341.5 | 136.3858 | 0.06105 | 147.558 | 0.06105 | 1.3639 | 0.0006105 | 1.4756 | 0.0006105 | 1.3632 | 1.475 | 16.0152 | 7.1534 | 2365.7943
39043.5546 | 2411 | 0 | 39043.5546 | 2014 | 1 |  | 1193.5 | 1383.5 | 147.1917 | 0 | 122.9548 | 0.06105 | 1.4719 | 0 | 1.2295 | 0.0006105 | 1.4719 | 1.2289 | 7.3986 | 28.6329 | 5.9267
39043.5551 | 2328 | 0 | 39043.5551 | 1704 | 1 |  | 1235.5 | 1425.5 | 142.1245 | 0 | 104.0293 | 0.06105 | 1.4212 | 0 | 1.0403 | 0.0006105 | 1.4212 | 1.0397 | 11.2277 | 52.0482 | 9.8064
39043.5556 | 1155 | 306 | 39043.5556 | 1979 | 1 |  | 1277.5 | 1467.5 | 70.5128 | 18.6813 | 120.8181 | 0.06105 | 0.70513 | 0.18681 | 1.2082 | 0.0006105 | 0.51832 | 1.2076 | 1005.3495 | 43.3228 | 111.4642
39043.556 | 605 | 478 | 39043.5561 | 911 | 305 |  | 1319.5 | 1509.5 | 36.9353 | 29.1819 | 55.6166 | 18.6203 | 0.36935 | 0.29182 | 0.55617 | 0.1862 | 0.077534 | 0.36996 | 4162.3292 | 602.5824 | 270.2874
39043.5565 | 428 | 609 | 39043.5565 | 908 | 1027 |  | 1361.5 | 1551.5 | 26.1294 | 37.1795 | 55.4335 | 62.6984 | 0.26129 | 0.37179 | 0.55433 | 0.62698 | 0.1105 | 0.07265 | 1297.6253 | 4218.698 | 249.004
39043.557 | 874 | 0 | 39043.557 | 1875 | 0 |  | 1403.5 | 1593.5 | 53.3578 | 0 | 114.4689 | 0 | 0.53358 | 0 | 1.1447 | 0 | 0.53358 | 1.1447 | 196.2677 | 38.1003 | 195.7342

## B4-C6
Open Burn Test 12 |  |  | 2006-11-22 | 13:02 |  |  | Vs = |  | 158.4481 |  | R = | 100
Mixed | 7-C | Tray C | IRMS | 2
0 | 250 kW |  | Bundle | Ch. 4 & 6 | Cable B | Even - | Cable C |  | Even
Time-27 | N11 | N12 | Time-28 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R6-G | R4-6
39043.539 | 0 | 0 | 39043.539 | 0 | 0 |  | -153.5 | 36.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518976 | 518976 | 518975.9997
39043.5395 | 0 | 0 | 39043.5395 | 0 | 0 |  | -111.5 | 78.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518976 | 518976 | 518975.9997
39043.54 | 0 | 0 | 39043.54 | 0 | 0 |  | -69 | 121 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518976 | 518976 | 518975.9997
39043.5405 | 0 | 0 | 39043.5405 | 0 | 0 |  | -27.5 | 162.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518976 | 518976 | 518975.9997
39043.5409 | 0 | 0 | 39043.541 | 0 | 0 |  | 15 | 205 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518976 | 518976 | 518975.9997
39043.5414 | 0 | 0 | 39043.5414 | 0 | 0 |  | 57 | 247 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518976 | 518976 | 518975.9997
39043.5419 | 0 | 0 | 39043.5419 | 0 | 0 |  | 99 | 289 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518976 | 518976 | 518975.9997
39043.5424 | 0 | 0 | 39043.5424 | 0 | 0 |  | 140.5 | 330.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518976 | 518976 | 518975.9997
39043.5429 | 0 | 0 | 39043.5429 | 0 | 0 |  | 182.5 | 372.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518976 | 518976 | 518975.9997
39043.5434 | 0 | 0 | 39043.5434 | 0 | 0 |  | 224.5 | 414.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518976 | 518976 | 518975.9997
39043.5439 | 0 | 0 | 39043.5439 | 0 | 0 |  | 266.5 | 456.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518976 | 518976 | 518975.9997
39043.5443 | 0 | 0 | 39043.5444 | 0 | 0 |  | 308.5 | 498.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518976 | 518976 | 518975.9997
39043.5448 | 819 | 1 | 39043.5448 | 0 | 0 |  | 350.5 | 540.5 | 50 | 0.06105 | 0.030525 | 0 | 0.5 | 0.0006105 | 0.00030525 | 0 | 0.49939 | 0.00030525 | 217.1614 | 518976.0004 | 177503.7973
39043.5453 | 1475 | 0 | 39043.5453 | 1505 | 0 |  | 392.5 | 582.5 | 90.0488 | 0 | 91.8803 | 0 | 0.90049 | 0 | 0.9188 | 0 | 0.90049 | 0.9188 | 75.958 | 72.4505 | 75.0575
39043.5458 | 1685 | 0 | 39043.5458 | 1627 | 0 |  | 434.5 | 624.5 | 102.8694 | 0 | 99.3284 | 0 | 1.0287 | 0 | 0.99328 | 0 | 1.0287 | 0.99328 | 54.0285 | 59.5194 | 52.9998
39043.5463 | 1920 | 0 | 39043.5463 | 2013 | 0 |  | 476.5 | 666.5 | 117.2161 | 0 | 122.8938 | 0 | 1.1722 | 0 | 1.2289 | 0 | 1.1722 | 1.2289 | 35.176 | 28.9309 | 34.0039
39043.5468 | 1995 | 0 | 39043.5468 | 1964 | 0 |  | 518.5 | 708.5 | 121.7949 | 0 | 119.9023 | 0 | 1.2179 | 0 | 1.199 | 0 | 1.2179 | 1.199 | 30.0942 | 32.1477 | 28.8763
39043.5473 | 1989 | 0 | 39043.5473 | 2259 | 0 |  | 560.5 | 750.5 | 121.4286 | 0 | 137.9121 | 0 | 1.2143 | 0 | 1.3791 | 0 | 1.2143 | 1.3791 | 30.4867 | 14.8907 | 29.2724
39043.5477 | 2005 | 0 | 39043.5478 | 2493 | 0 |  | 602.5 | 792.5 | 122.4054 | 0 | 152.1978 | 0 | 1.2241 | 0 | 1.522 | 0 | 1.2241 | 1.522 | 29.4454 | 4.1067 | 28.2213
39043.5482 | 2105 | 0 | 39043.5482 | 2009 | 0 |  | 644.5 | 834.5 | 128.5104 | 0 | 122.6496 | 0 | 1.2851 | 0 | 1.2265 | 0 | 1.2851 | 1.2265 | 23.296 | 29.1877 | 22.0109
39043.5487 | 2285 | 0 | 39043.5487 | 1980 | 1 |  | 686.5 | 876.5 | 139.4994 | 0 | 120.8791 | 0.06105 | 1.395 | 0 | 1.2088 | 0.0006105 | 1.395 | 1.2082 | 13.5834 | 31.146 | 12.1884
39043.5492 | 1969 | 1 | 39043.5492 | 2464 | 0 |  | 728.5 | 918.5 | 120.2076 | 0.06105 | 150.4274 | 0 | 1.2021 | 0.0006105 | 1.5043 | 0 | 1.2015 | 1.5043 | 32.1345 | 5.332 | 3165.7185
39043.5497 | 2463 | 0 | 39043.5497 | 2020 | 1 |  | 770.5 | 960.5 | 150.3663 | 0 | 123.3211 | 0.06105 | 1.5037 | 0 | 1.2332 | 0.0006105 | 1.5037 | 1.2326 | 5.3747 | 28.5478 | 3.8711
39043.5502 | 2228 | 0 | 39043.5502 | 2497 | 0 |  | 812.5 | 1002.5 | 136.0195 | 0 | 152.442 | 0 | 1.3602 | 0 | 1.5244 | 0 | 1.3602 | 1.5244 | 16.4892 | 3.9399 | 15.129
39043.5507 | 2490 | 1 | 39043.5507 | 2513 | 0 |  | 854.5 | 1044.5 | 152.0147 | 0.06105 | 153.4188 | 0 | 1.5201 | 0.0006105 | 1.5342 | 0 | 1.5195 | 1.5342 | 4.2864 | 3.2782 | 331.3127
39043.5511 | 1982 | 0 | 39043.5512 | 2363 | 0 |  | 896.5 | 1086.5 | 121.0012 | 0 | 144.2613 | 0 | 1.21 | 0 | 1.4426 | 0 | 1.21 | 1.4426 | 30.9475 | 9.8341 | 29.7375
39043.5516 | 2551 | 0 | 39043.5516 | 2112 | 0 |  | 938.5 | 1128.5 | 155.7387 | 0 | 128.9377 | 0 | 1.5574 | 0 | 1.2894 | 0 | 1.5574 | 1.2894 | 1.7397 | 22.8873 | 0.18232
39043.5521 | 2378 | 1 | 39043.5521 | 1954 | 0 |  | 980.5 | 1170.5 | 145.177 | 0.06105 | 119.2918 | 0 | 1.4518 | 0.0006105 | 1.1929 | 0 | 1.4512 | 1.1929 | 9.1569 | 32.824 | 5347.2634
39043.5526 | 2274 | 0 | 39043.5526 | 2396 | 0 |  | 1022.5 | 1212.5 | 138.8278 | 0 | 146.2759 | 0 | 1.3883 | 0 | 1.4628 | 0 | 1.3883 | 1.4628 | 14.1328 | 8.3214 | 12.7445
39043.5531 | 1955 | 1 | 39043.5531 | 2375 | 0 |  | 1064.5 | 1254.5 | 119.3529 | 0.06105 | 144.9939 | 0 | 1.1935 | 0.0006105 | 1.4499 | 0 | 1.1929 | 1.4499 | 32.9545 | 9.2792 | 5429.1304
39043.5536 | 2262 | 0 | 39043.5536 | 2144 | 1 |  | 1106.5 | 1296.5 | 138.0952 | 0 | 130.8913 | 0.06105 | 1.381 | 0 | 1.3089 | 0.0006105 | 1.381 | 1.3083 | 14.7383 | 21.1097 | 13.3573
39043.5541 | 1991 | 0 | 39043.5541 | 2507 | 0 |  | 1148.5 | 1338.5 | 121.5507 | 0 | 153.0525 | 0 | 1.2155 | 0 | 1.5305 | 0 | 1.2155 | 1.5305 | 30.3556 | 3.5253 | 29.1401
39043.5545 | 2459 | 0 | 39043.5546 | 1972 | 0 |  | 1190.5 | 1380.5 | 150.1221 | 0 | 120.3907 | 0 | 1.5012 | 0 | 1.2039 | 0 | 1.5012 | 1.2039 | 5.5462 | 31.6116 | 4.0449
39043.555 | 1917 | 0 | 39043.555 | 2129 | 0 |  | 1232.5 | 1422.5 | 117.033 | 0 | 129.9756 | 0 | 1.1703 | 0 | 1.2998 | 0 | 1.1703 | 1.2998 | 35.3876 | 21.9061 | 34.2173
39043.5555 | 2016 | 0 | 39043.5555 | 1415 | 0 |  | 1274.5 | 1464.5 | 123.0769 | 0 | 86.3858 | 0 | 1.2308 | 0 | 0.86386 | 0 | 1.2308 | 0.86386 | 28.7391 | 83.4191 | 27.5083
39043.556 | 2245 | 0 | 39043.556 | 860 | 0 |  | 1316.5 | 1506.5 | 137.0574 | 0 | 52.5031 | 0 | 1.3706 | 0 | 0.52503 | 0 | 1.3706 | 0.52503 | 15.6071 | 201.7884 | 14.2366
39043.5565 | 2238 | 0 | 39043.5565 | 1698 | 3 |  | 1358.5 | 1548.5 | 136.63 | 0 | 103.663 | 0.18315 | 1.3663 | 0 | 1.0366 | 0.0018315 | 1.3663 | 1.0348 | 15.9687 | 53.1198 | 14.6024
39043.557 | 2579 | 0 | 39043.557 | 1884 | 0 |  | 1400.5 | 1590.5 | 157.4481 | 0 | 115.0183 | 0 | 1.5745 | 0 | 1.1502 | 0 | 1.5745 | 1.1502 | 0.63513 | 37.759 | 0.93935

## B4-C5
Open Burn Test 12 |  |  | 2006-11-22 | 13:02 |  |  | Vs = |  | 158.326 |  | R = | 100
Mixed | 7-C | Tray C | IRMS | 2
0 | 250 kW |  | Bundle | Ch. 4 & 5 | Cable B | Even - | Cable C |  | Odd
Time-25 | N11 | N12 | Time-26 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R5-G | R4-5
39043.539 | 0 | 0 | 39043.539 | 0 | 0 |  | -156 | 34 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518576 | 518576 | 518575.9997
39043.5394 | 0 | 0 | 39043.5395 | 0 | 0 |  | -114 | 76 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518576 | 518576 | 518575.9997
39043.5399 | 0 | 0 | 39043.54 | 0 | 0 |  | -72 | 118 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518576 | 518576 | 518575.9997
39043.5404 | 0 | 0 | 39043.5404 | 0 | 0 |  | -30 | 160 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518576 | 518576 | 518575.9997
39043.5409 | 0 | 0 | 39043.5409 | 0 | 0 |  | 12 | 202 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518576 | 518576 | 518575.9997
39043.5414 | 0 | 0 | 39043.5414 | 0 | 0 |  | 54 | 244 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518576 | 518576 | 518575.9997
39043.5419 | 0 | 0 | 39043.5419 | 0 | 0 |  | 96 | 286 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518576 | 518576 | 518575.9997
39043.5424 | 0 | 0 | 39043.5424 | 0 | 0 |  | 138 | 328 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518576 | 518576 | 518575.9997
39043.5428 | 0 | 0 | 39043.5429 | 0 | 0 |  | 180 | 370 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518576 | 518576 | 518575.9997
39043.5433 | 0 | 0 | 39043.5434 | 0 | 0 |  | 222 | 412 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518576 | 518576 | 518575.9997
39043.5438 | 0 | 0 | 39043.5438 | 0 | 0 |  | 264 | 454 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518576 | 518576 | 518575.9997
39043.5443 | 0 | 0 | 39043.5443 | 0 | 0 |  | 306 | 496 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518576 | 518576 | 518575.9997
39043.5448 | 791 | 1 | 39043.5448 | 0 | 0 |  | 348 | 538 | 48.2906 | 0.06105 | 0.030525 | 0 | 0.48291 | 0.0006105 | 0.00030525 | 0 | 0.4823 | 0.00030525 | 228.1494 | 518575.9999 | 180103.2696
39043.5453 | 1959 | 0 | 39043.5453 | 129 | 0 |  | 390 | 580 | 119.5971 | 0 | 7.8755 | 0 | 1.196 | 0 | 0.078755 | 0 | 1.196 | 0.078755 | 32.3828 | 1910.3721 | 31.1869
39043.5458 | 2053 | 0 | 39043.5458 | 1965 | 0 |  | 432 | 622 | 125.3358 | 0 | 119.9634 | 0 | 1.2534 | 0 | 1.1996 | 0 | 1.2534 | 1.1996 | 26.3215 | 31.9786 | 25.0681
39043.5462 | 2253 | 0 | 39043.5463 | 2406 | 0 |  | 474 | 664 | 137.5458 | 0 | 146.8864 | 0 | 1.3755 | 0 | 1.4689 | 0 | 1.3755 | 1.4689 | 15.1079 | 7.788 | 13.7324
39043.5467 | 2130 | 0 | 39043.5468 | 2485 | 0 |  | 516 | 706 | 130.0366 | 0 | 151.7094 | 0 | 1.3004 | 0 | 1.5171 | 0 | 1.3004 | 1.5171 | 21.7549 | 4.3614 | 20.4546
39043.5472 | 2406 | 0 | 39043.5472 | 1929 | 0 |  | 558 | 748 | 146.8864 | 0 | 117.7656 | 0 | 1.4689 | 0 | 1.1777 | 0 | 1.4689 | 1.1777 | 7.788 | 34.4417 | 6.3192
39043.5477 | 2547 | 0 | 39043.5477 | 2253 | 0 |  | 600 | 790 | 155.4945 | 0 | 137.5458 | 0 | 1.5549 | 0 | 1.3755 | 0 | 1.5549 | 1.3755 | 1.821 | 15.1079 | 0.26602
39043.5482 | 2337 | 0 | 39043.5482 | 2476 | 0 |  | 642 | 832 | 142.674 | 0 | 151.16 | 0 | 1.4267 | 0 | 1.5116 | 0 | 1.4267 | 1.5116 | 10.9705 | 4.7407 | 9.5437
39043.5487 | 2577 | 1 | 39043.5487 | 2561 | 0 |  | 684 | 874 | 157.326 | 0.06105 | 156.3492 | 0 | 1.5733 | 0.0006105 | 1.5635 | 0 | 1.5726 | 1.5635 | 0.65601 | 1.2643 | 19.2029
39043.5492 | 2476 | 1 | 39043.5492 | 2034 | 0 |  | 726 | 916 | 151.16 | 0.06105 | 124.1758 | 0 | 1.5116 | 0.0006105 | 1.2418 | 0 | 1.511 | 1.2418 | 4.7496 | 27.5015 | 2510.2625
39043.5497 | 2221 | 0 | 39043.5497 | 2058 | 1 |  | 768 | 958 | 135.5922 | 0 | 125.641 | 0.06105 | 1.3559 | 0 | 1.2564 | 0.0006105 | 1.3559 | 1.2558 | 16.7663 | 26.0758 | 15.4104
39043.5501 | 2048 | 0 | 39043.5502 | 2490 | 0 |  | 810 | 1000 | 125.0305 | 0 | 152.0147 | 0 | 1.2503 | 0 | 1.5201 | 0 | 1.2503 | 1.5201 | 26.6299 | 4.1518 | 25.3796
39043.5506 | 2328 | 0 | 39043.5506 | 2569 | 0 |  | 851.5 | 1041.5 | 142.1245 | 0 | 156.8376 | 0 | 1.4212 | 0 | 1.5684 | 0 | 1.4212 | 1.5684 | 11.3995 | 0.94901 | 9.9782
39043.5511 | 2160 | 0 | 39043.5511 | 2521 | 0 |  | 894 | 1084 | 131.8681 | 0 | 153.9072 | 0 | 1.3187 | 0 | 1.5391 | 0 | 1.3187 | 1.5391 | 20.0639 | 2.8711 | 18.7452
39043.5516 | 2009 | 0 | 39043.5516 | 2062 | 1 |  | 936 | 1126 | 122.6496 | 0 | 125.8852 | 0.06105 | 1.2265 | 0 | 1.2589 | 0.0006105 | 1.2265 | 1.2582 | 29.0881 | 25.8311 | 27.8616
39043.5521 | 2159 | 0 | 39043.5521 | 1969 | 0 |  | 977.5 | 1167.5 | 131.8071 | 0 | 120.2076 | 0 | 1.3181 | 0 | 1.2021 | 0 | 1.3181 | 1.2021 | 20.1195 | 31.7105 | 18.8014
39043.5526 | 2360 | 0 | 39043.5526 | 1944 | 0 |  | 1020 | 1210 | 144.0781 | 0 | 118.6813 | 0 | 1.4408 | 0 | 1.1868 | 0 | 1.4408 | 1.1868 | 9.889 | 33.4043 | 8.4482
39043.5531 | 2379 | 0 | 39043.5531 | 2182 | 1 |  | 1061.5 | 1251.5 | 145.2381 | 0 | 133.2112 | 0.06105 | 1.4524 | 0 | 1.3321 | 0.0006105 | 1.4524 | 1.3315 | 9.0113 | 18.9078 | 7.559
39043.5535 | 1956 | 0 | 39043.5536 | 1918 | 0 |  | 1103.5 | 1293.5 | 119.4139 | 0 | 117.094 | 0 | 1.1941 | 0 | 1.1709 | 0 | 1.1941 | 1.1709 | 32.5859 | 35.2127 | 31.3918
39043.554 | 2054 | 0 | 39043.554 | 2438 | 0 |  | 1145.5 | 1335.5 | 125.3968 | 0 | 148.84 | 0 | 1.254 | 0 | 1.4884 | 0 | 1.254 | 1.4884 | 26.26 | 6.3733 | 25.006
39043.5545 | 2467 | 0 | 39043.5545 | 2245 | 0 |  | 1188 | 1378 | 150.6105 | 0 | 137.0574 | 0 | 1.5061 | 0 | 1.3706 | 0 | 1.5061 | 1.3706 | 5.1228 | 15.518 | 3.6167
39043.555 | 2221 | 0 | 39043.555 | 2393 | 0 |  | 1230 | 1420 | 135.5922 | 0 | 146.0928 | 0 | 1.3559 | 0 | 1.4609 | 0 | 1.3559 | 1.4609 | 16.7663 | 8.3736 | 15.4104
39043.5555 | 2548 | 0 | 39043.5555 | 1471 | 0 |  | 1272 | 1462 | 155.5556 | 0 | 89.8046 | 0 | 1.5556 | 0 | 0.89805 | 0 | 1.5556 | 0.89805 | 1.781 | 76.3005 | 0.22545
39043.556 | 2390 | 0 | 39043.556 | 906 | 0 |  | 1314 | 1504 | 145.9096 | 0 | 55.3114 | 0 | 1.4591 | 0 | 0.55311 | 0 | 1.4591 | 0.55311 | 8.5096 | 186.245 | 7.0505
39043.5565 | 2541 | 0 | 39043.5565 | 350 | 0 |  | 1355.5 | 1545.5 | 155.1282 | 0 | 21.3675 | 0 | 1.5513 | 0 | 0.21368 | 0 | 1.5513 | 0.21368 | 2.0614 | 640.9657 | 0.51011
39043.5569 | 2235 | 0 | 39043.557 | 40 | 0 |  | 1398 | 1588 | 136.4469 | 0 | 2.442 | 0 | 1.3645 | 0 | 0.02442 | 0 | 1.3645 | 0.02442 | 16.0349 | 6383.45 | 14.6704

## B3-C6
Open Burn Test 12 |  |  | 2006-11-22 | 13:02 |  |  | Vs = |  | 157.8376 |  | R = | 100
Mixed | 7-C | Tray C | IRMS | 2
0 | 250 kW |  | Bundle | Ch. 3 & 6 | Cable B | Odd - | Cable C |  | Even
Time-23 | N11 | N12 | Time-24 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R6-G | R3-6
39043.5389 | 0 | 0 | 39043.5389 | 0 | 0 |  | -159 | 31 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 516976 | 516976 | 516975.9997
39043.5394 | 0 | 0 | 39043.5394 | 0 | 0 |  | -116.5 | 73.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 516976 | 516976 | 516975.9997
39043.5399 | 0 | 0 | 39043.5399 | 0 | 0 |  | -74.5 | 115.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 516976 | 516976 | 516975.9997
39043.5404 | 0 | 0 | 39043.5404 | 0 | 0 |  | -33 | 157 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 516976 | 516976 | 516975.9997
39043.5409 | 0 | 0 | 39043.5409 | 0 | 0 |  | 9.5 | 199.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 516976 | 516976 | 516975.9997
39043.5414 | 0 | 0 | 39043.5414 | 0 | 0 |  | 51 | 241 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 516976 | 516976 | 516975.9997
39043.5418 | 0 | 0 | 39043.5419 | 0 | 0 |  | 93 | 283 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 516976 | 516976 | 516975.9997
39043.5423 | 0 | 0 | 39043.5423 | 0 | 0 |  | 135 | 325 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 516976 | 516976 | 516975.9997
39043.5428 | 0 | 0 | 39043.5428 | 0 | 0 |  | 177 | 367 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 516976 | 516976 | 516975.9997
39043.5433 | 0 | 0 | 39043.5433 | 0 | 0 |  | 219 | 409 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 516976 | 516976 | 516975.9997
39043.5438 | 0 | 0 | 39043.5438 | 0 | 0 |  | 261 | 451 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 516976 | 516976 | 516975.9997
39043.5443 | 0 | 0 | 39043.5443 | 0 | 0 |  | 303 | 493 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 516976 | 516976 | 516975.9997
39043.5448 | 663 | 1 | 39043.5448 | 0 | 0 |  | 345 | 535 | 40.4762 | 0.06105 | 0.030525 | 0 | 0.40476 | 0.0006105 | 0.00030525 | 0 | 0.40415 | 0.00030525 | 290.3898 | 516976.0002 | 192100.8414
39043.5452 | 1460 | 1 | 39043.5453 | 941 | 0 |  | 387 | 577 | 89.1331 | 0.06105 | 57.4481 | 0 | 0.89133 | 0.0006105 | 0.57448 | 0 | 0.89072 | 0.57448 | 77.1639 | 174.7481 | 71513.9741
39043.5457 | 1659 | 0 | 39043.5458 | 1771 | 0 |  | 429.5 | 619.5 | 101.2821 | 0 | 108.1197 | 0 | 1.0128 | 0 | 1.0812 | 0 | 1.0128 | 1.0812 | 55.8397 | 45.9842 | 54.8268
39043.5462 | 2027 | 0 | 39043.5462 | 1995 | 0 |  | 471 | 661 | 123.7485 | 0 | 121.7949 | 0 | 1.2375 | 0 | 1.2179 | 0 | 1.2375 | 1.2179 | 27.5471 | 29.593 | 26.3096
39043.5467 | 2383 | 0 | 39043.5467 | 2225 | 0 |  | 513 | 703 | 145.4823 | 0 | 135.8364 | 0 | 1.4548 | 0 | 1.3584 | 0 | 1.4548 | 1.3584 | 8.4927 | 16.1969 | 7.0378
39043.5472 | 2334 | 0 | 39043.5472 | 2098 | 0 |  | 555 | 745 | 142.4908 | 0 | 128.083 | 0 | 1.4249 | 0 | 1.2808 | 0 | 1.4249 | 1.2808 | 10.7704 | 23.2307 | 9.3454
39043.5477 | 2546 | 0 | 39043.5477 | 2081 | 0 |  | 597 | 787 | 155.4335 | 0 | 127.0452 | 0 | 1.5543 | 0 | 1.2705 | 0 | 1.5543 | 1.2705 | 1.5467 | 24.2374 | 0.0075946
39043.5482 | 2556 | 0 | 39043.5482 | 2488 | 0 |  | 639 | 829 | 156.044 | 0 | 151.8926 | 0 | 1.5604 | 0 | 1.5189 | 0 | 1.5604 | 1.5189 | 1.1495 | 3.914 | 0.41099
39043.5486 | 2469 | 1 | 39043.5487 | 2507 | 1 |  | 681 | 871 | 150.7326 | 0.06105 | 153.0525 | 0.06105 | 1.5073 | 0.0006105 | 1.5305 | 0.0006105 | 1.5067 | 1.5299 | 4.7769 | 3.154 | 352.7862
39043.5491 | 2004 | 0 | 39043.5492 | 2312 | 1 |  | 723 | 913 | 122.3443 | 0 | 141.1477 | 0.06105 | 1.2234 | 0 | 1.4115 | 0.0006105 | 1.2234 | 1.4109 | 29.011 | 11.8728 | 27.7875
39043.5496 | 1964 | 1 | 39043.5496 | 1952 | 0 |  | 765 | 955 | 119.9023 | 0.06105 | 119.1697 | 0 | 1.199 | 0.0006105 | 1.1917 | 0 | 1.1984 | 1.1917 | 31.7044 | 32.4477 | 15198.3958
39043.5501 | 2078 | 1 | 39043.5501 | 2336 | 0 |  | 807 | 997 | 126.862 | 0.06105 | 142.6129 | 0 | 1.2686 | 0.0006105 | 1.4261 | 0 | 1.268 | 1.4261 | 24.5392 | 10.6755 | 4884.4288
| 2069 | 1 | 39043.5506 | 1985 | 0 |  | 850 | 1040 | 126.3126 | 0.06105 | 121.1844 | 0 | 1.2631 | 0.0006105 | 1.2118 | 0 | 1.2625 | 1.2118 | 25.01 | 30.2458 | 11968.2153
39043.5511 | 2059 | 1 | 39043.5511 | 2009 | 1 |  | 891 | 1081 | 125.7021 | 0.06105 | 122.6496 | 0.06105 | 1.257 | 0.0006105 | 1.2265 | 0.0006105 | 1.2564 | 1.2259 | 25.6205 | 28.7601 | 11734.983
39043.5516 | 2007 | 1 | 39043.5516 | 2013 | 0 |  | 933 | 1123 | 122.5275 | 0.06105 | 122.8938 | 0 | 1.2253 | 0.0006105 | 1.2289 | 0 | 1.2247 | 1.2289 | 28.8831 | 28.4342 | 12782.6766
39043.552 | 2376 | 0 | 39043.5521 | 2500 | 0 |  | 975 | 1165 | 145.0549 | 0 | 152.6252 | 0 | 1.4505 | 0 | 1.5263 | 0 | 1.4505 | 1.5263 | 8.8123 | 3.4152 | 7.3617
39043.5525 | 2233 | 0 | 39043.5526 | 2536 | 0 |  | 1017 | 1207 | 136.3248 | 0 | 154.823 | 0 | 1.3632 | 0 | 1.5482 | 0 | 1.3632 | 1.5482 | 15.7806 | 1.9472 | 14.4173
39043.553 | 2554 | 0 | 39043.553 | 2365 | 0 |  | 1059 | 1249 | 155.9219 | 0 | 144.3834 | 0 | 1.5592 | 0 | 1.4438 | 0 | 1.5592 | 1.4438 | 1.2287 | 9.3184 | 0.33056
39043.5535 | 2156 | 1 | 39043.5535 | 2519 | 1 |  | 1101 | 1291 | 131.6239 | 0.06105 | 153.7851 | 0.06105 | 1.3162 | 0.0006105 | 1.5379 | 0.0006105 | 1.3156 | 1.5372 | 20.2811 | 2.6414 | 1102.4006
39043.554 | 2204 | 1 | 39043.554 | 2533 | 1 |  | 1143 | 1333 | 134.5543 | 0.06105 | 154.6398 | 0.06105 | 1.3455 | 0.0006105 | 1.5464 | 0.0006105 | 1.3449 | 1.5458 | 17.6993 | 2.0733 | 772.6402
39043.5545 | 1932 | 0 | 39043.5545 | 1933 | 0 |  | 1185 | 1375 | 117.9487 | 0 | 118.0098 | 0 | 1.1795 | 0 | 1.1801 | 0 | 1.1795 | 1.1801 | 33.8188 | 33.7496 | 32.6394
39043.555 | 1922 | 0 | 39043.555 | 1867 | 0 |  | 1227 | 1417 | 117.3382 | 0 | 113.9805 | 0 | 1.1734 | 0 | 1.1398 | 0 | 1.1734 | 1.1398 | 34.5151 | 38.4778 | 33.3417
39043.5555 | 1988 | 0 | 39043.5555 | 1799 | 0 |  | 1269 | 1459 | 121.3675 | 0 | 109.8291 | 0 | 1.2137 | 0 | 1.0983 | 0 | 1.2137 | 1.0983 | 30.0493 | 43.7121 | 28.8356
39043.5559 | 2569 | 0 | 39043.556 | 714 | 0 |  | 1311 | 1501 | 156.8376 | 0 | 43.5897 | 0 | 1.5684 | 0 | 0.4359 | 0 | 1.5684 | 0.4359 | 0.6376 | 262.098 | 0.93077
39043.5564 | 2001 | 0 | 39043.5564 | 1692 | 1 |  | 1353 | 1543 | 122.1612 | 0 | 103.2967 | 0.06105 | 1.2216 | 0 | 1.033 | 0.0006105 | 1.2216 | 1.0324 | 29.2044 | 52.8906 | 27.9828
39043.5569 | 2443 | 0 | 39043.5569 | 474 | 0 |  | 1395 | 1585 | 149.1453 | 0 | 28.9377 | 0 | 1.4915 | 0 | 0.28938 | 0 | 1.4915 | 0.28938 | 5.8281 | 445.4388 | 4.3366

## B3-C5
Open Burn Test 12 |  |  | 2006-11-22 | 13:02 |  |  | Vs = |  | 158.265 |  | R = | 100
Mixed | 7-C | Tray C | IRMS | 2
0 | 250 kW |  | Bundle | Ch. 3 & 5 | Cable B | Odd - | Cable C |  | Odd
Time-21 | N11 | N12 | Time-22 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R5-G | R3-5
39043.5389 | 0 | 0 | 39043.5389 | 0 | 0 |  | -161.5 | 28.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518376 | 518376 | 518375.9997
39043.5394 | 0 | 0 | 39043.5394 | 0 | 0 |  | -119.5 | 70.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518376 | 518376 | 518375.9997
39043.5399 | 0 | 0 | 39043.5399 | 0 | 0 |  | -77.5 | 112.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518376 | 518376 | 518375.9997
39043.5404 | 0 | 0 | 39043.5404 | 0 | 0 |  | -35.5 | 154.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518376 | 518376 | 518375.9997
39043.5408 | 0 | 0 | 39043.5409 | 0 | 0 |  | 6.5 | 196.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518376 | 518376 | 518375.9997
39043.5413 | 0 | 0 | 39043.5413 | 0 | 0 |  | 48.5 | 238.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518376 | 518376 | 518375.9997
39043.5418 | 0 | 0 | 39043.5418 | 0 | 0 |  | 90.5 | 280.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518376 | 518376 | 518375.9997
39043.5423 | 0 | 0 | 39043.5423 | 0 | 0 |  | 132.5 | 322.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518376 | 518376 | 518375.9997
39043.5428 | 0 | 0 | 39043.5428 | 0 | 0 |  | 174.5 | 364.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518376 | 518376 | 518375.9997
39043.5433 | 0 | 0 | 39043.5433 | 0 | 0 |  | 216.5 | 406.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518376 | 518376 | 518375.9997
39043.5438 | 0 | 0 | 39043.5438 | 0 | 0 |  | 258.5 | 448.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518376 | 518376 | 518375.9997
39043.5442 | 0 | 0 | 39043.5443 | 0 | 0 |  | 300.5 | 490.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518376 | 518376 | 518375.9997
39043.5447 | 972 | 1 | 39043.5447 | 0 | 0 |  | 342.5 | 532.5 | 59.3407 | 0.06105 | 0.030525 | 0 | 0.59341 | 0.0006105 | 0.00030525 | 0 | 0.5928 | 0.00030525 | 166.8775 | 518376.0004 | 161906.7665
39043.5452 | 1554 | 0 | 39043.5452 | 29 | 0 |  | 384.5 | 574.5 | 94.8718 | 0 | 1.7705 | 0 | 0.94872 | 0 | 0.017705 | 0 | 0.94872 | 0.017705 | 66.8198 | 8839.2414 | 65.8711
39043.5457 | 1768 | 0 | 39043.5457 | 1044 | 0 |  | 426.5 | 616.5 | 107.9365 | 0 | 63.7363 | 0 | 1.0794 | 0 | 0.63736 | 0 | 1.0794 | 0.63736 | 46.6278 | 148.3123 | 45.5485
39043.5462 | 1871 | 0 | 39043.5462 | 2136 | 0 |  | 468.5 | 658.5 | 114.2247 | 0 | 130.4029 | 0 | 1.1422 | 0 | 1.304 | 0 | 1.1422 | 1.304 | 38.5559 | 21.3661 | 37.4136
39043.5467 | 1893 | 0 | 39043.5467 | 2058 | 0 |  | 510.5 | 700.5 | 115.5678 | 0 | 125.641 | 0 | 1.1557 | 0 | 1.2564 | 0 | 1.1557 | 1.2564 | 36.9456 | 25.966 | 35.7899
39043.5472 | 2505 | 0 | 39043.5472 | 2299 | 0 |  | 552.5 | 742.5 | 152.9304 | 0 | 140.3541 | 0 | 1.5293 | 0 | 1.4035 | 0 | 1.5293 | 1.4035 | 3.4882 | 12.7612 | 1.9589
39043.5477 | 2195 | 0 | 39043.5477 | 2421 | 0 |  | 594.5 | 784.5 | 134.0049 | 0 | 147.8022 | 0 | 1.34 | 0 | 1.478 | 0 | 1.34 | 1.478 | 18.1039 | 7.0789 | 16.7638
39043.5481 | 2318 | 0 | 39043.5481 | 2045 | 0 |  | 636.5 | 826.5 | 141.514 | 0 | 124.8474 | 0 | 1.4151 | 0 | 1.2485 | 0 | 1.4151 | 1.2485 | 11.8369 | 26.7667 | 10.4218
39043.5486 | 2103 | 1 | 39043.5486 | 2110 | 1 |  | 678.5 | 868.5 | 128.3883 | 0.06105 | 128.8156 | 0.06105 | 1.2839 | 0.0006105 | 1.2882 | 0.0006105 | 1.2833 | 1.2875 | 23.3301 | 22.919 | 9106.1544
39043.5491 | 2532 | 0 | 39043.5491 | 1994 | 0 |  | 720.5 | 910.5 | 154.5788 | 0 | 121.7338 | 0 | 1.5458 | 0 | 1.2173 | 0 | 1.5458 | 1.2173 | 2.3847 | 30.009 | 0.83889
39043.5496 | 2304 | 0 | 39043.5496 | 2128 | 0 |  | 762.5 | 952.5 | 140.6593 | 0 | 129.9145 | 0 | 1.4066 | 0 | 1.2991 | 0 | 1.4066 | 1.2991 | 12.5165 | 21.8224 | 11.1099
39043.5501 | 2264 | 1 | 39043.5501 | 2576 | 1 |  | 804.5 | 994.5 | 138.2173 | 0.06105 | 157.265 | 0.06105 | 1.3822 | 0.0006105 | 1.5726 | 0.0006105 | 1.3816 | 1.572 | 15.5912 | 0.6377 | 207.4489
39043.5506 | 2024 | 0 | 39043.5506 | 2507 | 0 |  | 846.5 | 1036.5 | 123.5653 | 0 | 153.0525 | 0 | 1.2357 | 0 | 1.5305 | 0 | 1.2357 | 1.5305 | 28.082 | 3.4057 | 26.8464
39043.5511 | 2239 | 0 | 39043.5511 | 2344 | 0 |  | 888.5 | 1078.5 | 136.6911 | 0 | 143.1013 | 0 | 1.3669 | 0 | 1.431 | 0 | 1.3669 | 1.431 | 15.7829 | 10.5964 | 14.416
39043.5515 | 2183 | 0 | 39043.5516 | 2425 | 1 |  | 930.5 | 1120.5 | 133.2723 | 0 | 148.0464 | 0.06105 | 1.3327 | 0 | 1.4805 | 0.0006105 | 1.3327 | 1.4799 | 18.7531 | 6.9464 | 17.4204
39043.552 | 2086 | 1 | 39043.552 | 2269 | 0 |  | 972.5 | 1162.5 | 127.3504 | 0.06105 | 138.5226 | 0 | 1.2735 | 0.0006105 | 1.3852 | 0 | 1.2729 | 1.3852 | 24.3688 | 14.2521 | 6304.2372
39043.5525 | 2050 | 0 | 39043.5525 | 2218 | 1 |  | 1014.5 | 1204.5 | 125.1526 | 0 | 135.409 | 0.06105 | 1.2515 | 0 | 1.3541 | 0.0006105 | 1.2515 | 1.3535 | 26.4576 | 16.9319 | 25.206
39043.553 | 2213 | 0 | 39043.553 | 2510 | 1 |  | 1056 | 1246 | 135.1038 | 0 | 153.2357 | 0.06105 | 1.351 | 0 | 1.5324 | 0.0006105 | 1.351 | 1.5317 | 17.1432 | 3.3232 | 15.7922
39043.5535 | 2319 | 1 | 39043.5535 | 1921 | 0 |  | 1098.5 | 1288.5 | 141.5751 | 0.06105 | 117.2772 | 0 | 1.4158 | 0.0006105 | 1.1728 | 0 | 1.4151 | 1.1728 | 11.8084 | 34.9495 | 7054.1543
39043.554 | 2082 | 0 | 39043.554 | 2411 | 0 |  | 1140.5 | 1330.5 | 127.1062 | 0 | 147.1917 | 0 | 1.2711 | 0 | 1.4719 | 0 | 1.2711 | 1.4719 | 24.5139 | 7.523 | 23.2429
39043.5545 | 2086 | 0 | 39043.5545 | 2273 | 0 |  | 1182.5 | 1372.5 | 127.3504 | 0 | 138.7668 | 0 | 1.2735 | 0 | 1.3877 | 0 | 1.2735 | 1.3877 | 24.2752 | 14.051 | 23.0017
39043.5549 | 2459 | 0 | 39043.555 | 2162 | 0 |  | 1224 | 1414 | 150.1221 | 0 | 131.9902 | 0 | 1.5012 | 0 | 1.3199 | 0 | 1.5012 | 1.3199 | 5.4242 | 19.9066 | 3.9229
39043.5554 | 2087 | 0 | 39043.5554 | 1725 | 0 |  | 1266 | 1456 | 127.4115 | 0 | 105.3114 | 0 | 1.2741 | 0 | 1.0531 | 0 | 1.2741 | 1.0531 | 24.2156 | 50.2829 | 22.9415
39043.5559 | 2375 | 0 | 39043.5559 | 359 | 0 |  | 1308.5 | 1498.5 | 144.9939 | 0 | 21.917 | 0 | 1.4499 | 0 | 0.21917 | 0 | 1.4499 | 0.21917 | 9.1528 | 622.1114 | 7.7029
39043.5564 | 2572 | 0 | 39043.5564 | 245 | 0 |  | 1350 | 1540 | 157.0208 | 0 | 14.9573 | 0 | 1.5702 | 0 | 0.14957 | 0 | 1.5702 | 0.14957 | 0.79238 | 958.1143 | 0.77783
39043.5569 | 2573 | 0 | 39043.5569 | 79 | 0 |  | 1392 | 1582 | 157.0818 | 0 | 4.823 | 0 | 1.5708 | 0 | 0.04823 | 0 | 1.5708 | 0.04823 | 0.75321 | 3181.4937 | 0.81761

## B3-B4
Open Burn Test 12 |  |  | 2006-11-22 | 13:02 |  |  | Vs = |  | 159.1197 |  | R = | 100
Mixed | 7-C | Tray C | IRMS | 2
0 | 250 kW |  | Bundle | Ch. 3 & 4 | Cable B | Odd -Even
Time-19 | N11 | N12 | Time-20 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R4-G | R3-4
39043.5389 | 0 | 0 | 39043.5389 | 0 | 0 |  | -164.5 | 25.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 521176 | 521176 | 521175.9997
39043.5394 | 0 | 0 | 39043.5394 | 0 | 0 |  | -122.5 | 67.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 521176 | 521176 | 521175.9997
39043.5398 | 0 | 0 | 39043.5398 | 0 | 0 |  | -80.5 | 109.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 521176 | 521176 | 521175.9997
39043.5403 | 0 | 0 | 39043.5403 | 0 | 0 |  | -38.5 | 151.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 521176 | 521176 | 521175.9997
39043.5408 | 0 | 0 | 39043.5408 | 0 | 0 |  | 3.5 | 193.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 521176 | 521176 | 521175.9997
39043.5413 | 0 | 0 | 39043.5413 | 0 | 0 |  | 45.5 | 235.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 521176 | 521176 | 521175.9997
39043.5418 | 0 | 0 | 39043.5418 | 0 | 0 |  | 87.5 | 277.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 521176 | 521176 | 521175.9997
39043.5423 | 0 | 0 | 39043.5423 | 0 | 0 |  | 129.5 | 319.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 521176 | 521176 | 521175.9997
39043.5428 | 0 | 0 | 39043.5428 | 0 | 0 |  | 171.5 | 361.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 521176 | 521176 | 521175.9997
39043.5432 | 0 | 0 | 39043.5433 | 0 | 0 |  | 213.5 | 403.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 521176 | 521176 | 521175.9997
39043.5437 | 0 | 0 | 39043.5437 | 0 | 0 |  | 255.5 | 445.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 521176 | 521176 | 521175.9997
39043.5442 | 0 | 0 | 39043.5442 | 0 | 0 |  | 297.5 | 487.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 521176 | 521176 | 521175.9997
39043.5447 | 0 | 0 | 39043.5447 | 1082 | 1 |  | 339.5 | 529.5 | 0.030525 | 0 | 66.0562 | 0.06105 | 0.00030525 | 0 | 0.66056 | 0.0006105 | 0.00030525 | 0.65995 | 521176 | 141.1082 | 521175.9997
39043.5452 | 1384 | 190 | 39043.5452 | 1407 | 82 |  | 381.5 | 571.5 | 84.4933 | 11.5995 | 85.8974 | 5.0061 | 0.84493 | 0.116 | 0.85897 | 0.050061 | 0.72894 | 0.80891 | 122.893 | 95.3194 | 265.1684
39043.5457 | 1747 | 274 | 39043.5457 | 2064 | 249 |  | 423.5 | 613.5 | 106.6545 | 16.7277 | 126.0073 | 15.2015 | 1.0665 | 0.16728 | 1.2601 | 0.15201 | 0.89927 | 1.1081 | 131.9177 | 33.3517 | 53.4326
39043.5462 | 2180 | 120 | 39043.5462 | 2125 | 80 |  | 465.5 | 655.5 | 133.0891 | 7.326 | 129.7314 | 4.884 | 1.3309 | 0.07326 | 1.2973 | 0.04884 | 1.2576 | 1.2485 | 26.2181 | 27.6676 | 55.3312
39043.5466 | 2379 | 32 | 39043.5467 | 2022 | 29 |  | 507.5 | 697.5 | 145.2381 | 1.9536 | 123.4432 | 1.7705 | 1.4524 | 0.019536 | 1.2344 | 0.017705 | 1.4328 | 1.2167 | 10.0896 | 34.2629 | 155.8111
39043.5471 | 2011 | 4 | 39043.5471 | 2162 | 4 |  | 549.5 | 739.5 | 122.7717 | 0.2442 | 131.9902 | 0.2442 | 1.2277 | 0.002442 | 1.3199 | 0.002442 | 1.2253 | 1.3175 | 29.9533 | 20.7204 | 2537.6093
39043.5476 | 1989 | 1 | 39043.5476 | 2230 | 1 |  | 591.5 | 781.5 | 121.4286 | 0.06105 | 136.1416 | 0.06105 | 1.2143 | 0.0006105 | 1.3614 | 0.0006105 | 1.2137 | 1.3608 | 31.148 | 16.91 | 8915.3724
39043.5481 | 2168 | 0 | 39043.5481 | 2056 | 1 |  | 633.5 | 823.5 | 132.3565 | 0 | 125.5189 | 0.06105 | 1.3236 | 0 | 1.2552 | 0.0006105 | 1.3236 | 1.2546 | 20.2205 | 26.8311 | 18.8969
39043.5486 | 2005 | 1 | 39043.5486 | 1970 | 1 |  | 675.5 | 865.5 | 122.4054 | 0.06105 | 120.2686 | 0.06105 | 1.2241 | 0.0006105 | 1.2027 | 0.0006105 | 1.2234 | 1.2021 | 30.0553 | 32.3747 | 14683.4001
39043.5491 | 2316 | 1 | 39043.5491 | 2450 | 1 |  | 717.5 | 907.5 | 141.3919 | 0.06105 | 149.5726 | 0.06105 | 1.4139 | 0.0006105 | 1.4957 | 0.0006105 | 1.4133 | 1.4951 | 12.6286 | 6.4062 | 1742.2104
39043.5496 | 2487 | 1 | 39043.5496 | 2546 | 1 |  | 759.5 | 949.5 | 151.8315 | 0.06105 | 155.4335 | 0.06105 | 1.5183 | 0.0006105 | 1.5543 | 0.0006105 | 1.5177 | 1.5537 | 4.8842 | 2.3917 | 276.5201
39043.55 | 2542 | 1 | 39043.5501 | 2334 | 1 |  | 801.5 | 991.5 | 155.1893 | 0.06105 | 142.4908 | 0.06105 | 1.5519 | 0.0006105 | 1.4249 | 0.0006105 | 1.5513 | 1.4243 | 2.5421 | 11.8753 | 672.7655
39043.5505 | 2486 | 1 | 39043.5505 | 2071 | 1 |  | 843.5 | 1033.5 | 151.7705 | 0.06105 | 126.4347 | 0.06105 | 1.5177 | 0.0006105 | 1.2643 | 0.0006105 | 1.5171 | 1.2637 | 4.8517 | 26.1239 | 2472.7033
39043.551 | 1982 | 1 | 39043.551 | 2590 | 1 |  | 885.5 | 1075.5 | 121.0012 | 0.06105 | 158.1197 | 0.06105 | 1.21 | 0.0006105 | 1.5812 | 0.0006105 | 1.2094 | 1.5806 | 34.2479 | 0.63339 | 392.3582
39043.5515 | 2037 | 1 | 39043.5515 | 2314 | 1 |  | 927.5 | 1117.5 | 124.359 | 0.06105 | 141.2698 | 0.06105 | 1.2436 | 0.0006105 | 1.4127 | 0.0006105 | 1.243 | 1.4121 | 28.0745 | 12.6602 | 6387.1855
39043.552 | 2574 | 1 | 39043.552 | 2564 | 1 |  | 969.5 | 1159.5 | 157.1429 | 0.06105 | 156.5324 | 0.06105 | 1.5714 | 0.0006105 | 1.5653 | 0.0006105 | 1.5708 | 1.5647 | 1.2878 | 1.7052 | 52.6118
39043.5525 | 2475 | 1 | 39043.5525 | 2032 | 2 |  | 1011.5 | 1201.5 | 151.0989 | 0.06105 | 124.0537 | 0.1221 | 1.511 | 0.0006105 | 1.2405 | 0.001221 | 1.5104 | 1.2393 | 5.3179 | 28.8287 | 2917.5825
39043.553 | 2028 | 1 | 39043.553 | 2048 | 2 |  | 1053.5 | 1243.5 | 123.8095 | 0.06105 | 125.0305 | 0.1221 | 1.2381 | 0.0006105 | 1.2503 | 0.001221 | 1.2375 | 1.2491 | 28.5853 | 27.3849 | 12412.3934
39043.5534 | 2074 | 2 | 39043.5535 | 2015 | 2 |  | 1095.5 | 1285.5 | 126.6178 | 0.1221 | 123.0159 | 0.1221 | 1.2662 | 0.001221 | 1.2302 | 0.001221 | 1.265 | 1.2289 | 25.7784 | 29.4917 | 6039.6965
39043.5539 | 2167 | 2 | 39043.5539 | 2379 | 1 |  | 1137.5 | 1327.5 | 132.2955 | 0.1221 | 145.2381 | 0.06105 | 1.323 | 0.001221 | 1.4524 | 0.0006105 | 1.3217 | 1.4518 | 20.4923 | 9.5815 | 1912.1604
39043.5544 | 2496 | 2 | 39043.5544 | 2038 | 2 |  | 1179.5 | 1369.5 | 152.381 | 0.1221 | 124.42 | 0.1221 | 1.5238 | 0.001221 | 1.2442 | 0.001221 | 1.5226 | 1.243 | 4.4383 | 28.5484 | 1203.4658
39043.5549 | 2180 | 5 | 39043.5549 | 1988 | 7 |  | 1221.5 | 1411.5 | 133.0891 | 0.30525 | 121.3675 | 0.42735 | 1.3309 | 0.0030525 | 1.2137 | 0.0042735 | 1.3278 | 1.2094 | 19.7465 | 31.7843 | 2032.6054
39043.5554 | 1972 | 80 | 39043.5554 | 2407 | 4 |  | 1263.5 | 1453.5 | 120.3907 | 4.884 | 146.9475 | 0.2442 | 1.2039 | 0.04884 | 1.4695 | 0.002442 | 1.1551 | 1.467 | 68.2009 | 8.3174 | 53.2118
39043.5559 | 2165 | 1 | 39043.5559 | 2026 | 1 |  | 1305.5 | 1495.5 | 132.1734 | 0.06105 | 123.6874 | 0.06105 | 1.3217 | 0.0006105 | 1.2369 | 0.0006105 | 1.3211 | 1.2363 | 20.4293 | 28.7302 | 9828.4642
39043.5564 | 2404 | 1 | 39043.5564 | 2046 | 1 |  | 1347.5 | 1537.5 | 146.7643 | 0.06105 | 124.9084 | 0.06105 | 1.4676 | 0.0006105 | 1.2491 | 0.0006105 | 1.467 | 1.2485 | 8.4347 | 27.5622 | 4351.1961
39043.5569 | 2239 | 1 | 39043.5569 | 2238 | 0 |  | 1389.5 | 1579.5 | 136.6911 | 0.06105 | 136.63 | 0 | 1.3669 | 0.0006105 | 1.3663 | 0 | 1.3663 | 1.3663 | 16.4602 | 16.4602 | 5178.3341

## A2-C6
Open Burn Test 12 |  |  | 2006-11-22 | 13:02 |  |  | Vs = |  | 159.0586 |  | R = | 100
Mixed | 7-C | Tray C | IRMS | 2
0 | 250 kW |  | Bundle | Ch. 2 & 6 | Cable A | Even - | Cable C |  | Even
Time-17 | N11 | N12 | Time-18 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R6-G | R2-6
39043.5388 | 0 | 0 | 39043.5388 | 0 | 0 |  | -167.5 | 22.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 520976 | 520976 | 520975.9997
39043.5393 | 0 | 0 | 39043.5393 | 0 | 0 |  | -125 | 65 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 520976 | 520976 | 520975.9997
39043.5398 | 0 | 0 | 39043.5398 | 0 | 0 |  | -83.5 | 106.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 520976 | 520976 | 520975.9997
39043.5403 | 0 | 0 | 39043.5403 | 0 | 0 |  | -41 | 149 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 520976 | 520976 | 520975.9997
39043.5408 | 0 | 0 | 39043.5408 | 0 | 0 |  | 1 | 191 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 520976 | 520976 | 520975.9997
39043.5413 | 0 | 0 | 39043.5413 | 0 | 0 |  | 43 | 233 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 520976 | 520976 | 520975.9997
39043.5417 | 0 | 0 | 39043.5418 | 0 | 0 |  | 85 | 275 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 520976 | 520976 | 520975.9997
39043.5422 | 0 | 0 | 39043.5422 | 0 | 0 |  | 126.5 | 316.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 520976 | 520976 | 520975.9997
39043.5427 | 0 | 0 | 39043.5427 | 0 | 0 |  | 168.5 | 358.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 520976 | 520976 | 520975.9997
39043.5432 | 0 | 0 | 39043.5432 | 0 | 0 |  | 210.5 | 400.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 520976 | 520976 | 520975.9997
39043.5437 | 0 | 0 | 39043.5437 | 0 | 0 |  | 252.5 | 442.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 520976 | 520976 | 520975.9997
39043.5442 | 0 | 0 | 39043.5442 | 0 | 0 |  | 294.5 | 484.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 520976 | 520976 | 520975.9997
39043.5447 | 1388 | 1 | 39043.5447 | 0 | 0 |  | 336.5 | 526.5 | 84.7375 | 0.06105 | 0.030525 | 0 | 0.84737 | 0.0006105 | 0.00030525 | 0 | 0.84676 | 0.00030525 | 87.7707 | 520976.0006 | 121614.6564
39043.5452 | 1716 | 1 | 39043.5452 | 0 | 0 |  | 378.5 | 568.5 | 104.7619 | 0.06105 | 0.030525 | 0 | 1.0476 | 0.0006105 | 0.00030525 | 0 | 1.047 | 0.00030525 | 51.8589 | 520976.0006 | 88820.951
39043.5456 | 1969 | 0 | 39043.5456 | 1494 | 0 |  | 420.5 | 610.5 | 120.2076 | 0 | 91.2088 | 0 | 1.2021 | 0 | 0.91209 | 0 | 1.2021 | 0.91209 | 32.32 | 74.3896 | 31.1179
39043.5461 | 2009 | 0 | 39043.5461 | 2070 | 0 |  | 462.5 | 652.5 | 122.6496 | 0 | 126.3736 | 0 | 1.2265 | 0 | 1.2637 | 0 | 1.2265 | 1.2637 | 29.6854 | 25.8638 | 28.4589
39043.5466 | 1791 | 0 | 39043.5466 | 1916 | 0 |  | 504.5 | 694.5 | 109.3407 | 0 | 116.9719 | 0 | 1.0934 | 0 | 1.1697 | 0 | 1.0934 | 1.1697 | 45.4707 | 35.9802 | 44.3773
39043.5471 | 2329 | 12 | 39043.5471 | 2296 | 1 |  | 546.5 | 736.5 | 142.1856 | 0.7326 | 140.1709 | 0.06105 | 1.4219 | 0.007326 | 1.4017 | 0.0006105 | 1.4145 | 1.4011 | 12.4032 | 13.5281 | 262.5317
39043.5476 | 2434 | 0 | 39043.5476 | 2442 | 0 |  | 588.5 | 778.5 | 148.5958 | 0 | 149.0842 | 0 | 1.486 | 0 | 1.4908 | 0 | 1.486 | 1.4908 | 7.0411 | 6.6904 | 5.5551
39043.5481 | 2174 | 0 | 39043.5481 | 2546 | 0 |  | 630.5 | 820.5 | 132.7228 | 0 | 155.4335 | 0 | 1.3272 | 0 | 1.5543 | 0 | 1.3272 | 1.5543 | 19.8427 | 2.3323 | 18.5155
39043.5486 | 2085 | 1 | 39043.5486 | 2446 | 1 |  | 672.5 | 862.5 | 127.2894 | 0.06105 | 149.3284 | 0.06105 | 1.2729 | 0.0006105 | 1.4933 | 0.0006105 | 1.2723 | 1.4927 | 25.1551 | 6.5292 | 3183.3039
39043.549 | 2323 | 0 | 39043.5491 | 2400 | 0 |  | 714.5 | 904.5 | 141.8193 | 0 | 146.5201 | 0 | 1.4182 | 0 | 1.4652 | 0 | 1.4182 | 1.4652 | 12.1558 | 8.5575 | 10.7376
39043.5495 | 2468 | 1 | 39043.5495 | 1984 | 0 |  | 756.5 | 946.5 | 150.6716 | 0.06105 | 121.1233 | 0 | 1.5067 | 0.0006105 | 1.2112 | 0 | 1.5061 | 1.2112 | 5.5759 | 31.3196 | 3252.6466
39043.55 | 2387 | 1 | 39043.55 | 2117 | 0 |  | 798.5 | 988.5 | 145.7265 | 0.06105 | 129.243 | 0 | 1.4573 | 0.0006105 | 1.2924 | 0 | 1.4567 | 1.2924 | 9.1692 | 23.0694 | 4074.8008
39043.5505 | 2007 | 0 | 39043.5505 | 2157 | 1 |  | 840.5 | 1030.5 | 122.5275 | 0 | 131.685 | 0.06105 | 1.2253 | 0 | 1.3168 | 0.0006105 | 1.2253 | 1.3162 | 29.8146 | 20.8432 | 28.5894
39043.551 | 2027 | 1 | 39043.551 | 1967 | 1 |  | 882.5 | 1072.5 | 123.7485 | 0.06105 | 120.0855 | 0.06105 | 1.2375 | 0.0006105 | 1.2009 | 0.0006105 | 1.2369 | 1.2002 | 28.5913 | 32.5289 | 14171.6458
39043.5515 | 2125 | 0 | 39043.5515 | 2264 | 1 |  | 924.5 | 1114.5 | 129.7314 | 0 | 138.2173 | 0.06105 | 1.2973 | 0 | 1.3822 | 0.0006105 | 1.2973 | 1.3816 | 22.6061 | 15.1295 | 21.3088
39043.552 | 2110 | 1 | 39043.552 | 2043 | 0 |  | 966.5 | 1156.5 | 128.8156 | 0.06105 | 124.7253 | 0 | 1.2882 | 0.0006105 | 1.2473 | 0 | 1.2875 | 1.2473 | 23.5294 | 27.5272 | 10671.3579
39043.5524 | 2429 | 0 | 39043.5525 | 2164 | 0 |  | 1008.5 | 1198.5 | 148.2906 | 0 | 132.1123 | 0 | 1.4829 | 0 | 1.3211 | 0 | 1.4829 | 1.3211 | 7.2614 | 20.3965 | 5.7785
39043.5529 | 2178 | 1 | 39043.5529 | 2154 | 1 |  | 1050.5 | 1240.5 | 132.967 | 0.06105 | 131.5018 | 0.06105 | 1.3297 | 0.0006105 | 1.315 | 0.0006105 | 1.3291 | 1.3144 | 19.6746 | 21.0148 | 7404.2859
39043.5534 | 2427 | 1 | 39043.5534 | 2535 | 1 |  | 1092.5 | 1282.5 | 148.1685 | 0.06105 | 154.7619 | 0.06105 | 1.4817 | 0.0006105 | 1.5476 | 0.0006105 | 1.4811 | 1.547 | 7.463 | 2.7922 | 481.8255
39043.5539 | 2589 | 1 | 39043.5539 | 2503 | 0 |  | 1134.5 | 1324.5 | 158.0586 | 0.06105 | 152.8083 | 0 | 1.5806 | 0.0006105 | 1.5281 | 0 | 1.58 | 1.5281 | 0.63896 | 4.0903 | 60.4367
39043.5544 | 2087 | 0 | 39043.5544 | 1929 | 1 |  | 1176.5 | 1366.5 | 127.4115 | 0 | 117.7656 | 0.06105 | 1.2741 | 0 | 1.1777 | 0.0006105 | 1.2741 | 1.177 | 24.8385 | 35.1338 | 23.5644
39043.5549 | 2076 | 1 | 39043.5549 | 2254 | 0 |  | 1218.5 | 1408.5 | 126.7399 | 0.06105 | 137.6068 | 0 | 1.2674 | 0.0006105 | 1.3761 | 0 | 1.2668 | 1.3761 | 25.5914 | 15.5892 | 7126.1069
39043.5554 | 2261 | 0 | 39043.5554 | 2138 | 0 |  | 1260.5 | 1450.5 | 138.0342 | 0 | 130.525 | 0 | 1.3803 | 0 | 1.3053 | 0 | 1.3803 | 1.3053 | 15.2313 | 21.8606 | 13.851
39043.5558 | 2478 | 0 | 39043.5559 | 1914 | 1 |  | 1302.5 | 1492.5 | 151.2821 | 0 | 116.8498 | 0.06105 | 1.5128 | 0 | 1.1685 | 0.0006105 | 1.5128 | 1.1679 | 5.1404 | 36.1934 | 3.6276
39043.5563 | 1959 | 0 | 39043.5563 | 2146 | 1 |  | 1344.5 | 1534.5 | 119.5971 | 0 | 131.0134 | 0.06105 | 1.196 | 0 | 1.3101 | 0.0006105 | 1.196 | 1.3095 | 32.9954 | 21.4629 | 31.7994
39043.5568 | 1952 | 0 | 39043.5568 | 2195 | 4 |  | 1386.5 | 1576.5 | 119.1697 | 0 | 134.0049 | 0.2442 | 1.1917 | 0 | 1.34 | 0.002442 | 1.1917 | 1.3376 | 33.4723 | 18.9128 | 32.2806

## A2-C5
Open Burn Test 12 |  |  | 2006-11-22 | 13:02 |  |  | Vs = |  | 160.707 |  | R = | 100
Mixed | 7-C | Tray C | IRMS | 2
0 | 250 kW |  | Bundle | Ch. 2 & 5 | Cable A | Even - | Cable C |  | Odd
Time-15 | N11 | N12 | Time-16 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R5-G | R2-5
39043.5388 | 0 | 0 | 39043.5388 | 0 | 0 |  | -170 | 20 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 526376 | 526376 | 526375.9997
39043.5393 | 0 | 0 | 39043.5393 | 0 | 1 |  | -128 | 62 | 0.030525 | 0 | 0.030525 | 0.06105 | 0.00030525 | 0 | 0.00030525 | 0.0006105 | 0.00030525 | 0.00030525 | 526376 | 526376 | 526375.9997
39043.5398 | 0 | 0 | 39043.5398 | 0 | 0 |  | -86 | 104 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 526376 | 526376 | 526375.9997
39043.5403 | 0 | 0 | 39043.5403 | 0 | 0 |  | -44 | 146 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 526376 | 526376 | 526375.9997
39043.5407 | 0 | 0 | 39043.5408 | 0 | 0 |  | -2 | 188 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 526376 | 526376 | 526375.9997
39043.5412 | 0 | 0 | 39043.5413 | 0 | 0 |  | 40 | 230 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 526376 | 526376 | 526375.9997
39043.5417 | 0 | 0 | 39043.5417 | 0 | 0 |  | 82 | 272 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 526376 | 526376 | 526375.9997
39043.5422 | 0 | 0 | 39043.5422 | 0 | 0 |  | 124 | 314 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 526376 | 526376 | 526375.9997
39043.5427 | 0 | 0 | 39043.5427 | 0 | 0 |  | 166 | 356 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 526376 | 526376 | 526375.9997
39043.5432 | 0 | 0 | 39043.5432 | 0 | 0 |  | 208 | 398 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 526376 | 526376 | 526375.9997
39043.5437 | 0 | 0 | 39043.5437 | 0 | 0 |  | 250 | 440 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 526376 | 526376 | 526375.9997
39043.5441 | 0 | 0 | 39043.5442 | 0 | 0 |  | 292 | 482 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 526376 | 526376 | 526375.9997
39043.5446 | 1516 | 1 | 39043.5447 | 0 | 0 |  | 334 | 524 | 92.5519 | 0.06105 | 0.030525 | 0 | 0.92552 | 0.0006105 | 0.00030525 | 0 | 0.92491 | 0.00030525 | 73.6885 | 526376.001 | 111516.8142
39043.5451 | 1980 | 1 | 39043.5451 | 0 | 0 |  | 376 | 566 | 120.8791 | 0.06105 | 0.030525 | 0 | 1.2088 | 0.0006105 | 0.00030525 | 0 | 1.2082 | 0.00030525 | 32.9651 | 526376 | 65125.6275
39043.5456 | 1967 | 0 | 39043.5456 | 1539 | 0 |  | 418 | 608 | 120.0855 | 0 | 93.956 | 0 | 1.2009 | 0 | 0.93956 | 0 | 1.2009 | 0.93956 | 33.8271 | 71.0448 | 32.6263
39043.5461 | 2360 | 0 | 39043.5461 | 2211 | 0 |  | 460 | 650 | 144.0781 | 0 | 134.9817 | 0 | 1.4408 | 0 | 1.3498 | 0 | 1.4408 | 1.3498 | 11.5415 | 19.0583 | 10.1007
39043.5466 | 2367 | 0 | 39043.5466 | 2365 | 0 |  | 502 | 692 | 144.5055 | 0 | 144.3834 | 0 | 1.4451 | 0 | 1.4438 | 0 | 1.4451 | 1.4438 | 11.2117 | 11.3057 | 9.7666
39043.5471 | 2219 | 20 | 39043.5471 | 2432 | 0 |  | 544 | 734 | 135.4701 | 1.221 | 148.4737 | 0 | 1.3547 | 0.01221 | 1.4847 | 0 | 1.3425 | 1.4847 | 21.1311 | 8.2393 | 149.7228
39043.5475 | 2211 | 0 | 39043.5476 | 2007 | 0 |  | 586 | 776 | 134.9817 | 0 | 122.5275 | 0 | 1.3498 | 0 | 1.2253 | 0 | 1.3498 | 1.2253 | 19.0583 | 31.1599 | 17.7085
39043.548 | 1958 | 0 | 39043.5481 | 1999 | 0 |  | 628 | 818 | 119.536 | 0 | 122.0391 | 0 | 1.1954 | 0 | 1.2204 | 0 | 1.1954 | 1.2204 | 34.4423 | 31.6848 | 33.2469
39043.5485 | 1940 | 0 | 39043.5485 | 2131 | 1 |  | 670 | 860 | 118.4371 | 0 | 130.0977 | 0.06105 | 1.1844 | 0 | 1.301 | 0.0006105 | 1.1844 | 1.3004 | 35.6897 | 23.5859 | 34.5053
39043.549 | 2546 | 1 | 39043.549 | 2146 | 1 |  | 712 | 902 | 155.4335 | 0.06105 | 131.0134 | 0.06105 | 1.5543 | 0.0006105 | 1.3101 | 0.0006105 | 1.5537 | 1.3095 | 3.3999 | 22.9903 | 1595.9893
39043.5495 | 2230 | 1 | 39043.5495 | 2577 | 1 |  | 754 | 944 | 136.1416 | 0.06105 | 157.326 | 0.06105 | 1.3614 | 0.0006105 | 1.5733 | 0.0006105 | 1.3608 | 1.5726 | 18.436 | 2.1544 | 846.4889
39043.55 | 2437 | 0 | 39043.55 | 2246 | 0 |  | 796 | 986 | 148.779 | 0 | 137.1184 | 0 | 1.4878 | 0 | 1.3712 | 0 | 1.4878 | 1.3712 | 8.0172 | 17.203 | 6.5294
39043.5505 | 2500 | 0 | 39043.5505 | 2054 | 1 |  | 838 | 1028 | 152.6252 | 0 | 125.3968 | 0.06105 | 1.5263 | 0 | 1.254 | 0.0006105 | 1.5263 | 1.2534 | 5.2952 | 28.2211 | 3.7689
39043.5509 | 2252 | 0 | 39043.551 | 2456 | 1 |  | 880 | 1070 | 137.4847 | 0 | 149.9389 | 0.06105 | 1.3748 | 0 | 1.4994 | 0.0006105 | 1.3748 | 1.4988 | 16.8908 | 7.2253 | 15.5159
39043.5514 | 2346 | 1 | 39043.5515 | 2532 | 1 |  | 922 | 1112 | 143.2234 | 0.06105 | 154.5788 | 0.06105 | 1.4322 | 0.0006105 | 1.5458 | 0.0006105 | 1.4316 | 1.5452 | 12.3447 | 3.9788 | 1092.0089
39043.5519 | 2616 | 1 | 39043.5519 | 2116 | 0 |  | 964 | 1154 | 159.707 | 0.06105 | 129.1819 | 0 | 1.5971 | 0.0006105 | 1.2918 | 0 | 1.5965 | 1.2918 | 0.62737 | 24.4036 | 301.7013
39043.5524 | 2332 | 0 | 39043.5524 | 2020 | 1 |  | 1006 | 1196 | 142.3687 | 0 | 123.3211 | 0.06105 | 1.4237 | 0 | 1.2332 | 0.0006105 | 1.4237 | 1.2326 | 12.8808 | 30.3804 | 11.4571
39043.5529 | 2201 | 1 | 39043.5529 | 1989 | 1 |  | 1047.5 | 1237.5 | 134.3712 | 0.06105 | 121.4286 | 0.06105 | 1.3437 | 0.0006105 | 1.2143 | 0.0006105 | 1.3431 | 1.2137 | 19.6357 | 32.4463 | 10543.3207
39043.5534 | 2609 | 0 | 39043.5534 | 2107 | 0 |  | 1090 | 1280 | 159.2796 | 0 | 128.6325 | 0 | 1.5928 | 0 | 1.2863 | 0 | 1.5928 | 1.2863 | 0.89613 | 24.935 | 0.69667
39043.5539 | 2460 | 1 | 39043.5539 | 1933 | 0 |  | 1132 | 1322 | 150.1832 | 0.06105 | 118.0098 | 0 | 1.5018 | 0.0006105 | 1.1801 | 0 | 1.5012 | 1.1801 | 7.0181 | 36.1811 | 4553.2843
39043.5544 | 2300 | 0 | 39043.5544 | 1926 | 0 |  | 1174 | 1364 | 140.4151 | 0 | 117.5824 | 0 | 1.4042 | 0 | 1.1758 | 0 | 1.4042 | 1.1758 | 14.4513 | 36.676 | 13.0472
39043.5548 | 2115 | 0 | 39043.5548 | 2376 | 0 |  | 1215.5 | 1405.5 | 129.1209 | 0 | 145.0549 | 0 | 1.2912 | 0 | 1.4505 | 0 | 1.2912 | 1.4505 | 24.4624 | 10.7904 | 23.1712
39043.5553 | 2161 | 0 | 39043.5553 | 2080 | 0 |  | 1257.5 | 1447.5 | 131.9292 | 0 | 126.9841 | 0 | 1.3193 | 0 | 1.2698 | 0 | 1.3193 | 1.2698 | 21.813 | 26.5567 | 20.4938
39043.5558 | 2072 | 0 | 39043.5558 | 587 | 0 |  | 1300 | 1490 | 126.4957 | 0 | 35.8364 | 0 | 1.265 | 0 | 0.35836 | 0 | 1.265 | 0.35836 | 27.0454 | 348.4463 | 25.7804
39043.5563 | 2214 | 0 | 39043.5563 | 606 | 0 |  | 1341.5 | 1531.5 | 135.1648 | 0 | 36.9963 | 0 | 1.3516 | 0 | 0.36996 | 0 | 1.3516 | 0.36996 | 18.897 | 334.3861 | 17.5454
39043.5568 | 2393 | 0 | 39043.5568 | 98 | 0 |  | 1383.5 | 1573.5 | 146.0928 | 0 | 5.9829 | 0 | 1.4609 | 0 | 0.059829 | 0 | 1.4609 | 0.059829 | 10.0033 | 2586.102 | 8.5424

## A2-B4
Open Burn Test 12 |  |  | 2006-11-22 | 13:02 |  |  | Vs = |  | 160.4628 |  | R = | 100
Mixed | 7-C | Tray C | IRMS | 2
0 | 250 kW |  | Bundle | Ch. 2 & 4 | Cable A | Even - | Cable B |  | Even
Time-13 | N11 | N12 | Time-14 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R4-G | R2-4
39043.5388 | 0 | 0 | 39043.5388 | 0 | 0 |  | -172.5 | 17.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 525576 | 525576 | 525575.9997
39043.5393 | 0 | 0 | 39043.5393 | 0 | 0 |  | -130.5 | 59.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 525576 | 525576 | 525575.9997
39043.5397 | 0 | 0 | 39043.5398 | 0 | 0 |  | -89 | 101 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 525576 | 525576 | 525575.9997
39043.5402 | 0 | 0 | 39043.5402 | 0 | 0 |  | -47 | 143 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 525576 | 525576 | 525575.9997
39043.5407 | 0 | 0 | 39043.5407 | 0 | 0 |  | -4.5 | 185.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 525576 | 525576 | 525575.9997
39043.5412 | 0 | 0 | 39043.5412 | 0 | 0 |  | 37 | 227 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 525576 | 525576 | 525575.9997
39043.5417 | 0 | 0 | 39043.5417 | 0 | 0 |  | 79.5 | 269.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 525576 | 525576 | 525575.9997
39043.5422 | 0 | 0 | 39043.5422 | 0 | 0 |  | 121 | 311 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 525576 | 525576 | 525575.9997
39043.5427 | 0 | 0 | 39043.5427 | 0 | 0 |  | 163 | 353 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 525576 | 525576 | 525575.9997
39043.5431 | 0 | 0 | 39043.5432 | 0 | 0 |  | 205 | 395 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 525576 | 525576 | 525575.9997
39043.5436 | 0 | 0 | 39043.5436 | 0 | 0 |  | 247 | 437 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 525576 | 525576 | 525575.9997
39043.5441 | 0 | 0 | 39043.5441 | 0 | 0 |  | 289.5 | 479.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 525576 | 525576 | 525575.9997
39043.5446 | 1385 | 0 | 39043.5446 | 1462 | 0 |  | 331 | 521 | 84.5543 | 0 | 89.2552 | 0 | 0.84554 | 0 | 0.89255 | 0 | 0.84554 | 0.89255 | 89.7747 | 79.7798 | 88.9292
39043.5451 | 1722 | 97 | 39043.5451 | 1507 | 9 |  | 373 | 563 | 105.1282 | 5.9219 | 92.0024 | 0.54945 | 1.0513 | 0.059219 | 0.92002 | 0.0054945 | 0.99206 | 0.91453 | 60.5583 | 75.6086 | 359.2577
39043.5456 | 2109 | 3 | 39043.5456 | 2139 | 3 |  | 415 | 605 | 128.7546 | 0.18315 | 130.5861 | 0.18315 | 1.2875 | 0.0018315 | 1.3059 | 0.0018315 | 1.2857 | 1.304 | 24.8153 | 23.0415 | 3223.344
39043.5461 | 1885 | 8 | 39043.5461 | 1867 | 8 |  | 457 | 647 | 115.0794 | 0.4884 | 113.9805 | 0.4884 | 1.1508 | 0.004884 | 1.1398 | 0.004884 | 1.1459 | 1.1349 | 40.0166 | 41.4017 | 2691.4424
39043.5465 | 1879 | 4 | 39043.5466 | 2102 | 4 |  | 499 | 689 | 114.7131 | 0.2442 | 128.3272 | 0.2442 | 1.1471 | 0.002442 | 1.2833 | 0.002442 | 1.1447 | 1.2808 | 40.308 | 25.2088 | 3751.7658
39043.547 | 1939 | 1 | 39043.547 | 2110 | 1 |  | 541 | 731 | 118.3761 | 0.06105 | 128.8156 | 0.06105 | 1.1838 | 0.0006105 | 1.2882 | 0.0006105 | 1.1832 | 1.2875 | 35.6465 | 24.6122 | 13596.2001
39043.5475 | 2374 | 0 | 39043.5475 | 1913 | 0 |  | 583 | 773 | 144.9328 | 0 | 116.7888 | 0 | 1.4493 | 0 | 1.1679 | 0 | 1.4493 | 1.1679 | 10.7152 | 37.3957 | 9.2659
39043.548 | 2393 | 1 | 39043.548 | 2117 | 0 |  | 625 | 815 | 146.0928 | 0.06105 | 129.243 | 0 | 1.4609 | 0.0006105 | 1.2924 | 0 | 1.4603 | 1.2924 | 9.8574 | 24.1559 | 4560.1186
39043.5485 | 2253 | 0 | 39043.5485 | 2386 | 1 |  | 667 | 857 | 137.5458 | 0 | 145.6654 | 0.06105 | 1.3755 | 0 | 1.4567 | 0.0006105 | 1.3755 | 1.456 | 16.6613 | 10.2046 | 15.2859
39043.549 | 2414 | 0 | 39043.549 | 2052 | 1 |  | 709 | 899 | 147.3748 | 0 | 125.2747 | 0.06105 | 1.4737 | 0 | 1.2527 | 0.0006105 | 1.4737 | 1.2521 | 8.8807 | 28.1511 | 7.4069
39043.5495 | 2102 | 1 | 39043.5495 | 2469 | 0 |  | 751 | 941 | 128.3272 | 0.06105 | 150.7326 | 0 | 1.2833 | 0.0006105 | 1.5073 | 0 | 1.2827 | 1.5073 | 25.2399 | 6.4552 | 3185.8051
39043.5499 | 1973 | 0 | 39043.55 | 2545 | 0 |  | 793 | 983 | 120.4518 | 0 | 155.3724 | 0 | 1.2045 | 0 | 1.5537 | 0 | 1.2045 | 1.5537 | 33.2174 | 3.2762 | 32.0129
39043.5504 | 2558 | 0 | 39043.5505 | 2175 | 1 |  | 835 | 1025 | 156.1661 | 0 | 132.7839 | 0.06105 | 1.5617 | 0 | 1.3278 | 0.0006105 | 1.5617 | 1.3272 | 2.7514 | 20.9006 | 1.1897
39043.5509 | 2415 | 0 | 39043.5509 | 2298 | 1 |  | 877 | 1067 | 147.4359 | 0 | 140.293 | 0.06105 | 1.4744 | 0 | 1.4029 | 0.0006105 | 1.4744 | 1.4023 | 8.8356 | 14.4266 | 7.3613
39043.5514 | 2488 | 0 | 39043.5514 | 1988 | 0 |  | 919 | 1109 | 151.8926 | 0 | 121.3675 | 0 | 1.5189 | 0 | 1.2137 | 0 | 1.5189 | 1.2137 | 5.6423 | 32.2123 | 4.1234
39043.5519 | 1999 | 0 | 39043.5519 | 2492 | 0 |  | 961 | 1151 | 122.0391 | 0 | 152.1368 | 0 | 1.2204 | 0 | 1.5214 | 0 | 1.2204 | 1.5214 | 31.4847 | 5.4727 | 30.2644
39043.5524 | 2244 | 1 | 39043.5524 | 2092 | 0 |  | 1003 | 1193 | 136.9963 | 0.06105 | 127.7167 | 0 | 1.37 | 0.0006105 | 1.2772 | 0 | 1.3694 | 1.2772 | 17.1667 | 25.6396 | 7823.7304
39043.5529 | 2175 | 1 | 39043.5529 | 2612 | 1 |  | 1045 | 1235 | 132.7839 | 0.06105 | 159.4628 | 0.06105 | 1.3278 | 0.0006105 | 1.5946 | 0.0006105 | 1.3272 | 1.594 | 22.5017 | 0.62842 | 282.5073
39043.5533 | 2054 | 0 | 39043.5534 | 2388 | 0 |  | 1087 | 1277 | 125.3968 | 0 | 145.7875 | 0 | 1.254 | 0 | 1.4579 | 0 | 1.254 | 1.4579 | 27.964 | 10.0662 | 26.71
39043.5538 | 2502 | 0 | 39043.5539 | 2080 | 0 |  | 1129 | 1319 | 152.7473 | 0 | 126.9841 | 0 | 1.5275 | 0 | 1.2698 | 0 | 1.5275 | 1.2698 | 5.0512 | 26.3644 | 3.5237
39043.5543 | 2395 | 0 | 39043.5543 | 2327 | 0 |  | 1171 | 1361 | 146.2149 | 0 | 142.0635 | 0 | 1.4621 | 0 | 1.4206 | 0 | 1.4621 | 1.4206 | 9.7445 | 12.9514 | 8.2823
39043.5548 | 2194 | 0 | 39043.5548 | 2243 | 0 |  | 1213 | 1403 | 133.9438 | 0 | 136.9353 | 0 | 1.3394 | 0 | 1.3694 | 0 | 1.3394 | 1.3694 | 19.7985 | 17.1815 | 18.4591
39043.5553 | 2482 | 0 | 39043.5553 | 2538 | 0 |  | 1255 | 1445 | 151.5263 | 0 | 154.9451 | 0 | 1.5153 | 0 | 1.5495 | 0 | 1.5153 | 1.5495 | 5.8977 | 3.5611 | 4.3824
39043.5558 | 2518 | 0 | 39043.5558 | 2550 | 0 |  | 1297 | 1487 | 153.7241 | 0 | 155.6777 | 0 | 1.5372 | 0 | 1.5568 | 0 | 1.5372 | 1.5568 | 4.3836 | 3.0737 | 2.8464
39043.5563 | 2057 | 0 | 39043.5563 | 2517 | 0 |  | 1339 | 1529 | 125.58 | 0 | 153.663 | 0 | 1.2558 | 0 | 1.5366 | 0 | 1.2558 | 1.5366 | 27.7773 | 4.4251 | 26.5215
39043.5567 | 2512 | 0 | 39043.5568 | 2353 | 0 |  | 1381 | 1571 | 153.3578 | 0 | 143.6508 | 0 | 1.5336 | 0 | 1.4365 | 0 | 1.5336 | 1.4365 | 4.633 | 11.7034 | 3.0994

## A2-B3
Open Burn Test 12 |  |  | 2006-11-22 | 13:02 |  |  | Vs = |  | 158.0208 |  | R = | 100
Mixed | 7-C | Tray C | IRMS | 2
0 | 250 kW |  | Bundle | Ch. 2 & 3 | Cable A | Even - | Cable B |  | Odd
Time-11 | N11 | N12 | Time-12 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R3-G | R2-3
39043.5387 | 0 | 0 | 39043.5387 | 0 | 0 |  | -175.5 | 14.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517576 | 517576 | 517575.9997
39043.5392 | 0 | 0 | 39043.5392 | 0 | 0 |  | -133.5 | 56.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517576 | 517576 | 517575.9997
39043.5397 | 0 | 0 | 39043.5397 | 0 | 0 |  | -91.5 | 98.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517576 | 517576 | 517575.9997
39043.5402 | 0 | 0 | 39043.5402 | 0 | 0 |  | -49.5 | 140.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517576 | 517576 | 517575.9997
39043.5407 | 0 | 0 | 39043.5407 | 0 | 0 |  | -7.5 | 182.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517576 | 517576 | 517575.9997
39043.5412 | 0 | 0 | 39043.5412 | 0 | 0 |  | 34.5 | 224.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517576 | 517576 | 517575.9997
39043.5417 | 0 | 0 | 39043.5417 | 0 | 0 |  | 76.5 | 266.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517576 | 517576 | 517575.9997
39043.5421 | 0 | 0 | 39043.5422 | 0 | 0 |  | 118.5 | 308.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517576 | 517576 | 517575.9997
39043.5426 | 0 | 0 | 39043.5426 | 0 | 0 |  | 160.5 | 350.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517576 | 517576 | 517575.9997
39043.5431 | 0 | 0 | 39043.5431 | 0 | 0 |  | 202.5 | 392.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517576 | 517576 | 517575.9997
39043.5436 | 0 | 0 | 39043.5436 | 0 | 0 |  | 244.5 | 434.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517576 | 517576 | 517575.9997
39043.5441 | 0 | 0 | 39043.5441 | 0 | 0 |  | 286.5 | 476.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517576 | 517576 | 517575.9997
39043.5446 | 616 | 1 | 39043.5446 | 0 | 0 |  | 328.5 | 518.5 | 37.6068 | 0.06105 | 0.030525 | 0 | 0.37607 | 0.0006105 | 0.00030525 | 0 | 0.37546 | 0.00030525 | 320.7123 | 517576 | 197099.9187
39043.5451 | 1576 | 41 | 39043.5451 | 1115 | 6 |  | 370.5 | 560.5 | 96.2149 | 2.5031 | 68.0708 | 0.3663 | 0.96215 | 0.025031 | 0.68071 | 0.003663 | 0.93712 | 0.67705 | 67.2951 | 133.9334 | 1356.4443
39043.5455 | 2190 | 14 | 39043.5456 | 1566 | 5 |  | 412.5 | 602.5 | 133.6996 | 0.8547 | 95.6044 | 0.30525 | 1.337 | 0.008547 | 0.95604 | 0.0030525 | 1.3284 | 0.95299 | 18.4864 | 66.65 | 1098.064
39043.546 | 2387 | 9 | 39043.546 | 1917 | 9 |  | 454.5 | 644.5 | 145.7265 | 0.54945 | 117.033 | 0.54945 | 1.4573 | 0.0054945 | 1.1703 | 0.0054945 | 1.4518 | 1.1648 | 8.5554 | 37.2409 | 580.0346
39043.5465 | 1988 | 4 | 39043.5465 | 1910 | 2 |  | 496.5 | 686.5 | 121.3675 | 0.2442 | 116.6056 | 0.1221 | 1.2137 | 0.002442 | 1.1661 | 0.001221 | 1.2112 | 1.1648 | 30.4331 | 35.6774 | 3920.5653
39043.547 | 2325 | 1 | 39043.547 | 1962 | 0 |  | 538.5 | 728.5 | 141.9414 | 0.06105 | 119.7802 | 0 | 1.4194 | 0.0006105 | 1.1978 | 0 | 1.4188 | 1.1978 | 11.3483 | 31.9256 | 6349.5153
39043.5475 | 2038 | 0 | 39043.5475 | 2105 | 0 |  | 580.5 | 770.5 | 124.42 | 0 | 128.5104 | 0 | 1.2442 | 0 | 1.2851 | 0 | 1.2442 | 1.2851 | 27.0059 | 22.9634 | 25.7617
39043.548 | 2265 | 0 | 39043.548 | 2540 | 0 |  | 622.5 | 812.5 | 138.2784 | 0 | 155.0672 | 0 | 1.3828 | 0 | 1.5507 | 0 | 1.3828 | 1.5507 | 14.2773 | 1.9047 | 12.8945
39043.5485 | 1968 | 1 | 39043.5485 | 2043 | 0 |  | 664.5 | 854.5 | 120.1465 | 0.06105 | 124.7253 | 0 | 1.2015 | 0.0006105 | 1.2473 | 0 | 1.2009 | 1.2473 | 31.5996 | 26.6951 | 13050.536
39043.5489 | 2360 | 1 | 39043.549 | 2097 | 1 |  | 706.5 | 896.5 | 144.0781 | 0.06105 | 128.022 | 0.06105 | 1.4408 | 0.0006105 | 1.2802 | 0.0006105 | 1.4402 | 1.2796 | 9.6987 | 23.5596 | 4335.5444
39043.5494 | 2194 | 0 | 39043.5494 | 2149 | 1 |  | 748.5 | 938.5 | 133.9438 | 0 | 131.1966 | 0.06105 | 1.3394 | 0 | 1.312 | 0.0006105 | 1.3394 | 1.3114 | 17.9754 | 20.5019 | 16.6359
39043.5499 | 2007 | 0 | 39043.5499 | 2021 | 0 |  | 790.5 | 980.5 | 122.5275 | 0 | 123.3822 | 0 | 1.2253 | 0 | 1.2338 | 0 | 1.2253 | 1.2338 | 28.9676 | 28.0742 | 27.7423
39043.5504 | 2065 | 0 | 39043.5504 | 2092 | 0 |  | 832.5 | 1022.5 | 126.0684 | 0 | 127.7167 | 0 | 1.2607 | 0 | 1.2772 | 0 | 1.2607 | 1.2772 | 25.3453 | 23.7275 | 24.0846
39043.5509 | 1988 | 0 | 39043.5509 | 2211 | 1 |  | 874.5 | 1064.5 | 121.3675 | 0 | 134.9817 | 0.06105 | 1.2137 | 0 | 1.3498 | 0.0006105 | 1.2137 | 1.3492 | 30.2002 | 17.1213 | 28.9865
39043.5514 | 2286 | 0 | 39043.5514 | 2158 | 1 |  | 916.5 | 1106.5 | 139.5604 | 0 | 131.746 | 0.06105 | 1.3956 | 0 | 1.3175 | 0.0006105 | 1.3956 | 1.3168 | 13.2275 | 19.9991 | 11.8319
39043.5519 | 2298 | 0 | 39043.5519 | 2321 | 0 |  | 958.5 | 1148.5 | 140.293 | 0 | 141.6972 | 0 | 1.4029 | 0 | 1.417 | 0 | 1.4029 | 1.417 | 12.6362 | 11.52 | 11.2333
39043.5523 | 2507 | 1 | 39043.5524 | 2524 | 0 |  | 1000.5 | 1190.5 | 153.0525 | 0.06105 | 154.0904 | 0 | 1.5305 | 0.0006105 | 1.5409 | 0 | 1.5299 | 1.5409 | 3.299 | 2.5507 | 199.9268
39043.5528 | 2099 | 1 | 39043.5528 | 2058 | 0 |  | 1042.5 | 1232.5 | 128.1441 | 0.06105 | 125.641 | 0 | 1.2814 | 0.0006105 | 1.2564 | 0 | 1.2808 | 1.2564 | 23.3692 | 25.7716 | 10007.3013
39043.5533 | 2339 | 0 | 39043.5533 | 2434 | 0 |  | 1084.5 | 1274.5 | 142.7961 | 0 | 148.5958 | 0 | 1.428 | 0 | 1.486 | 0 | 1.428 | 1.486 | 10.6618 | 6.3426 | 9.2339
39043.5538 | 2019 | 0 | 39043.5538 | 2168 | 0 |  | 1126.5 | 1316.5 | 123.2601 | 0 | 132.3565 | 0 | 1.2326 | 0 | 1.3236 | 0 | 1.2326 | 1.3236 | 28.2011 | 19.3902 | 26.9685
39043.5543 | 2286 | 0 | 39043.5543 | 2408 | 0 |  | 1168.5 | 1358.5 | 139.5604 | 0 | 147.0085 | 0 | 1.3956 | 0 | 1.4701 | 0 | 1.3956 | 1.4701 | 13.2275 | 7.4909 | 11.8319
39043.5548 | 2267 | 0 | 39043.5548 | 1907 | 0 |  | 1210 | 1400 | 138.4005 | 0 | 116.4225 | 0 | 1.384 | 0 | 1.1642 | 0 | 1.384 | 1.1642 | 14.1764 | 35.7305 | 12.7924
39043.5553 | 1996 | 0 | 39043.5553 | 2195 | 0 |  | 1252 | 1442 | 121.8559 | 0 | 134.0049 | 0 | 1.2186 | 0 | 1.34 | 0 | 1.2186 | 1.34 | 29.6784 | 17.9216 | 28.4598
39043.5557 | 2465 | 0 | 39043.5558 | 2384 | 0 |  | 1294 | 1484 | 150.4884 | 0 | 145.5433 | 0 | 1.5049 | 0 | 1.4554 | 0 | 1.5049 | 1.4554 | 5.0053 | 8.573 | 3.5004
39043.5562 | 2306 | 0 | 39043.5563 | 2569 | 0 |  | 1336 | 1526 | 140.7814 | 0 | 156.8376 | 0 | 1.4078 | 0 | 1.5684 | 0 | 1.4078 | 1.5684 | 12.2454 | 0.75438 | 10.8376
39043.5567 | 1937 | 0 | 39043.5567 | 2572 | 0 |  | 1378 | 1568 | 118.254 | 0 | 157.0208 | 0 | 1.1825 | 0 | 1.5702 | 0 | 1.1825 | 1.5702 | 33.6283 | 0.63686 | 32.4458

## A1-C6
Open Burn Test 12 |  |  | 2006-11-22 | 13:02 |  |  | Vs = |  | 159.9744 |  | R = | 100
Mixed | 7-C | Tray C | IRMS | 2
0 | 250 kW |  | Bundle | Ch. 1 & 6 | Cable A | Odd - | Cable C |  | Even
Time-9 | N11 | N12 | Time-10 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R6-G | R1-6
39043.5387 | 0 | 0 | 39043.5387 | 0 | 0 |  | -178.5 | 11.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 523976 | 523976 | 523975.9997
39043.5392 | 0 | 0 | 39043.5392 | 0 | 0 |  | -136.5 | 53.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 523976 | 523976 | 523975.9997
39043.5397 | 0 | 0 | 39043.5397 | 0 | 0 |  | -94.5 | 95.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 523976 | 523976 | 523975.9997
39043.5402 | 0 | 0 | 39043.5402 | 0 | 0 |  | -52.5 | 137.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 523976 | 523976 | 523975.9997
39043.5406 | 0 | 0 | 39043.5407 | 0 | 0 |  | -10.5 | 179.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 523976 | 523976 | 523975.9997
39043.5411 | 0 | 0 | 39043.5411 | 0 | 0 |  | 31.5 | 221.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 523976 | 523976 | 523975.9997
39043.5416 | 0 | 0 | 39043.5416 | 0 | 0 |  | 73.5 | 263.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 523976 | 523976 | 523975.9997
39043.5421 | 0 | 0 | 39043.5421 | 0 | 0 |  | 115.5 | 305.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 523976 | 523976 | 523975.9997
39043.5426 | 0 | 1 | 39043.5426 | 0 | 0 |  | 157.5 | 347.5 | 0.030525 | 0.06105 | 0.030525 | 0 | 0.00030525 | 0.0006105 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 524176.0764 | 523976 | 261838.0286
39043.5431 | 0 | 0 | 39043.5431 | 0 | 0 |  | 199.5 | 389.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 523976 | 523976 | 523975.9997
39043.5436 | 0 | 0 | 39043.5436 | 0 | 0 |  | 241.5 | 431.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 523976 | 523976 | 523975.9997
39043.5441 | 0 | 0 | 39043.5441 | 0 | 0 |  | 283.5 | 473.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 523976 | 523976 | 523975.9997
39043.5445 | 804 | 1 | 39043.5445 | 0 | 0 |  | 325.5 | 515.5 | 49.0842 | 0.06105 | 0.030525 | 0 | 0.49084 | 0.0006105 | 0.00030525 | 0 | 0.49023 | 0.00030525 | 226.1993 | 523976 | 181503.3604
39043.545 | 1575 | 1 | 39043.545 | 0 | 0 |  | 367.5 | 557.5 | 96.1538 | 0.06105 | 0.030525 | 0 | 0.96154 | 0.0006105 | 0.00030525 | 0 | 0.96093 | 0.00030525 | 66.4155 | 523976.0008 | 104418.072
39043.5455 | 2055 | 0 | 39043.5455 | 1845 | 0 |  | 409.5 | 599.5 | 125.4579 | 0 | 112.6374 | 0 | 1.2546 | 0 | 1.1264 | 0 | 1.2546 | 1.1264 | 27.5124 | 42.026 | 26.2578
39043.546 | 1837 | 0 | 39043.546 | 1880 | 0 |  | 451.5 | 641.5 | 112.149 | 0 | 114.7741 | 0 | 1.1215 | 0 | 1.1477 | 0 | 1.1215 | 1.1477 | 42.6445 | 39.3819 | 41.523
39043.5465 | 1939 | 0 | 39043.5465 | 2311 | 0 |  | 493.5 | 683.5 | 118.3761 | 0 | 141.0867 | 0 | 1.1838 | 0 | 1.4109 | 0 | 1.1838 | 1.4109 | 35.1408 | 13.3873 | 33.957
39043.547 | 2099 | 0 | 39043.547 | 1942 | 0 |  | 535.5 | 725.5 | 128.1441 | 0 | 118.5592 | 0 | 1.2814 | 0 | 1.1856 | 0 | 1.2814 | 1.1856 | 24.8394 | 34.932 | 23.558
39043.5475 | 2015 | 0 | 39043.5475 | 2074 | 0 |  | 577.5 | 767.5 | 123.0159 | 0 | 126.6178 | 0 | 1.2302 | 0 | 1.2662 | 0 | 1.2302 | 1.2662 | 30.0437 | 26.3443 | 28.8135
39043.5479 | 2418 | 0 | 39043.548 | 2274 | 0 |  | 619.5 | 809.5 | 147.619 | 0 | 138.8278 | 0 | 1.4762 | 0 | 1.3883 | 0 | 1.4762 | 1.3883 | 8.3697 | 15.2322 | 6.8935
39043.5484 | 2517 | 0 | 39043.5484 | 2182 | 1 |  | 661.5 | 851.5 | 153.663 | 0 | 133.2112 | 0.06105 | 1.5366 | 0 | 1.3321 | 0.0006105 | 1.5366 | 1.3315 | 4.1073 | 20.1458 | 2.5706
39043.5489 | 2133 | 1 | 39043.5489 | 2007 | 1 |  | 703.5 | 893.5 | 130.2198 | 0.06105 | 122.5275 | 0.06105 | 1.3022 | 0.0006105 | 1.2253 | 0.0006105 | 1.3016 | 1.2247 | 22.8953 | 30.644 | 11408.5798
39043.5494 | 2041 | 1 | 39043.5494 | 2322 | 0 |  | 745.5 | 935.5 | 124.6032 | 0.06105 | 141.7582 | 0 | 1.246 | 0.0006105 | 1.4176 | 0 | 1.2454 | 1.4176 | 28.5097 | 12.8501 | 6585.9541
39043.5499 | 2011 | 1 | 39043.5499 | 1945 | 1 |  | 787.5 | 977.5 | 122.7717 | 0.06105 | 118.7424 | 0.06105 | 1.2277 | 0.0006105 | 1.1874 | 0.0006105 | 1.2271 | 1.1868 | 30.3608 | 34.8007 | 15706.1977
39043.5504 | 1997 | 1 | 39043.5504 | 1967 | 0 |  | 829.5 | 1019.5 | 121.917 | 0.06105 | 120.0855 | 0 | 1.2192 | 0.0006105 | 1.2009 | 0 | 1.2186 | 1.2009 | 31.2786 | 33.2171 | 15518.7661
39043.5509 | 2093 | 0 | 39043.5509 | 1945 | 0 |  | 871.5 | 1061.5 | 127.7778 | 0 | 118.7424 | 0 | 1.2778 | 0 | 1.1874 | 0 | 1.2778 | 1.1874 | 25.1973 | 34.7239 | 23.9195
39043.5513 | 2109 | 1 | 39043.5514 | 2246 | 0 |  | 913.5 | 1103.5 | 128.7546 | 0.06105 | 137.1184 | 0 | 1.2875 | 0.0006105 | 1.3712 | 0 | 1.2869 | 1.3712 | 24.3283 | 16.6687 | 7291.922
39043.5518 | 2577 | 0 | 39043.5518 | 1948 | 0 |  | 955.5 | 1145.5 | 157.326 | 0 | 118.9255 | 0 | 1.5733 | 0 | 1.1893 | 0 | 1.5733 | 1.1893 | 1.6834 | 34.5164 | 0.11009
39043.5523 | 2058 | 0 | 39043.5523 | 1976 | 1 |  | 997.5 | 1187.5 | 125.641 | 0 | 120.6349 | 0.06105 | 1.2564 | 0 | 1.2063 | 0.0006105 | 1.2564 | 1.2057 | 27.3265 | 32.6775 | 26.0701
39043.5528 | 2285 | 0 | 39043.5528 | 2005 | 0 |  | 1039.5 | 1229.5 | 139.4994 | 0 | 122.4054 | 0 | 1.395 | 0 | 1.2241 | 0 | 1.395 | 1.2241 | 14.6775 | 30.6923 | 13.2825
39043.5533 | 2012 | 0 | 39043.5533 | 2196 | 1 |  | 1081.5 | 1271.5 | 122.8327 | 0 | 134.0659 | 0.06105 | 1.2283 | 0 | 1.3407 | 0.0006105 | 1.2283 | 1.34 | 30.2376 | 19.3795 | 29.0092
39043.5538 | 2604 | 0 | 39043.5538 | 2421 | 1 |  | 1123.5 | 1313.5 | 158.9744 | 0 | 147.8022 | 0.06105 | 1.5897 | 0 | 1.478 | 0.0006105 | 1.5897 | 1.4774 | 0.62903 | 8.2802 | 0.96071
39043.5543 | 2029 | 1 | 39043.5543 | 2216 | 1 |  | 1165.5 | 1355.5 | 123.8706 | 0.06105 | 135.2869 | 0.06105 | 1.2387 | 0.0006105 | 1.3529 | 0.0006105 | 1.2381 | 1.3523 | 29.2396 | 18.2847 | 9126.2048
39043.5547 | 2234 | 0 | 39043.5548 | 1877 | 1 |  | 1207.5 | 1397.5 | 136.3858 | 0 | 114.591 | 0.06105 | 1.3639 | 0 | 1.1459 | 0.0006105 | 1.3639 | 1.1453 | 17.2954 | 39.6791 | 15.9316
39043.5552 | 2578 | 0 | 39043.5552 | 2178 | 0 |  | 1249.5 | 1439.5 | 157.3871 | 0 | 132.967 | 0 | 1.5739 | 0 | 1.3297 | 0 | 1.5739 | 1.3297 | 1.6439 | 20.3113 | 0.070039
39043.5557 | 2273 | 0 | 39043.5557 | 937 | 0 |  | 1291.5 | 1481.5 | 138.7668 | 0 | 57.2039 | 0 | 1.3877 | 0 | 0.57204 | 0 | 1.3877 | 0.57204 | 15.2829 | 179.6564 | 13.8952
39043.5562 | 2316 | 0 | 39043.5562 | 1970 | 1 |  | 1333.5 | 1523.5 | 141.3919 | 0 | 120.2686 | 0.06105 | 1.4139 | 0 | 1.2027 | 0.0006105 | 1.4139 | 1.2021 | 13.1425 | 33.0818 | 11.7286
39043.5567 | 2111 | 0 | 39043.5567 | 1922 | 3 |  | 1375.5 | 1565.5 | 128.8767 | 0 | 117.3382 | 0.18315 | 1.2888 | 0 | 1.1734 | 0.0018315 | 1.2888 | 1.1716 | 24.1298 | 36.5492 | 22.841

## A1-C5
Open Burn Test 12 |  |  | 2006-11-22 | 13:02 |  |  | Vs = |  | 160.2186 |  | R = | 100
Mixed | 7-C | Tray C | IRMS | 2
0 | 250 kW |  | Bundle | Ch. 1 & 5 | Cable A | Odd - | Cable C |  | Odd
Time-7 | N11 | N12 | Time-8 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R5-G | R1-5
39043.5387 | 0 | 0 | 39043.5387 | 0 | 0 |  | -181 | 9 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 524776 | 524776 | 524775.9997
39043.5392 | 0 | 0 | 39043.5392 | 0 | 0 |  | -139.5 | 50.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 524776 | 524776 | 524775.9997
39043.5396 | 0 | 0 | 39043.5397 | 0 | 0 |  | -97.5 | 92.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 524776 | 524776 | 524775.9997
39043.5401 | 0 | 0 | 39043.5401 | 0 | 0 |  | -55.5 | 134.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 524776 | 524776 | 524775.9997
39043.5406 | 0 | 0 | 39043.5406 | 0 | 0 |  | -13.5 | 176.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 524776 | 524776 | 524775.9997
39043.5411 | 0 | 0 | 39043.5411 | 0 | 0 |  | 29 | 219 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 524776 | 524776 | 524775.9997
39043.5416 | 0 | 0 | 39043.5416 | 0 | 0 |  | 70.5 | 260.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 524776 | 524776 | 524775.9997
39043.5421 | 0 | 0 | 39043.5421 | 0 | 0 |  | 113 | 303 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 524776 | 524776 | 524775.9997
39043.5426 | 0 | 0 | 39043.5426 | 0 | 0 |  | 155 | 345 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 524776 | 524776 | 524775.9997
39043.543 | 0 | 0 | 39043.5431 | 0 | 0 |  | 197 | 387 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 524776 | 524776 | 524775.9997
39043.5435 | 0 | 0 | 39043.5435 | 0 | 0 |  | 238.5 | 428.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 524776 | 524776 | 524775.9997
39043.544 | 0 | 0 | 39043.544 | 0 | 0 |  | 280.5 | 470.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 524776 | 524776 | 524775.9997
39043.5445 | 764 | 1 | 39043.5445 | 0 | 0 |  | 322.5 | 512.5 | 46.6422 | 0.06105 | 0.030525 | 0 | 0.46642 | 0.0006105 | 0.00030525 | 0 | 0.46581 | 0.00030525 | 243.8244 | 524776.0003 | 185902.5749
39043.545 | 1554 | 1 | 39043.545 | 0 | 0 |  | 364.5 | 554.5 | 94.8718 | 0.06105 | 0.030525 | 0 | 0.94872 | 0.0006105 | 0.00030525 | 0 | 0.94811 | 0.00030525 | 68.9234 | 524776 | 106917.626
39043.5455 | 1923 | 0 | 39043.5455 | 1172 | 0 |  | 406.5 | 596.5 | 117.3993 | 0 | 71.5507 | 0 | 1.174 | 0 | 0.71551 | 0 | 1.174 | 0.71551 | 36.4732 | 123.9232 | 35.2992
39043.546 | 2070 | 0 | 39043.546 | 1928 | 0 |  | 448.5 | 638.5 | 126.3736 | 0 | 117.7045 | 0 | 1.2637 | 0 | 1.177 | 0 | 1.2637 | 1.177 | 26.7816 | 36.1193 | 25.5179
39043.5464 | 1830 | 0 | 39043.5465 | 2021 | 0 |  | 490.5 | 680.5 | 111.7216 | 0 | 123.3822 | 0 | 1.1172 | 0 | 1.2338 | 0 | 1.1172 | 1.2338 | 43.4087 | 29.8555 | 42.2915
39043.5469 | 2240 | 0 | 39043.5469 | 2413 | 0 |  | 532.5 | 722.5 | 136.7521 | 0 | 147.3138 | 0 | 1.3675 | 0 | 1.4731 | 0 | 1.3675 | 1.4731 | 17.1598 | 8.76 | 15.7923
39043.5474 | 2386 | 0 | 39043.5474 | 2438 | 0 |  | 574.5 | 764.5 | 145.6654 | 0 | 148.84 | 0 | 1.4567 | 0 | 1.4884 | 0 | 1.4567 | 1.4884 | 9.9908 | 7.6448 | 8.5341
39043.5479 | 1958 | 0 | 39043.5479 | 2427 | 0 |  | 616.5 | 806.5 | 119.536 | 0 | 148.1685 | 0 | 1.1954 | 0 | 1.4817 | 0 | 1.1954 | 1.4817 | 34.0337 | 8.1327 | 32.8383
39043.5484 | 2398 | 0 | 39043.5484 | 2494 | 1 |  | 658.5 | 848.5 | 146.398 | 0 | 152.2589 | 0.06105 | 1.464 | 0 | 1.5226 | 0.0006105 | 1.464 | 1.522 | 9.4404 | 5.27 | 7.9764
39043.5489 | 2542 | 1 | 39043.5489 | 2540 | 1 |  | 700.5 | 890.5 | 155.1893 | 0.06105 | 155.0672 | 0.06105 | 1.5519 | 0.0006105 | 1.5507 | 0.0006105 | 1.5513 | 1.5501 | 3.2804 | 3.3637 | 264.833
39043.5494 | 2132 | 1 | 39043.5494 | 2041 | 1 |  | 742.5 | 932.5 | 130.1587 | 0.06105 | 124.6032 | 0.06105 | 1.3016 | 0.0006105 | 1.246 | 0.0006105 | 1.301 | 1.2454 | 23.1435 | 28.6578 | 10945.2002
39043.5498 | 2186 | 0 | 39043.5499 | 2255 | 0 |  | 784.5 | 974.5 | 133.4554 | 0 | 137.6679 | 0 | 1.3346 | 0 | 1.3767 | 0 | 1.3346 | 1.3767 | 20.054 | 16.3805 | 18.7194
39043.5503 | 2147 | 0 | 39043.5503 | 2469 | 1 |  | 826.5 | 1016.5 | 131.0745 | 0 | 150.7326 | 0.06105 | 1.3107 | 0 | 1.5073 | 0.0006105 | 1.3107 | 1.5067 | 22.2347 | 6.3363 | 20.924
39043.5508 | 2569 | 1 | 39043.5508 | 2567 | 0 |  | 868.5 | 1058.5 | 156.8376 | 0.06105 | 156.7155 | 0 | 1.5684 | 0.0006105 | 1.5672 | 0 | 1.5678 | 1.5672 | 2.1948 | 2.2353 | 118.8976
39043.5513 | 2431 | 1 | 39043.5513 | 2094 | 1 |  | 910.5 | 1100.5 | 148.4127 | 0.06105 | 127.8388 | 0.06105 | 1.4841 | 0.0006105 | 1.2784 | 0.0006105 | 1.4835 | 1.2778 | 7.9709 | 25.4935 | 3908.1187
39043.5518 | 2603 | 0 | 39043.5518 | 2506 | 0 |  | 952.5 | 1142.5 | 158.9133 | 0 | 152.9915 | 0 | 1.5891 | 0 | 1.5299 | 0 | 1.5891 | 1.5299 | 0.82136 | 4.7239 | 0.76777
39043.5523 | 2566 | 0 | 39043.5523 | 2553 | 1 |  | 994.5 | 1184.5 | 156.6545 | 0 | 155.8608 | 0.06105 | 1.5665 | 0 | 1.5586 | 0.0006105 | 1.5665 | 1.558 | 2.2751 | 2.8362 | 0.70859
39043.5528 | 2086 | 1 | 39043.5528 | 2393 | 0 |  | 1036.5 | 1226.5 | 127.3504 | 0.06105 | 146.0928 | 0 | 1.2735 | 0.0006105 | 1.4609 | 0 | 1.2729 | 1.4609 | 25.9503 | 9.669 | 4737.8422
39043.5533 | 2608 | 0 | 39043.5533 | 2032 | 0 |  | 1078.5 | 1268.5 | 159.2186 | 0 | 124.0537 | 0 | 1.5922 | 0 | 1.2405 | 0 | 1.5922 | 1.2405 | 0.62807 | 29.1526 | 0.96412
39043.5537 | 2290 | 1 | 39043.5537 | 2071 | 1 |  | 1120.5 | 1310.5 | 139.8046 | 0.06105 | 126.4347 | 0.06105 | 1.398 | 0.0006105 | 1.2643 | 0.0006105 | 1.3974 | 1.2637 | 14.632 | 26.8219 | 7050.7398
39043.5542 | 2063 | 0 | 39043.5542 | 2375 | 0 |  | 1162.5 | 1352.5 | 125.9463 | 0 | 144.9939 | 0 | 1.2595 | 0 | 1.4499 | 0 | 1.2595 | 1.4499 | 27.2118 | 10.5002 | 25.9524
39043.5547 | 2117 | 0 | 39043.5547 | 2105 | 0 |  | 1204.5 | 1394.5 | 129.243 | 0 | 128.5104 | 0 | 1.2924 | 0 | 1.2851 | 0 | 1.2924 | 1.2851 | 23.9669 | 24.6736 | 22.6745
39043.5552 | 2451 | 0 | 39043.5552 | 1909 | 0 |  | 1246.5 | 1436.5 | 149.6337 | 0 | 116.5446 | 0 | 1.4963 | 0 | 1.1654 | 0 | 1.4963 | 1.1654 | 7.0738 | 37.4741 | 5.5775
39043.5557 | 2280 | 0 | 39043.5557 | 771 | 0 |  | 1288.5 | 1478.5 | 139.1941 | 0 | 47.0696 | 0 | 1.3919 | 0 | 0.4707 | 0 | 1.3919 | 0.4707 | 15.1044 | 240.3865 | 13.7124
39043.5562 | 2520 | 0 | 39043.5562 | 500 | 0 |  | 1330.5 | 1520.5 | 153.8462 | 0 | 30.525 | 0 | 1.5385 | 0 | 0.30525 | 0 | 1.5385 | 0.30525 | 4.1421 | 424.876 | 2.6036
39043.5567 | 2326 | 0 | 39043.5567 | 64 | 0 |  | 1372.5 | 1562.5 | 142.0024 | 0 | 3.9072 | 0 | 1.42 | 0 | 0.039072 | 0 | 1.42 | 0.039072 | 12.828 | 4000.5938 | 11.408

## A1-B4
Open Burn Test 12 |  |  | 2006-11-22 | 13:02 |  |  | Vs = |  | 158.0208 |  | R = | 100
Mixed | 7-C | Tray C | IRMS | 2
0 | 250 kW |  | Bundle | Ch. 1 & 4 | Cable A | Odd - | Cable B |  | Even
Time-5 | N11 | N12 | Time-6 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R4-G | R1-4
39043.5386 | 0 | 0 | 39043.5387 | 0 | 0 |  | -184 | 6 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517576 | 517576 | 517575.9997
39043.5391 | 0 | 0 | 39043.5391 | 0 | 0 |  | -142 | 48 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517576 | 517576 | 517575.9997
39043.5396 | 0 | 0 | 39043.5396 | 0 | 0 |  | -100 | 90 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517576 | 517576 | 517575.9997
39043.5401 | 0 | 0 | 39043.5401 | 0 | 0 |  | -58 | 132 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517576 | 517576 | 517575.9997
39043.5406 | 0 | 0 | 39043.5406 | 0 | 0 |  | -16 | 174 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517576 | 517576 | 517575.9997
39043.5411 | 0 | 0 | 39043.5411 | 0 | 0 |  | 26 | 216 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517576 | 517576 | 517575.9997
39043.5416 | 0 | 0 | 39043.5416 | 0 | 0 |  | 68 | 258 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517576 | 517576 | 517575.9997
39043.542 | 0 | 0 | 39043.5421 | 0 | 0 |  | 110 | 300 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517576 | 517576 | 517575.9997
39043.5425 | 0 | 0 | 39043.5425 | 0 | 0 |  | 152 | 342 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517576 | 517576 | 517575.9997
39043.543 | 0 | 0 | 39043.543 | 0 | 0 |  | 194 | 384 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517576 | 517576 | 517575.9997
39043.5435 | 0 | 0 | 39043.5435 | 0 | 0 |  | 236 | 426 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517576 | 517576 | 517575.9997
39043.544 | 0 | 0 | 39043.544 | 0 | 0 |  | 278 | 468 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517576 | 517576 | 517575.9997
39043.5445 | 420 | 1 | 39043.5445 | 0 | 0 |  | 320 | 510 | 25.641 | 0.06105 | 0.030525 | 0 | 0.25641 | 0.0006105 | 0.00030525 | 0 | 0.2558 | 0.00030525 | 517.5134 | 517576.0003 | 216696.1325
39043.545 | 1485 | 107 | 39043.545 | 1332 | 124 |  | 362 | 552 | 90.6593 | 6.5324 | 81.3187 | 7.5702 | 0.90659 | 0.065324 | 0.81319 | 0.075702 | 0.84127 | 0.73748 | 85.7032 | 118.1569 | 504.3493
39043.5454 | 1751 | 20 | 39043.5455 | 1682 | 17 |  | 404 | 594 | 106.8987 | 1.221 | 102.6862 | 1.0379 | 1.069 | 0.01221 | 1.0269 | 0.010379 | 1.0568 | 1.0165 | 49.4024 | 55.5861 | 1460.1222
39043.5459 | 2332 | 9 | 39043.5459 | 1912 | 11 |  | 446 | 636 | 142.3687 | 0.54945 | 116.7277 | 0.67155 | 1.4237 | 0.0054945 | 1.1673 | 0.0067155 | 1.4182 | 1.1606 | 11.1517 | 37.5275 | 750.0354
39043.5464 | 2083 | 5 | 39043.5464 | 1818 | 13 |  | 488 | 678 | 127.1673 | 0.30525 | 110.989 | 0.79365 | 1.2717 | 0.0030525 | 1.1099 | 0.0079365 | 1.2686 | 1.102 | 24.4543 | 43.9755 | 3056.6945
39043.5469 | 2382 | 1 | 39043.5469 | 2429 | 1 |  | 530 | 720 | 145.4212 | 0.06105 | 148.2906 | 0.06105 | 1.4542 | 0.0006105 | 1.4829 | 0.0006105 | 1.4536 | 1.4823 | 8.7233 | 6.5954 | 1270.7502
39043.5474 | 2049 | 0 | 39043.5474 | 2389 | 0 |  | 572 | 762 | 125.0916 | 0 | 145.8486 | 0 | 1.2509 | 0 | 1.4585 | 0 | 1.2509 | 1.4585 | 26.3241 | 8.3458 | 25.0731
39043.5479 | 2437 | 0 | 39043.5479 | 2041 | 0 |  | 614 | 804 | 148.779 | 0 | 124.6032 | 0 | 1.4878 | 0 | 1.246 | 0 | 1.4878 | 1.246 | 6.2117 | 26.8192 | 4.7239
39043.5484 | 2270 | 1 | 39043.5484 | 2303 | 1 |  | 656 | 846 | 138.5836 | 0.06105 | 140.5983 | 0.06105 | 1.3858 | 0.0006105 | 1.406 | 0.0006105 | 1.3852 | 1.4054 | 14.0816 | 12.4354 | 3510.2375
39043.5488 | 2131 | 0 | 39043.5489 | 2551 | 1 |  | 698 | 888 | 130.0977 | 0 | 155.7387 | 0.06105 | 1.301 | 0 | 1.5574 | 0.0006105 | 1.301 | 1.5568 | 21.4632 | 1.5051 | 20.1622
39043.5493 | 2553 | 0 | 39043.5494 | 2557 | 1 |  | 740 | 930 | 155.8608 | 0 | 156.105 | 0.06105 | 1.5586 | 0 | 1.5611 | 0.0006105 | 1.5586 | 1.5604 | 1.3858 | 1.2668 | 0.17279
39043.5498 | 2024 | 0 | 39043.5498 | 2400 | 0 |  | 782 | 972 | 123.5653 | 0 | 146.5201 | 0 | 1.2357 | 0 | 1.4652 | 0 | 1.2357 | 1.4652 | 27.8844 | 7.8492 | 26.6487
39043.5503 | 2269 | 1 | 39043.5503 | 2498 | 1 |  | 824 | 1014 | 138.5226 | 0.06105 | 152.5031 | 0.06105 | 1.3852 | 0.0006105 | 1.525 | 0.0006105 | 1.3846 | 1.5244 | 14.2552 | 3.6297 | 1115.1595
39043.5508 | 2005 | 0 | 39043.5508 | 2266 | 0 |  | 866 | 1056 | 122.4054 | 0 | 138.3394 | 0 | 1.2241 | 0 | 1.3834 | 0 | 1.2241 | 1.3834 | 29.0963 | 14.2268 | 27.8722
39043.5513 | 2572 | 0 | 39043.5513 | 2108 | 1 |  | 908 | 1098 | 157.0208 | 0 | 128.6935 | 0.06105 | 1.5702 | 0 | 1.2869 | 0.0006105 | 1.5702 | 1.2863 | 0.63686 | 22.8467 | 0.93335
39043.5518 | 2283 | 0 | 39043.5518 | 2404 | 1 |  | 950 | 1140 | 139.3773 | 0 | 146.7643 | 0.06105 | 1.3938 | 0 | 1.4676 | 0.0006105 | 1.3938 | 1.467 | 13.3763 | 7.7145 | 11.9825
39043.5522 | 2082 | 0 | 39043.5523 | 2077 | 1 |  | 992 | 1182 | 127.1062 | 0 | 126.801 | 0.06105 | 1.2711 | 0 | 1.268 | 0.0006105 | 1.2711 | 1.2674 | 24.3218 | 24.6811 | 23.0507
39043.5527 | 2072 | 0 | 39043.5528 | 2054 | 1 |  | 1034 | 1224 | 126.4957 | 0 | 125.3968 | 0.06105 | 1.265 | 0 | 1.254 | 0.0006105 | 1.265 | 1.2534 | 24.9218 | 26.0779 | 23.6569
39043.5532 | 2165 | 1 | 39043.5532 | 2082 | 0 |  | 1076 | 1266 | 132.1734 | 0.06105 | 127.1062 | 0 | 1.3217 | 0.0006105 | 1.2711 | 0 | 1.3211 | 1.2711 | 19.6019 | 24.3218 | 8263.2683
39043.5537 | 2105 | 0 | 39043.5537 | 2444 | 0 |  | 1118 | 1308 | 128.5104 | 0 | 149.2063 | 0 | 1.2851 | 0 | 1.4921 | 0 | 1.2851 | 1.4921 | 22.9634 | 5.9075 | 21.6783
39043.5542 | 2182 | 0 | 39043.5542 | 2128 | 0 |  | 1160 | 1350 | 133.2112 | 0 | 129.9145 | 0 | 1.3321 | 0 | 1.2991 | 0 | 1.3321 | 1.2991 | 18.6242 | 21.6344 | 17.2921
39043.5547 | 2140 | 0 | 39043.5547 | 1949 | 1 |  | 1201.5 | 1391.5 | 130.6471 | 0 | 118.9866 | 0.06105 | 1.3065 | 0 | 1.1899 | 0.0006105 | 1.3065 | 1.1893 | 20.9523 | 32.8737 | 19.6459
39043.5552 | 2022 | 0 | 39043.5552 | 2085 | 0 |  | 1243.5 | 1433.5 | 123.4432 | 0 | 127.2894 | 0 | 1.2344 | 0 | 1.2729 | 0 | 1.2344 | 1.2729 | 28.0109 | 24.1429 | 26.7764
39043.5556 | 2048 | 0 | 39043.5557 | 2139 | 0 |  | 1286 | 1476 | 125.0305 | 0 | 130.5861 | 0 | 1.2503 | 0 | 1.3059 | 0 | 1.2503 | 1.3059 | 26.3857 | 21.0089 | 25.1354
39043.5561 | 2274 | 0 | 39043.5562 | 2215 | 0 |  | 1328 | 1518 | 138.8278 | 0 | 135.2259 | 0 | 1.3883 | 0 | 1.3523 | 0 | 1.3883 | 1.3523 | 13.825 | 16.8569 | 12.4367
39043.5566 | 2404 | 0 | 39043.5566 | 2478 | 0 |  | 1369.5 | 1559.5 | 146.7643 | 0 | 151.2821 | 0 | 1.4676 | 0 | 1.5128 | 0 | 1.4676 | 1.5128 | 7.6697 | 4.4544 | 6.2021

## A1-B3
Open Burn Test 12 |  |  | 2006-11-22 | 13:02 |  |  | Vs = |  | 159.486 |  | R = | 100
Mixed | 7-C | Tray C | IRMS | 2
0 | 250 kW |  | Bundle | Ch. 1 & 3 | Cable A | Odd - | Cable B |  | Odd
Time-3 | N11 | N12 | Time-4 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R3-G | R1-3
39043.5386 | 0 | 0 | 39043.5386 | 0 | 0 |  | -186.5 | 3.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 522376 | 522376 | 522375.9997
39043.5391 | 0 | 0 | 39043.5391 | 0 | 0 |  | -144.5 | 45.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 522376 | 522376 | 522375.9997
39043.5396 | 0 | 0 | 39043.5396 | 0 | 0 |  | -103 | 87 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 522376 | 522376 | 522375.9997
39043.5401 | 0 | 0 | 39043.5401 | 0 | 0 |  | -61 | 129 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 522376 | 522376 | 522375.9997
39043.5405 | 0 | 0 | 39043.5406 | 0 | 0 |  | -19 | 171 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 522376 | 522376 | 522375.9997
39043.541 | 0 | 0 | 39043.5411 | 0 | 0 |  | 23.5 | 213.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 522376 | 522376 | 522375.9997
39043.5415 | 0 | 0 | 39043.5415 | 0 | 0 |  | 65.5 | 255.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 522376 | 522376 | 522375.9997
39043.542 | 0 | 0 | 39043.542 | 0 | 0 |  | 107.5 | 297.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 522376 | 522376 | 522375.9997
39043.5425 | 0 | 0 | 39043.5425 | 0 | 0 |  | 149.5 | 339.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 522376 | 522376 | 522375.9997
39043.543 | 0 | 0 | 39043.543 | 0 | 0 |  | 191 | 381 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 522376 | 522376 | 522375.9997
39043.5435 | 0 | 0 | 39043.5435 | 0 | 0 |  | 233 | 423 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 522376 | 522376 | 522375.9997
39043.5439 | 0 | 0 | 39043.544 | 0 | 0 |  | 275 | 465 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 522376 | 522376 | 522375.9997
39043.5444 | 59 | 1 | 39043.5445 | 0 | 0 |  | 317 | 507 | 3.602 | 0.06105 | 0.030525 | 0 | 0.03602 | 0.0006105 | 0.00030525 | 0 | 0.035409 | 0.00030525 | 4402.3938 | 522376 | 255189.1484
39043.5449 | 1506 | 60 | 39043.5449 | 1260 | 82 |  | 359 | 549 | 91.9414 | 3.663 | 76.9231 | 5.0061 | 0.91941 | 0.03663 | 0.76923 | 0.050061 | 0.88278 | 0.71917 | 79.1213 | 125.8775 | 971.8816
39043.5454 | 1956 | 20 | 39043.5454 | 1610 | 29 |  | 401 | 591 | 119.4139 | 1.221 | 98.2906 | 1.7705 | 1.1941 | 0.01221 | 0.98291 | 0.017705 | 1.1819 | 0.9652 | 34.4351 | 66.9689 | 1276.2161
39043.5459 | 2369 | 10 | 39043.5459 | 1960 | 12 |  | 443 | 633 | 144.6276 | 0.6105 | 119.6581 | 0.7326 | 1.4463 | 0.006105 | 1.1966 | 0.007326 | 1.4402 | 1.1893 | 10.4415 | 35.5894 | 612.5741
39043.5464 | 2386 | 7 | 39043.5464 | 1858 | 4 |  | 485 | 675 | 145.6654 | 0.42735 | 113.431 | 0.2442 | 1.4567 | 0.0042735 | 1.1343 | 0.002442 | 1.4524 | 1.1319 | 9.5835 | 41.6264 | 921.1364
39043.5469 | 1991 | 2 | 39043.5469 | 2069 | 1 |  | 527 | 717 | 121.5507 | 0.1221 | 126.3126 | 0.06105 | 1.2155 | 0.001221 | 1.2631 | 0.0006105 | 1.2143 | 1.2625 | 31.3607 | 26.3162 | 6451.9559
39043.5473 | 2429 | 0 | 39043.5474 | 2465 | 0 |  | 569 | 759 | 148.2906 | 0 | 150.4884 | 0 | 1.4829 | 0 | 1.5049 | 0 | 1.4829 | 1.5049 | 7.5496 | 5.9789 | 6.0667
39043.5478 | 2215 | 1 | 39043.5479 | 2251 | 0 |  | 611 | 801 | 135.2259 | 0.06105 | 137.4237 | 0 | 1.3523 | 0.0006105 | 1.3742 | 0 | 1.3516 | 1.3742 | 17.9991 | 16.0542 | 5483.2683
39043.5483 | 2419 | 1 | 39043.5483 | 2008 | 1 |  | 653 | 843 | 147.6801 | 0.06105 | 122.5885 | 0.06105 | 1.4768 | 0.0006105 | 1.2259 | 0.0006105 | 1.4762 | 1.2253 | 8.0084 | 30.3021 | 4473.8516
39043.5488 | 2335 | 1 | 39043.5488 | 2151 | 0 |  | 695 | 885 | 142.5519 | 0.06105 | 131.3187 | 0 | 1.4255 | 0.0006105 | 1.3132 | 0 | 1.4249 | 1.3132 | 11.9081 | 21.4496 | 4881.2272
39043.5493 | 2520 | 0 | 39043.5493 | 2367 | 1 |  | 737 | 927 | 153.8462 | 0 | 144.5055 | 0.06105 | 1.5385 | 0 | 1.4451 | 0.0006105 | 1.5385 | 1.4444 | 3.6659 | 10.4134 | 2.1274
39043.5498 | 2207 | 1 | 39043.5498 | 2003 | 0 |  | 779 | 969 | 134.7375 | 0.06105 | 122.2833 | 0 | 1.3474 | 0.0006105 | 1.2228 | 0 | 1.3468 | 1.2228 | 18.4037 | 30.4234 | 9432.8193
39043.5503 | 2074 | 1 | 39043.5503 | 1990 | 1 |  | 821 | 1011 | 126.6178 | 0.06105 | 121.4896 | 0.06105 | 1.2662 | 0.0006105 | 1.2149 | 0.0006105 | 1.2656 | 1.2143 | 26.0111 | 31.3517 | 12826.4626
39043.5508 | 2087 | 0 | 39043.5508 | 2320 | 1 |  | 863 | 1053 | 127.4115 | 0 | 141.6361 | 0.06105 | 1.2741 | 0 | 1.4164 | 0.0006105 | 1.2741 | 1.4158 | 25.1739 | 12.6511 | 23.8998
39043.5512 | 1999 | 0 | 39043.5513 | 2538 | 1 |  | 905 | 1095 | 122.0391 | 0 | 154.9451 | 0.06105 | 1.2204 | 0 | 1.5495 | 0.0006105 | 1.2204 | 1.5488 | 30.6843 | 2.9712 | 29.464
39043.5517 | 2279 | 0 | 39043.5517 | 2580 | 0 |  | 947 | 1137 | 139.1331 | 0 | 157.5092 | 0 | 1.3913 | 0 | 1.5751 | 0 | 1.3913 | 1.5751 | 14.6283 | 1.255 | 13.237
39043.5522 | 2596 | 1 | 39043.5522 | 2489 | 0 |  | 989 | 1179 | 158.486 | 0.06105 | 151.9536 | 0 | 1.5849 | 0.0006105 | 1.5195 | 0 | 1.5842 | 1.5195 | 0.63616 | 4.957 | 72.6381
39043.5527 | 2233 | 0 | 39043.5527 | 2220 | 1 |  | 1031 | 1221 | 136.3248 | 0 | 135.5311 | 0.06105 | 1.3632 | 0 | 1.3553 | 0.0006105 | 1.3632 | 1.3547 | 16.9897 | 17.7278 | 15.6265
39043.5532 | 2489 | 1 | 39043.5532 | 2390 | 0 |  | 1073 | 1263 | 151.9536 | 0.06105 | 145.9096 | 0 | 1.5195 | 0.0006105 | 1.4591 | 0 | 1.5189 | 1.4591 | 4.9805 | 9.3046 | 1041.7651
39043.5537 | 2521 | 1 | 39043.5537 | 2439 | 0 |  | 1115 | 1305 | 153.9072 | 0.06105 | 148.9011 | 0 | 1.5391 | 0.0006105 | 1.489 | 0 | 1.5385 | 1.489 | 3.6465 | 7.1087 | 599.8394
39043.5542 | 2445 | 0 | 39043.5542 | 2056 | 1 |  | 1157 | 1347 | 149.2674 | 0 | 125.5189 | 0.06105 | 1.4927 | 0 | 1.2552 | 0.0006105 | 1.4927 | 1.2546 | 6.8458 | 27.1231 | 5.3531
39043.5546 | 2383 | 0 | 39043.5547 | 2447 | 0 |  | 1199 | 1389 | 145.4823 | 0 | 149.3895 | 0 | 1.4548 | 0 | 1.4939 | 0 | 1.4548 | 1.4939 | 9.6257 | 6.7585 | 8.1709
39043.5551 | 1967 | 0 | 39043.5552 | 1944 | 0 |  | 1241 | 1431 | 120.0855 | 0 | 118.6813 | 0 | 1.2009 | 0 | 1.1868 | 0 | 1.2009 | 1.1868 | 32.8104 | 34.3817 | 31.6095
39043.5556 | 2405 | 0 | 39043.5556 | 2528 | 0 |  | 1283 | 1473 | 146.8254 | 0 | 154.3346 | 0 | 1.4683 | 0 | 1.5433 | 0 | 1.4683 | 1.5433 | 8.6229 | 3.3378 | 7.1546
39043.5561 | 2355 | 0 | 39043.5561 | 2403 | 0 |  | 1325 | 1515 | 143.7729 | 0 | 146.7033 | 0 | 1.4377 | 0 | 1.467 | 0 | 1.4377 | 1.467 | 10.9291 | 8.7133 | 9.4914
39043.5566 | 2083 | 0 | 39043.5566 | 2052 | 0 |  | 1367 | 1557 | 127.1673 | 0 | 125.2747 | 0 | 1.2717 | 0 | 1.2527 | 0 | 1.2717 | 1.2527 | 25.4143 | 27.309 | 24.1426

## A1-A2
Open Burn Test 12 |  |  | 2006-11-22 | 13:02 |  |  | Vs = |  | 160.2186 |  | R = | 100
Mixed | 7-C | Tray C | IRMS | 2
0 | 250 kW |  | Bundle | Ch. 1 & 2 | Cable A | Odd-Even
Time-1 | N11 | N12 | Time-2 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R2-G | R1-2
39043.5386 | 0 | 0 | 39043.5386 | 0 | 0 |  | -189.5 | 0.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 524776 | 524776 | 524775.9997
39043.5391 | 0 | 0 | 39043.5391 | 0 | 0 |  | -147.5 | 42.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 524776 | 524776 | 524775.9997
39043.5395 | 0 | 0 | 39043.5396 | 0 | 0 |  | -105.5 | 84.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 524776 | 524776 | 524775.9997
39043.54 | 0 | 0 | 39043.54 | 0 | 0 |  | -63.5 | 126.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 524776 | 524776 | 524775.9997
39043.5405 | 0 | 0 | 39043.5405 | 0 | 0 |  | -21.5 | 168.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 524776 | 524776 | 524775.9997
39043.541 | 0 | 0 | 39043.541 | 0 | 0 |  | 20.5 | 210.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 524776 | 524776 | 524775.9997
39043.5415 | 0 | 0 | 39043.5415 | 0 | 0 |  | 62.5 | 252.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 524776 | 524776 | 524775.9997
39043.542 | 0 | 0 | 39043.542 | 0 | 0 |  | 104.5 | 294.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 524776 | 524776 | 524775.9997
39043.5425 | 0 | 0 | 39043.5425 | 0 | 0 |  | 146.5 | 336.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 524776 | 524776 | 524775.9997
39043.543 | 0 | 0 | 39043.543 | 0 | 0 |  | 188.5 | 378.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 524776 | 524776 | 524775.9997
39043.5434 | 0 | 0 | 39043.5434 | 0 | 0 |  | 230.5 | 420.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 524776 | 524776 | 524775.9997
39043.5439 | 1038 | 969 | 39043.5439 | 953 | 1180 |  | 272.5 | 462.5 | 63.37 | 59.1575 | 58.1807 | 72.0391 | 0.6337 | 0.59158 | 0.58181 | 0.72039 | 0.042125 | 0.13858 | 1441.1848 | 2359.1159 | 61.1222
39043.5444 | 1056 | 1088 | 39043.5444 | 1024 | 1226 |  | 314.5 | 504.5 | 64.4689 | 66.4225 | 62.5153 | 74.8474 | 0.64469 | 0.66422 | 0.62515 | 0.74847 | 0.019536 | 0.12332 | 697.7273 | 564.3619 | 37.5067
39043.5449 | 1556 | 572 | 39043.5449 | 1717 | 413 |  | 356.5 | 546.5 | 94.9939 | 34.9206 | 104.823 | 25.2137 | 0.94994 | 0.34921 | 1.0482 | 0.25214 | 0.60073 | 0.79609 | 498.8577 | 74.3017 | 36.9926
39043.5454 | 2187 | 186 | 39043.5454 | 1754 | 240 |  | 398.5 | 588.5 | 133.5165 | 11.3553 | 107.0818 | 14.652 | 1.3352 | 0.11355 | 1.0708 | 0.14652 | 1.2216 | 0.9243 | 23.0165 | 184.6885 | 87.6774
39043.5459 | 1829 | 73 | 39043.5459 | 1906 | 61 |  | 440.5 | 630.5 | 111.6606 | 4.4567 | 116.3614 | 3.7241 | 1.1166 | 0.044567 | 1.1636 | 0.037241 | 1.072 | 1.1264 | 50.3139 | 41.6751 | 291.0894
39043.5464 | 1920 | 35 | 39043.5464 | 2117 | 30 |  | 482.5 | 672.5 | 117.2161 | 2.1368 | 129.243 | 1.8315 | 1.1722 | 0.021368 | 1.2924 | 0.018315 | 1.1508 | 1.2741 | 40.3387 | 25.2098 | 385.0666
39043.5468 | 2080 | 31 | 39043.5469 | 2059 | 33 |  | 524.5 | 714.5 | 126.9841 | 1.8926 | 125.7021 | 2.0147 | 1.2698 | 0.018926 | 1.257 | 0.020147 | 1.2509 | 1.2369 | 27.9977 | 29.63 | 378.5328
39043.5473 | 1919 | 4 | 39043.5473 | 2121 | 3 |  | 566.5 | 756.5 | 117.1551 | 0.2442 | 129.4872 | 0.18315 | 1.1716 | 0.002442 | 1.2949 | 0.0018315 | 1.1691 | 1.293 | 37.1598 | 23.8577 | 3377.5279
39043.5478 | 2274 | 2 | 39043.5478 | 2000 | 3 |  | 608.5 | 798.5 | 138.8278 | 0.1221 | 122.1001 | 0.18315 | 1.3883 | 0.001221 | 1.221 | 0.0018315 | 1.3871 | 1.2192 | 15.4648 | 31.5726 | 4179.921
39043.5483 | 2525 | 2 | 39043.5483 | 2374 | 2 |  | 650.5 | 840.5 | 154.1514 | 0.1221 | 144.9328 | 0.1221 | 1.5415 | 0.001221 | 1.4493 | 0.001221 | 1.5403 | 1.4481 | 3.9681 | 10.7848 | 473.9932
39043.5488 | 2441 | 2 | 39043.5488 | 2288 | 1 |  | 692.5 | 882.5 | 149.0232 | 0.1221 | 139.6825 | 0.06105 | 1.4902 | 0.001221 | 1.3968 | 0.0006105 | 1.489 | 1.3962 | 7.5606 | 14.7939 | 1168.7551
39043.5493 | 2527 | 1 | 39043.5493 | 2361 | 0 |  | 734.5 | 924.5 | 154.2735 | 0.06105 | 144.1392 | 0 | 1.5427 | 0.0006105 | 1.4414 | 0 | 1.5421 | 1.4414 | 3.8688 | 11.1554 | 967.2595
39043.5498 | 2364 | 1 | 39043.5498 | 2047 | 1 |  | 776.5 | 966.5 | 144.3223 | 0.06105 | 124.9695 | 0.06105 | 1.4432 | 0.0006105 | 1.2497 | 0.0006105 | 1.4426 | 1.2491 | 11.0355 | 28.3455 | 5728.4846
39043.5502 | 2453 | 1 | 39043.5503 | 2239 | 1 |  | 818.5 | 1008.5 | 149.7558 | 0.06105 | 136.6911 | 0.06105 | 1.4976 | 0.0006105 | 1.3669 | 0.0006105 | 1.4969 | 1.3663 | 7.0059 | 17.3304 | 2516.6106
39043.5507 | 2561 | 1 | 39043.5507 | 2608 | 0 |  | 860 | 1050 | 156.3492 | 0.06105 | 159.2186 | 0 | 1.5635 | 0.0006105 | 1.5922 | 0 | 1.5629 | 1.5922 | 2.64 | 0.62807 | 38.9343
39043.5512 | 2601 | 1 | 39043.5512 | 2589 | 0 |  | 902.5 | 1092.5 | 158.7912 | 0.06105 | 158.0586 | 0 | 1.5879 | 0.0006105 | 1.5806 | 0 | 1.5873 | 1.5806 | 0.92527 | 1.3666 | 30.1711
39043.5517 | 1994 | 0 | 39043.5517 | 2294 | 1 |  | 944.5 | 1134.5 | 121.7338 | 0 | 140.0488 | 0.06105 | 1.2173 | 0 | 1.4005 | 0.0006105 | 1.2173 | 1.3999 | 31.6138 | 14.4518 | 30.3965
39043.5522 | 2326 | 1 | 39043.5522 | 2373 | 1 |  | 986 | 1176 | 142.0024 | 0.06105 | 144.8718 | 0.06105 | 1.42 | 0.0006105 | 1.4487 | 0.0006105 | 1.4194 | 1.4481 | 12.8857 | 10.6326 | 2858.0375
39043.5527 | 2105 | 1 | 39043.5527 | 2495 | 1 |  | 1028 | 1218 | 128.5104 | 0.06105 | 152.3199 | 0.06105 | 1.2851 | 0.0006105 | 1.5232 | 0.0006105 | 1.2845 | 1.5226 | 24.9132 | 5.196 | 2560.467
39043.5532 | 2409 | 1 | 39043.5532 | 2516 | 0 |  | 1070.5 | 1260.5 | 147.0696 | 0.06105 | 153.602 | 0 | 1.4707 | 0.0006105 | 1.536 | 0 | 1.4701 | 1.536 | 9.0314 | 4.3076 | 885.3331
39043.5536 | 2391 | 0 | 39043.5537 | 2295 | 1 |  | 1112.5 | 1302.5 | 145.9707 | 0 | 140.1099 | 0.06105 | 1.4597 | 0 | 1.4011 | 0.0006105 | 1.4597 | 1.4005 | 9.7608 | 14.4019 | 8.3011
39043.5541 | 2089 | 1 | 39043.5541 | 2407 | 0 |  | 1154 | 1344 | 127.5336 | 0.06105 | 146.9475 | 0 | 1.2753 | 0.0006105 | 1.4695 | 0 | 1.2747 | 1.4695 | 25.7775 | 9.0312 | 4426.3226
39043.5546 | 2020 | 0 | 39043.5546 | 2312 | 1 |  | 1196 | 1386 | 123.3211 | 0 | 141.1477 | 0.06105 | 1.2332 | 0 | 1.4115 | 0.0006105 | 1.2332 | 1.4109 | 29.9198 | 13.5604 | 28.6866
39043.5551 | 2152 | 1 | 39043.5551 | 2096 | 0 |  | 1238 | 1428 | 131.3797 | 0.06105 | 127.9609 | 0 | 1.3138 | 0.0006105 | 1.2796 | 0 | 1.3132 | 1.2796 | 22.0015 | 25.209 | 9490.5374
39043.5556 | 2489 | 1 | 39043.5556 | 1968 | 0 |  | 1280.5 | 1470.5 | 151.9536 | 0.06105 | 120.1465 | 0 | 1.5195 | 0.0006105 | 1.2015 | 0 | 1.5189 | 1.2015 | 5.4479 | 33.3526 | 3360.9593
39043.5561 | 2521 | 2 | 39043.5561 | 2322 | 2 |  | 1322.5 | 1512.5 | 153.9072 | 0.1221 | 141.7582 | 0.1221 | 1.5391 | 0.001221 | 1.4176 | 0.001221 | 1.5379 | 1.4164 | 4.1286 | 13.3116 | 595.4939
39043.5566 | 2233 | 3 | 39043.5566 | 2167 | 3 |  | 1364 | 1554 | 136.3248 | 0.18315 | 132.2955 | 0.18315 | 1.3632 | 0.0018315 | 1.323 | 0.0018315 | 1.3614 | 1.3211 | 17.6622 | 21.3031 | 2273.5577

## Raw IRMS Data
Time | DL1.V2000:B | DL1.V2001:B | DL1.V1500:B | Open Burn Test 12 |  |  | 2006-11-22 | 13:02
39043.5386 | 0 | 0 | 1 | Mixed | 7-C | Tray C | IRMS | 2
39043.5391 | 0 | 0 | 1 |  | 250 kW |  | Bundle
39043.5395 | 0 | 0 | 1
39043.54 | 0 | 0 | 1
39043.5405 | 0 | 0 | 1
39043.541 | 0 | 0 | 1
39043.5415 | 0 | 0 | 1
39043.542 | 0 | 0 | 1
39043.5425 | 0 | 0 | 1
39043.543 | 0 | 0 | 1
39043.5434 | 0 | 0 | 1
39043.5439 | 1038 | 969 | 1
39043.5444 | 1056 | 1088 | 1
39043.5449 | 1556 | 572 | 1
39043.5454 | 2187 | 186 | 1
39043.5459 | 1829 | 73 | 1
39043.5464 | 1920 | 35 | 1
39043.5468 | 2080 | 31 | 1
39043.5473 | 1919 | 4 | 1
39043.5478 | 2274 | 2 | 1
39043.5483 | 2525 | 2 | 1
39043.5488 | 2441 | 2 | 1
39043.5493 | 2527 | 1 | 1
39043.5498 | 2364 | 1 | 1
39043.5502 | 2453 | 1 | 1
39043.5507 | 2561 | 1 | 1
39043.5512 | 2601 | 1 | 1
39043.5517 | 1994 | 0 | 1
39043.5522 | 2326 | 1 | 1
39043.5527 | 2105 | 1 | 1
39043.5532 | 2409 | 1 | 1
39043.5536 | 2391 | 0 | 1
39043.5541 | 2089 | 1 | 1
39043.5546 | 2020 | 0 | 1
39043.5551 | 2152 | 1 | 1
39043.5556 | 2489 | 1 | 1
39043.5561 | 2521 | 2 | 1
39043.5566 | 2233 | 3 | 1
1
39043.5386 | 0 | 0 | 2
39043.5391 | 0 | 0 | 2
39043.5396 | 0 | 0 | 2
39043.54 | 0 | 0 | 2
39043.5405 | 0 | 0 | 2
39043.541 | 0 | 0 | 2
39043.5415 | 0 | 0 | 2
39043.542 | 0 | 0 | 2
39043.5425 | 0 | 0 | 2
39043.543 | 0 | 0 | 2
39043.5434 | 0 | 0 | 2
39043.5439 | 953 | 1180 | 2
39043.5444 | 1024 | 1226 | 2
39043.5449 | 1717 | 413 | 2
39043.5454 | 1754 | 240 | 2
39043.5459 | 1906 | 61 | 2
39043.5464 | 2117 | 30 | 2
39043.5469 | 2059 | 33 | 2
39043.5473 | 2121 | 3 | 2
39043.5478 | 2000 | 3 | 2
39043.5483 | 2374 | 2 | 2
39043.5488 | 2288 | 1 | 2
39043.5493 | 2361 | 0 | 2
39043.5498 | 2047 | 1 | 2
39043.5503 | 2239 | 1 | 2
39043.5507 | 2608 | 0 | 2
39043.5512 | 2589 | 0 | 2
39043.5517 | 2294 | 1 | 2
39043.5522 | 2373 | 1 | 2
39043.5527 | 2495 | 1 | 2
39043.5532 | 2516 | 0 | 2
39043.5537 | 2295 | 1 | 2
39043.5541 | 2407 | 0 | 2
39043.5546 | 2312 | 1 | 2
39043.5551 | 2096 | 0 | 2
39043.5556 | 1968 | 0 | 2
39043.5561 | 2322 | 2 | 2
39043.5566 | 2167 | 3 | 2
2
39043.5386 | 0 | 0 | 3
39043.5391 | 0 | 0 | 3
39043.5396 | 0 | 0 | 3
39043.5401 | 0 | 0 | 3
39043.5405 | 0 | 0 | 3
39043.541 | 0 | 0 | 3
39043.5415 | 0 | 0 | 3
39043.542 | 0 | 0 | 3
39043.5425 | 0 | 0 | 3
39043.543 | 0 | 0 | 3
39043.5435 | 0 | 0 | 3
39043.5439 | 0 | 0 | 3
39043.5444 | 59 | 0 | 3
39043.5449 | 1506 | 60 | 3
39043.5454 | 1956 | 20 | 3
39043.5459 | 2369 | 10 | 3
39043.5464 | 2386 | 7 | 3
39043.5469 | 1991 | 2 | 3
39043.5473 | 2429 | 0 | 3
39043.5478 | 2215 | 1 | 3
39043.5483 | 2419 | 1 | 3
39043.5488 | 2335 | 1 | 3
39043.5493 | 2520 | 0 | 3
39043.5498 | 2207 | 1 | 3
39043.5503 | 2074 | 1 | 3
39043.5508 | 2087 | 0 | 3
39043.5512 | 1999 | 0 | 3
39043.5517 | 2279 | 0 | 3
39043.5522 | 2596 | 1 | 3
39043.5527 | 2233 | 0 | 3
39043.5532 | 2489 | 1 | 3
39043.5537 | 2521 | 1 | 3
39043.5542 | 2445 | 0 | 3
39043.5546 | 2383 | 0 | 3
39043.5551 | 1967 | 0 | 3
39043.5556 | 2405 | 0 | 3
39043.5561 | 2355 | 0 | 3
39043.5566 | 2083 | 0 | 3
3
39043.5386 | 0 | 0 | 4
39043.5391 | 0 | 0 | 4
39043.5396 | 0 | 0 | 4
39043.5401 | 0 | 0 | 4
39043.5406 | 0 | 0 | 4
39043.5411 | 0 | 0 | 4
39043.5415 | 0 | 0 | 4
39043.542 | 0 | 0 | 4
39043.5425 | 0 | 0 | 4
39043.543 | 0 | 0 | 4
39043.5435 | 0 | 0 | 4
39043.544 | 0 | 0 | 4
39043.5445 | 0 | 0 | 4
39043.5449 | 1260 | 82 | 4
39043.5454 | 1610 | 29 | 4
39043.5459 | 1960 | 12 | 4
39043.5464 | 1858 | 4 | 4
39043.5469 | 2069 | 1 | 4
39043.5474 | 2465 | 0 | 4
39043.5479 | 2251 | 0 | 4
39043.5483 | 2008 | 1 | 4
39043.5488 | 2151 | 0 | 4
39043.5493 | 2367 | 1 | 4
39043.5498 | 2003 | 0 | 4
39043.5503 | 1990 | 1 | 4
39043.5508 | 2320 | 1 | 4
39043.5513 | 2538 | 1 | 4
39043.5517 | 2580 | 0 | 4
39043.5522 | 2489 | 0 | 4
39043.5527 | 2220 | 1 | 4
39043.5532 | 2390 | 0 | 4
39043.5537 | 2439 | 0 | 4
39043.5542 | 2056 | 1 | 4
39043.5547 | 2447 | 0 | 4
39043.5552 | 1944 | 0 | 4
39043.5556 | 2528 | 0 | 4
39043.5561 | 2403 | 0 | 4
39043.5566 | 2052 | 0 | 4
4
39043.5386 | 0 | 0 | 5
39043.5391 | 0 | 0 | 5
39043.5396 | 0 | 0 | 5
39043.5401 | 0 | 0 | 5
39043.5406 | 0 | 0 | 5
39043.5411 | 0 | 0 | 5
39043.5416 | 0 | 0 | 5
39043.542 | 0 | 0 | 5
39043.5425 | 0 | 0 | 5
39043.543 | 0 | 0 | 5
39043.5435 | 0 | 0 | 5
39043.544 | 0 | 0 | 5
39043.5445 | 420 | 0 | 5
39043.545 | 1485 | 107 | 5
39043.5454 | 1751 | 20 | 5
39043.5459 | 2332 | 9 | 5
39043.5464 | 2083 | 5 | 5
39043.5469 | 2382 | 1 | 5
39043.5474 | 2049 | 0 | 5
39043.5479 | 2437 | 0 | 5
39043.5484 | 2270 | 1 | 5
39043.5488 | 2131 | 0 | 5
39043.5493 | 2553 | 0 | 5
39043.5498 | 2024 | 0 | 5
39043.5503 | 2269 | 1 | 5
39043.5508 | 2005 | 0 | 5
39043.5513 | 2572 | 0 | 5
39043.5518 | 2283 | 0 | 5
39043.5522 | 2082 | 0 | 5
39043.5527 | 2072 | 0 | 5
39043.5532 | 2165 | 1 | 5
39043.5537 | 2105 | 0 | 5
39043.5542 | 2182 | 0 | 5
39043.5547 | 2140 | 0 | 5
39043.5552 | 2022 | 0 | 5
39043.5556 | 2048 | 0 | 5
39043.5561 | 2274 | 0 | 5
39043.5566 | 2404 | 0 | 5
5
39043.5387 | 0 | 0 | 6
39043.5391 | 0 | 0 | 6
39043.5396 | 0 | 0 | 6
39043.5401 | 0 | 0 | 6
39043.5406 | 0 | 0 | 6
39043.5411 | 0 | 0 | 6
39043.5416 | 0 | 0 | 6
39043.5421 | 0 | 0 | 6
39043.5425 | 0 | 0 | 6
39043.543 | 0 | 0 | 6
39043.5435 | 0 | 0 | 6
39043.544 | 0 | 0 | 6
39043.5445 | 0 | 0 | 6
39043.545 | 1332 | 124 | 6
39043.5455 | 1682 | 17 | 6
39043.5459 | 1912 | 11 | 6
39043.5464 | 1818 | 13 | 6
39043.5469 | 2429 | 1 | 6
39043.5474 | 2389 | 0 | 6
39043.5479 | 2041 | 0 | 6
39043.5484 | 2303 | 1 | 6
39043.5489 | 2551 | 1 | 6
39043.5494 | 2557 | 1 | 6
39043.5498 | 2400 | 0 | 6
39043.5503 | 2498 | 1 | 6
39043.5508 | 2266 | 0 | 6
39043.5513 | 2108 | 1 | 6
39043.5518 | 2404 | 1 | 6
39043.5523 | 2077 | 1 | 6
39043.5528 | 2054 | 1 | 6
39043.5532 | 2082 | 0 | 6
39043.5537 | 2444 | 0 | 6
39043.5542 | 2128 | 0 | 6
39043.5547 | 1949 | 1 | 6
39043.5552 | 2085 | 0 | 6
39043.5557 | 2139 | 0 | 6
39043.5562 | 2215 | 0 | 6
39043.5566 | 2478 | 0 | 6
6
39043.5387 | 0 | 0 | 7
39043.5392 | 0 | 0 | 7
39043.5396 | 0 | 0 | 7
39043.5401 | 0 | 0 | 7
39043.5406 | 0 | 0 | 7
39043.5411 | 0 | 0 | 7
39043.5416 | 0 | 0 | 7
39043.5421 | 0 | 0 | 7
39043.5426 | 0 | 0 | 7
39043.543 | 0 | 0 | 7
39043.5435 | 0 | 0 | 7
39043.544 | 0 | 0 | 7
39043.5445 | 764 | 0 | 7
39043.545 | 1554 | 0 | 7
39043.5455 | 1923 | 0 | 7
39043.546 | 2070 | 0 | 7
39043.5464 | 1830 | 0 | 7
39043.5469 | 2240 | 0 | 7
39043.5474 | 2386 | 0 | 7
39043.5479 | 1958 | 0 | 7
39043.5484 | 2398 | 0 | 7
39043.5489 | 2542 | 1 | 7
39043.5494 | 2132 | 1 | 7
39043.5498 | 2186 | 0 | 7
39043.5503 | 2147 | 0 | 7
39043.5508 | 2569 | 1 | 7
39043.5513 | 2431 | 1 | 7
39043.5518 | 2603 | 0 | 7
39043.5523 | 2566 | 0 | 7
39043.5528 | 2086 | 1 | 7
39043.5533 | 2608 | 0 | 7
39043.5537 | 2290 | 1 | 7
39043.5542 | 2063 | 0 | 7
39043.5547 | 2117 | 0 | 7
39043.5552 | 2451 | 0 | 7
39043.5557 | 2280 | 0 | 7
39043.5562 | 2520 | 0 | 7
39043.5567 | 2326 | 0 | 7
7
39043.5387 | 0 | 0 | 8
39043.5392 | 0 | 0 | 8
39043.5397 | 0 | 0 | 8
39043.5401 | 0 | 0 | 8
39043.5406 | 0 | 0 | 8
39043.5411 | 0 | 0 | 8
39043.5416 | 0 | 0 | 8
39043.5421 | 0 | 0 | 8
39043.5426 | 0 | 0 | 8
39043.5431 | 0 | 0 | 8
39043.5435 | 0 | 0 | 8
39043.544 | 0 | 0 | 8
39043.5445 | 0 | 0 | 8
39043.545 | 0 | 0 | 8
39043.5455 | 1172 | 0 | 8
39043.546 | 1928 | 0 | 8
39043.5465 | 2021 | 0 | 8
39043.5469 | 2413 | 0 | 8
39043.5474 | 2438 | 0 | 8
39043.5479 | 2427 | 0 | 8
39043.5484 | 2494 | 1 | 8
39043.5489 | 2540 | 1 | 8
39043.5494 | 2041 | 1 | 8
39043.5499 | 2255 | 0 | 8
39043.5503 | 2469 | 1 | 8
39043.5508 | 2567 | 0 | 8
39043.5513 | 2094 | 1 | 8
39043.5518 | 2506 | 0 | 8
39043.5523 | 2553 | 1 | 8
39043.5528 | 2393 | 0 | 8
39043.5533 | 2032 | 0 | 8
39043.5537 | 2071 | 1 | 8
39043.5542 | 2375 | 0 | 8
39043.5547 | 2105 | 0 | 8
39043.5552 | 1909 | 0 | 8
39043.5557 | 771 | 0 | 8
39043.5562 | 500 | 0 | 8
39043.5567 | 64 | 0 | 8
8
39043.5387 | 0 | 0 | 9
39043.5392 | 0 | 0 | 9
39043.5397 | 0 | 0 | 9
39043.5402 | 0 | 0 | 9
39043.5406 | 0 | 0 | 9
39043.5411 | 0 | 0 | 9
39043.5416 | 0 | 0 | 9
39043.5421 | 0 | 0 | 9
39043.5426 | 0 | 1 | 9
39043.5431 | 0 | 0 | 9
39043.5436 | 0 | 0 | 9
39043.5441 | 0 | 0 | 9
39043.5445 | 804 | 0 | 9
39043.545 | 1575 | 0 | 9
39043.5455 | 2055 | 0 | 9
39043.546 | 1837 | 0 | 9
39043.5465 | 1939 | 0 | 9
39043.547 | 2099 | 0 | 9
39043.5475 | 2015 | 0 | 9
39043.5479 | 2418 | 0 | 9
39043.5484 | 2517 | 0 | 9
39043.5489 | 2133 | 1 | 9
39043.5494 | 2041 | 1 | 9
39043.5499 | 2011 | 1 | 9
39043.5504 | 1997 | 1 | 9
39043.5509 | 2093 | 0 | 9
39043.5513 | 2109 | 1 | 9
39043.5518 | 2577 | 0 | 9
39043.5523 | 2058 | 0 | 9
39043.5528 | 2285 | 0 | 9
39043.5533 | 2012 | 0 | 9
39043.5538 | 2604 | 0 | 9
39043.5543 | 2029 | 1 | 9
39043.5547 | 2234 | 0 | 9
39043.5552 | 2578 | 0 | 9
39043.5557 | 2273 | 0 | 9
39043.5562 | 2316 | 0 | 9
39043.5567 | 2111 | 0 | 9
9
39043.5387 | 0 | 0 | 10
39043.5392 | 0 | 0 | 10
39043.5397 | 0 | 0 | 10
39043.5402 | 0 | 0 | 10
39043.5407 | 0 | 0 | 10
39043.5411 | 0 | 0 | 10
39043.5416 | 0 | 0 | 10
39043.5421 | 0 | 0 | 10
39043.5426 | 0 | 0 | 10
39043.5431 | 0 | 0 | 10
39043.5436 | 0 | 0 | 10
39043.5441 | 0 | 0 | 10
39043.5445 | 0 | 0 | 10
39043.545 | 0 | 0 | 10
39043.5455 | 1845 | 0 | 10
39043.546 | 1880 | 0 | 10
39043.5465 | 2311 | 0 | 10
39043.547 | 1942 | 0 | 10
39043.5475 | 2074 | 0 | 10
39043.548 | 2274 | 0 | 10
39043.5484 | 2182 | 1 | 10
39043.5489 | 2007 | 1 | 10
39043.5494 | 2322 | 0 | 10
39043.5499 | 1945 | 1 | 10
39043.5504 | 1967 | 0 | 10
39043.5509 | 1945 | 0 | 10
39043.5514 | 2246 | 0 | 10
39043.5518 | 1948 | 0 | 10
39043.5523 | 1976 | 1 | 10
39043.5528 | 2005 | 0 | 10
39043.5533 | 2196 | 1 | 10
39043.5538 | 2421 | 1 | 10
39043.5543 | 2216 | 1 | 10
39043.5548 | 1877 | 1 | 10
39043.5552 | 2178 | 0 | 10
39043.5557 | 937 | 0 | 10
39043.5562 | 1970 | 1 | 10
39043.5567 | 1922 | 3 | 10
10
39043.5387 | 0 | 0 | 11
39043.5392 | 0 | 0 | 11
39043.5397 | 0 | 0 | 11
39043.5402 | 0 | 0 | 11
39043.5407 | 0 | 0 | 11
39043.5412 | 0 | 0 | 11
39043.5417 | 0 | 0 | 11
39043.5421 | 0 | 0 | 11
39043.5426 | 0 | 0 | 11
39043.5431 | 0 | 0 | 11
39043.5436 | 0 | 0 | 11
39043.5441 | 0 | 0 | 11
39043.5446 | 616 | 0 | 11
39043.5451 | 1576 | 41 | 11
39043.5455 | 2190 | 14 | 11
39043.546 | 2387 | 9 | 11
39043.5465 | 1988 | 4 | 11
39043.547 | 2325 | 1 | 11
39043.5475 | 2038 | 0 | 11
39043.548 | 2265 | 0 | 11
39043.5485 | 1968 | 1 | 11
39043.5489 | 2360 | 1 | 11
39043.5494 | 2194 | 0 | 11
39043.5499 | 2007 | 0 | 11
39043.5504 | 2065 | 0 | 11
39043.5509 | 1988 | 0 | 11
39043.5514 | 2286 | 0 | 11
39043.5519 | 2298 | 0 | 11
39043.5523 | 2507 | 1 | 11
39043.5528 | 2099 | 1 | 11
39043.5533 | 2339 | 0 | 11
39043.5538 | 2019 | 0 | 11
39043.5543 | 2286 | 0 | 11
39043.5548 | 2267 | 0 | 11
39043.5553 | 1996 | 0 | 11
39043.5557 | 2465 | 0 | 11
39043.5562 | 2306 | 0 | 11
39043.5567 | 1937 | 0 | 11
11
39043.5387 | 0 | 0 | 12
39043.5392 | 0 | 0 | 12
39043.5397 | 0 | 0 | 12
39043.5402 | 0 | 0 | 12
39043.5407 | 0 | 0 | 12
39043.5412 | 0 | 0 | 12
39043.5417 | 0 | 0 | 12
39043.5422 | 0 | 0 | 12
39043.5426 | 0 | 0 | 12
39043.5431 | 0 | 0 | 12
39043.5436 | 0 | 0 | 12
39043.5441 | 0 | 0 | 12
39043.5446 | 0 | 0 | 12
39043.5451 | 1115 | 6 | 12
39043.5456 | 1566 | 5 | 12
39043.546 | 1917 | 9 | 12
39043.5465 | 1910 | 2 | 12
39043.547 | 1962 | 0 | 12
39043.5475 | 2105 | 0 | 12
39043.548 | 2540 | 0 | 12
39043.5485 | 2043 | 0 | 12
39043.549 | 2097 | 1 | 12
39043.5494 | 2149 | 1 | 12
39043.5499 | 2021 | 0 | 12
39043.5504 | 2092 | 0 | 12
39043.5509 | 2211 | 1 | 12
39043.5514 | 2158 | 1 | 12
39043.5519 | 2321 | 0 | 12
39043.5524 | 2524 | 0 | 12
39043.5528 | 2058 | 0 | 12
39043.5533 | 2434 | 0 | 12
39043.5538 | 2168 | 0 | 12
39043.5543 | 2408 | 0 | 12
39043.5548 | 1907 | 0 | 12
39043.5553 | 2195 | 0 | 12
39043.5558 | 2384 | 0 | 12
39043.5563 | 2569 | 0 | 12
39043.5567 | 2572 | 0 | 12
12
39043.5388 | 0 | 0 | 13
39043.5393 | 0 | 0 | 13
39043.5397 | 0 | 0 | 13
39043.5402 | 0 | 0 | 13
39043.5407 | 0 | 0 | 13
39043.5412 | 0 | 0 | 13
39043.5417 | 0 | 0 | 13
39043.5422 | 0 | 0 | 13
39043.5427 | 0 | 0 | 13
39043.5431 | 0 | 0 | 13
39043.5436 | 0 | 0 | 13
39043.5441 | 0 | 0 | 13
39043.5446 | 1385 | 0 | 13
39043.5451 | 1722 | 97 | 13
39043.5456 | 2109 | 3 | 13
39043.5461 | 1885 | 8 | 13
39043.5465 | 1879 | 4 | 13
39043.547 | 1939 | 1 | 13
39043.5475 | 2374 | 0 | 13
39043.548 | 2393 | 1 | 13
39043.5485 | 2253 | 0 | 13
39043.549 | 2414 | 0 | 13
39043.5495 | 2102 | 1 | 13
39043.5499 | 1973 | 0 | 13
39043.5504 | 2558 | 0 | 13
39043.5509 | 2415 | 0 | 13
39043.5514 | 2488 | 0 | 13
39043.5519 | 1999 | 0 | 13
39043.5524 | 2244 | 1 | 13
39043.5529 | 2175 | 1 | 13
39043.5533 | 2054 | 0 | 13
39043.5538 | 2502 | 0 | 13
39043.5543 | 2395 | 0 | 13
39043.5548 | 2194 | 0 | 13
39043.5553 | 2482 | 0 | 13
39043.5558 | 2518 | 0 | 13
39043.5563 | 2057 | 0 | 13
39043.5567 | 2512 | 0 | 13
13
39043.5388 | 0 | 0 | 14
39043.5393 | 0 | 0 | 14
39043.5398 | 0 | 0 | 14
39043.5402 | 0 | 0 | 14
39043.5407 | 0 | 0 | 14
39043.5412 | 0 | 0 | 14
39043.5417 | 0 | 0 | 14
39043.5422 | 0 | 0 | 14
39043.5427 | 0 | 0 | 14
39043.5432 | 0 | 0 | 14
39043.5436 | 0 | 0 | 14
39043.5441 | 0 | 0 | 14
39043.5446 | 1462 | 0 | 14
39043.5451 | 1507 | 9 | 14
39043.5456 | 2139 | 3 | 14
39043.5461 | 1867 | 8 | 14
39043.5466 | 2102 | 4 | 14
39043.547 | 2110 | 1 | 14
39043.5475 | 1913 | 0 | 14
39043.548 | 2117 | 0 | 14
39043.5485 | 2386 | 1 | 14
39043.549 | 2052 | 1 | 14
39043.5495 | 2469 | 0 | 14
39043.55 | 2545 | 0 | 14
39043.5505 | 2175 | 1 | 14
39043.5509 | 2298 | 1 | 14
39043.5514 | 1988 | 0 | 14
39043.5519 | 2492 | 0 | 14
39043.5524 | 2092 | 0 | 14
39043.5529 | 2612 | 1 | 14
39043.5534 | 2388 | 0 | 14
39043.5539 | 2080 | 0 | 14
39043.5543 | 2327 | 0 | 14
39043.5548 | 2243 | 0 | 14
39043.5553 | 2538 | 0 | 14
39043.5558 | 2550 | 0 | 14
39043.5563 | 2517 | 0 | 14
39043.5568 | 2353 | 0 | 14
14
39043.5388 | 0 | 0 | 15
39043.5393 | 0 | 0 | 15
39043.5398 | 0 | 0 | 15
39043.5403 | 0 | 0 | 15
39043.5407 | 0 | 0 | 15
39043.5412 | 0 | 0 | 15
39043.5417 | 0 | 0 | 15
39043.5422 | 0 | 0 | 15
39043.5427 | 0 | 0 | 15
39043.5432 | 0 | 0 | 15
39043.5437 | 0 | 0 | 15
39043.5441 | 0 | 0 | 15
39043.5446 | 1516 | 0 | 15
39043.5451 | 1980 | 0 | 15
39043.5456 | 1967 | 0 | 15
39043.5461 | 2360 | 0 | 15
39043.5466 | 2367 | 0 | 15
39043.5471 | 2219 | 20 | 15
39043.5475 | 2211 | 0 | 15
39043.548 | 1958 | 0 | 15
39043.5485 | 1940 | 0 | 15
39043.549 | 2546 | 1 | 15
39043.5495 | 2230 | 1 | 15
39043.55 | 2437 | 0 | 15
39043.5505 | 2500 | 0 | 15
39043.5509 | 2252 | 0 | 15
39043.5514 | 2346 | 1 | 15
39043.5519 | 2616 | 1 | 15
39043.5524 | 2332 | 0 | 15
39043.5529 | 2201 | 1 | 15
39043.5534 | 2609 | 0 | 15
39043.5539 | 2460 | 1 | 15
39043.5544 | 2300 | 0 | 15
39043.5548 | 2115 | 0 | 15
39043.5553 | 2161 | 0 | 15
39043.5558 | 2072 | 0 | 15
39043.5563 | 2214 | 0 | 15
39043.5568 | 2393 | 0 | 15
15
39043.5388 | 0 | 0 | 16
39043.5393 | 0 | 1 | 16
39043.5398 | 0 | 0 | 16
39043.5403 | 0 | 0 | 16
39043.5408 | 0 | 0 | 16
39043.5413 | 0 | 0 | 16
39043.5417 | 0 | 0 | 16
39043.5422 | 0 | 0 | 16
39043.5427 | 0 | 0 | 16
39043.5432 | 0 | 0 | 16
39043.5437 | 0 | 0 | 16
39043.5442 | 0 | 0 | 16
39043.5447 | 0 | 0 | 16
39043.5451 | 0 | 0 | 16
39043.5456 | 1539 | 0 | 16
39043.5461 | 2211 | 0 | 16
39043.5466 | 2365 | 0 | 16
39043.5471 | 2432 | 0 | 16
39043.5476 | 2007 | 0 | 16
39043.5481 | 1999 | 0 | 16
39043.5485 | 2131 | 1 | 16
39043.549 | 2146 | 1 | 16
39043.5495 | 2577 | 1 | 16
39043.55 | 2246 | 0 | 16
39043.5505 | 2054 | 1 | 16
39043.551 | 2456 | 1 | 16
39043.5515 | 2532 | 1 | 16
39043.5519 | 2116 | 0 | 16
39043.5524 | 2020 | 1 | 16
39043.5529 | 1989 | 1 | 16
39043.5534 | 2107 | 0 | 16
39043.5539 | 1933 | 0 | 16
39043.5544 | 1926 | 0 | 16
39043.5548 | 2376 | 0 | 16
39043.5553 | 2080 | 0 | 16
39043.5558 | 587 | 0 | 16
39043.5563 | 606 | 0 | 16
39043.5568 | 98 | 0 | 16
16
39043.5388 | 0 | 0 | 17
39043.5393 | 0 | 0 | 17
39043.5398 | 0 | 0 | 17
39043.5403 | 0 | 0 | 17
39043.5408 | 0 | 0 | 17
39043.5413 | 0 | 0 | 17
39043.5417 | 0 | 0 | 17
39043.5422 | 0 | 0 | 17
39043.5427 | 0 | 0 | 17
39043.5432 | 0 | 0 | 17
39043.5437 | 0 | 0 | 17
39043.5442 | 0 | 0 | 17
39043.5447 | 1388 | 0 | 17
39043.5452 | 1716 | 0 | 17
39043.5456 | 1969 | 0 | 17
39043.5461 | 2009 | 0 | 17
39043.5466 | 1791 | 0 | 17
39043.5471 | 2329 | 12 | 17
39043.5476 | 2434 | 0 | 17
39043.5481 | 2174 | 0 | 17
39043.5486 | 2085 | 1 | 17
39043.549 | 2323 | 0 | 17
39043.5495 | 2468 | 1 | 17
39043.55 | 2387 | 1 | 17
39043.5505 | 2007 | 0 | 17
39043.551 | 2027 | 1 | 17
39043.5515 | 2125 | 0 | 17
39043.552 | 2110 | 1 | 17
39043.5524 | 2429 | 0 | 17
39043.5529 | 2178 | 1 | 17
39043.5534 | 2427 | 1 | 17
39043.5539 | 2589 | 1 | 17
39043.5544 | 2087 | 0 | 17
39043.5549 | 2076 | 1 | 17
39043.5554 | 2261 | 0 | 17
39043.5558 | 2478 | 0 | 17
39043.5563 | 1959 | 0 | 17
39043.5568 | 1952 | 0 | 17
17
39043.5388 | 0 | 0 | 18
39043.5393 | 0 | 0 | 18
39043.5398 | 0 | 0 | 18
39043.5403 | 0 | 0 | 18
39043.5408 | 0 | 0 | 18
39043.5413 | 0 | 0 | 18
39043.5418 | 0 | 0 | 18
39043.5422 | 0 | 0 | 18
39043.5427 | 0 | 0 | 18
39043.5432 | 0 | 0 | 18
39043.5437 | 0 | 0 | 18
39043.5442 | 0 | 0 | 18
39043.5447 | 0 | 0 | 18
39043.5452 | 0 | 0 | 18
39043.5456 | 1494 | 0 | 18
39043.5461 | 2070 | 0 | 18
39043.5466 | 1916 | 0 | 18
39043.5471 | 2296 | 1 | 18
39043.5476 | 2442 | 0 | 18
39043.5481 | 2546 | 0 | 18
39043.5486 | 2446 | 1 | 18
39043.5491 | 2400 | 0 | 18
39043.5495 | 1984 | 0 | 18
39043.55 | 2117 | 0 | 18
39043.5505 | 2157 | 1 | 18
39043.551 | 1967 | 1 | 18
39043.5515 | 2264 | 1 | 18
39043.552 | 2043 | 0 | 18
39043.5525 | 2164 | 0 | 18
39043.5529 | 2154 | 1 | 18
39043.5534 | 2535 | 1 | 18
39043.5539 | 2503 | 0 | 18
39043.5544 | 1929 | 1 | 18
39043.5549 | 2254 | 0 | 18
39043.5554 | 2138 | 0 | 18
39043.5559 | 1914 | 1 | 18
39043.5563 | 2146 | 1 | 18
39043.5568 | 2195 | 4 | 18
18
39043.5389 | 0 | 0 | 19
39043.5394 | 0 | 0 | 19
39043.5398 | 0 | 0 | 19
39043.5403 | 0 | 0 | 19
39043.5408 | 0 | 0 | 19
39043.5413 | 0 | 0 | 19
39043.5418 | 0 | 0 | 19
39043.5423 | 0 | 0 | 19
39043.5428 | 0 | 0 | 19
39043.5432 | 0 | 0 | 19
39043.5437 | 0 | 0 | 19
39043.5442 | 0 | 0 | 19
39043.5447 | 0 | 0 | 19
39043.5452 | 1384 | 190 | 19
39043.5457 | 1747 | 274 | 19
39043.5462 | 2180 | 120 | 19
39043.5466 | 2379 | 32 | 19
39043.5471 | 2011 | 4 | 19
39043.5476 | 1989 | 1 | 19
39043.5481 | 2168 | 0 | 19
39043.5486 | 2005 | 1 | 19
39043.5491 | 2316 | 1 | 19
39043.5496 | 2487 | 1 | 19
39043.55 | 2542 | 1 | 19
39043.5505 | 2486 | 1 | 19
39043.551 | 1982 | 1 | 19
39043.5515 | 2037 | 1 | 19
39043.552 | 2574 | 1 | 19
39043.5525 | 2475 | 1 | 19
39043.553 | 2028 | 1 | 19
39043.5534 | 2074 | 2 | 19
39043.5539 | 2167 | 2 | 19
39043.5544 | 2496 | 2 | 19
39043.5549 | 2180 | 5 | 19
39043.5554 | 1972 | 80 | 19
39043.5559 | 2165 | 1 | 19
39043.5564 | 2404 | 1 | 19
39043.5569 | 2239 | 1 | 19
19
39043.5389 | 0 | 0 | 20
39043.5394 | 0 | 0 | 20
39043.5398 | 0 | 0 | 20
39043.5403 | 0 | 0 | 20
39043.5408 | 0 | 0 | 20
39043.5413 | 0 | 0 | 20
39043.5418 | 0 | 0 | 20
39043.5423 | 0 | 0 | 20
39043.5428 | 0 | 0 | 20
39043.5433 | 0 | 0 | 20
39043.5437 | 0 | 0 | 20
39043.5442 | 0 | 0 | 20
39043.5447 | 1082 | 1 | 20
39043.5452 | 1407 | 82 | 20
39043.5457 | 2064 | 249 | 20
39043.5462 | 2125 | 80 | 20
39043.5467 | 2022 | 29 | 20
39043.5471 | 2162 | 4 | 20
39043.5476 | 2230 | 1 | 20
39043.5481 | 2056 | 1 | 20
39043.5486 | 1970 | 1 | 20
39043.5491 | 2450 | 1 | 20
39043.5496 | 2546 | 1 | 20
39043.5501 | 2334 | 1 | 20
39043.5505 | 2071 | 1 | 20
39043.551 | 2590 | 1 | 20
39043.5515 | 2314 | 1 | 20
39043.552 | 2564 | 1 | 20
39043.5525 | 2032 | 2 | 20
39043.553 | 2048 | 2 | 20
39043.5535 | 2015 | 2 | 20
39043.5539 | 2379 | 1 | 20
39043.5544 | 2038 | 2 | 20
39043.5549 | 1988 | 7 | 20
39043.5554 | 2407 | 4 | 20
39043.5559 | 2026 | 1 | 20
39043.5564 | 2046 | 1 | 20
39043.5569 | 2238 | 0 | 20
20
39043.5389 | 0 | 0 | 21
39043.5394 | 0 | 0 | 21
39043.5399 | 0 | 0 | 21
39043.5404 | 0 | 0 | 21
39043.5408 | 0 | 0 | 21
39043.5413 | 0 | 0 | 21
39043.5418 | 0 | 0 | 21
39043.5423 | 0 | 0 | 21
39043.5428 | 0 | 0 | 21
39043.5433 | 0 | 0 | 21
39043.5438 | 0 | 0 | 21
39043.5442 | 0 | 0 | 21
39043.5447 | 972 | 1 | 21
39043.5452 | 1554 | 0 | 21
39043.5457 | 1768 | 0 | 21
39043.5462 | 1871 | 0 | 21
39043.5467 | 1893 | 0 | 21
39043.5472 | 2505 | 0 | 21
39043.5477 | 2195 | 0 | 21
39043.5481 | 2318 | 0 | 21
39043.5486 | 2103 | 1 | 21
39043.5491 | 2532 | 0 | 21
39043.5496 | 2304 | 0 | 21
39043.5501 | 2264 | 1 | 21
39043.5506 | 2024 | 0 | 21
39043.5511 | 2239 | 0 | 21
39043.5515 | 2183 | 0 | 21
39043.552 | 2086 | 1 | 21
39043.5525 | 2050 | 0 | 21
39043.553 | 2213 | 0 | 21
39043.5535 | 2319 | 1 | 21
39043.554 | 2082 | 0 | 21
39043.5545 | 2086 | 0 | 21
39043.5549 | 2459 | 0 | 21
39043.5554 | 2087 | 0 | 21
39043.5559 | 2375 | 0 | 21
39043.5564 | 2572 | 0 | 21
39043.5569 | 2573 | 0 | 21
21
39043.5389 | 0 | 0 | 22
39043.5394 | 0 | 0 | 22
39043.5399 | 0 | 0 | 22
39043.5404 | 0 | 0 | 22
39043.5409 | 0 | 0 | 22
39043.5413 | 0 | 0 | 22
39043.5418 | 0 | 0 | 22
39043.5423 | 0 | 0 | 22
39043.5428 | 0 | 0 | 22
39043.5433 | 0 | 0 | 22
39043.5438 | 0 | 0 | 22
39043.5443 | 0 | 0 | 22
39043.5447 | 0 | 0 | 22
39043.5452 | 29 | 0 | 22
39043.5457 | 1044 | 0 | 22
39043.5462 | 2136 | 0 | 22
39043.5467 | 2058 | 0 | 22
39043.5472 | 2299 | 0 | 22
39043.5477 | 2421 | 0 | 22
39043.5481 | 2045 | 0 | 22
39043.5486 | 2110 | 1 | 22
39043.5491 | 1994 | 0 | 22
39043.5496 | 2128 | 0 | 22
39043.5501 | 2576 | 1 | 22
39043.5506 | 2507 | 0 | 22
39043.5511 | 2344 | 0 | 22
39043.5516 | 2425 | 1 | 22
39043.552 | 2269 | 0 | 22
39043.5525 | 2218 | 1 | 22
39043.553 | 2510 | 1 | 22
39043.5535 | 1921 | 0 | 22
39043.554 | 2411 | 0 | 22
39043.5545 | 2273 | 0 | 22
39043.555 | 2162 | 0 | 22
39043.5554 | 1725 | 0 | 22
39043.5559 | 359 | 0 | 22
39043.5564 | 245 | 0 | 22
39043.5569 | 79 | 0 | 22
22
39043.5389 | 0 | 0 | 23
39043.5394 | 0 | 0 | 23
39043.5399 | 0 | 0 | 23
39043.5404 | 0 | 0 | 23
39043.5409 | 0 | 0 | 23
39043.5414 | 0 | 0 | 23
39043.5418 | 0 | 0 | 23
39043.5423 | 0 | 0 | 23
39043.5428 | 0 | 0 | 23
39043.5433 | 0 | 0 | 23
39043.5438 | 0 | 0 | 23
39043.5443 | 0 | 0 | 23
39043.5448 | 663 | 0 | 23
39043.5452 | 1460 | 0 | 23
39043.5457 | 1659 | 0 | 23
39043.5462 | 2027 | 0 | 23
39043.5467 | 2383 | 0 | 23
39043.5472 | 2334 | 0 | 23
39043.5477 | 2546 | 0 | 23
39043.5482 | 2556 | 0 | 23
39043.5486 | 2469 | 1 | 23
39043.5491 | 2004 | 0 | 23
39043.5496 | 1964 | 1 | 23
39043.5501 | 2078 | 1 | 23
39043.5511 | 2059 | 1 | 23
39043.5516 | 2007 | 1 | 23
39043.552 | 2376 | 0 | 23
39043.5525 | 2233 | 0 | 23
39043.553 | 2554 | 0 | 23
39043.5535 | 2156 | 1 | 23
39043.554 | 2204 | 1 | 23
39043.5545 | 1932 | 0 | 23
39043.555 | 1922 | 0 | 23
39043.5555 | 1988 | 0 | 23
39043.5559 | 2569 | 0 | 23
39043.5564 | 2001 | 0 | 23
39043.5569 | 2443 | 0 | 23
23
39043.5389 | 0 | 0 | 24
39043.5394 | 0 | 0 | 24
39043.5399 | 0 | 0 | 24
39043.5404 | 0 | 0 | 24
39043.5409 | 0 | 0 | 24
39043.5414 | 0 | 0 | 24
39043.5419 | 0 | 0 | 24
39043.5423 | 0 | 0 | 24
39043.5428 | 0 | 0 | 24
39043.5433 | 0 | 0 | 24
39043.5438 | 0 | 0 | 24
39043.5443 | 0 | 0 | 24
39043.5448 | 0 | 0 | 24
39043.5453 | 941 | 0 | 24
39043.5458 | 1771 | 0 | 24
39043.5462 | 1995 | 0 | 24
39043.5467 | 2225 | 0 | 24
39043.5472 | 2098 | 0 | 24
39043.5477 | 2081 | 0 | 24
39043.5482 | 2488 | 0 | 24
39043.5487 | 2507 | 1 | 24
39043.5492 | 2312 | 1 | 24
39043.5496 | 1952 | 0 | 24
39043.5501 | 2336 | 0 | 24
39043.5506 | 1985 | 0 | 24
39043.5511 | 2009 | 1 | 24
39043.5516 | 2013 | 0 | 24
39043.5521 | 2500 | 0 | 24
39043.5526 | 2536 | 0 | 24
39043.553 | 2365 | 0 | 24
39043.5535 | 2519 | 1 | 24
39043.554 | 2533 | 1 | 24
39043.5545 | 1933 | 0 | 24
39043.555 | 1867 | 0 | 24
39043.5555 | 1799 | 0 | 24
39043.556 | 714 | 0 | 24
39043.5564 | 1692 | 1 | 24
39043.5569 | 474 | 0 | 24
24
39043.539 | 0 | 0 | 25
39043.5394 | 0 | 0 | 25
39043.5399 | 0 | 0 | 25
39043.5404 | 0 | 0 | 25
39043.5409 | 0 | 0 | 25
39043.5414 | 0 | 0 | 25
39043.5419 | 0 | 0 | 25
39043.5424 | 0 | 0 | 25
39043.5428 | 0 | 0 | 25
39043.5433 | 0 | 0 | 25
39043.5438 | 0 | 0 | 25
39043.5443 | 0 | 0 | 25
39043.5448 | 791 | 1 | 25
39043.5453 | 1959 | 0 | 25
39043.5458 | 2053 | 0 | 25
39043.5462 | 2253 | 0 | 25
39043.5467 | 2130 | 0 | 25
39043.5472 | 2406 | 0 | 25
39043.5477 | 2547 | 0 | 25
39043.5482 | 2337 | 0 | 25
39043.5487 | 2577 | 1 | 25
39043.5492 | 2476 | 1 | 25
39043.5497 | 2221 | 0 | 25
39043.5501 | 2048 | 0 | 25
39043.5506 | 2328 | 0 | 25
39043.5511 | 2160 | 0 | 25
39043.5516 | 2009 | 0 | 25
39043.5521 | 2159 | 0 | 25
39043.5526 | 2360 | 0 | 25
39043.5531 | 2379 | 0 | 25
39043.5535 | 1956 | 0 | 25
39043.554 | 2054 | 0 | 25
39043.5545 | 2467 | 0 | 25
39043.555 | 2221 | 0 | 25
39043.5555 | 2548 | 0 | 25
39043.556 | 2390 | 0 | 25
39043.5565 | 2541 | 0 | 25
39043.5569 | 2235 | 0 | 25
25
39043.539 | 0 | 0 | 26
39043.5395 | 0 | 0 | 26
39043.54 | 0 | 0 | 26
39043.5404 | 0 | 0 | 26
39043.5409 | 0 | 0 | 26
39043.5414 | 0 | 0 | 26
39043.5419 | 0 | 0 | 26
39043.5424 | 0 | 0 | 26
39043.5429 | 0 | 0 | 26
39043.5434 | 0 | 0 | 26
39043.5438 | 0 | 0 | 26
39043.5443 | 0 | 0 | 26
39043.5448 | 0 | 0 | 26
39043.5453 | 129 | 0 | 26
39043.5458 | 1965 | 0 | 26
39043.5463 | 2406 | 0 | 26
39043.5468 | 2485 | 0 | 26
39043.5472 | 1929 | 0 | 26
39043.5477 | 2253 | 0 | 26
39043.5482 | 2476 | 0 | 26
39043.5487 | 2561 | 0 | 26
39043.5492 | 2034 | 0 | 26
39043.5497 | 2058 | 1 | 26
39043.5502 | 2490 | 0 | 26
39043.5506 | 2569 | 0 | 26
39043.5511 | 2521 | 0 | 26
39043.5516 | 2062 | 1 | 26
39043.5521 | 1969 | 0 | 26
39043.5526 | 1944 | 0 | 26
39043.5531 | 2182 | 1 | 26
39043.5536 | 1918 | 0 | 26
39043.554 | 2438 | 0 | 26
39043.5545 | 2245 | 0 | 26
39043.555 | 2393 | 0 | 26
39043.5555 | 1471 | 0 | 26
39043.556 | 906 | 0 | 26
39043.5565 | 350 | 0 | 26
39043.557 | 40 | 0 | 26
26
39043.539 | 0 | 0 | 27
39043.5395 | 0 | 0 | 27
39043.54 | 0 | 0 | 27
39043.5405 | 0 | 0 | 27
39043.5409 | 0 | 0 | 27
39043.5414 | 0 | 0 | 27
39043.5419 | 0 | 0 | 27
39043.5424 | 0 | 0 | 27
39043.5429 | 0 | 0 | 27
39043.5434 | 0 | 0 | 27
39043.5439 | 0 | 0 | 27
39043.5443 | 0 | 0 | 27
39043.5448 | 819 | 0 | 27
39043.5453 | 1475 | 0 | 27
39043.5458 | 1685 | 0 | 27
39043.5463 | 1920 | 0 | 27
39043.5468 | 1995 | 0 | 27
39043.5473 | 1989 | 0 | 27
39043.5477 | 2005 | 0 | 27
39043.5482 | 2105 | 0 | 27
39043.5487 | 2285 | 0 | 27
39043.5492 | 1969 | 1 | 27
39043.5497 | 2463 | 0 | 27
39043.5502 | 2228 | 0 | 27
39043.5507 | 2490 | 1 | 27
39043.5511 | 1982 | 0 | 27
39043.5516 | 2551 | 0 | 27
39043.5521 | 2378 | 1 | 27
39043.5526 | 2274 | 0 | 27
39043.5531 | 1955 | 1 | 27
39043.5536 | 2262 | 0 | 27
39043.5541 | 1991 | 0 | 27
39043.5545 | 2459 | 0 | 27
39043.555 | 1917 | 0 | 27
39043.5555 | 2016 | 0 | 27
39043.556 | 2245 | 0 | 27
39043.5565 | 2238 | 0 | 27
39043.557 | 2579 | 0 | 27
27
39043.539 | 0 | 0 | 28
39043.5395 | 0 | 0 | 28
39043.54 | 0 | 0 | 28
39043.5405 | 0 | 0 | 28
39043.541 | 0 | 0 | 28
39043.5414 | 0 | 0 | 28
39043.5419 | 0 | 0 | 28
39043.5424 | 0 | 0 | 28
39043.5429 | 0 | 0 | 28
39043.5434 | 0 | 0 | 28
39043.5439 | 0 | 0 | 28
39043.5444 | 0 | 0 | 28
39043.5448 | 0 | 0 | 28
39043.5453 | 1505 | 0 | 28
39043.5458 | 1627 | 0 | 28
39043.5463 | 2013 | 0 | 28
39043.5468 | 1964 | 0 | 28
39043.5473 | 2259 | 0 | 28
39043.5478 | 2493 | 0 | 28
39043.5482 | 2009 | 0 | 28
39043.5487 | 1980 | 1 | 28
39043.5492 | 2464 | 0 | 28
39043.5497 | 2020 | 1 | 28
39043.5502 | 2497 | 0 | 28
39043.5507 | 2513 | 0 | 28
39043.5512 | 2363 | 0 | 28
39043.5516 | 2112 | 0 | 28
39043.5521 | 1954 | 0 | 28
39043.5526 | 2396 | 0 | 28
39043.5531 | 2375 | 0 | 28
39043.5536 | 2144 | 1 | 28
39043.5541 | 2507 | 0 | 28
39043.5546 | 1972 | 0 | 28
39043.555 | 2129 | 0 | 28
39043.5555 | 1415 | 0 | 28
39043.556 | 860 | 0 | 28
39043.5565 | 1698 | 3 | 28
39043.557 | 1884 | 0 | 28
28
39043.539 | 0 | 0 | 29
39043.5395 | 0 | 0 | 29
39043.54 | 0 | 0 | 29
39043.5405 | 0 | 0 | 29
39043.541 | 0 | 0 | 29
39043.5415 | 0 | 0 | 29
39043.5419 | 0 | 0 | 29
39043.5424 | 0 | 0 | 29
39043.5429 | 0 | 0 | 29
39043.5434 | 0 | 0 | 29
39043.5439 | 0 | 0 | 29
39043.5444 | 0 | 0 | 29
39043.5449 | 0 | 0 | 29
39043.5453 | 626 | 0 | 29
39043.5458 | 1530 | 0 | 29
39043.5463 | 2172 | 19 | 29
39043.5468 | 1997 | 7 | 29
39043.5473 | 1934 | 2 | 29
39043.5478 | 2087 | 1 | 29
39043.5483 | 2338 | 2 | 29
39043.5488 | 2124 | 1 | 29
39043.5492 | 2342 | 1 | 29
39043.5497 | 2239 | 1 | 29
39043.5502 | 2376 | 0 | 29
39043.5507 | 2218 | 0 | 29
39043.5512 | 2246 | 1 | 29
39043.5517 | 2158 | 1 | 29
39043.5522 | 2521 | 1 | 29
39043.5526 | 2339 | 1 | 29
39043.5531 | 2004 | 1 | 29
39043.5536 | 2514 | 1 | 29
39043.5541 | 2234 | 1 | 29
39043.5546 | 2411 | 0 | 29
39043.5551 | 2328 | 0 | 29
39043.5556 | 1155 | 306 | 29
39043.556 | 605 | 478 | 29
39043.5565 | 428 | 609 | 29
39043.557 | 874 | 0 | 29
29
39043.539 | 0 | 0 | 30
39043.5395 | 0 | 0 | 30
39043.54 | 0 | 0 | 30
39043.5405 | 0 | 0 | 30
39043.541 | 0 | 0 | 30
39043.5415 | 0 | 0 | 30
39043.542 | 0 | 0 | 30
39043.5424 | 0 | 0 | 30
39043.5429 | 0 | 0 | 30
39043.5434 | 0 | 0 | 30
39043.5439 | 0 | 0 | 30
39043.5444 | 0 | 0 | 30
39043.5449 | 0 | 0 | 30
39043.5454 | 1698 | 0 | 30
39043.5458 | 2107 | 13 | 30
39043.5463 | 2138 | 15 | 30
39043.5468 | 1935 | 8 | 30
39043.5473 | 2098 | 1 | 30
39043.5478 | 1996 | 1 | 30
39043.5483 | 2190 | 2 | 30
39043.5488 | 2573 | 1 | 30
39043.5492 | 2393 | 1 | 30
39043.5497 | 2333 | 1 | 30
39043.5502 | 2103 | 0 | 30
39043.5507 | 1958 | 0 | 30
39043.5512 | 2026 | 1 | 30
39043.5517 | 2273 | 1 | 30
39043.5522 | 1938 | 1 | 30
39043.5527 | 2362 | 1 | 30
39043.5531 | 2335 | 0 | 30
39043.5536 | 2270 | 1 | 30
39043.5541 | 2417 | 1 | 30
39043.5546 | 2014 | 1 | 30
39043.5551 | 1704 | 1 | 30
39043.5556 | 1979 | 1 | 30
39043.5561 | 911 | 305 | 30
39043.5565 | 908 | 1027 | 30
39043.557 | 1875 | 0 | 30
30

## Temperatures
DAQ Time | Burner Time | Bundle center | Air above bundle | Air below bundle | Intra-bundle | TRAY C
0 | -190 | 16.3 | 16.7 | 17.3 | 16.2 | 18.7
1 | -189 | 16.2 | 16.7 | 17.2 | 16.2 | 18.7
2 | -188 | 16.3 | 16.7 | 17.2 | 16.2 | 18.7
3 | -187 | 16.3 | 16.7 | 17.3 | 16.2 | 18.7
4 | -186 | 16.3 | 16.7 | 17.2 | 16.2 | 18.7
5 | -185 | 16.3 | 16.7 | 17.2 | 16.3 | 18.7
6 | -184 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7
7 | -183 | 16.3 | 16.7 | 17.3 | 16.2 | 18.7
8 | -182 | 16.3 | 16.7 | 17.2 | 16.2 | 18.7
9 | -181 | 16.3 | 16.7 | 17.2 | 16.3 | 18.7
10 | -180 | 16.3 | 16.7 | 17.3 | 16.2 | 18.7
11 | -179 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7
12 | -178 | 16.3 | 16.7 | 17.2 | 16.2 | 18.7
13 | -177 | 16.3 | 16.7 | 17.2 | 16.2 | 18.7
14 | -176 | 16.3 | 16.7 | 17.2 | 16.2 | 18.7
15 | -175 | 16.3 | 16.7 | 17.2 | 16.3 | 18.7
16 | -174 | 16.3 | 16.7 | 17.2 | 16.2 | 18.7
17 | -173 | 16.3 | 16.7 | 17.2 | 16.2 | 18.7
18 | -172 | 16.3 | 16.7 | 17.2 | 16.2 | 18.7
19 | -171 | 16.3 | 16.7 | 17.2 | 16.2 | 18.7
20 | -170 | 16.3 | 16.7 | 17.2 | 16.2 | 18.7
21 | -169 | 16.3 | 16.7 | 17.2 | 16.2 | 18.7
22 | -168 | 16.3 | 16.7 | 17.2 | 16.2 | 18.7
23 | -167 | 16.3 | 16.7 | 17.2 | 16.2 | 18.7
24 | -166 | 16.3 | 16.7 | 17.2 | 16.2 | 18.7
25 | -165 | 16.3 | 16.7 | 17.2 | 16.2 | 18.7
26 | -164 | 16.3 | 16.7 | 17.2 | 16.2 | 18.7
27 | -163 | 16.3 | 16.7 | 17.2 | 16.2 | 18.7
28 | -162 | 16.3 | 16.7 | 17.2 | 16.2 | 18.7
29 | -161 | 16.3 | 16.7 | 17.2 | 16.2 | 18.7
30 | -160 | 16.2 | 16.7 | 17.2 | 16.2 | 18.7
31 | -159 | 16.3 | 16.7 | 17.2 | 16.2 | 18.7
32 | -158 | 16.3 | 16.7 | 17.2 | 16.2 | 18.7
33 | -157 | 16.3 | 16.7 | 17.2 | 16.3 | 18.7
34 | -156 | 16.3 | 16.7 | 17.2 | 16.2 | 18.7
35 | -155 | 16.3 | 16.7 | 17.2 | 16.2 | 18.7
36 | -154 | 16.3 | 16.7 | 17.2 | 16.2 | 18.7
37 | -153 | 16.2 | 16.7 | 17.2 | 16.3 | 18.7
38 | -152 | 16.2 | 16.7 | 17.2 | 16.2 | 18.7
39 | -151 | 16.3 | 16.7 | 17.2 | 16.2 | 18.7
40 | -150 | 16.3 | 16.7 | 17.2 | 16.2 | 18.7
41 | -149 | 16.3 | 16.7 | 17.2 | 16.2 | 18.7
42 | -148 | 16.3 | 16.7 | 17.2 | 16.2 | 18.7
43 | -147 | 16.3 | 16.7 | 17.2 | 16.2 | 18.7
44 | -146 | 16.3 | 16.7 | 17.2 | 16.2 | 18.7
45 | -145 | 16.3 | 16.7 | 17.2 | 16.3 | 18.7
46 | -144 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7
47 | -143 | 16.3 | 16.7 | 17.2 | 16.2 | 18.7
48 | -142 | 16.3 | 16.7 | 17.3 | 16.2 | 18.7
49 | -141 | 16.3 | 16.7 | 17.3 | 16.2 | 18.7
50 | -140 | 16.3 | 16.7 | 17.3 | 16.2 | 18.7
51 | -139 | 16.3 | 16.7 | 17.3 | 16.2 | 18.7
52 | -138 | 16.3 | 16.7 | 17.3 | 16.2 | 18.7
53 | -137 | 16.3 | 16.7 | 17.3 | 16.2 | 18.7
54 | -136 | 16.3 | 16.7 | 17.3 | 16.2 | 18.7
55 | -135 | 16.3 | 16.7 | 17.3 | 16.2 | 18.7
56 | -134 | 16.3 | 16.7 | 17.3 | 16.2 | 18.7
57 | -133 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7
58 | -132 | 16.3 | 16.7 | 17.3 | 16.2 | 18.7
59 | -131 | 16.3 | 16.7 | 17.3 | 16.2 | 18.7
60 | -130 | 16.3 | 16.7 | 17.3 | 16.2 | 18.7
61 | -129 | 16.3 | 16.7 | 17.3 | 16.2 | 18.7
62 | -128 | 16.3 | 16.7 | 17.3 | 16.2 | 18.7
63 | -127 | 16.3 | 16.7 | 17.3 | 16.2 | 18.7
64 | -126 | 16.3 | 16.7 | 17.3 | 16.2 | 18.7
65 | -125 | 16.3 | 16.7 | 17.3 | 16.2 | 18.7
66 | -124 | 16.3 | 16.7 | 17.3 | 16.2 | 18.7
67 | -123 | 16.3 | 16.7 | 17.3 | 16.2 | 18.7
68 | -122 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7
69 | -121 | 16.3 | 16.7 | 17.3 | 16.2 | 18.7
70 | -120 | 16.3 | 16.7 | 17.3 | 16.2 | 18.7
71 | -119 | 16.3 | 16.7 | 17.3 | 16.2 | 18.7
72 | -118 | 16.3 | 16.7 | 17.3 | 16.2 | 18.7
73 | -117 | 16.3 | 16.7 | 17.3 | 16.2 | 18.7
74 | -116 | 16.3 | 16.7 | 17.3 | 16.2 | 18.7
75 | -115 | 16.3 | 16.7 | 17.3 | 16.2 | 18.7
76 | -114 | 16.3 | 16.7 | 17.3 | 16.2 | 18.7
77 | -113 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7
78 | -112 | 16.3 | 16.7 | 17.3 | 16.2 | 18.7
79 | -111 | 16.3 | 16.7 | 17.3 | 16.2 | 18.7
80 | -110 | 16.3 | 16.7 | 17.3 | 16.2 | 18.7
81 | -109 | 16.3 | 16.7 | 17.3 | 16.2 | 18.7
82 | -108 | 16.3 | 16.7 | 17.3 | 16.2 | 18.7
83 | -107 | 16.3 | 16.7 | 17.3 | 16.2 | 18.7
84 | -106 | 16.3 | 16.7 | 17.3 | 16.2 | 18.7
85 | -105 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7
86 | -104 | 16.3 | 16.7 | 17.3 | 16.2 | 18.7
87 | -103 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7
88 | -102 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7
89 | -101 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7
90 | -100 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7
91 | -99 | 16.3 | 16.7 | 17.3 | 16.2 | 18.7
92 | -98 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7
93 | -97 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7
94 | -96 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7
95 | -95 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7
96 | -94 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7
97 | -93 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7
98 | -92 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7
99 | -91 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7
100 | -90 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7
101 | -89 | 16.3 | 16.7 | 17.3 | 16.2 | 18.7
102 | -88 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7
103 | -87 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7
104 | -86 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7
105 | -85 | 16.3 | 16.7 | 17.2 | 16.3 | 18.7
106 | -84 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7
107 | -83 | 16.3 | 16.7 | 17.2 | 16.3 | 18.7
108 | -82 | 16.3 | 16.7 | 17.2 | 16.3 | 18.7
109 | -81 | 16.3 | 16.7 | 17.2 | 16.3 | 18.7
110 | -80 | 16.3 | 16.7 | 17.2 | 16.3 | 18.7
111 | -79 | 16.3 | 16.7 | 17.2 | 16.3 | 18.7
112 | -78 | 16.3 | 16.7 | 17.2 | 16.3 | 18.7
113 | -77 | 16.3 | 16.7 | 17.2 | 16.3 | 18.7
114 | -76 | 16.3 | 16.7 | 17.2 | 16.3 | 18.7
115 | -75 | 16.3 | 16.7 | 17.2 | 16.3 | 18.7
116 | -74 | 16.3 | 16.7 | 17.2 | 16.3 | 18.7
117 | -73 | 16.3 | 16.7 | 17.2 | 16.3 | 18.7
118 | -72 | 16.3 | 16.7 | 17.2 | 16.3 | 18.7
119 | -71 | 16.3 | 16.7 | 17.2 | 16.3 | 18.7
120 | -70 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7
121 | -69 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7
122 | -68 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7
123 | -67 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7
124 | -66 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7
125 | -65 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7
126 | -64 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7
127 | -63 | 16.3 | 16.7 | 17.2 | 16.3 | 18.7
128 | -62 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7
129 | -61 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7
130 | -60 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7
131 | -59 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7
132 | -58 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7
133 | -57 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7
134 | -56 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7
135 | -55 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7
136 | -54 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7
137 | -53 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7
138 | -52 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7
139 | -51 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7
140 | -50 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7
141 | -49 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7
142 | -48 | 16.3 | 16.8 | 17.3 | 16.3 | 18.7
143 | -47 | 16.3 | 16.8 | 17.3 | 16.3 | 18.7
144 | -46 | 16.3 | 16.8 | 17.3 | 16.3 | 18.7
145 | -45 | 16.3 | 16.8 | 17.3 | 16.3 | 18.7
146 | -44 | 16.3 | 16.8 | 17.3 | 16.3 | 18.7
147 | -43 | 16.3 | 16.8 | 17.3 | 16.3 | 18.7
148 | -42 | 16.3 | 16.8 | 17.3 | 16.3 | 18.7
149 | -41 | 16.3 | 16.8 | 17.4 | 16.3 | 18.7
150 | -40 | 16.3 | 16.8 | 17.3 | 16.3 | 18.7
151 | -39 | 16.3 | 16.8 | 17.4 | 16.3 | 18.7
152 | -38 | 16.3 | 16.8 | 17.4 | 16.3 | 18.7
153 | -37 | 16.3 | 16.8 | 17.3 | 16.3 | 18.7
154 | -36 | 16.3 | 16.8 | 17.4 | 16.3 | 18.7
155 | -35 | 16.3 | 16.8 | 17.3 | 16.3 | 18.7
156 | -34 | 16.3 | 16.8 | 17.4 | 16.3 | 18.7
157 | -33 | 16.3 | 16.8 | 17.4 | 16.3 | 18.7
158 | -32 | 16.3 | 16.8 | 17.4 | 16.3 | 18.7
159 | -31 | 16.3 | 16.8 | 17.4 | 16.3 | 18.7
160 | -30 | 16.3 | 16.8 | 17.4 | 16.3 | 18.7
161 | -29 | 16.3 | 16.8 | 17.4 | 16.3 | 18.7
162 | -28 | 16.3 | 16.8 | 17.4 | 16.3 | 18.7
163 | -27 | 16.3 | 16.8 | 17.4 | 16.3 | 18.7
164 | -26 | 16.3 | 16.8 | 17.4 | 16.3 | 18.7
165 | -25 | 16.3 | 16.8 | 17.4 | 16.3 | 18.7
166 | -24 | 16.3 | 16.8 | 17.4 | 16.3 | 18.7
167 | -23 | 16.3 | 16.8 | 17.4 | 16.3 | 18.7
168 | -22 | 16.3 | 16.8 | 17.4 | 16.3 | 18.7
169 | -21 | 16.3 | 16.8 | 17.4 | 16.3 | 18.7
170 | -20 | 16.3 | 16.8 | 17.4 | 16.3 | 18.7
171 | -19 | 16.3 | 16.8 | 17.4 | 16.3 | 18.7
172 | -18 | 16.3 | 16.8 | 17.4 | 16.3 | 18.7
173 | -17 | 16.3 | 16.8 | 17.4 | 16.3 | 18.7
174 | -16 | 16.3 | 16.8 | 17.4 | 16.3 | 18.7
175 | -15 | 16.3 | 16.8 | 17.4 | 16.3 | 18.7
176 | -14 | 16.3 | 16.8 | 17.3 | 16.3 | 18.7
177 | -13 | 16.3 | 16.8 | 17.4 | 16.3 | 18.7
178 | -12 | 16.3 | 16.8 | 17.4 | 16.3 | 18.7
179 | -11 | 16.3 | 16.8 | 17.4 | 16.3 | 18.7
180 | -10 | 16.3 | 16.8 | 17.3 | 16.3 | 18.7
181 | -9 | 16.3 | 16.8 | 17.3 | 16.3 | 18.7
182 | -8 | 16.3 | 16.8 | 17.3 | 16.3 | 18.7
183 | -7 | 16.3 | 16.8 | 17.3 | 16.3 | 18.7
184 | -6 | 16.3 | 16.8 | 17.3 | 16.3 | 18.7
185 | -5 | 16.3 | 16.8 | 17.3 | 16.3 | 18.7
186 | -4 | 16.3 | 16.8 | 17.3 | 16.3 | 18.7
187 | -3 | 16.3 | 16.8 | 17.3 | 16.3 | 18.7
188 | -2 | 16.3 | 16.8 | 17.3 | 16.3 | 18.7
189 | -1 | 16.3 | 16.8 | 17.3 | 16.3 | 18.7
190 | 0 | 16.3 | 16.8 | 17.3 | 16.3 | 18.7
191 | 1 | 16.3 | 16.8 | 17.3 | 16.3 | 18.7
192 | 2 | 16.3 | 16.8 | 17.3 | 16.3 | 18.7
193 | 3 | 16.3 | 16.8 | 17.3 | 16.3 | 18.7
194 | 4 | 16.3 | 16.8 | 17.7 | 16.3 | 18.8
195 | 5 | 16.3 | 22.8 | 36 | 16.3 | 21
196 | 6 | 16.3 | 38.8 | 72.3 | 16.3 | 27.8
197 | 7 | 16.4 | 67.2 | 120.5 | 16.4 | 37.9
198 | 8 | 16.5 | 106.6 | 177.1 | 16.6 | 51
199 | 9 | 16.7 | 143.5 | 224.8 | 16.9 | 66.8
200 | 10 | 17.1 | 200 | 297.3 | 17.4 | 86.7
201 | 11 | 17.6 | 263.9 | 366.5 | 18.3 | 110.6
202 | 12 | 18.2 | 318.5 | 429.8 | 19.1 | 136.8
203 | 13 | 19 | 361 | 477.1 | 20.2 | 163.3
204 | 14 | 19.9 | 399 | 511.9 | 21.6 | 189.5
205 | 15 | 20.9 | 435.3 | 556.2 | 23.5 | 211.1
206 | 16 | 21.9 | 476.9 | 595.5 | 25.9 | 229.4
207 | 17 | 22.9 | 512.1 | 622.7 | 28.4 | 249.9
208 | 18 | 23.9 | 554.6 | 651.3 | 31.6 | 274.4
209 | 19 | 24.9 | 587.8 | 670 | 35 | 299.4
210 | 20 | 25.9 | 616 | 694.7 | 38.4 | 321.9
211 | 21 | 27 | 633.4 | 708.5 | 41.6 | 345.3
212 | 22 | 28.1 | 650.8 | 729.3 | 44.8 | 365.1
213 | 23 | 29.3 | 660.8 | 740.8 | 47.8 | 383.3
214 | 24 | 30.5 | 672.3 | 741.6 | 50.8 | 399.6
215 | 25 | 31.8 | 680.2 | 742.1 | 53.5 | 413.9
216 | 26 | 33.3 | 691 | 752.5 | 56.4 | 429.2
217 | 27 | 34.9 | 692.3 | 744.4 | 59 | 444.9
218 | 28 | 36.5 | 691.7 | 746.9 | 61.6 | 456.7
219 | 29 | 38.2 | 683.5 | 739.9 | 63.8 | 469.5
220 | 30 | 40 | 677.5 | 738.9 | 66 | 478.6
221 | 31 | 41.9 | 670.4 | 743.9 | 68 | 487.6
222 | 32 | 44 | 664.8 | 753.3 | 69.8 | 493.8
223 | 33 | 46.2 | 661.5 | 766.3 | 71.5 | 498.4
224 | 34 | 48.5 | 647.8 | 755.4 | 72.8 | 499.1
225 | 35 | 51.1 | 635.6 | 736.9 | 74.3 | 503.1
226 | 36 | 53.8 | 625 | 730 | 75.9 | 509.8
227 | 37 | 56.7 | 610.7 | 716.2 | 77.2 | 512
228 | 38 | 59.8 | 595.6 | 697.2 | 78.2 | 513.9
229 | 39 | 63.1 | 591.1 | 703.4 | 79.5 | 518.7
230 | 40 | 66.4 | 581.2 | 695.2 | 80.5 | 517
231 | 41 | 70 | 573.7 | 690.1 | 81.7 | 519.7
232 | 42 | 73.6 | 561.9 | 681.2 | 82.6 | 523.2
233 | 43 | 77.5 | 557.7 | 688.8 | 83.8 | 525.5
234 | 44 | 81.4 | 549.2 | 672.9 | 84.9 | 529.5
235 | 45 | 85.5 | 547.6 | 667 | 86.2 | 538.8
236 | 46 | 89.7 | 552.8 | 673.2 | 87.7 | 548.1
237 | 47 | 93.8 | 550 | 669.3 | 88.9 | 555.4
238 | 48 | 97.9 | 549.1 | 663.6 | 90.1 | 561.6
239 | 49 | 101.9 | 543.3 | 653.6 | 91.1 | 565.8
240 | 50 | 105.9 | 542.6 | 653.5 | 92.3 | 570.4
241 | 51 | 109.7 | 533.4 | 639.3 | 93 | 572.3
242 | 52 | 113.4 | 525.5 | 630.6 | 93.7 | 573.6
243 | 53 | 116.9 | 517.5 | 621.9 | 94.2 | 574.7
244 | 54 | 120.3 | 516.6 | 636.5 | 94.9 | 578.2
245 | 55 | 123.4 | 519.6 | 643.5 | 96.1 | 585.3
246 | 56 | 126.4 | 519.5 | 631.4 | 97.3 | 591.9
247 | 57 | 129.2 | 518.6 | 618 | 98.3 | 598.8
248 | 58 | 131.8 | 515.4 | 619.1 | 99.1 | 602.2
249 | 59 | 134.3 | 523.7 | 638.9 | 100.4 | 604.6
250 | 60 | 136.6 | 529.5 | 650.8 | 101.6 | 610.1
251 | 61 | 139 | 531.2 | 655.7 | 102.5 | 613.8
252 | 62 | 141.2 | 530.6 | 659.1 | 103.5 | 615.7
253 | 63 | 143.4 | 530.3 | 662.7 | 104.4 | 616.6
254 | 64 | 145.4 | 529.7 | 663.2 | 105.3 | 617.9
255 | 65 | 147.4 | 536.5 | 671.2 | 106.4 | 622
256 | 66 | 149.3 | 536.1 | 669.6 | 107.5 | 627.7
257 | 67 | 151.2 | 543.1 | 688.4 | 108.9 | 633.2
258 | 68 | 153.1 | 552.3 | 706.1 | 110.4 | 638.2
259 | 69 | 155 | 559.2 | 711.7 | 112 | 642
260 | 70 | 157 | 566 | 725.4 | 113.5 | 645.2
261 | 71 | 159 | 569.4 | 734.9 | 115 | 646.2
262 | 72 | 161 | 573.6 | 740 | 116.9 | 646.3
263 | 73 | 163.1 | 578.5 | 740.8 | 118.3 | 648.5
264 | 74 | 165.2 | 580.7 | 738.6 | 119.9 | 651.7
265 | 75 | 167.2 | 580.6 | 740.8 | 121.3 | 651.7
266 | 76 | 169.3 | 583.2 | 746.9 | 122.8 | 653.8
267 | 77 | 171.4 | 588.7 | 752.3 | 124.3 | 655.4
268 | 78 | 173.4 | 584.6 | 745.6 | 125.2 | 654.7
269 | 79 | 175.4 | 580.8 | 743.1 | 126.2 | 655.4
270 | 80 | 177.3 | 582.3 | 743.1 | 127.5 | 657.5
271 | 81 | 179 | 582.7 | 750.2 | 128.9 | 659.1
272 | 82 | 180.9 | 582.3 | 750.9 | 130.3 | 661.5
273 | 83 | 182.8 | 581.5 | 751.2 | 131.7 | 663.7
274 | 84 | 184.7 | 582 | 758.4 | 133.1 | 662.4
275 | 85 | 186.5 | 583.7 | 760.3 | 134.2 | 660.7
276 | 86 | 188.5 | 586.1 | 758.9 | 135.6 | 661.6
277 | 87 | 190.8 | 593.7 | 765.3 | 137.1 | 665.3
278 | 88 | 193.3 | 596 | 766.2 | 138.6 | 668.2
279 | 89 | 196 | 600.9 | 771.5 | 140 | 668.6
280 | 90 | 198.9 | 594.1 | 762.4 | 141 | 666
281 | 91 | 201.5 | 591.7 | 758.3 | 142.1 | 664.6
282 | 92 | 204.3 | 584.6 | 751 | 143 | 664
283 | 93 | 207.4 | 580.9 | 741.6 | 144.2 | 664.6
284 | 94 | 210.6 | 577.1 | 718.6 | 145.2 | 667.6
285 | 95 | 213.5 | 576.3 | 712.7 | 146.6 | 671.5
286 | 96 | 215.8 | 571.9 | 695.4 | 147.5 | 673.8
287 | 97 | 217.5 | 572.5 | 681.1 | 148.7 | 676.4
288 | 98 | 219 | 576 | 678.2 | 150.1 | 680.6
289 | 99 | 220.3 | 578.4 | 674.4 | 151.2 | 684.1
290 | 100 | 221.6 | 583.6 | 661.1 | 152.5 | 689.9
291 | 101 | 222.9 | 586.8 | 662 | 153.7 | 694.3
292 | 102 | 224.3 | 592 | 680.4 | 154.9 | 698
293 | 103 | 226 | 590.9 | 677 | 155.7 | 699.7
294 | 104 | 228 | 596.4 | 678.1 | 156.5 | 702
295 | 105 | 229.8 | 598.6 | 681.5 | 157.2 | 703.9
296 | 106 | 231.7 | 605.4 | 707.4 | 158.2 | 706.9
297 | 107 | 233.6 | 609 | 707.2 | 159.1 | 709.9
298 | 108 | 235.3 | 614.7 | 703.6 | 160.1 | 712.1
299 | 109 | 237.2 | 616.9 | 700.1 | 161 | 713.2
300 | 110 | 239.1 | 611.7 | 691.7 | 161.5 | 712.3
301 | 111 | 240.4 | 596.8 | 673.2 | 161.1 | 709.6
302 | 112 | 241.5 | 592.2 | 658.9 | 161.2 | 709.5
303 | 113 | 242.1 | 597.3 | 665.4 | 162 | 712.2
304 | 114 | 242.6 | 601.8 | 677 | 162.9 | 714.4
305 | 115 | 243 | 606.3 | 673.8 | 164 | 715.9
306 | 116 | 243.2 | 602.9 | 674.6 | 164.5 | 714.7
307 | 117 | 243.2 | 604 | 695.7 | 165.4 | 716.3
308 | 118 | 242.9 | 602.2 | 699.1 | 166.5 | 714.5
309 | 119 | 242.8 | 603.4 | 692.9 | 167.4 | 714.2
310 | 120 | 243.3 | 603.1 | 682.5 | 168 | 715.5
311 | 121 | 244.3 | 594.6 | 668.1 | 168.2 | 712.9
312 | 122 | 245.4 | 589.6 | 657.5 | 168.3 | 710.6
313 | 123 | 246.8 | 588.5 | 640 | 168.5 | 710.3
314 | 124 | 248.1 | 589.8 | 633.1 | 169.1 | 712.1
315 | 125 | 249.4 | 585.8 | 629.5 | 169.5 | 711.7
316 | 126 | 250.8 | 587.3 | 638.9 | 170 | 713.3
317 | 127 | 252.3 | 594.1 | 665.5 | 171.2 | 714.9
318 | 128 | 253.9 | 606 | 686.5 | 172.5 | 715.4
319 | 129 | 255.8 | 617.3 | 714.9 | 174.1 | 717.7
320 | 130 | 258.4 | 621.7 | 724.8 | 175.4 | 717.6
321 | 131 | 260.7 | 617.1 | 716.7 | 175.9 | 715
322 | 132 | 262.6 | 615.1 | 717.1 | 176.7 | 713.6
323 | 133 | 264.7 | 615 | 714.5 | 177.4 | 712.1
324 | 134 | 267.3 | 609.7 | 706.1 | 177.8 | 710
325 | 135 | 269.5 | 607.9 | 710.6 | 178.3 | 709.5
326 | 136 | 270.2 | 607.6 | 719.4 | 178.9 | 708.7
327 | 137 | 271.4 | 609.9 | 731 | 179.9 | 709.7
328 | 138 | 273.7 | 608.1 | 738.2 | 180.3 | 707.7
329 | 139 | 278 | 606.9 | 735.8 | 180.6 | 703.9
330 | 140 | 281.3 | 603.4 | 735.8 | 180.8 | 701.4
331 | 141 | 284.4 | 601.7 | 733.7 | 181.2 | 703
332 | 142 | 287.9 | 603 | 744 | 181.8 | 702.5
333 | 143 | 290.6 | 599.2 | 738.1 | 182.3 | 699.8
334 | 144 | 292 | 599.1 | 749.8 | 182.9 | 698.6
335 | 145 | 293.9 | 598.6 | 731 | 183.6 | 700.3
336 | 146 | 295.9 | 598.9 | 729.5 | 184.1 | 700.5
337 | 147 | 297.9 | 597.7 | 727.2 | 184.4 | 699.7
338 | 148 | 300 | 600 | 717.2 | 185.1 | 701.4
339 | 149 | 302.2 | 602.9 | 709.3 | 186.3 | 703.9
340 | 150 | 304.2 | 603.4 | 701.4 | 187.1 | 704.8
341 | 151 | 306.4 | 602 | 701.6 | 187.8 | 706.8
342 | 152 | 308.8 | 607.8 | 697.1 | 188.7 | 709.5
343 | 153 | 311.4 | 607.7 | 695.4 | 189.3 | 709.5
344 | 154 | 313.8 | 608.8 | 698.3 | 189.8 | 709.8
345 | 155 | 316.4 | 618 | 709.5 | 191.1 | 712.5
346 | 156 | 318.9 | 622.5 | 710.4 | 192.4 | 713.6
347 | 157 | 321.5 | 625.2 | 713 | 193.4 | 714.7
348 | 158 | 323.9 | 624.8 | 706.4 | 194.6 | 716.2
349 | 159 | 326 | 634 | 706.7 | 196.2 | 718.2
350 | 160 | 328.1 | 633.5 | 700.6 | 197.2 | 718.8
351 | 161 | 330.1 | 639.4 | 703.4 | 198.4 | 720.6
352 | 162 | 332.2 | 643.6 | 707.4 | 199.9 | 722.3
353 | 163 | 334.1 | 646.5 | 706.7 | 201.2 | 722.7
354 | 164 | 336 | 648.9 | 701.5 | 202.6 | 723.3
355 | 165 | 337.8 | 645.9 | 693 | 203.7 | 722.6
356 | 166 | 339.4 | 652.8 | 703.7 | 205.6 | 723.6
357 | 167 | 341.1 | 651.4 | 709.6 | 207.1 | 723.3
358 | 168 | 342.9 | 649.5 | 709.9 | 208.9 | 722.7
359 | 169 | 344.8 | 642.3 | 703 | 210.3 | 721.6
360 | 170 | 346.8 | 640.2 | 712.9 | 212 | 720.4
361 | 171 | 348.6 | 643.5 | 726.8 | 213.6 | 719.4
362 | 172 | 350.8 | 646.7 | 740.6 | 215.6 | 720.2
363 | 173 | 353 | 650.8 | 752.2 | 217.8 | 720
364 | 174 | 355.5 | 657 | 749.6 | 219.9 | 720.6
365 | 175 | 357.9 | 658.2 | 762.7 | 222 | 720.4
366 | 176 | 360.5 | 657 | 768.5 | 223.7 | 721.2
367 | 177 | 362.9 | 661.6 | 779.2 | 225.8 | 720.8
368 | 178 | 365.1 | 659.2 | 783.8 | 227.4 | 719.9
369 | 179 | 366.9 | 661.6 | 793.3 | 229.4 | 719.1
370 | 180 | 368.9 | 663.8 | 797.4 | 231.5 | 718.3
371 | 181 | 370.5 | 657.2 | 792.4 | 232.8 | 717.5
372 | 182 | 371.9 | 652.9 | 791.9 | 234.2 | 717.4
373 | 183 | 373.6 | 654.1 | 790.6 | 235.9 | 718.3
374 | 184 | 375.4 | 658.5 | 788.8 | 237.5 | 719.8
375 | 185 | 377.3 | 659.2 | 793.2 | 239.1 | 719.5
376 | 186 | 379.2 | 661.8 | 796.6 | 240.9 | 720.8
377 | 187 | 381.5 | 655.4 | 784.6 | 242.1 | 720.9
378 | 188 | 384 | 652.3 | 770.1 | 243.7 | 723.5
379 | 189 | 386.4 | 647.7 | 764.3 | 245.4 | 723.6
380 | 190 | 388.8 | 645.7 | 762.8 | 247.3 | 724.4
381 | 191 | 391.1 | 634.6 | 745.1 | 248.9 | 725.2
382 | 192 | 393.3 | 632.1 | 748.8 | 250.6 | 726.7
383 | 193 | 395.4 | 635 | 753 | 252.6 | 729.4
384 | 194 | 397.8 | 639 | 755.1 | 254.8 | 731.7
385 | 195 | 400.5 | 639.2 | 755.9 | 256.4 | 732.7
386 | 196 | 403 | 641.3 | 760.2 | 258.3 | 733.7
387 | 197 | 405.8 | 646.6 | 771.1 | 260.5 | 734.7
388 | 198 | 408.6 | 642.8 | 760 | 262.3 | 734.7
389 | 199 | 411.4 | 642.7 | 758.2 | 264.2 | 735
390 | 200 | 414.3 | 637.1 | 743.3 | 265.7 | 734.4
391 | 201 | 416.9 | 635.1 | 737.3 | 267.5 | 733.9
392 | 202 | 419.4 | 632.5 | 741.5 | 269 | 733.4
393 | 203 | 421.9 | 632.8 | 742.3 | 270.8 | 734.8
394 | 204 | 424.6 | 631.4 | 743.4 | 272.4 | 735.1
395 | 205 | 427.3 | 635.4 | 754.9 | 274.2 | 734.6
396 | 206 | 430.2 | 638.8 | 757.7 | 276.3 | 735.4
397 | 207 | 433 | 637.1 | 758.1 | 277.8 | 735.3
398 | 208 | 435.7 | 641.6 | 765.9 | 279.8 | 735.2
399 | 209 | 438.7 | 649.1 | 780 | 281.8 | 735.1
400 | 210 | 441.7 | 647.2 | 773.6 | 283.8 | 734.5
401 | 211 | 444.7 | 646.1 | 774.9 | 285.7 | 733.8
402 | 212 | 447.8 | 651.9 | 783.8 | 287.8 | 734
403 | 213 | 450.9 | 667.7 | 790 | 290.8 | 736
404 | 214 | 454 | 679.3 | 798.7 | 294.1 | 738
405 | 215 | 457.3 | 681.8 | 796.8 | 296.7 | 737.8
406 | 216 | 460.3 | 688.1 | 804.8 | 299 | 739.6
407 | 217 | 463.5 | 692.2 | 808.9 | 302 | 739.8
408 | 218 | 467.1 | 695.4 | 813.9 | 304.4 | 739.6
409 | 219 | 470.7 | 700.9 | 820.2 | 307 | 740.6
410 | 220 | 474.5 | 701.1 | 822.9 | 309.7 | 740.6
411 | 221 | 478.3 | 700.8 | 820.5 | 312.2 | 741.5
412 | 222 | 482.1 | 701.5 | 818.5 | 314.7 | 743.2
413 | 223 | 485.9 | 701.5 | 812.9 | 317 | 744.9
414 | 224 | 489.4 | 701.3 | 812.8 | 319.6 | 746.1
415 | 225 | 492.8 | 702.2 | 810.6 | 322.3 | 748.2
416 | 226 | 495.8 | 700.6 | 789.6 | 324.7 | 749.1
417 | 227 | 498.5 | 702.1 | 784.8 | 327.3 | 750.2
418 | 228 | 501.1 | 702.6 | 771.3 | 329.3 | 751.6
419 | 229 | 503.7 | 700.3 | 757 | 331.8 | 751.9
420 | 230 | 506.2 | 699.1 | 744.5 | 334.2 | 753.3
421 | 231 | 508.8 | 702.9 | 734.1 | 336.9 | 754.7
422 | 232 | 511.5 | 708 | 726.8 | 339.6 | 754.9
423 | 233 | 514 | 705.4 | 709.8 | 341.5 | 755.3
424 | 234 | 516.8 | 711.1 | 711.9 | 345 | 756.9
425 | 235 | 519.7 | 720 | 723.4 | 348.6 | 758.7
426 | 236 | 523 | 726.4 | 737.8 | 352.3 | 760.2
427 | 237 | 526.1 | 723.7 | 725.7 | 355.2 | 761.3
428 | 238 | 529 | 722.4 | 735.4 | 357.9 | 762
429 | 239 | 532.1 | 719.2 | 739.4 | 360.1 | 762.9
430 | 240 | 535.2 | 717.8 | 744.4 | 362.3 | 762.9
431 | 241 | 538.3 | 717.8 | 745.6 | 364.4 | 763.7
432 | 242 | 541.3 | 717.9 | 746 | 366.7 | 765.6
433 | 243 | 544 | 714.7 | 735.1 | 368.3 | 766.8
434 | 244 | 546.2 | 712.7 | 730.5 | 370.1 | 767.4
435 | 245 | 548.5 | 714.2 | 724.8 | 372.8 | 768
436 | 246 | 550.9 | 718.1 | 733.2 | 375.7 | 769.2
437 | 247 | 553.3 | 716.9 | 721.9 | 378.2 | 769.9
438 | 248 | 555.4 | 715.5 | 716 | 380 | 771.1
439 | 249 | 557.2 | 716.8 | 712.6 | 381.9 | 772.5
440 | 250 | 559.1 | 713.2 | 705.7 | 383.5 | 773.7
441 | 251 | 560.9 | 710.5 | 702.1 | 385 | 774.1
442 | 252 | 562.8 | 711.8 | 703.7 | 387.1 | 775.1
443 | 253 | 564.7 | 712.6 | 714.4 | 389 | 775.3
444 | 254 | 566.7 | 711.6 | 725.9 | 391.3 | 775
445 | 255 | 568.8 | 707.6 | 734.7 | 393.6 | 775.1
446 | 256 | 571.1 | 705.3 | 734.3 | 395.7 | 775.3
447 | 257 | 573.6 | 704.5 | 740.2 | 399 | 775.3
448 | 258 | 576.2 | 705.5 | 755 | 403 | 774.6
449 | 259 | 578.7 | 707.9 | 767.1 | 406.5 | 774.4
450 | 260 | 581.4 | 705.9 | 779.1 | 410.6 | 773.2
451 | 261 | 584.1 | 708.2 | 787.8 | 414.8 | 772.4
452 | 262 | 586.7 | 714.1 | 798.2 | 418.9 | 772.5
453 | 263 | 589.4 | 719.1 | 809.9 | 422.9 | 772.2
454 | 264 | 592 | 722.4 | 818.1 | 426.2 | 771.9
455 | 265 | 594.6 | 728 | 824.2 | 429.8 | 773.5
456 | 266 | 597 | 726.7 | 829.1 | 432.5 | 772.9
457 | 267 | 599.4 | 732 | 834 | 436 | 773.4
458 | 268 | 601.9 | 736.8 | 838.3 | 439.7 | 774
459 | 269 | 604.2 | 740.7 | 833.8 | 442.6 | 775.2
460 | 270 | 606.2 | 746.8 | 823 | 445.4 | 777
461 | 271 | 608 | 750.4 | 816.3 | 448.1 | 778.8
462 | 272 | 609.9 | 751.8 | 822 | 451.5 | 780
463 | 273 | 611.6 | 752.6 | 812 | 454.3 | 780.4
464 | 274 | 613.6 | 756.1 | 819.6 | 457.4 | 780.6
465 | 275 | 616 | 760.5 | 828.9 | 461 | 781.3
466 | 276 | 618.4 | 762.6 | 827.4 | 463.6 | 780.7
467 | 277 | 620.9 | 760.7 | 826.6 | 465.5 | 781.3
468 | 278 | 623.4 | 753.9 | 824.9 | 467.7 | 780.4
469 | 279 | 625.9 | 750.4 | 828.2 | 470.5 | 779.5
470 | 280 | 628.5 | 744.2 | 823.8 | 472.9 | 776.9
471 | 281 | 631.2 | 741.1 | 818.1 | 475.2 | 776
472 | 282 | 633.9 | 742.2 | 821.6 | 477 | 776.3
473 | 283 | 636.5 | 746.1 | 818.4 | 479.5 | 776.7
474 | 284 | 638.7 | 741.9 | 813.5 | 480.4 | 776.1
475 | 285 | 640.6 | 735.9 | 809 | 481 | 775.2
476 | 286 | 642.4 | 735.3 | 813.4 | 482.1 | 775.1
477 | 287 | 644.1 | 732.1 | 812.2 | 482.9 | 775.5
478 | 288 | 645.8 | 730.8 | 812.8 | 482.9 | 775.9
479 | 289 | 647.5 | 735.5 | 816.8 | 484.4 | 777.4
480 | 290 | 649.2 | 733 | 817 | 485.6 | 777.6
481 | 291 | 650.8 | 732.9 | 809.7 | 486.4 | 778.2
482 | 292 | 652.4 | 730.6 | 802 | 487.8 | 778.1
483 | 293 | 654 | 731.8 | 806 | 488.7 | 778
484 | 294 | 655.2 | 730.9 | 806.5 | 489.6 | 778.6
485 | 295 | 656.1 | 730.9 | 802.1 | 490.1 | 778.9
486 | 296 | 657.3 | 732.4 | 808.2 | 491.5 | 779
487 | 297 | 658.7 | 736.2 | 815.7 | 493.5 | 779.4
488 | 298 | 660.1 | 735.4 | 822.6 | 495.1 | 779.8
489 | 299 | 661.6 | 734.5 | 827.7 | 496.1 | 778.4
490 | 300 | 663.1 | 736.7 | 828.2 | 498 | 777.1
491 | 301 | 664.9 | 736 | 828.6 | 500 | 776.1
492 | 302 | 666.6 | 733.8 | 832.5 | 501.5 | 775.2
493 | 303 | 668.2 | 735.1 | 833.5 | 503.2 | 775.3
494 | 304 | 669.7 | 738 | 833 | 505 | 774.8
495 | 305 | 671.1 | 739 | 833.9 | 506 | 773.4
496 | 306 | 672.8 | 737.5 | 835.5 | 506.8 | 773.1
497 | 307 | 674.8 | 736.1 | 832 | 506.9 | 772.8
498 | 308 | 676.7 | 736.8 | 828.7 | 506.7 | 773.5
499 | 309 | 678.5 | 726.4 | 817.5 | 505.1 | 773.1
500 | 310 | 679.9 | 726 | 814.8 | 503.7 | 774.1
501 | 311 | 681.4 | 721.4 | 809.3 | 502.5 | 773.5
502 | 312 | 682.6 | 717.8 | 801.4 | 501.4 | 774.8
503 | 313 | 683.8 | 711.1 | 792 | 500 | 775.2
504 | 314 | 685.2 | 710.1 | 795.9 | 499.9 | 776.1
505 | 315 | 686.7 | 705 | 786.5 | 499.2 | 775.5
506 | 316 | 688.2 | 704.5 | 788.9 | 499 | 775.6
507 | 317 | 689.8 | 702.9 | 792.9 | 499.6 | 774.8
508 | 318 | 691.5 | 702.3 | 798.7 | 500.2 | 773.7
509 | 319 | 692.8 | 708.2 | 811.4 | 501.9 | 773.6
510 | 320 | 694.1 | 707 | 807.2 | 502.6 | 772.1
511 | 321 | 695.6 | 708 | 813.2 | 503.9 | 770.7
512 | 322 | 697.2 | 707 | 823.6 | 504.7 | 770
513 | 323 | 698.8 | 709.8 | 829.6 | 505.9 | 769.8
514 | 324 | 700.2 | 710.1 | 832.9 | 506.8 | 768.4
515 | 325 | 701.7 | 711.7 | 834.6 | 507.8 | 768.6
516 | 326 | 703.1 | 713.7 | 836 | 508.8 | 768.6
517 | 327 | 704.3 | 711.2 | 833.5 | 509.5 | 768.3
518 | 328 | 705.6 | 708.7 | 835.5 | 510.1 | 768.4
519 | 329 | 706.6 | 707.5 | 829.6 | 511 | 768
520 | 330 | 707.4 | 706.1 | 830.6 | 512 | 765.8
521 | 331 | 709 | 702.4 | 831.2 | 512.9 | 763.9
522 | 332 | 710.1 | 701 | 830 | 513.1 | 764.4
523 | 333 | 711.1 | 700.7 | 828.7 | 513 | 764.1
524 | 334 | 711.9 | 699 | 826.2 | 512.3 | 763.9
525 | 335 | 712.8 | 698.8 | 825.6 | 512.2 | 764.1
526 | 336 | 713.9 | 697.7 | 824.1 | 512.4 | 763.2
527 | 337 | 714.9 | 697.3 | 825.4 | 512.7 | 762.3
528 | 338 | 715.3 | 692 | 815.1 | 511.2 | 761.2
529 | 339 | 716.1 | 692.2 | 814.3 | 510.9 | 761.1
530 | 340 | 717.3 | 690.9 | 814.1 | 510.9 | 759.2
531 | 341 | 718.2 | 687.9 | 808.5 | 510.2 | 759.1
532 | 342 | 719 | 682.6 | 807.5 | 509.4 | 757.9
533 | 343 | 719.6 | 679.6 | 808.7 | 509.4 | 757.1
534 | 344 | 720.3 | 679.4 | 815.8 | 509.3 | 757.8
535 | 345 | 721.1 | 679.8 | 813.6 | 508.9 | 757.8
536 | 346 | 721.9 | 681.4 | 812.3 | 509.5 | 756.7
537 | 347 | 722.4 | 679.5 | 809.6 | 509.6 | 755.4
538 | 348 | 723.2 | 675.2 | 806.6 | 509.5 | 754.7
539 | 349 | 724.2 | 673.8 | 807.3 | 510 | 753
540 | 350 | 725.1 | 673.9 | 804.7 | 510.9 | 751.3
541 | 351 | 725.6 | 672.9 | 803.7 | 511.4 | 750.2
542 | 352 | 726.2 | 670.7 | 805.3 | 511.8 | 748.9
543 | 353 | 726.7 | 669.1 | 804.9 | 511.5 | 747.9
544 | 354 | 727.2 | 668.8 | 804.1 | 511.2 | 747.1
545 | 355 | 727.4 | 667.5 | 805.3 | 511.1 | 746.2
546 | 356 | 727.5 | 668.8 | 806.6 | 511 | 746.7
547 | 357 | 727.6 | 668.4 | 808.3 | 511.5 | 745.4
548 | 358 | 727.8 | 665.9 | 809 | 511 | 744
549 | 359 | 728.4 | 662.5 | 806.2 | 511 | 742.8
550 | 360 | 729.1 | 660.9 | 805.1 | 511.5 | 741.3
551 | 361 | 729.9 | 661.1 | 804 | 511.8 | 739.7
552 | 362 | 730.1 | 661 | 805.8 | 511.9 | 738.6
553 | 363 | 730.6 | 658.7 | 803.1 | 512 | 737.4
554 | 364 | 731.3 | 655.4 | 798.2 | 512.3 | 736
555 | 365 | 731.9 | 654.3 | 791 | 512.1 | 735.8
556 | 366 | 731.8 | 654.9 | 790 | 511.8 | 736.1
557 | 367 | 731 | 658.8 | 793.9 | 511.8 | 738.7
558 | 368 | 730.7 | 662.7 | 802.3 | 512.4 | 740
559 | 369 | 730.6 | 663.3 | 808.8 | 513.2 | 739.2
560 | 370 | 730.5 | 664.6 | 810.6 | 514.2 | 737.4
561 | 371 | 730.8 | 663.6 | 811.2 | 515.6 | 736.8
562 | 372 | 731.3 | 661.1 | 808.3 | 516.4 | 734.6
563 | 373 | 732.1 | 659.8 | 804.5 | 517.1 | 733.2
564 | 374 | 733.1 | 658.6 | 798.9 | 517.6 | 732.2
565 | 375 | 734.2 | 660.2 | 792.4 | 518.4 | 730.7
566 | 376 | 735.3 | 664.4 | 792.7 | 519.4 | 730.2
567 | 377 | 735.7 | 665.8 | 805.3 | 520.5 | 730.4
568 | 378 | 736.2 | 669.8 | 808.7 | 522.5 | 729.7
569 | 379 | 736.8 | 670.9 | 815.2 | 525.1 | 730.1
570 | 380 | 737.2 | 667.4 | 809.9 | 527 | 730.2
571 | 381 | 737.3 | 671.7 | 813.5 | 529.2 | 732
572 | 382 | 737.7 | 673.5 | 817.8 | 531.9 | 735.5
573 | 383 | 738.2 | 673.5 | 821.5 | 535.7 | 734.7
574 | 384 | 738.5 | 674.4 | 818.9 | 540.4 | 736.8
575 | 385 | 739 | 679.2 | 823.4 | 545.2 | 738.4
576 | 386 | 739 | 680.1 | 820.9 | 549.9 | 739.4
577 | 387 | 739.3 | 683.6 | 820.9 | 555.2 | 741.2
578 | 388 | 739.5 | 683.1 | 822 | 559.9 | 739.6
579 | 389 | 739.9 | 682.6 | 816.7 | 564.7 | 739.9
580 | 390 | 739.9 | 687.9 | 822.4 | 569.4 | 740.8
581 | 391 | 739.5 | 689.1 | 823.8 | 573.8 | 741.7
582 | 392 | 739.5 | 693 | 828.9 | 579.4 | 742.8
583 | 393 | 739.4 | 692.7 | 831.2 | 585.1 | 744.2
584 | 394 | 739.4 | 692.5 | 827.8 | 590.8 | 743.4
585 | 395 | 739.6 | 694.3 | 833.2 | 596.6 | 745.3
586 | 396 | 739.8 | 694.9 | 834.9 | 601.3 | 746.9
587 | 397 | 739.7 | 698.4 | 839.2 | 605.7 | 749
588 | 398 | 740.2 | 701.3 | 843.1 | 610.5 | 749.7
589 | 399 | 740.9 | 701.1 | 840.4 | 615.2 | 748.4
590 | 400 | 742 | 694 | 828.4 | 619.5 | 746.8
591 | 401 | 743 | 691.5 | 826.3 | 624.5 | 745.3
592 | 402 | 744.1 | 690.3 | 814 | 629.6 | 742.7
593 | 403 | 745.2 | 690.4 | 812.7 | 635.7 | 741.1
594 | 404 | 746.1 | 691.3 | 810.9 | 641.9 | 739.5
595 | 405 | 746.6 | 688.8 | 808.9 | 646.6 | 737
596 | 406 | 746.8 | 683.8 | 803.6 | 650.3 | 736
597 | 407 | 746.7 | 680.9 | 804.7 | 654.2 | 736
598 | 408 | 746.8 | 678.6 | 802.8 | 658.2 | 735.1
599 | 409 | 747 | 676.6 | 798.8 | 662.1 | 733.5
600 | 410 | 747.1 | 676.5 | 797.7 | 666.3 | 733.6
601 | 411 | 747.2 | 677.2 | 802.7 | 670.4 | 733.5
602 | 412 | 747 | 680.4 | 806.7 | 673.6 | 735.6
603 | 413 | 746.5 | 681.4 | 800.9 | 676.5 | 738.8
604 | 414 | 746.2 | 678.7 | 790.2 | 678.8 | 739.4
605 | 415 | 746 | 678.4 | 787.3 | 681.4 | 741.2
606 | 416 | 745.7 | 678.8 | 781.6 | 683.2 | 743
607 | 417 | 745.3 | 678.6 | 789 | 684.9 | 743
608 | 418 | 745 | 679.2 | 785.2 | 686.9 | 744.5
609 | 419 | 745.1 | 676.8 | 777.4 | 689.3 | 743.7
610 | 420 | 744.9 | 676.2 | 789.9 | 692.7 | 744.1
611 | 421 | 745.2 | 674 | 787.7 | 696.2 | 741.4
612 | 422 | 745.5 | 673.9 | 788.8 | 700.6 | 740.8
613 | 423 | 745.9 | 672.6 | 787.9 | 704.5 | 739
614 | 424 | 746.8 | 670.2 | 777.2 | 709 | 736.9
615 | 425 | 747.5 | 669.5 | 777.7 | 713.7 | 736.5
616 | 426 | 748 | 670 | 777.1 | 717.9 | 735.5
617 | 427 | 747.8 | 669.7 | 780.7 | 722.1 | 734.7
618 | 428 | 747.2 | 670.3 | 787.4 | 725.7 | 734.1
619 | 429 | 746.7 | 672.1 | 788.2 | 729.1 | 735.3
620 | 430 | 746 | 671.5 | 792.7 | 732.6 | 735.4
621 | 431 | 745.7 | 671.3 | 793.6 | 736 | 735.1
622 | 432 | 745.9 | 670.4 | 793.9 | 740.1 | 732.8
623 | 433 | 746.1 | 672.4 | 795.2 | 745.1 | 731.1
624 | 434 | 746.2 | 672.5 | 794.6 | 749.4 | 731
625 | 435 | 746.6 | 669.8 | 791.3 | 754.1 | 730.1
626 | 436 | 747.3 | 669.6 | 792.7 | 760.9 | 729.1
627 | 437 | 747.3 | 675.4 | 799.7 | 764.6 | 732.2
628 | 438 | 746.8 | 678.4 | 801.2 | 765.3 | 734.3
629 | 439 | 746.1 | 677.2 | 795.7 | 767.2 | 736
630 | 440 | 744.9 | 672.2 | 774.1 | 769.9 | 737.4
631 | 441 | 744.1 | 672.5 | 779.4 | 772.4 | 738.8
632 | 442 | 743.6 | 672.3 | 785.2 | 774 | 739.3
633 | 443 | 743.5 | 671.9 | 783 | 775.3 | 740.9
634 | 444 | 743.1 | 674.4 | 785.8 | 775 | 744.3
635 | 445 | 742.2 | 683.4 | 795.8 | 774.9 | 746.7
636 | 446 | 742 | 689.2 | 803 | 776.1 | 749.2
637 | 447 | 742.1 | 688.9 | 801.3 | 778.3 | 750.7
638 | 448 | 742.3 | 687.1 | 801.2 | 780.7 | 748.6
639 | 449 | 743.2 | 683.8 | 793.4 | 784.9 | 747.9
640 | 450 | 744.2 | 682.4 | 789.9 | 790.1 | 746.3
641 | 451 | 744.3 | 679.3 | 785.9 | 791.4 | 744.6
642 | 452 | 744.6 | 679.5 | 783.5 | 794.2 | 743.5
643 | 453 | 744.9 | 677.8 | 787.1 | 797 | 741.7
644 | 454 | 745.2 | 678.5 | 782.3 | 801 | 740.8
645 | 455 | 745.3 | 676.9 | 771.6 | 804.7 | 741.1
646 | 456 | 745.3 | 677.1 | 778.5 | 807 | 742.8
647 | 457 | 745.3 | 680.3 | 784.8 | 807 | 742.2
648 | 458 | 745.2 | 680.4 | 782.5 | 806.9 | 741.9
649 | 459 | 745.7 | 677.6 | 779.7 | 809 | 742.5
650 | 460 | 746.3 | 681.5 | 778.6 | 811.9 | 740.4
651 | 461 | 746.8 | 686.7 | 783.1 | 813.6 | 741
652 | 462 | 747 | 692.6 | 787.8 | 813.5 | 743.4
653 | 463 | 747 | 696.5 | 793.9 | 813.3 | 745.3
654 | 464 | 747.6 | 694.9 | 792.2 | 813 | 741.1
655 | 465 | 748.4 | 696.8 | 793.6 | 814.1 | 739.2
656 | 466 | 749.2 | 700.7 | 792 | 814.8 | 737.7
657 | 467 | 750.1 | 702.1 | 795.4 | 815.9 | 737.5
658 | 468 | 750.4 | 704 | 798.4 | 816.1 | 739.2
659 | 469 | 751 | 704.5 | 798 | 815.7 | 739.8
660 | 470 | 751.6 | 704.7 | 801.4 | 816 | 738.7
661 | 471 | 752.1 | 712.4 | 807.8 | 816.4 | 740.9
662 | 472 | 752.4 | 717 | 809.7 | 814.9 | 743.3
663 | 473 | 752.7 | 721.1 | 814.7 | 813.2 | 743.9
664 | 474 | 752.9 | 723.1 | 817.9 | 811.8 | 746.1
665 | 475 | 753.1 | 726.6 | 820.1 | 810.9 | 748.7
666 | 476 | 753 | 728.5 | 819.6 | 810.4 | 751.5
667 | 477 | 753.5 | 730.5 | 823.6 | 809.8 | 753.4
668 | 478 | 754.1 | 730.7 | 827.3 | 809 | 754.6
669 | 479 | 754.6 | 731.4 | 829.9 | 809.2 | 756.1
670 | 480 | 755 | 731.7 | 828.8 | 808.4 | 758.4
671 | 481 | 755.3 | 732.5 | 829.7 | 807.7 | 761.3
672 | 482 | 755.7 | 733.4 | 830.6 | 807.1 | 763.1
673 | 483 | 756.4 | 732.3 | 825.7 | 807.4 | 764.6
674 | 484 | 756.8 | 731.2 | 823.5 | 806.4 | 766.6
675 | 485 | 756.9 | 729.5 | 821.4 | 805.3 | 768.9
676 | 486 | 757 | 729.6 | 820 | 804.5 | 771.3
677 | 487 | 756.9 | 727.5 | 818.3 | 804.2 | 772.6
678 | 488 | 757.4 | 729.8 | 821.8 | 803.7 | 774.1
679 | 489 | 757.7 | 730 | 821.4 | 803.9 | 774.7
680 | 490 | 758.6 | 730.7 | 823.5 | 804.6 | 774
681 | 491 | 759.4 | 728.3 | 820.4 | 805.3 | 772.1
682 | 492 | 759.8 | 730.8 | 820.8 | 806.5 | 772.7
683 | 493 | 759.9 | 732.1 | 820.5 | 806.9 | 775.6
684 | 494 | 760.1 | 732.6 | 824.2 | 807.2 | 776.4
685 | 495 | 760.5 | 733.3 | 825.2 | 807 | 776.9
686 | 496 | 761.2 | 731.7 | 822.6 | 808 | 778.2
687 | 497 | 762.7 | 733 | 824.1 | 809.4 | 776.7
688 | 498 | 763.8 | 730.9 | 823.8 | 811.9 | 774.3
689 | 499 | 764.6 | 731.8 | 824.3 | 814.5 | 774.4
690 | 500 | 765.9 | 732 | 825 | 817.3 | 774.6
691 | 501 | 766.5 | 733.7 | 825.7 | 818 | 777.5
692 | 502 | 766.9 | 734.2 | 825.1 | 818.3 | 779.5
693 | 503 | 768 | 732.9 | 825.5 | 820.1 | 778.7
694 | 504 | 768.5 | 733.2 | 824.8 | 820.4 | 779.9
695 | 505 | 768.7 | 735 | 821.9 | 820.1 | 780.1
696 | 506 | 769.1 | 735.3 | 820 | 819.3 | 782.2
697 | 507 | 769 | 731.1 | 811.5 | 818.6 | 782.7
698 | 508 | 769.4 | 728.7 | 810.7 | 818.9 | 783
699 | 509 | 769.7 | 730.9 | 811.5 | 818.8 | 782.7
700 | 510 | 770.2 | 732.3 | 817.3 | 818.7 | 784
701 | 511 | 771.1 | 730.1 | 818.4 | 818.4 | 784.3
702 | 512 | 772.4 | 729.5 | 817.3 | 819.3 | 781.9
703 | 513 | 773.6 | 731.3 | 816.9 | 820.8 | 781.3
704 | 514 | 775.1 | 728.7 | 815.4 | 823 | 778.8
705 | 515 | 776.9 | 727 | 813.6 | 825.9 | 775.2
706 | 516 | 778.3 | 726.8 | 816 | 829 | 774.3
707 | 517 | 779.2 | 727.2 | 811.7 | 830 | 774.2
708 | 518 | 779.9 | 727 | 814.2 | 829.6 | 773
709 | 519 | 780.1 | 725.1 | 814.2 | 829.4 | 772.3
710 | 520 | 780.8 | 721.9 | 810.3 | 829.6 | 769.3
711 | 521 | 781.6 | 722.4 | 809 | 831.2 | 769
712 | 522 | 782.2 | 727.4 | 812.1 | 832.6 | 770.1
713 | 523 | 782.8 | 725.7 | 809.2 | 833.4 | 768
714 | 524 | 783.2 | 728.4 | 808.7 | 833.9 | 768.7
715 | 525 | 783 | 729.7 | 808 | 832.6 | 768.9
716 | 526 | 783.3 | 727.5 | 807.5 | 833.6 | 766.6
717 | 527 | 783.7 | 731.3 | 810 | 833.4 | 769.2
718 | 528 | 783.5 | 730 | 808.4 | 831.6 | 767.6
719 | 529 | 784.4 | 726.2 | 806.1 | 832.1 | 766.4
720 | 530 | 785.1 | 726.1 | 806.9 | 832.5 | 766.2
721 | 531 | 785.9 | 723.7 | 806.4 | 834.2 | 764.6
722 | 532 | 786.8 | 721.3 | 805.8 | 834.9 | 763.2
723 | 533 | 787.6 | 718.8 | 804.7 | 835.3 | 761.2
724 | 534 | 788 | 719.4 | 804.3 | 834.2 | 760.1
725 | 535 | 788.2 | 719.3 | 800.9 | 832.3 | 759.5
726 | 536 | 788.5 | 716.2 | 797.8 | 831.7 | 757.5
727 | 537 | 789.4 | 714.4 | 795.8 | 832.6 | 756.3
728 | 538 | 789.8 | 714.4 | 796.5 | 832.9 | 756.8
729 | 539 | 789.8 | 714.1 | 798.3 | 833.2 | 757.7
730 | 540 | 789.7 | 715.2 | 798.2 | 832.8 | 758
731 | 541 | 789.2 | 716.5 | 792.9 | 831.2 | 758.3
732 | 542 | 788.7 | 719.8 | 788.1 | 829.1 | 759.3
733 | 543 | 787.8 | 722.2 | 792.5 | 824.5 | 760.3
734 | 544 | 787.7 | 726.2 | 795.1 | 822.8 | 761.8
735 | 545 | 787.1 | 725.3 | 797.3 | 820.7 | 762.2
736 | 546 | 786.9 | 720 | 795.5 | 818.8 | 761.7
737 | 547 | 787.4 | 718.7 | 799.9 | 820 | 761.8
738 | 548 | 788.1 | 717.4 | 799 | 822.7 | 761.9
739 | 549 | 788.9 | 717.8 | 800.5 | 826.5 | 762.4
740 | 550 | 788.9 | 720.1 | 801.9 | 827 | 763.4
741 | 551 | 788.8 | 720.8 | 803.1 | 825.1 | 764
742 | 552 | 788.7 | 725.3 | 802.7 | 823.8 | 764.3
743 | 553 | 788.7 | 725.7 | 804.7 | 822.3 | 763.5
744 | 554 | 788.6 | 726.7 | 805.9 | 820.5 | 763.1
745 | 555 | 789 | 721.9 | 806.6 | 819.9 | 762
746 | 556 | 789.9 | 713.1 | 798.5 | 820.9 | 760.4
747 | 557 | 791.4 | 703.4 | 789.8 | 823.6 | 758.4
748 | 558 | 792.4 | 706.1 | 794.3 | 825.8 | 758.4
749 | 559 | 793.1 | 704.1 | 797.7 | 826.5 | 757.1
750 | 560 | 793.5 | 705 | 796.9 | 825.9 | 756.7
751 | 561 | 793.7 | 706.9 | 797.2 | 827 | 756.3
752 | 562 | 794.6 | 708.4 | 797.3 | 827.5 | 756.6
753 | 563 | 794.5 | 709.9 | 796 | 827.2 | 758
754 | 564 | 794.3 | 714.1 | 796.5 | 825.2 | 760.7
755 | 565 | 794.1 | 715.4 | 796.9 | 822.5 | 761.6
756 | 566 | 794 | 716.6 | 798.4 | 821 | 763.4
757 | 567 | 794.3 | 723.1 | 797.5 | 820.7 | 765.8
758 | 568 | 794.4 | 723.9 | 793.4 | 820.2 | 768.6
759 | 569 | 794.6 | 725 | 791.9 | 820.1 | 771.4
760 | 570 | 793.8 | 724.4 | 787.5 | 818.7 | 773
761 | 571 | 793.6 | 728.2 | 787.8 | 818.9 | 775.5
762 | 572 | 793.5 | 727.1 | 778.2 | 818.4 | 777
763 | 573 | 792.9 | 728.1 | 776.9 | 818.8 | 778.9
764 | 574 | 792.5 | 727 | 766.9 | 818.7 | 781.2
765 | 575 | 792.2 | 726.8 | 763.8 | 818.3 | 782.9
766 | 576 | 792.3 | 728.2 | 769.4 | 819 | 785.1
767 | 577 | 792.3 | 729.8 | 772.7 | 819 | 787.4
768 | 578 | 792.6 | 728.7 | 777.5 | 817.5 | 788.3
769 | 579 | 792.7 | 730 | 781.5 | 815.6 | 790
770 | 580 | 793 | 730 | 784.8 | 813.6 | 790.5
771 | 581 | 793.5 | 726.9 | 785.6 | 811.5 | 790.6
772 | 582 | 794.3 | 724 | 787.4 | 810.5 | 789.6
773 | 583 | 794.9 | 725.3 | 791.3 | 810.3 | 791.1
774 | 584 | 795.2 | 728.6 | 790.7 | 809.5 | 793.1
775 | 585 | 795.7 | 727 | 794.4 | 808 | 792.7
776 | 586 | 796.6 | 723.5 | 792.1 | 806 | 789.9
777 | 587 | 797.7 | 718.2 | 792.5 | 805.6 | 789.2
778 | 588 | 798.2 | 714.1 | 790.4 | 805.8 | 788.6
779 | 589 | 799 | 709.2 | 788.7 | 805.4 | 785.8
780 | 590 | 799.9 | 704.1 | 781.6 | 805.1 | 783
781 | 591 | 800.6 | 698.8 | 776.9 | 805.5 | 779
782 | 592 | 801.4 | 694 | 773.5 | 806.2 | 775.3
783 | 593 | 802.1 | 691.5 | 773.6 | 807.2 | 773.1
784 | 594 | 802.5 | 693.5 | 775.7 | 808.5 | 772.3
785 | 595 | 802.7 | 694.2 | 779.9 | 809.1 | 771.6
786 | 596 | 803.1 | 690.4 | 782.4 | 808.6 | 768
787 | 597 | 803.2 | 691 | 785.1 | 808.2 | 766.8
788 | 598 | 803.2 | 690.5 | 785 | 806.9 | 766.5
789 | 599 | 803.6 | 691.5 | 785.7 | 806 | 765.6
790 | 600 | 803.7 | 692.9 | 791.6 | 804.3 | 767.9
791 | 601 | 803.5 | 698.1 | 794.2 | 802.2 | 769.2
792 | 602 | 803.3 | 701.9 | 798.4 | 799.7 | 769.6
793 | 603 | 803.9 | 701.1 | 797.2 | 796.7 | 767.2
794 | 604 | 804.4 | 697.8 | 791.6 | 793.6 | 765.2
795 | 605 | 804.7 | 701.2 | 793.4 | 793.1 | 764.5
796 | 606 | 805.3 | 701.8 | 795.5 | 792.9 | 762.8
797 | 607 | 805.6 | 697.8 | 792.2 | 791 | 761.8
798 | 608 | 805.8 | 701.6 | 796.6 | 789.9 | 763.3
799 | 609 | 805.7 | 696.2 | 787.3 | 787.8 | 761.4
800 | 610 | 805.8 | 689.5 | 777.7 | 783.9 | 758.4
801 | 611 | 805.6 | 689.7 | 775.2 | 781.7 | 762
802 | 612 | 805.4 | 693.2 | 779.7 | 780.9 | 762.8
803 | 613 | 805.4 | 691.6 | 779.1 | 779.1 | 760.4
804 | 614 | 805.7 | 686.2 | 768.8 | 776.2 | 759.4
805 | 615 | 805.4 | 686.3 | 767.4 | 774.7 | 762.1
806 | 616 | 805 | 684.8 | 763.7 | 773.8 | 763.3
807 | 617 | 804.5 | 683.1 | 758.8 | 772.3 | 764.4
808 | 618 | 804 | 682.8 | 759 | 771.4 | 765.9
809 | 619 | 803.5 | 684.2 | 760.7 | 770.9 | 765.9
810 | 620 | 803.3 | 687.9 | 760.1 | 771 | 768.6
811 | 621 | 802.7 | 695.3 | 766.5 | 771.8 | 769.9
812 | 622 | 802.3 | 698.1 | 775.3 | 772.3 | 771
813 | 623 | 802.3 | 702 | 781.6 | 773.2 | 773.4
814 | 624 | 802.6 | 702.1 | 784.7 | 772.9 | 773.2
815 | 625 | 803.2 | 701.9 | 781.3 | 771.9 | 773.3
816 | 626 | 804 | 701.5 | 784.6 | 770.7 | 773.5
817 | 627 | 804.6 | 704.9 | 791.1 | 771.2 | 773.2
818 | 628 | 805 | 701.9 | 788.1 | 770.1 | 771.6
819 | 629 | 805.3 | 700.7 | 784.7 | 768.5 | 771.8
820 | 630 | 805.7 | 702.9 | 786.5 | 768.3 | 773.6
821 | 631 | 806.1 | 699.5 | 788.5 | 767.6 | 771.9
822 | 632 | 806.6 | 694.3 | 782 | 765.7 | 768.4
823 | 633 | 806.7 | 688.3 | 774.3 | 763.8 | 767.7
824 | 634 | 806.6 | 680.4 | 762.9 | 761 | 765.5
825 | 635 | 806.4 | 675.1 | 758 | 759 | 765.2
826 | 636 | 806.6 | 672 | 759.9 | 758 | 764.7
827 | 637 | 806.6 | 671.5 | 761.9 | 757.2 | 766.1
828 | 638 | 806.6 | 670.5 | 765.3 | 756.5 | 765.6
829 | 639 | 806.6 | 670.9 | 766.4 | 755.5 | 765
830 | 640 | 806.9 | 668.2 | 761.9 | 754.6 | 764.8
831 | 641 | 807.3 | 668 | 762.5 | 754.3 | 763.8
832 | 642 | 807.3 | 665.6 | 757.6 | 753.1 | 761.4
833 | 643 | 807.2 | 666.8 | 766.2 | 752.5 | 762.3
834 | 644 | 806.7 | 672.7 | 767.2 | 752.8 | 764.9
835 | 645 | 805.9 | 681.7 | 764.8 | 753.9 | 767.1
836 | 646 | 805.3 | 684.4 | 764 | 754.9 | 767.6
837 | 647 | 804.9 | 689.8 | 765.4 | 755.7 | 768.1
838 | 648 | 804.6 | 689.7 | 759.8 | 755.8 | 769.7
839 | 649 | 804.1 | 689.8 | 755.3 | 755.5 | 770.9
840 | 650 | 803.6 | 692.3 | 750.7 | 755.1 | 772.2
841 | 651 | 802.8 | 695.8 | 750 | 755.2 | 774.6
842 | 652 | 801.8 | 696.3 | 749.3 | 755 | 775
843 | 653 | 801.3 | 696.3 | 751.2 | 754.4 | 776.1
844 | 654 | 801 | 698.1 | 758.6 | 754.6 | 776.8
845 | 655 | 800.9 | 697.9 | 758.5 | 754.2 | 778
846 | 656 | 801.1 | 698.9 | 760.8 | 754.2 | 780.3
847 | 657 | 801.3 | 698.7 | 764.6 | 753.7 | 778.9
848 | 658 | 801.5 | 699.8 | 761.6 | 752.7 | 781.3
849 | 659 | 801.9 | 697.4 | 757.5 | 752.1 | 782.5
850 | 660 | 802 | 693.5 | 755.6 | 753.1 | 782.6
851 | 661 | 801.7 | 698.3 | 760.1 | 758.2 | 784
852 | 662 | 801.4 | 701.5 | 761 | 764.2 | 785.1
853 | 663 | 801.6 | 704 | 764.4 | 769 | 785.9
854 | 664 | 801.8 | 709 | 762.9 | 774.3 | 787.8
855 | 665 | 801.7 | 706.3 | 759.1 | 776.5 | 787.6
856 | 666 | 802 | 704.4 | 763 | 777.5 | 785.9
857 | 667 | 802.5 | 702.6 | 763.5 | 777 | 786.3
858 | 668 | 802.7 | 699.7 | 764.9 | 776 | 786
859 | 669 | 802.8 | 697.6 | 761.6 | 774.8 | 786.6
860 | 670 | 803 | 692.4 | 759.6 | 773.5 | 785.1
861 | 671 | 803.7 | 689.6 | 758.6 | 771.9 | 784.1
862 | 672 | 803.8 | 689.8 | 762.3 | 771.7 | 783.5
863 | 673 | 803.8 | 685.9 | 757 | 769.4 | 781.1
864 | 674 | 803.6 | 685.2 | 755 | 767.5 | 782
865 | 675 | 803 | 688.2 | 753.1 | 767.9 | 783.2
866 | 676 | 802.4 | 693.1 | 757.1 | 770.1 | 786.1
867 | 677 | 801.9 | 696.7 | 757.3 | 772.5 | 787
868 | 678 | 801.2 | 699.2 | 761.2 | 774.5 | 786.6
869 | 679 | 801.1 | 700.7 | 770.3 | 776.4 | 787.2
870 | 680 | 801 | 706.4 | 776.3 | 780.1 | 788.4
871 | 681 | 801 | 708.4 | 777.3 | 782.5 | 789.1
872 | 682 | 801.3 | 712.9 | 783.1 | 785.2 | 790.2
873 | 683 | 801.7 | 714.1 | 781.2 | 787.4 | 791.9
874 | 684 | 802.1 | 711.9 | 777.2 | 787 | 793.4
875 | 685 | 802.4 | 711 | 773.5 | 786.3 | 793.9
876 | 686 | 802.8 | 702.4 | 762 | 781.4 | 792
877 | 687 | 802.7 | 693.1 | 748.6 | 775.2 | 790.4
878 | 688 | 802.2 | 689.2 | 740.2 | 769.8 | 788.2
879 | 689 | 801.4 | 686.6 | 740.1 | 766 | 788.7
880 | 690 | 801 | 684.4 | 743.3 | 763.4 | 788.2
881 | 691 | 800.9 | 686.5 | 748.8 | 762.4 | 787.9
882 | 692 | 801.3 | 687.5 | 749.8 | 761.9 | 788.3
883 | 693 | 801.3 | 689 | 749.3 | 762.9 | 789.3
884 | 694 | 801.7 | 685.3 | 755.3 | 761.9 | 786.8
885 | 695 | 802.2 | 683.7 | 751.8 | 760.9 | 785.9
886 | 696 | 802.3 | 686.9 | 754 | 761.7 | 787.7
887 | 697 | 801.8 | 694.3 | 753.2 | 764 | 789
888 | 698 | 801.2 | 700.6 | 755.9 | 766.7 | 790.2
889 | 699 | 800.8 | 703.9 | 755.8 | 769.7 | 791.1
890 | 700 | 800.4 | 707.8 | 756 | 772.5 | 793.5
891 | 701 | 800.1 | 705.4 | 754 | 772.9 | 793.8
892 | 702 | 800.4 | 707.6 | 758.3 | 773.9 | 794.4
893 | 703 | 800.5 | 710.8 | 759.8 | 775.9 | 795.5
894 | 704 | 800.1 | 710.7 | 755.1 | 776.9 | 796.7
895 | 705 | 799.9 | 710.9 | 757.4 | 776.8 | 797
896 | 706 | 799.7 | 714.5 | 754 | 777.2 | 799.2
897 | 707 | 799.6 | 714.2 | 746.8 | 777.6 | 800.6
898 | 708 | 799.6 | 710.4 | 743.5 | 776.2 | 801.3
899 | 709 | 799.2 | 709.3 | 741.3 | 776.1 | 802
900 | 710 | 799 | 713.2 | 742.4 | 777.3 | 802.5
901 | 711 | 798.6 | 714.2 | 745.2 | 778.2 | 803.9
902 | 712 | 798.1 | 715.8 | 750.5 | 780.2 | 805.6
903 | 713 | 798.4 | 714.4 | 756.5 | 780 | 805
904 | 714 | 799.3 | 711 | 754.4 | 777.7 | 803.5
905 | 715 | 799.9 | 706.1 | 751.6 | 774.9 | 801.3
906 | 716 | 800.5 | 701.4 | 746.3 | 771.7 | 800.9
907 | 717 | 801.3 | 700.6 | 756.4 | 769.7 | 799.1
908 | 718 | 801.8 | 704.6 | 760.1 | 769.8 | 800.5
909 | 719 | 802.4 | 705.1 | 765.5 | 770 | 798.1
910 | 720 | 803.2 | 699.2 | 762.1 | 768.2 | 794.7
911 | 721 | 804.3 | 698.6 | 766.7 | 767.7 | 791.6
912 | 722 | 805.1 | 693.3 | 764.2 | 766 | 788.1
913 | 723 | 805.6 | 694.5 | 766.1 | 764.9 | 787.5
914 | 724 | 805.4 | 697.5 | 760.9 | 764.4 | 789
915 | 725 | 805 | 700.6 | 766.5 | 765.6 | 788.3
916 | 726 | 804.3 | 705.7 | 761.8 | 767.5 | 788.3
917 | 727 | 804.3 | 706.7 | 762.8 | 767.8 | 788.6
918 | 728 | 804.5 | 706.6 | 765.4 | 768.2 | 788
919 | 729 | 805 | 704.8 | 766.7 | 767.4 | 788.7
920 | 730 | 805.2 | 704.3 | 767.2 | 767.1 | 790
921 | 731 | 805.3 | 703.7 | 767.6 | 767.4 | 789.8
922 | 732 | 805.9 | 701.6 | 766.5 | 765.8 | 789.9
923 | 733 | 806.1 | 704.6 | 761.8 | 766.1 | 791.4
924 | 734 | 805.6 | 702.2 | 752.2 | 763.8 | 791.3
925 | 735 | 804.6 | 703 | 747.8 | 763 | 792.2
926 | 736 | 803.9 | 701.9 | 745.6 | 762.8 | 792.1
927 | 737 | 803.2 | 705.8 | 742.7 | 762.8 | 793.8
928 | 738 | 802.4 | 707.6 | 735.6 | 763.2 | 794.9
929 | 739 | 801.7 | 707.6 | 740.6 | 762.7 | 796.4
930 | 740 | 801.4 | 706.6 | 740.9 | 762 | 797.3
931 | 741 | 800.9 | 710.5 | 741.6 | 762.9 | 798.2
932 | 742 | 800.1 | 714 | 747.8 | 764.8 | 799.1
933 | 743 | 799.4 | 719.2 | 757.7 | 767.6 | 801.2
934 | 744 | 799.3 | 721.3 | 757.4 | 769.6 | 802.3
935 | 745 | 799.8 | 719.5 | 756.7 | 769.8 | 801.4
936 | 746 | 800.1 | 720.8 | 763.5 | 770.9 | 802.8
937 | 747 | 800.2 | 723.1 | 770.3 | 772.8 | 803.1
938 | 748 | 800.6 | 727 | 767.2 | 775 | 804.6
939 | 749 | 800.8 | 732.6 | 762.5 | 777.5 | 805.5
940 | 750 | 800.7 | 735.1 | 765.7 | 779.3 | 805.9
941 | 751 | 800.2 | 735.1 | 771.1 | 780.3 | 805.7
942 | 752 | 800.2 | 732.9 | 775.6 | 780.8 | 807.1
943 | 753 | 800.4 | 732.8 | 771.8 | 781 | 807.5
944 | 754 | 800.3 | 733.3 | 769.7 | 781.3 | 808.2
945 | 755 | 800.1 | 734.5 | 769.4 | 781.9 | 808.5
946 | 756 | 800.3 | 733.5 | 769.4 | 781.2 | 809.2
947 | 757 | 800.5 | 730.7 | 761.4 | 780.4 | 808.7
948 | 758 | 800.8 | 728.6 | 756.7 | 780.3 | 808.7
949 | 759 | 801.1 | 725.4 | 759.2 | 779.6 | 808.1
950 | 760 | 801.7 | 721.1 | 761.1 | 778.6 | 807.6
951 | 761 | 802.3 | 718.1 | 764.7 | 778 | 806.7
952 | 762 | 802.8 | 719.2 | 772.7 | 779.4 | 805.6
953 | 763 | 803.6 | 723 | 776.5 | 782.5 | 805.8
954 | 764 | 804.8 | 723 | 779.1 | 781.7 | 803.6
955 | 765 | 805.5 | 724.4 | 781.6 | 783.5 | 802.1
956 | 766 | 806.1 | 722.6 | 786.1 | 784.6 | 800.4
957 | 767 | 807.1 | 723.1 | 784.6 | 785.6 | 800.2
958 | 768 | 808 | 726 | 783.5 | 786.3 | 800
959 | 769 | 808.2 | 729.6 | 779.8 | 788.3 | 801.5
960 | 770 | 808.5 | 727.5 | 773 | 785.7 | 802
961 | 771 | 808.4 | 720.3 | 757.8 | 780.4 | 801.8
962 | 772 | 807.9 | 722.7 | 753.3 | 779.2 | 803.4
963 | 773 | 807.1 | 722.7 | 753.6 | 779.5 | 804.5
964 | 774 | 806.7 | 724.1 | 758.9 | 780.4 | 805.9
965 | 775 | 806.6 | 726.9 | 761.2 | 782.5 | 805.7
966 | 776 | 806.5 | 727.7 | 762.8 | 783.9 | 806.2
967 | 777 | 806.4 | 725.7 | 759.1 | 783.5 | 805.3
968 | 778 | 806.4 | 721.2 | 749.9 | 779.8 | 805
969 | 779 | 806 | 720 | 750.9 | 778.3 | 805.3
970 | 780 | 805.6 | 724.7 | 751.7 | 780 | 806.5
971 | 781 | 805.3 | 726.6 | 759.9 | 780.4 | 806.7
972 | 782 | 805.1 | 727.4 | 767.6 | 781.5 | 807.7
973 | 783 | 805.1 | 729.5 | 771.9 | 782.7 | 807.9
974 | 784 | 805.6 | 730.6 | 772.9 | 784.5 | 808
975 | 785 | 806.1 | 733.1 | 771.5 | 785.8 | 809.3
976 | 786 | 806.2 | 736.2 | 768.4 | 786.5 | 810.3
977 | 787 | 806.4 | 739.4 | 770.6 | 787.3 | 811.3
978 | 788 | 806.3 | 745 | 776.4 | 790 | 811.3
979 | 789 | 806.6 | 748.4 | 775.9 | 793.4 | 812.3
980 | 790 | 807.1 | 749.4 | 776.3 | 795.8 | 813
981 | 791 | 807.4 | 749.8 | 777.6 | 797.3 | 813.7
982 | 792 | 807.6 | 748.8 | 777.8 | 796.9 | 814.6
983 | 793 | 807.5 | 747.6 | 777.5 | 796.7 | 815.2
984 | 794 | 807.4 | 745.7 | 773 | 795.8 | 814.5
985 | 795 | 807.7 | 738.8 | 768.2 | 792.4 | 814.9
986 | 796 | 807.8 | 738.9 | 767.1 | 791.6 | 815.9
987 | 797 | 807.5 | 739.5 | 764.4 | 790.5 | 817
988 | 798 | 807.1 | 741.5 | 770.5 | 791.1 | 816.6
989 | 799 | 807 | 744 | 772.2 | 792.1 | 816.5
990 | 800 | 807 | 744 | 776.2 | 791.9 | 815.9
991 | 801 | 807 | 746.1 | 778.3 | 792.6 | 816.8
992 | 802 | 806.9 | 750.1 | 781.8 | 794.5 | 818.1
993 | 803 | 806.9 | 750.1 | 783.5 | 794.6 | 819.6
994 | 804 | 807.5 | 749.4 | 785.7 | 796.3 | 818.9
995 | 805 | 808.9 | 747.2 | 789 | 797.2 | 816.8
996 | 806 | 810.2 | 744 | 788.6 | 796.5 | 812.3
997 | 807 | 811.8 | 735.4 | 785.3 | 792.1 | 809.1
998 | 808 | 812.2 | 734.9 | 788 | 791.7 | 807
999 | 809 | 812.5 | 735.8 | 785.2 | 792.4 | 807.7
1000 | 810 | 812.9 | 737.1 | 784.1 | 792.5 | 807.9
1001 | 811 | 813 | 739.8 | 784.3 | 792.4 | 808.3
1002 | 812 | 813 | 743.5 | 783.9 | 794.7 | 809.1
1003 | 813 | 813.2 | 742.8 | 784.6 | 795 | 808.3
1004 | 814 | 813.9 | 740.1 | 787.5 | 794.6 | 805.8
1005 | 815 | 814.4 | 735.1 | 787.9 | 792.5 | 803.2
1006 | 816 | 814.7 | 736.2 | 790.8 | 791.1 | 803
1007 | 817 | 815.4 | 732.5 | 790.3 | 787.7 | 801.2
1008 | 818 | 815.7 | 731.7 | 789.9 | 787 | 801.6
1009 | 819 | 815.8 | 728.1 | 787 | 784.7 | 801.1
1010 | 820 | 815.6 | 725.9 | 784.5 | 783.4 | 801.2
1011 | 821 | 816.1 | 722.9 | 779.4 | 780.9 | 799.7
1012 | 822 | 816.4 | 721.9 | 781.2 | 779.5 | 799.6
1013 | 823 | 816.3 | 727.3 | 785 | 782.2 | 800.6
1014 | 824 | 816.2 | 730.6 | 786.7 | 784.3 | 801.6
1015 | 825 | 816.4 | 722.9 | 785.4 | 779.9 | 797
1016 | 826 | 817.2 | 718.3 | 786.3 | 775.1 | 795.2
1017 | 827 | 817.6 | 720.6 | 787 | 777.4 | 795.8
1018 | 828 | 817.8 | 719.8 | 787.7 | 776.6 | 794.2
1019 | 829 | 817.8 | 723.2 | 790.8 | 779.6 | 794.8
1020 | 830 | 817.8 | 723.2 | 790.1 | 778.6 | 795.7
1021 | 831 | 817.3 | 727.8 | 788.1 | 780.9 | 797.5
1022 | 832 | 816.5 | 728.3 | 780.3 | 781 | 798.6
1023 | 833 | 815.8 | 732.8 | 771.9 | 782.1 | 800
1024 | 834 | 815.4 | 735 | 774 | 782.7 | 800.1
1025 | 835 | 815.1 | 736.4 | 778.1 | 783.4 | 800.7
1026 | 836 | 815.1 | 738.7 | 773.3 | 784.4 | 801.6
1027 | 837 | 814.5 | 742.2 | 775.3 | 785.3 | 802.5
1028 | 838 | 813.3 | 744 | 780.3 | 786.2 | 803.2
1029 | 839 | 812.6 | 745.4 | 782.8 | 787.3 | 804.8
1030 | 840 | 813 | 741.3 | 781.3 | 786.6 | 803.3
1031 | 841 | 814 | 732.3 | 778.2 | 783.5 | 799.9
1032 | 842 | 814.4 | 726.7 | 777.9 | 781.4 | 798.8
1033 | 843 | 814.6 | 722.4 | 779.9 | 779.5 | 796.9
1034 | 844 | 815.1 | 713.6 | 780.3 | 774.5 | 795.6
1035 | 845 | 816 | 709.1 | 779.9 | 770.3 | 793.4
1036 | 846 | 816.3 | 713.1 | 781.8 | 771.6 | 794
1037 | 847 | 816.3 | 716.3 | 779.3 | 773.8 | 794.9
1038 | 848 | 816 | 716 | 774.1 | 773.5 | 796.1
1039 | 849 | 815.3 | 713.5 | 767.5 | 770.9 | 796
1040 | 850 | 814.3 | 709.4 | 758 | 767 | 795.4
1041 | 851 | 813.4 | 706.8 | 752.5 | 763.3 | 796.3
1042 | 852 | 812.5 | 702.8 | 749.8 | 758.9 | 796.8
1043 | 853 | 811.4 | 704 | 744.2 | 757.9 | 796.4
1044 | 854 | 810.2 | 701.1 | 742.6 | 754.5 | 795.4
1045 | 855 | 809 | 704.2 | 743.1 | 755.3 | 797.1
1046 | 856 | 808.3 | 711.2 | 750.1 | 758.1 | 798.8
1047 | 857 | 808.1 | 714.4 | 759.1 | 760.3 | 798.1
1048 | 858 | 807.9 | 718.5 | 761.1 | 762.1 | 799.3
1049 | 859 | 807.1 | 719.9 | 755 | 762.8 | 800
1050 | 860 | 806.5 | 721.1 | 754.6 | 763.4 | 800.7
1051 | 861 | 806.8 | 714.8 | 750.4 | 759.8 | 800.5
1052 | 862 | 807.2 | 713.2 | 749.6 | 758.3 | 801.1
1053 | 863 | 807.4 | 720.5 | 756.9 | 762.4 | 803
1054 | 864 | 807.2 | 729.4 | 763.8 | 767.6 | 803.8
1055 | 865 | 806.9 | 731.7 | 765.8 | 770.8 | 805.3
1056 | 866 | 807.2 | 734.5 | 773.1 | 772.4 | 807.3
1057 | 867 | 806.9 | 739.8 | 774.1 | 774.6 | 807.5
1058 | 868 | 806.9 | 736 | 768.2 | 773.9 | 807.9
1059 | 869 | 806.9 | 735.6 | 768.8 | 774.4 | 808.1
1060 | 870 | 806.5 | 736.7 | 762.5 | 774.6 | 808.9
1061 | 871 | 806.7 | 733.5 | 767.5 | 774.2 | 808.5
1062 | 872 | 807.1 | 734.6 | 772.1 | 774.9 | 808.3
1063 | 873 | 807.5 | 727.3 | 766.3 | 772.7 | 805.5
1064 | 874 | 807.3 | 722.2 | 757.3 | 768.4 | 804.5
1065 | 875 | 806.6 | 720.8 | 753.3 | 766.3 | 804.6
1066 | 876 | 805.2 | 721.7 | 747.3 | 764.3 | 804.2
1067 | 877 | 803.9 | 726.7 | 749.7 | 766.2 | 804.9
1068 | 878 | 803 | 731.7 | 754.3 | 768.6 | 805.6
1069 | 879 | 802.2 | 735.7 | 755.8 | 771.3 | 806.5
1070 | 880 | 801.9 | 738.3 | 757.7 | 772.4 | 807.4
1071 | 881 | 801.9 | 738.1 | 762.5 | 772.9 | 807.7
1072 | 882 | 802.4 | 740.9 | 765.4 | 774.6 | 808.2
1073 | 883 | 803.2 | 744.3 | 772.5 | 777.6 | 808.8
1074 | 884 | 803.7 | 745.8 | 776.9 | 780.5 | 809.6
1075 | 885 | 804.2 | 746.7 | 775.9 | 782 | 810.2
1076 | 886 | 804.2 | 744.5 | 775.9 | 783.1 | 810.4
1077 | 887 | 804.2 | 746.3 | 774.8 | 785.3 | 811.6
1078 | 888 | 804.3 | 749.1 | 770.4 | 786.7 | 812.6
1079 | 889 | 804.2 | 744 | 758.7 | 784 | 813.5
1080 | 890 | 803.4 | 740.6 | 745.9 | 780.5 | 814.7
1081 | 891 | 802.9 | 743.7 | 748.5 | 781.8 | 815.4
1082 | 892 | 803.1 | 744.5 | 756.7 | 783.3 | 814.4
1083 | 893 | 803.5 | 741.6 | 758.8 | 783.8 | 814.1
1084 | 894 | 803.5 | 737.2 | 757.2 | 781.6 | 814
1085 | 895 | 804 | 730.9 | 756.7 | 778.9 | 812.8
1086 | 896 | 804.4 | 720.4 | 752.4 | 772.1 | 810.1
1087 | 897 | 804.3 | 713.9 | 746.4 | 766.2 | 809
1088 | 898 | 804.7 | 716.1 | 752.5 | 765.2 | 808.1
1089 | 899 | 804.6 | 721.3 | 755.6 | 767.7 | 808.1
1090 | 900 | 804.7 | 723.4 | 761.1 | 768.9 | 808.8
1091 | 901 | 805.4 | 723.1 | 771.4 | 769.2 | 807.1
1092 | 902 | 806.2 | 718.8 | 774 | 767.7 | 803.1
1093 | 903 | 806.6 | 713.8 | 767.6 | 764.2 | 800.3
1094 | 904 | 807.1 | 709.8 | 765.2 | 761.3 | 799.2
1095 | 905 | 807.4 | 711.8 | 764.5 | 760.1 | 799.1
1096 | 906 | 807.5 | 713.2 | 768.6 | 761 | 797.4
1097 | 907 | 807.6 | 704.7 | 762.1 | 756.3 | 792.7
1098 | 908 | 807.4 | 693.8 | 754.3 | 749.1 | 787.4
1099 | 909 | 807 | 685.7 | 754.1 | 740.9 | 783.6
1100 | 910 | 806.7 | 684.3 | 754.5 | 737.5 | 782.4
1101 | 911 | 806.2 | 686.5 | 753.2 | 736.4 | 784.1
1102 | 912 | 805.5 | 683.6 | 745.8 | 733.1 | 784.1
1103 | 913 | 804.3 | 683.7 | 735.9 | 730.2 | 784.2
1104 | 914 | 802.7 | 681.8 | 731.2 | 727.6 | 784.5
1105 | 915 | 801.2 | 681.9 | 727.6 | 725.8 | 785.1
1106 | 916 | 800.1 | 689.1 | 735.2 | 726.7 | 786.5
1107 | 917 | 799.5 | 695.3 | 740.9 | 729 | 789
1108 | 918 | 798.7 | 706 | 741.8 | 733.1 | 791
1109 | 919 | 797.8 | 713.3 | 742 | 737.6 | 792.5
1110 | 920 | 797.3 | 719.4 | 749.1 | 741.7 | 793.4
1111 | 921 | 797.1 | 723.9 | 752.7 | 745 | 794
1112 | 922 | 797.1 | 725.2 | 760.6 | 747.2 | 795.4
1113 | 923 | 797.4 | 726.8 | 763.4 | 749.9 | 796.6
1114 | 924 | 798 | 727.8 | 770.1 | 752.1 | 795.4
1115 | 925 | 798.7 | 729.7 | 774.5 | 755.3 | 794.6
1116 | 926 | 799.5 | 731 | 773.3 | 757.3 | 794.9
1117 | 927 | 799.9 | 731 | 776.4 | 759.2 | 795.3
1118 | 928 | 800.7 | 730.8 | 777.9 | 760.2 | 795.5
1119 | 929 | 801.3 | 722 | 774.6 | 758.4 | 791
1120 | 930 | 801.6 | 717.3 | 774.1 | 755.6 | 790
1121 | 931 | 801.4 | 720.6 | 771.9 | 755.8 | 792
1122 | 932 | 800.5 | 721.9 | 761.5 | 756.6 | 792.1
1123 | 933 | 798.9 | 711.1 | 742 | 751.5 | 790
1124 | 934 | 796.9 | 703.7 | 727.8 | 744.9 | 789.4
1125 | 935 | 794.7 | 697.7 | 716.8 | 738.7 | 788.6
1126 | 936 | 792.9 | 696.6 | 717.2 | 734.3 | 788.6
1127 | 937 | 792.5 | 696.2 | 730.4 | 732.5 | 788.3
1128 | 938 | 792.8 | 702.8 | 740.5 | 734.4 | 788.3
1129 | 939 | 793.1 | 710 | 745.6 | 738.5 | 789.4
1130 | 940 | 793.3 | 720 | 749.5 | 743.3 | 790.5
1131 | 941 | 793.2 | 726.7 | 752.9 | 747.1 | 791.2
1132 | 942 | 793.8 | 732.3 | 758.7 | 751.5 | 792.1
1133 | 943 | 794.5 | 734.1 | 763.5 | 754.1 | 792.8
1134 | 944 | 794.5 | 734.2 | 760.2 | 755.1 | 793.6
1135 | 945 | 794.4 | 740.1 | 766 | 756.5 | 794.7
1136 | 946 | 794.7 | 741.9 | 769.6 | 758.9 | 793
1137 | 947 | 795.4 | 736.9 | 765.8 | 759.1 | 792.5
1138 | 948 | 795.9 | 740.2 | 766.1 | 760.9 | 794.2
1139 | 949 | 795.5 | 739.7 | 756.4 | 762.2 | 795.8
1140 | 950 | 794.8 | 738.3 | 753.2 | 761.2 | 796.6
1141 | 951 | 794.5 | 738.4 | 750.4 | 760.8 | 797.4
1142 | 952 | 794.8 | 739.3 | 757.7 | 761.9 | 797.3
1143 | 953 | 795.1 | 744.8 | 762.6 | 765.3 | 798.4
1144 | 954 | 795.1 | 748.2 | 766.1 | 768 | 800.3
1145 | 955 | 795.4 | 747.5 | 773.7 | 769 | 800.9
1146 | 956 | 796.1 | 746 | 778.6 | 769.8 | 801.3
1147 | 957 | 796.7 | 746.7 | 779.3 | 771.7 | 801.1
1148 | 958 | 796.9 | 744.2 | 775.8 | 771.5 | 801.9
1149 | 959 | 796.7 | 744.8 | 770.4 | 771.7 | 802.7
1150 | 960 | 796.2 | 739.2 | 761.8 | 769 | 801.7
1151 | 961 | 795.1 | 733.5 | 754.5 | 765.7 | 801.1
1152 | 962 | 794.4 | 731.6 | 753.7 | 762.9 | 801.8
1153 | 963 | 793.7 | 731.6 | 754.1 | 761.3 | 803.5
1154 | 964 | 793.5 | 734.1 | 762 | 761.8 | 804.5
1155 | 965 | 793.9 | 737 | 765.8 | 764.5 | 803.7
1156 | 966 | 794.6 | 739 | 770.1 | 766.2 | 803.6
1157 | 967 | 795.8 | 734.7 | 771.8 | 766.5 | 802.3
1158 | 968 | 796.6 | 728 | 769.8 | 765 | 800.3
1159 | 969 | 796.4 | 726.7 | 758.8 | 762.7 | 801.5
1160 | 970 | 795.5 | 726.5 | 752.9 | 759.8 | 802.5
1161 | 971 | 794.7 | 729.9 | 754.2 | 758.9 | 802.7
1162 | 972 | 794.6 | 732.6 | 760.7 | 759.3 | 803
1163 | 973 | 794.6 | 736.3 | 759.7 | 760.5 | 804.3
1164 | 974 | 793.7 | 736.2 | 752.3 | 760.2 | 803.8
1165 | 975 | 792 | 728 | 736.6 | 757.1 | 802.8
1166 | 976 | 790 | 722.1 | 727.4 | 752.3 | 801.9
1167 | 977 | 788.6 | 723.6 | 726.7 | 749.2 | 802.1
1168 | 978 | 787.6 | 727.5 | 732.6 | 749.5 | 802.7
1169 | 979 | 786.4 | 730.2 | 728.1 | 749.5 | 802.4
1170 | 980 | 785.9 | 730.3 | 735 | 749.8 | 802.7
1171 | 981 | 786 | 733 | 745.5 | 750.7 | 804.2
1172 | 982 | 786.5 | 734.8 | 748.9 | 753 | 805.3
1173 | 983 | 786.9 | 731.3 | 747.4 | 753.2 | 805.8
1174 | 984 | 786.7 | 721.5 | 740.2 | 750.1 | 803.6
1175 | 985 | 786.5 | 723.1 | 740.3 | 747.9 | 803.2
1176 | 986 | 786.2 | 722.4 | 740.1 | 747.3 | 803.1
1177 | 987 | 785.6 | 722 | 738.8 | 745.6 | 802.5
1178 | 988 | 784.8 | 722 | 729.5 | 744 | 803
1179 | 989 | 783.4 | 718.9 | 720.5 | 741.4 | 803.3
1180 | 990 | 781.9 | 720.2 | 715 | 738.7 | 803
1181 | 991 | 780.9 | 724.7 | 714.5 | 738.5 | 803
1182 | 992 | 781 | 732.3 | 725.3 | 740.8 | 804
1183 | 993 | 781.5 | 733.4 | 729.1 | 742.7 | 804.2
1184 | 994 | 781.6 | 724.4 | 729 | 740.5 | 802.9
1185 | 995 | 781.5 | 716.3 | 728.8 | 737.1 | 800.4
1186 | 996 | 780.9 | 707.8 | 723.5 | 732.6 | 797.1
1187 | 997 | 780.8 | 709.2 | 732.6 | 730.4 | 796.4
1188 | 998 | 781.4 | 716.5 | 740.9 | 732.3 | 797.7
1189 | 999 | 781.6 | 724.3 | 745.2 | 736.8 | 799.8
1190 | 1000 | 781.3 | 727.2 | 745.4 | 739.8 | 800.2
1191 | 1001 | 780.5 | 730 | 738.3 | 742.5 | 800.4
1192 | 1002 | 779.6 | 723.7 | 733.8 | 740.5 | 799.3
1193 | 1003 | 778.9 | 722.6 | 731.1 | 738.1 | 799.9
1194 | 1004 | 778.9 | 723.4 | 737.1 | 737.8 | 799.2
1195 | 1005 | 779 | 717.5 | 738.3 | 736.4 | 797.5
1196 | 1006 | 779.6 | 718.8 | 744.1 | 736.2 | 798.1
1197 | 1007 | 779.9 | 723.3 | 749.2 | 738.4 | 798.6
1198 | 1008 | 780.5 | 729.8 | 753.1 | 741.7 | 799.5
1199 | 1009 | 781.1 | 736.3 | 759.9 | 745.3 | 800.8
1200 | 1010 | 781.4 | 741.1 | 763.7 | 748.9 | 801.3
1201 | 1011 | 781.8 | 745.6 | 767.9 | 753 | 801.6
1202 | 1012 | 782.8 | 749.1 | 770 | 756.5 | 803.5
1203 | 1013 | 783.5 | 752 | 772.3 | 759.6 | 802.2
1204 | 1014 | 784.2 | 755.9 | 775.8 | 762.9 | 802
1205 | 1015 | 785 | 757.7 | 778.2 | 765.8 | 802.2
1206 | 1016 | 785.6 | 760.2 | 779 | 768.7 | 802.1
1207 | 1017 | 786.1 | 761 | 782.4 | 772.1 | 800.8
1208 | 1018 | 787.4 | 756.1 | 780.9 | 773.4 | 799.2
1209 | 1019 | 788.1 | 749.6 | 773.7 | 771.2 | 799.5
1210 | 1020 | 788.3 | 750.8 | 773.6 | 771.1 | 800.3
1211 | 1021 | 788 | 745.5 | 769.2 | 768.8 | 799.3
1212 | 1022 | 787.6 | 733.7 | 757.9 | 762.6 | 795.6
1213 | 1023 | 786.8 | 726.4 | 752.9 | 756 | 794
1214 | 1024 | 786.8 | 723.1 | 752.6 | 753.6 | 794.3
1215 | 1025 | 785.7 | 719.3 | 742.2 | 749.5 | 794.6
1216 | 1026 | 784.9 | 715.9 | 742.9 | 746.3 | 793.8
1217 | 1027 | 784.6 | 710.4 | 743.7 | 742.9 | 792.1
1218 | 1028 | 784.7 | 712.1 | 749.5 | 741.7 | 790.9
1219 | 1029 | 784.8 | 718.9 | 756.3 | 744.1 | 791.7
1220 | 1030 | 785.4 | 725.6 | 763.1 | 747.8 | 791.5
1221 | 1031 | 786.2 | 735 | 767.1 | 752.7 | 792.9
1222 | 1032 | 786.5 | 732.6 | 770.9 | 754 | 789.4
1223 | 1033 | 786 | 733.1 | 763.1 | 754.3 | 790.6
1224 | 1034 | 785.4 | 730.6 | 762.4 | 752.1 | 790.1
1225 | 1035 | 784.4 | 733 | 753.5 | 751.5 | 792.1
1226 | 1036 | 783.1 | 731.9 | 749.4 | 749.8 | 792.1
1227 | 1037 | 782.1 | 734.7 | 752 | 749.2 | 792.8
1228 | 1038 | 781.4 | 739.2 | 754.9 | 751.1 | 794.3
1229 | 1039 | 781.4 | 741.3 | 760.8 | 753.6 | 793.1
1230 | 1040 | 781.9 | 738.1 | 759.7 | 753.3 | 793.7
1231 | 1041 | 782 | 743.3 | 761.8 | 754.4 | 795.3
1232 | 1042 | 782.1 | 741.6 | 762.2 | 754.7 | 794.3
1233 | 1043 | 782.3 | 737.3 | 761.9 | 752.4 | 793.5
1234 | 1044 | 782.5 | 736.1 | 764.9 | 752 | 792.5
1235 | 1045 | 782.6 | 738.1 | 767.4 | 752.6 | 792.8
1236 | 1046 | 782.5 | 738.2 | 764.2 | 752.2 | 792.8
1237 | 1047 | 782.1 | 736.7 | 765 | 751.4 | 792.8
1238 | 1048 | 781.9 | 737.8 | 763.8 | 751.2 | 793
1239 | 1049 | 781.7 | 740.2 | 763.6 | 751.6 | 793.9
1240 | 1050 | 781.2 | 744 | 761.7 | 752.7 | 795.8
1241 | 1051 | 780.9 | 743.6 | 761 | 753.9 | 796.7
1242 | 1052 | 781 | 737.8 | 759.7 | 752.4 | 795.5
1243 | 1053 | 780.9 | 727.5 | 754.4 | 747.3 | 790.8
1244 | 1054 | 780.9 | 724.3 | 756.1 | 744.1 | 789.9
1245 | 1055 | 781 | 728.4 | 760.8 | 744.7 | 790
1246 | 1056 | 780.6 | 734 | 763.3 | 747.5 | 790.9
1247 | 1057 | 780.3 | 737 | 763.6 | 749.8 | 791.8
1248 | 1058 | 780 | 741 | 767.9 | 752.5 | 792.4
1249 | 1059 | 779.9 | 746 | 769.8 | 754.9 | 793.6
1250 | 1060 | 779.5 | 750.8 | 770.7 | 758.1 | 795.4
1251 | 1061 | 778.9 | 754.2 | 770.9 | 761.8 | 796.6
1252 | 1062 | 777.7 | 748.5 | 755.9 | 761.3 | 795.7
1253 | 1063 | 776.4 | 737.9 | 747.7 | 755.7 | 794.2
1254 | 1064 | 775.4 | 737.8 | 746.2 | 752.2 | 794.3
1255 | 1065 | 774.8 | 735.8 | 748.3 | 750.4 | 793.3
1256 | 1066 | 775.1 | 743.8 | 757.6 | 752.6 | 794.8
1257 | 1067 | 775.2 | 749.7 | 763 | 756.4 | 795.8
1258 | 1068 | 775.4 | 754.3 | 766.8 | 761.2 | 797.1
1259 | 1069 | 775.6 | 758.5 | 767.9 | 764.9 | 797.3
1260 | 1070 | 775.7 | 760.5 | 767.1 | 768.2 | 797.4
1261 | 1071 | 775.8 | 761 | 767.4 | 771.1 | 798.9
1262 | 1072 | 776.3 | 764.5 | 769 | 773.6 | 799.5
1263 | 1073 | 777 | 766.6 | 769.5 | 777.5 | 800.3
1264 | 1074 | 777.7 | 766.6 | 770.7 | 780.4 | 800.7
1265 | 1075 | 777.9 | 756.1 | 766.2 | 776.8 | 798.9
1266 | 1076 | 778.1 | 752.4 | 760.1 | 773.7 | 799
1267 | 1077 | 778 | 746.1 | 758.5 | 769.5 | 797.8
1268 | 1078 | 777.4 | 745.7 | 759.8 | 767.2 | 799.1
1269 | 1079 | 776.9 | 743 | 757 | 765.5 | 799.9
1270 | 1080 | 776 | 741.3 | 752.1 | 763.2 | 799.9
1271 | 1081 | 774.9 | 744.1 | 749.9 | 763.3 | 800.1
1272 | 1082 | 774.9 | 746.5 | 754.8 | 765.7 | 800.8
1273 | 1083 | 775.1 | 749.6 | 756.1 | 768.2 | 802.2
1274 | 1084 | 774.9 | 753.5 | 759.1 | 769.9 | 802.8
1275 | 1085 | 774.8 | 750.5 | 760.7 | 770.5 | 802
1276 | 1086 | 774.4 | 751.5 | 759.8 | 771.6 | 803.6
1277 | 1087 | 774.1 | 750.1 | 751.2 | 770.4 | 803.2
1278 | 1088 | 773.5 | 738.6 | 745.2 | 764.5 | 800.5
1279 | 1089 | 773.1 | 739.5 | 747.4 | 760.5 | 801.5
1280 | 1090 | 772.7 | 746.1 | 752.2 | 762.4 | 803.1
1281 | 1091 | 772.9 | 750.9 | 754.5 | 767.1 | 803.9
1282 | 1092 | 772.8 | 750.5 | 754.3 | 768.4 | 804.7
1283 | 1093 | 772.8 | 752.2 | 758.6 | 769.8 | 804.8
1284 | 1094 | 773.3 | 755.9 | 761 | 773.2 | 804
1285 | 1095 | 774 | 756 | 762.5 | 774.3 | 803.8
1286 | 1096 | 774.2 | 748.1 | 759.4 | 771.3 | 802.3
1287 | 1097 | 774.2 | 747.1 | 763.8 | 768.7 | 802.3
1288 | 1098 | 774 | 749.4 | 766.8 | 769.7 | 802.8
1289 | 1099 | 774 | 751 | 768.6 | 770.7 | 803.3
1290 | 1100 | 774.1 | 756.1 | 770.4 | 773.3 | 803.6
1291 | 1101 | 774.4 | 759.4 | 773.2 | 775.1 | 802.1
1292 | 1102 | 774.7 | 758.5 | 770.1 | 776.1 | 801.9
1293 | 1103 | 775.1 | 756.1 | 763.2 | 774.6 | 801.3
1294 | 1104 | 775.4 | 754.7 | 765.6 | 774 | 800.1
1295 | 1105 | 775.3 | 753.2 | 767.5 | 773.5 | 799.7
1296 | 1106 | 775.1 | 758 | 771.5 | 775.7 | 798.3
1297 | 1107 | 775 | 760.2 | 775.5 | 777.4 | 799.3
1298 | 1108 | 775.1 | 756.2 | 775 | 776.9 | 799.7
1299 | 1109 | 775.4 | 749.4 | 774.1 | 773 | 798.8
1300 | 1110 | 775.6 | 749.2 | 776.1 | 770.3 | 799.9
1301 | 1111 | 775.8 | 748.7 | 778 | 769.3 | 798.6
1302 | 1112 | 775.9 | 746.6 | 776.7 | 768.2 | 798.1
1303 | 1113 | 775.8 | 742.2 | 777.8 | 766.5 | 794.4
1304 | 1114 | 775.7 | 742 | 775.1 | 765.2 | 795.2
1305 | 1115 | 775.1 | 744 | 767.8 | 764.6 | 795.7
1306 | 1116 | 774.2 | 747.9 | 765.6 | 765.4 | 796.1
1307 | 1117 | 773.7 | 751.2 | 770.3 | 766.7 | 796.8
1308 | 1118 | 773.4 | 756.5 | 770.4 | 769.2 | 797.8
1309 | 1119 | 773.6 | 762.7 | 772.5 | 773 | 798.1
1310 | 1120 | 774.2 | 765.7 | 773.4 | 776.1 | 798.9
1311 | 1121 | 774.4 | 766.9 | 772.7 | 778 | 799.3
1312 | 1122 | 774.5 | 770.4 | 770.7 | 778.8 | 800.2
1313 | 1123 | 774.6 | 771.9 | 763.4 | 780.8 | 801.1
1314 | 1124 | 774.8 | 772.9 | 763.9 | 782 | 802.4
1315 | 1125 | 774.4 | 770.2 | 757.7 | 779.1 | 803.9
1316 | 1126 | 773.9 | 770.3 | 757.9 | 779.5 | 805
1317 | 1127 | 774 | 771.9 | 763.2 | 780.9 | 804.8
1318 | 1128 | 773.9 | 774.3 | 767.1 | 782.5 | 805.2
1319 | 1129 | 773.9 | 773.3 | 764.3 | 784.2 | 805.6
1320 | 1130 | 773.8 | 772.6 | 766.2 | 785.3 | 806.8
1321 | 1131 | 773.9 | 774.8 | 771 | 787.1 | 807.3
1322 | 1132 | 774 | 774.8 | 775.3 | 787.4 | 807.7
1323 | 1133 | 774 | 773.3 | 777.6 | 787.3 | 808.3
1324 | 1134 | 773.8 | 766.7 | 767.2 | 784.5 | 805.9
1325 | 1135 | 771.8 | 739.7 | 737.9 | 770.5 | 799.7
1326 | 1136 | 768.7 | 713.2 | 715 | 753.1 | 795
1327 | 1137 | 765.7 | 687.4 | 695.2 | 736.1 | 789.7
1328 | 1138 | 762.7 | 664.7 | 678.4 | 719.7 | 783.2
1329 | 1139 | 759.6 | 646.9 | 662.1 | 704.8 | 776.6
1330 | 1140 | 756.5 | 631.1 | 648 | 690.1 | 769.1
1331 | 1141 | 753.5 | 614.5 | 634.8 | 674.8 | 755.7
1332 | 1142 | 750.6 | 601 | 623.9 | 660.4 | 747.8
1333 | 1143 | 747.8 | 587.2 | 613.7 | 647.8 | 739.6
1334 | 1144 | 745.2 | 575.6 | 603.9 | 636.6 | 732.3
1335 | 1145 | 742.6 | 564.8 | 595.5 | 625 | 725.3
1336 | 1146 | 740 | 554.7 | 587.3 | 614.4 | 718.7
1337 | 1147 | 737.4 | 545.1 | 580 | 604.1 | 711.8
1338 | 1148 | 734.7 | 533.9 | 573 | 594.2 | 705.6
1339 | 1149 | 732.3 | 522.5 | 567.9 | 582.8 | 699.2
1340 | 1150 | 729.9 | 512.8 | 563.5 | 574.4 | 692.5
1341 | 1151 | 727.5 | 504.2 | 557.3 | 567.7 | 686.2
1342 | 1152 | 725.2 | 495.4 | 551.2 | 559.3 | 680.7
1343 | 1153 | 722.9 | 487.6 | 547.1 | 550.9 | 674.7
1344 | 1154 | 720.6 | 480.7 | 543.6 | 541.9 | 668.7
1345 | 1155 | 718.4 | 474 | 539.4 | 534.5 | 663.9
1346 | 1156 | 716.1 | 468.4 | 534.9 | 527.6 | 658.7
1347 | 1157 | 713.8 | 463.3 | 532 | 520.7 | 653.5
1348 | 1158 | 711.5 | 458.2 | 529.4 | 512.7 | 648.4
1349 | 1159 | 709.4 | 453.3 | 526.1 | 505.8 | 643.1
1350 | 1160 | 707.2 | 448.4 | 521.3 | 501.4 | 638
1351 | 1161 | 704.9 | 444.1 | 515.9 | 499.4 | 634.2
1352 | 1162 | 702.9 | 439.6 | 510.5 | 496.4 | 629.7
1353 | 1163 | 700.9 | 435.7 | 505.9 | 492.7 | 625.8
1354 | 1164 | 698.9 | 433.2 | 501.3 | 489.9 | 621.3
1355 | 1165 | 696.9 | 429.8 | 497.4 | 487 | 617
1356 | 1166 | 694.9 | 426.3 | 493.8 | 482.6 | 612.6
1357 | 1167 | 692.8 | 421.6 | 490.9 | 476 | 608.5
1358 | 1168 | 690.8 | 417.8 | 487.4 | 470.3 | 604.4
1359 | 1169 | 688.8 | 413.3 | 484.4 | 464.9 | 599.6
1360 | 1170 | 686.7 | 410.9 | 480.3 | 462.9 | 595.4
1361 | 1171 | 684.6 | 407.6 | 476.6 | 459.5 | 592.1
1362 | 1172 | 682.7 | 404.7 | 473.6 | 456.2 | 588.2
1363 | 1173 | 680.6 | 401.1 | 471.8 | 452.4 | 584.8
1364 | 1174 | 678.5 | 397.6 | 470.5 | 447.8 | 581
1365 | 1175 | 676.5 | 394.1 | 468.7 | 444.2 | 576.9
1366 | 1176 | 674.6 | 391.7 | 465.1 | 440.6 | 573.8
1367 | 1177 | 672.8 | 389.2 | 461.1 | 437.2 | 570.9
1368 | 1178 | 671 | 386.9 | 457.4 | 435.4 | 567.6
1369 | 1179 | 669.2 | 385.3 | 453.6 | 434.4 | 564.7
1370 | 1180 | 667.3 | 383.5 | 450.4 | 433.5 | 561.4
1371 | 1181 | 665.5 | 381.9 | 447.6 | 431.9 | 558.4
1372 | 1182 | 663.7 | 381.2 | 445.5 | 431.1 | 555.4
1373 | 1183 | 662 | 380.7 | 443.8 | 430.8 | 553.1
1374 | 1184 | 660.2 | 379.1 | 442.5 | 430 | 550.4
1375 | 1185 | 658.1 | 376.8 | 440.7 | 427.5 | 547.6
1376 | 1186 | 656.2 | 374.1 | 437.5 | 422.5 | 544.4
1377 | 1187 | 654.2 | 371.7 | 435.1 | 417.4 | 540.5
1378 | 1188 | 652.3 | 368.4 | 432.5 | 412.4 | 537.2
1379 | 1189 | 650.5 | 364.7 | 430.5 | 408 | 534.6
1380 | 1190 | 648.5 | 361.7 | 429.1 | 404.6 | 531.6
1381 | 1191 | 646.5 | 358.3 | 428.2 | 401 | 528.9
1382 | 1192 | 644.7 | 354.7 | 426.9 | 396.8 | 525.6
1383 | 1193 | 642.9 | 352.1 | 424.7 | 393.8 | 522.6
1384 | 1194 | 641.3 | 349.9 | 422.4 | 391.9 | 520.3
1385 | 1195 | 639.5 | 347.3 | 420.8 | 389.4 | 517.4
1386 | 1196 | 637.7 | 344.6 | 419.4 | 386.2 | 514.6
1387 | 1197 | 636 | 342.1 | 417.5 | 382.8 | 512
1388 | 1198 | 634.2 | 340.4 | 415.8 | 379.8 | 509.2
1389 | 1199 | 632.4 | 338.6 | 414.1 | 377.6 | 506.6
1390 | 1200 | 630.8 | 336.6 | 411.8 | 376 | 504.4
1391 | 1201 | 629.2 | 335.7 | 409 | 375.1 | 502.7
1392 | 1202 | 627.7 | 333.5 | 407.2 | 372.1 | 500.4
1393 | 1203 | 626.2 | 331.6 | 405 | 369.4 | 497.9
1394 | 1204 | 624.7 | 329.1 | 402.4 | 367.3 | 495.8
1395 | 1205 | 623.1 | 326.6 | 400.7 | 365.1 | 493.6
1396 | 1206 | 621.5 | 325 | 399 | 363.1 | 491.4
1397 | 1207 | 620 | 322.9 | 396.5 | 361.4 | 488.7
1398 | 1208 | 618.5 | 321.1 | 394.1 | 359.2 | 486.4
1399 | 1209 | 617 | 319.5 | 392.4 | 357.1 | 484
1400 | 1210 | 615.4 | 318.3 | 390.3 | 354.8 | 481.5
1401 | 1211 | 613.7 | 317.4 | 389.4 | 353.2 | 479.6
1402 | 1212 | 611.8 | 318 | 387 | 352.7 | 477.9
1403 | 1213 | 609.9 | 318.1 | 384.9 | 352.3 | 476
1404 | 1214 | 608.1 | 316.7 | 383.5 | 351.3 | 474
1405 | 1215 | 606.4 | 317.7 | 381.5 | 351.9 | 472.5
1406 | 1216 | 604.8 | 316.1 | 380.6 | 350.5 | 470.6
1407 | 1217 | 603.2 | 315.4 | 378.9 | 348.9 | 468.3
1408 | 1218 | 601.7 | 314.8 | 376.4 | 348.3 | 466.6
1409 | 1219 | 600.3 | 314.5 | 374.2 | 348.1 | 464.8
1410 | 1220 | 598.6 | 312.9 | 372.8 | 346.1 | 463.3
1411 | 1221 | 597 | 310.9 | 371.2 | 343.6 | 461
1412 | 1222 | 595.3 | 308.6 | 369.3 | 341.6 | 459.2
1413 | 1223 | 593.5 | 308.9 | 367.3 | 341.9 | 457.4
1414 | 1224 | 591.8 | 308.1 | 365.8 | 341.3 | 455.9
1415 | 1225 | 590.2 | 307.9 | 363.7 | 341.4 | 454.4
1416 | 1226 | 588.9 | 308.1 | 362 | 341.9 | 452.9
1417 | 1227 | 587.1 | 307.9 | 361.2 | 340.9 | 451.3
1418 | 1228 | 585.4 | 306.8 | 359.6 | 339.3 | 449.6
1419 | 1229 | 583.9 | 306.4 | 357.5 | 338.8 | 447.9
1420 | 1230 | 582.5 | 305.8 | 355.2 | 337.8 | 446.2
1421 | 1231 | 581.3 | 305.4 | 353.3 | 337.6 | 445.1
1422 | 1232 | 580.1 | 305.6 | 351.2 | 337.2 | 444
1423 | 1233 | 578.7 | 305.7 | 349.4 | 336.7 | 442.7
1424 | 1234 | 576.9 | 305.3 | 347.9 | 335.1 | 440.9
1425 | 1235 | 575.1 | 303.8 | 346.6 | 333 | 439
1426 | 1236 | 573.3 | 301.9 | 345.3 | 330.6 | 437.3
1427 | 1237 | 571.7 | 299.7 | 343.5 | 327.4 | 435.3
1428 | 1238 | 570.1 | 297.5 | 342.1 | 325.5 | 433.5
1429 | 1239 | 568.3 | 295.9 | 341.1 | 323.9 | 431.9
1430 | 1240 | 566.7 | 293.2 | 339.4 | 321.2 | 430.1
1431 | 1241 | 565 | 292.5 | 338 | 319.7 | 428.2
1432 | 1242 | 563.4 | 291.4 | 336.3 | 318.4 | 426.5
1433 | 1243 | 561.9 | 291.1 | 334.3 | 318.8 | 425.1
1434 | 1244 | 560.5 | 289.4 | 332.8 | 317.2 | 423.9
1435 | 1245 | 559 | 287.5 | 331.2 | 315.1 | 422
1436 | 1246 | 557.4 | 287 | 329.4 | 314.2 | 420.8
1437 | 1247 | 556 | 285.6 | 328 | 312.1 | 419.4
1438 | 1248 | 554.7 | 284.3 | 326.2 | 310.4 | 418
1439 | 1249 | 553.4 | 282.7 | 324.2 | 308.8 | 416.3
1440 | 1250 | 552 | 281.3 | 322.8 | 307.6 | 414.8
1441 | 1251 | 550.6 | 279.7 | 321.2 | 306 | 413.1
1442 | 1252 | 549.2 | 277.9 | 319.7 | 304.5 | 411.8
1443 | 1253 | 547.9 | 277.1 | 317.8 | 304.1 | 410.5
1444 | 1254 | 546.6 | 276.6 | 316 | 303.1 | 409
1445 | 1255 | 545.1 | 277.3 | 313.9 | 302.5 | 407.3
1446 | 1256 | 543.5 | 276 | 312.3 | 301.7 | 405.9
1447 | 1257 | 541.7 | 275.7 | 310.7 | 301.2 | 404.7
1448 | 1258 | 540.1 | 274.8 | 309.1 | 300.3 | 403.6
1449 | 1259 | 538.6 | 274.5 | 307.1 | 299.7 | 402.4
1450 | 1260 | 537 | 274.4 | 305.7 | 299.5 | 400.6
1451 | 1261 | 535.4 | 274.2 | 304.6 | 298.6 | 399.4
1452 | 1262 | 533.7 | 273.8 | 302.8 | 297.8 | 398
1453 | 1263 | 532.1 | 272.8 | 301.9 | 295.8 | 396.4
1454 | 1264 | 530.5 | 271.1 | 301.1 | 293.3 | 394.9
1455 | 1265 | 529 | 270 | 299.9 | 291.4 | 393.5
1456 | 1266 | 527.4 | 269.7 | 298 | 290.8 | 392.2
1457 | 1267 | 525.9 | 268.3 | 296.6 | 289.3 | 391
1458 | 1268 | 524.4 | 267.5 | 294.8 | 287.8 | 389.9
1459 | 1269 | 522.9 | 267.1 | 292.9 | 287.5 | 388.6
1460 | 1270 | 521.4 | 265.6 | 290.9 | 286.5 | 387.2
1461 | 1271 | 519.9 | 264.8 | 289.1 | 285.6 | 385.8
1462 | 1272 | 518.6 | 262.7 | 287.2 | 283.6 | 384.1
1463 | 1273 | 517.2 | 261.2 | 285.2 | 282.1 | 382.7
1464 | 1274 | 515.9 | 260.1 | 283.7 | 280.9 | 381.2
1465 | 1275 | 514.6 | 259 | 282.2 | 279.4 | 379.9
1466 | 1276 | 513.2 | 257.4 | 279.9 | 278 | 378.3
1467 | 1277 | 511.9 | 256.1 | 278.2 | 276.4 | 377.1
1468 | 1278 | 510.6 | 254.4 | 276.1 | 274.8 | 375.7
1469 | 1279 | 509.2 | 252.9 | 274.3 | 273.4 | 374.1
1470 | 1280 | 507.8 | 251.9 | 272.5 | 272.3 | 372.6
1471 | 1281 | 506.4 | 251.3 | 270.9 | 271.6 | 371.3
1472 | 1282 | 505 | 249.6 | 269.5 | 270 | 369.8
1473 | 1283 | 503.6 | 248 | 268 | 269.3 | 368.5
1474 | 1284 | 502.2 | 247.1 | 266.6 | 268.6 | 367.5
1475 | 1285 | 500.8 | 247.5 | 265.3 | 268.7 | 366.6
1476 | 1286 | 499.6 | 246.5 | 263.7 | 267.2 | 365.3
1477 | 1287 | 498.3 | 245.5 | 262 | 266 | 364.1
1478 | 1288 | 497 | 245 | 260.5 | 266 | 363.4
1479 | 1289 | 495.5 | 244.6 | 259.4 | 265.8 | 361.9
1480 | 1290 | 494.2 | 243.5 | 258 | 264.5 | 360.7
1481 | 1291 | 492.8 | 243.2 | 256.7 | 263.7 | 359.5
1482 | 1292 | 491.5 | 242 | 255.9 | 262.7 | 358.4
1483 | 1293 | 490.2 | 241.7 | 255.1 | 262 | 357.2
1484 | 1294 | 489 | 241.4 | 253.7 | 261.7 | 355.9
1485 | 1295 | 487.7 | 240.5 | 252.5 | 261 | 354.7
1486 | 1296 | 486.3 | 240.7 | 251.6 | 260.6 | 353.7
1487 | 1297 | 484.9 | 240.7 | 250.5 | 259.7 | 352.8
1488 | 1298 | 483.7 | 240.3 | 249.1 | 258.5 | 351.8
1489 | 1299 | 482.3 | 240.2 | 248.3 | 258 | 350.5
1490 | 1300 | 480.8 | 239.5 | 247.3 | 257.2 | 349.6
1491 | 1301 | 479.3 | 238.6 | 246.4 | 255.7 | 348.7
1492 | 1302 | 478 | 239 | 244.9 | 255.5 | 347.4
1493 | 1303 | 476.6 | 238.8 | 243.9 | 255.1 | 346.7
1494 | 1304 | 475.2 | 238.4 | 242.6 | 255 | 345.6
1495 | 1305 | 473.9 | 238.5 | 241.2 | 254.9 | 344.9
1496 | 1306 | 472.7 | 238.6 | 239.6 | 254.6 | 344
1497 | 1307 | 471.5 | 238.6 | 238.4 | 254.2 | 342.8
1498 | 1308 | 470.1 | 237.6 | 237.3 | 252.9 | 341.7
1499 | 1309 | 468.7 | 237.2 | 235.4 | 252.9 | 340.6
1500 | 1310 | 467.3 | 235.9 | 234.1 | 252 | 339.6
1501 | 1311 | 466 | 234.5 | 233.4 | 250.8 | 338.4
1502 | 1312 | 464.7 | 234.2 | 232.6 | 250.1 | 337.7
1503 | 1313 | 463.2 | 234.2 | 231.4 | 249.6 | 336.6
1504 | 1314 | 461.8 | 233.3 | 229.6 | 248.6 | 335.4
1505 | 1315 | 460.5 | 232.1 | 228.1 | 247.6 | 334.4
1506 | 1316 | 459.1 | 230.7 | 226.9 | 245.9 | 333.4
1507 | 1317 | 457.7 | 230.5 | 226.1 | 245.6 | 332.2
1508 | 1318 | 456.3 | 229.8 | 225 | 245.4 | 331.1
1509 | 1319 | 455.1 | 229.1 | 223.6 | 245.1 | 330.3
1510 | 1320 | 453.9 | 228.3 | 222 | 244.3 | 329.2
1511 | 1321 | 452.8 | 227.6 | 219.4 | 243.9 | 328.2
1512 | 1322 | 451.7 | 226.7 | 218.8 | 243.5 | 327.2
1513 | 1323 | 450.4 | 226 | 217.6 | 243.7 | 326.4
1514 | 1324 | 449.2 | 225.7 | 217 | 243.2 | 325.3
1515 | 1325 | 447.9 | 224.5 | 216 | 241.3 | 323.9
1516 | 1326 | 446.6 | 223.9 | 215 | 240.2 | 322.8
1517 | 1327 | 445.4 | 223.8 | 214.6 | 239.4 | 322.2
1518 | 1328 | 444 | 223.8 | 214.2 | 238.9 | 321.1
1519 | 1329 | 442.6 | 223.1 | 213.8 | 238.2 | 320.4
1520 | 1330 | 441.3 | 221.9 | 212.7 | 236.5 | 319.6
1521 | 1331 | 440 | 221.2 | 211.9 | 235.1 | 318.6
1522 | 1332 | 438.8 | 220.9 | 210.6 | 234.8 | 317.8
1523 | 1333 | 437.6 | 220.8 | 209.4 | 234.1 | 316.9
1524 | 1334 | 436.4 | 220.6 | 208.8 | 233.7 | 316.3
1525 | 1335 | 435.3 | 220.3 | 207.8 | 233.5 | 315.7
1526 | 1336 | 434.3 | 219.9 | 207 | 232.8 | 314.9
1527 | 1337 | 433.3 | 219.6 | 205.7 | 232.5 | 314.2
1528 | 1338 | 432.2 | 220 | 204.7 | 232.6 | 313.6
1529 | 1339 | 431.1 | 221 | 203.6 | 233.4 | 312.9
1530 | 1340 | 430.1 | 221.7 | 203.1 | 234.1 | 312.4
1531 | 1341 | 429 | 221.5 | 203.1 | 234.1 | 312
1532 | 1342 | 427.7 | 222.2 | 202 | 234.2 | 311.2
1533 | 1343 | 426.7 | 221.7 | 200.6 | 233.2 | 310
1534 | 1344 | 425.6 | 221.8 | 199.3 | 233.7 | 309.2
1535 | 1345 | 424.4 | 221.3 | 198.7 | 233.1 | 308.4
1536 | 1346 | 423.3 | 221.1 | 197.6 | 233.3 | 307.7
1537 | 1347 | 422.2 | 221.3 | 196.6 | 233.8 | 307.2
1538 | 1348 | 421.2 | 222.3 | 196.3 | 234.6 | 306.5
1539 | 1349 | 420.1 | 222.5 | 195.4 | 235.1 | 305.7
1540 | 1350 | 418.9 | 222.5 | 194.4 | 235 | 305.1
1541 | 1351 | 417.8 | 221.2 | 193.6 | 232.9 | 304.4
1542 | 1352 | 416.8 | 219.7 | 193 | 231.1 | 303.4
1543 | 1353 | 415.8 | 218.4 | 192.6 | 229.7 | 302.8
1544 | 1354 | 414.7 | 218.1 | 192.1 | 229.8 | 302.2
1545 | 1355 | 413.6 | 218.1 | 191.3 | 230 | 301.5
1546 | 1356 | 412.5 | 217.9 | 190.5 | 229.9 | 300.8
1547 | 1357 | 411.5 | 218.9 | 190.1 | 230.5 | 300.3
1548 | 1358 | 410.4 | 219.7 | 189.2 | 231 | 299.7
1549 | 1359 | 409.1 | 220.1 | 188.6 | 231.5 | 299.1
1550 | 1360 | 407.8 | 219.4 | 188 | 231.2 | 298.3
1551 | 1361 | 406.5 | 218.8 | 187.4 | 230.8 | 297.1
1552 | 1362 | 405.1 | 218.5 | 186.6 | 231.4 | 296.6
1553 | 1363 | 403.9 | 218 | 186 | 230.9 | 296
1554 | 1364 | 402.7 | 216.3 | 185.5 | 229.4 | 295
1555 | 1365 | 401.7 | 215.7 | 184.6 | 229.3 | 294.5
1556 | 1366 | 400.5 | 215.4 | 183.3 | 229.6 | 293.9
1557 | 1367 | 399.5 | 215.5 | 182.5 | 229.8 | 293.1
1558 | 1368 | 398.4 | 215.6 | 181.7 | 230.1 | 292.5
1559 | 1369 | 397.3 | 216.2 | 180.8 | 230.8 | 292.1
1560 | 1370 | 396.2 | 216.9 | 180.2 | 231.4 | 291.6
1561 | 1371 | 394.9 | 217.5 | 179.9 | 231.7 | 290.9
1562 | 1372 | 393.8 | 217.8 | 179.3 | 231.6 | 290.2
1563 | 1373 | 392.9 | 217.7 | 179.2 | 231.6 | 289.8
1564 | 1374 | 391.9 | 217.5 | 178.8 | 231.5 | 289.1
1565 | 1375 | 390.8 | 217.6 | 178 | 231.4 | 288.5
1566 | 1376 | 389.7 | 217.5 | 177.1 | 231.4 | 288
1567 | 1377 | 388.8 | 216.8 | 176.3 | 230.8 | 287.4
1568 | 1378 | 387.6 | 216.6 | 176 | 230.8 | 286.9
1569 | 1379 | 386.4 | 216.3 | 175.6 | 230.6 | 286.1
1570 | 1380 | 385.2 | 216.4 | 174.9 | 230.9 | 285.3
1571 | 1381 | 384.2 | 215.9 | 174.2 | 230.3 | 284.8
1572 | 1382 | 383.3 | 215.2 | 173.9 | 229.3 | 284.1
1573 | 1383 | 382.4 | 214.8 | 173 | 229 | 283.5
1574 | 1384 | 381.7 | 214.7 | 173 | 229.3 | 283.1
1575 | 1385 | 381.1 | 214.1 | 172.8 | 229.5 | 282.6
1576 | 1386 | 380.5 | 213.4 | 172.8 | 229.7 | 282.1
1577 | 1387 | 379.9 | 213.1 | 172.6 | 229.8 | 281.7
1578 | 1388 | 379.2 | 213.1 | 172.2 | 229.9 | 281.2
1579 | 1389 | 378.6 | 213.4 | 171.4 | 229.4 | 280.4
1580 | 1390 | 377.8 | 212.8 | 170.8 | 227.9 | 279.6
1581 | 1391 | 377 | 211.9 | 170.2 | 227.2 | 278.9
1582 | 1392 | 376.2 | 212.1 | 169.9 | 227.2 | 278.1
1583 | 1393 | 375.4 | 211.8 | 169.3 | 226.9 | 277.7
1584 | 1394 | 374.4 | 211.5 | 169.2 | 226.7 | 277.2
1585 | 1395 | 373.3 | 210.7 | 169.5 | 226.3 | 276.2
1586 | 1396 | 372.2 | 210.3 | 169 | 226.2 | 275.8
1587 | 1397 | 371.2 | 210.2 | 169.3 | 226 | 275.2
1588 | 1398 | 370.4 | 210.3 | 168.8 | 225.8 | 274.6
1589 | 1399 | 369.5 | 210 | 168.6 | 225 | 273.9
1590 | 1400 | 368.5 | 209.2 | 168.2 | 224.1 | 273.1
1591 | 1401 | 367.5 | 208.5 | 168 | 222.9 | 272.4
1592 | 1402 | 366.5 | 207.8 | 167.3 | 222.4 | 271.9
1593 | 1403 | 365.6 | 206.9 | 166.7 | 221.9 | 271.2
1594 | 1404 | 364.8 | 206.5 | 165.8 | 221.9 | 270.8
1595 | 1405 | 364 | 206.1 | 165.4 | 221.4 | 270.1
1596 | 1406 | 363.2 | 205.8 | 165.6 | 221.3 | 269.7
1597 | 1407 | 362.4 | 206.2 | 164.9 | 221 | 269.3
1598 | 1408 | 361.6 | 206.6 | 164.4 | 221.1 | 268.8
1599 | 1409 | 360.7 | 206.7 | 163.7 | 221.3 | 268.5
1600 | 1410 | 359.8 | 206.8 | 163.2 | 221 | 268.2
1601 | 1411 | 359 | 206.1 | 163 | 220.7 | 267.8
1602 | 1412 | 358.2 | 206.1 | 162.7 | 220.7 | 267.5
1603 | 1413 | 357.3 | 205.9 | 162.4 | 220.3 | 266.6
1604 | 1414 | 356.3 | 205.1 | 162.2 | 219.8 | 265.7
1605 | 1415 | 355.5 | 204.8 | 161.8 | 219.2 | 265.1
1606 | 1416 | 354.6 | 205.1 | 161.7 | 218.8 | 264.5
1607 | 1417 | 353.9 | 205.2 | 161.4 | 218.5 | 264
1608 | 1418 | 353.2 | 204.9 | 160.8 | 218.1 | 263.5
1609 | 1419 | 352.5 | 205.1 | 160.2 | 218.2 | 263.2
1610 | 1420 | 351.7 | 205.2 | 159.8 | 218.4 | 262.8
1611 | 1421 | 351 | 204.7 | 159.2 | 217.6 | 262.1
1612 | 1422 | 350.3 | 204 | 158.4 | 217.2 | 261.4
1613 | 1423 | 349.4 | 203.7 | 157.9 | 217.2 | 261
1614 | 1424 | 348.8 | 204 | 157.6 | 217 | 260.7
1615 | 1425 | 348 | 204.2 | 157.3 | 217.1 | 260.2
1616 | 1426 | 347.3 | 204.2 | 157.2 | 217.2 | 259.7
1617 | 1427 | 346.5 | 204.6 | 157.5 | 217.3 | 259.3

## Test Facts
Last row in IRMS data sheets: | 43
Time when gas burner was ignited: | 190