## IS Test Matrix
Intermediate Scale Test Matrix - Revision F (12-06-06)
|  | Comments: 1) All tests were conducted as open burns with a Propene (Propylene) gas sand burner 2) Colors identify test conditions grouped into the same test run | [14 empty] | ACTUAL TEST CONDITIONS
Burn Test # | Rev. E Test # | Loc. | Cable Insulation Material | [8 empty] | Number of Conductors |  |  |  | Conductor Size (AWG) |  |  |  |  | Cable Bundle Size |  |  |  |  | Water Spary Optionsl | Raceway Type
|  |  | Thermoset | [5 empty] | Thermoplastic
|  |  | XLPE | EPR | Silicone | XLPO | TS/TP | Vita-Link | PE | PVC | Tefzel | 3 | 2 | 7 | 12 | 8 | 12 | 14 | 16 | 18 | 1 | 3 | 6 | 12 | Load Tr | * | 12" Tray | 2.5" Cnd | Air Drop
Prelim 1 | Prelim 1 | A | X | [8 empty] | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | A | X | [10 empty] | X |  |  | X |  |  |  | X | [5 empty] | X
Prelim 2 | Prelim 2 | A | X | [8 empty] | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | A | X | [10 empty] | X |  |  | X |  |  |  | X | [5 empty] | X
Prelim 3 | Prelim 3 | A | [7 empty] | X |  | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | A | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [5 empty] | X
Prelim 4 | Prelim 4 | A | [7 empty] | X |  | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | A | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [5 empty] | X
1 | 15 | A | X | [9 empty] | X | X | X |  | X |  | X | X |  |  |  |  | X |  | X
|  | B | X | [10 empty] | X |  |  | X | [6 empty] | X |  |  | X
|  | D | X | [10 empty] | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | E | X | [10 empty] | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | [10 empty] | X |  |  | X | [6 empty] | X |  |  | X
2 | 1 | A | X | [10 empty] | X |  |  | X | [6 empty] | X |  |  | X
|  | C | X | [10 empty] | X |  |  | X | [5 empty] | X |  |  |  | X
|  | A | X | [5 empty] | X |  |  |  |  | X |  |  | X | [6 empty] | X |  |  | X
|  | C | X | [5 empty] | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
| 11 | C - A | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [7 empty] | X
|  | E | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [5 empty] | X
|  | G | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [5 empty] | X
3 | 2 | A | X | X | [9 empty] | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X | [9 empty] | X |  |  | X | [5 empty] | X |  |  |  | X
| 3 | A |  | X |  |  |  |  | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C |  | X |  |  |  |  | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
| 10 | E | [7 empty] | X |  | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | [7 empty] | X |  | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
4 | 5 | A | X | X |  | X | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X |  | X | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
| 6 | A | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
| 9 | C - A | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [7 empty] | X
|  | E | X | [8 empty] | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | [8 empty] | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
5 | 4 | A | X | X | X | X |  |  | X |  | X |  |  | X |  |  | X | [6 empty] | X |  | X | X
|  | C | X | X | X | X |  |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
| 7 | A | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | X | [5 empty] | X |  | X | X
|  | C | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | X |  |  |  |  | X |  |  | X | X
|  | C - A | X | [10 empty] | X |  |  | X |  |  |  | X | [7 empty] | X
|  | E |  | X | [9 empty] | X |  |  | X |  |  |  | X | [5 empty] | X
|  | G |  | X | [9 empty] | X |  |  | X |  |  |  | X | [5 empty] | X
6 | 12 | A | X | X | X | X |  |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | C | X | X | X | X |  |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | E | X | [5 empty] | X |  | X |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
| 13 | C - A | X | [5 empty] | X |  | X |  |  | X |  |  | X |  |  |  |  | X | [6 empty] | X
|  | A |  | X | X | X | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | C |  | X | X | X | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | G |  |  |  |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  |  |  | X
7 | 14 | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | A | X | X |  | X | X |  |  | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C |  | X |  | X | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | E | X | [5 empty] | X | X |  |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G |  | X |  | X | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
8 | 16 | A | X | [5 empty] | X | X |  |  | X | X | X |  | X |  | X | X |  |  | X |  |  |  | X
|  | A | X | [5 empty] | X | X |  |  | X | X | X |  | X |  | X | X |  |  | X |  |  |  | X
|  | C | X | [5 empty] | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | E | X | [5 empty] | X |  |  |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | [5 empty] | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
9 | 19 | A | X | X | X |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | A | X | X | X |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | C | X | X | X |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | E | X | [5 empty] | X |  | X |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | X | X |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
10 | 20 | A | X | X | X | X | X |  |  |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | A | X | X | X | X | X |  |  |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | C | X | X | X | X | X |  |  | X |  |  |  | X | X |  | X |  |  | X |  |  | X |  |  | X | X
|  | E |  |  |  |  | X |  | X |  | X |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | X |  |  | X |  | X | X | X |  | X | X |  |  | X |  | X |  |  |  | X |  |  |  | X
11 | 21 | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X |  | X | X |  |  | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | E |  |  |  |  | X |  | X | X |  |  |  | X |  |  | X |  |  |  |  | X | [6 empty] | X
|  | G | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
12 | 24 | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X |  | X | X |  |  | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | E |  |  |  |  | X |  | X | X |  |  |  | X |  |  | X |  |  |  |  | X | [6 empty] | X
|  | G | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
13 | 25 | A | X | X |  | X | X | X | X |  | X |  |  | X |  |  | X | [7 empty] | X | X | X
|  | C | X | X |  | X | X | X | X |  | X |  |  | X |  |  | X | [7 empty] | X | X | X
|  | E | X | X | [9 empty] | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | F | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | F | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | G | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | G | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
14 | 27 | A | X | X |  | X | X |  | X | X | X |  |  | X |  |  | X | [7 empty] | X |  | X
|  | C | X | X |  | X | X |  | X | X | X |  |  | X |  |  | X | [7 empty] | X |  | X
|  | E |  |  |  |  | X |  | X | X |  |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | F | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | F | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | G | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | G | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X

## Shorting Summary
Shorting Sequence for Open Burn Test 11, Location C, IRMS #2
Test conditions: Cable: Bundle of 6, 7-conductor, 12 AWG, Tefzel, XLPO, EPR, XLPE, PVC, & TS/TP control cables (Items 12, 8, 2, 10, 1 & 3). Cable specimens present: Three lengths of cable were monitored for electrical performance (A, B & C [See Elect. Conn. Map]), a second bundle of 6 cables was monitored for temperature response. Raceway: 12" B-Line Series 2 tray (part number 248P09-12-144) located at position C in the Test Cell chamber with chamber end walls open and un-heated. Exposure conditions: Gas burner flow rate set to a nominal 250 kW heat release rate, increased to 300 kW during the test run. Electrical repsonse monitoring: IRMS system using 6 channels - two for each cable (see electrical connection map), cable tray was grounded. Thermal response monitoring: Two cable bundle temperatures (see thermocouple map), air temperatures above and below the cable bundle, and the cable tray rung temperature. Gas burner initiated: Following 207 seconds of baseline data monitoring.
DAQ Time | Burner Time | Event | Interpretation
207 | 0 | Ignited Gas Burner
421 | 214 | Conductors A1 & A2 short together at less than 100 ohms (42) | Cable A shorts internally
425 | 218 | Conductor A1 shorts to ground at less than 1000 ohms (683)
510-519 | 303-312 | The existing ground fault on conductor A1 decreases to less than 100 ohms (16); conductor A2 shorts to ground at less than 100 ohms (4) | Cable A shorted to ground
528 | 321 | Conductor B4 shorts to ground at less than 100 ohms (6)
574 | 367 | Conductor C6 shorts to ground at less than 1000 ohms (117)
614-616 | 407-409 | Conductor C5 shorts to ground at less than 100 ohms (6); the existing ground fault on conductor C6 decreases to less than 100 ohms (8) | Cable C shorted to ground
651 | 444 | Conductor B3 shorts to ground at less than 1000 ohms (164) | Cable B shorted to ground
656 | 449 | Conductors B3 & B4 short together at less than 1000 ohms (163) [erratic shorting behavior noted] | Cable B shorts internally
670 | 463 | Conductors C5 & C6 short together at less than 1000 ohms (403) | Cable C shorts internally
692 | 485 | The existing ground fault on conductor B3 decreases to less than 100 ohms (8)
754 | 547 | The existing internal short between conductors C5 & C6 decreases to less than 100 ohms (53) but is erratic in nature
908 | 701 | The existing internal short between conductors B3 & B4 decreases to less than 100 ohms (25)
1148 | 941 | Gas burner is shut off
Additional Observations
Observation 1 | Some erratic internal shorting behavior was noted.
Observation 2 | There was no evidence of cable-to-cable interactions prior to internal cable shorting or shorting to ground.

## Thermocouple Map
Thermocouple map for TC's on and within the cable
|  |  |  | Cable A = | TEFZEL | (Item #12)
|  |  |  | Cable B = | XLPO | (Item #8)
|  |  |  | Cable C = | EPR | (Item #2)
|  |  |  | Cable D = | XLPE | (Item #10)
|  |  |  | Cable E = | PVC | (Item #1)
|  |  |  | Cable F = | TS/TP | (Item #3)
Translation to data file names used in "Temperatures" WorkSheet:
| Map Name |  | Location
| C1 | = | Center of bundle, under jacket
| C2 | = | Air above bundle
| C3 | = | Air below bundle
| C4 | = | Intra-bundle, center

## Elect Conn Map
Electrical connection map within the cables
|  |  |  | Cable A = | TEFZEL | (Item #12)
|  |  |  | Cable B = | XLPO | (Item #8)
|  |  |  | Cable C = | EPR | (Item #2)
Tray rung under D-E-F
Cable Bundle Arrangement
Cable 7-Conductor Arrangement
| Lt Blue = | Even conductor set
| Lt Red = | Odd conductor set
| Gray = | Center conductor (not connected)
IRMS Electrical Connections

## C-C Individuals
Conductor to Conductor Resistances
Open Burn Test 11 |  |  | 2006-11-20 | 12:58
Mixed | 7-C | Tray C | IRMS | 2
0 | 250 kW
Burner Time | A1-A2 | Burner Time | A1-B3 | Burner Time | A1-B4 | Burner Time | A1-C5 | Burner Time | A1-C6 | Burner Time | A2-B3 | Burner Time | A2-B4 | Burner Time | A2-C5 | Burner Time | A2-C6 | Burner Time | B3-B4 | Burner Time | B3-C5 | Burner Time | B3-C6 | Burner Time | B4-C5 | Burner Time | B4-C6 | Burner Time | C5-C6
-206.5 | 519775.9997 | -204 | 517975.9997 | -201 | 518375.9997 | -198.5 | 518575.9997 | -195.5 | 519375.9997 | -192.5 | 523975.9997 | -190 | 519775.9997 | -187 | 511175.9997 | -184.5 | 521375.9997 | -181.5 | 512775.9997 | -178.5 | 512775.9997 | -176 | 510775.9997 | -173 | 503375.9997 | -170.5 | 498975.9997 | -167.5 | 511575.9997
-164.5 | 519775.9997 | -162 | 517975.9997 | -159 | 518375.9997 | -156.5 | 518575.9997 | -153.5 | 519375.9997 | -150.5 | 523975.9997 | -148 | 519775.9997 | -145 | 511175.9997 | -142.5 | 521375.9997 | -139.5 | 512775.9997 | -136.5 | 512775.9997 | -134 | 510775.9997 | -131 | 503375.9997 | -128.5 | 498975.9997 | -125.5 | 511575.9997
-122.5 | 519775.9997 | -120 | 517975.9997 | -117 | 518375.9997 | -114.5 | 518575.9997 | -111.5 | 519375.9997 | -108.5 | 523975.9997 | -106 | 519775.9997 | -103 | 511175.9997 | -100.5 | 521375.9997 | -97.5 | 512775.9997 | -94.5 | 512775.9997 | -92 | 510775.9997 | -89 | 503375.9997 | -86.5 | 498975.9997 | -83.5 | 511575.9997
-80.5 | 519775.9997 | -78 | 517975.9997 | -75 | 518375.9997 | -72.5 | 518575.9997 | -69.5 | 519375.9997 | -66.5 | 523975.9997 | -64 | 519775.9997 | -61 | 511175.9997 | -58.5 | 521375.9997 | -55.5 | 512775.9997 | -52.5 | 512775.9997 | -50 | 510775.9997 | -47 | 503375.9997 | -44.5 | 498975.9997 | -41.5 | 511575.9997
-38.5 | 519775.9997 | -36 | 517975.9997 | -33 | 518375.9997 | -30.5 | 518575.9997 | -27.5 | 519375.9997 | -24.5 | 523975.9997 | -22 | 519775.9997 | -19 | 511175.9997 | -16.5 | 521375.9997 | -13.5 | 512775.9997 | -10.5 | 512775.9997 | -8 | 510775.9997 | -5 | 503375.9997 | -2.5 | 498975.9997 | 0.5 | 511575.9997
3.5 | 519775.9997 | 6 | 517975.9997 | 9 | 518375.9997 | 11.5 | 518575.9997 | 14.5 | 519375.9997 | 17.5 | 523975.9997 | 20 | 519775.9997 | 23 | 511175.9997 | 25.5 | 521375.9997 | 28.5 | 512775.9997 | 31.5 | 512775.9997 | 34 | 510775.9997 | 37 | 503375.9997 | 39.5 | 498975.9997 | 42.5 | 511575.9997
45.5 | 519775.9997 | 48 | 517975.9997 | 51 | 518375.9997 | 53.5 | 518575.9997 | 56.5 | 519375.9997 | 59.5 | 523975.9997 | 62 | 519775.9997 | 65 | 511175.9997 | 67.5 | 521375.9997 | 70.5 | 512775.9997 | 73.5 | 512775.9997 | 76 | 510775.9997 | 79 | 503375.9997 | 81.5 | 498975.9997 | 84.5 | 511575.9997
87.5 | 519775.9997 | 90 | 517975.9997 | 93 | 518375.9997 | 95.5 | 518575.9997 | 98.5 | 519375.9997 | 101.5 | 523975.9997 | 104 | 519775.9997 | 107 | 511175.9997 | 109.5 | 521375.9997 | 112.5 | 512775.9997 | 115.5 | 512775.9997 | 118 | 510775.9997 | 121 | 503375.9997 | 123.5 | 498975.9997 | 126.5 | 511575.9997
129.5 | 519775.9997 | 132 | 517975.9997 | 135 | 518375.9997 | 137.5 | 518575.9997 | 140.5 | 519375.9997 | 143.5 | 523975.9997 | 146 | 519775.9997 | 149 | 511175.9997 | 151.5 | 521375.9997 | 154.5 | 512775.9997 | 157.5 | 512775.9997 | 160 | 510775.9997 | 163 | 503375.9997 | 165.5 | 498975.9997 | 168.5 | 511575.9997
171.5 | 519775.9997 | 174 | 517975.9997 | 177 | 518375.9997 | 179.5 | 518575.9997 | 182.5 | 519375.9997 | 185.5 | 523975.9997 | 188 | 519775.9997 | 191 | 511175.9997 | 193.5 | 521375.9997 | 196.5 | 512775.9997 | 199.5 | 512775.9997 | 202 | 510775.9997 | 205 | 503375.9997 | 207.5 | 498975.9997 | 210.5 | 511575.9997
213.5 | 42.398 | 216 | 517975.9997 | 219 | 518375.9997 | 221.5 | 518575.9997 | 224.5 | 519375.9997 | 227.5 | 523975.9997 | 230 | 519775.9997 | 233 | 511175.9997 | 235.5 | 521375.9997 | 238.5 | 512775.9997 | 241.5 | 512775.9997 | 244 | 510775.9997 | 246.5 | 503375.9997 | 249.5 | 498975.9997 | 252.5 | 511575.9997
255.5 | 48.5929 | 258 | 517975.9997 | 261 | 518375.9997 | 263.5 | 518575.9997 | 266.5 | 519375.9997 | 269.5 | 523975.9997 | 272 | 519775.9997 | 275 | 511175.9997 | 277.5 | 521375.9997 | 280.5 | 512775.9997 | 283.5 | 512775.9997 | 286 | 510775.9997 | 289 | 503375.9997 | 291.5 | 498975.9997 | 294.5 | 511575.9997
297 | 55.8493 | 300 | 248989.9302 | 303 | 233592.9375 | 305.5 | 9032.7582 | 308.5 | 23764.4244 | 311 | 6365.876 | 314 | 6.7509 | 317 | 9136.2127 | 319.5 | 56027.254 | 322.5 | 512775.9997 | 325.5 | 512775.9997 | 328 | 510775.9997 | 331 | 503375.9997 | 333.5 | 498975.9997 | 357.5 | 511575.9997
339 | 21.9642 | 342 | 48528.6311 | 344.5 | 52327.9054 | 347.5 | 25060.4549 | 350.5 | 40430.2156 | 353.5 | 1537.7065 | 356 | 25.5475 | 359 | 26527.6189 | 361.5 | 1537.4101 | 364.5 | 512775.9997 | 367.5 | 512775.9997 | 370 | 510775.9997 | 373 | 503375.9997 | 375.5 | 498975.9997 | 378 | 6894.6624
381 | 25.4227 | 384 | 22433.669 | 386.5 | 5536.9319 | 389.5 | 3901.0582 | 392.5 | 25169.6966 | 395 | 28432.5737 | 398 | 1.8197 | 401 | 28.1651 | 403.5 | 8.8048 | 406.5 | 63235.7397 | 409.5 | 512775.9997 | 412 | 255337.9994 | 415 | 19264.4536 | 417.5 | 5571.2913 | 420.5 | 1345.2289
423.5 | 7.0256 | 426 | 1500.0009 | 429 | 16000.1205 | 431.5 | 0.93764 | 434.5 | 27.4786 | 437.5 | 3594.8643 | 440 | 21.5522 | 443 | 23.5114 | 445.5 | 8.2409 | 448.5 | 162.9404 | 451.5 | 523.6858 | 454 | 163.0183 | 456.5 | 158.3963 | 459.5 | 58.699 | 462.5 | 402.9015
465 | 13.8952 | 468 | 20.4871 | 470.5 | 2.0428 | 473.5 | 28.3826 | 476.5 | 20.9905 | 479 | 29.1401 | 482 | 22.7964 | 484.5 | 13.7969 | 487.5 | 26.126 | 490.5 | 361.7967 | 493 | 6.34 | 496 | 27.4723 | 499 | 34.428 | 501.5 | 0.56786 | 504.5 | 456.5723
507.5 | 16.3237 | 510 | 0.57646 | 512.5 | 26.2739 | 515.5 | 30.779 | 518.5 | 15.9645 | 521 | 1.4082 | 524 | 28.6169 | 526.5 | 19.2322 | 529.5 | 24.4513 | 532.5 | 1681.8873 | 535 | 33.1656 | 538 | 5.5095 | 540.5 | 13.665 | 543.5 | 25.2719 | 546.5 | 52.9192
549.5 | 26.4279 | 552 | 10.4332 | 555 | 12.0571 | 557.5 | 6.0926 | 560.5 | 0.94106 | 563.5 | 27.3319 | 566 | 21.6697 | 569 | 12.4994 | 571.5 | 17.1742 | 574.5 | 484.0181 | 577 | 22.6798 | 580 | 18.5099 | 583 | 0.87192 | 585.5 | 29.1379 | 588.5 | 846.1499
591.5 | 0.056009 | 594 | 22.1288 | 597 | 23.1222 | 599.5 | 1.332 | 602.5 | 3478.9028 | 605 | 2.7388 | 608 | 8.3724 | 610.5 | 7.0668 | 613.5 | 1.1021 | 616.5 | 3329.527 | 619 | 24.0872 | 622 | 16.6635 | 625 | 9.3638 | 627.5 | 22.3005 | 630.5 | 394.0926
633.5 | 22.7366 | 636 | 7.2477 | 639 | 0.1774 | 641.5 | 11.4012 | 644.5 | 31.3911 | 647.5 | 27.5232 | 650 | 29.6063 | 653 | 20.5089 | 655.5 | 14.1981 | 658.5 | 239.5325 | 661.5 | 19.8982 | 664 | 28.1961 | 667 | 8.1436 | 669.5 | 12.3971 | 672.5 | 1547.8587
675.5 | 26.5547 | 678 | 5.1165 | 681 | 27.6823 | 683.5 | 24.2653 | 686.5 | 0.062466 | 689 | 7.3497 | 692 | 7.9976 | 694.5 | 15.0701 | 697.5 | 1.4313 | 700.5 | 25.1477 | 703.5 | 9.6506 | 706 | 0.94012 | 709 | 28.645 | 711.5 | 0.65263 | 714.5 | 5608.1227
717 | 20.7363 | 720 | 0.84199 | 722.5 | 11.6065 | 725.5 | 18.8577 | 728.5 | 12.0748 | 731 | 16.0911 | 734 | 0.78425 | 736.5 | 6.7875 | 739.5 | 2.8113 | 742.5 | 17.0701 | 745 | 0.099818 | 748 | 10.5429 | 750.5 | 0.29676 | 753.5 | 16.0765 | 756.5 | 8270.1281
759 | 10.6259 | 762 | 0.39205 | 764.5 | 13.5332 | 767.5 | 17.742 | 770.5 | 3.3477 | 773 | 5.9476 | 776 | 30.7455 | 778.5 | 0.90579 | 781.5 | 4.7081 | 784.5 | 27.9104 | 787.5 | 15.0056 | 790 | 28.2623 | 792.5 | 13.4528 | 795.5 | 18.2937 | 798.5 | 10.1736
801.5 | 14.1544 | 804 | 25.5457 | 807 | 9.7418 | 809.5 | 19.2531 | 812.5 | 26.0141 | 815 | 32.2215 | 818 | 20.1599 | 820.5 | 15.1774 | 823.5 | 24.6967 | 826.5 | 17.6811 | 829.5 | 20.1883 | 832 | 3.9871 | 835 | 1.127 | 837.5 | 3.3503 | 840.5 | 26.2476
843.5 | 23.5791 | 846 | 1.9629 | 849 | 3.3606 | 851.5 | 15.6235 | 854.5 | 0.78242 | 857 | 9.7832 | 860 | 0.94278 | 862.5 | 14.3771 | 865.5 | 17.2832 | 868.5 | 0.9127 | 871 | 11.7843 | 874 | 17.0505 | 876.5 | 26.1264 | 879.5 | 3.0832 | 882.5 | 6.594
885 | 15.4677 | 888 | 25.7969 | 891 | 9.6936 | 893.5 | 26.5134 | 896.5 | 13.4971 | 899 | 8.4131 | 902 | 0.38581 | 904.5 | 6.7875 | 907.5 | 21.6954 | 910.5 | 0.46961 | 913 | 7.3128 | 916 | 0.90406 | 918.5 | 6.5726 | 921.5 | 17.0897 | 924.5 | 0.90752
927 | 15.2027 | 930 | 6.2399 | 932.5 | 0.93678 | 935.5 | 9.6882 | 938.5 | 20.7002 | 941 | 0.59313 | 944 | 29.1427 | 946.5 | 20.0416 | 949.5 | 17.0109 | 952.5 | 1198.5222 | 955 | 8.0182 | 958 | 0.030396 | 960.5 | 22.6463 | 963.5 | 20.6546 | 966.5 | 8606.4058
969 | 5773.1915 | 972 | 5.2501 | 974.5 | 1.8333 | 977.5 | 2.0408 | 980.5 | 14.0655 | 983 | 4.5368 | 986 | 7.3477 | 988.5 | 3.8932 | 991.5 | 2.6421 | 994.5 | 707.2819 | 997 | 25.3367 | 1000 | 12.5129 | 1002.5 | 24.2679 | 1005.5 | 17.2603 | 1008.5 | 4227.0501
1011 | 3855.0388 | 1014 | 12.6261 | 1016.5 | 29.4531 | 1019.5 | 19.8223 | 1022.5 | 7.8202 | 1025 | 13.3842 | 1028 | 30.9486 | 1030.5 | 12566.3268 | 1033.5 | 20085.1431 | 1036.5 | 550.9531 | 1039 | 7.6409 | 1042 | 12.7188 | 1044.5 | 27.3736 | 1047.5 | 22.6721 | 1050.5 | 7927.3655
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!

## C-G Min
Average Conductor to Ground Resistances
Open Burn Test 11 |  |  | 2006-11-20 | 12:58
Mixed | 7-C | Tray C | IRMS | 2
0 | 250 kW
Burner Time | A1-G |  | Burner Time | A2-G | Burner Time | B3-G | Burner Time | B4-G | Burner Time | C5-G | Burner Time | C6-G
-201.1 | 517976 |  | -192.1 | 511176 | -186.5 | 510776 | -183.2 | 498976 | -180.9 | 503376 | -178.8 | 498976
-159.1 | 517976 |  | -150.1 | 511176 | -144.5 | 510776 | -141.2 | 498976 | -138.9 | 503376 | -136.8 | 498976
-117.1 | 517976 |  | -108.1 | 511176 | -102.5 | 510776 | -99.2 | 498976 | -96.9 | 503376 | -94.8 | 498976
-75.1 | 517976 |  | -66.1 | 511176 | -60.5 | 510776 | -57.2 | 498976 | -54.9 | 503376 | -52.8 | 498976
-33.1 | 517976 |  | -24.1 | 511176 | -18.5 | 510776 | -15.2 | 498976 | -12.9 | 503376 | -10.8 | 498976
8.9 | 517976 |  | 17.9 | 511176 | 23.5 | 510776 | 26.8 | 498976 | 29.1 | 503376 | 31.2 | 498976
50.9 | 517976 |  | 59.9 | 511176 | 65.5 | 510776 | 68.8 | 498976 | 71.1 | 503376 | 73.2 | 498976
92.9 | 517976 |  | 101.9 | 511176 | 107.5 | 510776 | 110.8 | 498976 | 113.1 | 503376 | 115.2 | 498976
134.9 | 517976 |  | 143.9 | 511176 | 149.5 | 510776 | 152.8 | 498976 | 155.1 | 503376 | 157.2 | 498976
176.9 | 517976 |  | 185.9 | 511176 | 191.5 | 510776 | 194.8 | 498976 | 197.1 | 503376 | 199.2 | 498976
218.9 | 683.427 |  | 227.9 | 2690.4522 | 233.5 | 510776 | 236.7 | 498976 | 239 | 503376 | 241.2 | 498976
260.9 | 691.9386 |  | 269.9 | 7345.0559 | 275.5 | 510776 | 278.8 | 498976 | 281.1 | 503376 | 283.2 | 498976
302.8 | 16.429 |  | 311.7 | 3.7507 | 317.4 | 510776 | 320.8 | 6.1838 | 327.3 | 503376 | 329.4 | 1689.0769
344.7 | 10.7855 |  | 353.8 | 0.62927 | 359.5 | 510776 | 362.7 | 11.8975 | 365 | 1121.9668 | 367.1 | 117.152
386.7 | 1.8218 |  | 395.7 | 3.3551 | 401.4 | 32024.7141 | 404.7 | 24.0162 | 407.1 | 5.9949 | 409.2 | 8.0719
428.9 | 0.63562 |  | 437.9 | 1.5264 | 443.5 | 163.6099 | 446.7 | 16.5119 | 449 | 28.6346 | 451.2 | 8.5861
470.7 | 3.5709 |  | 479.6 | 9.0802 | 485.3 | 7.7923 | 488.7 | 2.0605 | 490.9 | 3.4859 | 493.2 | 4.8176
512.8 | 0.98947 |  | 521.7 | 2.9619 | 527.3 | 6.9673 | 530.6 | 12.7225 | 532.8 | 24.3827 | 535.2 | 7.1085
554.9 | 0.63464 |  | 563.9 | 13.8699 | 569.4 | 5.3207 | 572.8 | 0.65494 | 575 | 23.5613 | 577.2 | 31.0399
596.9 | 1.6177 |  | 605.7 | 2.6528 | 611.3 | 8.1127 | 614.8 | 10.7514 | 616.9 | 4.9417 | 619.2 | 6.8002
638.9 | 1.3837 |  | 647.9 | 15.5754 | 653.5 | 9.9869 | 656.8 | 1.0839 | 659.1 | 5.4177 | 661.2 | 10.1026
680.9 | 1.4998 |  | 689.7 | 2.9771 | 695.4 | 2.4621 | 698.8 | 2.1441 | 701 | 6.3386 | 703.2 | 1.8522
722.7 | 2.3866 |  | 731.6 | 0.63415 | 737.3 | 1.6401 | 740.6 | 1.2216 | 742.8 | 1.3438 | 745.2 | 10.5739
764.7 | 1.9433 |  | 773.6 | 0.64488 | 779.4 | 16.3512 | 782.6 | 11.4463 | 784.9 | 4.2855 | 787.2 | 4.892
806.9 | 11.1655 |  | 815.7 | 16.5169 | 821.4 | 2.7197 | 824.8 | 0.98601 | 827 | 1.0826 | 829.2 | 15.2343
848.9 | 0.79084 |  | 857.7 | 0.63415 | 863.3 | 0.64286 | 866.7 | 1.8167 | 868.8 | 0.64286 | 871.2 | 5.5192
890.8 | 11.1179 |  | 899.6 | 1.1826 | 905.3 | 0.64539 | 908.7 | 0.82933 | 910.8 | 0.64437 | 913.2 | 0.66075
932.7 | 0.63587 |  | 941.6 | 2.1591 | 947.3 | 1.5658 | 950.6 | 3.3644 | 952.8 | 17.5001 | 955.2 | 6.8778
974.7 | 3.3644 |  | 983.6 | 4.1702 | 989.3 | 11.9328 | 992.6 | 11.9328 | 994.8 | 11.5918 | 997.2 | 9.7382
1016.7 | 9.2714 |  | 1025.6 | 14.7779 | 1031.3 | 9.0761 | 1034.6 | 10.1734 | 1036.8 | 9.6898 | 1039.2 | 19.8114
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!

## C5-C6
Open Burn Test 11 |  |  | 2006-11-20 | 12:58 |  |  | Vs = |  | 156.1893 |  | R = | 100
Mixed | 7-C | Tray C | IRMS | 2
0 | 250 kW |  | Bundle | Ch. 5 & 6 | Cable C | Odd-Even
Time-29 | N11 | N12 | Time-30 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R6-G | R5-6
39041.5358 | 0 | 0 | 39041.5358 | 0 | 0 |  | -167.5 | 39.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511576 | 511576 | 511575.9997
39041.5362 | 0 | 0 | 39041.5362 | 0 | 0 |  | -125.5 | 81.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511576 | 511576 | 511575.9997
39041.5367 | 0 | 0 | 39041.5367 | 0 | 0 |  | -83.5 | 123.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511576 | 511576 | 511575.9997
39041.5372 | 0 | 0 | 39041.5372 | 0 | 0 |  | -41.5 | 165.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511576 | 511576 | 511575.9997
39041.5377 | 0 | 0 | 39041.5377 | 0 | 0 |  | 0.5 | 207.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511576 | 511576 | 511575.9997
39041.5382 | 0 | 0 | 39041.5382 | 0 | 0 |  | 42.5 | 249.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511576 | 511576 | 511575.9997
39041.5387 | 0 | 0 | 39041.5387 | 0 | 0 |  | 84.5 | 291.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511576 | 511576 | 511575.9997
39041.5392 | 0 | 0 | 39041.5392 | 0 | 0 |  | 126.5 | 333.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511576 | 511576 | 511575.9997
39041.5396 | 0 | 0 | 39041.5397 | 0 | 0 |  | 168.5 | 375.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511576 | 511576 | 511575.9997
39041.5401 | 0 | 0 | 39041.5401 | 0 | 0 |  | 210.5 | 417.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511576 | 511576 | 511575.9997
39041.5406 | 0 | 0 | 39041.5406 | 0 | 0 |  | 252.5 | 459.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511576 | 511576 | 511575.9997
39041.5411 | 0 | 0 | 39041.5411 | 0 | 0 |  | 294.5 | 501.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511576 | 511576 | 511575.9997
39041.5416 | 0 | 0 | 39041.5421 | 386 | 243 |  | 357.5 | 564.5 | 0.030525 | 0 | 23.5653 | 14.8352 | 0.00030525 | 0 | 0.23565 | 0.14835 | 0.00030525 | 0.087302 | 511576 | 1689.0769 | 511575.9997
39041.5421 | 240 | 18 |  | 1261 | 141 |  | 378 | 585 | 14.652 | 1.0989 | 76.9841 | 8.6081 | 0.14652 | 0.010989 | 0.76984 | 0.086081 | 0.13553 | 0.68376 | 1121.9668 | 117.152 | 6894.6624
39041.5426 | 2105 | 6 | 39041.5426 | 2136 | 39 |  | 420.5 | 627.5 | 128.5104 | 0.3663 | 130.4029 | 2.381 | 1.2851 | 0.003663 | 1.304 | 0.02381 | 1.2814 | 1.2802 | 21.884 | 22.0129 | 1345.2289
39041.543 | 1825 | 43 | 39041.5431 | 1918 | 2 |  | 462.5 | 669.5 | 111.4164 | 2.6252 | 117.094 | 0.1221 | 1.1142 | 0.026252 | 1.1709 | 0.001221 | 1.0879 | 1.1697 | 44.3492 | 33.5016 | 402.9015
39041.5435 | 2100 | 12 | 39041.5435 | 2247 | 4 |  | 504.5 | 711.5 | 128.2051 | 0.7326 | 137.1795 | 0.2442 | 1.2821 | 0.007326 | 1.3718 | 0.002442 | 1.2747 | 1.3694 | 22.8934 | 13.9913 | 456.5723
39041.544 | 1662 | 0 | 39041.544 | 2361 | 0 |  | 546.5 | 753.5 | 101.4652 | 0 | 144.1392 | 0 | 1.0147 | 0 | 1.4414 | 0 | 1.0147 | 1.4414 | 53.9338 | 8.36 | 52.9192
39041.5445 | 2081 | 13 | 39041.5445 | 1971 | 15 |  | 588.5 | 795.5 | 127.0452 | 0.79365 | 120.3297 | 0.91575 | 1.2705 | 0.0079365 | 1.2033 | 0.0091575 | 1.2625 | 1.1941 | 23.5613 | 31.0399 | 846.1499
39041.545 | 1927 | 11 | 39041.545 | 2382 | 9 |  | 630.5 | 837.5 | 117.6435 | 0.67155 | 145.4212 | 0.54945 | 1.1764 | 0.0067155 | 1.4542 | 0.0054945 | 1.1697 | 1.4487 | 35.6796 | 7.5126 | 394.0926
39041.5455 | 2407 | 3 | 39041.5455 | 1763 | 1 |  | 672.5 | 879.5 | 146.9475 | 0.18315 | 107.6313 | 0.06105 | 1.4695 | 0.0018315 | 1.0763 | 0.0006105 | 1.4676 | 1.0757 | 6.3143 | 45.5502 | 1547.8587
39041.546 | 2007 | 2 | 39041.546 | 2037 | 1 |  | 714.5 | 921.5 | 122.5275 | 0.1221 | 124.359 | 0.06105 | 1.2253 | 0.001221 | 1.2436 | 0.0006105 | 1.2241 | 1.243 | 27.6076 | 25.6537 | 5608.1227
39041.5464 | 2168 | 1 | 39041.5465 | 2015 | 0 |  | 756.5 | 963.5 | 132.3565 | 0.06105 | 123.0159 | 0 | 1.3236 | 0.0006105 | 1.2302 | 0 | 1.323 | 1.2302 | 18.0456 | 26.9667 | 8270.1281
39041.5469 | 2293 | 0 | 39041.5469 | 1921 | 0 |  | 798.5 | 1005.5 | 139.9878 | 0 | 117.2772 | 0 | 1.3999 | 0 | 1.1728 | 0 | 1.3999 | 1.1728 | 11.5735 | 33.1796 | 10.1736
39041.5474 | 2007 | 0 | 39041.5474 | 1981 | 0 |  | 840.5 | 1047.5 | 122.5275 | 0 | 120.9402 | 0 | 1.2253 | 0 | 1.2094 | 0 | 1.2253 | 1.2094 | 27.4728 | 29.1459 | 26.2476
39041.5479 | 2368 | 0 | 39041.5479 | 2197 | 0 |  | 882.5 | 1089.5 | 144.5665 | 0 | 134.127 | 0 | 1.4457 | 0 | 1.3413 | 0 | 1.4457 | 1.3413 | 8.0397 | 16.4488 | 6.594
39041.5484 | 2542 | 0 | 39041.5484 | 1931 | 0 |  | 924.5 | 1131.5 | 155.1893 | 0 | 117.8877 | 0 | 1.5519 | 0 | 1.1789 | 0 | 1.5519 | 1.1789 | 0.64437 | 32.4899 | 0.90752
39041.5489 | 2178 | 1 | 39041.5489 | 1978 | 0 |  | 966.5 | 1173.5 | 132.967 | 0.06105 | 120.757 | 0 | 1.3297 | 0.0006105 | 1.2076 | 0 | 1.3291 | 1.2076 | 17.5001 | 29.3418 | 8606.4058
39041.5494 | 2093 | 1 | 39041.5494 | 2326 | 1 |  | 1008.5 | 1215.5 | 127.7778 | 0.06105 | 142.0024 | 0.06105 | 1.2778 | 0.0006105 | 1.42 | 0.0006105 | 1.2772 | 1.4194 | 22.3524 | 10.0141 | 4227.0501
39041.5498 | 1896 | 2 | 39041.5499 | 1946 | 2 |  | 1050.5 | 1257.5 | 115.7509 | 0.1221 | 118.8034 | 0.1221 | 1.1575 | 0.001221 | 1.188 | 0.001221 | 1.1563 | 1.1868 | 35.0898 | 31.5937 | 7927.3655

## B4-C6
Open Burn Test 11 |  |  | 2006-11-20 | 12:58 |  |  | Vs = |  | 152.3431 |  | R = | 100
Mixed | 7-C | Tray C | IRMS | 2
0 | 250 kW |  | Bundle | Ch. 4 & 6 | Cable B | Even - | Cable C |  | Even
Time-27 | N11 | N12 | Time-28 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R6-G | R4-6
39041.5357 | 0 | 0 | 39041.5357 | 0 | 0 |  | -170.5 | 36.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 498976 | 498976 | 498975.9997
39041.5362 | 0 | 0 | 39041.5362 | 0 | 0 |  | -128.5 | 78.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 498976 | 498976 | 498975.9997
39041.5367 | 0 | 0 | 39041.5367 | 0 | 0 |  | -86.5 | 120.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 498976 | 498976 | 498975.9997
39041.5372 | 0 | 0 | 39041.5372 | 0 | 0 |  | -44.5 | 162.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 498976 | 498976 | 498975.9997
39041.5377 | 0 | 0 | 39041.5377 | 0 | 0 |  | -2.5 | 204.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 498976 | 498976 | 498975.9997
39041.5381 | 0 | 0 | 39041.5382 | 0 | 0 |  | 39.5 | 246.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 498976 | 498976 | 498975.9997
39041.5386 | 0 | 0 | 39041.5386 | 0 | 0 |  | 81.5 | 288.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 498976 | 498976 | 498975.9997
39041.5391 | 0 | 0 | 39041.5391 | 0 | 0 |  | 123.5 | 330.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 498976 | 498976 | 498975.9997
39041.5396 | 0 | 0 | 39041.5396 | 0 | 0 |  | 165.5 | 372.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 498976 | 498976 | 498975.9997
39041.5401 | 0 | 0 | 39041.5401 | 0 | 0 |  | 207.5 | 414.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 498976 | 498976 | 498975.9997
39041.5406 | 0 | 0 | 39041.5406 | 0 | 0 |  | 249.5 | 456.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 498976 | 498976 | 498975.9997
39041.5411 | 0 | 0 | 39041.5411 | 0 | 0 |  | 291.5 | 498.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 498976 | 498976 | 498975.9997
39041.5416 | 0 | 0 | 39041.5416 | 0 | 0 |  | 333.5 | 540.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 498976 | 498976 | 498975.9997
39041.542 | 0 | 0 | 39041.542 | 6 | 0 |  | 375.5 | 582.5 | 0.030525 | 0 | 0.3663 | 0 | 0.00030525 | 0 | 0.003663 | 0 | 0.00030525 | 0.003663 | 498976 | 41489.6667 | 498975.9997
39041.5425 | 44 | 0 | 39041.5425 | 2309 | 0 |  | 417.5 | 624.5 | 2.6862 | 0 | 140.9646 | 0 | 0.026862 | 0 | 1.4096 | 0 | 0.026862 | 1.4096 | 5571.3182 | 8.0719 | 5571.2913
39041.543 | 1563 | 0 | 39041.543 | 1411 | 0 |  | 459.5 | 666.5 | 95.4212 | 0 | 86.1416 | 0 | 0.95421 | 0 | 0.86142 | 0 | 0.95421 | 0.86142 | 59.6532 | 76.8519 | 58.699
39041.5435 | 2445 | 0 | 39041.5435 | 2204 | 0 |  | 501.5 | 708.5 | 149.2674 | 0 | 134.5543 | 0 | 1.4927 | 0 | 1.3455 | 0 | 1.4927 | 1.3455 | 2.0605 | 13.2205 | 0.56786
39041.544 | 1973 | 0 | 39041.544 | 2017 | 0 |  | 543.5 | 750.5 | 120.4518 | 0 | 123.138 | 0 | 1.2045 | 0 | 1.2314 | 0 | 1.2045 | 1.2314 | 26.4764 | 23.7174 | 25.2719
39041.5445 | 1915 | 0 | 39041.5445 | 1809 | 0 |  | 585.5 | 792.5 | 116.9109 | 0 | 110.4396 | 0 | 1.1691 | 0 | 1.1044 | 0 | 1.1691 | 1.1044 | 30.307 | 37.9425 | 29.1379
39041.545 | 2020 | 0 | 39041.545 | 2207 | 0 |  | 627.5 | 834.5 | 123.3211 | 0 | 134.7375 | 0 | 1.2332 | 0 | 1.3474 | 0 | 1.2332 | 1.3474 | 23.5337 | 13.0666 | 22.3005
39041.5454 | 2194 | 0 | 39041.5455 | 2096 | 0 |  | 669.5 | 876.5 | 133.9438 | 0 | 127.9609 | 0 | 1.3394 | 0 | 1.2796 | 0 | 1.3394 | 1.2796 | 13.7366 | 19.0544 | 12.3971
39041.5459 | 2443 | 0 | 39041.5459 | 2450 | 0 |  | 711.5 | 918.5 | 149.1453 | 0 | 149.5726 | 0 | 1.4915 | 0 | 1.4957 | 0 | 1.4915 | 1.4957 | 2.1441 | 1.8522 | 0.65263
39041.5464 | 2126 | 0 | 39041.5464 | 2225 | 0 |  | 753.5 | 960.5 | 129.7924 | 0 | 135.8364 | 0 | 1.2979 | 0 | 1.3584 | 0 | 1.2979 | 1.3584 | 17.3744 | 12.1519 | 16.0765
39041.5469 | 2087 | 0 | 39041.5469 | 2379 | 0 |  | 795.5 | 1002.5 | 127.4115 | 0 | 145.2381 | 0 | 1.2741 | 0 | 1.4524 | 0 | 1.2741 | 1.4524 | 19.5678 | 4.892 | 18.2937
39041.5474 | 2381 | 0 | 39041.5474 | 1976 | 0 |  | 837.5 | 1044.5 | 145.3602 | 0 | 120.6349 | 0 | 1.4536 | 0 | 1.2063 | 0 | 1.4536 | 1.2063 | 4.8039 | 26.2844 | 3.3503
39041.5479 | 2387 | 0 | 39041.5479 | 2012 | 0 |  | 879.5 | 1086.5 | 145.7265 | 0 | 122.8327 | 0 | 1.4573 | 0 | 1.2283 | 0 | 1.4573 | 1.2283 | 4.5404 | 24.0249 | 3.0832
39041.5484 | 2108 | 0 | 39041.5484 | 2479 | 0 |  | 921.5 | 1128.5 | 128.6935 | 0 | 151.3431 | 0 | 1.2869 | 0 | 1.5134 | 0 | 1.2869 | 1.5134 | 18.3767 | 0.66075 | 17.0897
39041.5488 | 2047 | 0 | 39041.5489 | 2197 | 0 |  | 963.5 | 1170.5 | 124.9695 | 0 | 134.127 | 0 | 1.2497 | 0 | 1.3413 | 0 | 1.2497 | 1.3413 | 21.9043 | 13.5812 | 20.6546
39041.5493 | 2105 | 0 | 39041.5493 | 2093 | 0 |  | 1005.5 | 1212.5 | 128.5104 | 0 | 127.7778 | 0 | 1.2851 | 0 | 1.2778 | 0 | 1.2851 | 1.2778 | 18.5454 | 19.225 | 17.2603
39041.5498 | 2014 | 0 | 39041.5498 | 1920 | 0 |  | 1047.5 | 1254.5 | 122.9548 | 0 | 117.2161 | 0 | 1.2295 | 0 | 1.1722 | 0 | 1.2295 | 1.1722 | 23.9017 | 29.9677 | 22.6721

## B4-C5
Open Burn Test 11 |  |  | 2006-11-20 | 12:58 |  |  | Vs = |  | 153.6862 |  | R = | 100
Mixed | 7-C | Tray C | IRMS | 2
0 | 250 kW |  | Bundle | Ch. 4 & 5 | Cable B | Even - | Cable C |  | Odd
Time-25 | N11 | N12 | Time-26 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R5-G | R4-5
39041.5357 | 0 | 0 | 39041.5357 | 0 | 0 |  | -173 | 34 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 503376 | 503376 | 503375.9997
39041.5362 | 0 | 0 | 39041.5362 | 0 | 0 |  | -131 | 76 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 503376 | 503376 | 503375.9997
39041.5367 | 0 | 0 | 39041.5367 | 0 | 0 |  | -89 | 118 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 503376 | 503376 | 503375.9997
39041.5371 | 0 | 0 | 39041.5372 | 0 | 0 |  | -47 | 160 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 503376 | 503376 | 503375.9997
39041.5376 | 0 | 0 | 39041.5377 | 0 | 0 |  | -5 | 202 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 503376 | 503376 | 503375.9997
39041.5381 | 0 | 0 | 39041.5381 | 0 | 0 |  | 37 | 244 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 503376 | 503376 | 503375.9997
39041.5386 | 0 | 0 | 39041.5386 | 0 | 0 |  | 79 | 286 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 503376 | 503376 | 503375.9997
39041.5391 | 0 | 0 | 39041.5391 | 0 | 0 |  | 121 | 328 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 503376 | 503376 | 503375.9997
39041.5396 | 0 | 0 | 39041.5396 | 0 | 0 |  | 163 | 370 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 503376 | 503376 | 503375.9997
39041.5401 | 0 | 0 | 39041.5401 | 0 | 0 |  | 205 | 412 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 503376 | 503376 | 503375.9997
39041.5405 | 0 | 0 | 39041.5406 | 0 | 0 |  | 246.5 | 453.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 503376 | 503376 | 503375.9997
39041.541 | 0 | 0 | 39041.5411 | 0 | 0 |  | 289 | 496 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 503376 | 503376 | 503375.9997
39041.5415 | 0 | 0 | 39041.5415 | 0 | 0 |  | 331 | 538 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 503376 | 503376 | 503375.9997
39041.542 | 0 | 0 | 39041.542 | 19 | 0 |  | 373 | 580 | 0.030525 | 0 | 1.16 | 0 | 0.00030525 | 0 | 0.0116 | 0 | 0.00030525 | 0.0116 | 503376 | 13149.3684 | 503375.9997
39041.5425 | 13 | 0 | 39041.5425 | 2375 | 0 |  | 415 | 622 | 0.79365 | 0 | 144.9939 | 0 | 0.0079365 | 0 | 1.4499 | 0 | 0.0079365 | 1.4499 | 19264.4615 | 5.9949 | 19264.4536
39041.543 | 972 | 0 | 39041.543 | 1957 | 0 |  | 456.5 | 663.5 | 59.3407 | 0 | 119.475 | 0 | 0.59341 | 0 | 1.1947 | 0 | 0.59341 | 1.1947 | 158.9897 | 28.6346 | 158.3963
39041.5435 | 1857 | 0 | 39041.5435 | 2132 | 0 |  | 499 | 706 | 113.37 | 0 | 130.1587 | 0 | 1.1337 | 0 | 1.3016 | 0 | 1.1337 | 1.3016 | 35.5617 | 18.076 | 34.428
39041.5439 | 2189 | 0 | 39041.544 | 1872 | 0 |  | 540.5 | 747.5 | 133.6386 | 0 | 114.2857 | 0 | 1.3364 | 0 | 1.1429 | 0 | 1.3364 | 1.1429 | 15.0014 | 34.4754 | 13.665
39041.5444 | 2501 | 0 | 39041.5445 | 1906 | 0 |  | 583 | 790 | 152.6862 | 0 | 116.3614 | 0 | 1.5269 | 0 | 1.1636 | 0 | 1.5269 | 1.1636 | 0.65494 | 32.0766 | 0.87192
39041.5449 | 2273 | 0 | 39041.5449 | 1972 | 0 |  | 625 | 832 | 138.7668 | 0 | 120.3907 | 0 | 1.3877 | 0 | 1.2039 | 0 | 1.3877 | 1.2039 | 10.7514 | 27.6562 | 9.3638
39041.5454 | 2298 | 0 | 39041.5454 | 2332 | 0 |  | 667 | 874 | 140.293 | 0 | 142.3687 | 0 | 1.4029 | 0 | 1.4237 | 0 | 1.4029 | 1.4237 | 9.5466 | 7.9494 | 8.1436
39041.5459 | 1939 | 0 | 39041.5459 | 2116 | 0 |  | 709 | 916 | 118.3761 | 0 | 129.1819 | 0 | 1.1838 | 0 | 1.2918 | 0 | 1.1838 | 1.2918 | 29.8288 | 18.9688 | 28.645
39041.5464 | 2487 | 0 | 39041.5464 | 2484 | 0 |  | 750.5 | 957.5 | 151.8315 | 0 | 151.6484 | 0 | 1.5183 | 0 | 1.5165 | 0 | 1.5183 | 1.5165 | 1.2216 | 1.3438 | 0.29676
39041.5469 | 2193 | 0 | 39041.5469 | 2211 | 0 |  | 792.5 | 999.5 | 133.8828 | 0 | 134.9817 | 0 | 1.3388 | 0 | 1.3498 | 0 | 1.3388 | 1.3498 | 14.7916 | 13.8571 | 13.4528
39041.5473 | 2453 | 0 | 39041.5474 | 2069 | 0 |  | 835 | 1042 | 149.7558 | 0 | 126.3126 | 0 | 1.4976 | 0 | 1.2631 | 0 | 1.4976 | 1.2631 | 2.6245 | 21.6713 | 1.127
39041.5478 | 1977 | 0 | 39041.5478 | 2145 | 0 |  | 876.5 | 1083.5 | 120.696 | 0 | 130.9524 | 0 | 1.207 | 0 | 1.3095 | 0 | 1.207 | 1.3095 | 27.3333 | 17.3604 | 26.1264
39041.5483 | 2331 | 0 | 39041.5483 | 2327 | 0 |  | 918.5 | 1125.5 | 142.3077 | 0 | 142.0635 | 0 | 1.4231 | 0 | 1.4206 | 0 | 1.4231 | 1.4206 | 7.9957 | 8.1813 | 6.5726
39041.5488 | 2032 | 0 | 39041.5488 | 2014 | 0 |  | 960.5 | 1167.5 | 124.0537 | 0 | 122.9548 | 0 | 1.2405 | 0 | 1.2295 | 0 | 1.2405 | 1.2295 | 23.8868 | 24.994 | 22.6463
39041.5493 | 2006 | 0 | 39041.5493 | 2154 | 0 |  | 1002.5 | 1209.5 | 122.4664 | 0 | 131.5018 | 0 | 1.2247 | 0 | 1.315 | 0 | 1.2247 | 1.315 | 25.4925 | 16.87 | 24.2679
39041.5498 | 1958 | 0 | 39041.5498 | 2295 | 0 |  | 1044.5 | 1251.5 | 119.536 | 0 | 140.1099 | 0 | 1.1954 | 0 | 1.4011 | 0 | 1.1954 | 1.4011 | 28.5689 | 9.6898 | 27.3736

## B3-C6
Open Burn Test 11 |  |  | 2006-11-20 | 12:58 |  |  | Vs = |  | 155.9451 |  | R = | 100
Mixed | 7-C | Tray C | IRMS | 2
0 | 250 kW |  | Bundle | Ch. 3 & 6 | Cable B | Odd - | Cable C |  | Even
Time-23 | N11 | N12 | Time-24 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R6-G | R3-6
39041.5356 | 0 | 0 | 39041.5357 | 0 | 0 |  | -176 | 31 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510776 | 510776 | 510775.9997
39041.5361 | 0 | 0 | 39041.5362 | 0 | 0 |  | -134 | 73 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510776 | 510776 | 510775.9997
39041.5366 | 0 | 0 | 39041.5366 | 0 | 0 |  | -92 | 115 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510776 | 510776 | 510775.9997
39041.5371 | 0 | 0 | 39041.5371 | 0 | 0 |  | -50 | 157 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510776 | 510776 | 510775.9997
39041.5376 | 0 | 0 | 39041.5376 | 0 | 0 |  | -8 | 199 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510776 | 510776 | 510775.9997
39041.5381 | 0 | 0 | 39041.5381 | 0 | 0 |  | 34 | 241 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510776 | 510776 | 510775.9997
39041.5386 | 0 | 0 | 39041.5386 | 0 | 0 |  | 76 | 283 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510776 | 510776 | 510775.9997
39041.5391 | 0 | 0 | 39041.5391 | 0 | 0 |  | 118 | 325 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510776 | 510776 | 510775.9997
39041.5395 | 0 | 0 | 39041.5396 | 0 | 0 |  | 160 | 367 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510776 | 510776 | 510775.9997
39041.54 | 0 | 0 | 39041.54 | 0 | 0 |  | 202 | 409 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510776 | 510776 | 510775.9997
39041.5405 | 0 | 0 | 39041.5405 | 0 | 0 |  | 244 | 451 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510776 | 510776 | 510775.9997
39041.541 | 0 | 0 | 39041.541 | 0 | 0 |  | 286 | 493 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510776 | 510776 | 510775.9997
39041.5415 | 0 | 0 | 39041.5415 | 0 | 0 |  | 328 | 535 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510776 | 510776 | 510775.9997
39041.542 | 0 | 0 | 39041.542 | 422 | 0 |  | 370 | 577 | 0.030525 | 0 | 25.7631 | 0 | 0.00030525 | 0 | 0.25763 | 0 | 0.00030525 | 0.25763 | 510776 | 505.3033 | 510775.9997
39041.5425 | 1 | 0 | 39041.5425 | 2176 | 0 |  | 412 | 619 | 0.06105 | 0 | 132.8449 | 0 | 0.0006105 | 0 | 1.3284 | 0 | 0.0006105 | 1.3284 | 255338 | 17.3888 | 255337.9994
39041.5429 | 969 | 0 | 39041.543 | 1710 | 0 |  | 454 | 661 | 59.1575 | 0 | 104.3956 | 0 | 0.59158 | 0 | 1.044 | 0 | 0.59158 | 1.044 | 163.6099 | 49.3789 | 163.0183
39041.5434 | 1985 | 0 | 39041.5434 | 1822 | 0 |  | 496 | 703 | 121.1844 | 0 | 111.2332 | 0 | 1.2118 | 0 | 1.1123 | 0 | 1.2118 | 1.1123 | 28.6841 | 40.1965 | 27.4723
39041.5439 | 2388 | 0 | 39041.5439 | 2176 | 0 |  | 538 | 745 | 145.7875 | 0 | 132.8449 | 0 | 1.4579 | 0 | 1.3284 | 0 | 1.4579 | 1.3284 | 6.9673 | 17.3888 | 5.5095
39041.5444 | 2132 | 0 | 39041.5444 | 1905 | 0 |  | 580 | 787 | 130.1587 | 0 | 116.3004 | 0 | 1.3016 | 0 | 1.163 | 0 | 1.3016 | 1.163 | 19.8114 | 34.0882 | 18.5099
39041.5449 | 2165 | 0 | 39041.5449 | 2157 | 0 |  | 622 | 829 | 132.1734 | 0 | 131.685 | 0 | 1.3217 | 0 | 1.3168 | 0 | 1.3217 | 1.3168 | 17.9852 | 18.4228 | 16.6635
39041.5454 | 1974 | 0 | 39041.5454 | 2320 | 0 |  | 664 | 871 | 120.5128 | 0 | 141.6361 | 0 | 1.2051 | 0 | 1.4164 | 0 | 1.2051 | 1.4164 | 29.4012 | 10.1026 | 28.1961
39041.5459 | 2493 | 0 | 39041.5459 | 1866 | 0 |  | 706 | 913 | 152.1978 | 0 | 113.9194 | 0 | 1.522 | 0 | 1.1392 | 0 | 1.522 | 1.1392 | 2.4621 | 36.8907 | 0.94012
39041.5463 | 2282 | 0 | 39041.5464 | 2115 | 0 |  | 748 | 955 | 139.3162 | 0 | 129.1209 | 0 | 1.3932 | 0 | 1.2912 | 0 | 1.3932 | 1.2912 | 11.936 | 20.7745 | 10.5429
39041.5468 | 1973 | 0 | 39041.5469 | 1939 | 0 |  | 790 | 997 | 120.4518 | 0 | 118.3761 | 0 | 1.2045 | 0 | 1.1838 | 0 | 1.2045 | 1.1838 | 29.4668 | 31.737 | 28.2623
39041.5473 | 2422 | 0 | 39041.5473 | 2139 | 0 |  | 832 | 1039 | 147.8632 | 0 | 130.5861 | 0 | 1.4786 | 0 | 1.3059 | 0 | 1.4786 | 1.3059 | 5.4657 | 19.4194 | 3.9871
39041.5478 | 2158 | 0 | 39041.5478 | 2382 | 0 |  | 874 | 1081 | 131.746 | 0 | 145.4212 | 0 | 1.3175 | 0 | 1.4542 | 0 | 1.3175 | 1.4542 | 18.3679 | 7.2368 | 17.0505
39041.5483 | 2538 | 0 | 39041.5483 | 2512 | 0 |  | 916 | 1123 | 154.9451 | 0 | 153.3578 | 0 | 1.5495 | 0 | 1.5336 | 0 | 1.5495 | 1.5336 | 0.64539 | 1.6871 | 0.90406
39041.5488 | 2515 | 0 | 39041.5488 | 2390 | 0 |  | 958 | 1165 | 153.5409 | 0 | 145.9096 | 0 | 1.5354 | 0 | 1.4591 | 0 | 1.5354 | 1.4591 | 1.5658 | 6.8778 | 0.030396
39041.5493 | 2243 | 0 | 39041.5493 | 2039 | 0 |  | 1000 | 1207 | 136.9353 | 0 | 124.4811 | 0 | 1.3694 | 0 | 1.2448 | 0 | 1.3694 | 1.2448 | 13.8823 | 25.2761 | 12.5129
39041.5497 | 2239 | 0 | 39041.5498 | 2132 | 0 |  | 1042 | 1249 | 136.6911 | 0 | 130.1587 | 0 | 1.3669 | 0 | 1.3016 | 0 | 1.3669 | 1.3016 | 14.0858 | 19.8114 | 12.7188

## B3-C5
Open Burn Test 11 |  |  | 2006-11-20 | 12:58 |  |  | Vs = |  | 156.5556 |  | R = | 100
Mixed | 7-C | Tray C | IRMS | 2
0 | 250 kW |  | Bundle | Ch. 3 & 5 | Cable B | Odd - | Cable C |  | Odd
Time-21 | N11 | N12 | Time-22 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R5-G | R3-5
39041.5356 | 0 | 0 | 39041.5356 | 0 | 0 |  | -178.5 | 28.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 512776 | 512776 | 512775.9997
39041.5361 | 0 | 0 | 39041.5361 | 0 | 0 |  | -136.5 | 70.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 512776 | 512776 | 512775.9997
39041.5366 | 0 | 0 | 39041.5366 | 0 | 0 |  | -94.5 | 112.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 512776 | 512776 | 512775.9997
39041.5371 | 0 | 0 | 39041.5371 | 0 | 0 |  | -52.5 | 154.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 512776 | 512776 | 512775.9997
39041.5376 | 0 | 0 | 39041.5376 | 0 | 0 |  | -10.5 | 196.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 512776 | 512776 | 512775.9997
39041.5381 | 0 | 0 | 39041.5381 | 0 | 0 |  | 31.5 | 238.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 512776 | 512776 | 512775.9997
39041.5385 | 0 | 0 | 39041.5386 | 0 | 0 |  | 73.5 | 280.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 512776 | 512776 | 512775.9997
39041.539 | 0 | 0 | 39041.539 | 0 | 0 |  | 115.5 | 322.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 512776 | 512776 | 512775.9997
39041.5395 | 0 | 0 | 39041.5395 | 0 | 0 |  | 157.5 | 364.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 512776 | 512776 | 512775.9997
39041.54 | 0 | 0 | 39041.54 | 0 | 0 |  | 199.5 | 406.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 512776 | 512776 | 512775.9997
39041.5405 | 0 | 0 | 39041.5405 | 0 | 0 |  | 241.5 | 448.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 512776 | 512776 | 512775.9997
39041.541 | 0 | 0 | 39041.541 | 0 | 0 |  | 283.5 | 490.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 512776 | 512776 | 512775.9997
39041.5415 | 0 | 0 | 39041.5415 | 0 | 0 |  | 325.5 | 532.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 512776 | 512776 | 512775.9997
39041.5419 | 0 | 0 | 39041.542 | 5 | 0 |  | 367.5 | 574.5 | 0.030525 | 0 | 0.30525 | 0 | 0.00030525 | 0 | 0.0030525 | 0 | 0.00030525 | 0.0030525 | 512776 | 51187.6 | 512775.9997
39041.5424 | 0 | 0 | 39041.5424 | 988 | 0 |  | 409.5 | 616.5 | 0.030525 | 0 | 60.3175 | 0 | 0.00030525 | 0 | 0.60317 | 0 | 0.00030525 | 0.60317 | 512776 | 159.5526 | 512775.9997
39041.5429 | 411 | 0 | 39041.5429 | 1869 | 0 |  | 451.5 | 658.5 | 25.0916 | 0 | 114.1026 | 0 | 0.25092 | 0 | 1.141 | 0 | 0.25092 | 1.141 | 523.9367 | 37.206 | 523.6858
39041.5434 | 2379 | 0 | 39041.5434 | 2478 | 0 |  | 493 | 700 | 145.2381 | 0 | 151.2821 | 0 | 1.4524 | 0 | 1.5128 | 0 | 1.4524 | 1.5128 | 7.7923 | 3.4859 | 6.34
39041.5439 | 1909 | 0 | 39041.5439 | 1732 | 0 |  | 535 | 742 | 116.5446 | 0 | 105.7387 | 0 | 1.1654 | 0 | 1.0574 | 0 | 1.1654 | 1.0574 | 34.3311 | 48.0589 | 33.1656
39041.5444 | 2069 | 0 | 39041.5444 | 1912 | 0 |  | 577 | 784 | 126.3126 | 0 | 116.7277 | 0 | 1.2631 | 0 | 1.1673 | 0 | 1.2631 | 1.1673 | 23.943 | 34.1203 | 22.6798
39041.5448 | 2046 | 0 | 39041.5449 | 2393 | 0 |  | 619 | 826 | 124.9084 | 0 | 146.0928 | 0 | 1.2491 | 0 | 1.4609 | 0 | 1.2491 | 1.4609 | 25.3363 | 7.1617 | 24.0872
39041.5453 | 2116 | 0 | 39041.5454 | 2079 | 0 |  | 661.5 | 868.5 | 129.1819 | 0 | 126.9231 | 0 | 1.2918 | 0 | 1.2692 | 0 | 1.2918 | 1.2692 | 21.19 | 23.3468 | 19.8982
39041.5458 | 2309 | 0 | 39041.5458 | 2054 | 0 |  | 703.5 | 910.5 | 140.9646 | 0 | 125.3968 | 0 | 1.4096 | 0 | 1.254 | 0 | 1.4096 | 1.254 | 11.0602 | 24.8481 | 9.6506
39041.5463 | 2523 | 0 | 39041.5463 | 2003 | 0 |  | 745 | 952 | 154.0293 | 0 | 122.2833 | 0 | 1.5403 | 0 | 1.2228 | 0 | 1.5403 | 1.2228 | 1.6401 | 28.027 | 0.099818
39041.5468 | 2204 | 0 | 39041.5468 | 2459 | 0 |  | 787.5 | 994.5 | 134.5543 | 0 | 150.1221 | 0 | 1.3455 | 0 | 1.5012 | 0 | 1.3455 | 1.5012 | 16.3512 | 4.2855 | 15.0056
39041.5473 | 2111 | 0 | 39041.5473 | 2112 | 0 |  | 829.5 | 1036.5 | 128.8767 | 0 | 128.9377 | 0 | 1.2888 | 0 | 1.2894 | 0 | 1.2888 | 1.2894 | 21.477 | 21.4195 | 20.1883
39041.5478 | 2266 | 0 | 39041.5478 | 2548 | 0 |  | 871 | 1078 | 138.3394 | 0 | 155.5556 | 0 | 1.3834 | 0 | 1.5556 | 0 | 1.3834 | 1.5556 | 13.1677 | 0.64286 | 11.7843
39041.5483 | 2358 | 0 | 39041.5483 | 2059 | 0 |  | 913 | 1120 | 143.956 | 0 | 125.7021 | 0 | 1.4396 | 0 | 1.257 | 0 | 1.4396 | 1.257 | 8.7523 | 24.5449 | 7.3128
39041.5487 | 2343 | 0 | 39041.5488 | 1939 | 0 |  | 955 | 1162 | 143.0403 | 0 | 118.3761 | 0 | 1.4304 | 0 | 1.1838 | 0 | 1.4304 | 1.1838 | 9.4486 | 32.2527 | 8.0182
39041.5492 | 2026 | 0 | 39041.5492 | 2298 | 0 |  | 997 | 1204 | 123.6874 | 0 | 140.293 | 0 | 1.2369 | 0 | 1.4029 | 0 | 1.2369 | 1.4029 | 26.5735 | 11.5918 | 25.3367
39041.5497 | 2351 | 0 | 39041.5497 | 1904 | 0 |  | 1039 | 1246 | 143.5287 | 0 | 116.2393 | 0 | 1.4353 | 0 | 1.1624 | 0 | 1.4353 | 1.1624 | 9.0761 | 34.6838 | 7.6409

## B3-B4
Open Burn Test 11 |  |  | 2006-11-20 | 12:58 |  |  | Vs = |  | 156.5556 |  | R = | 100
Mixed | 7-C | Tray C | IRMS | 2
0 | 250 kW |  | Bundle | Ch. 3 & 4 | Cable B | Odd -Even
Time-19 | N11 | N12 | Time-20 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R4-G | R3-4
39041.5356 | 0 | 0 | 39041.5356 | 0 | 0 |  | -181.5 | 25.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 512776 | 512776 | 512775.9997
39041.5361 | 0 | 0 | 39041.5361 | 0 | 0 |  | -139.5 | 67.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 512776 | 512776 | 512775.9997
39041.5366 | 0 | 0 | 39041.5366 | 0 | 0 |  | -97.5 | 109.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 512776 | 512776 | 512775.9997
39041.537 | 0 | 0 | 39041.5371 | 0 | 0 |  | -55.5 | 151.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 512776 | 512776 | 512775.9997
39041.5375 | 0 | 0 | 39041.5375 | 0 | 0 |  | -13.5 | 193.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 512776 | 512776 | 512775.9997
39041.538 | 0 | 0 | 39041.538 | 0 | 0 |  | 28.5 | 235.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 512776 | 512776 | 512775.9997
39041.5385 | 0 | 0 | 39041.5385 | 0 | 0 |  | 70.5 | 277.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 512776 | 512776 | 512775.9997
39041.539 | 0 | 0 | 39041.539 | 0 | 0 |  | 112.5 | 319.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 512776 | 512776 | 512775.9997
39041.5395 | 0 | 0 | 39041.5395 | 0 | 0 |  | 154.5 | 361.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 512776 | 512776 | 512775.9997
39041.54 | 0 | 0 | 39041.54 | 0 | 0 |  | 196.5 | 403.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 512776 | 512776 | 512775.9997
39041.5405 | 0 | 0 | 39041.5405 | 0 | 0 |  | 238.5 | 445.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 512776 | 512776 | 512775.9997
39041.5409 | 0 | 0 | 39041.5409 | 0 | 0 |  | 280.5 | 487.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 512776 | 512776 | 512775.9997
39041.5414 | 0 | 0 | 39041.5414 | 0 | 0 |  | 322.5 | 529.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 512776 | 512776 | 512775.9997
39041.5419 | 0 | 0 | 39041.5419 | 0 | 0 |  | 364.5 | 571.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 512776 | 512776 | 512775.9997
39041.5424 | 12 | 4 | 39041.5424 | 35 | 16 |  | 406.5 | 613.5 | 0.7326 | 0.2442 | 2.1368 | 0.9768 | 0.007326 | 0.002442 | 0.021368 | 0.009768 | 0.004884 | 0.0116 | 32024.7141 | 13347.6245 | 63235.7397
39041.5429 | 951 | 572 | 39041.5429 | 940 | 628 |  | 448.5 | 655.5 | 58.0586 | 34.9206 | 57.3871 | 38.3394 | 0.58059 | 0.34921 | 0.57387 | 0.38339 | 0.23138 | 0.19048 | 517.3034 | 852.2401 | 162.9404
39041.5434 | 1872 | 23 | 39041.5434 | 2252 | 15 |  | 490.5 | 697.5 | 114.2857 | 1.4042 | 137.4847 | 0.91575 | 1.1429 | 0.014042 | 1.3748 | 0.0091575 | 1.1288 | 1.3657 | 41.0425 | 14.1962 | 361.7967
39041.5439 | 2169 | 4 | 39041.5439 | 2128 | 4 |  | 532.5 | 739.5 | 132.4176 | 0.2442 | 129.9145 | 0.2442 | 1.3242 | 0.002442 | 1.2991 | 0.002442 | 1.3217 | 1.2967 | 18.4264 | 20.7573 | 1681.8873
39041.5443 | 2430 | 2 | 39041.5444 | 2381 | 3 |  | 574.5 | 781.5 | 148.3516 | 0.1221 | 145.3602 | 0.18315 | 1.4835 | 0.001221 | 1.4536 | 0.0018315 | 1.4823 | 1.4518 | 5.593 | 7.8895 | 484.0181
39041.5448 | 2315 | 1 | 39041.5448 | 2222 | 1 |  | 616.5 | 823.5 | 141.3309 | 0.06105 | 135.6532 | 0.06105 | 1.4133 | 0.0006105 | 1.3565 | 0.0006105 | 1.4127 | 1.3559 | 10.8072 | 15.4801 | 3329.527
39041.5453 | 2340 | 1 | 39041.5453 | 2537 | 1 |  | 658.5 | 865.5 | 142.8571 | 0.06105 | 154.884 | 0.06105 | 1.4286 | 0.0006105 | 1.5488 | 0.0006105 | 1.428 | 1.5482 | 9.9869 | 1.0839 | 239.5325
39041.5458 | 2029 | 0 | 39041.5458 | 2319 | 0 |  | 700.5 | 907.5 | 123.8706 | 0 | 141.5751 | 0 | 1.2387 | 0 | 1.4158 | 0 | 1.2387 | 1.4158 | 26.3864 | 10.5813 | 25.1477
39041.5463 | 2166 | 0 | 39041.5463 | 2507 | 1 |  | 742.5 | 949.5 | 132.2344 | 0 | 153.0525 | 0.06105 | 1.3223 | 0 | 1.5305 | 0.0006105 | 1.3223 | 1.5299 | 18.3924 | 2.3296 | 17.0701
39041.5468 | 1986 | 0 | 39041.5468 | 2301 | 0 |  | 784.5 | 991.5 | 121.2454 | 0 | 140.4762 | 0 | 1.2125 | 0 | 1.4048 | 0 | 1.2125 | 1.4048 | 29.1229 | 11.4463 | 27.9104
39041.5473 | 2155 | 0 | 39041.5473 | 2526 | 1 |  | 826.5 | 1033.5 | 131.5629 | 0 | 154.2125 | 0.06105 | 1.3156 | 0 | 1.5421 | 0.0006105 | 1.3156 | 1.5415 | 18.9968 | 1.5596 | 17.6811
39041.5477 | 2548 | 0 | 39041.5478 | 2039 | 0 |  | 868.5 | 1075.5 | 155.5556 | 0 | 124.4811 | 0 | 1.5556 | 0 | 1.2448 | 0 | 1.5556 | 1.2448 | 0.64286 | 25.7666 | 0.9127
39041.5482 | 2537 | 0 | 39041.5482 | 2199 | 0 |  | 910.5 | 1117.5 | 154.884 | 0 | 134.2491 | 0 | 1.5488 | 0 | 1.3425 | 0 | 1.5488 | 1.3425 | 1.0792 | 16.6157 | 0.46961
39041.5487 | 2413 | 1 | 39041.5487 | 2360 | 0 |  | 952.5 | 1159.5 | 147.3138 | 0.06105 | 144.0781 | 0 | 1.4731 | 0.0006105 | 1.4408 | 0 | 1.4725 | 1.4408 | 6.3063 | 8.6602 | 1198.5222
39041.5492 | 2295 | 4 | 39041.5492 | 2294 | 3 |  | 994.5 | 1201.5 | 140.1099 | 0.2442 | 140.0488 | 0.18315 | 1.4011 | 0.002442 | 1.4005 | 0.0018315 | 1.3987 | 1.3987 | 11.9328 | 11.9328 | 707.2819
39041.5497 | 2078 | 20 | 39041.5497 | 1985 | 22 |  | 1036.5 | 1243.5 | 126.862 | 1.221 | 121.1844 | 1.3431 | 1.2686 | 0.01221 | 1.2118 | 0.013431 | 1.2564 | 1.1984 | 24.4001 | 30.936 | 550.9531

## A2-C6
Open Burn Test 11 |  |  | 2006-11-20 | 12:58 |  |  | Vs = |  | 159.1807 |  | R = | 100
Mixed | 7-C | Tray C | IRMS | 2
0 | 250 kW |  | Bundle | Ch. 2 & 6 | Cable A | Even - | Cable C |  | Even
Time-17 | N11 | N12 | Time-18 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R6-G | R2-6
39041.5356 | 0 | 0 | 39041.5356 | 0 | 0 |  | -184.5 | 22.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 521376 | 521376 | 521375.9997
39041.536 | 0 | 0 | 39041.5361 | 0 | 0 |  | -142.5 | 64.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 521376 | 521376 | 521375.9997
39041.5365 | 0 | 0 | 39041.5365 | 0 | 0 |  | -100.5 | 106.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 521376 | 521376 | 521375.9997
39041.537 | 0 | 0 | 39041.537 | 0 | 0 |  | -58.5 | 148.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 521376 | 521376 | 521375.9997
39041.5375 | 0 | 0 | 39041.5375 | 0 | 0 |  | -16.5 | 190.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 521376 | 521376 | 521375.9997
39041.538 | 0 | 0 | 39041.538 | 0 | 0 |  | 25.5 | 232.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 521376 | 521376 | 521375.9997
39041.5385 | 0 | 0 | 39041.5385 | 0 | 0 |  | 67.5 | 274.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 521376 | 521376 | 521375.9997
39041.539 | 0 | 0 | 39041.539 | 0 | 0 |  | 109.5 | 316.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 521376 | 521376 | 521375.9997
39041.5394 | 0 | 0 | 39041.5395 | 0 | 0 |  | 151.5 | 358.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 521376 | 521376 | 521375.9997
39041.5399 | 0 | 0 | 39041.5399 | 0 | 0 |  | 193.5 | 400.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 521376 | 521376 | 521375.9997
39041.5404 | 0 | 0 | 39041.5404 | 0 | 0 |  | 235.5 | 442.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 521376 | 521376 | 521375.9997
39041.5409 | 0 | 0 | 39041.5409 | 0 | 0 |  | 277.5 | 484.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 521376 | 521376 | 521375.9997
39041.5414 | 2046 | 1 | 39041.5414 | 0 | 0 |  | 319.5 | 526.5 | 124.9084 | 0.06105 | 0.030525 | 0 | 1.2491 | 0.0006105 | 0.00030525 | 0 | 1.2485 | 0.00030525 | 27.4513 | 521375.9995 | 56027.254
39041.5419 | 2591 | 1 | 39041.5419 | 1 | 0 |  | 361.5 | 568.5 | 158.1807 | 0.06105 | 0.06105 | 0 | 1.5818 | 0.0006105 | 0.0006105 | 0 | 1.5812 | 0.0006105 | 0.63243 | 260638.0001 | 1537.4101
39041.5424 | 2365 | 0 | 39041.5424 | 1363 | 0 |  | 403.5 | 610.5 | 144.3834 | 0 | 83.2112 | 0 | 1.4438 | 0 | 0.83211 | 0 | 1.4438 | 0.83211 | 10.2486 | 91.2971 | 8.8048
39041.5428 | 2377 | 0 | 39041.5429 | 1661 | 0 |  | 445.5 | 652.5 | 145.116 | 0 | 101.4042 | 0 | 1.4512 | 0 | 1.014 | 0 | 1.4512 | 1.014 | 9.692 | 56.9765 | 8.2409
39041.5433 | 2047 | 0 | 39041.5433 | 1871 | 0 |  | 487.5 | 694.5 | 124.9695 | 0 | 114.2247 | 0 | 1.2497 | 0 | 1.1422 | 0 | 1.2497 | 1.1422 | 27.3757 | 39.3576 | 26.126
39041.5438 | 2074 | 0 | 39041.5438 | 2052 | 0 |  | 529.5 | 736.5 | 126.6178 | 0 | 125.2747 | 0 | 1.2662 | 0 | 1.2527 | 0 | 1.2662 | 1.2527 | 25.7175 | 27.0653 | 24.4513
39041.5443 | 2200 | 0 | 39041.5443 | 1592 | 0 |  | 571.5 | 778.5 | 134.3101 | 0 | 97.1917 | 0 | 1.3431 | 0 | 0.97192 | 0 | 1.3431 | 0.97192 | 18.5173 | 63.7802 | 17.1742
39041.5448 | 2540 | 0 | 39041.5448 | 2222 | 0 |  | 613.5 | 820.5 | 155.0672 | 0 | 135.6532 | 0 | 1.5507 | 0 | 1.3565 | 0 | 1.5507 | 1.3565 | 2.6528 | 17.3438 | 1.1021
39041.5453 | 2256 | 0 | 39041.5453 | 1841 | 0 |  | 655.5 | 862.5 | 137.7289 | 0 | 112.3932 | 0 | 1.3773 | 0 | 1.1239 | 0 | 1.3773 | 1.1239 | 15.5754 | 41.6285 | 14.1981
39041.5458 | 2532 | 0 | 39041.5458 | 2051 | 0 |  | 697.5 | 904.5 | 154.5788 | 0 | 125.2137 | 0 | 1.5458 | 0 | 1.2521 | 0 | 1.5458 | 1.2521 | 2.9771 | 27.1273 | 1.4313
39041.5462 | 2499 | 0 | 39041.5463 | 2264 | 0 |  | 739.5 | 946.5 | 152.5641 | 0 | 138.2173 | 0 | 1.5256 | 0 | 1.3822 | 0 | 1.5256 | 1.3822 | 4.3369 | 15.167 | 2.8113
39041.5467 | 2455 | 0 | 39041.5467 | 2370 | 0 |  | 781.5 | 988.5 | 149.8779 | 0 | 144.6886 | 0 | 1.4988 | 0 | 1.4469 | 0 | 1.4988 | 1.4469 | 6.2069 | 10.016 | 4.7081
39041.5472 | 2070 | 0 | 39041.5472 | 1945 | 0 |  | 823.5 | 1030.5 | 126.3736 | 0 | 118.7424 | 0 | 1.2637 | 0 | 1.1874 | 0 | 1.2637 | 1.1874 | 25.9604 | 34.0555 | 24.6967
39041.5477 | 2198 | 0 | 39041.5477 | 2471 | 0 |  | 865.5 | 1072.5 | 134.188 | 0 | 150.8547 | 0 | 1.3419 | 0 | 1.5085 | 0 | 1.3419 | 1.5085 | 18.6251 | 5.5192 | 17.2832
39041.5482 | 2120 | 0 | 39041.5482 | 2078 | 0 |  | 907.5 | 1114.5 | 129.4261 | 0 | 126.862 | 0 | 1.2943 | 0 | 1.2686 | 0 | 1.2943 | 1.2686 | 22.9896 | 25.4755 | 21.6954
39041.5487 | 2203 | 0 | 39041.5487 | 2163 | 0 |  | 949.5 | 1156.5 | 134.4933 | 0 | 132.0513 | 0 | 1.3449 | 0 | 1.3205 | 0 | 1.3449 | 1.3205 | 18.3559 | 20.5446 | 17.0109
39041.5492 | 2503 | 0 | 39041.5492 | 2376 | 0 |  | 991.5 | 1198.5 | 152.8083 | 0 | 145.0549 | 0 | 1.5281 | 0 | 1.4505 | 0 | 1.5281 | 1.4505 | 4.1702 | 9.7382 | 2.6421
39041.5497 | 1865 | 1 | 39041.5497 | 1901 | 0 |  | 1033.5 | 1240.5 | 113.8584 | 0.06105 | 116.0562 | 0 | 1.1386 | 0.0006105 | 1.1606 | 0 | 1.138 | 1.1606 | 39.8848 | 37.1583 | 20085.1431

## A2-C5
Open Burn Test 11 |  |  | 2006-11-20 | 12:58 |  |  | Vs = |  | 156.0672 |  | R = | 100
Mixed | 7-C | Tray C | IRMS | 2
0 | 250 kW |  | Bundle | Ch. 2 & 5 | Cable A | Even - | Cable C |  | Odd
Time-15 | N11 | N12 | Time-16 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R5-G | R2-5
39041.5355 | 0 | 0 | 39041.5355 | 0 | 0 |  | -187 | 20 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511176 | 511176 | 511175.9997
39041.536 | 0 | 0 | 39041.536 | 0 | 0 |  | -145 | 62 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511176 | 511176 | 511175.9997
39041.5365 | 0 | 0 | 39041.5365 | 0 | 0 |  | -103 | 104 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511176 | 511176 | 511175.9997
39041.537 | 0 | 0 | 39041.537 | 0 | 0 |  | -61 | 146 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511176 | 511176 | 511175.9997
39041.5375 | 0 | 0 | 39041.5375 | 0 | 0 |  | -19 | 188 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511176 | 511176 | 511175.9997
39041.538 | 0 | 0 | 39041.538 | 0 | 0 |  | 23 | 230 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511176 | 511176 | 511175.9997
39041.5384 | 0 | 0 | 39041.5385 | 0 | 0 |  | 65 | 272 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511176 | 511176 | 511175.9997
39041.5389 | 0 | 0 | 39041.5389 | 0 | 0 |  | 107 | 314 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511176 | 511176 | 511175.9997
39041.5394 | 0 | 0 | 39041.5394 | 0 | 0 |  | 149 | 356 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511176 | 511176 | 511175.9997
39041.5399 | 0 | 0 | 39041.5399 | 0 | 0 |  | 191 | 398 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511176 | 511176 | 511175.9997
39041.5404 | 0 | 0 | 39041.5404 | 0 | 0 |  | 233 | 440 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511176 | 511176 | 511175.9997
39041.5409 | 0 | 0 | 39041.5409 | 0 | 0 |  | 275 | 482 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511176 | 511176 | 511175.9997
39041.5414 | 2464 | 1 | 39041.5414 | 0 | 0 |  | 317 | 524 | 150.4274 | 0.06105 | 0.030525 | 0 | 1.5043 | 0.0006105 | 0.00030525 | 0 | 1.5037 | 0.00030525 | 3.7507 | 511176.0007 | 9136.2127
39041.5418 | 2290 | 1 | 39041.5419 | 1 | 0 |  | 359 | 566 | 139.8046 | 0.06105 | 0.06105 | 0 | 1.398 | 0.0006105 | 0.0006105 | 0 | 1.3974 | 0.0006105 | 11.6374 | 255538 | 26527.6189
39041.5423 | 1976 | 0 | 39041.5423 | 1096 | 0 |  | 401 | 608 | 120.6349 | 0 | 66.9109 | 0 | 1.2063 | 0 | 0.66911 | 0 | 1.2063 | 0.66911 | 29.3715 | 133.2464 | 28.1651
39041.5428 | 2049 | 0 | 39041.5428 | 1420 | 0 |  | 443 | 650 | 125.0916 | 0 | 86.6911 | 0 | 1.2509 | 0 | 0.86691 | 0 | 1.2509 | 0.86691 | 24.7623 | 80.0268 | 23.5114
39041.5433 | 2220 | 0 | 39041.5433 | 1716 | 0 |  | 484.5 | 691.5 | 135.5311 | 0 | 104.7619 | 0 | 1.3553 | 0 | 1.0476 | 0 | 1.3553 | 1.0476 | 15.1523 | 48.9732 | 13.7969
39041.5438 | 2121 | 0 | 39041.5438 | 1422 | 0 |  | 526.5 | 733.5 | 129.4872 | 0 | 86.8132 | 0 | 1.2949 | 0 | 0.86813 | 0 | 1.2949 | 0.86813 | 20.5271 | 79.7736 | 19.2322
39041.5443 | 2245 | 0 | 39041.5443 | 2050 | 0 |  | 569 | 776 | 137.0574 | 0 | 125.1526 | 0 | 1.3706 | 0 | 1.2515 | 0 | 1.3706 | 1.2515 | 13.8699 | 24.7015 | 12.4994
39041.5448 | 2356 | 0 | 39041.5448 | 2436 | 0 |  | 610.5 | 817.5 | 143.8339 | 0 | 148.7179 | 0 | 1.4383 | 0 | 1.4872 | 0 | 1.4383 | 1.4872 | 8.5051 | 4.9417 | 7.0668
39041.5452 | 2099 | 0 | 39041.5453 | 2425 | 0 |  | 653 | 860 | 128.1441 | 0 | 148.0464 | 0 | 1.2814 | 0 | 1.4805 | 0 | 1.2814 | 1.4805 | 21.7904 | 5.4177 | 20.5089
39041.5457 | 2196 | 0 | 39041.5457 | 2404 | 0 |  | 694.5 | 901.5 | 134.0659 | 0 | 146.7643 | 0 | 1.3407 | 0 | 1.4676 | 0 | 1.3407 | 1.4676 | 16.4107 | 6.3386 | 15.0701
39041.5462 | 2362 | 0 | 39041.5462 | 2010 | 0 |  | 736.5 | 943.5 | 144.2002 | 0 | 122.7106 | 0 | 1.442 | 0 | 1.2271 | 0 | 1.442 | 1.2271 | 8.2295 | 27.1831 | 6.7875
39041.5467 | 2540 | 0 | 39041.5467 | 2426 | 0 |  | 778.5 | 985.5 | 155.0672 | 0 | 148.1074 | 0 | 1.5507 | 0 | 1.4811 | 0 | 1.5507 | 1.4811 | 0.64488 | 5.3743 | 0.90579
39041.5472 | 2194 | 0 | 39041.5472 | 2529 | 0 |  | 820.5 | 1027.5 | 133.9438 | 0 | 154.3956 | 0 | 1.3394 | 0 | 1.544 | 0 | 1.3394 | 1.544 | 16.5169 | 1.0826 | 15.1774
39041.5477 | 2209 | 0 | 39041.5477 | 2446 | 0 |  | 862.5 | 1069.5 | 134.8596 | 0 | 149.3284 | 0 | 1.3486 | 0 | 1.4933 | 0 | 1.3486 | 1.4933 | 15.7257 | 4.5127 | 14.3771
39041.5482 | 2362 | 0 | 39041.5482 | 2015 | 0 |  | 904.5 | 1111.5 | 144.2002 | 0 | 123.0159 | 0 | 1.442 | 0 | 1.2302 | 0 | 1.442 | 1.2302 | 8.2295 | 26.8675 | 6.7875
39041.5486 | 2107 | 0 | 39041.5487 | 1927 | 0 |  | 946.5 | 1153.5 | 128.6325 | 0 | 117.6435 | 0 | 1.2863 | 0 | 1.1764 | 0 | 1.2863 | 1.1764 | 21.328 | 32.6611 | 20.0416
39041.5491 | 2426 | 0 | 39041.5491 | 2001 | 1 |  | 988.5 | 1195.5 | 148.1074 | 0 | 122.1612 | 0.06105 | 1.4811 | 0 | 1.2216 | 0.0006105 | 1.4811 | 1.221 | 5.3743 | 27.819 | 3.8932
39041.5496 | 1963 | 1 | 39041.5496 | 2015 | 1 |  | 1030.5 | 1237.5 | 119.8413 | 0.06105 | 123.0159 | 0.06105 | 1.1984 | 0.0006105 | 1.2302 | 0.0006105 | 1.1978 | 1.2295 | 30.301 | 26.925 | 12566.3268

## A2-B4
Open Burn Test 11 |  |  | 2006-11-20 | 12:58 |  |  | Vs = |  | 158.6923 |  | R = | 100
Mixed | 7-C | Tray C | IRMS | 2
0 | 250 kW |  | Bundle | Ch. 2 & 4 | Cable A | Even - | Cable B |  | Even
Time-13 | N11 | N12 | Time-14 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R4-G | R2-4
39041.5355 | 0 | 0 | 39041.5355 | 0 | 0 |  | -190 | 17 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 519776 | 519776 | 519775.9997
39041.536 | 0 | 0 | 39041.536 | 0 | 0 |  | -148 | 59 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 519776 | 519776 | 519775.9997
39041.5365 | 0 | 0 | 39041.5365 | 0 | 0 |  | -106 | 101 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 519776 | 519776 | 519775.9997
39041.5369 | 0 | 0 | 39041.537 | 0 | 0 |  | -64 | 143 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 519776 | 519776 | 519775.9997
39041.5374 | 0 | 0 | 39041.5375 | 0 | 0 |  | -22 | 185 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 519776 | 519776 | 519775.9997
39041.5379 | 0 | 0 | 39041.5379 | 0 | 0 |  | 20 | 227 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 519776 | 519776 | 519775.9997
39041.5384 | 0 | 0 | 39041.5384 | 0 | 0 |  | 62 | 269 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 519776 | 519776 | 519775.9997
39041.5389 | 0 | 0 | 39041.5389 | 0 | 0 |  | 104 | 311 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 519776 | 519776 | 519775.9997
39041.5394 | 0 | 0 | 39041.5394 | 0 | 0 |  | 146 | 353 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 519776 | 519776 | 519775.9997
39041.5399 | 0 | 0 | 39041.5399 | 0 | 0 |  | 188 | 395 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 519776 | 519776 | 519775.9997
39041.5403 | 0 | 0 | 39041.5404 | 0 | 0 |  | 230 | 437 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 519776 | 519776 | 519775.9997
39041.5408 | 0 | 0 | 39041.5409 | 0 | 0 |  | 272 | 479 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 519776 | 519776 | 519775.9997
39041.5413 | 2402 | 0 | 39041.5413 | 2448 | 0 |  | 314 | 521 | 146.6422 | 0 | 149.4505 | 0 | 1.4664 | 0 | 1.4945 | 0 | 1.4664 | 1.4945 | 8.2173 | 6.1838 | 6.7509
39041.5418 | 2050 | 0 | 39041.5418 | 2323 | 0 |  | 356 | 563 | 125.1526 | 0 | 141.8193 | 0 | 1.2515 | 0 | 1.4182 | 0 | 1.2515 | 1.4182 | 26.799 | 11.8975 | 25.5475
39041.5423 | 2515 | 0 | 39041.5423 | 2096 | 0 |  | 398 | 605 | 153.5409 | 0 | 127.9609 | 0 | 1.5354 | 0 | 1.2796 | 0 | 1.5354 | 1.2796 | 3.3551 | 24.0162 | 1.8197
39041.5428 | 2116 | 0 | 39041.5428 | 2231 | 0 |  | 440 | 647 | 129.1819 | 0 | 136.2027 | 0 | 1.2918 | 0 | 1.362 | 0 | 1.2918 | 1.362 | 22.844 | 16.5119 | 21.5522
39041.5433 | 2095 | 0 | 39041.5433 | 2494 | 0 |  | 482 | 689 | 127.8999 | 0 | 152.2589 | 0 | 1.279 | 0 | 1.5226 | 0 | 1.279 | 1.5226 | 24.0754 | 4.2253 | 22.7964
39041.5437 | 2002 | 0 | 39041.5438 | 2306 | 0 |  | 524 | 731 | 122.2222 | 0 | 140.7814 | 0 | 1.2222 | 0 | 1.4078 | 0 | 1.2222 | 1.4078 | 29.8392 | 12.7225 | 28.6169
39041.5442 | 2114 | 0 | 39041.5443 | 2406 | 0 |  | 566 | 773 | 129.0598 | 0 | 146.8864 | 0 | 1.2906 | 0 | 1.4689 | 0 | 1.2906 | 1.4689 | 22.9603 | 8.0374 | 21.6697
39041.5447 | 2367 | 0 | 39041.5447 | 2256 | 0 |  | 608 | 815 | 144.5055 | 0 | 137.7289 | 0 | 1.4451 | 0 | 1.3773 | 0 | 1.4451 | 1.3773 | 9.8175 | 15.2207 | 8.3724
39041.5452 | 1987 | 0 | 39041.5452 | 2406 | 0 |  | 650 | 857 | 121.3065 | 0 | 146.8864 | 0 | 1.2131 | 0 | 1.4689 | 0 | 1.2131 | 1.4689 | 30.8193 | 8.0374 | 29.6063
39041.5457 | 2375 | 0 | 39041.5457 | 1985 | 0 |  | 692 | 899 | 144.9939 | 0 | 121.1844 | 0 | 1.4499 | 0 | 1.2118 | 0 | 1.4499 | 1.2118 | 9.4476 | 30.9511 | 7.9976
39041.5462 | 2579 | 0 | 39041.5462 | 2536 | 0 |  | 734 | 941 | 157.4481 | 0 | 154.823 | 0 | 1.5745 | 0 | 1.5482 | 0 | 1.5745 | 1.5482 | 0.79023 | 2.4992 | 0.78425
39041.5467 | 1970 | 0 | 39041.5467 | 2296 | 0 |  | 776 | 983 | 120.2686 | 0 | 140.1709 | 0 | 1.2027 | 0 | 1.4017 | 0 | 1.2027 | 1.4017 | 31.9482 | 13.2134 | 30.7455
39041.5472 | 2140 | 0 | 39041.5472 | 2574 | 0 |  | 818 | 1025 | 130.6471 | 0 | 157.1429 | 0 | 1.3065 | 0 | 1.5714 | 0 | 1.3065 | 1.5714 | 21.4664 | 0.98601 | 20.1599
39041.5476 | 2583 | 0 | 39041.5477 | 2553 | 0 |  | 860 | 1067 | 157.6923 | 0 | 155.8608 | 0 | 1.5769 | 0 | 1.5586 | 0 | 1.5769 | 1.5586 | 0.63415 | 1.8167 | 0.94278
39041.5481 | 2569 | 0 | 39041.5481 | 2578 | 0 |  | 902 | 1109 | 156.8376 | 0 | 157.3871 | 0 | 1.5684 | 0 | 1.5739 | 0 | 1.5684 | 1.5739 | 1.1826 | 0.82933 | 0.38581
39041.5486 | 1994 | 0 | 39041.5486 | 2083 | 0 |  | 944 | 1151 | 121.7338 | 0 | 127.1673 | 0 | 1.2173 | 0 | 1.2717 | 0 | 1.2173 | 1.2717 | 30.3601 | 24.7902 | 29.1427
39041.5491 | 2389 | 0 | 39041.5491 | 2140 | 0 |  | 986 | 1193 | 145.8486 | 0 | 130.6471 | 0 | 1.4585 | 0 | 1.3065 | 0 | 1.4585 | 1.3065 | 8.8062 | 21.4664 | 7.3477
39041.5496 | 1967 | 0 | 39041.5496 | 2116 | 0 |  | 1028 | 1235 | 120.0855 | 0 | 129.1819 | 0 | 1.2009 | 0 | 1.2918 | 0 | 1.2009 | 1.2918 | 32.1495 | 22.844 | 30.9486

## A2-B3
Open Burn Test 11 |  |  | 2006-11-20 | 12:58 |  |  | Vs = |  | 159.9744 |  | R = | 100
Mixed | 7-C | Tray C | IRMS | 2
0 | 250 kW |  | Bundle | Ch. 2 & 3 | Cable A | Even - | Cable B |  | Odd
Time-11 | N11 | N12 | Time-12 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R3-G | R2-3
39041.5355 | 0 | 0 | 39041.5355 | 0 | 0 |  | -192.5 | 14.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 523976 | 523976 | 523975.9997
39041.5359 | 0 | 0 | 39041.536 | 0 | 0 |  | -150.5 | 56.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 523976 | 523976 | 523975.9997
39041.5364 | 0 | 0 | 39041.5364 | 0 | 0 |  | -108.5 | 98.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 523976 | 523976 | 523975.9997
39041.5369 | 0 | 0 | 39041.5369 | 0 | 0 |  | -66.5 | 140.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 523976 | 523976 | 523975.9997
39041.5374 | 0 | 0 | 39041.5374 | 0 | 0 |  | -24.5 | 182.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 523976 | 523976 | 523975.9997
39041.5379 | 0 | 0 | 39041.5379 | 0 | 0 |  | 17.5 | 224.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 523976 | 523976 | 523975.9997
39041.5384 | 0 | 0 | 39041.5384 | 0 | 0 |  | 59.5 | 266.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 523976 | 523976 | 523975.9997
39041.5389 | 0 | 0 | 39041.5389 | 0 | 0 |  | 101.5 | 308.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 523976 | 523976 | 523975.9997
39041.5394 | 0 | 0 | 39041.5394 | 0 | 0 |  | 143.5 | 350.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 523976 | 523976 | 523975.9997
39041.5398 | 0 | 0 | 39041.5398 | 0 | 0 |  | 185.5 | 392.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 523976 | 523976 | 523975.9997
39041.5403 | 0 | 0 | 39041.5403 | 0 | 0 |  | 227.5 | 434.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 523976 | 523976 | 523975.9997
39041.5408 | 0 | 0 | 39041.5408 | 0 | 0 |  | 269.5 | 476.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 523976 | 523976 | 523975.9997
39041.5413 | 1909 | 11 | 39041.5413 | 0 | 0 |  | 311 | 518 | 116.5446 | 0.67155 | 0.030525 | 0 | 1.1654 | 0.0067155 | 0.00030525 | 0 | 1.1587 | 0.00030525 | 37.4805 | 523976 | 6365.876
39041.5418 | 2604 | 1 | 39041.5418 | 0 | 0 |  | 353.5 | 560.5 | 158.9744 | 0.06105 | 0.030525 | 0 | 1.5897 | 0.0006105 | 0.00030525 | 0 | 1.5891 | 0.00030525 | 0.62927 | 523975.9993 | 1537.7065
39041.5423 | 2335 | 1 | 39041.5423 | 0 | 0 |  | 395 | 602 | 142.5519 | 0.06105 | 0.030525 | 0 | 1.4255 | 0.0006105 | 0.00030525 | 0 | 1.4249 | 0.00030525 | 12.2271 | 523976.0003 | 28432.5737
39041.5428 | 2581 | 1 | 39041.5428 | 166 | 0 |  | 437.5 | 644.5 | 157.5702 | 0.06105 | 10.1343 | 0 | 1.5757 | 0.0006105 | 0.10134 | 0 | 1.5751 | 0.10134 | 1.5264 | 1478.5422 | 3594.8643
39041.5432 | 2010 | 0 | 39041.5433 | 2121 | 0 |  | 479 | 686 | 122.7106 | 0 | 129.4872 | 0 | 1.2271 | 0 | 1.2949 | 0 | 1.2271 | 1.2949 | 30.3672 | 23.5446 | 29.1401
39041.5437 | 2545 | 0 | 39041.5437 | 2409 | 0 |  | 521 | 728 | 155.3724 | 0 | 147.0696 | 0 | 1.5537 | 0 | 1.4707 | 0 | 1.5537 | 1.4707 | 2.9619 | 8.7746 | 1.4082
39041.5442 | 2038 | 0 | 39041.5442 | 2488 | 0 |  | 563.5 | 770.5 | 124.42 | 0 | 151.8926 | 0 | 1.2442 | 0 | 1.5189 | 0 | 1.2442 | 1.5189 | 28.5761 | 5.3207 | 27.3319
39041.5447 | 2513 | 0 | 39041.5447 | 2005 | 0 |  | 605 | 812 | 153.4188 | 0 | 122.4054 | 0 | 1.5342 | 0 | 1.2241 | 0 | 1.5342 | 1.2241 | 4.273 | 30.6923 | 2.7388
39041.5452 | 2035 | 0 | 39041.5452 | 2253 | 0 |  | 647.5 | 854.5 | 124.2369 | 0 | 137.5458 | 0 | 1.2424 | 0 | 1.3755 | 0 | 1.2424 | 1.3755 | 28.7656 | 16.3063 | 27.5232
39041.5457 | 2408 | 0 | 39041.5457 | 2365 | 0 |  | 689 | 896 | 147.0085 | 0 | 144.3834 | 0 | 1.4701 | 0 | 1.4438 | 0 | 1.4701 | 1.4438 | 8.8198 | 10.7983 | 7.3497
39041.5461 | 2231 | 0 | 39041.5462 | 2242 | 0 |  | 731 | 938 | 136.2027 | 0 | 136.8742 | 0 | 1.362 | 0 | 1.3687 | 0 | 1.362 | 1.3687 | 17.4532 | 16.8769 | 16.0911
39041.5466 | 2439 | 0 | 39041.5467 | 2146 | 0 |  | 773 | 980 | 148.9011 | 0 | 131.0134 | 0 | 1.489 | 0 | 1.3101 | 0 | 1.489 | 1.3101 | 7.4367 | 22.1053 | 5.9476
39041.5471 | 1964 | 0 | 39041.5471 | 2551 | 0 |  | 815 | 1022 | 119.9023 | 0 | 155.7387 | 0 | 1.199 | 0 | 1.5574 | 0 | 1.199 | 1.5574 | 33.4206 | 2.7197 | 32.2215
39041.5476 | 2356 | 0 | 39041.5476 | 2331 | 0 |  | 857 | 1064 | 143.8339 | 0 | 142.3077 | 0 | 1.4383 | 0 | 1.4231 | 0 | 1.4383 | 1.4231 | 11.2216 | 12.4144 | 9.7832
39041.5481 | 2385 | 0 | 39041.5481 | 2128 | 0 |  | 899 | 1106 | 145.6044 | 0 | 129.9145 | 0 | 1.456 | 0 | 1.2991 | 0 | 1.456 | 1.2991 | 9.8692 | 23.1382 | 8.4131
39041.5486 | 2565 | 0 | 39041.5486 | 1994 | 0 |  | 941 | 1148 | 156.5934 | 0 | 121.7338 | 0 | 1.5659 | 0 | 1.2173 | 0 | 1.5659 | 1.2173 | 2.1591 | 31.4132 | 0.59313
39041.5491 | 2471 | 0 | 39041.5491 | 1955 | 0 |  | 983 | 1190 | 150.8547 | 0 | 119.3529 | 0 | 1.5085 | 0 | 1.1935 | 0 | 1.5085 | 1.1935 | 6.0453 | 34.0348 | 4.5368
39041.5495 | 2283 | 0 | 39041.5496 | 1991 | 0 |  | 1025 | 1232 | 139.3773 | 0 | 121.5507 | 0 | 1.3938 | 0 | 1.2155 | 0 | 1.3938 | 1.2155 | 14.7779 | 31.6113 | 13.3842

## A1-C6
Open Burn Test 11 |  |  | 2006-11-20 | 12:58 |  |  | Vs = |  | 158.5702 |  | R = | 100
Mixed | 7-C | Tray C | IRMS | 2
0 | 250 kW |  | Bundle | Ch. 1 & 6 | Cable A | Odd - | Cable C |  | Even
Time-9 | N11 | N12 | Time-10 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R6-G | R1-6
39041.5354 | 0 | 0 | 39041.5354 | 0 | 0 |  | -195.5 | 11.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 519376 | 519376 | 519375.9997
39041.5359 | 0 | 0 | 39041.5359 | 0 | 0 |  | -153.5 | 53.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 519376 | 519376 | 519375.9997
39041.5364 | 0 | 0 | 39041.5364 | 0 | 0 |  | -111.5 | 95.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 519376 | 519376 | 519375.9997
39041.5369 | 0 | 0 | 39041.5369 | 0 | 0 |  | -69.5 | 137.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 519376 | 519376 | 519375.9997
39041.5374 | 0 | 0 | 39041.5374 | 0 | 0 |  | -27.5 | 179.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 519376 | 519376 | 519375.9997
39041.5379 | 0 | 0 | 39041.5379 | 0 | 0 |  | 14.5 | 221.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 519376 | 519376 | 519375.9997
39041.5383 | 0 | 0 | 39041.5384 | 0 | 0 |  | 56.5 | 263.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 519376 | 519376 | 519375.9997
39041.5388 | 0 | 0 | 39041.5388 | 0 | 0 |  | 98.5 | 305.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 519376 | 519376 | 519375.9997
39041.5393 | 0 | 0 | 39041.5393 | 0 | 0 |  | 140.5 | 347.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 519376 | 519376 | 519375.9997
39041.5398 | 0 | 0 | 39041.5398 | 0 | 0 |  | 182.5 | 389.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 519376 | 519376 | 519375.9997
39041.5403 | 0 | 0 | 39041.5403 | 0 | 0 |  | 224.5 | 431.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 519376 | 519376 | 519375.9997
39041.5408 | 0 | 0 | 39041.5408 | 0 | 0 |  | 266.5 | 473.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 519376 | 519376 | 519375.9997
39041.5413 | 2120 | 2 | 39041.5413 | 0 | 0 |  | 308.5 | 515.5 | 129.4261 | 0.1221 | 0.030525 | 0 | 1.2943 | 0.001221 | 0.00030525 | 0 | 1.293 | 0.00030525 | 22.5392 | 519376.0004 | 23764.4244
39041.5417 | 2192 | 1 | 39041.5418 | 0 | 0 |  | 350.5 | 557.5 | 133.8217 | 0.06105 | 0.030525 | 0 | 1.3382 | 0.0006105 | 0.00030525 | 0 | 1.3376 | 0.00030525 | 18.5021 | 519376.0004 | 40430.2156
39041.5422 | 2315 | 1 | 39041.5422 | 274 | 0 |  | 392.5 | 599.5 | 141.3309 | 0.06105 | 16.7277 | 0 | 1.4133 | 0.0006105 | 0.16728 | 0 | 1.4127 | 0.16728 | 12.2037 | 847.9489 | 25169.6966
39041.5427 | 2018 | 0 | 39041.5427 | 2392 | 0 |  | 434.5 | 641.5 | 123.199 | 0 | 146.0317 | 0 | 1.232 | 0 | 1.4603 | 0 | 1.232 | 1.4603 | 28.7106 | 8.5861 | 27.4786
39041.5432 | 2124 | 0 | 39041.5432 | 2478 | 0 |  | 476.5 | 683.5 | 129.6703 | 0 | 151.2821 | 0 | 1.2967 | 0 | 1.5128 | 0 | 1.2967 | 1.5128 | 22.2872 | 4.8176 | 20.9905
39041.5437 | 2214 | 0 | 39041.5437 | 2425 | 0 |  | 518.5 | 725.5 | 135.1648 | 0 | 148.0464 | 0 | 1.3516 | 0 | 1.4805 | 0 | 1.3516 | 1.4805 | 17.3162 | 7.1085 | 15.9645
39041.5442 | 2581 | 0 | 39041.5442 | 1711 | 0 |  | 560.5 | 767.5 | 157.5702 | 0 | 104.4567 | 0 | 1.5757 | 0 | 1.0446 | 0 | 1.5757 | 1.0446 | 0.63464 | 51.8048 | 0.94106
39041.5447 | 2050 | 1 | 39041.5447 | 2432 | 0 |  | 602.5 | 809.5 | 125.1526 | 0.06105 | 148.4737 | 0 | 1.2515 | 0.0006105 | 1.4847 | 0 | 1.2509 | 1.4847 | 26.9076 | 6.8002 | 3478.9028
39041.5452 | 1959 | 0 | 39041.5452 | 2348 | 0 |  | 644.5 | 851.5 | 119.5971 | 0 | 143.3455 | 0 | 1.196 | 0 | 1.4335 | 0 | 1.196 | 1.4335 | 32.587 | 10.621 | 31.3911
39041.5456 | 2559 | 0 | 39041.5456 | 1874 | 0 |  | 686.5 | 893.5 | 156.2271 | 0 | 114.4078 | 0 | 1.5623 | 0 | 1.1441 | 0 | 1.5623 | 1.1441 | 1.4998 | 38.6009 | 0.062466
39041.5461 | 2289 | 0 | 39041.5461 | 2349 | 0 |  | 728.5 | 935.5 | 139.7436 | 0 | 143.4066 | 0 | 1.3974 | 0 | 1.4341 | 0 | 1.3974 | 1.4341 | 13.4723 | 10.5739 | 12.0748
39041.5466 | 2477 | 0 | 39041.5466 | 2392 | 0 |  | 770.5 | 977.5 | 151.221 | 0 | 146.0317 | 0 | 1.5122 | 0 | 1.4603 | 0 | 1.5122 | 1.4603 | 4.8599 | 8.5861 | 3.3477
39041.5471 | 2041 | 0 | 39041.5471 | 2254 | 0 |  | 812.5 | 1019.5 | 124.6032 | 0 | 137.6068 | 0 | 1.246 | 0 | 1.3761 | 0 | 1.246 | 1.3761 | 27.2602 | 15.2343 | 26.0141
39041.5476 | 2577 | 0 | 39041.5476 | 1934 | 0 |  | 854.5 | 1061.5 | 157.326 | 0 | 118.0708 | 0 | 1.5733 | 0 | 1.1807 | 0 | 1.5733 | 1.1807 | 0.79084 | 34.3009 | 0.78242
39041.5481 | 2261 | 0 | 39041.5481 | 2407 | 0 |  | 896.5 | 1103.5 | 138.0342 | 0 | 146.9475 | 0 | 1.3803 | 0 | 1.4695 | 0 | 1.3803 | 1.4695 | 14.8775 | 7.9094 | 13.4971
39041.5486 | 2129 | 0 | 39041.5486 | 2042 | 0 |  | 938.5 | 1145.5 | 129.9756 | 0 | 124.6642 | 0 | 1.2998 | 0 | 1.2466 | 0 | 1.2998 | 1.2466 | 22 | 27.1978 | 20.7002
39041.549 | 2250 | 0 | 39041.5491 | 2245 | 0 |  | 980.5 | 1187.5 | 137.3626 | 0 | 137.0574 | 0 | 1.3736 | 0 | 1.3706 | 0 | 1.3736 | 1.3706 | 15.4391 | 15.6962 | 14.0655
39041.5495 | 2377 | 0 | 39041.5495 | 1926 | 1 |  | 1022.5 | 1229.5 | 145.116 | 0 | 117.5824 | 0.06105 | 1.4512 | 0 | 1.1758 | 0.0006105 | 1.4512 | 1.1752 | 9.2714 | 34.9288 | 7.8202

## A1-C5
Open Burn Test 11 |  |  | 2006-11-20 | 12:58 |  |  | Vs = |  | 158.326 |  | R = | 100
Mixed | 7-C | Tray C | IRMS | 2
0 | 250 kW |  | Bundle | Ch. 1 & 5 | Cable A | Odd - | Cable C |  | Odd
Time-7 | N11 | N12 | Time-8 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R5-G | R1-5
39041.5354 | 0 | 0 | 39041.5354 | 0 | 0 |  | -198.5 | 8.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518576 | 518576 | 518575.9997
39041.5359 | 0 | 0 | 39041.5359 | 0 | 0 |  | -156.5 | 50.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518576 | 518576 | 518575.9997
39041.5364 | 0 | 0 | 39041.5364 | 0 | 0 |  | -114.5 | 92.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518576 | 518576 | 518575.9997
39041.5369 | 0 | 0 | 39041.5369 | 0 | 0 |  | -72.5 | 134.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518576 | 518576 | 518575.9997
39041.5373 | 0 | 0 | 39041.5373 | 0 | 0 |  | -30.5 | 176.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518576 | 518576 | 518575.9997
39041.5378 | 0 | 0 | 39041.5378 | 0 | 0 |  | 11.5 | 218.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518576 | 518576 | 518575.9997
39041.5383 | 0 | 0 | 39041.5383 | 0 | 0 |  | 53.5 | 260.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518576 | 518576 | 518575.9997
39041.5388 | 0 | 0 | 39041.5388 | 0 | 0 |  | 95.5 | 302.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518576 | 518576 | 518575.9997
39041.5393 | 0 | 0 | 39041.5393 | 0 | 0 |  | 137.5 | 344.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518576 | 518576 | 518575.9997
39041.5398 | 0 | 0 | 39041.5398 | 0 | 0 |  | 179.5 | 386.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518576 | 518576 | 518575.9997
39041.5403 | 0 | 0 | 39041.5403 | 0 | 0 |  | 221.5 | 428.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518576 | 518576 | 518575.9997
39041.5407 | 0 | 0 | 39041.5408 | 0 | 0 |  | 263.5 | 470.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518576 | 518576 | 518575.9997
39041.5412 | 2228 | 4 | 39041.5412 | 0 | 0 |  | 305.5 | 512.5 | 136.0195 | 0.2442 | 0.030525 | 0 | 1.3602 | 0.002442 | 0.00030525 | 0 | 1.3578 | 0.00030525 | 16.429 | 518575.9999 | 9032.7582
39041.5417 | 2341 | 1 | 39041.5417 | 8 | 0 |  | 347.5 | 554.5 | 142.9182 | 0.06105 | 0.4884 | 0 | 1.4292 | 0.0006105 | 0.004884 | 0 | 1.4286 | 0.004884 | 10.7855 | 32317.25 | 25060.4549
39041.5422 | 2547 | 1 | 39041.5422 | 364 | 0 |  | 389.5 | 596.5 | 155.4945 | 0.06105 | 22.2222 | 0 | 1.5549 | 0.0006105 | 0.22222 | 0 | 1.5543 | 0.22222 | 1.8218 | 612.467 | 3901.0582
39041.5427 | 2577 | 0 | 39041.5427 | 1587 | 0 |  | 431.5 | 638.5 | 157.326 | 0 | 96.8864 | 0 | 1.5733 | 0 | 0.96886 | 0 | 1.5733 | 0.96886 | 0.63562 | 63.414 | 0.93764
39041.5432 | 2001 | 0 | 39041.5432 | 2181 | 0 |  | 473.5 | 680.5 | 122.1612 | 0 | 133.1502 | 0 | 1.2216 | 0 | 1.3315 | 0 | 1.2216 | 1.3315 | 29.6042 | 18.9078 | 28.3826
39041.5437 | 1965 | 0 | 39041.5437 | 2085 | 0 |  | 515.5 | 722.5 | 119.9634 | 0 | 127.2894 | 0 | 1.1996 | 0 | 1.2729 | 0 | 1.1996 | 1.2729 | 31.9786 | 24.3827 | 30.779
39041.5441 | 2411 | 0 | 39041.5442 | 1742 | 0 |  | 557.5 | 764.5 | 147.1917 | 0 | 106.3492 | 0 | 1.4719 | 0 | 1.0635 | 0 | 1.4719 | 1.0635 | 7.5645 | 48.8737 | 6.0926
39041.5446 | 2521 | 0 | 39041.5446 | 2184 | 0 |  | 599.5 | 806.5 | 153.9072 | 0 | 133.3333 | 0 | 1.5391 | 0 | 1.3333 | 0 | 1.5391 | 1.3333 | 2.8711 | 18.7445 | 1.332
39041.5451 | 2299 | 0 | 39041.5451 | 2203 | 0 |  | 641.5 | 848.5 | 140.3541 | 0 | 134.4933 | 0 | 1.4035 | 0 | 1.3449 | 0 | 1.4035 | 1.3449 | 12.8047 | 17.7204 | 11.4012
39041.5456 | 2066 | 0 | 39041.5456 | 1994 | 0 |  | 683.5 | 890.5 | 126.1294 | 0 | 121.7338 | 0 | 1.2613 | 0 | 1.2173 | 0 | 1.2613 | 1.2173 | 25.5266 | 30.0592 | 24.2653
39041.5461 | 2158 | 0 | 39041.5461 | 2105 | 0 |  | 725.5 | 932.5 | 131.746 | 0 | 128.5104 | 0 | 1.3175 | 0 | 1.2851 | 0 | 1.3175 | 1.2851 | 20.1752 | 23.201 | 18.8577
39041.5466 | 2178 | 0 | 39041.5466 | 2452 | 0 |  | 767.5 | 974.5 | 132.967 | 0 | 149.6947 | 0 | 1.3297 | 0 | 1.4969 | 0 | 1.3297 | 1.4969 | 19.0716 | 5.7659 | 17.742
39041.5471 | 2151 | 0 | 39041.5471 | 2103 | 0 |  | 809.5 | 1016.5 | 131.3187 | 0 | 128.3883 | 0 | 1.3132 | 0 | 1.2839 | 0 | 1.3132 | 1.2839 | 20.5662 | 23.3181 | 19.2531
39041.5475 | 2217 | 0 | 39041.5476 | 2130 | 0 |  | 851.5 | 1058.5 | 135.348 | 0 | 130.0366 | 0 | 1.3535 | 0 | 1.3004 | 0 | 1.3535 | 1.3004 | 16.977 | 21.7549 | 15.6235
39041.548 | 2030 | 0 | 39041.548 | 1962 | 0 |  | 893.5 | 1100.5 | 123.9316 | 0 | 119.7802 | 0 | 1.2393 | 0 | 1.1978 | 0 | 1.2393 | 1.1978 | 27.7527 | 32.1804 | 26.5134
39041.5485 | 2334 | 0 | 39041.5485 | 1968 | 0 |  | 935.5 | 1142.5 | 142.4908 | 0 | 120.1465 | 0 | 1.4249 | 0 | 1.2015 | 0 | 1.4249 | 1.2015 | 11.1131 | 31.7774 | 9.6882
39041.549 | 2504 | 0 | 39041.549 | 2186 | 0 |  | 977.5 | 1184.5 | 152.8694 | 0 | 133.4554 | 0 | 1.5287 | 0 | 1.3346 | 0 | 1.5287 | 1.3346 | 3.5695 | 18.6359 | 2.0408
39041.5495 | 2141 | 0 | 39041.5495 | 1896 | 1 |  | 1019.5 | 1226.5 | 130.7082 | 0 | 115.7509 | 0.06105 | 1.3071 | 0 | 1.1575 | 0.0006105 | 1.3071 | 1.1569 | 21.1294 | 36.8538 | 19.8223

## A1-B4
Open Burn Test 11 |  |  | 2006-11-20 | 12:58 |  |  | Vs = |  | 158.265 |  | R = | 100
Mixed | 7-C | Tray C | IRMS | 2
0 | 250 kW |  | Bundle | Ch. 1 & 4 | Cable A | Odd - | Cable B |  | Even
Time-5 | N11 | N12 | Time-6 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R4-G | R1-4
39041.5354 | 0 | 0 | 39041.5354 | 0 | 0 |  | -201 | 6 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518376 | 518376 | 518375.9997
39041.5358 | 0 | 0 | 39041.5359 | 0 | 0 |  | -159 | 48 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518376 | 518376 | 518375.9997
39041.5363 | 0 | 0 | 39041.5364 | 0 | 0 |  | -117 | 90 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518376 | 518376 | 518375.9997
39041.5368 | 0 | 0 | 39041.5368 | 0 | 0 |  | -75 | 132 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518376 | 518376 | 518375.9997
39041.5373 | 0 | 0 | 39041.5373 | 0 | 0 |  | -33 | 174 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518376 | 518376 | 518375.9997
39041.5378 | 0 | 0 | 39041.5378 | 0 | 0 |  | 9 | 216 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518376 | 518376 | 518375.9997
39041.5383 | 0 | 0 | 39041.5383 | 0 | 0 |  | 51 | 258 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518376 | 518376 | 518375.9997
39041.5388 | 0 | 0 | 39041.5388 | 0 | 0 |  | 93 | 300 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518376 | 518376 | 518375.9997
39041.5392 | 0 | 0 | 39041.5393 | 0 | 0 |  | 135 | 342 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518376 | 518376 | 518375.9997
39041.5397 | 0 | 0 | 39041.5398 | 0 | 0 |  | 177 | 384 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518376 | 518376 | 518375.9997
39041.5402 | 0 | 0 | 39041.5402 | 0 | 0 |  | 219 | 426 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518376 | 518376 | 518375.9997
39041.5407 | 0 | 0 | 39041.5407 | 0 | 0 |  | 261 | 468 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518376 | 518376 | 518375.9997
39041.5412 | 255 | 1 | 39041.5412 | 0 | 0 |  | 303 | 510 | 15.5678 | 0.06105 | 0.030525 | 0 | 0.15568 | 0.0006105 | 0.00030525 | 0 | 0.15507 | 0.00030525 | 920.229 | 518375.9999 | 233592.9375
39041.5417 | 2068 | 1 | 39041.5417 | 0 | 0 |  | 344.5 | 551.5 | 126.2515 | 0.06105 | 0.030525 | 0 | 1.2625 | 0.0006105 | 0.00030525 | 0 | 1.2619 | 0.00030525 | 25.3691 | 518375.9999 | 52327.9054
39041.5422 | 2536 | 1 | 39041.5422 | 0 | 0 |  | 386.5 | 593.5 | 154.823 | 0.06105 | 0.030525 | 0 | 1.5482 | 0.0006105 | 0.00030525 | 0 | 1.5476 | 0.00030525 | 2.2241 | 518375.9999 | 5536.9319
39041.5427 | 2423 | 1 | 39041.5427 | 129 | 0 |  | 429 | 636 | 147.9243 | 0.06105 | 7.8755 | 0 | 1.4792 | 0.0006105 | 0.078755 | 0 | 1.4786 | 0.078755 | 6.9935 | 1909.5969 | 16000.1205
39041.5431 | 2503 | 0 | 39041.5431 | 2123 | 0 |  | 470.5 | 677.5 | 152.8083 | 0 | 129.6093 | 0 | 1.5281 | 0 | 1.2961 | 0 | 1.5281 | 1.2961 | 3.5709 | 22.1093 | 2.0428
39041.5436 | 2033 | 0 | 39041.5436 | 2170 | 0 |  | 512.5 | 719.5 | 124.1148 | 0 | 132.4786 | 0 | 1.2411 | 0 | 1.3248 | 0 | 1.2411 | 1.3248 | 27.515 | 19.4645 | 26.2739
39041.5441 | 2285 | 0 | 39041.5441 | 2465 | 0 |  | 555 | 762 | 139.4994 | 0 | 150.4884 | 0 | 1.395 | 0 | 1.5049 | 0 | 1.395 | 1.5049 | 13.4521 | 5.1675 | 12.0571
39041.5446 | 2084 | 0 | 39041.5446 | 1975 | 0 |  | 597 | 804 | 127.2283 | 0 | 120.5739 | 0 | 1.2723 | 0 | 1.2057 | 0 | 1.2723 | 1.2057 | 24.3944 | 31.2597 | 23.1222
39041.5451 | 2557 | 0 | 39041.5451 | 2000 | 0 |  | 639 | 846 | 156.105 | 0 | 122.1001 | 0 | 1.5611 | 0 | 1.221 | 0 | 1.5611 | 1.221 | 1.3837 | 29.619 | 0.1774
39041.5456 | 2011 | 0 | 39041.5456 | 2279 | 0 |  | 681 | 888 | 122.7717 | 0 | 139.1331 | 0 | 1.2277 | 0 | 1.3913 | 0 | 1.2277 | 1.3913 | 28.91 | 13.7508 | 27.6823
39041.5461 | 2294 | 0 | 39041.5461 | 2545 | 0 |  | 722.5 | 929.5 | 140.0488 | 0 | 155.3724 | 0 | 1.4005 | 0 | 1.5537 | 0 | 1.4005 | 1.5537 | 13.007 | 1.8617 | 11.6065
39041.5465 | 2256 | 0 | 39041.5466 | 1998 | 0 |  | 764.5 | 971.5 | 137.7289 | 0 | 121.978 | 0 | 1.3773 | 0 | 1.2198 | 0 | 1.3773 | 1.2198 | 14.9105 | 29.7487 | 13.5332
39041.547 | 2332 | 0 | 39041.547 | 2210 | 0 |  | 807 | 1014 | 142.3687 | 0 | 134.9206 | 0 | 1.4237 | 0 | 1.3492 | 0 | 1.4237 | 1.3492 | 11.1655 | 17.3023 | 9.7418
39041.5475 | 2472 | 0 | 39041.5475 | 2538 | 0 |  | 849 | 1056 | 150.9158 | 0 | 154.9451 | 0 | 1.5092 | 0 | 1.5495 | 0 | 1.5092 | 1.5495 | 4.8697 | 2.1426 | 3.3606
39041.548 | 2333 | 0 | 39041.548 | 2543 | 0 |  | 891 | 1098 | 142.4298 | 0 | 155.2503 | 0 | 1.4243 | 0 | 1.5525 | 0 | 1.4243 | 1.5525 | 11.1179 | 1.9418 | 9.6936
39041.5485 | 2576 | 0 | 39041.5485 | 2508 | 0 |  | 932.5 | 1139.5 | 157.265 | 0 | 153.1136 | 0 | 1.5726 | 0 | 1.5311 | 0 | 1.5726 | 1.5311 | 0.63587 | 3.3644 | 0.93678
39041.549 | 2508 | 0 | 39041.549 | 2057 | 0 |  | 974.5 | 1181.5 | 153.1136 | 0 | 125.58 | 0 | 1.5311 | 0 | 1.2558 | 0 | 1.5311 | 1.2558 | 3.3644 | 26.0272 | 1.8333
39041.5495 | 1984 | 0 | 39041.5495 | 2353 | 0 |  | 1016.5 | 1223.5 | 121.1233 | 0 | 143.6508 | 0 | 1.2112 | 0 | 1.4365 | 0 | 1.2112 | 1.4365 | 30.6643 | 10.1734 | 29.4531

## A1-B3
Open Burn Test 11 |  |  | 2006-11-20 | 12:58 |  |  | Vs = |  | 158.1429 |  | R = | 100
Mixed | 7-C | Tray C | IRMS | 2
0 | 250 kW |  | Bundle | Ch. 1 & 3 | Cable A | Odd - | Cable B |  | Odd
Time-3 | N11 | N12 | Time-4 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R3-G | R1-3
39041.5353 | 0 | 0 | 39041.5353 | 0 | 0 |  | -204 | 3 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517976 | 517976 | 517975.9997
39041.5358 | 0 | 0 | 39041.5358 | 0 | 0 |  | -162 | 45 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517976 | 517976 | 517975.9997
39041.5363 | 0 | 0 | 39041.5363 | 0 | 0 |  | -120 | 87 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517976 | 517976 | 517975.9997
39041.5368 | 0 | 0 | 39041.5368 | 0 | 0 |  | -78 | 129 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517976 | 517976 | 517975.9997
39041.5373 | 0 | 0 | 39041.5373 | 0 | 0 |  | -36 | 171 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517976 | 517976 | 517975.9997
39041.5378 | 0 | 0 | 39041.5378 | 0 | 0 |  | 6 | 213 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517976 | 517976 | 517975.9997
39041.5382 | 0 | 0 | 39041.5383 | 0 | 0 |  | 48 | 255 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517976 | 517976 | 517975.9997
39041.5387 | 0 | 0 | 39041.5387 | 0 | 0 |  | 90 | 297 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517976 | 517976 | 517975.9997
39041.5392 | 0 | 0 | 39041.5392 | 0 | 0 |  | 132 | 339 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517976 | 517976 | 517975.9997
39041.5397 | 0 | 0 | 39041.5397 | 0 | 0 |  | 174 | 381 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517976 | 517976 | 517975.9997
39041.5402 | 0 | 0 | 39041.5402 | 0 | 0 |  | 216 | 423 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517976 | 517976 | 517975.9997
39041.5407 | 0 | 0 | 39041.5407 | 0 | 0 |  | 258 | 465 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517976 | 517976 | 517975.9997
39041.5412 | 99 | 1 | 39041.5412 | 0 | 0 |  | 300 | 507 | 6.044 | 0.06105 | 0.030525 | 0 | 0.06044 | 0.0006105 | 0.00030525 | 0 | 0.059829 | 0.00030525 | 2542.2295 | 517976 | 248989.9302
39041.5416 | 2104 | 1 | 39041.5417 | 0 | 0 |  | 342 | 549 | 128.4493 | 0.06105 | 0.030525 | 0 | 1.2845 | 0.0006105 | 0.00030525 | 0 | 1.2839 | 0.00030525 | 23.1279 | 517975.9998 | 48528.6311
39041.5421 | 2365 | 1 | 39041.5422 | 0 | 0 |  | 384 | 591 | 144.3834 | 0.06105 | 0.030525 | 0 | 1.4438 | 0.0006105 | 0.00030525 | 0 | 1.4432 | 0.00030525 | 9.5338 | 517975.9998 | 22433.669
39041.5426 | 2574 | 1 | 39041.5426 | 64 | 0 |  | 426 | 633 | 157.1429 | 0.06105 | 3.9072 | 0 | 1.5714 | 0.0006105 | 0.039072 | 0 | 1.5708 | 0.039072 | 0.63662 | 3947.4687 | 1500.0009
39041.5431 | 2127 | 0 | 39041.5431 | 2305 | 0 |  | 468 | 675 | 129.8535 | 0 | 140.7204 | 0 | 1.2985 | 0 | 1.4072 | 0 | 1.2985 | 1.4072 | 21.7856 | 12.3809 | 20.4871
39041.5436 | 2565 | 0 | 39041.5436 | 2387 | 0 |  | 510 | 717 | 156.5934 | 0 | 145.7265 | 0 | 1.5659 | 0 | 1.4573 | 0 | 1.5659 | 1.4573 | 0.98947 | 8.5203 | 0.57646
39041.5441 | 2316 | 0 | 39041.5441 | 2142 | 0 |  | 552 | 759 | 141.3919 | 0 | 130.7692 | 0 | 1.4139 | 0 | 1.3077 | 0 | 1.4139 | 1.3077 | 11.8472 | 20.9328 | 10.4332
39041.5446 | 2099 | 0 | 39041.5446 | 2396 | 0 |  | 594 | 801 | 128.1441 | 0 | 146.2759 | 0 | 1.2814 | 0 | 1.4628 | 0 | 1.2814 | 1.4628 | 23.4102 | 8.1127 | 22.1288
39041.545 | 2383 | 0 | 39041.5451 | 2282 | 0 |  | 636 | 843 | 145.4823 | 0 | 139.3162 | 0 | 1.4548 | 0 | 1.3932 | 0 | 1.4548 | 1.3932 | 8.7025 | 13.5136 | 7.2477
39041.5455 | 2430 | 0 | 39041.5456 | 2059 | 0 |  | 678 | 885 | 148.3516 | 0 | 125.7021 | 0 | 1.4835 | 0 | 1.257 | 0 | 1.4835 | 1.257 | 6.6 | 25.8077 | 5.1165
39041.546 | 2530 | 0 | 39041.546 | 2196 | 0 |  | 720 | 927 | 154.4567 | 0 | 134.0659 | 0 | 1.5446 | 0 | 1.3407 | 0 | 1.5446 | 1.3407 | 2.3866 | 17.959 | 0.84199
39041.5465 | 2541 | 0 | 39041.5465 | 2112 | 0 |  | 762 | 969 | 155.1282 | 0 | 128.9377 | 0 | 1.5513 | 0 | 1.2894 | 0 | 1.5513 | 1.2894 | 1.9433 | 22.6506 | 0.39205
39041.547 | 2043 | 0 | 39041.547 | 1953 | 0 |  | 804 | 1011 | 124.7253 | 0 | 119.2308 | 0 | 1.2473 | 0 | 1.1923 | 0 | 1.2473 | 1.1923 | 26.793 | 32.6359 | 25.5457
39041.5475 | 2503 | 0 | 39041.5475 | 2032 | 0 |  | 846 | 1053 | 152.8083 | 0 | 124.0537 | 0 | 1.5281 | 0 | 1.2405 | 0 | 1.5281 | 1.2405 | 3.491 | 27.4793 | 1.9629
39041.548 | 2039 | 0 | 39041.548 | 2000 | 0 |  | 888 | 1095 | 124.4811 | 0 | 122.1001 | 0 | 1.2448 | 0 | 1.221 | 0 | 1.2448 | 1.221 | 27.0417 | 29.519 | 25.7969
39041.5484 | 2405 | 0 | 39041.5485 | 1993 | 0 |  | 930 | 1137 | 146.8254 | 0 | 121.6728 | 0 | 1.4683 | 0 | 1.2167 | 0 | 1.4683 | 1.2167 | 7.7081 | 29.9739 | 6.2399
39041.5489 | 2427 | 0 | 39041.549 | 2096 | 0 |  | 972 | 1179 | 148.1685 | 0 | 127.9609 | 0 | 1.4817 | 0 | 1.2796 | 0 | 1.4817 | 1.2796 | 6.7318 | 23.5868 | 5.2501
39041.5494 | 2272 | 0 | 39041.5494 | 2290 | 0 |  | 1014 | 1221 | 138.7057 | 0 | 139.8046 | 0 | 1.3871 | 0 | 1.398 | 0 | 1.3871 | 1.398 | 14.0132 | 13.117 | 12.6261

## A1-A2
Open Burn Test 11 |  |  | 2006-11-20 | 12:58 |  |  | Vs = |  | 158.6923 |  | R = | 100
Mixed | 7-C | Tray C | IRMS | 2
0 | 250 kW |  | Bundle | Ch. 1 & 2 | Cable A | Odd-Even
Time-1 | N11 | N12 | Time-2 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R2-G | R1-2
39041.5353 | 0 | 0 | 39041.5353 | 0 | 0 |  | -206.5 | 0.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 519776 | 519776 | 519775.9997
39041.5358 | 0 | 0 | 39041.5358 | 0 | 0 |  | -164.5 | 42.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 519776 | 519776 | 519775.9997
39041.5363 | 0 | 0 | 39041.5363 | 0 | 0 |  | -122.5 | 84.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 519776 | 519776 | 519775.9997
39041.5368 | 0 | 0 | 39041.5368 | 0 | 0 |  | -80.5 | 126.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 519776 | 519776 | 519775.9997
39041.5372 | 0 | 0 | 39041.5373 | 0 | 0 |  | -38.5 | 168.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 519776 | 519776 | 519775.9997
39041.5377 | 0 | 0 | 39041.5377 | 0 | 0 |  | 3.5 | 210.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 519776 | 519776 | 519775.9997
39041.5382 | 0 | 0 | 39041.5382 | 0 | 0 |  | 45.5 | 252.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 519776 | 519776 | 519775.9997
39041.5387 | 0 | 0 | 39041.5387 | 0 | 0 |  | 87.5 | 294.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 519776 | 519776 | 519775.9997
39041.5392 | 0 | 0 | 39041.5392 | 0 | 0 |  | 129.5 | 336.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 519776 | 519776 | 519775.9997
39041.5397 | 0 | 0 | 39041.5397 | 0 | 0 |  | 171.5 | 378.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 519776 | 519776 | 519775.9997
39041.5402 | 948 | 1147 | 39041.5402 | 922 | 1007 |  | 213.5 | 420.5 | 57.8755 | 70.0244 | 56.2882 | 61.4774 | 0.57875 | 0.70024 | 0.56288 | 0.61477 | 0.12149 | 0.051893 | 683.427 | 2690.4522 | 42.398
39041.5406 | 1174 | 955 | 39041.5407 | 1181 | 1015 |  | 255.5 | 462.5 | 71.6728 | 58.3028 | 72.1001 | 61.9658 | 0.71673 | 0.58303 | 0.721 | 0.61966 | 0.1337 | 0.10134 | 691.9386 | 7345.0559 | 48.5929
39041.5411 | 1098 | 933 | 39041.5411 | 973 | 990 |  | 297 | 504 | 67.033 | 56.9597 | 59.4017 | 60.4396 | 0.67033 | 0.5696 | 0.59402 | 0.6044 | 0.10073 | 0.010379 | 601.2651 | 1101.4892 | 55.8493
39041.5416 | 2109 | 0 | 39041.5416 | 2578 | 0 |  | 339 | 546 | 128.7546 | 0 | 157.3871 | 0 | 1.2875 | 0 | 1.5739 | 0 | 1.2875 | 1.5739 | 23.2518 | 0.82933 | 21.9642
39041.5421 | 2052 | 0 | 39041.5421 | 2366 | 0 |  | 381 | 588 | 125.2747 | 0 | 144.4444 | 0 | 1.2527 | 0 | 1.4444 | 0 | 1.2527 | 1.4444 | 26.6754 | 9.8639 | 25.4227
39041.5426 | 2396 | 0 | 39041.5426 | 2435 | 0 |  | 423.5 | 630.5 | 146.2759 | 0 | 148.6569 | 0 | 1.4628 | 0 | 1.4866 | 0 | 1.4628 | 1.4866 | 8.4883 | 6.7507 | 7.0256
39041.5431 | 2255 | 0 | 39041.5431 | 2383 | 0 |  | 465 | 672 | 137.6679 | 0 | 145.4823 | 0 | 1.3767 | 0 | 1.4548 | 0 | 1.3767 | 1.4548 | 15.2718 | 9.0802 | 13.8952
39041.5436 | 2209 | 0 | 39041.5436 | 2492 | 0 |  | 507.5 | 714.5 | 134.8596 | 0 | 152.1368 | 0 | 1.3486 | 0 | 1.5214 | 0 | 1.3486 | 1.5214 | 17.6722 | 4.309 | 16.3237
39041.5441 | 2036 | 0 | 39041.5441 | 2141 | 0 |  | 549.5 | 756.5 | 124.2979 | 0 | 130.7082 | 0 | 1.243 | 0 | 1.3071 | 0 | 1.243 | 1.3071 | 27.6709 | 21.4096 | 26.4279
39041.5445 | 2558 | 0 | 39041.5445 | 2047 | 0 |  | 591.5 | 798.5 | 156.1661 | 0 | 124.9695 | 0 | 1.5617 | 0 | 1.2497 | 0 | 1.5617 | 1.2497 | 1.6177 | 26.9849 | 0.056009
39041.545 | 2096 | 0 | 39041.545 | 1960 | 0 |  | 633.5 | 840.5 | 127.9609 | 0 | 119.6581 | 0 | 1.2796 | 0 | 1.1966 | 0 | 1.2796 | 1.1966 | 24.0162 | 32.6214 | 22.7366
39041.5455 | 2034 | 0 | 39041.5455 | 2198 | 0 |  | 675.5 | 882.5 | 124.1758 | 0 | 134.188 | 0 | 1.2418 | 0 | 1.3419 | 0 | 1.2418 | 1.3419 | 27.7965 | 18.2611 | 26.5547
39041.546 | 2130 | 0 | 39041.546 | 2583 | 0 |  | 717 | 924 | 130.0366 | 0 | 157.6923 | 0 | 1.3004 | 0 | 1.5769 | 0 | 1.3004 | 1.5769 | 22.0366 | 0.63415 | 20.7363
39041.5465 | 2320 | 0 | 39041.5465 | 2469 | 0 |  | 759 | 966 | 141.6361 | 0 | 150.7326 | 0 | 1.4164 | 0 | 1.5073 | 0 | 1.4164 | 1.5073 | 12.0422 | 5.2807 | 10.6259
39041.547 | 2250 | 0 | 39041.547 | 2074 | 0 |  | 801.5 | 1008.5 | 137.3626 | 0 | 126.6178 | 0 | 1.3736 | 0 | 1.2662 | 0 | 1.3736 | 1.2662 | 15.528 | 25.3317 | 14.1544
39041.5475 | 2082 | 0 | 39041.5475 | 2260 | 0 |  | 843.5 | 1050.5 | 127.1062 | 0 | 137.9731 | 0 | 1.2711 | 0 | 1.3797 | 0 | 1.2711 | 1.3797 | 24.8501 | 15.0168 | 23.5791
39041.5479 | 2225 | 0 | 39041.548 | 1994 | 0 |  | 885 | 1092 | 135.8364 | 0 | 121.7338 | 0 | 1.3584 | 0 | 1.2173 | 0 | 1.3584 | 1.2173 | 16.8261 | 30.3601 | 15.4677
39041.5484 | 2230 | 0 | 39041.5484 | 2474 | 0 |  | 927 | 1134 | 136.1416 | 0 | 151.0379 | 0 | 1.3614 | 0 | 1.5104 | 0 | 1.3614 | 1.5104 | 16.5641 | 5.0679 | 15.2027
39041.5489 | 2078 | 1 | 39041.5489 | 2311 | 0 |  | 969 | 1176 | 126.862 | 0.06105 | 141.0867 | 0 | 1.2686 | 0.0006105 | 1.4109 | 0 | 1.268 | 1.4109 | 25.1998 | 12.4786 | 5773.1915
39041.5494 | 1952 | 3 | 39041.5494 | 2135 | 3 |  | 1011 | 1218 | 119.1697 | 0.18315 | 130.3419 | 0.18315 | 1.1917 | 0.0018315 | 1.3034 | 0.0018315 | 1.1899 | 1.3016 | 33.4514 | 21.8734 | 3855.0388

## Raw IRMS Data
Time | DL1.V2000:B | DL1.V2001:B | DL1.V1500:B | Open Burn Test 11 |  |  | 2006-11-20 | 12:58
39041.5353 | 0 | 0 | 1 | Mixed | 7-C | Tray C | IRMS | 2
39041.5358 | 0 | 0 | 1 |  | 250 kW |  | Bundle
39041.5363 | 0 | 0 | 1
39041.5368 | 0 | 0 | 1
39041.5372 | 0 | 0 | 1
39041.5377 | 0 | 0 | 1
39041.5382 | 0 | 0 | 1
39041.5387 | 0 | 0 | 1
39041.5392 | 0 | 0 | 1
39041.5397 | 0 | 0 | 1
39041.5402 | 948 | 1147 | 1
39041.5406 | 1174 | 955 | 1
39041.5411 | 1098 | 933 | 1
39041.5416 | 2109 | 0 | 1
39041.5421 | 2052 | 0 | 1
39041.5426 | 2396 | 0 | 1
39041.5431 | 2255 | 0 | 1
39041.5436 | 2209 | 0 | 1
39041.5441 | 2036 | 0 | 1
39041.5445 | 2558 | 0 | 1
39041.545 | 2096 | 0 | 1
39041.5455 | 2034 | 0 | 1
39041.546 | 2130 | 0 | 1
39041.5465 | 2320 | 0 | 1
39041.547 | 2250 | 0 | 1
39041.5475 | 2082 | 0 | 1
39041.5479 | 2225 | 0 | 1
39041.5484 | 2230 | 0 | 1
39041.5489 | 2078 | 1 | 1
39041.5494 | 1952 | 3 | 1
1
39041.5353 | 0 | 0 | 2
39041.5358 | 0 | 0 | 2
39041.5363 | 0 | 0 | 2
39041.5368 | 0 | 0 | 2
39041.5373 | 0 | 0 | 2
39041.5377 | 0 | 0 | 2
39041.5382 | 0 | 0 | 2
39041.5387 | 0 | 0 | 2
39041.5392 | 0 | 0 | 2
39041.5397 | 0 | 0 | 2
39041.5402 | 922 | 1007 | 2
39041.5407 | 1181 | 1015 | 2
39041.5411 | 973 | 990 | 2
39041.5416 | 2578 | 0 | 2
39041.5421 | 2366 | 0 | 2
39041.5426 | 2435 | 0 | 2
39041.5431 | 2383 | 0 | 2
39041.5436 | 2492 | 0 | 2
39041.5441 | 2141 | 0 | 2
39041.5445 | 2047 | 0 | 2
39041.545 | 1960 | 0 | 2
39041.5455 | 2198 | 0 | 2
39041.546 | 2583 | 0 | 2
39041.5465 | 2469 | 0 | 2
39041.547 | 2074 | 0 | 2
39041.5475 | 2260 | 0 | 2
39041.548 | 1994 | 0 | 2
39041.5484 | 2474 | 0 | 2
39041.5489 | 2311 | 0 | 2
39041.5494 | 2135 | 3 | 2
2
39041.5353 | 0 | 0 | 3
39041.5358 | 0 | 0 | 3
39041.5363 | 0 | 0 | 3
39041.5368 | 0 | 0 | 3
39041.5373 | 0 | 0 | 3
39041.5378 | 0 | 0 | 3
39041.5382 | 0 | 0 | 3
39041.5387 | 0 | 0 | 3
39041.5392 | 0 | 0 | 3
39041.5397 | 0 | 0 | 3
39041.5402 | 0 | 0 | 3
39041.5407 | 0 | 0 | 3
39041.5412 | 99 | 0 | 3
39041.5416 | 2104 | 0 | 3
39041.5421 | 2365 | 0 | 3
39041.5426 | 2574 | 0 | 3
39041.5431 | 2127 | 0 | 3
39041.5436 | 2565 | 0 | 3
39041.5441 | 2316 | 0 | 3
39041.5446 | 2099 | 0 | 3
39041.545 | 2383 | 0 | 3
39041.5455 | 2430 | 0 | 3
39041.546 | 2530 | 0 | 3
39041.5465 | 2541 | 0 | 3
39041.547 | 2043 | 0 | 3
39041.5475 | 2503 | 0 | 3
39041.548 | 2039 | 0 | 3
39041.5484 | 2405 | 0 | 3
39041.5489 | 2427 | 0 | 3
39041.5494 | 2272 | 0 | 3
3
39041.5353 | 0 | 0 | 4
39041.5358 | 0 | 0 | 4
39041.5363 | 0 | 0 | 4
39041.5368 | 0 | 0 | 4
39041.5373 | 0 | 0 | 4
39041.5378 | 0 | 0 | 4
39041.5383 | 0 | 0 | 4
39041.5387 | 0 | 0 | 4
39041.5392 | 0 | 0 | 4
39041.5397 | 0 | 0 | 4
39041.5402 | 0 | 0 | 4
39041.5407 | 0 | 0 | 4
39041.5412 | 0 | 0 | 4
39041.5417 | 0 | 0 | 4
39041.5422 | 0 | 0 | 4
39041.5426 | 64 | 0 | 4
39041.5431 | 2305 | 0 | 4
39041.5436 | 2387 | 0 | 4
39041.5441 | 2142 | 0 | 4
39041.5446 | 2396 | 0 | 4
39041.5451 | 2282 | 0 | 4
39041.5456 | 2059 | 0 | 4
39041.546 | 2196 | 0 | 4
39041.5465 | 2112 | 0 | 4
39041.547 | 1953 | 0 | 4
39041.5475 | 2032 | 0 | 4
39041.548 | 2000 | 0 | 4
39041.5485 | 1993 | 0 | 4
39041.549 | 2096 | 0 | 4
39041.5494 | 2290 | 0 | 4
4
39041.5354 | 0 | 0 | 5
39041.5358 | 0 | 0 | 5
39041.5363 | 0 | 0 | 5
39041.5368 | 0 | 0 | 5
39041.5373 | 0 | 0 | 5
39041.5378 | 0 | 0 | 5
39041.5383 | 0 | 0 | 5
39041.5388 | 0 | 0 | 5
39041.5392 | 0 | 0 | 5
39041.5397 | 0 | 0 | 5
39041.5402 | 0 | 0 | 5
39041.5407 | 0 | 0 | 5
39041.5412 | 255 | 0 | 5
39041.5417 | 2068 | 0 | 5
39041.5422 | 2536 | 0 | 5
39041.5427 | 2423 | 0 | 5
39041.5431 | 2503 | 0 | 5
39041.5436 | 2033 | 0 | 5
39041.5441 | 2285 | 0 | 5
39041.5446 | 2084 | 0 | 5
39041.5451 | 2557 | 0 | 5
39041.5456 | 2011 | 0 | 5
39041.5461 | 2294 | 0 | 5
39041.5465 | 2256 | 0 | 5
39041.547 | 2332 | 0 | 5
39041.5475 | 2472 | 0 | 5
39041.548 | 2333 | 0 | 5
39041.5485 | 2576 | 0 | 5
39041.549 | 2508 | 0 | 5
39041.5495 | 1984 | 0 | 5
5
39041.5354 | 0 | 0 | 6
39041.5359 | 0 | 0 | 6
39041.5364 | 0 | 0 | 6
39041.5368 | 0 | 0 | 6
39041.5373 | 0 | 0 | 6
39041.5378 | 0 | 0 | 6
39041.5383 | 0 | 0 | 6
39041.5388 | 0 | 0 | 6
39041.5393 | 0 | 0 | 6
39041.5398 | 0 | 0 | 6
39041.5402 | 0 | 0 | 6
39041.5407 | 0 | 0 | 6
39041.5412 | 0 | 0 | 6
39041.5417 | 0 | 0 | 6
39041.5422 | 0 | 0 | 6
39041.5427 | 129 | 0 | 6
39041.5431 | 2123 | 0 | 6
39041.5436 | 2170 | 0 | 6
39041.5441 | 2465 | 0 | 6
39041.5446 | 1975 | 0 | 6
39041.5451 | 2000 | 0 | 6
39041.5456 | 2279 | 0 | 6
39041.5461 | 2545 | 0 | 6
39041.5466 | 1998 | 0 | 6
39041.547 | 2210 | 0 | 6
39041.5475 | 2538 | 0 | 6
39041.548 | 2543 | 0 | 6
39041.5485 | 2508 | 0 | 6
39041.549 | 2057 | 0 | 6
39041.5495 | 2353 | 0 | 6
6
39041.5354 | 0 | 0 | 7
39041.5359 | 0 | 0 | 7
39041.5364 | 0 | 0 | 7
39041.5369 | 0 | 0 | 7
39041.5373 | 0 | 0 | 7
39041.5378 | 0 | 0 | 7
39041.5383 | 0 | 0 | 7
39041.5388 | 0 | 0 | 7
39041.5393 | 0 | 0 | 7
39041.5398 | 0 | 0 | 7
39041.5403 | 0 | 0 | 7
39041.5407 | 0 | 0 | 7
39041.5412 | 2228 | 4 | 7
39041.5417 | 2341 | 0 | 7
39041.5422 | 2547 | 0 | 7
39041.5427 | 2577 | 0 | 7
39041.5432 | 2001 | 0 | 7
39041.5437 | 1965 | 0 | 7
39041.5441 | 2411 | 0 | 7
39041.5446 | 2521 | 0 | 7
39041.5451 | 2299 | 0 | 7
39041.5456 | 2066 | 0 | 7
39041.5461 | 2158 | 0 | 7
39041.5466 | 2178 | 0 | 7
39041.5471 | 2151 | 0 | 7
39041.5475 | 2217 | 0 | 7
39041.548 | 2030 | 0 | 7
39041.5485 | 2334 | 0 | 7
39041.549 | 2504 | 0 | 7
39041.5495 | 2141 | 0 | 7
7
39041.5354 | 0 | 0 | 8
39041.5359 | 0 | 0 | 8
39041.5364 | 0 | 0 | 8
39041.5369 | 0 | 0 | 8
39041.5373 | 0 | 0 | 8
39041.5378 | 0 | 0 | 8
39041.5383 | 0 | 0 | 8
39041.5388 | 0 | 0 | 8
39041.5393 | 0 | 0 | 8
39041.5398 | 0 | 0 | 8
39041.5403 | 0 | 0 | 8
39041.5408 | 0 | 0 | 8
39041.5412 | 0 | 0 | 8
39041.5417 | 8 | 0 | 8
39041.5422 | 364 | 0 | 8
39041.5427 | 1587 | 0 | 8
39041.5432 | 2181 | 0 | 8
39041.5437 | 2085 | 0 | 8
39041.5442 | 1742 | 0 | 8
39041.5446 | 2184 | 0 | 8
39041.5451 | 2203 | 0 | 8
39041.5456 | 1994 | 0 | 8
39041.5461 | 2105 | 0 | 8
39041.5466 | 2452 | 0 | 8
39041.5471 | 2103 | 0 | 8
39041.5476 | 2130 | 0 | 8
39041.548 | 1962 | 0 | 8
39041.5485 | 1968 | 0 | 8
39041.549 | 2186 | 0 | 8
39041.5495 | 1896 | 1 | 8
8
39041.5354 | 0 | 0 | 9
39041.5359 | 0 | 0 | 9
39041.5364 | 0 | 0 | 9
39041.5369 | 0 | 0 | 9
39041.5374 | 0 | 0 | 9
39041.5379 | 0 | 0 | 9
39041.5383 | 0 | 0 | 9
39041.5388 | 0 | 0 | 9
39041.5393 | 0 | 0 | 9
39041.5398 | 0 | 0 | 9
39041.5403 | 0 | 0 | 9
39041.5408 | 0 | 0 | 9
39041.5413 | 2120 | 2 | 9
39041.5417 | 2192 | 0 | 9
39041.5422 | 2315 | 0 | 9
39041.5427 | 2018 | 0 | 9
39041.5432 | 2124 | 0 | 9
39041.5437 | 2214 | 0 | 9
39041.5442 | 2581 | 0 | 9
39041.5447 | 2050 | 1 | 9
39041.5452 | 1959 | 0 | 9
39041.5456 | 2559 | 0 | 9
39041.5461 | 2289 | 0 | 9
39041.5466 | 2477 | 0 | 9
39041.5471 | 2041 | 0 | 9
39041.5476 | 2577 | 0 | 9
39041.5481 | 2261 | 0 | 9
39041.5486 | 2129 | 0 | 9
39041.549 | 2250 | 0 | 9
39041.5495 | 2377 | 0 | 9
9
39041.5354 | 0 | 0 | 10
39041.5359 | 0 | 0 | 10
39041.5364 | 0 | 0 | 10
39041.5369 | 0 | 0 | 10
39041.5374 | 0 | 0 | 10
39041.5379 | 0 | 0 | 10
39041.5384 | 0 | 0 | 10
39041.5388 | 0 | 0 | 10
39041.5393 | 0 | 0 | 10
39041.5398 | 0 | 0 | 10
39041.5403 | 0 | 0 | 10
39041.5408 | 0 | 0 | 10
39041.5413 | 0 | 0 | 10
39041.5418 | 0 | 0 | 10
39041.5422 | 274 | 0 | 10
39041.5427 | 2392 | 0 | 10
39041.5432 | 2478 | 0 | 10
39041.5437 | 2425 | 0 | 10
39041.5442 | 1711 | 0 | 10
39041.5447 | 2432 | 0 | 10
39041.5452 | 2348 | 0 | 10
39041.5456 | 1874 | 0 | 10
39041.5461 | 2349 | 0 | 10
39041.5466 | 2392 | 0 | 10
39041.5471 | 2254 | 0 | 10
39041.5476 | 1934 | 0 | 10
39041.5481 | 2407 | 0 | 10
39041.5486 | 2042 | 0 | 10
39041.5491 | 2245 | 0 | 10
39041.5495 | 1926 | 1 | 10
10
39041.5355 | 0 | 0 | 11
39041.5359 | 0 | 0 | 11
39041.5364 | 0 | 0 | 11
39041.5369 | 0 | 0 | 11
39041.5374 | 0 | 0 | 11
39041.5379 | 0 | 0 | 11
39041.5384 | 0 | 0 | 11
39041.5389 | 0 | 0 | 11
39041.5394 | 0 | 0 | 11
39041.5398 | 0 | 0 | 11
39041.5403 | 0 | 0 | 11
39041.5408 | 0 | 0 | 11
39041.5413 | 1909 | 11 | 11
39041.5418 | 2604 | 0 | 11
39041.5423 | 2335 | 0 | 11
39041.5428 | 2581 | 0 | 11
39041.5432 | 2010 | 0 | 11
39041.5437 | 2545 | 0 | 11
39041.5442 | 2038 | 0 | 11
39041.5447 | 2513 | 0 | 11
39041.5452 | 2035 | 0 | 11
39041.5457 | 2408 | 0 | 11
39041.5461 | 2231 | 0 | 11
39041.5466 | 2439 | 0 | 11
39041.5471 | 1964 | 0 | 11
39041.5476 | 2356 | 0 | 11
39041.5481 | 2385 | 0 | 11
39041.5486 | 2565 | 0 | 11
39041.5491 | 2471 | 0 | 11
39041.5495 | 2283 | 0 | 11
11
39041.5355 | 0 | 0 | 12
39041.536 | 0 | 0 | 12
39041.5364 | 0 | 0 | 12
39041.5369 | 0 | 0 | 12
39041.5374 | 0 | 0 | 12
39041.5379 | 0 | 0 | 12
39041.5384 | 0 | 0 | 12
39041.5389 | 0 | 0 | 12
39041.5394 | 0 | 0 | 12
39041.5398 | 0 | 0 | 12
39041.5403 | 0 | 0 | 12
39041.5408 | 0 | 0 | 12
39041.5413 | 0 | 0 | 12
39041.5418 | 0 | 0 | 12
39041.5423 | 0 | 0 | 12
39041.5428 | 166 | 0 | 12
39041.5433 | 2121 | 0 | 12
39041.5437 | 2409 | 0 | 12
39041.5442 | 2488 | 0 | 12
39041.5447 | 2005 | 0 | 12
39041.5452 | 2253 | 0 | 12
39041.5457 | 2365 | 0 | 12
39041.5462 | 2242 | 0 | 12
39041.5467 | 2146 | 0 | 12
39041.5471 | 2551 | 0 | 12
39041.5476 | 2331 | 0 | 12
39041.5481 | 2128 | 0 | 12
39041.5486 | 1994 | 0 | 12
39041.5491 | 1955 | 0 | 12
39041.5496 | 1991 | 0 | 12
12
39041.5355 | 0 | 0 | 13
39041.536 | 0 | 0 | 13
39041.5365 | 0 | 0 | 13
39041.5369 | 0 | 0 | 13
39041.5374 | 0 | 0 | 13
39041.5379 | 0 | 0 | 13
39041.5384 | 0 | 0 | 13
39041.5389 | 0 | 0 | 13
39041.5394 | 0 | 0 | 13
39041.5399 | 0 | 0 | 13
39041.5403 | 0 | 0 | 13
39041.5408 | 0 | 0 | 13
39041.5413 | 2402 | 0 | 13
39041.5418 | 2050 | 0 | 13
39041.5423 | 2515 | 0 | 13
39041.5428 | 2116 | 0 | 13
39041.5433 | 2095 | 0 | 13
39041.5437 | 2002 | 0 | 13
39041.5442 | 2114 | 0 | 13
39041.5447 | 2367 | 0 | 13
39041.5452 | 1987 | 0 | 13
39041.5457 | 2375 | 0 | 13
39041.5462 | 2579 | 0 | 13
39041.5467 | 1970 | 0 | 13
39041.5472 | 2140 | 0 | 13
39041.5476 | 2583 | 0 | 13
39041.5481 | 2569 | 0 | 13
39041.5486 | 1994 | 0 | 13
39041.5491 | 2389 | 0 | 13
39041.5496 | 1967 | 0 | 13
13
39041.5355 | 0 | 0 | 14
39041.536 | 0 | 0 | 14
39041.5365 | 0 | 0 | 14
39041.537 | 0 | 0 | 14
39041.5375 | 0 | 0 | 14
39041.5379 | 0 | 0 | 14
39041.5384 | 0 | 0 | 14
39041.5389 | 0 | 0 | 14
39041.5394 | 0 | 0 | 14
39041.5399 | 0 | 0 | 14
39041.5404 | 0 | 0 | 14
39041.5409 | 0 | 0 | 14
39041.5413 | 2448 | 0 | 14
39041.5418 | 2323 | 0 | 14
39041.5423 | 2096 | 0 | 14
39041.5428 | 2231 | 0 | 14
39041.5433 | 2494 | 0 | 14
39041.5438 | 2306 | 0 | 14
39041.5443 | 2406 | 0 | 14
39041.5447 | 2256 | 0 | 14
39041.5452 | 2406 | 0 | 14
39041.5457 | 1985 | 0 | 14
39041.5462 | 2536 | 0 | 14
39041.5467 | 2296 | 0 | 14
39041.5472 | 2574 | 0 | 14
39041.5477 | 2553 | 0 | 14
39041.5481 | 2578 | 0 | 14
39041.5486 | 2083 | 0 | 14
39041.5491 | 2140 | 0 | 14
39041.5496 | 2116 | 0 | 14
14
39041.5355 | 0 | 0 | 15
39041.536 | 0 | 0 | 15
39041.5365 | 0 | 0 | 15
39041.537 | 0 | 0 | 15
39041.5375 | 0 | 0 | 15
39041.538 | 0 | 0 | 15
39041.5384 | 0 | 0 | 15
39041.5389 | 0 | 0 | 15
39041.5394 | 0 | 0 | 15
39041.5399 | 0 | 0 | 15
39041.5404 | 0 | 0 | 15
39041.5409 | 0 | 0 | 15
39041.5414 | 2464 | 0 | 15
39041.5418 | 2290 | 0 | 15
39041.5423 | 1976 | 0 | 15
39041.5428 | 2049 | 0 | 15
39041.5433 | 2220 | 0 | 15
39041.5438 | 2121 | 0 | 15
39041.5443 | 2245 | 0 | 15
39041.5448 | 2356 | 0 | 15
39041.5452 | 2099 | 0 | 15
39041.5457 | 2196 | 0 | 15
39041.5462 | 2362 | 0 | 15
39041.5467 | 2540 | 0 | 15
39041.5472 | 2194 | 0 | 15
39041.5477 | 2209 | 0 | 15
39041.5482 | 2362 | 0 | 15
39041.5486 | 2107 | 0 | 15
39041.5491 | 2426 | 0 | 15
39041.5496 | 1963 | 1 | 15
15
39041.5355 | 0 | 0 | 16
39041.536 | 0 | 0 | 16
39041.5365 | 0 | 0 | 16
39041.537 | 0 | 0 | 16
39041.5375 | 0 | 0 | 16
39041.538 | 0 | 0 | 16
39041.5385 | 0 | 0 | 16
39041.5389 | 0 | 0 | 16
39041.5394 | 0 | 0 | 16
39041.5399 | 0 | 0 | 16
39041.5404 | 0 | 0 | 16
39041.5409 | 0 | 0 | 16
39041.5414 | 0 | 0 | 16
39041.5419 | 1 | 0 | 16
39041.5423 | 1096 | 0 | 16
39041.5428 | 1420 | 0 | 16
39041.5433 | 1716 | 0 | 16
39041.5438 | 1422 | 0 | 16
39041.5443 | 2050 | 0 | 16
39041.5448 | 2436 | 0 | 16
39041.5453 | 2425 | 0 | 16
39041.5457 | 2404 | 0 | 16
39041.5462 | 2010 | 0 | 16
39041.5467 | 2426 | 0 | 16
39041.5472 | 2529 | 0 | 16
39041.5477 | 2446 | 0 | 16
39041.5482 | 2015 | 0 | 16
39041.5487 | 1927 | 0 | 16
39041.5491 | 2001 | 1 | 16
39041.5496 | 2015 | 1 | 16
16
39041.5356 | 0 | 0 | 17
39041.536 | 0 | 0 | 17
39041.5365 | 0 | 0 | 17
39041.537 | 0 | 0 | 17
39041.5375 | 0 | 0 | 17
39041.538 | 0 | 0 | 17
39041.5385 | 0 | 0 | 17
39041.539 | 0 | 0 | 17
39041.5394 | 0 | 0 | 17
39041.5399 | 0 | 0 | 17
39041.5404 | 0 | 0 | 17
39041.5409 | 0 | 0 | 17
39041.5414 | 2046 | 0 | 17
39041.5419 | 2591 | 0 | 17
39041.5424 | 2365 | 0 | 17
39041.5428 | 2377 | 0 | 17
39041.5433 | 2047 | 0 | 17
39041.5438 | 2074 | 0 | 17
39041.5443 | 2200 | 0 | 17
39041.5448 | 2540 | 0 | 17
39041.5453 | 2256 | 0 | 17
39041.5458 | 2532 | 0 | 17
39041.5462 | 2499 | 0 | 17
39041.5467 | 2455 | 0 | 17
39041.5472 | 2070 | 0 | 17
39041.5477 | 2198 | 0 | 17
39041.5482 | 2120 | 0 | 17
39041.5487 | 2203 | 0 | 17
39041.5492 | 2503 | 0 | 17
39041.5497 | 1865 | 1 | 17
17
39041.5356 | 0 | 0 | 18
39041.5361 | 0 | 0 | 18
39041.5365 | 0 | 0 | 18
39041.537 | 0 | 0 | 18
39041.5375 | 0 | 0 | 18
39041.538 | 0 | 0 | 18
39041.5385 | 0 | 0 | 18
39041.539 | 0 | 0 | 18
39041.5395 | 0 | 0 | 18
39041.5399 | 0 | 0 | 18
39041.5404 | 0 | 0 | 18
39041.5409 | 0 | 0 | 18
39041.5414 | 0 | 0 | 18
39041.5419 | 1 | 0 | 18
39041.5424 | 1363 | 0 | 18
39041.5429 | 1661 | 0 | 18
39041.5433 | 1871 | 0 | 18
39041.5438 | 2052 | 0 | 18
39041.5443 | 1592 | 0 | 18
39041.5448 | 2222 | 0 | 18
39041.5453 | 1841 | 0 | 18
39041.5458 | 2051 | 0 | 18
39041.5463 | 2264 | 0 | 18
39041.5467 | 2370 | 0 | 18
39041.5472 | 1945 | 0 | 18
39041.5477 | 2471 | 0 | 18
39041.5482 | 2078 | 0 | 18
39041.5487 | 2163 | 0 | 18
39041.5492 | 2376 | 0 | 18
39041.5497 | 1901 | 0 | 18
18
39041.5356 | 0 | 0 | 19
39041.5361 | 0 | 0 | 19
39041.5366 | 0 | 0 | 19
39041.537 | 0 | 0 | 19
39041.5375 | 0 | 0 | 19
39041.538 | 0 | 0 | 19
39041.5385 | 0 | 0 | 19
39041.539 | 0 | 0 | 19
39041.5395 | 0 | 0 | 19
39041.54 | 0 | 0 | 19
39041.5405 | 0 | 0 | 19
39041.5409 | 0 | 0 | 19
39041.5414 | 0 | 0 | 19
39041.5419 | 0 | 0 | 19
39041.5424 | 12 | 4 | 19
39041.5429 | 951 | 572 | 19
39041.5434 | 1872 | 23 | 19
39041.5439 | 2169 | 4 | 19
39041.5443 | 2430 | 2 | 19
39041.5448 | 2315 | 1 | 19
39041.5453 | 2340 | 1 | 19
39041.5458 | 2029 | 0 | 19
39041.5463 | 2166 | 0 | 19
39041.5468 | 1986 | 0 | 19
39041.5473 | 2155 | 0 | 19
39041.5477 | 2548 | 0 | 19
39041.5482 | 2537 | 0 | 19
39041.5487 | 2413 | 1 | 19
39041.5492 | 2295 | 4 | 19
39041.5497 | 2078 | 20 | 19
19
39041.5356 | 0 | 0 | 20
39041.5361 | 0 | 0 | 20
39041.5366 | 0 | 0 | 20
39041.5371 | 0 | 0 | 20
39041.5375 | 0 | 0 | 20
39041.538 | 0 | 0 | 20
39041.5385 | 0 | 0 | 20
39041.539 | 0 | 0 | 20
39041.5395 | 0 | 0 | 20
39041.54 | 0 | 0 | 20
39041.5405 | 0 | 0 | 20
39041.5409 | 0 | 0 | 20
39041.5414 | 0 | 0 | 20
39041.5419 | 0 | 0 | 20
39041.5424 | 35 | 16 | 20
39041.5429 | 940 | 628 | 20
39041.5434 | 2252 | 15 | 20
39041.5439 | 2128 | 4 | 20
39041.5444 | 2381 | 3 | 20
39041.5448 | 2222 | 1 | 20
39041.5453 | 2537 | 1 | 20
39041.5458 | 2319 | 0 | 20
39041.5463 | 2507 | 1 | 20
39041.5468 | 2301 | 0 | 20
39041.5473 | 2526 | 1 | 20
39041.5478 | 2039 | 0 | 20
39041.5482 | 2199 | 0 | 20
39041.5487 | 2360 | 0 | 20
39041.5492 | 2294 | 3 | 20
39041.5497 | 1985 | 22 | 20
20
39041.5356 | 0 | 0 | 21
39041.5361 | 0 | 0 | 21
39041.5366 | 0 | 0 | 21
39041.5371 | 0 | 0 | 21
39041.5376 | 0 | 0 | 21
39041.5381 | 0 | 0 | 21
39041.5385 | 0 | 0 | 21
39041.539 | 0 | 0 | 21
39041.5395 | 0 | 0 | 21
39041.54 | 0 | 0 | 21
39041.5405 | 0 | 0 | 21
39041.541 | 0 | 0 | 21
39041.5415 | 0 | 0 | 21
39041.5419 | 0 | 0 | 21
39041.5424 | 0 | 0 | 21
39041.5429 | 411 | 0 | 21
39041.5434 | 2379 | 0 | 21
39041.5439 | 1909 | 0 | 21
39041.5444 | 2069 | 0 | 21
39041.5448 | 2046 | 0 | 21
39041.5453 | 2116 | 0 | 21
39041.5458 | 2309 | 0 | 21
39041.5463 | 2523 | 0 | 21
39041.5468 | 2204 | 0 | 21
39041.5473 | 2111 | 0 | 21
39041.5478 | 2266 | 0 | 21
39041.5483 | 2358 | 0 | 21
39041.5487 | 2343 | 0 | 21
39041.5492 | 2026 | 0 | 21
39041.5497 | 2351 | 0 | 21
21
39041.5356 | 0 | 0 | 22
39041.5361 | 0 | 0 | 22
39041.5366 | 0 | 0 | 22
39041.5371 | 0 | 0 | 22
39041.5376 | 0 | 0 | 22
39041.5381 | 0 | 0 | 22
39041.5386 | 0 | 0 | 22
39041.539 | 0 | 0 | 22
39041.5395 | 0 | 0 | 22
39041.54 | 0 | 0 | 22
39041.5405 | 0 | 0 | 22
39041.541 | 0 | 0 | 22
39041.5415 | 0 | 0 | 22
39041.542 | 5 | 0 | 22
39041.5424 | 988 | 0 | 22
39041.5429 | 1869 | 0 | 22
39041.5434 | 2478 | 0 | 22
39041.5439 | 1732 | 0 | 22
39041.5444 | 1912 | 0 | 22
39041.5449 | 2393 | 0 | 22
39041.5454 | 2079 | 0 | 22
39041.5458 | 2054 | 0 | 22
39041.5463 | 2003 | 0 | 22
39041.5468 | 2459 | 0 | 22
39041.5473 | 2112 | 0 | 22
39041.5478 | 2548 | 0 | 22
39041.5483 | 2059 | 0 | 22
39041.5488 | 1939 | 0 | 22
39041.5492 | 2298 | 0 | 22
39041.5497 | 1904 | 0 | 22
22
39041.5356 | 0 | 0 | 23
39041.5361 | 0 | 0 | 23
39041.5366 | 0 | 0 | 23
39041.5371 | 0 | 0 | 23
39041.5376 | 0 | 0 | 23
39041.5381 | 0 | 0 | 23
39041.5386 | 0 | 0 | 23
39041.5391 | 0 | 0 | 23
39041.5395 | 0 | 0 | 23
39041.54 | 0 | 0 | 23
39041.5405 | 0 | 0 | 23
39041.541 | 0 | 0 | 23
39041.5415 | 0 | 0 | 23
39041.542 | 0 | 0 | 23
39041.5425 | 1 | 0 | 23
39041.5429 | 969 | 0 | 23
39041.5434 | 1985 | 0 | 23
39041.5439 | 2388 | 0 | 23
39041.5444 | 2132 | 0 | 23
39041.5449 | 2165 | 0 | 23
39041.5454 | 1974 | 0 | 23
39041.5459 | 2493 | 0 | 23
39041.5463 | 2282 | 0 | 23
39041.5468 | 1973 | 0 | 23
39041.5473 | 2422 | 0 | 23
39041.5478 | 2158 | 0 | 23
39041.5483 | 2538 | 0 | 23
39041.5488 | 2515 | 0 | 23
39041.5493 | 2243 | 0 | 23
39041.5497 | 2239 | 0 | 23
23
39041.5357 | 0 | 0 | 24
39041.5362 | 0 | 0 | 24
39041.5366 | 0 | 0 | 24
39041.5371 | 0 | 0 | 24
39041.5376 | 0 | 0 | 24
39041.5381 | 0 | 0 | 24
39041.5386 | 0 | 0 | 24
39041.5391 | 0 | 0 | 24
39041.5396 | 0 | 0 | 24
39041.54 | 0 | 0 | 24
39041.5405 | 0 | 0 | 24
39041.541 | 0 | 0 | 24
39041.5415 | 0 | 0 | 24
39041.542 | 422 | 0 | 24
39041.5425 | 2176 | 0 | 24
39041.543 | 1710 | 0 | 24
39041.5434 | 1822 | 0 | 24
39041.5439 | 2176 | 0 | 24
39041.5444 | 1905 | 0 | 24
39041.5449 | 2157 | 0 | 24
39041.5454 | 2320 | 0 | 24
39041.5459 | 1866 | 0 | 24
39041.5464 | 2115 | 0 | 24
39041.5469 | 1939 | 0 | 24
39041.5473 | 2139 | 0 | 24
39041.5478 | 2382 | 0 | 24
39041.5483 | 2512 | 0 | 24
39041.5488 | 2390 | 0 | 24
39041.5493 | 2039 | 0 | 24
39041.5498 | 2132 | 0 | 24
24
39041.5357 | 0 | 0 | 25
39041.5362 | 0 | 0 | 25
39041.5367 | 0 | 0 | 25
39041.5371 | 0 | 0 | 25
39041.5376 | 0 | 0 | 25
39041.5381 | 0 | 0 | 25
39041.5386 | 0 | 0 | 25
39041.5391 | 0 | 0 | 25
39041.5396 | 0 | 0 | 25
39041.5401 | 0 | 0 | 25
39041.5405 | 0 | 0 | 25
39041.541 | 0 | 0 | 25
39041.5415 | 0 | 0 | 25
39041.542 | 0 | 0 | 25
39041.5425 | 13 | 0 | 25
39041.543 | 972 | 0 | 25
39041.5435 | 1857 | 0 | 25
39041.5439 | 2189 | 0 | 25
39041.5444 | 2501 | 0 | 25
39041.5449 | 2273 | 0 | 25
39041.5454 | 2298 | 0 | 25
39041.5459 | 1939 | 0 | 25
39041.5464 | 2487 | 0 | 25
39041.5469 | 2193 | 0 | 25
39041.5473 | 2453 | 0 | 25
39041.5478 | 1977 | 0 | 25
39041.5483 | 2331 | 0 | 25
39041.5488 | 2032 | 0 | 25
39041.5493 | 2006 | 0 | 25
39041.5498 | 1958 | 0 | 25
25
39041.5357 | 0 | 0 | 26
39041.5362 | 0 | 0 | 26
39041.5367 | 0 | 0 | 26
39041.5372 | 0 | 0 | 26
39041.5377 | 0 | 0 | 26
39041.5381 | 0 | 0 | 26
39041.5386 | 0 | 0 | 26
39041.5391 | 0 | 0 | 26
39041.5396 | 0 | 0 | 26
39041.5401 | 0 | 0 | 26
39041.5406 | 0 | 0 | 26
39041.5411 | 0 | 0 | 26
39041.5415 | 0 | 0 | 26
39041.542 | 19 | 0 | 26
39041.5425 | 2375 | 0 | 26
39041.543 | 1957 | 0 | 26
39041.5435 | 2132 | 0 | 26
39041.544 | 1872 | 0 | 26
39041.5445 | 1906 | 0 | 26
39041.5449 | 1972 | 0 | 26
39041.5454 | 2332 | 0 | 26
39041.5459 | 2116 | 0 | 26
39041.5464 | 2484 | 0 | 26
39041.5469 | 2211 | 0 | 26
39041.5474 | 2069 | 0 | 26
39041.5478 | 2145 | 0 | 26
39041.5483 | 2327 | 0 | 26
39041.5488 | 2014 | 0 | 26
39041.5493 | 2154 | 0 | 26
39041.5498 | 2295 | 0 | 26
26
39041.5357 | 0 | 0 | 27
39041.5362 | 0 | 0 | 27
39041.5367 | 0 | 0 | 27
39041.5372 | 0 | 0 | 27
39041.5377 | 0 | 0 | 27
39041.5381 | 0 | 0 | 27
39041.5386 | 0 | 0 | 27
39041.5391 | 0 | 0 | 27
39041.5396 | 0 | 0 | 27
39041.5401 | 0 | 0 | 27
39041.5406 | 0 | 0 | 27
39041.5411 | 0 | 0 | 27
39041.5416 | 0 | 0 | 27
39041.542 | 0 | 0 | 27
39041.5425 | 44 | 0 | 27
39041.543 | 1563 | 0 | 27
39041.5435 | 2445 | 0 | 27
39041.544 | 1973 | 0 | 27
39041.5445 | 1915 | 0 | 27
39041.545 | 2020 | 0 | 27
39041.5454 | 2194 | 0 | 27
39041.5459 | 2443 | 0 | 27
39041.5464 | 2126 | 0 | 27
39041.5469 | 2087 | 0 | 27
39041.5474 | 2381 | 0 | 27
39041.5479 | 2387 | 0 | 27
39041.5484 | 2108 | 0 | 27
39041.5488 | 2047 | 0 | 27
39041.5493 | 2105 | 0 | 27
39041.5498 | 2014 | 0 | 27
27
39041.5357 | 0 | 0 | 28
39041.5362 | 0 | 0 | 28
39041.5367 | 0 | 0 | 28
39041.5372 | 0 | 0 | 28
39041.5377 | 0 | 0 | 28
39041.5382 | 0 | 0 | 28
39041.5386 | 0 | 0 | 28
39041.5391 | 0 | 0 | 28
39041.5396 | 0 | 0 | 28
39041.5401 | 0 | 0 | 28
39041.5406 | 0 | 0 | 28
39041.5411 | 0 | 0 | 28
39041.5416 | 0 | 0 | 28
39041.542 | 6 | 0 | 28
39041.5425 | 2309 | 0 | 28
39041.543 | 1411 | 0 | 28
39041.5435 | 2204 | 0 | 28
39041.544 | 2017 | 0 | 28
39041.5445 | 1809 | 0 | 28
39041.545 | 2207 | 0 | 28
39041.5455 | 2096 | 0 | 28
39041.5459 | 2450 | 0 | 28
39041.5464 | 2225 | 0 | 28
39041.5469 | 2379 | 0 | 28
39041.5474 | 1976 | 0 | 28
39041.5479 | 2012 | 0 | 28
39041.5484 | 2479 | 0 | 28
39041.5489 | 2197 | 0 | 28
39041.5493 | 2093 | 0 | 28
39041.5498 | 1920 | 0 | 28
28
39041.5358 | 0 | 0 | 29
39041.5362 | 0 | 0 | 29
39041.5367 | 0 | 0 | 29
39041.5372 | 0 | 0 | 29
39041.5377 | 0 | 0 | 29
39041.5382 | 0 | 0 | 29
39041.5387 | 0 | 0 | 29
39041.5392 | 0 | 0 | 29
39041.5396 | 0 | 0 | 29
39041.5401 | 0 | 0 | 29
39041.5406 | 0 | 0 | 29
39041.5411 | 0 | 0 | 29
39041.5416 | 0 | 0 | 29
39041.5421 | 240 | 18 | 29
39041.5426 | 2105 | 6 | 29
39041.543 | 1825 | 43 | 29
39041.5435 | 2100 | 12 | 29
39041.544 | 1662 | 0 | 29
39041.5445 | 2081 | 13 | 29
39041.545 | 1927 | 11 | 29
39041.5455 | 2407 | 3 | 29
39041.546 | 2007 | 2 | 29
39041.5464 | 2168 | 1 | 29
39041.5469 | 2293 | 0 | 29
39041.5474 | 2007 | 0 | 29
39041.5479 | 2368 | 0 | 29
39041.5484 | 2542 | 0 | 29
39041.5489 | 2178 | 1 | 29
39041.5494 | 2093 | 1 | 29
39041.5498 | 1896 | 2 | 29
29
39041.5358 | 0 | 0 | 30
39041.5362 | 0 | 0 | 30
39041.5367 | 0 | 0 | 30
39041.5372 | 0 | 0 | 30
39041.5377 | 0 | 0 | 30
39041.5382 | 0 | 0 | 30
39041.5387 | 0 | 0 | 30
39041.5392 | 0 | 0 | 30
39041.5397 | 0 | 0 | 30
39041.5401 | 0 | 0 | 30
39041.5406 | 0 | 0 | 30
39041.5411 | 0 | 0 | 30
39041.5421 | 386 | 243 | 30
39041.5426 | 2136 | 39 | 30
39041.5431 | 1918 | 2 | 30
39041.5435 | 2247 | 4 | 30
39041.544 | 2361 | 0 | 30
39041.5445 | 1971 | 15 | 30
39041.545 | 2382 | 9 | 30
39041.5455 | 1763 | 1 | 30
39041.546 | 2037 | 1 | 30
39041.5465 | 2015 | 0 | 30
39041.5469 | 1921 | 0 | 30
39041.5474 | 1981 | 0 | 30
39041.5479 | 2197 | 0 | 30
39041.5484 | 1931 | 0 | 30
39041.5489 | 1978 | 0 | 30
39041.5494 | 2326 | 1 | 30
39041.5499 | 1946 | 2 | 30
30

## Temperatures
DAQ Time | Burner Time | Bundle center | Air above bundle | Air below bundle | Intra-bundle | TRAY C
0 | -207 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
1 | -206 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
2 | -205 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8
3 | -204 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
4 | -203 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
5 | -202 | 15.8 | 15.7 | 16.1 | 15.8 | 17.7
6 | -201 | 15.8 | 15.7 | 16.1 | 15.8 | 17.7
7 | -200 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
8 | -199 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
9 | -198 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
10 | -197 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
11 | -196 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
12 | -195 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
13 | -194 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
14 | -193 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
15 | -192 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
16 | -191 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
17 | -190 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
18 | -189 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
19 | -188 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
20 | -187 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
21 | -186 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
22 | -185 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
23 | -184 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
24 | -183 | 15.8 | 15.7 | 16.1 | 15.8 | 17.7
25 | -182 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
26 | -181 | 15.8 | 15.7 | 16.1 | 15.8 | 17.7
27 | -180 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
28 | -179 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
29 | -178 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
30 | -177 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
31 | -176 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
32 | -175 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
33 | -174 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
34 | -173 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
35 | -172 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8
36 | -171 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8
37 | -170 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
38 | -169 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
39 | -168 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
40 | -167 | 15.8 | 15.7 | 16.1 | 15.8 | 17.7
41 | -166 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
42 | -165 | 15.8 | 15.7 | 16.1 | 15.8 | 17.7
43 | -164 | 15.8 | 15.7 | 16.1 | 15.7 | 17.7
44 | -163 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8
45 | -162 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8
46 | -161 | 15.8 | 15.7 | 16.1 | 15.7 | 17.7
47 | -160 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
48 | -159 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
49 | -158 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8
50 | -157 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8
51 | -156 | 15.8 | 15.7 | 16.1 | 15.7 | 17.7
52 | -155 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
53 | -154 | 15.8 | 15.7 | 16.1 | 15.8 | 17.7
54 | -153 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
55 | -152 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
56 | -151 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
57 | -150 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8
58 | -149 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8
59 | -148 | 15.8 | 15.7 | 16.1 | 15.8 | 17.7
60 | -147 | 15.8 | 15.7 | 16.1 | 15.8 | 17.7
61 | -146 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8
62 | -145 | 15.8 | 15.7 | 16.1 | 15.7 | 17.7
63 | -144 | 15.8 | 15.7 | 16.1 | 15.7 | 17.7
64 | -143 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8
65 | -142 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8
66 | -141 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
67 | -140 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
68 | -139 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8
69 | -138 | 15.8 | 15.7 | 16.1 | 15.8 | 17.7
70 | -137 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8
71 | -136 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8
72 | -135 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
73 | -134 | 15.8 | 15.7 | 16.1 | 15.8 | 17.7
74 | -133 | 15.8 | 15.7 | 16.1 | 15.7 | 17.7
75 | -132 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8
76 | -131 | 15.8 | 15.7 | 16.1 | 15.7 | 17.7
77 | -130 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
78 | -129 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
79 | -128 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8
80 | -127 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
81 | -126 | 15.8 | 15.8 | 16.1 | 15.8 | 17.8
82 | -125 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
83 | -124 | 15.8 | 15.7 | 16.1 | 15.8 | 17.7
84 | -123 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
85 | -122 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
86 | -121 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
87 | -120 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8
88 | -119 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
89 | -118 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
90 | -117 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
91 | -116 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
92 | -115 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
93 | -114 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
94 | -113 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
95 | -112 | 15.8 | 15.8 | 16.1 | 15.7 | 17.8
96 | -111 | 15.8 | 15.8 | 16.1 | 15.8 | 17.8
97 | -110 | 15.8 | 15.8 | 16.1 | 15.8 | 17.8
98 | -109 | 15.8 | 15.8 | 16.1 | 15.8 | 17.8
99 | -108 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
100 | -107 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
101 | -106 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
102 | -105 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
103 | -104 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
104 | -103 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
105 | -102 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
106 | -101 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
107 | -100 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
108 | -99 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
109 | -98 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
110 | -97 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8
111 | -96 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
112 | -95 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
113 | -94 | 15.8 | 15.8 | 16.1 | 15.8 | 17.8
114 | -93 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
115 | -92 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
116 | -91 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
117 | -90 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
118 | -89 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
119 | -88 | 15.8 | 15.7 | 16.1 | 15.8 | 17.7
120 | -87 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
121 | -86 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
122 | -85 | 15.8 | 15.8 | 16.1 | 15.8 | 17.8
123 | -84 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
124 | -83 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
125 | -82 | 15.8 | 15.8 | 16.1 | 15.8 | 17.8
126 | -81 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
127 | -80 | 15.8 | 15.8 | 16.1 | 15.8 | 17.8
128 | -79 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
129 | -78 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
130 | -77 | 15.8 | 15.8 | 16.1 | 15.8 | 17.8
131 | -76 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
132 | -75 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
133 | -74 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
134 | -73 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
135 | -72 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
136 | -71 | 15.8 | 15.8 | 16.1 | 15.8 | 17.8
137 | -70 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
138 | -69 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8
139 | -68 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
140 | -67 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
141 | -66 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
142 | -65 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
143 | -64 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
144 | -63 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
145 | -62 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
146 | -61 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
147 | -60 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
148 | -59 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
149 | -58 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
150 | -57 | 15.8 | 15.8 | 16.1 | 15.8 | 17.8
151 | -56 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
152 | -55 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
153 | -54 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
154 | -53 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
155 | -52 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
156 | -51 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
157 | -50 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
158 | -49 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
159 | -48 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
160 | -47 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
161 | -46 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
162 | -45 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
163 | -44 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
164 | -43 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
165 | -42 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
166 | -41 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8
167 | -40 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8
168 | -39 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8
169 | -38 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8
170 | -37 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8
171 | -36 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8
172 | -35 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
173 | -34 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8
174 | -33 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8
175 | -32 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8
176 | -31 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8
177 | -30 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8
178 | -29 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8
179 | -28 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8
180 | -27 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8
181 | -26 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8
182 | -25 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
183 | -24 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8
184 | -23 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8
185 | -22 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8
186 | -21 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8
187 | -20 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8
188 | -19 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8
189 | -18 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
190 | -17 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8
191 | -16 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8
192 | -15 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8
193 | -14 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8
194 | -13 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8
195 | -12 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8
196 | -11 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8
197 | -10 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8
198 | -9 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8
199 | -8 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8
200 | -7 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8
201 | -6 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8
202 | -5 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8
203 | -4 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8
204 | -3 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8
205 | -2 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8
206 | -1 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8
207 | 0 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
208 | 1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
209 | 2 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8
210 | 3 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8
211 | 4 | 15.8 | 15.9 | 17 | 15.8 | 18
212 | 5 | 15.8 | 23 | 35.8 | 19 | 21.3
213 | 6 | 15.8 | 43.8 | 75.4 | 26.2 | 29.3
214 | 7 | 15.9 | 69.6 | 128 | 31.4 | 39.1
215 | 8 | 16.2 | 109.6 | 195.7 | 39.7 | 56.2
216 | 9 | 16.7 | 158.1 | 265.2 | 47.4 | 69.5
217 | 10 | 17.4 | 199.3 | 321.7 | 53.5 | 84
218 | 11 | 18.1 | 247.8 | 378 | 61.2 | 101.9
219 | 12 | 19 | 277.2 | 409.7 | 65.3 | 118.6
220 | 13 | 19.9 | 326.2 | 465.8 | 70.8 | 135.1
221 | 14 | 20.8 | 382.1 | 517.8 | 77.3 | 159.3
222 | 15 | 21.8 | 429 | 562.8 | 81.3 | 183.6
223 | 16 | 22.8 | 468.6 | 601.7 | 83.1 | 203.7
224 | 17 | 23.9 | 506.7 | 640.4 | 87 | 222
225 | 18 | 24.9 | 544.6 | 672.1 | 91 | 243.9
226 | 19 | 26 | 585.4 | 702.9 | 94.6 | 262.8
227 | 20 | 27 | 617 | 727.4 | 99.7 | 280.6
228 | 21 | 28 | 646.5 | 750.5 | 107.5 | 300.4
229 | 22 | 29.1 | 667.1 | 766.3 | 111.3 | 319.3
230 | 23 | 30.3 | 672.4 | 775.1 | 113.4 | 333.9
231 | 24 | 31.6 | 676.5 | 784.2 | 117 | 349
232 | 25 | 32.9 | 682.9 | 791 | 119.4 | 364.8
233 | 26 | 34.2 | 678.6 | 793.1 | 122.3 | 377.6
234 | 27 | 35.7 | 675.1 | 788.4 | 125 | 387
235 | 28 | 37.1 | 659 | 776 | 126.4 | 395.2
236 | 29 | 38.6 | 650.4 | 773.2 | 128.8 | 405.6
237 | 30 | 40.2 | 644.2 | 774.4 | 130.9 | 413.5
238 | 31 | 41.9 | 637.9 | 771.6 | 132.1 | 419.2
239 | 32 | 43.6 | 626.4 | 763.8 | 132.8 | 424.8
240 | 33 | 45.5 | 615.1 | 755.2 | 134.1 | 431.8
241 | 34 | 47.5 | 608.1 | 757.8 | 136.6 | 435
242 | 35 | 49.6 | 602.5 | 759.5 | 138.2 | 440.1
243 | 36 | 51.8 | 602.9 | 769.1 | 140.7 | 446.9
244 | 37 | 54.1 | 601 | 767.7 | 142.2 | 458
245 | 38 | 56.4 | 598.5 | 770.2 | 144.3 | 462.4
246 | 39 | 58.9 | 598.9 | 777.6 | 147.5 | 469.3
247 | 40 | 61.6 | 602.3 | 785.5 | 149.9 | 476.1
248 | 41 | 64.4 | 607.1 | 791.2 | 152.2 | 483.1
249 | 42 | 67.3 | 611 | 788.1 | 154.3 | 490.7
250 | 43 | 70.3 | 608 | 779.8 | 155.5 | 494.7
251 | 44 | 74.5 | 604.4 | 774.5 | 156.6 | 501.3
252 | 45 | 78.7 | 598.9 | 764.4 | 157.3 | 505.3
253 | 46 | 82.1 | 602.2 | 768.8 | 158.9 | 510.4
254 | 47 | 85.2 | 597.4 | 762.8 | 159.7 | 511.8
255 | 48 | 88.4 | 583.4 | 749.3 | 159.8 | 513.8
256 | 49 | 91.7 | 578.3 | 744.3 | 160 | 517.7
257 | 50 | 95 | 580.1 | 754.2 | 161.2 | 521.5
258 | 51 | 98.4 | 584.3 | 756.6 | 162.9 | 528.3
259 | 52 | 101.8 | 578.3 | 758.8 | 164.1 | 532.8
260 | 53 | 105.1 | 578.7 | 761.1 | 165.3 | 537.9
261 | 54 | 108.8 | 574.9 | 754.7 | 166.5 | 541
262 | 55 | 113.6 | 574.3 | 743.7 | 167.4 | 546.5
263 | 56 | 119 | 574.4 | 746.7 | 168.7 | 550.4
264 | 57 | 123.9 | 572.8 | 739.8 | 169.9 | 556.6
265 | 58 | 128.4 | 573.7 | 729.4 | 171 | 562.6
266 | 59 | 133.1 | 574.3 | 719.3 | 171.9 | 567.8
267 | 60 | 138 | 570.1 | 707.6 | 172.4 | 572.6
268 | 61 | 142.6 | 558.9 | 695.3 | 172.6 | 573.7
269 | 62 | 147.1 | 552.1 | 679.8 | 173 | 576
270 | 63 | 151.8 | 546.9 | 664.5 | 173.1 | 578.8
271 | 64 | 156.3 | 546.8 | 660.2 | 173.9 | 583.6
272 | 65 | 160.5 | 551.1 | 676.4 | 175.6 | 587.5
273 | 66 | 164.4 | 555.7 | 683 | 177 | 593
274 | 67 | 168.1 | 564.3 | 699.6 | 179.1 | 599.1
275 | 68 | 171.5 | 562 | 705 | 180.6 | 601.5
276 | 69 | 174.9 | 552.8 | 692.8 | 181.2 | 601
277 | 70 | 178.2 | 543.8 | 685.7 | 181.6 | 599.5
278 | 71 | 181.3 | 535.1 | 672.6 | 181.8 | 600.6
279 | 72 | 184.1 | 539.3 | 680.8 | 183 | 604.4
280 | 73 | 186.8 | 546.1 | 690.4 | 184.9 | 608.6
281 | 74 | 189.5 | 557.9 | 706.6 | 187.1 | 614.6
282 | 75 | 192.1 | 570.5 | 724.3 | 189.4 | 619
283 | 76 | 194.7 | 572.6 | 725.9 | 191.2 | 619.7
284 | 77 | 197.2 | 570.1 | 722 | 192.2 | 621.2
285 | 78 | 199.6 | 572.6 | 719.7 | 193 | 623.3
286 | 79 | 202.1 | 572.1 | 717.8 | 193.6 | 624.1
287 | 80 | 204.6 | 563.2 | 705.2 | 193.6 | 622.2
288 | 81 | 206.9 | 558.6 | 702.3 | 193.7 | 624.3
289 | 82 | 209.2 | 564.5 | 715.7 | 194.5 | 626.2
290 | 83 | 211.5 | 569.2 | 722.8 | 195.5 | 628.9
291 | 84 | 213.8 | 563.1 | 714.6 | 195.7 | 626.2
292 | 85 | 216.1 | 561.6 | 701.5 | 195.7 | 628.2
293 | 86 | 218.2 | 563.1 | 686 | 195.8 | 631.1
294 | 87 | 220.1 | 558.6 | 671.4 | 195.7 | 633
295 | 88 | 221.7 | 552.9 | 670.1 | 195.6 | 633.7
296 | 89 | 223.1 | 548.8 | 666.8 | 195.9 | 635.1
297 | 90 | 224.5 | 544.2 | 669.1 | 196.3 | 636.5
298 | 91 | 225.8 | 540.1 | 665.3 | 196.8 | 636.5
299 | 92 | 227 | 537.3 | 660.1 | 197.3 | 636.1
300 | 93 | 228.2 | 536 | 653.3 | 197.9 | 637.9
301 | 94 | 229.4 | 544.7 | 671.2 | 199.4 | 640.3
302 | 95 | 230.3 | 546.8 | 680.9 | 200.9 | 639.5
303 | 96 | 231.1 | 544 | 688.5 | 201.9 | 639
304 | 97 | 232 | 544.8 | 681.4 | 202.8 | 640.6
305 | 98 | 232.8 | 543.9 | 674.5 | 203.3 | 642.8
306 | 99 | 233.5 | 542.9 | 673.2 | 204.2 | 645.4
307 | 100 | 234 | 543.6 | 677.9 | 205 | 643.7
308 | 101 | 234.9 | 543.6 | 666.6 | 205.6 | 640.1
309 | 102 | 235.8 | 545.4 | 675.7 | 206.6 | 641.9
310 | 103 | 236.8 | 550 | 679.3 | 207.9 | 642.4
311 | 104 | 237.9 | 552.6 | 679.9 | 208.9 | 642.2
312 | 105 | 238.8 | 553.9 | 687.9 | 209.9 | 641
313 | 106 | 239.9 | 555.1 | 680.6 | 210.7 | 641.6
314 | 107 | 240.9 | 555.7 | 669.1 | 211.4 | 645
315 | 108 | 241.6 | 556.1 | 674.2 | 212.3 | 647.1
316 | 109 | 242.4 | 564.4 | 682.8 | 213.8 | 650.1
317 | 110 | 243.5 | 566.8 | 694.3 | 215.2 | 648.4
318 | 111 | 245 | 562.3 | 701 | 216.3 | 645.7
319 | 112 | 246.5 | 557.6 | 695.8 | 217.1 | 643.9
320 | 113 | 247.9 | 552.2 | 680.7 | 217.4 | 647.2
321 | 114 | 249.1 | 545 | 669.5 | 217.8 | 646.8
322 | 115 | 250.2 | 543.3 | 658.5 | 218.1 | 648.2
323 | 116 | 251.4 | 547.8 | 661.8 | 219.3 | 651
324 | 117 | 252.8 | 554.2 | 678.9 | 221 | 653.7
325 | 118 | 254.3 | 555.2 | 690.9 | 222.4 | 652.1
326 | 119 | 255.7 | 555.6 | 696.5 | 223.8 | 652.6
327 | 120 | 257.1 | 552.5 | 704.9 | 224.9 | 652
328 | 121 | 258.5 | 554.8 | 717.2 | 226.3 | 649.6
329 | 122 | 260.1 | 551.6 | 723.4 | 227.5 | 647.3
330 | 123 | 261.7 | 547.9 | 722.4 | 227.7 | 644.3
331 | 124 | 263.2 | 543.3 | 720.3 | 225.3 | 641.2
332 | 125 | 264.6 | 541.2 | 726.2 | 223.4 | 637.4
333 | 126 | 265.9 | 537.2 | 729.6 | 223.1 | 636.1
334 | 127 | 267.3 | 539.7 | 739.2 | 224.5 | 637.9
335 | 128 | 268.7 | 541.3 | 743.1 | 226.5 | 637.6
336 | 129 | 270.2 | 541.2 | 748.3 | 228.1 | 633.5
337 | 130 | 271.6 | 551 | 764.5 | 230.4 | 632.2
338 | 131 | 272.9 | 555.6 | 768.5 | 232.4 | 630.7
339 | 132 | 274.1 | 558.3 | 766.5 | 234 | 629.4
340 | 133 | 275.4 | 561.4 | 770.8 | 235.6 | 629.2
341 | 134 | 276.7 | 559.3 | 768.5 | 237.2 | 626.3
342 | 135 | 278.1 | 552.6 | 761.2 | 238.2 | 623.5
343 | 136 | 278.8 | 550.4 | 767.2 | 239.3 | 620.1
344 | 137 | 279.6 | 547 | 765.2 | 240.3 | 616
345 | 138 | 280.9 | 539.6 | 754.1 | 241 | 612.3
346 | 139 | 282.4 | 530.1 | 736.4 | 241.2 | 608.3
347 | 140 | 283.9 | 527.9 | 747.5 | 242.2 | 605.7
348 | 141 | 285.5 | 533.5 | 759.7 | 243.4 | 606.2
349 | 142 | 287.1 | 534.8 | 754.8 | 244.3 | 605.7
350 | 143 | 288.7 | 530.5 | 746.7 | 244.7 | 603.6
351 | 144 | 290.3 | 530.9 | 747.5 | 245.4 | 605.2
352 | 145 | 291.9 | 533.7 | 737.6 | 246.1 | 607.4
353 | 146 | 293.6 | 532.7 | 720.6 | 246.5 | 609.5
354 | 147 | 295.3 | 535.5 | 713.8 | 247 | 609.8
355 | 148 | 297 | 537.3 | 707.8 | 247.3 | 610.1
356 | 149 | 298.5 | 540 | 721.6 | 248 | 611.8
357 | 150 | 300 | 543.8 | 721.2 | 249.1 | 616.3
358 | 151 | 301.6 | 547.2 | 728.4 | 250 | 615.7
359 | 152 | 303.1 | 552.9 | 726.8 | 250.8 | 617
360 | 153 | 304.7 | 565.9 | 735 | 252.3 | 622.5
361 | 154 | 306.3 | 577.6 | 746.4 | 254.1 | 626.1
362 | 155 | 308 | 589.9 | 751.9 | 256 | 632.8
363 | 156 | 309.9 | 595.7 | 764 | 257.9 | 635.5
364 | 157 | 311.7 | 603.7 | 776 | 260.1 | 638.2
365 | 158 | 313.5 | 602.5 | 789.6 | 261.9 | 636.5
366 | 159 | 315.2 | 605.3 | 797.3 | 263.7 | 635.9
367 | 160 | 316.8 | 603.5 | 800.9 | 265.1 | 634.1
368 | 161 | 318.4 | 600.7 | 791.3 | 266.3 | 631.5
369 | 162 | 319.9 | 595.1 | 786 | 267.2 | 631.4
370 | 163 | 321.4 | 595 | 783.7 | 268.4 | 633
371 | 164 | 322.9 | 588.7 | 775.1 | 269.3 | 631.3
372 | 165 | 324.3 | 586.4 | 775.9 | 270.4 | 628.9
373 | 166 | 325.8 | 580.3 | 770.3 | 271.2 | 626.9
374 | 167 | 327.1 | 577.5 | 772.6 | 272 | 624.7
375 | 168 | 328.5 | 578.9 | 782.1 | 273.1 | 624.1
376 | 169 | 330 | 580.2 | 783.5 | 274.1 | 623.9
377 | 170 | 331.5 | 580 | 780.2 | 275.1 | 623.3
378 | 171 | 333.1 | 584 | 785.4 | 276.3 | 624.2
379 | 172 | 334.7 | 586.4 | 791.4 | 277.4 | 625.4
380 | 173 | 336.3 | 587.8 | 794.6 | 278.4 | 624.4
381 | 174 | 337.9 | 589.3 | 792.2 | 279.5 | 625.2
382 | 175 | 339.5 | 583.4 | 783.3 | 280.2 | 625.7
383 | 176 | 341 | 580.7 | 778.4 | 280.6 | 626.5
384 | 177 | 342.5 | 580.4 | 767.1 | 281.1 | 627.5
385 | 178 | 343.9 | 577.4 | 760.3 | 281.6 | 626.8
386 | 179 | 345.4 | 583.2 | 762 | 282.4 | 627.9
387 | 180 | 347 | 579.1 | 748.5 | 283 | 629.2
388 | 181 | 348.5 | 578.2 | 744.7 | 283.6 | 631.7
389 | 182 | 350 | 581.9 | 762.8 | 284.5 | 631.4
390 | 183 | 351.7 | 582.4 | 768.6 | 285.3 | 630
391 | 184 | 353.4 | 581.4 | 775.4 | 286.1 | 628.2
392 | 185 | 355.2 | 582.5 | 779.5 | 286.9 | 628.7
393 | 186 | 348.5 | 584.7 | 779.3 | 287.6 | 630.9
394 | 187 | 348.4 | 593.4 | 780.6 | 288.2 | 634.9
395 | 188 | 351.9 | 590.2 | 777.1 | 288.9 | 632.7
396 | 189 | 355.3 | 592.2 | 784.9 | 289.6 | 634.5
397 | 190 | 358.5 | 602.2 | 795.9 | 290.7 | 636.7
398 | 191 | 361.8 | 609 | 799.9 | 291.7 | 636.2
399 | 192 | 364.8 | 609.9 | 794.1 | 292.7 | 635.1
400 | 193 | 367.6 | 608.7 | 796.6 | 293.5 | 632.8
401 | 194 | 370.2 | 615.3 | 801 | 294.3 | 634
402 | 195 | 372.9 | 618.7 | 799.6 | 295.2 | 634.7
403 | 196 | 375.4 | 614.7 | 804.8 | 295.8 | 633.5
404 | 197 | 378.1 | 611.8 | 801.9 | 296.4 | 633.3
405 | 198 | 380.8 | 609.1 | 795.4 | 297 | 634.9
406 | 199 | 383.5 | 605.3 | 797.1 | 297.6 | 633.9
407 | 200 | 386.3 | 599.8 | 793.1 | 298.2 | 633.7
408 | 201 | 389.1 | 599.5 | 796.4 | 298.8 | 634.4
409 | 202 | 392 | 600.7 | 799.3 | 299.5 | 634.2
410 | 203 | 394.9 | 588.8 | 793.5 | 300.2 | 632.3
411 | 204 | 397.9 | 556.6 | 790.4 | 300.8 | 628.7
412 | 205 | 400.7 | 556.9 | 790.9 | 301.6 | 628.9
413 | 206 | 403.5 | 560.2 | 783.5 | 302.3 | 628
414 | 207 | 406.2 | 571.9 | 792.9 | 303.1 | 627.9
415 | 208 | 409.1 | 580.3 | 796.1 | 303.9 | 627.4
416 | 209 | 412 | 583.2 | 795.2 | 304.8 | 627
417 | 210 | 414.8 | 589.4 | 798.9 | 305.6 | 626.4
418 | 211 | 417.6 | 594.5 | 799.5 | 306.5 | 628.2
419 | 212 | 420.3 | 592.8 | 800.7 | 307.3 | 626.1
420 | 213 | 423.1 | 586.9 | 797.8 | 308.1 | 623.9
421 | 214 | 425.8 | 581.7 | 794.8 | 308.8 | 623.4
422 | 215 | 428.1 | 581.6 | 795.8 | 309.5 | 623.7
423 | 216 | 430.5 | 585 | 796.7 | 310.3 | 625.3
424 | 217 | 432.8 | 588 | 800.7 | 311.1 | 624.6
425 | 218 | 435.3 | 584.4 | 789.9 | 311.8 | 622.4
426 | 219 | 437.7 | 592.5 | 794.3 | 312.6 | 623.7
427 | 220 | 440 | 596.1 | 782.2 | 313.2 | 626.1
428 | 221 | 442.3 | 603.6 | 796.9 | 314 | 628.5
429 | 222 | 444.5 | 611.5 | 801.7 | 314.9 | 630.1
430 | 223 | 446.9 | 616.9 | 798.6 | 315.6 | 634.3
431 | 224 | 449.2 | 617.7 | 804.3 | 316.4 | 635
432 | 225 | 451.6 | 616.6 | 804.3 | 317.2 | 635.5
433 | 226 | 453.8 | 617.4 | 803.6 | 317.9 | 637.4
434 | 227 | 456.2 | 619.3 | 808.4 | 318.6 | 638.7
435 | 228 | 458.6 | 614.3 | 803.5 | 319.3 | 638.5
436 | 229 | 460.8 | 616.2 | 803.2 | 320 | 641.7
437 | 230 | 463.1 | 619.5 | 805.7 | 320.8 | 642.9
438 | 231 | 465.6 | 615.2 | 798.7 | 321.4 | 642.7
439 | 232 | 467.9 | 621.7 | 807.1 | 322.2 | 644
440 | 233 | 470.1 | 629.9 | 813.2 | 322.9 | 645
441 | 234 | 472.3 | 637.3 | 819.3 | 323.7 | 646.2
442 | 235 | 474.6 | 642 | 819.9 | 324.5 | 648
443 | 236 | 476.9 | 644.3 | 817.6 | 325.3 | 650.1
444 | 237 | 479.1 | 647.6 | 813.4 | 326 | 650.3
445 | 238 | 481.1 | 647.6 | 813.5 | 326.8 | 650.3
446 | 239 | 483 | 643.5 | 814 | 327.5 | 651.2
447 | 240 | 484.9 | 641.2 | 816.7 | 328.3 | 652.2
448 | 241 | 486.7 | 645.6 | 816.2 | 328.9 | 653.9
449 | 242 | 488.6 | 652.1 | 813.2 | 329.7 | 658.6
450 | 243 | 490.4 | 657.9 | 818.5 | 330.4 | 662.3
451 | 244 | 492.4 | 664.2 | 815.8 | 331.1 | 667
452 | 245 | 495 | 672.7 | 800.4 | 331.7 | 672.6
453 | 246 | 497.7 | 682.7 | 805 | 332.4 | 677.7
454 | 247 | 500.8 | 685.6 | 810.5 | 333 | 680.6
455 | 248 | 503.9 | 688.7 | 812.6 | 333.7 | 683.9
456 | 249 | 507.4 | 694.2 | 815.6 | 334.4 | 688.1
457 | 250 | 511 | 700.8 | 817.3 | 335.1 | 692.4
458 | 251 | 514.7 | 700.5 | 820.4 | 335.8 | 692.5
459 | 252 | 518.4 | 695.9 | 818.2 | 336.6 | 692.7
460 | 253 | 521.9 | 692.4 | 811.4 | 337.3 | 694.2
461 | 254 | 525.2 | 687.3 | 807.7 | 338 | 694.2
462 | 255 | 528.8 | 692.2 | 809.3 | 338.7 | 696.2
463 | 256 | 532.8 | 697.1 | 810.1 | 339.4 | 698.8
464 | 257 | 536.8 | 701.1 | 818.5 | 340.2 | 703.5
465 | 258 | 540.4 | 703.3 | 820.5 | 340.9 | 703.9
466 | 259 | 544.1 | 708.6 | 821.3 | 341.6 | 705.2
467 | 260 | 547.9 | 707.6 | 820.5 | 342.4 | 706.2
468 | 261 | 551.4 | 705.7 | 819.4 | 343.1 | 706.8
469 | 262 | 554.9 | 705.6 | 823.1 | 343.8 | 706.6
470 | 263 | 558.6 | 700.8 | 827.2 | 344.6 | 707.3
471 | 264 | 562 | 700.7 | 833.8 | 345.4 | 707.9
472 | 265 | 565.5 | 700.1 | 836.6 | 346.1 | 705.6
473 | 266 | 569.1 | 701.6 | 841.5 | 346.8 | 703.5
474 | 267 | 572.6 | 696.1 | 842.9 | 347.5 | 702.5
475 | 268 | 575.3 | 689.7 | 839.7 | 348.2 | 701.2
476 | 269 | 578.1 | 691 | 842 | 348.9 | 700.7
477 | 270 | 581 | 687.7 | 840.2 | 349.7 | 698.9
478 | 271 | 583.5 | 683.7 | 831.8 | 350.4 | 700.9
479 | 272 | 585.7 | 687 | 825 | 351.2 | 705.4
480 | 273 | 587.9 | 686.5 | 815.7 | 352 | 709.5
481 | 274 | 589.7 | 686 | 814.3 | 352.8 | 711.8
482 | 275 | 591.4 | 688.9 | 824.1 | 353.5 | 711.7
483 | 276 | 593.7 | 690.3 | 830.6 | 354.2 | 711.4
484 | 277 | 596.2 | 688 | 829.3 | 355 | 710.1
485 | 278 | 598.7 | 684.5 | 832.9 | 355.6 | 707.3
486 | 279 | 601.1 | 681 | 832.5 | 356.2 | 704
487 | 280 | 604 | 680.1 | 835.5 | 356.8 | 703.2
488 | 281 | 607.2 | 675.4 | 833.1 | 357.4 | 701.1
489 | 282 | 610.4 | 673 | 839.3 | 357.9 | 699.3
490 | 283 | 613.5 | 670.3 | 838.3 | 358.5 | 697.6
491 | 284 | 616.5 | 671.1 | 837.1 | 359.2 | 696.2
492 | 285 | 619.5 | 672.8 | 835.9 | 359.8 | 695.7
493 | 286 | 622.2 | 672.6 | 839.3 | 360.5 | 696
494 | 287 | 624.9 | 674.8 | 841.4 | 361.2 | 696.6
495 | 288 | 627.2 | 673.3 | 839.7 | 361.9 | 696.5
496 | 289 | 629.7 | 670 | 838.4 | 362.6 | 696.4
497 | 290 | 632 | 672.6 | 838.6 | 363.2 | 697.3
498 | 291 | 634.3 | 673.1 | 835.7 | 363.8 | 699.4
499 | 292 | 636.5 | 670.5 | 836.4 | 364.4 | 698.9
500 | 293 | 638.9 | 673.2 | 836.6 | 365 | 700.1
501 | 294 | 640.5 | 675.2 | 837.3 | 365.6 | 700.5
502 | 295 | 641.9 | 676.8 | 833.3 | 366.3 | 702.6
503 | 296 | 643.5 | 681 | 823.7 | 367 | 706.1
504 | 297 | 644.9 | 685.2 | 817.6 | 367.6 | 709.9
505 | 298 | 645.9 | 686.8 | 811.1 | 368.4 | 711.5
506 | 299 | 646.9 | 686 | 795.9 | 369.3 | 713.2
507 | 300 | 648.4 | 685.8 | 785.5 | 370.3 | 716.1
508 | 301 | 650 | 686.1 | 786 | 371.4 | 717.5
509 | 302 | 650.8 | 690.2 | 795 | 372.6 | 720
510 | 303 | 651.6 | 689.9 | 802.1 | 374.1 | 720.2
511 | 304 | 653 | 689.2 | 813.5 | 376.1 | 719.9
512 | 305 | 654.3 | 691.1 | 813 | 377.8 | 720.7
513 | 306 | 655.4 | 689.8 | 813.1 | 379.1 | 720.4
514 | 307 | 656.3 | 695.7 | 810.2 | 380.2 | 724.8
515 | 308 | 656.3 | 704 | 812 | 381.2 | 726.3
516 | 309 | 656.5 | 709.8 | 816.9 | 382.1 | 728.4
517 | 310 | 657.3 | 711.5 | 824.2 | 382.9 | 728.4
518 | 311 | 658.2 | 710.9 | 830.9 | 383.8 | 726.2
519 | 312 | 658.4 | 715.8 | 836 | 385 | 724.9
520 | 313 | 659.6 | 718 | 840.3 | 386 | 724.7
521 | 314 | 659.9 | 717.7 | 841.4 | 387 | 724
522 | 315 | 660.1 | 724.2 | 845.5 | 388 | 725.9
523 | 316 | 660.3 | 729.8 | 843.2 | 389 | 727.6
524 | 317 | 660.3 | 731.4 | 841 | 390.1 | 729.8
525 | 318 | 660.6 | 733.1 | 835.8 | 391.1 | 731.9
526 | 319 | 661.3 | 733.5 | 828.8 | 392.1 | 733.1
527 | 320 | 662.2 | 730.9 | 835 | 393 | 732.8
528 | 321 | 663.3 | 729.2 | 838.5 | 394.1 | 733.2
529 | 322 | 663.5 | 730.1 | 823.3 | 394.9 | 735.7
530 | 323 | 663.5 | 728.1 | 812.3 | 395.8 | 736.5
531 | 324 | 663.5 | 728.9 | 796.2 | 396.6 | 738.5
532 | 325 | 663.5 | 727.3 | 792.3 | 397.5 | 740.5
533 | 326 | 664.1 | 722.3 | 776.5 | 398.3 | 740.4
534 | 327 | 665 | 717.7 | 775.8 | 399.1 | 740.5
535 | 328 | 665.9 | 721.4 | 783.2 | 399.9 | 741.2
536 | 329 | 666.4 | 726.7 | 790.8 | 400.8 | 744
537 | 330 | 666.9 | 725.4 | 792.8 | 401.7 | 745.4
538 | 331 | 667.5 | 722.2 | 784.8 | 402.6 | 746
539 | 332 | 667.8 | 724.4 | 774.1 | 403.5 | 747.1
540 | 333 | 668.3 | 723.2 | 772.9 | 404.4 | 750.1
541 | 334 | 669 | 718.8 | 770.2 | 405.4 | 749.4
542 | 335 | 669.7 | 710.8 | 749.6 | 406.4 | 747.9
543 | 336 | 670.4 | 703.3 | 736.9 | 407.4 | 747.2
544 | 337 | 671.2 | 694.3 | 727 | 408.5 | 745.4
545 | 338 | 672.2 | 689.1 | 714.5 | 409.7 | 744.9
546 | 339 | 672.7 | 680.9 | 703.8 | 410.8 | 742.9
547 | 340 | 672.8 | 676.8 | 693.8 | 412 | 743.1
548 | 341 | 673 | 675.6 | 692.7 | 413.1 | 743
549 | 342 | 673.5 | 675.4 | 685.3 | 414.4 | 743
550 | 343 | 674.1 | 678.2 | 690.6 | 415.6 | 744.8
551 | 344 | 674.8 | 683.7 | 699.8 | 416.8 | 747.1
552 | 345 | 675.5 | 691.4 | 710.7 | 418 | 749.6
553 | 346 | 676.3 | 696.7 | 718.9 | 419.3 | 751.7
554 | 347 | 677.3 | 699.1 | 717.5 | 420.6 | 752.5
555 | 348 | 678.7 | 699.2 | 710.8 | 421.8 | 753.3
556 | 349 | 679.6 | 700.6 | 705 | 423.1 | 754.2
557 | 350 | 680.6 | 701.3 | 696.6 | 424.4 | 755.5
558 | 351 | 681.1 | 700.7 | 690.6 | 425.7 | 756
559 | 352 | 681.4 | 702 | 679.7 | 427.2 | 756
560 | 353 | 682 | 701.4 | 684.9 | 428.7 | 755.6
561 | 354 | 682.4 | 701.2 | 691 | 430.4 | 756.2
562 | 355 | 682.9 | 699.6 | 692.7 | 432.1 | 758.1
563 | 356 | 683.6 | 697.9 | 684.4 | 433.9 | 758
564 | 357 | 684.2 | 694.5 | 669.6 | 435.8 | 755.6
565 | 358 | 684.8 | 687.2 | 659.5 | 437.8 | 754.9
566 | 359 | 685.7 | 684.6 | 663.4 | 440.1 | 755.5
567 | 360 | 686.5 | 675.4 | 655.7 | 442.5 | 754.2
568 | 361 | 687.7 | 669.2 | 643.2 | 445.1 | 751.7
569 | 362 | 688.6 | 668.6 | 646.1 | 447.9 | 750.5
570 | 363 | 689.1 | 668.3 | 665.9 | 450.9 | 750.4
571 | 364 | 690 | 663.7 | 673.9 | 454.2 | 750.8
572 | 365 | 690.9 | 659.6 | 687.5 | 457.5 | 749.1
573 | 366 | 692 | 651.3 | 678.9 | 460.9 | 746.7
574 | 367 | 692.9 | 653.4 | 676.9 | 464.2 | 747.1
575 | 368 | 693.9 | 649.7 | 686.1 | 467.3 | 745.8
576 | 369 | 694.7 | 648 | 701.3 | 470.4 | 746.6
577 | 370 | 695.7 | 650.7 | 721.7 | 473.5 | 747.6
578 | 371 | 697 | 655.3 | 744.5 | 476.5 | 747
579 | 372 | 698.9 | 654.9 | 751.4 | 479.3 | 747.8
580 | 373 | 700.2 | 658.5 | 761.4 | 482.1 | 748.6
581 | 374 | 701 | 667.2 | 775.4 | 484.9 | 750.4
582 | 375 | 701.4 | 673 | 780.9 | 487.6 | 753.9
583 | 376 | 701.6 | 676.5 | 782.1 | 490.2 | 754.6
584 | 377 | 702 | 678.3 | 776.8 | 492.7 | 754.7
585 | 378 | 702.4 | 682.3 | 787 | 495.3 | 756.2
586 | 379 | 703 | 681.2 | 794.1 | 498 | 757.4
587 | 380 | 704 | 681 | 804 | 500.5 | 755.5
588 | 381 | 705.2 | 687.4 | 807.6 | 503.1 | 758.1
589 | 382 | 706.4 | 685.5 | 796.2 | 505.9 | 757.7
590 | 383 | 707.2 | 687.3 | 783.6 | 508.9 | 760.2
591 | 384 | 707.7 | 690.8 | 783.5 | 512.1 | 762.2
592 | 385 | 708 | 690.6 | 774.9 | 515.4 | 763.3
593 | 386 | 708.3 | 692 | 774.7 | 519 | 765
594 | 387 | 709.1 | 693 | 772.7 | 522.8 | 765.9
595 | 388 | 709.8 | 700 | 780.9 | 526.9 | 768.7
596 | 389 | 710.7 | 703.3 | 784.9 | 531.3 | 771.2
597 | 390 | 711.4 | 706.4 | 775.9 | 536.1 | 771.5
598 | 391 | 712.1 | 706.7 | 786.6 | 541.3 | 773.6
599 | 392 | 713.1 | 707.3 | 792.5 | 546.9 | 774.7
600 | 393 | 714.2 | 710.4 | 793.5 | 553 | 775.4
601 | 394 | 715.8 | 714.5 | 794.4 | 559.9 | 777.8
602 | 395 | 717.7 | 716.4 | 798.4 | 567.3 | 780.1
603 | 396 | 719.1 | 716.5 | 805.3 | 574.9 | 782.8
604 | 397 | 720.4 | 717.4 | 804 | 583 | 784.8
605 | 398 | 721.9 | 717.6 | 802.7 | 592 | 785.8
606 | 399 | 722.9 | 716 | 799.3 | 601.7 | 787.6
607 | 400 | 723.9 | 718.5 | 788.4 | 611.4 | 786.4
608 | 401 | 725.2 | 719.9 | 785.7 | 620.8 | 787.3
609 | 402 | 726.8 | 719.3 | 781.3 | 629.6 | 788
610 | 403 | 728 | 717.2 | 763.6 | 637.9 | 787.2
611 | 404 | 728.8 | 715.5 | 759.4 | 646 | 787.4
612 | 405 | 729.5 | 713.1 | 753.7 | 653.6 | 787.9
613 | 406 | 730.3 | 713.3 | 753.2 | 660.3 | 788.8
614 | 407 | 731 | 713.9 | 752.7 | 666.1 | 789.5
615 | 408 | 731.9 | 713.3 | 758.4 | 671.7 | 790.7
616 | 409 | 732.8 | 714 | 768.5 | 676.7 | 792.3
617 | 410 | 734.1 | 717.2 | 776.4 | 681.5 | 794.8
618 | 411 | 735.5 | 718 | 784.8 | 686.3 | 796.7
619 | 412 | 736.9 | 716.5 | 793.6 | 690.6 | 796.8
620 | 413 | 738 | 716 | 791.3 | 694.4 | 796.7
621 | 414 | 739 | 719.7 | 796.5 | 698.2 | 799.2
622 | 415 | 740.1 | 720.2 | 805.4 | 702 | 801
623 | 416 | 741.1 | 721.2 | 796.1 | 705.3 | 800.6
624 | 417 | 741.7 | 719.4 | 791.6 | 708.3 | 801.5
625 | 418 | 742.6 | 717.2 | 784.3 | 711.2 | 801.5
626 | 419 | 743.8 | 717.6 | 790 | 714.3 | 800.3
627 | 420 | 744.9 | 722.2 | 795.7 | 717.4 | 801.3
628 | 421 | 745.9 | 722.4 | 792.1 | 720.2 | 803
629 | 422 | 746.6 | 722.7 | 795.2 | 722.8 | 802.8
630 | 423 | 747.4 | 721.8 | 791.5 | 725.1 | 801.7
631 | 424 | 748.1 | 723.4 | 782.4 | 727.3 | 802.3
632 | 425 | 749 | 724.3 | 775.8 | 729.6 | 803.1
633 | 426 | 750.2 | 723 | 781.5 | 732.2 | 804.9
634 | 427 | 751.1 | 724 | 781.7 | 734.6 | 806.6
635 | 428 | 752.1 | 726.3 | 773.3 | 736.8 | 808.5
636 | 429 | 753.3 | 728.2 | 757.8 | 739.2 | 810.3
637 | 430 | 754.5 | 723.5 | 747.9 | 742 | 809.9
638 | 431 | 755.6 | 722.1 | 741.9 | 745.2 | 811.2
639 | 432 | 756.8 | 723.4 | 752.1 | 748.4 | 811.8
640 | 433 | 758.1 | 727 | 764.9 | 751.2 | 815
641 | 434 | 759.5 | 727.8 | 773.9 | 753.7 | 814.9
642 | 435 | 761 | 723.4 | 781.8 | 755.4 | 814
643 | 436 | 761.9 | 723.4 | 786.4 | 756.8 | 816.7
644 | 437 | 762.8 | 723.5 | 778.3 | 757.8 | 818.3
645 | 438 | 763.6 | 722.2 | 767.4 | 758.9 | 818.8
646 | 439 | 764.2 | 722.7 | 762.7 | 760.2 | 818.6
647 | 440 | 764.6 | 721.8 | 761.3 | 761.2 | 817.3
648 | 441 | 765.1 | 724.1 | 767.3 | 762.1 | 817.5
649 | 442 | 765.8 | 724.8 | 770.6 | 762.9 | 819.4
650 | 443 | 766.6 | 722.4 | 767.5 | 763.7 | 820.6
651 | 444 | 767.3 | 722.4 | 765.4 | 764.7 | 821.5
652 | 445 | 768.1 | 723.8 | 764.3 | 765.9 | 820.2
653 | 446 | 768.8 | 722.6 | 755.6 | 766.8 | 821.9
654 | 447 | 769.8 | 721 | 756.5 | 768 | 822.3
655 | 448 | 770.7 | 720.3 | 759.8 | 769.2 | 822.4
656 | 449 | 771.7 | 719 | 762.1 | 769.8 | 822.2
657 | 450 | 772.8 | 720.2 | 768.4 | 770.5 | 821.5
658 | 451 | 773.6 | 720.4 | 777.8 | 771.4 | 821.5
659 | 452 | 774.3 | 721.4 | 791.5 | 771.8 | 820
660 | 453 | 775.2 | 720.8 | 799 | 772.1 | 818.5
661 | 454 | 776 | 722.6 | 803.3 | 772.3 | 819.8
662 | 455 | 776.7 | 722.6 | 806.5 | 772.2 | 820.5
663 | 456 | 777.7 | 721.6 | 802.5 | 772 | 815.5
664 | 457 | 778.7 | 718.2 | 801 | 771.9 | 812.1
665 | 458 | 779.4 | 718.1 | 806 | 771.9 | 812.9
666 | 459 | 780.8 | 721.2 | 812.2 | 772.1 | 813.8
667 | 460 | 782.4 | 717.4 | 814.3 | 772.4 | 812.6
668 | 461 | 783.8 | 717.1 | 818.3 | 772.9 | 810.2
669 | 462 | 784.7 | 714.1 | 820.1 | 773.2 | 807.2
670 | 463 | 785.1 | 715 | 820 | 773.6 | 805.8
671 | 464 | 785.3 | 716.9 | 822.1 | 773.7 | 803.6
672 | 465 | 785.4 | 720 | 825.3 | 773.4 | 802.6
673 | 466 | 786 | 721.6 | 826.1 | 772.8 | 806.2
674 | 467 | 786.3 | 722.1 | 825.7 | 772.1 | 804.2
675 | 468 | 786.7 | 725.4 | 820.1 | 771.6 | 806.4
676 | 469 | 787 | 724 | 806.8 | 771.2 | 809.6
677 | 470 | 787.7 | 724 | 802.4 | 771.5 | 810.5
678 | 471 | 788.1 | 723.8 | 800.3 | 772 | 812.1
679 | 472 | 788.5 | 725.8 | 803.6 | 772.5 | 812
680 | 473 | 789 | 727.6 | 806.4 | 772.9 | 813.4
681 | 474 | 789.6 | 724.8 | 810.8 | 773 | 813.8
682 | 475 | 789.9 | 726.2 | 811.8 | 773.1 | 814.7
683 | 476 | 790.5 | 728.6 | 817.3 | 773.4 | 817.1
684 | 477 | 791 | 729.4 | 814.2 | 773.5 | 819.1
685 | 478 | 791.4 | 728.7 | 809.4 | 773.8 | 819.5
686 | 479 | 791.5 | 731 | 811.8 | 774.1 | 821.8
687 | 480 | 791.9 | 731.3 | 810.9 | 774.4 | 824
688 | 481 | 792.2 | 729.4 | 802.3 | 774.4 | 823.7
689 | 482 | 792.5 | 727.3 | 790.6 | 774.4 | 822.9
690 | 483 | 792.9 | 725.4 | 782.1 | 774.9 | 823.3
691 | 484 | 793.5 | 726.7 | 774.7 | 775.7 | 824.5
692 | 485 | 794 | 724.3 | 768.7 | 776.5 | 825
693 | 486 | 794.5 | 724.1 | 771.4 | 777.1 | 825.8
694 | 487 | 795.2 | 725.1 | 776 | 777.9 | 827.6
695 | 488 | 795.9 | 724.8 | 776.2 | 778.6 | 828
696 | 489 | 796.5 | 726.6 | 783.1 | 779.3 | 828.4
697 | 490 | 797.3 | 724.4 | 785.6 | 779.9 | 828.3
698 | 491 | 798.1 | 722.9 | 784.3 | 780.6 | 825.9
699 | 492 | 799 | 719.8 | 786.8 | 781.4 | 823.6
700 | 493 | 799.7 | 717.8 | 795.2 | 782.1 | 822.1
701 | 494 | 800.2 | 717.6 | 798.3 | 782.6 | 822.6
702 | 495 | 800.6 | 718.9 | 795.9 | 783.2 | 823.1
703 | 496 | 800.9 | 721.9 | 794.4 | 783.6 | 825.5
704 | 497 | 801.4 | 723.4 | 795.9 | 784.1 | 827
705 | 498 | 801.9 | 721.6 | 797.1 | 785 | 826.4
706 | 499 | 802 | 723.8 | 805.2 | 785.7 | 826.2
707 | 500 | 802.3 | 727.7 | 811.1 | 786.1 | 827.2
708 | 501 | 802.5 | 729.5 | 812.4 | 786.1 | 827.9
709 | 502 | 802.6 | 729.4 | 813.1 | 786 | 826.3
710 | 503 | 802.7 | 729.2 | 809.6 | 785.7 | 825.7
711 | 504 | 803.1 | 728.1 | 804.3 | 785.3 | 825.7
712 | 505 | 803.9 | 723.1 | 806.9 | 785.7 | 824
713 | 506 | 804.1 | 721.5 | 809.1 | 786 | 820.6
714 | 507 | 804.1 | 718.7 | 806.9 | 785.7 | 819
715 | 508 | 804.1 | 717 | 810.6 | 785.1 | 817.1
716 | 509 | 804.2 | 714.8 | 812.5 | 784.8 | 815.7
717 | 510 | 804.3 | 715.9 | 813.9 | 784.6 | 816.1
718 | 511 | 804.2 | 717.4 | 814.6 | 784.1 | 819.6
719 | 512 | 804.6 | 716 | 804.4 | 783.4 | 821.2
720 | 513 | 805.1 | 716.4 | 799.8 | 783.1 | 822.7
721 | 514 | 805.4 | 714.8 | 794.8 | 783.4 | 822.5
722 | 515 | 805.4 | 716.8 | 796.9 | 784 | 822.8
723 | 516 | 805.6 | 716.7 | 796.5 | 784.1 | 823.6
724 | 517 | 806 | 718 | 796.9 | 784.7 | 823.5
725 | 518 | 806.5 | 719.5 | 793.5 | 785.4 | 823.6
726 | 519 | 807.2 | 720.7 | 796 | 786.1 | 822.9
727 | 520 | 807.9 | 722 | 796.6 | 786.9 | 824.6
728 | 521 | 808.3 | 722.1 | 799.6 | 787.9 | 823.3
729 | 522 | 808.5 | 723.8 | 804.5 | 788.7 | 824
730 | 523 | 808.9 | 719.2 | 802.7 | 788.6 | 822.5
731 | 524 | 809.7 | 714.5 | 794.3 | 788.9 | 818.2
732 | 525 | 810.6 | 708.9 | 793.8 | 789.7 | 814.5
733 | 526 | 811.2 | 705.2 | 797.9 | 790.3 | 810.5
734 | 527 | 811.7 | 704.3 | 803.4 | 790.9 | 807.9
735 | 528 | 811.7 | 703.6 | 802.6 | 790.9 | 805.4
736 | 529 | 811.8 | 703.4 | 802.4 | 790.8 | 804.3
737 | 530 | 811.7 | 705.3 | 804.7 | 790.5 | 803.2
738 | 531 | 811.8 | 703.3 | 806.5 | 789.9 | 801.2
739 | 532 | 812.2 | 705.9 | 810.1 | 789.7 | 801
740 | 533 | 812.6 | 707.7 | 813.1 | 789.5 | 799.6
741 | 534 | 813.3 | 707.7 | 812 | 789.4 | 799
742 | 535 | 814.1 | 710.5 | 813.8 | 789.7 | 797.8
743 | 536 | 814.2 | 713 | 814.8 | 790 | 798
744 | 537 | 814.1 | 714.5 | 813.6 | 789.9 | 798.3
745 | 538 | 814.5 | 715.3 | 814.7 | 789.6 | 798.1
746 | 539 | 814.6 | 716.4 | 812.4 | 789.5 | 795
747 | 540 | 814.7 | 717.9 | 813.1 | 789.4 | 792.8
748 | 541 | 815 | 717.6 | 814.4 | 789.5 | 791.9
749 | 542 | 815.1 | 718.5 | 815.3 | 789.6 | 791.7
750 | 543 | 814.9 | 717.6 | 816.3 | 789.2 | 792.2
751 | 544 | 814.8 | 717.3 | 814.4 | 788.7 | 792.1
752 | 545 | 814.6 | 719.1 | 816.4 | 788.5 | 791.3
753 | 546 | 814.6 | 718.7 | 813.9 | 788.1 | 791.3
754 | 547 | 814.8 | 713.6 | 808.3 | 787.9 | 789.4
755 | 548 | 815.2 | 708.3 | 803 | 788.2 | 786.3
756 | 549 | 816 | 709.3 | 804.9 | 788.7 | 785.2
757 | 550 | 816.2 | 708.4 | 804.7 | 789.2 | 783.1
758 | 551 | 816.2 | 708.3 | 801.2 | 789.5 | 781.5
759 | 552 | 816.1 | 707.9 | 801.9 | 789.8 | 779.8
760 | 553 | 815.6 | 707.1 | 803.7 | 789.6 | 778.3
761 | 554 | 815.1 | 708.6 | 805 | 789.3 | 778
762 | 555 | 814.9 | 709 | 805.4 | 788.6 | 778
763 | 556 | 815.3 | 708.5 | 805.2 | 788.2 | 776.5
764 | 557 | 815.3 | 707.2 | 802.8 | 788 | 774.7
765 | 558 | 815 | 708.5 | 805.1 | 788.1 | 772
766 | 559 | 814.9 | 707.3 | 806 | 787.8 | 770.6
767 | 560 | 815.3 | 704.8 | 805.5 | 788 | 769.5
768 | 561 | 815.4 | 703.2 | 806.2 | 788.6 | 766.9
769 | 562 | 815 | 704.6 | 805.3 | 788.9 | 765.5
770 | 563 | 814.3 | 707.1 | 804.2 | 788.6 | 765.6
771 | 564 | 813.8 | 709.4 | 806.3 | 788.2 | 766.1
772 | 565 | 813.2 | 711.4 | 810.1 | 787.5 | 765.7
773 | 566 | 812.9 | 712.3 | 811.8 | 786.8 | 764
774 | 567 | 812.8 | 715.2 | 813 | 786.6 | 763.1
775 | 568 | 812.9 | 712.1 | 813.9 | 786.6 | 761.3
776 | 569 | 812.4 | 711.1 | 811.3 | 786.8 | 759.8
777 | 570 | 811.7 | 708.7 | 808.1 | 786.4 | 759.7
778 | 571 | 811.4 | 708.9 | 807.5 | 786.1 | 758.9
779 | 572 | 811.3 | 707 | 802.3 | 785.9 | 758.6
780 | 573 | 811.3 | 706.5 | 802.9 | 786.4 | 759.7
781 | 574 | 811.4 | 703.9 | 803.6 | 787 | 758.5
782 | 575 | 811.3 | 702.5 | 804.7 | 787.7 | 757.2
783 | 576 | 811.5 | 701.4 | 805.5 | 788.2 | 755.4
784 | 577 | 811.7 | 705.2 | 807.5 | 788.8 | 754.8
785 | 578 | 811.4 | 708.6 | 809.2 | 789.1 | 755.6
786 | 579 | 810.8 | 709.3 | 806.6 | 788.6 | 755.8
787 | 580 | 810.5 | 710.5 | 804.8 | 788.3 | 757.6
788 | 581 | 810.1 | 711.7 | 805.2 | 788.1 | 758.5
789 | 582 | 809.5 | 713.1 | 802.1 | 787.4 | 761.5
790 | 583 | 809 | 716.8 | 800.9 | 787 | 765.3
791 | 584 | 808.8 | 718.8 | 802.7 | 786.8 | 767.1
792 | 585 | 808.6 | 715.3 | 801.6 | 786.9 | 765.5
793 | 586 | 808.3 | 717.5 | 803.5 | 787.6 | 764.6
794 | 587 | 807.7 | 720 | 803.3 | 787.6 | 766.9
795 | 588 | 807.4 | 721.1 | 798.1 | 786.9 | 769.3
796 | 589 | 807 | 721.4 | 799.9 | 786.7 | 771.2
797 | 590 | 806.6 | 723.4 | 803.2 | 786.5 | 771.9
798 | 591 | 806 | 726.3 | 805.2 | 786.2 | 771.7
799 | 592 | 805.5 | 725.7 | 807.1 | 785.7 | 772.2
800 | 593 | 804.9 | 727 | 807.3 | 785.6 | 772.8
801 | 594 | 804.1 | 724.7 | 808.2 | 784.9 | 772.7
802 | 595 | 804.3 | 723.8 | 809.5 | 784.8 | 770.3
803 | 596 | 804.6 | 722.2 | 809 | 785.4 | 768.1
804 | 597 | 804 | 726.4 | 808.3 | 785.8 | 770.4
805 | 598 | 803.4 | 728.1 | 801.7 | 785.3 | 772.1
806 | 599 | 802.8 | 729.8 | 800.7 | 785 | 773.6
807 | 600 | 802.2 | 730.8 | 803.1 | 784.8 | 774.9
808 | 601 | 801.7 | 734.3 | 803.3 | 784.9 | 775.7
809 | 602 | 801.3 | 735.6 | 803.6 | 784.7 | 778
810 | 603 | 801.1 | 733.8 | 803.9 | 784.4 | 778
811 | 604 | 800.9 | 733.9 | 802.3 | 784.3 | 780.5
812 | 605 | 800.5 | 735.2 | 802.3 | 784.6 | 783.2
813 | 606 | 800.3 | 733.1 | 802.3 | 784.6 | 783.8
814 | 607 | 800.2 | 732.9 | 803.5 | 785 | 785.2
815 | 608 | 799.9 | 733 | 801.7 | 785 | 786.8
816 | 609 | 799.9 | 732.2 | 801 | 785.3 | 788.6
817 | 610 | 800.2 | 732.6 | 800.2 | 786.1 | 788.5
818 | 611 | 800.6 | 732.7 | 798.8 | 787 | 789
819 | 612 | 800.4 | 729.3 | 793 | 787.2 | 791.2
820 | 613 | 800.3 | 726.7 | 792 | 787.5 | 790.2
821 | 614 | 800.3 | 721.1 | 785.6 | 787.7 | 788.6
822 | 615 | 800.5 | 715.1 | 777.5 | 788.3 | 787.6
823 | 616 | 800.7 | 707 | 773.4 | 789.3 | 785.5
824 | 617 | 800.5 | 703.4 | 777.3 | 790.7 | 784.2
825 | 618 | 800.6 | 699.8 | 782.8 | 791.8 | 780.7
826 | 619 | 800.5 | 696.8 | 784.7 | 792.9 | 776.9
827 | 620 | 800.2 | 698.3 | 786.2 | 793.9 | 775.1
828 | 621 | 799.9 | 700 | 787.3 | 794.4 | 774.2
829 | 622 | 799.4 | 699.8 | 786 | 794.4 | 774
830 | 623 | 799.1 | 698.4 | 787.8 | 794.4 | 773.6
831 | 624 | 798.7 | 696.1 | 788 | 794.7 | 773.2
832 | 625 | 798.4 | 694.8 | 785.3 | 794.7 | 772.6
833 | 626 | 798.2 | 693.9 | 782.9 | 794.9 | 771.8
834 | 627 | 797.8 | 694.1 | 787.1 | 795.4 | 769.7
835 | 628 | 797.3 | 693.8 | 791.8 | 795.5 | 767.8
836 | 629 | 796.7 | 693.8 | 794.3 | 795.4 | 766.6
837 | 630 | 796.4 | 697.9 | 796.6 | 795.5 | 765.4
838 | 631 | 795.8 | 703.4 | 797.5 | 795.2 | 765.5
839 | 632 | 795.3 | 704.7 | 799.5 | 794.3 | 765.6
840 | 633 | 794.8 | 708.4 | 800.4 | 793.6 | 765.5
841 | 634 | 794.2 | 712.3 | 801.9 | 792.7 | 768.3
842 | 635 | 793.8 | 713.2 | 802.5 | 791.4 | 768.8
843 | 636 | 793.4 | 714.9 | 802.9 | 790.5 | 769.9
844 | 637 | 793 | 714.3 | 803.1 | 789.4 | 768.9
845 | 638 | 792.9 | 714.9 | 803 | 788.4 | 770.4
846 | 639 | 792.6 | 719 | 804.9 | 787.9 | 771.7
847 | 640 | 792.3 | 719.4 | 806.5 | 787.4 | 768.9
848 | 641 | 792.2 | 721.9 | 806.6 | 787.2 | 769
849 | 642 | 791.9 | 723.4 | 806.9 | 786.8 | 770
850 | 643 | 791.4 | 724.7 | 806.7 | 786.5 | 769
851 | 644 | 791.2 | 725.5 | 808.8 | 786.3 | 768
852 | 645 | 791.2 | 725.6 | 809.7 | 786.4 | 766.9
853 | 646 | 791.3 | 726.4 | 807.8 | 787 | 767.4
854 | 647 | 791.5 | 726.6 | 806.3 | 787.5 | 769.1
855 | 648 | 791.4 | 727 | 807.6 | 788.4 | 767.7
856 | 649 | 791.1 | 729.5 | 807.1 | 788.7 | 768.4
857 | 650 | 790.5 | 730.9 | 805.5 | 787.9 | 771.1
858 | 651 | 790.2 | 732.9 | 803 | 787 | 773.7
859 | 652 | 790.1 | 734.6 | 801.4 | 786.5 | 776.1
860 | 653 | 790.1 | 735.6 | 801.3 | 786 | 779.4
861 | 654 | 790 | 735.4 | 796.8 | 785.3 | 782.5
862 | 655 | 790 | 734 | 794.7 | 784.9 | 783.1
863 | 656 | 790.1 | 732.8 | 796.7 | 785 | 782.2
864 | 657 | 790 | 731.5 | 799.4 | 785.3 | 779.9
865 | 658 | 789.8 | 732.5 | 800.7 | 785.3 | 781
866 | 659 | 789.6 | 730.1 | 799.1 | 784.8 | 781.7
867 | 660 | 789.7 | 730.2 | 799.1 | 784.7 | 783.6
868 | 661 | 790 | 728.1 | 797.2 | 784.9 | 785
869 | 662 | 790.4 | 727.9 | 796.2 | 785.5 | 786.9
870 | 663 | 790.5 | 728.8 | 798.3 | 786.1 | 787.4
871 | 664 | 790.4 | 730.2 | 800.8 | 786.6 | 787.9
872 | 665 | 790.7 | 729.8 | 800.7 | 786.7 | 789.3
873 | 666 | 790.9 | 729.6 | 798.1 | 786.5 | 791.1
874 | 667 | 791.2 | 727 | 795.6 | 786.9 | 791.3
875 | 668 | 791.6 | 727.2 | 795.9 | 787.8 | 792.5
876 | 669 | 791.6 | 726.6 | 797.8 | 788.7 | 791.2
877 | 670 | 791.9 | 722 | 794 | 789.2 | 789
878 | 671 | 792 | 712.2 | 787.4 | 789.7 | 785.8
879 | 672 | 792.1 | 704 | 785.8 | 790.3 | 782
880 | 673 | 792.1 | 700.5 | 788.2 | 791.1 | 779.5
881 | 674 | 791.8 | 701.6 | 792 | 791.6 | 777.4
882 | 675 | 791.7 | 705.8 | 794.4 | 792.2 | 776.1
883 | 676 | 791.3 | 710.5 | 796.5 | 792.2 | 776
884 | 677 | 790.8 | 713.8 | 797.2 | 791.4 | 780
885 | 678 | 790.3 | 716.9 | 799.6 | 790.7 | 781
886 | 679 | 789.8 | 719.7 | 799.9 | 789.5 | 782.3
887 | 680 | 789.7 | 722.3 | 799.2 | 788.6 | 782.6
888 | 681 | 790.1 | 718.2 | 796.4 | 788.3 | 780
889 | 682 | 790.3 | 714.4 | 796.8 | 788.6 | 778.2
890 | 683 | 790.5 | 711.2 | 797 | 789.3 | 775.6
891 | 684 | 790.5 | 711.8 | 798 | 790 | 775.1
892 | 685 | 790.4 | 713.6 | 797.1 | 790.5 | 775.7
893 | 686 | 790.4 | 713.6 | 798.7 | 790.6 | 776
894 | 687 | 790.5 | 713.3 | 798.5 | 791 | 771.9
895 | 688 | 790.3 | 714 | 799.8 | 791.4 | 770.4
896 | 689 | 790.3 | 713.5 | 800.9 | 791.4 | 769.4
897 | 690 | 790.9 | 717.3 | 803.6 | 792.1 | 769.2
898 | 691 | 791 | 717.5 | 804.7 | 792.6 | 766.9
899 | 692 | 790.9 | 717.3 | 806.6 | 792.4 | 764.5
900 | 693 | 790.9 | 714.9 | 807.2 | 791.7 | 762.2
901 | 694 | 791 | 708.8 | 804.3 | 791.2 | 758
902 | 695 | 790.9 | 702.2 | 797.7 | 790.9 | 754.9
903 | 696 | 790.9 | 698.2 | 796 | 791.3 | 752.9
904 | 697 | 790.8 | 697.2 | 797 | 791.8 | 751
905 | 698 | 790.5 | 700.8 | 799.1 | 792.1 | 749.4
906 | 699 | 790.1 | 705.2 | 801.9 | 792 | 749.4
907 | 700 | 789.9 | 705.7 | 802.2 | 792 | 748.3
908 | 701 | 789.7 | 704.8 | 802.5 | 792 | 748.5
909 | 702 | 789.8 | 699.4 | 798.4 | 791.7 | 745.6
910 | 703 | 790.2 | 694.5 | 793.6 | 791.7 | 743.8
911 | 704 | 790.1 | 690.8 | 793.6 | 792.2 | 740.8
912 | 705 | 790.4 | 689.2 | 793.7 | 793 | 738.4
913 | 706 | 790.3 | 687.8 | 796.5 | 794.5 | 735.4
914 | 707 | 790.1 | 690.4 | 800.3 | 795.2 | 733.9
915 | 708 | 790.2 | 694.7 | 801.4 | 795.4 | 733.1
916 | 709 | 790.2 | 695.8 | 802.5 | 795.3 | 732
917 | 710 | 790.4 | 700.3 | 804 | 795.2 | 730.5
918 | 711 | 790.1 | 704.6 | 805.6 | 794.7 | 729
919 | 712 | 789.5 | 710 | 807.3 | 793.7 | 729.5
920 | 713 | 789.3 | 713.1 | 806 | 792.3 | 732.6
921 | 714 | 789.4 | 716.8 | 804.6 | 791 | 736.3
922 | 715 | 789.5 | 719.7 | 807.1 | 790.1 | 739.3
923 | 716 | 789.5 | 722.3 | 808.1 | 789.6 | 740.4
924 | 717 | 789.5 | 721.2 | 809.2 | 788.7 | 738.8
925 | 718 | 790 | 719.7 | 810 | 788.7 | 736.5
926 | 719 | 790 | 719.3 | 809.8 | 788.6 | 736.6
927 | 720 | 789.9 | 722.3 | 810.3 | 788.1 | 738.2
928 | 721 | 789.8 | 726.9 | 809.7 | 787.5 | 740.6
929 | 722 | 789.5 | 727.7 | 809.1 | 786.9 | 739.3
930 | 723 | 789.9 | 726.4 | 810.3 | 787.2 | 737.1
931 | 724 | 790.1 | 726.3 | 810.1 | 787.8 | 735.5
932 | 725 | 790.3 | 726.1 | 810.2 | 788.4 | 734.6
933 | 726 | 790.2 | 728.7 | 810.6 | 788.7 | 736.7
934 | 727 | 790.2 | 731.6 | 810.8 | 788.8 | 738
935 | 728 | 790.2 | 729.2 | 810.7 | 788.3 | 737.6
936 | 729 | 790.6 | 727.1 | 808.5 | 788.1 | 738.8
937 | 730 | 790.8 | 728.7 | 808.1 | 787.9 | 741.5
938 | 731 | 790.6 | 730.6 | 807.4 | 787.4 | 743.8
939 | 732 | 790.5 | 733 | 807.9 | 786.9 | 746.2
940 | 733 | 790.6 | 735.6 | 808.8 | 786.6 | 747.2
941 | 734 | 791 | 731.8 | 808.7 | 786.6 | 746.4
942 | 735 | 791.3 | 729 | 808.2 | 786.6 | 745.3
943 | 736 | 791.5 | 731.5 | 809 | 786.7 | 746.8
944 | 737 | 791.3 | 736.1 | 808.2 | 787.1 | 746.3
945 | 738 | 791 | 739.1 | 808.1 | 786.6 | 748.8
946 | 739 | 790.9 | 737.6 | 809.1 | 785.8 | 749.2
947 | 740 | 791.1 | 734.9 | 809.9 | 785.7 | 747.5
948 | 741 | 791.4 | 734.5 | 809.2 | 785.8 | 746.1
949 | 742 | 791.8 | 735.7 | 809.8 | 786.4 | 745.3
950 | 743 | 791.9 | 735.7 | 808.9 | 786.6 | 743.6
951 | 744 | 792.1 | 735.7 | 811.7 | 786.6 | 741.3
952 | 745 | 792.6 | 735.1 | 811.1 | 787.2 | 740.2
953 | 746 | 793.1 | 733.4 | 809.4 | 788.2 | 737.8
954 | 747 | 793.2 | 735.3 | 811.1 | 789.3 | 737.4
955 | 748 | 793.3 | 736.6 | 811.8 | 789.8 | 736.8
956 | 749 | 793.5 | 734.8 | 812.5 | 790.2 | 735.4
957 | 750 | 793.4 | 735.8 | 812.4 | 790 | 735.4
958 | 751 | 793.2 | 738.3 | 812 | 789.2 | 737.9
959 | 752 | 792.9 | 739.8 | 812.2 | 788.3 | 741.3
960 | 753 | 792.8 | 742.8 | 812.3 | 787.4 | 745.1
961 | 754 | 792.7 | 746.3 | 810.7 | 786.8 | 749.3
962 | 755 | 792.6 | 747.6 | 803.6 | 786 | 750.3
963 | 756 | 792.5 | 749.2 | 804.5 | 785.5 | 752.4
964 | 757 | 792.4 | 748.3 | 804.4 | 784.9 | 754.7
965 | 758 | 792.6 | 747.5 | 803.3 | 784.5 | 753.7
966 | 759 | 792.6 | 747.7 | 805.2 | 784.4 | 755.9
967 | 760 | 792.5 | 748.4 | 806.6 | 784 | 758.1
968 | 761 | 792.5 | 748.4 | 808.2 | 783.8 | 757.8
969 | 762 | 792.4 | 745.7 | 809.6 | 783.4 | 756.7
970 | 763 | 792.3 | 744.8 | 811.1 | 783.1 | 754
971 | 764 | 792.1 | 745.7 | 810.3 | 782.5 | 755
972 | 765 | 791.8 | 747.2 | 811.5 | 782.2 | 756.7
973 | 766 | 791.6 | 747 | 811.4 | 781.8 | 760
974 | 767 | 791.4 | 747.2 | 810.9 | 781.3 | 761
975 | 768 | 791.3 | 747.9 | 810.6 | 780.8 | 763.1
976 | 769 | 791.1 | 748.5 | 809.8 | 780.6 | 765.2
977 | 770 | 791 | 747.8 | 809.9 | 780.1 | 764.2
978 | 771 | 790.9 | 747.4 | 810.1 | 779.7 | 764.5
979 | 772 | 790.8 | 747.6 | 810 | 779.5 | 763.8
980 | 773 | 790.9 | 744.5 | 811.6 | 780 | 760.9
981 | 774 | 791 | 740.6 | 813.3 | 780.5 | 756.9
982 | 775 | 791 | 738.8 | 813.7 | 781.3 | 754.7
983 | 776 | 791.2 | 736.7 | 813.8 | 782.2 | 753.2
984 | 777 | 791.3 | 737.6 | 812.3 | 782.7 | 751.7
985 | 778 | 791.1 | 741.2 | 813.6 | 783 | 752.2
986 | 779 | 791.1 | 743.1 | 813.3 | 782.9 | 753
987 | 780 | 790.9 | 745.6 | 813.5 | 782.7 | 754.1
988 | 781 | 790.6 | 746.1 | 814.1 | 782.1 | 754.9
989 | 782 | 790.6 | 748.5 | 814.8 | 782.4 | 755
990 | 783 | 790.7 | 750 | 816.3 | 782.6 | 756.1
991 | 784 | 790.6 | 750.5 | 815.4 | 782.5 | 757.2
992 | 785 | 790.5 | 750.9 | 815.3 | 782 | 759.5
993 | 786 | 790.5 | 752.7 | 816.3 | 782 | 760.3
994 | 787 | 790.5 | 753.2 | 817.6 | 782.2 | 760.7
995 | 788 | 790.4 | 755.3 | 816.7 | 782.5 | 760.2
996 | 789 | 790.1 | 756.9 | 816.6 | 782.2 | 763.1
997 | 790 | 789.9 | 758.8 | 815.2 | 781.9 | 766.6
998 | 791 | 790 | 758.9 | 815.4 | 782.2 | 768.3
999 | 792 | 790.1 | 759.2 | 815.9 | 782.4 | 767.8
1000 | 793 | 790.1 | 758.6 | 817.7 | 782.5 | 768.5
1001 | 794 | 790.4 | 756.6 | 818.1 | 782.8 | 768.7
1002 | 795 | 790.5 | 754.7 | 818 | 782.9 | 770.1
1003 | 796 | 790.7 | 750.8 | 817.4 | 783.2 | 770.6
1004 | 797 | 791 | 744.7 | 816.4 | 783.9 | 769.3
1005 | 798 | 791.2 | 744.1 | 814.1 | 784.6 | 771.2
1006 | 799 | 791.4 | 745.6 | 812.6 | 785 | 773.6
1007 | 800 | 791.6 | 746.3 | 814.6 | 785.2 | 775.1
1008 | 801 | 791.6 | 747.6 | 816.8 | 785.2 | 775.2
1009 | 802 | 791.7 | 749 | 819.2 | 785.4 | 775.2
1010 | 803 | 791.8 | 748.9 | 819.5 | 785.6 | 776
1011 | 804 | 791.8 | 749.5 | 819.3 | 786.4 | 774.1
1012 | 805 | 791.6 | 749.4 | 820.1 | 787.1 | 771.4
1013 | 806 | 791.4 | 751.3 | 821.4 | 787.3 | 771.2
1014 | 807 | 791.2 | 751.5 | 823.3 | 786.7 | 772.6
1015 | 808 | 791 | 750.3 | 822.6 | 786.2 | 772.8
1016 | 809 | 790.9 | 750.3 | 823.3 | 785.9 | 772.6
1017 | 810 | 791 | 752.1 | 822.8 | 786 | 774.8
1018 | 811 | 791 | 751.3 | 823.6 | 786.2 | 774.1
1019 | 812 | 791 | 751.9 | 823.9 | 786.5 | 774.6
1020 | 813 | 791.4 | 749.7 | 824 | 787 | 774.4
1021 | 814 | 791.8 | 746.3 | 823.5 | 788.1 | 772.1
1022 | 815 | 791.9 | 740.6 | 819.2 | 789.3 | 771.5
1023 | 816 | 791.9 | 740 | 820.1 | 790 | 773
1024 | 817 | 791.8 | 739.8 | 820.9 | 790.1 | 771.6
1025 | 818 | 791.6 | 739.2 | 820.3 | 789.6 | 770.7
1026 | 819 | 791.3 | 740.3 | 820.7 | 789.3 | 771.9
1027 | 820 | 791.4 | 740.8 | 821.4 | 788.9 | 772.4
1028 | 821 | 791.2 | 742.8 | 821.8 | 788.8 | 773.4
1029 | 822 | 791.2 | 744.6 | 821.6 | 788.5 | 775.9
1030 | 823 | 791.2 | 746 | 821.7 | 788.5 | 775.9
1031 | 824 | 791.1 | 747.7 | 822.7 | 788.4 | 777
1032 | 825 | 791.1 | 748.4 | 823.5 | 788.7 | 775.3
1033 | 826 | 791.1 | 745.6 | 822.9 | 789.3 | 773.6
1034 | 827 | 791.2 | 739.1 | 819.1 | 789.8 | 771.2
1035 | 828 | 791.4 | 735.2 | 815.6 | 790.2 | 771.2
1036 | 829 | 791.4 | 732.7 | 813 | 790.9 | 772.7
1037 | 830 | 791.3 | 734.1 | 814.1 | 791 | 774.3
1038 | 831 | 791.3 | 728.5 | 811.2 | 790.6 | 773.2
1039 | 832 | 791.2 | 728.6 | 812.4 | 790.5 | 773.9
1040 | 833 | 791.1 | 728.3 | 814.1 | 790.4 | 774.5
1041 | 834 | 790.9 | 730.2 | 814.8 | 790 | 775.4
1042 | 835 | 790.7 | 730.1 | 814.9 | 789.8 | 776.2
1043 | 836 | 790.3 | 732 | 816.7 | 789.6 | 776.2
1044 | 837 | 790.2 | 731 | 817.9 | 789.5 | 773.9
1045 | 838 | 790.2 | 723.9 | 813.1 | 790.4 | 769
1046 | 839 | 790.1 | 717.3 | 812 | 791.9 | 765.7
1047 | 840 | 789.7 | 717.2 | 814.9 | 792.6 | 765.2
1048 | 841 | 789.4 | 718.5 | 814.1 | 792.4 | 765.4
1049 | 842 | 789.3 | 715.1 | 812.3 | 793.1 | 763.3
1050 | 843 | 788.9 | 713.4 | 813.3 | 793.6 | 761
1051 | 844 | 788.6 | 713.4 | 813.7 | 794.2 | 759.4
1052 | 845 | 788.2 | 718.4 | 816 | 794.5 | 760.9
1053 | 846 | 787.9 | 717.2 | 814.1 | 794.3 | 760.8
1054 | 847 | 787.7 | 713.9 | 809.1 | 794.7 | 760.8
1055 | 848 | 787.5 | 708 | 800.6 | 795.4 | 759.2
1056 | 849 | 787.5 | 700.2 | 790.4 | 795.9 | 755.5
1057 | 850 | 787.1 | 690 | 779.5 | 796.4 | 750.8
1058 | 851 | 786.7 | 680.8 | 772.9 | 796.8 | 745.5
1059 | 852 | 786.3 | 676.7 | 775.5 | 796.7 | 743.7
1060 | 853 | 785.4 | 677.9 | 781.1 | 795.8 | 744.4
1061 | 854 | 784.6 | 677.3 | 783.9 | 794.8 | 742.1
1062 | 855 | 784 | 677.7 | 788.5 | 794.4 | 738.3
1063 | 856 | 783.4 | 680.8 | 793.7 | 794.5 | 736.5
1064 | 857 | 782.6 | 687.7 | 800.9 | 795.2 | 734.8
1065 | 858 | 781.8 | 698.4 | 807.5 | 795.5 | 736.9
1066 | 859 | 781.4 | 698 | 804.2 | 795.4 | 734.9
1067 | 860 | 781.2 | 695.1 | 804.6 | 795.7 | 730.9
1068 | 861 | 780.9 | 696.5 | 806.1 | 796.2 | 730.7
1069 | 862 | 780.7 | 700.2 | 810.1 | 796.8 | 730.3
1070 | 863 | 780.2 | 707.9 | 815.2 | 797.5 | 731.1
1071 | 864 | 779.7 | 716 | 818.4 | 797.5 | 731.2
1072 | 865 | 779.5 | 719.2 | 820.8 | 797.1 | 731.8
1073 | 866 | 779.4 | 722.8 | 821.7 | 796.9 | 734
1074 | 867 | 779.1 | 727.7 | 823.6 | 796.7 | 736.9
1075 | 868 | 778.8 | 730.6 | 825.5 | 795.8 | 737.5
1076 | 869 | 778.8 | 732.8 | 824.9 | 794.5 | 740.1
1077 | 870 | 778.8 | 734.2 | 824.7 | 793.6 | 743.4
1078 | 871 | 779 | 735.4 | 827.5 | 793.9 | 743
1079 | 872 | 779 | 736.7 | 829.8 | 794.5 | 742.5
1080 | 873 | 779.1 | 738.4 | 830.6 | 794.4 | 743.6
1081 | 874 | 779 | 741.4 | 830.4 | 793.8 | 747.4
1082 | 875 | 779.3 | 740.7 | 829.6 | 793.2 | 748.8
1083 | 876 | 779.4 | 740.3 | 830.9 | 793.6 | 750.1
1084 | 877 | 779.5 | 742.9 | 831.8 | 793.9 | 752.4
1085 | 878 | 779.7 | 743 | 830.6 | 793.8 | 754.8
1086 | 879 | 779.9 | 738.8 | 820.1 | 794.1 | 757.4
1087 | 880 | 780.1 | 735.7 | 811.3 | 795.4 | 759.1
1088 | 881 | 780.3 | 734.4 | 806.3 | 796.4 | 761.5
1089 | 882 | 780.5 | 732.4 | 807.1 | 797.1 | 762.5
1090 | 883 | 780.7 | 725.7 | 803.9 | 798 | 761.1
1091 | 884 | 780.6 | 719.8 | 804.8 | 799.6 | 759.6
1092 | 885 | 780.3 | 723.1 | 813.1 | 799.7 | 760.5
1093 | 886 | 780.3 | 726.6 | 818 | 799.1 | 761
1094 | 887 | 780.3 | 729.1 | 822.3 | 798.9 | 758.9
1095 | 888 | 780.2 | 730.7 | 822.4 | 798.7 | 760.1
1096 | 889 | 780.1 | 733.2 | 824.3 | 798.3 | 762.3
1097 | 890 | 780.1 | 736.4 | 828.8 | 798.7 | 760.3
1098 | 891 | 780.3 | 737.5 | 830.5 | 799.9 | 760.6
1099 | 892 | 780.5 | 736.7 | 830.2 | 801 | 761.1
1100 | 893 | 780.6 | 735.2 | 832 | 801.2 | 759.1
1101 | 894 | 780.4 | 736.7 | 834.2 | 800.7 | 757.9
1102 | 895 | 780.3 | 736.1 | 835.8 | 799.9 | 755.1
1103 | 896 | 780.4 | 733.9 | 835.5 | 800 | 753.3
1104 | 897 | 780.4 | 732.7 | 835.8 | 801 | 751.6
1105 | 898 | 780.3 | 730.6 | 835.5 | 802.1 | 748.8
1106 | 899 | 780.3 | 733.5 | 834 | 802.5 | 750.4
1107 | 900 | 780.3 | 732.5 | 831.8 | 802.9 | 750.4
1108 | 901 | 780.6 | 726.1 | 826.8 | 804.3 | 748.9
1109 | 902 | 780.7 | 719.7 | 818.6 | 806.6 | 745.5
1110 | 903 | 780.8 | 713.9 | 813.5 | 809.2 | 743
1111 | 904 | 780.8 | 710.9 | 815.3 | 811.5 | 741.5
1112 | 905 | 780.7 | 712.9 | 817.9 | 812 | 740.2
1113 | 906 | 780.6 | 715.4 | 817.3 | 812 | 739.7
1114 | 907 | 780.7 | 712 | 812.6 | 812.3 | 739.2
1115 | 908 | 780.6 | 708.8 | 809.3 | 813.3 | 736.5
1116 | 909 | 780.5 | 708.7 | 808.5 | 813.6 | 736.1
1117 | 910 | 780.4 | 713.6 | 814.6 | 813.1 | 737.3
1118 | 911 | 780.5 | 715.7 | 818.5 | 812.7 | 736.2
1119 | 912 | 780.5 | 715.1 | 819.4 | 812.3 | 736.4
1120 | 913 | 780.7 | 714.7 | 820.3 | 812.9 | 735.6
1121 | 914 | 780.8 | 718.1 | 820.2 | 813.5 | 736.6
1122 | 915 | 780.9 | 719.6 | 816.6 | 813 | 737.4
1123 | 916 | 780.9 | 723.8 | 818.3 | 812.6 | 738.6
1124 | 917 | 781.2 | 728.4 | 821.3 | 811.8 | 740.6
1125 | 918 | 781.5 | 727.5 | 823 | 811.1 | 739.3
1126 | 919 | 781.6 | 729 | 824.1 | 810.5 | 739.1
1127 | 920 | 781.8 | 729.5 | 821 | 809.5 | 741.8
1128 | 921 | 782.1 | 724.8 | 817.3 | 809.8 | 740.9
1129 | 922 | 782.2 | 717.8 | 810.6 | 811.6 | 740.3
1130 | 923 | 782.4 | 714.6 | 806.9 | 814.1 | 739.7
1131 | 924 | 782.6 | 706.9 | 802.2 | 816.4 | 736.7
1132 | 925 | 782.6 | 701.3 | 799.4 | 818.2 | 734.2
1133 | 926 | 782.1 | 698.7 | 800.6 | 819.4 | 733.1
1134 | 927 | 781.8 | 699.1 | 805.1 | 819.7 | 731.8
1135 | 928 | 781.7 | 701.3 | 809.8 | 819.5 | 731.1
1136 | 929 | 781.7 | 708.2 | 810.8 | 818 | 734.6
1137 | 930 | 781.7 | 715.2 | 812.3 | 815.4 | 737.7
1138 | 931 | 781.8 | 717.8 | 812 | 813.6 | 739.7
1139 | 932 | 781.8 | 717 | 810.8 | 812.4 | 740.9
1140 | 933 | 782 | 713.3 | 806.3 | 813.3 | 741.3
1141 | 934 | 781.9 | 707.5 | 801.1 | 815.8 | 739.5
1142 | 935 | 781.9 | 706 | 805.1 | 817.5 | 739.5
1143 | 936 | 781.8 | 706.1 | 809.4 | 818 | 738.3
1144 | 937 | 781.8 | 708 | 811.9 | 818.3 | 736.4
1145 | 938 | 781.6 | 707.3 | 810.5 | 818.8 | 735.7
1146 | 939 | 781.5 | 707.3 | 812.6 | 819.7 | 734.2
1147 | 940 | 781.5 | 700.7 | 809.4 | 822 | 729.9
1148 | 941 | 781.2 | 696.9 | 809.2 | 823.7 | 726.5
1149 | 942 | 781 | 689.8 | 802.4 | 825.3 | 721.8
1150 | 943 | 780.4 | 676 | 780.8 | 826.3 | 715.6
1151 | 944 | 779.3 | 663 | 760.1 | 826.8 | 709.1
1152 | 945 | 777.8 | 649.6 | 740.9 | 826.4 | 702.7
1153 | 946 | 776.3 | 636.9 | 724.8 | 824.5 | 696.2
1154 | 947 | 774.8 | 625.4 | 710.1 | 822.4 | 690.6
1155 | 948 | 772.3 | 613.9 | 696.3 | 820.1 | 684.5
1156 | 949 | 770 | 601.1 | 683.9 | 817.1 | 678.6
1157 | 950 | 768.1 | 590.8 | 672.8 | 814 | 672.7
1158 | 951 | 766.8 | 582.4 | 661.9 | 811.7 | 667.4
1159 | 952 | 765.3 | 574.4 | 651.6 | 809.4 | 662.4
1160 | 953 | 763.6 | 566.4 | 642.6 | 807.9 | 657.6
1161 | 954 | 762 | 558.2 | 635 | 806.1 | 652.8
1162 | 955 | 760.6 | 551 | 628.3 | 804.1 | 648.3
1163 | 956 | 758.6 | 544.8 | 622.4 | 802 | 643.3
1164 | 957 | 756.9 | 537.9 | 614.7 | 800 | 638.6
1165 | 958 | 755.2 | 530.1 | 608.7 | 797.2 | 634.2
1166 | 959 | 754 | 524.3 | 603.8 | 794.7 | 630.2
1167 | 960 | 752.9 | 518.3 | 596.8 | 793.2 | 625.6
1168 | 961 | 751.5 | 513.2 | 592.7 | 791.4 | 621.5
1169 | 962 | 750 | 508.7 | 588.1 | 789.8 | 617.3
1170 | 963 | 748.3 | 504.2 | 583.4 | 787.7 | 613.2
1171 | 964 | 746.8 | 499.3 | 578 | 786.1 | 609.3
1172 | 965 | 745.3 | 493.7 | 573 | 784.5 | 605.7
1173 | 966 | 744.2 | 488.6 | 568.8 | 782.9 | 601.9
1174 | 967 | 743 | 484.3 | 564.5 | 781.2 | 598.3
1175 | 968 | 742.1 | 480.1 | 561.1 | 779 | 594.8
1176 | 969 | 741.4 | 475.7 | 556.3 | 776.8 | 591.4
1177 | 970 | 740.1 | 469 | 552.3 | 774.9 | 587.4
1178 | 971 | 738.5 | 462.1 | 548.7 | 772 | 583.7
1179 | 972 | 737.5 | 455.2 | 544.6 | 768.3 | 580.1
1180 | 973 | 736.5 | 449.7 | 540 | 765.2 | 576.8
1181 | 974 | 735.8 | 445.6 | 536.1 | 762.4 | 573.2
1182 | 975 | 735.1 | 441.4 | 532.4 | 759.9 | 569.9
1183 | 976 | 734.6 | 437.1 | 528.9 | 757.5 | 566.8
1184 | 977 | 734.2 | 431.4 | 525.3 | 754.9 | 563.5
1185 | 978 | 733.4 | 426 | 521.6 | 752.2 | 559.9
1186 | 979 | 732.4 | 422.5 | 518.3 | 749.5 | 556.5
1187 | 980 | 731.5 | 419.8 | 514.7 | 747.2 | 553.5
1188 | 981 | 730.8 | 415.2 | 511.5 | 744.8 | 550.4
1189 | 982 | 730.1 | 411.1 | 508.3 | 742.3 | 547.8
1190 | 983 | 729.3 | 406.6 | 505.3 | 739 | 545.2
1191 | 984 | 728.4 | 402.7 | 502.3 | 735.6 | 542.2
1192 | 985 | 727.5 | 399 | 499.9 | 732.7 | 539.3
1193 | 986 | 726.5 | 396.1 | 497.2 | 729.9 | 536.5
1194 | 987 | 725.5 | 391.4 | 494.2 | 727.1 | 534
1195 | 988 | 724.3 | 387.8 | 491.3 | 724.2 | 531
1196 | 989 | 722.7 | 384.4 | 489.1 | 721.2 | 528.3
1197 | 990 | 721.4 | 382.1 | 486.4 | 718.3 | 525.5
1198 | 991 | 719.7 | 378.9 | 483.4 | 715.6 | 522.7
1199 | 992 | 718 | 375.4 | 481.2 | 712.7 | 520.4
1200 | 993 | 716.6 | 372 | 478.5 | 709.3 | 518.3
1201 | 994 | 715.1 | 369 | 475.7 | 706.4 | 515.6
1202 | 995 | 713.6 | 365.6 | 473.5 | 703.6 | 513.6
1203 | 996 | 712.4 | 363.6 | 471.5 | 700.5 | 510.8
1204 | 997 | 711.2 | 361.3 | 469.2 | 697.5 | 508.2
1205 | 998 | 709.9 | 359.5 | 468 | 694.8 | 505.6
1206 | 999 | 708.5 | 358.4 | 465.9 | 692.5 | 502.9
1207 | 1000 | 707.1 | 356.3 | 463.9 | 690.4 | 500.8
1208 | 1001 | 706 | 353.9 | 461.3 | 688.3 | 498.7
1209 | 1002 | 704.3 | 352.4 | 458.3 | 686.3 | 496.1
1210 | 1003 | 702.1 | 350.2 | 455.9 | 684 | 493.6
1211 | 1004 | 700.1 | 348 | 453.7 | 681.5 | 491.2
1212 | 1005 | 698.4 | 346.6 | 450.9 | 679.2 | 488.9
1213 | 1006 | 696.7 | 343.9 | 449.1 | 676.8 | 486.7
1214 | 1007 | 695 | 341.6 | 447 | 674.3 | 484.4
1215 | 1008 | 693.3 | 340 | 444.3 | 671.7 | 482.2
1216 | 1009 | 691.8 | 338.3 | 442.2 | 669.1 | 479.7
1217 | 1010 | 690.4 | 336.1 | 439.9 | 666.6 | 477.8
1218 | 1011 | 689 | 334 | 438.1 | 663.8 | 476
1219 | 1012 | 687.7 | 331.6 | 435.8 | 660.8 | 473.7
1220 | 1013 | 686.1 | 330.3 | 433.7 | 657.8 | 471.8
1221 | 1014 | 684.5 | 327.7 | 431.7 | 655.1 | 470
1222 | 1015 | 683 | 325.4 | 429.5 | 652.2 | 467.8
1223 | 1016 | 681.1 | 322.6 | 426.9 | 649.5 | 465.7
1224 | 1017 | 679.3 | 320.7 | 424.4 | 646.7 | 463.6
1225 | 1018 | 677.5 | 318.7 | 421.9 | 643.9 | 461.5
1226 | 1019 | 675.6 | 317.7 | 420.9 | 641 | 459.3
1227 | 1020 | 673.6 | 316.7 | 419.7 | 637.7 | 458
1228 | 1021 | 671.6 | 315.5 | 418 | 634.2 | 455.6
1229 | 1022 | 670 | 314 | 416.1 | 630.6 | 453.2
1230 | 1023 | 668.2 | 311.9 | 414.1 | 627.1 | 451.5
1231 | 1024 | 666.5 | 310.3 | 412.7 | 624 | 449.7
1232 | 1025 | 665 | 309 | 410.7 | 620.9 | 447.8
1233 | 1026 | 663.1 | 307.1 | 409.2 | 617.8 | 446.2
1234 | 1027 | 661.4 | 305.5 | 407.7 | 614.7 | 444
1235 | 1028 | 659.9 | 303.7 | 405.6 | 611.6 | 442.5
1236 | 1029 | 657.8 | 301.7 | 403.7 | 608.6 | 441.2
1237 | 1030 | 655.8 | 300.6 | 402.4 | 605.5 | 439.7
1238 | 1031 | 654.2 | 300.1 | 400.6 | 602.3 | 438.3
1239 | 1032 | 652.5 | 298.8 | 398.8 | 599.1 | 436.4
1240 | 1033 | 650.7 | 298.1 | 396.5 | 595.9 | 434.4
1241 | 1034 | 649.2 | 296.5 | 393.7 | 593 | 432.3
1242 | 1035 | 647.9 | 294.7 | 391.3 | 590.4 | 430.2
1243 | 1036 | 646.5 | 293.3 | 389.2 | 587.8 | 428.2
1244 | 1037 | 645.2 | 292.4 | 387 | 585.4 | 426.5
1245 | 1038 | 644.1 | 290.8 | 384.9 | 582.9 | 425
1246 | 1039 | 643.1 | 289.5 | 382.7 | 580.4 | 423.3
1247 | 1040 | 641.9 | 289.1 | 380.4 | 578 | 421.6
1248 | 1041 | 641 | 288.2 | 378.8 | 575.8 | 420.2
1249 | 1042 | 640.3 | 287 | 376.8 | 573.6 | 418.8
1250 | 1043 | 639.5 | 286.6 | 375.4 | 571.4 | 417.1
1251 | 1044 | 638.8 | 285.9 | 373.4 | 569 | 415.6
1252 | 1045 | 637.9 | 283.6 | 371.3 | 566.7 | 414.3
1253 | 1046 | 637.1 | 282.1 | 369.6 | 564.5 | 412.4
1254 | 1047 | 636.3 | 280.6 | 367.3 | 562.3 | 411
1255 | 1048 | 635.2 | 279.9 | 365.4 | 560.1 | 409.4
1256 | 1049 | 634.4 | 279.7 | 363.2 | 557.9 | 408
1257 | 1050 | 633.6 | 278.7 | 361.5 | 555.7 | 406.3
1258 | 1051 | 632.6 | 278.8 | 360.2 | 553.4 | 404.5
1259 | 1052 | 631.9 | 279.1 | 358.5 | 551 | 403.1
1260 | 1053 | 631.2 | 279 | 356.7 | 548.5 | 401.7
1261 | 1054 | 630.2 | 278.5 | 354.6 | 546.1 | 400.3
1262 | 1055 | 629.5 | 277.8 | 352.2 | 543.6 | 398.8
1263 | 1056 | 628.6 | 277.1 | 350.1 | 541 | 397.3
1264 | 1057 | 627.6 | 276 | 348.3 | 538.5 | 396
1265 | 1058 | 626.8 | 275.2 | 346.4 | 536.1 | 394.9
1266 | 1059 | 625.9 | 274.1 | 344.3 | 533.7 | 393.2
1267 | 1060 | 625.1 | 273.3 | 342.5 | 531.4 | 391.9
1268 | 1061 | 624.6 | 273.1 | 341.4 | 529.1 | 390.5
1269 | 1062 | 624.2 | 272.5 | 339.9 | 526.9 | 389
1270 | 1063 | 624 | 271 | 338.1 | 524.7 | 387.5
1271 | 1064 | 623.6 | 269.8 | 336.2 | 522.6 | 386.1
1272 | 1065 | 623.1 | 268.1 | 335 | 520.5 | 384.7
1273 | 1066 | 622.2 | 267.3 | 333.4 | 518.5 | 383.3
1274 | 1067 | 620.9 | 267 | 331.7 | 516.5 | 381.8
1275 | 1068 | 619.9 | 265.7 | 329.6 | 514.5 | 380.5
1276 | 1069 | 618.6 | 264 | 327.8 | 512.5 | 379.3
1277 | 1070 | 617.4 | 262.6 | 325.5 | 510.6 | 377.6
1278 | 1071 | 616 | 262.1 | 323.8 | 508.6 | 376.3
1279 | 1072 | 614.9 | 260.6 | 321.7 | 506.7 | 374.8
1280 | 1073 | 613.6 | 259 | 319.3 | 504.8 | 373.4
1281 | 1074 | 611.8 | 258.4 | 317.4 | 503 | 372.1
1282 | 1075 | 610.2 | 256.9 | 316 | 501.2 | 371.2
1283 | 1076 | 608.6 | 256.2 | 314.6 | 499.7 | 369.9
1284 | 1077 | 607.2 | 254.9 | 312.4 | 498 | 368.4
1285 | 1078 | 606 | 253.6 | 309.9 | 496.2 | 366.5
1286 | 1079 | 604.3 | 252.9 | 308.1 | 494.3 | 365
1287 | 1080 | 603.1 | 251.8 | 306 | 492.4 | 364
1288 | 1081 | 601.2 | 251 | 303.3 | 490.5 | 363.1
1289 | 1082 | 598.9 | 250.2 | 300.8 | 488.5 | 361.8
1290 | 1083 | 597 | 248.6 | 298.6 | 486.6 | 360.4
1291 | 1084 | 595.3 | 247 | 296.3 | 484.7 | 359.3
1292 | 1085 | 594 | 246 | 294.3 | 482.9 | 358.1
1293 | 1086 | 592.8 | 244.6 | 292.7 | 481 | 356.7
1294 | 1087 | 591.5 | 244.3 | 291 | 479.2 | 355.3
1295 | 1088 | 590 | 243.4 | 288.8 | 477.3 | 354.3
1296 | 1089 | 588.3 | 242.6 | 286.4 | 475.4 | 353.1
1297 | 1090 | 587.1 | 241.6 | 284 | 473.5 | 352.2
1298 | 1091 | 586.3 | 240.5 | 282.1 | 471.8 | 351
1299 | 1092 | 585.1 | 239.2 | 280.2 | 470.2 | 350
1300 | 1093 | 583.6 | 239.1 | 278 | 468.6 | 348.6
1301 | 1094 | 581.9 | 238.6 | 276.6 | 466.8 | 347.3
1302 | 1095 | 580.2 | 237.7 | 275.1 | 464.9 | 346.2
1303 | 1096 | 578.9 | 236.1 | 273.3 | 463.1 | 345
1304 | 1097 | 577.6 | 235.2 | 271.2 | 461.4 | 343.8
1305 | 1098 | 575.9 | 234.8 | 269.7 | 459.6 | 342.9
1306 | 1099 | 574.1 | 234.2 | 268.1 | 458 | 341.9
1307 | 1100 | 572.1 | 233.5 | 265.9 | 456.4 | 340.4
1308 | 1101 | 570.3 | 232.4 | 264.1 | 454.7 | 339.1
1309 | 1102 | 568.4 | 231.8 | 262.6 | 453.1 | 338
1310 | 1103 | 566.3 | 230.7 | 260.5 | 451.5 | 336.7
1311 | 1104 | 564.6 | 229.7 | 258.8 | 450 | 335.9
1312 | 1105 | 562.9 | 229.2 | 258 | 448.5 | 335.1
1313 | 1106 | 561.3 | 228.1 | 256.1 | 447.1 | 334.4
1314 | 1107 | 559.3 | 228 | 254.8 | 445.5 | 333
1315 | 1108 | 557.5 | 227.2 | 253.8 | 443.6 | 332.1
1316 | 1109 | 555.8 | 226.6 | 252.7 | 441.6 | 331.1
1317 | 1110 | 554.1 | 225.5 | 251.5 | 439.7 | 329.9
1318 | 1111 | 552.5 | 224.4 | 249.8 | 437.8 | 329
1319 | 1112 | 551.1 | 223.3 | 248.3 | 435.8 | 327.9
1320 | 1113 | 549.6 | 223.4 | 247.2 | 433.9 | 326.9
1321 | 1114 | 548.2 | 222.8 | 245.4 | 431.9 | 325.9
1322 | 1115 | 547.1 | 222.2 | 243.9 | 430.1 | 325.2
1323 | 1116 | 546 | 221.5 | 242.5 | 428.4 | 323.9
1324 | 1117 | 544.9 | 221.1 | 241.1 | 426.9 | 322.9
1325 | 1118 | 543.4 | 220.7 | 239.8 | 425.3 | 321.9
1326 | 1119 | 541.9 | 220.5 | 238.4 | 423.6 | 321.1
1327 | 1120 | 540.9 | 220 | 236.7 | 422 | 320.3

## Test Facts
Last row in IRMS data sheets: | 35
Time when gas burner was ignited: | 207