## Test Conditions
CAROLFIRE Intermediate Scale Test Number IT-9
Test Date: | 2006-11-14
Ignition Time Relative to Thermal Data: | 194 | s
Ignition Time Relative to Electrical Data: | 194 | s
A Note regarding Propene Gas Flow Reading and calculation of Heat Release Rate:
The indicated flow rate is recorded in Standard Liters per Minute (SLM) of Gas. There is a correction factor of 0.40 applied to reflect the behavior of Propene versus the Flow Controller calibration gas which is Nitrogen. Hence, the actual flow of Propene in SLM is the indicated flow (shown in the data set as "Propene Gas Flow Reading") times 0.40. The heat release rate (HRR) can then be estimated using the gas density at standard conditions, heat of combustion, and the combustion efficiency. The result of this calculation is also shown on the data sheet based on the assumed properties listed below in the rows immediately below. Note that altering the values listed here will result in revised calculations of the HRR.
| Gas Burner Heat Release Rate Calculation Parameters: | Value | Units
| Gas Density At Standard conditions | 1.802 | kg/m3
| Heat of Combustion | 45.79 | MJ/kg
| One liter equals | 0.001 | m3
| Combustion efficiency | 0.85 | %

## Data Plots
Plot for identical cable bundles at Locations A, C and G

## Thermal Data
Time |  | Burner |  |  | Hood & Ambient Facility Temperatures | [5 empty] | Stack |  |  | External Wind |  | Location A - 6-cable bundle 9-1 |  |  |  | Location A | Location C - 6-cable bundle 9-1 |  |  |  | Location C | Location E - 3+1 bundle 9-2 in Conduit |  |  | Location G - 6-cable bundle 9-1 |  |  |  | Location G | Slug Calorimeters
Time (s) | Offset Time (s) | Raw Gas Flow | Corrected Gas Flow (SLM) | Nominal HRR (kW) | Hood East | Hood West | Hood North | Hood South | Hood Top | Facility Ambient | O2 analyzer | stack temp | diff press stack *10 | wind direction | wind speed (mph) | TC-1 Cable E | TC-2 Above Bundle | TC3 Below Bundle | TC4 Bundle Center | Tray Rung | TC-1 Cable E | TC-2 Above Bundle | TC3 Below Bundle | TC4 Bundle Center | Tray Rung | Cable 1 TC | Air Inside Conduit | Conduit Temp | TC-1 Cable E | TC-2 Above Bundle | TC3 Below Bundle | TC4 Bundle Center | Tray Rung | Slug Calorimeter Above Location F | Slug Calorimeter Above Location G
0 | -194 | -6.8 | 0 | 0 | 14.2 | 14.6 | 14.3 | 14.7 | 15.4 | 13 | 21.7 | 13 | 4.8 | 262.1 | 13.5 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.7 | 13.8 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
1 | -193 | -6.8 | 0 | 0 | 14.2 | 14.6 | 14.3 | 14.7 | 15.4 | 13 | 21.7 | 13 | 3.7 | 239.8 | 13 | 13.7 | 13.1 | 13.1 | 14.2 | 14.8 | 14.3 | 13.7 | 13.8 | 14.6 | 15.2 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.2 | 17 | 16.6 | 16.1
2 | -192 | -6.9 | 0 | 0 | 14.2 | 14.6 | 14.3 | 14.7 | 15.4 | 13 | 21.7 | 13 | 3.5 | 254.1 | 14.2 | 13.7 | 13.1 | 13.1 | 14.2 | 14.8 | 14.3 | 13.7 | 13.8 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
3 | -191 | -6.8 | 0 | 0 | 14.2 | 14.6 | 14.4 | 14.7 | 15.4 | 13 | 21.7 | 13 | 3.8 | 251.6 | 14.4 | 13.7 | 13.1 | 13.1 | 14.2 | 14.8 | 14.3 | 13.7 | 13.8 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
4 | -190 | -6.6 | 0 | 0 | 14.2 | 14.6 | 14.4 | 14.7 | 15.4 | 13 | 21.7 | 13 | 4.6 | 255.7 | 16.2 | 13.7 | 13.1 | 13.1 | 14.2 | 14.8 | 14.3 | 13.7 | 13.8 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
5 | -189 | -6.8 | 0 | 0 | 14.2 | 14.6 | 14.4 | 14.7 | 15.4 | 13 | 21.7 | 13 | 4.4 | 258.7 | 17.7 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.7 | 13.8 | 14.6 | 15.2 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
6 | -188 | -6.9 | 0 | 0 | 14.2 | 14.6 | 14.4 | 14.7 | 15.4 | 13 | 21.7 | 13 | 4.1 | 256.3 | 18.8 | 13.7 | 13.1 | 13.1 | 14.2 | 14.8 | 14.3 | 13.7 | 13.8 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
7 | -187 | -6.9 | 0 | 0 | 14.2 | 14.6 | 14.4 | 14.7 | 15.4 | 13 | 21.7 | 13 | 3.7 | 254.8 | 17.8 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.7 | 13.8 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
8 | -186 | -6.8 | 0 | 0 | 14.2 | 14.6 | 14.4 | 14.7 | 15.4 | 13 | 21.7 | 13 | 3.4 | 254.8 | 17.8 | 13.7 | 13.1 | 13.1 | 14.2 | 14.8 | 14.3 | 13.7 | 13.8 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
9 | -185 | -6.7 | 0 | 0 | 14.2 | 14.6 | 14.4 | 14.7 | 15.4 | 13 | 21.7 | 13 | 3.7 | 254.4 | 17.9 | 13.7 | 13.1 | 13.1 | 14.2 | 14.8 | 14.3 | 13.7 | 13.8 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
10 | -184 | -6.6 | 0 | 0 | 14.2 | 14.6 | 14.4 | 14.7 | 15.4 | 13 | 21.7 | 13 | 4.5 | 258.8 | 16.1 | 13.7 | 13.1 | 13.1 | 14.2 | 14.8 | 14.3 | 13.7 | 13.8 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.2 | 15.2 | 15.1 | 17 | 16.6 | 16.1
11 | -183 | -6.8 | 0 | 0 | 14.2 | 14.6 | 14.5 | 14.7 | 15.4 | 13 | 21.7 | 13 | 4.7 | 256.6 | 13.8 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.7 | 13.8 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.2 | 15.2 | 15.1 | 17 | 16.6 | 16.1
12 | -182 | -6.8 | 0 | 0 | 14.2 | 14.5 | 14.5 | 14.7 | 15.4 | 13 | 21.7 | 13 | 5.5 | 260.3 | 14.6 | 13.7 | 13.1 | 13.1 | 14.2 | 14.8 | 14.3 | 13.7 | 13.8 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.2 | 15.2 | 15.1 | 17 | 16.6 | 16.1
13 | -181 | -6.8 | 0 | 0 | 14.2 | 14.5 | 14.5 | 14.7 | 15.4 | 13 | 21.7 | 13 | 4.9 | 245.1 | 12.6 | 13.7 | 13.1 | 13.1 | 14.2 | 14.8 | 14.3 | 13.7 | 13.8 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.2 | 15.2 | 15.1 | 17 | 16.6 | 16.1
14 | -180 | -6.8 | 0 | 0 | 14.2 | 14.5 | 14.5 | 14.7 | 15.4 | 13 | 21.7 | 13 | 3.5 | 235.2 | 11 | 13.7 | 13.1 | 13.1 | 14.2 | 14.8 | 14.3 | 13.7 | 13.8 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.2 | 15.2 | 15.1 | 17 | 16.6 | 16.1
15 | -179 | -6.8 | 0 | 0 | 14.2 | 14.5 | 14.5 | 14.7 | 15.4 | 13 | 21.7 | 13 | 3.9 | 257.5 | 10.3 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.7 | 13.8 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.2 | 15.2 | 15.1 | 17 | 16.6 | 16.1
16 | -178 | -6.9 | 0 | 0 | 14.2 | 14.5 | 14.5 | 14.7 | 15.4 | 13 | 21.7 | 13 | 3.4 | 238.3 | 11.2 | 13.7 | 13.1 | 13.1 | 14.2 | 14.8 | 14.3 | 13.7 | 13.8 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.2 | 15.2 | 15.1 | 17 | 16.6 | 16.1
17 | -177 | -6.8 | 0 | 0 | 14.2 | 14.5 | 14.5 | 14.7 | 15.4 | 13 | 21.7 | 13 | 3.3 | 242.4 | 13 | 13.7 | 13.1 | 13.1 | 14.2 | 14.8 | 14.3 | 13.7 | 13.8 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.2 | 15.2 | 15.1 | 17 | 16.6 | 16.1
18 | -176 | -6.8 | 0 | 0 | 14.2 | 14.5 | 14.5 | 14.7 | 15.4 | 13 | 21.7 | 13 | 3.1 | 249.7 | 12.9 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.7 | 13.8 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.2 | 15.2 | 15.1 | 17 | 16.6 | 16.1
19 | -175 | -6.8 | 0 | 0 | 14.2 | 14.5 | 14.5 | 14.7 | 15.4 | 13 | 21.7 | 13 | 3 | 259.3 | 15 | 13.7 | 13.1 | 13.1 | 14.2 | 14.8 | 14.3 | 13.7 | 13.8 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.2 | 15.2 | 15.1 | 17 | 16.6 | 16.1
20 | -174 | -6.8 | 0 | 0 | 14.2 | 14.5 | 14.5 | 14.7 | 15.4 | 13 | 21.7 | 13 | 3.5 | 248.4 | 14.5 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.7 | 13.8 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.2 | 15.2 | 15.2 | 17 | 16.6 | 16.1
21 | -173 | -6.8 | 0 | 0 | 14.2 | 14.5 | 14.5 | 14.7 | 15.4 | 13 | 21.7 | 13 | 4.4 | 266.7 | 15.3 | 13.7 | 13.1 | 13.1 | 14.2 | 14.8 | 14.3 | 13.7 | 13.8 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
22 | -172 | -6.8 | 0 | 0 | 14.2 | 14.5 | 14.5 | 14.7 | 15.4 | 13 | 21.7 | 13 | 5.4 | 269.2 | 14.1 | 13.7 | 13.1 | 13.1 | 14.2 | 14.8 | 14.3 | 13.7 | 13.8 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
23 | -171 | -6.8 | 0 | 0 | 14.1 | 14.5 | 14.5 | 14.7 | 15.4 | 13 | 21.7 | 13 | 4.8 | 270.4 | 12.8 | 13.7 | 13.1 | 13.1 | 14.2 | 14.8 | 14.3 | 13.7 | 13.8 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
24 | -170 | -6.9 | 0 | 0 | 14.1 | 14.5 | 14.5 | 14.7 | 15.4 | 13 | 21.7 | 13 | 4.3 | 255.5 | 12.4 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.7 | 13.8 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.2 | 17 | 16.6 | 16.1
25 | -169 | -6.8 | 0 | 0 | 14.1 | 14.5 | 14.5 | 14.7 | 15.4 | 13 | 21.7 | 13.1 | 3.7 | 259.6 | 12.3 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.7 | 13.8 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
26 | -168 | -6.8 | 0 | 0 | 14.1 | 14.5 | 14.5 | 14.7 | 15.4 | 13 | 21.7 | 13 | 3.3 | 244.5 | 13 | 13.7 | 13.1 | 13.1 | 14.2 | 14.8 | 14.3 | 13.7 | 13.8 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
27 | -167 | -6.8 | 0 | 0 | 14.1 | 14.5 | 14.5 | 14.7 | 15.4 | 13.1 | 21.7 | 13 | 3.5 | 247.1 | 14.3 | 13.7 | 13 | 13.1 | 14.2 | 14.8 | 14.3 | 13.7 | 13.8 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
28 | -166 | -6.7 | 0 | 0 | 14.1 | 14.5 | 14.4 | 14.7 | 15.4 | 13.1 | 21.7 | 13 | 3.8 | 253.9 | 14.5 | 13.7 | 13 | 13.1 | 14.2 | 14.9 | 14.3 | 13.7 | 13.8 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
29 | -165 | -6.8 | 0 | 0 | 14.1 | 14.5 | 14.4 | 14.7 | 15.4 | 13.1 | 21.7 | 13.1 | 3.9 | 249.3 | 14.6 | 13.7 | 13 | 13.1 | 14.2 | 14.9 | 14.3 | 13.7 | 13.8 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.2 | 17 | 16.6 | 16.1
30 | -164 | -6.8 | 0 | 0 | 14.1 | 14.5 | 14.4 | 14.7 | 15.4 | 13.1 | 21.7 | 13 | 3.4 | 256 | 14.2 | 13.7 | 13 | 13.1 | 14.2 | 14.9 | 14.3 | 13.7 | 13.8 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
31 | -163 | -6.8 | 0 | 0 | 14.1 | 14.5 | 14.4 | 14.7 | 15.4 | 13.1 | 21.7 | 13 | 3.1 | 255.9 | 13.7 | 13.7 | 13 | 13.1 | 14.2 | 14.9 | 14.3 | 13.7 | 13.8 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
32 | -162 | -6.8 | 0 | 0 | 14.1 | 14.5 | 14.4 | 14.7 | 15.4 | 13.1 | 21.7 | 13 | 3.2 | 258.6 | 13.2 | 13.7 | 13 | 13.1 | 14.2 | 14.9 | 14.3 | 13.7 | 13.8 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
33 | -161 | -6.9 | 0 | 0 | 14.1 | 14.5 | 14.4 | 14.6 | 15.4 | 13.1 | 21.7 | 13 | 4.4 | 253.9 | 13 | 13.7 | 13 | 13.1 | 14.2 | 14.9 | 14.3 | 13.7 | 13.8 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
34 | -160 | -6.9 | 0 | 0 | 14.1 | 14.5 | 14.4 | 14.6 | 15.4 | 13.1 | 21.7 | 13 | 5.8 | 262.7 | 13.8 | 13.7 | 13 | 13.1 | 14.2 | 14.9 | 14.3 | 13.7 | 13.8 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
35 | -159 | -6.8 | 0 | 0 | 14.1 | 14.5 | 14.4 | 14.6 | 15.4 | 13.1 | 21.7 | 13 | 5.3 | 274 | 13.4 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.7 | 13.8 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.2 | 17 | 16.6 | 16.1
36 | -158 | -6.8 | 0 | 0 | 14.1 | 14.5 | 14.4 | 14.6 | 15.4 | 13.1 | 21.7 | 13 | 5.1 | 267.6 | 12.5 | 13.7 | 13 | 13.1 | 14.2 | 14.9 | 14.3 | 13.7 | 13.8 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 16.9 | 16.6 | 16.1
37 | -157 | -6.8 | 0 | 0 | 14.1 | 14.5 | 14.4 | 14.6 | 15.4 | 13 | 21.7 | 13 | 5.1 | 248.2 | 14 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.7 | 13.8 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
38 | -156 | -6.8 | 0 | 0 | 14.1 | 14.5 | 14.4 | 14.6 | 15.4 | 13.1 | 21.7 | 13 | 4.6 | 255.2 | 17.6 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.7 | 13.8 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
39 | -155 | -6.8 | 0 | 0 | 14.1 | 14.5 | 14.4 | 14.6 | 15.4 | 13 | 21.7 | 13 | 5.3 | 252.3 | 18.8 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.7 | 13.8 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
40 | -154 | -6.9 | 0 | 0 | 14.1 | 14.6 | 14.4 | 14.6 | 15.4 | 13 | 21.7 | 13 | 5.3 | 255.7 | 19.6 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.7 | 13.8 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
41 | -153 | -6.9 | 0 | 0 | 14.1 | 14.6 | 14.4 | 14.6 | 15.3 | 13 | 21.7 | 13 | 4.2 | 259.3 | 16.8 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.7 | 13.8 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
42 | -152 | -6.9 | 0 | 0 | 14.1 | 14.6 | 14.4 | 14.7 | 15.3 | 13 | 21.7 | 13 | 3.5 | 241.6 | 15.4 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.7 | 13.8 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
43 | -151 | -6.8 | 0 | 0 | 14.1 | 14.6 | 14.4 | 14.7 | 15.3 | 13 | 21.7 | 13 | 3.5 | 237.5 | 15 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.7 | 13.8 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
44 | -150 | -6.8 | 0 | 0 | 14.1 | 14.6 | 14.4 | 14.7 | 15.3 | 13 | 21.7 | 13 | 3.6 | 247.5 | 13.5 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.7 | 13.8 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
45 | -149 | -6.7 | 0 | 0 | 14.1 | 14.6 | 14.4 | 14.7 | 15.3 | 13 | 21.7 | 13 | 3.5 | 245.9 | 14.8 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.7 | 13.8 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
46 | -148 | -6.8 | 0 | 0 | 14.1 | 14.6 | 14.4 | 14.7 | 15.3 | 13 | 21.7 | 13 | 3.5 | 250.9 | 14.1 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.7 | 13.8 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
47 | -147 | -6.9 | 0 | 0 | 14.1 | 14.6 | 14.4 | 14.7 | 15.3 | 13 | 21.7 | 13 | 3.7 | 253.8 | 12 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.7 | 13.8 | 14.6 | 15.2 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
48 | -146 | -6.5 | 0 | 0 | 14.1 | 14.6 | 14.4 | 14.7 | 15.3 | 13 | 21.7 | 13 | 3.5 | 267.6 | 9.5 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.7 | 13.8 | 14.6 | 15.2 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
49 | -145 | -6.9 | 0 | 0 | 14.1 | 14.6 | 14.4 | 14.7 | 15.3 | 13 | 21.7 | 13 | 3.5 | 241.9 | 8.8 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.7 | 13.8 | 14.6 | 15.2 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
50 | -144 | -6.9 | 0 | 0 | 14.1 | 14.6 | 14.4 | 14.7 | 15.3 | 13 | 21.7 | 13 | 3.1 | 240 | 8.4 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.7 | 13.8 | 14.6 | 15.2 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
51 | -143 | -6.8 | 0 | 0 | 14.1 | 14.6 | 14.4 | 14.7 | 15.3 | 13 | 21.7 | 13 | 2.5 | 252.9 | 9 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.7 | 13.8 | 14.6 | 15.2 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
52 | -142 | -6.8 | 0 | 0 | 14.1 | 14.6 | 14.4 | 14.7 | 15.3 | 13 | 21.7 | 13 | 2.2 | 243.1 | 9 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.7 | 13.8 | 14.6 | 15.2 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
53 | -141 | -6.8 | 0 | 0 | 14.1 | 14.6 | 14.5 | 14.7 | 15.3 | 13 | 21.8 | 13 | 2.2 | 234.5 | 8 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.7 | 13.8 | 14.6 | 15.2 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
54 | -140 | -6.8 | 0 | 0 | 14.1 | 14.6 | 14.5 | 14.7 | 15.3 | 13 | 21.8 | 13 | 2.3 | 258.1 | 7.4 | 13.7 | 13 | 13.1 | 14.2 | 14.9 | 14.3 | 13.7 | 13.8 | 14.6 | 15.2 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
55 | -139 | -6.9 | 0 | 0 | 14.1 | 14.6 | 14.5 | 14.6 | 15.3 | 13 | 21.7 | 13 | 2.3 | 230.9 | 8.5 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.7 | 13.8 | 14.6 | 15.2 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 16.9 | 16.6 | 16.1
56 | -138 | -6.9 | 0 | 0 | 14.1 | 14.6 | 14.5 | 14.6 | 15.3 | 13 | 21.8 | 13 | 2.3 | 232.2 | 10.4 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.7 | 13.8 | 14.6 | 15.2 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
57 | -137 | -6.9 | 0 | 0 | 14.1 | 14.6 | 14.5 | 14.6 | 15.3 | 13 | 21.8 | 13 | 2.1 | 229.7 | 9.3 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.7 | 13.8 | 14.6 | 15.2 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
58 | -136 | -6.9 | 0 | 0 | 14.1 | 14.5 | 14.5 | 14.6 | 15.3 | 13.1 | 21.8 | 13 | 2.3 | 268.1 | 7.9 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.7 | 13.8 | 14.6 | 15.2 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
59 | -135 | -6.9 | 0 | 0 | 14.1 | 14.5 | 14.5 | 14.6 | 15.3 | 13.1 | 21.8 | 13 | 2.4 | 258.8 | 7.7 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.7 | 13.7 | 14.6 | 15.2 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
60 | -134 | -6.8 | 0 | 0 | 14.1 | 14.5 | 14.5 | 14.6 | 15.3 | 13.1 | 21.8 | 13 | 2.2 | 249.5 | 7 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.6 | 13.7 | 14.6 | 15.2 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
61 | -133 | -6.8 | 0 | 0 | 14.1 | 14.5 | 14.5 | 14.6 | 15.3 | 13.1 | 21.8 | 13 | 2.6 | 252 | 7.2 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.6 | 13.8 | 14.6 | 15.2 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
62 | -132 | -6.8 | 0 | 0 | 14.1 | 14.5 | 14.5 | 14.6 | 15.3 | 13.1 | 21.8 | 13 | 3.1 | 249.1 | 7.6 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.6 | 13.7 | 14.6 | 15.2 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
63 | -131 | -6.8 | 0 | 0 | 14.1 | 14.5 | 14.5 | 14.6 | 15.3 | 13.1 | 21.7 | 13 | 3.6 | 246.2 | 7.3 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.6 | 13.7 | 14.6 | 15.2 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
64 | -130 | -6.7 | 0 | 0 | 14.1 | 14.5 | 14.5 | 14.5 | 15.3 | 13.1 | 21.8 | 13 | 3.4 | 245.7 | 6.7 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.6 | 13.7 | 14.6 | 15.2 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
65 | -129 | -6.7 | 0 | 0 | 14.2 | 14.5 | 14.5 | 14.5 | 15.3 | 13.1 | 21.8 | 13 | 3.1 | 250.4 | 6.5 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.6 | 13.7 | 14.6 | 15.2 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
66 | -128 | -6.8 | 0 | 0 | 14.2 | 14.5 | 14.4 | 14.5 | 15.3 | 13.1 | 21.8 | 13 | 2.6 | 249.6 | 6.8 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.6 | 13.7 | 14.6 | 15.2 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.2 | 17 | 16.6 | 16.1
67 | -127 | -6.8 | 0 | 0 | 14.2 | 14.5 | 14.4 | 14.5 | 15.3 | 13.1 | 21.8 | 13 | 3.2 | 244.4 | 7.5 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.6 | 13.7 | 14.6 | 15.2 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
68 | -126 | -6.9 | 0 | 0 | 14.2 | 14.5 | 14.4 | 14.5 | 15.3 | 13.1 | 21.8 | 13 | 3.3 | 242.5 | 8.3 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.6 | 13.8 | 14.6 | 15.2 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
69 | -125 | -6.8 | 0 | 0 | 14.2 | 14.5 | 14.4 | 14.5 | 15.3 | 13.1 | 21.7 | 13 | 3 | 222.1 | 9.2 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.6 | 13.7 | 14.6 | 15.2 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
70 | -124 | -6.9 | 0 | 0 | 14.2 | 14.5 | 14.4 | 14.5 | 15.4 | 13.1 | 21.7 | 13 | 3.5 | 234.9 | 8.8 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.6 | 13.7 | 14.6 | 15.2 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
71 | -123 | -6.9 | 0 | 0 | 14.2 | 14.5 | 14.4 | 14.5 | 15.4 | 13.1 | 21.7 | 13 | 4.3 | 232.9 | 9.4 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.7 | 13.8 | 14.6 | 15.2 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
72 | -122 | -6.9 | 0 | 0 | 14.3 | 14.4 | 14.4 | 14.5 | 15.4 | 13.1 | 21.7 | 13 | 3.8 | 242.6 | 7.9 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.7 | 13.8 | 14.6 | 15.2 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
73 | -121 | -6.9 | 0 | 0 | 14.3 | 14.4 | 14.3 | 14.5 | 15.4 | 13 | 21.7 | 13 | 3.7 | 233.9 | 8.3 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.6 | 13.8 | 14.6 | 15.2 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
74 | -120 | -6.9 | 0 | 0 | 14.3 | 14.4 | 14.3 | 14.5 | 15.4 | 13 | 21.8 | 13 | 3.8 | 242.2 | 8.7 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.7 | 13.8 | 14.6 | 15.2 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
75 | -119 | -6.9 | 0 | 0 | 14.3 | 14.4 | 14.3 | 14.5 | 15.4 | 13 | 21.8 | 13 | 3.7 | 241.2 | 12.5 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.7 | 13.8 | 14.6 | 15.2 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
76 | -118 | -6.9 | 0 | 0 | 14.3 | 14.4 | 14.3 | 14.5 | 15.4 | 13 | 21.8 | 13 | 3.3 | 254.7 | 12.8 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.7 | 13.7 | 14.6 | 15.2 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
77 | -117 | -6.8 | 0 | 0 | 14.4 | 14.4 | 14.3 | 14.6 | 15.4 | 13 | 21.8 | 13 | 3 | 243.5 | 12.7 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.7 | 13.8 | 14.6 | 15.2 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
78 | -116 | -6.9 | 0 | 0 | 14.4 | 14.4 | 14.3 | 14.6 | 15.4 | 13 | 21.8 | 13 | 3.3 | 240.7 | 13.4 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.7 | 13.8 | 14.6 | 15.2 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
79 | -115 | -6.8 | 0 | 0 | 14.4 | 14.4 | 14.3 | 14.6 | 15.4 | 13 | 21.7 | 13 | 3.5 | 244.9 | 13.6 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.7 | 13.8 | 14.6 | 15.2 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
80 | -114 | -6.8 | 0 | 0 | 14.4 | 14.4 | 14.3 | 14.6 | 15.4 | 13 | 21.7 | 13 | 3.8 | 248.1 | 13.4 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.7 | 13.8 | 14.6 | 15.2 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
81 | -113 | -6.9 | 0 | 0 | 14.4 | 14.4 | 14.3 | 14.6 | 15.4 | 13 | 21.7 | 12.9 | 3.4 | 244.1 | 12.5 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.7 | 13.8 | 14.6 | 15.2 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
82 | -112 | -6.9 | 0 | 0 | 14.4 | 14.4 | 14.3 | 14.6 | 15.4 | 13 | 21.7 | 12.9 | 3.2 | 246 | 11.4 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.7 | 13.8 | 14.6 | 15.2 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
83 | -111 | -6.9 | 0 | 0 | 14.4 | 14.4 | 14.3 | 14.6 | 15.4 | 13 | 21.7 | 13 | 3.4 | 239.1 | 11.8 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.7 | 13.8 | 14.6 | 15.2 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
84 | -110 | -6.9 | 0 | 0 | 14.4 | 14.4 | 14.3 | 14.6 | 15.4 | 13 | 21.8 | 13 | 3 | 230.9 | 10.5 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.7 | 13.8 | 14.6 | 15.2 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
85 | -109 | -6.9 | 0 | 0 | 14.4 | 14.4 | 14.4 | 14.6 | 15.4 | 13 | 21.8 | 13 | 3.4 | 261 | 8.4 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.7 | 13.8 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
86 | -108 | -6.8 | 0 | 0 | 14.4 | 14.4 | 14.4 | 14.6 | 15.3 | 13 | 21.7 | 13 | 2.7 | 274.9 | 8.1 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.7 | 13.8 | 14.6 | 15.2 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
87 | -107 | -6.8 | 0 | 0 | 14.4 | 14.4 | 14.4 | 14.6 | 15.4 | 13 | 21.7 | 13 | 2.3 | 265 | 8.5 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.7 | 13.9 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
88 | -106 | -6.8 | 0 | 0 | 14.4 | 14.5 | 14.4 | 14.6 | 15.3 | 13.1 | 21.8 | 13 | 2 | 243.8 | 8.9 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.7 | 13.9 | 14.6 | 15.2 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
89 | -105 | -6.8 | 0 | 0 | 14.4 | 14.5 | 14.4 | 14.6 | 15.3 | 13.1 | 21.8 | 13 | 2.2 | 236.9 | 9.3 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.7 | 13.9 | 14.6 | 15.2 | 15.5 | 15.4 | 16.7 | 15.4 | 15.2 | 15.2 | 15.1 | 17 | 16.6 | 16.1
90 | -104 | -6.8 | 0 | 0 | 14.4 | 14.5 | 14.4 | 14.6 | 15.3 | 13.1 | 21.7 | 13 | 2.7 | 237 | 11.8 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.7 | 13.9 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
91 | -103 | -6.8 | 0 | 0 | 14.4 | 14.5 | 14.4 | 14.6 | 15.3 | 13 | 21.7 | 13 | 2.7 | 246.7 | 11.8 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.7 | 13.9 | 14.6 | 15.2 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
92 | -102 | -6.8 | 0 | 0 | 14.3 | 14.5 | 14.4 | 14.6 | 15.3 | 13 | 21.8 | 13 | 2.6 | 242.6 | 10.9 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.7 | 13.9 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
93 | -101 | -6.9 | 0 | 0 | 14.3 | 14.5 | 14.4 | 14.6 | 15.3 | 13 | 21.7 | 13 | 2.4 | 242 | 10.5 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.7 | 13.9 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
94 | -100 | -6.8 | 0 | 0 | 14.3 | 14.6 | 14.4 | 14.6 | 15.3 | 13 | 21.8 | 13 | 2.7 | 267.6 | 12 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.7 | 13.9 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.2 | 15.2 | 15.1 | 17 | 16.6 | 16.1
95 | -99 | -6.9 | 0 | 0 | 14.3 | 14.6 | 14.4 | 14.6 | 15.3 | 13 | 21.8 | 12.9 | 2.7 | 274.8 | 12.5 | 13.7 | 13.1 | 13.2 | 14.2 | 14.9 | 14.3 | 13.7 | 13.9 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.2 | 15.2 | 15.1 | 17 | 16.6 | 16.1
96 | -98 | -6.8 | 0 | 0 | 14.3 | 14.6 | 14.4 | 14.6 | 15.3 | 13.1 | 21.8 | 12.9 | 2.8 | 266.5 | 11.4 | 13.7 | 13.1 | 13.2 | 14.2 | 14.9 | 14.3 | 13.7 | 13.9 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
97 | -97 | -6.9 | 0 | 0 | 14.3 | 14.6 | 14.4 | 14.6 | 15.3 | 13.1 | 21.8 | 12.9 | 2.8 | 276 | 12 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.7 | 13.9 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
98 | -96 | -6.8 | 0 | 0 | 14.3 | 14.6 | 14.4 | 14.6 | 15.3 | 13.1 | 21.8 | 12.9 | 2.8 | 262 | 11.7 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.7 | 13.9 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
99 | -95 | -6.8 | 0 | 0 | 14.3 | 14.6 | 14.5 | 14.6 | 15.3 | 13.1 | 21.8 | 12.9 | 2.7 | 264.6 | 11.5 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.7 | 13.9 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
100 | -94 | -6.8 | 0 | 0 | 14.3 | 14.6 | 14.5 | 14.6 | 15.3 | 13.1 | 21.8 | 12.9 | 2.8 | 273.6 | 11 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.7 | 13.9 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
101 | -93 | -6.8 | 0 | 0 | 14.3 | 14.6 | 14.5 | 14.6 | 15.3 | 13.1 | 21.8 | 12.9 | 2.8 | 254.1 | 10.4 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.7 | 13.9 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 16.9 | 16.6 | 16.1
102 | -92 | -6.6 | 0 | 0 | 14.3 | 14.6 | 14.5 | 14.6 | 15.3 | 13.1 | 21.8 | 12.9 | 2.7 | 263.5 | 9.9 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.7 | 13.9 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
103 | -91 | -6.5 | 0 | 0 | 14.3 | 14.7 | 14.5 | 14.6 | 15.3 | 13.1 | 21.8 | 13 | 3.8 | 245.1 | 9.2 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.7 | 13.9 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
104 | -90 | -6.6 | 0 | 0 | 14.3 | 14.7 | 14.6 | 14.5 | 15.3 | 13.1 | 21.8 | 13 | 3.9 | 247.2 | 8.9 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.7 | 13.9 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
105 | -89 | -6.6 | 0 | 0 | 14.3 | 14.7 | 14.6 | 14.5 | 15.3 | 13.1 | 21.7 | 13 | 4.1 | 252.2 | 7.8 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.8 | 13.9 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.1 | 15.1 | 17 | 16.6 | 16.1
106 | -88 | -6.7 | 0 | 0 | 14.3 | 14.7 | 14.6 | 14.5 | 15.3 | 13.1 | 21.8 | 13 | 4.2 | 243.5 | 7.1 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.7 | 13.9 | 14.6 | 15.2 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.1 | 15.1 | 17 | 16.6 | 16.1
107 | -87 | -6.7 | 0 | 0 | 14.3 | 14.7 | 14.6 | 14.5 | 15.3 | 13.1 | 21.8 | 13 | 4 | 243.5 | 6.5 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.8 | 13.9 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.1 | 15.1 | 17 | 16.6 | 16.1
108 | -86 | -6.8 | 0 | 0 | 14.3 | 14.7 | 14.6 | 14.5 | 15.3 | 13.1 | 21.8 | 13 | 3.1 | 227.6 | 6.1 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.8 | 13.9 | 14.6 | 15.2 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.1 | 15.1 | 17 | 16.6 | 16.1
109 | -85 | -6.8 | 0 | 0 | 14.3 | 14.7 | 14.7 | 14.5 | 15.3 | 13 | 21.7 | 13 | 3.4 | 209.3 | 4.4 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.8 | 13.9 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.1 | 15.1 | 17 | 16.6 | 16.1
110 | -84 | -6.8 | 0 | 0 | 14.3 | 14.7 | 14.7 | 14.5 | 15.3 | 13 | 21.8 | 13 | 3.5 | 261 | 5.6 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.8 | 13.9 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.1 | 15.1 | 17 | 16.6 | 16.1
111 | -83 | -6.8 | 0 | 0 | 14.3 | 14.6 | 14.7 | 14.5 | 15.3 | 13.1 | 21.8 | 13 | 4.2 | 241.9 | 8.3 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.8 | 13.9 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.1 | 15.1 | 17 | 16.6 | 16.1
112 | -82 | -6.9 | 0 | 0 | 14.3 | 14.6 | 14.7 | 14.5 | 15.3 | 13 | 21.8 | 13 | 4.3 | 273.5 | 9 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.8 | 13.9 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.1 | 15.1 | 17 | 16.6 | 16.1
113 | -81 | -6.9 | 0 | 0 | 14.3 | 14.6 | 14.7 | 14.5 | 15.3 | 13 | 21.8 | 13 | 3.8 | 271.5 | 12.1 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.8 | 13.9 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.1 | 15.1 | 17 | 16.6 | 16.1
114 | -80 | -6.9 | 0 | 0 | 14.3 | 14.6 | 14.7 | 14.5 | 15.3 | 13 | 21.8 | 13 | 3.7 | 269.3 | 15.4 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.8 | 13.9 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.1 | 15.1 | 17 | 16.6 | 16.1
115 | -79 | -6.9 | 0 | 0 | 14.3 | 14.6 | 14.7 | 14.5 | 15.3 | 13 | 21.8 | 13 | 3 | 280.1 | 14.2 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.8 | 13.9 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.1 | 15.1 | 17 | 16.6 | 16.1
116 | -78 | -6.9 | 0 | 0 | 14.3 | 14.6 | 14.7 | 14.5 | 15.3 | 13 | 21.8 | 13 | 3.1 | 274.2 | 14.9 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.8 | 13.9 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.1 | 15.1 | 17 | 16.6 | 16.1
117 | -77 | -6.9 | 0 | 0 | 14.4 | 14.6 | 14.8 | 14.5 | 15.3 | 13 | 21.8 | 13 | 2.7 | 278.7 | 14.9 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.8 | 13.9 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.1 | 15.1 | 17 | 16.6 | 16.1
118 | -76 | -6.9 | 0 | 0 | 14.4 | 14.6 | 14.8 | 14.5 | 15.3 | 13 | 21.8 | 13 | 2.7 | 272.9 | 14.3 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.8 | 13.9 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.1 | 15.1 | 17 | 16.6 | 16.1
119 | -75 | -6.9 | 0 | 0 | 14.4 | 14.6 | 14.8 | 14.6 | 15.3 | 13 | 21.8 | 12.9 | 3.8 | 271.1 | 13.6 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.8 | 13.9 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.1 | 15.1 | 16.9 | 16.6 | 16.1
120 | -74 | -6.9 | 0 | 0 | 14.4 | 14.6 | 14.8 | 14.6 | 15.3 | 13 | 21.8 | 13 | 4.8 | 256.1 | 12.9 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.8 | 13.9 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
121 | -73 | -6.9 | 0 | 0 | 14.4 | 14.6 | 14.8 | 14.6 | 15.3 | 13 | 21.8 | 13 | 4.9 | 289.1 | 10.2 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.8 | 13.9 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
122 | -72 | -6.8 | 0 | 0 | 14.4 | 14.6 | 14.8 | 14.6 | 15.3 | 13 | 21.8 | 13 | 4.2 | 260.2 | 9.6 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.8 | 13.9 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
123 | -71 | -6.9 | 0 | 0 | 14.4 | 14.6 | 14.8 | 14.6 | 15.3 | 13 | 21.8 | 13 | 3.7 | 253 | 13.2 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.8 | 13.9 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
124 | -70 | -6.9 | 0 | 0 | 14.4 | 14.6 | 14.7 | 14.6 | 15.3 | 13 | 21.8 | 13 | 4.7 | 241.3 | 15.2 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.8 | 13.9 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
125 | -69 | -6.9 | 0 | 0 | 14.4 | 14.6 | 14.7 | 14.6 | 15.3 | 13 | 21.8 | 13 | 4.4 | 250.8 | 15.9 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.8 | 13.9 | 14.5 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
126 | -68 | -6.9 | 0 | 0 | 14.4 | 14.6 | 14.7 | 14.7 | 15.3 | 13 | 21.7 | 13 | 4.7 | 252.6 | 15.4 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.9 | 13.9 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
127 | -67 | -6.9 | 0 | 0 | 14.4 | 14.6 | 14.7 | 14.7 | 15.3 | 13 | 21.8 | 13 | 5.6 | 259.9 | 15.3 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.9 | 13.9 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
128 | -66 | -6.9 | 0 | 0 | 14.4 | 14.6 | 14.7 | 14.7 | 15.3 | 13 | 21.8 | 13 | 5.3 | 263.9 | 15 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.9 | 13.9 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
129 | -65 | -6.9 | 0 | 0 | 14.4 | 14.6 | 14.7 | 14.7 | 15.3 | 13 | 21.7 | 13 | 3.9 | 234.5 | 12.5 | 13.7 | 13.1 | 13.2 | 14.2 | 14.9 | 14.3 | 13.9 | 13.9 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
130 | -64 | -6.9 | 0 | 0 | 14.4 | 14.6 | 14.7 | 14.7 | 15.3 | 13 | 21.8 | 13 | 4.7 | 278.9 | 10.8 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.9 | 13.9 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
131 | -63 | -6.9 | 0 | 0 | 14.4 | 14.6 | 14.7 | 14.7 | 15.3 | 13 | 21.8 | 13 | 5.4 | 238 | 10.2 | 13.7 | 13.1 | 13.2 | 14.2 | 14.9 | 14.3 | 13.9 | 13.9 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
132 | -62 | -6.9 | 0 | 0 | 14.4 | 14.6 | 14.7 | 14.6 | 15.3 | 13 | 21.7 | 13 | 4.6 | 264.4 | 9.1 | 13.7 | 13.1 | 13.2 | 14.2 | 14.9 | 14.3 | 13.9 | 13.9 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
133 | -61 | -6.9 | 0 | 0 | 14.4 | 14.6 | 14.7 | 14.6 | 15.3 | 13 | 21.7 | 13 | 4.7 | 242.5 | 10 | 13.7 | 13.1 | 13.2 | 14.2 | 14.9 | 14.3 | 13.9 | 13.9 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
134 | -60 | -2.5 | 0 | 0 | 14.4 | 14.6 | 14.7 | 14.6 | 15.3 | 13 | 21.8 | 13 | 4.1 | 248.3 | 13.2 | 13.7 | 13.1 | 13.2 | 14.2 | 14.9 | 14.3 | 13.9 | 13.9 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
135 | -59 | -6.9 | 0 | 0 | 14.5 | 14.6 | 14.7 | 14.7 | 15.3 | 13 | 21.8 | 13 | 3.6 | 253.4 | 14.5 | 13.7 | 13.1 | 13.2 | 14.2 | 14.9 | 14.3 | 13.9 | 13.9 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
136 | -58 | -6.9 | 0 | 0 | 14.4 | 14.6 | 14.7 | 14.7 | 15.3 | 13 | 21.8 | 13 | 3.6 | 252.5 | 15 | 13.7 | 13.1 | 13.2 | 14.2 | 14.9 | 14.3 | 13.9 | 13.9 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
137 | -57 | -6.9 | 0 | 0 | 14.4 | 14.6 | 14.7 | 14.7 | 15.3 | 13 | 21.8 | 13 | 3.5 | 252.9 | 16.2 | 13.7 | 13.1 | 13.2 | 14.2 | 14.9 | 14.3 | 13.9 | 13.9 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
138 | -56 | -6.9 | 0 | 0 | 14.5 | 14.6 | 14.7 | 14.7 | 15.3 | 13 | 21.8 | 13 | 3.3 | 257.5 | 14.5 | 13.7 | 13.1 | 13.2 | 14.2 | 14.9 | 14.3 | 13.9 | 13.9 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
139 | -55 | -6.8 | 0 | 0 | 14.5 | 14.6 | 14.7 | 14.7 | 15.3 | 13 | 21.8 | 13 | 3.5 | 261 | 13 | 13.7 | 13.1 | 13.2 | 14.2 | 14.9 | 14.3 | 13.9 | 13.9 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
140 | -54 | -6.7 | 0 | 0 | 14.5 | 14.6 | 14.7 | 14.7 | 15.3 | 13 | 21.8 | 13 | 3.7 | 260.1 | 12.9 | 13.7 | 13.1 | 13.2 | 14.2 | 14.9 | 14.3 | 13.9 | 13.9 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
141 | -53 | -6.6 | 0 | 0 | 14.5 | 14.6 | 14.7 | 14.7 | 15.3 | 13 | 21.8 | 13 | 4.1 | 270.8 | 11.5 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.9 | 13.9 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 16.9 | 16.6 | 16.1
142 | -52 | -6.8 | 0 | 0 | 14.5 | 14.6 | 14.7 | 14.7 | 15.3 | 13 | 21.8 | 13 | 4.1 | 271 | 10.9 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.9 | 13.9 | 14.5 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
143 | -51 | -6.9 | 0 | 0 | 14.5 | 14.6 | 14.7 | 14.7 | 15.3 | 13 | 21.8 | 13 | 3.5 | 254.3 | 11.4 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.9 | 13.9 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
144 | -50 | -6.9 | 0 | 0 | 14.5 | 14.6 | 14.7 | 14.7 | 15.3 | 13 | 21.8 | 13 | 3.7 | 256.2 | 12.8 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.9 | 13.9 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
145 | -49 | -6.9 | 0 | 0 | 14.5 | 14.6 | 14.7 | 14.7 | 15.3 | 13 | 21.8 | 13 | 3.8 | 261.1 | 15.2 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.9 | 13.9 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
146 | -48 | -6.9 | 0 | 0 | 14.5 | 14.6 | 14.7 | 14.7 | 15.3 | 13 | 21.7 | 13 | 4.7 | 252 | 16.2 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.9 | 13.9 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
147 | -47 | -6.9 | 0 | 0 | 14.5 | 14.6 | 14.7 | 14.7 | 15.3 | 13 | 21.8 | 13 | 5.7 | 248.8 | 15 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.9 | 13.9 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
148 | -46 | -6.9 | 0 | 0 | 14.5 | 14.6 | 14.7 | 14.7 | 15.3 | 13 | 21.7 | 13 | 4.6 | 248.9 | 14.7 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.9 | 13.9 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
149 | -45 | -6.9 | 0 | 0 | 14.5 | 14.6 | 14.7 | 14.6 | 15.3 | 13 | 21.8 | 13 | 3.3 | 251.1 | 16.5 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.8 | 13.9 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 16.9 | 16.6 | 16.1
150 | -44 | -6.9 | 0 | 0 | 14.5 | 14.6 | 14.7 | 14.6 | 15.3 | 13 | 21.8 | 13 | 2.6 | 257.3 | 15.5 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.8 | 13.9 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
151 | -43 | -6.9 | 0 | 0 | 14.5 | 14.6 | 14.7 | 14.6 | 15.3 | 13 | 21.8 | 13 | 2.6 | 258.5 | 16.1 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.8 | 13.9 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.1 | 15.1 | 17 | 16.6 | 16.1
152 | -42 | -6.9 | 0 | 0 | 14.5 | 14.6 | 14.7 | 14.6 | 15.3 | 13 | 21.8 | 12.9 | 2.9 | 249.6 | 15.6 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.9 | 13.9 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.1 | 15.1 | 17 | 16.6 | 16.1
153 | -41 | -6.9 | 0 | 0 | 14.4 | 14.6 | 14.7 | 14.6 | 15.3 | 13 | 21.8 | 12.9 | 3 | 255.6 | 14.6 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.8 | 13.9 | 14.5 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
154 | -40 | -6.9 | 0 | 0 | 14.4 | 14.7 | 14.7 | 14.7 | 15.3 | 13 | 21.8 | 12.9 | 2.8 | 256.9 | 13 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.8 | 13.9 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 16.9 | 16.6 | 16.1
155 | -39 | -6.9 | 0 | 0 | 14.4 | 14.7 | 14.7 | 14.6 | 15.3 | 13 | 21.8 | 12.9 | 3.3 | 256.3 | 15.1 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.8 | 13.9 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
156 | -38 | -6.9 | 0 | 0 | 14.4 | 14.7 | 14.6 | 14.6 | 15.3 | 13 | 21.8 | 12.9 | 4.1 | 268.4 | 14.7 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.8 | 13.9 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
157 | -37 | -6.9 | 0 | 0 | 14.4 | 14.7 | 14.6 | 14.6 | 15.3 | 13 | 21.8 | 12.9 | 3.7 | 258.5 | 14.7 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.8 | 13.9 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
158 | -36 | -6.9 | 0 | 0 | 14.4 | 14.7 | 14.6 | 14.6 | 15.3 | 13 | 21.8 | 12.9 | 3.8 | 257.9 | 15.9 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.8 | 13.9 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
159 | -35 | -6.9 | 0 | 0 | 14.4 | 14.7 | 14.6 | 14.6 | 15.3 | 13.1 | 21.8 | 12.9 | 3.6 | 260.4 | 16.3 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.8 | 13.9 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
160 | -34 | -6.9 | 0 | 0 | 14.4 | 14.8 | 14.6 | 14.5 | 15.3 | 13.1 | 21.8 | 12.9 | 4.1 | 274.4 | 16.8 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.8 | 13.9 | 14.5 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
161 | -33 | -6.9 | 0 | 0 | 14.4 | 14.8 | 14.5 | 14.5 | 15.3 | 13.1 | 21.8 | 12.9 | 5.1 | 275.2 | 18 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.8 | 13.9 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
162 | -32 | -6.9 | 0 | 0 | 14.4 | 14.8 | 14.6 | 14.5 | 15.3 | 13.1 | 21.8 | 12.9 | 4.7 | 262 | 20.4 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.9 | 13.9 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
163 | -31 | -6.9 | 0 | 0 | 14.4 | 14.8 | 14.5 | 14.5 | 15.4 | 13.1 | 21.7 | 12.9 | 5.5 | 264 | 22.4 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.9 | 13.9 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 16.9 | 16.6 | 16.1
164 | -30 | -6.9 | 0 | 0 | 14.4 | 14.8 | 14.6 | 14.6 | 15.4 | 13.1 | 21.7 | 12.9 | 5 | 262.4 | 20.3 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.9 | 13.9 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
165 | -29 | -6.9 | 0 | 0 | 14.4 | 14.8 | 14.6 | 14.6 | 15.4 | 13.1 | 21.7 | 12.9 | 5.2 | 266.1 | 19.2 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.9 | 13.9 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.1 | 15.2 | 17 | 16.6 | 16.1
166 | -28 | -6.9 | 0 | 0 | 14.4 | 14.8 | 14.6 | 14.6 | 15.4 | 13.1 | 21.7 | 12.9 | 6.5 | 264.9 | 19.5 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.9 | 13.9 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.1 | 15.1 | 17 | 16.6 | 16.1
167 | -27 | -6.9 | 0 | 0 | 14.4 | 14.8 | 14.5 | 14.6 | 15.4 | 13.1 | 21.7 | 12.9 | 6.5 | 263.7 | 19 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.9 | 13.9 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.1 | 15.1 | 17 | 16.6 | 16.1
168 | -26 | -6.9 | 0 | 0 | 14.4 | 14.7 | 14.6 | 14.6 | 15.4 | 13.1 | 21.7 | 12.9 | 5.5 | 260.6 | 17.6 | 13.7 | 13 | 13.1 | 14.2 | 14.9 | 14.3 | 13.9 | 13.9 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.1 | 15.1 | 16.9 | 16.6 | 16.1
169 | -25 | -6.9 | 0 | 0 | 14.4 | 14.7 | 14.6 | 14.6 | 15.4 | 13.1 | 21.7 | 12.9 | 5.7 | 258.5 | 16.9 | 13.7 | 13 | 13.1 | 14.2 | 14.9 | 14.3 | 13.9 | 13.9 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.1 | 15.1 | 16.9 | 16.6 | 16.1
170 | -24 | -6.9 | 0 | 0 | 14.4 | 14.7 | 14.6 | 14.6 | 15.4 | 13.1 | 21.7 | 12.9 | 5.3 | 262 | 17.3 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.9 | 13.9 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.1 | 15.1 | 17 | 16.6 | 16.1
171 | -23 | -6.9 | 0 | 0 | 14.4 | 14.7 | 14.6 | 14.6 | 15.4 | 13.1 | 21.7 | 12.9 | 3.9 | 264.1 | 15.8 | 13.7 | 13 | 13.1 | 14.2 | 14.9 | 14.3 | 13.9 | 13.9 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.1 | 15.1 | 17 | 16.6 | 16.1
172 | -22 | -6.9 | 0 | 0 | 14.4 | 14.7 | 14.6 | 14.6 | 15.4 | 13.1 | 21.7 | 13 | 4 | 245.1 | 15 | 13.7 | 13 | 13.1 | 14.2 | 14.9 | 14.3 | 13.9 | 13.9 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.1 | 15.1 | 17 | 16.6 | 16.1
173 | -21 | -6.9 | 0 | 0 | 14.5 | 14.7 | 14.6 | 14.6 | 15.4 | 13.1 | 21.7 | 12.9 | 3.4 | 265.2 | 13.5 | 13.7 | 13 | 13.1 | 14.2 | 14.9 | 14.3 | 13.9 | 13.8 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.1 | 15.1 | 17 | 16.6 | 16.1
174 | -20 | -6.9 | 0 | 0 | 14.5 | 14.7 | 14.6 | 14.6 | 15.4 | 13.1 | 21.7 | 12.9 | 3.2 | 250.8 | 11.7 | 13.7 | 13 | 13.1 | 14.2 | 14.9 | 14.3 | 13.9 | 13.9 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.1 | 15.1 | 16.9 | 16.6 | 16.1
175 | -19 | -6.9 | 0 | 0 | 14.5 | 14.7 | 14.6 | 14.6 | 15.3 | 13.1 | 21.8 | 12.9 | 2.9 | 247.1 | 12.2 | 13.7 | 13 | 13.1 | 14.2 | 14.9 | 14.3 | 13.9 | 13.9 | 14.5 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.1 | 15.1 | 17 | 16.6 | 16.1
176 | -18 | -6.9 | 0 | 0 | 14.5 | 14.7 | 14.6 | 14.6 | 15.3 | 13.1 | 21.7 | 13 | 3.7 | 257.2 | 12.6 | 13.7 | 13 | 13.1 | 14.2 | 14.9 | 14.3 | 13.9 | 13.9 | 14.5 | 15.2 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.1 | 15.1 | 17 | 16.6 | 16.1
177 | -17 | -6.9 | 0 | 0 | 14.5 | 14.7 | 14.7 | 14.6 | 15.4 | 13.1 | 21.7 | 13 | 4.3 | 265 | 11.9 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.9 | 13.9 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.1 | 15.2 | 17 | 16.6 | 16.1
178 | -16 | -6.9 | 0 | 0 | 14.5 | 14.7 | 14.7 | 14.6 | 15.3 | 13.1 | 21.7 | 13 | 4.7 | 267.6 | 14.2 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.9 | 13.8 | 14.5 | 15.2 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.1 | 15.1 | 16.9 | 16.6 | 16.1
179 | -15 | -6.9 | 0 | 0 | 14.5 | 14.7 | 14.7 | 14.7 | 15.3 | 13.1 | 21.7 | 12.9 | 4.7 | 262 | 15.6 | 13.7 | 13 | 13.1 | 14.2 | 14.9 | 14.3 | 13.9 | 13.8 | 14.6 | 15.2 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.1 | 15.1 | 17 | 16.6 | 16.1
180 | -14 | -6.9 | 0 | 0 | 14.5 | 14.7 | 14.7 | 14.7 | 15.3 | 13.1 | 21.7 | 12.9 | 4.2 | 259.7 | 16.2 | 13.7 | 13 | 13.1 | 14.2 | 14.9 | 14.3 | 13.9 | 13.8 | 14.5 | 15.2 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
181 | -13 | -6.9 | 0 | 0 | 14.4 | 14.7 | 14.7 | 14.7 | 15.3 | 13.1 | 21.7 | 13 | 4 | 251.7 | 15.3 | 13.7 | 13 | 13.1 | 14.2 | 14.9 | 14.3 | 13.9 | 13.8 | 14.5 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 16.9 | 16.6 | 16.1
182 | -12 | -6.9 | 0 | 0 | 14.4 | 14.7 | 14.7 | 14.7 | 15.3 | 13.1 | 21.7 | 12.9 | 4.1 | 261.6 | 16.7 | 13.7 | 13 | 13.1 | 14.2 | 14.9 | 14.3 | 13.8 | 13.8 | 14.5 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 16.9 | 16.6 | 16.1
183 | -11 | -6.9 | 0 | 0 | 14.4 | 14.7 | 14.7 | 14.7 | 15.3 | 13.1 | 21.7 | 12.9 | 3.6 | 253.7 | 16.8 | 13.7 | 13 | 13.1 | 14.2 | 14.9 | 14.3 | 13.8 | 13.8 | 14.5 | 15.2 | 15.5 | 15.4 | 16.7 | 15.3 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
184 | -10 | -6.9 | 0 | 0 | 14.4 | 14.7 | 14.7 | 14.7 | 15.3 | 13.1 | 21.7 | 12.9 | 3.4 | 264.1 | 16.1 | 13.7 | 13 | 13.1 | 14.2 | 14.9 | 14.3 | 13.8 | 13.9 | 14.5 | 15.2 | 15.5 | 15.4 | 16.7 | 15.3 | 15.1 | 15.2 | 15.1 | 16.9 | 16.6 | 16.1
185 | -9 | -6.9 | 0 | 0 | 14.4 | 14.7 | 14.7 | 14.7 | 15.3 | 13.1 | 21.7 | 12.9 | 3.4 | 259.7 | 16.3 | 13.7 | 13 | 13.1 | 14.2 | 14.9 | 14.3 | 13.8 | 13.8 | 14.5 | 15.2 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
186 | -8 | -6.9 | 0 | 0 | 14.4 | 14.7 | 14.7 | 14.6 | 15.3 | 13.1 | 21.7 | 12.9 | 3.8 | 255.6 | 17 | 13.7 | 13 | 13.1 | 14.2 | 14.9 | 14.3 | 13.8 | 13.9 | 14.5 | 15.2 | 15.5 | 15.4 | 16.7 | 15.3 | 15.1 | 15.2 | 15.1 | 16.9 | 16.6 | 16.1
187 | -7 | -6.9 | 0 | 0 | 14.4 | 14.7 | 14.7 | 14.6 | 15.3 | 13.1 | 21.7 | 12.9 | 3.8 | 252.7 | 15.8 | 13.7 | 13 | 13.1 | 14.2 | 14.9 | 14.3 | 13.8 | 13.9 | 14.5 | 15.2 | 15.5 | 15.4 | 16.7 | 15.3 | 15.1 | 15.2 | 15.2 | 17 | 16.6 | 16.1
188 | -6 | -6.9 | 0 | 0 | 14.4 | 14.7 | 14.7 | 14.6 | 15.3 | 13 | 21.8 | 12.9 | 3.5 | 256.6 | 16.1 | 13.7 | 13 | 13.1 | 14.2 | 14.9 | 14.3 | 13.8 | 13.9 | 14.6 | 15.2 | 15.5 | 15.4 | 16.7 | 15.3 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
189 | -5 | -6.9 | 0 | 0 | 14.4 | 14.7 | 14.7 | 14.6 | 15.3 | 13.1 | 21.7 | 12.9 | 2.9 | 252.2 | 16.7 | 13.7 | 13 | 13.1 | 14.2 | 14.9 | 14.3 | 13.8 | 13.8 | 14.5 | 15.2 | 15.5 | 15.4 | 16.7 | 15.3 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
190 | -4 | -6.9 | 0 | 0 | 14.3 | 14.7 | 14.7 | 14.6 | 15.3 | 13.1 | 21.7 | 12.9 | 2.9 | 247.4 | 16.3 | 13.7 | 13 | 13.1 | 14.2 | 14.9 | 14.3 | 13.8 | 13.9 | 14.5 | 15.2 | 15.5 | 15.4 | 16.7 | 15.3 | 15.1 | 15.2 | 15.1 | 16.9 | 16.6 | 16.1
191 | -3 | -6.9 | 0 | 0 | 14.3 | 14.7 | 14.7 | 14.6 | 15.3 | 13.1 | 21.7 | 12.9 | 2.8 | 246.1 | 14.9 | 13.7 | 13 | 13.1 | 14.2 | 14.9 | 14.3 | 13.8 | 13.9 | 14.5 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 16.9 | 16.6 | 16.1
192 | -2 | -6.9 | 0 | 0 | 14.3 | 14.7 | 14.7 | 14.6 | 15.3 | 13.1 | 21.7 | 12.9 | 3.3 | 251.6 | 13.5 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.8 | 13.9 | 14.6 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 16.9 | 16.6 | 16.1
193 | -1 | -6.8 | 0 | 0 | 14.3 | 14.7 | 14.6 | 14.6 | 15.3 | 13.1 | 21.7 | 12.9 | 3.1 | 268.2 | 12.4 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.8 | 13.9 | 14.5 | 15.2 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 16.9 | 16.6 | 16.1
194 | 0 | 127.7 | 51.08 | 59.7096 | 14.3 | 14.7 | 14.6 | 14.6 | 15.3 | 13.1 | 21.8 | 12.9 | 2.7 | 257.1 | 13 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.7 | 13.9 | 14.5 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 16.9 | 16.6 | 16.1
195 | 1 | 461.5 | 184.6 | 215.7868 | 14.3 | 14.7 | 14.6 | 14.6 | 15.3 | 13 | 21.8 | 12.9 | 1.9 | 269 | 12.5 | 13.7 | 13.1 | 13.1 | 14.2 | 14.9 | 14.3 | 13.7 | 13.9 | 14.5 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 16.9 | 16.6 | 16.1
196 | 2 | 604.6 | 241.84 | 282.697 | 14.3 | 14.7 | 14.6 | 14.6 | 15.3 | 13.1 | 21.8 | 12.9 | 1.9 | 266.3 | 12.1 | 13.7 | 13.1 | 13.2 | 14.2 | 14.9 | 14.3 | 13.7 | 13.9 | 14.5 | 15.3 | 15.5 | 15.4 | 16.7 | 15.4 | 15.1 | 15.2 | 15.1 | 16.9 | 16.6 | 16.1
197 | 3 | 628.9 | 251.56 | 294.0591 | 14.3 | 14.7 | 14.6 | 14.7 | 15.3 | 13 | 21.7 | 12.9 | 2.6 | 271.1 | 11.6 | 13.7 | 13.1 | 13.3 | 14.2 | 15 | 14.3 | 13.7 | 13.9 | 14.5 | 15.3 | 15.5 | 15.4 | 16.7 | 15.3 | 15.1 | 15.2 | 15.1 | 17 | 16.6 | 16.1
198 | 4 | 607.3 | 242.92 | 283.9595 | 14.3 | 14.7 | 14.6 | 14.8 | 15.3 | 13.1 | 21.7 | 12.9 | 4.1 | 256.8 | 10.9 | 13.7 | 15.6 | 19.2 | 14.2 | 15.7 | 14.3 | 13.8 | 15 | 14.6 | 15.4 | 15.5 | 15.4 | 16.7 | 15.3 | 15.2 | 15.2 | 15.1 | 17 | 16.6 | 16.1
199 | 5 | 583.7 | 233.48 | 272.9247 | 14.4 | 14.7 | 14.8 | 15 | 16.4 | 13.1 | 21.7 | 12.9 | 5 | 266.3 | 10 | 13.7 | 27.4 | 47.4 | 14.3 | 18.6 | 14.3 | 20.6 | 32.3 | 14.6 | 17.6 | 15.5 | 15.4 | 16.7 | 15.4 | 15.2 | 15.3 | 15.1 | 17.1 | 16.6 | 16.1
200 | 6 | 566.1 | 226.44 | 264.6953 | 14.5 | 14.7 | 15 | 15.2 | 28.3 | 13.1 | 21.7 | 12.9 | 4.7 | 248.1 | 9.2 | 13.7 | 60 | 100.9 | 14.6 | 23.8 | 14.3 | 36.7 | 63.4 | 14.6 | 21.4 | 15.5 | 15.4 | 16.8 | 15.3 | 15.6 | 15.7 | 15.1 | 17.2 | 16.6 | 16.1
201 | 7 | 559.8 | 223.92 | 261.7496 | 15 | 14.9 | 15.3 | 15.6 | 48.3 | 13.2 | 21.7 | 12.9 | 4.6 | 262.6 | 9.6 | 13.7 | 108.1 | 166.3 | 15.1 | 31.6 | 14.3 | 62.7 | 121.9 | 14.9 | 27.9 | 15.5 | 15.4 | 16.8 | 15.3 | 15.9 | 16.2 | 15.1 | 17.4 | 16.7 | 16.1
202 | 8 | 547.7 | 219.08 | 256.0919 | 15.9 | 15.3 | 15.6 | 16.1 | 73.4 | 13.3 | 21.7 | 12.9 | 4.5 | 247.2 | 10.9 | 13.7 | 150.8 | 210.6 | 15.6 | 36.8 | 14.3 | 92.9 | 168.8 | 15.4 | 34.1 | 15.5 | 15.4 | 16.8 | 15.3 | 16.1 | 16.4 | 15.1 | 17.5 | 16.8 | 16.1
203 | 9 | 535.6 | 214.24 | 250.4342 | 17.1 | 15.8 | 16.7 | 17.6 | 103.2 | 13.3 | 21.7 | 12.9 | 4.4 | 246.3 | 12.4 | 13.7 | 203 | 250.4 | 16.4 | 41.6 | 14.5 | 136.4 | 229 | 16.3 | 42.6 | 15.5 | 15.4 | 16.9 | 15.4 | 16.3 | 16.7 | 15.1 | 17.7 | 16.9 | 16.1
204 | 10 | 528.3 | 211.32 | 247.0209 | 18.6 | 16.8 | 18.9 | 19.8 | 139.2 | 13.4 | 21.7 | 12.9 | 4.6 | 251.1 | 12.6 | 13.8 | 257.6 | 289.3 | 17.2 | 47.3 | 14.7 | 185.7 | 289.8 | 17.6 | 54.6 | 15.5 | 15.4 | 17 | 15.3 | 17.1 | 17.1 | 15.1 | 18 | 17.1 | 16.1
205 | 11 | 523.7 | 209.48 | 244.8701 | 20.2 | 18.1 | 21.6 | 22 | 168.8 | 13.4 | 21.7 | 12.9 | 3.8 | 243 | 11.4 | 13.8 | 321.4 | 326.7 | 18.2 | 54.2 | 15.2 | 228.4 | 346.7 | 19.2 | 68.4 | 15.5 | 15.4 | 17.3 | 15.3 | 19.8 | 18 | 15.1 | 18.3 | 17.2 | 16.1
206 | 12 | 522.2 | 208.88 | 244.1687 | 22.5 | 19.6 | 25 | 25 | 189.2 | 13.5 | 21.7 | 12.9 | 3.1 | 243.7 | 11.1 | 13.9 | 384.5 | 388.6 | 19.3 | 63.1 | 15.9 | 282.8 | 414.1 | 20.9 | 81.9 | 15.5 | 15.4 | 17.4 | 15.3 | 27.6 | 19.9 | 15.1 | 18.5 | 17.4 | 16.1
207 | 13 | 522.2 | 208.88 | 244.1687 | 25.7 | 21.5 | 28.5 | 28.9 | 228.3 | 13.6 | 21.7 | 13 | 3.2 | 239.8 | 10.7 | 14.1 | 450.1 | 459.4 | 22.6 | 70.6 | 16.9 | 337 | 475.7 | 22.8 | 95.9 | 15.5 | 15.4 | 17.6 | 15.3 | 36.7 | 22.2 | 15.2 | 19 | 17.7 | 16.3
208 | 14 | 522.6 | 209.04 | 244.3557 | 29.6 | 23.9 | 33.1 | 35.3 | 307.1 | 13.6 | 21.8 | 13 | 4.1 | 232.5 | 8.6 | 14.3 | 507.5 | 504.4 | 27.4 | 82.1 | 18.1 | 397.4 | 539.5 | 25.4 | 114.8 | 15.5 | 15.4 | 17.8 | 15.3 | 48 | 24.5 | 15.2 | 19.5 | 18 | 16.5
209 | 15 | 523.6 | 209.44 | 244.8233 | 32.5 | 26.5 | 38.2 | 42.4 | 359.2 | 13.7 | 21.7 | 13 | 4.6 | 243.7 | 8.1 | 14.7 | 550.3 | 534.4 | 31.3 | 89.9 | 19.8 | 438.9 | 576.4 | 28.4 | 130.2 | 15.5 | 15.4 | 18.1 | 15.3 | 55.4 | 27.6 | 15.2 | 20.3 | 18.4 | 16.8
210 | 16 | 524.5 | 209.8 | 245.2441 | 35.7 | 30.1 | 43.8 | 48.7 | 390.3 | 13.7 | 21.7 | 13 | 4.5 | 237.6 | 7.9 | 15.3 | 598.4 | 577.2 | 35.9 | 96.6 | 21.7 | 481.1 | 615.6 | 31.3 | 147.5 | 15.5 | 15.4 | 18.4 | 15.4 | 63.4 | 30.7 | 15.2 | 20.9 | 18.7 | 17.1
211 | 17 | 525.9 | 210.36 | 245.8987 | 40.8 | 34.3 | 49.9 | 54.1 | 428.1 | 13.8 | 21.7 | 13 | 3.7 | 237.4 | 6.5 | 16.1 | 626.4 | 595.8 | 39.2 | 100.2 | 23.9 | 518.2 | 649.4 | 34.3 | 159.4 | 15.5 | 15.4 | 18.8 | 15.4 | 79 | 35.1 | 15.2 | 21.7 | 19 | 17.4
212 | 18 | 526.8 | 210.72 | 246.3195 | 46 | 39.1 | 56.1 | 58.4 | 436 | 13.8 | 21.7 | 13.1 | 3.3 | 221.8 | 6.8 | 17.1 | 652.3 | 625.1 | 43.4 | 107.9 | 26.5 | 541.4 | 679.3 | 37 | 170.7 | 15.5 | 15.4 | 19 | 15.4 | 86.3 | 39.4 | 15.2 | 22.6 | 19.3 | 17.7
213 | 19 | 527.3 | 210.92 | 246.5533 | 50.6 | 44.5 | 62.4 | 64.2 | 461.2 | 13.9 | 21.7 | 13.2 | 3.9 | 213.2 | 7.8 | 18.4 | 692.3 | 657.8 | 49.2 | 115.9 | 29.7 | 576.1 | 709.2 | 40.7 | 184.8 | 15.5 | 15.4 | 19.3 | 15.4 | 93.1 | 42.7 | 15.2 | 23.2 | 19.7 | 18.1
214 | 20 | 525.3 | 210.12 | 245.6182 | 56 | 48.9 | 67.6 | 71.2 | 498.2 | 13.9 | 21.7 | 13.3 | 4.2 | 246.2 | 6.4 | 19.8 | 722.8 | 686.6 | 52.7 | 123.8 | 33.4 | 601.8 | 734.7 | 43.8 | 199.9 | 15.5 | 15.5 | 19.8 | 15.4 | 102.7 | 46.2 | 15.3 | 23.8 | 20.1 | 18.4
215 | 21 | 515 | 206 | 240.8021 | 61.4 | 53.8 | 72.3 | 77.8 | 511.4 | 14 | 21.7 | 13.4 | 4.1 | 241 | 7 | 21.4 | 750.2 | 707.1 | 57.2 | 131.7 | 37.6 | 630.8 | 756.1 | 47.5 | 219.3 | 15.5 | 15.5 | 20.2 | 15.4 | 108.3 | 49.5 | 15.3 | 24.5 | 20.6 | 18.8
216 | 22 | 516.6 | 206.64 | 241.5503 | 67.4 | 59 | 77.5 | 84.9 | 519.4 | 14 | 21.7 | 13.5 | 4.5 | 212.2 | 7.6 | 23.1 | 771.1 | 718.7 | 59.6 | 137.8 | 42.1 | 648 | 774.1 | 50.7 | 235.4 | 15.5 | 15.5 | 20.4 | 15.4 | 113 | 53.7 | 15.3 | 25.3 | 21.1 | 19.1
217 | 23 | 510.3 | 204.12 | 238.6045 | 72.8 | 63.9 | 83.7 | 92.2 | 531.5 | 14 | 21.7 | 13.7 | 4.1 | 220.3 | 9.2 | 24.9 | 787.7 | 740.5 | 62.7 | 145.5 | 46.9 | 662.8 | 786.4 | 53.9 | 253.7 | 15.5 | 15.5 | 20.8 | 15.5 | 117.4 | 58 | 15.3 | 26 | 21.7 | 19.4
218 | 24 | 503.8 | 201.52 | 235.5653 | 77.9 | 69.1 | 90.7 | 99.7 | 537.5 | 14.1 | 21.7 | 14.1 | 4.2 | 227.4 | 11 | 26.9 | 789.4 | 747.8 | 64.1 | 150.4 | 51.8 | 669.4 | 788.4 | 56.7 | 263.3 | 15.5 | 15.6 | 21.1 | 15.5 | 121.8 | 61.6 | 15.4 | 26.8 | 22.3 | 19.6
219 | 25 | 498.3 | 199.32 | 232.9936 | 83.4 | 75.7 | 96.7 | 105.6 | 523.9 | 14.1 | 21.7 | 14.5 | 4.8 | 215.3 | 11.2 | 29 | 795.2 | 745.3 | 67.7 | 154.9 | 56.8 | 678.1 | 783.9 | 59.4 | 272.8 | 15.5 | 15.6 | 21.4 | 15.5 | 126.6 | 65.5 | 15.4 | 27.5 | 22.8 | 19.8
220 | 26 | 494.3 | 197.72 | 231.1233 | 89.6 | 82.3 | 101.6 | 111.5 | 500 | 14.2 | 21.7 | 15.2 | 5.1 | 231.4 | 11.4 | 31.2 | 798 | 734.5 | 70.3 | 160.5 | 61.8 | 677.1 | 780.1 | 61.8 | 283.5 | 15.5 | 15.6 | 21.8 | 15.5 | 130.8 | 69.1 | 15.5 | 28.6 | 23.3 | 20.1
221 | 27 | 490.1 | 196.04 | 229.1595 | 95.3 | 86.3 | 107.1 | 117.2 | 490.6 | 14.2 | 21.7 | 16 | 4.8 | 207.7 | 11.4 | 33.6 | 786 | 718.3 | 72.5 | 161.2 | 66.9 | 675.6 | 771.3 | 64.1 | 287.6 | 15.5 | 15.7 | 21.9 | 15.5 | 136 | 73 | 15.5 | 29.5 | 23.9 | 20.4
222 | 28 | 487.7 | 195.08 | 228.0373 | 100.8 | 89.7 | 112.7 | 122.2 | 473.4 | 14.2 | 21.7 | 16.9 | 5.2 | 204.9 | 10.7 | 36 | 793.2 | 723 | 76.2 | 165 | 71.9 | 671.6 | 770.9 | 66.3 | 293.8 | 15.5 | 15.7 | 22.3 | 15.6 | 138.8 | 77.2 | 15.5 | 30.3 | 24.4 | 20.6
223 | 29 | 486.1 | 194.44 | 227.2892 | 105.4 | 94.8 | 117.7 | 126.9 | 473.3 | 14.2 | 21.7 | 17.8 | 5.1 | 199 | 9.4 | 38.6 | 785.4 | 724.2 | 78.9 | 169 | 77 | 665.3 | 768.2 | 68.4 | 299.9 | 15.5 | 15.7 | 22.6 | 15.6 | 141.6 | 80.8 | 15.6 | 31 | 24.7 | 20.9
224 | 30 | 484.8 | 193.92 | 226.6813 | 110 | 99.7 | 122.3 | 131.1 | 469 | 14.2 | 21.7 | 18.7 | 5.3 | 223.7 | 9.1 | 41.2 | 801.7 | 732.8 | 83.5 | 174 | 82 | 671.3 | 782.3 | 71.2 | 313.5 | 15.5 | 15.8 | 22.7 | 15.6 | 145.3 | 84.1 | 15.6 | 31.9 | 25.1 | 21.1
225 | 31 | 482.5 | 193 | 225.6059 | 114.1 | 104.6 | 127.4 | 134.2 | 472.2 | 14.3 | 21.7 | 19.4 | 4.5 | 230.8 | 7.7 | 43.9 | 819.7 | 749.5 | 89.4 | 180.4 | 87 | 680 | 798.3 | 74.6 | 329.9 | 15.5 | 15.8 | 23 | 15.7 | 148.1 | 87.6 | 15.6 | 32.7 | 25.6 | 21.3
226 | 32 | 482.6 | 193.04 | 225.6526 | 118.2 | 108.8 | 132.1 | 137.6 | 481.7 | 14.3 | 21.7 | 20 | 4.6 | 216.3 | 7.4 | 46.6 | 835.9 | 758 | 94.5 | 190.8 | 92.1 | 688 | 803.1 | 78.4 | 345.2 | 15.5 | 15.9 | 23.4 | 15.7 | 151.1 | 90.8 | 15.7 | 33.5 | 26.3 | 21.6
227 | 33 | 481.7 | 192.68 | 225.2318 | 122.5 | 113.7 | 135.9 | 142.2 | 484 | 14.3 | 21.7 | 20.4 | 4.1 | 195.6 | 7.6 | 49.4 | 847.1 | 760.9 | 97.9 | 199.1 | 97 | 687.1 | 795.9 | 81.8 | 358.1 | 15.5 | 16 | 23.6 | 15.8 | 153.3 | 94 | 15.7 | 34.5 | 27 | 21.9
228 | 34 | 481.4 | 192.56 | 225.0915 | 126 | 117.9 | 139.8 | 146.2 | 473.5 | 14.3 | 21.7 | 20.9 | 3.8 | 242.8 | 8.5 | 52.2 | 855.6 | 759.8 | 101.7 | 209.4 | 101.9 | 680.8 | 789.6 | 84.6 | 370.5 | 15.5 | 16 | 23.9 | 15.8 | 155 | 97 | 15.8 | 35.6 | 27.8 | 22.1
229 | 35 | 480.4 | 192.16 | 224.624 | 129.1 | 122.7 | 144.1 | 148.5 | 459.6 | 14.3 | 21.7 | 21.3 | 4.3 | 221.7 | 10.9 | 55.1 | 853.5 | 756 | 103.5 | 213.9 | 107.3 | 668.8 | 784.2 | 86.5 | 375.1 | 15.5 | 16.1 | 24.2 | 15.9 | 157.3 | 100.2 | 15.8 | 36.6 | 28.6 | 22.3
230 | 36 | 478.3 | 191.32 | 223.6421 | 132.2 | 126.9 | 148.1 | 150.6 | 447.5 | 14.3 | 21.8 | 21.7 | 4.3 | 239.9 | 11.5 | 58 | 844.8 | 760.2 | 105.8 | 219.1 | 112.9 | 656.1 | 774.6 | 88.4 | 378.1 | 15.5 | 16.2 | 24.5 | 15.9 | 158.9 | 103.5 | 15.9 | 37.4 | 29.3 | 22.6
231 | 37 | 477.8 | 191.12 | 223.4083 | 135.8 | 130.2 | 152.1 | 152.2 | 444.2 | 14.5 | 21.7 | 22 | 4.3 | 241.8 | 12 | 61.1 | 849.2 | 767.8 | 108.7 | 228.9 | 117.9 | 654.9 | 776.2 | 90.7 | 387.7 | 15.5 | 16.3 | 25 | 15.9 | 160.3 | 106.7 | 15.9 | 38.4 | 29.8 | 22.8
232 | 38 | 477.5 | 191 | 223.268 | 138.3 | 133.2 | 154.8 | 154.4 | 429.6 | 14.7 | 21.8 | 22.4 | 4.1 | 242.9 | 11.9 | 64.2 | 849.8 | 766.6 | 110.6 | 236.9 | 122.5 | 643.6 | 762.9 | 92.1 | 392.6 | 15.5 | 16.3 | 25 | 16 | 161.6 | 110 | 15.9 | 39.1 | 30.3 | 23.1
233 | 39 | 476.5 | 190.6 | 222.8004 | 140.4 | 135.7 | 157.3 | 156 | 418 | 14.9 | 21.7 | 22.7 | 4 | 243.2 | 11.1 | 67.3 | 843.7 | 753 | 112.4 | 240 | 126.6 | 631.5 | 760.4 | 93.4 | 396.9 | 15.5 | 16.4 | 25.1 | 16 | 162.7 | 112.8 | 16 | 39.8 | 30.9 | 23.3
234 | 40 | 476.1 | 190.44 | 222.6134 | 142.8 | 137.4 | 159.2 | 157.6 | 404.4 | 15 | 21.7 | 23.1 | 3.6 | 238.4 | 11.2 | 70.5 | 832 | 740.6 | 114.4 | 244 | 130.6 | 620.7 | 744.4 | 94.5 | 399.6 | 15.5 | 16.5 | 25.3 | 16.1 | 163.6 | 115.4 | 16 | 40.7 | 31.4 | 23.5
235 | 41 | 476.2 | 190.48 | 222.6601 | 145.8 | 138.3 | 161.2 | 158.9 | 387.7 | 15.1 | 21.7 | 23.5 | 4 | 246.3 | 11.4 | 74 | 815.8 | 720.4 | 115.4 | 247.1 | 134.5 | 607.4 | 729 | 95.3 | 400.3 | 15.5 | 16.6 | 25.3 | 16.1 | 164.4 | 118.1 | 16.1 | 41.2 | 31.8 | 23.7
236 | 42 | 473.6 | 189.44 | 221.4444 | 148.9 | 139.2 | 162.9 | 158.9 | 383.2 | 15.1 | 21.7 | 23.9 | 4.1 | 254.7 | 10.4 | 77 | 813.4 | 719.8 | 116.9 | 251 | 138.2 | 601 | 735.2 | 96.3 | 402.8 | 15.5 | 16.6 | 25.5 | 16.2 | 165.5 | 120.4 | 16.1 | 41.9 | 32.2 | 23.9
237 | 43 | 473.8 | 189.52 | 221.538 | 151.8 | 140.7 | 164.2 | 158.2 | 381.2 | 15.1 | 21.7 | 24.3 | 4.7 | 262.8 | 8.3 | 80.1 | 819.7 | 711.5 | 120 | 255.1 | 141.4 | 601.1 | 733.5 | 97.6 | 409.5 | 15.5 | 16.7 | 26 | 16.3 | 166.3 | 122.6 | 16.2 | 42.7 | 32.6 | 24.1
238 | 44 | 473.9 | 189.56 | 221.5847 | 154 | 141.7 | 165.1 | 159.3 | 374.4 | 15.2 | 21.7 | 24.9 | 4.3 | 248.2 | 6.6 | 83.3 | 823.6 | 719.4 | 122.5 | 259.4 | 144.4 | 593.5 | 729.9 | 99 | 413.1 | 15.5 | 16.8 | 26.3 | 16.3 | 167 | 125.5 | 16.3 | 43.3 | 33.1 | 24.3
239 | 45 | 474.1 | 189.64 | 221.6782 | 155.2 | 143.6 | 166.1 | 161.8 | 371.2 | 15.3 | 21.7 | 25.4 | 4.1 | 239.9 | 6.2 | 86.5 | 835.3 | 734.9 | 125.5 | 265.7 | 147.2 | 598.3 | 740.4 | 100.7 | 420.3 | 15.5 | 16.9 | 26.4 | 16.4 | 168.1 | 127.6 | 16.3 | 44 | 33.6 | 24.5
240 | 46 | 472.1 | 188.84 | 220.7431 | 156.8 | 145.2 | 167.2 | 163.3 | 371.7 | 15.3 | 21.7 | 25.8 | 4.1 | 254.1 | 6.9 | 89.5 | 849.3 | 737.3 | 128.4 | 275.6 | 149.8 | 607.8 | 744 | 103 | 432 | 15.5 | 17 | 26.6 | 16.4 | 169.2 | 129.5 | 16.4 | 44.9 | 34.1 | 24.7
241 | 47 | 470.9 | 188.36 | 220.182 | 157.7 | 146.6 | 168.1 | 164.5 | 370.8 | 15.4 | 21.7 | 26.2 | 4.4 | 250.2 | 10.4 | 93.1 | 860.6 | 742.7 | 130.9 | 281.8 | 152.2 | 620.4 | 755.2 | 105.7 | 441.7 | 15.5 | 17.1 | 27.1 | 16.5 | 170.2 | 131.4 | 16.4 | 45.6 | 34.8 | 24.9
242 | 48 | 470.8 | 188.32 | 220.1352 | 158.4 | 148.4 | 168.6 | 164.9 | 378 | 15.4 | 21.7 | 26.4 | 3.9 | 259.7 | 11.7 | 96.8 | 873.9 | 744.7 | 134 | 290.9 | 154.4 | 628.4 | 764.7 | 108.3 | 453.4 | 15.5 | 17.2 | 27.6 | 16.5 | 170.9 | 133.6 | 16.5 | 46.1 | 35.4 | 25.2
243 | 49 | 471.4 | 188.56 | 220.4158 | 159.1 | 150.5 | 170.2 | 165.5 | 380.7 | 15.5 | 21.7 | 26.6 | 3.6 | 253.7 | 12.2 | 99.5 | 881.6 | 743.9 | 136.3 | 302 | 156.4 | 624.6 | 762.2 | 110.4 | 459.2 | 15.5 | 17.3 | 27.6 | 16.6 | 171.3 | 136 | 16.6 | 46.8 | 36.1 | 25.4
244 | 50 | 471 | 188.4 | 220.2287 | 159.9 | 152.6 | 171.6 | 165.9 | 381.8 | 15.5 | 21.7 | 26.8 | 3.9 | 258.3 | 11.8 | 102.4 | 887.4 | 745.6 | 139.1 | 310.6 | 158.3 | 622.6 | 757.1 | 112.3 | 467.9 | 15.5 | 17.4 | 27.8 | 16.7 | 171.9 | 137.7 | 16.7 | 47.6 | 36.8 | 25.6
245 | 51 | 470.1 | 188.04 | 219.8079 | 161 | 155 | 172.9 | 166.9 | 384.8 | 15.4 | 21.7 | 27.1 | 4.1 | 254.8 | 11.5 | 105.5 | 895 | 749.8 | 142.2 | 318.8 | 159.9 | 626 | 763.4 | 114.2 | 475.7 | 15.6 | 17.5 | 28 | 16.7 | 172.3 | 139.9 | 16.7 | 48.4 | 37.5 | 25.9
246 | 52 | 470.3 | 188.12 | 219.9014 | 162.6 | 156.8 | 174.1 | 167.5 | 386.1 | 15.4 | 21.7 | 27.2 | 3.9 | 258.9 | 9.9 | 108.6 | 899.8 | 763.9 | 145.5 | 327.3 | 161.4 | 627.6 | 759.6 | 116.1 | 482.4 | 15.6 | 17.6 | 28.3 | 16.8 | 173.4 | 142.1 | 16.8 | 49.3 | 38.3 | 26.1
247 | 53 | 469.3 | 187.72 | 219.4339 | 164.4 | 158 | 175.2 | 167.3 | 380.5 | 15.4 | 21.7 | 27.4 | 4 | 259.6 | 10.1 | 111.8 | 895 | 765.6 | 147.7 | 334.3 | 162.8 | 621.7 | 764.2 | 117.3 | 485.1 | 15.6 | 17.7 | 28.5 | 16.9 | 174.7 | 144.4 | 16.9 | 49.8 | 39 | 26.3
248 | 54 | 468.7 | 187.48 | 219.1533 | 165.9 | 159.6 | 176.1 | 167.7 | 382.7 | 15.3 | 21.7 | 27.7 | 4.1 | 255.1 | 9.8 | 114.9 | 895.2 | 770.9 | 150 | 339.5 | 164.1 | 622.2 | 762.1 | 118.6 | 490.1 | 15.6 | 17.8 | 28.4 | 16.9 | 176.8 | 145.8 | 17 | 50.7 | 39.7 | 26.5
249 | 55 | 469.6 | 187.84 | 219.5741 | 166.4 | 160.1 | 176.7 | 168.7 | 379.9 | 15.3 | 21.7 | 27.9 | 4.1 | 270.7 | 9.6 | 118 | 894.8 | 774.9 | 153.2 | 346.1 | 165.1 | 626.3 | 765.2 | 120.2 | 497.3 | 15.6 | 17.9 | 28.8 | 17 | 177.7 | 147 | 17.1 | 51.3 | 40.2 | 26.8
250 | 56 | 468.8 | 187.52 | 219.2001 | 167.4 | 160.9 | 176.3 | 169.5 | 378.6 | 15.3 | 21.7 | 28.2 | 4.2 | 259.8 | 10.6 | 121.1 | 891.8 | 789.9 | 155.3 | 353.2 | 166 | 621.4 | 768.6 | 121.4 | 499.6 | 15.6 | 18 | 29.3 | 17.1 | 178.5 | 148.5 | 17.2 | 52 | 40.8 | 27
251 | 57 | 469.1 | 187.64 | 219.3403 | 167.8 | 162.2 | 176.8 | 169.6 | 395.3 | 15.2 | 21.7 | 28.4 | 3.6 | 251.9 | 12.8 | 124.1 | 884.2 | 794.3 | 158.5 | 356.8 | 166.7 | 622.7 | 772.8 | 122.4 | 500.6 | 15.6 | 18.1 | 29.4 | 17.1 | 179 | 150.1 | 17.2 | 52.4 | 41.4 | 27.2
252 | 58 | 468.6 | 187.44 | 219.1066 | 168.1 | 163.4 | 177.3 | 170.1 | 395.6 | 15.2 | 21.7 | 28.7 | 3.9 | 254.1 | 12.7 | 127.6 | 879.9 | 787 | 161.6 | 359.5 | 167.4 | 624.3 | 772.6 | 123.2 | 503.3 | 15.6 | 18.2 | 29.7 | 17.2 | 179.7 | 151.2 | 17.3 | 53 | 41.9 | 27.4
253 | 59 | 468.2 | 187.28 | 218.9195 | 168.5 | 164 | 177.6 | 170.9 | 397.3 | 15.3 | 21.7 | 28.9 | 4.3 | 250.5 | 12.9 | 131.5 | 866.1 | 773 | 163 | 361.8 | 168.1 | 613.7 | 761.9 | 123.8 | 503.3 | 15.6 | 18.3 | 30 | 17.3 | 179.9 | 152.2 | 17.5 | 53.6 | 42.4 | 27.7
254 | 60 | 467.4 | 186.96 | 218.5455 | 169.6 | 165.2 | 177.7 | 171.8 | 405.6 | 15.3 | 21.6 | 29.2 | 3.9 | 248.7 | 12 | 135.8 | 862 | 769.8 | 164.9 | 364.6 | 168.9 | 614.4 | 768.2 | 124.8 | 506.1 | 15.6 | 18.4 | 30.3 | 17.4 | 180.4 | 153.5 | 17.5 | 54.2 | 42.9 | 27.9
255 | 61 | 468.6 | 187.44 | 219.1066 | 170.7 | 166.5 | 177.8 | 172.1 | 405 | 15.4 | 21.6 | 29.5 | 3.8 | 250 | 9.9 | 140.3 | 848.7 | 764.9 | 166.4 | 369.7 | 169.9 | 613.8 | 770.3 | 125.6 | 507.6 | 15.6 | 18.5 | 30.4 | 17.4 | 180.9 | 154.6 | 17.7 | 54.8 | 43.4 | 28.1
256 | 62 | 469.1 | 187.64 | 219.3403 | 171.3 | 167.6 | 178.2 | 172.7 | 397.5 | 15.5 | 21.6 | 29.7 | 5.5 | 258.1 | 8.4 | 145 | 849.1 | 765.8 | 168.8 | 375.8 | 170.9 | 612.4 | 764.1 | 126.5 | 509.7 | 15.6 | 18.6 | 30.9 | 17.5 | 181.5 | 156.3 | 17.8 | 55.5 | 43.9 | 28.3
257 | 63 | 467.5 | 187 | 218.5922 | 172.2 | 167.3 | 178.6 | 173.5 | 391.9 | 15.5 | 21.6 | 30 | 5.9 | 244.4 | 8.6 | 149.2 | 850.9 | 761.2 | 170.9 | 384.8 | 171.8 | 608.4 | 759.1 | 127.4 | 514 | 15.7 | 18.7 | 31.4 | 17.6 | 182.3 | 157.9 | 17.8 | 56.2 | 44.4 | 28.6
258 | 64 | 467.7 | 187.08 | 218.6857 | 172.8 | 166.4 | 178.9 | 174.1 | 388.5 | 15.6 | 21.6 | 30.3 | 6.4 | 252.9 | 9.6 | 152.8 | 851.3 | 760.5 | 173.4 | 387 | 172.6 | 608 | 756.2 | 128.4 | 515.8 | 15.7 | 18.8 | 31.5 | 17.7 | 183.9 | 158.8 | 18 | 56.7 | 45 | 28.8
259 | 65 | 469 | 187.6 | 219.2936 | 173 | 166.2 | 180.3 | 174.6 | 387.7 | 15.7 | 21.6 | 30.5 | 6.2 | 236.3 | 10.3 | 156.1 | 863.8 | 761.7 | 177.2 | 389.5 | 173.4 | 611.6 | 760.7 | 129.8 | 520.1 | 15.7 | 19 | 31.9 | 17.7 | 184.6 | 159.7 | 18.1 | 57.2 | 45.6 | 29.1
260 | 66 | 468.5 | 187.4 | 219.0598 | 172.8 | 167.2 | 181.4 | 174.7 | 382.4 | 15.8 | 21.6 | 30.8 | 5.4 | 234.7 | 10.5 | 159.4 | 873.5 | 762 | 180.3 | 396.4 | 174.1 | 612 | 757.7 | 131.3 | 525 | 15.7 | 19.1 | 32 | 17.8 | 184.9 | 160.4 | 18.2 | 57.8 | 46.1 | 29.4
261 | 67 | 468.7 | 187.48 | 219.1533 | 173.9 | 168.1 | 182.2 | 173.6 | 379.5 | 15.8 | 21.6 | 31 | 4.8 | 245.7 | 11 | 162.7 | 881.1 | 771.2 | 183.9 | 402 | 174.6 | 613.4 | 761 | 133 | 531.4 | 15.7 | 19.2 | 32.2 | 17.9 | 184.9 | 161.5 | 18.3 | 58.3 | 46.7 | 29.6
262 | 68 | 468 | 187.2 | 218.826 | 174.7 | 168.3 | 182.5 | 172.8 | 380.7 | 15.9 | 21.6 | 31.2 | 4.9 | 242.7 | 14.3 | 165.8 | 888.9 | 763.6 | 188.1 | 406.6 | 175.1 | 622.2 | 766.2 | 134.9 | 538.9 | 15.7 | 19.3 | 32.4 | 18 | 185.4 | 162.7 | 18.4 | 58.9 | 47.4 | 29.8
263 | 69 | 468.4 | 187.36 | 219.013 | 175.2 | 169.9 | 182.9 | 173.4 | 386.5 | 15.9 | 21.6 | 31.5 | 3.3 | 249.8 | 16 | 168.5 | 892.4 | 756 | 190.4 | 410.4 | 175.6 | 628.2 | 766.4 | 136.9 | 542.7 | 15.7 | 19.4 | 32.7 | 18.1 | 186.8 | 163.8 | 18.5 | 59.6 | 48.2 | 30
264 | 70 | 468 | 187.2 | 218.826 | 176.1 | 170.7 | 183.2 | 174.6 | 387.9 | 15.9 | 21.6 | 31.6 | 4.7 | 237.9 | 15.4 | 170.8 | 897.7 | 756.1 | 192.6 | 416.7 | 176.1 | 634.6 | 775.5 | 138.7 | 549.9 | 15.7 | 19.6 | 32.7 | 18.1 | 187.5 | 164.6 | 18.7 | 60.3 | 48.9 | 30.3
265 | 71 | 468 | 187.2 | 218.826 | 176.7 | 171.8 | 183.7 | 176.4 | 389.5 | 16 | 21.6 | 31.7 | 4.7 | 228.1 | 13.5 | 172.9 | 905 | 763.6 | 195.6 | 422.7 | 176.7 | 632.6 | 778.6 | 140.4 | 555.7 | 15.7 | 19.7 | 33.1 | 18.2 | 187.7 | 165.2 | 18.8 | 60.7 | 49.5 | 30.5
266 | 72 | 470.7 | 188.28 | 220.0885 | 177 | 173.9 | 184 | 177.2 | 397.4 | 16.1 | 21.6 | 31.8 | 4.2 | 247.2 | 12.1 | 174.9 | 911.8 | 768.7 | 198.3 | 428.7 | 177.4 | 638.6 | 784.9 | 142.3 | 561.3 | 15.7 | 19.8 | 33.5 | 18.3 | 188.2 | 166.3 | 18.9 | 61.4 | 50.3 | 30.7
267 | 73 | 471.2 | 188.48 | 220.3223 | 177.7 | 175 | 183.6 | 176.5 | 399.3 | 16 | 21.6 | 31.9 | 4.2 | 250.7 | 12 | 176.9 | 912.4 | 775.2 | 200.1 | 436 | 178.1 | 645.2 | 787.1 | 144.1 | 568.2 | 15.8 | 20 | 33.6 | 18.4 | 188.4 | 167.5 | 19 | 62.2 | 51.1 | 30.9
268 | 74 | 469.3 | 187.72 | 219.4339 | 178.4 | 176.1 | 182.8 | 176.5 | 401.2 | 16 | 21.6 | 32.1 | 3.8 | 264.7 | 13.2 | 178.9 | 914.9 | 780 | 202 | 443.8 | 179 | 650.8 | 793.2 | 146 | 574.4 | 15.8 | 20.1 | 34 | 18.5 | 189 | 168.5 | 19.2 | 62.6 | 51.9 | 31.2
269 | 75 | 468.4 | 187.36 | 219.013 | 178.5 | 176.4 | 182 | 176.9 | 399.1 | 15.9 | 21.6 | 32.2 | 4.4 | 271.7 | 12.4 | 181.1 | 913.8 | 781.7 | 205.1 | 447.9 | 180 | 655.4 | 795.3 | 148.4 | 580.7 | 15.8 | 20.2 | 34.4 | 18.6 | 189.3 | 169.7 | 19.3 | 63.4 | 52.7 | 31.4
270 | 76 | 467.5 | 187 | 218.5922 | 178.7 | 176.3 | 182.6 | 176.8 | 406.6 | 15.9 | 21.6 | 32.4 | 4.4 | 247.5 | 11.6 | 183.6 | 910 | 794.7 | 207.5 | 449.8 | 181 | 658.4 | 797.1 | 151 | 583.1 | 15.8 | 20.4 | 34.9 | 18.7 | 189.7 | 170.7 | 19.4 | 63.9 | 53.4 | 31.6
271 | 77 | 468.9 | 187.56 | 219.2468 | 179.4 | 176.6 | 183.4 | 177.3 | 419.2 | 16 | 21.6 | 32.5 | 5 | 254.3 | 12.9 | 186 | 902.5 | 797.7 | 208.2 | 452.9 | 182.3 | 648 | 791.9 | 152.8 | 582.2 | 15.8 | 20.5 | 35 | 18.7 | 190.3 | 171 | 19.5 | 64.3 | 54.2 | 31.8
272 | 78 | 469 | 187.6 | 219.2936 | 180.6 | 177.3 | 183.9 | 177.4 | 420.9 | 16 | 21.5 | 32.6 | 5.6 | 266.8 | 12.2 | 188.3 | 896.2 | 793.6 | 209.2 | 454.3 | 183.6 | 642.5 | 790.8 | 153.9 | 582.8 | 15.8 | 20.7 | 35.2 | 18.8 | 190.9 | 171.3 | 19.6 | 64.7 | 54.8 | 32.1
273 | 79 | 468.4 | 187.36 | 219.013 | 181.3 | 177.5 | 184.9 | 178.1 | 414.4 | 16.2 | 21.5 | 32.8 | 5.2 | 257.6 | 13.2 | 190.4 | 899.1 | 791 | 210.5 | 457.8 | 184.9 | 638 | 789.4 | 154.9 | 585.5 | 15.8 | 20.8 | 35.4 | 18.9 | 191.6 | 171.7 | 19.8 | 65 | 55.3 | 32.3
274 | 80 | 467.9 | 187.16 | 218.7793 | 181.4 | 178.2 | 185.3 | 178.4 | 402.9 | 16.2 | 21.5 | 33 | 5.9 | 264.1 | 17 | 192 | 902.3 | 791.3 | 212.2 | 460.2 | 186.3 | 636.7 | 786.2 | 155.9 | 589.4 | 15.8 | 21 | 35.7 | 19 | 192.4 | 172.1 | 19.9 | 65.5 | 56 | 32.5
275 | 81 | 467.9 | 187.16 | 218.7793 | 181.3 | 178.2 | 184.8 | 178.5 | 401.8 | 16.3 | 21.5 | 33.1 | 6.4 | 247.7 | 19 | 193.5 | 904.4 | 795.9 | 214.2 | 463.8 | 187.8 | 640.5 | 786.6 | 157.2 | 593.9 | 15.9 | 21.1 | 35.9 | 19.1 | 193.6 | 172.9 | 20.1 | 66 | 56.7 | 32.8
276 | 82 | 469 | 187.6 | 219.2936 | 181.3 | 178.2 | 184 | 179 | 402.9 | 16.4 | 21.5 | 33.2 | 5.1 | 259.2 | 18.6 | 195.4 | 906.4 | 789.8 | 215.2 | 464.6 | 189.5 | 638 | 782.8 | 158.3 | 595 | 15.9 | 21.3 | 36.3 | 19.2 | 193.9 | 173.5 | 20.2 | 66.5 | 57.3 | 33
277 | 83 | 468.6 | 187.44 | 219.1066 | 180.8 | 178.1 | 183.9 | 180 | 401.5 | 16.5 | 21.5 | 33.3 | 7.8 | 238.3 | 16.4 | 197.4 | 906.8 | 790 | 216.3 | 465.6 | 191.3 | 632 | 780 | 158.9 | 593.2 | 15.9 | 21.4 | 36.5 | 19.3 | 194.7 | 174.1 | 20.3 | 67.1 | 57.9 | 33.3
278 | 84 | 467.9 | 187.16 | 218.7793 | 181 | 177.3 | 184.7 | 180.7 | 401.6 | 16.6 | 21.5 | 33.5 | 9.4 | 247.8 | 15.8 | 200 | 900.6 | 786.2 | 218 | 468.1 | 193 | 632.1 | 770.2 | 159.7 | 594.3 | 15.9 | 21.6 | 36.7 | 19.4 | 195 | 174.6 | 20.5 | 67.7 | 58.4 | 33.5
279 | 85 | 468.1 | 187.24 | 218.8728 | 181.1 | 176.4 | 184.3 | 181.4 | 399.5 | 16.6 | 21.5 | 33.6 | 7.9 | 252.2 | 18.4 | 202.7 | 904.3 | 789.4 | 218.9 | 470.7 | 194.6 | 639.3 | 763 | 161.1 | 600.3 | 15.9 | 21.7 | 37.1 | 19.5 | 195.4 | 174.9 | 20.6 | 68.1 | 58.9 | 33.8
280 | 86 | 468 | 187.2 | 218.826 | 181.3 | 177.1 | 184.8 | 181.9 | 406.9 | 16.7 | 21.5 | 33.7 | 9.3 | 244.2 | 21.1 | 205 | 904.7 | 795.1 | 219.7 | 474.3 | 196.4 | 643.2 | 771.6 | 162.1 | 602.7 | 15.9 | 21.9 | 37.3 | 19.6 | 196.5 | 175.5 | 20.8 | 68.6 | 59.6 | 34
281 | 87 | 468 | 187.2 | 218.826 | 180.5 | 177 | 185.4 | 181.9 | 425 | 16.7 | 21.5 | 33.9 | 9.2 | 265.5 | 19.5 | 207.1 | 896.4 | 783.7 | 220 | 474.7 | 198.2 | 637.6 | 767.6 | 162.6 | 602.2 | 16 | 22 | 37.8 | 19.7 | 196.9 | 176.1 | 20.9 | 69.2 | 60.2 | 34.3
282 | 88 | 467.8 | 187.12 | 218.7325 | 180.6 | 177.1 | 185.5 | 182 | 435 | 16.7 | 21.5 | 34.1 | 8.2 | 264.3 | 16.5 | 208.6 | 884.5 | 770.8 | 220.3 | 473.8 | 200.9 | 629.7 | 754.4 | 162.8 | 599.5 | 16 | 22.2 | 38.1 | 19.8 | 196.8 | 176.6 | 21.1 | 69.6 | 60.8 | 34.6
283 | 89 | 467.5 | 187 | 218.5922 | 181.4 | 177.5 | 186.2 | 181.5 | 432.3 | 16.7 | 21.5 | 34.2 | 8.1 | 250.9 | 17 | 210 | 876.9 | 772.1 | 220.6 | 474 | 203.9 | 623.4 | 755.7 | 163.2 | 598.7 | 16 | 22.3 | 38.4 | 19.9 | 196.9 | 177.2 | 21.3 | 70.1 | 61.3 | 34.8
284 | 90 | 467.6 | 187.04 | 218.639 | 182.9 | 177.8 | 187 | 182.5 | 421.4 | 16.7 | 21.5 | 34.2 | 6.9 | 256.9 | 18.7 | 211.5 | 874.5 | 758.8 | 220.8 | 474.3 | 207.1 | 615.2 | 749.4 | 163.5 | 596.8 | 16 | 22.5 | 38.8 | 20 | 197.1 | 177.5 | 21.4 | 70.5 | 61.8 | 35
285 | 91 | 466.9 | 186.76 | 218.3117 | 183.8 | 177.3 | 188.6 | 183.8 | 417.7 | 16.7 | 21.5 | 34.3 | 6.7 | 246.1 | 18.5 | 213.4 | 865.2 | 748 | 221.3 | 472.1 | 210.2 | 612.4 | 746.6 | 163.8 | 596 | 16 | 22.7 | 39.2 | 20.1 | 198 | 178.1 | 21.6 | 71.1 | 62.3 | 35.3
286 | 92 | 467.3 | 186.92 | 218.4987 | 184 | 177.2 | 190.5 | 183.6 | 408.7 | 16.8 | 21.5 | 34.4 | 8.1 | 247.2 | 18.9 | 215.2 | 854.8 | 748.2 | 222.1 | 471.1 | 212.9 | 601.8 | 738.1 | 164 | 593.3 | 16 | 22.8 | 39.5 | 20.2 | 199.4 | 178.4 | 21.7 | 71.6 | 62.8 | 35.5
287 | 93 | 466.4 | 186.56 | 218.0779 | 184.4 | 177 | 190.7 | 184.2 | 417.3 | 16.8 | 21.5 | 34.4 | 6.3 | 249.1 | 22 | 216.4 | 853.1 | 748.7 | 223.1 | 472.3 | 215.5 | 607.4 | 747.4 | 164.5 | 594.6 | 16 | 23 | 39.7 | 20.3 | 201.3 | 178.9 | 21.8 | 72.1 | 63.2 | 35.8
288 | 94 | 467.5 | 187 | 218.5922 | 184.5 | 176.9 | 191.2 | 186.1 | 423.6 | 16.8 | 21.5 | 34.3 | 6 | 245.7 | 22.1 | 217.1 | 839.5 | 730.9 | 223.7 | 470.9 | 218 | 600 | 727.2 | 164.9 | 591.3 | 16.1 | 23.2 | 39.9 | 20.4 | 202 | 179.6 | 22 | 72.7 | 63.8 | 36.1
289 | 95 | 467.7 | 187.08 | 218.6857 | 185 | 177.7 | 193 | 187.5 | 415.8 | 16.9 | 21.5 | 34.3 | 7.7 | 248.2 | 19 | 217.9 | 843.4 | 739.9 | 224.9 | 475.4 | 220.4 | 594 | 723.3 | 165 | 590.2 | 16.1 | 23.4 | 39.9 | 20.5 | 204.9 | 180.4 | 22.2 | 73.1 | 64.3 | 36.4
290 | 96 | 467.9 | 187.16 | 218.7793 | 185.5 | 177.2 | 193.7 | 187.5 | 411.9 | 16.9 | 21.5 | 34.4 | 8.5 | 244.7 | 17.7 | 218.6 | 851.3 | 757.4 | 226.9 | 480.9 | 223.3 | 597.9 | 733.9 | 165.5 | 593.7 | 16.1 | 23.5 | 40.1 | 20.6 | 205.1 | 181.3 | 22.4 | 73.8 | 64.8 | 36.8
291 | 97 | 467.7 | 187.08 | 218.6857 | 186 | 176.8 | 193.7 | 187.9 | 414.3 | 17 | 21.5 | 34.5 | 6.1 | 241.5 | 17.6 | 219.1 | 849.4 | 756.1 | 228.2 | 478.3 | 226.3 | 604.5 | 740.8 | 166.3 | 595.4 | 16.1 | 23.7 | 40.3 | 20.7 | 206.3 | 181.9 | 22.5 | 74 | 65.3 | 37
292 | 98 | 467.7 | 187.08 | 218.6857 | 186.4 | 177.5 | 193.2 | 188.5 | 429 | 17.1 | 21.5 | 34.6 | 4 | 235.6 | 16.3 | 219.7 | 850.1 | 740.7 | 229.8 | 476.4 | 229.9 | 604.5 | 739.3 | 166.7 | 593 | 16.1 | 23.9 | 40.7 | 20.8 | 206.6 | 182.6 | 22.6 | 74.7 | 65.7 | 37.3
293 | 99 | 467.6 | 187.04 | 218.639 | 188 | 178.3 | 192.4 | 189.1 | 430.3 | 17.1 | 21.5 | 34.8 | 3.8 | 245.6 | 14.9 | 220.6 | 842 | 730.6 | 231.8 | 475.3 | 240.6 | 599.2 | 727.9 | 167.1 | 590.9 | 16.2 | 24.1 | 41 | 20.9 | 206.9 | 183.3 | 22.9 | 75.2 | 66.2 | 37.5
294 | 100 | 467.6 | 187.04 | 218.639 | 189.5 | 179.1 | 192.7 | 189.6 | 430.4 | 17.1 | 21.5 | 35 | 3 | 225.1 | 13.9 | 221.4 | 849.3 | 735.5 | 234.2 | 475.8 | 250.2 | 601.8 | 734.6 | 167.5 | 591.4 | 16.2 | 24.2 | 41.4 | 21 | 207 | 184.3 | 23 | 75.8 | 66.7 | 37.8
295 | 101 | 467.2 | 186.88 | 218.452 | 190.6 | 180.1 | 193.9 | 189.6 | 434.4 | 17.1 | 21.4 | 35.1 | 3.8 | 237.8 | 13.7 | 222.1 | 847.8 | 728.9 | 237 | 474.5 | 258.3 | 600.5 | 736.4 | 167.9 | 591 | 16.2 | 24.4 | 41.6 | 21.1 | 207.2 | 184.8 | 23.1 | 76.1 | 67.1 | 38
296 | 102 | 467.8 | 187.12 | 218.7325 | 191.2 | 181.2 | 194.6 | 190.1 | 429.5 | 17.2 | 21.4 | 35.3 | 4.9 | 218.9 | 14.3 | 223.1 | 845 | 729.1 | 240.5 | 474.1 | 265.7 | 592.1 | 731.1 | 167.9 | 587.9 | 16.2 | 24.6 | 41.9 | 21.2 | 207.6 | 185.1 | 23.4 | 76.5 | 67.6 | 38.3
297 | 103 | 467 | 186.8 | 218.3584 | 191.5 | 182 | 194.7 | 190.5 | 425.4 | 17.2 | 21.4 | 35.5 | 5.9 | 243.8 | 12.8 | 224.2 | 848.5 | 750.8 | 244.8 | 476.4 | 273 | 591.6 | 737.5 | 168.1 | 589.2 | 16.2 | 24.8 | 42.1 | 21.3 | 208.2 | 185.4 | 23.5 | 77 | 68.1 | 38.6
298 | 104 | 467 | 186.8 | 218.3584 | 191.2 | 181.2 | 194.8 | 190.9 | 423 | 17.2 | 21.4 | 35.6 | 6.9 | 245.7 | 13 | 226.4 | 857.6 | 752.8 | 248.2 | 480.2 | 280.6 | 594.1 | 746.7 | 168.6 | 592.2 | 16.3 | 25 | 42.3 | 21.4 | 208.1 | 185.6 | 23.7 | 77.5 | 68.5 | 38.8
299 | 105 | 467.3 | 186.92 | 218.4987 | 190.7 | 180.4 | 194.2 | 190.5 | 415.4 | 17.2 | 21.4 | 35.8 | 5.9 | 230.7 | 12.6 | 229.4 | 867.9 | 761.4 | 250.7 | 483.9 | 288.6 | 598.9 | 744.3 | 169.6 | 594.6 | 16.3 | 25.2 | 42.6 | 21.6 | 208.2 | 186.3 | 23.8 | 78.3 | 69.1 | 39.1
300 | 106 | 467.6 | 187.04 | 218.639 | 191.2 | 180.8 | 194.2 | 190.2 | 413.8 | 17.2 | 21.4 | 35.9 | 6.7 | 244.3 | 11 | 232.1 | 863.7 | 756.2 | 251.6 | 484.9 | 296.2 | 600.3 | 749.1 | 170.3 | 595.9 | 16.3 | 25.4 | 42.8 | 21.7 | 207.8 | 186.8 | 24 | 78.8 | 69.7 | 39.3
301 | 107 | 467.4 | 186.96 | 218.5455 | 191.5 | 180.3 | 194.6 | 189.6 | 419 | 17.2 | 21.4 | 35.9 | 6.1 | 246.7 | 11.3 | 233.6 | 861.7 | 753.2 | 250.9 | 484.6 | 303 | 598.2 | 738.2 | 170.8 | 593.5 | 16.4 | 25.5 | 43.2 | 21.8 | 207.7 | 187.1 | 24.2 | 79.4 | 70.2 | 39.6
302 | 108 | 467.4 | 186.96 | 218.5455 | 192.9 | 179.7 | 194.9 | 189 | 420.2 | 17.2 | 21.4 | 36.1 | 6.5 | 243.8 | 11.3 | 234.4 | 859.4 | 759.2 | 250.3 | 486.9 | 309 | 595.1 | 732 | 171.1 | 593 | 16.4 | 25.7 | 43.5 | 21.9 | 207.6 | 187.6 | 24.3 | 79.9 | 70.7 | 39.8
303 | 109 | 467.2 | 186.88 | 218.452 | 194.1 | 179.8 | 195.7 | 188.6 | 419.4 | 17.2 | 21.4 | 36.2 | 5.5 | 239.4 | 12 | 234.8 | 859.5 | 751.1 | 249.4 | 487.6 | 314.6 | 591.5 | 726.9 | 171.7 | 592.2 | 16.4 | 25.9 | 43.7 | 22 | 207.7 | 187.8 | 24.6 | 80.3 | 71.2 | 40
304 | 110 | 467.1 | 186.84 | 218.4052 | 194.9 | 180.6 | 195.8 | 190 | 416.7 | 17.3 | 21.4 | 36.4 | 5.9 | 230.8 | 11.3 | 234.8 | 862.6 | 734.9 | 248.7 | 485.9 | 319.4 | 591.5 | 726 | 172.4 | 592.6 | 16.4 | 26.1 | 43.9 | 22.1 | 208.2 | 187.9 | 24.7 | 80.6 | 71.7 | 40.3
305 | 111 | 466.7 | 186.68 | 218.2182 | 194.2 | 181.4 | 196.3 | 191 | 414.1 | 17.4 | 21.4 | 36.6 | 7.1 | 236 | 14 | 234.8 | 860.5 | 734.4 | 248.2 | 486 | 323.8 | 593.2 | 728.2 | 173 | 592.5 | 16.4 | 26.2 | 44.3 | 22.2 | 209.1 | 188.4 | 24.9 | 81 | 72.1 | 40.5
306 | 112 | 466.6 | 186.64 | 218.1714 | 194.5 | 181.7 | 196.6 | 191.1 | 404.3 | 17.5 | 21.4 | 36.7 | 5.8 | 248 | 13.1 | 234.7 | 864 | 746 | 248 | 487.2 | 327.9 | 589.7 | 727.6 | 173.6 | 592.3 | 16.5 | 26.4 | 44.6 | 22.3 | 210.7 | 189.1 | 25.1 | 81.6 | 72.6 | 40.8
307 | 113 | 467.2 | 186.88 | 218.452 | 195.1 | 181.8 | 197.6 | 191 | 401.9 | 17.5 | 21.4 | 36.8 | 4.7 | 236.7 | 11.9 | 234.8 | 869.1 | 756.6 | 248.1 | 489.6 | 332.3 | 593.8 | 738.3 | 174.4 | 594.7 | 16.5 | 26.6 | 44.9 | 22.5 | 211 | 190 | 25.3 | 82.1 | 73.1 | 41.1
308 | 114 | 466.8 | 186.72 | 218.2649 | 195.6 | 180.8 | 198 | 190.4 | 406.3 | 17.6 | 21.4 | 36.9 | 3.8 | 247.8 | 10.2 | 235 | 869.2 | 764 | 248.3 | 491.7 | 337.4 | 595 | 742.6 | 175.2 | 595 | 16.5 | 26.8 | 45.2 | 22.6 | 211.3 | 190.4 | 25.4 | 82.6 | 73.6 | 41.3
309 | 115 | 466.9 | 186.76 | 218.3117 | 195.7 | 180.7 | 198.1 | 190.5 | 401.3 | 17.6 | 21.4 | 36.9 | 3.2 | 244.8 | 8.3 | 235.3 | 875.1 | 766.2 | 248.8 | 493.7 | 342.1 | 587.8 | 740.3 | 175.9 | 594.7 | 16.5 | 27 | 45.4 | 22.7 | 211.2 | 191.1 | 25.6 | 83.3 | 74.1 | 41.6
310 | 116 | 466.7 | 186.68 | 218.2182 | 196.2 | 180.8 | 197.7 | 189.6 | 396.7 | 17.7 | 21.4 | 37 | 3.4 | 220.6 | 10.1 | 235.9 | 881.3 | 741.7 | 249 | 494 | 346.2 | 587.8 | 734.3 | 176.8 | 596.1 | 16.6 | 27.1 | 45.5 | 22.8 | 211.1 | 191.5 | 25.8 | 83.7 | 74.7 | 41.8
311 | 117 | 466.9 | 186.76 | 218.3117 | 196.6 | 180 | 197.1 | 189.7 | 388.6 | 17.7 | 21.4 | 37.2 | 3.7 | 217.6 | 10.2 | 236.4 | 882.9 | 712.6 | 248.3 | 490.5 | 348.6 | 581.4 | 713.1 | 177.3 | 593.8 | 16.6 | 27.3 | 45.6 | 22.9 | 211 | 191.7 | 26 | 84.2 | 75.2 | 42
312 | 118 | 466.4 | 186.56 | 218.0779 | 196.8 | 179.8 | 197.4 | 190 | 382.5 | 17.8 | 21.4 | 37.4 | 4.5 | 224.5 | 9 | 236.7 | 882.4 | 699 | 247.4 | 490.4 | 350.5 | 584.8 | 708.4 | 178.3 | 596 | 16.6 | 27.5 | 46 | 23.1 | 211 | 192.1 | 26.2 | 84.6 | 75.7 | 42.3
313 | 119 | 466.7 | 186.68 | 218.2182 | 196.9 | 178.7 | 197.9 | 189.3 | 382.9 | 17.8 | 21.4 | 37.5 | 4.3 | 201.7 | 8 | 237.4 | 879.3 | 721.7 | 246.5 | 491.2 | 353.1 | 590.8 | 726.6 | 179.5 | 596.2 | 16.6 | 27.7 | 46.3 | 23.2 | 210.7 | 192.1 | 26.4 | 85.2 | 76.2 | 42.5
314 | 120 | 466.9 | 186.76 | 218.3117 | 196.6 | 177.9 | 198.4 | 188.3 | 403.3 | 17.9 | 21.4 | 37.6 | 4.4 | 209.8 | 7.3 | 238.2 | 887.2 | 731.6 | 245.6 | 493.6 | 357.3 | 593.4 | 734.7 | 180.4 | 598.8 | 16.7 | 27.9 | 46.7 | 23.3 | 210.4 | 192 | 26.6 | 85.7 | 76.6 | 42.7
315 | 121 | 463.8 | 185.52 | 216.8622 | 197.3 | 178 | 198.9 | 189 | 413.9 | 18 | 21.3 | 37.8 | 4.2 | 230.9 | 8 | 239.2 | 889.3 | 735.4 | 244.8 | 495.9 | 362 | 591.3 | 733.7 | 181.1 | 597.3 | 16.7 | 28 | 47 | 23.4 | 210.2 | 191.7 | 26.7 | 85.9 | 77.2 | 42.9
316 | 122 | 463.4 | 185.36 | 216.6752 | 198.9 | 178.3 | 199.5 | 190.6 | 409.3 | 18.1 | 21.3 | 37.9 | 4.3 | 202.4 | 9.5 | 240.3 | 897 | 731.5 | 244.2 | 498.4 | 365.4 | 591 | 731.4 | 181.9 | 599.5 | 16.7 | 28.2 | 47.1 | 23.5 | 210 | 191.6 | 26.9 | 86.3 | 77.7 | 43.1
317 | 123 | 465.4 | 186.16 | 217.6103 | 198.9 | 177.1 | 199.7 | 190.6 | 409.2 | 18.1 | 21.3 | 37.9 | 4 | 195.5 | 9.6 | 241.5 | 898.1 | 727.9 | 243.7 | 500.1 | 368.2 | 602.9 | 732 | 183.3 | 605.2 | 16.8 | 28.4 | 47.2 | 23.7 | 210.1 | 192 | 27.1 | 86.8 | 78.2 | 43.3
318 | 124 | 465.8 | 186.32 | 217.7973 | 198.7 | 177.4 | 199.6 | 190.2 | 411.4 | 18.1 | 21.3 | 38 | 4.5 | 203 | 7.9 | 242.8 | 893 | 722.3 | 243.1 | 501 | 370.7 | 598.1 | 728 | 184.3 | 604.3 | 16.8 | 28.6 | 47.6 | 23.8 | 209.9 | 192.8 | 27.3 | 87.2 | 78.9 | 43.6
319 | 125 | 464.7 | 185.88 | 217.283 | 199.6 | 177.5 | 200.1 | 190.4 | 405 | 18.2 | 21.3 | 38 | 3.9 | 230.9 | 7.5 | 244 | 886.2 | 715.2 | 242.6 | 500.9 | 373.5 | 589.6 | 719.3 | 184.5 | 602.6 | 16.8 | 28.8 | 48 | 23.9 | 209.9 | 193 | 27.5 | 87.7 | 79.4 | 43.8
320 | 126 | 463.4 | 185.36 | 216.6752 | 200.5 | 177.8 | 200.6 | 190 | 403.7 | 18.2 | 21.3 | 38 | 3 | 237.8 | 6.6 | 245.2 | 884.5 | 713.5 | 242.1 | 501.1 | 375.9 | 587.7 | 714.6 | 185 | 602.9 | 16.8 | 29 | 48.4 | 24 | 210.1 | 193.1 | 27.7 | 88 | 79.9 | 44
321 | 127 | 464.9 | 185.96 | 217.3765 | 200.8 | 177.9 | 201.2 | 189.4 | 399.4 | 18.3 | 21.3 | 38 | 3.3 | 228.2 | 6.1 | 246.5 | 888.1 | 707.1 | 241.8 | 500.4 | 378.1 | 592.9 | 713.4 | 185.7 | 605.1 | 16.9 | 29.2 | 48.3 | 24.2 | 210.2 | 193.5 | 27.9 | 88.3 | 80.4 | 44.3
322 | 128 | 467 | 186.8 | 218.3584 | 201.1 | 178.5 | 201.7 | 189.8 | 396.9 | 18.3 | 21.3 | 38.1 | 3.6 | 227.8 | 6.8 | 247.6 | 881.3 | 714.9 | 241.5 | 499.9 | 380.8 | 585.5 | 705.3 | 186.1 | 601.5 | 16.9 | 29.3 | 48.7 | 24.3 | 210.5 | 194.3 | 28.1 | 88.9 | 80.8 | 44.5
323 | 129 | 467.1 | 186.84 | 218.4052 | 201.3 | 179.3 | 202.2 | 190 | 397.5 | 18.4 | 21.3 | 38.3 | 3.6 | 225.8 | 8 | 248.8 | 883.4 | 711.2 | 241.2 | 500.6 | 385.2 | 587 | 711.8 | 186.5 | 602.3 | 16.9 | 29.5 | 48.9 | 24.4 | 211 | 194.8 | 28.3 | 89.4 | 81.3 | 44.7
324 | 130 | 466.5 | 186.6 | 218.1246 | 201.9 | 179.1 | 203.2 | 190.7 | 394.1 | 18.5 | 21.3 | 38.4 | 3.9 | 228.7 | 8.3 | 249.9 | 888.9 | 717.7 | 241 | 502.8 | 389.1 | 592 | 713.2 | 187.3 | 604.9 | 17 | 29.7 | 49.2 | 24.6 | 211.9 | 195.3 | 28.5 | 89.7 | 81.8 | 45
325 | 131 | 465.6 | 186.24 | 217.7038 | 201.8 | 178.7 | 204.1 | 192.1 | 389.3 | 18.5 | 21.3 | 38.5 | 4.1 | 254.5 | 9.3 | 251.1 | 897.2 | 713.3 | 240.8 | 504.6 | 392.4 | 597.4 | 714.1 | 188.2 | 609.4 | 17 | 29.9 | 49.5 | 24.7 | 212.8 | 195.7 | 28.6 | 90.2 | 82.4 | 45.3
326 | 132 | 466.6 | 186.64 | 218.1714 | 201.7 | 178.7 | 204.3 | 193 | 382.3 | 18.5 | 21.3 | 38.6 | 4.5 | 232.6 | 9.2 | 252.4 | 896.6 | 698.1 | 240.7 | 502.7 | 395.1 | 593.2 | 712 | 188.9 | 607.2 | 17 | 30 | 50.3 | 24.8 | 213.4 | 196.3 | 28.9 | 90.7 | 83 | 45.5
327 | 133 | 467.1 | 186.84 | 218.4052 | 202.4 | 178.2 | 204.7 | 193.2 | 377.5 | 18.4 | 21.3 | 38.7 | 4.9 | 233.5 | 8.7 | 253.6 | 893.8 | 701.5 | 240.6 | 502.2 | 398.1 | 590.7 | 710.2 | 189.3 | 605.3 | 17.1 | 30.2 | 50.5 | 24.9 | 214.1 | 196.6 | 29.1 | 91.2 | 83.6 | 45.8
328 | 134 | 464.4 | 185.76 | 217.1427 | 202.7 | 177.2 | 205.1 | 193.3 | 382.1 | 18.4 | 21.3 | 38.8 | 5.3 | 243.7 | 9.5 | 254.8 | 891.9 | 723 | 240.5 | 506.7 | 402.3 | 595 | 721.5 | 189.9 | 607.3 | 17.1 | 30.4 | 50.4 | 25.1 | 214.5 | 196.8 | 29.3 | 91.6 | 84 | 46
329 | 135 | 465 | 186 | 217.4233 | 202.3 | 175.6 | 205.1 | 193.4 | 395.3 | 18.5 | 21.3 | 38.9 | 5.1 | 249.4 | 9.9 | 256 | 893.6 | 727.9 | 240.4 | 509.8 | 408 | 606.2 | 733.1 | 190.9 | 611.4 | 17.1 | 30.6 | 50.8 | 25.2 | 214.8 | 197.1 | 29.5 | 92.1 | 84.5 | 46.3
330 | 136 | 464.9 | 185.96 | 217.3765 | 201.4 | 176.6 | 205.3 | 193.9 | 415 | 18.6 | 21.3 | 39 | 4.6 | 250.3 | 9.3 | 257 | 894.9 | 734.1 | 240.4 | 513.3 | 414.2 | 603.7 | 736.2 | 191.6 | 610.8 | 17.1 | 30.8 | 51 | 25.3 | 215.3 | 197.8 | 29.7 | 92.5 | 85 | 46.5
331 | 137 | 465.3 | 186.12 | 217.5636 | 201.2 | 177.4 | 205.5 | 194.4 | 414.2 | 18.7 | 21.3 | 39 | 4.3 | 234.6 | 8.2 | 257.9 | 892 | 733.8 | 240.4 | 515.9 | 418.6 | 600.5 | 731.9 | 192.1 | 610.7 | 17.2 | 31 | 51.1 | 25.5 | 215.6 | 198.2 | 29.9 | 93 | 85.5 | 46.7
332 | 138 | 464.8 | 185.92 | 217.3298 | 201.6 | 178.6 | 205.9 | 195.1 | 410.2 | 18.7 | 21.3 | 39.1 | 4 | 233.9 | 7.6 | 258.7 | 892.4 | 737.8 | 240.5 | 517.2 | 422.9 | 608.3 | 733.5 | 193.2 | 613.3 | 17.2 | 31.2 | 51.4 | 25.6 | 215.6 | 198.4 | 30.1 | 93.4 | 86 | 46.9
333 | 139 | 465.2 | 186.08 | 217.5168 | 201.8 | 178.2 | 205.8 | 195.1 | 410.9 | 18.8 | 21.3 | 39.2 | 4.1 | 221.1 | 7 | 259.4 | 894.7 | 737.2 | 240.6 | 516.1 | 428.5 | 603.8 | 729.8 | 193.9 | 612 | 17.2 | 31.3 | 51.8 | 25.7 | 215.7 | 198.6 | 30.3 | 93.7 | 86.5 | 47.1
334 | 140 | 465.7 | 186.28 | 217.7506 | 202.7 | 177 | 206.1 | 195.5 | 410.6 | 18.8 | 21.3 | 39.3 | 3.8 | 247.8 | 6.8 | 259.9 | 893.1 | 746.1 | 240.8 | 517.1 | 434.5 | 600.9 | 728.3 | 194.3 | 611.4 | 17.3 | 31.5 | 52 | 25.9 | 216 | 198.7 | 30.5 | 94.1 | 87.1 | 47.4
335 | 141 | 465.9 | 186.36 | 217.8441 | 203.6 | 176.6 | 206.2 | 196.5 | 414 | 18.9 | 21.3 | 39.4 | 4.4 | 232.7 | 6 | 260.4 | 889.6 | 759.3 | 241 | 517.9 | 441.6 | 596.5 | 727.1 | 194.8 | 609.6 | 17.3 | 31.7 | 52.2 | 26 | 216.5 | 199.1 | 30.7 | 94.6 | 87.5 | 47.6
336 | 142 | 465.9 | 186.36 | 217.8441 | 204.5 | 177.5 | 206.2 | 196.3 | 408 | 18.9 | 21.3 | 39.7 | 4.5 | 200.8 | 5.7 | 261 | 889 | 765.1 | 241.3 | 518.3 | 448.8 | 591 | 727.2 | 195.3 | 608.6 | 17.3 | 31.8 | 52.2 | 26.1 | 216.7 | 199.2 | 30.9 | 95.1 | 88 | 47.8
337 | 143 | 465.3 | 186.12 | 217.5636 | 204.9 | 178 | 205.7 | 197.4 | 405.7 | 19 | 21.3 | 39.9 | 4.9 | 251.4 | 6.3 | 261.4 | 885.5 | 769.7 | 241.7 | 518.4 | 456.2 | 587.7 | 727.6 | 195.6 | 607.1 | 17.4 | 32 | 52.6 | 26.3 | 216.7 | 199.6 | 31.1 | 95.5 | 88.5 | 48.1
338 | 144 | 465.9 | 186.36 | 217.8441 | 204.7 | 178 | 205.3 | 198.1 | 408.5 | 19.1 | 21.3 | 40.1 | 4.9 | 225.4 | 6.1 | 261.8 | 890.4 | 771.3 | 242.2 | 520.1 | 464.3 | 593.8 | 735.9 | 196.3 | 608.2 | 17.4 | 32.2 | 52.9 | 26.4 | 217.4 | 200.1 | 31.3 | 96.1 | 89 | 48.3
339 | 145 | 467.4 | 186.96 | 218.5455 | 204.3 | 178.8 | 205.3 | 199.4 | 414.8 | 19.2 | 21.2 | 40.3 | 4.6 | 252.6 | 6.5 | 262.2 | 895.9 | 780.5 | 242.7 | 524.1 | 471.7 | 600.4 | 742.2 | 197.5 | 613.2 | 17.4 | 32.4 | 53.4 | 26.6 | 218.2 | 200.5 | 31.5 | 96.6 | 89.4 | 48.6
340 | 146 | 467.8 | 187.12 | 218.7325 | 204.2 | 179.8 | 205.3 | 200.8 | 418.9 | 19.2 | 21.2 | 40.5 | 3.9 | 240.3 | 7.2 | 262.7 | 897.5 | 773.9 | 243.3 | 525.4 | 479 | 606.7 | 745 | 198.7 | 615 | 17.5 | 32.6 | 53.8 | 26.7 | 219 | 201 | 31.7 | 97 | 90 | 48.8
341 | 147 | 467.1 | 186.84 | 218.4052 | 204.4 | 180 | 205.6 | 201.3 | 421.1 | 19.3 | 21.2 | 40.7 | 3.7 | 244.2 | 7.8 | 263.2 | 897.7 | 782.2 | 244 | 527.8 | 485.4 | 619.7 | 747.5 | 200.2 | 619 | 17.5 | 32.7 | 53.9 | 26.8 | 219.2 | 201.9 | 31.9 | 97.7 | 90.6 | 49.1
342 | 148 | 466.5 | 186.6 | 218.1246 | 204.3 | 180.2 | 206.2 | 202.5 | 426.3 | 19.3 | 21.2 | 41 | 4.3 | 249.7 | 9.7 | 263.7 | 897.5 | 787.9 | 244.7 | 530.4 | 490.9 | 624.1 | 748.1 | 201.5 | 622.9 | 17.6 | 32.9 | 54.1 | 27 | 220.3 | 202.5 | 32.1 | 98.2 | 91.2 | 49.4
343 | 149 | 466.8 | 186.72 | 218.2649 | 204.6 | 180.7 | 206.8 | 202.9 | 426.9 | 19.4 | 21.2 | 41.2 | 5.3 | 241.4 | 10.3 | 264.1 | 901.8 | 793 | 245.5 | 531.3 | 495.9 | 626.5 | 752 | 202.9 | 623.1 | 17.6 | 33.1 | 54.6 | 27.1 | 220.8 | 202.7 | 32.3 | 98.6 | 91.8 | 49.7
344 | 150 | 466.4 | 186.56 | 218.0779 | 205.3 | 181.7 | 207.2 | 203.4 | 442.2 | 19.4 | 21.2 | 41.2 | 5.3 | 240.9 | 9.9 | 264.7 | 893.9 | 791.2 | 246.2 | 533.2 | 502.4 | 632.7 | 759.2 | 204.4 | 625.3 | 17.6 | 33.3 | 55 | 27.3 | 221.1 | 202.9 | 32.5 | 99 | 92.3 | 50
345 | 151 | 466.7 | 186.68 | 218.2182 | 206.1 | 182.5 | 207.5 | 203.4 | 454.7 | 19.4 | 21.2 | 41.2 | 4.6 | 243.4 | 8.7 | 265.2 | 882.9 | 783.7 | 247 | 534 | 508 | 624.1 | 755.9 | 205.6 | 623.7 | 17.7 | 33.5 | 55.1 | 27.4 | 221.5 | 203.2 | 32.8 | 99.4 | 92.9 | 50.2
346 | 152 | 465.9 | 186.36 | 217.8441 | 206.9 | 182.8 | 207.4 | 203.6 | 453.1 | 19.5 | 21.2 | 41.2 | 3.8 | 253.4 | 7.8 | 265.7 | 881 | 794.9 | 247.9 | 537.4 | 511.8 | 627.4 | 758.9 | 206.8 | 626 | 17.7 | 33.7 | 55.5 | 27.5 | 221.4 | 203.4 | 33 | 99.8 | 93.5 | 50.5
347 | 153 | 466.6 | 186.64 | 218.1714 | 207 | 183.6 | 208 | 203.5 | 457.6 | 19.5 | 21.2 | 41.2 | 3.6 | 252.7 | 7.8 | 266.2 | 885.9 | 798.2 | 248.8 | 543.6 | 514.7 | 630.4 | 758.9 | 207.9 | 630 | 17.7 | 33.9 | 55.8 | 27.7 | 221.1 | 203.8 | 33.2 | 100.3 | 94 | 50.7
348 | 154 | 465.5 | 186.2 | 217.6571 | 207.7 | 184.1 | 207.5 | 202.3 | 453.2 | 19.5 | 21.2 | 41.2 | 3.4 | 275.1 | 7.6 | 266.6 | 890.4 | 809.1 | 249.8 | 547 | 515.8 | 638 | 760.3 | 209 | 633.9 | 17.8 | 34.1 | 56 | 27.8 | 220.9 | 204.3 | 33.4 | 100.9 | 94.5 | 51
349 | 155 | 466.3 | 186.52 | 218.0311 | 207.6 | 184.7 | 207.1 | 200.9 | 451.4 | 19.6 | 21.2 | 41.3 | 3.2 | 266.1 | 8.7 | 267 | 896.2 | 812.3 | 250.8 | 551.7 | 518 | 641.5 | 765 | 210.1 | 636.5 | 17.8 | 34.3 | 56.3 | 28 | 220.9 | 204.5 | 33.6 | 101.4 | 95.2 | 51.2
350 | 156 | 466.3 | 186.52 | 218.0311 | 207.9 | 185.1 | 207.1 | 200.9 | 446.4 | 19.6 | 21.2 | 41.5 | 3.2 | 259.7 | 9.2 | 267.5 | 899.6 | 809.2 | 251.9 | 556 | 522.4 | 637.7 | 767.2 | 211 | 637.6 | 17.9 | 34.5 | 56.7 | 28.1 | 220.6 | 204.4 | 33.8 | 101.8 | 95.8 | 51.4
351 | 157 | 466.2 | 186.48 | 217.9844 | 208.5 | 184.4 | 206.5 | 201.3 | 451.2 | 19.7 | 21.2 | 41.7 | 3 | 243.5 | 9.5 | 268.1 | 904.3 | 810 | 253 | 561.7 | 525.9 | 634.9 | 766.8 | 212 | 639.3 | 17.9 | 34.7 | 57 | 28.2 | 220.4 | 204.5 | 34 | 102.2 | 96.5 | 51.6
352 | 158 | 466.5 | 186.6 | 218.1246 | 208.8 | 184.4 | 206 | 201.9 | 456 | 19.7 | 21.2 | 41.9 | 3.5 | 239 | 8.9 | 268.8 | 901.9 | 820.3 | 254.1 | 568.1 | 528.2 | 646.5 | 770.7 | 213.2 | 642.6 | 17.9 | 34.9 | 57.3 | 28.4 | 220.7 | 204.5 | 34.2 | 102.7 | 97.1 | 51.8
353 | 159 | 466.9 | 186.76 | 218.3117 | 208.7 | 186.2 | 205.7 | 202.2 | 475.2 | 19.7 | 21.2 | 42 | 3.8 | 247.3 | 8.1 | 269.5 | 901.7 | 828.2 | 255.2 | 571 | 532.9 | 649.9 | 773.2 | 214.4 | 644.5 | 18 | 35 | 57.9 | 28.5 | 221.2 | 204.7 | 34.5 | 103 | 97.9 | 52.1
354 | 160 | 465.3 | 186.12 | 217.5636 | 209.6 | 188.6 | 205.7 | 202.5 | 486.7 | 19.8 | 21.2 | 42.2 | 3.8 | 233 | 7 | 270.3 | 888.4 | 825.4 | 256.4 | 571.4 | 538.3 | 646.7 | 772.3 | 215.5 | 643.7 | 18 | 35.2 | 58.2 | 28.7 | 221.1 | 204.9 | 34.7 | 103.4 | 98.6 | 52.3
355 | 161 | 466.5 | 186.6 | 218.1246 | 211.4 | 189.6 | 206.4 | 203.7 | 486.6 | 19.8 | 21.2 | 42.3 | 3.7 | 239.9 | 6.2 | 271.1 | 885.7 | 824.9 | 257.7 | 573.6 | 541.7 | 641.9 | 766.8 | 216.2 | 645.3 | 18 | 35.4 | 58.6 | 28.8 | 221.2 | 205.4 | 34.9 | 103.8 | 99.2 | 52.6
356 | 162 | 466.3 | 186.52 | 218.0311 | 212.8 | 190.9 | 208 | 204.9 | 485.7 | 19.9 | 21.2 | 42.6 | 4.2 | 230.3 | 6.2 | 271.9 | 885 | 828.4 | 259 | 576.7 | 544.9 | 641.6 | 768.1 | 217.2 | 647.2 | 18.1 | 35.6 | 58.8 | 29 | 221.6 | 205.4 | 35.1 | 104.2 | 99.8 | 52.8
357 | 163 | 467.3 | 186.92 | 218.4987 | 212.9 | 191.5 | 209.5 | 204.6 | 475.5 | 20.1 | 21.2 | 42.8 | 4.2 | 227.1 | 5.8 | 272.8 | 883 | 829.2 | 260.3 | 578.3 | 547.5 | 632.6 | 767.1 | 217.9 | 645.6 | 18.1 | 35.9 | 59 | 29.1 | 221.9 | 205.6 | 35.3 | 104.7 | 100.4 | 53.1
358 | 164 | 467 | 186.8 | 218.3584 | 212.2 | 192.2 | 210.3 | 204.2 | 468.3 | 20.1 | 21.2 | 42.9 | 4 | 243.6 | 5.3 | 273.7 | 883.1 | 838 | 261.6 | 580.8 | 551.2 | 636.4 | 770.5 | 218.8 | 645.6 | 18.2 | 36.1 | 59.3 | 29.3 | 222.7 | 205.8 | 35.5 | 105.1 | 101 | 53.4
359 | 165 | 466.8 | 186.72 | 218.2649 | 211.8 | 193.8 | 211 | 202.8 | 479.8 | 20.1 | 21.2 | 43 | 4.3 | 238.6 | 5.3 | 274.6 | 880.2 | 834.9 | 263 | 582.4 | 556.9 | 638.5 | 773.1 | 219.7 | 646.1 | 18.2 | 36.3 | 59.8 | 29.4 | 223.1 | 206.3 | 35.8 | 105.6 | 101.5 | 53.7
360 | 166 | 467.3 | 186.92 | 218.4987 | 211.7 | 193.8 | 211.7 | 202.4 | 504.1 | 20.2 | 21.2 | 43 | 3.7 | 235.2 | 5.2 | 275.6 | 877.5 | 827.5 | 264.4 | 581.8 | 562.5 | 643.4 | 772.7 | 220.7 | 645.3 | 18.3 | 36.5 | 60.3 | 29.5 | 223.4 | 206.4 | 36 | 106.1 | 102 | 54
361 | 167 | 467.3 | 186.92 | 218.4987 | 211.7 | 193.8 | 211.8 | 203 | 503.2 | 20.4 | 21.2 | 43 | 3.6 | 224.4 | 4.6 | 276.6 | 869.6 | 819.3 | 265.8 | 580.1 | 567.4 | 636 | 762.2 | 221.3 | 642.5 | 18.3 | 36.7 | 60.4 | 29.7 | 223.7 | 206.3 | 36.2 | 106.5 | 102.6 | 54.2
362 | 168 | 466.5 | 186.6 | 218.1246 | 212.9 | 195.3 | 212 | 203.3 | 498.4 | 20.4 | 21.2 | 43.1 | 4.1 | 206 | 4.3 | 277.5 | 868.1 | 825.9 | 267.2 | 580.3 | 573.6 | 635.6 | 761.1 | 222 | 641.4 | 18.3 | 36.9 | 60.8 | 29.8 | 224 | 206.5 | 36.5 | 106.9 | 103 | 54.5
363 | 169 | 467 | 186.8 | 218.3584 | 215.2 | 197.1 | 212.7 | 204.1 | 496.1 | 20.4 | 21.2 | 43.2 | 4.8 | 230.8 | 4.3 | 278.5 | 864.2 | 824.3 | 268.7 | 584.3 | 577.9 | 637.9 | 759.7 | 222.8 | 642 | 18.4 | 37.1 | 61 | 30 | 224.3 | 207 | 36.7 | 107.3 | 103.5 | 54.7
364 | 170 | 467 | 186.8 | 218.3584 | 216.3 | 197.1 | 213.5 | 204.9 | 497.5 | 20.5 | 21.2 | 43.3 | 5.1 | 253.8 | 4.3 | 279.5 | 866.5 | 838.2 | 270.1 | 587.2 | 581.6 | 640.9 | 765.9 | 223.7 | 643.8 | 18.4 | 37.4 | 61.3 | 30.1 | 224.6 | 207.4 | 36.9 | 107.7 | 104.1 | 55
365 | 171 | 467.2 | 186.88 | 218.452 | 216.1 | 197 | 214.3 | 205.6 | 503.2 | 20.6 | 21.2 | 43.4 | 5.2 | 205 | 5.4 | 280.6 | 862.8 | 836.4 | 271.6 | 587.8 | 584.9 | 646 | 767.9 | 224.6 | 644.1 | 18.5 | 37.6 | 61.8 | 30.3 | 225 | 208.1 | 37.1 | 108.1 | 104.6 | 55.2
366 | 172 | 466.9 | 186.76 | 218.3117 | 216.5 | 196.2 | 213.9 | 206.6 | 507.6 | 20.6 | 21.2 | 43.5 | 4.5 | 205.2 | 8.3 | 281.7 | 861.3 | 825.1 | 273.1 | 586.2 | 587.8 | 644.8 | 764.2 | 225.5 | 642.3 | 18.5 | 37.8 | 62.3 | 30.4 | 225.1 | 208.6 | 37.3 | 108.6 | 105.2 | 55.5
367 | 173 | 465.7 | 186.28 | 217.7506 | 217.8 | 195.7 | 214.4 | 206.5 | 511.7 | 20.7 | 21.2 | 43.6 | 4.2 | 199.9 | 8 | 282.7 | 861.8 | 805.5 | 274.5 | 584.1 | 592.4 | 644 | 756.9 | 226.4 | 641.2 | 18.6 | 38 | 62.7 | 30.6 | 225.7 | 208.9 | 37.5 | 109.1 | 105.7 | 55.9
368 | 174 | 466 | 186.4 | 217.8909 | 218.7 | 196.7 | 215.5 | 207.3 | 506.8 | 20.8 | 21.2 | 43.6 | 4.2 | 227.1 | 8.3 | 283.7 | 863.4 | 784.2 | 276 | 582.9 | 594.2 | 639.3 | 747.7 | 227.2 | 639.6 | 18.6 | 38.2 | 62.8 | 30.7 | 226 | 208.8 | 37.8 | 109.5 | 106.3 | 56.1
369 | 175 | 466.7 | 186.68 | 218.2182 | 218.5 | 197.5 | 217.1 | 207.4 | 492.4 | 20.9 | 21.2 | 43.7 | 4.2 | 214.2 | 9.1 | 284.8 | 861.4 | 758.9 | 277.4 | 580.7 | 594.6 | 631.3 | 735.1 | 227.9 | 637.6 | 18.6 | 38.4 | 63.1 | 30.9 | 226.2 | 208.7 | 38 | 110 | 106.8 | 56.4
370 | 176 | 467 | 186.8 | 218.3584 | 218.5 | 198 | 218 | 207.3 | 483.5 | 20.9 | 21.1 | 43.8 | 4.1 | 201 | 9.4 | 285.8 | 859.4 | 763 | 278.9 | 579.6 | 597.1 | 630.1 | 738.6 | 228.6 | 636 | 18.7 | 38.6 | 63.5 | 31 | 226.7 | 208.6 | 38.2 | 110.4 | 107.3 | 56.7
371 | 177 | 467.1 | 186.84 | 218.4052 | 218.1 | 198.4 | 218.4 | 207.6 | 488.2 | 20.9 | 21.1 | 43.9 | 4.1 | 245.7 | 8.3 | 286.9 | 861.2 | 763.1 | 280.3 | 579.1 | 602.1 | 632.3 | 742.2 | 229.4 | 636.6 | 18.7 | 38.8 | 63.8 | 31.2 | 227 | 208.9 | 38.4 | 111 | 107.8 | 57
372 | 178 | 467.4 | 186.96 | 218.5455 | 217.5 | 198.5 | 218.4 | 208.4 | 482.7 | 21 | 21.1 | 44 | 4.2 | 253.2 | 7.2 | 287.9 | 862.3 | 748.5 | 281.8 | 577.6 | 603.9 | 633.7 | 745.1 | 230.4 | 637.7 | 18.8 | 39 | 64.2 | 31.3 | 227.4 | 209.1 | 38.7 | 111.5 | 108.3 | 57.3
373 | 179 | 467.4 | 186.96 | 218.5455 | 217 | 198.7 | 218.4 | 208.4 | 468.7 | 21.1 | 21.1 | 44 | 4.1 | 211.8 | 6.2 | 289 | 865.6 | 738 | 283.3 | 577.1 | 605.4 | 635.6 | 738.8 | 231.4 | 638.2 | 18.8 | 39.3 | 64.2 | 31.5 | 227.8 | 209.5 | 38.9 | 112 | 108.8 | 57.5
374 | 180 | 467.9 | 187.16 | 218.7793 | 216.8 | 198.5 | 218.2 | 208.5 | 466.2 | 21.2 | 21.1 | 44 | 4.6 | 243.9 | 6.1 | 290.1 | 862.6 | 754 | 284.6 | 578.9 | 610.7 | 630.5 | 732 | 232.3 | 636.6 | 18.9 | 39.5 | 64.5 | 31.6 | 227.9 | 210 | 39.1 | 112.5 | 109.3 | 57.8
375 | 181 | 466.6 | 186.64 | 218.1714 | 217.3 | 199.2 | 218.8 | 208.7 | 476.9 | 21.2 | 21.1 | 44.1 | 4.8 | 241.3 | 5.7 | 291.1 | 866.8 | 766.1 | 286 | 578.9 | 616.2 | 638.4 | 742.3 | 233.3 | 638.6 | 18.9 | 39.7 | 65.1 | 31.8 | 228 | 210.1 | 39.3 | 112.8 | 109.8 | 58.1
376 | 182 | 466.9 | 186.76 | 218.3117 | 217.1 | 201.1 | 219.6 | 209.4 | 484.7 | 21.3 | 21.1 | 44.2 | 4.7 | 200.3 | 6.1 | 292.2 | 867 | 763 | 287.5 | 581.4 | 619.9 | 647.9 | 750 | 234.4 | 642.5 | 19 | 39.9 | 65.2 | 31.9 | 228.4 | 210.3 | 39.6 | 113.2 | 110.3 | 58.3
377 | 183 | 466.9 | 186.76 | 218.3117 | 216.8 | 201.8 | 220.2 | 209.7 | 475.6 | 21.3 | 21.1 | 44.3 | 4.4 | 226.6 | 7.4 | 293.3 | 873.2 | 757.5 | 288.9 | 580.5 | 621.5 | 644.3 | 746.3 | 235.5 | 642.2 | 19 | 40.1 | 65.6 | 32.1 | 228.6 | 210.7 | 39.8 | 113.7 | 110.9 | 58.5
378 | 184 | 466.5 | 186.6 | 218.1246 | 216.5 | 201.7 | 220.2 | 210.5 | 470.8 | 21.3 | 21.1 | 44.4 | 4.5 | 220.7 | 8.1 | 294.3 | 873.3 | 760.6 | 290.3 | 582 | 622.3 | 636.8 | 745.4 | 236.5 | 641.3 | 19.1 | 40.3 | 65.7 | 32.2 | 228.6 | 210.8 | 40 | 114.2 | 111.4 | 58.8
379 | 185 | 466.9 | 186.76 | 218.3117 | 216.3 | 202.5 | 220.2 | 210.6 | 467.4 | 21.3 | 21.1 | 44.4 | 4.5 | 227.9 | 7.4 | 295.3 | 875 | 744.8 | 291.8 | 581.2 | 623.8 | 636.1 | 738.7 | 237.5 | 642.5 | 19.1 | 40.5 | 66 | 32.4 | 228.4 | 211.1 | 40.2 | 114.6 | 111.9 | 59
380 | 186 | 466.3 | 186.52 | 218.0311 | 216.8 | 202.3 | 220.1 | 209.7 | 462.7 | 21.4 | 21.1 | 44.5 | 4.2 | 218 | 6.6 | 296.4 | 875.9 | 737.6 | 293.2 | 579.1 | 625.1 | 633.1 | 735.9 | 238.2 | 640.9 | 19.2 | 40.7 | 66.3 | 32.5 | 228.3 | 211.1 | 40.4 | 115.1 | 112.5 | 59.2
381 | 187 | 466.8 | 186.72 | 218.2649 | 217.9 | 200.9 | 219.8 | 208.9 | 457.3 | 21.4 | 21.1 | 44.5 | 4.1 | 233 | 5.7 | 297.4 | 876.9 | 766.1 | 294.7 | 582.8 | 627.3 | 640 | 744.2 | 239.3 | 642.9 | 19.2 | 41 | 66.6 | 32.7 | 228.7 | 211.3 | 40.6 | 115.5 | 113 | 59.5
382 | 188 | 466.3 | 186.52 | 218.0311 | 217.8 | 200 | 220 | 209.8 | 466.6 | 21.5 | 21.1 | 44.7 | 4.1 | 243 | 6.2 | 298.4 | 875.3 | 776.4 | 296.2 | 585 | 632.4 | 649.2 | 752.6 | 240.6 | 645.5 | 19.3 | 41.2 | 67.2 | 32.8 | 229.4 | 211.7 | 40.8 | 115.9 | 113.5 | 59.7
383 | 189 | 467.1 | 186.84 | 218.4052 | 218.8 | 200.6 | 220.1 | 210.3 | 481.5 | 21.6 | 21.1 | 45 | 5 | 245.7 | 8 | 299.5 | 872.9 | 784.5 | 297.6 | 588.4 | 638.3 | 647.9 | 749.5 | 241.7 | 646.2 | 19.3 | 41.5 | 67.6 | 33 | 229.5 | 212.1 | 41 | 116.3 | 114.2 | 60
384 | 190 | 467.4 | 186.96 | 218.5455 | 220 | 200.4 | 221.1 | 211.3 | 478.7 | 21.7 | 21.1 | 45 | 4.7 | 239.3 | 9.1 | 300.5 | 869.3 | 800.3 | 299 | 593.6 | 640.9 | 658.3 | 757.3 | 243.1 | 651.6 | 19.3 | 41.7 | 67.7 | 33.1 | 229.6 | 212.3 | 41.3 | 116.9 | 114.9 | 60.3
385 | 191 | 465.3 | 186.12 | 217.5636 | 219.9 | 200.4 | 222.4 | 211.4 | 473.2 | 21.8 | 21.1 | 45.1 | 4.1 | 251.1 | 8.4 | 301.6 | 864.2 | 797.7 | 300.4 | 600.4 | 640.3 | 667.7 | 758 | 244.6 | 655.8 | 19.4 | 41.9 | 68 | 33.3 | 229.7 | 212.7 | 41.5 | 117.4 | 115.6 | 60.5
386 | 192 | 465.4 | 186.16 | 217.6103 | 220.3 | 201.1 | 222.1 | 210.9 | 471.7 | 21.8 | 21.1 | 45.1 | 4.3 | 256.4 | 7.6 | 302.8 | 868.4 | 779.7 | 301.9 | 601.2 | 638.4 | 669.5 | 749.2 | 246.1 | 656.6 | 19.5 | 42.1 | 68.3 | 33.4 | 229.8 | 213.4 | 41.7 | 117.9 | 116.4 | 60.9
387 | 193 | 466.2 | 186.48 | 217.9844 | 220 | 201.6 | 220.2 | 211.2 | 463.3 | 21.8 | 21.1 | 45.2 | 4.2 | 249.7 | 7.2 | 303.9 | 869 | 765.9 | 303.5 | 601.9 | 637 | 672 | 743.9 | 247.7 | 657.9 | 19.5 | 42.3 | 68.7 | 33.6 | 229.7 | 214 | 42 | 118.4 | 117.1 | 61.2
388 | 194 | 465.2 | 186.08 | 217.5168 | 220.1 | 202.1 | 219.2 | 210 | 458.2 | 21.8 | 21.1 | 45.3 | 4.3 | 266.9 | 6.2 | 305.1 | 865.5 | 766.5 | 304.9 | 606.2 | 636.9 | 677.2 | 750 | 249.4 | 661 | 19.6 | 42.5 | 68.9 | 33.8 | 229.4 | 215.2 | 42.1 | 119.1 | 117.8 | 61.5
389 | 195 | 466.8 | 186.72 | 218.2649 | 219.9 | 202.3 | 219.4 | 208.5 | 456.1 | 21.8 | 21.1 | 45.3 | 4.3 | 246.2 | 8.6 | 306.2 | 862.5 | 768.6 | 306.4 | 610.9 | 635.2 | 686.2 | 752.5 | 251.2 | 663.6 | 19.6 | 42.7 | 69.2 | 33.9 | 229 | 215.8 | 42.4 | 119.9 | 118.5 | 61.8
390 | 196 | 467.2 | 186.88 | 218.452 | 219.9 | 202.1 | 220 | 209.1 | 459.5 | 21.9 | 21.1 | 45.3 | 3.8 | 246.3 | 10.4 | 307.4 | 864.5 | 774 | 307.8 | 615.1 | 634.2 | 693.5 | 754.5 | 253 | 668.6 | 19.7 | 42.9 | 69.7 | 34.1 | 229 | 215.9 | 42.6 | 120.3 | 119.2 | 62
391 | 197 | 463.9 | 185.56 | 216.9089 | 220.1 | 201.5 | 221.2 | 208.7 | 462.4 | 21.9 | 21.1 | 45.4 | 4.1 | 247.3 | 10.5 | 308.5 | 862.9 | 768.2 | 309.3 | 620.4 | 633.4 | 700.5 | 758.9 | 254.8 | 672 | 19.7 | 43.1 | 69.6 | 34.2 | 229.3 | 216.1 | 42.8 | 120.7 | 120.2 | 62.3
392 | 198 | 465.3 | 186.12 | 217.5636 | 220.3 | 201.2 | 222 | 208.1 | 465.4 | 22 | 21.1 | 45.5 | 5.3 | 240.4 | 9.6 | 309.7 | 869.6 | 758.7 | 310.8 | 621.8 | 632.6 | 706.5 | 759.2 | 256.7 | 675.2 | 19.8 | 43.3 | 69.9 | 34.4 | 229.4 | 216.5 | 43 | 121.2 | 121 | 62.5
393 | 199 | 465.7 | 186.28 | 217.7506 | 220.8 | 200.8 | 221.8 | 207 | 466.9 | 22.1 | 21.1 | 45.6 | 5.8 | 246.3 | 8.1 | 310.9 | 868.2 | 783.2 | 312.1 | 628.6 | 633.3 | 711.8 | 765.1 | 258.5 | 678.9 | 19.8 | 43.5 | 70.3 | 34.6 | 229.6 | 216.7 | 43.2 | 121.7 | 121.8 | 62.7
394 | 200 | 465.3 | 186.12 | 217.5636 | 221.5 | 201.1 | 221 | 206.3 | 477.3 | 22.1 | 21.1 | 45.7 | 5.9 | 246.7 | 8.1 | 312.1 | 866.5 | 796.9 | 313.5 | 634.1 | 635.6 | 714 | 768.5 | 260.2 | 681.6 | 19.9 | 43.8 | 70.8 | 34.7 | 229.9 | 216.9 | 43.4 | 122 | 122.5 | 63
395 | 201 | 465.6 | 186.24 | 217.7038 | 221.5 | 201.3 | 220.6 | 206.6 | 484.9 | 22.2 | 21.1 | 45.9 | 6.1 | 246.6 | 9.3 | 313.3 | 863.3 | 809.2 | 314.9 | 638.9 | 637.6 | 717.7 | 771.6 | 261.9 | 684.7 | 19.9 | 44 | 71.2 | 34.9 | 230.4 | 217 | 43.7 | 122.5 | 123.2 | 63.2
396 | 202 | 465.7 | 186.28 | 217.7506 | 221.7 | 200.8 | 220.9 | 205.7 | 487.2 | 22.3 | 21.1 | 46 | 6.1 | 249.3 | 8.7 | 314.5 | 864.6 | 812.7 | 316.5 | 640.8 | 641.3 | 718.5 | 774.4 | 263.5 | 687.8 | 20 | 44.2 | 71.4 | 35 | 230.9 | 217.3 | 43.9 | 123 | 124 | 63.5
397 | 203 | 466 | 186.4 | 217.8909 | 221.5 | 201.4 | 220.9 | 204.8 | 489.9 | 22.4 | 21.1 | 46 | 6.1 | 239 | 8.9 | 315.6 | 866 | 808 | 318.2 | 642.9 | 643.5 | 718 | 778.2 | 265.1 | 691.4 | 20 | 44.4 | 71.7 | 35.2 | 231.2 | 217.7 | 44.1 | 123.5 | 124.8 | 63.8
398 | 204 | 466.4 | 186.56 | 218.0779 | 221.1 | 202.9 | 220.8 | 205.5 | 491.2 | 22.5 | 21.1 | 46.1 | 5 | 243.4 | 10.9 | 316.7 | 860.4 | 805.1 | 319.9 | 646.5 | 644.7 | 722.8 | 780 | 266.7 | 694.1 | 20.1 | 44.7 | 71.9 | 35.4 | 231.4 | 218.2 | 44.3 | 124 | 125.6 | 64
399 | 205 | 466.2 | 186.48 | 217.9844 | 221.2 | 204.2 | 221.2 | 205.1 | 495.7 | 22.5 | 21.1 | 46.2 | 6.7 | 244.5 | 12.4 | 317.8 | 859.4 | 801.3 | 321.6 | 649.3 | 646.7 | 726.5 | 778.7 | 268.4 | 696 | 20.1 | 44.9 | 72.4 | 35.5 | 231.5 | 218.8 | 44.5 | 124.5 | 126.4 | 64.3
400 | 206 | 465.9 | 186.36 | 217.8441 | 221.4 | 205.4 | 221.9 | 205.6 | 493 | 22.6 | 21.1 | 46.3 | 8.1 | 238.4 | 12.7 | 319 | 867.1 | 802.9 | 323.4 | 652.5 | 649 | 720.9 | 781.6 | 269.7 | 698.2 | 20.2 | 45.2 | 72.6 | 35.7 | 231.5 | 219.5 | 44.7 | 125 | 127.4 | 64.5
401 | 207 | 466.4 | 186.56 | 218.0779 | 221.5 | 207.1 | 222.4 | 206.4 | 491.5 | 22.7 | 21 | 46.4 | 9.1 | 248.9 | 13.4 | 320.1 | 868.1 | 798.8 | 325.2 | 655.7 | 651.5 | 719.4 | 783.8 | 270.9 | 698.7 | 20.3 | 45.4 | 72.8 | 35.9 | 231.7 | 219.9 | 44.9 | 125.3 | 128.3 | 64.8
402 | 208 | 466.2 | 186.48 | 217.9844 | 221.2 | 208.4 | 221.9 | 205.9 | 499 | 22.7 | 21 | 46.5 | 6.2 | 248.5 | 14 | 321.2 | 864.5 | 807.6 | 327 | 658.1 | 655.5 | 725.6 | 788.7 | 272 | 701.8 | 20.3 | 45.6 | 73.1 | 36 | 232.3 | 220.4 | 45.1 | 125.6 | 129.1 | 65.1
403 | 209 | 466.5 | 186.6 | 218.1246 | 220.5 | 208.9 | 221 | 205.7 | 499.9 | 22.8 | 21 | 46.6 | 5.2 | 242.4 | 15.9 | 322.3 | 863.5 | 821 | 328.7 | 659.6 | 659 | 725.3 | 788.8 | 273.1 | 701.8 | 20.4 | 45.8 | 73.7 | 36.2 | 232.8 | 220.5 | 45.3 | 126.1 | 129.8 | 65.3
404 | 210 | 466.5 | 186.6 | 218.1246 | 222.2 | 208.7 | 220.1 | 206.2 | 496.4 | 22.9 | 21 | 46.9 | 5.2 | 244.7 | 19.1 | 323.4 | 866.8 | 825.9 | 330.2 | 661.6 | 660.6 | 727.1 | 786.2 | 274.2 | 702.3 | 20.4 | 46.1 | 73.9 | 36.4 | 233.2 | 220.6 | 45.6 | 126.5 | 130.7 | 65.7
405 | 211 | 466 | 186.4 | 217.8909 | 223.8 | 209.1 | 220.4 | 207.2 | 492.2 | 23 | 21 | 47.1 | 5 | 242.3 | 20.2 | 324.5 | 865.5 | 827.5 | 332 | 665.3 | 662.2 | 727.1 | 789.1 | 275.2 | 704.8 | 20.5 | 46.3 | 74.2 | 36.5 | 233.6 | 220.8 | 45.8 | 127 | 131.4 | 65.9
406 | 212 | 466.7 | 186.68 | 218.2182 | 223.6 | 209.1 | 220.9 | 206.9 | 491.6 | 23 | 21 | 47.2 | 6.6 | 231.5 | 17.4 | 325.6 | 867.5 | 827.6 | 334 | 668.4 | 665.2 | 728 | 794.6 | 276.2 | 706.4 | 20.5 | 46.5 | 74.5 | 36.7 | 234.2 | 221 | 46 | 127.5 | 132.1 | 66.2
407 | 213 | 466.8 | 186.72 | 218.2649 | 224.1 | 209.3 | 220.9 | 205.6 | 493.9 | 23.1 | 21 | 47.3 | 5.1 | 242.4 | 14.8 | 326.8 | 865.3 | 834.8 | 336.1 | 672.4 | 668.1 | 733 | 798.3 | 277.1 | 709.3 | 20.6 | 46.7 | 74.8 | 36.9 | 234.4 | 221 | 46.2 | 127.9 | 132.9 | 66.5
408 | 214 | 466.8 | 186.72 | 218.2649 | 223.8 | 209.7 | 220 | 204.1 | 498.7 | 23.1 | 21 | 47.3 | 5.1 | 239.9 | 15.9 | 328 | 860.9 | 843.1 | 338.1 | 676.2 | 670.4 | 738.1 | 799.3 | 278.1 | 712 | 20.7 | 46.9 | 75.2 | 37.1 | 234.7 | 221.7 | 46.4 | 128.3 | 133.8 | 66.8
409 | 215 | 466.6 | 186.64 | 218.1714 | 223.7 | 210.7 | 219.1 | 204.6 | 517.4 | 23.2 | 21 | 47.5 | 5 | 253.6 | 15.8 | 329.2 | 863.9 | 843.6 | 340 | 674.6 | 674.4 | 741.6 | 803.2 | 279 | 712 | 20.7 | 47.1 | 75.7 | 37.2 | 235 | 221.8 | 46.6 | 128.8 | 134.7 | 67
410 | 216 | 466.6 | 186.64 | 218.1714 | 224.9 | 211.7 | 218.4 | 206.3 | 542.3 | 23.2 | 21 | 47.6 | 5.2 | 253.6 | 16.7 | 330.4 | 860.8 | 846.1 | 341.9 | 677.2 | 677.6 | 746 | 805.4 | 279.8 | 713.6 | 20.8 | 47.4 | 76.1 | 37.4 | 235.7 | 222 | 46.9 | 129.2 | 135.6 | 67.3
411 | 217 | 466.9 | 186.76 | 218.3117 | 225.5 | 214.4 | 220 | 206.8 | 556.4 | 23.2 | 21 | 47.7 | 5.1 | 253.7 | 16.7 | 331.7 | 857.1 | 852.8 | 343.9 | 682.2 | 678.4 | 748.8 | 806.5 | 280.8 | 716.5 | 20.9 | 47.6 | 76.3 | 37.6 | 236.7 | 222.4 | 47.1 | 129.7 | 136.5 | 67.6
412 | 218 | 464.8 | 185.92 | 217.3298 | 224.7 | 216.6 | 221.8 | 207.9 | 561.7 | 23.2 | 21 | 47.7 | 6.7 | 252.8 | 17.1 | 333 | 859.6 | 850.1 | 345.8 | 684.6 | 679.4 | 746.5 | 807.3 | 281.6 | 716.5 | 20.9 | 47.9 | 76.7 | 37.7 | 237.5 | 223 | 47.3 | 130.3 | 137.5 | 67.8
413 | 219 | 464.2 | 185.68 | 217.0492 | 223.8 | 218 | 221.8 | 209.3 | 570.1 | 23.2 | 21 | 47.7 | 7.8 | 264.2 | 18.4 | 334.4 | 859 | 850.8 | 347.7 | 684.5 | 681.3 | 746.9 | 810.1 | 282.3 | 717.7 | 21 | 48.1 | 77.2 | 37.9 | 238.2 | 223.4 | 47.5 | 130.8 | 138.5 | 68.2
414 | 220 | 463.6 | 185.44 | 216.7687 | 224.4 | 219.9 | 222.2 | 210.2 | 583.7 | 23.3 | 21 | 47.8 | 6.8 | 270.8 | 18.4 | 335.9 | 857.4 | 847.4 | 349.7 | 688 | 683.8 | 748.8 | 810.7 | 283.2 | 720.6 | 21 | 48.3 | 77.9 | 38.1 | 238.9 | 223.7 | 47.8 | 131.2 | 139.4 | 68.5
415 | 221 | 462.7 | 185.08 | 216.3479 | 224.7 | 221.2 | 223.4 | 212.1 | 584.8 | 23.3 | 21 | 47.7 | 7.9 | 259.8 | 19 | 337.4 | 861.6 | 845.6 | 351.6 | 689 | 685.6 | 742.7 | 809.7 | 284 | 719.4 | 21.1 | 48.6 | 78 | 38.3 | 239.4 | 224 | 47.9 | 131.8 | 140.4 | 68.8
416 | 222 | 463.5 | 185.4 | 216.7219 | 225.8 | 221.3 | 224.9 | 213.3 | 583.4 | 23.4 | 21 | 47.6 | 8.2 | 260.6 | 21.1 | 338.9 | 859.2 | 836.3 | 353.7 | 690.1 | 685.3 | 741.8 | 811.1 | 284.8 | 721.8 | 21.2 | 48.8 | 78.3 | 38.4 | 240 | 224.4 | 48.2 | 132.3 | 141.2 | 69.1
417 | 223 | 464.2 | 185.68 | 217.0492 | 226.7 | 219.9 | 226 | 213.8 | 579.5 | 23.4 | 21 | 47.6 | 7.2 | 260.7 | 21.9 | 340.6 | 856.4 | 841.2 | 355.6 | 691 | 686.4 | 739.2 | 812.4 | 285.5 | 721.3 | 21.2 | 49 | 78.7 | 38.6 | 240.5 | 224.9 | 48.4 | 132.8 | 142 | 69.5
418 | 224 | 464.2 | 185.68 | 217.0492 | 227.1 | 220.8 | 227.1 | 215.2 | 577.2 | 23.4 | 21 | 47.6 | 6.4 | 251.3 | 20.5 | 342 | 858.6 | 843.9 | 357.5 | 690.6 | 688.8 | 735.7 | 812.2 | 286.1 | 720.3 | 21.3 | 49.2 | 79.3 | 38.8 | 241 | 225.2 | 48.7 | 133.3 | 142.8 | 69.8
419 | 225 | 463.6 | 185.44 | 216.7687 | 226.9 | 222.8 | 228.3 | 216.8 | 579.8 | 23.4 | 21 | 47.7 | 8.2 | 265 | 18.6 | 343.7 | 854 | 840.4 | 359.5 | 693.1 | 689.9 | 734 | 809 | 286.9 | 721.9 | 21.4 | 49.5 | 79.5 | 39 | 241.2 | 225.9 | 48.9 | 133.9 | 143.6 | 70.1
420 | 226 | 465.1 | 186.04 | 217.47 | 226.8 | 223.5 | 229.3 | 217.6 | 573.1 | 23.5 | 21 | 47.9 | 8.9 | 273.2 | 18.8 | 345.4 | 853.7 | 830.3 | 361.5 | 691 | 691.1 | 730.8 | 806.8 | 287.6 | 720.5 | 21.4 | 49.7 | 79.9 | 39.1 | 241.5 | 226.6 | 49.1 | 134.2 | 144.4 | 70.4
421 | 227 | 466.2 | 186.48 | 217.9844 | 227.2 | 223.2 | 229.9 | 218.5 | 574.3 | 23.5 | 21 | 48.2 | 8.2 | 273.8 | 18.4 | 346.6 | 854.5 | 820.8 | 363.4 | 688.6 | 692.9 | 726.9 | 802 | 288.2 | 719.4 | 21.5 | 50 | 80.4 | 39.3 | 242 | 227.1 | 49.3 | 134.6 | 145.2 | 70.7
422 | 228 | 465.9 | 186.36 | 217.8441 | 228.2 | 223.4 | 231.6 | 218.8 | 574 | 23.6 | 21 | 48.4 | 8.2 | 279.8 | 20.9 | 347.8 | 857.1 | 810.9 | 365.2 | 686.1 | 695.8 | 722.5 | 795.6 | 288.9 | 717.2 | 21.6 | 50.2 | 80.9 | 39.5 | 242 | 227.4 | 49.5 | 135.2 | 146 | 71
423 | 229 | 466.1 | 186.44 | 217.9376 | 229.1 | 224.5 | 233.3 | 220.2 | 572.3 | 23.6 | 21 | 48.5 | 8.3 | 272.5 | 19.9 | 349.1 | 856.1 | 798.1 | 367.2 | 683.6 | 698.8 | 718.9 | 791.2 | 289.5 | 714.4 | 21.6 | 50.5 | 81.3 | 39.7 | 242.7 | 227.6 | 49.8 | 135.7 | 146.7 | 71.3
424 | 230 | 466.9 | 186.76 | 218.3117 | 229.2 | 226.9 | 234.8 | 222.1 | 561 | 23.7 | 21 | 48.5 | 9 | 276.8 | 19.3 | 350.3 | 854.4 | 790.2 | 369.2 | 683.3 | 701.1 | 716.3 | 794.4 | 290.1 | 713.8 | 21.7 | 50.7 | 81.7 | 39.8 | 243.5 | 227.7 | 50 | 136.1 | 147.4 | 71.7
425 | 231 | 467.2 | 186.88 | 218.452 | 229.6 | 227.7 | 235.3 | 223.3 | 554.9 | 23.8 | 21 | 48.5 | 9.9 | 271.3 | 19 | 351.5 | 851.6 | 792.1 | 371.3 | 683 | 701.8 | 713.5 | 792.5 | 290.7 | 713.3 | 21.8 | 50.9 | 82 | 40 | 244.2 | 228 | 50.2 | 136.4 | 148.1 | 72
426 | 232 | 466.9 | 186.76 | 218.3117 | 229.7 | 228.2 | 235.7 | 223.3 | 560 | 23.9 | 21 | 48.5 | 11.8 | 264 | 16.9 | 352.9 | 848.6 | 784.6 | 373.4 | 681.8 | 703.9 | 709.9 | 789.7 | 291.4 | 710.7 | 21.8 | 51.1 | 82.4 | 40.2 | 245.2 | 228.6 | 50.4 | 136.8 | 148.7 | 72.3
427 | 233 | 466.7 | 186.68 | 218.2182 | 230.3 | 228.6 | 236.1 | 224.3 | 550.6 | 24 | 21 | 48.6 | 12.1 | 262.7 | 17.2 | 354.4 | 847.9 | 770 | 375.6 | 678.1 | 706.1 | 705.6 | 786.5 | 292 | 709.5 | 21.9 | 51.4 | 82.6 | 40.4 | 245.8 | 229.6 | 50.7 | 137.3 | 149.3 | 72.6
428 | 234 | 465.1 | 186.04 | 217.47 | 230.9 | 229.4 | 236.1 | 225.3 | 535.7 | 24.1 | 21 | 48.7 | 11.1 | 243.1 | 17.1 | 356.1 | 850.8 | 771.4 | 378.1 | 680.1 | 706.5 | 706.9 | 788.7 | 292.9 | 710.1 | 22 | 51.6 | 83.1 | 40.5 | 245.7 | 230.4 | 50.9 | 138 | 149.9 | 73
429 | 235 | 463.9 | 185.56 | 216.9089 | 231.2 | 229.3 | 236.7 | 226.4 | 528.9 | 24.2 | 21 | 48.8 | 9.1 | 238 | 20.6 | 358.1 | 847.9 | 783.9 | 380.7 | 681.2 | 704.9 | 711.7 | 790.8 | 293.8 | 712.1 | 22 | 51.9 | 83.2 | 40.7 | 245.8 | 230.7 | 51.1 | 138.5 | 150.6 | 73.2
430 | 236 | 464.8 | 185.92 | 217.3298 | 231.7 | 229.7 | 235.9 | 226.6 | 534.2 | 24.3 | 21 | 48.9 | 9.9 | 247.1 | 20.3 | 360.5 | 842.5 | 793.4 | 383.3 | 682.1 | 704.6 | 718.4 | 792.5 | 294.8 | 713 | 22.1 | 52.1 | 83.7 | 40.9 | 246 | 231.1 | 51.3 | 138.9 | 151.3 | 73.5
431 | 237 | 464.9 | 185.96 | 217.3765 | 231.8 | 230.2 | 235.1 | 226.3 | 531 | 24.4 | 20.9 | 49 | 9.9 | 253.8 | 17.9 | 362.9 | 840 | 800.3 | 385.6 | 680.8 | 704.5 | 724.9 | 795.1 | 295.8 | 715.3 | 22.2 | 52.3 | 84 | 41 | 246.1 | 231.3 | 51.5 | 139.5 | 152.1 | 73.8
432 | 238 | 464.6 | 185.84 | 217.2363 | 231.4 | 230.4 | 235.9 | 224.9 | 527.4 | 24.4 | 20.9 | 49.1 | 9.9 | 262.2 | 17.6 | 366.2 | 836.2 | 809.1 | 387.7 | 682.6 | 704.8 | 730 | 797.6 | 296.7 | 716.7 | 22.3 | 52.6 | 84.3 | 41.2 | 247.5 | 231.6 | 51.8 | 140.1 | 152.9 | 74.1
433 | 239 | 464.6 | 185.84 | 217.2363 | 230.8 | 230.5 | 235.7 | 222.6 | 525.8 | 24.4 | 20.9 | 49.2 | 9.8 | 243.1 | 16.4 | 369.5 | 835.3 | 812.3 | 390.1 | 684.1 | 705 | 733.1 | 801.1 | 297.8 | 719.4 | 22.3 | 52.8 | 84.7 | 41.4 | 247.5 | 232.2 | 52 | 140.7 | 153.6 | 74.4
434 | 240 | 465.6 | 186.24 | 217.7038 | 230.1 | 229.6 | 235.6 | 221.5 | 532.7 | 24.4 | 20.9 | 49.2 | 8.9 | 247.1 | 20.1 | 372.2 | 835.1 | 812.9 | 392.6 | 684.5 | 705.3 | 730.7 | 802.3 | 298.7 | 719.7 | 22.4 | 53.1 | 84.9 | 41.6 | 247.1 | 232.6 | 52.2 | 141.2 | 154.5 | 74.7
435 | 241 | 465.4 | 186.16 | 217.6103 | 229.9 | 230.1 | 235.8 | 221.7 | 540.2 | 24.5 | 20.9 | 49.2 | 6.5 | 250.8 | 20.6 | 374.6 | 830.5 | 814.6 | 395.1 | 686 | 705.9 | 728.7 | 802.2 | 299.5 | 720.7 | 22.5 | 53.4 | 85.2 | 41.7 | 247.2 | 232.5 | 52.4 | 141.6 | 155.3 | 74.9
436 | 242 | 465.6 | 186.24 | 217.7038 | 229.9 | 230.5 | 235 | 221 | 543.3 | 24.6 | 20.9 | 49.1 | 6.4 | 260 | 18.4 | 377.3 | 830.9 | 817.1 | 397.4 | 685.1 | 706.3 | 730.6 | 803.7 | 300.4 | 721.5 | 22.5 | 53.6 | 85.5 | 41.9 | 247.3 | 232.7 | 52.6 | 142.1 | 156.2 | 75.2
437 | 243 | 465.6 | 186.24 | 217.7038 | 231.2 | 230.8 | 232.9 | 220.2 | 537.9 | 24.6 | 20.9 | 49.1 | 6.9 | 257.6 | 18.5 | 379.9 | 831 | 807 | 399.9 | 684.6 | 706.7 | 730 | 802.5 | 301.2 | 720.5 | 22.6 | 53.9 | 85.9 | 42.1 | 247.1 | 232.8 | 52.9 | 142.6 | 157.1 | 75.5
438 | 244 | 465.9 | 186.36 | 217.8441 | 232.6 | 231.2 | 232.1 | 220.8 | 530.1 | 24.7 | 20.9 | 49.2 | 6.9 | 239.7 | 18.5 | 382.6 | 830 | 806.2 | 402.6 | 685.3 | 705.4 | 734.9 | 803.2 | 302.1 | 722.1 | 22.7 | 54.1 | 86.1 | 42.3 | 247.1 | 232.9 | 53.1 | 142.9 | 157.8 | 75.8
439 | 245 | 464.8 | 185.92 | 217.3298 | 233.7 | 231.2 | 232.5 | 221.7 | 533.6 | 24.7 | 20.9 | 49.3 | 8.7 | 243.8 | 21.4 | 385.2 | 835.8 | 806.4 | 405.4 | 685.3 | 705.2 | 738.2 | 804.2 | 303.1 | 723.4 | 22.8 | 54.4 | 86.6 | 42.4 | 247.2 | 232.8 | 53.3 | 143.3 | 158.6 | 76.1
440 | 246 | 466 | 186.4 | 217.8909 | 233.8 | 231.2 | 232.7 | 222.1 | 528.1 | 24.9 | 20.9 | 49.5 | 6.6 | 252.5 | 20.8 | 387.5 | 835.8 | 801.9 | 408.1 | 684.2 | 704.7 | 738.7 | 807 | 303.9 | 723.4 | 22.8 | 54.7 | 86.8 | 42.6 | 247.2 | 233.1 | 53.5 | 143.9 | 159.4 | 76.4
441 | 247 | 465.9 | 186.36 | 217.8441 | 233 | 230.8 | 233.2 | 222.1 | 528.4 | 24.9 | 20.9 | 49.7 | 7.9 | 246.7 | 19.6 | 389.7 | 837.4 | 798.6 | 410.6 | 684.2 | 705 | 737.7 | 806.6 | 304.6 | 722.7 | 22.9 | 54.9 | 87.2 | 42.8 | 246.9 | 233.4 | 53.7 | 144.3 | 160 | 76.6
442 | 248 | 465.8 | 186.32 | 217.7973 | 233 | 230.6 | 232 | 222.7 | 531.5 | 25 | 20.9 | 50.1 | 6.8 | 252.7 | 16.9 | 391.6 | 839.6 | 806.8 | 412.8 | 685.9 | 705.9 | 736.4 | 808.2 | 305.4 | 722.9 | 23 | 55.2 | 87.6 | 43 | 246.9 | 233.4 | 54 | 144.6 | 160.6 | 76.9
443 | 249 | 465.7 | 186.28 | 217.7506 | 234 | 230.3 | 231.8 | 222.9 | 530.8 | 25 | 20.9 | 50.3 | 6.7 | 237.5 | 16.2 | 393.4 | 841.5 | 807.7 | 415.2 | 686.8 | 705.3 | 735.2 | 807 | 306 | 722.5 | 23.1 | 55.5 | 87.9 | 43.1 | 246.9 | 233.5 | 54.2 | 145.1 | 161.3 | 77.2
444 | 250 | 465.8 | 186.32 | 217.7973 | 235.2 | 230.3 | 231.9 | 221 | 528.6 | 25 | 20.9 | 50.4 | 6.8 | 245.3 | 17.5 | 394.9 | 838.9 | 790.4 | 417.7 | 688.1 | 705.1 | 735.4 | 806.9 | 306.6 | 722.7 | 23.1 | 55.7 | 88.2 | 43.3 | 247.1 | 233.8 | 54.4 | 145.6 | 162 | 77.5
445 | 251 | 465.9 | 186.36 | 217.8441 | 236.4 | 230.8 | 231.3 | 221.5 | 523.9 | 24.9 | 20.9 | 50.6 | 5.9 | 238.5 | 14.6 | 396.1 | 839.2 | 790.2 | 420.3 | 689.9 | 704.3 | 734.3 | 805.9 | 307.3 | 724.1 | 23.2 | 56 | 88.4 | 43.5 | 247 | 233.9 | 54.6 | 145.9 | 162.6 | 77.8
446 | 252 | 465.8 | 186.32 | 217.7973 | 237.2 | 231.4 | 231.7 | 221.9 | 512.3 | 24.9 | 20.9 | 50.6 | 4.6 | 244.6 | 13.7 | 397.2 | 835 | 784.1 | 423.1 | 692.5 | 701.6 | 735.3 | 803.5 | 308.2 | 727.4 | 23.3 | 56.2 | 88.6 | 43.7 | 247.3 | 233.9 | 54.9 | 146.3 | 163.3 | 78.1
447 | 253 | 466.5 | 186.6 | 218.1246 | 236.9 | 230.8 | 231.9 | 221.8 | 506 | 24.9 | 20.9 | 50.8 | 4.7 | 246.8 | 14.6 | 398.1 | 834.6 | 773.2 | 426.2 | 692.5 | 699.9 | 738.4 | 803.4 | 309.1 | 729.5 | 23.4 | 56.5 | 89.1 | 43.9 | 247.2 | 233.9 | 55.1 | 146.8 | 164.2 | 78.4
448 | 254 | 466.4 | 186.56 | 218.0779 | 236.2 | 230.2 | 231.8 | 221.2 | 506.2 | 24.9 | 20.9 | 50.9 | 4.7 | 240.1 | 13.7 | 398.7 | 833.4 | 776.7 | 429 | 693.2 | 697.9 | 740.3 | 800 | 309.9 | 730.3 | 23.5 | 56.7 | 89.6 | 44 | 247.2 | 234 | 55.3 | 147.3 | 165 | 78.6
449 | 255 | 466.2 | 186.48 | 217.9844 | 236 | 230.7 | 231.5 | 220.1 | 505.8 | 25 | 20.9 | 51.1 | 5.5 | 215.3 | 11.2 | 399.1 | 829 | 787.3 | 431.7 | 694.6 | 696.9 | 742.4 | 799.2 | 310.7 | 731.9 | 23.5 | 57 | 89.9 | 44.2 | 247.3 | 234.1 | 55.6 | 147.6 | 165.8 | 78.9
450 | 256 | 466.9 | 186.76 | 218.3117 | 235.7 | 230.3 | 232.6 | 218.8 | 509.7 | 25 | 20.9 | 51.2 | 5.9 | 221.9 | 10.5 | 399.6 | 829.2 | 791.9 | 434.1 | 694.1 | 696.9 | 747 | 802.7 | 311.5 | 732.9 | 23.6 | 57.2 | 90.1 | 44.4 | 247.3 | 234.2 | 55.8 | 148 | 166.6 | 79.2
451 | 257 | 466.7 | 186.68 | 218.2182 | 235.2 | 229.8 | 233.4 | 218.2 | 517.1 | 25.1 | 20.9 | 51.3 | 5.8 | 201.9 | 9.2 | 400.4 | 826.5 | 791.5 | 436.7 | 694.8 | 695 | 752.9 | 802 | 312.4 | 735.7 | 23.7 | 57.4 | 90.4 | 44.6 | 247.4 | 234.4 | 56 | 148.4 | 167.5 | 79.5
452 | 258 | 466.6 | 186.64 | 218.1714 | 235.3 | 228.9 | 232.9 | 217.7 | 523.9 | 25.2 | 20.9 | 51.4 | 4.9 | 217.5 | 13.1 | 401.3 | 818.8 | 800.3 | 439.4 | 695.9 | 693 | 759.1 | 806 | 313.3 | 738.8 | 23.8 | 57.7 | 90.7 | 44.7 | 248.6 | 234.8 | 56.2 | 149.1 | 168.4 | 79.8
453 | 259 | 466.6 | 186.64 | 218.1714 | 235.3 | 228.6 | 231.5 | 218 | 533 | 25.3 | 20.9 | 51.5 | 4.3 | 216.4 | 15.4 | 402.5 | 813.5 | 794.1 | 442.1 | 696.5 | 692.2 | 765 | 805.4 | 314.4 | 741.9 | 23.9 | 57.9 | 91.1 | 44.9 | 249.1 | 235.1 | 56.5 | 149.5 | 169.3 | 80.1
454 | 260 | 466.6 | 186.64 | 218.1714 | 235.1 | 228.6 | 230 | 218.3 | 541.4 | 25.4 | 20.9 | 51.6 | 4.8 | 223.3 | 13.2 | 403.7 | 816.8 | 792.2 | 444.9 | 697.7 | 690.4 | 768.2 | 807 | 315.5 | 745.1 | 23.9 | 58.2 | 91.6 | 45.1 | 249.5 | 235.3 | 56.7 | 150 | 170.4 | 80.4
455 | 261 | 465 | 186 | 217.4233 | 235.2 | 228.9 | 229.8 | 219.1 | 544 | 25.5 | 20.9 | 51.6 | 4.2 | 233.4 | 9.8 | 405.1 | 818.3 | 798.4 | 447.6 | 696.6 | 688.1 | 767.3 | 804.7 | 316.4 | 745.3 | 24 | 58.4 | 91.8 | 45.3 | 249.9 | 235.7 | 56.9 | 150.5 | 171.4 | 80.7
456 | 262 | 465.2 | 186.08 | 217.5168 | 235.1 | 229 | 229.7 | 219.2 | 542.8 | 25.6 | 20.9 | 51.7 | 4.8 | 242.3 | 8.7 | 406.2 | 818.3 | 807.1 | 450.1 | 698.8 | 686.2 | 765.5 | 802.5 | 317.3 | 745.9 | 24.1 | 58.7 | 92 | 45.4 | 250.3 | 236 | 57.1 | 150.9 | 172.3 | 81
457 | 263 | 466.4 | 186.56 | 218.0779 | 235.2 | 228.7 | 230.7 | 219 | 539.3 | 25.6 | 20.9 | 51.7 | 5 | 225.7 | 7.3 | 407.4 | 820.8 | 796.6 | 453.4 | 700.1 | 684.6 | 761 | 798.7 | 318.1 | 745.4 | 24.2 | 58.9 | 92.2 | 45.6 | 250.7 | 236.2 | 57.4 | 151.3 | 173.1 | 81.3
458 | 264 | 467.3 | 186.92 | 218.4987 | 236.4 | 229.2 | 230.6 | 217.9 | 527.4 | 25.7 | 20.9 | 51.8 | 4.6 | 211.9 | 7.7 | 408.4 | 819.1 | 782.3 | 456.8 | 699.8 | 682.7 | 755.3 | 789.2 | 318.9 | 744.2 | 24.3 | 59.2 | 92.7 | 45.8 | 250.7 | 236.7 | 57.7 | 151.9 | 173.9 | 81.6
459 | 265 | 467.5 | 187 | 218.5922 | 237.8 | 229.9 | 228.9 | 217.4 | 521.6 | 25.8 | 20.9 | 51.9 | 5 | 224.3 | 8.2 | 409.6 | 820 | 787 | 459.8 | 700.2 | 681.2 | 753.7 | 786.1 | 319.7 | 743.7 | 24.4 | 59.4 | 92.9 | 46 | 250.7 | 237.3 | 57.9 | 152.4 | 174.7 | 81.9
460 | 266 | 466 | 186.4 | 217.8909 | 237.8 | 229.2 | 228.1 | 216.3 | 519.8 | 25.9 | 20.9 | 52 | 5.2 | 220.7 | 7.6 | 411.2 | 821.3 | 789.1 | 462.8 | 699.6 | 680.8 | 755.1 | 789.5 | 320.4 | 743.1 | 24.4 | 59.7 | 93.3 | 46.2 | 250.8 | 238.8 | 58.1 | 152.9 | 175.4 | 82.2
461 | 267 | 465.2 | 186.08 | 217.5168 | 237.9 | 229.1 | 228.3 | 215.7 | 522.6 | 25.9 | 20.9 | 52.1 | 4.9 | 221.4 | 7.4 | 413 | 817.8 | 786.8 | 465.9 | 698.5 | 681.2 | 759.5 | 794.5 | 321.3 | 745.2 | 24.5 | 60 | 93.5 | 46.4 | 251.1 | 239 | 58.3 | 153.2 | 176.1 | 82.5
462 | 268 | 466 | 186.4 | 217.8909 | 237.9 | 229.5 | 229.1 | 216.8 | 526.1 | 25.9 | 20.9 | 52.3 | 4.6 | 223.7 | 7.1 | 414.9 | 815.3 | 788.5 | 468.8 | 697.6 | 681.8 | 763.8 | 800 | 322.2 | 745.8 | 24.6 | 60.2 | 93.8 | 46.5 | 252.2 | 239.2 | 58.5 | 153.5 | 176.9 | 82.8
463 | 269 | 465.3 | 186.12 | 217.5636 | 237.8 | 230 | 230 | 218.2 | 539.4 | 25.9 | 20.8 | 52.5 | 5.2 | 218.7 | 6.6 | 416.9 | 814 | 794.1 | 472.1 | 699.7 | 681.8 | 767.7 | 800.8 | 323.3 | 747.5 | 24.7 | 60.5 | 94.2 | 46.7 | 253.2 | 239.2 | 58.8 | 154 | 177.7 | 83.1
464 | 270 | 464.8 | 185.92 | 217.3298 | 237.9 | 230.3 | 230.4 | 219.8 | 537.8 | 26 | 20.8 | 52.7 | 5.4 | 248.9 | 5.9 | 419.2 | 815.5 | 788 | 475.5 | 699.8 | 682 | 766.3 | 803.7 | 324.4 | 749.6 | 24.8 | 60.8 | 94.6 | 46.9 | 253.1 | 239.5 | 59 | 154.5 | 178.5 | 83.4
465 | 271 | 465.8 | 186.32 | 217.7973 | 238.7 | 230.3 | 230.8 | 221.3 | 543.5 | 26 | 20.8 | 52.8 | 5.9 | 217.5 | 5.3 | 421.2 | 816.3 | 792.9 | 478.6 | 699.3 | 682.7 | 765 | 804.2 | 325.3 | 748.3 | 24.8 | 61.1 | 95 | 47.1 | 253.1 | 239.9 | 59.2 | 155 | 179.4 | 83.7
466 | 272 | 465.8 | 186.32 | 217.7973 | 239.3 | 231.5 | 230.2 | 221.6 | 544.5 | 26.2 | 20.8 | 52.9 | 6.2 | 215.8 | 6.6 | 423.4 | 814.6 | 798.2 | 481.9 | 700.4 | 683.2 | 767.4 | 805 | 326.3 | 748.2 | 24.9 | 61.3 | 95.2 | 47.3 | 253.1 | 240.3 | 59.5 | 155.5 | 180.3 | 84
467 | 273 | 465.9 | 186.36 | 217.8441 | 239.3 | 231.7 | 229.7 | 222.2 | 557.2 | 26.3 | 20.8 | 52.9 | 6 | 235.6 | 8 | 425.7 | 818.4 | 806.5 | 484.9 | 700.5 | 683.8 | 761.4 | 804.1 | 327.3 | 747 | 25 | 61.6 | 96 | 47.4 | 253.2 | 240.3 | 59.7 | 155.9 | 181 | 84.3
468 | 274 | 466.1 | 186.44 | 217.9376 | 241 | 232.1 | 228.8 | 222.9 | 557.6 | 26.4 | 20.8 | 52.8 | 5.5 | 223.4 | 9.5 | 427.9 | 817.4 | 811.6 | 488.4 | 700 | 684.2 | 753.9 | 801.9 | 328 | 745.5 | 25.1 | 61.8 | 96.1 | 47.6 | 253.5 | 240.3 | 59.9 | 156.2 | 181.8 | 84.6
469 | 275 | 466.2 | 186.48 | 217.9844 | 242 | 233.7 | 229.5 | 222.5 | 561.2 | 26.5 | 20.8 | 52.7 | 3.7 | 258.6 | 8.7 | 429.8 | 813.8 | 822.1 | 491.2 | 701.9 | 684.9 | 755.3 | 802.4 | 328.8 | 745.5 | 25.2 | 62.1 | 96.4 | 47.8 | 254.1 | 240.5 | 60.2 | 156.8 | 182.5 | 84.9
470 | 276 | 466.5 | 186.6 | 218.1246 | 242.1 | 233.9 | 230.8 | 222.3 | 563.1 | 26.5 | 20.8 | 52.7 | 4.3 | 232.9 | 7.7 | 432.3 | 806.1 | 818 | 494.5 | 708.9 | 683.9 | 758.4 | 801 | 329.7 | 748.8 | 25.3 | 62.3 | 96.7 | 48 | 254.5 | 241.1 | 60.4 | 157.3 | 183.2 | 85.2
471 | 277 | 465.9 | 186.36 | 217.8441 | 242.4 | 232.3 | 231.9 | 223.7 | 555 | 26.5 | 20.8 | 52.7 | 4.9 | 251.6 | 9.7 | 435.5 | 806.5 | 805.9 | 498.2 | 710 | 681.4 | 759.5 | 796.5 | 330.9 | 750.2 | 25.4 | 62.6 | 97.2 | 48.2 | 254.9 | 241.3 | 60.7 | 157.8 | 184.3 | 85.5
472 | 278 | 465.8 | 186.32 | 217.7973 | 242.4 | 231.8 | 232.7 | 225 | 547.6 | 26.6 | 20.8 | 52.7 | 5 | 226.4 | 10.1 | 438.1 | 804.6 | 797.6 | 501.4 | 710.5 | 679.5 | 760.1 | 794.6 | 332.1 | 750.7 | 25.5 | 62.9 | 97.4 | 48.4 | 254.9 | 242 | 60.9 | 158.4 | 185.4 | 85.9
473 | 279 | 467.3 | 186.92 | 218.4987 | 241.9 | 232.2 | 234 | 225.2 | 539.6 | 26.6 | 20.8 | 52.8 | 5.6 | 240.2 | 10.6 | 441.1 | 803.2 | 790.2 | 504.5 | 709.2 | 678.4 | 760.9 | 788.9 | 333.1 | 750.7 | 25.5 | 63.1 | 97.7 | 48.5 | 254.7 | 242.3 | 61.1 | 158.8 | 186.3 | 86.2
474 | 280 | 465.8 | 186.32 | 217.7973 | 241.5 | 232.4 | 234.2 | 224.5 | 531.5 | 26.8 | 20.8 | 53 | 5.8 | 248.8 | 10 | 444.3 | 802.2 | 775.3 | 507.4 | 708.8 | 677.4 | 756.7 | 777.5 | 334.1 | 749.7 | 25.6 | 63.3 | 98 | 48.7 | 254.8 | 242.3 | 61.4 | 159.1 | 187.1 | 86.5
475 | 281 | 466.3 | 186.52 | 218.0311 | 241.3 | 233 | 233.4 | 223.8 | 523.6 | 26.9 | 20.8 | 53.2 | 4.9 | 237.2 | 10.5 | 447.5 | 798.8 | 770.2 | 510.2 | 709.2 | 676.4 | 756.1 | 773.5 | 335.1 | 750.7 | 25.7 | 63.6 | 98.3 | 48.9 | 255 | 242.7 | 61.6 | 159.6 | 187.9 | 86.8
476 | 282 | 466.1 | 186.44 | 217.9376 | 241.7 | 234.5 | 233.7 | 222.7 | 519.5 | 27.1 | 20.8 | 53.3 | 5.6 | 248.7 | 11.1 | 450.4 | 799.2 | 759.3 | 513.6 | 709.3 | 675.1 | 754.7 | 766 | 336.4 | 752.4 | 25.8 | 63.8 | 98.7 | 49.1 | 255.1 | 243 | 61.9 | 160 | 188.8 | 87.1
477 | 283 | 466 | 186.4 | 217.8909 | 242.7 | 234.8 | 234.5 | 221.8 | 515.8 | 27.1 | 20.8 | 53.5 | 5.4 | 232 | 11.5 | 453.3 | 801 | 762 | 517.2 | 709.4 | 674.6 | 756.4 | 759.9 | 337.5 | 752 | 25.9 | 64.1 | 99.1 | 49.3 | 255.6 | 243.5 | 62.1 | 160.4 | 189.7 | 87.3
478 | 284 | 466.3 | 186.52 | 218.0311 | 243.7 | 234.9 | 235.5 | 221.2 | 514.6 | 27.1 | 20.8 | 53.5 | 4.7 | 219.9 | 12.2 | 456.3 | 803 | 761 | 520.5 | 709.7 | 675.5 | 754.6 | 754.2 | 338.8 | 752.6 | 26 | 64.3 | 99.3 | 49.5 | 256.2 | 243.9 | 62.3 | 160.9 | 190.6 | 87.7
479 | 285 | 467.9 | 187.16 | 218.7793 | 245 | 235.7 | 235.9 | 222.5 | 514 | 27.1 | 20.8 | 53.4 | 4 | 238.4 | 9.3 | 459.1 | 804.5 | 757.7 | 523.5 | 709.5 | 676 | 752.4 | 749.7 | 339.8 | 751.4 | 26.1 | 64.5 | 99.6 | 49.7 | 257 | 244.1 | 62.6 | 161.3 | 191.6 | 88
480 | 286 | 467.9 | 187.16 | 218.7793 | 245.3 | 236.6 | 237.2 | 223.6 | 512.9 | 27.1 | 20.8 | 53.4 | 5 | 262.5 | 6.6 | 461.4 | 799.9 | 756.6 | 526.4 | 708.6 | 676.8 | 752.9 | 755.1 | 341 | 752.3 | 26.2 | 64.8 | 99.8 | 49.8 | 257.5 | 244.5 | 62.8 | 161.9 | 192.4 | 88.3
481 | 287 | 467.7 | 187.08 | 218.6857 | 245 | 237 | 237.4 | 224.5 | 506.7 | 27.2 | 20.8 | 53.4 | 4.4 | 221.9 | 6.6 | 463.6 | 794.3 | 750.6 | 529.4 | 708.2 | 675.8 | 748.9 | 745.6 | 342.2 | 751.5 | 26.3 | 65 | 100 | 50 | 258.1 | 245 | 63 | 162.2 | 193.2 | 88.6
482 | 288 | 467.3 | 186.92 | 218.4987 | 245.7 | 236.4 | 237 | 225.7 | 507 | 27.4 | 20.8 | 53.4 | 4.6 | 216.9 | 8.2 | 466.3 | 799 | 751.2 | 532.8 | 707.2 | 676.1 | 745.1 | 746.6 | 343.4 | 749.7 | 26.3 | 65.3 | 100.4 | 50.2 | 258.7 | 245.5 | 63.2 | 162.7 | 194.1 | 88.9
483 | 289 | 467.5 | 187 | 218.5922 | 246.6 | 236.8 | 237.7 | 227.2 | 502.9 | 27.4 | 20.8 | 53.5 | 4.7 | 225.5 | 7.7 | 469.2 | 797.6 | 762.1 | 536.3 | 708.9 | 676.7 | 744.1 | 749.8 | 344.4 | 750.8 | 26.4 | 65.5 | 100.7 | 50.4 | 259.1 | 245.6 | 63.5 | 163.1 | 194.8 | 89.2
484 | 290 | 467.3 | 186.92 | 218.4987 | 246.6 | 237.3 | 239.5 | 227.1 | 502.7 | 27.4 | 20.8 | 53.6 | 4.9 | 249.1 | 6.7 | 472.3 | 798.2 | 770.7 | 539.5 | 708.9 | 678.4 | 743.7 | 758.5 | 345.5 | 750.6 | 26.5 | 65.8 | 101.1 | 50.6 | 259.1 | 245.6 | 63.7 | 163.4 | 195.5 | 89.5
485 | 291 | 467.2 | 186.88 | 218.452 | 246.3 | 237.5 | 240 | 227.7 | 512.2 | 27.3 | 20.8 | 53.7 | 4.5 | 229.9 | 7.1 | 475.7 | 796.1 | 766.2 | 542.3 | 707.4 | 680.3 | 745 | 759.6 | 346.7 | 749.4 | 26.6 | 66 | 101.3 | 50.8 | 259.4 | 245.6 | 64 | 163.7 | 196.2 | 89.8
486 | 292 | 466.3 | 186.52 | 218.0311 | 246.1 | 236.3 | 240.2 | 227.8 | 509 | 27.3 | 20.8 | 53.9 | 4.6 | 202 | 8 | 479 | 794.1 | 768.9 | 545.7 | 707.8 | 679.4 | 744.9 | 754 | 347.7 | 749 | 26.7 | 66.2 | 101.6 | 51 | 259.7 | 245.7 | 64.2 | 164.1 | 196.9 | 90.1
487 | 293 | 467.1 | 186.84 | 218.4052 | 245.9 | 235.9 | 240.8 | 227.3 | 506.3 | 27.3 | 20.8 | 54.1 | 5.1 | 207 | 8 | 481.9 | 790 | 771.3 | 549 | 709 | 678.7 | 745.3 | 752.5 | 348.7 | 749.4 | 26.8 | 66.5 | 101.8 | 51.1 | 259.6 | 245.7 | 64.5 | 164.4 | 197.6 | 90.4
488 | 294 | 466.5 | 186.6 | 218.1246 | 245.6 | 236.1 | 240.6 | 226.4 | 500 | 27.3 | 20.7 | 54.2 | 5.5 | 243.6 | 7.1 | 485.1 | 784.8 | 778 | 552.3 | 711 | 679.6 | 748.8 | 757.7 | 349.8 | 751.4 | 26.9 | 66.7 | 102 | 51.3 | 259.4 | 245.6 | 64.7 | 164.8 | 198.3 | 90.7
489 | 295 | 466.9 | 186.76 | 218.3117 | 245.6 | 236 | 240.3 | 226.5 | 506.6 | 27.4 | 20.8 | 54.3 | 5.3 | 238.9 | 8.5 | 488.6 | 784.8 | 790 | 555.9 | 711.9 | 682.2 | 750.2 | 762.3 | 351.2 | 751.4 | 27 | 66.9 | 102.4 | 51.5 | 259.7 | 245.7 | 64.9 | 165.3 | 199.1 | 91
490 | 296 | 466.9 | 186.76 | 218.3117 | 245.3 | 235.6 | 239.6 | 226.8 | 512.7 | 27.5 | 20.8 | 54.4 | 5.6 | 242.7 | 6.9 | 492 | 783.7 | 799.4 | 559.5 | 713.5 | 686.4 | 753.4 | 768.3 | 352.4 | 752.9 | 27 | 67.2 | 102.7 | 51.7 | 260.1 | 245.9 | 65.2 | 165.7 | 199.9 | 91.3
491 | 297 | 466.9 | 186.76 | 218.3117 | 245 | 235.3 | 238.8 | 228 | 523.6 | 27.4 | 20.8 | 54.4 | 6.2 | 262.6 | 6.7 | 495.9 | 786 | 807.4 | 563.3 | 713.6 | 689.9 | 756.2 | 774.2 | 353.9 | 754 | 27.1 | 67.4 | 103.1 | 51.9 | 260.2 | 245.7 | 65.4 | 166.1 | 200.8 | 91.5
492 | 298 | 467.3 | 186.92 | 218.4987 | 245.3 | 235.2 | 237.1 | 228.8 | 531.6 | 27.5 | 20.7 | 54.5 | 6.1 | 235.8 | 7.3 | 500 | 784.2 | 815.7 | 566.5 | 717.4 | 692.7 | 759.2 | 778.8 | 355.2 | 755.7 | 27.2 | 67.7 | 103.3 | 52.1 | 260.2 | 245.6 | 65.6 | 166.4 | 201.7 | 91.8
493 | 299 | 467.2 | 186.88 | 218.452 | 245.6 | 235.2 | 236 | 227.8 | 538.9 | 27.6 | 20.7 | 54.5 | 5.9 | 251.6 | 7.6 | 504.4 | 782.8 | 821.3 | 569.8 | 719.5 | 695 | 759.1 | 781.3 | 356.5 | 757.3 | 27.3 | 67.9 | 103.7 | 52.3 | 260.2 | 245.6 | 65.9 | 166.8 | 202.6 | 92.2
494 | 300 | 467.2 | 186.88 | 218.452 | 245.3 | 235.2 | 235.3 | 227.9 | 548.3 | 27.7 | 20.7 | 54.4 | 5.1 | 257.5 | 7.3 | 509.3 | 781.9 | 819.8 | 573.2 | 718.8 | 697.8 | 755.2 | 783.3 | 357.8 | 757 | 27.4 | 68.2 | 104 | 52.5 | 260.7 | 245.6 | 66.1 | 167.1 | 203.4 | 92.5
495 | 301 | 467.2 | 186.88 | 218.452 | 246.3 | 235.8 | 234.1 | 229.9 | 560.1 | 27.8 | 20.7 | 54.3 | 4.8 | 248.8 | 9 | 513.8 | 783.4 | 808.7 | 577.4 | 716.1 | 701 | 750.4 | 782.5 | 359 | 754.8 | 27.5 | 68.4 | 104.6 | 52.7 | 261 | 245.6 | 66.4 | 167.5 | 204.2 | 92.8
496 | 302 | 467.3 | 186.92 | 218.4987 | 249.2 | 236 | 234 | 232.3 | 571.1 | 27.9 | 20.7 | 54.2 | 4.5 | 227.6 | 10.1 | 518.8 | 788.9 | 792.9 | 581.3 | 712.4 | 704 | 741.3 | 777.8 | 359.8 | 751.6 | 27.6 | 68.7 | 105.3 | 52.9 | 261.5 | 245.7 | 66.6 | 168 | 205 | 93.1
497 | 303 | 467 | 186.8 | 218.3584 | 250.6 | 235.6 | 235 | 234.8 | 571.2 | 28.1 | 20.7 | 54 | 4.1 | 255.5 | 10.6 | 525.7 | 790.8 | 792.9 | 583.4 | 711.7 | 705.9 | 734.3 | 775.4 | 360.4 | 749.8 | 27.7 | 68.9 | 105.7 | 53 | 262.4 | 245.9 | 66.9 | 168.4 | 205.8 | 93.4
498 | 304 | 467.2 | 186.88 | 218.452 | 251.4 | 236.2 | 236.4 | 236.8 | 562.8 | 28.2 | 20.7 | 54 | 4.1 | 204.9 | 10.8 | 532 | 792.7 | 799.9 | 585.1 | 714.5 | 707.1 | 730.6 | 774.8 | 361 | 749.6 | 27.8 | 69.2 | 105.9 | 53.2 | 262.9 | 246 | 67.1 | 168.9 | 206.4 | 93.8
499 | 305 | 467.5 | 187 | 218.5922 | 251.5 | 236.9 | 237.5 | 237.2 | 564.6 | 28.3 | 20.7 | 53.9 | 4.3 | 221.8 | 9.7 | 538.3 | 791.8 | 810.7 | 586.8 | 715 | 709.8 | 726.7 | 773.4 | 361.6 | 748.1 | 27.9 | 69.5 | 106.3 | 53.4 | 262.8 | 246.2 | 67.4 | 169.2 | 207.1 | 94.1
500 | 306 | 466.9 | 186.76 | 218.3117 | 251.1 | 235.4 | 238 | 236.9 | 571.4 | 28.4 | 20.7 | 54 | 4.8 | 237.7 | 8.6 | 545 | 792.6 | 811.6 | 588.7 | 715.1 | 713.3 | 727.6 | 773.5 | 362.5 | 746.6 | 27.9 | 69.7 | 107 | 53.6 | 263.4 | 246.6 | 67.6 | 169.5 | 207.7 | 94.4
501 | 307 | 466.8 | 186.72 | 218.2649 | 251.4 | 234 | 239.4 | 237.7 | 582.5 | 28.4 | 20.7 | 54.1 | 4.8 | 237.7 | 9 | 550.6 | 789.4 | 817.4 | 589.8 | 716.8 | 715.8 | 728.3 | 776.9 | 363.5 | 745.8 | 28 | 70 | 107.4 | 53.8 | 263.9 | 246.8 | 67.8 | 170 | 208.4 | 94.7
502 | 308 | 465.8 | 186.32 | 217.7973 | 252 | 233.8 | 240 | 238.5 | 591.6 | 28.5 | 20.7 | 54.3 | 5.2 | 206.1 | 9 | 555.9 | 786.8 | 822.8 | 591.1 | 720 | 716.2 | 727.7 | 779.3 | 364.3 | 746.5 | 28.1 | 70.2 | 107.6 | 54 | 264.7 | 247.1 | 68.1 | 170.3 | 209 | 95
503 | 309 | 465.3 | 186.12 | 217.5636 | 252.1 | 235.4 | 240.8 | 239.9 | 580.6 | 28.6 | 20.7 | 54.5 | 5.1 | 198.4 | 10.2 | 561 | 785.8 | 817 | 592.8 | 722.9 | 714.4 | 730.2 | 778 | 365.4 | 747.8 | 28.2 | 70.5 | 107.7 | 54.2 | 265.2 | 247.6 | 68.4 | 170.8 | 209.8 | 95.4
504 | 310 | 466.4 | 186.56 | 218.0779 | 251.9 | 237.4 | 241.8 | 241.7 | 565.7 | 28.6 | 20.7 | 54.6 | 4.9 | 202.8 | 10.7 | 567.2 | 783.1 | 807.5 | 595.4 | 724.9 | 713.5 | 730.8 | 773.6 | 366.6 | 748.7 | 28.3 | 70.8 | 108 | 54.4 | 265.6 | 248.2 | 68.5 | 171.3 | 210.5 | 95.7
505 | 311 | 466.8 | 186.72 | 218.2649 | 251.6 | 238 | 242 | 243.2 | 556.1 | 28.7 | 20.7 | 54.7 | 4.4 | 187.8 | 9 | 572.9 | 781.7 | 806 | 597.8 | 723.9 | 714.6 | 728.9 | 777.2 | 368 | 748 | 28.4 | 71 | 108.4 | 54.5 | 265.8 | 248.5 | 68.8 | 171.8 | 211.2 | 96
506 | 312 | 466.8 | 186.72 | 218.2649 | 251.4 | 237.8 | 242.2 | 243.3 | 551.7 | 28.6 | 20.7 | 54.8 | 4.3 | 224.3 | 7.5 | 578.4 | 777.3 | 812.7 | 599.1 | 725.6 | 716.3 | 733.4 | 780.5 | 369.3 | 748.3 | 28.5 | 71.3 | 108.7 | 54.7 | 266.1 | 248.7 | 69 | 172.3 | 211.9 | 96.3
507 | 313 | 466.3 | 186.52 | 218.0311 | 250.8 | 238.7 | 242.9 | 241.9 | 551.2 | 28.6 | 20.7 | 54.8 | 4.3 | 243.6 | 6.8 | 584.3 | 773.9 | 810.8 | 600.2 | 726.6 | 716.9 | 733.6 | 780.7 | 371 | 749.6 | 28.6 | 71.6 | 108.9 | 54.9 | 266.7 | 249 | 69.3 | 172.7 | 212.6 | 96.6
508 | 314 | 466.7 | 186.68 | 218.2182 | 250.8 | 240.3 | 243.7 | 241.6 | 548.9 | 28.6 | 20.7 | 54.9 | 4.4 | 235.3 | 6.1 | 590.1 | 773.2 | 800.8 | 602.1 | 723.7 | 717.1 | 735.5 | 781.7 | 372.8 | 750.3 | 28.7 | 71.9 | 109.3 | 55.1 | 266.6 | 249 | 69.5 | 173.2 | 213.3 | 97
509 | 315 | 466.9 | 186.76 | 218.3117 | 250.7 | 240.4 | 243.9 | 241.7 | 541.6 | 28.5 | 20.7 | 55.1 | 4.3 | 267.9 | 5.1 | 595.5 | 772.4 | 791 | 603.2 | 720.2 | 719.2 | 729.4 | 775.7 | 374.4 | 748.4 | 28.8 | 72.2 | 109.5 | 55.3 | 266.3 | 249 | 69.8 | 173.6 | 214 | 97.2
510 | 316 | 466.3 | 186.52 | 218.0311 | 250.7 | 240.3 | 244.1 | 242.2 | 523.9 | 28.5 | 20.7 | 55.2 | 4.7 | 266.7 | 4.8 | 601 | 771.6 | 787.8 | 603.9 | 722 | 721.8 | 725.4 | 767 | 376.3 | 747.3 | 28.9 | 72.4 | 109.9 | 55.5 | 266 | 249.1 | 70 | 174 | 214.7 | 97.5
511 | 317 | 466.6 | 186.64 | 218.1714 | 250.8 | 240.1 | 243.2 | 241 | 512.1 | 28.6 | 20.7 | 55.5 | 4.5 | 179.9 | 4.8 | 606.4 | 773.2 | 775.8 | 604.5 | 718.9 | 724.5 | 717 | 757.3 | 378.1 | 743.5 | 29 | 72.7 | 110.1 | 55.7 | 265.8 | 249.2 | 70.3 | 174.4 | 215.4 | 97.8
512 | 318 | 466.5 | 186.6 | 218.1246 | 250.8 | 239.7 | 242.7 | 239.4 | 502.2 | 28.6 | 20.7 | 55.7 | 4.6 | 188 | 4.1 | 611.8 | 773 | 774.9 | 604.4 | 717.1 | 728.2 | 707.2 | 748 | 379.6 | 740 | 29.1 | 73 | 110.4 | 55.9 | 265.5 | 249.1 | 70.5 | 174.8 | 216 | 98.1
513 | 319 | 466.3 | 186.52 | 218.0311 | 251.1 | 239.2 | 242.9 | 240 | 495.1 | 28.6 | 20.7 | 55.9 | 4.1 | 226.6 | 4.7 | 617.4 | 772.8 | 759.8 | 604.7 | 713.4 | 732.9 | 702.4 | 741.1 | 381.3 | 736.9 | 29.2 | 73.3 | 110.6 | 56.1 | 266.4 | 249 | 70.8 | 175.2 | 216.5 | 98.4
514 | 320 | 466.5 | 186.6 | 218.1246 | 250.6 | 238.6 | 243.4 | 240.5 | 493 | 28.6 | 20.7 | 56.1 | 3.8 | 245.4 | 4.3 | 623.5 | 768.8 | 762.3 | 604.9 | 713.8 | 735.9 | 696.9 | 735.6 | 382.9 | 734.5 | 29.3 | 73.5 | 110.8 | 56.3 | 266.4 | 248.9 | 71 | 175.5 | 217 | 98.8
515 | 321 | 467.1 | 186.84 | 218.4052 | 249.8 | 238 | 244.4 | 240.5 | 489.6 | 28.7 | 20.7 | 56.2 | 4.5 | 247 | 3.7 | 630.2 | 771.9 | 755.8 | 605.7 | 713.8 | 739.6 | 696.8 | 736.3 | 384.9 | 733.1 | 29.4 | 73.8 | 111.1 | 56.5 | 266.1 | 249 | 71.2 | 175.9 | 217.5 | 99.1
516 | 322 | 466.7 | 186.68 | 218.2182 | 249.5 | 237.5 | 245.5 | 240.3 | 488.3 | 28.8 | 20.7 | 56.3 | 5.5 | 218.3 | 3.3 | 636.8 | 771.4 | 750.3 | 605.8 | 712.6 | 743.5 | 702.2 | 737.4 | 387.1 | 732.1 | 29.4 | 74.1 | 111.4 | 56.6 | 265.9 | 248.9 | 71.5 | 176.2 | 218.1 | 99.4
517 | 323 | 466.3 | 186.52 | 218.0311 | 249.4 | 236.9 | 246.1 | 240 | 488.3 | 28.9 | 20.7 | 56.4 | 5.5 | 211.6 | 3.3 | 643.1 | 770.1 | 751.3 | 606.2 | 711.9 | 746 | 705.1 | 734.9 | 389 | 730.1 | 29.5 | 74.4 | 111.7 | 56.8 | 266 | 249.1 | 71.7 | 176.5 | 218.6 | 99.7
518 | 324 | 466.6 | 186.64 | 218.1714 | 249.9 | 236.4 | 245.6 | 239.8 | 489.9 | 29 | 20.7 | 56.6 | 5.3 | 239.8 | 3.9 | 649.7 | 766.8 | 761.2 | 606.7 | 713.3 | 748.2 | 706.6 | 740.9 | 391 | 731 | 29.6 | 74.7 | 112 | 57 | 266 | 249.1 | 72 | 176.9 | 219.1 | 100
519 | 325 | 467 | 186.8 | 218.3584 | 249.7 | 236.2 | 247 | 240 | 488.2 | 29 | 20.7 | 56.6 | 5.3 | 244.9 | 4.8 | 656.7 | 767.3 | 760.6 | 607.7 | 712.2 | 748.7 | 707 | 741.9 | 393.2 | 731.1 | 29.7 | 74.9 | 112.4 | 57.2 | 265.9 | 249.1 | 72.2 | 177.3 | 219.7 | 100.3
520 | 326 | 467 | 186.8 | 218.3584 | 249.6 | 236 | 247.5 | 240 | 486.6 | 29.1 | 20.7 | 56.7 | 5.6 | 262.4 | 5.7 | 662.7 | 766.9 | 743.9 | 608.2 | 709.6 | 747.9 | 708.8 | 736.7 | 395.7 | 728.9 | 29.8 | 75.2 | 112.6 | 57.4 | 266 | 249.5 | 72.4 | 177.7 | 220.4 | 100.6
521 | 327 | 466.9 | 186.76 | 218.3117 | 250.4 | 235.7 | 247.1 | 240.5 | 483 | 29.2 | 20.7 | 56.7 | 5.3 | 238.4 | 7 | 668.6 | 767.4 | 737.7 | 608.3 | 706.9 | 747 | 708.7 | 736.4 | 398 | 726.2 | 29.9 | 75.5 | 112.9 | 57.6 | 265.9 | 249.6 | 72.7 | 178.1 | 220.9 | 100.9
522 | 328 | 467.4 | 186.96 | 218.5455 | 250.8 | 235.4 | 247.3 | 240.5 | 482 | 29.3 | 20.7 | 56.8 | 5.8 | 248.2 | 8.2 | 674.9 | 766.1 | 751 | 608.8 | 707.7 | 747.2 | 712.8 | 744.7 | 400.4 | 725.8 | 30 | 75.7 | 113.3 | 57.8 | 265.7 | 250.2 | 73 | 178.6 | 221.4 | 101.2
523 | 329 | 467.2 | 186.88 | 218.452 | 251 | 234.6 | 247.8 | 239.6 | 482.1 | 29.2 | 20.7 | 56.8 | 5.4 | 251.1 | 9.3 | 680.9 | 765.6 | 765.5 | 609.7 | 712.9 | 748.5 | 710.8 | 749 | 402.5 | 728.4 | 30.1 | 76 | 113.3 | 58 | 265.4 | 250.9 | 73.2 | 179 | 222 | 101.5
524 | 330 | 466.2 | 186.48 | 217.9844 | 250.8 | 233.1 | 248.1 | 238.8 | 487.4 | 29.3 | 20.7 | 56.8 | 5.2 | 260.4 | 10 | 687 | 765 | 778 | 610.6 | 714.6 | 751.3 | 711.2 | 754.7 | 404.5 | 729.9 | 30.2 | 76.3 | 113.8 | 58.2 | 265.7 | 250.9 | 73.4 | 179.4 | 222.6 | 101.8
525 | 331 | 465.9 | 186.36 | 217.8441 | 250.5 | 232.4 | 248.7 | 238.5 | 499.5 | 29.4 | 20.7 | 56.7 | 4.3 | 257.8 | 13.6 | 692.8 | 762.9 | 780.6 | 611.4 | 716.8 | 751.3 | 712.2 | 756.7 | 406.4 | 729.8 | 30.3 | 76.5 | 114 | 58.4 | 265.8 | 250.9 | 73.7 | 179.8 | 223.3 | 102.1
526 | 332 | 466.3 | 186.52 | 218.0311 | 250.5 | 231.9 | 249.8 | 238.7 | 495 | 29.5 | 20.7 | 56.7 | 4.5 | 247 | 16.6 | 698.6 | 760.7 | 777.2 | 612.1 | 715.3 | 749 | 711.9 | 754 | 408.8 | 730.4 | 30.4 | 76.7 | 114.2 | 58.5 | 265.5 | 251.2 | 74 | 180.2 | 224 | 102.4
527 | 333 | 467.6 | 187.04 | 218.639 | 250.4 | 232.6 | 249.7 | 238.4 | 490.3 | 29.5 | 20.7 | 56.7 | 5.3 | 245.1 | 16.9 | 703.8 | 758.5 | 780 | 612.3 | 716 | 750.3 | 717.3 | 762.9 | 411.1 | 731.6 | 30.5 | 77 | 114.6 | 58.7 | 265.3 | 251.5 | 74.2 | 180.5 | 224.7 | 102.7
528 | 334 | 470.1 | 188.04 | 219.8079 | 250.6 | 233.2 | 249.5 | 237.4 | 505 | 29.6 | 20.7 | 56.6 | 5.6 | 248.6 | 15.6 | 709.1 | 758.6 | 782.8 | 613 | 716.8 | 754 | 724 | 768.8 | 413.8 | 733.2 | 30.6 | 77.3 | 115 | 58.9 | 265.7 | 251.6 | 74.4 | 181 | 225.4 | 103
529 | 335 | 468 | 187.2 | 218.826 | 251 | 233.3 | 249.2 | 237.7 | 514.5 | 29.6 | 20.7 | 56.6 | 5.7 | 255.5 | 15.4 | 714.9 | 762.7 | 778.1 | 614.3 | 713.7 | 756.4 | 725.8 | 772.3 | 416.4 | 734.8 | 30.7 | 77.5 | 115.4 | 59.1 | 266 | 251.7 | 74.7 | 181.4 | 226.1 | 103.3
530 | 336 | 467.6 | 187.04 | 218.639 | 251.2 | 233.6 | 248.3 | 238.6 | 515.8 | 29.7 | 20.7 | 56.6 | 7.1 | 253.5 | 16.1 | 720.5 | 760 | 775 | 615.2 | 714.4 | 758.9 | 727.5 | 772.8 | 418.6 | 735.1 | 30.8 | 77.7 | 115.5 | 59.3 | 265.9 | 252.2 | 74.9 | 181.8 | 226.8 | 103.6
531 | 337 | 467.5 | 187 | 218.5922 | 250.8 | 233.5 | 248.2 | 239.5 | 514.4 | 29.7 | 20.7 | 56.7 | 7.4 | 252 | 19.8 | 726.2 | 757.2 | 771.7 | 616.2 | 715.7 | 762.4 | 730.7 | 776.2 | 420.2 | 735.5 | 30.9 | 78 | 115.7 | 59.5 | 265.9 | 252.6 | 75.2 | 182.2 | 227.5 | 103.9
532 | 338 | 467.1 | 186.84 | 218.4052 | 250.5 | 234.1 | 248.4 | 238.3 | 525.3 | 29.7 | 20.7 | 56.8 | 6.3 | 248.3 | 19.1 | 731.9 | 755.3 | 772.1 | 617.1 | 715.2 | 767.1 | 735.2 | 779.8 | 421.9 | 735.1 | 31 | 78.2 | 116.1 | 59.7 | 265.5 | 253.2 | 75.4 | 182.7 | 228.2 | 104.2
533 | 339 | 467 | 186.8 | 218.3584 | 250.7 | 234.4 | 248.8 | 238.9 | 529.1 | 29.7 | 20.7 | 56.8 | 5.3 | 256.3 | 17.2 | 737.5 | 755.7 | 765.7 | 618.1 | 713.4 | 770.3 | 738 | 776.4 | 423.8 | 736.5 | 31.1 | 78.5 | 116.3 | 59.9 | 265.2 | 253.6 | 75.6 | 183.1 | 228.8 | 104.5
534 | 340 | 467.4 | 186.96 | 218.5455 | 250.7 | 233.6 | 248.3 | 239.6 | 525.3 | 29.8 | 20.7 | 56.8 | 5.4 | 256.9 | 16.1 | 742.7 | 754.2 | 765.6 | 618.9 | 712.6 | 771.9 | 739.1 | 774.9 | 425.1 | 734.4 | 31.2 | 78.8 | 116.8 | 60.1 | 265 | 253.6 | 75.9 | 183.5 | 229.5 | 104.7
535 | 341 | 468.2 | 187.28 | 218.9195 | 251.1 | 233.9 | 248.9 | 239.9 | 526 | 29.8 | 20.7 | 56.8 | 6.1 | 256.5 | 16 | 748.3 | 753.6 | 773.7 | 620.2 | 713.3 | 774.6 | 736.8 | 775.1 | 426.5 | 734.5 | 31.3 | 79 | 117.2 | 60.3 | 264.9 | 253.5 | 76.2 | 183.9 | 230.2 | 105
536 | 342 | 468.1 | 187.24 | 218.8728 | 251.7 | 234.9 | 249.1 | 239.4 | 538.2 | 29.8 | 20.6 | 56.7 | 6 | 241.5 | 17.8 | 754.1 | 754.5 | 765.5 | 621.4 | 709 | 775.1 | 729.9 | 764 | 427.6 | 731.2 | 31.4 | 79.3 | 117.6 | 60.5 | 265.6 | 253.4 | 76.4 | 184.2 | 230.8 | 105.3
537 | 343 | 468 | 187.2 | 218.826 | 252.4 | 234.7 | 249.5 | 239.3 | 535.1 | 29.8 | 20.6 | 56.7 | 6.6 | 243.5 | 14.7 | 759.8 | 755.7 | 760.3 | 622.7 | 704.3 | 773.7 | 718 | 748.7 | 428.2 | 727 | 31.5 | 79.6 | 117.9 | 60.7 | 266.4 | 253.3 | 76.7 | 184.6 | 231.5 | 105.7
538 | 344 | 468.3 | 187.32 | 218.9663 | 254.5 | 234.5 | 249.9 | 240.8 | 533.7 | 29.9 | 20.6 | 56.8 | 6.1 | 246.9 | 16.2 | 764.9 | 754.2 | 753.8 | 623.7 | 702.8 | 774.4 | 718.3 | 741.1 | 429.1 | 724.1 | 31.6 | 79.8 | 118.4 | 60.9 | 267 | 253.3 | 76.9 | 185 | 232.1 | 106
539 | 345 | 468.2 | 187.28 | 218.9195 | 255.7 | 235 | 250.1 | 241.9 | 523 | 29.9 | 20.6 | 56.9 | 6 | 251.5 | 17.7 | 770.8 | 753.7 | 748.5 | 624.8 | 702.5 | 773.6 | 716.6 | 734.3 | 430.1 | 721.4 | 31.8 | 80.1 | 118.5 | 61 | 267.5 | 253.5 | 77.2 | 185.4 | 232.6 | 106.3
540 | 346 | 468.1 | 187.24 | 218.8728 | 256.5 | 235 | 250 | 243 | 517.7 | 29.9 | 20.6 | 57 | 6 | 255.5 | 17.3 | 775.2 | 751.9 | 758 | 626 | 704.7 | 774.1 | 710.2 | 731.7 | 431.3 | 720.9 | 31.8 | 80.3 | 118.8 | 61.2 | 267.9 | 253.9 | 77.4 | 185.9 | 233.1 | 106.6
541 | 347 | 467.1 | 186.84 | 218.4052 | 256.8 | 235 | 250.2 | 243.3 | 515.3 | 29.9 | 20.6 | 57.1 | 5.8 | 240.9 | 15.3 | 780.3 | 752.1 | 749.6 | 627.1 | 701.4 | 775 | 705.3 | 727.7 | 432.4 | 718.1 | 32 | 80.6 | 119 | 61.4 | 267.9 | 254.5 | 77.7 | 186.4 | 233.6 | 107
542 | 348 | 467.4 | 186.96 | 218.5455 | 257.2 | 234.1 | 251.6 | 243.3 | 516.4 | 29.9 | 20.6 | 57.2 | 6.1 | 226.8 | 15.1 | 785.2 | 752 | 736.2 | 628.1 | 699.6 | 776.7 | 704.1 | 724.6 | 433.4 | 715.9 | 32.1 | 80.8 | 119.3 | 61.6 | 267.9 | 254.7 | 77.9 | 186.8 | 234.1 | 107.3
543 | 349 | 467.8 | 187.12 | 218.7325 | 257.6 | 233.8 | 252.9 | 242.6 | 511.8 | 30 | 20.6 | 57.4 | 5.7 | 238.6 | 12.1 | 790.8 | 753.8 | 729.8 | 629.5 | 696.1 | 777.2 | 704.3 | 721.3 | 434.6 | 713.4 | 32.2 | 81.1 | 119.7 | 61.8 | 268 | 255.2 | 78.2 | 187.3 | 234.6 | 107.6
544 | 350 | 466.9 | 186.76 | 218.3117 | 257.9 | 234.1 | 253.1 | 242.3 | 500.1 | 30 | 20.6 | 57.6 | 5.6 | 240.2 | 11.5 | 795.2 | 754 | 735 | 630.8 | 695.9 | 777.2 | 701 | 714.5 | 435.7 | 713.2 | 32.3 | 81.4 | 120 | 62 | 268.3 | 255.5 | 78.4 | 187.7 | 235.1 | 107.9
545 | 351 | 467.3 | 186.92 | 218.4987 | 258.3 | 234.5 | 253.2 | 242.8 | 489.7 | 30 | 20.6 | 57.7 | 5.8 | 245.3 | 12.3 | 798.9 | 752.6 | 725 | 631.9 | 694.8 | 778.9 | 699.2 | 712.5 | 436.5 | 711.5 | 32.4 | 81.6 | 120.1 | 62.2 | 268.6 | 255.9 | 78.7 | 188.2 | 235.6 | 108.2
546 | 352 | 467.8 | 187.12 | 218.7325 | 258.7 | 235 | 254 | 243.2 | 490 | 30 | 20.6 | 57.8 | 5.2 | 244.4 | 13.4 | 802.8 | 752.3 | 704.9 | 633.1 | 692.8 | 778.9 | 699.1 | 700.8 | 437.1 | 709.3 | 32.5 | 81.9 | 120.4 | 62.4 | 268.9 | 256.5 | 78.9 | 188.7 | 236.1 | 108.5
547 | 353 | 466.7 | 186.68 | 218.2182 | 260.5 | 235.9 | 255.3 | 243.3 | 486.7 | 30 | 20.6 | 58 | 4.8 | 244.4 | 13 | 807.3 | 753.4 | 694.9 | 634.2 | 691.3 | 777.9 | 696.9 | 687.5 | 437.6 | 706.4 | 32.6 | 82.2 | 120.7 | 62.6 | 269 | 257.3 | 79.2 | 189.2 | 236.6 | 108.8
548 | 354 | 467.6 | 187.04 | 218.639 | 262.1 | 236.8 | 256.5 | 244.1 | 483.6 | 30 | 20.6 | 58.1 | 4.5 | 248.8 | 12.3 | 810.8 | 752.6 | 695.7 | 635.3 | 689.9 | 777.7 | 695.6 | 681.3 | 437.9 | 704.1 | 32.7 | 82.5 | 121 | 62.8 | 269.4 | 257.9 | 79.4 | 189.6 | 237.2 | 109.1
549 | 355 | 467 | 186.8 | 218.3584 | 262.1 | 236 | 257.7 | 246 | 485.4 | 30.1 | 20.6 | 58.1 | 5.3 | 274.5 | 10.8 | 813.7 | 755.5 | 698.3 | 636.6 | 689 | 779.7 | 694.8 | 684.4 | 437.6 | 702.8 | 32.8 | 82.7 | 121.4 | 63 | 269.6 | 258.3 | 79.7 | 189.8 | 237.8 | 109.4
550 | 356 | 467.4 | 186.96 | 218.5455 | 262.6 | 234.5 | 258.5 | 246.1 | 487.8 | 30.2 | 20.6 | 58.2 | 5 | 254.2 | 8.9 | 817.2 | 756.6 | 707.6 | 638.3 | 691.2 | 781.6 | 694.2 | 691.1 | 437.1 | 702.4 | 32.9 | 83 | 121.6 | 63.2 | 271.5 | 258.6 | 79.9 | 190.3 | 238.2 | 109.7
551 | 357 | 467.4 | 186.96 | 218.5455 | 263.2 | 234 | 258.8 | 247.3 | 488.6 | 30.3 | 20.6 | 58.4 | 5.7 | 249.9 | 9.5 | 819.5 | 756.3 | 723.2 | 640 | 690.9 | 783.4 | 696.9 | 701.5 | 437 | 704.3 | 33 | 83.3 | 121.9 | 63.4 | 273.1 | 258.9 | 80.2 | 190.8 | 238.6 | 110.1
552 | 358 | 467.7 | 187.08 | 218.6857 | 264 | 233.7 | 259.1 | 248.3 | 486 | 30.2 | 20.6 | 58.5 | 5 | 238.6 | 9.1 | 823.2 | 758.8 | 718.2 | 642.1 | 690.4 | 783.3 | 697.8 | 700.9 | 436.9 | 704.4 | 33.1 | 83.6 | 122.1 | 63.6 | 273.2 | 259 | 80.5 | 191.2 | 239.1 | 110.5
553 | 359 | 467.9 | 187.16 | 218.7793 | 264.4 | 232.5 | 259.8 | 248.7 | 481.9 | 30.2 | 20.6 | 58.6 | 5.8 | 249.1 | 9 | 826.9 | 760.2 | 711 | 644.3 | 688.5 | 782.5 | 697.7 | 700.5 | 436.8 | 704.2 | 33.2 | 83.8 | 122.4 | 63.8 | 273.4 | 259.2 | 80.7 | 191.6 | 239.5 | 110.8
554 | 360 | 468 | 187.2 | 218.826 | 264 | 231.7 | 260.4 | 248.9 | 475.3 | 30.2 | 20.6 | 58.6 | 5.3 | 248.6 | 9.4 | 830.1 | 764.5 | 713.1 | 646.7 | 688.7 | 783.3 | 699.5 | 705.2 | 437 | 703.5 | 33.3 | 84.1 | 122.7 | 64 | 273.6 | 259.5 | 81 | 192 | 240 | 111.1
555 | 361 | 468.1 | 187.24 | 218.8728 | 263.8 | 231.4 | 260.2 | 248.7 | 476.4 | 30.2 | 20.6 | 58.6 | 5.6 | 255.3 | 10.1 | 832.6 | 762.5 | 722.9 | 648.8 | 690.1 | 784.7 | 700.9 | 708.3 | 437.5 | 704.5 | 33.5 | 84.4 | 123.1 | 64.2 | 273.6 | 259.8 | 81.2 | 192.3 | 240.4 | 111.4
556 | 362 | 467.2 | 186.88 | 218.452 | 263.6 | 232 | 260.2 | 248.1 | 477.2 | 30.2 | 20.6 | 58.7 | 5.5 | 245.8 | 11.5 | 836 | 761.8 | 714.7 | 650.9 | 688.2 | 784.6 | 703.4 | 705.5 | 438.1 | 702.3 | 33.6 | 84.7 | 123.3 | 64.4 | 273.9 | 260.1 | 81.5 | 192.6 | 241 | 111.7
557 | 363 | 468.3 | 187.32 | 218.9663 | 263.3 | 232.6 | 260.6 | 247.8 | 476.5 | 30.3 | 20.6 | 58.7 | 6.2 | 248.1 | 12.3 | 839 | 759.9 | 704 | 652.9 | 686.2 | 782.9 | 701.4 | 695.7 | 438.6 | 699.5 | 33.7 | 85 | 123.5 | 64.6 | 273.9 | 260.3 | 81.7 | 193 | 241.4 | 112
558 | 364 | 467.4 | 186.96 | 218.5455 | 263.7 | 232.9 | 260.8 | 247.1 | 473.6 | 30.4 | 20.6 | 58.7 | 6.5 | 245.4 | 10.1 | 842.3 | 757.4 | 696.8 | 654.7 | 683.6 | 781.1 | 699.5 | 688.6 | 439.4 | 696.8 | 33.8 | 85.3 | 123.8 | 64.8 | 273.9 | 260.6 | 82 | 193.3 | 241.9 | 112.2
559 | 365 | 468.6 | 187.44 | 219.1066 | 263.3 | 232.5 | 262.5 | 246.5 | 472.8 | 30.4 | 20.6 | 58.8 | 6 | 243.9 | 10.4 | 844.8 | 757.1 | 700.3 | 656.8 | 683.2 | 780.5 | 695.5 | 687 | 440.1 | 697.1 | 33.9 | 85.6 | 124.1 | 64.9 | 274 | 261 | 82.2 | 193.6 | 242.4 | 112.6
560 | 366 | 468.8 | 187.52 | 219.2001 | 263 | 232.7 | 264 | 245.7 | 468.2 | 30.4 | 20.6 | 58.7 | 5.5 | 239.2 | 9.6 | 846.5 | 754.8 | 709.7 | 659.1 | 683.5 | 781.3 | 693.3 | 693.1 | 441.1 | 697.7 | 34 | 85.9 | 124.4 | 65.2 | 274.2 | 261.2 | 82.5 | 194 | 242.8 | 112.9
561 | 367 | 467.8 | 187.12 | 218.7325 | 262.6 | 232.7 | 263.5 | 245.4 | 470.2 | 30.5 | 20.6 | 58.6 | 4.9 | 256.6 | 8.7 | 848.4 | 753.5 | 713.6 | 661.4 | 683.5 | 781.2 | 692.3 | 694.6 | 442.3 | 697 | 34.1 | 86.1 | 124.7 | 65.4 | 274.2 | 261.4 | 82.7 | 194.4 | 243.3 | 113.2
562 | 368 | 467.3 | 186.92 | 218.4987 | 263 | 233.2 | 263.8 | 245.4 | 465.1 | 30.5 | 20.6 | 58.5 | 4.9 | 273.2 | 7.7 | 849.5 | 754.7 | 715.2 | 663.8 | 682.6 | 781 | 692.4 | 694.8 | 443.5 | 696.3 | 34.2 | 86.4 | 125.2 | 65.5 | 275.2 | 261.9 | 83 | 194.9 | 243.7 | 113.5
563 | 369 | 468.5 | 187.4 | 219.0598 | 263.7 | 233.2 | 263.6 | 246.6 | 461.7 | 30.5 | 20.6 | 58.5 | 4.8 | 255.7 | 9.8 | 851.6 | 754.4 | 706.5 | 666.1 | 680 | 780 | 687.7 | 692.8 | 444.9 | 694.8 | 34.3 | 86.7 | 125.4 | 65.7 | 275.2 | 262.5 | 83.2 | 195.3 | 244.2 | 113.8
564 | 370 | 468.2 | 187.28 | 218.9195 | 264.5 | 232.9 | 262.8 | 247 | 461.2 | 30.5 | 20.6 | 58.5 | 4.6 | 222.5 | 10.2 | 854.7 | 754.7 | 700.8 | 668.3 | 678.1 | 777.2 | 685.9 | 680.7 | 446.2 | 691.5 | 34.5 | 86.9 | 125.7 | 65.9 | 275.2 | 262.7 | 83.5 | 195.6 | 244.5 | 114.1
565 | 371 | 467.3 | 186.92 | 218.4987 | 265.3 | 233 | 262.4 | 247.1 | 462.2 | 30.5 | 20.6 | 58.5 | 4.7 | 251.6 | 8.6 | 857 | 753.4 | 693.3 | 670.4 | 675.9 | 775.5 | 681.2 | 670 | 447.6 | 688.5 | 34.6 | 87.2 | 126 | 66.1 | 275.2 | 262.7 | 83.7 | 196 | 245 | 114.4
566 | 372 | 467 | 186.8 | 218.3584 | 265.6 | 233.2 | 263.3 | 247.7 | 464.5 | 30.5 | 20.6 | 58.5 | 3.8 | 270.9 | 9 | 859.9 | 752 | 690.5 | 672.6 | 675 | 774.2 | 678.2 | 664.2 | 449.1 | 686.1 | 34.7 | 87.4 | 126.3 | 66.3 | 275 | 263 | 84 | 196.4 | 245.4 | 114.7
567 | 373 | 468.3 | 187.32 | 218.9663 | 266 | 232.6 | 265 | 247.8 | 463.8 | 30.6 | 20.6 | 58.7 | 3.9 | 262.9 | 13.2 | 862.6 | 751 | 692.1 | 674.9 | 673.4 | 774 | 677.2 | 665.1 | 450.5 | 684.6 | 34.8 | 87.7 | 126.7 | 66.5 | 275.9 | 263.3 | 84.2 | 196.9 | 245.8 | 115
568 | 374 | 465.3 | 186.12 | 217.5636 | 266.9 | 232.6 | 266.1 | 247.6 | 460.4 | 30.6 | 20.6 | 58.8 | 3.8 | 251.9 | 15.3 | 865.2 | 749.8 | 685.3 | 677.1 | 671.7 | 774.4 | 673.6 | 664.5 | 451.9 | 683.4 | 34.9 | 88 | 126.8 | 66.7 | 275.8 | 263.6 | 84.5 | 197.3 | 246.3 | 115.3
569 | 375 | 464.2 | 185.68 | 217.0492 | 268.1 | 233.3 | 266.3 | 247.7 | 454.4 | 30.6 | 20.6 | 58.9 | 5.1 | 240 | 14.6 | 869.1 | 748 | 683 | 679.4 | 670.4 | 772.4 | 669.1 | 654.6 | 453.2 | 679.9 | 35 | 88.2 | 127.1 | 66.9 | 275.6 | 264 | 84.7 | 197.6 | 246.7 | 115.6
570 | 376 | 464.4 | 185.76 | 217.1427 | 268.5 | 233.3 | 267.2 | 248 | 452.8 | 30.7 | 20.6 | 59.1 | 5.7 | 255.8 | 13.3 | 870.5 | 745.8 | 682.9 | 681.5 | 670.1 | 771.1 | 668.4 | 650 | 454.5 | 678.1 | 35.1 | 88.5 | 127.3 | 67.1 | 275.4 | 264.3 | 85 | 198 | 247.1 | 115.9
571 | 377 | 464.8 | 185.92 | 217.3298 | 268.5 | 232.7 | 268.1 | 248.4 | 451.6 | 30.8 | 20.6 | 59.2 | 6.4 | 249.3 | 13 | 871.6 | 743.5 | 689.6 | 683.6 | 668.8 | 770.5 | 670.5 | 651.4 | 456 | 676.6 | 35.3 | 88.8 | 127.7 | 67.3 | 275.7 | 264.4 | 85.2 | 198.3 | 247.5 | 116.2
572 | 378 | 465.9 | 186.36 | 217.8441 | 268.6 | 232.7 | 268.5 | 248.5 | 454.2 | 30.9 | 20.6 | 59.3 | 7.9 | 252.6 | 13.7 | 871.3 | 742.5 | 689.7 | 685.5 | 667.3 | 769.4 | 661.1 | 650.7 | 457.4 | 675.2 | 35.4 | 89 | 127.9 | 67.5 | 275.6 | 264.4 | 85.5 | 198.6 | 247.9 | 116.5
573 | 379 | 465 | 186 | 217.4233 | 268.6 | 232.9 | 268 | 247.6 | 450.1 | 31 | 20.5 | 59.3 | 6.2 | 247.7 | 17 | 871.6 | 741.1 | 686.4 | 687.5 | 665.7 | 767.4 | 661.3 | 646.3 | 458.7 | 673 | 35.5 | 89.3 | 128.3 | 67.7 | 275.7 | 264.3 | 85.7 | 198.9 | 248.4 | 116.8
574 | 380 | 464.8 | 185.92 | 217.3298 | 269.3 | 233.1 | 268.3 | 246.8 | 449.8 | 31.1 | 20.5 | 59.2 | 5.6 | 250.6 | 18.3 | 873.5 | 740.4 | 688.5 | 689.7 | 664 | 766 | 662.3 | 640.7 | 460.2 | 671.2 | 35.6 | 89.6 | 128.6 | 67.9 | 275.6 | 264.5 | 86 | 199.3 | 248.8 | 117.1
575 | 381 | 464.5 | 185.8 | 217.1895 | 269.7 | 233.5 | 269.3 | 246.3 | 451.9 | 31.1 | 20.5 | 59.2 | 9 | 249.5 | 23.7 | 873.8 | 738.4 | 688.2 | 691.8 | 664.1 | 765.8 | 668.7 | 643.3 | 462 | 669.6 | 35.7 | 89.8 | 128.7 | 68.1 | 275.2 | 264.9 | 86.2 | 199.7 | 249.2 | 117.5
576 | 382 | 464.2 | 185.68 | 217.0492 | 269.7 | 233.3 | 268.9 | 246.5 | 456.2 | 31.2 | 20.6 | 59.4 | 10.4 | 260.7 | 22.6 | 874.1 | 739.1 | 688.3 | 694.1 | 664 | 765.2 | 666.9 | 644.1 | 463.5 | 669.3 | 35.8 | 90.1 | 129 | 68.3 | 275 | 264.8 | 86.4 | 199.9 | 249.6 | 117.8
577 | 383 | 465.6 | 186.24 | 217.7038 | 270.1 | 232.9 | 268.3 | 246.5 | 460.9 | 31.3 | 20.5 | 59.5 | 8.3 | 262.4 | 22.5 | 875.6 | 740.5 | 685.1 | 696.8 | 662.1 | 764.9 | 673.2 | 650.4 | 465.4 | 671.4 | 36 | 90.4 | 129.3 | 68.5 | 275.8 | 264.8 | 86.7 | 200.3 | 250 | 118
578 | 384 | 465.2 | 186.08 | 217.5168 | 271.2 | 232.9 | 268.3 | 245.5 | 462.6 | 31.4 | 20.5 | 59.5 | 7.6 | 260.6 | 20.7 | 876 | 739.7 | 692.4 | 699.6 | 663 | 764.2 | 678.6 | 649.8 | 467.3 | 672.7 | 36.1 | 90.6 | 129.6 | 68.7 | 275.7 | 264.9 | 86.9 | 200.7 | 250.4 | 118.3
579 | 385 | 464 | 185.6 | 216.9557 | 270.8 | 234 | 269.1 | 245.5 | 461.3 | 31.6 | 20.5 | 59.5 | 8.2 | 250.7 | 23 | 874.6 | 738.7 | 714.9 | 702.6 | 668.1 | 763.7 | 679.8 | 656.9 | 469.3 | 676.5 | 36.2 | 90.9 | 129.9 | 68.9 | 275.8 | 265.3 | 87.2 | 201.1 | 250.9 | 118.6
580 | 386 | 464.5 | 185.8 | 217.1895 | 270 | 234.3 | 270.3 | 246.2 | 466 | 31.7 | 20.5 | 59.5 | 9.2 | 264.7 | 22.3 | 873.2 | 738.3 | 738.2 | 705.3 | 673.4 | 765.5 | 679.4 | 675.8 | 471.4 | 680.7 | 36.3 | 91.2 | 130.3 | 69.1 | 276 | 265.5 | 87.5 | 201.5 | 251.4 | 119
581 | 387 | 466.1 | 186.44 | 217.9376 | 269.3 | 234.9 | 270.6 | 246.8 | 470.7 | 31.8 | 20.5 | 59.6 | 12.8 | 267 | 25.8 | 872.5 | 741.5 | 745.8 | 708 | 673.6 | 767.6 | 683.9 | 688.2 | 473.7 | 680.9 | 36.4 | 91.4 | 130.5 | 69.3 | 276.5 | 265.7 | 87.7 | 201.8 | 252 | 119.3
582 | 388 | 465.2 | 186.08 | 217.5168 | 268.7 | 235.3 | 271.4 | 246.8 | 473.4 | 31.8 | 20.5 | 59.7 | 13.4 | 264.2 | 28.1 | 871.9 | 742.9 | 756.9 | 710.7 | 676.2 | 767.6 | 689 | 696.1 | 475.8 | 682.5 | 36.6 | 91.6 | 130.7 | 69.5 | 277 | 265.8 | 88 | 202.2 | 252.5 | 119.6
583 | 389 | 464.7 | 185.88 | 217.283 | 268.3 | 235.2 | 272.8 | 247.8 | 480.3 | 31.9 | 20.5 | 59.7 | 9.7 | 251.4 | 26.2 | 871.7 | 744.7 | 760.8 | 713.5 | 676.5 | 767.2 | 688.9 | 701 | 478 | 684.3 | 36.7 | 91.9 | 131 | 69.7 | 277.3 | 266.1 | 88.2 | 202.5 | 252.9 | 119.9
584 | 390 | 464.9 | 185.96 | 217.3765 | 268.2 | 235.3 | 272.9 | 248.1 | 480.9 | 32 | 20.5 | 59.7 | 6.6 | 254.4 | 21.3 | 873.2 | 746.7 | 763.1 | 716.3 | 674.9 | 767.4 | 685.6 | 706.7 | 480.1 | 686 | 36.8 | 92.2 | 131.6 | 69.9 | 280.8 | 266.4 | 88.4 | 203 | 253.4 | 120.2
585 | 391 | 465.3 | 186.12 | 217.5636 | 268.5 | 235.1 | 272 | 249.4 | 482.1 | 32 | 20.5 | 59.6 | 6.3 | 261.6 | 18 | 874.7 | 748.1 | 766.6 | 718.9 | 675.6 | 768.2 | 686.1 | 711.8 | 482.4 | 686 | 36.9 | 92.5 | 131.8 | 70.1 | 280.7 | 266.6 | 88.7 | 203.3 | 253.8 | 120.6
586 | 392 | 466.4 | 186.56 | 218.0779 | 268.7 | 234.9 | 271.1 | 250.1 | 491.1 | 32.1 | 20.5 | 59.6 | 7.6 | 258 | 17.8 | 875.3 | 747.8 | 771.8 | 721.7 | 679 | 769.3 | 689.3 | 719.7 | 484.8 | 687.2 | 37 | 92.8 | 132.1 | 70.3 | 280.8 | 266.5 | 88.9 | 203.5 | 254.3 | 120.9
587 | 393 | 466.7 | 186.68 | 218.2182 | 268.2 | 236.1 | 270.4 | 249.6 | 501.1 | 32.2 | 20.5 | 59.6 | 8.4 | 258.5 | 19 | 875.2 | 747 | 775.9 | 724.3 | 680.9 | 770.5 | 693.4 | 729.4 | 487.2 | 690.4 | 37.1 | 93 | 132.4 | 70.5 | 280.9 | 266.6 | 89.2 | 203.9 | 254.7 | 121.2
588 | 394 | 467.2 | 186.88 | 218.452 | 268 | 236.5 | 269.7 | 248.1 | 504.6 | 32.3 | 20.5 | 59.7 | 8.4 | 268.8 | 17.2 | 875.1 | 745.6 | 776.5 | 726.8 | 679.5 | 771.5 | 696.6 | 735.3 | 489.4 | 691.7 | 37.3 | 93.3 | 132.6 | 70.7 | 280.9 | 266.5 | 89.4 | 204.1 | 255.2 | 121.5
589 | 395 | 467.3 | 186.92 | 218.4987 | 267.4 | 236.4 | 269 | 247.5 | 508.1 | 32.3 | 20.5 | 59.9 | 9.2 | 264.5 | 18.4 | 875.3 | 745.1 | 783.5 | 729.3 | 679.7 | 772.9 | 702.1 | 741.3 | 491.9 | 692 | 37.4 | 93.6 | 133 | 70.9 | 281.1 | 267 | 89.6 | 204.4 | 255.6 | 121.8
590 | 396 | 464.4 | 185.76 | 217.1427 | 267.7 | 236.3 | 268.2 | 248 | 535.5 | 32.3 | 20.5 | 60.1 | 8.6 | 263.2 | 20.5 | 875.9 | 745.8 | 795.3 | 731.9 | 681.9 | 775.4 | 706.7 | 748.5 | 494.4 | 692.6 | 37.5 | 93.9 | 133.6 | 71.1 | 281.2 | 267.3 | 89.9 | 204.8 | 256.1 | 122.1
591 | 397 | 465.1 | 186.04 | 217.47 | 267.4 | 236.2 | 267.1 | 249.1 | 554.6 | 32.3 | 20.5 | 60.2 | 9.4 | 264.4 | 20.9 | 878.1 | 747.5 | 799.3 | 734.5 | 682.1 | 777 | 705.7 | 752.5 | 496.7 | 694.2 | 37.6 | 94.2 | 133.8 | 71.3 | 281.4 | 267.9 | 90.1 | 205.2 | 256.6 | 122.4
592 | 398 | 465.3 | 186.12 | 217.5636 | 266.5 | 236.8 | 266.9 | 249.6 | 554.7 | 32.3 | 20.5 | 60.4 | 8.4 | 258 | 21 | 880.2 | 746.9 | 791.8 | 736.8 | 679.5 | 777.1 | 701.4 | 745.8 | 498.6 | 691.6 | 37.8 | 94.5 | 134.1 | 71.5 | 281.3 | 267.9 | 90.4 | 205.5 | 257.2 | 122.7
593 | 399 | 465.5 | 186.2 | 217.6571 | 266.4 | 237.9 | 267.2 | 249.5 | 549 | 32.3 | 20.5 | 60.4 | 5.7 | 255.3 | 20.6 | 882.4 | 744.9 | 788.5 | 739 | 680.1 | 777 | 700 | 737.4 | 500.5 | 689 | 37.9 | 94.8 | 134.2 | 71.7 | 281.4 | 268 | 90.6 | 205.8 | 257.7 | 123
594 | 400 | 465.5 | 186.2 | 217.6571 | 267.6 | 238.2 | 267.6 | 249.7 | 542.7 | 32.4 | 20.5 | 60.5 | 4.4 | 262.8 | 18 | 883 | 742.9 | 779 | 741.2 | 680.2 | 776.5 | 697.2 | 733.2 | 502.5 | 688.1 | 38 | 95.1 | 134.5 | 71.9 | 281.2 | 268.2 | 90.9 | 206.1 | 258.1 | 123.3
595 | 401 | 465.5 | 186.2 | 217.6571 | 268.2 | 238.8 | 267.1 | 251 | 530.9 | 32.5 | 20.5 | 60.4 | 4.9 | 251 | 15.1 | 882.9 | 742.1 | 773.4 | 743.6 | 681.7 | 776.3 | 695.9 | 731.8 | 504.6 | 689.3 | 38.1 | 95.4 | 134.8 | 72.1 | 281.2 | 268.4 | 91.1 | 206.5 | 258.5 | 123.6
596 | 402 | 464.6 | 185.84 | 217.2363 | 268.3 | 239 | 266.6 | 251.5 | 526.3 | 32.5 | 20.5 | 60.4 | 5.3 | 247.7 | 14.8 | 883.5 | 741.8 | 774.8 | 745.8 | 680.8 | 775.9 | 691.2 | 724.8 | 506.8 | 688 | 38.2 | 95.7 | 135.3 | 72.3 | 281.2 | 268.5 | 91.3 | 206.8 | 259 | 123.9
597 | 403 | 464.9 | 185.96 | 217.3765 | 268.7 | 239.4 | 266.4 | 250.8 | 516.3 | 32.5 | 20.5 | 60.4 | 6.3 | 256.5 | 14.2 | 884.5 | 741.9 | 771.2 | 747.9 | 680.4 | 775.7 | 687.1 | 720.9 | 508.8 | 686.4 | 38.4 | 96 | 135.6 | 72.5 | 281.2 | 268.6 | 91.6 | 207.2 | 259.4 | 124.2
598 | 404 | 465.7 | 186.28 | 217.7506 | 269.2 | 239 | 266.1 | 250.6 | 512.5 | 32.6 | 20.5 | 60.4 | 6.2 | 245.3 | 14.2 | 887.4 | 739.2 | 759.2 | 749.9 | 677 | 774 | 680.2 | 707.9 | 510.7 | 682.7 | 38.5 | 96.3 | 135.8 | 72.7 | 281.1 | 268.5 | 91.8 | 207.4 | 259.8 | 124.5
599 | 405 | 465.9 | 186.36 | 217.8441 | 269.8 | 238.6 | 266.1 | 250.2 | 501.2 | 32.7 | 20.5 | 60.3 | 6.4 | 265.3 | 13.7 | 890 | 735 | 747.3 | 751.5 | 674.1 | 771 | 673.5 | 691 | 512.4 | 679.2 | 38.6 | 96.5 | 135.9 | 73 | 281.1 | 268.3 | 92 | 207.7 | 260.2 | 124.9
600 | 406 | 466.2 | 186.48 | 217.9844 | 271.8 | 239.9 | 266.5 | 250.1 | 493.1 | 32.7 | 20.5 | 60.3 | 6.3 | 278.2 | 12.9 | 892.2 | 732.2 | 738.4 | 753.2 | 672.5 | 768.4 | 668.5 | 681.4 | 514.3 | 676.5 | 38.7 | 96.8 | 136.2 | 73.2 | 280.9 | 268.3 | 92.3 | 208.1 | 260.6 | 125.2
601 | 407 | 467.2 | 186.88 | 218.452 | 273 | 239.8 | 266.8 | 249.1 | 495.1 | 32.9 | 20.5 | 60.5 | 6.4 | 272.1 | 12.4 | 893.9 | 731.3 | 741 | 755 | 671.4 | 768.8 | 665.9 | 680.4 | 516.4 | 674.6 | 38.9 | 97.1 | 136.5 | 73.4 | 280.7 | 268.3 | 92.5 | 208.3 | 261 | 125.5
602 | 408 | 466.9 | 186.76 | 218.3117 | 273.2 | 238 | 266.7 | 248.8 | 495.3 | 32.9 | 20.5 | 60.6 | 6.5 | 266.5 | 13.3 | 895.2 | 733.2 | 750.5 | 757.5 | 671.3 | 768.6 | 666.7 | 680.6 | 518.2 | 674 | 39 | 97.4 | 136.7 | 73.6 | 280.5 | 268.5 | 92.7 | 208.6 | 261.5 | 125.7
603 | 409 | 467.5 | 187 | 218.5922 | 273 | 237.2 | 265.7 | 249.7 | 495 | 33 | 20.5 | 60.7 | 6.7 | 263 | 13.9 | 897.2 | 734.3 | 757.2 | 760.1 | 670.9 | 769.2 | 666.5 | 685.5 | 520.4 | 673.6 | 39.1 | 97.7 | 137 | 73.8 | 280.2 | 268.6 | 93 | 208.9 | 261.9 | 126
604 | 410 | 467.2 | 186.88 | 218.452 | 272.6 | 236.6 | 265.3 | 249.3 | 493.7 | 33 | 20.5 | 60.9 | 6.4 | 268 | 13.2 | 899.3 | 734.2 | 756.7 | 762.4 | 670.3 | 768.5 | 666.3 | 682.8 | 522.5 | 672.9 | 39.2 | 98 | 137.3 | 74 | 280.1 | 268.6 | 93.2 | 209.2 | 262.3 | 126.3
605 | 411 | 466.7 | 186.68 | 218.2182 | 272.5 | 236.9 | 264.3 | 248.4 | 490 | 32.8 | 20.5 | 61.1 | 5.8 | 268.8 | 13.4 | 899.7 | 735.5 | 752.4 | 764.8 | 670.6 | 768.3 | 667 | 686.7 | 524.5 | 673.2 | 39.3 | 98.2 | 137.5 | 74.2 | 280 | 268.6 | 93.5 | 209.5 | 262.7 | 126.6
606 | 412 | 466.8 | 186.72 | 218.2649 | 271.6 | 237.1 | 264.3 | 249 | 486.4 | 32.8 | 20.5 | 61.2 | 5.3 | 262.8 | 13.4 | 900.1 | 737.2 | 759.9 | 767.3 | 671.6 | 768.8 | 670.5 | 696.5 | 526.5 | 673.8 | 39.5 | 98.5 | 137.8 | 74.4 | 280 | 268.4 | 93.7 | 209.8 | 263 | 126.9
607 | 413 | 465.6 | 186.24 | 217.7038 | 270.9 | 236.7 | 264.6 | 249 | 489.7 | 32.8 | 20.5 | 61.3 | 6 | 261.5 | 14.9 | 899.9 | 738.6 | 766.7 | 770.1 | 673.5 | 770.4 | 676.4 | 710.3 | 528.7 | 678.8 | 39.6 | 98.8 | 138.1 | 74.6 | 280 | 268.4 | 93.9 | 210.1 | 263.4 | 127.1
608 | 414 | 464.1 | 185.64 | 217.0025 | 270 | 236.9 | 264 | 249 | 490.1 | 33 | 20.5 | 61.4 | 5.8 | 264 | 16.6 | 900.1 | 740.2 | 750.7 | 772.6 | 673.2 | 768.7 | 672.5 | 707.1 | 530.5 | 678.1 | 39.7 | 99.1 | 138.4 | 74.8 | 280 | 268.5 | 94.1 | 210.4 | 263.9 | 127.4
609 | 415 | 465.2 | 186.08 | 217.5168 | 270.4 | 238.1 | 263.3 | 249.1 | 485.9 | 33.1 | 20.5 | 61.4 | 6 | 260.8 | 17.9 | 902.2 | 739.5 | 743.4 | 775.4 | 670.5 | 767.1 | 673.4 | 702.2 | 532.7 | 676.3 | 39.8 | 99.4 | 138.8 | 75 | 280 | 268.8 | 94.4 | 210.7 | 264.3 | 127.7
610 | 416 | 465.6 | 186.24 | 217.7038 | 271 | 237.5 | 263.9 | 249.6 | 477.5 | 33.3 | 20.5 | 61.5 | 6.4 | 265.5 | 19 | 903 | 738.2 | 738.6 | 778 | 670.7 | 765 | 672.7 | 697.8 | 534.9 | 676.6 | 40 | 99.6 | 139.2 | 75.2 | 279.9 | 269 | 94.6 | 211 | 264.7 | 128
611 | 417 | 465.3 | 186.12 | 217.5636 | 271.2 | 236.9 | 264.5 | 250.4 | 473.1 | 33.4 | 20.5 | 61.7 | 7 | 271.7 | 18 | 903.5 | 738.4 | 745.3 | 780.7 | 670.4 | 764.2 | 672.8 | 698.1 | 537.1 | 676.6 | 40.1 | 99.9 | 139.4 | 75.4 | 280.2 | 269.2 | 94.8 | 211.3 | 265.1 | 128.3
612 | 418 | 465 | 186 | 217.4233 | 271.4 | 237.7 | 264.9 | 251.6 | 476.6 | 33.5 | 20.5 | 61.7 | 9.3 | 272.4 | 16.5 | 904.3 | 738.1 | 739.7 | 782.9 | 669.6 | 763.5 | 672.5 | 694 | 539.4 | 675.4 | 40.2 | 100.1 | 139.6 | 75.6 | 280.4 | 269.5 | 95.1 | 211.7 | 265.5 | 128.6
613 | 419 | 465.2 | 186.08 | 217.5168 | 271.8 | 237.8 | 265.8 | 251.9 | 477.9 | 33.6 | 20.5 | 61.9 | 8.4 | 273.8 | 15.5 | 905.7 | 736.8 | 727.4 | 784.7 | 668 | 761.4 | 673.2 | 683.4 | 541.6 | 673.1 | 40.4 | 100.4 | 139.9 | 75.8 | 280.6 | 269.8 | 95.3 | 212.1 | 265.9 | 128.9
614 | 420 | 466.9 | 186.76 | 218.3117 | 271.7 | 238.1 | 266.2 | 251.3 | 479.3 | 33.7 | 20.5 | 61.9 | 7.3 | 268.9 | 14.7 | 907.7 | 735.5 | 718.7 | 786.5 | 666.2 | 760.1 | 674.5 | 679.4 | 543.8 | 673 | 40.5 | 100.6 | 140 | 76 | 280.6 | 269.9 | 95.6 | 212.3 | 266.3 | 129.2
615 | 421 | 466.3 | 186.52 | 218.0311 | 271.5 | 238.3 | 267.6 | 251.5 | 480.3 | 33.8 | 20.5 | 62 | 7 | 259.9 | 14.8 | 908.1 | 734 | 723.8 | 788 | 666.7 | 759.6 | 674 | 680.5 | 546 | 672.2 | 40.6 | 100.9 | 140.4 | 76.2 | 280.9 | 269.9 | 95.8 | 212.6 | 266.7 | 129.5
616 | 422 | 466.7 | 186.68 | 218.2182 | 271.2 | 237.3 | 268.5 | 251.8 | 482 | 33.9 | 20.5 | 62.1 | 6.3 | 238.8 | 14.3 | 908.3 | 736 | 737.5 | 790 | 669.1 | 760.3 | 676.5 | 688.9 | 548.3 | 672.8 | 40.7 | 101.1 | 140.8 | 76.4 | 281.5 | 270 | 96 | 212.9 | 267.1 | 129.8
617 | 423 | 466.2 | 186.48 | 217.9844 | 270.6 | 237.7 | 268.8 | 251.9 | 489.2 | 33.9 | 20.4 | 62.1 | 5.3 | 240.1 | 15.1 | 907.4 | 737.9 | 749.8 | 791.9 | 671 | 759.7 | 672.2 | 690.8 | 551.1 | 672.8 | 40.9 | 101.4 | 141 | 76.6 | 281.7 | 270.1 | 96.3 | 213.2 | 267.5 | 130.1
618 | 424 | 465.9 | 186.36 | 217.8441 | 269.5 | 237.9 | 269.4 | 252.7 | 491.9 | 34 | 20.5 | 62.2 | 5.1 | 254.3 | 12.8 | 906.3 | 736.6 | 764.2 | 793.9 | 672.5 | 759.7 | 670.5 | 692.8 | 553.5 | 671.9 | 41 | 101.6 | 141.3 | 76.8 | 281.7 | 270.5 | 96.5 | 213.5 | 267.9 | 130.4
619 | 425 | 465.1 | 186.04 | 217.47 | 269.5 | 238 | 269.9 | 252.3 | 504.3 | 34 | 20.5 | 62.3 | 5.1 | 240.1 | 12.4 | 906.5 | 735.1 | 765.8 | 795.4 | 669.5 | 758.3 | 665.2 | 684.2 | 555.6 | 669.1 | 41.1 | 101.9 | 141.6 | 77 | 281.5 | 270.8 | 96.7 | 213.7 | 268.2 | 130.6
620 | 426 | 464.9 | 185.96 | 217.3765 | 270.3 | 238.8 | 268.7 | 252.2 | 510 | 34 | 20.5 | 62.3 | 4.7 | 234.8 | 13.7 | 908.2 | 734.2 | 746.3 | 797 | 667.2 | 756.5 | 663.2 | 678.2 | 557.6 | 666.9 | 41.3 | 102.2 | 141.9 | 77.2 | 281.6 | 270.9 | 97 | 214 | 268.6 | 130.9
621 | 427 | 465.8 | 186.32 | 217.7973 | 272.4 | 239.8 | 268 | 252.7 | 504.3 | 34 | 20.4 | 62.3 | 5.1 | 242.9 | 12 | 908.5 | 734.7 | 738.7 | 798.4 | 667.7 | 754.6 | 664.6 | 679.5 | 559.8 | 667.7 | 41.4 | 102.4 | 142.2 | 77.4 | 281.2 | 270.8 | 97.2 | 214.3 | 268.9 | 131.2
622 | 428 | 466 | 186.4 | 217.8909 | 273.4 | 240 | 268.2 | 252.6 | 496.6 | 34 | 20.4 | 62.2 | 6.9 | 246.3 | 12 | 908.2 | 735.5 | 738.5 | 799.7 | 668 | 753.4 | 663.9 | 681.3 | 561.8 | 667.4 | 41.5 | 102.7 | 142.6 | 77.6 | 281.1 | 270.9 | 97.4 | 214.7 | 269.2 | 131.5
623 | 429 | 464.2 | 185.68 | 217.0492 | 273.7 | 240.1 | 268.4 | 251.6 | 491.9 | 34 | 20.4 | 62.3 | 6 | 243.7 | 14 | 908.7 | 736.3 | 743 | 801.4 | 668.4 | 752.7 | 668.4 | 684.9 | 564 | 668.1 | 41.6 | 103 | 142.8 | 77.8 | 280.3 | 270.8 | 97.6 | 214.9 | 269.6 | 131.8
624 | 430 | 464.7 | 185.88 | 217.283 | 273.4 | 238.9 | 269.4 | 250.6 | 489.6 | 34 | 20.4 | 62.3 | 5.1 | 234 | 13.8 | 908.5 | 736.7 | 759 | 803.3 | 669.9 | 752.7 | 664.9 | 692.2 | 565.6 | 668.7 | 41.8 | 103.3 | 143 | 78 | 280.2 | 270.8 | 97.9 | 215.2 | 270 | 132.1
625 | 431 | 465 | 186 | 217.4233 | 272.6 | 238.8 | 269.3 | 250.7 | 491.3 | 34 | 20.5 | 62.3 | 5.4 | 250.9 | 11.1 | 907.4 | 736.6 | 765 | 804.9 | 671.8 | 752.2 | 665.9 | 696.5 | 567.4 | 668.1 | 41.9 | 103.5 | 143.2 | 78.2 | 280 | 270.9 | 98.1 | 215.5 | 270.3 | 132.4
626 | 432 | 466 | 186.4 | 217.8909 | 272 | 239.2 | 269.5 | 250.4 | 489 | 34 | 20.4 | 62.3 | 5 | 248.4 | 10.6 | 907.6 | 736.4 | 764.5 | 806 | 672.3 | 751.5 | 662.8 | 694.8 | 568.9 | 667.3 | 42 | 103.8 | 143.4 | 78.5 | 279.9 | 270.9 | 98.4 | 215.6 | 270.6 | 132.6
627 | 433 | 465.8 | 186.32 | 217.7973 | 272.1 | 239.2 | 269.6 | 249.9 | 485.9 | 34.1 | 20.4 | 62.3 | 4.4 | 247 | 12.8 | 908.8 | 735.5 | 762.4 | 806.9 | 671.3 | 749.2 | 661.8 | 691.9 | 570.4 | 664.9 | 42.2 | 104.1 | 143.8 | 78.7 | 279.9 | 270.8 | 98.6 | 215.8 | 270.9 | 132.9
628 | 434 | 466.7 | 186.68 | 218.2182 | 272 | 240.3 | 269.4 | 250 | 482.3 | 34.2 | 20.4 | 62.3 | 5.2 | 241.6 | 14.6 | 909.3 | 738.1 | 766 | 808.1 | 673.1 | 747.9 | 662.6 | 694.5 | 572 | 666.4 | 42.3 | 104.3 | 144.2 | 78.9 | 280 | 270.6 | 98.8 | 216.1 | 271.2 | 133.2
629 | 435 | 467.5 | 187 | 218.5922 | 272.4 | 240.4 | 268.4 | 250.8 | 479.3 | 34.3 | 20.4 | 62.3 | 5.7 | 225.8 | 13.1 | 908.5 | 739.2 | 777.1 | 809.2 | 677.4 | 746.9 | 658.1 | 696.3 | 573.2 | 667.1 | 42.4 | 104.6 | 144.7 | 79.1 | 279.8 | 270.6 | 99 | 216.3 | 271.5 | 133.5
630 | 436 | 467.3 | 186.92 | 218.4987 | 273.2 | 240.8 | 268.1 | 251.6 | 479.5 | 34.4 | 20.4 | 62.4 | 6.5 | 209.8 | 11.2 | 907.9 | 740.9 | 781.2 | 810.5 | 679.8 | 746.9 | 657.4 | 701.5 | 574.5 | 668.5 | 42.6 | 104.9 | 144.6 | 79.3 | 279.5 | 270.4 | 99.3 | 216.5 | 271.9 | 133.7
631 | 437 | 467.2 | 186.88 | 218.452 | 273 | 241.6 | 266.9 | 252 | 482.8 | 34.5 | 20.4 | 62.4 | 5.9 | 214.5 | 10.4 | 907.4 | 743.4 | 783 | 812 | 682.2 | 747 | 655.8 | 706.7 | 575.8 | 670.2 | 42.7 | 105.1 | 144.8 | 79.5 | 279.3 | 270.2 | 99.5 | 216.8 | 272.2 | 134
632 | 438 | 466.9 | 186.76 | 218.3117 | 272 | 241.8 | 266.1 | 252.3 | 488.1 | 34.6 | 20.4 | 62.5 | 5.5 | 220.7 | 8 | 906.4 | 744.2 | 768.7 | 812.8 | 681 | 747.1 | 659.7 | 710.7 | 577.4 | 670.5 | 42.8 | 105.4 | 145.1 | 79.7 | 279.4 | 270.2 | 99.7 | 217 | 272.5 | 134.3
633 | 439 | 466.4 | 186.56 | 218.0779 | 271.9 | 241.8 | 265.5 | 253.2 | 480.2 | 34.7 | 20.4 | 62.7 | 6 | 205.4 | 6.5 | 906.3 | 743.8 | 759.6 | 813.4 | 678.8 | 745.8 | 656.7 | 703.4 | 579 | 668.3 | 43 | 105.7 | 145.4 | 79.9 | 280 | 270.2 | 100 | 217.4 | 272.9 | 134.6
634 | 440 | 466.1 | 186.44 | 217.9376 | 271.7 | 240.7 | 265.6 | 254.2 | 475 | 34.8 | 20.4 | 62.8 | 6 | 244.1 | 6.3 | 907.3 | 744.6 | 755.4 | 814.5 | 678.1 | 744.3 | 654.6 | 701.9 | 580.5 | 667 | 43.1 | 105.9 | 145.8 | 80.1 | 280 | 270.2 | 100.2 | 217.5 | 273.3 | 134.9
635 | 441 | 464.2 | 185.68 | 217.0492 | 270.6 | 240.5 | 266.1 | 255 | 474.2 | 34.9 | 20.4 | 62.8 | 5.8 | 204 | 10.3 | 906.5 | 745.6 | 770.1 | 815.7 | 683.9 | 744.6 | 653.6 | 704.6 | 582.2 | 667.8 | 43.2 | 106.2 | 145.9 | 80.3 | 280.2 | 270.2 | 100.5 | 217.8 | 273.5 | 135.2
636 | 442 | 463.5 | 185.4 | 216.7219 | 269.6 | 240.2 | 266.8 | 254.3 | 485.7 | 35 | 20.4 | 62.8 | 6.1 | 215.4 | 12.5 | 905.8 | 747.1 | 787.2 | 817.2 | 686.9 | 746.7 | 653.3 | 712.7 | 583.9 | 670.2 | 43.4 | 106.5 | 146.1 | 80.5 | 280.6 | 270.2 | 100.7 | 218.1 | 273.9 | 135.5
637 | 443 | 464.6 | 185.84 | 217.2363 | 269.3 | 239.4 | 266.8 | 253 | 495.5 | 35 | 20.4 | 62.9 | 6.3 | 218.9 | 13 | 906 | 748.9 | 785.4 | 818.4 | 687.8 | 745.8 | 650.1 | 711.9 | 585.4 | 669.2 | 43.5 | 106.7 | 146.3 | 80.7 | 280.8 | 270.2 | 100.9 | 218.2 | 274.2 | 135.8
638 | 444 | 464.9 | 185.96 | 217.3765 | 269.2 | 239.7 | 266.9 | 252.5 | 486 | 35 | 20.4 | 62.9 | 6.6 | 207.7 | 11.7 | 905.9 | 750.6 | 796.2 | 819.6 | 691.3 | 744.5 | 646.3 | 711.8 | 586.7 | 668.1 | 43.6 | 107 | 146.6 | 80.9 | 280.7 | 270.2 | 101.2 | 218.6 | 274.6 | 136.1
639 | 445 | 465.1 | 186.04 | 217.47 | 269.3 | 240.3 | 266.7 | 253.6 | 478.3 | 35 | 20.4 | 62.9 | 6.3 | 221 | 8.6 | 905.1 | 751.5 | 800 | 820.8 | 692.4 | 745.1 | 649.8 | 715.5 | 588 | 668.7 | 43.8 | 107.2 | 146.9 | 81.1 | 280.7 | 270.3 | 101.4 | 218.8 | 274.9 | 136.4
640 | 446 | 465.2 | 186.08 | 217.5168 | 269.2 | 241.3 | 266.8 | 254.8 | 475.2 | 35.1 | 20.4 | 63 | 5.4 | 233.7 | 6.4 | 904.9 | 753 | 793.9 | 822 | 691.2 | 745.9 | 652.1 | 718.5 | 589.6 | 670.6 | 43.9 | 107.5 | 147.1 | 81.3 | 280.5 | 270.5 | 101.6 | 219 | 275.2 | 136.6
641 | 447 | 464.6 | 185.84 | 217.2363 | 269.3 | 241.7 | 266.6 | 254.8 | 475 | 35.1 | 20.4 | 63 | 5.3 | 220.8 | 6.1 | 905.4 | 754.7 | 786 | 823.3 | 690.9 | 745.5 | 653.9 | 716 | 591.1 | 671 | 44 | 107.8 | 147.4 | 81.5 | 280.1 | 270.5 | 101.8 | 219.2 | 275.5 | 136.9
642 | 448 | 465.6 | 186.24 | 217.7038 | 269.3 | 241.5 | 266.1 | 254.9 | 474.5 | 35.1 | 20.4 | 63.2 | 4.8 | 238.7 | 5.9 | 907.1 | 755.5 | 781.4 | 825.1 | 692.6 | 744.2 | 651.8 | 711.4 | 592.5 | 670.4 | 44.2 | 108 | 147.7 | 81.7 | 279.9 | 270.7 | 102.1 | 219.5 | 275.9 | 137.1
643 | 449 | 465.2 | 186.08 | 217.5168 | 270.4 | 241.8 | 265.5 | 255.2 | 467.6 | 35.1 | 20.4 | 63.4 | 5 | 243.5 | 6.9 | 908.8 | 755.7 | 772.6 | 826.5 | 690.9 | 743 | 651.2 | 712 | 594 | 671 | 44.3 | 108.3 | 147.9 | 82 | 280 | 270.9 | 102.3 | 219.9 | 276.2 | 137.4
644 | 450 | 466 | 186.4 | 217.8909 | 271.7 | 242.3 | 265.8 | 254.5 | 467.6 | 35.2 | 20.4 | 63.5 | 5.9 | 244.6 | 8.4 | 908.5 | 757.9 | 779 | 827.8 | 693.7 | 744 | 652.7 | 715.9 | 595.6 | 672.7 | 44.5 | 108.6 | 148.1 | 82.1 | 280 | 271 | 102.5 | 220.2 | 276.5 | 137.7
645 | 451 | 467.2 | 186.88 | 218.452 | 271.6 | 242.4 | 265.8 | 254.8 | 467.3 | 35.2 | 20.4 | 63.7 | 5.1 | 221.5 | 11.1 | 908.7 | 759.7 | 786.2 | 829.6 | 694 | 744.3 | 653.8 | 719.4 | 597.2 | 674 | 44.6 | 108.9 | 148.3 | 82.4 | 280.5 | 271.3 | 102.8 | 220.4 | 276.8 | 138
646 | 452 | 465.4 | 186.16 | 217.6103 | 271.7 | 242.6 | 264.9 | 255 | 470.7 | 35.3 | 20.4 | 63.9 | 5.3 | 208.4 | 11.7 | 909 | 760.3 | 783.5 | 831.2 | 693.3 | 743.9 | 656.4 | 718.5 | 598.8 | 673.6 | 44.7 | 109.2 | 148.6 | 82.6 | 281.4 | 271.5 | 103 | 220.7 | 277.1 | 138.2
647 | 453 | 465.3 | 186.12 | 217.5636 | 271.9 | 243.1 | 265.4 | 255 | 467.4 | 35.4 | 20.4 | 64.1 | 6.1 | 210.4 | 12.2 | 909.1 | 760.2 | 771.1 | 832.4 | 692.6 | 741.6 | 658.7 | 713.4 | 600.3 | 674.2 | 44.9 | 109.4 | 149 | 82.8 | 281.8 | 271.9 | 103.2 | 220.9 | 277.5 | 138.6
648 | 454 | 464.9 | 185.96 | 217.3765 | 271.4 | 243.8 | 267 | 255.7 | 464.7 | 35.5 | 20.4 | 64.3 | 5.8 | 224.5 | 11.7 | 909.3 | 761 | 763.7 | 833.7 | 692.6 | 740.8 | 665.1 | 708.2 | 602 | 675.2 | 45 | 109.7 | 149.3 | 83 | 281.9 | 272.3 | 103.4 | 221.2 | 277.8 | 138.8
649 | 455 | 465 | 186 | 217.4233 | 271.7 | 244.2 | 267.9 | 256.2 | 462 | 35.5 | 20.4 | 64.4 | 5 | 218.9 | 11.4 | 908.7 | 763 | 773.8 | 834.9 | 697.2 | 739.8 | 667.6 | 710.3 | 603.9 | 677.9 | 45.1 | 110 | 149.6 | 83.2 | 282.5 | 272.5 | 103.7 | 221.5 | 278.1 | 139.1
650 | 456 | 465.7 | 186.28 | 217.7506 | 271.8 | 245.6 | 268.8 | 255.8 | 458.9 | 35.6 | 20.4 | 64.4 | 5.3 | 213 | 11.9 | 908.3 | 763.5 | 771.5 | 836.1 | 695.5 | 739.1 | 666 | 710 | 605.5 | 678.1 | 45.3 | 110.3 | 150 | 83.4 | 283.9 | 273.2 | 103.9 | 221.8 | 278.5 | 139.4
651 | 457 | 465.8 | 186.32 | 217.7973 | 272.3 | 246.7 | 270.3 | 256.5 | 454 | 35.6 | 20.4 | 64.5 | 5.3 | 231.7 | 9.7 | 907.8 | 760.2 | 763.5 | 837 | 693.2 | 737.1 | 660.6 | 700.1 | 606.8 | 675.6 | 45.4 | 110.5 | 150.1 | 83.6 | 284.8 | 274 | 104.2 | 222.2 | 278.9 | 139.8
652 | 458 | 466.4 | 186.56 | 218.0779 | 274.4 | 247 | 271.6 | 256.6 | 451.8 | 35.6 | 20.4 | 64.4 | 6.6 | 217.3 | 7.8 | 907.8 | 760.2 | 764.5 | 837.8 | 694 | 736.3 | 660.4 | 701.5 | 608 | 674.9 | 45.5 | 110.7 | 150.3 | 83.8 | 285.4 | 274.7 | 104.3 | 222.5 | 279.3 | 140.1
653 | 459 | 466.5 | 186.6 | 218.1246 | 275.6 | 247.5 | 272 | 255.9 | 457.8 | 35.6 | 20.4 | 64.4 | 5.9 | 212 | 7.3 | 908.5 | 763.4 | 774.5 | 839.3 | 696.3 | 737.8 | 661.8 | 710.8 | 609.7 | 679.4 | 45.7 | 111 | 150.6 | 84 | 285.7 | 275 | 104.6 | 222.8 | 279.5 | 140.4
654 | 460 | 466.2 | 186.48 | 217.9844 | 276.1 | 247.7 | 270.5 | 255.5 | 466.5 | 35.6 | 20.4 | 64.5 | 5.4 | 237.1 | 8.2 | 908.3 | 763.3 | 772.9 | 840.1 | 696.2 | 739.4 | 660.5 | 717.3 | 611 | 679.4 | 45.8 | 111.3 | 150.9 | 84.2 | 286.2 | 275 | 104.8 | 223 | 279.9 | 140.6
655 | 461 | 466.1 | 186.44 | 217.9376 | 276 | 246.7 | 269.9 | 255.9 | 463.8 | 35.6 | 20.4 | 64.7 | 5.8 | 239.5 | 10 | 907 | 764.5 | 776.5 | 840.4 | 697.5 | 739.8 | 664.4 | 723.9 | 612.1 | 679.8 | 46 | 111.5 | 151.3 | 84.4 | 286.2 | 275 | 105 | 223.3 | 280.3 | 141
656 | 462 | 466.6 | 186.64 | 218.1714 | 276.4 | 247.1 | 269.5 | 256.4 | 461.5 | 35.7 | 20.4 | 64.7 | 5.1 | 222.3 | 10.4 | 905.8 | 765.1 | 780.8 | 840.9 | 698.2 | 738.2 | 661.8 | 717.3 | 613.1 | 679.4 | 46.1 | 111.8 | 151.6 | 84.6 | 286.2 | 275.1 | 105.3 | 223.5 | 280.6 | 141.2
657 | 463 | 466.8 | 186.72 | 218.2649 | 276.1 | 248.3 | 269.8 | 256.4 | 457.7 | 35.8 | 20.4 | 64.8 | 4.5 | 238.3 | 9.9 | 904.9 | 765.1 | 776.2 | 840.9 | 699 | 736.4 | 664 | 719.5 | 614 | 682.9 | 46.2 | 112 | 151.8 | 84.8 | 286.2 | 275.5 | 105.5 | 223.8 | 280.9 | 141.5
658 | 464 | 466.6 | 186.64 | 218.1714 | 275.3 | 248.7 | 270.6 | 255.8 | 459.9 | 35.9 | 20.4 | 64.9 | 5 | 237.5 | 9.8 | 904.7 | 764.9 | 774 | 840.7 | 699.4 | 736.3 | 666.4 | 719.1 | 615.4 | 681.8 | 46.4 | 112.3 | 152.2 | 85.1 | 287.1 | 275.6 | 105.7 | 224 | 281.3 | 141.8
659 | 465 | 466.6 | 186.64 | 218.1714 | 274.9 | 248.4 | 271.4 | 256.6 | 462.5 | 35.9 | 20.4 | 64.9 | 5.8 | 237.3 | 10.5 | 905.1 | 763.3 | 766.2 | 840.8 | 698.1 | 734.6 | 663.7 | 712.1 | 616.5 | 680.7 | 46.5 | 112.6 | 152.3 | 85.3 | 286.6 | 275.5 | 105.9 | 224.3 | 281.6 | 142.1
660 | 466 | 465.3 | 186.12 | 217.5636 | 275.6 | 247.5 | 270.6 | 257.8 | 461.4 | 36 | 20.4 | 64.9 | 5.6 | 223.5 | 9.6 | 905.9 | 760.9 | 759.4 | 841.1 | 697.3 | 733.6 | 660.6 | 705.3 | 617.7 | 678.3 | 46.6 | 112.8 | 152.4 | 85.5 | 285.9 | 275.3 | 106.2 | 224.5 | 282 | 142.4
661 | 467 | 466.8 | 186.72 | 218.2649 | 275.5 | 247.1 | 270.5 | 257.5 | 461.9 | 36.1 | 20.4 | 64.9 | 7 | 244.7 | 9.4 | 906.6 | 756.9 | 750.1 | 840.8 | 694.5 | 732.2 | 659.5 | 693 | 618.6 | 674.3 | 46.8 | 113.1 | 152.6 | 85.7 | 285.4 | 275.5 | 106.4 | 224.6 | 282.3 | 142.6
662 | 468 | 465 | 186 | 217.4233 | 275.7 | 245.7 | 270.3 | 256.9 | 456.8 | 36.1 | 20.4 | 64.9 | 6.2 | 234.4 | 10.3 | 907.2 | 753.1 | 743.1 | 840.7 | 692 | 729.9 | 656.5 | 680.4 | 619.4 | 671 | 46.9 | 113.4 | 152.9 | 85.9 | 285.1 | 275.2 | 106.6 | 224.8 | 282.6 | 142.9
663 | 469 | 463.6 | 185.44 | 216.7687 | 276.7 | 244.2 | 270.3 | 256.5 | 461.9 | 36.2 | 20.4 | 65.1 | 6.6 | 225.3 | 10.5 | 907.7 | 753.3 | 753.1 | 840.9 | 696.1 | 730.7 | 662 | 689.6 | 620.9 | 671.6 | 47.1 | 113.7 | 153.3 | 86.1 | 284.9 | 274.9 | 106.8 | 225 | 283 | 143.2
664 | 470 | 465.4 | 186.16 | 217.6103 | 277.4 | 242.9 | 270.1 | 256.2 | 476.5 | 36.3 | 20.4 | 65.3 | 5.8 | 225 | 9.3 | 906.9 | 756.2 | 773.5 | 842.1 | 698 | 733.6 | 661.3 | 703.3 | 622.7 | 674.6 | 47.2 | 113.9 | 153.8 | 86.3 | 284.7 | 274.8 | 107.1 | 225.1 | 283.4 | 143.5
665 | 471 | 466 | 186.4 | 217.8909 | 277.2 | 243.3 | 270.8 | 256.9 | 495.9 | 36.4 | 20.4 | 65.5 | 5.9 | 222.1 | 9.2 | 907.4 | 756.3 | 771.3 | 843.9 | 695.1 | 734.8 | 656.8 | 702.8 | 624.2 | 673.3 | 47.3 | 114.2 | 154.2 | 86.5 | 284.4 | 274.5 | 107.3 | 225.3 | 283.8 | 143.7
666 | 472 | 465.7 | 186.28 | 217.7506 | 277.6 | 244.1 | 270.5 | 257.9 | 503.8 | 36.4 | 20.4 | 65.5 | 4.9 | 234.8 | 8.8 | 908.9 | 754.3 | 767.5 | 845.5 | 693.4 | 733.9 | 654.5 | 694 | 625.4 | 669.9 | 47.5 | 114.5 | 154.5 | 86.7 | 284.7 | 274.4 | 107.5 | 225.5 | 284.3 | 144
667 | 473 | 465.5 | 186.2 | 217.6571 | 278.4 | 246.1 | 269.7 | 258.5 | 503.4 | 36.5 | 20.4 | 65.5 | 4.7 | 244.2 | 8.5 | 909.9 | 753.9 | 777.2 | 846.9 | 696.4 | 734.9 | 652.9 | 696.1 | 626.6 | 669.2 | 47.6 | 114.8 | 154.5 | 86.9 | 284.8 | 274.1 | 107.7 | 225.6 | 284.6 | 144.3
668 | 474 | 464.9 | 185.96 | 217.3765 | 279.4 | 247 | 270.2 | 259.9 | 511.9 | 36.6 | 20.4 | 65.5 | 4.3 | 218 | 10.5 | 910.4 | 754.9 | 785.2 | 848.5 | 697.2 | 738.1 | 654.4 | 705.7 | 628.4 | 669.2 | 47.8 | 115.1 | 155 | 87.1 | 285.2 | 274.1 | 108 | 225.9 | 285 | 144.6
669 | 475 | 466.5 | 186.6 | 218.1246 | 279.5 | 247 | 271.1 | 262.1 | 527.2 | 36.6 | 20.4 | 65.6 | 3.8 | 231.3 | 10.5 | 910.3 | 756 | 789.2 | 849.4 | 697.8 | 741.8 | 659.8 | 716.3 | 630.2 | 670.2 | 47.9 | 115.4 | 155.5 | 87.3 | 285.5 | 274.1 | 108.2 | 226.2 | 285.5 | 144.8
670 | 476 | 466.2 | 186.48 | 217.9844 | 279.9 | 247 | 271.5 | 263.3 | 528.7 | 36.7 | 20.4 | 65.8 | 4.1 | 236.1 | 9.1 | 909.3 | 755.6 | 787.4 | 849.9 | 696.4 | 742.2 | 662.9 | 713.6 | 631.6 | 668.5 | 48 | 115.6 | 155.8 | 87.5 | 286.1 | 274.2 | 108.4 | 226.5 | 285.9 | 145.1
671 | 477 | 466.3 | 186.52 | 218.0311 | 280.3 | 247.3 | 271.3 | 263.6 | 523.7 | 36.7 | 20.4 | 65.9 | 4 | 235.1 | 9.6 | 909.2 | 756.4 | 790.7 | 850.6 | 698.3 | 741.9 | 662 | 716.9 | 632.6 | 668.6 | 48.2 | 115.9 | 156.1 | 87.7 | 286.6 | 274.5 | 108.7 | 226.8 | 286.2 | 145.4
672 | 478 | 465.5 | 186.2 | 217.6571 | 280.4 | 246.8 | 271.5 | 263.9 | 524.3 | 36.7 | 20.4 | 66 | 4.5 | 235.3 | 8.6 | 909.3 | 754.7 | 790.6 | 850.9 | 697.6 | 741.9 | 659.9 | 714.4 | 633.7 | 666.8 | 48.3 | 116.1 | 156.4 | 87.9 | 287.1 | 274.9 | 108.9 | 227.1 | 286.6 | 145.7
673 | 479 | 465.4 | 186.16 | 217.6103 | 280.4 | 245.8 | 271.2 | 263.5 | 526.8 | 36.7 | 20.4 | 66.1 | 5.3 | 246.4 | 6.9 | 910.1 | 755 | 794.4 | 851.6 | 698.5 | 743.6 | 659.4 | 719.6 | 635 | 667.9 | 48.5 | 116.4 | 156.6 | 88.1 | 286.9 | 275.3 | 109.1 | 227.3 | 287 | 146
674 | 480 | 465.4 | 186.16 | 217.6103 | 280.3 | 246.3 | 271.5 | 263.8 | 531.8 | 36.6 | 20.4 | 66.1 | 5.7 | 229.6 | 6.7 | 909.7 | 757.5 | 801.9 | 852.2 | 700.4 | 745.8 | 659.8 | 727.5 | 636.4 | 670.3 | 48.6 | 116.6 | 157 | 88.3 | 286.8 | 275.5 | 109.3 | 227.5 | 287.4 | 146.3
675 | 481 | 465.3 | 186.12 | 217.5636 | 280.4 | 247.2 | 272 | 263.9 | 530.6 | 36.7 | 20.4 | 66.1 | 5.7 | 229.5 | 7.9 | 908.1 | 760 | 804.5 | 852.6 | 704.5 | 747.1 | 659.9 | 735 | 637.6 | 673.2 | 48.7 | 116.8 | 157.1 | 88.5 | 287 | 275.8 | 109.6 | 227.7 | 287.8 | 146.6
676 | 482 | 465.7 | 186.28 | 217.7506 | 280.3 | 247.8 | 271.4 | 263.8 | 525.9 | 36.6 | 20.3 | 66.1 | 5.9 | 208.5 | 9.1 | 907.9 | 761.6 | 797.7 | 852.8 | 704.6 | 748.9 | 662.3 | 738.8 | 638.8 | 675 | 48.9 | 117.1 | 157.2 | 88.7 | 287.4 | 276.2 | 109.8 | 227.9 | 288.2 | 146.9
677 | 483 | 465.5 | 186.2 | 217.6571 | 279.8 | 248.2 | 271 | 263.4 | 522.9 | 36.7 | 20.3 | 66.1 | 6.3 | 234.2 | 9.1 | 908.2 | 763.4 | 798.5 | 853.4 | 706.1 | 749 | 665.2 | 738.1 | 639.9 | 676.3 | 49 | 117.3 | 157.6 | 88.9 | 288.1 | 276.7 | 110.1 | 228.2 | 288.6 | 147.2
678 | 484 | 465.4 | 186.16 | 217.6103 | 279.2 | 248.7 | 270.5 | 263.5 | 519.3 | 36.7 | 20.4 | 66.1 | 5.9 | 250.9 | 9.1 | 908.6 | 765.5 | 807.5 | 854.2 | 708.1 | 750.3 | 669.1 | 741.8 | 641.3 | 678.9 | 49.2 | 117.6 | 158 | 89.1 | 288.2 | 277.4 | 110.3 | 228.5 | 289 | 147.5
679 | 485 | 466.3 | 186.52 | 218.0311 | 278.8 | 249.8 | 270.6 | 263.2 | 518.7 | 36.8 | 20.3 | 66 | 6.2 | 254.7 | 8.3 | 908.5 | 768 | 811.9 | 855 | 710.4 | 752.3 | 671.3 | 745.4 | 642.9 | 680.2 | 49.3 | 117.8 | 158.2 | 89.3 | 288 | 277.5 | 110.5 | 228.7 | 289.4 | 147.8
680 | 486 | 465.5 | 186.2 | 217.6571 | 278.8 | 250.6 | 271 | 262.6 | 522.5 | 36.8 | 20.3 | 66 | 7.2 | 243.3 | 8.2 | 908.4 | 769.6 | 814.6 | 856.1 | 712.3 | 753.6 | 668.6 | 747 | 644.3 | 680.4 | 49.4 | 118.1 | 158.4 | 89.6 | 287.9 | 277.6 | 110.7 | 228.9 | 289.9 | 148.1
681 | 487 | 466.3 | 186.52 | 218.0311 | 279.1 | 250.6 | 270.9 | 262.4 | 527.2 | 36.8 | 20.3 | 66 | 6.2 | 260 | 10.4 | 908.2 | 769.8 | 819.4 | 857 | 714.2 | 754.1 | 669.6 | 748.6 | 645.7 | 682.1 | 49.6 | 118.4 | 158.7 | 89.8 | 288.5 | 277.7 | 111 | 229.1 | 290.3 | 148.3
682 | 488 | 466 | 186.4 | 217.8909 | 278.8 | 250.8 | 271 | 263.1 | 533.8 | 36.8 | 20.3 | 66.2 | 5.6 | 245.4 | 12.8 | 907.9 | 772.4 | 813.7 | 857.4 | 717.6 | 756.1 | 675.2 | 756.2 | 647 | 685.5 | 49.7 | 118.6 | 159.1 | 90 | 288.8 | 277.9 | 111.1 | 229.3 | 290.8 | 148.6
683 | 489 | 466.2 | 186.48 | 217.9844 | 278.3 | 251.8 | 270.9 | 264.5 | 526.7 | 36.9 | 20.3 | 66.2 | 6 | 259.5 | 12.6 | 907.7 | 773.9 | 798.6 | 858.2 | 719.7 | 754.3 | 677.1 | 748.6 | 647.8 | 685.6 | 49.9 | 118.9 | 159.3 | 90.2 | 288.9 | 278.3 | 111.4 | 229.6 | 291.3 | 148.9
684 | 490 | 466.3 | 186.52 | 218.0311 | 278 | 253.7 | 271.3 | 266.1 | 514.6 | 37 | 20.3 | 66.3 | 6.3 | 255.9 | 11.4 | 908 | 773.9 | 791.1 | 859.3 | 721.3 | 751.7 | 678.1 | 737.3 | 648.8 | 686.5 | 50 | 119.2 | 159.8 | 90.4 | 288.8 | 278.9 | 111.7 | 230 | 291.9 | 149.2
685 | 491 | 466.4 | 186.56 | 218.0779 | 278.1 | 255.7 | 272.8 | 266.1 | 504 | 37 | 20.3 | 66.5 | 8.4 | 257.8 | 11.3 | 907.8 | 773.3 | 789.6 | 859.5 | 724.7 | 750.4 | 679.6 | 735.7 | 649.7 | 688.4 | 50.1 | 119.4 | 160 | 90.6 | 288.9 | 279.5 | 111.9 | 230.3 | 292.5 | 149.5
686 | 492 | 467 | 186.8 | 218.3584 | 278.3 | 255.7 | 273.7 | 265.3 | 503.8 | 37 | 20.3 | 66.6 | 6.8 | 245.5 | 15.4 | 907.9 | 773.7 | 790.9 | 859.5 | 725.9 | 750.9 | 681 | 741.9 | 650.8 | 691.9 | 50.3 | 119.7 | 160.3 | 90.8 | 289 | 280.1 | 112.1 | 230.6 | 293 | 149.8
687 | 493 | 466.6 | 186.64 | 218.1714 | 278.5 | 256.3 | 274.8 | 265.1 | 498.2 | 37.1 | 20.3 | 66.7 | 8.9 | 244.8 | 16.3 | 908.5 | 772.7 | 783.5 | 859.4 | 723.2 | 751.4 | 680.2 | 737.7 | 651.7 | 689.3 | 50.4 | 119.9 | 160.6 | 91 | 289.5 | 280.5 | 112.3 | 230.9 | 293.6 | 150.1
688 | 494 | 466.9 | 186.76 | 218.3117 | 278.5 | 256.7 | 275.5 | 265 | 494 | 37.1 | 20.3 | 66.8 | 7.6 | 242 | 15.9 | 909.1 | 768.7 | 769.6 | 858.9 | 720.2 | 748.6 | 678.5 | 719.6 | 652.2 | 685.2 | 50.6 | 120.2 | 160.8 | 91.2 | 290.4 | 281.3 | 112.6 | 231.3 | 294.1 | 150.3
689 | 495 | 467.1 | 186.84 | 218.4052 | 278.5 | 257.1 | 274.9 | 263.7 | 482.8 | 37.2 | 20.3 | 66.9 | 8.4 | 231.5 | 15.9 | 909.4 | 764.9 | 759.2 | 858 | 717.2 | 745.7 | 673.2 | 705.5 | 652.8 | 681.7 | 50.7 | 120.5 | 161.1 | 91.4 | 290.3 | 281.9 | 112.8 | 231.5 | 294.6 | 150.6
690 | 496 | 466.7 | 186.68 | 218.2182 | 278 | 257.6 | 274.6 | 263.3 | 476.4 | 37.2 | 20.3 | 67 | 8.3 | 228.3 | 14.2 | 910 | 763.4 | 750.5 | 857.1 | 716.2 | 744.1 | 673.6 | 698.3 | 653.6 | 680.6 | 50.8 | 120.7 | 161.4 | 91.6 | 290.7 | 282.2 | 113 | 231.8 | 295.1 | 150.9
691 | 497 | 466.8 | 186.72 | 218.2649 | 277.5 | 258.7 | 274.4 | 263.1 | 469.9 | 37.3 | 20.3 | 67.1 | 6.8 | 240 | 14 | 910.2 | 761.4 | 744.1 | 856.4 | 713.8 | 742.9 | 673.4 | 691.6 | 654.7 | 679.1 | 51 | 121 | 161.8 | 91.8 | 290.9 | 282.5 | 113.3 | 232.1 | 295.6 | 151.2
692 | 498 | 466.7 | 186.68 | 218.2182 | 277.7 | 259.2 | 274.4 | 262.5 | 467.1 | 37.3 | 20.3 | 67.2 | 6.6 | 234.3 | 15.8 | 910 | 759.8 | 735.7 | 855.8 | 710.6 | 741.9 | 671.6 | 683 | 655.8 | 676.7 | 51.1 | 121.2 | 161.9 | 92 | 291.2 | 282.7 | 113.4 | 232.3 | 296.2 | 151.5
693 | 499 | 464.8 | 185.92 | 217.3298 | 278.7 | 259.5 | 274.9 | 261.3 | 467 | 37.3 | 20.3 | 67.3 | 5 | 251.3 | 13.2 | 910.8 | 758.2 | 728.7 | 855.8 | 707.2 | 739.8 | 670.3 | 675.7 | 656.9 | 674.8 | 51.3 | 121.5 | 162.1 | 92.2 | 291.9 | 283 | 113.7 | 232.6 | 296.7 | 151.8
694 | 500 | 464.8 | 185.92 | 217.3298 | 279.5 | 258.8 | 274.4 | 260.5 | 464.9 | 37.4 | 20.3 | 67.4 | 4.5 | 241 | 11.4 | 911 | 756.9 | 725.5 | 855.5 | 706.4 | 738 | 668.6 | 672.6 | 658.1 | 673 | 51.4 | 121.8 | 162.3 | 92.4 | 292.3 | 283.4 | 113.9 | 232.9 | 297.3 | 152.1
695 | 501 | 465.5 | 186.2 | 217.6571 | 280.2 | 257.4 | 274.2 | 260.6 | 465.1 | 37.4 | 20.3 | 67.4 | 4.9 | 225.2 | 11.3 | 910.6 | 756.7 | 730.4 | 855 | 705.3 | 738.7 | 671.5 | 675 | 659.4 | 672.7 | 51.6 | 122.1 | 162.6 | 92.6 | 292.9 | 283.4 | 114.1 | 233.2 | 297.9 | 152.4
696 | 502 | 465.4 | 186.16 | 217.6103 | 280.2 | 256.3 | 275.1 | 259.9 | 476.3 | 37.4 | 20.3 | 67.4 | 5.4 | 240.4 | 12.4 | 909.8 | 754.4 | 737.1 | 854.5 | 703.4 | 737.1 | 664.9 | 670.8 | 660.5 | 670.1 | 51.7 | 122.4 | 162.9 | 92.8 | 293.6 | 283.6 | 114.3 | 233.4 | 298.4 | 152.7
697 | 503 | 465.1 | 186.04 | 217.47 | 280.2 | 254.9 | 275.5 | 259.2 | 479.8 | 37.5 | 20.3 | 67.3 | 5.2 | 226 | 12.6 | 909.8 | 751.5 | 736.8 | 854.1 | 701.8 | 735.4 | 661.9 | 664.5 | 661.5 | 667.1 | 51.9 | 122.7 | 163.4 | 93 | 294.4 | 283.8 | 114.6 | 233.6 | 299 | 153
698 | 504 | 468.1 | 187.24 | 218.8728 | 280.5 | 255.8 | 275.2 | 259.8 | 483.5 | 37.5 | 20.3 | 67.3 | 4.9 | 242.5 | 11.3 | 910 | 750.9 | 740.9 | 853.7 | 701.3 | 736.7 | 659 | 671.7 | 662.6 | 666.8 | 52 | 122.9 | 163.9 | 93.2 | 295.6 | 283.6 | 114.8 | 233.8 | 299.6 | 153.3
699 | 505 | 467 | 186.8 | 218.3584 | 281.3 | 257.1 | 274.8 | 260.4 | 497.6 | 37.4 | 20.3 | 67.3 | 5 | 252.3 | 10.4 | 909.7 | 750.1 | 736.7 | 853.2 | 699.1 | 738.8 | 656.7 | 671.5 | 663.7 | 665 | 52.2 | 123.2 | 164.6 | 93.4 | 296.8 | 283.4 | 115 | 234 | 300.2 | 153.7
700 | 506 | 465.9 | 186.36 | 217.8441 | 281.5 | 256.5 | 275.3 | 263.3 | 502.1 | 37.4 | 20.3 | 67.3 | 5.7 | 251.5 | 11.4 | 909.5 | 753.2 | 741.6 | 853.2 | 701.1 | 738.3 | 658 | 676.8 | 664.4 | 667.3 | 52.3 | 123.4 | 164.6 | 93.6 | 297 | 283.7 | 115.2 | 234.2 | 300.7 | 154
701 | 507 | 465.9 | 186.36 | 217.8441 | 282 | 256.8 | 275.3 | 265.1 | 497.9 | 37.4 | 20.3 | 67.3 | 5.5 | 258.6 | 11.4 | 909.2 | 755.2 | 745 | 853.6 | 702.7 | 737 | 659.9 | 681 | 665.1 | 668.1 | 52.4 | 123.7 | 164.8 | 93.8 | 298.4 | 283.9 | 115.5 | 234.6 | 301.4 | 154.3
702 | 508 | 465.5 | 186.2 | 217.6571 | 281.7 | 256.2 | 275.7 | 266.8 | 493.2 | 37.5 | 20.3 | 67.4 | 5.4 | 253.3 | 10.7 | 908.6 | 756.4 | 741.4 | 854 | 701.7 | 735.4 | 662.3 | 680.3 | 665.8 | 669.4 | 52.6 | 123.9 | 165.3 | 94.1 | 297.8 | 284 | 115.7 | 235 | 301.9 | 154.6
703 | 509 | 466 | 186.4 | 217.8909 | 281.9 | 255.1 | 276.6 | 267.5 | 493.7 | 37.5 | 20.3 | 67.6 | 6.2 | 251.3 | 11.7 | 907.9 | 757.2 | 736.4 | 854.1 | 700.2 | 735 | 663.1 | 684.8 | 666.5 | 669.1 | 52.7 | 124.1 | 165.6 | 94.3 | 297.8 | 284.2 | 115.9 | 235.2 | 302.5 | 154.9
704 | 510 | 466.1 | 186.44 | 217.9376 | 282.5 | 254.7 | 278.6 | 267.5 | 491.1 | 37.5 | 20.3 | 67.7 | 6.4 | 250.3 | 12.6 | 907.4 | 758.3 | 736.5 | 854.3 | 699.9 | 735.1 | 666.8 | 694.6 | 667.3 | 670.6 | 52.9 | 124.4 | 165.8 | 94.5 | 297.7 | 284.5 | 116.1 | 235.4 | 303 | 155.2
705 | 511 | 466.5 | 186.6 | 218.1246 | 282.9 | 255.5 | 279.1 | 266.7 | 487.4 | 37.5 | 20.3 | 67.8 | 5.9 | 252 | 13.8 | 907 | 760.5 | 747.7 | 854.7 | 701.1 | 737.6 | 671.6 | 708.2 | 668.1 | 673.4 | 53 | 124.6 | 166 | 94.7 | 297.9 | 284.6 | 116.4 | 235.8 | 303.6 | 155.5
706 | 512 | 466.3 | 186.52 | 218.0311 | 283.3 | 256.2 | 278.2 | 266.2 | 489.6 | 37.5 | 20.3 | 68 | 5.4 | 237 | 14.1 | 907 | 762.6 | 764.3 | 855 | 704.3 | 738.7 | 674.5 | 716 | 668.9 | 676.3 | 53.2 | 124.8 | 166.2 | 94.9 | 298.1 | 284.6 | 116.6 | 236.1 | 304.1 | 155.8
707 | 513 | 465.5 | 186.2 | 217.6571 | 283.1 | 257.6 | 276.4 | 264.7 | 498.4 | 37.6 | 20.3 | 68 | 4.9 | 238.6 | 14.3 | 906.1 | 765.7 | 778.6 | 855.5 | 708 | 741.6 | 677.9 | 729.7 | 669.8 | 681 | 53.3 | 125.1 | 166.4 | 95.1 | 298.2 | 285 | 116.8 | 236.3 | 304.7 | 156
708 | 514 | 466.8 | 186.72 | 218.2649 | 283 | 257.6 | 275.9 | 264.4 | 508 | 37.6 | 20.3 | 67.9 | 4.6 | 224.2 | 14.1 | 905.2 | 768.1 | 781.9 | 855.8 | 709.4 | 744.1 | 681.3 | 742.9 | 670.8 | 684.5 | 53.5 | 125.3 | 166.6 | 95.3 | 298.5 | 285.7 | 117 | 236.5 | 305.2 | 156.3
709 | 515 | 466.6 | 186.64 | 218.1714 | 282.9 | 258.2 | 276.1 | 265.1 | 517.5 | 37.7 | 20.3 | 67.9 | 6 | 225.5 | 11.7 | 905.4 | 770.3 | 776.7 | 856.5 | 708.5 | 745.5 | 683.7 | 745.6 | 671.7 | 685.9 | 53.6 | 125.6 | 167.1 | 95.5 | 298.4 | 286 | 117.3 | 236.7 | 305.8 | 156.6
710 | 516 | 466.7 | 186.68 | 218.2182 | 283.4 | 258.5 | 276.2 | 265.9 | 520.1 | 37.7 | 20.3 | 68 | 6.2 | 221.9 | 11.1 | 905 | 771.6 | 782.3 | 856.9 | 710 | 745.9 | 685.3 | 748 | 672.3 | 686.5 | 53.8 | 125.8 | 167.3 | 95.7 | 298.1 | 286.1 | 117.5 | 236.9 | 306.4 | 156.9
711 | 517 | 466.8 | 186.72 | 218.2649 | 283.4 | 259.1 | 276.3 | 265.9 | 514.8 | 37.8 | 20.3 | 68 | 6.1 | 236 | 12.3 | 904 | 773.1 | 794.5 | 856.8 | 712.2 | 745.9 | 685.9 | 750.4 | 672.9 | 687.7 | 53.9 | 126.1 | 167.4 | 95.9 | 298 | 286.1 | 117.7 | 237.1 | 306.9 | 157.2
712 | 518 | 466.9 | 186.76 | 218.3117 | 283.7 | 260.2 | 276.7 | 265.2 | 513.9 | 37.8 | 20.3 | 68 | 6.1 | 242.8 | 12.5 | 903.9 | 773.7 | 791.5 | 856.8 | 713.3 | 746.5 | 685 | 751.6 | 673.4 | 688.4 | 54 | 126.3 | 167.8 | 96.1 | 298 | 286.3 | 117.9 | 237.4 | 307.5 | 157.4
713 | 519 | 467 | 186.8 | 218.3584 | 284.2 | 260.9 | 277 | 264.6 | 518.8 | 37.8 | 20.3 | 68 | 6.1 | 238.6 | 11.6 | 904.1 | 773 | 788.9 | 856.8 | 712.8 | 746.2 | 682 | 743.4 | 673.8 | 685.3 | 54.2 | 126.6 | 168 | 96.3 | 297.9 | 286.5 | 118.2 | 237.7 | 307.9 | 157.7
714 | 520 | 467 | 186.8 | 218.3584 | 284.7 | 260.4 | 277.6 | 263.1 | 518.3 | 37.8 | 20.3 | 67.8 | 6.3 | 246.4 | 12.3 | 904.2 | 772.1 | 787.4 | 856.8 | 713.2 | 746 | 680 | 739.5 | 674.3 | 683.7 | 54.3 | 126.8 | 168.3 | 96.5 | 297.9 | 286.5 | 118.4 | 237.8 | 308.5 | 158
715 | 521 | 466.2 | 186.48 | 217.9844 | 284.7 | 260.8 | 278 | 261.9 | 519.3 | 37.8 | 20.3 | 67.8 | 6 | 246.6 | 13 | 903.5 | 772.3 | 790.7 | 856.5 | 714.8 | 747 | 681.8 | 745.5 | 675 | 685 | 54.5 | 127.1 | 168.5 | 96.8 | 297.8 | 286.7 | 118.6 | 238 | 309.1 | 158.3
716 | 522 | 466.9 | 186.76 | 218.3117 | 284.5 | 260.1 | 277.3 | 261.6 | 520 | 37.8 | 20.2 | 68 | 6 | 259.2 | 12.2 | 902.9 | 774.4 | 796.7 | 856.5 | 718.4 | 749.1 | 686.4 | 755.2 | 675.9 | 690 | 54.6 | 127.4 | 168.8 | 97 | 297.9 | 286.5 | 118.8 | 238.2 | 309.7 | 158.6
717 | 523 | 466.7 | 186.68 | 218.2182 | 284.6 | 258.7 | 276.1 | 262.4 | 530.9 | 37.8 | 20.2 | 68.2 | 6.3 | 271.1 | 10.5 | 901.9 | 775.5 | 804.6 | 856.6 | 721.4 | 751.1 | 687.9 | 761.1 | 677.1 | 692.2 | 54.8 | 127.7 | 169.2 | 97.2 | 297.6 | 286.4 | 119.1 | 238.4 | 310.2 | 158.9
718 | 524 | 466.7 | 186.68 | 218.2182 | 284.4 | 258.6 | 275.7 | 262.4 | 543.1 | 37.8 | 20.2 | 68.4 | 6.2 | 257 | 10.6 | 900.7 | 776.6 | 811.9 | 856.9 | 723.4 | 752.5 | 690.8 | 766.7 | 677.9 | 695.2 | 54.9 | 128 | 169.6 | 97.4 | 297.6 | 286.1 | 119.3 | 238.5 | 310.8 | 159.2
719 | 525 | 467.6 | 187.04 | 218.639 | 284 | 258.7 | 275.9 | 263.1 | 545.6 | 37.9 | 20.2 | 68.6 | 6.7 | 259.2 | 12.8 | 901.4 | 778.6 | 811.6 | 857.5 | 723.7 | 753.6 | 691.5 | 771.5 | 678.5 | 696.8 | 55.1 | 128.2 | 169.8 | 97.6 | 298.3 | 286.1 | 119.5 | 238.8 | 311.5 | 159.4
720 | 526 | 466.4 | 186.56 | 218.0779 | 283.6 | 258.8 | 275.1 | 264.5 | 549.8 | 37.9 | 20.2 | 68.8 | 7.5 | 249.9 | 11.9 | 902.5 | 780 | 807.9 | 858 | 724.9 | 755.2 | 692.5 | 775 | 679.3 | 698.6 | 55.2 | 128.5 | 170 | 97.8 | 299 | 286.1 | 119.8 | 239 | 312.1 | 159.7
721 | 527 | 465.7 | 186.28 | 217.7506 | 283.7 | 258.7 | 274.3 | 266.2 | 554.8 | 37.9 | 20.2 | 68.9 | 6.9 | 242.6 | 10.8 | 903.9 | 781.9 | 807.3 | 858.4 | 725.8 | 756.7 | 691.1 | 775.3 | 680 | 699.1 | 55.4 | 128.7 | 170.4 | 98 | 298.9 | 286.3 | 120 | 239.2 | 312.7 | 160
722 | 528 | 465.6 | 186.24 | 217.7038 | 283.7 | 257.6 | 274.9 | 267.7 | 550.6 | 37.8 | 20.2 | 69 | 5.7 | 256.4 | 9.3 | 903.2 | 781.8 | 813.3 | 858.7 | 727.2 | 759.1 | 697.1 | 778.1 | 680.7 | 701.4 | 55.5 | 129 | 170.6 | 98.2 | 299 | 286.4 | 120.2 | 239.4 | 313.5 | 160.3
723 | 529 | 466.5 | 186.6 | 218.1246 | 283.1 | 257.2 | 274.2 | 268.1 | 564.2 | 37.8 | 20.2 | 69 | 4.9 | 258.1 | 8.4 | 901.8 | 781.9 | 816.9 | 858.7 | 730.4 | 762.1 | 703.7 | 781.7 | 681.9 | 704.9 | 55.7 | 129.2 | 171.1 | 98.4 | 299.6 | 286.6 | 120.5 | 239.7 | 314.2 | 160.6
724 | 530 | 466.3 | 186.52 | 218.0311 | 282.6 | 257.2 | 274.9 | 269.2 | 572.3 | 37.7 | 20.2 | 69 | 5 | 234.7 | 8.3 | 900.9 | 783.2 | 818.7 | 858.9 | 731.9 | 764.3 | 707 | 785.5 | 682.8 | 709 | 55.8 | 129.5 | 171.4 | 98.6 | 299.6 | 286.8 | 120.7 | 239.9 | 314.9 | 160.9
725 | 531 | 466.4 | 186.56 | 218.0779 | 282.6 | 257.1 | 275.7 | 270.7 | 565 | 37.8 | 20.2 | 69.1 | 6.3 | 237.7 | 8.2 | 902.8 | 783.9 | 815.3 | 858.9 | 732 | 765 | 704 | 780.2 | 683.3 | 708 | 56 | 129.8 | 171.6 | 98.8 | 299.9 | 287 | 120.9 | 240.2 | 315.5 | 161.2
726 | 532 | 465.7 | 186.28 | 217.7506 | 282.6 | 256.4 | 276.1 | 271.2 | 559.3 | 37.8 | 20.2 | 69.1 | 8.2 | 257 | 10 | 903.3 | 784.9 | 813.2 | 859 | 732.7 | 765.7 | 702.2 | 776.7 | 683.7 | 706.1 | 56.2 | 130 | 172.1 | 99 | 299.8 | 287.1 | 121.2 | 240.4 | 316 | 161.5
727 | 533 | 466.5 | 186.6 | 218.1246 | 282.3 | 255.9 | 276.3 | 271.4 | 549.4 | 37.9 | 20.2 | 69.2 | 8.3 | 247.7 | 11.9 | 904.3 | 784.6 | 806.2 | 859 | 733 | 766.3 | 700 | 774.2 | 683.9 | 707.3 | 56.3 | 130.3 | 172.1 | 99.3 | 299.4 | 287.1 | 121.4 | 240.6 | 316.4 | 161.8
728 | 534 | 467 | 186.8 | 218.3584 | 281.7 | 255.9 | 276.2 | 271.7 | 539.1 | 38 | 20.2 | 69.2 | 7.3 | 238.6 | 14.5 | 905.2 | 783.9 | 800.1 | 859 | 730.3 | 765.7 | 697.9 | 767.6 | 684.1 | 705.3 | 56.5 | 130.5 | 172.4 | 99.5 | 299.4 | 287.1 | 121.7 | 240.8 | 316.9 | 162
729 | 535 | 465.9 | 186.36 | 217.8441 | 282.2 | 256.2 | 275.3 | 272.6 | 534.5 | 38.1 | 20.2 | 69.2 | 5.7 | 239.7 | 14 | 905.4 | 783.5 | 795.4 | 859 | 729.8 | 765.5 | 696.3 | 761.8 | 684.3 | 704.3 | 56.6 | 130.8 | 172.7 | 99.7 | 299.4 | 287.2 | 121.9 | 241 | 317.5 | 162.3
730 | 536 | 467.1 | 186.84 | 218.4052 | 282.8 | 256.5 | 275.1 | 273 | 527.9 | 38.2 | 20.2 | 69.3 | 5.5 | 237.9 | 12.5 | 905.9 | 782 | 785.6 | 859.1 | 726.4 | 765.6 | 694.7 | 758.9 | 684.7 | 702.4 | 56.8 | 131 | 173 | 99.9 | 299.3 | 287 | 122.1 | 241.2 | 318.1 | 162.6
731 | 537 | 465.5 | 186.2 | 217.6571 | 282.8 | 256.7 | 275.4 | 272.2 | 526.9 | 38.3 | 20.2 | 69.3 | 5 | 248.1 | 11.9 | 906.3 | 780.8 | 779.4 | 859.5 | 725.4 | 766.7 | 696 | 759.5 | 685.3 | 702.3 | 56.9 | 131.3 | 173.2 | 100.1 | 299.5 | 286.8 | 122.3 | 241.3 | 318.7 | 162.9
732 | 538 | 465.1 | 186.04 | 217.47 | 283.1 | 257.1 | 275.1 | 271.8 | 515.5 | 38.3 | 20.2 | 69.3 | 6.6 | 241.6 | 11.2 | 906.6 | 780 | 786.9 | 860 | 727.1 | 766.8 | 695.9 | 761.8 | 685.9 | 703.5 | 57.1 | 131.5 | 173.5 | 100.3 | 299.7 | 286.7 | 122.5 | 241.5 | 319.3 | 163.2
733 | 539 | 465.3 | 186.12 | 217.5636 | 282.6 | 256.6 | 275.5 | 272.1 | 512.5 | 38.3 | 20.2 | 69.3 | 7.9 | 244.9 | 11.3 | 906.9 | 779.4 | 791.3 | 860.5 | 728.1 | 768 | 693.1 | 760.7 | 686.7 | 702.4 | 57.2 | 131.7 | 173.8 | 100.5 | 300.4 | 286.6 | 122.8 | 241.7 | 319.9 | 163.4
734 | 540 | 466 | 186.4 | 217.8909 | 282.4 | 256.7 | 275.9 | 271.9 | 517.1 | 38.4 | 20.2 | 69.3 | 7.2 | 247.7 | 10 | 907 | 779.2 | 792.9 | 860.8 | 727.7 | 769.3 | 692.6 | 762.5 | 687.5 | 703.1 | 57.4 | 132 | 174 | 100.7 | 300.6 | 286.6 | 123 | 241.9 | 320.4 | 163.7
735 | 541 | 465.8 | 186.32 | 217.7973 | 283.2 | 257.5 | 275.3 | 271.5 | 517.7 | 38.5 | 20.2 | 69.3 | 8 | 250.9 | 8.8 | 907.9 | 780.5 | 793.7 | 861.6 | 726 | 770.9 | 694.2 | 766.3 | 688 | 703.6 | 57.6 | 132.3 | 174.3 | 100.9 | 300.4 | 286.6 | 123.2 | 242.1 | 321 | 164
736 | 542 | 465.6 | 186.24 | 217.7038 | 283.2 | 258.1 | 275.1 | 271.1 | 516.7 | 38.5 | 20.2 | 69.4 | 5.5 | 250.1 | 12.9 | 909.3 | 781.8 | 789 | 862.3 | 724.2 | 771.3 | 696 | 768.6 | 688.5 | 704.2 | 57.7 | 132.5 | 174.4 | 101.1 | 300.4 | 286.7 | 123.5 | 242.4 | 321.6 | 164.3
737 | 543 | 466 | 186.4 | 217.8909 | 283.5 | 257 | 275.2 | 271.3 | 513.5 | 38.5 | 20.2 | 69.4 | 6.4 | 254.5 | 13.6 | 909.5 | 781.2 | 787.2 | 862.8 | 722.9 | 770.6 | 696.2 | 765.1 | 688.8 | 702.4 | 57.9 | 132.8 | 174.8 | 101.3 | 300.2 | 287.1 | 123.7 | 242.6 | 322.1 | 164.6
738 | 544 | 466.3 | 186.52 | 218.0311 | 284.3 | 256.4 | 275.5 | 270.9 | 507.3 | 38.5 | 20.2 | 69.4 | 6.6 | 251.5 | 12.4 | 909.9 | 780.4 | 791.1 | 863.4 | 722.1 | 769.8 | 694.7 | 761.9 | 689 | 701.4 | 58 | 133 | 175 | 101.6 | 300.3 | 287.2 | 124 | 242.9 | 322.6 | 164.9
739 | 545 | 466.3 | 186.52 | 218.0311 | 284.8 | 256.2 | 276 | 269.6 | 510.3 | 38.5 | 20.2 | 69.3 | 6.8 | 241.4 | 11.6 | 910.7 | 781.6 | 795.3 | 864 | 723 | 771.9 | 694 | 764.9 | 689.8 | 702.4 | 58.2 | 133.3 | 175.4 | 101.8 | 301.6 | 287.5 | 124.2 | 243.1 | 323.1 | 165.2
740 | 546 | 466.7 | 186.68 | 218.2182 | 284.8 | 256.9 | 276.8 | 268.2 | 512.4 | 38.6 | 20.2 | 69.1 | 7.3 | 242.2 | 13.3 | 911.1 | 779.6 | 791.2 | 864.3 | 719.8 | 771.5 | 688.1 | 756.6 | 690.1 | 699.6 | 58.3 | 133.6 | 175.9 | 102 | 301.2 | 287.8 | 124.4 | 243.3 | 323.7 | 165.5
741 | 547 | 466.9 | 186.76 | 218.3117 | 285 | 256.6 | 278 | 267.2 | 510 | 38.6 | 20.2 | 68.9 | 6.9 | 243.9 | 10.8 | 912.2 | 777.4 | 789.9 | 864.9 | 717.7 | 770.7 | 685.6 | 750 | 690.4 | 697.3 | 58.5 | 133.8 | 176 | 102.2 | 300.9 | 287.9 | 124.7 | 243.5 | 324.3 | 165.8
742 | 548 | 466.4 | 186.56 | 218.0779 | 285.3 | 255.7 | 278.6 | 266.4 | 514.7 | 38.5 | 20.2 | 68.7 | 5.8 | 244 | 9.4 | 913 | 775.7 | 790 | 865.1 | 716.5 | 770.3 | 681.3 | 743.5 | 691 | 696 | 58.7 | 134.1 | 176.4 | 102.4 | 300.7 | 287.8 | 124.9 | 243.6 | 324.9 | 166
743 | 549 | 466.2 | 186.48 | 217.9844 | 286 | 255.6 | 278.8 | 266.3 | 522.7 | 38.5 | 20.2 | 68.7 | 7.9 | 251.7 | 9.2 | 913.5 | 773.7 | 790.1 | 865.7 | 717 | 769.8 | 676.2 | 737.9 | 691.2 | 693.5 | 58.8 | 134.3 | 176.8 | 102.6 | 300.5 | 287.6 | 125.1 | 243.8 | 325.4 | 166.3
744 | 550 | 466.2 | 186.48 | 217.9844 | 286.4 | 255.3 | 279.7 | 266.7 | 525.3 | 38.5 | 20.2 | 68.8 | 8.1 | 221.3 | 8.3 | 913.4 | 774.1 | 794.4 | 865.9 | 718.1 | 770.8 | 675.6 | 742.1 | 691.6 | 694.6 | 59 | 134.6 | 176.9 | 102.8 | 301.7 | 287.6 | 125.4 | 244 | 326 | 166.6
745 | 551 | 466.5 | 186.6 | 218.1246 | 287 | 255.5 | 280.3 | 268.9 | 528.3 | 38.5 | 20.2 | 69 | 6.5 | 252.4 | 7.3 | 913.4 | 772.6 | 790.4 | 866.2 | 715.5 | 770.6 | 674.4 | 737.6 | 692.1 | 692.9 | 59.1 | 134.8 | 177.2 | 103 | 302 | 287.7 | 125.6 | 244.1 | 326.3 | 166.9
746 | 552 | 465 | 186 | 217.4233 | 287.3 | 257.2 | 280 | 271.2 | 535.6 | 38.5 | 20.2 | 69.2 | 6 | 261.8 | 8.7 | 913.6 | 772.3 | 794.7 | 866.5 | 715.1 | 770.5 | 673.8 | 733.6 | 692.7 | 690.8 | 59.3 | 135.1 | 177.6 | 103.2 | 302.5 | 287.9 | 125.8 | 244.4 | 326.7 | 167.2
747 | 553 | 466.8 | 186.72 | 218.2649 | 287.3 | 257.5 | 280.5 | 272.8 | 539.9 | 38.5 | 20.2 | 69.4 | 6 | 258.5 | 12.1 | 914.4 | 773.7 | 797.4 | 867.2 | 715.5 | 771.7 | 674.7 | 739.6 | 693.3 | 692.7 | 59.4 | 135.5 | 177.8 | 103.4 | 303.1 | 288.1 | 126.1 | 244.6 | 327 | 167.5
748 | 554 | 466.3 | 186.52 | 218.0311 | 286.9 | 258.1 | 281.8 | 273.6 | 541.7 | 38.5 | 20.2 | 69.6 | 5.8 | 255.3 | 12.5 | 914.8 | 772.7 | 795.5 | 867.7 | 715 | 770.9 | 672.8 | 738.6 | 693.6 | 690.8 | 59.6 | 135.8 | 178.2 | 103.6 | 304.1 | 288 | 126.3 | 244.8 | 327.4 | 167.8
749 | 555 | 465.4 | 186.16 | 217.6103 | 287.4 | 258.2 | 282.4 | 274.9 | 532.8 | 38.6 | 20.2 | 69.7 | 5.5 | 249.7 | 11.6 | 915.2 | 770.4 | 787.2 | 867.9 | 713.1 | 769.2 | 670.1 | 732.6 | 693.6 | 689.2 | 59.8 | 136.1 | 178.4 | 103.8 | 304.7 | 288.4 | 126.6 | 245 | 327.9 | 168.1
750 | 556 | 464.7 | 185.88 | 217.283 | 288.2 | 257.8 | 282.9 | 275.6 | 524.2 | 38.7 | 20.2 | 69.8 | 4.4 | 245.1 | 11.5 | 915.1 | 765.6 | 772.2 | 867.5 | 708.8 | 766.2 | 666.9 | 718.1 | 693.6 | 684.8 | 59.9 | 136.3 | 178.9 | 104 | 306.5 | 288.7 | 126.8 | 245.2 | 328.3 | 168.4
751 | 557 | 464.7 | 185.88 | 217.283 | 289.1 | 258.2 | 283.4 | 274.6 | 509.5 | 38.8 | 20.2 | 69.7 | 4.3 | 240.5 | 11.8 | 915 | 762 | 760 | 867.1 | 705.5 | 762 | 663.3 | 701 | 693.5 | 680.5 | 60.1 | 136.6 | 179.1 | 104.3 | 305.9 | 289.4 | 127.1 | 245.6 | 328.7 | 168.7
752 | 558 | 464.9 | 185.96 | 217.3765 | 290.1 | 259.2 | 282 | 274.3 | 503.7 | 38.9 | 20.2 | 69.7 | 4.9 | 245.3 | 12.1 | 915.3 | 761.1 | 757.8 | 867.2 | 703.5 | 761.1 | 664.9 | 699.8 | 693.9 | 679.3 | 60.2 | 136.9 | 179.4 | 104.5 | 305.8 | 289.7 | 127.3 | 245.8 | 329.1 | 169
753 | 559 | 466.7 | 186.68 | 218.2182 | 290.4 | 260.3 | 282.8 | 273.1 | 501.1 | 39 | 20.2 | 69.8 | 5.1 | 243.1 | 11.8 | 915.1 | 761.2 | 756.1 | 867.2 | 702.1 | 760.7 | 663.1 | 703.6 | 694.4 | 679.1 | 60.4 | 137.2 | 179.4 | 104.7 | 305.6 | 290 | 127.5 | 246 | 329.6 | 169.3
754 | 560 | 465.6 | 186.24 | 217.7038 | 290.2 | 261.1 | 283.5 | 271.9 | 491.3 | 39.1 | 20.2 | 69.8 | 6.4 | 232.8 | 10.7 | 914.2 | 760.2 | 749.7 | 866.9 | 700.2 | 758.4 | 659.9 | 697.7 | 694.5 | 677.5 | 60.6 | 137.4 | 179.7 | 104.9 | 305.8 | 290 | 127.7 | 246.2 | 330.1 | 169.6
755 | 561 | 466.2 | 186.48 | 217.9844 | 291.1 | 260.4 | 283.7 | 272 | 483.6 | 39.3 | 20.2 | 69.7 | 6.3 | 269.9 | 9.8 | 913 | 752.6 | 736.8 | 865.9 | 695.2 | 753.5 | 652.3 | 677.8 | 694.4 | 671.1 | 60.7 | 137.6 | 180.3 | 105.1 | 306.7 | 290 | 128 | 246.3 | 330.6 | 169.9
756 | 562 | 467.1 | 186.84 | 218.4052 | 293.3 | 259.9 | 283.3 | 273.2 | 474.7 | 39.4 | 20.2 | 69.6 | 5.5 | 264 | 9.3 | 911.8 | 746.3 | 729.2 | 865.1 | 691.9 | 748.7 | 646.3 | 660.8 | 694.2 | 666.5 | 60.9 | 137.9 | 180.5 | 105.3 | 306.3 | 289.7 | 128.2 | 246.4 | 331 | 170.3
757 | 563 | 466.5 | 186.6 | 218.1246 | 294 | 260.2 | 283.3 | 274.3 | 467.9 | 39.4 | 20.2 | 69.6 | 5.5 | 265.3 | 8.1 | 911.3 | 744.3 | 736.8 | 864.8 | 691.5 | 746.5 | 643 | 658.4 | 694.3 | 664.4 | 61 | 138.1 | 180.5 | 105.5 | 306.1 | 289.3 | 128.4 | 246.4 | 331.5 | 170.6
758 | 564 | 464.4 | 185.76 | 217.1427 | 293.9 | 260.4 | 283.7 | 275.5 | 474.7 | 39.4 | 20.2 | 69.6 | 5.2 | 265.1 | 6.5 | 910.9 | 747.5 | 744.9 | 864.8 | 692.3 | 747.5 | 646 | 669.9 | 694.9 | 665.5 | 61.2 | 138.4 | 180.8 | 105.7 | 306.3 | 289.3 | 128.6 | 246.6 | 331.9 | 170.9
759 | 565 | 465.4 | 186.16 | 217.6103 | 293.8 | 262.3 | 283.1 | 276.6 | 476.4 | 39.3 | 20.2 | 69.7 | 4.5 | 262.4 | 7.6 | 910 | 748.1 | 749.6 | 865.2 | 691.4 | 746.5 | 647.9 | 674.6 | 695.2 | 665 | 61.4 | 138.6 | 181.1 | 105.9 | 305.8 | 289.2 | 128.8 | 246.8 | 332.5 | 171.2
760 | 566 | 465.6 | 186.24 | 217.7038 | 293.6 | 263.3 | 282.3 | 276.8 | 479.7 | 39.2 | 20.2 | 69.7 | 4.3 | 272.3 | 8.9 | 909.6 | 750.3 | 755.6 | 866 | 692.8 | 747.7 | 651.2 | 683.9 | 695.8 | 666.5 | 61.5 | 138.8 | 181.3 | 106.1 | 305.4 | 289.2 | 129.1 | 246.9 | 333 | 171.4
761 | 567 | 465.2 | 186.08 | 217.5168 | 293.8 | 263.2 | 281.8 | 276.2 | 491.3 | 39.2 | 20.2 | 69.8 | 4.9 | 259.7 | 10.3 | 909.2 | 752.9 | 766.6 | 866.3 | 694.2 | 750 | 653.8 | 696.5 | 696.9 | 667.3 | 61.7 | 139.1 | 181.8 | 106.3 | 305.5 | 289.3 | 129.3 | 247.1 | 333.6 | 171.7
762 | 568 | 465.3 | 186.12 | 217.5636 | 294 | 263.1 | 282.1 | 275.4 | 507.2 | 39.1 | 20.2 | 69.9 | 4.7 | 257.3 | 11.6 | 908.4 | 756.1 | 783.3 | 866.9 | 696.3 | 751.1 | 654.9 | 707.2 | 698.1 | 668.7 | 61.8 | 139.4 | 182.2 | 106.5 | 305.7 | 289.3 | 129.5 | 247.2 | 334.3 | 171.9
763 | 569 | 465.5 | 186.2 | 217.6571 | 293.4 | 263.3 | 281.5 | 274.9 | 522.6 | 39.1 | 20.2 | 70 | 4.6 | 267.3 | 11.9 | 907.2 | 756.6 | 789 | 867.4 | 696 | 751.8 | 652.9 | 707.3 | 699.1 | 667.5 | 62 | 139.6 | 182.5 | 106.8 | 306.1 | 289.3 | 129.8 | 247.4 | 334.8 | 172.2
764 | 570 | 467.7 | 187.08 | 218.6857 | 292.8 | 263.8 | 281.4 | 275.5 | 534.3 | 39.1 | 20.2 | 70.1 | 5.1 | 280.8 | 12 | 907.1 | 758 | 790.1 | 868.2 | 696.8 | 752.5 | 651.5 | 710.7 | 700.1 | 667.9 | 62.2 | 139.9 | 182.9 | 107 | 306.1 | 289.3 | 130 | 247.6 | 335.4 | 172.6
765 | 571 | 467.8 | 187.12 | 218.7325 | 292.7 | 264.6 | 282.5 | 276.7 | 544.6 | 39 | 20.2 | 70.2 | 5.5 | 288.5 | 12 | 906.8 | 755.2 | 789.1 | 868.7 | 693.6 | 751.7 | 648.7 | 702.6 | 701.1 | 665.3 | 62.3 | 140.2 | 183.7 | 107.2 | 306 | 289.2 | 130.2 | 247.7 | 336 | 172.9
766 | 572 | 465.5 | 186.2 | 217.6571 | 292.4 | 264.9 | 283.3 | 279 | 547.3 | 39.1 | 20.2 | 70.3 | 5.5 | 270 | 12.1 | 906.5 | 753 | 781.6 | 869 | 690.7 | 750.1 | 644.3 | 692.9 | 701.2 | 662.9 | 62.5 | 140.4 | 183.8 | 107.4 | 305.9 | 289.1 | 130.4 | 247.8 | 336.6 | 173.2
767 | 573 | 466.6 | 186.64 | 218.1714 | 292.3 | 265.6 | 282.9 | 281.6 | 546.2 | 39.1 | 20.2 | 70.3 | 5.8 | 276.4 | 11.9 | 906.5 | 756.1 | 791.5 | 869.6 | 693.8 | 751.5 | 647.6 | 706.5 | 701.9 | 665.2 | 62.7 | 140.7 | 184.1 | 107.6 | 307.3 | 289 | 130.7 | 248 | 337.2 | 173.5
768 | 574 | 466.5 | 186.6 | 218.1246 | 292.4 | 266.2 | 282.6 | 283.1 | 551.1 | 39.1 | 20.2 | 70.6 | 6.7 | 270.9 | 11 | 906.7 | 759.4 | 794.3 | 870 | 695 | 753.3 | 652.1 | 718.2 | 702.3 | 666.9 | 62.8 | 141.1 | 184.4 | 107.8 | 307.6 | 289.2 | 130.9 | 248.2 | 337.7 | 173.8
769 | 575 | 467.8 | 187.12 | 218.7325 | 292.9 | 266.3 | 283.8 | 283.7 | 543.2 | 39.1 | 20.2 | 70.7 | 6.9 | 261 | 10.7 | 906.6 | 762.1 | 799 | 870.3 | 698.6 | 753.7 | 656.2 | 726.4 | 702.4 | 669.8 | 63 | 141.4 | 184.4 | 108 | 307.8 | 289.4 | 131.2 | 248.5 | 338.2 | 174.1
770 | 576 | 467.4 | 186.96 | 218.5455 | 293.6 | 266.4 | 284.7 | 284.3 | 531.1 | 39.1 | 20.2 | 70.8 | 7 | 254.4 | 11.4 | 905.9 | 764 | 800.8 | 870.1 | 699.9 | 753.7 | 658.2 | 728.4 | 702.3 | 670.2 | 63.1 | 141.7 | 184.6 | 108.2 | 307.7 | 289.6 | 131.4 | 248.7 | 338.7 | 174.4
771 | 577 | 467.3 | 186.92 | 218.4987 | 294.7 | 266.5 | 284.2 | 284.3 | 519.5 | 39.1 | 20.2 | 70.8 | 7.1 | 254 | 11 | 905 | 762.2 | 798.3 | 869.6 | 699 | 752.8 | 655 | 721.7 | 702.2 | 667.1 | 63.3 | 141.9 | 185.3 | 108.4 | 307.7 | 289.9 | 131.7 | 248.9 | 339.1 | 174.7
772 | 578 | 467.7 | 187.08 | 218.6857 | 295.1 | 266.1 | 282.4 | 283.8 | 519.7 | 39 | 20.2 | 70.8 | 7.4 | 245 | 11 | 904.4 | 763.5 | 801.6 | 869.5 | 700.8 | 754.4 | 655.9 | 724.5 | 702.7 | 668.4 | 63.5 | 142.2 | 185.4 | 108.6 | 307.7 | 290.3 | 131.9 | 249 | 339.6 | 174.9
773 | 579 | 467.9 | 187.16 | 218.7793 | 294.7 | 265.1 | 281.4 | 282.5 | 516.4 | 39 | 20.2 | 70.8 | 7.5 | 249.3 | 10.7 | 903.8 | 764.2 | 798 | 869.5 | 700.8 | 754 | 654.9 | 725.8 | 702.6 | 668.6 | 63.6 | 142.4 | 185.6 | 108.8 | 307.5 | 290.4 | 132.1 | 249.3 | 340.1 | 175.2
774 | 580 | 467.7 | 187.08 | 218.6857 | 294 | 265.5 | 281.3 | 282.3 | 506.8 | 39.1 | 20.1 | 71 | 6.7 | 241 | 10.1 | 903.5 | 762 | 787.4 | 869.6 | 698.3 | 752.7 | 653.4 | 721.9 | 702.4 | 667.2 | 63.8 | 142.7 | 185.7 | 109.1 | 307 | 290.5 | 132.3 | 249.4 | 340.7 | 175.5
775 | 581 | 467.9 | 187.16 | 218.7793 | 293.8 | 266 | 281 | 281.8 | 499.2 | 39.1 | 20.1 | 71 | 6.8 | 239.9 | 9.7 | 903.5 | 762.9 | 784.4 | 869.5 | 700 | 753.1 | 655.8 | 726.7 | 702.5 | 667.7 | 63.9 | 142.9 | 186 | 109.3 | 307.4 | 290.5 | 132.6 | 249.5 | 341.1 | 175.7
776 | 582 | 467.5 | 187 | 218.5922 | 293.5 | 265.8 | 279.8 | 280.8 | 501.9 | 39.2 | 20.1 | 71.1 | 5.9 | 248.4 | 8.4 | 903.7 | 765.7 | 798.2 | 869.9 | 702.1 | 755.6 | 662.6 | 738.5 | 703.2 | 672.1 | 64.1 | 143.2 | 186.3 | 109.5 | 307.4 | 290.7 | 132.9 | 249.8 | 341.5 | 176
777 | 583 | 467.4 | 186.96 | 218.5455 | 293.1 | 266.1 | 280.4 | 279.4 | 505.9 | 39.3 | 20.1 | 71.1 | 5.6 | 251.1 | 8.5 | 904 | 768.1 | 803.4 | 870.8 | 702.4 | 756.7 | 665.2 | 743.8 | 703.7 | 674.4 | 64.3 | 143.5 | 186.4 | 109.7 | 306.9 | 291 | 133.1 | 250 | 341.9 | 176.3
778 | 584 | 467.4 | 186.96 | 218.5455 | 292.2 | 266.3 | 281.4 | 279.4 | 509.2 | 39.3 | 20.1 | 71.2 | 5.2 | 251.6 | 9.6 | 904 | 767.1 | 805.6 | 871.7 | 701.7 | 758.3 | 662.2 | 743.9 | 704.3 | 672.4 | 64.4 | 143.8 | 186.7 | 109.9 | 306.5 | 291.1 | 133.3 | 250 | 342.4 | 176.5
779 | 585 | 466.5 | 186.6 | 218.1246 | 291.7 | 266.6 | 281.5 | 278.6 | 504.7 | 39.4 | 20.1 | 71.1 | 5.7 | 242.8 | 9.6 | 904.6 | 768.9 | 802.9 | 872.2 | 702.8 | 759.7 | 666.4 | 750.4 | 704.6 | 674.1 | 64.6 | 144.1 | 186.8 | 110.1 | 306 | 291 | 133.6 | 250.2 | 343 | 176.8
780 | 586 | 466.5 | 186.6 | 218.1246 | 292 | 266.3 | 280.6 | 276.6 | 505.9 | 39.5 | 20.1 | 71.1 | 6.2 | 255.4 | 11.8 | 904.9 | 770.4 | 810.1 | 872.7 | 704.2 | 760.6 | 667 | 754.3 | 705 | 675 | 64.8 | 144.3 | 187 | 110.3 | 306 | 290.8 | 133.8 | 250.3 | 343.5 | 177
781 | 587 | 466.8 | 186.72 | 218.2649 | 291.6 | 265.6 | 279.2 | 276 | 509.3 | 39.6 | 20.1 | 71.1 | 6.4 | 255.2 | 14.1 | 904.8 | 768.6 | 802.3 | 873 | 703.3 | 760.6 | 664.5 | 751.4 | 705.2 | 673.3 | 64.9 | 144.6 | 187.3 | 110.5 | 306.2 | 290.5 | 134 | 250.4 | 343.9 | 177.3
782 | 588 | 467.3 | 186.92 | 218.4987 | 292.3 | 265.6 | 279.9 | 276.6 | 509.3 | 39.6 | 20.1 | 71.2 | 6 | 257.5 | 14.4 | 904.8 | 766 | 795.1 | 873.1 | 701.2 | 760.3 | 663.8 | 744.7 | 705.5 | 671.5 | 65.1 | 144.9 | 187.9 | 110.8 | 306.2 | 290.3 | 134.3 | 250.6 | 344.4 | 177.6
783 | 589 | 468 | 187.2 | 218.826 | 293.2 | 264.3 | 280.3 | 276.9 | 510.5 | 39.6 | 20.1 | 71.3 | 6.3 | 254.8 | 13.5 | 905.4 | 765.5 | 797.7 | 873.5 | 701.5 | 761.3 | 664.4 | 746.8 | 706 | 671.7 | 65.3 | 145.1 | 188.1 | 111 | 306.1 | 290.2 | 134.5 | 250.7 | 344.8 | 177.9
784 | 590 | 467.6 | 187.04 | 218.639 | 292.7 | 264.1 | 280.8 | 278 | 513.2 | 39.5 | 20.1 | 71.3 | 7.3 | 255 | 13 | 905.4 | 767.7 | 802.9 | 873.2 | 705.2 | 763.6 | 670.4 | 756.3 | 706.6 | 676.1 | 65.4 | 145.4 | 188.3 | 111.2 | 305.7 | 290.1 | 134.8 | 250.9 | 345.2 | 178.1
785 | 591 | 468.2 | 187.28 | 218.9195 | 292.3 | 263.6 | 280.7 | 278.9 | 514.4 | 39.4 | 20.1 | 71.4 | 7.4 | 248.8 | 13.4 | 906.1 | 770.2 | 807 | 873.4 | 706 | 764.5 | 671.6 | 759.8 | 707 | 677 | 65.6 | 145.6 | 188.6 | 111.4 | 305.8 | 290.1 | 135 | 251 | 345.8 | 178.4
786 | 592 | 468 | 187.2 | 218.826 | 292.3 | 263.3 | 279.8 | 279.3 | 516.1 | 39.5 | 20.1 | 71.4 | 5.8 | 270.1 | 13 | 905.7 | 768.4 | 807 | 873.2 | 704.2 | 765.7 | 669.4 | 756.5 | 707.4 | 675.6 | 65.7 | 145.8 | 189 | 111.6 | 305.9 | 290 | 135.2 | 251.1 | 346.3 | 178.7
787 | 593 | 468.8 | 187.52 | 219.2001 | 292.5 | 262.5 | 279.1 | 279.7 | 512.7 | 39.6 | 20.1 | 71.3 | 4.9 | 250.3 | 13.7 | 905.3 | 767.8 | 801.5 | 873 | 704.6 | 766.7 | 670.8 | 755.8 | 707.5 | 675.2 | 65.9 | 146.1 | 189.1 | 111.8 | 306.4 | 290.1 | 135.5 | 251.2 | 346.8 | 179
788 | 594 | 477.3 | 190.92 | 223.1745 | 292.1 | 262 | 279 | 279.5 | 507.5 | 39.7 | 20.1 | 71.3 | 5.1 | 246.6 | 14.2 | 904.6 | 769.9 | 797.4 | 872.6 | 706 | 767.5 | 676.7 | 761.8 | 707.5 | 679.1 | 66.1 | 146.3 | 189.2 | 112 | 307.2 | 290.2 | 135.7 | 251.4 | 347.2 | 179.3
789 | 595 | 472.3 | 188.92 | 220.8366 | 292 | 261.8 | 279.5 | 278.8 | 504.7 | 39.7 | 20.1 | 71.3 | 5.8 | 246.4 | 13.4 | 904.6 | 771 | 795.5 | 872.5 | 705.8 | 767.2 | 678.1 | 760.1 | 707.6 | 680.5 | 66.2 | 146.6 | 189.3 | 112.3 | 307.2 | 290.4 | 135.9 | 251.6 | 347.6 | 179.6
790 | 596 | 485.7 | 194.28 | 227.1021 | 291.7 | 263.3 | 279.4 | 279.3 | 502.9 | 39.8 | 20.1 | 71.4 | 6 | 236.8 | 12 | 904 | 771.2 | 795.5 | 873.2 | 707.7 | 765.4 | 678.9 | 754.3 | 707.7 | 680.6 | 66.4 | 146.8 | 189.7 | 112.5 | 307 | 290.8 | 136.2 | 251.8 | 348 | 179.9
791 | 597 | 512 | 204.8 | 239.3994 | 291.5 | 264.3 | 279.5 | 278.6 | 492.2 | 39.9 | 20.1 | 71.5 | 6.3 | 242.7 | 9.9 | 904.4 | 772 | 796.3 | 874.4 | 710.2 | 763 | 675.7 | 751.3 | 707.7 | 681.1 | 66.6 | 147.1 | 190 | 112.7 | 306.7 | 290.9 | 136.4 | 252 | 348.4 | 180.1
792 | 598 | 526.1 | 210.44 | 245.9922 | 291.7 | 265.5 | 280.1 | 277.1 | 485.9 | 40 | 20.1 | 71.6 | 5.9 | 261.8 | 8.6 | 904.3 | 771.5 | 794.5 | 875 | 708.1 | 762.3 | 671.1 | 752 | 707.9 | 681.4 | 66.7 | 147.5 | 190.2 | 112.9 | 306.2 | 291.1 | 136.6 | 252.1 | 348.8 | 180.3
793 | 599 | 531.1 | 212.44 | 248.3301 | 292.3 | 266.9 | 280 | 275.8 | 481 | 40 | 20.1 | 71.6 | 6.3 | 263.2 | 8.6 | 904.6 | 770 | 797.2 | 875.8 | 706.2 | 760.6 | 669 | 745.5 | 707.8 | 679.4 | 66.9 | 147.8 | 190.2 | 113.1 | 305.8 | 291 | 136.9 | 252.2 | 349.1 | 180.6
794 | 600 | 532.4 | 212.96 | 248.938 | 292.9 | 268 | 280.2 | 275.3 | 480.7 | 40 | 20.1 | 71.6 | 6 | 261.1 | 9.6 | 904.9 | 770.5 | 793.5 | 876 | 706.9 | 762.1 | 673.8 | 754.2 | 708.2 | 682.2 | 67.1 | 148.1 | 190.4 | 113.3 | 305.7 | 290.9 | 137.1 | 252.3 | 349.4 | 180.8
795 | 601 | 533.3 | 213.32 | 249.3588 | 292.8 | 269 | 279.8 | 274 | 485.8 | 40 | 20.1 | 71.8 | 6.5 | 260.8 | 11.2 | 904.6 | 771.8 | 791.7 | 875.8 | 707.4 | 764.4 | 676.3 | 764.1 | 708.9 | 683.5 | 67.2 | 148.3 | 190.6 | 113.6 | 305.5 | 291 | 137.3 | 252.5 | 349.8 | 181.1
796 | 602 | 533.7 | 213.48 | 249.5458 | 292.7 | 269.4 | 279.9 | 273.1 | 503.6 | 40 | 20.1 | 72 | 6.1 | 261.5 | 12.9 | 904.3 | 774.5 | 794.5 | 875.3 | 709.8 | 766.9 | 682 | 770.6 | 710 | 687 | 67.4 | 148.5 | 191 | 113.8 | 305.5 | 291 | 137.6 | 252.7 | 350.2 | 181.4
797 | 603 | 533.1 | 213.24 | 249.2653 | 292.1 | 269.6 | 280.5 | 272.9 | 516.1 | 40 | 20.1 | 72 | 6.6 | 262.6 | 13.8 | 902.4 | 777.5 | 801.8 | 874.9 | 714.3 | 767.9 | 687.2 | 777.2 | 710.9 | 690.6 | 67.6 | 148.8 | 191.2 | 114 | 305.6 | 291.4 | 137.8 | 252.9 | 350.7 | 181.6
798 | 604 | 532.8 | 213.12 | 249.125 | 291.6 | 270.2 | 280.5 | 272.5 | 517.6 | 40 | 20.1 | 72.1 | 7.3 | 259.2 | 13.9 | 901.1 | 779.1 | 801.2 | 874.3 | 716.2 | 768.8 | 694.9 | 781.9 | 711.6 | 695.7 | 67.7 | 149.1 | 191.5 | 114.2 | 305.5 | 291.7 | 138 | 253 | 351 | 181.9
799 | 605 | 532.9 | 213.16 | 249.1718 | 290.9 | 270.8 | 280.4 | 272.6 | 522.2 | 40 | 20.1 | 72.2 | 6.6 | 254.3 | 14.7 | 901.8 | 781.1 | 799.7 | 874 | 714.6 | 770.7 | 697.9 | 788.3 | 712.5 | 698.3 | 67.9 | 149.3 | 192.1 | 114.4 | 305.5 | 292.1 | 138.3 | 253.2 | 351.5 | 182.1
800 | 606 | 533.5 | 213.4 | 249.4523 | 290.6 | 271.9 | 280.8 | 272.9 | 534.9 | 40.1 | 20.1 | 72.4 | 6.6 | 255.7 | 14.4 | 902.1 | 781.3 | 792.2 | 873.7 | 712.8 | 771.2 | 694.6 | 785.3 | 713.4 | 697.3 | 68.1 | 149.5 | 192.2 | 114.6 | 305.5 | 292.3 | 138.5 | 253.3 | 352 | 182.4
801 | 607 | 534 | 213.6 | 249.6861 | 291.7 | 272.9 | 280.9 | 272.8 | 536 | 40.2 | 20.1 | 72.4 | 6.6 | 264.2 | 13 | 902 | 780.2 | 790 | 873.4 | 712.8 | 771.3 | 690.9 | 781.1 | 714 | 695.1 | 68.2 | 149.8 | 192.5 | 114.9 | 305.4 | 292.4 | 138.8 | 253.4 | 352.5 | 182.6
802 | 608 | 535.4 | 214.16 | 250.3407 | 292.5 | 272.3 | 280.7 | 272.9 | 540.1 | 40.3 | 20.1 | 72.4 | 6.6 | 260 | 13.4 | 901.2 | 780.7 | 786.6 | 873.1 | 711.2 | 773 | 693.6 | 785.2 | 714.7 | 696.3 | 68.4 | 150.1 | 193 | 115.1 | 305.3 | 292.3 | 139 | 253.6 | 352.9 | 182.9
803 | 609 | 535.7 | 214.28 | 250.481 | 292.3 | 271 | 280.1 | 273.1 | 539.5 | 40.4 | 20.1 | 72.2 | 5.9 | 254.7 | 15.1 | 899.1 | 781.2 | 790.8 | 872.6 | 713.3 | 775 | 704.5 | 791 | 715.5 | 701.3 | 68.6 | 150.3 | 193.3 | 115.3 | 305.5 | 292.5 | 139.2 | 253.7 | 353.3 | 183.1
804 | 610 | 534.7 | 213.88 | 250.0134 | 292.5 | 270.8 | 280.1 | 273.5 | 546.8 | 40.5 | 20.1 | 72.2 | 6 | 254.7 | 14.5 | 898.3 | 783.5 | 799.2 | 872.2 | 716.5 | 777.2 | 710.4 | 794.6 | 716.7 | 705.2 | 68.7 | 150.5 | 193.6 | 115.5 | 305.7 | 292.8 | 139.5 | 253.9 | 353.8 | 183.4
805 | 611 | 536.1 | 214.44 | 250.668 | 292.7 | 269.9 | 280.2 | 274.5 | 564.1 | 40.5 | 20.1 | 72.3 | 5.3 | 266.6 | 13.7 | 898 | 786.8 | 807.2 | 871.8 | 718.9 | 778.7 | 710.9 | 796.5 | 717.8 | 707.9 | 68.9 | 150.7 | 193.9 | 115.7 | 305.7 | 293 | 139.8 | 254.1 | 354.4 | 183.7
806 | 612 | 536.2 | 214.48 | 250.7148 | 292.6 | 269.2 | 279.8 | 275 | 583.2 | 40.5 | 20.1 | 72.4 | 5.2 | 257.2 | 14.5 | 896.7 | 789 | 807.2 | 871.3 | 720.6 | 780.1 | 712 | 798.5 | 718.9 | 710.9 | 69.1 | 151 | 194.2 | 116 | 305.8 | 293.2 | 140 | 254.3 | 355 | 183.9
807 | 613 | 537.3 | 214.92 | 251.2291 | 292.3 | 268.8 | 279.3 | 275.2 | 582.4 | 40.6 | 20.1 | 72.4 | 4.8 | 243.5 | 16.4 | 896.9 | 790.6 | 804.3 | 870.9 | 722.9 | 781.4 | 713.4 | 798.2 | 719.4 | 712.3 | 69.2 | 151.2 | 194.3 | 116.2 | 305.9 | 293.8 | 140.3 | 254.5 | 355.6 | 184.2
808 | 614 | 538 | 215.2 | 251.5564 | 292 | 268.5 | 279.1 | 275.2 | 581.5 | 40.6 | 20.1 | 72.4 | 5.1 | 257.1 | 16.4 | 896.2 | 790.9 | 798.7 | 870.4 | 723.5 | 783.3 | 716.9 | 800 | 719.9 | 713.7 | 69.4 | 151.4 | 194.6 | 116.4 | 305.8 | 294.5 | 140.5 | 254.7 | 356 | 184.4
809 | 615 | 538.5 | 215.4 | 251.7902 | 291.5 | 267.6 | 278.1 | 275.3 | 568.5 | 40.7 | 20.1 | 72.4 | 5.9 | 270.1 | 13.2 | 896.6 | 791.8 | 792 | 870 | 721.7 | 782.6 | 717.3 | 795.6 | 720 | 714 | 69.6 | 151.6 | 195 | 116.6 | 305.7 | 294.9 | 140.7 | 254.9 | 356.5 | 184.7
810 | 616 | 537.9 | 215.16 | 251.5096 | 291.7 | 268 | 278.7 | 275.6 | 560.4 | 40.7 | 20.1 | 72.3 | 5.6 | 255.5 | 11.1 | 897.6 | 792.4 | 797.7 | 870 | 722.6 | 783.8 | 719.7 | 798 | 720.6 | 718.1 | 69.7 | 151.8 | 195.3 | 116.9 | 305.8 | 295.2 | 141 | 255.1 | 356.9 | 184.9
811 | 617 | 538.7 | 215.48 | 251.8837 | 292.6 | 267.8 | 280.3 | 274.7 | 561.9 | 40.7 | 20.1 | 72.5 | 5.3 | 252.1 | 11.3 | 895.8 | 792.7 | 797.8 | 869.9 | 724.2 | 784.9 | 724.1 | 801.8 | 721.2 | 721.9 | 69.9 | 152.1 | 195.5 | 117.1 | 306 | 295.5 | 141.2 | 255.3 | 357.4 | 185.2
812 | 618 | 539.1 | 215.64 | 252.0707 | 293.6 | 267.1 | 280.7 | 273.7 | 563.6 | 40.6 | 20.1 | 72.5 | 4.6 | 256.6 | 11.8 | 896.7 | 793.6 | 797.6 | 869.5 | 726.3 | 785.4 | 727.2 | 804 | 721.9 | 723.3 | 70.1 | 152.4 | 195.8 | 117.3 | 306.6 | 295.8 | 141.4 | 255.4 | 357.9 | 185.5
813 | 619 | 540.7 | 216.28 | 252.8189 | 293.9 | 267.2 | 280.8 | 272.9 | 561.3 | 40.6 | 20.1 | 72.6 | 4.2 | 259.1 | 11.6 | 895.9 | 793.2 | 803.9 | 869.2 | 726.6 | 786.3 | 725.5 | 804.2 | 722.2 | 724.5 | 70.2 | 152.6 | 195.9 | 117.5 | 307.3 | 296 | 141.6 | 255.6 | 358.4 | 185.7
814 | 620 | 540.2 | 216.08 | 252.5851 | 293.7 | 268.3 | 281.7 | 272.3 | 561.7 | 40.7 | 20.1 | 72.8 | 4.6 | 248.6 | 12.2 | 895.9 | 793.7 | 803.3 | 869.4 | 727.7 | 787.7 | 728.5 | 805.4 | 722.8 | 726.5 | 70.4 | 152.9 | 196.2 | 117.8 | 308.5 | 296.6 | 141.9 | 255.9 | 358.7 | 186
815 | 621 | 541.6 | 216.64 | 253.2397 | 293.7 | 269.9 | 282.8 | 273.5 | 558.6 | 40.8 | 20.1 | 73 | 5.5 | 256.3 | 11.6 | 894.4 | 794.4 | 809.8 | 869.2 | 729.3 | 788.3 | 730.7 | 806.5 | 723.4 | 728.3 | 70.6 | 153.2 | 196.6 | 118 | 308.9 | 296.8 | 142.2 | 256.1 | 359.1 | 186.3
816 | 622 | 542.2 | 216.88 | 253.5202 | 293.5 | 271.2 | 283.6 | 274.1 | 565 | 40.9 | 20.1 | 73.2 | 5.7 | 245.2 | 11.6 | 893.9 | 794.7 | 817.5 | 869.1 | 732.2 | 789.5 | 730.4 | 806.6 | 724.2 | 729.6 | 70.7 | 153.5 | 196.8 | 118.2 | 309 | 297 | 142.4 | 256.3 | 359.6 | 186.6
817 | 623 | 543 | 217.2 | 253.8943 | 294.2 | 272.5 | 283.9 | 274 | 561.6 | 40.9 | 20.1 | 73.3 | 5.4 | 257 | 10.9 | 895.2 | 795 | 818.2 | 868.9 | 733.7 | 789.4 | 732.4 | 807.8 | 724.5 | 732.4 | 70.9 | 153.7 | 196.9 | 118.5 | 309.1 | 297.1 | 142.7 | 256.4 | 360 | 186.9
818 | 624 | 543.7 | 217.48 | 254.2216 | 295.5 | 274.2 | 285.4 | 273.3 | 566 | 40.9 | 20.1 | 73.4 | 4.9 | 262.4 | 9.6 | 895 | 796.1 | 819.1 | 868.7 | 732.7 | 790.5 | 732.8 | 807.6 | 725.4 | 732.5 | 71.1 | 153.9 | 197.4 | 118.7 | 309.2 | 297.1 | 142.9 | 256.6 | 360.5 | 187.1
819 | 625 | 543.6 | 217.44 | 254.1748 | 296.2 | 275.9 | 286.2 | 272.8 | 582.8 | 40.9 | 20 | 73.4 | 4.3 | 252.9 | 10.8 | 895 | 795.9 | 817.6 | 868.6 | 732.8 | 792.9 | 737.2 | 809.8 | 726.3 | 734.5 | 71.3 | 154.2 | 197.6 | 118.9 | 309.4 | 297.5 | 143.1 | 256.7 | 361.1 | 187.4
820 | 626 | 544.3 | 217.72 | 254.5021 | 296.4 | 275.7 | 287.4 | 272.3 | 575.2 | 41 | 20 | 73.5 | 5.5 | 256.9 | 11 | 896.8 | 795.8 | 809.4 | 868.8 | 729.5 | 793.6 | 737.5 | 808.5 | 726.7 | 733.7 | 71.4 | 154.4 | 197.9 | 119.2 | 309.7 | 298 | 143.3 | 257 | 361.6 | 187.7
821 | 627 | 545 | 218 | 254.8294 | 297.1 | 275.7 | 289.6 | 273.3 | 568.8 | 41 | 20 | 73.5 | 6.2 | 246.2 | 10.6 | 896.4 | 795.1 | 803.8 | 869 | 731.1 | 792.9 | 736.4 | 803.8 | 727.1 | 732.1 | 71.6 | 154.7 | 198.2 | 119.4 | 310.2 | 298.4 | 143.6 | 257.1 | 362.1 | 187.9
822 | 628 | 545.5 | 218.2 | 255.0632 | 297.5 | 275.9 | 290.3 | 274.9 | 557.8 | 41 | 20 | 73.5 | 5.6 | 253.2 | 11.5 | 893.7 | 793.6 | 810.9 | 868.8 | 734.9 | 793.1 | 734.8 | 803.6 | 727.5 | 736.4 | 71.8 | 154.9 | 198.3 | 119.6 | 310.3 | 298.7 | 143.8 | 257.3 | 362.5 | 188.2
823 | 629 | 544.5 | 217.8 | 254.5957 | 297.6 | 274.4 | 290 | 276.4 | 565.5 | 40.9 | 20 | 73.5 | 4.7 | 248.4 | 11.5 | 891.6 | 793.3 | 812.5 | 868.3 | 736 | 794.2 | 736.9 | 806.5 | 728.4 | 738.8 | 71.9 | 155.2 | 198.7 | 119.9 | 310.6 | 299 | 144.1 | 257.5 | 363 | 188.5
824 | 630 | 545.3 | 218.12 | 254.9697 | 298 | 274.1 | 290 | 277.2 | 583 | 40.9 | 20 | 73.6 | 5.2 | 253.2 | 13.3 | 891.1 | 793.5 | 814.1 | 868.2 | 737 | 795.8 | 734.9 | 808.8 | 729.7 | 739.2 | 72.1 | 155.5 | 199.3 | 120.1 | 311.1 | 299.2 | 144.3 | 257.7 | 363.5 | 188.7
825 | 631 | 544.5 | 217.8 | 254.5957 | 298.1 | 276.1 | 290.1 | 278.1 | 600.1 | 40.8 | 20 | 73.6 | 4.3 | 255.4 | 13.9 | 891.6 | 794.6 | 817.4 | 868.4 | 737.8 | 796.6 | 732.2 | 808.9 | 730.7 | 739.3 | 72.3 | 155.7 | 199.6 | 120.3 | 310.8 | 299.1 | 144.6 | 257.9 | 364.2 | 189
826 | 632 | 544.5 | 217.8 | 254.5957 | 297.7 | 276.1 | 290 | 279.8 | 609.1 | 40.9 | 20 | 73.5 | 5 | 245.4 | 13.5 | 890.9 | 796.3 | 823.9 | 868.6 | 741.3 | 797.9 | 731.5 | 810.6 | 731.4 | 741.2 | 72.4 | 156 | 199.8 | 120.6 | 310.9 | 298.7 | 144.8 | 258 | 364.7 | 189.3
827 | 633 | 545.2 | 218.08 | 254.923 | 297.3 | 275.5 | 290.3 | 280.5 | 608.4 | 40.9 | 20 | 73.5 | 4.7 | 241.3 | 13.1 | 891.7 | 796.2 | 818.8 | 868.3 | 740 | 798.6 | 732.3 | 809.6 | 731.8 | 741.9 | 72.6 | 156.2 | 200 | 120.8 | 311.3 | 298.9 | 145 | 258.2 | 365.3 | 189.6
828 | 634 | 544.7 | 217.88 | 254.6892 | 297.8 | 275.3 | 291 | 281.5 | 594.9 | 41.1 | 20 | 73.5 | 5 | 244.2 | 12.2 | 893.4 | 795.9 | 808.3 | 867.9 | 737.5 | 797.1 | 729.3 | 801.4 | 731.5 | 738.3 | 72.8 | 156.4 | 200.5 | 121.1 | 311.6 | 299.2 | 145.2 | 258.3 | 365.9 | 189.8
829 | 635 | 545 | 218 | 254.8294 | 298.8 | 275.7 | 292 | 281.9 | 574.9 | 41.1 | 20 | 73.6 | 4.9 | 243.2 | 11.3 | 894.5 | 794.7 | 802.1 | 867.4 | 737 | 796.3 | 731.8 | 800.6 | 731.4 | 740.5 | 73 | 156.7 | 200.7 | 121.3 | 311.6 | 299.5 | 145.5 | 258.6 | 366.2 | 190.1
830 | 636 | 546.8 | 218.72 | 255.6711 | 299.5 | 276.3 | 292.4 | 281.6 | 562.6 | 41.1 | 20 | 73.7 | 5.6 | 239.3 | 10.5 | 895.3 | 794.1 | 793.3 | 867.7 | 734.9 | 795.5 | 729.5 | 794.9 | 731.2 | 738.6 | 73.1 | 157 | 200.9 | 121.5 | 311.9 | 300 | 145.8 | 258.9 | 366.5 | 190.4
831 | 637 | 546.8 | 218.72 | 255.6711 | 300.4 | 276.5 | 293.2 | 281.1 | 549.2 | 41 | 20 | 73.9 | 5.4 | 239.7 | 9.4 | 895.4 | 790.9 | 786.3 | 867.7 | 731.6 | 795.8 | 727.1 | 789.4 | 731.4 | 736.9 | 73.3 | 157.3 | 201.1 | 121.8 | 311.9 | 300.4 | 146 | 259.1 | 366.9 | 190.7
832 | 638 | 547 | 218.8 | 255.7646 | 300.6 | 276.7 | 293.4 | 280.6 | 541.6 | 41 | 20 | 73.9 | 5 | 249.4 | 7.9 | 895 | 785 | 777.4 | 867.3 | 728.8 | 794.5 | 719.8 | 776.5 | 731.5 | 731.8 | 73.5 | 157.6 | 201.3 | 122 | 311.8 | 300.6 | 146.2 | 259.2 | 367.2 | 191
833 | 639 | 548.4 | 219.36 | 256.4192 | 301.3 | 277 | 293 | 280 | 534.2 | 41 | 20 | 73.9 | 5.1 | 253 | 8.8 | 894.6 | 781.8 | 769.8 | 866.8 | 726.8 | 794.6 | 718.1 | 771.2 | 731.7 | 729.4 | 73.6 | 157.8 | 201.7 | 122.3 | 312 | 300.9 | 146.5 | 259.4 | 367.4 | 191.2
834 | 640 | 548.8 | 219.52 | 256.6062 | 301.9 | 276.3 | 294 | 280.4 | 535.9 | 41 | 20 | 73.8 | 5.2 | 254.2 | 12 | 894.1 | 776.3 | 761.1 | 866.2 | 722.3 | 792.8 | 710.1 | 755.1 | 731.7 | 724.7 | 73.8 | 158 | 202.1 | 122.5 | 311.9 | 301.1 | 146.7 | 259.5 | 367.8 | 191.5
835 | 641 | 548.7 | 219.48 | 256.5595 | 303.3 | 276.4 | 294.1 | 281 | 528.7 | 41 | 20 | 73.8 | 5.4 | 246.6 | 12 | 893.4 | 771.5 | 755.9 | 865.8 | 719.9 | 788.9 | 700.5 | 742.5 | 731.5 | 720.5 | 74 | 158.2 | 202.3 | 122.8 | 312.3 | 301.1 | 146.9 | 259.7 | 368.1 | 191.7
836 | 642 | 549.2 | 219.68 | 256.7933 | 305.1 | 276.5 | 294.1 | 279.8 | 529.6 | 41 | 20 | 73.8 | 5.1 | 245.5 | 12.2 | 893.4 | 768.7 | 760 | 866.3 | 716.9 | 787.8 | 693 | 739.2 | 731.8 | 718.2 | 74.2 | 158.5 | 202.7 | 123 | 312.1 | 301 | 147.2 | 259.8 | 368.4 | 192
837 | 643 | 548.5 | 219.4 | 256.466 | 306.9 | 275.9 | 294.6 | 278.8 | 535.4 | 41.1 | 20 | 73.8 | 5.4 | 244.6 | 12.3 | 893.7 | 766.2 | 766.3 | 866.7 | 713.4 | 786.9 | 684.5 | 731.9 | 732.5 | 714.4 | 74.3 | 158.7 | 203.4 | 123.3 | 312.1 | 300.8 | 147.4 | 259.9 | 368.8 | 192.3
838 | 644 | 549.4 | 219.76 | 256.8868 | 307.5 | 275.7 | 295.3 | 279.1 | 542.2 | 41.2 | 20 | 73.9 | 5.4 | 244.6 | 12 | 894 | 765.4 | 778.4 | 867 | 714.2 | 786.2 | 676.9 | 727.9 | 733.1 | 711.3 | 74.5 | 159 | 203.9 | 123.5 | 312.3 | 300.9 | 147.6 | 260 | 369.1 | 192.5
839 | 645 | 549.6 | 219.84 | 256.9803 | 307.8 | 276.7 | 296.6 | 281.2 | 556.2 | 41.3 | 20 | 74.1 | 5.7 | 243.9 | 11.1 | 893.7 | 765.8 | 790.2 | 867.2 | 713.9 | 786.4 | 670.7 | 730.4 | 733.9 | 710.7 | 74.7 | 159.3 | 204.4 | 123.8 | 312.7 | 300.9 | 147.8 | 260.1 | 369.5 | 192.8
840 | 646 | 548.9 | 219.56 | 256.653 | 307.1 | 278.8 | 297.4 | 283.4 | 575.9 | 41.3 | 20 | 74.3 | 6.1 | 241 | 9.6 | 893.1 | 768.3 | 796.3 | 867 | 714.6 | 788.2 | 671.9 | 740.2 | 734.9 | 712 | 74.8 | 159.6 | 204.8 | 124 | 313.1 | 301.1 | 148.1 | 260.3 | 370 | 193.1
841 | 647 | 548.5 | 219.4 | 256.466 | 306.2 | 280.4 | 298.1 | 284.7 | 589 | 41.3 | 20 | 74.5 | 5.3 | 229.6 | 8.2 | 892.4 | 771.9 | 798.8 | 866.7 | 715.7 | 790.5 | 675.5 | 752 | 735.5 | 713 | 75 | 159.9 | 205.1 | 124.3 | 314.3 | 301.4 | 148.3 | 260.5 | 370.5 | 193.4
842 | 648 | 549.6 | 219.84 | 256.9803 | 305.6 | 281.1 | 298.2 | 286.6 | 603.8 | 41.3 | 20 | 74.6 | 5.8 | 240.5 | 7.5 | 891.7 | 775.5 | 802.9 | 866.1 | 718.1 | 792.5 | 684.8 | 761.7 | 736.1 | 716.6 | 75.2 | 160.2 | 205.2 | 124.6 | 316 | 301.6 | 148.6 | 260.7 | 371 | 193.7
843 | 649 | 550.8 | 220.32 | 257.5414 | 305.5 | 281.7 | 298 | 288.1 | 610.1 | 41.3 | 20 | 74.6 | 5.9 | 241.4 | 7.4 | 890.5 | 777.8 | 800.4 | 865.4 | 718 | 794.2 | 693.1 | 769.2 | 736.6 | 719.3 | 75.4 | 160.5 | 205.4 | 124.8 | 316.6 | 301.9 | 148.8 | 260.9 | 371.7 | 194
844 | 650 | 551.1 | 220.44 | 257.6817 | 305.5 | 282.4 | 296.6 | 288.9 | 607.5 | 41.3 | 20 | 74.8 | 6.4 | 247.6 | 7.6 | 891.2 | 778.1 | 798.5 | 865.1 | 715.9 | 794.5 | 697.7 | 771.5 | 736.8 | 718.7 | 75.5 | 160.8 | 205.7 | 125.1 | 316.9 | 302.2 | 149.1 | 261.2 | 372.2 | 194.3
845 | 651 | 549.9 | 219.96 | 257.1206 | 306.8 | 282.8 | 294.2 | 290.2 | 597.1 | 41.3 | 20 | 75 | 7.2 | 243.1 | 8.1 | 889.1 | 780.2 | 803 | 864.5 | 718.7 | 796.1 | 706.4 | 781 | 737.1 | 722.5 | 75.7 | 161.1 | 206.1 | 125.3 | 317.5 | 302.8 | 149.4 | 261.4 | 372.5 | 194.6
846 | 652 | 550.9 | 220.36 | 257.5881 | 307.4 | 282.9 | 293.2 | 291.9 | 600.1 | 41.3 | 20 | 75.1 | 7.8 | 242.9 | 8.6 | 887.9 | 782.6 | 800.8 | 863.9 | 720.4 | 797.3 | 714.2 | 786.8 | 737.3 | 726.7 | 75.9 | 161.3 | 206.5 | 125.6 | 317.8 | 303.5 | 149.6 | 261.7 | 373.1 | 194.8
847 | 653 | 550.1 | 220.04 | 257.2141 | 307.8 | 282.4 | 293.4 | 292.4 | 597.5 | 41.4 | 20 | 75.1 | 7.5 | 237 | 8.4 | 887 | 784.1 | 798.7 | 863.4 | 720.3 | 797.2 | 719.8 | 790.5 | 737.3 | 729 | 76 | 161.6 | 206.7 | 125.9 | 318.1 | 304.2 | 149.9 | 262 | 373.7 | 195.1
848 | 654 | 549.2 | 219.68 | 256.7933 | 307.9 | 281.2 | 294.5 | 292.1 | 588.8 | 41.4 | 20 | 75 | 7.2 | 248.4 | 7.8 | 887 | 785.9 | 800.5 | 863.2 | 721.6 | 796.8 | 720 | 795 | 737.4 | 729.9 | 76.2 | 161.8 | 206.8 | 126.1 | 318.3 | 305.2 | 150.1 | 262.4 | 374.2 | 195.4
849 | 655 | 549.7 | 219.88 | 257.0271 | 307.8 | 280.1 | 295 | 292.2 | 581.2 | 41.4 | 20 | 74.9 | 6.7 | 241.4 | 8.5 | 887.2 | 787.9 | 804.8 | 863.1 | 722 | 797.9 | 726.6 | 798.1 | 737.6 | 733.5 | 76.4 | 162.1 | 207.1 | 126.4 | 318.3 | 305.9 | 150.3 | 262.7 | 374.7 | 195.7
850 | 656 | 549.6 | 219.84 | 256.9803 | 308.1 | 279.6 | 294.8 | 292.6 | 592.6 | 41.4 | 20 | 74.8 | 5.5 | 237.5 | 7.8 | 887 | 789 | 809.3 | 863.1 | 723.5 | 798.9 | 733.4 | 803 | 738.2 | 737 | 76.6 | 162.4 | 207.4 | 126.7 | 318.4 | 306.5 | 150.6 | 262.9 | 375.2 | 196
851 | 657 | 550.2 | 220.08 | 257.2608 | 308.7 | 280.7 | 295.6 | 292.4 | 595.6 | 41.6 | 20 | 74.8 | 5.1 | 250.3 | 9.1 | 886.7 | 790.3 | 811.3 | 863.1 | 724.7 | 798.7 | 737.3 | 807.8 | 738.5 | 739.9 | 76.7 | 162.7 | 207.7 | 126.9 | 318.8 | 306.8 | 150.9 | 263.2 | 375.8 | 196.2
852 | 658 | 551.1 | 220.44 | 257.6817 | 309.6 | 282.4 | 296.1 | 291.3 | 591.7 | 41.7 | 20 | 74.9 | 5.5 | 237.7 | 12.3 | 887.9 | 791.3 | 804.1 | 862.8 | 724.4 | 798.8 | 733.6 | 804.8 | 738.9 | 738.2 | 76.9 | 162.9 | 208 | 127.2 | 319.1 | 307.1 | 151.1 | 263.3 | 376.4 | 196.5
853 | 659 | 551.5 | 220.6 | 257.8687 | 310.4 | 282.8 | 296.1 | 291.2 | 585.2 | 41.7 | 20 | 74.9 | 6.1 | 235 | 12.1 | 886.8 | 790.1 | 797.3 | 862.3 | 723.3 | 799.1 | 730.4 | 798.7 | 738.7 | 736.2 | 77.1 | 163.2 | 208.1 | 127.5 | 319 | 307.2 | 151.3 | 263.5 | 376.9 | 196.8
854 | 660 | 550.6 | 220.24 | 257.4479 | 310.6 | 282.5 | 296.9 | 290.1 | 572.3 | 41.8 | 20 | 75 | 6.3 | 236.3 | 11.7 | 888.1 | 788.4 | 783.9 | 861.9 | 720.7 | 798.7 | 727.7 | 791.3 | 738.3 | 734.7 | 77.3 | 163.5 | 208.3 | 127.7 | 319.2 | 307.5 | 151.6 | 263.7 | 377.2 | 197.1
855 | 661 | 552.2 | 220.88 | 258.196 | 310.6 | 282.6 | 297.3 | 288.4 | 558.1 | 41.8 | 20 | 75.1 | 6.1 | 234.1 | 12.2 | 888.1 | 786.3 | 771.3 | 861.8 | 718.7 | 797.4 | 728.5 | 788.8 | 738.1 | 735.7 | 77.4 | 163.7 | 208.8 | 128 | 319 | 308.1 | 151.9 | 264.1 | 377.5 | 197.3
856 | 662 | 552.8 | 221.12 | 258.4765 | 310.3 | 283 | 297.4 | 287.5 | 544.7 | 41.7 | 20 | 75.2 | 6.3 | 243 | 11.5 | 887.2 | 784.7 | 764.8 | 861.5 | 719.3 | 795.2 | 725 | 786.1 | 737.9 | 734.3 | 77.6 | 164.1 | 209.4 | 128.3 | 319.2 | 308.4 | 152.1 | 264.3 | 377.9 | 197.6
857 | 663 | 553 | 221.2 | 258.5701 | 312.2 | 282.6 | 298.4 | 287.3 | 540.2 | 41.6 | 20 | 75.4 | 6.1 | 233 | 11 | 886.7 | 783.5 | 766.3 | 861.4 | 717 | 795.1 | 722 | 781.1 | 738.1 | 733.6 | 77.8 | 164.4 | 209.5 | 128.5 | 319.7 | 308.6 | 152.3 | 264.5 | 378.2 | 197.9
858 | 664 | 552.6 | 221.04 | 258.383 | 313.9 | 283 | 299.1 | 286.9 | 537.9 | 41.6 | 20 | 75.4 | 5.9 | 242.7 | 10.3 | 886.6 | 781.6 | 780.5 | 861.7 | 719 | 795.5 | 713.3 | 772.6 | 738.3 | 730 | 78 | 164.7 | 209.8 | 128.8 | 319.6 | 308.7 | 152.6 | 264.7 | 378.6 | 198.2
859 | 665 | 551.6 | 220.64 | 257.9154 | 314.5 | 283.8 | 299.8 | 286.7 | 541.6 | 41.5 | 20 | 75.5 | 5.5 | 232.4 | 9.9 | 886.5 | 780.7 | 786.3 | 861.8 | 718.8 | 795.8 | 709 | 773.2 | 738.4 | 729 | 78.1 | 164.9 | 209.8 | 129.1 | 319.5 | 308.7 | 152.8 | 264.8 | 378.9 | 198.5
860 | 666 | 551.9 | 220.76 | 258.0557 | 314.8 | 283 | 300.9 | 286.2 | 540.5 | 41.5 | 20 | 75.4 | 5.2 | 248.9 | 8.8 | 886 | 781.6 | 794.6 | 862 | 720.6 | 796 | 710.2 | 777.8 | 738.3 | 730.2 | 78.3 | 165.2 | 210.1 | 129.3 | 319.7 | 308.8 | 153 | 265 | 379.3 | 198.8
861 | 667 | 552.2 | 220.88 | 258.196 | 314.9 | 282.6 | 299.9 | 285.6 | 556.1 | 41.6 | 20 | 75.4 | 5.3 | 248.7 | 9.2 | 886.3 | 784.3 | 806.8 | 862.1 | 724.9 | 796.5 | 705.8 | 780.5 | 739.2 | 732.4 | 78.5 | 165.5 | 210.4 | 129.6 | 320 | 308.8 | 153.3 | 265.1 | 379.8 | 199
862 | 668 | 552.2 | 220.88 | 258.196 | 314.5 | 282.2 | 298.3 | 285.3 | 571.6 | 41.7 | 20 | 75.5 | 5.9 | 245.2 | 9.3 | 885.6 | 784.6 | 802.2 | 861.9 | 725.4 | 795.8 | 703.7 | 778.5 | 739.5 | 731.1 | 78.7 | 165.8 | 210.8 | 129.9 | 319.7 | 308.6 | 153.5 | 265.3 | 380.3 | 199.3
863 | 669 | 552.2 | 220.88 | 258.196 | 313.9 | 282 | 297.6 | 286 | 572.5 | 41.7 | 20 | 75.5 | 6.3 | 238.1 | 8.7 | 884.6 | 783.1 | 797.6 | 861.7 | 724.9 | 796.6 | 701.5 | 780 | 739.7 | 729.6 | 78.9 | 166.2 | 211.1 | 130.1 | 319.6 | 308.3 | 153.8 | 265.4 | 380.8 | 199.6
864 | 670 | 552.6 | 221.04 | 258.383 | 313.8 | 282.5 | 297.4 | 286.4 | 581.3 | 41.8 | 20 | 75.5 | 5.8 | 254 | 10 | 884.1 | 783.4 | 799.5 | 861.8 | 726.1 | 799 | 700.5 | 784.5 | 740.2 | 729.6 | 79 | 166.5 | 211.7 | 130.4 | 319.9 | 308.3 | 154 | 265.5 | 381.2 | 199.9
865 | 671 | 552.9 | 221.16 | 258.5233 | 313.7 | 282.7 | 298.3 | 287 | 577.7 | 41.8 | 20 | 75.5 | 5.4 | 256.7 | 11.2 | 883.6 | 785.4 | 800.1 | 861.7 | 727.3 | 799.3 | 705.9 | 788.6 | 740.1 | 732.7 | 79.2 | 166.8 | 211.8 | 130.7 | 319.6 | 308.1 | 154.3 | 265.7 | 381.6 | 200.2
866 | 672 | 553 | 221.2 | 258.5701 | 313.4 | 283.8 | 299 | 287.8 | 571 | 41.8 | 19.9 | 75.6 | 5.5 | 258.8 | 12.8 | 883.9 | 788 | 804.1 | 861.6 | 728.9 | 800.6 | 711.7 | 795.2 | 740.2 | 736.1 | 79.4 | 167.1 | 211.9 | 130.9 | 319.7 | 308.1 | 154.6 | 265.8 | 382 | 200.5
867 | 673 | 552.5 | 221 | 258.3363 | 313.6 | 285 | 297.9 | 288.5 | 573.5 | 41.9 | 19.9 | 75.6 | 5.5 | 262.1 | 13.5 | 884.3 | 789.8 | 802 | 861.6 | 728.1 | 801.7 | 714.2 | 799.3 | 740.6 | 735.6 | 79.6 | 167.3 | 212.2 | 131.2 | 320.3 | 308.1 | 154.9 | 266 | 382.5 | 200.7
868 | 674 | 553.5 | 221.4 | 258.8038 | 314 | 284.9 | 296.3 | 288.2 | 576.5 | 42 | 19.9 | 75.6 | 6 | 279 | 12.2 | 883.9 | 791.9 | 800.5 | 861.7 | 728.6 | 801.4 | 714.3 | 799.9 | 740.5 | 737.3 | 79.7 | 167.6 | 212.4 | 131.5 | 320.6 | 308.6 | 155.1 | 266.3 | 382.9 | 201
869 | 675 | 553.3 | 221.32 | 258.7103 | 314.1 | 284.5 | 295 | 288.4 | 568.6 | 42 | 19.9 | 75.7 | 6.1 | 273.4 | 11.9 | 883.4 | 792.2 | 802.8 | 861.6 | 728.8 | 800.7 | 714.4 | 799 | 740.4 | 737.9 | 79.9 | 167.7 | 212.7 | 131.8 | 320.5 | 308.6 | 155.4 | 266.5 | 383.3 | 201.3
870 | 676 | 552.6 | 221.04 | 258.383 | 314.4 | 284.1 | 293.7 | 289 | 584.6 | 42 | 19.9 | 75.8 | 6.5 | 271.1 | 12.5 | 882.8 | 793 | 798.5 | 861.3 | 728.3 | 802.2 | 719.8 | 801.2 | 740.7 | 740.3 | 80.1 | 168 | 213.2 | 132 | 320.7 | 308.7 | 155.6 | 266.7 | 383.8 | 201.5
871 | 677 | 552.7 | 221.08 | 258.4298 | 315 | 283.4 | 294.1 | 288.3 | 592.3 | 42 | 19.9 | 75.9 | 6 | 263.8 | 13.3 | 883.3 | 791 | 789.2 | 861.2 | 724.6 | 800.5 | 717.2 | 793.5 | 740.8 | 736.7 | 80.3 | 168.2 | 213.4 | 132.3 | 321.3 | 308.8 | 155.9 | 266.7 | 384.2 | 201.8
872 | 678 | 552.9 | 221.16 | 258.5233 | 315.7 | 283 | 294.7 | 286.7 | 602.2 | 42 | 19.9 | 76 | 5.6 | 260.6 | 12.4 | 883.2 | 786.9 | 778.6 | 861.3 | 721.5 | 799 | 713.3 | 779.7 | 741 | 732.5 | 80.4 | 168.4 | 214 | 132.6 | 322 | 309.2 | 156.1 | 266.9 | 384.5 | 202.1
873 | 679 | 553.1 | 221.24 | 258.6168 | 316 | 283.3 | 294.9 | 286.6 | 599.5 | 42 | 19.9 | 76.1 | 5.8 | 262.9 | 12.5 | 882.7 | 784.8 | 776.6 | 861.4 | 720.5 | 799.8 | 709 | 776.9 | 741.4 | 730.5 | 80.6 | 168.7 | 214.2 | 132.8 | 322.5 | 309.5 | 156.4 | 267.1 | 384.9 | 202.4
874 | 680 | 552.8 | 221.12 | 258.4765 | 316.7 | 283.7 | 294.8 | 287 | 612.6 | 42 | 19.9 | 76.2 | 5.9 | 260.8 | 14.4 | 882 | 784.4 | 777 | 861.3 | 719.1 | 802.4 | 713.9 | 783.9 | 742.3 | 731.5 | 80.8 | 168.9 | 214.5 | 133.1 | 323.1 | 309.6 | 156.7 | 267.3 | 385.2 | 202.7
875 | 681 | 553.3 | 221.32 | 258.7103 | 317.2 | 284.2 | 296.4 | 289.1 | 617.6 | 42 | 19.9 | 76.3 | 6.1 | 284.2 | 14.9 | 881.8 | 783 | 786.9 | 862 | 718.3 | 803.4 | 708.9 | 778.6 | 742.7 | 728.2 | 81 | 169.3 | 214.9 | 133.4 | 323 | 309.6 | 156.9 | 267.5 | 385.6 | 203
876 | 682 | 554.4 | 221.76 | 259.2247 | 317.6 | 284.4 | 297.6 | 290.6 | 616.8 | 41.9 | 19.9 | 76.4 | 6.3 | 289.6 | 14 | 881.6 | 784.1 | 795.9 | 862.3 | 719.1 | 805.8 | 707.8 | 783.2 | 743.4 | 729.2 | 81.2 | 169.6 | 215.2 | 133.7 | 323.1 | 309.7 | 157.2 | 267.6 | 385.9 | 203.3
877 | 683 | 553.9 | 221.56 | 258.9909 | 317.5 | 285.1 | 297.9 | 291.8 | 623.7 | 41.8 | 19.9 | 76.4 | 6.4 | 267.5 | 11.7 | 881.5 | 785.2 | 798.2 | 862.4 | 718.8 | 807.6 | 711.1 | 787.5 | 744 | 729.7 | 81.3 | 169.8 | 215.5 | 133.9 | 323 | 309.9 | 157.5 | 267.7 | 386.3 | 203.5
878 | 684 | 553 | 221.2 | 258.5701 | 317.5 | 286.1 | 298.7 | 293.1 | 628 | 41.9 | 19.9 | 76.4 | 6.4 | 289.7 | 12.3 | 881.4 | 786.8 | 800.9 | 862.6 | 719.3 | 808.5 | 715.8 | 794.1 | 744.4 | 731.9 | 81.5 | 170.1 | 215.8 | 134.2 | 323 | 310.1 | 157.8 | 268 | 386.8 | 203.8
879 | 685 | 552.8 | 221.12 | 258.4765 | 317.8 | 287.2 | 299.3 | 293 | 638.2 | 41.9 | 19.9 | 76.5 | 6.8 | 250.3 | 10.7 | 881 | 785.8 | 796.4 | 862.4 | 717.8 | 808.5 | 715.8 | 792.6 | 744.7 | 730.3 | 81.7 | 170.3 | 216.3 | 134.5 | 323.5 | 310.4 | 158 | 268.2 | 387.2 | 204.1
880 | 686 | 553.3 | 221.32 | 258.7103 | 318.7 | 287.6 | 299.8 | 292.1 | 630.4 | 42 | 19.9 | 76.5 | 7.3 | 231.5 | 9.4 | 880.4 | 783.2 | 785.4 | 862.3 | 714.1 | 806.6 | 709.1 | 783.5 | 744.6 | 726 | 81.9 | 170.6 | 216.7 | 134.8 | 323.5 | 310.5 | 158.3 | 268.4 | 387.6 | 204.4
881 | 687 | 553.8 | 221.52 | 258.9441 | 319.4 | 287.2 | 300.4 | 291.9 | 609.7 | 42.1 | 19.9 | 76.6 | 7.7 | 261.9 | 8.1 | 880.5 | 784.4 | 785 | 862.4 | 713.9 | 804.9 | 712.5 | 787.4 | 744.1 | 728.7 | 82.1 | 170.9 | 216.7 | 135.1 | 323.5 | 310.5 | 158.6 | 268.6 | 387.9 | 204.6
882 | 688 | 555.7 | 222.28 | 259.8325 | 319.7 | 286.7 | 300.8 | 292.3 | 599.7 | 42.1 | 19.9 | 76.6 | 7.1 | 250.2 | 9.6 | 879.7 | 786.2 | 794.3 | 862.7 | 716 | 807.3 | 720.9 | 794.1 | 744.4 | 732.5 | 82.2 | 171.2 | 217 | 135.3 | 323.4 | 310.6 | 158.9 | 268.7 | 388.2 | 204.9
883 | 689 | 555.7 | 222.28 | 259.8325 | 320 | 286.6 | 301.4 | 292 | 600.5 | 42.2 | 19.9 | 76.5 | 6.2 | 244.8 | 13 | 877.9 | 787.3 | 797.5 | 862.2 | 718 | 808.9 | 721.6 | 796.9 | 745 | 735.2 | 82.4 | 171.4 | 217.2 | 135.6 | 323.4 | 310.8 | 159.1 | 268.8 | 388.7 | 205.1
884 | 690 | 555.7 | 222.28 | 259.8325 | 319.4 | 286.7 | 302.1 | 291.9 | 601.9 | 42.3 | 19.9 | 76.5 | 6.1 | 249.1 | 15.1 | 878 | 786.2 | 783.6 | 861.5 | 715.4 | 805.9 | 718.9 | 792.1 | 744.9 | 732.2 | 82.6 | 171.8 | 217.6 | 135.9 | 323.6 | 311 | 159.4 | 269.1 | 389.2 | 205.4
885 | 691 | 555.2 | 222.08 | 259.5987 | 319.3 | 286.9 | 301.9 | 291 | 581.2 | 42.3 | 19.9 | 76.4 | 6.3 | 259.5 | 13.5 | 878.4 | 782 | 768.5 | 861.2 | 712.9 | 799.7 | 714.5 | 779.6 | 744 | 728.4 | 82.8 | 172.1 | 217.8 | 136.2 | 323.6 | 311.3 | 159.7 | 269.3 | 389.6 | 205.7
886 | 692 | 555.3 | 222.12 | 259.6455 | 320 | 285.9 | 302.2 | 290.7 | 561.2 | 42.2 | 19.9 | 76.4 | 7 | 266.8 | 12.7 | 877.8 | 782.6 | 761.3 | 861.7 | 715.2 | 794.8 | 716.1 | 774.4 | 743.4 | 729.9 | 83 | 172.4 | 218 | 136.5 | 324.8 | 311.7 | 159.9 | 269.6 | 389.8 | 205.9
887 | 693 | 555.6 | 222.24 | 259.7858 | 320.8 | 285.7 | 302.8 | 290.5 | 546.2 | 42.3 | 19.9 | 76.3 | 5.6 | 255.5 | 13.3 | 877.8 | 783.1 | 756.3 | 862.1 | 714 | 792.4 | 714.8 | 774.9 | 743 | 729.6 | 83.2 | 172.7 | 218.1 | 136.7 | 324.5 | 312 | 160.2 | 269.8 | 390.1 | 206.2
888 | 694 | 555.5 | 222.2 | 259.739 | 320.6 | 285.9 | 303.5 | 290.8 | 535.2 | 42.3 | 19.9 | 76.2 | 6.1 | 256.8 | 13.7 | 877.7 | 782.8 | 751.4 | 862.4 | 711.1 | 790.8 | 714 | 774.9 | 742.6 | 729.4 | 83.3 | 172.9 | 218.4 | 137 | 324.7 | 312.2 | 160.5 | 270 | 390.3 | 206.5
889 | 695 | 555.7 | 222.28 | 259.8325 | 320.3 | 286 | 304.2 | 290.2 | 521.9 | 42.3 | 19.9 | 76.3 | 6.7 | 258.2 | 12.9 | 878.1 | 783.5 | 757.3 | 862.5 | 711.5 | 790 | 715.2 | 777.1 | 742.6 | 731 | 83.5 | 173.2 | 218.6 | 137.3 | 324.4 | 312.5 | 160.8 | 270.1 | 390.5 | 206.7
890 | 696 | 556.1 | 222.44 | 260.0195 | 320.3 | 285.1 | 304.8 | 289.9 | 524.2 | 42.3 | 19.9 | 76.4 | 7.2 | 248.5 | 12.6 | 878.1 | 784.7 | 751.4 | 862.8 | 709.9 | 790.9 | 722.1 | 779 | 742.9 | 733.8 | 83.7 | 173.5 | 218.9 | 137.6 | 324.8 | 312.9 | 161.1 | 270.4 | 390.7 | 207
891 | 697 | 555.8 | 222.32 | 259.8793 | 320.4 | 285.2 | 304.2 | 289.6 | 529.1 | 42.3 | 19.9 | 76.4 | 7.6 | 259.5 | 13.1 | 878 | 784 | 747.7 | 863 | 706.7 | 790.3 | 719.9 | 778 | 743.2 | 732.7 | 83.9 | 173.8 | 219.2 | 137.8 | 325.5 | 313.1 | 161.3 | 270.5 | 391.1 | 207.2
892 | 698 | 556.5 | 222.6 | 260.2066 | 320.9 | 285.1 | 303.8 | 289.6 | 554.2 | 42.3 | 19.9 | 76.5 | 8.3 | 238.5 | 16.7 | 878.1 | 784.4 | 749.1 | 862.7 | 706.6 | 796.7 | 723.8 | 783.7 | 744.4 | 732.1 | 84.1 | 174 | 219.7 | 138.1 | 326.1 | 313.3 | 161.6 | 270.8 | 391.4 | 207.5
893 | 699 | 555.5 | 222.2 | 259.739 | 321.7 | 284.2 | 304.1 | 289.1 | 563 | 42.3 | 19.9 | 76.8 | 10.6 | 244.1 | 17.3 | 878.4 | 784.2 | 756.9 | 862.2 | 707.5 | 798.3 | 723.7 | 786.1 | 744.8 | 731.4 | 84.2 | 174.3 | 219.9 | 138.4 | 326.2 | 313.5 | 161.8 | 271 | 391.7 | 207.8
894 | 700 | 556.4 | 222.56 | 260.1598 | 322.1 | 284.2 | 304.7 | 288.9 | 562 | 42.3 | 19.9 | 76.9 | 10.2 | 237.1 | 14.6 | 877.9 | 786 | 766.2 | 861.8 | 707.5 | 800.6 | 727.4 | 790.2 | 745.2 | 736.6 | 84.4 | 174.5 | 220.2 | 138.7 | 326.7 | 313.8 | 162.1 | 271.3 | 392.1 | 208.1
895 | 701 | 556.9 | 222.76 | 260.3936 | 322.3 | 283.7 | 304.7 | 289 | 562.4 | 42.3 | 19.9 | 77 | 8.4 | 252.7 | 12.4 | 877.3 | 788.1 | 770.5 | 861.4 | 709.1 | 800.5 | 732.7 | 796.9 | 745.2 | 737.7 | 84.6 | 174.8 | 220.5 | 139 | 327.8 | 314 | 162.3 | 271.6 | 392.4 | 208.4
896 | 702 | 556.7 | 222.68 | 260.3001 | 322.2 | 282.6 | 304.6 | 290.4 | 565.3 | 42.3 | 19.9 | 76.9 | 6.5 | 240.8 | 14.1 | 877.8 | 789.9 | 784.8 | 861 | 712 | 801.9 | 735.3 | 802 | 745.7 | 739.7 | 84.8 | 175.1 | 220.7 | 139.3 | 327.6 | 314.1 | 162.6 | 271.8 | 392.8 | 208.7
897 | 703 | 556.9 | 222.76 | 260.3936 | 322 | 281.7 | 303.7 | 291.3 | 576.3 | 42.4 | 19.9 | 76.6 | 6.8 | 244.6 | 17.4 | 877.1 | 791.1 | 789.3 | 860.4 | 713.4 | 804.3 | 734.5 | 804.6 | 746.3 | 741.2 | 85 | 175.4 | 221.1 | 139.5 | 327.4 | 314.2 | 162.9 | 272 | 393.3 | 208.9
898 | 704 | 557.2 | 222.88 | 260.5339 | 321.8 | 281.4 | 303.5 | 290.8 | 589.4 | 42.5 | 19.9 | 76.5 | 5.8 | 245.1 | 15.5 | 876.4 | 792.1 | 792.8 | 859.9 | 715.7 | 806.1 | 739 | 808.6 | 746.9 | 744.2 | 85.2 | 175.6 | 221.3 | 139.8 | 327.1 | 314.2 | 163.2 | 272.1 | 393.7 | 209.2
899 | 705 | 556.8 | 222.72 | 260.3468 | 321.7 | 281.6 | 303.8 | 291 | 597.6 | 42.6 | 19.9 | 76.5 | 6.2 | 247.8 | 14.6 | 875.1 | 793.5 | 790.4 | 859.6 | 717.5 | 803.4 | 741.4 | 811.7 | 747.2 | 745.8 | 85.3 | 175.9 | 221.6 | 140.1 | 326.9 | 314.4 | 163.4 | 272.3 | 394.1 | 209.4
900 | 706 | 555.9 | 222.36 | 259.926 | 322 | 282.1 | 302.8 | 290.7 | 586.5 | 42.7 | 19.9 | 76.6 | 6.1 | 273.9 | 13 | 875.3 | 794.2 | 785.1 | 859.1 | 720.1 | 800.3 | 746.1 | 810.3 | 746.8 | 747.6 | 85.5 | 176.2 | 221.8 | 140.4 | 327.4 | 314.7 | 163.7 | 272.4 | 394.6 | 209.7
901 | 707 | 555.9 | 222.36 | 259.926 | 323.1 | 284 | 302.7 | 290.6 | 572.5 | 42.8 | 19.8 | 76.6 | 7.4 | 248.4 | 13 | 876.5 | 794.4 | 775.6 | 858.6 | 719.8 | 796.6 | 747.7 | 804.9 | 746.4 | 748.3 | 85.7 | 176.6 | 222.1 | 140.7 | 327.5 | 314.9 | 163.9 | 272.7 | 394.9 | 210
902 | 708 | 556.6 | 222.64 | 260.2533 | 323.5 | 284.2 | 302.1 | 291.9 | 560.8 | 42.8 | 19.8 | 76.6 | 11.1 | 259.9 | 13.3 | 876.9 | 794 | 772.4 | 858.5 | 720.2 | 796.1 | 747.2 | 804.5 | 746.2 | 747.9 | 85.9 | 176.9 | 222.3 | 141 | 327.6 | 315.2 | 164.2 | 272.9 | 395.2 | 210.3
903 | 709 | 556.6 | 222.64 | 260.2533 | 323.6 | 284.7 | 302.2 | 292.5 | 565.4 | 43 | 19.8 | 76.9 | 11.7 | 255.7 | 14.9 | 876.7 | 793.8 | 784.3 | 858.3 | 721.7 | 799.5 | 742.5 | 802.6 | 746.8 | 746 | 86.1 | 177.1 | 222.7 | 141.2 | 328 | 315.4 | 164.5 | 273.1 | 395.4 | 210.5
904 | 710 | 556.3 | 222.52 | 260.1131 | 324 | 284.3 | 302.8 | 291.5 | 579.2 | 43 | 19.8 | 77 | 10.2 | 258.2 | 15.2 | 877.1 | 792 | 777.4 | 858 | 720 | 802.3 | 733.9 | 794.7 | 747.2 | 742.8 | 86.3 | 177.4 | 223.3 | 141.5 | 328.1 | 315.6 | 164.8 | 273.2 | 395.8 | 210.8
905 | 711 | 556.5 | 222.6 | 260.2066 | 324.2 | 283.9 | 303.4 | 290.2 | 588.2 | 43.1 | 19.8 | 76.9 | 7.9 | 256.2 | 15.4 | 877.2 | 790.7 | 781.8 | 858.1 | 718.4 | 804.5 | 732.7 | 795.7 | 747.5 | 742.8 | 86.5 | 177.6 | 223.6 | 141.8 | 328.2 | 315.7 | 165 | 273.4 | 396.1 | 211
906 | 712 | 557 | 222.8 | 260.4404 | 324.4 | 283.2 | 304 | 290.7 | 604 | 43.2 | 19.8 | 76.8 | 7.8 | 251.3 | 17.7 | 877.3 | 791.1 | 786.3 | 858.2 | 719.9 | 807.6 | 730.1 | 796.8 | 748.4 | 742.7 | 86.7 | 177.9 | 224.1 | 142.1 | 328.6 | 316 | 165.3 | 273.6 | 396.4 | 211.3
907 | 713 | 557.4 | 222.96 | 260.6274 | 325.1 | 283.2 | 304.1 | 292.6 | 614.6 | 43.3 | 19.8 | 77 | 8.7 | 250.5 | 19.1 | 877.2 | 792 | 788.1 | 858.4 | 719.1 | 808.7 | 726.8 | 797.5 | 748.8 | 742.8 | 86.8 | 178.2 | 224.5 | 142.4 | 328.6 | 316.4 | 165.6 | 273.7 | 396.8 | 211.6
908 | 714 | 558.1 | 223.24 | 260.9547 | 325.7 | 283.5 | 304.8 | 293.3 | 616.9 | 43.4 | 19.8 | 77.4 | 8.2 | 267.1 | 17.2 | 877.1 | 792.5 | 791.4 | 858.4 | 720.4 | 808.4 | 725.7 | 797.2 | 748.9 | 741.9 | 87 | 178.4 | 224.5 | 142.7 | 328.1 | 316.6 | 165.8 | 273.8 | 397.2 | 211.9
909 | 715 | 557 | 222.8 | 260.4404 | 325.8 | 284.2 | 303.9 | 294.3 | 613.3 | 43.4 | 19.8 | 77.6 | 8.1 | 240 | 15.6 | 876.9 | 792.8 | 783.7 | 858.5 | 718.9 | 808.8 | 724.3 | 798.6 | 748.7 | 741.2 | 87.2 | 178.7 | 224.6 | 143 | 327.8 | 316.7 | 166.1 | 274 | 397.5 | 212.1
910 | 716 | 557.9 | 223.16 | 260.8612 | 325.9 | 284.6 | 303.6 | 294.7 | 596.7 | 43.4 | 19.8 | 77.7 | 8.8 | 237.3 | 19.2 | 877 | 793.4 | 770 | 858.5 | 718.5 | 803.3 | 729.1 | 799.7 | 748 | 743.7 | 87.4 | 179 | 224.8 | 143.2 | 327.5 | 316.6 | 166.4 | 274.1 | 397.8 | 212.4
911 | 717 | 559.4 | 223.76 | 261.5625 | 326.1 | 285.2 | 304.6 | 294.2 | 581.6 | 43.5 | 19.8 | 77.7 | 9.5 | 245.2 | 20.6 | 877.6 | 793.4 | 769.9 | 858.5 | 718.9 | 802.8 | 730.3 | 799.3 | 747.7 | 743 | 87.6 | 179.3 | 225.2 | 143.5 | 327.4 | 316.8 | 166.6 | 274.4 | 398 | 212.6
912 | 718 | 558.1 | 223.24 | 260.9547 | 327.2 | 285.8 | 305.4 | 293.8 | 592.6 | 43.6 | 19.8 | 77.7 | 8.6 | 259.2 | 17.4 | 877.9 | 792.1 | 771 | 859.1 | 717.8 | 806.9 | 727.3 | 796.8 | 747.9 | 740.5 | 87.8 | 179.5 | 225.6 | 143.8 | 327.4 | 316.9 | 166.9 | 274.5 | 398.2 | 212.9
913 | 719 | 557.7 | 223.08 | 260.7677 | 327.4 | 285.6 | 306.6 | 292.8 | 602.6 | 43.7 | 19.8 | 77.7 | 7.8 | 250.4 | 13.2 | 878.4 | 793.2 | 779.3 | 859.3 | 719.6 | 810.8 | 728.1 | 800.6 | 748.5 | 742 | 87.9 | 179.8 | 225.9 | 144.1 | 327.7 | 316.7 | 167.2 | 274.7 | 398.5 | 213.1
914 | 720 | 557.6 | 223.04 | 260.7209 | 326.7 | 286.3 | 306.2 | 293.7 | 611.3 | 43.7 | 19.8 | 77.7 | 8 | 230.8 | 13.2 | 878.8 | 793.4 | 787.1 | 859.5 | 719 | 811.6 | 722.3 | 796.1 | 749 | 741.2 | 88.1 | 180 | 226.2 | 144.4 | 327.9 | 316.6 | 167.4 | 274.8 | 398.8 | 213.4
915 | 721 | 557.9 | 223.16 | 260.8612 | 326.3 | 287.5 | 305.9 | 296.2 | 614.6 | 43.7 | 19.8 | 77.7 | 8.3 | 239 | 13.4 | 878.8 | 793.1 | 793.2 | 859.6 | 719.8 | 811.6 | 716.7 | 792.3 | 749.4 | 739 | 88.3 | 180.3 | 226.7 | 144.7 | 328.1 | 316.4 | 167.7 | 274.9 | 399.2 | 213.7
916 | 722 | 559 | 223.6 | 261.3755 | 326.2 | 288.5 | 306.1 | 297.1 | 614 | 43.7 | 19.8 | 77.7 | 8 | 250.9 | 20 | 878.6 | 791.3 | 791.1 | 858.7 | 719.5 | 809 | 710.8 | 786.2 | 749.1 | 736.6 | 88.5 | 180.5 | 227 | 145 | 328.2 | 316.2 | 168 | 275 | 399.4 | 213.9
917 | 723 | 558.5 | 223.4 | 261.1417 | 327.2 | 289.8 | 305.8 | 298.1 | 600.1 | 43.5 | 19.8 | 77.5 | 8.4 | 261.1 | 18.9 | 878.2 | 786.7 | 778.5 | 857.9 | 717 | 805.6 | 701.4 | 772.7 | 748.3 | 732.2 | 88.7 | 180.7 | 227.1 | 145.3 | 328.1 | 316 | 168.2 | 275.1 | 399.7 | 214.2
918 | 724 | 557.5 | 223 | 260.6742 | 327.8 | 290.8 | 306 | 300.6 | 592.3 | 43.4 | 19.8 | 77.5 | 9 | 251.5 | 20.8 | 877.8 | 782.2 | 778.8 | 857.4 | 715.4 | 802.8 | 693.2 | 759 | 747.8 | 728 | 88.9 | 181.1 | 227.6 | 145.6 | 328.3 | 315.8 | 168.6 | 275.2 | 399.9 | 214.4
919 | 725 | 557.8 | 223.12 | 260.8144 | 328.4 | 291.1 | 306.1 | 301.5 | 586.8 | 43.3 | 19.8 | 77.3 | 8 | 258.2 | 21.8 | 877.9 | 780.6 | 782.8 | 857.8 | 714 | 801.7 | 685.6 | 754.3 | 747.5 | 725.8 | 89.1 | 181.4 | 228 | 145.9 | 328.6 | 315.8 | 168.8 | 275.3 | 400.1 | 214.7
920 | 726 | 559.1 | 223.64 | 261.4223 | 328 | 290.9 | 306.5 | 302.8 | 587.4 | 43.3 | 19.8 | 77.3 | 9.2 | 246.6 | 22.1 | 878.6 | 783.2 | 784.1 | 858 | 714.7 | 804.7 | 689.7 | 766.6 | 747.1 | 728.7 | 89.3 | 181.6 | 228 | 146.2 | 328.7 | 315.8 | 169.1 | 275.5 | 400.4 | 215
921 | 727 | 559.5 | 223.8 | 261.6093 | 327.9 | 291.3 | 306.4 | 303.5 | 589.9 | 43.3 | 19.8 | 77.5 | 13.4 | 238.5 | 22.8 | 879.1 | 785.6 | 783.8 | 857.9 | 714.4 | 807.7 | 698.1 | 777.5 | 747.2 | 730.8 | 89.5 | 181.8 | 228.3 | 146.4 | 331.3 | 316 | 169.4 | 275.7 | 400.6 | 215.2
922 | 728 | 558.8 | 223.52 | 261.282 | 327.9 | 291.3 | 306.4 | 304.2 | 603.7 | 43.3 | 19.8 | 77.6 | 13.6 | 248.8 | 20.7 | 879 | 786.9 | 784.6 | 857.6 | 715.3 | 809.5 | 700.4 | 780.4 | 747.7 | 730 | 89.6 | 182.1 | 229 | 146.7 | 332.6 | 316.3 | 169.7 | 275.9 | 400.9 | 215.6
923 | 729 | 557.6 | 223.04 | 260.7209 | 328 | 291.5 | 306.4 | 304.7 | 632.9 | 43.3 | 19.8 | 77.6 | 10.9 | 266.9 | 23.2 | 878.7 | 786.1 | 781.5 | 857.1 | 712.3 | 810.8 | 700.4 | 778.6 | 748.4 | 729.6 | 89.8 | 182.4 | 229.6 | 147 | 332.9 | 316.5 | 170 | 276.1 | 401.3 | 215.9
924 | 730 | 558.5 | 223.4 | 261.1417 | 327.7 | 292.3 | 307 | 305.1 | 644.1 | 43.4 | 19.8 | 77.5 | 8.5 | 252.4 | 23 | 878.6 | 784.4 | 781.9 | 856.8 | 711 | 810.9 | 696.3 | 771.8 | 748.9 | 728.1 | 90 | 182.8 | 230 | 147.3 | 333.3 | 316.6 | 170.3 | 276.2 | 401.7 | 216.2
925 | 731 | 559.7 | 223.88 | 261.7028 | 328.2 | 292.9 | 306.5 | 306.1 | 650.9 | 43.4 | 19.8 | 77.5 | 6.9 | 254.4 | 19.4 | 878.2 | 780.7 | 779.3 | 856.5 | 707.9 | 807.1 | 689.1 | 761.1 | 748.9 | 725.3 | 90.2 | 183.1 | 230.7 | 147.6 | 333.7 | 316.9 | 170.6 | 276.3 | 402 | 216.5
926 | 732 | 558.3 | 223.32 | 261.0482 | 328.7 | 293.7 | 307.7 | 307.1 | 650.8 | 43.5 | 19.8 | 77.5 | 7.1 | 248.2 | 18.2 | 877.5 | 775.3 | 773.7 | 856.1 | 705.4 | 804.7 | 681 | 744.3 | 749.1 | 722.4 | 90.4 | 183.3 | 231.4 | 147.9 | 334.1 | 317 | 170.9 | 276.5 | 402.4 | 216.8
927 | 733 | 558.2 | 223.28 | 261.0015 | 330 | 295 | 308.7 | 308.1 | 656.6 | 43.6 | 19.8 | 77.6 | 9.1 | 258.3 | 15.8 | 877.7 | 772.8 | 772.4 | 856.2 | 704.2 | 805.9 | 677.9 | 735.8 | 749.4 | 720.1 | 90.6 | 183.5 | 232 | 148.2 | 334.5 | 317.4 | 171.2 | 276.7 | 402.8 | 217.1
928 | 734 | 559 | 223.6 | 261.3755 | 330.2 | 296.6 | 309.8 | 308.9 | 661.5 | 43.7 | 19.8 | 77.6 | 10.4 | 243.4 | 16.2 | 877.6 | 771.3 | 766 | 856.2 | 702.7 | 805 | 672.1 | 725.4 | 749.5 | 717.4 | 90.8 | 183.8 | 232.4 | 148.5 | 335 | 317.9 | 171.6 | 276.9 | 403.2 | 217.3
929 | 735 | 558.9 | 223.56 | 261.3288 | 330.2 | 298.7 | 311.1 | 309.5 | 652.7 | 43.7 | 19.8 | 77.7 | 8.9 | 251.1 | 14.6 | 877.3 | 768 | 762.5 | 856.4 | 698.6 | 802.4 | 663.8 | 713.9 | 749.2 | 713.5 | 90.9 | 184.1 | 232.9 | 148.8 | 335.6 | 318.4 | 171.9 | 277.1 | 403.7 | 217.6
930 | 736 | 559.8 | 223.92 | 261.7496 | 331.2 | 300.9 | 311 | 310 | 645 | 43.8 | 19.8 | 77.7 | 9.6 | 246.8 | 18.9 | 877.6 | 767.1 | 767.2 | 856.9 | 697.4 | 803.2 | 663.7 | 713.1 | 748.6 | 711.5 | 91.1 | 184.5 | 233.3 | 149.1 | 336.2 | 318.7 | 172.3 | 277.2 | 404 | 217.9
931 | 737 | 560 | 224 | 261.8431 | 332 | 301.7 | 311 | 310.4 | 657.5 | 43.8 | 19.8 | 77.9 | 10.8 | 239.5 | 21.2 | 877.7 | 767.3 | 765.2 | 857.2 | 695.5 | 807.1 | 666.3 | 715.3 | 748.8 | 710.9 | 91.3 | 184.8 | 233.7 | 149.4 | 336.4 | 318.9 | 172.6 | 277.5 | 404.3 | 218.2
932 | 738 | 560.1 | 224.04 | 261.8899 | 332.8 | 302.3 | 310.5 | 310.6 | 679.6 | 43.8 | 19.8 | 78.1 | 7 | 242.5 | 19.1 | 877.9 | 768.7 | 769.8 | 857.4 | 693.6 | 811 | 669.3 | 718.3 | 749.1 | 709.8 | 91.5 | 185.1 | 234.1 | 149.7 | 337 | 319.2 | 172.9 | 277.6 | 404.7 | 218.5
933 | 739 | 559.9 | 223.96 | 261.7963 | 332.5 | 302.9 | 309.2 | 310.7 | 686.1 | 43.8 | 19.8 | 78.1 | 6.6 | 237.6 | 17.2 | 878.2 | 774.9 | 784.5 | 857.1 | 696.5 | 814.9 | 676.5 | 735.7 | 749.2 | 713.9 | 91.7 | 185.4 | 234.3 | 150 | 337.3 | 319.5 | 173.3 | 277.8 | 405.1 | 218.8
934 | 740 | 559.8 | 223.92 | 261.7496 | 332.6 | 303.4 | 309.6 | 311.5 | 687.9 | 43.8 | 19.8 | 78.1 | 9.4 | 248.1 | 14.5 | 878.3 | 778.1 | 784 | 857.2 | 696 | 817.4 | 683.5 | 749.8 | 749.1 | 717.3 | 91.9 | 185.7 | 234.6 | 150.3 | 337.3 | 319.6 | 173.7 | 278.1 | 405.5 | 219
935 | 741 | 560.1 | 224.04 | 261.8899 | 332.9 | 304.4 | 311 | 312.8 | 680.7 | 43.8 | 19.8 | 78.1 | 9.6 | 260.3 | 15.7 | 877.9 | 781.1 | 787.8 | 857 | 696.8 | 817.6 | 688.8 | 756.4 | 748.7 | 718 | 92.1 | 185.9 | 235 | 150.6 | 337.1 | 320.1 | 174 | 278.3 | 405.9 | 219.3
936 | 742 | 560.3 | 224.12 | 261.9834 | 332.9 | 304.6 | 311.5 | 313.4 | 680 | 43.8 | 19.8 | 78 | 8.7 | 254.3 | 21.4 | 877.4 | 781.1 | 793.3 | 856.7 | 698.1 | 818.8 | 689.7 | 760.2 | 748.6 | 716.6 | 92.3 | 186.2 | 235.3 | 150.9 | 337.1 | 320.1 | 174.4 | 278.4 | 406.3 | 219.6
937 | 743 | 560.2 | 224.08 | 261.9366 | 332.9 | 304.5 | 311.4 | 311.9 | 687.4 | 43.8 | 19.8 | 77.8 | 6.8 | 245.8 | 22.4 | 877.1 | 784.2 | 797.9 | 856.6 | 699 | 820.5 | 695.6 | 767.9 | 748.8 | 718.8 | 92.5 | 186.6 | 235.9 | 151.2 | 337 | 320.2 | 174.9 | 278.6 | 406.7 | 219.9
938 | 744 | 560.5 | 224.2 | 262.0769 | 332.8 | 304.1 | 310.5 | 311.3 | 691.3 | 43.9 | 19.8 | 77.7 | 7.6 | 241.7 | 22.1 | 876.3 | 783.6 | 798.7 | 856.8 | 698.1 | 820 | 691.7 | 766.8 | 748.7 | 717.5 | 92.7 | 187 | 236.1 | 151.5 | 336.9 | 320.4 | 175.4 | 278.8 | 407.1 | 220.1
939 | 745 | 559.8 | 223.92 | 261.7496 | 332.6 | 304.8 | 310.7 | 310.8 | 673.8 | 43.8 | 19.8 | 77.7 | 7.7 | 253 | 16.9 | 876.1 | 782.4 | 787.5 | 857 | 696.7 | 815 | 686.4 | 759.5 | 747.9 | 713.9 | 92.8 | 187.4 | 236.3 | 151.9 | 336.4 | 320.5 | 175.9 | 278.9 | 407.5 | 220.4
940 | 746 | 561.3 | 224.52 | 262.4509 | 332.6 | 305.1 | 310.9 | 310.3 | 663.2 | 43.7 | 19.8 | 77.8 | 7.1 | 258.3 | 18.7 | 876.1 | 783.8 | 780.6 | 857 | 696 | 815.8 | 685.2 | 758.8 | 747.6 | 713 | 93 | 187.8 | 236.9 | 152.2 | 336.2 | 320.6 | 176.4 | 279.1 | 407.7 | 220.7
941 | 747 | 561.8 | 224.72 | 262.6847 | 332.2 | 304 | 310.3 | 311.1 | 659.3 | 43.6 | 19.8 | 78 | 7.4 | 255.2 | 18.3 | 876 | 782.7 | 779.1 | 856.9 | 696.1 | 818.6 | 683.6 | 756.8 | 747.4 | 711.4 | 93.2 | 188.2 | 237.3 | 152.5 | 336 | 320.8 | 176.9 | 279.3 | 408 | 220.9
942 | 748 | 560.9 | 224.36 | 262.2639 | 332.2 | 303.4 | 308.9 | 311.7 | 650.4 | 43.6 | 19.8 | 78.1 | 6.8 | 254.7 | 16.7 | 875.5 | 779.5 | 777.2 | 857.5 | 693.6 | 819.7 | 680.9 | 754.4 | 747.3 | 709 | 93.4 | 188.5 | 237.9 | 152.8 | 335.7 | 320.8 | 177.4 | 279.4 | 408.2 | 221.2
943 | 749 | 561.3 | 224.52 | 262.4509 | 332.9 | 302.6 | 308.8 | 311.2 | 653.7 | 43.6 | 19.8 | 78.2 | 8.6 | 246.7 | 13.6 | 875.4 | 777.6 | 775.3 | 857.7 | 692.2 | 821 | 681.1 | 753.2 | 747 | 706.6 | 93.6 | 188.8 | 238.5 | 153.2 | 335.8 | 320.9 | 178.1 | 279.5 | 408.5 | 221.5
944 | 750 | 563 | 225.2 | 263.2458 | 333.7 | 302.2 | 309.9 | 311.7 | 649 | 43.7 | 19.8 | 78.4 | 9.5 | 254.3 | 12.4 | 876.1 | 780.7 | 785.4 | 858.1 | 692.9 | 822.9 | 687.4 | 764 | 746.7 | 708.4 | 93.8 | 189.1 | 238.5 | 153.5 | 335.7 | 321.1 | 178.7 | 279.7 | 408.7 | 221.8
945 | 751 | 561.6 | 224.64 | 262.5912 | 334.5 | 303.1 | 310.4 | 312.2 | 657.8 | 43.7 | 19.8 | 78.5 | 8.5 | 257.9 | 15.3 | 876.2 | 785.7 | 788.7 | 857.5 | 695.7 | 823.6 | 698.8 | 777.8 | 746.6 | 714.2 | 94 | 189.4 | 238.5 | 153.8 | 335.6 | 321.3 | 179.3 | 279.9 | 409 | 222.1
946 | 752 | 561.4 | 224.56 | 262.4977 | 334.1 | 302.9 | 310.3 | 312.3 | 658 | 43.7 | 19.8 | 78.5 | 7.9 | 258.8 | 15.7 | 875.9 | 789.1 | 784.2 | 856.3 | 697 | 821.2 | 709.9 | 783.9 | 746.1 | 717.1 | 94.2 | 189.7 | 238.8 | 154.1 | 335.5 | 321.3 | 179.8 | 280.1 | 409.3 | 222.3
947 | 753 | 560.4 | 224.16 | 262.0301 | 333.8 | 303.2 | 309.5 | 312.8 | 640.5 | 43.7 | 19.8 | 78.5 | 7.7 | 250.4 | 15.9 | 875.5 | 791.1 | 786.6 | 855.4 | 698.7 | 818.5 | 715.4 | 788.3 | 745.3 | 719.4 | 94.4 | 189.9 | 239 | 154.5 | 335.2 | 321.5 | 180.4 | 280.3 | 409.7 | 222.6
948 | 754 | 560.6 | 224.24 | 262.1236 | 333.4 | 303.2 | 308.6 | 311.4 | 655.5 | 43.7 | 19.8 | 78.5 | 7.8 | 245 | 15.1 | 875.2 | 788.3 | 777.7 | 855 | 696.6 | 818 | 706.9 | 778.3 | 745.2 | 715.5 | 94.6 | 190.2 | 239.9 | 154.8 | 335.3 | 321.8 | 180.9 | 280.5 | 410 | 222.9
949 | 755 | 561.3 | 224.52 | 262.4509 | 333.2 | 302.5 | 307.8 | 309.3 | 643.7 | 43.7 | 19.8 | 78.4 | 9 | 244.4 | 15.4 | 874.7 | 784 | 771.6 | 854.8 | 694 | 811.3 | 696.7 | 767.5 | 744.4 | 711.7 | 94.8 | 190.5 | 240.2 | 155.1 | 334.9 | 321.9 | 181.4 | 280.6 | 410.3 | 223.2
950 | 756 | 562.3 | 224.92 | 262.9185 | 333.9 | 301.9 | 307.8 | 308.2 | 624.2 | 43.7 | 19.8 | 78.4 | 10.4 | 247.3 | 15.3 | 874.3 | 779.7 | 759.2 | 854.8 | 691.7 | 806.7 | 691.6 | 757.2 | 743.4 | 708.1 | 95 | 190.9 | 240.3 | 155.4 | 334.8 | 322.1 | 182 | 280.7 | 410.5 | 223.4
951 | 757 | 560.9 | 224.36 | 262.2639 | 335.5 | 301.9 | 307.8 | 308.1 | 608.5 | 43.7 | 19.8 | 78.5 | 9.6 | 245.9 | 14.3 | 873.7 | 774.2 | 750.6 | 855 | 689.2 | 801.8 | 685.5 | 743.9 | 742.4 | 703.7 | 95.1 | 191.1 | 240.7 | 155.7 | 334.8 | 322 | 182.4 | 280.9 | 410.6 | 223.7
952 | 758 | 561.4 | 224.56 | 262.4977 | 336.9 | 302 | 308.1 | 308.7 | 592 | 43.8 | 19.7 | 78.6 | 8.8 | 238.6 | 14.3 | 873.4 | 771.4 | 749.7 | 855.6 | 689.1 | 798.6 | 682.9 | 738.1 | 741.4 | 701.2 | 95.3 | 191.4 | 241 | 156.1 | 334.4 | 321.7 | 183 | 281 | 410.7 | 224
953 | 759 | 562 | 224.8 | 262.7782 | 337.6 | 301.8 | 309.1 | 309.3 | 574.3 | 43.8 | 19.7 | 78.7 | 8 | 257.9 | 13.5 | 873.7 | 775.4 | 746.8 | 855.7 | 689.8 | 798.2 | 684 | 742.9 | 740.6 | 702.3 | 95.5 | 191.7 | 241.1 | 156.4 | 334 | 321.6 | 183.4 | 281.1 | 410.8 | 224.2
954 | 760 | 562.1 | 224.84 | 262.825 | 337.6 | 301.5 | 309.6 | 309 | 576.9 | 43.8 | 19.7 | 78.8 | 7.7 | 233.5 | 12.3 | 873.8 | 780.6 | 752.9 | 855.1 | 691.5 | 802.6 | 692.2 | 755.1 | 740.5 | 706.7 | 95.7 | 192 | 241.1 | 156.7 | 333.4 | 321.6 | 183.9 | 281.2 | 410.9 | 224.5
955 | 761 | 561.6 | 224.64 | 262.5912 | 337.4 | 300.7 | 308.8 | 308 | 585.6 | 43.8 | 19.7 | 78.9 | 7.8 | 221.8 | 11.3 | 873.7 | 783.7 | 752.4 | 854.2 | 693.7 | 806 | 696.9 | 762.7 | 740.3 | 707.9 | 95.9 | 192.3 | 241.3 | 157 | 332.9 | 321.5 | 184.3 | 281.4 | 411.1 | 224.7
956 | 762 | 562.7 | 225.08 | 263.1056 | 337.5 | 300 | 308.3 | 306.6 | 581.1 | 43.8 | 19.7 | 79 | 7.5 | 247 | 15.6 | 873.8 | 786.4 | 759.4 | 853.8 | 694.5 | 806.8 | 699.8 | 768.3 | 740.1 | 710.8 | 96.1 | 192.6 | 241.5 | 157.3 | 332.3 | 321.2 | 184.8 | 281.5 | 411.4 | 224.9
957 | 763 | 562.9 | 225.16 | 263.1991 | 337.3 | 299.2 | 307.9 | 305.6 | 592.7 | 43.8 | 19.7 | 79 | 9.6 | 238 | 19.7 | 873.9 | 788.4 | 757.9 | 853.6 | 695.1 | 811.3 | 704 | 776.5 | 740.1 | 711.4 | 96.3 | 192.9 | 241.8 | 157.6 | 331.7 | 321 | 185.2 | 281.6 | 411.7 | 225.2
958 | 764 | 562 | 224.8 | 262.7782 | 336.8 | 298.3 | 306.4 | 305.5 | 589.6 | 43.9 | 19.7 | 78.9 | 9.3 | 242.2 | 20.4 | 872 | 790.3 | 761.7 | 852.7 | 697.9 | 812.9 | 712.9 | 785.1 | 739.9 | 714.2 | 96.5 | 193.2 | 242 | 158 | 330.6 | 320.9 | 185.6 | 281.7 | 412 | 225.4
959 | 765 | 561.6 | 224.64 | 262.5912 | 335.9 | 298.8 | 304.5 | 304 | 594.7 | 43.9 | 19.7 | 79 | 9.1 | 246.3 | 18.8 | 870.8 | 792.4 | 768 | 851.6 | 700.7 | 814.7 | 721.5 | 791.7 | 740 | 719.8 | 96.7 | 193.6 | 242.4 | 158.3 | 330.1 | 321 | 186.1 | 281.9 | 412.2 | 225.6
960 | 766 | 561.5 | 224.6 | 262.5445 | 334.6 | 298.7 | 303.7 | 303.6 | 597.5 | 43.9 | 19.7 | 79 | 7.5 | 250.7 | 17.2 | 871.6 | 794.6 | 767 | 850.8 | 700.6 | 812.6 | 724.1 | 795.2 | 739.9 | 721.6 | 96.9 | 193.9 | 242.5 | 158.6 | 329.7 | 321 | 186.5 | 282 | 412.6 | 225.9
961 | 767 | 562.5 | 225 | 263.012 | 333.9 | 298.6 | 302.6 | 303.8 | 586.6 | 44 | 19.7 | 79 | 6.8 | 246 | 16.8 | 872.7 | 793.5 | 763.3 | 850.6 | 699.2 | 806.7 | 721.5 | 790.9 | 739.2 | 720.5 | 97.1 | 194.2 | 242.6 | 158.9 | 329.4 | 321 | 187 | 282.2 | 412.8 | 226.1
962 | 768 | 562.1 | 224.84 | 262.825 | 334.8 | 299.2 | 302.1 | 303.3 | 583.5 | 44.1 | 19.7 | 79 | 7.3 | 244.4 | 17.7 | 872.4 | 789.5 | 751.5 | 850.3 | 697.8 | 804 | 719.1 | 781 | 738.7 | 717.7 | 97.3 | 194.4 | 242.7 | 159.2 | 329.1 | 321 | 187.4 | 282.4 | 413.1 | 226.3
963 | 769 | 562.4 | 224.96 | 262.9653 | 336 | 299.3 | 302.8 | 302.1 | 575.9 | 44 | 19.7 | 78.9 | 7.4 | 246.8 | 15.9 | 872.4 | 788.1 | 751 | 850.7 | 697.7 | 802.2 | 713.6 | 770.5 | 737.9 | 716.1 | 97.5 | 194.7 | 242.9 | 159.5 | 328.7 | 320.8 | 187.8 | 282.5 | 413.2 | 226.5
964 | 770 | 563.5 | 225.4 | 263.4796 | 336.3 | 298.3 | 303.2 | 300.3 | 567.9 | 44 | 19.7 | 79 | 6.4 | 252.6 | 17.4 | 872.4 | 789.4 | 747.1 | 851.2 | 697.3 | 803.2 | 716.4 | 775.9 | 737.4 | 717 | 97.7 | 195 | 243 | 159.8 | 328.6 | 320.9 | 188.3 | 282.7 | 413.3 | 226.8
965 | 771 | 562.4 | 224.96 | 262.9653 | 337.1 | 297.2 | 304.1 | 299.1 | 569.9 | 44 | 19.7 | 79.1 | 6.7 | 249.2 | 19.1 | 872.2 | 790.2 | 737.3 | 851.3 | 696.5 | 803.2 | 720.7 | 778.3 | 737.1 | 720.3 | 97.9 | 195.3 | 243.3 | 160.1 | 328.2 | 320.8 | 188.7 | 282.8 | 413.5 | 227
966 | 772 | 561.3 | 224.52 | 262.4509 | 336.9 | 296.8 | 305 | 298 | 562 | 44 | 19.7 | 79.3 | 7.6 | 250.6 | 21.1 | 872.3 | 788.5 | 740.3 | 851.7 | 696.3 | 798.6 | 715.3 | 770.3 | 736.3 | 716.7 | 98.1 | 195.6 | 243.4 | 160.4 | 328.2 | 320.8 | 189.1 | 282.8 | 413.7 | 227.3
967 | 773 | 560.9 | 224.36 | 262.2639 | 336.7 | 296.2 | 305.4 | 296.3 | 557.8 | 44 | 19.7 | 79.5 | 8.1 | 252.5 | 22 | 872 | 788.9 | 739.1 | 851.2 | 696.3 | 802.3 | 719.1 | 774.8 | 736 | 718 | 98.3 | 195.9 | 243.7 | 160.7 | 327.6 | 320.7 | 189.5 | 282.9 | 413.9 | 227.5
968 | 774 | 562.1 | 224.84 | 262.825 | 336.4 | 295.9 | 305.4 | 295.4 | 575.8 | 44.1 | 19.7 | 79.6 | 7.8 | 250.7 | 21.5 | 871.7 | 786.8 | 736.6 | 850.7 | 695.3 | 805.2 | 722.2 | 777.2 | 736.1 | 717.1 | 98.5 | 196.1 | 244.1 | 161 | 327.4 | 320.6 | 190 | 283 | 414.1 | 227.7
969 | 775 | 562.1 | 224.84 | 262.825 | 336.5 | 294 | 305.6 | 295 | 589.1 | 44.1 | 19.7 | 79.8 | 8 | 245.7 | 20.7 | 871.8 | 785.7 | 735.7 | 850.8 | 695 | 806.2 | 717.1 | 773.8 | 736.2 | 714.7 | 98.7 | 196.4 | 244.4 | 161.3 | 327.5 | 320.6 | 190.3 | 283.2 | 414.2 | 228
970 | 776 | 562.6 | 225.04 | 263.0588 | 336.8 | 292.6 | 305.9 | 294.7 | 595.8 | 44.2 | 19.7 | 79.9 | 8.4 | 252.3 | 22.9 | 871.8 | 784.6 | 734.8 | 851.1 | 693 | 806.4 | 710.3 | 770.7 | 736.1 | 713.1 | 98.9 | 196.7 | 244.7 | 161.5 | 328.3 | 320.4 | 190.7 | 283.3 | 414.4 | 228.2
971 | 777 | 562.5 | 225 | 263.012 | 336.6 | 292.3 | 306.9 | 296.8 | 590.9 | 44.2 | 19.7 | 79.9 | 7.5 | 257.3 | 21.8 | 871.8 | 782.6 | 732.6 | 850.9 | 691.1 | 807 | 708.3 | 770.9 | 735.8 | 711.3 | 99.1 | 197 | 244.9 | 161.8 | 328.9 | 320.3 | 191.2 | 283.3 | 414.5 | 228.5
972 | 778 | 562.5 | 225 | 263.012 | 337 | 292.2 | 308.1 | 299 | 592.5 | 44.2 | 19.7 | 79.8 | 8 | 260.6 | 19 | 871.8 | 782.4 | 737.9 | 850.6 | 691 | 806.9 | 709.9 | 776.4 | 735.5 | 711.2 | 99.3 | 197.2 | 245.2 | 162.1 | 328.6 | 319.9 | 191.6 | 283.4 | 414.7 | 228.8
973 | 779 | 562.3 | 224.92 | 262.9185 | 337 | 292.1 | 308.6 | 300.4 | 601.9 | 44.2 | 19.7 | 79.8 | 8.3 | 264.1 | 15 | 871.5 | 785.5 | 746.4 | 850.4 | 692.9 | 810 | 717.5 | 783.9 | 735.4 | 715.8 | 99.5 | 197.5 | 245.4 | 162.4 | 328.6 | 320 | 192 | 283.5 | 414.8 | 229
974 | 780 | 562.2 | 224.88 | 262.8718 | 336.8 | 292.6 | 308.9 | 299.9 | 608.5 | 44.1 | 19.7 | 79.8 | 7.5 | 258.5 | 14.1 | 872.3 | 783.5 | 739 | 850.7 | 690.4 | 809.3 | 714 | 780 | 735.3 | 713.1 | 99.7 | 197.7 | 245.9 | 162.7 | 328.3 | 320 | 192.4 | 283.7 | 415.1 | 229.2
975 | 781 | 563.5 | 225.4 | 263.4796 | 336.8 | 293 | 309 | 300.4 | 613.3 | 44.1 | 19.7 | 79.6 | 7.9 | 261.7 | 15.6 | 872.3 | 780.4 | 732.5 | 850.8 | 689 | 809.6 | 708.4 | 773.3 | 735.1 | 711.1 | 99.9 | 198.1 | 246.4 | 163 | 328.3 | 320.2 | 192.8 | 283.7 | 415.3 | 229.5
976 | 782 | 563.8 | 225.52 | 263.6199 | 337.8 | 293 | 309.1 | 300.9 | 613.2 | 44.1 | 19.7 | 79.4 | 8.7 | 268 | 16.2 | 871.8 | 781.4 | 727.7 | 850.5 | 688.2 | 809.4 | 712.8 | 775.7 | 734.7 | 711.8 | 100.1 | 198.4 | 246.4 | 163.3 | 328.6 | 320.3 | 193.2 | 283.8 | 415.5 | 229.7
977 | 783 | 563 | 225.2 | 263.2458 | 338 | 293.5 | 309.1 | 302.5 | 605.9 | 44.1 | 19.7 | 79.3 | 9.7 | 256.1 | 15.5 | 871.9 | 783.8 | 724 | 849.9 | 688.7 | 805.9 | 719.9 | 782.5 | 734 | 714.9 | 100.3 | 198.7 | 246.3 | 163.6 | 328.8 | 320.8 | 193.7 | 284 | 415.6 | 229.9
978 | 784 | 563 | 225.2 | 263.2458 | 338.1 | 293.8 | 310.2 | 304.3 | 588.5 | 44.2 | 19.7 | 79.3 | 11.3 | 256.6 | 16 | 872 | 784.3 | 722.3 | 850.1 | 688.2 | 798.4 | 720.7 | 776.9 | 733.2 | 715.1 | 100.5 | 198.9 | 246.5 | 163.8 | 329.1 | 321.7 | 194.1 | 284.3 | 415.8 | 230.2
979 | 785 | 562.6 | 225.04 | 263.0588 | 339 | 294.8 | 311.7 | 304.6 | 566.4 | 44.2 | 19.7 | 79.2 | 9.1 | 258.3 | 15.6 | 871.7 | 785.8 | 738.5 | 850.7 | 690.6 | 793.6 | 721.2 | 773.3 | 732.2 | 715.4 | 100.7 | 199.2 | 246.7 | 164.1 | 330.2 | 322.4 | 194.6 | 284.6 | 416 | 230.5
980 | 786 | 562.7 | 225.08 | 263.1056 | 339.5 | 295.2 | 313.4 | 303.3 | 565.7 | 44.3 | 19.7 | 79 | 6.4 | 250.6 | 18.4 | 870.7 | 787.1 | 754.2 | 849.9 | 694.6 | 797.1 | 726.6 | 779.3 | 731.8 | 720.9 | 100.9 | 199.5 | 247 | 164.4 | 331.4 | 323.3 | 195 | 284.9 | 416.2 | 230.8
981 | 787 | 563.6 | 225.44 | 263.5264 | 339.3 | 295.9 | 313.9 | 302.7 | 566.9 | 44.4 | 19.7 | 78.8 | 6.2 | 252.6 | 18 | 871.5 | 789.1 | 751.3 | 849.3 | 694.6 | 796.3 | 730.2 | 785.1 | 731.4 | 721.9 | 101.1 | 199.7 | 247 | 164.7 | 331.1 | 323.8 | 195.5 | 285 | 416.6 | 231
982 | 788 | 563.6 | 225.44 | 263.5264 | 339.2 | 296.4 | 313.5 | 301.7 | 569.3 | 44.4 | 19.7 | 78.9 | 8.6 | 254.9 | 17.8 | 872.6 | 786.8 | 747 | 849.7 | 693.9 | 798.4 | 730.3 | 779.7 | 731.2 | 720.6 | 101.3 | 200 | 247.2 | 165 | 331.3 | 324.1 | 195.9 | 285.2 | 416.8 | 231.3
983 | 789 | 563.5 | 225.4 | 263.4796 | 339 | 297.6 | 312.2 | 301.8 | 569.6 | 44.4 | 19.7 | 79 | 8.4 | 254.1 | 17.5 | 873.2 | 785.5 | 755.1 | 850.5 | 693.5 | 800.4 | 723.2 | 778.3 | 730.9 | 719.4 | 101.5 | 200.2 | 247.4 | 165.3 | 331.3 | 324.1 | 196.3 | 285.3 | 416.9 | 231.5
984 | 790 | 563.9 | 225.56 | 263.6666 | 338.8 | 298.3 | 312.1 | 302.1 | 587 | 44.5 | 19.7 | 78.9 | 6.6 | 234.4 | 15.4 | 873.8 | 785.8 | 763.6 | 851.4 | 694.5 | 803.4 | 721.5 | 783.5 | 731.1 | 720 | 101.7 | 200.4 | 247.9 | 165.5 | 331.1 | 324 | 196.8 | 285.4 | 417.1 | 231.7
985 | 791 | 565.4 | 226.16 | 264.368 | 339.3 | 298 | 313.5 | 300.9 | 602.2 | 44.6 | 19.7 | 78.9 | 7.3 | 247.1 | 20 | 874.2 | 787 | 771 | 852 | 695.9 | 804.7 | 713.8 | 780 | 731.5 | 718.1 | 101.9 | 200.7 | 248.3 | 165.8 | 330.9 | 323.7 | 197.2 | 285.4 | 417.3 | 232
986 | 792 | 564.2 | 225.68 | 263.8069 | 339.3 | 298.3 | 313.5 | 299.6 | 613 | 44.6 | 19.7 | 78.9 | 6.1 | 243.3 | 19 | 874.5 | 788.9 | 778.4 | 852.5 | 696.3 | 805.7 | 711.8 | 779.8 | 731.7 | 718.1 | 102.1 | 201 | 248.5 | 166.1 | 330.8 | 324 | 197.6 | 285.5 | 417.5 | 232.2
987 | 793 | 564.6 | 225.84 | 263.9939 | 339.3 | 298.4 | 312.1 | 298.8 | 610.8 | 44.6 | 19.7 | 79 | 5.4 | 240.1 | 16.9 | 874.8 | 792.3 | 788.7 | 852.1 | 698.6 | 806.6 | 717.9 | 787.4 | 731.4 | 721.2 | 102.3 | 201.2 | 248.6 | 166.4 | 330.4 | 324 | 198 | 285.6 | 417.7 | 232.4
988 | 794 | 565.2 | 226.08 | 264.2745 | 339.1 | 298.9 | 311.9 | 299.2 | 610.6 | 44.6 | 19.6 | 79.1 | 6.3 | 255 | 14.8 | 875.9 | 795.5 | 788.6 | 852 | 701 | 805.7 | 719 | 790.7 | 731.2 | 723.7 | 102.5 | 201.5 | 248.7 | 166.7 | 330.2 | 323.9 | 198.5 | 285.7 | 417.9 | 232.7
989 | 795 | 564.8 | 225.92 | 264.0875 | 338.3 | 298.2 | 310.7 | 300.2 | 607.5 | 44.6 | 19.6 | 79.2 | 9.6 | 235.3 | 13.3 | 877.4 | 793.8 | 784.3 | 852.1 | 700 | 802 | 712.9 | 783.1 | 730.7 | 720.7 | 102.7 | 201.8 | 249.1 | 167 | 330.1 | 323.8 | 198.9 | 285.8 | 418.2 | 232.9
990 | 796 | 563.9 | 225.56 | 263.6666 | 339.1 | 298.3 | 309.6 | 301.3 | 599.3 | 44.7 | 19.6 | 79.3 | 10.1 | 252.8 | 11.6 | 877.6 | 791.5 | 775.5 | 852.4 | 698.2 | 801.1 | 707 | 776 | 730.3 | 717.3 | 102.9 | 202.1 | 249.5 | 167.2 | 330.1 | 323.6 | 199.3 | 285.9 | 418.4 | 233.1
991 | 797 | 564.2 | 225.68 | 263.8069 | 339.7 | 298.5 | 308.2 | 300.9 | 607.1 | 44.8 | 19.6 | 79.5 | 9.7 | 255.3 | 12.6 | 877.8 | 791.1 | 778.3 | 852.1 | 699.9 | 804.8 | 705.1 | 776.4 | 730.4 | 718.5 | 103.1 | 202.4 | 249.6 | 167.5 | 330.1 | 323.5 | 199.7 | 286 | 418.5 | 233.3
992 | 798 | 564.6 | 225.84 | 263.9939 | 339.7 | 299.4 | 307 | 300.4 | 627.9 | 44.9 | 19.6 | 79.7 | 9.3 | 250.9 | 16.6 | 878.1 | 791.2 | 786.2 | 852 | 700.1 | 808.4 | 705 | 779.6 | 730.6 | 718.3 | 103.3 | 202.6 | 250 | 167.8 | 330.3 | 323.4 | 200.2 | 286 | 418.8 | 233.6
993 | 799 | 563.8 | 225.52 | 263.6199 | 338.3 | 299.9 | 305.7 | 300.8 | 631.2 | 44.9 | 19.6 | 79.8 | 8.1 | 247.9 | 20.3 | 878.8 | 795.3 | 800.9 | 853 | 703.1 | 808.7 | 711.4 | 786.1 | 730.7 | 721.8 | 103.5 | 202.9 | 250.2 | 168.1 | 330 | 323.2 | 200.6 | 286.2 | 419.1 | 233.9
994 | 800 | 563.6 | 225.44 | 263.5264 | 336.6 | 301.1 | 306.1 | 300.3 | 641.8 | 45 | 19.6 | 79.8 | 6.3 | 238.6 | 22.5 | 878 | 797.2 | 804.7 | 853 | 705.7 | 810.5 | 715.5 | 790.9 | 730.6 | 723.8 | 103.7 | 203.1 | 250.6 | 168.3 | 329.5 | 323 | 201 | 286.3 | 419.4 | 234.1
995 | 801 | 564.3 | 225.72 | 263.8537 | 335.4 | 302.1 | 307.1 | 299.7 | 649.7 | 45 | 19.6 | 79.9 | 7.5 | 244.3 | 20.5 | 877.4 | 798.6 | 799.8 | 852.2 | 705.1 | 811 | 722.6 | 795.9 | 730.5 | 726.3 | 103.8 | 203.4 | 250.9 | 168.6 | 329.7 | 323.1 | 201.5 | 286.4 | 419.8 | 234.3
996 | 802 | 564.2 | 225.68 | 263.8069 | 335 | 301.9 | 308.1 | 300.5 | 641.6 | 44.9 | 19.6 | 80 | 6.5 | 254.1 | 16.2 | 878.2 | 800.6 | 793.1 | 851.8 | 705.4 | 811.3 | 731.2 | 800.4 | 730 | 727.9 | 104 | 203.6 | 251 | 168.9 | 329.6 | 323 | 201.9 | 286.5 | 420 | 234.5
997 | 803 | 564.7 | 225.88 | 264.0407 | 335.6 | 301.5 | 308.1 | 300.8 | 640.2 | 44.8 | 19.6 | 80.2 | 7.9 | 245.1 | 15.8 | 877.4 | 801.2 | 796.2 | 851.2 | 707.4 | 810.1 | 738.1 | 803.8 | 729.7 | 730.9 | 104.2 | 203.9 | 251 | 169.2 | 329.4 | 323 | 202.3 | 286.7 | 420.2 | 234.8
998 | 804 | 564.5 | 225.8 | 263.9472 | 335.8 | 301.4 | 308 | 299.7 | 655.9 | 44.8 | 19.6 | 80.4 | 6.9 | 259.1 | 15.5 | 879.2 | 802.4 | 797.4 | 851.2 | 708.2 | 813.6 | 742.8 | 805.3 | 729.9 | 733.2 | 104.4 | 204.2 | 251.4 | 169.5 | 329.4 | 323.1 | 202.8 | 286.8 | 420.4 | 235
999 | 805 | 564.9 | 225.96 | 264.1342 | 335.1 | 301.4 | 308.3 | 299 | 665.6 | 44.8 | 19.6 | 80.5 | 5.6 | 252.7 | 12.1 | 880.1 | 802.4 | 797.4 | 851.3 | 707.8 | 816.7 | 744.6 | 807.4 | 730.2 | 732.6 | 104.6 | 204.4 | 251.8 | 169.7 | 329.4 | 323.2 | 203.2 | 286.9 | 420.7 | 235.2
1000 | 806 | 563.4 | 225.36 | 263.4329 | 334.6 | 300.9 | 309.7 | 300.2 | 671.7 | 44.7 | 19.6 | 80.4 | 6 | 247.3 | 12.2 | 880.4 | 802.2 | 797.5 | 851.5 | 708.6 | 817.9 | 741.4 | 807.3 | 730.3 | 731.8 | 104.8 | 204.7 | 252 | 170 | 329.4 | 323 | 203.7 | 286.9 | 421 | 235.5
1001 | 807 | 563.2 | 225.28 | 263.3393 | 334.3 | 300.1 | 310.9 | 301 | 665.2 | 44.6 | 19.6 | 80.4 | 7.9 | 249.8 | 11.5 | 881.2 | 802.7 | 797.1 | 851.2 | 710 | 813 | 739.7 | 805.3 | 729.9 | 732.8 | 105 | 205 | 252.1 | 170.3 | 329.7 | 323 | 204.1 | 287 | 421.2 | 235.7
1002 | 808 | 562.8 | 225.12 | 263.1523 | 334.6 | 300 | 311.2 | 302.5 | 645 | 44.7 | 19.6 | 80.4 | 9.3 | 258.6 | 12.1 | 881.7 | 803.8 | 780.2 | 851.1 | 708.8 | 810.8 | 739.3 | 802.9 | 729.2 | 733.5 | 105.2 | 205.3 | 252.1 | 170.5 | 329.6 | 323 | 204.6 | 287.2 | 421.5 | 236
1003 | 809 | 564.4 | 225.76 | 263.9004 | 336.1 | 299.9 | 310.9 | 303.3 | 626.5 | 44.7 | 19.6 | 80.4 | 11.3 | 256.5 | 16.8 | 882.4 | 801 | 771 | 851.5 | 707.3 | 809.8 | 732.8 | 797.3 | 728.5 | 730.5 | 105.4 | 205.5 | 252.3 | 170.8 | 329.9 | 323.3 | 205 | 287.4 | 421.6 | 236.2
1004 | 810 | 566.5 | 226.6 | 264.8823 | 337 | 299.2 | 311 | 303.8 | 618.7 | 44.6 | 19.6 | 80.5 | 13.8 | 245.5 | 23.3 | 882 | 797.3 | 766 | 851.7 | 704.5 | 809.8 | 727.3 | 787.4 | 728.1 | 727 | 105.6 | 205.8 | 252.7 | 171.1 | 330 | 323.6 | 205.4 | 287.5 | 421.8 | 236.5
1005 | 811 | 566.1 | 226.44 | 264.6953 | 337.9 | 299 | 310.7 | 303.9 | 620.7 | 44.6 | 19.6 | 80.5 | 9.3 | 238.3 | 20.9 | 881.6 | 799.6 | 773.8 | 851.4 | 707.3 | 813.8 | 724.7 | 790.3 | 728.1 | 728.9 | 105.8 | 206 | 252.9 | 171.3 | 329.5 | 323.7 | 205.9 | 287.5 | 421.9 | 236.7
1006 | 812 | 565.5 | 226.2 | 264.4148 | 338.5 | 299 | 310.1 | 303.8 | 625.9 | 44.6 | 19.6 | 80.4 | 7.7 | 241.8 | 17.6 | 881.5 | 801.9 | 781.8 | 851.3 | 709.4 | 816.3 | 728.5 | 795.1 | 728.1 | 732 | 106 | 206.3 | 253.1 | 171.6 | 329.3 | 323.4 | 206.3 | 287.6 | 422.1 | 236.9
1007 | 813 | 564.8 | 225.92 | 264.0875 | 337.9 | 299 | 310.4 | 304.8 | 648.9 | 44.7 | 19.6 | 80.4 | 8.5 | 213 | 19.4 | 880 | 803.6 | 789.2 | 851 | 710.9 | 817.5 | 732.6 | 799.1 | 728.3 | 733.3 | 106.2 | 206.6 | 253.7 | 171.9 | 329.4 | 323.3 | 206.8 | 287.7 | 422.4 | 237.2
1008 | 814 | 565.6 | 226.24 | 264.4615 | 337.2 | 298.8 | 311.7 | 306.2 | 666.7 | 44.8 | 19.6 | 80.4 | 9 | 205 | 15.4 | 879.6 | 804.8 | 795.6 | 850.7 | 713.3 | 817.3 | 735.1 | 800.9 | 728.7 | 734.6 | 106.4 | 206.9 | 254.2 | 172.1 | 329.9 | 323.4 | 207.4 | 287.7 | 422.9 | 237.4
1009 | 815 | 565.7 | 226.28 | 264.5083 | 336.4 | 299.3 | 313.2 | 308.1 | 666.6 | 44.9 | 19.6 | 80.4 | 7.5 | 243.7 | 9 | 883.2 | 803.8 | 784.5 | 850.9 | 711.5 | 817.2 | 733.9 | 797.7 | 728.7 | 733.9 | 106.6 | 207.2 | 254.3 | 172.4 | 330.6 | 323.5 | 207.8 | 287.9 | 423.4 | 237.6
1010 | 816 | 565.3 | 226.12 | 264.3213 | 336.8 | 300.2 | 314.1 | 308.7 | 651.1 | 44.8 | 19.6 | 80.2 | 6.5 | 230.7 | 7.7 | 883.1 | 804.3 | 777.9 | 850.9 | 711.5 | 815.1 | 734.5 | 798.7 | 728.1 | 733.8 | 106.8 | 207.5 | 254.4 | 172.7 | 330.8 | 323.7 | 208.3 | 288.1 | 423.7 | 237.9
1011 | 817 | 564.4 | 225.76 | 263.9004 | 337.7 | 301.6 | 314.6 | 307.4 | 633.7 | 44.8 | 19.6 | 80.2 | 9.1 | 234.1 | 11.4 | 883.6 | 803.5 | 769.2 | 850.9 | 710.8 | 814.6 | 742 | 800.9 | 727.4 | 735.7 | 107 | 207.8 | 254.5 | 172.9 | 330.9 | 324 | 208.8 | 288.4 | 423.8 | 238.1
1012 | 818 | 563.6 | 225.44 | 263.5264 | 337.3 | 302.1 | 314.7 | 307.4 | 628.4 | 44.8 | 19.6 | 80.2 | 9.2 | 233.1 | 11.6 | 882 | 804.2 | 777 | 850.9 | 713.5 | 817 | 747.5 | 805.3 | 727.3 | 738.7 | 107.2 | 208 | 254.7 | 173.2 | 330.8 | 324.4 | 209.2 | 288.5 | 424 | 238.4
1013 | 819 | 564.8 | 225.92 | 264.0875 | 337.4 | 302 | 314.3 | 307.6 | 636.5 | 44.9 | 19.6 | 80.2 | 8.6 | 248.4 | 13.7 | 882.2 | 806.4 | 776.1 | 851.3 | 714.3 | 817 | 752.4 | 810.7 | 727.3 | 742.1 | 107.4 | 208.3 | 254.9 | 173.5 | 330.9 | 324.6 | 209.7 | 288.7 | 424.2 | 238.6
1014 | 820 | 563.4 | 225.36 | 263.4329 | 338 | 301.5 | 313.9 | 306.7 | 633.4 | 44.9 | 19.6 | 80.2 | 11.2 | 265.2 | 13.8 | 883.7 | 808.5 | 771.6 | 851.8 | 716.2 | 814.4 | 759.2 | 814.3 | 727 | 744.9 | 107.6 | 208.5 | 255.1 | 173.7 | 330.9 | 325 | 210.2 | 288.9 | 424.5 | 238.9
1015 | 821 | 564.3 | 225.72 | 263.8537 | 338.3 | 302.4 | 313.6 | 305.5 | 624.9 | 45 | 19.6 | 80.3 | 8.7 | 243.6 | 14 | 882.1 | 808.1 | 774.2 | 851.6 | 718.4 | 811.3 | 763.3 | 812.6 | 726.8 | 746.9 | 107.8 | 208.7 | 255.3 | 174 | 330.7 | 325.3 | 210.7 | 289 | 424.8 | 239.1
1016 | 822 | 564.7 | 225.88 | 264.0407 | 338 | 304.1 | 314.2 | 304.6 | 617.2 | 45.1 | 19.6 | 80.5 | 8 | 235 | 16.7 | 882.3 | 808 | 772.7 | 851.4 | 719.9 | 809.8 | 765.5 | 812.3 | 726.5 | 749.3 | 108 | 208.9 | 255.5 | 174.3 | 330.9 | 325.7 | 211.2 | 289.2 | 425.1 | 239.3
1017 | 823 | 564.4 | 225.76 | 263.9004 | 338.1 | 304.6 | 314.2 | 303.2 | 616.4 | 45.2 | 19.6 | 80.7 | 7.5 | 241.2 | 20.3 | 884.1 | 810.5 | 779.1 | 851.6 | 718.4 | 810.3 | 768.1 | 814.5 | 726.4 | 750.4 | 108.2 | 209.1 | 255.8 | 174.5 | 331.2 | 326 | 211.7 | 289.3 | 425.5 | 239.6
1018 | 824 | 564.4 | 225.76 | 263.9004 | 338.7 | 304.4 | 312.2 | 302.4 | 618 | 45.2 | 19.6 | 80.8 | 7.9 | 245.9 | 22.3 | 886.5 | 812.4 | 779.5 | 852.4 | 717.5 | 810.4 | 769.6 | 814.5 | 726.3 | 752.1 | 108.4 | 209.3 | 255.8 | 174.8 | 331.5 | 326.2 | 212.2 | 289.5 | 425.8 | 239.8
1019 | 825 | 565.1 | 226.04 | 264.2277 | 338.8 | 305.3 | 310.2 | 301.8 | 606.3 | 45.2 | 19.6 | 81 | 8.4 | 264.5 | 17.2 | 886.9 | 813.5 | 775.6 | 853.1 | 717.7 | 808.3 | 769.9 | 813.5 | 725.9 | 754.1 | 108.5 | 209.5 | 255.9 | 175.1 | 332.1 | 326.6 | 212.6 | 289.7 | 426 | 240
1020 | 826 | 566 | 226.4 | 264.6486 | 338.9 | 306 | 309.8 | 301.7 | 591.9 | 45.2 | 19.6 | 81.2 | 8.2 | 272.7 | 12.2 | 888.1 | 812.8 | 763.7 | 853.1 | 716.7 | 806.7 | 770.3 | 812.2 | 725.7 | 755.2 | 108.7 | 209.7 | 256.1 | 175.3 | 332.2 | 327.3 | 213.2 | 290 | 426.2 | 240.3
1021 | 827 | 565.3 | 226.12 | 264.3213 | 338.9 | 306.6 | 309.9 | 301.9 | 585.6 | 45.3 | 19.6 | 81.3 | 8.1 | 241.1 | 11.1 | 888.4 | 812.2 | 758.4 | 853.5 | 714.3 | 808.8 | 764 | 806.2 | 725.9 | 751.4 | 108.9 | 210 | 256.5 | 175.6 | 332.2 | 327.3 | 213.7 | 290.1 | 426.5 | 240.5
1022 | 828 | 565.7 | 226.28 | 264.5083 | 339 | 307.6 | 310.9 | 301.7 | 599.5 | 45.4 | 19.6 | 81.3 | 9.4 | 243.3 | 11.2 | 888.3 | 811 | 754.4 | 853.5 | 715 | 810.6 | 765.9 | 808.7 | 726.1 | 752.5 | 109.1 | 210.2 | 256.8 | 175.8 | 332.4 | 327.4 | 214.3 | 290.2 | 426.6 | 240.7
1023 | 829 | 566.1 | 226.44 | 264.6953 | 338.7 | 307.4 | 311.6 | 301.1 | 589.1 | 45.6 | 19.6 | 81.3 | 7.9 | 246.7 | 15.4 | 888.1 | 811.7 | 766.2 | 854.1 | 718.4 | 808.4 | 767.3 | 813.1 | 726 | 755.2 | 109.3 | 210.5 | 257 | 176.1 | 332.3 | 327.6 | 214.9 | 290.4 | 426.8 | 241
1024 | 830 | 565.5 | 226.2 | 264.4148 | 338 | 307.4 | 311.2 | 300.8 | 589.9 | 45.7 | 19.6 | 81.3 | 6.5 | 259.6 | 14.2 | 887.4 | 811.2 | 774.1 | 853.9 | 719.3 | 811.1 | 770.2 | 813.6 | 726.2 | 758.2 | 109.5 | 210.7 | 257.1 | 176.3 | 332.4 | 327.7 | 215.4 | 290.6 | 427 | 241.2
1025 | 831 | 565.5 | 226.2 | 264.4148 | 338.2 | 308 | 311.5 | 299.8 | 601 | 45.8 | 19.6 | 81.4 | 6.5 | 240.1 | 13.1 | 888.1 | 813.2 | 769.9 | 853.9 | 719.2 | 811.9 | 769.3 | 812.9 | 726.3 | 757.9 | 109.7 | 210.9 | 257.3 | 176.6 | 332.4 | 327.6 | 215.9 | 290.7 | 427.3 | 241.4
1026 | 832 | 565.7 | 226.28 | 264.5083 | 338 | 308.6 | 312.2 | 299.5 | 603.9 | 45.8 | 19.6 | 81.4 | 6.8 | 250 | 13.2 | 888.2 | 813.1 | 774.5 | 853.6 | 721.8 | 813.5 | 769.6 | 815.8 | 726.5 | 760.3 | 109.9 | 211.1 | 257.4 | 176.9 | 332.4 | 327.7 | 216.4 | 290.9 | 427.6 | 241.6
1027 | 833 | 566.2 | 226.48 | 264.7421 | 338.7 | 308.9 | 312 | 298.3 | 618.9 | 45.9 | 19.6 | 81.4 | 7.9 | 255.1 | 15.3 | 889.6 | 812.3 | 774.2 | 853.6 | 720.5 | 816.1 | 765.5 | 814.6 | 726.9 | 758.1 | 110.1 | 211.4 | 257.8 | 177.1 | 332.1 | 327.4 | 216.9 | 290.9 | 427.9 | 241.8
1028 | 834 | 566.8 | 226.72 | 265.0226 | 339.5 | 309.4 | 310.1 | 297.2 | 628.7 | 45.9 | 19.6 | 81.4 | 10.7 | 237.8 | 15.8 | 889.2 | 811.5 | 779.4 | 853.6 | 720.8 | 817.8 | 765.4 | 816.8 | 727.1 | 758.9 | 110.3 | 211.7 | 258.1 | 177.4 | 331.9 | 327.4 | 217.4 | 291.1 | 428.1 | 242.1
1029 | 835 | 567.7 | 227.08 | 265.4434 | 340.2 | 309.8 | 309.4 | 297.3 | 639.6 | 45.9 | 19.6 | 81.4 | 10.2 | 238.9 | 16.9 | 888.8 | 811.7 | 791.5 | 853.7 | 723.7 | 819.3 | 765.9 | 817.5 | 727.5 | 761.2 | 110.5 | 212 | 258.3 | 177.6 | 331.5 | 327.2 | 217.9 | 291.2 | 428.4 | 242.3
1030 | 836 | 566.6 | 226.64 | 264.9291 | 339.4 | 309.7 | 308.9 | 297.7 | 635.4 | 45.9 | 19.6 | 81.5 | 9 | 247.8 | 15.5 | 888.3 | 812.8 | 795.4 | 853.6 | 725.6 | 817.8 | 766.9 | 820.2 | 727.4 | 761.5 | 110.7 | 212.2 | 258.3 | 177.9 | 331.4 | 327.1 | 218.4 | 291.3 | 428.7 | 242.5
1031 | 837 | 566.1 | 226.44 | 264.6953 | 338.4 | 310.1 | 309.5 | 297.5 | 636.5 | 45.9 | 19.6 | 81.6 | 8.1 | 250.6 | 13.5 | 888.4 | 812.3 | 799.6 | 853.6 | 728.1 | 820 | 768 | 819.3 | 727.6 | 762.8 | 110.9 | 212.4 | 258.7 | 178.2 | 331.5 | 327.1 | 218.9 | 291.4 | 428.9 | 242.7
1032 | 838 | 566 | 226.4 | 264.6486 | 338 | 310.8 | 309 | 297.8 | 636.7 | 45.9 | 19.6 | 81.6 | 7.2 | 252 | 12.6 | 889.3 | 813 | 810.4 | 854 | 733 | 819.8 | 763.8 | 817.5 | 727.6 | 763.9 | 111.1 | 212.7 | 258.9 | 178.4 | 331.7 | 327 | 219.3 | 291.4 | 429.2 | 243
1033 | 839 | 567.5 | 227 | 265.3499 | 337.5 | 311.6 | 309.6 | 299.9 | 619.6 | 46 | 19.6 | 81.5 | 7.2 | 251 | 15 | 888.1 | 812.4 | 810.8 | 853.9 | 733.9 | 817.4 | 760.3 | 817.9 | 727.3 | 764.4 | 111.3 | 212.9 | 258.9 | 178.7 | 331.9 | 327 | 219.7 | 291.5 | 429.5 | 243.2
1034 | 840 | 566.9 | 226.76 | 265.0694 | 337.1 | 310.6 | 310.4 | 300.7 | 628.6 | 46 | 19.6 | 81.3 | 6.4 | 254.4 | 15.8 | 887.3 | 812.2 | 816.3 | 853.6 | 735.9 | 817.7 | 755.1 | 815.5 | 727.4 | 763.7 | 111.5 | 213.1 | 259.3 | 178.9 | 331.7 | 326.9 | 220.1 | 291.6 | 429.9 | 243.5
1035 | 841 | 565.3 | 226.12 | 264.3213 | 336.7 | 309.5 | 309.5 | 299.8 | 638.9 | 46 | 19.6 | 81.2 | 6.5 | 250 | 15.1 | 888.8 | 813 | 808.4 | 853.4 | 735.6 | 817.1 | 755.5 | 814.4 | 727.2 | 763.1 | 111.7 | 213.4 | 259.6 | 179.2 | 331.7 | 326.8 | 220.5 | 291.7 | 430.2 | 243.7
1036 | 842 | 567 | 226.8 | 265.1161 | 337 | 309.9 | 309 | 299.4 | 625.6 | 46 | 19.6 | 81.3 | 7.2 | 248.7 | 15 | 889.2 | 812.6 | 804.1 | 853.5 | 737.1 | 812.9 | 761 | 815.7 | 726.7 | 764.4 | 111.9 | 213.6 | 259.6 | 179.4 | 331.4 | 327 | 220.9 | 291.9 | 430.4 | 243.9
1037 | 843 | 567.5 | 227 | 265.3499 | 337.5 | 311.5 | 308.4 | 300.4 | 619.6 | 46 | 19.6 | 81.4 | 6.5 | 274.8 | 14.2 | 891.6 | 812.5 | 799 | 853.6 | 736.6 | 811.2 | 765.5 | 818.3 | 726.5 | 765.8 | 112 | 213.8 | 259.8 | 179.7 | 331.7 | 327.2 | 221.3 | 292 | 430.6 | 244.1
1038 | 844 | 565.9 | 226.36 | 264.6018 | 337.2 | 311.1 | 307.8 | 299.7 | 615.4 | 46 | 19.6 | 81.6 | 6.4 | 262.5 | 13.7 | 891.4 | 813.3 | 785 | 853.4 | 736.4 | 813 | 767.4 | 818.7 | 726.4 | 766.2 | 112.2 | 214 | 260.2 | 180 | 331.6 | 327.4 | 221.7 | 292 | 430.9 | 244.4
1039 | 845 | 566.4 | 226.56 | 264.8356 | 338.2 | 309.9 | 308.4 | 298.8 | 606.2 | 46 | 19.6 | 81.5 | 6.7 | 279.9 | 13 | 893.6 | 812.9 | 770.1 | 853.4 | 734.9 | 810.3 | 766 | 815.4 | 726.3 | 765.3 | 112.4 | 214.2 | 260.4 | 180.2 | 331.8 | 327.6 | 222.2 | 292.1 | 431.2 | 244.6
1040 | 846 | 567.9 | 227.16 | 265.537 | 339.3 | 309.3 | 310 | 297.9 | 589.5 | 46 | 19.6 | 81.5 | 6.8 | 261 | 12 | 894.7 | 809 | 752.8 | 853.3 | 732.6 | 803.1 | 759.2 | 801.7 | 725.9 | 761 | 112.6 | 214.4 | 260.6 | 180.5 | 332 | 328 | 222.7 | 292.3 | 431.4 | 244.8
1041 | 847 | 566.9 | 226.76 | 265.0694 | 340.9 | 308.6 | 311.8 | 298.1 | 571.7 | 46 | 19.6 | 81.5 | 7 | 262 | 13.3 | 896.1 | 802.1 | 739.1 | 854 | 729 | 795.2 | 750.6 | 783.9 | 725.3 | 758 | 112.8 | 214.7 | 260.7 | 180.7 | 332 | 328.3 | 223.1 | 292.5 | 431.5 | 245.1
1042 | 848 | 567.8 | 227.12 | 265.4902 | 342.4 | 308.2 | 312.1 | 299.2 | 558.4 | 45.9 | 19.6 | 81.6 | 6.7 | 253.6 | 15.2 | 896.2 | 802.2 | 737.1 | 854.5 | 729.3 | 794.7 | 751.1 | 784.6 | 725 | 759.4 | 113 | 214.9 | 260.8 | 181 | 332.2 | 328.3 | 223.6 | 292.7 | 431.5 | 245.3
1043 | 849 | 567.7 | 227.08 | 265.4434 | 342.5 | 307.6 | 312.5 | 299.7 | 555.6 | 45.9 | 19.5 | 81.7 | 6.3 | 257.9 | 16.1 | 894.6 | 803.6 | 755.9 | 854.6 | 732.8 | 798.3 | 752.4 | 790.5 | 725 | 761.9 | 113.2 | 215.1 | 261 | 181.2 | 332.5 | 328.5 | 224.2 | 292.8 | 431.6 | 245.5
1044 | 850 | 568 | 227.2 | 265.5837 | 341.6 | 306.6 | 312.8 | 300.2 | 559.7 | 45.9 | 19.6 | 81.8 | 6.2 | 266.6 | 16.2 | 896.2 | 805.7 | 760.6 | 855.2 | 732.9 | 796.9 | 750.4 | 791.2 | 724.9 | 763.1 | 113.4 | 215.4 | 261 | 181.5 | 332.7 | 329.3 | 224.5 | 293 | 431.9 | 245.7
1045 | 851 | 566.9 | 226.76 | 265.0694 | 341 | 305.7 | 312.7 | 300.1 | 551.9 | 45.9 | 19.5 | 81.8 | 5.7 | 261.3 | 13.1 | 895.8 | 807.6 | 770 | 855.5 | 734.1 | 795.4 | 748.4 | 792 | 724.7 | 761.7 | 113.6 | 215.7 | 261.1 | 181.7 | 332.7 | 329.8 | 225 | 293.2 | 432.3 | 246
1046 | 852 | 567.8 | 227.12 | 265.4902 | 339.8 | 305.9 | 312.3 | 300.3 | 562.3 | 46.1 | 19.5 | 81.9 | 6.4 | 255.4 | 16 | 896.3 | 807.5 | 767 | 855.6 | 734.3 | 801.2 | 748.5 | 796.3 | 724.8 | 762.5 | 113.8 | 215.9 | 261.3 | 182 | 332.9 | 329.8 | 225.3 | 293.2 | 432.3 | 246
1047 | 853 | 565.6 | 226.24 | 264.4615 | 336.9 | 306.4 | 312.2 | 300.9 | 584.1 | 46.4 | 19.5 | 82.2 | 7.3 | 238.7 | 17.9 | 897 | 807.4 | 760 | 856.1 | 730.8 | 803.5 | 749 | 800.4 | 725.1 | 760.5 | 113.9 | 216.1 | 261.6 | 182.2 | 332.8 | 329.9 | 225.7 | 293.3 | 432.2 | 245.7
1048 | 854 | 566.6 | 226.64 | 264.9291 | 337.3 | 305.5 | 310.2 | 300.1 | 598.4 | 46.5 | 19.5 | 82.5 | 6.6 | 267 | 17.4 | 895.9 | 807.5 | 776.8 | 856.3 | 731.4 | 808.2 | 752.7 | 801.9 | 725.3 | 760.5 | 114.1 | 216.3 | 261.9 | 182.5 | 332.7 | 330.1 | 226 | 293.4 | 432.5 | 246
1049 | 855 | 568.2 | 227.28 | 265.6772 | 340.5 | 303.8 | 307.3 | 299.8 | 612.9 | 46 | 19.5 | 82.5 | 5.9 | 274.7 | 18.3 | 894.9 | 807.5 | 786.4 | 856.1 | 733.8 | 811.8 | 753.6 | 804.2 | 725.8 | 763 | 114.3 | 216.5 | 262.3 | 182.7 | 332.5 | 329.8 | 226.5 | 293.4 | 433 | 246.9
1050 | 856 | 567.7 | 227.08 | 265.4434 | 340 | 303.5 | 308.3 | 301.1 | 633.4 | 46.1 | 19.5 | 82.5 | 7.3 | 273.1 | 16.2 | 893.7 | 808.5 | 792.8 | 855.7 | 734.4 | 813.9 | 761.2 | 807.5 | 726.2 | 765.6 | 114.5 | 216.7 | 262.5 | 183 | 332.1 | 329.5 | 226.9 | 293.5 | 433.4 | 247.1
1051 | 857 | 568.5 | 227.4 | 265.8175 | 339.2 | 303.7 | 309.3 | 302.9 | 643.7 | 46.1 | 19.5 | 82.6 | 8.7 | 266.7 | 19.8 | 892 | 810.1 | 800.8 | 855.6 | 737.7 | 814.3 | 763.5 | 810.9 | 726.4 | 767.2 | 114.7 | 217 | 262.7 | 183.2 | 332.3 | 329.7 | 227.3 | 293.7 | 433.7 | 247.3
1052 | 858 | 567.9 | 227.16 | 265.537 | 338.6 | 305.1 | 308.8 | 304.5 | 654.6 | 46.1 | 19.5 | 82.6 | 9.8 | 258.7 | 21 | 894.2 | 811.1 | 809.5 | 855.9 | 739.1 | 813.6 | 766.2 | 814.5 | 726.6 | 769.4 | 114.9 | 217.3 | 262.9 | 183.5 | 332.5 | 329.9 | 227.7 | 293.9 | 434.1 | 247.5
1053 | 859 | 567.3 | 226.92 | 265.2564 | 338 | 306.6 | 307.9 | 304.9 | 650.1 | 46 | 19.5 | 82.6 | 8.4 | 253.4 | 22.1 | 894.7 | 811.4 | 812.4 | 855.9 | 741.2 | 811.7 | 767.9 | 815 | 726.5 | 771 | 115.1 | 217.5 | 263.1 | 183.7 | 332.7 | 330 | 228.1 | 293.9 | 434.6 | 247.8
1054 | 860 | 567.3 | 226.92 | 265.2564 | 337.7 | 308.2 | 306.5 | 305 | 639.5 | 45.9 | 19.5 | 82.6 | 8.6 | 254.8 | 21.5 | 898.1 | 812.3 | 806.3 | 856 | 740.6 | 810.8 | 767.3 | 816.1 | 726.2 | 771.2 | 115.2 | 217.7 | 263.2 | 184 | 332.9 | 330.2 | 228.4 | 294 | 434.9 | 248
1055 | 861 | 565.5 | 226.2 | 264.4148 | 338.2 | 309.7 | 305.4 | 305.6 | 633.3 | 45.9 | 19.5 | 82.8 | 8.2 | 259.7 | 19.7 | 899.7 | 814.1 | 807.6 | 856.1 | 740.9 | 811.2 | 768.4 | 819.2 | 726.1 | 772.5 | 115.4 | 218 | 263.4 | 184.2 | 332.6 | 330.2 | 228.8 | 294.1 | 435.1 | 248.2
1056 | 862 | 566.3 | 226.52 | 264.7888 | 338.1 | 309.6 | 305.3 | 305.4 | 628.2 | 45.9 | 19.5 | 82.8 | 7.4 | 252.6 | 18.3 | 900.3 | 815.4 | 808.7 | 856 | 739.7 | 813.5 | 762.3 | 815.6 | 725.9 | 771 | 115.6 | 218.2 | 263.7 | 184.5 | 332.4 | 330 | 229.1 | 294.2 | 435.4 | 248.4
1057 | 863 | 566.1 | 226.44 | 264.6953 | 338.1 | 309.5 | 304.4 | 305.6 | 627.2 | 45.9 | 19.5 | 82.9 | 6.7 | 248.9 | 17.3 | 899.6 | 814.9 | 812.8 | 855.9 | 739.9 | 815 | 757.1 | 811.6 | 725.8 | 768.6 | 115.8 | 218.5 | 263.9 | 184.7 | 332.3 | 329.9 | 229.4 | 294.3 | 435.5 | 248.6
1058 | 864 | 566.5 | 226.6 | 264.8823 | 338.7 | 309.1 | 304.7 | 304 | 615.4 | 46 | 19.5 | 83 | 6.4 | 249.4 | 17 | 896.8 | 813.6 | 803.7 | 855.4 | 741.5 | 813.6 | 758.6 | 814.2 | 725.6 | 771.7 | 116 | 218.8 | 264 | 185 | 332 | 329.8 | 229.9 | 294.4 | 435.7 | 248.9
1059 | 865 | 567.6 | 227.04 | 265.3967 | 340 | 309.2 | 305.9 | 302.8 | 607.8 | 46 | 19.5 | 83.2 | 8 | 262.1 | 16 | 896.8 | 812 | 787.7 | 855.5 | 739.6 | 811.6 | 764.1 | 811.8 | 725.1 | 771.8 | 116.2 | 219 | 264.2 | 185.2 | 332.1 | 330.2 | 230.2 | 294.5 | 436 | 249.1
1060 | 866 | 567.6 | 227.04 | 265.3967 | 340.1 | 310 | 305.9 | 302.5 | 608.1 | 46.1 | 19.5 | 83.3 | 7.9 | 268.3 | 18.5 | 894.8 | 811.5 | 785.2 | 854.8 | 742.5 | 809.9 | 768.4 | 816.7 | 725 | 773.6 | 116.3 | 219.2 | 264.4 | 185.5 | 332.2 | 330.4 | 230.7 | 294.5 | 436.2 | 249.3
1061 | 867 | 566.3 | 226.52 | 264.7888 | 340.1 | 310.5 | 305.1 | 302.7 | 607 | 46.1 | 19.5 | 83.3 | 7.9 | 257.8 | 18.5 | 896.6 | 812.4 | 794.8 | 854.7 | 742.2 | 810.6 | 771.5 | 818.8 | 725 | 775 | 116.5 | 219.4 | 264.7 | 185.7 | 332.3 | 330.5 | 231.1 | 294.6 | 436.4 | 249.6
1062 | 868 | 566.3 | 226.52 | 264.7888 | 339.6 | 310.5 | 305.3 | 302.6 | 607.3 | 46.2 | 19.5 | 83.4 | 7.5 | 255.3 | 18.8 | 897.4 | 812.8 | 799.5 | 855 | 744.1 | 808.9 | 770.5 | 817.1 | 725 | 775.2 | 116.7 | 219.6 | 264.8 | 186 | 332.5 | 330.3 | 231.4 | 294.6 | 436.6 | 249.8
1063 | 869 | 566.1 | 226.44 | 264.6953 | 339 | 310.9 | 305 | 301.2 | 611.7 | 46.3 | 19.5 | 83.5 | 8.1 | 260.6 | 20.1 | 898.1 | 811.2 | 801.1 | 854.7 | 744.4 | 812.1 | 770 | 817.4 | 725.2 | 775.3 | 116.8 | 219.8 | 265.1 | 186.2 | 332.7 | 330.3 | 231.7 | 294.6 | 436.9 | 250
1064 | 870 | 565.5 | 226.2 | 264.4148 | 339.1 | 310.3 | 304.5 | 301.1 | 622.5 | 46.3 | 19.5 | 83.7 | 9.1 | 248.1 | 21.5 | 896.5 | 812.5 | 790.7 | 854.6 | 744.3 | 813.2 | 773.4 | 819.3 | 725.3 | 775.7 | 117 | 220 | 265.3 | 186.4 | 332.7 | 330.7 | 232.1 | 294.8 | 437.2 | 250.2
1065 | 871 | 566.4 | 226.56 | 264.8356 | 339.1 | 309.2 | 303 | 302.3 | 624.4 | 46.4 | 19.5 | 83.9 | 10 | 261.6 | 21.2 | 895.6 | 811.7 | 777.3 | 854.1 | 742.7 | 810.9 | 776.6 | 818.7 | 725.3 | 776.8 | 117.2 | 220.2 | 265.6 | 186.7 | 332.6 | 331.2 | 232.5 | 294.9 | 437.5 | 250.4
1066 | 872 | 566.4 | 226.56 | 264.8356 | 339.7 | 308.1 | 303.5 | 302.4 | 616 | 46.5 | 19.5 | 84 | 11 | 255.2 | 20.2 | 896.5 | 814.6 | 767.5 | 853.7 | 741.3 | 809.3 | 779.4 | 817.8 | 725.2 | 777 | 117.4 | 220.4 | 265.9 | 186.9 | 332.9 | 331.4 | 232.9 | 295 | 437.8 | 250.6
1067 | 873 | 566 | 226.4 | 264.6486 | 340.6 | 307.4 | 304.7 | 302.2 | 607.2 | 46.5 | 19.5 | 84.2 | 8.8 | 247.6 | 17 | 895.1 | 814.1 | 772.5 | 853.4 | 742.1 | 812.2 | 780.5 | 820 | 725.3 | 779 | 117.5 | 220.6 | 266.1 | 187.2 | 333.3 | 332.1 | 233.3 | 295.1 | 438.1 | 250.9
1068 | 874 | 566.7 | 226.68 | 264.9759 | 341.2 | 307.2 | 305.8 | 302.8 | 612.5 | 46.5 | 19.5 | 84.3 | 8.7 | 249.5 | 15.1 | 896.6 | 814.3 | 780.8 | 853.4 | 740.8 | 812.9 | 778.4 | 817.2 | 725.3 | 777.5 | 117.7 | 220.8 | 266.3 | 187.4 | 333.6 | 332.5 | 233.7 | 295.3 | 438.3 | 251.1
1069 | 875 | 566.3 | 226.52 | 264.7888 | 341.8 | 307.1 | 307.2 | 303.5 | 610 | 46.5 | 19.5 | 84.2 | 7.7 | 233 | 14.6 | 894.8 | 813.1 | 786.8 | 853.3 | 742.6 | 811.5 | 779.7 | 819.7 | 725.3 | 779 | 117.9 | 221 | 266.4 | 187.6 | 333.8 | 332.8 | 234 | 295.4 | 438.5 | 251.3
1070 | 876 | 567 | 226.8 | 265.1161 | 342.7 | 307.7 | 308.2 | 304 | 605.2 | 46.5 | 19.5 | 84.1 | 8.3 | 246 | 15.4 | 894.8 | 811.9 | 773.2 | 852.8 | 742.5 | 809.5 | 781.9 | 821.6 | 725.3 | 780.6 | 118 | 221.2 | 266.6 | 187.9 | 334.5 | 333.1 | 234.4 | 295.6 | 438.8 | 251.5
1071 | 877 | 566.8 | 226.72 | 265.0226 | 344 | 309.1 | 309.4 | 304.3 | 616.1 | 46.4 | 19.5 | 83.9 | 7.2 | 255.9 | 15 | 893.7 | 812.1 | 782.7 | 852.2 | 743.1 | 813.4 | 782.5 | 822.9 | 725.7 | 780.6 | 118.2 | 221.4 | 267 | 188.1 | 335.1 | 333.2 | 234.9 | 295.7 | 439.2 | 251.8
1072 | 878 | 567 | 226.8 | 265.1161 | 344.2 | 310.1 | 309.9 | 303.6 | 638.6 | 46.3 | 19.5 | 83.6 | 7 | 256.5 | 15.8 | 894.7 | 811.8 | 790.4 | 851.6 | 745.8 | 815.9 | 776.6 | 817 | 726.2 | 779.7 | 118.4 | 221.7 | 267.3 | 188.4 | 335.7 | 333.3 | 235.3 | 295.9 | 439.6 | 252
1073 | 879 | 567.3 | 226.92 | 265.2564 | 344.9 | 311.6 | 309.5 | 303.8 | 643.5 | 46.3 | 19.5 | 83.5 | 7.1 | 266.1 | 15.3 | 895.8 | 811.9 | 800.3 | 851.4 | 746.7 | 816.5 | 772.5 | 814.4 | 726.6 | 779.1 | 118.5 | 221.8 | 267.5 | 188.6 | 336.2 | 333.9 | 235.7 | 296 | 439.9 | 252.3
1074 | 880 | 567.4 | 226.96 | 265.3032 | 345.5 | 312.8 | 309.7 | 305.5 | 641.8 | 46.3 | 19.5 | 83.4 | 8.9 | 268.2 | 14 | 896.1 | 811.7 | 802.1 | 851.6 | 749.3 | 814.1 | 770.1 | 814.3 | 726.8 | 781.9 | 118.7 | 222.1 | 267.6 | 188.8 | 336.2 | 334.6 | 236.1 | 296.1 | 440.3 | 252.5
1075 | 881 | 567.6 | 227.04 | 265.3967 | 344.5 | 313.7 | 311.2 | 306.7 | 637.8 | 46.3 | 19.5 | 83.4 | 9.4 | 258.6 | 18.5 | 896.8 | 810.3 | 801.2 | 851.2 | 749.7 | 815.1 | 769.1 | 815.1 | 727.1 | 782.2 | 118.9 | 222.2 | 268 | 189.1 | 336.3 | 334.8 | 236.4 | 296.2 | 440.7 | 252.8
1076 | 882 | 567.8 | 227.12 | 265.4902 | 344.7 | 314.9 | 310.7 | 306.9 | 637.2 | 46.2 | 19.5 | 83.4 | 10 | 248.2 | 20.4 | 898.5 | 810.4 | 786.7 | 850.6 | 746.9 | 811.3 | 763.3 | 810 | 726.9 | 778.2 | 119 | 222.4 | 268.3 | 189.3 | 336.3 | 334.7 | 236.8 | 296.4 | 441.1 | 253
1077 | 883 | 567.9 | 227.16 | 265.537 | 345.6 | 314.7 | 311 | 307.1 | 614.9 | 46.2 | 19.5 | 83.4 | 10.6 | 247.6 | 19.1 | 900.8 | 809.7 | 774.3 | 850.3 | 744.9 | 808.7 | 756.1 | 799.9 | 726.4 | 773.2 | 119.2 | 222.6 | 268.2 | 189.5 | 336.4 | 334.6 | 237.2 | 296.5 | 441.3 | 253.2
1078 | 884 | 567.8 | 227.12 | 265.4902 | 347.4 | 313.9 | 310.3 | 307.7 | 593.6 | 46.2 | 19.5 | 83.4 | 11 | 254.1 | 20.7 | 901.3 | 805.2 | 762.5 | 850 | 742 | 804.1 | 748.8 | 786.7 | 725.9 | 769.4 | 119.3 | 222.8 | 268.3 | 189.8 | 336.3 | 334.4 | 237.5 | 296.6 | 441.3 | 253.5
1079 | 885 | 567.4 | 226.96 | 265.3032 | 349.3 | 313.8 | 310.6 | 307.3 | 576 | 46.2 | 19.5 | 83.4 | 10.7 | 260.3 | 21.2 | 901.2 | 803.4 | 765.7 | 850.4 | 741.1 | 802.7 | 742.9 | 782.7 | 725.5 | 767.6 | 119.5 | 223 | 268.5 | 190 | 336.3 | 334.3 | 237.9 | 296.7 | 441.3 | 253.7
1080 | 886 | 567.9 | 227.16 | 265.537 | 350.3 | 312.8 | 311.9 | 307.1 | 577.4 | 46.2 | 19.5 | 83.4 | 9 | 244.1 | 18.5 | 901.5 | 804.7 | 762.4 | 850.8 | 740.3 | 808.1 | 747.6 | 793.5 | 725.4 | 770.3 | 119.7 | 223.2 | 268.7 | 190.2 | 336.6 | 334.3 | 238.3 | 296.7 | 441.4 | 253.9
1081 | 887 | 567.7 | 227.08 | 265.4434 | 346.2 | 312.9 | 315.7 | 308.4 | 579.6 | 46.9 | 19.5 | 83.4 | 10.5 | 243.3 | 18.6 | 901.4 | 806.5 | 764.6 | 851.7 | 740.9 | 808.2 | 754.7 | 799.3 | 725.3 | 772.4 | 119.8 | 223.4 | 268.8 | 190.5 | 337 | 334.3 | 238.5 | 296.9 | 441 | 253.3
1082 | 888 | 567.5 | 227 | 265.3499 | 348.4 | 311 | 315 | 307.8 | 584.1 | 46.5 | 19.4 | 83.3 | 9.6 | 248.1 | 19.8 | 901.1 | 807.2 | 778.6 | 852 | 741.4 | 808.6 | 759.3 | 804.3 | 725.2 | 772.3 | 120 | 223.6 | 269 | 190.7 | 336.9 | 334.2 | 238.9 | 297 | 441.5 | 253.9
1083 | 889 | 566.3 | 226.52 | 264.7888 | 339.1 | 314.2 | 321.2 | 309.8 | 588.1 | 47.9 | 19.4 | 83.3 | 10.2 | 248.5 | 18.6 | 902.8 | 807.3 | 771.5 | 852.2 | 740.1 | 806.5 | 764.8 | 805.1 | 725.2 | 774.2 | 120.1 | 223.7 | 269.2 | 190.9 | 336.9 | 334.3 | 239.2 | 297.2 | 440.7 | 252.5
1084 | 890 | 565.9 | 226.36 | 264.6018 | 343 | 312.8 | 319 | 307 | 585.9 | 47.3 | 19.4 | 83.3 | 8.7 | 245.2 | 19.2 | 904.5 | 806.2 | 756.9 | 852.6 | 737.2 | 801 | 765.8 | 800.9 | 725 | 770.9 | 120.3 | 223.9 | 269.5 | 191.1 | 336.8 | 334.4 | 239.6 | 297.3 | 441.4 | 253.5
1085 | 891 | 569 | 227.6 | 266.0513 | 350.1 | 310.1 | 314.5 | 303.6 | 574.5 | 46.3 | 19.4 | 83.3 | 8.7 | 248.6 | 17.3 | 903.8 | 806 | 753.5 | 852.7 | 739 | 796 | 767.1 | 795.6 | 724.7 | 773.7 | 120.4 | 224.1 | 269.7 | 191.4 | 336.7 | 334.8 | 239.9 | 297.5 | 442.3 | 254.9
1086 | 892 | 568.2 | 227.28 | 265.6772 | 350.1 | 310.3 | 315 | 303.2 | 565 | 46.4 | 19.4 | 83.4 | 8.6 | 257.7 | 16.4 | 901.6 | 806.4 | 763.2 | 852.4 | 739.7 | 797.6 | 768 | 798.7 | 724.6 | 775.5 | 120.6 | 224.3 | 269.9 | 191.6 | 336.7 | 335.2 | 240.4 | 297.7 | 442.5 | 255.2
1087 | 893 | 567.5 | 227 | 265.3499 | 350.6 | 309.7 | 315.6 | 302.2 | 567.4 | 46.4 | 19.4 | 83.6 | 7.1 | 262.8 | 15.2 | 900.4 | 808.1 | 779.5 | 852.3 | 741.6 | 799.8 | 769.9 | 803 | 724.8 | 777.1 | 120.8 | 224.5 | 270.2 | 191.8 | 336.7 | 335.4 | 240.8 | 297.9 | 442.8 | 255.4
1088 | 894 | 567.1 | 226.84 | 265.1629 | 350.8 | 309.8 | 316.3 | 301.5 | 571.9 | 46.4 | 19.4 | 83.8 | 7.3 | 260.2 | 14.1 | 900.6 | 806.9 | 784.6 | 851.8 | 744.8 | 801.7 | 769.8 | 803.1 | 724.9 | 778.6 | 120.9 | 224.7 | 270.3 | 192 | 336.9 | 335.5 | 241.3 | 298 | 443.2 | 255.6
1089 | 895 | 567.4 | 226.96 | 265.3032 | 349.2 | 310 | 316.8 | 301.5 | 572 | 46.5 | 19.4 | 83.8 | 8.7 | 257.4 | 15.1 | 902.3 | 805.9 | 775.4 | 850.9 | 742.9 | 804.6 | 769.9 | 804.3 | 724.9 | 778.7 | 121.1 | 225 | 270.3 | 192.2 | 337.2 | 335.5 | 241.6 | 298.1 | 443.6 | 255.9
1090 | 896 | 566 | 226.4 | 264.6486 | 349.1 | 310.7 | 315.9 | 301.7 | 587.1 | 46.6 | 19.4 | 83.8 | 8.8 | 249.1 | 14.8 | 906.8 | 806.2 | 762.2 | 851.2 | 740.6 | 806.6 | 765.7 | 802.3 | 724.9 | 775.2 | 121.2 | 225.2 | 270.6 | 192.5 | 337.4 | 335.8 | 241.9 | 298.2 | 443.8 | 256.1
1091 | 897 | 566.5 | 226.6 | 264.8823 | 350.3 | 312.1 | 315 | 302.7 | 589.7 | 46.6 | 19.4 | 83.7 | 7.5 | 243.5 | 14.4 | 907.2 | 806.4 | 769.7 | 852.1 | 741 | 807.5 | 766.9 | 805.8 | 724.8 | 774.8 | 121.4 | 225.4 | 270.7 | 192.7 | 337.8 | 336.3 | 242.2 | 298.4 | 443.9 | 256.3
1092 | 898 | 565.1 | 226.04 | 264.2277 | 347.3 | 313.5 | 316.3 | 303.9 | 587.3 | 47.2 | 19.4 | 83.7 | 7 | 261.6 | 12.9 | 906.5 | 806.5 | 784.6 | 852.1 | 742.2 | 807.9 | 770 | 810 | 724.9 | 777.3 | 121.6 | 225.6 | 270.8 | 192.9 | 338 | 336.5 | 242.4 | 298.5 | 443.5 | 256
1093 | 899 | 565.7 | 226.28 | 264.5083 | 347.5 | 312.5 | 314.2 | 303.4 | 598.9 | 47 | 19.4 | 83.7 | 5.9 | 223.4 | 13.6 | 904 | 806.1 | 780.6 | 851.3 | 743 | 808.8 | 773.1 | 811.1 | 725.1 | 779.7 | 121.7 | 225.8 | 271.1 | 193.1 | 337.6 | 336.3 | 242.7 | 298.6 | 443.9 | 256.5
1094 | 900 | 565 | 226 | 264.181 | 345.2 | 312.9 | 315.3 | 303.6 | 620.5 | 47.4 | 19.4 | 83.9 | 6.4 | 233.2 | 13.9 | 903.5 | 807.8 | 777.8 | 850.5 | 742.1 | 810.9 | 778.8 | 815 | 725.4 | 780.2 | 121.9 | 226.1 | 271.4 | 193.3 | 337.5 | 336.2 | 243 | 298.7 | 444.1 | 256.3
1095 | 901 | 566.4 | 226.56 | 264.8356 | 344.3 | 312.9 | 317.1 | 303.5 | 631.8 | 47.5 | 19.4 | 84.1 | 7 | 246.4 | 15 | 901.8 | 807.2 | 776.5 | 849.8 | 742.9 | 812.7 | 783.1 | 815.9 | 725.7 | 782 | 122 | 226.3 | 271.7 | 193.5 | 337.3 | 336.3 | 243.3 | 298.8 | 444.2 | 256.4
1096 | 902 | 566.8 | 226.72 | 265.0226 | 346.1 | 312.1 | 316.9 | 301.8 | 641.9 | 47 | 19.4 | 84.2 | 8.6 | 244.8 | 15.8 | 900.3 | 805.9 | 790 | 849.1 | 744.9 | 813.8 | 786.3 | 815.8 | 726 | 783.3 | 122.2 | 226.5 | 271.9 | 193.8 | 337.2 | 336.2 | 243.7 | 299 | 444.9 | 257
1097 | 903 | 567.1 | 226.84 | 265.1629 | 347.9 | 312 | 316.9 | 301.1 | 658.5 | 46.7 | 19.4 | 84.3 | 9.7 | 252.5 | 13.5 | 902.4 | 806 | 797.5 | 848.4 | 745.5 | 815 | 785.4 | 817.6 | 726.4 | 782.3 | 122.3 | 226.7 | 272.5 | 194 | 337.4 | 335.9 | 244 | 299.1 | 445.6 | 257.6
1098 | 904 | 566.9 | 226.76 | 265.0694 | 346.9 | 313.3 | 316.5 | 301.3 | 658.7 | 46.7 | 19.4 | 84.3 | 12 | 263.5 | 12.7 | 903.4 | 807.1 | 803.4 | 847.9 | 747.3 | 815.2 | 784.6 | 817.3 | 726.6 | 783.7 | 122.5 | 226.9 | 272.5 | 194.2 | 337.5 | 335.7 | 244.3 | 299.1 | 446 | 257.8
1099 | 905 | 556.6 | 222.64 | 260.2533 | 343.8 | 315.4 | 318.5 | 302.6 | 663.9 | 47.4 | 19.3 | 84.3 | 12.9 | 266 | 16.3 | 902.8 | 806.6 | 810.2 | 847.6 | 748.4 | 815.3 | 784.2 | 817.3 | 726.7 | 784.7 | 122.6 | 227.1 | 272.8 | 194.4 | 337.6 | 335.6 | 244.5 | 299.2 | 445.8 | 257.4
1100 | 906 | 563.6 | 225.44 | 263.5264 | 347.6 | 314.4 | 315 | 302.9 | 672.1 | 46.9 | 19.4 | 84.2 | 12.5 | 232.6 | 20.1 | 903.7 | 807.1 | 806.2 | 847 | 749.1 | 817.7 | 785.4 | 817.2 | 726.9 | 786.7 | 122.8 | 227.4 | 273 | 194.7 | 337.7 | 335.5 | 244.9 | 299.3 | 446.5 | 258.2
1101 | 907 | 565.4 | 226.16 | 264.368 | 347.5 | 314.9 | 313.9 | 303.7 | 665.3 | 46.9 | 19.4 | 84.1 | 11.8 | 242.6 | 19.7 | 908.2 | 809 | 799.9 | 847.2 | 748.3 | 815.4 | 785.7 | 818.4 | 726.8 | 787.6 | 122.9 | 227.6 | 273.2 | 194.9 | 338 | 335.4 | 245.2 | 299.5 | 447 | 258.4
1102 | 908 | 555.4 | 222.16 | 259.6922 | 345.5 | 317.2 | 314.9 | 304.8 | 645.9 | 47.4 | 19.3 | 84.1 | 9.6 | 240.9 | 23.8 | 909.8 | 809.3 | 800.2 | 847.4 | 749.9 | 812.1 | 783.8 | 818.7 | 726.8 | 787.8 | 123.1 | 227.7 | 273.2 | 195.1 | 338.3 | 335.4 | 245.5 | 299.7 | 446.9 | 258.2
1103 | 909 | 555.9 | 222.36 | 259.926 | 346.4 | 318.9 | 314.2 | 305.6 | 626.3 | 47.3 | 19.3 | 84.1 | 9.4 | 232.7 | 22.7 | 909.5 | 808.8 | 798.2 | 847.1 | 749.9 | 810.8 | 785 | 819.3 | 726.7 | 788.2 | 123.2 | 228 | 273.4 | 195.3 | 338.4 | 335.4 | 245.7 | 299.9 | 447.1 | 258.5
1104 | 910 | 559 | 223.6 | 261.3755 | 346.8 | 318.4 | 313.8 | 305.9 | 625.2 | 47.4 | 19.3 | 84.1 | 7.1 | 243.6 | 18.3 | 909.9 | 810.7 | 787.6 | 847 | 747.1 | 810.2 | 781.3 | 814.9 | 726.6 | 784.1 | 123.4 | 228.2 | 273.7 | 195.6 | 338.4 | 335.6 | 245.9 | 300 | 447.3 | 258.7
1105 | 911 | 560.7 | 224.28 | 262.1704 | 348.8 | 317.3 | 312.4 | 305.3 | 616.9 | 47.4 | 19.3 | 84 | 7.7 | 240.6 | 19.7 | 910.1 | 810 | 782.2 | 846.8 | 747.1 | 811.7 | 786.1 | 815.6 | 726.5 | 785.5 | 123.5 | 228.4 | 273.9 | 195.8 | 338.6 | 335.8 | 246.3 | 300.2 | 447.4 | 259
1106 | 912 | 571.1 | 228.44 | 267.0332 | 351 | 316.8 | 312.1 | 304.9 | 622.7 | 47.1 | 19.4 | 83.9 | 9.5 | 247 | 21.3 | 911.6 | 811 | 775.6 | 846.7 | 745 | 815.4 | 784.6 | 816.6 | 726.7 | 785.7 | 123.7 | 228.6 | 274.2 | 196 | 338.8 | 335.7 | 246.6 | 300.2 | 447.8 | 259.6
1107 | 913 | 571.2 | 228.48 | 267.08 | 351.3 | 317 | 314.3 | 304.6 | 630.6 | 47.1 | 19.4 | 84 | 10.6 | 247.5 | 18.4 | 913.2 | 811.5 | 772 | 846.9 | 744.9 | 816.7 | 783.5 | 820.7 | 726.9 | 785.8 | 123.8 | 228.8 | 274.4 | 196.2 | 339.1 | 335.6 | 246.8 | 300.4 | 448 | 259.8
1108 | 914 | 571.9 | 228.76 | 267.4073 | 351.6 | 316.8 | 315.2 | 305.2 | 636.8 | 47.2 | 19.4 | 84 | 10.2 | 241.8 | 16.4 | 913.6 | 811 | 771.9 | 847.1 | 743.9 | 818.8 | 783.2 | 822 | 727.1 | 785.4 | 124 | 229 | 274.6 | 196.4 | 339.1 | 335.6 | 247.1 | 300.5 | 448.2 | 260
1109 | 915 | 572.6 | 229.04 | 267.7346 | 351.8 | 316 | 314.6 | 306.2 | 635.2 | 47.3 | 19.4 | 84 | 10.3 | 241.4 | 19 | 913.1 | 806.9 | 755 | 846.8 | 741.2 | 818.1 | 779.5 | 818.3 | 727.1 | 781.2 | 124.1 | 229.2 | 274.8 | 196.7 | 339.4 | 335.7 | 247.3 | 300.6 | 448.3 | 260.3
1110 | 916 | 571.9 | 228.76 | 267.4073 | 352 | 315.2 | 315.2 | 306.8 | 618.3 | 47.3 | 19.4 | 83.9 | 7.5 | 254.3 | 16.7 | 912.8 | 803.7 | 739.5 | 846.7 | 738.8 | 810.7 | 778 | 809.5 | 726.8 | 778.4 | 124.3 | 229.4 | 274.9 | 196.9 | 339.5 | 335.9 | 247.6 | 300.8 | 448.3 | 260.5
1111 | 917 | 571.1 | 228.44 | 267.0332 | 352.7 | 314.8 | 315.6 | 307.2 | 596 | 47.3 | 19.4 | 83.8 | 8.1 | 238.1 | 16.8 | 912.1 | 799.3 | 725.3 | 847 | 736 | 804.8 | 780.1 | 804.5 | 726.5 | 779.2 | 124.4 | 229.7 | 275.1 | 197.1 | 339.6 | 336.1 | 248 | 301 | 448.3 | 260.7
1112 | 918 | 570.9 | 228.36 | 266.9397 | 353.4 | 315 | 316.7 | 307.6 | 579.7 | 47.3 | 19.4 | 83.8 | 7.9 | 237.8 | 16.9 | 911.6 | 795.9 | 721.9 | 846.9 | 733.4 | 803.3 | 775.6 | 796.8 | 726.2 | 775.6 | 124.6 | 229.9 | 275.3 | 197.3 | 340 | 336.3 | 248.3 | 301.2 | 448.3 | 260.9
1113 | 919 | 571.9 | 228.76 | 267.4073 | 354.4 | 313.5 | 318.2 | 307.8 | 572.6 | 47.3 | 19.4 | 83.7 | 8.4 | 226.2 | 17.6 | 911.6 | 791.1 | 712.6 | 846.6 | 730.1 | 802.1 | 767.3 | 786.8 | 726 | 770.9 | 124.7 | 230.1 | 275.5 | 197.5 | 340 | 336.2 | 248.6 | 301.3 | 448.3 | 261.1
1114 | 920 | 571.2 | 228.48 | 267.08 | 356.4 | 311.8 | 319.2 | 309.3 | 569.8 | 47.3 | 19.4 | 83.6 | 9.4 | 252.4 | 15.5 | 911.1 | 787.8 | 695.9 | 846.1 | 728.1 | 799.8 | 761 | 777.5 | 725.9 | 767 | 124.9 | 230.3 | 275.7 | 197.7 | 340.3 | 336.2 | 248.9 | 301.3 | 448.2 | 261.3
1115 | 921 | 570.6 | 228.24 | 266.7994 | 355.9 | 310.9 | 320.2 | 309.7 | 561 | 47.2 | 19.4 | 83.8 | 9.8 | 238.9 | 16.9 | 910.9 | 785.1 | 700 | 846.6 | 726.6 | 796.5 | 755.9 | 773.4 | 725.9 | 764.8 | 125 | 230.5 | 275.8 | 197.9 | 340.4 | 336.3 | 249.2 | 301.5 | 448.2 | 261.6
1116 | 922 | 569.3 | 227.72 | 266.1916 | 355.1 | 309.9 | 321 | 310.6 | 559.7 | 47.2 | 19.4 | 84 | 9.5 | 243.9 | 16.5 | 910.7 | 784.2 | 697.1 | 847.5 | 722.7 | 800.2 | 749.5 | 770.4 | 726.2 | 762.1 | 125.2 | 230.8 | 275.9 | 198.2 | 340.4 | 336.3 | 249.4 | 301.6 | 448.1 | 261.8
1117 | 923 | 569.3 | 227.72 | 266.1916 | 357.9 | 309.8 | 321.5 | 311.1 | 560.9 | 47.3 | 19.4 | 84.2 | 8.1 | 236.8 | 19 | 910.4 | 782.7 | 704.7 | 847.6 | 720.3 | 799.8 | 745 | 767.1 | 726.5 | 759.5 | 125.3 | 231.1 | 276 | 198.4 | 340.6 | 336.4 | 249.6 | 301.7 | 448 | 262
1118 | 924 | 569.4 | 227.76 | 266.2383 | 358.5 | 309.9 | 321.6 | 310.8 | 559.5 | 47.3 | 19.4 | 84.2 | 7.5 | 239.6 | 20.4 | 910.3 | 783.2 | 712 | 846.6 | 719.9 | 803 | 745.4 | 772.9 | 727 | 759.2 | 125.5 | 231.3 | 276.3 | 198.6 | 340.3 | 336.4 | 249.8 | 301.8 | 448 | 262.3
1119 | 925 | 570.3 | 228.12 | 266.6591 | 358.6 | 310.1 | 322.9 | 311.3 | 565.6 | 47.4 | 19.4 | 84.2 | 7 | 235.9 | 18.5 | 910.3 | 780.3 | 693.3 | 845.6 | 716.5 | 798.7 | 741.8 | 767.2 | 727.2 | 755.3 | 125.7 | 231.4 | 276.5 | 198.8 | 340.1 | 336.3 | 250 | 301.9 | 447.9 | 262.5
1120 | 926 | 569.4 | 227.76 | 266.2383 | 359 | 309.1 | 323.2 | 311.3 | 561.2 | 47.4 | 19.4 | 84.2 | 7 | 241.4 | 16.6 | 910.1 | 779 | 676.2 | 845 | 713.7 | 794.1 | 739.8 | 765.4 | 727.4 | 752.9 | 125.8 | 231.6 | 276.6 | 199 | 339.9 | 336.4 | 250.2 | 302 | 447.9 | 262.7
1121 | 927 | 568.6 | 227.44 | 265.8643 | 359.1 | 308.7 | 323.7 | 311.7 | 553.8 | 47.4 | 19.4 | 84.2 | 7.2 | 239.5 | 17.9 | 909.7 | 777.4 | 681.3 | 844.7 | 712.4 | 788.7 | 739.1 | 761.4 | 727.5 | 752.5 | 125.9 | 231.8 | 276.9 | 199.2 | 340 | 336.9 | 250.5 | 302.2 | 447.8 | 262.9
1122 | 928 | 569.4 | 227.76 | 266.2383 | 359.1 | 308.7 | 323.3 | 312.5 | 552.2 | 47.4 | 19.4 | 84.3 | 8.5 | 239.4 | 17 | 909.4 | 780.8 | 700.4 | 844.4 | 712.9 | 792.7 | 743.1 | 768.8 | 728 | 754.7 | 126.1 | 232 | 277 | 199.4 | 339.8 | 337.3 | 250.7 | 302.3 | 447.8 | 263.2
1123 | 929 | 568.3 | 227.32 | 265.724 | 359.7 | 309.2 | 323.8 | 313.7 | 579.8 | 47.5 | 19.4 | 84.4 | 8.1 | 238.7 | 19.7 | 909.9 | 782.4 | 713.1 | 844.3 | 712.7 | 799.9 | 743.3 | 774.7 | 728.9 | 753.9 | 126.3 | 232.3 | 277.3 | 199.6 | 339.7 | 337.3 | 251 | 302.4 | 447.9 | 263.4
1124 | 930 | 568.8 | 227.52 | 265.9578 | 359.9 | 309.5 | 324 | 314 | 599.7 | 47.5 | 19.4 | 84.4 | 9.8 | 238.2 | 19.4 | 909.9 | 781.1 | 707.4 | 843.9 | 710.7 | 798.4 | 740.2 | 774.6 | 729.5 | 750.8 | 126.4 | 232.5 | 277.6 | 199.8 | 339.7 | 337.4 | 251.2 | 302.5 | 448 | 263.6
1125 | 931 | 568.9 | 227.56 | 266.0045 | 359.7 | 309.4 | 323.6 | 313 | 597.7 | 47.5 | 19.4 | 84.4 | 7.7 | 241.6 | 16.6 | 909 | 781.2 | 702.6 | 842.8 | 710.9 | 796.2 | 739 | 771.9 | 730 | 749.1 | 126.6 | 232.7 | 277.8 | 200 | 339.3 | 337.4 | 251.4 | 302.6 | 448.1 | 263.8
1126 | 932 | 570 | 228 | 266.5189 | 360.7 | 310.1 | 324.1 | 312.5 | 602.7 | 47.5 | 19.4 | 84.4 | 7.4 | 249 | 15.6 | 908.2 | 782.9 | 704.3 | 841.6 | 711.5 | 799.3 | 741 | 778.1 | 730.6 | 750.1 | 126.7 | 232.9 | 277.8 | 200.1 | 339.5 | 337.5 | 251.7 | 302.7 | 448.1 | 264
1127 | 933 | 569.7 | 227.88 | 266.3786 | 361 | 309.7 | 324.6 | 312.9 | 597.5 | 47.4 | 19.4 | 84.3 | 6.7 | 228.8 | 14.5 | 907 | 784.2 | 715.9 | 840.7 | 711.8 | 802.5 | 742.8 | 783.8 | 731.1 | 750.2 | 126.9 | 233.1 | 278 | 200.3 | 339.7 | 337.6 | 251.8 | 302.8 | 448.1 | 264.2
1128 | 934 | 569.9 | 227.96 | 266.4721 | 360.2 | 310.3 | 323.8 | 313.8 | 599.5 | 47.4 | 19.4 | 84.4 | 7.3 | 246.1 | 12.4 | 907.4 | 787 | 733.6 | 839.9 | 714 | 806.9 | 745 | 790.5 | 731.8 | 752.6 | 127 | 233.3 | 278.3 | 200.5 | 339.8 | 337.6 | 252.1 | 302.8 | 448.2 | 264.4
1129 | 935 | 569.6 | 227.84 | 266.3318 | 359.7 | 310.2 | 323.1 | 314.4 | 623.4 | 47.4 | 19.4 | 84.6 | 6.7 | 212.1 | 13 | 911.1 | 787 | 742.6 | 840.3 | 713.1 | 810.4 | 744.4 | 790.5 | 732.7 | 752.4 | 127.2 | 233.5 | 278.7 | 200.7 | 340 | 337.5 | 252.4 | 302.9 | 448.3 | 264.6
1130 | 936 | 569.8 | 227.92 | 266.4253 | 361.1 | 310 | 323 | 314.4 | 640.8 | 47.4 | 19.4 | 84.7 | 6.1 | 221.8 | 10.9 | 911.5 | 783.2 | 746.5 | 840.1 | 710.8 | 806.4 | 732.3 | 777.9 | 733.4 | 748.1 | 127.4 | 233.6 | 279.4 | 200.9 | 340.6 | 337.4 | 252.7 | 303 | 448.4 | 264.8
1131 | 937 | 570.1 | 228.04 | 266.5656 | 362.6 | 311 | 323.3 | 315.1 | 641 | 47.5 | 19.4 | 84.6 | 5.4 | 239.8 | 10.2 | 911.3 | 780.8 | 754.5 | 840.1 | 709.8 | 806.7 | 724.8 | 777 | 734 | 745.9 | 127.5 | 233.8 | 279.4 | 201 | 340.7 | 337.4 | 252.9 | 303.1 | 448.5 | 265.1
1132 | 938 | 569.8 | 227.92 | 266.4253 | 362.6 | 312.3 | 323.7 | 316.2 | 634.1 | 47.6 | 19.3 | 84.5 | 6.1 | 228.8 | 12.7 | 911.1 | 779.9 | 747.9 | 840 | 711.3 | 805.8 | 721.8 | 773.7 | 734.5 | 745.1 | 127.7 | 234 | 279.5 | 201.2 | 340.9 | 337.2 | 253.2 | 303.2 | 448.6 | 265.3
1133 | 939 | 569 | 227.6 | 266.0513 | 361.5 | 312.7 | 323 | 315.2 | 622.6 | 47.6 | 19.4 | 84.5 | 6.3 | 229.8 | 14.7 | 909.8 | 781.8 | 752 | 839.5 | 711.9 | 805.6 | 722.4 | 776.4 | 734.8 | 743.8 | 127.8 | 234.2 | 279.5 | 201.4 | 341.1 | 337.1 | 253.4 | 303.2 | 448.6 | 265.5
1134 | 940 | 569.7 | 227.88 | 266.3786 | 359.6 | 312.9 | 321.5 | 314.6 | 630.3 | 47.6 | 19.3 | 84.6 | 6.8 | 246.7 | 14.1 | 909 | 785.4 | 775.6 | 838.7 | 712.5 | 809.1 | 731.6 | 782.5 | 735.5 | 747.3 | 128 | 234.4 | 279.7 | 201.6 | 341 | 337 | 253.6 | 303.3 | 448.5 | 265.7
1135 | 941 | 569.2 | 227.68 | 266.1448 | 358 | 312.9 | 321.9 | 314.3 | 656.8 | 47.6 | 19.3 | 84.6 | 7.5 | 247.6 | 13.2 | 909.5 | 786.2 | 794.7 | 838.4 | 711.6 | 811.9 | 734.4 | 785.6 | 736.4 | 747.9 | 128.2 | 234.6 | 280.2 | 201.8 | 341.1 | 337 | 253.8 | 303.4 | 448.7 | 265.9
1136 | 942 | 568.9 | 227.56 | 266.0045 | 357.2 | 313.1 | 322 | 314.2 | 679 | 47.6 | 19.3 | 84.7 | 9.1 | 237.4 | 12.7 | 910.3 | 787.3 | 800.3 | 838.1 | 711.9 | 814.2 | 736.3 | 788.5 | 737.2 | 749.7 | 128.3 | 234.8 | 280.5 | 201.9 | 341.6 | 337 | 254.1 | 303.4 | 449 | 266.2
1137 | 943 | 568.9 | 227.56 | 266.0045 | 356.4 | 313.6 | 321.4 | 314.1 | 684.3 | 47.6 | 19.3 | 84.8 | 9 | 241.2 | 11.9 | 913.6 | 782.7 | 798.4 | 839.2 | 710.7 | 815.3 | 729.5 | 784.2 | 737.8 | 746.1 | 128.5 | 235 | 281.1 | 202.1 | 342.3 | 336.9 | 254.4 | 303.5 | 449.3 | 266.4
1138 | 944 | 569.6 | 227.84 | 266.3318 | 356.8 | 314.1 | 321.8 | 313.9 | 673.7 | 47.7 | 19.3 | 84.8 | 7.7 | 243.5 | 12.1 | 914 | 778.4 | 794.2 | 840.3 | 708.9 | 814.3 | 718.9 | 772.7 | 738 | 742.8 | 128.6 | 235.2 | 281.3 | 202.3 | 342.4 | 336.8 | 254.6 | 303.6 | 449.4 | 266.6
1139 | 945 | 569.2 | 227.68 | 266.1448 | 357.1 | 315 | 323.1 | 315.1 | 667.9 | 47.7 | 19.3 | 84.8 | 8 | 256.3 | 11.5 | 913.8 | 773 | 794.7 | 841 | 706.8 | 813.4 | 709.2 | 763.2 | 738.2 | 739.8 | 128.8 | 235.5 | 281.8 | 202.5 | 342.2 | 336.8 | 255 | 303.7 | 449.4 | 266.8
1140 | 946 | 569.1 | 227.64 | 266.098 | 357 | 316.6 | 324.7 | 315.2 | 667.1 | 47.7 | 19.3 | 84.6 | 7.2 | 271.5 | 9.6 | 913.1 | 768.2 | 783.4 | 841.7 | 701.8 | 810.7 | 706.4 | 755 | 738.2 | 736.5 | 129 | 235.7 | 282.2 | 202.6 | 342.5 | 337.2 | 255.2 | 303.8 | 449.4 | 267.1
1141 | 947 | 569.1 | 227.64 | 266.098 | 358.6 | 318.1 | 325.4 | 316.3 | 651.9 | 47.8 | 19.3 | 84.5 | 7.6 | 249.7 | 12.7 | 912.3 | 762.9 | 758.1 | 842.5 | 697.9 | 804.9 | 702.4 | 744.1 | 737.8 | 732.1 | 129.1 | 235.9 | 282.3 | 202.8 | 342.6 | 337.6 | 255.5 | 303.9 | 449.4 | 267.3
1142 | 948 | 568.6 | 227.44 | 265.8643 | 361.7 | 319.2 | 325.9 | 317 | 640.7 | 47.8 | 19.3 | 84.4 | 7.3 | 255.5 | 14 | 911.9 | 760.1 | 737.8 | 842.3 | 695.7 | 802.7 | 701.4 | 739.3 | 737.1 | 729.8 | 129.3 | 236.2 | 282.4 | 203 | 342.5 | 337.8 | 255.8 | 304 | 449.3 | 267.6
1143 | 949 | 569.4 | 227.76 | 266.2383 | 363 | 319.1 | 326.6 | 318.1 | 639.1 | 47.9 | 19.3 | 84.5 | 7.1 | 237.8 | 15.3 | 911.8 | 761 | 734.8 | 842.6 | 693.5 | 805.3 | 702.4 | 742.3 | 736.4 | 728.9 | 129.5 | 236.4 | 282.6 | 203.2 | 343.7 | 338 | 256.1 | 304.1 | 449.3 | 267.8
1144 | 950 | 568.7 | 227.48 | 265.911 | 364.1 | 318.7 | 326.9 | 318.4 | 650.2 | 48 | 19.3 | 84.6 | 7.9 | 238.2 | 14.4 | 910.2 | 756.1 | 726.7 | 842.4 | 689.7 | 806.1 | 699.5 | 730.5 | 736.3 | 725.6 | 129.6 | 236.7 | 283.5 | 203.3 | 344.8 | 338.2 | 256.4 | 304.2 | 449.3 | 268.1
1145 | 951 | 568.8 | 227.52 | 265.9578 | 364.7 | 319 | 327.4 | 319.3 | 645.7 | 48 | 19.3 | 84.8 | 7.3 | 237.6 | 14.6 | 909.2 | 751.4 | 716.1 | 841.9 | 687.2 | 804.8 | 694 | 718.7 | 736.7 | 723.2 | 129.8 | 236.9 | 283.9 | 203.5 | 345.8 | 338.3 | 256.7 | 304.3 | 449.4 | 268.3
1146 | 952 | 569.9 | 227.96 | 266.4721 | 366.3 | 319.9 | 328.7 | 320.1 | 652.8 | 47.9 | 19.3 | 84.9 | 6.2 | 225.8 | 13 | 909.2 | 753.1 | 721 | 842.2 | 685.2 | 808 | 698.3 | 722.6 | 736.9 | 722.8 | 130 | 237.2 | 283.8 | 203.7 | 346.1 | 338.5 | 257 | 304.5 | 449.5 | 268.6
1147 | 953 | 570 | 228 | 266.5189 | 366.2 | 321 | 329.6 | 320.8 | 658.1 | 47.9 | 19.3 | 84.9 | 5.1 | 240.5 | 12.3 | 910 | 758.9 | 728.7 | 842.3 | 686.9 | 812.7 | 700.6 | 738.7 | 737 | 725.3 | 130.1 | 237.4 | 283.8 | 203.9 | 346 | 338.8 | 257.3 | 304.6 | 449.6 | 268.8
1148 | 954 | 569.4 | 227.76 | 266.2383 | 365.6 | 320.8 | 329.4 | 320.6 | 654.4 | 47.8 | 19.3 | 84.9 | 5.6 | 245.8 | 13.6 | 909.7 | 759.3 | 717 | 841.6 | 684.1 | 808.9 | 700.2 | 743.8 | 736.9 | 724.5 | 130.3 | 237.6 | 284 | 204.1 | 345.7 | 339.5 | 257.6 | 304.8 | 449.8 | 269
1149 | 955 | 569.6 | 227.84 | 266.3318 | 364.7 | 320.2 | 329.2 | 320.1 | 638.3 | 47.8 | 19.3 | 84.9 | 7 | 233.7 | 11.5 | 909.1 | 760.6 | 724.2 | 841.1 | 684.9 | 806.5 | 700.1 | 745.6 | 736.8 | 722.7 | 130.5 | 237.9 | 284.3 | 204.2 | 345.8 | 340.3 | 257.9 | 305 | 449.8 | 269.3
1150 | 956 | 569.8 | 227.92 | 266.4253 | 363.2 | 320.3 | 328.9 | 320.2 | 637.4 | 47.8 | 19.3 | 85 | 6.5 | 257.7 | 10.2 | 908.2 | 765.7 | 754.9 | 840.1 | 689.7 | 809.8 | 702.6 | 753.7 | 737.2 | 724.1 | 130.6 | 238.1 | 284.5 | 204.4 | 345.5 | 340.4 | 258.2 | 305.1 | 449.8 | 269.6
1151 | 957 | 569.7 | 227.88 | 266.3786 | 362.1 | 319.9 | 328.1 | 320.7 | 647.5 | 47.8 | 19.3 | 85 | 6.4 | 271.9 | 8.4 | 905.8 | 769.7 | 774.8 | 838.2 | 692.5 | 812.3 | 708.4 | 761.5 | 737.6 | 727.6 | 130.8 | 238.3 | 284.8 | 204.6 | 345.4 | 340.4 | 258.3 | 305.2 | 449.9 | 269.8
1152 | 958 | 569.4 | 227.76 | 266.2383 | 361.2 | 319.8 | 327 | 320.8 | 655.5 | 47.6 | 19.3 | 84.8 | 6.4 | 266.7 | 9.3 | 904.7 | 773.5 | 771.4 | 836.4 | 694.7 | 814 | 716.3 | 770.9 | 737.4 | 730.9 | 131 | 238.6 | 284.9 | 204.8 | 345.1 | 340.8 | 258.5 | 305.3 | 450.3 | 270
1153 | 959 | 569.9 | 227.96 | 266.4721 | 360.6 | 319.9 | 326.1 | 319.2 | 659.3 | 47.5 | 19.3 | 84.7 | 6.4 | 243.7 | 8.9 | 907.6 | 776.3 | 780.7 | 835.7 | 696.2 | 813.7 | 725.1 | 775.4 | 738 | 733.1 | 131.2 | 238.8 | 285.1 | 205 | 345 | 341.1 | 258.7 | 305.4 | 450.5 | 270.2
1154 | 960 | 569.5 | 227.8 | 266.2851 | 361 | 319.6 | 325.3 | 317.2 | 654.1 | 47.5 | 19.3 | 84.8 | 7.8 | 256.8 | 11.7 | 909.3 | 774.1 | 768.4 | 835.4 | 694.2 | 811.4 | 722.2 | 772.2 | 737.7 | 729.3 | 131.3 | 239.1 | 285.4 | 205.1 | 344.9 | 341.6 | 258.9 | 305.6 | 450.7 | 270.4
1155 | 961 | 567.7 | 227.08 | 265.4434 | 360.9 | 319.4 | 324.8 | 316.3 | 644.5 | 47.6 | 19.3 | 85 | 8 | 257.7 | 14.1 | 909.5 | 768.3 | 745.4 | 835.7 | 690.6 | 806.3 | 714.2 | 760.4 | 737.2 | 726 | 131.5 | 239.4 | 285.8 | 205.3 | 344.8 | 341.8 | 259.1 | 305.7 | 450.7 | 270.7
1156 | 962 | 569.1 | 227.64 | 266.098 | 360.9 | 319 | 324.1 | 316.7 | 636.5 | 47.6 | 19.3 | 85.1 | 7.8 | 255.7 | 16.6 | 908.2 | 760.4 | 724.7 | 835.5 | 687 | 800.3 | 706.3 | 744 | 736.6 | 721.2 | 131.7 | 239.6 | 286.5 | 205.5 | 344.8 | 341.5 | 259.3 | 305.7 | 450.7 | 270.9
1157 | 963 | 570.5 | 228.2 | 266.7527 | 362.3 | 318.5 | 323.3 | 316.5 | 632.4 | 47.7 | 19.3 | 85.1 | 6.8 | 266 | 17.2 | 907 | 756 | 724.8 | 836.3 | 684.6 | 796.9 | 698.4 | 734.6 | 737 | 718.6 | 131.8 | 239.9 | 286.8 | 205.7 | 344.8 | 341.2 | 259.6 | 305.8 | 450.6 | 271.1
1158 | 964 | 571.4 | 228.56 | 267.1735 | 363.3 | 318.1 | 324.7 | 316.1 | 636.7 | 47.8 | 19.3 | 85.2 | 4.5 | 232.1 | 14.3 | 906.3 | 754.4 | 730.4 | 836.8 | 682.3 | 802.7 | 696.5 | 735.9 | 737.4 | 716.6 | 132 | 240 | 287 | 205.9 | 344.7 | 340.9 | 259.8 | 305.8 | 450.6 | 271.3
1159 | 965 | 572.7 | 229.08 | 267.7813 | 363.3 | 318.4 | 325.3 | 316.9 | 634.5 | 47.8 | 19.3 | 85.3 | 5 | 228.3 | 11.8 | 906.3 | 754.6 | 739.4 | 836.5 | 681.4 | 805.6 | 695.2 | 740.5 | 737.3 | 715.9 | 132.2 | 240.2 | 287.3 | 206 | 344.9 | 340.8 | 260 | 305.9 | 450.6 | 271.5
1160 | 966 | 573.6 | 229.44 | 268.2021 | 362.7 | 318.9 | 325.3 | 316.9 | 651.1 | 47.8 | 19.3 | 85.4 | 5 | 232.1 | 13.2 | 906.3 | 758.8 | 744.3 | 835.4 | 682.7 | 809.6 | 700.5 | 752.5 | 737.4 | 718.3 | 132.4 | 240.4 | 287.6 | 206.2 | 345.8 | 340.8 | 260.3 | 306 | 450.6 | 271.8
1161 | 967 | 573.7 | 229.48 | 268.2489 | 362.9 | 320.1 | 325.4 | 317.1 | 662.9 | 47.9 | 19.3 | 85.5 | 5.8 | 233.5 | 10.5 | 907.3 | 761.8 | 740.2 | 835.2 | 682.6 | 811.9 | 703.1 | 761 | 737.1 | 719.2 | 132.6 | 240.7 | 288 | 206.4 | 346.6 | 341.2 | 260.5 | 306.1 | 450.7 | 272
1162 | 968 | 573.7 | 229.48 | 268.2489 | 363.2 | 320.2 | 326.1 | 318.3 | 669.5 | 47.9 | 19.3 | 85.6 | 6.5 | 234.7 | 10.7 | 907.5 | 763.3 | 738.9 | 834.7 | 682.9 | 814.6 | 706.6 | 764.9 | 736.9 | 720.7 | 132.7 | 241 | 288 | 206.6 | 346.7 | 341.6 | 260.8 | 306.3 | 450.8 | 272.3
1163 | 969 | 573 | 229.2 | 267.9216 | 363.6 | 320.5 | 326.6 | 318.9 | 668.2 | 47.9 | 19.3 | 85.6 | 6.5 | 243.4 | 11.6 | 907.7 | 761.3 | 744.9 | 834.6 | 682.9 | 813.8 | 702.5 | 764 | 736.7 | 718.3 | 132.9 | 241.2 | 288.4 | 206.8 | 346.6 | 341.8 | 260.9 | 306.4 | 450.9 | 272.5
1164 | 970 | 571.7 | 228.68 | 267.3137 | 364.5 | 321.7 | 325.9 | 318.9 | 674.3 | 47.9 | 19.3 | 85.7 | 6.3 | 244.1 | 11.5 | 907.5 | 762 | 742.7 | 834.3 | 682.3 | 815.2 | 704.7 | 762.7 | 736.4 | 718.3 | 133.1 | 241.4 | 288.7 | 206.9 | 346.5 | 341.8 | 261.2 | 306.5 | 451 | 272.8
1165 | 971 | 569.5 | 227.8 | 266.2851 | 364.8 | 323.5 | 324.1 | 319.1 | 677.3 | 47.8 | 19.3 | 85.8 | 6.3 | 239.1 | 11.9 | 907.5 | 763 | 743.2 | 834.4 | 683.5 | 811.6 | 701.7 | 758.4 | 736 | 715.9 | 133.3 | 241.7 | 289 | 207.1 | 346.3 | 341.9 | 261.4 | 306.6 | 451.2 | 273
1166 | 972 | 568.5 | 227.4 | 265.8175 | 365 | 324.2 | 323.7 | 319.6 | 673.5 | 47.8 | 19.3 | 85.8 | 6.2 | 184.6 | 10 | 906.9 | 759.6 | 733.8 | 834.2 | 680.8 | 803.5 | 693.3 | 747.3 | 735.7 | 712.7 | 133.4 | 242 | 289.5 | 207.3 | 346.1 | 341.9 | 261.6 | 306.7 | 451.2 | 273.2
1167 | 973 | 568.6 | 227.44 | 265.8643 | 365.6 | 324.9 | 325.3 | 320.4 | 648.8 | 47.8 | 19.3 | 85.9 | 5.7 | 212.1 | 9.4 | 905.9 | 756.4 | 718.4 | 834.8 | 677.6 | 799.4 | 691.3 | 740.2 | 735.3 | 709.6 | 133.6 | 242.2 | 289.6 | 207.5 | 346.2 | 341.7 | 261.8 | 306.8 | 451.3 | 273.4
1168 | 974 | 568.4 | 227.36 | 265.7707 | 366.2 | 324.9 | 326.9 | 320.8 | 635.1 | 47.8 | 19.3 | 86 | 6.3 | 216.6 | 9.2 | 904.5 | 751 | 713.7 | 835.5 | 675.2 | 795.5 | 686 | 723.6 | 734.3 | 705.2 | 133.8 | 242.4 | 289.7 | 207.7 | 346.4 | 341.6 | 262.1 | 306.9 | 451.2 | 273.6
1169 | 975 | 569.8 | 227.92 | 266.4253 | 368.6 | 325.2 | 328.3 | 321.4 | 627.7 | 47.8 | 19.3 | 86.2 | 6.7 | 215.9 | 9.5 | 903.6 | 746.6 | 704 | 835.8 | 673.1 | 791.2 | 677.6 | 712.5 | 734.1 | 701.7 | 134 | 242.6 | 290.2 | 207.9 | 346.8 | 341.4 | 262.4 | 307 | 451.1 | 273.9
1170 | 976 | 570.2 | 228.08 | 266.6124 | 369.7 | 325.3 | 329.3 | 321.3 | 618.5 | 47.7 | 19.3 | 86.2 | 6.4 | 247.1 | 9 | 903.6 | 744.9 | 697.4 | 835.3 | 671.7 | 787.6 | 673.9 | 714.6 | 733.2 | 700.2 | 134.2 | 242.9 | 290.2 | 208.1 | 347.1 | 341.4 | 262.6 | 307.1 | 451 | 274.1
1171 | 977 | 569.8 | 227.92 | 266.4253 | 370.8 | 325 | 329.2 | 321.7 | 602.2 | 47.6 | 19.3 | 86.1 | 6.3 | 237.5 | 7.3 | 903.3 | 744 | 697.4 | 834.9 | 670.3 | 787.5 | 673.2 | 715.4 | 732.6 | 698 | 134.4 | 243.1 | 290.4 | 208.3 | 347.2 | 341.6 | 262.9 | 307.2 | 450.9 | 274.3
1172 | 978 | 570 | 228 | 266.5189 | 370.7 | 324.2 | 328.5 | 322 | 595.9 | 47.6 | 19.3 | 86.3 | 6.9 | 215.6 | 7.4 | 902.2 | 742.5 | 691.9 | 834.5 | 668.2 | 785.8 | 671.9 | 711.8 | 732.1 | 695.2 | 134.5 | 243.3 | 290.7 | 208.5 | 347.6 | 341.6 | 263 | 307.3 | 450.8 | 274.5
1173 | 979 | 568.9 | 227.56 | 266.0045 | 370.7 | 323.6 | 329 | 321.1 | 596.8 | 47.5 | 19.3 | 86.3 | 6.6 | 239.2 | 7.6 | 902.3 | 742.5 | 691.5 | 834.3 | 668 | 785.8 | 670.8 | 715.5 | 731.4 | 694.3 | 134.7 | 243.6 | 291 | 208.7 | 347.7 | 341.6 | 263.2 | 307.4 | 450.7 | 274.7
1174 | 980 | 569.1 | 227.64 | 266.098 | 370.3 | 323.3 | 328.8 | 320.8 | 597.1 | 47.6 | 19.3 | 86.4 | 6.8 | 257.4 | 7.6 | 902.3 | 744.3 | 699.1 | 834.1 | 667.3 | 784.8 | 666.9 | 720.1 | 730.9 | 694.1 | 134.9 | 243.8 | 291.3 | 208.9 | 347.6 | 341.5 | 263.3 | 307.5 | 450.7 | 275
1175 | 981 | 568.4 | 227.36 | 265.7707 | 371.4 | 323.3 | 329.8 | 320.5 | 591.7 | 47.7 | 19.3 | 86.3 | 7 | 273.4 | 8.7 | 903 | 749 | 716.4 | 834 | 669.4 | 787 | 671.8 | 729.3 | 730.5 | 695 | 135.1 | 244 | 291.5 | 209 | 347.2 | 341.5 | 263.5 | 307.6 | 450.7 | 275.2
1176 | 982 | 568.9 | 227.56 | 266.0045 | 370.7 | 323.3 | 331.4 | 320.5 | 601.8 | 47.7 | 19.3 | 86.3 | 7.7 | 239.7 | 8 | 902.7 | 745.6 | 715.2 | 833.4 | 665.9 | 786.5 | 666.4 | 721.2 | 729.9 | 693.4 | 135.3 | 244.3 | 292 | 209.2 | 347 | 341.1 | 263.7 | 307.6 | 450.7 | 275.4
1177 | 983 | 568.1 | 227.24 | 265.6305 | 369.6 | 323.5 | 331.6 | 321.8 | 604.2 | 47.7 | 19.3 | 86.2 | 6.7 | 220.4 | 7.4 | 902.6 | 745.7 | 716.2 | 833.2 | 665.7 | 787.5 | 663.9 | 719.3 | 729.5 | 692.3 | 135.4 | 244.5 | 291.9 | 209.4 | 346.6 | 340.9 | 263.8 | 307.7 | 450.7 | 275.6
1178 | 984 | 569 | 227.6 | 266.0513 | 369.2 | 323.9 | 330.4 | 322.1 | 619.7 | 47.7 | 19.3 | 86.2 | 5.5 | 241 | 6.8 | 903.2 | 749.1 | 725 | 832.5 | 665.9 | 793.1 | 665.9 | 725.4 | 729.1 | 694.7 | 135.6 | 244.7 | 292.3 | 209.6 | 346.6 | 340.8 | 264 | 307.7 | 450.8 | 275.8
1179 | 985 | 568.8 | 227.52 | 265.9578 | 368.7 | 324.7 | 330.7 | 322.2 | 635.9 | 47.7 | 19.3 | 86.1 | 5.5 | 238.3 | 8 | 903.1 | 751.6 | 728.2 | 831.3 | 666.5 | 798.1 | 667.6 | 733.4 | 728.9 | 696.2 | 135.8 | 244.9 | 292.6 | 209.8 | 347.1 | 340.9 | 264.2 | 307.8 | 450.9 | 276
1180 | 986 | 568.7 | 227.48 | 265.911 | 368.5 | 325.3 | 330.5 | 323.1 | 644.6 | 47.8 | 19.3 | 86.2 | 6.8 | 240 | 10.5 | 903.3 | 752.6 | 727.6 | 830.3 | 666.1 | 798.5 | 671.1 | 738.4 | 728.6 | 695.9 | 136 | 245 | 293 | 210 | 347.3 | 341.2 | 264.5 | 307.9 | 451.2 | 276.2
1181 | 987 | 568.8 | 227.52 | 265.9578 | 368.3 | 325.5 | 330 | 323.6 | 646.1 | 47.8 | 19.3 | 86.3 | 6.9 | 241.4 | 13.2 | 903.5 | 759.5 | 728.9 | 829.7 | 669.5 | 799.7 | 682 | 749.5 | 728.4 | 700.7 | 136.2 | 245.2 | 292.9 | 210.2 | 347.6 | 341.4 | 264.7 | 308.1 | 451.3 | 276.4
1182 | 988 | 568.6 | 227.44 | 265.8643 | 367.6 | 325.7 | 330.3 | 323.8 | 641 | 47.9 | 19.3 | 86.3 | 6.4 | 251.7 | 12.7 | 904.1 | 763.2 | 748 | 829.2 | 672.1 | 799.3 | 685.6 | 758.8 | 728.1 | 701.5 | 136.4 | 245.5 | 293 | 210.4 | 347.8 | 341.4 | 264.8 | 308.2 | 451.3 | 276.6
1183 | 989 | 567.9 | 227.16 | 265.537 | 367.6 | 325.8 | 329.6 | 323.1 | 646.9 | 47.9 | 19.3 | 86.4 | 6.2 | 245.4 | 11.3 | 904.3 | 766.8 | 770.9 | 828.4 | 675.3 | 803.2 | 691.3 | 765.6 | 728.2 | 705.3 | 136.6 | 245.7 | 293.3 | 210.6 | 347.8 | 341.4 | 265 | 308.3 | 451.4 | 276.8
1184 | 990 | 567.8 | 227.12 | 265.4902 | 367.4 | 325.3 | 328.6 | 322.9 | 659.9 | 48 | 19.2 | 86.4 | 5 | 258.4 | 9.4 | 904.5 | 770.3 | 780.2 | 827.7 | 678.6 | 806.2 | 696.7 | 771.6 | 728.3 | 708.5 | 136.7 | 246 | 293.5 | 210.8 | 347.7 | 341.4 | 265.1 | 308.4 | 451.7 | 277
1185 | 991 | 568 | 227.2 | 265.5837 | 366.8 | 325.3 | 327.5 | 321.9 | 657.5 | 48.1 | 19.2 | 86.4 | 4.9 | 233.2 | 8.1 | 905.3 | 773.5 | 776.8 | 827.2 | 681.1 | 806.6 | 703.9 | 775.7 | 728.5 | 710.3 | 136.9 | 246.2 | 293.6 | 211 | 347.6 | 341.3 | 265.3 | 308.5 | 452 | 277.2
1186 | 992 | 568.7 | 227.48 | 265.911 | 365.7 | 325.6 | 326.3 | 321.8 | 655.6 | 48.3 | 19.2 | 86.3 | 5.2 | 238.5 | 7.7 | 905.5 | 776.3 | 782.4 | 826.7 | 683.3 | 808.4 | 710.5 | 780 | 728.7 | 712.3 | 137.1 | 246.4 | 293.7 | 211.2 | 347.2 | 341.4 | 265.4 | 308.6 | 452.2 | 277.4
1187 | 993 | 569.2 | 227.68 | 266.1448 | 365.2 | 325.5 | 325 | 322.3 | 652.5 | 48.4 | 19.2 | 86.2 | 7.1 | 219.5 | 7.7 | 907.5 | 778 | 780.2 | 827.1 | 684 | 810.3 | 715.7 | 783.7 | 728.6 | 714.4 | 137.3 | 246.6 | 293.9 | 211.4 | 347.1 | 341.4 | 265.6 | 308.7 | 452.3 | 277.6
1188 | 994 | 569 | 227.6 | 266.0513 | 364.2 | 325.3 | 323.8 | 323.2 | 657 | 48.5 | 19.2 | 86.2 | 7.8 | 225.2 | 9.5 | 909.9 | 772.8 | 779.1 | 827.7 | 682.5 | 810.5 | 711.9 | 774.1 | 728.3 | 712.3 | 137.5 | 246.9 | 294.4 | 211.6 | 347.3 | 341.2 | 265.8 | 308.8 | 452.4 | 277.8
1189 | 995 | 568.8 | 227.52 | 265.9578 | 364 | 324.9 | 322.1 | 322.2 | 661.7 | 48.5 | 19.2 | 86.2 | 9.1 | 209.5 | 12.4 | 909.5 | 770.4 | 794.7 | 828.2 | 684.4 | 811 | 706.9 | 766.1 | 728.5 | 710.9 | 137.7 | 247.2 | 294.8 | 211.7 | 347.8 | 341.2 | 266 | 308.8 | 452.4 | 278
1190 | 996 | 567.9 | 227.16 | 265.537 | 364.2 | 325.2 | 323.4 | 321.9 | 667.5 | 48.6 | 19.2 | 86.3 | 8.4 | 200.5 | 11.8 | 907.4 | 772.8 | 807.4 | 827.3 | 689.3 | 811.4 | 706.4 | 771 | 728.7 | 713.3 | 137.9 | 247.4 | 294.8 | 211.9 | 347.8 | 341.3 | 266.2 | 309 | 452.6 | 278.2
1191 | 997 | 568.7 | 227.48 | 265.911 | 363.9 | 326.8 | 325.1 | 322.2 | 665.1 | 48.6 | 19.2 | 86.5 | 6.1 | 198.3 | 9.4 | 906.4 | 774.1 | 803.1 | 827.1 | 691.3 | 810 | 714 | 775.5 | 728.8 | 717.9 | 138.1 | 247.7 | 294.9 | 212.1 | 347.7 | 341.6 | 266.4 | 309.2 | 453.1 | 278.4
1192 | 998 | 569.5 | 227.8 | 266.2851 | 363.6 | 327 | 324.9 | 322.6 | 663.1 | 48.6 | 19.2 | 86.6 | 6.3 | 246.7 | 9.4 | 910 | 776.4 | 785.5 | 827.5 | 690.4 | 809.4 | 720.3 | 781.5 | 728.6 | 719.1 | 138.3 | 248 | 295.1 | 212.3 | 347.7 | 341.6 | 266.6 | 309.2 | 453.5 | 278.6
1193 | 999 | 569.3 | 227.72 | 266.1916 | 363.9 | 326.1 | 323.8 | 323.2 | 663.9 | 48.7 | 19.2 | 86.7 | 6.9 | 234.9 | 11.6 | 909 | 777.6 | 772.7 | 827.3 | 689.8 | 810.7 | 728 | 785.6 | 728.5 | 721.4 | 138.5 | 248.2 | 295.3 | 212.5 | 347.7 | 341.6 | 266.7 | 309.3 | 453.7 | 278.8
1194 | 1000 | 569.3 | 227.72 | 266.1916 | 364 | 325.2 | 323.4 | 322.9 | 654.6 | 48.7 | 19.2 | 86.8 | 8.2 | 229.4 | 15.1 | 912 | 775.6 | 765.5 | 828.4 | 688.6 | 806.8 | 733 | 784.7 | 728.4 | 720.2 | 138.6 | 248.4 | 295.5 | 212.7 | 347.8 | 341.9 | 266.9 | 309.5 | 453.9 | 279
1195 | 1001 | 568.9 | 227.56 | 266.0045 | 363.6 | 324.3 | 323.8 | 323.1 | 629.3 | 48.7 | 19.2 | 86.9 | 8.6 | 233.9 | 12.6 | 912.5 | 771.5 | 753.1 | 829.4 | 687.6 | 800.6 | 731 | 778.4 | 728.2 | 718.1 | 138.8 | 248.6 | 295.4 | 212.9 | 347.7 | 342.3 | 267.1 | 309.6 | 453.9 | 279.3
1196 | 1002 | 568.8 | 227.52 | 265.9578 | 364.5 | 323.7 | 323.4 | 322.8 | 608.9 | 48.8 | 19.2 | 86.9 | 7.9 | 253.5 | 11.2 | 911.7 | 771.5 | 753.9 | 829.1 | 688 | 800.5 | 732.1 | 782.3 | 728 | 719.3 | 139 | 248.8 | 295.5 | 213.1 | 347.2 | 342.5 | 267.3 | 309.8 | 453.8 | 279.5
1197 | 1003 | 568.3 | 227.32 | 265.724 | 364.7 | 323.1 | 323.6 | 321.5 | 603.4 | 48.8 | 19.2 | 86.9 | 7.4 | 240.7 | 11.6 | 911.5 | 774.7 | 771.5 | 829.2 | 690.2 | 805 | 735.8 | 786.3 | 728.2 | 721.9 | 139.2 | 249 | 295.6 | 213.2 | 347.2 | 342.6 | 267.5 | 309.9 | 453.7 | 279.7
1198 | 1004 | 568.9 | 227.56 | 266.0045 | 363.8 | 322.4 | 323.4 | 319.7 | 610.9 | 48.9 | 19.2 | 86.8 | 5.5 | 243.6 | 14.2 | 910.6 | 777 | 790.5 | 829 | 694 | 807.7 | 737.2 | 789.1 | 728.3 | 725.3 | 139.4 | 249.2 | 295.7 | 213.4 | 347.2 | 342.6 | 267.6 | 310 | 453.8 | 279.9
1199 | 1005 | 568.7 | 227.48 | 265.911 | 362.2 | 322.1 | 323.6 | 319.7 | 631.7 | 48.9 | 19.2 | 86.8 | 5.9 | 249.6 | 15.7 | 913.2 | 780.2 | 798.9 | 829.7 | 695.2 | 813.4 | 737.9 | 790.9 | 728.4 | 726.9 | 139.6 | 249.4 | 296.1 | 213.6 | 347.1 | 342.5 | 267.7 | 310 | 454.2 | 280
1200 | 1006 | 568.6 | 227.44 | 265.8643 | 361.3 | 322.1 | 323.7 | 318.5 | 650.3 | 48.9 | 19.2 | 86.8 | 6 | 236.2 | 14.4 | 914.9 | 781.5 | 794.2 | 830.7 | 696 | 816.9 | 740.9 | 794.4 | 728.5 | 727.7 | 139.8 | 249.7 | 296.5 | 213.8 | 347.2 | 342.4 | 267.9 | 310.1 | 454.5 | 280.2
1201 | 1007 | 568.3 | 227.32 | 265.724 | 360.7 | 322.2 | 323.6 | 317.6 | 650.7 | 48.9 | 19.2 | 87 | 7.3 | 251.7 | 14.5 | 915.5 | 783.9 | 796.6 | 830.4 | 698.8 | 812.5 | 741.7 | 797.2 | 728.3 | 729.6 | 140 | 249.9 | 296.5 | 214 | 347.1 | 342.6 | 268.1 | 310.2 | 454.7 | 280.4
1202 | 1008 | 568.4 | 227.36 | 265.7707 | 361.2 | 322.7 | 323.4 | 318.2 | 633.6 | 48.9 | 19.2 | 87.2 | 7.5 | 234 | 13.5 | 916 | 785.8 | 791.9 | 830.9 | 700.6 | 810.9 | 740.7 | 799 | 728.2 | 731.1 | 140.2 | 250.1 | 296.3 | 214.1 | 346.8 | 342.6 | 268.2 | 310.3 | 454.7 | 280.6
1203 | 1009 | 568.3 | 227.32 | 265.724 | 361.4 | 322.7 | 322.8 | 318.7 | 640 | 48.9 | 19.2 | 87.3 | 8 | 224.4 | 11.5 | 916 | 785.5 | 791.9 | 830.6 | 701.6 | 815.7 | 743 | 799.1 | 728.3 | 733.4 | 140.4 | 250.3 | 296.6 | 214.3 | 346.6 | 342.5 | 268.4 | 310.4 | 454.9 | 280.8
1204 | 1010 | 568.5 | 227.4 | 265.8175 | 361.9 | 322.6 | 321.7 | 318.2 | 654.1 | 48.9 | 19.2 | 87.5 | 8.8 | 239.4 | 14 | 917.3 | 785.8 | 782.5 | 831.2 | 701.7 | 819.5 | 742.8 | 800.6 | 728.5 | 734 | 140.6 | 250.5 | 296.9 | 214.5 | 346.3 | 342.4 | 268.5 | 310.4 | 455.1 | 281
1205 | 1011 | 568.2 | 227.28 | 265.6772 | 361.9 | 322.2 | 321.2 | 316.3 | 651.7 | 48.9 | 19.2 | 87.6 | 7.5 | 235.9 | 15.6 | 918.2 | 782.5 | 777.8 | 832.1 | 700.5 | 815.1 | 742.9 | 800.2 | 728.5 | 732.5 | 140.8 | 250.6 | 297.2 | 214.7 | 345.9 | 342.1 | 268.7 | 310.5 | 455.2 | 281.2
1206 | 1012 | 567.7 | 227.08 | 265.4434 | 362.4 | 321.4 | 320.5 | 315.1 | 646.9 | 48.8 | 19.2 | 87.6 | 6.8 | 241.6 | 15 | 918.9 | 780.8 | 762.1 | 832.4 | 699.3 | 814.4 | 743 | 796.2 | 728.5 | 732.6 | 141.1 | 250.9 | 297.4 | 214.9 | 345.6 | 342 | 268.9 | 310.5 | 455.3 | 281.3
1207 | 1013 | 568.7 | 227.48 | 265.911 | 362.8 | 321 | 319.5 | 314.3 | 631.8 | 48.8 | 19.2 | 87.7 | 6.9 | 236.8 | 13.1 | 919.2 | 775.5 | 756.2 | 833 | 697.6 | 813 | 737 | 789.8 | 728.5 | 729.6 | 141.3 | 251 | 297.4 | 215.1 | 344.9 | 341.8 | 269 | 310.6 | 455.3 | 281.6
1208 | 1014 | 568.3 | 227.32 | 265.724 | 362.7 | 321.4 | 318.8 | 314.9 | 624.5 | 48.8 | 19.2 | 87.8 | 5.6 | 256 | 11.9 | 918.4 | 769.8 | 752.2 | 833.6 | 695.6 | 813.7 | 735.5 | 783.2 | 728.5 | 728.4 | 141.5 | 251.2 | 297.6 | 215.3 | 345 | 341.7 | 269.2 | 310.7 | 455.2 | 281.8
1209 | 1015 | 567.7 | 227.08 | 265.4434 | 363.8 | 321.5 | 319.6 | 316.3 | 620.3 | 48.8 | 19.2 | 87.8 | 6.2 | 251.6 | 11.6 | 917.9 | 768.8 | 752.1 | 834.3 | 692.8 | 812.2 | 733.5 | 781.6 | 728.4 | 726.6 | 141.7 | 251.4 | 297.7 | 215.4 | 344.9 | 341.5 | 269.3 | 310.7 | 455.1 | 282
1210 | 1016 | 568.2 | 227.28 | 265.6772 | 363.7 | 322.4 | 320.9 | 316.4 | 623.7 | 48.7 | 19.2 | 87.7 | 6.4 | 244.5 | 11.1 | 917.2 | 772.1 | 749.7 | 834.5 | 693.1 | 813.9 | 739.2 | 788 | 728.5 | 729.4 | 141.9 | 251.6 | 297.8 | 215.6 | 345.1 | 341.4 | 269.5 | 310.8 | 455.1 | 282.2
1211 | 1017 | 568 | 227.2 | 265.5837 | 362.3 | 322.4 | 322.1 | 315.8 | 630.6 | 48.7 | 19.2 | 87.7 | 6.1 | 251.6 | 11.7 | 918 | 774.5 | 754.5 | 835.9 | 692.1 | 817 | 741.4 | 791.4 | 728.6 | 730.1 | 142.1 | 251.9 | 297.9 | 215.8 | 344.9 | 341.4 | 269.7 | 310.9 | 455.1 | 282.4
1212 | 1018 | 567.7 | 227.08 | 265.4434 | 362.7 | 321.6 | 322.4 | 315.8 | 640.9 | 48.7 | 19.2 | 87.8 | 5.7 | 254.3 | 10.1 | 918.3 | 775.7 | 761.9 | 835.7 | 694.3 | 818.6 | 743.5 | 792.6 | 728.6 | 731.9 | 142.3 | 252 | 298.1 | 216 | 344.6 | 341.4 | 269.8 | 310.9 | 455.2 | 282.5
1213 | 1019 | 568 | 227.2 | 265.5837 | 363.1 | 321.6 | 322 | 315.6 | 643.5 | 48.7 | 19.2 | 87.8 | 5.8 | 274.2 | 9.1 | 918.7 | 774 | 740.9 | 836.3 | 690.9 | 815.6 | 739.9 | 788.4 | 728.6 | 729.6 | 142.5 | 252.2 | 298.4 | 216.2 | 344.3 | 341.3 | 270 | 310.9 | 455.3 | 282.7
1214 | 1020 | 567.7 | 227.08 | 265.4434 | 363.3 | 321.2 | 322.7 | 315.6 | 631.3 | 48.7 | 19.2 | 87.9 | 6.3 | 251.4 | 9.8 | 918.1 | 777.1 | 746.9 | 836.8 | 692.3 | 815.8 | 743.8 | 793.2 | 728.6 | 731.9 | 142.7 | 252.4 | 298.5 | 216.4 | 343.9 | 341.3 | 270.2 | 311 | 455.3 | 282.9
1215 | 1021 | 568.4 | 227.36 | 265.7707 | 363.5 | 320.8 | 323.3 | 315 | 633.3 | 48.8 | 19.2 | 87.9 | 6.5 | 260.6 | 10.1 | 916.1 | 778.6 | 746.8 | 836.2 | 693.5 | 816.7 | 748.1 | 795.3 | 728.6 | 734.6 | 142.9 | 252.6 | 298.6 | 216.6 | 343.6 | 341.3 | 270.4 | 311.1 | 455.3 | 283.1
1216 | 1022 | 567.7 | 227.08 | 265.4434 | 363.5 | 320.4 | 322.7 | 314.8 | 638.8 | 48.8 | 19.2 | 88 | 6.2 | 269.8 | 10.7 | 916.6 | 779.6 | 753.2 | 836.2 | 694 | 819 | 753.4 | 797.9 | 728.8 | 735.5 | 143.1 | 252.8 | 299 | 216.7 | 343.7 | 341.3 | 270.5 | 311.1 | 455.5 | 283.3
1217 | 1023 | 567.2 | 226.88 | 265.2096 | 363.4 | 320.2 | 322.3 | 315.2 | 637.9 | 48.8 | 19.2 | 88.1 | 6.3 | 238.5 | 9.5 | 917.8 | 782 | 768.2 | 836.6 | 696.7 | 817.3 | 756 | 802.5 | 729.1 | 739 | 143.4 | 252.9 | 299 | 216.9 | 343.8 | 341.4 | 270.7 | 311.2 | 455.7 | 283.5
1218 | 1024 | 567.7 | 227.08 | 265.4434 | 362.7 | 320.6 | 323.3 | 315.4 | 629.8 | 48.9 | 19.2 | 88.3 | 6.9 | 254.5 | 9.6 | 918.9 | 782.9 | 780.1 | 837.2 | 700.6 | 810.7 | 757.4 | 799.9 | 729.1 | 742.1 | 143.6 | 253.2 | 299 | 217.1 | 343.7 | 341.6 | 270.9 | 311.4 | 455.9 | 283.7
1219 | 1025 | 567.8 | 227.12 | 265.4902 | 362.7 | 321.2 | 323.5 | 315.7 | 614.2 | 48.9 | 19.2 | 88.3 | 6.6 | 255.2 | 9.8 | 918.3 | 782.1 | 784.7 | 836.9 | 703.1 | 802.8 | 758.3 | 796 | 729.1 | 744.1 | 143.8 | 253.4 | 299.1 | 217.3 | 341.9 | 341.9 | 271.3 | 311.5 | 456.2 | 283.8
1220 | 1026 | 567.7 | 227.08 | 265.4434 | 363.1 | 321.2 | 323 | 314.9 | 617.5 | 48.9 | 19.2 | 88.5 | 7.3 | 228.7 | 8.5 | 917.2 | 782.7 | 769.9 | 836.6 | 703.3 | 806 | 758.7 | 797.4 | 729.1 | 744.3 | 144 | 253.6 | 299.2 | 217.5 | 340.2 | 342.2 | 271.7 | 311.6 | 456.6 | 284
1221 | 1027 | 568.1 | 227.24 | 265.6305 | 363.2 | 321 | 324 | 313.7 | 627.4 | 48.9 | 19.2 | 88.5 | 7.1 | 265.3 | 8.6 | 917.1 | 785.5 | 769.5 | 836.6 | 704.8 | 810.6 | 760.9 | 799.8 | 729.5 | 745.9 | 144.2 | 253.7 | 299.4 | 217.6 | 338.3 | 342.6 | 272.1 | 311.8 | 456.7 | 284.2
1222 | 1028 | 568.7 | 227.48 | 265.911 | 363.2 | 322.1 | 324.3 | 313.3 | 648.2 | 48.9 | 19.2 | 88.5 | 7.8 | 233.8 | 9.9 | 915.8 | 784.8 | 770.2 | 836.5 | 707.3 | 812.7 | 763.2 | 802 | 729.9 | 748.5 | 144.4 | 253.8 | 299.7 | 217.8 | 336.7 | 342.9 | 272.6 | 311.9 | 456.9 | 284.4
1223 | 1029 | 568.4 | 227.36 | 265.7707 | 363.4 | 323 | 323.8 | 313.3 | 647.5 | 49 | 19.2 | 88.4 | 8.3 | 257.7 | 10 | 915 | 785.1 | 776.1 | 836.9 | 708.9 | 804.4 | 764.6 | 800.2 | 730.1 | 750.4 | 144.7 | 254 | 299.8 | 218 | 335.1 | 343.4 | 273.1 | 312 | 457.1 | 284.6
1224 | 1030 | 568.7 | 227.48 | 265.911 | 363 | 322.6 | 322.6 | 314 | 628.7 | 49.1 | 19.2 | 88.4 | 8.4 | 263.9 | 10.9 | 913.3 | 784.1 | 794.7 | 837 | 712.9 | 800.4 | 761.8 | 800.6 | 730.1 | 752 | 144.9 | 254.1 | 299.8 | 218.1 | 333.3 | 343.7 | 273.5 | 312 | 457.3 | 284.8
1225 | 1031 | 568.6 | 227.44 | 265.8643 | 362.6 | 322.9 | 321.6 | 313.6 | 621.4 | 49 | 19.2 | 88.4 | 9.1 | 262.7 | 11.2 | 911 | 783.7 | 804.8 | 837.1 | 715.5 | 802.4 | 763.4 | 799.5 | 730.5 | 754.5 | 145.1 | 254.3 | 299.9 | 218.3 | 331.9 | 343.8 | 273.9 | 312.2 | 457.6 | 284.9
1226 | 1032 | 568.3 | 227.32 | 265.724 | 361.3 | 323.8 | 320.9 | 312.3 | 621.9 | 49 | 19.1 | 88.5 | 9.4 | 236.6 | 12.2 | 908.8 | 783.1 | 820 | 836.7 | 718.4 | 804.2 | 762.8 | 797.9 | 730.8 | 755.9 | 145.3 | 254.5 | 300.1 | 218.4 | 330.8 | 343.9 | 274.3 | 312.2 | 457.9 | 285.1
1227 | 1033 | 568.6 | 227.44 | 265.8643 | 360.5 | 325.6 | 319.7 | 311.2 | 623.8 | 49 | 19.1 | 88.5 | 8.8 | 246.9 | 14.2 | 908.2 | 782.5 | 820.9 | 836.3 | 719.3 | 806.9 | 764.5 | 797.2 | 731.2 | 756.3 | 145.5 | 254.6 | 300.3 | 218.6 | 329.6 | 344.2 | 274.7 | 312.3 | 458.3 | 285.3
1228 | 1034 | 568.6 | 227.44 | 265.8643 | 359.8 | 326.2 | 319.5 | 310.2 | 638.1 | 49.1 | 19.1 | 88.5 | 8.7 | 240.2 | 12.8 | 908.9 | 783.9 | 828.7 | 836.4 | 720.9 | 809.6 | 764.1 | 796.8 | 731.6 | 757.7 | 145.7 | 254.8 | 300.5 | 218.8 | 328.7 | 344.7 | 275.2 | 312.4 | 458.6 | 285.5
1229 | 1035 | 568.4 | 227.36 | 265.7707 | 358.9 | 327.3 | 318.9 | 310.3 | 650.9 | 49.1 | 19.2 | 88.5 | 6.2 | 240.9 | 13.2 | 912.2 | 785.6 | 821.1 | 837.5 | 721.4 | 810.3 | 763.7 | 799.2 | 732.1 | 759.8 | 146 | 255 | 300.6 | 219 | 328 | 345 | 275.6 | 312.5 | 458.8 | 285.7
1230 | 1036 | 568.5 | 227.4 | 265.8175 | 358.2 | 328.9 | 318.1 | 311.3 | 641.3 | 49.2 | 19.2 | 88.4 | 7 | 245.7 | 17.7 | 912.6 | 787.3 | 819.3 | 838.1 | 722.8 | 808 | 763.2 | 802.6 | 732.2 | 761.6 | 146.2 | 255.1 | 300.8 | 219.2 | 327.3 | 345.2 | 276 | 312.6 | 459 | 285.8
1231 | 1037 | 568.3 | 227.32 | 265.724 | 357.6 | 330.5 | 316.9 | 312 | 634.6 | 49.2 | 19.1 | 88.3 | 6.9 | 244.4 | 18 | 914.5 | 789.9 | 812.5 | 838.6 | 721.4 | 808.5 | 765.6 | 804.3 | 732.5 | 761.3 | 146.4 | 255.4 | 301 | 219.3 | 326.2 | 345.4 | 276.4 | 312.8 | 459.2 | 286
1232 | 1038 | 568 | 227.2 | 265.5837 | 357.8 | 332 | 316.4 | 312.4 | 627.8 | 49.3 | 19.2 | 88.1 | 6.7 | 247.3 | 18.2 | 916.3 | 791.4 | 814.3 | 839.7 | 720.7 | 808.8 | 766.1 | 807.5 | 732.9 | 762.6 | 146.6 | 255.6 | 301.2 | 219.5 | 325 | 345.5 | 276.8 | 312.9 | 459.2 | 286.2
1233 | 1039 | 568 | 227.2 | 265.5837 | 357.6 | 333.8 | 317.1 | 311.6 | 641.9 | 49.4 | 19.2 | 88.1 | 6.7 | 239.6 | 17.5 | 914.4 | 791.7 | 813.3 | 840.1 | 721.6 | 813.8 | 765.8 | 809.3 | 733.3 | 763.3 | 146.8 | 255.7 | 301.3 | 219.7 | 324.1 | 345.6 | 277.3 | 312.9 | 459.2 | 286.4
1234 | 1040 | 568.1 | 227.24 | 265.6305 | 357.4 | 333.9 | 317.4 | 312.2 | 643.4 | 49.4 | 19.2 | 88.1 | 6.2 | 240 | 15.9 | 910.7 | 790.6 | 809.1 | 839.9 | 722.4 | 814.9 | 769.9 | 810 | 733.7 | 763.9 | 147.1 | 255.9 | 301.5 | 219.9 | 322.8 | 345.7 | 277.5 | 313 | 459.3 | 286.6
1235 | 1041 | 568.4 | 227.36 | 265.7707 | 357.3 | 334.1 | 318 | 313.1 | 631.5 | 49.3 | 19.1 | 88.2 | 6.3 | 239.7 | 15.2 | 908.3 | 788.9 | 809.7 | 839.6 | 723.1 | 814.2 | 770.1 | 811.4 | 733.8 | 765.7 | 147.3 | 256.1 | 301.7 | 220.1 | 321.5 | 345.7 | 278 | 313 | 459.3 | 286.8
1236 | 1042 | 568.1 | 227.24 | 265.6305 | 357.1 | 334.5 | 317.8 | 313.6 | 640.9 | 49.2 | 19.1 | 88.4 | 6.8 | 249.9 | 14.1 | 906.6 | 787.6 | 818.1 | 839.4 | 724.2 | 815.3 | 769.8 | 811 | 733.9 | 767.5 | 147.5 | 256.2 | 301.9 | 220.3 | 320.5 | 345.7 | 278.4 | 313.2 | 459.4 | 287
1237 | 1043 | 567.6 | 227.04 | 265.3967 | 357.1 | 333.9 | 318 | 313.7 | 653.7 | 49.2 | 19.1 | 88.5 | 6.9 | 256.4 | 15.5 | 906.3 | 787.8 | 816.2 | 839.7 | 728.2 | 812.4 | 767.8 | 809.3 | 734 | 768.9 | 147.7 | 256.3 | 302.1 | 220.5 | 319.6 | 345.9 | 278.9 | 313.2 | 459.6 | 287.1
1238 | 1044 | 567.7 | 227.08 | 265.4434 | 356.8 | 333.9 | 318.9 | 313.5 | 639.3 | 49.2 | 19.1 | 88.5 | 6.9 | 250 | 14.6 | 907.5 | 787.7 | 822.4 | 840.4 | 730.5 | 805.6 | 765.7 | 811.4 | 733.8 | 769.6 | 147.9 | 256.5 | 302 | 220.7 | 318.5 | 346.1 | 279.2 | 313.4 | 459.9 | 287.3
1239 | 1045 | 568.1 | 227.24 | 265.6305 | 356.5 | 335.1 | 319.3 | 313.5 | 639.3 | 49.2 | 19.1 | 88.4 | 5.6 | 250.4 | 13.6 | 905.9 | 786.2 | 829.6 | 840.3 | 733.5 | 809.2 | 765.8 | 808.3 | 734 | 770.7 | 148.2 | 256.7 | 302.3 | 220.9 | 317.8 | 346.6 | 279.6 | 313.5 | 460.3 | 287.5
1240 | 1046 | 567.7 | 227.08 | 265.4434 | 356.3 | 336.2 | 320.3 | 313.3 | 647.7 | 49.2 | 19.1 | 88.4 | 5.9 | 251.7 | 13.4 | 905.9 | 786.2 | 831.4 | 840.6 | 735.8 | 809.5 | 763.7 | 807.1 | 734.1 | 771.9 | 148.4 | 256.9 | 302.4 | 221.1 | 317 | 346.7 | 280 | 313.6 | 460.7 | 287.7
1241 | 1047 | 542.8 | 217.12 | 253.8008 | 350.1 | 339 | 325.1 | 315.3 | 633.3 | 50.3 | 18.9 | 88.5 | 6.6 | 247.1 | 13.2 | 909.3 | 787.1 | 811.7 | 842 | 735.4 | 805.9 | 761.5 | 808.6 | 734 | 772.1 | 148.6 | 257 | 302.4 | 221.2 | 316.1 | 347 | 280.2 | 313.7 | 460.3 | 286.8
1242 | 1048 | 547.5 | 219 | 255.9984 | 351.3 | 339.1 | 323.8 | 314.4 | 619.2 | 50 | 18.9 | 88.5 | 6.5 | 230.7 | 10.4 | 910.7 | 790.1 | 812.7 | 842.9 | 735.2 | 800.9 | 760.9 | 809.6 | 733.7 | 771.5 | 148.8 | 257.2 | 302.5 | 221.4 | 315.5 | 347.4 | 280.6 | 313.9 | 460.8 | 287.3
1243 | 1049 | 541.8 | 216.72 | 253.3332 | 350.9 | 339.4 | 323.2 | 315 | 608.1 | 50 | 18.9 | 88.6 | 6 | 242.2 | 7.4 | 911.8 | 788.4 | 814.1 | 843.6 | 737.1 | 800.1 | 760.1 | 806.7 | 733.6 | 773 | 149 | 257.4 | 302.8 | 221.6 | 314.9 | 347.9 | 281 | 314.1 | 461 | 287.4
1244 | 1050 | 568 | 227.2 | 265.5837 | 355.8 | 338.4 | 318.6 | 313.2 | 604.5 | 49.1 | 19.1 | 88.5 | 5.5 | 245.2 | 7.2 | 914.5 | 789.3 | 805.4 | 845.4 | 737.8 | 794.1 | 757.2 | 802.3 | 733.5 | 773.1 | 149.3 | 257.6 | 302.9 | 221.8 | 314.1 | 348.5 | 281.5 | 314.3 | 461.9 | 288.4
1245 | 1051 | 570.7 | 228.28 | 266.8462 | 356.7 | 338.5 | 319 | 312.8 | 594.6 | 49.2 | 19.1 | 88.4 | 6.2 | 233.9 | 7.9 | 914.8 | 789.7 | 812.2 | 846.4 | 741.8 | 791.7 | 757 | 803.2 | 733.5 | 773.9 | 149.5 | 257.8 | 303 | 222 | 313.6 | 349.1 | 281.9 | 314.4 | 462.2 | 288.6
1246 | 1052 | 572.8 | 229.12 | 267.8281 | 356.4 | 340 | 319 | 313 | 590.7 | 49.2 | 19.1 | 88.3 | 6 | 217.1 | 8.8 | 915.5 | 789 | 817.7 | 847.9 | 744 | 794.4 | 755.7 | 803.4 | 733.5 | 775.1 | 149.7 | 258 | 303.1 | 222.1 | 313.3 | 349.9 | 282.2 | 314.8 | 462.5 | 288.8
1247 | 1053 | 572.4 | 228.96 | 267.641 | 356.4 | 341.7 | 319.1 | 313 | 585.5 | 49.3 | 19.1 | 88.3 | 7.2 | 262.8 | 8.5 | 915 | 790.1 | 815.5 | 849.4 | 744.5 | 797.7 | 752.3 | 803.4 | 733.7 | 775.6 | 149.9 | 258.2 | 303.2 | 222.3 | 313 | 350.8 | 282.7 | 315.2 | 462.8 | 289.1
1248 | 1054 | 572 | 228.8 | 267.454 | 356.5 | 343.8 | 318.9 | 313.7 | 579.7 | 49.4 | 19.1 | 88.4 | 7.4 | 243.6 | 8.9 | 916.9 | 791 | 808.4 | 850.1 | 745.6 | 790.1 | 749.4 | 797.2 | 733.7 | 775.7 | 150.2 | 258.4 | 303.3 | 222.5 | 312.8 | 351.3 | 283 | 315.4 | 463 | 289.3
1249 | 1055 | 571 | 228.4 | 266.9864 | 357.1 | 344.9 | 318.3 | 314.1 | 572.1 | 49.4 | 19.1 | 88.4 | 6.5 | 245.6 | 8.3 | 917.8 | 791 | 808.3 | 851.3 | 746.8 | 788.1 | 745.8 | 800 | 733.7 | 777.2 | 150.4 | 258.5 | 303.4 | 222.7 | 312.4 | 351.7 | 283.3 | 315.6 | 463.2 | 289.5
1250 | 1056 | 569.3 | 227.72 | 266.1916 | 357.3 | 344.4 | 317.4 | 314 | 572.8 | 49.5 | 19.1 | 88.2 | 6.2 | 244.7 | 7.7 | 917.4 | 791.1 | 803.3 | 851.8 | 746.1 | 794.7 | 745 | 802.4 | 733.9 | 778.4 | 150.6 | 258.8 | 303.6 | 222.9 | 312.1 | 352.1 | 283.5 | 315.7 | 463.5 | 289.6
1251 | 1057 | 570.1 | 228.04 | 266.5656 | 357.2 | 343 | 316.8 | 315 | 580.9 | 49.6 | 19.1 | 88.3 | 6.2 | 254.2 | 7.7 | 917.2 | 792.2 | 803.7 | 852.3 | 747.5 | 793.1 | 744.3 | 800 | 734 | 778.3 | 150.8 | 259 | 303.6 | 223 | 311.9 | 352.6 | 283.8 | 315.9 | 463.8 | 289.8
1252 | 1058 | 570.5 | 228.2 | 266.7527 | 357.5 | 342.6 | 317.1 | 314.3 | 574.2 | 49.7 | 19.1 | 88.5 | 6 | 237.8 | 7 | 914.9 | 790.5 | 805.4 | 852.2 | 748.3 | 786.3 | 744.1 | 798 | 733.8 | 779.5 | 151 | 259.1 | 303.7 | 223.2 | 311.4 | 353.1 | 284 | 316.1 | 463.9 | 290
1253 | 1059 | 571.4 | 228.56 | 267.1735 | 358.3 | 342.3 | 317.5 | 313.5 | 571 | 49.8 | 19.1 | 88.7 | 5.3 | 243.2 | 6.8 | 914.7 | 790.4 | 808.4 | 852.9 | 749 | 784.6 | 744.6 | 799.2 | 733.8 | 779.6 | 151.3 | 259.3 | 304 | 223.4 | 311.2 | 353.4 | 284.3 | 316.3 | 464.2 | 290.2
1254 | 1060 | 571.6 | 228.64 | 267.267 | 358.1 | 342.1 | 317.2 | 314 | 567.3 | 49.9 | 19.1 | 88.8 | 6.8 | 235 | 6.5 | 916.8 | 788.9 | 799.4 | 853.9 | 751.1 | 781.4 | 744.7 | 798.6 | 733.7 | 779.9 | 151.5 | 259.5 | 304.1 | 223.6 | 311.2 | 353.9 | 284.7 | 316.4 | 464.4 | 290.4
1255 | 1061 | 571.7 | 228.68 | 267.3137 | 357.3 | 341.2 | 317.2 | 314.6 | 557.3 | 49.9 | 19.1 | 89.1 | 7.3 | 245.8 | 8.4 | 916.2 | 787.6 | 796.1 | 854.4 | 752.7 | 776.1 | 744.6 | 792.5 | 733.7 | 781 | 151.7 | 259.7 | 304.3 | 223.8 | 311.2 | 354.5 | 285 | 316.6 | 464.6 | 290.6
1256 | 1062 | 570.2 | 228.08 | 266.6124 | 357.4 | 341.1 | 318.3 | 315.5 | 552.8 | 49.9 | 19.1 | 89.4 | 8.1 | 248.4 | 9 | 916.3 | 786.7 | 790.2 | 854.7 | 751.8 | 777.6 | 743.8 | 794.8 | 733.5 | 781.3 | 151.9 | 259.9 | 304.3 | 223.9 | 311.1 | 354.4 | 285.3 | 316.8 | 464.9 | 290.8
1257 | 1063 | 568.9 | 227.56 | 266.0045 | 356.5 | 340.6 | 319.6 | 316.3 | 560.4 | 50 | 19.1 | 89.6 | 8.1 | 264.3 | 8.8 | 916 | 788.1 | 805.7 | 854.6 | 754 | 782.6 | 744.4 | 799.2 | 733.8 | 782.5 | 152.2 | 260 | 304.4 | 224.1 | 310.6 | 354.4 | 285.6 | 317 | 465 | 290.9
1258 | 1064 | 568.6 | 227.44 | 265.8643 | 356.2 | 339.4 | 319.5 | 316.1 | 577.1 | 50 | 19.1 | 89.8 | 6.8 | 247.7 | 13.4 | 916.4 | 787.3 | 809.7 | 855 | 753.5 | 787.9 | 745.1 | 800.8 | 734.2 | 782.3 | 152.4 | 260.1 | 304.6 | 224.3 | 310.2 | 354.5 | 285.8 | 317 | 465.2 | 291.1
1259 | 1065 | 569.5 | 227.8 | 266.2851 | 356.9 | 338.2 | 318.2 | 317.4 | 594.9 | 50.1 | 19.1 | 89.8 | 6.2 | 245.1 | 13.4 | 915.7 | 786.5 | 800.2 | 854.9 | 755.3 | 786.2 | 747.8 | 802 | 734.3 | 784.1 | 152.6 | 260.2 | 304.8 | 224.4 | 310.1 | 354.5 | 286.2 | 317.1 | 465.5 | 291.3
1260 | 1066 | 570 | 228 | 266.5189 | 356.2 | 337.6 | 317.9 | 317.5 | 592.9 | 50.1 | 19.1 | 89.9 | 6.1 | 251.1 | 16.6 | 912.6 | 785.5 | 802.1 | 854.8 | 755.2 | 785.8 | 749.8 | 802.1 | 734.3 | 785.2 | 152.8 | 260.3 | 304.9 | 224.6 | 310.1 | 354.8 | 286.6 | 317.1 | 465.9 | 291.5
1261 | 1067 | 569.5 | 227.8 | 266.2851 | 356.5 | 337.6 | 317 | 317.6 | 586.1 | 50 | 19.1 | 89.9 | 6.6 | 253.4 | 17.7 | 911.1 | 785.6 | 808.5 | 854.5 | 756.1 | 784.9 | 749.2 | 802.8 | 734.4 | 785.4 | 153 | 260.5 | 305.1 | 224.8 | 310.1 | 355.1 | 287.1 | 317.3 | 466.5 | 291.7
1262 | 1068 | 568.5 | 227.4 | 265.8175 | 357.9 | 338.6 | 316.4 | 318.3 | 580.9 | 50 | 19.1 | 89.8 | 7.3 | 253.4 | 14.5 | 911.3 | 785.2 | 810.8 | 854.5 | 758.3 | 784 | 748.2 | 801.7 | 734.6 | 785.5 | 153.3 | 260.7 | 305.2 | 224.9 | 309.9 | 355.2 | 287.4 | 317.4 | 466.9 | 291.9
1263 | 1069 | 569.2 | 227.68 | 266.1448 | 358.1 | 339.8 | 317.9 | 318.7 | 576.7 | 49.9 | 19.1 | 89.7 | 7.7 | 254.2 | 14.5 | 912.3 | 785 | 815.1 | 854.7 | 759 | 779.6 | 746.9 | 797.6 | 734.6 | 786 | 153.5 | 260.8 | 305.4 | 225.1 | 310 | 355.6 | 287.8 | 317.6 | 467.2 | 292
1264 | 1070 | 568.9 | 227.56 | 266.0045 | 357.4 | 339.4 | 318.6 | 318.8 | 575.7 | 49.9 | 19.1 | 89.8 | 7.9 | 257.1 | 14.8 | 911.9 | 785 | 821.3 | 855.2 | 758.7 | 784.3 | 744.9 | 798.1 | 734.7 | 785.9 | 153.7 | 261 | 305.4 | 225.3 | 310 | 355.6 | 288.2 | 317.6 | 467.4 | 292.2
1265 | 1071 | 569.2 | 227.68 | 266.1448 | 357.9 | 338.4 | 319.5 | 318.7 | 581.2 | 49.9 | 19.1 | 89.7 | 7.5 | 250.7 | 17.3 | 911.8 | 784.6 | 813.1 | 855.7 | 759.6 | 782.7 | 743.3 | 793.3 | 734.8 | 785.7 | 153.9 | 261.1 | 305.4 | 225.4 | 310 | 355.2 | 288.6 | 317.7 | 467.6 | 292.4
1266 | 1072 | 569.7 | 227.88 | 266.3786 | 357.7 | 338.9 | 319.3 | 318.7 | 593.8 | 50 | 19.1 | 89.7 | 7.9 | 246.5 | 16.5 | 910.8 | 785.3 | 820.9 | 855.9 | 760.8 | 788.6 | 741.6 | 794.7 | 735.1 | 787.3 | 154.2 | 261.2 | 305.6 | 225.6 | 309.8 | 354.9 | 288.9 | 317.8 | 467.7 | 292.6
1267 | 1073 | 569.1 | 227.64 | 266.098 | 357.9 | 340 | 318.4 | 319.2 | 596 | 50 | 19.1 | 89.8 | 8.3 | 256.3 | 15.3 | 910.6 | 786.1 | 830.7 | 855.9 | 762.1 | 796.3 | 738.5 | 799.3 | 735.4 | 787.9 | 154.4 | 261.4 | 305.8 | 225.8 | 309.8 | 354.4 | 289.3 | 317.8 | 468.1 | 292.7
1268 | 1074 | 568.3 | 227.32 | 265.724 | 357.9 | 340.7 | 317.3 | 319.4 | 605.4 | 50.1 | 19.1 | 89.9 | 8 | 243.5 | 15 | 908.9 | 786 | 836.6 | 856 | 764.1 | 797.9 | 740.2 | 800.5 | 735.5 | 788.1 | 154.6 | 261.6 | 306 | 225.9 | 309.7 | 354.1 | 289.7 | 317.8 | 468.5 | 292.9
1269 | 1075 | 569.1 | 227.64 | 266.098 | 357.3 | 341.2 | 317.4 | 319.8 | 603.5 | 50.1 | 19.1 | 89.9 | 8.4 | 250.1 | 18.9 | 909.1 | 786.3 | 836.7 | 856.3 | 765.5 | 792.9 | 740.5 | 802.8 | 735.3 | 789.6 | 154.8 | 261.7 | 306 | 226.1 | 309.6 | 353.7 | 290 | 317.9 | 468.9 | 293.1
1270 | 1076 | 568.6 | 227.44 | 265.8643 | 356.3 | 341.3 | 317.6 | 320.4 | 596.4 | 50.2 | 19.1 | 90 | 7.4 | 249 | 19.8 | 909.4 | 786.8 | 812.9 | 856.7 | 764 | 792.2 | 740.7 | 804.8 | 735.1 | 789.6 | 155.1 | 261.9 | 306.1 | 226.3 | 309.7 | 353.6 | 290.4 | 318 | 469.2 | 293.3
1271 | 1077 | 568.9 | 227.56 | 266.0045 | 355.5 | 340.8 | 316.8 | 320.9 | 592.5 | 50.1 | 19.1 | 90 | 6.5 | 248.7 | 22.8 | 911.1 | 788.8 | 787.7 | 857.5 | 760.7 | 788.6 | 740.8 | 800.6 | 735 | 786.5 | 155.3 | 262 | 306.3 | 226.5 | 309.7 | 353.5 | 290.8 | 318.1 | 469.4 | 293.5
1272 | 1078 | 569.9 | 227.96 | 266.4721 | 355.9 | 339.6 | 316.1 | 321.3 | 579.2 | 50 | 19.1 | 89.9 | 6.2 | 248.9 | 21.6 | 914.1 | 789.8 | 788.8 | 858.7 | 760.4 | 788 | 740.2 | 800.8 | 734.6 | 785.4 | 155.5 | 262.2 | 306.3 | 226.6 | 309.8 | 353.3 | 291.1 | 318.2 | 469.4 | 293.6
1273 | 1079 | 570 | 228 | 266.5189 | 356.7 | 338.9 | 316.4 | 321 | 582.2 | 50.1 | 19.1 | 89.8 | 7.2 | 253 | 21.7 | 914.8 | 789.4 | 792.5 | 859.4 | 763.5 | 792.6 | 740.2 | 802.4 | 734.6 | 786.4 | 155.8 | 262.3 | 306.5 | 226.8 | 310.4 | 353.3 | 291.5 | 318.4 | 469.3 | 293.8
1274 | 1080 | 569.8 | 227.92 | 266.4253 | 357.3 | 338.5 | 316.7 | 319.7 | 585 | 50.2 | 19.1 | 89.8 | 7.9 | 256.9 | 21.1 | 914.9 | 788.8 | 799.2 | 860.4 | 765.2 | 783.5 | 739.5 | 796.3 | 734.5 | 787.7 | 156 | 262.5 | 306.7 | 227 | 310.2 | 353.4 | 291.9 | 318.6 | 469.5 | 294
1275 | 1081 | 569.8 | 227.92 | 266.4253 | 357.7 | 338.6 | 317 | 319.1 | 568.1 | 50.3 | 19.1 | 89.9 | 10.1 | 257.8 | 23.2 | 913.9 | 787.7 | 802.1 | 860.7 | 765.2 | 781.8 | 736.2 | 793.4 | 734.3 | 787.2 | 156.2 | 262.6 | 306.6 | 227.1 | 310 | 353.2 | 292.2 | 318.6 | 469.8 | 294.2
1276 | 1082 | 569.7 | 227.88 | 266.3786 | 358.8 | 339.6 | 316.3 | 319 | 580.7 | 50.3 | 19.1 | 90 | 10.8 | 255.9 | 21.6 | 912.7 | 786.8 | 797.2 | 860.4 | 763.9 | 791.3 | 735.2 | 795.5 | 734.5 | 786.3 | 156.5 | 262.8 | 306.8 | 227.3 | 310.2 | 352.8 | 292.5 | 318.7 | 470.1 | 294.4
1277 | 1083 | 569.7 | 227.88 | 266.3786 | 358.5 | 339.5 | 316.2 | 318.5 | 606.7 | 50.3 | 19.1 | 90.2 | 10.4 | 261.8 | 19.8 | 914 | 788.4 | 805.1 | 860.8 | 763.6 | 798.4 | 731.9 | 797.7 | 734.8 | 785.7 | 156.7 | 263 | 307.2 | 227.5 | 310.3 | 352.6 | 292.9 | 318.7 | 470.4 | 294.6
1278 | 1084 | 570.7 | 228.28 | 266.8462 | 358.4 | 338.7 | 317.1 | 317.1 | 638.4 | 50.3 | 19.1 | 90.2 | 10.4 | 256.6 | 21.9 | 912.6 | 786.8 | 823.3 | 860.7 | 763.4 | 802.7 | 727.6 | 797.4 | 735.1 | 784.5 | 156.9 | 263.1 | 307.5 | 227.7 | 310.9 | 352.5 | 293.5 | 318.7 | 470.6 | 294.8
1279 | 1085 | 568.5 | 227.4 | 265.8175 | 358.2 | 339 | 317.3 | 316.9 | 650.8 | 50.4 | 19.1 | 90.2 | 8 | 251.5 | 20.9 | 911.6 | 786.2 | 831.8 | 860.8 | 763 | 805.8 | 726.7 | 799.6 | 735.5 | 785.3 | 157.1 | 263.2 | 307.6 | 227.8 | 311 | 352.6 | 294 | 318.8 | 470.8 | 295
1280 | 1086 | 569.4 | 227.76 | 266.2383 | 358.5 | 339.2 | 317.6 | 318.2 | 654.1 | 50.4 | 19.1 | 90.1 | 7.1 | 259 | 18.4 | 912.3 | 784.8 | 837.7 | 861.1 | 761.2 | 808.6 | 727.1 | 800.6 | 735.8 | 784.8 | 157.4 | 263.4 | 307.7 | 228 | 310.9 | 352.6 | 294.5 | 318.9 | 471.1 | 295.2
1281 | 1087 | 568.9 | 227.56 | 266.0045 | 358.4 | 339.2 | 318 | 319.1 | 652.7 | 50.5 | 19.1 | 89.9 | 6.9 | 246.2 | 16.5 | 913.5 | 787.1 | 838.1 | 861.3 | 761.5 | 812 | 727.5 | 803.8 | 736 | 783.8 | 157.6 | 263.6 | 307.9 | 228.2 | 311.1 | 352.5 | 295 | 319 | 471.6 | 295.4
1282 | 1088 | 568.5 | 227.4 | 265.8175 | 358.2 | 339.1 | 319 | 320.2 | 663.9 | 50.5 | 19 | 89.8 | 6.9 | 240.6 | 15.3 | 912.2 | 787.3 | 835.4 | 861.1 | 761.4 | 814 | 725.5 | 803.3 | 736.4 | 783 | 157.8 | 263.7 | 308.1 | 228.4 | 311.8 | 352.6 | 295.6 | 319.1 | 471.9 | 295.6
1283 | 1089 | 567.8 | 227.12 | 265.4902 | 358.6 | 339.6 | 319.8 | 321.3 | 673.6 | 50.5 | 19 | 89.6 | 7 | 276.5 | 12.2 | 912.1 | 786.8 | 840.1 | 860.9 | 761.7 | 814 | 724.1 | 804.7 | 736.6 | 784 | 158.1 | 263.8 | 308.5 | 228.5 | 312 | 352.6 | 296 | 319.1 | 472.4 | 295.8
1284 | 1090 | 568 | 227.2 | 265.5837 | 358.9 | 340.6 | 321 | 322.7 | 667.5 | 50.4 | 19 | 89.5 | 6.8 | 269.2 | 13.2 | 910.2 | 786.8 | 840.8 | 860.7 | 760.5 | 815.5 | 724.5 | 806.5 | 736.6 | 783.7 | 158.3 | 263.9 | 308.5 | 228.7 | 311.8 | 352.6 | 296.6 | 319.3 | 472.9 | 296
1285 | 1091 | 567 | 226.8 | 265.1161 | 359.1 | 341.4 | 321.8 | 323.1 | 656.2 | 50.4 | 19 | 89.5 | 7.7 | 257.4 | 13 | 908.9 | 786 | 831.9 | 860.3 | 760.9 | 816.8 | 726 | 809.1 | 736.7 | 785 | 158.5 | 264.1 | 308.7 | 228.9 | 312.2 | 352.6 | 297.2 | 319.3 | 473 | 296.2
1286 | 1092 | 567 | 226.8 | 265.1161 | 360.2 | 341.8 | 323 | 322.3 | 650.6 | 50.4 | 19 | 89.4 | 6.5 | 268.3 | 13.9 | 908.3 | 787.4 | 824.1 | 861 | 760.6 | 818.5 | 728.6 | 812.6 | 736.7 | 785 | 158.8 | 264.2 | 308.8 | 229 | 312.3 | 352.5 | 297.7 | 319.4 | 473 | 296.4
1287 | 1093 | 567.4 | 226.96 | 265.3032 | 360.7 | 342.1 | 323.6 | 322.2 | 655.6 | 50.4 | 19 | 89.3 | 6.6 | 264.7 | 16.3 | 906.7 | 787.6 | 825.6 | 861.3 | 761 | 821.1 | 730.5 | 813.2 | 737 | 784.5 | 159 | 264.4 | 309.2 | 229.2 | 312.6 | 352.5 | 298 | 319.5 | 473 | 296.6
1288 | 1094 | 567.5 | 227 | 265.3499 | 360.7 | 341.2 | 323.9 | 322.6 | 665.8 | 50.4 | 19 | 89.3 | 6.4 | 263.4 | 17 | 905.9 | 786.7 | 825.5 | 860.7 | 762.2 | 817.4 | 730.8 | 812.5 | 737 | 785.7 | 159.3 | 264.6 | 309.3 | 229.4 | 312.9 | 352.7 | 298.4 | 319.6 | 473.2 | 296.7
1289 | 1095 | 567.4 | 226.96 | 265.3032 | 360.6 | 340.8 | 324.3 | 323.5 | 641.3 | 50.3 | 19 | 89.2 | 6.2 | 266.7 | 14.7 | 906.9 | 787.2 | 827.5 | 860.7 | 763.2 | 807.8 | 730 | 810.2 | 736.6 | 784.8 | 159.5 | 264.8 | 309.2 | 229.5 | 313.4 | 353.1 | 298.8 | 319.8 | 473.5 | 296.9
1290 | 1096 | 567.3 | 226.92 | 265.2564 | 360.7 | 341 | 323.6 | 323.8 | 629.6 | 50.4 | 19 | 89.1 | 6.2 | 261.1 | 12.7 | 905.9 | 785.7 | 831.5 | 860.7 | 765.7 | 807.8 | 731.1 | 808.9 | 736.3 | 787.2 | 159.7 | 264.9 | 309.3 | 229.7 | 313.6 | 353.4 | 299.3 | 319.9 | 473.6 | 297.1
1291 | 1097 | 568.2 | 227.28 | 265.6772 | 360.9 | 341.1 | 322.4 | 323 | 624.7 | 50.5 | 19 | 89.2 | 7 | 266.2 | 11.9 | 907.9 | 784.8 | 826.6 | 861.6 | 767.6 | 798.7 | 728.3 | 800.2 | 736 | 786.9 | 160 | 265.1 | 309.5 | 229.9 | 313.6 | 353.8 | 299.9 | 320.1 | 474 | 297.3
1292 | 1098 | 568.3 | 227.32 | 265.724 | 360.3 | 342.1 | 322 | 321.8 | 608.5 | 50.5 | 19 | 89.3 | 6.3 | 256.2 | 10.3 | 909.2 | 784.6 | 821.6 | 862.1 | 769.3 | 793.3 | 726.2 | 798.1 | 735.7 | 788.2 | 160.2 | 265.2 | 309.5 | 230.1 | 313.4 | 354.1 | 300.1 | 320.3 | 474.5 | 297.5
1293 | 1099 | 568 | 227.2 | 265.5837 | 360.3 | 343.3 | 321.8 | 320.9 | 604.5 | 50.5 | 19 | 89.5 | 5.9 | 289.3 | 10 | 906.7 | 783.9 | 832 | 862.3 | 770 | 793.3 | 727.1 | 797.1 | 735.5 | 788.4 | 160.4 | 265.3 | 309.6 | 230.3 | 313.5 | 354.4 | 300.5 | 320.5 | 474.8 | 297.6
1294 | 1100 | 567.2 | 226.88 | 265.2096 | 360.2 | 344 | 321.6 | 320 | 590.8 | 50.6 | 19 | 89.6 | 5.6 | 263.1 | 11.7 | 906.6 | 783.6 | 828.7 | 862.7 | 771 | 788.1 | 724.8 | 790.1 | 735.2 | 787.7 | 160.7 | 265.5 | 309.6 | 230.4 | 313.5 | 354.9 | 300.9 | 320.7 | 475 | 297.8
1295 | 1101 | 567.1 | 226.84 | 265.1629 | 360.9 | 344.5 | 321.9 | 320.2 | 576.8 | 50.6 | 19 | 89.8 | 5.1 | 252.6 | 12.9 | 908.3 | 784.3 | 832.4 | 863.6 | 771.6 | 788.5 | 723.1 | 789.4 | 735 | 787.2 | 160.9 | 265.6 | 309.7 | 230.6 | 313.4 | 355.1 | 301.1 | 320.9 | 475.1 | 298
1296 | 1102 | 566.6 | 226.64 | 264.9291 | 361 | 345.4 | 321.3 | 320.6 | 592.9 | 50.7 | 19 | 89.9 | 5.8 | 259.2 | 11.5 | 907.9 | 784.5 | 842.2 | 863.1 | 773.3 | 797.1 | 720.6 | 790.4 | 735.2 | 785.6 | 161.2 | 265.8 | 310 | 230.8 | 313.2 | 354.9 | 301.3 | 320.9 | 475.3 | 298.2
1297 | 1103 | 567.4 | 226.96 | 265.3032 | 360.6 | 346.2 | 321.5 | 320.5 | 612.4 | 50.8 | 19 | 90 | 6.5 | 229.1 | 8.9 | 909.6 | 784.1 | 844.7 | 863.2 | 772.5 | 802.4 | 717.3 | 789.1 | 735.5 | 783.1 | 161.4 | 265.9 | 310.4 | 231 | 313.2 | 354.8 | 301.7 | 320.9 | 475.5 | 298.4
1298 | 1104 | 566.9 | 226.76 | 265.0694 | 360.5 | 346.5 | 322.4 | 320.1 | 623.8 | 50.9 | 19 | 90.1 | 7.4 | 251.2 | 7.2 | 910 | 785.3 | 836.1 | 863.4 | 770.9 | 803.7 | 713.3 | 789 | 735.5 | 780.5 | 161.6 | 266 | 310.6 | 231.2 | 313.1 | 354.7 | 302.1 | 321 | 475.7 | 298.5
1299 | 1105 | 567.1 | 226.84 | 265.1629 | 361.2 | 346.3 | 323.2 | 320.8 | 617.8 | 50.9 | 19 | 90.3 | 8.9 | 246.3 | 8 | 911.5 | 784.4 | 835.4 | 864 | 769.1 | 801.7 | 715.2 | 795 | 735.3 | 782 | 161.9 | 266.2 | 310.5 | 231.4 | 313 | 354.4 | 302.4 | 321.1 | 475.6 | 298.7
1300 | 1106 | 567.1 | 226.84 | 265.1629 | 360.7 | 346.7 | 323.1 | 321.2 | 639.3 | 50.9 | 19 | 90.4 | 8.1 | 228.8 | 7.7 | 912.1 | 784.9 | 833.7 | 864.4 | 769.3 | 808.6 | 717.1 | 796.9 | 735.6 | 781.8 | 162.1 | 266.4 | 310.9 | 231.5 | 313 | 354.3 | 302.7 | 321.2 | 475.7 | 298.9
1301 | 1107 | 567.8 | 227.12 | 265.4902 | 360.7 | 347.3 | 323.5 | 321.5 | 662.4 | 50.9 | 19 | 90.4 | 7.6 | 274.7 | 6.7 | 910.5 | 783.3 | 843.4 | 864.5 | 769.6 | 814.6 | 718.1 | 798.2 | 735.9 | 782.2 | 162.4 | 266.7 | 311.2 | 231.7 | 312.7 | 354.1 | 303.2 | 321.2 | 475.9 | 299.1
1302 | 1108 | 568.1 | 227.24 | 265.6305 | 360.2 | 347.3 | 324.4 | 321.9 | 681 | 50.9 | 19 | 90.5 | 7.9 | 252.6 | 8.3 | 907.5 | 783.1 | 844.5 | 864.2 | 769.8 | 816 | 717.7 | 798.9 | 736.2 | 782.8 | 162.6 | 266.9 | 311.5 | 231.9 | 313 | 353.9 | 303.8 | 321.2 | 476.3 | 299.2
1303 | 1109 | 567.8 | 227.12 | 265.4902 | 360.4 | 347.5 | 325.1 | 323.4 | 688 | 51 | 19 | 90.5 | 6.5 | 259.4 | 11.7 | 905.8 | 783 | 838.7 | 863.4 | 771.1 | 818.9 | 718.4 | 801.9 | 736.2 | 784.5 | 162.8 | 267 | 311.5 | 232.1 | 313.3 | 353.8 | 304.5 | 321.3 | 476.7 | 299.4
1304 | 1110 | 567.6 | 227.04 | 265.3967 | 360.5 | 348 | 325.3 | 324.3 | 682.4 | 51 | 19 | 90.5 | 6.2 | 269.6 | 14.1 | 908.1 | 784.4 | 831.4 | 863.9 | 771.2 | 819 | 719.1 | 806 | 736 | 784.7 | 163.1 | 267.2 | 311.5 | 232.2 | 313.5 | 353.8 | 305 | 321.5 | 476.7 | 299.6
1305 | 1111 | 567.5 | 227 | 265.3499 | 360.1 | 348 | 325 | 324.3 | 664.3 | 51 | 19 | 90.4 | 6.8 | 256 | 16.4 | 910.6 | 787.2 | 827.7 | 864.5 | 767.7 | 819.9 | 718.5 | 809.8 | 735.8 | 783.6 | 163.3 | 267.4 | 311.6 | 232.4 | 313.2 | 353.8 | 305.2 | 321.6 | 476.8 | 299.8
1306 | 1112 | 567.8 | 227.12 | 265.4902 | 360.2 | 348.1 | 324.4 | 323.7 | 656.5 | 51.1 | 19 | 90.3 | 8.2 | 254.3 | 16.7 | 907.7 | 787.3 | 841 | 864 | 770.3 | 817.5 | 718.2 | 809.8 | 735.4 | 784.2 | 163.5 | 267.6 | 311.8 | 232.5 | 313.1 | 353.8 | 305.4 | 321.7 | 476.9 | 300
1307 | 1113 | 567.8 | 227.12 | 265.4902 | 359.4 | 348.8 | 323.4 | 323.1 | 638.8 | 51.1 | 19 | 90.3 | 8.2 | 258.1 | 18 | 906.4 | 785.8 | 841.1 | 864.3 | 772.7 | 814.8 | 716.5 | 809.2 | 734.9 | 786.1 | 163.8 | 267.8 | 311.8 | 232.7 | 312.9 | 353.7 | 305.6 | 321.8 | 476.9 | 300.1
1308 | 1114 | 568.8 | 227.52 | 265.9578 | 360.2 | 349.1 | 323.4 | 322.1 | 622.1 | 51.2 | 19 | 90.3 | 8.6 | 256.5 | 18.6 | 905.5 | 784.5 | 838.1 | 864.5 | 774.5 | 813 | 715.9 | 807.8 | 734.5 | 787.1 | 164 | 267.9 | 311.8 | 232.9 | 312.7 | 353.6 | 306.1 | 321.8 | 477 | 300.3
1309 | 1115 | 567.5 | 227 | 265.3499 | 359.9 | 349.1 | 323 | 320.9 | 618.9 | 51.2 | 19 | 90.2 | 10 | 252 | 19.6 | 906.1 | 783.6 | 840.7 | 864.8 | 775.1 | 816.4 | 715.6 | 806.9 | 734.2 | 787.6 | 164.2 | 268.1 | 312.1 | 233 | 312.5 | 353.5 | 306.2 | 321.9 | 477.3 | 300.5
1310 | 1116 | 568.1 | 227.24 | 265.6305 | 359 | 349.5 | 322.6 | 319.6 | 625.1 | 51.2 | 19 | 90.2 | 9.8 | 248.2 | 21.1 | 906.8 | 784.7 | 845.1 | 865.2 | 775.8 | 818.1 | 712.3 | 804 | 734.1 | 786.2 | 164.5 | 268.3 | 312.3 | 233.2 | 312.3 | 353.2 | 306.3 | 322 | 477.8 | 300.6
1311 | 1117 | 568.9 | 227.56 | 266.0045 | 357.8 | 349.2 | 323 | 319.2 | 628.7 | 51.4 | 19 | 90.1 | 10.7 | 252 | 21.9 | 904 | 783.9 | 839.8 | 864.6 | 777.8 | 816.1 | 711.9 | 805.9 | 733.8 | 787.4 | 164.7 | 268.5 | 312.3 | 233.4 | 312.7 | 353.1 | 306.5 | 322.1 | 478 | 300.8
1312 | 1118 | 569.6 | 227.84 | 266.3318 | 357.2 | 349.3 | 322.4 | 318.7 | 628.8 | 51.4 | 19 | 90 | 9.8 | 255.1 | 22.6 | 903 | 784.1 | 840.1 | 864.4 | 777.9 | 818.1 | 714 | 806.6 | 733.6 | 788.1 | 165 | 268.6 | 312.5 | 233.5 | 312.7 | 353.6 | 306.8 | 322.2 | 478.3 | 301
1313 | 1119 | 569.5 | 227.8 | 266.2851 | 358.4 | 349.3 | 321.3 | 318.5 | 641.4 | 51.3 | 19 | 89.9 | 10.6 | 256.3 | 22 | 903.1 | 785.1 | 833.5 | 864.1 | 778 | 820.7 | 716 | 805.3 | 733.7 | 789.2 | 165.2 | 268.8 | 312.9 | 233.7 | 312.7 | 353.7 | 306.9 | 322.2 | 478.6 | 301.1
1314 | 1120 | 569.6 | 227.84 | 266.3318 | 358.9 | 349.3 | 322.5 | 319.5 | 664.7 | 51.3 | 19 | 89.8 | 9.7 | 261.5 | 25.4 | 906.9 | 785.3 | 835.1 | 864.8 | 778 | 821.9 | 715.2 | 807.6 | 733.8 | 788.6 | 165.4 | 268.9 | 313.2 | 233.8 | 312.8 | 353.6 | 307.2 | 322.2 | 478.9 | 301.3
1315 | 1121 | 569.3 | 227.72 | 266.1916 | 359.2 | 349 | 323.5 | 319.7 | 679.5 | 51.4 | 19 | 89.8 | 9.1 | 258.8 | 27 | 905.7 | 784.4 | 831.5 | 865.3 | 778.4 | 822 | 715.6 | 808.2 | 733.8 | 789.2 | 165.7 | 269 | 313.3 | 234 | 312.8 | 353.6 | 307.6 | 322.3 | 479.1 | 301.5
1316 | 1122 | 569 | 227.6 | 266.0513 | 359.8 | 349 | 323.9 | 320.1 | 689 | 51.4 | 19 | 89.7 | 7.5 | 255.6 | 26.4 | 903.4 | 784 | 827.5 | 865.1 | 779.2 | 822.3 | 717.1 | 810.2 | 733.9 | 790.1 | 165.9 | 269.2 | 313.6 | 234.2 | 313.3 | 353.6 | 308 | 322.5 | 479.4 | 301.6
1317 | 1123 | 568.7 | 227.48 | 265.911 | 359.5 | 348.9 | 324 | 321.9 | 681 | 51.4 | 19 | 89.6 | 6.8 | 273 | 21.6 | 901 | 783.2 | 830.9 | 864.9 | 780.1 | 819.6 | 718.2 | 813.5 | 733.8 | 791.9 | 166.1 | 269.3 | 313.7 | 234.3 | 313.7 | 353.6 | 308.5 | 322.6 | 479.8 | 301.8
1318 | 1124 | 569.1 | 227.64 | 266.098 | 358.6 | 349.5 | 323.2 | 322.3 | 667.9 | 51.4 | 19 | 89.4 | 6.7 | 271.5 | 19.2 | 900.8 | 783.2 | 826.9 | 865 | 781.8 | 816.7 | 718.6 | 812.5 | 733.6 | 792.7 | 166.4 | 269.5 | 313.8 | 234.5 | 313.9 | 353.7 | 309.1 | 322.7 | 480.3 | 302
1319 | 1125 | 569.1 | 227.64 | 266.098 | 357.4 | 350.1 | 322.6 | 322.4 | 653.9 | 51.4 | 19 | 89.3 | 7.9 | 261.6 | 21.8 | 903.7 | 783.3 | 812.7 | 865.4 | 781.3 | 815.1 | 718.6 | 812.9 | 733.2 | 793.6 | 166.6 | 269.7 | 313.9 | 234.6 | 313.9 | 353.9 | 309.4 | 322.8 | 480.8 | 302.2
1320 | 1126 | 569.3 | 227.72 | 266.1916 | 357.5 | 350.2 | 322.5 | 322.4 | 646.2 | 51.4 | 19 | 89.4 | 7.2 | 273.1 | 17.7 | 902.8 | 784.2 | 807.4 | 865.4 | 781.6 | 815.8 | 718.9 | 814.7 | 732.8 | 794 | 166.8 | 269.9 | 314 | 234.8 | 313.9 | 353.9 | 309.6 | 322.9 | 481.1 | 302.4
1321 | 1127 | 569.7 | 227.88 | 266.3786 | 357.7 | 350.2 | 322.6 | 322.6 | 640.4 | 51.4 | 19 | 89.4 | 6.6 | 272.8 | 15.5 | 901 | 783.6 | 813.2 | 865.2 | 784.2 | 813.9 | 718.4 | 814.2 | 732.5 | 794.7 | 167.1 | 270.1 | 314.2 | 235 | 314 | 353.9 | 309.8 | 323 | 481.2 | 302.5
1322 | 1128 | 568.4 | 227.36 | 265.7707 | 357.4 | 350.9 | 323.4 | 322.7 | 634.2 | 51.4 | 19 | 89.3 | 7.6 | 259.7 | 16 | 899.7 | 782 | 811 | 864.7 | 785.2 | 815.5 | 718.9 | 810.5 | 732.4 | 794.7 | 167.3 | 270.3 | 314.3 | 235.1 | 313.9 | 353.8 | 310.1 | 323.1 | 481.7 | 302.7
1323 | 1129 | 568.6 | 227.44 | 265.8643 | 357.1 | 351.3 | 323.8 | 322.6 | 640 | 51.4 | 19 | 89.2 | 7.5 | 259.5 | 16.4 | 900.5 | 782.2 | 804.3 | 864.2 | 783 | 818.3 | 718.5 | 811.3 | 732.4 | 795.2 | 167.6 | 270.5 | 314.5 | 235.3 | 313.9 | 353.8 | 310.2 | 323.2 | 482.3 | 302.9
1324 | 1130 | 567.2 | 226.88 | 265.2096 | 356.6 | 351.2 | 324 | 322.5 | 640.7 | 51.4 | 19 | 89.3 | 8.2 | 267.5 | 16.1 | 902.7 | 783.6 | 777 | 864.1 | 777.1 | 808.1 | 715 | 811.8 | 731.9 | 790.3 | 167.8 | 270.7 | 314.7 | 235.5 | 314.3 | 353.6 | 310.5 | 323.3 | 482.6 | 303
1325 | 1131 | 568.5 | 227.4 | 265.8175 | 357.2 | 350.9 | 325.4 | 322.6 | 617.6 | 51.4 | 19 | 89.3 | 9.1 | 261.6 | 14.6 | 903.7 | 786.1 | 769.6 | 864.6 | 775.7 | 804.3 | 712.7 | 805.5 | 731.2 | 788.5 | 168 | 270.9 | 314.6 | 235.6 | 314.8 | 353.7 | 310.9 | 323.4 | 482.5 | 303.2
1326 | 1132 | 567.9 | 227.16 | 265.537 | 357.8 | 350.2 | 325.8 | 322.6 | 606.8 | 51.4 | 19 | 89.4 | 7.9 | 245.5 | 13.7 | 902.9 | 785.2 | 776 | 864.9 | 777.1 | 808.5 | 713.7 | 806.6 | 730.9 | 790.5 | 168.3 | 271 | 314.7 | 235.8 | 314.9 | 353.8 | 311.1 | 323.5 | 482.4 | 303.4
1327 | 1133 | 567.3 | 226.92 | 265.2564 | 358 | 349.9 | 325.6 | 322.6 | 615.9 | 51.4 | 19 | 89.3 | 7.3 | 273.7 | 12.1 | 902.8 | 784.8 | 788.8 | 865.3 | 776.3 | 815.7 | 712.4 | 806.9 | 731.1 | 790.9 | 168.5 | 271.1 | 314.9 | 236 | 315.4 | 353.7 | 311.4 | 323.6 | 482.3 | 303.6
1328 | 1134 | 567.8 | 227.12 | 265.4902 | 357.8 | 349.4 | 324.7 | 323.2 | 633.9 | 51.4 | 19 | 89.3 | 6.8 | 251 | 12.3 | 905 | 786.3 | 799.1 | 865.8 | 773.9 | 821 | 709.4 | 800.7 | 731.3 | 786.8 | 168.8 | 271.3 | 315.5 | 236.1 | 315.7 | 353.5 | 311.6 | 323.7 | 482.4 | 303.7
1329 | 1135 | 567.8 | 227.12 | 265.4902 | 357.4 | 349.3 | 324 | 323.7 | 644.4 | 51.3 | 19 | 89.4 | 8.7 | 238.5 | 11.3 | 905.1 | 786.2 | 814.3 | 865.8 | 776.7 | 823.3 | 707.7 | 802.2 | 731.4 | 787.7 | 169 | 271.4 | 315.5 | 236.3 | 316.1 | 353.4 | 311.9 | 323.7 | 482.4 | 303.9
1330 | 1136 | 567.9 | 227.16 | 265.537 | 356.9 | 350.4 | 324 | 323.8 | 644.4 | 51.3 | 19 | 89.3 | 7 | 248.1 | 10.5 | 906.2 | 787 | 824.7 | 866.2 | 779.5 | 818.4 | 704.8 | 802.2 | 731.4 | 788.9 | 169.2 | 271.6 | 315.5 | 236.5 | 316.4 | 353.3 | 312.1 | 323.8 | 482.6 | 304.1
1331 | 1137 | 568.1 | 227.24 | 265.6305 | 357.3 | 352.7 | 324.6 | 323.8 | 642.2 | 51.3 | 19 | 89.3 | 7.4 | 238.5 | 11 | 908.9 | 786.7 | 821.9 | 866.8 | 774.8 | 819 | 701.1 | 798.4 | 731.4 | 784.9 | 169.4 | 271.8 | 315.8 | 236.6 | 316.7 | 353 | 312.4 | 323.8 | 483 | 304.2
1332 | 1138 | 568 | 227.2 | 265.5837 | 359.2 | 353.3 | 325.6 | 323.1 | 646.3 | 51.4 | 19 | 89.3 | 8.8 | 230.5 | 11 | 908.2 | 786.9 | 804.3 | 866.5 | 771.5 | 820.6 | 700.9 | 797.9 | 731.1 | 781.8 | 169.7 | 272 | 316.1 | 236.8 | 316.7 | 352.7 | 312.7 | 323.8 | 483.1 | 304.4
1333 | 1139 | 568.1 | 227.24 | 265.6305 | 360.3 | 352.5 | 326 | 323.6 | 646 | 51.5 | 19 | 89.2 | 6.5 | 249.4 | 11.9 | 907.3 | 786.7 | 801.1 | 867.2 | 771.1 | 821.9 | 700 | 798.2 | 731 | 781.5 | 169.9 | 272.1 | 316.5 | 237 | 316.7 | 352.5 | 312.9 | 323.9 | 483 | 304.6
1334 | 1140 | 567.9 | 227.16 | 265.537 | 360.6 | 351.6 | 326.9 | 324.7 | 651.9 | 51.6 | 18.9 | 89.3 | 6.2 | 227.6 | 14.2 | 908.5 | 786.2 | 811.7 | 867.4 | 770 | 822.6 | 697.4 | 793.7 | 731 | 778.4 | 170.2 | 272.2 | 316.7 | 237.1 | 316.9 | 352.4 | 313.2 | 323.9 | 483 | 304.8
1335 | 1141 | 567.9 | 227.16 | 265.537 | 362.2 | 350.4 | 327.5 | 325.6 | 643.1 | 51.7 | 18.9 | 89.4 | 7.2 | 224.6 | 12.7 | 910.7 | 784.4 | 811.5 | 868.4 | 767.1 | 817.3 | 694.1 | 782.7 | 730.5 | 773.6 | 170.4 | 272.4 | 316.9 | 237.3 | 317 | 352 | 313.4 | 323.9 | 483 | 305
1336 | 1142 | 567.7 | 227.08 | 265.4434 | 363.8 | 349.9 | 328 | 327.1 | 637.9 | 51.6 | 18.9 | 89.5 | 7 | 264.2 | 9.8 | 908.9 | 782.8 | 812.3 | 868.4 | 768.2 | 817.9 | 692.4 | 782.8 | 730.2 | 772.7 | 170.6 | 272.6 | 317.1 | 237.5 | 317.5 | 351.8 | 313.8 | 323.9 | 482.9 | 305.2
1337 | 1143 | 567.9 | 227.16 | 265.537 | 364.4 | 349.6 | 328.9 | 327.5 | 653.1 | 51.6 | 19 | 89.7 | 7.6 | 247.7 | 10.2 | 907.8 | 779.6 | 813.5 | 868 | 769 | 819.4 | 695 | 785.3 | 730.2 | 775.5 | 170.8 | 272.7 | 317.1 | 237.6 | 317.9 | 351.9 | 314 | 324.1 | 482.9 | 305.4
1338 | 1144 | 567.9 | 227.16 | 265.537 | 365 | 349.8 | 328.8 | 328 | 667.9 | 51.5 | 18.9 | 89.8 | 8.9 | 250.3 | 12.9 | 907.5 | 778.5 | 814.1 | 867.6 | 768.1 | 820.8 | 699.7 | 790.7 | 730.1 | 777 | 171.1 | 272.9 | 317.4 | 237.8 | 318.5 | 352 | 314.3 | 324.2 | 483.3 | 305.5
1339 | 1145 | 567.7 | 227.08 | 265.4434 | 365.3 | 351 | 328.5 | 328.4 | 667.7 | 51.4 | 18.9 | 89.8 | 8.4 | 243.9 | 15.2 | 910.9 | 779.8 | 814.6 | 867.7 | 765.7 | 820.1 | 701.4 | 797.1 | 729.8 | 776.5 | 171.3 | 273 | 317.6 | 238 | 318.7 | 352.1 | 314.7 | 324.3 | 483.6 | 305.7
1340 | 1146 | 567.6 | 227.04 | 265.3967 | 364.4 | 351 | 328 | 328.2 | 645.1 | 51.4 | 19 | 89.6 | 8.4 | 248.5 | 15.7 | 910.3 | 779.5 | 819 | 868.1 | 764 | 814.5 | 702.1 | 798.5 | 729.4 | 775.6 | 171.5 | 273.2 | 317.4 | 238.2 | 319.1 | 352.1 | 315.2 | 324.4 | 483.5 | 305.9
1341 | 1147 | 567.9 | 227.16 | 265.537 | 363.6 | 350.7 | 328.4 | 328 | 649.5 | 51.4 | 19 | 89.4 | 8.3 | 223.4 | 14.1 | 909.6 | 778.5 | 816.7 | 868.2 | 763.1 | 817.3 | 702.4 | 800.2 | 729.4 | 775.4 | 171.8 | 273.3 | 317.8 | 238.3 | 319.4 | 352.3 | 315.3 | 324.5 | 483.5 | 306.1
1342 | 1148 | 567.7 | 227.08 | 265.4434 | 364.2 | 350.1 | 328.7 | 327.5 | 663.2 | 51.4 | 19 | 89.2 | 7.7 | 241.8 | 12.8 | 907.8 | 778.4 | 815.9 | 867.7 | 764.1 | 820.4 | 703 | 802.4 | 729.5 | 776.4 | 172 | 273.4 | 317.9 | 238.5 | 319.9 | 352.5 | 315.7 | 324.6 | 483.7 | 306.3
1343 | 1149 | 567.9 | 227.16 | 265.537 | 363.3 | 349.4 | 327.8 | 326.5 | 669.8 | 51.3 | 19 | 89.1 | 7.3 | 239.8 | 13.7 | 908.6 | 777.8 | 817.8 | 867.8 | 764.1 | 817.7 | 704.5 | 803 | 729.4 | 778 | 172.3 | 273.6 | 317.9 | 238.7 | 320.3 | 352.7 | 316.1 | 324.7 | 483.8 | 306.5
1344 | 1150 | 568.3 | 227.32 | 265.724 | 362.8 | 349.2 | 327.5 | 326.4 | 660.7 | 51.3 | 18.9 | 89 | 7.7 | 244 | 14.3 | 907.1 | 780 | 813.7 | 868.5 | 764.5 | 818.1 | 705.9 | 805.5 | 729.2 | 780.2 | 172.5 | 273.7 | 318 | 238.9 | 320.6 | 352.9 | 316.5 | 324.8 | 483.9 | 306.6
1345 | 1151 | 568.1 | 227.24 | 265.6305 | 362.1 | 350.8 | 327 | 326.3 | 652.8 | 51.4 | 19 | 89 | 7.7 | 247.9 | 16.8 | 904.2 | 779.9 | 822.7 | 868.2 | 768 | 818.7 | 706 | 808.1 | 729.2 | 781.7 | 172.7 | 273.8 | 318.2 | 239.1 | 320.9 | 352.9 | 316.6 | 324.9 | 484 | 306.8
1346 | 1152 | 568.3 | 227.32 | 265.724 | 361.3 | 351.3 | 326.6 | 325.6 | 664.4 | 51.4 | 19 | 89 | 8.3 | 233.6 | 15 | 905.3 | 780.7 | 836.2 | 867.7 | 768.8 | 819.6 | 705.8 | 811.7 | 729.2 | 781.8 | 173 | 274 | 318.5 | 239.3 | 321.1 | 353 | 316.8 | 325 | 484.3 | 307
1347 | 1153 | 568.2 | 227.28 | 265.6772 | 361 | 352.1 | 325.6 | 324.8 | 668.1 | 51.4 | 19 | 89.2 | 8.8 | 244.2 | 13 | 907.5 | 781 | 831.4 | 867.6 | 769 | 820.5 | 705.5 | 808.8 | 729.2 | 779.9 | 173.2 | 274.2 | 318.6 | 239.5 | 321.3 | 352.9 | 316.9 | 325 | 484.6 | 307.1
1348 | 1154 | 568 | 227.2 | 265.5837 | 361.2 | 352.8 | 324.8 | 325.3 | 673.9 | 51.4 | 19 | 89.4 | 7.6 | 238.3 | 12 | 914.9 | 779.4 | 814.8 | 868.9 | 763.5 | 820.1 | 700.9 | 792.4 | 729.3 | 773.7 | 173.4 | 274.4 | 319.4 | 239.7 | 321.6 | 353 | 317 | 325.1 | 484.8 | 307.3
1349 | 1155 | 568.5 | 227.4 | 265.8175 | 361.3 | 353.4 | 325 | 325.5 | 671.9 | 51.5 | 19 | 89.6 | 7.3 | 239.6 | 12.5 | 915.6 | 774 | 812.6 | 869 | 762.4 | 818.8 | 694.7 | 779.4 | 729.1 | 769.9 | 173.7 | 274.5 | 319.5 | 239.9 | 321.9 | 353.1 | 317.3 | 325.1 | 484.8 | 307.5
1350 | 1156 | 568.4 | 227.36 | 265.7707 | 361.3 | 353.8 | 326 | 325.9 | 672.6 | 51.6 | 18.9 | 89.9 | 7 | 237.4 | 11 | 917.4 | 769.5 | 812.5 | 870.4 | 759 | 820.4 | 692.1 | 776.9 | 729 | 767.9 | 173.9 | 274.7 | 319.6 | 240.1 | 322.2 | 353.1 | 317.5 | 325.1 | 484.7 | 307.6
1351 | 1157 | 568.1 | 227.24 | 265.6305 | 362.2 | 353.4 | 326.3 | 326.1 | 679.1 | 51.7 | 18.9 | 90 | 6.3 | 245.5 | 9.4 | 917.9 | 768.2 | 809.8 | 871.2 | 757.4 | 822.5 | 691.5 | 780.5 | 729.1 | 768.1 | 174.1 | 274.9 | 319.9 | 240.2 | 322.3 | 352.9 | 317.8 | 325.2 | 484.6 | 307.8
1352 | 1158 | 568.5 | 227.4 | 265.8175 | 363 | 353.7 | 327 | 326.9 | 670.9 | 51.8 | 18.9 | 90.1 | 5.9 | 214.3 | 8.1 | 918 | 762.4 | 780.6 | 871.9 | 752 | 819.2 | 689.1 | 767.3 | 729 | 763.4 | 174.4 | 275.2 | 320.3 | 240.4 | 322.7 | 352.7 | 318.1 | 325.2 | 484.7 | 308
1353 | 1159 | 568.4 | 227.36 | 265.7707 | 363.4 | 353.4 | 327.7 | 327.8 | 658.2 | 52 | 18.9 | 90.3 | 7 | 247.5 | 6.4 | 917.6 | 760.7 | 778.4 | 871.4 | 750.3 | 817.8 | 685.9 | 761.9 | 728.4 | 760.7 | 174.6 | 275.4 | 320.4 | 240.6 | 322.9 | 352.6 | 318.6 | 325.3 | 484.6 | 308.2
1354 | 1160 | 568.4 | 227.36 | 265.7707 | 363.4 | 354.6 | 328.8 | 327.4 | 655.7 | 52.1 | 18.9 | 90.5 | 8.3 | 245.1 | 6.8 | 917.1 | 757 | 777.3 | 872.2 | 747.6 | 817 | 685.9 | 760 | 727.9 | 758.6 | 174.8 | 275.6 | 320.7 | 240.8 | 323.2 | 352.6 | 318.9 | 325.3 | 484.5 | 308.4
1355 | 1161 | 568.2 | 227.28 | 265.6772 | 364.3 | 355.3 | 329.6 | 327.5 | 659.3 | 52.1 | 18.9 | 90.7 | 8.2 | 235.8 | 8.1 | 916.5 | 753.7 | 764.8 | 872.4 | 743.8 | 815.8 | 685.9 | 759.2 | 727.7 | 755.8 | 175.1 | 275.8 | 321.1 | 241 | 323.6 | 352.6 | 319.2 | 325.4 | 484.4 | 308.5
1356 | 1162 | 568.4 | 227.36 | 265.7707 | 366.5 | 354.7 | 330.6 | 328.2 | 654.4 | 52.1 | 18.9 | 90.7 | 6.8 | 236.6 | 9.4 | 915.5 | 748.6 | 740.1 | 873.1 | 739.1 | 806.7 | 682.2 | 747.5 | 727.2 | 751.3 | 175.3 | 275.9 | 321.4 | 241.2 | 324 | 352.9 | 319.8 | 325.4 | 484.3 | 308.7
1357 | 1163 | 568.3 | 227.32 | 265.724 | 368.5 | 354 | 332.2 | 328 | 653.4 | 52.1 | 18.9 | 90.6 | 6.4 | 249.3 | 11.3 | 914.2 | 743.8 | 723 | 872.9 | 734.7 | 809 | 677.9 | 732.2 | 726.9 | 747.8 | 175.5 | 276.1 | 321.6 | 241.3 | 324 | 352.9 | 320.2 | 325.4 | 484.1 | 308.9
1358 | 1164 | 567.9 | 227.16 | 265.537 | 369 | 353.9 | 333.2 | 328.7 | 662.7 | 52.2 | 18.9 | 90.5 | 6.9 | 251.2 | 12.3 | 913.2 | 741.8 | 716.9 | 872.9 | 730.9 | 810.4 | 675.8 | 723.8 | 726.5 | 744.4 | 175.8 | 276.3 | 321.9 | 241.5 | 324.2 | 353 | 320.5 | 325.4 | 484 | 309.1
1359 | 1165 | 568.4 | 227.36 | 265.7707 | 370.1 | 354.3 | 333.4 | 329 | 668.3 | 52.1 | 18.9 | 90.5 | 6.4 | 263.6 | 12.3 | 911.7 | 746.6 | 738.3 | 871.5 | 730.9 | 815.8 | 677.2 | 737.2 | 726.3 | 746.1 | 176 | 276.5 | 321.9 | 241.7 | 324.6 | 353 | 321 | 325.5 | 483.8 | 309.3
1360 | 1166 | 568.6 | 227.44 | 265.8643 | 370.9 | 355.3 | 333.1 | 329.7 | 679.1 | 52.1 | 18.9 | 90.4 | 5.9 | 246.4 | 12.7 | 911.5 | 752.1 | 740.5 | 870 | 730 | 817.7 | 680.5 | 752.7 | 726.2 | 749.4 | 176.2 | 276.6 | 321.8 | 241.9 | 325.3 | 353.1 | 321.3 | 325.6 | 483.9 | 309.5
1361 | 1167 | 568 | 227.2 | 265.5837 | 371.5 | 355.5 | 332.9 | 330.5 | 687.5 | 52.2 | 18.9 | 90.4 | 6.4 | 250.8 | 13.6 | 911.9 | 754.5 | 750 | 869.9 | 729 | 821 | 681.4 | 758.8 | 726.1 | 746.7 | 176.5 | 276.7 | 322.2 | 242.1 | 325.7 | 353.2 | 321.7 | 325.7 | 484 | 309.7
1362 | 1168 | 568.1 | 227.24 | 265.6305 | 371.1 | 355.2 | 332.3 | 330.8 | 688 | 52.2 | 18.9 | 90.4 | 6.7 | 253.4 | 14.4 | 911.8 | 753.6 | 775.1 | 870.4 | 727.2 | 820 | 680 | 758.7 | 725.7 | 744.2 | 176.7 | 276.9 | 322.3 | 242.2 | 326 | 353.3 | 321.8 | 325.8 | 483.9 | 309.9
1363 | 1169 | 568.3 | 227.32 | 265.724 | 371.2 | 355.8 | 332.2 | 330.5 | 691.7 | 52.2 | 18.9 | 90.4 | 5.8 | 246.3 | 13.4 | 911 | 755.3 | 798.4 | 871.2 | 728.9 | 822.4 | 680.7 | 761.2 | 725.4 | 743 | 176.9 | 277.2 | 322.4 | 242.4 | 326.3 | 353.3 | 322.1 | 325.8 | 483.7 | 310
1364 | 1170 | 568.3 | 227.32 | 265.724 | 370.8 | 358.2 | 332.1 | 330.3 | 694.8 | 52.2 | 18.9 | 90.3 | 7.2 | 257.9 | 13.1 | 911.2 | 759.9 | 825.4 | 870.7 | 734.6 | 821.6 | 682.4 | 769.2 | 725.2 | 746.9 | 177.2 | 277.4 | 322.6 | 242.6 | 326.9 | 353.4 | 322.5 | 325.9 | 483.7 | 310.2
1365 | 1171 | 568.1 | 227.24 | 265.6305 | 370.6 | 359.9 | 332.1 | 331.3 | 667.3 | 52.2 | 18.9 | 90.1 | 6.9 | 253.8 | 12.8 | 910.7 | 762.4 | 840.8 | 869.1 | 737.3 | 812.9 | 680.5 | 771.8 | 724.7 | 748.6 | 177.4 | 277.7 | 322.5 | 242.8 | 327.4 | 353.4 | 322.6 | 326.1 | 483.8 | 310.4
1366 | 1172 | 568.2 | 227.28 | 265.6772 | 370 | 360.3 | 332.2 | 331.1 | 642.6 | 52.1 | 18.9 | 90 | 7.2 | 250.7 | 13.4 | 910.1 | 764.2 | 851.7 | 867.6 | 740.6 | 812.5 | 680.5 | 776.1 | 724.2 | 749.5 | 177.6 | 277.8 | 322.4 | 243 | 327.5 | 353.4 | 322.6 | 326.1 | 484 | 310.6
1367 | 1173 | 568.3 | 227.32 | 265.724 | 368.7 | 361.3 | 331.8 | 330.5 | 627.6 | 52.2 | 18.9 | 90 | 8 | 250 | 14 | 908.7 | 765.1 | 854.3 | 866.1 | 741.7 | 809.1 | 683.3 | 779.7 | 723.8 | 751.7 | 177.9 | 278 | 322.5 | 243.1 | 327.5 | 353.5 | 322.7 | 326.3 | 484.1 | 310.7
1368 | 1174 | 568.2 | 227.28 | 265.6772 | 367.5 | 361.3 | 330.9 | 329.6 | 625.4 | 52.2 | 18.9 | 90.1 | 8.2 | 258.9 | 15.4 | 910.2 | 766.5 | 853.7 | 865.4 | 740.9 | 809.7 | 685.8 | 780.6 | 723.5 | 752.4 | 178.1 | 278.2 | 322.7 | 243.4 | 327.5 | 353.4 | 322.5 | 326.4 | 484.2 | 310.9
1369 | 1175 | 568.3 | 227.32 | 265.724 | 366.8 | 359.9 | 329.9 | 327.5 | 630.1 | 52.3 | 18.9 | 90.3 | 9.5 | 266.1 | 13.9 | 911.1 | 768 | 851.4 | 864.8 | 741 | 808.4 | 686.4 | 783.4 | 723.2 | 751.3 | 178.3 | 278.3 | 322.8 | 243.5 | 327.5 | 353.2 | 322.4 | 326.4 | 484.2 | 311
1370 | 1176 | 568.1 | 227.24 | 265.6305 | 365.9 | 358.5 | 329.9 | 325.4 | 624 | 52.3 | 18.9 | 90.6 | 10.2 | 266.4 | 15.1 | 913 | 770 | 851.3 | 865.1 | 741.2 | 806.1 | 688.6 | 786 | 722.9 | 752.8 | 178.6 | 278.5 | 322.9 | 243.7 | 327.5 | 353.1 | 322.3 | 326.5 | 484.1 | 311.1
1371 | 1177 | 568.6 | 227.44 | 265.8643 | 365.2 | 357.7 | 330.1 | 323.2 | 632.4 | 52.3 | 18.9 | 90.7 | 9.4 | 265.4 | 15.8 | 912.2 | 770.9 | 832.7 | 864.3 | 741.8 | 808.6 | 689.4 | 784.7 | 723 | 751.9 | 178.8 | 278.7 | 323.1 | 243.9 | 327.5 | 352.9 | 322.3 | 326.5 | 484 | 311.3
1372 | 1178 | 568.4 | 227.36 | 265.7707 | 366 | 358.2 | 330.9 | 321.5 | 636.9 | 52.3 | 18.9 | 90.8 | 5.7 | 270.8 | 13.4 | 912.3 | 771.3 | 814.3 | 863.8 | 738.3 | 810.3 | 686.9 | 785.9 | 722.8 | 750.2 | 179 | 278.9 | 323.3 | 244.1 | 327.5 | 352.9 | 322.4 | 326.6 | 483.9 | 311.4
1373 | 1179 | 567.9 | 227.16 | 265.537 | 366.3 | 358.1 | 330.6 | 319.6 | 628.5 | 52.3 | 18.9 | 90.9 | 7.7 | 259 | 16.1 | 912.4 | 768.9 | 803.8 | 863.3 | 736.8 | 810.1 | 686.8 | 782.4 | 722.6 | 748.3 | 179.3 | 279.3 | 323.7 | 244.3 | 327.6 | 353.2 | 322.4 | 326.6 | 483.8 | 311.6
1374 | 1180 | 568.1 | 227.24 | 265.6305 | 366.2 | 357.6 | 329.8 | 319.1 | 641.1 | 52.3 | 18.9 | 91.1 | 10.2 | 250.4 | 21.2 | 913 | 764 | 790.5 | 864.5 | 733.4 | 811 | 684.9 | 773.2 | 722.5 | 744.4 | 179.5 | 279.6 | 324 | 244.5 | 327.8 | 353.6 | 322.4 | 326.7 | 483.7 | 311.7
1375 | 1181 | 567.9 | 227.16 | 265.537 | 366.4 | 355.7 | 329.7 | 320.4 | 633.8 | 52.3 | 18.9 | 91.4 | 12.3 | 255.1 | 23.2 | 912.9 | 762 | 788.1 | 866.3 | 733.1 | 810.4 | 683.6 | 774.1 | 722 | 743.6 | 179.8 | 279.8 | 323.8 | 244.7 | 327.9 | 353.6 | 322.5 | 326.8 | 483.6 | 311.9
1376 | 1182 | 567.9 | 227.16 | 265.537 | 366.5 | 355.4 | 329.8 | 321 | 630.1 | 52.2 | 18.9 | 91.7 | 10.7 | 254.2 | 24.4 | 911.7 | 766.2 | 788.6 | 865.1 | 733.5 | 813.6 | 687.9 | 781.1 | 721.8 | 747.2 | 180 | 280.1 | 323.8 | 244.9 | 328 | 353.5 | 322.5 | 326.9 | 483.5 | 312
1377 | 1183 | 567.5 | 227 | 265.3499 | 365.7 | 355.6 | 329.1 | 320.6 | 635.2 | 52.1 | 18.9 | 91.9 | 9.6 | 254.8 | 23.5 | 910.9 | 768 | 797.1 | 863.5 | 733.5 | 813.6 | 689.4 | 785.4 | 721.7 | 746.8 | 180.2 | 280.2 | 323.9 | 245.1 | 328 | 353.3 | 322.4 | 326.9 | 483.6 | 312.1
1378 | 1184 | 568.1 | 227.24 | 265.6305 | 364.7 | 355.7 | 328.3 | 320.7 | 637.8 | 51.9 | 18.9 | 91.9 | 9.6 | 245 | 22.1 | 914.2 | 768.2 | 797.6 | 863.5 | 731.7 | 814.6 | 690.7 | 789.7 | 721.4 | 747.6 | 180.5 | 280.3 | 324 | 245.3 | 327.9 | 353.2 | 322.4 | 326.9 | 483.5 | 312.3
1379 | 1185 | 567.9 | 227.16 | 265.537 | 364.1 | 355.3 | 328.8 | 320.9 | 629.2 | 51.9 | 18.9 | 91.8 | 10.1 | 251.4 | 21.9 | 914.7 | 770.8 | 785.2 | 863.6 | 731.6 | 812.1 | 691.8 | 792.9 | 721.1 | 749.4 | 180.7 | 280.5 | 324.1 | 245.5 | 327.9 | 353.1 | 322.4 | 327 | 483.4 | 312.4
1380 | 1186 | 568 | 227.2 | 265.5837 | 364.8 | 354.3 | 329.3 | 320.7 | 614.6 | 51.8 | 18.9 | 91.6 | 8.2 | 262.2 | 20 | 914.5 | 772.2 | 770.6 | 863.8 | 730.6 | 806.5 | 692.7 | 796.1 | 720.7 | 751.1 | 180.9 | 280.6 | 324.2 | 245.7 | 327.7 | 353 | 322.3 | 327.1 | 483.4 | 312.5
1381 | 1187 | 567.9 | 227.16 | 265.537 | 366.1 | 353.4 | 329.4 | 320.2 | 599.2 | 51.8 | 18.9 | 91.4 | 7.4 | 260.6 | 17.8 | 912.6 | 773.4 | 760 | 862.7 | 730.2 | 799.8 | 691.6 | 792.5 | 720 | 751 | 181.2 | 280.9 | 324.3 | 245.9 | 327.6 | 353 | 322.3 | 327.2 | 483.4 | 312.7
1382 | 1188 | 567.3 | 226.92 | 265.2564 | 366 | 353.3 | 328.6 | 319.4 | 599.5 | 51.8 | 18.9 | 91.4 | 7.7 | 252.4 | 16.8 | 909.5 | 773.8 | 773.8 | 861.4 | 731.8 | 803.7 | 692.5 | 796.5 | 719.7 | 752.5 | 181.4 | 281.1 | 324.5 | 246.1 | 327.6 | 352.8 | 322.3 | 327.2 | 483.3 | 312.8
1383 | 1189 | 567.6 | 227.04 | 265.3967 | 366.6 | 353.2 | 327.7 | 318.9 | 628 | 51.9 | 18.9 | 91.5 | 8.7 | 247.4 | 18.1 | 908.1 | 772.8 | 775.2 | 860.3 | 731.6 | 811.3 | 694.1 | 798 | 720.1 | 752.9 | 181.6 | 281.2 | 324.9 | 246.3 | 327.8 | 352.8 | 322.5 | 327.2 | 483.3 | 312.9
1384 | 1190 | 567.9 | 227.16 | 265.537 | 366.7 | 353.7 | 327.9 | 318.8 | 639.1 | 51.9 | 18.9 | 91.7 | 10.6 | 257.6 | 16.3 | 910.4 | 772.2 | 771.5 | 859.8 | 730.2 | 815.7 | 690.2 | 797.1 | 720.1 | 750.2 | 181.9 | 281.4 | 325 | 246.6 | 327.6 | 352.6 | 322.6 | 327.2 | 483.6 | 313.1
1385 | 1191 | 569.7 | 227.88 | 266.3786 | 366.9 | 354.4 | 328.3 | 319.2 | 644.9 | 51.9 | 18.9 | 92 | 10.6 | 241.8 | 15.9 | 910.8 | 773.4 | 780 | 859.5 | 730.7 | 818.9 | 688.9 | 798.9 | 720 | 752.3 | 182.1 | 281.6 | 325 | 246.8 | 327.5 | 352.5 | 322.8 | 327.2 | 483.5 | 313.2
1386 | 1192 | 574.6 | 229.84 | 268.6697 | 366.9 | 354.8 | 327.8 | 319.9 | 649.3 | 52 | 18.9 | 92.1 | 9.2 | 252.6 | 18.5 | 912.2 | 774.6 | 782 | 860 | 731.4 | 818.6 | 690.2 | 798.9 | 719.8 | 753.9 | 182.3 | 281.9 | 325 | 247 | 327.4 | 352.4 | 322.9 | 327.3 | 483.5 | 313.4
1387 | 1193 | 571.1 | 228.44 | 267.0332 | 367.5 | 354.7 | 328 | 319.5 | 634.2 | 52 | 18.9 | 92.2 | 9 | 247.8 | 22.2 | 913.2 | 775.6 | 778.6 | 861.7 | 730.4 | 813.7 | 689.9 | 799 | 719.3 | 753.6 | 182.6 | 282 | 325.2 | 247.2 | 327.2 | 352.5 | 323.1 | 327.4 | 483.6 | 313.5
1388 | 1194 | 573.3 | 229.32 | 268.0619 | 367.8 | 354.1 | 328.2 | 320.2 | 616.6 | 52 | 18.9 | 92.2 | 8.8 | 252 | 20.7 | 912.4 | 775.3 | 767.4 | 862.8 | 729.1 | 804.5 | 691.4 | 797.3 | 718.6 | 756.3 | 182.8 | 282.1 | 325.2 | 247.4 | 327.4 | 352.9 | 323.3 | 327.6 | 483.5 | 313.7
1389 | 1195 | 580.1 | 232.04 | 271.2414 | 368.7 | 354.1 | 328 | 321.3 | 602.5 | 52.1 | 18.9 | 92 | 7.4 | 256.7 | 17.2 | 911.1 | 775.5 | 767.7 | 862.3 | 731 | 801 | 693.9 | 800 | 718.1 | 758.2 | 183 | 282.2 | 325.4 | 247.6 | 327.4 | 353.1 | 323.4 | 327.7 | 483.5 | 313.9
1390 | 1196 | 587.3 | 234.92 | 274.6079 | 369.1 | 354.1 | 327.7 | 321 | 611.3 | 52.1 | 18.9 | 92 | 5.9 | 239.4 | 15.9 | 909.2 | 774.6 | 778.1 | 861.7 | 731.5 | 804.7 | 697 | 799.6 | 718.1 | 760 | 183.3 | 282.3 | 325.6 | 247.8 | 327.7 | 353.1 | 323.8 | 327.8 | 483.6 | 314
1391 | 1197 | 594.6 | 237.84 | 278.0213 | 368.9 | 355.2 | 328.8 | 320.3 | 632.9 | 52.2 | 18.9 | 92.1 | 8.3 | 228.9 | 15.6 | 909.1 | 777.5 | 786 | 861.2 | 732.1 | 809.2 | 698.3 | 801.5 | 718.3 | 761.3 | 183.5 | 282.5 | 325.7 | 248 | 327.8 | 353.6 | 323.9 | 327.9 | 483.7 | 314.1
1392 | 1198 | 602.1 | 240.84 | 281.5281 | 369.8 | 356.1 | 329.8 | 320.7 | 634.6 | 52.2 | 18.9 | 92.1 | 9.2 | 244 | 14.2 | 910.6 | 779.5 | 797 | 861.2 | 732.9 | 809.6 | 698.3 | 805 | 718.2 | 762.7 | 183.7 | 282.6 | 325.7 | 248.2 | 328.1 | 354.5 | 324 | 328.1 | 483.9 | 314.3
1393 | 1199 | 606.9 | 242.76 | 283.7725 | 369.8 | 356.6 | 330.5 | 322 | 616.8 | 52.2 | 18.9 | 92.2 | 9.5 | 248.9 | 13.1 | 910.4 | 779 | 805.1 | 861.3 | 731.9 | 807.9 | 695.6 | 799.9 | 717.9 | 761.2 | 183.9 | 282.7 | 325.6 | 248.4 | 328.5 | 354.7 | 324.1 | 328.1 | 483.9 | 314.4
1394 | 1200 | 607.7 | 243.08 | 284.1465 | 370.3 | 356.7 | 329.9 | 322.9 | 617.6 | 52.2 | 18.9 | 92.1 | 8.3 | 249.6 | 11.4 | 909.4 | 779.1 | 805.5 | 860.7 | 732.7 | 811.2 | 695.4 | 803.3 | 717.8 | 763.3 | 184.2 | 282.7 | 325.8 | 248.6 | 328.8 | 354.8 | 324.2 | 328.2 | 483.8 | 314.6
1395 | 1201 | 609.3 | 243.72 | 284.8946 | 371 | 357 | 328.8 | 323.1 | 621.9 | 52.2 | 18.9 | 92 | 7.7 | 243.5 | 12.1 | 912.6 | 780.4 | 802.5 | 860.9 | 732.6 | 802.6 | 694.3 | 799.6 | 717.6 | 763.3 | 184.4 | 282.8 | 326 | 248.7 | 328.9 | 355.2 | 324.2 | 328.4 | 483.9 | 314.7
1396 | 1202 | 611.8 | 244.72 | 286.0636 | 372 | 356.6 | 327.3 | 323.2 | 615.9 | 52.2 | 18.9 | 91.9 | 8.4 | 229.3 | 14.4 | 913.4 | 781.3 | 804.1 | 861.4 | 732.6 | 807.2 | 693.1 | 802.1 | 717.4 | 764.7 | 184.6 | 283 | 326 | 248.9 | 329.3 | 355.4 | 324.3 | 328.5 | 483.9 | 314.9
1397 | 1203 | 611.2 | 244.48 | 285.783 | 372.3 | 355.9 | 326.6 | 323.4 | 625.5 | 52.1 | 18.9 | 91.9 | 8.7 | 251.3 | 15 | 913.5 | 781.3 | 801.9 | 861.8 | 733 | 808.8 | 692.9 | 804 | 717.2 | 765 | 184.9 | 283.1 | 326.2 | 249.1 | 329.4 | 355.2 | 324.5 | 328.6 | 483.9 | 315
1398 | 1204 | 610.8 | 244.32 | 285.596 | 372.8 | 355.8 | 326 | 322.9 | 625.5 | 52 | 18.9 | 91.9 | 10 | 248.2 | 17.6 | 912.4 | 781.1 | 806.2 | 861.5 | 732.6 | 808.7 | 693.3 | 804.4 | 717.2 | 766.2 | 185.1 | 283.2 | 326.4 | 249.3 | 329.6 | 355.3 | 324.5 | 328.6 | 483.9 | 315.1
1399 | 1205 | 611 | 244.4 | 285.6895 | 373.3 | 355.9 | 326.2 | 322.8 | 626.8 | 52 | 18.9 | 92 | 11 | 224.5 | 16 | 911.2 | 781.3 | 797.1 | 861.5 | 733 | 806.2 | 693.6 | 806.5 | 717 | 767.2 | 185.3 | 283.3 | 326.5 | 249.5 | 329.7 | 355.8 | 324.8 | 328.8 | 484 | 315.3
1400 | 1206 | 612.2 | 244.88 | 286.2506 | 372.8 | 355.8 | 325.3 | 323.5 | 615.7 | 52.1 | 18.9 | 91.9 | 10.2 | 233.2 | 14.4 | 909.6 | 782.8 | 786.1 | 861.3 | 732.8 | 800.8 | 693 | 806.9 | 716.5 | 768 | 185.6 | 283.3 | 326.6 | 249.7 | 329.9 | 356.1 | 325 | 328.9 | 484 | 315.5
1401 | 1207 | 614.3 | 245.72 | 287.2325 | 373.8 | 355.9 | 324.8 | 323.8 | 610.5 | 52.2 | 18.9 | 91.7 | 9 | 237.9 | 13.5 | 911.4 | 783.4 | 768.9 | 861.2 | 731.3 | 799.2 | 693 | 805.9 | 716.3 | 767.9 | 185.8 | 283.4 | 326.8 | 249.9 | 330.2 | 356.6 | 325.3 | 329 | 484 | 315.6
1402 | 1208 | 614.5 | 245.8 | 287.326 | 373.9 | 356.1 | 324.8 | 323.9 | 598.2 | 52.2 | 18.9 | 91.7 | 7.5 | 247.6 | 17.8 | 912.8 | 781.8 | 745.7 | 862.2 | 729.4 | 785.3 | 689.1 | 795.8 | 715.8 | 766.3 | 186 | 283.6 | 326.8 | 250.1 | 330.5 | 357.1 | 325.5 | 329.2 | 483.9 | 315.8
1403 | 1209 | 613.7 | 245.48 | 286.952 | 373.4 | 355.6 | 324.1 | 324.5 | 587 | 52.3 | 18.9 | 91.6 | 7.4 | 232.4 | 18 | 912.1 | 779.3 | 748.5 | 862.3 | 728.9 | 788.2 | 687.6 | 794 | 715.4 | 765.5 | 186.3 | 283.8 | 326.9 | 250.3 | 330.8 | 357.4 | 325.8 | 329.4 | 483.9 | 316
1404 | 1210 | 611.2 | 244.48 | 285.783 | 374.4 | 355.7 | 323.4 | 324.7 | 595.2 | 52.3 | 18.8 | 91.6 | 9.3 | 242.9 | 16 | 911.5 | 778.9 | 764.8 | 862.2 | 730.9 | 789.7 | 687.9 | 793.7 | 715.1 | 767 | 186.5 | 283.9 | 327.2 | 250.5 | 331.2 | 357.7 | 326 | 329.5 | 483.8 | 316.1
1405 | 1211 | 611 | 244.4 | 285.6895 | 375.1 | 355.9 | 324.1 | 324.9 | 588 | 52.4 | 18.8 | 91.7 | 11.3 | 243.6 | 14.6 | 910.3 | 777.5 | 793.1 | 861.8 | 732.9 | 787.5 | 690.3 | 793.2 | 714.8 | 768.8 | 186.8 | 284 | 327.3 | 250.7 | 331.6 | 358.4 | 326 | 329.7 | 483.7 | 316.3
1406 | 1212 | 610.4 | 244.16 | 285.409 | 374.8 | 356.4 | 325.4 | 325.1 | 595.4 | 52.5 | 18.8 | 91.9 | 11.9 | 247.8 | 13.6 | 910.2 | 775.8 | 808.3 | 861.1 | 735.5 | 785.5 | 692.8 | 793.6 | 714.9 | 770.2 | 187 | 284.1 | 327.5 | 250.9 | 331.6 | 359.1 | 326.2 | 330 | 483.9 | 316.4
1407 | 1213 | 611.8 | 244.72 | 286.0636 | 374 | 357.1 | 327.1 | 324.4 | 590 | 52.5 | 18.8 | 92.1 | 12.4 | 247.6 | 12.1 | 910.4 | 776.3 | 813.8 | 861.6 | 736.3 | 780.7 | 692.4 | 790.9 | 714.7 | 770.7 | 187.2 | 284.2 | 327.4 | 251.1 | 331.9 | 360 | 326.5 | 330.3 | 484.2 | 316.6
1408 | 1214 | 611.4 | 244.56 | 285.8765 | 374.1 | 357.6 | 328.5 | 324.2 | 581.4 | 52.5 | 18.8 | 92.2 | 9.5 | 240.9 | 12.4 | 911 | 776.6 | 812 | 861.8 | 736.8 | 780.7 | 692.5 | 793.1 | 714.4 | 771.2 | 187.5 | 284.4 | 327.4 | 251.3 | 332 | 360.7 | 326.8 | 330.5 | 484.3 | 316.8
1409 | 1215 | 613.7 | 245.48 | 286.952 | 375.1 | 358.1 | 328.5 | 325.2 | 575.7 | 52.4 | 18.8 | 92.1 | 9 | 229.2 | 17.3 | 912.6 | 776.9 | 802.7 | 863 | 739.6 | 773.7 | 691.8 | 787.3 | 714.2 | 771.9 | 187.7 | 284.6 | 327.6 | 251.4 | 332 | 361.2 | 327 | 330.6 | 484.4 | 317
1410 | 1216 | 616.4 | 246.56 | 288.2144 | 375.7 | 358.5 | 328.4 | 325.4 | 577.1 | 52.3 | 18.8 | 92 | 9 | 211.4 | 19.7 | 910 | 776.9 | 805.3 | 862.9 | 740.5 | 779 | 692.6 | 790.6 | 714.3 | 773.6 | 187.9 | 284.7 | 327.7 | 251.6 | 332 | 362.1 | 327.2 | 330.8 | 484.4 | 317.1
1411 | 1217 | 615 | 246 | 287.5598 | 376.4 | 358.3 | 328.3 | 324.9 | 595.4 | 52.2 | 18.8 | 91.9 | 8.4 | 213.5 | 20.6 | 909.1 | 775.7 | 808 | 862.3 | 742 | 785.8 | 693 | 795.2 | 714.4 | 774.1 | 188.2 | 284.9 | 327.9 | 251.8 | 332.4 | 362.6 | 327.4 | 331 | 484.6 | 317.3
1412 | 1218 | 612.7 | 245.08 | 286.4844 | 376.1 | 359.2 | 327.9 | 324.6 | 609.9 | 52.2 | 18.8 | 92 | 8.3 | 233.8 | 17.4 | 908.8 | 776 | 802.6 | 862 | 742.9 | 789.3 | 695 | 799.6 | 714.7 | 775.1 | 188.4 | 285.1 | 328.1 | 252 | 332.5 | 363.2 | 327.5 | 331.1 | 484.8 | 317.5
1413 | 1219 | 612.3 | 244.92 | 286.2974 | 376.1 | 360.4 | 327 | 325.3 | 605.4 | 52.1 | 18.8 | 92.2 | 7.6 | 222.5 | 14.5 | 907.8 | 776.7 | 796.4 | 861.7 | 743.2 | 788.5 | 696 | 802.7 | 714.8 | 777.3 | 188.7 | 285.3 | 328.1 | 252.1 | 332.6 | 364 | 327.7 | 331.2 | 484.9 | 317.6
1414 | 1220 | 613.3 | 245.32 | 286.7649 | 376.2 | 360.5 | 326.1 | 325.6 | 626.6 | 52 | 18.8 | 92.2 | 6.8 | 225.9 | 12.8 | 906.9 | 778.2 | 803.3 | 861.3 | 745.3 | 793.5 | 696.3 | 804.2 | 715.1 | 778.5 | 188.9 | 285.4 | 328.3 | 252.3 | 332.8 | 364.5 | 327.8 | 331.5 | 485.1 | 317.7
1415 | 1221 | 613.1 | 245.24 | 286.6714 | 376 | 360.8 | 325.8 | 324.9 | 619.8 | 51.8 | 18.8 | 92.3 | 7 | 226 | 11.4 | 905.4 | 777.9 | 798 | 861.2 | 747.1 | 790.5 | 696.3 | 805.5 | 715 | 779.2 | 189.1 | 285.6 | 328.3 | 252.4 | 333 | 365.2 | 328 | 331.7 | 485.2 | 317.9
1416 | 1222 | 615 | 246 | 287.5598 | 376.4 | 361.3 | 324.7 | 324.6 | 616 | 51.8 | 18.8 | 92.4 | 7.9 | 230.6 | 10.9 | 905.8 | 779.8 | 783.6 | 861.4 | 746.1 | 784.9 | 696.6 | 808.7 | 714.8 | 781.6 | 189.4 | 285.7 | 328.5 | 252.6 | 333 | 365.9 | 328 | 331.9 | 485.2 | 318
1417 | 1223 | 615.5 | 246.2 | 287.7936 | 377.1 | 361.2 | 323.8 | 325 | 602 | 51.8 | 18.8 | 92.4 | 8.1 | 207.2 | 10.7 | 905.5 | 780.4 | 789.2 | 861.6 | 749.6 | 778.1 | 695.1 | 805 | 714.5 | 783.2 | 189.6 | 285.8 | 328.6 | 252.8 | 333.1 | 366.6 | 328.3 | 332.2 | 485.4 | 318.2
1418 | 1224 | 616 | 246.4 | 288.0274 | 377.2 | 361.5 | 324.2 | 325.8 | 610.7 | 51.8 | 18.8 | 92.5 | 10.3 | 220.7 | 11.3 | 905.1 | 779.2 | 795.9 | 861.8 | 751.2 | 782.5 | 697.2 | 803.2 | 714.6 | 783.9 | 189.8 | 285.9 | 328.7 | 252.9 | 333.4 | 366.8 | 328.5 | 332.3 | 485.7 | 318.3
1419 | 1225 | 615.8 | 246.32 | 287.9339 | 376.1 | 362.3 | 325 | 326.7 | 620.6 | 51.8 | 18.8 | 92.5 | 9.1 | 217.4 | 12.9 | 906.5 | 780.9 | 808.1 | 862.7 | 751.3 | 788.2 | 697.5 | 806.4 | 714.8 | 783.9 | 190.1 | 286.1 | 328.8 | 253.1 | 333.6 | 366.6 | 328.7 | 332.4 | 486.2 | 318.5
1420 | 1226 | 615.2 | 246.08 | 287.6533 | 375.4 | 362.1 | 325.9 | 327.8 | 623.2 | 51.8 | 18.8 | 92.5 | 8.6 | 245.2 | 11.3 | 905.5 | 779.9 | 813.7 | 862.8 | 753.2 | 787.2 | 698.5 | 808.7 | 714.8 | 785.6 | 190.3 | 286.3 | 328.9 | 253.2 | 334 | 366.5 | 328.9 | 332.5 | 486.4 | 318.7
1421 | 1227 | 614.4 | 245.76 | 287.2793 | 374.7 | 362.1 | 326.8 | 328.2 | 621.7 | 51.9 | 18.8 | 92.5 | 9.3 | 236.1 | 10.7 | 906.5 | 779.5 | 809 | 862.6 | 755 | 787 | 698.4 | 810.7 | 714.8 | 786.3 | 190.5 | 286.4 | 329 | 253.4 | 334.5 | 366.6 | 329.3 | 332.7 | 486.7 | 318.9
1422 | 1228 | 615.1 | 246.04 | 287.6066 | 374.9 | 361.6 | 327.6 | 328.8 | 627.4 | 51.9 | 18.8 | 92.5 | 8.8 | 240.9 | 10.3 | 904.5 | 779.3 | 814.1 | 862.2 | 757.4 | 793.3 | 698 | 811.2 | 715 | 788.1 | 190.7 | 286.5 | 329.1 | 253.5 | 334.9 | 366.2 | 329.5 | 332.8 | 486.9 | 319
1423 | 1229 | 615.4 | 246.16 | 287.7469 | 374.3 | 362 | 328.2 | 330 | 633.8 | 52 | 18.8 | 92.4 | 8.1 | 208.3 | 8.7 | 904.7 | 779.4 | 810 | 861.9 | 758.5 | 798.8 | 699.1 | 812.4 | 715.2 | 790.3 | 191 | 286.5 | 329.3 | 253.7 | 335.3 | 366 | 329.9 | 332.9 | 487.2 | 319.2
1424 | 1230 | 614 | 245.6 | 287.0922 | 374.1 | 361.8 | 328.1 | 330.1 | 650.6 | 52 | 18.8 | 92.4 | 6.2 | 229.6 | 9.3 | 909.9 | 780.6 | 820.1 | 863.2 | 758 | 802.4 | 698.9 | 813.4 | 715.5 | 789.8 | 191.2 | 286.5 | 329.6 | 253.9 | 335.5 | 365.9 | 330.1 | 333 | 487.6 | 319.3
1425 | 1231 | 615.5 | 246.2 | 287.7936 | 373.6 | 362.2 | 327.7 | 330.4 | 669.1 | 52 | 18.8 | 92.3 | 6.3 | 231.8 | 10.7 | 909.4 | 781.4 | 828.5 | 863.4 | 759.9 | 807.4 | 697.1 | 813.6 | 715.8 | 788.7 | 191.4 | 286.6 | 329.7 | 254.1 | 335.6 | 365.8 | 330.3 | 333.1 | 487.7 | 319.5
1426 | 1232 | 615.2 | 246.08 | 287.6533 | 372.7 | 362.7 | 327.8 | 330.8 | 680.1 | 52 | 18.8 | 92.2 | 5.9 | 240.2 | 13.1 | 908.7 | 779.6 | 837.6 | 863.1 | 759.2 | 809.7 | 697 | 810.8 | 716.2 | 789.5 | 191.7 | 286.6 | 330 | 254.2 | 335.8 | 365.4 | 330.6 | 333.1 | 487.9 | 319.7
1427 | 1233 | 615.4 | 246.16 | 287.7469 | 372.4 | 363.5 | 328.4 | 330.9 | 703 | 52 | 18.8 | 92.3 | 8.3 | 249.8 | 16.8 | 907.7 | 780 | 843.9 | 862.8 | 760.5 | 813.4 | 695.4 | 812.5 | 716.6 | 788.1 | 191.9 | 286.8 | 330.5 | 254.4 | 336.2 | 365.1 | 330.9 | 333.2 | 488.3 | 319.8
1428 | 1234 | 615.4 | 246.16 | 287.7469 | 372.7 | 364.3 | 328.7 | 332.6 | 705.4 | 52 | 18.8 | 92.5 | 9.6 | 248 | 20 | 907 | 780.5 | 846.9 | 862.9 | 762.3 | 814.2 | 698.7 | 814.2 | 716.6 | 791.2 | 192.1 | 287 | 330.5 | 254.5 | 336.5 | 365 | 331.4 | 333.3 | 488.6 | 320
1429 | 1235 | 615.6 | 246.24 | 287.8404 | 372.4 | 364.5 | 328.5 | 333.6 | 694.1 | 52.1 | 18.8 | 92.8 | 9.5 | 251 | 17.8 | 905.7 | 780.2 | 849.4 | 862.8 | 761.1 | 815.1 | 700.6 | 812.6 | 716.6 | 790.5 | 192.3 | 287.4 | 330.5 | 254.7 | 336.9 | 364.8 | 331.8 | 333.5 | 488.9 | 320.2
1430 | 1236 | 616 | 246.4 | 288.0274 | 372.6 | 364.2 | 329.3 | 333.5 | 703.3 | 52.1 | 18.8 | 92.8 | 5.3 | 233.7 | 14.9 | 907.6 | 782 | 825.7 | 863 | 759 | 816 | 700.9 | 814.5 | 716.7 | 789.5 | 192.6 | 287.7 | 330.9 | 254.9 | 337.2 | 364.7 | 332.1 | 333.6 | 489.1 | 320.3
1431 | 1237 | 615.6 | 246.24 | 287.8404 | 372.3 | 363.6 | 329.9 | 333 | 702.3 | 52.1 | 18.8 | 92.7 | 4.2 | 225.5 | 17.6 | 906.8 | 783.1 | 807 | 863.2 | 759.4 | 817.9 | 701.9 | 817.3 | 716.5 | 789.9 | 192.8 | 287.8 | 331 | 255 | 337.5 | 364.6 | 332.4 | 333.7 | 489.1 | 320.5
1432 | 1238 | 615.6 | 246.24 | 287.8404 | 372.1 | 361.8 | 330.1 | 332.2 | 691.2 | 52.2 | 18.8 | 92.6 | 7.5 | 254.1 | 16.4 | 905.4 | 782.6 | 796.1 | 863 | 759.1 | 814.6 | 703.2 | 817.8 | 716.3 | 791.6 | 193 | 287.9 | 331 | 255.2 | 337.6 | 364.8 | 332.7 | 333.8 | 489.1 | 320.7
1433 | 1239 | 615.6 | 246.24 | 287.8404 | 372.6 | 360.6 | 330.4 | 332.3 | 676.8 | 52.3 | 18.8 | 92.5 | 11.6 | 269.6 | 16.2 | 905 | 783.6 | 787 | 862.9 | 757.9 | 815.5 | 701.7 | 818.9 | 716.1 | 792.9 | 193.2 | 288 | 331.3 | 255.4 | 337.8 | 365 | 332.8 | 334 | 489.2 | 320.9
1434 | 1240 | 615.3 | 246.12 | 287.7001 | 373.5 | 360.5 | 331.2 | 331.5 | 673 | 52.3 | 18.8 | 92.4 | 12.6 | 283.6 | 15.4 | 907.5 | 784.7 | 792.9 | 863.8 | 755.3 | 815.3 | 700.7 | 820.1 | 716.1 | 788.9 | 193.4 | 288.3 | 331.9 | 255.5 | 338.1 | 364.8 | 333.1 | 334 | 489.2 | 321.1
1435 | 1241 | 615 | 246 | 287.5598 | 374.4 | 360 | 332.2 | 331.1 | 666.4 | 52.4 | 18.8 | 92.4 | 11.9 | 260 | 17.8 | 912.3 | 786.3 | 797.5 | 865.7 | 753.2 | 815.2 | 696.8 | 816.9 | 716.2 | 785.7 | 193.7 | 288.5 | 331.9 | 255.6 | 338.3 | 364.5 | 333.2 | 334.1 | 489.2 | 321.2
1436 | 1242 | 615 | 246 | 287.5598 | 375.5 | 359.5 | 333.7 | 331.7 | 662.7 | 52.4 | 18.8 | 92.4 | 9.7 | 252 | 20.5 | 909.2 | 782.8 | 810.8 | 864.9 | 754.9 | 818 | 698.8 | 814.3 | 716.3 | 787.4 | 193.9 | 288.7 | 331.9 | 255.8 | 338.6 | 364.3 | 333.4 | 334.2 | 489 | 321.4
1437 | 1243 | 614.6 | 245.84 | 287.3728 | 375.7 | 361.4 | 333.9 | 331.4 | 683.2 | 52.5 | 18.8 | 92.5 | 10.1 | 239.9 | 21.1 | 906.7 | 779.4 | 811.9 | 864.2 | 755.3 | 818.4 | 700.5 | 810.2 | 716.6 | 787.9 | 194.1 | 288.9 | 332.3 | 256 | 338.9 | 364.2 | 333.7 | 334.3 | 489.2 | 321.6
1438 | 1244 | 614.2 | 245.68 | 287.1858 | 375.5 | 364.2 | 334.5 | 332.6 | 701.3 | 52.5 | 18.8 | 92.5 | 9.6 | 241 | 20.2 | 906.3 | 778.9 | 807.8 | 863.8 | 754.6 | 819.2 | 700.1 | 809.3 | 716.9 | 787 | 194.3 | 289.2 | 332.6 | 256.1 | 339.3 | 364.1 | 334.1 | 334.3 | 489.5 | 321.8
1439 | 1245 | 613.5 | 245.4 | 286.8585 | 375.2 | 366.5 | 335.7 | 334 | 707.8 | 52.6 | 18.8 | 92.6 | 8.1 | 240.8 | 20.9 | 906.4 | 780 | 811.3 | 863.4 | 754.4 | 823.2 | 701.7 | 809.8 | 717.1 | 789.9 | 194.6 | 289.4 | 332.6 | 256.2 | 339.7 | 364.3 | 334.5 | 334.5 | 489.7 | 321.9
1440 | 1246 | 613.7 | 245.48 | 286.952 | 374.8 | 366.8 | 336.5 | 334.1 | 710.7 | 52.6 | 18.8 | 92.5 | 11.3 | 240.8 | 21.4 | 905.3 | 778.8 | 823.2 | 863 | 756.5 | 823.5 | 701.6 | 810.7 | 717.1 | 791.2 | 194.8 | 289.5 | 332.7 | 256.4 | 340.1 | 364.3 | 334.7 | 334.7 | 489.9 | 322.1
1441 | 1247 | 614.3 | 245.72 | 287.2325 | 374.6 | 366.6 | 336.4 | 334.5 | 700 | 52.5 | 18.8 | 92.5 | 12.5 | 248.2 | 21.4 | 903.8 | 777.4 | 827.7 | 862.4 | 756.8 | 822.8 | 703.7 | 811.6 | 717 | 791.6 | 195 | 289.7 | 332.8 | 256.5 | 340.3 | 364.6 | 334.9 | 334.9 | 490.2 | 322.3
1442 | 1248 | 616 | 246.4 | 288.0274 | 374.2 | 367.3 | 337.2 | 334.2 | 685 | 52.5 | 18.8 | 92.5 | 10.4 | 236.4 | 23.5 | 903.1 | 776.4 | 833 | 862 | 758.2 | 819.1 | 704.4 | 812.8 | 716.6 | 793.3 | 195.2 | 289.8 | 333 | 256.7 | 340.5 | 364.9 | 335.2 | 335 | 490.9 | 322.5
1443 | 1249 | 615.2 | 246.08 | 287.6533 | 373.3 | 367.1 | 337.4 | 333.1 | 673.5 | 52.5 | 18.8 | 92.6 | 10.2 | 236 | 19.5 | 903.7 | 777.6 | 828.1 | 862.1 | 759.4 | 817.1 | 703.5 | 815.5 | 716.3 | 794.2 | 195.4 | 289.8 | 333.1 | 256.8 | 340.8 | 364.9 | 335.1 | 335.2 | 491.4 | 322.6
1444 | 1250 | 614.8 | 245.92 | 287.4663 | 373.5 | 366.4 | 336.8 | 332.7 | 664.3 | 52.5 | 18.8 | 92.6 | 11.8 | 232.5 | 17.8 | 906.1 | 777.7 | 816.2 | 862.7 | 757.6 | 809.4 | 701.6 | 818.7 | 716 | 794.8 | 195.7 | 289.8 | 333.3 | 257 | 340.8 | 365.2 | 335.3 | 335.3 | 491.7 | 322.8
1445 | 1251 | 615.2 | 246.08 | 287.6533 | 371.2 | 366.4 | 338.8 | 334.3 | 636.3 | 52.8 | 18.8 | 92.6 | 10.1 | 240.6 | 21.6 | 909.4 | 779.5 | 797.7 | 863.8 | 758.2 | 795.3 | 700.6 | 816.8 | 715.3 | 791.3 | 195.9 | 289.8 | 333.3 | 257.2 | 340.8 | 365.7 | 335.5 | 335.6 | 491.6 | 322.5
1446 | 1252 | 614.2 | 245.68 | 287.1858 | 368.9 | 366.8 | 339.5 | 336 | 614 | 53.1 | 18.8 | 92.6 | 13.3 | 246.1 | 26.5 | 908 | 777.6 | 799.2 | 863.7 | 760.1 | 792.3 | 701.8 | 809 | 714.7 | 791.6 | 196.1 | 290 | 333.2 | 257.4 | 341 | 366 | 335.6 | 335.7 | 491.3 | 322.2
1447 | 1253 | 613.6 | 245.44 | 286.9052 | 371.5 | 366 | 337.4 | 334.8 | 610.7 | 52.8 | 18.8 | 92.5 | 14.1 | 245.6 | 26.2 | 908.1 | 777.1 | 776.8 | 863.4 | 758.7 | 793.2 | 701.2 | 805.9 | 714.4 | 792.5 | 196.3 | 290.4 | 333.4 | 257.6 | 341.1 | 366.6 | 335.8 | 335.9 | 491.6 | 322.8
1448 | 1254 | 613.1 | 245.24 | 286.6714 | 362.2 | 370.2 | 343.3 | 337.5 | 604.7 | 54.5 | 18.7 | 92.8 | 13.5 | 242.9 | 25.4 | 908.6 | 779.3 | 787.3 | 864.2 | 760 | 791.4 | 700.4 | 805.5 | 714.1 | 791.7 | 196.5 | 290.7 | 333.5 | 257.8 | 341.2 | 367.5 | 336 | 336.1 | 490.8 | 321.2
1449 | 1255 | 612.7 | 245.08 | 286.4844 | 352.7 | 375 | 348.4 | 338.8 | 596.5 | 55.9 | 18.7 | 92.9 | 11.5 | 244.6 | 25.8 | 908.4 | 778.2 | 786.2 | 864.6 | 758.9 | 793.9 | 702.3 | 805.3 | 714 | 792.3 | 196.7 | 291.1 | 333.6 | 257.9 | 341.3 | 368.1 | 336 | 336.3 | 490 | 319.9
1450 | 1256 | 613.2 | 245.28 | 286.7182 | 359.9 | 373 | 343.2 | 335 | 604.8 | 54.2 | 18.7 | 92.7 | 9.3 | 245.3 | 24.1 | 910.3 | 778.8 | 783.1 | 864.7 | 758.4 | 802.3 | 700.6 | 805.8 | 714.3 | 791.6 | 197 | 291.5 | 333.8 | 258.1 | 341.4 | 368.3 | 336.2 | 336.4 | 490.8 | 321.5
1451 | 1257 | 612.8 | 245.12 | 286.5312 | 367.3 | 371.2 | 337.9 | 332.5 | 627.8 | 52.7 | 18.8 | 92.4 | 7.5 | 223.5 | 19.2 | 911.1 | 780.8 | 777.9 | 864.8 | 757.2 | 804.3 | 701.4 | 809.4 | 714.4 | 793.5 | 197.2 | 291.7 | 334 | 258.3 | 341.6 | 368.4 | 336.5 | 336.5 | 491.8 | 323
1452 | 1258 | 613.5 | 245.4 | 286.8585 | 367.6 | 372.2 | 337.4 | 332.2 | 648.1 | 52.6 | 18.8 | 92.4 | 7.7 | 238.2 | 17.6 | 910.7 | 782.4 | 774.8 | 864.9 | 755.1 | 809.7 | 703.9 | 814.3 | 714.5 | 793.8 | 197.4 | 291.9 | 334.1 | 258.5 | 341.9 | 368.3 | 336.6 | 336.6 | 491.8 | 323.2
1453 | 1259 | 614.4 | 245.76 | 287.2793 | 370.3 | 373.2 | 335.3 | 330.3 | 651.9 | 52.1 | 18.8 | 92.3 | 6.5 | 234.8 | 18.6 | 909.8 | 782.7 | 780.2 | 864.8 | 755.3 | 815.7 | 704.7 | 816.5 | 714.8 | 794.9 | 197.7 | 292 | 334.4 | 258.6 | 342 | 368.6 | 336.8 | 336.8 | 492.2 | 323.8
1454 | 1260 | 612.8 | 245.12 | 286.5312 | 372.9 | 373.3 | 334 | 330 | 659.4 | 51.9 | 18.7 | 92.5 | 7.1 | 237.4 | 16.2 | 908.2 | 780.7 | 794.6 | 864.3 | 757.1 | 816.2 | 708.5 | 813.5 | 715 | 796.5 | 197.9 | 292.2 | 334.7 | 258.8 | 342.1 | 368.9 | 337 | 336.9 | 492.4 | 324.2
1455 | 1261 | 612.8 | 245.12 | 286.5312 | 373.2 | 373.3 | 335.1 | 331 | 665.2 | 52 | 18.7 | 92.6 | 7.9 | 224.4 | 12.2 | 908.4 | 780.1 | 793.9 | 864 | 755.8 | 819.1 | 710 | 814.1 | 715.3 | 796.9 | 198.1 | 292.2 | 334.7 | 259 | 342.3 | 368.8 | 337.3 | 337.1 | 492.9 | 324.3
1456 | 1262 | 613 | 245.2 | 286.6247 | 373.2 | 371.9 | 334.8 | 331.3 | 676.6 | 51.9 | 18.7 | 92.6 | 10.1 | 246 | 11.4 | 908.9 | 780.5 | 805.4 | 864.5 | 755.2 | 821.4 | 708.1 | 814.1 | 715.3 | 795.9 | 198.3 | 292.2 | 335 | 259.2 | 342.4 | 368.9 | 337.4 | 337.1 | 493.3 | 324.5
1457 | 1263 | 613.8 | 245.52 | 286.9987 | 373.6 | 371.6 | 335 | 331.5 | 689.4 | 52 | 18.7 | 92.5 | 10.4 | 219.7 | 13.7 | 910.9 | 782.1 | 820.3 | 865.4 | 755.3 | 821.3 | 709.2 | 813.4 | 715.2 | 797.4 | 198.5 | 292.1 | 335.1 | 259.3 | 342.4 | 368.7 | 337.4 | 337.2 | 493.3 | 324.7
1458 | 1264 | 614.3 | 245.72 | 287.2325 | 373.5 | 371.3 | 334.6 | 330.6 | 692.1 | 52 | 18.8 | 92.5 | 9.2 | 245.7 | 12.3 | 910.8 | 780.7 | 815.7 | 865.3 | 757.3 | 817 | 709.3 | 813.8 | 715.1 | 798.6 | 198.8 | 292.1 | 335.1 | 259.5 | 342.8 | 368.6 | 337.5 | 337.3 | 493.5 | 324.8
1459 | 1265 | 614.3 | 245.72 | 287.2325 | 372.1 | 371.5 | 333.9 | 330.9 | 677.7 | 52.1 | 18.8 | 92.5 | 9.4 | 227.3 | 11.8 | 911.8 | 779.4 | 806.4 | 865.4 | 758.4 | 811.2 | 707.9 | 813.8 | 714.7 | 799.4 | 199 | 292.3 | 335.2 | 259.7 | 342.9 | 368.6 | 337.7 | 337.5 | 493.8 | 324.9
1460 | 1266 | 613.7 | 245.48 | 286.952 | 371.1 | 371.5 | 333.3 | 331 | 667.9 | 52.2 | 18.8 | 92.6 | 8.9 | 238.9 | 12.7 | 912.1 | 780.3 | 808.4 | 865.4 | 758.3 | 808.9 | 709.1 | 817.6 | 714.3 | 800.2 | 199.2 | 292.3 | 335.5 | 259.8 | 342.7 | 368.6 | 337.8 | 337.6 | 494.2 | 325
1461 | 1267 | 613.7 | 245.48 | 286.952 | 370.5 | 371.2 | 334.1 | 331.8 | 679.8 | 52.4 | 18.8 | 92.5 | 10.6 | 252.3 | 12.6 | 911.1 | 780.5 | 813.4 | 865 | 758.7 | 813.9 | 711 | 815.8 | 714.7 | 800.9 | 199.4 | 292.3 | 335.8 | 260 | 342.7 | 368.4 | 338 | 337.7 | 494.4 | 325.1
1462 | 1268 | 613.8 | 245.52 | 286.9987 | 366.5 | 373 | 337.5 | 334.4 | 678.1 | 53.2 | 18.7 | 92.6 | 10.8 | 238.3 | 12.5 | 909.2 | 779 | 815.3 | 864.7 | 760.1 | 815.8 | 710.2 | 815.4 | 714.7 | 801.6 | 199.6 | 292.4 | 335.7 | 260.1 | 342.9 | 368.4 | 338.1 | 337.8 | 494.1 | 324.5
1463 | 1269 | 613.2 | 245.28 | 286.7182 | 366 | 373.3 | 339 | 335.3 | 671.7 | 53.4 | 18.7 | 92.8 | 10 | 229.2 | 12.2 | 909.5 | 778.5 | 815.2 | 865.1 | 760.4 | 813.2 | 708.7 | 816.8 | 714.4 | 802.2 | 199.9 | 292.5 | 335.9 | 260.2 | 343.2 | 368.5 | 338.2 | 337.9 | 494.5 | 324.4
1464 | 1270 | 615 | 246 | 287.5598 | 373.1 | 371.4 | 334.4 | 333.4 | 665.3 | 52.4 | 18.8 | 92.9 | 10.6 | 234.3 | 12.1 | 906.9 | 777 | 821.6 | 863.8 | 763.5 | 810.3 | 707.3 | 819.7 | 714.1 | 803.6 | 200.1 | 292.6 | 336.1 | 260.4 | 343.4 | 368.6 | 338.5 | 338.1 | 495.9 | 325.7
1465 | 1271 | 614 | 245.6 | 287.0922 | 373.4 | 371.8 | 335 | 334 | 643.4 | 52.4 | 18.8 | 93 | 9.7 | 243.8 | 14.7 | 907.2 | 776.3 | 833.7 | 863.3 | 765.1 | 805.6 | 707.5 | 819.4 | 713.9 | 804 | 200.3 | 292.8 | 336.3 | 260.5 | 343.7 | 368.9 | 338.7 | 338.3 | 496.6 | 325.9
1466 | 1272 | 612.4 | 244.96 | 286.3441 | 373.7 | 371.8 | 334.6 | 334.6 | 644.3 | 52.5 | 18.7 | 92.9 | 10.1 | 246.1 | 18.7 | 908.1 | 776.9 | 839.5 | 863.1 | 765.9 | 808.5 | 707.4 | 817.8 | 713.9 | 804.7 | 200.5 | 292.9 | 336.3 | 260.7 | 344 | 369.1 | 338.9 | 338.5 | 497.1 | 326
1467 | 1273 | 612.9 | 245.16 | 286.5779 | 372.9 | 372.7 | 335.9 | 334.9 | 637.6 | 52.5 | 18.7 | 92.7 | 10.5 | 239.5 | 20.8 | 908.9 | 779.1 | 837.8 | 862.8 | 766.5 | 807.4 | 706.3 | 820.1 | 713.8 | 803.6 | 200.8 | 293.1 | 336.3 | 260.8 | 344 | 369.3 | 339.1 | 338.6 | 497.6 | 326.1
1468 | 1274 | 613 | 245.2 | 286.6247 | 372.4 | 372 | 336.6 | 335.4 | 647 | 52.5 | 18.7 | 92.7 | 13.2 | 256.7 | 19.9 | 907.8 | 778.8 | 848.9 | 862.2 | 769 | 810.4 | 706.8 | 817.9 | 713.9 | 803.9 | 201 | 293.5 | 336.4 | 261 | 344.1 | 369.5 | 339.3 | 338.7 | 497.7 | 326.2
1469 | 1275 | 612.8 | 245.12 | 286.5312 | 372.7 | 370.7 | 336 | 335.1 | 657.1 | 52.5 | 18.7 | 92.7 | 10.9 | 224.4 | 16.8 | 907.2 | 777.9 | 838.1 | 861.7 | 768.6 | 810.9 | 707.7 | 816 | 714.1 | 804.7 | 201.2 | 293.9 | 336.6 | 261.1 | 344.1 | 369.8 | 339.5 | 338.9 | 497.9 | 326.4
1470 | 1276 | 611.6 | 244.64 | 285.9701 | 373.6 | 370.5 | 335.2 | 334.8 | 645.4 | 52.5 | 18.7 | 92.9 | 9.6 | 244.8 | 21.1 | 908.8 | 779.2 | 825 | 861.7 | 767.3 | 806.6 | 708.1 | 819.1 | 713.9 | 804.3 | 201.4 | 294.4 | 336.8 | 261.3 | 344.1 | 370.1 | 339.7 | 339.1 | 498.2 | 326.5
1471 | 1277 | 611.7 | 244.68 | 286.0168 | 374.7 | 371.1 | 334.3 | 335.6 | 638.6 | 52.5 | 18.7 | 93 | 6.4 | 236.4 | 20.4 | 911.9 | 781.9 | 811.5 | 862.3 | 765.3 | 799.7 | 706.6 | 822.6 | 713.7 | 804.3 | 201.6 | 294.8 | 336.9 | 261.4 | 344.3 | 370.4 | 339.8 | 339.3 | 498.2 | 326.7
1472 | 1278 | 611.7 | 244.68 | 286.0168 | 375.7 | 371.9 | 335.6 | 335.5 | 642.3 | 52.6 | 18.7 | 92.8 | 7.3 | 242.5 | 20.5 | 913.5 | 782.5 | 797.7 | 862.6 | 764.8 | 803.5 | 708 | 819.3 | 713.7 | 804.5 | 201.9 | 295 | 337 | 261.6 | 344.4 | 370.6 | 339.9 | 339.4 | 498.1 | 326.8
1473 | 1279 | 611.7 | 244.68 | 286.0168 | 376.2 | 371.2 | 335.4 | 335.6 | 647 | 52.6 | 18.7 | 92.7 | 10.5 | 249.1 | 19.6 | 913.6 | 782.1 | 804.9 | 862.8 | 765.1 | 803.4 | 707.8 | 818.2 | 713.8 | 804.5 | 202.1 | 295.2 | 337.2 | 261.7 | 344.7 | 370.5 | 340 | 339.5 | 498.1 | 327
1474 | 1280 | 612.1 | 244.84 | 286.2039 | 376.6 | 371.5 | 335.4 | 335.5 | 638.6 | 52.6 | 18.7 | 92.7 | 13.6 | 256 | 20.5 | 915.3 | 782.4 | 808.3 | 863.3 | 766.8 | 801.9 | 708 | 816.3 | 713.7 | 805.1 | 202.3 | 295.2 | 337.2 | 261.9 | 344.7 | 370.3 | 340 | 339.6 | 498.2 | 327.1
1475 | 1281 | 613 | 245.2 | 286.6247 | 377.2 | 371.1 | 336 | 334.4 | 627.9 | 52.6 | 18.7 | 92.7 | 10.5 | 247.1 | 21 | 915.2 | 781.9 | 800.4 | 863.3 | 765.5 | 799.9 | 706.6 | 812.9 | 713.7 | 804.2 | 202.5 | 295.3 | 337.2 | 262 | 344.5 | 369.9 | 340 | 339.7 | 498.3 | 327.3
1476 | 1282 | 612.8 | 245.12 | 286.5312 | 377.8 | 371.3 | 335.2 | 332.7 | 635.3 | 52.6 | 18.7 | 92.8 | 9.8 | 238.6 | 23.1 | 914.7 | 782.3 | 791.7 | 862.9 | 764.9 | 804.8 | 706 | 813 | 713.6 | 804.2 | 202.8 | 295.4 | 337.3 | 262.2 | 344.5 | 369.5 | 340 | 339.8 | 498.3 | 327.4
1477 | 1283 | 615.3 | 246.12 | 287.7001 | 378.6 | 371 | 334 | 331.3 | 639.6 | 52.6 | 18.7 | 92.8 | 9.3 | 243 | 24.5 | 915.1 | 782.9 | 785.5 | 862.6 | 763.5 | 805.4 | 707.5 | 814.2 | 713.6 | 803.3 | 203 | 295.5 | 337.6 | 262.3 | 344.6 | 369.2 | 340.1 | 339.9 | 498.3 | 327.5
1478 | 1284 | 646.9 | 258.76 | 302.4755 | 379.3 | 370.2 | 333.6 | 330.8 | 635.7 | 52.7 | 18.7 | 92.9 | 8.7 | 259.4 | 22.9 | 915.2 | 784.1 | 797.5 | 862.5 | 762.8 | 806.8 | 707.6 | 814.8 | 713.5 | 804.8 | 203.2 | 295.6 | 337.6 | 262.5 | 344.6 | 369.1 | 340.2 | 340 | 498.2 | 327.7
1479 | 1285 | 672.8 | 269.12 | 314.5858 | 378.9 | 369.6 | 334.2 | 330.9 | 633.9 | 52.7 | 18.7 | 92.9 | 8.7 | 260.7 | 20.7 | 913.3 | 783.8 | 816.2 | 862.3 | 764.3 | 809.4 | 706.5 | 817.5 | 713.5 | 806.3 | 203.4 | 295.6 | 337.7 | 262.6 | 344.6 | 369 | 340.2 | 340.1 | 498.2 | 327.8
1480 | 1286 | 699.5 | 279.8 | 327.0701 | 377.9 | 369.4 | 334.3 | 331.2 | 633.9 | 52.7 | 18.7 | 92.8 | 9.2 | 265.7 | 19.2 | 911.5 | 782.5 | 834.2 | 861.9 | 767.4 | 809.2 | 705.7 | 817.2 | 713.9 | 807 | 203.6 | 295.7 | 338 | 262.8 | 344.7 | 369.1 | 340.3 | 340.1 | 498.5 | 328
1481 | 1287 | 727.3 | 290.92 | 340.0687 | 376.5 | 370.9 | 334.4 | 331.7 | 650.6 | 52.7 | 18.7 | 92.7 | 10.4 | 266.7 | 21.4 | 910.8 | 781.6 | 854.3 | 861.6 | 769.4 | 813.2 | 706.4 | 816.4 | 714.2 | 807 | 203.9 | 295.8 | 338.3 | 262.9 | 344.9 | 369.5 | 340.5 | 340.2 | 499.2 | 328.1
1482 | 1288 | 725.8 | 290.32 | 339.3674 | 375.1 | 372.9 | 335.2 | 332.1 | 663.6 | 52.6 | 18.7 | 92.7 | 11.2 | 270.1 | 19.5 | 910.1 | 780.8 | 862 | 861.3 | 770.7 | 813.6 | 708.1 | 814.6 | 714.4 | 807.1 | 204.1 | 295.9 | 338.5 | 263 | 345.3 | 369.6 | 340.8 | 340.3 | 500 | 328.3
1483 | 1289 | 715.4 | 286.16 | 334.5046 | 373.8 | 373.4 | 336 | 333.3 | 680.5 | 52.6 | 18.7 | 92.6 | 9.7 | 268.8 | 15.6 | 909.9 | 780.1 | 855.3 | 860.8 | 772 | 814.7 | 709.7 | 812.8 | 714.8 | 808.1 | 204.3 | 296.1 | 338.8 | 263.2 | 345.7 | 369.9 | 341.2 | 340.4 | 500.8 | 328.4
1484 | 1290 | 723 | 289.2 | 338.0581 | 373.4 | 373.6 | 337 | 333.8 | 701.1 | 52.6 | 18.7 | 92.6 | 8.5 | 250.9 | 14 | 908.6 | 780 | 855.2 | 860.7 | 772.6 | 815.9 | 712.8 | 811.8 | 715.2 | 809.7 | 204.5 | 296.3 | 339.1 | 263.3 | 346 | 370.4 | 341.6 | 340.6 | 501.6 | 328.6
1485 | 1291 | 727.2 | 290.88 | 340.022 | 373.9 | 375.4 | 338.4 | 333.8 | 714 | 52.6 | 18.7 | 92.6 | 9.3 | 244.1 | 15.6 | 909.3 | 780.7 | 856.1 | 860.5 | 773.6 | 820.5 | 714.6 | 813.9 | 715.6 | 810.7 | 204.8 | 296.5 | 339.4 | 263.5 | 346.6 | 371.1 | 342.1 | 340.8 | 502.5 | 328.7
1486 | 1292 | 723.9 | 289.56 | 338.479 | 374.1 | 376.8 | 339.6 | 335 | 719.5 | 52.5 | 18.7 | 92.7 | 10.1 | 256.8 | 13.8 | 908.8 | 779.9 | 858.3 | 860.3 | 774.6 | 819.4 | 715.7 | 809.7 | 715.9 | 811.3 | 205 | 296.8 | 339.8 | 263.6 | 347.2 | 371.4 | 342.8 | 341 | 503.1 | 328.9
1487 | 1293 | 729.4 | 291.76 | 341.0506 | 374.2 | 377.7 | 340.5 | 336.3 | 722 | 52.5 | 18.7 | 92.5 | 9.4 | 246.6 | 14.4 | 908.7 | 780.3 | 855.9 | 860 | 774.9 | 820.5 | 716.3 | 813 | 716.2 | 811.8 | 205.2 | 297 | 340 | 263.7 | 347.7 | 372 | 343.3 | 341.2 | 503.8 | 329.1
1488 | 1294 | 729.5 | 291.8 | 341.0974 | 375.2 | 377.3 | 341.4 | 336.2 | 726.5 | 52.5 | 18.7 | 92.3 | 9.8 | 237.8 | 13.8 | 908.4 | 781 | 852.4 | 860.2 | 776.3 | 822 | 716.5 | 815.5 | 716.4 | 813.3 | 205.4 | 297.2 | 340.2 | 263.9 | 348.2 | 372.5 | 344 | 341.5 | 504.3 | 329.3
1489 | 1295 | 724.8 | 289.92 | 338.8998 | 375.5 | 377.7 | 342.8 | 338 | 724.6 | 52.5 | 18.7 | 92.3 | 8.7 | 251.3 | 13.9 | 907.9 | 780.5 | 847.6 | 859.6 | 776.6 | 825.8 | 718.4 | 814 | 716.7 | 813.4 | 205.6 | 297.3 | 340.6 | 264 | 348.7 | 373 | 344.6 | 341.7 | 504.6 | 329.5
1490 | 1296 | 729.1 | 291.64 | 340.9104 | 376.5 | 378.1 | 343.9 | 339.9 | 721.7 | 52.4 | 18.7 | 92.3 | 8.6 | 234.8 | 13.5 | 911.7 | 782 | 828.5 | 859.7 | 773.9 | 828.1 | 719.7 | 819.2 | 716.6 | 811.8 | 205.8 | 297.4 | 340.8 | 264.1 | 349 | 373.5 | 345.1 | 341.9 | 504.8 | 329.7
1491 | 1297 | 741.9 | 296.76 | 346.8953 | 377.7 | 378.3 | 344.1 | 341 | 703.3 | 52.4 | 18.7 | 92.4 | 7.2 | 237.6 | 13.4 | 912.8 | 784.8 | 801.3 | 859.8 | 770.3 | 822.5 | 718.5 | 826.3 | 716.3 | 810.7 | 206.1 | 297.5 | 340.9 | 264.3 | 349.4 | 374 | 345.4 | 342.1 | 504.8 | 329.8
1492 | 1298 | 744.1 | 297.64 | 347.924 | 379.3 | 378.1 | 345.1 | 341.6 | 688.5 | 52.4 | 18.7 | 92.3 | 7.2 | 256.7 | 13.7 | 911.1 | 784.1 | 801.9 | 859.6 | 769.5 | 823.3 | 718 | 830.3 | 716 | 809.2 | 206.3 | 297.7 | 341.2 | 264.4 | 349.7 | 374.5 | 345.7 | 342.3 | 504.7 | 330
1493 | 1299 | 746.1 | 298.44 | 348.8592 | 381.5 | 377.4 | 345.9 | 341 | 690 | 52.4 | 18.7 | 92.3 | 8.1 | 257.8 | 14.3 | 910.5 | 783.3 | 815.2 | 859.5 | 769.7 | 827.1 | 719.6 | 830.3 | 715.9 | 810.4 | 206.5 | 297.9 | 341.4 | 264.6 | 350.1 | 374.8 | 346.1 | 342.5 | 504.6 | 330.2
1494 | 1300 | 750.5 | 300.2 | 350.9165 | 382 | 378.3 | 345.3 | 341.6 | 702.2 | 52.4 | 18.7 | 92.1 | 9.6 | 235.2 | 15.9 | 908.1 | 780.9 | 827.6 | 859 | 772.1 | 827.1 | 722.3 | 825.1 | 716.3 | 811.1 | 206.7 | 298.1 | 341.8 | 264.7 | 350.6 | 375.2 | 346.6 | 342.7 | 504.8 | 330.4
1495 | 1301 | 753.2 | 301.28 | 352.179 | 382.2 | 380.1 | 345.8 | 341.5 | 715.5 | 52.4 | 18.7 | 92.2 | 10.3 | 242 | 14.3 | 908.2 | 781.2 | 817.1 | 858.6 | 771.3 | 828.2 | 722.6 | 824.9 | 716.7 | 811 | 206.9 | 298.3 | 342.5 | 264.8 | 351.4 | 375.6 | 347.2 | 342.9 | 505.9 | 330.6
1496 | 1302 | 749.9 | 299.96 | 350.636 | 382.4 | 381.3 | 347.3 | 341 | 726 | 52.4 | 18.7 | 92.2 | 8.9 | 240.7 | 14.3 | 910.1 | 781.4 | 831.7 | 858.6 | 771.8 | 828.6 | 719.8 | 827.2 | 716.9 | 807.5 | 207.2 | 298.5 | 342.9 | 265 | 352.1 | 375.9 | 347.9 | 343.1 | 506.6 | 330.8
1497 | 1303 | 750.1 | 300.04 | 350.7295 | 382.8 | 383 | 349.7 | 341.4 | 731.1 | 52.4 | 18.7 | 92.3 | 8.5 | 239.1 | 16.7 | 910.8 | 781.7 | 829.8 | 858.5 | 771.6 | 828.7 | 721.7 | 824.3 | 716.9 | 808.1 | 207.4 | 298.7 | 342.9 | 265.1 | 352.8 | 376.4 | 348.5 | 343.3 | 506.8 | 331
1498 | 1304 | 747.4 | 298.96 | 349.467 | 382.9 | 384.1 | 351.3 | 343.1 | 730.8 | 52.5 | 18.7 | 92.5 | 7.6 | 244.9 | 19.7 | 911.9 | 784.2 | 835.9 | 858.7 | 772.2 | 830.1 | 725.4 | 826.1 | 717.1 | 809.4 | 207.6 | 298.9 | 343 | 265.3 | 353.4 | 377.3 | 349.4 | 343.6 | 506.9 | 331.2
1499 | 1305 | 746.4 | 298.56 | 348.9994 | 383.6 | 384.9 | 351.4 | 344.8 | 738.4 | 52.5 | 18.7 | 92.4 | 7.9 | 244.1 | 18.9 | 911.9 | 783.4 | 852.1 | 858.9 | 773.4 | 827.3 | 726.3 | 822.2 | 717.8 | 809.5 | 207.8 | 299 | 343.7 | 265.4 | 353.9 | 377.9 | 349.9 | 343.8 | 507.2 | 331.4
1500 | 1306 | 745.6 | 298.24 | 348.6254 | 384.2 | 386.2 | 352.6 | 345.3 | 746.4 | 52.6 | 18.7 | 92.3 | 7.1 | 238.3 | 18.6 | 912.4 | 782.6 | 868.9 | 859 | 776.4 | 828 | 726.3 | 820.5 | 718 | 810.8 | 208 | 299.3 | 344.1 | 265.6 | 354.3 | 378.5 | 350.3 | 344 | 507.7 | 331.6
1501 | 1307 | 742.7 | 297.08 | 347.2694 | 384 | 387.2 | 353.7 | 345 | 738.6 | 52.6 | 18.7 | 92.3 | 7.2 | 242.1 | 19.3 | 912.2 | 782.9 | 881.3 | 858.9 | 777.7 | 830.5 | 726.3 | 822.4 | 718.1 | 812.3 | 208.3 | 299.6 | 344.2 | 265.7 | 354.8 | 378.8 | 350.6 | 344.2 | 508.2 | 331.8
1502 | 1308 | 742 | 296.8 | 346.9421 | 384.3 | 389 | 353.9 | 343.9 | 735.8 | 52.7 | 18.7 | 92.5 | 8.1 | 236.5 | 18.4 | 914 | 783.5 | 880 | 859.1 | 780.9 | 828.2 | 722.9 | 828.3 | 718.2 | 811.7 | 208.5 | 299.9 | 345 | 265.8 | 355.1 | 378.8 | 351.2 | 344.4 | 508.7 | 332
1503 | 1309 | 740.2 | 296.08 | 346.1005 | 384.8 | 392.8 | 353.8 | 342.9 | 731.1 | 52.8 | 18.7 | 93 | 8.2 | 242.2 | 15 | 913.7 | 783 | 879.7 | 859.3 | 783.1 | 827.6 | 724.8 | 830.1 | 718.4 | 812.4 | 208.7 | 300.2 | 345 | 266 | 355.4 | 379.3 | 351.6 | 344.6 | 509.2 | 332.2
1504 | 1310 | 739.8 | 295.92 | 345.9134 | 385.2 | 394.4 | 353.7 | 343.6 | 729.4 | 52.8 | 18.7 | 93.5 | 9.1 | 248.7 | 11.5 | 913.1 | 782.6 | 885.5 | 859.3 | 785.2 | 825.5 | 728.6 | 827.9 | 718.3 | 813.5 | 208.9 | 300.5 | 344.9 | 266.1 | 355.8 | 380.1 | 352.1 | 344.9 | 509.8 | 332.4
1505 | 1311 | 740.4 | 296.16 | 346.194 | 385.5 | 396 | 354.3 | 344.6 | 726.8 | 52.9 | 18.7 | 94 | 9 | 248.9 | 12.3 | 913.2 | 782.6 | 883.5 | 859.5 | 787.1 | 825.8 | 730.9 | 825.3 | 717.9 | 814.4 | 209.1 | 300.6 | 345.1 | 266.3 | 356.2 | 380.7 | 352.8 | 345.2 | 510.5 | 332.6
1506 | 1312 | 739.8 | 295.92 | 345.9134 | 385.4 | 397.3 | 353.8 | 345.3 | 713.6 | 52.9 | 18.7 | 94.4 | 7.3 | 237.8 | 13.9 | 912.8 | 781.6 | 868.6 | 859.6 | 787.7 | 825.4 | 732.8 | 823.1 | 718.2 | 814.8 | 209.4 | 300.9 | 345.3 | 266.4 | 356.8 | 381.1 | 353.3 | 345.4 | 511 | 332.7
1507 | 1313 | 736.2 | 294.48 | 344.2302 | 385.4 | 398.5 | 353.8 | 345.7 | 711.9 | 53 | 18.7 | 94.6 | 7.9 | 236.9 | 15.8 | 911.1 | 779.7 | 864.9 | 859.2 | 788.4 | 824.9 | 735.5 | 819.1 | 718.3 | 815 | 209.6 | 301 | 345.8 | 266.6 | 357.2 | 381.6 | 353.6 | 345.7 | 512.2 | 332.9
1508 | 1314 | 737 | 294.8 | 344.6042 | 385.5 | 399.7 | 354.5 | 345.8 | 706.6 | 53 | 18.7 | 94.8 | 7.2 | 240.3 | 13.5 | 909.9 | 779.6 | 875.2 | 859.2 | 791.1 | 826 | 738.9 | 819.3 | 718.3 | 815.4 | 209.8 | 301.3 | 346.2 | 266.7 | 357.5 | 382.4 | 354 | 346.1 | 513.7 | 333.1
1509 | 1315 | 737.8 | 295.12 | 344.9783 | 385.5 | 400.7 | 354.9 | 346.4 | 704.5 | 53 | 18.7 | 95 | 6.8 | 246.9 | 11 | 908.8 | 779.2 | 878.7 | 859.3 | 791.9 | 827.2 | 740.5 | 819 | 718.3 | 815.8 | 210 | 301.7 | 346.2 | 266.8 | 358.2 | 382.7 | 354.3 | 346.3 | 514.8 | 333.3
1510 | 1316 | 737.1 | 294.84 | 344.651 | 386.2 | 399.6 | 355.3 | 347.7 | 721 | 53 | 18.7 | 95.2 | 6.8 | 244.8 | 11 | 910 | 778.9 | 879.1 | 859.4 | 791.9 | 828.4 | 741.8 | 818.3 | 718.2 | 816.9 | 210.3 | 302.1 | 346.4 | 266.9 | 358.6 | 382.9 | 354.6 | 346.6 | 515.4 | 333.6
1511 | 1317 | 736.2 | 294.48 | 344.2302 | 386.6 | 399.6 | 355.1 | 348.2 | 727 | 52.9 | 18.7 | 95.4 | 6.8 | 244 | 10.3 | 909.7 | 778.9 | 871.7 | 859.9 | 792.8 | 829.2 | 744.7 | 819.3 | 718.2 | 818 | 210.5 | 302.5 | 346.5 | 267 | 358.7 | 383.3 | 354.7 | 346.8 | 515.6 | 333.7
1512 | 1318 | 738 | 295.2 | 345.0718 | 386.2 | 399.6 | 355.2 | 347.9 | 730.2 | 52.8 | 18.7 | 95.5 | 6.9 | 256.5 | 11.3 | 908.6 | 778.4 | 867.1 | 859.9 | 793.6 | 829.2 | 745.2 | 817 | 718.6 | 818.6 | 210.7 | 302.7 | 346.9 | 267.2 | 358.8 | 383.7 | 355 | 347.1 | 516.2 | 333.9
1513 | 1319 | 740 | 296 | 346.0069 | 385.3 | 399.1 | 355.1 | 347.4 | 738.9 | 52.8 | 18.7 | 95.6 | 6.1 | 254.1 | 12.1 | 909.2 | 778.5 | 869.9 | 860 | 795.2 | 826.4 | 746.8 | 814.8 | 718.7 | 819.2 | 210.9 | 302.8 | 347.4 | 267.3 | 359 | 384 | 355.4 | 347.3 | 516.9 | 334.1
1514 | 1320 | 739.6 | 295.84 | 345.8199 | 385.4 | 399.5 | 355.4 | 347.7 | 747.6 | 52.8 | 18.7 | 95.6 | 6.1 | 250.5 | 10.3 | 909.3 | 778.6 | 873.9 | 860.5 | 794.7 | 827.6 | 749.6 | 818 | 719.2 | 820.6 | 211.2 | 303 | 347.9 | 267.4 | 359.4 | 384.7 | 355.9 | 347.6 | 517.5 | 334.3
1515 | 1321 | 735.1 | 294.04 | 343.7158 | 385.7 | 400.1 | 356.4 | 347.7 | 756.4 | 52.9 | 18.7 | 95.7 | 6.4 | 256.3 | 11.1 | 909.5 | 778 | 876.7 | 860.7 | 796.1 | 828.2 | 748.3 | 819.1 | 719.4 | 820.5 | 211.4 | 303.1 | 348.8 | 267.6 | 359.8 | 384.8 | 356.4 | 347.7 | 518.1 | 334.5
1516 | 1322 | 735.7 | 294.28 | 343.9964 | 385.6 | 402.8 | 358.5 | 348 | 745.1 | 52.9 | 18.7 | 95.8 | 7.1 | 225.4 | 9.6 | 909.1 | 777.6 | 876.3 | 860.9 | 797.2 | 829.4 | 749.4 | 817.7 | 719.6 | 820.8 | 211.6 | 303.4 | 348.6 | 267.7 | 360.1 | 385 | 356.7 | 347.9 | 518.6 | 334.7
1517 | 1323 | 737.2 | 294.88 | 344.6977 | 385.7 | 402.9 | 359.7 | 349.3 | 748.7 | 52.9 | 18.7 | 96.1 | 7.2 | 254.4 | 6.7 | 909 | 776.7 | 873.1 | 861 | 797.4 | 828.5 | 750.8 | 815.2 | 719.3 | 821.5 | 211.8 | 303.7 | 348.7 | 267.8 | 360.6 | 385.5 | 357.2 | 348.2 | 519.4 | 334.9
1518 | 1324 | 735.5 | 294.2 | 343.9028 | 385.8 | 402.3 | 359.9 | 349.6 | 736.9 | 52.9 | 18.7 | 96.4 | 7 | 257.2 | 8.1 | 908.7 | 778 | 867.3 | 861.5 | 797.9 | 829.3 | 753.5 | 819.2 | 719 | 823 | 212.1 | 303.9 | 348.8 | 268 | 360.9 | 386.4 | 357.6 | 348.5 | 520.1 | 335.1
1519 | 1325 | 736 | 294.4 | 344.1366 | 385.6 | 402 | 359.8 | 350.7 | 725.8 | 53 | 18.7 | 96.5 | 6.4 | 248.1 | 9.8 | 910.2 | 778.9 | 864.9 | 862 | 798.8 | 829.5 | 755.3 | 822.5 | 718.3 | 823.5 | 212.3 | 304.1 | 349 | 268.1 | 361.3 | 386.9 | 358.1 | 348.8 | 520.6 | 335.3
1520 | 1326 | 735.7 | 294.28 | 343.9964 | 386.1 | 402 | 359.7 | 351.3 | 716.2 | 53 | 18.7 | 96.6 | 6.9 | 247 | 10.4 | 911.4 | 779.3 | 855.3 | 862.5 | 797.5 | 828.3 | 754.9 | 821.9 | 718.4 | 823.2 | 212.5 | 304.5 | 349 | 268.2 | 361.5 | 387 | 358.2 | 349.1 | 520.9 | 335.5
1521 | 1327 | 736 | 294.4 | 344.1366 | 386.9 | 402 | 359.9 | 349.7 | 720.8 | 53.1 | 18.7 | 96.7 | 6.3 | 250.2 | 10.8 | 911.3 | 779.3 | 838.7 | 862.5 | 794.5 | 829.9 | 753.7 | 822.8 | 718.6 | 820.5 | 212.8 | 305 | 349.6 | 268.4 | 361.7 | 387.2 | 358.6 | 349.3 | 521.1 | 335.7
1522 | 1328 | 735.9 | 294.36 | 344.0899 | 387.7 | 401.7 | 359.5 | 348.1 | 733.7 | 53.1 | 18.7 | 96.7 | 6.2 | 246.5 | 13.3 | 914.3 | 779.5 | 852.7 | 862.8 | 795.6 | 830.2 | 751.2 | 825.2 | 718.7 | 819.2 | 213 | 305.4 | 350.5 | 268.5 | 362.2 | 387.6 | 359 | 349.5 | 521.3 | 335.9
1523 | 1329 | 735.8 | 294.32 | 344.0431 | 388.7 | 402.6 | 360.1 | 346.7 | 748.6 | 53.2 | 18.7 | 96.9 | 6.1 | 221.5 | 14.2 | 914.7 | 777.2 | 857 | 863.1 | 795.1 | 828.8 | 747.4 | 823.6 | 718.8 | 818 | 213.2 | 305.8 | 350.9 | 268.6 | 362.5 | 387.9 | 359.3 | 349.6 | 521.7 | 336.2
1524 | 1330 | 735.6 | 294.24 | 343.9496 | 389.5 | 403.1 | 361.7 | 347.9 | 764.6 | 53.3 | 18.7 | 97.2 | 6.5 | 232.4 | 14.5 | 914.2 | 776.2 | 859.2 | 863.3 | 794.1 | 828.1 | 746.8 | 822.2 | 718.8 | 817.2 | 213.4 | 306 | 351.7 | 268.7 | 363 | 388.3 | 359.8 | 349.8 | 522.6 | 336.4
1525 | 1331 | 734.6 | 293.84 | 343.482 | 390.5 | 404.8 | 362.4 | 349.4 | 777.8 | 53.3 | 18.7 | 97.4 | 6.3 | 235 | 15.1 | 915.1 | 775.4 | 870.4 | 863.2 | 793.3 | 826.7 | 747.2 | 822.1 | 718.8 | 816.6 | 213.7 | 306.5 | 352.1 | 268.9 | 363.5 | 388.2 | 360.3 | 349.9 | 523.1 | 336.6
1526 | 1332 | 734.3 | 293.72 | 343.3418 | 391.2 | 406.7 | 362.2 | 350.8 | 785.4 | 53.4 | 18.7 | 97.5 | 6.6 | 240.2 | 14.5 | 915.6 | 773.6 | 867.4 | 863.2 | 794.1 | 823.5 | 748.1 | 819.6 | 719.2 | 815.8 | 213.9 | 307 | 352.3 | 269 | 364 | 388.3 | 361.1 | 350.1 | 523.7 | 336.8
1527 | 1333 | 735 | 294 | 343.6691 | 391.3 | 407.7 | 362.2 | 351.6 | 783.1 | 53.5 | 18.6 | 97.5 | 6.1 | 263.8 | 12.2 | 917.1 | 772 | 866.9 | 863.3 | 794.5 | 824.8 | 754.5 | 815.9 | 719 | 816.1 | 214.1 | 307.3 | 352.4 | 269.1 | 364.6 | 388.3 | 361.6 | 350.4 | 524.3 | 337.1
1528 | 1334 | 733.8 | 293.52 | 343.108 | 392 | 408 | 362.5 | 352.5 | 780.4 | 53.6 | 18.6 | 97.3 | 6.2 | 240.5 | 9 | 918.2 | 773.5 | 849.1 | 863.8 | 791.6 | 826.3 | 758.8 | 815.8 | 718.5 | 816 | 214.4 | 307.6 | 352.8 | 269.2 | 365.1 | 388.5 | 362.2 | 350.6 | 524.9 | 337.3
1529 | 1335 | 734.9 | 293.96 | 343.6223 | 392.7 | 406.9 | 362.1 | 353.7 | 777.8 | 53.6 | 18.6 | 97.1 | 7.7 | 230.2 | 7.9 | 918.1 | 773.5 | 840.3 | 864.1 | 791.4 | 827.6 | 763.3 | 821.4 | 718.3 | 817.2 | 214.6 | 307.8 | 353 | 269.4 | 365.4 | 388.5 | 362.5 | 350.9 | 525.2 | 337.5
1530 | 1336 | 734 | 293.6 | 343.2015 | 393.2 | 405.3 | 362.4 | 354.7 | 773.6 | 53.7 | 18.6 | 96.9 | 7.5 | 242 | 7.6 | 916.4 | 772.1 | 847.5 | 864 | 793.5 | 828.7 | 767.9 | 820.6 | 718.4 | 817.7 | 214.8 | 308 | 353.3 | 269.5 | 365.6 | 388.5 | 362.7 | 351.1 | 525.3 | 337.7
1531 | 1337 | 736.1 | 294.44 | 344.1834 | 394.4 | 405.3 | 362 | 354.3 | 777.1 | 53.7 | 18.6 | 96.8 | 8.1 | 225.8 | 6.7 | 914.6 | 770.3 | 846.5 | 863.6 | 794.4 | 828 | 771.9 | 816.5 | 718.6 | 819.4 | 215 | 308.2 | 353.7 | 269.6 | 366.3 | 388.8 | 363.1 | 351.3 | 525.8 | 338
1532 | 1338 | 735.2 | 294.08 | 343.7626 | 394.8 | 405.5 | 360.7 | 354.4 | 777.3 | 53.7 | 18.6 | 96.6 | 7.2 | 240.5 | 6.8 | 912.2 | 768.8 | 850.9 | 863.3 | 794.4 | 824.6 | 774.2 | 815.3 | 718.4 | 820 | 215.3 | 308.4 | 354.2 | 269.7 | 366.9 | 389 | 363.6 | 351.6 | 526.8 | 338.2
1533 | 1339 | 733.1 | 293.24 | 342.7807 | 393.9 | 407.3 | 361.7 | 354.3 | 766.8 | 53.8 | 18.6 | 96.5 | 7.3 | 240.1 | 9.3 | 910.9 | 768.5 | 847.5 | 862.9 | 794.8 | 824.6 | 776.4 | 817.3 | 718.6 | 821.1 | 215.5 | 308.5 | 354.2 | 269.8 | 367.4 | 389.4 | 364 | 351.9 | 527.7 | 338.4
1534 | 1340 | 735.9 | 294.36 | 344.0899 | 393.1 | 409.4 | 363.6 | 354.7 | 756.2 | 53.8 | 18.6 | 96.5 | 7.6 | 241.3 | 11.9 | 911.8 | 769.3 | 853.5 | 862.7 | 794.6 | 826.2 | 774.4 | 817.3 | 718.7 | 821.1 | 215.8 | 308.7 | 354.5 | 270 | 368 | 389.5 | 364.5 | 352.1 | 528.8 | 338.7
1535 | 1341 | 737.2 | 294.88 | 344.6977 | 392.8 | 410.2 | 364.2 | 354.6 | 749 | 53.9 | 18.6 | 96.6 | 6.7 | 226.4 | 13.7 | 910.6 | 770.5 | 842.3 | 862.5 | 791.6 | 828.3 | 778.1 | 817.9 | 718.4 | 821 | 216 | 308.9 | 354.6 | 270.1 | 368.2 | 389.8 | 364.8 | 352.4 | 529.7 | 338.9
1536 | 1342 | 736.5 | 294.6 | 344.3704 | 393 | 408.8 | 364.5 | 354.9 | 730.6 | 53.9 | 18.6 | 96.5 | 6.8 | 240.8 | 11.8 | 911.1 | 772.7 | 821.8 | 862.6 | 788.5 | 829.4 | 781.4 | 822.2 | 717.5 | 818.4 | 216.2 | 309.1 | 354.8 | 270.2 | 368.9 | 390.3 | 365.1 | 352.7 | 529.8 | 339.1
1537 | 1343 | 736.1 | 294.44 | 344.1834 | 394.4 | 407.7 | 365 | 355.3 | 719.1 | 53.9 | 18.6 | 96.5 | 7.8 | 215.2 | 12.1 | 910.9 | 770.8 | 825.7 | 862.5 | 788.9 | 829.4 | 782.6 | 822.1 | 717.2 | 817.9 | 216.5 | 309.2 | 355.2 | 270.4 | 369.2 | 390.3 | 365.6 | 352.9 | 529.6 | 339.3
1538 | 1344 | 737.3 | 294.92 | 344.7445 | 396.1 | 408.9 | 365.2 | 354 | 733.4 | 53.9 | 18.6 | 96.4 | 7.7 | 211.3 | 11.7 | 910.1 | 769.7 | 809 | 862.1 | 785.6 | 829.9 | 783.6 | 820.4 | 716.9 | 817.4 | 216.7 | 309.4 | 355.6 | 270.5 | 369.7 | 390.3 | 365.9 | 353 | 529.5 | 339.5
1539 | 1345 | 738.6 | 295.44 | 345.3523 | 397.4 | 409.4 | 364.6 | 352.3 | 727.5 | 53.9 | 18.6 | 96.2 | 7.2 | 214 | 11.5 | 910.7 | 768.7 | 814.9 | 862.1 | 786.5 | 828.6 | 784 | 823.5 | 716.8 | 817 | 216.9 | 309.5 | 355.6 | 270.6 | 370 | 390.6 | 366.2 | 353.3 | 529.4 | 339.7
1540 | 1346 | 738.7 | 295.48 | 345.3991 | 397.9 | 409.1 | 364.1 | 350.8 | 716.8 | 53.9 | 18.6 | 96.2 | 7.2 | 214.9 | 11.6 | 911.2 | 767.6 | 831.3 | 861.9 | 787 | 828.4 | 787.7 | 827.2 | 716.6 | 819.7 | 217.2 | 309.7 | 355.8 | 270.7 | 370.2 | 390.8 | 366.4 | 353.5 | 529.4 | 340
1541 | 1347 | 734.8 | 293.92 | 343.5755 | 397.4 | 409.6 | 363.9 | 350.3 | 734.3 | 53.9 | 18.6 | 96.1 | 6.5 | 221.9 | 13.8 | 913.7 | 767.2 | 827.5 | 862.1 | 784.6 | 826.6 | 787.4 | 824.5 | 716.8 | 817.6 | 217.4 | 309.8 | 356.7 | 270.9 | 370.7 | 391 | 366.9 | 353.7 | 530.4 | 340.1
1542 | 1348 | 733.5 | 293.4 | 342.9677 | 397.6 | 410.4 | 363.6 | 350.1 | 749.8 | 53.9 | 18.6 | 96.1 | 6.4 | 240.9 | 10.7 | 913.8 | 768.5 | 813.6 | 862.1 | 781.2 | 831.4 | 786.8 | 831.7 | 717 | 815 | 217.6 | 310 | 357.1 | 271 | 371.2 | 391.2 | 367.5 | 354 | 531.1 | 340.4
1543 | 1349 | 734.6 | 293.84 | 343.482 | 398.8 | 413.1 | 364.1 | 350.7 | 754.1 | 53.9 | 18.6 | 96.1 | 6.2 | 234.4 | 11.2 | 915.5 | 768.1 | 791 | 862.2 | 777.7 | 833.2 | 785.3 | 832.3 | 716.9 | 811.6 | 217.9 | 310.2 | 357.5 | 271.1 | 371.8 | 391.4 | 367.9 | 354.2 | 531.1 | 340.6
1544 | 1350 | 734.4 | 293.76 | 343.3885 | 400.8 | 414.6 | 363.3 | 351.3 | 758.6 | 54 | 18.6 | 96 | 6.6 | 243.3 | 10.4 | 918.7 | 767.9 | 769.8 | 862.6 | 774.1 | 832.3 | 782 | 833.9 | 716.7 | 807.6 | 218.1 | 310.4 | 357.8 | 271.2 | 372.6 | 391.7 | 368.3 | 354.4 | 531 | 340.9
1545 | 1351 | 733.1 | 293.24 | 342.7807 | 403.1 | 414 | 362 | 352.3 | 761.4 | 54 | 18.6 | 96 | 7.5 | 240.8 | 10.4 | 920.2 | 766.9 | 784.2 | 863.5 | 771.6 | 832.1 | 779.8 | 832.8 | 716.4 | 804.4 | 218.4 | 310.6 | 358 | 271.4 | 372.9 | 392 | 368.7 | 354.7 | 530.9 | 341.1
1546 | 1352 | 734 | 293.6 | 343.2015 | 405.4 | 414.7 | 362 | 352.8 | 762.4 | 54.1 | 18.6 | 96 | 7.9 | 244 | 11.8 | 920.2 | 766.9 | 792.6 | 863.6 | 768.6 | 831.7 | 777.5 | 829.5 | 716 | 802.8 | 218.6 | 310.9 | 358.3 | 271.5 | 373.3 | 391.8 | 369 | 354.9 | 530.8 | 341.4
1547 | 1353 | 734.6 | 293.84 | 343.482 | 406.7 | 414.5 | 363.3 | 353.9 | 760.8 | 54.1 | 18.6 | 96 | 6.8 | 239.8 | 12.3 | 921.2 | 766.6 | 771.5 | 863.9 | 765.6 | 832.5 | 777.2 | 830.1 | 715.5 | 801.9 | 218.9 | 311.1 | 358.8 | 271.7 | 373.7 | 391.7 | 369.5 | 355.1 | 530.8 | 341.6
1548 | 1354 | 733.1 | 293.24 | 342.7807 | 408.1 | 413.4 | 364.1 | 356.2 | 761.6 | 54.1 | 18.6 | 95.9 | 7 | 241.9 | 11.5 | 923.2 | 767.2 | 767.2 | 864.7 | 761 | 832 | 775.7 | 829.9 | 715.5 | 799 | 219.1 | 311.3 | 359.3 | 271.8 | 374.2 | 391.7 | 369.9 | 355.3 | 530.8 | 341.9
1549 | 1355 | 733.2 | 293.28 | 342.8274 | 409.5 | 413.7 | 364.3 | 357.7 | 768 | 54 | 18.6 | 95.8 | 6 | 233.9 | 11.3 | 923.4 | 765.1 | 799.7 | 865.2 | 764 | 832.4 | 778.9 | 820.9 | 715.5 | 802.3 | 219.4 | 311.5 | 359.5 | 271.9 | 374.7 | 391.7 | 370.2 | 355.6 | 530.8 | 342.1
1550 | 1356 | 730.6 | 292.24 | 341.6117 | 409.9 | 416.4 | 364.5 | 358.6 | 763.2 | 54 | 18.6 | 95.8 | 6.9 | 233.1 | 9.4 | 920.7 | 762.5 | 823.7 | 865.1 | 766.4 | 831.1 | 781.9 | 815.4 | 715.6 | 804.6 | 219.6 | 311.7 | 359.6 | 272 | 374.8 | 391.8 | 370.5 | 355.8 | 531 | 342.4
1551 | 1357 | 728 | 291.2 | 340.396 | 409.5 | 416.9 | 365.8 | 359.4 | 749.7 | 54 | 18.6 | 96 | 8.4 | 260.3 | 6.5 | 918.9 | 760.5 | 840.5 | 864.7 | 767 | 830.6 | 783.6 | 812.1 | 715.4 | 806.8 | 219.9 | 311.9 | 359.6 | 272.2 | 374.6 | 392.1 | 370.4 | 356 | 531.5 | 342.6
1552 | 1358 | 730.7 | 292.28 | 341.6585 | 408.6 | 417.1 | 365.5 | 358.5 | 730.7 | 53.9 | 18.6 | 96.2 | 7 | 285.6 | 5.9 | 917.1 | 759.3 | 855.6 | 864.1 | 770.2 | 824 | 789.4 | 816.7 | 715.1 | 809.4 | 220.1 | 312.2 | 359.8 | 272.3 | 374.7 | 392.8 | 370.4 | 356.4 | 532.2 | 342.8
1553 | 1359 | 731.1 | 292.44 | 341.8455 | 409.1 | 419 | 365.1 | 357 | 716.9 | 53.7 | 18.6 | 96.4 | 7.9 | 236.5 | 6.8 | 917.7 | 760.3 | 862.8 | 863.6 | 775.3 | 817 | 787.9 | 820.4 | 714.8 | 810.9 | 220.4 | 312.5 | 360 | 272.4 | 374.9 | 393.6 | 370.6 | 356.7 | 533.2 | 343
1554 | 1360 | 731.2 | 292.48 | 341.8923 | 409.1 | 421 | 365.4 | 355.5 | 702.5 | 53.7 | 18.6 | 96.5 | 7.5 | 211.1 | 8.1 | 918.8 | 762.4 | 868.6 | 863.7 | 777.8 | 817.9 | 778.9 | 820.2 | 714.4 | 811.5 | 220.6 | 312.7 | 360.1 | 272.6 | 375 | 394 | 370.8 | 357 | 534.3 | 343.2
1555 | 1361 | 730.1 | 292.04 | 341.3779 | 408 | 422.5 | 365.7 | 355.5 | 699.1 | 53.8 | 18.6 | 96.6 | 6.6 | 221.4 | 7.2 | 916.2 | 762 | 870.6 | 863.4 | 779.1 | 820.2 | 780.2 | 816.7 | 714.4 | 811.9 | 220.9 | 313 | 360.3 | 272.7 | 375.2 | 394.2 | 370.8 | 357.2 | 535.2 | 343.4
1556 | 1362 | 730.1 | 292.04 | 341.3779 | 406.8 | 421.9 | 365.8 | 354.6 | 702.3 | 53.8 | 18.6 | 96.7 | 7.1 | 224.9 | 6.8 | 916.4 | 761.9 | 861.6 | 863.3 | 779.5 | 819.5 | 781.8 | 815.6 | 714.1 | 812.4 | 221.2 | 313.2 | 360.4 | 272.9 | 375.2 | 394.5 | 370.8 | 357.5 | 535.7 | 343.6
1557 | 1363 | 728 | 291.2 | 340.396 | 406.7 | 420.5 | 365.6 | 354.4 | 703.8 | 53.8 | 18.6 | 97 | 8.9 | 253.9 | 8.3 | 916.2 | 762.3 | 865.1 | 863.4 | 781.5 | 817.6 | 782.9 | 814.1 | 713.3 | 813.8 | 221.4 | 313.4 | 360.6 | 273 | 375.5 | 395.1 | 371.1 | 357.8 | 536 | 343.8
1558 | 1364 | 727.1 | 290.84 | 339.9752 | 405.9 | 419.2 | 364.6 | 354.2 | 703.7 | 53.8 | 18.6 | 97.2 | 8.4 | 233.8 | 7.6 | 915.8 | 762.3 | 856.1 | 863.2 | 781.4 | 818 | 785.6 | 808.8 | 713.4 | 813.9 | 221.7 | 313.6 | 360.8 | 273.1 | 375.9 | 395.3 | 371.4 | 358 | 536.3 | 344
1559 | 1365 | 728.1 | 291.24 | 340.4428 | 405.9 | 418.8 | 363.9 | 355.2 | 712.7 | 53.9 | 18.6 | 97.4 | 8.8 | 259.2 | 6.9 | 916.7 | 763.4 | 820.9 | 863.5 | 779.3 | 814.1 | 788.4 | 810 | 712.8 | 814.2 | 222 | 313.9 | 361.3 | 273.3 | 375.8 | 395.9 | 371.6 | 358.4 | 536.7 | 344.2
1560 | 1366 | 728.5 | 291.4 | 340.6298 | 406.8 | 418.6 | 364.3 | 356.1 | 692.5 | 54 | 18.6 | 97.5 | 7.9 | 210.3 | 7.8 | 920.2 | 763.5 | 798.6 | 864.2 | 776.2 | 804.8 | 790.8 | 808.7 | 712 | 813.9 | 222.3 | 314.1 | 361.3 | 273.4 | 376.2 | 396.9 | 371.8 | 358.7 | 536.7 | 344.5
1561 | 1367 | 728.5 | 291.4 | 340.6298 | 407.1 | 419.1 | 364.8 | 356.9 | 688.3 | 54.1 | 18.6 | 97.6 | 6.6 | 254.7 | 7.7 | 921.5 | 763.9 | 788.4 | 864.2 | 774.7 | 807.9 | 791.9 | 804 | 711.5 | 811.4 | 222.6 | 314.4 | 361.5 | 273.5 | 376.1 | 397.1 | 371.8 | 359 | 536.6 | 344.7
1562 | 1368 | 729.5 | 291.8 | 341.0974 | 406.2 | 422.2 | 365.2 | 357.1 | 707.6 | 54.2 | 18.6 | 97.7 | 6.9 | 242.5 | 12.3 | 921.7 | 763.3 | 799.5 | 864.2 | 775.2 | 812.4 | 791.7 | 803.1 | 711.6 | 811.4 | 222.9 | 314.6 | 362 | 273.7 | 376.4 | 397.1 | 372.1 | 359.2 | 536.6 | 344.9
1563 | 1369 | 726.4 | 290.56 | 339.6479 | 405.8 | 425.1 | 365 | 356.5 | 718.6 | 54.3 | 18.6 | 97.8 | 8.1 | 240.1 | 15.4 | 921.9 | 763.4 | 812.8 | 864.5 | 774.9 | 815.8 | 795.6 | 806.2 | 711.8 | 814 | 223.1 | 314.9 | 362 | 273.8 | 376.8 | 397.1 | 372.3 | 359.4 | 536.7 | 345.1
1564 | 1370 | 727.8 | 291.12 | 340.3025 | 406 | 425.8 | 363.8 | 356.7 | 715.6 | 54.4 | 18.6 | 97.8 | 7.9 | 250.5 | 14.9 | 921.2 | 763.3 | 816.9 | 864.5 | 775.7 | 815.8 | 797.8 | 807.1 | 711.8 | 815 | 223.4 | 315.1 | 362.1 | 274 | 376.9 | 397 | 372.4 | 359.6 | 537 | 345.4
1565 | 1371 | 727.9 | 291.16 | 340.3493 | 406.8 | 425.1 | 362.8 | 357.3 | 706.6 | 54.5 | 18.6 | 98 | 9.6 | 247.3 | 14.9 | 919.9 | 763.7 | 819.3 | 864.5 | 775.8 | 816.2 | 800.5 | 806 | 712.1 | 816.5 | 223.7 | 315.3 | 362.3 | 274.1 | 377.2 | 397 | 372.6 | 359.9 | 537.3 | 345.6
1566 | 1372 | 727.6 | 291.04 | 340.209 | 407.7 | 425.3 | 363 | 357.9 | 717.8 | 54.6 | 18.5 | 98.3 | 12.2 | 233.6 | 16.1 | 919.2 | 763.1 | 829.2 | 864.4 | 776.8 | 816.6 | 802.5 | 803.5 | 712.4 | 817.5 | 224 | 315.4 | 362.7 | 274.2 | 377.3 | 396.9 | 372.8 | 360.1 | 537.6 | 345.9
1567 | 1373 | 727.9 | 291.16 | 340.3493 | 407.8 | 425.4 | 363.6 | 357.6 | 738.4 | 54.6 | 18.6 | 98.7 | 13.4 | 258.2 | 16.1 | 919.7 | 761.6 | 833.3 | 864.3 | 777.1 | 814.3 | 799.3 | 800.6 | 712.8 | 817.7 | 224.3 | 315.7 | 363.2 | 274.4 | 377.5 | 396.8 | 373.1 | 360.2 | 538.1 | 346.1
1568 | 1374 | 729 | 291.6 | 340.8636 | 409.2 | 426.4 | 363.3 | 358.7 | 755.8 | 54.7 | 18.5 | 98.9 | 12.3 | 252.9 | 17.9 | 919.5 | 760.9 | 836 | 864.3 | 777.4 | 814.2 | 798.8 | 799.6 | 713.1 | 817.6 | 224.6 | 315.9 | 363.6 | 274.5 | 377.8 | 396.8 | 373.5 | 360.4 | 538.8 | 346.3
1569 | 1375 | 728.2 | 291.28 | 340.4895 | 410.6 | 425.3 | 362.7 | 358.8 | 759.5 | 54.6 | 18.5 | 98.8 | 11.9 | 252 | 17.8 | 919.3 | 760.6 | 846.8 | 864.2 | 777.7 | 814.6 | 801.3 | 801.4 | 713 | 818.9 | 224.9 | 316.2 | 363.7 | 274.7 | 378 | 397 | 373.8 | 360.6 | 539.4 | 346.6
1570 | 1376 | 726.8 | 290.72 | 339.8349 | 410 | 423.3 | 362.8 | 359.7 | 760.6 | 54.6 | 18.5 | 98.5 | 9.8 | 237 | 17 | 919.2 | 761.2 | 854.5 | 864.1 | 779.5 | 813 | 801.3 | 801.1 | 712.7 | 820.1 | 225.1 | 316.5 | 363.9 | 274.8 | 378.4 | 397.6 | 374.1 | 360.9 | 539.7 | 346.8
1571 | 1377 | 726.5 | 290.6 | 339.6947 | 410.5 | 422.2 | 363 | 360.1 | 751.9 | 54.6 | 18.5 | 98.4 | 10.1 | 231 | 14.6 | 918.7 | 761.2 | 861.4 | 864.1 | 779.8 | 813.6 | 799.2 | 800.4 | 712.7 | 821 | 225.4 | 316.8 | 364 | 275 | 378.5 | 397.9 | 374.1 | 361.1 | 540.4 | 347
1572 | 1378 | 724.8 | 289.92 | 338.8998 | 410.8 | 421.8 | 363.4 | 359.8 | 761.2 | 54.6 | 18.5 | 98.3 | 8.6 | 243.4 | 18 | 917.7 | 760.9 | 862.4 | 863.9 | 780.9 | 813.5 | 800.3 | 800.3 | 713.3 | 821.3 | 225.7 | 317 | 364.6 | 275.1 | 378.4 | 397.9 | 374.1 | 361.3 | 541.2 | 347.2
1573 | 1379 | 725.7 | 290.28 | 339.3206 | 410.7 | 423.5 | 364.9 | 359.8 | 754.6 | 54.6 | 18.5 | 98.2 | 8.7 | 241 | 19 | 916.4 | 760.8 | 863.7 | 863.6 | 781.4 | 814.5 | 800 | 803.3 | 713 | 822.1 | 226 | 317.3 | 365.1 | 275.3 | 379 | 397.8 | 374.3 | 361.4 | 541.8 | 347.4
1574 | 1380 | 725.2 | 290.08 | 339.0868 | 410 | 424.8 | 366.6 | 359.2 | 761 | 54.7 | 18.5 | 98.3 | 8.8 | 247.3 | 18.3 | 916.5 | 760.1 | 864.7 | 863.2 | 783.4 | 810.4 | 803.5 | 796.9 | 713 | 822.5 | 226.2 | 317.6 | 365.3 | 275.4 | 379.4 | 397.6 | 374.7 | 361.6 | 542.7 | 347.6
1575 | 1381 | 724 | 289.6 | 338.5257 | 408.2 | 425.4 | 367.7 | 359.6 | 773.5 | 54.7 | 18.5 | 98.3 | 7.9 | 254.2 | 20.1 | 915.2 | 758.7 | 861 | 862.6 | 785.1 | 809.5 | 808.2 | 794.8 | 713.9 | 822.5 | 226.5 | 318 | 365.8 | 275.6 | 379.8 | 397.7 | 375.3 | 361.8 | 543.6 | 347.9
1576 | 1382 | 725.3 | 290.12 | 339.1336 | 407.1 | 426.3 | 368 | 361 | 776.6 | 54.8 | 18.5 | 98.4 | 7.2 | 253.3 | 21.7 | 913.3 | 757.4 | 863.5 | 862.1 | 785.8 | 808.5 | 809.3 | 793.4 | 714.1 | 822.5 | 226.8 | 318.3 | 366 | 275.7 | 380.1 | 397.7 | 375.8 | 362 | 544.6 | 348.1
1577 | 1383 | 725.3 | 290.12 | 339.1336 | 405.9 | 427.6 | 368.3 | 361.8 | 763.2 | 54.8 | 18.5 | 98.3 | 6.9 | 257.4 | 19.3 | 911.3 | 756.7 | 864.2 | 861.4 | 786.9 | 807.2 | 811.6 | 794 | 714.4 | 823.8 | 227.1 | 318.6 | 366 | 275.9 | 380.4 | 398 | 376.2 | 362.3 | 545.7 | 348.4
1578 | 1384 | 722.9 | 289.16 | 338.0114 | 405.4 | 427.4 | 368.9 | 362.1 | 749.3 | 54.8 | 18.5 | 98.4 | 7.9 | 263.1 | 19.1 | 911.5 | 756.6 | 872.5 | 861 | 787.6 | 808 | 815.5 | 794.4 | 714.4 | 824.5 | 227.3 | 318.9 | 366.1 | 276 | 380.4 | 398.3 | 376.6 | 362.5 | 546.8 | 348.6
1579 | 1385 | 723.3 | 289.32 | 338.1984 | 405.5 | 428.1 | 369.4 | 362.5 | 754.1 | 54.8 | 18.5 | 98.4 | 7.4 | 266.2 | 19.9 | 910.9 | 756.8 | 880.6 | 860.7 | 789 | 807.5 | 818.3 | 794.8 | 714.9 | 825.1 | 227.6 | 319.1 | 366.5 | 276.2 | 380.5 | 398.4 | 376.7 | 362.8 | 547.8 | 348.9
1580 | 1386 | 723.2 | 289.28 | 338.1517 | 404.8 | 429.2 | 370 | 362.6 | 754 | 54.9 | 18.5 | 98.5 | 7.3 | 268.9 | 23.6 | 910.2 | 757.1 | 884.6 | 860.5 | 789.9 | 807.9 | 817.3 | 795.5 | 715 | 826.5 | 227.9 | 319.3 | 366.9 | 276.3 | 380.6 | 398.5 | 377 | 363 | 548.6 | 349.1
1581 | 1387 | 722.2 | 288.88 | 337.6841 | 404.5 | 430 | 371.1 | 362.4 | 753.1 | 54.9 | 18.5 | 98.6 | 6.2 | 252 | 23.6 | 908.8 | 757 | 884.2 | 860.2 | 790.8 | 808.3 | 817.6 | 795.5 | 715.4 | 827.2 | 228.2 | 319.6 | 367.1 | 276.4 | 380.5 | 398.8 | 377.3 | 363.3 | 549.2 | 349.3
1582 | 1388 | 722.2 | 288.88 | 337.6841 | 404.4 | 430.1 | 371.6 | 362.5 | 758.2 | 54.9 | 18.5 | 98.8 | 5.1 | 247.6 | 20.9 | 907.3 | 756.8 | 881.9 | 859.8 | 792.6 | 809.1 | 816.1 | 793.6 | 715.2 | 827.9 | 228.4 | 319.9 | 367.2 | 276.6 | 380.5 | 399 | 377.4 | 363.5 | 549.7 | 349.5
1583 | 1389 | 721.9 | 288.76 | 337.5438 | 403.7 | 428.9 | 371.1 | 362.6 | 759.6 | 54.9 | 18.5 | 98.8 | 5.9 | 248.3 | 17.2 | 905.8 | 756.5 | 878.2 | 859.3 | 794.6 | 807.7 | 816.2 | 790.9 | 715.1 | 828.5 | 228.7 | 320.2 | 367.4 | 276.8 | 380.5 | 399.1 | 377.6 | 363.7 | 550.3 | 349.7
1584 | 1390 | 723.6 | 289.44 | 338.3387 | 402.8 | 428 | 370.9 | 363 | 755 | 55 | 18.5 | 99 | 8.5 | 262.2 | 17 | 905.8 | 756.3 | 876.3 | 859 | 794.9 | 806.8 | 816.9 | 791.5 | 715.1 | 828.9 | 229 | 320.5 | 367.7 | 276.9 | 380.6 | 399.3 | 377.7 | 364 | 551.2 | 350
1585 | 1391 | 723.8 | 289.52 | 338.4322 | 402.7 | 428.9 | 371.5 | 363.2 | 742.6 | 55 | 18.5 | 99.3 | 8.6 | 257.5 | 16.8 | 904.8 | 756.1 | 874.1 | 858.6 | 795.8 | 806 | 818.3 | 792.7 | 714.6 | 828.8 | 229.2 | 320.8 | 367.9 | 277.1 | 381 | 399.6 | 378.1 | 364.2 | 552.4 | 350.2
1586 | 1392 | 722.6 | 289.04 | 337.8711 | 403 | 429.5 | 371.9 | 363.2 | 745.3 | 55 | 18.5 | 99.5 | 8 | 247.6 | 15.5 | 903.2 | 754.4 | 865.7 | 857.9 | 795.7 | 804.8 | 818.7 | 792 | 714.7 | 828.1 | 229.5 | 321.1 | 368.2 | 277.2 | 381.3 | 399.8 | 378.4 | 364.4 | 553.7 | 350.4
1587 | 1393 | 722.5 | 289 | 337.8243 | 403.3 | 431.6 | 372.5 | 363.6 | 740.1 | 55.1 | 18.5 | 99.5 | 7 | 261.4 | 17 | 902.3 | 754.6 | 871.9 | 857.4 | 797.6 | 804.5 | 818.5 | 791.4 | 714.3 | 828.2 | 229.8 | 321.4 | 368.4 | 277.4 | 381.8 | 400 | 378.7 | 364.7 | 554.9 | 350.7
1588 | 1394 | 721.4 | 288.56 | 337.31 | 402.5 | 431.9 | 372.6 | 363.4 | 730.6 | 55.2 | 18.5 | 99.5 | 7.5 | 270.6 | 18.2 | 900.1 | 754 | 877.2 | 856.9 | 798.4 | 804.4 | 819 | 791.4 | 714.6 | 828.3 | 230.1 | 321.6 | 368.6 | 277.5 | 382.2 | 400.2 | 379.1 | 364.9 | 555.9 | 350.9
1589 | 1395 | 720.4 | 288.16 | 336.8424 | 401.1 | 431 | 372.5 | 363.7 | 732.9 | 55.3 | 18.5 | 99.2 | 9.6 | 267.4 | 16 | 899.3 | 754 | 878.4 | 856.3 | 799.1 | 805 | 819.5 | 789.9 | 714.9 | 828.9 | 230.3 | 321.8 | 369 | 277.7 | 382.2 | 400.8 | 379.4 | 365.2 | 557.1 | 351.1
1590 | 1396 | 720.8 | 288.32 | 337.0295 | 400.9 | 430.1 | 373.4 | 363.6 | 739.2 | 55.4 | 18.5 | 99 | 9.4 | 252.1 | 12.9 | 900.3 | 754.5 | 873 | 856 | 798.3 | 806.1 | 818.8 | 791.8 | 713.9 | 830 | 230.6 | 322 | 369.3 | 277.8 | 382.4 | 401.1 | 379.7 | 365.5 | 557.9 | 351.3
1591 | 1397 | 720 | 288 | 336.6554 | 401.2 | 430.6 | 373.7 | 364.4 | 733.1 | 55.5 | 18.5 | 98.6 | 8 | 258.4 | 13 | 900.1 | 753.9 | 879.7 | 855.6 | 800.3 | 806.2 | 818.5 | 793.3 | 714.1 | 829.9 | 230.9 | 322.3 | 369.2 | 278 | 382.5 | 401.3 | 380.1 | 365.8 | 558.2 | 351.6
1592 | 1398 | 719.4 | 287.76 | 336.3749 | 401.4 | 431.7 | 373.4 | 365.2 | 712.4 | 55.5 | 18.5 | 98.4 | 10.1 | 245.3 | 17.5 | 899.8 | 754.6 | 878.3 | 855.2 | 801.5 | 805.7 | 817.2 | 798.9 | 714.4 | 830.8 | 231.2 | 322.5 | 369.4 | 278.1 | 382.6 | 401.6 | 380.3 | 366.1 | 558.8 | 351.8
1593 | 1399 | 718.1 | 287.24 | 335.767 | 402.2 | 433.6 | 374.2 | 366.2 | 693.8 | 55.6 | 18.5 | 98.6 | 10.5 | 233.2 | 18.5 | 899.3 | 755 | 881 | 855.2 | 801.9 | 803.8 | 814.9 | 797.5 | 714.4 | 829.9 | 231.5 | 322.8 | 369.6 | 278.3 | 382.2 | 401.7 | 380.3 | 366.3 | 559.7 | 352.1
1594 | 1400 | 717.1 | 286.84 | 335.2994 | 402.6 | 434.3 | 373.8 | 365.2 | 706.3 | 55.7 | 18.5 | 98.7 | 9.3 | 249.4 | 15.1 | 898.2 | 754.7 | 885.4 | 854.7 | 803.1 | 805.6 | 815.1 | 793.3 | 714.1 | 830 | 231.7 | 323 | 369.9 | 278.4 | 381.9 | 401.8 | 380.2 | 366.6 | 560.6 | 352.2
1595 | 1401 | 716.6 | 286.64 | 335.0656 | 401.6 | 436 | 374.2 | 363.5 | 707.5 | 55.7 | 18.5 | 98.8 | 10.5 | 250.6 | 14.9 | 898.1 | 754.4 | 884.9 | 854.2 | 804.1 | 805.4 | 816.4 | 793 | 714.1 | 831.9 | 232 | 323.3 | 370 | 278.6 | 382 | 401.9 | 380.3 | 366.8 | 561 | 352.4
1596 | 1402 | 717.4 | 286.96 | 335.4397 | 401 | 437.8 | 374.5 | 362.7 | 698.9 | 55.7 | 18.5 | 99 | 10.3 | 260 | 13.9 | 897.5 | 754.2 | 885.8 | 853.9 | 804.9 | 805.5 | 815.3 | 792 | 714.3 | 832.1 | 232.3 | 323.6 | 370.1 | 278.7 | 382 | 402 | 380.4 | 367 | 561.5 | 352.7
1597 | 1403 | 716.6 | 286.64 | 335.0656 | 400.7 | 438.1 | 374.3 | 363.2 | 700 | 55.7 | 18.5 | 98.9 | 10.3 | 251.2 | 12.4 | 896.5 | 753.6 | 885 | 853.6 | 805.6 | 804.6 | 818.2 | 789.6 | 714.2 | 832.6 | 232.6 | 323.9 | 370.5 | 278.9 | 381.8 | 402.1 | 380.4 | 367.2 | 562.1 | 352.9
1598 | 1404 | 717.1 | 286.84 | 335.2994 | 400.1 | 436.9 | 373.5 | 363.3 | 711.9 | 55.7 | 18.5 | 98.8 | 9.9 | 247.3 | 11.2 | 895.7 | 752.6 | 883.4 | 853.1 | 804.8 | 806 | 818.4 | 785.9 | 714 | 832.4 | 232.9 | 324.2 | 370.8 | 279 | 382.1 | 402.5 | 380.5 | 367.4 | 562.8 | 353.1
1599 | 1405 | 716.6 | 286.64 | 335.0656 | 400.4 | 435 | 373.6 | 362.3 | 724.8 | 55.7 | 18.5 | 98.9 | 9.7 | 228.6 | 11.3 | 895.4 | 752.9 | 876.7 | 852.8 | 806.4 | 806.5 | 820.9 | 787.7 | 713.9 | 834.2 | 233.1 | 324.5 | 371.1 | 279.2 | 382.5 | 402.6 | 380.9 | 367.7 | 563.3 | 353.3
1600 | 1406 | 716.9 | 286.76 | 335.2059 | 400.3 | 433.4 | 373.5 | 363 | 736.4 | 55.8 | 18.5 | 98.9 | 8.5 | 232.5 | 11.9 | 895.7 | 753 | 880 | 852.6 | 807.7 | 805.9 | 820.6 | 786.7 | 713.9 | 834.9 | 233.4 | 324.7 | 371.5 | 279.3 | 382.9 | 402.5 | 381.3 | 367.9 | 563.7 | 353.5
1601 | 1407 | 715.7 | 286.28 | 334.6448 | 399.7 | 434.2 | 373.1 | 364 | 731.9 | 55.8 | 18.5 | 98.8 | 5.9 | 224.5 | 14.4 | 897.1 | 754.5 | 871.9 | 852.4 | 808.6 | 804.4 | 818 | 787 | 714.1 | 836 | 233.7 | 324.9 | 371.7 | 279.5 | 383.3 | 402.4 | 381.6 | 368.1 | 564.2 | 353.7
1602 | 1408 | 715.5 | 286.2 | 334.5513 | 399.5 | 435.4 | 372.7 | 364.5 | 740.8 | 55.9 | 18.5 | 98.6 | 6.1 | 238.8 | 17.9 | 896.8 | 754.2 | 868 | 852.3 | 808.2 | 805.8 | 812.8 | 786.5 | 714.1 | 835 | 234 | 325 | 372.1 | 279.7 | 383.6 | 402.5 | 381.9 | 368.3 | 564.8 | 354
1603 | 1409 | 715.7 | 286.28 | 334.6448 | 400.3 | 436.1 | 372.8 | 364.6 | 741.7 | 55.9 | 18.5 | 98.4 | 8.3 | 238.2 | 17.1 | 898.1 | 753.9 | 824.1 | 851.8 | 803.2 | 804.9 | 806.3 | 790.7 | 713.6 | 831.6 | 234.3 | 325.3 | 372.4 | 279.8 | 383.7 | 402.6 | 382.2 | 368.5 | 565.1 | 354.2
1604 | 1410 | 715 | 286 | 334.3175 | 403.2 | 435.5 | 373.3 | 364.4 | 730.8 | 56 | 18.5 | 98.3 | 8.3 | 209.5 | 14.9 | 898 | 753.3 | 797.4 | 851.4 | 799.2 | 802.1 | 795.4 | 792.2 | 712.6 | 826 | 234.6 | 325.6 | 372.8 | 280 | 384.2 | 402.5 | 382.7 | 368.7 | 565 | 354.5
1605 | 1411 | 714.2 | 285.68 | 333.9435 | 405.5 | 434.9 | 373.5 | 365.5 | 721.3 | 56.1 | 18.5 | 98.2 | 8 | 211.4 | 10.9 | 899.1 | 753.7 | 787.7 | 850.9 | 797.4 | 801.1 | 793.2 | 793.8 | 711.9 | 824.1 | 234.9 | 325.9 | 372.9 | 280.2 | 384.4 | 402.3 | 383 | 368.9 | 564.6 | 354.7
1606 | 1412 | 712.3 | 284.92 | 333.0551 | 407.1 | 433.8 | 373.9 | 366.2 | 722.5 | 56.2 | 18.5 | 98.4 | 12.1 | 227.7 | 12.7 | 901.3 | 752.7 | 789.1 | 850.9 | 795.2 | 801 | 795 | 793.7 | 711.8 | 823.8 | 235.2 | 326.5 | 373.2 | 280.4 | 384.5 | 402.1 | 383.2 | 369.1 | 564.3 | 355
1607 | 1413 | 713.5 | 285.4 | 333.6162 | 408.9 | 432.1 | 374.2 | 366.6 | 724.6 | 56.2 | 18.5 | 98.7 | 10.6 | 225.1 | 15.6 | 901 | 753.5 | 798.8 | 850.8 | 795.4 | 801.1 | 797.2 | 792.1 | 712 | 824.2 | 235.5 | 327.1 | 373.2 | 280.5 | 384.5 | 402 | 383.3 | 369.3 | 564.1 | 355.2
1608 | 1414 | 714.5 | 285.8 | 334.0837 | 410.6 | 431.5 | 374.5 | 366.6 | 719.8 | 56.3 | 18.5 | 98.8 | 9.5 | 233.7 | 16.6 | 901.6 | 754 | 793.3 | 850.8 | 794.3 | 801.5 | 802.8 | 795 | 712.3 | 825.9 | 235.8 | 327.6 | 373.5 | 280.7 | 384.2 | 401.8 | 383.2 | 369.5 | 564.2 | 355.4
1609 | 1415 | 713.7 | 285.48 | 333.7097 | 411.8 | 431.1 | 374.5 | 365.2 | 716.8 | 56.4 | 18.5 | 98.8 | 9.2 | 229.6 | 13.7 | 904.2 | 754.4 | 801.1 | 850.9 | 793 | 801.2 | 805.3 | 794.4 | 712.1 | 823.4 | 236 | 328.1 | 373.7 | 280.8 | 383.9 | 401.4 | 383.2 | 369.6 | 564.4 | 355.6
1610 | 1416 | 711.6 | 284.64 | 332.7278 | 412.2 | 430.2 | 375.6 | 362.6 | 721.7 | 56.5 | 18.5 | 98.8 | 8.3 | 238.5 | 12.1 | 904.8 | 753.8 | 816 | 850.7 | 794.3 | 802.8 | 801.6 | 789.2 | 711.7 | 822.4 | 236.3 | 328.7 | 374.1 | 281 | 383.7 | 401.1 | 383.2 | 369.7 | 564.3 | 355.8
1611 | 1417 | 712.2 | 284.88 | 333.0083 | 412.7 | 429 | 375 | 361.1 | 727.8 | 56.5 | 18.5 | 98.9 | 7.2 | 238.4 | 13.3 | 904.2 | 752.9 | 827 | 850.3 | 794.3 | 801.7 | 801.3 | 784.3 | 711.6 | 823.5 | 236.6 | 329 | 374 | 281.1 | 383.6 | 401.3 | 383.3 | 369.9 | 564.3 | 355.9
1612 | 1418 | 710.9 | 284.36 | 332.4005 | 414.6 | 427.4 | 374.6 | 360.9 | 736.7 | 56.4 | 18.5 | 98.9 | 8.2 | 227 | 11.8 | 903.5 | 752 | 827.9 | 849.9 | 793.3 | 801.3 | 804.9 | 783 | 711.7 | 824.5 | 236.9 | 329.5 | 374.2 | 281.3 | 383.9 | 401.9 | 383.4 | 370.1 | 564.4 | 356.1
1613 | 1419 | 711.7 | 284.68 | 332.7745 | 415.3 | 426.1 | 374 | 360.7 | 741.1 | 56.3 | 18.5 | 98.9 | 8.5 | 218.2 | 16.8 | 905.2 | 750.8 | 840.8 | 849.4 | 793.1 | 801.7 | 808.1 | 781.1 | 712.3 | 825.2 | 237.2 | 329.7 | 374.7 | 281.4 | 384.3 | 402 | 383.6 | 370.3 | 564.9 | 356.4
1614 | 1420 | 712.2 | 284.88 | 333.0083 | 416.3 | 425.5 | 373.7 | 361 | 758.3 | 56.3 | 18.5 | 98.9 | 8.6 | 221 | 14.1 | 906.5 | 750.6 | 851.2 | 849.2 | 790.6 | 801.2 | 810.6 | 780.5 | 712.7 | 824.7 | 237.5 | 329.8 | 375.3 | 281.6 | 384.8 | 401.8 | 384 | 370.4 | 565.4 | 356.6
1615 | 1421 | 710.7 | 284.28 | 332.3069 | 416 | 425.4 | 374.3 | 362.4 | 767.5 | 56.3 | 18.5 | 98.9 | 8.6 | 229.3 | 12.7 | 907.3 | 750 | 860.2 | 848.8 | 790.3 | 799.8 | 812.9 | 779 | 712.7 | 824.1 | 237.8 | 329.9 | 375.3 | 281.8 | 385.2 | 401.6 | 384.4 | 370.5 | 565.7 | 356.8
1616 | 1422 | 710 | 284 | 331.9796 | 415.5 | 425.9 | 374 | 363.4 | 778.9 | 56.3 | 18.4 | 98.8 | 8.5 | 237 | 11.3 | 909.2 | 749.7 | 851.3 | 848.5 | 789.6 | 799.6 | 813.1 | 779.4 | 712.5 | 824.2 | 238.1 | 330 | 375.9 | 281.9 | 385.4 | 401.6 | 384.8 | 370.7 | 565.9 | 357
1617 | 1423 | 711.2 | 284.48 | 332.5407 | 415.9 | 426.5 | 373.9 | 364.6 | 787.2 | 56.2 | 18.5 | 98.8 | 7.9 | 226.3 | 10.2 | 910.6 | 749.4 | 850.2 | 848.3 | 790.3 | 797 | 809.7 | 777.8 | 712.6 | 824.2 | 238.4 | 330.2 | 376.3 | 282.1 | 385.8 | 401.6 | 385.2 | 370.8 | 566.2 | 357.3
1618 | 1424 | 714.2 | 285.68 | 333.9435 | 415.1 | 427.7 | 374.3 | 366 | 788.3 | 56.2 | 18.5 | 98.7 | 8.4 | 234.2 | 9.8 | 909.1 | 747.2 | 850.9 | 847.8 | 790.8 | 796.6 | 812.3 | 776.9 | 712.3 | 826.1 | 238.8 | 330.4 | 376.2 | 282.2 | 386.1 | 401.5 | 385.6 | 371 | 566.5 | 357.5
1619 | 1425 | 714.2 | 285.68 | 333.9435 | 414.5 | 427.8 | 374.7 | 366.5 | 771.3 | 56.2 | 18.5 | 98.5 | 10.1 | 241.1 | 10.5 | 908.5 | 747.2 | 850.4 | 847.4 | 791.9 | 797.9 | 814.2 | 776.6 | 712.1 | 827 | 239.1 | 330.6 | 376.2 | 282.4 | 386.3 | 401.7 | 385.9 | 371.2 | 567 | 357.7
1620 | 1426 | 711.1 | 284.44 | 332.494 | 414.8 | 427.2 | 374.2 | 366.3 | 771.5 | 56.3 | 18.4 | 98.3 | 11.5 | 246.4 | 13.5 | 907.8 | 746.4 | 851.5 | 847 | 792.5 | 799 | 817.4 | 777.5 | 711.8 | 828.6 | 239.4 | 330.8 | 376.6 | 282.5 | 386.2 | 401.7 | 386 | 371.4 | 567.7 | 358
1621 | 1427 | 711.5 | 284.6 | 332.681 | 414.9 | 428.9 | 373.6 | 366.6 | 766.9 | 56.3 | 18.4 | 98.3 | 9.8 | 232.3 | 14.1 | 909.4 | 746.6 | 859.9 | 845.8 | 795.4 | 799 | 815.9 | 778 | 712 | 829.8 | 239.7 | 331 | 376.9 | 282.7 | 386.2 | 401.8 | 386.2 | 371.5 | 568.3 | 358.2
1622 | 1428 | 714 | 285.6 | 333.8499 | 414.4 | 433.1 | 372.8 | 366.3 | 757.8 | 56.3 | 18.4 | 98.4 | 7.6 | 214.1 | 13.9 | 909.6 | 746.3 | 863 | 845.3 | 798.1 | 797 | 807.6 | 778.1 | 712.6 | 829.2 | 240 | 331.2 | 377 | 282.9 | 386.3 | 401.7 | 386.4 | 371.6 | 569 | 358.4
1623 | 1429 | 711 | 284.4 | 332.4472 | 414.3 | 434.3 | 371.8 | 366.1 | 759.1 | 56.3 | 18.4 | 98.6 | 7.7 | 229.2 | 11.9 | 909.4 | 746.4 | 869 | 845.2 | 799.7 | 796.2 | 800.5 | 782.1 | 713.2 | 829 | 240.3 | 331.3 | 377.4 | 283 | 386.5 | 401.5 | 386.7 | 371.8 | 569.8 | 358.6
1624 | 1430 | 709 | 283.6 | 331.5121 | 413.8 | 435 | 372.4 | 366.7 | 766.3 | 56.3 | 18.4 | 98.8 | 6.8 | 243.3 | 11.2 | 908.4 | 746.7 | 867.5 | 844.8 | 801.1 | 794.9 | 802.9 | 779.9 | 713.2 | 828.4 | 240.6 | 331.5 | 377.7 | 283.2 | 386.7 | 401.5 | 386.8 | 372 | 570.5 | 358.9
1625 | 1431 | 708.2 | 283.28 | 331.138 | 413.7 | 434.8 | 372.8 | 367.6 | 766 | 56.3 | 18.4 | 99 | 7.5 | 252.3 | 11.8 | 907.6 | 745.7 | 865.2 | 844.5 | 801.7 | 795.6 | 807.9 | 778.8 | 712.8 | 829.1 | 240.9 | 331.8 | 377.8 | 283.3 | 386.7 | 401.7 | 387 | 372.2 | 570.7 | 359.1
1626 | 1432 | 708.3 | 283.32 | 331.1848 | 413.2 | 434.5 | 372.9 | 367.7 | 764.5 | 56.2 | 18.4 | 98.9 | 7.1 | 251 | 12.6 | 908.7 | 747.3 | 866.4 | 844.2 | 801.6 | 795.8 | 810.2 | 782.3 | 712.3 | 830.1 | 241.2 | 332.2 | 378.3 | 283.5 | 386.9 | 402 | 387.1 | 372.4 | 571 | 359.3
1627 | 1433 | 707.1 | 282.84 | 330.6237 | 413.3 | 435.4 | 373.3 | 366.7 | 752.3 | 56.1 | 18.4 | 98.8 | 7.1 | 208.5 | 11.6 | 910 | 746.4 | 873.5 | 843.5 | 800.8 | 795.5 | 805.5 | 781.8 | 711.8 | 827.8 | 241.6 | 332.6 | 378.2 | 283.7 | 386.6 | 402 | 387.1 | 372.6 | 570.9 | 359.5
1628 | 1434 | 705.5 | 282.2 | 329.8755 | 412.8 | 438.3 | 374 | 366.3 | 761.5 | 56.2 | 18.4 | 98.9 | 7.9 | 218.4 | 15.5 | 912.9 | 745.6 | 877.3 | 842.9 | 799 | 794.5 | 798 | 780.2 | 712 | 823.1 | 241.9 | 332.9 | 379.2 | 283.8 | 386.5 | 401.7 | 387.1 | 372.7 | 570.7 | 359.7
1629 | 1435 | 707.4 | 282.96 | 330.7639 | 413.3 | 440.1 | 375.2 | 365.4 | 770.9 | 56.3 | 18.4 | 98.9 | 7.8 | 203.5 | 17.1 | 912.4 | 744.6 | 875.9 | 841.7 | 799.2 | 793.9 | 790.5 | 778.4 | 712.1 | 822.1 | 242.2 | 333.4 | 379.4 | 284 | 386.5 | 401.4 | 387.3 | 372.7 | 570.7 | 359.9
1630 | 1436 | 709 | 283.6 | 331.5121 | 413.5 | 440.3 | 376.1 | 364 | 773.6 | 56.3 | 18.4 | 98.9 | 9.1 | 207.4 | 19.4 | 913.2 | 744.4 | 878.3 | 841 | 801.1 | 792.4 | 790.6 | 776.7 | 712.1 | 823.3 | 242.5 | 333.8 | 379.3 | 284.1 | 386.7 | 401.5 | 387.5 | 372.9 | 570.8 | 360.1
1631 | 1437 | 708.1 | 283.24 | 331.0912 | 413.1 | 439.9 | 376.7 | 363.4 | 764.8 | 56.3 | 18.4 | 98.9 | 8.5 | 203.6 | 19.3 | 912.1 | 744.5 | 881.2 | 840.4 | 802.9 | 792.6 | 790.5 | 776.5 | 712.5 | 823.9 | 242.8 | 334 | 379.4 | 284.3 | 387 | 401.9 | 387.7 | 373.1 | 571.1 | 360.4
1632 | 1438 | 708 | 283.2 | 331.0445 | 413.5 | 438.7 | 376.1 | 363.6 | 765.7 | 56.3 | 18.4 | 99.1 | 7.6 | 203.5 | 18.5 | 911.1 | 744.9 | 875.9 | 839.9 | 802 | 790.2 | 797.5 | 771 | 712.5 | 823.6 | 243.1 | 334.3 | 379.7 | 284.5 | 387.4 | 402.1 | 388 | 373.3 | 571.6 | 360.6
1633 | 1439 | 706.4 | 282.56 | 330.2964 | 413.8 | 438 | 376 | 364.4 | 769.3 | 56.4 | 18.4 | 99.4 | 7.5 | 220.4 | 15.9 | 911.4 | 745 | 873.4 | 839 | 802.7 | 789.3 | 800.7 | 770.1 | 712.4 | 824.9 | 243.5 | 335 | 380 | 284.6 | 387.7 | 402 | 388.2 | 373.4 | 571.7 | 360.8
1634 | 1440 | 705.1 | 282.04 | 329.6885 | 414 | 440.3 | 376.6 | 365.1 | 762.3 | 56.4 | 18.4 | 99.7 | 8.7 | 224.3 | 13.9 | 913.1 | 745.6 | 870.4 | 838.5 | 804.7 | 791.3 | 802.8 | 775.4 | 712.4 | 826.5 | 243.8 | 335.5 | 380 | 284.8 | 387.8 | 401.9 | 388.4 | 373.6 | 571.7 | 361
1635 | 1441 | 705.9 | 282.36 | 330.0626 | 413.8 | 443.5 | 376.2 | 365.5 | 751.9 | 56.5 | 18.4 | 100.1 | 8.6 | 194.6 | 11.2 | 913.4 | 745.7 | 867.7 | 836.2 | 805.4 | 791.4 | 807.9 | 775.1 | 712.5 | 827.9 | 244.1 | 336 | 380.2 | 284.9 | 387.8 | 401.8 | 388.6 | 373.8 | 572.1 | 361.2
1636 | 1442 | 706.4 | 282.56 | 330.2964 | 414.7 | 445.9 | 375.8 | 364.6 | 760.1 | 56.5 | 18.4 | 100.3 | 9.3 | 212.9 | 14 | 912.3 | 745.6 | 864.7 | 834.9 | 804.7 | 791.4 | 804.3 | 774.2 | 712.8 | 826.4 | 244.5 | 336.7 | 381.2 | 285.1 | 388 | 401.7 | 388.8 | 373.9 | 572.9 | 361.4
1637 | 1443 | 704.6 | 281.84 | 329.4547 | 415.4 | 447.2 | 375 | 364.9 | 757.2 | 56.5 | 18.4 | 100.3 | 8.9 | 225.8 | 11.7 | 912.2 | 746.8 | 849.1 | 835.2 | 803.3 | 794.3 | 807.8 | 775.7 | 712.6 | 827.2 | 244.8 | 337.3 | 381 | 285.2 | 388.1 | 401.8 | 389 | 374.1 | 573.4 | 361.6
1638 | 1444 | 703.4 | 281.36 | 328.8936 | 415 | 446 | 374.6 | 365.3 | 762.9 | 56.6 | 18.4 | 100.3 | 9.2 | 219.9 | 12.5 | 914 | 746.7 | 857.1 | 834.1 | 803.4 | 793.6 | 810.3 | 776.8 | 712.7 | 826.9 | 245.2 | 337.7 | 381.4 | 285.4 | 388 | 401.7 | 389.1 | 374.3 | 573.3 | 361.8
1639 | 1445 | 703.4 | 281.36 | 328.8936 | 414.4 | 446.6 | 375 | 364.6 | 767.9 | 56.6 | 18.4 | 100.4 | 9.5 | 227 | 11.9 | 915.6 | 748.2 | 859.2 | 831.7 | 802.7 | 793 | 801.3 | 779.2 | 713 | 823.7 | 245.5 | 338 | 382.5 | 285.6 | 387.9 | 401.5 | 389.1 | 374.3 | 573.2 | 362
1640 | 1446 | 703.2 | 281.28 | 328.8001 | 414.1 | 448.9 | 376.3 | 364.3 | 756.6 | 56.7 | 18.4 | 100.4 | 11.8 | 240.3 | 11.7 | 918.5 | 747.8 | 841.3 | 831.2 | 797.6 | 792.1 | 790.9 | 782 | 712.9 | 818.8 | 245.9 | 338.4 | 383 | 285.7 | 387.8 | 401.3 | 389.2 | 374.4 | 573.3 | 362.2
1641 | 1447 | 701.1 | 280.44 | 327.8182 | 414.8 | 449.8 | 377.2 | 362.9 | 743.9 | 56.8 | 18.4 | 100.4 | 10.9 | 244.2 | 9.7 | 917.1 | 747.9 | 817.7 | 830.9 | 793.6 | 790 | 782.7 | 784.6 | 712.5 | 815 | 246.4 | 338.7 | 383 | 285.9 | 388.1 | 401.3 | 389.4 | 374.6 | 573.1 | 362.4
1642 | 1448 | 704 | 281.6 | 329.1742 | 417.1 | 449.5 | 377 | 362.9 | 744.8 | 56.8 | 18.4 | 100.5 | 9.4 | 243 | 11.9 | 922.2 | 746.3 | 797.7 | 831.4 | 787.1 | 788.3 | 777.4 | 785.8 | 712.3 | 809 | 246.8 | 339 | 383.5 | 286 | 388.4 | 401.2 | 389.6 | 374.7 | 572.8 | 362.6
1643 | 1449 | 702.5 | 281 | 328.4728 | 419.9 | 449 | 377.1 | 364.1 | 739.8 | 56.8 | 18.4 | 100.7 | 8.1 | 236.4 | 15.3 | 924.3 | 745.9 | 766.2 | 832.5 | 781.5 | 785 | 765.8 | 788.5 | 712.1 | 802.4 | 247.2 | 339.3 | 383.8 | 286.2 | 389 | 401.1 | 389.9 | 374.8 | 572.6 | 362.8
1644 | 1450 | 703 | 281.2 | 328.7066 | 422.4 | 449 | 378.8 | 365.3 | 729.3 | 56.9 | 18.4 | 100.7 | 9.1 | 226 | 14.2 | 924 | 744.8 | 751.6 | 831.2 | 777 | 786.7 | 764.5 | 784.8 | 711.9 | 800.4 | 247.6 | 339.7 | 383.7 | 286.3 | 389.3 | 401.1 | 390 | 374.9 | 572.2 | 363
1645 | 1451 | 703.4 | 281.36 | 328.8936 | 424.3 | 450.4 | 379.2 | 365.2 | 726.5 | 56.9 | 18.4 | 100.7 | 8.4 | 229.3 | 12.7 | 923.1 | 744.8 | 759.1 | 830.5 | 775 | 788.4 | 762.7 | 781.1 | 711.6 | 798.3 | 248 | 340.1 | 384.1 | 286.5 | 389.4 | 401.2 | 390.2 | 375 | 571.7 | 363.2
1646 | 1452 | 703.3 | 281.32 | 328.8469 | 425.9 | 448 | 379.7 | 364.9 | 728.7 | 56.9 | 18.4 | 100.8 | 9.2 | 234.5 | 13 | 923.6 | 743.2 | 772.7 | 830.7 | 774.1 | 789.1 | 767.7 | 776.6 | 711.5 | 800 | 248.5 | 340.5 | 384.1 | 286.7 | 389.6 | 401.5 | 390.3 | 375.2 | 571.4 | 363.4
1647 | 1453 | 702.2 | 280.88 | 328.3325 | 427.4 | 446.2 | 380.1 | 365.4 | 741.6 | 56.9 | 18.4 | 100.9 | 7.9 | 238.7 | 14.4 | 921.9 | 741.4 | 793.8 | 830.8 | 773.3 | 789.1 | 768.1 | 772.5 | 711.7 | 799.8 | 248.9 | 341 | 384.6 | 286.8 | 389.7 | 401.6 | 390.4 | 375.4 | 571.3 | 363.6
1648 | 1454 | 701.9 | 280.76 | 328.1923 | 428.6 | 446.3 | 379 | 365.7 | 751.2 | 57 | 18.4 | 100.9 | 7.6 | 239.2 | 13.7 | 921.4 | 741.4 | 811.4 | 831.2 | 773 | 787.8 | 770.9 | 770.5 | 712.1 | 799.7 | 249.3 | 341.4 | 385 | 287 | 390 | 401.5 | 390.7 | 375.5 | 571.3 | 363.8
1649 | 1455 | 702.2 | 280.88 | 328.3325 | 429.8 | 447.5 | 378.2 | 366 | 761.3 | 57.1 | 18.4 | 101 | 8.4 | 220.7 | 12.3 | 922 | 739.6 | 830.4 | 831.6 | 774.9 | 787.1 | 771.8 | 771.1 | 712.7 | 801.1 | 249.8 | 341.7 | 385.3 | 287.1 | 390.3 | 401.3 | 391.1 | 375.6 | 571.6 | 364
1650 | 1456 | 702.6 | 281.04 | 328.5196 | 428.5 | 448.7 | 377.8 | 366.6 | 756.1 | 57.1 | 18.4 | 101.1 | 8.4 | 239.1 | 10.7 | 922.1 | 739.2 | 837.4 | 832 | 773.9 | 787.5 | 771.3 | 770.1 | 713.4 | 801.8 | 250.3 | 342 | 385.7 | 287.3 | 390.9 | 401.4 | 391.4 | 375.7 | 572.1 | 364.3
1651 | 1457 | 701.4 | 280.56 | 327.9585 | 428.5 | 448.7 | 377 | 366.5 | 758.9 | 57.1 | 18.4 | 101.1 | 7 | 247.7 | 12.5 | 920.8 | 739.7 | 841.6 | 831.9 | 774.2 | 787 | 777.8 | 769.5 | 713.8 | 803.3 | 250.8 | 342.3 | 386 | 287.5 | 391 | 401.4 | 391.7 | 375.9 | 572.4 | 364.5
1652 | 1458 | 701.3 | 280.52 | 327.9117 | 427 | 448.7 | 377.4 | 365.6 | 765.1 | 57.1 | 18.4 | 101.1 | 6.6 | 248.1 | 12 | 918.9 | 739.7 | 843.1 | 831.7 | 774.6 | 786.5 | 785.6 | 767.6 | 714.1 | 805.3 | 251.3 | 342.7 | 385.9 | 287.6 | 391.2 | 401.5 | 392.1 | 376.1 | 572.5 | 364.7
1653 | 1459 | 703.7 | 281.48 | 329.0339 | 426.1 | 448.6 | 377.2 | 364.3 | 762.3 | 57.1 | 18.4 | 101 | 7 | 240.9 | 12.6 | 918.6 | 739.1 | 843.4 | 831.5 | 776.3 | 786.9 | 792.8 | 767.2 | 714.3 | 807.9 | 251.8 | 343.1 | 386.1 | 287.8 | 391.7 | 401.7 | 392.4 | 376.3 | 572.5 | 364.9
1654 | 1460 | 701.6 | 280.64 | 328.052 | 426.7 | 449 | 376.1 | 362.9 | 762.1 | 57.1 | 18.4 | 100.9 | 6.2 | 250.4 | 14.3 | 917.3 | 739 | 846.5 | 831.3 | 777.8 | 786.2 | 799.7 | 765.6 | 714.7 | 809.6 | 252.2 | 343.4 | 386.2 | 287.9 | 391.8 | 401.8 | 392.5 | 376.4 | 572.6 | 365.2
1655 | 1461 | 701.5 | 280.6 | 328.0052 | 426.7 | 448.9 | 376.1 | 362.3 | 761.4 | 57.1 | 18.4 | 100.7 | 7 | 241.6 | 13.6 | 916.2 | 739.2 | 854.8 | 831.3 | 779.3 | 785.5 | 806.6 | 765.1 | 714.8 | 811.1 | 252.6 | 343.7 | 386.5 | 288.1 | 392.2 | 402.3 | 392.7 | 376.6 | 572.8 | 365.4
1656 | 1462 | 700.9 | 280.36 | 327.7247 | 425.8 | 448.3 | 377 | 362.2 | 755.7 | 57.1 | 18.4 | 100.6 | 7.9 | 239.8 | 13.1 | 913.6 | 739.4 | 857.6 | 830.7 | 780.6 | 786 | 813.4 | 764.8 | 714.7 | 813.2 | 253 | 344 | 386.5 | 288.3 | 392.6 | 402.6 | 392.9 | 376.8 | 573.5 | 365.6
1657 | 1463 | 700.8 | 280.32 | 327.6779 | 425.2 | 448 | 376.7 | 361.4 | 750.1 | 57.2 | 18.4 | 100.5 | 7 | 223.2 | 11.5 | 912.9 | 740.7 | 863.3 | 829.6 | 783.3 | 784.2 | 818.4 | 764.1 | 714.8 | 814.5 | 253.3 | 344.2 | 386.8 | 288.4 | 392.8 | 403 | 393.2 | 377 | 574.2 | 365.8
1658 | 1464 | 699.7 | 279.88 | 327.1636 | 424.3 | 448.2 | 376.1 | 361.6 | 750.2 | 57.3 | 18.4 | 100.4 | 6.8 | 238.3 | 9.1 | 911.5 | 741 | 868.9 | 828.4 | 786 | 783.2 | 821.9 | 765.2 | 715.1 | 815.9 | 253.7 | 344.5 | 387.1 | 288.6 | 393.2 | 403.4 | 393.4 | 377.2 | 574.6 | 366
1659 | 1465 | 700.7 | 280.28 | 327.6312 | 423.5 | 449.8 | 376.5 | 361.9 | 756.2 | 57.3 | 18.4 | 100.4 | 7.1 | 228.7 | 9.1 | 909.6 | 740.6 | 860.6 | 827.8 | 786.4 | 780.4 | 823.6 | 761.9 | 715.1 | 815.9 | 254 | 344.8 | 387.4 | 288.8 | 393.9 | 403.5 | 393.7 | 377.3 | 575.2 | 366.2
1660 | 1466 | 700.3 | 280.12 | 327.4441 | 422.5 | 449 | 376.7 | 363 | 758.7 | 57.4 | 18.4 | 100.4 | 7.4 | 236.3 | 9.7 | 907.5 | 740.1 | 864.6 | 826.4 | 787.7 | 780 | 825.7 | 760.6 | 715.1 | 817.2 | 254.3 | 345 | 387.5 | 288.9 | 394.8 | 403.9 | 394.1 | 377.6 | 575.6 | 366.4
1661 | 1467 | 700.6 | 280.24 | 327.5844 | 421.7 | 448.1 | 376.1 | 362.6 | 759 | 57.4 | 18.4 | 100.4 | 8 | 220.6 | 10.3 | 905.5 | 740.3 | 867.3 | 825.3 | 788.2 | 781.1 | 828 | 760.5 | 715 | 818.2 | 254.6 | 345.2 | 387.6 | 289.1 | 395.5 | 404.4 | 394.5 | 377.8 | 576.2 | 366.7
1662 | 1468 | 699.4 | 279.76 | 327.0233 | 420.7 | 447.4 | 375.6 | 361.9 | 755.4 | 57.4 | 18.4 | 100.6 | 7.9 | 238.8 | 8.5 | 903.8 | 741.3 | 864.2 | 824.5 | 788.4 | 782 | 825.2 | 761.2 | 715.1 | 819.1 | 254.9 | 345.4 | 387.7 | 289.3 | 396.2 | 404.8 | 394.8 | 378.1 | 576.7 | 366.9
1663 | 1469 | 699.9 | 279.96 | 327.2571 | 420.2 | 448.5 | 376.4 | 362.2 | 749.7 | 57.5 | 18.4 | 100.6 | 6.3 | 222.7 | 8.3 | 902.7 | 741.4 | 850.2 | 824.1 | 788.7 | 781.7 | 823.9 | 762.9 | 715.2 | 819.9 | 255.2 | 345.7 | 387.9 | 289.4 | 397 | 405.1 | 395.1 | 378.3 | 577.1 | 367.1
1664 | 1470 | 699.1 | 279.64 | 326.883 | 419.8 | 448.8 | 376.4 | 361.7 | 753.8 | 57.5 | 18.4 | 100.4 | 7.1 | 237.8 | 9 | 901.9 | 741.7 | 846.6 | 823.4 | 790.5 | 780.7 | 823.8 | 762.7 | 715.5 | 820.8 | 255.5 | 345.9 | 388.2 | 289.6 | 397.7 | 405.1 | 395.3 | 378.4 | 577.2 | 367.3
1665 | 1471 | 699.5 | 279.8 | 327.0701 | 418.8 | 446.8 | 376.5 | 362 | 763.9 | 57.5 | 18.4 | 100.2 | 7.4 | 220.5 | 9.4 | 899.8 | 741.6 | 849.5 | 822.4 | 791.7 | 780.7 | 827.6 | 762.4 | 715.9 | 822.2 | 255.8 | 346.2 | 388.7 | 289.8 | 398.3 | 405.2 | 395.7 | 378.6 | 577.6 | 367.6
1666 | 1472 | 699.3 | 279.72 | 326.9766 | 418.6 | 446.3 | 377.2 | 361.8 | 761.4 | 57.6 | 18.4 | 100 | 7.1 | 221 | 11.7 | 898.5 | 742.7 | 850 | 821.8 | 792.2 | 781.4 | 827.6 | 762.1 | 716.2 | 823.1 | 256.1 | 346.5 | 388.7 | 289.9 | 399 | 405.6 | 396 | 378.8 | 578.1 | 367.8
1667 | 1473 | 697.9 | 279.16 | 326.322 | 418.9 | 449.2 | 377.4 | 362.3 | 749.4 | 57.6 | 18.4 | 100 | 6.4 | 217.9 | 12.8 | 896.2 | 743.2 | 845 | 821.1 | 791.7 | 781.4 | 830.7 | 765.5 | 716.2 | 824.3 | 256.4 | 346.8 | 388.8 | 290.1 | 399.7 | 405.9 | 396.2 | 379.1 | 578.7 | 368
1668 | 1474 | 700 | 280 | 327.3039 | 419.4 | 451.5 | 377.5 | 363.9 | 745.5 | 57.5 | 18.3 | 100.1 | 6.7 | 210.4 | 12.7 | 895.7 | 743.6 | 838 | 820.5 | 792.3 | 782.2 | 828.8 | 765.8 | 716.1 | 826.5 | 256.7 | 347 | 389.1 | 290.2 | 400.2 | 406.3 | 396.4 | 379.3 | 579.1 | 368.2
1669 | 1475 | 701.3 | 280.52 | 327.9117 | 420.2 | 452 | 377 | 364.4 | 738.8 | 57.5 | 18.3 | 100.2 | 6.2 | 217.2 | 11.8 | 895.7 | 744.4 | 839.8 | 820 | 793.1 | 781 | 830.8 | 764.2 | 716.2 | 828 | 257 | 347.2 | 389.2 | 290.4 | 400.7 | 406.6 | 396.6 | 379.6 | 579.2 | 368.4
1670 | 1476 | 699.5 | 279.8 | 327.0701 | 419.4 | 451.9 | 376.4 | 363.9 | 738.6 | 57.6 | 18.3 | 100.2 | 5.6 | 223.9 | 11.4 | 894 | 744.5 | 824.2 | 819.6 | 793.3 | 780 | 830.8 | 762.4 | 716.3 | 828.1 | 257.3 | 347.4 | 389.3 | 290.6 | 401.4 | 407 | 396.7 | 379.8 | 579.4 | 368.6
1671 | 1477 | 698.5 | 279.4 | 326.6025 | 419.1 | 452.8 | 376 | 363.2 | 744.1 | 57.7 | 18.4 | 100.3 | 6.8 | 212.4 | 12.9 | 893.8 | 744.1 | 823.9 | 818.8 | 794.6 | 780.1 | 831.2 | 763.7 | 716.3 | 829.6 | 257.5 | 347.5 | 389.6 | 290.7 | 402.1 | 407.3 | 396.9 | 380 | 579.7 | 368.8
1672 | 1478 | 696.8 | 278.72 | 325.8076 | 418.9 | 453 | 375.6 | 363.6 | 740.4 | 57.7 | 18.4 | 100.4 | 6.4 | 239.6 | 13.2 | 892.2 | 743.9 | 832.7 | 818 | 794.9 | 778.3 | 834.3 | 761.1 | 716.3 | 828.8 | 257.8 | 347.7 | 389.7 | 290.9 | 402.9 | 407.7 | 397.1 | 380.1 | 579.8 | 369
1673 | 1479 | 697.7 | 279.08 | 326.2284 | 419 | 450.5 | 375.9 | 364.1 | 737.2 | 57.7 | 18.3 | 100.4 | 5.7 | 242.3 | 11.9 | 891.9 | 744.3 | 844.4 | 817.4 | 795.9 | 777.5 | 838.1 | 760 | 716.2 | 829.2 | 258.1 | 347.8 | 390 | 291 | 404.5 | 407.9 | 397.5 | 380.3 | 580.6 | 369.3
1674 | 1480 | 696 | 278.4 | 325.4336 | 419.2 | 450.6 | 376.4 | 364.9 | 743 | 57.8 | 18.3 | 100.5 | 6.3 | 243.7 | 10.8 | 891.3 | 744.6 | 847.5 | 816.8 | 796 | 776 | 837 | 758.9 | 716.3 | 830.4 | 258.4 | 348 | 390.2 | 291.2 | 405.7 | 407.9 | 397.9 | 380.5 | 581.5 | 369.5
1675 | 1481 | 696.3 | 278.52 | 325.5738 | 420.4 | 449.7 | 376.9 | 365.5 | 745 | 57.8 | 18.3 | 100.6 | 5.6 | 238.9 | 9.5 | 891.4 | 745.5 | 830.8 | 816.1 | 794.4 | 777.7 | 832.8 | 760.7 | 716.3 | 830.8 | 258.7 | 348.2 | 390.7 | 291.3 | 406.7 | 407.8 | 398.1 | 380.7 | 582.1 | 369.7
1676 | 1482 | 697.1 | 278.84 | 325.9479 | 422.8 | 448.5 | 375.7 | 366.2 | 749.9 | 57.8 | 18.3 | 100.4 | 6.7 | 238.2 | 10.5 | 893.4 | 745.8 | 835.9 | 815.4 | 794.8 | 778.6 | 830.1 | 763.9 | 716.5 | 830.6 | 259 | 348.4 | 391.1 | 291.5 | 407.7 | 408 | 398.3 | 380.9 | 582.1 | 370
1677 | 1483 | 696.6 | 278.64 | 325.7141 | 423.9 | 448.5 | 375.7 | 366.1 | 761.1 | 57.8 | 18.3 | 100.2 | 7.5 | 235.7 | 10.5 | 892.1 | 744.7 | 844.2 | 814.7 | 794.8 | 776.7 | 825.4 | 760.4 | 716.4 | 829.7 | 259.3 | 348.7 | 391.3 | 291.7 | 408.5 | 407.7 | 398.6 | 381 | 582 | 370.2
1678 | 1484 | 696.1 | 278.44 | 325.4803 | 424.6 | 448.9 | 375.9 | 366.7 | 766 | 57.8 | 18.3 | 100.1 | 7 | 239.1 | 10.5 | 892.1 | 744.1 | 841.9 | 814.2 | 794.3 | 775.4 | 828.9 | 757.6 | 716.3 | 829.9 | 259.5 | 349 | 391.3 | 291.8 | 409.3 | 407.7 | 398.8 | 381.2 | 582.1 | 370.4
1679 | 1485 | 697.1 | 278.84 | 325.9479 | 425.6 | 449.9 | 376.1 | 366 | 769.9 | 57.8 | 18.3 | 99.9 | 6.9 | 235.2 | 10 | 891.8 | 744.9 | 844.8 | 813.9 | 793.7 | 774.7 | 830.2 | 757.2 | 716.1 | 829.4 | 259.8 | 349.3 | 391.5 | 292 | 409.7 | 407.5 | 399 | 381.3 | 582.2 | 370.6
1680 | 1486 | 697.8 | 279.12 | 326.2752 | 427.1 | 449.3 | 376 | 365.1 | 774.4 | 57.8 | 18.3 | 100 | 6.6 | 244.2 | 9.8 | 890.6 | 744.1 | 851.3 | 813.5 | 793.5 | 773.7 | 831.6 | 755.9 | 716.1 | 829.2 | 260.1 | 349.5 | 391.8 | 292.1 | 410.1 | 407.5 | 399.1 | 381.4 | 582.2 | 370.8
1681 | 1487 | 698.5 | 279.4 | 326.6025 | 426.7 | 448.2 | 376.3 | 364.8 | 759.9 | 57.8 | 18.3 | 100.1 | 6.8 | 242.7 | 10 | 889.1 | 743.8 | 851.2 | 813 | 793.2 | 774.1 | 830.1 | 759 | 715.8 | 830 | 260.4 | 349.8 | 391.9 | 292.3 | 410.5 | 407.7 | 399.2 | 381.6 | 582.2 | 371
1682 | 1488 | 697.9 | 279.16 | 326.322 | 426.1 | 448.1 | 376.7 | 363.3 | 741.9 | 57.8 | 18.3 | 100.2 | 5.8 | 243.6 | 11.6 | 887.7 | 742.9 | 848.2 | 812.7 | 793.5 | 775.3 | 831.9 | 760 | 715.9 | 829.6 | 260.7 | 350 | 392.1 | 292.5 | 411.2 | 407.9 | 399.4 | 381.8 | 582.4 | 371.2
1683 | 1489 | 697.4 | 278.96 | 326.0882 | 425.1 | 447.9 | 377.6 | 362.6 | 748.5 | 57.8 | 18.3 | 100.2 | 6.4 | 246 | 12.3 | 886.6 | 741.9 | 845.9 | 812.2 | 793.7 | 773.2 | 834.9 | 756.9 | 716.2 | 829.2 | 261 | 350.2 | 392.4 | 292.6 | 411.8 | 407.8 | 399.8 | 381.9 | 583.3 | 371.4
1684 | 1490 | 696 | 278.4 | 325.4336 | 424.7 | 446.1 | 378.7 | 363.5 | 750.4 | 57.8 | 18.3 | 100.2 | 6.6 | 239.5 | 12.9 | 886.6 | 742.7 | 836.2 | 811.9 | 793.4 | 775.1 | 835.7 | 761.8 | 716.3 | 829.9 | 261.2 | 350.4 | 392.5 | 292.8 | 412.3 | 407.9 | 400.1 | 382.1 | 583.8 | 371.6
1685 | 1491 | 695.2 | 278.08 | 325.0595 | 424.5 | 448.9 | 378.7 | 364.8 | 733.2 | 57.8 | 18.3 | 100.2 | 6.5 | 237.3 | 12.5 | 886.2 | 742.5 | 842.9 | 811.6 | 795.3 | 774.9 | 836.1 | 761.9 | 716.4 | 830.8 | 261.5 | 350.6 | 392.5 | 292.9 | 412.6 | 408.2 | 400.3 | 382.3 | 583.6 | 371.9
1686 | 1492 | 695.8 | 278.32 | 325.34 | 424.3 | 450.8 | 378.4 | 365.3 | 727.9 | 57.8 | 18.3 | 100.2 | 6.7 | 244.2 | 12.1 | 884.4 | 742.3 | 850.1 | 811.3 | 795.6 | 774.7 | 835.8 | 759 | 716.1 | 831.4 | 261.8 | 350.8 | 392.8 | 293.1 | 412.7 | 408.5 | 400.5 | 382.5 | 583.7 | 372.1
1687 | 1493 | 697.6 | 279.04 | 326.1817 | 424.3 | 450.2 | 378.4 | 366 | 736.1 | 57.9 | 18.3 | 100.2 | 7.1 | 241.2 | 11.1 | 883.1 | 741.7 | 852.2 | 811 | 796.8 | 773.9 | 834.4 | 760 | 716.1 | 832.6 | 262.1 | 350.9 | 392.9 | 293.3 | 413 | 408.8 | 400.6 | 382.7 | 584 | 372.3
1688 | 1494 | 696.4 | 278.56 | 325.6206 | 425.3 | 448.1 | 378.1 | 364.9 | 737.4 | 57.9 | 18.3 | 100.3 | 6.6 | 249.1 | 10 | 882.4 | 741.5 | 862 | 810.7 | 797.3 | 772.8 | 834.5 | 762 | 716.2 | 832 | 262.4 | 351 | 393.1 | 293.4 | 413.1 | 409.3 | 400.7 | 382.8 | 584.5 | 372.5
1689 | 1495 | 698 | 279.2 | 326.3687 | 425.8 | 446.6 | 378.4 | 363.8 | 730.5 | 57.9 | 18.3 | 100.4 | 7.2 | 243.4 | 9.7 | 882.1 | 741.8 | 854.1 | 810.6 | 797.5 | 771.7 | 832.8 | 764.7 | 716.1 | 833.8 | 262.6 | 351.2 | 393.2 | 293.6 | 413.1 | 409.5 | 400.9 | 383.1 | 585 | 372.7
1690 | 1496 | 697.8 | 279.12 | 326.2752 | 424.8 | 446 | 378.5 | 364.4 | 723.4 | 58 | 18.3 | 100.4 | 6.9 | 233.1 | 9.2 | 882.1 | 742.9 | 841 | 810.2 | 798.1 | 770.4 | 831.1 | 764.7 | 716.2 | 835 | 262.9 | 351.4 | 393.3 | 293.8 | 413.2 | 410.2 | 401.2 | 383.4 | 585.2 | 372.9
1691 | 1497 | 695.7 | 278.28 | 325.2933 | 424 | 447.8 | 378.7 | 365.2 | 712.1 | 58 | 18.3 | 100.4 | 6.1 | 206 | 8.2 | 882.6 | 742.7 | 836.7 | 810.2 | 799.2 | 770.5 | 832.2 | 763.6 | 716.3 | 834.8 | 263.2 | 351.5 | 393.2 | 293.9 | 413.1 | 410.5 | 401.4 | 383.6 | 584.9 | 373.1
1692 | 1498 | 693.8 | 277.52 | 324.4049 | 423.6 | 446.8 | 378.1 | 365.8 | 719.4 | 57.9 | 18.3 | 100.2 | 6.7 | 225.7 | 8.5 | 883.5 | 741.4 | 836.9 | 810.1 | 799.1 | 772.3 | 834.7 | 760.1 | 716.5 | 834.3 | 263.5 | 351.6 | 393.5 | 294.1 | 413 | 410.7 | 401.5 | 383.7 | 584.6 | 373.3
1693 | 1499 | 694.2 | 277.68 | 324.5919 | 423.8 | 446.7 | 378 | 365.2 | 719.4 | 57.9 | 18.3 | 100.2 | 7.2 | 243.2 | 9.2 | 884.5 | 742.9 | 832.4 | 810.1 | 798.2 | 773.1 | 834.2 | 758.8 | 716.6 | 834.7 | 263.7 | 351.6 | 393.6 | 294.2 | 412.9 | 411.1 | 401.6 | 383.9 | 584.6 | 373.5
1694 | 1500 | 695 | 278 | 324.966 | 425.4 | 449.4 | 378 | 364.4 | 714.5 | 57.9 | 18.3 | 100.4 | 6.2 | 255.6 | 8.6 | 884 | 742.4 | 831.6 | 810 | 798 | 774.3 | 831.2 | 759.1 | 716.6 | 835.1 | 264 | 351.7 | 393.7 | 294.4 | 412.6 | 411.1 | 401.6 | 384.1 | 584.3 | 373.7
1695 | 1501 | 695.8 | 278.32 | 325.34 | 425.4 | 452 | 377.2 | 363.5 | 711.8 | 57.9 | 18.3 | 100.6 | 6.2 | 229.7 | 8 | 883.4 | 741.7 | 834.5 | 810 | 799.2 | 774.4 | 832.7 | 757.4 | 716.8 | 835.1 | 264.3 | 351.9 | 393.9 | 294.6 | 412.3 | 410.9 | 401.6 | 384.2 | 584.3 | 373.9
1696 | 1502 | 696.8 | 278.72 | 325.8076 | 425.2 | 453.5 | 377.3 | 363.5 | 714.9 | 57.9 | 18.3 | 100.8 | 6.2 | 229.2 | 8.3 | 883.1 | 742.2 | 839 | 809.9 | 801.1 | 773.7 | 834.3 | 755.7 | 716.8 | 835.5 | 264.6 | 352 | 394.1 | 294.7 | 412.1 | 410.8 | 401.5 | 384.3 | 584.9 | 374.1
1697 | 1503 | 696.2 | 278.48 | 325.5271 | 424.1 | 453.1 | 377.6 | 363.3 | 724.5 | 57.9 | 18.3 | 101 | 6.3 | 247.3 | 6.6 | 882.3 | 742.5 | 846.4 | 809.7 | 801.6 | 772.4 | 834 | 754.3 | 716.9 | 835.1 | 264.8 | 352.2 | 394.4 | 294.9 | 411.8 | 411.4 | 401.5 | 384.5 | 585.5 | 374.2
1698 | 1504 | 694.6 | 277.84 | 324.779 | 422.4 | 453.2 | 377.2 | 363.1 | 739.1 | 57.9 | 18.3 | 101.2 | 6.6 | 246.1 | 5.3 | 882.8 | 741.8 | 856.6 | 809.8 | 801.6 | 770.4 | 834.1 | 752.5 | 716.9 | 833.9 | 265.1 | 352.6 | 394.7 | 295 | 411.8 | 412 | 401.6 | 384.7 | 586.2 | 374.4
1699 | 1505 | 693.8 | 277.52 | 324.4049 | 421.4 | 453.3 | 377.6 | 363.8 | 750.1 | 57.9 | 18.3 | 101.5 | 5.8 | 250.3 | 6.5 | 884.4 | 741.6 | 870.7 | 809.8 | 801.6 | 770.7 | 830 | 752.8 | 717.1 | 833.3 | 265.3 | 352.8 | 395 | 295.2 | 412.1 | 412.1 | 401.8 | 384.9 | 586.5 | 374.6
1700 | 1506 | 693.8 | 277.52 | 324.4049 | 421.8 | 452 | 378.4 | 364.3 | 760.6 | 57.9 | 18.3 | 101.7 | 5.9 | 253.2 | 7.3 | 885.6 | 741.5 | 873.8 | 809.8 | 801.8 | 770.8 | 826.1 | 753 | 717.1 | 832 | 265.5 | 353.1 | 395.2 | 295.3 | 412.5 | 412.4 | 402.2 | 385.1 | 586.4 | 374.8
1701 | 1507 | 692.9 | 277.16 | 323.9841 | 422.5 | 449.8 | 378.1 | 364.8 | 758.6 | 58 | 18.3 | 102 | 6.8 | 211.6 | 6.8 | 886.3 | 741.6 | 862.6 | 810.2 | 799 | 772.8 | 825.1 | 753.8 | 717 | 831 | 265.8 | 353.3 | 395.1 | 295.5 | 412.8 | 412.8 | 402.2 | 385.3 | 586.2 | 375
1702 | 1508 | 692.6 | 277.04 | 323.8438 | 423.8 | 447.7 | 377.9 | 365.9 | 742.1 | 58.1 | 18.3 | 102.2 | 6.7 | 228.1 | 6.5 | 887.7 | 742.4 | 843.7 | 810.4 | 795.2 | 773.5 | 826.5 | 757.8 | 716.9 | 828 | 266 | 353.6 | 395.2 | 295.7 | 412.9 | 413 | 402.4 | 385.4 | 586.1 | 375.2
1703 | 1509 | 693.8 | 277.52 | 324.4049 | 424.8 | 445.9 | 377.1 | 366.5 | 746.9 | 58.1 | 18.3 | 102.4 | 6 | 233.7 | 7.1 | 887.9 | 742.2 | 839.8 | 810.5 | 794.1 | 773.4 | 827 | 760.4 | 716.9 | 827.4 | 266.2 | 353.8 | 395.5 | 295.8 | 413.1 | 413.2 | 402.5 | 385.5 | 585.7 | 375.4
1704 | 1510 | 695.7 | 278.28 | 325.2933 | 425 | 443.4 | 376.6 | 365.4 | 753 | 58.1 | 18.3 | 102.4 | 6 | 233 | 6.4 | 887.4 | 741.7 | 842.4 | 810.5 | 793.6 | 773.1 | 828.9 | 760.5 | 717.1 | 826.7 | 266.4 | 353.9 | 395.7 | 296 | 413.5 | 413.4 | 402.6 | 385.6 | 585.3 | 375.6
1705 | 1511 | 696.3 | 278.52 | 325.5738 | 425.3 | 442.8 | 377.1 | 364.9 | 763.6 | 58.2 | 18.3 | 102.3 | 6 | 250.1 | 5.9 | 887.4 | 741 | 842.6 | 810.6 | 794.3 | 772.2 | 828.4 | 758.2 | 717.3 | 826.8 | 266.5 | 354.1 | 396.1 | 296.1 | 414 | 413.1 | 403 | 385.7 | 585.2 | 375.8
1706 | 1512 | 695.6 | 278.24 | 325.2465 | 425.7 | 441 | 377.3 | 364.2 | 764.2 | 58.2 | 18.3 | 102.1 | 5.7 | 239.5 | 5.8 | 886.1 | 741.1 | 837.7 | 810.9 | 795.5 | 773.1 | 830.7 | 756.9 | 717.5 | 828 | 266.7 | 354.1 | 396.1 | 296.3 | 414.7 | 412.6 | 403.4 | 385.7 | 585.3 | 376
1707 | 1513 | 695.7 | 278.28 | 325.2933 | 426 | 443.1 | 378.3 | 365 | 756.9 | 58.2 | 18.3 | 102.1 | 5.9 | 259.5 | 5.8 | 885.4 | 741.6 | 839.3 | 811.2 | 797.6 | 771.4 | 833.3 | 754.4 | 717.7 | 828.8 | 266.8 | 354.1 | 396.3 | 296.5 | 415.4 | 412.2 | 403.8 | 385.8 | 585.7 | 376.2
1708 | 1514 | 695.9 | 278.36 | 325.3868 | 427.8 | 444.1 | 378.7 | 365.8 | 757 | 58.1 | 18.3 | 102 | 5.7 | 262.8 | 6.1 | 887.3 | 742.4 | 845.7 | 811.8 | 797.9 | 770.3 | 832.7 | 753.7 | 717.8 | 830.2 | 266.9 | 354.1 | 396.6 | 296.6 | 415.8 | 412 | 404 | 385.9 | 586.2 | 376.4
1709 | 1515 | 693.8 | 277.52 | 324.4049 | 429.3 | 443.6 | 379.6 | 365.4 | 752.1 | 58.1 | 18.3 | 101.9 | 6.1 | 249.8 | 6.8 | 888.4 | 742.8 | 847.6 | 812.1 | 796.7 | 771.2 | 831.9 | 754.3 | 717.6 | 829.3 | 267.1 | 354.1 | 396.5 | 296.8 | 416 | 411.7 | 404.2 | 386 | 586.4 | 376.6
1710 | 1516 | 692.5 | 277 | 323.797 | 430.5 | 444.5 | 380.1 | 365 | 763.4 | 58.1 | 18.3 | 101.9 | 6.2 | 221.8 | 6.7 | 888.6 | 742.1 | 859.4 | 811.9 | 797.1 | 770.1 | 827.4 | 752.5 | 717.7 | 828.5 | 267.2 | 354.2 | 397.1 | 297 | 416.5 | 411.8 | 404.4 | 386.1 | 586.1 | 376.8
1711 | 1517 | 693.3 | 277.32 | 324.1711 | 431.2 | 444.2 | 380.4 | 364.9 | 777.1 | 58.2 | 18.3 | 101.8 | 6.6 | 243.2 | 6.5 | 890.4 | 741.6 | 856.6 | 812.2 | 794.6 | 770.4 | 821 | 754.9 | 717.8 | 827 | 267.3 | 354.5 | 397.5 | 297.1 | 416.8 | 411.8 | 404.7 | 386.3 | 586.2 | 377
1712 | 1518 | 693.2 | 277.28 | 324.1243 | 431.5 | 442.6 | 380.4 | 365.1 | 782.9 | 58.2 | 18.3 | 101.8 | 7.8 | 258.9 | 7.4 | 890.9 | 741.6 | 847.4 | 812.3 | 792 | 769.1 | 815.6 | 756.3 | 717.6 | 824.3 | 267.4 | 354.8 | 397.8 | 297.3 | 417.3 | 411.7 | 404.9 | 386.3 | 586.4 | 377.2
1713 | 1519 | 694.1 | 277.64 | 324.5452 | 431.4 | 442.2 | 380.7 | 365.2 | 783.5 | 58.3 | 18.3 | 101.7 | 7.9 | 267.3 | 7.6 | 890.6 | 741.7 | 847.5 | 812.3 | 792.4 | 769.7 | 817.4 | 757.2 | 717.7 | 824.5 | 267.6 | 355.1 | 397.7 | 297.5 | 417.5 | 411.4 | 405.1 | 386.4 | 586.2 | 377.4
1714 | 1520 | 694.9 | 277.96 | 324.9192 | 431.2 | 441.8 | 380.8 | 365.6 | 778 | 58.3 | 18.3 | 101.7 | 8 | 281 | 7.3 | 891 | 741.1 | 839.2 | 812.5 | 792.4 | 769.7 | 821.7 | 756.6 | 717.9 | 825.6 | 267.8 | 355.4 | 397.6 | 297.6 | 417.5 | 411.2 | 405.2 | 386.5 | 586 | 377.6
1715 | 1521 | 694 | 277.6 | 324.4984 | 432.9 | 440.3 | 380.1 | 366.2 | 775.6 | 58.3 | 18.3 | 101.8 | 7.2 | 256.8 | 7 | 891.9 | 740.8 | 840.8 | 812.7 | 792.6 | 769.9 | 824.8 | 754.9 | 718 | 826.4 | 268 | 355.8 | 398 | 297.8 | 418 | 410.9 | 405.4 | 386.6 | 586.1 | 377.8
1716 | 1522 | 692.8 | 277.12 | 323.9373 | 433.4 | 439.4 | 379.2 | 366 | 783.1 | 58.4 | 18.3 | 101.8 | 8.5 | 270.6 | 8.2 | 892.4 | 741.3 | 839.8 | 812.9 | 792.7 | 769.7 | 820.6 | 754.8 | 718.4 | 825.3 | 268.3 | 356.1 | 398.9 | 297.9 | 418.7 | 410.6 | 405.7 | 386.6 | 586.2 | 378
1717 | 1523 | 692.3 | 276.92 | 323.7035 | 433.3 | 439.9 | 379.6 | 366.6 | 789.6 | 58.5 | 18.3 | 102 | 9.3 | 274.1 | 9.8 | 893 | 741.1 | 835.4 | 813.1 | 793.1 | 769.5 | 814.4 | 755.9 | 718.6 | 824.1 | 268.5 | 356.3 | 399.2 | 298.1 | 419.4 | 410.7 | 406.1 | 386.7 | 586.5 | 378.2
1718 | 1524 | 692.9 | 277.16 | 323.9841 | 433.4 | 441.1 | 379.8 | 367.1 | 787.4 | 58.5 | 18.3 | 102.1 | 8.3 | 254.6 | 11.5 | 892.6 | 741.3 | 840.8 | 813.2 | 792.8 | 768.6 | 817.8 | 755 | 718.6 | 824.7 | 268.7 | 356.5 | 399.4 | 298.3 | 420.3 | 410.8 | 406.4 | 386.8 | 587 | 378.4
1719 | 1525 | 693.9 | 277.56 | 324.4516 | 432.9 | 442.9 | 379.4 | 367.8 | 791.8 | 58.5 | 18.3 | 102 | 7.1 | 262.9 | 13.5 | 894.6 | 741.2 | 848.4 | 813.2 | 792.7 | 767.6 | 816.2 | 754.2 | 718.6 | 824.1 | 268.9 | 356.6 | 399.7 | 298.4 | 421.1 | 410.6 | 406.7 | 386.9 | 587.2 | 378.7
1720 | 1526 | 693.8 | 277.52 | 324.4049 | 432.9 | 444.7 | 379.1 | 367.8 | 786.7 | 58.6 | 18.2 | 102 | 7.1 | 273.1 | 13.1 | 895.3 | 740.7 | 854 | 813.1 | 792.5 | 768.7 | 808.7 | 754.8 | 718.7 | 820.8 | 269.1 | 357 | 400 | 298.6 | 421.9 | 410.2 | 407 | 386.9 | 587.2 | 378.9
1721 | 1527 | 693.4 | 277.36 | 324.2179 | 433.3 | 444.4 | 379.8 | 367.1 | 783.4 | 58.6 | 18.2 | 102.1 | 7.3 | 278.4 | 13.5 | 895.9 | 740.8 | 850.8 | 813.4 | 793.2 | 769.1 | 804.2 | 754.2 | 718.9 | 820.3 | 269.3 | 357.3 | 400.5 | 298.7 | 422.1 | 409.9 | 407.2 | 387 | 587.4 | 379.1
1722 | 1528 | 694.2 | 277.68 | 324.5919 | 433.6 | 445.1 | 381.4 | 367.3 | 776.1 | 58.7 | 18.2 | 102.2 | 7.6 | 272 | 12.8 | 895.4 | 741.6 | 849.6 | 813.8 | 792.6 | 770.7 | 805.5 | 754.7 | 718.9 | 820.6 | 269.5 | 357.6 | 400.5 | 298.9 | 422.1 | 410.4 | 407.2 | 387.2 | 587.7 | 379.3
1723 | 1529 | 693.5 | 277.4 | 324.2646 | 433.5 | 447.9 | 383 | 367.7 | 771.6 | 58.8 | 18.2 | 102.3 | 7.6 | 258.4 | 11.4 | 895 | 742.3 | 840.1 | 814.1 | 792.5 | 770.2 | 810.6 | 756.2 | 718.7 | 821.8 | 269.7 | 357.9 | 400.3 | 299 | 421.9 | 411.1 | 407.1 | 387.4 | 587.7 | 379.5
1724 | 1530 | 691.6 | 276.64 | 323.3762 | 433.5 | 450.1 | 383.1 | 367.4 | 775.5 | 58.9 | 18.2 | 102.5 | 7.7 | 254.4 | 10.4 | 893.9 | 741.6 | 845.4 | 814.2 | 794.8 | 769 | 814.8 | 756.3 | 718.7 | 820.9 | 269.9 | 358.2 | 400.7 | 299.2 | 421.5 | 411.5 | 407.2 | 387.4 | 587.4 | 379.7
1725 | 1531 | 690 | 276 | 322.6281 | 433.7 | 449.8 | 381.8 | 366.5 | 774.4 | 59 | 18.2 | 102.7 | 7.3 | 254.6 | 10.4 | 893.3 | 741.7 | 857.6 | 814.6 | 795.5 | 770.4 | 818.7 | 754.9 | 718.8 | 822.8 | 270.1 | 358.5 | 400.9 | 299.4 | 421.6 | 411.8 | 407.2 | 387.6 | 587.2 | 379.8
1726 | 1532 | 690.9 | 276.36 | 323.0489 | 433.3 | 448.7 | 380.8 | 366.2 | 773.2 | 59.1 | 18.2 | 102.8 | 6.7 | 250.3 | 10.4 | 892.9 | 741.7 | 857.7 | 815 | 796.6 | 771.4 | 821.5 | 754.4 | 718.6 | 823.8 | 270.4 | 358.8 | 400.9 | 299.5 | 421.8 | 412.3 | 407.3 | 387.7 | 587.4 | 380
1727 | 1533 | 691.9 | 276.76 | 323.5165 | 431.5 | 448 | 381.5 | 366.3 | 754.5 | 59.3 | 18.2 | 102.8 | 7.4 | 256.6 | 11.2 | 892.3 | 741.3 | 852.4 | 815.2 | 796.5 | 770.2 | 819.1 | 753.6 | 718.1 | 824.2 | 270.6 | 359 | 401 | 299.6 | 422.3 | 413.5 | 407.5 | 387.8 | 587.6 | 380.2
1728 | 1534 | 692.5 | 277 | 323.797 | 431.9 | 447.9 | 382.3 | 367 | 729.1 | 59.3 | 18.2 | 102.9 | 7.1 | 272.6 | 9.5 | 892.1 | 740.9 | 845 | 815.5 | 796.6 | 768.7 | 821.4 | 754.1 | 717.6 | 824.3 | 270.8 | 359.3 | 401.1 | 299.8 | 422.9 | 414.3 | 407.8 | 388 | 588 | 380.4
1729 | 1535 | 691.7 | 276.68 | 323.423 | 433.5 | 447.4 | 382.5 | 367.4 | 719.2 | 59.3 | 18.2 | 102.8 | 7.4 | 266.2 | 8.2 | 892.3 | 741.6 | 842.7 | 815.8 | 797.7 | 767.9 | 822.1 | 754.7 | 717.4 | 825 | 271 | 359.5 | 401.2 | 299.9 | 423 | 414.5 | 407.8 | 388.3 | 588.5 | 380.6
1730 | 1536 | 691.7 | 276.68 | 323.423 | 433 | 446.4 | 382.8 | 366.5 | 719 | 59.3 | 18.2 | 102.9 | 6.8 | 271 | 12.8 | 892.3 | 741.8 | 849.3 | 816.2 | 799.8 | 768.7 | 828.4 | 755.1 | 717.5 | 825.5 | 271.2 | 359.8 | 401.3 | 300.1 | 422.8 | 414.5 | 407.7 | 388.4 | 588.6 | 380.8
1731 | 1537 | 691.6 | 276.64 | 323.3762 | 432.2 | 446.2 | 382.6 | 365.6 | 727.3 | 59.3 | 18.2 | 102.9 | 6.5 | 249.1 | 13 | 893.2 | 743.2 | 859.6 | 816.5 | 801.9 | 768.8 | 827.8 | 755 | 717.9 | 826 | 271.3 | 359.9 | 401.7 | 300.2 | 422.8 | 415.3 | 407.8 | 388.6 | 588.9 | 380.9
1732 | 1538 | 691.5 | 276.6 | 323.3295 | 431 | 449.7 | 382.6 | 364.9 | 735.8 | 59.4 | 18.2 | 103.1 | 7.4 | 244.4 | 14.8 | 892.3 | 743 | 859.3 | 816.9 | 802.2 | 768.3 | 829.5 | 753.3 | 718 | 826.5 | 271.5 | 359.9 | 401.7 | 300.4 | 422.9 | 415.7 | 407.9 | 388.8 | 589.4 | 381.1
1733 | 1539 | 690.8 | 276.32 | 323.0022 | 429.9 | 449.9 | 382 | 365.2 | 741.4 | 59.3 | 18.2 | 103.3 | 8.2 | 254.7 | 15.6 | 891.5 | 743 | 857.2 | 817 | 803.3 | 767.1 | 832.4 | 753.9 | 717.7 | 827.4 | 271.6 | 359.7 | 401.8 | 300.6 | 423.1 | 416.2 | 408.1 | 389 | 590 | 381.3
1734 | 1540 | 689.9 | 275.96 | 322.5813 | 429.4 | 448.8 | 382 | 367.2 | 732.7 | 59.3 | 18.2 | 103.5 | 9.7 | 253.6 | 16.7 | 892.4 | 743.6 | 855.1 | 817.3 | 804.4 | 766.4 | 832.4 | 756.8 | 717.5 | 829.5 | 271.7 | 359.7 | 401.8 | 300.7 | 423.3 | 417 | 408.4 | 389.3 | 590.7 | 381.5
1735 | 1541 | 690.8 | 276.32 | 323.0022 | 427.8 | 448.4 | 381.1 | 367.1 | 715.1 | 59.3 | 18.2 | 103.7 | 9.9 | 271.3 | 16.7 | 891 | 743.8 | 861.6 | 817.6 | 805.8 | 766 | 833.5 | 755.3 | 717.4 | 829.1 | 271.8 | 359.6 | 401.8 | 300.9 | 423.4 | 417.4 | 408.5 | 389.4 | 591.2 | 381.7
1736 | 1542 | 689.7 | 275.88 | 322.4878 | 426.3 | 448.2 | 380 | 365.9 | 707.4 | 59.4 | 18.2 | 103.8 | 8.4 | 254 | 15.9 | 890.9 | 744.5 | 863.6 | 817.8 | 807.5 | 765.2 | 836.4 | 756.3 | 717.2 | 830.3 | 271.9 | 359.5 | 402 | 301.1 | 423.3 | 417.7 | 408.6 | 389.6 | 591.6 | 381.9
1737 | 1543 | 690.2 | 276.08 | 322.7216 | 425.8 | 447.1 | 380 | 365.7 | 708.8 | 59.4 | 18.2 | 103.5 | 6.7 | 242.1 | 17.5 | 891.2 | 744.9 | 866.1 | 818 | 809.2 | 765.1 | 834.9 | 756.6 | 717.2 | 830.9 | 272 | 359.4 | 402.2 | 301.2 | 423.1 | 418 | 408.6 | 389.8 | 592 | 382.1
1738 | 1544 | 689.3 | 275.72 | 322.3008 | 424.9 | 445.4 | 380.5 | 365.1 | 724.9 | 59.3 | 18.2 | 103.2 | 6.5 | 266.2 | 15.3 | 890.5 | 744.5 | 870.1 | 818.1 | 809.2 | 764.1 | 833.5 | 754.4 | 717 | 831.4 | 272.1 | 359.4 | 402.4 | 301.4 | 422.7 | 418.2 | 408.5 | 389.9 | 592.3 | 382.2
1739 | 1545 | 688.3 | 275.32 | 321.8332 | 423.8 | 445.6 | 380.5 | 365 | 730.1 | 59.2 | 18.2 | 102.9 | 10 | 262.9 | 14.9 | 889.9 | 744.1 | 864.8 | 818.2 | 808.9 | 763.2 | 834.7 | 752.1 | 716.8 | 831.1 | 272.1 | 359.6 | 402.4 | 301.6 | 422.5 | 418.5 | 408.6 | 390.1 | 592.5 | 382.4
1740 | 1546 | 689.5 | 275.8 | 322.3943 | 422.4 | 444.8 | 379.9 | 365.2 | 730 | 59.2 | 18.2 | 102.9 | 8.5 | 259.1 | 14.9 | 889.6 | 743.6 | 856.8 | 818.2 | 811.5 | 764.8 | 832.2 | 750.4 | 717 | 830 | 272.3 | 359.8 | 402.8 | 301.8 | 422.3 | 418.3 | 408.7 | 390.1 | 593.1 | 382.5
1741 | 1547 | 690.2 | 276.08 | 322.7216 | 422 | 444.8 | 379 | 365.2 | 734.4 | 59.2 | 18.2 | 103 | 8.1 | 255.9 | 15.8 | 890.2 | 744.7 | 857.9 | 818.5 | 812.5 | 766.5 | 824.2 | 753 | 717.4 | 830.9 | 272.4 | 360 | 403 | 301.9 | 422.2 | 417.7 | 408.9 | 390.2 | 593.8 | 382.7
1742 | 1548 | 689 | 275.6 | 322.1605 | 423.1 | 448.1 | 379 | 365.5 | 725.6 | 59.3 | 18.2 | 103.1 | 7.4 | 248.6 | 17.6 | 890 | 745.5 | 861.9 | 818.9 | 814.4 | 766.8 | 824.7 | 752.4 | 717.7 | 830.8 | 272.5 | 360.2 | 403.1 | 302.1 | 422.2 | 417.8 | 409.1 | 390.3 | 594.6 | 382.9
1743 | 1549 | 687.6 | 275.04 | 321.5059 | 422.8 | 452.4 | 378.4 | 366.9 | 730.2 | 59.5 | 18.2 | 103 | 7.6 | 248.5 | 17.8 | 889.4 | 745.6 | 864.5 | 819.1 | 813.4 | 765.4 | 828.7 | 753.5 | 717.4 | 830 | 272.7 | 360.4 | 403.2 | 302.3 | 422.3 | 417.9 | 409.3 | 390.5 | 595.2 | 383.1
1744 | 1550 | 686.5 | 274.6 | 320.9916 | 423.5 | 453.9 | 379 | 367.3 | 730.2 | 59.5 | 18.2 | 102.8 | 8 | 250.9 | 15.5 | 889.1 | 745.1 | 856.3 | 819.1 | 813 | 764.8 | 828.8 | 752.6 | 717.4 | 830.5 | 272.8 | 360.8 | 403.1 | 302.4 | 422.3 | 417.8 | 409.3 | 390.6 | 595.5 | 383.3
1745 | 1551 | 688 | 275.2 | 321.6929 | 424.4 | 454.2 | 379.2 | 367.2 | 732 | 59.5 | 18.2 | 102.6 | 8.1 | 259.7 | 12.3 | 888.8 | 745.4 | 846 | 819.4 | 813.2 | 765.3 | 828.4 | 756.3 | 717.5 | 831.9 | 273 | 361.1 | 403.4 | 302.6 | 422.2 | 418.4 | 409.3 | 390.8 | 595.6 | 383.4
1746 | 1552 | 687.6 | 275.04 | 321.5059 | 423.3 | 455.8 | 378.5 | 367.5 | 731.3 | 59.6 | 18.2 | 102.4 | 8.4 | 261.8 | 11.4 | 887.6 | 745.6 | 845.8 | 819.4 | 813.3 | 766.1 | 830.3 | 755.5 | 717.5 | 832.1 | 273.1 | 361.2 | 403.5 | 302.7 | 422.3 | 418.8 | 409.3 | 391 | 595.7 | 383.6
1747 | 1553 | 688 | 275.2 | 321.6929 | 422.2 | 456 | 379.6 | 367.7 | 748.2 | 59.7 | 18.2 | 102.4 | 9.1 | 266.4 | 13.2 | 887.5 | 745.5 | 846.7 | 819.8 | 814.6 | 766.1 | 831.7 | 755.1 | 717.8 | 834.4 | 273.2 | 361.3 | 403.7 | 302.9 | 422.7 | 419.2 | 409.6 | 391.2 | 595.8 | 383.8
1748 | 1554 | 687.1 | 274.84 | 321.2721 | 421.3 | 456.7 | 380 | 367.7 | 758.3 | 59.7 | 18.2 | 102.5 | 9.7 | 262.8 | 17.3 | 887.5 | 745.2 | 852.7 | 820.5 | 814 | 766 | 827.8 | 754 | 718.1 | 833.8 | 273.3 | 361.4 | 404 | 303 | 423.1 | 419.7 | 409.8 | 391.3 | 596.2 | 384
1749 | 1555 | 687.6 | 275.04 | 321.5059 | 422.2 | 456.8 | 380.1 | 368.2 | 761.6 | 59.7 | 18.2 | 102.8 | 9.8 | 264.9 | 18.6 | 889.1 | 744.3 | 834.1 | 820.6 | 811.9 | 766.7 | 827.2 | 755.7 | 718.1 | 833.9 | 273.5 | 361.4 | 404.2 | 303.2 | 423.1 | 420 | 410 | 391.5 | 596.5 | 384.2
1750 | 1556 | 687.3 | 274.92 | 321.3656 | 424 | 459.8 | 380.7 | 369 | 765.4 | 59.8 | 18.2 | 103.1 | 9 | 272.7 | 16.2 | 890.4 | 743.7 | 840.9 | 820.4 | 812.3 | 767.4 | 825.2 | 755.8 | 718.2 | 833.9 | 273.6 | 361.5 | 404.7 | 303.4 | 423.1 | 420.1 | 410.2 | 391.7 | 596.2 | 384.4
1751 | 1557 | 687.1 | 274.84 | 321.2721 | 425.2 | 462.2 | 382 | 369.3 | 763.3 | 59.9 | 18.2 | 103.2 | 8.2 | 274.8 | 14.4 | 891.6 | 744.2 | 853.5 | 820.5 | 814 | 768.2 | 826.3 | 754.8 | 718.4 | 832.9 | 273.7 | 361.7 | 404.7 | 303.6 | 423.1 | 420.2 | 410.4 | 391.9 | 595.8 | 384.6
1752 | 1558 | 688.2 | 275.28 | 321.7865 | 425.9 | 462.8 | 382.6 | 369.1 | 758 | 60 | 18.2 | 103.1 | 7.4 | 259.6 | 15.8 | 892.8 | 744.3 | 863 | 820.7 | 814.8 | 768.3 | 823.9 | 756.5 | 718.5 | 833 | 273.8 | 361.8 | 404.9 | 303.8 | 422.8 | 420.3 | 410.4 | 392.1 | 595.6 | 384.7
1753 | 1559 | 687.8 | 275.12 | 321.5994 | 425.6 | 463.9 | 382.8 | 367.7 | 742.9 | 60.1 | 18.2 | 103.1 | 6.7 | 268.5 | 16.3 | 893.2 | 745.4 | 859.8 | 821 | 816.2 | 768.3 | 815.8 | 757.7 | 718.7 | 833.6 | 273.9 | 362.1 | 404.8 | 303.9 | 422.2 | 420.3 | 410.4 | 392.2 | 595.8 | 384.9
1754 | 1560 | 687.2 | 274.88 | 321.3189 | 424.4 | 463.2 | 382.9 | 366.3 | 735.3 | 60.1 | 18.2 | 103.1 | 6.5 | 270.7 | 16.7 | 893.4 | 745 | 861.9 | 821.2 | 816.8 | 766.9 | 817.4 | 756.3 | 718.8 | 832.5 | 274 | 362.4 | 404.7 | 304.1 | 422 | 420.2 | 410.3 | 392.3 | 596.1 | 385.1
1755 | 1561 | 686.6 | 274.64 | 321.0383 | 423.5 | 463.3 | 382.8 | 366.5 | 719.2 | 60.1 | 18.2 | 102.9 | 7 | 252 | 15.7 | 892.8 | 744.6 | 863.8 | 821.6 | 816.6 | 766.5 | 821.6 | 755.6 | 718.4 | 831.8 | 274.1 | 362.5 | 404.8 | 304.2 | 421.7 | 420.4 | 410.3 | 392.5 | 596.6 | 385.2
1756 | 1562 | 688.2 | 275.28 | 321.7865 | 423.5 | 461.7 | 382 | 366.8 | 724.9 | 60 | 18.2 | 103 | 7.5 | 252.7 | 13.5 | 893.8 | 744.8 | 860 | 821.9 | 817.1 | 767.2 | 823.8 | 753.9 | 718.4 | 832 | 274.3 | 362.6 | 405 | 304.4 | 421.5 | 420.7 | 410.3 | 392.6 | 597 | 385.4
1757 | 1563 | 689.1 | 275.64 | 322.2073 | 424.1 | 460.5 | 381.4 | 366.5 | 737.5 | 59.9 | 18.2 | 103 | 7.8 | 253.9 | 12.5 | 893.6 | 745.1 | 866.4 | 822.2 | 817.4 | 767.4 | 824.1 | 753.1 | 718.4 | 832.8 | 274.4 | 362.8 | 405.4 | 304.6 | 421.2 | 420.7 | 410.3 | 392.8 | 597.3 | 385.5
1758 | 1564 | 686.7 | 274.68 | 321.0851 | 424.6 | 458.8 | 381.2 | 366.3 | 743.5 | 59.9 | 18.2 | 103.1 | 8 | 261.4 | 12.5 | 893.3 | 744.2 | 861.9 | 822.2 | 817.4 | 766.7 | 825.3 | 751.8 | 718.3 | 833 | 274.5 | 363.1 | 405.6 | 304.7 | 420.8 | 420.7 | 410.3 | 392.9 | 597.7 | 385.7
1759 | 1565 | 687 | 274.8 | 321.2254 | 425.2 | 457.7 | 381 | 366.3 | 750.6 | 60 | 18.2 | 103.4 | 9.8 | 262.9 | 11.5 | 893.1 | 743.1 | 868.1 | 822.4 | 816.5 | 767.5 | 827 | 751.4 | 718.4 | 833.1 | 274.6 | 363.4 | 405.7 | 304.9 | 420.5 | 421 | 410.5 | 393.1 | 597.8 | 385.9
1760 | 1566 | 687.4 | 274.96 | 321.4124 | 425.8 | 457.8 | 381.1 | 366.2 | 749.4 | 60 | 18.2 | 103.8 | 9.4 | 258.8 | 10.7 | 893.3 | 742.5 | 853.4 | 822.6 | 815.4 | 767.5 | 828.8 | 751.5 | 718.5 | 832.8 | 274.7 | 363.7 | 405.6 | 305 | 420.3 | 420.9 | 410.6 | 393.2 | 598.2 | 386.1
1761 | 1567 | 687.5 | 275 | 321.4592 | 426.3 | 457.6 | 381.2 | 366.5 | 748.7 | 60 | 18.2 | 104 | 8.2 | 241.8 | 10.1 | 894.2 | 743.4 | 847.5 | 822.7 | 815.2 | 768.2 | 831.5 | 752.2 | 718.6 | 834.1 | 274.8 | 363.9 | 405.8 | 305.2 | 420 | 421 | 410.7 | 393.4 | 598.3 | 386.2
1762 | 1568 | 686.1 | 274.44 | 320.8045 | 427.6 | 455.4 | 381.3 | 366.6 | 745 | 60 | 18.2 | 104.1 | 9.2 | 245.2 | 9.2 | 894.5 | 743.9 | 828.8 | 822.9 | 813.9 | 767.2 | 833.7 | 752.6 | 718.7 | 834.8 | 274.9 | 364.1 | 406 | 305.4 | 420 | 421.4 | 410.8 | 393.6 | 598.3 | 386.4
1763 | 1569 | 686.8 | 274.72 | 321.1319 | 429.3 | 455.2 | 381.4 | 366.9 | 725.5 | 60.1 | 18.2 | 104 | 8.1 | 254 | 11.5 | 895.1 | 744.7 | 816.4 | 823 | 812.3 | 765.1 | 832 | 753.6 | 718.3 | 835.3 | 275 | 364.2 | 405.9 | 305.5 | 419.7 | 422 | 410.8 | 393.7 | 598.2 | 386.6
1764 | 1570 | 687.9 | 275.16 | 321.6462 | 430.8 | 456.1 | 381.4 | 367 | 708.8 | 60.1 | 18.2 | 103.9 | 7.4 | 242.3 | 12.1 | 895.2 | 745.2 | 817.5 | 823 | 811.5 | 764.2 | 830.1 | 756.4 | 718.4 | 836 | 275.1 | 364.6 | 405.8 | 305.7 | 419.4 | 422 | 410.8 | 393.9 | 597.9 | 386.7
1765 | 1571 | 687.9 | 275.16 | 321.6462 | 431.2 | 455.4 | 380.8 | 366.9 | 692.4 | 60.1 | 18.2 | 103.8 | 7.5 | 252.8 | 13.3 | 895.1 | 744.6 | 825 | 823.2 | 811.3 | 764.1 | 830.5 | 754.5 | 718.5 | 836.1 | 275.3 | 364.9 | 406 | 305.9 | 419.2 | 422.5 | 410.9 | 394.1 | 597.8 | 386.9
1766 | 1572 | 687.7 | 275.08 | 321.5527 | 432.7 | 454.4 | 380.6 | 367.2 | 686.1 | 60.1 | 18.2 | 103.9 | 7.5 | 252.6 | 14.6 | 895 | 744.1 | 835.4 | 823.4 | 812.2 | 764.2 | 832.1 | 755.7 | 718.4 | 836.3 | 275.4 | 365.2 | 406.1 | 306.2 | 419.2 | 423 | 411.1 | 394.4 | 597.9 | 387
1767 | 1573 | 687.5 | 275 | 321.4592 | 433.6 | 453.8 | 380.9 | 366.9 | 678.2 | 60.1 | 18.2 | 104 | 7.4 | 244.1 | 14 | 895.4 | 743.7 | 832.3 | 823.6 | 812.6 | 763 | 832.3 | 754.4 | 718.4 | 836.1 | 275.5 | 365.4 | 406.2 | 306.4 | 419.2 | 423.8 | 411.3 | 394.6 | 598.4 | 387.2
1768 | 1574 | 687.2 | 274.88 | 321.3189 | 434 | 452.6 | 381.2 | 366.7 | 667.8 | 60.2 | 18.2 | 104.1 | 6.6 | 250.2 | 13.5 | 896.1 | 743.7 | 844.9 | 823.6 | 814.3 | 761.3 | 832 | 756.4 | 718.4 | 836.8 | 275.6 | 365.5 | 406.3 | 306.5 | 419.3 | 423.9 | 411.4 | 394.8 | 598.8 | 387.4
1769 | 1575 | 687 | 274.8 | 321.2254 | 433.6 | 451.1 | 381.4 | 367 | 664.4 | 60.2 | 18.2 | 104.3 | 5.8 | 246.9 | 13.7 | 896.5 | 743.8 | 852.5 | 823.9 | 815.1 | 761.2 | 832.6 | 755.6 | 718.2 | 836.9 | 275.7 | 365.6 | 406.3 | 306.7 | 419.4 | 424.3 | 411.6 | 395 | 599.4 | 387.6
1770 | 1576 | 686.9 | 274.76 | 321.1786 | 433.2 | 450.6 | 382.1 | 367.8 | 668.8 | 60.2 | 18.2 | 104.4 | 6.4 | 240.8 | 13 | 895.7 | 743.5 | 860.6 | 824.2 | 815.2 | 760.9 | 829.3 | 755.9 | 718.1 | 837.3 | 275.8 | 365.8 | 406.5 | 306.9 | 419.5 | 424.5 | 411.8 | 395.1 | 599.8 | 387.8
1771 | 1577 | 686.5 | 274.6 | 320.9916 | 433 | 451.6 | 381.4 | 367.7 | 662.5 | 60.2 | 18.1 | 104.5 | 7.1 | 247.4 | 12 | 895.4 | 743.1 | 864.7 | 824.4 | 815.9 | 760.9 | 830.1 | 757.9 | 718.2 | 838.4 | 276 | 366 | 406.7 | 307.1 | 419.8 | 425 | 412 | 395.4 | 600.1 | 388
1772 | 1578 | 686.2 | 274.48 | 320.8513 | 431.4 | 452.1 | 380.4 | 368.5 | 653 | 60.3 | 18.1 | 104.5 | 8.3 | 243.1 | 10.5 | 895.8 | 743.4 | 858.9 | 824.8 | 817.3 | 760.2 | 831 | 759.5 | 718.3 | 837.5 | 276.1 | 366 | 406.7 | 307.3 | 419.6 | 425.1 | 412.2 | 395.6 | 600.5 | 388.1
1773 | 1579 | 685.7 | 274.28 | 320.6175 | 430.2 | 451.5 | 381.1 | 368.4 | 661.1 | 60.2 | 18.1 | 104.5 | 8.4 | 251.1 | 9 | 896.1 | 744.8 | 854.7 | 825.1 | 817.8 | 761.3 | 831.8 | 758.3 | 718.2 | 837.6 | 276.3 | 365.9 | 406.8 | 307.5 | 419.4 | 425 | 412.3 | 395.7 | 600.9 | 388.3
1774 | 1580 | 685.1 | 274.04 | 320.337 | 430.5 | 451.5 | 381.9 | 368.4 | 686.3 | 60.2 | 18.1 | 104.6 | 9.6 | 235.6 | 7.8 | 895.3 | 745 | 857.6 | 825.1 | 818.5 | 763.7 | 833.3 | 757.4 | 718.7 | 838.1 | 276.4 | 365.9 | 407 | 307.7 | 419.3 | 424.8 | 412.4 | 395.8 | 601 | 388.5
1775 | 1581 | 685.9 | 274.36 | 320.711 | 429.9 | 452.1 | 382.6 | 369 | 714.5 | 60.2 | 18.1 | 104.8 | 9.9 | 257.6 | 8.7 | 895.8 | 745.1 | 860.1 | 825.3 | 819.3 | 765.9 | 827.7 | 757.7 | 719.4 | 837.8 | 276.5 | 365.9 | 407.5 | 307.8 | 419.6 | 424.5 | 412.8 | 395.8 | 601.2 | 388.6
1776 | 1582 | 686.1 | 274.44 | 320.8045 | 430.9 | 454.5 | 383.1 | 369.6 | 735.3 | 60.3 | 18.1 | 104.8 | 8.5 | 267.1 | 10.2 | 896.1 | 744.5 | 863.3 | 825.4 | 818.8 | 765.3 | 826.5 | 756.4 | 719.6 | 837.4 | 276.7 | 365.9 | 407.7 | 308 | 420 | 423.7 | 413.2 | 395.9 | 601.5 | 388.8
1777 | 1583 | 685.6 | 274.24 | 320.5708 | 431.2 | 456.9 | 382.6 | 369.9 | 741.1 | 60.3 | 18.1 | 104.8 | 10.3 | 243.4 | 11.4 | 895.4 | 743.6 | 866.1 | 825.6 | 819.2 | 765.6 | 829.5 | 757.2 | 719.9 | 838.3 | 276.8 | 365.8 | 407.7 | 308.2 | 420.2 | 423.5 | 413.4 | 396.1 | 601.7 | 389.1
1778 | 1584 | 686.6 | 274.64 | 321.0383 | 430.8 | 457.4 | 382 | 370 | 736.2 | 60.2 | 18.1 | 104.6 | 7.9 | 244.1 | 12.4 | 895 | 743.4 | 867.9 | 825.9 | 819.5 | 765.3 | 829.9 | 754.4 | 720.2 | 838.6 | 276.9 | 365.7 | 407.9 | 308.3 | 420.3 | 423.4 | 413.5 | 396.2 | 602.1 | 389.2
1779 | 1585 | 687.2 | 274.88 | 321.3189 | 430.7 | 457.1 | 382.4 | 369.8 | 744.7 | 60.3 | 18.1 | 104.1 | 9.2 | 244 | 16.2 | 895.5 | 743.4 | 868.1 | 826.2 | 819.8 | 765.9 | 829.2 | 753.1 | 720.4 | 838.1 | 277 | 365.6 | 408.2 | 308.5 | 420.2 | 423.3 | 413.5 | 396.2 | 602.2 | 389.4
1780 | 1586 | 687.1 | 274.84 | 321.2721 | 432.1 | 458.1 | 383.5 | 369.8 | 747.4 | 60.3 | 18.1 | 103.8 | 10 | 240.6 | 17.5 | 896.1 | 743.5 | 868.7 | 826.9 | 819.8 | 768.2 | 829.5 | 754.2 | 720.4 | 837.7 | 277.1 | 365.6 | 408.2 | 308.7 | 419.9 | 423.2 | 413.4 | 396.4 | 602 | 389.6
1781 | 1587 | 687.2 | 274.88 | 321.3189 | 434.5 | 459 | 384.1 | 369.4 | 752.6 | 60.4 | 18.1 | 103.7 | 9.9 | 243.4 | 17 | 896.9 | 743.7 | 871.1 | 827 | 820.3 | 768 | 827.4 | 755.5 | 720.5 | 836.8 | 277.2 | 365.6 | 408.5 | 308.9 | 419.9 | 423 | 413.6 | 396.5 | 601.8 | 389.7
1782 | 1588 | 686.7 | 274.68 | 321.0851 | 434.5 | 459.3 | 384.5 | 369.2 | 751.5 | 60.4 | 18.1 | 103.6 | 12.6 | 247.5 | 18.3 | 897.1 | 744 | 874.7 | 827.1 | 820.7 | 769.7 | 824.2 | 755.7 | 720.6 | 837.6 | 277.3 | 365.9 | 408.7 | 309.1 | 419.8 | 422.9 | 413.7 | 396.5 | 601.8 | 389.9
1783 | 1589 | 686.1 | 274.44 | 320.8045 | 435.1 | 457.8 | 385.8 | 369.8 | 756.2 | 60.4 | 18.1 | 103.6 | 13.1 | 247.3 | 19.2 | 898.1 | 744.1 | 868.4 | 827 | 819.9 | 770.5 | 821.8 | 757.7 | 720.5 | 836.5 | 277.4 | 366.3 | 409 | 309.2 | 419.8 | 422.6 | 413.8 | 396.6 | 602 | 390
1784 | 1590 | 686.6 | 274.64 | 321.0383 | 437 | 455.7 | 385.7 | 369.8 | 756.2 | 60.4 | 18.1 | 103.7 | 13.6 | 241.9 | 18.9 | 899.4 | 744.8 | 862.7 | 827.1 | 818.4 | 770.1 | 817.2 | 760.1 | 720.5 | 833.6 | 277.5 | 366.7 | 409.1 | 309.4 | 419.8 | 422.1 | 414 | 396.7 | 601.8 | 390.2
1785 | 1591 | 686.8 | 274.72 | 321.1319 | 439.5 | 454.7 | 386.1 | 369.9 | 748.5 | 60.5 | 18.1 | 103.6 | 11.6 | 245.2 | 22.2 | 900.2 | 744.9 | 857.9 | 826.9 | 814.8 | 767.5 | 805.9 | 760 | 720.5 | 829.2 | 277.7 | 367.1 | 409.4 | 309.6 | 419.9 | 422.1 | 414.1 | 396.7 | 601.2 | 390.4
1786 | 1592 | 686.6 | 274.64 | 321.0383 | 439.5 | 456.1 | 386.6 | 369.9 | 748.9 | 60.5 | 18.1 | 103.4 | 9.8 | 242.2 | 22 | 900.7 | 743.9 | 860.9 | 827 | 813.6 | 766.8 | 803.9 | 756.5 | 720.7 | 828.3 | 277.8 | 367.5 | 409.7 | 309.8 | 419.9 | 421.8 | 414.2 | 396.8 | 600.8 | 390.5
1787 | 1593 | 686.6 | 274.64 | 321.0383 | 440.2 | 459.4 | 387.3 | 369.6 | 759.9 | 60.5 | 18.1 | 103.2 | 10.3 | 241.8 | 22.9 | 900.1 | 742.4 | 861.3 | 826.8 | 814.9 | 767.4 | 804.9 | 754.4 | 720.7 | 828.8 | 277.9 | 367.9 | 409.8 | 310 | 420 | 421.4 | 414.4 | 396.9 | 600.7 | 390.7
1788 | 1594 | 686.9 | 274.76 | 321.1786 | 441.1 | 461.5 | 386.9 | 370 | 762.4 | 60.6 | 18.1 | 103.1 | 11.1 | 243 | 22.9 | 899.6 | 742 | 859.3 | 826.8 | 816.4 | 767.8 | 811.3 | 752.7 | 720.9 | 830 | 278 | 368.2 | 409.7 | 310.1 | 420 | 421.6 | 414.6 | 397.1 | 600.9 | 390.9
1789 | 1595 | 686.8 | 274.72 | 321.1319 | 440.9 | 462.8 | 385.3 | 369.2 | 742.7 | 60.6 | 18.1 | 103 | 12.2 | 241.3 | 22.7 | 899.5 | 742.5 | 866.3 | 826.8 | 817 | 768.1 | 813.6 | 756.6 | 720.8 | 831.8 | 278 | 368.4 | 409.8 | 310.3 | 419.9 | 421.8 | 414.6 | 397.2 | 601.4 | 391
1790 | 1596 | 685.8 | 274.32 | 320.6643 | 440.4 | 464.3 | 385.2 | 369 | 726.9 | 60.5 | 18.1 | 103 | 12.1 | 239.4 | 22.5 | 899.2 | 742.6 | 870.1 | 826.9 | 818.2 | 768.7 | 814.3 | 754.4 | 720.7 | 831.7 | 277.9 | 368.6 | 409.9 | 310.5 | 419.7 | 421.9 | 414.6 | 397.3 | 601.9 | 391.2
1791 | 1597 | 685.2 | 274.08 | 320.3837 | 440.3 | 463 | 385.5 | 368.5 | 723.2 | 60.6 | 18.1 | 103.1 | 10.9 | 249.2 | 18.6 | 899.4 | 742.9 | 866.9 | 827 | 818.4 | 767.5 | 814.9 | 756.5 | 720.6 | 832.7 | 278 | 368.8 | 409.9 | 310.7 | 419.6 | 422.2 | 414.6 | 397.4 | 602.2 | 391.3
1792 | 1598 | 686.4 | 274.56 | 320.9448 | 438.8 | 461.5 | 385.3 | 368.5 | 704.4 | 60.6 | 18.1 | 103.3 | 11 | 241 | 17.4 | 898.4 | 742.7 | 863.9 | 827.1 | 818.4 | 766.9 | 817.4 | 757.5 | 720.4 | 833.4 | 278.1 | 368.9 | 410 | 310.9 | 419.4 | 422.7 | 414.6 | 397.6 | 602.4 | 391.5
1793 | 1599 | 685.2 | 274.08 | 320.3837 | 438.3 | 460.8 | 384.9 | 368.3 | 717 | 60.6 | 18.1 | 103.4 | 10.1 | 239.6 | 20.4 | 898.2 | 742.5 | 859 | 827 | 818.3 | 768.7 | 821.9 | 757.3 | 720.4 | 833.6 | 278.3 | 369 | 410.2 | 311.1 | 419.3 | 422.9 | 414.8 | 397.8 | 602.8 | 391.6
1794 | 1600 | 685.3 | 274.12 | 320.4305 | 437.4 | 458.4 | 384 | 368.9 | 730.2 | 60.6 | 18.1 | 103.5 | 10.4 | 245.9 | 19.9 | 897.9 | 742.8 | 853.9 | 827 | 819.3 | 768.4 | 822.9 | 757.4 | 720.6 | 834.9 | 278.4 | 369.1 | 410.4 | 311.2 | 419.2 | 423.2 | 414.8 | 397.8 | 603 | 391.8
1795 | 1601 | 686 | 274.4 | 320.7578 | 437.9 | 455.7 | 382.6 | 370.3 | 736.7 | 60.6 | 18.1 | 103.5 | 9.9 | 250.9 | 19.7 | 897.2 | 742.9 | 852.4 | 827.2 | 820.2 | 768.7 | 825.4 | 756.6 | 721 | 835.8 | 278.5 | 369.2 | 410.5 | 311.4 | 419.2 | 423.4 | 414.9 | 397.9 | 602.9 | 391.9
1796 | 1602 | 686.8 | 274.72 | 321.1319 | 440.7 | 455.8 | 382.9 | 370.5 | 732.4 | 60.6 | 18.1 | 103.6 | 9 | 245.1 | 17.5 | 896.6 | 743.2 | 849.1 | 827.3 | 820.8 | 770.4 | 825.9 | 755.7 | 721.1 | 836.4 | 278.7 | 369.4 | 410.6 | 311.6 | 419 | 423 | 415.1 | 398 | 602.7 | 392.1
1797 | 1603 | 686 | 274.4 | 320.7578 | 441.8 | 456.1 | 382.8 | 370.4 | 742 | 60.5 | 18.1 | 103.7 | 9.4 | 239.5 | 15 | 896.5 | 743 | 848.1 | 827.3 | 820.8 | 769.7 | 827.6 | 754.6 | 721.2 | 836 | 278.8 | 369.6 | 410.7 | 311.8 | 418.7 | 422.6 | 415.1 | 397.9 | 602.6 | 392.2
1798 | 1604 | 687.1 | 274.84 | 321.2721 | 442.2 | 456.8 | 383.4 | 370.1 | 746.1 | 60.5 | 18.1 | 103.7 | 8.9 | 242 | 16.4 | 896.7 | 743.5 | 852.6 | 827.5 | 822.1 | 769.9 | 825.7 | 754.5 | 721.4 | 836.7 | 278.9 | 369.7 | 411 | 312 | 418.7 | 422.2 | 415.2 | 398 | 602.7 | 392.4
1799 | 1605 | 687.3 | 274.92 | 321.3656 | 441.9 | 456.9 | 383.2 | 370.3 | 745.6 | 60.5 | 18.1 | 103.6 | 9 | 241.3 | 20.6 | 896.8 | 743.6 | 858.6 | 827.4 | 823 | 769.6 | 824.4 | 753.7 | 721.4 | 836.2 | 279 | 369.8 | 411.2 | 312.2 | 418.8 | 421.9 | 415.3 | 398.1 | 603.2 | 392.5
1800 | 1606 | 686.5 | 274.6 | 320.9916 | 442.6 | 459.8 | 383.6 | 369.6 | 757.9 | 60.6 | 18.1 | 103.4 | 8.6 | 240.9 | 21.6 | 898.9 | 744.2 | 856.9 | 827.4 | 823.4 | 771.5 | 818.4 | 756.7 | 721.5 | 835.2 | 279.1 | 369.8 | 411.6 | 312.4 | 418.8 | 421.9 | 415.4 | 398.2 | 603.3 | 392.7
1801 | 1607 | 687.5 | 275 | 321.4592 | 441.9 | 463 | 384.7 | 370 | 758.6 | 60.7 | 18.1 | 103.4 | 6.6 | 233.3 | 19.8 | 899.5 | 744.9 | 854.4 | 827.3 | 822 | 772.8 | 814.9 | 759.2 | 721.7 | 832.3 | 279.2 | 369.9 | 411.7 | 312.5 | 418.9 | 421.6 | 415.6 | 398.3 | 603.2 | 392.8
1802 | 1608 | 684.8 | 273.92 | 320.1967 | 441.3 | 464.4 | 385.6 | 370.5 | 757.2 | 60.7 | 18.1 | 103.4 | 7 | 235.5 | 18.7 | 900.3 | 744.3 | 843 | 827 | 816.6 | 773 | 811.7 | 761.1 | 722 | 830.2 | 279.3 | 370 | 412.1 | 312.8 | 419.2 | 421.5 | 415.7 | 398.3 | 602.9 | 393
1803 | 1609 | 684.5 | 273.8 | 320.0564 | 442 | 464.5 | 386.1 | 370.9 | 760.3 | 60.7 | 18.1 | 103.5 | 8.1 | 236.7 | 17.5 | 901.3 | 743.8 | 828.8 | 826.9 | 810.9 | 773.4 | 804.1 | 763.6 | 722.3 | 825.8 | 279.4 | 370.1 | 412.2 | 313 | 419.4 | 421.6 | 415.9 | 398.4 | 602.5 | 393.1
1804 | 1610 | 685.4 | 274.16 | 320.4772 | 443.1 | 468.8 | 386 | 370.7 | 764.4 | 60.8 | 18.1 | 103.5 | 9.6 | 235.5 | 19.4 | 901.7 | 743.1 | 812.9 | 826.9 | 806.2 | 774 | 801.8 | 764 | 722.8 | 823.1 | 279.6 | 370.2 | 412.5 | 313.2 | 419.6 | 421.5 | 416 | 398.4 | 602.1 | 393.3
1805 | 1611 | 686.7 | 274.68 | 321.0851 | 443 | 474 | 385.8 | 370 | 769.1 | 60.8 | 18.1 | 103.6 | 8.3 | 244.8 | 17.2 | 902.1 | 743.2 | 813 | 826.9 | 805.7 | 773.9 | 795.8 | 763.6 | 722.9 | 820.3 | 279.7 | 370.1 | 412.9 | 313.4 | 420 | 421.2 | 416.3 | 398.5 | 601.8 | 393.5
1806 | 1612 | 685.8 | 274.32 | 320.6643 | 442.5 | 475.2 | 386.7 | 370.4 | 757.1 | 60.8 | 18.1 | 103.7 | 8.1 | 244.9 | 17.5 | 902.6 | 743.2 | 806.4 | 826.8 | 803.4 | 774.2 | 795 | 762.5 | 723 | 819.3 | 279.9 | 370.1 | 412.9 | 313.6 | 420.2 | 420.7 | 416.5 | 398.5 | 601.4 | 393.7
1807 | 1613 | 686.9 | 274.76 | 321.1786 | 443.8 | 474 | 387.4 | 370.8 | 756.9 | 60.8 | 18.1 | 103.8 | 8.4 | 251.6 | 19.5 | 903.1 | 742.8 | 781.9 | 826.6 | 799.8 | 773.5 | 789.9 | 761.9 | 723.1 | 814.6 | 280 | 370 | 413.5 | 313.8 | 420.4 | 420.1 | 416.7 | 398.6 | 601 | 393.8
1808 | 1614 | 686.6 | 274.64 | 321.0383 | 446.1 | 471.3 | 388 | 371.3 | 753.8 | 60.9 | 18.1 | 103.6 | 9.1 | 247.1 | 18.8 | 904.1 | 742.3 | 781.9 | 826.1 | 796.9 | 770.3 | 785.8 | 761.4 | 723.3 | 812.7 | 280.1 | 370 | 413.6 | 313.9 | 420.3 | 419.7 | 416.7 | 398.6 | 600.5 | 394
1809 | 1615 | 685.7 | 274.28 | 320.6175 | 447.1 | 473.5 | 389.2 | 371.9 | 753 | 60.9 | 18.1 | 103.4 | 10.4 | 266.9 | 15.5 | 906.5 | 741.9 | 782.9 | 825.7 | 791.2 | 767 | 776.5 | 765.3 | 723.3 | 806 | 280.2 | 370.2 | 414.2 | 314.1 | 420.4 | 419.2 | 416.8 | 398.6 | 600 | 394.2
1810 | 1616 | 685 | 274 | 320.2902 | 448 | 475.8 | 390.9 | 372.6 | 752.4 | 60.8 | 18.1 | 103.2 | 9.1 | 257.6 | 15.6 | 909.3 | 741 | 768.5 | 825.6 | 787.4 | 766.7 | 766.3 | 765.1 | 723.2 | 800.5 | 280.3 | 370.3 | 414.4 | 314.3 | 420.6 | 418.6 | 417.2 | 398.5 | 599.6 | 394.3
1811 | 1617 | 685.8 | 274.32 | 320.6643 | 449.5 | 479.2 | 392.6 | 373.3 | 740.2 | 60.8 | 18.1 | 103.2 | 8.8 | 236.6 | 16.8 | 911.9 | 739.8 | 770.6 | 825.6 | 783.2 | 767 | 759.5 | 766 | 723.1 | 796.7 | 280.4 | 370.5 | 414.2 | 314.4 | 420.7 | 418.4 | 417.4 | 398.5 | 599.1 | 394.5
1812 | 1618 | 685.8 | 274.32 | 320.6643 | 450.7 | 480 | 391.8 | 373.4 | 733.5 | 60.8 | 18.1 | 103.1 | 7.4 | 258 | 14.5 | 910.9 | 739.4 | 767.9 | 825.3 | 782.7 | 766.4 | 768.9 | 760.4 | 721.1 | 797.9 | 280.5 | 370.8 | 414.1 | 314.6 | 421 | 418.5 | 417.4 | 398.7 | 598.5 | 394.6
1813 | 1619 | 685.3 | 274.12 | 320.4305 | 452.3 | 483.8 | 391.3 | 373.3 | 746 | 60.8 | 18.1 | 103 | 8.1 | 243.7 | 12.9 | 910.4 | 738.2 | 783.5 | 825.2 | 780.3 | 767 | 776.4 | 755.3 | 720.3 | 799.9 | 280.6 | 371 | 414.4 | 314.8 | 421.3 | 418.9 | 417.7 | 398.8 | 598.1 | 394.8
1814 | 1620 | 684.3 | 273.72 | 319.9629 | 453.2 | 486.7 | 390.6 | 373.7 | 753.4 | 60.8 | 18.1 | 103.1 | 10.9 | 252.3 | 14.1 | 909.3 | 738.2 | 790.7 | 825.1 | 781.5 | 766.4 | 785.7 | 755 | 720 | 801 | 280.6 | 371.1 | 414.4 | 315 | 421.7 | 419.6 | 417.9 | 398.9 | 597.9 | 395
1815 | 1621 | 684.2 | 273.68 | 319.9162 | 454.2 | 487.9 | 390.2 | 374 | 728.6 | 60.8 | 18.1 | 103.2 | 11.9 | 257 | 19.3 | 908.8 | 737.8 | 803.9 | 825.3 | 784.1 | 766.3 | 792.4 | 754.3 | 719.7 | 804.5 | 280.7 | 371.1 | 414.5 | 315.2 | 422.1 | 420.3 | 418.1 | 399.1 | 597.8 | 395.1
1816 | 1622 | 685.4 | 274.16 | 320.4772 | 458.7 | 484.7 | 390.1 | 374 | 729.9 | 60.7 | 18.1 | 103.3 | 11.8 | 265 | 22.8 | 907.8 | 737.2 | 816.4 | 825.5 | 786.2 | 768 | 799.1 | 754.5 | 719.9 | 806.6 | 280.8 | 371.2 | 414.6 | 315.4 | 422.4 | 420.8 | 418.3 | 399.3 | 598 | 395.3
1817 | 1623 | 685.7 | 274.28 | 320.6175 | 461 | 480.6 | 390.9 | 373.3 | 737.7 | 60.6 | 18.1 | 103.4 | 11.3 | 261.2 | 22.8 | 906.6 | 737.4 | 824.5 | 825.6 | 789.4 | 768.5 | 805.7 | 754.5 | 720.1 | 809.6 | 280.9 | 371.4 | 414.6 | 315.5 | 422.5 | 421.1 | 418.2 | 399.4 | 597.9 | 395.5
1818 | 1624 | 684.4 | 273.76 | 320.0097 | 459.5 | 479.8 | 391.3 | 371.2 | 741.2 | 60.6 | 18.1 | 103.4 | 10.1 | 255.4 | 18.3 | 905.8 | 737.1 | 836 | 825.7 | 790.4 | 768.2 | 805 | 753 | 720.2 | 810 | 281 | 371.6 | 414.9 | 315.7 | 422.6 | 421.2 | 418.1 | 399.5 | 597.9 | 395.6
1819 | 1625 | 684.6 | 273.84 | 320.1032 | 456.8 | 478.9 | 391.4 | 369.8 | 755.2 | 60.6 | 18.1 | 103.4 | 11.1 | 263.3 | 17.1 | 906.1 | 737.2 | 845.7 | 825.5 | 792.3 | 768.4 | 798.2 | 754.7 | 720.5 | 807.9 | 281.2 | 371.7 | 415.7 | 315.9 | 422.9 | 421.4 | 418.3 | 399.6 | 598.1 | 395.8
1820 | 1626 | 684.2 | 273.68 | 319.9162 | 455.1 | 477.3 | 391.1 | 369 | 759.5 | 60.5 | 18.1 | 103.3 | 12.6 | 258.5 | 18 | 906.5 | 737.8 | 825.9 | 825.2 | 788.4 | 770 | 791.8 | 758.3 | 720.7 | 804.9 | 281.3 | 371.9 | 416 | 316.1 | 423.1 | 421.2 | 418.4 | 399.6 | 598.1 | 396
1821 | 1627 | 684.9 | 273.96 | 320.2435 | 455.2 | 474.4 | 391.7 | 369.6 | 743.2 | 60.5 | 18.1 | 103.2 | 11.9 | 258.2 | 22.9 | 909.6 | 738.6 | 790.4 | 824.9 | 781.3 | 762.8 | 780.1 | 763.2 | 720.3 | 797.2 | 281.4 | 372 | 416 | 316.3 | 423.5 | 420.9 | 418.6 | 399.6 | 597.8 | 396.1
1822 | 1628 | 685.8 | 274.32 | 320.6643 | 456.9 | 474.4 | 391.9 | 370.1 | 732 | 60.5 | 18.1 | 103.4 | 8.3 | 255.2 | 22.8 | 912.4 | 738.5 | 801.6 | 824.8 | 780.5 | 761.2 | 771.5 | 763.1 | 719.9 | 792.7 | 281.5 | 372.2 | 416.3 | 316.5 | 423.7 | 420.7 | 418.7 | 399.7 | 597.2 | 396.3
1823 | 1629 | 685.4 | 274.16 | 320.4772 | 456.6 | 476 | 391.4 | 370.7 | 740.6 | 60.5 | 18.1 | 103.6 | 8.1 | 248.7 | 21.9 | 913.5 | 738.2 | 807 | 824.6 | 779.6 | 764 | 774.8 | 758.5 | 719.5 | 792.6 | 281.7 | 372.4 | 416.3 | 316.7 | 423.6 | 420.6 | 418.8 | 399.8 | 596.7 | 396.5
1824 | 1630 | 684.6 | 273.84 | 320.1032 | 453.7 | 479.2 | 390.9 | 370.6 | 734.9 | 60.5 | 18.1 | 103.7 | 8 | 258.9 | 19.4 | 915.5 | 737 | 797 | 824.3 | 775.5 | 763.4 | 771.5 | 755.8 | 718.9 | 787.6 | 281.8 | 372.6 | 416 | 316.8 | 423.7 | 420.4 | 418.9 | 399.8 | 596.2 | 396.6
1825 | 1631 | 684.8 | 273.92 | 320.1967 | 453.2 | 482.9 | 390.1 | 370.7 | 718.2 | 60.6 | 18.1 | 103.8 | 9.4 | 261.4 | 18.3 | 916.3 | 736.1 | 765.1 | 824 | 769.8 | 756.1 | 761.9 | 750.1 | 718.2 | 782.3 | 281.9 | 372.8 | 416 | 317 | 423.9 | 420.3 | 419 | 399.9 | 595.5 | 396.8
1826 | 1632 | 684.9 | 273.96 | 320.2435 | 454.8 | 482.4 | 388.9 | 371.4 | 693 | 60.7 | 18.1 | 103.8 | 10.1 | 268.3 | 20.8 | 915.7 | 736.7 | 765.1 | 823.6 | 767.7 | 754.9 | 761.6 | 746.1 | 717.2 | 778.8 | 282 | 372.8 | 415.9 | 317.2 | 423.9 | 419.6 | 419 | 399.9 | 594.8 | 396.9
1827 | 1633 | 685 | 274 | 320.2902 | 453.7 | 480.8 | 387.7 | 371.7 | 697 | 60.8 | 18.1 | 103.9 | 9.4 | 266.6 | 20 | 915.8 | 737.9 | 785.2 | 823.4 | 769.3 | 759.5 | 771.7 | 746 | 716.6 | 781.3 | 282.2 | 372.9 | 416.3 | 317.3 | 423.9 | 419.2 | 418.9 | 399.9 | 594.2 | 397.1
1828 | 1634 | 684.6 | 273.84 | 320.1032 | 453 | 478.9 | 388.2 | 371.1 | 700.6 | 60.9 | 18.1 | 103.9 | 9.1 | 271.7 | 19.7 | 916.8 | 738.5 | 777 | 823.6 | 767.7 | 760.8 | 773.8 | 742.8 | 716.6 | 781.7 | 282.3 | 373 | 416.6 | 317.5 | 424.1 | 419.3 | 419 | 400 | 594 | 397.2
1829 | 1635 | 684.9 | 273.96 | 320.2435 | 453.8 | 479.1 | 388.2 | 370.7 | 705 | 60.9 | 18.1 | 104 | 9.5 | 265.3 | 18 | 918.9 | 739.2 | 755.4 | 823.5 | 762.1 | 756.8 | 763 | 734.5 | 716.4 | 775.4 | 282.5 | 373.2 | 417.3 | 317.7 | 424.3 | 419.1 | 419.1 | 400 | 593.8 | 397.4
1830 | 1636 | 684.9 | 273.96 | 320.2435 | 455.7 | 480.2 | 389.5 | 370.7 | 699.3 | 60.9 | 18.1 | 104 | 9.8 | 267.2 | 17.6 | 920.7 | 739.4 | 746.9 | 823.4 | 758.9 | 753.7 | 750.6 | 727.7 | 716 | 771.7 | 282.7 | 373.5 | 417.6 | 317.9 | 424.5 | 418.6 | 419.1 | 400 | 593.4 | 397.5
1831 | 1637 | 684.4 | 273.76 | 320.0097 | 459.4 | 479.2 | 391.8 | 371.2 | 704.5 | 60.8 | 18.1 | 103.9 | 11.2 | 262.4 | 16 | 920.5 | 739.7 | 734.3 | 823.2 | 756.9 | 755.4 | 744.8 | 725.2 | 715.4 | 769.9 | 282.9 | 373.7 | 417.9 | 318.1 | 424.8 | 418.2 | 419.1 | 400 | 592.9 | 397.7
1832 | 1638 | 685.3 | 274.12 | 320.4305 | 461.7 | 480.3 | 392.5 | 372.2 | 715.7 | 60.8 | 18.1 | 103.9 | 10.6 | 262.3 | 15.8 | 921.7 | 738.7 | 731 | 823.1 | 755.8 | 757.6 | 741.3 | 723.2 | 715 | 768.1 | 283 | 374 | 418 | 318.3 | 425.1 | 418 | 419.3 | 400.1 | 592.4 | 397.9
1833 | 1639 | 684.7 | 273.88 | 320.1499 | 464.3 | 479.9 | 393.1 | 373.2 | 721.5 | 60.7 | 18.1 | 104 | 11 | 251 | 15.6 | 923.9 | 739 | 738.5 | 822.8 | 753.2 | 756.7 | 740 | 718 | 714.7 | 765.3 | 283.1 | 374.2 | 418.3 | 318.5 | 425.5 | 418 | 419.5 | 400.1 | 592 | 398
1834 | 1640 | 685.1 | 274.04 | 320.337 | 465.6 | 478.4 | 393.6 | 374.1 | 724 | 60.6 | 18.1 | 103.9 | 10.4 | 264.6 | 13.2 | 923.7 | 738 | 739.8 | 822.6 | 750 | 757.7 | 741.4 | 718.8 | 714.3 | 765.3 | 283.3 | 374.5 | 418.4 | 318.7 | 425.8 | 418 | 419.7 | 400.2 | 591.5 | 398.2
1835 | 1641 | 683.6 | 273.44 | 319.6356 | 466.8 | 480.5 | 394.2 | 374.9 | 723.8 | 60.6 | 18.1 | 103.9 | 9.4 | 250.3 | 12.9 | 925.5 | 737.3 | 761.7 | 822.4 | 748.9 | 759.1 | 733.5 | 715.3 | 714 | 762 | 283.4 | 374.8 | 419.2 | 318.9 | 426.1 | 418 | 419.9 | 400.2 | 591 | 398.3
1836 | 1642 | 684.8 | 273.92 | 320.1967 | 468 | 480.4 | 395.3 | 374.7 | 719.8 | 60.5 | 18.1 | 104 | 8.4 | 255.2 | 14.9 | 926 | 737.3 | 756.2 | 822.3 | 747.2 | 757.3 | 727.3 | 717.8 | 713.8 | 760.6 | 283.6 | 375.1 | 419.4 | 319.1 | 426.2 | 418.1 | 420.1 | 400.3 | 590.6 | 398.5
1837 | 1643 | 684.6 | 273.84 | 320.1032 | 469.7 | 479.5 | 395.9 | 374.9 | 722.5 | 60.5 | 18.1 | 103.9 | 8.3 | 257.4 | 14.7 | 925.2 | 736.9 | 760.8 | 822.2 | 744.4 | 758.3 | 726.3 | 717.3 | 713.6 | 759.5 | 283.8 | 375.2 | 419.5 | 319.3 | 426.4 | 417.7 | 420.2 | 400.2 | 590.2 | 398.7
1838 | 1644 | 686.5 | 274.6 | 320.9916 | 469.3 | 479.7 | 396 | 375.6 | 744.6 | 60.6 | 18.1 | 103.9 | 9 | 256.3 | 13.9 | 924.2 | 738.2 | 761.1 | 821.8 | 743.2 | 760.1 | 726.3 | 720.4 | 713.6 | 760 | 283.9 | 375.4 | 420 | 319.5 | 426.6 | 417.6 | 420.4 | 400.2 | 589.9 | 398.8
1839 | 1645 | 685.2 | 274.08 | 320.3837 | 469.4 | 480.7 | 396.8 | 376 | 750.8 | 60.7 | 18.1 | 104 | 9.3 | 259.4 | 15.2 | 925.6 | 739.9 | 765.9 | 821.8 | 740.8 | 760.2 | 723.9 | 717.6 | 713.2 | 757.5 | 284.1 | 375.6 | 420.2 | 319.7 | 427 | 417.7 | 420.5 | 400.3 | 589.8 | 399
1840 | 1646 | 685.1 | 274.04 | 320.337 | 469.2 | 481.8 | 397.1 | 375.8 | 740.4 | 60.7 | 18.1 | 104 | 9.4 | 260.2 | 15.2 | 924 | 738.8 | 768.1 | 821.7 | 742.8 | 761.9 | 731.3 | 722.2 | 712.9 | 759.8 | 284.3 | 375.9 | 419.9 | 319.9 | 427.2 | 418 | 420.6 | 400.5 | 589.3 | 399.1
1841 | 1647 | 684.6 | 273.84 | 320.1032 | 468.3 | 479.8 | 396.4 | 375.9 | 744.9 | 60.7 | 18.1 | 104 | 9.3 | 257.7 | 15.4 | 923.4 | 738.2 | 771.3 | 821.2 | 742.2 | 763.2 | 742.5 | 728.3 | 712.7 | 760.6 | 284.5 | 376 | 420 | 320.1 | 427.4 | 418.4 | 420.8 | 400.6 | 588.9 | 399.3
1842 | 1648 | 685.1 | 274.04 | 320.337 | 467.2 | 481.4 | 395.7 | 376.2 | 752.7 | 60.7 | 18.1 | 103.8 | 8.4 | 253.1 | 17.3 | 924.3 | 739 | 780.4 | 820.9 | 741 | 764.4 | 750.4 | 730.2 | 712.8 | 760.2 | 284.7 | 376.3 | 420.4 | 320.3 | 427.6 | 418.8 | 421 | 400.6 | 588.6 | 399.5
1843 | 1649 | 684 | 273.6 | 319.8226 | 466.8 | 482.7 | 395.6 | 377 | 766.8 | 60.7 | 18.1 | 103.7 | 8.8 | 258.4 | 19.7 | 925 | 740.9 | 792.8 | 820.5 | 738.6 | 764.8 | 752.5 | 728.8 | 712.8 | 758.9 | 284.8 | 376.6 | 421.2 | 320.4 | 427.9 | 419.2 | 421.3 | 400.7 | 588.4 | 399.6
1844 | 1650 | 686.4 | 274.56 | 320.9448 | 465.5 | 481.9 | 395.9 | 377.6 | 767.2 | 60.8 | 18.1 | 103.5 | 7.7 | 253.9 | 20.3 | 923.2 | 740.6 | 797.8 | 820.2 | 738.7 | 765.5 | 756.5 | 730.2 | 712.9 | 760.2 | 284.9 | 376.8 | 421.3 | 320.6 | 428.1 | 419.4 | 421.5 | 400.8 | 588.3 | 399.8
1845 | 1651 | 691.3 | 276.52 | 323.2359 | 464.8 | 485.6 | 396.5 | 377.1 | 774.2 | 60.8 | 18.1 | 103.3 | 6.7 | 241.9 | 19.6 | 921.5 | 741 | 792.5 | 820 | 738.6 | 763.8 | 769.9 | 734.5 | 713 | 764.2 | 285.1 | 377 | 421.1 | 320.8 | 428.3 | 420 | 421.6 | 400.9 | 588.1 | 400
1846 | 1652 | 688.2 | 275.28 | 321.7865 | 464.6 | 484.4 | 396 | 376.7 | 767.1 | 61 | 18.1 | 103.2 | 7.2 | 247.3 | 16.5 | 920.2 | 743.3 | 780.1 | 819.6 | 737 | 765.1 | 777 | 739.9 | 712.8 | 764.3 | 285.2 | 377.3 | 421.1 | 321 | 428.6 | 419.8 | 421.8 | 400.9 | 588.1 | 400.2
1847 | 1653 | 684.4 | 273.76 | 320.0097 | 465.5 | 484 | 394.9 | 376 | 758.3 | 61 | 18.1 | 103 | 8.2 | 257.9 | 15.6 | 921.9 | 745.1 | 769 | 819.4 | 734.5 | 763.6 | 784.3 | 741.3 | 712.6 | 764 | 285.4 | 377.5 | 421.3 | 321.2 | 428.7 | 419.7 | 421.8 | 401 | 587.8 | 400.3
1848 | 1654 | 685.6 | 274.24 | 320.5708 | 464.2 | 480.4 | 394.3 | 376.1 | 746.1 | 61 | 18.1 | 102.9 | 8.1 | 265.6 | 13.1 | 919.4 | 745.8 | 768.8 | 819.1 | 734.5 | 764.4 | 790.3 | 743.2 | 712.4 | 765.2 | 285.6 | 377.7 | 421.4 | 321.4 | 428.7 | 419.8 | 421.9 | 401.2 | 587.3 | 400.5
1849 | 1655 | 685.9 | 274.36 | 320.711 | 464.1 | 476.9 | 394 | 376.2 | 749.9 | 61 | 18.1 | 103 | 6.7 | 254.7 | 12.6 | 917.3 | 746.9 | 779.6 | 818.7 | 735.4 | 764.1 | 798.2 | 747.3 | 712.3 | 767.9 | 285.8 | 378 | 421.4 | 321.6 | 428.7 | 420 | 421.9 | 401.4 | 586.9 | 400.6
1850 | 1656 | 685.6 | 274.24 | 320.5708 | 465.3 | 475 | 393.7 | 376.1 | 753.3 | 60.9 | 18.1 | 102.9 | 6.2 | 251.9 | 16.3 | 917.1 | 746.3 | 783.2 | 818.4 | 735.6 | 763.9 | 800.9 | 747 | 712.3 | 767.6 | 286 | 378.3 | 421.5 | 321.8 | 428.8 | 420.3 | 422 | 401.4 | 586.6 | 400.8
1851 | 1657 | 685.1 | 274.04 | 320.337 | 467.4 | 478.3 | 393.3 | 376 | 756.3 | 60.9 | 18.1 | 102.7 | 6.7 | 237.5 | 13.2 | 917.2 | 745.8 | 781.7 | 818.2 | 735.8 | 766.3 | 801.6 | 747.2 | 712.2 | 767.5 | 286.2 | 378.6 | 421.8 | 322 | 428.9 | 420.1 | 422.1 | 401.4 | 586.3 | 401
1852 | 1658 | 686.9 | 274.76 | 321.1786 | 467.3 | 479.7 | 392.9 | 376.6 | 755.9 | 60.9 | 18.1 | 102.6 | 7 | 249.3 | 12.9 | 918 | 746.3 | 801.2 | 818 | 735.2 | 766.8 | 800.1 | 747.5 | 712.4 | 768.2 | 286.4 | 378.9 | 422.2 | 322.2 | 429 | 419.8 | 422.2 | 401.4 | 585.9 | 401.1
1853 | 1659 | 685.6 | 274.24 | 320.5708 | 465.7 | 476.5 | 392.4 | 377.1 | 758.2 | 60.9 | 18.1 | 102.5 | 6.8 | 267.2 | 12.4 | 919 | 747.3 | 802.9 | 817.9 | 736.2 | 767.5 | 800.8 | 748.4 | 712.3 | 769.7 | 286.6 | 379.1 | 422.1 | 322.3 | 429.1 | 419.7 | 422.2 | 401.5 | 585.6 | 401.3
1854 | 1660 | 686.2 | 274.48 | 320.8513 | 466.2 | 473.7 | 392.3 | 376.8 | 757.5 | 60.9 | 18.1 | 102.5 | 6.5 | 267.5 | 10 | 917 | 747.4 | 798 | 817.9 | 738 | 767 | 801.5 | 750.2 | 712.3 | 773 | 286.8 | 379.4 | 422.3 | 322.5 | 429.3 | 419.9 | 422.3 | 401.6 | 585.3 | 401.4
1855 | 1661 | 686.6 | 274.64 | 321.0383 | 465.6 | 471 | 391.9 | 376.3 | 749.3 | 60.9 | 18.1 | 102.8 | 6.2 | 259.3 | 10.8 | 914.8 | 747.9 | 790 | 817.5 | 739.9 | 766.4 | 807.2 | 751.7 | 712.2 | 775.7 | 287 | 379.7 | 422.1 | 322.7 | 429.3 | 420.1 | 422.3 | 401.8 | 585.1 | 401.6
1856 | 1662 | 686.5 | 274.6 | 320.9916 | 465.4 | 468 | 391.7 | 376.3 | 750.2 | 60.8 | 18.1 | 103 | 6.3 | 264.6 | 13.6 | 914.6 | 749.7 | 793.2 | 817.2 | 740.5 | 766 | 810.5 | 752.8 | 712.3 | 777.3 | 287.2 | 379.9 | 422.3 | 322.9 | 429.3 | 420.3 | 422.1 | 401.9 | 585 | 401.7
1857 | 1663 | 686.2 | 274.48 | 320.8513 | 463.3 | 466.9 | 392.4 | 376.3 | 754.9 | 60.8 | 18.1 | 103.1 | 6.5 | 255.6 | 15.4 | 913.9 | 751.3 | 791.7 | 816.8 | 741.3 | 766.5 | 810.6 | 755.2 | 712.3 | 777 | 287.4 | 380.2 | 422.7 | 323.1 | 429.3 | 420.3 | 422.1 | 401.9 | 585 | 401.9
1858 | 1664 | 688.5 | 275.4 | 321.9267 | 462.6 | 465.1 | 393.7 | 376.3 | 743.6 | 60.8 | 18.1 | 103.2 | 6.5 | 263.4 | 16 | 914 | 752 | 793 | 816.6 | 742.5 | 766.1 | 804.9 | 756.3 | 712.1 | 778.2 | 287.5 | 380.3 | 422.9 | 323.3 | 429.4 | 420.4 | 422.1 | 402 | 584.9 | 402
1859 | 1665 | 690.5 | 276.2 | 322.8619 | 463.9 | 466.2 | 393.7 | 376.5 | 738.5 | 60.9 | 18.1 | 103.3 | 7.1 | 254 | 15.6 | 913.6 | 752.8 | 791.3 | 816.5 | 743.2 | 765 | 804.5 | 755.8 | 711.7 | 779.3 | 287.7 | 380.5 | 422.7 | 323.5 | 429.2 | 420.4 | 422 | 402.1 | 584.5 | 402.2
1860 | 1666 | 687 | 274.8 | 321.2254 | 465.2 | 466 | 392.2 | 376 | 734.4 | 60.9 | 18.1 | 103.5 | 7.7 | 255.3 | 15.1 | 913.3 | 752.5 | 795.3 | 816.2 | 743.5 | 764.8 | 802.3 | 755.7 | 711.5 | 778.8 | 287.9 | 380.7 | 422.9 | 323.7 | 429 | 420.1 | 421.8 | 402.2 | 584.2 | 402.3
1861 | 1667 | 686.5 | 274.6 | 320.9916 | 466.1 | 464 | 389.8 | 374.4 | 726.3 | 60.9 | 18.1 | 103.6 | 7.7 | 255.3 | 15.1 | 912.5 | 752.5 | 789.7 | 815.9 | 744.6 | 766.5 | 801.7 | 755.4 | 711.6 | 781.9 | 288.2 | 381 | 423 | 323.9 | 428.8 | 420.1 | 421.7 | 402.1 | 583.8 | 402.4
1862 | 1668 | 686.4 | 274.56 | 320.9448 | 466.2 | 465.8 | 390.4 | 373.3 | 722.5 | 60.8 | 18.1 | 103.8 | 6.9 | 250 | 15.4 | 913.2 | 752.5 | 797.7 | 815.8 | 746.7 | 766.2 | 799.6 | 756.1 | 711.4 | 781.7 | 288.4 | 381.2 | 423.1 | 324.1 | 428.7 | 420.1 | 421.7 | 402.2 | 583.7 | 402.5
1863 | 1669 | 687.2 | 274.88 | 321.3189 | 464.8 | 468 | 390.5 | 373.6 | 718.8 | 60.8 | 18.1 | 103.8 | 6.7 | 244.9 | 15.2 | 915.4 | 752.6 | 802.2 | 816 | 748.1 | 766.7 | 801.5 | 755.8 | 711.3 | 782.2 | 288.6 | 381.4 | 423.1 | 324.3 | 428.7 | 419.9 | 421.6 | 402.3 | 583.7 | 402.7
1864 | 1670 | 686.9 | 274.76 | 321.1786 | 461.9 | 469.5 | 391.5 | 373.5 | 715.8 | 60.9 | 18.1 | 104 | 7.2 | 248.2 | 15.1 | 914.9 | 753.9 | 804.5 | 815.9 | 748 | 766.5 | 799.7 | 756.9 | 711.2 | 781.1 | 288.8 | 381.6 | 423.1 | 324.5 | 428.6 | 419.7 | 421.4 | 402.3 | 583.4 | 402.8
1865 | 1671 | 686.8 | 274.72 | 321.1319 | 461.9 | 467.5 | 391.1 | 372.2 | 714 | 60.9 | 18.1 | 104.2 | 7.2 | 245.3 | 13 | 913.9 | 755.1 | 805.9 | 815.9 | 748.9 | 767.3 | 801.6 | 758.6 | 711.1 | 783.1 | 288.9 | 381.9 | 423.1 | 324.8 | 428.4 | 419.3 | 421.2 | 402.4 | 583.1 | 402.9
1866 | 1672 | 686.7 | 274.68 | 321.0851 | 461.1 | 467.1 | 390.9 | 371.6 | 724.3 | 60.9 | 18 | 104.6 | 7.5 | 255.3 | 14.2 | 913.2 | 757.6 | 810.3 | 815.7 | 750.3 | 770.1 | 804.5 | 761 | 711 | 784.4 | 289.1 | 382.1 | 423.4 | 325 | 428.3 | 418.8 | 421.1 | 402.3 | 582.8 | 403
1867 | 1673 | 686.8 | 274.72 | 321.1319 | 460.4 | 467.4 | 390.5 | 371.2 | 735.2 | 61 | 18.1 | 104.9 | 6.9 | 252.3 | 15.7 | 914.4 | 758.3 | 832.4 | 815.5 | 752.6 | 768.7 | 801.2 | 758.8 | 711 | 785.2 | 289.4 | 382.3 | 423.8 | 325.2 | 428.3 | 418.5 | 421.1 | 402.3 | 582.6 | 403.1
1868 | 1674 | 686.8 | 274.72 | 321.1319 | 458.5 | 466.1 | 389 | 370.7 | 736.1 | 61 | 18.1 | 105.1 | 4.6 | 241.7 | 17.6 | 914.2 | 757.6 | 838.9 | 815.6 | 753.7 | 768 | 804.3 | 757.6 | 711 | 786 | 289.6 | 382.5 | 423.8 | 325.4 | 428.3 | 418.5 | 421 | 402.3 | 582.6 | 403.3
1869 | 1675 | 686.5 | 274.6 | 320.9916 | 458.1 | 463.9 | 389.3 | 370.9 | 742.1 | 61 | 18 | 105.2 | 5.2 | 242.4 | 17.6 | 914.7 | 760.2 | 836.3 | 815.7 | 753.1 | 768.8 | 802.5 | 757.1 | 711 | 782.7 | 289.8 | 382.8 | 424.2 | 325.6 | 428.3 | 418.2 | 420.9 | 402.3 | 582.5 | 403.4
1870 | 1676 | 686.8 | 274.72 | 321.1319 | 459.7 | 460.7 | 390.9 | 371.3 | 748.3 | 61 | 18 | 105.4 | 6 | 252.8 | 16.8 | 918 | 760.8 | 826.8 | 815.9 | 753.4 | 770 | 798.4 | 755.6 | 711.4 | 783.2 | 290 | 383 | 424.6 | 325.8 | 428.4 | 418.3 | 421.1 | 402.4 | 582.2 | 403.5
1871 | 1677 | 686.1 | 274.44 | 320.8045 | 461.5 | 460.6 | 391.3 | 371.7 | 753 | 60.9 | 18.1 | 105.6 | 6.7 | 252.8 | 14.9 | 919.7 | 758.8 | 820.6 | 816 | 752.7 | 771.3 | 791.8 | 752.6 | 711.6 | 780.9 | 290.2 | 383.3 | 425 | 326 | 428.5 | 418.4 | 421.2 | 402.5 | 582.1 | 403.7
1872 | 1678 | 686.3 | 274.52 | 320.8981 | 462.8 | 464.1 | 391.6 | 371.3 | 761.5 | 60.9 | 18 | 105.6 | 6 | 251.8 | 15.4 | 921.4 | 757.8 | 802.4 | 816 | 748.9 | 770.2 | 785 | 747.3 | 711.9 | 777.9 | 290.5 | 383.5 | 425.2 | 326.2 | 428.5 | 418.4 | 421.3 | 402.5 | 581.9 | 403.8
1873 | 1679 | 686.2 | 274.48 | 320.8513 | 463.9 | 464.7 | 392.3 | 371.8 | 763.2 | 60.9 | 18 | 105.7 | 8 | 259 | 16.5 | 922.3 | 756.9 | 792.6 | 816 | 748.2 | 769 | 778.2 | 744.5 | 711.9 | 775.6 | 290.7 | 383.8 | 425.4 | 326.4 | 428.7 | 418.6 | 421.4 | 402.5 | 581.6 | 403.9
1874 | 1680 | 686.4 | 274.56 | 320.9448 | 464.2 | 463.5 | 392.5 | 372.1 | 762.5 | 60.9 | 18 | 105.8 | 9 | 268.9 | 14.6 | 920.7 | 755.5 | 804.5 | 815.9 | 752 | 769.9 | 775.7 | 745.2 | 712.1 | 775.9 | 290.8 | 384.1 | 425.9 | 326.6 | 428.9 | 418.7 | 421.6 | 402.6 | 581.3 | 404.1
1875 | 1681 | 686.5 | 274.6 | 320.9916 | 464.2 | 465.2 | 393.1 | 373.2 | 761.8 | 60.9 | 18 | 105.8 | 10.1 | 257.6 | 13.8 | 922.1 | 754.7 | 787.9 | 816 | 749 | 767.3 | 769.9 | 739 | 712 | 773.5 | 291 | 384.3 | 426 | 326.9 | 429.3 | 418.8 | 421.7 | 402.6 | 581.1 | 404.2
1876 | 1682 | 686.2 | 274.48 | 320.8513 | 465.1 | 466.6 | 393.8 | 373.7 | 756.1 | 61 | 18 | 105.6 | 8.9 | 255.6 | 14.7 | 923.8 | 752.8 | 763.6 | 815.9 | 743.7 | 765.2 | 758.2 | 730.8 | 711.7 | 768.1 | 291.3 | 384.6 | 426.3 | 327.1 | 429.7 | 418.8 | 421.8 | 402.7 | 580.8 | 404.4
1877 | 1683 | 686.5 | 274.6 | 320.9916 | 466.6 | 469.5 | 394.7 | 374.2 | 756.1 | 61.1 | 18 | 105.5 | 7.4 | 233.7 | 16.2 | 923.3 | 754.1 | 786.5 | 815.9 | 744.6 | 769.8 | 758.2 | 735.5 | 712 | 770.3 | 291.5 | 384.9 | 426.5 | 327.3 | 430 | 418.9 | 421.8 | 402.7 | 580.4 | 404.5
1878 | 1684 | 686.4 | 274.56 | 320.9448 | 467.7 | 471.2 | 395 | 374.7 | 758.2 | 61.1 | 18 | 105.4 | 6.7 | 237.4 | 13.8 | 920.5 | 753.8 | 808.5 | 815.8 | 747.5 | 768.5 | 760.9 | 739 | 712.1 | 772.2 | 291.8 | 385.1 | 426.5 | 327.5 | 430.1 | 418.6 | 421.8 | 402.6 | 580.1 | 404.7
1879 | 1685 | 686.1 | 274.44 | 320.8045 | 467.8 | 471.6 | 394.7 | 374.1 | 765.3 | 61.2 | 18 | 105.2 | 7 | 237.4 | 15.8 | 919.8 | 752.3 | 832.1 | 815.8 | 748 | 767.8 | 760.8 | 741.9 | 712.3 | 771.6 | 292 | 385.2 | 426.8 | 327.7 | 430.3 | 418.3 | 421.8 | 402.8 | 579.9 | 404.8
1880 | 1686 | 686.1 | 274.44 | 320.8045 | 467.3 | 471.1 | 394.5 | 373.8 | 760 | 61.3 | 18 | 105 | 8.6 | 233.9 | 17.8 | 918.2 | 752.2 | 849.3 | 815.8 | 749.4 | 769.1 | 761.5 | 744 | 712.5 | 772.6 | 292.3 | 385.5 | 426.7 | 327.9 | 430.3 | 418.2 | 421.8 | 402.7 | 579.8 | 404.9
1881 | 1687 | 686.2 | 274.48 | 320.8513 | 467.7 | 470.1 | 394.4 | 373.9 | 750.3 | 61.4 | 18 | 104.8 | 9.4 | 245.6 | 14.8 | 915.9 | 751.5 | 851.7 | 815.6 | 751.3 | 770.2 | 775.2 | 746.3 | 712.5 | 776.6 | 292.6 | 385.8 | 426.6 | 328.1 | 430.3 | 418.3 | 421.9 | 402.8 | 579.8 | 405.1
1882 | 1688 | 685.9 | 274.36 | 320.711 | 466.3 | 472 | 394.3 | 373.3 | 744 | 61.4 | 18 | 104.7 | 8.7 | 230.8 | 14.6 | 913.8 | 750.6 | 861.2 | 815.5 | 754.1 | 769.2 | 784.7 | 745.9 | 712.6 | 779.3 | 292.9 | 386 | 426.7 | 328.3 | 430.5 | 418.9 | 421.9 | 403 | 580 | 405.2
1883 | 1689 | 685.7 | 274.28 | 320.6175 | 465 | 470 | 394.3 | 373 | 733.6 | 61.3 | 18 | 104.6 | 8.7 | 243 | 15.2 | 912.2 | 751.4 | 863.7 | 815.4 | 757.3 | 769.7 | 794.2 | 748 | 712.6 | 780.7 | 293.1 | 386.3 | 426.9 | 328.6 | 430.8 | 419.6 | 422.1 | 403.2 | 580.5 | 405.4
1884 | 1690 | 686.1 | 274.44 | 320.8045 | 463.3 | 465.8 | 394.2 | 373.9 | 729.1 | 61.4 | 18 | 104.6 | 9.1 | 229.4 | 15.1 | 911.4 | 751.7 | 859.8 | 815.4 | 760.8 | 771 | 798.5 | 750.6 | 712.6 | 783.6 | 293.3 | 386.5 | 427 | 328.8 | 431.1 | 420.5 | 422.1 | 403.4 | 581.5 | 405.5
1885 | 1691 | 686.3 | 274.52 | 320.8981 | 467.8 | 461.9 | 394.6 | 374.9 | 733.4 | 61.5 | 18 | 104.7 | 9.2 | 238.3 | 17.3 | 910.8 | 751.9 | 860.1 | 815.3 | 763.2 | 770.5 | 796.9 | 751.9 | 712.5 | 785.2 | 293.6 | 386.8 | 426.9 | 329 | 431.2 | 421.2 | 422.1 | 403.5 | 582.2 | 405.6
1886 | 1692 | 686 | 274.4 | 320.7578 | 467.5 | 458.4 | 394.6 | 374.1 | 725.7 | 61.5 | 18 | 104.7 | 7.7 | 242.5 | 16.8 | 909.2 | 751.9 | 864 | 815.3 | 765.1 | 770 | 796.3 | 755 | 712.3 | 786.9 | 293.8 | 387 | 426.9 | 329.2 | 431.3 | 421.8 | 422.2 | 403.6 | 582.7 | 405.8
1887 | 1693 | 688.3 | 275.32 | 321.8332 | 465.1 | 458.3 | 394.3 | 372.7 | 727.3 | 61.6 | 18 | 104.6 | 7.2 | 227.8 | 14.3 | 906.9 | 751.6 | 869.9 | 815.1 | 767.1 | 771.8 | 800.5 | 756.2 | 712.3 | 789.5 | 294 | 387.2 | 427 | 329.4 | 431.7 | 422 | 422.2 | 403.7 | 582.8 | 405.9
1888 | 1694 | 687.3 | 274.92 | 321.3656 | 462.3 | 461.8 | 394.5 | 371.8 | 730.7 | 61.6 | 18 | 104.7 | 7.9 | 223.6 | 11.1 | 905.4 | 751.5 | 871.3 | 814.8 | 768.5 | 772.2 | 804.9 | 755.9 | 712.5 | 791.5 | 294.2 | 387.4 | 427.2 | 329.7 | 431.9 | 422.1 | 422.1 | 403.8 | 582.8 | 406
1889 | 1695 | 685.5 | 274.2 | 320.524 | 461.1 | 460.9 | 394.5 | 372 | 725.1 | 61.6 | 18 | 104.8 | 9.6 | 243.3 | 10.8 | 903.7 | 750.5 | 874.3 | 814.7 | 769.6 | 772.7 | 806.9 | 758.3 | 712.8 | 793.4 | 294.3 | 387.5 | 427.2 | 329.9 | 432 | 422.4 | 422 | 403.9 | 583 | 406.1
1890 | 1696 | 685.9 | 274.36 | 320.711 | 458.5 | 458.4 | 394.3 | 371.7 | 713.6 | 61.6 | 18 | 104.8 | 9 | 206.9 | 12.4 | 901.5 | 750.2 | 873.2 | 814.4 | 770.6 | 774 | 812.8 | 760 | 712.9 | 793.5 | 294.6 | 387.6 | 427.2 | 330.1 | 432.1 | 422.6 | 421.9 | 403.9 | 583.4 | 406.3
1891 | 1697 | 686.7 | 274.68 | 321.0851 | 455.8 | 458 | 395 | 371.4 | 722.2 | 61.7 | 18 | 104.8 | 9.5 | 220.8 | 15.4 | 901 | 750.8 | 861.9 | 814 | 771.5 | 774.2 | 818.9 | 760.8 | 712.9 | 795 | 294.9 | 387.8 | 427.6 | 330.3 | 432.4 | 422.7 | 421.9 | 404 | 584.3 | 406.4
1892 | 1698 | 686.2 | 274.48 | 320.8513 | 459.3 | 454.4 | 395.9 | 371.3 | 733.4 | 61.7 | 18 | 104.7 | 9.5 | 221 | 12.2 | 901 | 753.2 | 864.7 | 813.6 | 772.6 | 775.6 | 818.8 | 761.8 | 713.5 | 797.1 | 295.2 | 387.9 | 427.8 | 330.6 | 432.8 | 422.6 | 421.8 | 404 | 584.6 | 406.5
1893 | 1699 | 685.3 | 274.12 | 320.4305 | 457 | 454.1 | 397.5 | 371.8 | 746.7 | 61.6 | 18 | 104.5 | 10.3 | 220.1 | 12 | 900.7 | 753.6 | 865.2 | 813.4 | 773 | 776 | 818.1 | 760.5 | 714.1 | 797.2 | 295.6 | 388.2 | 427.8 | 330.8 | 433.1 | 422.3 | 421.7 | 404 | 584.5 | 406.7
1894 | 1700 | 685.5 | 274.2 | 320.524 | 455.1 | 458.8 | 397.2 | 371.2 | 759.8 | 61.5 | 18 | 104.4 | 9 | 237.2 | 12.5 | 902.2 | 754.8 | 865.8 | 813.2 | 773.4 | 775.6 | 819.7 | 759.1 | 714.7 | 797 | 295.9 | 388.4 | 428.2 | 331 | 433.3 | 422.5 | 421.7 | 404.1 | 584.5 | 406.8
1895 | 1701 | 686.8 | 274.72 | 321.1319 | 453.8 | 459.2 | 396.6 | 371.3 | 765.7 | 61.6 | 18 | 104.3 | 8.6 | 241.4 | 11.8 | 900.9 | 754.8 | 857.7 | 813.1 | 774.7 | 776.7 | 822 | 759.5 | 715.2 | 799.1 | 296.2 | 388.6 | 428.1 | 331.3 | 433.5 | 422.5 | 421.6 | 404.2 | 584.4 | 407
1896 | 1702 | 686.8 | 274.72 | 321.1319 | 452.5 | 459.6 | 396.5 | 371.5 | 762.4 | 61.6 | 18 | 104.1 | 7.3 | 248 | 9.4 | 903 | 755.6 | 863.4 | 813.1 | 775.7 | 777.4 | 815.3 | 763.5 | 715.7 | 798.4 | 296.5 | 388.7 | 428.6 | 331.5 | 433.7 | 422.5 | 421.6 | 404.2 | 584.7 | 407.1
1897 | 1703 | 686.4 | 274.56 | 320.9448 | 450.8 | 461.1 | 396.3 | 371.4 | 743.4 | 61.7 | 18 | 104.1 | 9 | 248.4 | 11.5 | 906.7 | 758 | 854.9 | 813 | 776 | 773.6 | 795.3 | 771.6 | 715.9 | 791.9 | 296.7 | 388.9 | 429.7 | 331.7 | 433.9 | 422.5 | 421.6 | 404.3 | 585.2 | 407.3
1898 | 1704 | 686.9 | 274.76 | 321.1786 | 448.4 | 462.5 | 397.1 | 371.8 | 719.2 | 61.7 | 18 | 104 | 9.5 | 258.5 | 14.5 | 906.3 | 759.2 | 828.4 | 813.2 | 773.9 | 774.1 | 791.2 | 772.2 | 716 | 791.5 | 296.9 | 389.1 | 429 | 331.9 | 433.8 | 422.5 | 421.5 | 404.3 | 585.1 | 407.4
1899 | 1705 | 686.5 | 274.6 | 320.9916 | 447.6 | 465.8 | 397 | 372.3 | 712.2 | 61.8 | 18 | 104.2 | 9.9 | 242.3 | 14 | 905.9 | 761.5 | 788.5 | 813.1 | 771.6 | 768.8 | 793.6 | 771 | 715.9 | 790.7 | 297 | 389.3 | 428.8 | 332.2 | 433.8 | 422.9 | 421.4 | 404.5 | 584.7 | 407.5
1900 | 1706 | 686.4 | 274.56 | 320.9448 | 448.2 | 467.8 | 396.7 | 372.8 | 697 | 61.8 | 18 | 104.6 | 12.9 | 243.2 | 16.5 | 908.3 | 762.6 | 780.1 | 813 | 769.7 | 765 | 791.8 | 755.1 | 715.8 | 785.1 | 297.3 | 389.5 | 429 | 332.4 | 433.9 | 423 | 421.4 | 404.6 | 584.1 | 407.6
1901 | 1707 | 686.2 | 274.48 | 320.8513 | 448 | 466.1 | 397.3 | 373.1 | 704.6 | 61.8 | 18 | 104.7 | 11.7 | 243.1 | 18.8 | 910.5 | 762.7 | 775.9 | 812.9 | 766.1 | 769.9 | 792 | 753.1 | 716.2 | 785.1 | 297.6 | 389.6 | 429.3 | 332.6 | 434.1 | 423.2 | 421.4 | 404.6 | 583.6 | 407.8
1902 | 1708 | 686.4 | 274.56 | 320.9448 | 448 | 467.6 | 397.1 | 373.9 | 724.7 | 61.7 | 18 | 104.7 | 13.7 | 233.7 | 17.5 | 914.1 | 761.1 | 765.7 | 812.9 | 761.1 | 770.7 | 783.3 | 744.6 | 716.8 | 780.7 | 297.8 | 389.7 | 430.3 | 332.8 | 434.4 | 423.2 | 421.4 | 404.6 | 583.3 | 407.9
1903 | 1709 | 686.2 | 274.48 | 320.8513 | 449.4 | 470.4 | 396.9 | 375.5 | 720.4 | 61.7 | 18 | 104.6 | 13.3 | 245.3 | 18.5 | 917.7 | 759 | 766.7 | 812.9 | 757.2 | 765.6 | 773.1 | 731.7 | 717.2 | 776.1 | 298.1 | 390 | 430.2 | 333 | 434.7 | 423 | 421.5 | 404.6 | 583.1 | 408
1904 | 1710 | 685.9 | 274.36 | 320.711 | 449.9 | 470 | 396.9 | 376.2 | 720.2 | 61.7 | 18 | 104.6 | 10 | 250.1 | 26.1 | 920.4 | 756.2 | 753.4 | 813.1 | 753.2 | 766.6 | 762.4 | 718.3 | 717.7 | 772 | 298.3 | 390.1 | 430.7 | 333.2 | 435.1 | 422.7 | 421.5 | 404.6 | 582.7 | 408.2
1905 | 1711 | 686 | 274.4 | 320.7578 | 451.1 | 468.8 | 398 | 376.9 | 722.5 | 61.7 | 18 | 104.5 | 8.9 | 234.8 | 22.6 | 922.3 | 752.4 | 751.4 | 813.5 | 750 | 761.3 | 748.5 | 713.4 | 718.1 | 768.8 | 298.6 | 390.3 | 431.3 | 333.5 | 435.4 | 422.5 | 421.4 | 404.7 | 582.3 | 408.3
1906 | 1712 | 686.3 | 274.52 | 320.8981 | 454.9 | 467.3 | 399.4 | 377.2 | 708.7 | 61.7 | 18 | 104.5 | 8.6 | 235.3 | 21.4 | 924.2 | 747.7 | 732.3 | 814 | 745.7 | 758.7 | 736.9 | 709 | 718 | 764.7 | 299 | 390.3 | 431 | 333.7 | 435.7 | 422.5 | 421.5 | 404.8 | 581.9 | 408.5
1907 | 1713 | 687 | 274.8 | 321.2254 | 457.1 | 468.5 | 400.4 | 376.8 | 692.5 | 61.8 | 18 | 104.5 | 9.8 | 217.3 | 18.1 | 924.7 | 744.7 | 733.8 | 814.2 | 742.4 | 756.5 | 728.7 | 703 | 718.1 | 761.2 | 299.2 | 390.5 | 431.1 | 333.9 | 435.9 | 422.3 | 421.5 | 404.7 | 581.4 | 408.6
1908 | 1714 | 686.8 | 274.72 | 321.1319 | 461.4 | 468.3 | 400.6 | 377.1 | 709.6 | 61.9 | 18 | 104.4 | 9.1 | 228.8 | 15.5 | 925 | 742.8 | 738.1 | 814.2 | 739.9 | 757.7 | 721.2 | 699.2 | 718.6 | 759.4 | 299.4 | 390.7 | 431.7 | 334.1 | 436.1 | 422.1 | 421.5 | 404.7 | 581 | 408.8
1909 | 1715 | 685.5 | 274.2 | 320.524 | 462 | 466.9 | 402.2 | 377.7 | 728.7 | 61.9 | 18 | 104 | 7.7 | 215.5 | 17.4 | 926.7 | 738.6 | 743.1 | 814.5 | 735.9 | 755.6 | 713 | 690.2 | 718.8 | 756.5 | 299.6 | 390.8 | 432.1 | 334.3 | 436.4 | 421.9 | 421.7 | 404.7 | 580.7 | 408.9
1910 | 1716 | 685.6 | 274.24 | 320.5708 | 464 | 467.3 | 403.4 | 378 | 737 | 61.9 | 18 | 103.9 | 8.1 | 221.2 | 19 | 923.7 | 740.4 | 765.9 | 814.8 | 736.3 | 758.2 | 710.3 | 696.4 | 719 | 755.6 | 299.9 | 390.8 | 432.4 | 334.6 | 436.7 | 421.9 | 421.7 | 404.7 | 580.5 | 409
1911 | 1717 | 685.1 | 274.04 | 320.337 | 464.2 | 468.4 | 404.2 | 378.3 | 740.5 | 61.8 | 18 | 104 | 10.6 | 266.6 | 11.9 | 923.2 | 740.3 | 752.9 | 814.9 | 733.3 | 760.2 | 713.1 | 701.9 | 719 | 755 | 300.2 | 391 | 432.4 | 334.8 | 436.9 | 422 | 421.8 | 404.8 | 580.3 | 409.2
1912 | 1718 | 684.4 | 273.76 | 320.0097 | 465.2 | 468.7 | 404.8 | 378.8 | 732.9 | 61.9 | 18 | 104 | 11.3 | 240.5 | 11.8 | 923.3 | 738 | 728.1 | 815.2 | 727.2 | 754.7 | 710.8 | 696.5 | 718.7 | 750.7 | 300.4 | 391.2 | 432.8 | 335 | 437.3 | 421.9 | 421.9 | 404.8 | 580.1 | 409.3
1913 | 1719 | 685.7 | 274.28 | 320.6175 | 466.5 | 468.9 | 404.8 | 379.7 | 726.5 | 61.8 | 18 | 104 | 10.4 | 233.8 | 11.3 | 920.1 | 738.5 | 724.9 | 815.1 | 725.5 | 756.8 | 711.9 | 696.1 | 718.3 | 748.2 | 300.6 | 391.6 | 432.6 | 335.2 | 437.6 | 421.8 | 422 | 404.9 | 579.6 | 409.5
1914 | 1720 | 685.6 | 274.24 | 320.5708 | 467.5 | 469.7 | 404.5 | 379.8 | 724 | 61.7 | 18 | 104 | 9.5 | 226.2 | 10.3 | 917.5 | 742 | 738.8 | 815 | 725.9 | 761.5 | 716.5 | 701.7 | 718.2 | 748.8 | 300.9 | 391.9 | 432.4 | 335.5 | 437.8 | 421.7 | 422 | 404.9 | 579.1 | 409.6
1915 | 1721 | 686.1 | 274.44 | 320.8045 | 469.2 | 469.5 | 404 | 379.4 | 728.7 | 61.6 | 18 | 104 | 8.7 | 231.7 | 14.1 | 916.8 | 744.2 | 757.8 | 814.6 | 725.7 | 761.9 | 725.3 | 709.5 | 718.6 | 751.2 | 301.2 | 392.1 | 432.9 | 335.7 | 438 | 421.5 | 422.1 | 404.9 | 578.7 | 409.8
1916 | 1722 | 685.6 | 274.24 | 320.5708 | 469.6 | 471.3 | 403.7 | 379.6 | 743.9 | 61.5 | 18 | 104.2 | 10.2 | 238.8 | 15.8 | 917.1 | 742.9 | 782.4 | 814.4 | 723.2 | 762.6 | 723.7 | 706.1 | 718.8 | 747.3 | 301.5 | 392.4 | 433.8 | 335.9 | 438.4 | 421.3 | 422.2 | 404.9 | 578.6 | 409.9
1917 | 1723 | 686.6 | 274.64 | 321.0383 | 468.4 | 472.3 | 404.1 | 380.3 | 746.7 | 61.5 | 18 | 104.3 | 10.8 | 225.6 | 12.4 | 915.2 | 745.6 | 795.5 | 814.2 | 724.6 | 764.4 | 727.8 | 711.8 | 718.8 | 746.9 | 301.8 | 392.7 | 433.6 | 336.1 | 438.5 | 421.2 | 422.2 | 405 | 578.5 | 410.1
1918 | 1724 | 687.7 | 275.08 | 321.5527 | 468.3 | 469 | 404.6 | 380.1 | 753.6 | 61.5 | 18 | 104.5 | 9.4 | 215.8 | 12.8 | 913.9 | 747.8 | 800.5 | 813.7 | 724.9 | 765.8 | 732.1 | 717 | 719 | 746.3 | 302 | 393 | 433.6 | 336.4 | 438.5 | 421.2 | 422.2 | 405 | 578.2 | 410.2
1919 | 1725 | 686.6 | 274.64 | 321.0383 | 471.1 | 464.8 | 405.1 | 380 | 751.3 | 61.5 | 18 | 104.4 | 6.8 | 240.8 | 14.2 | 913.4 | 751.3 | 799.5 | 813.4 | 725.7 | 770.1 | 740.7 | 726.6 | 719.6 | 748.9 | 302.4 | 393.1 | 433.6 | 336.6 | 438.6 | 421.2 | 422.2 | 405 | 577.8 | 410.4
1920 | 1726 | 685.9 | 274.36 | 320.711 | 471.6 | 463 | 405.3 | 379.6 | 757.5 | 61.5 | 18 | 104.2 | 6 | 240.3 | 19.3 | 912.9 | 755.1 | 804.5 | 813 | 726.3 | 771.7 | 744.1 | 731.4 | 720 | 749.1 | 302.7 | 393.2 | 433.9 | 336.8 | 438.6 | 421 | 422.2 | 405 | 577.6 | 410.5
1921 | 1727 | 686 | 274.4 | 320.7578 | 470.5 | 463.4 | 405 | 380.1 | 768.1 | 61.5 | 18 | 104 | 6.6 | 243 | 17.2 | 914.4 | 755.9 | 820.9 | 812.9 | 727.9 | 770.8 | 743.8 | 733.1 | 720.3 | 749.3 | 303.1 | 393.4 | 434.4 | 337 | 438.6 | 420.9 | 422.2 | 405 | 577.5 | 410.6
1922 | 1728 | 685.5 | 274.2 | 320.524 | 470 | 463.1 | 405 | 380.4 | 760.2 | 61.5 | 18 | 103.9 | 9.2 | 216.5 | 15.4 | 914.1 | 757.4 | 832.1 | 812.6 | 728.4 | 772 | 738 | 733.1 | 720.7 | 749.4 | 303.5 | 393.6 | 435 | 337.3 | 438.7 | 420.6 | 422.3 | 405 | 577.6 | 410.8
1923 | 1729 | 685.4 | 274.16 | 320.4772 | 468.5 | 463.2 | 404.9 | 380 | 746.5 | 61.5 | 18 | 104 | 8.7 | 248.1 | 13.3 | 912 | 760.4 | 833.2 | 812.5 | 729.6 | 773.4 | 746.1 | 738.1 | 720.7 | 752.6 | 303.8 | 393.9 | 434.4 | 337.5 | 438.7 | 420.3 | 422.2 | 405 | 577.8 | 410.9
1924 | 1730 | 685.4 | 274.16 | 320.4772 | 466.4 | 463 | 404.4 | 379.7 | 751.2 | 61.5 | 18 | 104 | 9.1 | 252.8 | 11.1 | 910.7 | 761.6 | 843.6 | 812.3 | 731.7 | 775.1 | 762.2 | 742.6 | 720.8 | 755.2 | 304 | 394.1 | 434.4 | 337.7 | 438.7 | 419.9 | 422.1 | 405.1 | 577.7 | 411.1
1925 | 1731 | 685.3 | 274.12 | 320.4305 | 463.7 | 461.5 | 403.4 | 379.5 | 761.2 | 61.6 | 18 | 104.1 | 8.1 | 248.8 | 13.7 | 913.5 | 763.3 | 853.2 | 812.2 | 731.9 | 776.3 | 764.2 | 746.8 | 721.1 | 756 | 304.1 | 394.2 | 435.3 | 338 | 438.8 | 419.6 | 422.1 | 405 | 577.8 | 411.2
1926 | 1732 | 684.2 | 273.68 | 319.9162 | 460.4 | 458.9 | 403.2 | 379.5 | 769.9 | 61.6 | 18 | 104.2 | 6.5 | 257.1 | 16.4 | 910.5 | 763.1 | 853.1 | 812 | 736.2 | 779.1 | 773.4 | 749.5 | 721.5 | 759.4 | 304.3 | 394.2 | 435.1 | 338.2 | 438.9 | 419.5 | 422.2 | 405.1 | 578.2 | 411.3
1927 | 1733 | 686.2 | 274.48 | 320.8513 | 457.8 | 455.8 | 402.9 | 379.1 | 772.9 | 61.6 | 18 | 104.2 | 5.9 | 243.2 | 18 | 909.6 | 763.8 | 859.1 | 811.7 | 740.5 | 778.2 | 781.2 | 750.1 | 721.7 | 760.8 | 304.6 | 394.4 | 434.9 | 338.4 | 439.1 | 419.6 | 422.3 | 405.2 | 578.5 | 411.4
1928 | 1734 | 687 | 274.8 | 321.2254 | 456.1 | 452.7 | 402.1 | 378.1 | 768.7 | 61.6 | 18 | 104.2 | 6.4 | 245.9 | 18.8 | 912.5 | 766.1 | 865.6 | 811.9 | 743 | 779.1 | 787.3 | 756.7 | 721.5 | 764.1 | 304.8 | 394.5 | 435 | 338.7 | 438.9 | 419.9 | 422.2 | 405.3 | 578.7 | 411.6
1929 | 1735 | 685.9 | 274.36 | 320.711 | 452.4 | 451.3 | 401.2 | 377.2 | 761 | 61.7 | 18 | 104.1 | 7.9 | 252.4 | 19 | 911 | 766.6 | 865.5 | 812.1 | 746.6 | 777.8 | 794 | 756 | 721.2 | 765.9 | 305.1 | 394.7 | 434.8 | 338.9 | 438.5 | 419.9 | 422 | 405.4 | 578.6 | 411.7
1930 | 1736 | 685.9 | 274.36 | 320.711 | 449.3 | 452.1 | 400.6 | 376.3 | 756.4 | 61.7 | 18 | 104.1 | 6.5 | 250.2 | 19.2 | 909.8 | 768.4 | 874.1 | 812.1 | 750.1 | 779.4 | 794.8 | 759.3 | 720.9 | 768.2 | 305.5 | 395 | 434.9 | 339.1 | 438.3 | 419.8 | 421.8 | 405.3 | 578.7 | 411.8
1931 | 1737 | 685.6 | 274.24 | 320.5708 | 446.5 | 452 | 399.6 | 375.2 | 748.8 | 61.8 | 18 | 104.3 | 6.3 | 249.4 | 15.8 | 909 | 767.5 | 866.3 | 811.9 | 750.9 | 779.5 | 791.2 | 759.4 | 720.8 | 768.7 | 305.7 | 395.2 | 435 | 339.4 | 438.2 | 419.5 | 421.7 | 405.3 | 579 | 411.9
1932 | 1738 | 686.4 | 274.56 | 320.9448 | 444.2 | 452.5 | 400 | 373.8 | 752.5 | 61.8 | 18 | 104.5 | 7.3 | 250.6 | 15.3 | 909.2 | 769.5 | 848.1 | 811.9 | 748.4 | 780.7 | 791.9 | 766.5 | 720.7 | 768.6 | 305.9 | 395.4 | 435.4 | 339.6 | 438 | 419.4 | 421.5 | 405.3 | 579.3 | 412
1933 | 1739 | 686.4 | 274.56 | 320.9448 | 442.5 | 451.3 | 399.3 | 373.2 | 737.4 | 61.8 | 18 | 104.9 | 6.9 | 267.8 | 13.8 | 912.1 | 772.8 | 809.1 | 811.9 | 745.7 | 776.7 | 787.8 | 771.5 | 720.5 | 765.5 | 306.2 | 395.7 | 435.5 | 339.9 | 438.1 | 419.4 | 421.5 | 405.4 | 579.1 | 412.1
1934 | 1740 | 686.7 | 274.68 | 321.0851 | 442.2 | 450.7 | 399.5 | 373.3 | 732.7 | 61.8 | 18 | 105.2 | 6.3 | 259.6 | 13.7 | 916.1 | 767 | 760.9 | 811.8 | 740.9 | 767.8 | 777.3 | 752.3 | 720.3 | 760.6 | 306.6 | 395.9 | 435.5 | 340.1 | 438 | 419.2 | 421.4 | 405.4 | 578.6 | 412.2
1935 | 1741 | 687.5 | 275 | 321.4592 | 442.8 | 449.9 | 399.1 | 373.4 | 703.7 | 61.8 | 18 | 105.3 | 6.7 | 247.5 | 10.7 | 917.7 | 760.1 | 741.5 | 811.9 | 737.3 | 755.9 | 760.9 | 729.6 | 719.7 | 755.7 | 306.9 | 396.2 | 435.3 | 340.4 | 438.2 | 419.1 | 421.5 | 405.3 | 578 | 412.3
1936 | 1742 | 686.3 | 274.52 | 320.8981 | 441.7 | 449.1 | 399.1 | 374.2 | 676.5 | 61.9 | 18 | 105.4 | 6.4 | 244.2 | 12.7 | 917.4 | 760.7 | 746.6 | 812.2 | 736.2 | 757.9 | 761 | 733.2 | 719.2 | 756.7 | 307.2 | 396.5 | 435 | 340.6 | 438.5 | 419 | 421.6 | 405.4 | 577.3 | 412.4
1937 | 1743 | 685.6 | 274.24 | 320.5708 | 439.9 | 448.1 | 399.6 | 375.2 | 665.3 | 61.9 | 18 | 105.5 | 7.4 | 237.5 | 12.3 | 917.7 | 760.4 | 746.9 | 812.6 | 735.2 | 760.5 | 763.8 | 735.9 | 719 | 756.6 | 307.4 | 396.7 | 435 | 340.9 | 438.6 | 419.1 | 421.7 | 405.5 | 576.8 | 412.5
1938 | 1744 | 686.5 | 274.6 | 320.9916 | 438.9 | 447.3 | 399 | 375.7 | 654.3 | 61.8 | 18 | 105.6 | 7.4 | 247.2 | 10.8 | 916.3 | 762.5 | 758.4 | 812.9 | 737 | 761.6 | 770.9 | 743.6 | 718.6 | 758.5 | 307.6 | 396.8 | 435 | 341.1 | 438.6 | 419.1 | 421.6 | 405.6 | 576.3 | 412.7
1939 | 1745 | 686.2 | 274.48 | 320.8513 | 439.5 | 449.1 | 398.5 | 375.5 | 677.9 | 61.8 | 18 | 105.8 | 8.4 | 240.8 | 12.6 | 914.7 | 763.1 | 761.6 | 812.9 | 735.2 | 768.4 | 775.8 | 747.4 | 719 | 757.5 | 307.9 | 396.9 | 435.4 | 341.4 | 438.5 | 418.7 | 421.5 | 405.5 | 575.9 | 412.8
1940 | 1746 | 684.8 | 273.92 | 320.1967 | 439 | 449.5 | 398.8 | 374.6 | 705.6 | 61.7 | 18 | 105.9 | 9.7 | 250.5 | 12.1 | 917.7 | 759.3 | 749.3 | 812.8 | 731 | 770.2 | 770.5 | 740.6 | 719.1 | 754.6 | 308.2 | 397 | 435.7 | 341.6 | 438.5 | 418.3 | 421.4 | 405.5 | 575.7 | 412.9
1941 | 1747 | 686.5 | 274.6 | 320.9916 | 439.7 | 450.9 | 399.3 | 374.3 | 704 | 61.7 | 18 | 106 | 9.5 | 250.5 | 10.9 | 917.5 | 758.6 | 746.8 | 812.8 | 728.7 | 768.5 | 771.4 | 738.3 | 719.3 | 753.1 | 308.4 | 397.2 | 435.6 | 341.9 | 438.7 | 418 | 421.5 | 405.4 | 575.4 | 413
1942 | 1748 | 687.2 | 274.88 | 321.3189 | 441.2 | 449.9 | 399.5 | 374.7 | 710.8 | 61.6 | 18 | 106 | 8.9 | 255.3 | 10.8 | 915.9 | 761.6 | 767.6 | 812.6 | 729.6 | 771.8 | 777.4 | 744.4 | 719.7 | 755.8 | 308.7 | 397.2 | 435.7 | 342.1 | 439 | 417.8 | 421.7 | 405.4 | 575 | 413.1
1943 | 1749 | 685.6 | 274.24 | 320.5708 | 442.8 | 449.1 | 398.9 | 376.3 | 723.8 | 61.6 | 18 | 106.1 | 8.5 | 247.8 | 13.3 | 915.2 | 762.3 | 779.4 | 812.5 | 730 | 776.5 | 781.3 | 749.5 | 720.2 | 756.2 | 309 | 397.2 | 436 | 342.3 | 439.3 | 417.9 | 421.8 | 405.4 | 574.7 | 413.3
1944 | 1750 | 684.2 | 273.68 | 319.9162 | 444.4 | 448.7 | 398.5 | 377.8 | 729.6 | 61.6 | 18 | 106 | 10.1 | 241.9 | 18.4 | 914.8 | 765.9 | 775.4 | 812.6 | 730.2 | 777.7 | 781.2 | 753 | 720.9 | 756.8 | 309.3 | 397.3 | 436 | 342.6 | 439.6 | 418 | 421.9 | 405.5 | 574.4 | 413.4
1945 | 1751 | 686 | 274.4 | 320.7578 | 446 | 448.3 | 398.9 | 377.8 | 736.2 | 61.6 | 18 | 105.6 | 10.2 | 239 | 19.7 | 917.7 | 762.2 | 743.9 | 812.5 | 726.5 | 772.3 | 770.5 | 740.6 | 721 | 753.4 | 309.6 | 397.6 | 436.3 | 342.8 | 439.8 | 418 | 421.9 | 405.5 | 574.1 | 413.5
1946 | 1752 | 684.9 | 273.96 | 320.2435 | 447.3 | 447.3 | 399.6 | 378 | 717.7 | 61.6 | 18 | 105.4 | 12.5 | 222.8 | 17 | 919.4 | 755.9 | 740.5 | 812.8 | 722.2 | 765.7 | 754.2 | 724.3 | 720.9 | 747.9 | 309.8 | 397.8 | 436.5 | 343.1 | 440.1 | 417.9 | 422 | 405.4 | 573.7 | 413.7
1947 | 1753 | 685 | 274 | 320.2902 | 448.3 | 447.2 | 400.7 | 378.9 | 713.3 | 61.6 | 18 | 105.6 | 12.4 | 227.8 | 15.6 | 917.9 | 758.1 | 748.7 | 812.9 | 723.2 | 771.3 | 751.2 | 731.1 | 721 | 748.8 | 310.1 | 398.1 | 436.5 | 343.3 | 440.1 | 417.8 | 422 | 405.5 | 573.2 | 413.8
1948 | 1754 | 684.7 | 273.88 | 320.1499 | 449.1 | 447.9 | 401 | 378.5 | 737 | 61.7 | 18 | 105.6 | 11.2 | 217.3 | 12.1 | 918.5 | 759.3 | 758.1 | 812.8 | 721.4 | 774.8 | 754 | 738 | 721.6 | 750 | 310.4 | 398.3 | 437 | 343.6 | 440.3 | 418.1 | 422.1 | 405.5 | 572.9 | 413.9
1949 | 1755 | 684.8 | 273.92 | 320.1967 | 449.7 | 448.8 | 401 | 378.8 | 744.8 | 61.7 | 18 | 105.6 | 7.4 | 229.2 | 10.5 | 918.2 | 758.4 | 754.3 | 812.3 | 718.5 | 776.5 | 753.1 | 738 | 722.3 | 749.3 | 310.7 | 398.4 | 437.2 | 343.8 | 440.6 | 418.4 | 422.2 | 405.5 | 572.9 | 414
1950 | 1756 | 684.9 | 273.96 | 320.2435 | 452.8 | 448.1 | 402.2 | 379.3 | 744.3 | 61.8 | 18 | 105.6 | 8.5 | 248.2 | 13.6 | 918.8 | 755.5 | 721.2 | 812.7 | 714.6 | 766.7 | 748.7 | 724.8 | 722.2 | 744.7 | 310.9 | 398.5 | 437.2 | 344.1 | 440.9 | 418.4 | 422.4 | 405.5 | 572.8 | 414.2
1951 | 1757 | 685.3 | 274.12 | 320.4305 | 454.4 | 448.3 | 402.4 | 379.2 | 729.5 | 61.8 | 18 | 105.6 | 10 | 239.5 | 20.3 | 920 | 750.5 | 702.8 | 813.1 | 710 | 761.6 | 739.1 | 710.1 | 721.8 | 740.5 | 311.2 | 398.7 | 437 | 344.3 | 441.3 | 418.3 | 422.5 | 405.5 | 572.5 | 414.3
1952 | 1758 | 685.1 | 274.04 | 320.337 | 453.8 | 446.6 | 401.9 | 379 | 726.5 | 61.8 | 18 | 105.6 | 8 | 237.9 | 19.5 | 919.9 | 749.6 | 691.9 | 813.4 | 708.4 | 767 | 737.7 | 715.4 | 721.9 | 740.6 | 311.6 | 398.7 | 437.4 | 344.6 | 441.3 | 418 | 422.6 | 405.4 | 571.9 | 414.4
1953 | 1759 | 685.2 | 274.08 | 320.3837 | 454.3 | 446.1 | 401.4 | 379.5 | 735.6 | 61.7 | 18 | 105.4 | 6.5 | 241.5 | 18 | 920.4 | 747 | 681.3 | 813.6 | 705.7 | 764.1 | 732.7 | 712.1 | 722 | 737.3 | 311.8 | 398.7 | 437.9 | 344.8 | 441.5 | 417.8 | 422.8 | 405.4 | 571.6 | 414.6
1954 | 1760 | 685.5 | 274.2 | 320.524 | 455.6 | 448.4 | 401.6 | 380.3 | 732.4 | 61.7 | 18 | 105.3 | 9.2 | 245.8 | 17.5 | 921.2 | 743.4 | 675 | 813.9 | 701.1 | 754.5 | 720.9 | 693.4 | 721.9 | 733 | 312 | 399 | 438.3 | 345.1 | 441.7 | 417.6 | 423 | 405.4 | 571.3 | 414.7
1955 | 1761 | 685.5 | 274.2 | 320.524 | 457.2 | 448.6 | 401.7 | 381.2 | 727.3 | 61.6 | 18 | 105.2 | 11.1 | 240.5 | 15 | 919.4 | 743.9 | 704.8 | 814.1 | 701.9 | 755.1 | 714.4 | 695.1 | 721.6 | 731.8 | 312.3 | 399.2 | 438.2 | 345.3 | 442 | 417.2 | 423.2 | 405.4 | 570.8 | 414.9
1956 | 1762 | 685.6 | 274.24 | 320.5708 | 458.8 | 450 | 402.4 | 381.6 | 740.5 | 61.6 | 18 | 105.1 | 14.5 | 244.5 | 16.2 | 917.6 | 749.1 | 737.3 | 814.1 | 704.4 | 759.7 | 715.1 | 706.1 | 721.9 | 734.6 | 312.8 | 399.4 | 438.7 | 345.5 | 442.2 | 417.1 | 423.3 | 405.3 | 570.6 | 415
1957 | 1763 | 686.4 | 274.56 | 320.9448 | 458.9 | 450.3 | 403.8 | 382.1 | 739.5 | 61.6 | 18 | 105.1 | 13 | 267.1 | 14.8 | 916.3 | 752.7 | 745.7 | 814 | 703.9 | 762.8 | 723.2 | 717.6 | 722 | 735.7 | 313.1 | 399.6 | 438.4 | 345.8 | 442.4 | 416.7 | 423.3 | 405.3 | 570.4 | 415.1
1958 | 1764 | 685.6 | 274.24 | 320.5708 | 459.8 | 451.7 | 404.4 | 382.1 | 737.9 | 61.7 | 18 | 105 | 11.6 | 226.8 | 20.6 | 914.7 | 756.4 | 758.9 | 813.7 | 705.1 | 764.6 | 728 | 724.4 | 722 | 735.6 | 313.5 | 399.7 | 438.4 | 346 | 442.6 | 416.4 | 423.4 | 405.3 | 570.2 | 415.3
1959 | 1765 | 684.9 | 273.96 | 320.2435 | 460.7 | 450.3 | 404.2 | 381.6 | 744.1 | 61.7 | 18 | 104.9 | 10.5 | 242.9 | 21.6 | 913.3 | 759.8 | 775 | 813.4 | 708.7 | 769.8 | 742.7 | 736.8 | 722.3 | 739.6 | 313.8 | 399.9 | 438.4 | 346.3 | 442.5 | 416.4 | 423.5 | 405.4 | 569.9 | 415.4
1960 | 1766 | 686.1 | 274.44 | 320.8045 | 460.7 | 449.2 | 403.9 | 381.5 | 747.6 | 61.8 | 18 | 104.9 | 13.7 | 243.2 | 23.1 | 914.3 | 762.6 | 783.4 | 813.2 | 711.1 | 771.4 | 751.9 | 745.4 | 722.5 | 742.3 | 314.2 | 400 | 438.4 | 346.5 | 442.3 | 416.4 | 423.4 | 405.4 | 569.7 | 415.5
1961 | 1767 | 686.7 | 274.68 | 321.0851 | 460.6 | 449 | 403.9 | 380.8 | 745.9 | 61.9 | 17.9 | 104.9 | 13 | 238.2 | 19.7 | 917.5 | 764.5 | 781.6 | 813.3 | 710.2 | 773.5 | 754.5 | 748.8 | 722.7 | 742.5 | 314.5 | 400.2 | 438.9 | 346.8 | 442.1 | 416.4 | 423.3 | 405.4 | 569.6 | 415.6
1962 | 1768 | 685.2 | 274.08 | 320.3837 | 460.9 | 448.1 | 404 | 380.3 | 744.1 | 61.9 | 17.9 | 104.7 | 8.5 | 242.2 | 24.1 | 917.3 | 762.5 | 770.6 | 813 | 709.9 | 772.9 | 747.3 | 743 | 722.9 | 740.6 | 314.6 | 400.3 | 439.2 | 347 | 442 | 416.1 | 423.2 | 405.3 | 569.6 | 415.7
1963 | 1769 | 685.1 | 274.04 | 320.337 | 463.5 | 446.2 | 403.7 | 380.4 | 733.4 | 61.9 | 17.9 | 104.5 | 8.7 | 249.6 | 24.6 | 917.9 | 760.5 | 762 | 812.9 | 708.9 | 772.1 | 746 | 740.5 | 722.8 | 740.1 | 315 | 400.5 | 439 | 347.3 | 441.8 | 416 | 423.2 | 405.4 | 569.5 | 415.8
1964 | 1770 | 684.8 | 273.92 | 320.1967 | 463.1 | 446.4 | 403.7 | 380.6 | 726 | 61.9 | 17.9 | 104.5 | 10.7 | 259.6 | 24.1 | 917.1 | 762.5 | 765.6 | 813 | 708.8 | 773.8 | 752.9 | 746.4 | 722.8 | 741.4 | 315.1 | 400.6 | 439.1 | 347.6 | 441.7 | 415.9 | 423.2 | 405.4 | 569.2 | 415.9
1965 | 1771 | 684.6 | 273.84 | 320.1032 | 460.9 | 446.5 | 403.4 | 380.6 | 725.1 | 62 | 17.9 | 104.7 | 11.7 | 256.4 | 21.9 | 916.4 | 765.2 | 754.8 | 812.8 | 707.6 | 777.2 | 762.9 | 750.5 | 723.1 | 742.4 | 315.4 | 400.7 | 439.2 | 347.8 | 441.8 | 416 | 423.2 | 405.4 | 568.8 | 416
1966 | 1772 | 684.7 | 273.88 | 320.1499 | 460.6 | 445.8 | 402.5 | 379.8 | 729.2 | 62 | 17.9 | 105.1 | 11.1 | 261.6 | 21.8 | 916.8 | 764.7 | 748.7 | 812.5 | 706.2 | 779.6 | 761.4 | 751.2 | 723.4 | 741.8 | 315.8 | 400.9 | 439.3 | 348.1 | 442 | 416 | 423.2 | 405.5 | 568.6 | 416.1
1967 | 1773 | 684.5 | 273.8 | 320.0564 | 460.2 | 445 | 401.5 | 379.9 | 729 | 62 | 17.9 | 105.1 | 9.8 | 258.8 | 22.6 | 916.4 | 762.3 | 740.6 | 812.3 | 703.5 | 771.7 | 750.2 | 737.3 | 723.3 | 738.1 | 316 | 401.2 | 439.8 | 348.3 | 442.2 | 416.1 | 423.3 | 405.5 | 568.5 | 416.3
1968 | 1774 | 684.6 | 273.84 | 320.1032 | 460.9 | 445.3 | 401.6 | 380.4 | 726.7 | 62.1 | 17.9 | 105 | 9.9 | 238.1 | 20.5 | 914.9 | 763 | 754.1 | 812 | 704.8 | 775.2 | 743 | 735.6 | 723.4 | 738.8 | 316.1 | 401.4 | 439.9 | 348.6 | 442.5 | 416.3 | 423.4 | 405.5 | 568.1 | 416.4
1969 | 1775 | 684.9 | 273.96 | 320.2435 | 461.7 | 445.7 | 402 | 380.6 | 738.9 | 62.1 | 17.9 | 105.1 | 9.4 | 252.8 | 23.4 | 915.5 | 765.8 | 777.7 | 811.7 | 707.4 | 778.3 | 751.3 | 744.9 | 723.7 | 741.7 | 316.4 | 401.7 | 440.2 | 348.8 | 443 | 416.7 | 423.4 | 405.6 | 567.9 | 416.5
1970 | 1776 | 685.1 | 274.04 | 320.337 | 461 | 445.1 | 402.5 | 380.8 | 753.1 | 62.1 | 17.9 | 105.3 | 9.9 | 252.7 | 22.6 | 915.5 | 763.5 | 765.7 | 811.3 | 705.7 | 778.1 | 751.3 | 742.8 | 723.9 | 739.6 | 316.8 | 401.9 | 440.4 | 349.1 | 443.7 | 416.8 | 423.6 | 405.6 | 567.9 | 416.7
1971 | 1777 | 685.5 | 274.2 | 320.524 | 462 | 445.1 | 402.9 | 381.7 | 754.9 | 62.1 | 17.9 | 105.3 | 10.5 | 242 | 20.5 | 916.8 | 758.5 | 762.7 | 811.1 | 702.8 | 781.2 | 745.4 | 732.5 | 724.2 | 736.4 | 317 | 402.1 | 440.9 | 349.4 | 444.4 | 416.9 | 423.9 | 405.6 | 567.8 | 416.8
1972 | 1778 | 685.3 | 274.12 | 320.4305 | 462.2 | 444.6 | 403.3 | 382.7 | 760.7 | 62.1 | 17.9 | 104.9 | 9.5 | 260.3 | 19.9 | 917.9 | 756.3 | 776.1 | 811.3 | 702.7 | 783.3 | 742.3 | 736 | 724.6 | 736.4 | 317.3 | 402.3 | 441.2 | 349.6 | 444.8 | 417 | 424.2 | 405.6 | 567.6 | 417
1973 | 1779 | 685.5 | 274.2 | 320.524 | 462.1 | 445 | 404.5 | 383.3 | 762.4 | 62 | 17.9 | 104.5 | 7.8 | 254.9 | 19.6 | 918.3 | 758.1 | 785.6 | 811.6 | 702.8 | 781.3 | 739.5 | 735 | 725 | 735.5 | 317.7 | 402.5 | 441.4 | 349.9 | 445 | 416.9 | 424.3 | 405.6 | 567.5 | 417.1
1974 | 1780 | 685.3 | 274.12 | 320.4305 | 461 | 445.1 | 406.2 | 382.6 | 763.5 | 62 | 17.9 | 104.4 | 7.9 | 249.9 | 20.9 | 917.1 | 759.8 | 770.7 | 811.7 | 702.2 | 783.1 | 745.1 | 742.8 | 725.4 | 738.2 | 317.9 | 402.6 | 441.3 | 350.1 | 445 | 417 | 424.3 | 405.6 | 567.5 | 417.2
1975 | 1781 | 685.6 | 274.24 | 320.5708 | 460.4 | 445.3 | 406.7 | 382.3 | 764.7 | 62 | 17.9 | 104.3 | 8.8 | 255.2 | 21.6 | 916.4 | 761.3 | 744 | 811.6 | 699.9 | 781.3 | 755.1 | 748.3 | 725.4 | 738.3 | 318.1 | 402.8 | 441.1 | 350.4 | 445.1 | 417.8 | 424.3 | 405.8 | 567.4 | 417.3
1976 | 1782 | 685.3 | 274.12 | 320.4305 | 459.8 | 444.7 | 406.8 | 382.5 | 752.8 | 61.9 | 17.9 | 104 | 7.9 | 253 | 20.7 | 915.8 | 763.7 | 732.3 | 811.6 | 699.2 | 777 | 762.1 | 749.3 | 725.2 | 739.4 | 318.3 | 403 | 441.1 | 350.7 | 445.1 | 418.3 | 424.4 | 405.9 | 567.1 | 417.5
1977 | 1783 | 685.6 | 274.24 | 320.5708 | 459.7 | 442.6 | 405.7 | 382.5 | 729.7 | 61.9 | 17.9 | 104 | 7 | 240.8 | 17.5 | 915.3 | 763.2 | 713.7 | 811.5 | 696.6 | 769.5 | 768 | 744.3 | 724.8 | 740.3 | 318.6 | 403.1 | 441 | 351 | 445.2 | 418.8 | 424.5 | 406.1 | 566.7 | 417.6
1978 | 1784 | 685.4 | 274.16 | 320.4772 | 458.6 | 441 | 405.9 | 382.2 | 708.7 | 61.9 | 17.9 | 104.3 | 8.1 | 274.5 | 14.5 | 914.8 | 764.3 | 719.4 | 811.5 | 696.9 | 759.8 | 771.6 | 738.6 | 724.3 | 740.1 | 318.9 | 403.3 | 441 | 351.2 | 445.4 | 419.6 | 424.5 | 406.3 | 566.3 | 417.7
1979 | 1785 | 685.2 | 274.08 | 320.3837 | 459.1 | 440.4 | 405.2 | 382 | 688.6 | 61.9 | 17.9 | 104.4 | 7.1 | 259.2 | 15.4 | 912.9 | 767.2 | 744.5 | 811.4 | 699.8 | 763.1 | 780.7 | 745.9 | 724 | 745.4 | 319.2 | 403.5 | 440.8 | 351.5 | 445.4 | 420.1 | 424.6 | 406.4 | 566 | 417.8
1980 | 1786 | 685.3 | 274.12 | 320.4305 | 457.4 | 440.2 | 404.9 | 381.7 | 700.3 | 62 | 17.9 | 104.4 | 7.6 | 264.6 | 17.5 | 913.3 | 768.4 | 760.9 | 811.3 | 702.7 | 772.4 | 783.3 | 753.2 | 724.8 | 747 | 319.5 | 403.8 | 441.3 | 351.8 | 445.6 | 420.3 | 424.5 | 406.3 | 565.9 | 418
1981 | 1787 | 685.8 | 274.32 | 320.6643 | 454.3 | 439.5 | 405.1 | 381.3 | 719.2 | 62.1 | 17.9 | 104.3 | 7.7 | 258.3 | 15.2 | 916.1 | 767.1 | 740 | 811.2 | 698.3 | 773.2 | 777.7 | 748.6 | 725.3 | 743.8 | 319.8 | 404 | 442 | 352.1 | 445.9 | 420.7 | 424.6 | 406.4 | 566.3 | 418.1
1982 | 1788 | 686.1 | 274.44 | 320.8045 | 452.4 | 439.6 | 405.9 | 381.4 | 719.8 | 62.1 | 17.9 | 104.1 | 7.8 | 255.3 | 12.3 | 916.6 | 763.2 | 719.7 | 811.1 | 695.6 | 766.9 | 765.5 | 734.6 | 725.1 | 739.6 | 320 | 404.2 | 442.2 | 352.3 | 446.5 | 420.9 | 424.9 | 406.4 | 566.3 | 418.2
1983 | 1789 | 685.6 | 274.24 | 320.5708 | 452.1 | 439.6 | 407.8 | 381.6 | 716.3 | 62.2 | 17.9 | 104 | 9 | 249.5 | 10.8 | 916.5 | 759.3 | 701.8 | 811 | 693.1 | 762.1 | 757.7 | 727 | 725 | 736.7 | 320.2 | 404.4 | 442 | 352.6 | 446.8 | 421.1 | 425 | 406.5 | 566 | 418.4
1984 | 1790 | 685.6 | 274.24 | 320.5708 | 451.2 | 439.1 | 408.5 | 380.7 | 695.5 | 62.2 | 17.9 | 104 | 10.3 | 254.5 | 11.1 | 916.5 | 755.4 | 709.1 | 811 | 690.5 | 757.9 | 745.7 | 722.1 | 724.5 | 733.7 | 320.7 | 404.7 | 442 | 352.9 | 446.8 | 421.4 | 425 | 406.6 | 565.5 | 418.5
1985 | 1791 | 685.7 | 274.28 | 320.6175 | 450.6 | 437.2 | 409 | 380.2 | 694.2 | 62.2 | 17.9 | 104 | 9.8 | 260.8 | 13.1 | 914.4 | 760 | 729.5 | 810.8 | 692.8 | 768.2 | 747.1 | 733.4 | 724.7 | 735.8 | 320.8 | 404.9 | 441.7 | 353.1 | 447 | 421.7 | 425.1 | 406.7 | 565 | 418.6
1986 | 1792 | 685.9 | 274.36 | 320.711 | 449.1 | 435.5 | 408.1 | 380.4 | 715.5 | 62.2 | 17.9 | 104.3 | 8.6 | 255.1 | 13.6 | 912.3 | 763.8 | 747.3 | 810.5 | 697.1 | 775.4 | 755.6 | 740.7 | 725.2 | 738.6 | 321 | 405.1 | 442 | 353.4 | 447.2 | 421.8 | 425.2 | 406.8 | 564.9 | 418.7
1987 | 1793 | 685.1 | 274.04 | 320.337 | 447.3 | 435.3 | 406.6 | 380.8 | 737.3 | 62.2 | 17.9 | 104.3 | 7 | 264.4 | 13 | 912.2 | 768.3 | 761.2 | 810.3 | 698.4 | 778.6 | 763.5 | 747.6 | 725.7 | 740.9 | 321.3 | 405.3 | 442.2 | 353.7 | 447.2 | 421.6 | 425.2 | 406.8 | 565.2 | 418.9
1988 | 1794 | 686.6 | 274.64 | 321.0383 | 448.4 | 436.3 | 406.6 | 380.6 | 751.8 | 62.2 | 17.9 | 104.4 | 7.7 | 255.2 | 11.8 | 915.3 | 769.3 | 757 | 810.1 | 698.1 | 778.4 | 761.5 | 751.5 | 726.1 | 740.6 | 321.6 | 405.4 | 442.5 | 353.9 | 447.3 | 421.3 | 425.4 | 406.9 | 565.4 | 419
1989 | 1795 | 685.7 | 274.28 | 320.6175 | 450 | 435.8 | 406.5 | 380.8 | 749.6 | 62.2 | 17.9 | 104.7 | 8.5 | 240.3 | 16.1 | 915.1 | 764.7 | 742.9 | 809.8 | 695.7 | 775.1 | 755.6 | 742.6 | 726.1 | 737.1 | 321.8 | 405.6 | 442.6 | 354.2 | 447.3 | 420.9 | 425.4 | 406.9 | 565.3 | 419.1
1990 | 1796 | 686.7 | 274.68 | 321.0851 | 451 | 435.5 | 407 | 380.9 | 741.6 | 62.2 | 17.9 | 104.9 | 8.2 | 252.2 | 18.5 | 913.9 | 764.9 | 743.4 | 809.6 | 697.3 | 775.7 | 758.7 | 743 | 726.3 | 736.8 | 322.1 | 405.8 | 442.8 | 354.5 | 447.5 | 420.5 | 425.5 | 406.9 | 564.9 | 419.2
1991 | 1797 | 686.2 | 274.48 | 320.8513 | 452.4 | 434.6 | 406.5 | 381.4 | 748 | 62.1 | 17.9 | 104.9 | 9.1 | 254.4 | 19.4 | 913.6 | 764.7 | 748 | 809.6 | 697.2 | 782.2 | 761.9 | 750.6 | 726.6 | 738.5 | 322.2 | 406 | 442.9 | 354.7 | 447.5 | 420.3 | 425.5 | 406.9 | 564.6 | 419.4
1992 | 1798 | 685.8 | 274.32 | 320.6643 | 453.8 | 433.9 | 406.6 | 381.2 | 744.8 | 62.1 | 17.9 | 105.1 | 9.4 | 250.6 | 19.1 | 914 | 766.7 | 760.6 | 809.7 | 697.6 | 782.7 | 762 | 751.9 | 726.8 | 737.6 | 322.5 | 406.2 | 443.1 | 355 | 447.2 | 420 | 425.6 | 406.9 | 564.4 | 419.5
1993 | 1799 | 685 | 274 | 320.2902 | 455.2 | 433.6 | 407.9 | 380.9 | 738.4 | 62 | 17.9 | 105.3 | 10.4 | 258.4 | 16.2 | 914.1 | 768.9 | 762.5 | 809.9 | 698.8 | 783.7 | 768.1 | 758.5 | 726.9 | 739.6 | 322.8 | 406.3 | 442.9 | 355.2 | 447 | 420.2 | 425.5 | 407 | 564.1 | 419.6
1994 | 1800 | 684.8 | 273.92 | 320.1967 | 454.9 | 434.2 | 408.4 | 380.9 | 743 | 62 | 17.9 | 105.3 | 9.9 | 242.7 | 14.2 | 914.9 | 768 | 764 | 809.9 | 698.9 | 784 | 768.1 | 756.2 | 727.3 | 739.7 | 323 | 406.5 | 443.4 | 355.5 | 446.9 | 420.2 | 425.5 | 407 | 563.8 | 419.6
1995 | 1801 | 685.3 | 274.12 | 320.4305 | 455.9 | 434.8 | 409.5 | 381.3 | 751 | 62 | 17.9 | 105.3 | 9.9 | 248.6 | 16.2 | 915.7 | 765 | 781.8 | 810 | 700.1 | 787.7 | 758.6 | 753.1 | 727.7 | 737.9 | 323.2 | 406.6 | 444 | 355.8 | 446.7 | 419.8 | 425.5 | 406.9 | 563.7 | 419.7
1996 | 1802 | 684.3 | 273.72 | 319.9629 | 457.2 | 436 | 409.8 | 381.9 | 760.5 | 61.8 | 17.9 | 105.3 | 11 | 233.6 | 19 | 916.7 | 763.1 | 767 | 810.1 | 698.4 | 788.8 | 749.2 | 747.7 | 728.1 | 737.3 | 323.5 | 406.8 | 444.5 | 356 | 446.7 | 419.4 | 425.5 | 406.9 | 563.7 | 419.9
1997 | 1803 | 684.2 | 273.68 | 319.9162 | 457.5 | 436.1 | 410.6 | 382.2 | 757.3 | 61.7 | 17.9 | 105.2 | 8.9 | 249.6 | 16 | 916.8 | 762.1 | 752.5 | 810.3 | 697.8 | 786.9 | 744.1 | 748.6 | 728.2 | 735.8 | 323.7 | 407 | 444.4 | 356.3 | 446.7 | 419.2 | 425.5 | 406.9 | 563.7 | 420
1998 | 1804 | 683.8 | 273.52 | 319.7291 | 458.8 | 435.1 | 410.2 | 382.8 | 758.8 | 61.6 | 17.9 | 105.3 | 10.2 | 224.1 | 16.3 | 916.1 | 762.7 | 758.3 | 810.3 | 697.5 | 785.9 | 741.9 | 749.8 | 728.3 | 735.4 | 323.9 | 407.2 | 444.6 | 356.6 | 446.8 | 419.3 | 425.7 | 406.9 | 563.5 | 420.1
1999 | 1805 | 684.5 | 273.8 | 320.0564 | 461.1 | 433.6 | 409.8 | 383.1 | 761 | 61.6 | 17.9 | 105.2 | 10.4 | 266.6 | 13.3 | 916.1 | 763.1 | 764.5 | 810.2 | 696.4 | 785.8 | 743.5 | 747.7 | 728.4 | 735.4 | 324.3 | 407.5 | 444.7 | 356.8 | 447.1 | 419.3 | 425.9 | 406.9 | 563.2 | 420.2
2000 | 1806 | 684.5 | 273.8 | 320.0564 | 463.1 | 432.6 | 410.1 | 382.7 | 759.2 | 61.7 | 17.9 | 105.1 | 9.6 | 239.9 | 12.8 | 915.6 | 767 | 780 | 810.3 | 700 | 785.5 | 744.4 | 750.7 | 728.8 | 736.1 | 324.8 | 407.7 | 444.8 | 357.1 | 447.2 | 419.2 | 426 | 406.9 | 563 | 420.4
2001 | 1807 | 686.1 | 274.44 | 320.8045 | 463.1 | 432.6 | 410.6 | 383.1 | 752.3 | 61.7 | 17.9 | 105 | 7.6 | 250.4 | 15.7 | 915.4 | 769.5 | 771.4 | 810.4 | 700.5 | 786.4 | 742.6 | 753.7 | 728.9 | 737 | 325.2 | 408 | 444.6 | 357.3 | 447.3 | 419.1 | 426.1 | 407 | 563 | 420.5
2002 | 1808 | 685.4 | 274.16 | 320.4772 | 462.7 | 433.9 | 411.3 | 383.1 | 748.3 | 61.6 | 17.9 | 105 | 8.4 | 243.7 | 18.7 | 914.5 | 771.8 | 775.1 | 810.3 | 700.3 | 785.5 | 749 | 758.9 | 729.1 | 737.6 | 325.6 | 408.2 | 445 | 357.6 | 447.3 | 419.2 | 426.3 | 407 | 562.8 | 420.6
2003 | 1809 | 685 | 274 | 320.2902 | 461.9 | 434.4 | 411.4 | 382.9 | 741.3 | 61.6 | 17.9 | 105 | 7.8 | 248.4 | 18.4 | 915.4 | 775.8 | 782.3 | 810.4 | 703.5 | 784 | 757.9 | 763.8 | 729 | 739.9 | 325.8 | 408.4 | 444.7 | 357.9 | 447.2 | 419.3 | 426.2 | 407.1 | 562.6 | 420.7
2004 | 1810 | 685 | 274 | 320.2902 | 460.5 | 433.9 | 410.6 | 383.4 | 727.2 | 61.6 | 17.9 | 105.1 | 8.7 | 238.7 | 17 | 914.4 | 778.2 | 796.4 | 810.9 | 709 | 787.8 | 766.3 | 767 | 729.1 | 744.5 | 326.1 | 408.7 | 444.4 | 358.2 | 447 | 419.5 | 426.2 | 407.3 | 562.3 | 420.8
2005 | 1811 | 686.2 | 274.48 | 320.8513 | 459 | 432.4 | 409.3 | 382.7 | 724.6 | 61.5 | 17.9 | 105 | 8 | 240.1 | 14.7 | 915.8 | 780.4 | 802.3 | 811.3 | 712.1 | 790.2 | 774.8 | 772.4 | 729.1 | 747.8 | 326.3 | 408.9 | 444.4 | 358.4 | 446.7 | 419.3 | 426.1 | 407.3 | 562.3 | 420.9
2006 | 1812 | 686.5 | 274.6 | 320.9916 | 458 | 431.5 | 408.9 | 382.2 | 718 | 61.4 | 17.9 | 104.8 | 7.5 | 235.9 | 16 | 914.5 | 780.5 | 830.4 | 811.5 | 716.5 | 792.5 | 778.1 | 776.6 | 729 | 750.3 | 326.6 | 409 | 444.4 | 358.7 | 446.5 | 419.2 | 425.9 | 407.3 | 562.2 | 421
2007 | 1813 | 686.6 | 274.64 | 321.0383 | 457 | 431.3 | 408.4 | 381.1 | 726.6 | 61.3 | 17.9 | 104.7 | 8.7 | 238.7 | 18.1 | 912.2 | 780.4 | 835.9 | 811.6 | 717.9 | 792.8 | 781.4 | 778.4 | 729.2 | 750.9 | 326.8 | 409.2 | 444.8 | 359 | 446.4 | 419.1 | 425.8 | 407.3 | 562.5 | 421.1
2008 | 1814 | 686.7 | 274.68 | 321.0851 | 455.3 | 432.8 | 407.1 | 379.4 | 738.1 | 61.1 | 17.9 | 104.7 | 9.4 | 237.9 | 16.7 | 912.2 | 783.5 | 837.3 | 811.7 | 718.1 | 795.2 | 784.9 | 782.3 | 729.5 | 752.3 | 327 | 409.4 | 444.7 | 359.2 | 446.3 | 419.1 | 425.7 | 407.3 | 562.7 | 421.2
2009 | 1815 | 686.3 | 274.52 | 320.8981 | 454.6 | 432 | 406.4 | 379.2 | 748.3 | 61 | 17.9 | 104.9 | 9.6 | 238.8 | 15.8 | 911.7 | 785 | 837.2 | 811.8 | 720.2 | 800.5 | 787.1 | 784.4 | 730 | 753.7 | 327.4 | 409.6 | 445 | 359.5 | 446.6 | 419 | 425.8 | 407.3 | 562.9 | 421.3
2010 | 1816 | 685.8 | 274.32 | 320.6643 | 453.6 | 431.6 | 405.7 | 380.2 | 753.5 | 61 | 17.9 | 105 | 7.8 | 267 | 14 | 911.8 | 785.1 | 845.9 | 812 | 723.2 | 800.3 | 790.1 | 784.9 | 730.2 | 755.4 | 327.8 | 409.7 | 445 | 359.8 | 446.7 | 418.9 | 425.8 | 407.3 | 562.9 | 421.4
2011 | 1817 | 686.1 | 274.44 | 320.8045 | 452.8 | 431.6 | 405.9 | 380.4 | 753.7 | 61.1 | 17.9 | 104.9 | 7.6 | 244.3 | 13 | 912.3 | 788.1 | 833.4 | 812.3 | 722.9 | 801.6 | 791.3 | 788.9 | 730.3 | 756.6 | 328.2 | 409.9 | 445 | 360 | 446.6 | 418.9 | 425.8 | 407.3 | 562.9 | 421.5
2012 | 1818 | 686.1 | 274.44 | 320.8045 | 452.6 | 431.6 | 405.7 | 380.1 | 759 | 61.1 | 17.9 | 104.8 | 7.6 | 237.4 | 13.7 | 914.3 | 788.6 | 833.4 | 812.8 | 724 | 802.8 | 793 | 788.9 | 730.6 | 757.2 | 328.5 | 410 | 445.3 | 360.3 | 446.3 | 418.7 | 425.7 | 407.3 | 562.8 | 421.6
2013 | 1819 | 686.1 | 274.44 | 320.8045 | 452.6 | 431.2 | 405.7 | 380.3 | 764.1 | 60.9 | 17.9 | 104.8 | 6.8 | 238.7 | 13.6 | 916.6 | 786.1 | 828.3 | 813.2 | 722.8 | 802.7 | 781.1 | 781.4 | 730.9 | 754.4 | 328.8 | 410.2 | 446 | 360.6 | 446 | 418.5 | 425.7 | 407.3 | 562.6 | 421.7
2014 | 1820 | 685 | 274 | 320.2902 | 454 | 431 | 405.8 | 380.1 | 766.6 | 60.8 | 17.9 | 104.8 | 6.4 | 228.1 | 14.1 | 914 | 785.6 | 828 | 813.5 | 725 | 803.6 | 783.8 | 781.7 | 731.3 | 756.8 | 329.1 | 410.4 | 445.6 | 360.8 | 445.7 | 418.8 | 425.7 | 407.3 | 562.5 | 421.7
2015 | 1821 | 685.1 | 274.04 | 320.337 | 453.8 | 430.9 | 405.9 | 379.2 | 773.9 | 60.8 | 17.9 | 104.8 | 6.4 | 248.6 | 12.7 | 913.7 | 783.9 | 833.9 | 813.6 | 725 | 801.2 | 794.1 | 786.1 | 731.9 | 758.8 | 329.3 | 410.5 | 445.7 | 361.1 | 445.9 | 419.2 | 425.8 | 407.3 | 562.5 | 421.8
2016 | 1822 | 685.4 | 274.16 | 320.4772 | 452.5 | 430.5 | 405.6 | 379.8 | 778.5 | 60.8 | 17.9 | 105 | 6.8 | 237.8 | 11.6 | 912.5 | 785 | 843 | 813.7 | 726.5 | 804.9 | 795.9 | 788.8 | 732.2 | 758.6 | 329.7 | 410.6 | 446 | 361.3 | 446.3 | 419.6 | 426 | 407.4 | 562.9 | 422
2017 | 1823 | 685.3 | 274.12 | 320.4305 | 452.3 | 429.8 | 405.3 | 380.3 | 771.9 | 61 | 17.9 | 105.3 | 6.9 | 230.3 | 10.8 | 914.2 | 785.2 | 844.1 | 814 | 726.7 | 804.8 | 794 | 787 | 732.7 | 760.4 | 329.9 | 410.7 | 446.2 | 361.6 | 446.5 | 419.9 | 426.2 | 407.4 | 563 | 422.1
2018 | 1824 | 685.3 | 274.12 | 320.4305 | 451.6 | 430.5 | 405.4 | 380.5 | 772.7 | 61.1 | 17.9 | 105.5 | 7.2 | 240.3 | 10.8 | 921.1 | 782.2 | 837 | 814.4 | 725 | 804.1 | 781.6 | 784.1 | 732.9 | 756.4 | 330 | 410.8 | 447.4 | 361.8 | 446.6 | 420.2 | 426.3 | 407.4 | 563.2 | 422.2
2019 | 1825 | 685.7 | 274.28 | 320.6175 | 451.7 | 431.7 | 406.2 | 380.8 | 764.6 | 61.3 | 17.9 | 105.5 | 7.2 | 241.1 | 11 | 920.6 | 780.4 | 841.5 | 814.6 | 725.9 | 804.9 | 776.8 | 780.8 | 733.3 | 757.1 | 330.2 | 411 | 447.2 | 362.1 | 446.5 | 420.2 | 426.3 | 407.3 | 563.2 | 422.3
2020 | 1826 | 685.3 | 274.12 | 320.4305 | 450.7 | 432.5 | 407.4 | 380.7 | 778.9 | 61.4 | 17.9 | 105.3 | 6.1 | 245.1 | 10.6 | 916.3 | 779.6 | 851.2 | 814.7 | 728.1 | 806 | 784.1 | 781.4 | 733.8 | 760.2 | 330.4 | 411.1 | 447.1 | 362.3 | 446.4 | 420.3 | 426.4 | 407.4 | 563.2 | 422.4
2021 | 1827 | 685.4 | 274.16 | 320.4772 | 449.3 | 432.7 | 407.7 | 380.2 | 781.8 | 61.5 | 17.9 | 105.1 | 6.1 | 254.3 | 9.1 | 920.2 | 778.1 | 822.6 | 814.8 | 723 | 803.5 | 784.3 | 779 | 734 | 757.9 | 330.6 | 411.2 | 447.3 | 362.6 | 446.5 | 420.4 | 426.7 | 407.4 | 563.5 | 422.5
2022 | 1828 | 685.1 | 274.04 | 320.337 | 448.7 | 432 | 408.3 | 379.8 | 763.6 | 61.6 | 17.9 | 105.1 | 6 | 249.4 | 10 | 923 | 769.8 | 783.3 | 815.1 | 718.2 | 794.4 | 770 | 759.2 | 733.6 | 752.1 | 330.8 | 411.3 | 447.2 | 362.8 | 446.7 | 420.4 | 426.9 | 407.4 | 563.4 | 422.7
2023 | 1829 | 685.3 | 274.12 | 320.4305 | 449.3 | 430.8 | 408.9 | 380.1 | 733.5 | 61.7 | 17.9 | 105.2 | 5.8 | 245.1 | 12 | 922.7 | 762.1 | 750.2 | 815.2 | 715.2 | 779.7 | 753.5 | 737.3 | 732.9 | 747.5 | 331 | 411.4 | 447.2 | 363.1 | 446.9 | 420.3 | 427.1 | 407.4 | 563 | 422.8
2024 | 1830 | 685.3 | 274.12 | 320.4305 | 449.9 | 429.3 | 408.6 | 380.1 | 708.7 | 61.8 | 17.9 | 105.3 | 5.6 | 245.6 | 11.9 | 921.7 | 763.4 | 758.9 | 815.8 | 716.4 | 780.8 | 749.6 | 734.5 | 732.6 | 746 | 331.5 | 411.5 | 447.1 | 363.3 | 447.1 | 420.2 | 427.2 | 407.5 | 562.4 | 422.9
2025 | 1831 | 685.6 | 274.24 | 320.5708 | 450.2 | 428.1 | 408.6 | 381 | 717.2 | 61.9 | 17.9 | 105.4 | 5.5 | 226.8 | 10.7 | 920.4 | 766.2 | 762.6 | 816.3 | 715.6 | 784.3 | 754 | 743.6 | 732.8 | 747.6 | 331.7 | 411.7 | 447.1 | 363.6 | 447.3 | 420.3 | 427.3 | 407.5 | 562 | 423
2026 | 1832 | 685.7 | 274.28 | 320.6175 | 450.1 | 427.1 | 408.5 | 382.5 | 706.9 | 62 | 17.9 | 105.3 | 5.3 | 247.9 | 9.9 | 919.5 | 765.1 | 768.4 | 816.7 | 714.7 | 782.8 | 753.7 | 747.8 | 732.5 | 745.6 | 332 | 411.8 | 447 | 363.8 | 447.4 | 420.5 | 427.3 | 407.7 | 561.7 | 423.1
2027 | 1833 | 685.8 | 274.32 | 320.6643 | 449.6 | 426.2 | 407.7 | 383.3 | 709.8 | 62.1 | 17.9 | 105.3 | 5.4 | 253.1 | 9.4 | 918.7 | 769.6 | 785.1 | 816.9 | 715.8 | 791.9 | 761.8 | 756.7 | 732.9 | 748 | 332.1 | 412 | 447 | 364 | 447.1 | 420.6 | 427.3 | 407.7 | 561.4 | 423.2
2028 | 1834 | 685.6 | 274.24 | 320.5708 | 449.3 | 425.4 | 406.5 | 383.5 | 726.5 | 62 | 17.9 | 105.2 | 4.8 | 245.1 | 9.6 | 916.6 | 772.4 | 795.4 | 817 | 716.2 | 795.6 | 769.2 | 760.5 | 733.2 | 749.2 | 332.3 | 412.1 | 447.2 | 364.3 | 447.1 | 420.3 | 427.3 | 407.7 | 561.2 | 423.3
2029 | 1835 | 685.8 | 274.32 | 320.6643 | 448.8 | 424.8 | 406.1 | 383 | 734.5 | 62 | 17.9 | 105.2 | 5 | 252.2 | 8.3 | 914.8 | 774.9 | 819.4 | 817.1 | 720 | 796.7 | 780.9 | 768.5 | 733.5 | 753.1 | 332.6 | 412.3 | 447.1 | 364.5 | 447 | 420 | 427.3 | 407.7 | 561.1 | 423.4
2030 | 1836 | 686.2 | 274.48 | 320.8513 | 446.9 | 424.5 | 406.4 | 382.5 | 727.6 | 62.1 | 17.9 | 105.3 | 4.9 | 245.7 | 8.7 | 915.9 | 776.3 | 827.5 | 817.3 | 720.4 | 797 | 782.5 | 774.4 | 733.9 | 754 | 332.8 | 412.5 | 447.3 | 364.8 | 447 | 419.9 | 427.2 | 407.7 | 561.3 | 423.5
2031 | 1837 | 685.6 | 274.24 | 320.5708 | 445 | 424.6 | 406.1 | 381.6 | 737 | 62.1 | 17.9 | 105.5 | 5 | 233.8 | 8.8 | 915.3 | 777.5 | 828.7 | 817.5 | 721.9 | 798.9 | 789 | 778.7 | 734.2 | 756.4 | 333 | 412.7 | 447.4 | 365 | 447 | 419.7 | 427.1 | 407.7 | 561.5 | 423.6
2032 | 1838 | 685.9 | 274.36 | 320.711 | 443.8 | 424.7 | 407 | 380.6 | 745.4 | 62.1 | 17.9 | 105.7 | 5.6 | 228 | 8.7 | 914.2 | 778.8 | 817.3 | 817.6 | 723.3 | 802 | 798.2 | 781.1 | 734.7 | 758.7 | 333.2 | 412.9 | 447.3 | 365.2 | 447.1 | 419.7 | 427.1 | 407.8 | 561.5 | 423.7
2033 | 1839 | 686.2 | 274.48 | 320.8513 | 443.2 | 424.5 | 406.7 | 379.9 | 747 | 62 | 17.9 | 105.8 | 5.6 | 232 | 7.6 | 914.7 | 781.4 | 822.6 | 817.5 | 723.5 | 803.1 | 798.7 | 785.9 | 734.9 | 757.1 | 333.4 | 413 | 447.4 | 365.5 | 447.3 | 419.6 | 427.1 | 407.7 | 561.6 | 423.8
2034 | 1840 | 686 | 274.4 | 320.7578 | 442.8 | 424.4 | 406.2 | 379.8 | 760.7 | 61.9 | 17.9 | 105.9 | 6 | 233 | 7.6 | 919.1 | 779 | 797.6 | 817.5 | 720 | 800.7 | 787.9 | 776.2 | 735.3 | 755.1 | 333.6 | 413.2 | 448 | 365.7 | 447.2 | 419.6 | 427.2 | 407.7 | 561.5 | 423.8
2035 | 1841 | 686 | 274.4 | 320.7578 | 443.2 | 424.3 | 406.8 | 379.9 | 741.4 | 62 | 17.9 | 105.8 | 6 | 240.7 | 6.9 | 922.6 | 769.5 | 776.8 | 817.7 | 716.1 | 785.1 | 768.6 | 747.1 | 734.9 | 749.3 | 334 | 413.4 | 448.2 | 365.9 | 447.2 | 419.5 | 427.4 | 407.7 | 561.3 | 423.9
2036 | 1842 | 685.4 | 274.16 | 320.4772 | 444.1 | 424.1 | 407 | 380.9 | 724.2 | 62.1 | 17.9 | 105.7 | 6.4 | 280 | 6.7 | 921.5 | 763.8 | 755.6 | 817.9 | 713.6 | 778.1 | 754.4 | 730.3 | 734.7 | 745.2 | 334.2 | 413.6 | 448.6 | 366.2 | 447.3 | 419.5 | 427.5 | 407.7 | 560.9 | 424
2037 | 1843 | 684.8 | 273.92 | 320.1967 | 444.2 | 424 | 407.3 | 381 | 713.1 | 62.2 | 17.9 | 105.9 | 6.2 | 253.6 | 7.3 | 920.4 | 758.4 | 737.3 | 818.1 | 709.8 | 772.5 | 744.7 | 717.4 | 734.2 | 741.7 | 334.4 | 413.7 | 448.1 | 366.4 | 447.5 | 419.5 | 427.6 | 407.7 | 560.5 | 424.1
2038 | 1844 | 685.6 | 274.24 | 320.5708 | 444.7 | 423.1 | 407 | 380.9 | 681.7 | 62.2 | 17.9 | 106.3 | 6.1 | 239.3 | 7.1 | 919.4 | 752.5 | 722 | 818.1 | 706.2 | 761.9 | 732.8 | 702.5 | 733.5 | 737.6 | 334.7 | 413.8 | 447.7 | 366.6 | 447.6 | 419.5 | 427.6 | 407.8 | 560 | 424.2
2039 | 1845 | 686.3 | 274.52 | 320.8981 | 446.1 | 422.1 | 406.5 | 379.7 | 652.7 | 62.1 | 17.9 | 106.5 | 6.4 | 247.2 | 7.4 | 918.6 | 748.1 | 704.6 | 818.4 | 703.7 | 758 | 723.4 | 698.2 | 733.2 | 734.5 | 334.9 | 413.9 | 447.6 | 366.9 | 447.7 | 419.4 | 427.7 | 407.8 | 559.5 | 424.3
2040 | 1846 | 685.3 | 274.12 | 320.4305 | 446.5 | 421.1 | 405.4 | 379.8 | 654.5 | 62.1 | 17.9 | 106.6 | 6.4 | 245.7 | 9.6 | 917.5 | 750.9 | 707.2 | 818.7 | 702.4 | 764.5 | 721.6 | 701.2 | 733.2 | 732.2 | 335.2 | 414 | 447.9 | 367.1 | 447.8 | 419.2 | 427.9 | 407.7 | 559 | 424.4
2041 | 1847 | 685.9 | 274.36 | 320.711 | 446.3 | 420.7 | 404 | 380.5 | 676.5 | 62.2 | 17.9 | 106.5 | 7.2 | 249.8 | 9.3 | 916.8 | 757 | 741.3 | 818.8 | 704.7 | 777.6 | 731.3 | 720.8 | 733.9 | 733.6 | 335.5 | 414.2 | 448.4 | 367.3 | 448.1 | 419.2 | 428.1 | 407.7 | 558.6 | 424.5
2042 | 1848 | 686.3 | 274.52 | 320.8981 | 445.8 | 420.8 | 403.9 | 381.6 | 703.5 | 62.3 | 17.9 | 106.5 | 7.6 | 244.2 | 8.8 | 916.2 | 760.3 | 771.3 | 819.1 | 707.7 | 784.2 | 740.7 | 729.4 | 734.8 | 736.4 | 335.7 | 414.4 | 448.3 | 367.6 | 448.2 | 419 | 428.2 | 407.7 | 558.4 | 424.7
2043 | 1849 | 685.7 | 274.28 | 320.6175 | 444.8 | 420.6 | 404.8 | 382.2 | 716.8 | 62.3 | 17.9 | 106.5 | 7.3 | 266.5 | 9.6 | 912.2 | 764.6 | 784.2 | 819 | 709.8 | 788.6 | 757.9 | 743.3 | 735.3 | 740 | 336 | 414.5 | 448.1 | 367.8 | 448.3 | 419.1 | 428.2 | 407.8 | 558.6 | 424.8
2044 | 1850 | 686.7 | 274.68 | 321.0851 | 443.6 | 420.5 | 405.5 | 382.1 | 734.8 | 62.3 | 17.9 | 106.5 | 7.2 | 258.8 | 12.3 | 911.7 | 766.6 | 808.7 | 819 | 713.8 | 791.7 | 770.4 | 754.7 | 736 | 742.5 | 336.2 | 414.7 | 448.5 | 368 | 448.6 | 419.2 | 428.3 | 407.8 | 559 | 424.9
2045 | 1851 | 686.5 | 274.6 | 320.9916 | 442.7 | 421.6 | 405.9 | 382 | 746.3 | 62.2 | 17.9 | 106.5 | 8 | 246.8 | 11.1 | 909 | 766.7 | 819.9 | 818.8 | 717.5 | 792.1 | 776.6 | 757.8 | 736.4 | 745.4 | 336.5 | 414.9 | 448.5 | 368.3 | 448.7 | 419.2 | 428.4 | 407.8 | 559.3 | 425
2046 | 1852 | 686.7 | 274.68 | 321.0851 | 441.9 | 422.6 | 406.9 | 381.8 | 748.1 | 62.2 | 17.9 | 106.3 | 7.3 | 207.6 | 9 | 906.4 | 766.8 | 838 | 818.4 | 719.8 | 791.7 | 785.8 | 765.6 | 736.5 | 749.4 | 337 | 415 | 448.3 | 368.5 | 448.8 | 419.2 | 428.5 | 407.8 | 559.8 | 425.1
2047 | 1853 | 686.4 | 274.56 | 320.9448 | 441.2 | 422.7 | 408.1 | 381.5 | 746.1 | 62.2 | 17.9 | 106 | 7.6 | 265.8 | 8 | 903.5 | 767.2 | 850.2 | 818 | 722.5 | 797 | 793.7 | 772.6 | 736.5 | 752.6 | 337.2 | 415.1 | 448.5 | 368.7 | 448.9 | 419.4 | 428.7 | 407.8 | 560.4 | 425.2
2048 | 1854 | 686.6 | 274.64 | 321.0383 | 440.5 | 422.6 | 407.4 | 380.9 | 748.1 | 62.2 | 17.9 | 105.8 | 7.8 | 243.5 | 8.7 | 902.9 | 770.1 | 847.2 | 817.6 | 723.7 | 796.6 | 799.6 | 774 | 736.8 | 753.8 | 337.4 | 415.2 | 448.7 | 369 | 449.1 | 419.8 | 428.9 | 407.9 | 561 | 425.3
2049 | 1855 | 686.2 | 274.48 | 320.8513 | 440.3 | 422.5 | 407.4 | 381 | 761 | 62.3 | 17.9 | 105.9 | 7.5 | 249.3 | 10.4 | 901.8 | 771.3 | 844.1 | 817.3 | 724.5 | 799.5 | 800.8 | 776.4 | 737.4 | 755.3 | 337.6 | 415.4 | 449 | 369.2 | 449.3 | 420.1 | 429.2 | 408 | 561.4 | 425.4
2050 | 1856 | 685 | 274 | 320.2902 | 440.4 | 423.4 | 408.4 | 381.3 | 768 | 62.3 | 17.9 | 105.9 | 7.9 | 243.5 | 10.5 | 900.8 | 773.4 | 853.6 | 817 | 727.2 | 800.9 | 806.2 | 778.7 | 738 | 757.8 | 338 | 415.5 | 448.9 | 369.4 | 449.2 | 420.4 | 429.3 | 408.1 | 561.5 | 425.5
2051 | 1857 | 686.5 | 274.6 | 320.9916 | 440.5 | 424.2 | 409.1 | 381.4 | 773.7 | 62.4 | 17.9 | 106 | 9.1 | 251.8 | 11 | 901.8 | 773.9 | 857 | 816.8 | 727.7 | 800.4 | 803.5 | 781.5 | 738.5 | 758.4 | 338.1 | 415.6 | 449.3 | 369.6 | 449.1 | 420.7 | 429.4 | 408.1 | 561.6 | 425.6
2052 | 1858 | 685.7 | 274.28 | 320.6175 | 440.3 | 426.1 | 409.3 | 381.5 | 775.6 | 62.4 | 17.9 | 106.1 | 9.1 | 281.3 | 10.5 | 903.5 | 776.1 | 849.4 | 816.8 | 728.8 | 803.7 | 792 | 787.2 | 739 | 757.1 | 338.3 | 415.7 | 449.7 | 369.8 | 449 | 420.9 | 429.6 | 408.1 | 562 | 425.7
2053 | 1859 | 685.9 | 274.36 | 320.711 | 440.3 | 426.9 | 410 | 381.9 | 779.4 | 62.5 | 17.9 | 106.1 | 7.8 | 258.1 | 10.4 | 903.6 | 775.7 | 854.4 | 816.7 | 731.2 | 804.4 | 791.1 | 786.6 | 739.5 | 759.3 | 338.6 | 415.9 | 449.8 | 370 | 449.1 | 420.9 | 429.6 | 408.1 | 562.2 | 425.8
2054 | 1860 | 686.5 | 274.6 | 320.9916 | 439.8 | 427.2 | 410.8 | 382 | 784.4 | 62.5 | 17.9 | 106 | 7.9 | 255.2 | 12.6 | 906.3 | 776.9 | 847.3 | 816.7 | 732 | 805.3 | 792.6 | 789.5 | 740.1 | 759.7 | 338.8 | 416 | 449.9 | 370.2 | 449.4 | 421.1 | 429.8 | 408.2 | 562.5 | 425.9
2055 | 1861 | 686.6 | 274.64 | 321.0383 | 439.4 | 428 | 411.3 | 382.2 | 789.2 | 62.6 | 17.9 | 105.8 | 9.2 | 252.2 | 12.8 | 907.7 | 778.7 | 825.1 | 816.8 | 728.4 | 808.9 | 790.1 | 794.1 | 740.4 | 758.7 | 339 | 416.2 | 450.4 | 370.4 | 449.5 | 421.3 | 430.1 | 408.2 | 563 | 426.1
2056 | 1862 | 686.7 | 274.68 | 321.0851 | 439.4 | 428.3 | 412.3 | 383.2 | 788.5 | 62.8 | 17.9 | 105.5 | 9.8 | 253 | 14.7 | 909.1 | 779.7 | 791 | 816.7 | 725.4 | 811.7 | 786.9 | 801.2 | 740.6 | 757.5 | 339.2 | 416.4 | 450.3 | 370.6 | 449.7 | 421.3 | 430.3 | 408.3 | 562.9 | 426.2
2057 | 1863 | 686.3 | 274.52 | 320.8981 | 439.9 | 428.3 | 412.4 | 383.2 | 770.6 | 62.9 | 17.9 | 105.4 | 8.1 | 251.8 | 14.1 | 911 | 774.3 | 788.4 | 816.7 | 724.5 | 814 | 783.2 | 793.1 | 740.5 | 755.2 | 339.5 | 416.5 | 450.4 | 370.8 | 450 | 421.4 | 430.6 | 408.4 | 562.7 | 426.3
2058 | 1864 | 686.1 | 274.44 | 320.8045 | 440.7 | 428 | 413 | 383 | 770.8 | 63.1 | 17.9 | 105.4 | 8.6 | 240.8 | 13.2 | 913.3 | 772.1 | 785.7 | 817.1 | 723.8 | 815.7 | 780.1 | 783.3 | 740.9 | 754.6 | 339.8 | 416.6 | 450.7 | 371 | 450.3 | 421.5 | 430.8 | 408.4 | 562.3 | 426.4
2059 | 1865 | 686.4 | 274.56 | 320.9448 | 441.4 | 427.7 | 412.9 | 383.6 | 770.5 | 63.1 | 17.9 | 105.3 | 9 | 220.7 | 12.4 | 915.1 | 771.3 | 790.8 | 817.5 | 722.9 | 814.7 | 775.5 | 779.7 | 741.3 | 753 | 340 | 416.8 | 450.9 | 371.2 | 450.7 | 421.5 | 431 | 408.5 | 562.1 | 426.6
2060 | 1866 | 686.1 | 274.44 | 320.8045 | 441.6 | 427.4 | 413.1 | 384 | 771.1 | 63.1 | 17.9 | 105.1 | 7.6 | 217.3 | 13.2 | 915.7 | 770.1 | 794 | 817.9 | 721.6 | 816.3 | 773 | 778.5 | 741.5 | 753.1 | 340.4 | 416.9 | 450.8 | 371.5 | 450.8 | 421.5 | 431.2 | 408.5 | 561.9 | 426.7
2061 | 1867 | 686.6 | 274.64 | 321.0383 | 441.9 | 427.2 | 413.8 | 384.4 | 773.8 | 63.1 | 17.9 | 105 | 6.2 | 235.8 | 10.3 | 914.1 | 772.6 | 797.5 | 818.4 | 723.9 | 816.2 | 772.7 | 780.5 | 741.9 | 754.6 | 340.5 | 417 | 451 | 371.7 | 451.1 | 421.5 | 431.3 | 408.5 | 561.7 | 426.8
2062 | 1868 | 686.8 | 274.72 | 321.1319 | 441.8 | 427.2 | 413.8 | 384.4 | 777.5 | 63.1 | 17.9 | 104.9 | 7.5 | 226 | 10.1 | 916.3 | 771.9 | 794.7 | 818.9 | 723.3 | 814.2 | 775.2 | 784 | 742.2 | 755.7 | 340.7 | 417.2 | 451.1 | 371.9 | 451.1 | 421.6 | 431.5 | 408.6 | 561.6 | 426.9
2063 | 1869 | 687.2 | 274.88 | 321.3189 | 441.9 | 427.1 | 413.9 | 384.4 | 779 | 63 | 17.9 | 105 | 6.4 | 239.7 | 12.2 | 915.6 | 770.1 | 772.9 | 819.1 | 720.8 | 813.2 | 773.4 | 784.3 | 742.5 | 754.5 | 340.9 | 417.3 | 451.1 | 372.1 | 451.2 | 421.7 | 431.6 | 408.6 | 561.5 | 427
2064 | 1870 | 686.2 | 274.48 | 320.8513 | 442.4 | 427 | 413.8 | 384.2 | 764.4 | 63 | 17.9 | 105 | 5.5 | 258.5 | 11.9 | 916.9 | 762.9 | 733.7 | 819.2 | 716.4 | 803.9 | 767.1 | 762.3 | 742.1 | 749.5 | 341.1 | 417.5 | 451.2 | 372.3 | 451.5 | 421.8 | 431.7 | 408.6 | 561.3 | 427.1
2065 | 1871 | 683.8 | 273.52 | 319.7291 | 443.6 | 426.2 | 413.4 | 384.2 | 735.5 | 63 | 17.9 | 105 | 5.2 | 262.4 | 12.3 | 916.9 | 756.7 | 705.4 | 819.4 | 711.5 | 788.3 | 754.3 | 741.6 | 741.3 | 745.2 | 341.4 | 417.6 | 451 | 372.5 | 451.8 | 421.9 | 431.9 | 408.7 | 560.9 | 427.2
2066 | 1872 | 686.2 | 274.48 | 320.8513 | 446.4 | 425.1 | 413.4 | 384 | 711.5 | 63.1 | 17.9 | 105.1 | 5.2 | 264.6 | 12.3 | 916.2 | 751.8 | 692.3 | 819.4 | 707.9 | 779.7 | 743.6 | 731.2 | 740.8 | 741.9 | 341.7 | 417.7 | 451.2 | 372.8 | 452.2 | 421.8 | 432 | 408.6 | 560.4 | 427.3
2067 | 1873 | 685.4 | 274.16 | 320.4772 | 447.9 | 424 | 412.4 | 383.7 | 704.9 | 63.1 | 17.9 | 105.1 | 5.2 | 242.1 | 11.5 | 914.8 | 752.2 | 694.2 | 819.6 | 705.5 | 784.9 | 738.3 | 732.3 | 740.6 | 740.6 | 342.1 | 417.7 | 451.2 | 372.9 | 452.4 | 421.5 | 432.1 | 408.6 | 560 | 427.4
2068 | 1874 | 685.4 | 274.16 | 320.4772 | 448 | 423.1 | 412 | 383.6 | 698.7 | 63.2 | 17.9 | 105.1 | 6.1 | 272 | 11.4 | 913.5 | 758.2 | 715.1 | 820.1 | 707.6 | 788.3 | 749 | 748.5 | 740.8 | 745.4 | 342.3 | 417.7 | 450.9 | 373.2 | 452.3 | 421.6 | 432.1 | 408.7 | 559.6 | 427.5
2069 | 1875 | 685.6 | 274.24 | 320.5708 | 447.1 | 422.6 | 412.1 | 383.9 | 706.5 | 63.2 | 17.9 | 105.1 | 6.3 | 258.2 | 12.3 | 913.1 | 759.1 | 706 | 820.3 | 705.4 | 792.3 | 761.5 | 755.4 | 741 | 744 | 342.6 | 417.7 | 451 | 373.4 | 452.1 | 421.6 | 432.1 | 408.7 | 559.3 | 427.6
2070 | 1876 | 685.2 | 274.08 | 320.3837 | 446.5 | 422.1 | 412.1 | 384.2 | 701.9 | 63.2 | 17.9 | 105.2 | 6.9 | 260 | 10.6 | 912.7 | 760.9 | 699.6 | 820.2 | 704 | 794 | 770.7 | 757.1 | 741.4 | 744 | 342.8 | 417.8 | 451.2 | 373.6 | 451.9 | 421.1 | 432 | 408.7 | 559.1 | 427.7
2071 | 1877 | 685.1 | 274.04 | 320.337 | 446.6 | 421.9 | 411.3 | 383.8 | 700.6 | 63.3 | 17.9 | 105.3 | 7.1 | 282.4 | 9.1 | 912.2 | 760.2 | 717.6 | 820.3 | 703.2 | 797.8 | 769.8 | 755.9 | 741.7 | 742.3 | 343.1 | 418 | 451.2 | 373.8 | 451.7 | 420.6 | 432 | 408.6 | 558.9 | 427.8
2072 | 1878 | 684.6 | 273.84 | 320.1032 | 447.2 | 422 | 410.9 | 383.7 | 704.5 | 63.3 | 17.9 | 105.3 | 7.2 | 286.2 | 8.9 | 911.9 | 762.9 | 728.3 | 820.3 | 703.7 | 801.2 | 769.2 | 758.4 | 742.4 | 744.2 | 343.4 | 418.1 | 451.4 | 374 | 451.9 | 420.4 | 432 | 408.6 | 558.7 | 427.9
2073 | 1879 | 685.3 | 274.12 | 320.4305 | 448.2 | 422.2 | 411.5 | 383.6 | 703.4 | 63.3 | 17.9 | 105.5 | 7.6 | 266.1 | 9.2 | 912 | 759.9 | 727.7 | 820 | 703.5 | 800.1 | 767.9 | 757.6 | 742.5 | 741.9 | 343.7 | 418.2 | 451.6 | 374.2 | 452.2 | 420.3 | 432.1 | 408.6 | 558.7 | 428
2074 | 1880 | 685.5 | 274.2 | 320.524 | 448.3 | 422 | 413.4 | 384.1 | 707.4 | 63.4 | 17.9 | 105.5 | 7.2 | 238.4 | 8.4 | 912.1 | 758.7 | 732 | 819.7 | 703 | 805 | 762.4 | 758 | 743.1 | 741.1 | 343.9 | 418.3 | 451.7 | 374.3 | 452.4 | 420.4 | 432.2 | 408.7 | 558.4 | 428.1
2075 | 1881 | 685.3 | 274.12 | 320.4305 | 447.9 | 421.5 | 413.9 | 384.3 | 720.8 | 63.5 | 17.9 | 105.6 | 8.1 | 269.5 | 8 | 912.1 | 764 | 763.4 | 819.9 | 707.7 | 806.8 | 766.7 | 766.3 | 743.8 | 744.3 | 344 | 418.5 | 451.8 | 374.5 | 452.5 | 420.6 | 432.3 | 408.7 | 558.2 | 428.3
2076 | 1882 | 686.3 | 274.52 | 320.8981 | 447.3 | 421.5 | 415 | 385.1 | 733.8 | 63.6 | 17.9 | 105.6 | 7 | 257.8 | 8.6 | 909.4 | 766.6 | 785.5 | 820 | 711.2 | 809.6 | 770.9 | 771.1 | 744.4 | 747.5 | 344.2 | 418.6 | 451.5 | 374.7 | 452.4 | 420.9 | 432.5 | 408.8 | 558.1 | 428.3
2077 | 1883 | 686.1 | 274.44 | 320.8045 | 446.8 | 422 | 415 | 384.9 | 744.9 | 63.7 | 17.9 | 105.5 | 5.8 | 261.5 | 10 | 908.6 | 768.7 | 793.9 | 819.9 | 713.4 | 809.9 | 777.8 | 773.2 | 744.7 | 749.3 | 344.4 | 418.7 | 451.9 | 374.9 | 452.5 | 421.1 | 432.7 | 408.8 | 558.5 | 428.5
2078 | 1884 | 686.2 | 274.48 | 320.8513 | 446.3 | 422.6 | 414.2 | 385 | 750.8 | 63.6 | 17.9 | 105.3 | 6.4 | 252.3 | 10.3 | 909.9 | 773.4 | 783 | 820 | 712.8 | 809.9 | 783 | 781.3 | 744.8 | 751.6 | 344.6 | 418.8 | 452 | 375.1 | 452.7 | 421.1 | 432.8 | 408.9 | 559 | 428.6
2079 | 1885 | 686.5 | 274.6 | 320.9916 | 446.3 | 422.7 | 414.2 | 385.1 | 742 | 63.5 | 17.9 | 105.4 | 5.5 | 259.3 | 11.5 | 909.3 | 776.3 | 784.5 | 820 | 712.6 | 812.4 | 786.3 | 793.1 | 745.1 | 751.6 | 344.8 | 418.8 | 451.9 | 375.3 | 453 | 421.1 | 432.8 | 408.9 | 558.9 | 428.7
2080 | 1886 | 686.6 | 274.64 | 321.0383 | 446.1 | 423.1 | 413.9 | 384.8 | 749.3 | 63.4 | 17.9 | 105.4 | 6.6 | 235.6 | 12.9 | 909.3 | 775.2 | 798.6 | 820 | 713.4 | 813.9 | 786.5 | 796.5 | 745.7 | 751.8 | 345 | 418.9 | 452.3 | 375.5 | 453.2 | 421 | 432.9 | 408.9 | 558.8 | 428.8
2081 | 1887 | 686.1 | 274.44 | 320.8045 | 445.5 | 423.6 | 413.4 | 384.5 | 756.8 | 63.4 | 17.9 | 105.4 | 8 | 228.5 | 12.2 | 912.3 | 774.8 | 811.6 | 820.1 | 716 | 813.7 | 787.5 | 792.8 | 746.3 | 753.7 | 345.2 | 419 | 452.3 | 375.7 | 453.5 | 420.9 | 433.2 | 408.9 | 558.8 | 428.9
2082 | 1888 | 686.3 | 274.52 | 320.8981 | 445.1 | 424.5 | 413.6 | 384.6 | 765.8 | 63.3 | 17.9 | 105.6 | 8.5 | 237.3 | 12.3 | 915.7 | 777.9 | 821.7 | 820.6 | 717.2 | 816.6 | 786.9 | 796.4 | 746.8 | 754.6 | 345.5 | 419.1 | 452.5 | 375.9 | 453.5 | 420.8 | 433.4 | 408.9 | 558.9 | 429
2083 | 1889 | 686.6 | 274.64 | 321.0383 | 444.9 | 425.6 | 414 | 384.6 | 764.7 | 63.2 | 17.8 | 106 | 9.8 | 237.6 | 10.3 | 916.7 | 778.6 | 831.5 | 821.1 | 719.1 | 816.9 | 780.2 | 799.1 | 747.3 | 754.8 | 345.8 | 419.2 | 453 | 376.1 | 453.6 | 420.8 | 433.4 | 408.9 | 559.1 | 429.1
2084 | 1890 | 687 | 274.8 | 321.2254 | 445 | 426.7 | 414 | 385 | 759.5 | 63.2 | 17.8 | 106.1 | 10.6 | 244.5 | 9.7 | 917.4 | 775.2 | 828.9 | 821.3 | 717.4 | 813.1 | 765.3 | 790.4 | 747.6 | 751.3 | 346 | 419.3 | 453.4 | 376.3 | 453.5 | 421.1 | 433.4 | 409 | 559.3 | 429.1
2085 | 1891 | 685.8 | 274.32 | 320.6643 | 445.3 | 427.9 | 414.9 | 384.8 | 763 | 63.2 | 17.8 | 106.1 | 8.9 | 231.7 | 9.9 | 916.8 | 774.8 | 826.8 | 821.4 | 720.2 | 815.1 | 758.2 | 786.3 | 747.9 | 751.3 | 346.2 | 419.4 | 453.7 | 376.4 | 453.3 | 421.2 | 433.3 | 408.9 | 559.5 | 429.2
2086 | 1892 | 686 | 274.4 | 320.7578 | 445.5 | 429 | 415.1 | 384.9 | 759.9 | 63.3 | 17.9 | 106 | 7.9 | 255.6 | 8.9 | 916.9 | 775.3 | 835.9 | 821.5 | 719.8 | 813.1 | 758.9 | 782.4 | 748.5 | 753 | 346.4 | 419.6 | 453.7 | 376.6 | 453.2 | 421.4 | 433.5 | 408.9 | 559.6 | 429.3
2087 | 1893 | 685.9 | 274.36 | 320.711 | 445.5 | 430 | 415.3 | 384.9 | 757 | 63.3 | 17.9 | 106.2 | 8.4 | 246.8 | 10 | 918.3 | 773 | 844.4 | 821.7 | 719.3 | 811.4 | 749.9 | 776.4 | 748.9 | 749.9 | 346.6 | 419.7 | 454 | 376.8 | 453.2 | 421.5 | 433.7 | 408.9 | 559.7 | 429.4
2088 | 1894 | 686 | 274.4 | 320.7578 | 445.5 | 430.9 | 416.1 | 384.7 | 766.9 | 63.4 | 17.9 | 106.2 | 7.4 | 242.1 | 13.4 | 918.6 | 772.4 | 851.5 | 821.8 | 721.8 | 815.3 | 745.3 | 778.4 | 749.5 | 750.9 | 346.8 | 419.8 | 454.5 | 377 | 452.9 | 421.4 | 433.8 | 409 | 559.8 | 429.6
2089 | 1895 | 686.1 | 274.44 | 320.8045 | 445.7 | 431.8 | 417.5 | 384.8 | 771.4 | 63.4 | 17.9 | 106.1 | 7.9 | 242.2 | 16.5 | 919.8 | 768.4 | 816.7 | 822 | 716.7 | 811.7 | 741.5 | 772.1 | 749.9 | 748.7 | 347.1 | 419.9 | 454.7 | 377.2 | 452.6 | 421.7 | 433.9 | 409 | 560.1 | 429.7
2090 | 1896 | 686.4 | 274.56 | 320.9448 | 446 | 432.3 | 418.4 | 384.4 | 760.2 | 63.3 | 17.9 | 106.3 | 10.7 | 247.7 | 16 | 920.1 | 763.9 | 786.2 | 822.4 | 714.7 | 806.7 | 735.3 | 753.2 | 749.5 | 744.2 | 347.3 | 420 | 454.6 | 377.3 | 452.7 | 421.8 | 434 | 409.1 | 560 | 429.8
2091 | 1897 | 686 | 274.4 | 320.7578 | 446.6 | 432 | 418.5 | 383.8 | 752.6 | 63.3 | 17.8 | 106.4 | 9.7 | 241.5 | 15.7 | 919.4 | 763.8 | 780.7 | 823 | 713 | 804.2 | 733.1 | 750.3 | 749.5 | 742 | 347.5 | 420.2 | 455.1 | 377.5 | 452.9 | 421.8 | 434.2 | 409 | 559.8 | 429.9
2092 | 1898 | 685.4 | 274.16 | 320.4772 | 446.7 | 431.5 | 417.8 | 383.8 | 752.3 | 63.3 | 17.8 | 106.5 | 8.6 | 242 | 15.3 | 917.7 | 767.7 | 812.1 | 823.6 | 717.2 | 808.5 | 745.4 | 766.3 | 749.8 | 748 | 347.7 | 420.3 | 454.6 | 377.7 | 453.1 | 422 | 434.3 | 409.2 | 559.4 | 430
2093 | 1899 | 686.1 | 274.44 | 320.8045 | 446.1 | 431.2 | 418.1 | 384.1 | 756.6 | 63.4 | 17.8 | 106.5 | 7.2 | 237.7 | 14.9 | 914 | 768.7 | 833.7 | 823.9 | 719.8 | 810.1 | 758.6 | 767.9 | 750 | 750.3 | 348 | 420.4 | 454.3 | 377.9 | 453 | 422 | 434.3 | 409.2 | 559.5 | 430.1
2094 | 1900 | 684.9 | 273.96 | 320.2435 | 445.1 | 431 | 417.3 | 383.3 | 748.3 | 63.4 | 17.9 | 106.5 | 7.6 | 235.8 | 15.3 | 911.2 | 768.6 | 849 | 824 | 722.7 | 811 | 769.7 | 780 | 749.8 | 753.6 | 348.2 | 420.5 | 454.3 | 378.1 | 452.8 | 422.1 | 434.3 | 409.2 | 559.9 | 430.2
2095 | 1901 | 685.6 | 274.24 | 320.5708 | 444.1 | 430.6 | 416.6 | 382.5 | 732.5 | 63.4 | 17.8 | 106.5 | 6.8 | 261.4 | 15.2 | 908.5 | 768 | 855.4 | 823.9 | 726.8 | 813.2 | 781.9 | 782.9 | 749.7 | 757.3 | 348.4 | 420.6 | 454.4 | 378.3 | 452.6 | 422.1 | 434.3 | 409.3 | 560.7 | 430.3
2096 | 1902 | 684.6 | 273.84 | 320.1032 | 443 | 430 | 415.3 | 382.2 | 740.4 | 63.4 | 17.8 | 106.7 | 6.2 | 259 | 16.7 | 907 | 767.6 | 852.9 | 823.8 | 730.1 | 812.8 | 790.9 | 785.9 | 749.7 | 759.6 | 348.6 | 420.8 | 454.4 | 378.4 | 452.7 | 422.1 | 434.4 | 409.3 | 561.5 | 430.4
2097 | 1903 | 684.6 | 273.84 | 320.1032 | 442 | 429.8 | 414.7 | 381.6 | 739.3 | 63.4 | 17.8 | 106.7 | 6.6 | 251.4 | 16.7 | 907.3 | 769.5 | 856.6 | 823.8 | 733.2 | 814 | 797.4 | 792.6 | 749.6 | 762.3 | 348.8 | 421 | 454.4 | 378.6 | 452.8 | 422.5 | 434.5 | 409.5 | 562.4 | 430.5
2098 | 1904 | 684.7 | 273.88 | 320.1499 | 441 | 429.9 | 413.9 | 381.8 | 731.7 | 63.4 | 17.8 | 106.7 | 7.2 | 256.1 | 15.9 | 911.8 | 773.5 | 842.9 | 823.6 | 730.9 | 813.5 | 794.9 | 796.7 | 749.3 | 761.5 | 349 | 421.1 | 454.5 | 378.8 | 453 | 422.8 | 434.7 | 409.5 | 563.2 | 430.6
2099 | 1905 | 684.7 | 273.88 | 320.1499 | 440.9 | 429.5 | 414 | 382.7 | 711.9 | 63.3 | 17.8 | 106.6 | 7 | 267 | 16.4 | 914.1 | 776.8 | 803.8 | 823.1 | 727.8 | 798.6 | 784.8 | 791.2 | 748.6 | 756.4 | 349.2 | 421.3 | 454.3 | 379 | 452.9 | 423.3 | 434.7 | 409.6 | 563.2 | 430.7
2100 | 1906 | 684.7 | 273.88 | 320.1499 | 441.9 | 428.4 | 412.3 | 382.4 | 683.6 | 63.3 | 17.8 | 106.4 | 7 | 259.7 | 15.1 | 916.3 | 771.2 | 766 | 822.7 | 725.7 | 790 | 776.3 | 771.2 | 748.1 | 753.4 | 349.4 | 421.4 | 454.1 | 379.2 | 452.7 | 423.5 | 434.6 | 409.8 | 562.7 | 430.8
2101 | 1907 | 685.7 | 274.28 | 320.6175 | 444.1 | 427 | 410.3 | 380.3 | 667.9 | 63.4 | 17.8 | 106.3 | 6.9 | 259.9 | 14.5 | 919.2 | 760.2 | 744.2 | 822.2 | 721.6 | 781.6 | 762.5 | 746.4 | 747.8 | 748.3 | 349.6 | 421.5 | 454.2 | 379.3 | 452.7 | 423.4 | 434.6 | 409.8 | 562.2 | 430.8
2102 | 1908 | 685.9 | 274.36 | 320.711 | 446.5 | 426 | 409.3 | 379.5 | 677.4 | 63.5 | 17.8 | 106.3 | 5.9 | 250.3 | 16.2 | 919.6 | 753.6 | 740.5 | 822 | 718.6 | 788.6 | 749.5 | 741.7 | 748.3 | 745.3 | 349.9 | 421.6 | 454.8 | 379.5 | 453 | 423.3 | 434.8 | 409.7 | 561.7 | 431
2103 | 1909 | 682.9 | 273.16 | 319.3083 | 447.4 | 425.9 | 408.9 | 380 | 710 | 63.5 | 17.8 | 106.4 | 6.3 | 244.5 | 17.5 | 917.9 | 753.3 | 764.3 | 822 | 718.1 | 796.2 | 741.4 | 752.4 | 749.3 | 745.8 | 350.1 | 421.6 | 455.2 | 379.7 | 453.1 | 423.1 | 435.1 | 409.7 | 561.4 | 431.1
2104 | 1910 | 455.7 | 182.28 | 213.0748 | 447.1 | 426.3 | 409.2 | 380.6 | 733.5 | 63.5 | 17.8 | 106.6 | 6 | 239.6 | 16.8 | 916.8 | 751 | 757 | 822 | 715.1 | 799.6 | 738.5 | 748.5 | 750.2 | 744.1 | 350.3 | 421.7 | 455.4 | 379.8 | 453.4 | 422.9 | 435.4 | 409.6 | 561.2 | 431.2
2105 | 1911 | -2.4 | 0 | 0 | 447.3 | 427.2 | 410.6 | 381.2 | 738.4 | 63.6 | 17.8 | 106.7 | 6.3 | 230.4 | 15.6 | 916.7 | 749.6 | 746.8 | 822 | 714.1 | 799.6 | 735.3 | 742.2 | 750.8 | 740.5 | 350.5 | 421.8 | 455.6 | 380 | 453.7 | 422.9 | 435.5 | 409.6 | 561.1 | 431.3
2106 | 1912 | -6.9 | 0 | 0 | 447.1 | 427.3 | 412.2 | 381.9 | 720.1 | 63.6 | 17.8 | 106.9 | 6.1 | 252.1 | 13.1 | 915.9 | 740.6 | 707.8 | 821.7 | 708.3 | 781.8 | 720.8 | 712.2 | 750.3 | 734.7 | 350.7 | 421.9 | 454.9 | 380.2 | 453.7 | 422.7 | 435.6 | 409.6 | 560.9 | 431.5
2107 | 1913 | -6.9 | 0 | 0 | 445.2 | 426.5 | 412.4 | 380.8 | 674.4 | 63.6 | 17.8 | 106.9 | 6.3 | 263 | 14.3 | 914.6 | 728.1 | 660.7 | 821.3 | 701.7 | 753.4 | 697.9 | 676.5 | 748.9 | 727.9 | 350.9 | 422 | 454 | 380.3 | 453.5 | 421.6 | 435.5 | 409.5 | 560.4 | 431.5
2108 | 1914 | -6.9 | 0 | 0 | 442.3 | 424.5 | 410.3 | 379.1 | 633.7 | 63.7 | 17.8 | 107 | 6.3 | 262.7 | 15.7 | 912.7 | 717.1 | 614.7 | 820.8 | 695.4 | 728.2 | 674.2 | 646.6 | 747.3 | 721.3 | 351.1 | 422.1 | 453.5 | 380.5 | 452.9 | 420.3 | 435.2 | 409.3 | 559.7 | 431.6
2109 | 1915 | -6.9 | 0 | 0 | 438.3 | 421.7 | 407.2 | 377 | 601.2 | 63.6 | 17.8 | 106.9 | 6.2 | 253.1 | 16 | 910.3 | 706.6 | 575.5 | 820.2 | 688.9 | 709.8 | 652.7 | 620.7 | 745.5 | 714.3 | 351.3 | 422.2 | 453.1 | 380.6 | 452.1 | 418.4 | 434.7 | 409 | 559 | 431.6
2110 | 1916 | -6.8 | 0 | 0 | 433.9 | 418.7 | 402.8 | 374 | 574.9 | 63.5 | 17.8 | 106.6 | 5.9 | 247.6 | 15.5 | 907.1 | 697.8 | 543.2 | 819.8 | 682.4 | 693.3 | 632.9 | 597.6 | 743.9 | 708 | 351.5 | 422.3 | 452.8 | 380.8 | 450.9 | 416 | 434.2 | 408.6 | 558.3 | 431.6
2111 | 1917 | -6.8 | 0 | 0 | 429.9 | 415.7 | 398.2 | 370.5 | 551.5 | 63.3 | 17.8 | 106.1 | 5.8 | 257.3 | 14 | 903.4 | 689.5 | 515.2 | 819.6 | 676.3 | 681.1 | 614.6 | 578 | 742.4 | 701.4 | 351.7 | 422.3 | 452.4 | 380.9 | 449.8 | 413.4 | 433.5 | 408.2 | 557.6 | 431.6
2112 | 1918 | -6.8 | 0 | 0 | 426.4 | 412.7 | 393.5 | 366.8 | 531.2 | 63.3 | 17.8 | 105.3 | 4.8 | 246.8 | 12.9 | 899.3 | 681.4 | 490.7 | 819.3 | 670.5 | 669.3 | 598.1 | 560.3 | 741 | 695.4 | 351.9 | 422.4 | 452 | 381.1 | 448.6 | 410.9 | 432.8 | 407.7 | 556.9 | 431.6
2113 | 1919 | -6.8 | 0 | 0 | 423.1 | 409.7 | 388.7 | 362.8 | 514 | 63.3 | 17.8 | 104.3 | 5.3 | 235.9 | 13 | 895.1 | 672.6 | 468.2 | 818.4 | 665.6 | 658.9 | 582.4 | 544.9 | 739.7 | 689.7 | 352.1 | 422.4 | 451.6 | 381.3 | 447.3 | 408 | 432.1 | 407.2 | 556.2 | 431.5
2114 | 1920 | -6.8 | 0 | 0 | 419.6 | 406.3 | 384.1 | 358.9 | 499.2 | 63.1 | 17.8 | 103.4 | 6.3 | 236.1 | 11.8 | 890.7 | 665 | 446.8 | 817.4 | 660.2 | 650.4 | 568 | 531 | 738.4 | 684.1 | 352.3 | 422.4 | 451.3 | 381.4 | 445.9 | 404.8 | 431.4 | 406.6 | 555.4 | 431.5
2115 | 1921 | -6.8 | 0 | 0 | 415.8 | 402.8 | 379.9 | 355.4 | 486.1 | 62.9 | 17.8 | 102.5 | 6 | 242.5 | 11.1 | 886.1 | 658.2 | 429.1 | 816.6 | 655.1 | 640.6 | 556 | 516.9 | 737 | 678.5 | 352.5 | 422.4 | 450.9 | 381.6 | 444.4 | 401.4 | 430.7 | 406 | 554.7 | 431.4
2116 | 1922 | -6.8 | 0 | 0 | 411.4 | 399.2 | 375.9 | 352.5 | 474.3 | 62.9 | 17.8 | 101.8 | 5.8 | 232.6 | 9.8 | 881.5 | 651.9 | 413.9 | 815.8 | 649.5 | 631.9 | 543 | 505.9 | 735.7 | 672.8 | 352.8 | 422.4 | 450.5 | 381.7 | 443 | 398 | 429.9 | 405.2 | 554 | 431.4
2117 | 1923 | -6.8 | 0 | 0 | 407.4 | 395.8 | 372 | 349.3 | 463.4 | 62.9 | 17.8 | 101 | 5.4 | 244.7 | 10.5 | 876.7 | 645.5 | 399.1 | 815.1 | 644.3 | 624.3 | 531.7 | 496.4 | 734.3 | 667.3 | 352.9 | 422.4 | 450.1 | 381.9 | 441.6 | 394.6 | 429.1 | 404.6 | 553.3 | 431.3
2118 | 1924 | -6.8 | 0 | 0 | 404 | 393 | 368.4 | 346.2 | 453.5 | 63 | 17.8 | 100.4 | 6.3 | 250.4 | 11.9 | 871.6 | 639.6 | 384.9 | 814.4 | 639.3 | 616.6 | 522 | 487.1 | 733 | 662 | 353.1 | 422.4 | 449.7 | 382 | 440.1 | 391.4 | 428.3 | 404 | 552.5 | 431.2
2119 | 1925 | -6.8 | 0 | 0 | 400.9 | 390.4 | 365 | 343.3 | 444.8 | 63 | 17.8 | 99.7 | 7 | 224.9 | 11.8 | 866.5 | 634.1 | 372.2 | 813.8 | 634.2 | 610 | 513.3 | 478.7 | 731.8 | 657.2 | 353.3 | 422.3 | 449.3 | 382.2 | 438.8 | 388.3 | 427.5 | 403.3 | 551.8 | 431.1
2120 | 1926 | -6.8 | 0 | 0 | 398.4 | 388 | 361.5 | 340.5 | 437.5 | 63 | 17.8 | 99.1 | 7.6 | 238.2 | 9.9 | 861.8 | 629.1 | 361.2 | 813.3 | 629.5 | 604.4 | 504.3 | 470.5 | 730.6 | 652.4 | 353.6 | 422.3 | 448.9 | 382.3 | 437.4 | 385.3 | 426.8 | 402.6 | 551 | 431
2121 | 1927 | -6.8 | 0 | 0 | 395.9 | 385.6 | 358.2 | 337.8 | 430.8 | 63 | 17.8 | 98.4 | 6.8 | 247 | 9.9 | 857.3 | 624 | 350.7 | 812.5 | 624.7 | 598.4 | 496.6 | 462.3 | 729.4 | 647.7 | 353.8 | 422.3 | 448.5 | 382.5 | 436.1 | 382.5 | 426.1 | 402 | 550.3 | 430.9
2122 | 1928 | -6.8 | 0 | 0 | 393.2 | 383.1 | 355.3 | 335.3 | 424.7 | 63 | 17.8 | 97.8 | 5.2 | 233.4 | 11.2 | 852.8 | 619.3 | 341 | 811.6 | 619.8 | 592.8 | 489.5 | 454.4 | 728.2 | 642.9 | 353.9 | 422.2 | 448.1 | 382.6 | 434.6 | 379.7 | 425.3 | 401.3 | 549.5 | 430.9
2123 | 1929 | -6.8 | 0 | 0 | 390.8 | 381 | 352.6 | 333 | 419.6 | 63 | 17.8 | 97.3 | 4.2 | 235 | 13.8 | 848.3 | 614.2 | 332.7 | 810.2 | 616.2 | 585.8 | 483.2 | 447.5 | 726.9 | 638.3 | 354.1 | 422.1 | 447.7 | 382.8 | 433.3 | 377.3 | 424.5 | 400.6 | 548.8 | 430.8
2124 | 1930 | -6.8 | 0 | 0 | 388.5 | 378.8 | 350 | 331 | 414.4 | 63 | 17.8 | 96.8 | 4.4 | 238 | 16.1 | 843.7 | 609.5 | 324.5 | 808.8 | 611.3 | 581.4 | 478.9 | 441.1 | 725.9 | 633.9 | 354.3 | 422 | 447.3 | 382.9 | 432 | 375 | 423.8 | 400 | 548.1 | 430.7
2125 | 1931 | -6.8 | 0 | 0 | 386.3 | 376.9 | 347.8 | 329 | 409.4 | 62.9 | 17.8 | 96.4 | 4.4 | 240.2 | 15.3 | 839.2 | 604.8 | 316.9 | 807 | 607.6 | 575.3 | 471.6 | 436.4 | 724.6 | 629.5 | 354.5 | 421.9 | 446.9 | 383.1 | 430.7 | 372.7 | 423.2 | 399.4 | 547.3 | 430.5
2126 | 1932 | -6.8 | 0 | 0 | 384.1 | 375.1 | 345.7 | 327 | 404.9 | 62.9 | 17.8 | 96 | 5.5 | 240.7 | 13.8 | 834.8 | 599.9 | 309.6 | 805.7 | 603.6 | 569 | 465.3 | 431.5 | 723.3 | 625 | 354.7 | 421.8 | 446.5 | 383.2 | 429.6 | 370.5 | 422.4 | 398.7 | 546.6 | 430.4
2127 | 1933 | -6.8 | 0 | 0 | 382 | 373.2 | 343.8 | 325 | 401 | 62.9 | 17.8 | 95.6 | 6.6 | 239.4 | 11.9 | 830.6 | 596.4 | 304 | 804.1 | 600.1 | 562.4 | 461 | 425.7 | 721.9 | 620.8 | 354.9 | 421.7 | 446.1 | 383.4 | 428.5 | 368.4 | 421.8 | 398 | 545.8 | 430.4
2128 | 1934 | -6.8 | 0 | 0 | 379.9 | 371.5 | 341.8 | 323.2 | 397.7 | 63 | 17.8 | 95.2 | 6.2 | 240.1 | 11.2 | 826.4 | 590.8 | 298.8 | 801.8 | 596.7 | 555.7 | 457.4 | 419.9 | 720.6 | 617.1 | 355.1 | 421.6 | 445.7 | 383.5 | 427.3 | 366.3 | 421.1 | 397.3 | 545.1 | 430.2
2129 | 1935 | -6.8 | 0 | 0 | 377.9 | 370.1 | 339.9 | 321.4 | 394.6 | 63 | 17.8 | 94.8 | 5.2 | 248.8 | 10.4 | 822 | 585.5 | 293.7 | 799.6 | 593.2 | 549.8 | 453.3 | 414.7 | 719.2 | 614.1 | 355.3 | 421.4 | 445.3 | 383.7 | 426.1 | 364.1 | 420.4 | 396.7 | 544.4 | 430.1
2130 | 1936 | -6.8 | 0 | 0 | 376 | 369 | 338.1 | 319.8 | 391.7 | 63 | 17.8 | 94.4 | 4.5 | 253.6 | 9.7 | 817.6 | 580.7 | 288.9 | 797.4 | 589.8 | 544 | 447.8 | 409.2 | 717.7 | 610 | 355.5 | 421.3 | 444.8 | 383.8 | 424.9 | 362.1 | 419.8 | 396 | 543.6 | 430
2131 | 1937 | -6.8 | 0 | 0 | 374.5 | 367.8 | 336.3 | 318.3 | 389.1 | 62.9 | 17.8 | 94 | 4.5 | 267.5 | 10.1 | 813.4 | 576.1 | 283.6 | 795.2 | 586.7 | 539.8 | 444.8 | 404.9 | 716.2 | 605.6 | 355.7 | 421.2 | 444.5 | 383.9 | 423.8 | 360.2 | 419.1 | 395.4 | 542.9 | 429.9
2132 | 1938 | -6.8 | 0 | 0 | 372.9 | 366.8 | 334.8 | 316.8 | 386.9 | 62.8 | 17.8 | 93.7 | 5.5 | 253 | 11.1 | 809.2 | 572.2 | 279.3 | 793.2 | 583.5 | 535.4 | 440.6 | 401.3 | 714.7 | 601.3 | 355.9 | 421 | 444 | 384.1 | 422.7 | 358.3 | 418.5 | 394.7 | 542.1 | 429.7
2133 | 1939 | -6.8 | 0 | 0 | 371.4 | 365.9 | 333.4 | 315.3 | 384.6 | 62.6 | 17.8 | 93.5 | 5.5 | 254.1 | 12.7 | 805 | 568.3 | 274.7 | 791.2 | 580.4 | 530.1 | 436.3 | 397.1 | 713.3 | 597.5 | 356.1 | 420.9 | 443.6 | 384.2 | 421.5 | 356.6 | 417.8 | 394 | 541.4 | 429.6
2134 | 1940 | -6.8 | 0 | 0 | 370 | 365 | 332 | 314.1 | 382.6 | 62.4 | 17.8 | 93.1 | 4.6 | 251 | 12.9 | 801.1 | 564.6 | 270 | 788.7 | 576.6 | 525.7 | 432 | 393.1 | 711.9 | 593.7 | 356.3 | 420.7 | 443.2 | 384.3 | 420.3 | 354.8 | 417.2 | 393.4 | 540.6 | 429.5
2135 | 1941 | -6.8 | 0 | 0 | 368.8 | 364.1 | 330.7 | 312.9 | 380.6 | 62.3 | 17.8 | 92.7 | 5.1 | 248.9 | 11.2 | 797 | 560.8 | 266.1 | 786.4 | 573.4 | 521.3 | 428.8 | 389.5 | 710.6 | 590.4 | 356.5 | 420.6 | 442.8 | 384.4 | 419.2 | 353.2 | 416.5 | 392.8 | 539.9 | 429.4
2136 | 1942 | -6.8 | 0 | 0 | 367.3 | 363.2 | 329.5 | 311.8 | 378.5 | 62.1 | 17.8 | 92.3 | 5.4 | 243 | 9.4 | 793 | 557 | 262.7 | 784.3 | 570.2 | 517.1 | 426.5 | 385.8 | 709.4 | 587.3 | 356.7 | 420.4 | 442.4 | 384.5 | 418 | 351.6 | 415.9 | 392.1 | 539.1 | 429.2
2137 | 1943 | -6.8 | 0 | 0 | 366.1 | 362.2 | 328.3 | 310.7 | 376.4 | 62 | 17.8 | 92 | 6.6 | 245.3 | 9.1 | 789.2 | 553.6 | 258.5 | 782 | 567.2 | 513.1 | 425.1 | 382.3 | 708 | 584 | 356.8 | 420.3 | 442 | 384.7 | 416.9 | 350.1 | 415.2 | 391.5 | 538.4 | 429.1
2138 | 1944 | -6.8 | 0 | 0 | 365.2 | 361.4 | 327.1 | 309.5 | 374.6 | 61.9 | 17.8 | 91.7 | 7.3 | 255.3 | 10.5 | 785.4 | 549.9 | 254.4 | 779.8 | 564.5 | 510.1 | 423.6 | 379.5 | 706.7 | 580.7 | 357 | 420.1 | 441.6 | 384.8 | 416 | 348.6 | 414.7 | 390.8 | 537.7 | 428.9
2139 | 1945 | -6.8 | 0 | 0 | 364.4 | 360.4 | 326 | 308.6 | 373 | 61.8 | 17.8 | 91.5 | 6.3 | 276.4 | 11.1 | 781.7 | 546.3 | 250.5 | 777.9 | 561.1 | 507.4 | 424 | 376.2 | 705.3 | 577.7 | 357.2 | 419.9 | 441.2 | 384.9 | 415.1 | 347.2 | 414.2 | 390.2 | 536.9 | 428.7
2140 | 1946 | -6.8 | 0 | 0 | 363.7 | 359.6 | 324.9 | 307.9 | 371.5 | 61.7 | 17.8 | 91.2 | 6 | 247.9 | 12.3 | 777.9 | 542.9 | 246.2 | 775.7 | 559 | 502.2 | 420 | 371.9 | 703.9 | 574.5 | 357.3 | 419.7 | 440.8 | 385 | 414.3 | 345.9 | 413.6 | 389.6 | 536.2 | 428.6
2141 | 1947 | -6.8 | 0 | 0 | 363 | 358.6 | 323.7 | 307 | 370.2 | 61.6 | 17.8 | 90.9 | 6.5 | 237.3 | 13 | 774.3 | 539.5 | 242.6 | 773.7 | 556.4 | 497.5 | 418.5 | 368.1 | 702.4 | 572 | 357.5 | 419.5 | 440.4 | 385.1 | 413.4 | 344.7 | 413.1 | 388.9 | 535.4 | 428.5
2142 | 1948 | -6.8 | 0 | 0 | 362.2 | 357.6 | 322.6 | 306.1 | 368.9 | 61.4 | 17.8 | 90.6 | 6.7 | 250.1 | 12.4 | 770.6 | 536.4 | 240.4 | 771.9 | 553.1 | 493.8 | 416 | 365.4 | 701 | 568.9 | 357.6 | 419.3 | 440 | 385.2 | 412.5 | 343.3 | 412.6 | 388.3 | 534.7 | 428.3
2143 | 1949 | -6.8 | 0 | 0 | 361.6 | 356.9 | 321.7 | 305.2 | 367.5 | 61.4 | 17.9 | 90.3 | 5.8 | 242.8 | 13.1 | 767.1 | 532.7 | 237.5 | 769.9 | 550.6 | 491.1 | 415.3 | 362.8 | 699.6 | 565.7 | 357.8 | 419.2 | 439.6 | 385.4 | 411.6 | 342 | 412 | 387.7 | 534 | 428.1
2144 | 1950 | -6.8 | 0 | 0 | 360.7 | 355.9 | 320.9 | 304.3 | 366.2 | 61.3 | 17.9 | 90.1 | 6 | 259.6 | 12.8 | 763.7 | 529.8 | 234.1 | 767.8 | 548.5 | 488.4 | 413.3 | 359.8 | 698.2 | 562.7 | 357.9 | 418.9 | 439.1 | 385.5 | 410.8 | 340.9 | 411.5 | 387.1 | 533.2 | 428
2145 | 1951 | -6.8 | 0 | 0 | 359.9 | 355.1 | 320.2 | 303.5 | 365.1 | 61.1 | 17.9 | 89.8 | 7.6 | 272 | 12.9 | 760.3 | 526.5 | 230.9 | 765.4 | 546 | 484.9 | 409.4 | 357.4 | 696.8 | 559.8 | 358.1 | 418.8 | 438.8 | 385.6 | 410 | 339.9 | 411 | 386.5 | 532.5 | 427.8
2146 | 1952 | -6.8 | 0 | 0 | 359.2 | 353.9 | 319.6 | 302.7 | 364.2 | 60.9 | 17.9 | 89.5 | 7.8 | 252.3 | 12.2 | 756.9 | 523 | 228.2 | 763.2 | 543.7 | 480.9 | 406.3 | 353.7 | 695.4 | 557.5 | 358.2 | 418.6 | 438.3 | 385.7 | 409.3 | 338.9 | 410.5 | 386 | 531.7 | 427.6
2147 | 1953 | -6.8 | 0 | 0 | 358.6 | 352.8 | 318.8 | 301.9 | 363.1 | 60.8 | 17.9 | 89.2 | 7.2 | 258 | 12.3 | 753.4 | 519.4 | 226.3 | 761.1 | 541.4 | 476.4 | 402.8 | 351 | 694 | 555.3 | 358.4 | 418.3 | 437.9 | 385.8 | 408.5 | 337.9 | 410 | 385.4 | 531 | 427.5
2148 | 1954 | -6.8 | 0 | 0 | 357.9 | 352.2 | 317.9 | 301.1 | 361.6 | 60.7 | 17.9 | 88.8 | 6.9 | 267.9 | 12.5 | 750.1 | 516.4 | 224.3 | 759.3 | 538.7 | 472.3 | 398.6 | 348.1 | 692.6 | 552.4 | 358.5 | 418.1 | 437.5 | 385.8 | 407.8 | 337 | 409.5 | 384.8 | 530.3 | 427.3
2149 | 1955 | -6.8 | 0 | 0 | 357.5 | 351.4 | 317.1 | 300.3 | 360.6 | 60.5 | 17.9 | 88.5 | 7.7 | 252.4 | 14 | 746.7 | 513.3 | 221.9 | 757.4 | 536 | 469.2 | 394.4 | 346.1 | 691.4 | 549.5 | 358.6 | 417.9 | 437.1 | 385.9 | 407.1 | 336.1 | 409 | 384.3 | 529.6 | 427.2
2150 | 1956 | -6.8 | 0 | 0 | 356.7 | 350.5 | 316.4 | 299.6 | 359.5 | 60.4 | 17.9 | 88.1 | 7.8 | 264.7 | 14.9 | 743.5 | 510.8 | 220.4 | 755.5 | 533.7 | 470.6 | 393.7 | 344.6 | 691.5 | 546.4 | 358.8 | 417.7 | 436.7 | 386 | 406.3 | 335.2 | 408.6 | 383.7 | 528.8 | 427
2151 | 1957 | -6.8 | 0 | 0 | 355.8 | 350 | 315.6 | 298.9 | 357.9 | 60.3 | 17.9 | 87.8 | 7.5 | 240.7 | 15.2 | 740.6 | 507.8 | 226.7 | 755.8 | 531.2 | 473 | 394.3 | 347.5 | 690.5 | 544 | 358.9 | 417.5 | 436.3 | 386.1 | 405.6 | 334.2 | 408.1 | 383.2 | 528.1 | 426.8
2152 | 1958 | -6.8 | 0 | 0 | 354.7 | 348.9 | 315 | 298.1 | 356.8 | 60.3 | 17.9 | 87.5 | 6.1 | 251.9 | 15.5 | 737.3 | 504.4 | 225.5 | 753.4 | 528.5 | 473.8 | 394.6 | 347.9 | 692.1 | 540.9 | 359 | 417.3 | 435.9 | 386.2 | 405 | 333.2 | 407.6 | 382.6 | 527.4 | 426.7
2153 | 1959 | -6.8 | 0 | 0 | 352.7 | 346.6 | 314.5 | 297.5 | 354.9 | 60.3 | 17.9 | 87.2 | 5.7 | 239.7 | 15.9 | 734 | 502.4 | 223 | 750.3 | 526.2 | 473 | 393.2 | 345.1 | 691.2 | 537.9 | 359.2 | 417.1 | 435.5 | 386.3 | 404.4 | 332.1 | 407.2 | 382 | 526.7 | 426.5
2154 | 1960 | -6.8 | 0 | 0 | 351.4 | 345.2 | 314 | 296.7 | 350.7 | 60.1 | 17.9 | 86.9 | 6.4 | 256.7 | 19.1 | 731.1 | 499.8 | 224.2 | 747.3 | 524.1 | 468.8 | 388 | 346.1 | 688.2 | 535.6 | 359.3 | 416.9 | 435 | 386.3 | 403.7 | 331.1 | 406.7 | 381.4 | 526 | 426.3
2155 | 1961 | -6.8 | 0 | 0 | 348.4 | 344.7 | 313.3 | 295.5 | 335.2 | 60 | 17.9 | 86.7 | 6.3 | 250.2 | 20.4 | 727.9 | 497 | 223.4 | 746 | 521.9 | 461.5 | 378.7 | 347 | 682.1 | 533.3 | 359.4 | 416.6 | 434.7 | 386.4 | 403 | 330 | 406.3 | 380.8 | 525.2 | 426.2
2156 | 1962 | -6.8 | 0 | 0 | 343.8 | 343.8 | 312.5 | 294.4 | 322.3 | 59.9 | 17.9 | 86.5 | 5.7 | 249.4 | 19.3 | 725.4 | 493 | 228.9 | 747.9 | 519.3 | 456 | 372.8 | 346.3 | 677.9 | 530.1 | 359.6 | 416.4 | 434.3 | 386.5 | 402.4 | 328.8 | 405.8 | 380.1 | 524.5 | 426
2157 | 1963 | -6.8 | 0 | 0 | 339.7 | 342.5 | 311.5 | 293.1 | 321.9 | 59.8 | 17.9 | 86.4 | 5.2 | 250.7 | 19.5 | 722 | 490.8 | 225.9 | 745.5 | 517.1 | 455.2 | 373.2 | 344 | 681.1 | 526.4 | 359.7 | 416.2 | 433.8 | 386.6 | 401.7 | 327.8 | 405.3 | 379.5 | 523.8 | 425.8
2158 | 1964 | -6.8 | 0 | 0 | 338.9 | 340.6 | 310.4 | 291.6 | 290.1 | 59.8 | 17.9 | 86.2 | 6.1 | 252.3 | 20.1 | 718.7 | 487.9 | 222.3 | 741.6 | 515.1 | 445.6 | 360.4 | 339.4 | 673.2 | 523.6 | 359.8 | 415.9 | 433.3 | 386.6 | 401 | 326.6 | 404.9 | 378.9 | 523 | 425.7
2159 | 1965 | -6.8 | 0 | 0 | 337.8 | 339.6 | 308.7 | 289.5 | 283.5 | 59.7 | 17.9 | 86 | 6.7 | 251.6 | 17.3 | 715.4 | 483.1 | 220.6 | 738.2 | 513.3 | 441.3 | 355.9 | 338 | 670.1 | 520.5 | 359.9 | 415.7 | 432.9 | 386.7 | 400.1 | 325.2 | 404.3 | 378.3 | 522.3 | 425.5
2160 | 1966 | -6.8 | 0 | 0 | 335.2 | 338.4 | 307 | 287.3 | 244.5 | 59.7 | 17.9 | 85.7 | 8 | 246.1 | 16.1 | 711.8 | 479.6 | 217.2 | 734.4 | 511 | 437.1 | 341.5 | 337.1 | 665.9 | 516.7 | 360.1 | 415.5 | 432.4 | 386.8 | 399.3 | 323.8 | 403.8 | 377.6 | 521.6 | 425.3
2161 | 1967 | -6.8 | 0 | 0 | 333.8 | 335.9 | 306.1 | 285.9 | 204 | 59.7 | 17.9 | 85.6 | 7.8 | 257.5 | 15.6 | 707.7 | 470.6 | 214.1 | 729.4 | 508.4 | 428.7 | 306.4 | 332.6 | 654.8 | 510.7 | 360.2 | 415.3 | 431.9 | 386.8 | 398.4 | 322.2 | 403.2 | 377 | 520.8 | 425.1
2162 | 1968 | -6.8 | 0 | 0 | 331.7 | 333.9 | 304.3 | 285.1 | 102.5 | 59.6 | 17.9 | 85.3 | 7.4 | 259 | 16.6 | 703.6 | 459.9 | 210.5 | 727.5 | 506 | 421.3 | 294.7 | 326.1 | 643.1 | 502.6 | 360.3 | 415 | 431.6 | 386.9 | 397.6 | 320.7 | 402.7 | 376.3 | 520 | 424.9
2163 | 1969 | -6.8 | 0 | 0 | 329.4 | 332.4 | 302.4 | 284.1 | 76 | 59.5 | 17.9 | 85.1 | 5.7 | 255.3 | 16 | 699.7 | 449.6 | 206.8 | 725.2 | 503.6 | 412.9 | 285 | 318.8 | 629.4 | 494.8 | 360.4 | 414.8 | 431.2 | 387 | 396.6 | 319.5 | 402.2 | 375.7 | 519.3 | 424.6
2164 | 1970 | -6.8 | 0 | 0 | 328.8 | 331.5 | 301.3 | 283.3 | 68.4 | 59.4 | 17.9 | 84.9 | 6.4 | 256.1 | 18.1 | 695.7 | 435.1 | 203.2 | 722.4 | 501.2 | 391.5 | 280.2 | 310.7 | 620.1 | 488.7 | 360.5 | 414.5 | 430.8 | 387 | 395.6 | 318.4 | 401.7 | 375 | 518.5 | 424.4
2165 | 1971 | -6.8 | 0 | 0 | 328.3 | 331 | 300.2 | 282.6 | 67.2 | 59.4 | 17.9 | 84.7 | 7.7 | 254.9 | 18.9 | 691.5 | 425.2 | 200 | 719.9 | 498.9 | 374.9 | 279.3 | 304.6 | 608.2 | 485.3 | 360.7 | 414.2 | 430.3 | 387.1 | 394.6 | 317.5 | 401.2 | 374.5 | 517.8 | 424.2
2166 | 1972 | -6.8 | 0 | 0 | 327.8 | 330.3 | 298.9 | 282 | 68.6 | 59.3 | 17.9 | 84.6 | 7.6 | 253.5 | 17.3 | 687.5 | 416.4 | 196.9 | 717 | 496.7 | 370.5 | 277 | 300.8 | 586.4 | 482.2 | 360.8 | 414 | 429.9 | 387.2 | 393.8 | 316.7 | 400.6 | 373.9 | 517 | 424.1
2167 | 1973 | -6.8 | 0 | 0 | 327.8 | 329.5 | 298.1 | 282.1 | 67.7 | 59.3 | 17.9 | 84.4 | 7.2 | 257.9 | 14.3 | 683.7 | 409.7 | 194 | 713.6 | 494.3 | 363.7 | 277.1 | 296.8 | 575.7 | 479.2 | 360.9 | 413.7 | 429.5 | 387.2 | 393 | 315.8 | 400.2 | 373.3 | 516.2 | 423.9
2168 | 1974 | -6.8 | 0 | 0 | 327.7 | 328.8 | 297.7 | 282.2 | 63.6 | 59.2 | 17.9 | 84.3 | 6.8 | 257 | 12.7 | 680 | 404.9 | 190.7 | 711.5 | 491.9 | 354.3 | 267.6 | 292.3 | 569.7 | 476 | 361 | 413.5 | 429 | 387.3 | 392.2 | 314.8 | 399.6 | 372.7 | 515.4 | 423.6
2169 | 1975 | -6.8 | 0 | 0 | 327.5 | 327.9 | 297 | 282 | 61.2 | 59.2 | 17.9 | 84.3 | 7.4 | 267.8 | 14.1 | 676.2 | 398.2 | 187.2 | 708.6 | 489.2 | 345.3 | 264.8 | 286.8 | 566.2 | 472.7 | 361.1 | 413.3 | 428.6 | 387.3 | 391.5 | 313.9 | 399.1 | 372.1 | 514.6 | 423.4
2170 | 1976 | -6.8 | 0 | 0 | 327.4 | 327.1 | 296.5 | 281.7 | 60.1 | 59.1 | 17.9 | 84.1 | 7.6 | 245.2 | 13.8 | 672.7 | 388.2 | 184.3 | 704.5 | 486.6 | 336.3 | 259.4 | 277.3 | 563.1 | 470.1 | 361.2 | 413 | 428.1 | 387.4 | 390.8 | 313 | 398.5 | 371.5 | 513.8 | 423.2
2171 | 1977 | -6.8 | 0 | 0 | 327.4 | 326 | 296.1 | 281.5 | 60.2 | 59 | 17.9 | 83.8 | 8.5 | 257.7 | 12.2 | 669.8 | 379.9 | 181.7 | 701.7 | 484.3 | 322.5 | 251.9 | 268.7 | 561.4 | 466.8 | 361.3 | 412.8 | 427.7 | 387.5 | 390.2 | 312.2 | 398.1 | 370.9 | 513.1 | 423
2172 | 1978 | -6.8 | 0 | 0 | 327.6 | 325.2 | 295.4 | 281.1 | 61 | 58.8 | 17.9 | 83.7 | 7.6 | 238.5 | 10.3 | 666 | 373.4 | 178.9 | 699 | 482.2 | 315.6 | 243.8 | 263.2 | 559.4 | 463 | 361.5 | 412.5 | 427.3 | 387.5 | 389.6 | 311.4 | 397.6 | 370.3 | 512.3 | 422.8
2173 | 1979 | -6.8 | 0 | 0 | 327.7 | 324.3 | 294.6 | 280.6 | 60.1 | 58.6 | 17.9 | 83.4 | 7 | 267.1 | 8 | 662.2 | 368 | 177 | 695.5 | 480 | 309.1 | 235.5 | 258.4 | 557.7 | 458.5 | 361.6 | 412.3 | 426.9 | 387.5 | 388.9 | 310.6 | 397 | 369.8 | 511.5 | 422.6
2174 | 1980 | -6.8 | 0 | 0 | 327.5 | 323.5 | 293.7 | 280 | 60.1 | 58.3 | 18 | 83.2 | 5.7 | 256.6 | 9.1 | 658 | 363.4 | 174.7 | 692.1 | 478.2 | 303.3 | 214.5 | 254.5 | 553.2 | 454.4 | 361.7 | 412 | 426.5 | 387.6 | 388.2 | 309.9 | 396.6 | 369.2 | 510.8 | 422.4
2175 | 1981 | -6.8 | 0 | 0 | 327.6 | 322.9 | 293.1 | 279.5 | 59.7 | 58.1 | 18 | 82.8 | 5.5 | 250.8 | 9.9 | 654 | 358.2 | 172.6 | 688.1 | 476.3 | 295.3 | 215 | 248 | 548.7 | 449.5 | 361.8 | 411.7 | 426.1 | 387.6 | 387.6 | 309.2 | 396.1 | 368.6 | 510 | 422.2
2176 | 1982 | -6.8 | 0 | 0 | 327.5 | 322.2 | 292.4 | 279 | 58.4 | 57.9 | 18 | 82.6 | 5 | 240.6 | 9.7 | 650.3 | 354.4 | 169.7 | 684.8 | 474.7 | 286.9 | 214.5 | 242.3 | 539.4 | 441.5 | 361.9 | 411.4 | 425.7 | 387.7 | 386.9 | 308.6 | 395.6 | 368 | 509.3 | 421.9
2177 | 1983 | -6.8 | 0 | 0 | 327.2 | 321.3 | 291.5 | 278.6 | 56.2 | 57.7 | 18 | 82.4 | 5.4 | 250.7 | 12.3 | 646.7 | 350.7 | 167.2 | 681.8 | 472.7 | 280.3 | 209.6 | 241.3 | 529 | 429.6 | 361.9 | 411.2 | 425.2 | 387.7 | 386.2 | 307.9 | 395.1 | 367.5 | 508.5 | 421.7
2178 | 1984 | -6.8 | 0 | 0 | 327 | 320.6 | 290.6 | 277.9 | 57.1 | 57.5 | 18 | 82.2 | 4.9 | 246.7 | 13.9 | 643.1 | 347.1 | 165 | 678.9 | 471.2 | 274.6 | 197.3 | 240 | 521.1 | 420.2 | 362.1 | 410.9 | 424.8 | 387.8 | 385.6 | 307.1 | 394.7 | 367 | 507.8 | 421.5
2179 | 1985 | -6.8 | 0 | 0 | 326.4 | 319.9 | 290 | 277.1 | 56.4 | 57.3 | 18 | 82 | 5 | 256.9 | 14.2 | 639.5 | 343.1 | 163.1 | 676 | 469.4 | 261.1 | 179.2 | 238.4 | 514.6 | 412.5 | 362.2 | 410.6 | 424.4 | 387.8 | 385 | 306.4 | 394.2 | 366.4 | 507.1 | 421.3
2180 | 1986 | -6.8 | 0 | 0 | 325.9 | 319.1 | 289.3 | 276.4 | 55 | 57.1 | 18 | 81.7 | 5.4 | 245.8 | 17.7 | 635.7 | 339.7 | 162 | 673.1 | 467.1 | 248 | 169.5 | 237.2 | 507.2 | 405.7 | 362.3 | 410.4 | 424 | 387.9 | 384.3 | 305.8 | 393.7 | 365.9 | 506.3 | 421.1
2181 | 1987 | -6.8 | 0 | 0 | 325.7 | 318.7 | 288.7 | 275.8 | 53.3 | 57 | 18 | 81.5 | 6 | 250.9 | 16.2 | 632.3 | 336.3 | 160 | 667.9 | 465.1 | 244.6 | 158.3 | 235.9 | 500 | 400.1 | 362.3 | 410.1 | 423.6 | 387.9 | 383.7 | 305.2 | 393.2 | 365.4 | 505.6 | 420.9
2182 | 1988 | -6.8 | 0 | 0 | 325.2 | 318.4 | 288 | 275.2 | 53.7 | 56.9 | 18 | 81.3 | 6.1 | 256.5 | 14.3 | 628.8 | 328.8 | 159 | 663.9 | 463.3 | 238.9 | 162.7 | 225.2 | 494 | 397 | 362.4 | 409.8 | 423.2 | 387.9 | 383.3 | 304.6 | 392.7 | 364.8 | 504.9 | 420.6
2183 | 1989 | -6.7 | 0 | 0 | 324.7 | 318.1 | 287.4 | 274.7 | 53 | 56.7 | 18 | 81.2 | 6.5 | 264.6 | 13.9 | 625 | 322.8 | 157.3 | 661 | 461.3 | 233.1 | 168.8 | 220.1 | 487.8 | 394.7 | 362.6 | 409.5 | 422.8 | 388 | 382.8 | 304 | 392.3 | 364.3 | 504.2 | 420.4
2184 | 1990 | -6.8 | 0 | 0 | 324.5 | 317.7 | 287 | 274.2 | 54 | 56.5 | 18 | 81.1 | 6.8 | 259.1 | 13.6 | 620.9 | 318.5 | 155.6 | 659.3 | 459.1 | 227.2 | 172.7 | 218.4 | 480.7 | 392.1 | 362.6 | 409.3 | 422.3 | 388 | 382.1 | 303.2 | 391.9 | 363.8 | 503.5 | 420.2
2185 | 1991 | -6.8 | 0 | 0 | 324.2 | 316.8 | 286.6 | 273.7 | 54.8 | 56.3 | 18 | 81 | 7.8 | 252.4 | 15.8 | 616.6 | 315.4 | 154.1 | 657.6 | 457.4 | 219.8 | 174.4 | 218.6 | 471.8 | 389.9 | 362.7 | 409 | 421.8 | 388.1 | 381.5 | 302.4 | 391.4 | 363.2 | 502.8 | 420
2186 | 1992 | -6.8 | 0 | 0 | 323.9 | 316.1 | 285.9 | 273.2 | 53.4 | 56.1 | 18 | 80.9 | 8 | 241 | 14.1 | 611.9 | 312.2 | 152.1 | 656.3 | 455.9 | 208.8 | 179.1 | 218.1 | 466.6 | 388.2 | 362.8 | 408.7 | 421.4 | 388.1 | 380.9 | 301.6 | 390.9 | 362.7 | 502.1 | 419.8
2187 | 1993 | -6.8 | 0 | 0 | 323.5 | 315.4 | 285.3 | 272.8 | 54.6 | 55.9 | 18 | 80.6 | 7.3 | 252.2 | 11.9 | 609.2 | 306.8 | 149.7 | 654.7 | 454.1 | 195 | 144.8 | 216.5 | 460.6 | 385.2 | 362.9 | 408.4 | 421 | 388.1 | 380.2 | 300.9 | 390.5 | 362.2 | 501.4 | 419.6
2188 | 1994 | -6.8 | 0 | 0 | 322.9 | 315 | 284.8 | 272.5 | 55.7 | 55.8 | 18 | 80.4 | 7.1 | 248.8 | 14.4 | 606.1 | 302.3 | 147.2 | 652.9 | 452.4 | 189.2 | 152 | 214 | 455 | 381.6 | 363 | 408.2 | 420.6 | 388.2 | 379.5 | 300.1 | 390.1 | 361.7 | 500.7 | 419.3
2189 | 1995 | -6.8 | 0 | 0 | 322.5 | 314.3 | 284.4 | 272.1 | 53.3 | 55.6 | 18 | 80.2 | 5.5 | 244.3 | 16.6 | 602.7 | 298.4 | 144.3 | 651.4 | 450.7 | 185.1 | 159.6 | 211.6 | 448.8 | 378.7 | 363.1 | 407.9 | 420.2 | 388.2 | 378.8 | 299.4 | 389.6 | 361.2 | 500.1 | 419.1
2190 | 1996 | -6.8 | 0 | 0 | 322.1 | 313.6 | 283.9 | 271.8 | 52.9 | 55.5 | 18 | 80 | 4.6 | 241.2 | 16.2 | 599.5 | 295.2 | 142.2 | 649.6 | 448.7 | 176.3 | 160.8 | 204.6 | 441.1 | 375.9 | 363.2 | 407.6 | 419.8 | 388.2 | 378.3 | 298.6 | 389.2 | 360.7 | 499.5 | 418.9
2191 | 1997 | -6.8 | 0 | 0 | 321.4 | 312.5 | 283.3 | 271.5 | 53.2 | 55.5 | 18 | 79.8 | 6.4 | 243.5 | 17.2 | 596.6 | 292.9 | 140.5 | 648 | 446.6 | 167.5 | 164.3 | 198.6 | 432.7 | 374 | 363.2 | 407.4 | 419.4 | 388.2 | 377.7 | 297.9 | 388.8 | 360.2 | 498.9 | 418.6
2192 | 1998 | -6.8 | 0 | 0 | 320.7 | 311.5 | 282.9 | 271.1 | 52.5 | 55.5 | 18 | 79.6 | 6.3 | 248.4 | 17.1 | 593.4 | 290.4 | 138.4 | 645.8 | 444.8 | 166 | 165.5 | 196 | 424.2 | 372.2 | 363.3 | 407.1 | 418.9 | 388.2 | 377.2 | 297.1 | 388.3 | 359.6 | 498.2 | 418.4
2193 | 1999 | -6.8 | 0 | 0 | 320.2 | 310.8 | 282.5 | 270.6 | 50.4 | 55.5 | 18 | 79.4 | 6.3 | 246.8 | 16.1 | 589.9 | 287.6 | 134.7 | 643.5 | 442.7 | 159.3 | 163.4 | 193.3 | 416.7 | 369.7 | 363.4 | 406.8 | 418.5 | 388.3 | 376.6 | 296.4 | 387.9 | 359.1 | 497.5 | 418.2
2194 | 2000 | -6.8 | 0 | 0 | 319.4 | 310.1 | 281.9 | 270.2 | 54 | 55.5 | 18 | 79.2 | 6.2 | 250.4 | 14.8 | 586.6 | 284.5 | 132.4 | 641.1 | 440.7 | 146 | 162.6 | 187.3 | 408.3 | 367.1 | 363.5 | 406.5 | 418.1 | 388.3 | 376 | 295.7 | 387.5 | 358.6 | 496.9 | 418
2195 | 2001 | -6.8 | 0 | 0 | 318.9 | 309.9 | 281.4 | 269.9 | 56.4 | 55.4 | 18 | 79 | 5 | 237.2 | 14.5 | 583.5 | 282 | 130.9 | 638.4 | 438.4 | 136.2 | 162.7 | 184.2 | 400.3 | 364.4 | 363.6 | 406.3 | 417.7 | 388.3 | 375.3 | 295 | 387 | 358.1 | 496.2 | 417.8
2196 | 2002 | -6.7 | 0 | 0 | 318.4 | 309.5 | 281.2 | 269.7 | 56.9 | 55.4 | 18 | 78.9 | 4.4 | 243.3 | 14.6 | 580.3 | 278.1 | 128.9 | 635.6 | 436.4 | 129.2 | 161.9 | 184 | 393.3 | 361.4 | 363.6 | 406 | 417.3 | 388.3 | 374.7 | 294.3 | 386.6 | 357.5 | 495.5 | 417.5
2197 | 2003 | -6.8 | 0 | 0 | 317.7 | 308.7 | 280.9 | 269.3 | 55.4 | 55.3 | 18 | 78.7 | 4.4 | 252.1 | 12.3 | 576.4 | 270.6 | 127.1 | 632.8 | 434 | 128.4 | 158.7 | 183 | 386.3 | 358.7 | 363.7 | 405.7 | 416.9 | 388.3 | 374.2 | 293.6 | 386.1 | 357 | 494.9 | 417.3
2198 | 2004 | -6.8 | 0 | 0 | 317.2 | 308 | 280.6 | 268.9 | 51.2 | 55.2 | 18 | 78.4 | 5.5 | 232.5 | 10.6 | 572.4 | 268.2 | 125.3 | 630.8 | 430.6 | 127.2 | 156.1 | 181.7 | 375 | 356.5 | 363.8 | 405.4 | 416.5 | 388.3 | 373.5 | 292.9 | 385.7 | 356.5 | 494.2 | 417
2199 | 2005 | -6.7 | 0 | 0 | 316.6 | 307.7 | 280.2 | 268.5 | 50.3 | 55.2 | 18 | 78.1 | 6.5 | 261.6 | 9.5 | 569 | 265.7 | 125.2 | 628.9 | 427.5 | 121.2 | 145.6 | 180.4 | 363.5 | 354.5 | 363.9 | 405.1 | 416.1 | 388.3 | 372.8 | 292.2 | 385.2 | 356 | 493.5 | 416.8
2200 | 2006 | -6.8 | 0 | 0 | 315.9 | 307.4 | 279.6 | 268.1 | 53.8 | 55.1 | 18 | 78 | 6.7 | 244.2 | 10 | 565.6 | 262.2 | 124.6 | 626.9 | 425.3 | 108 | 142.6 | 178.3 | 353.4 | 351.8 | 363.9 | 404.9 | 415.7 | 388.3 | 372 | 291.5 | 384.8 | 355.4 | 492.9 | 416.6
2201 | 2007 | -6.8 | 0 | 0 | 315 | 307 | 279.2 | 267.7 | 57 | 55 | 18 | 77.8 | 7 | 264.9 | 11.3 | 562.4 | 258.1 | 123.7 | 624.8 | 423.2 | 100.5 | 139 | 174.9 | 345.4 | 347 | 364 | 404.6 | 415.3 | 388.2 | 371.4 | 290.8 | 384.4 | 354.9 | 492.3 | 416.4
2202 | 2008 | -6.7 | 0 | 0 | 314.5 | 306.4 | 278.8 | 267.3 | 57.1 | 54.9 | 18 | 77.7 | 7.3 | 251.5 | 10 | 559.2 | 254.4 | 123 | 622.7 | 421.2 | 97.7 | 141.7 | 172.7 | 337.6 | 341.2 | 364.1 | 404.3 | 414.9 | 388.2 | 370.8 | 290.2 | 384 | 354.4 | 491.6 | 416.1
2203 | 2009 | -6.8 | 0 | 0 | 313.9 | 305.7 | 278.4 | 266.9 | 54.6 | 54.9 | 18 | 77.6 | 6.7 | 261.3 | 8.3 | 556.1 | 249.4 | 122.7 | 620.4 | 419.6 | 90.2 | 141.7 | 170.5 | 331.1 | 336.9 | 364.1 | 403.9 | 414.5 | 388.2 | 370.3 | 289.6 | 383.6 | 353.9 | 491 | 415.9
2204 | 2010 | -6.8 | 0 | 0 | 313.6 | 305.2 | 278 | 266.4 | 54.1 | 54.8 | 18 | 77.5 | 5.5 | 236.9 | 7.9 | 553.1 | 229.4 | 122.1 | 617.6 | 417.9 | 87.7 | 143 | 167.3 | 325.9 | 333.9 | 364.2 | 403.6 | 414.1 | 388.2 | 369.7 | 289.1 | 383.2 | 353.4 | 490.3 | 415.6
2205 | 2011 | -6.7 | 0 | 0 | 312.9 | 304.6 | 277.5 | 266 | 52.7 | 54.7 | 18 | 77.4 | 4.8 | 248.9 | 9.3 | 549.6 | 229.4 | 120.8 | 615.6 | 416.2 | 82.2 | 141.4 | 165.6 | 320.6 | 331.4 | 364.3 | 403.3 | 413.8 | 388.2 | 369.1 | 288.5 | 382.7 | 352.8 | 489.7 | 415.4
2206 | 2012 | -6.7 | 0 | 0 | 312.2 | 303.9 | 277.1 | 265.7 | 53.7 | 54.6 | 18.1 | 77.2 | 5.6 | 236.6 | 11.2 | 546.3 | 221.7 | 120 | 613.5 | 414.7 | 78.6 | 137.3 | 164.1 | 315.9 | 326.2 | 364.3 | 403 | 413.4 | 388.2 | 368.5 | 287.9 | 382.3 | 352.3 | 489 | 415.2
2207 | 2013 | -6.8 | 0 | 0 | 311.7 | 303.1 | 276.8 | 265.3 | 54.2 | 54.5 | 18.1 | 77.1 | 5 | 247.8 | 11.2 | 543 | 217.7 | 119.5 | 610.8 | 412.9 | 75.3 | 128.3 | 162.7 | 308.9 | 318.9 | 364.4 | 402.7 | 413 | 388.2 | 368 | 287.3 | 381.9 | 351.8 | 488.4 | 414.9
2208 | 2014 | -6.7 | 0 | 0 | 311.2 | 302.4 | 276.3 | 265 | 55.6 | 54.4 | 18.1 | 77 | 4.7 | 244 | 10.3 | 539.4 | 214.7 | 118.4 | 608.3 | 411.1 | 71.7 | 126.9 | 161.5 | 300.8 | 312.5 | 364.4 | 402.4 | 412.6 | 388.1 | 367.5 | 286.9 | 381.4 | 351.3 | 487.8 | 414.7
2209 | 2015 | -6.7 | 0 | 0 | 310.6 | 301.6 | 276.1 | 264.7 | 55.9 | 54.4 | 18.1 | 76.8 | 5.2 | 234.1 | 11.9 | 535.5 | 212.3 | 117.2 | 607.2 | 409.2 | 71.4 | 126.4 | 159.4 | 294.8 | 307.2 | 364.5 | 402.2 | 412.2 | 388.1 | 367 | 286.3 | 380.8 | 350.8 | 487.1 | 414.4
2210 | 2016 | -6.8 | 0 | 0 | 310.2 | 301.4 | 275.9 | 264.3 | 56.9 | 54.3 | 18.1 | 76.7 | 4.9 | 242.3 | 12.1 | 531.8 | 206.7 | 116 | 605.5 | 407.6 | 72.1 | 87.9 | 156.6 | 289.8 | 303.2 | 364.5 | 401.9 | 411.7 | 388.1 | 366.4 | 285.7 | 380.4 | 350.3 | 486.5 | 414.2
2211 | 2017 | -6.8 | 0 | 0 | 309.5 | 300.8 | 275.6 | 263.9 | 54.4 | 54.2 | 18.1 | 76.5 | 4.8 | 248.6 | 12 | 528.2 | 199.5 | 114.9 | 602.6 | 406.2 | 71.9 | 73.7 | 154.5 | 285.4 | 300.7 | 364.6 | 401.7 | 411.4 | 388.1 | 365.8 | 285.2 | 380 | 349.7 | 485.9 | 414
2212 | 2018 | -6.7 | 0 | 0 | 309 | 300.3 | 275.2 | 263.5 | 53.2 | 54.2 | 18.1 | 76.3 | 5.1 | 240.7 | 12.4 | 524.6 | 191.3 | 113.8 | 599.8 | 404.3 | 73 | 72.4 | 152.2 | 281 | 299.5 | 364.6 | 401.4 | 411 | 388.1 | 365.3 | 284.6 | 379.6 | 349.3 | 485.3 | 413.7
2213 | 2019 | -6.7 | 0 | 0 | 308.7 | 300.1 | 275 | 263.1 | 55 | 54.2 | 18.1 | 76.2 | 5.9 | 228.2 | 12 | 520.8 | 186.4 | 112.9 | 597.3 | 402.5 | 74 | 72.3 | 148.5 | 276.8 | 299.3 | 364.7 | 401.1 | 410.6 | 388 | 364.8 | 284.1 | 379.2 | 348.7 | 484.6 | 413.5
2214 | 2020 | -6.7 | 0 | 0 | 308.3 | 300.1 | 274.7 | 262.8 | 56.9 | 54.1 | 18.1 | 76 | 5.8 | 245.8 | 10.3 | 517.1 | 180.9 | 112.2 | 594.5 | 400.8 | 73.2 | 70.9 | 131.1 | 272.6 | 298.5 | 364.8 | 400.8 | 410.2 | 388 | 364.3 | 283.6 | 378.8 | 348.2 | 484 | 413.2
2215 | 2021 | -6.7 | 0 | 0 | 307.6 | 299.9 | 274.2 | 262.4 | 56.6 | 54.1 | 18.1 | 75.8 | 5.1 | 252.8 | 10.1 | 513.1 | 179.4 | 110.6 | 592.2 | 399 | 76.3 | 77.7 | 127.8 | 262.6 | 296.6 | 364.8 | 400.6 | 409.8 | 388 | 363.9 | 283.1 | 378.3 | 347.6 | 483.3 | 413
2216 | 2022 | -6.7 | 0 | 0 | 306.9 | 299.6 | 273.9 | 262 | 57.8 | 54 | 18.1 | 75.7 | 5.3 | 252.3 | 11 | 509.5 | 178.6 | 109.9 | 590 | 397.1 | 72.5 | 74.1 | 128.9 | 249.7 | 294.6 | 364.9 | 400.3 | 409.4 | 388 | 363.4 | 282.6 | 377.9 | 347.1 | 482.7 | 412.7
2217 | 2023 | -6.7 | 0 | 0 | 306.2 | 299.1 | 273.6 | 261.7 | 57 | 54 | 18.1 | 75.5 | 4.9 | 246.1 | 12.2 | 506 | 178.1 | 106.1 | 586.6 | 395.4 | 69.3 | 71.6 | 129.4 | 224.5 | 292.3 | 364.9 | 400 | 409.1 | 387.9 | 363 | 282 | 377.4 | 346.6 | 482.1 | 412.4
2218 | 2024 | -6.7 | 0 | 0 | 305.6 | 298.4 | 273.3 | 261.3 | 53.1 | 53.9 | 18.1 | 75.3 | 5 | 259.8 | 11.6 | 502.5 | 177.2 | 105 | 583.3 | 393.7 | 67.3 | 72.3 | 130.6 | 224.6 | 289.7 | 365 | 399.7 | 408.7 | 387.9 | 362.6 | 281.5 | 377 | 346.1 | 481.4 | 412.2
2219 | 2025 | -6.8 | 0 | 0 | 305.4 | 297.7 | 273 | 260.9 | 55.8 | 53.9 | 18.1 | 75.2 | 5 | 258.7 | 11.8 | 498.8 | 174.8 | 104.1 | 580.2 | 391.9 | 66.4 | 73.9 | 131.2 | 220.4 | 286.4 | 365 | 399.4 | 408.3 | 387.9 | 362.2 | 281 | 376.5 | 345.6 | 480.8 | 412
2220 | 2026 | -6.7 | 0 | 0 | 304.8 | 296.9 | 272.6 | 260.6 | 55.8 | 53.8 | 18.1 | 75.1 | 4.8 | 258.1 | 11.5 | 495.2 | 169.1 | 102.6 | 576.9 | 390.6 | 72.3 | 74 | 131.2 | 214.2 | 282.2 | 365 | 399.2 | 407.9 | 387.8 | 361.7 | 280.5 | 375.9 | 345.1 | 480.2 | 411.7
2221 | 2027 | -6.7 | 0 | 0 | 304.2 | 296.2 | 272.2 | 260.2 | 55.5 | 53.7 | 18.1 | 75 | 4.6 | 246.1 | 10.1 | 491.6 | 164.4 | 101.4 | 573.9 | 389.1 | 75.5 | 77.5 | 130.4 | 210.2 | 275 | 365.1 | 398.9 | 407.6 | 387.8 | 361.2 | 279.9 | 375.4 | 344.6 | 479.6 | 411.4
2222 | 2028 | -6.7 | 0 | 0 | 303.6 | 295.7 | 271.7 | 259.7 | 56.6 | 53.7 | 18.1 | 74.8 | 4.2 | 258.6 | 11.5 | 488 | 157.8 | 100.5 | 570.6 | 387.3 | 72.9 | 81.3 | 130.6 | 207.4 | 266.7 | 365.1 | 398.6 | 407.2 | 387.8 | 360.7 | 279.2 | 374.9 | 344.1 | 479 | 411.2
2223 | 2029 | -6.7 | 0 | 0 | 303.1 | 295.1 | 271.3 | 259.4 | 56.2 | 53.7 | 18.1 | 74.6 | 4.4 | 257.7 | 11.8 | 484.1 | 140.7 | 99.3 | 567.5 | 385.6 | 72.2 | 81.7 | 130.9 | 201.2 | 259 | 365.1 | 398.4 | 406.8 | 387.7 | 360.3 | 278.6 | 374.5 | 343.6 | 478.3 | 411
2224 | 2030 | -6.7 | 0 | 0 | 302.8 | 294.4 | 271 | 258.9 | 53.7 | 53.5 | 18.1 | 74.5 | 4.4 | 259.7 | 10.6 | 479.8 | 125.1 | 98.1 | 564.1 | 384.1 | 74.8 | 80.5 | 130.5 | 198.6 | 253.2 | 365.2 | 398.1 | 406.3 | 387.7 | 359.9 | 278.2 | 374.1 | 343.1 | 477.7 | 410.7
2225 | 2031 | -6.7 | 0 | 0 | 302.4 | 293.8 | 270.6 | 258.4 | 52.6 | 53.4 | 18.1 | 74.5 | 4.4 | 250.5 | 9.5 | 475.8 | 130.1 | 96.6 | 561.2 | 382.6 | 71.3 | 73.4 | 129.7 | 197.4 | 248.9 | 365.2 | 397.8 | 406 | 387.7 | 359.5 | 277.6 | 373.6 | 342.5 | 477.1 | 410.5
2226 | 2032 | -6.7 | 0 | 0 | 301.6 | 293.3 | 270.2 | 257.9 | 54.7 | 53.3 | 18.1 | 74.5 | 4.5 | 248.5 | 9.5 | 471.4 | 133.2 | 94.8 | 558.3 | 380.8 | 73.2 | 76.3 | 129.4 | 196.2 | 244.4 | 365.3 | 397.5 | 405.6 | 387.6 | 358.9 | 277 | 373.1 | 342 | 476.5 | 410.2
2227 | 2033 | -6.7 | 0 | 0 | 300.9 | 292.9 | 269.9 | 257.6 | 56.4 | 53.2 | 18.1 | 74.4 | 5.5 | 248.5 | 9.5 | 467.4 | 133.8 | 93.7 | 555.1 | 379.2 | 69.5 | 74.2 | 128.4 | 185.5 | 235.1 | 365.3 | 397.3 | 405.2 | 387.6 | 358.5 | 276.5 | 372.7 | 341.6 | 475.9 | 410
2228 | 2034 | -6.7 | 0 | 0 | 300.4 | 292.5 | 269.7 | 257.2 | 57.5 | 53.2 | 18.1 | 74.2 | 5.7 | 248.7 | 8.9 | 463.2 | 135.6 | 92.7 | 551.8 | 377.6 | 70.5 | 76.8 | 127.7 | 187.4 | 215.3 | 365.3 | 397 | 404.8 | 387.5 | 358 | 275.8 | 372.2 | 341 | 475.3 | 409.7
2229 | 2035 | -6.7 | 0 | 0 | 299.7 | 292.1 | 269.4 | 256.8 | 53.4 | 53.1 | 18.1 | 74.1 | 5.8 | 249.8 | 8.9 | 459 | 135.4 | 91.8 | 547.7 | 376.1 | 78.5 | 82 | 126.1 | 186.9 | 170.2 | 365.4 | 396.7 | 404.4 | 387.5 | 357.8 | 275.3 | 371.8 | 340.5 | 474.7 | 409.4
2230 | 2036 | -6.7 | 0 | 0 | 299.1 | 291.8 | 269.1 | 256.5 | 51.4 | 53.1 | 18.1 | 73.9 | 5.9 | 242.4 | 9.6 | 455.1 | 135.9 | 91.4 | 543.4 | 374.7 | 75.3 | 82.1 | 125.6 | 178 | 109.5 | 365.4 | 396.4 | 404.1 | 387.4 | 357.3 | 274.8 | 371.3 | 340 | 474.1 | 409.2
2231 | 2037 | -6.7 | 0 | 0 | 298.8 | 291.3 | 268.8 | 256.2 | 49.8 | 53 | 18.1 | 73.7 | 7 | 228.6 | 9.8 | 450.9 | 133.3 | 90.8 | 538.9 | 372.7 | 74.6 | 77.5 | 124.2 | 170.3 | 92.4 | 365.4 | 396.1 | 403.7 | 387.4 | 356.8 | 274.2 | 370.8 | 339.5 | 473.5 | 408.9
2232 | 2038 | -6.7 | 0 | 0 | 298.4 | 290.7 | 268.4 | 255.9 | 50.8 | 53 | 18.1 | 73.5 | 7.5 | 236.5 | 9.9 | 446.8 | 133 | 90.1 | 534.3 | 370.6 | 73.1 | 81.2 | 123.6 | 148.1 | 89.3 | 365.5 | 395.8 | 403.3 | 387.3 | 356.3 | 273.5 | 370.4 | 339 | 472.9 | 408.7
2233 | 2039 | -6.7 | 0 | 0 | 298 | 290.4 | 268.1 | 255.5 | 52.7 | 52.9 | 18.1 | 73.3 | 7.3 | 255.6 | 10.8 | 442.8 | 132.1 | 89.6 | 529.8 | 368.8 | 73.2 | 81 | 123.3 | 138.6 | 87.2 | 365.5 | 395.5 | 402.9 | 387.2 | 355.8 | 273 | 370 | 338.5 | 472.3 | 408.4
2234 | 2040 | -6.7 | 0 | 0 | 297.6 | 290 | 267.8 | 255.1 | 51.5 | 52.9 | 18.1 | 73.1 | 5.8 | 252.4 | 12.9 | 438.9 | 132.1 | 89.1 | 524.9 | 367.4 | 74.4 | 76.9 | 122.8 | 133.8 | 86.9 | 365.5 | 395.2 | 402.6 | 387.2 | 355.2 | 272.5 | 369.5 | 338 | 471.7 | 408.2
2235 | 2041 | -6.7 | 0 | 0 | 297.1 | 289.6 | 267.4 | 254.8 | 53.6 | 52.8 | 18.1 | 73 | 4.1 | 259.4 | 15.3 | 435.1 | 130.9 | 88.6 | 519.6 | 366.2 | 75.1 | 75.9 | 121.9 | 131.7 | 86.8 | 365.5 | 394.9 | 402.2 | 387.1 | 354.8 | 271.9 | 369.1 | 337.5 | 471.1 | 407.9
2236 | 2042 | -6.8 | 0 | 0 | 296.6 | 288.9 | 267.1 | 254.3 | 53.1 | 52.6 | 18.1 | 72.9 | 5 | 254.4 | 15.7 | 431.4 | 131.2 | 88 | 514.7 | 365 | 73.3 | 82 | 121.4 | 129.8 | 85.8 | 365.6 | 394.7 | 401.8 | 387 | 354.3 | 271.2 | 368.6 | 337 | 470.6 | 407.6
2237 | 2043 | -6.7 | 0 | 0 | 296.1 | 288.1 | 266.9 | 254 | 50.4 | 52.5 | 18.1 | 72.8 | 6.4 | 255.5 | 15.3 | 427.6 | 130.5 | 87.4 | 510 | 363.5 | 71.4 | 84.1 | 120.8 | 127.7 | 85.4 | 365.6 | 394.4 | 401.3 | 387 | 353.9 | 270.7 | 368.2 | 336.6 | 470 | 407.4
2238 | 2044 | -6.7 | 0 | 0 | 295.9 | 287.5 | 266.6 | 253.6 | 52.7 | 52.4 | 18.2 | 72.6 | 6.7 | 237.7 | 12 | 423.7 | 129.6 | 86.2 | 505.4 | 361.9 | 68.9 | 80.5 | 119.2 | 126.2 | 83.6 | 365.6 | 394.1 | 401 | 386.9 | 353.5 | 270 | 367.8 | 336.1 | 469.4 | 407.1
2239 | 2045 | -6.8 | 0 | 0 | 295.5 | 287.2 | 266.2 | 253.2 | 52.5 | 52.2 | 18.2 | 72.5 | 6.9 | 259.8 | 15.4 | 419.8 | 129.4 | 85.6 | 500.8 | 360.2 | 65 | 77.8 | 117.3 | 124.2 | 81.5 | 365.7 | 393.9 | 400.6 | 386.8 | 353.2 | 269.2 | 367.4 | 335.6 | 468.8 | 406.9
2240 | 2046 | -6.8 | 0 | 0 | 295.1 | 287.1 | 265.8 | 252.9 | 52.1 | 52.1 | 18.2 | 72.4 | 7.5 | 259.2 | 18.1 | 415.9 | 128.1 | 83.5 | 496.2 | 358.4 | 65.6 | 77.9 | 116 | 122.3 | 81.2 | 365.7 | 393.6 | 400.3 | 386.8 | 352.7 | 268.4 | 367 | 335.1 | 468.2 | 406.6
2241 | 2047 | -6.7 | 0 | 0 | 294.4 | 286.9 | 265.6 | 252.7 | 51.9 | 52 | 18.2 | 72.3 | 6.7 | 263.9 | 19.6 | 412.1 | 127.5 | 78.3 | 491.6 | 356.5 | 67.5 | 82 | 115.3 | 119.3 | 81.2 | 365.7 | 393.3 | 399.9 | 386.7 | 352.6 | 267.7 | 366.6 | 334.6 | 467.6 | 406.3
2242 | 2048 | -6.7 | 0 | 0 | 294 | 286.4 | 265.3 | 252.3 | 51.4 | 51.8 | 18.2 | 72.2 | 7.5 | 271.5 | 17.7 | 408.3 | 124 | 77.4 | 487 | 355 | 68.7 | 82.2 | 114.7 | 116.7 | 81.1 | 365.7 | 393 | 399.6 | 386.7 | 352.2 | 267 | 366.3 | 334.2 | 467.1 | 406.1
2243 | 2049 | -6.8 | 0 | 0 | 293.7 | 285.7 | 265 | 251.9 | 52.8 | 51.6 | 18.2 | 72.1 | 7.9 | 253.2 | 17.5 | 404.4 | 120.5 | 77.2 | 482.7 | 353.4 | 67.1 | 83.9 | 114.1 | 113.9 | 80.7 | 365.8 | 392.7 | 399.2 | 386.6 | 351.9 | 266.3 | 365.9 | 333.7 | 466.5 | 405.8
2244 | 2050 | -6.8 | 0 | 0 | 293.1 | 285.4 | 264.7 | 251.5 | 54 | 51.5 | 18.2 | 71.9 | 7.9 | 241.8 | 19.1 | 400.6 | 118 | 77.3 | 478.6 | 352.2 | 66.3 | 83.2 | 113 | 111.1 | 79.4 | 365.8 | 392.4 | 398.8 | 386.6 | 351.5 | 265.5 | 365.5 | 333.3 | 465.9 | 405.5
2245 | 2051 | -6.8 | 0 | 0 | 293.1 | 284.8 | 264.2 | 251.2 | 52.4 | 51.4 | 18.2 | 71.6 | 8.8 | 253.8 | 19.3 | 396.8 | 115.7 | 77.5 | 474.5 | 350.6 | 68.9 | 80.9 | 112.4 | 109.5 | 78.4 | 365.8 | 392.1 | 398.5 | 386.5 | 351 | 264.9 | 365.1 | 332.8 | 465.3 | 405.2
2246 | 2052 | -6.8 | 0 | 0 | 292.9 | 284.3 | 263.7 | 251 | 51 | 51.3 | 18.2 | 71.5 | 10.1 | 259.2 | 20.2 | 393.1 | 115.3 | 77.5 | 470.4 | 349.1 | 68.2 | 80.1 | 111 | 106.9 | 77.6 | 365.8 | 391.9 | 398.1 | 386.5 | 350.6 | 264.3 | 364.7 | 332.3 | 464.8 | 405
2247 | 2053 | -6.8 | 0 | 0 | 292.3 | 283.8 | 263.3 | 250.7 | 45.4 | 51.1 | 18.2 | 71.3 | 11 | 251.1 | 22.9 | 389.4 | 114.2 | 77.6 | 466.3 | 347.8 | 62.6 | 77.4 | 109.8 | 106.9 | 76.1 | 365.9 | 391.6 | 397.7 | 386.4 | 350.4 | 263.8 | 364.4 | 331.8 | 464.2 | 404.7
2248 | 2054 | -6.8 | 0 | 0 | 292.1 | 283.1 | 262.9 | 250.2 | 45.1 | 51 | 18.2 | 71.1 | 10.8 | 254.1 | 26.1 | 385.7 | 114 | 77.3 | 462.3 | 346.5 | 64.1 | 80.4 | 109 | 104.8 | 75.1 | 365.9 | 391.4 | 397.3 | 386.3 | 350.1 | 263.4 | 364 | 331.4 | 463.6 | 404.4
2249 | 2055 | -6.8 | 0 | 0 | 291.9 | 282.3 | 262.4 | 249.7 | 45.4 | 51 | 18.2 | 70.9 | 10.9 | 245.1 | 29.7 | 382 | 113.1 | 76.7 | 458.6 | 345.1 | 65.9 | 79.4 | 108.1 | 103 | 74.2 | 365.9 | 391.1 | 397 | 386.2 | 349.7 | 263.2 | 363.7 | 330.9 | 463.1 | 404.2
2250 | 2056 | -6.8 | 0 | 0 | 291.6 | 282 | 261.8 | 249.1 | 43.4 | 51 | 18.2 | 70.7 | 11.5 | 250.3 | 27.9 | 378.3 | 111.1 | 76 | 454.5 | 343.7 | 68.3 | 76.1 | 105.4 | 102 | 73.7 | 365.9 | 390.8 | 396.6 | 386.2 | 349.2 | 262.8 | 363.3 | 330.4 | 462.5 | 403.9
2251 | 2057 | -6.8 | 0 | 0 | 291.4 | 281.7 | 261.3 | 248.6 | 45.9 | 50.9 | 18.2 | 70.5 | 13 | 251.5 | 24.9 | 374.3 | 108.7 | 75.2 | 450.1 | 341.5 | 65.7 | 78 | 104.4 | 100 | 73.9 | 366 | 390.6 | 396.3 | 386.1 | 348.7 | 262.5 | 362.9 | 330 | 462 | 403.7
2252 | 2058 | -6.7 | 0 | 0 | 291.1 | 281.1 | 260.8 | 248.1 | 48.8 | 50.9 | 18.2 | 70.3 | 12.8 | 236.9 | 23 | 370.1 | 105.7 | 74 | 445.8 | 339.3 | 63.4 | 76 | 104.1 | 98.6 | 74.6 | 366 | 390.3 | 395.9 | 386 | 348.5 | 262.2 | 362.6 | 329.5 | 461.4 | 403.4
2253 | 2059 | -6.8 | 0 | 0 | 290.7 | 280.6 | 260.3 | 247.7 | 48.1 | 50.8 | 18.2 | 70.1 | 10.3 | 246.6 | 21 | 366.2 | 102.9 | 72.8 | 441.5 | 337.8 | 65.6 | 78.3 | 103 | 97.4 | 74.4 | 366 | 390 | 395.5 | 385.9 | 348.2 | 261.8 | 362.2 | 329.1 | 460.8 | 403.1
2254 | 2060 | -6.7 | 0 | 0 | 290.2 | 279.9 | 259.9 | 247.5 | 45.1 | 50.7 | 18.2 | 70 | 8.2 | 241.3 | 23.5 | 361.9 | 101 | 71.8 | 437.5 | 336.1 | 65.4 | 79.8 | 101.2 | 97 | 74.4 | 366 | 389.7 | 395.1 | 385.8 | 347.8 | 261.6 | 361.9 | 328.6 | 460.3 | 402.9
2255 | 2061 | -6.7 | 0 | 0 | 289.4 | 279.6 | 259.5 | 247.1 | 41.1 | 50.7 | 18.2 | 69.8 | 8 | 237.5 | 26.2 | 356.5 | 99.5 | 71 | 433.6 | 334.5 | 63.7 | 79.3 | 100.3 | 96.3 | 74.4 | 366 | 389.5 | 394.7 | 385.7 | 347.3 | 261.3 | 361.6 | 328.2 | 459.7 | 402.6
2256 | 2062 | -6.8 | 0 | 0 | 288.7 | 279.4 | 259.2 | 246.6 | 45.7 | 50.6 | 18.2 | 69.6 | 7.9 | 256.2 | 21.6 | 351.8 | 97.9 | 70.2 | 429.7 | 332.8 | 62.8 | 76.8 | 99.7 | 95.4 | 73.7 | 366 | 389.2 | 394.4 | 385.6 | 346.7 | 261 | 361.3 | 327.7 | 459.1 | 402.3
2257 | 2063 | -6.8 | 0 | 0 | 287.9 | 279.3 | 258.7 | 246.2 | 46.7 | 50.5 | 18.2 | 69.4 | 8.3 | 263.9 | 19.2 | 347.6 | 97.2 | 69.6 | 426 | 331.4 | 64.8 | 76.5 | 99.2 | 94.9 | 72.3 | 366 | 388.9 | 394 | 385.6 | 346.4 | 260.5 | 361 | 327.3 | 458.6 | 402.1
2258 | 2064 | -6.8 | 0 | 0 | 287.4 | 279.1 | 258.3 | 246 | 47 | 50.5 | 18.2 | 69.2 | 7 | 252.9 | 20.8 | 343.3 | 92.8 | 69.3 | 422.1 | 329.5 | 63.4 | 79.1 | 98.7 | 95.4 | 71.3 | 366.1 | 388.6 | 393.7 | 385.5 | 346.1 | 259.9 | 360.5 | 326.8 | 458 | 401.8
2259 | 2065 | -6.8 | 0 | 0 | 287 | 278.8 | 258 | 245.8 | 48.8 | 50.4 | 18.2 | 69.1 | 7.6 | 249.7 | 18.2 | 339.1 | 92.4 | 69 | 418.1 | 327.9 | 64.3 | 80.5 | 98.1 | 95.2 | 69.2 | 366.1 | 388.3 | 393.4 | 385.4 | 345.6 | 259.3 | 360.1 | 326.3 | 457.5 | 401.5
2260 | 2066 | -6.7 | 0 | 0 | 286.7 | 278.7 | 257.7 | 245.5 | 47.2 | 50.4 | 18.2 | 68.9 | 8.7 | 244.4 | 22 | 335.3 | 91.4 | 68.2 | 414.3 | 326.4 | 65.3 | 80.8 | 97.5 | 94 | 69.6 | 366.1 | 388 | 393 | 385.3 | 345.2 | 258.7 | 359.8 | 325.8 | 456.9 | 401.3
2261 | 2067 | -6.7 | 0 | 0 | 286.4 | 278.2 | 257.4 | 245.2 | 46.4 | 50.4 | 18.2 | 68.7 | 8.2 | 241.7 | 20.4 | 331.5 | 90.2 | 67.2 | 410.6 | 324.7 | 64.7 | 80.7 | 96.9 | 93.6 | 70 | 366.1 | 387.7 | 392.6 | 385.2 | 344.9 | 258.1 | 359.4 | 325.4 | 456.4 | 401
2262 | 2068 | -6.8 | 0 | 0 | 286.1 | 277.3 | 257.1 | 244.9 | 43.8 | 50.4 | 18.2 | 68.5 | 7.4 | 243.9 | 20.7 | 327.8 | 86.6 | 66.7 | 406.8 | 322.9 | 64.3 | 80 | 96.4 | 93.5 | 71.1 | 366.1 | 387.4 | 392.3 | 385.1 | 344.4 | 257.4 | 359.1 | 325 | 455.8 | 400.7
2263 | 2069 | -6.8 | 0 | 0 | 285.8 | 276.6 | 256.8 | 244.6 | 46.3 | 50.3 | 18.2 | 68.3 | 8.3 | 247.9 | 18.3 | 324.3 | 86.4 | 66.4 | 402.9 | 321.3 | 66 | 80.4 | 95.1 | 93.4 | 71.7 | 366.1 | 387.2 | 392 | 385 | 343.8 | 257 | 358.7 | 324.6 | 455.3 | 400.5
2264 | 2070 | -6.8 | 0 | 0 | 285.7 | 276.5 | 256.5 | 244.2 | 44.7 | 50.3 | 18.2 | 68.1 | 7.9 | 249.7 | 20.7 | 320.9 | 83.4 | 66.1 | 399.6 | 319.5 | 64.8 | 80.1 | 94 | 93.1 | 72 | 366.1 | 386.9 | 391.6 | 384.9 | 343.3 | 256.5 | 358.3 | 324.2 | 454.8 | 400.2
2265 | 2071 | -6.7 | 0 | 0 | 285.5 | 276.5 | 256.2 | 243.7 | 44.2 | 50.2 | 18.2 | 67.8 | 7.6 | 240.9 | 18.2 | 317.4 | 79.3 | 65.9 | 396.1 | 317.9 | 63.9 | 81.6 | 93.7 | 92.9 | 71.9 | 366.1 | 386.6 | 391.2 | 384.8 | 342.7 | 256 | 357.9 | 323.7 | 454.2 | 399.9
2266 | 2072 | -6.7 | 0 | 0 | 285 | 276.1 | 255.9 | 243.3 | 45.2 | 50.2 | 18.2 | 67.5 | 7.7 | 259.9 | 15 | 313.7 | 77.8 | 65.6 | 391.8 | 316 | 65.9 | 79.6 | 93.5 | 92.7 | 72 | 366.1 | 386.3 | 390.9 | 384.7 | 342 | 255.7 | 357.5 | 323.3 | 453.7 | 399.7
2267 | 2073 | -6.7 | 0 | 0 | 284.4 | 275.9 | 255.5 | 243 | 46.2 | 50.1 | 18.2 | 67.3 | 10.8 | 264.9 | 13.5 | 310.1 | 77.6 | 65.3 | 389 | 314.1 | 65.3 | 79.7 | 93.8 | 92.5 | 72.3 | 366.1 | 386.1 | 390.5 | 384.6 | 341.5 | 255.4 | 357.2 | 322.9 | 453.1 | 399.4
2268 | 2074 | -6.7 | 0 | 0 | 283.9 | 275.5 | 255.2 | 242.8 | 47 | 50 | 18.2 | 67.1 | 10.5 | 246.7 | 12.7 | 306.6 | 76.4 | 65 | 385.6 | 312.3 | 64.9 | 78.5 | 94.6 | 89.9 | 72.1 | 366.1 | 385.8 | 390.2 | 384.5 | 341 | 255 | 356.8 | 322.5 | 452.6 | 399.1
2269 | 2075 | -6.8 | 0 | 0 | 283.7 | 274.8 | 255 | 242.6 | 48.5 | 49.9 | 18.2 | 67 | 10.6 | 240.2 | 11.7 | 303.1 | 73.7 | 64.8 | 382.5 | 310.5 | 63.7 | 78.4 | 95.1 | 87.3 | 72 | 366.1 | 385.5 | 389.8 | 384.4 | 340.7 | 254.5 | 356.5 | 322.1 | 452.1 | 398.9
2270 | 2076 | -6.7 | 0 | 0 | 283.4 | 274.3 | 254.8 | 242.2 | 47.3 | 49.8 | 18.3 | 66.9 | 8.9 | 235.9 | 16.5 | 299.6 | 71.4 | 64.6 | 378.7 | 308.4 | 64.5 | 78.5 | 96.3 | 88.3 | 71.1 | 366.1 | 385.2 | 389.5 | 384.3 | 340.3 | 254 | 356.1 | 321.7 | 451.5 | 398.6
2271 | 2077 | -6.8 | 0 | 0 | 283 | 273.6 | 254.7 | 241.8 | 48.7 | 49.8 | 18.3 | 66.8 | 8.2 | 240.2 | 21 | 296.1 | 73 | 64.3 | 375.4 | 306.1 | 63.7 | 75.7 | 97.5 | 88.9 | 70.4 | 366.1 | 385 | 389.2 | 384.2 | 340 | 253.4 | 355.7 | 321.2 | 451 | 398.4
2272 | 2078 | -6.8 | 0 | 0 | 282.8 | 272.9 | 254.5 | 241.6 | 47.8 | 49.7 | 18.3 | 66.7 | 8.1 | 234.3 | 19.5 | 292.6 | 71.2 | 64 | 372.2 | 303.7 | 64 | 76.4 | 97.8 | 87.9 | 70.6 | 366.1 | 384.7 | 388.8 | 384.1 | 339.7 | 252.8 | 355.4 | 320.8 | 450.4 | 398.1
2273 | 2079 | -6.7 | 0 | 0 | 282.7 | 272.4 | 254.3 | 241.3 | 47.6 | 49.6 | 18.3 | 66.5 | 7.6 | 235.3 | 18.3 | 289 | 69.6 | 63.6 | 368.3 | 301.2 | 63.4 | 77.6 | 98.2 | 85.7 | 71 | 366.1 | 384.5 | 388.5 | 384 | 339.2 | 252.1 | 355 | 320.2 | 449.9 | 397.8
2274 | 2080 | -6.7 | 0 | 0 | 282.4 | 272.1 | 254.1 | 241 | 44.1 | 49.6 | 18.3 | 66.4 | 8.2 | 249.1 | 18.7 | 285.4 | 69 | 63.3 | 364.3 | 298.5 | 63.4 | 75.3 | 99 | 87.8 | 71.2 | 366.1 | 384.2 | 388.1 | 383.9 | 338.9 | 251.4 | 354.6 | 319.8 | 449.4 | 397.6
2275 | 2081 | -6.8 | 0 | 0 | 282 | 272.2 | 253.7 | 240.6 | 45.7 | 49.5 | 18.3 | 66.3 | 8.5 | 238.4 | 18.9 | 281.3 | 69.6 | 63.2 | 360.6 | 295.4 | 63.2 | 75.8 | 99.2 | 88.6 | 71.3 | 366.1 | 383.9 | 387.8 | 383.8 | 338.6 | 250.7 | 354.3 | 319.4 | 448.8 | 397.3
2276 | 2082 | -6.8 | 0 | 0 | 281.1 | 272.1 | 253.3 | 240.1 | 44.9 | 49.3 | 18.3 | 66.2 | 6.9 | 225.8 | 18.4 | 277.6 | 70.1 | 62.9 | 358.4 | 291.3 | 63.4 | 77.8 | 99.1 | 88.9 | 71.3 | 366.1 | 383.6 | 387.4 | 383.7 | 338.4 | 250.2 | 354 | 319 | 448.3 | 397
2277 | 2083 | -6.8 | 0 | 0 | 280.7 | 271.9 | 253 | 239.8 | 45.5 | 49.2 | 18.3 | 66.1 | 5.7 | 237.1 | 16.4 | 274.1 | 68.5 | 62.8 | 353.6 | 285.8 | 62.4 | 76.3 | 98.9 | 88.9 | 71.2 | 366.1 | 383.4 | 387.1 | 383.7 | 338 | 249.7 | 353.6 | 318.6 | 447.8 | 396.7
2278 | 2084 | -6.8 | 0 | 0 | 280.4 | 271.8 | 252.8 | 239.6 | 50.2 | 49 | 18.3 | 66 | 4.3 | 222.2 | 13.2 | 270.5 | 67.3 | 62.4 | 351.3 | 277.5 | 62.7 | 77.7 | 98.5 | 89.1 | 71.2 | 366 | 383.1 | 386.8 | 383.6 | 337.6 | 249.3 | 353.2 | 318.2 | 447.3 | 396.4
2279 | 2085 | -6.8 | 0 | 0 | 280.1 | 271.3 | 252.7 | 239.3 | 49.3 | 48.9 | 18.3 | 65.8 | 4.7 | 234.9 | 11.9 | 267 | 66.5 | 62 | 348.8 | 264.2 | 61.9 | 76.8 | 97.9 | 88.5 | 70 | 366 | 382.8 | 386.4 | 383.5 | 337.2 | 249 | 352.9 | 317.8 | 446.7 | 396.2
2280 | 2086 | -6.7 | 0 | 0 | 279.8 | 270.8 | 252.6 | 239 | 46.7 | 48.7 | 18.3 | 65.8 | 5.2 | 223.1 | 11.6 | 263.2 | 66.4 | 61.7 | 346 | 244.6 | 63.5 | 75.9 | 97.3 | 88.9 | 69.4 | 366 | 382.6 | 386.1 | 383.4 | 336.6 | 248.6 | 352.6 | 317.4 | 446.2 | 395.9
2281 | 2087 | -6.8 | 0 | 0 | 279.4 | 270.4 | 252.4 | 238.8 | 47.3 | 48.6 | 18.3 | 65.7 | 5.4 | 221.4 | 12.5 | 259.6 | 64.5 | 61.3 | 342.7 | 220.1 | 64.7 | 78.7 | 96.8 | 88.4 | 69.3 | 366 | 382.3 | 385.8 | 383.3 | 336.1 | 248.3 | 352.3 | 317 | 445.7 | 395.6
2282 | 2088 | -6.7 | 0 | 0 | 279.1 | 270.1 | 252.2 | 238.7 | 49.3 | 48.4 | 18.3 | 65.6 | 5.9 | 223.9 | 13.2 | 256.7 | 62.5 | 60.6 | 339.6 | 191.4 | 63.1 | 76.7 | 96.7 | 88.4 | 69.4 | 366 | 382.1 | 385.4 | 383.2 | 335.9 | 248 | 351.9 | 316.6 | 445.2 | 395.3
2283 | 2089 | -6.8 | 0 | 0 | 278.7 | 269.7 | 252 | 238.6 | 47.4 | 48.4 | 18.3 | 65.6 | 6.2 | 223.8 | 10.2 | 253.8 | 62.4 | 59.9 | 336.7 | 165 | 61.7 | 74.6 | 96.4 | 88.5 | 69.6 | 366 | 381.8 | 385.1 | 383 | 335.6 | 247.8 | 351.6 | 316.2 | 444.7 | 395.1
2284 | 2090 | -6.7 | 0 | 0 | 278.4 | 269.4 | 251.7 | 238.3 | 45.1 | 48.3 | 18.3 | 65.6 | 5.6 | 213.6 | 9.1 | 250.9 | 61.7 | 59.5 | 333.3 | 142.6 | 62.3 | 74.7 | 96 | 88.6 | 69.6 | 366 | 381.5 | 384.7 | 382.9 | 335.1 | 247.6 | 351.2 | 315.8 | 444.2 | 394.8
2285 | 2091 | -6.7 | 0 | 0 | 278.2 | 269 | 251.5 | 237.9 | 43.8 | 48.3 | 18.3 | 65.6 | 6.1 | 217.1 | 11.1 | 248.1 | 61.1 | 59.3 | 330.6 | 124.9 | 62.7 | 77.2 | 95.2 | 88.3 | 69.7 | 365.9 | 381.3 | 384.4 | 382.8 | 334.7 | 247.2 | 350.8 | 315.4 | 443.6 | 394.6
2286 | 2092 | -6.7 | 0 | 0 | 277.7 | 268.4 | 251.4 | 237.5 | 44.6 | 48.2 | 18.3 | 65.5 | 7.2 | 219.8 | 11.1 | 244.9 | 61.4 | 59 | 327.9 | 111.7 | 62.2 | 76.5 | 95.1 | 87.9 | 69.6 | 365.9 | 381 | 384.1 | 382.7 | 334.3 | 247 | 350.5 | 315 | 443.1 | 394.3
2287 | 2093 | -6.7 | 0 | 0 | 277 | 268 | 251.3 | 237.3 | 43.3 | 48.2 | 18.3 | 65.5 | 7.2 | 209 | 10.6 | 241.6 | 61.8 | 58.8 | 324.8 | 101.2 | 61.4 | 76.8 | 95.8 | 87.6 | 69.3 | 365.9 | 380.8 | 383.7 | 382.6 | 333.8 | 246.7 | 350.1 | 314.6 | 442.6 | 394
2288 | 2094 | -6.7 | 0 | 0 | 276.5 | 267.4 | 251.1 | 237.2 | 45.8 | 48.1 | 18.3 | 65.4 | 6.4 | 224 | 10.4 | 238.2 | 62.4 | 58.6 | 322.4 | 94.5 | 61.9 | 75.1 | 96.8 | 86.8 | 69.2 | 365.9 | 380.6 | 383.4 | 382.4 | 333.5 | 246.4 | 349.8 | 314.3 | 442.1 | 393.8
2289 | 2095 | -6.7 | 0 | 0 | 276.2 | 266.8 | 250.6 | 236.8 | 47.9 | 47.9 | 18.3 | 65.3 | 5.9 | 209.8 | 17.6 | 235 | 61.6 | 58.4 | 319.7 | 89.8 | 62.7 | 78 | 97.3 | 86.7 | 69.2 | 365.9 | 380.3 | 383.1 | 382.3 | 333.1 | 246.2 | 349.5 | 313.9 | 441.6 | 393.5
2290 | 2096 | -6.7 | 0 | 0 | 275.6 | 266.6 | 250.3 | 236.5 | 46.7 | 47.8 | 18.3 | 65.3 | 5.9 | 212.5 | 20.9 | 232 | 60.3 | 58.4 | 316.8 | 86 | 63.8 | 77.8 | 97.2 | 86.5 | 68.8 | 365.9 | 380.1 | 382.8 | 382.2 | 332.9 | 245.9 | 349.2 | 313.5 | 441.1 | 393.2
2291 | 2097 | -6.7 | 0 | 0 | 275.1 | 266.6 | 250.2 | 236.2 | 47.8 | 47.7 | 18.3 | 65.2 | 5.8 | 216 | 17.9 | 228.6 | 61.3 | 58.3 | 314 | 83.5 | 64 | 77.9 | 96.9 | 86.2 | 68.9 | 365.9 | 379.9 | 382.4 | 382 | 332.6 | 245.5 | 348.9 | 313.1 | 440.6 | 393
2292 | 2098 | -6.7 | 0 | 0 | 275.1 | 266.5 | 250.1 | 236 | 47.8 | 47.7 | 18.3 | 65.1 | 6.5 | 210.3 | 16.5 | 225.3 | 61.5 | 58.3 | 311.7 | 80.8 | 64.6 | 78.4 | 96.2 | 86.4 | 69.1 | 365.8 | 379.6 | 382.1 | 381.9 | 332.2 | 245.2 | 348.6 | 312.6 | 440.1 | 392.7
2293 | 2099 | -6.7 | 0 | 0 | 274.6 | 266 | 249.8 | 235.8 | 45.9 | 47.6 | 18.3 | 64.9 | 7 | 206.6 | 15.4 | 222.3 | 61.7 | 57.9 | 309.1 | 80.5 | 65 | 78.7 | 96 | 86.4 | 69.3 | 365.8 | 379.4 | 381.8 | 381.8 | 331.9 | 244.9 | 348.3 | 312.3 | 439.6 | 392.4
2294 | 2100 | -6.8 | 0 | 0 | 274.5 | 265.3 | 249.5 | 235.6 | 44.9 | 47.6 | 18.4 | 64.8 | 5.7 | 204.6 | 14.7 | 219.3 | 62.5 | 57.5 | 306.5 | 79.8 | 64 | 79.2 | 95.3 | 86 | 69.1 | 365.8 | 379.2 | 381.4 | 381.7 | 331.7 | 244.7 | 347.9 | 311.9 | 439.1 | 392.2
2295 | 2101 | -6.7 | 0 | 0 | 274.4 | 265 | 249.3 | 235.2 | 44.3 | 47.5 | 18.4 | 64.7 | 6.1 | 205.6 | 16.5 | 216.2 | 61.8 | 57.2 | 304.1 | 78.5 | 63.1 | 78.2 | 94.7 | 85.2 | 69.2 | 365.8 | 378.9 | 381.1 | 381.5 | 331.4 | 244.5 | 347.6 | 311.4 | 438.6 | 391.9
2296 | 2102 | -6.7 | 0 | 0 | 273.9 | 264.9 | 249.1 | 234.9 | 46.3 | 47.3 | 18.4 | 64.6 | 6.2 | 216 | 16.8 | 213 | 61.3 | 57 | 301.5 | 77.5 | 63.5 | 80.3 | 93.4 | 84.8 | 69.3 | 365.8 | 378.7 | 380.8 | 381.4 | 331 | 244.3 | 347.2 | 311 | 438.1 | 391.6
2297 | 2103 | -6.7 | 0 | 0 | 273.4 | 264.7 | 248.8 | 234.6 | 46.5 | 47.2 | 18.4 | 64.5 | 7.5 | 197.6 | 17.9 | 210.1 | 61.2 | 56.6 | 299 | 76.2 | 63.2 | 78.7 | 93.1 | 84.2 | 69.4 | 365.8 | 378.4 | 380.5 | 381.3 | 330.7 | 244.1 | 346.9 | 310.6 | 437.6 | 391.4
2298 | 2104 | -6.7 | 0 | 0 | 272.7 | 264 | 248.6 | 234.3 | 44.9 | 47.2 | 18.4 | 64.3 | 9.3 | 201.3 | 19 | 207.2 | 61 | 55.1 | 296.5 | 75.8 | 62.3 | 80.5 | 92.5 | 83.7 | 69.2 | 365.8 | 378.2 | 380.1 | 381.1 | 330.4 | 243.8 | 346.6 | 310.2 | 437.1 | 391.1
2299 | 2105 | -6.7 | 0 | 0 | 272.3 | 263.4 | 248.4 | 234 | 40 | 47.1 | 18.4 | 64.2 | 9.6 | 205.2 | 20.1 | 204.4 | 61.5 | 53 | 294 | 75.6 | 62.8 | 81.7 | 92 | 83.6 | 69.2 | 365.8 | 378 | 379.8 | 381 | 330.1 | 243.6 | 346.3 | 309.8 | 436.6 | 390.9
2300 | 2106 | -6.8 | 0 | 0 | 271.8 | 263.2 | 248.2 | 233.6 | 40.3 | 47 | 18.4 | 64.1 | 10.1 | 201.2 | 19.7 | 201.7 | 61 | 51.6 | 291.6 | 74.9 | 62.3 | 78.8 | 89.8 | 84 | 69.4 | 365.8 | 377.7 | 379.5 | 380.9 | 329.8 | 243.4 | 346 | 309.4 | 436.1 | 390.6
2301 | 2107 | -6.8 | 0 | 0 | 271.3 | 263 | 247.9 | 233.3 | 44.3 | 46.9 | 18.4 | 64 | 8.1 | 218.6 | 21.1 | 199.1 | 60.1 | 50.4 | 289 | 73.3 | 61.9 | 76.7 | 84.8 | 84 | 69.5 | 365.7 | 377.5 | 379.2 | 380.8 | 329.5 | 243.1 | 345.6 | 309 | 435.6 | 390.3
2302 | 2108 | -6.8 | 0 | 0 | 270.7 | 262.7 | 247.6 | 233 | 45.9 | 46.7 | 18.4 | 63.9 | 5.3 | 226.6 | 18.5 | 196.5 | 58.3 | 49.6 | 286.5 | 72.8 | 62.6 | 78.9 | 79.1 | 84.1 | 69.7 | 365.7 | 377.2 | 378.9 | 380.6 | 329.2 | 242.8 | 345.3 | 308.6 | 435.1 | 390
2303 | 2109 | -6.8 | 0 | 0 | 270.4 | 262.8 | 247.3 | 232.8 | 44 | 46.7 | 18.4 | 63.8 | 4.9 | 239.3 | 14.7 | 194.1 | 56.7 | 48.7 | 284 | 71.8 | 63 | 79.6 | 74.9 | 84.2 | 69.8 | 365.7 | 377 | 378.6 | 380.5 | 328.9 | 242.4 | 345 | 308.2 | 434.6 | 389.8
2304 | 2110 | -6.7 | 0 | 0 | 269.9 | 262.5 | 247 | 232.5 | 46.3 | 46.6 | 18.4 | 63.8 | 7 | 228.5 | 16.1 | 191.4 | 56.4 | 47.6 | 281.8 | 70.9 | 62.4 | 80 | 71.6 | 83.9 | 69.8 | 365.7 | 376.7 | 378.3 | 380.4 | 328.6 | 242.1 | 344.6 | 307.8 | 434.2 | 389.5
2305 | 2111 | -6.8 | 0 | 0 | 269.5 | 262.1 | 246.8 | 232.3 | 45.6 | 46.6 | 18.4 | 63.8 | 8.2 | 233.9 | 19.4 | 188.8 | 56 | 46.7 | 279 | 69.9 | 61.4 | 79.9 | 68.6 | 83.6 | 69.8 | 365.7 | 376.5 | 377.9 | 380.2 | 328.4 | 241.8 | 344.3 | 307.4 | 433.7 | 389.2
2306 | 2112 | -6.7 | 0 | 0 | 269.4 | 261.5 | 246.3 | 232 | 41.8 | 46.5 | 18.4 | 63.7 | 8.6 | 253.2 | 20.8 | 186.4 | 56.2 | 46.1 | 276.9 | 69.5 | 61 | 78.8 | 66.1 | 83.2 | 69.7 | 365.7 | 376.2 | 377.6 | 380.1 | 328.1 | 241.5 | 344 | 307 | 433.2 | 389
2307 | 2113 | -6.7 | 0 | 0 | 268.9 | 261.1 | 245.9 | 231.7 | 39.3 | 46.4 | 18.4 | 63.6 | 9.2 | 245.5 | 19.3 | 183.8 | 56.5 | 45.8 | 274.4 | 69 | 61.5 | 80.5 | 64.6 | 83 | 69.6 | 365.6 | 376 | 377.3 | 380 | 327.8 | 241.2 | 343.7 | 306.7 | 432.7 | 388.7
2308 | 2114 | -6.7 | 0 | 0 | 268.3 | 260.7 | 245.5 | 231.4 | 38.1 | 46.3 | 18.4 | 63.5 | 8 | 255.9 | 17.5 | 181.3 | 57.4 | 45.5 | 271.9 | 68.6 | 62 | 78.8 | 64.3 | 82.4 | 69.7 | 365.6 | 375.7 | 377 | 379.8 | 327.6 | 240.9 | 343.4 | 306.3 | 432.2 | 388.4
2309 | 2115 | -6.7 | 0 | 0 | 268.1 | 260 | 245.1 | 231 | 40.5 | 46.2 | 18.4 | 63.3 | 8.2 | 231.8 | 14.9 | 178.6 | 58.4 | 45.2 | 269.5 | 68 | 61.4 | 77.7 | 62.7 | 82.3 | 69.8 | 365.6 | 375.5 | 376.7 | 379.7 | 327.3 | 240.7 | 343 | 305.9 | 431.7 | 388.2
2310 | 2116 | -6.8 | 0 | 0 | 267.7 | 259.7 | 244.9 | 230.7 | 42.5 | 46.1 | 18.4 | 63.2 | 7.7 | 237.5 | 15.2 | 176 | 59.2 | 46 | 267.3 | 67.2 | 61.6 | 77.5 | 57.6 | 82.6 | 69.6 | 365.6 | 375.2 | 376.4 | 379.5 | 327.1 | 240.3 | 342.8 | 305.5 | 431.3 | 387.9
2311 | 2117 | -6.8 | 0 | 0 | 267.2 | 259.3 | 244.8 | 230.5 | 42.4 | 46 | 18.4 | 63.1 | 7.4 | 243 | 18.6 | 173.5 | 59.1 | 46.7 | 265 | 65.8 | 62 | 79.2 | 55.5 | 82.6 | 69.5 | 365.5 | 375 | 376.1 | 379.4 | 326.7 | 240 | 342.5 | 305.2 | 430.8 | 387.6
2312 | 2118 | -6.7 | 0 | 0 | 266.8 | 258.9 | 244.5 | 230.2 | 41.7 | 45.9 | 18.4 | 62.9 | 6.1 | 245.1 | 20.1 | 171.2 | 58.1 | 47.2 | 262.8 | 65.3 | 62 | 79.6 | 57.2 | 82.5 | 69.6 | 365.5 | 374.7 | 375.7 | 379.2 | 326.5 | 239.6 | 342.2 | 304.8 | 430.3 | 387.4
2313 | 2119 | -6.7 | 0 | 0 | 266.6 | 258.8 | 244.2 | 230 | 40.6 | 45.8 | 18.4 | 62.8 | 5.7 | 239.7 | 17.6 | 168.9 | 57.2 | 47.5 | 260.4 | 64.6 | 62 | 79.9 | 57.4 | 82.5 | 69.7 | 365.5 | 374.5 | 375.4 | 379.1 | 326.3 | 239.3 | 341.8 | 304.3 | 429.8 | 387.1
2314 | 2120 | -6.7 | 0 | 0 | 266.3 | 258.9 | 244 | 229.8 | 40.1 | 45.8 | 18.4 | 62.7 | 8 | 211.2 | 16.6 | 166.6 | 57.2 | 47.7 | 258 | 64 | 62.1 | 80.6 | 57.7 | 82.8 | 69.7 | 365.4 | 374.2 | 375.1 | 378.9 | 326.1 | 238.9 | 341.5 | 304 | 429.4 | 386.9
2315 | 2121 | -6.7 | 0 | 0 | 265.8 | 258.7 | 243.8 | 229.7 | 40.3 | 45.7 | 18.4 | 62.6 | 7.5 | 224.4 | 13.6 | 164.6 | 56.1 | 47.7 | 255.8 | 64.1 | 61.6 | 79.6 | 58.4 | 82.7 | 69.8 | 365.4 | 374 | 374.8 | 378.8 | 325.7 | 238.5 | 341.1 | 303.7 | 428.9 | 386.6
2316 | 2122 | -6.7 | 0 | 0 | 265.3 | 258.2 | 243.6 | 229.5 | 39.1 | 45.6 | 18.4 | 62.6 | 8.1 | 233.2 | 13.6 | 162.4 | 55.6 | 47.9 | 253.5 | 63.8 | 61.1 | 80.3 | 57.6 | 82 | 69.7 | 365.4 | 373.7 | 374.5 | 378.6 | 325.4 | 237.9 | 340.7 | 303.3 | 428.4 | 386.3
2317 | 2123 | -6.7 | 0 | 0 | 264.9 | 258.2 | 243.3 | 229.3 | 40.3 | 45.6 | 18.4 | 62.5 | 6.6 | 247.2 | 12.6 | 160.3 | 55.1 | 47.9 | 251.3 | 63.3 | 60.8 | 81.2 | 56.8 | 82.1 | 68.9 | 365.3 | 373.5 | 374.2 | 378.5 | 325.2 | 237.5 | 340.5 | 302.9 | 427.9 | 386.1
2318 | 2124 | -6.7 | 0 | 0 | 264.5 | 258.4 | 243 | 229.1 | 45.1 | 45.6 | 18.5 | 62.4 | 5.4 | 256.1 | 16.2 | 158.1 | 55.4 | 48 | 242.8 | 62.4 | 61.4 | 80.7 | 56.6 | 81.8 | 68.1 | 365.3 | 373.2 | 373.9 | 378.4 | 324.9 | 237 | 340.2 | 302.6 | 427.5 | 385.8
2319 | 2125 | -6.7 | 0 | 0 | 264.2 | 258.5 | 242.8 | 228.9 | 57.4 | 45.5 | 18.5 | 62.4 | 5.1 | 255.4 | 16.4 | 155.8 | 57.4 | 48 | 239.1 | 62.3 | 60.7 | 81 | 56.8 | 79.9 | 67.6 | 365.3 | 373 | 373.6 | 378.2 | 324.5 | 236.7 | 339.9 | 302.3 | 427 | 385.5
2320 | 2126 | -6.7 | 0 | 0 | 264 | 258.3 | 242.5 | 228.7 | 65 | 45.5 | 18.5 | 62.3 | 5.2 | 271 | 15.9 | 153.4 | 58.8 | 48 | 235.5 | 61.9 | 60.3 | 81.2 | 55.6 | 78.7 | 67.6 | 365.3 | 372.7 | 373.3 | 378.1 | 324.2 | 236.3 | 339.6 | 301.9 | 426.5 | 385.3
2321 | 2127 | -6.7 | 0 | 0 | 263.9 | 258 | 242.3 | 228.6 | 68.5 | 45.5 | 18.5 | 62.2 | 4.4 | 251.4 | 16.4 | 150.9 | 59.6 | 48 | 231.3 | 62 | 60 | 80.2 | 56.6 | 78.2 | 67.9 | 365.2 | 372.5 | 373 | 377.9 | 323.9 | 236 | 339.4 | 301.6 | 426 | 385
2322 | 2128 | -6.6 | 0 | 0 | 263.9 | 257.2 | 242.1 | 228.4 | 69.7 | 45.5 | 18.5 | 62.1 | 5.5 | 262.3 | 17.1 | 148.5 | 59.7 | 47.8 | 227.3 | 61.6 | 60.1 | 80.6 | 56.6 | 78.3 | 68.1 | 365.2 | 372.2 | 372.7 | 377.8 | 323.6 | 235.9 | 339.1 | 301.2 | 425.6 | 384.8
2323 | 2129 | -6.7 | 0 | 0 | 263.7 | 256.5 | 242.1 | 228.2 | 70.3 | 45.4 | 18.5 | 61.9 | 6 | 262.3 | 18.8 | 146.2 | 59.2 | 47.5 | 223.8 | 61.1 | 60.6 | 82.1 | 57.4 | 78.1 | 68.2 | 365.2 | 372 | 372.4 | 377.6 | 323.3 | 235.7 | 338.8 | 300.9 | 425.1 | 384.5
2324 | 2130 | -6.6 | 0 | 0 | 263.7 | 256.1 | 242 | 227.9 | 70.5 | 45.4 | 18.5 | 61.8 | 7 | 258.1 | 17.9 | 144 | 59.4 | 47.2 | 220.6 | 60.7 | 61 | 82.1 | 57.6 | 78 | 68.2 | 365.1 | 371.7 | 372.1 | 377.5 | 323 | 235.7 | 338.5 | 300.6 | 424.7 | 384.3
2325 | 2131 | -6.6 | 0 | 0 | 263.7 | 255.5 | 241.9 | 227.7 | 70.7 | 45.3 | 18.5 | 61.7 | 6.5 | 251.6 | 18.6 | 141.7 | 59.7 | 46.9 | 217.6 | 60.6 | 61.4 | 82.8 | 58.2 | 78 | 68.4 | 365.1 | 371.5 | 371.8 | 377.3 | 322.7 | 235.6 | 338.1 | 300.3 | 424.2 | 384
2326.1 | 2132.1 | -6.7 | 0 | 0 | 263.7 | 254.8 | 241.7 | 227.5 | 70.8 | 45.2 | 18.5 | 61.6 | 5.9 | 252.7 | 17.9 | 139.5 | 60.1 | 46.7 | 215.1 | 60.2 | 61.6 | 82.5 | 58.7 | 78 | 68.4 | 365.1 | 371.3 | 371.5 | 377.2 | 322.5 | 235.5 | 337.8 | 299.9 | 423.7 | 383.7
2327.1 | 2133.1 | -6.6 | 0 | 0 | 263.6 | 254.3 | 241.4 | 227.2 | 70.6 | 45.1 | 18.5 | 61.6 | 6.1 | 245.3 | 16.1 | 137.3 | 59.3 | 46.6 | 212.6 | 59.8 | 61.9 | 82 | 58.7 | 77.8 | 68.8 | 365 | 371 | 371.2 | 377 | 322.3 | 235.4 | 337.5 | 299.6 | 423.3 | 383.5
2328.1 | 2134.1 | -6.7 | 0 | 0 | 263.2 | 254.3 | 241.3 | 227.1 | 70.3 | 45 | 18.5 | 61.6 | 5.5 | 245.1 | 14.7 | 135 | 59.2 | 46.4 | 210.2 | 59.6 | 62.2 | 81.8 | 59.2 | 77.8 | 68.9 | 365 | 370.8 | 370.9 | 376.9 | 322.2 | 235.3 | 337.3 | 299.3 | 422.8 | 383.2
2329.1 | 2135.1 | -6.7 | 0 | 0 | 262.9 | 254.6 | 241.3 | 226.9 | 69.9 | 44.9 | 18.5 | 61.6 | 6.3 | 256.7 | 15.8 | 132.9 | 59.6 | 46.2 | 208.3 | 59.4 | 62.6 | 82.7 | 59.5 | 77.9 | 69.1 | 365 | 370.6 | 370.6 | 376.7 | 321.9 | 235.3 | 337 | 298.9 | 422.4 | 383
2330.1 | 2136.1 | -6.7 | 0 | 0 | 262.6 | 254.3 | 241.1 | 226.7 | 70 | 44.8 | 18.5 | 61.6 | 7.6 | 258.5 | 15.5 | 130.9 | 58.7 | 46.2 | 206.2 | 58.9 | 62.8 | 83.6 | 59.5 | 77.9 | 69 | 364.9 | 370.3 | 370.3 | 376.6 | 321.6 | 235.2 | 336.7 | 298.6 | 421.9 | 382.7
2331.1 | 2137.1 | -6.7 | 0 | 0 | 262.4 | 254.1 | 241 | 226.6 | 70.5 | 44.6 | 18.5 | 61.5 | 7.6 | 242.7 | 16.1 | 128.7 | 58.9 | 46.1 | 204.3 | 58.5 | 62.8 | 81.3 | 59.3 | 77.8 | 69 | 364.9 | 370.1 | 370 | 376.4 | 321.4 | 235 | 336.4 | 298.3 | 421.5 | 382.5
2332.1 | 2138.1 | -6.7 | 0 | 0 | 262.2 | 253.8 | 240.8 | 226.6 | 71 | 44.5 | 18.5 | 61.4 | 8 | 252 | 16.9 | 126.8 | 59.3 | 46 | 202.6 | 58.6 | 63.2 | 78.9 | 58.5 | 78 | 68.7 | 364.9 | 369.9 | 369.7 | 376.3 | 321.2 | 234.9 | 336.2 | 298 | 421 | 382.2
2333.1 | 2139.1 | -6.7 | 0 | 0 | 262.1 | 253.6 | 240.6 | 226.4 | 71.5 | 44.4 | 18.5 | 61.3 | 8.1 | 222.3 | 15.4 | 124.9 | 59 | 45.9 | 200.9 | 58.7 | 63.4 | 80.1 | 57.3 | 78.3 | 68.8 | 364.9 | 369.7 | 369.4 | 376.1 | 320.9 | 234.9 | 335.9 | 297.7 | 420.6 | 381.9
2334.1 | 2140.1 | -6.7 | 0 | 0 | 262.2 | 253.3 | 240.5 | 226.4 | 72 | 44.3 | 18.5 | 61.2 | 6.7 | 254.6 | 11.2 | 122.8 | 58.7 | 45.9 | 199.2 | 58.4 | 63.5 | 79.3 | 56.8 | 78.4 | 68.8 | 364.8 | 369.4 | 369.1 | 375.9 | 320.7 | 234.8 | 335.6 | 297.4 | 420.2 | 381.7
2335.1 | 2141.1 | -6.8 | 0 | 0 | 262.1 | 253.2 | 240.4 | 226.3 | 72.4 | 44.2 | 18.5 | 61.1 | 7.3 | 238.9 | 13.6 | 120.9 | 58.5 | 45.9 | 197.6 | 58.1 | 63.6 | 79.7 | 56.4 | 78.3 | 68.7 | 364.8 | 369.2 | 368.8 | 375.8 | 320.4 | 234.8 | 335.2 | 297.1 | 419.7 | 381.4
2336.1 | 2142.1 | -6.7 | 0 | 0 | 262 | 253 | 240.3 | 226.2 | 73 | 44.1 | 18.5 | 61 | 8.6 | 255.1 | 15.3 | 119 | 58.4 | 45.9 | 196 | 57.7 | 63.5 | 80.6 | 55.8 | 78.3 | 68.6 | 364.7 | 369 | 368.6 | 375.6 | 320.1 | 234.9 | 334.9 | 296.8 | 419.3 | 381.2
2337.1 | 2143.1 | -6.8 | 0 | 0 | 262 | 252.8 | 240.1 | 226 | 73.1 | 44 | 18.5 | 60.9 | 6.5 | 245.2 | 12.8 | 117.1 | 58.3 | 46 | 194.5 | 57.3 | 63.3 | 80.7 | 55.4 | 78.7 | 68.7 | 364.7 | 368.8 | 368.3 | 375.4 | 319.9 | 234.9 | 334.7 | 296.5 | 418.8 | 380.9
2338.1 | 2144.1 | -6.8 | 0 | 0 | 262 | 252.9 | 240 | 225.7 | 73.7 | 43.9 | 18.5 | 60.9 | 4.9 | 243.2 | 17.2 | 115.4 | 58.6 | 46 | 193 | 56.9 | 62.8 | 79.5 | 55.3 | 79.1 | 68.7 | 364.7 | 368.6 | 368 | 375.3 | 319.6 | 234.9 | 334.4 | 296.2 | 418.4 | 380.7
2339.1 | 2145.1 | -6.7 | 0 | 0 | 261.8 | 252.9 | 239.9 | 225.5 | 74.5 | 43.8 | 18.5 | 60.9 | 6.6 | 239.7 | 21.8 | 113.7 | 59 | 45.9 | 191.5 | 56.7 | 62.8 | 80.3 | 56 | 79.1 | 68.9 | 364.6 | 368.4 | 367.7 | 375.1 | 319.4 | 234.9 | 334.1 | 295.9 | 417.9 | 380.4
2340.1 | 2146.1 | -6.8 | 0 | 0 | 261.4 | 253 | 239.8 | 225.5 | 74.8 | 43.6 | 18.6 | 60.8 | 8.8 | 242.9 | 20.5 | 112 | 58.7 | 46 | 190.2 | 56.3 | 62.6 | 80 | 56.7 | 78.8 | 69 | 364.6 | 368.2 | 367.4 | 374.9 | 319.2 | 234.9 | 333.8 | 295.5 | 417.5 | 380.1
2341.1 | 2147.1 | -6.7 | 0 | 0 | 261.2 | 253 | 239.6 | 225.4 | 75.7 | 43.6 | 18.6 | 60.8 | 8.1 | 237.5 | 17.9 | 110.4 | 58.6 | 46 | 188.6 | 56.3 | 62.2 | 79.1 | 56.7 | 78.7 | 69.1 | 364.6 | 368 | 367.2 | 374.8 | 319 | 234.9 | 333.5 | 295.2 | 417.1 | 379.9
2342.1 | 2148.1 | -6.7 | 0 | 0 | 261 | 252.7 | 239.6 | 225.4 | 76.9 | 43.5 | 18.6 | 60.7 | 8.2 | 250.8 | 19.5 | 108.8 | 58.8 | 46 | 187.2 | 55.9 | 62.2 | 78.4 | 56.6 | 78.8 | 69.1 | 364.6 | 367.7 | 366.9 | 374.6 | 318.8 | 234.8 | 333.3 | 294.9 | 416.6 | 379.6
2343.1 | 2149.1 | -6.7 | 0 | 0 | 260.5 | 252.4 | 239.5 | 225.4 | 78.7 | 43.4 | 18.6 | 60.6 | 7.6 | 246.2 | 21.9 | 107.2 | 58.5 | 45.9 | 186 | 55.4 | 62.1 | 79 | 57.4 | 78.8 | 69.3 | 364.5 | 367.5 | 366.6 | 374.5 | 318.5 | 234.8 | 333 | 294.6 | 416.2 | 379.4
2344.1 | 2150.1 | -6.8 | 0 | 0 | 260 | 252.3 | 239.2 | 225.2 | 83.1 | 43.3 | 18.6 | 60.5 | 6.2 | 245.1 | 23.5 | 105.7 | 58.8 | 46 | 184.5 | 55.2 | 62.3 | 79.7 | 58.2 | 78.6 | 69.3 | 364.5 | 367.3 | 366.3 | 374.3 | 318.3 | 234.7 | 332.8 | 294.3 | 415.7 | 379.1
2345.1 | 2151.1 | -6.8 | 0 | 0 | 259.7 | 252.2 | 238.9 | 225 | 95.6 | 43.3 | 18.6 | 60.4 | 6.5 | 243.6 | 22.3 | 104.2 | 58.8 | 46 | 183.1 | 55 | 62.4 | 79.7 | 58.8 | 78.5 | 69.2 | 364.5 | 367.1 | 366 | 374.2 | 318 | 234.7 | 332.5 | 293.9 | 415.3 | 378.8
2346.1 | 2152.1 | -6.7 | 0 | 0 | 259.4 | 252.1 | 238.6 | 224.9 | 113.7 | 43.3 | 18.6 | 60.3 | 5.7 | 246.7 | 19.4 | 102.9 | 58.8 | 46.2 | 181.7 | 54.7 | 62 | 79.6 | 59 | 78.4 | 69.4 | 364.4 | 366.9 | 365.7 | 374 | 317.8 | 234.7 | 332.2 | 293.6 | 414.9 | 378.6
2347.1 | 2153.1 | -6.7 | 0 | 0 | 259.2 | 252.1 | 238.6 | 224.7 | 129.2 | 43.3 | 18.6 | 60.2 | 6.1 | 244.6 | 16.5 | 101.4 | 59.3 | 46.2 | 180.4 | 54.6 | 62.5 | 80.4 | 59.2 | 78.3 | 69.6 | 364.4 | 366.6 | 365.4 | 373.9 | 317.5 | 234.6 | 332 | 293.3 | 414.4 | 378.3
2348.1 | 2154.1 | -6.7 | 0 | 0 | 259.1 | 251.7 | 238.5 | 224.5 | 142.2 | 43.2 | 18.6 | 60.2 | 6.8 | 252.7 | 16.9 | 100 | 59.7 | 46.4 | 179.1 | 54.5 | 62.9 | 80.7 | 59.3 | 78.8 | 69.6 | 364.3 | 366.4 | 365.1 | 373.7 | 317.2 | 234.6 | 331.7 | 293 | 414 | 378.1
2349.1 | 2155.1 | -6.7 | 0 | 0 | 259 | 251.3 | 238.5 | 224.5 | 153.4 | 43.1 | 18.6 | 60.2 | 6.1 | 259.4 | 17.1 | 98.6 | 60 | 46.6 | 177.7 | 54.2 | 63.3 | 79.3 | 59.7 | 79.4 | 69.3 | 364.3 | 366.2 | 364.9 | 373.5 | 316.8 | 234.6 | 331.5 | 292.7 | 413.6 | 377.8
2350.1 | 2156.1 | -6.7 | 0 | 0 | 259 | 251.2 | 238.3 | 224.4 | 163.5 | 43.1 | 18.6 | 60.1 | 7.1 | 250.1 | 16.1 | 97.3 | 60.2 | 46.5 | 176.3 | 54 | 63.5 | 78.8 | 59.6 | 79.6 | 69.3 | 364.3 | 365.9 | 364.6 | 373.4 | 316.7 | 234.7 | 331.2 | 292.4 | 413.1 | 377.6
2351.1 | 2157.1 | -6.7 | 0 | 0 | 258.8 | 251.2 | 238.1 | 224.1 | 172.3 | 43.1 | 18.6 | 60 | 7.5 | 246.2 | 17.8 | 95.7 | 60.6 | 46.5 | 175.2 | 54.1 | 63.6 | 79.3 | 59.2 | 79.4 | 69.2 | 364.2 | 365.7 | 364.3 | 373.2 | 316.6 | 234.7 | 330.8 | 292.1 | 412.7 | 377.3
2352.1 | 2158.1 | -6.7 | 0 | 0 | 258.6 | 251.3 | 237.8 | 223.9 | 180.1 | 43.1 | 18.6 | 59.9 | 5.9 | 242.8 | 17 | 94.3 | 60.7 | 46.8 | 173.9 | 53.9 | 63.7 | 78.8 | 58.4 | 79.2 | 69.3 | 364.2 | 365.5 | 364.1 | 373 | 316.4 | 234.6 | 330.4 | 291.8 | 412.3 | 377.1
2353.1 | 2159.1 | -6.7 | 0 | 0 | 258.5 | 251.3 | 237.5 | 223.9 | 187 | 43.1 | 18.6 | 59.8 | 5.7 | 239.4 | 16.2 | 92.9 | 60.3 | 46.9 | 172.4 | 53.5 | 63.9 | 78.5 | 57.5 | 79.1 | 69.3 | 364.2 | 365.2 | 363.8 | 372.8 | 316.2 | 234.5 | 330.1 | 291.5 | 411.9 | 376.8
2354.1 | 2160.1 | -6.7 | 0 | 0 | 258.2 | 251.4 | 237.3 | 223.8 | 193.6 | 43.1 | 18.6 | 59.8 | 5.8 | 249.4 | 15.3 | 91.5 | 60.5 | 46.9 | 171.4 | 53.3 | 63.5 | 78.3 | 56.6 | 79.1 | 69.1 | 364.1 | 365 | 363.5 | 372.7 | 316 | 234.4 | 329.9 | 291.2 | 411.5 | 376.6
2355.1 | 2161.1 | -6.7 | 0 | 0 | 258 | 251.1 | 237.2 | 223.7 | 199.2 | 43.1 | 18.6 | 59.8 | 5.7 | 258.3 | 12.7 | 90.1 | 60.6 | 47 | 170.1 | 53.4 | 63.4 | 78 | 55.8 | 79.1 | 69 | 364.1 | 364.8 | 363.2 | 372.5 | 315.8 | 234.3 | 329.6 | 290.9 | 411 | 376.3
2356.1 | 2162.1 | -6.6 | 0 | 0 | 257.6 | 250.9 | 237.1 | 223.5 | 204.5 | 43.1 | 18.6 | 59.7 | 5.5 | 249.9 | 12.2 | 88.7 | 60.8 | 47.1 | 168.9 | 53 | 63.5 | 77.1 | 55.5 | 79 | 69 | 364 | 364.6 | 363 | 372.4 | 315.5 | 234.2 | 329.4 | 290.6 | 410.6 | 376.1
2357.1 | 2163.1 | -6.7 | 0 | 0 | 257.1 | 250.6 | 237 | 223.3 | 209.4 | 43.1 | 18.6 | 59.8 | 5.4 | 241.2 | 11.5 | 87.4 | 60.5 | 47 | 167.7 | 52.8 | 63.1 | 75.5 | 54.9 | 79.2 | 68.9 | 364 | 364.3 | 362.7 | 372.2 | 315.3 | 234 | 329.2 | 290.3 | 410.2 | 375.8
2358.1 | 2164.1 | -6.7 | 0 | 0 | 256.8 | 250.4 | 236.8 | 223.2 | 213.3 | 43 | 18.6 | 59.7 | 4.9 | 242.5 | 10.2 | 86.3 | 60.7 | 47 | 166.5 | 52.8 | 62.9 | 75.3 | 54.1 | 79.1 | 69 | 363.9 | 364.1 | 362.4 | 372 | 315.2 | 233.9 | 328.9 | 290 | 409.8 | 375.5
2359.1 | 2165.1 | -6.7 | 0 | 0 | 256.4 | 250 | 236.6 | 223 | 217.2 | 43 | 18.6 | 59.7 | 5.1 | 241.9 | 9.4 | 85.1 | 60.8 | 47.1 | 165.4 | 52.7 | 63.1 | 76.6 | 53.8 | 78.9 | 69 | 363.9 | 363.9 | 362.2 | 371.9 | 315 | 233.7 | 328.7 | 289.7 | 409.4 | 375.3
2360.1 | 2166.1 | -6.7 | 0 | 0 | 255.9 | 249.7 | 236.6 | 222.9 | 220.5 | 43 | 18.6 | 59.6 | 5.5 | 245.2 | 9.6 | 84 | 60.5 | 47.2 | 164.2 | 52.5 | 63 | 76.5 | 53.6 | 79 | 69 | 363.9 | 363.7 | 361.9 | 371.7 | 314.9 | 233.5 | 328.5 | 289.4 | 408.9 | 375
2361.1 | 2167.1 | -6.7 | 0 | 0 | 255.6 | 249.3 | 236.4 | 222.6 | 223.6 | 43 | 18.6 | 59.5 | 5.9 | 251.5 | 9.2 | 82.9 | 60.5 | 47.2 | 163 | 52.7 | 62.8 | 75.1 | 53.7 | 78.9 | 69.2 | 363.8 | 363.5 | 361.6 | 371.5 | 314.7 | 233.3 | 328.2 | 289.1 | 408.5 | 374.8
2362.1 | 2168.1 | -6.7 | 0 | 0 | 255.4 | 248.7 | 236.3 | 222.4 | 226 | 43 | 18.6 | 59.5 | 6.2 | 250.7 | 10 | 81.8 | 60.2 | 47.3 | 161.9 | 52.7 | 62.7 | 75.8 | 54.1 | 78.7 | 69.3 | 363.8 | 363.3 | 361.4 | 371.4 | 314.5 | 233.2 | 328 | 288.9 | 408.1 | 374.6
2363.1 | 2169.1 | -6.7 | 0 | 0 | 255.3 | 248.5 | 236.1 | 222.3 | 228.3 | 42.9 | 18.6 | 59.5 | 6.3 | 247 | 10.6 | 80.8 | 60.2 | 47.4 | 160.9 | 52.7 | 62.5 | 75.4 | 54.9 | 78.4 | 69.4 | 363.7 | 363.1 | 361.1 | 371.2 | 314.3 | 233 | 327.7 | 288.6 | 407.7 | 374.3
2364.1 | 2170.1 | -6.7 | 0 | 0 | 254.9 | 248.4 | 235.9 | 222.1 | 230.6 | 42.8 | 18.6 | 59.4 | 6.8 | 247.6 | 13.4 | 79.6 | 60.2 | 47.4 | 159.7 | 52.6 | 62.5 | 75.2 | 56.1 | 78.3 | 69.6 | 363.7 | 362.9 | 360.8 | 371.1 | 314.1 | 232.8 | 327.5 | 288.3 | 407.3 | 374.1
2365.1 | 2171.1 | -6.6 | 0 | 0 | 254.4 | 248 | 235.6 | 221.9 | 232.6 | 42.8 | 18.7 | 59.4 | 6.1 | 252.5 | 15.4 | 78.6 | 60.4 | 47.5 | 158.6 | 52.3 | 62.8 | 75.9 | 57.1 | 78.2 | 69.7 | 363.6 | 362.7 | 360.5 | 370.9 | 313.9 | 232.7 | 327.3 | 288 | 406.9 | 373.8
2366.1 | 2172.1 | -6.6 | 0 | 0 | 253.9 | 247.7 | 235.3 | 221.7 | 234.5 | 42.8 | 18.7 | 59.3 | 6.5 | 250.3 | 14.9 | 77.6 | 60.7 | 47.5 | 157.6 | 52.4 | 63 | 75.2 | 56.9 | 78.2 | 69.7 | 363.6 | 362.5 | 360.3 | 370.7 | 313.7 | 232.5 | 327 | 287.8 | 406.5 | 373.6
2367.1 | 2173.1 | -6.6 | 0 | 0 | 253.6 | 247.6 | 235.1 | 221.5 | 236.4 | 42.7 | 18.7 | 59.1 | 6.2 | 232.5 | 14.5 | 76.6 | 60.8 | 47.6 | 156.5 | 52.5 | 63.2 | 76.1 | 55.7 | 78.2 | 69.9 | 363.5 | 362.3 | 360 | 370.6 | 313.5 | 232.4 | 326.8 | 287.5 | 406.1 | 373.3
2368.1 | 2174.1 | -6.7 | 0 | 0 | 253.4 | 247.2 | 234.9 | 221.3 | 238 | 42.7 | 18.7 | 59 | 5.5 | 245.7 | 13 | 75.7 | 61 | 47.6 | 155.4 | 52.6 | 63.5 | 76.8 | 55.6 | 78.6 | 70.1 | 363.5 | 362.1 | 359.7 | 370.4 | 313.3 | 232.2 | 326.6 | 287.2 | 405.7 | 373.1
2369.1 | 2175.1 | -6.7 | 0 | 0 | 253.1 | 247 | 234.6 | 221.2 | 238.9 | 42.7 | 18.7 | 58.9 | 4.7 | 217.6 | 11.3 | 74.8 | 60.8 | 47.7 | 154.3 | 52.3 | 63.8 | 76.8 | 56.3 | 79.1 | 70.3 | 363.5 | 361.8 | 359.5 | 370.2 | 313.1 | 232.1 | 326.3 | 286.9 | 405.2 | 372.8
2370.1 | 2176.1 | -6.7 | 0 | 0 | 252.9 | 246.7 | 234.3 | 221 | 239.8 | 42.6 | 18.7 | 58.8 | 4.6 | 211.5 | 10.8 | 73.9 | 61 | 47.8 | 153.2 | 52.2 | 63.6 | 76.3 | 55.4 | 79.5 | 70.4 | 363.4 | 361.6 | 359.2 | 370.1 | 312.9 | 232 | 326.1 | 286.6 | 404.8 | 372.6
2371.1 | 2177.1 | -6.6 | 0 | 0 | 252.7 | 246.7 | 234.1 | 220.9 | 241 | 42.6 | 18.7 | 58.8 | 4.8 | 209.1 | 13.8 | 73 | 61.4 | 47.8 | 152.3 | 51.9 | 62.9 | 75.7 | 54.5 | 79.7 | 70.4 | 363.4 | 361.4 | 358.9 | 369.9 | 312.8 | 231.8 | 325.8 | 286.4 | 404.4 | 372.4
2372.1 | 2178.1 | -6.6 | 0 | 0 | 252.3 | 246.6 | 233.8 | 220.8 | 242.2 | 42.5 | 18.7 | 58.9 | 4.6 | 220 | 14.4 | 72.1 | 61.4 | 47.8 | 151.1 | 51.8 | 62.1 | 74 | 53.4 | 79.7 | 70.2 | 363.3 | 361.2 | 358.7 | 369.7 | 312.6 | 231.7 | 325.6 | 286.1 | 404 | 372.1
2373.1 | 2179.1 | -6.6 | 0 | 0 | 251.9 | 246.3 | 233.7 | 220.6 | 243.3 | 42.4 | 18.7 | 58.9 | 4.8 | 218.3 | 13.3 | 71.2 | 61.5 | 47.9 | 150.2 | 51.5 | 62.4 | 74.6 | 52.4 | 79.3 | 70.1 | 363.2 | 361 | 358.4 | 369.5 | 312.4 | 231.5 | 325.4 | 285.8 | 403.6 | 371.9
2374.1 | 2180.1 | -6.7 | 0 | 0 | 251.6 | 246.4 | 233.6 | 220.4 | 244.3 | 42.4 | 18.7 | 58.8 | 4.3 | 208.6 | 11.6 | 70.3 | 61.7 | 47.9 | 149.5 | 51.4 | 62.6 | 75.6 | 51.9 | 79 | 70.1 | 363.2 | 360.8 | 358.2 | 369.4 | 312.2 | 231.4 | 325.2 | 285.5 | 403.2 | 371.6
2375.1 | 2181.1 | -6.7 | 0 | 0 | 251.4 | 246.5 | 233.2 | 220.2 | 245.2 | 42.4 | 18.7 | 58.8 | 4.6 | 249.4 | 10 | 69.5 | 61.5 | 47.9 | 148.4 | 51 | 62.8 | 76 | 51.5 | 78.9 | 69.9 | 363.2 | 360.6 | 357.9 | 369.2 | 311.9 | 231.3 | 324.9 | 285.2 | 402.8 | 371.4
2376.1 | 2182.1 | -6.7 | 0 | 0 | 251.3 | 246.5 | 232.9 | 220 | 245.9 | 42.3 | 18.7 | 58.7 | 4.9 | 243.1 | 9.4 | 68.8 | 61.3 | 48.1 | 147.3 | 50.8 | 63.2 | 75.9 | 51.6 | 78.7 | 69.8 | 363.1 | 360.4 | 357.6 | 369 | 311.7 | 231.1 | 324.7 | 284.9 | 402.4 | 371.1
2377.1 | 2183.1 | -6.6 | 0 | 0 | 251 | 246.3 | 232.8 | 219.8 | 246.1 | 42.1 | 18.7 | 58.7 | 5 | 228.9 | 8.5 | 68 | 61.2 | 48.2 | 146.3 | 50.7 | 63.4 | 75.7 | 52.4 | 78.5 | 69.9 | 363.1 | 360.2 | 357.4 | 368.9 | 311.5 | 230.9 | 324.4 | 284.7 | 402 | 370.9
2378.1 | 2184.1 | -6.6 | 0 | 0 | 250.6 | 246 | 232.7 | 219.6 | 246.3 | 42 | 18.7 | 58.6 | 5.3 | 247.5 | 10.7 | 67.2 | 61.2 | 48.2 | 145.3 | 50.5 | 63.5 | 75.8 | 53.7 | 78.5 | 70.1 | 363 | 360 | 357.1 | 368.7 | 311.2 | 230.6 | 324.2 | 284.4 | 401.6 | 370.6
2379.1 | 2185.1 | -6.7 | 0 | 0 | 250.3 | 245.9 | 232.5 | 219.3 | 247.3 | 41.9 | 18.7 | 58.6 | 5 | 243.3 | 12.3 | 66.4 | 61.2 | 48.2 | 144.2 | 50.4 | 63.6 | 76.1 | 53.7 | 78.4 | 70.3 | 362.9 | 359.8 | 356.9 | 368.5 | 311 | 230.4 | 323.9 | 284.1 | 401.2 | 370.4
2380.1 | 2186.1 | -6.7 | 0 | 0 | 249.8 | 245.8 | 232.4 | 219.2 | 247.9 | 41.9 | 18.7 | 58.6 | 5.1 | 243.9 | 14.3 | 65.8 | 61.4 | 48.2 | 143.2 | 50.2 | 63.7 | 76 | 52.5 | 78.2 | 70.4 | 362.9 | 359.5 | 356.6 | 368.3 | 310.8 | 230.2 | 323.7 | 283.8 | 400.8 | 370.1
2381.1 | 2187.1 | -6.7 | 0 | 0 | 249.1 | 245.3 | 232.1 | 219 | 247.3 | 41.9 | 18.7 | 58.5 | 4.4 | 250.3 | 15 | 65.2 | 61.3 | 48.2 | 142.2 | 50.2 | 63.7 | 75.6 | 51.4 | 78.2 | 70.2 | 362.8 | 359.3 | 356.3 | 368.1 | 310.6 | 230 | 323.5 | 283.6 | 400.4 | 369.9
2382.1 | 2188.1 | -6.7 | 0 | 0 | 248.6 | 245 | 231.9 | 218.9 | 247.6 | 41.9 | 18.7 | 58.4 | 4.1 | 243.1 | 16.5 | 64.8 | 61 | 48.2 | 141.2 | 50 | 63.9 | 75.7 | 50.4 | 78.2 | 70 | 362.8 | 359.1 | 356.1 | 368 | 310.3 | 229.8 | 323.3 | 283.3 | 400 | 369.7
2383.1 | 2189.1 | -6.7 | 0 | 0 | 248 | 244.9 | 231.7 | 218.9 | 248 | 41.9 | 18.8 | 58.4 | 4.2 | 235.7 | 16.3 | 64.3 | 60.9 | 48.3 | 140 | 50.1 | 64.1 | 75.6 | 49.6 | 78.3 | 69.7 | 362.7 | 358.9 | 355.8 | 367.8 | 310.1 | 229.5 | 323 | 283 | 399.6 | 369.4
2384.1 | 2190.1 | -6.7 | 0 | 0 | 247.3 | 244.7 | 231.5 | 218.7 | 247.8 | 41.9 | 18.8 | 58.5 | 4.9 | 243.9 | 16.3 | 63.9 | 61.3 | 48.3 | 139 | 50.1 | 64.5 | 74.1 | 48.6 | 79.1 | 69.5 | 362.6 | 358.7 | 355.6 | 367.6 | 309.9 | 229.4 | 322.8 | 282.7 | 399.3 | 369.2
2385.1 | 2191.1 | -6.7 | 0 | 0 | 247.2 | 244 | 231.2 | 218.3 | 248.1 | 41.8 | 18.8 | 58.5 | 5.2 | 264.7 | 17.2 | 63.5 | 61.5 | 48.2 | 138 | 49.9 | 64.7 | 72.9 | 47.8 | 79.5 | 69.6 | 362.6 | 358.5 | 355.3 | 367.4 | 309.7 | 229.2 | 322.6 | 282.5 | 398.9 | 369
2386.1 | 2192.1 | -6.6 | 0 | 0 | 247.2 | 243.5 | 230.8 | 218 | 248.2 | 41.7 | 18.8 | 58.6 | 5.8 | 260.9 | 16.3 | 63.1 | 61.5 | 48.2 | 137 | 49.6 | 64.7 | 74 | 47.1 | 79.8 | 69.8 | 362.5 | 358.3 | 355 | 367.2 | 309.5 | 229.1 | 322.3 | 282.2 | 398.5 | 368.7
2387.1 | 2193.1 | -6.6 | 0 | 0 | 247.1 | 243.2 | 230.5 | 217.8 | 248.7 | 41.7 | 18.8 | 58.5 | 5 | 253.6 | 16.8 | 62.7 | 61.8 | 48.2 | 136 | 49.5 | 64.5 | 74.9 | 46.5 | 80 | 70 | 362.5 | 358.2 | 354.8 | 367.1 | 309.3 | 228.9 | 322.1 | 281.9 | 398.1 | 368.5
2388.1 | 2194.1 | -6.6 | 0 | 0 | 246.9 | 243.1 | 230.4 | 217.6 | 249.2 | 41.7 | 18.8 | 58.5 | 4.3 | 246.5 | 16.7 | 62.4 | 62.1 | 48.2 | 135.1 | 49.3 | 64.3 | 75.2 | 45.8 | 79.8 | 70.1 | 362.4 | 358 | 354.5 | 366.9 | 309 | 228.8 | 321.8 | 281.6 | 397.7 | 368.2
2389.1 | 2195.1 | -6.6 | 0 | 0 | 246.7 | 243 | 230.3 | 217.4 | 249.7 | 41.6 | 18.8 | 58.4 | 4.8 | 244.6 | 15.6 | 62.1 | 62.3 | 48.1 | 134.1 | 49.2 | 64.5 | 74.8 | 45.3 | 79 | 70.4 | 362.3 | 357.8 | 354.3 | 366.7 | 308.8 | 228.6 | 321.6 | 281.4 | 397.3 | 368
2390.1 | 2196.1 | -6.5 | 0 | 0 | 246.3 | 242.7 | 230.1 | 217.3 | 250.3 | 41.6 | 18.8 | 58.4 | 4 | 251.1 | 13.9 | 61.8 | 62.6 | 48.1 | 133.2 | 49.2 | 64.5 | 74.9 | 44.8 | 78.5 | 70.5 | 362.3 | 357.6 | 354.1 | 366.5 | 308.6 | 228.4 | 321.3 | 281.1 | 396.9 | 367.7
2391.1 | 2197.1 | -6.6 | 0 | 0 | 246.1 | 242.2 | 229.9 | 217.1 | 250.7 | 41.5 | 18.8 | 58.4 | 3.7 | 253.4 | 13.3 | 61.5 | 62.9 | 48.2 | 132.3 | 49 | 64.6 | 74.9 | 44.4 | 78.3 | 70.6 | 362.2 | 357.4 | 353.8 | 366.3 | 308.4 | 228.2 | 321.1 | 280.9 | 396.6 | 367.5
2392.1 | 2198.1 | -6.6 | 0 | 0 | 245.8 | 241.9 | 229.7 | 217 | 251.1 | 41.5 | 18.8 | 58.4 | 3.9 | 256.7 | 12.9 | 61.2 | 63.1 | 48.1 | 131.4 | 48.8 | 64.6 | 74.2 | 44.3 | 78.1 | 70.8 | 362.1 | 357.2 | 353.5 | 366.1 | 308.2 | 228.1 | 320.9 | 280.6 | 396.1 | 367.2
2393.1 | 2199.1 | -6.6 | 0 | 0 | 245.7 | 241.9 | 229.4 | 216.8 | 251.2 | 41.4 | 18.8 | 58.5 | 4.4 | 259.9 | 11.7 | 60.9 | 63.3 | 48.2 | 130.6 | 48.7 | 64.4 | 74.4 | 44.5 | 78 | 70.8 | 362.1 | 357 | 353.3 | 366 | 308 | 227.9 | 320.6 | 280.3 | 395.8 | 367
2394.1 | 2200.1 | -6.7 | 0 | 0 | 245.5 | 242 | 229.2 | 216.7 | 251.3 | 41.4 | 18.8 | 58.4 | 4.9 | 277.4 | 11.7 | 60.6 | 63.6 | 48.2 | 129.6 | 48.6 | 63.3 | 74.4 | 44.4 | 78.3 | 70.8 | 362 | 356.8 | 353 | 365.8 | 307.7 | 227.7 | 320.4 | 280 | 395.4 | 366.7
2395.1 | 2201.1 | -6.7 | 0 | 0 | 245.1 | 241.9 | 229.1 | 216.6 | 251.5 | 41.3 | 18.8 | 58.3 | 5.1 | 262.6 | 11.8 | 60.4 | 63.8 | 48.1 | 128.7 | 48.4 | 63.4 | 74.5 | 44.1 | 78.3 | 70.8 | 361.9 | 356.6 | 352.8 | 365.6 | 307.5 | 227.5 | 320.1 | 279.8 | 395 | 366.5
2396.1 | 2202.1 | -6.6 | 0 | 0 | 244.3 | 241.6 | 229 | 216.4 | 251.8 | 41.3 | 18.8 | 58.3 | 5.3 | 243.2 | 12.3 | 60.1 | 64 | 48.2 | 127.9 | 48.5 | 63.9 | 74.7 | 43.6 | 78.1 | 70.9 | 361.9 | 356.4 | 352.5 | 365.4 | 307.4 | 227.3 | 319.8 | 279.5 | 394.6 | 366.2
2397.1 | 2203.1 | -6.5 | 0 | 0 | 243.7 | 241.2 | 228.7 | 216.2 | 252 | 41.2 | 18.8 | 58.2 | 5.2 | 252.5 | 10.8 | 59.8 | 64.1 | 48.2 | 127 | 48.3 | 64 | 74.9 | 43.4 | 77.9 | 70.8 | 361.8 | 356.2 | 352.3 | 365.2 | 307.2 | 227.1 | 319.6 | 279.2 | 394.2 | 366
2398.1 | 2204.1 | -6.4 | 0 | 0 | 243.5 | 240.8 | 228.5 | 216.1 | 252 | 41.2 | 18.8 | 58.2 | 5.3 | 241.4 | 10.6 | 59.5 | 64.4 | 48.2 | 126.1 | 48.2 | 64.2 | 74.4 | 44.8 | 77.8 | 70.8 | 361.7 | 356 | 352 | 365.1 | 306.9 | 226.9 | 319.4 | 279 | 393.8 | 365.8
2399.1 | 2205.1 | -6.4 | 0 | 0 | 243.4 | 240.7 | 228.3 | 215.9 | 251.6 | 41.2 | 18.8 | 58.2 | 4.9 | 254 | 10.7 | 59.2 | 64.5 | 48.2 | 125.2 | 48 | 64.4 | 74.1 | 44.6 | 77.6 | 70.8 | 361.6 | 355.8 | 351.8 | 364.9 | 306.7 | 226.7 | 319.1 | 278.7 | 393.5 | 365.5
2400.1 | 2206.1 | -6.3 | 0 | 0 | 243.3 | 240.6 | 228 | 215.7 | 251.2 | 41.2 | 18.8 | 58.3 | 4.7 | 257.8 | 10.8 | 58.8 | 64.7 | 48.2 | 124.4 | 48 | 63.7 | 74.6 | 44.3 | 77.7 | 70.7 | 361.6 | 355.6 | 351.5 | 364.7 | 306.5 | 226.5 | 318.9 | 278.5 | 393.1 | 365.3
2401.1 | 2207.1 | -6.3 | 0 | 0 | 243.2 | 240.5 | 227.9 | 215.5 | 250.7 | 41.1 | 18.8 | 58.3 | 5.5 | 261.1 | 10.4 | 58.5 | 65 | 48.2 | 123.5 | 47.9 | 63.5 | 74.9 | 44 | 77.7 | 70.6 | 361.5 | 355.4 | 351.3 | 364.5 | 306.3 | 226.3 | 318.6 | 278.2 | 392.7 | 365
2402.1 | 2208.1 | -6.6 | 0 | 0 | 242.9 | 240.3 | 227.9 | 215.4 | 250.4 | 41.2 | 18.8 | 58.3 | 4.8 | 254.6 | 12.1 | 58.3 | 64.8 | 48.3 | 122.4 | 47.7 | 63.9 | 74.9 | 43.7 | 77.6 | 70.6 | 361.4 | 355.2 | 351 | 364.3 | 306.1 | 226.1 | 318.4 | 278 | 392.3 | 364.8
2403.1 | 2209.1 | -6.6 | 0 | 0 | 242.8 | 240.1 | 227.7 | 215.2 | 250.6 | 41.2 | 18.8 | 58.2 | 4.4 | 258.8 | 11 | 58.2 | 64.7 | 48.3 | 121.6 | 47.6 | 63.2 | 75 | 43.5 | 77.6 | 70.8 | 361.4 | 355 | 350.8 | 364.2 | 305.9 | 226 | 318.2 | 277.8 | 392 | 364.6
2404.1 | 2210.1 | -6.5 | 0 | 0 | 242.8 | 239.6 | 227.3 | 215 | 250.9 | 41.2 | 18.8 | 58.2 | 4.3 | 252.4 | 11.5 | 57.9 | 65 | 48.3 | 120.8 | 47.7 | 62.5 | 73.6 | 43.5 | 77.8 | 70.8 | 361.3 | 354.8 | 350.5 | 364 | 305.7 | 225.8 | 317.9 | 277.5 | 391.6 | 364.3
2405.1 | 2211.1 | -6.3 | 0 | 0 | 242.4 | 239.6 | 227.1 | 214.9 | 251 | 41.2 | 18.8 | 58.1 | 4.4 | 249.7 | 13.8 | 57.6 | 65.3 | 48.4 | 119.9 | 47.5 | 62.2 | 70.7 | 43.4 | 78 | 70.8 | 361.2 | 354.6 | 350.3 | 363.8 | 305.5 | 225.6 | 317.6 | 277.2 | 391.2 | 364.1
2406.1 | 2212.1 | -6.3 | 0 | 0 | 241.8 | 239.6 | 227 | 214.6 | 251.2 | 41.1 | 18.8 | 58.1 | 4.4 | 258.9 | 12.9 | 57.2 | 65.7 | 48.4 | 119.2 | 47.5 | 62.8 | 71.8 | 43.3 | 77.9 | 70.7 | 361.1 | 354.4 | 350 | 363.6 | 305.3 | 225.5 | 317.4 | 277 | 390.8 | 363.9
2407.1 | 2213.1 | -6.2 | 0 | 0 | 241.6 | 239.4 | 226.7 | 214.4 | 251.2 | 41.1 | 18.8 | 58.1 | 4.2 | 238.1 | 11.7 | 56.9 | 65.7 | 48.4 | 118.2 | 47.4 | 63.2 | 73.3 | 43.2 | 77.7 | 70.5 | 361.1 | 354.2 | 349.8 | 363.4 | 305.2 | 225.3 | 317.1 | 276.7 | 390.5 | 363.6
2408.1 | 2214.1 | -6.3 | 0 | 0 | 241.6 | 238.7 | 226.4 | 214.3 | 251.3 | 41 | 18.8 | 57.9 | 4.6 | 247.1 | 11.3 | 56.5 | 66.1 | 48.4 | 117.4 | 47.2 | 63.5 | 73.4 | 43.3 | 77.6 | 70.5 | 361 | 354 | 349.5 | 363.2 | 305 | 225.1 | 316.9 | 276.5 | 390.1 | 363.4
2409.1 | 2215.1 | -6.4 | 0 | 0 | 241.5 | 238.1 | 226 | 214.2 | 251.3 | 41 | 18.8 | 57.8 | 4.4 | 253.5 | 11.3 | 56.2 | 66.5 | 48.3 | 116.6 | 46.9 | 63.5 | 73.6 | 44.1 | 77.6 | 70.6 | 360.9 | 353.8 | 349.3 | 363.1 | 304.8 | 225 | 316.7 | 276.2 | 389.7 | 363.2
2410.1 | 2216.1 | -6.5 | 0 | 0 | 241.3 | 237.9 | 225.6 | 214.1 | 251.4 | 40.9 | 18.9 | 57.8 | 4.7 | 240.8 | 11.6 | 55.8 | 66.7 | 48.3 | 115.7 | 46.7 | 63.8 | 73.8 | 43.8 | 77.8 | 70.6 | 360.8 | 353.6 | 349.1 | 362.9 | 304.6 | 224.9 | 316.4 | 276 | 389.4 | 362.9
2411.1 | 2217.1 | -6.6 | 0 | 0 | 241.2 | 237.7 | 225.3 | 213.9 | 251.5 | 40.9 | 18.9 | 57.7 | 6 | 241.5 | 10.9 | 55.6 | 67.1 | 48.3 | 115 | 46.5 | 64.1 | 73.9 | 43.8 | 77.7 | 70.8 | 360.7 | 353.4 | 348.8 | 362.7 | 304.5 | 224.7 | 316.1 | 275.7 | 389 | 362.7
2412.1 | 2218.1 | -6.6 | 0 | 0 | 240.9 | 237.4 | 225.2 | 213.8 | 251.6 | 40.8 | 18.9 | 57.7 | 5.9 | 240.5 | 9 | 55.4 | 67.7 | 48.3 | 114.2 | 46.5 | 64.4 | 74.5 | 43.6 | 77.9 | 70.8 | 360.7 | 353.2 | 348.6 | 362.5 | 304.2 | 224.5 | 315.9 | 275.4 | 388.6 | 362.5
2413.1 | 2219.1 | -6.6 | 0 | 0 | 240.6 | 237.1 | 225.2 | 213.7 | 251.6 | 40.8 | 18.9 | 57.7 | 5.5 | 247.5 | 8 | 55.3 | 67.9 | 48.2 | 113.2 | 46.5 | 64.6 | 74.1 | 43.4 | 78.2 | 70.9 | 360.6 | 353 | 348.3 | 362.3 | 304 | 224.3 | 315.6 | 275.2 | 388.3 | 362.2
2414.1 | 2220.1 | -6.7 | 0 | 0 | 240.4 | 236.9 | 225 | 213.6 | 251.6 | 40.9 | 18.9 | 57.6 | 5.7 | 257.8 | 9.9 | 54.8 | 68.3 | 48.2 | 112.6 | 46.4 | 64.8 | 74.1 | 43.1 | 78.5 | 70.8 | 360.5 | 352.8 | 348.1 | 362.1 | 303.9 | 224.2 | 315.4 | 274.9 | 387.9 | 362
2415.1 | 2221.1 | -6.7 | 0 | 0 | 240.2 | 236.7 | 224.8 | 213.4 | 251.5 | 40.8 | 18.9 | 57.5 | 6.3 | 244.3 | 12.2 | 54.6 | 68.6 | 48.3 | 111.8 | 46.3 | 64.8 | 74.2 | 42.9 | 78.9 | 70.8 | 360.4 | 352.5 | 347.8 | 362 | 303.7 | 224 | 315.2 | 274.7 | 387.5 | 361.8
2416.1 | 2222.1 | -6.7 | 0 | 0 | 239.9 | 236.7 | 224.7 | 213.2 | 251.4 | 40.8 | 18.9 | 57.4 | 5.5 | 233 | 14.2 | 54.6 | 68.8 | 48.3 | 110.9 | 46.2 | 64.7 | 74.6 | 42.8 | 79.1 | 70.7 | 360.3 | 352.3 | 347.6 | 361.8 | 303.5 | 223.8 | 315 | 274.4 | 387.2 | 361.5
2417.1 | 2223.1 | -6.7 | 0 | 0 | 239.7 | 236.8 | 224.5 | 212.9 | 250.9 | 40.8 | 18.9 | 57.4 | 5.6 | 241.3 | 13.2 | 54.6 | 69.1 | 48.3 | 110.3 | 46.2 | 64.8 | 74.6 | 42.6 | 79.2 | 70.7 | 360.2 | 352.1 | 347.4 | 361.6 | 303.4 | 223.7 | 314.7 | 274.2 | 386.8 | 361.3
2418.1 | 2224.1 | -6.6 | 0 | 0 | 239.7 | 236.6 | 224.3 | 212.6 | 250.7 | 40.7 | 18.9 | 57.3 | 5.1 | 215.9 | 13 | 54.4 | 69.4 | 48.3 | 109.5 | 46.2 | 65.1 | 74.6 | 42.3 | 78.9 | 70.7 | 360.2 | 351.9 | 347.1 | 361.4 | 303.2 | 223.5 | 314.5 | 273.9 | 386.4 | 361.1
2419.1 | 2225.1 | -6.5 | 0 | 0 | 239.6 | 236.1 | 224.2 | 212.4 | 250.7 | 40.7 | 18.9 | 57.3 | 4.7 | 240.8 | 12 | 54.1 | 69.7 | 48.3 | 108.7 | 46.1 | 65.2 | 74.7 | 42.1 | 78.7 | 70.7 | 360.1 | 351.7 | 346.9 | 361.2 | 303 | 223.3 | 314.3 | 273.7 | 386.1 | 360.8
2420.1 | 2226.1 | -6.5 | 0 | 0 | 239.5 | 235.8 | 224 | 212.3 | 250.4 | 40.6 | 18.9 | 57.3 | 4.2 | 249.1 | 13.9 | 54.2 | 70.1 | 48.2 | 108.1 | 46.1 | 65.4 | 74.7 | 41.6 | 78.7 | 70.7 | 360 | 351.5 | 346.6 | 361.1 | 302.8 | 223.2 | 314 | 273.4 | 385.7 | 360.6
2421.1 | 2227.1 | -6.5 | 0 | 0 | 239.3 | 235.5 | 223.8 | 212.1 | 249.9 | 40.5 | 18.9 | 57.3 | 5 | 232.4 | 12.8 | 54.2 | 70.5 | 48.2 | 107.4 | 46 | 65.4 | 74.3 | 41.3 | 78.8 | 70.6 | 359.9 | 351.3 | 346.4 | 360.9 | 302.6 | 223.1 | 313.8 | 273.2 | 385.4 | 360.4
2422.1 | 2228.1 | -6.6 | 0 | 0 | 239 | 235.2 | 223.4 | 212.1 | 249.5 | 40.5 | 18.9 | 57.2 | 5.4 | 233.4 | 11.4 | 54 | 71 | 48.2 | 106.7 | 45.9 | 65.3 | 73.5 | 41.1 | 79.1 | 70.5 | 359.8 | 351.1 | 346.2 | 360.7 | 302.4 | 222.9 | 313.6 | 273 | 385 | 360.1
2423.1 | 2229.1 | -6.6 | 0 | 0 | 238.7 | 235.2 | 223.2 | 212.1 | 249.4 | 40.4 | 18.9 | 57.1 | 5.5 | 238.9 | 12.1 | 54 | 71.4 | 48.2 | 106 | 45.8 | 65.1 | 73.3 | 40.8 | 79.3 | 70.7 | 359.7 | 350.9 | 345.9 | 360.5 | 302.2 | 222.8 | 313.4 | 272.7 | 384.6 | 359.9
2424.1 | 2230.1 | -6.7 | 0 | 0 | 238.4 | 235.4 | 222.9 | 212 | 249.4 | 40.3 | 18.9 | 57 | 5.8 | 235.3 | 13.1 | 53.8 | 71.9 | 48.1 | 105.2 | 45.8 | 65 | 73.5 | 40.6 | 79.2 | 70.7 | 359.7 | 350.7 | 345.7 | 360.3 | 302 | 222.6 | 313.1 | 272.5 | 384.3 | 359.7
2425.1 | 2231.1 | -6.6 | 0 | 0 | 238.1 | 235.2 | 222.7 | 211.8 | 249.4 | 40.3 | 18.9 | 56.9 | 5.4 | 248.7 | 12.3 | 53.6 | 72.2 | 48.1 | 104.6 | 45.6 | 65.3 | 73.5 | 40.6 | 79.4 | 70.7 | 359.6 | 350.5 | 345.4 | 360.2 | 301.8 | 222.5 | 312.9 | 272.2 | 383.9 | 359.4
2426.1 | 2232.1 | -6.6 | 0 | 0 | 238 | 234.7 | 222.5 | 211.6 | 249.1 | 40.2 | 18.9 | 56.8 | 5.7 | 248.8 | 11.9 | 53.4 | 72.6 | 48.1 | 103.9 | 45.5 | 65.5 | 73.1 | 40.7 | 79.2 | 70.8 | 359.5 | 350.3 | 345.2 | 360 | 301.6 | 222.3 | 312.6 | 272 | 383.6 | 359.2
2427.1 | 2233.1 | -6.4 | 0 | 0 | 238 | 234.4 | 222.4 | 211.4 | 248.6 | 40.1 | 18.9 | 56.7 | 5 | 264.9 | 10.1 | 53.4 | 73.1 | 48.1 | 103.2 | 45.4 | 65.3 | 73.1 | 40.8 | 79.1 | 70.8 | 359.4 | 350.1 | 345 | 359.8 | 301.4 | 222.2 | 312.4 | 271.7 | 383.2 | 359
2428.1 | 2234.1 | -6.3 | 0 | 0 | 238 | 234.5 | 222.2 | 211.1 | 248.3 | 40 | 18.9 | 56.6 | 4.2 | 226.7 | 10.6 | 53.3 | 73.5 | 48 | 102.5 | 45.3 | 65.2 | 73.3 | 40.8 | 78.9 | 70.7 | 359.3 | 349.9 | 344.8 | 359.6 | 301.2 | 222 | 312.2 | 271.5 | 382.9 | 358.7
2429.1 | 2235.1 | -6.4 | 0 | 0 | 237.8 | 234.5 | 221.9 | 211 | 248.2 | 40 | 18.9 | 56.6 | 4.8 | 261.5 | 10 | 53.4 | 73.9 | 47.9 | 101.8 | 45.1 | 65.2 | 73.5 | 41.1 | 78.8 | 70.6 | 359.2 | 349.7 | 344.5 | 359.4 | 301 | 221.8 | 311.9 | 271.2 | 382.5 | 358.5
2430.1 | 2236.1 | -6.5 | 0 | 0 | 237.5 | 234.4 | 221.7 | 210.9 | 248 | 39.9 | 18.9 | 56.5 | 5 | 232.1 | 9.6 | 53.3 | 74.2 | 47.9 | 101 | 45 | 64.7 | 73.6 | 40.8 | 78.9 | 70.6 | 359.1 | 349.5 | 344.3 | 359.2 | 300.8 | 221.7 | 311.7 | 271 | 382.2 | 358.3
2431.1 | 2237.1 | -6.5 | 0 | 0 | 237.4 | 234.2 | 221.6 | 210.7 | 247.9 | 39.8 | 18.9 | 56.5 | 4.5 | 244.9 | 9 | 53.1 | 74.6 | 47.8 | 100.4 | 44.8 | 64.5 | 73.9 | 40.8 | 79 | 70.6 | 359 | 349.3 | 344 | 359 | 300.6 | 221.5 | 311.5 | 270.8 | 381.8 | 358.1
2432.1 | 2238.1 | -6.4 | 0 | 0 | 237.3 | 234 | 221.6 | 210.5 | 247.8 | 39.8 | 18.9 | 56.5 | 4.9 | 226.2 | 8.9 | 53.1 | 75 | 47.8 | 99.7 | 44.8 | 64.5 | 73.4 | 41.1 | 78.8 | 70.6 | 358.9 | 349.1 | 343.8 | 358.9 | 300.4 | 221.3 | 311.2 | 270.6 | 381.5 | 357.8
2433.1 | 2239.1 | -6.3 | 0 | 0 | 236.9 | 233.8 | 221.3 | 210.3 | 247.8 | 39.8 | 18.9 | 56.5 | 4 | 237.7 | 9.5 | 53 | 75.3 | 47.7 | 99 | 44.7 | 64 | 73.4 | 41.2 | 79 | 70.6 | 358.9 | 349 | 343.6 | 358.7 | 300.2 | 221.2 | 311 | 270.3 | 381.1 | 357.6
2434.1 | 2240.1 | -6.5 | 0 | 0 | 236.9 | 233.6 | 221.1 | 210.3 | 247.7 | 39.8 | 18.9 | 56.5 | 4 | 228.8 | 8.4 | 52.7 | 75.8 | 47.7 | 98.4 | 44.5 | 64.2 | 73.7 | 41 | 79.1 | 70.5 | 358.8 | 348.8 | 343.4 | 358.5 | 300 | 221 | 310.8 | 270.1 | 380.8 | 357.4
2435.1 | 2241.1 | -6.5 | 0 | 0 | 236.8 | 233.4 | 220.8 | 210.2 | 247.4 | 39.8 | 18.9 | 56.5 | 3.7 | 224.1 | 8.1 | 52.8 | 76.1 | 47.7 | 97.8 | 44.5 | 64.5 | 73.5 | 40.8 | 78.7 | 70.5 | 358.7 | 348.6 | 343.1 | 358.3 | 299.8 | 220.9 | 310.6 | 269.8 | 380.4 | 357.1
2436.1 | 2242.1 | -6.6 | 0 | 0 | 236.8 | 233.1 | 220.6 | 210.1 | 247.1 | 39.8 | 19 | 56.5 | 3.9 | 242 | 7.3 | 52.7 | 76.5 | 47.7 | 97.2 | 44.5 | 64.5 | 73.1 | 40.7 | 78.2 | 70.6 | 358.6 | 348.4 | 342.9 | 358.1 | 299.6 | 220.8 | 310.3 | 269.6 | 380.1 | 356.9
2437.1 | 2243.1 | -6.7 | 0 | 0 | 236.3 | 232.9 | 220.4 | 209.9 | 247.1 | 39.8 | 19 | 56.5 | 4.7 | 248.9 | 6.8 | 52.5 | 76.8 | 47.7 | 96.6 | 44.5 | 64.6 | 73.5 | 40.8 | 78.2 | 70.6 | 358.5 | 348.2 | 342.7 | 357.9 | 299.4 | 220.6 | 310.1 | 269.4 | 379.7 | 356.7
2438.1 | 2244.1 | -6.7 | 0 | 0 | 235.8 | 232.8 | 220.2 | 209.8 | 247.2 | 39.8 | 19 | 56.4 | 4.7 | 243.3 | 7.1 | 52.2 | 77.1 | 47.7 | 96 | 44.4 | 63.9 | 73.7 | 41.2 | 78.6 | 70.7 | 358.4 | 348 | 342.4 | 357.7 | 299.2 | 220.4 | 309.9 | 269.2 | 379.4 | 356.4
2439.1 | 2245.1 | -6.7 | 0 | 0 | 235.5 | 232.7 | 220 | 209.6 | 247.3 | 39.8 | 19 | 56.4 | 5.2 | 238.1 | 7.2 | 52.1 | 77.4 | 47.8 | 95.3 | 44.4 | 63.3 | 72.4 | 42.5 | 78.8 | 70.7 | 358.3 | 347.8 | 342.2 | 357.5 | 299.1 | 220.3 | 309.6 | 268.9 | 379 | 356.2
2440.1 | 2246.1 | -6.6 | 0 | 0 | 235.2 | 232.5 | 219.9 | 209.3 | 247.2 | 39.8 | 19 | 56.2 | 5.4 | 231.7 | 6.4 | 52.2 | 77.6 | 47.7 | 94.7 | 44.5 | 63.3 | 71.5 | 45.3 | 78.7 | 70.6 | 358.2 | 347.7 | 342 | 357.4 | 298.9 | 220.2 | 309.4 | 268.7 | 378.7 | 356
2441.1 | 2247.1 | -6.5 | 0 | 0 | 235 | 232.2 | 219.8 | 209.1 | 247.1 | 39.8 | 19 | 56.2 | 5.6 | 212.9 | 6 | 52.3 | 77.6 | 47.7 | 94.2 | 44.4 | 63.2 | 71.5 | 48.2 | 78.7 | 70.6 | 358.1 | 347.5 | 341.7 | 357.2 | 298.7 | 220 | 309.1 | 268.5 | 378.3 | 355.7
2442.1 | 2248.1 | -6.3 | 0 | 0 | 234.9 | 231.9 | 219.6 | 208.9 | 247.1 | 39.8 | 19 | 56.1 | 4.7 | 227.6 | 6.2 | 52.2 | 77.7 | 47.6 | 93.6 | 44.4 | 63.7 | 72.6 | 48.6 | 78.6 | 70.6 | 358 | 347.3 | 341.5 | 357 | 298.5 | 219.9 | 308.9 | 268.2 | 378 | 355.5
2443.1 | 2249.1 | -6.4 | 0 | 0 | 234.6 | 231.6 | 219.5 | 208.9 | 247.1 | 39.8 | 19 | 56.1 | 4.7 | 262.8 | 6.5 | 51.9 | 78 | 47.6 | 93 | 44.4 | 63.8 | 73.4 | 48.5 | 78.5 | 70.6 | 357.9 | 347.1 | 341.3 | 356.8 | 298.3 | 219.7 | 308.6 | 268 | 377.7 | 355.3
2444.1 | 2250.1 | -6.6 | 0 | 0 | 234.2 | 231.4 | 219.4 | 208.9 | 247.1 | 39.8 | 19 | 56 | 4.3 | 241.3 | 7.9 | 51.5 | 78.3 | 47.6 | 92.5 | 44.4 | 64 | 73.7 | 48.3 | 78.5 | 70.6 | 357.8 | 346.9 | 341.1 | 356.6 | 298.1 | 219.5 | 308.4 | 267.7 | 377.3 | 355
2445.1 | 2251.1 | -6.6 | 0 | 0 | 233.7 | 231.3 | 219.2 | 208.7 | 247 | 39.8 | 19 | 56 | 4.2 | 225.7 | 9.2 | 51.5 | 78.7 | 47.6 | 91.9 | 44.2 | 63.7 | 73.8 | 49.1 | 78.7 | 70.5 | 357.8 | 346.7 | 340.8 | 356.4 | 297.9 | 219.4 | 308.2 | 267.5 | 377 | 354.8
2446.1 | 2252.1 | -6.4 | 0 | 0 | 233.6 | 231.1 | 219.1 | 208.5 | 247 | 39.7 | 19 | 55.9 | 3.9 | 226.1 | 10.8 | 51.7 | 78.9 | 47.6 | 91.4 | 44.1 | 63.6 | 73.8 | 50.3 | 79 | 70.5 | 357.7 | 346.5 | 340.6 | 356.2 | 297.7 | 219.3 | 308 | 267.3 | 376.6 | 354.6
2447.1 | 2253.1 | -6.4 | 0 | 0 | 233.5 | 230.7 | 218.8 | 208.3 | 247 | 39.6 | 19 | 55.9 | 4.1 | 217.1 | 12.7 | 51.6 | 79.2 | 47.6 | 90.9 | 44 | 64 | 73.6 | 49.7 | 79.1 | 70.6 | 357.6 | 346.3 | 340.4 | 356 | 297.6 | 219.2 | 307.8 | 267.1 | 376.3 | 354.4
2448.1 | 2254.1 | -6.3 | 0 | 0 | 233.4 | 230.5 | 218.6 | 208 | 246.9 | 39.5 | 19 | 55.8 | 4.5 | 231.6 | 10.5 | 51.4 | 79.5 | 47.5 | 90.4 | 43.9 | 64.1 | 73.8 | 49.1 | 79.2 | 70.6 | 357.5 | 346.1 | 340.2 | 355.9 | 297.4 | 219 | 307.6 | 266.8 | 376 | 354.1
2449.1 | 2255.1 | -6.5 | 0 | 0 | 233.5 | 230.2 | 218.4 | 207.8 | 246.5 | 39.4 | 19 | 55.8 | 3.9 | 210.3 | 8.4 | 51.4 | 79.8 | 47.4 | 89.8 | 43.7 | 64.2 | 74 | 49.7 | 79.2 | 70.7 | 357.4 | 346 | 339.9 | 355.7 | 297.2 | 218.8 | 307.3 | 266.6 | 375.6 | 353.9
2450.1 | 2256.1 | -6.4 | 0 | 0 | 233.7 | 230.1 | 218.2 | 207.6 | 245.9 | 39.3 | 19 | 55.8 | 2.9 | 237.4 | 8.1 | 51.3 | 80.1 | 47.5 | 89.3 | 43.6 | 64.4 | 74.3 | 49.8 | 78.9 | 70.6 | 357.3 | 345.8 | 339.7 | 355.5 | 297 | 218.7 | 307.1 | 266.4 | 375.3 | 353.7
2451.1 | 2257.1 | -6.5 | 0 | 0 | 233.4 | 230.1 | 218 | 207.6 | 245.3 | 39.2 | 19 | 55.8 | 3.2 | 225 | 8.6 | 51.3 | 80.5 | 47.9 | 88.8 | 43.5 | 64.5 | 74.4 | 49.6 | 78.9 | 70.6 | 357.2 | 345.6 | 339.5 | 355.3 | 296.8 | 218.6 | 306.9 | 266.1 | 375 | 353.5
2452.1 | 2258.1 | -6.6 | 0 | 0 | 233 | 230.1 | 217.8 | 207.5 | 244.6 | 39.2 | 19 | 55.8 | 4.2 | 207.9 | 9.5 | 51.4 | 80.7 | 48.4 | 88.3 | 43.4 | 64.6 | 74.4 | 48.6 | 78.9 | 70.6 | 357.1 | 345.4 | 339.3 | 355.1 | 296.6 | 218.4 | 306.7 | 265.9 | 374.6 | 353.3
2453.1 | 2259.1 | -6.6 | 0 | 0 | 232.7 | 229.9 | 217.8 | 207.3 | 243.9 | 39.1 | 19 | 55.8 | 5.1 | 215.7 | 11.3 | 51.4 | 80.9 | 48.4 | 87.7 | 43.3 | 64.8 | 74.4 | 47.8 | 78.9 | 70.5 | 357 | 345.2 | 339 | 354.9 | 296.5 | 218.2 | 306.5 | 265.7 | 374.3 | 353
2454.1 | 2260.1 | -6.5 | 0 | 0 | 232.5 | 229.6 | 217.8 | 207.2 | 242.9 | 39 | 19 | 55.8 | 5.9 | 201.8 | 11.3 | 51.4 | 81.2 | 48.4 | 87.2 | 43.2 | 64.8 | 74.1 | 46.8 | 78.9 | 70.6 | 356.9 | 345 | 338.8 | 354.7 | 296.3 | 218.1 | 306.2 | 265.5 | 373.9 | 352.8
2455.1 | 2261.1 | -6.4 | 0 | 0 | 232.2 | 229.7 | 217.5 | 207 | 242.3 | 38.9 | 19 | 55.7 | 5.4 | 211.7 | 8.4 | 51.1 | 81.4 | 48.3 | 86.8 | 43.1 | 64.8 | 74.1 | 46.5 | 79.2 | 70.7 | 356.8 | 344.9 | 338.6 | 354.5 | 296.1 | 217.9 | 306 | 265.3 | 373.6 | 352.6
2456.1 | 2262.1 | -6.4 | 0 | 0 | 232.1 | 229.6 | 217.3 | 206.9 | 241.8 | 38.8 | 19 | 55.7 | 5 | 240.8 | 6.2 | 51.1 | 81.6 | 48.2 | 86.3 | 42.9 | 64.6 | 74.5 | 47.2 | 79.5 | 70.8 | 356.7 | 344.7 | 338.4 | 354.4 | 295.9 | 217.7 | 305.8 | 265 | 373.3 | 352.3
2457.1 | 2263.1 | -6.4 | 0 | 0 | 231.9 | 229.3 | 217.2 | 206.7 | 241.7 | 38.7 | 19.1 | 55.7 | 4.6 | 204.2 | 5.5 | 51.1 | 81.8 | 48.1 | 85.9 | 42.8 | 64.6 | 74.6 | 47.2 | 79.4 | 70.8 | 356.6 | 344.5 | 338.1 | 354.2 | 295.7 | 217.6 | 305.6 | 264.8 | 373 | 352.1
2458.1 | 2264.1 | -6.3 | 0 | 0 | 231.6 | 229.2 | 217 | 206.6 | 241.7 | 38.6 | 19.1 | 55.6 | 5 | 251.8 | 4.7 | 51.2 | 81.9 | 48 | 85.5 | 42.7 | 64.5 | 74.7 | 47.8 | 79.3 | 70.7 | 356.5 | 344.3 | 337.9 | 354 | 295.5 | 217.4 | 305.4 | 264.6 | 372.6 | 351.9
2459.1 | 2265.1 | -6.5 | 0 | 0 | 231.5 | 229 | 216.9 | 206.5 | 241.5 | 38.5 | 19.1 | 55.6 | 5 | 252 | 6 | 51.3 | 82.1 | 47.9 | 85 | 42.6 | 64.5 | 74.8 | 50 | 79.3 | 70.6 | 356.4 | 344.1 | 337.7 | 353.8 | 295.3 | 217.2 | 305.1 | 264.4 | 372.3 | 351.7
2460.1 | 2266.1 | -6.5 | 0 | 0 | 231.3 | 228.7 | 216.7 | 206.3 | 241.5 | 38.5 | 19.1 | 55.6 | 4.2 | 254.6 | 8.9 | 51.2 | 82.5 | 47.8 | 84.6 | 42.5 | 64.5 | 74.5 | 51.1 | 79.1 | 70.5 | 356.3 | 343.9 | 337.5 | 353.6 | 295.1 | 217.1 | 304.9 | 264.1 | 372 | 351.4
2461.1 | 2267.1 | -6.5 | 0 | 0 | 231 | 228.5 | 216.6 | 206.1 | 241.2 | 38.4 | 19.1 | 55.6 | 4.8 | 246.7 | 12.1 | 51.1 | 82.8 | 47.7 | 84.2 | 42.4 | 64.2 | 74.5 | 51.3 | 78.8 | 70.6 | 356.2 | 343.7 | 337.3 | 353.4 | 294.9 | 216.9 | 304.7 | 263.9 | 371.6 | 351.2
2462.1 | 2268.1 | -6.5 | 0 | 0 | 230.7 | 228.5 | 216.4 | 206 | 240.3 | 38.4 | 19.1 | 55.6 | 5.1 | 240.9 | 15.1 | 51.2 | 83.1 | 47.5 | 83.7 | 42.2 | 62.6 | 74.4 | 50.7 | 78.7 | 70.6 | 356.1 | 343.5 | 337 | 353.2 | 294.7 | 216.8 | 304.5 | 263.7 | 371.3 | 351
2463.1 | 2269.1 | -6.5 | 0 | 0 | 230.5 | 228.2 | 216.2 | 206 | 238.9 | 38.4 | 19.1 | 55.6 | 6.1 | 225.7 | 13.4 | 51 | 83.3 | 47.4 | 83.4 | 42.2 | 62.7 | 74.4 | 50.4 | 78.7 | 70.6 | 356 | 343.4 | 336.8 | 353 | 294.6 | 216.6 | 304.3 | 263.5 | 371 | 350.8
2464.1 | 2270.1 | -6.5 | 0 | 0 | 230.2 | 228.2 | 216 | 206 | 238.2 | 38.3 | 19.1 | 55.7 | 6.3 | 226.3 | 12.1 | 50.6 | 83.5 | 47.1 | 83 | 42.1 | 63.5 | 74.4 | 50 | 78.2 | 70.4 | 356 | 343.2 | 336.6 | 352.8 | 294.4 | 216.5 | 304 | 263.3 | 370.7 | 350.5
2465.1 | 2271.1 | -6.4 | 0 | 0 | 229.8 | 228.2 | 215.8 | 205.9 | 237.8 | 38.3 | 19.1 | 55.7 | 5.3 | 209.8 | 10 | 50.8 | 83.4 | 47 | 82.5 | 41.9 | 63.3 | 74.5 | 49.2 | 78.1 | 70.4 | 355.9 | 343 | 336.4 | 352.6 | 294.2 | 216.3 | 303.8 | 263 | 370.3 | 350.3
2466.1 | 2272.1 | -6.5 | 0 | 0 | 229.9 | 227.5 | 215.7 | 205.7 | 237.7 | 38.4 | 19.1 | 55.6 | 6.1 | 201.7 | 8.1 | 50.9 | 83.7 | 46.9 | 82.1 | 41.8 | 62.5 | 74.6 | 48.2 | 78.1 | 70.3 | 355.8 | 342.8 | 336.2 | 352.5 | 294 | 216.2 | 303.6 | 262.8 | 370 | 350.1
2467.1 | 2273.1 | -6.5 | 0 | 0 | 229.7 | 227.3 | 215.5 | 205.4 | 237.8 | 38.4 | 19.1 | 55.6 | 5.6 | 232.8 | 7.1 | 50.9 | 83.9 | 46.8 | 81.7 | 41.8 | 62.5 | 74.1 | 47.3 | 77.9 | 70.3 | 355.7 | 342.6 | 335.9 | 352.3 | 293.8 | 216 | 303.4 | 262.6 | 369.7 | 349.9
2468.1 | 2274.1 | -6.5 | 0 | 0 | 229.4 | 227.3 | 215.4 | 205.2 | 238 | 38.4 | 19.1 | 55.5 | 5.4 | 224.5 | 7.6 | 50.4 | 84 | 46.6 | 81.3 | 41.7 | 62.4 | 72.4 | 46.3 | 77.8 | 70 | 355.6 | 342.4 | 335.7 | 352.1 | 293.6 | 215.9 | 303.1 | 262.4 | 369.4 | 349.6
2469.1 | 2275.1 | -6.5 | 0 | 0 | 229 | 227.2 | 215.1 | 205 | 238.5 | 38.4 | 19.1 | 55.5 | 5.4 | 231.5 | 10.5 | 50.1 | 83.9 | 46.5 | 80.9 | 41.6 | 62.2 | 72.3 | 45.4 | 77.8 | 69.9 | 355.5 | 342.2 | 335.5 | 351.9 | 293.4 | 215.7 | 302.9 | 262.1 | 369.1 | 349.4
2470.1 | 2276.1 | -6.4 | 0 | 0 | 228.8 | 227.3 | 214.9 | 204.9 | 238.9 | 38.4 | 19.1 | 55.5 | 4.4 | 241.2 | 11.1 | 49.8 | 83.7 | 46.4 | 80.5 | 41.4 | 62.7 | 73 | 44.6 | 78 | 69.8 | 355.4 | 342 | 335.3 | 351.7 | 293.3 | 215.6 | 302.7 | 261.9 | 368.8 | 349.2
2471.1 | 2277.1 | -6.6 | 0 | 0 | 228.8 | 227.1 | 214.9 | 204.7 | 239 | 38.5 | 19.1 | 55.5 | 4.4 | 224.8 | 9 | 49.9 | 83.8 | 46.4 | 80.1 | 41.4 | 63.2 | 72.6 | 44.1 | 78 | 69.6 | 355.3 | 341.8 | 335.1 | 351.5 | 293.1 | 215.4 | 302.5 | 261.7 | 368.5 | 348.9
2472.1 | 2278.1 | -6.6 | 0 | 0 | 228.8 | 226.9 | 214.9 | 204.6 | 238.9 | 38.5 | 19.1 | 55.4 | 4.8 | 256.4 | 7.9 | 50.1 | 83.8 | 46.5 | 79.7 | 41.3 | 63.5 | 72.5 | 43.8 | 78.3 | 69.5 | 355.2 | 341.6 | 334.9 | 351.3 | 292.9 | 215.3 | 302.3 | 261.5 | 368.1 | 348.7
2473.1 | 2279.1 | -6.5 | 0 | 0 | 228.6 | 226.9 | 214.7 | 204.5 | 238.7 | 38.5 | 19.1 | 55.4 | 5.7 | 218.8 | 8.6 | 50 | 83.7 | 46.4 | 79.3 | 41.2 | 63.9 | 72.1 | 43.5 | 78.9 | 69.3 | 355.1 | 341.5 | 334.6 | 351.1 | 292.8 | 215.2 | 302.1 | 261.3 | 367.8 | 348.5
2474.1 | 2280.1 | -6.3 | 0 | 0 | 228.6 | 226.9 | 214.4 | 204.5 | 238.5 | 38.5 | 19.1 | 55.4 | 4.2 | 246.3 | 9.2 | 49.9 | 83.6 | 46.4 | 79 | 41.1 | 64 | 72.2 | 43.4 | 79.4 | 69.5 | 355 | 341.3 | 334.4 | 351 | 292.6 | 215 | 301.8 | 261.1 | 367.5 | 348.3
2475.1 | 2281.1 | -6.5 | 0 | 0 | 228.4 | 226.8 | 214.2 | 204.4 | 238.4 | 38.5 | 19.1 | 55.4 | 3.8 | 223 | 7.7 | 49.5 | 83.4 | 46.4 | 78.7 | 41 | 64.1 | 72.9 | 43.3 | 79.7 | 69.6 | 354.9 | 341.1 | 334.2 | 350.8 | 292.4 | 214.9 | 301.6 | 260.9 | 367.2 | 348.1
2476.1 | 2282.1 | -6.5 | 0 | 0 | 228.4 | 226.8 | 214 | 204.2 | 238.2 | 38.5 | 19.1 | 55.3 | 4.3 | 251.5 | 8.6 | 49.7 | 83.3 | 46.4 | 78.4 | 41 | 64.3 | 73.2 | 43.1 | 79.9 | 69.7 | 354.8 | 340.9 | 334 | 350.6 | 292.2 | 214.8 | 301.4 | 260.7 | 366.9 | 347.8
2477.1 | 2283.1 | -6.4 | 0 | 0 | 228.2 | 226.3 | 214 | 204 | 238.4 | 38.5 | 19.1 | 55.3 | 3.9 | 225.6 | 8.7 | 49.8 | 83.3 | 46.4 | 78 | 40.9 | 64.2 | 73.2 | 42.8 | 80 | 69.8 | 354.7 | 340.7 | 333.8 | 350.4 | 292 | 214.6 | 301.2 | 260.5 | 366.6 | 347.6
2478.1 | 2284.1 | -6.4 | 0 | 0 | 228.1 | 225.9 | 213.8 | 203.8 | 238.1 | 38.5 | 19.1 | 55.2 | 4.6 | 230.7 | 8.8 | 49.7 | 83.5 | 46.3 | 77.7 | 40.9 | 64.3 | 73.5 | 42.6 | 79.8 | 69.9 | 354.6 | 340.5 | 333.6 | 350.2 | 291.8 | 214.5 | 301 | 260.2 | 366.2 | 347.4
2479.1 | 2285.1 | -6.5 | 0 | 0 | 227.9 | 225.8 | 213.6 | 203.5 | 237.7 | 38.5 | 19.1 | 55.1 | 4.4 | 238.2 | 7.9 | 49.4 | 83.7 | 46.3 | 77.3 | 40.8 | 64.4 | 73.9 | 42.4 | 79.7 | 70.1 | 354.5 | 340.3 | 333.4 | 350 | 291.6 | 214.3 | 300.8 | 260.1 | 365.9 | 347.2
2480.1 | 2286.1 | -6.6 | 0 | 0 | 227.6 | 225.5 | 213.3 | 203.4 | 237.6 | 38.5 | 19.1 | 55.1 | 4.5 | 223.1 | 8 | 49.5 | 83.9 | 46.2 | 76.9 | 40.8 | 64.6 | 73.3 | 42.3 | 79.9 | 70.2 | 354.4 | 340.1 | 333.1 | 349.8 | 291.4 | 214.1 | 300.5 | 259.9 | 365.6 | 347
2481.1 | 2287.1 | -6.4 | 0 | 0 | 227.5 | 225.4 | 213.2 | 203.4 | 237.6 | 38.5 | 19.1 | 55 | 4.9 | 233.6 | 9.6 | 49.7 | 84.1 | 46.2 | 76.6 | 40.7 | 65.1 | 72.9 | 42.4 | 80.3 | 70.2 | 354.3 | 340 | 332.9 | 349.6 | 291.2 | 214 | 300.3 | 259.6 | 365.3 | 346.8
2482.1 | 2288.1 | -5.8 | 0 | 0 | 227.3 | 225.5 | 213.1 | 203.3 | 237.8 | 38.5 | 19.1 | 54.9 | 4.5 | 250.7 | 10.7 | 49.8 | 84.3 | 46.1 | 76.2 | 40.7 | 65.4 | 73.2 | 42.5 | 80.7 | 70 | 354.2 | 339.8 | 332.7 | 349.5 | 291 | 213.8 | 300.1 | 259.4 | 365 | 346.5
2483.1 | 2289.1 | -5.9 | 0 | 0 | 226.9 | 225.2 | 213 | 203.2 | 237.9 | 38.5 | 19.1 | 55 | 4.8 | 239.9 | 11.6 | 49.8 | 84.4 | 46.1 | 75.9 | 40.6 | 65.5 | 73.6 | 42.4 | 81 | 70 | 354.1 | 339.6 | 332.5 | 349.3 | 290.9 | 213.6 | 299.9 | 259.2 | 364.7 | 346.3
2484.1 | 2290.1 | -6.3 | 0 | 0 | 226.7 | 224.8 | 212.9 | 203.2 | 238.1 | 38.5 | 19.2 | 54.9 | 4.7 | 236.9 | 12.4 | 49.6 | 84.4 | 46 | 75.6 | 40.5 | 65.7 | 73.2 | 42.2 | 81.2 | 70.1 | 354 | 339.4 | 332.3 | 349.1 | 290.7 | 213.5 | 299.7 | 259 | 364.4 | 346.1
2485.1 | 2291.1 | -6.3 | 0 | 0 | 226.6 | 224.7 | 212.7 | 203 | 238.3 | 38.4 | 19.2 | 54.9 | 4.8 | 246.3 | 11.9 | 49.5 | 84.5 | 45.9 | 75.3 | 40.4 | 65.9 | 73 | 42.5 | 81.4 | 70.1 | 353.9 | 339.2 | 332.1 | 348.9 | 290.5 | 213.3 | 299.4 | 258.8 | 364.1 | 345.9
2486.1 | 2292.1 | -6.4 | 0 | 0 | 226.3 | 224.6 | 212.6 | 202.9 | 238.3 | 38.4 | 19.2 | 54.8 | 4.3 | 257.6 | 10.9 | 49.7 | 84.5 | 45.9 | 74.9 | 40.3 | 66.3 | 72.7 | 43.2 | 81.6 | 70 | 353.8 | 339 | 331.9 | 348.7 | 290.3 | 213.1 | 299.2 | 258.6 | 363.8 | 345.7
2487.1 | 2293.1 | -6.3 | 0 | 0 | 226.1 | 224.7 | 212.3 | 202.6 | 238.2 | 38.4 | 19.2 | 54.8 | 4.2 | 248.6 | 9.3 | 49.5 | 84.6 | 45.8 | 74.6 | 40.2 | 66.4 | 72.3 | 43 | 81.6 | 70.1 | 353.7 | 338.8 | 331.7 | 348.5 | 290.1 | 213 | 299 | 258.4 | 363.5 | 345.5
2488.1 | 2294.1 | -6.4 | 0 | 0 | 225.8 | 224.4 | 212 | 202.4 | 238.1 | 38.4 | 19.2 | 54.8 | 3.9 | 230.3 | 8.2 | 49.3 | 84.7 | 45.8 | 74.3 | 40.1 | 66.3 | 72.8 | 43.3 | 81.6 | 70.1 | 353.6 | 338.6 | 331.5 | 348.3 | 290 | 212.8 | 298.8 | 258.2 | 363.2 | 345.2
2489.1 | 2295.1 | -6.3 | 0 | 0 | 225.4 | 224 | 211.8 | 202.3 | 238.1 | 38.3 | 19.2 | 54.8 | 3.9 | 214.8 | 7 | 48.9 | 84.9 | 45.6 | 74 | 40 | 66.3 | 73.3 | 43 | 81.6 | 70 | 353.5 | 338.5 | 331.3 | 348.1 | 289.7 | 212.7 | 298.5 | 258 | 362.9 | 345
2490.1 | 2296.1 | -6.4 | 0 | 0 | 224.9 | 223.8 | 211.7 | 202.1 | 238 | 38.3 | 19.2 | 54.7 | 4 | 228.3 | 7.1 | 49.1 | 85.1 | 45.6 | 73.6 | 40 | 66.5 | 73.4 | 44.5 | 81.6 | 70 | 353.4 | 338.3 | 331 | 348 | 289.6 | 212.5 | 298.3 | 257.8 | 362.6 | 344.8
2491.1 | 2297.1 | -6.5 | 0 | 0 | 224.7 | 223.7 | 211.6 | 202.1 | 237.6 | 38.3 | 19.2 | 54.6 | 3.8 | 227.1 | 6.1 | 49.1 | 85.2 | 45.6 | 73.4 | 39.9 | 66.4 | 73 | 45.6 | 81.7 | 70 | 353.3 | 338.1 | 330.8 | 347.8 | 289.4 | 212.3 | 298.1 | 257.6 | 362.3 | 344.6
2492.1 | 2298.1 | -6.5 | 0 | 0 | 224.8 | 223.6 | 211.4 | 202 | 237 | 38.3 | 19.2 | 54.6 | 5.6 | 246.7 | 5.5 | 49.1 | 85.1 | 45.6 | 73.1 | 39.9 | 66.3 | 72.8 | 45.1 | 81.9 | 70 | 353.2 | 337.9 | 330.6 | 347.6 | 289.2 | 212.2 | 297.9 | 257.4 | 362 | 344.4
2493.1 | 2299.1 | -6.3 | 0 | 0 | 224.9 | 223.5 | 211.2 | 201.9 | 236.5 | 38.2 | 19.2 | 54.5 | 6.7 | 239.9 | 6 | 49 | 85.1 | 45.6 | 72.7 | 39.8 | 66.1 | 72.7 | 44.4 | 81.9 | 69.9 | 353.1 | 337.7 | 330.4 | 347.4 | 289 | 212 | 297.6 | 257.2 | 361.6 | 344.2
2494.1 | 2300.1 | -6.4 | 0 | 0 | 225 | 223.5 | 211.1 | 201.7 | 236 | 38.2 | 19.2 | 54.4 | 6 | 241.5 | 7.5 | 49 | 85.2 | 45.5 | 72.4 | 39.7 | 66 | 73.2 | 43.6 | 82 | 69.9 | 353 | 337.6 | 330.2 | 347.2 | 288.8 | 211.8 | 297.4 | 257 | 361.3 | 344
2495.1 | 2301.1 | -6.5 | 0 | 0 | 225 | 223.6 | 210.9 | 201.6 | 235.4 | 38.1 | 19.2 | 54.4 | 4.6 | 247.9 | 7.5 | 48.8 | 85.4 | 45.4 | 72.2 | 39.7 | 65.9 | 73.7 | 43.2 | 81.9 | 69.9 | 352.9 | 337.4 | 330 | 347 | 288.7 | 211.6 | 297.1 | 256.8 | 361.1 | 343.7
2496.1 | 2302.1 | -6.5 | 0 | 0 | 224.8 | 223.5 | 210.6 | 201.5 | 235 | 38.1 | 19.2 | 54.4 | 4.6 | 249.3 | 9.2 | 48.7 | 85.4 | 45.3 | 71.9 | 39.9 | 65.8 | 73.8 | 43.8 | 81.7 | 69.8 | 352.8 | 337.2 | 329.8 | 346.9 | 288.5 | 211.4 | 296.9 | 256.6 | 360.7 | 343.5
2497.1 | 2303.1 | -6.6 | 0 | 0 | 224.7 | 223.2 | 210.6 | 201.4 | 235 | 38.1 | 19.2 | 54.3 | 3.9 | 223.1 | 11.1 | 48.5 | 85.4 | 45.4 | 71.6 | 40 | 65.9 | 73.6 | 45.6 | 81.5 | 69.7 | 352.7 | 337 | 329.6 | 346.7 | 288.4 | 211.2 | 296.7 | 256.4 | 360.5 | 343.3
2498.1 | 2304.1 | -6.6 | 0 | 0 | 224.7 | 222.8 | 210.6 | 201.2 | 235.1 | 38.1 | 19.2 | 54.3 | 4.9 | 213 | 8 | 48.6 | 85.4 | 45.4 | 71.4 | 39.9 | 65.9 | 72.8 | 45.2 | 81.3 | 69.6 | 352.6 | 336.8 | 329.4 | 346.5 | 288.2 | 211.1 | 296.5 | 256.3 | 360.2 | 343.1
2499.1 | 2305.1 | -6.4 | 0 | 0 | 224.5 | 222.4 | 210.5 | 201.1 | 235.3 | 38 | 19.2 | 54.2 | 5.5 | 234.6 | 7.9 | 48.5 | 85.5 | 45.3 | 71.1 | 39.8 | 65.7 | 72.4 | 44.5 | 80.9 | 69.6 | 352.5 | 336.7 | 329.2 | 346.3 | 288.1 | 210.9 | 296.3 | 256 | 359.9 | 342.9
2500.1 | 2306.1 | -6.2 | 0 | 0 | 224.4 | 222 | 210.5 | 201.1 | 235.4 | 38 | 19.2 | 54.1 | 4.7 | 216.1 | 9.7 | 48.3 | 85.5 | 45.3 | 70.9 | 39.7 | 65.6 | 72.3 | 44.2 | 80.5 | 69.4 | 352.4 | 336.5 | 329 | 346.1 | 287.9 | 210.7 | 296 | 255.8 | 359.6 | 342.6
2501.1 | 2307.1 | -6.2 | 0 | 0 | 224.5 | 222 | 210.3 | 201 | 235.5 | 38 | 19.2 | 54 | 4.9 | 245.2 | 9.8 | 48.2 | 85.4 | 45.3 | 70.6 | 39.7 | 65.4 | 72.8 | 44.2 | 80.1 | 69.4 | 352.3 | 336.3 | 328.8 | 345.9 | 287.7 | 210.6 | 295.8 | 255.7 | 359.3 | 342.4
2502.1 | 2308.1 | -6.4 | 0 | 0 | 224.6 | 222.1 | 210.2 | 200.9 | 235.2 | 38 | 19.2 | 54 | 4.7 | 239.7 | 8.8 | 48.3 | 85.4 | 45.4 | 70.3 | 39.6 | 65.3 | 73.2 | 44.4 | 79.7 | 69.4 | 352.2 | 336.1 | 328.6 | 345.7 | 287.6 | 210.4 | 295.7 | 255.5 | 359 | 342.2
2503.1 | 2309.1 | -6.4 | 0 | 0 | 224.6 | 222 | 210.1 | 200.8 | 234.8 | 38 | 19.2 | 54 | 4.5 | 223.7 | 8.2 | 48.3 | 85.4 | 45.4 | 70.1 | 39.6 | 65.1 | 73.4 | 45.8 | 79.6 | 69.5 | 352.1 | 336 | 328.4 | 345.5 | 287.4 | 210.2 | 295.4 | 255.3 | 358.7 | 342
2504.1 | 2310.1 | -6.3 | 0 | 0 | 224.5 | 221.2 | 209.9 | 200.6 | 233.9 | 38 | 19.2 | 53.9 | 4.3 | 207.1 | 9 | 48.2 | 85.3 | 45.4 | 69.8 | 39.6 | 65.1 | 73.4 | 46.5 | 79.7 | 69.7 | 352 | 335.8 | 328.2 | 345.4 | 287.2 | 210 | 295.2 | 255 | 358.4 | 341.8
2505.1 | 2311.1 | -6.4 | 0 | 0 | 224.1 | 220.6 | 209.6 | 200.4 | 233.5 | 38 | 19.2 | 53.8 | 4.9 | 233.3 | 8.7 | 48.3 | 85.2 | 45.4 | 69.5 | 39.6 | 65.4 | 73.3 | 46.3 | 80.2 | 69.8 | 351.9 | 335.6 | 328 | 345.2 | 287.1 | 209.9 | 295 | 254.9 | 358.1 | 341.6
2506.1 | 2312.1 | -6.4 | 0 | 0 | 223.7 | 220.4 | 209.4 | 200.3 | 233.2 | 38 | 19.2 | 53.8 | 4 | 214.2 | 8.8 | 48.4 | 84.6 | 45.4 | 69.3 | 39.6 | 65.5 | 73.7 | 46 | 80.8 | 69.9 | 351.8 | 335.5 | 327.8 | 345 | 286.9 | 209.7 | 294.8 | 254.7 | 357.8 | 341.4
2507.1 | 2313.1 | -6.4 | 0 | 0 | 223.5 | 220.4 | 209.4 | 200.1 | 233.3 | 38 | 19.2 | 53.8 | 4.5 | 250.8 | 7.6 | 48.3 | 84.4 | 45.4 | 69 | 39.5 | 65.7 | 73.7 | 46 | 81.3 | 69.9 | 351.7 | 335.3 | 327.6 | 344.8 | 286.8 | 209.6 | 294.6 | 254.5 | 357.5 | 341.2
2508.1 | 2314.1 | -6.3 | 0 | 0 | 223.2 | 220.2 | 209.2 | 200 | 233.5 | 38 | 19.2 | 53.7 | 4.6 | 235.3 | 7 | 48.3 | 84.5 | 45.4 | 68.8 | 39.5 | 66.1 | 73.5 | 45.3 | 81.5 | 69.8 | 351.6 | 335.2 | 327.4 | 344.6 | 286.7 | 209.5 | 294.4 | 254.3 | 357.2 | 340.9
2509.1 | 2315.1 | -6.5 | 0 | 0 | 222.9 | 220.2 | 209.1 | 199.8 | 233.7 | 38 | 19.3 | 53.5 | 5 | 225.5 | 6.7 | 48.3 | 84.6 | 45.4 | 68.5 | 39.5 | 65.8 | 73.1 | 45.5 | 81.7 | 69.8 | 351.5 | 335 | 327.2 | 344.4 | 286.5 | 209.3 | 294.1 | 254.1 | 356.9 | 340.7
2510.1 | 2316.1 | -6.3 | 0 | 0 | 222.7 | 220.2 | 209 | 199.7 | 233.8 | 38 | 19.3 | 53.5 | 4.7 | 259.5 | 7.5 | 48.2 | 84.5 | 45.4 | 68.2 | 39.4 | 65.8 | 73 | 45.3 | 81.8 | 69.7 | 351.4 | 334.8 | 327 | 344.2 | 286.3 | 209.2 | 293.9 | 253.9 | 356.6 | 340.5
2511.1 | 2317.1 | -6.2 | 0 | 0 | 222.5 | 220.2 | 208.9 | 199.8 | 233.9 | 38 | 19.3 | 53.5 | 5 | 249.1 | 11.4 | 48.2 | 84.5 | 45.4 | 68 | 39.4 | 65.9 | 72.8 | 44.6 | 81.7 | 69.8 | 351.3 | 334.7 | 326.8 | 344 | 286.1 | 209 | 293.7 | 253.7 | 356.3 | 340.3
2512.1 | 2318.1 | -6.2 | 0 | 0 | 222.4 | 220.2 | 208.7 | 199.7 | 233.9 | 38 | 19.3 | 53.4 | 4.6 | 259 | 11.4 | 48.1 | 84.4 | 45.3 | 67.7 | 39.4 | 66 | 73 | 44.8 | 81.7 | 69.8 | 351.2 | 334.5 | 326.6 | 343.8 | 285.9 | 208.9 | 293.5 | 253.5 | 356.1 | 340.1
2513.1 | 2319.1 | -6.2 | 0 | 0 | 222.4 | 220 | 208.6 | 199.5 | 234 | 38 | 19.3 | 53.4 | 4.7 | 244.7 | 9.6 | 48.1 | 84.5 | 45.2 | 67.5 | 39.3 | 66.2 | 72.8 | 45 | 81.6 | 69.8 | 351.1 | 334.4 | 326.4 | 343.6 | 285.8 | 208.7 | 293.3 | 253.3 | 355.8 | 339.9
2514.1 | 2320.1 | -6.2 | 0 | 0 | 222.2 | 220 | 208.6 | 199.3 | 233.9 | 38 | 19.3 | 53.3 | 4.9 | 237.7 | 9.9 | 48.1 | 84.3 | 45.3 | 67.3 | 39.3 | 66 | 73 | 44.4 | 81.5 | 69.8 | 351 | 334.2 | 326.2 | 343.5 | 285.6 | 208.5 | 293.1 | 253.1 | 355.5 | 339.7
2515.1 | 2321.1 | -6.3 | 0 | 0 | 222 | 219.9 | 208.3 | 199.1 | 233.2 | 38 | 19.3 | 53.3 | 4.7 | 248 | 9.9 | 48.2 | 84.1 | 45.2 | 67 | 39.4 | 66 | 73.6 | 43.8 | 81.4 | 69.8 | 350.9 | 334 | 326 | 343.3 | 285.5 | 208.4 | 292.9 | 252.9 | 355.2 | 339.5
2516.1 | 2322.1 | -6.5 | 0 | 0 | 221.9 | 219.6 | 208.2 | 199 | 232.5 | 37.9 | 19.3 | 53.2 | 4.4 | 233.4 | 9.4 | 48.1 | 84 | 45.3 | 66.9 | 39.4 | 66.3 | 73.7 | 43.6 | 81.4 | 69.8 | 350.8 | 333.9 | 325.8 | 343.1 | 285.3 | 208.2 | 292.6 | 252.7 | 354.9 | 339.3
2517.1 | 2323.1 | -6.2 | 0 | 0 | 221.4 | 219.2 | 208.1 | 198.8 | 231.9 | 37.9 | 19.3 | 53.2 | 4.8 | 251.9 | 9.7 | 48 | 83.8 | 45.3 | 66.7 | 39.4 | 66.2 | 73.6 | 43.4 | 81.4 | 69.8 | 350.7 | 333.7 | 325.6 | 342.9 | 285.1 | 208 | 292.4 | 252.5 | 354.6 | 339
2518.1 | 2324.1 | -6.2 | 0 | 0 | 221 | 219 | 208 | 198.7 | 231.2 | 37.9 | 19.3 | 53.1 | 4.4 | 247.3 | 11.2 | 48 | 83.8 | 45.2 | 66.5 | 39.4 | 65.8 | 73.9 | 43.5 | 81.4 | 69.8 | 350.6 | 333.6 | 325.4 | 342.7 | 284.9 | 207.9 | 292.2 | 252.3 | 354.3 | 338.8
2519.1 | 2325.1 | -6.4 | 0 | 0 | 220.8 | 218.7 | 207.8 | 198.6 | 230.5 | 37.9 | 19.3 | 53 | 4 | 263.8 | 10.2 | 47.9 | 83.3 | 45.2 | 66.3 | 39.4 | 65.8 | 74.1 | 43.9 | 81.3 | 69.8 | 350.5 | 333.4 | 325.2 | 342.5 | 284.7 | 207.7 | 292 | 252.1 | 354 | 338.6
2520.1 | 2326.1 | -6.4 | 0 | 0 | 220.7 | 218.3 | 207.6 | 198.4 | 230.1 | 37.9 | 19.3 | 53 | 4 | 269.4 | 8 | 47.9 | 82.7 | 45.1 | 66.1 | 39.4 | 65.8 | 73.8 | 44.3 | 81.3 | 69.8 | 350.4 | 333.2 | 325 | 342.3 | 284.6 | 207.6 | 291.8 | 252 | 353.8 | 338.4
2521.1 | 2327.1 | -6.5 | 0 | 0 | 220.5 | 218.1 | 207.5 | 198.3 | 229.6 | 37.7 | 19.3 | 52.9 | 4 | 237.2 | 7.4 | 47.7 | 82.4 | 45.1 | 65.9 | 39.5 | 65.7 | 74.1 | 43.9 | 81.4 | 69.8 | 350.3 | 333.1 | 324.8 | 342.1 | 284.4 | 207.4 | 291.5 | 251.8 | 353.5 | 338.2
2522.1 | 2328.1 | -6.3 | 0 | 0 | 220.3 | 217.9 | 207.4 | 198.3 | 229.1 | 37.7 | 19.3 | 52.8 | 4.1 | 272.8 | 10 | 47.6 | 82 | 45.1 | 65.7 | 39.5 | 65.5 | 74.4 | 44 | 81.5 | 69.8 | 350.2 | 332.9 | 324.6 | 341.9 | 284.2 | 207.3 | 291.3 | 251.6 | 353.2 | 338
2523.1 | 2329.1 | -6.1 | 0 | 0 | 220.4 | 217.7 | 207.2 | 198 | 228.6 | 37.7 | 19.3 | 52.8 | 4.4 | 269 | 13.2 | 47.6 | 81.8 | 45.1 | 65.5 | 39.5 | 65.5 | 74.4 | 44.5 | 81.6 | 69.9 | 350.1 | 332.7 | 324.5 | 341.7 | 284 | 207.2 | 291.2 | 251.4 | 352.9 | 337.8
2524.1 | 2330.1 | -6.3 | 0 | 0 | 220.3 | 217.4 | 207.1 | 197.8 | 228 | 37.7 | 19.3 | 52.8 | 3.8 | 270.2 | 14.6 | 47.5 | 81.7 | 45 | 65.3 | 39.5 | 65.3 | 74.5 | 44.9 | 81.8 | 69.9 | 350 | 332.6 | 324.3 | 341.6 | 283.9 | 207 | 290.9 | 251.2 | 352.6 | 337.6
2525.1 | 2331.1 | -6.4 | 0 | 0 | 220.3 | 217 | 207 | 197.7 | 227.5 | 37.6 | 19.3 | 52.8 | 4.5 | 261.7 | 14.5 | 47.5 | 81.6 | 45.1 | 65.1 | 39.5 | 65.3 | 74.6 | 44.7 | 81.9 | 69.9 | 349.9 | 332.4 | 324 | 341.4 | 283.7 | 206.9 | 290.8 | 251 | 352.3 | 337.3
2526.1 | 2332.1 | -6.4 | 0 | 0 | 220.2 | 216.6 | 206.9 | 197.7 | 227.5 | 37.6 | 19.3 | 52.7 | 4.6 | 266.3 | 13.7 | 47.3 | 81.6 | 45 | 64.9 | 39.4 | 65.5 | 74.6 | 44.6 | 81.9 | 70 | 349.9 | 332.2 | 323.9 | 341.2 | 283.6 | 206.8 | 290.6 | 250.9 | 352 | 337.2
2527.1 | 2333.1 | -6.3 | 0 | 0 | 220 | 216.1 | 206.8 | 197.6 | 227.6 | 37.5 | 19.3 | 52.7 | 4.5 | 268.8 | 12.7 | 47.2 | 81.6 | 45 | 64.7 | 39.3 | 65.8 | 74.6 | 44.2 | 82 | 70 | 349.8 | 332 | 323.7 | 341 | 283.4 | 206.7 | 290.4 | 250.7 | 351.8 | 336.9
2528.1 | 2334.1 | -6.3 | 0 | 0 | 219.8 | 215.8 | 206.7 | 197.5 | 227.8 | 37.4 | 19.3 | 52.7 | 5 | 263.3 | 12.4 | 47.2 | 81.3 | 45.1 | 64.5 | 39.3 | 66 | 74.4 | 44.2 | 82 | 70 | 349.7 | 331.9 | 323.5 | 340.8 | 283.3 | 206.5 | 290.1 | 250.5 | 351.5 | 336.7
2529.1 | 2335.1 | -6.4 | 0 | 0 | 219.6 | 215.6 | 206.5 | 197.4 | 227.7 | 37.3 | 19.3 | 52.7 | 5 | 264.9 | 13.6 | 47.1 | 81.2 | 45.1 | 64.3 | 39.3 | 66.1 | 73.9 | 44.2 | 81.9 | 70 | 349.6 | 331.7 | 323.3 | 340.6 | 283.1 | 206.4 | 289.9 | 250.3 | 351.2 | 336.5
2530.1 | 2336.1 | -6.6 | 0 | 0 | 219.4 | 215.7 | 206.3 | 197.2 | 227.7 | 37.2 | 19.3 | 52.8 | 5.1 | 267.5 | 13.7 | 47 | 81.3 | 45.1 | 64.1 | 39.2 | 66.1 | 74.3 | 44.7 | 81.9 | 69.9 | 349.5 | 331.5 | 323.1 | 340.4 | 282.9 | 206.3 | 289.7 | 250.1 | 350.9 | 336.3
2531.1 | 2337.1 | -6.4 | 0 | 0 | 219.2 | 215.8 | 206.2 | 197.1 | 227.6 | 37.2 | 19.3 | 52.8 | 4.9 | 262.2 | 14 | 46.9 | 81.5 | 45.1 | 63.9 | 39.1 | 66.1 | 74.6 | 44.7 | 82 | 69.8 | 349.4 | 331.4 | 322.9 | 340.2 | 282.8 | 206.2 | 289.5 | 249.9 | 350.6 | 336.1
2532.1 | 2338.1 | -6 | 0 | 0 | 218.8 | 215.7 | 206.1 | 197.1 | 227.6 | 37.1 | 19.3 | 52.7 | 4.5 | 250.9 | 14.2 | 46.8 | 81.7 | 45.2 | 63.7 | 39.1 | 66.2 | 74.4 | 44.4 | 82 | 69.7 | 349.3 | 331.2 | 322.7 | 340 | 282.6 | 206 | 289.3 | 249.7 | 350.4 | 335.9
2533.1 | 2339.1 | -5.7 | 0 | 0 | 218.7 | 215.6 | 206 | 197 | 227.5 | 37.1 | 19.3 | 52.8 | 6.1 | 255.3 | 13.3 | 46.8 | 81.9 | 45.2 | 63.5 | 39.1 | 66.2 | 74 | 44.6 | 81.9 | 69.7 | 349.2 | 331 | 322.5 | 339.8 | 282.4 | 205.9 | 289.2 | 249.6 | 350.1 | 335.7
2534.1 | 2340.1 | -6 | 0 | 0 | 218.6 | 215.4 | 206 | 197 | 226.7 | 37 | 19.3 | 52.7 | 6.9 | 261.3 | 14.5 | 46.9 | 82 | 45.2 | 63.3 | 39.1 | 66.1 | 73.7 | 44.3 | 81.9 | 69.6 | 349.1 | 330.8 | 322.3 | 339.7 | 282.3 | 205.8 | 288.9 | 249.3 | 349.8 | 335.5
2535.1 | 2341.1 | -6.2 | 0 | 0 | 218.4 | 215.1 | 205.9 | 196.9 | 225.9 | 36.9 | 19.3 | 52.7 | 6.1 | 256 | 14.1 | 47 | 82.1 | 45.3 | 63.1 | 39 | 65.8 | 74 | 44.3 | 81.8 | 69.5 | 349 | 330.7 | 322.1 | 339.5 | 282.1 | 205.7 | 288.7 | 249.2 | 349.5 | 335.3
2536.1 | 2342.1 | -6.1 | 0 | 0 | 218.4 | 214.8 | 205.8 | 196.7 | 225.7 | 36.8 | 19.3 | 52.7 | 5.7 | 251.7 | 15.1 | 46.9 | 82.2 | 45.3 | 63 | 39 | 65.3 | 74.4 | 45.2 | 81.8 | 69.5 | 348.9 | 330.5 | 321.9 | 339.3 | 281.9 | 205.5 | 288.5 | 249 | 349.2 | 335
2537.1 | 2343.1 | -6.2 | 0 | 0 | 218.3 | 214.6 | 205.7 | 196.4 | 225.6 | 36.7 | 19.3 | 52.7 | 4.9 | 249.1 | 18.5 | 46.9 | 82.4 | 45.2 | 62.8 | 38.9 | 65.2 | 74.7 | 46.1 | 81.8 | 69.4 | 348.8 | 330.3 | 321.8 | 339.1 | 281.7 | 205.3 | 288.2 | 248.8 | 349 | 334.9
2538.1 | 2344.1 | -6.2 | 0 | 0 | 218.4 | 214.4 | 205.6 | 196.2 | 225.6 | 36.6 | 19.4 | 52.8 | 3.7 | 241.5 | 19.5 | 46.9 | 82.4 | 45.2 | 62.5 | 38.8 | 65.2 | 74.9 | 45.6 | 81.7 | 69.4 | 348.7 | 330.1 | 321.6 | 338.9 | 281.5 | 205.2 | 288 | 248.6 | 348.7 | 334.6
2539.1 | 2345.1 | -6.3 | 0 | 0 | 218.1 | 214.5 | 205.5 | 196.1 | 225.6 | 36.6 | 19.4 | 52.8 | 3.3 | 257.9 | 17.7 | 46.8 | 82.6 | 45.1 | 62.4 | 38.7 | 64.8 | 75.1 | 45.2 | 81.6 | 69.4 | 348.6 | 330 | 321.4 | 338.7 | 281.4 | 205.1 | 287.8 | 248.4 | 348.4 | 334.4
2540.1 | 2346.1 | -6.5 | 0 | 0 | 217.8 | 214.6 | 205.3 | 195.9 | 225.3 | 36.6 | 19.4 | 52.9 | 4.1 | 257.9 | 15.3 | 46.7 | 82.7 | 45.1 | 62.2 | 38.7 | 64.4 | 75.2 | 45.5 | 81.5 | 69.4 | 348.5 | 329.8 | 321.2 | 338.5 | 281.2 | 205 | 287.7 | 248.3 | 348.1 | 334.2
2541.1 | 2347.1 | -6.3 | 0 | 0 | 217.4 | 214.6 | 205.1 | 195.7 | 225.1 | 36.5 | 19.4 | 52.9 | 5 | 243 | 12.8 | 46.7 | 82.8 | 45.1 | 62 | 38.6 | 62.9 | 75.3 | 45.2 | 81.4 | 69.3 | 348.4 | 329.6 | 321 | 338.3 | 281.1 | 204.9 | 287.5 | 248.1 | 347.9 | 334
2542.1 | 2348.1 | -5.9 | 0 | 0 | 216.9 | 214.3 | 204.8 | 195.7 | 225.1 | 36.5 | 19.4 | 52.8 | 5.5 | 264.5 | 13.5 | 46.7 | 82.9 | 45.1 | 61.8 | 38.6 | 62.3 | 75.5 | 45.2 | 81 | 69.4 | 348.3 | 329.5 | 320.8 | 338.1 | 280.9 | 204.7 | 287.3 | 247.9 | 347.6 | 333.8
2543.1 | 2349.1 | -5.9 | 0 | 0 | 216.5 | 214.3 | 204.7 | 195.7 | 225.2 | 36.4 | 19.4 | 52.8 | 5.4 | 266.7 | 14.5 | 46.7 | 83 | 45.1 | 61.6 | 38.5 | 62.2 | 75.4 | 45.6 | 80.5 | 69 | 348.2 | 329.3 | 320.6 | 338 | 280.7 | 204.6 | 287.1 | 247.7 | 347.3 | 333.6
2544.1 | 2350.1 | -6 | 0 | 0 | 216.3 | 214.1 | 204.6 | 195.7 | 225.3 | 36.5 | 19.4 | 52.8 | 5.1 | 253.9 | 12.6 | 46.6 | 83.1 | 45 | 61.5 | 38.5 | 61.7 | 75.3 | 46.4 | 80.2 | 68.9 | 348.1 | 329.1 | 320.4 | 337.8 | 280.5 | 204.4 | 286.8 | 247.5 | 347.1 | 333.4
2545.1 | 2351.1 | -6.3 | 0 | 0 | 216 | 213.9 | 204.5 | 195.6 | 225.1 | 36.5 | 19.4 | 52.7 | 4.6 | 256.6 | 14.6 | 46.6 | 83.2 | 44.9 | 61.3 | 38.4 | 60.9 | 75.3 | 46.4 | 80.4 | 68.7 | 348 | 328.9 | 320.3 | 337.6 | 280.4 | 204.3 | 286.7 | 247.4 | 346.8 | 333.2
2546.1 | 2352.1 | -6.4 | 0 | 0 | 215.8 | 213.6 | 204.4 | 195.5 | 224.9 | 36.5 | 19.4 | 52.7 | 4.3 | 242 | 16.2 | 46.6 | 83.2 | 44.9 | 61.1 | 38.4 | 60.9 | 74.9 | 46.1 | 80.6 | 68.7 | 347.9 | 328.8 | 320.1 | 337.4 | 280.2 | 204.2 | 286.5 | 247.2 | 346.5 | 333
2547.1 | 2353.1 | -6.4 | 0 | 0 | 215.6 | 213.2 | 204.2 | 195.3 | 224.7 | 36.4 | 19.4 | 52.6 | 4.5 | 252 | 13.4 | 46.4 | 83.3 | 44.8 | 61 | 38.2 | 62 | 75 | 45.7 | 80.7 | 68.5 | 347.7 | 328.6 | 319.9 | 337.2 | 280.1 | 204.1 | 286.3 | 247 | 346.3 | 332.8
2548.1 | 2354.1 | -6.3 | 0 | 0 | 215.5 | 213 | 204 | 195.3 | 224.4 | 36.3 | 19.4 | 52.6 | 4.7 | 246.4 | 11.3 | 46.2 | 83.4 | 44.7 | 60.8 | 38.1 | 63.1 | 75.4 | 45.5 | 80.9 | 68.5 | 347.6 | 328.4 | 319.7 | 337 | 279.9 | 204 | 286.1 | 246.8 | 346 | 332.6
2549.1 | 2355.1 | -6.3 | 0 | 0 | 215.6 | 212.9 | 204 | 195.2 | 224 | 36.3 | 19.4 | 52.5 | 4.9 | 260.1 | 11.2 | 46.2 | 83.5 | 44.7 | 60.6 | 38 | 63.8 | 75.3 | 45.4 | 81.2 | 68.6 | 347.6 | 328.2 | 319.5 | 336.8 | 279.7 | 203.9 | 285.9 | 246.6 | 345.7 | 332.4
2550.1 | 2356.1 | -6.2 | 0 | 0 | 215.4 | 212.5 | 203.8 | 194.9 | 223.8 | 36.4 | 19.4 | 52.5 | 4.8 | 253.8 | 12.3 | 46.1 | 83.6 | 44.7 | 60.4 | 38 | 64.3 | 75.2 | 45.3 | 81.3 | 68.6 | 347.5 | 328 | 319.3 | 336.7 | 279.5 | 203.8 | 285.7 | 246.4 | 345.5 | 332.2
2551.1 | 2357.1 | -6.4 | 0 | 0 | 215.1 | 212 | 203.5 | 194.6 | 223.6 | 36.4 | 19.4 | 52.5 | 4.5 | 244.7 | 12.5 | 45.9 | 83.6 | 44.6 | 60.3 | 37.9 | 64.3 | 75.3 | 45 | 81.4 | 68.5 | 347.4 | 327.9 | 319.1 | 336.5 | 279.4 | 203.7 | 285.5 | 246.2 | 345.2 | 332
2552.1 | 2358.1 | -6.4 | 0 | 0 | 214.8 | 211.6 | 203.3 | 194.4 | 222.3 | 36.5 | 19.4 | 52.5 | 4.4 | 259.5 | 10.2 | 45.9 | 83.6 | 44.6 | 60.1 | 37.9 | 64.6 | 75.5 | 45.3 | 81.5 | 68.4 | 347.3 | 327.7 | 318.9 | 336.3 | 279.2 | 203.6 | 285.4 | 246.1 | 344.9 | 331.8
2553.1 | 2359.1 | -6.5 | 0 | 0 | 215 | 211.6 | 203.1 | 194.3 | 221.3 | 36.5 | 19.4 | 52.5 | 5.2 | 230.5 | 9.6 | 46 | 83.7 | 44.6 | 60 | 37.9 | 64.8 | 74.9 | 45.4 | 81.5 | 68.3 | 347.2 | 327.5 | 318.7 | 336.1 | 279 | 203.4 | 285.1 | 245.9 | 344.6 | 331.6
2554.1 | 2360.1 | -6.5 | 0 | 0 | 215.3 | 211.2 | 202.9 | 194.2 | 220.8 | 36.4 | 19.4 | 52.4 | 5.3 | 210.2 | 10 | 46.1 | 83.6 | 44.5 | 59.9 | 37.9 | 65.1 | 73 | 44.9 | 81.5 | 68.3 | 347.1 | 327.3 | 318.6 | 335.9 | 278.8 | 203.3 | 284.9 | 245.7 | 344.4 | 331.4
2555.1 | 2361.1 | -6.5 | 0 | 0 | 215.3 | 210.9 | 202.7 | 194.1 | 220.2 | 36.3 | 19.4 | 52.3 | 5.4 | 235.9 | 9.6 | 46.1 | 85.2 | 44.5 | 59.7 | 37.8 | 65.3 | 72.3 | 45 | 82.3 | 68.2 | 347 | 327.2 | 318.4 | 335.7 | 278.7 | 203.2 | 284.7 | 245.6 | 344.1 | 331.2
2556.1 | 2362.1 | -6.3 | 0 | 0 | 215 | 210.8 | 202.6 | 194 | 219.9 | 36.3 | 19.4 | 52.3 | 6 | 245.7 | 9 | 46.3 | 85.6 | 44.5 | 59.6 | 37.7 | 65.2 | 72.3 | 45.7 | 82.2 | 68.4 | 346.9 | 327 | 318.2 | 335.5 | 278.5 | 203.1 | 284.6 | 245.4 | 343.8 | 331
2557.1 | 2363.1 | -6.3 | 0 | 0 | 214.6 | 210.5 | 202.4 | 194 | 220.2 | 36.3 | 19.4 | 52.2 | 4.9 | 238.4 | 9.7 | 46.5 | 85.5 | 44.5 | 59.5 | 37.7 | 66.1 | 71.6 | 45.6 | 81.6 | 68.4 | 346.8 | 326.8 | 318 | 335.4 | 278.4 | 203 | 284.4 | 245.2 | 343.6 | 330.8
2558.1 | 2364.1 | -6.5 | 0 | 0 | 214.2 | 210.3 | 202.4 | 193.9 | 219.5 | 36.3 | 19.4 | 52.2 | 4.4 | 249.7 | 10.1 | 46.8 | 85.5 | 44.5 | 59.4 | 37.6 | 66.3 | 71.3 | 45.6 | 81.5 | 68.4 | 346.7 | 326.7 | 317.8 | 335.2 | 278.2 | 202.9 | 284.1 | 245 | 343.3 | 330.6
2559.1 | 2365.1 | -6.6 | 0 | 0 | 213.8 | 210.3 | 202.3 | 193.8 | 218.5 | 36.3 | 19.4 | 52.2 | 5.7 | 247.7 | 12.3 | 47.2 | 85.3 | 44.4 | 59.3 | 37.6 | 65.8 | 70.8 | 45.6 | 81.6 | 68.3 | 346.6 | 326.5 | 317.6 | 335 | 278 | 202.7 | 283.9 | 244.8 | 343.1 | 330.4
2560.1 | 2366.1 | -6.7 | 0 | 0 | 213.5 | 210.2 | 202.2 | 193.6 | 218.1 | 36.2 | 19.4 | 52.2 | 5.5 | 229.1 | 12.1 | 47.4 | 85.1 | 44.4 | 59.2 | 37.5 | 65.8 | 70.5 | 45.2 | 81.8 | 68.3 | 346.4 | 326.3 | 317.4 | 334.8 | 277.9 | 202.6 | 283.7 | 244.7 | 342.8 | 330.1
2561.1 | 2367.1 | -6.5 | 0 | 0 | 213.5 | 209.8 | 202 | 193.5 | 217.9 | 36.2 | 19.4 | 52.1 | 6.1 | 250.7 | 11.9 | 47.5 | 84.1 | 44.3 | 59 | 37.5 | 66 | 70.8 | 44.6 | 82 | 68.3 | 346.3 | 326.1 | 317.3 | 334.6 | 277.7 | 202.5 | 283.6 | 244.5 | 342.5 | 330
2562.1 | 2368.1 | -6.4 | 0 | 0 | 213.5 | 209.5 | 202 | 193.4 | 218.1 | 36.2 | 19.4 | 52.1 | 6.4 | 232.8 | 13.3 | 47.5 | 83.8 | 44.2 | 58.8 | 37.5 | 65.5 | 71 | 44.2 | 81.6 | 68.3 | 346.2 | 326 | 317.1 | 334.4 | 277.5 | 202.4 | 283.3 | 244.3 | 342.3 | 329.8
2563.1 | 2369.1 | -6.3 | 0 | 0 | 213.2 | 209.4 | 201.9 | 193.3 | 218.7 | 36.2 | 19.4 | 52 | 4.8 | 220.5 | 12.1 | 47.5 | 83.1 | 44.2 | 58.6 | 37.4 | 64.8 | 70.6 | 43.6 | 81.8 | 68.2 | 346.1 | 325.8 | 316.9 | 334.2 | 277.4 | 202.3 | 283.1 | 244.2 | 342 | 329.6
2564.1 | 2370.1 | -6.2 | 0 | 0 | 213 | 209.4 | 201.9 | 193.2 | 218.4 | 36.1 | 19.4 | 51.9 | 5 | 238.8 | 12 | 47.6 | 82.1 | 44.3 | 58.4 | 37.4 | 63.8 | 70.8 | 43.2 | 82 | 68.2 | 346 | 325.6 | 316.7 | 334 | 277.2 | 202.2 | 283 | 244 | 341.7 | 329.3
2565.1 | 2371.1 | -6.1 | 0 | 0 | 212.9 | 209.4 | 201.7 | 193.1 | 218.1 | 36.2 | 19.4 | 51.8 | 4 | 233.7 | 15.3 | 47.7 | 81.2 | 44.3 | 58.2 | 37.4 | 63 | 71.1 | 42.9 | 82.1 | 68.1 | 345.9 | 325.4 | 316.5 | 333.8 | 277 | 202.1 | 282.8 | 243.8 | 341.5 | 329.1
2566.1 | 2372.1 | -6.3 | 0 | 0 | 212.9 | 209.2 | 201.7 | 193 | 218 | 36.2 | 19.4 | 51.8 | 4.8 | 247.6 | 14.5 | 47.8 | 80.7 | 44.2 | 57.9 | 37.4 | 63.7 | 71.4 | 42.6 | 82 | 68.1 | 345.8 | 325.3 | 316.3 | 333.7 | 276.8 | 201.9 | 282.6 | 243.6 | 341.2 | 328.9
2567.1 | 2373.1 | -6.4 | 0 | 0 | 212.9 | 209 | 201.6 | 192.8 | 218.1 | 36.2 | 19.4 | 51.8 | 5.1 | 246.7 | 14.7 | 47.8 | 80.4 | 44.3 | 57.7 | 37.5 | 63.1 | 71.4 | 42.3 | 82 | 68 | 345.7 | 325.1 | 316.2 | 333.5 | 276.7 | 201.8 | 282.4 | 243.4 | 340.9 | 328.7
2568.1 | 2374.1 | -6.5 | 0 | 0 | 212.9 | 208.9 | 201.6 | 192.6 | 217.8 | 36.2 | 19.4 | 51.8 | 4.8 | 239 | 13 | 47.9 | 80.3 | 44.3 | 57.4 | 37.4 | 63.3 | 71.3 | 41.6 | 82.1 | 68 | 345.6 | 324.9 | 316 | 333.3 | 276.5 | 201.6 | 282.2 | 243.2 | 340.7 | 328.5
2569.1 | 2375.1 | -6.5 | 0 | 0 | 212.5 | 208.7 | 201.4 | 192.4 | 217.6 | 36.2 | 19.4 | 51.8 | 4.7 | 252.1 | 12 | 47.9 | 80.3 | 44.2 | 57.2 | 37.4 | 63.4 | 71.3 | 40.8 | 82 | 68.1 | 345.5 | 324.8 | 315.8 | 333.1 | 276.3 | 201.5 | 282 | 243.1 | 340.4 | 328.3
2570.1 | 2376.1 | -6.5 | 0 | 0 | 212 | 208.4 | 201.2 | 192.4 | 217.3 | 36.2 | 19.4 | 51.8 | 5.2 | 250.9 | 11.4 | 47.9 | 80.4 | 44.2 | 57 | 37.4 | 63.9 | 71.2 | 40.3 | 81.7 | 68.1 | 345.4 | 324.6 | 315.6 | 332.9 | 276.2 | 201.4 | 281.8 | 242.9 | 340.1 | 328.1
2571.1 | 2377.1 | -6.6 | 0 | 0 | 211.7 | 208.2 | 201 | 192.3 | 217.4 | 36.2 | 19.4 | 51.7 | 5.4 | 236.2 | 10.1 | 48.1 | 80.5 | 44.1 | 56.8 | 37.3 | 64.3 | 71.3 | 40 | 81.2 | 68.2 | 345.3 | 324.4 | 315.4 | 332.7 | 276 | 201.2 | 281.6 | 242.7 | 339.9 | 327.9
2572.1 | 2378.1 | -6.5 | 0 | 0 | 211.5 | 208 | 201 | 192 | 217.7 | 36.2 | 19.4 | 51.7 | 6.1 | 235 | 8.4 | 48.1 | 80.1 | 44 | 56.5 | 37.2 | 64 | 71.2 | 39.9 | 80.8 | 68.3 | 345.2 | 324.3 | 315.2 | 332.6 | 275.9 | 201.1 | 281.4 | 242.6 | 339.6 | 327.7
2573.1 | 2379.1 | -6.6 | 0 | 0 | 211.6 | 208 | 201.1 | 191.8 | 218 | 36.3 | 19.4 | 51.6 | 6.2 | 220.6 | 8.5 | 48.1 | 80 | 43.8 | 56.4 | 37.2 | 63 | 71.2 | 39.9 | 80.7 | 68.4 | 345.1 | 324.1 | 315.1 | 332.4 | 275.7 | 201 | 281.3 | 242.4 | 339.4 | 327.5
2574.1 | 2380.1 | -6.5 | 0 | 0 | 211.8 | 207.9 | 201 | 191.6 | 218.4 | 36.4 | 19.5 | 51.5 | 6.4 | 217.3 | 7.9 | 48 | 80.1 | 43.7 | 56.1 | 37.1 | 64 | 71.7 | 39.7 | 80.7 | 68.3 | 345 | 323.9 | 314.9 | 332.2 | 275.5 | 200.9 | 281 | 242.2 | 339.1 | 327.3
2575.1 | 2381.1 | -6.5 | 0 | 0 | 211.7 | 207.8 | 200.7 | 191.4 | 218.8 | 36.4 | 19.5 | 51.5 | 5.5 | 238.5 | 7 | 47.8 | 79.9 | 43.6 | 55.9 | 37 | 63.7 | 72.1 | 39.6 | 80.9 | 68.4 | 344.9 | 323.8 | 314.7 | 332 | 275.4 | 200.7 | 280.8 | 242 | 338.9 | 327.1
2576.1 | 2382.1 | -6.5 | 0 | 0 | 211.3 | 207.6 | 200.6 | 191.4 | 219.2 | 36.5 | 19.5 | 51.4 | 5.4 | 231.1 | 5.6 | 47.6 | 79.8 | 43.5 | 55.7 | 37 | 64.3 | 71.9 | 39.6 | 81.1 | 68.2 | 344.8 | 323.6 | 314.5 | 331.8 | 275.2 | 200.6 | 280.7 | 241.9 | 338.6 | 326.9
2577.1 | 2383.1 | -6.3 | 0 | 0 | 210.9 | 207.8 | 200.4 | 191.4 | 219.6 | 36.5 | 19.5 | 51.4 | 4.8 | 225.8 | 6.5 | 47.4 | 79.8 | 43.4 | 55.5 | 36.8 | 64.4 | 71.7 | 39.6 | 81.3 | 68.1 | 344.7 | 323.5 | 314.4 | 331.6 | 275 | 200.4 | 280.5 | 241.7 | 338.4 | 326.7
2578.1 | 2384.1 | -6.2 | 0 | 0 | 210.7 | 207.7 | 200.3 | 191.2 | 220 | 36.4 | 19.5 | 51.4 | 5.6 | 257.1 | 8.2 | 47.3 | 79.8 | 43.3 | 55.3 | 36.8 | 62.8 | 72.1 | 39.6 | 81.4 | 68 | 344.6 | 323.3 | 314.2 | 331.4 | 274.9 | 200.3 | 280.3 | 241.6 | 338.1 | 326.5
2579.1 | 2385.1 | -6.5 | 0 | 0 | 210.6 | 207.2 | 200.2 | 190.9 | 220.3 | 36.3 | 19.5 | 51.3 | 5.7 | 238.4 | 10.6 | 47.2 | 79.8 | 43.2 | 55.1 | 36.8 | 61.9 | 72 | 39.7 | 81.6 | 68 | 344.5 | 323.1 | 314 | 331.2 | 274.7 | 200.1 | 280 | 241.4 | 337.9 | 326.4
2580.1 | 2386.1 | -6.5 | 0 | 0 | 210.4 | 207.2 | 200 | 190.9 | 220.6 | 36.2 | 19.5 | 51.3 | 5.8 | 248.6 | 12.6 | 47.1 | 79.8 | 43.1 | 54.9 | 36.7 | 63.5 | 70 | 39.6 | 82 | 67.9 | 344.4 | 323 | 313.8 | 331 | 274.5 | 200 | 279.9 | 241.2 | 337.6 | 326.1
2581.1 | 2387.1 | -6.5 | 0 | 0 | 210.2 | 207.3 | 199.7 | 190.9 | 220.9 | 36.2 | 19.5 | 51.3 | 5.4 | 238.3 | 14.2 | 47.1 | 79.9 | 43.1 | 54.7 | 36.7 | 64.2 | 69.8 | 39.5 | 82.3 | 67.8 | 344.3 | 322.8 | 313.6 | 330.9 | 274.4 | 199.9 | 279.7 | 241.1 | 337.3 | 326
2582.1 | 2388.1 | -6.6 | 0 | 0 | 210.3 | 207.5 | 199.5 | 190.9 | 221.2 | 36.2 | 19.5 | 51.2 | 4.5 | 236.8 | 13.6 | 47.2 | 79.9 | 43 | 54.4 | 36.7 | 64.2 | 70 | 39.4 | 82.4 | 67.9 | 344.2 | 322.7 | 313.4 | 330.7 | 274.3 | 199.8 | 279.5 | 240.9 | 337.1 | 325.7
2583.1 | 2389.1 | -6.5 | 0 | 0 | 210 | 207.6 | 199.4 | 190.7 | 221.4 | 36.1 | 19.5 | 51.2 | 4.9 | 242.9 | 11.7 | 47 | 80 | 42.9 | 54.3 | 36.6 | 63.9 | 70.2 | 39.4 | 82.4 | 67.9 | 344.1 | 322.5 | 313.3 | 330.5 | 274.1 | 199.7 | 279.3 | 240.7 | 336.8 | 325.6
2584.1 | 2390.1 | -6.5 | 0 | 0 | 209.8 | 207.3 | 199.2 | 190.6 | 221.5 | 36.1 | 19.5 | 51.2 | 4.7 | 240.3 | 11.4 | 46.9 | 80.1 | 42.8 | 54.1 | 36.5 | 64.6 | 70 | 39.3 | 82.4 | 67.8 | 344 | 322.3 | 313.1 | 330.3 | 273.9 | 199.5 | 279.1 | 240.5 | 336.6 | 325.4
2585.1 | 2391.1 | -6.5 | 0 | 0 | 209.7 | 207.1 | 199 | 190.5 | 221.8 | 36.1 | 19.5 | 51.2 | 4.6 | 231.5 | 10.7 | 46.9 | 80.1 | 42.7 | 53.9 | 36.5 | 65.3 | 70.2 | 39.2 | 82.3 | 67.8 | 343.9 | 322.2 | 312.9 | 330.1 | 273.8 | 199.3 | 278.9 | 240.4 | 336.3 | 325.2
2586.1 | 2392.1 | -6.4 | 0 | 0 | 209.6 | 207.2 | 198.9 | 190.3 | 222 | 36 | 19.5 | 51.1 | 5.5 | 241.5 | 11.2 | 46.8 | 80 | 42.5 | 53.7 | 36.4 | 65.6 | 70.4 | 39.1 | 82.3 | 67.8 | 343.8 | 322 | 312.7 | 329.9 | 273.6 | 199.2 | 278.7 | 240.2 | 336 | 325
2587.1 | 2393.1 | -6.4 | 0 | 0 | 209.5 | 207.1 | 198.8 | 190.1 | 222.3 | 35.9 | 19.5 | 51 | 5.9 | 206.2 | 10.8 | 46.7 | 79.7 | 42.4 | 53.4 | 36.4 | 65.6 | 70.3 | 39.2 | 82.4 | 67.8 | 343.7 | 321.9 | 312.6 | 329.7 | 273.5 | 199 | 278.6 | 240 | 335.8 | 324.8
2588.1 | 2394.1 | -6.5 | 0 | 0 | 209.7 | 207.2 | 198.6 | 189.9 | 222.5 | 35.9 | 19.5 | 51 | 4.7 | 226.1 | 12.3 | 46.6 | 79.7 | 42.3 | 53.2 | 36.3 | 65.5 | 69.9 | 39.6 | 82.4 | 67.8 | 343.6 | 321.7 | 312.4 | 329.6 | 273.3 | 198.9 | 278.4 | 239.8 | 335.6 | 324.6
2589.1 | 2395.1 | -6.6 | 0 | 0 | 209.7 | 207.1 | 198.5 | 189.7 | 222.6 | 35.8 | 19.5 | 51 | 4.7 | 248.5 | 10.6 | 46.5 | 79.6 | 42.1 | 53.1 | 36.2 | 65.1 | 70.3 | 40 | 82.5 | 67.8 | 343.5 | 321.6 | 312.2 | 329.4 | 273.1 | 198.7 | 278.1 | 239.7 | 335.3 | 324.4
2590.1 | 2396.1 | -6.5 | 0 | 0 | 209.3 | 207.1 | 198.5 | 189.5 | 222.8 | 35.8 | 19.5 | 51 | 6.4 | 237.4 | 12.3 | 46.4 | 79.4 | 42.1 | 53 | 36.1 | 65 | 70.5 | 40.4 | 82.5 | 67.7 | 343.4 | 321.4 | 312 | 329.2 | 273 | 198.5 | 277.9 | 239.5 | 335.1 | 324.2
2591.1 | 2397.1 | -6.5 | 0 | 0 | 208.9 | 207.2 | 198.4 | 189.4 | 222.9 | 35.8 | 19.5 | 50.9 | 5.5 | 215.1 | 9.7 | 46.5 | 79.3 | 42.2 | 52.8 | 36.1 | 64.6 | 69.8 | 41.1 | 82.4 | 67.6 | 343.3 | 321.3 | 311.9 | 329 | 272.8 | 198.4 | 277.7 | 239.4 | 334.8 | 324
2592.1 | 2398.1 | -6.5 | 0 | 0 | 208.7 | 206.9 | 198.3 | 189.3 | 222.9 | 35.8 | 19.5 | 50.9 | 4.8 | 256.4 | 9.8 | 46.5 | 79.4 | 42.2 | 52.7 | 36.1 | 64.6 | 69.6 | 41.9 | 82.2 | 67.4 | 343.2 | 321.1 | 311.7 | 328.8 | 272.7 | 198.2 | 277.5 | 239.2 | 334.6 | 323.8
2593.1 | 2399.1 | -6.4 | 0 | 0 | 208.7 | 206.5 | 198.1 | 189.2 | 223 | 35.8 | 19.5 | 50.9 | 5.3 | 243.3 | 11.4 | 46.5 | 79.4 | 42.2 | 52.6 | 36.1 | 65 | 70.1 | 42 | 82.2 | 67.3 | 343.1 | 320.9 | 311.5 | 328.6 | 272.5 | 198.1 | 277.3 | 239 | 334.3 | 323.6
2594.1 | 2400.1 | -6.2 | 0 | 0 | 208.7 | 206.4 | 197.8 | 189.2 | 223.1 | 35.8 | 19.5 | 50.9 | 6.4 | 237.6 | 13.2 | 46.5 | 79.5 | 42.2 | 52.4 | 36 | 64.9 | 70.4 | 42.1 | 82.2 | 67.1 | 343 | 320.8 | 311.4 | 328.4 | 272.3 | 197.9 | 277.1 | 238.9 | 334.1 | 323.4
2595.1 | 2401.1 | -6.2 | 0 | 0 | 208.9 | 206.3 | 197.6 | 189.2 | 223.2 | 35.8 | 19.5 | 50.8 | 6.4 | 242.4 | 12.1 | 46.5 | 79.5 | 42.2 | 52.3 | 36 | 64.3 | 70.4 | 42.1 | 82.2 | 67.1 | 342.9 | 320.6 | 311.2 | 328.2 | 272.1 | 197.7 | 276.9 | 238.7 | 333.8 | 323.2
2596.1 | 2402.1 | -6.4 | 0 | 0 | 209 | 205.9 | 197.5 | 189.1 | 223.3 | 35.8 | 19.6 | 50.7 | 5.8 | 252.1 | 10.4 | 46.5 | 79.2 | 42.1 | 52.1 | 36 | 63.7 | 70.4 | 42.2 | 82.2 | 67 | 342.8 | 320.5 | 311 | 328.1 | 272 | 197.6 | 276.8 | 238.6 | 333.6 | 323
2597.1 | 2403.1 | -6.5 | 0 | 0 | 209.1 | 205.7 | 197.3 | 189.1 | 223.3 | 35.8 | 19.6 | 50.7 | 5.7 | 244.7 | 9.7 | 46.4 | 79.1 | 42 | 52 | 35.9 | 63 | 69.9 | 42 | 82.2 | 67 | 342.7 | 320.3 | 310.8 | 327.9 | 271.8 | 197.5 | 276.6 | 238.4 | 333.3 | 322.8
2598.1 | 2404.1 | -6.5 | 0 | 0 | 208.9 | 205.4 | 197.2 | 189.1 | 223.1 | 35.8 | 19.6 | 50.6 | 6.5 | 226.1 | 9 | 46.3 | 79 | 42 | 51.9 | 35.9 | 63.8 | 69.9 | 41.8 | 82.2 | 66.9 | 342.6 | 320.2 | 310.7 | 327.7 | 271.6 | 197.4 | 276.4 | 238.2 | 333.1 | 322.6
2599.1 | 2405.1 | -6.3 | 0 | 0 | 208.8 | 205.1 | 197.1 | 189 | 222.7 | 35.8 | 19.6 | 50.6 | 7 | 236.2 | 10.2 | 46.3 | 79.1 | 42 | 51.7 | 35.9 | 63.3 | 70.2 | 41.5 | 82.1 | 66.9 | 342.5 | 320 | 310.5 | 327.5 | 271.5 | 197.3 | 276.2 | 238.1 | 332.8 | 322.4
2600.1 | 2406.1 | -6.3 | 0 | 0 | 208.7 | 204.9 | 197 | 188.8 | 222.3 | 35.8 | 19.6 | 50.5 | 6.6 | 224.8 | 9.2 | 46.2 | 79.2 | 42 | 51.6 | 35.8 | 62.6 | 70.5 | 41.3 | 82 | 66.8 | 342.4 | 319.8 | 310.3 | 327.3 | 271.3 | 197.2 | 276 | 237.9 | 332.6 | 322.2
2601.1 | 2407.1 | -6.2 | 0 | 0 | 208.5 | 204.7 | 196.8 | 188.6 | 221.9 | 35.8 | 19.6 | 50.4 | 4.3 | 232.2 | 10.1 | 46.2 | 79.1 | 42 | 51.5 | 35.8 | 63.4 | 70.6 | 41.1 | 81.7 | 66.9 | 342.3 | 319.7 | 310.2 | 327.1 | 271.2 | 197.1 | 275.8 | 237.8 | 332.3 | 322
2602.1 | 2408.1 | -6.4 | 0 | 0 | 208.2 | 204.6 | 196.7 | 188.5 | 221.8 | 35.8 | 19.6 | 50.3 | 4.4 | 239.9 | 9 | 46.2 | 79.1 | 42 | 51.4 | 35.8 | 63.4 | 70.8 | 40.8 | 81.5 | 67.1 | 342.2 | 319.5 | 310 | 326.9 | 271 | 196.9 | 275.7 | 237.5 | 332.1 | 321.9
2603.1 | 2409.1 | -6.4 | 0 | 0 | 207.7 | 204.8 | 196.6 | 188.3 | 221.9 | 35.8 | 19.6 | 50.3 | 4.8 | 221.3 | 9.3 | 46.2 | 79.3 | 42.1 | 51.3 | 35.8 | 61.5 | 70.6 | 40.5 | 81.4 | 67 | 342.1 | 319.4 | 309.8 | 326.8 | 270.9 | 196.8 | 275.4 | 237.4 | 331.9 | 321.7
2604.1 | 2410.1 | -6.5 | 0 | 0 | 207.5 | 204.9 | 196.5 | 188.2 | 222.1 | 35.7 | 19.6 | 50.3 | 6.3 | 245.2 | 10.6 | 46.1 | 79 | 42 | 51.2 | 35.8 | 62.3 | 71 | 40.5 | 81.3 | 66.9 | 342 | 319.2 | 309.6 | 326.6 | 270.7 | 196.7 | 275.3 | 237.2 | 331.6 | 321.5
2605.1 | 2411.1 | -6.6 | 0 | 0 | 207.1 | 205 | 196.5 | 188.1 | 222.1 | 35.7 | 19.6 | 50.4 | 6.7 | 221.7 | 11.2 | 46.1 | 79.1 | 42 | 51.1 | 35.8 | 63.4 | 70.7 | 40.2 | 81.1 | 66.9 | 341.9 | 319.1 | 309.5 | 326.4 | 270.6 | 196.6 | 275.1 | 237.1 | 331.4 | 321.3
2606.1 | 2412.1 | -6.6 | 0 | 0 | 206.8 | 205 | 196.3 | 188.1 | 222.1 | 35.7 | 19.6 | 50.4 | 5.7 | 230.3 | 11.1 | 45.9 | 79.2 | 42 | 51 | 35.7 | 63.3 | 70.4 | 40 | 81.2 | 67 | 341.8 | 318.9 | 309.3 | 326.2 | 270.4 | 196.5 | 275 | 236.9 | 331.1 | 321.1
2607.1 | 2413.1 | -6.7 | 0 | 0 | 206.6 | 204.8 | 196.1 | 188 | 222.2 | 35.7 | 19.6 | 50.4 | 6 | 231.2 | 9.8 | 45.8 | 79.3 | 42 | 50.8 | 35.7 | 64.1 | 70.2 | 39.8 | 81.1 | 67 | 341.7 | 318.7 | 309.1 | 326 | 270.3 | 196.4 | 274.8 | 236.7 | 330.9 | 320.9
2608.1 | 2414.1 | -6.7 | 0 | 0 | 206.5 | 204.5 | 196.1 | 187.8 | 222.2 | 35.6 | 19.6 | 50.4 | 6.2 | 230.5 | 10.5 | 45.7 | 79.3 | 42 | 50.7 | 35.6 | 64.5 | 69.9 | 39.7 | 81 | 67 | 341.6 | 318.6 | 309 | 325.8 | 270.1 | 196.3 | 274.6 | 236.6 | 330.6 | 320.7
2609.1 | 2415.1 | -6.5 | 0 | 0 | 206.6 | 204.2 | 196 | 187.7 | 222.3 | 35.6 | 19.6 | 50.4 | 6.1 | 218.4 | 10.8 | 45.6 | 79.4 | 42 | 50.6 | 35.6 | 65.3 | 70.3 | 39.6 | 80.8 | 67 | 341.5 | 318.4 | 308.8 | 325.6 | 270 | 196.2 | 274.4 | 236.4 | 330.4 | 320.5
2610.1 | 2416.1 | -6.4 | 0 | 0 | 206.7 | 204.3 | 195.8 | 187.4 | 222.3 | 35.6 | 19.6 | 50.4 | 5.1 | 244.6 | 13.4 | 45.6 | 79.3 | 42 | 50.5 | 35.6 | 64.8 | 69.8 | 39.5 | 81 | 67 | 341.4 | 318.3 | 308.6 | 325.4 | 269.8 | 196.1 | 274.3 | 236.3 | 330.1 | 320.3
2611.1 | 2417.1 | -6.4 | 0 | 0 | 206.8 | 204.5 | 195.5 | 187.2 | 222.2 | 35.6 | 19.6 | 50.4 | 4.1 | 246.8 | 15.7 | 45.5 | 79.1 | 42.1 | 50.4 | 35.6 | 64.6 | 69 | 39.4 | 81.2 | 67.1 | 341.3 | 318.1 | 308.5 | 325.2 | 269.7 | 196 | 274.1 | 236.1 | 329.9 | 320.1
2612.1 | 2418.1 | -6.3 | 0 | 0 | 206.7 | 204.3 | 195.4 | 187.2 | 222.2 | 35.6 | 19.6 | 50.4 | 4.8 | 243.8 | 15.4 | 45.4 | 79.2 | 42.2 | 50.3 | 35.6 | 64.7 | 69.3 | 39.3 | 81.4 | 67.1 | 341.2 | 318 | 308.3 | 325.1 | 269.5 | 195.9 | 273.9 | 235.9 | 329.7 | 319.9
2613.1 | 2419.1 | -6.2 | 0 | 0 | 206.5 | 203.9 | 195.3 | 187.2 | 222.2 | 35.6 | 19.6 | 50.4 | 6 | 254.1 | 16.1 | 45.4 | 79.3 | 42.2 | 50.3 | 35.6 | 63.2 | 69.2 | 39.2 | 81.5 | 67.1 | 341.1 | 317.8 | 308.1 | 324.9 | 269.3 | 195.7 | 273.7 | 235.8 | 329.4 | 319.7
2614.1 | 2420.1 | -6.1 | 0 | 0 | 206.4 | 203.6 | 195.2 | 187.1 | 222.1 | 35.6 | 19.6 | 50.3 | 5.6 | 263.3 | 17.9 | 45.4 | 79.4 | 42.2 | 50.2 | 35.6 | 62.4 | 69.3 | 39.2 | 81.6 | 67.2 | 341 | 317.7 | 307.9 | 324.7 | 269.2 | 195.6 | 273.5 | 235.7 | 329.2 | 319.6
2615.1 | 2421.1 | -5.9 | 0 | 0 | 206.1 | 203.3 | 195.2 | 187 | 222 | 35.5 | 19.6 | 50.3 | 5.2 | 264.3 | 17.5 | 45.4 | 79.5 | 42.2 | 50.1 | 35.5 | 63.4 | 69.7 | 39.3 | 81.5 | 67.2 | 340.9 | 317.5 | 307.8 | 324.5 | 269 | 195.5 | 273.2 | 235.5 | 328.9 | 319.4
2616.1 | 2422.1 | -5.7 | 0 | 0 | 205.9 | 203.1 | 195 | 186.7 | 221.8 | 35.5 | 19.6 | 50.2 | 5.1 | 264 | 15.5 | 45.1 | 79.5 | 42.1 | 50 | 35.4 | 63.4 | 70.1 | 39.4 | 81.4 | 67.1 | 340.8 | 317.3 | 307.6 | 324.3 | 268.8 | 195.4 | 273.1 | 235.3 | 328.7 | 319.2
2617.1 | 2423.1 | -6 | 0 | 0 | 206 | 202.8 | 194.9 | 186.5 | 221.7 | 35.5 | 19.6 | 50.1 | 6.6 | 262.8 | 16.5 | 45 | 79.6 | 42 | 50 | 35.4 | 64.1 | 70.4 | 39.5 | 81.3 | 67.1 | 340.7 | 317.2 | 307.4 | 324.1 | 268.7 | 195.2 | 272.9 | 235.2 | 328.5 | 319
2618.1 | 2424.1 | -6.5 | 0 | 0 | 206 | 202.6 | 194.9 | 186.3 | 221.7 | 35.5 | 19.6 | 50 | 6.6 | 257.6 | 17.8 | 45 | 79.3 | 41.9 | 49.9 | 35.4 | 64.3 | 69.9 | 39.7 | 81.2 | 66.8 | 340.6 | 317 | 307.2 | 323.9 | 268.6 | 195.1 | 272.8 | 235 | 328.2 | 318.8
2619.1 | 2425.1 | -6.3 | 0 | 0 | 206.1 | 202.5 | 195 | 186.1 | 221.6 | 35.4 | 19.6 | 49.9 | 4.8 | 258.6 | 17.1 | 45 | 79 | 41.8 | 49.8 | 35.3 | 64.6 | 69.3 | 39.9 | 80.9 | 66.4 | 340.5 | 316.9 | 307.1 | 323.7 | 268.4 | 195 | 272.6 | 234.9 | 328 | 318.6
2620.1 | 2426.1 | -6.2 | 0 | 0 | 205.9 | 202.2 | 195 | 186 | 221.5 | 35.4 | 19.6 | 49.9 | 5.2 | 245.5 | 15.6 | 44.9 | 78.9 | 41.7 | 49.7 | 35.2 | 62.8 | 68.3 | 40 | 80.9 | 66.3 | 340.4 | 316.7 | 306.9 | 323.6 | 268.2 | 194.9 | 272.4 | 234.7 | 327.7 | 318.4
2621.1 | 2427.1 | -6.1 | 0 | 0 | 205.5 | 202 | 194.9 | 186 | 221.4 | 35.3 | 19.6 | 49.9 | 5.4 | 249 | 14.7 | 44.7 | 78.8 | 41.6 | 49.7 | 35.2 | 61.3 | 67.8 | 40 | 81.2 | 66.2 | 340.3 | 316.6 | 306.8 | 323.4 | 268.1 | 194.7 | 272.3 | 234.5 | 327.5 | 318.3
2622.1 | 2428.1 | -6.1 | 0 | 0 | 205 | 202 | 194.8 | 186 | 221.4 | 35.3 | 19.6 | 49.8 | 5 | 263.5 | 13.4 | 44.7 | 78.8 | 41.6 | 49.6 | 35.1 | 62.6 | 67.6 | 40 | 81.5 | 66.2 | 340.2 | 316.4 | 306.6 | 323.2 | 267.9 | 194.5 | 272.1 | 234.4 | 327.3 | 318.1
2623.1 | 2429.1 | -6.3 | 0 | 0 | 204.6 | 202.1 | 194.6 | 186 | 221.3 | 35.2 | 19.6 | 49.8 | 5.6 | 252.1 | 12 | 44.4 | 78.8 | 41.5 | 49.6 | 35 | 60.5 | 67.6 | 39.9 | 81.7 | 66.2 | 340.1 | 316.3 | 306.4 | 323 | 267.8 | 194.4 | 272 | 234.2 | 327 | 317.9
2624.1 | 2430.1 | -6.4 | 0 | 0 | 204.4 | 202.1 | 194.4 | 185.9 | 221.2 | 35.2 | 19.6 | 49.7 | 7 | 266 | 12.3 | 44.2 | 78.9 | 41.4 | 49.5 | 34.9 | 58.9 | 67.6 | 40.1 | 81.8 | 66.3 | 340 | 316.1 | 306.3 | 322.8 | 267.6 | 194.3 | 271.8 | 234.1 | 326.8 | 317.7
2625.1 | 2431.1 | -6.4 | 0 | 0 | 204.1 | 201.8 | 194.2 | 185.9 | 221.2 | 35.2 | 19.6 | 49.7 | 7.7 | 262.8 | 12.5 | 44.2 | 79 | 41.4 | 49.4 | 34.8 | 59.2 | 67.7 | 40.1 | 82 | 66.1 | 339.9 | 316 | 306.1 | 322.6 | 267.5 | 194.2 | 271.6 | 233.9 | 326.6 | 317.5
2626.1 | 2432.1 | -6.5 | 0 | 0 | 203.9 | 201.5 | 194 | 185.7 | 221.1 | 35.1 | 19.6 | 49.6 | 7.5 | 266.1 | 12.1 | 44.2 | 78.8 | 41.3 | 49.3 | 34.8 | 58.3 | 67.9 | 40.1 | 81.9 | 66.1 | 339.8 | 315.8 | 305.9 | 322.4 | 267.3 | 194.1 | 271.5 | 233.8 | 326.3 | 317.4
2627.1 | 2433.1 | -6.3 | 0 | 0 | 203.6 | 201.7 | 193.8 | 185.5 | 221.1 | 35.1 | 19.6 | 49.6 | 5.7 | 249.9 | 12.6 | 44.3 | 78.7 | 41.3 | 49.2 | 34.8 | 58.2 | 68 | 40.2 | 81.8 | 66.1 | 339.7 | 315.7 | 305.8 | 322.3 | 267.2 | 194 | 271.3 | 233.6 | 326.1 | 317.2
2628.1 | 2434.1 | -6.3 | 0 | 0 | 203.6 | 201.8 | 193.6 | 185.2 | 221.1 | 35.1 | 19.6 | 49.6 | 5 | 244.2 | 12.7 | 44.3 | 78.8 | 41.3 | 49.2 | 34.7 | 58.2 | 68 | 40.2 | 81.8 | 66.1 | 339.6 | 315.5 | 305.6 | 322.1 | 267 | 194 | 271.1 | 233.4 | 325.9 | 317
2629.1 | 2435.1 | -6.5 | 0 | 0 | 203.7 | 201.5 | 193.4 | 185.1 | 221 | 35.2 | 19.7 | 49.6 | 5.1 | 252.6 | 14.1 | 44.2 | 78.8 | 41.2 | 49.1 | 34.7 | 59.8 | 67.7 | 40.2 | 81.8 | 66 | 339.5 | 315.4 | 305.4 | 321.9 | 266.8 | 193.9 | 270.9 | 233.3 | 325.6 | 316.8
2630.1 | 2436.1 | -6.7 | 0 | 0 | 203.7 | 201.2 | 193.3 | 185.1 | 220.9 | 35.2 | 19.7 | 49.5 | 5.4 | 248.2 | 16.4 | 44.1 | 78.8 | 41.2 | 49 | 34.7 | 61.3 | 67.1 | 40.4 | 81.9 | 66 | 339.4 | 315.2 | 305.3 | 321.7 | 266.7 | 193.8 | 270.7 | 233.1 | 325.4 | 316.6
2631.1 | 2437.1 | -6.8 | 0 | 0 | 203.9 | 201.2 | 193.2 | 185 | 220.8 | 35.2 | 19.7 | 49.6 | 5 | 248.2 | 17.8 | 44.2 | 78.6 | 41.2 | 49 | 34.7 | 60.2 | 66.9 | 40.7 | 81.9 | 65.9 | 339.3 | 315.1 | 305.1 | 321.5 | 266.6 | 193.6 | 270.5 | 233 | 325.2 | 316.5
2632.1 | 2438.1 | -6.8 | 0 | 0 | 204.1 | 201.3 | 193 | 184.9 | 220.6 | 35.2 | 19.7 | 49.6 | 5.1 | 251.4 | 19.1 | 44.2 | 78.6 | 41.2 | 48.9 | 34.7 | 60.8 | 67.4 | 40.9 | 82 | 65.9 | 339.2 | 314.9 | 305 | 321.3 | 266.4 | 193.5 | 270.4 | 232.8 | 324.9 | 316.3
2633.1 | 2439.1 | -6.7 | 0 | 0 | 204.2 | 201.3 | 192.9 | 184.8 | 220.5 | 35.2 | 19.7 | 49.5 | 5.4 | 247.9 | 19.1 | 44.2 | 78.7 | 41.2 | 48.8 | 34.7 | 60 | 67 | 41 | 82 | 65.8 | 339.1 | 314.8 | 304.8 | 321.1 | 266.2 | 193.4 | 270.1 | 232.7 | 324.7 | 316.1
2634.1 | 2440.1 | -6.6 | 0 | 0 | 204.1 | 201.1 | 192.8 | 184.6 | 220.3 | 35.2 | 19.7 | 49.5 | 4.4 | 244.4 | 18.8 | 44.2 | 78.6 | 41.2 | 48.7 | 34.7 | 58.6 | 67.2 | 41.2 | 82 | 65.9 | 339 | 314.6 | 304.6 | 320.9 | 266.1 | 193.3 | 270 | 232.5 | 324.5 | 315.9
2635.1 | 2441.1 | -6.6 | 0 | 0 | 203.8 | 200.9 | 192.7 | 184.5 | 220.1 | 35.2 | 19.7 | 49.4 | 4.3 | 248 | 18.5 | 44.2 | 78.5 | 41.2 | 48.7 | 34.7 | 58.1 | 67 | 41.4 | 82 | 66 | 338.9 | 314.5 | 304.5 | 320.7 | 266 | 193.2 | 269.8 | 232.4 | 324.2 | 315.8
2636.1 | 2442.1 | -6.6 | 0 | 0 | 203.2 | 201 | 192.6 | 184.5 | 219.9 | 35.1 | 19.7 | 49.4 | 4 | 255.9 | 16.9 | 44.3 | 78.1 | 41.2 | 48.6 | 34.7 | 58.5 | 66.6 | 41.5 | 81.9 | 66 | 338.8 | 314.3 | 304.3 | 320.5 | 265.8 | 193 | 269.7 | 232.2 | 324 | 315.6
2637.1 | 2443.1 | -6.7 | 0 | 0 | 202.7 | 201.1 | 192.5 | 184.4 | 219.7 | 35.1 | 19.7 | 49.3 | 4.7 | 267.4 | 18.1 | 44.2 | 77.6 | 41.1 | 48.5 | 34.6 | 59.4 | 67.1 | 41.7 | 81.7 | 65.9 | 338.7 | 314.2 | 304.1 | 320.4 | 265.7 | 192.9 | 269.5 | 232.1 | 323.8 | 315.4
2638.1 | 2444.1 | -6.7 | 0 | 0 | 202.3 | 201.2 | 192.3 | 184.2 | 219.5 | 35.1 | 19.7 | 49.2 | 5.1 | 248.5 | 18.3 | 44.2 | 77.1 | 41.1 | 48.4 | 34.6 | 60.3 | 67.8 | 41.8 | 81.7 | 65.8 | 338.6 | 314 | 304 | 320.2 | 265.5 | 192.8 | 269.3 | 231.9 | 323.5 | 315.2
2639.1 | 2445.1 | -6.6 | 0 | 0 | 202 | 200.9 | 192.1 | 184.1 | 219.3 | 35.1 | 19.7 | 49.2 | 4.7 | 243.9 | 17 | 44.2 | 76.7 | 41 | 48.4 | 34.5 | 60.5 | 68.4 | 42.1 | 81.8 | 65.8 | 338.5 | 313.9 | 303.8 | 320 | 265.3 | 192.6 | 269.1 | 231.8 | 323.3 | 315.1
2640.1 | 2446.1 | -6.6 | 0 | 0 | 201.9 | 200.6 | 192.1 | 184 | 219.2 | 35.1 | 19.7 | 49.1 | 4.9 | 249.7 | 15 | 44.2 | 76.5 | 41 | 48.3 | 34.5 | 61.1 | 69.3 | 42.6 | 81.8 | 65.7 | 338.4 | 313.7 | 303.6 | 319.8 | 265.2 | 192.5 | 269 | 231.6 | 323.1 | 314.9
2641.1 | 2447.1 | -6.6 | 0 | 0 | 201.9 | 200.5 | 192.1 | 183.9 | 219.1 | 35 | 19.7 | 49.1 | 4.2 | 252.5 | 15.6 | 44.1 | 76.4 | 40.9 | 48.2 | 34.4 | 60.5 | 69.1 | 43.1 | 81.8 | 65.7 | 338.3 | 313.6 | 303.5 | 319.6 | 265.1 | 192.4 | 268.8 | 231.5 | 322.9 | 314.7
2642.1 | 2448.1 | -6.5 | 0 | 0 | 201.9 | 200.4 | 191.9 | 183.9 | 219 | 34.9 | 19.7 | 49.1 | 4.5 | 255.6 | 17.8 | 44.1 | 76.3 | 40.9 | 48.2 | 34.4 | 58.4 | 68.8 | 43.5 | 81.7 | 65.7 | 338.2 | 313.4 | 303.3 | 319.4 | 264.9 | 192.2 | 268.6 | 231.3 | 322.6 | 314.5
2643.1 | 2449.1 | -6.5 | 0 | 0 | 201.7 | 200.2 | 191.7 | 183.9 | 218.9 | 34.8 | 19.7 | 49.1 | 4.3 | 255.3 | 18.1 | 44 | 76.2 | 40.8 | 48.1 | 34.4 | 56.9 | 68.1 | 44 | 81.6 | 65.6 | 338.1 | 313.3 | 303.2 | 319.2 | 264.7 | 192.1 | 268.4 | 231.2 | 322.4 | 314.4
2644.1 | 2450.1 | -6.4 | 0 | 0 | 201.7 | 200 | 191.5 | 183.7 | 218.8 | 34.7 | 19.7 | 49.1 | 3.9 | 263.3 | 16.8 | 44 | 76.2 | 40.7 | 48 | 34.4 | 56 | 68 | 44.4 | 81.6 | 65.6 | 338 | 313.1 | 303 | 319.1 | 264.6 | 191.9 | 268.3 | 231 | 322.2 | 314.2
2645.1 | 2451.1 | -6.3 | 0 | 0 | 201.8 | 199.7 | 191.4 | 183.5 | 218.6 | 34.7 | 19.7 | 49.1 | 4.2 | 275.9 | 13.9 | 43.9 | 76.3 | 40.7 | 48 | 34.3 | 55.5 | 68 | 44.8 | 81.5 | 65.6 | 337.8 | 313 | 302.8 | 318.9 | 264.4 | 191.8 | 268.1 | 230.8 | 321.9 | 314
2646.1 | 2452.1 | -6.3 | 0 | 0 | 201.3 | 199.6 | 191.3 | 183.3 | 218.5 | 34.7 | 19.7 | 49 | 5 | 260.4 | 13.2 | 43.9 | 76.2 | 40.6 | 47.9 | 34.2 | 55.3 | 67.7 | 45.3 | 81.4 | 65.6 | 337.7 | 312.8 | 302.7 | 318.7 | 264.3 | 191.7 | 267.9 | 230.7 | 321.7 | 313.8
2647.1 | 2453.1 | -6.4 | 0 | 0 | 201 | 199.5 | 191.1 | 183.3 | 218.3 | 34.6 | 19.7 | 49 | 5 | 251.3 | 14.3 | 43.9 | 76.3 | 40.6 | 47.9 | 34.2 | 56.3 | 68.1 | 45.7 | 81.4 | 65.6 | 337.6 | 312.7 | 302.5 | 318.5 | 264.1 | 191.5 | 267.8 | 230.5 | 321.5 | 313.6
2648.1 | 2454.1 | -6.5 | 0 | 0 | 200.7 | 199.5 | 191 | 183.2 | 218.1 | 34.6 | 19.7 | 48.9 | 5 | 249.9 | 13.7 | 43.9 | 76.3 | 40.6 | 47.8 | 34.1 | 57.4 | 68.3 | 46.2 | 81.5 | 65.5 | 337.5 | 312.5 | 302.3 | 318.3 | 264 | 191.4 | 267.6 | 230.4 | 321.3 | 313.5
2649.1 | 2455.1 | -6.6 | 0 | 0 | 200.4 | 199.5 | 190.9 | 183.1 | 217.9 | 34.6 | 19.7 | 48.8 | 5 | 256.6 | 13.5 | 44 | 76.5 | 40.5 | 47.7 | 34.1 | 56.5 | 68.9 | 46.6 | 81.4 | 65.5 | 337.4 | 312.4 | 302.2 | 318.1 | 263.8 | 191.3 | 267.4 | 230.2 | 321 | 313.3
2650.1 | 2456.1 | -6.5 | 0 | 0 | 200.5 | 199.4 | 190.7 | 183 | 217.8 | 34.6 | 19.7 | 48.8 | 5 | 260.4 | 15.1 | 44 | 76.6 | 40.5 | 47.7 | 34.1 | 55.4 | 68.1 | 47.1 | 81.2 | 65.5 | 337.4 | 312.2 | 302 | 317.9 | 263.7 | 191.2 | 267.2 | 230.1 | 320.8 | 313.1
2651.1 | 2457.1 | -6.4 | 0 | 0 | 200.5 | 199.4 | 190.6 | 182.8 | 217.6 | 34.6 | 19.7 | 48.8 | 5.2 | 252.1 | 14.6 | 43.9 | 76.7 | 40.5 | 47.6 | 34 | 54.9 | 67.3 | 47.9 | 81.1 | 65.2 | 337.3 | 312.1 | 301.9 | 317.7 | 263.5 | 191 | 267.1 | 229.9 | 320.6 | 313
2652.1 | 2458.1 | -6.5 | 0 | 0 | 200.5 | 199.4 | 190.6 | 182.6 | 217.5 | 34.6 | 19.7 | 48.8 | 5.4 | 260.8 | 15.4 | 43.8 | 76.9 | 40.4 | 47.6 | 34 | 56.1 | 67.7 | 48.5 | 81.1 | 65.2 | 337.2 | 311.9 | 301.7 | 317.5 | 263.3 | 190.9 | 266.9 | 229.8 | 320.3 | 312.8
2653.1 | 2459.1 | -6.4 | 0 | 0 | 200.7 | 199.4 | 190.6 | 182.6 | 217.5 | 34.6 | 19.7 | 48.8 | 4.8 | 264.4 | 16 | 43.7 | 76.8 | 40.4 | 47.5 | 34 | 56.3 | 68.4 | 49.1 | 81.1 | 65.2 | 337.1 | 311.8 | 301.6 | 317.4 | 263.1 | 190.7 | 266.7 | 229.6 | 320.1 | 312.6
2654.1 | 2460.1 | -6.3 | 0 | 0 | 200.8 | 199.2 | 190.4 | 182.5 | 217.4 | 34.6 | 19.7 | 48.8 | 4.9 | 256.3 | 14.2 | 43.6 | 76.6 | 40.4 | 47.5 | 34 | 55.6 | 69.3 | 49.7 | 81.2 | 65.3 | 336.9 | 311.7 | 301.4 | 317.2 | 263 | 190.5 | 266.5 | 229.5 | 319.9 | 312.4
2655.1 | 2461.1 | -6.4 | 0 | 0 | 200.9 | 199 | 190.2 | 182.5 | 217.2 | 34.5 | 19.7 | 48.7 | 4.2 | 241.8 | 13.4 | 43.6 | 76.6 | 40.3 | 47.4 | 33.9 | 54.9 | 69.6 | 50.1 | 81.3 | 65.3 | 336.9 | 311.5 | 301.3 | 317 | 262.8 | 190.4 | 266.4 | 229.3 | 319.7 | 312.2
2656.1 | 2462.1 | -6.4 | 0 | 0 | 200.7 | 198.8 | 190.2 | 182.5 | 217.1 | 34.5 | 19.7 | 48.7 | 4.2 | 243.9 | 13.7 | 43.6 | 76.4 | 40.3 | 47.3 | 33.9 | 54.1 | 69.8 | 50.6 | 81.3 | 65.3 | 336.7 | 311.4 | 301.1 | 316.8 | 262.7 | 190.2 | 266.2 | 229.2 | 319.4 | 312.1
2657.1 | 2463.1 | -6.6 | 0 | 0 | 200.4 | 198.4 | 190.2 | 182.4 | 217 | 34.5 | 19.7 | 48.7 | 5.6 | 253.3 | 12 | 43.5 | 76.4 | 40.2 | 47.3 | 33.8 | 53.5 | 69.4 | 51.2 | 81.3 | 65.3 | 336.6 | 311.2 | 300.9 | 316.6 | 262.5 | 190.1 | 266 | 229 | 319.2 | 311.9
2658.1 | 2464.1 | -6.6 | 0 | 0 | 200.1 | 198.3 | 190.1 | 182.2 | 216.9 | 34.4 | 19.8 | 48.6 | 5.7 | 249.7 | 11 | 43.5 | 76.3 | 40.2 | 47.2 | 33.8 | 53.5 | 69.4 | 51.9 | 81.3 | 65.3 | 336.5 | 311.1 | 300.8 | 316.4 | 262.3 | 189.9 | 265.8 | 228.8 | 319 | 311.7
2659.1 | 2465.1 | -6.5 | 0 | 0 | 199.8 | 198.2 | 189.9 | 182.1 | 216.8 | 34.3 | 19.8 | 48.6 | 5.5 | 240.2 | 10 | 43.4 | 76.2 | 40.2 | 47.2 | 33.7 | 53.1 | 69.6 | 52.5 | 81.3 | 65.3 | 336.4 | 310.9 | 300.6 | 316.2 | 262.1 | 189.7 | 265.7 | 228.7 | 318.8 | 311.6
2660.1 | 2466.1 | -6.5 | 0 | 0 | 199.5 | 198.2 | 189.8 | 181.9 | 216.6 | 34.3 | 19.8 | 48.6 | 6.2 | 250 | 10 | 43.4 | 76.3 | 40.2 | 47.1 | 33.7 | 52.3 | 69.8 | 53.2 | 81.3 | 65.3 | 336.3 | 310.8 | 300.4 | 316 | 262 | 189.6 | 265.5 | 228.5 | 318.5 | 311.4
2661.1 | 2467.1 | -6.5 | 0 | 0 | 199.2 | 198.2 | 189.7 | 181.8 | 216.6 | 34.3 | 19.8 | 48.6 | 4.5 | 246.9 | 16.4 | 43.4 | 76.4 | 40.2 | 47 | 33.7 | 53.8 | 70 | 53.8 | 81.3 | 65.3 | 336.2 | 310.6 | 300.3 | 315.9 | 261.9 | 189.4 | 265.3 | 228.4 | 318.3 | 311.2
2662.1 | 2468.1 | -6.4 | 0 | 0 | 198.7 | 198.3 | 189.6 | 181.7 | 216.5 | 34.2 | 19.8 | 48.6 | 3.7 | 244.1 | 16.5 | 43.4 | 76.1 | 40.2 | 47 | 33.6 | 55.2 | 69.6 | 54.5 | 81.3 | 65.4 | 336.1 | 310.5 | 300.1 | 315.7 | 261.7 | 189.3 | 265.1 | 228.2 | 318.1 | 311