## IS Test Matrix
Intermediate Scale Test Matrix - Revision F (12-06-06)
|  | Comments: 1) All tests were conducted as open burns with a Propene (Propylene) gas sand burner 2) Colors identify test conditions grouped into the same test run | [14 empty] | ACTUAL TEST CONDITIONS
Burn Test # | Rev. E Test # | Loc. | Cable Insulation Material | [8 empty] | Number of Conductors |  |  |  | Conductor Size (AWG) |  |  |  |  | Cable Bundle Size |  |  |  |  | Water Spary Optionsl | Raceway Type
|  |  | Thermoset | [5 empty] | Thermoplastic
|  |  | XLPE | EPR | Silicone | XLPO | TS/TP | Vita-Link | PE | PVC | Tefzel | 3 | 2 | 7 | 12 | 8 | 12 | 14 | 16 | 18 | 1 | 3 | 6 | 12 | Load Tr | * | 12" Tray | 2.5" Cnd | Air Drop
Prelim 1 | Prelim 1 | A | X | [8 empty] | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | A | X | [10 empty] | X |  |  | X |  |  |  | X | [5 empty] | X
Prelim 2 | Prelim 2 | A | X | [8 empty] | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | A | X | [10 empty] | X |  |  | X |  |  |  | X | [5 empty] | X
Prelim 3 | Prelim 3 | A | [7 empty] | X |  | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | A | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [5 empty] | X
Prelim 4 | Prelim 4 | A | [7 empty] | X |  | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | A | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [5 empty] | X
1 | 15 | A | X | [9 empty] | X | X | X |  | X |  | X | X |  |  |  |  | X |  | X
|  | B | X | [10 empty] | X |  |  | X | [6 empty] | X |  |  | X
|  | D | X | [10 empty] | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | E | X | [10 empty] | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | [10 empty] | X |  |  | X | [6 empty] | X |  |  | X
2 | 1 | A | X | [10 empty] | X |  |  | X | [6 empty] | X |  |  | X
|  | C | X | [10 empty] | X |  |  | X | [5 empty] | X |  |  |  | X
|  | A | X | [5 empty] | X |  |  |  |  | X |  |  | X | [6 empty] | X |  |  | X
|  | C | X | [5 empty] | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
| 11 | C - A | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [7 empty] | X
|  | E | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [5 empty] | X
|  | G | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [5 empty] | X
3 | 2 | A | X | X | [9 empty] | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X | [9 empty] | X |  |  | X | [5 empty] | X |  |  |  | X
| 3 | A |  | X |  |  |  |  | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C |  | X |  |  |  |  | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
| 10 | E | [7 empty] | X |  | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | [7 empty] | X |  | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
4 | 5 | A | X | X |  | X | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X |  | X | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
| 6 | A | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
| 9 | C - A | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [7 empty] | X
|  | E | X | [8 empty] | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | [8 empty] | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
5 | 4 | A | X | X | X | X |  |  | X |  | X |  |  | X |  |  | X | [6 empty] | X |  | X | X
|  | C | X | X | X | X |  |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
| 7 | A | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | X | [5 empty] | X |  | X | X
|  | C | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | X |  |  |  |  | X |  |  | X | X
|  | C - A | X | [10 empty] | X |  |  | X |  |  |  | X | [7 empty] | X
|  | E |  | X | [9 empty] | X |  |  | X |  |  |  | X | [5 empty] | X
|  | G |  | X | [9 empty] | X |  |  | X |  |  |  | X | [5 empty] | X
6 | 12 | A | X | X | X | X |  |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | C | X | X | X | X |  |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | E | X | [5 empty] | X |  | X |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
| 13 | C - A | X | [5 empty] | X |  | X |  |  | X |  |  | X |  |  |  |  | X | [6 empty] | X
|  | A |  | X | X | X | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | C |  | X | X | X | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | G |  |  |  |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  |  |  | X
7 | 14 | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | A | X | X |  | X | X |  |  | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C |  | X |  | X | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | E | X | [5 empty] | X | X |  |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G |  | X |  | X | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
8 | 16 | A | X | [5 empty] | X | X |  |  | X | X | X |  | X |  | X | X |  |  | X |  |  |  | X
|  | A | X | [5 empty] | X | X |  |  | X | X | X |  | X |  | X | X |  |  | X |  |  |  | X
|  | C | X | [5 empty] | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | E | X | [5 empty] | X |  |  |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | [5 empty] | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
9 | 19 | A | X | X | X |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | A | X | X | X |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | C | X | X | X |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | E | X | [5 empty] | X |  | X |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | X | X |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
10 | 20 | A | X | X | X | X | X |  |  |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | A | X | X | X | X | X |  |  |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | C | X | X | X | X | X |  |  | X |  |  |  | X | X |  | X |  |  | X |  |  | X |  |  | X | X
|  | E |  |  |  |  | X |  | X |  | X |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | X |  |  | X |  | X | X | X |  | X | X |  |  | X |  | X |  |  |  | X |  |  |  | X
11 | 21 | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X |  | X | X |  |  | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | E |  |  |  |  | X |  | X | X |  |  |  | X |  |  | X |  |  |  |  | X | [6 empty] | X
|  | G | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
12 | 24 | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X |  | X | X |  |  | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | E |  |  |  |  | X |  | X | X |  |  |  | X |  |  | X |  |  |  |  | X | [6 empty] | X
|  | G | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
13 | 25 | A | X | X |  | X | X | X | X |  | X |  |  | X |  |  | X | [7 empty] | X | X | X
|  | C | X | X |  | X | X | X | X |  | X |  |  | X |  |  | X | [7 empty] | X | X | X
|  | E | X | X | [9 empty] | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | F | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | F | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | G | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | G | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
14 | 27 | A | X | X |  | X | X |  | X | X | X |  |  | X |  |  | X | [7 empty] | X |  | X
|  | C | X | X |  | X | X |  | X | X | X |  |  | X |  |  | X | [7 empty] | X |  | X
|  | E |  |  |  |  | X |  | X | X |  |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | F | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | F | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | G | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | G | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X

## Shorting Summary
Shorting Sequence for Open Burn Test 8, Location C, IRMS #2
Test conditions: Cable: Bundle of 6, 7-conductor, 12 AWG, XLPE & PE control cables (Items 10 & 15). Cable specimens present: Six lengths of cable were monitored for electrical performance (A, B, C, D, E, & F [See Elect. Conn. Map]), a second bundle of 6 cables was monitored for temperature response. Raceway: 12" B-Line Series 2 tray (part number 248P09-12-144) located at position C in the Test Cell chamber with chamber end walls open and un-heated. Exposure conditions: Gas burner flow rate set to a nominal 150 kW heat release rate and increased to ~300 kW during the test. Electrical repsonse monitoring: IRMS system using 12 channels - two for each cable (see electrical connection map), cable tray was grounded. Thermal response monitoring: Four cable bundle temperatures (see thermocouple map) and the cable tray rung temperature. Gas burner initiated: Following 219 seconds of baseline data monitoring. Special Note: This test was run with the bunker door open and a fan in the exhaust stack pulling the smoke/air mixture out from inside the bunker. The forced air blower was off.
DAQ Time | Burner Time | Event | Interpretation
219 | 0 | Ignited Gas Burner
876 | 657 | Conductor E9 shorts to ground at less than 100 ohms (16)
1064 | 845 | Conductor E10 shorts to ground at less than 100 ohms (8) | Cable E shorts to ground
1092 | 873 | Conductors E9 & E10 short together at less than 100 ohms (1) | Cable E shorted internally
1228 | 1009 | Conductor D7 shorts to ground at less than 1000 ohms (222)
1252 | 1033 | Conductors D7 & D8 short together at less than 1000 ohms (279) | Cable D shorted internally
1266-1268 | 1047-1049 | Conductors F11 & F12 short to ground (85 & 563) | Cable F shorts to ground
1291 | 1072 | Conductors F11 & F12 short together at less than 1000 ohms (756) | Cable F shorted internally
1412-1418 | 1193-1199 | The existing ground fault on conductor D7 decreases to less than 100 ohms (1) and conductor D8 shorts to ground at less than 100 ohms (4) | Cable D shorts to ground
1453 | 1234 | The existing ground fault on conductor F12 decreases to less than 100 ohms (2)
1564-1573 | 1345-1354 | Conductors C5 & C6 both short to ground (31 & 324) | Cable C shorts to ground
1661 | 1442 | The existing internal fault between conductors F11 & F12 decreases to less than 100 ohms (13)
1663 | 1444 | Conductors A1 & A2 short together at less than 100 ohms (39) | Cable A shorted internally
1669-1691 | 1450-1472 | Conductors A1 & A2 both short to ground (114 & 88) | Cable A shorts to ground
1719-1735 | 1500-1516 | Conductors B3 & B4 both short to ground at less than 100 ohms (29 & 39) | Cable B shorts to ground
1758 | 1539 | The existing ground fault on conductor C6 decreases to less than 100 ohms (22)
1806 | 1587 | The existing internal fault between conductors D7 & D8 decreases to less than 100 ohms (9)
1854 | 1635 | The existing ground fault on conductor A1 decreases to less than 100 ohms (17)
1906 | 1687 | Conductors B3 & B4 short together at less than 1000 ohms (831) | Cable B shorted internally
1955 | 1736 | Conductors C5 & C6 short together at less than 100 ohms (22) | Cable C shorted internally
2092 | 1873 | The existing internal fault between conductors B3 & B4 decreases to less than 100 ohms (18)
2257 | 2038 | Gas burner is shut off
Additional Observations
Observation 1 | The progression of cable failure generally started with the bottom cables and worked up to the top cable group during the test.
Observation 2 | No cable to cable interactions were observed during this test.

## Thermocouple Map
Thermocouple map for TC's on and within the cable
|  |  |  | Cable A = | XLPE (7/C) | (Item #10)
|  |  |  | Cable B = | PE (7/C) | (Item #15)
|  |  |  | Cable C = | PE (7/C) | (Item #15)
|  |  |  | Cable D = | XLPE (7/C) | (Item #10)
|  |  |  | Cable E = | PE (7/C) | (Item #15)
|  |  |  | Cable F = | XLPE (7/C) | (Item #10)
Translation to data file names used in "PenTemps" WorkSheet:
| Map Name |  | Location
| C1 | = | Center of bundle, under jacket
| C2 | = | Air above bundle
| C3 | = | Air below bundle
| C4 | = | Intra-bundle, center

## Elect Conn Map
Electrical connection map within the cables
|  |  |  | Cable A = | XLPE (7/C) | (Item #10)
|  |  |  | Cable B = | PE (7/C) | (Item #15)
|  |  |  | Cable C = | PE (7/C) | (Item #15)
|  |  |  | Cable D = | XLPE (7/C) | (Item #10)
|  |  |  | Cable E = | PE (7/C) | (Item #15)
|  |  |  | Cable F = | XLPE (7/C) | (Item #10)
Cable tray rung below D-E-F
Cable Bundle Arrangement
Cable 7-Conductor Arrangement
| Lt Blue = | Even conductor set
| Lt Red = | Odd conductor set
| Gray = | Center conductor (not connected)
IRMS Electrical Connections

## C-C Individuals
Conductor to Conductor Resistances
Open Burn Test 8 |  |  | 2006-11-10 | 13:06
Mix | 7-C | Tray C | IRMS | 2
0 | 150 kW
Burner Time | A1-A2 | Burner Time | A1-B3 | Burner Time | A1-B4 | Burner Time | A1-C5 | Burner Time | A1-C6 | Burner Time | A2-B3 | Burner Time | A2-B4 | Burner Time | A2-C5 | Burner Time | A2-C6 | Burner Time | B3-B4 | Burner Time | B3-C5 | Burner Time | B3-C6 | Burner Time | B3-D7 | Burner Time | B3-D8 | Burner Time | B3-E9 | Burner Time | B3-E10 | Burner Time | B4-C5 | Burner Time | B4-C6 | Burner Time | B4-D7 | Burner Time | B4-D8 | Burner Time | B4-E9 | Burner Time | B4-E10 | Burner Time | C5-C6 | Burner Time | C5-E9 | Burner Time | C5-E10 | Burner Time | C5-F11 | Burner Time | C5-F12 | Burner Time | C6-E9 | Burner Time | C6-E10 | Burner Time | C6-F11 | Burner Time | C6-F12 | Burner Time | D7-D8 | Burner Time | D7-E9 | Burner Time | D7-E10 | Burner Time | D8-E9 | Burner Time | D8-E10 | Burner Time | E9-E10 | Burner Time | E9-F11 | Burner Time | E9-F12 | Burner Time | E10-F11 | Burner Time | E10-F12 | Burner Time | F11-F12
-218.5 | 498775.9997 | -216 | 507975.9997 | -213 | 492575.9997 | -210.5 | 514775.9997 | -207.5 | 474775.9997 | -188 | 519775.9997 | -185 | 511175.9997 | -182.5 | 497775.9997 | -179.5 | 519775.9997 | -160 | 512975.9997 | -157 | 511575.9997 | -154.5 | 500575.9997 | -151.5 | 515775.9997 | -148.5 | 512175.9997 | -146 | 517575.9997 | -143 | 524375.9997 | -134.5 | 513775.9997 | -132 | 520775.9997 | -129 | 516175.9997 | -126.5 | 507975.9997 | -123.5 | 523575.9997 | -120.5 | 520575.9997 | -112.5 | 515175.9997 | -104 | 526175.9997 | -101 | 520575.9997 | -98.5 | 507375.9997 | -95.5 | 521575.9997 | -87 | 518775.9997 | -84.5 | 517775.9997 | -81.5 | 523975.9997 | -78.5 | 503975.9997 | -76 | 512775.9997 | -73 | 490575.9997 | -70.5 | 520975.9997 | -62 | 519175.9997 | -59 | 516975.9997 | -50.5 | 523975.9997 | -48 | 525775.9997 | -45 | 525175.9997 | -42.5 | 508575.9997 | -39.5 | 525575.9997 | -36.5 | 518175.9997
-34 | 498775.9997 | -31 | 507975.9997 | -28.5 | 492575.9997 | -25.5 | 514775.9997 | -22.5 | 474775.9997 | -3.5 | 519775.9997 | -0.5 | 511175.9997 | 2.5 | 497775.9997 | 5.5 | 519775.9997 | 24.5 | 512975.9997 | 27.5 | 511575.9997 | 30.5 | 500575.9997 | 33 | 515775.9997 | 36 | 512175.9997 | 39 | 517575.9997 | 41.5 | 524375.9997 | 50 | 513775.9997 | 52.5 | 520775.9997 | 55.5 | 516175.9997 | 58.5 | 507975.9997 | 61 | 523575.9997 | 64 | 520575.9997 | 72.5 | 515175.9997 | 81 | 526175.9997 | 83.5 | 520575.9997 | 86.5 | 253538.0296 | 89 | 521575.9997 | 97.5 | 518775.9997 | 100.5 | 517775.9997 | 103.5 | 523975.9997 | 106 | 503975.9997 | 109 | 512775.9997 | 111.5 | 490575.9997 | 114.5 | 520975.9997 | 123 | 519175.9997 | 125.5 | 516975.9997 | 134 | 523975.9997 | 137 | 525775.9997 | 139.5 | 525175.9997 | 142.5 | 508575.9997 | 145.5 | 525575.9997 | 148 | 518175.9997
151 | 498775.9997 | 153.5 | 507975.9997 | 156.5 | 492575.9997 | 159.5 | 514775.9997 | 162 | 474775.9997 | 181.5 | 519775.9997 | 184.5 | 511175.9997 | 187 | 497775.9997 | 190 | 519775.9997 | 209.5 | 512975.9997 | 212.5 | 511575.9997 | 215 | 500575.9997 | 218 | 515775.9997 | 220.5 | 512175.9997 | 223.5 | 517575.9997 | 226.5 | 524375.9997 | 234.5 | 513775.9997 | 237.5 | 520775.9997 | 240.5 | 516175.9997 | 243 | 507975.9997 | 246 | 523575.9997 | 248.5 | 520575.9997 | 257 | 515175.9997 | 265.5 | 526175.9997 | 268.5 | 520575.9997 | 271 | 507375.9997 | 274 | 521575.9997 | 282.5 | 518775.9997 | 285 | 517775.9997 | 288 | 261838.0286 | 291 | 503975.9997 | 293.5 | 512775.9997 | 296.5 | 490575.9997 | 299.5 | 520975.9997 | 307.5 | 519175.9997 | 310.5 | 516975.9997 | 318.5 | 523975.9997 | 321.5 | 525775.9997 | 324.5 | 525175.9997 | 327 | 508575.9997 | 330 | 525575.9997 | 332.5 | 518175.9997
335.5 | 498775.9997 | 338.5 | 507975.9997 | 341 | 492575.9997 | 344 | 514775.9997 | 346.5 | 474775.9997 | 366.5 | 519775.9997 | 369 | 511175.9997 | 372 | 497775.9997 | 374.5 | 519775.9997 | 394.5 | 512975.9997 | 397 | 511575.9997 | 400 | 500575.9997 | 402.5 | 515775.9997 | 405.5 | 512175.9997 | 408.5 | 517575.9997 | 411 | 524375.9997 | 419.5 | 513775.9997 | 422.5 | 520775.9997 | 425 | 516175.9997 | 428 | 507975.9997 | 430.5 | 523575.9997 | 433.5 | 520575.9997 | 442 | 515175.9997 | 450.5 | 526175.9997 | 453 | 520575.9997 | 456 | 507375.9997 | 458.5 | 521575.9997 | 467 | 518775.9997 | 470 | 517775.9997 | 472.5 | 523975.9997 | 475.5 | 503975.9997 | 478.5 | 512775.9997 | 481.5 | 490575.9997 | 484 | 520975.9997 | 492.5 | 519175.9997 | 495 | 516975.9997 | 503.5 | 523975.9997 | 506.5 | 525775.9997 | 509 | 525175.9997 | 512 | 508575.9997 | 514.5 | 525575.9997 | 517.5 | 518175.9997
520.5 | 498775.9997 | 523 | 507975.9997 | 526 | 492575.9997 | 528.5 | 514775.9997 | 531.5 | 474775.9997 | 551 | 519775.9997 | 554 | 511175.9997 | 556.5 | 497775.9997 | 559.5 | 519775.9997 | 579 | 512975.9997 | 582 | 511575.9997 | 585 | 500575.9997 | 587.5 | 515775.9997 | 590.5 | 512175.9997 | 593 | 517575.9997 | 596 | 524375.9997 | 604.5 | 513775.9997 | 607 | 520775.9997 | 610 | 516175.9997 | 612.5 | 507975.9997 | 615.5 | 523575.9997 | 618.5 | 520575.9997 | 626.5 | 515175.9997 | 635 | 526175.9997 | 638 | 520575.9997 | 640.5 | 507375.9997 | 643.5 | 521575.9997 | 652 | 518775.9997 | 654.5 | 517775.9997 | 657.5 | 523975.9997 | 660.5 | 503975.9997 | 663 | 512775.9997 | 666 | 490575.9997 | 668.5 | 520975.9997 | 677 | 519175.9997 | 680 | 516975.9997 | 688.5 | 130918.9988 | 691 | 30473.5374 | 694 | 47696.4026 | 696.5 | 508575.9997 | 699.5 | 525575.9997 | 702.5 | 518175.9997
705 | 498775.9997 | 708 | 507975.9997 | 710.5 | 492575.9997 | 713.5 | 514775.9997 | 716.5 | 474775.9997 | 736 | 519775.9997 | 738.5 | 511175.9997 | 741.5 | 497775.9997 | 744.5 | 519775.9997 | 764 | 512975.9997 | 766.5 | 511575.9997 | 769.5 | 500575.9997 | 772.5 | 515775.9997 | 775 | 512175.9997 | 778 | 517575.9997 | 780.5 | 524375.9997 | 789 | 513775.9997 | 792 | 520775.9997 | 794.5 | 516175.9997 | 797.5 | 507975.9997 | 800.5 | 523575.9997 | 803 | 520575.9997 | 811.5 | 515175.9997 | 820 | 526175.9997 | 822.5 | 520575.9997 | 825.5 | 507375.9997 | 828.5 | 521575.9997 | 836.5 | 518775.9997 | 839.5 | 517775.9997 | 842.5 | 523975.9997 | 845 | 503975.9997 | 848 | 512775.9997 | 850.5 | 490575.9997 | 853.5 | 520975.9997 | 862 | 519175.9997 | 864.5 | 516975.9997 | 873 | 0.86917 | 876 | 61226.355 | 878.5 | 32.4584 | 881.5 | 21733.7266 | 884.5 | 14.1957 | 887 | 125380.8835
890 | 498775.9997 | 892.5 | 507975.9997 | 895.5 | 492575.9997 | 898.5 | 514775.9997 | 901 | 474775.9997 | 920.5 | 519775.9997 | 923.5 | 511175.9997 | 926.5 | 497775.9997 | 929 | 519775.9997 | 948.5 | 512975.9997 | 951.5 | 511575.9997 | 954.5 | 500575.9997 | 957 | 515775.9997 | 960 | 512175.9997 | 962.5 | 517575.9997 | 965.5 | 524375.9997 | 974 | 513775.9997 | 976.5 | 520775.9997 | 979.5 | 516175.9997 | 982.5 | 507975.9997 | 985 | 523575.9997 | 988 | 520575.9997 | 996.5 | 515175.9997 | 1004.5 | 526175.9997 | 1007.5 | 520575.9997 | 1010.5 | 507375.9997 | 1013 | 521575.9997 | 1021.5 | 518775.9997 | 1024 | 517775.9997 | 1027 | 523975.9997 | 1030 | 503975.9997 | 1032.5 | 279.2142 | 1035.5 | 221.0781 | 1038.5 | 883.0005 | 1046.5 | 259537.9994 | 1049.5 | 258437.9994 | 1058 | 13.181 | 1060.5 | 3.3086 | 1063.5 | 31.8435 | 1066 | 29.3744 | 1069 | 8.0044 | 1071.5 | 756.4327
1074.5 | 498775.9997 | 1077.5 | 507975.9997 | 1080.5 | 492575.9997 | 1083 | 514775.9997 | 1086 | 474775.9997 | 1105.5 | 519775.9997 | 1108.5 | 511175.9997 | 1111 | 497775.9997 | 1114 | 519775.9997 | 1133.5 | 512975.9997 | 1136.5 | 511575.9997 | 1139 | 500575.9997 | 1142 | 515775.9997 | 1144.5 | 512175.9997 | 1147.5 | 517575.9997 | 1150 | 524375.9997 | 1158.5 | 513775.9997 | 1161.5 | 520775.9997 | 1164.5 | 516175.9997 | 1167 | 507975.9997 | 1170 | 523575.9997 | 1172.5 | 520575.9997 | 1181 | 515175.9997 | 1189.5 | 526175.9997 | 1192.5 | 520575.9997 | 1195 | 507375.9997 | 1198 | 521575.9997 | 1206.5 | 518775.9997 | 1209 | 517775.9997 | 1211.5 | 523975.9997 | 1214.5 | 503975.9997 | 1217.5 | 2267.4701 | 1220 | 0.26781 | 1223 | 27.3604 | 1231.5 | 2.7521 | 1234 | 9.8282 | 1242.5 | 17.8747 | 1245.5 | 5.1637 | 1248 | 15.4069 | 1251 | 2.1869 | 1253.5 | 21.1103 | 1256.5 | 926.6061
1259.5 | 3737.6707 | 1262 | 507975.9997 | 1265 | 492575.9997 | 1267.5 | 514775.9997 | 1270.5 | 474775.9997 | 1290.5 | 519775.9997 | 1293 | 511175.9997 | 1296 | 497775.9997 | 1298.5 | 519775.9997 | 1318.5 | 512975.9997 | 1321 | 511575.9997 | 1324 | 500575.9997 | 1326.5 | 515775.9997 | 1329.5 | 512175.9997 | 1332.5 | 517575.9997 | 1335 | 524375.9997 | 1343.5 | 513775.9997 | 1346.5 | 520775.9997 | 1349 | 516175.9997 | 1351.5 | 507975.9997 | 1354.5 | 523575.9997 | 1357.5 | 520575.9997 | 1365.5 | 2895.7382 | 1374 | 48.8648 | 1377 | 64.6497 | 1379.5 | 30.0863 | 1382.5 | 49.2797 | 1391 | 1032.7772 | 1393.5 | 1876.546 | 1396.5 | 410.4821 | 1399.5 | 323.23 | 1402 | 2503.3928 | 1405 | 0.60563 | 1408 | 7.6915 | 1416.5 | 12.7885 | 1419 | 5.6257 | 1427.5 | 8.8348 | 1430 | 29.2602 | 1433 | 2.725 | 1435.5 | 0.91586 | 1438.5 | 27.6605 | 1441.5 | 12.5179
1444 | 38.5835 | 1447 | 113.1114 | 1449.5 | 163.7422 | 1452.5 | 1736.4929 | 1455.5 | 91.3965 | 1475 | 87.108 | 1477.5 | 106.0723 | 1480.5 | 461.7734 | 1483 | 273.8889 | 1503 | 4471.7612 | 1505.5 | 32.0768 | 1508.5 | 27.7887 | 1511.5 | 32.5383 | 1514.5 | 60.0205 | 1517 | 56.1518 | 1519.5 | 58.6062 | 1528.5 | 41.4848 | 1531 | 51.3487 | 1534 | 48.767 | 1536.5 | 42.3621 | 1539.5 | 37.4587 | 1542.5 | 41.6945 | 1550.5 | 4731.3949 | 1559 | 31.5539 | 1561.5 | 38.4528 | 1564.5 | 7.8104 | 1567.5 | 26.3637 | 1575.5 | 34.5221 | 1578.5 | 27.5978 | 1581.5 | 45.8761 | 1584 | 20.6127 | 1587 | 8.5411 | 1589.5 | 0.81565 | 1592.5 | 0.0083349 | 1601 | 20.1919 | 1603.5 | 29.4325 | 1612 | 29.1401 | 1615 | 11.6722 | 1618 | 27.435 | 1620.5 | 9.0803 | 1623.5 | 18.8468 | 1626 | 15.3735
1629 | 59.2043 | 1631.5 | 40.9878 | 1634.5 | 51.831 | 1637.5 | 6145.943 | 1640 | 15.4928 | 1659.5 | 16.5396 | 1662.5 | 30.9313 | 1665.5 | 90.6971 | 1668 | 65.46 | 1687.5 | 830.6214 | 1690.5 | 19.4416 | 1693.5 | 3.7759 | 1696 | 4.3987 | 1699 | 18.3842 | 1701.5 | 22.1523 | 1704.5 | 36.3491 | 1713 | 12.6672 | 1715.5 | 3.9325 | 1718.5 | 21.9372 | 1721.5 | 2.1075 | 1724 | 18.7226 | 1727 | 15.7007 | 1735.5 | 21.8768 | 1743.5 | 14.6374 | 1746.5 | 3.7192 | 1749.5 | 0.072244 | 1752 | 14.868 | 1760.5 | 13033.6521 | 1763.5 | 15.2303 | 1766 | 22.1321 | 1769 | 9.6937 | 1771.5 | 2.1853 | 1774.5 | 14.8744 | 1777.5 | 0.90051 | 1785.5 | 18.3241 | 1788.5 | 6.4869 | 1797 | 0.15018 | 1799.5 | 11.3774 | 1802.5 | 29.1766 | 1805.5 | 0.89454 | 1808 | 12.0244 | 1811 | 23.3157
1813.5 | 59.5344 | 1816.5 | 11.583 | 1819.5 | 11.0423 | 1822 | 5.1252 | 1825 | 5.7942 | 1844.5 | 18.0174 | 1847.5 | 21.9923 | 1850 | 0.84741 | 1853 | 15.2027 | 1872.5 | 18.4014 | 1875.5 | 11.7722 | 1878 | 2.4471 | 1881 | 3.8723 | 1883.5 | 15.1368 | 1886.5 | 28.3943 | 1889.5 | 3.4968 | 1897.5 | 28.8895 | 1900.5 | 20.1068 | 1903.5 | 10.1422 | 1906 | 2.0218 | 1909 | 18.5559 | 1911.5 | 0.27015 | 1920 | 26.7581 | 1928.5 | 31.0153 | 1931.5 | 29.4095 | 1934 | 0.072244 | 1937 | 0.95047 | 1945.5 | 3.7871 | 1948 | 0.93421 | 1951 | 23.558 | 1953.5 | 22.7939 | 1956.5 | 15.3269 | 1959.5 | 17.7801 | 1962 | 16.7575 | 1970.5 | 24.043 | 1973.5 | 0.93077 | 1981.5 | 6.6669 | 1984.5 | 0.96837 | 1987.5 | 30.898 | 1990 | 17.8245 | 1993 | 28.0446 | 1995.5 | 0.88152
1998.5 | 18.7106 | 2001.5 | 26.8321 | 2004 | 2.5822 | 2007 | 25.0747 | 2009.5 | 10.12 | 2029.5 | 26.809 | 2032 | 16.0977 | 2035 | 20.783 | 2037.5 | 5.1753 | 2057.5 | 21.3509 | 2060 | 0.90752 | 2063 | 23.1317 | 2065.5 | 12.9569 | 2068.5 | 16.0003 | 2071.5 | 26.3941 | 2074 | 14.6548 | 2082.5 | 14.6998 | 2085.5 | 21.1453 | 2088 | 29.7647 | 2091 | 28.4146 | 2093.5 | 25.1047 | 2096.5 | 12.6395 | 2105 | 12.6194 | 2113.5 | 0.056339 | 2116 | 25.9933 | 2119 | 15.6052 | 2121.5 | 3.5766 | 2130 | 26.1824 | 2133 | 12.6838 | 2135.5 | 0.23044 | 2138.5 | 0.05191 | 2141.5 | 21.0668 | 2144 | 9.2077 | 2147 | 15.4188 | 2155.5 | 28.0759 | 2158 | 0.48062 | 2166.5 | 21.257 | 2169.5 | 15.0688 | 2172 | 0.96582 | 2175 | 0.12045 | 2177.5 | 10.7982 | 2180.5 | 4.1874
2183.5 | 8306.7874 | 2186 | 0.89193 | 2189 | 0.61533 | 2191.5 | 22.9812 | 2194.5 | 0.7449 | 2214 | 22.379 | 2217 | 26.4691 | 2219.5 | 22.3742 | 2222.5 | 8.2316 | 2242 | 350.7412 | 2245 | 25.9916 | 2247.5 | 2.7102 | 2250.5 | 20.8988 | 2253.5 | 30.7083 | 2256 | 1.9669 | 2259 | 32.4607 | 2267.5 | 21.9588 | 2270 | 31.2028 | 2273 | 28.7664 | 2275.5 | 17.6276 | 2278.5 | 15.1036 | 2281.5 | 0.49593 | 2289.5 | 919.1713 | 2298 | 8.1756 | 2301 | 9.3952 | 2303.5 | 6.0753 | 2306.5 | 2.2613 | 2315 | 21.3159 | 2317.5 | 9.565 | 2320.5 | 26.3833 | 2323 | 10.0417 | 2326 | 217.379 | 2328.5 | 15.9406 | 2331.5 | 11.6245 | 2340 | 4.8752 | 2342.5 | 0.65153 | 2351.5 | 25.883 | 2354 | 1.8443 | 2356.5 | 0.29572 | 2359.5 | 25.5002 | 2362.5 | 13409.2705 | 2365.5 | 9.9408
2368 | 519.1456 | 2371 | 10.4254 | 2373.5 | 3.5258 | 2376.5 | 5.3944 | 2379 | 134.1708 | 2399 | 4864.1339 | 2401.5 | 8239.6351 | 2404.5 | 433.6744 | 2407.5 | 26.3647 | 2427 | 2943.8317 | 2429.5 | 16.9587 | 2432.5 | 4634.0989 | 2435.5 | 95.1527 | 2438 | 12975.6055 | 2441 | 29.5175 | 2443.5 | 36.7137 | 2452 | 1.6678 | 2454.5 | 4469.6014 | 2457.5 | 3661.9593 | 2460.5 | 666.7092 | 2463.5 | 10.808 | 2466 | 3.3751 | 2474.5 | 175.3101 | 2482.5 | 32.4384 | 2485.5 | 5.7409 | 2488.5 | 25.7762 | 2491.5 | 33.5484 | 2499.5 | 24.3752 | 2502.5 | 4.2808 | 2505.5 | 4.5803 | 2508 | 19.0255 | 2511 | 387.574 | 2513.5 | 10.5344 | 2516.5 | 24.2937 | 2524.5 | 34.2694 | 2527.5 | 22.0687 | 2536 | 2.1109 | 2539 | 25.4503 | 2541.5 | 1.2339 | 2544.5 | 22.2074 | 2547.5 | 16.077 | 2550 | 0.93592
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!

## C-G Min
Minimum Conductor to Ground Resistances
Open Burn Test 8 |  |  | 2006-11-10 | 13:06
Mix | 7-C | Tray C | IRMS | 2
0 | 150 kW
Burner Time | A1-G |  | Burner Time | A2-G | Burner Time | B3-G | Burner Time | B4-G | Burner Time | C5-G | Burner Time | C6-G | Burner Time | D7-G | Burner Time | D8-G | Burner Time | E9-G | Burner Time | E10-G | Burner Time | F11-G | Burner Time | F12-G
-213.1 | 474776 |  | -190.7 | 497776 | -162.7222 | 500576 | -147.1111 | 492576 | -132.8889 | 497776 | -124.1667 | 474776 | -100 | 490576 | -94.4 | 507976 | -82.1111 | 259338 | -79 | 508576 | -61.4 | 507376 | -59 | 503976
-28.3 | 474776 |  | -6 | 497776 | 21.9444 | 500576 | 37.4444 | 492576 | 51.8889 | 497776 | 60.6667 | 474776 | 84.7 | 490576 | 90.4 | 507976 | 102.6111 | 490576 | 105.7222 | 508576 | 123.5 | 507376 | 125.6 | 503976
156.5 | 474776 |  | 178.8 | 497776 | 206.7222 | 500576 | 222.2778 | 492576 | 236.6111 | 497776 | 245.3333 | 474776 | 269.6 | 490576 | 275 | 507976 | 287.3333 | 490576 | 290.4444 | 508576 | 308 | 507376 | 310.4 | 503976
341.1 | 474776 |  | 363.5 | 497776 | 391.5556 | 500576 | 407.0556 | 492576 | 421.3889 | 497776 | 430.0556 | 474776 | 454.3 | 490576 | 459.9 | 507976 | 472.1667 | 490576 | 475.1667 | 508576 | 492.9 | 507376 | 495 | 503976
525.9 | 474776 |  | 548.3 | 497776 | 576.3333 | 500576 | 591.8889 | 492576 | 606.1111 | 497776 | 614.8889 | 474776 | 639 | 490576 | 644.6 | 507976 | 656.8889 | 16.4363 | 660 | 508576 | 677.6 | 507376 | 680 | 211070.4326
710.7 | 474776 |  | 733.1 | 497776 | 761.1111 | 500576 | 776.6111 | 492576 | 790.9444 | 497776 | 799.7222 | 474776 | 823.8 | 490576 | 829.4 | 507976 | 841.6667 | 5.7523 | 844.7222 | 8.4751 | 862.5 | 276872.3418 | 864.7 | 3104.9348
895.5 | 474776 |  | 917.9 | 497776 | 945.8333 | 500576 | 961.4444 | 492576 | 975.8333 | 497776 | 984.4444 | 474776 | 1008.6 | 221.5439 | 1014.2 | 1120.6159 | 1026.3889 | 2.5447 | 1029.5556 | 1.8537 | 1047.1 | 85.3534 | 1049.4 | 562.7711
1080.3 | 474776 |  | 1102.7 | 497776 | 1130.6667 | 500576 | 1146.2778 | 492576 | 1160.5556 | 497776 | 1169.2222 | 474776 | 1193.4 | 1.212 | 1198.9 | 4.2723 | 1211.2222 | 0.63488 | 1214.2222 | 3.6845 | 1231.9 | 2.6799 | 1234.1 | 1.6282
1264.9 | 6205.0831 |  | 1287.5 | 2470.4372 | 1315.5 | 500576 | 1331 | 492576 | 1345.1667 | 31.2664 | 1353.9444 | 323.5933 | 1378.1 | 0.87911 | 1383.7 | 5.3566 | 1396 | 3.0453 | 1399.0556 | 0.63317 | 1416.6 | 5.2594 | 1419 | 2.2734
1449.7 | 113.8367 |  | 1472 | 87.8819 | 1500.1667 | 28.9737 | 1515.7778 | 38.612 | 1530 | 9.2286 | 1538.6667 | 21.8752 | 1562.9 | 0.67214 | 1568.5 | 2.3733 | 1580.7222 | 2.0413 | 1583.7778 | 4.9372 | 1601.5 | 0.62903 | 1603.8 | 1.1313
1634.5 | 16.7345 |  | 1656.9 | 17.8857 | 1684.8333 | 5.2282 | 1700.4444 | 3.6044 | 1714.8333 | 0.6416 | 1723.5 | 2.1788 | 1747.6 | 0.6386 | 1753.2 | 0.96098 | 1765.3889 | 0.62639 | 1768.6667 | 0.62903 | 1786.3 | 7.2778 | 1788.5 | 2.8318
1819.3 | 6.5996 |  | 1841.7 | 0.66235 | 1869.7222 | 3.9178 | 1885.2778 | 1.2988 | 1899.5556 | 0.63194 | 1908.2778 | 0.63661 | 1932.5 | 0.63909 | 1938 | 0.6376 | 1950.3333 | 0.62687 | 1953.3889 | 6.8226 | 1971 | 2.4261 | 1973.3 | 4.1049
2004.1 | 4.0279 |  | 2026.5 | 6.6631 | 2054.5556 | 0.63415 | 2070.0556 | 0.64488 | 2084.3889 | 0.64034 | 2093.0556 | 0.63292 | 2117.2 | 10.5624 | 2122.9 | 0.64897 | 2135.1111 | 0.62759 | 2138.1667 | 1.4107 | 2155.9 | 3.6511 | 2158 | 0.62711
2188.9 | 0.64897 |  | 2211.3 | 9.6785 | 2239.2778 | 0.64371 | 2254.8889 | 2.0533 | 2269.1111 | 3.7955 | 2277.7778 | 1.5548 | 2301.9 | 13.0317 | 2307.5 | 0.64465 | 2319.7778 | 1.0297 | 2322.9444 | 2.0917 | 2340.6 | 0.64974 | 2342.8 | 17.1445
2373.6 | 4.9587 |  | 2396.1 | 12.3754 | 2424.1111 | 10.3771 | 2439.5556 | 3.188 | 2453.8889 | 1.655 | 2462.6111 | 0.78445 | 2486.8 | 2.0324 | 2492.3 | 4.4994 | 2504.5556 | 2.7937 | 2507.7222 | 0.62855 | 2525.5 | 0.63612 | 2527.7 | 0.65415
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!

## F11-F12
Open Burn Test 8 |  |  | 2006-11-10 | 13:06 |  |  | Vs = |  | 158.2039 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 150 kW |  | Bundle | Ch. 11 & 12 | Cable F | Odd -Even
Time-131 | N11 | N12 | Time-132 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R11-G | R12-G | R11-12
39031.5427 | 0 | 0 | 39031.5427 | 0 | 0 |  | -36.5 | 182.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518176 | 518176 | 518175.9997
39031.5448 | 0 | 0 | 39031.5448 | 0 | 0 |  | 148 | 367 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518176 | 518176 | 518175.9997
39031.547 | 0 | 0 | 39031.547 | 0 | 0 |  | 332.5 | 551.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518176 | 518176 | 518175.9997
39031.5491 | 0 | 0 | 39031.5491 | 0 | 0 |  | 517.5 | 736.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518176 | 518176 | 518175.9997
39031.5512 | 0 | 0 | 39031.5512 | 0 | 0 |  | 702.5 | 921.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518176 | 518176 | 518175.9997
39031.5534 | 1 | 2 | 39031.5534 | 736 | 676 |  | 887 | 1106 | 0.06105 | 0.1221 | 44.9328 | 41.2698 | 0.0006105 | 0.001221 | 0.44933 | 0.4127 | 0.0006105 | 0.03663 | 276872.3418 | 3104.9348 | 125380.8835
39031.5555 | 1442 | 116 | 39031.5555 | 333 | 398 |  | 1071.5 | 1290.5 | 88.0342 | 7.0818 | 20.3297 | 24.2979 | 0.88034 | 0.070818 | 0.2033 | 0.24298 | 0.80952 | 0.039683 | 85.3534 | 562.7711 | 756.4327
39031.5577 | 2235 | 1 | 39031.5577 | 2524 | 1 |  | 1256.5 | 1475.5 | 136.4469 | 0.06105 | 154.0904 | 0.06105 | 1.3645 | 0.0006105 | 1.5409 | 0.0006105 | 1.3639 | 1.5403 | 16.2238 | 2.6772 | 926.6061
39031.5598 | 2275 | 0 | 39031.5598 | 2098 | 0 |  | 1441.5 | 1660.5 | 138.8889 | 0 | 128.083 | 0 | 1.3889 | 0 | 1.2808 | 0 | 1.3889 | 1.2808 | 13.9068 | 23.5167 | 12.5179
39031.5619 | 2220 | 0 | 39031.5619 | 2043 | 0 |  | 1626 | 1845 | 135.5311 | 0 | 124.7253 | 0 | 1.3553 | 0 | 1.2473 | 0 | 1.3553 | 1.2473 | 16.7288 | 26.8419 | 15.3735
39031.5641 | 2080 | 0 | 39031.5641 | 2442 | 0 |  | 1811 | 2030 | 126.9841 | 0 | 149.0842 | 0 | 1.2698 | 0 | 1.4908 | 0 | 1.2698 | 1.4908 | 24.5856 | 6.1171 | 23.3157
39031.5662 | 2530 | 0 | 39031.5662 | 2137 | 0 |  | 1995.5 | 2214.5 | 154.4567 | 0 | 130.464 | 0 | 1.5446 | 0 | 1.3046 | 0 | 1.5446 | 1.3046 | 2.4261 | 21.2625 | 0.88152
39031.5683 | 2452 | 0 | 39031.5684 | 1985 | 0 |  | 2180.5 | 2399.5 | 149.6947 | 0 | 121.1844 | 0 | 1.4969 | 0 | 1.2118 | 0 | 1.4969 | 1.2118 | 5.6843 | 30.5481 | 4.1874
39031.5705 | 2327 | 0 | 39031.5705 | 2119 | 0 |  | 2365.5 | 2584.5 | 142.0635 | 0 | 129.3651 | 0 | 1.4206 | 0 | 1.2937 | 0 | 1.4206 | 1.2937 | 11.3614 | 22.2926 | 9.9408
39031.5726 | 2575 | 0 | 39031.5726 | 2306 | 0 |  | 2550 | 2769 | 157.2039 | 0 | 140.7814 | 0 | 1.572 | 0 | 1.4078 | 0 | 1.572 | 1.4078 | 0.63612 | 12.3755 | 0.93592

## E10-F12
Open Burn Test 8 |  |  | 2006-11-10 | 13:06 |  |  | Vs = |  | 160.4628 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 150 kW |  | Bundle | Ch. 10 & 12 | Cable E | Even - | Cable F |  | Even
Time-129 | N11 | N12 | Time-130 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R10-G | R12-G | R10-12
39031.5427 | 0 | 0 | 39031.5427 | 0 | 0 |  | -39.5 | 179.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 525576 | 525576 | 525575.9997
39031.5448 | 0 | 0 | 39031.5448 | 0 | 0 |  | 145.5 | 364.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 525576 | 525576 | 525575.9997
39031.5469 | 0 | 0 | 39031.5469 | 0 | 0 |  | 330 | 549 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 525576 | 525576 | 525575.9997
39031.5491 | 0 | 0 | 39031.5491 | 0 | 0 |  | 514.5 | 733.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 525576 | 525576 | 525575.9997
39031.5512 | 0 | 0 | 39031.5512 | 0 | 0 |  | 699.5 | 918.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 525576 | 525576 | 525575.9997
39031.5533 | 2274 | 0 | 39031.5534 | 0 | 0 |  | 884.5 | 1103.5 | 138.8278 | 0 | 0.030525 | 0 | 1.3883 | 0 | 0.00030525 | 0 | 1.3883 | 0.00030525 | 15.584 | 525576 | 14.1957
39031.5555 | 2401 | 0 | 39031.5555 | 8 | 0 |  | 1069 | 1288 | 146.5812 | 0 | 0.4884 | 0 | 1.4658 | 0 | 0.004884 | 0 | 1.4658 | 0.004884 | 9.4702 | 32754.75 | 8.0044
39031.5576 | 2147 | 0 | 39031.5576 | 2242 | 0 |  | 1253.5 | 1472.5 | 131.0745 | 0 | 136.8742 | 0 | 1.3107 | 0 | 1.3687 | 0 | 1.3107 | 1.3687 | 22.4211 | 17.2337 | 21.1103
39031.5598 | 2039 | 0 | 39031.5598 | 2290 | 0 |  | 1438.5 | 1657.5 | 124.4811 | 0 | 139.8046 | 0 | 1.2448 | 0 | 1.398 | 0 | 1.2448 | 1.398 | 28.9053 | 14.7764 | 27.6605
39031.5619 | 2187 | 0 | 39031.5619 | 2261 | 0 |  | 1623.5 | 1842.5 | 133.5165 | 0 | 138.0342 | 0 | 1.3352 | 0 | 1.3803 | 0 | 1.3352 | 1.3803 | 20.182 | 16.2486 | 18.8468
39031.564 | 2317 | 0 | 39031.5641 | 2556 | 0 |  | 1808 | 2027 | 141.453 | 0 | 156.044 | 0 | 1.4145 | 0 | 1.5604 | 0 | 1.4145 | 1.5604 | 13.4389 | 2.8318 | 12.0244
39031.5662 | 2033 | 0 | 39031.5662 | 2348 | 0 |  | 1993 | 2212 | 124.1148 | 0 | 143.3455 | 0 | 1.2411 | 0 | 1.4335 | 0 | 1.2411 | 1.4335 | 29.2858 | 11.9412 | 28.0446
39031.5683 | 2342 | 0 | 39031.5683 | 2612 | 0 |  | 2177.5 | 2396.5 | 142.9792 | 0 | 159.4628 | 0 | 1.4298 | 0 | 1.5946 | 0 | 1.4298 | 1.5946 | 12.228 | 0.62711 | 10.7982
39031.5705 | 2062 | 1 | 39031.5705 | 2005 | 0 |  | 2362.5 | 2581.5 | 125.8852 | 0.06105 | 122.4054 | 0 | 1.2589 | 0.0006105 | 1.2241 | 0 | 1.2582 | 1.2241 | 27.5238 | 31.0913 | 13409.2705
39031.5726 | 2238 | 0 | 39031.5726 | 2358 | 0 |  | 2547.5 | 2766.5 | 136.63 | 0 | 143.956 | 0 | 1.3663 | 0 | 1.4396 | 0 | 1.3663 | 1.4396 | 17.4433 | 11.4665 | 16.077

## E10-F11
Open Burn Test 8 |  |  | 2006-11-10 | 13:06 |  |  | Vs = |  | 155.2735 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 150 kW |  | Bundle | Ch. 10 & 11 | Cable E | Even - | Cable F |  | Odd
Time-127 | N11 | N12 | Time-128 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R10-G | R11-G | R10-11
39031.5426 | 0 | 0 | 39031.5426 | 0 | 0 |  | -42.5 | 176.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 508576 | 508576 | 508575.9997
39031.5448 | 0 | 0 | 39031.5448 | 0 | 0 |  | 142.5 | 361.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 508576 | 508576 | 508575.9997
39031.5469 | 0 | 0 | 39031.5469 | 0 | 1 |  | 327 | 546 | 0.030525 | 0 | 0.030525 | 0.06105 | 0.00030525 | 0 | 0.00030525 | 0.0006105 | 0.00030525 | 0.00030525 | 508576 | 508576 | 508575.9997
39031.549 | 0 | 0 | 39031.5491 | 0 | 0 |  | 512 | 731 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 508576 | 508576 | 508575.9997
39031.5512 | 0 | 0 | 39031.5512 | 0 | 0 |  | 696.5 | 915.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 508576 | 508576 | 508575.9997
39031.5533 | 2325 | 1 | 39031.5533 | 0 | 0 |  | 881.5 | 1100.5 | 141.9414 | 0.06105 | 0.030525 | 0 | 1.4194 | 0.0006105 | 0.00030525 | 0 | 1.4188 | 0.00030525 | 9.3967 | 508575.9998 | 21733.7266
39031.5554 | 1948 | 0 | 39031.5555 | 1240 | 0 |  | 1066 | 1285 | 118.9255 | 0 | 75.7021 | 0 | 1.1893 | 0 | 0.75702 | 0 | 1.1893 | 0.75702 | 30.5637 | 105.1113 | 29.3744
39031.5576 | 2453 | 0 | 39031.5576 | 2477 | 0 |  | 1251 | 1470 | 149.7558 | 0 | 151.221 | 0 | 1.4976 | 0 | 1.5122 | 0 | 1.4976 | 1.5122 | 3.6845 | 2.6799 | 2.1869
39031.5597 | 2483 | 0 | 39031.5597 | 2374 | 0 |  | 1435.5 | 1654.5 | 151.5873 | 0 | 144.9328 | 0 | 1.5159 | 0 | 1.4493 | 0 | 1.5159 | 1.4493 | 2.4317 | 7.1348 | 0.91586
39031.5619 | 2302 | 0 | 39031.5619 | 1979 | 0 |  | 1620.5 | 1839.5 | 140.5372 | 0 | 120.8181 | 0 | 1.4054 | 0 | 1.2082 | 0 | 1.4054 | 1.2082 | 10.4857 | 28.5184 | 9.0803
39031.564 | 2527 | 0 | 39031.564 | 2354 | 0 |  | 1805.5 | 2024.5 | 154.2735 | 0 | 143.7118 | 0 | 1.5427 | 0 | 1.4371 | 0 | 1.5427 | 1.4371 | 0.6482 | 8.045 | 0.89454
39031.5661 | 2135 | 0 | 39031.5662 | 2099 | 0 |  | 1990 | 2209 | 130.3419 | 0 | 128.1441 | 0 | 1.3034 | 0 | 1.2814 | 0 | 1.3034 | 1.2814 | 19.1279 | 21.171 | 17.8245
39031.5683 | 2508 | 0 | 39031.5683 | 2241 | 0 |  | 2175 | 2394 | 153.1136 | 0 | 136.8132 | 0 | 1.5311 | 0 | 1.3681 | 0 | 1.5311 | 1.3681 | 1.4107 | 13.4931 | 0.12045
39031.5704 | 2007 | 0 | 39031.5704 | 2219 | 0 |  | 2359.5 | 2578.5 | 122.5275 | 0 | 135.4701 | 0 | 1.2253 | 0 | 1.3547 | 0 | 1.2253 | 1.3547 | 26.7255 | 14.6183 | 25.5002
39031.5726 | 2060 | 0 | 39031.5726 | 1980 | 0 |  | 2544.5 | 2763.5 | 125.7631 | 0 | 120.8791 | 0 | 1.2576 | 0 | 1.2088 | 0 | 1.2576 | 1.2088 | 23.465 | 28.4535 | 22.2074

## E9-F12
Open Burn Test 8 |  |  | 2006-11-10 | 13:06 |  |  | Vs = |  | 160.3407 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 150 kW |  | Bundle | Ch. 9 & 12 | Cable E | Odd - | Cable F |  | Even
Time-125 | N11 | N12 | Time-126 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R9-G | R12-G | R9-12
39031.5426 | 0 | 0 | 39031.5426 | 0 | 0 |  | -45 | 174 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 525176 | 525176 | 525175.9997
39031.5447 | 0 | 0 | 39031.5447 | 0 | 0 |  | 139.5 | 358.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 525176 | 525176 | 525175.9997
39031.5469 | 0 | 0 | 39031.5469 | 0 | 0 |  | 324.5 | 543.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 525176 | 525176 | 525175.9997
39031.549 | 0 | 0 | 39031.549 | 0 | 0 |  | 509 | 728 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 525176 | 525176 | 525175.9997
39031.5511 | 1670 | 2 | 39031.5512 | 0 | 1 |  | 694 | 913 | 101.9536 | 0.1221 | 0.030525 | 0.06105 | 1.0195 | 0.001221 | 0.00030525 | 0.0006105 | 1.0183 | 0.00030525 | 57.3369 | 211070.4326 | 47696.4026
39031.5533 | 1965 | 0 | 39031.5533 | 0 | 0 |  | 878.5 | 1097.5 | 119.9634 | 0 | 0.030525 | 0 | 1.1996 | 0 | 0.00030525 | 0 | 1.1996 | 0.00030525 | 33.658 | 525176 | 32.4584
39031.5554 | 1974 | 0 | 39031.5554 | 0 | 0 |  | 1063.5 | 1282.5 | 120.5128 | 0 | 0.030525 | 0 | 1.2051 | 0 | 0.00030525 | 0 | 1.2051 | 0.00030525 | 33.0486 | 525176 | 31.8435
39031.5575 | 2249 | 0 | 39031.5576 | 1940 | 0 |  | 1248 | 1467 | 137.3016 | 0 | 118.4371 | 0 | 1.373 | 0 | 1.1844 | 0 | 1.373 | 1.1844 | 16.7799 | 35.3804 | 15.4069
39031.5597 | 2519 | 0 | 39031.5597 | 2568 | 0 |  | 1433 | 1652 | 153.7851 | 0 | 156.7766 | 0 | 1.5379 | 0 | 1.5678 | 0 | 1.5379 | 1.5678 | 4.2628 | 2.2734 | 2.725
39031.5618 | 2041 | 0 | 39031.5619 | 2597 | 0 |  | 1618 | 1837 | 124.6032 | 0 | 158.547 | 0 | 1.246 | 0 | 1.5855 | 0 | 1.246 | 1.5855 | 28.681 | 1.1313 | 27.435
39031.564 | 2014 | 0 | 39031.564 | 2082 | 0 |  | 1802.5 | 2021.5 | 122.9548 | 0 | 127.1062 | 0 | 1.2295 | 0 | 1.2711 | 0 | 1.2295 | 1.2711 | 30.4062 | 26.147 | 29.1766
39031.5661 | 1988 | 0 | 39031.5661 | 2037 | 0 |  | 1987.5 | 2206.5 | 121.3675 | 0 | 124.359 | 0 | 1.2137 | 0 | 1.2436 | 0 | 1.2137 | 1.2436 | 32.1117 | 28.9337 | 30.898
39031.5682 | 2610 | 0 | 39031.5683 | 2060 | 0 |  | 2172 | 2391 | 159.3407 | 0 | 125.7631 | 0 | 1.5934 | 0 | 1.2576 | 0 | 1.5934 | 1.2576 | 0.62759 | 27.4942 | 0.96582
39031.5704 | 2593 | 0 | 39031.5704 | 2242 | 0 |  | 2356.5 | 2575.5 | 158.3028 | 0 | 136.8742 | 0 | 1.583 | 0 | 1.3687 | 0 | 1.583 | 1.3687 | 1.2873 | 17.1445 | 0.29572
39031.5725 | 2555 | 0 | 39031.5725 | 2561 | 0 |  | 2541.5 | 2760.5 | 155.9829 | 0 | 156.3492 | 0 | 1.5598 | 0 | 1.5635 | 0 | 1.5598 | 1.5635 | 2.7937 | 2.5529 | 1.2339

## E9-F11
Open Burn Test 8 |  |  | 2006-11-10 | 13:06 |  |  | Vs = |  | 160.5238 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 150 kW |  | Bundle | Ch. 9 & 11 | Cable E | Odd - | Cable F |  | Odd
Time-123 | N11 | N12 | Time-124 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R9-G | R11-G | R9-11
39031.5425 | 0 | 0 | 39031.5426 | 0 | 0 |  | -48 | 171 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 525776 | 525776 | 525775.9997
39031.5447 | 0 | 0 | 39031.5447 | 0 | 0 |  | 137 | 356 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 525776 | 525776 | 525775.9997
39031.5468 | 0 | 0 | 39031.5468 | 0 | 0 |  | 321.5 | 540.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 525776 | 525776 | 525775.9997
39031.549 | 0 | 0 | 39031.549 | 0 | 0 |  | 506.5 | 725.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 525776 | 525776 | 525775.9997
39031.5511 | 1712 | 3 | 39031.5511 | 0 | 0 |  | 691 | 910 | 104.5177 | 0.18315 | 0.030525 | 0 | 1.0452 | 0.0018315 | 0.00030525 | 0 | 1.0433 | 0.00030525 | 53.6794 | 525775.9998 | 30473.5374
39031.5532 | 2016 | 1 | 39031.5533 | 0 | 0 |  | 876 | 1095 | 123.0769 | 0.06105 | 0.030525 | 0 | 1.2308 | 0.0006105 | 0.00030525 | 0 | 1.2302 | 0.00030525 | 30.4407 | 525776.0011 | 61226.355
39031.5554 | 2508 | 0 | 39031.5554 | 0 | 0 |  | 1060.5 | 1279.5 | 153.1136 | 0 | 0.030525 | 0 | 1.5311 | 0 | 0.00030525 | 0 | 1.5311 | 0.00030525 | 4.8397 | 525776 | 3.3086
39031.5575 | 2465 | 0 | 39031.5575 | 1974 | 0 |  | 1245.5 | 1464.5 | 150.4884 | 0 | 120.5128 | 0 | 1.5049 | 0 | 1.2051 | 0 | 1.5049 | 1.2051 | 6.6686 | 33.2006 | 5.1637
39031.5597 | 2015 | 0 | 39031.5597 | 2498 | 0 |  | 1430 | 1649 | 123.0159 | 0 | 152.5031 | 0 | 1.2302 | 0 | 1.525 | 0 | 1.2302 | 1.525 | 30.4903 | 5.2594 | 29.2602
39031.5618 | 2325 | 0 | 39031.5618 | 2061 | 0 |  | 1615 | 1834 | 141.9414 | 0 | 125.8242 | 0 | 1.4194 | 0 | 1.2582 | 0 | 1.4194 | 1.2582 | 13.0916 | 27.5779 | 11.6722
39031.5639 | 2331 | 0 | 39031.5639 | 2451 | 0 |  | 1799.5 | 2018.5 | 142.3077 | 0 | 149.6337 | 0 | 1.4231 | 0 | 1.4963 | 0 | 1.4231 | 1.4963 | 12.8005 | 7.2778 | 11.3774
39031.5661 | 2613 | 0 | 39031.5661 | 2351 | 0 |  | 1984.5 | 2203.5 | 159.5238 | 0 | 143.5287 | 0 | 1.5952 | 0 | 1.4353 | 0 | 1.5952 | 1.4353 | 0.62687 | 11.8409 | 0.96837
39031.5682 | 2258 | 0 | 39031.5682 | 2317 | 0 |  | 2169.5 | 2388.5 | 137.851 | 0 | 141.453 | 0 | 1.3785 | 0 | 1.4145 | 0 | 1.3785 | 1.4145 | 16.4473 | 13.4821 | 15.0688
39031.5703 | 2543 | 0 | 39031.5704 | 2036 | 0 |  | 2354 | 2573 | 155.2503 | 0 | 124.2979 | 0 | 1.5525 | 0 | 1.243 | 0 | 1.5525 | 1.243 | 3.3968 | 29.1444 | 1.8443
39031.5725 | 2075 | 0 | 39031.5725 | 2223 | 0 |  | 2539 | 2758 | 126.6789 | 0 | 135.7143 | 0 | 1.2668 | 0 | 1.3571 | 0 | 1.2668 | 1.3571 | 26.7171 | 18.2807 | 25.4503

## E9-E10
Open Burn Test 8 |  |  | 2006-11-10 | 13:06 |  |  | Vs = |  | 159.9744 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 150 kW |  | Bundle | Ch. 9 & 10 | Cable E | Odd -Even
Time-121 | N11 | N12 | Time-122 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R9-G | R10-G | R9-10
39031.5425 | 0 | 0 | 39031.5425 | 0 | 0 |  | -50.5 | 168.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 523976 | 523976 | 523975.9997
39031.5447 | 0 | 0 | 39031.5447 | 0 | 0 |  | 134 | 353 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 523976 | 523976 | 523975.9997
39031.5468 | 0 | 0 | 39031.5468 | 0 | 0 |  | 318.5 | 537.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 523976 | 523976 | 523975.9997
39031.5489 | 0 | 0 | 39031.5489 | 0 | 0 |  | 503.5 | 722.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 523976 | 523976 | 523975.9997
39031.5511 | 2 | 0 | 39031.5511 | 0 | 0 |  | 688.5 | 907.5 | 0.1221 | 0 | 0.030525 | 0 | 0.001221 | 0 | 0.00030525 | 0 | 0.001221 | 0.00030525 | 130919 | 523976 | 130918.9988
39031.5532 | 2200 | 473 | 39031.5532 | 2305 | 227 |  | 873 | 1092 | 134.3101 | 28.8767 | 140.7204 | 13.8584 | 1.3431 | 0.28877 | 1.4072 | 0.13858 | 1.0543 | 1.2686 | 5.7523 | 8.4751 | 0.86917
39031.5553 | 2287 | 0 | 39031.5554 | 2107 | 0 |  | 1058 | 1277 | 139.6215 | 0 | 128.6325 | 0 | 1.3962 | 0 | 1.2863 | 0 | 1.3962 | 1.2863 | 14.5772 | 24.3654 | 13.181
39031.5575 | 2198 | 0 | 39031.5575 | 2330 | 0 |  | 1242.5 | 1461.5 | 134.188 | 0 | 142.2466 | 0 | 1.3419 | 0 | 1.4225 | 0 | 1.3419 | 1.4225 | 19.2166 | 12.4627 | 17.8747
39031.5596 | 2376 | 0 | 39031.5596 | 2397 | 0 |  | 1427.5 | 1646.5 | 145.0549 | 0 | 146.337 | 0 | 1.4505 | 0 | 1.4634 | 0 | 1.4505 | 1.4634 | 10.2854 | 9.3191 | 8.8348
39031.5618 | 2010 | 0 | 39031.5618 | 2312 | 0 |  | 1612 | 1831 | 122.7106 | 0 | 141.1477 | 0 | 1.2271 | 0 | 1.4115 | 0 | 1.2271 | 1.4115 | 30.3672 | 13.3382 | 29.1401
39031.5639 | 2576 | 0 | 39031.5639 | 2604 | 0 |  | 1797 | 2016 | 157.265 | 0 | 158.9744 | 0 | 1.5726 | 0 | 1.5897 | 0 | 1.5726 | 1.5897 | 1.7228 | 0.62903 | 0.15018
39031.566 | 2423 | 0 | 39031.5661 | 2272 | 0 |  | 1981.5 | 2200.5 | 147.9243 | 0 | 138.7057 | 0 | 1.4792 | 0 | 1.3871 | 0 | 1.4792 | 1.3871 | 8.1461 | 15.3336 | 6.6669
39031.5682 | 2138 | 0 | 39031.5682 | 2367 | 0 |  | 2166.5 | 2385.5 | 130.525 | 0 | 144.5055 | 0 | 1.3053 | 0 | 1.4451 | 0 | 1.3053 | 1.4451 | 22.5622 | 10.7047 | 21.257
39031.5703 | 2061 | 0 | 39031.5703 | 2351 | 0 |  | 2351.5 | 2570.5 | 125.8242 | 0 | 143.5287 | 0 | 1.2582 | 0 | 1.4353 | 0 | 1.2582 | 1.4353 | 27.1412 | 11.4581 | 25.883
39031.5725 | 2528 | 0 | 39031.5725 | 2488 | 0 |  | 2536 | 2755 | 154.3346 | 0 | 151.8926 | 0 | 1.5433 | 0 | 1.5189 | 0 | 1.5433 | 1.5189 | 3.6543 | 5.3207 | 2.1109

## D8-E10
Open Burn Test 8 |  |  | 2006-11-10 | 13:06 |  |  | Vs = |  | 157.8376 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 150 kW |  | Bundle | Ch. 8 & 10 | Cable D | Even - | Cable E |  | Even
Time-115 | N11 | N12 | Time-116 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R8-G | R10-G | R8-10
39031.5424 | 0 | 0 | 39031.5424 | 0 | 0 |  | -59 | 160 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 516976 | 516976 | 516975.9997
39031.5446 | 0 | 0 | 39031.5446 | 0 | 0 |  | 125.5 | 344.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 516976 | 516976 | 516975.9997
39031.5467 | 0 | 0 | 39031.5467 | 0 | 0 |  | 310.5 | 529.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 516976 | 516976 | 516975.9997
39031.5488 | 0 | 0 | 39031.5489 | 0 | 0 |  | 495 | 714 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 516976 | 516976 | 516975.9997
39031.551 | 0 | 0 | 39031.551 | 0 | 0 |  | 680 | 899 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 516976 | 516976 | 516975.9997
39031.5531 | 0 | 0 | 39031.5531 | 1729 | 1 |  | 864.5 | 1083.5 | 0.030525 | 0 | 105.5556 | 0.06105 | 0.00030525 | 0 | 1.0556 | 0.0006105 | 0.00030525 | 1.0549 | 516976 | 49.6169 | 516975.9997
39031.5553 | 1 | 0 | 39031.5553 | 2238 | 0 |  | 1049.5 | 1268.5 | 0.06105 | 0 | 136.63 | 0 | 0.0006105 | 0 | 1.3663 | 0 | 0.0006105 | 1.3663 | 258438 | 15.5219 | 258437.9994
39031.5574 | 2324 | 0 | 39031.5574 | 2086 | 0 |  | 1234 | 1453 | 141.8803 | 0 | 127.3504 | 0 | 1.4188 | 0 | 1.2735 | 0 | 1.4188 | 1.2735 | 11.247 | 23.9396 | 9.8282
39031.5595 | 2414 | 0 | 39031.5595 | 2152 | 0 |  | 1419 | 1638 | 147.3748 | 0 | 131.3797 | 0 | 1.4737 | 0 | 1.3138 | 0 | 1.4737 | 1.3138 | 7.0994 | 20.1385 | 5.6257
39031.5617 | 1979 | 0 | 39031.5617 | 2260 | 0 |  | 1603.5 | 1822.5 | 120.8181 | 0 | 137.9731 | 0 | 1.2082 | 0 | 1.3797 | 0 | 1.2082 | 1.3797 | 30.6407 | 14.3973 | 29.4325
39031.5638 | 2395 | 0 | 39031.5638 | 2530 | 0 |  | 1788.5 | 2007.5 | 146.2149 | 0 | 154.4567 | 0 | 1.4621 | 0 | 1.5446 | 0 | 1.4621 | 1.5446 | 7.9491 | 2.1889 | 6.4869
39031.5659 | 2569 | 0 | 39031.566 | 2171 | 0 |  | 1973.5 | 2192.5 | 156.8376 | 0 | 132.5397 | 0 | 1.5684 | 0 | 1.3254 | 0 | 1.5684 | 1.3254 | 0.6376 | 19.0871 | 0.93077
39031.5681 | 2534 | 0 | 39031.5681 | 2224 | 0 |  | 2158 | 2377 | 154.7009 | 0 | 135.7753 | 0 | 1.547 | 0 | 1.3578 | 0 | 1.547 | 1.3578 | 2.0276 | 16.2491 | 0.48062
39031.5702 | 2562 | 0 | 39031.5702 | 2011 | 0 |  | 2342.5 | 2561.5 | 156.4103 | 0 | 122.7717 | 0 | 1.5641 | 0 | 1.2277 | 0 | 1.5641 | 1.2277 | 0.91257 | 28.5619 | 0.65153
39031.5724 | 2096 | 0 | 39031.5724 | 2544 | 0 |  | 2527.5 | 2746.5 | 127.9609 | 0 | 155.3114 | 0 | 1.2796 | 0 | 1.5531 | 0 | 1.2796 | 1.5531 | 23.3483 | 1.6266 | 22.0687

## D8-E9
Open Burn Test 8 |  |  | 2006-11-10 | 13:06 |  |  | Vs = |  | 158.5092 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 150 kW |  | Bundle | Ch. 8 & 9 | Cable D | Even - | Cable E |  | Odd
Time-113 | N11 | N12 | Time-114 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R8-G | R9-G | R8-9
39031.5424 | 0 | 0 | 39031.5424 | 0 | 0 |  | -62 | 157 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 519176 | 519176 | 519175.9997
39031.5445 | 0 | 0 | 39031.5445 | 0 | 0 |  | 123 | 342 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 519176 | 519176 | 519175.9997
39031.5467 | 0 | 0 | 39031.5467 | 0 | 0 |  | 307.5 | 526.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 519176 | 519176 | 519175.9997
39031.5488 | 0 | 0 | 39031.5488 | 0 | 0 |  | 492.5 | 711.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 519176 | 519176 | 519175.9997
39031.5509 | 0 | 0 | 39031.551 | 1633 | 1 |  | 677 | 896 | 0.030525 | 0 | 99.6947 | 0.06105 | 0.00030525 | 0 | 0.99695 | 0.0006105 | 0.00030525 | 0.99634 | 519176 | 59.0919 | 519175.9997
39031.5531 | 0 | 0 | 39031.5531 | 1907 | 2 |  | 862 | 1081 | 0.030525 | 0 | 116.4225 | 0.1221 | 0.00030525 | 0 | 1.1642 | 0.001221 | 0.00030525 | 1.163 | 519176 | 36.2929 | 519175.9997
39031.5552 | 1 | 0 | 39031.5552 | 2082 | 0 |  | 1046.5 | 1265.5 | 0.06105 | 0 | 127.1062 | 0 | 0.0006105 | 0 | 1.2711 | 0 | 0.0006105 | 1.2711 | 259538 | 24.7061 | 259537.9994
39031.5574 | 2490 | 0 | 39031.5574 | 2580 | 0 |  | 1231.5 | 1450.5 | 152.0147 | 0 | 157.5092 | 0 | 1.5201 | 0 | 1.5751 | 0 | 1.5201 | 1.5751 | 4.2723 | 0.63488 | 2.7521
39031.5595 | 2274 | 0 | 39031.5595 | 2445 | 0 |  | 1416.5 | 1635.5 | 138.8278 | 0 | 149.2674 | 0 | 1.3883 | 0 | 1.4927 | 0 | 1.3883 | 1.4927 | 14.1768 | 6.1914 | 12.7885
39031.5616 | 2137 | 0 | 39031.5617 | 2008 | 0 |  | 1601 | 1820 | 130.464 | 0 | 122.5885 | 0 | 1.3046 | 0 | 1.2259 | 0 | 1.3046 | 1.2259 | 21.4965 | 29.3018 | 20.1919
39031.5638 | 2170 | 0 | 39031.5638 | 2326 | 0 |  | 1785.5 | 2004.5 | 132.4786 | 0 | 142.0024 | 0 | 1.3248 | 0 | 1.42 | 0 | 1.3248 | 1.42 | 19.6488 | 11.6242 | 18.3241
39031.5659 | 2072 | 0 | 39031.5659 | 2132 | 0 |  | 1970.5 | 2189.5 | 126.4957 | 0 | 130.1587 | 0 | 1.265 | 0 | 1.3016 | 0 | 1.265 | 1.3016 | 25.3079 | 21.7814 | 24.043
39031.5681 | 2008 | 0 | 39031.5681 | 2447 | 0 |  | 2155.5 | 2374.5 | 122.5885 | 0 | 149.3895 | 0 | 1.2259 | 0 | 1.4939 | 0 | 1.2259 | 1.4939 | 29.3018 | 6.1046 | 28.0759
39031.5702 | 2441 | 0 | 39031.5702 | 2203 | 0 |  | 2340 | 2559 | 149.0232 | 0 | 134.4933 | 0 | 1.4902 | 0 | 1.3449 | 0 | 1.4902 | 1.3449 | 6.3654 | 17.8566 | 4.8752
39031.5723 | 1917 | 0 | 39031.5723 | 2016 | 1 |  | 2524.5 | 2743.5 | 117.033 | 0 | 123.0769 | 0.06105 | 1.1703 | 0 | 1.2308 | 0.0006105 | 1.1703 | 1.2302 | 35.4397 | 28.8526 | 34.2694

## D7-E10
Open Burn Test 8 |  |  | 2006-11-10 | 13:06 |  |  | Vs = |  | 159.0586 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 150 kW |  | Bundle | Ch. 7 & 10 | Cable D | Odd - | Cable E |  | Even
Time-107 | N11 | N12 | Time-108 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R7-G | R10-G | R7-10
39031.5423 | 0 | 0 | 39031.5423 | 0 | 0 |  | -70.5 | 148.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 520976 | 520976 | 520975.9997
39031.5444 | 0 | 0 | 39031.5444 | 0 | 0 |  | 114.5 | 333.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 520976 | 520976 | 520975.9997
39031.5466 | 0 | 0 | 39031.5466 | 0 | 0 |  | 299.5 | 518.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 520976 | 520976 | 520975.9997
39031.5487 | 0 | 0 | 39031.5487 | 0 | 0 |  | 484 | 703 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 520976 | 520976 | 520975.9997
39031.5508 | 0 | 0 | 39031.5509 | 0 | 0 |  | 668.5 | 887.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 520976 | 520976 | 520975.9997
39031.553 | 0 | 0 | 39031.553 | 485 | 0 |  | 853.5 | 1072.5 | 0.030525 | 0 | 29.6093 | 0 | 0.00030525 | 0 | 0.29609 | 0 | 0.00030525 | 0.29609 | 520976 | 437.1918 | 520975.9997
39031.5551 | 265 | 0 | 39031.5551 | 2436 | 0 |  | 1038.5 | 1257.5 | 16.1783 | 0 | 148.7179 | 0 | 0.16178 | 0 | 1.4872 | 0 | 0.16178 | 1.4872 | 883.1623 | 6.9532 | 883.0005
39031.5573 | 2026 | 0 | 39031.5573 | 2200 | 0 |  | 1223 | 1442 | 123.6874 | 0 | 134.3101 | 0 | 1.2369 | 0 | 1.3431 | 0 | 1.2369 | 1.3431 | 28.5972 | 18.4264 | 27.3604
39031.5594 | 2387 | 0 | 39031.5594 | 2286 | 0 |  | 1408 | 1627 | 145.7265 | 0 | 139.5604 | 0 | 1.4573 | 0 | 1.3956 | 0 | 1.4573 | 1.3956 | 9.1487 | 13.9711 | 7.6915
39031.5615 | 2565 | 0 | 39031.5616 | 2267 | 0 |  | 1592.5 | 1811.5 | 156.5934 | 0 | 138.4005 | 0 | 1.5659 | 0 | 1.384 | 0 | 1.5659 | 1.384 | 1.5743 | 14.9263 | 0.0083349
39031.5637 | 2543 | 0 | 39031.5637 | 2084 | 0 |  | 1777.5 | 1996.5 | 155.2503 | 0 | 127.2283 | 0 | 1.5525 | 0 | 1.2723 | 0 | 1.5525 | 1.2723 | 2.453 | 25.0182 | 0.90051
39031.5658 | 2206 | 0 | 39031.5658 | 2423 | 0 |  | 1962 | 2181 | 134.6764 | 0 | 147.9243 | 0 | 1.3468 | 0 | 1.4792 | 0 | 1.3468 | 1.4792 | 18.1043 | 7.527 | 16.7575
39031.568 | 2231 | 0 | 39031.568 | 2295 | 0 |  | 2147 | 2366 | 136.2027 | 0 | 140.1099 | 0 | 1.362 | 0 | 1.4011 | 0 | 1.362 | 1.4011 | 16.7808 | 13.5242 | 15.4188
39031.5701 | 2305 | 0 | 39031.5701 | 2554 | 2 |  | 2331.5 | 2550.5 | 140.7204 | 0 | 155.9219 | 0.1221 | 1.4072 | 0 | 1.5592 | 0.001221 | 1.4072 | 1.558 | 13.0317 | 2.0917 | 11.6245
39031.5722 | 2075 | 0 | 39031.5722 | 2589 | 1 |  | 2516.5 | 2735.5 | 126.6789 | 0 | 158.0586 | 0.06105 | 1.2668 | 0 | 1.5806 | 0.0006105 | 1.2668 | 1.58 | 25.5605 | 0.67156 | 24.2937

## D7-E9
Open Burn Test 8 |  |  | 2006-11-10 | 13:06 |  |  | Vs = |  | 149.779 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 150 kW |  | Bundle | Ch. 7 & 9 | Cable D | Odd - | Cable E |  | Odd
Time-105 | N11 | N12 | Time-106 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R7-G | R9-G | R7-9
39031.5423 | 0 | 0 | 39031.5423 | 0 | 0 |  | -73 | 146 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 490576 | 490576 | 490575.9997
39031.5444 | 0 | 0 | 39031.5444 | 0 | 0 |  | 111.5 | 330.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 490576 | 490576 | 490575.9997
39031.5465 | 0 | 0 | 39031.5466 | 0 | 0 |  | 296.5 | 515.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 490576 | 490576 | 490575.9997
39031.5487 | 0 | 0 | 39031.5487 | 0 | 0 |  | 481.5 | 700.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 490576 | 490576 | 490575.9997
39031.5508 | 0 | 0 | 39031.5508 | 2017 | 1 |  | 666 | 885 | 0.030525 | 0 | 123.138 | 0.06105 | 0.00030525 | 0 | 1.2314 | 0.0006105 | 0.00030525 | 1.2308 | 490576 | 21.6954 | 490575.9997
39031.553 | 0 | 0 | 39031.553 | 2320 | 2 |  | 850.5 | 1069.5 | 0.030525 | 0 | 141.6361 | 0.1221 | 0.00030525 | 0 | 1.4164 | 0.001221 | 0.00030525 | 1.4151 | 490576 | 5.8404 | 490575.9997
39031.5551 | 763 | 0 | 39031.5551 | 2329 | 0 |  | 1035.5 | 1254.5 | 46.5812 | 0 | 142.1856 | 0 | 0.46581 | 0 | 1.4219 | 0 | 0.46581 | 1.4219 | 221.5439 | 5.3405 | 221.0781
39031.5572 | 2424 | 0 | 39031.5572 | 2005 | 0 |  | 1220 | 1439 | 147.9853 | 0 | 122.4054 | 0 | 1.4799 | 0 | 1.2241 | 0 | 1.4799 | 1.2241 | 1.212 | 22.3631 | 0.26781
39031.5594 | 2432 | 0 | 39031.5594 | 2328 | 0 |  | 1405 | 1624 | 148.4737 | 0 | 142.1245 | 0 | 1.4847 | 0 | 1.4212 | 0 | 1.4847 | 1.4212 | 0.87911 | 5.3857 | 0.60563
39031.5615 | 2437 | 0 | 39031.5615 | 2216 | 0 |  | 1589.5 | 1808.5 | 148.779 | 0 | 135.2869 | 0 | 1.4878 | 0 | 1.3529 | 0 | 1.4878 | 1.3529 | 0.67214 | 10.7121 | 0.81565
39031.5636 | 2112 | 0 | 39031.5637 | 2043 | 0 |  | 1774.5 | 1993.5 | 128.9377 | 0 | 124.7253 | 0 | 1.2894 | 0 | 1.2473 | 0 | 1.2894 | 1.2473 | 16.1638 | 20.0871 | 14.8744
39031.5658 | 2061 | 0 | 39031.5658 | 2260 | 0 |  | 1959.5 | 2178.5 | 125.8242 | 0 | 137.9731 | 0 | 1.2582 | 0 | 1.3797 | 0 | 1.2582 | 1.3797 | 19.0383 | 8.5566 | 17.7801
39031.5679 | 2219 | 0 | 39031.5679 | 2044 | 0 |  | 2144 | 2363 | 135.4701 | 0 | 124.7863 | 0 | 1.3547 | 0 | 1.2479 | 0 | 1.3547 | 1.2479 | 10.5624 | 20.0284 | 9.2077
39031.5701 | 2093 | 0 | 39031.5701 | 2040 | 0 |  | 2328.5 | 2547.5 | 127.7778 | 0 | 124.5421 | 0 | 1.2778 | 0 | 1.2454 | 0 | 1.2778 | 1.2454 | 17.2183 | 20.2637 | 15.9406
39031.5722 | 2193 | 0 | 39031.5722 | 2042 | 0 |  | 2513.5 | 2732.5 | 133.8828 | 0 | 124.6642 | 0 | 1.3388 | 0 | 1.2466 | 0 | 1.3388 | 1.2466 | 11.8732 | 20.1459 | 10.5344

## D7-D8
Open Burn Test 8 |  |  | 2006-11-10 | 13:06 |  |  | Vs = |  | 156.5556 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 150 kW |  | Bundle | Ch. 7 & 8 | Cable D | Odd -Even
Time-103 | N11 | N12 | Time-104 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R7-G | R8-G | R7-8
39031.5422 | 0 | 0 | 39031.5422 | 0 | 0 |  | -76 | 143 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 512776 | 512776 | 512775.9997
39031.5444 | 0 | 0 | 39031.5444 | 0 | 0 |  | 109 | 328 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 512776 | 512776 | 512775.9997
39031.5465 | 0 | 0 | 39031.5465 | 0 | 0 |  | 293.5 | 512.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 512776 | 512776 | 512775.9997
39031.5486 | 0 | 0 | 39031.5487 | 0 | 0 |  | 478.5 | 697.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 512776 | 512776 | 512775.9997
39031.5508 | 0 | 0 | 39031.5508 | 0 | 0 |  | 663 | 882 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 512776 | 512776 | 512775.9997
39031.5529 | 0 | 0 | 39031.5529 | 0 | 0 |  | 848 | 1067 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 512776 | 512776 | 512775.9997
39031.5551 | 766 | 445 | 39031.5551 | 966 | 712 |  | 1032.5 | 1251.5 | 46.7643 | 27.1673 | 58.9744 | 43.4676 | 0.46764 | 0.27167 | 0.58974 | 0.43468 | 0.19597 | 0.15507 | 639.3338 | 1120.6159 | 279.2142
39031.5572 | 2123 | 4 | 39031.5572 | 2035 | 2 |  | 1217.5 | 1436.5 | 129.6093 | 0.2442 | 124.2369 | 0.1221 | 1.2961 | 0.002442 | 1.2424 | 0.001221 | 1.2937 | 1.2411 | 20.981 | 26.162 | 2267.4701
39031.5593 | 2071 | 1 | 39031.5594 | 2434 | 0 |  | 1402 | 1621 | 126.4347 | 0.06105 | 148.5958 | 0 | 1.2643 | 0.0006105 | 1.486 | 0 | 1.2637 | 1.486 | 24.0517 | 5.3566 | 2503.3928
39031.5615 | 2332 | 0 | 39031.5615 | 2112 | 0 |  | 1587 | 1806 | 142.3687 | 0 | 128.9377 | 0 | 1.4237 | 0 | 1.2894 | 0 | 1.4237 | 1.2894 | 9.9648 | 21.4195 | 8.5411
39031.5636 | 2473 | 0 | 39031.5636 | 2043 | 0 |  | 1771.5 | 1990.5 | 150.9768 | 0 | 124.7253 | 0 | 1.5098 | 0 | 1.2473 | 0 | 1.5098 | 1.2473 | 3.6951 | 25.5203 | 2.1853
39031.5658 | 2198 | 0 | 39031.5658 | 2149 | 0 |  | 1956.5 | 2175.5 | 134.188 | 0 | 131.1966 | 0 | 1.3419 | 0 | 1.312 | 0 | 1.3419 | 1.312 | 16.6688 | 19.329 | 15.3269
39031.5679 | 2096 | 0 | 39031.5679 | 2160 | 0 |  | 2141.5 | 2360.5 | 127.9609 | 0 | 131.8681 | 0 | 1.2796 | 0 | 1.3187 | 0 | 1.2796 | 1.3187 | 22.3464 | 18.7213 | 21.0668
39031.57 | 2224 | 1 | 39031.57 | 2548 | 1 |  | 2326 | 2545 | 135.7753 | 0.06105 | 155.5556 | 0.06105 | 1.3578 | 0.0006105 | 1.5556 | 0.0006105 | 1.3571 | 1.5549 | 16.4604 | 0.64465 | 217.379
39031.5722 | 2489 | 5 | 39031.5722 | 1942 | 9 |  | 2511 | 2730 | 151.9536 | 0.30525 | 118.5592 | 0.54945 | 1.5195 | 0.0030525 | 1.1856 | 0.0054945 | 1.5165 | 1.1801 | 3.0508 | 37.9965 | 387.574

## C6-F12
Open Burn Test 8 |  |  | 2006-11-10 | 13:06 |  |  | Vs = |  | 153.8694 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 150 kW |  | Bundle | Ch. 6 & 12 | Cable C | Even - | Cable F |  | Even
Time-101 | N11 | N12 | Time-102 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R12-G | R6-12
39031.5422 | 0 | 0 | 39031.5422 | 0 | 0 |  | -78.5 | 140.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 503976 | 503976 | 503975.9997
39031.5443 | 0 | 0 | 39031.5444 | 0 | 0 |  | 106 | 325 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 503976 | 503976 | 503975.9997
39031.5465 | 0 | 0 | 39031.5465 | 0 | 0 |  | 291 | 510 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 503976 | 503976 | 503975.9997
39031.5486 | 0 | 0 | 39031.5486 | 0 | 0 |  | 475.5 | 694.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 503976 | 503976 | 503975.9997
39031.5508 | 0 | 0 | 39031.5508 | 0 | 0 |  | 660.5 | 879.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 503976 | 503976 | 503975.9997
39031.5529 | 0 | 0 | 39031.5529 | 0 | 0 |  | 845 | 1064 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 503976 | 503976 | 503975.9997
39031.555 | 0 | 0 | 39031.555 | 0 | 0 |  | 1030 | 1249 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 503976 | 503976 | 503975.9997
39031.5572 | 0 | 0 | 39031.5572 | 2480 | 0 |  | 1214.5 | 1433.5 | 0.030525 | 0 | 151.4042 | 0 | 0.00030525 | 0 | 1.514 | 0 | 0.00030525 | 1.514 | 503976 | 1.6282 | 503975.9997
39031.5593 | 595 | 0 | 39031.5593 | 2361 | 0 |  | 1399.5 | 1618.5 | 36.3248 | 0 | 144.1392 | 0 | 0.36325 | 0 | 1.4414 | 0 | 0.36325 | 1.4414 | 323.5933 | 6.7505 | 323.23
39031.5614 | 2068 | 0 | 39031.5615 | 2042 | 0 |  | 1584 | 1803 | 126.2515 | 0 | 124.6642 | 0 | 1.2625 | 0 | 1.2466 | 0 | 1.2625 | 1.2466 | 21.8752 | 23.427 | 20.6127
39031.5636 | 2269 | 0 | 39031.5636 | 2166 | 0 |  | 1769 | 1988 | 138.5226 | 0 | 132.2344 | 0 | 1.3852 | 0 | 1.3223 | 0 | 1.3852 | 1.3223 | 11.0789 | 16.361 | 9.6937
39031.5657 | 2032 | 0 | 39031.5657 | 2421 | 0 |  | 1953.5 | 2172.5 | 124.0537 | 0 | 147.8022 | 0 | 1.2405 | 0 | 1.478 | 0 | 1.2405 | 1.478 | 24.0344 | 4.1049 | 22.7939
39031.5679 | 2484 | 0 | 39031.5679 | 2072 | 0 |  | 2138.5 | 2357.5 | 151.6484 | 0 | 126.4957 | 0 | 1.5165 | 0 | 1.265 | 0 | 1.5165 | 1.265 | 1.4646 | 21.64 | 0.05191
39031.57 | 2262 | 0 | 39031.57 | 2092 | 2 |  | 2323 | 2542 | 138.0952 | 0 | 127.7167 | 0.1221 | 1.381 | 0 | 1.2772 | 0.001221 | 1.381 | 1.2759 | 11.4226 | 20.5923 | 10.0417
39031.5721 | 2095 | 0 | 39031.5722 | 2504 | 0 |  | 2508 | 2727 | 127.8999 | 0 | 152.8694 | 0 | 1.279 | 0 | 1.5287 | 0 | 1.279 | 1.5287 | 20.3045 | 0.65415 | 19.0255

## C6-F11
Open Burn Test 8 |  |  | 2006-11-10 | 13:06 |  |  | Vs = |  | 159.9744 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 150 kW |  | Bundle | Ch. 6 & 11 | Cable C | Even - | Cable F |  | Odd
Time-99 | N11 | N12 | Time-100 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R11-G | R6-11
39031.5422 | 0 | 0 | 39031.5422 | 0 | 0 |  | -81.5 | 137.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 523976 | 523976 | 523975.9997
39031.5443 | 0 | 0 | 39031.5443 | 0 | 0 |  | 103.5 | 322.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 523976 | 523976 | 523975.9997
39031.5464 | 0 | 1 | 39031.5465 | 0 | 0 |  | 288 | 507 | 0.030525 | 0.06105 | 0.030525 | 0 | 0.00030525 | 0.0006105 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 524176.0764 | 523976 | 261838.0286
39031.5486 | 0 | 0 | 39031.5486 | 0 | 0 |  | 472.5 | 691.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 523976 | 523976 | 523975.9997
39031.5507 | 0 | 0 | 39031.5507 | 0 | 0 |  | 657.5 | 876.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 523976 | 523976 | 523975.9997
39031.5529 | 0 | 0 | 39031.5529 | 0 | 0 |  | 842.5 | 1061.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 523976 | 523976 | 523975.9997
39031.555 | 0 | 0 | 39031.555 | 0 | 0 |  | 1027 | 1246 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 523976 | 523976 | 523975.9997
39031.5571 | 0 | 0 | 39031.5571 | 2303 | 0 |  | 1211.5 | 1430.5 | 0.030525 | 0 | 140.5983 | 0 | 0.00030525 | 0 | 1.406 | 0 | 0.00030525 | 1.406 | 523976 | 13.7812 | 523975.9997
39031.5593 | 513 | 0 | 39031.5593 | 2235 | 0 |  | 1396.5 | 1615.5 | 31.3187 | 0 | 136.4469 | 0 | 0.31319 | 0 | 1.3645 | 0 | 0.31319 | 1.3645 | 410.7953 | 17.243 | 410.4821
39031.5614 | 1783 | 0 | 39031.5614 | 2604 | 0 |  | 1581.5 | 1800.5 | 108.8523 | 0 | 158.9744 | 0 | 1.0885 | 0 | 1.5897 | 0 | 1.0885 | 1.5897 | 46.9647 | 0.62903 | 45.8761
39031.5635 | 2123 | 0 | 39031.5636 | 2442 | 0 |  | 1766 | 1985 | 129.6093 | 0 | 149.0842 | 0 | 1.2961 | 0 | 1.4908 | 0 | 1.2961 | 1.4908 | 23.4282 | 7.3047 | 22.1321
39031.5657 | 2099 | 0 | 39031.5657 | 2412 | 0 |  | 1951 | 2170 | 128.1441 | 0 | 147.2527 | 0 | 1.2814 | 0 | 1.4725 | 0 | 1.2814 | 1.4725 | 24.8394 | 8.6393 | 23.558
39031.5678 | 2574 | 0 | 39031.5678 | 2084 | 0 |  | 2135.5 | 2354.5 | 157.1429 | 0 | 127.2283 | 0 | 1.5714 | 0 | 1.2723 | 0 | 1.5714 | 1.2723 | 1.8019 | 25.738 | 0.23044
39031.57 | 2053 | 0 | 39031.57 | 2144 | 0 |  | 2320.5 | 2539.5 | 125.3358 | 0 | 130.8913 | 0 | 1.2534 | 0 | 1.3089 | 0 | 1.2534 | 1.3089 | 27.6366 | 22.2192 | 26.3833
39031.5721 | 2470 | 0 | 39031.5721 | 2021 | 0 |  | 2505.5 | 2724.5 | 150.7937 | 0 | 123.3822 | 0 | 1.5079 | 0 | 1.2338 | 0 | 1.5079 | 1.2338 | 6.0883 | 29.6576 | 4.5803

## C6-E10
Open Burn Test 8 |  |  | 2006-11-10 | 13:06 |  |  | Vs = |  | 158.0818 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 150 kW |  | Bundle | Ch. 6 & 10 | Cable C | Even - | Cable E |  | Even
Time-97 | N11 | N12 | Time-98 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R10-G | R6-10
39031.5421 | 0 | 0 | 39031.5421 | 0 | 0 |  | -84.5 | 134.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517776 | 517776 | 517775.9997
39031.5443 | 0 | 0 | 39031.5443 | 0 | 0 |  | 100.5 | 319.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517776 | 517776 | 517775.9997
39031.5464 | 0 | 0 | 39031.5464 | 0 | 0 |  | 285 | 504 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517776 | 517776 | 517775.9997
39031.5485 | 0 | 0 | 39031.5486 | 0 | 0 |  | 470 | 689 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517776 | 517776 | 517775.9997
39031.5507 | 0 | 0 | 39031.5507 | 0 | 0 |  | 654.5 | 873.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517776 | 517776 | 517775.9997
39031.5528 | 0 | 0 | 39031.5528 | 0 | 0 |  | 839.5 | 1058.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517776 | 517776 | 517775.9997
39031.555 | 0 | 0 | 39031.555 | 2420 | 0 |  | 1024 | 1243 | 0.030525 | 0 | 147.7411 | 0 | 0.00030525 | 0 | 1.4774 | 0 | 0.00030525 | 1.4774 | 517776 | 6.9992 | 517775.9997
39031.5571 | 0 | 0 | 39031.5571 | 2080 | 0 |  | 1209 | 1428 | 0.030525 | 0 | 126.9841 | 0 | 0.00030525 | 0 | 1.2698 | 0 | 0.00030525 | 1.2698 | 517776 | 24.4894 | 517775.9997
39031.5592 | 131 | 0 | 39031.5592 | 2262 | 0 |  | 1393.5 | 1612.5 | 7.9976 | 0 | 138.0952 | 0 | 0.079976 | 0 | 1.381 | 0 | 0.079976 | 1.381 | 1876.626 | 14.473 | 1876.546
39031.5614 | 2010 | 0 | 39031.5614 | 1970 | 0 |  | 1578.5 | 1797.5 | 122.7106 | 0 | 120.2686 | 0 | 1.2271 | 0 | 1.2027 | 0 | 1.2271 | 1.2027 | 28.8249 | 31.4406 | 27.5978
39031.5635 | 2221 | 0 | 39031.5635 | 2131 | 0 |  | 1763.5 | 1982.5 | 135.5922 | 0 | 130.0977 | 0 | 1.3559 | 0 | 1.301 | 0 | 1.3559 | 1.301 | 16.5862 | 21.5101 | 15.2303
39031.5656 | 2573 | 0 | 39031.5657 | 2424 | 0 |  | 1948 | 2167 | 157.0818 | 0 | 147.9853 | 0 | 1.5708 | 0 | 1.4799 | 0 | 1.5708 | 1.4799 | 0.63661 | 6.8226 | 0.93421
39031.5678 | 2270 | 0 | 39031.5678 | 2003 | 0 |  | 2133 | 2352 | 138.5836 | 0 | 122.2833 | 0 | 1.3858 | 0 | 1.2228 | 0 | 1.3858 | 1.2228 | 14.0696 | 29.2751 | 12.6838
39031.5699 | 2333 | 0 | 39031.5699 | 2226 | 0 |  | 2317.5 | 2536.5 | 142.4298 | 0 | 135.8974 | 0 | 1.4243 | 0 | 1.359 | 0 | 1.4243 | 1.359 | 10.9893 | 16.3243 | 9.565
39031.5721 | 2448 | 0 | 39031.5721 | 2123 | 0 |  | 2502.5 | 2721.5 | 149.4505 | 0 | 129.6093 | 0 | 1.4945 | 0 | 1.2961 | 0 | 1.4945 | 1.2961 | 5.7753 | 21.968 | 4.2808

## C6-E9
Open Burn Test 8 |  |  | 2006-11-10 | 13:06 |  |  | Vs = |  | 158.3871 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 150 kW |  | Bundle | Ch. 6 & 9 | Cable C | Even - | Cable E |  | Odd
Time-95 | N11 | N12 | Time-96 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R9-G | R6-9
39031.5421 | 0 | 0 | 39031.5421 | 1 | 0 |  | -87 | 132 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 518776 | 259338 | 518775.9997
39031.5442 | 0 | 0 | 39031.5442 | 0 | 0 |  | 97.5 | 316.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518776 | 518776 | 518775.9997
39031.5464 | 0 | 0 | 39031.5464 | 0 | 0 |  | 282.5 | 501.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518776 | 518776 | 518775.9997
39031.5485 | 0 | 0 | 39031.5485 | 0 | 0 |  | 467 | 686 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518776 | 518776 | 518775.9997
39031.5506 | 0 | 0 | 39031.5507 | 1912 | 3 |  | 652 | 871 | 0.030525 | 0 | 116.7277 | 0.18315 | 0.00030525 | 0 | 1.1673 | 0.0018315 | 0.00030525 | 1.1654 | 518776 | 35.9026 | 518775.9997
39031.5528 | 0 | 0 | 39031.5528 | 2001 | 1 |  | 836.5 | 1055.5 | 0.030525 | 0 | 122.1612 | 0.06105 | 0.00030525 | 0 | 1.2216 | 0.0006105 | 0.00030525 | 1.221 | 518776 | 29.719 | 518775.9997
39031.5549 | 0 | 0 | 39031.5549 | 2530 | 0 |  | 1021.5 | 1240.5 | 0.030525 | 0 | 154.4567 | 0 | 0.00030525 | 0 | 1.5446 | 0 | 0.00030525 | 1.5446 | 518776 | 2.5447 | 518775.9997
39031.5571 | 0 | 0 | 39031.5571 | 2578 | 0 |  | 1206.5 | 1425.5 | 0.030525 | 0 | 157.3871 | 0 | 0.00030525 | 0 | 1.5739 | 0 | 0.00030525 | 1.5739 | 518776 | 0.63538 | 518775.9997
39031.5592 | 229 | 0 | 39031.5592 | 1980 | 0 |  | 1391 | 1610 | 13.9805 | 0 | 120.8791 | 0 | 0.1398 | 0 | 1.2088 | 0 | 0.1398 | 1.2088 | 1032.917 | 31.0293 | 1032.7772
39031.5613 | 1912 | 0 | 39031.5614 | 2368 | 0 |  | 1575.5 | 1794.5 | 116.7277 | 0 | 144.5665 | 0 | 1.1673 | 0 | 1.4457 | 0 | 1.1673 | 1.4457 | 35.6893 | 9.56 | 34.5221
39031.5635 | 1979 | 1 | 39031.5635 | 2044 | 0 |  | 1760.5 | 1979.5 | 120.8181 | 0.06105 | 124.7863 | 0 | 1.2082 | 0.0006105 | 1.2479 | 0 | 1.2076 | 1.2479 | 31.1697 | 26.9266 | 13033.6521
39031.5656 | 2464 | 0 | 39031.5656 | 2546 | 0 |  | 1945.5 | 2164.5 | 150.4274 | 0 | 155.4335 | 0 | 1.5043 | 0 | 1.5543 | 0 | 1.5043 | 1.5543 | 5.2914 | 1.9002 | 3.7871
39031.5678 | 2036 | 0 | 39031.5678 | 2060 | 0 |  | 2130 | 2349 | 124.2979 | 0 | 125.7631 | 0 | 1.243 | 0 | 1.2576 | 0 | 1.243 | 1.2576 | 27.4253 | 25.9408 | 26.1824
39031.5699 | 2116 | 0 | 39031.5699 | 2066 | 1 |  | 2315 | 2534 | 129.1819 | 0 | 126.1294 | 0.06105 | 1.2918 | 0 | 1.2613 | 0.0006105 | 1.2918 | 1.2607 | 22.6078 | 25.6358 | 21.3159
39031.572 | 2065 | 0 | 39031.572 | 2520 | 0 |  | 2499.5 | 2718.5 | 126.0684 | 0 | 153.8462 | 0 | 1.2607 | 0 | 1.5385 | 0 | 1.2607 | 1.5385 | 25.6358 | 2.9516 | 24.3752

## C5-F12
Open Burn Test 8 |  |  | 2006-11-10 | 13:06 |  |  | Vs = |  | 159.2418 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 150 kW |  | Bundle | Ch. 5 & 12 | Cable C | Odd - | Cable F |  | Even
Time-89 | N11 | N12 | Time-90 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R12-G | R5-12
39031.542 | 0 | 0 | 39031.542 | 0 | 0 |  | -95.5 | 123.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 521576 | 521576 | 521575.9997
39031.5441 | 0 | 0 | 39031.5442 | 0 | 0 |  | 89 | 308 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 521576 | 521576 | 521575.9997
39031.5463 | 0 | 0 | 39031.5463 | 0 | 0 |  | 274 | 493 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 521576 | 521576 | 521575.9997
39031.5484 | 0 | 0 | 39031.5484 | 0 | 0 |  | 458.5 | 677.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 521576 | 521576 | 521575.9997
39031.5506 | 0 | 0 | 39031.5506 | 0 | 0 |  | 643.5 | 862.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 521576 | 521576 | 521575.9997
39031.5527 | 0 | 0 | 39031.5527 | 0 | 0 |  | 828.5 | 1047.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 521576 | 521576 | 521575.9997
39031.5548 | 0 | 0 | 39031.5548 | 0 | 0 |  | 1013 | 1232 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 521576 | 521576 | 521575.9997
39031.557 | 0 | 0 | 39031.557 | 2506 | 0 |  | 1198 | 1417 | 0.030525 | 0 | 152.9915 | 0 | 0.00030525 | 0 | 1.5299 | 0 | 0.00030525 | 1.5299 | 521576 | 4.0854 | 521575.9997
39031.5591 | 1735 | 0 | 39031.5591 | 2010 | 0 |  | 1382.5 | 1601.5 | 105.9219 | 0 | 122.7106 | 0 | 1.0592 | 0 | 1.2271 | 0 | 1.0592 | 1.2271 | 50.3389 | 29.7701 | 49.2797
39031.5612 | 2044 | 0 | 39031.5613 | 2579 | 0 |  | 1567.5 | 1786.5 | 124.7863 | 0 | 157.4481 | 0 | 1.2479 | 0 | 1.5745 | 0 | 1.2479 | 1.5745 | 27.6115 | 1.1392 | 26.3637
39031.5634 | 2244 | 0 | 39031.5634 | 2031 | 0 |  | 1752 | 1971 | 136.9963 | 0 | 123.9927 | 0 | 1.37 | 0 | 1.2399 | 0 | 1.37 | 1.2399 | 16.238 | 28.4284 | 14.868
39031.5655 | 2592 | 0 | 39031.5655 | 2171 | 0 |  | 1937 | 2156 | 158.2418 | 0 | 132.5397 | 0 | 1.5824 | 0 | 1.3254 | 0 | 1.5824 | 1.3254 | 0.63194 | 20.1465 | 0.95047
39031.5677 | 2482 | 0 | 39031.5677 | 2039 | 0 |  | 2121.5 | 2340.5 | 151.5263 | 0 | 124.4811 | 0 | 1.5153 | 0 | 1.2448 | 0 | 1.5153 | 1.2448 | 5.0919 | 27.9245 | 3.5766
39031.5698 | 2513 | 0 | 39031.5698 | 2064 | 0 |  | 2306.5 | 2525.5 | 153.4188 | 0 | 126.0073 | 0 | 1.5342 | 0 | 1.2601 | 0 | 1.5342 | 1.2601 | 3.7955 | 26.375 | 2.2613
39031.5719 | 1936 | 0 | 39031.572 | 2017 | 0 |  | 2491.5 | 2710.5 | 118.1929 | 0 | 123.138 | 0 | 1.1819 | 0 | 1.2314 | 0 | 1.1819 | 1.2314 | 34.7304 | 29.3198 | 33.5484

## C5-F11
Open Burn Test 8 |  |  | 2006-11-10 | 13:06 |  |  | Vs = |  | 154.9072 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 150 kW |  | Bundle | Ch. 5 & 11 | Cable C | Odd - | Cable F |  | Odd
Time-87 | N11 | N12 | Time-88 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R11-G | R5-11
39031.542 | 0 | 0 | 39031.542 | 0 | 0 |  | -98.5 | 120.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 507376 | 507376 | 507375.9997
39031.5441 | 0 | 1 | 39031.5441 | 0 | 0 |  | 86.5 | 305.5 | 0.030525 | 0.06105 | 0.030525 | 0 | 0.00030525 | 0.0006105 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 507576.0789 | 507376 | 253538.0296
39031.5462 | 0 | 0 | 39031.5463 | 0 | 0 |  | 271 | 490 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 507376 | 507376 | 507375.9997
39031.5484 | 0 | 0 | 39031.5484 | 0 | 0 |  | 456 | 675 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 507376 | 507376 | 507375.9997
39031.5505 | 0 | 0 | 39031.5505 | 0 | 0 |  | 640.5 | 859.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 507376 | 507376 | 507375.9997
39031.5527 | 0 | 0 | 39031.5527 | 0 | 0 |  | 825.5 | 1044.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 507376 | 507376 | 507375.9997
39031.5548 | 0 | 0 | 39031.5548 | 0 | 0 |  | 1010.5 | 1229.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 507376 | 507376 | 507375.9997
39031.5569 | 0 | 0 | 39031.557 | 2422 | 0 |  | 1195 | 1414 | 0.030525 | 0 | 147.8632 | 0 | 0.00030525 | 0 | 1.4786 | 0 | 0.00030525 | 1.4786 | 507376 | 4.7638 | 507375.9997
39031.5591 | 1933 | 0 | 39031.5591 | 2026 | 0 |  | 1379.5 | 1598.5 | 118.0098 | 0 | 123.6874 | 0 | 1.1801 | 0 | 1.2369 | 0 | 1.1801 | 1.2369 | 31.2664 | 25.2409 | 30.0863
39031.5612 | 2323 | 0 | 39031.5612 | 2520 | 0 |  | 1564.5 | 1783.5 | 141.8193 | 0 | 153.8462 | 0 | 1.4182 | 0 | 1.5385 | 0 | 1.4182 | 1.5385 | 9.2286 | 0.68968 | 7.8104
39031.5634 | 2501 | 0 | 39031.5634 | 2131 | 0 |  | 1749.5 | 1968.5 | 152.6862 | 0 | 130.0977 | 0 | 1.5269 | 0 | 1.301 | 0 | 1.5269 | 1.301 | 1.4546 | 19.0699 | 0.072244
39031.5655 | 2501 | 0 | 39031.5655 | 2311 | 0 |  | 1934 | 2153 | 152.6862 | 0 | 141.0867 | 0 | 1.5269 | 0 | 1.4109 | 0 | 1.5269 | 1.4109 | 1.4546 | 9.7958 | 0.072244
39031.5676 | 2170 | 0 | 39031.5677 | 2448 | 0 |  | 2119 | 2338 | 132.4786 | 0 | 149.4505 | 0 | 1.3248 | 0 | 1.4945 | 0 | 1.3248 | 1.4945 | 16.93 | 3.6511 | 15.6052
39031.5698 | 2360 | 0 | 39031.5698 | 2521 | 0 |  | 2303.5 | 2522.5 | 144.0781 | 0 | 153.9072 | 0 | 1.4408 | 0 | 1.5391 | 0 | 1.4408 | 1.5391 | 7.5161 | 0.64974 | 6.0753
39031.5719 | 1998 | 0 | 39031.5719 | 2257 | 0 |  | 2488.5 | 2707.5 | 121.978 | 0 | 137.79 | 0 | 1.2198 | 0 | 1.3779 | 0 | 1.2198 | 1.3779 | 26.996 | 12.4227 | 25.7762

## C5-E10
Open Burn Test 8 |  |  | 2006-11-10 | 13:06 |  |  | Vs = |  | 158.9365 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 150 kW |  | Bundle | Ch. 5 & 10 | Cable C | Odd - | Cable E |  | Even
Time-85 | N11 | N12 | Time-86 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R10-G | R5-10
39031.5419 | 0 | 0 | 39031.542 | 0 | 0 |  | -101 | 118 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 520576 | 520576 | 520575.9997
39031.5441 | 0 | 0 | 39031.5441 | 0 | 0 |  | 83.5 | 302.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 520576 | 520576 | 520575.9997
39031.5462 | 0 | 0 | 39031.5462 | 0 | 0 |  | 268.5 | 487.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 520576 | 520576 | 520575.9997
39031.5483 | 0 | 0 | 39031.5484 | 0 | 0 |  | 453 | 672 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 520576 | 520576 | 520575.9997
39031.5505 | 0 | 0 | 39031.5505 | 0 | 0 |  | 638 | 857 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 520576 | 520576 | 520575.9997
39031.5526 | 0 | 0 | 39031.5526 | 0 | 0 |  | 822.5 | 1041.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 520576 | 520576 | 520575.9997
39031.5548 | 0 | 0 | 39031.5548 | 2433 | 0 |  | 1007.5 | 1226.5 | 0.030525 | 0 | 148.5348 | 0 | 0.00030525 | 0 | 1.4853 | 0 | 0.00030525 | 1.4853 | 520576 | 7.0029 | 520575.9997
39031.5569 | 0 | 0 | 39031.5569 | 2178 | 0 |  | 1192.5 | 1411.5 | 0.030525 | 0 | 132.967 | 0 | 0.00030525 | 0 | 1.3297 | 0 | 0.00030525 | 1.3297 | 520576 | 19.5308 | 520575.9997
39031.559 | 1572 | 0 | 39031.5591 | 2116 | 0 |  | 1377 | 1596 | 95.9707 | 0 | 129.1819 | 0 | 0.95971 | 0 | 1.2918 | 0 | 0.95971 | 1.2918 | 65.6094 | 23.0331 | 64.6497
39031.5612 | 1865 | 0 | 39031.5612 | 2443 | 0 |  | 1561.5 | 1780.5 | 113.8584 | 0 | 149.1453 | 0 | 1.1386 | 0 | 1.4915 | 0 | 1.1386 | 1.4915 | 39.5914 | 6.5649 | 38.4528
39031.5633 | 2474 | 0 | 39031.5633 | 2587 | 0 |  | 1746.5 | 1965.5 | 151.0379 | 0 | 157.9365 | 0 | 1.5104 | 0 | 1.5794 | 0 | 1.5104 | 1.5794 | 5.2296 | 0.63317 | 3.7192
39031.5655 | 1993 | 0 | 39031.5655 | 2000 | 0 |  | 1931.5 | 2150.5 | 121.6728 | 0 | 122.1001 | 0 | 1.2167 | 0 | 1.221 | 0 | 1.2167 | 1.221 | 30.6262 | 30.169 | 29.4095
39031.5676 | 2046 | 0 | 39031.5676 | 2197 | 0 |  | 2116 | 2335 | 124.9084 | 0 | 134.127 | 0 | 1.2491 | 0 | 1.3413 | 0 | 1.2491 | 1.3413 | 27.2424 | 18.497 | 25.9933
39031.5697 | 2349 | 0 | 39031.5698 | 2056 | 0 |  | 2301 | 2520 | 143.4066 | 0 | 125.5189 | 0 | 1.4341 | 0 | 1.2552 | 0 | 1.4341 | 1.2552 | 10.8293 | 26.6235 | 9.3952
39031.5719 | 2428 | 0 | 39031.5719 | 2153 | 0 |  | 2485.5 | 2704.5 | 148.2295 | 0 | 131.4408 | 0 | 1.4823 | 0 | 1.3144 | 0 | 1.4823 | 1.3144 | 7.2232 | 20.9187 | 5.7409

## C5-E9
Open Burn Test 8 |  |  | 2006-11-10 | 13:06 |  |  | Vs = |  | 160.6459 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 150 kW |  | Bundle | Ch. 5 & 9 | Cable C | Odd - | Cable E |  | Odd
Time-83 | N11 | N12 | Time-84 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R9-G | R5-9
39031.5419 | 0 | 0 | 39031.5419 | 0 | 0 |  | -104 | 115 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 526176 | 526176 | 526175.9997
39031.544 | 0 | 0 | 39031.5441 | 0 | 0 |  | 81 | 300 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 526176 | 526176 | 526175.9997
39031.5462 | 0 | 0 | 39031.5462 | 0 | 0 |  | 265.5 | 484.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 526176 | 526176 | 526175.9997
39031.5483 | 0 | 0 | 39031.5483 | 0 | 0 |  | 450.5 | 669.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 526176 | 526176 | 526175.9997
39031.5505 | 0 | 0 | 39031.5505 | 1642 | 4 |  | 635 | 854 | 0.030525 | 0 | 100.2442 | 0.2442 | 0.00030525 | 0 | 1.0024 | 0.002442 | 0.00030525 | 1 | 526176 | 60.6459 | 526175.9997
39031.5526 | 0 | 0 | 39031.5526 | 1838 | 1 |  | 820 | 1039 | 0.030525 | 0 | 112.21 | 0.06105 | 0.00030525 | 0 | 1.1221 | 0.0006105 | 0.00030525 | 1.1215 | 526176 | 43.2433 | 526175.9997
39031.5547 | 0 | 0 | 39031.5547 | 2532 | 0 |  | 1004.5 | 1223.5 | 0.030525 | 0 | 154.5788 | 0 | 0.00030525 | 0 | 1.5458 | 0 | 0.00030525 | 1.5458 | 526176 | 3.925 | 526175.9997
39031.5569 | 0 | 0 | 39031.5569 | 2445 | 0 |  | 1189.5 | 1408.5 | 0.030525 | 0 | 149.2674 | 0 | 0.00030525 | 0 | 1.4927 | 0 | 0.00030525 | 1.4927 | 526176 | 7.6229 | 526175.9997
39031.559 | 1755 | 0 | 39031.559 | 2132 | 0 |  | 1374 | 1593 | 107.1429 | 0 | 130.1587 | 0 | 1.0714 | 0 | 1.3016 | 0 | 1.0714 | 1.3016 | 49.9362 | 23.4231 | 48.8648
39031.5611 | 1982 | 0 | 39031.5612 | 2118 | 0 |  | 1559 | 1778 | 121.0012 | 0 | 129.304 | 0 | 1.21 | 0 | 1.293 | 0 | 1.21 | 1.293 | 32.7639 | 24.2389 | 31.5539
39031.5633 | 2268 | 0 | 39031.5633 | 2615 | 0 |  | 1743.5 | 1962.5 | 138.4615 | 0 | 159.6459 | 0 | 1.3846 | 0 | 1.5965 | 0 | 1.3846 | 1.5965 | 16.022 | 0.62639 | 14.6374
39031.5654 | 1990 | 0 | 39031.5654 | 2160 | 0 |  | 1928.5 | 2147.5 | 121.4896 | 0 | 131.8681 | 0 | 1.2149 | 0 | 1.3187 | 0 | 1.2149 | 1.3187 | 32.2302 | 21.8231 | 31.0153
39031.5676 | 2589 | 0 | 39031.5676 | 2486 | 0 |  | 2113.5 | 2332.5 | 158.0586 | 0 | 151.7705 | 0 | 1.5806 | 0 | 1.5177 | 0 | 1.5806 | 1.5177 | 1.6369 | 5.8479 | 0.056339
39031.5697 | 2400 | 0 | 39031.5697 | 2587 | 0 |  | 2298 | 2517 | 146.5201 | 0 | 157.9365 | 0 | 1.4652 | 0 | 1.5794 | 0 | 1.4652 | 1.5794 | 9.6408 | 1.7155 | 8.1756
39031.5718 | 1969 | 0 | 39031.5719 | 2553 | 0 |  | 2482.5 | 2701.5 | 120.2076 | 0 | 155.8608 | 0 | 1.2021 | 0 | 1.5586 | 0 | 1.2021 | 1.5586 | 33.6404 | 3.0701 | 32.4384

## C5-C6
Open Burn Test 8 |  |  | 2006-11-10 | 13:06 |  |  | Vs = |  | 157.2882 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 150 kW |  | Bundle | Ch. 5 & 6 | Cable C | Odd-Even
Time-77 | N11 | N12 | Time-78 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R6-G | R5-6
39031.5418 | 0 | 0 | 39031.5418 | 0 | 0 |  | -112.5 | 106.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515176 | 515176 | 515175.9997
39031.5439 | 0 | 0 | 39031.544 | 0 | 0 |  | 72.5 | 291.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515176 | 515176 | 515175.9997
39031.5461 | 0 | 0 | 39031.5461 | 0 | 0 |  | 257 | 476 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515176 | 515176 | 515175.9997
39031.5482 | 0 | 0 | 39031.5482 | 0 | 0 |  | 442 | 661 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515176 | 515176 | 515175.9997
39031.5504 | 0 | 0 | 39031.5504 | 0 | 0 |  | 626.5 | 845.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515176 | 515176 | 515175.9997
39031.5525 | 0 | 0 | 39031.5525 | 0 | 0 |  | 811.5 | 1030.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515176 | 515176 | 515175.9997
39031.5546 | 0 | 0 | 39031.5547 | 0 | 0 |  | 996.5 | 1215.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515176 | 515176 | 515175.9997
39031.5568 | 0 | 0 | 39031.5568 | 0 | 0 |  | 1181 | 1400 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515176 | 515176 | 515175.9997
39031.5589 | 86 | 0 | 39031.5589 | 0 | 0 |  | 1365.5 | 1584.5 | 5.2503 | 0 | 0.030525 | 0 | 0.052503 | 0 | 0.00030525 | 0 | 0.052503 | 0.00030525 | 2895.7907 | 515176 | 2895.7382
39031.5611 | 1941 | 3 | 39031.5611 | 1999 | 1 |  | 1550.5 | 1769.5 | 118.4982 | 0.18315 | 122.0391 | 0.06105 | 1.185 | 0.0018315 | 1.2204 | 0.0006105 | 1.1832 | 1.2198 | 32.9616 | 28.9418 | 4731.3949
39031.5632 | 2092 | 0 | 39031.5632 | 2100 | 0 |  | 1735.5 | 1954.5 | 127.7167 | 0 | 128.2051 | 0 | 1.2772 | 0 | 1.2821 | 0 | 1.2772 | 1.2821 | 23.1539 | 22.6848 | 21.8768
39031.5653 | 2013 | 0 | 39031.5653 | 2255 | 0 |  | 1920 | 2139 | 122.8938 | 0 | 137.6679 | 0 | 1.2289 | 0 | 1.3767 | 0 | 1.2289 | 1.3767 | 27.9871 | 14.2519 | 26.7581
39031.5675 | 2260 | 0 | 39031.5675 | 2560 | 0 |  | 2105 | 2324 | 137.9731 | 0 | 156.2882 | 0 | 1.3797 | 0 | 1.5629 | 0 | 1.3797 | 1.5629 | 13.9991 | 0.63984 | 12.6194
39031.5696 | 1975 | 1 | 39031.5696 | 2537 | 1 |  | 2289.5 | 2508.5 | 120.5739 | 0.06105 | 154.884 | 0.06105 | 1.2057 | 0.0006105 | 1.5488 | 0.0006105 | 1.2051 | 1.5482 | 31.4911 | 1.5548 | 919.1713
39031.5717 | 2428 | 3 | 39031.5718 | 2485 | 3 |  | 2474.5 | 2693.5 | 148.2295 | 0.18315 | 151.7094 | 0.18315 | 1.4823 | 0.0018315 | 1.5171 | 0.0018315 | 1.4805 | 1.5153 | 6.3273 | 3.7534 | 175.3101

## B4-E10
Open Burn Test 8 |  |  | 2006-11-10 | 13:06 |  |  | Vs = |  | 158.9365 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 150 kW |  | Bundle | Ch. 4 & 10 | Cable B | Even - | Cable E |  | Even
Time-71 | N11 | N12 | Time-72 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R10-G | R4-10
39031.5417 | 0 | 0 | 39031.5417 | 0 | 0 |  | -120.5 | 98.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 520576 | 520576 | 520575.9997
39031.5438 | 0 | 0 | 39031.5439 | 0 | 0 |  | 64 | 283 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 520576 | 520576 | 520575.9997
39031.546 | 0 | 0 | 39031.546 | 0 | 0 |  | 248.5 | 467.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 520576 | 520576 | 520575.9997
39031.5481 | 0 | 0 | 39031.5481 | 0 | 0 |  | 433.5 | 652.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 520576 | 520576 | 520575.9997
39031.5503 | 0 | 0 | 39031.5503 | 0 | 0 |  | 618.5 | 837.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 520576 | 520576 | 520575.9997
39031.5524 | 0 | 0 | 39031.5524 | 0 | 1 |  | 803 | 1022 | 0.030525 | 0 | 0.030525 | 0.06105 | 0.00030525 | 0 | 0.00030525 | 0.0006105 | 0.00030525 | 0.00030525 | 520576 | 520576 | 520575.9997
39031.5545 | 0 | 0 | 39031.5546 | 2556 | 0 |  | 988 | 1207 | 0.030525 | 0 | 156.044 | 0 | 0.00030525 | 0 | 1.5604 | 0 | 0.00030525 | 1.5604 | 520576 | 1.8537 | 520575.9997
39031.5567 | 0 | 0 | 39031.5567 | 2431 | 0 |  | 1172.5 | 1391.5 | 0.030525 | 0 | 148.4127 | 0 | 0.00030525 | 0 | 1.4841 | 0 | 0.00030525 | 1.4841 | 520576 | 7.0909 | 520575.9997
39031.5588 | 0 | 0 | 39031.5588 | 2587 | 0 |  | 1357.5 | 1576.5 | 0.030525 | 0 | 157.9365 | 0 | 0.00030525 | 0 | 1.5794 | 0 | 0.00030525 | 1.5794 | 520576 | 0.63317 | 520575.9997
39031.561 | 1823 | 0 | 39031.561 | 2157 | 0 |  | 1542.5 | 1761.5 | 111.2943 | 0 | 131.685 | 0 | 1.1129 | 0 | 1.3168 | 0 | 1.1129 | 1.3168 | 42.8075 | 20.6945 | 41.6945
39031.5631 | 2224 | 0 | 39031.5631 | 2148 | 0 |  | 1727 | 1946 | 135.7753 | 0 | 131.1355 | 0 | 1.3578 | 0 | 1.3114 | 0 | 1.3578 | 1.3114 | 17.0585 | 21.2002 | 15.7007
39031.5652 | 2570 | 0 | 39031.5652 | 2163 | 0 |  | 1911.5 | 2130.5 | 156.8987 | 0 | 132.0513 | 0 | 1.569 | 0 | 1.3205 | 0 | 1.569 | 1.3205 | 1.2988 | 20.3597 | 0.27015
39031.5674 | 2283 | 0 | 39031.5674 | 1996 | 0 |  | 2096.5 | 2315.5 | 139.3773 | 0 | 121.8559 | 0 | 1.3938 | 0 | 1.2186 | 0 | 1.3938 | 1.2186 | 14.0333 | 30.4299 | 12.6395
39031.5695 | 2551 | 0 | 39031.5695 | 2053 | 0 |  | 2281.5 | 2500.5 | 155.7387 | 0 | 125.3358 | 0 | 1.5574 | 0 | 1.2534 | 0 | 1.5574 | 1.2534 | 2.0533 | 26.8086 | 0.49593
39031.5716 | 2482 | 0 | 39031.5717 | 1988 | 0 |  | 2466 | 2685 | 151.5263 | 0 | 121.3675 | 0 | 1.5153 | 0 | 1.2137 | 0 | 1.5153 | 1.2137 | 4.8904 | 30.9547 | 3.3751

## B4-E9
Open Burn Test 8 |  |  | 2006-11-10 | 13:06 |  |  | Vs = |  | 159.8523 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 150 kW |  | Bundle | Ch. 4 & 9 | Cable B | Even - | Cable E |  | Odd
Time-69 | N11 | N12 | Time-70 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R9-G | R4-9
39031.5417 | 0 | 0 | 39031.5417 | 0 | 0 |  | -123.5 | 95.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 523576 | 523576 | 523575.9997
39031.5438 | 0 | 0 | 39031.5438 | 0 | 0 |  | 61 | 280 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 523576 | 523576 | 523575.9997
39031.5459 | 0 | 0 | 39031.546 | 0 | 0 |  | 246 | 465 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 523576 | 523576 | 523575.9997
39031.5481 | 0 | 0 | 39031.5481 | 0 | 0 |  | 430.5 | 649.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 523576 | 523576 | 523575.9997
39031.5502 | 0 | 0 | 39031.5502 | 2181 | 0 |  | 615.5 | 834.5 | 0.030525 | 0 | 133.1502 | 0 | 0.00030525 | 0 | 1.3315 | 0 | 0.00030525 | 1.3315 | 523576 | 20.0541 | 523575.9997
39031.5524 | 0 | 0 | 39031.5524 | 2212 | 4 |  | 800.5 | 1019.5 | 0.030525 | 0 | 135.0427 | 0.2442 | 0.00030525 | 0 | 1.3504 | 0.002442 | 0.00030525 | 1.348 | 523576 | 18.5861 | 523575.9997
39031.5545 | 0 | 0 | 39031.5545 | 2018 | 0 |  | 985 | 1204 | 0.030525 | 0 | 123.199 | 0 | 0.00030525 | 0 | 1.232 | 0 | 0.00030525 | 1.232 | 523576 | 29.7512 | 523575.9997
39031.5566 | 0 | 0 | 39031.5567 | 2213 | 0 |  | 1170 | 1389 | 0.030525 | 0 | 135.1038 | 0 | 0.00030525 | 0 | 1.351 | 0 | 0.00030525 | 1.351 | 523576 | 18.3181 | 523575.9997
39031.5588 | 0 | 0 | 39031.5588 | 2541 | 0 |  | 1354.5 | 1573.5 | 0.030525 | 0 | 155.1282 | 0 | 0.00030525 | 0 | 1.5513 | 0 | 0.00030525 | 1.5513 | 523576 | 3.0453 | 523575.9997
39031.5609 | 1889 | 0 | 39031.5609 | 2566 | 0 |  | 1539.5 | 1758.5 | 115.3236 | 0 | 156.6545 | 0 | 1.1532 | 0 | 1.5665 | 0 | 1.1532 | 1.5665 | 38.612 | 2.0413 | 37.4587
39031.5631 | 2181 | 0 | 39031.5631 | 2129 | 0 |  | 1724 | 1943 | 133.1502 | 0 | 129.9756 | 0 | 1.3315 | 0 | 1.2998 | 0 | 1.3315 | 1.2998 | 20.0541 | 22.9864 | 18.7226
39031.5652 | 2184 | 0 | 39031.5652 | 2602 | 0 |  | 1909 | 2128 | 133.3333 | 0 | 158.8523 | 0 | 1.3333 | 0 | 1.5885 | 0 | 1.3333 | 1.5885 | 19.8892 | 0.62952 | 18.5559
39031.5673 | 2072 | 0 | 39031.5673 | 2568 | 0 |  | 2093.5 | 2312.5 | 126.4957 | 0 | 156.7766 | 0 | 1.265 | 0 | 1.5678 | 0 | 1.265 | 1.5678 | 26.3697 | 1.9618 | 25.1047
39031.5695 | 2248 | 0 | 39031.5695 | 2275 | 0 |  | 2278.5 | 2497.5 | 137.2405 | 0 | 138.8889 | 0 | 1.3724 | 0 | 1.3889 | 0 | 1.3724 | 1.3889 | 16.476 | 15.0936 | 15.1036
39031.5716 | 2333 | 0 | 39031.5716 | 2081 | 0 |  | 2463.5 | 2682.5 | 142.4298 | 0 | 127.0452 | 0 | 1.4243 | 0 | 1.2705 | 0 | 1.4243 | 1.2705 | 12.2323 | 25.8232 | 10.808

## B4-D8
Open Burn Test 8 |  |  | 2006-11-10 | 13:06 |  |  | Vs = |  | 155.0904 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 150 kW |  | Bundle | Ch. 4 & 8 | Cable B | Even - | Cable D |  | Even
Time-67 | N11 | N12 | Time-68 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R8-G | R4-8
39031.5416 | 0 | 0 | 39031.5417 | 0 | 0 |  | -126.5 | 92.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 507976 | 507976 | 507975.9997
39031.5438 | 0 | 0 | 39031.5438 | 0 | 0 |  | 58.5 | 277.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 507976 | 507976 | 507975.9997
39031.5459 | 0 | 0 | 39031.5459 | 0 | 0 |  | 243 | 462 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 507976 | 507976 | 507975.9997
39031.5481 | 0 | 0 | 39031.5481 | 0 | 0 |  | 428 | 647 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 507976 | 507976 | 507975.9997
39031.5502 | 0 | 0 | 39031.5502 | 0 | 0 |  | 612.5 | 831.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 507976 | 507976 | 507975.9997
39031.5523 | 0 | 0 | 39031.5523 | 0 | 0 |  | 797.5 | 1016.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 507976 | 507976 | 507975.9997
39031.5545 | 0 | 0 | 39031.5545 | 96 | 0 |  | 982.5 | 1201.5 | 0.030525 | 0 | 5.8608 | 0 | 0.00030525 | 0 | 0.058608 | 0 | 0.00030525 | 0.058608 | 507976 | 2546.2292 | 507975.9997
39031.5566 | 0 | 0 | 39031.5566 | 1937 | 0 |  | 1167 | 1386 | 0.030525 | 0 | 118.254 | 0 | 0.00030525 | 0 | 1.1825 | 0 | 0.00030525 | 1.1825 | 507976 | 31.1502 | 507975.9997
39031.5587 | 0 | 0 | 39031.5588 | 1960 | 0 |  | 1351.5 | 1570.5 | 0.030525 | 0 | 119.6581 | 0 | 0.00030525 | 0 | 1.1966 | 0 | 0.00030525 | 1.1966 | 507976 | 29.6112 | 507975.9997
39031.5609 | 1771 | 0 | 39031.5609 | 2262 | 0 |  | 1536.5 | 1755.5 | 108.1197 | 0 | 138.0952 | 0 | 1.0812 | 0 | 1.381 | 0 | 1.0812 | 1.381 | 43.4433 | 12.3068 | 42.3621
39031.563 | 2452 | 0 | 39031.563 | 2100 | 0 |  | 1721.5 | 1940.5 | 149.6947 | 0 | 128.2051 | 0 | 1.4969 | 0 | 1.2821 | 0 | 1.4969 | 1.2821 | 3.6044 | 20.9705 | 2.1075
39031.5652 | 2454 | 0 | 39031.5652 | 2075 | 0 |  | 1906 | 2125 | 149.8168 | 0 | 126.6789 | 0 | 1.4982 | 0 | 1.2668 | 0 | 1.4982 | 1.2668 | 3.52 | 22.428 | 2.0218
39031.5673 | 1960 | 0 | 39031.5673 | 2524 | 0 |  | 2091 | 2310 | 119.6581 | 0 | 154.0904 | 0 | 1.1966 | 0 | 1.5409 | 0 | 1.1966 | 1.5409 | 29.6112 | 0.64897 | 28.4146
39031.5694 | 2136 | 0 | 39031.5695 | 1962 | 0 |  | 2275.5 | 2494.5 | 130.4029 | 0 | 119.7802 | 0 | 1.304 | 0 | 1.1978 | 0 | 1.304 | 1.1978 | 18.9316 | 29.4791 | 17.6276
39031.5716 | 1917 | 4 | 39031.5716 | 2431 | 0 |  | 2460.5 | 2679.5 | 117.033 | 0.2442 | 148.4127 | 0 | 1.1703 | 0.002442 | 1.4841 | 0 | 1.1679 | 1.4841 | 34.1747 | 4.4994 | 666.7092

## B4-D7
Open Burn Test 8 |  |  | 2006-11-10 | 13:06 |  |  | Vs = |  | 157.5934 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 150 kW |  | Bundle | Ch. 4 & 7 | Cable B | Even - | Cable D |  | Odd
Time-65 | N11 | N12 | Time-66 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R7-G | R4-7
39031.5416 | 0 | 0 | 39031.5416 | 0 | 0 |  | -129 | 90 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 516176 | 516176 | 516175.9997
39031.5437 | 0 | 0 | 39031.5438 | 0 | 0 |  | 55.5 | 274.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 516176 | 516176 | 516175.9997
39031.5459 | 0 | 0 | 39031.5459 | 0 | 0 |  | 240.5 | 459.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 516176 | 516176 | 516175.9997
39031.548 | 0 | 0 | 39031.548 | 0 | 0 |  | 425 | 644 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 516176 | 516176 | 516175.9997
39031.5502 | 0 | 0 | 39031.5502 | 0 | 0 |  | 610 | 829 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 516176 | 516176 | 516175.9997
39031.5523 | 0 | 0 | 39031.5523 | 0 | 0 |  | 794.5 | 1013.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 516176 | 516176 | 516175.9997
39031.5544 | 0 | 0 | 39031.5545 | 65 | 0 |  | 979.5 | 1198.5 | 0.030525 | 0 | 3.9683 | 0 | 0.00030525 | 0 | 0.039683 | 0 | 0.00030525 | 0.039683 | 516176 | 3871.3538 | 516175.9997
39031.5566 | 0 | 0 | 39031.5566 | 2034 | 0 |  | 1164.5 | 1383.5 | 0.030525 | 0 | 124.1758 | 0 | 0.00030525 | 0 | 1.2418 | 0 | 0.00030525 | 1.2418 | 516176 | 26.9115 | 516175.9997
39031.5587 | 0 | 0 | 39031.5587 | 2520 | 0 |  | 1349 | 1568 | 0.030525 | 0 | 153.8462 | 0 | 0.00030525 | 0 | 1.5385 | 0 | 0.00030525 | 1.5385 | 516176 | 2.4357 | 516175.9997
39031.5609 | 1723 | 0 | 39031.5609 | 2464 | 0 |  | 1534 | 1753 | 105.1893 | 0 | 150.4274 | 0 | 1.0519 | 0 | 1.5043 | 0 | 1.0519 | 1.5043 | 49.8189 | 4.7638 | 48.767
39031.563 | 2095 | 0 | 39031.563 | 2565 | 0 |  | 1718.5 | 1937.5 | 127.8999 | 0 | 156.5934 | 0 | 1.279 | 0 | 1.5659 | 0 | 1.279 | 1.5659 | 23.2162 | 0.6386 | 21.9372
39031.5651 | 2314 | 0 | 39031.5652 | 1978 | 1 |  | 1903.5 | 2122.5 | 141.2698 | 0 | 120.757 | 0.06105 | 1.4127 | 0 | 1.2076 | 0.0006105 | 1.4127 | 1.207 | 11.5549 | 30.5706 | 10.1422
39031.5673 | 1971 | 0 | 39031.5673 | 2265 | 0 |  | 2088 | 2307 | 120.3297 | 0 | 138.2784 | 0 | 1.2033 | 0 | 1.3828 | 0 | 1.2033 | 1.3828 | 30.968 | 13.9682 | 29.7647
39031.5694 | 1986 | 0 | 39031.5694 | 2159 | 0 |  | 2273 | 2492 | 121.2454 | 0 | 131.8071 | 0 | 1.2125 | 0 | 1.3181 | 0 | 1.2125 | 1.3181 | 29.9789 | 19.5637 | 28.7664
39031.5716 | 2440 | 1 | 39031.5716 | 1908 | 0 |  | 2457.5 | 2676.5 | 148.9621 | 0.06105 | 116.4835 | 0 | 1.4896 | 0.0006105 | 1.1648 | 0 | 1.489 | 1.1648 | 5.8034 | 35.2925 | 3661.9593

## B4-C6
Open Burn Test 8 |  |  | 2006-11-10 | 13:06 |  |  | Vs = |  | 158.9976 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 150 kW |  | Bundle | Ch. 4 & 6 | Cable B | Even - | Cable C |  | Even
Time-63 | N11 | N12 | Time-64 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R6-G | R4-6
39031.5416 | 0 | 0 | 39031.5416 | 0 | 0 |  | -132 | 87 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 520776 | 520776 | 520775.9997
39031.5437 | 0 | 0 | 39031.5437 | 0 | 0 |  | 52.5 | 271.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 520776 | 520776 | 520775.9997
39031.5459 | 0 | 0 | 39031.5459 | 0 | 0 |  | 237.5 | 456.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 520776 | 520776 | 520775.9997
39031.548 | 0 | 0 | 39031.548 | 0 | 0 |  | 422.5 | 641.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 520776 | 520776 | 520775.9997
39031.5501 | 0 | 0 | 39031.5502 | 0 | 0 |  | 607 | 826 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 520776 | 520776 | 520775.9997
39031.5523 | 0 | 0 | 39031.5523 | 0 | 0 |  | 792 | 1011 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 520776 | 520776 | 520775.9997
39031.5544 | 0 | 0 | 39031.5544 | 0 | 0 |  | 976.5 | 1195.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 520776 | 520776 | 520775.9997
39031.5566 | 0 | 0 | 39031.5566 | 0 | 0 |  | 1161.5 | 1380.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 520776 | 520776 | 520775.9997
39031.5587 | 0 | 0 | 39031.5587 | 0 | 0 |  | 1346.5 | 1565.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 520776 | 520776 | 520775.9997
39031.5608 | 1709 | 0 | 39031.5608 | 2086 | 0 |  | 1531 | 1750 | 104.3346 | 0 | 127.3504 | 0 | 1.0433 | 0 | 1.2735 | 0 | 1.0433 | 1.2735 | 52.392 | 24.8504 | 51.3487
39031.563 | 2470 | 0 | 39031.563 | 2054 | 0 |  | 1715.5 | 1934.5 | 150.7937 | 0 | 125.3968 | 0 | 1.5079 | 0 | 1.254 | 0 | 1.5079 | 1.254 | 5.4405 | 26.7955 | 3.9325
39031.5651 | 2145 | 0 | 39031.5651 | 2039 | 0 |  | 1900.5 | 2119.5 | 130.9524 | 0 | 124.4811 | 0 | 1.3095 | 0 | 1.2448 | 0 | 1.3095 | 1.2448 | 21.4163 | 27.7283 | 20.1068
39031.5672 | 2127 | 0 | 39031.5673 | 2588 | 0 |  | 2085.5 | 2304.5 | 129.8535 | 0 | 157.9976 | 0 | 1.2985 | 0 | 1.58 | 0 | 1.2985 | 1.58 | 22.4438 | 0.63292 | 21.1453
39031.5694 | 1967 | 0 | 39031.5694 | 2191 | 0 |  | 2270 | 2489 | 120.0855 | 0 | 133.7607 | 0 | 1.2009 | 0 | 1.3376 | 0 | 1.2009 | 1.3376 | 32.4037 | 18.8672 | 31.2028
39031.5715 | 2114 | 1 | 39031.5715 | 2367 | 1 |  | 2454.5 | 2673.5 | 129.0598 | 0.06105 | 144.5055 | 0.06105 | 1.2906 | 0.0006105 | 1.4451 | 0.0006105 | 1.29 | 1.4444 | 23.3176 | 10.0512 | 4469.6014

## B4-C5
Open Burn Test 8 |  |  | 2006-11-10 | 13:06 |  |  | Vs = |  | 156.8608 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 150 kW |  | Bundle | Ch. 4 & 5 | Cable B | Even - | Cable C |  | Odd
Time-61 | N11 | N12 | Time-62 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R5-G | R4-5
39031.5416 | 0 | 0 | 39031.5416 | 0 | 0 |  | -134.5 | 84.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 513776 | 513776 | 513775.9997
39031.5437 | 0 | 0 | 39031.5437 | 0 | 0 |  | 50 | 269 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 513776 | 513776 | 513775.9997
39031.5458 | 0 | 0 | 39031.5458 | 0 | 0 |  | 234.5 | 453.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 513776 | 513776 | 513775.9997
39031.548 | 0 | 0 | 39031.548 | 0 | 0 |  | 419.5 | 638.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 513776 | 513776 | 513775.9997
39031.5501 | 0 | 0 | 39031.5501 | 0 | 0 |  | 604.5 | 823.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 513776 | 513776 | 513775.9997
39031.5522 | 0 | 0 | 39031.5523 | 0 | 0 |  | 789 | 1008 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 513776 | 513776 | 513775.9997
39031.5544 | 0 | 0 | 39031.5544 | 0 | 0 |  | 974 | 1193 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 513776 | 513776 | 513775.9997
39031.5565 | 0 | 0 | 39031.5565 | 0 | 0 |  | 1158.5 | 1377.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 513776 | 513776 | 513775.9997
39031.5587 | 0 | 0 | 39031.5587 | 11 | 0 |  | 1343.5 | 1562.5 | 0.030525 | 0 | 0.67155 | 0 | 0.00030525 | 0 | 0.0067155 | 0 | 0.00030525 | 0.0067155 | 513776 | 23258 | 513775.9997
39031.5608 | 1802 | 0 | 39031.5608 | 1920 | 0 |  | 1528.5 | 1747.5 | 110.0122 | 0 | 117.2161 | 0 | 1.1001 | 0 | 1.1722 | 0 | 1.1001 | 1.1722 | 42.5849 | 33.8219 | 41.4848
39031.5629 | 2253 | 0 | 39031.563 | 2553 | 0 |  | 1713 | 1932 | 137.5458 | 0 | 155.8608 | 0 | 1.3755 | 0 | 1.5586 | 0 | 1.3755 | 1.5586 | 14.0426 | 0.6416 | 12.6672
39031.5651 | 1975 | 0 | 39031.5651 | 2175 | 0 |  | 1897.5 | 2116.5 | 120.5739 | 0 | 132.7839 | 0 | 1.2057 | 0 | 1.3278 | 0 | 1.2057 | 1.3278 | 30.0952 | 18.1324 | 28.8895
39031.5672 | 2214 | 0 | 39031.5672 | 2127 | 0 |  | 2082.5 | 2301.5 | 135.1648 | 0 | 129.8535 | 0 | 1.3516 | 0 | 1.2985 | 0 | 1.3516 | 1.2985 | 16.0515 | 20.7983 | 14.6998
39031.5694 | 2085 | 0 | 39031.5694 | 2026 | 0 |  | 2267.5 | 2486.5 | 127.2894 | 0 | 123.6874 | 0 | 1.2729 | 0 | 1.2369 | 0 | 1.2729 | 1.2369 | 23.2317 | 26.8203 | 21.9588
39031.5715 | 2490 | 0 | 39031.5715 | 1911 | 0 |  | 2452 | 2671 | 152.0147 | 0 | 116.6667 | 0 | 1.5201 | 0 | 1.1667 | 0 | 1.5201 | 1.1667 | 3.188 | 34.4521 | 1.6678

## B3-E10
Open Burn Test 8 |  |  | 2006-11-10 | 13:06 |  |  | Vs = |  | 160.0965 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 150 kW |  | Bundle | Ch. 3 & 10 | Ch. 3 & 9 | Cable B | Odd - |  | Cable E | Even
Time-55 | N11 | N12 | Time-56 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R10-G | R3-10
39031.5414 | 0 | 0 | 39031.5415 | 0 | 0 |  | -143 | 76 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 524376 | 524376 | 524375.9997
39031.5436 | 0 | 0 | 39031.5436 | 0 | 0 |  | 41.5 | 260.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 524376 | 524376 | 524375.9997
39031.5457 | 0 | 0 | 39031.5457 | 0 | 0 |  | 226.5 | 445.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 524376 | 524376 | 524375.9997
39031.5479 | 0 | 0 | 39031.5479 | 0 | 0 |  | 411 | 630 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 524376 | 524376 | 524375.9997
39031.55 | 0 | 0 | 39031.55 | 0 | 0 |  | 596 | 815 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 524376 | 524376 | 524375.9997
39031.5521 | 0 | 0 | 39031.5522 | 0 | 0 |  | 780.5 | 999.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 524376 | 524376 | 524375.9997
39031.5543 | 0 | 0 | 39031.5543 | 1998 | 0 |  | 965.5 | 1184.5 | 0.030525 | 0 | 121.978 | 0 | 0.00030525 | 0 | 1.2198 | 0 | 0.00030525 | 1.2198 | 524376 | 31.2503 | 524375.9997
39031.5564 | 0 | 0 | 39031.5564 | 2114 | 0 |  | 1150 | 1369 | 0.030525 | 0 | 129.0598 | 0 | 0.00030525 | 0 | 1.2906 | 0 | 0.00030525 | 1.2906 | 524376 | 24.0482 | 524375.9997
39031.5586 | 0 | 0 | 39031.5586 | 2102 | 0 |  | 1335 | 1554 | 0.030525 | 0 | 128.3272 | 0 | 0.00030525 | 0 | 1.2833 | 0 | 0.00030525 | 1.2833 | 524376 | 24.7564 | 524375.9997
39031.5607 | 1643 | 0 | 39031.5607 | 2499 | 0 |  | 1519.5 | 1738.5 | 100.3053 | 0 | 152.5641 | 0 | 1.0031 | 0 | 1.5256 | 0 | 1.0031 | 1.5256 | 59.6093 | 4.9372 | 58.6062
39031.5628 | 1907 | 0 | 39031.5628 | 2379 | 0 |  | 1704.5 | 1923.5 | 116.4225 | 0 | 145.2381 | 0 | 1.1642 | 0 | 1.4524 | 0 | 1.1642 | 1.4524 | 37.5134 | 10.2303 | 36.3491
39031.565 | 2497 | 0 | 39031.565 | 2372 | 0 |  | 1889.5 | 2108.5 | 152.442 | 0 | 144.8107 | 0 | 1.5244 | 0 | 1.4481 | 0 | 1.5244 | 1.4481 | 5.0212 | 10.5556 | 3.4968
39031.5671 | 2260 | 0 | 39031.5671 | 2140 | 0 |  | 2074 | 2293 | 137.9731 | 0 | 130.6471 | 0 | 1.3797 | 0 | 1.3065 | 0 | 1.3797 | 1.3065 | 16.0345 | 22.5411 | 14.6548
39031.5692 | 1962 | 0 | 39031.5693 | 2382 | 0 |  | 2259 | 2478 | 119.7802 | 0 | 145.4212 | 0 | 1.1978 | 0 | 1.4542 | 0 | 1.1978 | 1.4542 | 33.6585 | 10.0915 | 32.4607
39031.5714 | 1902 | 0 | 39031.5714 | 2606 | 0 |  | 2443.5 | 2662.5 | 116.1172 | 0 | 159.0965 | 0 | 1.1612 | 0 | 1.591 | 0 | 1.1612 | 1.591 | 37.8749 | 0.62855 | 36.7137

## B3-E9
Open Burn Test 8 |  |  | 2006-11-10 | 13:06 |  |  | Vs = |  | 158.0208 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 150 kW |  | Bundle | Ch. 3 & 9 | Cable B | Odd - | Cable E |  | Odd
Time-53 | N11 | N12 | Time-54 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R9-G | R3-9
39031.5414 | 0 | 0 | 39031.5414 | 0 | 0 |  | -146 | 73 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517576 | 517576 | 517575.9997
39031.5436 | 0 | 0 | 39031.5436 | 0 | 0 |  | 39 | 258 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517576 | 517576 | 517575.9997
39031.5457 | 0 | 0 | 39031.5457 | 0 | 0 |  | 223.5 | 442.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517576 | 517576 | 517575.9997
39031.5478 | 0 | 0 | 39031.5478 | 0 | 0 |  | 408.5 | 627.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517576 | 517576 | 517575.9997
39031.55 | 0 | 0 | 39031.55 | 2228 | 5 |  | 593 | 812 | 0.030525 | 0 | 136.0195 | 0.30525 | 0.00030525 | 0 | 1.3602 | 0.0030525 | 0.00030525 | 1.3571 | 517576 | 16.4363 | 517575.9997
39031.5521 | 0 | 0 | 39031.5521 | 2226 | 3 |  | 778 | 997 | 0.030525 | 0 | 135.8974 | 0.18315 | 0.00030525 | 0 | 1.359 | 0.0018315 | 0.00030525 | 1.3571 | 517576 | 16.4363 | 517575.9997
39031.5542 | 0 | 0 | 39031.5543 | 2164 | 0 |  | 962.5 | 1181.5 | 0.030525 | 0 | 132.1123 | 0 | 0.00030525 | 0 | 1.3211 | 0 | 0.00030525 | 1.3211 | 517576 | 19.6109 | 517575.9997
39031.5564 | 0 | 0 | 39031.5564 | 2402 | 0 |  | 1147.5 | 1366.5 | 0.030525 | 0 | 146.6422 | 0 | 0.00030525 | 0 | 1.4664 | 0 | 0.00030525 | 1.4664 | 517576 | 7.7594 | 517575.9997
39031.5585 | 0 | 0 | 39031.5585 | 1989 | 0 |  | 1332.5 | 1551.5 | 0.030525 | 0 | 121.4286 | 0 | 0.00030525 | 0 | 1.2143 | 0 | 0.00030525 | 1.2143 | 517576 | 30.1347 | 517575.9997
39031.5607 | 1647 | 0 | 39031.5607 | 2185 | 0 |  | 1517 | 1736 | 100.5495 | 0 | 133.3944 | 0 | 1.0055 | 0 | 1.3339 | 0 | 1.0055 | 1.3339 | 57.1573 | 18.4613 | 56.1518
39031.5628 | 2097 | 0 | 39031.5628 | 2442 | 0 |  | 1701.5 | 1920.5 | 128.022 | 0 | 149.0842 | 0 | 1.2802 | 0 | 1.4908 | 0 | 1.2802 | 1.4908 | 23.4325 | 5.9943 | 22.1523
39031.5649 | 1997 | 0 | 39031.565 | 2572 | 0 |  | 1886.5 | 2105.5 | 121.917 | 0 | 157.0208 | 0 | 1.2192 | 0 | 1.5702 | 0 | 1.2192 | 1.5702 | 29.6134 | 0.63686 | 28.3943
39031.5671 | 2028 | 0 | 39031.5671 | 2118 | 0 |  | 2071.5 | 2290.5 | 123.8095 | 0 | 129.304 | 0 | 1.2381 | 0 | 1.293 | 0 | 1.2381 | 1.293 | 27.6321 | 22.2087 | 26.3941
39031.5692 | 2501 | 0 | 39031.5692 | 2562 | 0 |  | 2256 | 2475 | 152.6862 | 0 | 156.4103 | 0 | 1.5269 | 0 | 1.5641 | 0 | 1.5269 | 1.5641 | 3.4938 | 1.0297 | 1.9669
39031.5714 | 1980 | 0 | 39031.5714 | 2268 | 0 |  | 2441 | 2660 | 120.8791 | 0 | 138.4615 | 0 | 1.2088 | 0 | 1.3846 | 0 | 1.2088 | 1.3846 | 30.7263 | 14.1261 | 29.5175

## B3-D8
Open Burn Test 8 |  |  | 2006-11-10 | 13:06 |  |  | Vs = |  | 156.3724 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 150 kW |  | Bundle | Ch. 3 & 8 | Cable B | Odd - | Cable D |  | Even
Time-51 | N11 | N12 | Time-52 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R8-G | R3-8
39031.5414 | 0 | 0 | 39031.5414 | 0 | 0 |  | -148.5 | 70.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 512176 | 512176 | 512175.9997
39031.5435 | 0 | 0 | 39031.5435 | 0 | 0 |  | 36 | 255 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 512176 | 512176 | 512175.9997
39031.5457 | 0 | 0 | 39031.5457 | 0 | 0 |  | 220.5 | 439.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 512176 | 512176 | 512175.9997
39031.5478 | 0 | 0 | 39031.5478 | 0 | 0 |  | 405.5 | 624.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 512176 | 512176 | 512175.9997
39031.5499 | 0 | 0 | 39031.55 | 0 | 0 |  | 590.5 | 809.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 512176 | 512176 | 512175.9997
39031.5521 | 0 | 0 | 39031.5521 | 0 | 1 |  | 775 | 994 | 0.030525 | 0 | 0.030525 | 0.06105 | 0.00030525 | 0 | 0.00030525 | 0.0006105 | 0.00030525 | 0.00030525 | 512176 | 512176 | 512175.9997
39031.5542 | 0 | 0 | 39031.5542 | 46 | 0 |  | 960 | 1179 | 0.030525 | 0 | 2.8083 | 0 | 0.00030525 | 0 | 0.028083 | 0 | 0.00030525 | 0.028083 | 512176 | 5468.2174 | 512175.9997
39031.5564 | 0 | 0 | 39031.5564 | 2020 | 0 |  | 1144.5 | 1363.5 | 0.030525 | 0 | 123.3211 | 0 | 0.00030525 | 0 | 1.2332 | 0 | 0.00030525 | 1.2332 | 512176 | 26.801 | 512175.9997
39031.5585 | 0 | 0 | 39031.5585 | 1925 | 0 |  | 1329.5 | 1548.5 | 0.030525 | 0 | 117.5214 | 0 | 0.00030525 | 0 | 1.1752 | 0 | 0.00030525 | 1.1752 | 512176 | 33.0587 | 512175.9997
39031.5606 | 1591 | 0 | 39031.5606 | 2502 | 0 |  | 1514.5 | 1733.5 | 97.1306 | 0 | 152.7473 | 0 | 0.97131 | 0 | 1.5275 | 0 | 0.97131 | 1.5275 | 60.9918 | 2.3733 | 60.0205
39031.5628 | 2140 | 0 | 39031.5628 | 2537 | 0 |  | 1699 | 1918 | 130.6471 | 0 | 154.884 | 0 | 1.3065 | 0 | 1.5488 | 0 | 1.3065 | 1.5488 | 19.6907 | 0.96098 | 18.3842
39031.5649 | 2199 | 0 | 39031.5649 | 2545 | 0 |  | 1883.5 | 2102.5 | 134.2491 | 0 | 155.3724 | 0 | 1.3425 | 0 | 1.5537 | 0 | 1.3425 | 1.5537 | 16.4793 | 0.64361 | 15.1368
39031.567 | 2183 | 0 | 39031.5671 | 1980 | 0 |  | 2068.5 | 2287.5 | 133.2723 | 0 | 120.8791 | 0 | 1.3327 | 0 | 1.2088 | 0 | 1.3327 | 1.2088 | 17.333 | 29.3626 | 16.0003
39031.5692 | 1942 | 0 | 39031.5692 | 2019 | 0 |  | 2253.5 | 2472.5 | 118.5592 | 0 | 123.2601 | 0 | 1.1856 | 0 | 1.2326 | 0 | 1.1856 | 1.2326 | 31.8939 | 26.8638 | 30.7083
39031.5713 | 1918 | 1 | 39031.5713 | 2044 | 0 |  | 2438 | 2657 | 117.094 | 0.06105 | 124.7863 | 0 | 1.1709 | 0.0006105 | 1.2479 | 0 | 1.1703 | 1.2479 | 33.6311 | 25.3121 | 12975.6055

## B3-D7
Open Burn Test 8 |  |  | 2006-11-10 | 13:06 |  |  | Vs = |  | 157.4713 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 150 kW |  | Bundle | Ch. 3 & 7 | Cable B | Odd - | Cable D |  | Odd
Time-49 | N11 | N12 | Time-50 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R7-G | R3-7
39031.5414 | 0 | 0 | 39031.5414 | 0 | 0 |  | -151.5 | 67.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515776 | 515776 | 515775.9997
39031.5435 | 0 | 0 | 39031.5435 | 0 | 0 |  | 33 | 252 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515776 | 515776 | 515775.9997
39031.5456 | 0 | 0 | 39031.5456 | 0 | 0 |  | 218 | 437 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515776 | 515776 | 515775.9997
39031.5478 | 0 | 0 | 39031.5478 | 0 | 0 |  | 402.5 | 621.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515776 | 515776 | 515775.9997
39031.5499 | 0 | 0 | 39031.5499 | 0 | 0 |  | 587.5 | 806.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515776 | 515776 | 515775.9997
39031.552 | 0 | 0 | 39031.5521 | 0 | 0 |  | 772.5 | 991.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515776 | 515776 | 515775.9997
39031.5542 | 0 | 0 | 39031.5542 | 17 | 0 |  | 957 | 1176 | 0.030525 | 0 | 1.0379 | 0 | 0.00030525 | 0 | 0.010379 | 0 | 0.00030525 | 0.010379 | 515776 | 15072.8235 | 515775.9997
39031.5563 | 0 | 0 | 39031.5563 | 1984 | 0 |  | 1142 | 1361 | 0.030525 | 0 | 121.1233 | 0 | 0.00030525 | 0 | 1.2112 | 0 | 0.00030525 | 1.2112 | 515776 | 30.0091 | 515775.9997
39031.5585 | 0 | 0 | 39031.5585 | 1970 | 0 |  | 1326.5 | 1545.5 | 0.030525 | 0 | 120.2686 | 0 | 0.00030525 | 0 | 1.2027 | 0 | 0.00030525 | 1.2027 | 515776 | 30.933 | 515775.9997
39031.5606 | 1929 | 0 | 39031.5606 | 2177 | 0 |  | 1511.5 | 1730.5 | 117.7656 | 0 | 132.906 | 0 | 1.1777 | 0 | 1.3291 | 0 | 1.1777 | 1.3291 | 33.7159 | 18.4832 | 32.5383
39031.5627 | 2436 | 0 | 39031.5628 | 2520 | 0 |  | 1696 | 1915 | 148.7179 | 0 | 153.8462 | 0 | 1.4872 | 0 | 1.5385 | 0 | 1.4872 | 1.5385 | 5.8859 | 2.3563 | 4.3987
39031.5649 | 2448 | 0 | 39031.5649 | 2563 | 0 |  | 1881 | 2100 | 149.4505 | 0 | 156.4713 | 0 | 1.4945 | 0 | 1.5647 | 0 | 1.4945 | 1.5647 | 5.3668 | 0.63909 | 3.8723
39031.567 | 2256 | 0 | 39031.567 | 2294 | 0 |  | 2065.5 | 2284.5 | 137.7289 | 0 | 140.0488 | 0 | 1.3773 | 0 | 1.4005 | 0 | 1.3773 | 1.4005 | 14.3342 | 12.4403 | 12.9569
39031.5692 | 2111 | 0 | 39031.5692 | 2151 | 0 |  | 2250.5 | 2469.5 | 128.8767 | 0 | 131.3187 | 0 | 1.2888 | 0 | 1.3132 | 0 | 1.2888 | 1.3132 | 22.1876 | 19.9154 | 20.8988
39031.5713 | 2238 | 7 | 39031.5713 | 2528 | 0 |  | 2435.5 | 2654.5 | 136.63 | 0.42735 | 154.3346 | 0 | 1.3663 | 0.0042735 | 1.5433 | 0 | 1.362 | 1.5433 | 18.0951 | 2.0324 | 95.1527

## B3-C6
Open Burn Test 8 |  |  | 2006-11-10 | 13:06 |  |  | Vs = |  | 152.8315 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 150 kW |  | Bundle | Ch. 3 & 6 | Cable B | Odd - | Cable C |  | Even
Time-47 | N11 | N12 | Time-48 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R6-G | R3-6
39031.5413 | 0 | 0 | 39031.5413 | 0 | 0 |  | -154.5 | 64.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500576 | 500576 | 500575.9997
39031.5435 | 0 | 0 | 39031.5435 | 0 | 0 |  | 30.5 | 249.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500576 | 500576 | 500575.9997
39031.5456 | 0 | 0 | 39031.5456 | 0 | 0 |  | 215 | 434 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500576 | 500576 | 500575.9997
39031.5477 | 0 | 0 | 39031.5478 | 0 | 0 |  | 400 | 619 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500576 | 500576 | 500575.9997
| 0 | 0 | 39031.5499 | 0 | 0 |  | 585 | 804 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500576 | 500576 | 500575.9997
39031.552 | 0 | 0 | 39031.552 | 0 | 0 |  | 769.5 | 988.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500576 | 500576 | 500575.9997
39031.5542 | 0 | 0 | 39031.5542 | 0 | 0 |  | 954.5 | 1173.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500576 | 500576 | 500575.9997
39031.5563 | 0 | 0 | 39031.5563 | 0 | 0 |  | 1139 | 1358 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500576 | 500576 | 500575.9997
39031.5584 | 0 | 0 | 39031.5584 | 0 | 0 |  | 1324 | 1543 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500576 | 500576 | 500575.9997
39031.5606 | 1941 | 0 | 39031.5606 | 1504 | 0 |  | 1508.5 | 1727.5 | 118.4982 | 0 | 91.8193 | 0 | 1.185 | 0 | 0.91819 | 0 | 1.185 | 0.91819 | 28.9737 | 66.4481 | 27.7887
39031.5627 | 2379 | 0 | 39031.5627 | 2450 | 0 |  | 1693.5 | 1912.5 | 145.2381 | 0 | 149.5726 | 0 | 1.4524 | 0 | 1.4957 | 0 | 1.4524 | 1.4957 | 5.2282 | 2.1788 | 3.7759
39031.5648 | 2409 | 0 | 39031.5649 | 2092 | 0 |  | 1878 | 2097 | 147.0696 | 0 | 127.7167 | 0 | 1.4707 | 0 | 1.2772 | 0 | 1.4707 | 1.2772 | 3.9178 | 19.6644 | 2.4471
39031.567 | 2013 | 0 | 39031.567 | 2487 | 0 |  | 2063 | 2282 | 122.8938 | 0 | 151.8315 | 0 | 1.2289 | 0 | 1.5183 | 0 | 1.2289 | 1.5183 | 24.3607 | 0.65862 | 23.1317
39031.5691 | 2403 | 0 | 39031.5691 | 2449 | 0 |  | 2247.5 | 2466.5 | 146.7033 | 0 | 149.5116 | 0 | 1.467 | 0 | 1.4951 | 0 | 1.467 | 1.4951 | 4.1773 | 2.2205 | 2.7102
39031.5713 | 2094 | 1 | 39031.5713 | 2220 | 1 |  | 2432.5 | 2651.5 | 127.8388 | 0.06105 | 135.5311 | 0.06105 | 1.2784 | 0.0006105 | 1.3553 | 0.0006105 | 1.2778 | 1.3547 | 19.6328 | 12.8 | 4634.0989

## B3-C5
Open Burn Test 8 |  |  | 2006-11-10 | 13:06 |  |  | Vs = |  | 156.1893 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 150 kW |  | Bundle | Ch. 3 & 5 | Cable B | Odd - | Cable C |  | Odd
Time-45 | N11 | N12 | Time-46 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R5-G | R3-5
39031.5413 | 0 | 0 | 39031.5413 | 0 | 0 |  | -157 | 62 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511576 | 511576 | 511575.9997
39031.5434 | 0 | 0 | 39031.5434 | 0 | 0 |  | 27.5 | 246.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511576 | 511576 | 511575.9997
39031.5456 | 0 | 0 | 39031.5456 | 0 | 0 |  | 212.5 | 431.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511576 | 511576 | 511575.9997
39031.5477 | 0 | 0 | 39031.5477 | 0 | 0 |  | 397 | 616 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511576 | 511576 | 511575.9997
39031.5498 | 0 | 0 | 39031.5499 | 0 | 0 |  | 582 | 801 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511576 | 511576 | 511575.9997
39031.552 | 0 | 0 | 39031.552 | 0 | 0 |  | 766.5 | 985.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511576 | 511576 | 511575.9997
39031.5541 | 0 | 0 | 39031.5541 | 0 | 0 |  | 951.5 | 1170.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511576 | 511576 | 511575.9997
39031.5563 | 0 | 0 | 39031.5563 | 0 | 0 |  | 1136.5 | 1355.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511576 | 511576 | 511575.9997
39031.5584 | 0 | 0 | 39031.5584 | 0 | 0 |  | 1321 | 1540 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511576 | 511576 | 511575.9997
39031.5605 | 1920 | 0 | 39031.5605 | 1841 | 0 |  | 1505.5 | 1724.5 | 117.2161 | 0 | 112.3932 | 0 | 1.1722 | 0 | 1.1239 | 0 | 1.1722 | 1.1239 | 33.249 | 38.9669 | 32.0768
39031.5627 | 2119 | 0 | 39031.5627 | 2311 | 0 |  | 1690.5 | 1909.5 | 129.3651 | 0 | 141.0867 | 0 | 1.2937 | 0 | 1.4109 | 0 | 1.2937 | 1.4109 | 20.7353 | 10.7045 | 19.4416
39031.5648 | 2261 | 0 | 39031.5648 | 2140 | 0 |  | 1875.5 | 2094.5 | 138.0342 | 0 | 130.6471 | 0 | 1.3803 | 0 | 1.3065 | 0 | 1.3803 | 1.3065 | 13.1526 | 19.5505 | 11.7722
39031.5669 | 2542 | 0 | 39031.567 | 2179 | 0 |  | 2060 | 2279 | 155.1893 | 0 | 133.0281 | 0 | 1.5519 | 0 | 1.3303 | 0 | 1.5519 | 1.3303 | 0.64437 | 17.4107 | 0.90752
39031.5691 | 2011 | 0 | 39031.5691 | 1959 | 0 |  | 2245 | 2464 | 122.7717 | 0 | 119.5971 | 0 | 1.2277 | 0 | 1.196 | 0 | 1.2277 | 1.196 | 27.2193 | 30.5962 | 25.9916
39031.5712 | 2163 | 0 | 39031.5712 | 2475 | 0 |  | 2429.5 | 2648.5 | 132.0513 | 0 | 151.0989 | 0 | 1.3205 | 0 | 1.511 | 0 | 1.3205 | 1.511 | 18.2792 | 3.3689 | 16.9587

## B3-B4
Open Burn Test 8 |  |  | 2006-11-10 | 13:06 |  |  | Vs = |  | 156.6166 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 150 kW |  | Bundle | Ch. 3 & 4 | Cable B | Odd -Even
Time-43 | N11 | N12 | Time-44 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R4-G | R3-4
39031.5413 | 0 | 0 | 39031.5413 | 0 | 0 |  | -160 | 59 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 512976 | 512976 | 512975.9997
39031.5434 | 0 | 0 | 39031.5434 | 0 | 0 |  | 24.5 | 243.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 512976 | 512976 | 512975.9997
39031.5455 | 0 | 0 | 39031.5455 | 0 | 0 |  | 209.5 | 428.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 512976 | 512976 | 512975.9997
39031.5477 | 0 | 0 | 39031.5477 | 0 | 0 |  | 394.5 | 613.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 512976 | 512976 | 512975.9997
39031.5498 | 0 | 0 | 39031.5498 | 0 | 0 |  | 579 | 798 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 512976 | 512976 | 512975.9997
39031.5519 | 0 | 0 | 39031.552 | 0 | 0 |  | 764 | 983 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 512976 | 512976 | 512975.9997
39031.5541 | 0 | 0 | 39031.5541 | 0 | 0 |  | 948.5 | 1167.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 512976 | 512976 | 512975.9997
39031.5562 | 0 | 0 | 39031.5562 | 0 | 0 |  | 1133.5 | 1352.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 512976 | 512976 | 512975.9997
39031.5584 | 0 | 0 | 39031.5584 | 0 | 0 |  | 1318.5 | 1537.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 512976 | 512976 | 512975.9997
39031.5605 | 1511 | 11 | 39031.5605 | 1373 | 15 |  | 1503 | 1722 | 92.2466 | 0.67155 | 83.8217 | 0.91575 | 0.92247 | 0.0067155 | 0.83822 | 0.0091575 | 0.91575 | 0.82906 | 70.8747 | 89.1942 | 4471.7612
39031.5626 | 2014 | 14 | 39031.5627 | 2023 | 13 |  | 1687.5 | 1906.5 | 122.9548 | 0.8547 | 123.5043 | 0.79365 | 1.2295 | 0.008547 | 1.235 | 0.0079365 | 1.221 | 1.2271 | 28.286 | 27.6155 | 830.6214
39031.5648 | 2143 | 0 | 39031.5648 | 2004 | 0 |  | 1872.5 | 2091.5 | 130.8303 | 0 | 122.3443 | 0 | 1.3083 | 0 | 1.2234 | 0 | 1.3083 | 1.2234 | 19.7098 | 28.013 | 18.4014
39031.5669 | 2092 | 0 | 39031.5669 | 2436 | 0 |  | 2057.5 | 2276.5 | 127.7167 | 0 | 148.7179 | 0 | 1.2772 | 0 | 1.4872 | 0 | 1.2772 | 1.4872 | 22.6281 | 5.3112 | 21.3509
39031.5691 | 2549 | 1 | 39031.5691 | 2016 | 1 |  | 2242 | 2461 | 155.6166 | 0.06105 | 123.0769 | 0.06105 | 1.5562 | 0.0006105 | 1.2308 | 0.0006105 | 1.5556 | 1.2302 | 0.64371 | 29.5421 | 350.7412
39031.5712 | 1984 | 3 | 39031.5712 | 2175 | 2 |  | 2427 | 2646 | 121.1233 | 0.18315 | 132.7839 | 0.1221 | 1.2112 | 0.0018315 | 1.3278 | 0.001221 | 1.2094 | 1.3266 | 29.5965 | 18.0211 | 2943.8317

## A2-C6
Open Burn Test 8 |  |  | 2006-11-10 | 13:06 |  |  | Vs = |  | 158.6923 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 150 kW |  | Bundle | Ch. 2 & 6 | Cable A | Even - | Cable C |  | Even
Time-29 | N11 | N12 | Time-30 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R6-G | R2-6
39031.541 | 0 | 0 | 39031.541 | 0 | 0 |  | -179.5 | 39.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 519776 | 519776 | 519775.9997
39031.5432 | 0 | 0 | 39031.5432 | 0 | 0 |  | 5.5 | 224.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 519776 | 519776 | 519775.9997
39031.5453 | 0 | 0 | 39031.5453 | 0 | 0 |  | 190 | 409 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 519776 | 519776 | 519775.9997
39031.5474 | 0 | 0 | 39031.5475 | 0 | 0 |  | 374.5 | 593.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 519776 | 519776 | 519775.9997
39031.5496 | 0 | 0 | 39031.5496 | 0 | 0 |  | 559.5 | 778.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 519776 | 519776 | 519775.9997
39031.5517 | 0 | 0 | 39031.5517 | 0 | 0 |  | 744.5 | 963.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 519776 | 519776 | 519775.9997
39031.5539 | 0 | 0 | 39031.5539 | 0 | 0 |  | 929 | 1148 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 519776 | 519776 | 519775.9997
39031.556 | 0 | 0 | 39031.556 | 0 | 0 |  | 1114 | 1333 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 519776 | 519776 | 519775.9997
39031.5581 | 0 | 0 | 39031.5581 | 0 | 0 |  | 1298.5 | 1517.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 519776 | 519776 | 519775.9997
39031.5603 | 1446 | 129 |  | 1796 | 140 |  | 1483 | 1702 | 88.2784 | 7.8755 | 109.6459 | 8.547 | 0.88278 | 0.078755 | 1.0965 | 0.08547 | 0.80403 | 1.011 | 107.5927 | 52.6503 | 273.8889
39031.5624 | 1562 | 0 | 39031.5624 | 2413 | 0 |  | 1668 | 1887 | 95.3602 | 0 | 147.3138 | 0 | 0.9536 | 0 | 1.4731 | 0 | 0.9536 | 1.4731 | 66.4136 | 7.724 | 65.46
39031.5645 | 2230 | 0 | 39031.5646 | 1986 | 0 |  | 1853 | 2072 | 136.1416 | 0 | 121.2454 | 0 | 1.3614 | 0 | 1.2125 | 0 | 1.3614 | 1.2125 | 16.5641 | 30.8852 | 15.2027
39031.5667 | 2437 | 0 | 39031.5667 | 2583 | 0 |  | 2037.5 | 2256.5 | 148.779 | 0 | 157.6923 | 0 | 1.4878 | 0 | 1.5769 | 0 | 1.4878 | 1.5769 | 6.6631 | 0.63415 | 5.1753
39031.5688 | 2370 | 0 | 39031.5688 | 2065 | 0 |  | 2222.5 | 2441.5 | 144.6886 | 0 | 126.0684 | 0 | 1.4469 | 0 | 1.2607 | 0 | 1.4469 | 1.2607 | 9.6785 | 25.878 | 8.2316
39031.571 | 2037 | 0 | 39031.571 | 1977 | 1 |  | 2407.5 | 2626.5 | 124.359 | 0 | 120.696 | 0.06105 | 1.2436 | 0 | 1.207 | 0.0006105 | 1.2436 | 1.2063 | 27.6082 | 31.5476 | 26.3647

## A2-C5
Open Burn Test 8 |  |  | 2006-11-10 | 13:06 |  |  | Vs = |  | 151.9768 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 150 kW |  | Bundle | Ch. 2 & 5 | Cable A | Even - | Cable C |  | Odd
Time-27 | N11 | N12 | Time-28 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R5-G | R2-5
39031.541 | 0 | 0 | 39031.541 | 0 | 0 |  | -182.5 | 36.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 497776 | 497776 | 497775.9997
39031.5431 | 0 | 0 | 39031.5431 | 0 | 0 |  | 2.5 | 221.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 497776 | 497776 | 497775.9997
39031.5453 | 0 | 0 | 39031.5453 | 0 | 0 |  | 187 | 406 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 497776 | 497776 | 497775.9997
39031.5474 | 0 | 0 | 39031.5474 | 0 | 0 |  | 372 | 591 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 497776 | 497776 | 497775.9997
39031.5495 | 0 | 0 | 39031.5496 | 0 | 0 |  | 556.5 | 775.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 497776 | 497776 | 497775.9997
39031.5517 | 0 | 0 | 39031.5517 | 0 | 0 |  | 741.5 | 960.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 497776 | 497776 | 497775.9997
39031.5538 | 0 | 0 | 39031.5538 | 0 | 0 |  | 926.5 | 1145.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 497776 | 497776 | 497775.9997
39031.556 | 0 | 0 | 39031.556 | 0 | 0 |  | 1111 | 1330 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 497776 | 497776 | 497775.9997
39031.5581 | 0 | 0 | 39031.5581 | 0 | 0 |  | 1296 | 1515 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 497776 | 497776 | 497775.9997
39031.5602 | 1426 | 66 | 39031.5603 | 1779 | 77 |  | 1480.5 | 1699.5 | 87.0574 | 4.0293 | 108.6081 | 4.7009 | 0.87057 | 0.040293 | 1.0861 | 0.047009 | 0.83028 | 1.0391 | 87.8819 | 44.0032 | 461.7734
39031.5624 | 1300 | 0 | 39031.5624 | 2436 | 0 |  | 1665.5 | 1884.5 | 79.3651 | 0 | 148.7179 | 0 | 0.79365 | 0 | 1.4872 | 0 | 0.79365 | 1.4872 | 91.4908 | 2.1913 | 90.6971
39031.5645 | 2473 | 0 | 39031.5645 | 2384 | 0 |  | 1850 | 2069 | 150.9768 | 0 | 145.5433 | 0 | 1.5098 | 0 | 1.4554 | 0 | 1.5098 | 1.4554 | 0.66235 | 4.4203 | 0.84741
39031.5667 | 2040 | 0 | 39031.5667 | 1979 | 0 |  | 2035 | 2254 | 124.5421 | 0 | 120.8181 | 0 | 1.2454 | 0 | 1.2082 | 0 | 1.2454 | 1.2082 | 22.0284 | 25.7898 | 20.783
39031.5688 | 2014 | 0 | 39031.5688 | 2253 | 0 |  | 2219.5 | 2438.5 | 122.9548 | 0 | 137.5458 | 0 | 1.2295 | 0 | 1.3755 | 0 | 1.2295 | 1.3755 | 23.6038 | 10.4918 | 22.3742
39031.5709 | 2222 | 1 | 39031.5709 | 2449 | 1 |  | 2404.5 | 2623.5 | 135.6532 | 0.06105 | 149.5116 | 0.06105 | 1.3565 | 0.0006105 | 1.4951 | 0.0006105 | 1.3559 | 1.4945 | 12.3754 | 1.655 | 433.6744

## A2-B4
Open Burn Test 8 |  |  | 2006-11-10 | 13:06 |  |  | Vs = |  | 156.0672 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 150 kW |  | Bundle | Ch. 2 & 4 | Cable A | Even - | Cable B |  | Even
Time-25 | N11 | N12 | Time-26 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R4-G | R2-4
39031.541 | 0 | 0 | 39031.541 | 0 | 0 |  | -185 | 34 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511176 | 511176 | 511175.9997
39031.5431 | 0 | 0 | 39031.5431 | 0 | 0 |  | -0.5 | 218.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511176 | 511176 | 511175.9997
39031.5452 | 0 | 0 | 39031.5453 | 0 | 0 |  | 184.5 | 403.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511176 | 511176 | 511175.9997
39031.5474 | 0 | 0 | 39031.5474 | 0 | 0 |  | 369 | 588 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511176 | 511176 | 511175.9997
39031.5495 | 0 | 0 | 39031.5495 | 0 | 0 |  | 554 | 773 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511176 | 511176 | 511175.9997
39031.5517 | 0 | 0 | 39031.5517 | 0 | 0 |  | 738.5 | 957.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511176 | 511176 | 511175.9997
39031.5538 | 0 | 0 | 39031.5538 | 0 | 0 |  | 923.5 | 1142.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511176 | 511176 | 511175.9997
39031.5559 | 0 | 0 | 39031.5559 | 0 | 0 |  | 1108.5 | 1327.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511176 | 511176 | 511175.9997
39031.5581 | 0 | 0 | 39031.5581 | 0 | 0 |  | 1293 | 1512 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511176 | 511176 | 511175.9997
39031.5602 | 1236 | 0 | 39031.5602 | 1506 | 0 |  | 1477.5 | 1696.5 | 75.4579 | 0 | 91.9414 | 0 | 0.75458 | 0 | 0.91941 | 0 | 0.75458 | 0.91941 | 106.8269 | 69.7463 | 106.0723
39031.5623 | 1935 | 0 | 39031.5624 | 1434 | 0 |  | 1662.5 | 1881.5 | 118.1319 | 0 | 87.5458 | 0 | 1.1813 | 0 | 0.87546 | 0 | 1.1813 | 0.87546 | 32.1127 | 78.2692 | 30.9313
39031.5645 | 2074 | 0 | 39031.5645 | 2002 | 0 |  | 1847.5 | 2066.5 | 126.6178 | 0 | 122.2222 | 0 | 1.2662 | 0 | 1.2222 | 0 | 1.2662 | 1.2222 | 23.2584 | 27.6913 | 21.9923
39031.5666 | 2177 | 0 | 39031.5666 | 2540 | 0 |  | 2032 | 2251 | 132.906 | 0 | 155.0672 | 0 | 1.3291 | 0 | 1.5507 | 0 | 1.3291 | 1.5507 | 17.4267 | 0.64488 | 16.0977
39031.5688 | 2002 | 0 | 39031.5688 | 1981 | 0 |  | 2217 | 2436 | 122.2222 | 0 | 120.9402 | 0 | 1.2222 | 0 | 1.2094 | 0 | 1.2222 | 1.2094 | 27.6913 | 29.0449 | 26.4691
39031.5709 | 2201 | 1 | 39031.5709 | 1962 | 0 |  | 2401.5 | 2620.5 | 134.3712 | 0.06105 | 119.7802 | 0 | 1.3437 | 0.0006105 | 1.1978 | 0 | 1.3431 | 1.1978 | 16.1779 | 30.2946 | 8239.6351

## A2-B3
Open Burn Test 8 |  |  | 2006-11-10 | 13:06 |  |  | Vs = |  | 158.6923 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 150 kW |  | Bundle | Ch. 2 & 3 | Cable A | Even - | Cable B |  | Odd
Time-23 | N11 | N12 | Time-24 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R3-G | R2-3
39031.5409 | 0 | 0 | 39031.5409 | 0 | 0 |  | -188 | 31 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 519776 | 519776 | 519775.9997
39031.5431 | 0 | 0 | 39031.5431 | 0 | 0 |  | -3.5 | 215.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 519776 | 519776 | 519775.9997
39031.5452 | 0 | 0 | 39031.5452 | 0 | 0 |  | 181.5 | 400.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 519776 | 519776 | 519775.9997
39031.5473 | 0 | 0 | 39031.5474 | 0 | 0 |  | 366.5 | 585.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 519776 | 519776 | 519775.9997
39031.5495 | 0 | 0 | 39031.5495 | 0 | 0 |  | 551 | 770 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 519776 | 519776 | 519775.9997
39031.5516 | 0 | 0 | 39031.5516 | 0 | 0 |  | 736 | 955 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 519776 | 519776 | 519775.9997
39031.5538 | 0 | 0 | 39031.5538 | 0 | 0 |  | 920.5 | 1139.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 519776 | 519776 | 519775.9997
39031.5559 | 0 | 0 | 39031.5559 | 0 | 0 |  | 1105.5 | 1324.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 519776 | 519776 | 519775.9997
39031.558 | 0 | 0 | 39031.5581 | 0 | 0 |  | 1290.5 | 1509.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 519776 | 519776 | 519775.9997
39031.5602 | 1383 | 0 | 39031.5602 | 1490 | 0 |  | 1475 | 1694 | 84.4322 | 0 | 90.9646 | 0 | 0.84432 | 0 | 0.90965 | 0 | 0.84432 | 0.90965 | 87.9523 | 74.455 | 87.108
39031.5623 | 2205 | 0 | 39031.5623 | 1918 | 0 |  | 1659.5 | 1878.5 | 134.6154 | 0 | 117.094 | 0 | 1.3462 | 0 | 1.1709 | 0 | 1.3462 | 1.1709 | 17.8857 | 35.5255 | 16.5396
39031.5645 | 2178 | 0 | 39031.5645 | 2046 | 0 |  | 1844.5 | 2063.5 | 132.967 | 0 | 124.9084 | 0 | 1.3297 | 0 | 1.2491 | 0 | 1.3297 | 1.2491 | 19.3471 | 27.0469 | 18.0174
39031.5666 | 2030 | 0 | 39031.5666 | 2583 | 0 |  | 2029.5 | 2248.5 | 123.9316 | 0 | 157.6923 | 0 | 1.2393 | 0 | 1.5769 | 0 | 1.2393 | 1.5769 | 28.0483 | 0.63415 | 26.809
39031.5687 | 2102 | 0 | 39031.5687 | 2537 | 0 |  | 2214 | 2433 | 128.3272 | 0 | 154.884 | 0 | 1.2833 | 0 | 1.5488 | 0 | 1.2833 | 1.5488 | 23.6622 | 2.4588 | 22.379
39031.5709 | 2081 | 1 | 39031.5709 | 2355 | 0 |  | 2399 | 2618 | 127.0452 | 0.06105 | 143.7729 | 0 | 1.2705 | 0.0006105 | 1.4377 | 0 | 1.2698 | 1.4377 | 25.0381 | 10.3771 | 4864.1339

## A1-C6
Open Burn Test 8 |  |  | 2006-11-10 | 13:06 |  |  | Vs = |  | 144.956 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 150 kW |  | Bundle | Ch. 1 & 6 | Cable A | Odd - | Cable C |  | Even
Time-9 | N11 | N12 | Time-10 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R6-G | R1-6
39031.5407 | 0 | 0 | 39031.5407 | 0 | 0 |  | -207.5 | 11.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 474776 | 474776 | 474775.9997
39031.5428 | 0 | 0 | 39031.5429 | 0 | 0 |  | -22.5 | 196.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 474776 | 474776 | 474775.9997
39031.545 | 0 | 0 | 39031.545 | 0 | 0 |  | 162 | 381 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 474776 | 474776 | 474775.9997
39031.5471 | 0 | 0 | 39031.5471 | 0 | 0 |  | 346.5 | 565.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 474776 | 474776 | 474775.9997
39031.5493 | 0 | 0 | 39031.5493 | 0 | 0 |  | 531.5 | 750.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 474776 | 474776 | 474775.9997
39031.5514 | 0 | 0 | 39031.5514 | 0 | 0 |  | 716.5 | 935.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 474776 | 474776 | 474775.9997
39031.5535 | 0 | 0 | 39031.5536 | 0 | 0 |  | 901 | 1120 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 474776 | 474776 | 474775.9997
39031.5557 | 0 | 0 | 39031.5557 | 0 | 0 |  | 1086 | 1305 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 474776 | 474776 | 474775.9997
39031.5578 | 0 | 0 | 39031.5578 | 0 | 0 |  | 1270.5 | 1489.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 474776 | 474776 | 474775.9997
39031.56 | 1162 | 409 | 39031.56 | 1498 | 398 |  | 1455.5 | 1674.5 | 70.9402 | 24.9695 | 91.453 | 24.2979 | 0.7094 | 0.24969 | 0.91453 | 0.24298 | 0.45971 | 0.67155 | 428.411 | 87.0203 | 91.3965
39031.5621 | 2034 | 0 | 39031.5621 | 2043 | 1 |  | 1640 | 1859 | 124.1758 | 0 | 124.7253 | 0.06105 | 1.2418 | 0 | 1.2473 | 0.0006105 | 1.2418 | 1.2466 | 16.7345 | 16.2772 | 15.4928
39031.5642 | 2216 | 0 | 39031.5642 | 2197 | 0 |  | 1825 | 2044 | 135.2869 | 0 | 134.127 | 0 | 1.3529 | 0 | 1.3413 | 0 | 1.3529 | 1.3413 | 7.1471 | 8.0737 | 5.7942
39031.5664 | 2131 | 0 | 39031.5664 | 1987 | 0 |  | 2009.5 | 2228.5 | 130.0977 | 0 | 121.3065 | 0 | 1.301 | 0 | 1.2131 | 0 | 1.301 | 1.2131 | 11.4209 | 19.4957 | 10.12
39031.5685 | 2358 | 0 | 39031.5685 | 2129 | 0 |  | 2194.5 | 2413.5 | 143.956 | 0 | 129.9756 | 0 | 1.4396 | 0 | 1.2998 | 0 | 1.4396 | 1.2998 | 0.69466 | 11.5256 | 0.7449
39031.5706 | 2201 | 1 | 39031.5707 | 2356 | 1 |  | 2379 | 2598 | 134.3712 | 0.06105 | 143.8339 | 0.06105 | 1.3437 | 0.0006105 | 1.4383 | 0.0006105 | 1.3431 | 1.4377 | 8.3657 | 0.78445 | 134.1708

## A1-C5
Open Burn Test 8 |  |  | 2006-11-10 | 13:06 |  |  | Vs = |  | 157.1661 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 150 kW |  | Bundle | Ch. 1 & 5 | Cable A | Odd - | Cable C |  | Odd
Time-7 | N11 | N12 | Time-8 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R5-G | R1-5
39031.5407 | 0 | 0 | 39031.5407 | 0 | 0 |  | -210.5 | 8.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 514776 | 514776 | 514775.9997
39031.5428 | 0 | 0 | 39031.5428 | 0 | 0 |  | -25.5 | 193.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 514776 | 514776 | 514775.9997
39031.545 | 0 | 0 | 39031.545 | 0 | 0 |  | 159.5 | 378.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 514776 | 514776 | 514775.9997
39031.5471 | 0 | 0 | 39031.5471 | 0 | 0 |  | 344 | 563 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 514776 | 514776 | 514775.9997
39031.5492 | 0 | 0 | 39031.5492 | 0 | 0 |  | 528.5 | 747.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 514776 | 514776 | 514775.9997
39031.5514 | 0 | 0 | 39031.5514 | 0 | 0 |  | 713.5 | 932.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 514776 | 514776 | 514775.9997
39031.5535 | 0 | 0 | 39031.5535 | 0 | 0 |  | 898.5 | 1117.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 514776 | 514776 | 514775.9997
39031.5556 | 0 | 0 | 39031.5557 | 0 | 0 |  | 1083 | 1302 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 514776 | 514776 | 514775.9997
39031.5578 | 0 | 0 | 39031.5578 | 0 | 0 |  | 1267.5 | 1486.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 514776 | 514776 | 514775.9997
39031.5599 | 1014 | 23 | 39031.5599 | 1906 | 1 |  | 1452.5 | 1671.5 | 61.9048 | 1.4042 | 116.3614 | 0.06105 | 0.61905 | 0.014042 | 1.1636 | 0.0006105 | 0.60501 | 1.163 | 168.6047 | 35.0965 | 1736.4929
39031.5621 | 1861 | 3 | 39031.5621 | 1909 | 3 |  | 1637.5 | 1856.5 | 113.6142 | 0.18315 | 116.5446 | 0.18315 | 1.1361 | 0.0018315 | 1.1654 | 0.0018315 | 1.1343 | 1.1636 | 38.5727 | 35.0528 | 6145.943
39031.5642 | 2415 | 0 | 39031.5642 | 1981 | 0 |  | 1822 | 2041 | 147.4359 | 0 | 120.9402 | 0 | 1.4744 | 0 | 1.2094 | 0 | 1.4744 | 1.2094 | 6.5996 | 29.9536 | 5.1252
39031.5663 | 2038 | 0 | 39031.5664 | 2558 | 0 |  | 2007 | 2226 | 124.42 | 0 | 156.1661 | 0 | 1.2442 | 0 | 1.5617 | 0 | 1.2442 | 1.5617 | 26.3189 | 0.64034 | 25.0747
39031.5685 | 2072 | 0 | 39031.5685 | 2440 | 0 |  | 2191.5 | 2410.5 | 126.4957 | 0 | 148.9621 | 0 | 1.265 | 0 | 1.4896 | 0 | 1.265 | 1.4896 | 24.2461 | 5.5074 | 22.9812
39031.5706 | 2409 | 0 | 39031.5706 | 2500 | 1 |  | 2376.5 | 2595.5 | 147.0696 | 0 | 152.6252 | 0.06105 | 1.4707 | 0 | 1.5263 | 0.0006105 | 1.4707 | 1.5256 | 6.8651 | 3.0164 | 5.3944

## A1-B4
Open Burn Test 8 |  |  | 2006-11-10 | 13:06 |  |  | Vs = |  | 150.3895 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 150 kW |  | Bundle | Ch. 1 & 4 | Cable A | Odd - | Cable B |  | Even
Time-5 | N11 | N12 | Time-6 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R4-G | R1-4
39031.5406 | 0 | 0 | 39031.5407 | 0 | 0 |  | -213 | 6 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 492576 | 492576 | 492575.9997
39031.5428 | 0 | 0 | 39031.5428 | 0 | 0 |  | -28.5 | 190.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 492576 | 492576 | 492575.9997
39031.5449 | 0 | 0 | 39031.5449 | 0 | 0 |  | 156.5 | 375.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 492576 | 492576 | 492575.9997
39031.547 | 0 | 0 | 39031.5471 | 0 | 0 |  | 341 | 560 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 492576 | 492576 | 492575.9997
39031.5492 | 0 | 0 | 39031.5492 | 0 | 0 |  | 526 | 745 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 492576 | 492576 | 492575.9997
39031.5513 | 0 | 0 | 39031.5513 | 0 | 0 |  | 710.5 | 929.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 492576 | 492576 | 492575.9997
39031.5535 | 0 | 0 | 39031.5535 | 0 | 0 |  | 895.5 | 1114.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 492576 | 492576 | 492575.9997
39031.5556 | 0 | 0 | 39031.5556 | 0 | 0 |  | 1080.5 | 1299.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 492576 | 492576 | 492575.9997
39031.5577 | 0 | 0 | 39031.5578 | 0 | 0 |  | 1265 | 1484 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 492576 | 492576 | 492575.9997
39031.5599 | 932 | 0 | 39031.5599 | 1451 | 0 |  | 1449.5 | 1668.5 | 56.8987 | 0 | 88.5836 | 0 | 0.56899 | 0 | 0.88584 | 0 | 0.56899 | 0.88584 | 164.3112 | 69.7712 | 163.7422
39031.562 | 1612 | 0 | 39031.562 | 2195 | 0 |  | 1634.5 | 1853.5 | 98.4127 | 0 | 134.0049 | 0 | 0.98413 | 0 | 1.34 | 0 | 0.98413 | 1.34 | 52.8151 | 12.2269 | 51.831
39031.5642 | 2192 | 0 | 39031.5642 | 2427 | 0 |  | 1819.5 | 2038.5 | 133.8217 | 0 | 148.1685 | 0 | 1.3382 | 0 | 1.4817 | 0 | 1.3382 | 1.4817 | 12.3805 | 1.499 | 11.0423
39031.5663 | 2368 | 0 | 39031.5663 | 2447 | 0 |  | 2004 | 2223 | 144.5665 | 0 | 149.3895 | 0 | 1.4457 | 0 | 1.4939 | 0 | 1.4457 | 1.4939 | 4.0279 | 0.66939 | 2.5822
39031.5684 | 2442 | 0 | 39031.5685 | 1974 | 0 |  | 2189 | 2408 | 149.0842 | 0 | 120.5128 | 0 | 1.4908 | 0 | 1.2051 | 0 | 1.4908 | 1.2051 | 0.87551 | 24.7913 | 0.61533
39031.5706 | 2347 | 0 | 39031.5706 | 2252 | 0 |  | 2373.5 | 2592.5 | 143.2845 | 0 | 137.4847 | 0 | 1.4328 | 0 | 1.3748 | 0 | 1.4328 | 1.3748 | 4.9587 | 9.3863 | 3.5258

## A1-B3
Open Burn Test 8 |  |  | 2006-11-10 | 13:06 |  |  | Vs = |  | 155.0904 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 150 kW |  | Bundle | Ch. 1 & 3 | Cable A | Odd - | Cable B |  | Odd
Time-3 | N11 | N12 | Time-4 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R3-G | R1-3
39031.5406 | 0 | 0 | 39031.5406 | 0 | 0 |  | -216 | 3 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 507976 | 507976 | 507975.9997
39031.5427 | 0 | 0 | 39031.5428 | 0 | 0 |  | -31 | 188 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 507976 | 507976 | 507975.9997
39031.5449 | 0 | 0 | 39031.5449 | 0 | 0 |  | 153.5 | 372.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 507976 | 507976 | 507975.9997
39031.547 | 0 | 0 | 39031.547 | 0 | 0 |  | 338.5 | 557.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 507976 | 507976 | 507975.9997
39031.5492 | 0 | 0 | 39031.5492 | 0 | 0 |  | 523 | 742 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 507976 | 507976 | 507975.9997
39031.5513 | 0 | 0 | 39031.5513 | 0 | 0 |  | 708 | 927 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 507976 | 507976 | 507975.9997
39031.5534 | 0 | 0 | 39031.5534 | 0 | 0 |  | 892.5 | 1111.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 507976 | 507976 | 507975.9997
39031.5556 | 0 | 0 | 39031.5556 | 0 | 0 |  | 1077.5 | 1296.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 507976 | 507976 | 507975.9997
39031.5577 | 0 | 0 | 39031.5577 | 0 | 0 |  | 1262 | 1481 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 507976 | 507976 | 507975.9997
39031.5598 | 1188 | 0 | 39031.5599 | 1289 | 0 |  | 1447 | 1666 | 72.5275 | 0 | 78.6935 | 0 | 0.72527 | 0 | 0.78694 | 0 | 0.72527 | 0.78694 | 113.8367 | 97.0815 | 113.1114
39031.562 | 1788 | 0 | 39031.562 | 2264 | 0 |  | 1631.5 | 1850.5 | 109.1575 | 0 | 138.2173 | 0 | 1.0916 | 0 | 1.3822 | 0 | 1.0916 | 1.3822 | 42.0794 | 12.2076 | 40.9878
39031.5641 | 2249 | 0 | 39031.5641 | 2171 | 0 |  | 1816.5 | 2035.5 | 137.3016 | 0 | 132.5397 | 0 | 1.373 | 0 | 1.3254 | 0 | 1.373 | 1.3254 | 12.956 | 17.0143 | 11.583
39031.5663 | 1984 | 0 | 39031.5663 | 2241 | 0 |  | 2001.5 | 2220.5 | 121.1233 | 0 | 136.8132 | 0 | 1.2112 | 0 | 1.3681 | 0 | 1.2112 | 1.3681 | 28.0433 | 13.3592 | 26.8321
39031.5684 | 2524 | 0 | 39031.5684 | 2277 | 0 |  | 2186 | 2405 | 154.0904 | 0 | 139.011 | 0 | 1.5409 | 0 | 1.3901 | 0 | 1.5409 | 1.3901 | 0.64897 | 11.567 | 0.89193
39031.5705 | 2272 | 0 | 39031.5706 | 2172 | 0 |  | 2371 | 2590 | 138.7057 | 0 | 132.6007 | 0 | 1.3871 | 0 | 1.326 | 0 | 1.3871 | 1.326 | 11.8125 | 16.9604 | 10.4254

## A1-A2
Open Burn Test 8 |  |  | 2006-11-10 | 13:06 |  |  | Vs = |  | 152.2821 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 150 kW |  | Bundle | Ch. 1 & 2 | Cable A | Odd-Even
Time-1 | N11 | N12 | Time-2 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R2-G | R1-2
39031.5406 | 0 | 0 | 39031.5406 | 0 | 0 |  | -218.5 | 0.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 498776 | 498776 | 498775.9997
39031.5427 | 0 | 0 | 39031.5427 | 0 | 0 |  | -34 | 185 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 498776 | 498776 | 498775.9997
39031.5448 | 0 | 0 | 39031.5449 | 0 | 0 |  | 151 | 370 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 498776 | 498776 | 498775.9997
39031.547 | 0 | 0 | 39031.547 | 0 | 0 |  | 335.5 | 554.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 498776 | 498776 | 498775.9997
39031.5491 | 0 | 0 | 39031.5491 | 0 | 0 |  | 520.5 | 739.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 498776 | 498776 | 498775.9997
39031.5513 | 0 | 0 | 39031.5513 | 0 | 0 |  | 705 | 924 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 498776 | 498776 | 498775.9997
39031.5534 | 0 | 0 | 39031.5534 | 0 | 0 |  | 890 | 1109 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 498776 | 498776 | 498775.9997
39031.5555 | 0 | 0 | 39031.5556 | 0 | 0 |  | 1074.5 | 1293.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 498776 | 498776 | 498775.9997
39031.5577 | 101 | 60 | 39031.5577 | 349 | 258 |  | 1259.5 | 1478.5 | 6.1661 | 3.663 | 21.3065 | 15.7509 | 0.061661 | 0.03663 | 0.21306 | 0.15751 | 0.025031 | 0.055556 | 6205.0831 | 2470.4372 | 3737.6707
39031.5598 | 1214 | 895 | 39031.5598 | 1385 | 695 |  | 1444 | 1663 | 74.1148 | 54.6398 | 84.5543 | 42.4298 | 0.74115 | 0.5464 | 0.84554 | 0.4243 | 0.19475 | 0.42125 | 302.8179 | 862.0543 | 38.5835
39031.562 | 1761 | 352 | 39031.562 | 1618 | 353 |  | 1629 | 1848 | 107.5092 | 21.4896 | 98.779 | 21.5507 | 1.0751 | 0.2149 | 0.98779 | 0.21551 | 0.8602 | 0.77228 | 65.6666 | 120.4752 | 59.2043
39031.5641 | 2130 | 4 | 39031.5641 | 2478 | 3 |  | 1813.5 | 2032.5 | 130.0366 | 0.2442 | 151.2821 | 0.18315 | 1.3004 | 0.002442 | 1.5128 | 0.0018315 | 1.2979 | 1.511 | 23.8989 | 0.66519 | 59.5344
39031.5662 | 2079 | 0 | 39031.5663 | 2046 | 0 |  | 1998.5 | 2217.5 | 126.9231 | 0 | 124.9084 | 0 | 1.2692 | 0 | 1.2491 | 0 | 1.2692 | 1.2491 | 19.9798 | 21.915 | 18.7106
39031.5684 | 1987 | 1 | 39031.5684 | 2086 | 1 |  | 2183.5 | 2402.5 | 121.3065 | 0.06105 | 127.3504 | 0.06105 | 1.2131 | 0.0006105 | 1.2735 | 0.0006105 | 1.2125 | 1.2729 | 25.6136 | 19.6233 | 8306.7874
39031.5705 | 2265 | 5 | 39031.5705 | 2212 | 5 |  | 2368 | 2587 | 138.2784 | 0.30525 | 135.0427 | 0.30525 | 1.3828 | 0.0030525 | 1.3504 | 0.0030525 | 1.3797 | 1.3474 | 10.3242 | 13.0818 | 519.1456

## Raw IRMS Data
Time | DL1.V2000:B | DL1.V2001:B | DL1.V1500:B | Open Burn Test 8 |  |  | 2006-11-10 | 13:06
39031.5406 | 0 | 0 | 1 | Mix | 7-C | Tray C | IRMS | 2
39031.5427 | 0 | 0 | 1 |  | 150 kW |  | Bundle
39031.5448 | 0 | 0 | 1
39031.547 | 0 | 0 | 1
39031.5491 | 0 | 0 | 1
39031.5513 | 0 | 0 | 1
39031.5534 | 0 | 0 | 1
39031.5555 | 0 | 0 | 1
39031.5577 | 101 | 60 | 1
39031.5598 | 1214 | 895 | 1
39031.562 | 1761 | 352 | 1
39031.5641 | 2130 | 4 | 1
39031.5662 | 2079 | 0 | 1
39031.5684 | 1987 | 1 | 1
39031.5705 | 2265 | 5 | 1
1
39031.5406 | 0 | 0 | 2
39031.5427 | 0 | 0 | 2
39031.5449 | 0 | 0 | 2
39031.547 | 0 | 0 | 2
39031.5491 | 0 | 0 | 2
39031.5513 | 0 | 0 | 2
39031.5534 | 0 | 0 | 2
39031.5556 | 0 | 0 | 2
39031.5577 | 349 | 258 | 2
39031.5598 | 1385 | 695 | 2
39031.562 | 1618 | 353 | 2
39031.5641 | 2478 | 3 | 2
39031.5663 | 2046 | 0 | 2
39031.5684 | 2086 | 1 | 2
39031.5705 | 2212 | 5 | 2
2
39031.5406 | 0 | 0 | 3
39031.5427 | 0 | 0 | 3
39031.5449 | 0 | 0 | 3
39031.547 | 0 | 0 | 3
39031.5492 | 0 | 0 | 3
39031.5513 | 0 | 0 | 3
39031.5534 | 0 | 0 | 3
39031.5556 | 0 | 0 | 3
39031.5577 | 0 | 0 | 3
39031.5598 | 1188 | 0 | 3
39031.562 | 1788 | 0 | 3
39031.5641 | 2249 | 0 | 3
39031.5663 | 1984 | 0 | 3
39031.5684 | 2524 | 0 | 3
39031.5705 | 2272 | 0 | 3
3
39031.5406 | 0 | 0 | 4
39031.5428 | 0 | 0 | 4
39031.5449 | 0 | 0 | 4
39031.547 | 0 | 0 | 4
39031.5492 | 0 | 0 | 4
39031.5513 | 0 | 0 | 4
39031.5534 | 0 | 0 | 4
39031.5556 | 0 | 0 | 4
39031.5577 | 0 | 0 | 4
39031.5599 | 1289 | 0 | 4
39031.562 | 2264 | 0 | 4
39031.5641 | 2171 | 0 | 4
39031.5663 | 2241 | 0 | 4
39031.5684 | 2277 | 0 | 4
39031.5706 | 2172 | 0 | 4
4
39031.5406 | 0 | 0 | 5
39031.5428 | 0 | 0 | 5
39031.5449 | 0 | 0 | 5
39031.547 | 0 | 0 | 5
39031.5492 | 0 | 0 | 5
39031.5513 | 0 | 0 | 5
39031.5535 | 0 | 0 | 5
39031.5556 | 0 | 0 | 5
39031.5577 | 0 | 0 | 5
39031.5599 | 932 | 0 | 5
39031.562 | 1612 | 0 | 5
39031.5642 | 2192 | 0 | 5
39031.5663 | 2368 | 0 | 5
39031.5684 | 2442 | 0 | 5
39031.5706 | 2347 | 0 | 5
5
39031.5407 | 0 | 0 | 6
39031.5428 | 0 | 0 | 6
39031.5449 | 0 | 0 | 6
39031.5471 | 0 | 0 | 6
39031.5492 | 0 | 0 | 6
39031.5513 | 0 | 0 | 6
39031.5535 | 0 | 0 | 6
39031.5556 | 0 | 0 | 6
39031.5578 | 0 | 0 | 6
39031.5599 | 1451 | 0 | 6
39031.562 | 2195 | 0 | 6
39031.5642 | 2427 | 0 | 6
39031.5663 | 2447 | 0 | 6
39031.5685 | 1974 | 0 | 6
39031.5706 | 2252 | 0 | 6
6
39031.5407 | 0 | 0 | 7
39031.5428 | 0 | 0 | 7
39031.545 | 0 | 0 | 7
39031.5471 | 0 | 0 | 7
39031.5492 | 0 | 0 | 7
39031.5514 | 0 | 0 | 7
39031.5535 | 0 | 0 | 7
39031.5556 | 0 | 0 | 7
39031.5578 | 0 | 0 | 7
39031.5599 | 1014 | 23 | 7
39031.5621 | 1861 | 3 | 7
39031.5642 | 2415 | 0 | 7
39031.5663 | 2038 | 0 | 7
39031.5685 | 2072 | 0 | 7
39031.5706 | 2409 | 0 | 7
7
39031.5407 | 0 | 0 | 8
39031.5428 | 0 | 0 | 8
39031.545 | 0 | 0 | 8
39031.5471 | 0 | 0 | 8
39031.5492 | 0 | 0 | 8
39031.5514 | 0 | 0 | 8
39031.5535 | 0 | 0 | 8
39031.5557 | 0 | 0 | 8
39031.5578 | 0 | 0 | 8
39031.5599 | 1906 | 1 | 8
39031.5621 | 1909 | 3 | 8
39031.5642 | 1981 | 0 | 8
39031.5664 | 2558 | 0 | 8
39031.5685 | 2440 | 0 | 8
39031.5706 | 2500 | 1 | 8
8
39031.5407 | 0 | 0 | 9
39031.5428 | 0 | 0 | 9
39031.545 | 0 | 0 | 9
39031.5471 | 0 | 0 | 9
39031.5493 | 0 | 0 | 9
39031.5514 | 0 | 0 | 9
39031.5535 | 0 | 0 | 9
39031.5557 | 0 | 0 | 9
39031.5578 | 0 | 0 | 9
39031.56 | 1162 | 409 | 9
39031.5621 | 2034 | 0 | 9
39031.5642 | 2216 | 0 | 9
39031.5664 | 2131 | 0 | 9
39031.5685 | 2358 | 0 | 9
39031.5706 | 2201 | 1 | 9
9
39031.5407 | 0 | 0 | 10
39031.5429 | 0 | 0 | 10
39031.545 | 0 | 0 | 10
39031.5471 | 0 | 0 | 10
39031.5493 | 0 | 0 | 10
39031.5514 | 0 | 0 | 10
39031.5536 | 0 | 0 | 10
39031.5557 | 0 | 0 | 10
39031.5578 | 0 | 0 | 10
39031.56 | 1498 | 398 | 10
39031.5621 | 2043 | 1 | 10
39031.5642 | 2197 | 0 | 10
39031.5664 | 1987 | 0 | 10
39031.5685 | 2129 | 0 | 10
39031.5707 | 2356 | 1 | 10
10
39031.5407 | 0 | 0 | 11
39031.5429 | 0 | 0 | 11
39031.545 | 0 | 0 | 11
39031.5472 | 0 | 0 | 11
39031.5493 | 0 | 0 | 11
39031.5514 | 0 | 0 | 11
39031.5536 | 0 | 0 | 11
39031.5557 | 0 | 0 | 11
39031.5578 | 0 | 0 | 11
39031.56 | 1282 | 0 | 11
39031.5621 | 1793 | 0 | 11
39031.5643 | 1886 | 0 | 11
39031.5664 | 2504 | 0 | 11
39031.5685 | 2126 | 0 | 11
39031.5707 | 1909 | 1 | 11
11
39031.5408 | 0 | 0 | 12
39031.5429 | 0 | 0 | 12
39031.545 | 0 | 0 | 12
39031.5472 | 0 | 0 | 12
39031.5493 | 0 | 0 | 12
39031.5514 | 0 | 0 | 12
39031.5536 | 3 | 0 | 12
39031.5557 | 192 | 0 | 12
39031.5579 | 2449 | 0 | 12
39031.56 | 1970 | 0 | 12
39031.5621 | 2350 | 0 | 12
39031.5643 | 2346 | 0 | 12
39031.5664 | 2452 | 0 | 12
39031.5686 | 2159 | 0 | 12
39031.5707 | 2041 | 0 | 12
12
39031.5408 | 0 | 0 | 13
39031.5429 | 0 | 0 | 13
39031.545 | 0 | 0 | 13
39031.5472 | 0 | 0 | 13
39031.5493 | 0 | 0 | 13
39031.5515 | 0 | 0 | 13
39031.5536 | 0 | 0 | 13
39031.5557 | 0 | 0 | 13
39031.5579 | 0 | 0 | 13
39031.56 | 1503 | 0 | 13
39031.5622 | 1962 | 0 | 13
39031.5643 | 2315 | 0 | 13
39031.5664 | 2492 | 0 | 13
39031.5686 | 1938 | 0 | 13
13
39031.5408 | 0 | 0 | 14
39031.5429 | 0 | 0 | 14
39031.5451 | 0 | 0 | 14
39031.5472 | 0 | 0 | 14
39031.5493 | 0 | 0 | 14
39031.5515 | 0 | 0 | 14
39031.5536 | 0 | 0 | 14
39031.5558 | 1348 | 0 | 14
39031.5579 | 2111 | 0 | 14
39031.56 | 2039 | 0 | 14
39031.5622 | 2558 | 0 | 14
39031.5643 | 2343 | 0 | 14
39031.5664 | 2009 | 0 | 14
39031.5686 | 2386 | 0 | 14
39031.5707 | 2158 | 0 | 14
14
39031.5408 | 0 | 0 | 15
39031.5429 | 0 | 0 | 15
39031.5451 | 0 | 0 | 15
39031.5472 | 0 | 0 | 15
39031.5494 | 0 | 0 | 15
39031.5515 | 0 | 0 | 15
39031.5536 | 0 | 0 | 15
39031.5558 | 0 | 0 | 15
39031.5579 | 0 | 0 | 15
39031.56 | 1291 | 0 | 15
39031.5622 | 1878 | 0 | 15
39031.5643 | 1937 | 0 | 15
39031.5665 | 2553 | 0 | 15
39031.5686 | 2240 | 0 | 15
39031.5707 | 2052 | 0 | 15
15
39031.5408 | 0 | 0 | 16
39031.543 | 0 | 0 | 16
39031.5451 | 0 | 0 | 16
39031.5472 | 0 | 0 | 16
39031.5494 | 2036 | 0 | 16
39031.5515 | 2541 | 0 | 16
39031.5536 | 2022 | 0 | 16
39031.5558 | 2074 | 0 | 16
39031.5579 | 2078 | 0 | 16
39031.5601 | 2054 | 0 | 16
39031.5622 | 2501 | 0 | 16
39031.5643 | 2295 | 0 | 16
39031.5665 | 2199 | 0 | 16
39031.5686 | 2217 | 0 | 16
39031.5708 | 2550 | 0 | 16
16
39031.5408 | 0 | 0 | 17
39031.543 | 0 | 0 | 17
39031.5451 | 0 | 0 | 17
39031.5472 | 0 | 0 | 17
39031.5494 | 0 | 0 | 17
39031.5515 | 0 | 0 | 17
39031.5537 | 0 | 0 | 17
39031.5558 | 0 | 0 | 17
39031.5579 | 0 | 0 | 17
39031.5601 | 1842 | 0 | 17
39031.5622 | 2241 | 0 | 17
39031.5644 | 2469 | 0 | 17
39031.5665 | 1963 | 0 | 17
39031.5686 | 2170 | 0 | 17
39031.5708 | 1951 | 0 | 17
17
39031.5408 | 0 | 0 | 18
39031.543 | 0 | 0 | 18
39031.5451 | 0 | 0 | 18
39031.5473 | 0 | 0 | 18
39031.5494 | 0 | 0 | 18
39031.5515 | 0 | 0 | 18
39031.5537 | 2054 | 0 | 18
39031.5558 | 2224 | 0 | 18
39031.558 | 2524 | 0 | 18
39031.5601 | 2561 | 0 | 18
39031.5622 | 2145 | 0 | 18
39031.5644 | 2603 | 0 | 18
39031.5665 | 2273 | 0 | 18
39031.5686 | 2522 | 0 | 18
39031.5708 | 2406 | 0 | 18
18
39031.5409 | 0 | 0 | 19
39031.543 | 0 | 0 | 19
39031.5451 | 0 | 0 | 19
39031.5473 | 0 | 0 | 19
39031.5494 | 0 | 0 | 19
39031.5516 | 0 | 0 | 19
39031.5537 | 0 | 0 | 19
39031.5558 | 0 | 0 | 19
39031.558 | 0 | 0 | 19
39031.5601 | 1640 | 0 | 19
39031.5622 | 1776 | 0 | 19
39031.5644 | 1960 | 0 | 19
39031.5665 | 2003 | 0 | 19
39031.5687 | 2006 | 0 | 19
39031.5708 | 2038 | 0 | 19
19
39031.5409 | 0 | 0 | 20
39031.543 | 0 | 0 | 20
39031.5452 | 0 | 0 | 20
39031.5473 | 0 | 0 | 20
39031.5494 | 0 | 0 | 20
39031.5516 | 0 | 0 | 20
39031.5537 | 0 | 0 | 20
39031.5559 | 1254 | 0 | 20
39031.558 | 2126 | 0 | 20
39031.5601 | 2081 | 0 | 20
39031.5623 | 2595 | 0 | 20
39031.5644 | 2001 | 0 | 20
39031.5665 | 2351 | 0 | 20
39031.5687 | 2357 | 0 | 20
39031.5708 | 2158 | 0 | 20
20
39031.5409 | 0 | 0 | 21
39031.543 | 0 | 0 | 21
39031.5452 | 0 | 0 | 21
39031.5473 | 0 | 0 | 21
39031.5495 | 0 | 0 | 21
39031.5516 | 0 | 0 | 21
39031.5537 | 0 | 0 | 21
39031.5559 | 0 | 0 | 21
39031.558 | 0 | 0 | 21
39031.5602 | 1450 | 0 | 21
39031.5623 | 1897 | 0 | 21
39031.5644 | 1965 | 0 | 21
39031.5666 | 2098 | 0 | 21
39031.5687 | 2210 | 0 | 21
39031.5708 | 1882 | 0 | 21
21
39031.5409 | 0 | 0 | 22
39031.5431 | 0 | 0 | 22
39031.5452 | 0 | 0 | 22
39031.5473 | 0 | 0 | 22
39031.5495 | 0 | 0 | 22
39031.5516 | 0 | 0 | 22
39031.5537 | 0 | 0 | 22
39031.5559 | 376 | 0 | 22
39031.558 | 1965 | 0 | 22
39031.5602 | 1976 | 0 | 22
39031.5623 | 2584 | 0 | 22
39031.5644 | 2161 | 0 | 22
39031.5666 | 2054 | 0 | 22
39031.5687 | 2578 | 0 | 22
39031.5709 | 1965 | 0 | 22
22
39031.5409 | 0 | 0 | 23
39031.5431 | 0 | 0 | 23
39031.5452 | 0 | 0 | 23
39031.5473 | 0 | 0 | 23
39031.5495 | 0 | 0 | 23
39031.5516 | 0 | 0 | 23
39031.5538 | 0 | 0 | 23
39031.5559 | 0 | 0 | 23
39031.558 | 0 | 0 | 23
39031.5602 | 1383 | 0 | 23
39031.5623 | 2205 | 0 | 23
39031.5645 | 2178 | 0 | 23
39031.5666 | 2030 | 0 | 23
39031.5687 | 2102 | 0 | 23
39031.5709 | 2081 | 1 | 23
23
39031.5409 | 0 | 0 | 24
39031.5431 | 0 | 0 | 24
39031.5452 | 0 | 0 | 24
39031.5474 | 0 | 0 | 24
39031.5495 | 0 | 0 | 24
39031.5516 | 0 | 0 | 24
39031.5538 | 0 | 0 | 24
39031.5559 | 0 | 0 | 24
39031.5581 | 0 | 0 | 24
39031.5602 | 1490 | 0 | 24
39031.5623 | 1918 | 0 | 24
39031.5645 | 2046 | 0 | 24
39031.5666 | 2583 | 0 | 24
39031.5687 | 2537 | 0 | 24
39031.5709 | 2355 | 0 | 24
24
39031.541 | 0 | 0 | 25
39031.5431 | 0 | 0 | 25
39031.5452 | 0 | 0 | 25
39031.5474 | 0 | 0 | 25
39031.5495 | 0 | 0 | 25
39031.5517 | 0 | 0 | 25
39031.5538 | 0 | 0 | 25
39031.5559 | 0 | 0 | 25
39031.5581 | 0 | 0 | 25
39031.5602 | 1236 | 0 | 25
39031.5623 | 1935 | 0 | 25
39031.5645 | 2074 | 0 | 25
39031.5666 | 2177 | 0 | 25
39031.5688 | 2002 | 0 | 25
39031.5709 | 2201 | 1 | 25
25
39031.541 | 0 | 0 | 26
39031.5431 | 0 | 0 | 26
39031.5453 | 0 | 0 | 26
39031.5474 | 0 | 0 | 26
39031.5495 | 0 | 0 | 26
39031.5517 | 0 | 0 | 26
39031.5538 | 0 | 0 | 26
39031.5559 | 0 | 0 | 26
39031.5581 | 0 | 0 | 26
39031.5602 | 1506 | 0 | 26
39031.5624 | 1434 | 0 | 26
39031.5645 | 2002 | 0 | 26
39031.5666 | 2540 | 0 | 26
39031.5688 | 1981 | 0 | 26
39031.5709 | 1962 | 0 | 26
26
39031.541 | 0 | 0 | 27
39031.5431 | 0 | 0 | 27
39031.5453 | 0 | 0 | 27
39031.5474 | 0 | 0 | 27
39031.5495 | 0 | 0 | 27
39031.5517 | 0 | 0 | 27
39031.5538 | 0 | 0 | 27
39031.556 | 0 | 0 | 27
39031.5581 | 0 | 0 | 27
39031.5602 | 1426 | 66 | 27
39031.5624 | 1300 | 0 | 27
39031.5645 | 2473 | 0 | 27
39031.5667 | 2040 | 0 | 27
39031.5688 | 2014 | 0 | 27
39031.5709 | 2222 | 1 | 27
27
39031.541 | 0 | 0 | 28
39031.5431 | 0 | 0 | 28
39031.5453 | 0 | 0 | 28
39031.5474 | 0 | 0 | 28
39031.5496 | 0 | 0 | 28
39031.5517 | 0 | 0 | 28
39031.5538 | 0 | 0 | 28
39031.556 | 0 | 0 | 28
39031.5581 | 0 | 0 | 28
39031.5603 | 1779 | 77 | 28
39031.5624 | 2436 | 0 | 28
39031.5645 | 2384 | 0 | 28
39031.5667 | 1979 | 0 | 28
39031.5688 | 2253 | 0 | 28
39031.5709 | 2449 | 1 | 28
28
39031.541 | 0 | 0 | 29
39031.5432 | 0 | 0 | 29
39031.5453 | 0 | 0 | 29
39031.5474 | 0 | 0 | 29
39031.5496 | 0 | 0 | 29
39031.5517 | 0 | 0 | 29
39031.5539 | 0 | 0 | 29
39031.556 | 0 | 0 | 29
39031.5581 | 0 | 0 | 29
39031.5603 | 1446 | 129 | 29
39031.5624 | 1562 | 0 | 29
39031.5645 | 2230 | 0 | 29
39031.5667 | 2437 | 0 | 29
39031.5688 | 2370 | 0 | 29
39031.571 | 2037 | 0 | 29
29
39031.541 | 0 | 0 | 30
39031.5432 | 0 | 0 | 30
39031.5453 | 0 | 0 | 30
39031.5475 | 0 | 0 | 30
39031.5496 | 0 | 0 | 30
39031.5517 | 0 | 0 | 30
39031.5539 | 0 | 0 | 30
39031.556 | 0 | 0 | 30
39031.5581 | 0 | 0 | 30
39031.5624 | 2413 | 0 | 30
39031.5646 | 1986 | 0 | 30
39031.5667 | 2583 | 0 | 30
39031.5688 | 2065 | 0 | 30
39031.571 | 1977 | 1 | 30
30
39031.5411 | 0 | 0 | 31
39031.5432 | 0 | 0 | 31
39031.5453 | 0 | 0 | 31
39031.5475 | 0 | 0 | 31
39031.5496 | 0 | 0 | 31
39031.5517 | 0 | 0 | 31
39031.5539 | 0 | 0 | 31
39031.556 | 0 | 0 | 31
39031.5582 | 0 | 0 | 31
39031.5603 | 1685 | 0 | 31
39031.5624 | 1992 | 0 | 31
39031.5646 | 2426 | 0 | 31
39031.5667 | 2213 | 0 | 31
39031.5689 | 2299 | 0 | 31
39031.571 | 1887 | 0 | 31
31
39031.5411 | 0 | 0 | 32
39031.5432 | 0 | 0 | 32
39031.5453 | 0 | 0 | 32
39031.5475 | 0 | 0 | 32
39031.5496 | 0 | 0 | 32
39031.5518 | 0 | 0 | 32
39031.5539 | 0 | 0 | 32
39031.556 | 1849 | 0 | 32
39031.5582 | 1944 | 0 | 32
39031.5603 | 1980 | 0 | 32
39031.5625 | 2450 | 0 | 32
39031.5646 | 2068 | 0 | 32
39031.5667 | 2014 | 0 | 32
39031.5689 | 2134 | 0 | 32
39031.571 | 2186 | 0 | 32
32
39031.5411 | 0 | 0 | 33
39031.5432 | 0 | 0 | 33
39031.5454 | 0 | 0 | 33
39031.5475 | 0 | 0 | 33
39031.5496 | 0 | 0 | 33
39031.5518 | 0 | 0 | 33
39031.5539 | 0 | 0 | 33
39031.5561 | 0 | 0 | 33
39031.5582 | 0 | 0 | 33
39031.5603 | 1595 | 0 | 33
39031.5625 | 2082 | 0 | 33
39031.5646 | 2214 | 0 | 33
39031.5668 | 2383 | 0 | 33
39031.5689 | 2477 | 0 | 33
39031.571 | 2352 | 1 | 33
33
39031.5411 | 0 | 0 | 34
39031.5433 | 0 | 0 | 34
39031.5454 | 0 | 0 | 34
39031.5475 | 0 | 0 | 34
39031.5497 | 0 | 0 | 34
39031.5518 | 0 | 0 | 34
39031.5539 | 0 | 0 | 34
39031.5561 | 2167 | 0 | 34
39031.5582 | 2423 | 0 | 34
39031.5604 | 2550 | 0 | 34
39031.5625 | 2024 | 0 | 34
39031.5646 | 2589 | 0 | 34
39031.5668 | 2274 | 0 | 34
39031.5689 | 2046 | 0 | 34
39031.5711 | 1933 | 0 | 34
34
39031.5411 | 0 | 0 | 35
39031.5433 | 0 | 0 | 35
39031.5454 | 0 | 0 | 35
39031.5475 | 0 | 0 | 35
39031.5497 | 0 | 0 | 35
39031.5518 | 0 | 0 | 35
39031.554 | 0 | 0 | 35
39031.5561 | 0 | 0 | 35
39031.5582 | 0 | 0 | 35
39031.5604 | 1735 | 0 | 35
39031.5625 | 2149 | 0 | 35
39031.5647 | 2125 | 0 | 35
39031.5668 | 2068 | 0 | 35
39031.5689 | 2257 | 0 | 35
39031.5711 | 1920 | 0 | 35
35
39031.5411 | 0 | 0 | 36
39031.5433 | 0 | 0 | 36
39031.5454 | 0 | 0 | 36
39031.5476 | 0 | 0 | 36
39031.5497 | 2183 | 0 | 36
39031.5518 | 2157 | 1 | 36
39031.554 | 2461 | 0 | 36
39031.5561 | 1941 | 0 | 36
39031.5583 | 2515 | 0 | 36
39031.5604 | 2072 | 0 | 36
39031.5625 | 2370 | 0 | 36
39031.5647 | 2113 | 0 | 36
39031.5668 | 2540 | 0 | 36
39031.5689 | 2327 | 0 | 36
39031.5711 | 2174 | 0 | 36
36
39031.5412 | 0 | 0 | 37
39031.5433 | 0 | 0 | 37
39031.5454 | 0 | 0 | 37
39031.5476 | 0 | 0 | 37
39031.5497 | 0 | 0 | 37
39031.5519 | 0 | 0 | 37
39031.554 | 0 | 0 | 37
39031.5561 | 0 | 0 | 37
39031.5583 | 0 | 0 | 37
39031.5604 | 1668 | 0 | 37
39031.5625 | 1692 | 0 | 37
39031.5647 | 2417 | 0 | 37
39031.5668 | 2560 | 0 | 37
39031.569 | 2282 | 0 | 37
39031.5711 | 2393 | 0 | 37
37
39031.5412 | 0 | 0 | 38
39031.5433 | 0 | 0 | 38
39031.5455 | 0 | 0 | 38
39031.5476 | 0 | 0 | 38
39031.5497 | 0 | 0 | 38
39031.5519 | 0 | 0 | 38
39031.554 | 2085 | 0 | 38
39031.5561 | 1948 | 0 | 38
39031.5583 | 2302 | 0 | 38
39031.5604 | 1973 | 0 | 38
39031.5626 | 2114 | 0 | 38
39031.5647 | 2558 | 0 | 38
39031.5668 | 2036 | 0 | 38
39031.569 | 2603 | 0 | 38
39031.5711 | 2244 | 0 | 38
38
39031.5412 | 0 | 0 | 39
39031.5433 | 0 | 0 | 39
39031.5455 | 0 | 0 | 39
39031.5476 | 0 | 0 | 39
39031.5497 | 0 | 0 | 39
39031.5519 | 0 | 0 | 39
39031.554 | 0 | 0 | 39
39031.5562 | 0 | 0 | 39
39031.5583 | 0 | 0 | 39
39031.5604 | 1606 | 0 | 39
39031.5626 | 2117 | 0 | 39
39031.5647 | 2217 | 0 | 39
39031.5669 | 1947 | 0 | 39
39031.569 | 2501 | 0 | 39
39031.5711 | 2263 | 0 | 39
39
39031.5412 | 0 | 0 | 40
39031.5433 | 0 | 0 | 40
39031.5455 | 0 | 0 | 40
39031.5476 | 0 | 0 | 40
39031.5498 | 0 | 0 | 40
39031.5519 | 0 | 0 | 40
39031.554 | 0 | 0 | 40
39031.5562 | 1553 | 0 | 40
39031.5583 | 2316 | 0 | 40
39031.5605 | 2490 | 0 | 40
39031.5626 | 2571 | 0 | 40
39031.5647 | 2205 | 0 | 40
39031.5669 | 2235 | 0 | 40
39031.569 | 2151 | 0 | 40
39031.5711 | 2148 | 0 | 40
40
39031.5412 | 0 | 0 | 41
39031.5434 | 0 | 0 | 41
39031.5455 | 0 | 0 | 41
39031.5476 | 0 | 0 | 41
39031.5498 | 0 | 0 | 41
39031.5519 | 0 | 0 | 41
39031.5541 | 0 | 0 | 41
39031.5562 | 0 | 0 | 41
39031.5583 | 0 | 0 | 41
39031.5605 | 1872 | 0 | 41
39031.5626 | 1829 | 0 | 41
39031.5647 | 1975 | 0 | 41
39031.5669 | 2185 | 0 | 41
39031.569 | 1955 | 0 | 41
39031.5712 | 2022 | 0 | 41
41
39031.5412 | 0 | 0 | 42
39031.5434 | 0 | 0 | 42
39031.5455 | 0 | 0 | 42
39031.5477 | 0 | 0 | 42
39031.5498 | 0 | 0 | 42
39031.5519 | 0 | 0 | 42
39031.5541 | 0 | 0 | 42
39031.5562 | 573 | 0 | 42
39031.5583 | 2056 | 0 | 42
39031.5605 | 2391 | 0 | 42
39031.5626 | 2014 | 0 | 42
39031.5648 | 2153 | 0 | 42
39031.5669 | 2536 | 0 | 42
39031.569 | 2213 | 0 | 42
39031.5712 | 2475 | 0 | 42
42
39031.5413 | 0 | 0 | 43
39031.5434 | 0 | 0 | 43
39031.5455 | 0 | 0 | 43
39031.5477 | 0 | 0 | 43
39031.5498 | 0 | 0 | 43
39031.5519 | 0 | 0 | 43
39031.5541 | 0 | 0 | 43
39031.5562 | 0 | 0 | 43
39031.5584 | 0 | 0 | 43
39031.5605 | 1511 | 11 | 43
39031.5626 | 2014 | 14 | 43
39031.5648 | 2143 | 0 | 43
39031.5669 | 2092 | 0 | 43
39031.5691 | 2549 | 1 | 43
39031.5712 | 1984 | 3 | 43
43
39031.5413 | 0 | 0 | 44
39031.5434 | 0 | 0 | 44
39031.5455 | 0 | 0 | 44
39031.5477 | 0 | 0 | 44
39031.5498 | 0 | 0 | 44
39031.552 | 0 | 0 | 44
39031.5541 | 0 | 0 | 44
39031.5562 | 0 | 0 | 44
39031.5584 | 0 | 0 | 44
39031.5605 | 1373 | 15 | 44
39031.5627 | 2023 | 13 | 44
39031.5648 | 2004 | 0 | 44
39031.5669 | 2436 | 0 | 44
39031.5691 | 2016 | 1 | 44
39031.5712 | 2175 | 2 | 44
44
39031.5413 | 0 | 0 | 45
39031.5434 | 0 | 0 | 45
39031.5456 | 0 | 0 | 45
39031.5477 | 0 | 0 | 45
39031.5498 | 0 | 0 | 45
39031.552 | 0 | 0 | 45
39031.5541 | 0 | 0 | 45
39031.5563 | 0 | 0 | 45
39031.5584 | 0 | 0 | 45
39031.5605 | 1920 | 0 | 45
39031.5627 | 2119 | 0 | 45
39031.5648 | 2261 | 0 | 45
39031.5669 | 2542 | 0 | 45
39031.5691 | 2011 | 0 | 45
39031.5712 | 2163 | 0 | 45
45
39031.5413 | 0 | 0 | 46
39031.5434 | 0 | 0 | 46
39031.5456 | 0 | 0 | 46
39031.5477 | 0 | 0 | 46
39031.5499 | 0 | 0 | 46
39031.552 | 0 | 0 | 46
39031.5541 | 0 | 0 | 46
39031.5563 | 0 | 0 | 46
39031.5584 | 0 | 0 | 46
39031.5605 | 1841 | 0 | 46
39031.5627 | 2311 | 0 | 46
39031.5648 | 2140 | 0 | 46
39031.567 | 2179 | 0 | 46
39031.5691 | 1959 | 0 | 46
39031.5712 | 2475 | 0 | 46
46
39031.5413 | 0 | 0 | 47
39031.5435 | 0 | 0 | 47
39031.5456 | 0 | 0 | 47
39031.5477 | 0 | 0 | 47
39031.552 | 0 | 0 | 47
39031.5542 | 0 | 0 | 47
39031.5563 | 0 | 0 | 47
39031.5584 | 0 | 0 | 47
39031.5606 | 1941 | 0 | 47
39031.5627 | 2379 | 0 | 47
39031.5648 | 2409 | 0 | 47
39031.567 | 2013 | 0 | 47
39031.5691 | 2403 | 0 | 47
39031.5713 | 2094 | 1 | 47
47
39031.5413 | 0 | 0 | 48
39031.5435 | 0 | 0 | 48
39031.5456 | 0 | 0 | 48
39031.5478 | 0 | 0 | 48
39031.5499 | 0 | 0 | 48
39031.552 | 0 | 0 | 48
39031.5542 | 0 | 0 | 48
39031.5563 | 0 | 0 | 48
39031.5584 | 0 | 0 | 48
39031.5606 | 1504 | 0 | 48
39031.5627 | 2450 | 0 | 48
39031.5649 | 2092 | 0 | 48
39031.567 | 2487 | 0 | 48
39031.5691 | 2449 | 0 | 48
39031.5713 | 2220 | 1 | 48
48
39031.5414 | 0 | 0 | 49
39031.5435 | 0 | 0 | 49
39031.5456 | 0 | 0 | 49
39031.5478 | 0 | 0 | 49
39031.5499 | 0 | 0 | 49
39031.552 | 0 | 0 | 49
39031.5542 | 0 | 0 | 49
39031.5563 | 0 | 0 | 49
39031.5585 | 0 | 0 | 49
39031.5606 | 1929 | 0 | 49
39031.5627 | 2436 | 0 | 49
39031.5649 | 2448 | 0 | 49
39031.567 | 2256 | 0 | 49
39031.5692 | 2111 | 0 | 49
39031.5713 | 2238 | 7 | 49
49
39031.5414 | 0 | 0 | 50
39031.5435 | 0 | 0 | 50
39031.5456 | 0 | 0 | 50
39031.5478 | 0 | 0 | 50
39031.5499 | 0 | 0 | 50
39031.5521 | 0 | 0 | 50
39031.5542 | 17 | 0 | 50
39031.5563 | 1984 | 0 | 50
39031.5585 | 1970 | 0 | 50
39031.5606 | 2177 | 0 | 50
39031.5628 | 2520 | 0 | 50
39031.5649 | 2563 | 0 | 50
39031.567 | 2294 | 0 | 50
39031.5692 | 2151 | 0 | 50
39031.5713 | 2528 | 0 | 50
50
39031.5414 | 0 | 0 | 51
39031.5435 | 0 | 0 | 51
39031.5457 | 0 | 0 | 51
39031.5478 | 0 | 0 | 51
39031.5499 | 0 | 0 | 51
39031.5521 | 0 | 0 | 51
39031.5542 | 0 | 0 | 51
39031.5564 | 0 | 0 | 51
39031.5585 | 0 | 0 | 51
39031.5606 | 1591 | 0 | 51
39031.5628 | 2140 | 0 | 51
39031.5649 | 2199 | 0 | 51
39031.567 | 2183 | 0 | 51
39031.5692 | 1942 | 0 | 51
39031.5713 | 1918 | 1 | 51
51
39031.5414 | 0 | 0 | 52
39031.5435 | 0 | 0 | 52
39031.5457 | 0 | 0 | 52
39031.5478 | 0 | 0 | 52
39031.55 | 0 | 0 | 52
39031.5521 | 0 | 1 | 52
39031.5542 | 46 | 0 | 52
39031.5564 | 2020 | 0 | 52
39031.5585 | 1925 | 0 | 52
39031.5606 | 2502 | 0 | 52
39031.5628 | 2537 | 0 | 52
39031.5649 | 2545 | 0 | 52
39031.5671 | 1980 | 0 | 52
39031.5692 | 2019 | 0 | 52
39031.5713 | 2044 | 0 | 52
52
39031.5414 | 0 | 0 | 53
39031.5436 | 0 | 0 | 53
39031.5457 | 0 | 0 | 53
39031.5478 | 0 | 0 | 53
39031.55 | 0 | 0 | 53
39031.5521 | 0 | 0 | 53
39031.5542 | 0 | 0 | 53
39031.5564 | 0 | 0 | 53
39031.5585 | 0 | 0 | 53
39031.5607 | 1647 | 0 | 53
39031.5628 | 2097 | 0 | 53
39031.5649 | 1997 | 0 | 53
39031.5671 | 2028 | 0 | 53
39031.5692 | 2501 | 0 | 53
39031.5714 | 1980 | 0 | 53
53
39031.5414 | 0 | 0 | 54
39031.5436 | 0 | 0 | 54
39031.5457 | 0 | 0 | 54
39031.5478 | 0 | 0 | 54
39031.55 | 2228 | 5 | 54
39031.5521 | 2226 | 3 | 54
39031.5543 | 2164 | 0 | 54
39031.5564 | 2402 | 0 | 54
39031.5585 | 1989 | 0 | 54
39031.5607 | 2185 | 0 | 54
39031.5628 | 2442 | 0 | 54
39031.565 | 2572 | 0 | 54
39031.5671 | 2118 | 0 | 54
39031.5692 | 2562 | 0 | 54
39031.5714 | 2268 | 0 | 54
54
39031.5414 | 0 | 0 | 55
39031.5436 | 0 | 0 | 55
39031.5457 | 0 | 0 | 55
39031.5479 | 0 | 0 | 55
39031.55 | 0 | 0 | 55
39031.5521 | 0 | 0 | 55
39031.5543 | 0 | 0 | 55
39031.5564 | 0 | 0 | 55
39031.5586 | 0 | 0 | 55
39031.5607 | 1643 | 0 | 55
39031.5628 | 1907 | 0 | 55
39031.565 | 2497 | 0 | 55
39031.5671 | 2260 | 0 | 55
39031.5692 | 1962 | 0 | 55
39031.5714 | 1902 | 0 | 55
55
39031.5415 | 0 | 0 | 56
39031.5436 | 0 | 0 | 56
39031.5457 | 0 | 0 | 56
39031.5479 | 0 | 0 | 56
39031.55 | 0 | 0 | 56
39031.5522 | 0 | 0 | 56
39031.5543 | 1998 | 0 | 56
39031.5564 | 2114 | 0 | 56
39031.5586 | 2102 | 0 | 56
39031.5607 | 2499 | 0 | 56
39031.5628 | 2379 | 0 | 56
39031.565 | 2372 | 0 | 56
39031.5671 | 2140 | 0 | 56
39031.5693 | 2382 | 0 | 56
39031.5714 | 2606 | 0 | 56
56
39031.5415 | 0 | 0 | 57
39031.5436 | 0 | 0 | 57
39031.5458 | 0 | 0 | 57
39031.5479 | 0 | 0 | 57
39031.55 | 0 | 0 | 57
39031.5522 | 0 | 0 | 57
39031.5543 | 0 | 0 | 57
39031.5564 | 0 | 0 | 57
39031.5586 | 0 | 0 | 57
39031.5607 | 1952 | 0 | 57
39031.5629 | 1861 | 0 | 57
39031.565 | 2508 | 0 | 57
39031.5671 | 2478 | 0 | 57
39031.5693 | 1992 | 0 | 57
39031.5714 | 2024 | 0 | 57
57
39031.5415 | 0 | 0 | 58
39031.5436 | 0 | 0 | 58
39031.5458 | 0 | 0 | 58
39031.5479 | 0 | 0 | 58
39031.55 | 0 | 0 | 58
39031.5522 | 0 | 0 | 58
39031.5543 | 0 | 0 | 58
39031.5565 | 1899 | 0 | 58
39031.5586 | 1998 | 0 | 58
39031.5607 | 1980 | 0 | 58
39031.5629 | 2211 | 0 | 58
39031.565 | 2462 | 0 | 58
39031.5672 | 2130 | 0 | 58
39031.5693 | 2569 | 0 | 58
39031.5714 | 2104 | 0 | 58
58
39031.5415 | 0 | 0 | 59
39031.5437 | 0 | 0 | 59
39031.5458 | 0 | 0 | 59
39031.5479 | 0 | 0 | 59
39031.5501 | 0 | 0 | 59
39031.5522 | 0 | 0 | 59
39031.5543 | 0 | 0 | 59
39031.5565 | 0 | 0 | 59
39031.5586 | 0 | 0 | 59
39031.5608 | 1743 | 0 | 59
39031.5629 | 1947 | 0 | 59
39031.565 | 2049 | 0 | 59
39031.5672 | 1963 | 0 | 59
39031.5693 | 2496 | 0 | 59
39031.5715 | 2176 | 0 | 59
59
39031.5415 | 0 | 0 | 60
39031.5437 | 0 | 0 | 60
39031.5458 | 0 | 0 | 60
39031.5479 | 0 | 0 | 60
39031.5501 | 0 | 0 | 60
39031.5522 | 0 | 0 | 60
39031.5544 | 0 | 0 | 60
39031.5565 | 2383 | 0 | 60
39031.5586 | 2534 | 0 | 60
39031.5608 | 2109 | 0 | 60
39031.5629 | 2411 | 0 | 60
39031.5651 | 2610 | 0 | 60
39031.5672 | 2052 | 0 | 60
39031.5693 | 2553 | 0 | 60
39031.5715 | 2573 | 0 | 60
60
39031.5416 | 0 | 0 | 61
39031.5437 | 0 | 0 | 61
39031.5458 | 0 | 0 | 61
39031.548 | 0 | 0 | 61
39031.5501 | 0 | 0 | 61
39031.5522 | 0 | 0 | 61
39031.5544 | 0 | 0 | 61
39031.5565 | 0 | 0 | 61
39031.5587 | 0 | 0 | 61
39031.5608 | 1802 | 0 | 61
39031.5629 | 2253 | 0 | 61
39031.5651 | 1975 | 0 | 61
39031.5672 | 2214 | 0 | 61
39031.5694 | 2085 | 0 | 61
39031.5715 | 2490 | 0 | 61
61
39031.5416 | 0 | 0 | 62
39031.5437 | 0 | 0 | 62
39031.5458 | 0 | 0 | 62
39031.548 | 0 | 0 | 62
39031.5501 | 0 | 0 | 62
39031.5523 | 0 | 0 | 62
39031.5544 | 0 | 0 | 62
39031.5565 | 0 | 0 | 62
39031.5587 | 11 | 0 | 62
39031.5608 | 1920 | 0 | 62
39031.563 | 2553 | 0 | 62
39031.5651 | 2175 | 0 | 62
39031.5672 | 2127 | 0 | 62
39031.5694 | 2026 | 0 | 62
39031.5715 | 1911 | 0 | 62
62
39031.5416 | 0 | 0 | 63
39031.5437 | 0 | 0 | 63
39031.5459 | 0 | 0 | 63
39031.548 | 0 | 0 | 63
39031.5501 | 0 | 0 | 63
39031.5523 | 0 | 0 | 63
39031.5544 | 0 | 0 | 63
39031.5566 | 0 | 0 | 63
39031.5587 | 0 | 0 | 63
39031.5608 | 1709 | 0 | 63
39031.563 | 2470 | 0 | 63
39031.5651 | 2145 | 0 | 63
39031.5672 | 2127 | 0 | 63
39031.5694 | 1967 | 0 | 63
39031.5715 | 2114 | 1 | 63
63
39031.5416 | 0 | 0 | 64
39031.5437 | 0 | 0 | 64
39031.5459 | 0 | 0 | 64
39031.548 | 0 | 0 | 64
39031.5502 | 0 | 0 | 64
39031.5523 | 0 | 0 | 64
39031.5544 | 0 | 0 | 64
39031.5566 | 0 | 0 | 64
39031.5587 | 0 | 0 | 64
39031.5608 | 2086 | 0 | 64
39031.563 | 2054 | 0 | 64
39031.5651 | 2039 | 0 | 64
39031.5673 | 2588 | 0 | 64
39031.5694 | 2191 | 0 | 64
39031.5715 | 2367 | 1 | 64
64
39031.5416 | 0 | 0 | 65
39031.5437 | 0 | 0 | 65
39031.5459 | 0 | 0 | 65
39031.548 | 0 | 0 | 65
39031.5502 | 0 | 0 | 65
39031.5523 | 0 | 0 | 65
39031.5544 | 0 | 0 | 65
39031.5566 | 0 | 0 | 65
39031.5587 | 0 | 0 | 65
39031.5609 | 1723 | 0 | 65
39031.563 | 2095 | 0 | 65
39031.5651 | 2314 | 0 | 65
39031.5673 | 1971 | 0 | 65
39031.5694 | 1986 | 0 | 65
39031.5716 | 2440 | 1 | 65
65
39031.5416 | 0 | 0 | 66
39031.5438 | 0 | 0 | 66
39031.5459 | 0 | 0 | 66
39031.548 | 0 | 0 | 66
39031.5502 | 0 | 0 | 66
39031.5523 | 0 | 0 | 66
39031.5545 | 65 | 0 | 66
39031.5566 | 2034 | 0 | 66
39031.5587 | 2520 | 0 | 66
39031.5609 | 2464 | 0 | 66
39031.563 | 2565 | 0 | 66
39031.5652 | 1978 | 1 | 66
39031.5673 | 2265 | 0 | 66
39031.5694 | 2159 | 0 | 66
39031.5716 | 1908 | 0 | 66
66
39031.5416 | 0 | 0 | 67
39031.5438 | 0 | 0 | 67
39031.5459 | 0 | 0 | 67
39031.5481 | 0 | 0 | 67
39031.5502 | 0 | 0 | 67
39031.5523 | 0 | 0 | 67
39031.5545 | 0 | 0 | 67
39031.5566 | 0 | 0 | 67
39031.5587 | 0 | 0 | 67
39031.5609 | 1771 | 0 | 67
39031.563 | 2452 | 0 | 67
39031.5652 | 2454 | 0 | 67
39031.5673 | 1960 | 0 | 67
39031.5694 | 2136 | 0 | 67
39031.5716 | 1917 | 4 | 67
67
39031.5417 | 0 | 0 | 68
39031.5438 | 0 | 0 | 68
39031.5459 | 0 | 0 | 68
39031.5481 | 0 | 0 | 68
39031.5502 | 0 | 0 | 68
39031.5523 | 0 | 0 | 68
39031.5545 | 96 | 0 | 68
39031.5566 | 1937 | 0 | 68
39031.5588 | 1960 | 0 | 68
39031.5609 | 2262 | 0 | 68
39031.563 | 2100 | 0 | 68
39031.5652 | 2075 | 0 | 68
39031.5673 | 2524 | 0 | 68
39031.5695 | 1962 | 0 | 68
39031.5716 | 2431 | 0 | 68
68
39031.5417 | 0 | 0 | 69
39031.5438 | 0 | 0 | 69
39031.5459 | 0 | 0 | 69
39031.5481 | 0 | 0 | 69
39031.5502 | 0 | 0 | 69
39031.5524 | 0 | 0 | 69
39031.5545 | 0 | 0 | 69
39031.5566 | 0 | 0 | 69
39031.5588 | 0 | 0 | 69
39031.5609 | 1889 | 0 | 69
39031.5631 | 2181 | 0 | 69
39031.5652 | 2184 | 0 | 69
39031.5673 | 2072 | 0 | 69
39031.5695 | 2248 | 0 | 69
39031.5716 | 2333 | 0 | 69
69
39031.5417 | 0 | 0 | 70
39031.5438 | 0 | 0 | 70
39031.546 | 0 | 0 | 70
39031.5481 | 0 | 0 | 70
39031.5502 | 2181 | 0 | 70
39031.5524 | 2212 | 4 | 70
39031.5545 | 2018 | 0 | 70
39031.5567 | 2213 | 0 | 70
39031.5588 | 2541 | 0 | 70
39031.5609 | 2566 | 0 | 70
39031.5631 | 2129 | 0 | 70
39031.5652 | 2602 | 0 | 70
39031.5673 | 2568 | 0 | 70
39031.5695 | 2275 | 0 | 70
39031.5716 | 2081 | 0 | 70
70
39031.5417 | 0 | 0 | 71
39031.5438 | 0 | 0 | 71
39031.546 | 0 | 0 | 71
39031.5481 | 0 | 0 | 71
39031.5503 | 0 | 0 | 71
39031.5524 | 0 | 0 | 71
39031.5545 | 0 | 0 | 71
39031.5567 | 0 | 0 | 71
39031.5588 | 0 | 0 | 71
39031.561 | 1823 | 0 | 71
39031.5631 | 2224 | 0 | 71
39031.5652 | 2570 | 0 | 71
39031.5674 | 2283 | 0 | 71
39031.5695 | 2551 | 0 | 71
39031.5716 | 2482 | 0 | 71
71
39031.5417 | 0 | 0 | 72
39031.5439 | 0 | 0 | 72
39031.546 | 0 | 0 | 72
39031.5481 | 0 | 0 | 72
39031.5503 | 0 | 0 | 72
39031.5524 | 0 | 1 | 72
39031.5546 | 2556 | 0 | 72
39031.5567 | 2431 | 0 | 72
39031.5588 | 2587 | 0 | 72
39031.561 | 2157 | 0 | 72
39031.5631 | 2148 | 0 | 72
39031.5652 | 2163 | 0 | 72
39031.5674 | 1996 | 0 | 72
39031.5695 | 2053 | 0 | 72
39031.5717 | 1988 | 0 | 72
72
39031.5417 | 0 | 0 | 73
39031.5439 | 0 | 0 | 73
39031.546 | 0 | 0 | 73
39031.5482 | 0 | 0 | 73
39031.5503 | 0 | 0 | 73
39031.5524 | 0 | 0 | 73
39031.5546 | 0 | 0 | 73
39031.5567 | 0 | 0 | 73
39031.5588 | 0 | 0 | 73
39031.561 | 1906 | 0 | 73
39031.5631 | 2062 | 0 | 73
39031.5653 | 2169 | 0 | 73
39031.5674 | 2188 | 0 | 73
39031.5695 | 2507 | 0 | 73
39031.5717 | 2284 | 0 | 73
73
39031.5418 | 0 | 0 | 74
39031.5439 | 0 | 0 | 74
39031.546 | 0 | 0 | 74
39031.5482 | 0 | 0 | 74
39031.5503 | 0 | 0 | 74
39031.5525 | 0 | 0 | 74
39031.5546 | 0 | 0 | 74
39031.5567 | 2189 | 0 | 74
39031.5589 | 2022 | 0 | 74
39031.561 | 1974 | 0 | 74
39031.5631 | 2519 | 0 | 74
39031.5653 | 2046 | 0 | 74
39031.5674 | 2577 | 0 | 74
39031.5696 | 2232 | 0 | 74
39031.5717 | 2085 | 0 | 74
74
39031.5418 | 0 | 0 | 75
39031.5439 | 0 | 0 | 75
39031.5461 | 0 | 0 | 75
39031.5482 | 0 | 0 | 75
39031.5503 | 0 | 0 | 75
39031.5525 | 0 | 0 | 75
39031.5546 | 0 | 0 | 75
39031.5567 | 0 | 0 | 75
39031.5589 | 1 | 0 | 75
39031.561 | 2294 | 0 | 75
39031.5632 | 1988 | 0 | 75
39031.5653 | 2578 | 0 | 75
39031.5674 | 2026 | 0 | 75
39031.5696 | 2083 | 0 | 75
39031.5717 | 2237 | 0 | 75
75
39031.5418 | 0 | 0 | 76
39031.5439 | 0 | 0 | 76
39031.5461 | 0 | 0 | 76
39031.5482 | 0 | 0 | 76
39031.5503 | 0 | 0 | 76
39031.5525 | 0 | 0 | 76
39031.5546 | 0 | 0 | 76
39031.5568 | 2208 | 0 | 76
39031.5589 | 2212 | 0 | 76
39031.561 | 2587 | 0 | 76
39031.5632 | 2538 | 0 | 76
39031.5653 | 2311 | 0 | 76
39031.5675 | 2510 | 0 | 76
39031.5696 | 2480 | 0 | 76
39031.5717 | 2573 | 0 | 76
76
39031.5418 | 0 | 0 | 77
39031.5439 | 0 | 0 | 77
39031.5461 | 0 | 0 | 77
39031.5482 | 0 | 0 | 77
39031.5504 | 0 | 0 | 77
39031.5525 | 0 | 0 | 77
39031.5546 | 0 | 0 | 77
39031.5568 | 0 | 0 | 77
39031.5589 | 86 | 0 | 77
39031.5611 | 1941 | 3 | 77
39031.5632 | 2092 | 0 | 77
39031.5653 | 2013 | 0 | 77
39031.5675 | 2260 | 0 | 77
39031.5696 | 1975 | 1 | 77
39031.5717 | 2428 | 3 | 77
77
39031.5418 | 0 | 0 | 78
39031.544 | 0 | 0 | 78
39031.5461 | 0 | 0 | 78
39031.5482 | 0 | 0 | 78
39031.5504 | 0 | 0 | 78
39031.5525 | 0 | 0 | 78
39031.5547 | 0 | 0 | 78
39031.5568 | 0 | 0 | 78
39031.5589 | 0 | 0 | 78
39031.5611 | 1999 | 1 | 78
39031.5632 | 2100 | 0 | 78
39031.5653 | 2255 | 0 | 78
39031.5675 | 2560 | 0 | 78
39031.5696 | 2537 | 1 | 78
39031.5718 | 2485 | 3 | 78
78
39031.5418 | 0 | 0 | 79
39031.544 | 0 | 0 | 79
39031.5461 | 0 | 0 | 79
39031.5483 | 0 | 0 | 79
39031.5504 | 0 | 0 | 79
39031.5525 | 0 | 0 | 79
39031.5547 | 0 | 0 | 79
39031.5568 | 0 | 0 | 79
39031.5589 | 6 | 0 | 79
39031.5611 | 2146 | 0 | 79
39031.5632 | 2234 | 0 | 79
39031.5654 | 2264 | 0 | 79
39031.5675 | 2445 | 0 | 79
39031.5696 | 2513 | 0 | 79
39031.5718 | 1928 | 1 | 79
79
39031.5419 | 0 | 0 | 80
39031.544 | 0 | 0 | 80
39031.5461 | 0 | 0 | 80
39031.5483 | 0 | 0 | 80
39031.5504 | 0 | 0 | 80
39031.5525 | 0 | 0 | 80
39031.5547 | 140 | 0 | 80
39031.5568 | 1941 | 0 | 80
39031.559 | 2065 | 0 | 80
39031.5611 | 2568 | 0 | 80
39031.5632 | 2470 | 0 | 80
39031.5654 | 2209 | 0 | 80
39031.5675 | 2019 | 0 | 80
39031.5697 | 1953 | 0 | 80
39031.5718 | 2078 | 0 | 80
80
39031.5419 | 0 | 0 | 81
39031.544 | 0 | 0 | 81
39031.5461 | 0 | 0 | 81
39031.5483 | 0 | 0 | 81
39031.5504 | 0 | 0 | 81
39031.5526 | 0 | 0 | 81
39031.5547 | 0 | 0 | 81
39031.5568 | 0 | 0 | 81
39031.559 | 797 | 0 | 81
39031.5611 | 1894 | 0 | 81
39031.5633 | 2254 | 0 | 81
39031.5654 | 2020 | 0 | 81
39031.5675 | 2580 | 0 | 81
39031.5697 | 2193 | 0 | 81
39031.5718 | 2422 | 2 | 81
81
39031.5419 | 0 | 0 | 82
39031.544 | 0 | 0 | 82
39031.5462 | 0 | 0 | 82
39031.5483 | 0 | 0 | 82
39031.5504 | 0 | 0 | 82
39031.5526 | 0 | 0 | 82
39031.5547 | 79 | 0 | 82
39031.5569 | 1933 | 0 | 82
39031.559 | 2229 | 0 | 82
39031.5611 | 2327 | 0 | 82
39031.5633 | 2475 | 0 | 82
39031.5654 | 2456 | 0 | 82
39031.5675 | 2145 | 0 | 82
39031.5697 | 2249 | 0 | 82
39031.5718 | 1925 | 0 | 82
82
39031.5419 | 0 | 0 | 83
39031.544 | 0 | 0 | 83
39031.5462 | 0 | 0 | 83
39031.5483 | 0 | 0 | 83
39031.5505 | 0 | 0 | 83
39031.5526 | 0 | 0 | 83
39031.5547 | 0 | 0 | 83
39031.5569 | 0 | 0 | 83
39031.559 | 1755 | 0 | 83
39031.5611 | 1982 | 0 | 83
39031.5633 | 2268 | 0 | 83
39031.5654 | 1990 | 0 | 83
39031.5676 | 2589 | 0 | 83
39031.5697 | 2400 | 0 | 83
39031.5718 | 1969 | 0 | 83
83
39031.5419 | 0 | 0 | 84
39031.5441 | 0 | 0 | 84
39031.5462 | 0 | 0 | 84
39031.5483 | 0 | 0 | 84
39031.5505 | 1642 | 4 | 84
39031.5526 | 1838 | 1 | 84
39031.5547 | 2532 | 0 | 84
39031.5569 | 2445 | 0 | 84
39031.559 | 2132 | 0 | 84
39031.5612 | 2118 | 0 | 84
39031.5633 | 2615 | 0 | 84
39031.5654 | 2160 | 0 | 84
39031.5676 | 2486 | 0 | 84
39031.5697 | 2587 | 0 | 84
39031.5719 | 2553 | 0 | 84
84
39031.5419 | 0 | 0 | 85
39031.5441 | 0 | 0 | 85
39031.5462 | 0 | 0 | 85
39031.5483 | 0 | 0 | 85
39031.5505 | 0 | 0 | 85
39031.5526 | 0 | 0 | 85
39031.5548 | 0 | 0 | 85
39031.5569 | 0 | 0 | 85
39031.559 | 1572 | 0 | 85
39031.5612 | 1865 | 0 | 85
39031.5633 | 2474 | 0 | 85
39031.5655 | 1993 | 0 | 85
39031.5676 | 2046 | 0 | 85
39031.5697 | 2349 | 0 | 85
39031.5719 | 2428 | 0 | 85
85
39031.542 | 0 | 0 | 86
39031.5441 | 0 | 0 | 86
39031.5462 | 0 | 0 | 86
39031.5484 | 0 | 0 | 86
39031.5505 | 0 | 0 | 86
39031.5526 | 0 | 0 | 86
39031.5548 | 2433 | 0 | 86
39031.5569 | 2178 | 0 | 86
39031.5591 | 2116 | 0 | 86
39031.5612 | 2443 | 0 | 86
39031.5633 | 2587 | 0 | 86
39031.5655 | 2000 | 0 | 86
39031.5676 | 2197 | 0 | 86
39031.5698 | 2056 | 0 | 86
39031.5719 | 2153 | 0 | 86
86
39031.542 | 0 | 0 | 87
39031.5441 | 0 | 1 | 87
39031.5462 | 0 | 0 | 87
39031.5484 | 0 | 0 | 87
39031.5505 | 0 | 0 | 87
39031.5527 | 0 | 0 | 87
39031.5548 | 0 | 0 | 87
39031.5569 | 0 | 0 | 87
39031.5591 | 1933 | 0 | 87
39031.5612 | 2323 | 0 | 87
39031.5634 | 2501 | 0 | 87
39031.5655 | 2501 | 0 | 87
39031.5676 | 2170 | 0 | 87
39031.5698 | 2360 | 0 | 87
39031.5719 | 1998 | 0 | 87
87
39031.542 | 0 | 0 | 88
39031.5441 | 0 | 0 | 88
39031.5463 | 0 | 0 | 88
39031.5484 | 0 | 0 | 88
39031.5505 | 0 | 0 | 88
39031.5527 | 0 | 0 | 88
39031.5548 | 0 | 0 | 88
39031.557 | 2422 | 0 | 88
39031.5591 | 2026 | 0 | 88
39031.5612 | 2520 | 0 | 88
39031.5634 | 2131 | 0 | 88
39031.5655 | 2311 | 0 | 88
39031.5677 | 2448 | 0 | 88
39031.5698 | 2521 | 0 | 88
39031.5719 | 2257 | 0 | 88
88
39031.542 | 0 | 0 | 89
39031.5441 | 0 | 0 | 89
39031.5463 | 0 | 0 | 89
39031.5484 | 0 | 0 | 89
39031.5506 | 0 | 0 | 89
39031.5527 | 0 | 0 | 89
39031.5548 | 0 | 0 | 89
39031.557 | 0 | 0 | 89
39031.5591 | 1735 | 0 | 89
39031.5612 | 2044 | 0 | 89
39031.5634 | 2244 | 0 | 89
39031.5655 | 2592 | 0 | 89
39031.5677 | 2482 | 0 | 89
39031.5698 | 2513 | 0 | 89
39031.5719 | 1936 | 0 | 89
89
39031.542 | 0 | 0 | 90
39031.5442 | 0 | 0 | 90
39031.5463 | 0 | 0 | 90
39031.5484 | 0 | 0 | 90
39031.5506 | 0 | 0 | 90
39031.5527 | 0 | 0 | 90
39031.5548 | 0 | 0 | 90
39031.557 | 2506 | 0 | 90
39031.5591 | 2010 | 0 | 90
39031.5613 | 2579 | 0 | 90
39031.5634 | 2031 | 0 | 90
39031.5655 | 2171 | 0 | 90
39031.5677 | 2039 | 0 | 90
39031.5698 | 2064 | 0 | 90
39031.572 | 2017 | 0 | 90
90
39031.542 | 0 | 0 | 91
39031.5442 | 0 | 0 | 91
39031.5463 | 0 | 0 | 91
39031.5484 | 0 | 0 | 91
39031.5506 | 0 | 0 | 91
39031.5527 | 0 | 0 | 91
39031.5549 | 0 | 0 | 91
39031.557 | 0 | 0 | 91
39031.5591 | 0 | 0 | 91
39031.5613 | 1827 | 0 | 91
39031.5634 | 2443 | 0 | 91
39031.5656 | 2333 | 0 | 91
39031.5677 | 2140 | 0 | 91
39031.5698 | 2439 | 0 | 91
39031.572 | 1960 | 0 | 91
91
39031.542 | 0 | 0 | 92
39031.5442 | 0 | 0 | 92
39031.5463 | 0 | 0 | 92
39031.5485 | 0 | 0 | 92
39031.5506 | 0 | 0 | 92
39031.5527 | 0 | 0 | 92
39031.5549 | 97 | 0 | 92
39031.557 | 2311 | 0 | 92
39031.5592 | 1970 | 0 | 92
39031.5613 | 2376 | 0 | 92
39031.5634 | 1982 | 0 | 92
39031.5656 | 2520 | 0 | 92
39031.5677 | 2476 | 0 | 92
39031.5698 | 2041 | 0 | 92
39031.572 | 2036 | 0 | 92
92
39031.5421 | 0 | 0 | 93
39031.5442 | 0 | 0 | 93
39031.5463 | 0 | 0 | 93
39031.5485 | 0 | 0 | 93
39031.5506 | 0 | 0 | 93
39031.5528 | 0 | 0 | 93
39031.5549 | 0 | 0 | 93
39031.557 | 0 | 0 | 93
39031.5592 | 941 | 0 | 93
39031.5613 | 1669 | 0 | 93
39031.5634 | 2038 | 0 | 93
39031.5656 | 2179 | 0 | 93
39031.5677 | 1980 | 0 | 93
39031.5699 | 2389 | 2 | 93
39031.572 | 2481 | 2 | 93
93
39031.5421 | 0 | 0 | 94
39031.5442 | 0 | 0 | 94
39031.5464 | 0 | 0 | 94
39031.5485 | 0 | 0 | 94
39031.5506 | 0 | 0 | 94
39031.5528 | 0 | 0 | 94
39031.5549 | 311 | 0 | 94
39031.557 | 2483 | 0 | 94
39031.5592 | 2092 | 0 | 94
39031.5613 | 2520 | 0 | 94
39031.5635 | 2187 | 0 | 94
39031.5656 | 2037 | 0 | 94
39031.5677 | 2405 | 0 | 94
39031.5699 | 2557 | 0 | 94
39031.572 | 2369 | 0 | 94
94
39031.5421 | 0 | 0 | 95
39031.5442 | 0 | 0 | 95
39031.5464 | 0 | 0 | 95
39031.5485 | 0 | 0 | 95
39031.5506 | 0 | 0 | 95
39031.5528 | 0 | 0 | 95
39031.5549 | 0 | 0 | 95
39031.5571 | 0 | 0 | 95
39031.5592 | 229 | 0 | 95
39031.5613 | 1912 | 0 | 95
39031.5635 | 1979 | 1 | 95
39031.5656 | 2464 | 0 | 95
39031.5678 | 2036 | 0 | 95
39031.5699 | 2116 | 0 | 95
39031.572 | 2065 | 0 | 95
95
39031.5421 | 1 | 0 | 96
39031.5442 | 0 | 0 | 96
39031.5464 | 0 | 0 | 96
39031.5485 | 0 | 0 | 96
39031.5507 | 1912 | 3 | 96
39031.5528 | 2001 | 1 | 96
39031.5549 | 2530 | 0 | 96
39031.5571 | 2578 | 0 | 96
39031.5592 | 1980 | 0 | 96
39031.5614 | 2368 | 0 | 96
39031.5635 | 2044 | 0 | 96
39031.5656 | 2546 | 0 | 96
39031.5678 | 2060 | 0 | 96
39031.5699 | 2066 | 1 | 96
39031.572 | 2520 | 0 | 96
96
39031.5421 | 0 | 0 | 97
39031.5443 | 0 | 0 | 97
39031.5464 | 0 | 0 | 97
39031.5485 | 0 | 0 | 97
39031.5507 | 0 | 0 | 97
39031.5528 | 0 | 0 | 97
39031.555 | 0 | 0 | 97
39031.5571 | 0 | 0 | 97
39031.5592 | 131 | 0 | 97
39031.5614 | 2010 | 0 | 97
39031.5635 | 2221 | 0 | 97
39031.5656 | 2573 | 0 | 97
39031.5678 | 2270 | 0 | 97
39031.5699 | 2333 | 0 | 97
39031.5721 | 2448 | 0 | 97
97
39031.5421 | 0 | 0 | 98
39031.5443 | 0 | 0 | 98
39031.5464 | 0 | 0 | 98
39031.5486 | 0 | 0 | 98
39031.5507 | 0 | 0 | 98
39031.5528 | 0 | 0 | 98
39031.555 | 2420 | 0 | 98
39031.5571 | 2080 | 0 | 98
39031.5592 | 2262 | 0 | 98
39031.5614 | 1970 | 0 | 98
39031.5635 | 2131 | 0 | 98
39031.5657 | 2424 | 0 | 98
39031.5678 | 2003 | 0 | 98
39031.5699 | 2226 | 0 | 98
39031.5721 | 2123 | 0 | 98
98
39031.5422 | 0 | 0 | 99
39031.5443 | 0 | 0 | 99
39031.5464 | 0 | 1 | 99
39031.5486 | 0 | 0 | 99
39031.5507 | 0 | 0 | 99
39031.5529 | 0 | 0 | 99
39031.555 | 0 | 0 | 99
39031.5571 | 0 | 0 | 99
39031.5593 | 513 | 0 | 99
39031.5614 | 1783 | 0 | 99
39031.5635 | 2123 | 0 | 99
39031.5657 | 2099 | 0 | 99
39031.5678 | 2574 | 0 | 99
39031.57 | 2053 | 0 | 99
39031.5721 | 2470 | 0 | 99
99
39031.5422 | 0 | 0 | 100
39031.5443 | 0 | 0 | 100
39031.5465 | 0 | 0 | 100
39031.5486 | 0 | 0 | 100
39031.5507 | 0 | 0 | 100
39031.5529 | 0 | 0 | 100
39031.555 | 0 | 0 | 100
39031.5571 | 2303 | 0 | 100
39031.5593 | 2235 | 0 | 100
39031.5614 | 2604 | 0 | 100
39031.5636 | 2442 | 0 | 100
39031.5657 | 2412 | 0 | 100
39031.5678 | 2084 | 0 | 100
39031.57 | 2144 | 0 | 100
39031.5721 | 2021 | 0 | 100
100
39031.5422 | 0 | 0 | 101
39031.5443 | 0 | 0 | 101
39031.5465 | 0 | 0 | 101
39031.5486 | 0 | 0 | 101
39031.5508 | 0 | 0 | 101
39031.5529 | 0 | 0 | 101
39031.555 | 0 | 0 | 101
39031.5572 | 0 | 0 | 101
39031.5593 | 595 | 0 | 101
39031.5614 | 2068 | 0 | 101
39031.5636 | 2269 | 0 | 101
39031.5657 | 2032 | 0 | 101
39031.5679 | 2484 | 0 | 101
39031.57 | 2262 | 0 | 101
39031.5721 | 2095 | 0 | 101
101
39031.5422 | 0 | 0 | 102
39031.5444 | 0 | 0 | 102
39031.5465 | 0 | 0 | 102
39031.5486 | 0 | 0 | 102
39031.5508 | 0 | 0 | 102
39031.5529 | 0 | 0 | 102
39031.555 | 0 | 0 | 102
39031.5572 | 2480 | 0 | 102
39031.5593 | 2361 | 0 | 102
39031.5615 | 2042 | 0 | 102
39031.5636 | 2166 | 0 | 102
39031.5657 | 2421 | 0 | 102
39031.5679 | 2072 | 0 | 102
39031.57 | 2092 | 2 | 102
39031.5722 | 2504 | 0 | 102
102
39031.5422 | 0 | 0 | 103
39031.5444 | 0 | 0 | 103
39031.5465 | 0 | 0 | 103
39031.5486 | 0 | 0 | 103
39031.5508 | 0 | 0 | 103
39031.5529 | 0 | 0 | 103
39031.5551 | 766 | 445 | 103
39031.5572 | 2123 | 4 | 103
39031.5593 | 2071 | 1 | 103
39031.5615 | 2332 | 0 | 103
39031.5636 | 2473 | 0 | 103
39031.5658 | 2198 | 0 | 103
39031.5679 | 2096 | 0 | 103
39031.57 | 2224 | 1 | 103
39031.5722 | 2489 | 5 | 103
103
39031.5422 | 0 | 0 | 104
39031.5444 | 0 | 0 | 104
39031.5465 | 0 | 0 | 104
39031.5487 | 0 | 0 | 104
39031.5508 | 0 | 0 | 104
39031.5529 | 0 | 0 | 104
39031.5551 | 966 | 712 | 104
39031.5572 | 2035 | 2 | 104
39031.5594 | 2434 | 0 | 104
39031.5615 | 2112 | 0 | 104
39031.5636 | 2043 | 0 | 104
39031.5658 | 2149 | 0 | 104
39031.5679 | 2160 | 0 | 104
39031.57 | 2548 | 1 | 104
39031.5722 | 1942 | 9 | 104
104
39031.5423 | 0 | 0 | 105
39031.5444 | 0 | 0 | 105
39031.5465 | 0 | 0 | 105
39031.5487 | 0 | 0 | 105
39031.5508 | 0 | 0 | 105
39031.553 | 0 | 0 | 105
39031.5551 | 763 | 0 | 105
39031.5572 | 2424 | 0 | 105
39031.5594 | 2432 | 0 | 105
39031.5615 | 2437 | 0 | 105
39031.5636 | 2112 | 0 | 105
39031.5658 | 2061 | 0 | 105
39031.5679 | 2219 | 0 | 105
39031.5701 | 2093 | 0 | 105
39031.5722 | 2193 | 0 | 105
105
39031.5423 | 0 | 0 | 106
39031.5444 | 0 | 0 | 106
39031.5466 | 0 | 0 | 106
39031.5487 | 0 | 0 | 106
39031.5508 | 2017 | 1 | 106
39031.553 | 2320 | 2 | 106
39031.5551 | 2329 | 0 | 106
39031.5572 | 2005 | 0 | 106
39031.5594 | 2328 | 0 | 106
39031.5615 | 2216 | 0 | 106
39031.5637 | 2043 | 0 | 106
39031.5658 | 2260 | 0 | 106
39031.5679 | 2044 | 0 | 106
39031.5701 | 2040 | 0 | 106
39031.5722 | 2042 | 0 | 106
106
39031.5423 | 0 | 0 | 107
39031.5444 | 0 | 0 | 107
39031.5466 | 0 | 0 | 107
39031.5487 | 0 | 0 | 107
39031.5508 | 0 | 0 | 107
39031.553 | 0 | 0 | 107
39031.5551 | 265 | 0 | 107
39031.5573 | 2026 | 0 | 107
39031.5594 | 2387 | 0 | 107
39031.5615 | 2565 | 0 | 107
39031.5637 | 2543 | 0 | 107
39031.5658 | 2206 | 0 | 107
39031.568 | 2231 | 0 | 107
39031.5701 | 2305 | 0 | 107
39031.5722 | 2075 | 0 | 107
107
39031.5423 | 0 | 0 | 108
39031.5444 | 0 | 0 | 108
39031.5466 | 0 | 0 | 108
39031.5487 | 0 | 0 | 108
39031.5509 | 0 | 0 | 108
39031.553 | 485 | 0 | 108
39031.5551 | 2436 | 0 | 108
39031.5573 | 2200 | 0 | 108
39031.5594 | 2286 | 0 | 108
39031.5616 | 2267 | 0 | 108
39031.5637 | 2084 | 0 | 108
39031.5658 | 2423 | 0 | 108
39031.568 | 2295 | 0 | 108
39031.5701 | 2554 | 2 | 108
39031.5722 | 2589 | 1 | 108
108
39031.5423 | 0 | 0 | 109
39031.5445 | 0 | 0 | 109
39031.5466 | 0 | 0 | 109
39031.5487 | 0 | 0 | 109
39031.5509 | 0 | 0 | 109
39031.553 | 0 | 0 | 109
39031.5552 | 1814 | 0 | 109
39031.5573 | 2206 | 0 | 109
39031.5594 | 2419 | 0 | 109
39031.5616 | 2075 | 0 | 109
39031.5637 | 2254 | 0 | 109
39031.5658 | 2217 | 0 | 109
39031.568 | 2597 | 0 | 109
39031.5701 | 2556 | 0 | 109
39031.5723 | 2445 | 0 | 109
109
39031.5423 | 0 | 0 | 110
39031.5445 | 0 | 0 | 110
39031.5466 | 0 | 0 | 110
39031.5488 | 0 | 0 | 110
39031.5509 | 0 | 0 | 110
39031.553 | 0 | 0 | 110
39031.5552 | 0 | 0 | 110
39031.5573 | 2502 | 0 | 110
39031.5594 | 2553 | 0 | 110
39031.5616 | 2396 | 0 | 110
39031.5637 | 2076 | 0 | 110
39031.5659 | 2499 | 0 | 110
39031.568 | 2143 | 0 | 110
39031.5701 | 1995 | 1 | 110
39031.5723 | 2233 | 1 | 110
110
39031.5424 | 0 | 0 | 111
39031.5445 | 0 | 0 | 111
39031.5466 | 0 | 0 | 111
39031.5488 | 0 | 0 | 111
39031.5509 | 0 | 0 | 111
39031.553 | 0 | 0 | 111
39031.5552 | 82 | 0 | 111
39031.5573 | 2438 | 0 | 111
39031.5595 | 2245 | 0 | 111
39031.5616 | 2088 | 0 | 111
39031.5637 | 2554 | 0 | 111
39031.5659 | 2549 | 0 | 111
39031.568 | 2563 | 0 | 111
39031.5702 | 1971 | 0 | 111
39031.5723 | 2194 | 0 | 111
111
39031.5424 | 0 | 0 | 112
39031.5445 | 0 | 0 | 112
39031.5467 | 0 | 0 | 112
39031.5488 | 0 | 0 | 112
39031.5509 | 0 | 0 | 112
39031.5531 | 0 | 0 | 112
39031.5552 | 0 | 0 | 112
39031.5573 | 2466 | 0 | 112
39031.5595 | 1982 | 0 | 112
39031.5616 | 2582 | 0 | 112
39031.5638 | 2130 | 0 | 112
39031.5659 | 2373 | 0 | 112
39031.568 | 2409 | 0 | 112
39031.5702 | 1978 | 1 | 112
39031.5723 | 2524 | 1 | 112
112
39031.5424 | 0 | 0 | 113
39031.5445 | 0 | 0 | 113
39031.5467 | 0 | 0 | 113
39031.5488 | 0 | 0 | 113
39031.5509 | 0 | 0 | 113
39031.5531 | 0 | 0 | 113
39031.5552 | 1 | 0 | 113
39031.5574 | 2490 | 0 | 113
39031.5595 | 2274 | 0 | 113
39031.5616 | 2137 | 0 | 113
39031.5638 | 2170 | 0 | 113
39031.5659 | 2072 | 0 | 113
39031.5681 | 2008 | 0 | 113
39031.5702 | 2441 | 0 | 113
39031.5723 | 1917 | 0 | 113
113
39031.5424 | 0 | 0 | 114
39031.5445 | 0 | 0 | 114
39031.5467 | 0 | 0 | 114
39031.5488 | 0 | 0 | 114
39031.551 | 1633 | 1 | 114
39031.5531 | 1907 | 2 | 114
39031.5552 | 2082 | 0 | 114
39031.5574 | 2580 | 0 | 114
39031.5595 | 2445 | 0 | 114
39031.5617 | 2008 | 0 | 114
39031.5638 | 2326 | 0 | 114
39031.5659 | 2132 | 0 | 114
39031.5681 | 2447 | 0 | 114
39031.5702 | 2203 | 0 | 114
39031.5723 | 2016 | 1 | 114
114
39031.5424 | 0 | 0 | 115
39031.5446 | 0 | 0 | 115
39031.5467 | 0 | 0 | 115
39031.5488 | 0 | 0 | 115
39031.551 | 0 | 0 | 115
39031.5531 | 0 | 0 | 115
39031.5553 | 1 | 0 | 115
39031.5574 | 2324 | 0 | 115
39031.5595 | 2414 | 0 | 115
39031.5617 | 1979 | 0 | 115
39031.5638 | 2395 | 0 | 115
39031.5659 | 2569 | 0 | 115
39031.5681 | 2534 | 0 | 115
39031.5702 | 2562 | 0 | 115
39031.5724 | 2096 | 0 | 115
115
39031.5424 | 0 | 0 | 116
39031.5446 | 0 | 0 | 116
39031.5467 | 0 | 0 | 116
39031.5489 | 0 | 0 | 116
39031.551 | 0 | 0 | 116
39031.5531 | 1729 | 1 | 116
39031.5553 | 2238 | 0 | 116
39031.5574 | 2086 | 0 | 116
39031.5595 | 2152 | 0 | 116
39031.5617 | 2260 | 0 | 116
39031.5638 | 2530 | 0 | 116
39031.566 | 2171 | 0 | 116
39031.5681 | 2224 | 0 | 116
39031.5702 | 2011 | 0 | 116
39031.5724 | 2544 | 0 | 116
116
39031.5425 | 0 | 0 | 117
39031.5446 | 0 | 0 | 117
39031.5467 | 0 | 0 | 117
39031.5489 | 0 | 0 | 117
39031.551 | 0 | 0 | 117
39031.5531 | 0 | 0 | 117
39031.5553 | 76 | 0 | 117
39031.5574 | 2345 | 0 | 117
39031.5596 | 2527 | 0 | 117
39031.5617 | 1991 | 0 | 117
39031.5638 | 2050 | 0 | 117
39031.566 | 2592 | 0 | 117
39031.5681 | 2305 | 0 | 117
39031.5703 | 1964 | 0 | 117
39031.5724 | 2253 | 0 | 117
117
39031.5425 | 0 | 0 | 118
39031.5446 | 0 | 0 | 118
39031.5467 | 0 | 0 | 118
39031.5489 | 0 | 0 | 118
39031.551 | 0 | 0 | 118
39031.5532 | 0 | 0 | 118
39031.5553 | 0 | 0 | 118
39031.5574 | 2306 | 0 | 118
39031.5596 | 2254 | 0 | 118
39031.5617 | 2005 | 0 | 118
39031.5639 | 2049 | 0 | 118
39031.566 | 2067 | 0 | 118
39031.5681 | 2292 | 0 | 118
39031.5703 | 2220 | 0 | 118
39031.5724 | 2580 | 0 | 118
118
39031.5425 | 0 | 0 | 119
39031.5446 | 0 | 0 | 119
39031.5468 | 0 | 0 | 119
39031.5489 | 0 | 0 | 119
39031.551 | 0 | 0 | 119
39031.5532 | 0 | 0 | 119
39031.5553 | 106 | 0 | 119
39031.5575 | 2503 | 0 | 119
39031.5596 | 1964 | 0 | 119
39031.5617 | 2361 | 0 | 119
39031.5639 | 1992 | 0 | 119
39031.566 | 2504 | 0 | 119
39031.5681 | 2286 | 0 | 119
39031.5703 | 2331 | 0 | 119
39031.5724 | 1857 | 0 | 119
119
39031.5425 | 0 | 0 | 120
39031.5446 | 0 | 0 | 120
39031.5468 | 0 | 0 | 120
39031.5489 | 0 | 0 | 120
39031.5511 | 0 | 0 | 120
39031.5532 | 0 | 0 | 120
39031.5553 | 0 | 0 | 120
39031.5575 | 2512 | 0 | 120
39031.5596 | 2204 | 0 | 120
39031.5617 | 2147 | 0 | 120
39031.5639 | 2040 | 0 | 120
39031.566 | 1993 | 0 | 120
39031.5682 | 2193 | 0 | 120
39031.5703 | 2205 | 0 | 120
39031.5724 | 2187 | 0 | 120
120
39031.5425 | 0 | 0 | 121
39031.5447 | 0 | 0 | 121
39031.5468 | 0 | 0 | 121
39031.5489 | 0 | 0 | 121
39031.5511 | 2 | 0 | 121
39031.5532 | 2200 | 473 | 121
39031.5553 | 2287 | 0 | 121
39031.5575 | 2198 | 0 | 121
39031.5596 | 2376 | 0 | 121
39031.5618 | 2010 | 0 | 121
39031.5639 | 2576 | 0 | 121
39031.566 | 2423 | 0 | 121
39031.5682 | 2138 | 0 | 121
39031.5703 | 2061 | 0 | 121
39031.5725 | 2528 | 0 | 121
121
39031.5425 | 0 | 0 | 122
39031.5447 | 0 | 0 | 122
39031.5468 | 0 | 0 | 122
39031.5489 | 0 | 0 | 122
39031.5511 | 0 | 0 | 122
39031.5532 | 2305 | 227 | 122
39031.5554 | 2107 | 0 | 122
39031.5575 | 2330 | 0 | 122
39031.5596 | 2397 | 0 | 122
39031.5618 | 2312 | 0 | 122
39031.5639 | 2604 | 0 | 122
39031.5661 | 2272 | 0 | 122
39031.5682 | 2367 | 0 | 122
39031.5703 | 2351 | 0 | 122
39031.5725 | 2488 | 0 | 122
122
39031.5425 | 0 | 0 | 123
39031.5447 | 0 | 0 | 123
39031.5468 | 0 | 0 | 123
39031.549 | 0 | 0 | 123
39031.5511 | 1712 | 3 | 123
39031.5532 | 2016 | 1 | 123
39031.5554 | 2508 | 0 | 123
39031.5575 | 2465 | 0 | 123
39031.5597 | 2015 | 0 | 123
39031.5618 | 2325 | 0 | 123
39031.5639 | 2331 | 0 | 123
39031.5661 | 2613 | 0 | 123
39031.5682 | 2258 | 0 | 123
39031.5703 | 2543 | 0 | 123
39031.5725 | 2075 | 0 | 123
123
39031.5426 | 0 | 0 | 124
39031.5447 | 0 | 0 | 124
39031.5468 | 0 | 0 | 124
39031.549 | 0 | 0 | 124
39031.5511 | 0 | 0 | 124
39031.5533 | 0 | 0 | 124
39031.5554 | 0 | 0 | 124
39031.5575 | 1974 | 0 | 124
39031.5597 | 2498 | 0 | 124
39031.5618 | 2061 | 0 | 124
39031.5639 | 2451 | 0 | 124
39031.5661 | 2351 | 0 | 124
39031.5682 | 2317 | 0 | 124
39031.5704 | 2036 | 0 | 124
39031.5725 | 2223 | 0 | 124
124
39031.5426 | 0 | 0 | 125
39031.5447 | 0 | 0 | 125
39031.5469 | 0 | 0 | 125
39031.549 | 0 | 0 | 125
39031.5511 | 1670 | 2 | 125
39031.5533 | 1965 | 0 | 125
39031.5554 | 1974 | 0 | 125
39031.5575 | 2249 | 0 | 125
39031.5597 | 2519 | 0 | 125
39031.5618 | 2041 | 0 | 125
39031.564 | 2014 | 0 | 125
39031.5661 | 1988 | 0 | 125
39031.5682 | 2610 | 0 | 125
39031.5704 | 2593 | 0 | 125
39031.5725 | 2555 | 0 | 125
125
39031.5426 | 0 | 0 | 126
39031.5447 | 0 | 0 | 126
39031.5469 | 0 | 0 | 126
39031.549 | 0 | 0 | 126
39031.5512 | 0 | 1 | 126
39031.5533 | 0 | 0 | 126
39031.5554 | 0 | 0 | 126
39031.5576 | 1940 | 0 | 126
39031.5597 | 2568 | 0 | 126
39031.5619 | 2597 | 0 | 126
39031.564 | 2082 | 0 | 126
39031.5661 | 2037 | 0 | 126
39031.5683 | 2060 | 0 | 126
39031.5704 | 2242 | 0 | 126
39031.5725 | 2561 | 0 | 126
126
39031.5426 | 0 | 0 | 127
39031.5448 | 0 | 0 | 127
39031.5469 | 0 | 0 | 127
39031.549 | 0 | 0 | 127
39031.5512 | 0 | 0 | 127
39031.5533 | 2325 | 1 | 127
39031.5554 | 1948 | 0 | 127
39031.5576 | 2453 | 0 | 127
39031.5597 | 2483 | 0 | 127
39031.5619 | 2302 | 0 | 127
39031.564 | 2527 | 0 | 127
39031.5661 | 2135 | 0 | 127
39031.5683 | 2508 | 0 | 127
39031.5704 | 2007 | 0 | 127
39031.5726 | 2060 | 0 | 127
127
39031.5426 | 0 | 0 | 128
39031.5448 | 0 | 0 | 128
39031.5469 | 0 | 1 | 128
39031.5491 | 0 | 0 | 128
39031.5512 | 0 | 0 | 128
39031.5533 | 0 | 0 | 128
39031.5555 | 1240 | 0 | 128
39031.5576 | 2477 | 0 | 128
39031.5597 | 2374 | 0 | 128
39031.5619 | 1979 | 0 | 128
39031.564 | 2354 | 0 | 128
39031.5662 | 2099 | 0 | 128
39031.5683 | 2241 | 0 | 128
39031.5704 | 2219 | 0 | 128
39031.5726 | 1980 | 0 | 128
128
39031.5427 | 0 | 0 | 129
39031.5448 | 0 | 0 | 129
39031.5469 | 0 | 0 | 129
39031.5491 | 0 | 0 | 129
39031.5512 | 0 | 0 | 129
39031.5533 | 2274 | 0 | 129
39031.5555 | 2401 | 0 | 129
39031.5576 | 2147 | 0 | 129
39031.5598 | 2039 | 0 | 129
39031.5619 | 2187 | 0 | 129
39031.564 | 2317 | 0 | 129
39031.5662 | 2033 | 0 | 129
39031.5683 | 2342 | 0 | 129
39031.5705 | 2062 | 1 | 129
39031.5726 | 2238 | 0 | 129
129
39031.5427 | 0 | 0 | 130
39031.5448 | 0 | 0 | 130
39031.5469 | 0 | 0 | 130
39031.5491 | 0 | 0 | 130
39031.5512 | 0 | 0 | 130
39031.5534 | 0 | 0 | 130
39031.5555 | 8 | 0 | 130
39031.5576 | 2242 | 0 | 130
39031.5598 | 2290 | 0 | 130
39031.5619 | 2261 | 0 | 130
39031.5641 | 2556 | 0 | 130
39031.5662 | 2348 | 0 | 130
39031.5683 | 2612 | 0 | 130
39031.5705 | 2005 | 0 | 130
39031.5726 | 2358 | 0 | 130
130
39031.5427 | 0 | 0 | 131
39031.5448 | 0 | 0 | 131
39031.547 | 0 | 0 | 131
39031.5491 | 0 | 0 | 131
39031.5512 | 0 | 0 | 131
39031.5534 | 1 | 2 | 131
39031.5555 | 1442 | 116 | 131
39031.5577 | 2235 | 1 | 131
39031.5598 | 2275 | 0 | 131
39031.5619 | 2220 | 0 | 131
39031.5641 | 2080 | 0 | 131
39031.5662 | 2530 | 0 | 131
39031.5683 | 2452 | 0 | 131
39031.5705 | 2327 | 0 | 131
39031.5726 | 2575 | 0 | 131
131
39031.5427 | 0 | 0 | 132
39031.5448 | 0 | 0 | 132
39031.547 | 0 | 0 | 132
39031.5491 | 0 | 0 | 132
39031.5512 | 0 | 0 | 132
39031.5534 | 736 | 676 | 132
39031.5555 | 333 | 398 | 132
39031.5577 | 2524 | 1 | 132
39031.5598 | 2098 | 0 | 132
39031.5619 | 2043 | 0 | 132
39031.5641 | 2442 | 0 | 132
39031.5662 | 2137 | 0 | 132
39031.5684 | 1985 | 0 | 132
39031.5705 | 2119 | 0 | 132
39031.5726 | 2306 | 0 | 132
132

## Temps
DAQ Time | Burner Time | Bundle center | Air above bundle | Air below bundle | Intra-bundle | TRAY C
0 | -219 | 15 | 14.7 | 15.2 | 14.8 | 16.2
1 | -218 | 15 | 14.7 | 15.2 | 14.8 | 16.2
2 | -217 | 15 | 14.7 | 15.2 | 14.8 | 16.2
3 | -216 | 15 | 14.7 | 15.2 | 14.8 | 16.2
4 | -215 | 15 | 14.7 | 15.2 | 14.8 | 16.2
5 | -214 | 15 | 14.7 | 15.2 | 14.8 | 16.2
6.1 | -212.9 | 15 | 14.7 | 15.2 | 14.8 | 16.2
7.1 | -211.9 | 15 | 14.7 | 15.1 | 14.8 | 16.2
8.1 | -210.9 | 15 | 14.7 | 15.2 | 14.8 | 16.2
9.1 | -209.9 | 15 | 14.7 | 15.2 | 14.8 | 16.2
10.1 | -208.9 | 15 | 14.7 | 15.2 | 14.8 | 16.2
11.1 | -207.9 | 15 | 14.7 | 15.2 | 14.8 | 16.2
12.1 | -206.9 | 15 | 14.7 | 15.2 | 14.8 | 16.2
13.1 | -205.9 | 15 | 14.7 | 15.2 | 14.8 | 16.2
14.1 | -204.9 | 15 | 14.7 | 15.2 | 14.8 | 16.2
15.1 | -203.9 | 15 | 14.7 | 15.2 | 14.8 | 16.2
16.1 | -202.9 | 15 | 14.7 | 15.2 | 14.8 | 16.2
17.1 | -201.9 | 15 | 14.7 | 15.2 | 14.8 | 16.2
18.1 | -200.9 | 15 | 14.7 | 15.2 | 14.8 | 16.2
19.1 | -199.9 | 15 | 14.7 | 15.2 | 14.8 | 16.2
20.1 | -198.9 | 15 | 14.7 | 15.2 | 14.8 | 16.2
21.1 | -197.9 | 15 | 14.7 | 15.2 | 14.8 | 16.2
22.1 | -196.9 | 15 | 14.7 | 15.2 | 14.8 | 16.2
23.1 | -195.9 | 15 | 14.7 | 15.2 | 14.8 | 16.2
24.1 | -194.9 | 15 | 14.7 | 15.2 | 14.8 | 16.2
25.1 | -193.9 | 15 | 14.7 | 15.2 | 14.8 | 16.2
26.1 | -192.9 | 15 | 14.7 | 15.2 | 14.8 | 16.2
27.1 | -191.9 | 15 | 14.7 | 15.2 | 14.8 | 16.2
28.1 | -190.9 | 15 | 14.7 | 15.2 | 14.8 | 16.2
29.1 | -189.9 | 15 | 14.7 | 15.2 | 14.8 | 16.2
30.1 | -188.9 | 15 | 14.7 | 15.2 | 14.8 | 16.2
31.1 | -187.9 | 15 | 14.7 | 15.2 | 14.8 | 16.2
32.1 | -186.9 | 15 | 14.7 | 15.2 | 14.8 | 16.2
33.1 | -185.9 | 15 | 14.7 | 15.2 | 14.8 | 16.2
34.1 | -184.9 | 15 | 14.7 | 15.2 | 14.8 | 16.2
35.1 | -183.9 | 15 | 14.7 | 15.2 | 14.8 | 16.2
36.1 | -182.9 | 15 | 14.7 | 15.2 | 14.8 | 16.2
37.1 | -181.9 | 15 | 14.7 | 15.2 | 14.8 | 16.2
38.1 | -180.9 | 15 | 14.7 | 15.2 | 14.8 | 16.2
39.1 | -179.9 | 15 | 14.7 | 15.2 | 14.8 | 16.2
40.1 | -178.9 | 15 | 14.7 | 15.2 | 14.8 | 16.2
41.1 | -177.9 | 15 | 14.7 | 15.2 | 14.8 | 16.2
42.1 | -176.9 | 15 | 14.7 | 15.2 | 14.8 | 16.2
43.1 | -175.9 | 15 | 14.7 | 15.2 | 14.8 | 16.2
44.1 | -174.9 | 15 | 14.7 | 15.2 | 14.8 | 16.2
45.1 | -173.9 | 15 | 14.8 | 15.2 | 14.8 | 16.2
46.2 | -172.8 | 15 | 14.7 | 15.2 | 14.8 | 16.2
47.2 | -171.8 | 15 | 14.8 | 15.2 | 14.8 | 16.2
48.2 | -170.8 | 15 | 14.7 | 15.2 | 14.8 | 16.2
49.2 | -169.8 | 15 | 14.7 | 15.2 | 14.8 | 16.2
50.2 | -168.8 | 15 | 14.8 | 15.2 | 14.8 | 16.2
51.2 | -167.8 | 15 | 14.7 | 15.2 | 14.8 | 16.2
52.2 | -166.8 | 15 | 14.8 | 15.2 | 14.8 | 16.2
53.2 | -165.8 | 15 | 14.8 | 15.2 | 14.8 | 16.2
54.2 | -164.8 | 15 | 14.8 | 15.2 | 14.8 | 16.2
55.2 | -163.8 | 15 | 14.8 | 15.2 | 14.8 | 16.2
56.2 | -162.8 | 15 | 14.8 | 15.2 | 14.8 | 16.2
57.2 | -161.8 | 15 | 14.7 | 15.2 | 14.8 | 16.2
58.2 | -160.8 | 15 | 14.8 | 15.2 | 14.8 | 16.2
59.2 | -159.8 | 15 | 14.8 | 15.2 | 14.8 | 16.2
60.2 | -158.8 | 15 | 14.7 | 15.2 | 14.8 | 16.2
61.2 | -157.8 | 15 | 14.8 | 15.2 | 14.8 | 16.2
62.2 | -156.8 | 15 | 14.7 | 15.2 | 14.8 | 16.2
63.2 | -155.8 | 15 | 14.8 | 15.2 | 14.8 | 16.2
64.2 | -154.8 | 15 | 14.8 | 15.2 | 14.8 | 16.2
65.2 | -153.8 | 15 | 14.8 | 15.2 | 14.8 | 16.2
66.2 | -152.8 | 15 | 14.7 | 15.2 | 14.8 | 16.2
67.2 | -151.8 | 15 | 14.8 | 15.2 | 14.8 | 16.2
68.2 | -150.8 | 15 | 14.8 | 15.2 | 14.8 | 16.2
69.2 | -149.8 | 15 | 14.8 | 15.2 | 14.8 | 16.2
70.2 | -148.8 | 15 | 14.8 | 15.2 | 14.8 | 16.2
71.2 | -147.8 | 15 | 14.8 | 15.2 | 14.8 | 16.2
72.2 | -146.8 | 15 | 14.8 | 15.2 | 14.8 | 16.2
73.2 | -145.8 | 15 | 14.8 | 15.2 | 14.8 | 16.2
74.2 | -144.8 | 15 | 14.8 | 15.2 | 14.8 | 16.2
75.2 | -143.8 | 15 | 14.8 | 15.2 | 14.8 | 16.2
76.2 | -142.8 | 15 | 14.8 | 15.2 | 14.8 | 16.2
77.2 | -141.8 | 15 | 14.8 | 15.2 | 14.8 | 16.2
78.2 | -140.8 | 15 | 14.8 | 15.2 | 14.8 | 16.2
79.2 | -139.8 | 15 | 14.8 | 15.2 | 14.8 | 16.2
80.2 | -138.8 | 15 | 14.8 | 15.2 | 14.8 | 16.2
81.2 | -137.8 | 15 | 14.8 | 15.2 | 14.8 | 16.2
82.2 | -136.8 | 15 | 14.8 | 15.2 | 14.8 | 16.2
83.3 | -135.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
84.3 | -134.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
85.3 | -133.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
86.3 | -132.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
87.3 | -131.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
88.3 | -130.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
89.3 | -129.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
90.3 | -128.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
91.3 | -127.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
92.3 | -126.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
93.3 | -125.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
94.3 | -124.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
95.3 | -123.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
96.3 | -122.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
97.3 | -121.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
98.3 | -120.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
99.3 | -119.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
100.3 | -118.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
101.3 | -117.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
102.3 | -116.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
103.3 | -115.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
104.3 | -114.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
105.3 | -113.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
106.3 | -112.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
107.3 | -111.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
108.3 | -110.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
109.3 | -109.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
110.3 | -108.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
111.3 | -107.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
112.3 | -106.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
113.3 | -105.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
114.3 | -104.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
115.3 | -103.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
116.3 | -102.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
117.3 | -101.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
118.3 | -100.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
119.3 | -99.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
120.3 | -98.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
121.3 | -97.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
122.3 | -96.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
123.3 | -95.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
124.3 | -94.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
125.3 | -93.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
126.3 | -92.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
127.3 | -91.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
128.3 | -90.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
129.3 | -89.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
130.3 | -88.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
131.3 | -87.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
132.3 | -86.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
133.3 | -85.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
134.3 | -84.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
135.3 | -83.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
136.3 | -82.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
137.3 | -81.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
138.3 | -80.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
139.3 | -79.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
140.3 | -78.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
141.3 | -77.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
142.3 | -76.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
143.3 | -75.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
144.3 | -74.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
145.3 | -73.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
146.3 | -72.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
147.3 | -71.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
148.3 | -70.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
149.3 | -69.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
150.3 | -68.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
151.3 | -67.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
152.3 | -66.7 | 15 | 14.8 | 15.3 | 14.8 | 16.2
153.3 | -65.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
154.3 | -64.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
155.3 | -63.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
156.3 | -62.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
157.3 | -61.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
158.3 | -60.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
159.3 | -59.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
160.3 | -58.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
161.3 | -57.7 | 15 | 14.8 | 15.3 | 14.8 | 16.2
162.3 | -56.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
163.3 | -55.7 | 15 | 14.8 | 15.3 | 14.8 | 16.2
164.3 | -54.7 | 15 | 14.8 | 15.3 | 14.8 | 16.2
165.3 | -53.7 | 15 | 14.8 | 15.3 | 14.8 | 16.2
166.3 | -52.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
167.3 | -51.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
168.3 | -50.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
169.3 | -49.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
170.3 | -48.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
171.3 | -47.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
172.3 | -46.7 | 15 | 14.8 | 15.3 | 14.8 | 16.2
173.3 | -45.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
174.3 | -44.7 | 15 | 14.8 | 15.3 | 14.8 | 16.2
175.3 | -43.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
176.3 | -42.7 | 15 | 14.8 | 15.3 | 14.8 | 16.2
177.3 | -41.7 | 15 | 14.8 | 15.3 | 14.8 | 16.2
178.3 | -40.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
179.3 | -39.7 | 15 | 14.8 | 15.3 | 14.8 | 16.2
180.3 | -38.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
181.3 | -37.7 | 15 | 14.8 | 15.3 | 14.8 | 16.2
182.3 | -36.7 | 15.1 | 14.8 | 15.3 | 14.8 | 16.2
183.3 | -35.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
184.3 | -34.7 | 15 | 14.8 | 15.3 | 14.8 | 16.2
185.3 | -33.7 | 15 | 14.8 | 15.3 | 14.8 | 16.2
186.3 | -32.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
187.3 | -31.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
188.3 | -30.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
189.3 | -29.7 | 15 | 14.8 | 15.3 | 14.8 | 16.2
190.3 | -28.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
191.3 | -27.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
192.3 | -26.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
193.3 | -25.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
194.3 | -24.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
195.3 | -23.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
196.3 | -22.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
197.3 | -21.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
198.3 | -20.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
199.3 | -19.7 | 15.1 | 14.8 | 15.2 | 14.8 | 16.2
200.3 | -18.7 | 15 | 14.8 | 15.3 | 14.8 | 16.2
201.3 | -17.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
202.3 | -16.7 | 15 | 14.8 | 15.3 | 14.8 | 16.2
203.3 | -15.7 | 15 | 14.8 | 15.3 | 14.8 | 16.2
204.3 | -14.7 | 15 | 14.8 | 15.3 | 14.8 | 16.2
205.3 | -13.7 | 15 | 14.8 | 15.3 | 14.8 | 16.2
206.3 | -12.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
207.3 | -11.7 | 15 | 14.8 | 15.3 | 14.8 | 16.2
208.3 | -10.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
209.3 | -9.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
210.3 | -8.7 | 15 | 14.8 | 15.3 | 14.8 | 16.2
211.3 | -7.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
212.3 | -6.7 | 15 | 14.8 | 15.3 | 14.8 | 16.2
213.3 | -5.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
214.3 | -4.7 | 15 | 14.8 | 15.3 | 14.8 | 16.2
215.3 | -3.7 | 15 | 14.8 | 15.3 | 14.8 | 16.2
216.3 | -2.7 | 15 | 14.8 | 15.2 | 14.8 | 16.2
217.3 | -1.7 | 15 | 14.8 | 15.3 | 14.8 | 16.2
218.3 | -0.7 | 15 | 14.8 | 15.3 | 14.8 | 16.2
219.3 | 0.3 | 15 | 14.8 | 15.3 | 14.8 | 16.2
220.3 | 1.3 | 15 | 14.8 | 15.3 | 14.8 | 16.2
221.3 | 2.3 | 15 | 14.8 | 15.3 | 14.8 | 16.2
222.3 | 3.3 | 15 | 14.8 | 15.3 | 14.8 | 16.2
223.3 | 4.3 | 15 | 14.8 | 15.3 | 14.8 | 16.2
224.3 | 5.3 | 15 | 14.8 | 15.3 | 14.8 | 16.2
225.3 | 6.3 | 15 | 14.8 | 15.3 | 14.8 | 16.3
226.3 | 7.3 | 15.1 | 15.1 | 15.8 | 14.8 | 16.4
227.3 | 8.3 | 15.1 | 16.3 | 17.6 | 14.9 | 16.7
228.3 | 9.3 | 15.1 | 18.8 | 20.7 | 14.9 | 17.3
229.3 | 10.3 | 15.1 | 23.7 | 24.3 | 14.9 | 18.4
230.3 | 11.3 | 15.1 | 28.7 | 29.7 | 14.9 | 19.4
231.3 | 12.3 | 15.1 | 33.4 | 34 | 14.9 | 20
232.3 | 13.3 | 15.1 | 40.2 | 39.7 | 14.9 | 21.7
233.3 | 14.3 | 15.1 | 48.3 | 51.9 | 15 | 23.4
234.3 | 15.3 | 15.1 | 61 | 65.5 | 15 | 25.9
235.3 | 16.3 | 15.1 | 78.8 | 94.9 | 15.1 | 29.7
236.3 | 17.3 | 15.1 | 89.6 | 110 | 15.1 | 31.3
237.3 | 18.3 | 15.1 | 102.3 | 131.7 | 15.2 | 34.3
238.3 | 19.3 | 15.1 | 115.1 | 141.2 | 15.3 | 36.4
239.3 | 20.3 | 15.1 | 129.1 | 159.9 | 15.4 | 39.2
240.3 | 21.3 | 15.1 | 136.6 | 173.5 | 15.5 | 42.2
241.3 | 22.3 | 15.1 | 139.7 | 173.1 | 15.6 | 43.7
242.3 | 23.3 | 15.1 | 150 | 193.3 | 15.7 | 46.4
243.3 | 24.3 | 15.1 | 160.6 | 211.5 | 15.8 | 49.3
244.3 | 25.3 | 15.1 | 171.5 | 222.4 | 16 | 52.3
245.3 | 26.3 | 15.1 | 180.6 | 246.3 | 16.1 | 56.1
246.3 | 27.3 | 15.2 | 190.2 | 261 | 16.2 | 59.8
247.3 | 28.3 | 15.2 | 193.2 | 257.4 | 16.4 | 62
248.3 | 29.3 | 15.2 | 195.2 | 266 | 16.5 | 64.6
249.3 | 30.3 | 15.3 | 198.9 | 266.4 | 16.7 | 67.2
250.3 | 31.3 | 15.3 | 208.9 | 288.6 | 16.9 | 70.2
251.3 | 32.3 | 15.3 | 215.8 | 296.6 | 17 | 73
252.3 | 33.3 | 15.4 | 220.3 | 300.5 | 17.2 | 75.4
253.3 | 34.3 | 15.5 | 225 | 298.7 | 17.4 | 76.7
254.3 | 35.3 | 15.5 | 230.2 | 306.2 | 17.6 | 79.7
255.3 | 36.3 | 15.6 | 240.1 | 316 | 17.8 | 83.1
256.3 | 37.3 | 15.7 | 247.6 | 323.6 | 18.1 | 86.4
257.3 | 38.3 | 15.8 | 248.8 | 318.2 | 18.3 | 88.5
258.3 | 39.3 | 15.9 | 248.4 | 319.1 | 18.5 | 90.2
259.3 | 40.3 | 16 | 248.5 | 315.3 | 18.7 | 92.3
260.3 | 41.3 | 16.1 | 251.5 | 317.8 | 19 | 94.1
261.3 | 42.3 | 16.2 | 258.8 | 333.6 | 19.3 | 97.5
262.3 | 43.3 | 16.3 | 266.9 | 343.9 | 19.7 | 100
263.3 | 44.3 | 16.5 | 273.5 | 347.9 | 20.1 | 103.1
264.3 | 45.3 | 16.6 | 271.2 | 342.3 | 20.5 | 103.1
265.3 | 46.3 | 16.8 | 272.3 | 342.5 | 21 | 104.7
266.3 | 47.3 | 17 | 270.7 | 338.9 | 21.4 | 106.1
267.3 | 48.3 | 17.2 | 269.8 | 339.9 | 21.8 | 107.4
268.3 | 49.3 | 17.4 | 269.5 | 343.2 | 22.1 | 109.6
269.3 | 50.3 | 17.7 | 272.7 | 348.3 | 22.5 | 111.4
270.3 | 51.3 | 17.9 | 274.1 | 345.1 | 22.9 | 114.1
271.3 | 52.3 | 18.2 | 280.9 | 358.1 | 23.3 | 120.9
272.3 | 53.3 | 18.5 | 285.7 | 372.9 | 23.7 | 125.1
273.3 | 54.3 | 18.8 | 286.1 | 369.6 | 24.1 | 127.4
274.3 | 55.3 | 19.1 | 289.1 | 374 | 24.5 | 131.8
275.3 | 56.3 | 19.4 | 291 | 372.7 | 24.9 | 133.9
276.3 | 57.3 | 19.7 | 290.8 | 371.7 | 25.3 | 134.9
277.3 | 58.3 | 20 | 290.3 | 375.9 | 25.7 | 136
278.3 | 59.3 | 20.3 | 288.7 | 370.6 | 26.1 | 136.5
279.3 | 60.3 | 20.7 | 286.9 | 365.8 | 26.5 | 137.9
280.3 | 61.3 | 21 | 287.9 | 368.8 | 26.8 | 141
281.3 | 62.3 | 21.4 | 285.8 | 361.7 | 27.2 | 141.4
282.3 | 63.3 | 21.8 | 284.9 | 361.5 | 27.6 | 142.5
283.3 | 64.3 | 22.1 | 284.9 | 361.7 | 28 | 144.2
284.3 | 65.3 | 22.5 | 283.6 | 356.1 | 28.3 | 145.4
285.3 | 66.3 | 22.8 | 284.8 | 354.4 | 28.7 | 147.9
286.3 | 67.3 | 23.2 | 282.7 | 344.1 | 29.1 | 149.2
287.3 | 68.3 | 23.6 | 282.8 | 346.7 | 29.4 | 151.4
288.3 | 69.3 | 24 | 282.3 | 347 | 29.8 | 153.6
289.3 | 70.3 | 24.3 | 285.2 | 345.9 | 30.1 | 158.3
290.3 | 71.3 | 24.7 | 290.5 | 350 | 30.6 | 162.2
291.3 | 72.3 | 25.1 | 295.6 | 355.5 | 31 | 164.8
292.3 | 73.3 | 25.5 | 301.5 | 355.6 | 31.5 | 167.4
293.3 | 74.3 | 25.9 | 305.8 | 361 | 32.1 | 169.6
294.3 | 75.3 | 26.3 | 310.5 | 375 | 32.6 | 173.2
295.3 | 76.3 | 26.7 | 315.7 | 376.7 | 33.1 | 177
296.3 | 77.3 | 27.1 | 319.1 | 375.5 | 33.6 | 180
297.3 | 78.3 | 27.6 | 318.2 | 371.2 | 34.1 | 180
298.3 | 79.3 | 28 | 313.6 | 362.5 | 34.5 | 179.6
299.3 | 80.3 | 28.4 | 310.4 | 358.5 | 34.9 | 179.7
300.3 | 81.3 | 28.8 | 309.3 | 360.6 | 35.3 | 180.9
301.3 | 82.3 | 29.3 | 310.3 | 358.3 | 35.8 | 184.3
302.3 | 83.3 | 29.7 | 310.6 | 360.9 | 36.2 | 185.5
303.3 | 84.3 | 30.1 | 308.5 | 358.3 | 36.7 | 186.1
304.3 | 85.3 | 30.5 | 310 | 369 | 37.1 | 189.2
305.3 | 86.3 | 31 | 306.7 | 359 | 37.5 | 189.1
306.3 | 87.3 | 31.4 | 307.4 | 367.3 | 37.9 | 190.4
307.3 | 88.3 | 31.9 | 309.3 | 366.6 | 38.3 | 193.8
308.3 | 89.3 | 32.3 | 309.5 | 368.5 | 38.8 | 195.4
309.3 | 90.3 | 32.7 | 312.8 | 370.7 | 39.3 | 198.5
310.3 | 91.3 | 33.2 | 310.7 | 369.7 | 39.8 | 198
311.3 | 92.3 | 33.6 | 312 | 378.5 | 40.2 | 200.8
312.3 | 93.3 | 34.1 | 315 | 379.4 | 40.8 | 205
313.3 | 94.3 | 34.6 | 321.1 | 377.4 | 41.2 | 209.2
314.3 | 95.3 | 35 | 332.4 | 397.1 | 41.8 | 216
315.3 | 96.3 | 35.5 | 339.4 | 403.2 | 42.4 | 220.1
316.3 | 97.3 | 36 | 338.9 | 400.9 | 43 | 221.2
317.3 | 98.3 | 36.4 | 336.5 | 403.3 | 43.5 | 221.8
318.3 | 99.3 | 36.9 | 339.1 | 406.8 | 44 | 224.2
319.3 | 100.3 | 37.4 | 343.8 | 413.2 | 44.6 | 229.5
320.3 | 101.3 | 37.8 | 347.5 | 423.7 | 45.2 | 234.1
321.3 | 102.3 | 38.4 | 347.8 | 419.4 | 45.8 | 233.9
322.3 | 103.3 | 38.9 | 344.1 | 410.3 | 46.3 | 232.9
323.3 | 104.3 | 39.4 | 342.4 | 403.5 | 46.8 | 234.7
324.3 | 105.3 | 39.9 | 342.5 | 407.5 | 47.3 | 235.8
325.3 | 106.3 | 40.4 | 345.4 | 409.6 | 47.8 | 239.7
326.3 | 107.3 | 40.9 | 347.5 | 409.6 | 48.4 | 243.2
327.3 | 108.3 | 41.5 | 349.6 | 409 | 48.9 | 245
328.3 | 109.3 | 42 | 354.6 | 413.2 | 49.6 | 252.2
329.3 | 110.3 | 42.5 | 357.2 | 419.8 | 50.1 | 253.9
330.3 | 111.3 | 43.1 | 353.6 | 408.4 | 50.7 | 252.9
331.3 | 112.3 | 43.6 | 350.5 | 408.5 | 51.2 | 253.1
332.3 | 113.3 | 44.2 | 349.6 | 412.2 | 51.6 | 254.3
333.3 | 114.3 | 44.7 | 354.6 | 425.4 | 52.1 | 257.2
334.3 | 115.3 | 45.3 | 362.6 | 435.9 | 52.6 | 263.2
335.3 | 116.3 | 45.9 | 366.7 | 433.1 | 53.3 | 266.6
336.3 | 117.3 | 46.4 | 363.8 | 431.5 | 53.7 | 266.1
337.3 | 118.3 | 47 | 367.8 | 450.3 | 54.2 | 268.2
338.3 | 119.3 | 47.6 | 374.2 | 471.3 | 54.8 | 272.8
339.3 | 120.3 | 48.2 | 374.9 | 468.9 | 55.4 | 274.4
340.3 | 121.3 | 48.8 | 370.3 | 451.6 | 55.9 | 274.2
341.3 | 122.3 | 49.3 | 363.4 | 435 | 56.4 | 273.2
342.3 | 123.3 | 49.9 | 359.2 | 426.3 | 56.9 | 273.9
343.3 | 124.3 | 50.5 | 357.4 | 419.8 | 57.4 | 273.6
344.3 | 125.3 | 51.1 | 357.9 | 416.2 | 57.9 | 276.4
345.3 | 126.3 | 51.7 | 359 | 414 | 58.5 | 278.5
346.3 | 127.3 | 52.3 | 358.9 | 412.9 | 59 | 280.3
347.3 | 128.3 | 52.9 | 356.4 | 407.6 | 59.5 | 279.8
348.3 | 129.3 | 53.5 | 353.2 | 403.4 | 60 | 280.1
349.3 | 130.3 | 54.1 | 350.9 | 402.6 | 60.5 | 280.2
350.3 | 131.3 | 54.7 | 347.5 | 398.2 | 60.9 | 280.7
351.3 | 132.3 | 55.3 | 346.9 | 395.5 | 61.4 | 281.9
352.3 | 133.3 | 55.9 | 345 | 387.6 | 61.8 | 283.1
353.3 | 134.3 | 56.5 | 344.3 | 384.8 | 62.3 | 284.6
354.3 | 135.3 | 57.1 | 342.7 | 385.3 | 62.7 | 284.1
355.3 | 136.3 | 57.7 | 340.9 | 380.6 | 63.2 | 283.7
356.3 | 137.3 | 58.3 | 337.5 | 377.6 | 63.6 | 282.6
357.3 | 138.3 | 58.9 | 334.2 | 379.1 | 64 | 282.3
358.3 | 139.3 | 59.5 | 336.2 | 390.6 | 64.3 | 283.4
359.3 | 140.3 | 60.1 | 333.4 | 385.5 | 64.8 | 283.9
360.3 | 141.3 | 60.7 | 333.1 | 379.1 | 65.3 | 285.6
361.3 | 142.3 | 61.3 | 329.9 | 373 | 65.7 | 284.1
362.3 | 143.3 | 61.9 | 325.9 | 366 | 66 | 283.2
363.3 | 144.3 | 62.5 | 322.9 | 364.5 | 66.3 | 282.5
364.3 | 145.3 | 63.1 | 319.4 | 358.2 | 66.7 | 282.3
365.3 | 146.3 | 63.7 | 316 | 350.4 | 67 | 281.6
366.3 | 147.3 | 64.3 | 312 | 341.4 | 67.4 | 281.3
367.3 | 148.3 | 64.9 | 310.9 | 342 | 67.7 | 282.2
368.3 | 149.3 | 65.5 | 308.3 | 338.3 | 68 | 281.7
369.3 | 150.3 | 66.1 | 306.6 | 335.5 | 68.4 | 281.1
370.3 | 151.3 | 66.7 | 301.5 | 328.8 | 68.6 | 280.2
371.3 | 152.3 | 67.3 | 299.3 | 329.8 | 68.8 | 279.7
372.3 | 153.3 | 67.9 | 297.2 | 327.6 | 69 | 278.7
373.3 | 154.3 | 68.5 | 300.8 | 332.2 | 69.3 | 281
374.3 | 155.3 | 69.1 | 305.9 | 331.2 | 69.8 | 284.2
375.3 | 156.3 | 69.7 | 309.9 | 334.6 | 70.3 | 285.2
376.3 | 157.3 | 70.2 | 310.5 | 336.1 | 70.7 | 284
377.3 | 158.3 | 70.8 | 309.7 | 336.4 | 71.1 | 283.5
378.3 | 159.3 | 71.4 | 310.5 | 349.6 | 71.4 | 283.5
379.3 | 160.3 | 72 | 309.3 | 347.2 | 71.6 | 283
380.3 | 161.3 | 72.6 | 310.3 | 351.8 | 71.9 | 283.5
381.3 | 162.3 | 73.2 | 309.5 | 349.5 | 72.3 | 282.8
382.3 | 163.3 | 73.8 | 309 | 356 | 72.6 | 282.8
383.3 | 164.3 | 74.4 | 309.1 | 362.5 | 72.9 | 283.2
384.3 | 165.3 | 74.9 | 310 | 365.3 | 73.2 | 283.6
385.3 | 166.3 | 75.5 | 310.1 | 363.7 | 73.5 | 283.9
386.3 | 167.3 | 76.1 | 307.5 | 355.6 | 73.9 | 283.2
387.3 | 168.3 | 76.7 | 302.9 | 347.4 | 74.1 | 281.2
388.3 | 169.3 | 77.3 | 299.8 | 345.2 | 74.4 | 280.9
389.3 | 170.3 | 77.9 | 298.7 | 345.1 | 74.7 | 280.9
390.3 | 171.3 | 78.4 | 301.9 | 354.4 | 74.9 | 281.8
391.3 | 172.3 | 79 | 300.7 | 351.6 | 75.2 | 281.5
392.3 | 173.3 | 79.6 | 301.8 | 359.4 | 75.5 | 281.3
393.3 | 174.3 | 80.2 | 306.1 | 372.8 | 75.8 | 282.2
394.3 | 175.3 | 80.8 | 311.2 | 378.2 | 76.2 | 284.2
395.3 | 176.3 | 81.3 | 319.6 | 396.4 | 76.6 | 286.1
396.3 | 177.3 | 81.9 | 325.9 | 407.5 | 77.2 | 288.1
397.3 | 178.3 | 82.5 | 326.1 | 403.1 | 77.7 | 287.9
398.3 | 179.3 | 83.1 | 326.1 | 394.6 | 78.1 | 287.6
399.3 | 180.3 | 83.7 | 324.3 | 391.5 | 78.4 | 286.9
400.3 | 181.3 | 84.3 | 322.5 | 389.3 | 78.7 | 287.6
401.3 | 182.3 | 84.9 | 326 | 396.3 | 79 | 291
402.3 | 183.3 | 85.5 | 326.9 | 389.4 | 79.5 | 291.8
403.3 | 184.3 | 86.1 | 328.9 | 389.8 | 79.9 | 293.9
404.3 | 185.3 | 86.7 | 333.7 | 391.2 | 80.4 | 297.1
405.3 | 186.3 | 87.3 | 335.8 | 397.3 | 80.9 | 299.1
406.3 | 187.3 | 87.9 | 338.6 | 403.7 | 81.5 | 300.8
407.3 | 188.3 | 88.5 | 343.3 | 416.9 | 82 | 304
408.3 | 189.3 | 89.1 | 351.1 | 433 | 82.7 | 308.6
409.3 | 190.3 | 89.7 | 352.3 | 436 | 83.3 | 309.6
410.3 | 191.3 | 90.4 | 357.4 | 442.1 | 84 | 313.6
411.3 | 192.3 | 91 | 359.8 | 443.9 | 84.6 | 314.4
412.3 | 193.3 | 91.6 | 362.7 | 446.9 | 85.3 | 316.5
413.3 | 194.3 | 92.2 | 372.4 | 453.6 | 86.2 | 321.8
414.3 | 195.3 | 92.9 | 372.1 | 450.2 | 86.8 | 322.8
415.3 | 196.3 | 93.5 | 371.4 | 449.6 | 87.5 | 322.7
416.3 | 197.3 | 94.2 | 370.5 | 450.4 | 87.9 | 323
417.3 | 198.3 | 94.8 | 371.4 | 454.2 | 88.4 | 323.1
418.3 | 199.3 | 95.5 | 369.3 | 455 | 88.9 | 322
419.3 | 200.3 | 96.1 | 366.1 | 448.7 | 89.1 | 321.3
420.3 | 201.3 | 96.8 | 362.3 | 444.4 | 89.5 | 321.5
421.3 | 202.3 | 97.4 | 362.6 | 447.1 | 89.9 | 322.4
422.3 | 203.3 | 98.1 | 362.2 | 449.2 | 90.4 | 324.2
423.3 | 204.3 | 98.8 | 364.5 | 450.5 | 91 | 326.4
424.3 | 205.3 | 99.4 | 365.4 | 454.1 | 91.6 | 328.2
425.3 | 206.3 | 100.1 | 366.1 | 449.5 | 91.9 | 328.5
426.3 | 207.3 | 100.8 | 366.3 | 442.7 | 92.2 | 329.1
427.3 | 208.3 | 101.5 | 364.2 | 440.8 | 92.6 | 329.7
428.3 | 209.3 | 102.2 | 359.9 | 429.6 | 93 | 329.6
429.3 | 210.3 | 102.9 | 356.6 | 426.6 | 93.3 | 330.2
430.3 | 211.3 | 103.6 | 353.7 | 422.3 | 93.8 | 330.5
431.3 | 212.3 | 104.3 | 349.7 | 418.1 | 94.2 | 329.2
432.3 | 213.3 | 105 | 348.3 | 417.2 | 94.6 | 328.8
433.3 | 214.3 | 105.7 | 346.9 | 408.3 | 94.9 | 329.9
434.3 | 215.3 | 106.5 | 347.1 | 405.6 | 95.4 | 331
435.3 | 216.3 | 107.2 | 342.8 | 399.8 | 95.7 | 329.3
436.3 | 217.3 | 108 | 343.2 | 402.6 | 96 | 329.8
437.3 | 218.3 | 108.8 | 343.2 | 401.9 | 96.3 | 330.3
438.3 | 219.3 | 109.6 | 345.6 | 408.7 | 96.6 | 331
439.3 | 220.3 | 110.5 | 343.3 | 401.6 | 96.9 | 329.4
440.3 | 221.3 | 111.3 | 344.2 | 410.5 | 97.5 | 329.3
441.3 | 222.3 | 112.2 | 344.2 | 408.5 | 97.9 | 328.6
442.3 | 223.3 | 113.1 | 340.3 | 406.1 | 98.1 | 327.4
443.3 | 224.3 | 114 | 338.1 | 407.3 | 98.3 | 327.6
444.3 | 225.3 | 114.9 | 336.7 | 405.9 | 98.6 | 327.2
445.3 | 226.3 | 115.8 | 335.3 | 402.3 | 99 | 327.5
446.3 | 227.3 | 116.7 | 332.7 | 394.7 | 99.2 | 326.1
447.3 | 228.3 | 117.6 | 329.4 | 386.8 | 99.4 | 325
448.3 | 229.3 | 118.5 | 325.1 | 377.8 | 99.6 | 323.6
449.3 | 230.3 | 119.4 | 321.2 | 368.3 | 99.8 | 322.3
450.3 | 231.3 | 120.3 | 316.3 | 363.2 | 100 | 320.8
451.3 | 232.3 | 121.2 | 313.9 | 362.4 | 100.2 | 319.8
452.3 | 233.3 | 122.1 | 313.2 | 365.3 | 100.5 | 319.2
453.3 | 234.3 | 123 | 312.2 | 367.7 | 100.7 | 318.4
454.3 | 235.3 | 123.9 | 313.9 | 370 | 100.9 | 319.2
455.3 | 236.3 | 124.8 | 314.5 | 366.6 | 101.3 | 319.7
456.3 | 237.3 | 125.6 | 313.7 | 362.3 | 101.6 | 319.9
457.3 | 238.3 | 126.5 | 315.1 | 359.8 | 102.2 | 320.8
458.3 | 239.3 | 127.3 | 314.5 | 359.9 | 102.7 | 320.5
459.3 | 240.3 | 128.2 | 316.1 | 361.3 | 103.3 | 321.2
460.3 | 241.3 | 129 | 317.3 | 363.4 | 103.9 | 321.4
461.3 | 242.3 | 129.8 | 320.5 | 363.6 | 104.5 | 323.4
462.3 | 243.3 | 130.6 | 323.8 | 365.1 | 105.1 | 325.2
463.3 | 244.3 | 131.4 | 328 | 371.2 | 105.6 | 327
464.3 | 245.3 | 132.3 | 333.7 | 372.4 | 106.5 | 328.3
465.3 | 246.3 | 133.1 | 334.8 | 377.6 | 106.9 | 327.7
466.3 | 247.3 | 133.9 | 332.2 | 374.8 | 107.1 | 327
467.3 | 248.3 | 134.7 | 331.9 | 376.1 | 107.3 | 327.6
468.3 | 249.3 | 135.5 | 331.9 | 376.4 | 107.7 | 328.3
469.3 | 250.3 | 136.4 | 334 | 385.8 | 108.3 | 328.9
470.3 | 251.3 | 137.2 | 337.9 | 392.4 | 109.1 | 329.7
471.3 | 252.3 | 138 | 336.1 | 386.5 | 109.6 | 329
472.3 | 253.3 | 138.8 | 334.2 | 383.6 | 109.9 | 329.3
473.3 | 254.3 | 139.7 | 334 | 380.5 | 110.1 | 329.5
474.3 | 255.3 | 140.5 | 333.3 | 376.9 | 110.4 | 329.9
475.3 | 256.3 | 141.3 | 332.6 | 380.5 | 110.9 | 329.4
476.3 | 257.3 | 142.1 | 333.5 | 381.9 | 111.3 | 329.9
477.3 | 258.3 | 142.9 | 332.6 | 380.8 | 111.5 | 330.1
478.3 | 259.3 | 143.7 | 333.6 | 384.9 | 112.1 | 331.2
479.3 | 260.3 | 144.5 | 333.3 | 381.7 | 112.3 | 331.9
480.3 | 261.3 | 145.3 | 331.2 | 377.6 | 112.5 | 331.1
481.3 | 262.3 | 146.1 | 329.1 | 372.2 | 112.9 | 330.4
482.3 | 263.3 | 146.9 | 329.2 | 370.3 | 113.4 | 331.4
483.3 | 264.3 | 147.7 | 328.2 | 369.5 | 114 | 330.9
484.3 | 265.3 | 148.5 | 324.9 | 364.5 | 114.5 | 330.2
485.3 | 266.3 | 149.3 | 322.2 | 361.1 | 114.7 | 329.3
486.3 | 267.3 | 150.1 | 319.6 | 357 | 115 | 327.9
487.3 | 268.3 | 150.9 | 315.2 | 349 | 115.1 | 326.3
488.3 | 269.3 | 151.6 | 310 | 342.3 | 115.1 | 325
489.3 | 270.3 | 152.4 | 306.1 | 337.3 | 115.2 | 323.8
490.3 | 271.3 | 153.2 | 304.5 | 335 | 115.6 | 323.1
491.3 | 272.3 | 153.9 | 302.9 | 341.8 | 115.7 | 323
492.3 | 273.3 | 154.6 | 302.7 | 342.6 | 116.2 | 323.2
493.3 | 274.3 | 155.3 | 300.4 | 344.3 | 116.3 | 322.4
494.3 | 275.3 | 156 | 302.6 | 351.4 | 116.9 | 322.9
495.3 | 276.3 | 156.6 | 306.1 | 354.2 | 117.5 | 324.2
496.3 | 277.3 | 157.3 | 308.6 | 357.4 | 117.8 | 324.9
497.3 | 278.3 | 157.9 | 310.7 | 355.5 | 118.1 | 325.8
498.3 | 279.3 | 158.6 | 310 | 351.6 | 118.1 | 325.1
499.3 | 280.3 | 159.2 | 308.6 | 348.3 | 118 | 324.2
500.3 | 281.3 | 159.9 | 310 | 355.3 | 118.1 | 324.9
501.3 | 282.3 | 160.5 | 314 | 359.6 | 118.8 | 326.6
502.3 | 283.3 | 161.1 | 316.9 | 367.1 | 119.8 | 328.8
503.3 | 284.3 | 161.8 | 327.1 | 381.7 | 120.9 | 331.1
504.3 | 285.3 | 162.4 | 331.2 | 384.4 | 121.3 | 333.1
505.3 | 286.3 | 163 | 331.3 | 379.9 | 121.4 | 332.2
506.3 | 287.3 | 163.6 | 331.4 | 381.4 | 121.6 | 332.8
507.3 | 288.3 | 164.3 | 330.5 | 377.5 | 121.9 | 332.7
508.3 | 289.3 | 164.9 | 331.3 | 373 | 122 | 332.8
509.3 | 290.3 | 165.4 | 330.3 | 370 | 122.1 | 332.5
510.3 | 291.3 | 166 | 328.3 | 364.5 | 122.3 | 332
511.3 | 292.3 | 166.5 | 328 | 366.2 | 122.4 | 331.8
512.3 | 293.3 | 167 | 328.2 | 365.1 | 122.6 | 332.4
513.3 | 294.3 | 167.5 | 330 | 376.1 | 122.7 | 333
514.3 | 295.3 | 168 | 329.8 | 378.4 | 123 | 332.6
515.3 | 296.3 | 168.5 | 328.8 | 377.1 | 123.1 | 332.2
516.3 | 297.3 | 169 | 325.4 | 370 | 123.2 | 331
517.3 | 298.3 | 169.4 | 322.6 | 371.2 | 123.3 | 331.2
518.3 | 299.3 | 169.9 | 324.9 | 382.6 | 123.5 | 331.7
519.3 | 300.3 | 170.3 | 331.6 | 386.6 | 124 | 333.8
520.3 | 301.3 | 170.8 | 332.4 | 382.9 | 124.3 | 333.3
521.3 | 302.3 | 171.3 | 330.4 | 376.1 | 124.5 | 332.5
522.3 | 303.3 | 171.7 | 326.5 | 372.3 | 124.7 | 331
523.3 | 304.3 | 172.1 | 329.3 | 379.8 | 124.8 | 331.5
524.3 | 305.3 | 172.6 | 331.4 | 378.2 | 125.2 | 333.7
525.3 | 306.3 | 173.1 | 333.4 | 377.4 | 125.8 | 334.8
526.3 | 307.3 | 173.6 | 332.4 | 371.4 | 126 | 334
527.3 | 308.3 | 174 | 331.5 | 369.6 | 126.2 | 333.1
528.3 | 309.3 | 174.5 | 328.3 | 364 | 126.4 | 332.2
529.3 | 310.3 | 175 | 326 | 363 | 126.6 | 331.4
530.3 | 311.3 | 175.4 | 320.6 | 354.3 | 126.6 | 330.5
531.3 | 312.3 | 175.9 | 319 | 351.4 | 126.8 | 330.6
532.3 | 313.3 | 176.4 | 316.6 | 347.3 | 127.1 | 330
533.3 | 314.3 | 176.8 | 313.6 | 339.7 | 127.2 | 329.2
534.3 | 315.3 | 177.2 | 312.2 | 332.3 | 127.4 | 328.8
535.3 | 316.3 | 177.7 | 310.9 | 326.4 | 127.6 | 328.2
536.3 | 317.3 | 178.1 | 309.7 | 323.3 | 127.8 | 328
537.3 | 318.3 | 178.6 | 308.6 | 322.7 | 127.9 | 327.2
538.3 | 319.3 | 179 | 305.7 | 319.3 | 128.1 | 326.6
539.3 | 320.3 | 179.4 | 303.5 | 315.6 | 128.2 | 325.4
540.3 | 321.3 | 179.8 | 301.1 | 314.7 | 128.2 | 324.9
541.3 | 322.3 | 180.1 | 296.9 | 312.3 | 128.2 | 323.4
542.3 | 323.3 | 180.6 | 295.8 | 313.4 | 128.3 | 322.9
543.3 | 324.3 | 181 | 294.3 | 311.7 | 128.4 | 322.4
544.3 | 325.3 | 181.4 | 295.7 | 314.4 | 128.7 | 323.9
545.3 | 326.3 | 181.7 | 297.6 | 317.8 | 129.3 | 324.5
546.3 | 327.3 | 182.1 | 298.9 | 323.1 | 129.7 | 325.1
547.3 | 328.3 | 182.5 | 303.5 | 331 | 130.1 | 326.4
548.3 | 329.3 | 182.9 | 308.3 | 336.9 | 130.7 | 327.6
549.3 | 330.3 | 183.3 | 312.4 | 341.5 | 131.2 | 328.8
550.3 | 331.3 | 183.7 | 316.2 | 346.3 | 131.6 | 329.2
551.3 | 332.3 | 184 | 318.7 | 346 | 132.1 | 330.2
552.3 | 333.3 | 184.4 | 321 | 351.9 | 132.8 | 331.1
553.3 | 334.3 | 184.8 | 322.8 | 353 | 133.5 | 331.3
554.3 | 335.3 | 185.3 | 325.1 | 352.7 | 133.9 | 331.1
555.3 | 336.3 | 185.7 | 323.8 | 351.3 | 133.9 | 330.3
556.3 | 337.3 | 186.1 | 327.4 | 355.5 | 134.3 | 332.3
557.3 | 338.3 | 186.5 | 326.7 | 353.4 | 134.6 | 331.9
558.3 | 339.3 | 186.9 | 327.9 | 353 | 135 | 332.6
559.3 | 340.3 | 187.3 | 329 | 353 | 135.4 | 334.3
560.3 | 341.3 | 187.7 | 332.4 | 356.1 | 136.1 | 335.8
561.3 | 342.3 | 188.1 | 336.5 | 358.6 | 136.8 | 337.1
562.3 | 343.3 | 188.5 | 339.6 | 364.7 | 137.4 | 339.3
563.3 | 344.3 | 189 | 343.8 | 370.8 | 138.1 | 341
564.3 | 345.3 | 189.4 | 344.2 | 377.4 | 138.7 | 340.5
565.3 | 346.3 | 189.8 | 343.6 | 381.2 | 138.9 | 340.2
566.3 | 347.3 | 190.2 | 340.7 | 376.4 | 139 | 339.2
567.3 | 348.3 | 190.6 | 338.3 | 375.4 | 139 | 338.2
568.3 | 349.3 | 191 | 336 | 374.5 | 139.1 | 337.8
569.3 | 350.3 | 191.3 | 336.8 | 377.6 | 139.3 | 338.4
570.3 | 351.3 | 191.7 | 335.1 | 369.4 | 139.5 | 337.7
571.3 | 352.3 | 192.1 | 332.8 | 363.6 | 139.7 | 336.9
572.3 | 353.3 | 192.5 | 331.9 | 361.5 | 140 | 336.4
573.3 | 354.3 | 192.9 | 329.2 | 357.1 | 140.1 | 335.5
574.3 | 355.3 | 193.2 | 324.8 | 349.8 | 140.3 | 334.5
575.3 | 356.3 | 193.6 | 320 | 343.8 | 140.3 | 333.4
576.3 | 357.3 | 193.9 | 316.2 | 340.1 | 140.5 | 332.5
577.3 | 358.3 | 194.3 | 313 | 338.8 | 140.5 | 331.2
578.3 | 359.3 | 194.7 | 311 | 337.9 | 140.6 | 330.5
579.3 | 360.3 | 195 | 308.7 | 333.8 | 140.7 | 329.7
580.3 | 361.3 | 195.4 | 306.7 | 331.1 | 140.8 | 328.8
581.3 | 362.3 | 195.7 | 305.4 | 331.9 | 140.9 | 328.3
582.3 | 363.3 | 196.1 | 302.4 | 325.2 | 141 | 327.1
583.3 | 364.3 | 196.4 | 299.2 | 322.8 | 141.1 | 326.2
584.3 | 365.3 | 196.7 | 296.2 | 316.5 | 141.2 | 325.4
585.3 | 366.3 | 197.1 | 294.4 | 315.8 | 141.3 | 324.6
586.3 | 367.3 | 197.4 | 292.7 | 313.7 | 141.5 | 323.9
587.3 | 368.3 | 197.7 | 290 | 310.2 | 141.6 | 322.6
588.3 | 369.3 | 198.1 | 287.2 | 309.6 | 141.7 | 321.7
589.3 | 370.3 | 198.4 | 286.6 | 309.5 | 141.8 | 320.9
590.3 | 371.3 | 198.7 | 286.1 | 308.4 | 142 | 320.8
591.3 | 372.3 | 199 | 285.3 | 306.2 | 142.1 | 319.9
592.3 | 373.3 | 199.3 | 285.3 | 302.9 | 142.3 | 319.6
593.3 | 374.3 | 199.7 | 284.3 | 301.6 | 142.4 | 319
594.3 | 375.3 | 200 | 284.1 | 302.2 | 142.6 | 318.7
595.3 | 376.3 | 200.3 | 283.5 | 305.1 | 142.8 | 317.8
596.3 | 377.3 | 200.6 | 281.4 | 303 | 142.9 | 317.2
597.3 | 378.3 | 200.9 | 281.8 | 307.2 | 143 | 316.7
598.3 | 379.3 | 201.2 | 282.6 | 309.2 | 143.1 | 316.1
599.3 | 380.3 | 201.5 | 282.3 | 307.2 | 143.3 | 315.7
600.3 | 381.3 | 201.9 | 281.9 | 309.1 | 143.5 | 315.1
601.3 | 382.3 | 202.2 | 283.6 | 317.4 | 143.7 | 315.3
602.3 | 383.3 | 202.5 | 287.9 | 329.8 | 144.1 | 316.4
603.3 | 384.3 | 202.8 | 290.5 | 333 | 144.4 | 316.8
604.3 | 385.3 | 203.1 | 293.8 | 339.9 | 144.8 | 317.3
605.3 | 386.3 | 203.4 | 295.4 | 346.2 | 145.1 | 317.3
606.3 | 387.3 | 203.8 | 299.6 | 362.2 | 145.7 | 318.4
607.3 | 388.3 | 204.1 | 305.3 | 366 | 146.2 | 320
608.3 | 389.3 | 204.4 | 310.4 | 371 | 146.6 | 321.2
609.3 | 390.3 | 204.8 | 312.1 | 369.6 | 147.1 | 320.7
610.3 | 391.3 | 205.1 | 312.9 | 370.1 | 147.4 | 320.6
611.3 | 392.3 | 205.4 | 314.3 | 372.4 | 147.7 | 320.9
612.3 | 393.3 | 205.8 | 318.3 | 375.6 | 148.1 | 321.8
613.3 | 394.3 | 206.1 | 320.4 | 373.6 | 148.5 | 322.4
614.3 | 395.3 | 206.5 | 319.9 | 368.7 | 148.7 | 321.6
615.3 | 396.3 | 206.9 | 318.8 | 361.8 | 148.9 | 321.2
616.3 | 397.3 | 207.2 | 316.4 | 357.9 | 149 | 321.1
617.3 | 398.3 | 207.6 | 317.2 | 361.1 | 149.2 | 322.1
618.3 | 399.3 | 207.9 | 320.3 | 364 | 149.5 | 322.8
619.3 | 400.3 | 208.3 | 322.2 | 369.9 | 149.8 | 323.2
620.3 | 401.3 | 208.6 | 323.8 | 369.9 | 150 | 323.9
621.3 | 402.3 | 209 | 322.2 | 363.5 | 150.3 | 323.7
622.3 | 403.3 | 209.3 | 319.9 | 362.2 | 150.5 | 323.1
623.3 | 404.3 | 209.7 | 316.4 | 356.7 | 150.7 | 322.2
624.3 | 405.3 | 210 | 314.5 | 356.5 | 150.9 | 322
625.3 | 406.3 | 210.4 | 310.2 | 348.9 | 151.1 | 320.7
626.3 | 407.3 | 210.7 | 306.8 | 344.4 | 151.2 | 319.8
627.3 | 408.3 | 211 | 304.4 | 339 | 151.3 | 319.4
628.3 | 409.3 | 211.3 | 302.8 | 335 | 151.5 | 318.9
629.3 | 410.3 | 211.6 | 304.2 | 339.6 | 151.8 | 319.4
630.3 | 411.3 | 211.9 | 305.6 | 341.3 | 152.1 | 319.4
631.3 | 412.3 | 212.2 | 304.7 | 341.5 | 152.4 | 319.4
632.3 | 413.3 | 212.5 | 306.1 | 343 | 152.6 | 319.6
633.3 | 414.3 | 212.8 | 307.2 | 343.2 | 152.9 | 320
634.3 | 415.3 | 213.1 | 309.8 | 345.8 | 153.2 | 320.6
635.3 | 416.3 | 213.4 | 312.6 | 353.5 | 153.6 | 321.3
636.3 | 417.3 | 213.7 | 314.3 | 360.8 | 153.9 | 321.9
637.3 | 418.3 | 213.9 | 317.6 | 366.8 | 154.4 | 323.3
638.3 | 419.3 | 214.2 | 320.4 | 367.9 | 154.9 | 324.3
639.3 | 420.3 | 214.5 | 325.9 | 372.2 | 155.6 | 327.4
640.3 | 421.3 | 214.7 | 334.3 | 390.3 | 156.4 | 330.3
641.3 | 422.3 | 215 | 336.1 | 391.9 | 157.2 | 332
642.3 | 423.3 | 215.3 | 337.4 | 390.5 | 157.7 | 332.6
643.3 | 424.3 | 215.5 | 340.2 | 395.9 | 158.3 | 334.3
644.3 | 425.3 | 215.8 | 342.1 | 399.3 | 158.9 | 335.1
645.3 | 426.3 | 216.1 | 343.9 | 405.7 | 159.5 | 335.3
646.3 | 427.3 | 216.3 | 343.4 | 400.3 | 160 | 335.9
647.3 | 428.3 | 216.6 | 342.2 | 398.4 | 160.5 | 335.9
648.3 | 429.3 | 216.9 | 340.9 | 393.8 | 160.9 | 335.7
649.3 | 430.3 | 217.1 | 340.1 | 390.7 | 161.3 | 335.5
650.3 | 431.3 | 217.4 | 339.7 | 387.8 | 161.6 | 335.7
651.3 | 432.3 | 217.7 | 338.9 | 384.9 | 161.9 | 335.6
652.3 | 433.3 | 218 | 338.4 | 390.7 | 162.2 | 335.7
653.3 | 434.3 | 218.2 | 338.8 | 397.8 | 162.5 | 336.3
654.3 | 435.3 | 218.5 | 338.6 | 396.2 | 162.9 | 336.3
655.3 | 436.3 | 218.8 | 336 | 388.8 | 163.3 | 336
656.3 | 437.3 | 219.1 | 333.9 | 383.2 | 163.7 | 335.5
657.3 | 438.3 | 219.4 | 331.9 | 382.2 | 164 | 335.7
658.3 | 439.3 | 219.7 | 330.7 | 382.9 | 164.3 | 335.2
659.3 | 440.3 | 220 | 331.6 | 385.9 | 164.8 | 335.7
660.3 | 441.3 | 220.2 | 329.3 | 378.4 | 165.2 | 335.2
661.3 | 442.3 | 220.5 | 329.7 | 381.5 | 165.7 | 335.6
662.3 | 443.3 | 220.8 | 327.8 | 378.2 | 166.3 | 335.1
663.3 | 444.3 | 221 | 326.1 | 374.4 | 167 | 335
664.3 | 445.3 | 221.3 | 326.1 | 375.6 | 167.7 | 335.2
665.3 | 446.3 | 221.6 | 326.2 | 377.7 | 168.7 | 335.3
666.3 | 447.3 | 221.8 | 330.3 | 394.5 | 170.1 | 337.7
667.3 | 448.3 | 222.1 | 337.3 | 409.6 | 172.2 | 339.8
668.3 | 449.3 | 222.4 | 342.5 | 416.5 | 174 | 342
669.3 | 450.3 | 222.6 | 348 | 426.5 | 176.3 | 343.8
670.3 | 451.3 | 222.9 | 348.7 | 421.2 | 178.2 | 344.6
671.3 | 452.3 | 223.1 | 348 | 420.4 | 179.9 | 345.1
672.3 | 453.3 | 223.4 | 346.9 | 422.3 | 181.3 | 344.9
673.3 | 454.3 | 223.7 | 348.8 | 424.8 | 182.8 | 346.4
674.3 | 455.3 | 223.9 | 349.1 | 422.2 | 184.5 | 347.9
675.3 | 456.3 | 224.2 | 349 | 420.8 | 186.3 | 348.3
676.3 | 457.3 | 224.5 | 348.6 | 414.4 | 187.9 | 348.6
677.3 | 458.3 | 224.7 | 353 | 425.4 | 190 | 351
678.3 | 459.3 | 225 | 352.7 | 423.7 | 191.9 | 351
679.3 | 460.3 | 225.3 | 350.8 | 414.1 | 193.2 | 350.6
680.3 | 461.3 | 225.6 | 348.8 | 408.5 | 194.4 | 350.4
681.3 | 462.3 | 225.8 | 348.2 | 408.8 | 195.6 | 351
682.3 | 463.3 | 226.1 | 347.2 | 405.4 | 196.6 | 350.8
683.3 | 464.3 | 226.4 | 348.3 | 401.7 | 197.9 | 351.6
684.3 | 465.3 | 226.7 | 349.7 | 401.7 | 199.3 | 352
685.3 | 466.3 | 226.9 | 347.8 | 397.2 | 200.2 | 351.9
686.3 | 467.3 | 227.2 | 344.5 | 391.6 | 201 | 351.2
687.3 | 468.3 | 227.5 | 341.5 | 388.2 | 201.5 | 350.5
688.3 | 469.3 | 227.8 | 340.1 | 383.5 | 202.1 | 350.6
689.3 | 470.3 | 228 | 336.5 | 376.2 | 202.6 | 350
690.3 | 471.3 | 228.3 | 333.3 | 371.5 | 202.9 | 349.2
691.3 | 472.3 | 228.5 | 329 | 365 | 202.8 | 347.9
692.3 | 473.3 | 228.8 | 324.4 | 359.2 | 202.6 | 346.7
693.3 | 474.3 | 229 | 321.4 | 355.5 | 202.6 | 346.2
694.3 | 475.3 | 229.3 | 319.2 | 353.1 | 202.8 | 345.7
695.3 | 476.3 | 229.5 | 315.7 | 347.4 | 202.8 | 344.7
696.3 | 477.3 | 229.7 | 311.9 | 343.7 | 202.7 | 343.4
697.3 | 478.3 | 229.9 | 309.5 | 340.9 | 202.6 | 342.7
698.3 | 479.3 | 230.1 | 306.5 | 339.1 | 202.5 | 341.6
699.3 | 480.3 | 230.3 | 302.9 | 334.1 | 202.1 | 340.5
700.3 | 481.3 | 230.6 | 300.8 | 331.8 | 201.8 | 339.7
701.3 | 482.3 | 230.8 | 299 | 330.4 | 201.8 | 339.2
702.3 | 483.3 | 231 | 300.3 | 331.6 | 202.3 | 340.2
703.3 | 484.3 | 231.2 | 306.1 | 335.9 | 203.6 | 342.4
704.3 | 485.3 | 231.4 | 310.3 | 337.7 | 205.1 | 343.1
705.3 | 486.3 | 231.6 | 307.5 | 332 | 205.3 | 341.5
706.3 | 487.3 | 231.8 | 309.5 | 338.3 | 205.9 | 342.1
707.3 | 488.3 | 231.9 | 311.5 | 342.1 | 207.1 | 341.7
708.3 | 489.3 | 232.1 | 309 | 338.9 | 207 | 340.6
709.3 | 490.3 | 232.3 | 307.7 | 337.7 | 207 | 340.4
710.3 | 491.3 | 232.5 | 306.1 | 337 | 206.8 | 339.7
711.3 | 492.3 | 232.7 | 306.9 | 342.4 | 206.9 | 339.5
712.3 | 493.3 | 232.8 | 306 | 338.4 | 207.1 | 338.7
713.3 | 494.3 | 233 | 304 | 336.2 | 206.8 | 337.8
714.3 | 495.3 | 233.2 | 302.2 | 333.8 | 206.8 | 337
715.3 | 496.3 | 233.4 | 300.8 | 333.3 | 206.7 | 336.2
716.3 | 497.3 | 233.5 | 299.7 | 333.8 | 206.6 | 336.2
717.3 | 498.3 | 233.7 | 298.1 | 329.7 | 206.7 | 335.9
718.3 | 499.3 | 233.8 | 295.7 | 324.9 | 206.5 | 335.2
719.3 | 500.3 | 234 | 293 | 320.6 | 206.2 | 334.1
720.3 | 501.3 | 234.2 | 289.8 | 317.9 | 205.6 | 332.8
721.3 | 502.3 | 234.3 | 289.6 | 316.6 | 205.5 | 332.8
722.3 | 503.3 | 234.5 | 288.7 | 316.2 | 205.2 | 332
723.3 | 504.3 | 234.7 | 287.8 | 316.5 | 205 | 331.3
724.3 | 505.3 | 234.8 | 290.1 | 319 | 205.5 | 331.6
725.3 | 506.3 | 235 | 291.8 | 322 | 206.3 | 332.3
726.3 | 507.3 | 235.2 | 293.7 | 324.4 | 206.9 | 332.6
727.3 | 508.3 | 235.3 | 294.7 | 326 | 207.4 | 332.5
728.3 | 509.3 | 235.5 | 293.4 | 324.8 | 207.7 | 331.8
729.3 | 510.3 | 235.7 | 292.4 | 322.6 | 207.8 | 331.4
730.3 | 511.3 | 235.9 | 292.9 | 326.3 | 208.1 | 331.3
731.3 | 512.3 | 236 | 297.3 | 329.5 | 209.2 | 332.4
732.3 | 513.3 | 236.2 | 299.6 | 329.6 | 210.5 | 334.8
733.3 | 514.3 | 236.4 | 303.9 | 333.1 | 212.4 | 337
734.3 | 515.3 | 236.5 | 307.3 | 333.6 | 214 | 337.8
735.3 | 516.3 | 236.7 | 309.5 | 336.6 | 215.1 | 338
736.3 | 517.3 | 236.9 | 312.9 | 338.6 | 215.9 | 339.3
737.3 | 518.3 | 237.1 | 315.9 | 345.5 | 216.9 | 340
738.3 | 519.3 | 237.3 | 316.7 | 350 | 217.6 | 339.7
739.3 | 520.3 | 237.5 | 314.9 | 346.6 | 217.6 | 338.4
740.3 | 521.3 | 237.7 | 314.3 | 345.4 | 217.5 | 338.1
741.3 | 522.3 | 237.9 | 314.9 | 347.9 | 217.9 | 338.8
742.3 | 523.3 | 238.1 | 313.8 | 342.8 | 218.3 | 338.6
743.3 | 524.3 | 238.3 | 312.8 | 339.7 | 218.7 | 338.6
744.3 | 525.3 | 238.5 | 312.4 | 339.6 | 218.8 | 338.1
745.3 | 526.3 | 238.7 | 315.2 | 347.1 | 220 | 338.6
746.3 | 527.3 | 238.9 | 323.2 | 371.6 | 222.3 | 341.7
747.3 | 528.3 | 239.1 | 330.7 | 385.8 | 225.4 | 342.9
748.3 | 529.3 | 239.3 | 330.5 | 388.1 | 226.1 | 343.2
749.3 | 530.3 | 239.5 | 337.1 | 395.4 | 228.6 | 346.7
750.3 | 531.3 | 239.7 | 342.4 | 395.2 | 230.4 | 348.2
751.3 | 532.3 | 239.9 | 344.3 | 387.2 | 231.9 | 348.9
752.3 | 533.3 | 240.2 | 345.4 | 387.5 | 232.9 | 351.7
753.3 | 534.3 | 240.4 | 350.9 | 388.8 | 234.8 | 353.8
754.3 | 535.3 | 240.6 | 351 | 381.1 | 235.4 | 353.4
755.3 | 536.3 | 240.9 | 351.4 | 378.7 | 235.8 | 353.9
756.3 | 537.3 | 241.1 | 355.6 | 382.9 | 237.4 | 355.6
757.3 | 538.3 | 241.4 | 358 | 395.1 | 239.2 | 357.4
758.3 | 539.3 | 241.6 | 363.3 | 403.1 | 241.6 | 359.3
759.3 | 540.3 | 241.9 | 362.4 | 401.3 | 242.5 | 358.8
760.3 | 541.3 | 242.1 | 360.4 | 395.9 | 242.6 | 358
761.3 | 542.3 | 242.4 | 354.6 | 387.2 | 241.5 | 356.5
762.3 | 543.3 | 242.6 | 348.3 | 378.5 | 240.2 | 355.1
763.3 | 544.3 | 242.9 | 345.1 | 377.7 | 239.4 | 354.7
764.3 | 545.3 | 243.2 | 343 | 375.8 | 239 | 354
765.3 | 546.3 | 243.4 | 340 | 369.9 | 238.5 | 354.1
766.3 | 547.3 | 243.7 | 336.8 | 363.8 | 237.9 | 353.3
767.3 | 548.3 | 243.9 | 333.2 | 360.7 | 237.3 | 352.5
768.3 | 549.3 | 244.1 | 330.3 | 357.2 | 237 | 351.9
769.3 | 550.3 | 244.3 | 327 | 350.1 | 236.6 | 351
770.3 | 551.3 | 244.5 | 322.6 | 344.4 | 235.5 | 349.7
771.3 | 552.3 | 244.7 | 319.8 | 342.3 | 234.6 | 349
772.3 | 553.3 | 244.8 | 317.8 | 340.9 | 234.2 | 348.5
773.3 | 554.3 | 245 | 317.6 | 341.1 | 234.4 | 348.4
774.3 | 555.3 | 245.2 | 321.8 | 343 | 235.7 | 349.4
775.3 | 556.3 | 245.4 | 323.3 | 342.7 | 236.9 | 349.7
776.3 | 557.3 | 245.5 | 321.8 | 339.3 | 236.5 | 349.1
777.3 | 558.3 | 245.7 | 319.2 | 335 | 236.1 | 348.4
778.3 | 559.3 | 245.8 | 317.9 | 331.7 | 235.7 | 347.8
779.3 | 560.3 | 246 | 319.7 | 335.1 | 237 | 348.6
780.3 | 561.3 | 246.1 | 317.6 | 333 | 236.8 | 347.7
781.3 | 562.3 | 246.3 | 316.4 | 331.3 | 236.6 | 347.2
782.3 | 563.3 | 246.5 | 315.5 | 329.8 | 236.8 | 346.7
783.3 | 564.3 | 246.7 | 316.8 | 338 | 237.8 | 347.1
784.3 | 565.3 | 246.9 | 316.3 | 336.6 | 237.9 | 346.8
785.3 | 566.3 | 247.1 | 319.6 | 340 | 238.7 | 347.6
786.3 | 567.3 | 247.3 | 321.4 | 341.5 | 239.5 | 347.8
787.3 | 568.3 | 247.6 | 321.3 | 337.8 | 239.9 | 347.1
788.3 | 569.3 | 248 | 319.3 | 334.9 | 239.5 | 346.1
789.3 | 570.3 | 248.3 | 316.1 | 332.6 | 238.7 | 345.2
790.3 | 571.3 | 248.6 | 313.8 | 329.3 | 238 | 344.7
791.3 | 572.3 | 248.9 | 313.4 | 327.6 | 237.9 | 344.3
792.3 | 573.3 | 249 | 313.3 | 328 | 237.5 | 344.4
793.3 | 574.3 | 249.2 | 311.8 | 325.9 | 237 | 344
794.3 | 575.3 | 249.4 | 312.7 | 324.7 | 237.6 | 344.8
795.3 | 576.3 | 249.5 | 316.3 | 332.4 | 239.4 | 345.4
796.3 | 577.3 | 249.7 | 320.5 | 347.9 | 241.7 | 347.3
797.3 | 578.3 | 250 | 322.4 | 357 | 243.4 | 347.7
798.3 | 579.3 | 250.2 | 324.1 | 365.7 | 244.6 | 348.6
799.3 | 580.3 | 250.4 | 330.3 | 379.5 | 248.5 | 351.6
800.3 | 581.3 | 250.6 | 332.5 | 390.4 | 250 | 351.2
801.3 | 582.3 | 250.8 | 334.5 | 397.1 | 251.2 | 351.3
802.3 | 583.3 | 250.9 | 334.1 | 398.3 | 251.3 | 351.7
803.3 | 584.3 | 251.2 | 333.7 | 398.5 | 251.4 | 351.8
804.3 | 585.3 | 251.4 | 335.1 | 402.3 | 252.5 | 352.4
805.3 | 586.3 | 251.7 | 336.3 | 400.9 | 254.3 | 353.8
806.3 | 587.3 | 252 | 336.9 | 399.8 | 255.4 | 354.4
807.3 | 588.3 | 252.2 | 338.1 | 400.3 | 256.9 | 354.5
808.3 | 589.3 | 252.3 | 342 | 409.3 | 259.3 | 356.3
809.3 | 590.3 | 252.5 | 342.8 | 408.5 | 260 | 356.5
810.3 | 591.3 | 252.7 | 343.7 | 407.5 | 260.5 | 356.8
811.3 | 592.3 | 252.9 | 340.4 | 397.4 | 259.5 | 355.8
812.3 | 593.3 | 253 | 336.3 | 389.1 | 257.7 | 354.6
813.3 | 594.3 | 253.2 | 333.3 | 384.3 | 256.3 | 353.9
814.3 | 595.3 | 253.4 | 333.1 | 384.7 | 256.7 | 355
815.3 | 596.3 | 253.6 | 332.6 | 382.8 | 256.8 | 354.8
816.3 | 597.3 | 253.7 | 335 | 383.7 | 257.3 | 355.4
817.3 | 598.3 | 253.9 | 334.9 | 382.5 | 257.2 | 355.4
818.3 | 599.3 | 254.1 | 335.1 | 386.4 | 257.3 | 355.6
819.3 | 600.3 | 254.3 | 339.5 | 403.5 | 258.8 | 356.7
820.3 | 601.3 | 254.5 | 342.8 | 406.7 | 260.6 | 357.6
821.3 | 602.3 | 254.6 | 346.9 | 415.2 | 262.5 | 358.6
822.3 | 603.3 | 254.8 | 348.2 | 415.7 | 263.8 | 358.8
823.3 | 604.3 | 255 | 345.3 | 408.1 | 263.1 | 358.1
824.3 | 605.3 | 255.2 | 343.7 | 406 | 263.4 | 358
825.3 | 606.3 | 255.4 | 343.1 | 409.8 | 263.2 | 358
826.3 | 607.3 | 255.7 | 346.3 | 413.3 | 265.3 | 360
827.3 | 608.3 | 256 | 351.6 | 424.7 | 268.1 | 361.5
828.3 | 609.3 | 256.3 | 356.8 | 439.1 | 271 | 363.3
829.3 | 610.3 | 256.6 | 359.3 | 444.2 | 272.7 | 364.8
830.3 | 611.3 | 256.9 | 361.5 | 442.2 | 274.3 | 365.4
831.3 | 612.3 | 257.1 | 365 | 444.1 | 276.9 | 366.3
832.3 | 613.3 | 257.4 | 363.3 | 442.9 | 276.4 | 365.9
833.3 | 614.3 | 257.7 | 363.8 | 442.5 | 277 | 366.6
834.3 | 615.3 | 257.9 | 363.5 | 436.3 | 277.7 | 367.6
835.3 | 616.3 | 258.2 | 363.1 | 431.9 | 277.9 | 368.3
836.3 | 617.3 | 258.4 | 364.9 | 435.4 | 279 | 368.9
837.3 | 618.3 | 258.5 | 366.6 | 439.5 | 280.2 | 370.6
838.3 | 619.3 | 258.7 | 368.2 | 438 | 281.5 | 371.7
839.3 | 620.3 | 258.9 | 367.5 | 438.9 | 281.8 | 372.1
840.3 | 621.3 | 259.1 | 368.6 | 440.2 | 283.9 | 373.4
841.3 | 622.3 | 259.4 | 370.7 | 447.2 | 286.1 | 375.8
842.3 | 623.3 | 259.6 | 371.7 | 445.8 | 287.3 | 376.1
843.3 | 624.3 | 259.8 | 367.6 | 434.2 | 285.6 | 374.8
844.3 | 625.3 | 260 | 363.3 | 428.9 | 283.9 | 373.8
845.3 | 626.3 | 260.2 | 358.5 | 419.1 | 281.8 | 372.5
846.3 | 627.3 | 260.4 | 354.4 | 412 | 279.7 | 371.9
847.3 | 628.3 | 260.6 | 351.8 | 410.9 | 278.3 | 371.7
848.3 | 629.3 | 260.8 | 351.6 | 418.2 | 278.6 | 372
849.3 | 630.3 | 261 | 355.4 | 436.3 | 280.8 | 373.6
850.3 | 631.3 | 261.2 | 358.9 | 451.2 | 282.9 | 374.9
851.3 | 632.3 | 261.5 | 360.9 | 456 | 284.9 | 375.9
852.3 | 633.3 | 261.7 | 365.4 | 465.6 | 288.4 | 377.9
853.3 | 634.3 | 261.9 | 369.7 | 475.8 | 291.9 | 379.7
854.3 | 635.3 | 262.2 | 379.1 | 498.3 | 298.4 | 382.4
855.3 | 636.3 | 262.4 | 385.3 | 512 | 302.5 | 383.5
856.3 | 637.3 | 262.7 | 385.3 | 517.3 | 304.1 | 384.6
857.3 | 638.3 | 262.9 | 383.9 | 510.4 | 304.8 | 385.6
858.3 | 639.3 | 263.1 | 382.3 | 511.9 | 304.3 | 385.2
859.3 | 640.3 | 263.4 | 380.7 | 504.7 | 303.7 | 387
860.3 | 641.3 | 263.6 | 380.9 | 491.2 | 304.2 | 388.7
861.3 | 642.3 | 263.9 | 380.4 | 482.4 | 304.5 | 389.5
862.3 | 643.3 | 264.1 | 382.2 | 482 | 305.7 | 392
863.3 | 644.3 | 264.4 | 385.6 | 484.8 | 308.6 | 393.6
864.3 | 645.3 | 264.6 | 383.4 | 480.3 | 307.4 | 392.7
865.3 | 646.3 | 264.9 | 379.7 | 473.2 | 304.9 | 391.7
866.3 | 647.3 | 265.2 | 377 | 475.7 | 303.1 | 391.6
867.3 | 648.3 | 265.4 | 381.3 | 492.8 | 306 | 394.1
868.3 | 649.3 | 265.7 | 388.8 | 507.4 | 310.9 | 396.4
869.3 | 650.3 | 266 | 388.3 | 493.7 | 311.5 | 397.1
870.3 | 651.3 | 266.2 | 389.4 | 493 | 312.7 | 398.9
871.3 | 652.3 | 266.5 | 387.8 | 476.2 | 312 | 399.4
872.3 | 653.3 | 266.7 | 386.9 | 463.4 | 312 | 400.7
873.3 | 654.3 | 267 | 384.6 | 453.4 | 311.6 | 400.3
874.3 | 655.3 | 267.2 | 382.3 | 449.5 | 310.7 | 399.7
875.3 | 656.3 | 267.5 | 383.6 | 461.3 | 311.6 | 400.5
876.3 | 657.3 | 267.7 | 382.2 | 457 | 311.4 | 400.1
877.3 | 658.3 | 268 | 380.8 | 457.4 | 310.8 | 399.8
878.3 | 659.3 | 268.3 | 384.2 | 465.7 | 312.6 | 401.6
879.3 | 660.3 | 268.5 | 384.6 | 462.5 | 313 | 402.7
880.3 | 661.3 | 268.7 | 384.2 | 465.3 | 312.7 | 403.4
881.3 | 662.3 | 268.9 | 381.4 | 462.5 | 311.1 | 401.9
882.3 | 663.3 | 269.2 | 378.8 | 454.8 | 309.3 | 401
883.3 | 664.3 | 269.4 | 377.5 | 452.4 | 308.8 | 401.4
884.3 | 665.3 | 269.7 | 375 | 441.3 | 308 | 401.1
885.3 | 666.3 | 269.9 | 375.5 | 443.1 | 308.2 | 401.9
886.3 | 667.3 | 270.2 | 374.6 | 435.9 | 308.5 | 402.2
887.3 | 668.3 | 270.5 | 373.1 | 428.7 | 308.7 | 402.1
888.3 | 669.3 | 270.7 | 370.6 | 422.3 | 307.4 | 401.6
889.3 | 670.3 | 270.9 | 368.4 | 417.2 | 306.8 | 401.1
890.3 | 671.3 | 271.1 | 364.8 | 409.8 | 305.5 | 400.4
891.3 | 672.3 | 271.4 | 361.5 | 405.6 | 303.8 | 399.5
892.3 | 673.3 | 271.6 | 357.7 | 399.4 | 301.8 | 398.4
893.3 | 674.3 | 271.8 | 353.6 | 390.5 | 299.6 | 397.7
894.3 | 675.3 | 272 | 349.3 | 381.9 | 297.4 | 396.5
895.3 | 676.3 | 272.3 | 344.7 | 374.3 | 294.8 | 395
896.3 | 677.3 | 272.5 | 340.1 | 367.3 | 292.4 | 394
897.3 | 678.3 | 272.7 | 336.9 | 365.1 | 291.2 | 393.5
898.3 | 679.3 | 272.9 | 335.9 | 366.7 | 291.2 | 393.2
899.3 | 680.3 | 273.1 | 334.2 | 363.8 | 290.3 | 392.3
900.3 | 681.3 | 273.4 | 332.4 | 362.9 | 288.9 | 391.2
901.3 | 682.3 | 273.6 | 330.7 | 362.1 | 287.7 | 390.1
902.3 | 683.3 | 273.9 | 330.7 | 365.4 | 288.2 | 390.4
903.3 | 684.3 | 274.1 | 332.9 | 372.2 | 288.8 | 390.4
904.3 | 685.3 | 274.4 | 334.4 | 374.3 | 289.7 | 390.5
905.3 | 686.3 | 274.6 | 336.4 | 377.2 | 290.4 | 390.5
906.3 | 687.3 | 274.8 | 338.1 | 382.2 | 291.6 | 391.3
907.3 | 688.3 | 275 | 337.2 | 380.9 | 291 | 390.9
908.3 | 689.3 | 275.3 | 341.2 | 388.5 | 293 | 392.4
909.3 | 690.3 | 275.5 | 346.1 | 393.3 | 294.7 | 394.3
910.3 | 691.3 | 275.7 | 352.7 | 411.7 | 297.5 | 395.6
911.3 | 692.3 | 275.8 | 355.8 | 421.9 | 299.4 | 396.7
912.3 | 693.3 | 276 | 361.6 | 430.8 | 301.8 | 399.6
913.3 | 694.3 | 276.2 | 362.7 | 437.1 | 303.6 | 399.8
914.3 | 695.3 | 276.4 | 364.6 | 439.5 | 305.2 | 400.9
915.3 | 696.3 | 276.6 | 364 | 430.4 | 305.5 | 401.5
916.3 | 697.3 | 276.9 | 362 | 424.3 | 304.6 | 400.7
917.3 | 698.3 | 277.1 | 359 | 417.6 | 302.6 | 399.8
918.3 | 699.3 | 277.3 | 355.9 | 408.9 | 300.5 | 398.3
919.3 | 700.3 | 277.6 | 351.7 | 402.5 | 298 | 397.3
920.3 | 701.3 | 277.8 | 349 | 397.2 | 296.5 | 396.3
921.3 | 702.3 | 278 | 344.4 | 387.4 | 294.2 | 395.1
922.3 | 703.3 | 278.2 | 341.4 | 382.3 | 292.4 | 394
923.3 | 704.3 | 278.5 | 339.3 | 381.1 | 291.6 | 393
924.3 | 705.3 | 278.7 | 342.1 | 387.6 | 293.1 | 395
925.3 | 706.3 | 278.9 | 345.1 | 400 | 295.3 | 395.4
926.3 | 707.3 | 279.1 | 350.6 | 401.7 | 298.4 | 399
927.3 | 708.3 | 279.3 | 353.5 | 403.6 | 300.3 | 400
928.3 | 709.3 | 279.5 | 355 | 404.7 | 301.4 | 401.9
929.3 | 710.3 | 279.8 | 356.1 | 405.3 | 302.5 | 402
930.3 | 711.3 | 280 | 356.2 | 404.9 | 302.8 | 401.4
931.3 | 712.3 | 280.3 | 354 | 399.7 | 301.5 | 400.5
932.3 | 713.3 | 280.5 | 354.6 | 399.9 | 301.8 | 401
933.3 | 714.3 | 280.8 | 356.9 | 397.9 | 303.4 | 402.5
934.3 | 715.3 | 281 | 356.9 | 398.3 | 303.3 | 402.3
935.3 | 716.3 | 281.3 | 357.5 | 396.5 | 303.6 | 402.5
936.3 | 717.3 | 281.6 | 357.7 | 400.3 | 303.9 | 403.1
937.3 | 718.3 | 281.8 | 357.4 | 398.4 | 304 | 403.1
938.3 | 719.3 | 282 | 359.5 | 401.7 | 305.1 | 404.7
939.3 | 720.3 | 282.3 | 360.8 | 398.8 | 305.8 | 404.9
940.3 | 721.3 | 282.5 | 357.5 | 391.9 | 303.9 | 403.5
941.3 | 722.3 | 282.7 | 354.3 | 387.7 | 301.7 | 402.4
942.3 | 723.3 | 283 | 350.7 | 381.4 | 299.9 | 401.2
943.3 | 724.3 | 283.2 | 347 | 377.3 | 297.9 | 399.8
944.3 | 725.3 | 283.4 | 343.8 | 373.3 | 296.4 | 398.3
945.3 | 726.3 | 283.7 | 343.3 | 375.6 | 296.1 | 398.7
946.3 | 727.3 | 283.9 | 347 | 388.5 | 297.9 | 400.1
947.3 | 728.3 | 284.2 | 350.7 | 396.9 | 299.9 | 401.5
948.3 | 729.3 | 284.4 | 352.6 | 393.5 | 300.2 | 402.3
949.3 | 730.3 | 284.7 | 354.8 | 392.4 | 301.3 | 403.2
950.3 | 731.3 | 284.9 | 357.5 | 393.1 | 302.2 | 403.7
951.3 | 732.3 | 285.1 | 356.4 | 392.8 | 301.8 | 402.7
952.3 | 733.3 | 285.3 | 355.9 | 390.8 | 301.2 | 402.7
953.3 | 734.3 | 285.6 | 356.9 | 392.6 | 301.1 | 401.9
954.3 | 735.3 | 285.8 | 357.7 | 391.8 | 301.1 | 401.4
955.3 | 736.3 | 286 | 357.6 | 399.7 | 300.8 | 401.1
956.3 | 737.3 | 286.3 | 359.7 | 412.5 | 301.9 | 402.1
957.3 | 738.3 | 286.5 | 364.4 | 434.1 | 304 | 404
958.3 | 739.3 | 286.7 | 368.9 | 446.8 | 307.2 | 405
959.3 | 740.3 | 287 | 367.6 | 435.7 | 306.3 | 405
960.3 | 741.3 | 287.2 | 366.8 | 435.8 | 306.7 | 405.5
961.3 | 742.3 | 287.5 | 366.2 | 431.9 | 306.5 | 405.2
962.3 | 743.3 | 287.7 | 366.5 | 432.3 | 306.7 | 405.6
963.3 | 744.3 | 288 | 366 | 429.2 | 306.9 | 405.6
964.3 | 745.3 | 288.3 | 363.9 | 435.1 | 306.1 | 404.7
965.3 | 746.3 | 288.5 | 362.7 | 432.6 | 306 | 404.5
966.3 | 747.3 | 288.8 | 360 | 425 | 304.5 | 403.4
967.3 | 748.3 | 289.1 | 357.1 | 417.3 | 302.7 | 402.3
968.3 | 749.3 | 289.4 | 356 | 410.5 | 302.2 | 401.9
969.3 | 750.3 | 289.6 | 355.3 | 410.8 | 301.8 | 401.8
970.3 | 751.3 | 289.9 | 354 | 406.4 | 301.2 | 400.6
971.3 | 752.3 | 290.1 | 352.4 | 406.5 | 300.3 | 400.6
972.3 | 753.3 | 290.4 | 351.3 | 403.5 | 300.5 | 399.8
973.3 | 754.3 | 290.6 | 348.8 | 403.4 | 298.9 | 398.8
974.3 | 755.3 | 290.9 | 347.6 | 399.9 | 298.1 | 398
975.3 | 756.3 | 291.2 | 347.7 | 402.3 | 298 | 398.1
976.3 | 757.3 | 291.4 | 351.9 | 406.5 | 299.8 | 399.3
977.3 | 758.3 | 291.7 | 357.5 | 423.6 | 302.2 | 401
978.3 | 759.3 | 291.9 | 362.1 | 429.5 | 304.3 | 402.3
979.3 | 760.3 | 292.2 | 362.8 | 426.5 | 305 | 402.1
980.3 | 761.3 | 292.4 | 368.5 | 432.8 | 307.6 | 404.3
981.3 | 762.3 | 292.7 | 371.1 | 431.4 | 309.1 | 405.5
982.3 | 763.3 | 292.9 | 372 | 430.2 | 310.2 | 406
983.3 | 764.3 | 293.2 | 369.2 | 422.9 | 308.8 | 404.9
984.3 | 765.3 | 293.4 | 367.9 | 419.3 | 308.4 | 404.6
985.3 | 766.3 | 293.7 | 364.6 | 413.6 | 307.1 | 403
986.3 | 767.3 | 294 | 360.7 | 408.8 | 305.1 | 401.7
987.3 | 768.3 | 294.2 | 359.9 | 410.4 | 305 | 402.4
988.3 | 769.3 | 294.5 | 360.1 | 409.1 | 305.4 | 402.7
989.3 | 770.3 | 294.8 | 359.6 | 409.5 | 305.4 | 402.2
990.3 | 771.3 | 295 | 362 | 424.4 | 306.9 | 404.1
991.3 | 772.3 | 295.3 | 369 | 439.7 | 311.3 | 406.9
992.3 | 773.3 | 295.6 | 379 | 464.6 | 315.8 | 410.7
993.3 | 774.3 | 295.8 | 389.5 | 496.2 | 321.3 | 414.8
994.3 | 775.3 | 296.1 | 397.2 | 508.1 | 326.2 | 419.5
995.3 | 776.3 | 296.4 | 400.9 | 497.6 | 328.6 | 422
996.3 | 777.3 | 296.7 | 400.2 | 494.4 | 330 | 422.7
997.3 | 778.3 | 297 | 401 | 500.9 | 330.6 | 423.5
998.3 | 779.3 | 297.2 | 401.3 | 494.8 | 331.4 | 425.2
999.3 | 780.3 | 297.5 | 403.3 | 489.9 | 332.4 | 427.1
1000.3 | 781.3 | 297.8 | 404.7 | 487.7 | 333.3 | 428.4
1001.3 | 782.3 | 298.1 | 407.7 | 485.4 | 335.3 | 431
1002.3 | 783.3 | 298.4 | 404.2 | 474.6 | 333.9 | 429.2
1003.3 | 784.3 | 298.7 | 399.4 | 460.8 | 332 | 428.2
1004.3 | 785.3 | 299 | 393.1 | 448.4 | 329.3 | 425.9
1005.3 | 786.3 | 299.3 | 388.6 | 442.2 | 326.8 | 424.6
1006.3 | 787.3 | 299.7 | 387 | 436.7 | 325.8 | 424.6
1007.3 | 788.3 | 300 | 386.2 | 433.7 | 325.8 | 425.1
1008.3 | 789.3 | 300.2 | 385.8 | 436.9 | 325.8 | 425.3
1009.3 | 790.3 | 300.5 | 385.4 | 437.2 | 325.1 | 425.6
1010.3 | 791.3 | 300.7 | 384 | 431.7 | 324.7 | 424.9
1011.3 | 792.3 | 301 | 381 | 428.6 | 323.1 | 423.7
1012.3 | 793.3 | 301.4 | 378.9 | 429.1 | 322 | 423.2
1013.3 | 794.3 | 301.7 | 377.2 | 434.2 | 321.2 | 423
1014.3 | 795.3 | 302.1 | 373.2 | 426.9 | 319.4 | 421.2
1015.3 | 796.3 | 302.4 | 369.2 | 418.9 | 317.5 | 419.4
1016.3 | 797.3 | 302.7 | 365.3 | 410.5 | 315.6 | 418.1
1017.3 | 798.3 | 303.1 | 362 | 415.3 | 314 | 417.5
1018.3 | 799.3 | 303.4 | 359.6 | 410.7 | 312.6 | 416.1
1019.3 | 800.3 | 303.7 | 356.1 | 403.9 | 310.6 | 414.5
1020.3 | 801.3 | 304 | 357.9 | 408.3 | 311.4 | 416.1
1021.3 | 802.3 | 304.4 | 360.9 | 413.6 | 313.3 | 417.3
1022.3 | 803.3 | 304.7 | 363.8 | 414.9 | 315.3 | 418.6
1023.3 | 804.3 | 305 | 363.2 | 410 | 314.6 | 417.5
1024.3 | 805.3 | 305.3 | 360.9 | 403.8 | 313 | 416
1025.3 | 806.3 | 305.6 | 359.4 | 406.1 | 312.2 | 415.8
1026.3 | 807.3 | 305.9 | 356.9 | 399.6 | 311.2 | 414.7
1027.3 | 808.3 | 306.2 | 354.7 | 397.8 | 310.2 | 414.4
1028.3 | 809.3 | 306.4 | 355.8 | 406.5 | 310.4 | 414.8
1029.3 | 810.3 | 306.7 | 358.8 | 413.4 | 311.6 | 415.9
1030.3 | 811.3 | 307 | 366.4 | 428.7 | 315.5 | 419.7
1031.3 | 812.3 | 307.3 | 373.4 | 429.9 | 319.7 | 423
1032.3 | 813.3 | 307.6 | 371.3 | 422.2 | 319.1 | 421
1033.3 | 814.3 | 307.9 | 368.5 | 413.8 | 317.9 | 419.3
1034.3 | 815.3 | 308.2 | 365.9 | 407.7 | 316.4 | 418.8
1035.3 | 816.3 | 308.5 | 365.9 | 410.6 | 316.4 | 418.2
1036.3 | 817.3 | 308.7 | 364.2 | 407.1 | 315.9 | 417.9
1037.3 | 818.3 | 309 | 364.1 | 406.7 | 315.4 | 417.4
1038.3 | 819.3 | 309.3 | 365 | 411.5 | 315.6 | 417.4
1039.3 | 820.3 | 309.6 | 362.1 | 404.7 | 314 | 415.7
1040.3 | 821.3 | 309.8 | 360.8 | 403.5 | 312.7 | 415
1041.3 | 822.3 | 310.1 | 360 | 400.2 | 312.3 | 414.2
1042.3 | 823.3 | 310.4 | 357.2 | 393.4 | 310.7 | 412.9
1043.3 | 824.3 | 310.7 | 355.5 | 391.7 | 309.9 | 412.3
1044.3 | 825.3 | 310.9 | 351.3 | 384.3 | 307.9 | 410.3
1045.3 | 826.3 | 311.2 | 347.5 | 380.4 | 305.8 | 408.8
1046.3 | 827.3 | 311.5 | 344.5 | 374.7 | 304.7 | 407.4
1047.3 | 828.3 | 311.8 | 341.2 | 368.4 | 303.1 | 405.7
1048.3 | 829.3 | 312 | 340.8 | 367.2 | 302.8 | 405.5
1049.3 | 830.3 | 312.3 | 341.9 | 374.5 | 303.5 | 406.4
1050.3 | 831.3 | 312.6 | 344.4 | 374.3 | 304.8 | 406.9
1051.3 | 832.3 | 312.9 | 343.4 | 368.9 | 304.4 | 405.7
1052.3 | 833.3 | 313.1 | 343.1 | 366.9 | 304.1 | 405.4
1053.3 | 834.3 | 313.4 | 342.5 | 364.4 | 303.6 | 404.6
1054.3 | 835.3 | 313.6 | 341.5 | 363.6 | 302.7 | 403.7
1055.3 | 836.3 | 313.9 | 338.3 | 359.8 | 301.1 | 402.2
1056.3 | 837.3 | 314.1 | 335 | 355.4 | 299.4 | 400.7
1057.3 | 838.3 | 314.4 | 333.6 | 355.6 | 298.6 | 400.2
1058.3 | 839.3 | 314.6 | 332.1 | 353.4 | 297.6 | 399.5
1059.3 | 840.3 | 314.8 | 331.1 | 354.5 | 297.4 | 399.2
1060.3 | 841.3 | 315.1 | 334.7 | 361.9 | 298.4 | 399.9
1061.3 | 842.3 | 315.3 | 335.9 | 363.7 | 298.9 | 399.8
1062.3 | 843.3 | 315.5 | 337.8 | 363.3 | 299.6 | 400
1063.3 | 844.3 | 315.8 | 339.1 | 368.4 | 299.8 | 399.8
1064.3 | 845.3 | 316 | 338.9 | 372.4 | 299.9 | 399.5
1065.3 | 846.3 | 316.2 | 341.5 | 386.6 | 301.4 | 400.5
1066.3 | 847.3 | 316.4 | 341 | 384.6 | 301.1 | 398.8
1067.3 | 848.3 | 316.6 | 339.5 | 383.5 | 299.8 | 397.8
1068.3 | 849.3 | 316.8 | 338.5 | 381.8 | 298.8 | 397.1
1069.3 | 850.3 | 317 | 336.5 | 376.6 | 297.9 | 396.1
1070.3 | 851.3 | 317.2 | 336.7 | 384.4 | 298.4 | 396.6
1071.3 | 852.3 | 317.5 | 338.6 | 387.5 | 299.8 | 397.4
1072.3 | 853.3 | 317.7 | 342.6 | 399 | 301.6 | 398.4
1073.3 | 854.3 | 317.9 | 346.9 | 403.5 | 304.3 | 399.4
1074.3 | 855.3 | 318.1 | 343.1 | 391.5 | 302.2 | 397.3
1075.3 | 856.3 | 318.4 | 340.9 | 386.6 | 301.1 | 396.9
1076.3 | 857.3 | 318.6 | 341.3 | 387.6 | 301.2 | 397.1
1077.3 | 858.3 | 318.8 | 342.5 | 394.1 | 301.5 | 397
1078.3 | 859.3 | 319 | 345.5 | 399.5 | 302.4 | 397.5
1079.3 | 860.3 | 319.2 | 351.8 | 414.1 | 304.5 | 399.1
1080.3 | 861.3 | 319.4 | 357 | 426.6 | 306.7 | 401
1081.3 | 862.3 | 319.6 | 361.2 | 428.4 | 308.5 | 403.1
1082.3 | 863.3 | 319.8 | 366.9 | 438.1 | 311.7 | 404.7
1083.3 | 864.3 | 320 | 369.1 | 440.8 | 313 | 405.6
1084.3 | 865.3 | 320.2 | 373.4 | 447 | 315.6 | 408
1085.3 | 866.3 | 320.5 | 374.4 | 441 | 316.9 | 410.1
1086.3 | 867.3 | 320.7 | 372.7 | 433.4 | 316.7 | 409.9
1087.3 | 868.3 | 320.9 | 371.9 | 435.2 | 317.4 | 410.9
1088.3 | 869.3 | 321.2 | 370.8 | 433.6 | 317.2 | 410.6
1089.3 | 870.3 | 321.3 | 369.6 | 432.5 | 316.7 | 409.9
1090.3 | 871.3 | 321.5 | 368.6 | 434.5 | 316.5 | 409.5
1091.3 | 872.3 | 321.7 | 365.8 | 427.5 | 315 | 408.1
1092.3 | 873.3 | 321.9 | 365.1 | 424 | 314.5 | 408.3
1093.3 | 874.3 | 322.1 | 364.9 | 418.3 | 314.6 | 408.3
1094.3 | 875.3 | 322.4 | 365.5 | 420.8 | 315.6 | 408.7
1095.3 | 876.3 | 322.6 | 367.3 | 424.2 | 316.6 | 409.2
1096.3 | 877.3 | 322.9 | 364.6 | 415.1 | 314.8 | 407.4
1097.3 | 878.3 | 323.1 | 360.4 | 409 | 312.8 | 405.9
1098.3 | 879.3 | 323.4 | 357 | 404.1 | 311.2 | 404.9
1099.3 | 880.3 | 323.6 | 353.4 | 398 | 309.6 | 404.2
1100.3 | 881.3 | 323.8 | 349.5 | 390.4 | 307.6 | 402.5
1101.3 | 882.3 | 324 | 344.6 | 381.2 | 305.4 | 400.5
1102.3 | 883.3 | 324.2 | 339.3 | 373.2 | 303.1 | 399.1
1103.3 | 884.3 | 324.4 | 334.6 | 365.5 | 301 | 397.5
1104.3 | 885.3 | 324.7 | 330.8 | 359.5 | 299.4 | 396.2
1105.3 | 886.3 | 324.9 | 329 | 357.3 | 298.4 | 395.6
1106.3 | 887.3 | 325.1 | 327.1 | 351.8 | 297.3 | 394.3
1107.3 | 888.3 | 325.3 | 328.3 | 355.5 | 297.4 | 394.8
1108.3 | 889.3 | 325.5 | 338.3 | 376.4 | 301.6 | 398.8
1109.3 | 890.3 | 325.7 | 342.1 | 385.6 | 303.2 | 399.5
1110.3 | 891.3 | 326 | 345.7 | 382.9 | 305 | 400.6
1111.3 | 892.3 | 326.2 | 349.4 | 385.1 | 306.4 | 402.2
1112.3 | 893.3 | 326.4 | 357.6 | 404.6 | 311.3 | 407.2
1113.3 | 894.3 | 326.6 | 359.9 | 402.4 | 312.7 | 407
1114.3 | 895.3 | 326.8 | 364.2 | 406.1 | 314.5 | 408.3
1115.3 | 896.3 | 327 | 361.6 | 397.6 | 313.3 | 406.2
1116.3 | 897.3 | 327.1 | 360.2 | 395.3 | 312.2 | 405.4
1117.3 | 898.3 | 327.4 | 357.8 | 392.8 | 311 | 404.4
1118.3 | 899.3 | 327.5 | 355.2 | 393.5 | 309.6 | 403.3
1119.3 | 900.3 | 327.7 | 354.3 | 395.5 | 309.5 | 403.1
1120.3 | 901.3 | 327.9 | 355.9 | 399.5 | 310 | 404.1
1121.3 | 902.3 | 328.1 | 356.9 | 398.3 | 310.9 | 404.3
1122.3 | 903.3 | 328.2 | 356.2 | 393.7 | 310.2 | 403.5
1123.3 | 904.3 | 328.4 | 360.4 | 408.4 | 312.2 | 405.3
1124.3 | 905.3 | 328.6 | 364.6 | 405.6 | 314.3 | 406.9
1125.3 | 906.3 | 328.8 | 362.4 | 400.5 | 313.6 | 405.5
1126.3 | 907.3 | 329 | 359.3 | 394.9 | 311.8 | 403.9
1127.3 | 908.3 | 329.2 | 355.6 | 391.7 | 310.1 | 402.8
1128.3 | 909.3 | 329.5 | 355.7 | 391.5 | 309.7 | 403.4
1129.3 | 910.3 | 329.7 | 356.5 | 398.1 | 310.4 | 405.2
1130.3 | 911.3 | 329.9 | 354.8 | 394.1 | 309.9 | 403.7
1131.3 | 912.3 | 330.2 | 352.4 | 393 | 309 | 402.2
1132.3 | 913.3 | 330.4 | 348.9 | 382.3 | 307.7 | 400.8
1133.3 | 914.3 | 330.6 | 345.5 | 378.5 | 305.7 | 399.8
1134.3 | 915.3 | 330.8 | 343.4 | 376 | 304.7 | 398.7
1135.3 | 916.3 | 331 | 341.6 | 376.2 | 303.7 | 397.6
1136.3 | 917.3 | 331.2 | 339.4 | 373.1 | 302.5 | 396.6
1137.3 | 918.3 | 331.4 | 339.5 | 372 | 302.4 | 396.7
1138.3 | 919.3 | 331.6 | 342.2 | 384.8 | 303.9 | 397.9
1139.3 | 920.3 | 331.8 | 343.3 | 388.4 | 304.1 | 397.6
1140.3 | 921.3 | 332 | 344.4 | 397.5 | 304.7 | 397.7
1141.3 | 922.3 | 332.2 | 344.7 | 397.2 | 304.7 | 397.4
1142.3 | 923.3 | 332.4 | 344.9 | 396.8 | 304 | 396.9
1143.3 | 924.3 | 332.6 | 348.5 | 402.3 | 305.7 | 398.3
1144.3 | 925.3 | 332.8 | 350 | 405.8 | 306.4 | 398.5
1145.3 | 926.3 | 333 | 350.7 | 400.3 | 306.6 | 398.2
1146.3 | 927.3 | 333.2 | 349.4 | 393.6 | 305.8 | 396.9
1147.3 | 928.3 | 333.4 | 345.8 | 387.1 | 304.2 | 395.2
1148.3 | 929.3 | 333.6 | 342.2 | 381.5 | 302.8 | 393.8
1149.3 | 930.3 | 333.8 | 338.4 | 375.1 | 301.2 | 392.6
1150.3 | 931.3 | 334 | 337.1 | 379.4 | 300.3 | 392.1
1151.3 | 932.3 | 334.2 | 336 | 376.1 | 299.8 | 391.3
1152.3 | 933.3 | 334.4 | 335.2 | 379 | 298.9 | 390.9
1153.3 | 934.3 | 334.6 | 336.4 | 387 | 299.6 | 391.3
1154.3 | 935.3 | 334.8 | 340.2 | 397 | 301.8 | 393.6
1155.3 | 936.3 | 335 | 346.9 | 404.5 | 304.5 | 395.9
1156.3 | 937.3 | 335.2 | 361.1 | 435.7 | 312.1 | 401.5
1157.3 | 938.3 | 335.4 | 369.8 | 442.1 | 317.3 | 404.6
1158.3 | 939.3 | 335.6 | 371 | 440.6 | 318.3 | 405
1159.3 | 940.3 | 335.8 | 369.6 | 435.3 | 317.2 | 404
1160.3 | 941.3 | 336 | 368.8 | 432.7 | 316.4 | 403.4
1161.3 | 942.3 | 336.2 | 366.2 | 424.1 | 315.4 | 402.1
1162.3 | 943.3 | 336.4 | 363.2 | 421.4 | 314.3 | 401.1
1163.3 | 944.3 | 336.6 | 365.6 | 431.8 | 315.4 | 401.9
1164.3 | 945.3 | 336.8 | 363 | 423.4 | 314.1 | 400.2
1165.3 | 946.3 | 337 | 361.7 | 420.8 | 312.9 | 399.7
1166.3 | 947.3 | 337.2 | 360.1 | 415.1 | 312.1 | 399.6
1167.3 | 948.3 | 337.4 | 359.2 | 417.3 | 311.9 | 399.4
1168.3 | 949.3 | 337.6 | 360.6 | 430 | 312.5 | 399.8
1169.3 | 950.3 | 337.7 | 359.4 | 428.3 | 312.2 | 398.9
1170.3 | 951.3 | 338 | 355.7 | 417.3 | 310.7 | 397.3
1171.3 | 952.3 | 338.1 | 351.8 | 406.3 | 308.9 | 395.8
1172.3 | 953.3 | 338.3 | 346.1 | 394.2 | 306.5 | 394
1173.3 | 954.3 | 338.5 | 342.2 | 387 | 304.6 | 392.8
1174.3 | 955.3 | 338.7 | 341.2 | 384.6 | 304.1 | 392.1
1175.3 | 956.3 | 338.9 | 339.3 | 384 | 303 | 390.9
1176.3 | 957.3 | 339.1 | 338.8 | 384.1 | 302.1 | 390.5
1177.3 | 958.3 | 339.3 | 342.1 | 383.2 | 303.7 | 391.7
1178.3 | 959.3 | 339.5 | 342.4 | 378.7 | 303.8 | 391.2
1179.3 | 960.3 | 339.7 | 342.7 | 378 | 303.4 | 391.1
1180.3 | 961.3 | 339.9 | 342.9 | 377.5 | 303.2 | 390.6
1181.3 | 962.3 | 340.1 | 342.6 | 377.9 | 303 | 390.2
1182.3 | 963.3 | 340.3 | 345.4 | 384.1 | 304.8 | 391.8
1183.3 | 964.3 | 340.5 | 345.7 | 394.5 | 305.2 | 391.3
1184.3 | 965.3 | 340.7 | 346 | 409.8 | 305 | 390.7
1185.3 | 966.3 | 340.9 | 346.9 | 424.1 | 306 | 390.6
1186.3 | 967.3 | 341 | 353.1 | 442.9 | 308.3 | 392.3
1187.3 | 968.3 | 341.2 | 356.6 | 437.3 | 309.7 | 392.8
1188.3 | 969.3 | 341.4 | 361.5 | 450.8 | 311.5 | 394.6
1189.3 | 970.3 | 341.6 | 366.9 | 468 | 314.7 | 397.5
1190.3 | 971.3 | 341.8 | 372 | 473.7 | 318.5 | 398.6
1191.3 | 972.3 | 342 | 373.9 | 474.1 | 318.8 | 399.1
1192.3 | 973.3 | 342.2 | 375.9 | 482.6 | 320.2 | 400.6
1193.3 | 974.3 | 342.4 | 376.6 | 484.6 | 320.8 | 401.2
1194.3 | 975.3 | 342.6 | 377.6 | 481.4 | 321.9 | 403
1195.3 | 976.3 | 342.7 | 379.7 | 484.9 | 323.1 | 404
1196.3 | 977.3 | 342.9 | 382.8 | 484.9 | 324.6 | 405.2
1197.3 | 978.3 | 343.1 | 382.5 | 478.4 | 324 | 404.5
1198.3 | 979.3 | 343.3 | 384.4 | 493.2 | 324.9 | 406.3
1199.3 | 980.3 | 343.5 | 386.6 | 480.9 | 326.5 | 408.2
1200.3 | 981.3 | 343.7 | 385.7 | 472.9 | 326.3 | 408.1
1201.3 | 982.3 | 344 | 387.1 | 471.6 | 327.5 | 410.2
1202.3 | 983.3 | 344.2 | 395.2 | 477.5 | 332.5 | 414.5
1203.3 | 984.3 | 344.4 | 400.6 | 497.5 | 336.2 | 415.7
1204.3 | 985.3 | 344.6 | 403.3 | 507.2 | 337.6 | 416.5
1205.3 | 986.3 | 344.8 | 405.3 | 517.7 | 338.8 | 418
1206.3 | 987.3 | 345 | 405.4 | 510.7 | 338.1 | 417.5
1207.3 | 988.3 | 345.2 | 406.7 | 505.7 | 338.8 | 418.8
1208.3 | 989.3 | 345.4 | 408.1 | 507.8 | 339.8 | 421.8
1209.3 | 990.3 | 345.7 | 407.1 | 502.7 | 339.5 | 421
1210.3 | 991.3 | 345.9 | 406.3 | 503.6 | 338.7 | 420.9
1211.3 | 992.3 | 346.1 | 405.1 | 499.2 | 337.5 | 420.9
1212.3 | 993.3 | 346.3 | 403.7 | 490 | 336.9 | 420.5
1213.3 | 994.3 | 346.6 | 400.7 | 483.5 | 335.6 | 419.7
1214.3 | 995.3 | 346.8 | 397.5 | 483.3 | 334.4 | 418.8
1215.3 | 996.3 | 347 | 396.3 | 480.9 | 334.3 | 418.5
1216.3 | 997.3 | 347.2 | 396.8 | 484 | 334.5 | 419.2
1217.3 | 998.3 | 347.5 | 399 | 487.8 | 336 | 419.8
1218.3 | 999.3 | 347.7 | 398.3 | 488.7 | 335.9 | 419.6
1219.3 | 1000.3 | 348 | 396.9 | 480.8 | 335.1 | 419.8
1220.3 | 1001.3 | 348.3 | 396.3 | 473.4 | 335 | 420.6
1221.3 | 1002.3 | 348.5 | 397.3 | 477.3 | 335.8 | 421.5
1222.3 | 1003.3 | 348.8 | 399.4 | 473.1 | 338 | 423.1
1223.3 | 1004.3 | 349 | 397.7 | 462.4 | 337.2 | 421.8
1224.3 | 1005.3 | 349.3 | 392.1 | 446.8 | 334.9 | 419.5
1225.3 | 1006.3 | 349.5 | 388 | 445.4 | 332.9 | 418.2
1226.3 | 1007.3 | 349.7 | 386.6 | 442.9 | 332.3 | 417.6
1227.3 | 1008.3 | 349.9 | 382.6 | 431.4 | 330.6 | 416.3
1228.3 | 1009.3 | 350.2 | 380.5 | 434.1 | 330 | 416.9
1229.3 | 1010.3 | 350.5 | 382.2 | 443.4 | 331.9 | 418
1230.3 | 1011.3 | 350.8 | 390.3 | 463.2 | 336.5 | 421.7
1231.3 | 1012.3 | 351 | 396.7 | 477.8 | 340.9 | 425.5
1232.3 | 1013.3 | 351.3 | 397.6 | 476.5 | 342.1 | 425.3
1233.3 | 1014.3 | 351.6 | 402.7 | 483.8 | 345.2 | 426.7
1234.3 | 1015.3 | 351.9 | 407 | 488.2 | 348 | 427.1
1235.3 | 1016.3 | 352.1 | 407.9 | 489.2 | 348 | 427
1236.3 | 1017.3 | 352.4 | 412.6 | 482.9 | 350.2 | 431.7
1237.3 | 1018.3 | 352.7 | 411.1 | 471.5 | 349.4 | 430.7
1238.3 | 1019.3 | 353 | 415.2 | 471.9 | 350.7 | 432.7
1239.3 | 1020.3 | 353.2 | 420.4 | 476.9 | 353.7 | 434.7
1240.3 | 1021.3 | 353.5 | 423.7 | 484.6 | 355 | 435.7
1241.3 | 1022.3 | 353.8 | 428.7 | 480 | 359.8 | 439.3
1242.3 | 1023.3 | 354 | 428.6 | 476.2 | 360.5 | 438.6
1243.3 | 1024.3 | 354.3 | 425.3 | 471.4 | 359.1 | 438.2
1244.3 | 1025.3 | 354.5 | 425.4 | 472.4 | 358.6 | 438.7
1245.3 | 1026.3 | 354.8 | 422.6 | 462.8 | 357.1 | 437.5
1246.3 | 1027.3 | 355 | 420.1 | 459.6 | 355.6 | 436.3
1247.3 | 1028.3 | 355.3 | 417.9 | 460.2 | 354 | 435.4
1248.3 | 1029.3 | 355.6 | 414.6 | 455.5 | 351.8 | 434
1249.3 | 1030.3 | 355.8 | 413.5 | 462.6 | 350.8 | 433.6
1250.3 | 1031.3 | 356.1 | 419.1 | 482.3 | 355.9 | 437.4
1251.3 | 1032.3 | 356.4 | 425.9 | 495.1 | 359.4 | 441.2
1252.3 | 1033.3 | 356.7 | 429.7 | 498.4 | 361.4 | 442
1253.3 | 1034.3 | 356.9 | 430.3 | 503 | 361.1 | 441.6
1254.3 | 1035.3 | 357.2 | 434.6 | 505 | 364 | 444.1
1255.3 | 1036.3 | 357.5 | 436.8 | 509 | 365.2 | 444.7
1256.3 | 1037.3 | 357.7 | 440.8 | 520.7 | 368.2 | 447.2
1257.3 | 1038.3 | 358 | 441.5 | 513.7 | 368.9 | 448
1258.3 | 1039.3 | 358.2 | 445.1 | 515.1 | 370.5 | 449.5
1259.3 | 1040.3 | 358.5 | 448.9 | 509.5 | 372.2 | 451.4
1260.3 | 1041.3 | 358.9 | 455.9 | 513.3 | 374.7 | 453.4
1261.3 | 1042.3 | 359.1 | 460.4 | 505.2 | 376.4 | 453.3
1262.3 | 1043.3 | 359.4 | 460.6 | 498.9 | 377.1 | 453.5
1263.3 | 1044.3 | 359.7 | 458.4 | 490.3 | 376.5 | 453.1
1264.3 | 1045.3 | 360 | 456.9 | 491.5 | 376.1 | 452.1
1265.3 | 1046.3 | 360.4 | 461.5 | 510.8 | 377.4 | 453.2
1266.3 | 1047.3 | 360.7 | 468.7 | 511.2 | 380.4 | 454.9
1267.3 | 1048.3 | 361 | 472.2 | 511.9 | 381.9 | 456.1
1268.3 | 1049.3 | 361.3 | 475.3 | 509.3 | 383.6 | 456.9
1269.3 | 1050.3 | 361.6 | 488.6 | 508 | 391.9 | 458.5
1270.3 | 1051.3 | 361.9 | 501.8 | 515.1 | 394.6 | 459.4
1271.3 | 1052.3 | 362.2 | 511.1 | 515.6 | 395.9 | 460.9
1272.3 | 1053.3 | 362.6 | 519.7 | 504.4 | 396.4 | 460.1
1273.3 | 1054.3 | 362.9 | 522.4 | 505.6 | 395.3 | 460
1274.3 | 1055.3 | 363.2 | 529.4 | 505.4 | 397 | 461.5
1275.3 | 1056.3 | 363.5 | 529.9 | 507.9 | 396.9 | 461.2
1276.3 | 1057.3 | 363.8 | 532.9 | 506.2 | 398.6 | 462.6
1277.3 | 1058.3 | 364.2 | 533.2 | 500 | 399.6 | 463.5
1278.3 | 1059.3 | 364.5 | 551 | 514.7 | 407.4 | 466.7
1279.3 | 1060.3 | 364.8 | 561.4 | 512.5 | 409.8 | 469
1280.3 | 1061.3 | 365.2 | 576.9 | 519.1 | 416.2 | 468.1
1281.3 | 1062.3 | 365.5 | 570.3 | 505.5 | 413.8 | 466
1282.3 | 1063.3 | 365.8 | 563.9 | 491.3 | 411.4 | 464
1283.3 | 1064.3 | 366.1 | 559 | 480.2 | 414.5 | 462.1
1284.3 | 1065.3 | 366.5 | 559.8 | 470.4 | 415.3 | 460.8
1285.3 | 1066.3 | 366.8 | 550.4 | 458 | 413.3 | 458.3
1286.3 | 1067.3 | 367.1 | 541.3 | 457 | 412.1 | 457.6
1287.3 | 1068.3 | 367.5 | 545 | 462.4 | 412.6 | 459.3
1288.3 | 1069.3 | 367.8 | 544.2 | 470 | 412.8 | 460.6
1289.3 | 1070.3 | 368.1 | 552.4 | 468.4 | 416.2 | 463.2
1290.3 | 1071.3 | 368.5 | 558 | 467.9 | 418.9 | 465.4
1291.3 | 1072.3 | 368.8 | 566.5 | 468.7 | 422.7 | 467.1
1292.3 | 1073.3 | 369.1 | 591.2 | 494.4 | 437.6 | 470.4
1293.3 | 1074.3 | 369.5 | 606.4 | 495.2 | 442.6 | 473.7
1294.3 | 1075.3 | 369.8 | 602.7 | 487 | 440.5 | 472.3
1295.3 | 1076.3 | 370.1 | 588.1 | 475.2 | 436.5 | 469.8
1296.3 | 1077.3 | 370.5 | 578.9 | 475.8 | 434.6 | 469.4
1297.3 | 1078.3 | 370.8 | 576.8 | 487.2 | 434.1 | 470.1
1298.3 | 1079.3 | 371.1 | 586.6 | 485.4 | 441.3 | 473.7
1299.3 | 1080.3 | 371.4 | 579.8 | 473.5 | 439.4 | 471.5
1300.3 | 1081.3 | 371.7 | 574.4 | 467.1 | 439 | 469.8
1301.3 | 1082.3 | 372 | 564.6 | 456.4 | 436.8 | 467.8
1302.3 | 1083.3 | 372.3 | 556 | 443 | 435 | 465.2
1303.3 | 1084.3 | 372.6 | 550.2 | 437.3 | 434.3 | 464
1304.3 | 1085.3 | 372.9 | 544.5 | 430.5 | 431.1 | 463.5
1305.3 | 1086.3 | 373.2 | 539.9 | 430.8 | 429.1 | 462.9
1306.3 | 1087.3 | 373.5 | 531.1 | 424 | 426.7 | 462.7
1307.3 | 1088.3 | 373.8 | 520.6 | 422.3 | 423.2 | 461.6
1308.3 | 1089.3 | 374.1 | 511.3 | 421.1 | 420.6 | 460.9
1309.3 | 1090.3 | 374.4 | 515.9 | 432 | 422 | 463.4
1310.3 | 1091.3 | 374.7 | 513.3 | 427.5 | 421.9 | 462.2
1311.3 | 1092.3 | 375.1 | 506.2 | 429.2 | 420.2 | 461.3
1312.3 | 1093.3 | 375.4 | 504.2 | 434.4 | 419.9 | 461.2
1313.3 | 1094.3 | 375.7 | 497.7 | 428.4 | 417.9 | 459.8
1314.3 | 1095.3 | 376 | 490.9 | 422.4 | 415.7 | 459.4
1315.3 | 1096.3 | 376.3 | 483.8 | 419.5 | 412.6 | 457.9
1316.3 | 1097.3 | 376.6 | 476.8 | 418.6 | 409.7 | 456.4
1317.3 | 1098.3 | 376.9 | 470.7 | 415.6 | 407.4 | 455.5
1318.3 | 1099.3 | 377.1 | 468.6 | 415.8 | 406.4 | 455.5
1319.3 | 1100.3 | 377.4 | 467.5 | 414.7 | 405.2 | 454.7
1320.3 | 1101.3 | 377.6 | 461.1 | 410.6 | 402.8 | 452.7
1321.3 | 1102.3 | 377.9 | 455.9 | 405.9 | 400.4 | 450.8
1322.3 | 1103.3 | 378.1 | 451.3 | 403.9 | 398.3 | 450.4
1323.3 | 1104.3 | 378.3 | 449.3 | 402.7 | 397.3 | 450.2
1324.3 | 1105.3 | 378.5 | 450.3 | 406 | 397.3 | 450.4
1325.3 | 1106.3 | 378.7 | 445.8 | 402.8 | 395.5 | 448.5
1326.3 | 1107.3 | 378.9 | 439.9 | 398.4 | 392.6 | 446.8
1327.3 | 1108.3 | 379.1 | 434 | 393.6 | 391.2 | 445.2
1328.3 | 1109.3 | 379.3 | 428.9 | 387.3 | 389.6 | 443.9
1329.3 | 1110.3 | 379.6 | 424.9 | 383.7 | 387.3 | 442.2
1330.3 | 1111.3 | 379.8 | 420.3 | 379.9 | 384.9 | 440.5
1331.3 | 1112.3 | 380.1 | 416.9 | 376.8 | 382.8 | 439.6
1332.3 | 1113.3 | 380.3 | 414.2 | 374.7 | 381.7 | 438.3
1333.3 | 1114.3 | 380.6 | 417.9 | 381.9 | 382 | 440
1334.3 | 1115.3 | 380.8 | 431.2 | 394.7 | 386.5 | 441.7
1335.3 | 1116.3 | 381.1 | 435.5 | 404.1 | 388.2 | 441.9
1336.3 | 1117.3 | 381.3 | 436.5 | 404.2 | 389.2 | 441.9
1337.3 | 1118.3 | 381.6 | 433.8 | 401.6 | 388.5 | 440.8
1338.3 | 1119.3 | 381.9 | 433 | 415 | 387.9 | 441.1
1339.3 | 1120.3 | 382.1 | 436.3 | 421.2 | 387.9 | 440.8
1340.3 | 1121.3 | 382.4 | 433 | 420.2 | 386 | 440.2
1341.3 | 1122.3 | 382.6 | 430.5 | 419.6 | 384.8 | 439.7
1342.3 | 1123.3 | 382.9 | 427.7 | 416.2 | 383.6 | 438.9
1343.3 | 1124.3 | 383.1 | 421.5 | 408 | 380.5 | 436.5
1344.3 | 1125.3 | 383.3 | 418.9 | 410 | 378.8 | 436.2
1345.3 | 1126.3 | 383.6 | 417.1 | 405.1 | 378.2 | 435
1346.3 | 1127.3 | 383.8 | 413.7 | 402.8 | 376.4 | 433.6
1347.3 | 1128.3 | 384 | 410.7 | 399.3 | 374.8 | 431.9
1348.3 | 1129.3 | 384.2 | 405.4 | 389.8 | 374.5 | 430
1349.3 | 1130.3 | 384.4 | 402.1 | 382.5 | 373 | 428.3
1350.3 | 1131.3 | 384.6 | 398.4 | 375.8 | 370.3 | 426.5
1351.3 | 1132.3 | 384.8 | 398.6 | 378.3 | 369.4 | 426.6
1352.3 | 1133.3 | 384.9 | 400 | 384.1 | 369.2 | 426.6
1353.3 | 1134.3 | 385.1 | 400.8 | 385 | 368.9 | 426.2
1354.3 | 1135.3 | 385.3 | 411.5 | 397.3 | 373.9 | 429.9
1355.3 | 1136.3 | 385.5 | 418.2 | 408.9 | 376.1 | 429.8
1356.3 | 1137.3 | 385.7 | 419.2 | 410.1 | 376.4 | 430.2
1357.3 | 1138.3 | 385.9 | 416.8 | 405.9 | 376 | 429.6
1358.3 | 1139.3 | 386.1 | 418.8 | 409.2 | 376.7 | 430.4
1359.3 | 1140.3 | 386.3 | 416.4 | 403 | 375.3 | 428.9
1360.3 | 1141.3 | 386.5 | 412.3 | 400.8 | 373.2 | 427
1361.3 | 1142.3 | 386.7 | 411.7 | 403.3 | 372.3 | 426.3
1362.3 | 1143.3 | 386.9 | 415.8 | 399.8 | 374 | 427.6
1363.3 | 1144.3 | 387.1 | 414.9 | 394.4 | 373.8 | 426.5
1364.3 | 1145.3 | 387.3 | 415.2 | 402.4 | 373.4 | 426.5
1365.3 | 1146.3 | 387.4 | 418.5 | 409.7 | 374.7 | 427.7
1366.3 | 1147.3 | 387.6 | 423.9 | 406.2 | 377.7 | 428.2
1367.3 | 1148.3 | 387.8 | 419.5 | 396.8 | 376.3 | 426.2
1368.3 | 1149.3 | 388 | 418.3 | 399.2 | 375.6 | 425.8
1369.3 | 1150.3 | 388.1 | 419.6 | 401 | 375.7 | 426.4
1370.3 | 1151.3 | 388.2 | 416.9 | 398.4 | 374.8 | 424.5
1371.3 | 1152.3 | 388.4 | 414.1 | 395.8 | 373 | 423.1
1372.3 | 1153.3 | 388.6 | 409.9 | 391 | 370.8 | 421.8
1373.3 | 1154.3 | 388.8 | 408.1 | 390.2 | 369.8 | 421
1374.3 | 1155.3 | 389 | 405.2 | 389.2 | 368.3 | 420.3
1375.3 | 1156.3 | 389.2 | 409.2 | 395.4 | 369 | 420.7
1376.3 | 1157.3 | 389.4 | 414.1 | 414 | 370.1 | 421.9
1377.3 | 1158.3 | 389.6 | 421.1 | 417.9 | 372.2 | 422.7
1378.3 | 1159.3 | 389.8 | 432.5 | 432.5 | 378 | 425.8
1379.3 | 1160.3 | 390 | 444.7 | 431.3 | 385.7 | 427.6
1380.3 | 1161.3 | 390.2 | 440.4 | 424.1 | 383.3 | 426.4
1381.3 | 1162.3 | 390.4 | 436.1 | 419.3 | 381.9 | 425.3
1382.3 | 1163.3 | 390.6 | 435.1 | 419.9 | 381.1 | 425.4
1383.3 | 1164.3 | 390.7 | 438.8 | 429.4 | 382.1 | 427.2
1384.3 | 1165.3 | 391 | 451 | 435.1 | 385.2 | 428.7
1385.3 | 1166.3 | 391.2 | 454.8 | 433 | 386.8 | 429.5
1386.3 | 1167.3 | 391.4 | 457.2 | 432.2 | 387.6 | 429.6
1387.3 | 1168.3 | 391.6 | 457.2 | 431 | 388 | 429.2
1388.3 | 1169.3 | 391.8 | 451.6 | 417.1 | 386.4 | 426.8
1389.3 | 1170.3 | 392.1 | 442 | 408.2 | 383.1 | 424.7
1390.3 | 1171.3 | 392.3 | 437.5 | 403.2 | 382.2 | 424.1
1391.3 | 1172.3 | 392.5 | 432.5 | 405.3 | 380.5 | 423.3
1392.3 | 1173.3 | 392.7 | 429.2 | 398.8 | 379.7 | 422.1
1393.3 | 1174.3 | 392.9 | 426.4 | 395.9 | 378.3 | 422.2
1394.3 | 1175.3 | 393.1 | 422.1 | 395.1 | 376.6 | 420.9
1395.3 | 1176.3 | 393.4 | 420.5 | 400.5 | 375 | 420.6
1396.3 | 1177.3 | 393.7 | 420.4 | 403.6 | 374.9 | 420.4
1397.3 | 1178.3 | 393.9 | 418.2 | 401.9 | 374.5 | 419.4
1398.3 | 1179.3 | 394.1 | 412.4 | 395.4 | 372.5 | 417.7
1399.3 | 1180.3 | 394.4 | 409.6 | 390.7 | 371.8 | 417.1
1400.3 | 1181.3 | 394.6 | 404.4 | 383.8 | 370.3 | 415.5
1401.3 | 1182.3 | 394.8 | 401.8 | 379.2 | 369.4 | 414.4
1402.3 | 1183.3 | 394.9 | 400.5 | 377.3 | 367.9 | 413.6
1403.3 | 1184.3 | 395.1 | 401.4 | 382.1 | 367.1 | 413.7
1404.3 | 1185.3 | 395.3 | 406.7 | 391.1 | 369 | 415.8
1405.3 | 1186.3 | 395.4 | 409.4 | 401.6 | 370.3 | 416.4
1406.3 | 1187.3 | 395.4 | 412.9 | 408 | 371.2 | 416.8
1407.3 | 1188.3 | 395.5 | 409.8 | 405.9 | 369.9 | 415.9
1408.3 | 1189.3 | 395.6 | 411.7 | 408.9 | 370.8 | 416.3
1409.3 | 1190.3 | 395.8 | 411.4 | 405.8 | 370.7 | 415.4
1410.3 | 1191.3 | 395.9 | 409.7 | 403.5 | 370.1 | 414.7
1411.3 | 1192.3 | 396.1 | 407.7 | 397.1 | 369.2 | 413.8
1412.3 | 1193.3 | 396.2 | 406.8 | 392.4 | 368.6 | 413.1
1413.3 | 1194.3 | 396.4 | 407.1 | 399.7 | 368 | 413.2
1414.3 | 1195.3 | 396.5 | 403.4 | 395.4 | 366.1 | 411.9
1415.3 | 1196.3 | 396.6 | 402 | 391 | 365.5 | 410.9
1416.3 | 1197.3 | 396.7 | 398.2 | 385.2 | 364.2 | 409.8
1417.3 | 1198.3 | 396.9 | 398 | 382.9 | 364.3 | 408.9
1418.3 | 1199.3 | 397.1 | 398.7 | 386 | 364.5 | 408.6
1419.3 | 1200.3 | 397.2 | 400.7 | 393.4 | 365.3 | 409.2
1420.3 | 1201.3 | 397.4 | 403.2 | 396.7 | 366.5 | 409.6
1421.3 | 1202.3 | 397.6 | 408.1 | 401.5 | 368.5 | 411.1
1422.3 | 1203.3 | 397.8 | 412.9 | 405.9 | 370.3 | 411.6
1423.3 | 1204.3 | 398 | 418.4 | 424.5 | 372.5 | 412.8
1424.3 | 1205.3 | 398.2 | 424.8 | 429.6 | 375.2 | 414.6
1425.3 | 1206.3 | 398.4 | 428.7 | 440.1 | 377.5 | 416
1426.3 | 1207.3 | 398.6 | 433.1 | 445.9 | 380.2 | 418
1427.3 | 1208.3 | 398.8 | 438.7 | 451.7 | 383 | 418.6
1428.3 | 1209.3 | 399.1 | 437.5 | 443.8 | 383.2 | 417.7
1429.3 | 1210.3 | 399.3 | 437.4 | 444.8 | 382.5 | 418.3
1430.3 | 1211.3 | 399.6 | 434.1 | 434.2 | 381.8 | 417
1431.3 | 1212.3 | 399.8 | 429.5 | 427.4 | 380.4 | 415.9
1432.3 | 1213.3 | 400.1 | 428.4 | 423.5 | 380.1 | 416.3
1433.3 | 1214.3 | 400.4 | 431.4 | 424.1 | 381.6 | 417.7
1434.3 | 1215.3 | 400.6 | 453 | 440.6 | 390.9 | 423.9
1435.3 | 1216.3 | 400.9 | 468.9 | 450.7 | 395.9 | 426.5
1436.3 | 1217.3 | 401.1 | 470.1 | 450.1 | 397.1 | 426.8
1437.3 | 1218.3 | 401.3 | 467 | 448 | 396.4 | 427.1
1438.3 | 1219.3 | 401.5 | 470.5 | 461.6 | 398 | 429.1
1439.3 | 1220.3 | 401.9 | 483 | 484.3 | 403.4 | 431.3
1440.3 | 1221.3 | 402.2 | 486.6 | 487.5 | 405 | 432.6
1441.3 | 1222.3 | 402.5 | 505.2 | 506.8 | 412.8 | 437.9
1442.3 | 1223.3 | 402.8 | 516.8 | 523.7 | 418 | 442.4
1443.3 | 1224.3 | 403.2 | 526.9 | 519.3 | 423.7 | 448.2
1444.3 | 1225.3 | 403.6 | 538.9 | 519.8 | 431.4 | 454.8
1445.3 | 1226.3 | 403.9 | 557.6 | 528.3 | 438.7 | 458.9
1446.3 | 1227.3 | 404.2 | 555.7 | 525.4 | 438.6 | 458.2
1447.3 | 1228.3 | 404.6 | 557.7 | 527.9 | 439.6 | 459.7
1448.3 | 1229.3 | 405 | 555.8 | 516.5 | 440.2 | 459.6
1449.3 | 1230.3 | 405.3 | 548.7 | 506.9 | 438.5 | 459.2
1450.3 | 1231.3 | 405.7 | 539.9 | 493.7 | 436.3 | 458.2
1451.3 | 1232.3 | 406.1 | 531 | 485.2 | 434.5 | 457.1
1452.3 | 1233.3 | 406.4 | 533 | 489.5 | 435.6 | 458.6
1453.3 | 1234.3 | 406.7 | 530.6 | 487.3 | 436.1 | 459.8
1454.3 | 1235.3 | 407 | 524.1 | 482.4 | 434.8 | 459.1
1455.3 | 1236.3 | 407.3 | 519.1 | 483.4 | 434.1 | 459.5
1456.3 | 1237.3 | 407.7 | 510.6 | 478 | 431.3 | 457.5
1457.3 | 1238.3 | 408.2 | 509.9 | 475.1 | 430.7 | 456.9
1458.3 | 1239.3 | 408.5 | 509.2 | 470 | 429.7 | 456.3
1459.3 | 1240.3 | 408.9 | 507 | 471 | 428.8 | 456.6
1460.3 | 1241.3 | 409.4 | 502 | 468.1 | 427.1 | 455.7
1461.3 | 1242.3 | 409.7 | 501.8 | 461.9 | 427.5 | 454.7
1462.3 | 1243.3 | 410.1 | 501.7 | 458.2 | 429 | 453.9
1463.3 | 1244.3 | 410.4 | 500.5 | 455 | 428.1 | 454.4
1464.3 | 1245.3 | 410.7 | 495.8 | 444.4 | 425.9 | 452.4
1465.3 | 1246.3 | 411.1 | 497.9 | 436.5 | 427.1 | 450.5
1466.3 | 1247.3 | 411.5 | 500.1 | 431 | 426 | 449
1467.3 | 1248.3 | 411.9 | 496 | 427 | 424.7 | 448.9
1468.3 | 1249.3 | 412.4 | 491.3 | 420.9 | 423.9 | 448.6
1469.3 | 1250.3 | 413 | 495.7 | 429.4 | 425.9 | 449.2
1470.3 | 1251.3 | 413.6 | 501.1 | 438.4 | 427.7 | 451
1471.3 | 1252.3 | 414 | 505.2 | 443.3 | 428.8 | 451.9
1472.3 | 1253.3 | 414.5 | 513.7 | 464.7 | 431.9 | 455.2
1473.3 | 1254.3 | 414.9 | 530.8 | 485.4 | 442.2 | 461.9
1474.3 | 1255.3 | 415.4 | 540.6 | 516.1 | 444.4 | 462
1475.3 | 1256.3 | 415.9 | 545.3 | 517.8 | 445.7 | 461.9
1476.3 | 1257.3 | 416.4 | 550.9 | 523.6 | 445.4 | 461.9
1477.3 | 1258.3 | 416.9 | 567.1 | 544.5 | 453.7 | 469.5
1478.3 | 1259.3 | 417.4 | 579.6 | 546.8 | 458 | 471.4
1479.3 | 1260.3 | 417.9 | 582.1 | 545.6 | 459.5 | 472.7
1480.3 | 1261.3 | 418.3 | 587.9 | 539.7 | 461.8 | 474.3
1481.3 | 1262.3 | 418.7 | 598.2 | 531.8 | 462.2 | 473.8
1482.3 | 1263.3 | 419.2 | 594.4 | 529.5 | 461 | 472.2
1483.3 | 1264.3 | 419.7 | 595.5 | 518.2 | 460 | 471.3
1484.3 | 1265.3 | 420.2 | 599.6 | 516.3 | 459 | 469.9
1485.3 | 1266.3 | 420.7 | 611.3 | 524.7 | 461.5 | 470.7
1486.3 | 1267.3 | 421.2 | 613.5 | 527.8 | 462.6 | 471.9
1487.3 | 1268.3 | 421.9 | 622.7 | 534.5 | 465.3 | 473.7
1488.3 | 1269.3 | 422.4 | 631.6 | 546.1 | 467.9 | 473.8
1489.3 | 1270.3 | 422.9 | 641.9 | 569.8 | 472.2 | 475.3
1490.3 | 1271.3 | 423.4 | 651.7 | 581.9 | 476.8 | 477.3
1491.3 | 1272.3 | 424 | 661.2 | 593.2 | 482.7 | 479.3
1492.3 | 1273.3 | 424.5 | 668.9 | 598 | 488.1 | 484.8
1493.3 | 1274.3 | 425.1 | 678.4 | 611.2 | 495.5 | 490.6
1494.3 | 1275.3 | 425.7 | 679.7 | 605.1 | 498.7 | 492.4
1495.3 | 1276.3 | 426.4 | 688.1 | 616.5 | 500.7 | 493.3
1496.3 | 1277.3 | 427.1 | 700.6 | 631.7 | 512.2 | 495.2
1497.3 | 1278.3 | 427.8 | 708.6 | 630.5 | 522.4 | 497.3
1498.3 | 1279.3 | 428.4 | 719.1 | 619 | 526.9 | 498.1
1499.3 | 1280.3 | 428.9 | 730.9 | 596.2 | 532.7 | 495.8
1500.3 | 1281.3 | 429.5 | 740.1 | 579.3 | 547.6 | 494
1501.3 | 1282.3 | 430.3 | 751.7 | 577.8 | 560 | 494
1502.3 | 1283.3 | 431.3 | 761.8 | 615.9 | 569.4 | 497.5
1503.3 | 1284.3 | 431.9 | 761.8 | 627.9 | 571.3 | 503.5
1504.3 | 1285.3 | 432.5 | 764.6 | 644.9 | 575.6 | 508.1
1505.3 | 1286.3 | 433.1 | 770.4 | 621.8 | 579.2 | 509.1
1506.3 | 1287.3 | 433.8 | 779.7 | 617.7 | 585.6 | 510
1507.3 | 1288.3 | 434.4 | 782.9 | 638.5 | 589.5 | 514.6
1508.3 | 1289.3 | 435 | 789.2 | 657.3 | 591.4 | 515.6
1509.3 | 1290.3 | 435.7 | 793.1 | 680.9 | 593.8 | 517.5
1510.3 | 1291.3 | 436.5 | 794 | 699.4 | 598.4 | 525.4
1511.3 | 1292.3 | 437.2 | 792.5 | 685.9 | 601.8 | 529.5
1512.3 | 1293.3 | 437.8 | 802.3 | 663.3 | 605.9 | 529.5
1513.3 | 1294.3 | 438.4 | 804.2 | 646.3 | 610.4 | 529.9
1514.3 | 1295.3 | 439 | 808.2 | 628.5 | 616.3 | 527.5
1515.3 | 1296.3 | 439.7 | 813.3 | 604.2 | 616.5 | 525.1
1516.3 | 1297.3 | 440.3 | 820.5 | 591 | 620.6 | 523.5
1517.3 | 1298.3 | 440.9 | 827.8 | 571 | 620.8 | 522
1518.3 | 1299.3 | 441.6 | 831.2 | 552.2 | 621.1 | 519.5
1519.3 | 1300.3 | 442.3 | 832.8 | 540.1 | 621.7 | 517.1
1520.3 | 1301.3 | 443 | 828.2 | 538.3 | 624 | 517.3
1521.3 | 1302.3 | 443.6 | 829.6 | 535 | 626 | 517.5
1522.3 | 1303.3 | 444.3 | 824.7 | 552.5 | 625 | 520.7
1523.3 | 1304.3 | 444.9 | 821.1 | 561.9 | 625 | 525.3
1524.3 | 1305.3 | 445.5 | 818.3 | 566.9 | 622.9 | 527.5
1525.3 | 1306.3 | 446.1 | 816.3 | 565.6 | 623.3 | 526.7
1526.3 | 1307.3 | 446.8 | 820.7 | 564.7 | 627.5 | 527.1
1527.3 | 1308.3 | 447.4 | 822.6 | 559.4 | 630.2 | 526.1
1528.3 | 1309.3 | 448.1 | 824.5 | 571.5 | 630.5 | 528.6
1529.3 | 1310.3 | 448.6 | 825.4 | 560 | 633 | 526.6
1530.3 | 1311.3 | 449.2 | 828.4 | 558 | 634.4 | 524.6
1531.3 | 1312.3 | 449.8 | 833.2 | 559.4 | 636.1 | 526.5
1532.3 | 1313.3 | 450.4 | 836.5 | 553.4 | 641 | 526.4
1533.3 | 1314.3 | 451 | 832.2 | 542.5 | 636.1 | 525.2
1534.3 | 1315.3 | 451.5 | 834.7 | 533.7 | 640.1 | 522.5
1535.3 | 1316.3 | 452.3 | 840.2 | 535.4 | 644.1 | 523.2
1536.3 | 1317.3 | 452.9 | 838.2 | 536.6 | 643.8 | 524
1537.3 | 1318.3 | 453.4 | 835.9 | 521.6 | 640.6 | 521.6
1538.3 | 1319.3 | 453.9 | 844.4 | 509.9 | 640.7 | 520.5
1539.3 | 1320.3 | 454.3 | 845.7 | 501.2 | 642 | 518.8
1540.3 | 1321.3 | 454.8 | 837.5 | 495.4 | 646.9 | 516.4
1541.3 | 1322.3 | 455.3 | 833.8 | 494.4 | 647.9 | 515.7
1542.3 | 1323.3 | 455.8 | 833.8 | 494.9 | 650.6 | 515.4
1543.3 | 1324.3 | 456.2 | 836.7 | 491.7 | 650.6 | 514.6
1544.3 | 1325.3 | 456.8 | 842.7 | 502.5 | 646 | 515.3
1545.3 | 1326.3 | 457.2 | 839.6 | 504.1 | 644.1 | 515.6
1546.3 | 1327.3 | 457.6 | 843.2 | 503.1 | 649.2 | 515.1
1547.3 | 1328.3 | 458.1 | 840.3 | 506.1 | 648.7 | 517.3
1548.3 | 1329.3 | 458.6 | 840.8 | 496 | 650.3 | 516.3
1549.3 | 1330.3 | 459 | 840 | 498.6 | 652 | 517.3
1550.3 | 1331.3 | 459.5 | 840.4 | 500.2 | 650.3 | 519.2
1551.3 | 1332.3 | 459.9 | 837.1 | 489.7 | 651.7 | 517.6
1552.3 | 1333.3 | 460.2 | 840.2 | 484.9 | 654.1 | 516
1553.3 | 1334.3 | 460.5 | 847.2 | 476.1 | 654.3 | 513.6
1554.3 | 1335.3 | 460.9 | 845.8 | 469.6 | 650.8 | 512.5
1555.3 | 1336.3 | 461.4 | 848.9 | 465.9 | 650.6 | 511.1
1556.3 | 1337.3 | 461.9 | 852.8 | 461.2 | 653.1 | 509.2
1557.3 | 1338.3 | 462.3 | 850.8 | 461.4 | 652 | 507.7
1558.3 | 1339.3 | 462.6 | 854.1 | 458.5 | 652.4 | 507.1
1559.3 | 1340.3 | 463 | 852.1 | 460.1 | 649.5 | 507.3
1560.3 | 1341.3 | 463.4 | 854.3 | 457.5 | 650.3 | 506
1561.3 | 1342.3 | 463.9 | 850 | 459.5 | 657 | 505.1
1562.3 | 1343.3 | 464.3 | 848.3 | 460.3 | 651.6 | 505.2
1563.3 | 1344.3 | 464.8 | 839.2 | 470.5 | 646.8 | 507.5
1564.3 | 1345.3 | 465.2 | 840.6 | 474.3 | 644.6 | 507.7
1565.3 | 1346.3 | 465.6 | 827.2 | 478.3 | 640.6 | 508.2
1566.3 | 1347.3 | 466.1 | 825.8 | 485.6 | 641 | 507.6
1567.3 | 1348.3 | 466.5 | 825.3 | 493.7 | 638.5 | 508.9
1568.3 | 1349.3 | 467 | 821.6 | 489.4 | 635.7 | 510.6
1569.3 | 1350.3 | 467.4 | 828.2 | 503.3 | 632.2 | 513.4
1570.3 | 1351.3 | 467.8 | 822.8 | 510.3 | 630.7 | 517.4
1571.3 | 1352.3 | 468.3 | 822.6 | 498.1 | 625.4 | 517.2
1572.3 | 1353.3 | 468.7 | 827.6 | 503.2 | 619.5 | 518.4
1573.3 | 1354.3 | 469 | 832.6 | 509.4 | 614.5 | 518.6
1574.3 | 1355.3 | 469.4 | 832.8 | 511.4 | 608 | 518.5
1575.3 | 1356.3 | 469.8 | 818.1 | 516.3 | 604 | 520.9
1576.3 | 1357.3 | 470.2 | 813.4 | 528.3 | 600.1 | 525
1577.3 | 1358.3 | 470.6 | 817.2 | 528 | 599.6 | 525.9
1578.3 | 1359.3 | 471.2 | 809.4 | 548.1 | 600 | 529.2
1579.3 | 1360.3 | 471.6 | 805.6 | 550.3 | 599.9 | 530.5
1580.3 | 1361.3 | 472.1 | 808.7 | 553.8 | 601.6 | 531.2
1581.3 | 1362.3 | 472.6 | 811.2 | 561.7 | 599.2 | 531.3
1582.3 | 1363.3 | 473.1 | 808.6 | 572.4 | 598.5 | 533.7
1583.3 | 1364.3 | 473.7 | 808.1 | 560.8 | 596.6 | 532.3
1584.3 | 1365.3 | 474.3 | 816.4 | 557.5 | 589.2 | 531.1
1585.3 | 1366.3 | 474.9 | 828.1 | 558.6 | 587.1 | 531.4
1586.3 | 1367.3 | 475.4 | 841.2 | 546.7 | 583.7 | 530.3
1587.3 | 1368.3 | 475.8 | 845.2 | 540.7 | 581.6 | 529.6
1588.3 | 1369.3 | 476.3 | 847.9 | 536.7 | 578.5 | 529
1589.3 | 1370.3 | 476.9 | 850.9 | 528.5 | 575.1 | 527.9
1590.3 | 1371.3 | 477.4 | 847 | 535.6 | 572.2 | 528.1
1591.3 | 1372.3 | 478 | 846.4 | 530.9 | 570.1 | 527.5
1592.3 | 1373.3 | 478.6 | 840.4 | 529.8 | 565.9 | 525.3
1593.3 | 1374.3 | 479.1 | 834.5 | 538.6 | 573.7 | 524.8
1594.3 | 1375.3 | 479.6 | 832.1 | 540.7 | 570.8 | 524.7
1595.3 | 1376.3 | 480.2 | 839.3 | 544.7 | 568.5 | 523.9
1596.3 | 1377.3 | 480.8 | 836.1 | 540.3 | 563.4 | 522.8
1597.3 | 1378.3 | 481.4 | 832.7 | 547.2 | 560.9 | 524.3
1598.3 | 1379.3 | 482 | 822.7 | 548.7 | 557 | 523.3
1599.3 | 1380.3 | 482.6 | 822.7 | 535 | 553 | 522.1
1600.3 | 1381.3 | 483.2 | 827.6 | 523.4 | 548.3 | 520.9
1601.3 | 1382.3 | 483.8 | 826 | 514.1 | 544.1 | 519.9
1602.3 | 1383.3 | 484.5 | 832 | 512.9 | 542 | 517.9
1603.3 | 1384.3 | 485.1 | 826.4 | 515.9 | 540.3 | 517
1604.3 | 1385.3 | 485.7 | 824.9 | 513.7 | 537 | 515.9
1605.3 | 1386.3 | 486.3 | 822.8 | 517.1 | 533.8 | 515.8
1606.3 | 1387.3 | 486.9 | 807.2 | 517 | 532.5 | 516.1
1607.3 | 1388.3 | 487.5 | 810 | 508.9 | 534.9 | 514.4
1608.3 | 1389.3 | 488 | 809.4 | 503.2 | 533.8 | 512.4
1609.3 | 1390.3 | 488.6 | 804.5 | 512 | 534.3 | 513.3
1610.3 | 1391.3 | 489.1 | 800.6 | 521.8 | 531.4 | 513.6
1611.3 | 1392.3 | 489.7 | 800.2 | 529.4 | 534.9 | 513.1
1612.3 | 1393.3 | 490.3 | 800.4 | 542.7 | 542.1 | 514.6
1613.3 | 1394.3 | 491 | 791.7 | 558.7 | 541.3 | 518.5
1614.3 | 1395.3 | 491.6 | 787.7 | 591.7 | 544.9 | 524.1
1615.3 | 1396.3 | 492.2 | 787.4 | 616.2 | 552.5 | 531
1616.3 | 1397.3 | 492.8 | 789 | 602.5 | 556.8 | 533.2
1617.3 | 1398.3 | 493.4 | 784.5 | 598.8 | 557.2 | 534.1
1618.3 | 1399.3 | 494.1 | 781.7 | 592.8 | 560.8 | 537.2
1619.3 | 1400.3 | 494.8 | 784.7 | 589.4 | 559.7 | 537.3
1620.3 | 1401.3 | 495.5 | 791.4 | 572.3 | 558 | 536.3
1621.3 | 1402.3 | 496.1 | 806.3 | 561.5 | 557.3 | 534.3
1622.3 | 1403.3 | 496.8 | 816.6 | 554.6 | 557.5 | 532.8
1623.3 | 1404.3 | 497.4 | 817.4 | 561.3 | 556.5 | 532.5
1624.3 | 1405.3 | 498 | 819.5 | 575.4 | 559.1 | 535.3
1625.3 | 1406.3 | 498.7 | 808.9 | 577.9 | 559.7 | 537.7
1626.3 | 1407.3 | 499.3 | 810.5 | 576.8 | 560.8 | 540.2
1627.3 | 1408.3 | 500 | 811.6 | 569 | 565.7 | 540.5
1628.3 | 1409.3 | 500.5 | 818.6 | 568.5 | 563.9 | 540.3
1629.3 | 1410.3 | 501.1 | 810.1 | 567.4 | 563 | 540.9
1630.3 | 1411.3 | 501.7 | 813.3 | 565.3 | 561.8 | 539.4
1631.3 | 1412.3 | 502.3 | 815.5 | 563.3 | 573.6 | 537.7
1632.3 | 1413.3 | 503 | 818.9 | 564.6 | 578.3 | 538.8
1633.3 | 1414.3 | 503.5 | 816.4 | 590.8 | 580.9 | 542.7
1634.3 | 1415.3 | 504.2 | 813.6 | 622.4 | 587.3 | 547.5
1635.3 | 1416.3 | 504.8 | 806.3 | 645.1 | 591.8 | 553.3
1636.3 | 1417.3 | 505.4 | 802.9 | 637.9 | 591.4 | 556.2
1637.3 | 1418.3 | 506 | 806.9 | 617.6 | 589.6 | 553.9
1638.3 | 1419.3 | 506.7 | 814.8 | 616.3 | 590.7 | 552.1
1639.3 | 1420.3 | 507.4 | 818.3 | 618.5 | 590.5 | 552
1640.3 | 1421.3 | 508 | 814.6 | 610.8 | 592.2 | 551.8
1641.3 | 1422.3 | 508.6 | 821.7 | 598.6 | 590 | 550.1
1642.3 | 1423.3 | 509.1 | 822.4 | 575.1 | 595.3 | 546.3
1643.3 | 1424.3 | 509.7 | 822.2 | 559.3 | 606.4 | 543.3
1644.3 | 1425.3 | 510.3 | 817.2 | 546.9 | 611.6 | 540.5
1645.3 | 1426.3 | 510.9 | 816.4 | 537.6 | 616.5 | 538.6
1646.3 | 1427.3 | 511.5 | 819.2 | 528.9 | 614.2 | 537.1
1647.3 | 1428.3 | 511.9 | 822.4 | 519.6 | 621.5 | 534.2
1648.3 | 1429.3 | 512.3 | 829.4 | 515.6 | 625.5 | 532.3
1649.3 | 1430.3 | 512.8 | 835.6 | 508.8 | 619.4 | 530.5
1650.3 | 1431.3 | 513.3 | 843.2 | 504.4 | 610.2 | 529.4
1651.3 | 1432.3 | 513.8 | 844.8 | 500.6 | 603.8 | 529.2
1652.3 | 1433.3 | 514.2 | 843.2 | 497.4 | 604.5 | 526.8
1653.3 | 1434.3 | 514.7 | 842.7 | 511.3 | 608.6 | 528.8
1654.3 | 1435.3 | 515.2 | 832.8 | 540.6 | 605.7 | 530.7
1655.3 | 1436.3 | 515.7 | 823.6 | 553 | 604.3 | 533.9
1656.3 | 1437.3 | 516.1 | 817.7 | 578 | 605.4 | 536.6
1657.3 | 1438.3 | 516.6 | 812.4 | 571.3 | 605.5 | 537.9
1658.3 | 1439.3 | 517.2 | 815.5 | 553 | 607.7 | 536.2
1659.3 | 1440.3 | 517.7 | 821.5 | 539.6 | 607.4 | 535
1660.3 | 1441.3 | 518.1 | 819.9 | 531.8 | 615.4 | 532.7
1661.3 | 1442.3 | 518.4 | 816.7 | 522.1 | 617.3 | 530.2
1662.3 | 1443.3 | 518.7 | 813.9 | 509.9 | 622.5 | 528.1
1663.3 | 1444.3 | 519.1 | 817.9 | 520.3 | 615.8 | 528
1664.3 | 1445.3 | 519.5 | 812.4 | 547 | 616.8 | 530
1665.3 | 1446.3 | 519.8 | 813.5 | 534 | 610.4 | 529.2
1666.3 | 1447.3 | 520.3 | 818.8 | 517.1 | 607.2 | 526.9
1667.3 | 1448.3 | 520.7 | 824.7 | 507.6 | 605.8 | 525.4
1668.3 | 1449.3 | 520.9 | 821 | 495.9 | 608 | 522.8
1669.3 | 1450.3 | 521 | 809 | 483.2 | 614.3 | 520.6
1670.3 | 1451.3 | 521.3 | 802.3 | 477.1 | 620.6 | 518.7
1671.3 | 1452.3 | 521.8 | 803.3 | 488.1 | 625.1 | 519.5
1672.3 | 1453.3 | 522.2 | 804.5 | 501.7 | 619.5 | 520.6
1673.3 | 1454.3 | 522.8 | 813.5 | 508.1 | 623.7 | 521.2
1674.3 | 1455.3 | 523.3 | 816.7 | 529.6 | 628 | 523.9
1675.3 | 1456.3 | 523.8 | 822.4 | 531.6 | 620.8 | 523.8
1676.3 | 1457.3 | 524.3 | 819.1 | 525.7 | 616 | 522.1
1677.3 | 1458.3 | 524.7 | 808.3 | 521.9 | 617.8 | 520.5
1678.3 | 1459.3 | 525 | 807.7 | 510.9 | 617.2 | 518.6
1679.3 | 1460.3 | 525.3 | 802.4 | 496.8 | 615.4 | 516.9
1680.3 | 1461.3 | 525.7 | 802.6 | 491.2 | 619.8 | 515.4
1681.3 | 1462.3 | 526 | 804.2 | 492.3 | 618 | 515
1682.3 | 1463.3 | 526.4 | 807.8 | 488.4 | 620.2 | 514.9
1683.3 | 1464.3 | 526.8 | 808.1 | 501.4 | 617.9 | 517.7
1684.3 | 1465.3 | 527.1 | 811.3 | 516.4 | 616 | 521.2
1685.3 | 1466.3 | 527.5 | 806.1 | 518.1 | 613.3 | 526.2
1686.3 | 1467.3 | 528 | 806.9 | 510 | 610.1 | 526.4
1687.3 | 1468.3 | 528.4 | 810.9 | 502.2 | 608.7 | 525
1688.3 | 1469.3 | 528.9 | 816.4 | 501 | 609.2 | 525.1
1689.3 | 1470.3 | 529.4 | 819.4 | 500.9 | 605.4 | 523.5
1690.3 | 1471.3 | 529.6 | 823.8 | 501.2 | 609.4 | 522.4
1691.3 | 1472.3 | 529.8 | 820.7 | 499.9 | 618.5 | 520.3
1692.3 | 1473.3 | 530.2 | 819.8 | 519 | 622.1 | 521.9
1693.3 | 1474.3 | 530.5 | 817.6 | 541.6 | 620.4 | 524.1
1694.3 | 1475.3 | 530.8 | 815.9 | 537.1 | 618.4 | 525
1695.3 | 1476.3 | 531.3 | 813.2 | 525.5 | 617.6 | 526.4
1696.3 | 1477.3 | 531.8 | 812.6 | 526.9 | 618.6 | 525.6
1697.3 | 1478.3 | 532.2 | 810.6 | 532.7 | 615.1 | 526.6
1698.3 | 1479.3 | 532.6 | 809.5 | 520.5 | 615.1 | 525.4
1699.3 | 1480.3 | 532.8 | 811.2 | 509.8 | 618.9 | 522.8
1700.3 | 1481.3 | 533 | 808.2 | 500.1 | 622.2 | 520.5
1701.3 | 1482.3 | 533.4 | 811.8 | 494.6 | 622.7 | 519.5
1702.3 | 1483.3 | 533.7 | 812.9 | 496.5 | 622.7 | 518.8
1703.3 | 1484.3 | 534 | 810.1 | 502.5 | 627 | 518.7
1704.3 | 1485.3 | 534.2 | 808.6 | 496.8 | 627.3 | 517.6
1705.3 | 1486.3 | 534.4 | 807.8 | 494.7 | 630.2 | 515.8
1706.3 | 1487.3 | 534.8 | 802.5 | 487.2 | 629.1 | 514.7
1707.3 | 1488.3 | 535.2 | 804.1 | 489.6 | 629.9 | 514.7
1708.3 | 1489.3 | 535.6 | 803.9 | 485 | 625.8 | 513.6
1709.3 | 1490.3 | 535.8 | 811 | 484.2 | 624.8 | 512.3
1710.3 | 1491.3 | 536.2 | 815.5 | 495.5 | 627.9 | 512
1711.3 | 1492.3 | 536.6 | 814.6 | 492.7 | 630.2 | 511
1712.3 | 1493.3 | 536.8 | 816.2 | 493.2 | 633.9 | 509.8
1713.3 | 1494.3 | 537.2 | 804.3 | 492.8 | 631.4 | 509.3
1714.3 | 1495.3 | 537.6 | 805.8 | 487.2 | 626.6 | 508.9
1715.3 | 1496.3 | 538.1 | 806.4 | 483.6 | 626 | 507.7
1716.3 | 1497.3 | 538.4 | 806.2 | 482.4 | 627.9 | 507
1717.3 | 1498.3 | 538.6 | 796.8 | 479.7 | 626.8 | 505.9
1718.3 | 1499.3 | 539 | 793.1 | 480.4 | 626.5 | 505.3
1719.3 | 1500.3 | 539.4 | 791.3 | 477.1 | 624.8 | 504.8
1720.3 | 1501.3 | 539.6 | 781.4 | 473.5 | 624.6 | 503
1721.3 | 1502.3 | 539.7 | 789.9 | 467.3 | 628.3 | 501.7
1722.3 | 1503.3 | 539.9 | 788.6 | 458.5 | 627.7 | 500.1
1723.3 | 1504.3 | 539.9 | 786.1 | 454.6 | 625.9 | 499.3
1724.3 | 1505.3 | 540.2 | 784.4 | 451.3 | 628.8 | 498.1
1725.3 | 1506.3 | 540.6 | 784.7 | 449.9 | 629.9 | 497.9
1726.3 | 1507.3 | 541 | 777.6 | 446.3 | 625.3 | 497.5
1727.3 | 1508.3 | 541.2 | 778.3 | 449.2 | 628.2 | 497.9
1728.3 | 1509.3 | 541.5 | 769.8 | 443.3 | 628.7 | 496.4
1729.3 | 1510.3 | 541.5 | 761.6 | 442.4 | 632.2 | 495
1730.3 | 1511.3 | 541.9 | 758.4 | 435.5 | 631.3 | 493.9
1731.3 | 1512.3 | 542.2 | 764.1 | 434.8 | 634.1 | 494.1
1732.3 | 1513.3 | 542.3 | 763.2 | 434.8 | 634.4 | 493.4
1733.3 | 1514.3 | 542.1 | 768.2 | 438.2 | 633 | 493.1
1734.3 | 1515.3 | 541.6 | 760.6 | 426.7 | 633.8 | 491.6
1735.3 | 1516.3 | 541.3 | 753 | 419.2 | 635.4 | 490.6
1736.3 | 1517.3 | 541.9 | 758.9 | 419.8 | 636.1 | 490.3
1737.3 | 1518.3 | 542.5 | 764.7 | 430.5 | 642.4 | 490.8
1738.3 | 1519.3 | 543 | 769.7 | 458.8 | 644 | 493.5
1739.3 | 1520.3 | 543.3 | 770.8 | 478.7 | 642.8 | 498.4
1740.3 | 1521.3 | 543.6 | 764.9 | 499.5 | 640.4 | 497.7
1741.3 | 1522.3 | 544 | 760.6 | 501.9 | 640.6 | 497
1742.3 | 1523.3 | 544.2 | 768.4 | 513.9 | 641.5 | 496.4
1743.3 | 1524.3 | 544.3 | 780.3 | 534.7 | 642.3 | 497.2
1744.3 | 1525.3 | 544.6 | 785.5 | 567.5 | 641.3 | 502.5
1745.3 | 1526.3 | 544.9 | 785.4 | 561.1 | 636.8 | 502.3
1746.3 | 1527.3 | 545.2 | 775.2 | 550.8 | 636.3 | 501.7
1747.3 | 1528.3 | 545.2 | 767.1 | 532.6 | 633.8 | 500.5
1748.3 | 1529.3 | 545.2 | 757.2 | 515.3 | 636.6 | 498.6
1749.3 | 1530.3 | 545.6 | 759 | 511.3 | 638.2 | 499.1
1750.3 | 1531.3 | 546.1 | 766.4 | 508.6 | 635.6 | 499.9
1751.3 | 1532.3 | 546.3 | 763.1 | 503.7 | 634.9 | 500
1752.3 | 1533.3 | 546.5 | 758.1 | 493.4 | 633.8 | 498.5
1753.3 | 1534.3 | 547 | 760.2 | 492 | 636.9 | 498.8
1754.3 | 1535.3 | 547 | 762.1 | 482.6 | 635.2 | 497.8
1755.3 | 1536.3 | 546.9 | 766 | 475.9 | 634.9 | 496.4
1756.3 | 1537.3 | 547 | 771.9 | 489.4 | 637.3 | 496.9
1757.3 | 1538.3 | 547.2 | 776.7 | 509.2 | 636.6 | 501.9
1758.3 | 1539.3 | 547.3 | 768.9 | 510.3 | 630.2 | 505.9
1759.3 | 1540.3 | 547.1 | 760.1 | 499.6 | 632 | 504.3
1760.3 | 1541.3 | 547.3 | 761.5 | 492 | 637.4 | 503
1761.3 | 1542.3 | 547.6 | 764.3 | 482.1 | 637.1 | 502.6
1762.3 | 1543.3 | 548 | 770.5 | 474.7 | 636.1 | 503
1763.3 | 1544.3 | 548.2 | 767.7 | 483.7 | 635.8 | 503.2
1764.3 | 1545.3 | 548.6 | 761.3 | 481.5 | 635.3 | 502.1
1765.3 | 1546.3 | 549 | 759.7 | 480 | 636.2 | 501.1
1766.3 | 1547.3 | 549.1 | 754.8 | 474.3 | 633.1 | 499.7
1767.3 | 1548.3 | 549.3 | 753.7 | 463.8 | 632.1 | 498
1768.3 | 1549.3 | 549.4 | 745.9 | 453.6 | 634.5 | 496.5
1769.3 | 1550.3 | 549.8 | 742.8 | 457 | 637.2 | 496.7
1770.3 | 1551.3 | 550.2 | 746.2 | 456.8 | 633 | 497.6
1771.3 | 1552.3 | 550.4 | 742.3 | 451.2 | 628.5 | 496.3
1772.3 | 1553.3 | 550.7 | 739.3 | 442.9 | 629.5 | 495.9
1773.3 | 1554.3 | 551.1 | 741.9 | 441.6 | 629.1 | 495.5
1774.3 | 1555.3 | 551.4 | 740.4 | 437.1 | 631.7 | 494.7
1775.3 | 1556.3 | 551.6 | 739.1 | 434.8 | 632.3 | 494
1776.3 | 1557.3 | 551.8 | 737.8 | 428.7 | 635.8 | 492.7
1777.3 | 1558.3 | 551.9 | 739.4 | 425.5 | 636.6 | 491.2
1778.3 | 1559.3 | 552.1 | 739.6 | 421.4 | 639 | 490.4
1779.3 | 1560.3 | 552.4 | 734.7 | 419.2 | 639.7 | 489.8
1780.3 | 1561.3 | 552.8 | 740.7 | 424.5 | 640.1 | 489.6
1781.3 | 1562.3 | 553.4 | 746.3 | 437.9 | 640.1 | 491.6
1782.3 | 1563.3 | 554.1 | 752.7 | 439.7 | 639.9 | 494
1783.3 | 1564.3 | 554.5 | 751.9 | 439.5 | 641.4 | 493.5
1784.3 | 1565.3 | 554.7 | 746.8 | 433.6 | 641 | 491.8
1785.3 | 1566.3 | 554.9 | 742.2 | 431.6 | 641.1 | 490.8
1786.3 | 1567.3 | 555.5 | 742.2 | 427.5 | 640 | 489.7
1787.3 | 1568.3 | 556.4 | 740.5 | 431.9 | 639.5 | 491.7
1788.3 | 1569.3 | 557 | 742.6 | 435.2 | 642.4 | 491.1
1789.3 | 1570.3 | 557.5 | 739.9 | 436 | 637.1 | 490.1
1790.3 | 1571.3 | 557.8 | 743.4 | 431.1 | 636.6 | 489.1
1791.3 | 1572.3 | 558.3 | 738.4 | 434.9 | 638.1 | 488.9
1792.3 | 1573.3 | 559.1 | 735.2 | 438.4 | 637.6 | 489.5
1793.3 | 1574.3 | 559.8 | 741 | 453.5 | 640 | 490.9
1794.3 | 1575.3 | 560.5 | 738.6 | 455.3 | 639.9 | 491.8
1795.3 | 1576.3 | 561.4 | 740.5 | 449.1 | 644.5 | 490.1
1796.3 | 1577.3 | 562.3 | 738.9 | 443.4 | 643.7 | 489.2
1797.3 | 1578.3 | 563.4 | 739.6 | 437.5 | 643.2 | 489.4
1798.3 | 1579.3 | 564.5 | 745.9 | 444.1 | 642.8 | 490.5
1799.3 | 1580.3 | 565.4 | 746.5 | 454.8 | 642.2 | 491.9
1800.3 | 1581.3 | 566.3 | 742.1 | 452.5 | 637.5 | 493.8
1801.3 | 1582.3 | 566.9 | 746.6 | 458.7 | 638.4 | 494.7
1802.3 | 1583.3 | 567.9 | 751.2 | 462.2 | 641.9 | 495.1
1803.3 | 1584.3 | 568.4 | 760.6 | 483.5 | 645.5 | 498.4
1804.3 | 1585.3 | 568.7 | 759 | 486.3 | 649.7 | 497.7
1805.3 | 1586.3 | 569.4 | 751.8 | 478.8 | 652.7 | 496.9
1806.3 | 1587.3 | 570.2 | 748.6 | 479.9 | 652.8 | 497.6
1807.3 | 1588.3 | 571.1 | 750.3 | 481.6 | 655 | 498.2
1808.3 | 1589.3 | 572 | 762 | 483.6 | 655.2 | 498.9
1809.3 | 1590.3 | 572.7 | 767.1 | 486.5 | 657.4 | 501
1810.3 | 1591.3 | 573.5 | 770.5 | 482.6 | 658.1 | 503
1811.3 | 1592.3 | 574 | 780.3 | 487.7 | 658.8 | 508.4
1812.3 | 1593.3 | 574.8 | 779.8 | 491.4 | 658.9 | 508.5
1813.3 | 1594.3 | 575.4 | 778.1 | 498.8 | 657.5 | 509.9
1814.3 | 1595.3 | 576 | 773.8 | 495.7 | 658.8 | 509.5
1815.3 | 1596.3 | 576.6 | 772.8 | 488.6 | 660.7 | 509.1
1816.3 | 1597.3 | 577.2 | 772 | 480.5 | 658.3 | 509.2
1817.3 | 1598.3 | 578 | 778.2 | 473.9 | 657.5 | 510.2
1818.3 | 1599.3 | 578.8 | 781.2 | 473.7 | 659.4 | 511.4
1819.3 | 1600.3 | 579.6 | 781.3 | 471.3 | 659.2 | 511.9
1820.3 | 1601.3 | 580.1 | 777 | 469.3 | 656.6 | 511.7
1821.3 | 1602.3 | 580.9 | 776.5 | 473.8 | 657.4 | 512.4
1822.3 | 1603.3 | 581.4 | 772.9 | 474.1 | 655.6 | 512.9
1823.3 | 1604.3 | 582 | 773.4 | 477.9 | 654.9 | 513.5
1824.3 | 1605.3 | 582.7 | 773.1 | 503.1 | 655.2 | 515.6
1825.3 | 1606.3 | 583.5 | 770.9 | 496.3 | 654.8 | 516.1
1826.3 | 1607.3 | 584 | 764 | 491.7 | 656.8 | 515.3
1827.3 | 1608.3 | 584.7 | 764.3 | 498 | 658.9 | 516.2
1828.3 | 1609.3 | 585.6 | 769.5 | 504.2 | 660.8 | 517.9
1829.3 | 1610.3 | 586.6 | 767.3 | 501.7 | 658.5 | 518.3
1830.3 | 1611.3 | 587.5 | 770.7 | 521.6 | 656.6 | 520.6
1831.3 | 1612.3 | 588.2 | 776.3 | 535.3 | 655.7 | 525.1
1832.3 | 1613.3 | 589 | 784.3 | 550.9 | 656.3 | 529.7
1833.3 | 1614.3 | 589.9 | 787.7 | 564.1 | 657.2 | 533.8
1834.3 | 1615.3 | 590.6 | 786.8 | 571.5 | 659 | 535.9
1835.3 | 1616.3 | 591.5 | 788.4 | 576.9 | 659.9 | 539.6
1836.3 | 1617.3 | 592.3 | 789 | 596.5 | 658.5 | 546.2
1837.3 | 1618.3 | 593 | 784.8 | 619.6 | 657.4 | 552.6
1838.3 | 1619.3 | 593.8 | 781.6 | 629.3 | 656.2 | 555.3
1839.3 | 1620.3 | 594.5 | 784.3 | 639.9 | 657.2 | 558
1840.3 | 1621.3 | 595.5 | 786 | 661.3 | 658.9 | 559.5
1841.3 | 1622.3 | 596.2 | 792.5 | 683.6 | 660 | 564.5
1842.3 | 1623.3 | 597.3 | 790.6 | 697.4 | 660.7 | 566.3
1843.3 | 1624.3 | 598.5 | 789.6 | 691.5 | 661.1 | 570.6
1844.3 | 1625.3 | 599.7 | 789.5 | 678.9 | 663.2 | 575.2
1845.3 | 1626.3 | 601 | 786.7 | 665.4 | 663.2 | 578.7
1846.3 | 1627.3 | 602.5 | 784.6 | 651.2 | 664.1 | 579.2
1847.3 | 1628.3 | 603.6 | 780.7 | 645.2 | 660.8 | 581.3
1848.3 | 1629.3 | 604.7 | 774.4 | 639.1 | 660.2 | 580.7
1849.3 | 1630.3 | 605.7 | 772 | 614.9 | 660.7 | 578.8
1850.3 | 1631.3 | 606.8 | 767.5 | 604.7 | 661.9 | 577.2
1851.3 | 1632.3 | 607.7 | 759.7 | 594 | 662.5 | 576
1852.3 | 1633.3 | 608.7 | 758.5 | 586.3 | 665.2 | 574.1
1853.3 | 1634.3 | 610.1 | 758.4 | 591.5 | 665.6 | 574.4
1854.3 | 1635.3 | 611.2 | 762.3 | 620.9 | 664.7 | 577.8
1855.3 | 1636.3 | 612 | 762.9 | 633.5 | 663.9 | 581.7
1856.3 | 1637.3 | 613 | 759.2 | 630.1 | 661.8 | 583.6
1857.3 | 1638.3 | 614.1 | 759.2 | 614.3 | 662.6 | 582.6
1858.3 | 1639.3 | 615.3 | 762.9 | 607.8 | 665.1 | 581.9
1859.3 | 1640.3 | 616.3 | 769.3 | 599.1 | 668.2 | 584.5
1860.3 | 1641.3 | 617.3 | 772.9 | 614.2 | 670.8 | 586.7
1861.3 | 1642.3 | 618.3 | 771.8 | 603.5 | 670.1 | 588.8
1862.3 | 1643.3 | 619.5 | 765.4 | 602 | 669.9 | 587.7
1863.3 | 1644.3 | 620.6 | 765.5 | 610.3 | 669 | 587.4
1864.3 | 1645.3 | 621.6 | 758.7 | 611.5 | 667.2 | 586.1
1865.3 | 1646.3 | 622.5 | 759.4 | 617.6 | 667.2 | 587.7
1866.3 | 1647.3 | 623.5 | 761.4 | 611.1 | 666.8 | 587.6
1867.3 | 1648.3 | 624.6 | 752.3 | 598.2 | 664.7 | 586.3
1868.3 | 1649.3 | 625.6 | 749.3 | 592.8 | 663.3 | 585.3
1869.3 | 1650.3 | 626.2 | 740.8 | 582.4 | 662 | 583.2
1870.3 | 1651.3 | 626.5 | 729.2 | 567.4 | 662.2 | 580
1871.3 | 1652.3 | 627.3 | 731.4 | 571.1 | 663.8 | 579.1
1872.3 | 1653.3 | 628.4 | 738 | 571.8 | 663.2 | 580.1
1873.3 | 1654.3 | 629.7 | 737.8 | 574.6 | 661.5 | 581.2
1874.3 | 1655.3 | 630.6 | 743 | 604.3 | 661.1 | 583.9
1875.3 | 1656.3 | 631.6 | 744.1 | 613.4 | 662 | 584.4
1876.3 | 1657.3 | 632.7 | 732.9 | 605.4 | 658.9 | 583
1877.3 | 1658.3 | 633.5 | 723.5 | 584.3 | 658.4 | 580.1
1878.3 | 1659.3 | 634.3 | 716 | 571.4 | 657.1 | 577.6
1879.3 | 1660.3 | 635.3 | 709.4 | 561.6 | 657.5 | 575.6
1880.3 | 1661.3 | 636.2 | 710.4 | 566.8 | 658.8 | 574.6
1881.3 | 1662.3 | 637 | 713.2 | 581.9 | 660.3 | 574.6
1882.3 | 1663.3 | 637.9 | 713.3 | 578.5 | 660.4 | 574.1
1883.3 | 1664.3 | 639 | 716.6 | 582.9 | 661.6 | 574.1
1884.3 | 1665.3 | 639.6 | 728.6 | 599 | 660.5 | 576.9
1885.3 | 1666.3 | 640.4 | 740 | 607.4 | 660.2 | 580.1
1886.3 | 1667.3 | 641.2 | 747.4 | 611.4 | 660.1 | 583.9
1887.3 | 1668.3 | 642.3 | 750.1 | 612 | 658.2 | 588.7
1888.3 | 1669.3 | 643.2 | 755.6 | 613.9 | 658.2 | 593.1
1889.3 | 1670.3 | 643.6 | 758.4 | 640.5 | 658.2 | 597.4
1890.3 | 1671.3 | 643.7 | 762.9 | 668 | 659.2 | 604.1
1891.3 | 1672.3 | 644 | 761.7 | 682.1 | 659.4 | 603.1
1892.3 | 1673.3 | 645.1 | 761.5 | 684.8 | 659.4 | 604.7
1893.3 | 1674.3 | 646 | 762.4 | 706.3 | 658.7 | 607.1
1894.3 | 1675.3 | 646.2 | 771.8 | 727.7 | 658.7 | 612.6
1895.3 | 1676.3 | 646.8 | 779.5 | 724.2 | 660.3 | 616.7
1896.3 | 1677.3 | 647.8 | 780.8 | 732.7 | 659.7 | 617.1
1897.4 | 1678.4 | 648.8 | 774.4 | 731.5 | 657.1 | 618.2
1898.4 | 1679.4 | 649.8 | 772.8 | 726.3 | 656.3 | 620
1899.4 | 1680.4 | 650.5 | 776.2 | 743.8 | 657.5 | 621.5
1900.4 | 1681.4 | 651.3 | 780.3 | 764.8 | 658.7 | 625.1
1901.4 | 1682.4 | 652.1 | 780.6 | 764.6 | 660.7 | 630.2
1902.4 | 1683.4 | 653.6 | 774.9 | 745 | 660.1 | 629.4
1903.4 | 1684.4 | 655 | 767.6 | 724.5 | 660.2 | 627.1
1904.4 | 1685.4 | 656.7 | 760.8 | 703.9 | 659.1 | 627.9
1905.4 | 1686.4 | 658 | 761.8 | 692 | 659.8 | 629.2
1906.4 | 1687.4 | 658.7 | 763.4 | 697.4 | 659.1 | 630
1907.4 | 1688.4 | 659.7 | 766.7 | 697 | 659.6 | 632.9
1908.4 | 1689.4 | 660.7 | 760 | 689.6 | 658.3 | 630.8
1909.4 | 1690.4 | 662 | 753.2 | 681.5 | 657.4 | 628.7
1910.4 | 1691.4 | 663 | 752.2 | 689.4 | 656.9 | 628.2
1911.4 | 1692.4 | 663.8 | 749.5 | 693.7 | 655.7 | 627.2
1912.4 | 1693.4 | 665 | 748.9 | 686.4 | 655.5 | 626.4
1913.4 | 1694.4 | 665.9 | 748.9 | 679.5 | 655.3 | 626.2
1914.4 | 1695.4 | 667.1 | 744.6 | 671.7 | 655.6 | 625.4
1915.4 | 1696.4 | 668.3 | 743.9 | 673 | 656.7 | 624.7
1916.4 | 1697.4 | 669 | 744.6 | 673.9 | 657 | 624.7
1917.4 | 1698.4 | 669.7 | 750.2 | 679.9 | 659 | 626
1918.4 | 1699.4 | 670.6 | 751.2 | 684.6 | 659.2 | 627.3
1919.4 | 1700.4 | 671.6 | 753.5 | 691.3 | 658.3 | 628.6
1920.4 | 1701.4 | 672.5 | 752 | 697.5 | 657.1 | 628.3
1921.4 | 1702.4 | 673.7 | 755.1 | 681.8 | 659.1 | 629.3
1922.4 | 1703.4 | 674.9 | 757.6 | 683.7 | 660 | 632.8
1923.4 | 1704.4 | 675.5 | 760 | 699.5 | 660.6 | 633.5
1924.4 | 1705.4 | 675.9 | 769.1 | 710 | 660.8 | 636.9
1925.4 | 1706.4 | 676.3 | 776.5 | 701.9 | 663.3 | 641.2
1926.4 | 1707.4 | 676.8 | 780.2 | 711.4 | 664.7 | 643.9
1927.4 | 1708.4 | 677.2 | 784.3 | 734 | 666.8 | 649.9
1928.4 | 1709.4 | 677.7 | 784 | 743.8 | 668.8 | 655.5
1929.4 | 1710.4 | 678.6 | 783.1 | 734.1 | 668.2 | 658.7
1930.4 | 1711.4 | 680.2 | 781.8 | 719.6 | 669.1 | 660.1
1931.4 | 1712.4 | 681.6 | 779.4 | 719.1 | 670.5 | 660.9
1932.4 | 1713.4 | 682.3 | 776.4 | 729.5 | 670.8 | 664.9
1933.4 | 1714.4 | 683.1 | 778.8 | 726.4 | 671 | 666.1
1934.4 | 1715.4 | 683.9 | 779.9 | 731.3 | 670.9 | 666
1935.4 | 1716.4 | 684.1 | 783.9 | 756.2 | 672.5 | 666.8
1936.4 | 1717.4 | 685.2 | 775.8 | 751.7 | 671.5 | 665.1
1937.4 | 1718.4 | 686.4 | 776.6 | 757.7 | 672.9 | 664.9
1938.4 | 1719.4 | 687.3 | 778.1 | 761.3 | 673.8 | 664.1
1939.4 | 1720.4 | 688.3 | 779.5 | 759.8 | 675.3 | 664.5
1940.4 | 1721.4 | 688.8 | 789.1 | 772.5 | 677.1 | 666.6
1941.4 | 1722.4 | 689.4 | 797.4 | 786.6 | 679.1 | 669.3
1942.4 | 1723.4 | 690.1 | 797 | 791.8 | 681.5 | 674.5
1943.4 | 1724.4 | 690.8 | 795.8 | 792.8 | 681.6 | 678.8
1944.4 | 1725.4 | 691.9 | 796.9 | 781.7 | 681.4 | 678.2
1945.4 | 1726.4 | 692.9 | 798 | 778.6 | 682.1 | 682
1946.4 | 1727.4 | 693.5 | 803 | 787.6 | 683 | 683.9
1947.4 | 1728.4 | 694.5 | 795.8 | 777.3 | 681.3 | 682.5
1948.4 | 1729.4 | 696 | 784.5 | 762.5 | 678.7 | 679.8
1949.4 | 1730.4 | 697.5 | 779.8 | 750.2 | 677.2 | 679.4
1950.4 | 1731.4 | 698.3 | 781.8 | 760 | 676.9 | 683.1
1951.4 | 1732.4 | 699.6 | 773 | 746.7 | 674.9 | 681.7
1952.4 | 1733.4 | 700.9 | 772 | 747.7 | 675.8 | 683.3
1953.4 | 1734.4 | 702 | 767.6 | 736.6 | 676.5 | 681.3
1954.4 | 1735.4 | 703.2 | 770.2 | 737.9 | 675.5 | 682.3
1955.4 | 1736.4 | 704.2 | 768.2 | 733.6 | 674.6 | 683.8
1956.4 | 1737.4 | 705 | 770.5 | 723.7 | 675 | 685.5
1957.4 | 1738.4 | 705.4 | 750.3 | 710.3 | 673 | 680.3
1958.4 | 1739.4 | 706.6 | 737.2 | 689.1 | 672.7 | 675.8
1959.4 | 1740.4 | 708 | 740.7 | 675.9 | 674.6 | 674.6
1960.4 | 1741.4 | 708.7 | 742.6 | 687.2 | 674.5 | 674
1961.4 | 1742.4 | 709.9 | 737.2 | 669.3 | 674.9 | 670.9
1962.4 | 1743.4 | 711 | 736.9 | 656.4 | 675.3 | 670.1
1963.4 | 1744.4 | 712.2 | 738.8 | 642.8 | 675.5 | 668.2
1964.4 | 1745.4 | 713.1 | 743.5 | 638 | 677 | 669
1965.4 | 1746.4 | 713.6 | 750.3 | 650.5 | 680 | 671.1
1966.4 | 1747.4 | 714 | 756.9 | 661.6 | 682 | 673.2
1967.4 | 1748.4 | 714.3 | 767.1 | 675.3 | 682.9 | 677.8
1968.4 | 1749.4 | 714.6 | 771.6 | 681.7 | 685.3 | 678
1969.4 | 1750.4 | 715 | 775.6 | 694.8 | 688.3 | 679.8
1970.4 | 1751.4 | 715.2 | 778.5 | 700 | 688.9 | 682.2
1971.4 | 1752.4 | 715.9 | 777.3 | 699.9 | 690.4 | 681.5
1972.4 | 1753.4 | 716.6 | 775.5 | 692.8 | 690.3 | 682.7
1973.4 | 1754.4 | 717.2 | 779.8 | 694 | 691.5 | 684.2
1974.4 | 1755.4 | 717.4 | 782.3 | 719.7 | 692.7 | 689
1975.4 | 1756.4 | 718.3 | 778.4 | 727.3 | 693.7 | 689.7
1976.4 | 1757.4 | 719 | 771.4 | 740.5 | 694.9 | 687.6
1977.4 | 1758.4 | 719.3 | 775.8 | 747.1 | 694.9 | 689.1
1978.4 | 1759.4 | 719.6 | 781.4 | 754.7 | 696.2 | 690.8
1979.4 | 1760.4 | 719.8 | 786.4 | 756.6 | 696.9 | 695
1980.4 | 1761.4 | 720.1 | 792.1 | 761.9 | 699.7 | 697.3
1981.4 | 1762.4 | 720.5 | 794.7 | 756.6 | 700.7 | 697.3
1982.4 | 1763.4 | 721.1 | 791.9 | 765.7 | 702.3 | 700.6
1983.4 | 1764.4 | 721.6 | 792.1 | 757.1 | 703.5 | 704.1
1984.4 | 1765.4 | 721.9 | 793.5 | 761.5 | 703.4 | 707.4
1985.4 | 1766.4 | 722.5 | 793 | 757.8 | 705.4 | 708.8
1986.4 | 1767.4 | 722.8 | 792.7 | 775.1 | 705.1 | 710
1987.4 | 1768.4 | 723.9 | 787.3 | 773 | 704.5 | 710.4
1988.4 | 1769.4 | 724.7 | 786.5 | 771.4 | 704.9 | 713.8
1989.4 | 1770.4 | 725.5 | 789.1 | 764.8 | 705 | 717.1
1990.4 | 1771.4 | 726.1 | 787.7 | 756.5 | 704.7 | 715.6
1991.4 | 1772.4 | 726.6 | 786.9 | 752.1 | 704.6 | 715.9
1992.4 | 1773.4 | 727.2 | 787.8 | 745.7 | 705 | 717.7
1993.4 | 1774.4 | 727.8 | 791.2 | 756.8 | 709.1 | 721.4
1994.4 | 1775.4 | 728.5 | 780.8 | 747.6 | 708.4 | 719.4
1995.4 | 1776.4 | 729.4 | 783.6 | 759.9 | 709.1 | 720.1
1996.4 | 1777.4 | 729.7 | 787 | 769.5 | 709.7 | 723.7
1997.4 | 1778.4 | 730.2 | 787.4 | 777.1 | 709.1 | 721.9
1998.4 | 1779.4 | 731.2 | 786.3 | 774.6 | 709.2 | 719.5
1999.4 | 1780.4 | 732.1 | 777.6 | 750.2 | 708.5 | 718.3
2000.4 | 1781.4 | 732.9 | 779.7 | 733.5 | 710.9 | 715.9
2001.4 | 1782.4 | 733.7 | 782.5 | 742.8 | 713.6 | 717.8
2002.4 | 1783.4 | 734.5 | 778.7 | 733.9 | 713.9 | 717.6
2003.4 | 1784.4 | 735.4 | 770.3 | 743.1 | 712.8 | 714.8
2004.4 | 1785.4 | 736.2 | 770.6 | 748.3 | 710.3 | 715.8
2005.4 | 1786.4 | 736.7 | 768.5 | 741.6 | 709.6 | 714.8
2006.4 | 1787.4 | 737.5 | 759.4 | 735.4 | 707.1 | 711.2
2007.4 | 1788.4 | 738.3 | 760.5 | 749.2 | 706.9 | 712.1
2008.4 | 1789.4 | 738.7 | 758 | 734.6 | 706.1 | 710.5
2009.4 | 1790.4 | 739.4 | 761.7 | 732.6 | 706.8 | 709.6
2010.4 | 1791.4 | 739.9 | 756.8 | 730.6 | 705.9 | 707.5
2011.4 | 1792.4 | 740.6 | 740.8 | 706.1 | 704.5 | 701.8
2012.4 | 1793.4 | 740.9 | 718 | 680 | 701.2 | 696.1
2013.4 | 1794.4 | 741.5 | 699.8 | 659.7 | 699 | 690.8
2014.4 | 1795.4 | 741.9 | 691.2 | 663 | 695.5 | 687.5
2015.4 | 1796.4 | 742.7 | 690.4 | 668.4 | 693.2 | 685.9
2016.4 | 1797.4 | 743.6 | 684.2 | 652.4 | 691.6 | 682.5
2017.4 | 1798.4 | 744.7 | 682.4 | 653.3 | 691.3 | 680.5
2018.4 | 1799.4 | 745.5 | 692.1 | 673.1 | 691.1 | 680.1
2019.4 | 1800.4 | 745.8 | 692.8 | 661.9 | 692.5 | 676.5
2020.4 | 1801.4 | 746.4 | 688.4 | 648.1 | 693.7 | 673.9
2021.4 | 1802.4 | 746.9 | 685.3 | 636.2 | 694.7 | 670.7
2022.4 | 1803.4 | 747.4 | 678.7 | 624.9 | 693.1 | 667.7
2023.4 | 1804.4 | 747.8 | 674.1 | 617.5 | 693.1 | 664.6
2024.4 | 1805.4 | 747.9 | 666.5 | 604.1 | 694.1 | 660.8
2025.4 | 1806.4 | 747.9 | 657.7 | 592.2 | 694.6 | 657.1
2026.4 | 1807.4 | 748.1 | 654 | 584.3 | 692.9 | 654.2
2027.4 | 1808.4 | 748.1 | 670.1 | 602.9 | 692.8 | 654.8
2028.4 | 1809.4 | 747.9 | 684.3 | 623.3 | 692.3 | 656.6
2029.4 | 1810.4 | 747.8 | 701 | 642.7 | 693.3 | 661.5
2030.4 | 1811.4 | 747.9 | 704.8 | 645.8 | 693.2 | 662.6
2031.4 | 1812.4 | 748.3 | 709.1 | 648.7 | 695 | 664.8
2032.4 | 1813.4 | 748 | 718.2 | 670 | 695.2 | 667.7
2033.4 | 1814.4 | 747.8 | 730.8 | 687.9 | 696.5 | 669.6
2034.4 | 1815.4 | 748 | 733 | 691.5 | 695.2 | 670.9
2035.4 | 1816.4 | 747.8 | 739.8 | 710.7 | 695 | 672.9
2036.4 | 1817.4 | 748 | 741.2 | 707 | 695.9 | 671.6
2037.4 | 1818.4 | 748.2 | 747.4 | 704.3 | 697.1 | 672.4
2038.4 | 1819.4 | 748.1 | 754.1 | 707.6 | 698.7 | 674.8
2039.4 | 1820.4 | 748.5 | 757.4 | 702.1 | 701.7 | 677.3
2040.4 | 1821.4 | 749 | 760.7 | 692.4 | 704.4 | 678.6
2041.4 | 1822.4 | 749.2 | 765.3 | 687.8 | 705.5 | 679.3
2042.4 | 1823.4 | 749.4 | 771.5 | 699.6 | 709 | 680.9
2043.4 | 1824.4 | 749.3 | 776.8 | 713.5 | 710.9 | 685.9
2044.4 | 1825.4 | 749.2 | 782.3 | 729.4 | 712.5 | 688.5
2045.4 | 1826.4 | 749.6 | 776.1 | 733.2 | 712.5 | 687
2046.4 | 1827.4 | 749.9 | 780.5 | 739 | 712.5 | 689.8
2047.4 | 1828.4 | 749.9 | 783 | 760.5 | 712.6 | 693.8
2048.4 | 1829.4 | 749.8 | 786.5 | 773 | 713.1 | 698
2049.4 | 1830.4 | 750 | 787.8 | 787 | 713.8 | 701.5
2050.4 | 1831.4 | 750.1 | 791.5 | 790.6 | 713.9 | 706.9
2051.4 | 1832.4 | 750.4 | 792.3 | 791.1 | 716.4 | 708.9
2052.4 | 1833.4 | 750.7 | 790.3 | 784 | 714.9 | 710.6
2053.4 | 1834.4 | 751.2 | 787 | 780.1 | 715.3 | 711.7
2054.4 | 1835.4 | 751.7 | 787.7 | 764.4 | 717.7 | 711.7
2055.4 | 1836.4 | 752.2 | 792.2 | 765.8 | 720.2 | 715.3
2056.4 | 1837.4 | 752.6 | 793.4 | 773.1 | 722.7 | 718.6
2057.4 | 1838.4 | 752.9 | 792.6 | 761.2 | 722.4 | 718.4
2058.4 | 1839.4 | 753.6 | 791.2 | 747.4 | 722.9 | 716.7
2059.4 | 1840.4 | 753.9 | 791.7 | 743.8 | 724.5 | 717.1
2060.4 | 1841.4 | 754.3 | 795 | 749.6 | 726.6 | 719.7
2061.4 | 1842.4 | 754.9 | 789.8 | 733.2 | 726.8 | 718.2
2062.4 | 1843.4 | 755.8 | 782.5 | 720.6 | 724.9 | 716.6
2063.4 | 1844.4 | 756.8 | 767.8 | 709.7 | 723 | 712
2064.4 | 1845.4 | 757.9 | 747.7 | 691.9 | 719.9 | 707.5
2065.4 | 1846.4 | 759 | 738.7 | 685.7 | 719.1 | 704.5
2066.4 | 1847.4 | 760 | 728.8 | 671.4 | 718.5 | 701
2067.4 | 1848.4 | 760.8 | 731.3 | 670.2 | 716 | 701.3
2068.4 | 1849.4 | 761.2 | 731.1 | 672.9 | 715.2 | 699.7
2069.4 | 1850.4 | 761.9 | 727 | 671.9 | 716.2 | 695.6
2070.4 | 1851.4 | 762.3 | 736.5 | 673.5 | 715.6 | 695.2
2071.4 | 1852.4 | 762.8 | 736.3 | 682.9 | 713.2 | 694.4
2072.4 | 1853.4 | 763 | 741.9 | 681.5 | 712.7 | 697
2073.4 | 1854.4 | 762.9 | 747.6 | 682.4 | 714.3 | 699.2
2074.4 | 1855.4 | 763.3 | 743.1 | 674.3 | 716 | 697.8
2075.4 | 1856.4 | 763.8 | 737.9 | 671.6 | 716.3 | 697.3
2076.4 | 1857.4 | 764.2 | 738.8 | 683.2 | 716.3 | 696.8
2077.4 | 1858.4 | 764.1 | 740 | 688.9 | 714.3 | 697.5
2078.4 | 1859.4 | 764 | 735.1 | 685.9 | 713.6 | 696.5
2079.4 | 1860.4 | 764.5 | 732.1 | 687.1 | 713.6 | 694.8
2080.4 | 1861.4 | 764.9 | 729.1 | 690.7 | 712 | 693.8
2081.4 | 1862.4 | 765.3 | 728.3 | 675.2 | 711 | 692.9
2082.4 | 1863.4 | 765.6 | 720.2 | 663.6 | 710.1 | 689
2083.4 | 1864.4 | 766.1 | 712.7 | 651.7 | 708.8 | 685.9
2084.4 | 1865.4 | 766.6 | 707.9 | 662.2 | 707.8 | 685.1
2085.4 | 1866.4 | 767.3 | 702.8 | 665 | 706 | 682.5
2086.4 | 1867.4 | 767.7 | 705.8 | 665.7 | 704.7 | 681
2087.4 | 1868.4 | 767.9 | 707.6 | 677.6 | 705.7 | 680.3
2088.4 | 1869.4 | 768 | 714.1 | 693.6 | 706.8 | 681.7
2089.4 | 1870.4 | 767.8 | 720.6 | 700.8 | 706.3 | 682.5
2090.4 | 1871.4 | 767.5 | 725.8 | 702.2 | 706.4 | 683.2
2091.4 | 1872.4 | 767.4 | 722 | 698.6 | 707.4 | 681.7
2092.4 | 1873.4 | 767.7 | 707.9 | 683.4 | 707.4 | 678.9
2093.4 | 1874.4 | 768 | 703.7 | 678.1 | 705.8 | 677
2094.4 | 1875.4 | 768.3 | 708.4 | 682.7 | 706.8 | 677.9
2095.4 | 1876.4 | 768.1 | 704.4 | 675.1 | 705.1 | 676.6
2096.4 | 1877.4 | 768.3 | 690.1 | 657 | 707.7 | 671.5
2097.4 | 1878.4 | 768.5 | 675.7 | 642.6 | 703.4 | 667.2
2098.4 | 1879.4 | 768.3 | 660.3 | 622.8 | 701.5 | 662.8
2099.4 | 1880.4 | 767.6 | 640.6 | 602.7 | 698.9 | 658.3
2100.4 | 1881.4 | 766.5 | 624.8 | 588.7 | 700.1 | 654.4
2101.4 | 1882.4 | 765.8 | 612.8 | 576.5 | 702.1 | 650.2
2102.4 | 1883.4 | 766.1 | 608.3 | 571.1 | 695.9 | 646.5
2103.4 | 1884.4 | 766.4 | 614.3 | 600.8 | 693.4 | 645.5
2104.4 | 1885.4 | 766.5 | 628.3 | 611.1 | 691.8 | 646.6
2105.4 | 1886.4 | 766.7 | 647.3 | 635 | 691.1 | 649
2106.4 | 1887.4 | 766.6 | 659.8 | 663.7 | 693.6 | 649.8
2107.4 | 1888.4 | 766.1 | 673.4 | 687 | 693.2 | 652.6
2108.4 | 1889.4 | 765.9 | 689.8 | 695 | 695.9 | 656.2
2109.4 | 1890.4 | 765.5 | 705.8 | 703.1 | 697.9 | 661.4
2110.4 | 1891.4 | 765.5 | 704 | 700.3 | 698.2 | 660.9
2111.4 | 1892.4 | 765.8 | 702.2 | 687.5 | 699.5 | 660.3
2112.4 | 1893.4 | 766.3 | 701.2 | 682 | 700.8 | 659.7
2113.4 | 1894.4 | 766.6 | 699.7 | 680.1 | 698.8 | 659
2114.4 | 1895.4 | 766.8 | 698.3 | 693.1 | 700.8 | 657.8
2115.4 | 1896.4 | 767.1 | 688.6 | 669.4 | 700.3 | 655.7
2116.4 | 1897.4 | 767.6 | 674.3 | 642.1 | 700.5 | 652.5
2117.4 | 1898.4 | 767.8 | 655.9 | 621.4 | 696.4 | 648.1
2118.4 | 1899.4 | 767.5 | 638.9 | 604.3 | 694.5 | 643.9
2119.4 | 1900.4 | 767.1 | 627 | 588.3 | 695.5 | 640
2120.4 | 1901.4 | 766.6 | 615.7 | 579.2 | 691.6 | 635.9
2121.4 | 1902.4 | 766.4 | 615 | 578.9 | 690.2 | 634.2
2122.4 | 1903.4 | 766.6 | 612.1 | 570.5 | 689.5 | 631.8
2123.4 | 1904.4 | 766.7 | 611.3 | 566.5 | 687.4 | 629.4
2124.4 | 1905.4 | 766.8 | 606.6 | 563 | 685.9 | 626.8
2125.4 | 1906.4 | 767 | 603 | 557.6 | 684 | 624.3
2126.4 | 1907.4 | 767 | 613.3 | 570.8 | 684.2 | 625.2
2127.4 | 1908.4 | 766.9 | 628.8 | 592.1 | 682.7 | 627.4
2128.4 | 1909.4 | 766.6 | 633.1 | 593.3 | 682.8 | 626.5
2129.4 | 1910.4 | 766.8 | 637.4 | 596.1 | 685.6 | 628.9
2130.4 | 1911.4 | 766.8 | 648.8 | 603.1 | 685.9 | 630.8
2131.4 | 1912.4 | 766.9 | 645.4 | 605.5 | 685.7 | 629.6
2132.4 | 1913.4 | 767.1 | 643.9 | 599.1 | 685.9 | 629
2133.4 | 1914.4 | 766.7 | 660.1 | 610.8 | 687.5 | 631.5
2134.4 | 1915.4 | 766.2 | 667.8 | 629.9 | 689.1 | 631.9
2135.4 | 1916.4 | 766.1 | 661.1 | 630.2 | 688.7 | 631.3
2136.4 | 1917.4 | 766.4 | 654.2 | 630 | 688.8 | 629.9
2137.4 | 1918.4 | 766.6 | 653.4 | 622.3 | 688.6 | 629.1
2138.4 | 1919.4 | 766.4 | 663 | 641.2 | 688.9 | 631
2139.4 | 1920.4 | 766.4 | 663 | 634.4 | 688.5 | 629.8
2140.4 | 1921.4 | 766.5 | 665.3 | 636.8 | 688.6 | 630.8
2141.4 | 1922.4 | 766.7 | 670.4 | 633 | 689.5 | 631.6
2142.4 | 1923.4 | 767 | 676.1 | 630.8 | 691.1 | 631.3
2143.4 | 1924.4 | 766.8 | 679.6 | 633.6 | 691.3 | 633.5
2144.4 | 1925.4 | 767.1 | 678.8 | 624.7 | 689.9 | 633.9
2145.4 | 1926.4 | 767.6 | 684.9 | 626.9 | 690.1 | 637.2
2146.4 | 1927.4 | 767.5 | 695.7 | 645.1 | 693.5 | 640.3
2147.4 | 1928.4 | 767.4 | 704.4 | 653.2 | 694 | 644.8
2148.4 | 1929.4 | 767.8 | 701.9 | 645.1 | 693.1 | 645.1
2149.4 | 1930.4 | 768 | 709.9 | 652.9 | 693.1 | 648.7
2150.4 | 1931.4 | 767.7 | 716.6 | 650.8 | 694.9 | 652.4
2151.4 | 1932.4 | 767.4 | 710.5 | 648.7 | 694.5 | 651.2
2152.4 | 1933.4 | 767.6 | 698.5 | 644 | 692.4 | 648.7
2153.4 | 1934.4 | 768 | 693.9 | 644 | 691 | 648.4
2154.4 | 1935.4 | 768.1 | 704.9 | 679.7 | 692.4 | 651.6
2155.4 | 1936.4 | 768 | 699.6 | 677.2 | 689 | 650.6
2156.4 | 1937.4 | 768.2 | 702.6 | 701.8 | 687.2 | 651.5
2157.4 | 1938.4 | 768.2 | 712.2 | 712.2 | 687.2 | 654.2
2158.4 | 1939.4 | 768.3 | 711.9 | 716 | 684.4 | 654.7
2159.4 | 1940.4 | 768.7 | 707.8 | 707.5 | 682.6 | 654.5
2160.4 | 1941.4 | 769.1 | 710.4 | 715.4 | 681.1 | 654.1
2161.4 | 1942.4 | 769.5 | 711.1 | 716.2 | 680.6 | 654.9
2162.4 | 1943.4 | 770 | 711.2 | 716.1 | 679.6 | 656.6
2163.4 | 1944.4 | 770.4 | 718.2 | 716 | 680.7 | 658.5
2164.4 | 1945.4 | 770.5 | 728.9 | 722.5 | 683.6 | 661.7
2165.4 | 1946.4 | 770.7 | 734.2 | 716.8 | 687 | 665.6
2166.4 | 1947.4 | 770.9 | 738.5 | 715.3 | 689.4 | 667.8
2167.4 | 1948.4 | 770.8 | 740.1 | 716.8 | 690.4 | 670.2
2168.4 | 1949.4 | 770.9 | 741.7 | 735.7 | 689.9 | 671
2169.4 | 1950.4 | 771.1 | 731.3 | 740.3 | 686.4 | 671.4
2170.4 | 1951.4 | 771.8 | 728.7 | 750.6 | 685.4 | 672.4
2171.4 | 1952.4 | 772.1 | 731.1 | 750.4 | 684 | 674.3
2172.4 | 1953.4 | 772.3 | 734.1 | 757.6 | 685.3 | 677.6
2173.4 | 1954.4 | 772.3 | 735.8 | 769.2 | 685.5 | 678.7
2174.4 | 1955.4 | 772.5 | 733.5 | 789 | 684.1 | 677.7
2175.4 | 1956.4 | 773.2 | 719.6 | 796.7 | 679.7 | 676.2
2176.4 | 1957.4 | 774.3 | 703.4 | 797.3 | 674.1 | 672.8
2177.4 | 1958.4 | 775.4 | 705.6 | 814.1 | 673.7 | 675.9
2178.4 | 1959.4 | 775.7 | 715.9 | 826.2 | 676.9 | 678
2179.4 | 1960.4 | 775.9 | 721.1 | 838.1 | 680.6 | 680.7
2180.4 | 1961.4 | 776.4 | 725.3 | 841.6 | 681.8 | 679.9
2181.4 | 1962.4 | 776.9 | 727 | 842.2 | 680.5 | 677.3
2182.4 | 1963.4 | 777.6 | 728.9 | 850.2 | 681.1 | 679.3
2183.4 | 1964.4 | 778 | 736.5 | 845.6 | 681.6 | 683.7
2184.4 | 1965.4 | 778.4 | 741.6 | 855.7 | 683.6 | 686.7
2185.4 | 1966.4 | 778.8 | 749.7 | 862.8 | 687.3 | 692.7
2186.4 | 1967.4 | 778.9 | 752.7 | 865 | 689.9 | 695.9
2187.4 | 1968.4 | 779.3 | 752.4 | 855.1 | 691.4 | 699.8
2188.4 | 1969.4 | 779.5 | 759.1 | 850.6 | 695.1 | 705.5
2189.4 | 1970.4 | 779.9 | 758.3 | 835.8 | 696.5 | 708.5
2190.4 | 1971.4 | 780.4 | 760.7 | 825.9 | 697.2 | 711
2191.4 | 1972.4 | 780.9 | 757.1 | 825.1 | 695.9 | 712.9
2192.4 | 1973.4 | 781.6 | 752.4 | 818.8 | 693.7 | 715.5
2193.4 | 1974.4 | 782.4 | 745.7 | 804.5 | 689.8 | 716
2194.4 | 1975.4 | 783 | 743 | 807.4 | 687.4 | 715.9
2195.4 | 1976.4 | 783.9 | 733.3 | 824.3 | 684.5 | 715.5
2196.4 | 1977.4 | 784.9 | 730.8 | 841.3 | 681.8 | 717.3
2197.4 | 1978.4 | 785.5 | 731.5 | 847.1 | 681.9 | 717.7
2198.4 | 1979.4 | 786.1 | 737.6 | 840.4 | 683.1 | 720.8
2199.4 | 1980.4 | 786.8 | 734.8 | 828.9 | 681.8 | 721.1
2200.4 | 1981.4 | 787.6 | 730.9 | 809.1 | 679.7 | 718.7
2201.4 | 1982.4 | 788.4 | 730.2 | 802 | 679.2 | 720.3
2202.4 | 1983.4 | 788.8 | 733.4 | 800.3 | 679.1 | 720.8
2203.4 | 1984.4 | 789.2 | 737.1 | 799.6 | 679.2 | 721.5
2204.4 | 1985.4 | 789.2 | 741.3 | 796.4 | 681.9 | 721.9
2205.4 | 1986.4 | 789.5 | 735.3 | 796.9 | 681 | 720.3
2206.4 | 1987.4 | 789.5 | 733.7 | 801.3 | 681.4 | 720.1
2207.4 | 1988.4 | 789.8 | 728.9 | 774.8 | 678.6 | 719.1
2208.4 | 1989.4 | 790.2 | 726.3 | 762.9 | 677.9 | 718.1
2209.4 | 1990.4 | 790.6 | 731.9 | 769.1 | 681 | 718.4
2210.4 | 1991.4 | 790.8 | 733.4 | 771.1 | 680.9 | 717
2211.4 | 1992.4 | 791.2 | 735.8 | 758.3 | 682 | 718.8
2212.4 | 1993.4 | 791.9 | 727.9 | 745.5 | 677.8 | 715.6
2213.4 | 1994.4 | 792.7 | 715 | 736.2 | 672.2 | 711.1
2214.4 | 1995.4 | 793.8 | 702.6 | 732.2 | 666.3 | 707.6
2215.4 | 1996.4 | 794.5 | 697.4 | 728.7 | 663.6 | 706.2
2216.4 | 1997.4 | 794.8 | 693.9 | 726.3 | 661.7 | 702.7
2217.4 | 1998.4 | 794.9 | 692.9 | 727 | 662 | 701.5
2218.4 | 1999.4 | 795.3 | 690.5 | 730.1 | 661.6 | 700.4
2219.4 | 2000.4 | 795.9 | 689.6 | 717.8 | 659.3 | 698.6
2220.4 | 2001.4 | 796 | 687.9 | 713.3 | 657.8 | 696
2221.4 | 2002.4 | 796.2 | 675 | 699.6 | 653.4 | 692.3
2222.4 | 2003.4 | 796.8 | 665.8 | 681.6 | 647.1 | 688.8
2223.4 | 2004.4 | 796.9 | 677.6 | 687.2 | 650.6 | 689.6
2224.4 | 2005.4 | 796.5 | 674.9 | 684.9 | 650.2 | 687.7
2225.4 | 2006.4 | 796.8 | 670.4 | 677.5 | 647.9 | 685.8
2226.4 | 2007.4 | 797.2 | 662.7 | 670.9 | 645.1 | 683.3
2227.4 | 2008.4 | 797.8 | 653.5 | 657.2 | 640.3 | 679.4
2228.4 | 2009.4 | 798.4 | 654.1 | 666.7 | 638.5 | 677.6
2229.4 | 2010.4 | 798.4 | 666.8 | 683 | 644 | 679.4
2230.4 | 2011.4 | 798 | 679.4 | 683.9 | 648.5 | 682.6
2231.4 | 2012.4 | 797.8 | 687.8 | 691.1 | 651.9 | 684.8
2232.4 | 2013.4 | 797.4 | 695.8 | 706.7 | 655.6 | 686.6
2233.4 | 2014.4 | 797.3 | 687.2 | 689.8 | 652.2 | 682.4
2234.4 | 2015.4 | 797.5 | 688.5 | 695.1 | 652 | 683.1
2235.4 | 2016.4 | 797.3 | 697.8 | 685.3 | 655.2 | 684
2236.4 | 2017.4 | 796.9 | 702.3 | 681.8 | 658 | 683.5
2237.4 | 2018.4 | 796.5 | 702.5 | 688.9 | 658.1 | 683.4
2238.4 | 2019.4 | 796.4 | 701.3 | 695.8 | 658.5 | 683.6
2239.4 | 2020.4 | 796.5 | 699.4 | 708.2 | 657.7 | 683.2
2240.4 | 2021.4 | 796.7 | 697.5 | 707.9 | 656.1 | 681.7
2241.4 | 2022.4 | 796.8 | 703.8 | 728.6 | 658.5 | 684.2
2242.4 | 2023.4 | 796.5 | 706.4 | 737.4 | 658.9 | 686.7
2243.4 | 2024.4 | 796.2 | 718 | 760 | 664 | 691
2244.4 | 2025.4 | 795.9 | 725.2 | 787.8 | 667.8 | 692.9
2245.4 | 2026.4 | 795.7 | 721 | 803.8 | 666.8 | 691.4
2246.4 | 2027.4 | 795.9 | 726.5 | 822.3 | 668.9 | 695.7
2247.4 | 2028.4 | 796.1 | 731 | 806.4 | 669.3 | 699.3
2248.4 | 2029.4 | 796.7 | 731.2 | 778.8 | 669.4 | 701.4
2249.4 | 2030.4 | 797 | 724 | 770.9 | 667 | 701.7
2250.4 | 2031.4 | 797.2 | 727.9 | 789.5 | 670.7 | 705.1
2251.4 | 2032.4 | 796.8 | 733.7 | 790 | 674.1 | 706.8
2252.4 | 2033.4 | 796.6 | 734.6 | 792.1 | 673.9 | 705.9
2253.4 | 2034.4 | 796.3 | 736.2 | 781.8 | 674.9 | 706.9
2254.4 | 2035.4 | 796.7 | 725.5 | 773.8 | 671.7 | 705.9
2255.4 | 2036.4 | 796.9 | 734.2 | 786.6 | 675.8 | 710.7
2256.4 | 2037.4 | 796.7 | 737.1 | 769 | 677.4 | 713.7
2257.4 | 2038.4 | 796.8 | 734.3 | 755.4 | 676.4 | 711.7
2258.4 | 2039.4 | 797.4 | 709.4 | 715.5 | 666.4 | 704.6
2259.4 | 2040.4 | 798.1 | 671.6 | 672.6 | 651.1 | 695.8
2260.4 | 2041.4 | 797.9 | 635.6 | 638.9 | 636.1 | 687.7
2261.4 | 2042.4 | 797 | 606.3 | 605.3 | 620.7 | 680.9
2262.4 | 2043.4 | 796.3 | 581.1 | 574.1 | 608.9 | 673.9
2263.4 | 2044.4 | 795.6 | 560 | 550 | 598 | 666.7
2264.4 | 2045.4 | 794.6 | 539.4 | 525.9 | 586.3 | 660.1
2265.4 | 2046.4 | 793.6 | 521.3 | 504.2 | 575.7 | 653.7
2266.4 | 2047.4 | 792.6 | 506.5 | 483.4 | 569.3 | 648
2267.4 | 2048.4 | 791.2 | 493.3 | 467.7 | 563.7 | 642.2
2268.4 | 2049.4 | 789.7 | 481.3 | 450.6 | 557.4 | 636.7
2269.4 | 2050.4 | 788.2 | 468.8 | 436.5 | 551.9 | 631.4
2270.4 | 2051.4 | 786.5 | 459.8 | 424.8 | 546.6 | 626.3
2271.4 | 2052.4 | 784.9 | 449.5 | 413.1 | 540.2 | 620.9
2272.4 | 2053.4 | 783.7 | 439.7 | 399.7 | 534.2 | 615.6
2273.4 | 2054.4 | 782.5 | 432.7 | 388.4 | 530.4 | 611.4
2274.4 | 2055.4 | 780.7 | 426 | 379.3 | 526.2 | 607.4
2275.4 | 2056.4 | 778.8 | 419.3 | 369.9 | 522 | 603.3
2276.4 | 2057.4 | 776.6 | 414.8 | 362.5 | 517.9 | 599.3
2277.4 | 2058.4 | 774.6 | 410.1 | 354.5 | 513.7 | 595
2278.4 | 2059.4 | 772.6 | 405.2 | 347.6 | 510.1 | 591.1
2279.4 | 2060.4 | 770.6 | 401.3 | 340.9 | 506.8 | 587.7
2280.4 | 2061.4 | 768.6 | 397.7 | 335.6 | 502.9 | 584.1
2281.4 | 2062.4 | 766.4 | 395.7 | 331.4 | 500.9 | 580.2
2282.4 | 2063.4 | 764.3 | 394.3 | 325.7 | 498.9 | 576.2
2283.4 | 2064.4 | 762.2 | 392 | 320 | 495.9 | 572.8
2284.4 | 2065.4 | 760.2 | 387.7 | 314.4 | 493.7 | 569.4
2285.4 | 2066.4 | 758.2 | 383.4 | 310.2 | 490.8 | 566.1
2286.4 | 2067.4 | 756.5 | 378.4 | 304.3 | 488.6 | 562.7
2287.4 | 2068.4 | 754.8 | 375.4 | 301.2 | 486.4 | 559.4
2288.4 | 2069.4 | 752.8 | 372.7 | 297.3 | 484.1 | 557
2289.4 | 2070.4 | 750.9 | 370.7 | 293.3 | 481.6 | 554.1
2290.4 | 2071.4 | 749 | 367.9 | 289.6 | 479.3 | 551.1
2291.4 | 2072.4 | 747 | 365.4 | 287.3 | 476.6 | 548.3
2292.4 | 2073.4 | 745 | 362.5 | 284.7 | 474.9 | 545.3
2293.4 | 2074.4 | 743.2 | 359.3 | 280.3 | 471.6 | 542.4
2294.4 | 2075.4 | 741.3 | 357.8 | 276.5 | 468.8 | 539.5
2295.4 | 2076.4 | 739.3 | 357.1 | 275.5 | 466.7 | 537.3
2296.4 | 2077.4 | 737.3 | 356 | 272.9 | 465.2 | 535
2297.4 | 2078.4 | 735.8 | 352.2 | 268.6 | 462.9 | 532.4
2298.4 | 2079.4 | 734.3 | 349 | 265.1 | 461.4 | 529.1
2299.4 | 2080.4 | 732.5 | 347.8 | 261.6 | 460.9 | 526.7
2300.4 | 2081.4 | 730.8 | 347.8 | 258.7 | 459.2 | 524.9
2301.4 | 2082.4 | 729.1 | 347.8 | 256.5 | 457.4 | 522.4
2302.4 | 2083.4 | 727.2 | 348.4 | 254.4 | 457.3 | 520.5
2303.4 | 2084.4 | 725.4 | 347.5 | 253.2 | 455.4 | 518.8
2304.4 | 2085.4 | 723.7 | 346.9 | 251.7 | 455.1 | 517
2305.4 | 2086.4 | 722 | 346.5 | 251.6 | 454.3 | 515.1
2306.4 | 2087.4 | 720.3 | 345.6 | 249.5 | 453.8 | 513.4
2307.4 | 2088.4 | 718.8 | 343.7 | 249 | 449.7 | 511.7
2308.4 | 2089.4 | 717.1 | 342.2 | 247.9 | 448.2 | 509.4
2309.4 | 2090.4 | 715.5 | 339.4 | 245.5 | 446.6 | 506.9
2310.4 | 2091.4 | 713.9 | 337.6 | 243.7 | 445 | 504.2
2311.4 | 2092.4 | 712.1 | 337 | 243 | 443.3 | 501.6
2312.4 | 2093.4 | 710.4 | 335.9 | 242.7 | 442.3 | 499.9
2313.4 | 2094.4 | 708.7 | 335.5 | 242.2 | 441.6 | 498.2
2314.4 | 2095.4 | 707.1 | 335.1 | 240.6 | 440.2 | 496.4
2315.4 | 2096.4 | 705.5 | 333.9 | 238.2 | 439 | 494.6
2316.4 | 2097.4 | 704.3 | 331.3 | 236.5 | 436 | 492.6
2317.4 | 2098.4 | 703 | 329.7 | 235.1 | 435.1 | 490.8
2318.4 | 2099.4 | 701.6 | 327.3 | 233.2 | 434.6 | 488.4
2319.4 | 2100.4 | 700.1 | 326.8 | 232 | 433.7 | 486.7
2320.4 | 2101.4 | 698.7 | 327.3 | 230.1 | 432.6 | 485.2
2321.4 | 2102.4 | 697.3 | 326.7 | 228.1 | 432.1 | 483.6
2322.4 | 2103.4 | 695.9 | 326.7 | 226.9 | 431.7 | 482.1
2323.4 | 2104.4 | 694.4 | 327.3 | 225.7 | 431 | 480.6
2324.4 | 2105.4 | 692.8 | 327.3 | 224.4 | 430.1 | 479.4
2325.4 | 2106.4 | 691.3 | 326.6 | 223.9 | 429 | 478
2326.4 | 2107.4 | 689.9 | 326 | 222.8 | 429.5 | 476.5
2327.4 | 2108.4 | 688.6 | 325 | 220.9 | 427.4 | 475.1
2328.4 | 2109.4 | 687.3 | 324.9 | 220.9 | 425.8 | 473.2
2329.4 | 2110.4 | 686 | 325.1 | 220.2 | 424.8 | 471.8
2330.4 | 2111.4 | 684.6 | 324.8 | 218.5 | 425.4 | 470.6
2331.4 | 2112.4 | 683.2 | 324.1 | 217.1 | 424.4 | 469.4
2332.4 | 2113.4 | 681.8 | 323.9 | 216.9 | 423.7 | 468
2333.4 | 2114.4 | 680.5 | 322.9 | 214.8 | 422.2 | 466.7
2334.4 | 2115.4 | 679.2 | 322.1 | 212.9 | 420.6 | 465.2
2335.4 | 2116.4 | 677.9 | 321.1 | 210.7 | 419.8 | 463
2336.4 | 2117.4 | 676.7 | 319.7 | 209 | 419.2 | 461
2337.4 | 2118.4 | 675.4 | 319.3 | 207.3 | 418.3 | 459.3
2338.4 | 2119.4 | 674.1 | 319.3 | 206.2 | 417.9 | 458.2
2339.4 | 2120.4 | 672.9 | 319.4 | 205.1 | 417.5 | 457.1
2340.4 | 2121.4 | 671.7 | 318.8 | 204.3 | 417.1 | 455.8
2341.4 | 2122.4 | 670.4 | 318.7 | 203.5 | 416.9 | 454.9
2342.4 | 2123.4 | 669.2 | 318.7 | 202.9 | 416 | 453.7
2343.4 | 2124.4 | 667.9 | 318.3 | 203.3 | 416.3 | 452.6
2344.4 | 2125.4 | 666.6 | 317.2 | 203.3 | 416.7 | 451.6
2345.4 | 2126.4 | 665.3 | 315.9 | 203.2 | 415.3 | 450.2
2346.4 | 2127.4 | 664 | 315.2 | 203.6 | 415.2 | 448.8
2347.4 | 2128.4 | 662.7 | 314.6 | 203.8 | 413.5 | 447.5
2348.4 | 2129.4 | 661.6 | 314.2 | 202.6 | 412 | 446.4
2349.4 | 2130.4 | 660.4 | 314 | 202 | 412.9 | 444.7
2350.4 | 2131.4 | 659.1 | 313.4 | 202.1 | 413.1 | 443.5
2351.4 | 2132.4 | 657.8 | 312.5 | 202 | 412.5 | 441.4
2352.4 | 2133.4 | 656.7 | 312.1 | 201.6 | 412.2 | 440.8
2353.4 | 2134.4 | 655.5 | 311.7 | 200.5 | 412 | 439.7
2354.4 | 2135.4 | 654.3 | 311 | 200.5 | 411.3 | 438.2
2355.4 | 2136.4 | 653.1 | 309.6 | 199.1 | 410.7 | 437.2
2356.4 | 2137.4 | 652 | 309 | 197.7 | 409 | 435.8
2357.4 | 2138.4 | 650.9 | 308.2 | 197.4 | 407.9 | 434.3
2358.4 | 2139.4 | 649.8 | 307.7 | 197.4 | 407.4 | 433.6
2359.4 | 2140.4 | 648.7 | 307 | 196.3 | 406.7 | 432.7
2360.4 | 2141.4 | 647.5 | 306.2 | 195.7 | 405.9 | 431.6
2361.4 | 2142.4 | 646.3 | 306.3 | 196.3 | 406.3 | 430.4
2362.4 | 2143.4 | 645.2 | 305.6 | 196.6 | 405 | 429.2
2363.4 | 2144.4 | 644.3 | 304.2 | 196.4 | 403.2 | 428.1
2364.4 | 2145.4 | 643.5 | 302.4 | 194.2 | 401.3 | 426.7
2365.4 | 2146.4 | 642.7 | 301.3 | 192.9 | 399.7 | 425.5
2366.4 | 2147.4 | 641.7 | 300.6 | 192.3 | 399.4 | 424.5
2367.4 | 2148.4 | 640.7 | 300 | 192.3 | 398.8 | 423.1
2368.4 | 2149.4 | 639.6 | 299.9 | 192.2 | 399.1 | 422.2
2369.4 | 2150.4 | 638.5 | 299.4 | 192.1 | 398 | 421.4
2370.4 | 2151.4 | 637.4 | 298.5 | 191.9 | 397.6 | 420.3
2371.4 | 2152.4 | 636.3 | 297.5 | 191.6 | 396.9 | 419.3
2372.4 | 2153.4 | 635.3 | 297.3 | 190.4 | 396.5 | 418.4
2373.4 | 2154.4 | 634.3 | 296.9 | 189.9 | 395.1 | 417.6
2374.4 | 2155.4 | 633.2 | 296.3 | 189.8 | 394.4 | 416.4
2375.4 | 2156.4 | 632.2 | 295.4 | 188.6 | 393.9 | 415.2
2376.4 | 2157.4 | 631.2 | 294.2 | 187 | 391.7 | 414.2
2377.4 | 2158.4 | 630.3 | 293.9 | 186.8 | 390.7 | 413.1
2378.4 | 2159.4 | 629.5 | 293.4 | 186.1 | 391.2 | 412.2
2379.4 | 2160.4 | 628.6 | 292.8 | 185.2 | 391.8 | 411.2
2380.4 | 2161.4 | 627.6 | 291.9 | 185.4 | 392.4 | 410.2
2381.4 | 2162.4 | 626.6 | 291.1 | 185 | 392.3 | 409.4
2382.4 | 2163.4 | 625.7 | 290.3 | 183.8 | 391.9 | 408.3
2383.4 | 2164.4 | 624.8 | 289.9 | 182.3 | 391 | 407.5
2384.4 | 2165.4 | 623.9 | 289.1 | 181.3 | 389.3 | 406.5
2385.4 | 2166.4 | 622.9 | 289.4 | 179.9 | 389.2 | 405.5
2386.4 | 2167.4 | 622 | 289.3 | 180.1 | 388.7 | 404.5
2387.4 | 2168.4 | 621.1 | 288.4 | 179.9 | 387.5 | 403.6
2388.4 | 2169.4 | 620.1 | 287.6 | 180.3 | 387.7 | 402.6
2389.4 | 2170.4 | 619.2 | 286.5 | 180.1 | 387.6 | 401.6
2390.4 | 2171.4 | 618.4 | 285.8 | 178.6 | 387 | 400.7
2391.4 | 2172.4 | 617.6 | 285.4 | 177.6 | 385.9 | 399.7
2392.4 | 2173.4 | 616.8 | 284.7 | 177 | 385.5 | 399
2393.4 | 2174.4 | 616 | 283.8 | 175.5 | 382.8 | 398
2394.4 | 2175.4 | 615.4 | 282.8 | 173.9 | 379.5 | 397.4
2395.4 | 2176.4 | 614.8 | 281.2 | 172.4 | 376.9 | 396
2396.4 | 2177.4 | 614.2 | 279.7 | 171.7 | 375.5 | 394.6
2397.4 | 2178.4 | 613.7 | 278.9 | 170.3 | 374.9 | 393.2
2398.4 | 2179.4 | 613.2 | 278.3 | 169.4 | 375.3 | 392.3
2399.4 | 2180.4 | 612.4 | 278.6 | 169.6 | 374.6 | 391.1
2400.4 | 2181.4 | 611.6 | 278.5 | 169.5 | 373.8 | 390.5
2401.4 | 2182.4 | 610.8 | 278.3 | 169.2 | 371.4 | 389.8
2402.4 | 2183.4 | 609.9 | 277.6 | 168.7 | 369.7 | 389.1
2403.4 | 2184.4 | 609.1 | 277 | 168.9 | 370.8 | 388.3
2404.4 | 2185.4 | 608.2 | 277.1 | 169.1 | 372.5 | 387.5
2405.4 | 2186.4 | 607.4 | 277.2 | 169.5 | 373.8 | 386.8
2406.4 | 2187.4 | 606.5 | 276.4 | 169.7 | 374 | 386.2
2407.4 | 2188.4 | 605.6 | 275.8 | 170.5 | 374 | 385.6
2408.4 | 2189.4 | 604.8 | 275.7 | 170.5 | 374 | 384.7
2409.4 | 2190.4 | 604 | 275.5 | 170.7 | 374.3 | 384
2410.4 | 2191.4 | 603.2 | 274.9 | 171.2 | 373.6 | 383.4
2411.4 | 2192.4 | 602.5 | 275.1 | 171.6 | 372.3 | 382.5
2412.4 | 2193.4 | 601.8 | 275.3 | 170.9 | 372.2 | 381.7
2413.4 | 2194.4 | 601.1 | 274.5 | 170.4 | 371.3 | 380.9
2414.4 | 2195.4 | 600.4 | 274 | 169.9 | 369.5 | 379.9
2415.4 | 2196.4 | 599.7 | 273.8 | 169 | 368.8 | 379.1
2416.4 | 2197.4 | 599 | 273.3 | 167.8 | 368.2 | 378.3
2417.4 | 2198.4 | 598.3 | 273.4 | 166.5 | 369 | 377.7
2418.4 | 2199.4 | 597.5 | 273.3 | 165.3 | 369.3 | 377.2
2419.4 | 2200.4 | 596.8 | 273.2 | 165.1 | 368.1 | 376.5
2420.4 | 2201.4 | 596.1 | 273 | 164.5 | 367 | 375.9
2421.4 | 2202.4 | 595.4 | 273.2 | 164.1 | 367.6 | 375.2
2422.4 | 2203.4 | 594.7 | 272.8 | 164.1 | 367.6 | 374.2
2423.4 | 2204.4 | 593.9 | 271.8 | 163.4 | 367.7 | 373.3
2424.4 | 2205.4 | 593.1 | 271.3 | 163.1 | 366.6 | 372.7
2425.4 | 2206.4 | 592.5 | 270.8 | 162.4 | 364.3 | 372
2426.4 | 2207.4 | 592 | 270.2 | 161.5 | 363.8 | 371.2
2427.4 | 2208.4 | 591.4 | 270 | 161.7 | 363.9 | 370.3
2428.4 | 2209.4 | 590.8 | 269.4 | 161.4 | 363 | 369.4
2429.4 | 2210.4 | 590.3 | 268.4 | 160.2 | 363.1 | 368.8
2430.4 | 2211.4 | 589.7 | 267.4 | 160.1 | 361.9 | 368
2431.4 | 2212.4 | 589.1 | 266.9 | 159.6 | 358.4 | 367.4
2432.4 | 2213.4 | 588.5 | 266.6 | 158.8 | 357.7 | 366.7
2433.4 | 2214.4 | 588 | 266.9 | 157.7 | 357.5 | 365.8
2434.4 | 2215.4 | 587.4 | 267 | 156.7 | 357.5 | 364.9
2435.4 | 2216.4 | 586.9 | 266.1 | 155 | 356.3 | 363.5
2436.4 | 2217.4 | 586.7 | 264.1 | 153.5 | 355.1 | 362.1
2437.4 | 2218.4 | 586.4 | 262.2 | 151.9 | 354 | 361.4
2438.4 | 2219.4 | 586.3 | 259.7 | 150.4 | 353.2 | 360.5
2439.4 | 2220.4 | 586.4 | 257.7 | 149 | 351.8 | 359.6
2440.4 | 2221.4 | 586.5 | 256.6 | 148.7 | 352.4 | 358
2441.4 | 2222.4 | 586.3 | 256.3 | 149.2 | 352.1 | 356.7
2442.4 | 2223.4 | 585.7 | 256.2 | 149 | 352.1 | 355.8
2443.4 | 2224.4 | 585 | 256.3 | 148.8 | 351.6 | 355.3
2444.4 | 2225.4 | 584.2 | 256.2 | 149.2 | 351.3 | 355.1
2445.4 | 2226.4 | 583.6 | 255.9 | 149.6 | 351.2 | 354.7
2446.4 | 2227.4 | 582.8 | 255.6 | 150 | 352 | 354.3
2447.4 | 2228.4 | 582.1 | 255.3 | 150.1 | 351.2 | 354
2448.4 | 2229.4 | 581.4 | 255.1 | 150.2 | 350.8 | 353.5
2449.4 | 2230.4 | 580.9 | 254.8 | 149.6 | 348.6 | 353
2450.4 | 2231.4 | 580.4 | 254.4 | 149.3 | 348.6 | 352.3
2451.4 | 2232.4 | 579.8 | 254.1 | 148.6 | 348.7 | 351.6
2452.4 | 2233.4 | 579.1 | 253.7 | 148.2 | 348.1 | 351.1
2453.4 | 2234.4 | 578.5 | 253.2 | 147.3 | 348.4 | 350.5
2454.4 | 2235.4 | 577.9 | 253 | 146.6 | 346.8 | 349.7
2455.4 | 2236.4 | 577.3 | 253.1 | 146.3 | 345.8 | 348.7
2456.4 | 2237.4 | 576.7 | 253.2 | 146 | 346.9 | 348.3
2457.4 | 2238.4 | 576.1 | 252.9 | 145.5 | 347.2 | 347.9
2458.4 | 2239.4 | 575.6 | 253 | 145.8 | 347.6 | 347.5
2459.4 | 2240.4 | 575.1 | 252.7 | 145.7 | 347.3 | 346.3
2460.4 | 2241.4 | 574.5 | 252.5 | 145.8 | 347.7 | 345.7
2461.4 | 2242.4 | 574 | 252.2 | 145.7 | 347.5 | 345.3
2462.4 | 2243.4 | 573.5 | 251.9 | 145 | 346.8 | 343.9
2463.4 | 2244.4 | 573 | 251.8 | 144.5 | 346.2 | 342.7
2464.4 | 2245.4 | 572.5 | 251.8 | 144.2 | 345.7 | 341.9
2465.4 | 2246.4 | 572 | 251.9 | 143.5 | 343.2 | 341.6
2466.4 | 2247.4 | 571.4 | 251.4 | 142.8 | 339.9 | 340.9
2467.4 | 2248.4 | 570.8 | 250.4 | 142.3 | 338 | 340.1
2468.4 | 2249.4 | 570.3 | 250.1 | 141.7 | 339.2 | 339.7
2469.4 | 2250.4 | 569.7 | 249.7 | 141.8 | 339.9 | 339.4
2470.4 | 2251.4 | 569.3 | 249.2 | 141.1 | 339.9 | 339.1
2471.4 | 2252.4 | 568.9 | 248.7 | 140.8 | 340.4 | 338.6
2472.4 | 2253.4 | 568.4 | 248.4 | 140.7 | 340.9 | 338
2473.4 | 2254.4 | 567.9 | 247.9 | 141.1 | 341.7 | 337.6
2474.4 | 2255.4 | 567.3 | 247.6 | 140.2 | 342.1 | 337.1
2475.4 | 2256.4 | 566.7 | 247.2 | 139.4 | 342.2 | 336.5
2476.4 | 2257.4 | 566.2 | 247.5 | 139.4 | 342 | 335.9
2477.4 | 2258.4 | 565.7 | 247.3 | 139.8 | 341.9 | 335.6
2478.4 | 2259.4 | 565.2 | 246.3 | 140.3 | 340.9 | 335.4
2479.4 | 2260.4 | 564.7 | 246.1 | 140.1 | 340.7 | 335
2480.4 | 2261.4 | 564.2 | 245.5 | 139.7 | 339.9 | 334.6
2481.4 | 2262.4 | 563.9 | 244.6 | 139.8 | 338.9 | 334.3
2482.4 | 2263.4 | 563.5 | 244.2 | 140 | 339.3 | 333.9
2483.4 | 2264.4 | 563.1 | 244.1 | 140 | 338.5 | 333.6
2484.4 | 2265.4 | 562.7 | 243.8 | 140.1 | 337.2 | 333.2
2485.4 | 2266.4 | 562.4 | 243 | 139.3 | 336.4 | 332.7
2486.4 | 2267.4 | 562 | 242.8 | 139.1 | 336.3 | 332.1
2487.4 | 2268.4 | 561.6 | 242.4 | 138.9 | 336.2 | 331.6
2488.4 | 2269.4 | 561.2 | 241.6 | 138.5 | 335.5 | 331.2
2489.4 | 2270.4 | 560.7 | 241.3 | 138.5 | 335.3 | 330.9
2490.4 | 2271.4 | 560.3 | 240.6 | 137.2 | 334.2 | 330.2
2491.4 | 2272.4 | 559.8 | 240.4 | 136.3 | 333.1 | 329.6
2492.4 | 2273.4 | 559.3 | 240.1 | 136 | 333.4 | 329
2493.4 | 2274.4 | 558.8 | 239.7 | 136.4 | 333.9 | 328.5
2494.4 | 2275.4 | 558.2 | 239.4 | 136.7 | 334 | 327.9
2495.4 | 2276.4 | 557.9 | 238.9 | 137 | 333.2 | 327.6
2496.4 | 2277.4 | 557.5 | 238.1 | 136.5 | 332.7 | 327.1
2497.4 | 2278.4 | 557.1 | 237.5 | 135.5 | 332.2 | 326.7
2498.4 | 2279.4 | 556.7 | 236.4 | 134.4 | 330.1 | 326.2
2499.4 | 2280.4 | 556.3 | 236.3 | 134.6 | 329.1 | 325.3
2500.4 | 2281.4 | 555.9 | 236.2 | 134.6 | 329.3 | 324.4
2501.4 | 2282.4 | 555.5 | 235.8 | 134.8 | 329.8 | 323.6
2502.4 | 2283.4 | 555.1 | 235.4 | 134.7 | 329.2 | 323.1
2503.4 | 2284.4 | 554.7 | 234.9 | 134.5 | 328.1 | 323
2504.4 | 2285.4 | 554.4 | 234.8 | 134.3 | 327.8 | 322.2
2505.4 | 2286.4 | 554 | 234.3 | 134.2 | 327 | 321.8
2506.4 | 2287.4 | 553.7 | 233.9 | 134.2 | 327.8 | 321.2
2507.4 | 2288.4 | 553.3 | 233.5 | 133.3 | 328.6 | 320.8
2508.4 | 2289.4 | 553 | 233.4 | 132.9 | 327.8 | 320.4
2509.4 | 2290.4 | 552.6 | 232.8 | 132.8 | 328 | 319.6
2510.4 | 2291.4 | 552.2 | 232.3 | 132.7 | 328 | 318.9
2511.4 | 2292.4 | 551.8 | 231.6 | 132.6 | 328.3 | 318.2
2512.4 | 2293.4 | 551.4 | 231.2 | 132.5 | 327.7 | 317.7
2513.4 | 2294.4 | 551.1 | 230.7 | 132.6 | 327.3 | 317.4
2514.4 | 2295.4 | 550.7 | 230.2 | 132.1 | 326.7 | 317.1
2515.4 | 2296.4 | 550.4 | 229.6 | 131.1 | 325.7 | 316.6
2516.4 | 2297.4 | 550.1 | 229.5 | 130.6 | 325.6 | 315.8
2517.4 | 2298.4 | 549.8 | 229.7 | 130.1 | 325.9 | 315.5
2518.4 | 2299.4 | 549.5 | 229.7 | 129 | 325.7 | 315
2519.4 | 2300.4 | 549.3 | 229.3 | 128.2 | 325 | 314.2
2520.4 | 2301.4 | 549.5 | 228.4 | 127.2 | 323.7 | 313.3
2521.4 | 2302.4 | 549.6 | 227.7 | 126 | 321.6 | 312.4
2522.4 | 2303.4 | 549.6 | 226.6 | 124.7 | 319.5 | 311.7
2523.4 | 2304.4 | 549.7 | 225.8 | 123.8 | 317.8 | 311.3
2524.4 | 2305.4 | 549.7 | 225.5 | 123.7 | 317.6 | 310.8
2525.4 | 2306.4 | 549.3 | 226 | 123.7 | 319.2 | 310.5
2526.4 | 2307.4 | 548.9 | 225.8 | 123.6 | 318.9 | 310.3
2527.4 | 2308.4 | 548.4 | 225.7 | 123.4 | 319.7 | 310.2
2528.4 | 2309.4 | 547.8 | 225.3 | 123.3 | 320.8 | 309.8
2529.4 | 2310.4 | 547.3 | 225.2 | 123.5 | 320.7 | 309.3
2530.4 | 2311.4 | 546.9 | 224.9 | 123.2 | 319.3 | 308.9
2531.4 | 2312.4 | 546.4 | 224.6 | 123.4 | 318.3 | 308.5
2532.4 | 2313.4 | 546 | 224.5 | 123.7 | 318.2 | 308.1
2533.4 | 2314.4 | 545.6 | 223.8 | 123.2 | 318.9 | 307.7
2534.4 | 2315.4 | 545.2 | 223.3 | 122.5 | 317.9 | 307.3
2535.4 | 2316.4 | 544.9 | 222.5 | 121.7 | 315.2 | 306.9
2536.4 | 2317.4 | 544.5 | 222 | 121.1 | 314.9 | 306.3
2537.4 | 2318.4 | 544.1 | 221.6 | 121.1 | 315.6 | 305.8
2538.4 | 2319.4 | 543.8 | 220.8 | 121 | 315 | 305.5
2539.4 | 2320.4 | 543.5 | 220.4 | 121 | 314.9 | 305.2
2540.4 | 2321.4 | 543.2 | 220.4 | 121.2 | 316.1 | 304.7
2541.4 | 2322.4 | 542.8 | 220.2 | 120.8 | 317.1 | 304.4
2542.4 | 2323.4 | 542.4 | 219.8 | 120.7 | 317.6 | 304.1
2543.4 | 2324.4 | 542 | 219.9 | 120.5 | 317.7 | 303.8
2544.4 | 2325.4 | 541.6 | 220.1 | 120.3 | 317.1 | 303.5
2545.4 | 2326.4 | 541.2 | 220.1 | 119.9 | 317.2 | 303.2
2546.4 | 2327.4 | 540.9 | 219.8 | 120.1 | 317.3 | 302.9
2547.4 | 2328.4 | 540.6 | 219.4 | 120.2 | 317.2 | 302.7
2548.4 | 2329.4 | 540.2 | 219.6 | 120.6 | 318 | 302.5
2549.4 | 2330.4 | 539.9 | 219.6 | 121 | 317.9 | 302.2
2550.4 | 2331.4 | 539.5 | 218.8 | 121.4 | 316.5 | 301.7
2551.4 | 2332.4 | 539.2 | 218.6 | 121.4 | 316.1 | 301.5
2552.4 | 2333.4 | 538.8 | 218.5 | 121.4 | 315.3 | 301
2553.4 | 2334.4 | 538.4 | 217.9 | 121.5 | 315 | 300.3
2554.4 | 2335.4 | 538 | 217.7 | 121.8 | 314.5 | 300
2555.4 | 2336.4 | 537.7 | 217.3 | 121.7 | 314.1 | 299.8
2556.4 | 2337.4 | 537.3 | 216.9 | 122.1 | 313.8 | 299.4
2557.4 | 2338.4 | 536.8 | 216.9 | 122.5 | 313.2 | 298.9
2558.4 | 2339.4 | 536.3 | 216.9 | 122.4 | 311.7 | 298.4
2559.4 | 2340.4 | 535.8 | 216.6 | 122 | 311.6 | 297.6
2560.4 | 2341.4 | 535.4 | 216.8 | 121.5 | 311.9 | 297.1
2561.4 | 2342.4 | 535.1 | 216.9 | 121.2 | 312.4 | 296.8
2562.4 | 2343.4 | 534.8 | 217.1 | 121.2 | 312.6 | 296.4
2563.4 | 2344.4 | 534.5 | 216.7 | 121 | 312.7 | 296
2564.4 | 2345.4 | 534.1 | 216.5 | 120.8 | 312.7 | 295.5
2565.4 | 2346.4 | 533.9 | 216.6 | 120.3 | 312.5 | 294.8
2566.4 | 2347.4 | 533.9 | 215.9 | 120.1 | 311.6 | 294.4
2567.4 | 2348.4 | 533.7 | 215.6 | 119.6 | 311.7 | 294.1
2568.4 | 2349.4 | 533.3 | 215.5 | 119.6 | 311.5 | 293.5
2569.4 | 2350.4 | 533 | 214.9 | 119.4 | 311 | 293.1
2570.4 | 2351.4 | 532.7 | 214.7 | 118.5 | 308.8 | 293
2571.4 | 2352.4 | 532.4 | 214.7 | 117.7 | 308.4 | 292.5
2572.4 | 2353.4 | 532.1 | 214.7 | 117.4 | 309.1 | 291.8
2573.4 | 2354.4 | 531.7 | 214.8 | 117.4 | 309.8 | 291.3
2574.4 | 2355.4 | 531.3 | 214.4 | 117.3 | 310.5 | 291
2575.4 | 2356.4 | 531 | 213.9 | 117.1 | 310.9 | 290.4
2576.4 | 2357.4 | 530.5 | 213.9 | 117.2 | 310.1 | 289.9
2577.4 | 2358.4 | 530 | 213.9 | 117.4 | 310.1 | 289.9
2578.4 | 2359.4 | 529.6 | 213.5 | 117.6 | 310.2 | 289.6
2579.4 | 2360.4 | 529.3 | 213.1 | 117.9 | 309.5 | 289.4
2580.4 | 2361.4 | 529.1 | 213.2 | 118 | 308.3 | 289
2581.4 | 2362.4 | 528.8 | 213.2 | 118.3 | 308.1 | 288.8
2582.4 | 2363.4 | 528.6 | 212.8 | 118.2 | 306.9 | 288.4
2583.4 | 2364.4 | 528.4 | 212 | 117.8 | 306.5 | 288.1
2584.4 | 2365.4 | 528 | 211.9 | 116.9 | 307.3 | 287.8
2585.4 | 2366.4 | 527.7 | 211.8 | 116.5 | 306.3 | 287.3
2586.4 | 2367.4 | 527.4 | 211.3 | 116.3 | 306.3 | 286.7
2587.4 | 2368.4 | 527.1 | 211 | 116.2 | 306.1 | 286.2
2588.4 | 2369.4 | 526.7 | 210.9 | 116.2 | 305.8 | 285.5
2589.4 | 2370.4 | 526.4 | 210.8 | 116.3 | 305.2 | 285.2
2590.4 | 2371.4 | 526.1 | 210.5 | 116.4 | 305.8 | 284.9
2591.4 | 2372.4 | 525.8 | 210.3 | 116.5 | 305.4 | 284.7
2592.4 | 2373.4 | 525.4 | 209.9 | 116.6 | 306 | 284.4
2593.4 | 2374.4 | 525 | 209.4 | 116.2 | 306.6 | 283.8
2594.4 | 2375.4 | 524.7 | 209.1 | 115.8 | 305.7 | 283
2595.4 | 2376.4 | 524.3 | 209.1 | 115.7 | 304 | 282.4
2596.4 | 2377.4 | 524 | 208.6 | 114.5 | 302.4 | 282.1
2597.4 | 2378.4 | 523.7 | 208.5 | 114.1 | 300.7 | 281.6
2598.4 | 2379.4 | 523.3 | 208.4 | 113.4 | 300.1 | 281.2
2599.4 | 2380.4 | 522.8 | 207.9 | 112.8 | 299 | 280.7
2600.4 | 2381.4 | 522.3 | 207.1 | 112.1 | 298.9 | 279.7
2601.4 | 2382.4 | 521.8 | 207.2 | 111.5 | 299.4 | 279.4
2602.4 | 2383.4 | 521.5 | 207.3 | 111.4 | 299.9 | 278.6
2603.4 | 2384.4 | 521.1 | 207.1 | 111.6 | 300 | 278.4
2604.4 | 2385.4 | 520.8 | 206.5 | 111.6 | 300.3 | 278.3
2605.4 | 2386.4 | 520.6 | 206.1 | 111.3 | 300.4 | 278.3
2606.4 | 2387.4 | 520.4 | 206 | 111.5 | 299.9 | 278
2607.4 | 2388.4 | 520.1 | 205.7 | 111.7 | 300.2 | 277.5
2608.4 | 2389.4 | 519.8 | 205.4 | 111.8 | 299.7 | 277.2
2609.4 | 2390.4 | 519.6 | 205.3 | 112 | 299.5 | 277.1
2610.4 | 2391.4 | 519.3 | 204.6 | 112.2 | 299.8 | 276.9
2611.4 | 2392.4 | 519 | 203.7 | 112.2 | 300.1 | 276.6
2612.4 | 2393.4 | 518.6 | 203.9 | 112.2 | 300.1 | 276.3
2613.4 | 2394.4 | 518.3 | 204 | 112.1 | 299.5 | 276.1
2614.4 | 2395.4 | 518 | 203.7 | 111.8 | 296.8 | 275.2
2615.4 | 2396.4 | 517.6 | 203.1 | 111.1 | 296.9 | 274.9
2616.4 | 2397.4 | 517.3 | 202.2 | 110.3 | 295.6 | 274.6
2617.4 | 2398.4 | 517.2 | 201.4 | 109.7 | 294.5 | 274.2
2618.4 | 2399.4 | 517 | 201.5 | 109.1 | 294.6 | 273.9
2619.4 | 2400.4 | 516.7 | 201.4 | 108.7 | 294.6 | 273.6
2620.4 | 2401.4 | 516.4 | 200.7 | 108.8 | 294.5 | 273.4
2621.4 | 2402.4 | 516.2 | 200.3 | 109 | 294.8 | 273
2622.4 | 2403.4 | 515.9 | 200 | 108.8 | 295.6 | 272.5
2623.4 | 2404.4 | 515.6 | 200.1 | 108.2 | 295.2 | 272.2
2624.4 | 2405.4 | 515.3 | 199.7 | 107.8 | 294.6 | 271.6
2625.4 | 2406.4 | 515.1 | 199.8 | 107.3 | 294.1 | 271
2626.4 | 2407.4 | 514.7 | 199.5 | 106.3 | 292.4 | 270.4
2627.4 | 2408.4 | 514.2 | 198.6 | 105.5 | 290.5 | 270.1
2628.4 | 2409.4 | 513.7 | 197.8 | 104.8 | 291.2 | 269.8
2629.4 | 2410.4 | 513.3 | 197.1 | 104.8 | 291.7 | 269.5
2630.4 | 2411.4 | 513 | 196.2 | 105.1 | 291.1 | 269.3
2631.4 | 2412.4 | 512.6 | 196.4 | 104.9 | 291 | 269.1
2632.4 | 2413.4 | 512.2 | 196.9 | 104.7 | 291.4 | 268.9
2633.4 | 2414.4 | 511.8 | 197.2 | 104.9 | 290.7 | 268.6
2634.4 | 2415.4 | 511.5 | 197.2 | 105.2 | 291.3 | 268.5
2635.4 | 2416.4 | 511.1 | 197.1 | 105.4 | 291.6 | 268.2
2636.4 | 2417.4 | 510.7 | 197.2 | 105.3 | 292 | 268
2637.4 | 2418.4 | 510.4 | 197.1 | 105.4 | 292.8 | 267.8
2638.4 | 2419.4 | 510.1 | 197.1 | 105.4 | 293.3 | 267.5
2639.4 | 2420.4 | 509.7 | 197.4 | 105.5 | 294 | 267.4
2640.4 | 2421.4 | 509.3 | 197.4 | 105.5 | 293.7 | 267.2
2641.4 | 2422.4 | 508.9 | 196.9 | 105.8 | 293.7 | 267
2642.4 | 2423.4 | 508.6 | 196.4 | 105.9 | 293.9 | 266.8
2643.4 | 2424.4 | 508.3 | 196.4 | 105.9 | 294.7 | 266.6
2644.4 | 2425.4 | 507.9 | 196.3 | 105.9 | 294.5 | 266.4
2645.4 | 2426.4 | 507.6 | 196.4 | 105.7 | 294.8 | 266.1
2646.4 | 2427.4 | 507.2 | 196.4 | 105.7 | 294.4 | 265.8
2647.4 | 2428.4 | 506.8 | 196 | 105.5 | 294.5 | 265.7
2648.4 | 2429.4 | 506.4 | 195.9 | 105.6 | 293.7 | 265.6
2649.4 | 2430.4 | 506.1 | 195.7 | 105.3 | 293.8 | 265.3
2650.4 | 2431.4 | 505.6 | 195.6 | 105.6 | 294 | 265
2651.4 | 2432.4 | 505.2 | 195.3 | 105.7 | 293.7 | 264.8
2652.4 | 2433.4 | 504.8 | 195 | 105.9 | 294.2 | 264.5
2653.4 | 2434.4 | 504.5 | 194.7 | 106.1 | 293.9 | 264.1
2654.4 | 2435.4 | 504.2 | 194.2 | 106.3 | 293.2 | 263.6
2655.4 | 2436.4 | 503.8 | 193.5 | 106.1 | 292.4 | 263.4
2656.4 | 2437.4 | 503.4 | 192.6 | 106.1 | 291.4 | 263
2657.4 | 2438.4 | 503 | 192.1 | 106.1 | 290.1 | 262.5
2658.4 | 2439.4 | 502.6 | 191.7 | 105.6 | 289.8 | 262.3
2659.4 | 2440.4 | 502.2 | 192.1 | 105 | 290.3 | 262
2660.4 | 2441.4 | 501.8 | 191.7 | 104.5 | 290.9 | 261.8
2661.4 | 2442.4 | 501.4 | 191.3 | 104.4 | 291 | 261.4
2662.4 | 2443.4 | 501 | 191 | 104.1 | 290.3 | 260.8
2663.4 | 2444.4 | 500.5 | 190.9 | 103.6 | 289.7 | 260.5
2664.4 | 2445.4 | 500.1 | 191 | 103.4 | 289.6 | 260.3
2665.4 | 2446.4 | 499.8 | 191.3 | 103 | 289.5 | 260.1
2666.4 | 2447.4 | 499.4 | 191.5 | 102.3 | 288.9 | 259.7
2667.4 | 2448.4 | 499 | 191.3 | 101.6 | 287.9 | 259.3
2668.4 | 2449.4 | 498.7 | 190.4 | 101.1 | 287.7 | 259
2669.4 | 2450.4 | 498.3 | 189.7 | 100.9 | 288.3 | 258.7

## Test Facts
Last row in IRMS data sheets: | 20
Time when Penlight power was initiated: | 219