## IS Test Matrix
Intermediate Scale Test Matrix - Revision F (12-06-06)
|  | Comments: 1) All tests were conducted as open burns with a Propene (Propylene) gas sand burner 2) Colors identify test conditions grouped into the same test run | [14 empty] | ACTUAL TEST CONDITIONS
Burn Test # | Rev. E Test # | Loc. | Cable Insulation Material | [8 empty] | Number of Conductors |  |  |  | Conductor Size (AWG) |  |  |  |  | Cable Bundle Size |  |  |  |  | Water Spary Optionsl | Raceway Type
|  |  | Thermoset | [5 empty] | Thermoplastic
|  |  | XLPE | EPR | Silicone | XLPO | TS/TP | Vita-Link | PE | PVC | Tefzel | 3 | 2 | 7 | 12 | 8 | 12 | 14 | 16 | 18 | 1 | 3 | 6 | 12 | Load Tr | * | 12" Tray | 2.5" Cnd | Air Drop
Prelim 1 | Prelim 1 | A | X | [8 empty] | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | A | X | [10 empty] | X |  |  | X |  |  |  | X | [5 empty] | X
Prelim 2 | Prelim 2 | A | X | [8 empty] | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | A | X | [10 empty] | X |  |  | X |  |  |  | X | [5 empty] | X
Prelim 3 | Prelim 3 | A | [7 empty] | X |  | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | A | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [5 empty] | X
Prelim 4 | Prelim 4 | A | [7 empty] | X |  | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | A | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [5 empty] | X
1 | 15 | A | X | [9 empty] | X | X | X |  | X |  | X | X |  |  |  |  | X |  | X
|  | B | X | [10 empty] | X |  |  | X | [6 empty] | X |  |  | X
|  | D | X | [10 empty] | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | E | X | [10 empty] | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | [10 empty] | X |  |  | X | [6 empty] | X |  |  | X
2 | 1 | A | X | [10 empty] | X |  |  | X | [6 empty] | X |  |  | X
|  | C | X | [10 empty] | X |  |  | X | [5 empty] | X |  |  |  | X
|  | A | X | [5 empty] | X |  |  |  |  | X |  |  | X | [6 empty] | X |  |  | X
|  | C | X | [5 empty] | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
| 11 | C - A | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [7 empty] | X
|  | E | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [5 empty] | X
|  | G | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [5 empty] | X
3 | 2 | A | X | X | [9 empty] | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X | [9 empty] | X |  |  | X | [5 empty] | X |  |  |  | X
| 3 | A |  | X |  |  |  |  | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C |  | X |  |  |  |  | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
| 10 | E | [7 empty] | X |  | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | [7 empty] | X |  | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
4 | 5 | A | X | X |  | X | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X |  | X | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
| 6 | A | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
| 9 | C - A | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [7 empty] | X
|  | E | X | [8 empty] | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | [8 empty] | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
5 | 4 | A | X | X | X | X |  |  | X |  | X |  |  | X |  |  | X | [6 empty] | X |  | X | X
|  | C | X | X | X | X |  |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
| 7 | A | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | X | [5 empty] | X |  | X | X
|  | C | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | X |  |  |  |  | X |  |  | X | X
|  | C - A | X | [10 empty] | X |  |  | X |  |  |  | X | [7 empty] | X
|  | E |  | X | [9 empty] | X |  |  | X |  |  |  | X | [5 empty] | X
|  | G |  | X | [9 empty] | X |  |  | X |  |  |  | X | [5 empty] | X
6 | 12 | A | X | X | X | X |  |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | C | X | X | X | X |  |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | E | X | [5 empty] | X |  | X |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
| 13 | C - A | X | [5 empty] | X |  | X |  |  | X |  |  | X |  |  |  |  | X | [6 empty] | X
|  | A |  | X | X | X | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | C |  | X | X | X | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | G |  |  |  |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  |  |  | X
7 | 14 | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | A | X | X |  | X | X |  |  | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C |  | X |  | X | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | E | X | [5 empty] | X | X |  |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G |  | X |  | X | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
8 | 16 | A | X | [5 empty] | X | X |  |  | X | X | X |  | X |  | X | X |  |  | X |  |  |  | X
|  | A | X | [5 empty] | X | X |  |  | X | X | X |  | X |  | X | X |  |  | X |  |  |  | X
|  | C | X | [5 empty] | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | E | X | [5 empty] | X |  |  |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | [5 empty] | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
9 | 19 | A | X | X | X |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | A | X | X | X |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | C | X | X | X |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | E | X | [5 empty] | X |  | X |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | X | X |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
10 | 20 | A | X | X | X | X | X |  |  |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | A | X | X | X | X | X |  |  |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | C | X | X | X | X | X |  |  | X |  |  |  | X | X |  | X |  |  | X |  |  | X |  |  | X | X
|  | E |  |  |  |  | X |  | X |  | X |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | X |  |  | X |  | X | X | X |  | X | X |  |  | X |  | X |  |  |  | X |  |  |  | X
11 | 21 | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X |  | X | X |  |  | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | E |  |  |  |  | X |  | X | X |  |  |  | X |  |  | X |  |  |  |  | X | [6 empty] | X
|  | G | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
12 | 24 | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X |  | X | X |  |  | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | E |  |  |  |  | X |  | X | X |  |  |  | X |  |  | X |  |  |  |  | X | [6 empty] | X
|  | G | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
13 | 25 | A | X | X |  | X | X | X | X |  | X |  |  | X |  |  | X | [7 empty] | X | X | X
|  | C | X | X |  | X | X | X | X |  | X |  |  | X |  |  | X | [7 empty] | X | X | X
|  | E | X | X | [9 empty] | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | F | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | F | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | G | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | G | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
14 | 27 | A | X | X |  | X | X |  | X | X | X |  |  | X |  |  | X | [7 empty] | X |  | X
|  | C | X | X |  | X | X |  | X | X | X |  |  | X |  |  | X | [7 empty] | X |  | X
|  | E |  |  |  |  | X |  | X | X |  |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | F | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | F | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | G | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | G | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X

## Shorting Summary
Shorting Sequence for Open Burn Test 13, Location F, IRMS #1
Test conditions: Cable: Bundle of 6, 7-conductor, 12 AWG, XLPE, EPR, Vita-Link, XLPO, PE & Tefzel control cables (Items 10, 2, 11, 8, 15 & 12). Cable specimens present: Three lengths of cable were monitored for electrical performance (A, B & C [See Elect. Conn. Map]), a second bundle of 6 cables was monitored for temperature response. Raceway: 12" B-Line Series 2 tray (part number 248P09-12-144) located at position F in the Test Cell chamber with chamber end walls open and un-heated. Exposure conditions: Initial gas burner flow rate set to a nominal 150 kW heat release rate and increased to 300 kW during the test run. Electrical repsonse monitoring: IRMS system using 6 channels - two for each cable (see electrical connection map), cable tray was grounded. Thermal response monitoring: Two cable bundle temperatures (see thermocouple map), air temperatures above and below the cable bundle, and the cable tray rung temperature. Gas burner initiated: Following 239 seconds of baseline data monitoring. Special Note: Vita-Link cable was used in place of silicone rubber cable during this test.
DAQ Time | Burner Time | Event | Interpretation
239 | 0 | Ignited Gas Burner
1197-1200 | 958-961 | Conductors B3 & B4 both short to ground at less than 100 ohms (35 & 56) | Cable B shorted to ground
1244 | 1005 | Conductors B3 & B4 short together at less than 100 ohms (16) | Cable B shorts internally
1485 | 1246 | Conductor A2 shorts to ground at less than 100 ohms (47) | Cable A partially shorted to ground
1513 | 1274 | Conductors A1 & A2 short together at less than 100 ohms (377) | Cable A shorts internally
1518 | 1279 | Conductor A1 shorts to ground at less than 100 ohms (73) | Cable A shorted to ground
2280 | 2041 | Extinguished Gas Burner
2330 | 2091 | Initiated water sprinkler
2465 | 2226 | Conductor C6 IR value to ground momentarily drops to less than 1000 ohms (883) then recovers | Momentary high impedance ground fault on C6
2762 | 2523 | Water sprinkler shut off
Additional Observations
Observation 1 | The cables tended to short to ground prior to shorting internally.
Observation 2 | Cable C did not show any signs of failure except for a momentary resistance to ground drop below 1000 ohms while the water sprinkler was active. It then recovered to >1000 ohms.
Observation 3 | There was no evidence of cable-to-cable interactions prior to internal cable shorting or shorting to ground.

## Thermocouple Map
Thermocouple map for TC's on and within the cable
|  |  |  | Cable A = | XLPE | (Item #10)
|  |  |  | Cable B = | EPR | (Item #2)
|  |  |  | Cable C = | Vita-Link | (Item #11)
|  |  |  | Cable D = | XLPO | (Item #8)
|  |  |  | Cable E = | PE | (Item #15)
|  |  |  | Cable F = | TEFZEL | (Item #12)
Translation to data file names used in "Temperatures" WorkSheet:
| Map Name |  | Location
| F1 | = | Center of bundle, under jacket
| F2 | = | Air above bundle
| F3 | = | Air below bundle
| F4 | = | Intra-bundle, center

## Elect Conn Map
Electrical connection map within the cables
|  |  |  | Cable A = | XLPE | (Item #10)
|  |  |  | Cable B = | EPR | (Item #2)
|  |  |  | Cable C = | Vita-Link | (Item #11)
Tray rung under D-E-F
Cable Bundle Arrangement
Cable 7-Conductor Arrangement
| Lt Blue = | Even conductor set
| Lt Red = | Odd conductor set
| Gray = | Center conductor (not connected)
IRMS Electrical Connections

## C-C Individuals
Conductor to Conductor Resistances
Open Burn Test 13 |  |  | 2006-11-28 | 9:21
Mixed | 7-C | Tray F | IRMS | 1
0 | 150 kW
Burner Time | A1-A2 | Burner Time | A1-B3 | Burner Time | A1-B4 | Burner Time | A1-C5 | Burner Time | A1-C6 | Burner Time | A2-B3 | Burner Time | A2-B4 | Burner Time | A2-C5 | Burner Time | A2-C6 | Burner Time | B3-B4 | Burner Time | B3-C5 | Burner Time | B3-C6 | Burner Time | B4-C5 | Burner Time | B4-C6 | Burner Time | C5-C6
-238 | 255437.9994 | -235.5 | 256637.9994 | -232.5 | 259737.9994 | -229.5 | 254337.9994 | -227 | 256237.9994 | -224 | 258437.9994 | -221.5 | 256337.9994 | -218.5 | 251937.9994 | -215.5 | 255837.9994 | -213 | 258737.9994 | -210 | 259037.9994 | -207.5 | 260537.9994 | -204.5 | 260637.9994 | -201.5 | 260637.9994 | -199 | 211201.9994
-196 | 255437.9994 | -193.5 | 256637.9994 | -190.5 | 259737.9994 | -187.5 | 254337.9994 | -185 | 256237.9994 | -182.5 | 258437.9994 | -179.5 | 256337.9994 | -176.5 | 251937.9994 | -174 | 255837.9994 | -171 | 258737.9994 | -168 | 259037.9994 | -165.5 | 260537.9994 | -162.5 | 260637.9994 | -159.5 | 260637.9994 | -157 | 211201.9994
-154 | 255437.9994 | -151.5 | 256637.9994 | -148.5 | 259737.9994 | -145.5 | 254337.9994 | -143 | 256237.9994 | -140 | 258437.9994 | -137.5 | 256337.9994 | -134.5 | 251937.9994 | -131.5 | 255837.9994 | -129 | 258737.9994 | -126 | 259037.9994 | -123.5 | 260537.9994 | -120.5 | 260637.9994 | -117.5 | 260637.9994 | -115 | 211201.9994
-112 | 255437.9994 | -109.5 | 256637.9994 | -106.5 | 259737.9994 | -103.5 | 254337.9994 | -101 | 256237.9994 | -98.5 | 258437.9994 | -95.5 | 256337.9994 | -92.5 | 251937.9994 | -90 | 255837.9994 | -87 | 258737.9994 | -84 | 259037.9994 | -81.5 | 260537.9994 | -78.5 | 260637.9994 | -75.5 | 260438.0767 | -73 | 211201.9994
-70 | 255437.9994 | -67.5 | 256637.9994 | -64.5 | 259737.9994 | -62 | 254337.9994 | -59 | 256038.078 | -56 | 258437.9994 | -53.5 | 256337.9994 | -50.5 | 251937.9994 | -47.5 | 255837.9994 | -45 | 258737.9994 | -42.5 | 259037.9994 | -39.5 | 260537.9994 | -36.5 | 260637.9994 | -34 | 260637.9994 | -31 | 211201.9994
-28 | 255437.9994 | -25.5 | 256637.9994 | -22.5 | 259737.9994 | -20 | 254337.9994 | -17 | 256237.9994 | -14.5 | 258437.9994 | -11.5 | 256337.9994 | -8.5 | 251937.9994 | -6 | 255837.9994 | -3 | 258737.9994 | 5.4855e-07 | 259037.9994 | 2.5 | 260537.9994 | 5.5 | 260637.9994 | 8 | 260637.9994 | 11 | 211201.9994
14 | 255437.9994 | 16.5 | 256637.9994 | 19.5 | 259737.9994 | 22.5 | 254337.9994 | 25 | 256237.9994 | 27.5 | 258437.9994 | 30.5 | 256337.9994 | 33.5 | 251937.9994 | 36 | 255837.9994 | 39 | 258737.9994 | 41.5 | 259037.9994 | 44.5 | 260537.9994 | 47.5 | 260637.9994 | 50 | 260637.9994 | 53 | 211201.9994
55.5 | 255437.9994 | 58.5 | 256637.9994 | 61.5 | 259737.9994 | 64 | 254337.9994 | 67 | 256237.9994 | 69.5 | 258437.9994 | 72.5 | 256337.9994 | 75.5 | 251937.9994 | 78.5 | 255837.9994 | 81 | 258737.9994 | 84 | 259037.9994 | 86.5 | 260537.9994 | 89.5 | 260637.9994 | 92 | 260637.9994 | 95 | 211201.9994
97.5 | 255437.9994 | 100.5 | 256637.9994 | 103.5 | 259737.9994 | 106 | 254337.9994 | 109 | 256237.9994 | 111.5 | 258437.9994 | 114.5 | 256337.9994 | 117.5 | 251937.9994 | 120 | 255837.9994 | 123 | 258737.9994 | 125.5 | 259037.9994 | 128.5 | 260537.9994 | 131.5 | 260637.9994 | 134 | 260637.9994 | 137 | 211201.9994
139.5 | 255437.9994 | 142.5 | 256637.9994 | 145.5 | 259737.9994 | 148 | 254337.9994 | 151 | 256237.9994 | 153.5 | 258437.9994 | 156.5 | 256337.9994 | 159.5 | 251937.9994 | 162 | 255837.9994 | 165 | 258737.9994 | 167.5 | 259037.9994 | 170.5 | 260537.9994 | 173.5 | 260637.9994 | 176 | 260637.9994 | 179 | 211201.9994
181.5 | 255437.9994 | 184.5 | 256637.9994 | 187.5 | 259737.9994 | 190 | 254337.9994 | 193 | 256237.9994 | 195.5 | 258437.9994 | 198.5 | 256337.9994 | 201.5 | 251937.9994 | 204.5 | 255837.9994 | 207 | 258737.9994 | 210 | 259037.9994 | 212.5 | 260537.9994 | 215.5 | 260637.9994 | 218 | 260637.9994 | 221 | 211201.9994
223.5 | 255437.9994 | 226.5 | 256637.9994 | 229.5 | 259737.9994 | 232 | 254337.9994 | 235 | 256237.9994 | 237.5 | 258437.9994 | 240.5 | 256337.9994 | 243.5 | 251937.9994 | 246 | 255837.9994 | 249 | 258737.9994 | 251.5 | 259037.9994 | 254.5 | 260537.9994 | 257.5 | 260637.9994 | 260 | 260637.9994 | 263 | 211201.9994
265.5 | 255437.9994 | 268.5 | 256637.9994 | 271.5 | 259737.9994 | 274 | 254337.9994 | 277 | 256237.9994 | 279.5 | 258437.9994 | 282.5 | 256337.9994 | 285.5 | 251937.9994 | 288 | 255837.9994 | 291 | 258737.9994 | 293.5 | 259037.9994 | 296.5 | 260537.9994 | 299.5 | 260637.9994 | 302 | 260637.9994 | 305 | 211201.9994
307.5 | 255437.9994 | 310.5 | 256637.9994 | 313.5 | 259737.9994 | 316 | 254337.9994 | 319 | 256237.9994 | 321.5 | 258437.9994 | 324.5 | 256337.9994 | 327.5 | 251937.9994 | 330 | 255837.9994 | 333 | 258737.9994 | 335.5 | 259037.9994 | 338.5 | 260537.9994 | 341.5 | 260637.9994 | 344 | 260637.9994 | 347 | 211201.9994
349.5 | 255437.9994 | 352.5 | 256637.9994 | 355.5 | 259737.9994 | 358 | 254337.9994 | 361 | 256237.9994 | 363.5 | 258437.9994 | 366.5 | 256337.9994 | 369.5 | 251937.9994 | 372 | 255837.9994 | 375 | 258737.9994 | 377.5 | 259037.9994 | 380.5 | 260537.9994 | 383.5 | 260637.9994 | 386 | 260637.9994 | 389 | 211201.9994
391.5 | 255437.9994 | 394.5 | 256637.9994 | 397.5 | 259737.9994 | 400 | 254337.9994 | 403 | 256237.9994 | 405.5 | 258437.9994 | 408.5 | 256337.9994 | 411.5 | 251937.9994 | 414 | 255837.9994 | 417 | 258737.9994 | 419.5 | 259037.9994 | 422.5 | 260537.9994 | 425.5 | 260637.9994 | 428 | 260637.9994 | 431 | 211201.9994
433.5 | 255437.9994 | 436.5 | 256637.9994 | 439.5 | 259737.9994 | 442 | 254337.9994 | 445 | 256237.9994 | 447.5 | 258437.9994 | 450.5 | 256337.9994 | 453.5 | 251937.9994 | 456 | 255837.9994 | 459 | 258737.9994 | 461.5 | 259037.9994 | 464.5 | 260537.9994 | 467.5 | 260637.9994 | 470 | 260637.9994 | 473 | 211201.9994
475.5 | 255437.9994 | 478.5 | 256637.9994 | 481.5 | 259737.9994 | 484 | 254337.9994 | 487 | 256237.9994 | 489.5 | 258437.9994 | 492.5 | 256337.9994 | 495.5 | 251937.9994 | 498 | 255837.9994 | 501 | 258737.9994 | 503.5 | 259037.9994 | 506.5 | 260537.9994 | 509.5 | 260637.9994 | 512 | 260637.9994 | 515 | 211201.9994
517.5 | 255437.9994 | 520.5 | 256637.9994 | 523.5 | 259737.9994 | 526 | 254337.9994 | 529 | 256237.9994 | 531.5 | 258437.9994 | 534.5 | 256337.9994 | 537.5 | 251937.9994 | 540 | 255837.9994 | 543 | 258737.9994 | 545.5 | 259037.9994 | 548.5 | 260537.9994 | 551.5 | 260637.9994 | 554 | 260637.9994 | 557 | 211201.9994
559.5 | 255437.9994 | 562.5 | 256637.9994 | 565.5 | 259737.9994 | 568 | 254337.9994 | 571 | 256237.9994 | 573.5 | 258437.9994 | 576.5 | 256337.9994 | 579.5 | 251937.9994 | 582 | 255837.9994 | 585 | 258737.9994 | 587.5 | 259037.9994 | 590.5 | 260537.9994 | 593.5 | 260637.9994 | 596 | 260637.9994 | 599 | 211201.9994
601.5 | 255437.9994 | 604.5 | 256637.9994 | 607.5 | 259737.9994 | 610 | 254337.9994 | 613 | 256237.9994 | 615.5 | 258437.9994 | 618.5 | 256337.9994 | 621.5 | 251937.9994 | 624 | 255837.9994 | 627 | 258737.9994 | 629.5 | 259037.9994 | 632.5 | 260537.9994 | 635.5 | 260637.9994 | 638 | 260637.9994 | 641 | 211201.9994
643.5 | 255437.9994 | 646.5 | 256637.9994 | 649.5 | 259737.9994 | 652 | 254337.9994 | 655 | 256237.9994 | 657.5 | 258437.9994 | 660.5 | 256337.9994 | 663.5 | 251937.9994 | 666 | 255837.9994 | 669 | 258737.9994 | 671.5 | 259037.9994 | 674.5 | 260537.9994 | 677.5 | 260637.9994 | 680 | 260637.9994 | 683 | 211201.9994
685.5 | 255437.9994 | 688.5 | 256637.9994 | 691.5 | 259737.9994 | 694 | 254337.9994 | 697 | 256237.9994 | 699.5 | 258437.9994 | 702.5 | 256337.9994 | 705.5 | 251937.9994 | 708 | 255837.9994 | 711 | 258737.9994 | 713.5 | 259037.9994 | 716.5 | 260537.9994 | 719.5 | 260637.9994 | 722 | 260637.9994 | 725 | 211201.9994
727.5 | 255437.9994 | 730.5 | 256637.9994 | 733.5 | 259737.9994 | 736 | 254337.9994 | 739 | 256237.9994 | 741.5 | 258437.9994 | 744.5 | 256337.9994 | 747.5 | 251937.9994 | 750 | 255837.9994 | 752.5 | 258737.9994 | 755.5 | 259037.9994 | 758.5 | 260537.9994 | 761.5 | 260637.9994 | 764 | 260637.9994 | 767 | 211201.9994
769.5 | 255437.9994 | 772.5 | 256637.9994 | 775.5 | 259737.9994 | 778 | 254337.9994 | 781 | 256237.9994 | 783.5 | 258437.9994 | 786.5 | 256337.9994 | 789.5 | 251937.9994 | 792 | 255837.9994 | 795 | 258737.9994 | 797.5 | 259037.9994 | 800.5 | 260537.9994 | 803.5 | 260637.9994 | 806 | 260637.9994 | 809 | 211201.9994
811.5 | 255437.9994 | 814.5 | 256637.9994 | 817.5 | 259737.9994 | 820 | 254337.9994 | 823 | 256237.9994 | 825.5 | 258437.9994 | 828.5 | 256337.9994 | 831.5 | 251937.9994 | 834 | 255837.9994 | 837 | 258737.9994 | 839.5 | 259037.9994 | 842.5 | 260537.9994 | 845.5 | 260637.9994 | 848 | 260637.9994 | 851 | 211201.9994
853.5 | 255437.9994 | 856.5 | 256637.9994 | 859.5 | 259737.9994 | 862 | 254337.9994 | 865 | 256237.9994 | 867.5 | 258437.9994 | 870.5 | 256337.9994 | 873.5 | 251937.9994 | 876 | 255837.9994 | 879 | 258737.9994 | 881.5 | 259037.9994 | 884.5 | 260537.9994 | 887.5 | 260637.9994 | 890 | 260637.9994 | 893 | 211201.9994
895.5 | 255437.9994 | 898.5 | 256637.9994 | 901.5 | 259737.9994 | 904 | 254337.9994 | 907 | 256237.9994 | 909.5 | 258437.9994 | 912.5 | 256337.9994 | 915.5 | 251937.9994 | 918 | 255837.9994 | 921 | 258737.9994 | 923.5 | 259037.9994 | 926.5 | 260537.9994 | 929.5 | 260637.9994 | 932 | 260637.9994 | 935 | 211201.9994
937.5 | 255437.9994 | 940.5 | 256637.9994 | 943 | 259737.9994 | 946 | 254337.9994 | 948.5 | 256237.9994 | 951.5 | 258437.9994 | 954.5 | 256337.9994 | 957 | 251937.9994 | 960 | 255837.9994 | 963 | 143282.6225 | 965.5 | 67411.976 | 968.5 | 78108.0205 | 971.5 | 161276.1226 | 974 | 93202.2407 | 977 | 211201.9994
979.5 | 255437.9994 | 982.5 | 256637.9994 | 985.5 | 259737.9994 | 988 | 254337.9994 | 991 | 256237.9994 | 993.5 | 258437.9994 | 996.5 | 256337.9994 | 999.5 | 251937.9994 | 1002 | 255837.9994 | 1004.5 | 16.3105 | 1007.5 | 6735.3998 | 1010.5 | 50118.7634 | 1013 | 13932.6544 | 1016 | 51057.941 | 1018.5 | 211201.9994
1021.5 | 255437.9994 | 1024.5 | 256637.9994 | 1027 | 259737.9994 | 1030 | 254337.9994 | 1032.5 | 256237.9994 | 1035.5 | 258437.9994 | 1038.5 | 256337.9994 | 1041 | 251937.9994 | 1044 | 255837.9994 | 1046.5 | 8.7567 | 1049.5 | 8634.6666 | 1052.5 | 63113.7756 | 1055.5 | 23628.9342 | 1058 | 51718.1571 | 1061 | 211201.9994
1063.5 | 255437.9994 | 1066.5 | 256637.9994 | 1069.5 | 259737.9994 | 1072 | 254337.9994 | 1074.5 | 256237.9994 | 1077.5 | 258437.9994 | 1080.5 | 256337.9994 | 1083.5 | 251937.9994 | 1086 | 255837.9994 | 1088.5 | 35.5058 | 1091.5 | 24528.5309 | 1094.5 | 42321.756 | 1097 | 66612.4425 | 1100 | 9234.457 | 1102.5 | 211201.9994
1105.5 | 255437.9994 | 1108 | 256637.9994 | 1111 | 259737.9994 | 1114 | 254337.9994 | 1116.5 | 256237.9994 | 1119.5 | 258437.9994 | 1122.5 | 256337.9994 | 1125.5 | 251937.9994 | 1128 | 255837.9994 | 1131 | 20.2198 | 1133.5 | 40822.2408 | 1136.5 | 47619.7225 | 1139.5 | 55216.8147 | 1142 | 22829.241 | 1145 | 211201.9994
1147.5 | 255437.9994 | 1150.5 | 256637.9994 | 1153 | 259737.9994 | 1156 | 254337.9994 | 1158.5 | 256237.9994 | 1161.5 | 258437.9994 | 1164.5 | 256337.9994 | 1167.5 | 251937.9994 | 1170 | 255837.9994 | 1173 | 33.9943 | 1175.5 | 33625.0193 | 1178.5 | 60614.7348 | 1181.5 | 29426.7097 | 1184 | 71510.5633 | 1186.5 | 211201.9994
1189.5 | 255437.9994 | 1192.5 | 256637.9994 | 1195 | 259737.9994 | 1198 | 254337.9994 | 1200.5 | 256237.9994 | 1203.5 | 258437.9994 | 1206.5 | 256337.9994 | 1209 | 251937.9994 | 1212 | 255837.9994 | 1214.5 | 30.3219 | 1217.5 | 23129.0712 | 1220.5 | 70810.8213 | 1223.5 | 72710.103 | 1226 | 29626.633 | 1228.5 | 211201.9994
1231.5 | 127668.9988 | 1234.5 | 51247.5969 | 1237 | 32379.7451 | 1240 | 251739.0219 | 1243 | 253639.0143 | 1245.5 | 72.8402 | 1248.5 | 7913.668 | 1251.5 | 80805.9263 | 1254 | 94301.1403 | 1256.5 | 8.0483 | 1259.5 | 55816.4524 | 1262.5 | 51418.2646 | 1265.5 | 19530.5067 | 1268 | 14332.501 | 1271 | 211201.9994
1273.5 | 37.1035 | 1276.5 | 71.9809 | 1279.5 | 88.2718 | 1282 | 249739.8079 | 1284.5 | 232647.2066 | 1287.5 | 626.013 | 1290.5 | 893.7882 | 1293 | 184164.9007 | 1296 | 137184.3784 | 1298.5 | 174.9355 | 1301.5 | 91402.7146 | 1304.5 | 87504.414 | 1307.5 | 109595.9509 | 1310 | 119792.0389 | 1313 | 211201.9994
1315.5 | 70.7441 | 1318.5 | 21.3873 | 1321 | 9.8541 | 1324 | 19130.4783 | 1327 | 21129.7539 | 1329.5 | 13.0689 | 1332.5 | 27.1924 | 1335 | 20729.7719 | 1338 | 67411.6506 | 1341 | 2592.6314 | 1343.5 | 74309.3134 | 1346.5 | 71210.6678 | 1349.5 | 48519.3844 | 1352 | 36124.1401 | 1355 | 211201.9994
1357.5 | 428.836 | 1360.5 | 26.7604 | 1363.5 | 5.7589 | 1366 | 12732.9937 | 1368.5 | 13132.8747 | 1371.5 | 20.949 | 1374.5 | 15.4882 | 1377 | 10433.8586 | 1380 | 49918.4882 | 1382.5 | 26.9685 | 1385.5 | 28327.0645 | 1388.5 | 67512.0874 | 1391 | 29726.5947 | 1394 | 31325.981 | 1396.5 | 211201.9994
1399.5 | 28.7784 | 1402.5 | 8.9574 | 1405 | 10.8277 | 1408 | 43320.9672 | 1411 | 11233.6159 | 1413.5 | 9.8282 | 1416.5 | 22.4986 | 1419.5 | 59714.298 | 1422 | 38822.8252 | 1425 | 1.925 | 1427.5 | 15731.9268 | 1430.5 | 41222.1781 | 1433 | 19130.6601 | 1436 | 51118.3872 | 1439 | 211201.9994
1441.5 | 11.0356 | 1444.5 | 6.5581 | 1447 | 17.53 | 1450 | 33124.976 | 1452.5 | 25627.9984 | 1455.5 | 33.0599 | 1458.5 | 1.3831 | 1461.5 | 39122.4714 | 1464 | 47219.5432 | 1466.5 | 3.2418 | 1469.5 | 57315.8736 | 1472.5 | 13132.9593 | 1475 | 52517.8503 | 1478 | 11333.6516 | 1480.5 | 211201.9994
1483.5 | 2211.2018 | 1486.5 | 23.1894 | 1489 | 16.2245 | 1492 | 44620.4562 | 1494.5 | 63513.2132 | 1497.5 | 26.884 | 1500.5 | 12.7014 | 1503 | 63312.8697 | 1506 | 23728.7251 | 1508.5 | 1.7574 | 1511.5 | 20829.9587 | 1514.5 | 58715.4638 | 1517 | 66187.1919 | 1520 | 21129.893 | 1522.5 | 211201.9994
1525.5 | 244.7677 | 1528.5 | 9.5858 | 1531 | 14.684 | 1534 | 66112.0062 | 1536.5 | 66186.3198 | 1539.5 | 21.5948 | 1542.5 | 34.6726 | 1545 | 64912.2348 | 1548 | 30725.9901 | 1550.5 | 13.253 | 1553.5 | 57715.7192 | 1556.5 | 54716.9985 | 1559 | 49219.1159 | 1562 | 56816.2011 | 1564.5 | 211201.9994
1567.5 | 392.2214 | 1570.5 | 24.2958 | 1573 | 32.8922 | 1576 | 50018.3339 | 1578.5 | 17231.2753 | 1581.5 | 12.3554 | 1584.5 | 33.8074 | 1587 | 62613.1474 | 1590 | 66811.8851 | 1592.5 | 1.4238 | 1595.5 | 18830.7305 | 1598.5 | 28327.1274 | 1601 | 21429.778 | 1604 | 61714.3218 | 1606.5 | 211201.9994
1609.5 | 2931.4449 | 1612.5 | 33.6076 | 1615 | 22.1534 | 1618 | 39022.6572 | 1620.5 | 14432.3676 | 1623.5 | 6.9456 | 1626.5 | 26.8687 | 1629 | 33024.8917 | 1632 | 62213.6824 | 1634.5 | 25.8246 | 1637.5 | 36124.0545 | 1640.5 | 12233.3046 | 1643 | 50318.694 | 1646 | 61914.2451 | 1648.5 | 211201.9994
1651.5 | 2913.9663 | 1654.5 | 10.0738 | 1657 | 10.193 | 1660 | 23228.8669 | 1662.5 | 61314.0714 | 1665.5 | 29.366 | 1668.5 | 31.6912 | 1671 | 66311.6794 | 1674 | 41121.9266 | 1676.5 | 12.7415 | 1679.5 | 57493.5928 | 1682.5 | 37323.6744 | 1685 | 61814.2835 | 1688 | 50218.7324 | 1690.5 | 211201.9994
1693.5 | 299.2555 | 1696.5 | 34.1089 | 1699 | 30.0225 | 1702 | 55816.0544 | 1704.5 | 32125.4626 | 1707.5 | 8.3449 | 1710.5 | 17.7929 | 1713 | 30026.082 | 1716 | 68711.1427 | 1718.5 | 1.7992 | 1721.5 | 19030.6533 | 1724.5 | 60914.6197 | 1727 | 49119.1543 | 1730 | 38123.3731 | 1732.5 | 211201.9994
1735.5 | 1850.9097 | 1738.5 | 33.9653 | 1741 | 19.2023 | 1744 | 67811.3381 | 1746.5 | 52517.5044 | 1749.5 | 15.4225 | 1752.5 | 8.7325 | 1755 | 7035.2076 | 1758 | 24528.4125 | 1760.5 | 6.7495 | 1763.5 | 9034.5123 | 1766.5 | 20730.0434 | 1769 | 3136.7965 | 1772 | 52617.8119 | 1774.5 | 211201.9994
1777.5 | 11452.8862 | 1780.5 | 31.9162 | 1783 | 6.527 | 1786 | 58514.9932 | 1788.5 | 29226.594 | 1791.5 | 11.9516 | 1794.5 | 32.6706 | 1797 | 29826.1613 | 1800 | 36623.6848 | 1802.5 | 7.2562 | 1805.5 | 54317.0312 | 1808.5 | 58715.4638 | 1811 | 47419.8063 | 1814 | 50318.694 | 1816.5 | 211201.9994
1819.5 | 6653.8646 | 1822.5 | 17.3194 | 1825 | 20.4006 | 1828 | 56515.7793 | 1830.5 | 11033.694 | 1833.5 | 8.2977 | 1836.5 | 8.4457 | 1839 | 15731.7557 | 1842 | 63513.1745 | 1844.5 | 17.1274 | 1847.5 | 1537.4065 | 1850.5 | 45520.5283 | 1853 | 1537.4101 | 1856 | 1537.4101 | 1858.5 | 211201.9994
1861.5 | 15.563 | 1864.5 | 2.2215 | 1867 | 18.6958 | 1870 | 8134.8016 | 1872.5 | 20529.9879 | 1875.5 | 7.8277 | 1878.5 | 18.9789 | 1881 | 34224.4155 | 1884 | 47819.3088 | 1886.5 | 16.473 | 1889.5 | 40722.2794 | 1892.5 | 1537.4099 | 1895 | 17424.6241 | 1898 | 53717.39 | 1900.5 | 211201.9994
1903.5 | 23.8944 | 1906.5 | 1.336 | 1909 | 34.1601 | 1912 | 33624.7795 | 1914.5 | 9634.2401 | 1917.5 | 17.0997 | 1920.5 | 2.8704 | 1923 | 46619.4956 | 1926 | 63313.2526 | 1928.5 | 26.5213 | 1931.5 | 10533.9334 | 1934.5 | 60114.9266 | 1937 | 4036.4513 | 1940 | 30826.1728 | 1942.5 | 211201.9994
1945.5 | 0.23446 | 1948.5 | 13.9771 | 1951 | 23.4705 | 1954 | 45819.9846 | 1956.5 | 4836.1126 | 1959.5 | 2.2681 | 1962.5 | 29.9091 | 1965 | 27327.1532 | 1968 | 52817.3552 | 1970.5 | 26.9044 | 1973.5 | 1637.3679 | 1976.5 | 51118.3797 | 1979 | 57016.1244 | 1982 | 12233.3064 | 1984.5 | 211201.9994
1987.5 | 7.2112 | 1990.5 | 4.0819 | 1993 | 28.371 | 1996 | 49399.1395 | 1998.5 | 49018.8698 | 2001.5 | 22.7863 | 2004.5 | 2.5696 | 2007 | 11433.4618 | 2011 | 37623.2941 | 2012.5 | 0.27266 | 2015.5 | 56894.0558 | 2018.5 | 1737.3332 | 2021 | 15725.9281 | 2024 | 60314.8588 | 2026.5 | 211201.9994
2029.5 | 20.8729 | 2032.5 | 3.2086 | 2035 | 2.1564 | 2038 | 4136.3737 | 2040.5 | 51417.9335 | 2043.5 | 6.8076 | 2046.5 | 6.0195 | 2049 | 45020.1305 | 2052 | 22429.233 | 2054.5 | 4.5475 | 2057.5 | 10533.9334 | 2060.5 | 33425.1707 | 2063 | 34824.6387 | 2066 | 7934.9556 | 2068.5 | 211201.9994
2071.5 | 26.4191 | 2074.5 | 31.569 | 2077 | 23.5916 | 2080 | 40422.1069 | 2082.5 | 30126.2429 | 2085.5 | 17.8727 | 2088.5 | 23.9636 | 2091 | 44320.4082 | 2094 | 68711.1427 | 2096.5 | 18.011 | 2099.5 | 48300.6932 | 2102.5 | 23628.9307 | 2105 | 12233.3064 | 2108 | 14632.3859 | 2110.5 | 211201.9994
2113.5 | 786.5071 | 2116.5 | 12.5272 | 2119 | 17.53 | 2122 | 68111.2202 | 2124.5 | 36123.9022 | 2127.5 | 36.0781 | 2130.5 | 6.4319 | 2133 | 50118.107 | 2136 | 16325.2328 | 2138.5 | 2.6856 | 2141.5 | 22229.4185 | 2144.5 | 13705.268 | 2147 | 7831.9878 | 2150 | 2402.4685 | 2152.5 | 42160.3969
2155.5 | 4173.0403 | 2158.5 | 31.6383 | 2161 | 16.0097 | 2164 | 62290.7626 | 2166.5 | 54075.2446 | 2169.5 | 14.7329 | 2172.5 | 28.2394 | 2175 | 33789.8803 | 2178 | 19486.7985 | 2180.5 | 27.4834 | 2183.5 | 19347.9877 | 2186.5 | 24163.169 | 2189 | 39869.0879 | 2192 | 18154.5085 | 2194.5 | 6503.168
2197.5 | 2008.2549 | 2200.5 | 31.9858 | 2203 | 35.6695 | 2205.5 | 18123.3127 | 2208.5 | 22614.4225 | 2211.5 | 11.6506 | 2214.5 | 27.0628 | 2217 | 58452.3939 | 2220 | 28536.5309 | 2222.5 | 17.3471 | 2225.5 | 58825.7625 | 2228.5 | 22466.0972 | 2231 | 59660.4279 | 2234 | 45354.1733 | 2236.5 | 3421.6634
2239.5 | 638.0635 | 2242.5 | 30.9486 | 2245 | 9.3735 | 2248 | 50553.3177 | 2250.5 | 59636.2133 | 2253.5 | 13.0176 | 2256.5 | 5.2938 | 2259 | 15185.8602 | 2261.5 | 47779.0357 | 2264.5 | 19.0772 | 2267.5 | 43477.1969 | 2270 | 47159.9531 | 2273 | 48846.0165 | 2276 | 3082.7675 | 2278.5 | 3886.7978
2281.5 | 416.2478 | 2284.5 | 25.1697 | 2287 | 10.3389 | 2290 | 55113.7945 | 2292.5 | 66212.8317 | 2295.5 | 34.6244 | 2298.5 | 21.0078 | 2301 | 13913.6211 | 2303.5 | 22920.3379 | 2306.5 | 4.3276 | 2309.5 | 36680.6807 | 2312 | 53023.7396 | 2315 | 12921.3327 | 2317.5 | 2620.3892 | 2320.5 | 3421.6634
2323.5 | 550.9726 | 2326 | 6.3742 | 2329 | 26.7597 | 2332 | 50829.0532 | 2334.5 | 25022.2318 | 2337.5 | 32.8493 | 2340 | 11.5824 | 2343 | 59173.2336 | 2346 | 15427.3623 | 2348.5 | 8.7092 | 2351.5 | 3106.5156 | 2354 | 2912.1151 | 2357 | 3601.723 | 2360 | 27454.4364 | 2362.5 | 5460.5557
2365.5 | 144.0214 | 2368 | 18.7213 | 2371 | 23.8345 | 2374 | 18101.8089 | 2376.5 | 46418.0225 | 2379.5 | 18.0396 | 2382.5 | 19.8403 | 2385 | 22783.2829 | 2387.5 | 16947.9133 | 2390.5 | 0.93335 | 2393.5 | 13365.4008 | 2396 | 40408.1041 | 2399 | 3112.7264 | 2401.5 | 3335.1519 | 2404.5 | 6943.3817
2407.5 | 206.3116 | 2410 | 17.5972 | 2413 | 32.2669 | 2415.5 | 30757.4311 | 2418.5 | 54874.7913 | 2421.5 | 10.6583 | 2424.5 | 11.3311 | 2427 | 16426.4509 | 2429.5 | 32387.1158 | 2432.5 | 9.8603 | 2435.5 | 59697.0681 | 2438.5 | 13224.629 | 2441 | 3314.9562 | 2443.5 | 11687.116 | 2446.5 | 6114.7439
2449.5 | 294.7877 | 2452.5 | 7.8155 | 2455 | 8.9444 | 2457.5 | 40465.8135 | 2460.5 | 34664.5852 | 2463.5 | 16.4992 | 2466 | 10.1397 | 2469 | 66089.2002 | 2471.5 | 18509.8651 | 2474.5 | 13.253 | 2477.5 | 3602.9029 | 2480.5 | 42584.9241 | 2483 | 50074.7902 | 2486 | 3440.3019 | 2488.5 | 5053.6823
2491.5 | 333.1548 | 2494 | 17.1533 | 2497 | 11.918 | 2499.5 | 67331.4239 | 2502.5 | 65371.2093 | 2505.5 | 29.9677 | 2508 | 9.7481 | 2511 | 48191.3523 | 2514 | 61781.1909 | 2516.5 | 5.7499 | 2519.5 | 43185.1772 | 2522.5 | 41803.345 | 2525 | 55381.9361 | 2528 | 24081.8402 | 2530.5 | 9961.9872
2533.5 | 79.414 | 2536.5 | 29.523 | 2539 | 28.698 | 2541.5 | 54899.6244 | 2544.5 | 49946.2641 | 2547.5 | 8.0152 | 2550.5 | 22.7404 | 2553 | 17653.5461 | 2556 | 62965.9857 | 2558.5 | 0.61447 | 2561.5 | 51478.4495 | 2564.5 | 46227.0024 | 2567 | 22507.7658 | 2569.5 | 18289.1563 | 2572.5 | 6716.1746
2575.5 | 200.1409 | 2578 | 39.9537 | 2581 | 10.0475 | 2583.5 | 60882.6293 | 2586.5 | 61317.5465 | 2589.5 | 29.4992 | 2592 | 21.5404 | 2595 | 67192.0212 | 2597.5 | 64291.3176 | 2600.5 | 19.5888 | 2603.5 | 56377.3968 | 2606.5 | 19132.228 | 2609 | 3106.7088 | 2611.5 | 7023.0202 | 2614.5 | 4595.5725
2617.5 | 236.4373 | 2620 | 34.6139 | 2623 | 19.5423 | 2626 | 56531.6731 | 2628.5 | 36558.4839 | 2631.5 | 39.3865 | 2634 | 40.4946 | 2637 | 37189.9961 | 2639.5 | 71714.8741 | 2642.5 | 8.5669 | 2645.5 | 43545.173 | 2648 | 40767.0288 | 2651 | 37757.6995 | 2654 | 53343.5259 | 2656.5 | 4395.7585
2659.5 | 11.186 | 2662 | 1.5455 | 2665 | 19.6561 | 2667.5 | 57467.7432 | 2670.5 | 19415.8316 | 2673.5 | 0.65153 | 2676 | 29.5718 | 2679 | 15507.703 | 2682 | 21822.733 | 2684.5 | 12.2344 | 2687.5 | 60963.8279 | 2690.5 | 12625.5935 | 2693 | 28616.7971 | 2695.5 | 31061.5639 | 2698.5 | 4930.9744
2701.5 | 64.5844 | 2704 | 23.0069 | 2707 | 8.802 | 2709.5 | 42154.4551 | 2712.5 | 38756.2969 | 2715.5 | 4.8663 | 2718.5 | 0.01809 | 2721 | 53915.2034 | 2724 | 13834.5288 | 2726.5 | 3.7169 | 2729.5 | 61011.2451 | 2732.5 | 58905.4376 | 2735 | 19693.4403 | 2738 | 61983.0138 | 2740.5 | 5937.1786
2743.5 | 10.3388 | 2746.5 | 3.7746 | 2749 | 3.9495 | 2751.5 | 19812.6225 | 2754.5 | 51850.8073 | 2757.5 | 8.8191 | 2760 | 7.4531 | 2763 | 23577.8868 | 2765.5 | 37387.9996 | 2768.5 | 26.1404 | 2771.5 | 7590.8406 | 2774 | 32102.2623 | 2777 | 42425.4134 | 2779.5 | 19609.3091 | 2782.5 | 6716.1746
2785.5 | 1.3151 | 2788 | 6.9277 | 2791 | 19.4288 | 2793.5 | 1530.7464 | 2796.5 | 1529.0002 | 2799.5 | 9.9738 | 2802 | 10.0906 | 2805 | 17049.603 | 2807.5 | 13542.0846 | 2810.5 | 5.3909 | 2813.5 | 20144.2831 | 2816 | 36995.1168 | 2819 | 38758.7948 | 2821.5 | 26017.7045 | 2824.5 | 12329.519
2827.5 | 20.2273 | 2830 | 8.622 | 2833 | 21.0958 | 2835.5 | 47270.202 | 2838.5 | 50499.7193 | 2841.5 | 20.6576 | 2844 | 3.7829 | 2847 | 1530.6773 | 2849.5 | 1535.5963 | 2852.5 | 0.59901 | 2855.5 | 6014.6997 | 2858 | 10725.6403 | 2861 | 8608.1839 | 2863.5 | 43388.0211 | 2866.5 | 14992.9915
2869.5 | 5.009 | 2872 | 9.1983 | 2875 | 4.6925 | 2877.5 | 4621.5944 | 2880.5 | 46883.0671 | 2883.5 | 1.4708 | 2886 | 12.7014 | 2889 | 38101.4563 | 2892 | 8931.0155 | 2894.5 | 0.27266 | 2897.5 | 51977.0417 | 2900 | 54575.1105 | 2903 | 50482.6318 | 2906 | 48001.1523 | 2908 | 19109.266
2911.5 | 16.5445 | 2914.5 | 8.336 | 2917 | 16.2245 | 2919.5 | 38715.8862 | 2922.5 | 5633.6011 | 2925.5 | 14.2601 | 2928 | 16.4105 | 2931 | 23363.6049 | 2934 | 22920.0753 | 2936.5 | 1.3823 | 2939.5 | 38648.3072 | 2942 | 59069.9309 | 2945 | 55809.2777 | 2947.5 | 58293.2516 | 2950.5 | 30085.9957
2953.5 | 19.4152 | 2956 | 25.1697 | 2959 | 19.8271 | 2961.5 | 32174.6486 | 2964.5 | 4734.3033 | 2967.5 | 2.0571 | 2970 | 12.4964 | 2973 | 12113.9203 | 2975.5 | 30913.8238 | 2978.5 | 8.2363 | 2981.5 | 53734.121 | 2984 | 9330.8345 | 2987 | 26507.4659 | 2989.5 | 9031.0674 | 2992.5 | 105550.9988
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!

## C-G Min
Average Conductor to Ground Resistances
Open Burn Test 13 |  |  | 2006-11-28 | 9:21
Mixed | 7-C | Tray F | IRMS | 1
0 | 150 kW
Burner Time | A1-G |  | Burner Time | A2-G | Burner Time | B3-G | Burner Time | B4-G | Burner Time | C5-G | Burner Time | C6-G
-232.5 | 254338 |  | -223.5 | 251938 | -218 | 256638 | -214.6 | 256338 | -212.3 | 211202 | -210.1 | 211202
-190.5 | 254338 |  | -181.7 | 251938 | -176.1 | 256638 | -172.6 | 256338 | -170.3 | 211202 | -168.2 | 211202
-148.5 | 254338 |  | -139.5 | 251938 | -134 | 256638 | -130.6 | 256338 | -128.3 | 211202 | -126.1 | 211202
-106.5 | 254338 |  | -97.7 | 251938 | -92.1 | 256638 | -88.6 | 256338 | -86.3 | 211202 | -84.2 | 211202
-64.6 | 254338 |  | -55.5 | 251938 | -50.1 | 256638 | -46.7 | 256338 | -44.5 | 211202 | -42.2 | 211202
-22.6 | 254338 |  | -13.7 | 251938 | -8.1 | 256638 | -4.7 | 256338 | -2.4 | 211202 | -0.3 | 211202
19.5 | 254338 |  | 28.3 | 251938 | 33.8 | 256638 | 37.3 | 256338 | 39.6 | 211202 | 41.7 | 211202
61.3 | 254338 |  | 70.3 | 251938 | 75.9 | 256638 | 79.3 | 256338 | 81.6 | 211202 | 83.8 | 211202
103.3 | 254338 |  | 112.2 | 251938 | 117.8 | 256638 | 121.3 | 256338 | 123.5 | 211202 | 125.7 | 211202
145.3 | 254338 |  | 154.2 | 251938 | 159.8 | 256638 | 163.3 | 256338 | 165.5 | 211202 | 167.7 | 211202
187.3 | 254338 |  | 196.3 | 251938 | 201.9 | 256638 | 205.3 | 256338 | 207.6 | 211202 | 209.8 | 211202
229.3 | 254338 |  | 238.2 | 251938 | 243.8 | 256638 | 247.3 | 256338 | 249.5 | 211202 | 251.7 | 211202
271.3 | 254338 |  | 280.2 | 251938 | 285.8 | 256638 | 289.3 | 256338 | 291.5 | 211202 | 293.7 | 211202
313.3 | 254338 |  | 322.2 | 251938 | 327.8 | 256638 | 331.3 | 256338 | 333.5 | 211202 | 335.7 | 211202
355.3 | 254338 |  | 364.2 | 251938 | 369.8 | 256638 | 373.3 | 256338 | 375.5 | 211202 | 377.7 | 211202
397.3 | 254338 |  | 406.2 | 251938 | 411.8 | 256638 | 415.3 | 256338 | 417.5 | 211202 | 419.7 | 211202
439.3 | 254338 |  | 448.2 | 251938 | 453.8 | 256638 | 457.3 | 256338 | 459.5 | 211202 | 461.7 | 211202
481.3 | 254338 |  | 490.2 | 251938 | 495.8 | 256638 | 499.3 | 256338 | 501.5 | 211202 | 503.7 | 211202
523.3 | 254338 |  | 532.2 | 251938 | 537.8 | 256638 | 541.3 | 256338 | 543.5 | 211202 | 545.7 | 211202
565.3 | 254338 |  | 574.2 | 251938 | 579.8 | 256638 | 583.3 | 256338 | 585.5 | 211202 | 587.7 | 211202
607.3 | 254338 |  | 616.2 | 251938 | 621.8 | 256638 | 625.3 | 256338 | 627.5 | 211202 | 629.7 | 211202
649.3 | 254338 |  | 658.2 | 251938 | 663.8 | 256638 | 667.3 | 256338 | 669.5 | 211202 | 671.7 | 211202
691.3 | 254338 |  | 700.2 | 251938 | 705.8 | 256638 | 709.3 | 256338 | 711.5 | 211202 | 713.7 | 211202
733.3 | 254338 |  | 742.2 | 251938 | 747.7 | 256638 | 751.2 | 256338 | 753.5 | 211202 | 755.7 | 211202
775.3 | 254338 |  | 784.2 | 251938 | 789.8 | 256638 | 793.3 | 256338 | 795.5 | 211202 | 797.7 | 211202
817.3 | 254338 |  | 826.2 | 251938 | 831.8 | 256638 | 835.3 | 256338 | 837.5 | 211202 | 839.7 | 211202
859.3 | 254338 |  | 868.2 | 251938 | 873.8 | 256638 | 877.3 | 256338 | 879.5 | 211202 | 881.7 | 211202
901.3 | 254338 |  | 910.2 | 251938 | 915.8 | 256638 | 919.3 | 256338 | 921.5 | 211202 | 923.7 | 211202
943.1 | 254338 |  | 952.1 | 251938 | 957.8 | 35.2679 | 961.2 | 55.7908 | 963.4 | 211202 | 965.6 | 211202
985.3 | 254338 |  | 994.2 | 251938 | 999.7 | 2.7113 | 1003.1 | 5.6926 | 1005.3 | 211202 | 1007.6 | 63775.3574
1027.1 | 254338 |  | 1036.1 | 251938 | 1041.7 | 3.491 | 1045.1 | 10.0203 | 1047.4 | 211202 | 1049.6 | 211202
1069.2 | 254338 |  | 1078.2 | 251938 | 1083.7 | 6.7457 | 1087.1 | 2.3884 | 1089.3 | 211202 | 1091.5 | 211202
1111 | 254338 |  | 1120.2 | 251938 | 1125.7 | 15.2842 | 1129.2 | 9.65 | 1131.5 | 211202 | 1133.6 | 211202
1153.1 | 254338 |  | 1162.2 | 251938 | 1167.8 | 14.9747 | 1171.2 | 12.7815 | 1173.4 | 211202 | 1175.5 | 211202
1195.1 | 254338 |  | 1204.1 | 251938 | 1209.7 | 8.3562 | 1213.1 | 12.8792 | 1215.3 | 211202 | 1217.5 | 211202
1237.2 | 10497.5886 |  | 1246.2 | 47.3322 | 1251.7 | 8.4471 | 1255.1 | 5.8643 | 1257.5 | 211202 | 1259.7 | 211202
1279.2 | 72.8875 |  | 1288.1 | 115.8971 | 1293.7 | 10.6282 | 1297.2 | 14.1142 | 1299.4 | 211202 | 1301.6 | 211202
1321.2 | 8.1829 |  | 1330.1 | 9.0169 | 1335.8 | 16.8065 | 1339.2 | 16.1488 | 1341.4 | 211202 | 1343.7 | 211202
1363.2 | 5.3159 |  | 1372.1 | 4.3654 | 1377.7 | 12.3322 | 1381.1 | 3.7011 | 1383.2 | 211202 | 1385.5 | 211202
1405.2 | 4.6296 |  | 1414.2 | 11.247 | 1419.8 | 3.4524 | 1423.1 | 3.4024 | 1425.4 | 211202 | 1427.7 | 211202
1447.1 | 8.0093 |  | 1456.2 | 2.9045 | 1461.7 | 4.7503 | 1465 | 4.5899 | 1467.3 | 211202 | 1469.5 | 211202
1489.1 | 8.2634 |  | 1498.1 | 10.275 | 1503.7 | 3.2873 | 1507 | 3.9352 | 1509.2 | 130269 | 1511.5 | 211202
1531.1 | 10.9978 |  | 1540.1 | 5.4887 | 1545.7 | 4.2912 | 1549 | 8.4763 | 1551.2 | 211202 | 1553.5 | 128069
1573.1 | 7.2574 |  | 1582.1 | 13.7431 | 1587.7 | 2.9586 | 1591 | 2.9177 | 1593.2 | 211202 | 1595.5 | 211202
1615.1 | 6.0149 |  | 1624.1 | 8.4017 | 1629.7 | 4.971 | 1633 | 13.9753 | 1635.2 | 211202 | 1637.5 | 211202
1657.1 | 10.103 |  | 1666.1 | 19.2162 | 1671.7 | 10.188 | 1675 | 4.4966 | 1677.2 | 129469 | 1679.5 | 211202
1699.1 | 14.392 |  | 1708.1 | 7.3819 | 1713.7 | 3.3285 | 1717 | 11.7126 | 1719.2 | 211202 | 1721.5 | 211202
1741.1 | 20.5186 |  | 1750.1 | 2.9159 | 1755.7 | 3.6567 | 1759 | 1.258 | 1761.2 | 211202 | 1763.5 | 211202
1783.1 | 7.9958 |  | 1792.1 | 13.3441 | 1797.7 | 0.83385 | 1801 | 0.63439 | 1803.2 | 211202 | 1805.5 | 211202
1825.1 | 4.5443 |  | 1834.1 | 6.7082 | 1839.7 | 0.63636 | 1843 | 0.63243 | 1845.2 | 211202 | 1847.5 | 211202
1867.1 | 3.3474 |  | 1876.1 | 9.2722 | 1881.7 | 0.63268 | 1885 | 7.2143 | 1887.2 | 130269 | 1889.5 | 211202
1909.1 | 2.8598 |  | 1918.1 | 4.3704 | 1923.7 | 4.2826 | 1927 | 1.6133 | 1929.2 | 211202 | 1931.5 | 211202
1951.1 | 1.7674 |  | 1960.1 | 3.7888 | 1965.7 | 0.6376 | 1969 | 1.1481 | 1971.2 | 211202 | 1973.5 | 211202
1993.1 | 5.5666 |  | 2002.3 | 2.1335 | 2007.7 | 0.71048 | 2011 | 0.67338 | 2013.2 | 127118.9999 | 2015.7 | 211202
2035.1 | 1.6945 |  | 2044.1 | 7.4761 | 2049.7 | 0.6421 | 2053 | 3.1821 | 2055.2 | 211202 | 2057.5 | 211202
2077.1 | 13.3796 |  | 2086.1 | 3.1227 | 2091.7 | 10.0245 | 2095 | 4.969 | 2097.2 | 129469 | 2099.5 | 211202
2119.1 | 13.9033 |  | 2128.1 | 6.8663 | 2133.7 | 4.2021 | 2137 | 0.98335 | 2139.2 | 42160.4 | 2141.5 | 3053.7612
2161.1 | 17.3613 |  | 2170.1 | 8.6362 | 2175.7 | 7.814 | 2179 | 2.9586 | 2181.2 | 6503.1875 | 2183.5 | 1135.6842
2203 | 7.7704 |  | 2212.1 | 13.0468 | 2217.7 | 10.1178 | 2221 | 18.8646 | 2223.1 | 3421.7 | 2225.5 | 882.8
2245.1 | 10.8051 |  | 2254 | 6.5277 | 2259.6 | 20.3898 | 2263 | 1.2973 | 2265.2 | 3886.8302 | 2267.3 | 1114.3793
2287.1 | 7.6804 |  | 2296 | 5.9899 | 2301.6 | 5.8209 | 2304.9 | 1.1009 | 2307.2 | 3421.7 | 2309.2 | 1281.0588
2329 | 7.8278 |  | 2338 | 6.6882 | 2343.5 | 1.2191 | 2346.9 | 1.455 | 2349.2 | 5460.5789 | 2351.4 | 1931.75
2371 | 7.7704 |  | 2380 | 7.4951 | 2385.5 | 0.63686 | 2388.9 | 1.258 | 2391.2 | 6943.4 | 2393.2 | 1525.4
2412.9 | 13.9508 |  | 2422 | 7.071 | 2427.6 | 1.189 | 2430.9 | 1.3367 | 2433.1 | 6114.7647 | 2435.3 | 2476.8537
2455 | 9.2502 |  | 2463.9 | 8.0854 | 2469.7 | 1.4642 | 2472.9 | 1.4156 | 2475.1 | 5053.7073 | 2477.4 | 2056.1429
2496.9 | 13.3179 |  | 2506 | 11.1565 | 2511.6 | 7.2237 | 2514.9 | 2.5002 | 2517.1 | 9962 | 2519.5 | 3886.8302
2539 | 10.8223 |  | 2548.1 | 7.6198 | 2553.7 | 0.95086 | 2556.9 | 7.7017 | 2559.1 | 6716.1935 | 2561.4 | 3201.5938
2580.9 | 11.4706 |  | 2589.9 | 22.8151 | 2595.6 | 8.1071 | 2598.8 | 1.258 | 2601.1 | 4595.6 | 2603.3 | 3673.25
2623 | 17.0038 |  | 2631.9 | 17.6182 | 2637.5 | 4.1652 | 2640.9 | 12.2758 | 2643.2 | 4395.7872 | 2645.3 | 3673.25
2664.9 | 3.0662 |  | 2674 | 0.91257 | 2679.6 | 5.1829 | 2682.8 | 12.4895 | 2685.1 | 4931 | 2687.4 | 4212.2857
2706.9 | 10.241 |  | 2716.1 | 1.5596 | 2721.6 | 5.2187 | 2725 | 0.64286 | 2727.1 | 5937.2 | 2729.5 | 6114.7647
2749 | 5.2636 |  | 2757.9 | 0.80394 | 2763.6 | 0.7606 | 2766.8 | 1.9449 | 2769.1 | 6716.1935 | 2771.2 | 6303.0909
2790.9 | 0.64336 |  | 2799.9 | 0.64514 | 2805.5 | 3.232 | 2808.8 | 2.5342 | 2811.1 | 12329.5294 | 2813.2 | 13986.8
2832.9 | 10.0463 |  | 2841.9 | 0.64437 | 2847.5 | 2.146 | 2850.8 | 2.5406 | 2853.1 | 14993 | 2855.2 | 36519.7143
2874.9 | 1.8982 |  | 2884 | 3.0032 | 2889.5 | 1.8245 | 2892.9 | 1.3589 | 2895 | 19109.2727 | 2897.3 | 70334
2917 | 2.2906 |  | 2926 | 5.1597 | 2931.6 | 2.9177 | 2934.8 | 11.52 | 2937.1 | 30086 | 2939.3 | 86779.3334
2958.9 | 1.9244 |  | 2967.9 | 3.5809 | 2973.5 | 3.7587 | 2976.8 | 3.6334 | 2979.1 | 50307.6 | 2981.2 | 127869
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!

## C5-C6
Open Burn Test 13 |  |  | 2006-11-28 | 9:21 |  |  | Vs = |  | 129 |  | R = | 100
Mixed | 7-C | Tray F | IRMS | 1
0 | 150 kW |  | Bundle | Ch. 5 & 6 | Cable C | Odd-Even
Time-29 | N11 | N12 | Time-30 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R6-G | R5-6
39049.385 | 1 | 0 | 39049.385 | 1 | 0 |  | -199 | 40 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39049.3855 | 1 | 0 | 39049.3855 | 1 | 0 |  | -157 | 82 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39049.386 | 1 | 0 | 39049.386 | 1 | 0 |  | -115 | 124 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39049.3865 | 1 | 0 | 39049.3865 | 1 | 0 |  | -73 | 166 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39049.387 | 1 | 0 | 39049.387 | 1 | 0 |  | -31 | 208 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39049.3875 | 1 | 0 | 39049.3875 | 1 | 0 |  | 11 | 250 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39049.3879 | 1 | 0 | 39049.388 | 1 | 0 |  | 53 | 292 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39049.3884 | 1 | 0 | 39049.3884 | 1 | 0 |  | 95 | 334 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39049.3889 | 1 | 0 | 39049.3889 | 1 | 0 |  | 137 | 376 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39049.3894 | 1 | 0 | 39049.3894 | 1 | 0 |  | 179 | 418 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39049.3899 | 1 | 0 | 39049.3899 | 1 | 0 |  | 221 | 460 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39049.3904 | 1 | 0 | 39049.3904 | 1 | 0 |  | 263 | 502 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39049.3909 | 1 | 0 | 39049.3909 | 1 | 0 |  | 305 | 544 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39049.3913 | 1 | 0 | 39049.3914 | 1 | 0 |  | 347 | 586 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39049.3918 | 1 | 0 | 39049.3919 | 1 | 0 |  | 389 | 628 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39049.3923 | 1 | 0 | 39049.3923 | 1 | 0 |  | 431 | 670 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39049.3928 | 1 | 0 | 39049.3928 | 1 | 0 |  | 473 | 712 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39049.3933 | 1 | 0 | 39049.3933 | 1 | 0 |  | 515 | 754 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39049.3938 | 1 | 0 | 39049.3938 | 1 | 0 |  | 557 | 796 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39049.3943 | 1 | 0 | 39049.3943 | 1 | 0 |  | 599 | 838 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39049.3947 | 1 | 0 | 39049.3948 | 1 | 0 |  | 641 | 880 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39049.3952 | 1 | 0 | 39049.3953 | 1 | 0 |  | 683 | 922 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39049.3957 | 1 | 0 | 39049.3957 | 1 | 0 |  | 725 | 964 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39049.3962 | 1 | 0 | 39049.3962 | 1 | 0 |  | 767 | 1006 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39049.3967 | 1 | 0 | 39049.3967 | 1 | 0 |  | 809 | 1048 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39049.3972 | 1 | 0 | 39049.3972 | 1 | 0 |  | 851 | 1090 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39049.3977 | 1 | 0 | 39049.3977 | 1 | 0 |  | 893 | 1132 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39049.3981 | 1 | 0 | 39049.3982 | 1 | 0 |  | 935 | 1174 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39049.3986 | 1 | 0 | 39049.3987 | 1 | 0 |  | 977 | 1216 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39049.3991 | 1 | 0 | 39049.3991 | 1 | 0 |  | 1018.5 | 1257.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39049.3996 | 1 | 0 | 39049.3996 | 1 | 0 |  | 1061 | 1300 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39049.4001 | 1 | 0 | 39049.4001 | 1 | 0 |  | 1102.5 | 1341.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39049.4006 | 1 | 0 | 39049.4006 | 1 | 0 |  | 1145 | 1384 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39049.4011 | 1 | 0 | 39049.4011 | 1 | 0 |  | 1186.5 | 1425.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39049.4016 | 1 | 0 | 39049.4016 | 1 | 0 |  | 1228.5 | 1467.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39049.402 | 1 | 0 | 39049.4021 | 1 | 0 |  | 1271 | 1510 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39049.4025 | 1 | 0 | 39049.4025 | 1 | 0 |  | 1313 | 1552 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39049.403 | 1 | 0 | 39049.403 | 1 | 0 |  | 1355 | 1594 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39049.4035 | 1 | 0 | 39049.4035 | 1 | 0 |  | 1396.5 | 1635.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39049.404 | 1 | 0 | 39049.404 | 1 | 0 |  | 1439 | 1678 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39049.4045 | 1 | 0 | 39049.4045 | 1 | 0 |  | 1480.5 | 1719.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39049.405 | 1 | 0 | 39049.405 | 1 | 0 |  | 1522.5 | 1761.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39049.4054 | 1 | 0 | 39049.4055 | 1 | 0 |  | 1564.5 | 1803.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39049.4059 | 1 | 0 | 39049.4059 | 1 | 0 |  | 1606.5 | 1845.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39049.4064 | 1 | 0 | 39049.4064 | 1 | 0 |  | 1648.5 | 1887.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39049.4069 | 1 | 0 | 39049.4069 | 1 | 0 |  | 1690.5 | 1929.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39049.4074 | 1 | 0 | 39049.4074 | 1 | 0 |  | 1732.5 | 1971.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39049.4079 | 1 | 0 | 39049.4079 | 1 | 0 |  | 1774.5 | 2013.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39049.4084 | 1 | 0 | 39049.4084 | 1 | 0 |  | 1816.5 | 2055.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39049.4088 | 1 | 0 | 39049.4089 | 1 | 0 |  | 1858.5 | 2097.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39049.4093 | 1 | 0 | 39049.4093 | 1 | 0 |  | 1900.5 | 2139.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39049.4098 | 1 | 0 | 39049.4098 | 1 | 0 |  | 1942.5 | 2181.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39049.4103 | 1 | 0 | 39049.4103 | 1 | 0 |  | 1984.5 | 2223.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39049.4108 | 1 | 0 | 39049.4108 | 1 | 0 |  | 2026.5 | 2265.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39049.4113 | 1 | 0 | 39049.4113 | 1 | 0 |  | 2068.5 | 2307.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39049.4118 | 1 | 0 | 39049.4118 | 1 | 0 |  | 2110.5 | 2349.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39049.4122 | 5 | 0 | 39049.4123 | 67 | 0 |  | 2152.5 | 2391.5 | 0.30525 | 0 | 4.0904 | 0 | 0.0030525 | 0 | 0.040904 | 0 | 0.0030525 | 0.040904 | 42160.4 | 3053.7612 | 42160.3969
39049.4127 | 32 | 0 | 39049.4127 | 171 | 0 |  | 2194.5 | 2433.5 | 1.9536 | 0 | 10.4396 | 0 | 0.019536 | 0 | 0.1044 | 0 | 0.019536 | 0.1044 | 6503.1875 | 1135.6842 | 6503.168
39049.4132 | 60 | 0 | 39049.4132 | 215 | 0 |  | 2236.5 | 2475.5 | 3.663 | 0 | 13.1258 | 0 | 0.03663 | 0 | 0.13126 | 0 | 0.03663 | 0.13126 | 3421.7 | 882.8 | 3421.6634
39049.4137 | 53 | 0 | 39049.4137 | 174 | 0 |  | 2278.5 | 2517.5 | 3.2357 | 0 | 10.6227 | 0 | 0.032357 | 0 | 0.10623 | 0 | 0.032357 | 0.10623 | 3886.8302 | 1114.3793 | 3886.7978
39049.4142 | 60 | 0 | 39049.4142 | 153 | 0 |  | 2320.5 | 2559.5 | 3.663 | 0 | 9.3407 | 0 | 0.03663 | 0 | 0.093407 | 0 | 0.03663 | 0.093407 | 3421.7 | 1281.0588 | 3421.6634
39049.4147 | 38 | 0 | 39049.4147 | 104 | 0 |  | 2362.5 | 2601.5 | 2.3199 | 0 | 6.3492 | 0 | 0.023199 | 0 | 0.063492 | 0 | 0.023199 | 0.063492 | 5460.5789 | 1931.75 | 5460.5557
39049.4152 | 30 | 0 | 39049.4152 | 130 | 0 |  | 2404.5 | 2643.5 | 1.8315 | 0 | 7.9365 | 0 | 0.018315 | 0 | 0.079365 | 0 | 0.018315 | 0.079365 | 6943.4 | 1525.4 | 6943.3817
39049.4156 | 34 | 0 | 39049.4157 | 82 | 0 |  | 2446.5 | 2685.5 | 2.0757 | 0 | 5.0061 | 0 | 0.020757 | 0 | 0.050061 | 0 | 0.020757 | 0.050061 | 6114.7647 | 2476.8537 | 6114.7439
39049.4161 | 41 | 0 | 39049.4161 | 98 | 0 |  | 2488.5 | 2727.5 | 2.5031 | 0 | 5.9829 | 0 | 0.025031 | 0 | 0.059829 | 0 | 0.025031 | 0.059829 | 5053.7073 | 2056.1429 | 5053.6823
39049.4166 | 21 | 0 | 39049.4166 | 53 | 0 |  | 2530.5 | 2769.5 | 1.2821 | 0 | 3.2357 | 0 | 0.012821 | 0 | 0.032357 | 0 | 0.012821 | 0.032357 | 9962 | 3886.8302 | 9961.9872
39049.4171 | 31 | 0 | 39049.4171 | 64 | 0 |  | 2572.5 | 2811.5 | 1.8926 | 0 | 3.9072 | 0 | 0.018926 | 0 | 0.039072 | 0 | 0.018926 | 0.039072 | 6716.1935 | 3201.5938 | 6716.1746
39049.4176 | 45 | 0 | 39049.4176 | 56 | 0 |  | 2614.5 | 2853.5 | 2.7473 | 0 | 3.4188 | 0 | 0.027473 | 0 | 0.034188 | 0 | 0.027473 | 0.034188 | 4595.6 | 3673.25 | 4595.5725
39049.4181 | 47 | 0 | 39049.4181 | 56 | 0 |  | 2656.5 | 2895.5 | 2.8694 | 0 | 3.4188 | 0 | 0.028694 | 0 | 0.034188 | 0 | 0.028694 | 0.034188 | 4395.7872 | 3673.25 | 4395.7585
39049.4186 | 42 | 0 | 39049.4186 | 49 | 0 |  | 2698.5 | 2937.5 | 2.5641 | 0 | 2.9915 | 0 | 0.025641 | 0 | 0.029915 | 0 | 0.025641 | 0.029915 | 4931 | 4212.2857 | 4930.9744
39049.4191 | 35 | 0 | 39049.4191 | 34 | 0 |  | 2740.5 | 2979.5 | 2.1368 | 0 | 2.0757 | 0 | 0.021368 | 0 | 0.020757 | 0 | 0.021368 | 0.020757 | 5937.2 | 6114.7647 | 5937.1786
39049.4195 | 31 | 0 | 39049.4195 | 33 | 0 |  | 2782.5 | 3021.5 | 1.8926 | 0 | 2.0147 | 0 | 0.018926 | 0 | 0.020147 | 0 | 0.018926 | 0.020147 | 6716.1935 | 6303.0909 | 6716.1746
39049.42 | 17 | 0 | 39049.42 | 15 | 0 |  | 2824.5 | 3063.5 | 1.0379 | 0 | 0.91575 | 0 | 0.010379 | 0 | 0.0091575 | 0 | 0.010379 | 0.0091575 | 12329.5294 | 13986.8 | 12329.519
39049.4205 | 14 | 0 | 39049.4205 | 4 | 0 |  | 2866.5 | 3105.5 | 0.8547 | 0 | 0.2442 | 0 | 0.008547 | 0 | 0.002442 | 0 | 0.008547 | 0.002442 | 14993 | 52725.5 | 14992.9915
39049.421 | 11 | 0 |  | 3 | 0 |  | 2908 | 3147 | 0.67155 | 0 | 0.18315 | 0 | 0.0067155 | 0 | 0.0018315 | 0 | 0.0067155 | 0.0018315 | 19109.2727 | 70334 | 19109.266
39049.4215 | 7 | 0 | 39049.4215 | 2 | 0 |  | 2950.5 | 3189.5 | 0.42735 | 0 | 0.1221 | 0 | 0.0042735 | 0 | 0.001221 | 0 | 0.0042735 | 0.001221 | 30086 | 105551 | 30085.9957
39049.422 | 2 | 0 | 39049.422 | 1 | 0 |  | 2992.5 | 3231.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988

## B4-C6
Open Burn Test 13 |  |  | 2006-11-28 | 9:21 |  |  | Vs = |  | 159.1807 |  | R = | 100
Mixed | 7-C | Tray F | IRMS | 1
0 | 150 kW |  | Bundle | Ch. 4 & 6 | Cable B | Even - | Cable C |  | Even
Time-27 | N11 | N12 | Time-28 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R6-G | R4-6
39049.385 | 1 | 0 | 39049.385 | 1 | 0 |  | -201.5 | 37.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260638 | 260638 | 260637.9994
39049.3855 | 1 | 0 | 39049.3855 | 1 | 0 |  | -159.5 | 79.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260638 | 260638 | 260637.9994
39049.386 | 1 | 0 | 39049.386 | 1 | 0 |  | -117.5 | 121.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260638 | 260638 | 260637.9994
39049.3865 | 1 | 1 | 39049.3865 | 1 | 0 |  | -75.5 | 163.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 679321670.44 | 260638 | 260438.0767
39049.3869 | 1 | 0 | 39049.387 | 1 | 0 |  | -34 | 205 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260638 | 260638 | 260637.9994
39049.3874 | 1 | 0 | 39049.3874 | 1 | 0 |  | 8 | 247 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260638 | 260638 | 260637.9994
39049.3879 | 1 | 0 | 39049.3879 | 1 | 0 |  | 50 | 289 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260638 | 260638 | 260637.9994
39049.3884 | 1 | 0 | 39049.3884 | 1 | 0 |  | 92 | 331 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260638 | 260638 | 260637.9994
39049.3889 | 1 | 0 | 39049.3889 | 1 | 0 |  | 134 | 373 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260638 | 260638 | 260637.9994
39049.3894 | 1 | 0 | 39049.3894 | 1 | 0 |  | 176 | 415 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260638 | 260638 | 260637.9994
39049.3898 | 1 | 0 | 39049.3899 | 1 | 0 |  | 218 | 457 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260638 | 260638 | 260637.9994
39049.3903 | 1 | 0 | 39049.3904 | 1 | 0 |  | 260 | 499 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260638 | 260638 | 260637.9994
39049.3908 | 1 | 0 | 39049.3908 | 1 | 0 |  | 302 | 541 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260638 | 260638 | 260637.9994
39049.3913 | 1 | 0 | 39049.3913 | 1 | 0 |  | 344 | 583 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260638 | 260638 | 260637.9994
39049.3918 | 1 | 0 | 39049.3918 | 1 | 0 |  | 386 | 625 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260638 | 260638 | 260637.9994
39049.3923 | 1 | 0 | 39049.3923 | 1 | 0 |  | 428 | 667 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260638 | 260638 | 260637.9994
39049.3928 | 1 | 0 | 39049.3928 | 1 | 0 |  | 470 | 709 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260638 | 260638 | 260637.9994
39049.3933 | 1 | 0 | 39049.3933 | 1 | 0 |  | 512 | 751 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260638 | 260638 | 260637.9994
39049.3937 | 1 | 0 | 39049.3938 | 1 | 0 |  | 554 | 793 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260638 | 260638 | 260637.9994
39049.3942 | 1 | 0 | 39049.3942 | 1 | 0 |  | 596 | 835 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260638 | 260638 | 260637.9994
39049.3947 | 1 | 0 | 39049.3947 | 1 | 0 |  | 638 | 877 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260638 | 260638 | 260637.9994
39049.3952 | 1 | 0 | 39049.3952 | 1 | 0 |  | 680 | 919 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260638 | 260638 | 260637.9994
39049.3957 | 1 | 0 | 39049.3957 | 1 | 0 |  | 722 | 961 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260638 | 260638 | 260637.9994
39049.3962 | 1 | 0 | 39049.3962 | 1 | 0 |  | 764 | 1003 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260638 | 260638 | 260637.9994
39049.3967 | 1 | 0 | 39049.3967 | 1 | 0 |  | 806 | 1045 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260638 | 260638 | 260637.9994
39049.3971 | 1 | 0 | 39049.3972 | 1 | 0 |  | 848 | 1087 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260638 | 260638 | 260637.9994
39049.3976 | 1 | 0 | 39049.3977 | 1 | 0 |  | 890 | 1129 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260638 | 260638 | 260637.9994
39049.3981 | 1 | 0 | 39049.3981 | 1 | 0 |  | 932 | 1171 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260638 | 260638 | 260637.9994
39049.3986 | 1674 | 1 | 39049.3986 | 1 | 0 |  | 974 | 1213 | 102.1978 | 0.06105 | 0.06105 | 0 | 1.022 | 0.0006105 | 0.0006105 | 0 | 1.0214 | 0.0006105 | 55.7908 | 260638.0001 | 93202.2407
39049.3991 | 2095 | 1 | 39049.3991 | 1 | 1 |  | 1016 | 1255 | 127.8999 | 0.06105 | 0.06105 | 0.06105 | 1.279 | 0.0006105 | 0.0006105 | 0.0006105 | 1.2784 | 0 | 24.4689 | 63775.3574 | 51057.941
39049.3996 | 2089 | 1 | 39049.3996 | 1 | 0 |  | 1058 | 1297 | 127.5336 | 0.06105 | 0.06105 | 0 | 1.2753 | 0.0006105 | 0.0006105 | 0 | 1.2747 | 0.0006105 | 24.8266 | 260638.0004 | 51718.1571
39049.4001 | 2514 | 1 | 39049.4001 | 1 | 0 |  | 1100 | 1339 | 153.4799 | 0.06105 | 0.06105 | 0 | 1.5348 | 0.0006105 | 0.0006105 | 0 | 1.5342 | 0.0006105 | 3.7159 | 260638.0001 | 9234.457
39049.4005 | 2378 | 1 | 39049.4006 | 1 | 0 |  | 1142 | 1381 | 145.177 | 0.06105 | 0.06105 | 0 | 1.4518 | 0.0006105 | 0.0006105 | 0 | 1.4512 | 0.0006105 | 9.65 | 260638.0001 | 22829.241
39049.401 | 1891 | 1 | 39049.4011 | 1 | 0 |  | 1184 | 1423 | 115.4457 | 0.06105 | 0.06105 | 0 | 1.1545 | 0.0006105 | 0.0006105 | 0 | 1.1538 | 0.0006105 | 37.9037 | 260638.0001 | 71510.5633
39049.4015 | 2310 | 1 | 39049.4015 | 1 | 0 |  | 1226 | 1465 | 141.0256 | 0.06105 | 0.06105 | 0 | 1.4103 | 0.0006105 | 0.0006105 | 0 | 1.4096 | 0.0006105 | 12.8792 | 260637.9999 | 29626.633
39049.402 | 2463 | 1 | 39049.402 | 1 | 0 |  | 1268 | 1507 | 150.3663 | 0.06105 | 0.06105 | 0 | 1.5037 | 0.0006105 | 0.0006105 | 0 | 1.5031 | 0.0006105 | 5.8643 | 260638.0001 | 14332.501
39049.4025 | 1408 | 1 | 39049.4025 | 1 | 0 |  | 1310 | 1549 | 85.9585 | 0.06105 | 0.06105 | 0 | 0.85958 | 0.0006105 | 0.0006105 | 0 | 0.85897 | 0.0006105 | 85.2438 | 260638.0001 | 119792.0389
39049.403 | 2245 | 1 | 39049.403 | 1 | 0 |  | 1352 | 1591 | 137.0574 | 0.06105 | 0.06105 | 0 | 1.3706 | 0.0006105 | 0.0006105 | 0 | 1.37 | 0.0006105 | 16.1488 | 260638.0001 | 36124.1401
39049.4035 | 2293 | 1 | 39049.4035 | 1 | 0 |  | 1394 | 1633 | 139.9878 | 0.06105 | 0.06105 | 0 | 1.3999 | 0.0006105 | 0.0006105 | 0 | 1.3993 | 0.0006105 | 13.7164 | 260638.0001 | 31325.981
39049.4039 | 2095 | 1 | 39049.404 | 1 | 0 |  | 1436 | 1675 | 127.8999 | 0.06105 | 0.06105 | 0 | 1.279 | 0.0006105 | 0.0006105 | 0 | 1.2784 | 0.0006105 | 24.469 | 260638.0001 | 51118.3872
39049.4044 | 2493 | 1 | 39049.4045 | 1 | 0 |  | 1478 | 1717 | 152.1978 | 0.06105 | 0.06105 | 0 | 1.522 | 0.0006105 | 0.0006105 | 0 | 1.5214 | 0.0006105 | 4.5899 | 260638.0001 | 11333.6516
39049.4049 | 2395 | 1 | 39049.4049 | 1 | 0 |  | 1520 | 1759 | 146.2149 | 0.06105 | 0.06105 | 0 | 1.4621 | 0.0006105 | 0.0006105 | 0 | 1.4615 | 0.0006105 | 8.8713 | 260637.9999 | 21129.893
39049.4054 | 2038 | 1 | 39049.4054 | 1 | 0 |  | 1562 | 1801 | 124.42 | 0.06105 | 0.06105 | 0 | 1.2442 | 0.0006105 | 0.0006105 | 0 | 1.2436 | 0.0006105 | 27.9519 | 260638.0001 | 56816.2011
39049.4059 | 1989 | 1 | 39049.4059 | 1 | 0 |  | 1604 | 1843 | 121.4286 | 0.06105 | 0.06105 | 0 | 1.2143 | 0.0006105 | 0.0006105 | 0 | 1.2137 | 0.0006105 | 31.1056 | 260638.0001 | 61714.3218
39049.4064 | 1987 | 1 | 39049.4064 | 1 | 0 |  | 1646 | 1885 | 121.3065 | 0.06105 | 0.06105 | 0 | 1.2131 | 0.0006105 | 0.0006105 | 0 | 1.2125 | 0.0006105 | 31.2377 | 260638.0001 | 61914.2451
39049.4069 | 2104 | 1 | 39049.4069 | 1 | 0 |  | 1688 | 1927 | 128.4493 | 0.06105 | 0.06105 | 0 | 1.2845 | 0.0006105 | 0.0006105 | 0 | 1.2839 | 0.0006105 | 23.9363 | 260638.0001 | 50218.7324
39049.4073 | 2225 | 1 | 39049.4074 | 1 | 0 |  | 1730 | 1969 | 135.8364 | 0.06105 | 0.06105 | 0 | 1.3584 | 0.0006105 | 0.0006105 | 0 | 1.3578 | 0.0006105 | 17.1933 | 260638.0001 | 38123.3731
39049.4078 | 2080 | 1 | 39049.4079 | 1 | 0 |  | 1772 | 2011 | 126.9841 | 0.06105 | 0.06105 | 0 | 1.2698 | 0.0006105 | 0.0006105 | 0 | 1.2692 | 0.0006105 | 25.367 | 260638.0001 | 52617.8119
39049.4083 | 2103 | 1 | 39049.4083 | 1 | 0 |  | 1814 | 2053 | 128.3883 | 0.06105 | 0.06105 | 0 | 1.2839 | 0.0006105 | 0.0006105 | 0 | 1.2833 | 0.0006105 | 23.9952 | 260638.0001 | 50318.694
39049.4088 | 2591 | 1 | 39049.4088 | 1 | 0 |  | 1856 | 2095 | 158.1807 | 0.06105 | 0.06105 | 0 | 1.5818 | 0.0006105 | 0.0006105 | 0 | 1.5812 | 0.0006105 | 0.63243 | 260638.0001 | 1537.4101
39049.4093 | 2069 | 1 | 39049.4093 | 1 | 0 |  | 1898 | 2137 | 126.3126 | 0.06105 | 0.06105 | 0 | 1.2631 | 0.0006105 | 0.0006105 | 0 | 1.2625 | 0.0006105 | 26.0339 | 260638.0001 | 53717.39
39049.4098 | 2298 | 1 | 39049.4098 | 1 | 0 |  | 1940 | 2179 | 140.293 | 0.06105 | 0.06105 | 0 | 1.4029 | 0.0006105 | 0.0006105 | 0 | 1.4023 | 0.0006105 | 13.4689 | 260638.0001 | 30826.1728
39049.4103 | 2484 | 1 | 39049.4103 | 1 | 0 |  | 1982 | 2221 | 151.6484 | 0.06105 | 0.06105 | 0 | 1.5165 | 0.0006105 | 0.0006105 | 0 | 1.5159 | 0.0006105 | 4.969 | 260638.0004 | 12233.3064
39049.4108 | 2003 | 1 | 39049.4108 | 1 | 0 |  | 2024 | 2263 | 122.2833 | 0.06105 | 0.06105 | 0 | 1.2228 | 0.0006105 | 0.0006105 | 0 | 1.2222 | 0.0006105 | 30.1888 | 260637.9999 | 60314.8588
39049.4112 | 2527 | 1 | 39049.4113 | 1 | 0 |  | 2066 | 2305 | 154.2735 | 0.06105 | 0.06105 | 0 | 1.5427 | 0.0006105 | 0.0006105 | 0 | 1.5421 | 0.0006105 | 3.1821 | 260638.0001 | 7934.9556
39049.4117 | 2460 | 1 | 39049.4117 | 1 | 0 |  | 2108 | 2347 | 150.1832 | 0.06105 | 0.06105 | 0 | 1.5018 | 0.0006105 | 0.0006105 | 0 | 1.5012 | 0.0006105 | 5.9935 | 260638.0001 | 14632.3859
39049.4122 | 2582 | 1 | 39049.4122 | 38 | 0 |  | 2150 | 2389 | 157.6313 | 0.06105 | 2.3199 | 0 | 1.5763 | 0.0006105 | 0.023199 | 0 | 1.5757 | 0.023199 | 0.98335 | 6761.5263 | 2402.4685
39049.4127 | 2416 | 1 | 39049.4127 | 121 | 0 |  | 2192 | 2431 | 147.4969 | 0.06105 | 7.3871 | 0 | 1.475 | 0.0006105 | 0.073871 | 0 | 1.4744 | 0.073871 | 7.9248 | 2054.8595 | 18154.5085
39049.4132 | 2122 | 1 | 39049.4132 | 166 | 0 |  | 2234 | 2473 | 129.5482 | 0.06105 | 10.1343 | 0 | 1.2955 | 0.0006105 | 0.10134 | 0 | 1.2949 | 0.10134 | 22.8852 | 1470.7108 | 45354.1733
39049.4137 | 2574 | 1 | 39049.4137 | 125 | 0 |  | 2276 | 2515 | 157.1429 | 0.06105 | 7.6313 | 0 | 1.5714 | 0.0006105 | 0.076313 | 0 | 1.5708 | 0.076313 | 1.2973 | 1985.904 | 3082.7675
39049.4142 | 2579 | 1 | 39049.4142 | 112 | 0 |  | 2317.5 | 2556.5 | 157.4481 | 0.06105 | 6.8376 | 0 | 1.5745 | 0.0006105 | 0.068376 | 0 | 1.5739 | 0.068376 | 1.1009 | 2228.0179 | 2620.3892
39049.4146 | 2321 | 1 | 39049.4147 | 99 | 0 |  | 2360 | 2599 | 141.6972 | 0.06105 | 6.044 | 0 | 1.417 | 0.0006105 | 0.06044 | 0 | 1.4164 | 0.06044 | 12.3442 | 2533.7172 | 27454.4364
39049.4151 | 2572 | 1 | 39049.4151 | 78 | 0 |  | 2401.5 | 2640.5 | 157.0208 | 0.06105 | 4.7619 | 0 | 1.5702 | 0.0006105 | 0.047619 | 0 | 1.5696 | 0.047619 | 1.3761 | 3242.7949 | 3335.1519
39049.4156 | 2486 | 1 | 39049.4156 | 76 | 0 |  | 2443.5 | 2682.5 | 151.7705 | 0.06105 | 4.6398 | 0 | 1.5177 | 0.0006105 | 0.046398 | 0 | 1.5171 | 0.046398 | 4.8846 | 3330.7632 | 11687.116
39049.4161 | 2571 | 1 | 39049.4161 | 72 | 0 |  | 2486 | 2725 | 156.9597 | 0.06105 | 4.3956 | 0 | 1.5696 | 0.0006105 | 0.043956 | 0 | 1.569 | 0.043956 | 1.4156 | 3521.3611 | 3440.3019
39049.4166 | 2362 | 1 | 39049.4166 | 38 | 0 |  | 2528 | 2767 | 144.2002 | 0.06105 | 2.3199 | 0 | 1.442 | 0.0006105 | 0.023199 | 0 | 1.4414 | 0.023199 | 10.3931 | 6761.5263 | 24081.8402
39049.4171 | 2421 | 1 | 39049.4171 | 35 | 0 |  | 2569.5 | 2808.5 | 147.8022 | 0.06105 | 2.1368 | 0 | 1.478 | 0.0006105 | 0.021368 | 0 | 1.4774 | 0.021368 | 7.7017 | 7349.6571 | 18289.1563
39049.4176 | 2535 | 1 | 39049.4176 | 42 | 0 |  | 2611.5 | 2850.5 | 154.7619 | 0.06105 | 2.5641 | 0 | 1.5476 | 0.0006105 | 0.025641 | 0 | 1.547 | 0.025641 | 2.8564 | 6108.0476 | 7023.0202
39049.418 | 2064 | 1 | 39049.4181 | 43 | 0 |  | 2654 | 2893 | 126.0073 | 0.06105 | 2.6252 | 0 | 1.2601 | 0.0006105 | 0.026252 | 0 | 1.2595 | 0.026252 | 26.3395 | 5963.6744 | 53343.5259
39049.4185 | 2293 | 1 | 39049.4185 | 23 | 0 |  | 2695.5 | 2934.5 | 139.9878 | 0.06105 | 1.4042 | 0 | 1.3999 | 0.0006105 | 0.014042 | 0 | 1.3993 | 0.014042 | 13.7165 | 11236.4348 | 31061.5639
39049.419 | 1982 | 1 | 39049.419 | 19 | 0 |  | 2738 | 2977 | 121.0012 | 0.06105 | 1.16 | 0 | 1.21 | 0.0006105 | 0.0116 | 0 | 1.2094 | 0.0116 | 31.569 | 13623.0526 | 61983.0138
39049.4195 | 2409 | 1 | 39049.4195 | 17 | 0 |  | 2779.5 | 3018.5 | 147.0696 | 0.06105 | 1.0379 | 0 | 1.4707 | 0.0006105 | 0.010379 | 0 | 1.4701 | 0.010379 | 8.2384 | 15237.5294 | 19609.3091
39049.42 | 2345 | 1 | 39049.42 | 12 | 0 |  | 2821.5 | 3060.5 | 143.1624 | 0.06105 | 0.7326 | 0 | 1.4316 | 0.0006105 | 0.007326 | 0 | 1.431 | 0.007326 | 11.1937 | 21628.1667 | 26017.7045
39049.4205 | 2172 | 1 | 39049.4205 | 3 | 0 |  | 2863.5 | 3102.5 | 132.6007 | 0.06105 | 0.18315 | 0 | 1.326 | 0.0006105 | 0.0018315 | 0 | 1.3254 | 0.0018315 | 20.0544 | 86812.6667 | 43388.0211
39049.421 | 2126 | 1 | 39049.421 | 2 | 0 |  | 2906 | 3145 | 129.7924 | 0.06105 | 0.1221 | 0 | 1.2979 | 0.0006105 | 0.001221 | 0 | 1.2973 | 0.001221 | 22.6532 | 130269.0001 | 48001.1523
39049.4214 | 2023 | 1 | 39049.4215 | 2 | 0 |  | 2947.5 | 3186.5 | 123.5043 | 0.06105 | 0.1221 | 0 | 1.235 | 0.0006105 | 0.001221 | 0 | 1.2344 | 0.001221 | 28.9011 | 130269 | 58293.2516
39049.4219 | 2516 | 1 | 39049.4219 | 2 | 0 |  | 2989.5 | 3228.5 | 153.602 | 0.06105 | 0.1221 | 0 | 1.536 | 0.0006105 | 0.001221 | 0 | 1.5354 | 0.001221 | 3.6334 | 130269 | 9031.0674

## B4-C5
Open Burn Test 13 |  |  | 2006-11-28 | 9:21 |  |  | Vs = |  | 159.1807 |  | R = | 100
Mixed | 7-C | Tray F | IRMS | 1
0 | 150 kW |  | Bundle | Ch. 4 & 5 | Cable B | Even - | Cable C |  | Odd
Time-25 | N11 | N12 | Time-26 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R5-G | R4-5
39049.385 | 1 | 0 | 39049.385 | 1 | 0 |  | -204.5 | 34.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260638 | 260638 | 260637.9994
39049.3855 | 1 | 0 | 39049.3855 | 1 | 0 |  | -162.5 | 76.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260638 | 260638 | 260637.9994
39049.3859 | 1 | 0 | 39049.3859 | 1 | 0 |  | -120.5 | 118.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260638 | 260638 | 260637.9994
39049.3864 | 1 | 0 | 39049.3864 | 1 | 0 |  | -78.5 | 160.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260638 | 260638 | 260637.9994
39049.3869 | 1 | 0 | 39049.3869 | 1 | 0 |  | -36.5 | 202.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260638 | 260638 | 260637.9994
39049.3874 | 1 | 0 | 39049.3874 | 1 | 0 |  | 5.5 | 244.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260638 | 260638 | 260637.9994
39049.3879 | 1 | 0 | 39049.3879 | 1 | 0 |  | 47.5 | 286.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260638 | 260638 | 260637.9994
39049.3884 | 1 | 0 | 39049.3884 | 1 | 0 |  | 89.5 | 328.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260638 | 260638 | 260637.9994
39049.3889 | 1 | 0 | 39049.3889 | 1 | 0 |  | 131.5 | 370.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260638 | 260638 | 260637.9994
39049.3893 | 1 | 0 | 39049.3894 | 1 | 0 |  | 173.5 | 412.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260638 | 260638 | 260637.9994
39049.3898 | 1 | 0 | 39049.3898 | 1 | 0 |  | 215.5 | 454.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260638 | 260638 | 260637.9994
39049.3903 | 1 | 0 | 39049.3903 | 1 | 0 |  | 257.5 | 496.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260638 | 260638 | 260637.9994
39049.3908 | 1 | 0 | 39049.3908 | 1 | 0 |  | 299.5 | 538.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260638 | 260638 | 260637.9994
39049.3913 | 1 | 0 | 39049.3913 | 1 | 0 |  | 341.5 | 580.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260638 | 260638 | 260637.9994
39049.3918 | 1 | 0 | 39049.3918 | 1 | 0 |  | 383.5 | 622.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260638 | 260638 | 260637.9994
39049.3923 | 1 | 0 | 39049.3923 | 1 | 0 |  | 425.5 | 664.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260638 | 260638 | 260637.9994
39049.3927 | 1 | 0 | 39049.3928 | 1 | 0 |  | 467.5 | 706.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260638 | 260638 | 260637.9994
39049.3932 | 1 | 0 | 39049.3932 | 1 | 0 |  | 509.5 | 748.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260638 | 260638 | 260637.9994
39049.3937 | 1 | 0 | 39049.3937 | 1 | 0 |  | 551.5 | 790.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260638 | 260638 | 260637.9994
39049.3942 | 1 | 0 | 39049.3942 | 1 | 0 |  | 593.5 | 832.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260638 | 260638 | 260637.9994
39049.3947 | 1 | 0 | 39049.3947 | 1 | 0 |  | 635.5 | 874.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260638 | 260638 | 260637.9994
39049.3952 | 1 | 0 | 39049.3952 | 1 | 0 |  | 677.5 | 916.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260638 | 260638 | 260637.9994
39049.3957 | 1 | 0 | 39049.3957 | 1 | 0 |  | 719.5 | 958.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260638 | 260638 | 260637.9994
39049.3961 | 1 | 0 | 39049.3962 | 1 | 0 |  | 761.5 | 1000.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260638 | 260638 | 260637.9994
39049.3966 | 1 | 0 | 39049.3966 | 1 | 0 |  | 803.5 | 1042.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260638 | 260638 | 260637.9994
39049.3971 | 1 | 0 | 39049.3971 | 1 | 0 |  | 845.5 | 1084.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260638 | 260638 | 260637.9994
39049.3976 | 1 | 0 | 39049.3976 | 1 | 0 |  | 887.5 | 1126.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260638 | 260638 | 260637.9994
39049.3981 | 1 | 0 | 39049.3981 | 1 | 0 |  | 929.5 | 1168.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260638 | 260638 | 260637.9994
39049.3986 | 993 | 1 | 39049.3986 | 1 | 0 |  | 971.5 | 1210.5 | 60.6227 | 0.06105 | 0.06105 | 0 | 0.60623 | 0.0006105 | 0.0006105 | 0 | 0.60562 | 0.0006105 | 162.74 | 260637.9999 | 161276.1226
39049.3991 | 2467 | 1 | 39049.3991 | 1 | 0 |  | 1013 | 1252 | 150.6105 | 0.06105 | 0.06105 | 0 | 1.5061 | 0.0006105 | 0.0006105 | 0 | 1.5055 | 0.0006105 | 5.6926 | 260637.9999 | 13932.6544
39049.3995 | 2370 | 1 | 39049.3996 | 1 | 0 |  | 1055.5 | 1294.5 | 144.6886 | 0.06105 | 0.06105 | 0 | 1.4469 | 0.0006105 | 0.0006105 | 0 | 1.4463 | 0.0006105 | 10.0203 | 260638.0001 | 23628.9342
39049.4 | 1940 | 1 | 39049.4 | 1 | 0 |  | 1097 | 1336 | 118.4371 | 0.06105 | 0.06105 | 0 | 1.1844 | 0.0006105 | 0.0006105 | 0 | 1.1838 | 0.0006105 | 34.4188 | 260638.0004 | 66612.4425
39049.4005 | 2054 | 1 | 39049.4005 | 1 | 0 |  | 1139.5 | 1378.5 | 125.3968 | 0.06105 | 0.06105 | 0 | 1.254 | 0.0006105 | 0.0006105 | 0 | 1.2534 | 0.0006105 | 26.9547 | 260638.0001 | 55216.8147
39049.401 | 2312 | 1 | 39049.401 | 1 | 0 |  | 1181.5 | 1420.5 | 141.1477 | 0.06105 | 0.06105 | 0 | 1.4115 | 0.0006105 | 0.0006105 | 0 | 1.4109 | 0.0006105 | 12.7815 | 260638.0001 | 29426.7097
39049.4015 | 1879 | 1 | 39049.4015 | 1 | 0 |  | 1223.5 | 1462.5 | 114.7131 | 0.06105 | 0.06105 | 0 | 1.1471 | 0.0006105 | 0.0006105 | 0 | 1.1465 | 0.0006105 | 38.7849 | 260637.9999 | 72710.103
39049.402 | 2411 | 1 | 39049.402 | 1 | 0 |  | 1265.5 | 1504.5 | 147.1917 | 0.06105 | 0.06105 | 0 | 1.4719 | 0.0006105 | 0.0006105 | 0 | 1.4713 | 0.0006105 | 8.1485 | 260637.9999 | 19530.5067
39049.4025 | 1510 | 1 | 39049.4025 | 1 | 0 |  | 1307.5 | 1546.5 | 92.1856 | 0.06105 | 0.06105 | 0 | 0.92186 | 0.0006105 | 0.0006105 | 0 | 0.92125 | 0.0006105 | 72.7224 | 260638.0001 | 109595.9509
39049.403 | 2121 | 1 | 39049.403 | 1 | 0 |  | 1349.5 | 1588.5 | 129.4872 | 0.06105 | 0.06105 | 0 | 1.2949 | 0.0006105 | 0.0006105 | 0 | 1.2943 | 0.0006105 | 22.9425 | 260638.0001 | 48519.3844
39049.4034 | 2309 | 1 | 39049.4034 | 1 | 0 |  | 1391 | 1630 | 140.9646 | 0.06105 | 0.06105 | 0 | 1.4096 | 0.0006105 | 0.0006105 | 0 | 1.409 | 0.0006105 | 12.9281 | 260637.9999 | 29726.5947
39049.4039 | 2415 | 1 | 39049.4039 | 1 | 0 |  | 1433 | 1672 | 147.4359 | 0.06105 | 0.06105 | 0 | 1.4744 | 0.0006105 | 0.0006105 | 0 | 1.4737 | 0.0006105 | 7.9693 | 260638.0001 | 19130.6601
39049.4044 | 2081 | 1 | 39049.4044 | 1 | 0 |  | 1475 | 1714 | 127.0452 | 0.06105 | 0.06105 | 0 | 1.2705 | 0.0006105 | 0.0006105 | 0 | 1.2698 | 0.0006105 | 25.3067 | 260638.0001 | 52517.8503
39049.4049 | 1944 | 1 | 39049.4049 | 2 | 0 |  | 1517 | 1756 | 118.6813 | 0.06105 | 0.1221 | 0 | 1.1868 | 0.0006105 | 0.001221 | 0 | 1.1862 | 0.001221 | 34.1421 | 130269 | 66187.1919
39049.4054 | 2114 | 1 | 39049.4054 | 1 | 0 |  | 1559 | 1798 | 129.0598 | 0.06105 | 0.06105 | 0 | 1.2906 | 0.0006105 | 0.0006105 | 0 | 1.29 | 0.0006105 | 23.3497 | 260638.0004 | 49219.1159
39049.4059 | 2392 | 1 | 39049.4059 | 1 | 0 |  | 1601 | 1840 | 146.0317 | 0.06105 | 0.06105 | 0 | 1.4603 | 0.0006105 | 0.0006105 | 0 | 1.4597 | 0.0006105 | 9.0079 | 260638.0001 | 21429.778
39049.4063 | 2103 | 1 | 39049.4064 | 1 | 0 |  | 1643 | 1882 | 128.3883 | 0.06105 | 0.06105 | 0 | 1.2839 | 0.0006105 | 0.0006105 | 0 | 1.2833 | 0.0006105 | 23.9952 | 260638.0001 | 50318.694
39049.4068 | 1988 | 1 | 39049.4069 | 1 | 0 |  | 1685 | 1924 | 121.3675 | 0.06105 | 0.06105 | 0 | 1.2137 | 0.0006105 | 0.0006105 | 0 | 1.2131 | 0.0006105 | 31.1716 | 260638.0004 | 61814.2835
39049.4073 | 2115 | 1 | 39049.4073 | 1 | 0 |  | 1727 | 1966 | 129.1209 | 0.06105 | 0.06105 | 0 | 1.2912 | 0.0006105 | 0.0006105 | 0 | 1.2906 | 0.0006105 | 23.2914 | 260638.0001 | 49119.1543
39049.4078 | 2575 | 1 | 39049.4078 | 1 | 0 |  | 1769 | 2008 | 157.2039 | 0.06105 | 0.06105 | 0 | 1.572 | 0.0006105 | 0.0006105 | 0 | 1.5714 | 0.0006105 | 1.258 | 260638.0001 | 3136.7965
39049.4083 | 2132 | 1 | 39049.4083 | 1 | 0 |  | 1811 | 2050 | 130.1587 | 0.06105 | 0.06105 | 0 | 1.3016 | 0.0006105 | 0.0006105 | 0 | 1.301 | 0.0006105 | 22.3078 | 260637.9999 | 47419.8063
39049.4088 | 2591 | 1 | 39049.4088 | 1 | 0 |  | 1853 | 2092 | 158.1807 | 0.06105 | 0.06105 | 0 | 1.5818 | 0.0006105 | 0.0006105 | 0 | 1.5812 | 0.0006105 | 0.63243 | 260638.0001 | 1537.4101
39049.4093 | 2432 | 1 | 39049.4093 | 2 | 0 |  | 1895 | 2134 | 148.4737 | 0.06105 | 0.1221 | 0 | 1.4847 | 0.0006105 | 0.001221 | 0 | 1.4841 | 0.001221 | 7.2143 | 130269 | 17424.6241
39049.4097 | 2566 | 1 | 39049.4098 | 1 | 0 |  | 1937 | 2176 | 156.6545 | 0.06105 | 0.06105 | 0 | 1.5665 | 0.0006105 | 0.0006105 | 0 | 1.5659 | 0.0006105 | 1.6133 | 260638.0001 | 4036.4513
39049.4102 | 2036 | 1 | 39049.4103 | 1 | 0 |  | 1979 | 2218 | 124.2979 | 0.06105 | 0.06105 | 0 | 1.243 | 0.0006105 | 0.0006105 | 0 | 1.2424 | 0.0006105 | 28.0776 | 260638.0001 | 57016.1244
39049.4107 | 2449 | 1 | 39049.4107 | 2 | 0 |  | 2021 | 2260 | 149.5116 | 0.06105 | 0.1221 | 0 | 1.4951 | 0.0006105 | 0.001221 | 0 | 1.4945 | 0.001221 | 6.4698 | 130268.9999 | 15725.9281
39049.4112 | 2258 | 1 | 39049.4112 | 1 | 0 |  | 2063 | 2302 | 137.851 | 0.06105 | 0.06105 | 0 | 1.3785 | 0.0006105 | 0.0006105 | 0 | 1.3779 | 0.0006105 | 15.4798 | 260638.0001 | 34824.6387
39049.4117 | 2484 | 1 | 39049.4117 | 1 | 0 |  | 2105 | 2344 | 151.6484 | 0.06105 | 0.06105 | 0 | 1.5165 | 0.0006105 | 0.0006105 | 0 | 1.5159 | 0.0006105 | 4.969 | 260638.0004 | 12233.3064
39049.4122 | 2528 | 1 | 39049.4122 | 2 | 0 |  | 2147 | 2386 | 154.3346 | 0.06105 | 0.1221 | 0 | 1.5433 | 0.0006105 | 0.001221 | 0 | 1.5427 | 0.001221 | 3.1413 | 130269 | 7831.9878
39049.4127 | 2206 | 1 | 39049.4127 | 11 | 0 |  | 2189 | 2428 | 134.6764 | 0.06105 | 0.67155 | 0 | 1.3468 | 0.0006105 | 0.0067155 | 0 | 1.3462 | 0.0067155 | 18.2032 | 23603.4545 | 39869.0879
39049.4131 | 2004 | 1 | 39049.4132 | 25 | 0 |  | 2231 | 2470 | 122.3443 | 0.06105 | 1.5263 | 0 | 1.2234 | 0.0006105 | 0.015263 | 0 | 1.2228 | 0.015263 | 30.124 | 10329.52 | 59660.4279
39049.4136 | 2113 | 1 | 39049.4137 | 26 | 0 |  | 2273 | 2512 | 128.9988 | 0.06105 | 1.5873 | 0 | 1.29 | 0.0006105 | 0.015873 | 0 | 1.2894 | 0.015873 | 23.4083 | 9928.3846 | 48846.0165
39049.4141 | 2475 | 1 | 39049.4141 | 43 | 0 |  | 2315 | 2554 | 151.0989 | 0.06105 | 2.6252 | 0 | 1.511 | 0.0006105 | 0.026252 | 0 | 1.5104 | 0.026252 | 5.3509 | 5963.6744 | 12921.3327
39049.4146 | 2570 | 1 | 39049.4146 | 26 | 0 |  | 2357 | 2596 | 156.8987 | 0.06105 | 1.5873 | 0 | 1.569 | 0.0006105 | 0.015873 | 0 | 1.5684 | 0.015873 | 1.455 | 9928.3846 | 3601.723
39049.4151 | 2575 | 1 | 39049.4151 | 21 | 0 |  | 2399 | 2638 | 157.2039 | 0.06105 | 1.2821 | 0 | 1.572 | 0.0006105 | 0.012821 | 0 | 1.5714 | 0.012821 | 1.258 | 12316.0952 | 3112.7264
39049.4156 | 2573 | 1 | 39049.4156 | 18 | 0 |  | 2441 | 2680 | 157.0818 | 0.06105 | 1.0989 | 0 | 1.5708 | 0.0006105 | 0.010989 | 0 | 1.5702 | 0.010989 | 1.3367 | 14385.4444 | 3314.9562
39049.4161 | 2100 | 1 | 39049.4161 | 29 | 0 |  | 2483 | 2722 | 128.2051 | 0.06105 | 1.7705 | 0 | 1.2821 | 0.0006105 | 0.017705 | 0 | 1.2814 | 0.017705 | 24.1726 | 8890.9655 | 50074.7902
39049.4166 | 2050 | 1 | 39049.4166 | 12 | 0 |  | 2525 | 2764 | 125.1526 | 0.06105 | 0.7326 | 0 | 1.2515 | 0.0006105 | 0.007326 | 0 | 1.2509 | 0.007326 | 27.2026 | 21628.1667 | 55381.9361
39049.417 | 2380 | 1 | 39049.4171 | 15 | 0 |  | 2567 | 2806 | 145.2991 | 0.06105 | 0.91575 | 0 | 1.453 | 0.0006105 | 0.0091575 | 0 | 1.4524 | 0.0091575 | 9.5578 | 17282.5333 | 22507.7658
39049.4175 | 2575 | 1 | 39049.4175 | 26 | 0 |  | 2609 | 2848 | 157.2039 | 0.06105 | 1.5873 | 0 | 1.572 | 0.0006105 | 0.015873 | 0 | 1.5714 | 0.015873 | 1.258 | 9928.3846 | 3106.7088
39049.418 | 2225 | 1 | 39049.418 | 26 | 0 |  | 2651 | 2890 | 135.8364 | 0.06105 | 1.5873 | 0 | 1.3584 | 0.0006105 | 0.015873 | 0 | 1.3578 | 0.015873 | 17.1934 | 9928.3846 | 37757.6995
39049.4185 | 2318 | 1 | 39049.4185 | 20 | 0 |  | 2693 | 2932 | 141.514 | 0.06105 | 1.221 | 0 | 1.4151 | 0.0006105 | 0.01221 | 0 | 1.4145 | 0.01221 | 12.4895 | 12936.9 | 28616.7971
39049.419 | 2408 | 1 | 39049.419 | 19 | 0 |  | 2735 | 2974 | 147.0085 | 0.06105 | 1.16 | 0 | 1.4701 | 0.0006105 | 0.0116 | 0 | 1.4695 | 0.0116 | 8.2834 | 13623.0526 | 19693.4403
39049.4195 | 2180 | 1 | 39049.4195 | 13 | 0 |  | 2777 | 3016 | 133.0891 | 0.06105 | 0.79365 | 0 | 1.3309 | 0.0006105 | 0.0079365 | 0 | 1.3303 | 0.0079365 | 19.6136 | 19956.7692 | 42425.4134
39049.42 | 2217 | 1 | 39049.42 | 12 | 0 |  | 2819 | 3058 | 135.348 | 0.06105 | 0.7326 | 0 | 1.3535 | 0.0006105 | 0.007326 | 0 | 1.3529 | 0.007326 | 17.6165 | 21628.1667 | 38758.7948
39049.4204 | 2520 | 1 | 39049.4205 | 9 | 0 |  | 2861 | 3100 | 153.8462 | 0.06105 | 0.54945 | 0 | 1.5385 | 0.0006105 | 0.0054945 | 0 | 1.5379 | 0.0054945 | 3.4688 | 28870.8889 | 8608.1839
39049.4209 | 2100 | 1 | 39049.4209 | 8 | 0 |  | 2903 | 3142 | 128.2051 | 0.06105 | 0.4884 | 0 | 1.2821 | 0.0006105 | 0.004884 | 0 | 1.2814 | 0.004884 | 24.1725 | 32492.25 | 50482.6318
39049.4214 | 2047 | 1 | 39049.4214 | 6 | 0 |  | 2945 | 3184 | 124.9695 | 0.06105 | 0.3663 | 0 | 1.2497 | 0.0006105 | 0.003663 | 0 | 1.2491 | 0.003663 | 27.3891 | 43356.3333 | 55809.2777
39049.4219 | 2341 | 1 | 39049.4219 | 3 | 0 |  | 2987 | 3226 | 142.9182 | 0.06105 | 0.18315 | 0 | 1.4292 | 0.0006105 | 0.0018315 | 0 | 1.4286 | 0.0018315 | 11.3838 | 86812.6667 | 26507.4659

## B3-C6
Open Burn Test 13 |  |  | 2006-11-28 | 9:21 |  |  | Vs = |  | 159.1197 |  | R = | 100
Mixed | 7-C | Tray F | IRMS | 1
0 | 150 kW |  | Bundle | Ch. 3 & 6 | Cable B | Odd - | Cable C |  | Even
Time-23 | N11 | N12 | Time-24 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R6-G | R3-6
39049.3849 | 1 | 0 | 39049.3849 | 1 | 0 |  | -207.5 | 31.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260538 | 260538 | 260537.9994
39049.3854 | 1 | 0 | 39049.3854 | 1 | 0 |  | -165.5 | 73.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260538 | 260538 | 260537.9994
39049.3859 | 1 | 0 | 39049.3859 | 1 | 0 |  | -123.5 | 115.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260538 | 260538 | 260537.9994
39049.3864 | 1 | 0 | 39049.3864 | 1 | 0 |  | -81.5 | 157.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260538 | 260538 | 260537.9994
39049.3869 | 1 | 0 | 39049.3869 | 1 | 0 |  | -39.5 | 199.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260538 | 260538 | 260537.9994
39049.3874 | 1 | 0 | 39049.3874 | 1 | 0 |  | 2.5 | 241.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260538 | 260538 | 260537.9994
39049.3878 | 1 | 0 | 39049.3879 | 1 | 0 |  | 44.5 | 283.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260538 | 260538 | 260537.9994
39049.3883 | 1 | 0 | 39049.3883 | 1 | 0 |  | 86.5 | 325.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260538 | 260538 | 260537.9994
39049.3888 | 1 | 0 | 39049.3888 | 1 | 0 |  | 128.5 | 367.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260538 | 260538 | 260537.9994
39049.3893 | 1 | 0 | 39049.3893 | 1 | 0 |  | 170.5 | 409.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260538 | 260538 | 260537.9994
39049.3898 | 1 | 0 | 39049.3898 | 1 | 0 |  | 212.5 | 451.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260538 | 260538 | 260537.9994
39049.3903 | 1 | 0 | 39049.3903 | 1 | 0 |  | 254.5 | 493.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260538 | 260538 | 260537.9994
39049.3908 | 1 | 0 | 39049.3908 | 1 | 0 |  | 296.5 | 535.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260538 | 260538 | 260537.9994
39049.3913 | 1 | 0 | 39049.3913 | 1 | 0 |  | 338.5 | 577.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260538 | 260538 | 260537.9994
39049.3917 | 1 | 0 | 39049.3917 | 1 | 0 |  | 380.5 | 619.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260538 | 260538 | 260537.9994
39049.3922 | 1 | 0 | 39049.3922 | 1 | 0 |  | 422.5 | 661.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260538 | 260538 | 260537.9994
39049.3927 | 1 | 0 | 39049.3927 | 1 | 0 |  | 464.5 | 703.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260538 | 260538 | 260537.9994
39049.3932 | 1 | 0 | 39049.3932 | 1 | 0 |  | 506.5 | 745.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260538 | 260538 | 260537.9994
39049.3937 | 1 | 0 | 39049.3937 | 1 | 0 |  | 548.5 | 787.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260538 | 260538 | 260537.9994
39049.3942 | 1 | 0 | 39049.3942 | 1 | 0 |  | 590.5 | 829.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260538 | 260538 | 260537.9994
39049.3947 | 1 | 0 | 39049.3947 | 1 | 0 |  | 632.5 | 871.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260538 | 260538 | 260537.9994
39049.3951 | 1 | 0 | 39049.3952 | 1 | 0 |  | 674.5 | 913.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260538 | 260538 | 260537.9994
39049.3956 | 1 | 0 | 39049.3956 | 1 | 0 |  | 716.5 | 955.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260538 | 260538 | 260537.9994
39049.3961 | 1 | 0 | 39049.3961 | 1 | 0 |  | 758.5 | 997.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260538 | 260538 | 260537.9994
39049.3966 | 1 | 0 | 39049.3966 | 1 | 0 |  | 800.5 | 1039.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260538 | 260538 | 260537.9994
39049.3971 | 1 | 0 | 39049.3971 | 1 | 0 |  | 842.5 | 1081.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260538 | 260538 | 260537.9994
39049.3976 | 1 | 0 | 39049.3976 | 1 | 0 |  | 884.5 | 1123.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260538 | 260538 | 260537.9994
39049.3981 | 1 | 0 | 39049.3981 | 1 | 0 |  | 926.5 | 1165.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260538 | 260538 | 260537.9994
39049.3985 | 1824 | 1 | 39049.3986 | 1 | 0 |  | 968.5 | 1207.5 | 111.3553 | 0.06105 | 0.06105 | 0 | 1.1136 | 0.0006105 | 0.0006105 | 0 | 1.1129 | 0.0006105 | 42.9172 | 260537.9999 | 78108.0205
39049.399 | 2104 | 1 | 39049.399 | 1 | 0 |  | 1010.5 | 1249.5 | 128.4493 | 0.06105 | 0.06105 | 0 | 1.2845 | 0.0006105 | 0.0006105 | 0 | 1.2839 | 0.0006105 | 23.8887 | 260538.0001 | 50118.7634
39049.3995 | 1974 | 1 | 39049.3995 | 1 | 0 |  | 1052.5 | 1291.5 | 120.5128 | 0.06105 | 0.06105 | 0 | 1.2051 | 0.0006105 | 0.0006105 | 0 | 1.2045 | 0.0006105 | 32.0517 | 260538.0001 | 63113.7756
39049.4 | 2182 | 1 | 39049.4 | 1 | 0 |  | 1094.5 | 1333.5 | 133.2112 | 0.06105 | 0.06105 | 0 | 1.3321 | 0.0006105 | 0.0006105 | 0 | 1.3315 | 0.0006105 | 19.4581 | 260537.9999 | 42321.756
39049.4005 | 2129 | 1 | 39049.4005 | 1 | 0 |  | 1136.5 | 1375.5 | 129.9756 | 0.06105 | 0.06105 | 0 | 1.2998 | 0.0006105 | 0.0006105 | 0 | 1.2991 | 0.0006105 | 22.4333 | 260537.9999 | 47619.7225
39049.401 | 1999 | 1 | 39049.401 | 1 | 0 |  | 1178.5 | 1417.5 | 122.0391 | 0.06105 | 0.06105 | 0 | 1.2204 | 0.0006105 | 0.0006105 | 0 | 1.2198 | 0.0006105 | 30.3994 | 260538.0001 | 60614.7348
39049.4015 | 1897 | 1 | 39049.4015 | 1 | 0 |  | 1220.5 | 1459.5 | 115.812 | 0.06105 | 0.06105 | 0 | 1.1581 | 0.0006105 | 0.0006105 | 0 | 1.1575 | 0.0006105 | 37.4146 | 260538.0001 | 70810.8213
39049.4019 | 2091 | 1 | 39049.402 | 1 | 0 |  | 1262.5 | 1501.5 | 127.6557 | 0.06105 | 0.06105 | 0 | 1.2766 | 0.0006105 | 0.0006105 | 0 | 1.2759 | 0.0006105 | 24.6593 | 260538.0001 | 51418.2646
39049.4024 | 1730 | 1 | 39049.4024 | 1 | 0 |  | 1304.5 | 1543.5 | 105.6166 | 0.06105 | 0.06105 | 0 | 1.0562 | 0.0006105 | 0.0006105 | 0 | 1.0556 | 0.0006105 | 50.6871 | 260538.0001 | 87504.414
39049.4029 | 1893 | 1 | 39049.4029 | 1 | 0 |  | 1346.5 | 1585.5 | 115.5678 | 0.06105 | 0.06105 | 0 | 1.1557 | 0.0006105 | 0.0006105 | 0 | 1.1551 | 0.0006105 | 37.7051 | 260538.0001 | 71210.6678
39049.4034 | 1930 | 1 | 39049.4034 | 1 | 0 |  | 1388.5 | 1627.5 | 117.8266 | 0.06105 | 0.06105 | 0 | 1.1783 | 0.0006105 | 0.0006105 | 0 | 1.1777 | 0.0006105 | 35.0638 | 260537.9999 | 67512.0874
39049.4039 | 2193 | 1 | 39049.4039 | 1 | 0 |  | 1430.5 | 1669.5 | 133.8828 | 0.06105 | 0.06105 | 0 | 1.3388 | 0.0006105 | 0.0006105 | 0 | 1.3382 | 0.0006105 | 18.8586 | 260538.0001 | 41222.1781
39049.4044 | 2474 | 1 | 39049.4044 | 1 | 0 |  | 1472.5 | 1711.5 | 151.0379 | 0.06105 | 0.06105 | 0 | 1.5104 | 0.0006105 | 0.0006105 | 0 | 1.5098 | 0.0006105 | 5.353 | 260537.9999 | 13132.9593
39049.4049 | 2018 | 1 | 39049.4049 | 1 | 0 |  | 1514.5 | 1753.5 | 123.199 | 0.06105 | 0.06105 | 0 | 1.232 | 0.0006105 | 0.0006105 | 0 | 1.2314 | 0.0006105 | 29.1711 | 260537.9999 | 58715.4638
39049.4053 | 2058 | 1 | 39049.4054 | 1 | 0 |  | 1556.5 | 1795.5 | 125.641 | 0.06105 | 0.06105 | 0 | 1.2564 | 0.0006105 | 0.0006105 | 0 | 1.2558 | 0.0006105 | 26.6592 | 260537.9999 | 54716.9985
39049.4058 | 2322 | 1 | 39049.4058 | 1 | 0 |  | 1598.5 | 1837.5 | 141.7582 | 0.06105 | 0.06105 | 0 | 1.4176 | 0.0006105 | 0.0006105 | 0 | 1.417 | 0.0006105 | 12.2525 | 260538.0001 | 28327.1274
39049.4063 | 2483 | 1 | 39049.4063 | 1 | 0 |  | 1640.5 | 1879.5 | 151.5873 | 0.06105 | 0.06105 | 0 | 1.5159 | 0.0006105 | 0.0006105 | 0 | 1.5153 | 0.0006105 | 4.971 | 260538.0001 | 12233.3046
39049.4068 | 2232 | 1 | 39049.4068 | 1 | 0 |  | 1682.5 | 1921.5 | 136.2637 | 0.06105 | 0.06105 | 0 | 1.3626 | 0.0006105 | 0.0006105 | 0 | 1.362 | 0.0006105 | 16.7808 | 260538.0004 | 37323.6744
39049.4073 | 1996 | 1 | 39049.4073 | 1 | 0 |  | 1724.5 | 1963.5 | 121.8559 | 0.06105 | 0.06105 | 0 | 1.2186 | 0.0006105 | 0.0006105 | 0 | 1.2179 | 0.0006105 | 30.5955 | 260538.0001 | 60914.6197
39049.4078 | 2398 | 1 | 39049.4078 | 1 | 0 |  | 1766.5 | 2005.5 | 146.398 | 0.06105 | 0.06105 | 0 | 1.464 | 0.0006105 | 0.0006105 | 0 | 1.4634 | 0.0006105 | 8.6934 | 260538.0001 | 20730.0434
39049.4083 | 2018 | 1 | 39049.4083 | 1 | 0 |  | 1808.5 | 2047.5 | 123.199 | 0.06105 | 0.06105 | 0 | 1.232 | 0.0006105 | 0.0006105 | 0 | 1.2314 | 0.0006105 | 29.1711 | 260537.9999 | 58715.4638
39049.4088 | 2150 | 1 | 39049.4088 | 1 | 0 |  | 1850.5 | 2089.5 | 131.2576 | 0.06105 | 0.06105 | 0 | 1.3126 | 0.0006105 | 0.0006105 | 0 | 1.312 | 0.0006105 | 21.2369 | 260538.0001 | 45520.5283
39049.4092 | 2590 | 1 | 39049.4092 | 1 | 0 |  | 1892.5 | 2131.5 | 158.1197 | 0.06105 | 0.06105 | 0 | 1.5812 | 0.0006105 | 0.0006105 | 0 | 1.5806 | 0.0006105 | 0.63268 | 260538.0001 | 1537.4099
39049.4097 | 2004 | 1 | 39049.4097 | 1 | 0 |  | 1934.5 | 2173.5 | 122.3443 | 0.06105 | 0.06105 | 0 | 1.2234 | 0.0006105 | 0.0006105 | 0 | 1.2228 | 0.0006105 | 30.0739 | 260538.0001 | 60114.9266
39049.4102 | 2094 | 1 | 39049.4102 | 1 | 0 |  | 1976.5 | 2215.5 | 127.8388 | 0.06105 | 0.06105 | 0 | 1.2784 | 0.0006105 | 0.0006105 | 0 | 1.2778 | 0.0006105 | 24.4807 | 260537.9999 | 51118.3797
39049.4107 | 2588 | 1 | 39049.4107 | 1 | 0 |  | 2018.5 | 2257.5 | 157.9976 | 0.06105 | 0.06105 | 0 | 1.58 | 0.0006105 | 0.0006105 | 0 | 1.5794 | 0.0006105 | 0.71048 | 260537.9999 | 1737.3332
39049.4112 | 2271 | 1 | 39049.4112 | 1 | 0 |  | 2060.5 | 2299.5 | 138.6447 | 0.06105 | 0.06105 | 0 | 1.3864 | 0.0006105 | 0.0006105 | 0 | 1.3858 | 0.0006105 | 14.7745 | 260538.0001 | 33425.1707
39049.4117 | 2369 | 1 | 39049.4117 | 1 | 0 |  | 2102.5 | 2341.5 | 144.6276 | 0.06105 | 0.06105 | 0 | 1.4463 | 0.0006105 | 0.0006105 | 0 | 1.4457 | 0.0006105 | 10.0245 | 260537.9999 | 23628.9307
39049.4122 | 2467 | 1 | 39049.4122 | 25 | 0 |  | 2144.5 | 2383.5 | 150.6105 | 0.06105 | 1.5263 | 0 | 1.5061 | 0.0006105 | 0.015263 | 0 | 1.5055 | 0.015263 | 5.6521 | 10325.52 | 13705.268
39049.4126 | 2353 | 1 | 39049.4127 | 111 | 0 |  | 2186.5 | 2425.5 | 143.6508 | 0.06105 | 6.7766 | 0 | 1.4365 | 0.0006105 | 0.067766 | 0 | 1.4359 | 0.067766 | 10.7732 | 2248.0901 | 24163.169
39049.4131 | 2367 | 1 | 39049.4131 | 150 | 0 |  | 2228.5 | 2467.5 | 144.5055 | 0.06105 | 9.1575 | 0 | 1.4451 | 0.0006105 | 0.091575 | 0 | 1.4444 | 0.091575 | 10.1178 | 1637.5867 | 22466.0972
39049.4136 | 2113 | 1 | 39049.4136 | 110 | 0 |  | 2270 | 2509 | 128.9988 | 0.06105 | 6.7155 | 0 | 1.29 | 0.0006105 | 0.067155 | 0 | 1.2894 | 0.067155 | 23.3613 | 2269.4364 | 47159.9531
39049.4141 | 2052 | 1 | 39049.4141 | 109 | 0 |  | 2312 | 2551 | 125.2747 | 0.06105 | 6.6545 | 0 | 1.2527 | 0.0006105 | 0.066545 | 0 | 1.2521 | 0.066545 | 27.0303 | 2291.1743 | 53023.7396
39049.4146 | 2575 | 1 | 39049.4146 | 108 | 0 |  | 2354 | 2593 | 157.2039 | 0.06105 | 6.5934 | 0 | 1.572 | 0.0006105 | 0.065934 | 0 | 1.5714 | 0.065934 | 1.2191 | 2313.3148 | 2912.1151
39049.4151 | 2184 | 1 | 39049.4151 | 107 | 0 |  | 2396 | 2635 | 133.3333 | 0.06105 | 6.5324 | 0 | 1.3333 | 0.0006105 | 0.065324 | 0 | 1.3327 | 0.065324 | 19.349 | 2335.8692 | 40408.1041
39049.4156 | 2469 | 1 | 39049.4156 | 79 | 0 |  | 2438.5 | 2677.5 | 150.7326 | 0.06105 | 4.823 | 0 | 1.5073 | 0.0006105 | 0.04823 | 0 | 1.5067 | 0.04823 | 5.5665 | 3199.2152 | 13224.629
39049.416 | 2165 | 1 | 39049.4161 | 86 | 0 |  | 2480.5 | 2719.5 | 132.1734 | 0.06105 | 5.2503 | 0 | 1.3217 | 0.0006105 | 0.052503 | 0 | 1.3211 | 0.052503 | 20.3968 | 2930.6744 | 42584.9241
39049.4165 | 2178 | 1 | 39049.4165 | 57 | 0 |  | 2522.5 | 2761.5 | 132.967 | 0.06105 | 3.4799 | 0 | 1.3297 | 0.0006105 | 0.034799 | 0 | 1.3291 | 0.034799 | 19.6777 | 4472.5965 | 41803.345
39049.417 | 2137 | 1 | 39049.417 | 34 | 0 |  | 2564.5 | 2803.5 | 130.464 | 0.06105 | 2.0757 | 0 | 1.3046 | 0.0006105 | 0.020757 | 0 | 1.304 | 0.020757 | 21.9749 | 7565.8235 | 46227.0024
39049.4175 | 2411 | 1 | 39049.4175 | 41 | 0 |  | 2606.5 | 2845.5 | 147.1917 | 0.06105 | 2.5031 | 0 | 1.4719 | 0.0006105 | 0.025031 | 0 | 1.4713 | 0.025031 | 8.1071 | 6257.0244 | 19132.228
39049.418 | 2192 | 1 | 39049.418 | 36 | 0 |  | 2648 | 2887 | 133.8217 | 0.06105 | 2.1978 | 0 | 1.3382 | 0.0006105 | 0.021978 | 0 | 1.3376 | 0.021978 | 18.9129 | 7139.9444 | 40767.0288
39049.4185 | 2478 | 1 | 39049.4185 | 23 | 0 |  | 2690.5 | 2929.5 | 151.2821 | 0.06105 | 1.4042 | 0 | 1.5128 | 0.0006105 | 0.014042 | 0 | 1.5122 | 0.014042 | 5.1829 | 11232.087 | 12625.5935
39049.419 | 2012 | 1 | 39049.419 | 19 | 0 |  | 2732.5 | 2971.5 | 122.8327 | 0.06105 | 1.16 | 0 | 1.2283 | 0.0006105 | 0.0116 | 0 | 1.2277 | 0.0116 | 29.5565 | 13617.7895 | 58905.4376
39049.4194 | 2282 | 1 | 39049.4195 | 19 | 0 |  | 2774 | 3013 | 139.3162 | 0.06105 | 1.16 | 0 | 1.3932 | 0.0006105 | 0.0116 | 0 | 1.3926 | 0.0116 | 14.221 | 13617.7895 | 32102.2623
39049.4199 | 2233 | 1 | 39049.4199 | 17 | 0 |  | 2816 | 3055 | 136.3248 | 0.06105 | 1.0379 | 0 | 1.3632 | 0.0006105 | 0.010379 | 0 | 1.3626 | 0.010379 | 16.7285 | 15231.6471 | 36995.1168
39049.4204 | 2498 | 1 | 39049.4204 | 3 | 0 |  | 2858 | 3097 | 152.5031 | 0.06105 | 0.18315 | 0 | 1.525 | 0.0006105 | 0.0018315 | 0 | 1.5244 | 0.0018315 | 4.3404 | 86779.3334 | 10725.6403
39049.4209 | 2059 | 1 | 39049.4209 | 3 | 0 |  | 2900 | 3139 | 125.7021 | 0.06105 | 0.18315 | 0 | 1.257 | 0.0006105 | 0.0018315 | 0 | 1.2564 | 0.0018315 | 26.5977 | 86779.3333 | 54575.1105
39049.4214 | 2014 | 1 | 39049.4214 | 3 | 0 |  | 2942 | 3181 | 122.9548 | 0.06105 | 0.18315 | 0 | 1.2295 | 0.0006105 | 0.0018315 | 0 | 1.2289 | 0.0018315 | 29.4277 | 86779.3334 | 59069.9309
39049.4219 | 2512 | 1 | 39049.4219 | 2 | 0 |  | 2984 | 3223 | 153.3578 | 0.06105 | 0.1221 | 0 | 1.5336 | 0.0006105 | 0.001221 | 0 | 1.533 | 0.001221 | 3.7587 | 130219 | 9330.8345

## B3-C5
Open Burn Test 13 |  |  | 2006-11-28 | 9:21 |  |  | Vs = |  | 158.2039 |  | R = | 100
Mixed | 7-C | Tray F | IRMS | 1
0 | 150 kW |  | Bundle | Ch. 3 & 5 | Cable B | Odd - | Cable C |  | Odd
Time-21 | N11 | N12 | Time-22 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R5-G | R3-5
39049.3849 | 1 | 0 | 39049.3849 | 1 | 0 |  | -210 | 29 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259038 | 259038 | 259037.9994
39049.3854 | 1 | 0 | 39049.3854 | 1 | 0 |  | -168 | 71 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259038 | 259038 | 259037.9994
39049.3859 | 1 | 0 | 39049.3859 | 1 | 0 |  | -126 | 113 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259038 | 259038 | 259037.9994
39049.3864 | 1 | 0 | 39049.3864 | 1 | 0 |  | -84 | 155 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259038 | 259038 | 259037.9994
39049.3868 | 1 | 0 | 39049.3869 | 1 | 0 |  | -42.5 | 196.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259038 | 259038 | 259037.9994
39049.3873 | 1 | 0 | 39049.3873 | 1 | 0 |  | 5.4855e-07 | 239 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259038 | 259038 | 259037.9994
39049.3878 | 1 | 0 | 39049.3878 | 1 | 0 |  | 41.5 | 280.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259038 | 259038 | 259037.9994
39049.3883 | 1 | 0 | 39049.3883 | 1 | 0 |  | 84 | 323 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259038 | 259038 | 259037.9994
39049.3888 | 1 | 0 | 39049.3888 | 1 | 0 |  | 125.5 | 364.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259038 | 259038 | 259037.9994
39049.3893 | 1 | 0 | 39049.3893 | 1 | 0 |  | 167.5 | 406.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259038 | 259038 | 259037.9994
| 1 | 0 | 39049.3898 | 1 | 0 |  | 210 | 449 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259038 | 259038 | 259037.9994
39049.3902 | 1 | 0 | 39049.3903 | 1 | 0 |  | 251.5 | 490.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259038 | 259038 | 259037.9994
39049.3907 | 1 | 0 | 39049.3907 | 1 | 0 |  | 293.5 | 532.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259038 | 259038 | 259037.9994
39049.3912 | 1 | 0 | 39049.3912 | 1 | 0 |  | 335.5 | 574.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259038 | 259038 | 259037.9994
39049.3917 | 1 | 0 | 39049.3917 | 1 | 0 |  | 377.5 | 616.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259038 | 259038 | 259037.9994
39049.3922 | 1 | 0 | 39049.3922 | 1 | 0 |  | 419.5 | 658.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259038 | 259038 | 259037.9994
39049.3927 | 1 | 0 | 39049.3927 | 1 | 0 |  | 461.5 | 700.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259038 | 259038 | 259037.9994
39049.3932 | 1 | 0 | 39049.3932 | 1 | 0 |  | 503.5 | 742.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259038 | 259038 | 259037.9994
39049.3936 | 1 | 0 | 39049.3937 | 1 | 0 |  | 545.5 | 784.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259038 | 259038 | 259037.9994
39049.3941 | 1 | 0 | 39049.3941 | 1 | 0 |  | 587.5 | 826.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259038 | 259038 | 259037.9994
39049.3946 | 1 | 0 | 39049.3946 | 1 | 0 |  | 629.5 | 868.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259038 | 259038 | 259037.9994
39049.3951 | 1 | 0 | 39049.3951 | 1 | 0 |  | 671.5 | 910.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259038 | 259038 | 259037.9994
39049.3956 | 1 | 0 | 39049.3956 | 1 | 0 |  | 713.5 | 952.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259038 | 259038 | 259037.9994
39049.3961 | 1 | 0 | 39049.3961 | 1 | 0 |  | 755.5 | 994.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259038 | 259038 | 259037.9994
39049.3966 | 1 | 0 | 39049.3966 | 1 | 0 |  | 797.5 | 1036.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259038 | 259038 | 259037.9994
39049.397 | 1 | 0 | 39049.3971 | 1 | 0 |  | 839.5 | 1078.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259038 | 259038 | 259037.9994
39049.3975 | 1 | 0 | 39049.3975 | 1 | 0 |  | 881.5 | 1120.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259038 | 259038 | 259037.9994
39049.398 | 1 | 0 | 39049.398 | 1 | 0 |  | 923.5 | 1162.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259038 | 259038 | 259037.9994
39049.3985 | 1916 | 1 | 39049.3985 | 1 | 0 |  | 965.5 | 1204.5 | 116.9719 | 0.06105 | 0.06105 | 0 | 1.1697 | 0.0006105 | 0.0006105 | 0 | 1.1691 | 0.0006105 | 35.2679 | 259038 | 67411.976
39049.399 | 2523 | 1 | 39049.399 | 1 | 0 |  | 1007.5 | 1246.5 | 154.0293 | 0.06105 | 0.06105 | 0 | 1.5403 | 0.0006105 | 0.0006105 | 0 | 1.5397 | 0.0006105 | 2.7113 | 259038 | 6735.3998
39049.3995 | 2504 | 1 | 39049.3995 | 1 | 0 |  | 1049.5 | 1288.5 | 152.8694 | 0.06105 | 0.06105 | 0 | 1.5287 | 0.0006105 | 0.0006105 | 0 | 1.5281 | 0.0006105 | 3.491 | 259038 | 8634.6666
39049.4 | 2345 | 1 | 39049.4 | 1 | 0 |  | 1091.5 | 1330.5 | 143.1624 | 0.06105 | 0.06105 | 0 | 1.4316 | 0.0006105 | 0.0006105 | 0 | 1.431 | 0.0006105 | 10.5111 | 259038 | 24528.5309
39049.4005 | 2182 | 1 | 39049.4005 | 1 | 0 |  | 1133.5 | 1372.5 | 133.2112 | 0.06105 | 0.06105 | 0 | 1.3321 | 0.0006105 | 0.0006105 | 0 | 1.3315 | 0.0006105 | 18.7703 | 259038 | 40822.2408
39049.4009 | 2254 | 1 | 39049.4009 | 1 | 0 |  | 1175.5 | 1414.5 | 137.6068 | 0.06105 | 0.06105 | 0 | 1.3761 | 0.0006105 | 0.0006105 | 0 | 1.3755 | 0.0006105 | 14.9747 | 259038.0003 | 33625.0193
39049.4014 | 2359 | 1 | 39049.4014 | 1 | 0 |  | 1217.5 | 1456.5 | 144.0171 | 0.06105 | 0.06105 | 0 | 1.4402 | 0.0006105 | 0.0006105 | 0 | 1.4396 | 0.0006105 | 9.855 | 259038.0003 | 23129.0712
39049.4019 | 2032 | 1 | 39049.4019 | 1 | 0 |  | 1259.5 | 1498.5 | 124.0537 | 0.06105 | 0.06105 | 0 | 1.2405 | 0.0006105 | 0.0006105 | 0 | 1.2399 | 0.0006105 | 27.5421 | 259038 | 55816.4524
39049.4024 | 1676 | 1 | 39049.4024 | 1 | 0 |  | 1301.5 | 1540.5 | 102.3199 | 0.06105 | 0.06105 | 0 | 1.0232 | 0.0006105 | 0.0006105 | 0 | 1.0226 | 0.0006105 | 54.6496 | 259038.0003 | 91402.7146
39049.4029 | 1847 | 1 | 39049.4029 | 1 | 0 |  | 1343.5 | 1582.5 | 112.7595 | 0.06105 | 0.06105 | 0 | 1.1276 | 0.0006105 | 0.0006105 | 0 | 1.127 | 0.0006105 | 40.324 | 259038.0003 | 74309.3134
39049.4034 | 2307 | 1 | 39049.4034 | 1 | 0 |  | 1385.5 | 1624.5 | 140.8425 | 0.06105 | 0.06105 | 0 | 1.4084 | 0.0006105 | 0.0006105 | 0 | 1.4078 | 0.0006105 | 12.3322 | 259038 | 28327.0645
39049.4039 | 2433 | 1 | 39049.4039 | 1 | 0 |  | 1427.5 | 1666.5 | 148.5348 | 0.06105 | 0.06105 | 0 | 1.4853 | 0.0006105 | 0.0006105 | 0 | 1.4847 | 0.0006105 | 6.5123 | 259038.0003 | 15731.9268
39049.4043 | 2017 | 1 | 39049.4044 | 1 | 0 |  | 1469.5 | 1708.5 | 123.138 | 0.06105 | 0.06105 | 0 | 1.2314 | 0.0006105 | 0.0006105 | 0 | 1.2308 | 0.0006105 | 28.4911 | 259038.0003 | 57315.8736
39049.4048 | 2382 | 1 | 39049.4048 | 1 | 0 |  | 1511.5 | 1750.5 | 145.4212 | 0.06105 | 0.06105 | 0 | 1.4542 | 0.0006105 | 0.0006105 | 0 | 1.4536 | 0.0006105 | 8.7938 | 259038.0003 | 20829.9587
39049.4053 | 2013 | 1 | 39049.4053 | 1 | 0 |  | 1553.5 | 1792.5 | 122.8938 | 0.06105 | 0.06105 | 0 | 1.2289 | 0.0006105 | 0.0006105 | 0 | 1.2283 | 0.0006105 | 28.7465 | 259038.0003 | 57715.7192
39049.4058 | 2402 | 1 | 39049.4058 | 1 | 0 |  | 1595.5 | 1834.5 | 146.6422 | 0.06105 | 0.06105 | 0 | 1.4664 | 0.0006105 | 0.0006105 | 0 | 1.4658 | 0.0006105 | 7.8875 | 259038.0003 | 18830.7305
39049.4063 | 2229 | 1 | 39049.4063 | 1 | 0 |  | 1637.5 | 1876.5 | 136.0806 | 0.06105 | 0.06105 | 0 | 1.3608 | 0.0006105 | 0.0006105 | 0 | 1.3602 | 0.0006105 | 16.2648 | 259038 | 36124.0545
39049.4068 | 2015 | 1 | 39049.4068 | 2 | 0 |  | 1679.5 | 1918.5 | 123.0159 | 0.06105 | 0.1221 | 0 | 1.2302 | 0.0006105 | 0.001221 | 0 | 1.2295 | 0.001221 | 28.6187 | 129469 | 57493.5928
39049.4073 | 2400 | 1 | 39049.4073 | 1 | 0 |  | 1721.5 | 1960.5 | 146.5201 | 0.06105 | 0.06105 | 0 | 1.4652 | 0.0006105 | 0.0006105 | 0 | 1.4646 | 0.0006105 | 7.9775 | 259038.0003 | 19030.6533
39049.4077 | 2500 | 1 | 39049.4078 | 1 | 0 |  | 1763.5 | 2002.5 | 152.6252 | 0.06105 | 0.06105 | 0 | 1.5263 | 0.0006105 | 0.0006105 | 0 | 1.5256 | 0.0006105 | 3.6567 | 259038 | 9034.5123
39049.4082 | 2047 | 1 | 39049.4082 | 1 | 0 |  | 1805.5 | 2044.5 | 124.9695 | 0.06105 | 0.06105 | 0 | 1.2497 | 0.0006105 | 0.0006105 | 0 | 1.2491 | 0.0006105 | 26.607 | 259038 | 54317.0312
39049.4087 | 2575 | 1 | 39049.4087 | 1 | 0 |  | 1847.5 | 2086.5 | 157.2039 | 0.06105 | 0.06105 | 0 | 1.572 | 0.0006105 | 0.0006105 | 0 | 1.5714 | 0.0006105 | 0.63636 | 259038.0003 | 1537.4065
39049.4092 | 2183 | 1 | 39049.4092 | 1 | 0 |  | 1889.5 | 2128.5 | 133.2723 | 0.06105 | 0.06105 | 0 | 1.3327 | 0.0006105 | 0.0006105 | 0 | 1.3321 | 0.0006105 | 18.7159 | 259038.0003 | 40722.2794
39049.4097 | 2485 | 1 | 39049.4097 | 1 | 0 |  | 1931.5 | 2170.5 | 151.7094 | 0.06105 | 0.06105 | 0 | 1.5171 | 0.0006105 | 0.0006105 | 0 | 1.5165 | 0.0006105 | 4.2826 | 259038 | 10533.9334
39049.4102 | 2574 | 1 | 39049.4102 | 1 | 0 |  | 1973.5 | 2212.5 | 157.1429 | 0.06105 | 0.06105 | 0 | 1.5714 | 0.0006105 | 0.0006105 | 0 | 1.5708 | 0.0006105 | 0.67548 | 259038 | 1637.3679
39049.4107 | 2021 | 1 | 39049.4107 | 2 | 0 |  | 2015.5 | 2254.5 | 123.3822 | 0.06105 | 0.1221 | 0 | 1.2338 | 0.0006105 | 0.001221 | 0 | 1.2332 | 0.001221 | 28.2366 | 129469 | 56894.0558
39049.4111 | 2485 | 1 | 39049.4112 | 1 | 0 |  | 2057.5 | 2296.5 | 151.7094 | 0.06105 | 0.06105 | 0 | 1.5171 | 0.0006105 | 0.0006105 | 0 | 1.5165 | 0.0006105 | 4.2826 | 259038 | 10533.9334
39049.4116 | 2107 | 1 | 39049.4116 | 2 | 0 |  | 2099.5 | 2338.5 | 128.6325 | 0.06105 | 0.1221 | 0 | 1.2863 | 0.0006105 | 0.001221 | 0 | 1.2857 | 0.001221 | 23 | 129469 | 48300.6932
39049.4121 | 2368 | 1 | 39049.4121 | 1 | 0 |  | 2141.5 | 2380.5 | 144.5665 | 0.06105 | 0.06105 | 0 | 1.4457 | 0.0006105 | 0.0006105 | 0 | 1.4451 | 0.0006105 | 9.4373 | 259038 | 22229.4185
39049.4126 | 2396 | 1 | 39049.4126 | 12 | 0 |  | 2183.5 | 2422.5 | 146.2759 | 0.06105 | 0.7326 | 0 | 1.4628 | 0.0006105 | 0.007326 | 0 | 1.4621 | 0.007326 | 8.1578 | 21494.8333 | 19347.9877
39049.4131 | 1995 | 1 | 39049.4131 | 31 | 0 |  | 2225.5 | 2464.5 | 121.7949 | 0.06105 | 1.8926 | 0 | 1.2179 | 0.0006105 | 0.018926 | 0 | 1.2173 | 0.018926 | 29.9089 | 8259.2903 | 58825.7625
39049.4136 | 2150 | 1 | 39049.4136 | 33 | 0 |  | 2267.5 | 2506.5 | 131.2576 | 0.06105 | 2.0147 | 0 | 1.3126 | 0.0006105 | 0.020147 | 0 | 1.312 | 0.020147 | 20.539 | 7752.6667 | 43477.1969
39049.4141 | 2220 | 1 | 39049.4141 | 25 | 0 |  | 2309.5 | 2548.5 | 135.5311 | 0.06105 | 1.5263 | 0 | 1.3553 | 0.0006105 | 0.015263 | 0 | 1.3547 | 0.015263 | 16.7364 | 10265.52 | 36680.6807
39049.4145 | 2559 | 1 | 39049.4146 | 26 | 0 |  | 2351.5 | 2590.5 | 156.2271 | 0.06105 | 1.5873 | 0 | 1.5623 | 0.0006105 | 0.015873 | 0 | 1.5617 | 0.015873 | 1.2658 | 9866.8462 | 3106.5156
39049.415 | 2456 | 1 | 39049.415 | 14 | 0 |  | 2393.5 | 2632.5 | 149.9389 | 0.06105 | 0.8547 | 0 | 1.4994 | 0.0006105 | 0.008547 | 0 | 1.4988 | 0.008547 | 5.5145 | 18409.8571 | 13365.4008
39049.4155 | 1989 | 1 | 39049.4155 | 19 | 0 |  | 2435.5 | 2674.5 | 121.4286 | 0.06105 | 1.16 | 0 | 1.2143 | 0.0006105 | 0.0116 | 0 | 1.2137 | 0.0116 | 30.3009 | 13538.8421 | 59697.0681
39049.416 | 2554 | 1 | 39049.416 | 25 | 0 |  | 2477.5 | 2716.5 | 155.9219 | 0.06105 | 1.5263 | 0 | 1.5592 | 0.0006105 | 0.015263 | 0 | 1.5586 | 0.015263 | 1.4642 | 10265.52 | 3602.9029
39049.4165 | 2155 | 1 | 39049.4165 | 21 | 0 |  | 2519.5 | 2758.5 | 131.5629 | 0.06105 | 1.2821 | 0 | 1.3156 | 0.0006105 | 0.012821 | 0 | 1.315 | 0.012821 | 20.2591 | 12239.9048 | 43185.1772
39049.417 | 2073 | 1 | 39049.417 | 13 | 0 |  | 2561.5 | 2800.5 | 126.5568 | 0.06105 | 0.79365 | 0 | 1.2656 | 0.0006105 | 0.0079365 | 0 | 1.265 | 0.0079365 | 25.0184 | 19833.6923 | 51478.4495
39049.4175 | 2022 | 1 | 39049.4175 | 21 | 0 |  | 2603.5 | 2842.5 | 123.4432 | 0.06105 | 1.2821 | 0 | 1.2344 | 0.0006105 | 0.012821 | 0 | 1.2338 | 0.012821 | 28.1733 | 12239.9048 | 56377.3968
39049.418 | 2150 | 1 | 39049.418 | 29 | 0 |  | 2645.5 | 2884.5 | 131.2576 | 0.06105 | 1.7705 | 0 | 1.3126 | 0.0006105 | 0.017705 | 0 | 1.312 | 0.017705 | 20.539 | 8835.7931 | 43545.173
39049.4184 | 1976 | 1 | 39049.4184 | 20 | 0 |  | 2687.5 | 2926.5 | 120.6349 | 0.06105 | 1.221 | 0 | 1.2063 | 0.0006105 | 0.01221 | 0 | 1.2057 | 0.01221 | 31.1586 | 12856.9 | 60963.8279
39049.4189 | 1976 | 1 | 39049.4189 | 18 | 0 |  | 2729.5 | 2968.5 | 120.6349 | 0.06105 | 1.0989 | 0 | 1.2063 | 0.0006105 | 0.010989 | 0 | 1.2057 | 0.010989 | 31.1586 | 14296.5556 | 61011.2451
39049.4194 | 2514 | 1 | 39049.4194 | 16 | 0 |  | 2771.5 | 3010.5 | 153.4799 | 0.06105 | 0.9768 | 0 | 1.5348 | 0.0006105 | 0.009768 | 0 | 1.5342 | 0.009768 | 3.0792 | 16096.125 | 7590.8406
39049.4199 | 2388 | 1 | 39049.4199 | 12 | 0 |  | 2813.5 | 3052.5 | 145.7875 | 0.06105 | 0.7326 | 0 | 1.4579 | 0.0006105 | 0.007326 | 0 | 1.4573 | 0.007326 | 8.5203 | 21494.8333 | 20144.2831
39049.4204 | 2530 | 1 | 39049.4204 | 10 | 0 |  | 2855.5 | 3094.5 | 154.4567 | 0.06105 | 0.6105 | 0 | 1.5446 | 0.0006105 | 0.006105 | 0 | 1.544 | 0.006105 | 2.427 | 25813.8 | 6014.6997
39049.4209 | 2069 | 1 | 39049.4209 | 8 | 0 |  | 2897.5 | 3136.5 | 126.3126 | 0.06105 | 0.4884 | 0 | 1.2631 | 0.0006105 | 0.004884 | 0 | 1.2625 | 0.004884 | 25.2602 | 32292.25 | 51977.0417
39049.4214 | 2203 | 1 | 39049.4214 | 6 | 0 |  | 2939.5 | 3178.5 | 134.4933 | 0.06105 | 0.3663 | 0 | 1.3449 | 0.0006105 | 0.003663 | 0 | 1.3443 | 0.003663 | 17.6376 | 43089.6667 | 38648.3072
39049.4218 | 2052 | 1 | 39049.4219 | 5 | 0 |  | 2981.5 | 3220.5 | 125.2747 | 0.06105 | 0.30525 | 0 | 1.2527 | 0.0006105 | 0.0030525 | 0 | 1.2521 | 0.0030525 | 26.2984 | 51727.6 | 53734.121

## B3-B4
Open Burn Test 13 |  |  | 2006-11-28 | 9:21 |  |  | Vs = |  | 158.0208 |  | R = | 100
Mixed | 7-C | Tray F | IRMS | 1
0 | 150 kW |  | Bundle | Ch. 3 & 4 | Cable B | Odd -Even
Time-19 | N11 | N12 | Time-20 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R4-G | R3-4
39049.3849 | 1 | 0 | 39049.3849 | 1 | 0 |  | -213 | 26 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258738 | 258738 | 258737.9994
39049.3853 | 1 | 0 | 39049.3854 | 1 | 0 |  | -171 | 68 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258738 | 258738 | 258737.9994
39049.3858 | 1 | 0 | 39049.3859 | 1 | 0 |  | -129 | 110 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258738 | 258738 | 258737.9994
39049.3863 | 1 | 0 | 39049.3863 | 1 | 0 |  | -87 | 152 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258738 | 258738 | 258737.9994
39049.3868 | 1 | 0 | 39049.3868 | 1 | 0 |  | -45 | 194 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258738 | 258738 | 258737.9994
39049.3873 | 1 | 0 | 39049.3873 | 1 | 0 |  | -3 | 236 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258738 | 258738 | 258737.9994
39049.3878 | 1 | 0 | 39049.3878 | 1 | 0 |  | 39 | 278 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258738 | 258738 | 258737.9994
39049.3883 | 1 | 0 | 39049.3883 | 1 | 0 |  | 81 | 320 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258738 | 258738 | 258737.9994
39049.3887 | 1 | 0 | 39049.3888 | 1 | 0 |  | 123 | 362 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258738 | 258738 | 258737.9994
39049.3892 | 1 | 0 | 39049.3893 | 1 | 0 |  | 165 | 404 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258738 | 258738 | 258737.9994
39049.3897 | 1 | 0 | 39049.3897 | 1 | 0 |  | 207 | 446 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258738 | 258738 | 258737.9994
39049.3902 | 1 | 0 | 39049.3902 | 1 | 0 |  | 249 | 488 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258738 | 258738 | 258737.9994
39049.3907 | 1 | 0 | 39049.3907 | 1 | 0 |  | 291 | 530 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258738 | 258738 | 258737.9994
39049.3912 | 1 | 0 | 39049.3912 | 1 | 0 |  | 333 | 572 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258738 | 258738 | 258737.9994
39049.3917 | 1 | 0 | 39049.3917 | 1 | 0 |  | 375 | 614 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258738 | 258738 | 258737.9994
39049.3922 | 1 | 0 | 39049.3922 | 1 | 0 |  | 417 | 656 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258738 | 258738 | 258737.9994
39049.3926 | 1 | 0 | 39049.3927 | 1 | 0 |  | 459 | 698 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258738 | 258738 | 258737.9994
39049.3931 | 1 | 0 | 39049.3931 | 1 | 0 |  | 501 | 740 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258738 | 258738 | 258737.9994
39049.3936 | 1 | 0 | 39049.3936 | 1 | 0 |  | 543 | 782 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258738 | 258738 | 258737.9994
39049.3941 | 1 | 0 | 39049.3941 | 1 | 0 |  | 585 | 824 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258738 | 258738 | 258737.9994
39049.3946 | 1 | 0 | 39049.3946 | 1 | 0 |  | 627 | 866 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258738 | 258738 | 258737.9994
39049.3951 | 1 | 0 | 39049.3951 | 1 | 0 |  | 669 | 908 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258738 | 258738 | 258737.9994
39049.3956 | 1 | 0 | 39049.3956 | 1 | 0 |  | 711 | 950 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258738 | 258738 | 258737.9994
39049.396 | 1 | 0 | 39049.3961 | 1 | 0 |  | 752.5 | 991.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258738 | 258738 | 258737.9994
39049.3965 | 1 | 0 | 39049.3966 | 1 | 0 |  | 795 | 1034 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258738 | 258738 | 258737.9994
39049.397 | 1 | 0 | 39049.397 | 1 | 0 |  | 837 | 1076 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258738 | 258738 | 258737.9994
39049.3975 | 1 | 0 | 39049.3975 | 1 | 0 |  | 879 | 1118 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258738 | 258738 | 258737.9994
39049.398 | 1 | 0 | 39049.398 | 1 | 0 |  | 921 | 1160 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258738 | 258738 | 258737.9994
39049.3985 | 1154 | 1 | 39049.3985 | 1 | 0 |  | 963 | 1202 | 70.4518 | 0.06105 | 0.06105 | 0 | 0.70452 | 0.0006105 | 0.0006105 | 0 | 0.70391 | 0.0006105 | 124.4042 | 258738.0001 | 143282.6225
39049.399 | 2200 | 0 | 39049.399 | 2296 | 0 |  | 1004.5 | 1243.5 | 134.3101 | 0 | 140.1709 | 0 | 1.3431 | 0 | 1.4017 | 0 | 1.3431 | 1.4017 | 17.6536 | 12.7343 | 16.3105
39049.3994 | 2349 | 0 | 39049.3995 | 2202 | 0 |  | 1046.5 | 1285.5 | 143.4066 | 0 | 134.4322 | 0 | 1.4341 | 0 | 1.3443 | 0 | 1.4341 | 1.3443 | 10.1907 | 17.5468 | 8.7567
39049.3999 | 1894 | 0 | 39049.3999 | 2528 | 0 |  | 1088.5 | 1327.5 | 115.6288 | 0 | 154.3346 | 0 | 1.1563 | 0 | 1.5433 | 0 | 1.1563 | 1.5433 | 36.6621 | 2.3884 | 35.5058
39049.4004 | 2130 | 0 | 39049.4004 | 1948 | 1 |  | 1131 | 1370 | 130.0366 | 0 | 118.9255 | 0.06105 | 1.3004 | 0 | 1.1893 | 0.0006105 | 1.3004 | 1.1886 | 21.5202 | 32.942 | 20.2198
39049.4009 | 1915 | 0 | 39049.4009 | 1857 | 0 |  | 1173 | 1412 | 116.9109 | 0 | 113.37 | 0 | 1.1691 | 0 | 1.1337 | 0 | 1.1691 | 1.1337 | 35.1634 | 39.385 | 33.9943
39049.4014 | 1968 | 0 | 39049.4014 | 2044 | 0 |  | 1214.5 | 1453.5 | 120.1465 | 0 | 124.7863 | 0 | 1.2015 | 0 | 1.2479 | 0 | 1.2015 | 1.2479 | 31.5234 | 26.6331 | 30.3219
39049.4019 | 2364 | 0 | 39049.4019 | 2307 | 0 |  | 1256.5 | 1495.5 | 144.3223 | 0 | 140.8425 | 0 | 1.4432 | 0 | 1.4084 | 0 | 1.4432 | 1.4084 | 9.4915 | 12.1968 | 8.0483
39049.4024 | 2281 | 37 | 39049.4024 | 2073 | 55 |  | 1298.5 | 1537.5 | 139.2552 | 2.2589 | 126.5568 | 3.3578 | 1.3926 | 0.022589 | 1.2656 | 0.033578 | 1.37 | 1.232 | 14.4551 | 31.4733 | 174.9355
39049.4028 | 2218 | 2 | 39049.4029 | 2226 | 2 |  | 1341 | 1580 | 135.409 | 0.1221 | 135.8974 | 0.1221 | 1.3541 | 0.001221 | 1.359 | 0.001221 | 1.3529 | 1.3578 | 16.8065 | 16.3817 | 2592.6314
39049.4033 | 2019 | 0 | 39049.4033 | 2496 | 0 |  | 1382.5 | 1621.5 | 123.2601 | 0 | 152.381 | 0 | 1.2326 | 0 | 1.5238 | 0 | 1.2326 | 1.5238 | 28.2011 | 3.7011 | 26.9685
39049.4038 | 2502 | 0 | 39049.4038 | 2277 | 0 |  | 1425 | 1664 | 152.7473 | 0 | 139.011 | 0 | 1.5275 | 0 | 1.3901 | 0 | 1.5275 | 1.3901 | 3.4524 | 13.675 | 1.925
39049.4043 | 2471 | 0 | 39049.4043 | 2266 | 0 |  | 1466.5 | 1705.5 | 150.8547 | 0 | 138.3394 | 0 | 1.5085 | 0 | 1.3834 | 0 | 1.5085 | 1.3834 | 4.7503 | 14.2268 | 3.2418
39049.4048 | 2506 | 0 | 39049.4048 | 2250 | 0 |  | 1508.5 | 1747.5 | 152.9915 | 0 | 137.3626 | 0 | 1.5299 | 0 | 1.3736 | 0 | 1.5299 | 1.3736 | 3.2873 | 15.0391 | 1.7574
39049.4053 | 2258 | 0 | 39049.4053 | 2158 | 0 |  | 1550.5 | 1789.5 | 137.851 | 0 | 131.746 | 0 | 1.3785 | 0 | 1.3175 | 0 | 1.3785 | 1.3175 | 14.6315 | 19.9435 | 13.253
39049.4058 | 2514 | 0 | 39049.4058 | 2515 | 0 |  | 1592.5 | 1831.5 | 153.4799 | 0 | 153.5409 | 0 | 1.5348 | 0 | 1.5354 | 0 | 1.5348 | 1.5354 | 2.9586 | 2.9177 | 1.4238
39049.4062 | 2037 | 0 | 39049.4063 | 2271 | 0 |  | 1634.5 | 1873.5 | 124.359 | 0 | 138.6447 | 0 | 1.2436 | 0 | 1.3864 | 0 | 1.2436 | 1.3864 | 27.0682 | 13.9753 | 25.8246
39049.4067 | 2268 | 0 | 39049.4067 | 2477 | 0 |  | 1676.5 | 1915.5 | 138.4615 | 0 | 151.221 | 0 | 1.3846 | 0 | 1.5122 | 0 | 1.3846 | 1.5122 | 14.1261 | 4.4966 | 12.7415
39049.4072 | 2505 | 0 | 39049.4072 | 2317 | 0 |  | 1718.5 | 1957.5 | 152.9304 | 0 | 141.453 | 0 | 1.5293 | 0 | 1.4145 | 0 | 1.5293 | 1.4145 | 3.3285 | 11.7126 | 1.7992
39049.4077 | 2392 | 0 | 39049.4077 | 2196 | 0 |  | 1760.5 | 1999.5 | 146.0317 | 0 | 134.0659 | 0 | 1.4603 | 0 | 1.3407 | 0 | 1.4603 | 1.3407 | 8.2099 | 17.8679 | 6.7495
39049.4082 | 2381 | 0 | 39049.4082 | 2174 | 0 |  | 1802.5 | 2041.5 | 145.3602 | 0 | 132.7228 | 0 | 1.4536 | 0 | 1.3272 | 0 | 1.4536 | 1.3272 | 8.7098 | 19.0607 | 7.2562
39049.4087 | 2185 | 0 | 39049.4087 | 2055 | 0 |  | 1844.5 | 2083.5 | 133.3944 | 0 | 125.4579 | 0 | 1.3339 | 0 | 1.2546 | 0 | 1.3339 | 1.2546 | 18.4613 | 25.9552 | 17.1274
39049.4092 | 2197 | 0 | 39049.4092 | 2414 | 0 |  | 1886.5 | 2125.5 | 134.127 | 0 | 147.3748 | 0 | 1.3413 | 0 | 1.4737 | 0 | 1.3413 | 1.4737 | 17.8143 | 7.2237 | 16.473
39049.4097 | 2026 | 0 | 39049.4097 | 2310 | 0 |  | 1928.5 | 2167.5 | 123.6874 | 0 | 141.0256 | 0 | 1.2369 | 0 | 1.4103 | 0 | 1.2369 | 1.4103 | 27.7581 | 12.0511 | 26.5213
39049.4101 | 2020 | 0 | 39049.4102 | 2559 | 0 |  | 1970.5 | 2209.5 | 123.3211 | 0 | 156.2271 | 0 | 1.2332 | 0 | 1.5623 | 0 | 1.2332 | 1.5623 | 28.1376 | 1.1481 | 26.9044
39049.4106 | 2542 | 0 | 39049.4106 | 2058 | 0 |  | 2012.5 | 2251.5 | 155.1893 | 0 | 125.641 | 0 | 1.5519 | 0 | 1.2564 | 0 | 1.5519 | 1.2564 | 1.8245 | 25.7716 | 0.27266
39049.4111 | 2441 | 0 | 39049.4111 | 2054 | 0 |  | 2054.5 | 2293.5 | 149.0232 | 0 | 125.3968 | 0 | 1.4902 | 0 | 1.254 | 0 | 1.4902 | 1.254 | 6.0377 | 26.0166 | 4.5475
39049.4116 | 2169 | 0 | 39049.4116 | 2085 | 0 |  | 2096.5 | 2335.5 | 132.4176 | 0 | 127.2894 | 0 | 1.3242 | 0 | 1.2729 | 0 | 1.3242 | 1.2729 | 19.3352 | 24.1429 | 18.011
39049.4121 | 2484 | 0 | 39049.4121 | 2376 | 0 |  | 2138.5 | 2377.5 | 151.6484 | 0 | 145.0549 | 0 | 1.5165 | 0 | 1.4505 | 0 | 1.5165 | 1.4505 | 4.2021 | 8.9386 | 2.6856
39049.4126 | 2011 | 0 | 39049.4126 | 2514 | 0 |  | 2180.5 | 2419.5 | 122.7717 | 0 | 153.4799 | 0 | 1.2277 | 0 | 1.5348 | 0 | 1.2277 | 1.5348 | 28.7111 | 2.9586 | 27.4834
39049.4131 | 2181 | 0 | 39049.4131 | 2170 | 0 |  | 2222.5 | 2461.5 | 133.1502 | 0 | 132.4786 | 0 | 1.3315 | 0 | 1.3248 | 0 | 1.3315 | 1.3248 | 18.6786 | 19.2802 | 17.3471
39049.4135 | 2150 | 0 | 39049.4136 | 2527 | 0 |  | 2264.5 | 2503.5 | 131.2576 | 0 | 154.2735 | 0 | 1.3126 | 0 | 1.5427 | 0 | 1.3126 | 1.5427 | 20.3898 | 2.429 | 19.0772
39049.414 | 2446 | 0 | 39049.414 | 2536 | 0 |  | 2306.5 | 2545.5 | 149.3284 | 0 | 154.823 | 0 | 1.4933 | 0 | 1.5482 | 0 | 1.4933 | 1.5482 | 5.8209 | 2.0655 | 4.3276
39049.4145 | 2350 | 0 | 39049.4145 | 2009 | 0 |  | 2348.5 | 2587.5 | 143.4676 | 0 | 122.6496 | 0 | 1.4347 | 0 | 1.2265 | 0 | 1.4347 | 1.2265 | 10.1438 | 28.8392 | 8.7092
39049.415 | 2572 | 0 | 39049.415 | 2083 | 0 |  | 2390.5 | 2629.5 | 157.0208 | 0 | 127.1673 | 0 | 1.5702 | 0 | 1.2717 | 0 | 1.5702 | 1.2717 | 0.63686 | 24.2621 | 0.93335
39049.4155 | 2326 | 0 | 39049.4155 | 2503 | 0 |  | 2432.5 | 2671.5 | 142.0024 | 0 | 152.8083 | 0 | 1.42 | 0 | 1.5281 | 0 | 1.42 | 1.5281 | 11.2803 | 3.4111 | 9.8603
39049.416 | 2258 | 0 | 39049.416 | 2547 | 0 |  | 2474.5 | 2713.5 | 137.851 | 0 | 155.4945 | 0 | 1.3785 | 0 | 1.5549 | 0 | 1.3785 | 1.5549 | 14.6315 | 1.6247 | 13.253
39049.4165 | 2414 | 0 | 39049.4165 | 2194 | 0 |  | 2516.5 | 2755.5 | 147.3748 | 0 | 133.9438 | 0 | 1.4737 | 0 | 1.3394 | 0 | 1.4737 | 1.3394 | 7.2237 | 17.9754 | 5.7499
39049.4169 | 2564 | 0 | 39049.417 | 1994 | 0 |  | 2558.5 | 2797.5 | 156.5324 | 0 | 121.7338 | 0 | 1.5653 | 0 | 1.2173 | 0 | 1.5653 | 1.2173 | 0.95086 | 29.8084 | 0.61447
39049.4174 | 2141 | 0 | 39049.4174 | 2330 | 0 |  | 2600.5 | 2839.5 | 130.7082 | 0 | 142.2466 | 0 | 1.3071 | 0 | 1.4225 | 0 | 1.3071 | 1.4225 | 20.8958 | 11.0893 | 19.5888
39049.4179 | 2353 | 0 | 39049.4179 | 2082 | 0 |  | 2642.5 | 2881.5 | 143.6508 | 0 | 127.1062 | 0 | 1.4365 | 0 | 1.2711 | 0 | 1.4365 | 1.2711 | 10.0034 | 24.3218 | 8.5669
39049.4184 | 2278 | 0 | 39049.4184 | 2265 | 0 |  | 2684.5 | 2923.5 | 139.072 | 0 | 138.2784 | 0 | 1.3907 | 0 | 1.3828 | 0 | 1.3907 | 1.3828 | 13.6251 | 14.2773 | 12.2344
39049.4189 | 2460 | 0 | 39049.4189 | 2321 | 0 |  | 2726.5 | 2965.5 | 150.1832 | 0 | 141.6972 | 0 | 1.5018 | 0 | 1.417 | 0 | 1.5018 | 1.417 | 5.2187 | 11.52 | 3.7169
39049.4194 | 2032 | 0 | 39049.4194 | 2539 | 0 |  | 2768.5 | 3007.5 | 124.0537 | 0 | 155.0061 | 0 | 1.2405 | 0 | 1.5501 | 0 | 1.2405 | 1.5501 | 27.3809 | 1.9449 | 26.1404
39049.4199 | 2422 | 0 | 39049.4199 | 2432 | 0 |  | 2810.5 | 3049.5 | 147.8632 | 0 | 148.4737 | 0 | 1.4786 | 0 | 1.4847 | 0 | 1.4786 | 1.4847 | 6.8695 | 6.4301 | 5.3909
39049.4203 | 2534 | 0 | 39049.4204 | 2266 | 0 |  | 2852.5 | 3091.5 | 154.7009 | 0 | 138.3394 | 0 | 1.547 | 0 | 1.3834 | 0 | 1.547 | 1.3834 | 2.146 | 14.2268 | 0.59901
39049.4208 | 2542 | 0 | 39049.4208 | 2040 | 0 |  | 2894.5 | 3133.5 | 155.1893 | 0 | 124.5421 | 0 | 1.5519 | 0 | 1.2454 | 0 | 1.5519 | 1.2454 | 1.8245 | 26.8814 | 0.27266
39049.4213 | 2515 | 0 | 39049.4213 | 2321 | 0 |  | 2936.5 | 3175.5 | 153.5409 | 0 | 141.6972 | 0 | 1.5354 | 0 | 1.417 | 0 | 1.5354 | 1.417 | 2.9177 | 11.52 | 1.3823
39049.4218 | 2360 | 0 | 39049.4218 | 2163 | 0 |  | 2978.5 | 3217.5 | 144.0781 | 0 | 132.0513 | 0 | 1.4408 | 0 | 1.3205 | 0 | 1.4408 | 1.3205 | 9.6771 | 19.6662 | 8.2363

## A2-C6
Open Burn Test 13 |  |  | 2006-11-28 | 9:21 |  |  | Vs = |  | 156.2503 |  | R = | 100
Mixed | 7-C | Tray F | IRMS | 1
0 | 150 kW |  | Bundle | Ch. 2 & 6 | Cable A | Even - | Cable C |  | Even
Time-17 | N11 | N12 | Time-18 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R6-G | R2-6
39049.3848 | 1 | 0 | 39049.3848 | 1 | 0 |  | -215.5 | 23.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
39049.3853 | 1 | 0 | 39049.3853 | 1 | 0 |  | -174 | 65 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
39049.3858 | 1 | 0 | 39049.3858 | 1 | 0 |  | -131.5 | 107.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
39049.3863 | 1 | 0 | 39049.3863 | 1 | 0 |  | -90 | 149 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
39049.3868 | 1 | 0 | 39049.3868 | 1 | 0 |  | -47.5 | 191.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
39049.3873 | 1 | 0 | 39049.3873 | 1 | 0 |  | -6 | 233 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
39049.3877 | 1 | 0 | 39049.3878 | 1 | 0 |  | 36 | 275 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
39049.3882 | 1 | 0 | 39049.3883 | 1 | 0 |  | 78.5 | 317.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
39049.3887 | 1 | 0 | 39049.3887 | 1 | 0 |  | 120 | 359 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
39049.3892 | 1 | 0 | 39049.3892 | 1 | 0 |  | 162 | 401 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
39049.3897 | 1 | 0 | 39049.3897 | 1 | 0 |  | 204.5 | 443.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
39049.3902 | 1 | 0 | 39049.3902 | 1 | 0 |  | 246 | 485 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
39049.3907 | 1 | 0 | 39049.3907 | 1 | 0 |  | 288 | 527 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
39049.3911 | 1 | 0 | 39049.3912 | 1 | 0 |  | 330 | 569 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
39049.3916 | 1 | 0 | 39049.3917 | 1 | 0 |  | 372 | 611 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
39049.3921 | 1 | 0 | 39049.3921 | 1 | 0 |  | 414 | 653 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
39049.3926 | 1 | 0 | 39049.3926 | 1 | 0 |  | 456 | 695 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
39049.3931 | 1 | 0 | 39049.3931 | 1 | 0 |  | 498 | 737 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
39049.3936 | 1 | 0 | 39049.3936 | 1 | 0 |  | 540 | 779 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
39049.3941 | 1 | 0 | 39049.3941 | 1 | 0 |  | 582 | 821 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
39049.3945 | 1 | 0 | 39049.3946 | 1 | 0 |  | 624 | 863 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
39049.395 | 1 | 0 | 39049.3951 | 1 | 0 |  | 666 | 905 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
39049.3955 | 1 | 0 | 39049.3955 | 1 | 0 |  | 708 | 947 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
39049.396 | 1 | 0 | 39049.396 | 1 | 0 |  | 750 | 989 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
39049.3965 | 1 | 0 | 39049.3965 | 1 | 0 |  | 792 | 1031 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
39049.397 | 1 | 0 | 39049.397 | 1 | 0 |  | 834 | 1073 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
39049.3975 | 1 | 0 | 39049.3975 | 1 | 0 |  | 876 | 1115 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
39049.398 | 1 | 0 | 39049.398 | 1 | 0 |  | 918 | 1157 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
39049.3984 | 1 | 0 | 39049.3985 | 1 | 0 |  | 960 | 1199 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
39049.3989 | 1 | 0 | 39049.3989 | 1 | 0 |  | 1002 | 1241 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
39049.3994 | 1 | 0 | 39049.3994 | 1 | 0 |  | 1044 | 1283 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
39049.3999 | 1 | 0 | 39049.3999 | 1 | 0 |  | 1086 | 1325 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
39049.4004 | 1 | 0 | 39049.4004 | 1 | 0 |  | 1128 | 1367 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
39049.4009 | 1 | 0 | 39049.4009 | 1 | 0 |  | 1170 | 1409 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
39049.4014 | 1 | 0 | 39049.4014 | 1 | 0 |  | 1212 | 1451 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
39049.4018 | 1615 | 1 | 39049.4019 | 1 | 0 |  | 1254 | 1493 | 98.5958 | 0.06105 | 0.06105 | 0 | 0.98596 | 0.0006105 | 0.0006105 | 0 | 0.98535 | 0.0006105 | 58.5118 | 255838 | 94301.1403
39049.4023 | 1186 | 1 | 39049.4023 | 1 | 0 |  | 1296 | 1535 | 72.4054 | 0.06105 | 0.06105 | 0 | 0.72405 | 0.0006105 | 0.0006105 | 0 | 0.72344 | 0.0006105 | 115.8971 | 255838.0001 | 137184.3784
39049.4028 | 1884 | 1 | 39049.4028 | 1 | 0 |  | 1338 | 1577 | 115.0183 | 0.06105 | 0.06105 | 0 | 1.1502 | 0.0006105 | 0.0006105 | 0 | 1.1496 | 0.0006105 | 35.8672 | 255837.9999 | 67411.6506
39049.4033 | 2059 | 1 | 39049.4033 | 1 | 0 |  | 1380 | 1619 | 125.7021 | 0.06105 | 0.06105 | 0 | 1.257 | 0.0006105 | 0.0006105 | 0 | 1.2564 | 0.0006105 | 24.3139 | 255838.0004 | 49918.4882
39049.4038 | 2170 | 1 | 39049.4038 | 1 | 0 |  | 1422 | 1661 | 132.4786 | 0.06105 | 0.06105 | 0 | 1.3248 | 0.0006105 | 0.0006105 | 0 | 1.3242 | 0.0006105 | 17.9521 | 255838.0001 | 38822.8252
39049.4043 | 2086 | 1 | 39049.4043 | 1 | 0 |  | 1464 | 1703 | 127.3504 | 0.06105 | 0.06105 | 0 | 1.2735 | 0.0006105 | 0.0006105 | 0 | 1.2729 | 0.0006105 | 22.7041 | 255837.9999 | 47219.5432
39049.4048 | 2321 | 1 | 39049.4048 | 1 | 0 |  | 1506 | 1745 | 141.6972 | 0.06105 | 0.06105 | 0 | 1.417 | 0.0006105 | 0.0006105 | 0 | 1.4164 | 0.0006105 | 10.275 | 255837.9999 | 23728.7251
39049.4052 | 2251 | 1 | 39049.4053 | 1 | 0 |  | 1548 | 1787 | 137.4237 | 0.06105 | 0.06105 | 0 | 1.3742 | 0.0006105 | 0.0006105 | 0 | 1.3736 | 0.0006105 | 13.7058 | 255837.9999 | 30725.9901
39049.4057 | 1890 | 1 | 39049.4058 | 1 | 0 |  | 1590 | 1829 | 115.3846 | 0.06105 | 0.06105 | 0 | 1.1538 | 0.0006105 | 0.0006105 | 0 | 1.1532 | 0.0006105 | 35.4357 | 255837.9999 | 66811.8851
39049.4062 | 1936 | 1 | 39049.4062 | 1 | 0 |  | 1632 | 1871 | 118.1929 | 0.06105 | 0.06105 | 0 | 1.1819 | 0.0006105 | 0.0006105 | 0 | 1.1813 | 0.0006105 | 32.216 | 255837.9999 | 62213.6824
39049.4067 | 2147 | 1 | 39049.4067 | 1 | 0 |  | 1674 | 1913 | 131.0745 | 0.06105 | 0.06105 | 0 | 1.3107 | 0.0006105 | 0.0006105 | 0 | 1.3101 | 0.0006105 | 19.2162 | 255838.0001 | 41121.9266
39049.4072 | 1871 | 1 | 39049.4072 | 1 | 0 |  | 1716 | 1955 | 114.2247 | 0.06105 | 0.06105 | 0 | 1.1422 | 0.0006105 | 0.0006105 | 0 | 1.1416 | 0.0006105 | 36.8118 | 255837.9999 | 68711.1427
39049.4077 | 2313 | 1 | 39049.4077 | 1 | 0 |  | 1758 | 1997 | 141.2088 | 0.06105 | 0.06105 | 0 | 1.4121 | 0.0006105 | 0.0006105 | 0 | 1.4115 | 0.0006105 | 10.6566 | 255837.9999 | 24528.4125
39049.4082 | 2192 | 1 | 39049.4082 | 1 | 0 |  | 1800 | 2039 | 133.8217 | 0.06105 | 0.06105 | 0 | 1.3382 | 0.0006105 | 0.0006105 | 0 | 1.3376 | 0.0006105 | 16.7677 | 255838.0001 | 36623.6848
39049.4086 | 1923 | 1 | 39049.4087 | 1 | 0 |  | 1842 | 2081 | 117.3993 | 0.06105 | 0.06105 | 0 | 1.174 | 0.0006105 | 0.0006105 | 0 | 1.1734 | 0.0006105 | 33.1103 | 255838.0001 | 63513.1745
39049.4091 | 2080 | 1 | 39049.4092 | 1 | 0 |  | 1884 | 2123 | 126.9841 | 0.06105 | 0.06105 | 0 | 1.2698 | 0.0006105 | 0.0006105 | 0 | 1.2692 | 0.0006105 | 23.0582 | 255837.9999 | 47819.3088
39049.4096 | 1925 | 1 | 39049.4096 | 1 | 0 |  | 1926 | 2165 | 117.5214 | 0.06105 | 0.06105 | 0 | 1.1752 | 0.0006105 | 0.0006105 | 0 | 1.1746 | 0.0006105 | 32.9719 | 255838.0001 | 63313.2526
39049.4101 | 2030 | 1 | 39049.4101 | 1 | 0 |  | 1968 | 2207 | 123.9316 | 0.06105 | 0.06105 | 0 | 1.2393 | 0.0006105 | 0.0006105 | 0 | 1.2387 | 0.0006105 | 26.0907 | 255838.0001 | 52817.3552
| 2182 | 1 | 39049.4106 | 1 | 0 |  | 2011 | 2250 | 133.2112 | 0.06105 | 0.06105 | 0 | 1.3321 | 0.0006105 | 0.0006105 | 0 | 1.3315 | 0.0006105 | 17.3031 | 255837.9999 | 37623.2941
39049.4111 | 2334 | 1 | 39049.4111 | 1 | 0 |  | 2052 | 2291 | 142.4908 | 0.06105 | 0.06105 | 0 | 1.4249 | 0.0006105 | 0.0006105 | 0 | 1.4243 | 0.0006105 | 9.6605 | 255838.0001 | 22429.233
39049.4116 | 1871 | 1 | 39049.4116 | 1 | 0 |  | 2094 | 2333 | 114.2247 | 0.06105 | 0.06105 | 0 | 1.1422 | 0.0006105 | 0.0006105 | 0 | 1.1416 | 0.0006105 | 36.8118 | 255837.9999 | 68711.1427
39049.412 | 2395 | 1 | 39049.4121 | 2 | 0 |  | 2136 | 2375 | 146.2149 | 0.06105 | 0.1221 | 0 | 1.4621 | 0.0006105 | 0.001221 | 0 | 1.4615 | 0.001221 | 6.8663 | 127869 | 16325.2328
39049.4125 | 2356 | 1 | 39049.4126 | 95 | 0 |  | 2178 | 2417 | 143.8339 | 0.06105 | 5.7998 | 0 | 1.4383 | 0.0006105 | 0.057998 | 0 | 1.4377 | 0.057998 | 8.6362 | 2594.0842 | 19486.7985
39049.413 | 2257 | 1 | 39049.413 | 136 | 0 |  | 2220 | 2459 | 137.79 | 0.06105 | 8.3028 | 0 | 1.3779 | 0.0006105 | 0.083028 | 0 | 1.3773 | 0.083028 | 13.4037 | 1781.8971 | 28536.5309
39049.4135 | 2050 | 1 | 39049.4135 | 154 | 0 |  | 2261.5 | 2500.5 | 125.1526 | 0.06105 | 9.4017 | 0 | 1.2515 | 0.0006105 | 0.094017 | 0 | 1.2509 | 0.094017 | 24.8607 | 1561.9351 | 47779.0357
39049.414 | 2318 | 1 | 39049.414 | 119 | 0 |  | 2303.5 | 2542.5 | 141.514 | 0.06105 | 7.265 | 0 | 1.4151 | 0.0006105 | 0.07265 | 0 | 1.4145 | 0.07265 | 10.418 | 2050.7395 | 22920.3379
39049.4145 | 2399 | 1 | 39049.4145 | 82 | 0 |  | 2346 | 2585 | 146.4591 | 0.06105 | 5.0061 | 0 | 1.4646 | 0.0006105 | 0.050061 | 0 | 1.464 | 0.050061 | 6.6882 | 3021.1951 | 15427.3623
39049.415 | 2381 | 1 | 39049.415 | 114 | 0 |  | 2387.5 | 2626.5 | 145.3602 | 0.06105 | 6.9597 | 0 | 1.4536 | 0.0006105 | 0.069597 | 0 | 1.453 | 0.069597 | 7.4951 | 2145.0702 | 16947.9133
39049.4155 | 2225 | 1 | 39049.4155 | 73 | 0 |  | 2429.5 | 2668.5 | 135.8364 | 0.06105 | 4.4567 | 0 | 1.3584 | 0.0006105 | 0.044567 | 0 | 1.3578 | 0.044567 | 15.0353 | 3406 | 32387.1158
39049.4159 | 2368 | 1 | 39049.4159 | 71 | 0 |  | 2471.5 | 2710.5 | 144.5665 | 0.06105 | 4.3346 | 0 | 1.4457 | 0.0006105 | 0.043346 | 0 | 1.4451 | 0.043346 | 8.0854 | 3504.7606 | 18509.8651
39049.4164 | 1927 | 1 | 39049.4164 | 55 | 0 |  | 2514 | 2753 | 117.6435 | 0.06105 | 3.3578 | 0 | 1.1764 | 0.0006105 | 0.033578 | 0 | 1.1758 | 0.033578 | 32.8342 | 4553.4182 | 61781.1909
39049.4169 | 1921 | 1 | 39049.4169 | 31 | 0 |  | 2556 | 2795 | 117.2772 | 0.06105 | 1.8926 | 0 | 1.1728 | 0.0006105 | 0.018926 | 0 | 1.1722 | 0.018926 | 33.2492 | 8156.0645 | 62965.9857
39049.4174 | 1905 | 1 | 39049.4174 | 41 | 0 |  | 2597.5 | 2836.5 | 116.3004 | 0.06105 | 2.5031 | 0 | 1.163 | 0.0006105 | 0.025031 | 0 | 1.1624 | 0.025031 | 34.369 | 6142.3902 | 64291.3176
39049.4179 | 1831 | 1 | 39049.4179 | 36 | 0 |  | 2639.5 | 2878.5 | 111.7827 | 0.06105 | 2.1978 | 0 | 1.1178 | 0.0006105 | 0.021978 | 0 | 1.1172 | 0.021978 | 39.8025 | 7009.3889 | 71714.8741
39049.4184 | 2338 | 1 | 39049.4184 | 25 | 0 |  | 2682 | 2921 | 142.735 | 0.06105 | 1.5263 | 0 | 1.4274 | 0.0006105 | 0.015263 | 0 | 1.4267 | 0.015263 | 9.4729 | 10137.52 | 21822.733
39049.4189 | 2419 | 1 | 39049.4189 | 19 | 0 |  | 2724 | 2963 | 147.6801 | 0.06105 | 1.16 | 0 | 1.4768 | 0.0006105 | 0.0116 | 0 | 1.4762 | 0.0116 | 5.8056 | 13370.4211 | 13834.5288
39049.4193 | 2182 | 1 | 39049.4194 | 17 | 0 |  | 2765.5 | 3004.5 | 133.2112 | 0.06105 | 1.0379 | 0 | 1.3321 | 0.0006105 | 0.010379 | 0 | 1.3315 | 0.010379 | 17.3031 | 14955.1765 | 37387.9996
39049.4198 | 2422 | 1 | 39049.4198 | 18 | 0 |  | 2807.5 | 3046.5 | 147.8632 | 0.06105 | 1.0989 | 0 | 1.4786 | 0.0006105 | 0.010989 | 0 | 1.478 | 0.010989 | 5.6745 | 14118.7778 | 13542.0846
39049.4203 | 2543 | 1 | 39049.4203 | 4 | 0 |  | 2849.5 | 3088.5 | 155.2503 | 0.06105 | 0.2442 | 0 | 1.5525 | 0.0006105 | 0.002442 | 0 | 1.5519 | 0.002442 | 0.64437 | 63884.5 | 1535.5963
39049.4208 | 2469 | 1 | 39049.4208 | 2 | 0 |  | 2892 | 3131 | 150.7326 | 0.06105 | 0.1221 | 0 | 1.5073 | 0.0006105 | 0.001221 | 0 | 1.5067 | 0.001221 | 3.6621 | 127869 | 8931.0155
39049.4213 | 2329 | 1 | 39049.4213 | 2 | 0 |  | 2934 | 3173 | 142.1856 | 0.06105 | 0.1221 | 0 | 1.4219 | 0.0006105 | 0.001221 | 0 | 1.4212 | 0.001221 | 9.8961 | 127869.0001 | 22920.0753
39049.4218 | 2249 | 1 | 39049.4218 | 2 | 0 |  | 2975.5 | 3214.5 | 137.3016 | 0.06105 | 0.1221 | 0 | 1.373 | 0.0006105 | 0.001221 | 0 | 1.3724 | 0.001221 | 13.8069 | 127869 | 30913.8238

## A2-C5
Open Burn Test 13 |  |  | 2006-11-28 | 9:21 |  |  | Vs = |  | 153.8694 |  | R = | 100
Mixed | 7-C | Tray F | IRMS | 1
0 | 150 kW |  | Bundle | Ch. 2 & 5 | Cable A | Even - | Cable C |  | Odd
Time-15 | N11 | N12 | Time-16 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R5-G | R2-5
39049.3848 | 1 | 0 | 39049.3848 | 1 | 0 |  | -218.5 | 20.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
39049.3853 | 1 | 0 | 39049.3853 | 1 | 0 |  | -176.5 | 62.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
39049.3858 | 1 | 0 | 39049.3858 | 1 | 0 |  | -134.5 | 104.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
39049.3863 | 1 | 0 | 39049.3863 | 1 | 0 |  | -92.5 | 146.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
39049.3867 | 1 | 0 | 39049.3868 | 1 | 0 |  | -50.5 | 188.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
39049.3872 | 1 | 0 | 39049.3872 | 1 | 0 |  | -8.5 | 230.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
39049.3877 | 1 | 0 | 39049.3877 | 1 | 0 |  | 33.5 | 272.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
39049.3882 | 1 | 0 | 39049.3882 | 1 | 0 |  | 75.5 | 314.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
39049.3887 | 1 | 0 | 39049.3887 | 1 | 0 |  | 117.5 | 356.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
39049.3892 | 1 | 0 | 39049.3892 | 1 | 0 |  | 159.5 | 398.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
39049.3897 | 1 | 0 | 39049.3897 | 1 | 0 |  | 201.5 | 440.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
39049.3902 | 1 | 0 | 39049.3902 | 1 | 0 |  | 243.5 | 482.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
39049.3906 | 1 | 0 | 39049.3906 | 1 | 0 |  | 285.5 | 524.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
39049.3911 | 1 | 0 | 39049.3911 | 1 | 0 |  | 327.5 | 566.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
39049.3916 | 1 | 0 | 39049.3916 | 1 | 0 |  | 369.5 | 608.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
39049.3921 | 1 | 0 | 39049.3921 | 1 | 0 |  | 411.5 | 650.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
39049.3926 | 1 | 0 | 39049.3926 | 1 | 0 |  | 453.5 | 692.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
39049.3931 | 1 | 0 | 39049.3931 | 1 | 0 |  | 495.5 | 734.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
39049.3936 | 1 | 0 | 39049.3936 | 1 | 0 |  | 537.5 | 776.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
39049.394 | 1 | 0 | 39049.3941 | 1 | 0 |  | 579.5 | 818.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
39049.3945 | 1 | 0 | 39049.3945 | 1 | 0 |  | 621.5 | 860.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
39049.395 | 1 | 0 | 39049.395 | 1 | 0 |  | 663.5 | 902.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
39049.3955 | 1 | 0 | 39049.3955 | 1 | 0 |  | 705.5 | 944.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
39049.396 | 1 | 0 | 39049.396 | 1 | 0 |  | 747.5 | 986.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
39049.3965 | 1 | 0 | 39049.3965 | 1 | 0 |  | 789.5 | 1028.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
39049.397 | 1 | 0 | 39049.397 | 1 | 0 |  | 831.5 | 1070.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
39049.3974 | 1 | 0 | 39049.3975 | 1 | 0 |  | 873.5 | 1112.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
39049.3979 | 1 | 0 | 39049.3979 | 1 | 0 |  | 915.5 | 1154.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
39049.3984 | 1 | 0 | 39049.3984 | 1 | 0 |  | 957 | 1196 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
39049.3989 | 1 | 0 | 39049.3989 | 1 | 0 |  | 999.5 | 1238.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
39049.3994 | 1 | 0 | 39049.3994 | 1 | 0 |  | 1041 | 1280 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
39049.3999 | 1 | 0 | 39049.3999 | 1 | 0 |  | 1083.5 | 1322.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
39049.4004 | 1 | 0 | 39049.4004 | 1 | 0 |  | 1125.5 | 1364.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
39049.4008 | 1 | 0 | 39049.4009 | 1 | 0 |  | 1167.5 | 1406.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
39049.4013 | 1 | 0 | 39049.4013 | 1 | 0 |  | 1209 | 1448 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
39049.4018 | 1711 | 1 | 39049.4018 | 1 | 0 |  | 1251.5 | 1490.5 | 104.4567 | 0.06105 | 0.06105 | 0 | 1.0446 | 0.0006105 | 0.0006105 | 0 | 1.044 | 0.0006105 | 47.3322 | 251937.9999 | 80805.9263
39049.4023 | 677 | 1 | 39049.4023 | 1 | 0 |  | 1293 | 1532 | 41.3309 | 0.06105 | 0.06105 | 0 | 0.41331 | 0.0006105 | 0.0006105 | 0 | 0.4127 | 0.0006105 | 272.6895 | 251938 | 184164.9007
39049.4028 | 2312 | 1 | 39049.4028 | 1 | 0 |  | 1335 | 1574 | 141.1477 | 0.06105 | 0.06105 | 0 | 1.4115 | 0.0006105 | 0.0006105 | 0 | 1.4109 | 0.0006105 | 9.0169 | 251937.9999 | 20729.7719
39049.4033 | 2415 | 1 | 39049.4033 | 1 | 0 |  | 1377 | 1616 | 147.4359 | 0.06105 | 0.06105 | 0 | 1.4744 | 0.0006105 | 0.0006105 | 0 | 1.4737 | 0.0006105 | 4.3654 | 251937.9999 | 10433.8586
39049.4038 | 1922 | 1 | 39049.4038 | 1 | 0 |  | 1419.5 | 1658.5 | 117.3382 | 0.06105 | 0.06105 | 0 | 1.1734 | 0.0006105 | 0.0006105 | 0 | 1.1728 | 0.0006105 | 31.1494 | 251938.0001 | 59714.298
39049.4042 | 2128 | 1 | 39049.4043 | 1 | 0 |  | 1461.5 | 1700.5 | 129.9145 | 0.06105 | 0.06105 | 0 | 1.2991 | 0.0006105 | 0.0006105 | 0 | 1.2985 | 0.0006105 | 18.4476 | 251938.0001 | 39122.4714
39049.4047 | 1886 | 1 | 39049.4047 | 1 | 0 |  | 1503 | 1742 | 115.1404 | 0.06105 | 0.06105 | 0 | 1.1514 | 0.0006105 | 0.0006105 | 0 | 1.1508 | 0.0006105 | 33.6541 | 251938.0003 | 63312.8697
39049.4052 | 1870 | 1 | 39049.4052 | 1 | 0 |  | 1545 | 1784 | 114.1636 | 0.06105 | 0.06105 | 0 | 1.1416 | 0.0006105 | 0.0006105 | 0 | 1.141 | 0.0006105 | 34.7983 | 251938.0001 | 64912.2348
39049.4057 | 1893 | 1 | 39049.4057 | 1 | 0 |  | 1587 | 1826 | 115.5678 | 0.06105 | 0.06105 | 0 | 1.1557 | 0.0006105 | 0.0006105 | 0 | 1.1551 | 0.0006105 | 33.1596 | 251938.0001 | 62613.1474
39049.4062 | 2189 | 1 | 39049.4062 | 1 | 0 |  | 1629 | 1868 | 133.6386 | 0.06105 | 0.06105 | 0 | 1.3364 | 0.0006105 | 0.0006105 | 0 | 1.3358 | 0.0006105 | 15.1453 | 251938.0001 | 33024.8917
39049.4067 | 1856 | 1 | 39049.4067 | 1 | 0 |  | 1671 | 1910 | 113.3089 | 0.06105 | 0.06105 | 0 | 1.1331 | 0.0006105 | 0.0006105 | 0 | 1.1325 | 0.0006105 | 35.8156 | 251937.9999 | 66311.6794
39049.4072 | 2219 | 1 | 39049.4072 | 1 | 0 |  | 1713 | 1952 | 135.4701 | 0.06105 | 0.06105 | 0 | 1.3547 | 0.0006105 | 0.0006105 | 0 | 1.3541 | 0.0006105 | 13.5879 | 251938.0001 | 30026.082
39049.4076 | 2449 | 1 | 39049.4077 | 1 | 0 |  | 1755 | 1994 | 149.5116 | 0.06105 | 0.06105 | 0 | 1.4951 | 0.0006105 | 0.0006105 | 0 | 1.4945 | 0.0006105 | 2.9159 | 251937.9999 | 7035.2076
39049.4081 | 2221 | 1 | 39049.4081 | 1 | 0 |  | 1797 | 2036 | 135.5922 | 0.06105 | 0.06105 | 0 | 1.3559 | 0.0006105 | 0.0006105 | 0 | 1.3553 | 0.0006105 | 13.4856 | 251938.0003 | 29826.1613
39049.4086 | 2362 | 1 | 39049.4086 | 1 | 0 |  | 1839 | 2078 | 144.2002 | 0.06105 | 0.06105 | 0 | 1.442 | 0.0006105 | 0.0006105 | 0 | 1.4414 | 0.0006105 | 6.7082 | 251938.0001 | 15731.7557
39049.4091 | 2177 | 1 | 39049.4091 | 1 | 0 |  | 1881 | 2120 | 132.906 | 0.06105 | 0.06105 | 0 | 1.3291 | 0.0006105 | 0.0006105 | 0 | 1.3284 | 0.0006105 | 15.7803 | 251938.0001 | 34224.4155
39049.4096 | 2053 | 1 | 39049.4096 | 1 | 0 |  | 1923 | 2162 | 125.3358 | 0.06105 | 0.06105 | 0 | 1.2534 | 0.0006105 | 0.0006105 | 0 | 1.2527 | 0.0006105 | 22.7768 | 251938.0001 | 46619.4956
39049.4101 | 2246 | 1 | 39049.4101 | 1 | 0 |  | 1965 | 2204 | 137.1184 | 0.06105 | 0.06105 | 0 | 1.3712 | 0.0006105 | 0.0006105 | 0 | 1.3706 | 0.0006105 | 12.2218 | 251938.0001 | 27327.1532
39049.4106 | 2405 | 1 | 39049.4106 | 1 | 0 |  | 2007 | 2246 | 146.8254 | 0.06105 | 0.06105 | 0 | 1.4683 | 0.0006105 | 0.0006105 | 0 | 1.4676 | 0.0006105 | 4.7995 | 251938.0001 | 11433.4618
39049.411 | 2069 | 1 | 39049.4111 | 1 | 0 |  | 2049 | 2288 | 126.3126 | 0.06105 | 0.06105 | 0 | 1.2631 | 0.0006105 | 0.0006105 | 0 | 1.2625 | 0.0006105 | 21.8269 | 251938.0001 | 45020.1305
39049.4115 | 2076 | 1 | 39049.4116 | 1 | 0 |  | 2091 | 2330 | 126.7399 | 0.06105 | 0.06105 | 0 | 1.2674 | 0.0006105 | 0.0006105 | 0 | 1.2668 | 0.0006105 | 21.4159 | 251937.9999 | 44320.4082
39049.412 | 2018 | 1 | 39049.412 | 1 | 0 |  | 2133 | 2372 | 123.199 | 0.06105 | 0.06105 | 0 | 1.232 | 0.0006105 | 0.0006105 | 0 | 1.2314 | 0.0006105 | 24.9073 | 251938.0001 | 50118.107
39049.4125 | 2180 | 1 | 39049.4125 | 11 | 0 |  | 2175 | 2414 | 133.0891 | 0.06105 | 0.67155 | 0 | 1.3309 | 0.0006105 | 0.0067155 | 0 | 1.3303 | 0.0067155 | 15.621 | 22812.5455 | 33789.8803
39049.413 | 1929 | 1 | 39049.413 | 25 | 0 |  | 2217 | 2456 | 117.7656 | 0.06105 | 1.5263 | 0 | 1.1777 | 0.0006105 | 0.015263 | 0 | 1.177 | 0.015263 | 30.6734 | 9981.52 | 58452.3939
39049.4135 | 2366 | 1 | 39049.4135 | 25 | 0 |  | 2259 | 2498 | 144.4444 | 0.06105 | 1.5263 | 0 | 1.4444 | 0.0006105 | 0.015263 | 0 | 1.4438 | 0.015263 | 6.5277 | 9981.52 | 15185.8602
39049.414 | 2378 | 1 | 39049.414 | 40 | 0 |  | 2301 | 2540 | 145.177 | 0.06105 | 2.442 | 0 | 1.4518 | 0.0006105 | 0.02442 | 0 | 1.4512 | 0.02442 | 5.9899 | 6200.95 | 13913.6211
39049.4144 | 1921 | 1 | 39049.4145 | 28 | 0 |  | 2343 | 2582 | 117.2772 | 0.06105 | 1.7094 | 0 | 1.1728 | 0.0006105 | 0.017094 | 0 | 1.1722 | 0.017094 | 31.2179 | 8901.3571 | 59173.2336
39049.4149 | 2290 | 1 | 39049.415 | 17 | 0 |  | 2385 | 2624 | 139.8046 | 0.06105 | 1.0379 | 0 | 1.398 | 0.0006105 | 0.010379 | 0 | 1.3974 | 0.010379 | 10.0647 | 14725.7647 | 22783.2829
39049.4154 | 2354 | 1 | 39049.4154 | 17 | 0 |  | 2427 | 2666 | 143.7118 | 0.06105 | 1.0379 | 0 | 1.4371 | 0.0006105 | 0.010379 | 0 | 1.4365 | 0.010379 | 7.071 | 14725.7647 | 16426.4509
39049.4159 | 1854 | 1 | 39049.4159 | 17 | 0 |  | 2469 | 2708 | 113.1868 | 0.06105 | 1.0379 | 0 | 1.1319 | 0.0006105 | 0.010379 | 0 | 1.1313 | 0.010379 | 35.9624 | 14725.7647 | 66089.2002
39049.4164 | 2034 | 1 | 39049.4164 | 18 | 0 |  | 2511 | 2750 | 124.1758 | 0.06105 | 1.0989 | 0 | 1.2418 | 0.0006105 | 0.010989 | 0 | 1.2411 | 0.010989 | 23.9243 | 13902.1111 | 48191.3523
39049.4169 | 2342 | 1 | 39049.4169 | 12 | 0 |  | 2553 | 2792 | 142.9792 | 0.06105 | 0.7326 | 0 | 1.4298 | 0.0006105 | 0.007326 | 0 | 1.4292 | 0.007326 | 7.6198 | 20903.1667 | 17653.5461
39049.4174 | 1841 | 1 | 39049.4174 | 24 | 0 |  | 2595 | 2834 | 112.3932 | 0.06105 | 1.4652 | 0 | 1.1239 | 0.0006105 | 0.014652 | 0 | 1.1233 | 0.014652 | 36.923 | 10401.5833 | 67192.0212
39049.4178 | 2143 | 1 | 39049.4179 | 30 | 0 |  | 2637 | 2876 | 130.8303 | 0.06105 | 1.8315 | 0 | 1.3083 | 0.0006105 | 0.018315 | 0 | 1.3077 | 0.018315 | 17.6182 | 8301.2667 | 37189.9961
39049.4183 | 2363 | 1 | 39049.4184 | 21 | 0 |  | 2679 | 2918 | 144.2613 | 0.06105 | 1.2821 | 0 | 1.4426 | 0.0006105 | 0.012821 | 0 | 1.442 | 0.012821 | 6.663 | 11901.8095 | 15507.703
39049.4188 | 1977 | 1 | 39049.4188 | 15 | 0 |  | 2721 | 2960 | 120.696 | 0.06105 | 0.91575 | 0 | 1.207 | 0.0006105 | 0.0091575 | 0 | 1.2063 | 0.0091575 | 27.4991 | 16702.5333 | 53915.2034
39049.4193 | 2282 | 1 | 39049.4193 | 17 | 0 |  | 2763 | 3002 | 139.3162 | 0.06105 | 1.0379 | 0 | 1.3932 | 0.0006105 | 0.010379 | 0 | 1.3926 | 0.010379 | 10.4507 | 14725.7647 | 23577.8868
39049.4198 | 2348 | 1 | 39049.4198 | 13 | 0 |  | 2805 | 3044 | 143.3455 | 0.06105 | 0.79365 | 0 | 1.4335 | 0.0006105 | 0.0079365 | 0 | 1.4328 | 0.0079365 | 7.3447 | 19287.5385 | 17049.603
39049.4203 | 2504 | 1 | 39049.4203 | 12 | 0 |  | 2847 | 3086 | 152.8694 | 0.06105 | 0.7326 | 0 | 1.5287 | 0.0006105 | 0.007326 | 0 | 1.5281 | 0.007326 | 0.65442 | 20903.1667 | 1530.6773
39049.4208 | 2137 | 1 | 39049.4208 | 9 | 0 |  | 2889 | 3128 | 130.464 | 0.06105 | 0.54945 | 0 | 1.3046 | 0.0006105 | 0.0054945 | 0 | 1.304 | 0.0054945 | 17.9485 | 27904.2222 | 38101.4563
39049.4212 | 2285 | 1 | 39049.4213 | 8 | 0 |  | 2931 | 3170 | 139.4994 | 0.06105 | 0.4884 | 0 | 1.395 | 0.0006105 | 0.004884 | 0 | 1.3944 | 0.004884 | 10.3056 | 31404.75 | 23363.6049
39049.4217 | 2398 | 1 | 39049.4218 | 5 | 0 |  | 2973 | 3212 | 146.398 | 0.06105 | 0.30525 | 0 | 1.464 | 0.0006105 | 0.0030525 | 0 | 1.4634 | 0.0030525 | 5.1056 | 50307.6 | 12113.9203

## A2-B4
Open Burn Test 13 |  |  | 2006-11-28 | 9:21 |  |  | Vs = |  | 156.5556 |  | R = | 100
Mixed | 7-C | Tray F | IRMS | 1
0 | 150 kW |  | Bundle | Ch. 2 & 4 | Cable A | Even - | Cable B |  | Even
Time-13 | N11 | N12 | Time-14 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R4-G | R2-4
39049.3848 | 1 | 0 | 39049.3848 | 1 | 0 |  | -221.5 | 17.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
39049.3853 | 1 | 0 | 39049.3853 | 1 | 0 |  | -179.5 | 59.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
39049.3857 | 1 | 0 | 39049.3858 | 1 | 0 |  | -137.5 | 101.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
39049.3862 | 1 | 0 | 39049.3862 | 1 | 0 |  | -95.5 | 143.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
39049.3867 | 1 | 0 | 39049.3867 | 1 | 0 |  | -53.5 | 185.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
39049.3872 | 1 | 0 | 39049.3872 | 1 | 0 |  | -11.5 | 227.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
39049.3877 | 1 | 0 | 39049.3877 | 1 | 0 |  | 30.5 | 269.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
39049.3882 | 1 | 0 | 39049.3882 | 1 | 0 |  | 72.5 | 311.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
39049.3887 | 1 | 0 | 39049.3887 | 1 | 0 |  | 114.5 | 353.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
39049.3891 | 1 | 0 | 39049.3892 | 1 | 0 |  | 156.5 | 395.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
39049.3896 | 1 | 0 | 39049.3896 | 1 | 0 |  | 198.5 | 437.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
39049.3901 | 1 | 0 | 39049.3901 | 1 | 0 |  | 240.5 | 479.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
39049.3906 | 1 | 0 | 39049.3906 | 1 | 0 |  | 282.5 | 521.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
39049.3911 | 1 | 0 | 39049.3911 | 1 | 0 |  | 324.5 | 563.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
39049.3916 | 1 | 0 | 39049.3916 | 1 | 0 |  | 366.5 | 605.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
39049.3921 | 1 | 0 | 39049.3921 | 1 | 0 |  | 408.5 | 647.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
39049.3925 | 1 | 0 | 39049.3926 | 1 | 0 |  | 450.5 | 689.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
39049.393 | 1 | 0 | 39049.393 | 1 | 0 |  | 492.5 | 731.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
39049.3935 | 1 | 0 | 39049.3935 | 1 | 0 |  | 534.5 | 773.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
39049.394 | 1 | 0 | 39049.394 | 1 | 0 |  | 576.5 | 815.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
39049.3945 | 1 | 0 | 39049.3945 | 1 | 0 |  | 618.5 | 857.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
39049.395 | 1 | 0 | 39049.395 | 1 | 0 |  | 660.5 | 899.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
39049.3955 | 1 | 0 | 39049.3955 | 1 | 0 |  | 702.5 | 941.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
39049.3959 | 1 | 0 | 39049.396 | 1 | 0 |  | 744.5 | 983.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
39049.3964 | 1 | 0 | 39049.3964 | 1 | 0 |  | 786.5 | 1025.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
39049.3969 | 1 | 0 | 39049.3969 | 1 | 0 |  | 828.5 | 1067.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
39049.3974 | 1 | 0 | 39049.3974 | 1 | 0 |  | 870.5 | 1109.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
39049.3979 | 1 | 0 | 39049.3979 | 1 | 0 |  | 912.5 | 1151.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
39049.3984 | 1 | 0 | 39049.3984 | 1 | 0 |  | 954.5 | 1193.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
39049.3989 | 1 | 0 | 39049.3989 | 1 | 0 |  | 996.5 | 1235.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
39049.3994 | 1 | 0 | 39049.3994 | 1 | 0 |  | 1038.5 | 1277.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
39049.3998 | 1 | 0 | 39049.3998 | 1 | 0 |  | 1080.5 | 1319.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
39049.4003 | 1 | 0 | 39049.4003 | 1 | 0 |  | 1122.5 | 1361.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
39049.4008 | 1 | 0 | 39049.4008 | 1 | 0 |  | 1164.5 | 1403.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
39049.4013 | 1 | 0 | 39049.4013 | 1 | 0 |  | 1206.5 | 1445.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
39049.4018 | 32 | 0 | 39049.4018 | 1739 | 0 |  | 1248.5 | 1487.5 | 1.9536 | 0 | 106.1661 | 0 | 0.019536 | 0 | 1.0617 | 0 | 0.019536 | 1.0617 | 7913.6875 | 47.4629 | 7913.668
39049.4023 | 258 | 0 | 39049.4023 | 289 | 0 |  | 1290.5 | 1529.5 | 15.7509 | 0 | 17.6435 | 0 | 0.15751 | 0 | 0.17643 | 0 | 0.15751 | 0.17643 | 893.9457 | 787.3287 | 893.7882
39049.4028 | 1997 | 0 | 39049.4028 | 2101 | 0 |  | 1332.5 | 1571.5 | 121.917 | 0 | 128.2662 | 0 | 1.2192 | 0 | 1.2827 | 0 | 1.2192 | 1.2827 | 28.4116 | 22.0552 | 27.1924
39049.4032 | 2195 | 0 | 39049.4033 | 2060 | 0 |  | 1374.5 | 1613.5 | 134.0049 | 0 | 125.7631 | 0 | 1.34 | 0 | 1.2576 | 0 | 1.34 | 1.2576 | 16.8282 | 24.4845 | 15.4882
39049.4037 | 2072 | 0 | 39049.4037 | 2480 | 0 |  | 1416.5 | 1655.5 | 126.4957 | 0 | 151.4042 | 0 | 1.265 | 0 | 1.514 | 0 | 1.265 | 1.514 | 23.7635 | 3.4024 | 22.4986
39049.4042 | 2492 | 0 | 39049.4042 | 2017 | 0 |  | 1458.5 | 1697.5 | 152.1368 | 0 | 123.138 | 0 | 1.5214 | 0 | 1.2314 | 0 | 1.5214 | 1.2314 | 2.9045 | 27.1383 | 1.3831
39049.4047 | 2248 | 0 | 39049.4047 | 2336 | 0 |  | 1500.5 | 1739.5 | 137.2405 | 0 | 142.6129 | 0 | 1.3724 | 0 | 1.4261 | 0 | 1.3724 | 1.4261 | 14.0738 | 9.7765 | 12.7014
39049.4052 | 1888 | 0 | 39049.4052 | 2364 | 0 |  | 1542.5 | 1781.5 | 115.2625 | 0 | 144.3223 | 0 | 1.1526 | 0 | 1.4432 | 0 | 1.1526 | 1.4432 | 35.8252 | 8.4763 | 34.6726
39049.4057 | 1900 | 0 | 39049.4057 | 2026 | 0 |  | 1584.5 | 1823.5 | 115.9951 | 0 | 123.6874 | 0 | 1.16 | 0 | 1.2369 | 0 | 1.16 | 1.2369 | 34.9674 | 26.5735 | 33.8074
39049.4062 | 2002 | 0 | 39049.4062 | 2106 | 0 |  | 1626.5 | 1865.5 | 122.2222 | 0 | 128.5714 | 0 | 1.2222 | 0 | 1.2857 | 0 | 1.2222 | 1.2857 | 28.0909 | 21.7654 | 26.8687
39049.4066 | 1930 | 0 | 39049.4067 | 1947 | 0 |  | 1668.5 | 1907.5 | 117.8266 | 0 | 118.8645 | 0 | 1.1783 | 0 | 1.1886 | 0 | 1.1783 | 1.1886 | 32.8694 | 31.7093 | 31.6912
39049.4071 | 2153 | 0 | 39049.4071 | 2008 | 0 |  | 1710.5 | 1949.5 | 131.4408 | 0 | 122.5885 | 0 | 1.3144 | 0 | 1.2259 | 0 | 1.3144 | 1.2259 | 19.1073 | 27.7082 | 17.7929
39049.4076 | 2328 | 0 | 39049.4076 | 2170 | 0 |  | 1752.5 | 1991.5 | 142.1245 | 0 | 132.4786 | 0 | 1.4212 | 0 | 1.3248 | 0 | 1.4212 | 1.3248 | 10.1538 | 18.1742 | 8.7325
39049.4081 | 1916 | 0 | 39049.4081 | 1955 | 0 |  | 1794.5 | 2033.5 | 116.9719 | 0 | 119.3529 | 0 | 1.1697 | 0 | 1.1935 | 0 | 1.1697 | 1.1935 | 33.8403 | 31.1703 | 32.6706
39049.4086 | 2334 | 0 | 39049.4086 | 2314 | 0 |  | 1836.5 | 2075.5 | 142.4908 | 0 | 141.2698 | 0 | 1.4249 | 0 | 1.4127 | 0 | 1.4249 | 1.4127 | 9.8706 | 10.8202 | 8.4457
39049.4091 | 2132 | 0 | 39049.4091 | 2065 | 0 |  | 1878.5 | 2117.5 | 130.1587 | 0 | 126.0684 | 0 | 1.3016 | 0 | 1.2607 | 0 | 1.3016 | 1.2607 | 20.2805 | 24.1831 | 18.9789
39049.4096 | 2457 | 0 | 39049.4096 | 1961 | 0 |  | 1920.5 | 2159.5 | 150 | 0 | 119.7192 | 0 | 1.5 | 0 | 1.1972 | 0 | 1.5 | 1.1972 | 4.3704 | 30.769 | 2.8704
39049.41 | 1956 | 0 | 39049.4101 | 2257 | 0 |  | 1962.5 | 2201.5 | 119.4139 | 0 | 137.79 | 0 | 1.1941 | 0 | 1.3779 | 0 | 1.1941 | 1.3779 | 31.1033 | 13.619 | 29.9091
39049.4105 | 2464 | 0 | 39049.4105 | 2383 | 0 |  | 2004.5 | 2243.5 | 150.4274 | 0 | 145.4823 | 0 | 1.5043 | 0 | 1.4548 | 0 | 1.5043 | 1.4548 | 4.0739 | 7.6114 | 2.5696
39049.411 | 2386 | 0 | 39049.411 | 2483 | 0 |  | 2046.5 | 2285.5 | 145.6654 | 0 | 151.5873 | 0 | 1.4567 | 0 | 1.5159 | 0 | 1.4567 | 1.5159 | 7.4761 | 3.2775 | 6.0195
39049.4115 | 2048 | 0 | 39049.4115 | 2339 | 0 |  | 2088.5 | 2327.5 | 125.0305 | 0 | 142.7961 | 0 | 1.2503 | 0 | 1.428 | 0 | 1.2503 | 1.428 | 25.2139 | 9.6357 | 23.9636
39049.412 | 2377 | 0 | 39049.412 | 2261 | 0 |  | 2130.5 | 2369.5 | 145.116 | 0 | 138.0342 | 0 | 1.4512 | 0 | 1.3803 | 0 | 1.4512 | 1.3803 | 7.883 | 13.418 | 6.4319
39049.4125 | 1981 | 0 | 39049.4125 | 2102 | 0 |  | 2172.5 | 2411.5 | 120.9402 | 0 | 128.3272 | 0 | 1.2094 | 0 | 1.2833 | 0 | 1.2094 | 1.2833 | 29.4488 | 21.9971 | 28.2394
39049.413 | 1999 | 0 | 39049.413 | 2129 | 0 |  | 2214.5 | 2453.5 | 122.0391 | 0 | 129.9756 | 0 | 1.2204 | 0 | 1.2998 | 0 | 1.2204 | 1.2998 | 28.2831 | 20.45 | 27.0628
39049.4134 | 2402 | 0 | 39049.4135 | 2151 | 0 |  | 2256.5 | 2495.5 | 146.6422 | 0 | 131.3187 | 0 | 1.4664 | 0 | 1.3132 | 0 | 1.4664 | 1.3132 | 6.7602 | 19.218 | 5.2938
39049.4139 | 2097 | 0 | 39049.4139 | 2403 | 0 |  | 2298.5 | 2537.5 | 128.022 | 0 | 146.7033 | 0 | 1.2802 | 0 | 1.467 | 0 | 1.2802 | 1.467 | 22.288 | 6.7158 | 21.0078
39049.4144 | 2270 | 0 | 39049.4144 | 2228 | 0 |  | 2340 | 2579 | 138.5836 | 0 | 136.0195 | 0 | 1.3858 | 0 | 1.3602 | 0 | 1.3858 | 1.3602 | 12.9683 | 15.0978 | 11.5824
39049.4149 | 2117 | 0 | 39049.4149 | 2246 | 0 |  | 2382.5 | 2621.5 | 129.243 | 0 | 137.1184 | 0 | 1.2924 | 0 | 1.3712 | 0 | 1.2924 | 1.3712 | 21.1327 | 14.1754 | 19.8403
39049.4154 | 2275 | 0 | 39049.4154 | 2231 | 0 |  | 2424.5 | 2663.5 | 138.8889 | 0 | 136.2027 | 0 | 1.3889 | 0 | 1.362 | 0 | 1.3889 | 1.362 | 12.72 | 14.9431 | 11.3311
39049.4159 | 2299 | 0 | 39049.4159 | 2076 | 0 |  | 2466 | 2705 | 140.3541 | 0 | 126.7399 | 0 | 1.4035 | 0 | 1.2674 | 0 | 1.4035 | 1.2674 | 11.5433 | 23.525 | 10.1397
39049.4164 | 2307 | 0 | 39049.4164 | 1817 | 0 |  | 2508 | 2747 | 140.8425 | 0 | 110.928 | 0 | 1.4084 | 0 | 1.1093 | 0 | 1.4084 | 1.1093 | 11.1565 | 41.1326 | 9.7481
39049.4169 | 2068 | 0 | 39049.4169 | 1893 | 0 |  | 2550.5 | 2789.5 | 126.2515 | 0 | 115.5678 | 0 | 1.2625 | 0 | 1.1557 | 0 | 1.2625 | 1.1557 | 24.0029 | 35.4665 | 22.7404
39049.4173 | 2088 | 0 | 39049.4173 | 2202 | 0 |  | 2592 | 2831 | 127.4725 | 0 | 134.4322 | 0 | 1.2747 | 0 | 1.3443 | 0 | 1.2747 | 1.3443 | 22.8151 | 16.4569 | 21.5404
39049.4178 | 1811 | 0 | 39049.4178 | 2284 | 0 |  | 2634 | 2873 | 110.5617 | 0 | 139.4383 | 0 | 1.1056 | 0 | 1.3944 | 0 | 1.1056 | 1.3944 | 41.6002 | 12.2758 | 40.4946
39049.4183 | 1961 | 0 | 39049.4183 | 2146 | 0 |  | 2676 | 2915 | 119.7192 | 0 | 131.0134 | 0 | 1.1972 | 0 | 1.3101 | 0 | 1.1972 | 1.3101 | 30.769 | 19.4958 | 29.5718
39049.4188 | 2525 | 0 | 39049.4188 | 2548 | 0 |  | 2718.5 | 2957.5 | 154.1514 | 0 | 155.5556 | 0 | 1.5415 | 0 | 1.5556 | 0 | 1.5415 | 1.5556 | 1.5596 | 0.64286 | 0.01809
39049.4193 | 2355 | 0 | 39049.4193 | 2510 | 0 |  | 2760 | 2999 | 143.7729 | 0 | 153.2357 | 0 | 1.4377 | 0 | 1.5324 | 0 | 1.4377 | 1.5324 | 8.8909 | 2.1665 | 7.4531
39049.4198 | 2300 | 0 | 39049.4198 | 2501 | 0 |  | 2802 | 3041 | 140.4151 | 0 | 152.6862 | 0 | 1.4042 | 0 | 1.5269 | 0 | 1.4042 | 1.5269 | 11.4948 | 2.5342 | 10.0906
39049.4202 | 2436 | 0 | 39049.4203 | 2290 | 0 |  | 2844 | 3083 | 148.7179 | 0 | 139.8046 | 0 | 1.4872 | 0 | 1.398 | 0 | 1.4872 | 1.398 | 5.2701 | 11.9817 | 3.7829
39049.4207 | 2248 | 0 | 39049.4208 | 2530 | 0 |  | 2886 | 3125 | 137.2405 | 0 | 154.4567 | 0 | 1.3724 | 0 | 1.5446 | 0 | 1.3724 | 1.5446 | 14.0738 | 1.3589 | 12.7014
39049.4212 | 2178 | 0 | 39049.4212 | 2065 | 0 |  | 2928 | 3167 | 132.967 | 0 | 126.0684 | 0 | 1.3297 | 0 | 1.2607 | 0 | 1.3297 | 1.2607 | 17.7401 | 24.1831 | 16.4105
39049.4217 | 2252 | 0 | 39049.4217 | 2280 | 0 |  | 2970 | 3209 | 137.4847 | 0 | 139.1941 | 0 | 1.3748 | 0 | 1.3919 | 0 | 1.3748 | 1.3919 | 13.8712 | 12.4728 | 12.4964

## A2-B3
Open Burn Test 13 |  |  | 2006-11-28 | 9:21 |  |  | Vs = |  | 157.8376 |  | R = | 100
Mixed | 7-C | Tray F | IRMS | 1
0 | 150 kW |  | Bundle | Ch. 2 & 3 | Cable A | Even - | Cable B |  | Odd
Time-11 | N11 | N12 | Time-12 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R3-G | R2-3
39049.3847 | 1 | 0 | 39049.3848 | 1 | 0 |  | -224 | 15 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
39049.3852 | 1 | 0 | 39049.3852 | 1 | 0 |  | -182.5 | 56.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
39049.3857 | 1 | 0 | 39049.3857 | 1 | 0 |  | -140 | 99 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
39049.3862 | 1 | 0 | 39049.3862 | 1 | 0 |  | -98.5 | 140.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
39049.3867 | 1 | 0 | 39049.3867 | 1 | 0 |  | -56 | 183 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
39049.3872 | 1 | 0 | 39049.3872 | 1 | 0 |  | -14.5 | 224.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
39049.3877 | 1 | 0 | 39049.3877 | 1 | 0 |  | 27.5 | 266.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
39049.3881 | 1 | 0 | 39049.3881 | 1 | 0 |  | 69.5 | 308.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
39049.3886 | 1 | 0 | 39049.3886 | 1 | 0 |  | 111.5 | 350.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
39049.3891 | 1 | 0 | 39049.3891 | 1 | 0 |  | 153.5 | 392.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
39049.3896 | 1 | 0 | 39049.3896 | 1 | 0 |  | 195.5 | 434.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
39049.3901 | 1 | 0 | 39049.3901 | 1 | 0 |  | 237.5 | 476.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
39049.3906 | 1 | 0 | 39049.3906 | 1 | 0 |  | 279.5 | 518.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
39049.3911 | 1 | 0 | 39049.3911 | 1 | 0 |  | 321.5 | 560.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
39049.3915 | 1 | 0 | 39049.3916 | 1 | 0 |  | 363.5 | 602.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
39049.392 | 1 | 0 | 39049.392 | 1 | 0 |  | 405.5 | 644.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
39049.3925 | 1 | 0 | 39049.3925 | 1 | 0 |  | 447.5 | 686.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
39049.393 | 1 | 0 | 39049.393 | 1 | 0 |  | 489.5 | 728.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
39049.3935 | 1 | 0 | 39049.3935 | 1 | 0 |  | 531.5 | 770.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
39049.394 | 1 | 0 | 39049.394 | 1 | 0 |  | 573.5 | 812.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
39049.3945 | 1 | 0 | 39049.3945 | 1 | 0 |  | 615.5 | 854.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
39049.3949 | 1 | 0 | 39049.395 | 1 | 0 |  | 657.5 | 896.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
39049.3954 | 1 | 0 | 39049.3954 | 1 | 0 |  | 699.5 | 938.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
39049.3959 | 1 | 0 | 39049.3959 | 1 | 0 |  | 741.5 | 980.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
39049.3964 | 1 | 0 | 39049.3964 | 1 | 0 |  | 783.5 | 1022.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
39049.3969 | 1 | 0 | 39049.3969 | 1 | 0 |  | 825.5 | 1064.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
39049.3974 | 1 | 0 | 39049.3974 | 1 | 0 |  | 867.5 | 1106.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
39049.3979 | 1 | 0 | 39049.3979 | 1 | 0 |  | 909.5 | 1148.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
39049.3983 | 1 | 0 | 39049.3984 | 1 | 0 |  | 951.5 | 1190.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
39049.3988 | 1 | 0 | 39049.3988 | 2036 | 0 |  | 993.5 | 1232.5 | 0.06105 | 0 | 124.2979 | 0 | 0.0006105 | 0 | 1.243 | 0 | 0.0006105 | 1.243 | 258438 | 26.9833 | 258437.9994
39049.3993 | 1 | 0 | 39049.3993 | 2030 | 0 |  | 1035.5 | 1274.5 | 0.06105 | 0 | 123.9316 | 0 | 0.0006105 | 0 | 1.2393 | 0 | 0.0006105 | 1.2393 | 258438 | 27.3586 | 258437.9994
39049.3998 | 1 | 0 | 39049.3998 | 2422 | 0 |  | 1077.5 | 1316.5 | 0.06105 | 0 | 147.8632 | 0 | 0.0006105 | 0 | 1.4786 | 0 | 0.0006105 | 1.4786 | 258438 | 6.7457 | 258437.9994
39049.4003 | 1 | 0 | 39049.4003 | 1898 | 0 |  | 1119.5 | 1358.5 | 0.06105 | 0 | 115.873 | 0 | 0.0006105 | 0 | 1.1587 | 0 | 0.0006105 | 1.1587 | 258438 | 36.216 | 258437.9994
39049.4008 | 1 | 0 | 39049.4008 | 2050 | 0 |  | 1161.5 | 1400.5 | 0.06105 | 0 | 125.1526 | 0 | 0.0006105 | 0 | 1.2515 | 0 | 0.0006105 | 1.2515 | 258438 | 26.1161 | 258437.9994
39049.4013 | 1 | 0 | 39049.4013 | 2386 | 0 |  | 1203.5 | 1442.5 | 0.06105 | 0 | 145.6654 | 0 | 0.0006105 | 0 | 1.4567 | 0 | 0.0006105 | 1.4567 | 258438 | 8.3562 | 258437.9994
39049.4017 | 1488 | 0 | 39049.4018 | 2384 | 0 |  | 1245.5 | 1484.5 | 90.8425 | 0 | 145.5433 | 0 | 0.90842 | 0 | 1.4554 | 0 | 0.90842 | 1.4554 | 73.7487 | 8.4471 | 72.8402
39049.4022 | 356 | 0 | 39049.4022 | 2337 | 0 |  | 1287.5 | 1526.5 | 21.7338 | 0 | 142.674 | 0 | 0.21734 | 0 | 1.4267 | 0 | 0.21734 | 1.4267 | 626.2303 | 10.6282 | 626.013
39049.4027 | 2259 | 0 | 39049.4027 | 1551 | 0 |  | 1329.5 | 1568.5 | 137.9121 | 0 | 94.6886 | 0 | 1.3791 | 0 | 0.94689 | 0 | 1.3791 | 0.94689 | 14.448 | 66.6912 | 13.0689
39049.4032 | 2115 | 0 | 39049.4032 | 1964 | 0 |  | 1371.5 | 1610.5 | 129.1209 | 0 | 119.9023 | 0 | 1.2912 | 0 | 1.199 | 0 | 1.2912 | 1.199 | 22.2402 | 31.6385 | 20.949
39049.4037 | 2324 | 0 | 39049.4037 | 1995 | 0 |  | 1413.5 | 1652.5 | 141.8803 | 0 | 121.7949 | 0 | 1.4188 | 0 | 1.2179 | 0 | 1.4188 | 1.2179 | 11.247 | 29.593 | 9.8282
39049.4042 | 1926 | 0 | 39049.4042 | 1967 | 0 |  | 1455.5 | 1694.5 | 117.5824 | 0 | 120.0855 | 0 | 1.1758 | 0 | 1.2009 | 0 | 1.1758 | 1.2009 | 34.2357 | 31.4377 | 33.0599
39049.4047 | 2018 | 0 | 39049.4047 | 2351 | 0 |  | 1497.5 | 1736.5 | 123.199 | 0 | 143.5287 | 0 | 1.232 | 0 | 1.4353 | 0 | 1.232 | 1.4353 | 28.116 | 9.9694 | 26.884
39049.4052 | 2104 | 0 | 39049.4052 | 2479 | 0 |  | 1539.5 | 1778.5 | 128.4493 | 0 | 151.3431 | 0 | 1.2845 | 0 | 1.5134 | 0 | 1.2845 | 1.5134 | 22.8793 | 4.2912 | 21.5948
39049.4056 | 2273 | 0 | 39049.4056 | 2244 | 0 |  | 1581.5 | 1820.5 | 138.7668 | 0 | 136.9963 | 0 | 1.3877 | 0 | 1.37 | 0 | 1.3877 | 1.37 | 13.7431 | 15.213 | 12.3554
39049.4061 | 2385 | 0 | 39049.4061 | 2434 | 0 |  | 1623.5 | 1862.5 | 145.6044 | 0 | 148.5958 | 0 | 1.456 | 0 | 1.486 | 0 | 1.456 | 1.486 | 8.4017 | 6.2194 | 6.9456
39049.4066 | 1980 | 0 | 39049.4066 | 2187 | 0 |  | 1665.5 | 1904.5 | 120.8791 | 0 | 133.5165 | 0 | 1.2088 | 0 | 1.3352 | 0 | 1.2088 | 1.3352 | 30.5747 | 18.2158 | 29.366
39049.4071 | 2355 | 0 | 39049.4071 | 2009 | 0 |  | 1707.5 | 1946.5 | 143.7729 | 0 | 122.6496 | 0 | 1.4377 | 0 | 1.2265 | 0 | 1.4377 | 1.2265 | 9.7826 | 28.6899 | 8.3449
39049.4076 | 2214 | 0 | 39049.4076 | 2092 | 0 |  | 1749.5 | 1988.5 | 135.1648 | 0 | 127.7167 | 0 | 1.3516 | 0 | 1.2772 | 0 | 1.3516 | 1.2772 | 16.7742 | 23.5841 | 15.4225
39049.4081 | 2281 | 0 | 39049.4081 | 2564 | 0 |  | 1791.5 | 2030.5 | 139.2552 | 0 | 156.5324 | 0 | 1.3926 | 0 | 1.5653 | 0 | 1.3926 | 1.5653 | 13.3441 | 0.83385 | 11.9516
39049.4086 | 2356 | 0 | 39049.4086 | 2386 | 0 |  | 1833.5 | 2072.5 | 143.8339 | 0 | 145.6654 | 0 | 1.4383 | 0 | 1.4567 | 0 | 1.4383 | 1.4567 | 9.736 | 8.3562 | 8.2977
39049.409 | 2366 | 0 | 39049.4091 | 2298 | 0 |  | 1875.5 | 2114.5 | 144.4444 | 0 | 140.293 | 0 | 1.4444 | 0 | 1.4029 | 0 | 1.4444 | 1.4029 | 9.2722 | 12.5057 | 7.8277
39049.4095 | 2183 | 0 | 39049.4095 | 2384 | 0 |  | 1917.5 | 2156.5 | 133.2723 | 0 | 145.5433 | 0 | 1.3327 | 0 | 1.4554 | 0 | 1.3327 | 1.4554 | 18.4324 | 8.4471 | 17.0997
39049.41 | 2491 | 0 | 39049.41 | 2569 | 0 |  | 1959.5 | 2198.5 | 152.0757 | 0 | 156.8376 | 0 | 1.5208 | 0 | 1.5684 | 0 | 1.5208 | 1.5684 | 3.7888 | 0.6376 | 2.2681
39049.4105 | 2084 | 0 | 39049.4105 | 2557 | 0 |  | 2001.5 | 2240.5 | 127.2283 | 0 | 156.105 | 0 | 1.2723 | 0 | 1.5611 | 0 | 1.2723 | 1.5611 | 24.0585 | 1.1099 | 22.7863
39049.411 | 2388 | 0 | 39049.411 | 2001 | 0 |  | 2043.5 | 2282.5 | 145.7875 | 0 | 122.1612 | 0 | 1.4579 | 0 | 1.2216 | 0 | 1.4579 | 1.2216 | 8.2655 | 29.2044 | 6.8076
39049.4115 | 2169 | 0 | 39049.4115 | 2047 | 0 |  | 2085.5 | 2324.5 | 132.4176 | 0 | 124.9695 | 0 | 1.3242 | 0 | 1.2497 | 0 | 1.3242 | 1.2497 | 19.1969 | 26.3009 | 17.8727
39049.412 | 1884 | 0 | 39049.412 | 2060 | 0 |  | 2127.5 | 2366.5 | 115.0183 | 0 | 125.7631 | 0 | 1.1502 | 0 | 1.2576 | 0 | 1.1502 | 1.2576 | 37.2282 | 25.5039 | 36.0781
39049.4124 | 2227 | 0 | 39049.4125 | 2398 | 0 |  | 2169.5 | 2408.5 | 135.9585 | 0 | 146.398 | 0 | 1.3596 | 0 | 1.464 | 0 | 1.3596 | 1.464 | 16.0925 | 7.814 | 14.7329
39049.4129 | 2287 | 0 | 39049.4129 | 2207 | 0 |  | 2211.5 | 2450.5 | 139.6215 | 0 | 134.7375 | 0 | 1.3962 | 0 | 1.3474 | 0 | 1.3962 | 1.3474 | 13.0468 | 17.1445 | 11.6506
39049.4134 | 2260 | 0 | 39049.4134 | 2000 | 0 |  | 2253.5 | 2492.5 | 137.9731 | 0 | 122.1001 | 0 | 1.3797 | 0 | 1.221 | 0 | 1.3797 | 1.221 | 14.3973 | 29.269 | 13.0176
39049.4139 | 1904 | 0 | 39049.4139 | 2037 | 0 |  | 2295.5 | 2534.5 | 116.2393 | 0 | 124.359 | 0 | 1.1624 | 0 | 1.2436 | 0 | 1.1624 | 1.2436 | 35.7868 | 26.921 | 34.6244
39049.4144 | 1929 | 0 | 39049.4144 | 2050 | 0 |  | 2337.5 | 2576.5 | 117.7656 | 0 | 125.1526 | 0 | 1.1777 | 0 | 1.2515 | 0 | 1.1777 | 1.2515 | 34.027 | 26.1161 | 32.8493
39049.4149 | 2166 | 0 | 39049.4149 | 2367 | 0 |  | 2379.5 | 2618.5 | 132.2344 | 0 | 144.5055 | 0 | 1.3223 | 0 | 1.4451 | 0 | 1.3223 | 1.4451 | 19.362 | 9.226 | 18.0396
39049.4154 | 2307 | 0 | 39049.4154 | 2555 | 0 |  | 2421.5 | 2660.5 | 140.8425 | 0 | 155.9829 | 0 | 1.4084 | 0 | 1.5598 | 0 | 1.4084 | 1.5598 | 12.0668 | 1.189 | 10.6583
39049.4158 | 2194 | 0 | 39049.4159 | 2027 | 0 |  | 2463.5 | 2702.5 | 133.9438 | 0 | 123.7485 | 0 | 1.3394 | 0 | 1.2375 | 0 | 1.3394 | 1.2375 | 17.8387 | 27.5471 | 16.4992
39049.4163 | 1971 | 0 | 39049.4163 | 2297 | 0 |  | 2505.5 | 2744.5 | 120.3297 | 0 | 140.232 | 0 | 1.2033 | 0 | 1.4023 | 0 | 1.2033 | 1.4023 | 31.171 | 12.5546 | 29.9677
39049.4168 | 2362 | 0 | 39049.4168 | 2007 | 0 |  | 2547.5 | 2786.5 | 144.2002 | 0 | 122.5275 | 0 | 1.442 | 0 | 1.2253 | 0 | 1.442 | 1.2253 | 9.4572 | 28.8181 | 8.0152
39049.4173 | 1978 | 0 | 39049.4173 | 2145 | 0 |  | 2589.5 | 2828.5 | 120.757 | 0 | 130.9524 | 0 | 1.2076 | 0 | 1.3095 | 0 | 1.2076 | 1.3095 | 30.7068 | 20.5305 | 29.4992
39049.4178 | 1840 | 0 | 39049.4178 | 2482 | 0 |  | 2631.5 | 2870.5 | 112.3321 | 0 | 151.5263 | 0 | 1.1233 | 0 | 1.5153 | 0 | 1.1233 | 1.5153 | 40.5098 | 4.1652 | 39.3865
39049.4183 | 2562 | 0 | 39049.4183 | 2032 | 0 |  | 2673.5 | 2912.5 | 156.4103 | 0 | 124.0537 | 0 | 1.5641 | 0 | 1.2405 | 0 | 1.5641 | 1.2405 | 0.91257 | 27.2333 | 0.65153
39049.4188 | 2431 | 0 | 39049.4188 | 2256 | 0 |  | 2715.5 | 2954.5 | 148.4127 | 0 | 137.7289 | 0 | 1.4841 | 0 | 1.3773 | 0 | 1.4841 | 1.3773 | 6.3505 | 14.6002 | 4.8663
39049.4192 | 2345 | 0 | 39049.4193 | 2547 | 0 |  | 2757.5 | 2996.5 | 143.1624 | 0 | 155.4945 | 0 | 1.4316 | 0 | 1.5549 | 0 | 1.4316 | 1.5549 | 10.2507 | 1.5069 | 8.8191
39049.4197 | 2321 | 0 | 39049.4197 | 2046 | 0 |  | 2799.5 | 3038.5 | 141.6972 | 0 | 124.9084 | 0 | 1.417 | 0 | 1.2491 | 0 | 1.417 | 1.2491 | 11.3908 | 26.3627 | 9.9738
39049.4202 | 2120 | 0 | 39049.4202 | 2213 | 0 |  | 2841.5 | 3080.5 | 129.4261 | 0 | 135.1038 | 0 | 1.2943 | 0 | 1.351 | 0 | 1.2943 | 1.351 | 21.9519 | 16.8269 | 20.6576
39049.4207 | 2510 | 0 | 39049.4207 | 2440 | 0 |  | 2883.5 | 3122.5 | 153.2357 | 0 | 148.9621 | 0 | 1.5324 | 0 | 1.4896 | 0 | 1.5324 | 1.4896 | 3.0032 | 5.9582 | 1.4708
39049.4212 | 2236 | 0 | 39049.4212 | 2447 | 0 |  | 2925.5 | 3164.5 | 136.5079 | 0 | 149.3895 | 0 | 1.3651 | 0 | 1.4939 | 0 | 1.3651 | 1.4939 | 15.6252 | 5.6551 | 14.2601
39049.4217 | 2496 | 0 | 39049.4217 | 1960 | 0 |  | 2967.5 | 3206.5 | 152.381 | 0 | 119.6581 | 0 | 1.5238 | 0 | 1.1966 | 0 | 1.5238 | 1.1966 | 3.5809 | 31.9071 | 2.0571

## A1-C6
Open Burn Test 13 |  |  | 2006-11-28 | 9:21 |  |  | Vs = |  | 156.4945 |  | R = | 100
Mixed | 7-C | Tray F | IRMS | 1
0 | 150 kW |  | Bundle | Ch. 1 & 6 | Cable A | Odd - | Cable C |  | Even
Time-9 | N11 | N12 | Time-10 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R6-G | R1-6
39049.3847 | 1 | 0 | 39049.3847 | 1 | 0 |  | -227 | 12 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256238 | 256238 | 256237.9994
39049.3852 | 1 | 0 | 39049.3852 | 1 | 0 |  | -185 | 54 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256238 | 256238 | 256237.9994
39049.3857 | 1 | 0 | 39049.3857 | 1 | 0 |  | -143 | 96 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256238 | 256238 | 256237.9994
39049.3862 | 1 | 0 | 39049.3862 | 1 | 0 |  | -101 | 138 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256238 | 256238 | 256237.9994
39049.3866 | 1 | 1 | 39049.3867 | 1 | 0 |  | -59 | 180 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 656579126.44 | 256238 | 256038.078
39049.3871 | 1 | 0 | 39049.3872 | 1 | 0 |  | -17 | 222 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256238 | 256238 | 256237.9994
39049.3876 | 1 | 0 | 39049.3876 | 1 | 0 |  | 25 | 264 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256238 | 256238 | 256237.9994
39049.3881 | 1 | 0 | 39049.3881 | 1 | 0 |  | 67 | 306 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256238 | 256238 | 256237.9994
39049.3886 | 1 | 0 | 39049.3886 | 1 | 0 |  | 109 | 348 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256238 | 256238 | 256237.9994
39049.3891 | 1 | 0 | 39049.3891 | 1 | 0 |  | 151 | 390 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256238 | 256238 | 256237.9994
39049.3896 | 1 | 0 | 39049.3896 | 1 | 0 |  | 193 | 432 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256238 | 256238 | 256237.9994
39049.39 | 1 | 0 | 39049.3901 | 1 | 0 |  | 235 | 474 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256238 | 256238 | 256237.9994
39049.3905 | 1 | 0 | 39049.3906 | 1 | 0 |  | 277 | 516 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256238 | 256238 | 256237.9994
39049.391 | 1 | 0 | 39049.391 | 1 | 0 |  | 319 | 558 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256238 | 256238 | 256237.9994
39049.3915 | 1 | 0 | 39049.3915 | 1 | 0 |  | 361 | 600 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256238 | 256238 | 256237.9994
39049.392 | 1 | 0 | 39049.392 | 1 | 0 |  | 403 | 642 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256238 | 256238 | 256237.9994
39049.3925 | 1 | 0 | 39049.3925 | 1 | 0 |  | 445 | 684 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256238 | 256238 | 256237.9994
39049.393 | 1 | 0 | 39049.393 | 1 | 0 |  | 487 | 726 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256238 | 256238 | 256237.9994
39049.3934 | 1 | 0 | 39049.3935 | 1 | 0 |  | 529 | 768 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256238 | 256238 | 256237.9994
39049.3939 | 1 | 0 | 39049.394 | 1 | 0 |  | 571 | 810 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256238 | 256238 | 256237.9994
39049.3944 | 1 | 0 | 39049.3944 | 1 | 0 |  | 613 | 852 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256238 | 256238 | 256237.9994
39049.3949 | 1 | 0 | 39049.3949 | 1 | 0 |  | 655 | 894 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256238 | 256238 | 256237.9994
39049.3954 | 1 | 0 | 39049.3954 | 1 | 0 |  | 697 | 936 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256238 | 256238 | 256237.9994
39049.3959 | 1 | 0 | 39049.3959 | 1 | 0 |  | 739 | 978 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256238 | 256238 | 256237.9994
39049.3964 | 1 | 0 | 39049.3964 | 1 | 0 |  | 781 | 1020 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256238 | 256238 | 256237.9994
39049.3969 | 1 | 0 | 39049.3969 | 1 | 0 |  | 823 | 1062 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256238 | 256238 | 256237.9994
39049.3973 | 1 | 0 | 39049.3974 | 1 | 0 |  | 865 | 1104 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256238 | 256238 | 256237.9994
39049.3978 | 1 | 0 | 39049.3978 | 1 | 0 |  | 907 | 1146 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256238 | 256238 | 256237.9994
39049.3983 | 1 | 0 | 39049.3983 | 1 | 0 |  | 948.5 | 1187.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256238 | 256238 | 256237.9994
39049.3988 | 1 | 0 | 39049.3988 | 1 | 0 |  | 991 | 1230 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256238 | 256238 | 256237.9994
39049.3993 | 1 | 0 | 39049.3993 | 1 | 0 |  | 1032.5 | 1271.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256238 | 256238 | 256237.9994
39049.3998 | 1 | 0 | 39049.3998 | 1 | 0 |  | 1074.5 | 1313.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256238 | 256238 | 256237.9994
39049.4003 | 1 | 0 | 39049.4003 | 1 | 0 |  | 1116.5 | 1355.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256238 | 256238 | 256237.9994
39049.4007 | 1 | 0 | 39049.4008 | 1 | 0 |  | 1158.5 | 1397.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256238 | 256238 | 256237.9994
39049.4012 | 1 | 0 | 39049.4012 | 1 | 0 |  | 1200.5 | 1439.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256238 | 256238 | 256237.9994
39049.4017 | 25 | 1 | 39049.4017 | 1 | 0 |  | 1243 | 1482 | 1.5263 | 0.06105 | 0.06105 | 0 | 0.015263 | 0.0006105 | 0.0006105 | 0 | 0.014652 | 0.0006105 | 10576.7553 | 256238 | 253639.0143
39049.4022 | 235 | 1 | 39049.4022 | 1 | 0 |  | 1284.5 | 1523.5 | 14.3468 | 0.06105 | 0.06105 | 0 | 0.14347 | 0.0006105 | 0.0006105 | 0 | 0.14286 | 0.0006105 | 995.0358 | 256238 | 232647.2066
39049.4027 | 2351 | 1 | 39049.4027 | 1 | 0 |  | 1327 | 1566 | 143.5287 | 0.06105 | 0.06105 | 0 | 1.4353 | 0.0006105 | 0.0006105 | 0 | 1.4347 | 0.0006105 | 9.0374 | 256238.0003 | 21129.7539
39049.4032 | 2431 | 1 | 39049.4032 | 1 | 0 |  | 1368.5 | 1607.5 | 148.4127 | 0.06105 | 0.06105 | 0 | 1.4841 | 0.0006105 | 0.0006105 | 0 | 1.4835 | 0.0006105 | 5.4477 | 256238.0001 | 13132.8747
39049.4037 | 2450 | 1 | 39049.4037 | 1 | 0 |  | 1411 | 1650 | 149.5726 | 0.06105 | 0.06105 | 0 | 1.4957 | 0.0006105 | 0.0006105 | 0 | 1.4951 | 0.0006105 | 4.6296 | 256237.9998 | 11233.6159
39049.4041 | 2306 | 1 | 39049.4042 | 1 | 0 |  | 1452.5 | 1691.5 | 140.7814 | 0.06105 | 0.06105 | 0 | 1.4078 | 0.0006105 | 0.0006105 | 0 | 1.4072 | 0.0006105 | 11.1662 | 256238.0001 | 25627.9984
39049.4046 | 1927 | 1 | 39049.4046 | 1 | 0 |  | 1494.5 | 1733.5 | 117.6435 | 0.06105 | 0.06105 | 0 | 1.1764 | 0.0006105 | 0.0006105 | 0 | 1.1758 | 0.0006105 | 33.0415 | 256238.0001 | 63513.2132
39049.4051 | 1900 | 1 | 39049.4051 | 2 | 0 |  | 1536.5 | 1775.5 | 115.9951 | 0.06105 | 0.1221 | 0 | 1.16 | 0.0006105 | 0.001221 | 0 | 1.1593 | 0.001221 | 34.9331 | 128069 | 66186.3198
39049.4056 | 2390 | 1 | 39049.4056 | 1 | 0 |  | 1578.5 | 1817.5 | 145.9096 | 0.06105 | 0.06105 | 0 | 1.4591 | 0.0006105 | 0.0006105 | 0 | 1.4585 | 0.0006105 | 7.2574 | 256238.0001 | 17231.2753
39049.4061 | 2418 | 1 | 39049.4061 | 1 | 0 |  | 1620.5 | 1859.5 | 147.619 | 0.06105 | 0.06105 | 0 | 1.4762 | 0.0006105 | 0.0006105 | 0 | 1.4756 | 0.0006105 | 6.0149 | 256238.0003 | 14432.3676
39049.4066 | 1949 | 1 | 39049.4066 | 1 | 0 |  | 1662.5 | 1901.5 | 118.9866 | 0.06105 | 0.06105 | 0 | 1.1899 | 0.0006105 | 0.0006105 | 0 | 1.1893 | 0.0006105 | 31.539 | 256238.0001 | 61314.0714
39049.4071 | 2241 | 1 | 39049.4071 | 1 | 0 |  | 1704.5 | 1943.5 | 136.8132 | 0.06105 | 0.06105 | 0 | 1.3681 | 0.0006105 | 0.0006105 | 0 | 1.3675 | 0.0006105 | 14.392 | 256237.9998 | 32125.4626
39049.4075 | 2037 | 1 | 39049.4076 | 1 | 0 |  | 1746.5 | 1985.5 | 124.359 | 0.06105 | 0.06105 | 0 | 1.2436 | 0.0006105 | 0.0006105 | 0 | 1.243 | 0.0006105 | 25.8536 | 256238.0001 | 52517.5044
39049.408 | 2270 | 1 | 39049.408 | 1 | 0 |  | 1788.5 | 2027.5 | 138.5836 | 0.06105 | 0.06105 | 0 | 1.3858 | 0.0006105 | 0.0006105 | 0 | 1.3852 | 0.0006105 | 12.9299 | 256238.0001 | 29226.594
39049.4085 | 2452 | 1 | 39049.4085 | 1 | 0 |  | 1830.5 | 2069.5 | 149.6947 | 0.06105 | 0.06105 | 0 | 1.4969 | 0.0006105 | 0.0006105 | 0 | 1.4963 | 0.0006105 | 4.5443 | 256238.0003 | 11033.694
39049.409 | 2357 | 1 | 39049.409 | 1 | 0 |  | 1872.5 | 2111.5 | 143.895 | 0.06105 | 0.06105 | 0 | 1.4389 | 0.0006105 | 0.0006105 | 0 | 1.4383 | 0.0006105 | 8.7598 | 256237.9998 | 20529.9879
39049.4095 | 2466 | 1 | 39049.4095 | 1 | 0 |  | 1914.5 | 2153.5 | 150.5495 | 0.06105 | 0.06105 | 0 | 1.5055 | 0.0006105 | 0.0006105 | 0 | 1.5049 | 0.0006105 | 3.9505 | 256238.0001 | 9634.2401
39049.41 | 2514 | 1 | 39049.41 | 1 | 0 |  | 1956.5 | 2195.5 | 153.4799 | 0.06105 | 0.06105 | 0 | 1.5348 | 0.0006105 | 0.0006105 | 0 | 1.5342 | 0.0006105 | 1.965 | 256238.0001 | 4836.1126
39049.4105 | 2072 | 1 | 39049.4105 | 1 | 0 |  | 1998.5 | 2237.5 | 126.4957 | 0.06105 | 0.06105 | 0 | 1.265 | 0.0006105 | 0.0006105 | 0 | 1.2643 | 0.0006105 | 23.7267 | 256238.0001 | 49018.8698
39049.4109 | 2048 | 1 | 39049.411 | 1 | 0 |  | 2040.5 | 2279.5 | 125.0305 | 0.06105 | 0.06105 | 0 | 1.2503 | 0.0006105 | 0.0006105 | 0 | 1.2497 | 0.0006105 | 25.1773 | 256238.0003 | 51417.9335
39049.4114 | 2261 | 1 | 39049.4114 | 1 | 0 |  | 2082.5 | 2321.5 | 138.0342 | 0.06105 | 0.06105 | 0 | 1.3803 | 0.0006105 | 0.0006105 | 0 | 1.3797 | 0.0006105 | 13.3796 | 256238.0003 | 30126.2429
39049.4119 | 2201 | 1 | 39049.4119 | 1 | 0 |  | 2124.5 | 2363.5 | 134.3712 | 0.06105 | 0.06105 | 0 | 1.3437 | 0.0006105 | 0.0006105 | 0 | 1.3431 | 0.0006105 | 16.4718 | 256238.0001 | 36123.9022
39049.4124 | 2006 | 1 | 39049.4124 | 72 | 0 |  | 2166.5 | 2405.5 | 122.4664 | 0.06105 | 4.3956 | 0 | 1.2247 | 0.0006105 | 0.043956 | 0 | 1.2241 | 0.043956 | 27.7999 | 3460.25 | 54075.2446
39049.4129 | 2326 | 1 | 39049.4129 | 111 | 0 |  | 2208.5 | 2447.5 | 142.0024 | 0.06105 | 6.7766 | 0 | 1.42 | 0.0006105 | 0.067766 | 0 | 1.4194 | 0.067766 | 10.2101 | 2209.3514 | 22614.4225
39049.4134 | 1930 | 1 | 39049.4134 | 146 | 0 |  | 2250.5 | 2489.5 | 117.8266 | 0.06105 | 8.9133 | 0 | 1.1783 | 0.0006105 | 0.089133 | 0 | 1.1777 | 0.089133 | 32.8357 | 1655.7397 | 59636.2133
39049.4139 | 1870 | 1 | 39049.4139 | 112 | 0 |  | 2292.5 | 2531.5 | 114.1636 | 0.06105 | 6.8376 | 0 | 1.1416 | 0.0006105 | 0.068376 | 0 | 1.141 | 0.068376 | 37.0999 | 2188.7321 | 66212.8317
39049.4144 | 2302 | 1 | 39049.4144 | 100 | 0 |  | 2334.5 | 2573.5 | 140.5372 | 0.06105 | 6.105 | 0 | 1.4054 | 0.0006105 | 0.06105 | 0 | 1.4048 | 0.06105 | 11.3596 | 2463.38 | 25022.2318
39049.4148 | 2076 | 1 | 39049.4148 | 117 | 0 |  | 2376.5 | 2615.5 | 126.7399 | 0.06105 | 7.1429 | 0 | 1.2674 | 0.0006105 | 0.071429 | 0 | 1.2668 | 0.071429 | 23.4887 | 2090.9231 | 46418.0225
39049.4153 | 1998 | 1 | 39049.4153 | 71 | 0 |  | 2418.5 | 2657.5 | 121.978 | 0.06105 | 4.3346 | 0 | 1.2198 | 0.0006105 | 0.043346 | 0 | 1.2192 | 0.043346 | 28.3119 | 3510.3944 | 54874.7913
39049.4158 | 2207 | 1 | 39049.4158 | 63 | 0 |  | 2460.5 | 2699.5 | 134.7375 | 0.06105 | 3.8462 | 0 | 1.3474 | 0.0006105 | 0.038462 | 0 | 1.3468 | 0.038462 | 16.1552 | 3968.8571 | 34664.5852
39049.4163 | 1893 | 1 | 39049.4163 | 60 | 0 |  | 2502.5 | 2741.5 | 115.5678 | 0.06105 | 3.663 | 0 | 1.1557 | 0.0006105 | 0.03663 | 0 | 1.1551 | 0.03663 | 35.4328 | 4172.3 | 65371.2093
39049.4168 | 2055 | 1 | 39049.4168 | 40 | 0 |  | 2544.5 | 2783.5 | 125.4579 | 0.06105 | 2.442 | 0 | 1.2546 | 0.0006105 | 0.02442 | 0 | 1.254 | 0.02442 | 24.7509 | 6308.45 | 49946.2641
39049.4173 | 1938 | 1 | 39049.4173 | 46 | 0 |  | 2586.5 | 2825.5 | 118.315 | 0.06105 | 2.8083 | 0 | 1.1832 | 0.0006105 | 0.028083 | 0 | 1.1825 | 0.028083 | 32.2863 | 5472.5652 | 61317.5465
39049.4178 | 2191 | 1 | 39049.4178 | 40 | 0 |  | 2628.5 | 2867.5 | 133.7607 | 0.06105 | 2.442 | 0 | 1.3376 | 0.0006105 | 0.02442 | 0 | 1.337 | 0.02442 | 17.0038 | 6308.45 | 36558.4839
39049.4182 | 2366 | 1 | 39049.4183 | 29 | 0 |  | 2670.5 | 2909.5 | 144.4444 | 0.06105 | 1.7705 | 0 | 1.4444 | 0.0006105 | 0.017705 | 0 | 1.4438 | 0.017705 | 8.3459 | 8739.2414 | 19415.8316
39049.4187 | 2171 | 1 | 39049.4187 | 25 | 0 |  | 2712.5 | 2951.5 | 132.5397 | 0.06105 | 1.5263 | 0 | 1.3254 | 0.0006105 | 0.015263 | 0 | 1.3248 | 0.015263 | 18.0821 | 10153.52 | 38756.2969
39049.4192 | 2040 | 1 | 39049.4192 | 19 | 0 |  | 2754.5 | 2993.5 | 124.5421 | 0.06105 | 1.16 | 0 | 1.2454 | 0.0006105 | 0.0116 | 0 | 1.2448 | 0.0116 | 25.6686 | 13391.4737 | 51850.8073
39049.4197 | 2547 | 1 | 39049.4197 | 15 | 0 |  | 2796.5 | 3035.5 | 155.4945 | 0.06105 | 0.91575 | 0 | 1.5549 | 0.0006105 | 0.0091575 | 0 | 1.5543 | 0.0091575 | 0.64336 | 16989.2 | 1529.0002
39049.4202 | 2056 | 1 | 39049.4202 | 7 | 0 |  | 2838.5 | 3077.5 | 125.5189 | 0.06105 | 0.42735 | 0 | 1.2552 | 0.0006105 | 0.0042735 | 0 | 1.2546 | 0.0042735 | 24.6901 | 36519.7143 | 50499.7193
39049.4207 | 2093 | 1 | 39049.4207 | 3 | 0 |  | 2880.5 | 3119.5 | 127.7778 | 0.06105 | 0.18315 | 0 | 1.2778 | 0.0006105 | 0.0018315 | 0 | 1.2772 | 0.0018315 | 22.4847 | 85346 | 46883.0671
39049.4212 | 2506 | 1 | 39049.4212 | 2 | 0 |  | 2922.5 | 3161.5 | 152.9915 | 0.06105 | 0.1221 | 0 | 1.5299 | 0.0006105 | 0.001221 | 0 | 1.5293 | 0.001221 | 2.2906 | 128069 | 5633.6011
39049.4216 | 2515 | 1 | 39049.4217 | 2 | 0 |  | 2964.5 | 3203.5 | 153.5409 | 0.06105 | 0.1221 | 0 | 1.5354 | 0.0006105 | 0.001221 | 0 | 1.5348 | 0.001221 | 1.9244 | 128069 | 4734.3033

## A1-C5
Open Burn Test 13 |  |  | 2006-11-28 | 9:21 |  |  | Vs = |  | 155.3346 |  | R = | 100
Mixed | 7-C | Tray F | IRMS | 1
0 | 150 kW |  | Bundle | Ch. 1 & 5 | Cable A | Odd - | Cable C |  | Odd
Time-7 | N11 | N12 | Time-8 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R5-G | R1-5
39049.3847 | 1 | 0 | 39049.3847 | 1 | 0 |  | -229.5 | 9.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254338 | 254338 | 254337.9994
39049.3852 | 1 | 0 | 39049.3852 | 1 | 0 |  | -187.5 | 51.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254338 | 254338 | 254337.9994
39049.3856 | 1 | 0 | 39049.3857 | 1 | 0 |  | -145.5 | 93.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254338 | 254338 | 254337.9994
39049.3861 | 1 | 0 | 39049.3861 | 1 | 0 |  | -103.5 | 135.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254338 | 254338 | 254337.9994
39049.3866 | 1 | 0 | 39049.3866 | 1 | 0 |  | -62 | 177 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254338 | 254338 | 254337.9994
39049.3871 | 1 | 0 | 39049.3871 | 1 | 0 |  | -20 | 219 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254338 | 254338 | 254337.9994
39049.3876 | 1 | 0 | 39049.3876 | 1 | 0 |  | 22.5 | 261.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254338 | 254338 | 254337.9994
39049.3881 | 1 | 0 | 39049.3881 | 1 | 0 |  | 64 | 303 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254338 | 254338 | 254337.9994
39049.3886 | 1 | 0 | 39049.3886 | 1 | 0 |  | 106 | 345 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254338 | 254338 | 254337.9994
39049.389 | 1 | 0 | 39049.3891 | 1 | 0 |  | 148 | 387 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254338 | 254338 | 254337.9994
39049.3895 | 1 | 0 | 39049.3895 | 1 | 0 |  | 190 | 429 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254338 | 254338 | 254337.9994
39049.39 | 1 | 0 | 39049.39 | 1 | 0 |  | 232 | 471 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254338 | 254338 | 254337.9994
39049.3905 | 1 | 0 | 39049.3905 | 1 | 0 |  | 274 | 513 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254338 | 254338 | 254337.9994
39049.391 | 1 | 0 | 39049.391 | 1 | 0 |  | 316 | 555 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254338 | 254338 | 254337.9994
39049.3915 | 1 | 0 | 39049.3915 | 1 | 0 |  | 358 | 597 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254338 | 254338 | 254337.9994
39049.392 | 1 | 0 | 39049.392 | 1 | 0 |  | 400 | 639 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254338 | 254338 | 254337.9994
39049.3924 | 1 | 0 | 39049.3925 | 1 | 0 |  | 442 | 681 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254338 | 254338 | 254337.9994
39049.3929 | 1 | 0 | 39049.393 | 1 | 0 |  | 484 | 723 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254338 | 254338 | 254337.9994
39049.3934 | 1 | 0 | 39049.3934 | 1 | 0 |  | 526 | 765 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254338 | 254338 | 254337.9994
39049.3939 | 1 | 0 | 39049.3939 | 1 | 0 |  | 568 | 807 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254338 | 254338 | 254337.9994
39049.3944 | 1 | 0 | 39049.3944 | 1 | 0 |  | 610 | 849 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254338 | 254338 | 254337.9994
39049.3949 | 1 | 0 | 39049.3949 | 1 | 0 |  | 652 | 891 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254338 | 254338 | 254337.9994
39049.3954 | 1 | 0 | 39049.3954 | 1 | 0 |  | 694 | 933 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254338 | 254338 | 254337.9994
39049.3958 | 1 | 0 | 39049.3959 | 1 | 0 |  | 736 | 975 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254338 | 254338 | 254337.9994
39049.3963 | 1 | 0 | 39049.3964 | 1 | 0 |  | 778 | 1017 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254338 | 254338 | 254337.9994
39049.3968 | 1 | 0 | 39049.3968 | 1 | 0 |  | 820 | 1059 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254338 | 254338 | 254337.9994
39049.3973 | 1 | 0 | 39049.3973 | 1 | 0 |  | 862 | 1101 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254338 | 254338 | 254337.9994
39049.3978 | 1 | 0 | 39049.3978 | 1 | 0 |  | 904 | 1143 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254338 | 254338 | 254337.9994
39049.3983 | 1 | 0 | 39049.3983 | 1 | 0 |  | 946 | 1185 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254338 | 254338 | 254337.9994
39049.3988 | 1 | 0 | 39049.3988 | 1 | 0 |  | 988 | 1227 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254338 | 254338 | 254337.9994
39049.3992 | 1 | 0 | 39049.3993 | 1 | 0 |  | 1030 | 1269 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254338 | 254338 | 254337.9994
39049.3997 | 1 | 0 | 39049.3998 | 1 | 0 |  | 1072 | 1311 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254338 | 254338 | 254337.9994
39049.4002 | 1 | 0 | 39049.4002 | 1 | 0 |  | 1114 | 1353 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254338 | 254338 | 254337.9994
39049.4007 | 1 | 0 | 39049.4007 | 1 | 0 |  | 1156 | 1395 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254338 | 254338 | 254337.9994
39049.4012 | 1 | 0 | 39049.4012 | 1 | 0 |  | 1198 | 1437 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254338 | 254338 | 254337.9994
39049.4017 | 25 | 1 | 39049.4017 | 1 | 0 |  | 1240 | 1479 | 1.5263 | 0.06105 | 0.06105 | 0 | 0.015263 | 0.0006105 | 0.0006105 | 0 | 0.014652 | 0.0006105 | 10497.5886 | 254338 | 251739.0219
39049.4022 | 45 | 1 | 39049.4022 | 1 | 0 |  | 1282 | 1521 | 2.7473 | 0.06105 | 0.06105 | 0 | 0.027473 | 0.0006105 | 0.0006105 | 0 | 0.026862 | 0.0006105 | 5680.4599 | 254338 | 249739.8079
39049.4027 | 2352 | 1 | 39049.4027 | 1 | 0 |  | 1324 | 1563 | 143.5897 | 0.06105 | 0.06105 | 0 | 1.4359 | 0.0006105 | 0.0006105 | 0 | 1.4353 | 0.0006105 | 8.1829 | 254337.9998 | 19130.4783
39049.4031 | 2416 | 1 | 39049.4032 | 1 | 0 |  | 1366 | 1605 | 147.4969 | 0.06105 | 0.06105 | 0 | 1.475 | 0.0006105 | 0.0006105 | 0 | 1.4744 | 0.0006105 | 5.3159 | 254338.0002 | 12732.9937
39049.4036 | 2110 | 1 | 39049.4036 | 1 | 0 |  | 1408 | 1647 | 128.8156 | 0.06105 | 0.06105 | 0 | 1.2882 | 0.0006105 | 0.0006105 | 0 | 1.2875 | 0.0006105 | 20.5965 | 254338 | 43320.9672
39049.4041 | 2212 | 1 | 39049.4041 | 1 | 0 |  | 1450 | 1689 | 135.0427 | 0.06105 | 0.06105 | 0 | 1.3504 | 0.0006105 | 0.0006105 | 0 | 1.3498 | 0.0006105 | 15.033 | 254338.0002 | 33124.976
39049.4046 | 2097 | 1 | 39049.4046 | 1 | 0 |  | 1492 | 1731 | 128.022 | 0.06105 | 0.06105 | 0 | 1.2802 | 0.0006105 | 0.0006105 | 0 | 1.2796 | 0.0006105 | 21.3445 | 254338 | 44620.4562
39049.4051 | 1882 | 1 | 39049.4051 | 1 | 0 |  | 1534 | 1773 | 114.8962 | 0.06105 | 0.06105 | 0 | 1.149 | 0.0006105 | 0.0006105 | 0 | 1.1484 | 0.0006105 | 35.2143 | 254338.0002 | 66112.0062
39049.4056 | 2043 | 1 | 39049.4056 | 1 | 0 |  | 1576 | 1815 | 124.7253 | 0.06105 | 0.06105 | 0 | 1.2473 | 0.0006105 | 0.0006105 | 0 | 1.2466 | 0.0006105 | 24.5534 | 254338.0002 | 50018.3339
39049.4061 | 2153 | 1 | 39049.4061 | 1 | 0 |  | 1618 | 1857 | 131.4408 | 0.06105 | 0.06105 | 0 | 1.3144 | 0.0006105 | 0.0006105 | 0 | 1.3138 | 0.0006105 | 18.1868 | 254338.0002 | 39022.6572
39049.4065 | 2311 | 1 | 39049.4066 | 1 | 0 |  | 1660 | 1899 | 141.0867 | 0.06105 | 0.06105 | 0 | 1.4109 | 0.0006105 | 0.0006105 | 0 | 1.4103 | 0.0006105 | 10.103 | 254338.0002 | 23228.8669
39049.407 | 1985 | 1 | 39049.407 | 1 | 0 |  | 1702 | 1941 | 121.1844 | 0.06105 | 0.06105 | 0 | 1.2118 | 0.0006105 | 0.0006105 | 0 | 1.2112 | 0.0006105 | 28.1946 | 254338.0002 | 55816.0544
39049.4075 | 1865 | 1 | 39049.4075 | 1 | 0 |  | 1744 | 1983 | 113.8584 | 0.06105 | 0.06105 | 0 | 1.1386 | 0.0006105 | 0.0006105 | 0 | 1.138 | 0.0006105 | 36.4474 | 254338 | 67811.3381
39049.408 | 1958 | 1 | 39049.408 | 1 | 0 |  | 1786 | 2025 | 119.536 | 0.06105 | 0.06105 | 0 | 1.1954 | 0.0006105 | 0.0006105 | 0 | 1.1947 | 0.0006105 | 29.9632 | 254337.9998 | 58514.9932
39049.4085 | 1978 | 1 | 39049.4085 | 1 | 0 |  | 1828 | 2067 | 120.757 | 0.06105 | 0.06105 | 0 | 1.2076 | 0.0006105 | 0.0006105 | 0 | 1.207 | 0.0006105 | 28.6485 | 254338 | 56515.7793
39049.409 | 2462 | 1 | 39049.409 | 1 | 0 |  | 1870 | 2109 | 150.3053 | 0.06105 | 0.06105 | 0 | 1.5031 | 0.0006105 | 0.0006105 | 0 | 1.5024 | 0.0006105 | 3.3474 | 254338 | 8134.8016
39049.4095 | 2207 | 1 | 39049.4095 | 1 | 0 |  | 1912 | 2151 | 134.7375 | 0.06105 | 0.06105 | 0 | 1.3474 | 0.0006105 | 0.0006105 | 0 | 1.3468 | 0.0006105 | 15.2937 | 254338 | 33624.7795
39049.4099 | 2085 | 1 | 39049.41 | 1 | 0 |  | 1954 | 2193 | 127.2894 | 0.06105 | 0.06105 | 0 | 1.2729 | 0.0006105 | 0.0006105 | 0 | 1.2723 | 0.0006105 | 22.0432 | 254338 | 45819.9846
39049.4104 | 2049 | 1 | 39049.4105 | 2 | 0 |  | 1996 | 2235 | 125.0916 | 0.06105 | 0.1221 | 0 | 1.2509 | 0.0006105 | 0.001221 | 0 | 1.2503 | 0.001221 | 24.1885 | 127118.9999 | 49399.1395
39049.4109 | 2502 | 1 | 39049.4109 | 1 | 0 |  | 2038 | 2277 | 152.7473 | 0.06105 | 0.06105 | 0 | 1.5275 | 0.0006105 | 0.0006105 | 0 | 1.5269 | 0.0006105 | 1.6945 | 254338.0002 | 4136.3737
39049.4114 | 2139 | 1 | 39049.4114 | 1 | 0 |  | 2080 | 2319 | 130.5861 | 0.06105 | 0.06105 | 0 | 1.3059 | 0.0006105 | 0.0006105 | 0 | 1.3053 | 0.0006105 | 18.9607 | 254338 | 40422.1069
39049.4119 | 1862 | 1 | 39049.4119 | 1 | 0 |  | 2122 | 2361 | 113.6752 | 0.06105 | 0.06105 | 0 | 1.1368 | 0.0006105 | 0.0006105 | 0 | 1.1361 | 0.0006105 | 36.6674 | 254338 | 68111.2202
39049.4124 | 1919 | 1 | 39049.4124 | 6 | 0 |  | 2164 | 2403 | 117.1551 | 0.06105 | 0.3663 | 0 | 1.1716 | 0.0006105 | 0.003663 | 0 | 1.1709 | 0.003663 | 32.6059 | 42306.3333 | 62290.7626
39049.4129 | 2361 | 1 | 39049.4129 | 16 | 0 |  | 2205.5 | 2444.5 | 144.1392 | 0.06105 | 0.9768 | 0 | 1.4414 | 0.0006105 | 0.009768 | 0 | 1.4408 | 0.009768 | 7.7704 | 15802.375 | 18123.3127
39049.4133 | 2031 | 1 | 39049.4134 | 34 | 0 |  | 2248 | 2487 | 123.9927 | 0.06105 | 2.0757 | 0 | 1.2399 | 0.0006105 | 0.020757 | 0 | 1.2393 | 0.020757 | 25.2898 | 7383.4706 | 50553.3177
39049.4138 | 1985 | 1 | 39049.4139 | 33 | 0 |  | 2290 | 2529 | 121.1844 | 0.06105 | 2.0147 | 0 | 1.2118 | 0.0006105 | 0.020147 | 0 | 1.2112 | 0.020147 | 28.1947 | 7610.2424 | 55113.7945
39049.4143 | 2028 | 1 | 39049.4143 | 35 | 0 |  | 2332 | 2571 | 123.8095 | 0.06105 | 2.1368 | 0 | 1.2381 | 0.0006105 | 0.021368 | 0 | 1.2375 | 0.021368 | 25.4753 | 7169.6571 | 50829.0532
39049.4148 | 2361 | 1 | 39049.4148 | 19 | 0 |  | 2374 | 2613 | 144.1392 | 0.06105 | 1.16 | 0 | 1.4414 | 0.0006105 | 0.0116 | 0 | 1.4408 | 0.0116 | 7.7704 | 13291.4737 | 18101.8089
39049.4153 | 2233 | 1 | 39049.4153 | 23 | 0 |  | 2415.5 | 2654.5 | 136.3248 | 0.06105 | 1.4042 | 0 | 1.3632 | 0.0006105 | 0.014042 | 0 | 1.3626 | 0.014042 | 13.9508 | 10962.5217 | 30757.4311
39049.4158 | 2136 | 1 | 39049.4158 | 17 | 0 |  | 2457.5 | 2696.5 | 130.4029 | 0.06105 | 1.0379 | 0 | 1.304 | 0.0006105 | 0.010379 | 0 | 1.3034 | 0.010379 | 19.1279 | 14866.9412 | 40465.8135
39049.4163 | 1865 | 1 | 39049.4163 | 19 | 0 |  | 2499.5 | 2738.5 | 113.8584 | 0.06105 | 1.16 | 0 | 1.1386 | 0.0006105 | 0.0116 | 0 | 1.138 | 0.0116 | 36.4476 | 13291.4737 | 67331.4239
39049.4167 | 1992 | 1 | 39049.4168 | 11 | 0 |  | 2541.5 | 2780.5 | 121.6117 | 0.06105 | 0.67155 | 0 | 1.2161 | 0.0006105 | 0.0067155 | 0 | 1.2155 | 0.0067155 | 27.7439 | 23030.7273 | 54899.6244
39049.4172 | 1929 | 1 | 39049.4172 | 23 | 0 |  | 2583.5 | 2822.5 | 117.7656 | 0.06105 | 1.4042 | 0 | 1.1777 | 0.0006105 | 0.014042 | 0 | 1.177 | 0.014042 | 31.9182 | 10962.5217 | 60882.6293
39049.4177 | 1972 | 1 | 39049.4177 | 27 | 0 |  | 2626 | 2865 | 120.3907 | 0.06105 | 1.6484 | 0 | 1.2039 | 0.0006105 | 0.016484 | 0 | 1.2033 | 0.016484 | 29.0402 | 9323.6296 | 56531.6731
39049.4182 | 1963 | 1 | 39049.4182 | 25 | 0 |  | 2667.5 | 2906.5 | 119.8413 | 0.06105 | 1.5263 | 0 | 1.1984 | 0.0006105 | 0.015263 | 0 | 1.1978 | 0.015263 | 29.6322 | 10077.52 | 57467.7432
39049.4187 | 2119 | 1 | 39049.4187 | 17 | 0 |  | 2709.5 | 2948.5 | 129.3651 | 0.06105 | 1.0379 | 0 | 1.2937 | 0.0006105 | 0.010379 | 0 | 1.293 | 0.010379 | 20.0841 | 14866.9412 | 42154.4551
39049.4192 | 2344 | 1 | 39049.4192 | 16 | 0 |  | 2751.5 | 2990.5 | 143.1013 | 0.06105 | 0.9768 | 0 | 1.431 | 0.0006105 | 0.009768 | 0 | 1.4304 | 0.009768 | 8.5523 | 15802.375 | 19812.6225
39049.4197 | 2528 | 1 | 39049.4197 | 12 | 0 |  | 2793.5 | 3032.5 | 154.3346 | 0.06105 | 0.7326 | 0 | 1.5433 | 0.0006105 | 0.007326 | 0 | 1.5427 | 0.007326 | 0.6482 | 21103.1667 | 1530.7464
39049.4202 | 2069 | 1 | 39049.4202 | 9 | 0 |  | 2835.5 | 3074.5 | 126.3126 | 0.06105 | 0.54945 | 0 | 1.2631 | 0.0006105 | 0.0054945 | 0 | 1.2625 | 0.0054945 | 22.9875 | 28170.8889 | 47270.202
39049.4206 | 2497 | 1 | 39049.4206 | 9 | 0 |  | 2877.5 | 3116.5 | 152.442 | 0.06105 | 0.54945 | 0 | 1.5244 | 0.0006105 | 0.0054945 | 0 | 1.5238 | 0.0054945 | 1.8982 | 28170.8889 | 4621.5944
39049.4211 | 2155 | 1 | 39049.4211 | 8 | 0 |  | 2919.5 | 3158.5 | 131.5629 | 0.06105 | 0.4884 | 0 | 1.3156 | 0.0006105 | 0.004884 | 0 | 1.315 | 0.004884 | 18.0771 | 31704.75 | 38715.8862
39049.4216 | 2221 | 1 | 39049.4216 | 5 | 0 |  | 2961.5 | 3200.5 | 135.5922 | 0.06105 | 0.30525 | 0 | 1.3559 | 0.0006105 | 0.0030525 | 0 | 1.3553 | 0.0030525 | 14.5667 | 50787.6 | 32174.6486

## A1-B4
Open Burn Test 13 |  |  | 2006-11-28 | 9:21 |  |  | Vs = |  | 158.6313 |  | R = | 100
Mixed | 7-C | Tray F | IRMS | 1
0 | 150 kW |  | Bundle | Ch. 1 & 4 | Cable A | Odd - | Cable B |  | Even
Time-5 | N11 | N12 | Time-6 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R4-G | R1-4
39049.3846 | 1 | 0 | 39049.3847 | 1 | 0 |  | -232.5 | 6.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259738 | 259738 | 259737.9994
39049.3851 | 1 | 0 | 39049.3851 | 1 | 0 |  | -190.5 | 48.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259738 | 259738 | 259737.9994
39049.3856 | 1 | 0 | 39049.3856 | 1 | 0 |  | -148.5 | 90.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259738 | 259738 | 259737.9994
39049.3861 | 1 | 0 | 39049.3861 | 1 | 0 |  | -106.5 | 132.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259738 | 259738 | 259737.9994
39049.3866 | 1 | 0 | 39049.3866 | 1 | 0 |  | -64.5 | 174.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259738 | 259738 | 259737.9994
39049.3871 | 1 | 0 | 39049.3871 | 1 | 0 |  | -22.5 | 216.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259738 | 259738 | 259737.9994
39049.3876 | 1 | 0 | 39049.3876 | 1 | 0 |  | 19.5 | 258.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259738 | 259738 | 259737.9994
39049.388 | 1 | 0 | 39049.3881 | 1 | 0 |  | 61.5 | 300.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259738 | 259738 | 259737.9994
39049.3885 | 1 | 0 | 39049.3885 | 1 | 0 |  | 103.5 | 342.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259738 | 259738 | 259737.9994
39049.389 | 1 | 0 | 39049.389 | 1 | 0 |  | 145.5 | 384.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259738 | 259738 | 259737.9994
39049.3895 | 1 | 0 | 39049.3895 | 1 | 0 |  | 187.5 | 426.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259738 | 259738 | 259737.9994
39049.39 | 1 | 0 | 39049.39 | 1 | 0 |  | 229.5 | 468.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259738 | 259738 | 259737.9994
39049.3905 | 1 | 0 | 39049.3905 | 1 | 0 |  | 271.5 | 510.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259738 | 259738 | 259737.9994
39049.391 | 1 | 0 | 39049.391 | 1 | 0 |  | 313.5 | 552.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259738 | 259738 | 259737.9994
39049.3914 | 1 | 0 | 39049.3915 | 1 | 0 |  | 355.5 | 594.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259738 | 259738 | 259737.9994
39049.3919 | 1 | 0 | 39049.3919 | 1 | 0 |  | 397.5 | 636.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259738 | 259738 | 259737.9994
39049.3924 | 1 | 0 | 39049.3924 | 1 | 0 |  | 439.5 | 678.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259738 | 259738 | 259737.9994
39049.3929 | 1 | 0 | 39049.3929 | 1 | 0 |  | 481.5 | 720.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259738 | 259738 | 259737.9994
39049.3934 | 1 | 0 | 39049.3934 | 1 | 0 |  | 523.5 | 762.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259738 | 259738 | 259737.9994
39049.3939 | 1 | 0 | 39049.3939 | 1 | 0 |  | 565.5 | 804.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259738 | 259738 | 259737.9994
39049.3944 | 1 | 0 | 39049.3944 | 1 | 0 |  | 607.5 | 846.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259738 | 259738 | 259737.9994
39049.3948 | 1 | 0 | 39049.3949 | 1 | 0 |  | 649.5 | 888.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259738 | 259738 | 259737.9994
39049.3953 | 1 | 0 | 39049.3953 | 1 | 0 |  | 691.5 | 930.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259738 | 259738 | 259737.9994
39049.3958 | 1 | 0 | 39049.3958 | 1 | 0 |  | 733.5 | 972.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259738 | 259738 | 259737.9994
39049.3963 | 1 | 0 | 39049.3963 | 1 | 0 |  | 775.5 | 1014.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259738 | 259738 | 259737.9994
39049.3968 | 1 | 0 | 39049.3968 | 1 | 0 |  | 817.5 | 1056.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259738 | 259738 | 259737.9994
39049.3973 | 1 | 0 | 39049.3973 | 1 | 0 |  | 859.5 | 1098.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259738 | 259738 | 259737.9994
39049.3978 | 1 | 0 | 39049.3978 | 1 | 0 |  | 901.5 | 1140.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259738 | 259738 | 259737.9994
39049.3982 | 1 | 0 | 39049.3983 | 1 | 0 |  | 943 | 1182 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259738 | 259738 | 259737.9994
39049.3987 | 1 | 0 | 39049.3988 | 2094 | 0 |  | 985.5 | 1224.5 | 0.06105 | 0 | 127.8388 | 0 | 0.0006105 | 0 | 1.2784 | 0 | 0.0006105 | 1.2784 | 259738 | 24.0869 | 259737.9994
39049.3992 | 1 | 0 | 39049.3992 | 2307 | 0 |  | 1027 | 1266 | 0.06105 | 0 | 140.8425 | 0 | 0.0006105 | 0 | 1.4084 | 0 | 0.0006105 | 1.4084 | 259738 | 12.6303 | 259737.9994
39049.3997 | 1 | 0 | 39049.3997 | 2457 | 0 |  | 1069.5 | 1308.5 | 0.06105 | 0 | 150 | 0 | 0.0006105 | 0 | 1.5 | 0 | 0.0006105 | 1.5 | 259738 | 5.7542 | 259737.9994
39049.4002 | 1 | 0 | 39049.4002 | 2067 | 0 |  | 1111 | 1350 | 0.06105 | 0 | 126.1905 | 0 | 0.0006105 | 0 | 1.2619 | 0 | 0.0006105 | 1.2619 | 259738 | 25.7078 | 259737.9994
39049.4007 | 1 | 0 | 39049.4007 | 2276 | 0 |  | 1153 | 1392 | 0.06105 | 0 | 138.9499 | 0 | 0.0006105 | 0 | 1.3895 | 0 | 0.0006105 | 1.3895 | 259738 | 14.1643 | 259737.9994
39049.4012 | 1 | 0 | 39049.4012 | 1926 | 0 |  | 1195 | 1434 | 0.06105 | 0 | 117.5824 | 0 | 0.0006105 | 0 | 1.1758 | 0 | 0.0006105 | 1.1758 | 259738 | 34.9107 | 259737.9994
39049.4016 | 8 | 0 | 39049.4017 | 2073 | 0 |  | 1237 | 1476 | 0.4884 | 0 | 126.5568 | 0 | 0.004884 | 0 | 1.2656 | 0 | 0.004884 | 1.2656 | 32379.75 | 25.3439 | 32379.7451
39049.4021 | 1374 | 0 | 39049.4022 | 2277 | 0 |  | 1279.5 | 1518.5 | 83.8828 | 0 | 139.011 | 0 | 0.83883 | 0 | 1.3901 | 0 | 0.83883 | 1.3901 | 89.1106 | 14.1142 | 88.2718
39049.4026 | 2335 | 0 | 39049.4026 | 1983 | 0 |  | 1321 | 1560 | 142.5519 | 0 | 121.0623 | 0 | 1.4255 | 0 | 1.2106 | 0 | 1.4255 | 1.2106 | 11.2797 | 31.0328 | 9.8541
39049.4031 | 2423 | 0 | 39049.4031 | 2247 | 0 |  | 1363.5 | 1602.5 | 147.9243 | 0 | 137.1795 | 0 | 1.4792 | 0 | 1.3718 | 0 | 1.4792 | 1.3718 | 7.2381 | 15.6377 | 5.7589
39049.4036 | 2315 | 0 | 39049.4036 | 2470 | 0 |  | 1405 | 1644 | 141.3309 | 0 | 150.7937 | 0 | 1.4133 | 0 | 1.5079 | 0 | 1.4133 | 1.5079 | 12.241 | 5.1976 | 10.8277
39049.4041 | 2186 | 0 | 39049.4041 | 2444 | 0 |  | 1447 | 1686 | 133.4554 | 0 | 149.2063 | 0 | 1.3346 | 0 | 1.4921 | 0 | 1.3346 | 1.4921 | 18.8646 | 6.3167 | 17.53
39049.4046 | 2210 | 0 | 39049.4046 | 2500 | 0 |  | 1489 | 1728 | 134.9206 | 0 | 152.6252 | 0 | 1.3492 | 0 | 1.5263 | 0 | 1.3492 | 1.5263 | 17.5738 | 3.9352 | 16.2245
39049.405 | 2239 | 0 | 39049.4051 | 2322 | 0 |  | 1531 | 1770 | 136.6911 | 0 | 141.7582 | 0 | 1.3669 | 0 | 1.4176 | 0 | 1.3669 | 1.4176 | 16.0509 | 11.9027 | 14.684
39049.4055 | 1938 | 0 | 39049.4056 | 2107 | 0 |  | 1573 | 1812 | 118.315 | 0 | 128.6325 | 0 | 1.1832 | 0 | 1.2863 | 0 | 1.1832 | 1.2863 | 34.0753 | 23.3213 | 32.8922
39049.406 | 2105 | 0 | 39049.406 | 1957 | 0 |  | 1615 | 1854 | 128.5104 | 0 | 119.475 | 0 | 1.2851 | 0 | 1.1947 | 0 | 1.2851 | 1.1947 | 23.4385 | 32.7736 | 22.1534
39049.4065 | 2328 | 0 | 39049.4065 | 2122 | 0 |  | 1657 | 1896 | 142.1245 | 0 | 129.5482 | 0 | 1.4212 | 0 | 1.2955 | 0 | 1.4212 | 1.2955 | 11.6143 | 22.4496 | 10.193
39049.407 | 1980 | 0 | 39049.407 | 2214 | 0 |  | 1699 | 1938 | 120.8791 | 0 | 135.1648 | 0 | 1.2088 | 0 | 1.3516 | 0 | 1.2088 | 1.3516 | 31.2313 | 17.3613 | 30.0225
39049.4075 | 2156 | 0 | 39049.4075 | 2130 | 0 |  | 1741 | 1980 | 131.6239 | 0 | 130.0366 | 0 | 1.3162 | 0 | 1.3004 | 0 | 1.3162 | 1.3004 | 20.5186 | 21.9897 | 19.2023
39049.408 | 2406 | 0 | 39049.408 | 2582 | 0 |  | 1783 | 2022 | 146.8864 | 0 | 157.6313 | 0 | 1.4689 | 0 | 1.5763 | 0 | 1.4689 | 1.5763 | 7.9958 | 0.63439 | 6.527
39049.4084 | 2135 | 0 | 39049.4085 | 2064 | 0 |  | 1825 | 2064 | 130.3419 | 0 | 126.0073 | 0 | 1.3034 | 0 | 1.2601 | 0 | 1.3034 | 1.2601 | 21.704 | 25.8905 | 20.4006
39049.4089 | 2165 | 0 | 39049.409 | 1998 | 0 |  | 1867 | 2106 | 132.1734 | 0 | 121.978 | 0 | 1.3217 | 0 | 1.2198 | 0 | 1.3217 | 1.2198 | 20.0176 | 30.049 | 18.6958
39049.4094 | 1920 | 0 | 39049.4094 | 2044 | 0 |  | 1909 | 2148 | 117.2161 | 0 | 124.7863 | 0 | 1.1722 | 0 | 1.2479 | 0 | 1.1722 | 1.2479 | 35.3323 | 27.1223 | 34.1601
39049.4099 | 2083 | 0 | 39049.4099 | 2513 | 0 |  | 1951 | 2190 | 127.1673 | 0 | 153.4188 | 0 | 1.2717 | 0 | 1.5342 | 0 | 1.2717 | 1.5342 | 24.7422 | 3.3975 | 23.4705
39049.4104 | 2005 | 0 | 39049.4104 | 2581 | 0 |  | 1993 | 2232 | 122.4054 | 0 | 157.5702 | 0 | 1.2241 | 0 | 1.5757 | 0 | 1.2241 | 1.5757 | 29.595 | 0.67338 | 28.371
39049.4109 | 2506 | 0 | 39049.4109 | 2490 | 0 |  | 2035 | 2274 | 152.9915 | 0 | 152.0147 | 0 | 1.5299 | 0 | 1.5201 | 0 | 1.5299 | 1.5201 | 3.6864 | 4.3526 | 2.1564
39049.4114 | 2081 | 0 | 39049.4114 | 2128 | 0 |  | 2077 | 2316 | 127.0452 | 0 | 129.9145 | 0 | 1.2705 | 0 | 1.2991 | 0 | 1.2705 | 1.2991 | 24.8621 | 22.1043 | 23.5916
39049.4119 | 2186 | 0 | 39049.4119 | 2505 | 0 |  | 2119 | 2358 | 133.4554 | 0 | 152.9304 | 0 | 1.3346 | 0 | 1.5293 | 0 | 1.3346 | 1.5293 | 18.8646 | 3.7277 | 17.53
39049.4123 | 2214 | 0 | 39049.4124 | 2274 | 0 |  | 2161 | 2400 | 135.1648 | 0 | 138.8278 | 0 | 1.3516 | 0 | 1.3883 | 0 | 1.3516 | 1.3883 | 17.3613 | 14.2647 | 16.0097
39049.4128 | 1899 | 0 | 39049.4128 | 2186 | 0 |  | 2203 | 2442 | 115.9341 | 0 | 133.4554 | 0 | 1.1593 | 0 | 1.3346 | 0 | 1.1593 | 1.3346 | 36.8289 | 18.8646 | 35.6695
39049.4133 | 2345 | 0 | 39049.4133 | 2457 | 0 |  | 2245 | 2484 | 143.1624 | 0 | 150 | 0 | 1.4316 | 0 | 1.5 | 0 | 1.4316 | 1.5 | 10.8051 | 5.7542 | 9.3735
39049.4138 | 2325 | 0 | 39049.4138 | 2025 | 0 |  | 2287 | 2526 | 141.9414 | 0 | 123.6264 | 0 | 1.4194 | 0 | 1.2363 | 0 | 1.4194 | 1.2363 | 11.7583 | 28.3151 | 10.3389
39049.4143 | 2030 | 0 | 39049.4143 | 2214 | 0 |  | 2329 | 2568 | 123.9316 | 0 | 135.1648 | 0 | 1.2393 | 0 | 1.3516 | 0 | 1.2393 | 1.3516 | 27.999 | 17.3613 | 26.7597
39049.4148 | 2077 | 0 | 39049.4148 | 1980 | 0 |  | 2371 | 2610 | 126.801 | 0 | 120.8791 | 0 | 1.268 | 0 | 1.2088 | 0 | 1.268 | 1.2088 | 25.1026 | 31.2313 | 23.8345
39049.4153 | 1947 | 0 | 39049.4153 | 2544 | 0 |  | 2413 | 2652 | 118.8645 | 0 | 155.3114 | 0 | 1.1886 | 0 | 1.5531 | 0 | 1.1886 | 1.5531 | 33.4556 | 2.1376 | 32.2669
39049.4157 | 2354 | 0 | 39049.4158 | 1974 | 0 |  | 2455 | 2694 | 143.7118 | 0 | 120.5128 | 0 | 1.4371 | 0 | 1.2051 | 0 | 1.4371 | 1.2051 | 10.3815 | 31.6302 | 8.9444
39049.4162 | 2293 | 0 | 39049.4163 | 2535 | 0 |  | 2497 | 2736 | 139.9878 | 0 | 154.7619 | 0 | 1.3999 | 0 | 1.5476 | 0 | 1.3999 | 1.5476 | 13.3179 | 2.5002 | 11.918
39049.4167 | 2000 | 0 | 39049.4167 | 2247 | 0 |  | 2539 | 2778 | 122.1001 | 0 | 137.1795 | 0 | 1.221 | 0 | 1.3718 | 0 | 1.221 | 1.3718 | 29.919 | 15.6377 | 28.698
39049.4172 | 2331 | 0 | 39049.4172 | 2345 | 0 |  | 2581 | 2820 | 142.3077 | 0 | 143.1624 | 0 | 1.4231 | 0 | 1.4316 | 0 | 1.4231 | 1.4316 | 11.4706 | 10.8051 | 10.0475
39049.4177 | 2150 | 0 | 39049.4177 | 1999 | 0 |  | 2623 | 2862 | 131.2576 | 0 | 122.0391 | 0 | 1.3126 | 0 | 1.2204 | 0 | 1.3126 | 1.2204 | 20.8549 | 29.984 | 19.5423
39049.4182 | 2148 | 0 | 39049.4182 | 2211 | 0 |  | 2665 | 2904 | 131.1355 | 0 | 134.9817 | 0 | 1.3114 | 0 | 1.3498 | 0 | 1.3114 | 1.3498 | 20.9674 | 17.5206 | 19.6561
39049.4187 | 2357 | 0 | 39049.4187 | 2444 | 0 |  | 2707 | 2946 | 143.895 | 0 | 149.2063 | 0 | 1.4389 | 0 | 1.4921 | 0 | 1.4389 | 1.4921 | 10.241 | 6.3167 | 8.802
39049.4191 | 2464 | 0 | 39049.4192 | 1967 | 0 |  | 2749 | 2988 | 150.4274 | 0 | 120.0855 | 0 | 1.5043 | 0 | 1.2009 | 0 | 1.5043 | 1.2009 | 5.4537 | 32.0986 | 3.9495
39049.4196 | 2152 | 0 | 39049.4197 | 2100 | 0 |  | 2791 | 3030 | 131.3797 | 0 | 128.2051 | 0 | 1.3138 | 0 | 1.2821 | 0 | 1.3138 | 1.2821 | 20.7426 | 23.7324 | 19.4288
39049.4201 | 2123 | 0 | 39049.4201 | 2534 | 0 |  | 2833 | 3072 | 129.6093 | 0 | 154.7009 | 0 | 1.2961 | 0 | 1.547 | 0 | 1.2961 | 1.547 | 22.3919 | 2.5406 | 21.0958
39049.4206 | 2447 | 0 | 39049.4206 | 2521 | 0 |  | 2875 | 3114 | 149.3895 | 0 | 153.9072 | 0 | 1.4939 | 0 | 1.5391 | 0 | 1.4939 | 1.5391 | 6.1864 | 3.0694 | 4.6925
39049.4211 | 2210 | 0 | 39049.4211 | 2073 | 0 |  | 2917 | 3156 | 134.9206 | 0 | 126.5568 | 0 | 1.3492 | 0 | 1.2656 | 0 | 1.3492 | 1.2656 | 17.5738 | 25.3439 | 16.2245
39049.4216 | 2145 | 0 | 39049.4216 | 2281 | 0 |  | 2959 | 3198 | 130.9524 | 0 | 139.2552 | 0 | 1.3095 | 0 | 1.3926 | 0 | 1.3095 | 1.3926 | 21.1366 | 13.9141 | 19.8271

## A1-B3
Open Burn Test 13 |  |  | 2006-11-28 | 9:21 |  |  | Vs = |  | 156.7387 |  | R = | 100
Mixed | 7-C | Tray F | IRMS | 1
0 | 150 kW |  | Bundle | Ch. 1 & 3 | Cable A | Odd - | Cable B |  | Odd
Time-3 | N11 | N12 | Time-4 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R3-G | R1-3
39049.3846 | 1 | 0 | 39049.3846 | 1 | 0 |  | -235.5 | 3.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256638 | 256638 | 256637.9994
39049.3851 | 1 | 0 | 39049.3851 | 1 | 0 |  | -193.5 | 45.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256638 | 256638 | 256637.9994
39049.3856 | 1 | 0 | 39049.3856 | 1 | 0 |  | -151.5 | 87.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256638 | 256638 | 256637.9994
39049.3861 | 1 | 0 | 39049.3861 | 1 | 0 |  | -109.5 | 129.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256638 | 256638 | 256637.9994
39049.3866 | 1 | 0 | 39049.3866 | 1 | 0 |  | -67.5 | 171.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256638 | 256638 | 256637.9994
39049.387 | 1 | 0 | 39049.387 | 1 | 0 |  | -25.5 | 213.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256638 | 256638 | 256637.9994
39049.3875 | 1 | 0 | 39049.3875 | 1 | 0 |  | 16.5 | 255.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256638 | 256638 | 256637.9994
39049.388 | 1 | 0 | 39049.388 | 1 | 0 |  | 58.5 | 297.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256638 | 256638 | 256637.9994
39049.3885 | 1 | 0 | 39049.3885 | 1 | 0 |  | 100.5 | 339.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256638 | 256638 | 256637.9994
39049.389 | 1 | 0 | 39049.389 | 1 | 0 |  | 142.5 | 381.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256638 | 256638 | 256637.9994
39049.3895 | 1 | 0 | 39049.3895 | 1 | 0 |  | 184.5 | 423.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256638 | 256638 | 256637.9994
39049.39 | 1 | 0 | 39049.39 | 1 | 0 |  | 226.5 | 465.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256638 | 256638 | 256637.9994
39049.3904 | 1 | 0 | 39049.3905 | 1 | 0 |  | 268.5 | 507.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256638 | 256638 | 256637.9994
39049.3909 | 1 | 0 | 39049.3909 | 1 | 0 |  | 310.5 | 549.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256638 | 256638 | 256637.9994
39049.3914 | 1 | 0 | 39049.3914 | 1 | 0 |  | 352.5 | 591.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256638 | 256638 | 256637.9994
39049.3919 | 1 | 0 | 39049.3919 | 1 | 0 |  | 394.5 | 633.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256638 | 256638 | 256637.9994
39049.3924 | 1 | 0 | 39049.3924 | 1 | 0 |  | 436.5 | 675.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256638 | 256638 | 256637.9994
39049.3929 | 1 | 0 | 39049.3929 | 1 | 0 |  | 478.5 | 717.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256638 | 256638 | 256637.9994
39049.3934 | 1 | 0 | 39049.3934 | 1 | 0 |  | 520.5 | 759.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256638 | 256638 | 256637.9994
39049.3938 | 1 | 0 | 39049.3939 | 1 | 0 |  | 562.5 | 801.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256638 | 256638 | 256637.9994
39049.3943 | 1 | 0 | 39049.3943 | 1 | 0 |  | 604.5 | 843.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256638 | 256638 | 256637.9994
39049.3948 | 1 | 0 | 39049.3948 | 1 | 0 |  | 646.5 | 885.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256638 | 256638 | 256637.9994
39049.3953 | 1 | 0 | 39049.3953 | 1 | 0 |  | 688.5 | 927.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256638 | 256638 | 256637.9994
39049.3958 | 1 | 0 | 39049.3958 | 1 | 0 |  | 730.5 | 969.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256638 | 256638 | 256637.9994
39049.3963 | 1 | 0 | 39049.3963 | 1 | 0 |  | 772.5 | 1011.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256638 | 256638 | 256637.9994
39049.3968 | 1 | 0 | 39049.3968 | 1 | 0 |  | 814.5 | 1053.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256638 | 256638 | 256637.9994
39049.3972 | 1 | 0 | 39049.3973 | 1 | 0 |  | 856.5 | 1095.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256638 | 256638 | 256637.9994
39049.3977 | 1 | 0 | 39049.3977 | 1 | 0 |  | 898.5 | 1137.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256638 | 256638 | 256637.9994
39049.3982 | 1 | 0 | 39049.3982 | 1 | 0 |  | 940.5 | 1179.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256638 | 256638 | 256637.9994
39049.3987 | 1 | 0 | 39049.3987 | 15 | 0 |  | 982.5 | 1221.5 | 0.06105 | 0 | 0.91575 | 0 | 0.0006105 | 0 | 0.0091575 | 0 | 0.0006105 | 0.0091575 | 256638 | 17015.8667 | 256637.9994
39049.3992 | 1 | 0 | 39049.3992 | 2176 | 0 |  | 1024.5 | 1263.5 | 0.06105 | 0 | 132.8449 | 0 | 0.0006105 | 0 | 1.3284 | 0 | 0.0006105 | 1.3284 | 256638 | 17.9862 | 256637.9994
39049.3997 | 1 | 0 | 39049.3997 | 2315 | 0 |  | 1066.5 | 1305.5 | 0.06105 | 0 | 141.3309 | 0 | 0.0006105 | 0 | 1.4133 | 0 | 0.0006105 | 1.4133 | 256638 | 10.9019 | 256637.9994
39049.4002 | 1 | 0 |  | 2227 | 0 |  | 1108 | 1347 | 0.06105 | 0 | 135.9585 | 0 | 0.0006105 | 0 | 1.3596 | 0 | 0.0006105 | 1.3596 | 256638 | 15.2842 | 256637.9994
39049.4006 | 1 | 0 | 39049.4007 | 2138 | 0 |  | 1150.5 | 1389.5 | 0.06105 | 0 | 130.525 | 0 | 0.0006105 | 0 | 1.3053 | 0 | 0.0006105 | 1.3053 | 256638 | 20.0833 | 256637.9994
39049.4011 | 1 | 0 | 39049.4011 | 1997 | 0 |  | 1192.5 | 1431.5 | 0.06105 | 0 | 121.917 | 0 | 0.0006105 | 0 | 1.2192 | 0 | 0.0006105 | 1.2192 | 256638 | 28.5618 | 256637.9994
39049.4016 | 5 | 0 | 39049.4016 | 2083 | 0 |  | 1234.5 | 1473.5 | 0.30525 | 0 | 127.1673 | 0 | 0.0030525 | 0 | 1.2717 | 0 | 0.0030525 | 1.2717 | 51247.6 | 23.254 | 51247.5969
39049.4021 | 1485 | 0 | 39049.4021 | 2172 | 0 |  | 1276.5 | 1515.5 | 90.6593 | 0 | 132.6007 | 0 | 0.90659 | 0 | 1.326 | 0 | 0.90659 | 1.326 | 72.8875 | 18.2035 | 71.9809
39049.4026 | 2093 | 0 | 39049.4026 | 1621 | 0 |  | 1318.5 | 1557.5 | 127.7778 | 0 | 98.9621 | 0 | 1.2778 | 0 | 0.98962 | 0 | 1.2778 | 0.98962 | 22.6651 | 58.3825 | 21.3873
39049.4031 | 2006 | 0 | 39049.4031 | 1938 | 0 |  | 1360.5 | 1599.5 | 122.4664 | 0 | 118.315 | 0 | 1.2247 | 0 | 1.1832 | 0 | 1.2247 | 1.1832 | 27.985 | 32.4757 | 26.7604
39049.4036 | 2326 | 0 | 39049.4036 | 2382 | 0 |  | 1402.5 | 1641.5 | 142.0024 | 0 | 145.4212 | 0 | 1.42 | 0 | 1.4542 | 0 | 1.42 | 1.4542 | 10.3775 | 7.7825 | 8.9574
39049.4041 | 2377 | 0 | 39049.4041 | 2087 | 0 |  | 1444.5 | 1683.5 | 145.116 | 0 | 127.4115 | 0 | 1.4512 | 0 | 1.2741 | 0 | 1.4512 | 1.2741 | 8.0093 | 23.0177 | 6.5581
39049.4045 | 2063 | 0 | 39049.4045 | 2180 | 0 |  | 1486.5 | 1725.5 | 125.9463 | 0 | 133.0891 | 0 | 1.2595 | 0 | 1.3309 | 0 | 1.2595 | 1.3309 | 24.4489 | 17.7697 | 23.1894
39049.405 | 2313 | 0 | 39049.405 | 2435 | 0 |  | 1528.5 | 1767.5 | 141.2088 | 0 | 148.6569 | 0 | 1.4121 | 0 | 1.4866 | 0 | 1.4121 | 1.4866 | 10.9978 | 5.4366 | 9.5858
39049.4055 | 2045 | 0 | 39049.4055 | 2332 | 0 |  | 1570.5 | 1809.5 | 124.8474 | 0 | 142.3687 | 0 | 1.2485 | 0 | 1.4237 | 0 | 1.2485 | 1.4237 | 25.5443 | 10.0935 | 24.2958
39049.406 | 1905 | 0 | 39049.406 | 2377 | 0 |  | 1612.5 | 1851.5 | 116.3004 | 0 | 145.116 | 0 | 1.163 | 0 | 1.4512 | 0 | 1.163 | 1.4512 | 34.7706 | 8.0093 | 33.6076
39049.4065 | 2303 | 0 | 39049.4065 | 2330 | 0 |  | 1654.5 | 1893.5 | 140.5983 | 0 | 142.2466 | 0 | 1.406 | 0 | 1.4225 | 0 | 1.406 | 1.4225 | 11.4798 | 10.188 | 10.0738
39049.407 | 1898 | 0 | 39049.407 | 2392 | 0 |  | 1696.5 | 1935.5 | 115.873 | 0 | 146.0317 | 0 | 1.1587 | 0 | 1.4603 | 0 | 1.1587 | 1.4603 | 35.2677 | 7.3319 | 34.1089
39049.4075 | 1900 | 0 | 39049.4075 | 2170 | 0 |  | 1738.5 | 1977.5 | 115.9951 | 0 | 132.4786 | 0 | 1.16 | 0 | 1.3248 | 0 | 1.16 | 1.3248 | 35.1253 | 18.3124 | 33.9653
39049.4079 | 1929 | 0 | 39049.408 | 2168 | 0 |  | 1780.5 | 2019.5 | 117.7656 | 0 | 132.3565 | 0 | 1.1777 | 0 | 1.3236 | 0 | 1.1777 | 1.3236 | 33.0938 | 18.4216 | 31.9162
39049.4084 | 2164 | 0 | 39049.4084 | 2160 | 0 |  | 1822.5 | 2061.5 | 132.1123 | 0 | 131.8681 | 0 | 1.3211 | 0 | 1.3187 | 0 | 1.3211 | 1.3187 | 18.6405 | 18.8602 | 17.3194
39049.4089 | 2475 | 0 | 39049.4089 | 2011 | 0 |  | 1864.5 | 2103.5 | 151.0989 | 0 | 122.7717 | 0 | 1.511 | 0 | 1.2277 | 0 | 1.511 | 1.2277 | 3.7325 | 27.6668 | 2.2215
39049.4094 | 2496 | 0 | 39049.4094 | 2001 | 0 |  | 1906.5 | 2145.5 | 152.381 | 0 | 122.1612 | 0 | 1.5238 | 0 | 1.2216 | 0 | 1.5238 | 1.2216 | 2.8598 | 28.3048 | 1.336
39049.4099 | 2226 | 0 | 39049.4099 | 2016 | 0 |  | 1948.5 | 2187.5 | 135.8974 | 0 | 123.0769 | 0 | 1.359 | 0 | 1.2308 | 0 | 1.359 | 1.2308 | 15.336 | 27.3502 | 13.9771
39049.4104 | 2432 | 0 | 39049.4104 | 2162 | 0 |  | 1990.5 | 2229.5 | 148.4737 | 0 | 131.9902 | 0 | 1.4847 | 0 | 1.3199 | 0 | 1.4847 | 1.3199 | 5.5666 | 18.7502 | 4.0819
39049.4109 | 2452 | 0 | 39049.4109 | 2551 | 0 |  | 2032.5 | 2271.5 | 149.6947 | 0 | 155.7387 | 0 | 1.4969 | 0 | 1.5574 | 0 | 1.4969 | 1.5574 | 4.7055 | 0.6421 | 3.2086
39049.4113 | 1934 | 0 | 39049.4114 | 2213 | 0 |  | 2074.5 | 2313.5 | 118.0708 | 0 | 135.1038 | 0 | 1.1807 | 0 | 1.351 | 0 | 1.1807 | 1.351 | 32.7497 | 16.0136 | 31.569
39049.4118 | 2254 | 0 | 39049.4118 | 2110 | 0 |  | 2116.5 | 2355.5 | 137.6068 | 0 | 128.8156 | 0 | 1.3761 | 0 | 1.2882 | 0 | 1.3761 | 1.2882 | 13.9033 | 21.6768 | 12.5272
39049.4123 | 1933 | 0 | 39049.4123 | 1979 | 0 |  | 2158.5 | 2397.5 | 118.0098 | 0 | 120.8181 | 0 | 1.1801 | 0 | 1.2082 | 0 | 1.1801 | 1.2082 | 32.8184 | 29.7312 | 31.6383
39049.4128 | 1928 | 0 | 39049.4128 | 2151 | 0 |  | 2200.5 | 2439.5 | 117.7045 | 0 | 131.3187 | 0 | 1.177 | 0 | 1.3132 | 0 | 1.177 | 1.3132 | 33.1629 | 19.3575 | 31.9858
39049.4133 | 1943 | 0 | 39049.4133 | 2061 | 0 |  | 2242.5 | 2481.5 | 118.6203 | 0 | 125.8242 | 0 | 1.1862 | 0 | 1.2582 | 0 | 1.1862 | 1.2582 | 32.1348 | 24.5696 | 30.9486
39049.4138 | 2031 | 0 | 39049.4138 | 2422 | 0 |  | 2284.5 | 2523.5 | 123.9927 | 0 | 147.8632 | 0 | 1.2399 | 0 | 1.4786 | 0 | 1.2399 | 1.4786 | 26.4097 | 6.0025 | 25.1697
39049.4142 | 2381 | 0 | 39049.4143 | 2488 | 0 |  | 2326 | 2565 | 145.3602 | 0 | 151.8926 | 0 | 1.4536 | 0 | 1.5189 | 0 | 1.4536 | 1.5189 | 7.8278 | 3.1905 | 6.3742
39049.4147 | 2139 | 0 | 39049.4148 | 2494 | 0 |  | 2368 | 2607 | 130.5861 | 0 | 152.2589 | 0 | 1.3059 | 0 | 1.5226 | 0 | 1.3059 | 1.5226 | 20.0271 | 2.9423 | 18.7213
39049.4152 | 2159 | 0 | 39049.4152 | 2139 | 0 |  | 2410 | 2649 | 131.8071 | 0 | 130.5861 | 0 | 1.3181 | 0 | 1.3059 | 0 | 1.3181 | 1.3059 | 18.9152 | 20.0271 | 17.5972
39049.4157 | 2350 | 0 | 39049.4157 | 2162 | 0 |  | 2452.5 | 2691.5 | 143.4676 | 0 | 131.9902 | 0 | 1.4347 | 0 | 1.3199 | 0 | 1.4347 | 1.3199 | 9.2502 | 18.7502 | 7.8155
39049.4162 | 2167 | 0 | 39049.4162 | 2320 | 0 |  | 2494 | 2733 | 132.2955 | 0 | 141.6361 | 0 | 1.323 | 0 | 1.4164 | 0 | 1.323 | 1.4164 | 18.4762 | 10.6629 | 17.1533
39049.4167 | 1964 | 0 | 39049.4167 | 2096 | 0 |  | 2536.5 | 2775.5 | 119.9023 | 0 | 127.9609 | 0 | 1.199 | 0 | 1.2796 | 0 | 1.199 | 1.2796 | 30.722 | 22.4895 | 29.523
39049.4172 | 1820 | 0 | 39049.4172 | 2126 | 1 |  | 2578 | 2817 | 111.1111 | 0 | 129.7924 | 0.06105 | 1.1111 | 0 | 1.2979 | 0.0006105 | 1.1111 | 1.2973 | 41.0648 | 20.8179 | 39.9537
39049.4177 | 1891 | 0 | 39049.4177 | 2339 | 0 |  | 2620 | 2859 | 115.4457 | 0 | 142.7961 | 0 | 1.1545 | 0 | 1.428 | 0 | 1.1545 | 1.428 | 35.7684 | 9.764 | 34.6139
39049.4181 | 2491 | 0 | 39049.4182 | 2367 | 0 |  | 2662 | 2901 | 152.0757 | 0 | 144.5055 | 0 | 1.5208 | 0 | 1.4451 | 0 | 1.5208 | 1.4451 | 3.0662 | 8.4656 | 1.5455
39049.4186 | 2066 | 0 | 39049.4186 | 1972 | 0 |  | 2704 | 2943 | 126.1294 | 0 | 120.3907 | 0 | 1.2613 | 0 | 1.2039 | 0 | 1.2613 | 1.2039 | 24.2682 | 30.1917 | 23.0069
39049.4191 | 2439 | 0 | 39049.4191 | 2548 | 0 |  | 2746.5 | 2985.5 | 148.9011 | 0 | 155.5556 | 0 | 1.489 | 0 | 1.5556 | 0 | 1.489 | 1.5556 | 5.2636 | 0.7606 | 3.7746
39049.4196 | 2369 | 0 | 39049.4196 | 2487 | 0 |  | 2788 | 3027 | 144.6276 | 0 | 151.8315 | 0 | 1.4463 | 0 | 1.5183 | 0 | 1.4463 | 1.5183 | 8.374 | 3.232 | 6.9277
39049.4201 | 2333 | 0 | 39049.4201 | 2131 | 0 |  | 2830 | 3069 | 142.4298 | 0 | 130.0977 | 0 | 1.4243 | 0 | 1.301 | 0 | 1.4243 | 1.301 | 10.0463 | 20.4777 | 8.622
39049.4206 | 2321 | 0 | 39049.4206 | 2139 | 0 |  | 2872 | 3111 | 141.6972 | 0 | 130.5861 | 0 | 1.417 | 0 | 1.3059 | 0 | 1.417 | 1.3059 | 10.6153 | 20.0271 | 9.1983
39049.4211 | 2339 | 0 | 39049.4211 | 2074 | 0 |  | 2914.5 | 3153.5 | 142.7961 | 0 | 126.6178 | 0 | 1.428 | 0 | 1.2662 | 0 | 1.428 | 1.2662 | 9.764 | 23.7888 | 8.336
39049.4215 | 2031 | 0 | 39049.4216 | 1954 | 0 |  | 2956 | 3195 | 123.9927 | 0 | 119.2918 | 0 | 1.2399 | 0 | 1.1929 | 0 | 1.2399 | 1.1929 | 26.4097 | 31.391 | 25.1697

## A1-A2
Open Burn Test 13 |  |  | 2006-11-28 | 9:21 |  |  | Vs = |  | 156.0061 |  | R = | 100
Mixed | 7-C | Tray F | IRMS | 1
0 | 150 kW |  | Bundle | Ch. 1 & 2 | Cable A | Odd-Even
Time-1 | N11 | N12 | Time-2 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R2-G | R1-2
39049.3846 | 1 | 0 | 39049.3846 | 1 | 0 |  | -238 | 1 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255438 | 255438 | 255437.9994
39049.3851 | 1 | 0 | 39049.3851 | 1 | 0 |  | -196 | 43 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255438 | 255438 | 255437.9994
39049.3855 | 1 | 0 | 39049.3856 | 1 | 0 |  | -154 | 85 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255438 | 255438 | 255437.9994
39049.386 | 1 | 0 | 39049.3861 | 1 | 0 |  | -112 | 127 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255438 | 255438 | 255437.9994
39049.3865 | 1 | 0 | 39049.3865 | 1 | 0 |  | -70 | 169 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255438 | 255438 | 255437.9994
39049.387 | 1 | 0 | 39049.387 | 1 | 0 |  | -28 | 211 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255438 | 255438 | 255437.9994
39049.3875 | 1 | 0 | 39049.3875 | 1 | 0 |  | 14 | 253 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255438 | 255438 | 255437.9994
39049.388 | 1 | 0 | 39049.388 | 1 | 0 |  | 55.5 | 294.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255438 | 255438 | 255437.9994
39049.3885 | 1 | 0 | 39049.3885 | 1 | 0 |  | 97.5 | 336.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255438 | 255438 | 255437.9994
39049.3889 | 1 | 0 | 39049.389 | 1 | 0 |  | 139.5 | 378.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255438 | 255438 | 255437.9994
39049.3894 | 1 | 0 | 39049.3894 | 1 | 0 |  | 181.5 | 420.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255438 | 255438 | 255437.9994
39049.3899 | 1 | 0 | 39049.3899 | 1 | 0 |  | 223.5 | 462.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255438 | 255438 | 255437.9994
39049.3904 | 1 | 0 | 39049.3904 | 1 | 0 |  | 265.5 | 504.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255438 | 255438 | 255437.9994
39049.3909 | 1 | 0 | 39049.3909 | 1 | 0 |  | 307.5 | 546.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255438 | 255438 | 255437.9994
39049.3914 | 1 | 0 | 39049.3914 | 1 | 0 |  | 349.5 | 588.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255438 | 255438 | 255437.9994
39049.3919 | 1 | 0 | 39049.3919 | 1 | 0 |  | 391.5 | 630.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255438 | 255438 | 255437.9994
39049.3923 | 1 | 0 | 39049.3924 | 1 | 0 |  | 433.5 | 672.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255438 | 255438 | 255437.9994
39049.3928 | 1 | 0 | 39049.3928 | 1 | 0 |  | 475.5 | 714.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255438 | 255438 | 255437.9994
39049.3933 | 1 | 0 | 39049.3933 | 1 | 0 |  | 517.5 | 756.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255438 | 255438 | 255437.9994
39049.3938 | 1 | 0 | 39049.3938 | 1 | 0 |  | 559.5 | 798.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255438 | 255438 | 255437.9994
39049.3943 | 1 | 0 | 39049.3943 | 1 | 0 |  | 601.5 | 840.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255438 | 255438 | 255437.9994
39049.3948 | 1 | 0 | 39049.3948 | 1 | 0 |  | 643.5 | 882.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255438 | 255438 | 255437.9994
39049.3953 | 1 | 0 | 39049.3953 | 1 | 0 |  | 685.5 | 924.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255438 | 255438 | 255437.9994
39049.3958 | 1 | 0 | 39049.3958 | 1 | 0 |  | 727.5 | 966.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255438 | 255438 | 255437.9994
39049.3962 | 1 | 0 | 39049.3962 | 1 | 0 |  | 769.5 | 1008.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255438 | 255438 | 255437.9994
39049.3967 | 1 | 0 | 39049.3967 | 1 | 0 |  | 811.5 | 1050.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255438 | 255438 | 255437.9994
39049.3972 | 1 | 0 | 39049.3972 | 1 | 0 |  | 853.5 | 1092.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255438 | 255438 | 255437.9994
39049.3977 | 1 | 0 | 39049.3977 | 1 | 0 |  | 895.5 | 1134.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255438 | 255438 | 255437.9994
39049.3982 | 1 | 0 | 39049.3982 | 1 | 0 |  | 937.5 | 1176.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255438 | 255438 | 255437.9994
39049.3987 | 1 | 0 | 39049.3987 | 1 | 0 |  | 979.5 | 1218.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255438 | 255438 | 255437.9994
39049.3992 | 1 | 0 | 39049.3992 | 1 | 0 |  | 1021.5 | 1260.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255438 | 255438 | 255437.9994
39049.3996 | 1 | 0 | 39049.3997 | 1 | 0 |  | 1063.5 | 1302.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255438 | 255438 | 255437.9994
39049.4001 | 1 | 0 | 39049.4001 | 1 | 0 |  | 1105.5 | 1344.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255438 | 255438 | 255437.9994
39049.4006 | 1 | 0 | 39049.4006 | 1 | 0 |  | 1147.5 | 1386.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255438 | 255438 | 255437.9994
39049.4011 | 1 | 0 | 39049.4011 | 1 | 0 |  | 1189.5 | 1428.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255438 | 255438 | 255437.9994
39049.4016 | 2 | 0 | 39049.4016 | 833 | 0 |  | 1231.5 | 1470.5 | 0.1221 | 0 | 50.8547 | 0 | 0.001221 | 0 | 0.50855 | 0 | 0.001221 | 0.50855 | 127669 | 206.7683 | 127668.9988
39049.4021 | 1110 | 1029 | 39049.4021 | 1123 | 1118 |  | 1273.5 | 1512.5 | 67.7656 | 62.8205 | 68.5592 | 68.254 | 0.67766 | 0.62821 | 0.68559 | 0.68254 | 0.049451 | 0.0030525 | 829.6625 | 1103.9233 | 37.1035
39049.4026 | 1784 | 267 | 39049.4026 | 1729 | 146 |  | 1315.5 | 1554.5 | 108.9133 | 16.3004 | 105.5556 | 8.9133 | 1.0891 | 0.163 | 1.0556 | 0.089133 | 0.92613 | 0.96642 | 72.0219 | 59.8703 | 70.7441
39049.403 | 1986 | 17 | 39049.4031 | 2226 | 14 |  | 1357.5 | 1596.5 | 121.2454 | 1.0379 | 135.8974 | 0.8547 | 1.2125 | 0.010379 | 1.359 | 0.008547 | 1.2021 | 1.3504 | 30.6581 | 15.2045 | 428.836
39049.4035 | 1966 | 0 | 39049.4035 | 2034 | 1 |  | 1399.5 | 1638.5 | 120.0244 | 0 | 124.1758 | 0.06105 | 1.2002 | 0 | 1.2418 | 0.0006105 | 1.2002 | 1.2411 | 29.9786 | 25.695 | 28.7784
39049.404 | 2273 | 0 | 39049.404 | 2243 | 0 |  | 1441.5 | 1680.5 | 138.7668 | 0 | 136.9353 | 0 | 1.3877 | 0 | 1.3694 | 0 | 1.3877 | 1.3694 | 12.4232 | 13.9269 | 11.0356
39049.4045 | 2361 | 2 | 39049.4045 | 1980 | 4 |  | 1483.5 | 1722.5 | 144.1392 | 0.1221 | 120.8791 | 0.2442 | 1.4414 | 0.001221 | 1.2088 | 0.002442 | 1.4402 | 1.2063 | 8.2634 | 29.8497 | 2211.2018
39049.405 | 2123 | 9 | 39049.405 | 2425 | 9 |  | 1525.5 | 1764.5 | 129.6093 | 0.54945 | 148.0464 | 0.54945 | 1.2961 | 0.0054945 | 1.4805 | 0.0054945 | 1.2906 | 1.475 | 22.173 | 5.4887 | 244.7677
39049.4055 | 2160 | 23 | 39049.4055 | 1971 | 23 |  | 1567.5 | 1806.5 | 131.8681 | 1.4042 | 120.3297 | 1.4042 | 1.3187 | 0.014042 | 1.2033 | 0.014042 | 1.3046 | 1.1893 | 19.1462 | 31.9705 | 392.2214
39049.406 | 2095 | 4 | 39049.406 | 1913 | 10 |  | 1609.5 | 1848.5 | 127.8999 | 0.2442 | 116.7888 | 0.6105 | 1.279 | 0.002442 | 1.1679 | 0.006105 | 1.2766 | 1.1618 | 22.1397 | 34.5769 | 2931.4449
39049.4064 | 1959 | 5 | 39049.4065 | 1930 | 4 |  | 1651.5 | 1890.5 | 119.5971 | 0.30525 | 117.8266 | 0.2442 | 1.196 | 0.0030525 | 1.1783 | 0.002442 | 1.1929 | 1.1758 | 30.7618 | 32.6911 | 2913.9663
39049.4069 | 2021 | 12 | 39049.4069 | 2384 | 14 |  | 1693.5 | 1932.5 | 123.3822 | 0.7326 | 145.5433 | 0.8547 | 1.2338 | 0.007326 | 1.4554 | 0.008547 | 1.2265 | 1.4469 | 28.9411 | 7.3819 | 299.2555
39049.4074 | 2072 | 6 | 39049.4074 | 1967 | 5 |  | 1735.5 | 1974.5 | 126.4957 | 0.3663 | 120.0855 | 0.30525 | 1.265 | 0.003663 | 1.2009 | 0.0030525 | 1.2613 | 1.1978 | 23.6232 | 30.3158 | 1850.9097
39049.4079 | 1907 | 1 | 39049.4079 | 2104 | 1 |  | 1777.5 | 2016.5 | 116.4225 | 0.06105 | 128.4493 | 0.06105 | 1.1642 | 0.0006105 | 1.2845 | 0.0006105 | 1.1636 | 1.2839 | 34.1011 | 21.4936 | 11452.8862
39049.4084 | 2235 | 1 | 39049.4084 | 2023 | 0 |  | 1819.5 | 2058.5 | 136.4469 | 0.06105 | 123.5043 | 0 | 1.3645 | 0.0006105 | 1.235 | 0 | 1.3639 | 1.235 | 14.3655 | 26.3164 | 6653.8646
39049.4089 | 2186 | 0 | 39049.4089 | 1934 | 0 |  | 1861.5 | 2100.5 | 133.4554 | 0 | 118.0708 | 0 | 1.3346 | 0 | 1.1807 | 0 | 1.3346 | 1.1807 | 16.8975 | 32.1293 | 15.563
39049.4094 | 2042 | 0 | 39049.4094 | 2412 | 0 |  | 1903.5 | 2142.5 | 124.6642 | 0 | 147.2527 | 0 | 1.2466 | 0 | 1.4725 | 0 | 1.2466 | 1.4725 | 25.141 | 5.9444 | 23.8944
39049.4098 | 2511 | 0 | 39049.4099 | 2365 | 0 |  | 1945.5 | 2184.5 | 153.2967 | 0 | 144.3834 | 0 | 1.533 | 0 | 1.4438 | 0 | 1.533 | 1.4438 | 1.7674 | 8.0499 | 0.23446
39049.4103 | 2352 | 0 | 39049.4103 | 2502 | 0 |  | 1987.5 | 2226.5 | 143.5897 | 0 | 152.7473 | 0 | 1.4359 | 0 | 1.5275 | 0 | 1.4359 | 1.5275 | 8.6471 | 2.1335 | 7.2112
39049.4108 | 2092 | 0 | 39049.4108 | 2251 | 0 |  | 2029.5 | 2268.5 | 127.7167 | 0 | 137.4237 | 0 | 1.2772 | 0 | 1.3742 | 0 | 1.2772 | 1.3742 | 22.1501 | 13.522 | 20.8729
39049.4113 | 2002 | 0 | 39049.4113 | 2478 | 0 |  | 2071.5 | 2310.5 | 122.2222 | 0 | 151.2821 | 0 | 1.2222 | 0 | 1.5128 | 0 | 1.2222 | 1.5128 | 27.6414 | 3.1227 | 26.4191
39049.4118 | 2004 | 6 | 39049.4118 | 2337 | 7 |  | 2113.5 | 2352.5 | 122.3443 | 0.3663 | 142.674 | 0.42735 | 1.2234 | 0.003663 | 1.4267 | 0.0042735 | 1.2198 | 1.4225 | 28.5001 | 9.4724 | 786.5071
39049.4123 | 1932 | 3 | 39049.4123 | 2043 | 4 |  | 2155.5 | 2394.5 | 117.9487 | 0.18315 | 124.7253 | 0.2442 | 1.1795 | 0.0018315 | 1.2473 | 0.002442 | 1.1777 | 1.2448 | 32.5163 | 25.2815 | 4173.0403
39049.4128 | 1935 | 4 | 39049.4128 | 2225 | 5 |  | 2197.5 | 2436.5 | 118.1319 | 0.2442 | 135.8364 | 0.30525 | 1.1813 | 0.002442 | 1.3584 | 0.0030525 | 1.1789 | 1.3553 | 32.5777 | 14.9856 | 2008.2549
39049.4133 | 2065 | 7 | 39049.4133 | 2323 | 8 |  | 2239.5 | 2478.5 | 126.0684 | 0.42735 | 141.8193 | 0.4884 | 1.2607 | 0.0042735 | 1.4182 | 0.004884 | 1.2564 | 1.4133 | 24.6516 | 10.1807 | 638.0635
39049.4137 | 2376 | 11 | 39049.4137 | 1891 | 8 |  | 2281.5 | 2520.5 | 145.0549 | 0.67155 | 115.4457 | 0.4884 | 1.4505 | 0.0067155 | 1.1545 | 0.004884 | 1.4438 | 1.1496 | 7.6804 | 37.3491 | 416.2478
39049.4142 | 2033 | 13 | 39049.4142 | 2206 | 15 |  | 2323.5 | 2562.5 | 124.1148 | 0.79365 | 134.6764 | 0.91575 | 1.2411 | 0.0079365 | 1.3468 | 0.0091575 | 1.2332 | 1.3376 | 26.9192 | 16.3623 | 550.9726
39049.4147 | 2203 | 18 | 39049.4147 | 2368 | 21 |  | 2365.5 | 2604.5 | 134.4933 | 1.0989 | 144.5665 | 1.2821 | 1.3449 | 0.010989 | 1.4457 | 0.012821 | 1.3339 | 1.4328 | 17.8798 | 8.4044 | 144.0214
39049.4152 | 1881 | 23 | 39049.4152 | 2376 | 28 |  | 2407.5 | 2646.5 | 114.8352 | 1.4042 | 145.0549 | 1.7094 | 1.1484 | 0.014042 | 1.4505 | 0.017094 | 1.1343 | 1.4335 | 43.0838 | 7.8572 | 206.3116
39049.4157 | 1970 | 29 | 39049.4157 | 2182 | 31 |  | 2449.5 | 2688.5 | 120.2686 | 1.7705 | 133.2112 | 1.8926 | 1.2027 | 0.017705 | 1.3321 | 0.018926 | 1.185 | 1.3132 | 32.8632 | 18.1546 | 294.7877
39049.4162 | 1878 | 33 | 39049.4162 | 2142 | 38 |  | 2491.5 | 2730.5 | 114.652 | 2.0147 | 130.7692 | 2.3199 | 1.1465 | 0.020147 | 1.3077 | 0.023199 | 1.1264 | 1.2845 | 40.2106 | 20.5713 | 333.1548
39049.4167 | 2329 | 38 | 39049.4167 | 2210 | 39 |  | 2533.5 | 2772.5 | 142.1856 | 2.3199 | 134.9206 | 2.381 | 1.4219 | 0.023199 | 1.3492 | 0.02381 | 1.3987 | 1.3254 | 10.8223 | 19.0751 | 79.414
39049.4171 | 2171 | 41 | 39049.4172 | 2004 | 40 |  | 2575.5 | 2814.5 | 132.5397 | 2.5031 | 122.3443 | 2.442 | 1.3254 | 0.025031 | 1.2234 | 0.02442 | 1.3004 | 1.199 | 19.2245 | 31.401 | 200.1409
39049.4176 | 1898 | 44 | 39049.4176 | 2151 | 49 |  | 2617.5 | 2856.5 | 115.873 | 2.6862 | 131.3187 | 2.9915 | 1.1587 | 0.026862 | 1.3132 | 0.029915 | 1.1319 | 1.2833 | 40.119 | 20.4246 | 236.4373
39049.4181 | 2270 | 0 | 39049.4181 | 2259 | 0 |  | 2659.5 | 2898.5 | 138.5836 | 0 | 137.9121 | 0 | 1.3858 | 0 | 1.3791 | 0 | 1.3858 | 1.3791 | 12.5718 | 13.12 | 11.186
39049.4186 | 1886 | 76 | 39049.4186 | 2344 | 0 |  | 2701.5 | 2940.5 | 115.1404 | 4.6398 | 143.1013 | 0 | 1.1514 | 0.046398 | 1.431 | 0 | 1.105 | 1.431 | 69.2056 | 9.0179 | 64.5844
39049.4191 | 2287 | 0 | 39049.4191 | 2535 | 0 |  | 2743.5 | 2982.5 | 139.6215 | 0 | 154.7619 | 0 | 1.3962 | 0 | 1.5476 | 0 | 1.3962 | 1.5476 | 11.735 | 0.80394 | 10.3388
39049.4196 | 2485 | 0 | 39049.4196 | 2539 | 0 |  | 2785.5 | 3024.5 | 151.7094 | 0 | 155.0061 | 0 | 1.5171 | 0 | 1.5501 | 0 | 1.5171 | 1.5501 | 2.8322 | 0.64514 | 1.3151
39049.4201 | 2103 | 0 | 39049.4201 | 2301 | 0 |  | 2827.5 | 3066.5 | 128.3883 | 0 | 140.4762 | 0 | 1.2839 | 0 | 1.4048 | 0 | 1.2839 | 1.4048 | 21.5112 | 11.0552 | 20.2273
39049.4205 | 2400 | 0 | 39049.4206 | 2442 | 0 |  | 2869.5 | 3108.5 | 146.5201 | 0 | 149.0842 | 0 | 1.4652 | 0 | 1.4908 | 0 | 1.4652 | 1.4908 | 6.4742 | 4.6429 | 5.009
39049.421 | 2168 | 0 | 39049.421 | 2430 | 0 |  | 2911.5 | 3150.5 | 132.3565 | 0 | 148.3516 | 0 | 1.3236 | 0 | 1.4835 | 0 | 1.3236 | 1.4835 | 17.8681 | 5.1597 | 16.5445
39049.4215 | 2117 | 0 | 39049.4215 | 2280 | 0 |  | 2953.5 | 3192.5 | 129.243 | 0 | 139.1941 | 0 | 1.2924 | 0 | 1.3919 | 0 | 1.2924 | 1.3919 | 20.7076 | 12.0781 | 19.4152

## Raw IRMS Data
Time | DL1.V2000:B | DL1.V2001:B | DL1.V1500:B | Open Burn Test 13 |  |  | 2006-11-28 | 9:21
39049.3846 | 1 | 0 | 1 | Mixed | 7-C | Tray F | IRMS | 1
39049.3851 | 1 | 0 | 1 |  | 150 kW |  | Bundle
39049.3855 | 1 | 0 | 1
39049.386 | 1 | 0 | 1
39049.3865 | 1 | 0 | 1
39049.387 | 1 | 0 | 1
39049.3875 | 1 | 0 | 1
39049.388 | 1 | 0 | 1
39049.3885 | 1 | 0 | 1
39049.3889 | 0 | 0 | 1
39049.3894 | 1 | 0 | 1
39049.3899 | 1 | 0 | 1
39049.3904 | 1 | 0 | 1
39049.3909 | 1 | 0 | 1
39049.3914 | 1 | 0 | 1
39049.3919 | 1 | 0 | 1
39049.3923 | 1 | 0 | 1
39049.3928 | 1 | 0 | 1
39049.3933 | 1 | 0 | 1
39049.3938 | 1 | 0 | 1
39049.3943 | 1 | 0 | 1
39049.3948 | 1 | 0 | 1
39049.3953 | 1 | 0 | 1
39049.3958 | 1 | 0 | 1
39049.3962 | 1 | 0 | 1
39049.3967 | 1 | 0 | 1
39049.3972 | 0 | 0 | 1
39049.3977 | 1 | 0 | 1
39049.3982 | 1 | 0 | 1
39049.3987 | 1 | 0 | 1
39049.3992 | 1 | 0 | 1
39049.3996 | 1 | 0 | 1
39049.4001 | 1 | 0 | 1
39049.4006 | 1 | 0 | 1
39049.4011 | 0 | 0 | 1
39049.4016 | 2 | 0 | 1
39049.4021 | 1110 | 1029 | 1
39049.4026 | 1784 | 267 | 1
39049.403 | 1986 | 17 | 1
39049.4035 | 1966 | 0 | 1
39049.404 | 2273 | 0 | 1
39049.4045 | 2361 | 2 | 1
39049.405 | 2123 | 9 | 1
39049.4055 | 2160 | 23 | 1
39049.406 | 2095 | 4 | 1
39049.4064 | 1959 | 5 | 1
39049.4069 | 2021 | 12 | 1
39049.4074 | 2072 | 6 | 1
39049.4079 | 1907 | 1 | 1
39049.4084 | 2235 | 1 | 1
39049.4089 | 2186 | 0 | 1
39049.4094 | 2042 | 0 | 1
39049.4098 | 2511 | 0 | 1
39049.4103 | 2352 | 0 | 1
39049.4108 | 2092 | 0 | 1
39049.4113 | 2002 | 0 | 1
39049.4118 | 2004 | 6 | 1
39049.4123 | 1932 | 3 | 1
39049.4128 | 1935 | 4 | 1
39049.4133 | 2065 | 7 | 1
39049.4137 | 2376 | 11 | 1
39049.4142 | 2033 | 13 | 1
39049.4147 | 2203 | 18 | 1
39049.4152 | 1881 | 23 | 1
39049.4157 | 1970 | 29 | 1
39049.4162 | 1878 | 33 | 1
39049.4167 | 2329 | 38 | 1
39049.4171 | 2171 | 41 | 1
39049.4176 | 1898 | 44 | 1
39049.4181 | 2270 | 0 | 1
39049.4186 | 1886 | 76 | 1
39049.4191 | 2287 | 0 | 1
39049.4196 | 2485 | 0 | 1
39049.4201 | 2103 | 0 | 1
39049.4205 | 2400 | 0 | 1
39049.421 | 2168 | 0 | 1
39049.4215 | 2117 | 0 | 1
1
39049.3846 | 1 | 0 | 2
39049.3851 | 1 | 0 | 2
39049.3856 | 1 | 0 | 2
39049.3861 | 1 | 0 | 2
39049.3865 | 1 | 0 | 2
39049.387 | 1 | 0 | 2
39049.3875 | 1 | 0 | 2
39049.388 | 1 | 0 | 2
39049.3885 | 1 | 0 | 2
39049.389 | 1 | 0 | 2
39049.3894 | 1 | 0 | 2
39049.3899 | 1 | 0 | 2
39049.3904 | 1 | 0 | 2
39049.3909 | 1 | 0 | 2
39049.3914 | 1 | 0 | 2
39049.3919 | 1 | 0 | 2
39049.3924 | 1 | 0 | 2
39049.3928 | 1 | 0 | 2
39049.3933 | 1 | 0 | 2
39049.3938 | 1 | 0 | 2
39049.3943 | 1 | 0 | 2
39049.3948 | 1 | 0 | 2
39049.3953 | 1 | 0 | 2
39049.3958 | 1 | 0 | 2
39049.3962 | 1 | 0 | 2
39049.3967 | 1 | 0 | 2
39049.3972 | 1 | 0 | 2
39049.3977 | 1 | 0 | 2
39049.3982 | 1 | 0 | 2
39049.3987 | 1 | 0 | 2
39049.3992 | 1 | 0 | 2
39049.3997 | 1 | 0 | 2
39049.4001 | 1 | 0 | 2
39049.4006 | 1 | 0 | 2
39049.4011 | 1 | 0 | 2
39049.4016 | 833 | 0 | 2
39049.4021 | 1123 | 1118 | 2
39049.4026 | 1729 | 146 | 2
39049.4031 | 2226 | 14 | 2
39049.4035 | 2034 | 1 | 2
39049.404 | 2243 | 0 | 2
39049.4045 | 1980 | 4 | 2
39049.405 | 2425 | 9 | 2
39049.4055 | 1971 | 23 | 2
39049.406 | 1913 | 10 | 2
39049.4065 | 1930 | 4 | 2
39049.4069 | 2384 | 14 | 2
39049.4074 | 1967 | 5 | 2
39049.4079 | 2104 | 1 | 2
39049.4084 | 2023 | 0 | 2
39049.4089 | 1934 | 0 | 2
39049.4094 | 2412 | 0 | 2
39049.4099 | 2365 | 0 | 2
39049.4103 | 2502 | 0 | 2
39049.4108 | 2251 | 0 | 2
39049.4113 | 2478 | 0 | 2
39049.4118 | 2337 | 7 | 2
39049.4123 | 2043 | 4 | 2
39049.4128 | 2225 | 5 | 2
39049.4133 | 2323 | 8 | 2
39049.4137 | 1891 | 8 | 2
39049.4142 | 2206 | 15 | 2
39049.4147 | 2368 | 21 | 2
39049.4152 | 2376 | 28 | 2
39049.4157 | 2182 | 31 | 2
39049.4162 | 2142 | 38 | 2
39049.4167 | 2210 | 39 | 2
39049.4172 | 2004 | 40 | 2
39049.4176 | 2151 | 49 | 2
39049.4181 | 2259 | 0 | 2
39049.4186 | 2344 | 0 | 2
39049.4191 | 2535 | 0 | 2
39049.4196 | 2539 | 0 | 2
39049.4201 | 2301 | 0 | 2
39049.4206 | 2442 | 0 | 2
39049.421 | 2430 | 0 | 2
39049.4215 | 2280 | 0 | 2
2
39049.3846 | 0 | 0 | 3
39049.3851 | 1 | 0 | 3
39049.3856 | 1 | 0 | 3
39049.3861 | 1 | 0 | 3
39049.3866 | 1 | 0 | 3
39049.387 | 1 | 0 | 3
39049.3875 | 1 | 0 | 3
39049.388 | 1 | 0 | 3
39049.3885 | 0 | 0 | 3
39049.389 | 1 | 0 | 3
39049.3895 | 1 | 0 | 3
39049.39 | 1 | 0 | 3
39049.3904 | 1 | 0 | 3
39049.3909 | 1 | 0 | 3
39049.3914 | 1 | 0 | 3
39049.3919 | 1 | 0 | 3
39049.3924 | 1 | 0 | 3
39049.3929 | 1 | 0 | 3
39049.3934 | 1 | 0 | 3
39049.3938 | 1 | 0 | 3
39049.3943 | 1 | 0 | 3
39049.3948 | 1 | 0 | 3
39049.3953 | 1 | 0 | 3
39049.3958 | 1 | 0 | 3
39049.3963 | 1 | 0 | 3
39049.3968 | 0 | 0 | 3
39049.3972 | 1 | 0 | 3
39049.3977 | 1 | 0 | 3
39049.3982 | 1 | 0 | 3
39049.3987 | 1 | 0 | 3
39049.3992 | 1 | 0 | 3
39049.3997 | 1 | 0 | 3
39049.4002 | 1 | 0 | 3
39049.4006 | 1 | 0 | 3
39049.4011 | 1 | 0 | 3
39049.4016 | 5 | 0 | 3
39049.4021 | 1485 | 0 | 3
39049.4026 | 2093 | 0 | 3
39049.4031 | 2006 | 0 | 3
39049.4036 | 2326 | 0 | 3
39049.4041 | 2377 | 0 | 3
39049.4045 | 2063 | 0 | 3
39049.405 | 2313 | 0 | 3
39049.4055 | 2045 | 0 | 3
39049.406 | 1905 | 0 | 3
39049.4065 | 2303 | 0 | 3
39049.407 | 1898 | 0 | 3
39049.4075 | 1900 | 0 | 3
39049.4079 | 1929 | 0 | 3
39049.4084 | 2164 | 0 | 3
39049.4089 | 2475 | 0 | 3
39049.4094 | 2496 | 0 | 3
39049.4099 | 2226 | 0 | 3
39049.4104 | 2432 | 0 | 3
39049.4109 | 2452 | 0 | 3
39049.4113 | 1934 | 0 | 3
39049.4118 | 2254 | 0 | 3
39049.4123 | 1933 | 0 | 3
39049.4128 | 1928 | 0 | 3
39049.4133 | 1943 | 0 | 3
39049.4138 | 2031 | 0 | 3
39049.4142 | 2381 | 0 | 3
39049.4147 | 2139 | 0 | 3
39049.4152 | 2159 | 0 | 3
39049.4157 | 2350 | 0 | 3
39049.4162 | 2167 | 0 | 3
39049.4167 | 1964 | 0 | 3
39049.4172 | 1820 | 0 | 3
39049.4177 | 1891 | 0 | 3
39049.4181 | 2491 | 0 | 3
39049.4186 | 2066 | 0 | 3
39049.4191 | 2439 | 0 | 3
39049.4196 | 2369 | 0 | 3
39049.4201 | 2333 | 0 | 3
39049.4206 | 2321 | 0 | 3
39049.4211 | 2339 | 0 | 3
39049.4215 | 2031 | 0 | 3
3
39049.3846 | 1 | 0 | 4
39049.3851 | 1 | 0 | 4
39049.3856 | 1 | 0 | 4
39049.3861 | 0 | 0 | 4
39049.3866 | 1 | 0 | 4
39049.387 | 1 | 0 | 4
39049.3875 | 1 | 0 | 4
39049.388 | 1 | 0 | 4
39049.3885 | 1 | 0 | 4
39049.389 | 1 | 0 | 4
39049.3895 | 1 | 0 | 4
39049.39 | 1 | 0 | 4
39049.3905 | 1 | 0 | 4
39049.3909 | 1 | 0 | 4
39049.3914 | 1 | 0 | 4
39049.3919 | 1 | 0 | 4
39049.3924 | 1 | 0 | 4
39049.3929 | 0 | 0 | 4
39049.3934 | 1 | 0 | 4
39049.3939 | 1 | 0 | 4
39049.3943 | 1 | 0 | 4
39049.3948 | 1 | 0 | 4
39049.3953 | 1 | 0 | 4
39049.3958 | 1 | 0 | 4
39049.3963 | 1 | 0 | 4
39049.3968 | 1 | 0 | 4
39049.3973 | 1 | 0 | 4
39049.3977 | 0 | 0 | 4
39049.3982 | 1 | 0 | 4
39049.3987 | 15 | 0 | 4
39049.3992 | 2176 | 0 | 4
39049.3997 | 2315 | 0 | 4
39049.4007 | 2138 | 0 | 4
39049.4011 | 1997 | 0 | 4
39049.4016 | 2083 | 0 | 4
39049.4021 | 2172 | 0 | 4
39049.4026 | 1621 | 0 | 4
39049.4031 | 1938 | 0 | 4
39049.4036 | 2382 | 0 | 4
39049.4041 | 2087 | 0 | 4
39049.4045 | 2180 | 0 | 4
39049.405 | 2435 | 0 | 4
39049.4055 | 2332 | 0 | 4
39049.406 | 2377 | 0 | 4
39049.4065 | 2330 | 0 | 4
39049.407 | 2392 | 0 | 4
39049.4075 | 2170 | 0 | 4
39049.408 | 2168 | 0 | 4
39049.4084 | 2160 | 0 | 4
39049.4089 | 2011 | 0 | 4
39049.4094 | 2001 | 0 | 4
39049.4099 | 2016 | 0 | 4
39049.4104 | 2162 | 0 | 4
39049.4109 | 2551 | 0 | 4
39049.4114 | 2213 | 0 | 4
39049.4118 | 2110 | 0 | 4
39049.4123 | 1979 | 0 | 4
39049.4128 | 2151 | 0 | 4
39049.4133 | 2061 | 0 | 4
39049.4138 | 2422 | 0 | 4
39049.4143 | 2488 | 0 | 4
39049.4148 | 2494 | 0 | 4
39049.4152 | 2139 | 0 | 4
39049.4157 | 2162 | 0 | 4
39049.4162 | 2320 | 0 | 4
39049.4167 | 2096 | 0 | 4
39049.4172 | 2126 | 1 | 4
39049.4177 | 2339 | 0 | 4
39049.4182 | 2367 | 0 | 4
39049.4186 | 1972 | 0 | 4
39049.4191 | 2548 | 0 | 4
39049.4196 | 2487 | 0 | 4
39049.4201 | 2131 | 0 | 4
39049.4206 | 2139 | 0 | 4
39049.4211 | 2074 | 0 | 4
39049.4216 | 1954 | 0 | 4
4
39049.3846 | 1 | 0 | 5
39049.3851 | 1 | 0 | 5
39049.3856 | 1 | 0 | 5
39049.3861 | 1 | 0 | 5
39049.3866 | 1 | 0 | 5
39049.3871 | 1 | 0 | 5
39049.3876 | 1 | 0 | 5
39049.388 | 0 | 0 | 5
39049.3885 | 1 | 0 | 5
39049.389 | 1 | 0 | 5
39049.3895 | 1 | 0 | 5
39049.39 | 1 | 0 | 5
39049.3905 | 1 | 0 | 5
39049.391 | 1 | 0 | 5
39049.3914 | 1 | 0 | 5
39049.3919 | 1 | 0 | 5
39049.3924 | 1 | 0 | 5
39049.3929 | 1 | 0 | 5
39049.3934 | 1 | 0 | 5
39049.3939 | 1 | 0 | 5
39049.3944 | 1 | 0 | 5
39049.3948 | 1 | 0 | 5
39049.3953 | 1 | 0 | 5
39049.3958 | 1 | 0 | 5
39049.3963 | 1 | 0 | 5
39049.3968 | 1 | 0 | 5
39049.3973 | 1 | 0 | 5
39049.3978 | 1 | 0 | 5
39049.3982 | 1 | 0 | 5
39049.3987 | 1 | 0 | 5
39049.3992 | 1 | 0 | 5
39049.3997 | 1 | 0 | 5
39049.4002 | 1 | 0 | 5
39049.4007 | 1 | 0 | 5
39049.4012 | 1 | 0 | 5
39049.4016 | 8 | 0 | 5
39049.4021 | 1374 | 0 | 5
39049.4026 | 2335 | 0 | 5
39049.4031 | 2423 | 0 | 5
39049.4036 | 2315 | 0 | 5
39049.4041 | 2186 | 0 | 5
39049.4046 | 2210 | 0 | 5
39049.405 | 2239 | 0 | 5
39049.4055 | 1938 | 0 | 5
39049.406 | 2105 | 0 | 5
39049.4065 | 2328 | 0 | 5
39049.407 | 1980 | 0 | 5
39049.4075 | 2156 | 0 | 5
39049.408 | 2406 | 0 | 5
39049.4084 | 2135 | 0 | 5
39049.4089 | 2165 | 0 | 5
39049.4094 | 1920 | 0 | 5
39049.4099 | 2083 | 0 | 5
39049.4104 | 2005 | 0 | 5
39049.4109 | 2506 | 0 | 5
39049.4114 | 2081 | 0 | 5
39049.4119 | 2186 | 0 | 5
39049.4123 | 2214 | 0 | 5
39049.4128 | 1899 | 0 | 5
39049.4133 | 2345 | 0 | 5
39049.4138 | 2325 | 0 | 5
39049.4143 | 2030 | 0 | 5
39049.4148 | 2077 | 0 | 5
39049.4153 | 1947 | 0 | 5
39049.4157 | 2354 | 0 | 5
39049.4162 | 2293 | 0 | 5
39049.4167 | 2000 | 0 | 5
39049.4172 | 2331 | 0 | 5
39049.4177 | 2150 | 0 | 5
39049.4182 | 2148 | 0 | 5
39049.4187 | 2357 | 0 | 5
39049.4191 | 2464 | 0 | 5
39049.4196 | 2152 | 0 | 5
39049.4201 | 2123 | 0 | 5
39049.4206 | 2447 | 0 | 5
39049.4211 | 2210 | 0 | 5
39049.4216 | 2145 | 0 | 5
5
39049.3847 | 1 | 0 | 6
39049.3851 | 1 | 0 | 6
39049.3856 | 1 | 0 | 6
39049.3861 | 1 | 0 | 6
39049.3866 | 1 | 0 | 6
39049.3871 | 1 | 0 | 6
39049.3876 | 1 | 0 | 6
39049.3881 | 1 | 0 | 6
39049.3885 | 1 | 0 | 6
39049.389 | 1 | 0 | 6
39049.3895 | 1 | 0 | 6
39049.39 | 1 | 0 | 6
39049.3905 | 1 | 0 | 6
39049.391 | 1 | 0 | 6
39049.3915 | 1 | 0 | 6
39049.3919 | 1 | 0 | 6
39049.3924 | 1 | 0 | 6
39049.3929 | 1 | 0 | 6
39049.3934 | 1 | 0 | 6
39049.3939 | 1 | 0 | 6
39049.3944 | 1 | 0 | 6
39049.3949 | 1 | 0 | 6
39049.3953 | 1 | 0 | 6
39049.3958 | 1 | 0 | 6
39049.3963 | 1 | 0 | 6
39049.3968 | 1 | 0 | 6
39049.3973 | 1 | 0 | 6
39049.3978 | 1 | 0 | 6
39049.3983 | 1 | 0 | 6
39049.3988 | 2094 | 0 | 6
39049.3992 | 2307 | 0 | 6
39049.3997 | 2457 | 0 | 6
39049.4002 | 2067 | 0 | 6
39049.4007 | 2276 | 0 | 6
39049.4012 | 1926 | 0 | 6
39049.4017 | 2073 | 0 | 6
39049.4022 | 2277 | 0 | 6
39049.4026 | 1983 | 0 | 6
39049.4031 | 2247 | 0 | 6
39049.4036 | 2470 | 0 | 6
39049.4041 | 2444 | 0 | 6
39049.4046 | 2500 | 0 | 6
39049.4051 | 2322 | 0 | 6
39049.4056 | 2107 | 0 | 6
39049.406 | 1957 | 0 | 6
39049.4065 | 2122 | 0 | 6
39049.407 | 2214 | 0 | 6
39049.4075 | 2130 | 0 | 6
39049.408 | 2582 | 0 | 6
39049.4085 | 2064 | 0 | 6
39049.409 | 1998 | 0 | 6
39049.4094 | 2044 | 0 | 6
39049.4099 | 2513 | 0 | 6
39049.4104 | 2581 | 0 | 6
39049.4109 | 2490 | 0 | 6
39049.4114 | 2128 | 0 | 6
39049.4119 | 2505 | 0 | 6
39049.4124 | 2274 | 0 | 6
39049.4128 | 2186 | 0 | 6
39049.4133 | 2457 | 0 | 6
39049.4138 | 2025 | 0 | 6
39049.4143 | 2214 | 0 | 6
39049.4148 | 1980 | 0 | 6
39049.4153 | 2544 | 0 | 6
39049.4158 | 1974 | 0 | 6
39049.4163 | 2535 | 0 | 6
39049.4167 | 2247 | 0 | 6
39049.4172 | 2345 | 0 | 6
39049.4177 | 1999 | 0 | 6
39049.4182 | 2211 | 0 | 6
39049.4187 | 2444 | 0 | 6
39049.4192 | 1967 | 0 | 6
39049.4197 | 2100 | 0 | 6
39049.4201 | 2534 | 0 | 6
39049.4206 | 2521 | 0 | 6
39049.4211 | 2073 | 0 | 6
39049.4216 | 2281 | 0 | 6
6
39049.3847 | 1 | 0 | 7
39049.3852 | 1 | 0 | 7
39049.3856 | 0 | 0 | 7
39049.3861 | 1 | 0 | 7
39049.3866 | 1 | 0 | 7
39049.3871 | 0 | 0 | 7
39049.3876 | 1 | 0 | 7
39049.3881 | 1 | 0 | 7
39049.3886 | 1 | 0 | 7
39049.389 | 1 | 0 | 7
39049.3895 | 1 | 0 | 7
39049.39 | 1 | 0 | 7
39049.3905 | 1 | 0 | 7
39049.391 | 1 | 0 | 7
39049.3915 | 1 | 0 | 7
39049.392 | 1 | 0 | 7
39049.3924 | 1 | 0 | 7
39049.3929 | 1 | 0 | 7
39049.3934 | 1 | 0 | 7
39049.3939 | 1 | 0 | 7
39049.3944 | 1 | 0 | 7
39049.3949 | 1 | 0 | 7
39049.3954 | 1 | 0 | 7
39049.3958 | 1 | 0 | 7
39049.3963 | 0 | 0 | 7
39049.3968 | 1 | 0 | 7
39049.3973 | 1 | 0 | 7
39049.3978 | 1 | 0 | 7
39049.3983 | 1 | 0 | 7
39049.3988 | 1 | 0 | 7
39049.3992 | 1 | 0 | 7
39049.3997 | 1 | 0 | 7
39049.4002 | 1 | 0 | 7
39049.4007 | 1 | 0 | 7
39049.4012 | 1 | 0 | 7
39049.4017 | 25 | 0 | 7
39049.4022 | 45 | 0 | 7
39049.4027 | 2352 | 0 | 7
39049.4031 | 2416 | 0 | 7
39049.4036 | 2110 | 0 | 7
39049.4041 | 2212 | 0 | 7
39049.4046 | 2097 | 0 | 7
39049.4051 | 1882 | 0 | 7
39049.4056 | 2043 | 0 | 7
39049.4061 | 2153 | 0 | 7
39049.4065 | 2311 | 0 | 7
39049.407 | 1985 | 0 | 7
39049.4075 | 1865 | 0 | 7
39049.408 | 1958 | 0 | 7
39049.4085 | 1978 | 0 | 7
39049.409 | 2462 | 0 | 7
39049.4095 | 2207 | 0 | 7
39049.4099 | 2085 | 0 | 7
39049.4104 | 2049 | 0 | 7
39049.4109 | 2502 | 0 | 7
39049.4114 | 2139 | 0 | 7
39049.4119 | 1862 | 0 | 7
39049.4124 | 1919 | 0 | 7
39049.4129 | 2361 | 0 | 7
39049.4133 | 2031 | 0 | 7
39049.4138 | 1985 | 0 | 7
39049.4143 | 2028 | 0 | 7
39049.4148 | 2361 | 0 | 7
39049.4153 | 2233 | 0 | 7
39049.4158 | 2136 | 0 | 7
39049.4163 | 1865 | 0 | 7
39049.4167 | 1992 | 0 | 7
39049.4172 | 1929 | 1 | 7
39049.4177 | 1972 | 0 | 7
39049.4182 | 1963 | 0 | 7
39049.4187 | 2119 | 0 | 7
39049.4192 | 2344 | 0 | 7
39049.4197 | 2528 | 0 | 7
39049.4202 | 2069 | 0 | 7
39049.4206 | 2497 | 0 | 7
39049.4211 | 2155 | 0 | 7
39049.4216 | 2221 | 0 | 7
7
39049.3847 | 1 | 0 | 8
39049.3852 | 1 | 0 | 8
39049.3857 | 1 | 0 | 8
39049.3861 | 1 | 0 | 8
39049.3866 | 1 | 0 | 8
39049.3871 | 1 | 0 | 8
39049.3876 | 1 | 0 | 8
39049.3881 | 1 | 0 | 8
39049.3886 | 1 | 0 | 8
39049.3891 | 1 | 0 | 8
39049.3895 | 1 | 0 | 8
39049.39 | 1 | 0 | 8
39049.3905 | 1 | 0 | 8
39049.391 | 1 | 0 | 8
39049.3915 | 1 | 0 | 8
39049.392 | 1 | 0 | 8
39049.3925 | 1 | 0 | 8
39049.393 | 1 | 0 | 8
39049.3934 | 1 | 0 | 8
39049.3939 | 1 | 0 | 8
39049.3944 | 1 | 0 | 8
39049.3949 | 1 | 0 | 8
39049.3954 | 1 | 0 | 8
39049.3959 | 1 | 0 | 8
39049.3964 | 1 | 0 | 8
39049.3968 | 1 | 1 | 8
39049.3973 | 1 | 0 | 8
39049.3978 | 1 | 0 | 8
39049.3983 | 1 | 0 | 8
39049.3988 | 1 | 0 | 8
39049.3993 | 1 | 0 | 8
39049.3998 | 0 | 0 | 8
39049.4002 | 1 | 0 | 8
39049.4007 | 1 | 0 | 8
39049.4012 | 1 | 0 | 8
39049.4017 | 1 | 0 | 8
39049.4022 | 1 | 0 | 8
39049.4027 | 1 | 0 | 8
39049.4032 | 1 | 0 | 8
39049.4036 | 1 | 0 | 8
39049.4041 | 1 | 0 | 8
39049.4046 | 1 | 0 | 8
39049.4051 | 1 | 0 | 8
39049.4056 | 1 | 0 | 8
39049.4061 | 1 | 0 | 8
39049.4066 | 1 | 0 | 8
39049.407 | 1 | 0 | 8
39049.4075 | 1 | 0 | 8
39049.408 | 1 | 0 | 8
39049.4085 | 1 | 0 | 8
39049.409 | 1 | 0 | 8
39049.4095 | 1 | 0 | 8
39049.41 | 1 | 0 | 8
39049.4105 | 2 | 0 | 8
39049.4109 | 1 | 0 | 8
39049.4114 | 1 | 0 | 8
39049.4119 | 1 | 0 | 8
39049.4124 | 6 | 0 | 8
39049.4129 | 16 | 0 | 8
39049.4134 | 34 | 0 | 8
39049.4139 | 33 | 0 | 8
39049.4143 | 35 | 0 | 8
39049.4148 | 19 | 0 | 8
39049.4153 | 23 | 0 | 8
39049.4158 | 17 | 0 | 8
39049.4163 | 19 | 0 | 8
39049.4168 | 11 | 0 | 8
39049.4172 | 23 | 0 | 8
39049.4177 | 27 | 0 | 8
39049.4182 | 25 | 0 | 8
39049.4187 | 17 | 0 | 8
39049.4192 | 16 | 0 | 8
39049.4197 | 12 | 0 | 8
39049.4202 | 9 | 0 | 8
39049.4206 | 9 | 0 | 8
39049.4211 | 8 | 0 | 8
39049.4216 | 5 | 0 | 8
8
39049.3847 | 1 | 0 | 9
39049.3852 | 1 | 0 | 9
39049.3857 | 0 | 0 | 9
39049.3862 | 1 | 0 | 9
39049.3866 | 1 | 1 | 9
39049.3871 | 1 | 0 | 9
39049.3876 | 1 | 0 | 9
39049.3881 | 1 | 0 | 9
39049.3886 | 1 | 0 | 9
39049.3891 | 1 | 0 | 9
39049.3896 | 1 | 0 | 9
39049.39 | 1 | 0 | 9
39049.3905 | 1 | 0 | 9
39049.391 | 1 | 0 | 9
39049.3915 | 1 | 0 | 9
39049.392 | 1 | 0 | 9
39049.3925 | 1 | 0 | 9
39049.393 | 1 | 0 | 9
39049.3934 | 1 | 0 | 9
39049.3939 | 1 | 0 | 9
39049.3944 | 1 | 0 | 9
39049.3949 | 1 | 0 | 9
39049.3954 | 1 | 0 | 9
39049.3959 | 1 | 0 | 9
39049.3964 | 1 | 0 | 9
39049.3969 | 1 | 0 | 9
39049.3973 | 0 | 0 | 9
39049.3978 | 1 | 0 | 9
39049.3983 | 0 | 0 | 9
39049.3988 | 1 | 0 | 9
39049.3993 | 1 | 0 | 9
39049.3998 | 1 | 0 | 9
39049.4003 | 1 | 0 | 9
39049.4007 | 1 | 0 | 9
39049.4012 | 1 | 0 | 9
39049.4017 | 25 | 0 | 9
39049.4022 | 235 | 0 | 9
39049.4027 | 2351 | 0 | 9
39049.4032 | 2431 | 0 | 9
39049.4037 | 2450 | 0 | 9
39049.4041 | 2306 | 0 | 9
39049.4046 | 1927 | 0 | 9
39049.4051 | 1900 | 0 | 9
39049.4056 | 2390 | 0 | 9
39049.4061 | 2418 | 0 | 9
39049.4066 | 1949 | 0 | 9
39049.4071 | 2241 | 0 | 9
39049.4075 | 2037 | 0 | 9
39049.408 | 2270 | 0 | 9
39049.4085 | 2452 | 0 | 9
39049.409 | 2357 | 0 | 9
39049.4095 | 2466 | 0 | 9
39049.41 | 2514 | 0 | 9
39049.4105 | 2072 | 0 | 9
39049.4109 | 2048 | 0 | 9
39049.4114 | 2261 | 0 | 9
39049.4119 | 2201 | 0 | 9
39049.4124 | 2006 | 0 | 9
39049.4129 | 2326 | 0 | 9
39049.4134 | 1930 | 0 | 9
39049.4139 | 1870 | 0 | 9
39049.4144 | 2302 | 0 | 9
39049.4148 | 2076 | 0 | 9
39049.4153 | 1998 | 0 | 9
39049.4158 | 2207 | 0 | 9
39049.4163 | 1893 | 0 | 9
39049.4168 | 2055 | 0 | 9
39049.4173 | 1938 | 0 | 9
39049.4178 | 2191 | 0 | 9
39049.4182 | 2366 | 0 | 9
39049.4187 | 2171 | 0 | 9
39049.4192 | 2040 | 0 | 9
39049.4197 | 2547 | 0 | 9
39049.4202 | 2056 | 0 | 9
39049.4207 | 2093 | 0 | 9
39049.4212 | 2506 | 0 | 9
39049.4216 | 2515 | 0 | 9
9
39049.3847 | 0 | 0 | 10
39049.3852 | 1 | 0 | 10
39049.3857 | 1 | 0 | 10
39049.3862 | 1 | 0 | 10
39049.3867 | 1 | 0 | 10
39049.3872 | 1 | 0 | 10
39049.3876 | 1 | 0 | 10
39049.3881 | 1 | 0 | 10
39049.3886 | 1 | 0 | 10
39049.3891 | 0 | 0 | 10
39049.3896 | 0 | 0 | 10
39049.3901 | 1 | 0 | 10
39049.3906 | 1 | 0 | 10
39049.391 | 1 | 0 | 10
39049.3915 | 1 | 0 | 10
39049.392 | 1 | 0 | 10
39049.3925 | 1 | 0 | 10
39049.393 | 1 | 0 | 10
39049.3935 | 1 | 0 | 10
39049.394 | 1 | 0 | 10
39049.3944 | 1 | 0 | 10
39049.3949 | 1 | 0 | 10
39049.3954 | 1 | 0 | 10
39049.3959 | 0 | 0 | 10
39049.3964 | 1 | 0 | 10
39049.3969 | 0 | 0 | 10
39049.3974 | 1 | 0 | 10
39049.3978 | 1 | 0 | 10
39049.3983 | 1 | 0 | 10
39049.3988 | 1 | 0 | 10
39049.3993 | 1 | 0 | 10
39049.3998 | 1 | 0 | 10
39049.4003 | 1 | 0 | 10
39049.4008 | 1 | 0 | 10
39049.4012 | 1 | 0 | 10
39049.4017 | 1 | 0 | 10
39049.4022 | 1 | 0 | 10
39049.4027 | 1 | 0 | 10
39049.4032 | 1 | 0 | 10
39049.4037 | 1 | 0 | 10
39049.4042 | 1 | 0 | 10
39049.4046 | 1 | 0 | 10
39049.4051 | 2 | 0 | 10
39049.4056 | 1 | 0 | 10
39049.4061 | 1 | 0 | 10
39049.4066 | 1 | 0 | 10
39049.4071 | 1 | 0 | 10
39049.4076 | 1 | 0 | 10
39049.408 | 1 | 0 | 10
39049.4085 | 1 | 0 | 10
39049.409 | 1 | 0 | 10
39049.4095 | 1 | 0 | 10
39049.41 | 1 | 0 | 10
39049.4105 | 1 | 0 | 10
39049.411 | 1 | 0 | 10
39049.4114 | 1 | 0 | 10
39049.4119 | 1 | 0 | 10
39049.4124 | 72 | 0 | 10
39049.4129 | 111 | 0 | 10
39049.4134 | 146 | 0 | 10
39049.4139 | 112 | 0 | 10
39049.4144 | 100 | 0 | 10
39049.4148 | 117 | 0 | 10
39049.4153 | 71 | 0 | 10
39049.4158 | 63 | 0 | 10
39049.4163 | 60 | 0 | 10
39049.4168 | 40 | 0 | 10
39049.4173 | 46 | 0 | 10
39049.4178 | 40 | 0 | 10
39049.4183 | 29 | 0 | 10
39049.4187 | 25 | 0 | 10
39049.4192 | 19 | 0 | 10
39049.4197 | 15 | 0 | 10
39049.4202 | 7 | 0 | 10
39049.4207 | 3 | 0 | 10
39049.4212 | 2 | 0 | 10
39049.4217 | 2 | 0 | 10
10
39049.3847 | 1 | 0 | 11
39049.3852 | 1 | 0 | 11
39049.3857 | 1 | 0 | 11
39049.3862 | 1 | 0 | 11
39049.3867 | 1 | 0 | 11
39049.3872 | 1 | 0 | 11
39049.3877 | 1 | 0 | 11
39049.3881 | 1 | 0 | 11
39049.3886 | 1 | 0 | 11
39049.3891 | 0 | 0 | 11
39049.3896 | 1 | 0 | 11
39049.3901 | 1 | 0 | 11
39049.3906 | 1 | 0 | 11
39049.3911 | 1 | 0 | 11
39049.3915 | 1 | 0 | 11
39049.392 | 1 | 0 | 11
39049.3925 | 1 | 0 | 11
39049.393 | 0 | 0 | 11
39049.3935 | 1 | 0 | 11
39049.394 | 1 | 0 | 11
39049.3945 | 1 | 0 | 11
39049.3949 | 1 | 0 | 11
39049.3954 | 1 | 0 | 11
39049.3959 | 1 | 0 | 11
39049.3964 | 1 | 0 | 11
39049.3969 | 1 | 0 | 11
39049.3974 | 1 | 0 | 11
39049.3979 | 1 | 0 | 11
39049.3983 | 1 | 0 | 11
39049.3988 | 1 | 0 | 11
39049.3993 | 1 | 0 | 11
39049.3998 | 1 | 0 | 11
39049.4003 | 1 | 0 | 11
39049.4008 | 1 | 0 | 11
39049.4013 | 1 | 0 | 11
39049.4017 | 1488 | 0 | 11
39049.4022 | 356 | 0 | 11
39049.4027 | 2259 | 0 | 11
39049.4032 | 2115 | 0 | 11
39049.4037 | 2324 | 0 | 11
39049.4042 | 1926 | 0 | 11
39049.4047 | 2018 | 0 | 11
39049.4052 | 2104 | 0 | 11
39049.4056 | 2273 | 0 | 11
39049.4061 | 2385 | 0 | 11
39049.4066 | 1980 | 0 | 11
39049.4071 | 2355 | 0 | 11
39049.4076 | 2214 | 0 | 11
39049.4081 | 2281 | 0 | 11
39049.4086 | 2356 | 0 | 11
39049.409 | 2366 | 0 | 11
39049.4095 | 2183 | 0 | 11
39049.41 | 2491 | 0 | 11
39049.4105 | 2084 | 0 | 11
39049.411 | 2388 | 0 | 11
39049.4115 | 2169 | 0 | 11
39049.412 | 1884 | 0 | 11
39049.4124 | 2227 | 0 | 11
39049.4129 | 2287 | 0 | 11
39049.4134 | 2260 | 0 | 11
39049.4139 | 1904 | 0 | 11
39049.4144 | 1929 | 0 | 11
39049.4149 | 2166 | 0 | 11
39049.4154 | 2307 | 0 | 11
39049.4158 | 2194 | 0 | 11
39049.4163 | 1971 | 0 | 11
39049.4168 | 2362 | 0 | 11
39049.4173 | 1978 | 0 | 11
39049.4178 | 1840 | 0 | 11
39049.4183 | 2562 | 0 | 11
39049.4188 | 2431 | 0 | 11
39049.4192 | 2345 | 0 | 11
39049.4197 | 2321 | 0 | 11
39049.4202 | 2120 | 0 | 11
39049.4207 | 2510 | 0 | 11
39049.4212 | 2236 | 0 | 11
39049.4217 | 2496 | 0 | 11
11
39049.3848 | 1 | 0 | 12
39049.3852 | 1 | 0 | 12
39049.3857 | 1 | 0 | 12
39049.3862 | 1 | 0 | 12
39049.3867 | 1 | 0 | 12
39049.3872 | 1 | 0 | 12
39049.3877 | 1 | 0 | 12
39049.3881 | 1 | 0 | 12
39049.3886 | 1 | 0 | 12
39049.3891 | 1 | 0 | 12
39049.3896 | 1 | 0 | 12
39049.3901 | 1 | 0 | 12
39049.3906 | 1 | 0 | 12
39049.3911 | 1 | 0 | 12
39049.3916 | 1 | 0 | 12
39049.392 | 1 | 0 | 12
39049.3925 | 1 | 0 | 12
39049.393 | 1 | 0 | 12
39049.3935 | 1 | 0 | 12
39049.394 | 1 | 0 | 12
39049.3945 | 0 | 0 | 12
39049.395 | 1 | 0 | 12
39049.3954 | 1 | 0 | 12
39049.3959 | 1 | 0 | 12
39049.3964 | 1 | 0 | 12
39049.3969 | 1 | 0 | 12
39049.3974 | 1 | 0 | 12
39049.3979 | 1 | 0 | 12
39049.3984 | 1 | 0 | 12
39049.3988 | 2036 | 0 | 12
39049.3993 | 2030 | 0 | 12
39049.3998 | 2422 | 0 | 12
39049.4003 | 1898 | 0 | 12
39049.4008 | 2050 | 0 | 12
39049.4013 | 2386 | 0 | 12
39049.4018 | 2384 | 0 | 12
39049.4022 | 2337 | 0 | 12
39049.4027 | 1551 | 0 | 12
39049.4032 | 1964 | 0 | 12
39049.4037 | 1995 | 0 | 12
39049.4042 | 1967 | 0 | 12
39049.4047 | 2351 | 0 | 12
39049.4052 | 2479 | 0 | 12
39049.4056 | 2244 | 0 | 12
39049.4061 | 2434 | 0 | 12
39049.4066 | 2187 | 0 | 12
39049.4071 | 2009 | 0 | 12
39049.4076 | 2092 | 0 | 12
39049.4081 | 2564 | 0 | 12
39049.4086 | 2386 | 0 | 12
39049.4091 | 2298 | 0 | 12
39049.4095 | 2384 | 0 | 12
39049.41 | 2569 | 0 | 12
39049.4105 | 2557 | 0 | 12
39049.411 | 2001 | 0 | 12
39049.4115 | 2047 | 0 | 12
39049.412 | 2060 | 0 | 12
39049.4125 | 2398 | 0 | 12
39049.4129 | 2207 | 0 | 12
39049.4134 | 2000 | 0 | 12
39049.4139 | 2037 | 0 | 12
39049.4144 | 2050 | 0 | 12
39049.4149 | 2367 | 0 | 12
39049.4154 | 2555 | 0 | 12
39049.4159 | 2027 | 0 | 12
39049.4163 | 2297 | 0 | 12
39049.4168 | 2007 | 0 | 12
39049.4173 | 2145 | 0 | 12
39049.4178 | 2482 | 0 | 12
39049.4183 | 2032 | 0 | 12
39049.4188 | 2256 | 0 | 12
39049.4193 | 2547 | 0 | 12
39049.4197 | 2046 | 0 | 12
39049.4202 | 2213 | 0 | 12
39049.4207 | 2440 | 0 | 12
39049.4212 | 2447 | 0 | 12
39049.4217 | 1960 | 0 | 12
12
39049.3848 | 1 | 0 | 13
39049.3853 | 1 | 0 | 13
39049.3857 | 1 | 0 | 13
39049.3862 | 1 | 0 | 13
39049.3867 | 1 | 0 | 13
39049.3872 | 1 | 0 | 13
39049.3877 | 1 | 0 | 13
39049.3882 | 1 | 0 | 13
39049.3887 | 1 | 0 | 13
39049.3891 | 1 | 0 | 13
39049.3896 | 0 | 0 | 13
39049.3901 | 1 | 0 | 13
39049.3906 | 1 | 0 | 13
39049.3911 | 1 | 0 | 13
39049.3916 | 1 | 0 | 13
39049.3921 | 1 | 0 | 13
39049.3925 | 1 | 0 | 13
39049.393 | 1 | 0 | 13
39049.3935 | 0 | 0 | 13
39049.394 | 1 | 0 | 13
39049.3945 | 1 | 0 | 13
39049.395 | 1 | 0 | 13
39049.3955 | 1 | 0 | 13
39049.3959 | 1 | 0 | 13
39049.3964 | 1 | 0 | 13
39049.3969 | 1 | 0 | 13
39049.3974 | 1 | 0 | 13
39049.3979 | 1 | 0 | 13
39049.3984 | 1 | 0 | 13
39049.3989 | 1 | 0 | 13
39049.3994 | 1 | 0 | 13
39049.3998 | 1 | 0 | 13
39049.4003 | 1 | 0 | 13
39049.4008 | 1 | 0 | 13
39049.4013 | 1 | 0 | 13
39049.4018 | 32 | 0 | 13
39049.4023 | 258 | 0 | 13
39049.4028 | 1997 | 0 | 13
39049.4032 | 2195 | 0 | 13
39049.4037 | 2072 | 0 | 13
39049.4042 | 2492 | 0 | 13
39049.4047 | 2248 | 0 | 13
39049.4052 | 1888 | 0 | 13
39049.4057 | 1900 | 0 | 13
39049.4062 | 2002 | 0 | 13
39049.4066 | 1930 | 0 | 13
39049.4071 | 2153 | 0 | 13
39049.4076 | 2328 | 0 | 13
39049.4081 | 1916 | 0 | 13
39049.4086 | 2334 | 0 | 13
39049.4091 | 2132 | 0 | 13
39049.4096 | 2457 | 0 | 13
39049.41 | 1956 | 0 | 13
39049.4105 | 2464 | 0 | 13
39049.411 | 2386 | 0 | 13
39049.4115 | 2048 | 0 | 13
39049.412 | 2377 | 0 | 13
39049.4125 | 1981 | 0 | 13
39049.413 | 1999 | 0 | 13
39049.4134 | 2402 | 0 | 13
39049.4139 | 2097 | 0 | 13
39049.4144 | 2270 | 0 | 13
39049.4149 | 2117 | 0 | 13
39049.4154 | 2275 | 0 | 13
39049.4159 | 2299 | 0 | 13
39049.4164 | 2307 | 0 | 13
39049.4169 | 2068 | 0 | 13
39049.4173 | 2088 | 0 | 13
39049.4178 | 1811 | 0 | 13
39049.4183 | 1961 | 0 | 13
39049.4188 | 2525 | 0 | 13
39049.4193 | 2355 | 0 | 13
39049.4198 | 2300 | 0 | 13
39049.4202 | 2436 | 0 | 13
39049.4207 | 2248 | 0 | 13
39049.4212 | 2178 | 0 | 13
39049.4217 | 2252 | 0 | 13
13
39049.3848 | 1 | 0 | 14
39049.3853 | 1 | 0 | 14
39049.3858 | 1 | 0 | 14
39049.3862 | 1 | 0 | 14
39049.3867 | 1 | 0 | 14
39049.3872 | 1 | 0 | 14
39049.3877 | 1 | 0 | 14
39049.3882 | 1 | 0 | 14
39049.3887 | 1 | 0 | 14
39049.3892 | 0 | 0 | 14
39049.3896 | 1 | 0 | 14
39049.3901 | 0 | 0 | 14
39049.3906 | 1 | 0 | 14
39049.3911 | 1 | 0 | 14
39049.3916 | 1 | 0 | 14
39049.3921 | 1 | 0 | 14
39049.3926 | 1 | 0 | 14
39049.393 | 1 | 0 | 14
39049.3935 | 1 | 0 | 14
39049.394 | 1 | 0 | 14
39049.3945 | 0 | 0 | 14
39049.395 | 1 | 0 | 14
39049.3955 | 1 | 0 | 14
39049.396 | 1 | 0 | 14
39049.3964 | 1 | 0 | 14
39049.3969 | 1 | 0 | 14
39049.3974 | 1 | 0 | 14
39049.3979 | 1 | 0 | 14
39049.3984 | 1 | 0 | 14
39049.3989 | 1 | 0 | 14
39049.3994 | 1 | 0 | 14
39049.3998 | 1 | 0 | 14
39049.4003 | 1 | 0 | 14
39049.4008 | 1 | 0 | 14
39049.4013 | 1 | 0 | 14
39049.4018 | 1739 | 0 | 14
39049.4023 | 289 | 0 | 14
39049.4028 | 2101 | 0 | 14
39049.4033 | 2060 | 0 | 14
39049.4037 | 2480 | 0 | 14
39049.4042 | 2017 | 0 | 14
39049.4047 | 2336 | 0 | 14
39049.4052 | 2364 | 0 | 14
39049.4057 | 2026 | 0 | 14
39049.4062 | 2106 | 0 | 14
39049.4067 | 1947 | 0 | 14
39049.4071 | 2008 | 0 | 14
39049.4076 | 2170 | 0 | 14
39049.4081 | 1955 | 0 | 14
39049.4086 | 2314 | 0 | 14
39049.4091 | 2065 | 0 | 14
39049.4096 | 1961 | 0 | 14
39049.4101 | 2257 | 0 | 14
39049.4105 | 2383 | 0 | 14
39049.411 | 2483 | 0 | 14
39049.4115 | 2339 | 0 | 14
39049.412 | 2261 | 0 | 14
39049.4125 | 2102 | 0 | 14
39049.413 | 2129 | 0 | 14
39049.4135 | 2151 | 0 | 14
39049.4139 | 2403 | 0 | 14
39049.4144 | 2228 | 0 | 14
39049.4149 | 2246 | 0 | 14
39049.4154 | 2231 | 0 | 14
39049.4159 | 2076 | 0 | 14
39049.4164 | 1817 | 0 | 14
39049.4169 | 1893 | 0 | 14
39049.4173 | 2202 | 0 | 14
39049.4178 | 2284 | 0 | 14
39049.4183 | 2146 | 0 | 14
39049.4188 | 2548 | 0 | 14
39049.4193 | 2510 | 0 | 14
39049.4198 | 2501 | 0 | 14
39049.4203 | 2290 | 0 | 14
39049.4208 | 2530 | 0 | 14
39049.4212 | 2065 | 0 | 14
39049.4217 | 2280 | 0 | 14
14
39049.3848 | 1 | 0 | 15
39049.3853 | 0 | 0 | 15
39049.3858 | 1 | 0 | 15
39049.3863 | 1 | 0 | 15
39049.3867 | 1 | 0 | 15
39049.3872 | 1 | 0 | 15
39049.3877 | 1 | 0 | 15
39049.3882 | 1 | 0 | 15
39049.3887 | 1 | 0 | 15
39049.3892 | 1 | 0 | 15
39049.3897 | 1 | 0 | 15
39049.3902 | 1 | 0 | 15
39049.3906 | 1 | 0 | 15
39049.3911 | 1 | 0 | 15
39049.3916 | 1 | 0 | 15
39049.3921 | 1 | 0 | 15
39049.3926 | 1 | 0 | 15
39049.3931 | 0 | 0 | 15
39049.3936 | 1 | 0 | 15
39049.394 | 1 | 0 | 15
39049.3945 | 0 | 0 | 15
39049.395 | 1 | 0 | 15
39049.3955 | 1 | 0 | 15
39049.396 | 1 | 0 | 15
39049.3965 | 1 | 0 | 15
39049.397 | 1 | 0 | 15
39049.3974 | 0 | 0 | 15
39049.3979 | 1 | 0 | 15
39049.3984 | 1 | 0 | 15
39049.3989 | 1 | 0 | 15
39049.3994 | 1 | 0 | 15
39049.3999 | 1 | 0 | 15
39049.4004 | 1 | 0 | 15
39049.4008 | 1 | 0 | 15
39049.4013 | 1 | 0 | 15
39049.4018 | 1711 | 0 | 15
39049.4023 | 677 | 0 | 15
39049.4028 | 2312 | 0 | 15
39049.4033 | 2415 | 0 | 15
39049.4038 | 1922 | 0 | 15
39049.4042 | 2128 | 0 | 15
39049.4047 | 1886 | 0 | 15
39049.4052 | 1870 | 0 | 15
39049.4057 | 1893 | 0 | 15
39049.4062 | 2189 | 0 | 15
39049.4067 | 1856 | 0 | 15
39049.4072 | 2219 | 0 | 15
39049.4076 | 2449 | 0 | 15
39049.4081 | 2221 | 0 | 15
39049.4086 | 2362 | 0 | 15
39049.4091 | 2177 | 0 | 15
39049.4096 | 2053 | 0 | 15
39049.4101 | 2246 | 0 | 15
39049.4106 | 2405 | 0 | 15
39049.411 | 2069 | 0 | 15
39049.4115 | 2076 | 0 | 15
39049.412 | 2018 | 0 | 15
39049.4125 | 2180 | 0 | 15
39049.413 | 1929 | 0 | 15
39049.4135 | 2366 | 0 | 15
39049.414 | 2378 | 0 | 15
39049.4144 | 1921 | 0 | 15
39049.4149 | 2290 | 0 | 15
39049.4154 | 2354 | 0 | 15
39049.4159 | 1854 | 0 | 15
39049.4164 | 2034 | 0 | 15
39049.4169 | 2342 | 0 | 15
39049.4174 | 1841 | 0 | 15
39049.4178 | 2143 | 0 | 15
39049.4183 | 2363 | 0 | 15
39049.4188 | 1977 | 0 | 15
39049.4193 | 2282 | 0 | 15
39049.4198 | 2348 | 0 | 15
39049.4203 | 2504 | 0 | 15
39049.4208 | 2137 | 0 | 15
39049.4212 | 2285 | 0 | 15
39049.4217 | 2398 | 0 | 15
15
39049.3848 | 0 | 0 | 16
39049.3853 | 1 | 0 | 16
39049.3858 | 1 | 0 | 16
39049.3863 | 1 | 0 | 16
39049.3868 | 1 | 0 | 16
39049.3872 | 1 | 0 | 16
39049.3877 | 1 | 0 | 16
39049.3882 | 1 | 0 | 16
39049.3887 | 1 | 0 | 16
39049.3892 | 1 | 0 | 16
39049.3897 | 1 | 0 | 16
39049.3902 | 1 | 0 | 16
39049.3906 | 0 | 0 | 16
39049.3911 | 1 | 0 | 16
39049.3916 | 1 | 0 | 16
39049.3921 | 0 | 0 | 16
39049.3926 | 1 | 0 | 16
39049.3931 | 1 | 0 | 16
39049.3936 | 1 | 0 | 16
39049.3941 | 1 | 0 | 16
39049.3945 | 1 | 0 | 16
39049.395 | 1 | 0 | 16
39049.3955 | 1 | 0 | 16
39049.396 | 1 | 0 | 16
39049.3965 | 1 | 0 | 16
39049.397 | 1 | 0 | 16
39049.3975 | 1 | 0 | 16
39049.3979 | 0 | 0 | 16
39049.3984 | 1 | 0 | 16
39049.3989 | 1 | 0 | 16
39049.3994 | 1 | 0 | 16
39049.3999 | 0 | 0 | 16
39049.4004 | 1 | 0 | 16
39049.4009 | 1 | 0 | 16
39049.4013 | 1 | 0 | 16
39049.4018 | 1 | 0 | 16
39049.4023 | 1 | 0 | 16
39049.4028 | 1 | 0 | 16
39049.4033 | 1 | 0 | 16
39049.4038 | 1 | 0 | 16
39049.4043 | 1 | 0 | 16
39049.4047 | 1 | 0 | 16
39049.4052 | 1 | 0 | 16
39049.4057 | 1 | 0 | 16
39049.4062 | 1 | 0 | 16
39049.4067 | 1 | 0 | 16
39049.4072 | 1 | 0 | 16
39049.4077 | 1 | 0 | 16
39049.4081 | 1 | 0 | 16
39049.4086 | 1 | 0 | 16
39049.4091 | 1 | 0 | 16
39049.4096 | 1 | 0 | 16
39049.4101 | 1 | 0 | 16
39049.4106 | 1 | 0 | 16
39049.4111 | 1 | 0 | 16
39049.4116 | 1 | 0 | 16
39049.412 | 1 | 0 | 16
39049.4125 | 11 | 0 | 16
39049.413 | 25 | 0 | 16
39049.4135 | 25 | 0 | 16
39049.414 | 40 | 0 | 16
39049.4145 | 28 | 0 | 16
39049.415 | 17 | 0 | 16
39049.4154 | 17 | 0 | 16
39049.4159 | 17 | 0 | 16
39049.4164 | 18 | 0 | 16
39049.4169 | 12 | 0 | 16
39049.4174 | 24 | 0 | 16
39049.4179 | 30 | 0 | 16
39049.4184 | 21 | 0 | 16
39049.4188 | 15 | 0 | 16
39049.4193 | 17 | 0 | 16
39049.4198 | 13 | 0 | 16
39049.4203 | 12 | 0 | 16
39049.4208 | 9 | 0 | 16
39049.4213 | 8 | 0 | 16
39049.4218 | 5 | 0 | 16
16
39049.3848 | 1 | 0 | 17
39049.3853 | 1 | 0 | 17
39049.3858 | 1 | 0 | 17
39049.3863 | 1 | 0 | 17
39049.3868 | 1 | 0 | 17
39049.3873 | 0 | 0 | 17
39049.3877 | 1 | 0 | 17
39049.3882 | 1 | 0 | 17
39049.3887 | 1 | 0 | 17
39049.3892 | 0 | 0 | 17
39049.3897 | 1 | 0 | 17
39049.3902 | 1 | 0 | 17
39049.3907 | 1 | 0 | 17
39049.3911 | 1 | 0 | 17
39049.3916 | 1 | 0 | 17
39049.3921 | 1 | 0 | 17
39049.3926 | 1 | 0 | 17
39049.3931 | 1 | 0 | 17
39049.3936 | 1 | 0 | 17
39049.3941 | 1 | 0 | 17
39049.3945 | 1 | 0 | 17
39049.395 | 1 | 0 | 17
39049.3955 | 1 | 0 | 17
39049.396 | 1 | 0 | 17
39049.3965 | 1 | 0 | 17
39049.397 | 1 | 0 | 17
39049.3975 | 1 | 0 | 17
39049.398 | 1 | 0 | 17
39049.3984 | 1 | 0 | 17
39049.3989 | 1 | 0 | 17
39049.3994 | 1 | 0 | 17
39049.3999 | 1 | 0 | 17
39049.4004 | 1 | 0 | 17
39049.4009 | 1 | 0 | 17
39049.4014 | 1 | 0 | 17
39049.4018 | 1615 | 0 | 17
39049.4023 | 1186 | 0 | 17
39049.4028 | 1884 | 0 | 17
39049.4033 | 2059 | 0 | 17
39049.4038 | 2170 | 0 | 17
39049.4043 | 2086 | 0 | 17
39049.4048 | 2321 | 0 | 17
39049.4052 | 2251 | 0 | 17
39049.4057 | 1890 | 0 | 17
39049.4062 | 1936 | 0 | 17
39049.4067 | 2147 | 0 | 17
39049.4072 | 1871 | 0 | 17
39049.4077 | 2313 | 0 | 17
39049.4082 | 2192 | 0 | 17
39049.4086 | 1923 | 0 | 17
39049.4091 | 2080 | 0 | 17
39049.4096 | 1925 | 0 | 17
39049.4101 | 2030 | 0 | 17
39049.4111 | 2334 | 0 | 17
39049.4116 | 1871 | 0 | 17
39049.412 | 2395 | 0 | 17
39049.4125 | 2356 | 0 | 17
39049.413 | 2257 | 0 | 17
39049.4135 | 2050 | 0 | 17
39049.414 | 2318 | 0 | 17
39049.4145 | 2399 | 0 | 17
39049.415 | 2381 | 0 | 17
39049.4155 | 2225 | 0 | 17
39049.4159 | 2368 | 0 | 17
39049.4164 | 1927 | 0 | 17
39049.4169 | 1921 | 0 | 17
39049.4174 | 1905 | 0 | 17
39049.4179 | 1831 | 0 | 17
39049.4184 | 2338 | 0 | 17
39049.4189 | 2419 | 0 | 17
39049.4193 | 2182 | 0 | 17
39049.4198 | 2422 | 0 | 17
39049.4203 | 2543 | 0 | 17
39049.4208 | 2469 | 0 | 17
39049.4213 | 2329 | 0 | 17
39049.4218 | 2249 | 0 | 17
17
39049.3848 | 1 | 0 | 18
39049.3853 | 1 | 0 | 18
39049.3858 | 1 | 0 | 18
39049.3863 | 1 | 0 | 18
39049.3868 | 1 | 0 | 18
39049.3873 | 1 | 0 | 18
39049.3878 | 1 | 0 | 18
39049.3883 | 1 | 0 | 18
39049.3887 | 1 | 0 | 18
39049.3892 | 1 | 0 | 18
39049.3897 | 1 | 0 | 18
39049.3902 | 1 | 0 | 18
39049.3907 | 1 | 0 | 18
39049.3912 | 1 | 0 | 18
39049.3917 | 1 | 0 | 18
39049.3921 | 1 | 0 | 18
39049.3926 | 1 | 0 | 18
39049.3931 | 1 | 0 | 18
39049.3936 | 0 | 0 | 18
39049.3941 | 1 | 0 | 18
39049.3946 | 0 | 0 | 18
39049.3951 | 1 | 0 | 18
39049.3955 | 1 | 0 | 18
39049.396 | 1 | 0 | 18
39049.3965 | 1 | 0 | 18
39049.397 | 1 | 0 | 18
39049.3975 | 1 | 0 | 18
39049.398 | 1 | 0 | 18
39049.3985 | 1 | 0 | 18
39049.3989 | 1 | 0 | 18
39049.3994 | 1 | 0 | 18
39049.3999 | 1 | 0 | 18
39049.4004 | 1 | 0 | 18
39049.4009 | 1 | 0 | 18
39049.4014 | 1 | 0 | 18
39049.4019 | 1 | 0 | 18
39049.4023 | 1 | 0 | 18
39049.4028 | 1 | 0 | 18
39049.4033 | 1 | 0 | 18
39049.4038 | 1 | 0 | 18
39049.4043 | 1 | 0 | 18
39049.4048 | 1 | 0 | 18
39049.4053 | 1 | 0 | 18
39049.4058 | 1 | 0 | 18
39049.4062 | 1 | 0 | 18
39049.4067 | 1 | 0 | 18
39049.4072 | 1 | 0 | 18
39049.4077 | 1 | 0 | 18
39049.4082 | 1 | 0 | 18
39049.4087 | 1 | 0 | 18
39049.4092 | 1 | 0 | 18
39049.4096 | 1 | 0 | 18
39049.4101 | 1 | 0 | 18
39049.4106 | 1 | 0 | 18
39049.4111 | 1 | 0 | 18
39049.4116 | 1 | 0 | 18
39049.4121 | 2 | 0 | 18
39049.4126 | 95 | 0 | 18
39049.413 | 136 | 0 | 18
39049.4135 | 154 | 0 | 18
39049.414 | 119 | 0 | 18
39049.4145 | 82 | 0 | 18
39049.415 | 114 | 0 | 18
39049.4155 | 73 | 0 | 18
39049.4159 | 71 | 0 | 18
39049.4164 | 55 | 0 | 18
39049.4169 | 31 | 0 | 18
39049.4174 | 41 | 0 | 18
39049.4179 | 36 | 0 | 18
39049.4184 | 25 | 0 | 18
39049.4189 | 19 | 0 | 18
39049.4194 | 17 | 0 | 18
39049.4198 | 18 | 0 | 18
39049.4203 | 4 | 0 | 18
39049.4208 | 2 | 0 | 18
39049.4213 | 2 | 0 | 18
39049.4218 | 2 | 0 | 18
18
39049.3849 | 1 | 0 | 19
39049.3853 | 1 | 0 | 19
39049.3858 | 1 | 0 | 19
39049.3863 | 1 | 0 | 19
39049.3868 | 1 | 0 | 19
39049.3873 | 1 | 0 | 19
39049.3878 | 1 | 0 | 19
39049.3883 | 1 | 0 | 19
39049.3887 | 1 | 0 | 19
39049.3892 | 1 | 0 | 19
39049.3897 | 1 | 0 | 19
39049.3902 | 1 | 0 | 19
39049.3907 | 1 | 0 | 19
39049.3912 | 1 | 0 | 19
39049.3917 | 1 | 0 | 19
39049.3922 | 1 | 0 | 19
39049.3926 | 0 | 0 | 19
39049.3931 | 1 | 0 | 19
39049.3936 | 1 | 0 | 19
39049.3941 | 1 | 0 | 19
39049.3946 | 1 | 0 | 19
39049.3951 | 1 | 0 | 19
39049.3956 | 1 | 0 | 19
39049.396 | 1 | 0 | 19
39049.3965 | 0 | 0 | 19
39049.397 | 1 | 0 | 19
39049.3975 | 1 | 0 | 19
39049.398 | 1 | 0 | 19
39049.3985 | 1154 | 0 | 19
39049.399 | 2200 | 0 | 19
39049.3994 | 2349 | 0 | 19
39049.3999 | 1894 | 0 | 19
39049.4004 | 2130 | 0 | 19
39049.4009 | 1915 | 0 | 19
39049.4014 | 1968 | 0 | 19
39049.4019 | 2364 | 0 | 19
39049.4024 | 2281 | 37 | 19
39049.4028 | 2218 | 2 | 19
39049.4033 | 2019 | 0 | 19
39049.4038 | 2502 | 0 | 19
39049.4043 | 2471 | 0 | 19
39049.4048 | 2506 | 0 | 19
39049.4053 | 2258 | 0 | 19
39049.4058 | 2514 | 0 | 19
39049.4062 | 2037 | 0 | 19
39049.4067 | 2268 | 0 | 19
39049.4072 | 2505 | 0 | 19
39049.4077 | 2392 | 0 | 19
39049.4082 | 2381 | 0 | 19
39049.4087 | 2185 | 0 | 19
39049.4092 | 2197 | 0 | 19
39049.4097 | 2026 | 0 | 19
39049.4101 | 2020 | 0 | 19
39049.4106 | 2542 | 0 | 19
39049.4111 | 2441 | 0 | 19
39049.4116 | 2169 | 0 | 19
39049.4121 | 2484 | 0 | 19
39049.4126 | 2011 | 0 | 19
39049.4131 | 2181 | 0 | 19
39049.4135 | 2150 | 0 | 19
39049.414 | 2446 | 0 | 19
39049.4145 | 2350 | 0 | 19
39049.415 | 2572 | 0 | 19
39049.4155 | 2326 | 0 | 19
39049.416 | 2258 | 0 | 19
39049.4165 | 2414 | 0 | 19
39049.4169 | 2564 | 0 | 19
39049.4174 | 2141 | 0 | 19
39049.4179 | 2353 | 0 | 19
39049.4184 | 2278 | 0 | 19
39049.4189 | 2460 | 0 | 19
39049.4194 | 2032 | 0 | 19
39049.4199 | 2422 | 0 | 19
39049.4203 | 2534 | 0 | 19
39049.4208 | 2542 | 0 | 19
39049.4213 | 2515 | 0 | 19
39049.4218 | 2360 | 0 | 19
19
39049.3849 | 1 | 0 | 20
39049.3854 | 1 | 0 | 20
39049.3859 | 1 | 0 | 20
39049.3863 | 1 | 0 | 20
39049.3868 | 1 | 0 | 20
39049.3873 | 1 | 0 | 20
39049.3878 | 1 | 0 | 20
39049.3883 | 1 | 0 | 20
39049.3888 | 1 | 0 | 20
39049.3893 | 1 | 0 | 20
39049.3897 | 1 | 0 | 20
39049.3902 | 1 | 0 | 20
39049.3907 | 1 | 0 | 20
39049.3912 | 1 | 0 | 20
39049.3917 | 1 | 0 | 20
39049.3922 | 1 | 0 | 20
39049.3927 | 1 | 0 | 20
39049.3931 | 1 | 0 | 20
39049.3936 | 1 | 0 | 20
39049.3941 | 1 | 0 | 20
39049.3946 | 1 | 0 | 20
39049.3951 | 1 | 0 | 20
39049.3956 | 1 | 0 | 20
39049.3961 | 1 | 0 | 20
39049.3966 | 1 | 0 | 20
39049.397 | 1 | 0 | 20
39049.3975 | 0 | 0 | 20
39049.398 | 1 | 0 | 20
39049.3985 | 1 | 0 | 20
39049.399 | 2296 | 0 | 20
39049.3995 | 2202 | 0 | 20
39049.3999 | 2528 | 0 | 20
39049.4004 | 1948 | 1 | 20
39049.4009 | 1857 | 0 | 20
39049.4014 | 2044 | 0 | 20
39049.4019 | 2307 | 0 | 20
39049.4024 | 2073 | 55 | 20
39049.4029 | 2226 | 2 | 20
39049.4033 | 2496 | 0 | 20
39049.4038 | 2277 | 0 | 20
39049.4043 | 2266 | 0 | 20
39049.4048 | 2250 | 0 | 20
39049.4053 | 2158 | 0 | 20
39049.4058 | 2515 | 0 | 20
39049.4063 | 2271 | 0 | 20
39049.4067 | 2477 | 0 | 20
39049.4072 | 2317 | 0 | 20
39049.4077 | 2196 | 0 | 20
39049.4082 | 2174 | 0 | 20
39049.4087 | 2055 | 0 | 20
39049.4092 | 2414 | 0 | 20
39049.4097 | 2310 | 0 | 20
39049.4102 | 2559 | 0 | 20
39049.4106 | 2058 | 0 | 20
39049.4111 | 2054 | 0 | 20
39049.4116 | 2085 | 0 | 20
39049.4121 | 2376 | 0 | 20
39049.4126 | 2514 | 0 | 20
39049.4131 | 2170 | 0 | 20
39049.4136 | 2527 | 0 | 20
39049.414 | 2536 | 0 | 20
39049.4145 | 2009 | 0 | 20
39049.415 | 2083 | 0 | 20
39049.4155 | 2503 | 0 | 20
39049.416 | 2547 | 0 | 20
39049.4165 | 2194 | 0 | 20
39049.417 | 1994 | 0 | 20
39049.4174 | 2330 | 0 | 20
39049.4179 | 2082 | 0 | 20
39049.4184 | 2265 | 0 | 20
39049.4189 | 2321 | 0 | 20
39049.4194 | 2539 | 0 | 20
39049.4199 | 2432 | 0 | 20
39049.4204 | 2266 | 0 | 20
39049.4208 | 2040 | 0 | 20
39049.4213 | 2321 | 0 | 20
39049.4218 | 2163 | 0 | 20
20
39049.3849 | 1 | 0 | 21
39049.3854 | 1 | 0 | 21
39049.3859 | 1 | 0 | 21
39049.3864 | 1 | 0 | 21
39049.3868 | 1 | 0 | 21
39049.3873 | 1 | 0 | 21
39049.3878 | 1 | 0 | 21
39049.3883 | 1 | 0 | 21
39049.3888 | 1 | 0 | 21
39049.3893 | 1 | 0 | 21
39049.3902 | 1 | 0 | 21
39049.3907 | 1 | 0 | 21
39049.3912 | 1 | 0 | 21
39049.3917 | 1 | 0 | 21
39049.3922 | 1 | 0 | 21
39049.3927 | 1 | 0 | 21
39049.3932 | 1 | 0 | 21
39049.3936 | 1 | 0 | 21
39049.3941 | 1 | 0 | 21
39049.3946 | 1 | 0 | 21
39049.3951 | 1 | 0 | 21
39049.3956 | 1 | 0 | 21
39049.3961 | 1 | 0 | 21
39049.3966 | 1 | 0 | 21
39049.397 | 1 | 0 | 21
39049.3975 | 1 | 0 | 21
39049.398 | 1 | 0 | 21
39049.3985 | 1916 | 0 | 21
39049.399 | 2523 | 0 | 21
39049.3995 | 2504 | 0 | 21
39049.4 | 2345 | 0 | 21
39049.4005 | 2182 | 0 | 21
39049.4009 | 2254 | 0 | 21
39049.4014 | 2359 | 0 | 21
39049.4019 | 2032 | 0 | 21
39049.4024 | 1676 | 0 | 21
39049.4029 | 1847 | 0 | 21
39049.4034 | 2307 | 0 | 21
39049.4039 | 2433 | 0 | 21
39049.4043 | 2017 | 0 | 21
39049.4048 | 2382 | 0 | 21
39049.4053 | 2013 | 0 | 21
39049.4058 | 2402 | 0 | 21
39049.4063 | 2229 | 0 | 21
39049.4068 | 2015 | 0 | 21
39049.4073 | 2400 | 0 | 21
39049.4077 | 2500 | 0 | 21
39049.4082 | 2047 | 0 | 21
39049.4087 | 2575 | 0 | 21
39049.4092 | 2183 | 0 | 21
39049.4097 | 2485 | 0 | 21
39049.4102 | 2574 | 0 | 21
39049.4107 | 2021 | 0 | 21
39049.4111 | 2485 | 0 | 21
39049.4116 | 2107 | 0 | 21
39049.4121 | 2368 | 0 | 21
39049.4126 | 2396 | 0 | 21
39049.4131 | 1995 | 0 | 21
39049.4136 | 2150 | 0 | 21
39049.4141 | 2220 | 0 | 21
39049.4145 | 2559 | 0 | 21
39049.415 | 2456 | 0 | 21
39049.4155 | 1989 | 0 | 21
39049.416 | 2554 | 0 | 21
39049.4165 | 2155 | 0 | 21
39049.417 | 2073 | 0 | 21
39049.4175 | 2022 | 0 | 21
39049.418 | 2150 | 0 | 21
39049.4184 | 1976 | 0 | 21
39049.4189 | 1976 | 0 | 21
39049.4194 | 2514 | 0 | 21
39049.4199 | 2388 | 0 | 21
39049.4204 | 2530 | 0 | 21
39049.4209 | 2069 | 0 | 21
39049.4214 | 2203 | 0 | 21
39049.4218 | 2052 | 0 | 21
21
39049.3849 | 1 | 0 | 22
39049.3854 | 1 | 0 | 22
39049.3859 | 1 | 0 | 22
39049.3864 | 0 | 0 | 22
39049.3869 | 1 | 0 | 22
39049.3873 | 1 | 0 | 22
39049.3878 | 1 | 0 | 22
39049.3883 | 1 | 0 | 22
39049.3888 | 0 | 0 | 22
39049.3893 | 1 | 0 | 22
39049.3898 | 1 | 0 | 22
39049.3903 | 1 | 0 | 22
39049.3907 | 1 | 0 | 22
39049.3912 | 1 | 0 | 22
39049.3917 | 1 | 0 | 22
39049.3922 | 1 | 0 | 22
39049.3927 | 1 | 0 | 22
39049.3932 | 1 | 0 | 22
39049.3937 | 1 | 0 | 22
39049.3941 | 1 | 0 | 22
39049.3946 | 1 | 0 | 22
39049.3951 | 1 | 0 | 22
39049.3956 | 1 | 0 | 22
39049.3961 | 1 | 0 | 22
39049.3966 | 1 | 0 | 22
39049.3971 | 1 | 0 | 22
39049.3975 | 1 | 0 | 22
39049.398 | 1 | 0 | 22
39049.3985 | 1 | 0 | 22
39049.399 | 1 | 0 | 22
39049.3995 | 1 | 0 | 22
39049.4 | 1 | 0 | 22
39049.4005 | 1 | 0 | 22
39049.4009 | 1 | 0 | 22
39049.4014 | 1 | 0 | 22
39049.4019 | 1 | 0 | 22
39049.4024 | 1 | 0 | 22
39049.4029 | 1 | 0 | 22
39049.4034 | 1 | 0 | 22
39049.4039 | 1 | 0 | 22
39049.4044 | 1 | 0 | 22
39049.4048 | 1 | 0 | 22
39049.4053 | 1 | 0 | 22
39049.4058 | 1 | 0 | 22
39049.4063 | 1 | 0 | 22
39049.4068 | 2 | 0 | 22
39049.4073 | 1 | 0 | 22
39049.4078 | 1 | 0 | 22
39049.4082 | 1 | 0 | 22
39049.4087 | 1 | 0 | 22
39049.4092 | 1 | 0 | 22
39049.4097 | 1 | 0 | 22
39049.4102 | 1 | 0 | 22
39049.4107 | 2 | 0 | 22
39049.4112 | 1 | 0 | 22
39049.4116 | 2 | 0 | 22
39049.4121 | 1 | 0 | 22
39049.4126 | 12 | 0 | 22
39049.4131 | 31 | 0 | 22
39049.4136 | 33 | 0 | 22
39049.4141 | 25 | 0 | 22
39049.4146 | 26 | 0 | 22
39049.415 | 14 | 0 | 22
39049.4155 | 19 | 0 | 22
39049.416 | 25 | 0 | 22
39049.4165 | 21 | 0 | 22
39049.417 | 13 | 0 | 22
39049.4175 | 21 | 0 | 22
39049.418 | 29 | 0 | 22
39049.4184 | 20 | 0 | 22
39049.4189 | 18 | 0 | 22
39049.4194 | 16 | 0 | 22
39049.4199 | 12 | 0 | 22
39049.4204 | 10 | 0 | 22
39049.4209 | 8 | 0 | 22
39049.4214 | 6 | 0 | 22
39049.4219 | 5 | 0 | 22
22
39049.3849 | 1 | 0 | 23
39049.3854 | 1 | 0 | 23
39049.3859 | 1 | 0 | 23
39049.3864 | 1 | 0 | 23
39049.3869 | 1 | 0 | 23
39049.3874 | 1 | 0 | 23
39049.3878 | 1 | 0 | 23
39049.3883 | 1 | 0 | 23
39049.3888 | 1 | 0 | 23
39049.3893 | 1 | 0 | 23
39049.3898 | 1 | 0 | 23
39049.3903 | 1 | 0 | 23
39049.3908 | 1 | 0 | 23
39049.3913 | 1 | 0 | 23
39049.3917 | 1 | 0 | 23
39049.3922 | 1 | 0 | 23
39049.3927 | 1 | 0 | 23
39049.3932 | 1 | 0 | 23
39049.3937 | 1 | 0 | 23
39049.3942 | 1 | 0 | 23
39049.3947 | 1 | 0 | 23
39049.3951 | 1 | 0 | 23
39049.3956 | 1 | 0 | 23
39049.3961 | 1 | 0 | 23
39049.3966 | 0 | 0 | 23
39049.3971 | 1 | 0 | 23
39049.3976 | 1 | 0 | 23
39049.3981 | 1 | 0 | 23
39049.3985 | 1824 | 0 | 23
39049.399 | 2104 | 0 | 23
39049.3995 | 1974 | 0 | 23
39049.4 | 2182 | 0 | 23
39049.4005 | 2129 | 0 | 23
39049.401 | 1999 | 0 | 23
39049.4015 | 1897 | 0 | 23
39049.4019 | 2091 | 0 | 23
39049.4024 | 1730 | 0 | 23
39049.4029 | 1893 | 0 | 23
39049.4034 | 1930 | 0 | 23
39049.4039 | 2193 | 0 | 23
39049.4044 | 2474 | 0 | 23
39049.4049 | 2018 | 0 | 23
39049.4053 | 2058 | 0 | 23
39049.4058 | 2322 | 0 | 23
39049.4063 | 2483 | 0 | 23
39049.4068 | 2232 | 0 | 23
39049.4073 | 1996 | 0 | 23
39049.4078 | 2398 | 0 | 23
39049.4083 | 2018 | 0 | 23
39049.4088 | 2150 | 0 | 23
39049.4092 | 2590 | 0 | 23
39049.4097 | 2004 | 0 | 23
39049.4102 | 2094 | 0 | 23
39049.4107 | 2588 | 0 | 23
39049.4112 | 2271 | 0 | 23
39049.4117 | 2369 | 0 | 23
39049.4122 | 2467 | 0 | 23
39049.4126 | 2353 | 0 | 23
39049.4131 | 2367 | 0 | 23
39049.4136 | 2113 | 0 | 23
39049.4141 | 2052 | 0 | 23
39049.4146 | 2575 | 0 | 23
39049.4151 | 2184 | 0 | 23
39049.4156 | 2469 | 0 | 23
39049.416 | 2165 | 0 | 23
39049.4165 | 2178 | 0 | 23
39049.417 | 2137 | 0 | 23
39049.4175 | 2411 | 0 | 23
39049.418 | 2192 | 0 | 23
39049.4185 | 2478 | 0 | 23
39049.419 | 2012 | 0 | 23
39049.4194 | 2282 | 0 | 23
39049.4199 | 2233 | 0 | 23
39049.4204 | 2498 | 0 | 23
39049.4209 | 2059 | 0 | 23
39049.4214 | 2014 | 0 | 23
39049.4219 | 2512 | 0 | 23
23
39049.3849 | 1 | 0 | 24
39049.3854 | 1 | 0 | 24
39049.3859 | 1 | 0 | 24
39049.3864 | 1 | 0 | 24
39049.3869 | 1 | 0 | 24
39049.3874 | 1 | 0 | 24
39049.3879 | 1 | 0 | 24
39049.3883 | 1 | 0 | 24
39049.3888 | 1 | 0 | 24
39049.3893 | 1 | 0 | 24
39049.3898 | 1 | 0 | 24
39049.3903 | 1 | 0 | 24
39049.3908 | 1 | 0 | 24
39049.3913 | 1 | 0 | 24
39049.3917 | 1 | 0 | 24
39049.3922 | 1 | 0 | 24
39049.3927 | 1 | 0 | 24
39049.3932 | 1 | 0 | 24
39049.3937 | 1 | 0 | 24
39049.3942 | 1 | 0 | 24
39049.3947 | 1 | 0 | 24
39049.3952 | 1 | 0 | 24
39049.3956 | 1 | 0 | 24
39049.3961 | 1 | 0 | 24
39049.3966 | 1 | 0 | 24
39049.3971 | 1 | 0 | 24
39049.3976 | 1 | 0 | 24
39049.3981 | 1 | 0 | 24
39049.3986 | 1 | 0 | 24
39049.399 | 1 | 0 | 24
39049.3995 | 1 | 0 | 24
39049.4 | 1 | 0 | 24
39049.4005 | 1 | 0 | 24
39049.401 | 1 | 0 | 24
39049.4015 | 1 | 0 | 24
39049.402 | 1 | 0 | 24
39049.4024 | 1 | 0 | 24
39049.4029 | 1 | 0 | 24
39049.4034 | 1 | 0 | 24
39049.4039 | 1 | 0 | 24
39049.4044 | 1 | 0 | 24
39049.4049 | 1 | 0 | 24
39049.4054 | 1 | 0 | 24
39049.4058 | 1 | 0 | 24
39049.4063 | 1 | 0 | 24
39049.4068 | 1 | 0 | 24
39049.4073 | 1 | 0 | 24
39049.4078 | 1 | 0 | 24
39049.4083 | 1 | 0 | 24
39049.4088 | 1 | 0 | 24
39049.4092 | 1 | 0 | 24
39049.4097 | 1 | 0 | 24
39049.4102 | 1 | 0 | 24
39049.4107 | 1 | 0 | 24
39049.4112 | 1 | 0 | 24
39049.4117 | 1 | 0 | 24
39049.4122 | 25 | 0 | 24
39049.4127 | 111 | 0 | 24
39049.4131 | 150 | 0 | 24
39049.4136 | 110 | 0 | 24
39049.4141 | 109 | 0 | 24
39049.4146 | 108 | 0 | 24
39049.4151 | 107 | 0 | 24
39049.4156 | 79 | 0 | 24
39049.4161 | 86 | 0 | 24
39049.4165 | 57 | 0 | 24
39049.417 | 34 | 0 | 24
39049.4175 | 41 | 0 | 24
39049.418 | 36 | 0 | 24
39049.4185 | 23 | 0 | 24
39049.419 | 19 | 0 | 24
39049.4195 | 19 | 0 | 24
39049.4199 | 17 | 0 | 24
39049.4204 | 3 | 0 | 24
39049.4209 | 3 | 0 | 24
39049.4214 | 3 | 0 | 24
39049.4219 | 2 | 0 | 24
24
39049.385 | 1 | 0 | 25
39049.3855 | 1 | 0 | 25
39049.3859 | 1 | 0 | 25
39049.3864 | 1 | 0 | 25
39049.3869 | 0 | 0 | 25
39049.3874 | 1 | 0 | 25
39049.3879 | 1 | 0 | 25
39049.3884 | 1 | 0 | 25
39049.3889 | 1 | 0 | 25
39049.3893 | 1 | 0 | 25
39049.3898 | 1 | 0 | 25
39049.3903 | 1 | 0 | 25
39049.3908 | 1 | 0 | 25
39049.3913 | 1 | 0 | 25
39049.3918 | 0 | 0 | 25
39049.3923 | 1 | 0 | 25
39049.3927 | 1 | 0 | 25
39049.3932 | 1 | 0 | 25
39049.3937 | 1 | 0 | 25
39049.3942 | 1 | 0 | 25
39049.3947 | 1 | 0 | 25
39049.3952 | 1 | 0 | 25
39049.3957 | 1 | 0 | 25
39049.3961 | 1 | 0 | 25
39049.3966 | 1 | 0 | 25
39049.3971 | 1 | 0 | 25
39049.3976 | 1 | 0 | 25
39049.3981 | 1 | 0 | 25
39049.3986 | 993 | 0 | 25
39049.3991 | 2467 | 0 | 25
39049.3995 | 2370 | 0 | 25
39049.4 | 1940 | 0 | 25
39049.4005 | 2054 | 0 | 25
39049.401 | 2312 | 0 | 25
39049.4015 | 1879 | 0 | 25
39049.402 | 2411 | 0 | 25
39049.4025 | 1510 | 0 | 25
39049.403 | 2121 | 0 | 25
39049.4034 | 2309 | 0 | 25
39049.4039 | 2415 | 0 | 25
39049.4044 | 2081 | 0 | 25
39049.4049 | 1944 | 0 | 25
39049.4054 | 2114 | 0 | 25
39049.4059 | 2392 | 0 | 25
39049.4063 | 2103 | 0 | 25
39049.4068 | 1988 | 0 | 25
39049.4073 | 2115 | 0 | 25
39049.4078 | 2575 | 0 | 25
39049.4083 | 2132 | 0 | 25
39049.4088 | 2591 | 0 | 25
39049.4093 | 2432 | 0 | 25
39049.4097 | 2566 | 0 | 25
39049.4102 | 2036 | 0 | 25
39049.4107 | 2449 | 0 | 25
39049.4112 | 2258 | 0 | 25
39049.4117 | 2484 | 0 | 25
39049.4122 | 2528 | 0 | 25
39049.4127 | 2206 | 0 | 25
39049.4131 | 2004 | 0 | 25
39049.4136 | 2113 | 0 | 25
39049.4141 | 2475 | 0 | 25
39049.4146 | 2570 | 0 | 25
39049.4151 | 2575 | 0 | 25
39049.4156 | 2573 | 0 | 25
39049.4161 | 2100 | 0 | 25
39049.4166 | 2050 | 0 | 25
39049.417 | 2380 | 0 | 25
39049.4175 | 2575 | 0 | 25
39049.418 | 2225 | 0 | 25
39049.4185 | 2318 | 0 | 25
39049.419 | 2408 | 0 | 25
39049.4195 | 2180 | 0 | 25
39049.42 | 2217 | 0 | 25
39049.4204 | 2520 | 0 | 25
39049.4209 | 2100 | 0 | 25
39049.4214 | 2047 | 0 | 25
39049.4219 | 2341 | 0 | 25
25
39049.385 | 1 | 0 | 26
39049.3855 | 1 | 0 | 26
39049.3859 | 1 | 0 | 26
39049.3864 | 1 | 0 | 26
39049.3869 | 1 | 0 | 26
39049.3874 | 1 | 0 | 26
39049.3879 | 1 | 0 | 26
39049.3884 | 1 | 0 | 26
39049.3889 | 1 | 0 | 26
39049.3894 | 1 | 0 | 26
39049.3898 | 1 | 0 | 26
39049.3903 | 0 | 0 | 26
39049.3908 | 1 | 0 | 26
39049.3913 | 1 | 0 | 26
39049.3918 | 1 | 0 | 26
39049.3923 | 1 | 0 | 26
39049.3928 | 1 | 0 | 26
39049.3932 | 1 | 0 | 26
39049.3937 | 1 | 0 | 26
39049.3942 | 1 | 0 | 26
39049.3947 | 1 | 0 | 26
39049.3952 | 1 | 0 | 26
39049.3957 | 1 | 0 | 26
39049.3962 | 1 | 0 | 26
39049.3966 | 1 | 0 | 26
39049.3971 | 1 | 0 | 26
39049.3976 | 1 | 0 | 26
39049.3981 | 1 | 0 | 26
39049.3986 | 1 | 0 | 26
39049.3991 | 1 | 0 | 26
39049.3996 | 1 | 0 | 26
39049.4 | 1 | 0 | 26
39049.4005 | 1 | 0 | 26
39049.401 | 1 | 0 | 26
39049.4015 | 1 | 0 | 26
39049.402 | 1 | 0 | 26
39049.4025 | 1 | 0 | 26
39049.403 | 1 | 0 | 26
39049.4034 | 1 | 0 | 26
39049.4039 | 1 | 0 | 26
39049.4044 | 1 | 0 | 26
39049.4049 | 2 | 0 | 26
39049.4054 | 1 | 0 | 26
39049.4059 | 1 | 0 | 26
39049.4064 | 1 | 0 | 26
39049.4069 | 1 | 0 | 26
39049.4073 | 1 | 0 | 26
39049.4078 | 1 | 0 | 26
39049.4083 | 1 | 0 | 26
39049.4088 | 1 | 0 | 26
39049.4093 | 2 | 0 | 26
39049.4098 | 1 | 0 | 26
39049.4103 | 1 | 0 | 26
39049.4107 | 2 | 0 | 26
39049.4112 | 1 | 0 | 26
39049.4117 | 1 | 0 | 26
39049.4122 | 2 | 0 | 26
39049.4127 | 11 | 0 | 26
39049.4132 | 25 | 0 | 26
39049.4137 | 26 | 0 | 26
39049.4141 | 43 | 0 | 26
39049.4146 | 26 | 0 | 26
39049.4151 | 21 | 0 | 26
39049.4156 | 18 | 0 | 26
39049.4161 | 29 | 0 | 26
39049.4166 | 12 | 0 | 26
39049.4171 | 15 | 0 | 26
39049.4175 | 26 | 0 | 26
39049.418 | 26 | 0 | 26
39049.4185 | 20 | 0 | 26
39049.419 | 19 | 0 | 26
39049.4195 | 13 | 0 | 26
39049.42 | 12 | 0 | 26
39049.4205 | 9 | 0 | 26
39049.4209 | 8 | 0 | 26
39049.4214 | 6 | 0 | 26
39049.4219 | 3 | 0 | 26
26
39049.385 | 1 | 0 | 27
39049.3855 | 0 | 0 | 27
39049.386 | 1 | 0 | 27
39049.3865 | 1 | 1 | 27
39049.3869 | 1 | 0 | 27
39049.3874 | 1 | 0 | 27
39049.3879 | 1 | 0 | 27
39049.3884 | 1 | 0 | 27
39049.3889 | 1 | 0 | 27
39049.3894 | 1 | 0 | 27
39049.3898 | 1 | 0 | 27
39049.3903 | 1 | 0 | 27
39049.3908 | 1 | 0 | 27
39049.3913 | 1 | 0 | 27
39049.3918 | 1 | 0 | 27
39049.3923 | 1 | 0 | 27
39049.3928 | 1 | 0 | 27
39049.3933 | 1 | 0 | 27
39049.3937 | 1 | 0 | 27
39049.3942 | 1 | 0 | 27
39049.3947 | 1 | 0 | 27
39049.3952 | 1 | 0 | 27
39049.3957 | 1 | 0 | 27
39049.3962 | 1 | 0 | 27
39049.3967 | 1 | 0 | 27
39049.3971 | 1 | 0 | 27
39049.3976 | 1 | 0 | 27
39049.3981 | 1 | 0 | 27
39049.3986 | 1674 | 0 | 27
39049.3991 | 2095 | 0 | 27
39049.3996 | 2089 | 0 | 27
39049.4001 | 2514 | 0 | 27
39049.4005 | 2378 | 0 | 27
39049.401 | 1891 | 0 | 27
39049.4015 | 2310 | 0 | 27
39049.402 | 2463 | 0 | 27
39049.4025 | 1408 | 0 | 27
39049.403 | 2245 | 0 | 27
39049.4035 | 2293 | 0 | 27
39049.4039 | 2095 | 0 | 27
39049.4044 | 2493 | 0 | 27
39049.4049 | 2395 | 0 | 27
39049.4054 | 2038 | 0 | 27
39049.4059 | 1989 | 0 | 27
39049.4064 | 1987 | 0 | 27
39049.4069 | 2104 | 0 | 27
39049.4073 | 2225 | 0 | 27
39049.4078 | 2080 | 0 | 27
39049.4083 | 2103 | 0 | 27
39049.4088 | 2591 | 0 | 27
39049.4093 | 2069 | 0 | 27
39049.4098 | 2298 | 0 | 27
39049.4103 | 2484 | 0 | 27
39049.4108 | 2003 | 0 | 27
39049.4112 | 2527 | 0 | 27
39049.4117 | 2460 | 0 | 27
39049.4122 | 2582 | 0 | 27
39049.4127 | 2416 | 0 | 27
39049.4132 | 2122 | 0 | 27
39049.4137 | 2574 | 0 | 27
39049.4142 | 2579 | 0 | 27
39049.4146 | 2321 | 0 | 27
39049.4151 | 2572 | 0 | 27
39049.4156 | 2486 | 0 | 27
39049.4161 | 2571 | 0 | 27
39049.4166 | 2362 | 0 | 27
39049.4171 | 2421 | 0 | 27
39049.4176 | 2535 | 0 | 27
39049.418 | 2064 | 0 | 27
39049.4185 | 2293 | 0 | 27
39049.419 | 1982 | 0 | 27
39049.4195 | 2409 | 0 | 27
39049.42 | 2345 | 0 | 27
39049.4205 | 2172 | 0 | 27
39049.421 | 2126 | 0 | 27
39049.4214 | 2023 | 0 | 27
39049.4219 | 2516 | 0 | 27
27
39049.385 | 1 | 0 | 28
39049.3855 | 1 | 0 | 28
39049.386 | 1 | 0 | 28
39049.3865 | 1 | 0 | 28
39049.387 | 1 | 0 | 28
39049.3874 | 1 | 0 | 28
39049.3879 | 0 | 0 | 28
39049.3884 | 0 | 0 | 28
39049.3889 | 0 | 0 | 28
39049.3894 | 1 | 0 | 28
39049.3899 | 1 | 0 | 28
39049.3904 | 1 | 0 | 28
39049.3908 | 1 | 0 | 28
39049.3913 | 1 | 0 | 28
39049.3918 | 0 | 0 | 28
39049.3923 | 1 | 0 | 28
39049.3928 | 1 | 0 | 28
39049.3933 | 1 | 0 | 28
39049.3938 | 1 | 0 | 28
39049.3942 | 1 | 0 | 28
39049.3947 | 1 | 0 | 28
39049.3952 | 1 | 0 | 28
39049.3957 | 1 | 0 | 28
39049.3962 | 1 | 0 | 28
39049.3967 | 1 | 0 | 28
39049.3972 | 1 | 0 | 28
39049.3977 | 1 | 0 | 28
39049.3981 | 1 | 0 | 28
39049.3986 | 1 | 0 | 28
39049.3991 | 1 | 1 | 28
39049.3996 | 1 | 0 | 28
39049.4001 | 1 | 0 | 28
39049.4006 | 1 | 0 | 28
39049.4011 | 1 | 0 | 28
39049.4015 | 1 | 0 | 28
39049.402 | 1 | 0 | 28
39049.4025 | 1 | 0 | 28
39049.403 | 1 | 0 | 28
39049.4035 | 1 | 0 | 28
39049.404 | 1 | 0 | 28
39049.4045 | 1 | 0 | 28
39049.4049 | 1 | 0 | 28
39049.4054 | 1 | 0 | 28
39049.4059 | 1 | 0 | 28
39049.4064 | 1 | 0 | 28
39049.4069 | 1 | 0 | 28
39049.4074 | 1 | 0 | 28
39049.4079 | 1 | 0 | 28
39049.4083 | 1 | 0 | 28
39049.4088 | 1 | 0 | 28
39049.4093 | 1 | 0 | 28
39049.4098 | 1 | 0 | 28
39049.4103 | 1 | 0 | 28
39049.4108 | 1 | 0 | 28
39049.4113 | 1 | 0 | 28
39049.4117 | 1 | 0 | 28
39049.4122 | 38 | 0 | 28
39049.4127 | 121 | 0 | 28
39049.4132 | 166 | 0 | 28
39049.4137 | 125 | 0 | 28
39049.4142 | 112 | 0 | 28
39049.4147 | 99 | 0 | 28
39049.4151 | 78 | 0 | 28
39049.4156 | 76 | 0 | 28
39049.4161 | 72 | 0 | 28
39049.4166 | 38 | 0 | 28
39049.4171 | 35 | 0 | 28
39049.4176 | 42 | 0 | 28
39049.4181 | 43 | 0 | 28
39049.4185 | 23 | 0 | 28
39049.419 | 19 | 0 | 28
39049.4195 | 17 | 0 | 28
39049.42 | 12 | 0 | 28
39049.4205 | 3 | 0 | 28
39049.421 | 2 | 0 | 28
39049.4215 | 2 | 0 | 28
39049.4219 | 2 | 0 | 28
28
39049.385 | 1 | 0 | 29
39049.3855 | 1 | 0 | 29
39049.386 | 1 | 0 | 29
39049.3865 | 1 | 0 | 29
39049.387 | 1 | 0 | 29
39049.3875 | 1 | 0 | 29
39049.3879 | 1 | 0 | 29
39049.3884 | 1 | 0 | 29
39049.3889 | 1 | 0 | 29
39049.3894 | 1 | 0 | 29
39049.3899 | 1 | 0 | 29
39049.3904 | 1 | 0 | 29
39049.3909 | 1 | 0 | 29
39049.3913 | 1 | 0 | 29
39049.3918 | 1 | 0 | 29
39049.3923 | 1 | 0 | 29
39049.3928 | 1 | 0 | 29
39049.3933 | 1 | 0 | 29
39049.3938 | 1 | 0 | 29
39049.3943 | 1 | 0 | 29
39049.3947 | 0 | 0 | 29
39049.3952 | 1 | 0 | 29
39049.3957 | 1 | 0 | 29
39049.3962 | 1 | 0 | 29
39049.3967 | 1 | 0 | 29
39049.3972 | 1 | 0 | 29
39049.3977 | 1 | 0 | 29
39049.3981 | 1 | 0 | 29
39049.3986 | 1 | 0 | 29
39049.3991 | 1 | 0 | 29
39049.3996 | 1 | 0 | 29
39049.4001 | 1 | 0 | 29
39049.4006 | 1 | 0 | 29
39049.4011 | 1 | 0 | 29
39049.4016 | 1 | 0 | 29
39049.402 | 1 | 0 | 29
39049.4025 | 1 | 0 | 29
39049.403 | 1 | 0 | 29
39049.4035 | 0 | 0 | 29
39049.404 | 1 | 0 | 29
39049.4045 | 1 | 0 | 29
39049.405 | 1 | 0 | 29
39049.4054 | 1 | 0 | 29
39049.4059 | 1 | 0 | 29
39049.4064 | 1 | 0 | 29
39049.4069 | 1 | 0 | 29
39049.4074 | 1 | 0 | 29
39049.4079 | 1 | 0 | 29
39049.4084 | 1 | 0 | 29
39049.4088 | 1 | 0 | 29
39049.4093 | 1 | 0 | 29
39049.4098 | 1 | 0 | 29
39049.4103 | 1 | 0 | 29
39049.4108 | 1 | 0 | 29
39049.4113 | 1 | 0 | 29
39049.4118 | 1 | 0 | 29
39049.4122 | 5 | 0 | 29
39049.4127 | 32 | 0 | 29
39049.4132 | 60 | 0 | 29
39049.4137 | 53 | 0 | 29
39049.4142 | 60 | 0 | 29
39049.4147 | 38 | 0 | 29
39049.4152 | 30 | 0 | 29
39049.4156 | 34 | 0 | 29
39049.4161 | 41 | 0 | 29
39049.4166 | 21 | 0 | 29
39049.4171 | 31 | 0 | 29
39049.4176 | 45 | 0 | 29
39049.4181 | 47 | 0 | 29
39049.4186 | 42 | 0 | 29
39049.4191 | 35 | 0 | 29
39049.4195 | 31 | 0 | 29
39049.42 | 17 | 0 | 29
39049.4205 | 14 | 0 | 29
39049.421 | 11 | 0 | 29
39049.4215 | 7 | 0 | 29
39049.422 | 2 | 0 | 29
29
39049.385 | 1 | 0 | 30
39049.3855 | 1 | 0 | 30
39049.386 | 1 | 0 | 30
39049.3865 | 1 | 0 | 30
39049.387 | 0 | 0 | 30
39049.3875 | 1 | 0 | 30
39049.388 | 1 | 0 | 30
39049.3884 | 1 | 0 | 30
39049.3889 | 1 | 0 | 30
39049.3894 | 1 | 0 | 30
39049.3899 | 1 | 0 | 30
39049.3904 | 1 | 0 | 30
39049.3909 | 1 | 0 | 30
39049.3914 | 1 | 0 | 30
39049.3919 | 1 | 0 | 30
39049.3923 | 1 | 0 | 30
39049.3928 | 1 | 0 | 30
39049.3933 | 1 | 0 | 30
39049.3938 | 1 | 0 | 30
39049.3943 | 1 | 0 | 30
39049.3948 | 1 | 0 | 30
39049.3953 | 1 | 0 | 30
39049.3957 | 1 | 0 | 30
39049.3962 | 1 | 0 | 30
39049.3967 | 1 | 0 | 30
39049.3972 | 1 | 0 | 30
39049.3977 | 1 | 0 | 30
39049.3982 | 1 | 0 | 30
39049.3987 | 1 | 0 | 30
39049.3991 | 1 | 0 | 30
39049.3996 | 1 | 0 | 30
39049.4001 | 1 | 0 | 30
39049.4006 | 1 | 0 | 30
39049.4011 | 1 | 0 | 30
39049.4016 | 1 | 0 | 30
39049.4021 | 1 | 0 | 30
39049.4025 | 1 | 0 | 30
39049.403 | 1 | 0 | 30
39049.4035 | 1 | 0 | 30
39049.404 | 1 | 0 | 30
39049.4045 | 1 | 0 | 30
39049.405 | 1 | 0 | 30
39049.4055 | 1 | 0 | 30
39049.4059 | 1 | 0 | 30
39049.4064 | 1 | 0 | 30
39049.4069 | 1 | 0 | 30
39049.4074 | 1 | 0 | 30
39049.4079 | 1 | 0 | 30
39049.4084 | 1 | 0 | 30
39049.4089 | 1 | 0 | 30
39049.4093 | 1 | 0 | 30
39049.4098 | 1 | 0 | 30
39049.4103 | 1 | 0 | 30
39049.4108 | 1 | 0 | 30
39049.4113 | 1 | 0 | 30
39049.4118 | 1 | 0 | 30
39049.4123 | 67 | 0 | 30
39049.4127 | 171 | 0 | 30
39049.4132 | 215 | 0 | 30
39049.4137 | 174 | 0 | 30
39049.4142 | 153 | 0 | 30
39049.4147 | 104 | 0 | 30
39049.4152 | 130 | 0 | 30
39049.4157 | 82 | 0 | 30
39049.4161 | 98 | 0 | 30
39049.4166 | 53 | 0 | 30
39049.4171 | 64 | 0 | 30
39049.4176 | 56 | 0 | 30
39049.4181 | 56 | 0 | 30
39049.4186 | 49 | 0 | 30
39049.4191 | 34 | 0 | 30
39049.4195 | 33 | 0 | 30
39049.42 | 15 | 0 | 30
39049.4205 | 4 | 0 | 30
39049.4215 | 2 | 0 | 30
39049.422 | 1 | 0 | 30
30

## Temperatures
DAQ Time | Burner Time | Bundle center | Air above bundle | Air below bundle | Intra-bundle | TRAY F
0 | -239 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
1 | -238 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
2 | -237 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
3 | -236 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
4 | -235 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
5 | -234 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
6 | -233 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
7 | -232 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
8 | -231 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
9 | -230 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
10 | -229 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
11 | -228 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
12 | -227 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
13 | -226 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
14 | -225 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
15 | -224 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
16 | -223 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
17 | -222 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
18 | -221 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
19 | -220 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
20 | -219 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
21 | -218 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
22 | -217 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
23 | -216 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
24 | -215 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
25 | -214 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
26 | -213 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
27 | -212 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
28 | -211 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
29 | -210 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
30 | -209 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
31 | -208 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
32 | -207 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
33 | -206 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
34 | -205 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
35 | -204 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
36 | -203 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
37 | -202 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
38 | -201 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
39 | -200 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
40 | -199 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
41 | -198 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
42 | -197 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
43 | -196 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
44 | -195 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
45 | -194 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
46 | -193 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
47 | -192 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
48 | -191 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
49 | -190 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
50 | -189 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
51 | -188 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
52 | -187 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
53 | -186 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
54 | -185 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
55 | -184 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
56 | -183 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
57 | -182 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
58 | -181 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
59 | -180 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
60 | -179 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
61 | -178 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
62 | -177 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
63 | -176 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
64 | -175 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
65 | -174 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
66 | -173 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
67 | -172 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
68 | -171 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
69 | -170 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
70 | -169 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
71 | -168 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
72 | -167 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
73 | -166 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
74 | -165 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
75 | -164 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
76 | -163 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
77 | -162 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
78 | -161 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
79 | -160 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
80 | -159 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
81 | -158 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
82 | -157 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
83 | -156 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
84 | -155 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
85 | -154 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
86 | -153 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
87 | -152 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
88 | -151 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
89 | -150 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
90 | -149 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
91 | -148 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
92 | -147 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
93 | -146 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
94 | -145 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
95 | -144 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
96 | -143 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
97 | -142 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
98 | -141 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
99 | -140 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
100 | -139 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
101 | -138 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
102 | -137 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
103 | -136 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
104 | -135 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
105 | -134 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
106 | -133 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
107 | -132 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
108 | -131 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
109 | -130 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
110 | -129 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
111 | -128 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
112 | -127 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
113 | -126 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
114 | -125 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
115 | -124 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
116 | -123 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
117 | -122 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
118 | -121 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
119 | -120 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
120 | -119 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
121 | -118 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
122 | -117 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
123 | -116 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
124 | -115 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
125 | -114 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
126 | -113 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
127 | -112 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
128 | -111 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
129 | -110 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
130 | -109 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
131 | -108 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
132 | -107 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
133 | -106 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
134 | -105 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
135 | -104 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
136 | -103 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
137 | -102 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
138 | -101 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
139 | -100 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
140 | -99 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
141 | -98 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
142 | -97 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
143 | -96 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
144 | -95 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
145 | -94 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
146 | -93 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
147 | -92 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
148 | -91 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
149 | -90 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
150 | -89 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
151 | -88 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
152 | -87 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
153 | -86 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
154 | -85 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
155 | -84 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
156 | -83 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
157 | -82 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
158 | -81 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
159 | -80 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
160 | -79 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
161 | -78 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
162 | -77 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
163 | -76 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
164 | -75 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
165 | -74 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
166 | -73 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
167 | -72 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
168 | -71 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
169 | -70 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
170 | -69 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
171 | -68 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
172 | -67 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
173 | -66 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
174 | -65 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
175 | -64 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
176 | -63 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
177 | -62 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
178 | -61 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
179 | -60 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
180 | -59 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
181 | -58 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
182 | -57 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
183 | -56 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
184 | -55 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
185 | -54 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
186 | -53 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
187 | -52 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
188 | -51 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
189 | -50 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
190 | -49 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
191 | -48 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
192 | -47 | 12.6 | 11.8 | 12.1 | 12.7 | 13.5
193 | -46 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
194 | -45 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
195 | -44 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
196 | -43 | 12.6 | 11.8 | 12.1 | 12.7 | 13.5
197 | -42 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
198 | -41 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
199 | -40 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
200 | -39 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
201 | -38 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5
202 | -37 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
203 | -36 | 12.6 | 11.8 | 12.2 | 12.7 | 13.5
204 | -35 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
205 | -34 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
206 | -33 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
207 | -32 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
208 | -31 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
209 | -30 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
210 | -29 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
211 | -28 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
212 | -27 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
213 | -26 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
214 | -25 | 12.6 | 11.8 | 12.2 | 12.7 | 13.5
215 | -24 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
216 | -23 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
217 | -22 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
218 | -21 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
219 | -20 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
220 | -19 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
221 | -18 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
222 | -17 | 12.6 | 11.8 | 12.2 | 12.7 | 13.5
223 | -16 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
224 | -15 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
225 | -14 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
226 | -13 | 12.6 | 11.8 | 12.2 | 12.7 | 13.5
227 | -12 | 12.6 | 11.8 | 12.2 | 12.7 | 13.5
228 | -11 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
229 | -10 | 12.6 | 11.8 | 12.1 | 12.7 | 13.5
230 | -9 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
231 | -8 | 12.6 | 11.8 | 12.2 | 12.7 | 13.5
232 | -7 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
233 | -6 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
234 | -5 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
235 | -4 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
236 | -3 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
237 | -2 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
238 | -1 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
239 | 0 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
240 | 1 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
241 | 2 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
242 | 3 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
243 | 4 | 12.6 | 11.8 | 12.2 | 12.7 | 13.5
244 | 5 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
245 | 6 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
246 | 7 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5
247 | 8 | 12.6 | 11.9 | 12.8 | 12.7 | 13.6
248 | 9 | 12.6 | 12.9 | 15.1 | 12.8 | 14.6
249 | 10 | 12.6 | 14.5 | 18.6 | 13.3 | 15.9
250 | 11 | 12.6 | 16.9 | 22.8 | 13.9 | 17.3
251 | 12 | 12.6 | 18.9 | 25.8 | 14.3 | 18
252 | 13 | 12.6 | 21.5 | 30.5 | 15.1 | 19.6
253 | 14 | 12.7 | 24.2 | 34 | 15.4 | 20.9
254 | 15 | 12.7 | 26.9 | 37.3 | 15.9 | 21.3
255 | 16 | 12.8 | 29.3 | 41.7 | 16.2 | 21.9
256 | 17 | 12.8 | 32 | 46.9 | 16.8 | 23.6
257 | 18 | 12.9 | 34.9 | 52.6 | 17.6 | 25.1
258 | 19 | 13 | 38.1 | 56.2 | 17.8 | 26.2
259 | 20 | 13.1 | 40.7 | 58.2 | 17.7 | 26.6
260 | 21 | 13.2 | 44.2 | 62.8 | 18.6 | 27.9
261 | 22 | 13.4 | 47.4 | 66.7 | 19.2 | 29.4
262 | 23 | 13.5 | 50.5 | 71.4 | 19.7 | 30.6
263 | 24 | 13.7 | 54 | 76 | 20.7 | 31.6
264 | 25 | 13.8 | 57.4 | 78.7 | 21 | 31.8
265 | 26 | 14 | 60.3 | 81.4 | 21.5 | 32
266 | 27 | 14.2 | 62.7 | 81.8 | 21.1 | 32.6
267 | 28 | 14.3 | 65.2 | 86.7 | 22.2 | 33.5
268 | 29 | 14.5 | 67.9 | 89 | 22.2 | 34.8
269 | 30 | 14.7 | 70.4 | 91 | 22 | 35.7
270 | 31 | 14.9 | 72.2 | 91.9 | 21.6 | 35.9
271 | 32 | 15.1 | 74.6 | 95.1 | 22.1 | 36.5
272 | 33 | 15.3 | 77.2 | 97.1 | 22.3 | 37.4
273 | 34 | 15.5 | 79.2 | 99.6 | 22 | 38.5
274 | 35 | 15.7 | 81.3 | 102.4 | 22 | 39.5
275 | 36 | 15.9 | 83.1 | 104 | 22.1 | 40.4
276 | 37 | 16 | 84.8 | 105.5 | 22.2 | 41.1
277 | 38 | 16.2 | 86.8 | 106.5 | 22 | 42
278 | 39 | 16.4 | 89 | 108.6 | 22 | 43.5
279 | 40 | 16.6 | 91.4 | 110.3 | 22.3 | 44.7
280 | 41 | 16.7 | 93.2 | 112.7 | 22.6 | 44.8
281 | 42 | 16.9 | 95.3 | 114.3 | 22.4 | 45.4
282 | 43 | 17.1 | 98.2 | 118.4 | 23.3 | 46.9
283 | 44 | 17.3 | 100.9 | 120.7 | 23.7 | 47.4
284 | 45 | 17.4 | 103.1 | 122.4 | 24 | 48.6
285 | 46 | 17.6 | 104.9 | 124.9 | 24.3 | 49.1
286 | 47 | 17.8 | 107.2 | 127 | 24.4 | 49.6
287 | 48 | 18 | 108.7 | 127.7 | 24.5 | 50.3
288 | 49 | 18.2 | 110 | 128.4 | 24.4 | 50.9
289 | 50 | 18.4 | 111.5 | 129.9 | 24.1 | 51.5
290 | 51 | 18.7 | 112.1 | 130.7 | 23.8 | 51.4
291 | 52 | 18.9 | 113.2 | 131 | 23.8 | 51.5
292 | 53 | 19.1 | 113.2 | 129.8 | 23.2 | 51.1
293 | 54 | 19.3 | 112.9 | 128.7 | 22.6 | 50.5
294 | 55 | 19.4 | 113.8 | 131.3 | 23 | 51.4
295 | 56 | 19.6 | 114.9 | 133.1 | 22.9 | 52
296 | 57 | 19.7 | 115.6 | 133.2 | 22.7 | 52.6
297 | 58 | 19.9 | 116.3 | 134.4 | 22.8 | 52.4
298 | 59 | 20 | 117.6 | 136.6 | 23.3 | 52.9
299 | 60 | 20.2 | 117.7 | 136 | 22.9 | 53.5
300 | 61 | 20.4 | 118 | 135.8 | 22.6 | 54.1
301 | 62 | 20.5 | 118.7 | 136.5 | 22.8 | 55.1
302 | 63 | 20.6 | 119.4 | 138.3 | 22.8 | 56.2
303 | 64 | 20.8 | 120.6 | 140.3 | 23 | 57.1
304 | 65 | 20.9 | 123 | 142.3 | 23.1 | 58.9
305 | 66 | 21.1 | 124.5 | 144.2 | 23.4 | 60.2
306 | 67 | 21.2 | 126.6 | 146.8 | 24.2 | 62.3
307 | 68 | 21.4 | 128.9 | 149.6 | 24.9 | 63.8
308 | 69 | 21.5 | 130.6 | 151 | 24.6 | 64.3
309 | 70 | 21.7 | 130.9 | 150 | 24 | 63.6
310 | 71 | 21.9 | 131 | 149 | 23.5 | 63.3
311 | 72 | 22.1 | 131.9 | 150.7 | 23.9 | 64.3
312 | 73 | 22.2 | 133.4 | 152.1 | 24.4 | 65.8
313 | 74 | 22.4 | 134.8 | 153.6 | 25.1 | 66.8
314 | 75 | 22.6 | 136.3 | 154.7 | 25.1 | 67.3
315 | 76 | 22.8 | 137.6 | 155 | 25.2 | 67
316 | 77 | 22.9 | 139.3 | 157.6 | 25.6 | 67.5
317 | 78 | 23.1 | 140 | 157.7 | 25.4 | 67.6
318 | 79 | 23.3 | 140.7 | 157.9 | 25.4 | 67.7
319 | 80 | 23.5 | 141.4 | 158.3 | 25.4 | 69
320 | 81 | 23.7 | 142 | 157.7 | 25.1 | 69
321 | 82 | 23.9 | 142.1 | 156.7 | 24.9 | 68.6
322 | 83 | 24.1 | 142.4 | 156.2 | 24.9 | 68.5
323 | 84 | 24.3 | 142.4 | 155.4 | 25 | 68.6
324 | 85 | 24.5 | 142.2 | 154.9 | 24.9 | 68.6
325 | 86 | 24.6 | 142.3 | 154.4 | 24.7 | 69.2
326 | 87 | 24.8 | 142.5 | 154 | 24.5 | 70.2
327 | 88 | 25 | 143.1 | 155.5 | 24.6 | 72.7
328 | 89 | 25.1 | 144.5 | 157.1 | 25.1 | 74.3
329 | 90 | 25.3 | 145.8 | 158.7 | 25.9 | 75.2
330 | 91 | 25.4 | 146.5 | 159.6 | 26.1 | 75.5
331 | 92 | 25.6 | 146.8 | 160.1 | 25.9 | 75.4
332 | 93 | 25.8 | 147.1 | 162.1 | 26.2 | 75.9
333 | 94 | 26 | 147.1 | 161.5 | 26 | 76.2
334 | 95 | 26.1 | 148.2 | 162.6 | 26.5 | 76.8
335 | 96 | 26.3 | 148.5 | 162.2 | 26.4 | 76.9
336 | 97 | 26.5 | 148.4 | 162.3 | 26.1 | 77
337 | 98 | 26.7 | 148.1 | 162.4 | 26 | 76.9
338 | 99 | 26.9 | 148.4 | 162.4 | 26.4 | 77.1
339 | 100 | 27.1 | 148.2 | 161.4 | 26.1 | 76.8
340 | 101 | 27.3 | 148.1 | 161.7 | 25.9 | 77.4
341 | 102 | 27.4 | 148.3 | 161.6 | 26.2 | 77.9
342 | 103 | 27.6 | 148.8 | 162.7 | 26.4 | 78.8
343 | 104 | 27.8 | 148.9 | 163.4 | 26.7 | 79.6
344 | 105 | 28 | 149.1 | 163.6 | 26.8 | 80.5
345 | 106 | 28.1 | 149.6 | 163.8 | 26.7 | 81.2
346 | 107 | 28.3 | 150.2 | 164.7 | 26.9 | 82
347 | 108 | 28.5 | 151.1 | 170.1 | 27.4 | 83.3
348 | 109 | 28.7 | 151.3 | 168.9 | 27.1 | 83.5
349 | 110 | 28.9 | 151.9 | 168.8 | 27.3 | 83.5
350 | 111 | 29.1 | 151.9 | 168.4 | 27 | 83.7
351 | 112 | 29.3 | 152.1 | 167.6 | 26.7 | 84.1
352 | 113 | 29.5 | 152.8 | 167.9 | 27.3 | 84.9
353 | 114 | 29.7 | 154 | 168.4 | 28 | 85.6
354 | 115 | 29.8 | 155.1 | 169.3 | 28.2 | 86.5
355 | 116 | 30 | 155.1 | 170.2 | 28.5 | 87.1
356 | 117 | 30.2 | 154.8 | 169.2 | 28.1 | 87
357 | 118 | 30.4 | 154.8 | 168.9 | 28 | 86.9
358 | 119 | 30.6 | 155.6 | 170.8 | 28.7 | 87.8
359 | 120 | 30.8 | 156.3 | 172.2 | 28.8 | 88.5
360 | 121 | 31 | 157 | 172.9 | 29.2 | 88.9
361 | 122 | 31.2 | 157.7 | 173.4 | 29.6 | 90
362 | 123 | 31.4 | 157.6 | 173.2 | 29.7 | 89.5
363 | 124 | 31.7 | 157.6 | 172.9 | 29.5 | 89.5
364 | 125 | 31.9 | 157.5 | 172.2 | 29.3 | 89.6
365 | 126 | 32.1 | 157.4 | 171.2 | 29.1 | 89.5
366 | 127 | 32.3 | 157.6 | 170.6 | 29 | 89.9
367 | 128 | 32.5 | 157.2 | 169.8 | 28.8 | 90.3
368 | 129 | 32.7 | 157 | 169.8 | 28.9 | 90.3
369 | 130 | 32.9 | 157.1 | 171.4 | 29.4 | 90.8
370 | 131 | 33.1 | 157.7 | 172 | 29.6 | 91.7
371 | 132 | 33.3 | 157.2 | 172.1 | 29.2 | 92.1
372 | 133 | 33.5 | 157.2 | 173.8 | 29.3 | 92.8
373 | 134 | 33.7 | 156.2 | 171.7 | 28.9 | 92.6
374 | 135 | 33.9 | 156 | 171.2 | 28.7 | 92.8
375 | 136 | 34.1 | 156.2 | 171 | 28.7 | 93.7
376 | 137 | 34.3 | 157 | 172 | 29.1 | 94.5
377 | 138 | 34.5 | 157.7 | 172.4 | 29.3 | 95.5
378 | 139 | 34.7 | 158.2 | 172.6 | 29.6 | 95.7
379 | 140 | 34.8 | 158.2 | 172 | 29.6 | 96
380 | 141 | 35 | 157.5 | 170.4 | 29.2 | 95.7
381 | 142 | 35.2 | 157.7 | 169.6 | 29.1 | 95.6
382 | 143 | 35.4 | 157.8 | 170.4 | 29.1 | 96.2
383 | 144 | 35.6 | 159 | 171.6 | 29.3 | 97.3
384 | 145 | 35.8 | 159.6 | 171.8 | 29.2 | 97.7
385 | 146 | 36 | 159.9 | 171.8 | 29.5 | 98
386 | 147 | 36.1 | 159.7 | 170.8 | 29.2 | 97.8
387 | 148 | 36.3 | 159.1 | 169.2 | 28.8 | 97.2
388 | 149 | 36.5 | 158.6 | 168 | 28.8 | 97
389 | 150 | 36.7 | 158.3 | 168.4 | 29.3 | 97.7
390 | 151 | 36.8 | 158.5 | 168.4 | 29.5 | 98
391 | 152 | 37 | 158.8 | 167.7 | 29.4 | 98.3
392 | 153 | 37.2 | 160 | 168.9 | 29.9 | 100.8
393 | 154 | 37.3 | 160.6 | 169.5 | 29.8 | 101.8
394 | 155 | 37.5 | 161 | 169.8 | 29.9 | 101.9
395 | 156 | 37.7 | 161.4 | 171.2 | 30 | 102.4
396 | 157 | 37.9 | 162.1 | 172.8 | 30.4 | 103.3
397 | 158 | 38 | 162.4 | 173.8 | 30.6 | 103.8
398 | 159 | 38.2 | 162.2 | 173.6 | 30.6 | 104
399 | 160 | 38.4 | 162.1 | 173.6 | 30.6 | 104
400 | 161 | 38.6 | 162.7 | 173.7 | 30.6 | 103.9
401 | 162 | 38.7 | 163 | 174.9 | 31 | 104
402 | 163 | 38.9 | 163.6 | 175.5 | 31.4 | 104.2
403 | 164 | 39.1 | 163.5 | 176.1 | 31.6 | 104
404 | 165 | 39.3 | 163.8 | 177 | 31.9 | 104.5
405 | 166 | 39.5 | 164.1 | 177.1 | 31.7 | 106.1
406 | 167 | 39.7 | 164 | 177.3 | 31.9 | 106.1
407 | 168 | 39.9 | 164.2 | 178.4 | 32.1 | 106.6
408 | 169 | 40 | 163.5 | 177.5 | 32 | 106.5
409 | 170 | 40.2 | 163.4 | 178.7 | 32.4 | 106.9
410 | 171 | 40.4 | 163.4 | 178.8 | 32.4 | 106.9
411 | 172 | 40.6 | 162.7 | 178.1 | 32.2 | 106.9
412 | 173 | 40.8 | 162.9 | 179.7 | 32.6 | 107.2
413 | 174 | 41 | 163.3 | 180.2 | 32.7 | 108.3
414 | 175 | 41.2 | 162.8 | 178.7 | 32.6 | 108.7
415 | 176 | 41.4 | 162.7 | 181.2 | 32.6 | 109
416 | 177 | 41.6 | 162.6 | 181.5 | 33 | 109.6
417 | 178 | 41.8 | 162.5 | 181.4 | 33 | 109.6
418 | 179 | 42 | 162.3 | 182.1 | 33 | 109.9
419 | 180 | 42.2 | 162.4 | 182.1 | 33.1 | 110.8
420 | 181 | 42.4 | 162.1 | 180.7 | 32.8 | 110.7
421 | 182 | 42.6 | 161.2 | 180 | 32.7 | 110.5
422 | 183 | 42.8 | 161.4 | 180.6 | 33.2 | 111.3
423 | 184 | 43 | 161.7 | 181.5 | 33.4 | 111.5
424 | 185 | 43.1 | 162.7 | 182.2 | 33.7 | 112.9
425 | 186 | 43.3 | 163.1 | 181.8 | 33.6 | 113.3
426 | 187 | 43.6 | 163.3 | 181.4 | 33.8 | 113.5
427 | 188 | 43.7 | 164 | 182.1 | 33.8 | 113.9
428 | 189 | 43.9 | 164 | 183.9 | 34 | 114.7
429 | 190 | 44.1 | 164 | 184.2 | 34.1 | 115.2
430 | 191 | 44.3 | 164.2 | 184.4 | 34 | 115.4
431 | 192 | 44.5 | 163.9 | 183.7 | 34.3 | 115.3
432 | 193 | 44.7 | 163.6 | 182.7 | 34 | 115
433 | 194 | 44.9 | 163.2 | 181.6 | 34 | 114.6
434 | 195 | 45.1 | 163.2 | 182.1 | 34.4 | 114.7
435 | 196 | 45.3 | 163.8 | 181.2 | 34.6 | 115.2
436 | 197 | 45.4 | 163.6 | 180.4 | 34.4 | 115.1
437 | 198 | 45.6 | 163.5 | 180.2 | 34.1 | 115.7
438 | 199 | 45.8 | 164.5 | 181.6 | 34.4 | 117.3
439 | 200 | 46 | 164.4 | 182.1 | 34.5 | 117.9
440 | 201 | 46.2 | 165.4 | 184.8 | 35.3 | 119
441 | 202 | 46.3 | 165.6 | 184 | 35.3 | 119
442 | 203 | 46.5 | 165.3 | 184 | 35.5 | 118.9
443 | 204 | 46.7 | 165.8 | 185.6 | 35.9 | 119.8
444 | 205 | 46.9 | 166.4 | 185 | 35.7 | 120.6
445 | 206 | 47.1 | 166.2 | 184.6 | 35.5 | 120.5
446 | 207 | 47.3 | 166.5 | 184.7 | 35.5 | 120.4
447 | 208 | 47.5 | 167 | 185.5 | 35.9 | 120.8
448 | 209 | 47.7 | 167.2 | 184.1 | 35.8 | 120.5
449 | 210 | 47.8 | 167.5 | 185 | 36 | 120.8
450 | 211 | 48 | 168 | 184.6 | 36 | 121.5
451 | 212 | 48.2 | 167.6 | 184.8 | 35.9 | 121.8
452 | 213 | 48.4 | 168 | 185.1 | 36.1 | 122.3
453 | 214 | 48.6 | 168 | 186.4 | 36.2 | 122.5
454 | 215 | 48.8 | 168 | 185.6 | 36.2 | 123.1
455 | 216 | 49 | 167.4 | 184.7 | 36 | 123.2
456 | 217 | 49.1 | 168.1 | 186.2 | 36.5 | 124.2
457 | 218 | 49.3 | 168.6 | 186.1 | 36.7 | 124.9
458 | 219 | 49.5 | 169.6 | 187.1 | 37 | 125.7
459 | 220 | 49.7 | 169.5 | 187.6 | 37.3 | 126
460 | 221 | 49.8 | 171.8 | 189.5 | 38.6 | 127.5
461 | 222 | 50 | 171.8 | 189.7 | 38.4 | 127.6
462 | 223 | 50.2 | 171.8 | 190.3 | 38.4 | 127.9
463 | 224 | 50.4 | 171.9 | 190.3 | 38.2 | 128.2
464 | 225 | 50.6 | 172.3 | 190.8 | 38.4 | 128.6
465 | 226 | 50.8 | 172.2 | 189.7 | 38.2 | 128.9
466 | 227 | 51 | 171.9 | 188.8 | 38.4 | 128.6
467 | 228 | 51.2 | 172 | 188 | 38.8 | 129.2
468 | 229 | 51.4 | 171.3 | 186.6 | 38.5 | 129
469 | 230 | 51.6 | 171 | 186.4 | 38.3 | 129
470 | 231 | 51.8 | 170.7 | 186.5 | 38.2 | 129.1
471 | 232 | 52 | 170.5 | 186.8 | 38.2 | 129.5
472 | 233 | 52.2 | 170.5 | 187.7 | 38.4 | 129.6
473 | 234 | 52.4 | 171.1 | 189.6 | 38.6 | 130.4
474 | 235 | 52.5 | 171.3 | 189.9 | 38.9 | 131.1
475 | 236 | 52.7 | 171.1 | 190.4 | 39.2 | 130.9
476 | 237 | 52.9 | 171.9 | 191.8 | 39.7 | 132.1
477 | 238 | 53.1 | 172.5 | 193.6 | 39.9 | 133.2
478 | 239 | 53.2 | 173.4 | 195.4 | 40.1 | 133.9
479 | 240 | 53.4 | 174 | 196 | 40.4 | 134.4
480 | 241 | 53.6 | 174.5 | 196.4 | 40.6 | 135.5
481 | 242 | 53.8 | 174.7 | 194.9 | 40.2 | 135.1
482 | 243 | 54 | 175.3 | 196.2 | 40.2 | 135.8
483 | 244 | 54.2 | 176 | 196 | 40.4 | 135.8
484 | 245 | 54.4 | 176.1 | 197.9 | 40.6 | 135.9
485 | 246 | 54.6 | 178.2 | 203 | 41.6 | 136.7
486 | 247 | 54.8 | 180.2 | 204 | 42.1 | 137.6
487 | 248 | 54.9 | 180.8 | 205.4 | 42.4 | 138
488 | 249 | 55.2 | 181.1 | 205.2 | 42.3 | 138.1
489 | 250 | 55.4 | 180.4 | 204.8 | 42 | 137.7
490 | 251 | 55.6 | 180.6 | 206 | 42.5 | 138.3
491 | 252 | 55.8 | 180.8 | 205.5 | 42.7 | 138.7
492 | 253 | 56 | 181.1 | 206.3 | 42.6 | 139.4
493 | 254 | 56.2 | 180.6 | 205.7 | 42.5 | 139.5
494 | 255 | 56.4 | 179.8 | 204.3 | 42.4 | 139.5
495 | 256 | 56.6 | 178.5 | 201.5 | 42.1 | 139
496 | 257 | 56.8 | 177.7 | 200.4 | 41.9 | 138.5
497 | 258 | 57.1 | 178.1 | 199.7 | 41.8 | 139.8
498 | 259 | 57.2 | 179.2 | 200.7 | 41.8 | 140.7
499 | 260 | 57.4 | 180.3 | 201.9 | 41.9 | 141.4
500 | 261 | 57.6 | 180.9 | 201.3 | 41.9 | 142.2
501 | 262 | 57.8 | 181.5 | 201.4 | 42.1 | 142.4
502 | 263 | 58 | 182 | 201.9 | 42.6 | 142.7
503 | 264 | 58.1 | 182.3 | 203 | 43 | 143.7
504 | 265 | 58.3 | 183.1 | 203.7 | 43.2 | 144.8
505 | 266 | 58.5 | 183.4 | 203.9 | 43.2 | 144.8
506 | 267 | 58.7 | 183.8 | 203.9 | 43.2 | 145.3
507 | 268 | 58.9 | 184.7 | 204.8 | 43.5 | 146.8
508 | 269 | 59.1 | 183.7 | 203.1 | 43.2 | 146.1
509 | 270 | 59.2 | 183.4 | 206 | 43.9 | 146.8
510 | 271 | 59.4 | 182.6 | 204.6 | 43.9 | 146.7
511 | 272 | 59.6 | 182.5 | 204.3 | 43.9 | 146.9
512 | 273 | 59.8 | 181.4 | 203.5 | 43.9 | 146.6
513 | 274 | 60 | 181.6 | 204.4 | 44.2 | 147.3
514 | 275 | 60.2 | 180.7 | 202.8 | 44 | 147.2
515 | 276 | 60.3 | 181 | 204.4 | 44.3 | 148
516 | 277 | 60.5 | 182.4 | 206.4 | 44.9 | 149.2
517 | 278 | 60.7 | 182.6 | 205.9 | 44.8 | 149.2
518 | 279 | 60.9 | 182.5 | 204.3 | 44.6 | 148.9
519 | 280 | 61.1 | 182.3 | 203.9 | 44.7 | 148.4
520 | 281 | 61.3 | 182.7 | 204.2 | 45.1 | 148.4
521 | 282 | 61.5 | 182.8 | 204 | 45.2 | 148.8
522 | 283 | 61.6 | 182.4 | 203 | 44.8 | 148.6
523 | 284 | 61.8 | 182.2 | 202 | 44.8 | 148.3
524 | 285 | 62 | 182.3 | 203 | 45.2 | 148.6
525 | 286 | 62.2 | 182.1 | 202.7 | 45.3 | 149.2
526 | 287 | 62.4 | 182.3 | 203.7 | 45.3 | 150.1
527 | 288 | 62.5 | 182.1 | 203.5 | 45.6 | 150.3
528 | 289 | 62.7 | 181.9 | 202.8 | 45.5 | 150.3
529 | 290 | 62.9 | 181.5 | 204.4 | 45.8 | 151
530 | 291 | 63 | 180.5 | 202.3 | 45.5 | 150.9
531 | 292 | 63.2 | 180.9 | 205.3 | 46 | 150.7
532 | 293 | 63.4 | 181.5 | 204.8 | 46.2 | 151
533 | 294 | 63.6 | 181.9 | 204.7 | 46.3 | 151.4
534 | 295 | 63.7 | 182.2 | 205.3 | 46.3 | 151.6
535 | 296 | 63.9 | 182.1 | 205.1 | 46.1 | 151.8
536 | 297 | 64.1 | 182.4 | 205.2 | 46.4 | 152.4
537 | 298 | 64.3 | 182.6 | 204.8 | 46.4 | 152.5
538 | 299 | 64.4 | 183.2 | 206.3 | 46.8 | 152.7
539 | 300 | 64.6 | 183.6 | 205.7 | 46.9 | 152.4
540 | 301 | 64.8 | 183.7 | 205.3 | 47 | 152.3
541 | 302 | 64.9 | 184.4 | 205.4 | 47 | 153.2
542 | 303 | 65.1 | 185.3 | 205.7 | 47.1 | 154.1
543 | 304 | 65.3 | 186.2 | 206.1 | 47.3 | 154.6
544 | 305 | 65.5 | 186.5 | 206.3 | 47.8 | 155.4
545 | 306 | 65.6 | 186.7 | 206 | 48 | 155.1
546 | 307 | 65.8 | 186.7 | 206.5 | 48.2 | 155
547 | 308 | 66 | 186.1 | 205.2 | 47.9 | 154.7
548 | 309 | 66.2 | 186.7 | 206.5 | 48.1 | 155
549 | 310 | 66.4 | 187 | 207 | 48.3 | 155.3
550 | 311 | 66.5 | 187.1 | 207.2 | 48.6 | 155.4
551 | 312 | 66.7 | 187.5 | 208.3 | 49.2 | 156.2
552 | 313 | 66.9 | 187.1 | 208.7 | 49 | 156.6
553 | 314 | 67.1 | 187.3 | 208.2 | 49.2 | 157
554 | 315 | 67.3 | 187.6 | 208.4 | 49.5 | 157.2
555 | 316 | 67.4 | 188.2 | 208.4 | 49.5 | 157.7
556 | 317 | 67.6 | 189.4 | 210.9 | 49.8 | 158
557 | 318 | 67.8 | 190.5 | 212.2 | 49.8 | 159.1
558 | 319 | 68 | 193.1 | 223.1 | 50.4 | 161.2
559 | 320 | 68.2 | 193.9 | 225.4 | 50.3 | 163.2
560 | 321 | 68.4 | 194 | 226.6 | 50.8 | 162.6
561 | 322 | 68.6 | 194.5 | 227.1 | 51.2 | 162.6
562 | 323 | 68.8 | 195.8 | 229.5 | 51.5 | 162.9
563 | 324 | 69 | 196.7 | 228.7 | 51.4 | 163
564 | 325 | 69.2 | 197.5 | 228.1 | 51.3 | 162.7
565 | 326 | 69.3 | 198.1 | 227.1 | 51.3 | 163
566 | 327 | 69.6 | 198.8 | 228 | 51.4 | 163.4
567 | 328 | 69.8 | 199.4 | 230.4 | 51.6 | 163.8
568 | 329 | 69.9 | 200 | 230.4 | 51.7 | 164.2
569 | 330 | 70.1 | 200.3 | 232.6 | 51.9 | 164.3
570 | 331 | 70.3 | 201.9 | 234.4 | 52.2 | 165.6
571 | 332 | 70.5 | 203.6 | 237 | 52.5 | 166.3
572 | 333 | 70.7 | 207.1 | 242.5 | 53.2 | 168.7
573 | 334 | 70.9 | 209.5 | 245.6 | 53.4 | 170.1
574 | 335 | 71.1 | 211 | 248.7 | 53.5 | 171.1
575 | 336 | 71.3 | 213 | 253.2 | 53.9 | 172.8
576 | 337 | 71.6 | 214.6 | 256.7 | 54.2 | 173.9
577 | 338 | 71.8 | 217.3 | 259.6 | 54.7 | 175.5
578 | 339 | 72 | 219.8 | 268.4 | 55.6 | 177.3
579 | 340 | 72.2 | 221.8 | 270.8 | 55.9 | 179.6
580 | 341 | 72.4 | 222.7 | 270.9 | 55.8 | 180.1
581 | 342 | 72.7 | 225.3 | 276.7 | 56.1 | 180.6
582 | 343 | 72.9 | 227.8 | 278.1 | 56.2 | 181.9
583 | 344 | 73.2 | 230.4 | 279.5 | 56.4 | 182.4
584 | 345 | 73.4 | 232.6 | 279 | 56.6 | 183.2
585 | 346 | 73.6 | 233.5 | 278.8 | 56.7 | 183.4
586 | 347 | 73.9 | 233.9 | 277.4 | 56.7 | 183.3
587 | 348 | 74.1 | 234.1 | 276.5 | 57.1 | 182.8
588 | 349 | 74.4 | 234.7 | 276.4 | 57.2 | 183
589 | 350 | 74.7 | 236.6 | 278.7 | 57.7 | 184.3
590 | 351 | 74.9 | 238.6 | 278.4 | 57.6 | 186
591 | 352 | 75.1 | 239.6 | 278.5 | 57.7 | 187.2
592 | 353 | 75.4 | 241.4 | 280.3 | 58 | 188.2
593 | 354 | 75.6 | 243.5 | 282.6 | 58.2 | 189.5
594 | 355 | 75.9 | 243.2 | 280.4 | 57.9 | 190.2
595 | 356 | 76.1 | 243.7 | 281.2 | 58.2 | 189.7
596 | 357 | 76.4 | 246.4 | 285.2 | 59.3 | 190.8
597 | 358 | 76.6 | 248.1 | 286.5 | 59.6 | 191.9
598 | 359 | 76.9 | 248.5 | 285.4 | 59.7 | 191.7
599 | 360 | 77.1 | 248.6 | 285.9 | 60 | 191.5
600 | 361 | 77.4 | 249.4 | 286.7 | 60.2 | 193
601 | 362 | 77.6 | 249 | 285.1 | 60.1 | 193
602 | 363 | 77.9 | 248.3 | 282.7 | 59.9 | 192.5
603 | 364 | 78.1 | 248.2 | 283.8 | 60.2 | 192.8
604 | 365 | 78.4 | 249.9 | 286 | 61 | 195.2
605 | 366 | 78.6 | 248.8 | 282.2 | 60.7 | 194.9
606 | 367 | 78.9 | 247.9 | 282 | 60.8 | 194.4
607 | 368 | 79.1 | 249.4 | 283.7 | 61.2 | 195.2
608 | 369 | 79.4 | 250.6 | 286.1 | 61.8 | 196
609 | 370 | 79.6 | 251.5 | 285.5 | 62.3 | 196.8
610 | 371 | 79.9 | 251.1 | 284.8 | 62.3 | 197
611 | 372 | 80.1 | 251 | 284.8 | 62.4 | 197
612 | 373 | 80.4 | 251.3 | 286.9 | 62.7 | 197.9
613 | 374 | 80.6 | 252.5 | 288.2 | 63 | 199.5
614 | 375 | 80.9 | 252.6 | 288.8 | 64.3 | 200
615 | 376 | 81.1 | 253.2 | 289.2 | 66.6 | 200.7
616 | 377 | 81.4 | 254.8 | 291.3 | 69.5 | 202.1
617 | 378 | 81.7 | 256 | 294.3 | 71.1 | 203.6
618 | 379 | 81.9 | 256.8 | 296.5 | 72.1 | 205
619 | 380 | 82.2 | 257.5 | 296.8 | 72.7 | 206.3
620 | 381 | 82.5 | 257.5 | 297.7 | 73.2 | 206.3
621 | 382 | 82.8 | 256.8 | 296 | 73.1 | 205.7
622 | 383 | 83.1 | 257 | 300.1 | 74.8 | 205.8
623 | 384 | 83.5 | 256.6 | 300.3 | 75.6 | 206.9
624 | 385 | 83.8 | 256.1 | 302.8 | 76.6 | 207.8
625 | 386 | 84.1 | 256.1 | 301.9 | 77 | 208.2
626 | 387 | 84.4 | 257 | 304.3 | 79.4 | 209.3
627 | 388 | 84.8 | 258.1 | 306.1 | 80.1 | 209.9
628 | 389 | 85.1 | 258.5 | 304.7 | 80 | 209.8
629 | 390 | 85.5 | 258.8 | 304.1 | 81 | 209.5
630 | 391 | 85.8 | 260 | 306.9 | 82.3 | 210.1
631 | 392 | 86.2 | 260 | 304.5 | 82.3 | 210.1
632 | 393 | 86.5 | 259.3 | 304 | 81.7 | 209.8
633 | 394 | 86.8 | 260.3 | 307 | 83.2 | 211.1
634 | 395 | 87.2 | 261.6 | 306.4 | 84.6 | 212
635 | 396 | 87.5 | 261.4 | 303.6 | 84.6 | 211.6
636 | 397 | 87.9 | 260.3 | 302.6 | 85.4 | 211.1
637 | 398 | 88.2 | 260.9 | 308.2 | 87.3 | 213
638 | 399 | 88.6 | 261.2 | 308.4 | 88.6 | 215.5
639 | 400 | 88.9 | 261.5 | 306.8 | 88 | 215.5
640 | 401 | 89.2 | 261.9 | 312.5 | 88.9 | 216.8
641 | 402 | 89.6 | 265.2 | 318.1 | 91.2 | 219.2
642 | 403 | 89.9 | 266.2 | 318.9 | 92 | 220
643 | 404 | 90.3 | 266.9 | 320.1 | 92.4 | 219.7
644 | 405 | 90.6 | 268.1 | 319.5 | 93.4 | 219.8
645 | 406 | 90.9 | 267.4 | 317.6 | 92.5 | 220.3
646 | 407 | 91.3 | 267.6 | 317.9 | 93 | 220.3
647 | 408 | 91.6 | 267.7 | 318.2 | 93.1 | 220.7
648 | 409 | 91.9 | 268.6 | 319.3 | 94 | 221.4
649 | 410 | 92.3 | 267.6 | 316.8 | 93.5 | 220.9
650 | 411 | 92.6 | 267.1 | 315.9 | 92.5 | 220.6
651 | 412 | 93 | 267 | 314.7 | 92.7 | 221
652 | 413 | 93.3 | 268.5 | 316.4 | 94.1 | 221
653 | 414 | 93.6 | 269.8 | 318.6 | 94.3 | 222.2
654 | 415 | 94 | 270.4 | 319 | 94.4 | 223.2
655 | 416 | 94.3 | 269.7 | 317.6 | 93.9 | 223.3
656 | 417 | 94.6 | 271.2 | 317 | 94.5 | 224.4
657 | 418 | 94.9 | 273.9 | 317.3 | 94.8 | 225.6
658 | 419 | 95.3 | 274 | 316.7 | 94.8 | 226.3
659 | 420 | 95.6 | 274.9 | 317.5 | 95 | 226.6
660 | 421 | 95.9 | 275.8 | 320.4 | 95.8 | 227.2
661 | 422 | 96.3 | 276.3 | 321.7 | 96.7 | 227.7
662 | 423 | 96.6 | 276.1 | 320.2 | 97.1 | 227.8
663 | 424 | 96.9 | 275.9 | 319.3 | 97.6 | 228.7
664 | 425 | 97.2 | 276.2 | 320 | 99.1 | 231.7
665 | 426 | 97.5 | 277 | 319.7 | 100.5 | 233.4
666 | 427 | 97.9 | 278.2 | 326.2 | 101.3 | 234
667 | 428 | 98.2 | 278.1 | 328.4 | 100.4 | 234.5
668 | 429 | 98.5 | 279.3 | 336.3 | 101.2 | 235.8
669 | 430 | 98.8 | 279.1 | 333.4 | 102.4 | 235
670 | 431 | 99.2 | 278.7 | 331.6 | 101.7 | 234.4
671 | 432 | 99.5 | 279.3 | 331.9 | 101.8 | 234.9
672 | 433 | 99.8 | 279.3 | 332.3 | 102.2 | 236.1
673 | 434 | 100.2 | 278.9 | 330.8 | 101.9 | 236.2
674 | 435 | 100.5 | 279.5 | 330 | 102.8 | 236.6
675 | 436 | 100.8 | 279.8 | 328.2 | 101.5 | 237.1
676 | 437 | 101.2 | 281 | 328 | 101.9 | 238.2
677 | 438 | 101.5 | 281.7 | 329 | 101.7 | 239.7
678 | 439 | 101.8 | 282.9 | 330.1 | 103.3 | 240.8
679 | 440 | 102.2 | 283.1 | 333.1 | 103.2 | 241.3
680 | 441 | 102.5 | 284.3 | 334 | 103.5 | 242.5
681 | 442 | 102.8 | 284.2 | 331.3 | 103.6 | 242.4
682 | 443 | 103.2 | 284.2 | 330.1 | 103.3 | 242.4
683 | 444 | 103.5 | 284 | 328.3 | 103.6 | 242.7
684 | 445 | 103.8 | 284 | 328.5 | 104.9 | 243.6
685 | 446 | 104.1 | 286.3 | 331.5 | 107.1 | 244.2
686 | 447 | 104.5 | 287.1 | 331.1 | 107.6 | 244.6
687 | 448 | 104.8 | 286.8 | 328.7 | 106.9 | 244
688 | 449 | 105.1 | 289 | 328.8 | 107.8 | 245.6
689 | 450 | 105.5 | 289.9 | 329.5 | 106.9 | 247.4
690 | 451 | 105.8 | 290.1 | 330.3 | 106.8 | 247.7
691 | 452 | 106.1 | 289.1 | 328.5 | 105.8 | 247.7
692 | 453 | 106.5 | 288.8 | 327.6 | 106.6 | 247.6
693 | 454 | 106.8 | 288.6 | 327.4 | 107.2 | 247.6
694 | 455 | 107.1 | 288 | 331.3 | 106.8 | 247.8
695 | 456 | 107.5 | 287.5 | 330.2 | 106.3 | 248.2
696 | 457 | 107.8 | 288.2 | 329.4 | 106.3 | 249.5
697 | 458 | 108.1 | 288 | 327.2 | 106 | 249.7
698 | 459 | 108.5 | 287.3 | 326.2 | 106.4 | 250.1
699 | 460 | 108.8 | 286.2 | 324.6 | 106.5 | 250.3
700 | 461 | 109.2 | 286.3 | 324.4 | 106.6 | 250.4
701 | 462 | 109.5 | 288 | 324.5 | 106.7 | 251.5
702 | 463 | 109.8 | 288.2 | 329.3 | 107.9 | 252.8
703 | 464 | 110.2 | 289.3 | 329.4 | 107.9 | 254.4
704 | 465 | 110.5 | 288.4 | 330.6 | 108.4 | 255
705 | 466 | 110.8 | 289.4 | 333.4 | 109.4 | 256.9
706 | 467 | 111.2 | 287.4 | 329.4 | 108.1 | 256.8
707 | 468 | 111.5 | 286.7 | 330.9 | 108.9 | 256.6
708 | 469 | 111.8 | 287.6 | 336.1 | 110.1 | 257.3
709 | 470 | 112.2 | 289.5 | 338.7 | 112 | 258.1
710 | 471 | 112.5 | 290.5 | 340.2 | 111.8 | 259
711 | 472 | 112.8 | 292 | 340.8 | 112.2 | 259.9
712 | 473 | 113.2 | 293.6 | 339.7 | 113.6 | 259.6
713 | 474 | 113.5 | 293.3 | 339.5 | 113.5 | 258.8
714 | 475 | 113.9 | 293.6 | 339.4 | 114 | 259.7
715 | 476 | 114.3 | 293.5 | 339.1 | 112.6 | 260.9
716 | 477 | 114.6 | 294.2 | 342.6 | 112.3 | 262
717 | 478 | 115 | 295.5 | 344.1 | 114.9 | 262.5
718 | 479 | 115.3 | 295.7 | 345.2 | 115 | 263
719 | 480 | 115.7 | 294.9 | 342.2 | 114.5 | 262.5
720 | 481 | 116.1 | 295.1 | 341.6 | 116.2 | 262.2
721 | 482 | 116.4 | 295.2 | 341.8 | 117.4 | 261.2
722 | 483 | 116.8 | 295.8 | 342.9 | 119 | 261.7
723 | 484 | 117.2 | 295.7 | 340.6 | 117.9 | 261
724 | 485 | 117.6 | 295.4 | 341.7 | 118.7 | 260.6
725 | 486 | 117.9 | 296.2 | 341.5 | 120.3 | 260.9
726 | 487 | 118.3 | 296.1 | 339.2 | 120.1 | 260.7
727 | 488 | 118.7 | 296.6 | 338.8 | 119.6 | 261.6
728 | 489 | 119.1 | 296.5 | 336.2 | 119.1 | 262.4
729 | 490 | 119.5 | 296.1 | 335.3 | 120.5 | 261.8
730 | 491 | 119.9 | 296.1 | 334.5 | 121.9 | 261.8
731 | 492 | 120.2 | 295 | 332.6 | 121.2 | 262
732 | 493 | 120.6 | 295.1 | 334.7 | 122.1 | 262.8
733 | 494 | 121 | 294.8 | 335.6 | 121.8 | 263.4
734 | 495 | 121.4 | 294.7 | 338 | 122.4 | 263.5
735 | 496 | 121.8 | 294.4 | 337.6 | 122.7 | 263
736 | 497 | 122.2 | 294 | 337 | 123.6 | 262.8
737 | 498 | 122.6 | 294 | 337.3 | 122.2 | 263.2
738 | 499 | 123 | 293.6 | 334.2 | 121.2 | 263.1
739 | 500 | 123.4 | 293.6 | 334 | 119.8 | 263.7
740 | 501 | 123.8 | 293.6 | 335.5 | 121.1 | 265
741 | 502 | 124.2 | 294.9 | 336.9 | 121.3 | 266.4
742 | 503 | 124.6 | 295.9 | 336.1 | 121.7 | 266.8
743 | 504 | 125 | 295.4 | 334.1 | 121.8 | 267.3
744 | 505 | 125.5 | 294.1 | 334.3 | 121.6 | 267.7
745 | 506 | 125.9 | 293.7 | 337 | 122.7 | 267.4
746 | 507 | 126.3 | 293.1 | 337.8 | 124.7 | 267.6
747 | 508 | 126.7 | 292.6 | 338.1 | 126.3 | 267.1
748 | 509 | 127.1 | 293.7 | 339.6 | 127.4 | 267.9
749 | 510 | 127.5 | 293.2 | 337.1 | 127 | 267.9
750 | 511 | 128 | 293.4 | 338.8 | 128.2 | 267.7
751 | 512 | 128.4 | 294.3 | 338.2 | 128 | 268.6
752 | 513 | 128.8 | 294.4 | 339 | 129 | 269.2
753 | 514 | 129.2 | 295.1 | 339.9 | 131.3 | 269.5
754 | 515 | 129.6 | 295.5 | 338.1 | 131.1 | 269.1
755 | 516 | 130.1 | 296.3 | 341.5 | 131.3 | 269.6
756 | 517 | 130.5 | 297.9 | 347.9 | 132.5 | 273.2
757 | 518 | 130.9 | 298.7 | 348.2 | 131.6 | 273.9
758 | 519 | 131.4 | 299.1 | 349 | 132.2 | 274.1
759 | 520 | 131.8 | 300.2 | 354.3 | 133.4 | 274.9
760 | 521 | 132.2 | 300.3 | 351.6 | 131.9 | 275.2
761 | 522 | 132.7 | 300.4 | 351.1 | 130 | 275.5
762 | 523 | 133.1 | 301.9 | 352.4 | 131.2 | 276.5
763 | 524 | 133.5 | 300.3 | 349.1 | 131.6 | 276.1
764 | 525 | 134 | 301.4 | 352.3 | 133.6 | 276.2
765 | 526 | 134.4 | 302.3 | 351.4 | 134.4 | 276
766 | 527 | 134.9 | 302.1 | 349.7 | 134.9 | 275.6
767 | 528 | 135.3 | 302.4 | 353.3 | 136 | 275.7
768 | 529 | 135.8 | 303 | 351.6 | 137.4 | 275.2
769 | 530 | 136.2 | 302.2 | 345.1 | 137.6 | 274.2
770 | 531 | 136.7 | 299.9 | 339.8 | 136.4 | 272.6
771 | 532 | 137.1 | 299.9 | 341.9 | 136.5 | 273.9
772 | 533 | 137.5 | 299 | 338 | 135.7 | 273.8
773 | 534 | 138 | 298.7 | 337.6 | 135.2 | 273.6
774 | 535 | 138.4 | 299.5 | 337.3 | 136 | 274.1
775 | 536 | 138.9 | 299.1 | 335.5 | 136.3 | 274.3
776 | 537 | 139.3 | 299.6 | 335.6 | 137 | 274.6
777 | 538 | 139.7 | 299.8 | 336.6 | 137.4 | 274.7
778 | 539 | 140.2 | 300.4 | 336.8 | 137.2 | 275.2
779 | 540 | 140.6 | 301 | 341.1 | 138.1 | 276.5
780 | 541 | 141 | 301.5 | 345.1 | 139.7 | 278.8
781 | 542 | 141.5 | 303 | 347.4 | 140.3 | 279.2
782 | 543 | 141.9 | 303.7 | 346.2 | 139.3 | 278.8
783 | 544 | 142.3 | 304.2 | 344.7 | 139.7 | 278.8
784 | 545 | 142.8 | 306.8 | 348.3 | 142.1 | 278.7
785 | 546 | 143.2 | 307.4 | 350.8 | 142.4 | 278.9
786 | 547 | 143.6 | 308 | 351.5 | 142.3 | 279
787 | 548 | 144.1 | 305.4 | 346.2 | 140.9 | 277.5
788 | 549 | 144.5 | 303.6 | 341.4 | 140.3 | 276.2
789 | 550 | 144.9 | 302.3 | 338.1 | 140.1 | 275.6
790 | 551 | 145.4 | 301.1 | 335.8 | 140.1 | 275.7
791 | 552 | 145.8 | 300.7 | 335.2 | 141.6 | 276.1
792 | 553 | 146.2 | 300.1 | 335.9 | 142.4 | 276.4
793 | 554 | 146.6 | 299.2 | 334.2 | 142.7 | 275.8
794 | 555 | 147 | 299.7 | 335.4 | 143.8 | 275.8
795 | 556 | 147.5 | 299 | 334.5 | 142.8 | 275.8
796 | 557 | 147.9 | 298.9 | 334.6 | 142.1 | 276.8
797 | 558 | 148.3 | 299.5 | 334.7 | 142 | 277.9
798 | 559 | 148.7 | 300.7 | 336.7 | 142.7 | 279
799 | 560 | 149.1 | 302.6 | 340.8 | 144.6 | 281
800 | 561 | 149.5 | 303.3 | 340.3 | 144.7 | 281.5
801 | 562 | 149.9 | 302.8 | 338.6 | 144.7 | 280.2
802 | 563 | 150.4 | 302.9 | 339.4 | 145.7 | 279.9
803 | 564 | 150.8 | 302.7 | 340.9 | 145.5 | 279.9
804 | 565 | 151.2 | 303.7 | 341.8 | 146.7 | 280.2
805 | 566 | 151.6 | 304.4 | 342.2 | 147.4 | 280.1
806 | 567 | 152 | 304.9 | 341.3 | 147 | 280.1
807 | 568 | 152.4 | 304.6 | 340.4 | 147.3 | 280.3
808 | 569 | 152.8 | 304 | 337.6 | 147.6 | 280.2
809 | 570 | 153.2 | 303.1 | 336 | 147.1 | 279.6
810 | 571 | 153.6 | 302.5 | 340.2 | 149.2 | 279.7
811 | 572 | 154 | 302.5 | 337.8 | 149.3 | 279.1
812 | 573 | 154.4 | 302.6 | 337.1 | 148.7 | 279.3
813 | 574 | 154.9 | 302.9 | 339 | 149.1 | 279.9
814 | 575 | 155.3 | 303 | 338.2 | 149 | 280.6
815 | 576 | 155.7 | 302.8 | 337.6 | 148.9 | 281.1
816 | 577 | 156 | 303.5 | 337.4 | 149.7 | 281.7
817 | 578 | 156.4 | 303.7 | 334.8 | 149.4 | 281.1
818 | 579 | 156.8 | 302.5 | 331.7 | 149.1 | 280.1
819 | 580 | 157.2 | 301.7 | 330.7 | 149.2 | 279.8
820 | 581 | 157.6 | 301 | 331.4 | 150.1 | 279.7
821 | 582 | 158 | 301 | 330.7 | 151.1 | 280
822 | 583 | 158.4 | 301.7 | 329.5 | 151 | 279.7
823 | 584 | 158.8 | 302.3 | 330 | 151.7 | 280.1
824 | 585 | 159.1 | 303 | 334.1 | 152.2 | 281
825 | 586 | 159.5 | 302.9 | 336.8 | 153.3 | 281.8
826 | 587 | 159.9 | 304 | 341.1 | 152.9 | 282.4
827 | 588 | 160.3 | 304.4 | 341.7 | 153.3 | 283.2
828 | 589 | 160.7 | 304.9 | 341.6 | 154 | 283.6
829 | 590 | 161 | 306.4 | 342.7 | 154.6 | 284
830 | 591 | 161.4 | 307.5 | 343.4 | 154.8 | 285
831 | 592 | 161.8 | 308.3 | 342.6 | 154.1 | 285.2
832 | 593 | 162.2 | 309.1 | 343 | 153.8 | 285
833 | 594 | 162.6 | 309.2 | 342.9 | 154.4 | 285.4
834 | 595 | 163 | 310.5 | 344.5 | 154.9 | 286.1
835 | 596 | 163.3 | 311.2 | 342.5 | 154 | 286.1
836 | 597 | 163.7 | 311.2 | 340.4 | 152.8 | 285.7
837 | 598 | 164.1 | 311.4 | 339.3 | 153.5 | 286.3
838 | 599 | 164.5 | 310.8 | 338.4 | 153.2 | 285.9
839 | 600 | 164.9 | 310.3 | 337.6 | 153.3 | 285.8
840 | 601 | 165.2 | 309.3 | 336.8 | 154.1 | 285.2
841 | 602 | 165.6 | 309 | 337.5 | 155.9 | 284.8
842 | 603 | 166 | 307.2 | 338.2 | 155.9 | 284.8
843 | 604 | 166.3 | 307 | 342.3 | 157.5 | 285.8
844 | 605 | 166.7 | 307.9 | 342.9 | 158.7 | 286
845 | 606 | 167.1 | 308.5 | 343.3 | 158.7 | 285.9
846 | 607 | 167.4 | 308.2 | 343.6 | 158.9 | 285.5
847 | 608 | 167.8 | 307.3 | 342.1 | 158.6 | 285.4
848 | 609 | 168.2 | 307.2 | 340.9 | 159.5 | 285.5
849 | 610 | 168.6 | 307.2 | 342.9 | 159.3 | 285.4
850 | 611 | 168.9 | 307.9 | 344.5 | 160.7 | 286.3
851 | 612 | 169.3 | 307.3 | 348.1 | 160.5 | 286.3
852 | 613 | 169.7 | 307.2 | 346.1 | 161.4 | 286.5
853 | 614 | 170.1 | 305.9 | 343.5 | 162.5 | 286
854 | 615 | 170.4 | 303.9 | 339.5 | 161.6 | 285.2
855 | 616 | 170.8 | 303 | 338.7 | 161.5 | 284.8
856 | 617 | 171.2 | 303.5 | 341.2 | 163.2 | 284.8
857 | 618 | 171.6 | 304.5 | 344 | 163.9 | 285.6
858 | 619 | 172 | 305.4 | 345.3 | 165.4 | 286
859 | 620 | 172.3 | 306.8 | 346.7 | 166.5 | 286.3
860 | 621 | 172.7 | 309 | 351.1 | 167.2 | 287
861 | 622 | 173.1 | 309.8 | 351.1 | 167.6 | 287.2
862 | 623 | 173.5 | 309.7 | 350.9 | 167 | 287.3
863 | 624 | 173.9 | 310.5 | 352.9 | 168.1 | 287.8
864 | 625 | 174.2 | 311 | 351.2 | 168.5 | 287.2
865 | 626 | 174.6 | 311.4 | 349.9 | 169.2 | 286.9
866 | 627 | 175 | 311.7 | 347.8 | 168.3 | 287.2
867 | 628 | 175.4 | 313.1 | 349.4 | 168.6 | 288
868 | 629 | 175.8 | 313.9 | 349.6 | 168.2 | 288.8
869 | 630 | 176.2 | 314.4 | 346.4 | 168.6 | 288.6
870 | 631 | 176.6 | 314.4 | 345 | 169 | 288.1
871 | 632 | 176.9 | 315.3 | 346.3 | 170.5 | 288.5
872 | 633 | 177.3 | 315.8 | 345.4 | 171.2 | 289.1
873 | 634 | 177.7 | 315.7 | 342.4 | 170.7 | 289.2
874 | 635 | 178.1 | 315.1 | 340.6 | 170.2 | 288.8
875 | 636 | 178.5 | 316 | 341.7 | 170.4 | 289.4
876 | 637 | 178.9 | 315.9 | 341 | 169.9 | 289.4
877 | 638 | 179.3 | 316.1 | 345.3 | 171.7 | 290
878 | 639 | 179.7 | 316.7 | 349 | 172.6 | 291
879 | 640 | 180.1 | 318.3 | 351.9 | 173.1 | 291.3
880 | 641 | 180.5 | 318.7 | 351.1 | 173 | 291.6
881 | 642 | 180.8 | 317.7 | 348.5 | 173.6 | 290.5
882 | 643 | 181.2 | 315.8 | 344.3 | 172.1 | 289.1
883 | 644 | 181.6 | 314.8 | 343.2 | 172.2 | 288.9
884 | 645 | 182 | 313.7 | 341.8 | 172.8 | 288.5
885 | 646 | 182.4 | 313.7 | 343.5 | 173.8 | 288.8
886 | 647 | 182.8 | 313.8 | 347.2 | 174.6 | 289.6
887 | 648 | 183.2 | 315.1 | 350.8 | 175.6 | 290.4
888 | 649 | 183.6 | 315.6 | 352.1 | 176.1 | 290.4
889 | 650 | 184 | 315.7 | 353.5 | 176.1 | 290.5
890 | 651 | 184.3 | 317.7 | 353.8 | 176.2 | 291.8
891 | 652 | 184.7 | 316.3 | 349.5 | 175.5 | 291
892 | 653 | 185.1 | 315 | 348.6 | 176.3 | 290
893 | 654 | 185.5 | 314.6 | 348.9 | 175.9 | 290.4
894 | 655 | 185.8 | 315.8 | 351.1 | 176 | 291.6
895 | 656 | 186.2 | 316.6 | 349.1 | 175.8 | 291.8
896 | 657 | 186.6 | 317 | 347.3 | 175.3 | 292.3
897 | 658 | 186.9 | 317.1 | 345.9 | 175.3 | 292.7
898 | 659 | 187.3 | 316.8 | 344.5 | 176 | 292.9
899 | 660 | 187.6 | 317.6 | 344.2 | 176.4 | 293.4
900 | 661 | 188 | 317.7 | 343.6 | 176.5 | 293.4
901 | 662 | 188.4 | 317.8 | 343.9 | 176.9 | 293.6
902 | 663 | 188.7 | 319.1 | 345.3 | 177.8 | 294
903 | 664 | 189.1 | 318.7 | 344.6 | 178.5 | 294.2
904 | 665 | 189.4 | 318.3 | 342.4 | 179.3 | 293.3
905 | 666 | 189.8 | 317.6 | 341.4 | 180.1 | 293
906 | 667 | 190.1 | 317.6 | 342.9 | 179.8 | 293.5
907 | 668 | 190.5 | 318.7 | 351.2 | 182.5 | 294.7
908 | 669 | 190.8 | 320.3 | 353.3 | 183.2 | 295.9
909 | 670 | 191.2 | 321.2 | 354 | 183.9 | 296
910 | 671 | 191.6 | 322.2 | 354.3 | 184.5 | 296.2
911 | 672 | 191.9 | 322.9 | 356.2 | 184.1 | 296.6
912 | 673 | 192.3 | 323.2 | 357.7 | 184.5 | 296.9
913 | 674 | 192.6 | 325.9 | 362.8 | 185.4 | 298
914 | 675 | 193 | 326.7 | 362.8 | 185.8 | 298.7
915 | 676 | 193.3 | 328.1 | 363.9 | 186.6 | 299.2
916 | 677 | 193.7 | 329.1 | 361.9 | 186.8 | 299
917 | 678 | 194.1 | 328.9 | 362 | 187.6 | 298.6
918 | 679 | 194.4 | 329.8 | 361.6 | 188.2 | 298.9
919 | 680 | 194.8 | 331.3 | 361.8 | 188.9 | 299.8
920 | 681 | 195.2 | 331 | 359.4 | 188 | 299.8
921 | 682 | 195.5 | 331 | 357.7 | 187.4 | 299.9
922 | 683 | 195.9 | 331.6 | 360 | 187.7 | 300.7
923 | 684 | 196.2 | 334.1 | 363.7 | 189.7 | 302.6
924 | 685 | 196.6 | 336.1 | 367.8 | 190 | 304
925 | 686 | 197 | 338 | 367 | 189.7 | 304.8
926 | 687 | 197.3 | 338.7 | 366.3 | 189.9 | 305
927 | 688 | 197.7 | 339.3 | 367.5 | 191.6 | 305
928 | 689 | 198 | 341.8 | 368.9 | 191.2 | 305.6
929 | 690 | 198.4 | 344 | 370.6 | 190.6 | 306.1
930 | 691 | 198.8 | 345 | 369.9 | 191.2 | 307
931 | 692 | 199.1 | 345.4 | 369.3 | 191.4 | 307.2
932 | 693 | 199.5 | 346.1 | 368.5 | 191.7 | 306.8
933 | 694 | 199.8 | 346.2 | 367.3 | 191.8 | 306.4
934 | 695 | 200.2 | 345.7 | 365.7 | 192.2 | 306.4
935 | 696 | 200.5 | 345.7 | 363.3 | 191.5 | 306
936 | 697 | 200.9 | 346.4 | 364.1 | 191.7 | 306.9
937 | 698 | 201.2 | 347.1 | 364.3 | 192.7 | 308.6
938 | 699 | 201.6 | 347.2 | 363.8 | 192.6 | 308.5
939 | 700 | 201.9 | 347.6 | 363.5 | 192.5 | 308.4
940 | 701 | 202.3 | 348.6 | 364 | 193.2 | 308.6
941 | 702 | 202.6 | 349.7 | 367.5 | 193.3 | 309
942 | 703 | 203 | 351.5 | 376.3 | 193.9 | 312.2
943 | 704 | 203.4 | 354.3 | 385.3 | 195 | 315.5
944 | 705 | 203.7 | 354.2 | 386.8 | 195.3 | 315.2
945 | 706 | 204.1 | 356 | 390.2 | 196.5 | 315.1
946 | 707 | 204.5 | 357.9 | 394.1 | 196.1 | 316.4
947 | 708 | 204.8 | 360.9 | 397.7 | 196.8 | 318.6
948 | 709 | 205.2 | 361.9 | 398.7 | 197.3 | 319.4
949 | 710 | 205.6 | 363.5 | 403.3 | 198.4 | 320.1
950 | 711 | 206 | 364.2 | 404.7 | 199.3 | 320.2
951 | 712 | 206.4 | 364.1 | 406.9 | 199.4 | 319.6
952 | 713 | 206.8 | 364 | 407 | 199.5 | 319.7
953 | 714 | 207.2 | 363.4 | 407.4 | 199.1 | 320.1
954 | 715 | 207.6 | 365.2 | 410.4 | 200.4 | 321.4
955 | 716 | 208 | 367.2 | 413 | 201.1 | 322.8
956 | 717 | 208.4 | 369.2 | 420.7 | 202.4 | 325.7
957 | 718 | 208.8 | 372 | 425.1 | 203.2 | 327.8
958 | 719 | 209.2 | 372.7 | 423.6 | 203.2 | 326.9
959 | 720 | 209.6 | 372.5 | 420.5 | 203.1 | 326.9
960 | 721 | 210 | 373.3 | 421.5 | 203.7 | 328
961 | 722 | 210.4 | 374.9 | 422.8 | 204.4 | 329.1
962 | 723 | 210.8 | 376.4 | 428.7 | 205 | 330.1
963 | 724 | 211.2 | 379 | 436.7 | 206 | 331.3
964 | 725 | 211.6 | 381.2 | 439.8 | 206.4 | 334.4
965 | 726 | 212 | 381.9 | 437.9 | 206.6 | 335.2
966 | 727 | 212.4 | 382.7 | 436.6 | 206.7 | 335.7
967 | 728 | 212.7 | 382.1 | 433.7 | 206.9 | 335.4
968 | 729 | 213.1 | 382.9 | 437.7 | 207.6 | 335.8
969 | 730 | 213.5 | 383.7 | 438.8 | 207.7 | 337
970 | 731 | 213.9 | 384.1 | 441.3 | 208.6 | 337.8
971 | 732 | 214.3 | 386.5 | 445.9 | 209.2 | 338.8
972 | 733 | 214.7 | 389.3 | 455 | 210 | 341.3
973 | 734 | 215.1 | 391 | 466.3 | 210.9 | 343.4
974 | 735 | 215.5 | 393 | 472.5 | 212.1 | 345
975 | 736 | 215.9 | 393.2 | 471.7 | 211.7 | 345.4
976 | 737 | 216.3 | 394.1 | 473.7 | 212 | 346.6
977 | 738 | 216.7 | 394.9 | 471.7 | 212.2 | 346.7
978 | 739 | 217.2 | 394.9 | 469.6 | 212.4 | 346.7
979 | 740 | 217.6 | 396.7 | 471.1 | 213 | 348.8
980 | 741 | 218 | 397.8 | 471.5 | 213.1 | 350.8
981 | 742 | 218.4 | 398.5 | 467.8 | 213.1 | 351.8
982 | 743 | 218.9 | 399.4 | 466.3 | 213 | 351.7
983 | 744 | 219.3 | 402 | 468.3 | 213.6 | 353.5
984 | 745 | 219.7 | 403 | 470.2 | 214.1 | 355.2
985 | 746 | 220.1 | 401.8 | 466.8 | 213.6 | 354.2
986 | 747 | 220.5 | 401.9 | 465.6 | 213.5 | 354.2
987 | 748 | 220.9 | 401.9 | 463.1 | 213.3 | 354.3
988 | 749 | 221.3 | 404 | 471.9 | 213.7 | 356.4
989 | 750 | 221.7 | 405.8 | 475.8 | 214.5 | 357.1
990 | 751 | 222.1 | 407.9 | 479.6 | 215 | 358
991 | 752 | 222.5 | 406.1 | 473.9 | 215.1 | 357.2
992 | 753 | 222.8 | 405.3 | 475.3 | 215.5 | 357.3
993 | 754 | 223.3 | 405.8 | 472.7 | 215.8 | 357.6
994 | 755 | 223.7 | 405.8 | 468.5 | 216.1 | 357.9
995 | 756 | 224.1 | 405.6 | 462.1 | 216 | 358.1
996 | 757 | 224.5 | 404.1 | 458.3 | 216 | 357.7
997 | 758 | 224.8 | 404.3 | 458 | 216.7 | 359.1
998 | 759 | 225.2 | 403.3 | 453.1 | 216.7 | 358.8
999 | 760 | 225.6 | 401.9 | 450.8 | 216.7 | 358.5
1000 | 761 | 226 | 403.1 | 454.7 | 217.5 | 358.8
1001 | 762 | 226.4 | 405 | 459.9 | 217.9 | 360.5
1002 | 763 | 226.7 | 406.5 | 465.3 | 218.8 | 362.8
1003 | 764 | 227.1 | 406.6 | 466.6 | 219 | 363.8
1004 | 765 | 227.4 | 406.5 | 464.4 | 219.7 | 363
1005 | 766 | 227.8 | 408.2 | 467.8 | 220.3 | 365.1
1006 | 767 | 228.1 | 409.2 | 465.7 | 220.6 | 366.1
1007 | 768 | 228.4 | 409.5 | 468.5 | 220.9 | 365.9
1008 | 769 | 228.8 | 410.9 | 472.8 | 221.4 | 367.7
1009 | 770 | 229.1 | 410.8 | 473.1 | 221.7 | 369.2
1010 | 771 | 229.4 | 411.2 | 475 | 222.1 | 370.3
1011 | 772 | 229.7 | 413.6 | 476.8 | 222.7 | 372.1
1012 | 773 | 230 | 414.3 | 478.3 | 222.9 | 373.1
1013 | 774 | 230.3 | 413.2 | 473 | 222.9 | 372.2
1014 | 775 | 230.5 | 411.2 | 469.2 | 222.9 | 371.4
1015 | 776 | 230.8 | 411.8 | 473.9 | 223.6 | 372.7
1016 | 777 | 231.1 | 413.9 | 476.2 | 224.5 | 374.6
1017 | 778 | 231.3 | 415.5 | 476.4 | 224.9 | 375
1018 | 779 | 231.6 | 412.8 | 470.9 | 224.7 | 372.9
1019 | 780 | 231.9 | 410.9 | 471.9 | 224.8 | 372.5
1020 | 781 | 232.1 | 411.2 | 472 | 225 | 373.8
1021 | 782 | 232.3 | 412.7 | 473 | 225.5 | 374.9
1022 | 783 | 232.6 | 414.1 | 479 | 225.9 | 376.3
1023 | 784 | 232.8 | 418 | 479.2 | 226.4 | 377.8
1024 | 785 | 233 | 417.7 | 474.4 | 226.4 | 377.5
1025 | 786 | 233.2 | 417.1 | 476.1 | 226.8 | 379.1
1026 | 787 | 233.4 | 416.7 | 475.1 | 226.8 | 379.4
1027 | 788 | 233.6 | 416.5 | 474.3 | 227.2 | 379.7
1028 | 789 | 233.8 | 415.6 | 472.2 | 227.1 | 379.2
1029 | 790 | 234 | 416.5 | 473.4 | 227.3 | 380.5
1030 | 791 | 234.2 | 417.1 | 472.2 | 227.4 | 380.5
1031 | 792 | 234.4 | 416.2 | 470.9 | 227.4 | 379.4
1032 | 793 | 234.6 | 416.3 | 471.3 | 227.4 | 380.3
1033 | 794 | 234.9 | 417.1 | 471.2 | 227.4 | 381.4
1034 | 795 | 235.1 | 415.4 | 465 | 227.3 | 379.8
1035 | 796 | 235.3 | 414.9 | 464.6 | 227.4 | 379.4
1036 | 797 | 235.6 | 418 | 465.7 | 227.5 | 380.5
1037 | 798 | 235.8 | 419.3 | 470.4 | 227.9 | 382.3
1038 | 799 | 236 | 421.7 | 479 | 228.4 | 384.1
1039 | 800 | 236.3 | 422.4 | 478.7 | 228.9 | 384.3
1040 | 801 | 236.5 | 423.1 | 477.6 | 229.4 | 384.2
1041 | 802 | 236.8 | 424.5 | 480.1 | 230.3 | 384.9
1042 | 803 | 237.2 | 424.6 | 478.5 | 230.9 | 385.4
1043 | 804 | 237.7 | 423.7 | 476.8 | 231.4 | 385.2
1044 | 805 | 238.1 | 422.1 | 473 | 231.7 | 385.1
1045 | 806 | 238.5 | 419.9 | 469.2 | 231.9 | 386.1
1046 | 807 | 238.9 | 419.6 | 470.5 | 232.3 | 386.4
1047 | 808 | 239.2 | 419.7 | 470.6 | 232.5 | 387.7
1048 | 809 | 239.6 | 418.9 | 469.3 | 232.8 | 387.7
1049 | 810 | 240 | 418 | 468.2 | 233.3 | 388.4
1050 | 811 | 240.4 | 418.2 | 469.9 | 233.6 | 389.4
1051 | 812 | 240.8 | 419.4 | 470 | 234.1 | 391.1
1052 | 813 | 241.2 | 421.9 | 474.6 | 234.6 | 393.9
1053 | 814 | 241.6 | 423.7 | 481 | 235.3 | 396.4
1054 | 815 | 241.9 | 427.7 | 492.3 | 236.4 | 400.4
1055 | 816 | 242.3 | 431.6 | 499.8 | 237.3 | 404.6
1056 | 817 | 242.7 | 436.8 | 511.3 | 238.2 | 408.3
1057 | 818 | 243.1 | 437.9 | 511 | 239 | 407.6
1058 | 819 | 243.4 | 437.5 | 509.5 | 239.3 | 406.2
1059 | 820 | 243.8 | 438.3 | 508.8 | 240 | 406.1
1060 | 821 | 244.1 | 438.8 | 511.6 | 240.4 | 405.9
1061 | 822 | 244.5 | 439.9 | 515 | 240.8 | 406.8
1062 | 823 | 244.8 | 440.9 | 514.6 | 241 | 406
1063 | 824 | 245.2 | 440.6 | 512.6 | 241.2 | 406.2
1064 | 825 | 245.5 | 440.4 | 510.3 | 241.4 | 404.9
1065 | 826 | 245.9 | 438.6 | 504.8 | 241.5 | 405.7
1066 | 827 | 246.3 | 435.6 | 495.8 | 241.6 | 404.1
1067 | 828 | 246.6 | 432.1 | 495.9 | 241.6 | 402.3
1068 | 829 | 247 | 432.2 | 499 | 241.8 | 404.2
1069 | 830 | 247.4 | 429.3 | 494.9 | 241.9 | 402.6
1070 | 831 | 247.7 | 428.7 | 492.7 | 242 | 403.1
1071 | 832 | 248.1 | 430.1 | 496.6 | 242.3 | 405.5
1072 | 833 | 248.4 | 431.1 | 496.2 | 242.6 | 406.3
1073 | 834 | 248.8 | 430.9 | 497 | 242.8 | 406.2
1074 | 835 | 249.1 | 434.8 | 501.5 | 243.1 | 407.7
1075 | 836 | 249.5 | 434.4 | 495.7 | 243.3 | 406.6
1076 | 837 | 249.9 | 432.6 | 492.5 | 243.4 | 405
1077 | 838 | 250.2 | 431.6 | 494.3 | 243.6 | 405.6
1078 | 839 | 250.6 | 432.4 | 497.6 | 243.9 | 406.6
1079 | 840 | 251 | 437.3 | 505.8 | 244.5 | 410
1080 | 841 | 251.4 | 438.7 | 504 | 244.9 | 409.4
1081 | 842 | 251.7 | 438 | 507.3 | 245.2 | 408.7
1082 | 843 | 252 | 437.6 | 507 | 245.4 | 408.6
1083 | 844 | 252.4 | 435.2 | 501.8 | 245.7 | 408.3
1084 | 845 | 252.7 | 435.5 | 505.6 | 246.1 | 409.2
1085 | 846 | 253.1 | 436.7 | 509.5 | 246.4 | 410.4
1086 | 847 | 253.5 | 436.3 | 506.6 | 246.7 | 410.6
1087 | 848 | 253.9 | 434.9 | 498.6 | 246.8 | 409.3
1088 | 849 | 254.3 | 433.1 | 491.8 | 246.8 | 408.2
1089 | 850 | 254.7 | 430.8 | 484.6 | 246.8 | 407.1
1090 | 851 | 255.1 | 431.1 | 477.9 | 246.8 | 407
1091 | 852 | 255.5 | 429.8 | 472.1 | 246.9 | 406.6
1092 | 853 | 256 | 428.2 | 466.7 | 247.1 | 406.1
1093 | 854 | 256.4 | 428.1 | 465.2 | 247.2 | 406.6
1094 | 855 | 256.7 | 431.4 | 464.2 | 247.3 | 408.3
1095 | 856 | 257.1 | 430.8 | 461.8 | 247.3 | 407.8
1096 | 857 | 257.4 | 429.7 | 463.2 | 247.4 | 408.1
1097 | 858 | 257.8 | 428.5 | 465.1 | 247.5 | 408.6
1098 | 859 | 258.2 | 427.7 | 464.4 | 247.6 | 409
1099 | 860 | 258.6 | 427.9 | 460.3 | 247.7 | 410.2
1100 | 861 | 258.9 | 426.2 | 456.2 | 247.8 | 408.7
1101 | 862 | 259.3 | 425.1 | 454.3 | 248.1 | 407.8
1102 | 863 | 259.7 | 424.9 | 454.3 | 248.3 | 407.7
1103 | 864 | 260 | 425.1 | 453.8 | 248.7 | 408.7
1104 | 865 | 260.4 | 425.3 | 455.1 | 249.1 | 409
1105 | 866 | 260.8 | 424.9 | 453 | 249.4 | 408.8
1106 | 867 | 261.1 | 426.6 | 457.9 | 249.8 | 410.3
1107 | 868 | 261.5 | 427.7 | 458.8 | 250.2 | 411.3
1108 | 869 | 261.8 | 428.8 | 461.9 | 250.7 | 412.2
1109 | 870 | 262.2 | 431.1 | 470 | 251.2 | 414.2
1110 | 871 | 262.5 | 430.8 | 468.8 | 251.6 | 414.6
1111 | 872 | 262.9 | 428.6 | 464.6 | 251.9 | 413.8
1112 | 873 | 263.2 | 427.7 | 464.2 | 252.3 | 414.2
1113 | 874 | 263.6 | 427.4 | 467.7 | 252.9 | 415.5
1114 | 875 | 263.9 | 430.8 | 478.9 | 253.8 | 418.3
1115 | 876 | 264.2 | 432 | 484.6 | 254.2 | 418.5
1116 | 877 | 264.6 | 434 | 488.5 | 254.7 | 419.4
1117 | 878 | 264.9 | 433 | 486.6 | 255 | 417.7
1118 | 879 | 265.2 | 432.5 | 485.9 | 255.3 | 417.2
1119 | 880 | 265.6 | 434.1 | 494.9 | 255.7 | 418.1
1120 | 881 | 265.9 | 437.2 | 501.5 | 256.3 | 420.2
1121 | 882 | 266.2 | 438.3 | 501.3 | 256.9 | 420.7
1122 | 883 | 266.6 | 440.1 | 506.5 | 257.4 | 421.1
1123 | 884 | 266.9 | 443.3 | 511.3 | 257.8 | 422.6
1124 | 885 | 267.3 | 443.2 | 506.8 | 258.2 | 422.9
1125 | 886 | 267.6 | 443.3 | 503 | 258.5 | 423.9
1126 | 887 | 267.9 | 442.1 | 499.3 | 258.8 | 423.3
1127 | 888 | 268.3 | 442.4 | 497.6 | 259.2 | 424.5
1128 | 889 | 268.6 | 442.5 | 498.3 | 259.6 | 425.2
1129 | 890 | 269 | 445.9 | 507.8 | 260.1 | 427.6
1130 | 891 | 269.3 | 446 | 509.7 | 260.6 | 429.3
1131 | 892 | 269.7 | 449.3 | 519.5 | 261.3 | 432.6
1132 | 893 | 270 | 450.7 | 522.4 | 261.7 | 432.7
1133 | 894 | 270.4 | 449.9 | 518.9 | 262 | 431.4
1134 | 895 | 270.7 | 451.7 | 521.6 | 262.3 | 434
1135 | 896 | 271.1 | 453.4 | 525.6 | 262.7 | 435.7
1136 | 897 | 271.4 | 456.9 | 536.6 | 263.2 | 438.5
1137 | 898 | 271.7 | 456.9 | 538.3 | 263.6 | 436.5
1138 | 899 | 272.1 | 457.4 | 540.3 | 264.1 | 435.3
1139 | 900 | 272.4 | 457.3 | 539.7 | 264.3 | 434.9
1140 | 901 | 272.7 | 457.8 | 535.6 | 264.5 | 434
1141 | 902 | 273.1 | 455.7 | 528.3 | 264.7 | 432.8
1142 | 903 | 273.4 | 453.4 | 522.5 | 264.9 | 431.8
1143 | 904 | 273.7 | 453.4 | 522.4 | 265.1 | 432.3
1144 | 905 | 274.1 | 455.6 | 526.8 | 265.6 | 434.5
1145 | 906 | 274.4 | 457.5 | 530.1 | 265.9 | 437.5
1146 | 907 | 274.7 | 457.5 | 529.6 | 266.2 | 437.2
1147 | 908 | 275.1 | 453.7 | 521.5 | 266.3 | 434.4
1148 | 909 | 275.4 | 451.4 | 520.4 | 266.6 | 433.9
1149 | 910 | 275.8 | 449.6 | 515.7 | 266.8 | 433.4
1150 | 911 | 276.1 | 448.2 | 514.5 | 267.2 | 432.4
1151 | 912 | 276.5 | 450.1 | 523.4 | 267.7 | 435.6
1152 | 913 | 276.8 | 451.7 | 523.1 | 268.3 | 437.4
1153 | 914 | 277.2 | 450.5 | 518.9 | 268.4 | 436
1154 | 915 | 277.5 | 448.4 | 516.6 | 268.7 | 435.8
1155 | 916 | 277.8 | 445.6 | 511.9 | 269.1 | 434.7
1156 | 917 | 278.2 | 443.3 | 508.7 | 269.3 | 433.8
1157 | 918 | 278.5 | 443.7 | 509.3 | 269.5 | 433.5
1158 | 919 | 278.8 | 443.6 | 503.1 | 269.7 | 433.1
1159 | 920 | 279.2 | 441.5 | 495.2 | 269.8 | 431.8
1160 | 921 | 279.5 | 440.4 | 489.1 | 270 | 431.5
1161 | 922 | 279.8 | 439.6 | 484.7 | 270.1 | 431.5
1162 | 923 | 280.1 | 440.6 | 480 | 270.2 | 432.4
1163 | 924 | 280.5 | 439.1 | 472.9 | 270.2 | 431.3
1164 | 925 | 280.8 | 438.4 | 472.7 | 270.5 | 431.6
1165 | 926 | 281.1 | 440 | 479 | 270.8 | 433
1166 | 927 | 281.3 | 440.5 | 476.9 | 271.1 | 432.6
1167 | 928 | 281.6 | 440.4 | 475.6 | 271.2 | 431.9
1168 | 929 | 282 | 438.6 | 471.4 | 271.4 | 430.9
1169 | 930 | 282.3 | 438.6 | 470.2 | 271.6 | 430.6
1170 | 931 | 282.6 | 440.1 | 471.2 | 271.9 | 432.3
1171 | 932 | 282.9 | 442 | 475.7 | 272.1 | 435.1
1172 | 933 | 283.3 | 444.3 | 475.7 | 272.2 | 437.1
1173 | 934 | 283.6 | 449 | 485.1 | 272.4 | 441.2
1174 | 935 | 283.9 | 451.7 | 489.2 | 272.6 | 441.7
1175 | 936 | 284.3 | 450.9 | 486.8 | 273 | 439.3
1176 | 937 | 284.6 | 451.9 | 495.8 | 273.3 | 440
1177 | 938 | 285 | 453.8 | 502 | 273.8 | 441.8
1178 | 939 | 285.3 | 455.2 | 499.4 | 274.1 | 442.5
1179 | 940 | 285.6 | 454.8 | 496.7 | 274.3 | 441.8
1180 | 941 | 286 | 453.8 | 498.7 | 274.6 | 441.3
1181 | 942 | 286.3 | 454.4 | 498.8 | 274.8 | 442.1
1182 | 943 | 286.6 | 454.9 | 500.6 | 275.2 | 442.1
1183 | 944 | 287 | 455.7 | 503.8 | 275.6 | 442.3
1184 | 945 | 287.4 | 458 | 514.7 | 276 | 444.9
1185 | 946 | 287.7 | 460.9 | 524.7 | 276.7 | 446.8
1186 | 947 | 288 | 460.2 | 523.8 | 277.1 | 445.6
1187 | 948 | 288.4 | 461.5 | 531.4 | 277.6 | 445.5
1188 | 949 | 288.8 | 464.1 | 531.5 | 278.1 | 446.7
1189 | 950 | 289.1 | 464.6 | 537.1 | 278.6 | 448
1190 | 951 | 289.5 | 469.2 | 556.2 | 279.1 | 451.4
1191 | 952 | 289.9 | 470.4 | 560.9 | 279.6 | 452.2
1192 | 953 | 290.3 | 470 | 556.5 | 280 | 450.6
1193 | 954 | 290.6 | 468.6 | 549.7 | 280.5 | 448.8
1194 | 955 | 291 | 467.6 | 544.2 | 280.9 | 447.7
1195 | 956 | 291.4 | 464.8 | 535.6 | 281.2 | 446.4
1196 | 957 | 291.8 | 463.4 | 527.1 | 281.4 | 445.9
1197 | 958 | 292.2 | 461.1 | 517.7 | 281.7 | 444.4
1198 | 959 | 292.6 | 458.9 | 510.4 | 282 | 443.3
1199 | 960 | 293 | 458.2 | 507.3 | 282.4 | 444.2
1200 | 961 | 293.4 | 458.8 | 503.4 | 282.7 | 445.8
1201 | 962 | 293.8 | 458.3 | 497.2 | 283 | 446.3
1202 | 963 | 294.3 | 457.1 | 493 | 283.4 | 444.9
1203 | 964 | 294.7 | 457.2 | 489.3 | 283.6 | 445.9
1204 | 965 | 295.1 | 458.3 | 490.8 | 284 | 446.6
1205 | 966 | 295.6 | 460.7 | 488.1 | 284.2 | 446.7
1206 | 967 | 296 | 461.1 | 487.3 | 284.6 | 446.7
1207 | 968 | 296.4 | 460.9 | 489.3 | 284.9 | 446.2
1208 | 969 | 296.8 | 459.1 | 487.5 | 285.3 | 445
1209 | 970 | 297.3 | 457.8 | 490.2 | 285.6 | 444.9
1210 | 971 | 297.7 | 457.3 | 491.4 | 286 | 445
1211 | 972 | 298.1 | 458.2 | 493 | 286.4 | 445.6
1212 | 973 | 298.4 | 459 | 491.8 | 286.7 | 445.8
1213 | 974 | 298.8 | 459.5 | 491.4 | 286.9 | 446.3
1214 | 975 | 299.2 | 460.6 | 490.9 | 287.2 | 446.9
1215 | 976 | 299.6 | 464.2 | 486.5 | 287.3 | 449.6
1216 | 977 | 300.1 | 465.2 | 485.9 | 287.5 | 448.6
1217 | 978 | 300.5 | 464.5 | 484.6 | 287.8 | 448.1
1218 | 979 | 301 | 465.3 | 490.6 | 288.2 | 449.1
1219 | 980 | 301.4 | 466.2 | 493.3 | 288.6 | 450
1220 | 981 | 301.8 | 465.3 | 492.9 | 288.9 | 448.7
1221 | 982 | 302.3 | 464 | 492.3 | 289.2 | 447.7
1222 | 983 | 302.7 | 463.9 | 495.1 | 289.6 | 448.3
1223 | 984 | 303.2 | 463.9 | 497.4 | 290.2 | 448.7
1224 | 985 | 303.6 | 464.8 | 497.5 | 290.5 | 448.7
1225 | 986 | 304.1 | 467 | 502.7 | 291.1 | 449.8
1226 | 987 | 304.6 | 469.8 | 511.8 | 291.7 | 452.7
1227 | 988 | 305.1 | 474.1 | 522.6 | 292.4 | 455
1228 | 989 | 305.6 | 475.1 | 522.8 | 292.8 | 455
1229 | 990 | 306.1 | 475.3 | 521.1 | 293.3 | 454.3
1230 | 991 | 306.6 | 475.8 | 522.8 | 293.7 | 455.6
1231 | 992 | 307 | 473.5 | 519.1 | 294.2 | 454
1232 | 993 | 307.5 | 471.6 | 516.8 | 294.6 | 453.5
1233 | 994 | 308 | 470.4 | 513.4 | 295 | 453.3
1234 | 995 | 308.5 | 470.4 | 514.7 | 295.4 | 453.9
1235 | 996 | 309 | 469.6 | 517.9 | 296 | 453.8
1236 | 997 | 309.4 | 470.4 | 519.8 | 296.4 | 455.4
1237 | 998 | 309.9 | 469.2 | 514 | 296.8 | 454.1
1238 | 999 | 310.4 | 467.1 | 509.1 | 297.2 | 452.6
1239 | 1000 | 310.9 | 467.1 | 509.7 | 297.7 | 452.8
1240 | 1001 | 311.3 | 467.1 | 508.1 | 297.9 | 453.6
1241 | 1002 | 311.8 | 466.4 | 508.4 | 298.3 | 454.2
1242 | 1003 | 312.2 | 466.5 | 507.5 | 298.6 | 454.8
1243 | 1004 | 312.7 | 468.4 | 509 | 299 | 455.6
1244 | 1005 | 313.1 | 468.3 | 507.1 | 299.3 | 455.1
1245 | 1006 | 313.6 | 466.6 | 507.4 | 299.9 | 454.8
1246 | 1007 | 314 | 467.1 | 508.9 | 300.4 | 455.4
1247 | 1008 | 314.5 | 468.2 | 515.1 | 301 | 457.1
1248 | 1009 | 315 | 468.3 | 521.1 | 301.6 | 458.2
1249 | 1010 | 315.4 | 471.8 | 537.2 | 302.4 | 461.8
1250 | 1011 | 315.9 | 474.2 | 545.2 | 303.2 | 463.6
1251 | 1012 | 316.4 | 473.8 | 544.7 | 303.6 | 462.9
1252 | 1013 | 316.9 | 474.6 | 545.9 | 304.2 | 463.5
1253 | 1014 | 317.4 | 475.6 | 543.5 | 304.7 | 463.3
1254 | 1015 | 317.9 | 476.7 | 549 | 305.3 | 463.7
1255 | 1016 | 318.4 | 477.5 | 548.4 | 305.8 | 464.1
1256 | 1017 | 318.9 | 477 | 543.1 | 306.4 | 463.4
1257 | 1018 | 319.3 | 476.5 | 543.3 | 306.8 | 463.5
1258 | 1019 | 319.8 | 478.1 | 545.8 | 307.3 | 465
1259 | 1020 | 320.3 | 477.5 | 538.3 | 307.6 | 465.5
1260 | 1021 | 320.8 | 476.3 | 534.3 | 308 | 464.2
1261 | 1022 | 321.3 | 475.2 | 532.4 | 308.5 | 464.1
1262 | 1023 | 321.8 | 474.5 | 527.7 | 308.8 | 463.8
1263 | 1024 | 322.3 | 472.2 | 524.7 | 308.9 | 462.3
1264 | 1025 | 322.8 | 471.1 | 525.9 | 309 | 464.2
1265 | 1026 | 323.3 | 471.3 | 527.6 | 309.2 | 467
1266 | 1027 | 323.8 | 470.9 | 521.6 | 309.6 | 466.7
1267 | 1028 | 324.3 | 471 | 530.1 | 310.1 | 467.7
1268 | 1029 | 324.7 | 474 | 540.5 | 310.9 | 471.1
1269 | 1030 | 325.2 | 474.6 | 543.9 | 311.5 | 471.9
1270 | 1031 | 325.8 | 476.4 | 548.2 | 312.2 | 473.1
1271 | 1032 | 326.2 | 479.4 | 550.1 | 312.8 | 472.8
1272 | 1033 | 326.7 | 481.1 | 547 | 313.3 | 471.8
1273 | 1034 | 327.2 | 482.2 | 550.6 | 314 | 473.2
1274 | 1035 | 327.7 | 484.5 | 546.2 | 314.3 | 474.1
1275 | 1036 | 328.2 | 484.8 | 540.6 | 314.7 | 473.5
1276 | 1037 | 328.7 | 484.3 | 535.2 | 315 | 472.6
1277 | 1038 | 329.2 | 486.5 | 534.8 | 315.4 | 474.3
1278 | 1039 | 329.7 | 487.5 | 536.8 | 315.9 | 476.4
1279 | 1040 | 330.2 | 488.2 | 543.3 | 316.5 | 477.2
1280 | 1041 | 330.7 | 489.1 | 540.7 | 316.9 | 477.7
1281 | 1042 | 331.2 | 489.9 | 540.4 | 317.5 | 478.2
1282 | 1043 | 331.7 | 488.9 | 536.3 | 317.9 | 477.3
1283 | 1044 | 332.2 | 487.4 | 539.8 | 318.6 | 475.9
1284 | 1045 | 332.6 | 490.2 | 555.1 | 319.7 | 478.1
1285 | 1046 | 333.1 | 493.6 | 572.8 | 320.5 | 483.5
1286 | 1047 | 333.6 | 496.7 | 587.7 | 321.4 | 487.1
1287 | 1048 | 334.1 | 499.6 | 590.7 | 322.3 | 487.9
1288 | 1049 | 334.6 | 501.4 | 599 | 323.3 | 489.2
1289 | 1050 | 335.1 | 500.4 | 599.6 | 323.9 | 488.3
1290 | 1051 | 335.6 | 505.1 | 609 | 324.9 | 490
1291 | 1052 | 336.1 | 508.8 | 618.4 | 325.8 | 493.5
1292 | 1053 | 336.7 | 512.4 | 623.5 | 326.9 | 494.6
1293 | 1054 | 337.3 | 511.8 | 618.5 | 327.5 | 494.8
1294 | 1055 | 337.9 | 515.2 | 622.9 | 328.2 | 496.7
1295 | 1056 | 338.4 | 516.6 | 614.6 | 329 | 496.5
1296 | 1057 | 339.1 | 515.8 | 604.7 | 329.7 | 494.6
1297 | 1058 | 339.6 | 514.7 | 593.3 | 330.4 | 493.5
1298 | 1059 | 340.2 | 510.7 | 578.4 | 330.9 | 490.9
1299 | 1060 | 340.8 | 509 | 575.7 | 331.5 | 491.4
1300 | 1061 | 341.3 | 511.7 | 575 | 332.2 | 493.7
1301 | 1062 | 341.8 | 514.7 | 568.3 | 332.7 | 494.9
1302 | 1063 | 342.4 | 518.1 | 585 | 333.6 | 497.4
1303 | 1064 | 342.9 | 520.6 | 585.4 | 334.4 | 500.6
1304 | 1065 | 343.5 | 520.3 | 587.8 | 335.3 | 500.2
1305 | 1066 | 344 | 519.7 | 581.4 | 336.1 | 499.1
1306 | 1067 | 344.5 | 517.7 | 575.9 | 336.8 | 498.3
1307 | 1068 | 345 | 515.9 | 577.2 | 337.6 | 499
1308 | 1069 | 345.6 | 515.5 | 584.8 | 338.9 | 501
1309 | 1070 | 346.2 | 516.7 | 586.2 | 339.9 | 502.6
1310 | 1071 | 346.7 | 514.4 | 582 | 340.8 | 501.1
1311 | 1072 | 347.3 | 515.2 | 593.2 | 341.9 | 504
1312 | 1073 | 348 | 518.8 | 605.6 | 343.3 | 507.8
1313 | 1074 | 348.6 | 522.5 | 616.7 | 345 | 512.5
1314 | 1075 | 349.2 | 524.3 | 629.3 | 346.6 | 514.9
1315 | 1076 | 349.9 | 527.1 | 639.6 | 348.4 | 517.7
1316 | 1077 | 350.5 | 532.9 | 641.1 | 349.6 | 521.3
1317 | 1078 | 351.2 | 536.6 | 635.7 | 350.6 | 524.3
1318 | 1079 | 351.9 | 537.3 | 633 | 351.9 | 522.8
1319 | 1080 | 352.6 | 539.6 | 634.5 | 353.4 | 524
1320 | 1081 | 353.2 | 543.8 | 636.1 | 354.7 | 527.1
1321 | 1082 | 353.9 | 543.4 | 627.4 | 355.5 | 527.2
1322 | 1083 | 354.6 | 540.1 | 614.1 | 356.1 | 523.5
1323 | 1084 | 355.3 | 536.2 | 601.6 | 356.6 | 521.5
1324 | 1085 | 355.9 | 533.4 | 595.4 | 357.2 | 520.1
1325 | 1086 | 356.6 | 534.2 | 594.8 | 358.1 | 520.8
1326 | 1087 | 357.2 | 534.8 | 590.1 | 358.9 | 520.5
1327 | 1088 | 357.9 | 534.7 | 586.1 | 359.4 | 522.1
1328 | 1089 | 358.5 | 535.3 | 591.4 | 360.3 | 525.7
1329 | 1090 | 359.2 | 537.7 | 604.5 | 361.7 | 529.3
1330 | 1091 | 359.9 | 537.7 | 611.4 | 362.9 | 530.2
1331 | 1092 | 360.5 | 538.1 | 609.3 | 364.2 | 530
1332 | 1093 | 361.2 | 537.2 | 600.4 | 365 | 526.8
1333 | 1094 | 361.8 | 533.9 | 594.1 | 365.9 | 524.2
1334 | 1095 | 362.5 | 534.3 | 604.6 | 367.2 | 527.3
1335 | 1096 | 363.1 | 532.7 | 601.6 | 368.3 | 527.2
1336 | 1097 | 363.8 | 532.5 | 600.4 | 369.1 | 527.8
1337 | 1098 | 364.5 | 531.6 | 592.6 | 369.6 | 525.6
1338 | 1099 | 365.1 | 531.2 | 596.2 | 370.2 | 526.6
1339 | 1100 | 365.8 | 535 | 598.2 | 371.1 | 532.3
1340 | 1101 | 366.5 | 538.7 | 600.5 | 371.8 | 535.3
1341 | 1102 | 367.1 | 539.2 | 600.7 | 372.7 | 535.8
1342 | 1103 | 367.7 | 538.3 | 595.2 | 373.4 | 533.7
1343 | 1104 | 368.4 | 538.6 | 598.6 | 374.4 | 533.4
1344 | 1105 | 369 | 539.5 | 597.4 | 375.3 | 533.2
1345 | 1106 | 369.7 | 536 | 594.4 | 375.7 | 531
1346 | 1107 | 370.3 | 533.2 | 588.3 | 376 | 529.3
1347 | 1108 | 370.9 | 529.6 | 584.5 | 376.6 | 530.6
1348 | 1109 | 371.6 | 529.2 | 589.3 | 377.6 | 532.7
1349 | 1110 | 372.2 | 527.5 | 589.4 | 378.4 | 531.8
1350 | 1111 | 372.8 | 527 | 576.5 | 378.6 | 530.6
1351 | 1112 | 373.4 | 527.9 | 568.1 | 379 | 531.2
1352 | 1113 | 374 | 527.8 | 569.2 | 379.7 | 532.8
1353 | 1114 | 374.6 | 531.3 | 571.5 | 380.6 | 535.3
1354 | 1115 | 375.3 | 531.8 | 578.8 | 381.3 | 536.3
1355 | 1116 | 376 | 531.4 | 583.9 | 382.2 | 536.1
1356 | 1117 | 376.6 | 529.7 | 573.7 | 382.7 | 531.9
1357 | 1118 | 377.2 | 528.1 | 569.3 | 383.4 | 528.9
1358 | 1119 | 377.9 | 527.8 | 572.9 | 384.3 | 529.3
1359 | 1120 | 378.5 | 529.2 | 574.6 | 385.3 | 529.8
1360 | 1121 | 379.1 | 529.1 | 571.8 | 385.9 | 529.7
1361 | 1122 | 379.8 | 534.1 | 585.8 | 387 | 535.6
1362 | 1123 | 380.4 | 537.6 | 593.7 | 388.2 | 539.5
1363 | 1124 | 381 | 539.5 | 590.6 | 388.8 | 536.8
1364 | 1125 | 381.6 | 538.9 | 585.2 | 389.3 | 534.8
1365 | 1126 | 382.3 | 542.6 | 585.7 | 390 | 533.4
1366 | 1127 | 382.9 | 543.5 | 596.6 | 390.8 | 533.5
1367 | 1128 | 383.6 | 548.4 | 606.9 | 391.6 | 538
1368 | 1129 | 384.2 | 549.6 | 609.4 | 392.5 | 540.5
1369 | 1130 | 384.8 | 550 | 603.3 | 393.2 | 537
1370 | 1131 | 385.4 | 548.6 | 603.7 | 393.9 | 537
1371 | 1132 | 386 | 548.5 | 607.2 | 394.9 | 540.3
1372 | 1133 | 386.6 | 549.4 | 605.2 | 395.7 | 540.3
1373 | 1134 | 387.2 | 550.9 | 615.2 | 396.7 | 539.5
1374 | 1135 | 387.8 | 554.3 | 626.4 | 398 | 544.1
1375 | 1136 | 388.4 | 554.2 | 628.1 | 399.1 | 542.7
1376 | 1137 | 389 | 554.7 | 627.7 | 399.7 | 542.5
1377 | 1138 | 389.6 | 555.5 | 623.9 | 400.6 | 541.4
1378 | 1139 | 390.3 | 555.2 | 620.1 | 401.3 | 539.4
1379 | 1140 | 390.9 | 560.5 | 626.8 | 402.6 | 542
1380 | 1141 | 391.5 | 562.8 | 630.1 | 404.1 | 543.6
1381 | 1142 | 392.2 | 560.5 | 628.5 | 405.2 | 541.9
1382 | 1143 | 392.8 | 561 | 623.7 | 406 | 542.2
1383 | 1144 | 393.5 | 563.3 | 617.2 | 406.8 | 541.3
1384 | 1145 | 394.1 | 565.3 | 615 | 407.8 | 542
1385 | 1146 | 394.8 | 566.2 | 614.8 | 408.8 | 542.4
1386 | 1147 | 395.4 | 566.6 | 611.8 | 409.5 | 542.4
1387 | 1148 | 396.1 | 568.1 | 615.6 | 410.4 | 543.9
1388 | 1149 | 396.8 | 571.5 | 609.2 | 411.2 | 542.9
1389 | 1150 | 397.5 | 576.6 | 610.9 | 412.2 | 542.7
1390 | 1151 | 398.3 | 577.5 | 613.6 | 413 | 545
1391 | 1152 | 399.2 | 581.5 | 620.3 | 414.1 | 547.8
1392 | 1153 | 400 | 581.2 | 623.5 | 415.1 | 547.5
1393 | 1154 | 400.6 | 579.4 | 621.3 | 415.9 | 547.1
1394 | 1155 | 401.2 | 576.5 | 622.1 | 416.9 | 547.4
1395 | 1156 | 401.8 | 578.2 | 621 | 417.6 | 548.8
1396 | 1157 | 402.5 | 582.8 | 612.8 | 418.3 | 549.5
1397 | 1158 | 403.1 | 582.4 | 613.2 | 419 | 550.8
1398 | 1159 | 403.8 | 581.2 | 613.2 | 420.1 | 551.2
1399 | 1160 | 404.5 | 584 | 621.1 | 421.5 | 554.5
1400 | 1161 | 405.1 | 585.9 | 621.1 | 422.3 | 553.1
1401 | 1162 | 405.8 | 590.6 | 626.3 | 423 | 552.8
1402 | 1163 | 406.4 | 587.1 | 619.1 | 423.7 | 550.4
1403 | 1164 | 407 | 582.8 | 618.5 | 424.6 | 547.7
1404 | 1165 | 407.6 | 582.5 | 617.1 | 425.5 | 548.1
1405 | 1166 | 408.3 | 584.5 | 610.5 | 426.1 | 549.2
1406 | 1167 | 409.1 | 593.4 | 610.1 | 426.7 | 549.9
1407 | 1168 | 409.8 | 595.4 | 621 | 427.7 | 554.5
1408 | 1169 | 410.5 | 594.7 | 618.3 | 428.6 | 555.2
1409 | 1170 | 411.2 | 595.2 | 622.9 | 429.9 | 554
1410 | 1171 | 411.7 | 592.6 | 617.1 | 430.5 | 553.1
1411 | 1172 | 412.3 | 588.6 | 606.2 | 430.9 | 550.2
1412.1 | 1173.1 | 412.9 | 585.2 | 600.5 | 431.4 | 550.5
1413.1 | 1174.1 | 413.5 | 583.7 | 606.2 | 432.3 | 551.3
1414.1 | 1175.1 | 414.2 | 584.9 | 602.3 | 432.8 | 551.8
1415.1 | 1176.1 | 414.8 | 583.7 | 604.7 | 433.6 | 551.7
1416.1 | 1177.1 | 415.4 | 586.9 | 608.1 | 434.4 | 553.5
1417.1 | 1178.1 | 416.1 | 588.1 | 605.4 | 435 | 553.7
1418.1 | 1179.1 | 416.8 | 590.8 | 616.5 | 436.4 | 557.7
1419.1 | 1180.1 | 417.4 | 590.2 | 618.8 | 437.8 | 558.9
1420.1 | 1181.1 | 418.1 | 588.2 | 620.8 | 439 | 558.5
1421.1 | 1182.1 | 418.9 | 587.9 | 625.8 | 440.2 | 559.6
1422.1 | 1183.1 | 419.7 | 588 | 625.8 | 441.1 | 561
1423.1 | 1184.1 | 420.5 | 585.7 | 619.2 | 442 | 559.4
1424.1 | 1185.1 | 421.2 | 583.4 | 617.7 | 442.8 | 557.7
1425.1 | 1186.1 | 421.9 | 580.6 | 625.4 | 444.3 | 558.7
1426.1 | 1187.1 | 422.7 | 582.2 | 633.2 | 445.9 | 563.6
1427.1 | 1188.1 | 423.5 | 582 | 633.3 | 446.9 | 563
1428.1 | 1189.1 | 424.4 | 582 | 629.1 | 447.5 | 561.6
1429.1 | 1190.1 | 425.3 | 581.1 | 623.4 | 448 | 560
1430.1 | 1191.1 | 426.2 | 578.3 | 616.3 | 448.3 | 558.1
1431.1 | 1192.1 | 427.1 | 575.2 | 608 | 449.1 | 556.4
1432.1 | 1193.1 | 428 | 574 | 600.1 | 449.2 | 554.4
1433.1 | 1194.1 | 429 | 573.7 | 589.8 | 449.3 | 554.9
1434.1 | 1195.1 | 430 | 576.4 | 590.9 | 450.4 | 559.1
1435.1 | 1196.1 | 431 | 575.6 | 587.7 | 450.8 | 557.7
1436.1 | 1197.1 | 432 | 576.9 | 589.9 | 451.6 | 557.6
1437.1 | 1198.1 | 432.8 | 578.2 | 591 | 452.2 | 557.5
1438.1 | 1199.1 | 433.5 | 579 | 596.7 | 452.9 | 557.4
1439.1 | 1200.1 | 434.2 | 578.2 | 592.6 | 453.3 | 557.5
1440.1 | 1201.1 | 434.7 | 576.5 | 587.6 | 453.5 | 556.4
1441.1 | 1202.1 | 435.5 | 580.2 | 589.4 | 454 | 560.1
1442.1 | 1203.1 | 436.3 | 581.7 | 586.1 | 454.5 | 561.2
1443.1 | 1204.1 | 436.9 | 581.2 | 591 | 455.5 | 560.8
1444.1 | 1205.1 | 437.5 | 579.7 | 600.4 | 456.7 | 561.3
1445.1 | 1206.1 | 438.3 | 583 | 605.4 | 457 | 563.2
1446.1 | 1207.1 | 438.9 | 583 | 607.7 | 457.7 | 562.7
1447.1 | 1208.1 | 439.7 | 584.3 | 613.9 | 458.9 | 563.5
1448.1 | 1209.1 | 440.6 | 585.1 | 618.1 | 460.7 | 565.4
1449.1 | 1210.1 | 441.1 | 584.4 | 622.2 | 462.1 | 563.2
1450.1 | 1211.1 | 441.7 | 582.7 | 626.4 | 463.2 | 561.1
1451.1 | 1212.1 | 442.7 | 587.2 | 626.2 | 464.3 | 561.4
1452.1 | 1213.1 | 443.4 | 583.9 | 628.6 | 464.2 | 563.1
1453.1 | 1214.1 | 443.9 | 581 | 620.6 | 463.9 | 560.4
1454.1 | 1215.1 | 444.4 | 585.2 | 620.2 | 463.7 | 562.7
1455.1 | 1216.1 | 444.9 | 583.9 | 617.9 | 463.7 | 561.5
1456.1 | 1217.1 | 445.6 | 588.2 | 624.8 | 464.6 | 565
1457.1 | 1218.1 | 446.3 | 593.5 | 634.3 | 465.9 | 568.2
1458.1 | 1219.1 | 447 | 593.8 | 630.1 | 466.3 | 568.2
1459.1 | 1220.1 | 447.5 | 590.8 | 626.7 | 466.7 | 565.1
1460.1 | 1221.1 | 448.1 | 587.9 | 621.5 | 467.2 | 563.2
1461.1 | 1222.1 | 448.6 | 585.8 | 617.6 | 467.4 | 562.7
1462.1 | 1223.1 | 449.1 | 585.8 | 618.4 | 467.4 | 563.4
1463.1 | 1224.1 | 449.7 | 584.7 | 615.4 | 467.2 | 562.6
1464.1 | 1225.1 | 450.6 | 589.5 | 619.7 | 467.8 | 566
1465.1 | 1226.1 | 451.1 | 588.7 | 616.6 | 467.8 | 565.9
1466.1 | 1227.1 | 451.5 | 588.1 | 623.6 | 468.1 | 566.3
1467.1 | 1228.1 | 452 | 588.2 | 633.8 | 469.1 | 568.1
1468.1 | 1229.1 | 452.3 | 587.7 | 631.4 | 468.5 | 567.2
1469.1 | 1230.1 | 453 | 588.8 | 638.8 | 468.6 | 567.5
1470.1 | 1231.1 | 453.6 | 591.1 | 637.9 | 468.8 | 569.6
1471.1 | 1232.1 | 454.1 | 588.8 | 637.4 | 469 | 568.1
1472.1 | 1233.1 | 454.8 | 588.9 | 639 | 469.7 | 568.9
1473.1 | 1234.1 | 455.4 | 586.7 | 633.8 | 470 | 567.9
1474.1 | 1235.1 | 456.1 | 588.3 | 638.9 | 470.4 | 569.8
1475.1 | 1236.1 | 456.7 | 587.1 | 639.4 | 470.6 | 571.2
1476.1 | 1237.1 | 457.1 | 586.1 | 642.8 | 471 | 572.4
1477.1 | 1238.1 | 457.5 | 585.2 | 647.9 | 471.1 | 572.3
1478.1 | 1239.1 | 458.2 | 587 | 659.4 | 471.5 | 575.9
1479.1 | 1240.1 | 458.7 | 585.6 | 656.6 | 471.4 | 575.1
1480.1 | 1241.1 | 459.3 | 582.9 | 649.5 | 471.3 | 572.7
1481.1 | 1242.1 | 459.9 | 582.9 | 644 | 471.6 | 571.9
1482.1 | 1243.1 | 460.6 | 587.1 | 648.7 | 471.8 | 573.6
1483.1 | 1244.1 | 461.1 | 588.2 | 654.6 | 471.8 | 574.1
1484.1 | 1245.1 | 461.8 | 587.5 | 658.3 | 471.9 | 574.4
1485.1 | 1246.1 | 462.4 | 587 | 662.9 | 471.8 | 577.9
1486.1 | 1247.1 | 462.9 | 585.8 | 667.5 | 472.1 | 579.4
1487.1 | 1248.1 | 463.5 | 585.5 | 667.7 | 472.5 | 578.4
1488.1 | 1249.1 | 464.1 | 587.5 | 675.5 | 472.8 | 581
1489.1 | 1250.1 | 464.5 | 588 | 676.9 | 472.5 | 585
1490.1 | 1251.1 | 465.2 | 590.1 | 672.1 | 473.1 | 583.5
1491.1 | 1252.1 | 465.9 | 591.8 | 674.5 | 473.8 | 584.7
1492.1 | 1253.1 | 466.4 | 593.8 | 678.4 | 473.8 | 583.8
1493.1 | 1254.1 | 467.1 | 599.8 | 673.4 | 474.1 | 582.7
1494.1 | 1255.1 | 467.8 | 601.1 | 670.8 | 474.7 | 584
1495.1 | 1256.1 | 468.2 | 599.4 | 661.3 | 475.1 | 582.5
1496.1 | 1257.1 | 468.9 | 600 | 656.6 | 475.6 | 583
1497.1 | 1258.1 | 469.2 | 599.9 | 648.2 | 475.7 | 582.6
1498.1 | 1259.1 | 469.6 | 597.8 | 636 | 476.2 | 578.6
1499.1 | 1260.1 | 470.1 | 597.6 | 634.2 | 476.6 | 579.3
1500.1 | 1261.1 | 470.8 | 607.3 | 644 | 477.4 | 584
1501.1 | 1262.1 | 471.2 | 606.4 | 639.8 | 478.3 | 581.7
1502.1 | 1263.1 | 471.8 | 606.2 | 637.7 | 479.1 | 580.2
1503.1 | 1264.1 | 472.2 | 604.7 | 642.1 | 479.5 | 581.5
1504.1 | 1265.1 | 472.7 | 604 | 654.6 | 480.2 | 582.5
1505.1 | 1266.1 | 473.1 | 600.6 | 652.6 | 480.6 | 581.5
1506.1 | 1267.1 | 473.2 | 598.1 | 642.9 | 480.5 | 579.3
1507.1 | 1268.1 | 473.3 | 595.4 | 630.2 | 480.3 | 576.6
1508.1 | 1269.1 | 473.9 | 599.8 | 629 | 480.7 | 575.9
1509.1 | 1270.1 | 474.7 | 604.6 | 631.9 | 481.7 | 577.3
1510.1 | 1271.1 | 475.1 | 602 | 624.3 | 482.1 | 577.8
1511.1 | 1272.1 | 475.4 | 601.8 | 624.8 | 482.3 | 577.6
1512.1 | 1273.1 | 476 | 603.7 | 623.1 | 482.5 | 577.8
1513.1 | 1274.1 | 476.5 | 604.1 | 633.5 | 483.1 | 580.4
1514.1 | 1275.1 | 477.1 | 607 | 631.7 | 483.9 | 580.8
1515.1 | 1276.1 | 477.8 | 609.5 | 632.6 | 484.6 | 580.1
1516.1 | 1277.1 | 478.3 | 609.8 | 637.9 | 485.4 | 580.1
1517.1 | 1278.1 | 479 | 610.9 | 644.2 | 485.9 | 580.7
1518.1 | 1279.1 | 479.8 | 614.7 | 654.2 | 486.5 | 585
1519.1 | 1280.1 | 480.1 | 612.9 | 658.9 | 486.8 | 587
1520.1 | 1281.1 | 480.4 | 612 | 658 | 486.8 | 587.5
1521.1 | 1282.1 | 481.2 | 611 | 671.5 | 487.8 | 588.4
1522.1 | 1283.1 | 481.9 | 613.2 | 684.2 | 488.3 | 591.4
1523.1 | 1284.1 | 482.1 | 610.8 | 681 | 488 | 589.3
1524.1 | 1285.1 | 482.6 | 611.5 | 680.8 | 488.4 | 588.9
1525.1 | 1286.1 | 483 | 613.5 | 685 | 488.5 | 588.2
1526.1 | 1287.1 | 483.7 | 613.6 | 685.9 | 489.2 | 588.6
1527.1 | 1288.1 | 484.3 | 613.1 | 676 | 489.3 | 588.5
1528.1 | 1289.1 | 485 | 615.3 | 679.4 | 489.2 | 590.4
1529.1 | 1290.1 | 485.7 | 619.1 | 679.9 | 489.2 | 591.8
1530.1 | 1291.1 | 485.9 | 621 | 678.3 | 488.7 | 591.6
1531.1 | 1292.1 | 486.3 | 620.2 | 679.7 | 489 | 592.3
1532.1 | 1293.1 | 487 | 618.7 | 683.8 | 489.7 | 593.5
1533.1 | 1294.1 | 487.7 | 616.5 | 680.5 | 490.1 | 594.5
1534.1 | 1295.1 | 488.3 | 617.4 | 676.3 | 490.4 | 593.6
1535.1 | 1296.1 | 488.8 | 623.6 | 676.3 | 490.2 | 592.5
1536.1 | 1297.1 | 489.6 | 625.9 | 680.1 | 490.9 | 595.2
1537.1 | 1298.1 | 490 | 626.1 | 676.4 | 490.7 | 594.6
1538.1 | 1299.1 | 490.3 | 625.7 | 682.3 | 490.5 | 596.3
1539.1 | 1300.1 | 490.9 | 624.3 | 686.5 | 491 | 599.6
1540.1 | 1301.1 | 491 | 623.3 | 684.7 | 490.6 | 601.1
1541.1 | 1302.1 | 491.2 | 622.2 | 686.3 | 490.4 | 599.8
1542.1 | 1303.1 | 491.8 | 621.5 | 682.4 | 490.7 | 599.2
1543.1 | 1304.1 | 492.5 | 620.3 | 675.2 | 491.2 | 598
1544.1 | 1305.1 | 493.1 | 623.3 | 683.9 | 491.5 | 599.4
1545.1 | 1306.1 | 493.4 | 622.5 | 680.2 | 491.5 | 599.6
1546.1 | 1307.1 | 493.8 | 619.5 | 685.9 | 491.3 | 598.1
1547.1 | 1308.1 | 494 | 617.3 | 673 | 491.1 | 596.1
1548.1 | 1309.1 | 494.5 | 621.7 | 672.8 | 490.8 | 597.9
1549.1 | 1310.1 | 495.3 | 628.3 | 682.5 | 490.9 | 601.5
1550.1 | 1311.1 | 496 | 627.1 | 686.5 | 491 | 602.1
1551.1 | 1312.1 | 496.8 | 627.9 | 685.5 | 491.9 | 600.7
1552.1 | 1313.1 | 497.6 | 629.3 | 691.3 | 492.7 | 600.9
1553.1 | 1314.1 | 497.7 | 627.6 | 684.7 | 492.2 | 600.7
1554.1 | 1315.1 | 498.2 | 625.9 | 675.5 | 492.2 | 598.5
1555.1 | 1316.1 | 498.6 | 629.3 | 671.4 | 492 | 597.8
1556.1 | 1317.1 | 499.5 | 629.1 | 673.2 | 492 | 600.8
1557.1 | 1318.1 | 500.1 | 635.4 | 675.1 | 492.1 | 601.6
1558.1 | 1319.1 | 501 | 636.7 | 673.5 | 492.9 | 600.8
1559.1 | 1320.1 | 501.5 | 635.2 | 677.7 | 493.1 | 601.7
1560.1 | 1321.1 | 502.2 | 632.3 | 673.4 | 493.1 | 600.2
1561.1 | 1322.1 | 502.7 | 632.6 | 668.8 | 493.4 | 600
1562.1 | 1323.1 | 503.1 | 639.2 | 669.1 | 493.7 | 599.1
1563.1 | 1324.1 | 503.8 | 641.8 | 672.3 | 494.1 | 599.5
1564.1 | 1325.1 | 505.4 | 645.8 | 677.4 | 495.2 | 600.1
1565.1 | 1326.1 | 505.9 | 645.1 | 675.4 | 495.6 | 602.7
1566.1 | 1327.1 | 506.1 | 640.7 | 669.2 | 495.8 | 600.3
1567.1 | 1328.1 | 506.8 | 640.1 | 664.8 | 496.2 | 598.9
1568.1 | 1329.1 | 507.8 | 641.3 | 664 | 496.9 | 600.4
1569.1 | 1330.1 | 508.8 | 643.9 | 666.4 | 497.7 | 604.3
1570.1 | 1331.1 | 510.2 | 645.2 | 662.9 | 499.2 | 604.7
1571.1 | 1332.1 | 511.6 | 653.3 | 665.7 | 500.7 | 603.6
1572.1 | 1333.1 | 512.3 | 654.1 | 674.8 | 501.3 | 607.2
1573.1 | 1334.1 | 512.7 | 652.4 | 679.1 | 501.7 | 607
1574.1 | 1335.1 | 513.6 | 652.4 | 684.6 | 502.2 | 608
1575.1 | 1336.1 | 514.6 | 654.2 | 691.1 | 503.2 | 611.2
1576.1 | 1337.1 | 515.6 | 654.1 | 697.3 | 503.9 | 612.7
1577.1 | 1338.1 | 516.4 | 654.2 | 705.4 | 504.9 | 615.2
1578.1 | 1339.1 | 517.5 | 654.1 | 713.2 | 505.5 | 615.6
1579.1 | 1340.1 | 518.8 | 653.3 | 715.4 | 505.8 | 618.3
1580.1 | 1341.1 | 519.2 | 651 | 715.9 | 505.5 | 619.7
1581.1 | 1342.1 | 519.6 | 649 | 709.9 | 505.4 | 616.6
1582.1 | 1343.1 | 520.6 | 648.2 | 714.9 | 505.6 | 616
1583.1 | 1344.1 | 521.3 | 648.9 | 718 | 505.9 | 618.6
1584.1 | 1345.1 | 521.7 | 647.8 | 724 | 505.7 | 620.4
1585.1 | 1346.1 | 522.3 | 644 | 716.5 | 506 | 619
1586.1 | 1347.1 | 523.2 | 642.9 | 718.8 | 506.1 | 617
1587.1 | 1348.1 | 524 | 642 | 715.5 | 506.5 | 617.4
1588.1 | 1349.1 | 525 | 645.3 | 713.6 | 507.2 | 617.2
1589.1 | 1350.1 | 526 | 645.3 | 718.4 | 507.7 | 618.4
1590.1 | 1351.1 | 526.6 | 641.9 | 714 | 508.1 | 616.3
1591.1 | 1352.1 | 527.4 | 639.6 | 710.6 | 508.3 | 615.3
1592.1 | 1353.1 | 528.4 | 641.8 | 713.7 | 508.7 | 618.3
1593.1 | 1354.1 | 529.3 | 639.8 | 712 | 509.1 | 619
1594.1 | 1355.1 | 530.4 | 641.1 | 718.2 | 509.3 | 620.1
1595.1 | 1356.1 | 531.6 | 642.5 | 722.1 | 510 | 622.7
1596.1 | 1357.1 | 532.6 | 643.1 | 724.8 | 510.6 | 625.3
1597.1 | 1358.1 | 532.9 | 642.5 | 724 | 510.6 | 625.6
1598.1 | 1359.1 | 533.9 | 642.1 | 727.4 | 510.7 | 627.5
1599.1 | 1360.1 | 534.8 | 641 | 732 | 510.7 | 629.4
1600.1 | 1361.1 | 535.8 | 639.3 | 733 | 511.5 | 630
1601.1 | 1362.1 | 536.5 | 637.4 | 729.7 | 511.8 | 627.7
1602.1 | 1363.1 | 537.3 | 637.8 | 733 | 512.1 | 626.9
1603.1 | 1364.1 | 538.3 | 637.5 | 731.4 | 512.5 | 625.1
1604.1 | 1365.1 | 539.1 | 637.5 | 733.9 | 512.6 | 625.7
1605.1 | 1366.1 | 539.9 | 637 | 730 | 512.5 | 625.7
1606.1 | 1367.1 | 540.4 | 638.3 | 729.5 | 512.4 | 625.8
1607.1 | 1368.1 | 541.3 | 639.3 | 730.3 | 512.3 | 627.3
1608.1 | 1369.1 | 542.4 | 638.2 | 730.5 | 512.7 | 625.9
1609.1 | 1370.1 | 542.9 | 637.3 | 726.8 | 513.1 | 624.8
1610.1 | 1371.1 | 543.9 | 635.8 | 727.7 | 513.5 | 622.7
1611.1 | 1372.1 | 544.5 | 635.8 | 725 | 513.7 | 625
1612.1 | 1373.1 | 545.2 | 633.8 | 719 | 513.9 | 625
1613.1 | 1374.1 | 546.7 | 632.6 | 719.5 | 514.2 | 624.7
1614.1 | 1375.1 | 547.2 | 630.4 | 712.3 | 514.2 | 624.3
1615.1 | 1376.1 | 548.3 | 632.4 | 711.4 | 514.9 | 624.6
1616.1 | 1377.1 | 549.7 | 633.4 | 711.4 | 515.6 | 626.3
1617.1 | 1378.1 | 551.2 | 635.3 | 718.7 | 516.5 | 629.2
1618.1 | 1379.1 | 552.2 | 635 | 708.8 | 517.2 | 626.4
1619.1 | 1380.1 | 553.3 | 635.7 | 707 | 517.6 | 627
1620.1 | 1381.1 | 554.4 | 635.4 | 696 | 518.7 | 626.6
1621.1 | 1382.1 | 555.2 | 634.8 | 690.6 | 520.3 | 624.9
1622.1 | 1383.1 | 555.9 | 636.3 | 691.9 | 521.1 | 626.4
1623.1 | 1384.1 | 556.5 | 637.8 | 701.5 | 521.5 | 628.7
1624.1 | 1385.1 | 557 | 634.1 | 702.8 | 521.7 | 627.8
1625.1 | 1386.1 | 557.5 | 634.7 | 694.4 | 522 | 623.8
1626.1 | 1387.1 | 557.9 | 634.7 | 685.7 | 522.6 | 621.4
1627.1 | 1388.1 | 559.2 | 635.5 | 688.1 | 523.2 | 621.7
1628.1 | 1389.1 | 560.2 | 636.6 | 680.5 | 523.9 | 620.6
1629.1 | 1390.1 | 561 | 635.9 | 678.2 | 524.3 | 619.5
1630.1 | 1391.1 | 561.2 | 634 | 679 | 524.7 | 620.3
1631.1 | 1392.1 | 561.7 | 634.2 | 682.4 | 524.7 | 621.7
1632.1 | 1393.1 | 562.1 | 633.2 | 683 | 525 | 623
1633.1 | 1394.1 | 563.2 | 632.5 | 693.6 | 525.8 | 625.1
1634.1 | 1395.1 | 563.2 | 630.4 | 696 | 525.9 | 626.5
1635.1 | 1396.1 | 562.9 | 629.2 | 695.3 | 525.8 | 625.2
1636.1 | 1397.1 | 562.9 | 628.1 | 697.8 | 525.9 | 623.7
1637.1 | 1398.1 | 563.8 | 629.2 | 697.5 | 526.2 | 621.7
1638.1 | 1399.1 | 564.4 | 629.2 | 700.3 | 526.6 | 621.8
1639.1 | 1400.1 | 565.8 | 629.4 | 702.3 | 527.6 | 621.5
1640.1 | 1401.1 | 567.2 | 628.4 | 696 | 528.8 | 619.6
1641.1 | 1402.1 | 568.3 | 627 | 683.6 | 530.4 | 617.8
1642.1 | 1403.1 | 569.4 | 626.9 | 677.1 | 531.6 | 616.9
1643.1 | 1404.1 | 569.5 | 624.8 | 672.2 | 532.2 | 615.5
1644.1 | 1405.1 | 570.5 | 623.9 | 669 | 533.2 | 613.9
1645.1 | 1406.1 | 570.5 | 626.2 | 665.5 | 533.8 | 613.8
1646.1 | 1407.1 | 571.4 | 623.8 | 658.6 | 534.6 | 612.8
1647.1 | 1408.1 | 570.8 | 621.5 | 656.4 | 534.2 | 611.7
1648.1 | 1409.1 | 570.6 | 619.9 | 653.9 | 534.3 | 611.7
1649.1 | 1410.1 | 570.6 | 619.9 | 655 | 533.6 | 612.7
1650.1 | 1411.1 | 571.9 | 623.7 | 664.6 | 533.6 | 616.2
1651.1 | 1412.1 | 573.2 | 625.4 | 666.7 | 534.3 | 616.1
1652.1 | 1413.1 | 573.2 | 624 | 667.4 | 534.6 | 615.2
1653.1 | 1414.1 | 572.1 | 623 | 664.7 | 533.9 | 615.1
1654.1 | 1415.1 | 572.4 | 622.8 | 665.6 | 533.5 | 614.6
1655.1 | 1416.1 | 573.5 | 625.8 | 669.6 | 534.2 | 617.1
1656.1 | 1417.1 | 574.7 | 624.1 | 672.5 | 534.9 | 616.4
1657.1 | 1418.1 | 575.3 | 623.7 | 674.8 | 535.5 | 616.2
1658.1 | 1419.1 | 575.5 | 623 | 671.6 | 536.4 | 615
1659.1 | 1420.1 | 575.9 | 620.8 | 672.4 | 537 | 615.1
1660.1 | 1421.1 | 576.1 | 618.5 | 673.7 | 537.2 | 614.2
1661.1 | 1422.1 | 576.6 | 619.5 | 677.1 | 537.3 | 614.9
1662.1 | 1423.1 | 578 | 619.3 | 676.8 | 538.1 | 614.9
1663.1 | 1424.1 | 578.4 | 619.9 | 676.1 | 538.5 | 613.5
1664.1 | 1425.1 | 578.9 | 619.9 | 674.8 | 538.7 | 613.8
1665.1 | 1426.1 | 579.6 | 619.4 | 678 | 539.5 | 614.3
1666.1 | 1427.1 | 580.4 | 619.5 | 677 | 540.1 | 614
1667.1 | 1428.1 | 580.1 | 619.3 | 673 | 540.5 | 613.6
1668.1 | 1429.1 | 580.5 | 619.5 | 676.9 | 541.1 | 614.6
1669.1 | 1430.1 | 580.9 | 619.1 | 674.8 | 541.4 | 614.6
1670.1 | 1431.1 | 581.8 | 619.3 | 674.7 | 542.1 | 614.1
1671.1 | 1432.1 | 583.7 | 619.1 | 677.8 | 543.4 | 613.7
1672.1 | 1433.1 | 584.9 | 621.2 | 683.4 | 544.7 | 614.7
1673.1 | 1434.1 | 585.5 | 622 | 677 | 545.8 | 614.6
1674.1 | 1435.1 | 586.3 | 623 | 670.2 | 547.1 | 612.3
1675.1 | 1436.1 | 586.8 | 624.4 | 669.9 | 548.1 | 612.5
1676.1 | 1437.1 | 587.2 | 624.2 | 669.3 | 549.1 | 613.3
1677.1 | 1438.1 | 588.2 | 624.9 | 671.4 | 550.4 | 615.7
1678.1 | 1439.1 | 589.1 | 627.7 | 677.9 | 551.7 | 620.5
1679.1 | 1440.1 | 589.4 | 628.9 | 677.7 | 552.6 | 619.4
1680.1 | 1441.1 | 589.6 | 628.8 | 676.2 | 553.3 | 616.5
1681.1 | 1442.1 | 590.9 | 627.7 | 684 | 554.2 | 617.3
1682.1 | 1443.1 | 591 | 626 | 680.6 | 555.4 | 616.1
1683.1 | 1444.1 | 590.9 | 626.3 | 682.4 | 556.1 | 616.6
1684.1 | 1445.1 | 591.5 | 626.2 | 683 | 556.9 | 616.3
1685.1 | 1446.1 | 591.6 | 627 | 683.4 | 557.2 | 616.7
1686.1 | 1447.1 | 591.2 | 626.9 | 686.6 | 557.2 | 618.4
1687.1 | 1448.1 | 591.1 | 626.1 | 690 | 557.4 | 620.1
1688.1 | 1449.1 | 590.9 | 625.1 | 691.2 | 557.4 | 619.2
1689.1 | 1450.1 | 591.1 | 624.5 | 691.1 | 557.3 | 618.3
1690.1 | 1451.1 | 592.3 | 622.5 | 688 | 557.9 | 617.9
1691.1 | 1452.1 | 593.7 | 621.1 | 692.3 | 558.4 | 618
1692.1 | 1453.1 | 594.1 | 621.6 | 690.8 | 559 | 618.1
1693.1 | 1454.1 | 594.5 | 620 | 687.9 | 559.7 | 619.2
1694.1 | 1455.1 | 595.7 | 619.2 | 686.6 | 560.6 | 618.6
1695.1 | 1456.1 | 595.7 | 619.3 | 686.9 | 560.9 | 620.2
1696.1 | 1457.1 | 595.3 | 618.5 | 688.5 | 561.2 | 619.2
1697.1 | 1458.1 | 595.7 | 621 | 695 | 561.3 | 620.2
1698.1 | 1459.1 | 596.6 | 620 | 695 | 561.8 | 621.8
1699.1 | 1460.1 | 596.9 | 620.1 | 694.9 | 562.2 | 622.5
1700.1 | 1461.1 | 597.9 | 622.4 | 695.4 | 562.9 | 623.5
1701.1 | 1462.1 | 598.3 | 623.5 | 701.3 | 563.7 | 626
1702.1 | 1463.1 | 598.3 | 621.8 | 696.2 | 564.3 | 624.9
1703.1 | 1464.1 | 598.5 | 622.5 | 693.8 | 564.7 | 623
1704.1 | 1465.1 | 599.2 | 623.4 | 694.7 | 565.2 | 623.7
1705.1 | 1466.1 | 599.4 | 624.5 | 693.1 | 565.8 | 623
1706.1 | 1467.1 | 599.1 | 628.2 | 691 | 566 | 621.2
1707.1 | 1468.1 | 599.7 | 632.1 | 681 | 566.6 | 618.8
1708.1 | 1469.1 | 601.6 | 631.2 | 682 | 567.8 | 620.9
1709.1 | 1470.1 | 602.3 | 633.3 | 687.5 | 568.6 | 623.4
1710.1 | 1471.1 | 602.4 | 633.1 | 699.2 | 569 | 627.4
1711.1 | 1472.1 | 602.9 | 632.8 | 701.6 | 569.5 | 628.4
1712.1 | 1473.1 | 604.2 | 634 | 701.6 | 570.6 | 627.7
1713.1 | 1474.1 | 605.3 | 634.4 | 697.7 | 572.1 | 627.4
1714.1 | 1475.1 | 605.4 | 632.4 | 697.2 | 572.9 | 626.9
1715.1 | 1476.1 | 605.5 | 631.5 | 698.8 | 573.6 | 626.8
1716.1 | 1477.1 | 605.4 | 630.3 | 700.7 | 573.8 | 625.2
1717.1 | 1478.1 | 605.7 | 628.7 | 699.5 | 574.2 | 626
1718.1 | 1479.1 | 606.9 | 628.5 | 697.8 | 575 | 627.1
1719.1 | 1480.1 | 606.5 | 628.2 | 697.6 | 575.3 | 627.8
1720.1 | 1481.1 | 606.1 | 630.3 | 696.3 | 575.6 | 629
1721.1 | 1482.1 | 606.1 | 630.6 | 696.4 | 576 | 629.3
1722.1 | 1483.1 | 606.6 | 630.9 | 695.8 | 576.5 | 629.3
1723.1 | 1484.1 | 606.4 | 629.8 | 689.5 | 576.2 | 627.4
1724.1 | 1485.1 | 605.7 | 627.4 | 681.9 | 575.5 | 624.3
1725.1 | 1486.1 | 605.6 | 626.2 | 679.7 | 574.9 | 623.3
1726.1 | 1487.1 | 605 | 626.9 | 671.8 | 573.8 | 625
1727.1 | 1488.1 | 605.3 | 625.4 | 665.8 | 573.3 | 622.5
1728.1 | 1489.1 | 606.1 | 623.8 | 658.4 | 573.1 | 621.2
1729.1 | 1490.1 | 606.6 | 625.7 | 654.8 | 573.2 | 618.7
1730.1 | 1491.1 | 606.9 | 625 | 652.9 | 573.8 | 618.9
1731.1 | 1492.1 | 607.1 | 624.1 | 644.6 | 574.2 | 617.1
1732.1 | 1493.1 | 607.9 | 623.4 | 641.6 | 574.7 | 616.8
1733.1 | 1494.1 | 608.8 | 623.4 | 638.9 | 575.1 | 617.8
1734.1 | 1495.1 | 609.5 | 623.3 | 650.9 | 575.7 | 618.8
1735.1 | 1496.1 | 610.2 | 624.5 | 667.4 | 576.5 | 620.5
1736.1 | 1497.1 | 611.4 | 625 | 672.2 | 577.7 | 621.7
1737.1 | 1498.1 | 611.3 | 623.5 | 676.8 | 578.3 | 622.6
1738.1 | 1499.1 | 611.2 | 623.2 | 672.9 | 578.7 | 622.5
1739.1 | 1500.1 | 611.7 | 623 | 677 | 579.4 | 624.3
1740.1 | 1501.1 | 612.4 | 621.6 | 672.5 | 580.2 | 623.5
1741.1 | 1502.1 | 612.3 | 622.7 | 679.4 | 580.5 | 625
1742.1 | 1503.1 | 611.7 | 622.8 | 677.6 | 580.7 | 625.6
1743.1 | 1504.1 | 611.9 | 621.5 | 678.7 | 581 | 626.4
1744.1 | 1505.1 | 612.5 | 619.1 | 681 | 581.7 | 624.7
1745.1 | 1506.1 | 613.2 | 620.1 | 679 | 582.4 | 622.6
1746.1 | 1507.1 | 613.7 | 621.4 | 684.6 | 583.1 | 622.4
1747.1 | 1508.1 | 613.9 | 623.5 | 682.6 | 583.9 | 622.3
1748.1 | 1509.1 | 613.9 | 625.5 | 683.7 | 584.3 | 623.2
1749.1 | 1510.1 | 613.8 | 626.1 | 686.7 | 584.5 | 624.6
1750.1 | 1511.1 | 614.2 | 628.5 | 694 | 584.7 | 626.9
1751.1 | 1512.1 | 614.8 | 629 | 697 | 585.7 | 627.5
1752.1 | 1513.1 | 615.5 | 631.2 | 699.6 | 586.7 | 628.2
1753.1 | 1514.1 | 615.5 | 629.7 | 698.8 | 587 | 627.7
1754.1 | 1515.1 | 615.5 | 631.7 | 695.6 | 586.9 | 627.4
1755.1 | 1516.1 | 615.3 | 632.8 | 698.4 | 586.6 | 628.3
1756.1 | 1517.1 | 615 | 631.7 | 691.7 | 586.1 | 627.9
1757.1 | 1518.1 | 615 | 630.8 | 693.5 | 585.7 | 629.5
1758.1 | 1519.1 | 615 | 629.3 | 691.4 | 585.3 | 630
1759.1 | 1520.1 | 615.7 | 629.3 | 696.2 | 585.4 | 630.4
1760.1 | 1521.1 | 616.2 | 628.6 | 701.9 | 585.3 | 630.5
1761.1 | 1522.1 | 616.1 | 629.1 | 708.4 | 585.3 | 631.5
1762.1 | 1523.1 | 616.1 | 629.7 | 709.5 | 585.4 | 633
1763.1 | 1524.1 | 616.4 | 629.3 | 704.2 | 585.7 | 632.5
1764.1 | 1525.1 | 616.5 | 628.7 | 709.4 | 585.7 | 635
1765.1 | 1526.1 | 616.4 | 628.7 | 709.8 | 585.6 | 637.4
1766.1 | 1527.1 | 616.7 | 629.3 | 710.4 | 585.6 | 638
1767.1 | 1528.1 | 616.5 | 630.2 | 711.8 | 585.5 | 639.8
1768.1 | 1529.1 | 617.2 | 631.2 | 711.7 | 585.9 | 640.4
1769.1 | 1530.1 | 617.7 | 631.9 | 711.3 | 586.2 | 641.9
1770.1 | 1531.1 | 618.2 | 632.2 | 712 | 586.6 | 643.1
1771.1 | 1532.1 | 618.3 | 632.6 | 717.2 | 586.9 | 645.3
1772.1 | 1533.1 | 618.6 | 633 | 718.5 | 587.4 | 645.7
1773.1 | 1534.1 | 619.1 | 633.2 | 719.2 | 588 | 645.8
1774.1 | 1535.1 | 618.9 | 631.7 | 714.9 | 588.2 | 645.5
1775.1 | 1536.1 | 618.7 | 632.1 | 718.2 | 587.9 | 646.4
1776.1 | 1537.1 | 618.8 | 632.4 | 718.6 | 587.8 | 647.4
1777.1 | 1538.1 | 618.6 | 632.8 | 716 | 587.5 | 647.7
1778.1 | 1539.1 | 618.3 | 632.6 | 713 | 587.1 | 648.5
1779.1 | 1540.1 | 618.4 | 631.7 | 710.8 | 586.9 | 648.1
1780.1 | 1541.1 | 617.9 | 629.6 | 710.9 | 586.3 | 647
1781.1 | 1542.1 | 618.4 | 632 | 719 | 586.1 | 647
1782.1 | 1543.1 | 618.7 | 632.5 | 720.9 | 586.1 | 646.8
1783.1 | 1544.1 | 619.4 | 631.4 | 719.8 | 586.3 | 647.1
1784.1 | 1545.1 | 619.9 | 631.3 | 722.4 | 586.6 | 646.7
1785.1 | 1546.1 | 620.7 | 632.5 | 723.1 | 587.5 | 646.6
1786.1 | 1547.1 | 622 | 634.7 | 716.2 | 589 | 645.5
1787.1 | 1548.1 | 622.7 | 634.5 | 715.1 | 590.1 | 645.3
1788.1 | 1549.1 | 623.6 | 635.6 | 706.9 | 591.2 | 643.1
1789.1 | 1550.1 | 624.9 | 635.8 | 702.3 | 592.5 | 642.8
1790.1 | 1551.1 | 625.3 | 634.5 | 700.1 | 593.7 | 642.3
1791.1 | 1552.1 | 624.7 | 633.7 | 704.5 | 594.2 | 642.8
1792.1 | 1553.1 | 624.4 | 632.7 | 704.3 | 594.5 | 642.8
1793.1 | 1554.1 | 624.2 | 634.2 | 708.8 | 594.7 | 644.2
1794.1 | 1555.1 | 624.1 | 634.6 | 713.7 | 594.9 | 647.4
1795.1 | 1556.1 | 623.8 | 635.5 | 717 | 594.9 | 649.2
1796.1 | 1557.1 | 623.7 | 635.1 | 717.1 | 594.7 | 648.3
1797.1 | 1558.1 | 623 | 634.1 | 706.8 | 594.1 | 645.4
1798.1 | 1559.1 | 623.3 | 634.1 | 712.5 | 593.8 | 645.7
1799.1 | 1560.1 | 623.5 | 632.9 | 712.8 | 593.8 | 646.3
1800.1 | 1561.1 | 623.3 | 630.7 | 715.9 | 593.8 | 647.4
1801.1 | 1562.1 | 623.2 | 629.1 | 714.9 | 593.8 | 647.2
1802.1 | 1563.1 | 623.4 | 629.3 | 717.1 | 594 | 647.7
1803.1 | 1564.1 | 624 | 631.4 | 716.5 | 594.4 | 648.4
1804.1 | 1565.1 | 624.2 | 632.5 | 712.7 | 594.7 | 647.5
1805.1 | 1566.1 | 624.7 | 632.9 | 716 | 594.9 | 649
1806.1 | 1567.1 | 625.7 | 633.5 | 716.8 | 595.7 | 651.7
1807.1 | 1568.1 | 626.7 | 636.5 | 720 | 596.4 | 653.1
1808.1 | 1569.1 | 627.2 | 636.5 | 724 | 597 | 654.2
1809.1 | 1570.1 | 627.4 | 634.5 | 720.9 | 597.7 | 654.1
1810.1 | 1571.1 | 627.4 | 634.1 | 720.5 | 598.1 | 652.8
1811.1 | 1572.1 | 627.7 | 635.2 | 715.9 | 598.5 | 651.1
1812.1 | 1573.1 | 628.5 | 638.2 | 717 | 599.4 | 652.3
1813.1 | 1574.1 | 629.4 | 640.9 | 718.6 | 600.5 | 655.4
1814.1 | 1575.1 | 629.2 | 639.9 | 719.1 | 601.1 | 657.6
1815.1 | 1576.1 | 628.9 | 639.5 | 720.4 | 601.1 | 656.7
1816.1 | 1577.1 | 630 | 641.2 | 727.2 | 601.7 | 659.5
1817.1 | 1578.1 | 630.8 | 640.2 | 730.5 | 602.5 | 660.4
1818.1 | 1579.1 | 630.8 | 639.2 | 732.5 | 602.9 | 661.4
1819.1 | 1580.1 | 630.2 | 639 | 731.8 | 603 | 660.4
1820.1 | 1581.1 | 629.5 | 637.2 | 726.8 | 602.7 | 658.7
1821.1 | 1582.1 | 629.7 | 638.7 | 725.9 | 602.6 | 658.5
1822.1 | 1583.1 | 630.2 | 639.6 | 721.7 | 602.9 | 657.1
1823.1 | 1584.1 | 630.8 | 640.2 | 717 | 603 | 656
1824.1 | 1585.1 | 631.3 | 640.3 | 713.2 | 603.3 | 655.6
1825.1 | 1586.1 | 631.9 | 641.4 | 719.2 | 603.7 | 658
1826.1 | 1587.1 | 633.1 | 643.2 | 719 | 604.4 | 660
1827.1 | 1588.1 | 633.4 | 641.9 | 721.6 | 605 | 660
1828.1 | 1589.1 | 632.5 | 638.6 | 717.7 | 604.7 | 658.7
1829.1 | 1590.1 | 632.1 | 635.7 | 710 | 604.4 | 656.1
1830.1 | 1591.1 | 633.3 | 637.1 | 716 | 604.7 | 656.6
1831.1 | 1592.1 | 633.7 | 639.1 | 716.5 | 605 | 658.9
1832.1 | 1593.1 | 634 | 640.1 | 705.6 | 605.6 | 657.1
1833.1 | 1594.1 | 634.6 | 647.7 | 701.2 | 606.1 | 656
1834.1 | 1595.1 | 635.2 | 649.6 | 711.2 | 606.9 | 658.3
1835.1 | 1596.1 | 635.5 | 648.8 | 711.9 | 607.6 | 661.7
1836.1 | 1597.1 | 636 | 649.7 | 709.1 | 608.2 | 663
1837.1 | 1598.1 | 635.7 | 649.3 | 701.5 | 608.4 | 661.9
1838.1 | 1599.1 | 636.1 | 649.7 | 705.5 | 608.7 | 660.3
1839.1 | 1600.1 | 636.3 | 648.3 | 706.1 | 609.1 | 659.2
1840.1 | 1601.1 | 636.5 | 647 | 707.9 | 609.4 | 657.6
1841.1 | 1602.1 | 637.5 | 647.3 | 710.7 | 609.9 | 658.3
1842.1 | 1603.1 | 638.2 | 647.1 | 713.8 | 610.6 | 659.4
1843.1 | 1604.1 | 638.8 | 646.4 | 720.4 | 611.5 | 662.4
1844.1 | 1605.1 | 638.5 | 644.7 | 721.5 | 612.2 | 663.4
1845.1 | 1606.1 | 638.5 | 643.2 | 723.9 | 612.7 | 663.7
1846.1 | 1607.1 | 638.9 | 640.8 | 725 | 613.3 | 662.7
1847.1 | 1608.1 | 638.4 | 640.5 | 728.1 | 613.2 | 665.4
1848.1 | 1609.1 | 637.9 | 639.3 | 726.3 | 613.1 | 666.3
1849.1 | 1610.1 | 637.7 | 638.8 | 728 | 612.8 | 666.5
1850.1 | 1611.1 | 637.6 | 637.7 | 726.5 | 612.6 | 664.4
1851.1 | 1612.1 | 637.9 | 637.2 | 726 | 612.7 | 664
1852.1 | 1613.1 | 637.9 | 637.4 | 725.7 | 612.8 | 662.7
1853.1 | 1614.1 | 638.6 | 637.4 | 728.1 | 613.3 | 663.9
1854.1 | 1615.1 | 638.4 | 636.2 | 722.8 | 613.3 | 663.2
1855.1 | 1616.1 | 638.5 | 636.6 | 728.9 | 613.2 | 664.9
1856.1 | 1617.1 | 638.9 | 636.9 | 723.9 | 613.3 | 666.9
1857.1 | 1618.1 | 640.1 | 638 | 725.6 | 614 | 666.8
1858.1 | 1619.1 | 641.1 | 639.5 | 731.3 | 614.8 | 666.8
1859.1 | 1620.1 | 642 | 639.4 | 738.1 | 615.7 | 667.6
1860.1 | 1621.1 | 642 | 638.4 | 733.2 | 616.5 | 667
1861.1 | 1622.1 | 641.4 | 638.1 | 724.8 | 616.6 | 663.5
1862.1 | 1623.1 | 641.3 | 637.3 | 718.8 | 616.6 | 661.7
1863.1 | 1624.1 | 641.8 | 637.5 | 717.7 | 616.5 | 661
1864.1 | 1625.1 | 642.4 | 638.7 | 720.4 | 616.8 | 663
1865.1 | 1626.1 | 643 | 639 | 717.8 | 617.3 | 662.8
1866.1 | 1627.1 | 644.1 | 640.8 | 721 | 618 | 663.5
1867.1 | 1628.1 | 646.1 | 643.1 | 717 | 619.3 | 663.5
1868.1 | 1629.1 | 646.9 | 644.6 | 717.1 | 620.4 | 664.5
1869.1 | 1630.1 | 648 | 644.7 | 718.7 | 621.8 | 665.6
1870.1 | 1631.1 | 649.1 | 646.6 | 717.9 | 623.4 | 667.6
1871.1 | 1632.1 | 649.8 | 645.3 | 713.4 | 624.9 | 666.9
1872.1 | 1633.1 | 649.8 | 643.7 | 711.2 | 626 | 663.9
1873.1 | 1634.1 | 648.5 | 643.3 | 710.6 | 626 | 663.1
1874.1 | 1635.1 | 647.8 | 642 | 713.7 | 625.6 | 664
1875.1 | 1636.1 | 648.3 | 641.7 | 720.5 | 625.5 | 666.2
1876.1 | 1637.1 | 648.9 | 641.1 | 717.5 | 625.9 | 666.9
1877.1 | 1638.1 | 649.1 | 640.5 | 719 | 626.1 | 666.5
1878.1 | 1639.1 | 649 | 640.9 | 724.2 | 626.2 | 666.8
1879.1 | 1640.1 | 649.1 | 641.3 | 726.1 | 626.3 | 668.1
1880.1 | 1641.1 | 649.7 | 644.3 | 723.8 | 626.6 | 668
1881.1 | 1642.1 | 650.4 | 645.2 | 722.3 | 627.2 | 668.7
1882.1 | 1643.1 | 650.4 | 644.2 | 719.3 | 627.3 | 665.8
1883.1 | 1644.1 | 650.7 | 644.9 | 722.6 | 627.5 | 666.7
1884.1 | 1645.1 | 650.9 | 647.1 | 720 | 627.6 | 666.9
1885.1 | 1646.1 | 652 | 648 | 714.4 | 628.1 | 665.8
1886.1 | 1647.1 | 653.1 | 647.7 | 712.1 | 628.7 | 664.5
1887.1 | 1648.1 | 653.8 | 648.6 | 720.4 | 629.3 | 664.8
1888.1 | 1649.1 | 654.6 | 649 | 719.6 | 630.1 | 666.1
1889.1 | 1650.1 | 654.9 | 648.4 | 714.3 | 630.7 | 666.9
1890.1 | 1651.1 | 654.6 | 650 | 723.2 | 630.9 | 669.3
1891.1 | 1652.1 | 654.3 | 649.3 | 723.1 | 631.1 | 670.3
1892.1 | 1653.1 | 654.5 | 649 | 717.8 | 631.5 | 667.3
1893.1 | 1654.1 | 654 | 647.2 | 714.5 | 631.3 | 665.1
1894.1 | 1655.1 | 653.6 | 644.4 | 713.4 | 631 | 664.9
1895.1 | 1656.1 | 653.8 | 643.9 | 714.9 | 630.8 | 667.4
1896.1 | 1657.1 | 654 | 644.1 | 715.9 | 630.8 | 670.6
1897.1 | 1658.1 | 654.8 | 643.1 | 714.2 | 630.9 | 669.1
1898.1 | 1659.1 | 655.1 | 642.3 | 718.9 | 630.9 | 668.9
1899.1 | 1660.1 | 655.2 | 642 | 719.5 | 630.9 | 668.6
1900.1 | 1661.1 | 655.6 | 642.1 | 722.9 | 631 | 669.5
1901.1 | 1662.1 | 655.3 | 641.3 | 722.2 | 631 | 669.7
1902.1 | 1663.1 | 654.5 | 640.2 | 720.2 | 630.4 | 669.2
1903.1 | 1664.1 | 654.4 | 641 | 719.4 | 630.2 | 668.1
1904.1 | 1665.1 | 654.8 | 640.8 | 720.8 | 630 | 668.4
1905.1 | 1666.1 | 654.6 | 640.2 | 717.3 | 629.5 | 669.2
1906.1 | 1667.1 | 654.2 | 640.8 | 718.1 | 628.9 | 670.1
1907.1 | 1668.1 | 654.2 | 640.8 | 717.3 | 628.7 | 670.5
1908.1 | 1669.1 | 654.1 | 639.6 | 719.6 | 628.3 | 671.1
1909.1 | 1670.1 | 654 | 638.5 | 719.2 | 628.1 | 670.9
1910.1 | 1671.1 | 654.4 | 639.5 | 720.2 | 628.1 | 670
1911.1 | 1672.1 | 654.8 | 639.5 | 715.2 | 628.4 | 668.6
1912.1 | 1673.1 | 655.3 | 638.3 | 719 | 628.6 | 669.1
1913.1 | 1674.1 | 655.5 | 637.9 | 722.9 | 628.8 | 670.9
1914.1 | 1675.1 | 655.2 | 636.4 | 719.8 | 628.8 | 671.2
1915.1 | 1676.1 | 655 | 635.3 | 714.2 | 628.7 | 669.7
1916.1 | 1677.1 | 655.4 | 635.3 | 718.3 | 628.7 | 671.7
1917.1 | 1678.1 | 655.2 | 636.3 | 716.2 | 628.6 | 672.7
1918.1 | 1679.1 | 655 | 635.2 | 712.7 | 628.3 | 672.7
1919.1 | 1680.1 | 655.3 | 634.9 | 713.6 | 628.1 | 671.7
1920.1 | 1681.1 | 655.8 | 635.9 | 717.9 | 628.3 | 672.8
1921.1 | 1682.1 | 655.8 | 635.9 | 720.8 | 628.3 | 674.1
1922.1 | 1683.1 | 655.6 | 634.7 | 716.4 | 628.3 | 671.7
1923.1 | 1684.1 | 655.5 | 633.9 | 714.1 | 628.1 | 670.6
1924.1 | 1685.1 | 656 | 633.9 | 715.2 | 628.1 | 670.3
1925.1 | 1686.1 | 656.8 | 636.2 | 715.6 | 628.5 | 672.3
1926.1 | 1687.1 | 658.2 | 638.4 | 712 | 629.4 | 671.9
1927.1 | 1688.1 | 659.1 | 638.6 | 707.1 | 630.2 | 670.2
1928.1 | 1689.1 | 660.3 | 639.8 | 700.8 | 631.4 | 668.3
1929.1 | 1690.1 | 661.2 | 640.1 | 704.6 | 632.6 | 668.5
1930.1 | 1691.1 | 661.9 | 639.2 | 706.9 | 633.8 | 671
1931.1 | 1692.1 | 661.8 | 639.4 | 711.6 | 634.4 | 671.9
1932.1 | 1693.1 | 660.9 | 638.3 | 714 | 634.4 | 670.2
1933.1 | 1694.1 | 660.5 | 636.4 | 705.1 | 634.5 | 666.1
1934.1 | 1695.1 | 661.5 | 636.3 | 693.4 | 635.1 | 664.1
1935.1 | 1696.1 | 662.8 | 636.3 | 693.9 | 635.9 | 665.8
1936.1 | 1697.1 | 662.6 | 635.7 | 697 | 636.3 | 667.3
1937.1 | 1698.1 | 662.2 | 634.7 | 698.5 | 636.4 | 666.5
1938.1 | 1699.1 | 662.4 | 633.2 | 696.2 | 636.6 | 666.2
1939.1 | 1700.1 | 663.9 | 633.7 | 699.8 | 637.6 | 666.1
1940.1 | 1701.1 | 663.8 | 635.7 | 701.2 | 638.3 | 666.4
1941.1 | 1702.1 | 664.3 | 636.4 | 700.5 | 638.9 | 665.2
1942.1 | 1703.1 | 664.3 | 636.8 | 701.5 | 639.1 | 665.2
1943.1 | 1704.1 | 664.4 | 634.9 | 697.5 | 639 | 663.8
1944.1 | 1705.1 | 665 | 633.4 | 695.5 | 639 | 663.5
1945.1 | 1706.1 | 665.9 | 633.4 | 702.8 | 639.6 | 666.2
1946.1 | 1707.1 | 666.3 | 634.3 | 704.6 | 640.1 | 668.3
1947.1 | 1708.1 | 666.1 | 634.9 | 711.1 | 640.5 | 670.6
1948.1 | 1709.1 | 666 | 634.5 | 713.9 | 640.9 | 672.4
1949.1 | 1710.1 | 665.7 | 634.9 | 714.9 | 641 | 673.8
1950.1 | 1711.1 | 665.9 | 634.2 | 718.4 | 641.3 | 675.6
1951.1 | 1712.1 | 666.2 | 634.4 | 718.1 | 641.6 | 675.8
1952.1 | 1713.1 | 666.3 | 635.8 | 716.4 | 641.9 | 674.1
1953.1 | 1714.1 | 666.4 | 636.3 | 714.5 | 642 | 671.8
1954.1 | 1715.1 | 667.3 | 636.7 | 707.9 | 642.5 | 671.3
1955.1 | 1716.1 | 668.9 | 636.3 | 705.7 | 643.5 | 673
1956.1 | 1717.1 | 669.2 | 635.9 | 708.2 | 644 | 674.8
1957.1 | 1718.1 | 668.7 | 634.2 | 712.5 | 643.9 | 675.8
1958.1 | 1719.1 | 668.1 | 632.5 | 710.8 | 643.5 | 675
1959.1 | 1720.1 | 668.4 | 633.1 | 712.1 | 643.6 | 675.3
1960.1 | 1721.1 | 669 | 631.9 | 716.9 | 643.7 | 676.2
1961.1 | 1722.1 | 668.8 | 630.1 | 718.5 | 643.5 | 677.2
1962.1 | 1723.1 | 668.8 | 629.3 | 716.3 | 643.2 | 676.7
1963.1 | 1724.1 | 669.3 | 630.9 | 718.7 | 643.6 | 677.1
1964.1 | 1725.1 | 669.8 | 631.5 | 716.7 | 644.1 | 676.9
1965.1 | 1726.1 | 670.2 | 632.7 | 718.7 | 644.5 | 678.4
1966.1 | 1727.1 | 670.4 | 634.8 | 723.2 | 644.9 | 681.4
1967.1 | 1728.1 | 671.1 | 636.5 | 727.8 | 645.4 | 681.5
1968.1 | 1729.1 | 671.8 | 637.8 | 727 | 646.3 | 681.5
1969.1 | 1730.1 | 672.6 | 639 | 734.1 | 647 | 682.1
1970.1 | 1731.1 | 672.6 | 639.2 | 734.9 | 647.4 | 682.8
1971.1 | 1732.1 | 672.2 | 639 | 733.7 | 647.3 | 682.8
1972.1 | 1733.1 | 672.1 | 640.9 | 736.8 | 647.3 | 683.6
1973.1 | 1734.1 | 672.4 | 641.8 | 739 | 647.4 | 684.6
1974.1 | 1735.1 | 672.8 | 640.9 | 741 | 647.7 | 684.4
1975.1 | 1736.1 | 672.8 | 640.2 | 739.8 | 648 | 682
1976.1 | 1737.1 | 672.5 | 637.7 | 732.1 | 647.6 | 679
1977.1 | 1738.1 | 672.3 | 635.6 | 730.3 | 647.2 | 677.1
1978.1 | 1739.1 | 672.8 | 634.8 | 725.9 | 647.5 | 676.4
1979.1 | 1740.1 | 673.1 | 634.4 | 720 | 647.5 | 675.2
1980.1 | 1741.1 | 673.6 | 633.8 | 717.3 | 647.4 | 674.4
1981.1 | 1742.1 | 674.4 | 634.3 | 714.4 | 647.9 | 676.3
1982.1 | 1743.1 | 675.3 | 635.6 | 713.3 | 648.6 | 678
1983.1 | 1744.1 | 675 | 635.2 | 714.5 | 649 | 679.2
1984.1 | 1745.1 | 674.8 | 635.4 | 717.7 | 649.2 | 679.9
1985.1 | 1746.1 | 675.1 | 638.5 | 723.2 | 649.8 | 681.4
1986.1 | 1747.1 | 675.3 | 639.4 | 723.2 | 650 | 681.3
1987.1 | 1748.1 | 675.3 | 639.1 | 724.9 | 650.2 | 682.7
1988.1 | 1749.1 | 675.6 | 637.7 | 727.1 | 650.4 | 683.6
1989.1 | 1750.1 | 675.2 | 637.1 | 725.9 | 650.2 | 682.7
1990.1 | 1751.1 | 675.2 | 636.8 | 722.1 | 650.1 | 680.8
1991.1 | 1752.1 | 675.3 | 637.5 | 716.2 | 649.9 | 679.4
1992.1 | 1753.1 | 676.2 | 638.8 | 710.4 | 650.2 | 678.9
1993.1 | 1754.1 | 677.1 | 641.5 | 705 | 650.9 | 679.5
1994.1 | 1755.1 | 678.1 | 641.9 | 699.3 | 651.8 | 678.8
1995.1 | 1756.1 | 678.9 | 642.1 | 705.5 | 652.7 | 679.7
1996.1 | 1757.1 | 679.5 | 642.1 | 710.8 | 653.8 | 682.3
1997.1 | 1758.1 | 679.9 | 640.4 | 712.3 | 654.7 | 680.8
1998.1 | 1759.1 | 680.1 | 638.1 | 711.3 | 655.1 | 677.9
1999.1 | 1760.1 | 680 | 635.3 | 707.3 | 655.1 | 675.5
2000.1 | 1761.1 | 679.6 | 634.9 | 705.5 | 655.1 | 674.4
2001.1 | 1762.1 | 679.7 | 635.8 | 705.4 | 655.2 | 674.8
2002.1 | 1763.1 | 680.9 | 637.8 | 706.1 | 655.9 | 677.1
2003.1 | 1764.1 | 682.1 | 640 | 711.9 | 656.9 | 680.2
2004.1 | 1765.1 | 681.8 | 639.8 | 710.4 | 657.3 | 681.2
2005.1 | 1766.1 | 681.1 | 639.3 | 712.1 | 657.3 | 680.3
2006.1 | 1767.1 | 681.2 | 640.1 | 711.2 | 657.3 | 676.6
2007.1 | 1768.1 | 681.4 | 639.5 | 707.9 | 657.1 | 674.9
2008.1 | 1769.1 | 681.2 | 637.5 | 706 | 656.7 | 673.4
2009.1 | 1770.1 | 680.9 | 637.2 | 706.3 | 656.2 | 674.7
2010.1 | 1771.1 | 681.3 | 636.7 | 710.6 | 656.2 | 677.4
2011.1 | 1772.1 | 681.2 | 637.7 | 710.4 | 656.1 | 677.7
2012.1 | 1773.1 | 681.5 | 638.2 | 709.6 | 656.2 | 678.6
2013.1 | 1774.1 | 681.9 | 638.9 | 713 | 656.3 | 680
2014.1 | 1775.1 | 681.8 | 638 | 711.2 | 656.2 | 678.2
2015.1 | 1776.1 | 682 | 636.3 | 713.2 | 656.4 | 678
2016.1 | 1777.1 | 682.2 | 635.3 | 713.4 | 656.6 | 677.6
2017.1 | 1778.1 | 682.4 | 637.3 | 711.6 | 657 | 675.4
2018.1 | 1779.1 | 683 | 640.1 | 711.9 | 657.5 | 675.6
2019.1 | 1780.1 | 683.4 | 640.8 | 708.1 | 658.1 | 674.6
2020.1 | 1781.1 | 683.3 | 638.1 | 702.6 | 658 | 672.5
2021.1 | 1782.1 | 682.9 | 637.2 | 702.4 | 657.6 | 673.6
2022.1 | 1783.1 | 682.4 | 636.7 | 701.8 | 657.2 | 672.5
2023.1 | 1784.1 | 682.7 | 637 | 703.3 | 657 | 674.3
2024.1 | 1785.1 | 683.2 | 639.2 | 705.5 | 657.3 | 678.8
2025.1 | 1786.1 | 683.7 | 640.4 | 709.7 | 657.9 | 681.1
2026.1 | 1787.1 | 683.9 | 640.8 | 711.6 | 658.6 | 680.6
2027.1 | 1788.1 | 684 | 640.6 | 717.1 | 658.8 | 682.5
2028.1 | 1789.1 | 683.6 | 640.3 | 715.6 | 658.9 | 682.1
2029.1 | 1790.1 | 683.5 | 638.8 | 717.1 | 658.8 | 682.5
2030.1 | 1791.1 | 683.5 | 637.6 | 718.1 | 658.7 | 682.6
2031.1 | 1792.1 | 683.6 | 636.9 | 719.1 | 658.7 | 682.5
2032.1 | 1793.1 | 683.9 | 637 | 720.2 | 659 | 682.2
2033.1 | 1794.1 | 684.5 | 636.2 | 718.7 | 659.5 | 682
2034.1 | 1795.1 | 684.2 | 636.3 | 716.5 | 659.4 | 680.5
2035.1 | 1796.1 | 683.7 | 635.8 | 713.4 | 658.9 | 679.4
2036.1 | 1797.1 | 683.3 | 634.6 | 712.5 | 658.4 | 679.5
2037.1 | 1798.1 | 683.2 | 634.5 | 713.6 | 657.9 | 680.6
2038.1 | 1799.1 | 683.6 | 635.9 | 711 | 658 | 681
2039.1 | 1800.1 | 684.6 | 637.2 | 713.6 | 658.4 | 683.7
2040.1 | 1801.1 | 684.6 | 637.1 | 711.2 | 658.6 | 684.7
2041.1 | 1802.1 | 684.9 | 637 | 713.2 | 659.1 | 685.1
2042.1 | 1803.1 | 685.7 | 638.4 | 716.5 | 659.8 | 686.5
2043.1 | 1804.1 | 686.4 | 639.1 | 716.8 | 660.4 | 685.8
2044.1 | 1805.1 | 686.8 | 639.1 | 713 | 661 | 684.2
2045.1 | 1806.1 | 686.9 | 639.3 | 708.7 | 661.4 | 681.8
2046.1 | 1807.1 | 687.9 | 639.1 | 716.2 | 662.4 | 683.9
2047.1 | 1808.1 | 688.1 | 637.7 | 720.7 | 663 | 686.5
2048.1 | 1809.1 | 687.7 | 637 | 725.1 | 663.2 | 687.5
2049.1 | 1810.1 | 687.7 | 638.1 | 729.9 | 663.6 | 689
2050.1 | 1811.1 | 687.5 | 640.5 | 729.2 | 663.9 | 688.7
2051.1 | 1812.1 | 687.3 | 643.3 | 729.5 | 664 | 687.2
2052.1 | 1813.1 | 687.2 | 645.6 | 731.8 | 664 | 686.5
2053.1 | 1814.1 | 687.7 | 646.5 | 732.1 | 664.5 | 686.3
2054.1 | 1815.1 | 688.1 | 647.9 | 729.8 | 664.9 | 686.2
2055.1 | 1816.1 | 687.8 | 648.5 | 731.4 | 665 | 686.8
2056.1 | 1817.1 | 687.8 | 649.8 | 730.8 | 665.1 | 686.6
2057.1 | 1818.1 | 688.4 | 650.9 | 728.5 | 665.3 | 687.6
2058.1 | 1819.1 | 689.4 | 649.9 | 730 | 665.6 | 688.8
2059.1 | 1820.1 | 689.4 | 647.5 | 729.8 | 665.7 | 688.6
2060.1 | 1821.1 | 689 | 645 | 730.6 | 665.5 | 687.4
2061.1 | 1822.1 | 689 | 646.3 | 733.9 | 665.6 | 689.3
2062.1 | 1823.1 | 688.9 | 645.5 | 733.8 | 665.4 | 689
2063.1 | 1824.1 | 688.8 | 644.8 | 733.7 | 665.1 | 689.5
2064.1 | 1825.1 | 689 | 645.4 | 732.9 | 665.1 | 689.8
2065.1 | 1826.1 | 689.4 | 646.4 | 734.9 | 665.3 | 690.6
2066.1 | 1827.1 | 689.8 | 646.4 | 734 | 665.7 | 691.3
2067.1 | 1828.1 | 689.9 | 645.2 | 730.4 | 666.2 | 690.5
2068.1 | 1829.1 | 689.6 | 642.8 | 729.6 | 666.3 | 689.4
2069.1 | 1830.1 | 689.2 | 642.5 | 729.9 | 666.2 | 690.1
2070.1 | 1831.1 | 689.3 | 642 | 731.1 | 666.2 | 690.3
2071.1 | 1832.1 | 689.3 | 642.3 | 730.2 | 666.1 | 690.5
2072.1 | 1833.1 | 689.2 | 641 | 729.7 | 665.7 | 690.2
2073.1 | 1834.1 | 688.7 | 640 | 723.7 | 665.1 | 690.4
2074.1 | 1835.1 | 688.9 | 639.2 | 721.8 | 664.9 | 689.9
2075.1 | 1836.1 | 689.6 | 637.9 | 722.3 | 665 | 692
2076.1 | 1837.1 | 689.4 | 637 | 721.7 | 664.8 | 692.2
2077.1 | 1838.1 | 689.6 | 638 | 723.8 | 664.8 | 693.1
2078.1 | 1839.1 | 689.1 | 636.5 | 717.2 | 664.6 | 691.7
2079.1 | 1840.1 | 688.5 | 633.5 | 713.7 | 664.1 | 689.5
2080.1 | 1841.1 | 688 | 631.4 | 712.5 | 663.3 | 687.1
2081.1 | 1842.1 | 688.2 | 631.8 | 714.3 | 663.1 | 687.8
2082.1 | 1843.1 | 689.5 | 634 | 710.9 | 663.9 | 687.6
2083.1 | 1844.1 | 690.4 | 635.5 | 710.1 | 664.5 | 689.5
2084.1 | 1845.1 | 690.7 | 636.6 | 708.1 | 665.2 | 691
2085.1 | 1846.1 | 690.9 | 635.9 | 708.5 | 665.9 | 690.9
2086.1 | 1847.1 | 691.5 | 634.3 | 707.1 | 667 | 688.2
2087.1 | 1848.1 | 692 | 634.6 | 710.5 | 667.5 | 691
2088.1 | 1849.1 | 692 | 636.8 | 715 | 667.9 | 692.4
2089.1 | 1850.1 | 691.7 | 636.9 | 714.7 | 668 | 691.7
2090.1 | 1851.1 | 691.5 | 636.4 | 716.7 | 667.9 | 691.9
2091.1 | 1852.1 | 691 | 634.8 | 715.1 | 667.7 | 689.8
2092.1 | 1853.1 | 692.2 | 635.8 | 714.7 | 668.4 | 689.8
2093.1 | 1854.1 | 692.9 | 637.8 | 713.4 | 669.3 | 690.5
2094.1 | 1855.1 | 693.3 | 638.2 | 714.7 | 670 | 690.9
2095.1 | 1856.1 | 693.7 | 638.5 | 722.4 | 670.7 | 692.6
2096.1 | 1857.1 | 693.3 | 637.9 | 725.4 | 670.9 | 693
2097.1 | 1858.1 | 692.8 | 636.3 | 725.3 | 670.7 | 692
2098.1 | 1859.1 | 692.7 | 636.1 | 721.5 | 670.4 | 691.1
2099.1 | 1860.1 | 692.9 | 635.1 | 724.7 | 670.6 | 691.9
2100.1 | 1861.1 | 692.7 | 635.6 | 726.3 | 670.6 | 692.7
2101.1 | 1862.1 | 693.1 | 638.7 | 729.7 | 671.1 | 691.7
2102.1 | 1863.1 | 693 | 641.4 | 729.9 | 671.3 | 692.9
2103.1 | 1864.1 | 693 | 641 | 723.6 | 671.1 | 690.6
2104.1 | 1865.1 | 693.8 | 642 | 722.9 | 671.4 | 693.5
2105.1 | 1866.1 | 694.8 | 642.5 | 726.2 | 672.4 | 694.3
2106.1 | 1867.1 | 695.4 | 642.8 | 726 | 673.1 | 693.5
2107.1 | 1868.1 | 696 | 643.2 | 721.4 | 674.1 | 692.9
2108.1 | 1869.1 | 696.7 | 644.5 | 720.1 | 674.8 | 691.4
2109.1 | 1870.1 | 697.1 | 644.9 | 719.1 | 675.6 | 693
2110.1 | 1871.1 | 697.3 | 644.9 | 715.6 | 675.9 | 693.6
2111.1 | 1872.1 | 697.2 | 643.7 | 713.6 | 675.9 | 693.4
2112.1 | 1873.1 | 697.4 | 644.4 | 713.2 | 676.2 | 694.3
2113.1 | 1874.1 | 697.8 | 644.1 | 706.9 | 676.8 | 693.1
2114.1 | 1875.1 | 698 | 644.3 | 710.4 | 677 | 693.4
2115.1 | 1876.1 | 697.5 | 642.9 | 711.2 | 676.9 | 693.4
2116.1 | 1877.1 | 697 | 640.9 | 712.3 | 676.4 | 692
2117.1 | 1878.1 | 696.6 | 641.3 | 710.3 | 675.7 | 691.8
2118.1 | 1879.1 | 696.5 | 640.9 | 713.3 | 675.4 | 693.8
2119.1 | 1880.1 | 696.5 | 640.5 | 713.8 | 675.4 | 695.3
2120.1 | 1881.1 | 696.9 | 639.9 | 713.4 | 675.5 | 695.6
2121.1 | 1882.1 | 697.5 | 639.2 | 714.3 | 675.9 | 695
2122.1 | 1883.1 | 697.5 | 638.8 | 717.9 | 676 | 695.9
2123.1 | 1884.1 | 696.9 | 637.5 | 716.6 | 675.6 | 694.9
2124.1 | 1885.1 | 696.7 | 636 | 716.5 | 675 | 695.1
2125.1 | 1886.1 | 696.2 | 635.1 | 716 | 674.4 | 694.5
2126.1 | 1887.1 | 696 | 634.6 | 711 | 674.2 | 691
2127.1 | 1888.1 | 696.4 | 633.5 | 710.8 | 674.5 | 689.6
2128.1 | 1889.1 | 697 | 632.8 | 706.1 | 674.9 | 689.2
2129.1 | 1890.1 | 696.9 | 632.1 | 705.6 | 674.6 | 688.9
2130.1 | 1891.1 | 697 | 634.3 | 710.2 | 674.9 | 692.7
2131.1 | 1892.1 | 697 | 635.5 | 713.3 | 675.2 | 693.7
2132.1 | 1893.1 | 697.3 | 636.2 | 715 | 675.5 | 693.9
2133.1 | 1894.1 | 697.3 | 636.4 | 711.5 | 675.5 | 691.2
2134.1 | 1895.1 | 697.8 | 636.9 | 708.9 | 676 | 690.8
2135.1 | 1896.1 | 698.7 | 637.7 | 707.6 | 677 | 690.8
2136.1 | 1897.1 | 699.3 | 637.2 | 702.9 | 677.8 | 690.9
2137.1 | 1898.1 | 699.3 | 635.8 | 705.5 | 678.1 | 690.1
2138.1 | 1899.1 | 699.5 | 635.3 | 703.7 | 678.3 | 689.7
2139.1 | 1900.1 | 700.3 | 636.9 | 705.6 | 679.1 | 690.7
2140.1 | 1901.1 | 701 | 641 | 710.7 | 679.9 | 694.1
2141.1 | 1902.1 | 701.3 | 643.3 | 714.7 | 680.4 | 695.6
2142.1 | 1903.1 | 700.9 | 642.5 | 713.8 | 680.8 | 694.5
2143.1 | 1904.1 | 700.4 | 641 | 712.5 | 680.7 | 692.8
2144.1 | 1905.1 | 700.3 | 642.9 | 716.6 | 681 | 694.1
2145.1 | 1906.1 | 700.2 | 643.7 | 717.6 | 680.9 | 695.9
2146.1 | 1907.1 | 699.8 | 643.1 | 717.3 | 680.6 | 695.3
2147.1 | 1908.1 | 699.5 | 642.2 | 717.2 | 680.4 | 694.7
2148.1 | 1909.1 | 699.4 | 641 | 715.5 | 679.8 | 694.5
2149.1 | 1910.1 | 699.1 | 640.1 | 714.8 | 679.2 | 694.4
2150.1 | 1911.1 | 698.7 | 637.9 | 715.3 | 678.7 | 693.5
2151.1 | 1912.1 | 698.5 | 637.7 | 718 | 678.3 | 694.4
2152.1 | 1913.1 | 698.4 | 639.8 | 716.6 | 678.4 | 697
2153.1 | 1914.1 | 698.2 | 640 | 715.3 | 678 | 695.6
2154.1 | 1915.1 | 698.3 | 640.1 | 716.6 | 678 | 696.3
2155.1 | 1916.1 | 698.1 | 639.4 | 715.8 | 677.8 | 696
2156.1 | 1917.1 | 698.1 | 639.2 | 713.9 | 677.6 | 696.1
2157.1 | 1918.1 | 698.1 | 638.9 | 713.7 | 677.5 | 696.8
2158.1 | 1919.1 | 698.1 | 638.9 | 714.6 | 677.6 | 697.2
2159.1 | 1920.1 | 698.8 | 639.8 | 718.4 | 678.4 | 699.2
2160.1 | 1921.1 | 699.2 | 640.8 | 723.1 | 679 | 701.5
2161.1 | 1922.1 | 699.4 | 643.6 | 723.8 | 679.6 | 701.4
2162.1 | 1923.1 | 699.4 | 645.3 | 722.5 | 679.8 | 700.7
2163.1 | 1924.1 | 699.7 | 645.9 | 720.9 | 680.3 | 699.5
2164.1 | 1925.1 | 700.6 | 646.7 | 720.8 | 681.4 | 699.9
2165.1 | 1926.1 | 701.6 | 649.3 | 720.5 | 682.5 | 702.1
2166.1 | 1927.1 | 701.6 | 650.3 | 718.9 | 682.9 | 703.1
2167.1 | 1928.1 | 701.3 | 650.1 | 718.4 | 682.8 | 702.7
2168.1 | 1929.1 | 700.9 | 648.8 | 716.9 | 682.6 | 701.2
2169.1 | 1930.1 | 700.6 | 647.3 | 718.1 | 682.3 | 700.7
2170.1 | 1931.1 | 701 | 645.6 | 720.5 | 682.3 | 701.1
2171.1 | 1932.1 | 700.8 | 645 | 715.9 | 682.2 | 700.2
2172.1 | 1933.1 | 700.8 | 644.6 | 713.6 | 682.3 | 699.6
2173.1 | 1934.1 | 701 | 644.4 | 712.7 | 682.7 | 698.3
2174.1 | 1935.1 | 701.1 | 643.4 | 709.2 | 682.6 | 696.6
2175.1 | 1936.1 | 701.2 | 642.9 | 710.5 | 682.7 | 695.6
2176.1 | 1937.1 | 701.2 | 642.4 | 712.9 | 682.6 | 698.2
2177.1 | 1938.1 | 700.7 | 641.4 | 712.9 | 682.1 | 698.7
2178.1 | 1939.1 | 700.6 | 641 | 716 | 682 | 699.1
2179.1 | 1940.1 | 701.1 | 642.2 | 718.2 | 682.5 | 701
2180.1 | 1941.1 | 701.4 | 643.4 | 721.5 | 682.9 | 703.5
2181.1 | 1942.1 | 701.4 | 643.5 | 716.9 | 683.3 | 702.6
2182.1 | 1943.1 | 702 | 645 | 710.1 | 684.2 | 702.9
2183.1 | 1944.1 | 702.7 | 647.3 | 700.9 | 684.7 | 702.5
2184.1 | 1945.1 | 702.9 | 647.1 | 704.1 | 684.7 | 703.1
2185.1 | 1946.1 | 702.9 | 647.1 | 706.2 | 684.8 | 704.8
2186.1 | 1947.1 | 702.9 | 647 | 704.7 | 684.8 | 704
2187.1 | 1948.1 | 703.1 | 646.5 | 704.7 | 685.2 | 703.7
2188.1 | 1949.1 | 703.4 | 645.5 | 706 | 685.6 | 702.2
2189.1 | 1950.1 | 702.9 | 644 | 705.6 | 685.2 | 700.7
2190.1 | 1951.1 | 702.3 | 643 | 705.1 | 684.4 | 699.8
2191.1 | 1952.1 | 701.7 | 641.4 | 704.1 | 684 | 698.7
2192.1 | 1953.1 | 701.2 | 638.7 | 696.8 | 683.4 | 694.5
2193.1 | 1954.1 | 701.1 | 636 | 692.7 | 682.8 | 691.5
2194.1 | 1955.1 | 700.6 | 632.9 | 688.6 | 681.8 | 690.1
2195.1 | 1956.1 | 699.9 | 630 | 687.6 | 680.6 | 689.9
2196.1 | 1957.1 | 699.5 | 627.9 | 687 | 679.7 | 690.7
2197.1 | 1958.1 | 699.1 | 626.4 | 688.8 | 679 | 692.2
2198.1 | 1959.1 | 698.8 | 626.6 | 694.2 | 678.6 | 695.9
2199.1 | 1960.1 | 698.9 | 628.5 | 696.4 | 678.7 | 698.5
2200.1 | 1961.1 | 699 | 629.6 | 690.8 | 679 | 698.3
2201.1 | 1962.1 | 699.4 | 629.7 | 695.7 | 679.4 | 699.5
2202.1 | 1963.1 | 699.5 | 630.4 | 697.2 | 679.6 | 699.6
2203.1 | 1964.1 | 699.2 | 630.3 | 698.8 | 679.4 | 698.4
2204.1 | 1965.1 | 699.2 | 631.4 | 697.7 | 679.2 | 699.5
2205.1 | 1966.1 | 699.7 | 633.8 | 694.7 | 680 | 699.3
2206.1 | 1967.1 | 700.6 | 635.2 | 695.7 | 681.2 | 697.9
2207.1 | 1968.1 | 700.9 | 636.4 | 698.9 | 681.7 | 698.6
2208.1 | 1969.1 | 700.7 | 638.2 | 697.1 | 681.6 | 698.5
2209.1 | 1970.1 | 700.7 | 639.9 | 692.5 | 682 | 698.4
2210.1 | 1971.1 | 700.9 | 641.5 | 686.2 | 682.4 | 695.9
2211.1 | 1972.1 | 701.2 | 641.5 | 690.6 | 682.7 | 695.6
2212.1 | 1973.1 | 701.1 | 641.7 | 692.8 | 682.9 | 697.4
2213.1 | 1974.1 | 701.4 | 641.8 | 695.9 | 683.6 | 699.9
2214.1 | 1975.1 | 701.7 | 640.9 | 697.3 | 684.1 | 700.9
2215.1 | 1976.1 | 701.6 | 639.8 | 702.3 | 684 | 700.9
2216.1 | 1977.1 | 701.2 | 638.9 | 702.5 | 684.1 | 700.3
2217.1 | 1978.1 | 700.9 | 637.7 | 700.6 | 684.1 | 697.1
2218.1 | 1979.1 | 701.1 | 638.9 | 703.5 | 684.5 | 697.6
2219.1 | 1980.1 | 701.2 | 639.5 | 704.6 | 684.8 | 698
2220.1 | 1981.1 | 701.2 | 639.2 | 708.6 | 684.7 | 699.6
2221.1 | 1982.1 | 701.1 | 637.9 | 707 | 684.3 | 697.9
2222.1 | 1983.1 | 701.4 | 638.6 | 705 | 684.1 | 697.8
2223.1 | 1984.1 | 701.2 | 639.3 | 704.2 | 683.7 | 697.8
2224.1 | 1985.1 | 701 | 640.5 | 702 | 683.4 | 699.1
2225.1 | 1986.1 | 701 | 640.5 | 697.6 | 683.6 | 696.8
2226.1 | 1987.1 | 700.9 | 639 | 697.4 | 683.5 | 695.1
2227.1 | 1988.1 | 701.3 | 639.3 | 696.2 | 683.3 | 696.9
2228.1 | 1989.1 | 701.8 | 640.5 | 693.1 | 683.7 | 696.9
2229.1 | 1990.1 | 701.8 | 640 | 691.6 | 684 | 695.2
2230.1 | 1991.1 | 701.6 | 638.4 | 692.7 | 683.4 | 693.6
2231.1 | 1992.1 | 701.1 | 636.2 | 688.7 | 682.5 | 690.2
2232.1 | 1993.1 | 700.9 | 635.3 | 684.9 | 682.3 | 689.9
2233.1 | 1994.1 | 700.7 | 634.5 | 680.8 | 682 | 689.5
2234.1 | 1995.1 | 700.6 | 634.7 | 681.5 | 681.7 | 689.3
2235.1 | 1996.1 | 701.1 | 635.9 | 681 | 682.1 | 690.1
2236.1 | 1997.1 | 701.4 | 638.5 | 678 | 682.2 | 689.1
2237.1 | 1998.1 | 701.4 | 638.8 | 677.8 | 682.5 | 687.6
2238.1 | 1999.1 | 701.7 | 638.2 | 682.5 | 682.6 | 689.8
2239.1 | 2000.1 | 701.7 | 637.1 | 685.7 | 682.2 | 691
2240.1 | 2001.1 | 701.4 | 636.4 | 682.9 | 681.8 | 688.7
2241.1 | 2002.1 | 701.3 | 635.1 | 679.7 | 681.6 | 686.6
2242.1 | 2003.1 | 701.8 | 635.9 | 682.1 | 681.8 | 688.7
2243.1 | 2004.1 | 702.1 | 636.3 | 677.9 | 682.4 | 688.9
2244.1 | 2005.1 | 702.2 | 635 | 675.8 | 682.7 | 687.5
2245.1 | 2006.1 | 702.6 | 633.8 | 680.1 | 683.1 | 686.9
2246.1 | 2007.1 | 702.5 | 632.8 | 681.9 | 682.9 | 687.6
2247.1 | 2008.1 | 702.2 | 632.3 | 687 | 682.3 | 689.4
2248.1 | 2009.1 | 702 | 633.5 | 687.1 | 682.2 | 690.7
2249.1 | 2010.1 | 702.1 | 634.3 | 687.8 | 682.7 | 689.4
2250.1 | 2011.1 | 702.4 | 636.6 | 683.3 | 682.8 | 689.4
2251.1 | 2012.1 | 702.6 | 638.8 | 680.1 | 682.8 | 689.5
2252.1 | 2013.1 | 702.6 | 638.5 | 681.8 | 682.9 | 689.3
2253.1 | 2014.1 | 702.6 | 638.9 | 682.9 | 683.3 | 691.3
2254.1 | 2015.1 | 702.7 | 640.1 | 686.5 | 683.3 | 693.4
2255.1 | 2016.1 | 702.5 | 640.7 | 684.3 | 683.2 | 692.4
2256.1 | 2017.1 | 702.4 | 641.2 | 684.1 | 683.1 | 692.4
2257.1 | 2018.1 | 702.7 | 644 | 683.3 | 683.8 | 694
2258.1 | 2019.1 | 702.9 | 646.3 | 684.6 | 684.4 | 693.4
2259.1 | 2020.1 | 703 | 646.3 | 685.1 | 684.6 | 692.1
2260.1 | 2021.1 | 702.6 | 643.8 | 684.7 | 684.3 | 688.7
2261.1 | 2022.1 | 702.7 | 642.3 | 687.8 | 684.5 | 687.9
2262.1 | 2023.1 | 702.6 | 640.8 | 684.4 | 684.6 | 685.4
2263.1 | 2024.1 | 702.5 | 639.5 | 678.4 | 684.5 | 682.8
2264.1 | 2025.1 | 702.5 | 638.4 | 676.4 | 684.3 | 682.2
2265.1 | 2026.1 | 702.2 | 636.6 | 672.5 | 683.7 | 679.8
2266.1 | 2027.1 | 701.9 | 634.2 | 669.4 | 683.1 | 678.5
2267.1 | 2028.1 | 702 | 633.7 | 671.7 | 683.1 | 682
2268.1 | 2029.1 | 702 | 634.3 | 670.8 | 683.1 | 683.9
2269.1 | 2030.1 | 701.8 | 634.3 | 669.5 | 682.3 | 683.8
2270.1 | 2031.1 | 701.5 | 634.5 | 669 | 681.9 | 682.3
2271.1 | 2032.1 | 701.4 | 635.6 | 674.7 | 681.7 | 684.9
2272.1 | 2033.1 | 701.4 | 637.4 | 680.3 | 681.5 | 687.3
2273.1 | 2034.1 | 701.2 | 639 | 682.4 | 681.8 | 688
2274.1 | 2035.1 | 701.1 | 639 | 683.4 | 682.1 | 686.8
2275.1 | 2036.1 | 700.9 | 638.7 | 681.7 | 681.7 | 685.2
2276.1 | 2037.1 | 700.6 | 637.5 | 685.5 | 681.2 | 683.9
2277.1 | 2038.1 | 700.4 | 635.6 | 687.6 | 680.7 | 684.1
2278.1 | 2039.1 | 700.2 | 634.5 | 690.3 | 680 | 684.2
2279.1 | 2040.1 | 700 | 633.6 | 689.5 | 680 | 684.5
2280.1 | 2041.1 | 699.8 | 632.3 | 687.1 | 679.8 | 683.2
2281.1 | 2042.1 | 699.4 | 630.9 | 685.3 | 679.3 | 682.4
2282.1 | 2043.1 | 698.7 | 628.6 | 677.6 | 678.4 | 678.4
2283.1 | 2044.1 | 697.8 | 625.5 | 668.2 | 677.5 | 674
2284.1 | 2045.1 | 697.2 | 622.5 | 659.7 | 676.9 | 669.8
2285.1 | 2046.1 | 696.7 | 620 | 654 | 676.3 | 667.9
2286.1 | 2047.1 | 696.1 | 618.8 | 647 | 676 | 665.1
2287.1 | 2048.1 | 695.8 | 617.7 | 638.7 | 675.9 | 660.8
2288.1 | 2049.1 | 695.2 | 616.1 | 630.7 | 675.4 | 656.8
2289.1 | 2050.1 | 694.8 | 617.2 | 625 | 675.5 | 654.1
2290.1 | 2051.1 | 694.4 | 616.5 | 620.8 | 674.9 | 652.4
2291.1 | 2052.1 | 693.8 | 615 | 618.1 | 674.5 | 650.7
2292.1 | 2053.1 | 693.3 | 614.3 | 614.1 | 674 | 649.4
2293.1 | 2054.1 | 692.7 | 612.3 | 610.7 | 673.1 | 648.2
2294.1 | 2055.1 | 692 | 610.1 | 605.8 | 672.2 | 646.9
2295.1 | 2056.1 | 691.3 | 607.7 | 602.3 | 671.3 | 645.3
2296.1 | 2057.1 | 690.5 | 605.3 | 598.7 | 670.2 | 643.9
2297.1 | 2058.1 | 689.6 | 603.3 | 596.4 | 669.5 | 642.4
2298.1 | 2059.1 | 688.9 | 602.4 | 597.4 | 668.9 | 641.2
2299.1 | 2060.1 | 688.1 | 601.8 | 593.3 | 667.9 | 638.8
2300.1 | 2061.1 | 687.3 | 600.7 | 589 | 666.8 | 636.5
2301.1 | 2062.1 | 686.4 | 598.9 | 585.1 | 665.5 | 634.3
2302.1 | 2063.1 | 685.6 | 596.4 | 584.1 | 664.5 | 634.3
2303.1 | 2064.1 | 684.6 | 595.5 | 581.8 | 663.5 | 633.9
2304.1 | 2065.1 | 684 | 593.6 | 580 | 663.2 | 632.9
2305.1 | 2066.1 | 683.6 | 592 | 578.3 | 662.8 | 631.8
2306.1 | 2067.1 | 683 | 591.6 | 576.7 | 661.9 | 629.8
2307.1 | 2068.1 | 682.3 | 590.9 | 574.1 | 661 | 627.4
2308.1 | 2069.1 | 681.7 | 589.6 | 573.7 | 660.3 | 625.3
2309.1 | 2070.1 | 681 | 589.1 | 573.1 | 659.5 | 623.8
2310.1 | 2071.1 | 680.2 | 587.8 | 571.7 | 658.7 | 622.9
2311.1 | 2072.1 | 679.4 | 586.4 | 569.7 | 658.2 | 621.2
2312.1 | 2073.1 | 678.6 | 585.5 | 568.7 | 657.8 | 619.9
2313.1 | 2074.1 | 678 | 584.9 | 567 | 657.4 | 619
2314.1 | 2075.1 | 677.4 | 584.2 | 565.1 | 657.1 | 618.5
2315.1 | 2076.1 | 676.7 | 582.8 | 562.6 | 656.7 | 617.1
2316.1 | 2077.1 | 675.8 | 581.5 | 560.9 | 656 | 616.3
2317.1 | 2078.1 | 675 | 579.9 | 559.3 | 655.4 | 614.8
2318.1 | 2079.1 | 674.2 | 578.1 | 557.7 | 654.9 | 613.2
2319.1 | 2080.1 | 673.7 | 577.1 | 557 | 654.8 | 612.2
2320.1 | 2081.1 | 673.1 | 576.3 | 556 | 654.3 | 611.3
2321.1 | 2082.1 | 672.5 | 575.2 | 555.5 | 653.7 | 610
2322.1 | 2083.1 | 671.8 | 574.3 | 554.6 | 653.6 | 608.4
2323.1 | 2084.1 | 671.4 | 572.7 | 553.7 | 653.6 | 607.5
2324.1 | 2085.1 | 670.9 | 571.1 | 552.2 | 653.2 | 606.4
2325.1 | 2086.1 | 670.5 | 569.7 | 552.1 | 653.2 | 606
2326.1 | 2087.1 | 669.3 | 568.7 | 551.3 | 655 | 604.7
2327.1 | 2088.1 | 664.2 | 566.5 | 551.8 | 657.9 | 603.5
2328.1 | 2089.1 | 657.4 | 563.7 | 551.1 | 662.8 | 602.3
2329.1 | 2090.1 | 656.7 | 562.1 | 551 | 667.7 | 600.2
2330.1 | 2091.1 | 651.1 | 559.5 | 549.8 | 669.7 | 598.4
2331.1 | 2092.1 | 625.9 | 551 | 539.2 | 647.1 | 596.4
2332.1 | 2093.1 | 586.9 | 529.8 | 523.7 | 619.6 | 593.1
2333.1 | 2094.1 | 599.3 | 524.9 | 521.2 | 622.4 | 590.9
2334.1 | 2095.1 | 602.7 | 510 | 511.5 | 605.2 | 589.3
2335.1 | 2096.1 | 599.6 | 481.2 | 497.2 | 577.1 | 586.2
2336.1 | 2097.1 | 578.4 | 452.5 | 484.6 | 555.9 | 582.7
2337.1 | 2098.1 | 550.4 | 435.2 | 479 | 547.6 | 579
2338.1 | 2099.1 | 558.7 | 421.8 | 473.4 | 536.5 | 575.1
2339.1 | 2100.1 | 566.7 | 412.6 | 469 | 527.8 | 570.1
2340.1 | 2101.1 | 572.7 | 405.5 | 464.4 | 520.6 | 565.3
2341.1 | 2102.1 | 578.4 | 403.5 | 456.2 | 511.8 | 560.1
2342.1 | 2103.1 | 580.2 | 402.6 | 448.2 | 506.7 | 549.5
2343.1 | 2104.1 | 580.3 | 403.3 | 440.5 | 502.1 | 529.9
2344.1 | 2105.1 | 578.7 | 403.6 | 433.4 | 497.9 | 501
2345.1 | 2106.1 | 575.3 | 401.2 | 424.5 | 493 | 469
2346.1 | 2107.1 | 570.5 | 399.8 | 417.8 | 487.6 | 436.9
2347.1 | 2108.1 | 565.4 | 397.6 | 411.2 | 480.4 | 402.7
2348.1 | 2109.1 | 559.2 | 395.1 | 404.4 | 471.9 | 286.3
2349.1 | 2110.1 | 551.2 | 393.4 | 397.8 | 460.1 | 107.5
2350.1 | 2111.1 | 538.6 | 391.5 | 391.9 | 441.5 | 96.5
2351.1 | 2112.1 | 488.8 | 390.5 | 387.5 | 413 | 96.2
2352.1 | 2113.1 | 175 | 389.4 | 382 | 392 | 96.1
2353.1 | 2114.1 | 125.5 | 388.4 | 375 | 374.4 | 94.7
2354.1 | 2115.1 | 124 | 387.5 | 367 | 361.2 | 93.6
2355.1 | 2116.1 | 123.3 | 386.4 | 211.3 | 348.5 | 93.5
2356.1 | 2117.1 | 120.7 | 385.5 | 150.4 | 335.8 | 93
2357.1 | 2118.1 | 119.4 | 384.1 | 147.2 | 321.1 | 93
2358.1 | 2119.1 | 118.2 | 382.9 | 144.6 | 305.5 | 91.7
2359.1 | 2120.1 | 118.4 | 382.3 | 143.7 | 294.1 | 89.9
2360.1 | 2121.1 | 115.2 | 381.1 | 140.2 | 283.5 | 87.6
2361.1 | 2122.1 | 112.8 | 380.5 | 136.7 | 273 | 86.9
2362.1 | 2123.1 | 110.6 | 379.5 | 135.1 | 259.9 | 86.2
2363.1 | 2124.1 | 109.7 | 375.9 | 133.4 | 251.3 | 84.8
2364.1 | 2125.1 | 108.1 | 369.4 | 130.5 | 244.4 | 84.7
2365.1 | 2126.1 | 106.2 | 365.3 | 127.8 | 237.5 | 83.8
2366.1 | 2127.1 | 106 | 362.9 | 126 | 229.8 | 82.7
2367.1 | 2128.1 | 104.7 | 361.1 | 124.5 | 223.1 | 82.1
2368.1 | 2129.1 | 104.4 | 360.3 | 123.1 | 217.5 | 81.2
2369.1 | 2130.1 | 104.6 | 359.3 | 121.6 | 212 | 80.2
2370.1 | 2131.1 | 103.4 | 358.3 | 120.4 | 206.3 | 80
2371.1 | 2132.1 | 102.3 | 358 | 119.5 | 201.1 | 79.5
2372.1 | 2133.1 | 101.3 | 358.7 | 117.8 | 195.8 | 78.8
2373.1 | 2134.1 | 100 | 359.7 | 116.3 | 191.1 | 78.3
2374.1 | 2135.1 | 98.9 | 360.4 | 114.5 | 186.2 | 77.7
2375.1 | 2136.1 | 98.1 | 360.6 | 113 | 181.1 | 75.5
2376.1 | 2137.1 | 97.3 | 361.1 | 110.9 | 176.3 | 73.8
2377.1 | 2138.1 | 96.5 | 361.3 | 109.4 | 171 | 73
2378.1 | 2139.1 | 96.1 | 361.9 | 109 | 166.2 | 72.8
2379.1 | 2140.1 | 95.4 | 361.9 | 106.4 | 161.2 | 71.7
2380.1 | 2141.1 | 94.7 | 362 | 105 | 156.6 | 70.6
2381.1 | 2142.1 | 94.2 | 362.5 | 103.2 | 152.8 | 69
2382.1 | 2143.1 | 93.8 | 362.8 | 102.7 | 149.6 | 68.3
2383.1 | 2144.1 | 93 | 362.6 | 101.7 | 146.3 | 68.3
2384.1 | 2145.1 | 92.4 | 362.3 | 100.8 | 143.6 | 67.6
2385.1 | 2146.1 | 91.7 | 362.1 | 99.3 | 136.3 | 67.5
2386.1 | 2147.1 | 91.3 | 362.2 | 98.5 | 130.4 | 68.4
2387.1 | 2148.1 | 90.7 | 361.6 | 98.8 | 129.6 | 69.3
2388.1 | 2149.1 | 90.1 | 361.4 | 97.1 | 127.7 | 68.7
2389.1 | 2150.1 | 89.4 | 360.5 | 94 | 124.8 | 67.8
2390.1 | 2151.1 | 88.9 | 360 | 92.7 | 123.8 | 67.8
2391.1 | 2152.1 | 88.3 | 359.8 | 92.1 | 122.6 | 67.5
2392.1 | 2153.1 | 87.8 | 357.3 | 92 | 121.2 | 67.4
2393.1 | 2154.1 | 87.4 | 353.9 | 90.4 | 119.6 | 67.4
2394.1 | 2155.1 | 86.6 | 352.9 | 89.4 | 118.2 | 66.3
2395.1 | 2156.1 | 85.9 | 352.9 | 88.6 | 117 | 64.7
2396.1 | 2157.1 | 85.5 | 352.8 | 88.7 | 115.7 | 63.5
2397.1 | 2158.1 | 85.3 | 352.3 | 86.5 | 114.2 | 61.8
2398.1 | 2159.1 | 84.9 | 351.9 | 85.5 | 112.6 | 61.1
2399.1 | 2160.1 | 84.3 | 351.4 | 83.3 | 111.1 | 60.6
2400.1 | 2161.1 | 83.2 | 350.8 | 82.5 | 109.8 | 60.1
2401.1 | 2162.1 | 83.1 | 349.7 | 82.1 | 109 | 59.4
2402.1 | 2163.1 | 82.6 | 348.9 | 80.9 | 107.9 | 59.1
2403.1 | 2164.1 | 82.1 | 348.3 | 79.7 | 106.8 | 58.2
2404.1 | 2165.1 | 81.8 | 347.5 | 79.1 | 106.1 | 58.6
2405.1 | 2166.1 | 81.3 | 346.7 | 78.2 | 106 | 58.8
2406.1 | 2167.1 | 81 | 346.1 | 77.5 | 105.7 | 59
2407.1 | 2168.1 | 80.7 | 345.4 | 76.6 | 105.2 | 59.1
2408.1 | 2169.1 | 80.5 | 344.4 | 75.5 | 104.5 | 59.9
2409.1 | 2170.1 | 80 | 343.6 | 75.6 | 103.4 | 59.5
2410.1 | 2171.1 | 79.7 | 342.6 | 74.5 | 103.2 | 59.3
2411.1 | 2172.1 | 79.4 | 341.8 | 73 | 103.1 | 59.4
2412.1 | 2173.1 | 79.1 | 341.2 | 72.2 | 102.3 | 60.2
2413.1 | 2174.1 | 78.7 | 340.5 | 71.8 | 102.1 | 60.5
2414.1 | 2175.1 | 78.4 | 339.9 | 71 | 101.6 | 60.1
2415.1 | 2176.1 | 78.2 | 339 | 69.9 | 100.9 | 60.5
2416.1 | 2177.1 | 77.8 | 338.4 | 69 | 100.7 | 61
2417.1 | 2178.1 | 77.5 | 337.8 | 68.3 | 100.6 | 61.2
2418.1 | 2179.1 | 77.2 | 337.3 | 67.6 | 100.4 | 61.5
2419.1 | 2180.1 | 77.1 | 336.7 | 66.8 | 100.4 | 61.6
2420.1 | 2181.1 | 76.9 | 336 | 67.1 | 100.1 | 61
2421.1 | 2182.1 | 76.8 | 335.3 | 67.3 | 99.5 | 60.7
2422.1 | 2183.1 | 76.4 | 334.2 | 66.6 | 99 | 59.6
2423.1 | 2184.1 | 76.3 | 333.1 | 65.8 | 98.7 | 59
2424.1 | 2185.1 | 76.3 | 331.7 | 64.7 | 98.7 | 59.1
2425.1 | 2186.1 | 76.1 | 331 | 64.5 | 98.7 | 58.5
2426.1 | 2187.1 | 75.8 | 330.5 | 63.8 | 98.3 | 56.9
2427.1 | 2188.1 | 75.5 | 329.8 | 63.3 | 98.1 | 55.5
2428.1 | 2189.1 | 75.1 | 328.9 | 62.2 | 97.7 | 54.8
2429.1 | 2190.1 | 75.3 | 328.2 | 62.4 | 97.3 | 54.5
2430.1 | 2191.1 | 75 | 327.5 | 62.4 | 96.5 | 54.7
2431.1 | 2192.1 | 74.5 | 326.6 | 61.7 | 95.9 | 56.1
2432.1 | 2193.1 | 74.4 | 326.4 | 60.9 | 95.7 | 56.3
2433.1 | 2194.1 | 74.2 | 326 | 61.1 | 95.6 | 55.9
2434.1 | 2195.1 | 74.2 | 325.5 | 60.1 | 95.7 | 55.6
2435.1 | 2196.1 | 74.2 | 325.3 | 60.1 | 95.6 | 55.6
2436.1 | 2197.1 | 74.1 | 324.8 | 61 | 95.3 | 56
2437.1 | 2198.1 | 73.9 | 323.4 | 60.8 | 94.9 | 56.1
2438.1 | 2199.1 | 73.5 | 323.1 | 60.2 | 94.4 | 56.5
2439.1 | 2200.1 | 73.4 | 322.8 | 59 | 94.2 | 57.2
2440.1 | 2201.1 | 73.3 | 322.5 | 58.8 | 93.9 | 57.1
2441.1 | 2202.1 | 72.9 | 322 | 58.2 | 93.6 | 56.6
2442.1 | 2203.1 | 72.8 | 321.1 | 58.3 | 93.2 | 56.5
2443.1 | 2204.1 | 72.8 | 320.3 | 58.5 | 93 | 56.7
2444.1 | 2205.1 | 72.6 | 319.4 | 57.6 | 92.8 | 57.7
2445.1 | 2206.1 | 72.5 | 318.7 | 57.1 | 92.8 | 57.6
2446.1 | 2207.1 | 72.2 | 317.9 | 56.8 | 93 | 57.4
2447.1 | 2208.1 | 72.3 | 317.4 | 56.9 | 92.6 | 57.6
2448.1 | 2209.1 | 72.2 | 316.7 | 56.1 | 92.4 | 57.5
2449.1 | 2210.1 | 72.1 | 316.4 | 55.4 | 92 | 57.4
2450.1 | 2211.1 | 71.8 | 316.4 | 55.5 | 91.5 | 56.8
2451.1 | 2212.1 | 71.5 | 316.3 | 55.7 | 91.2 | 56.6
2452.1 | 2213.1 | 71.4 | 316 | 55.4 | 90.9 | 56.7
2453.1 | 2214.1 | 71.3 | 315.2 | 55.1 | 90 | 56.4
2454.1 | 2215.1 | 71.1 | 313 | 54.5 | 89.6 | 56.4
2455.1 | 2216.1 | 71.2 | 310.9 | 55.1 | 89.8 | 56.7
2456.1 | 2217.1 | 71.2 | 309.2 | 55.3 | 89.9 | 56.9
2457.1 | 2218.1 | 70.9 | 308 | 54.5 | 89.4 | 57.5
2458.1 | 2219.1 | 70.6 | 307.1 | 54.2 | 89 | 57.6
2459.1 | 2220.1 | 70.5 | 306 | 53.9 | 88.9 | 57.4
2460.1 | 2221.1 | 70.5 | 305.4 | 52.9 | 88.8 | 57.7
2461.1 | 2222.1 | 70.3 | 305.2 | 53.4 | 88.5 | 58.6
2462.1 | 2223.1 | 70.2 | 304.6 | 53.9 | 88.4 | 58.6
2463.1 | 2224.1 | 70 | 304 | 53.7 | 88.3 | 58.3
2464.1 | 2225.1 | 69.9 | 303.5 | 53.2 | 88.1 | 58.5
2465.1 | 2226.1 | 69.8 | 303.1 | 53.5 | 88 | 58.4
2466.1 | 2227.1 | 69.8 | 303.2 | 53.4 | 88 | 57.9
2467.1 | 2228.1 | 69.6 | 303.8 | 53.8 | 87.7 | 57.9
2468.1 | 2229.1 | 69.3 | 304.4 | 53.6 | 87.4 | 58.8
2469.1 | 2230.1 | 69.2 | 304.8 | 52.7 | 87.1 | 58.5
2470.1 | 2231.1 | 69.2 | 304.9 | 53 | 86.9 | 58
2471.1 | 2232.1 | 69.2 | 305 | 52.9 | 86.8 | 57.4
2472.1 | 2233.1 | 68.9 | 305.2 | 52.1 | 86.7 | 57.2
2473.1 | 2234.1 | 68.8 | 305 | 51.7 | 86.4 | 56.8
2474.1 | 2235.1 | 68.7 | 304.6 | 51 | 86.4 | 56.8
2475.1 | 2236.1 | 68.7 | 304.4 | 50.8 | 86.1 | 57.1
2476.1 | 2237.1 | 68.7 | 304.2 | 50.1 | 85.9 | 56.7
2477.1 | 2238.1 | 68.6 | 304.1 | 50.2 | 85.6 | 56.2
2478.1 | 2239.1 | 68.4 | 303.9 | 51.1 | 85.2 | 56.4
2479.1 | 2240.1 | 68.2 | 303.8 | 50.4 | 84.8 | 56.4
2480.1 | 2241.1 | 68.1 | 303.5 | 49.6 | 84.3 | 55.6
2481.1 | 2242.1 | 68 | 303.2 | 49.3 | 84 | 55.1
2482.1 | 2243.1 | 67.9 | 303 | 49.8 | 83.6 | 55.2
2483.1 | 2244.1 | 67.7 | 301.1 | 50.3 | 83.6 | 55.2
2484.1 | 2245.1 | 67.4 | 298.8 | 50.1 | 83.2 | 55.3
2485.1 | 2246.1 | 67.2 | 297.1 | 49.4 | 83 | 55.7
2486.1 | 2247.1 | 67.2 | 295.6 | 49.2 | 82.9 | 56.1
2487.1 | 2248.1 | 67.2 | 294.4 | 48.9 | 82.7 | 55.8
2488.1 | 2249.1 | 67.1 | 293.7 | 48.8 | 83 | 56.3
2489.1 | 2250.1 | 66.9 | 293.1 | 48.6 | 82.9 | 55.9
2490.1 | 2251.1 | 66.8 | 292.6 | 48.4 | 82.8 | 55.5
2491.1 | 2252.1 | 66.7 | 292.2 | 48.2 | 82.8 | 54.9
2492.1 | 2253.1 | 66.5 | 291.9 | 47.9 | 82.6 | 54.9
2493.1 | 2254.1 | 66.2 | 292.5 | 47.8 | 82.4 | 55
2494.1 | 2255.1 | 66.3 | 293.1 | 47.6 | 82.3 | 55.6
2495.1 | 2256.1 | 66.3 | 293 | 48.5 | 82.2 | 55.4
2496.1 | 2257.1 | 66.3 | 289.5 | 47.9 | 82 | 54.8
2497.1 | 2258.1 | 66.1 | 287.2 | 48.1 | 81.8 | 54.7
2498.1 | 2259.1 | 66.1 | 286.1 | 47.9 | 81.8 | 54
2499.1 | 2260.1 | 66.2 | 285.1 | 47.7 | 81.6 | 53.5
2500.1 | 2261.1 | 66.3 | 285.9 | 48.1 | 81.6 | 53.4
2501.1 | 2262.1 | 66.2 | 286.3 | 48.4 | 81.3 | 53.1
2502.1 | 2263.1 | 66.1 | 287 | 49.3 | 81 | 53.4
2503.1 | 2264.1 | 66.2 | 287.6 | 50.1 | 81.2 | 52.9
2504.1 | 2265.1 | 66.1 | 288.1 | 51.7 | 81.1 | 52.9
2505.1 | 2266.1 | 66 | 288.3 | 50.3 | 81.3 | 52.8
2506.1 | 2267.1 | 65.9 | 288.8 | 49.2 | 81.4 | 53.4
2507.1 | 2268.1 | 65.9 | 288.8 | 48.2 | 81.4 | 53.6
2508.1 | 2269.1 | 65.8 | 288.6 | 47.5 | 81.4 | 52.5
2509.1 | 2270.1 | 65.8 | 288.5 | 48.2 | 81.4 | 52.7
2510.1 | 2271.1 | 65.8 | 288.2 | 48.2 | 81.3 | 52.3
2511.1 | 2272.1 | 65.8 | 288.1 | 48 | 81.4 | 51.7
2512.1 | 2273.1 | 65.9 | 288.2 | 47.7 | 81.4 | 51.5
2513.1 | 2274.1 | 66 | 288.1 | 47.5 | 81.3 | 51.4
2514.1 | 2275.1 | 65.9 | 287.9 | 47.7 | 81.4 | 51.7
2515.1 | 2276.1 | 65.6 | 288 | 47.9 | 81 | 51.6
2516.1 | 2277.1 | 65.5 | 288.2 | 47.7 | 80.9 | 51.3
2517.1 | 2278.1 | 65.4 | 288.3 | 47.6 | 80.9 | 51.1
2518.1 | 2279.1 | 65.2 | 288.4 | 47.7 | 80.7 | 50.5
2519.1 | 2280.1 | 65 | 288.4 | 47.5 | 80.6 | 50.4
2520.1 | 2281.1 | 65 | 288 | 47.5 | 80.6 | 50.2
2521.1 | 2282.1 | 64.9 | 287.8 | 47.5 | 80.4 | 50.8
2522.1 | 2283.1 | 65 | 287.1 | 47.5 | 80.2 | 50.1
2523.1 | 2284.1 | 65 | 286.8 | 47.3 | 80.2 | 49.4
2524.1 | 2285.1 | 64.8 | 286.7 | 48 | 80.3 | 48.9
2525.1 | 2286.1 | 64.5 | 286.3 | 47.2 | 79.8 | 50
2526.1 | 2287.1 | 64.5 | 286.1 | 47.7 | 79.8 | 49.4
2527.1 | 2288.1 | 64.4 | 285.9 | 47.9 | 79.7 | 49
2528.1 | 2289.1 | 64.3 | 285.9 | 47.3 | 79.6 | 48.8
2529.1 | 2290.1 | 64.1 | 285.7 | 46.9 | 79.5 | 48
2530.1 | 2291.1 | 64.1 | 285 | 47.3 | 79.6 | 47.8
2531.1 | 2292.1 | 64.1 | 284.7 | 47 | 79.6 | 47.5
2532.1 | 2293.1 | 64.1 | 284.3 | 46.9 | 79.4 | 47
2533.1 | 2294.1 | 64.1 | 284 | 47.3 | 79.4 | 46.9
2534.1 | 2295.1 | 64.2 | 283.7 | 47.1 | 79.5 | 46.9
2535.1 | 2296.1 | 64 | 283.3 | 46.9 | 79.2 | 47.2
2536.1 | 2297.1 | 63.9 | 283.2 | 46.8 | 79.1 | 47.3
2537.1 | 2298.1 | 63.8 | 282.7 | 46.2 | 78.8 | 47.3
2538.1 | 2299.1 | 63.7 | 281.8 | 47.5 | 78.5 | 47.4
2539.1 | 2300.1 | 63.6 | 281.3 | 49.3 | 78.6 | 47.4
2540.1 | 2301.1 | 63.4 | 281.1 | 49.2 | 78.6 | 46.7
2541.1 | 2302.1 | 63.3 | 281.1 | 49.3 | 78.3 | 46.6
2542.1 | 2303.1 | 63.2 | 281.2 | 49.3 | 78 | 46.4
2543.1 | 2304.1 | 63.2 | 281 | 49.5 | 77.8 | 47.1
2544.1 | 2305.1 | 63 | 281 | 48.5 | 77.6 | 47.9
2545.1 | 2306.1 | 62.8 | 280.7 | 48.1 | 77.4 | 47.9
2546.1 | 2307.1 | 62.8 | 280.3 | 47.2 | 77.5 | 47.7
2547.1 | 2308.1 | 62.9 | 280.2 | 47.9 | 77.4 | 47.6
2548.1 | 2309.1 | 62.8 | 279.7 | 49 | 77.5 | 47.8
2549.1 | 2310.1 | 62.7 | 279.4 | 48.6 | 77.5 | 48.6
2550.1 | 2311.1 | 62.8 | 279.1 | 48 | 77.7 | 47.9
2551.1 | 2312.1 | 62.8 | 278.8 | 47.4 | 77.7 | 47.4
2552.1 | 2313.1 | 62.7 | 278.5 | 46.8 | 77.7 | 47.5
2553.1 | 2314.1 | 62.6 | 278.3 | 47 | 77.3 | 47.6
2554.1 | 2315.1 | 62.5 | 278.1 | 48.6 | 77.4 | 47.2
2555.1 | 2316.1 | 62.5 | 277.6 | 48.8 | 77.4 | 47.2
2556.1 | 2317.1 | 62.5 | 276.9 | 48.8 | 77.3 | 47.9
2557.1 | 2318.1 | 62.4 | 276.2 | 49 | 77.2 | 48.3
2558.1 | 2319.1 | 62.3 | 275.6 | 48.6 | 77.4 | 48.8
2559.1 | 2320.1 | 62.2 | 275.1 | 48 | 77.4 | 48.6
2560.1 | 2321.1 | 62.1 | 274.7 | 48.5 | 77.2 | 48.6
2561.1 | 2322.1 | 62.1 | 274.5 | 48.7 | 77.1 | 49.1
2562.1 | 2323.1 | 62.1 | 274 | 49.3 | 77 | 49.5
2563.1 | 2324.1 | 62 | 274 | 49.8 | 76.9 | 49.3
2564.1 | 2325.1 | 61.9 | 273.9 | 49.8 | 76.8 | 48.8
2565.1 | 2326.1 | 61.8 | 274 | 49.7 | 76.8 | 48.7
2566.1 | 2327.1 | 61.7 | 273.9 | 50 | 76.6 | 48.2
2567.1 | 2328.1 | 61.8 | 273.8 | 49.8 | 76.6 | 47.6
2568.1 | 2329.1 | 61.7 | 273.5 | 49.8 | 76.4 | 47.4
2569.1 | 2330.1 | 61.8 | 273.3 | 49.6 | 76.4 | 47.7
2570.1 | 2331.1 | 61.6 | 273.2 | 49.9 | 76.4 | 48.1
2571.1 | 2332.1 | 61.4 | 273 | 50.4 | 76.3 | 48.5
2572.1 | 2333.1 | 61.4 | 272.6 | 50.7 | 76.2 | 49
2573.1 | 2334.1 | 61.4 | 272.5 | 49.9 | 76.1 | 48.6
2574.1 | 2335.1 | 61.3 | 272.2 | 49.9 | 76.4 | 48.6
2575.1 | 2336.1 | 61.3 | 272.1 | 50.6 | 76.4 | 48.3
2576.1 | 2337.1 | 61.2 | 271.9 | 51.1 | 76.3 | 48.1
2577.1 | 2338.1 | 61.3 | 271.7 | 50.7 | 76.2 | 47.8
2578.1 | 2339.1 | 61.4 | 271.5 | 51 | 76 | 48.5
2579.1 | 2340.1 | 61.2 | 271.5 | 50.8 | 75.9 | 48.6
2580.1 | 2341.1 | 61.1 | 271.6 | 51 | 75.9 | 48.4
2581.1 | 2342.1 | 61.1 | 271.2 | 50.7 | 75.8 | 48.8
2582.1 | 2343.1 | 61 | 270.7 | 50.8 | 75.8 | 48.1
2583.1 | 2344.1 | 61.1 | 270 | 51 | 75.8 | 48.5
2584.1 | 2345.1 | 61 | 269.5 | 50.5 | 75.8 | 48.5
2585.1 | 2346.1 | 61.1 | 268.9 | 50.6 | 75.6 | 47.5
2586.1 | 2347.1 | 61.1 | 268.5 | 50 | 75.5 | 47
2587.1 | 2348.1 | 61 | 268.3 | 50.7 | 75.3 | 46.4
2588.1 | 2349.1 | 61 | 267.8 | 50 | 75.2 | 46.7
2589.1 | 2350.1 | 60.9 | 267.2 | 50 | 75.3 | 47.7
2590.1 | 2351.1 | 60.9 | 266.9 | 50.3 | 75.1 | 47.3
2591.1 | 2352.1 | 60.7 | 266.4 | 50.2 | 75 | 46.7
2592.1 | 2353.1 | 60.7 | 266 | 49.9 | 75 | 46.3
2593.1 | 2354.1 | 60.8 | 265.6 | 49.8 | 74.8 | 46.9
2594.1 | 2355.1 | 60.8 | 265.3 | 49.5 | 74.7 | 47.4
2595.1 | 2356.1 | 60.7 | 264.4 | 49.7 | 74.7 | 47.5
2596.1 | 2357.1 | 60.5 | 263.2 | 49.6 | 74.6 | 47.7
2597.1 | 2358.1 | 60.5 | 262.1 | 49.8 | 74.6 | 48.2
2598.1 | 2359.1 | 60.4 | 261.3 | 48.8 | 74.3 | 47.1
2599.1 | 2360.1 | 60.5 | 260.8 | 49.4 | 74.1 | 47.1
2600.1 | 2361.1 | 60.4 | 260.1 | 49.2 | 74 | 47.9
2601.1 | 2362.1 | 60.3 | 259.4 | 49.2 | 73.8 | 48.4
2602.1 | 2363.1 | 60.3 | 259 | 49.1 | 73.7 | 48.3
2603.1 | 2364.1 | 60.2 | 258.6 | 49 | 73.6 | 48.3
2604.1 | 2365.1 | 60.1 | 258.3 | 48.9 | 73.5 | 48.5
2605.1 | 2366.1 | 59.9 | 258.2 | 48.9 | 73.5 | 48
2606.1 | 2367.1 | 59.8 | 255.2 | 49.6 | 73.5 | 47.4
2607.1 | 2368.1 | 59.8 | 245 | 50 | 73.4 | 47.1
2608.1 | 2369.1 | 59.7 | 238 | 49.8 | 73.4 | 47.2
2609.1 | 2370.1 | 59.7 | 234 | 49.8 | 73.3 | 47.2
2610.1 | 2371.1 | 59.6 | 232.5 | 49.6 | 73.4 | 47.8
2611.1 | 2372.1 | 59.5 | 234.8 | 50.4 | 73.4 | 47.7
2612.1 | 2373.1 | 59.5 | 238 | 50.2 | 73.3 | 47.1
2613.1 | 2374.1 | 59.3 | 241.1 | 50 | 73.3 | 47.3
2614.1 | 2375.1 | 59.3 | 243.5 | 50.1 | 73.3 | 48
2615.1 | 2376.1 | 59.2 | 245.8 | 50.4 | 73.2 | 48
2616.1 | 2377.1 | 59.2 | 247.8 | 50.5 | 73.1 | 47.1
2617.1 | 2378.1 | 59.1 | 249.4 | 50.5 | 73 | 47.9
2618.1 | 2379.1 | 58.9 | 250.7 | 50.1 | 72.8 | 47.5
2619.1 | 2380.1 | 58.9 | 251.5 | 49.2 | 72.6 | 47
2620.1 | 2381.1 | 58.8 | 252.2 | 49.5 | 72.6 | 48
2621.1 | 2382.1 | 58.8 | 252.5 | 49.3 | 72.5 | 48.5
2622.1 | 2383.1 | 59 | 252.5 | 49.4 | 72.4 | 48.3
2623.1 | 2384.1 | 58.8 | 252.5 | 49.7 | 72.3 | 48.2
2624.1 | 2385.1 | 59 | 252.4 | 49.4 | 72 | 48.3
2625.1 | 2386.1 | 58.9 | 252.3 | 49.4 | 71.9 | 47.9
2626.1 | 2387.1 | 58.7 | 252.2 | 49.4 | 71.8 | 48.3
2627.1 | 2388.1 | 58.7 | 252.5 | 49.3 | 71.7 | 48.3
2628.1 | 2389.1 | 58.7 | 252.8 | 49.1 | 71.6 | 48
2629.1 | 2390.1 | 58.5 | 253.2 | 49 | 71.6 | 48.2
2630.1 | 2391.1 | 58.3 | 253.7 | 49 | 71.6 | 48.1
2631.1 | 2392.1 | 58.2 | 254.3 | 48.5 | 71.5 | 47.7
2632.1 | 2393.1 | 58.2 | 254.6 | 49 | 71.4 | 47.8
2633.1 | 2394.1 | 58.2 | 254.2 | 48.9 | 71.3 | 47.8
2634.1 | 2395.1 | 58.1 | 252.1 | 49.1 | 71.4 | 47.9
2635.1 | 2396.1 | 58.1 | 249.8 | 49 | 71.3 | 48
2636.1 | 2397.1 | 58.1 | 248.3 | 48.6 | 71.2 | 48.2
2637.1 | 2398.1 | 57.9 | 247.2 | 48.2 | 71.2 | 47.5
2638.1 | 2399.1 | 57.8 | 246.3 | 48 | 71.1 | 47.5
2639.1 | 2400.1 | 57.9 | 245.7 | 48.1 | 70.8 | 47.4
2640.1 | 2401.1 | 57.9 | 245.4 | 48 | 70.7 | 47.1
2641.1 | 2402.1 | 57.8 | 245.3 | 47.8 | 70.7 | 47.3
2642.1 | 2403.1 | 57.6 | 245.4 | 48.2 | 70.8 | 47.4
2643.1 | 2404.1 | 57.5 | 245.3 | 47.5 | 70.7 | 47.2
2644.1 | 2405.1 | 57.4 | 245.5 | 47.2 | 70.6 | 47.2
2645.1 | 2406.1 | 57.2 | 245.6 | 48 | 70.5 | 47.4
2646.1 | 2407.1 | 57.2 | 245.4 | 47.9 | 70.4 | 47.5
2647.1 | 2408.1 | 57.3 | 245.4 | 47 | 70.3 | 47.5
2648.1 | 2409.1 | 57.2 | 245.3 | 47.2 | 70.2 | 47.6
2649.1 | 2410.1 | 57.1 | 245.4 | 47.8 | 70 | 47.4
2650.1 | 2411.1 | 57 | 245.6 | 47.7 | 70.2 | 47.5
2651.1 | 2412.1 | 56.9 | 245.5 | 47.7 | 70.2 | 47.5
2652.1 | 2413.1 | 56.8 | 245.6 | 47.6 | 70.1 | 47.2
2653.1 | 2414.1 | 57 | 245.5 | 47.1 | 69.9 | 47.3
2654.1 | 2415.1 | 57 | 245.1 | 47.3 | 70 | 47.1
2655.1 | 2416.1 | 56.8 | 244.6 | 47.7 | 70 | 46.4
2656.1 | 2417.1 | 56.5 | 244.1 | 48.2 | 70 | 46.5
2657.1 | 2418.1 | 56.5 | 244.2 | 49.6 | 70 | 46.7
2658.1 | 2419.1 | 56.5 | 244.9 | 49.8 | 70 | 46.7
2659.1 | 2420.1 | 56.5 | 245.9 | 49.4 | 69.9 | 46.5
2660.1 | 2421.1 | 56.3 | 246.4 | 49.2 | 69.8 | 46.3
2661.1 | 2422.1 | 56.1 | 247.1 | 48.9 | 69.8 | 46.6
2662.1 | 2423.1 | 56.2 | 248 | 48.4 | 69.7 | 46.8
2663.1 | 2424.1 | 56.3 | 248.5 | 48 | 69.5 | 46.6
2664.1 | 2425.1 | 56.2 | 249.1 | 47.8 | 69.4 | 46.4
2665.1 | 2426.1 | 56.2 | 249.7 | 48.1 | 69.5 | 46.4
2666.1 | 2427.1 | 56.1 | 250.3 | 48.7 | 69.4 | 46.6
2667.1 | 2428.1 | 56 | 250.6 | 47.7 | 69.4 | 46.5
2668.1 | 2429.1 | 56 | 250.6 | 47.6 | 69.3 | 46.2
2669.1 | 2430.1 | 55.9 | 250.7 | 48.3 | 69.1 | 46.9
2670.1 | 2431.1 | 55.7 | 250.8 | 47.8 | 69.1 | 47
2671.1 | 2432.1 | 55.7 | 250.6 | 47.5 | 69 | 46.7
2672.1 | 2433.1 | 55.7 | 250.6 | 47.1 | 69 | 46.3
2673.1 | 2434.1 | 55.7 | 250.6 | 46.9 | 68.8 | 46.5
2674.1 | 2435.1 | 55.6 | 250.5 | 46.4 | 68.9 | 46.5
2675.1 | 2436.1 | 55.4 | 250.4 | 46.5 | 68.8 | 46.4
2676.1 | 2437.1 | 55.3 | 250.5 | 47 | 68.8 | 45.9
2677.1 | 2438.1 | 55.3 | 250.3 | 47 | 68.7 | 46
2678.1 | 2439.1 | 55.3 | 250.1 | 47.7 | 68.6 | 46.6
2679.1 | 2440.1 | 55.1 | 249.8 | 47.3 | 68.6 | 47.1
2680.1 | 2441.1 | 55 | 249.4 | 46.8 | 68.6 | 47
2681.1 | 2442.1 | 54.9 | 249.4 | 47 | 68.5 | 46.9
2682.1 | 2443.1 | 54.8 | 249.6 | 47.4 | 68.3 | 47
2683.1 | 2444.1 | 54.6 | 249.7 | 47.8 | 68.3 | 47
2684.1 | 2445.1 | 54.6 | 249.8 | 47.7 | 68.2 | 46.8
2685.1 | 2446.1 | 54.6 | 249.5 | 48 | 68.1 | 46.1
2686.1 | 2447.1 | 54.5 | 248.8 | 47.2 | 68 | 46.1
2687.1 | 2448.1 | 54.4 | 248.3 | 47.1 | 67.9 | 46.4
2688.1 | 2449.1 | 54.4 | 248 | 47.2 | 67.7 | 46.4
2689.1 | 2450.1 | 54.5 | 247.7 | 47.2 | 67.7 | 46.4
2690.1 | 2451.1 | 54.4 | 247.6 | 47 | 67.6 | 46.3
2691.1 | 2452.1 | 54.3 | 247.3 | 46.7 | 67.6 | 45.9
2692.1 | 2453.1 | 54.3 | 247.1 | 46.9 | 67.6 | 45.6
2693.1 | 2454.1 | 54.2 | 247 | 46.7 | 67.4 | 45.8
2694.1 | 2455.1 | 54.1 | 246.9 | 46.8 | 67.5 | 46.1
2695.1 | 2456.1 | 54.1 | 247.1 | 46.4 | 67.4 | 46.2
2696.1 | 2457.1 | 54.1 | 247.2 | 46.5 | 67.3 | 46.2
2697.1 | 2458.1 | 54 | 247.2 | 46.6 | 67.4 | 45.6
2698.1 | 2459.1 | 54 | 247.4 | 46.8 | 67.3 | 45.5
2699.1 | 2460.1 | 54 | 247.5 | 46.4 | 67 | 45.6
2700.1 | 2461.1 | 53.9 | 247.5 | 46.2 | 67.1 | 45.6
2701.1 | 2462.1 | 53.8 | 247.3 | 46.9 | 67.1 | 45.7
2702.1 | 2463.1 | 53.9 | 247.4 | 46.9 | 67.1 | 45.3
2703.1 | 2464.1 | 53.8 | 247.4 | 46.2 | 67.1 | 45.5
2704.1 | 2465.1 | 53.8 | 247.4 | 46 | 67.1 | 45.9
2705.1 | 2466.1 | 53.8 | 247 | 45.8 | 67 | 46
2706.1 | 2467.1 | 53.7 | 246.8 | 46.2 | 67 | 45.6
2707.1 | 2468.1 | 53.6 | 246.8 | 46.3 | 66.9 | 45.5
2708.1 | 2469.1 | 53.6 | 246.8 | 45.8 | 66.9 | 45.6
2709.1 | 2470.1 | 53.5 | 246.5 | 45.8 | 66.8 | 45.6
2710.1 | 2471.1 | 53.5 | 246.4 | 46.4 | 66.5 | 45.2
2711.1 | 2472.1 | 53.5 | 246.3 | 45.9 | 66.4 | 45.3
2712.1 | 2473.1 | 53.4 | 246 | 46 | 66.5 | 45.6
2713.1 | 2474.1 | 53.3 | 245.5 | 46.1 | 66.3 | 45.4
2714.1 | 2475.1 | 53.3 | 244.7 | 46.7 | 66.3 | 44.9
2715.1 | 2476.1 | 53.2 | 244.1 | 45.7 | 66.3 | 45.5
2716.1 | 2477.1 | 53.1 | 243.7 | 45.6 | 66.5 | 45.6
2717.1 | 2478.1 | 53.1 | 243.2 | 45.4 | 66.5 | 45.3
2718.1 | 2479.1 | 52.9 | 243 | 45.8 | 66.6 | 44.7
2719.1 | 2480.1 | 52.8 | 242.8 | 45.4 | 66.4 | 44.5
2720.1 | 2481.1 | 52.7 | 243 | 45.7 | 66.5 | 44.6
2721.1 | 2482.1 | 52.7 | 243.2 | 45.2 | 66.3 | 44.1
2722.1 | 2483.1 | 52.8 | 243.1 | 45.7 | 66.2 | 44.3
2723.1 | 2484.1 | 52.8 | 243.1 | 45 | 66.2 | 44.2
2724.1 | 2485.1 | 52.8 | 242.9 | 44.9 | 66 | 44.1
2725.1 | 2486.1 | 52.8 | 242.8 | 44.8 | 65.7 | 44
2726.1 | 2487.1 | 52.7 | 242.8 | 44.9 | 65.8 | 44.2
2727.1 | 2488.1 | 52.7 | 242.7 | 44.9 | 65.8 | 44.3
2728.1 | 2489.1 | 52.6 | 242.6 | 45.3 | 65.8 | 43.8
2729.1 | 2490.1 | 52.5 | 242.7 | 45.1 | 65.8 | 44
2730.1 | 2491.1 | 52.6 | 242.6 | 44.3 | 65.7 | 44.1
2731.1 | 2492.1 | 52.5 | 242.2 | 44.2 | 65.8 | 44.3
2732.1 | 2493.1 | 52.3 | 241.9 | 45.2 | 65.6 | 44.2
2733.1 | 2494.1 | 52.2 | 241.7 | 44.9 | 65.6 | 44.2
2734.1 | 2495.1 | 52.1 | 241.6 | 45.1 | 65.4 | 43.8
2735.1 | 2496.1 | 52 | 241.6 | 45.6 | 65.5 | 43.8
2736.1 | 2497.1 | 52.1 | 241.5 | 44.8 | 65.4 | 43.9
2737.1 | 2498.1 | 51.9 | 241.4 | 44.6 | 65.4 | 44.3
2738.1 | 2499.1 | 51.9 | 241.3 | 44.5 | 65.4 | 44.1
2739.1 | 2500.1 | 51.9 | 241.2 | 44.9 | 65.4 | 43.6
2740.1 | 2501.1 | 51.7 | 240.9 | 44.7 | 65.3 | 43.7
2741.1 | 2502.1 | 51.7 | 240.5 | 44 | 65.2 | 43.9
2742.1 | 2503.1 | 51.8 | 240 | 44.4 | 65.1 | 44.5
2743.1 | 2504.1 | 51.8 | 239.5 | 44 | 65 | 44.1
2744.1 | 2505.1 | 51.8 | 239.1 | 43.8 | 65 | 44
2745.1 | 2506.1 | 51.8 | 238.8 | 43.8 | 65 | 43.9
2746.1 | 2507.1 | 51.8 | 238.6 | 43.3 | 65 | 44.1
2747.1 | 2508.1 | 51.5 | 238.4 | 43.5 | 65.1 | 44.2
2748.1 | 2509.1 | 51.4 | 238.2 | 43.2 | 65.1 | 43.9
2749.1 | 2510.1 | 51.3 | 237.9 | 43.3 | 65.1 | 43.7
2750.1 | 2511.1 | 51.2 | 237.5 | 42.7 | 65.1 | 43.7
2751.1 | 2512.1 | 51.1 | 236.6 | 43.1 | 65 | 44.1
2752.1 | 2513.1 | 51.1 | 235.8 | 43 | 65 | 43.8
2753.1 | 2514.1 | 51.1 | 235.5 | 43.1 | 64.9 | 43.5
2754.1 | 2515.1 | 51.1 | 235.2 | 43.2 | 64.8 | 43.1
2755.1 | 2516.1 | 51 | 235.2 | 42.9 | 64.8 | 43.7
2756.1 | 2517.1 | 50.9 | 235.1 | 43.1 | 64.8 | 44.2
2757.1 | 2518.1 | 50.9 | 235.2 | 43.3 | 64.7 | 44.1
2758.1 | 2519.1 | 51 | 235.2 | 42.9 | 64.6 | 43.5
2759.1 | 2520.1 | 51 | 235.6 | 42.7 | 64.5 | 43.4
2760.1 | 2521.1 | 50.9 | 236 | 43.1 | 64.4 | 43.8
2761.1 | 2522.1 | 50.9 | 236.1 | 42.9 | 64.3 | 44.1
2762.1 | 2523.1 | 50.7 | 236.3 | 43 | 64.3 | 44.5
2763.1 | 2524.1 | 50.7 | 236.3 | 43.4 | 64.3 | 44.6
2764.1 | 2525.1 | 50.6 | 236.4 | 43.6 | 64.2 | 43.9
2765.1 | 2526.1 | 50.6 | 236.5 | 43.5 | 64.1 | 43.9
2766.1 | 2527.1 | 50.6 | 236.5 | 43.2 | 64 | 44.1
2767.1 | 2528.1 | 50.6 | 236.4 | 43.3 | 64 | 44.1
2768.1 | 2529.1 | 49.7 | 236.1 | 43.1 | 64 | 43.8
2769.1 | 2530.1 | 49.9 | 235.8 | 43.2 | 64 | 43.8
2770.1 | 2531.1 | 50.3 | 235.4 | 42.7 | 63.9 | 44.4
2771.1 | 2532.1 | 50.5 | 235.4 | 42.9 | 63.7 | 44.2
2772.1 | 2533.1 | 50.5 | 235.5 | 42.6 | 63.7 | 43.6
2773.1 | 2534.1 | 50.4 | 235.4 | 43 | 63.7 | 43.6
2774.1 | 2535.1 | 50.4 | 235.3 | 43.5 | 63.7 | 43.7
2775.1 | 2536.1 | 50.4 | 234.2 | 43.5 | 63.2 | 43.6
2776.1 | 2537.1 | 39.2 | 230.4 | 42.9 | 47.6 | 43.4
2777.1 | 2538.1 | 36.6 | 228.9 | 41.8 | 48 | 43.4
2778.1 | 2539.1 | 37.4 | 229 | 41.5 | 48.7 | 42.9
2779.1 | 2540.1 | 38.3 | 230.5 | 42 | 50.4 | 43.3
2780.1 | 2541.1 | 39 | 231.8 | 42.4 | 51.6 | 43.8
2781.1 | 2542.1 | 40.2 | 233.1 | 44 | 52.6 | 43.8
2782.1 | 2543.1 | 41.3 | 234.3 | 44.3 | 53.4 | 43.5
2783.1 | 2544.1 | 42.1 | 235.9 | 44.8 | 54.1 | 43.2
2784.1 | 2545.1 | 43.2 | 237.6 | 45.1 | 54.7 | 43.4
2785.1 | 2546.1 | 44 | 238.9 | 45.8 | 55.2 | 43.5
2786.1 | 2547.1 | 44.8 | 240.1 | 45.9 | 55.7 | 43.4
2787.1 | 2548.1 | 45.5 | 241.6 | 46.7 | 56.1 | 43.5
2788.1 | 2549.1 | 46.2 | 243.2 | 49.8 | 56.6 | 43.6
2789.1 | 2550.1 | 46.8 | 244.5 | 51.7 | 57.1 | 43.8
2790.1 | 2551.1 | 47.5 | 245.7 | 53.5 | 57.5 | 44.1
2791.1 | 2552.1 | 48.1 | 246.7 | 55.5 | 58 | 44.5
2792.1 | 2553.1 | 48.7 | 247.6 | 57.1 | 58.5 | 44.8
2793.1 | 2554.1 | 49.3 | 248.4 | 58.1 | 59.1 | 45.2
2794.1 | 2555.1 | 49.6 | 249.3 | 59 | 59.6 | 45.4
2795.1 | 2556.1 | 50.4 | 250.1 | 59.8 | 60.1 | 45.8
2796.1 | 2557.1 | 50.8 | 251 | 60.4 | 60.6 | 46.1
2797.1 | 2558.1 | 50.8 | 251.7 | 60.8 | 61 | 46.5
2798.1 | 2559.1 | 50.9 | 252.4 | 61.1 | 61.4 | 46.6
2799.1 | 2560.1 | 51.2 | 253.1 | 61.4 | 61.7 | 47.3
2800.1 | 2561.1 | 52.1 | 253.7 | 61.7 | 62 | 48.1
2801.1 | 2562.1 | 52.3 | 254.2 | 61.8 | 62.4 | 48.1
2802.1 | 2563.1 | 52.3 | 254.7 | 61.9 | 62.7 | 48.1
2803.1 | 2564.1 | 52.4 | 255.1 | 62.2 | 63 | 48.5
2804.1 | 2565.1 | 52.5 | 255.5 | 62.4 | 63.2 | 49
2805.1 | 2566.1 | 52.8 | 255.9 | 62.5 | 63.6 | 49.1
2806.1 | 2567.1 | 53.1 | 256.3 | 62.6 | 63.9 | 49.5
2807.1 | 2568.1 | 53.4 | 256.6 | 62.8 | 64.3 | 49.6
2808.1 | 2569.1 | 53.6 | 256.9 | 62.8 | 64.5 | 49.9
2809.1 | 2570.1 | 54.5 | 257.2 | 63 | 64.8 | 50.3
2810.1 | 2571.1 | 55.1 | 257.4 | 63 | 65 | 50.5
2811.1 | 2572.1 | 54.9 | 257.6 | 63.2 | 65.3 | 50.8
2812.1 | 2573.1 | 54.9 | 257.8 | 63.3 | 65.5 | 51.4
2813.1 | 2574.1 | 54.9 | 257.9 | 63.4 | 65.7 | 51.7
2814.1 | 2575.1 | 54.9 | 258.2 | 63.6 | 65.8 | 51.8
2815.1 | 2576.1 | 55.1 | 258.4 | 63.6 | 66 | 52
2816.1 | 2577.1 | 55.3 | 258.5 | 63.7 | 66.1 | 52.3
2817.1 | 2578.1 | 55.4 | 258.7 | 63.8 | 66.3 | 52.8
2818.1 | 2579.1 | 55.6 | 258.9 | 63.9 | 66.5 | 52.9
2819.1 | 2580.1 | 55.7 | 259 | 63.9 | 66.6 | 53.4
2820.1 | 2581.1 | 55.9 | 259.1 | 64 | 66.8 | 54
2821.1 | 2582.1 | 56.1 | 259.1 | 63.8 | 67 | 54.4
2822.1 | 2583.1 | 56.3 | 259.2 | 64 | 67.1 | 54.7
2823.1 | 2584.1 | 56.4 | 259.3 | 63.8 | 67.3 | 54.8
2824.1 | 2585.1 | 56.6 | 259.4 | 64 | 67.4 | 55
2825.1 | 2586.1 | 56.8 | 259.4 | 64.2 | 67.6 | 55.3
2826.1 | 2587.1 | 57 | 259.3 | 64.4 | 67.8 | 55.7
2827.1 | 2588.1 | 57.1 | 259.3 | 64.5 | 67.9 | 55.9
2828.1 | 2589.1 | 57.2 | 259.2 | 64.5 | 68 | 56.1
2829.1 | 2590.1 | 57.4 | 259.3 | 64.6 | 68.2 | 56.2
2830.1 | 2591.1 | 57.5 | 259.3 | 64.6 | 68.2 | 56.6
2831.1 | 2592.1 | 57.6 | 259.4 | 64.7 | 68.4 | 56.8
2832.1 | 2593.1 | 57.8 | 259.4 | 64.5 | 68.4 | 57
2833.1 | 2594.1 | 57.9 | 259.4 | 64.4 | 68.5 | 57.4
2834.1 | 2595.1 | 58.1 | 259.4 | 64.6 | 68.6 | 57.7
2835.1 | 2596.1 | 58.2 | 259.4 | 64.9 | 68.7 | 58
2836.1 | 2597.1 | 58.3 | 259.3 | 64.8 | 68.7 | 58.3
2837.1 | 2598.1 | 58.5 | 259.3 | 64.9 | 68.9 | 58.5
2838.1 | 2599.1 | 58.6 | 259.2 | 64.9 | 68.9 | 58.6
2839.1 | 2600.1 | 58.7 | 259.1 | 65 | 69 | 58.6
2840.1 | 2601.1 | 58.8 | 259.1 | 65 | 69.1 | 58.8
2841.1 | 2602.1 | 58.9 | 259.1 | 65 | 69.2 | 59.1
2842.1 | 2603.1 | 59.1 | 259 | 65.2 | 69.3 | 59.5
2843.1 | 2604.1 | 59.3 | 259 | 65.3 | 69.4 | 59.7
2844.1 | 2605.1 | 59.4 | 258.9 | 65.3 | 69.5 | 59.9
2845.1 | 2606.1 | 59.5 | 259 | 65.2 | 69.7 | 59.9
2846.1 | 2607.1 | 59.7 | 259 | 65.4 | 69.8 | 60.1
2847.1 | 2608.1 | 59.7 | 258.9 | 65.4 | 69.9 | 60.4
2848.1 | 2609.1 | 59.9 | 258.9 | 65.4 | 70 | 60.6
2849.1 | 2610.1 | 60 | 258.8 | 65.3 | 70 | 60.8
2850.1 | 2611.1 | 60.1 | 258.9 | 65.4 | 70.1 | 61
2851.1 | 2612.1 | 60.2 | 258.9 | 65.3 | 70.1 | 61.2
2852.1 | 2613.1 | 60.3 | 258.8 | 65.1 | 70.2 | 61.4
2853.1 | 2614.1 | 60.4 | 258.8 | 65 | 70.2 | 61.6
2854.1 | 2615.1 | 60.5 | 258.8 | 65.1 | 70.3 | 61.7
2855.1 | 2616.1 | 60.6 | 258.7 | 65.3 | 70.4 | 61.9
2856.1 | 2617.1 | 60.7 | 258.7 | 65.3 | 70.4 | 62
2857.1 | 2618.1 | 60.8 | 258.6 | 65.3 | 70.4 | 62.3
2858.1 | 2619.1 | 61 | 258.6 | 65.7 | 70.5 | 62.4
2859.1 | 2620.1 | 61.2 | 258.5 | 65.7 | 70.6 | 62.5
2860.1 | 2621.1 | 61.2 | 258.5 | 65.6 | 70.7 | 62.7
2861.1 | 2622.1 | 61.3 | 258.3 | 65.2 | 70.7 | 62.8
2862.1 | 2623.1 | 61.4 | 258.3 | 64.7 | 70.8 | 62.7
2863.1 | 2624.1 | 61.5 | 258.3 | 64.9 | 70.9 | 62.6
2864.1 | 2625.1 | 61.6 | 258.3 | 65.5 | 70.9 | 62.8
2865.1 | 2626.1 | 61.6 | 258.2 | 65.5 | 70.9 | 63
2866.1 | 2627.1 | 61.7 | 258.1 | 65.7 | 70.9 | 63.1
2867.1 | 2628.1 | 61.8 | 258.1 | 65.8 | 71 | 63.3
2868.1 | 2629.1 | 61.9 | 258 | 65.8 | 71 | 63.4
2869.1 | 2630.1 | 62 | 257.8 | 65.8 | 71 | 63.5
2870.1 | 2631.1 | 62 | 257.6 | 65.8 | 71 | 63.7
2871.1 | 2632.1 | 62.1 | 257.4 | 65.5 | 71 | 63.9
2872.1 | 2633.1 | 62.2 | 257.4 | 65.7 | 71 | 64
2873.1 | 2634.1 | 62.3 | 257.2 | 65.8 | 71.1 | 64.1
2874.1 | 2635.1 | 62.3 | 257 | 66 | 71.1 | 64.3
2875.1 | 2636.1 | 62.4 | 256.9 | 66 | 71.1 | 64.3
2876.1 | 2637.1 | 62.5 | 256.9 | 66 | 71.1 | 64.3
2877.1 | 2638.1 | 62.6 | 256.7 | 66 | 71.1 | 64.4
2878.1 | 2639.1 | 62.7 | 256.7 | 65.9 | 71.1 | 64.4
2879.1 | 2640.1 | 62.8 | 256.6 | 65.7 | 71.1 | 64.5
2880.1 | 2641.1 | 62.9 | 256.4 | 65.8 | 71.2 | 64.6
2881.1 | 2642.1 | 63 | 256.2 | 65.5 | 71.2 | 64.7
2882.1 | 2643.1 | 63.1 | 256.1 | 65.6 | 71.3 | 64.8
2883.1 | 2644.1 | 63.2 | 255.9 | 65.6 | 71.3 | 65
2884.1 | 2645.1 | 63.3 | 255.8 | 65.7 | 71.4 | 65.2
2885.1 | 2646.1 | 63.4 | 255.8 | 65.7 | 71.4 | 65.2
2886.1 | 2647.1 | 63.5 | 255.5 | 65.5 | 71.5 | 65.3
2887.1 | 2648.1 | 63.6 | 255.2 | 65.7 | 71.6 | 65.4
2888.1 | 2649.1 | 63.6 | 255.2 | 65.8 | 71.6 | 65.5
2889.1 | 2650.1 | 63.7 | 255.2 | 65.8 | 71.6 | 65.6
2890.1 | 2651.1 | 63.8 | 255.2 | 66 | 71.7 | 65.7
2891.1 | 2652.1 | 63.9 | 255.2 | 65.7 | 71.8 | 65.6
2892.1 | 2653.1 | 63.9 | 255.2 | 65.4 | 71.8 | 65.7
2893.1 | 2654.1 | 64 | 255.3 | 65.1 | 71.8 | 65.7
2894.1 | 2655.1 | 64.1 | 255.1 | 64.7 | 71.8 | 65.7
2895.1 | 2656.1 | 64.2 | 254.9 | 65 | 71.8 | 65.9
2896.1 | 2657.1 | 64.3 | 254.8 | 65.1 | 71.9 | 66
2897.1 | 2658.1 | 64.4 | 254.6 | 65.7 | 72 | 66.1
2898.1 | 2659.1 | 64.4 | 254.6 | 66 | 72 | 66.1
2899.1 | 2660.1 | 64.5 | 254.6 | 66.1 | 72.1 | 66.2
2900.1 | 2661.1 | 64.5 | 254.5 | 66.2 | 72.1 | 66.3
2901.1 | 2662.1 | 64.6 | 254.4 | 66.5 | 72.1 | 66.5
2902.1 | 2663.1 | 64.6 | 254.2 | 66.4 | 72.1 | 66.5
2903.1 | 2664.1 | 64.7 | 254.2 | 66.3 | 72 | 66.4
2904.1 | 2665.1 | 64.7 | 254 | 66.6 | 72 | 66.4
2905.1 | 2666.1 | 64.8 | 254 | 66.5 | 71.9 | 66.4
2906.1 | 2667.1 | 64.8 | 253.9 | 66.7 | 71.9 | 66.4
2907.1 | 2668.1 | 64.8 | 253.8 | 66.6 | 71.9 | 66.5
2908.1 | 2669.1 | 64.8 | 253.7 | 66.5 | 71.8 | 66.7
2909.1 | 2670.1 | 64.8 | 253.5 | 66.5 | 71.8 | 66.8
2910.1 | 2671.1 | 64.9 | 253.4 | 66.5 | 71.7 | 66.9
2911.1 | 2672.1 | 64.9 | 253.2 | 66.3 | 71.7 | 66.8
2912.1 | 2673.1 | 64.9 | 253.2 | 66.3 | 71.6 | 66.8
2913.1 | 2674.1 | 65 | 253.1 | 66.3 | 71.7 | 66.9
2914.1 | 2675.1 | 65 | 252.9 | 65.9 | 71.7 | 67.1
2915.1 | 2676.1 | 65 | 252.7 | 65.5 | 71.7 | 67
2916.1 | 2677.1 | 65.1 | 252.7 | 65.6 | 71.7 | 67
2917.1 | 2678.1 | 65.2 | 252.6 | 65.9 | 71.7 | 67.1
2918.1 | 2679.1 | 65.2 | 252.6 | 66.1 | 71.7 | 67.2
2919.1 | 2680.1 | 65.3 | 252.6 | 66.2 | 71.7 | 67.3
2920.1 | 2681.1 | 65.3 | 252.6 | 66.3 | 71.8 | 67.3
2921.1 | 2682.1 | 65.4 | 252.4 | 66 | 71.9 | 67.3
2922.1 | 2683.1 | 65.4 | 252.4 | 65.7 | 72 | 67.2
2923.1 | 2684.1 | 65.4 | 252.5 | 65.5 | 72 | 67.2
2924.1 | 2685.1 | 65.4 | 252.5 | 65.3 | 72 | 67.1
2925.1 | 2686.1 | 65.5 | 252.4 | 65.6 | 71.9 | 67.3
2926.1 | 2687.1 | 65.5 | 252.2 | 65.1 | 71.9 | 67.4
2927.1 | 2688.1 | 65.5 | 252.3 | 65.6 | 72 | 67.4
2928.1 | 2689.1 | 65.5 | 252.3 | 65.9 | 72 | 67.4
2929.1 | 2690.1 | 65.5 | 252.3 | 65.8 | 72 | 67.3
2930.1 | 2691.1 | 65.6 | 252.2 | 65.7 | 72 | 67.3
2931.1 | 2692.1 | 65.6 | 252.1 | 66.1 | 72 | 67.3
2932.1 | 2693.1 | 65.6 | 252 | 66.2 | 72 | 67.5
2933.1 | 2694.1 | 65.7 | 251.9 | 65.9 | 72 | 67.6
2934.1 | 2695.1 | 65.7 | 251.7 | 65.9 | 72.1 | 67.7
2935.1 | 2696.1 | 65.7 | 251.7 | 66.2 | 72.1 | 67.6
2936.1 | 2697.1 | 65.7 | 251.8 | 66.4 | 72.2 | 67.7
2937.1 | 2698.1 | 65.8 | 251.7 | 66.5 | 72.3 | 67.7
2938.1 | 2699.1 | 65.8 | 251.5 | 66.5 | 72.3 | 67.9
2939.1 | 2700.1 | 65.8 | 251.5 | 66.2 | 72.3 | 68
2940.1 | 2701.1 | 65.8 | 251.4 | 66.3 | 72.3 | 68.1
2941.1 | 2702.1 | 65.8 | 251.4 | 66.4 | 72.4 | 68.1
2942.1 | 2703.1 | 65.8 | 251.2 | 66.6 | 72.5 | 68.1
2943.1 | 2704.1 | 65.8 | 251 | 66.7 | 72.6 | 68.1
2944.1 | 2705.1 | 65.8 | 250.8 | 66.5 | 72.6 | 68.2
2945.1 | 2706.1 | 65.8 | 250.8 | 66.6 | 72.6 | 68.3
2946.1 | 2707.1 | 65.8 | 250.6 | 66.6 | 72.7 | 68.3
2947.1 | 2708.1 | 65.8 | 250.6 | 65.9 | 72.8 | 68.2
2948.1 | 2709.1 | 65.8 | 250.6 | 65.9 | 72.8 | 67.9
2949.1 | 2710.1 | 65.8 | 250.4 | 66.3 | 72.8 | 68
2950.1 | 2711.1 | 65.8 | 250.3 | 66 | 72.9 | 68.1
2951.1 | 2712.1 | 65.9 | 250.3 | 66.2 | 73 | 68.3
2952.1 | 2713.1 | 65.9 | 250.1 | 66.4 | 73.1 | 68.2
2953.1 | 2714.1 | 65.8 | 249.9 | 66.4 | 73.1 | 68.3
2954.1 | 2715.1 | 65.7 | 249.9 | 66.2 | 73.1 | 68.2
2955.1 | 2716.1 | 65.7 | 249.7 | 66 | 73 | 68.3
2956.1 | 2717.1 | 65.7 | 249.5 | 65.9 | 72.9 | 68.3
2957.1 | 2718.1 | 65.7 | 249.5 | 65.5 | 73 | 68.3
2958.1 | 2719.1 | 65.8 | 249.4 | 65.2 | 73 | 68.1
2959.1 | 2720.1 | 65.8 | 249.2 | 65.4 | 73 | 68.1
2960.1 | 2721.1 | 65.7 | 249.1 | 65.5 | 73 | 68.1
2961.1 | 2722.1 | 65.7 | 249.1 | 65 | 72.9 | 67.9
2962.1 | 2723.1 | 65.7 | 249 | 64.5 | 72.9 | 68
2963.1 | 2724.1 | 65.7 | 248.9 | 64.3 | 72.8 | 67.9
2964.1 | 2725.1 | 65.7 | 248.9 | 64.1 | 72.8 | 68
2965.1 | 2726.1 | 65.7 | 249.1 | 64.7 | 72.8 | 68.1
2966.1 | 2727.1 | 65.7 | 249.1 | 64.7 | 72.8 | 68.3
2967.1 | 2728.1 | 65.7 | 249.1 | 65.4 | 72.9 | 68.4
2968.1 | 2729.1 | 65.7 | 249 | 65.9 | 72.9 | 68.2
2969.1 | 2730.1 | 65.6 | 248.7 | 65.4 | 72.8 | 68.2
2970.1 | 2731.1 | 65.6 | 248.6 | 65.7 | 72.7 | 68.1
2971.1 | 2732.1 | 65.6 | 248.4 | 65.8 | 72.8 | 68.3
2972.1 | 2733.1 | 65.6 | 248 | 65.6 | 73 | 68.4
2973.1 | 2734.1 | 65.7 | 248.1 | 65.4 | 73.1 | 68.4
2974.1 | 2735.1 | 65.7 | 248 | 65 | 73 | 68.2
2975.1 | 2736.1 | 65.6 | 248.1 | 65 | 73 | 68.2
2976.1 | 2737.1 | 65.7 | 248 | 65.6 | 73.1 | 68.1
2977.1 | 2738.1 | 65.7 | 247.9 | 65.6 | 73.1 | 68
2978.1 | 2739.1 | 65.7 | 248 | 65.5 | 73 | 68.1
2979.1 | 2740.1 | 65.7 | 248.1 | 65.4 | 72.8 | 68
2980.1 | 2741.1 | 65.7 | 248.1 | 65.5 | 72.8 | 68
2981.1 | 2742.1 | 65.7 | 248.1 | 65.6 | 72.7 | 68.1
2982.1 | 2743.1 | 65.7 | 247.9 | 65.7 | 72.8 | 68.1
2983.1 | 2744.1 | 65.7 | 247.9 | 65.6 | 72.9 | 68.2
2984.1 | 2745.1 | 65.7 | 247.5 | 65.4 | 72.9 | 68.2
2985.1 | 2746.1 | 65.7 | 247.4 | 65.2 | 72.8 | 68.3
2986.1 | 2747.1 | 65.7 | 247.4 | 65 | 72.8 | 68.4
2987.1 | 2748.1 | 65.6 | 247.4 | 65 | 72.6 | 68.4
2988.1 | 2749.1 | 65.7 | 247 | 65.3 | 72.6 | 68.4
2989.1 | 2750.1 | 65.8 | 246.8 | 65.2 | 72.6 | 68.4
2990.1 | 2751.1 | 65.8 | 247 | 65.1 | 72.5 | 68.4
2991.1 | 2752.1 | 65.8 | 247 | 64.4 | 72.4 | 68.5
2992.1 | 2753.1 | 65.9 | 247 | 64.4 | 72.5 | 68.2
2993.1 | 2754.1 | 65.9 | 247.1 | 63.8 | 72.5 | 68.2
2994.1 | 2755.1 | 65.9 | 247.2 | 63.4 | 72.7 | 68.4
2995.1 | 2756.1 | 65.9 | 247.3 | 63.8 | 72.8 | 68.3
2996.1 | 2757.1 | 66.1 | 247.2 | 64 | 73 | 68.1
2997.1 | 2758.1 | 66 | 247.2 | 63.9 | 73.1 | 68.2
2998.1 | 2759.1 | 66 | 247 | 63.4 | 73.1 | 68.1
2999.1 | 2760.1 | 66 | 247.1 | 63.2 | 73.1 | 68
3000.1 | 2761.1 | 66 | 247.2 | 63.1 | 73.1 | 68.2
3001.1 | 2762.1 | 65.9 | 247.1 | 64.1 | 73.1 | 68.2
3002.1 | 2763.1 | 65.9 | 246.9 | 63.9 | 72.9 | 68.2
3003.1 | 2764.1 | 65.9 | 246.8 | 64.5 | 72.8 | 68.1
3004.1 | 2765.1 | 65.9 | 246.8 | 65 | 72.8 | 68
3005.1 | 2766.1 | 65.9 | 246.6 | 65.3 | 72.7 | 67.9
3006.1 | 2767.1 | 65.9 | 246.4 | 64.2 | 72.7 | 68.1
3007.1 | 2768.1 | 65.9 | 246.4 | 63.9 | 72.7 | 68.2
3008.1 | 2769.1 | 65.9 | 246.3 | 64.1 | 72.6 | 68.3
3009.1 | 2770.1 | 65.9 | 246 | 64.5 | 72.4 | 68.1
3010.1 | 2771.1 | 65.9 | 246 | 64.4 | 72.3 | 68.1
3011.1 | 2772.1 | 65.9 | 245.7 | 64.1 | 72.3 | 68.1
3012.1 | 2773.1 | 66 | 245.7 | 64.3 | 72.4 | 68.3
3013.1 | 2774.1 | 66 | 245.7 | 64.5 | 72.5 | 68.4
3014.1 | 2775.1 | 66 | 245.9 | 64.2 | 72.4 | 68.4
3015.1 | 2776.1 | 66 | 245.8 | 64.3 | 72.5 | 68.4
3016.1 | 2777.1 | 66 | 245.9 | 63.8 | 72.6 | 68.5
3017.1 | 2778.1 | 66 | 245.7 | 63.8 | 72.6 | 68.3
3018.1 | 2779.1 | 66 | 245.3 | 63.5 | 72.6 | 68.1
3019.1 | 2780.1 | 65.9 | 245.2 | 62.8 | 72.6 | 68
3020.1 | 2781.1 | 65.9 | 245 | 62.7 | 72.5 | 68
3021.1 | 2782.1 | 65.8 | 244.9 | 63.1 | 72.4 | 68.1
3022.1 | 2783.1 | 65.8 | 244.7 | 63.6 | 72.4 | 68.2
3023.1 | 2784.1 | 65.9 | 244.7 | 64.4 | 72.4 | 68.1
3024.1 | 2785.1 | 65.9 | 244.7 | 64.5 | 72.5 | 68.2
3025.1 | 2786.1 | 65.9 | 244.7 | 65.1 | 72.5 | 68.4
3026.1 | 2787.1 | 65.9 | 244.6 | 64.9 | 72.5 | 68.5
3027.1 | 2788.1 | 65.9 | 244.8 | 65 | 72.5 | 68.4
3028.1 | 2789.1 | 66 | 244.8 | 63.5 | 72.5 | 68.3
3029.1 | 2790.1 | 66 | 244.4 | 63.1 | 72.5 | 68.2
3030.1 | 2791.1 | 66 | 244.6 | 62.9 | 72.7 | 68.2
3031.1 | 2792.1 | 66 | 244.6 | 62.4 | 72.8 | 68.4
3032.1 | 2793.1 | 66 | 244.6 | 62 | 72.8 | 68.1
3033.1 | 2794.1 | 66 | 244.5 | 62.4 | 72.8 | 67.9
3034.1 | 2795.1 | 65.9 | 244.5 | 62 | 72.6 | 68
3035.1 | 2796.1 | 66 | 244.3 | 61.6 | 72.6 | 68.2
3036.1 | 2797.1 | 65.9 | 244.4 | 62.2 | 72.5 | 68.1
3037.1 | 2798.1 | 65.8 | 244.1 | 62.9 | 72.3 | 68.1
3038.1 | 2799.1 | 65.9 | 244.3 | 62.2 | 72.3 | 68.3
3039.1 | 2800.1 | 66 | 244.1 | 61.9 | 72.4 | 68.3
3040.1 | 2801.1 | 66 | 244.1 | 61.7 | 72.4 | 68.1
3041.1 | 2802.1 | 65.9 | 244 | 62.3 | 72.4 | 68
3042.1 | 2803.1 | 66 | 243.8 | 62.8 | 72.4 | 68.1
3043.1 | 2804.1 | 65.9 | 243.8 | 63.2 | 72.4 | 68.3
3044.1 | 2805.1 | 66 | 243.7 | 62.9 | 72.5 | 68.4
3045.1 | 2806.1 | 66 | 243.3 | 62.5 | 72.6 | 68.4
3046.1 | 2807.1 | 66 | 243.5 | 63.1 | 72.5 | 68.3
3047.1 | 2808.1 | 65.9 | 243.5 | 63.1 | 72.3 | 68.3
3048.1 | 2809.1 | 65.9 | 243.4 | 62.6 | 72.2 | 68.2
3049.1 | 2810.1 | 65.9 | 243.2 | 61.8 | 72.1 | 68.1
3050.1 | 2811.1 | 65.9 | 243 | 61.3 | 72.1 | 68
3051.1 | 2812.1 | 65.9 | 243.1 | 61.4 | 72.2 | 68
3052.1 | 2813.1 | 65.8 | 243 | 62.7 | 72.1 | 68.3
3053.1 | 2814.1 | 65.8 | 242.9 | 63.6 | 71.9 | 68.1
3054.1 | 2815.1 | 65.8 | 242.9 | 64 | 71.9 | 67.9
3055.1 | 2816.1 | 65.8 | 242.7 | 63.9 | 71.7 | 68.1
3056.1 | 2817.1 | 65.8 | 242.5 | 63.9 | 71.6 | 68.2
3057.1 | 2818.1 | 65.8 | 242.4 | 63.9 | 71.8 | 68.2
3058.1 | 2819.1 | 65.8 | 242 | 64.7 | 71.6 | 68.2
3059.1 | 2820.1 | 65.8 | 241.9 | 64.1 | 71.3 | 68.3
3060.1 | 2821.1 | 65.8 | 241.9 | 63.2 | 71.2 | 68.3
3061.1 | 2822.1 | 65.8 | 241.8 | 62.8 | 71.4 | 68.3
3062.1 | 2823.1 | 65.9 | 241.7 | 62.2 | 71.7 | 68.4
3063.1 | 2824.1 | 65.8 | 241.2 | 62.5 | 71.7 | 68.2
3064.1 | 2825.1 | 65.8 | 241.3 | 62.8 | 71.3 | 68
3065.1 | 2826.1 | 65.8 | 241.1 | 63 | 71.2 | 68.2
3066.1 | 2827.1 | 65.8 | 241.1 | 62.6 | 71.4 | 68.1
3067.1 | 2828.1 | 65.8 | 241 | 63.6 | 71.7 | 68
3068.1 | 2829.1 | 65.8 | 240.9 | 63.8 | 71.8 | 68.2
3069.1 | 2830.1 | 65.7 | 241.1 | 64.1 | 71.8 | 68.2
3070.1 | 2831.1 | 65.8 | 240.9 | 63.3 | 71.7 | 68.1
3071.1 | 2832.1 | 65.8 | 240.8 | 62.9 | 71.9 | 67.7
3072.1 | 2833.1 | 65.8 | 240.8 | 63 | 72 | 67.8
3073.1 | 2834.1 | 65.8 | 240.7 | 63.4 | 71.9 | 68
3074.1 | 2835.1 | 65.8 | 240.8 | 62.8 | 71.8 | 67.9
3075.1 | 2836.1 | 65.7 | 240.8 | 62.2 | 71.6 | 67.9
3076.1 | 2837.1 | 65.6 | 240.6 | 62 | 71.2 | 68.1
3077.1 | 2838.1 | 65.6 | 240.4 | 62.9 | 70.9 | 68.2
3078.1 | 2839.1 | 65.6 | 240.1 | 63.7 | 70.7 | 68.3
3079.1 | 2840.1 | 65.6 | 240 | 63.8 | 70.6 | 68.2
3080.1 | 2841.1 | 65.7 | 240 | 64.2 | 70.5 | 68.1
3081.1 | 2842.1 | 65.7 | 239.7 | 63 | 70.6 | 68.2
3082.1 | 2843.1 | 65.7 | 239.3 | 62.4 | 70.7 | 68.3
3083.1 | 2844.1 | 65.7 | 239.3 | 63 | 71 | 68.3
3084.1 | 2845.1 | 65.8 | 239.1 | 63.3 | 71.2 | 68.2
3085.1 | 2846.1 | 65.8 | 239.1 | 62.6 | 71.5 | 68.2
3086.1 | 2847.1 | 65.7 | 239.2 | 62 | 71.4 | 68.3
3087.1 | 2848.1 | 65.7 | 239.2 | 61.7 | 71.2 | 68.3
3088.1 | 2849.1 | 65.6 | 239.1 | 62 | 71.1 | 68.3
3089.1 | 2850.1 | 65.8 | 239.1 | 62.5 | 70.9 | 68.3
3090.1 | 2851.1 | 66.2 | 239 | 64.2 | 71 | 68.3
3091.1 | 2852.1 | 66.7 | 238.7 | 62.8 | 71.4 | 68.2
3092.1 | 2853.1 | 69.1 | 238.5 | 63.1 | 71.8 | 68.4
3093.1 | 2854.1 | 69.4 | 238.3 | 64.3 | 72.2 | 68.6
3094.1 | 2855.1 | 74.2 | 238.3 | 64.6 | 72.8 | 68.6
3095.1 | 2856.1 | 74.2 | 238.2 | 64.4 | 73.5 | 68.6
3096.1 | 2857.1 | 74.2 | 238.1 | 63.8 | 73.8 | 68.5
3097.1 | 2858.1 | 74.2 | 238.2 | 64.1 | 76.4 | 68.4
3098.1 | 2859.1 | 79 | 237.9 | 64.3 | 81.7 | 68.7
3099.1 | 2860.1 | 79.7 | 237.9 | 63.7 | 82.4 | 68.8
3100.1 | 2861.1 | 80.7 | 237.9 | 62.5 | 84.2 | 69
3101.1 | 2862.1 | 80.9 | 237.6 | 64.8 | 85.1 | 68.8
3102.1 | 2863.1 | 81 | 236.2 | 65 | 85.8 | 68.9
3103.1 | 2864.1 | 81.6 | 235.8 | 64.3 | 85.4 | 68.6
3104.1 | 2865.1 | 80.9 | 235.8 | 65.1 | 84.7 | 68.2
3105.1 | 2866.1 | 80.5 | 234 | 65.5 | 85 | 68.3
3106.1 | 2867.1 | 82.5 | 232.8 | 65.9 | 86.7 | 68.4
3107.1 | 2868.1 | 81.7 | 233 | 66.8 | 86.4 | 68.4
3108.1 | 2869.1 | 81.6 | 233.4 | 67.6 | 86.2 | 68.7
3109.1 | 2870.1 | 81.1 | 233.6 | 66 | 85.8 | 68.9
3110.1 | 2871.1 | 80.2 | 233.6 | 65.3 | 85.3 | 68.8
3111.1 | 2872.1 | 79.2 | 233.9 | 66.4 | 84.9 | 68.7
3112.1 | 2873.1 | 78.5 | 234 | 67.4 | 84.4 | 68.5
3113.1 | 2874.1 | 78.7 | 234.1 | 67.5 | 84 | 68.4
3114.1 | 2875.1 | 77.9 | 234.3 | 66.7 | 83.6 | 68.6
3115.1 | 2876.1 | 77.4 | 234.3 | 65.2 | 83.3 | 68.8
3116.1 | 2877.1 | 76.8 | 234.3 | 64.9 | 82.8 | 68.9
3117.1 | 2878.1 | 77 | 234.3 | 64.6 | 82.4 | 68.9
3118.1 | 2879.1 | 76.5 | 234.6 | 64.1 | 82.1 | 68.8
3119.1 | 2880.1 | 76.1 | 234.5 | 63.4 | 81.8 | 68.7
3120.1 | 2881.1 | 75.8 | 234.6 | 63 | 81.5 | 68.8
3121.1 | 2882.1 | 75.4 | 234.7 | 62.4 | 81.2 | 68.8
3122.1 | 2883.1 | 75.1 | 234.6 | 62.4 | 81 | 68.9
3123.1 | 2884.1 | 75 | 234.8 | 62.7 | 80.8 | 68.6
3124.1 | 2885.1 | 74.7 | 234.9 | 62 | 80.5 | 68.2
3125.1 | 2886.1 | 74.4 | 234.8 | 61.9 | 80.1 | 68.1
3126.1 | 2887.1 | 74.3 | 234.9 | 62.3 | 79.8 | 68.3
3127.1 | 2888.1 | 74.2 | 234.7 | 63.3 | 79.7 | 68.5
3128.1 | 2889.1 | 74 | 234.6 | 63.3 | 79.5 | 68.5
3129.1 | 2890.1 | 73.8 | 234.4 | 62.8 | 79.3 | 68.4
3130.1 | 2891.1 | 73.7 | 234.5 | 62.2 | 79.3 | 68.4
3131.1 | 2892.1 | 73.7 | 234.6 | 61.7 | 79.2 | 68.5
3132.1 | 2893.1 | 73.5 | 234.8 | 61.6 | 79.2 | 68.6
3133.1 | 2894.1 | 73.1 | 234.8 | 61.4 | 79 | 68.1
3134.1 | 2895.1 | 72.9 | 234.7 | 61.1 | 78.9 | 68.2
3135.1 | 2896.1 | 72.8 | 234.3 | 61 | 78.8 | 68
3136.1 | 2897.1 | 72.8 | 233.9 | 60.8 | 78.6 | 68.1
3137.1 | 2898.1 | 72.8 | 233.4 | 60.9 | 78.5 | 68.1
3138.1 | 2899.1 | 72.7 | 233.5 | 60.9 | 78.4 | 68.1
3139.1 | 2900.1 | 72.6 | 233.5 | 61.1 | 78.3 | 67.9
3140.1 | 2901.1 | 72.3 | 233.5 | 61.4 | 78.1 | 67.8
3141.1 | 2902.1 | 72.2 | 233.5 | 62.5 | 78 | 68.1
3142.1 | 2903.1 | 72 | 233.4 | 62.7 | 77.9 | 68.4
3143.1 | 2904.1 | 72 | 233.1 | 62.8 | 77.7 | 68.4
3144.1 | 2905.1 | 71.8 | 232.8 | 63.2 | 77.5 | 68.3
3145.1 | 2906.1 | 71.7 | 232.8 | 62.8 | 77.4 | 68.4
3146.1 | 2907.1 | 71.6 | 232.6 | 62.3 | 77.3 | 68.1
3147.1 | 2908.1 | 71.6 | 232.2 | 62.9 | 77.2 | 68.3
3148.1 | 2909.1 | 71.4 | 231.8 | 63.4 | 77.1 | 68.3
3149.1 | 2910.1 | 71.4 | 231.5 | 63.5 | 77.1 | 68.3
3150.1 | 2911.1 | 71.4 | 231.5 | 63.1 | 77.1 | 68
3151.1 | 2912.1 | 71.4 | 231.4 | 63.6 | 77.1 | 67.9
3152.1 | 2913.1 | 71.3 | 231.2 | 63.8 | 77.1 | 67.9
3153.1 | 2914.1 | 71.4 | 231.2 | 62.7 | 77.2 | 68
3154.1 | 2915.1 | 71.4 | 231.2 | 62.2 | 77.4 | 68.2
3155.1 | 2916.1 | 71.3 | 231.3 | 61.7 | 77.5 | 68.1
3156.1 | 2917.1 | 71.2 | 231.3 | 61.4 | 77.5 | 68.2
3157.1 | 2918.1 | 71.2 | 231.1 | 61.5 | 77.6 | 68.4
3158.1 | 2919.1 | 71.3 | 230.8 | 62.3 | 77.7 | 68.4
3159.1 | 2920.1 | 71.4 | 230.5 | 62.3 | 77.8 | 68.2
3160.1 | 2921.1 | 71.2 | 230.1 | 62.3 | 77.9 | 67.9
3161.1 | 2922.1 | 71.1 | 229.9 | 61.7 | 77.8 | 68
3162.1 | 2923.1 | 71 | 229.8 | 61.4 | 77.8 | 68
3163.1 | 2924.1 | 71.1 | 229.8 | 61.6 | 78 | 68.2
3164.1 | 2925.1 | 71 | 229.9 | 61 | 78.1 | 68.1
3165.1 | 2926.1 | 70.8 | 229.8 | 60.7 | 78.2 | 67.9
3166.1 | 2927.1 | 70.8 | 229.5 | 60.4 | 78.3 | 67.7
3167.1 | 2928.1 | 70.7 | 229 | 60.8 | 78.4 | 67.7
3168.1 | 2929.1 | 70.4 | 228.6 | 61.5 | 78.4 | 68
3169.1 | 2930.1 | 70.2 | 228.3 | 62 | 78.3 | 68
3170.1 | 2931.1 | 70.1 | 228.4 | 62.2 | 78.3 | 67.9
3171.1 | 2932.1 | 70 | 228.3 | 61.7 | 78.4 | 67.4
3172.1 | 2933.1 | 69.8 | 228.5 | 61.2 | 78.5 | 67.4
3173.1 | 2934.1 | 69.8 | 228.8 | 60.7 | 78.6 | 67.4
3174.1 | 2935.1 | 69.7 | 228.9 | 60.5 | 78.7 | 67.6
3175.1 | 2936.1 | 69.8 | 228.9 | 60.2 | 78.9 | 67.9
3176.1 | 2937.1 | 69.7 | 228.9 | 59.9 | 79 | 68
3177.1 | 2938.1 | 69.6 | 228.8 | 59.6 | 79.1 | 68
3178.1 | 2939.1 | 69.5 | 228.8 | 59.4 | 79.2 | 67.8
3179.1 | 2940.1 | 69.4 | 228.7 | 59.2 | 79.3 | 67.8
3180.1 | 2941.1 | 69.6 | 228.5 | 58.9 | 79.5 | 67.7
3181.1 | 2942.1 | 69.6 | 228.4 | 58.8 | 79.7 | 67.5
3182.1 | 2943.1 | 69.2 | 228.1 | 59.5 | 79.8 | 67.6
3183.1 | 2944.1 | 69.1 | 227.8 | 60.2 | 79.9 | 67.5
3184.1 | 2945.1 | 69.2 | 227.6 | 60.7 | 80 | 67.5
3185.1 | 2946.1 | 69.3 | 227.6 | 60.7 | 80.1 | 67.5
3186.1 | 2947.1 | 69.3 | 227.5 | 60.3 | 80.4 | 67.5
3187.1 | 2948.1 | 69.2 | 227.3 | 60.3 | 80.6 | 67.6
3188.1 | 2949.1 | 68.9 | 227.2 | 60.4 | 80.8 | 67.7
3189.1 | 2950.1 | 68.7 | 227.2 | 60.9 | 80.8 | 67.6
3190.1 | 2951.1 | 68.8 | 227.2 | 60.6 | 80.9 | 67.7
3191.1 | 2952.1 | 68.8 | 227.3 | 60.3 | 81 | 67.8
3192.1 | 2953.1 | 68.6 | 227.3 | 59.8 | 81.1 | 67.8
3193.1 | 2954.1 | 68.7 | 227.4 | 59.6 | 81.2 | 67.6
3194.1 | 2955.1 | 68.7 | 227.3 | 59.5 | 81.4 | 67.4
3195.1 | 2956.1 | 68.5 | 227.2 | 59.5 | 81.5 | 67.2
3196.1 | 2957.1 | 68.4 | 227.1 | 59.8 | 81.6 | 67.4
3197.1 | 2958.1 | 68.5 | 227 | 59.6 | 81.8 | 67.4
3198.1 | 2959.1 | 68.5 | 227 | 59.7 | 82 | 67.4
3199.1 | 2960.1 | 68.5 | 227.1 | 59.3 | 82.2 | 67.2
3200.1 | 2961.1 | 68.4 | 227.2 | 59.1 | 82.5 | 67.2
3201.1 | 2962.1 | 68.4 | 227.4 | 58.8 | 82.7 | 67.2
3202.1 | 2963.1 | 68.3 | 227.4 | 58.9 | 83.1 | 67.1
3203.1 | 2964.1 | 68.2 | 227.6 | 59 | 83.3 | 67.1
3204.1 | 2965.1 | 68.1 | 227.6 | 58.7 | 83.5 | 67.2
3205.1 | 2966.1 | 68 | 227.4 | 58.4 | 83.7 | 67.2
3206.1 | 2967.1 | 68.1 | 227.2 | 58.2 | 83.8 | 67.4
3207.1 | 2968.1 | 68.2 | 227 | 58.1 | 84 | 67.4
3208.1 | 2969.1 | 68.2 | 227 | 57.8 | 84.3 | 67.4
3209.1 | 2970.1 | 68.2 | 226.9 | 57.7 | 84.6 | 67.3
3210.1 | 2971.1 | 68.2 | 226.9 | 57.9 | 84.9 | 66.8
3211.1 | 2972.1 | 68.1 | 226.9 | 57.6 | 85.1 | 66.9
3212.1 | 2973.1 | 68.1 | 226.9 | 57.5 | 85.3 | 66.6
3213.1 | 2974.1 | 68.2 | 226.9 | 57.3 | 85.6 | 66.6
3214.1 | 2975.1 | 68.1 | 226.8 | 57.2 | 85.8 | 66.8
3215.1 | 2976.1 | 68 | 226.7 | 57.1 | 86.1 | 66.8
3216.1 | 2977.1 | 67.8 | 226.6 | 57.1 | 86.3 | 66.8
3217.1 | 2978.1 | 67.8 | 226.5 | 58.1 | 86.5 | 66.8
3218.1 | 2979.1 | 67.8 | 226.4 | 58 | 86.6 | 67
3219.1 | 2980.1 | 67.9 | 226.3 | 58 | 86.9 | 67.1
3220.1 | 2981.1 | 67.9 | 226 | 57.7 | 87.1 | 67
3221.1 | 2982.1 | 67.7 | 225.7 | 57.7 | 87.2 | 67
3222.1 | 2983.1 | 67.6 | 225.3 | 57.8 | 87.2 | 67
3223.1 | 2984.1 | 67.7 | 225 | 58.7 | 87.3 | 67.2
3224.1 | 2985.1 | 67.6 | 224.7 | 59.5 | 87.4 | 67.3
3225.1 | 2986.1 | 67.6 | 224.7 | 59.3 | 87.5 | 67.4
3226.1 | 2987.1 | 67.7 | 224.4 | 59.3 | 87.7 | 67.3
3227.1 | 2988.1 | 67.6 | 224.4 | 59.4 | 87.9 | 67.4
3228.1 | 2989.1 | 67.6 | 224.4 | 59.1 | 88.1 | 67.5
3229.1 | 2990.1 | 67.6 | 224.4 | 58.9 | 88.2 | 67.4
3230.1 | 2991.1 | 67.6 | 224.4 | 59 | 88.4 | 67.6
3231.1 | 2992.1 | 67.5 | 224.1 | 58.9 | 88.5 | 67.4
3232.1 | 2993.1 | 67.6 | 223.9 | 59 | 88.6 | 67.3
3233.1 | 2994.1 | 67.6 | 223.7 | 58.9 | 88.8 | 67.2
3234.1 | 2995.1 | 67.6 | 223.7 | 58.8 | 88.9 | 67.1
3235.1 | 2996.1 | 67.6 | 223.7 | 58.6 | 89 | 67.1
3236.1 | 2997.1 | 67.6 | 223.6 | 58.3 | 89.1 | 66.7
3237.1 | 2998.1 | 67.4 | 223.5 | 58.2 | 89.2 | 66.7
3238.1 | 2999.1 | 67.3 | 223.7 | 58.1 | 89.3 | 66.8
3239.1 | 3000.1 | 67.3 | 223.7 | 57.9 | 89.3 | 66.8
3240.1 | 3001.1 | 67.4 | 223.9 | 57.8 | 89.3 | 66.9
3241.1 | 3002.1 | 67.4 | 224 | 57.7 | 89.5 | 67
3242.1 | 3003.1 | 67.3 | 223.9 | 57.6 | 89.5 | 67
3243.1 | 3004.1 | 67.2 | 223.4 | 57.4 | 89.5 | 66.9
3244.1 | 3005.1 | 67.1 | 223 | 57.3 | 89.5 | 66.7
3245.1 | 3006.1 | 67.3 | 222.5 | 57.2 | 89.5 | 66.7
3246.1 | 3007.1 | 67.2 | 222.3 | 57.1 | 89.5 | 66.8
3247.1 | 3008.1 | 67 | 222.2 | 57.2 | 89.6 | 66.9
3248.1 | 3009.1 | 66.9 | 222 | 57.3 | 89.5 | 66.9
3249.1 | 3010.1 | 67 | 221.9 | 57.7 | 89.6 | 66.9
3250.1 | 3011.1 | 67 | 222 | 57.6 | 89.6 | 67.1
3251.1 | 3012.1 | 67.2 | 222 | 57.6 | 89.8 | 67
3252.1 | 3013.1 | 67.1 | 221.7 | 57.6 | 90 | 66.6
3253.1 | 3014.1 | 67.1 | 221.4 | 57.5 | 90.2 | 66.7
3254.1 | 3015.1 | 66.8 | 221.3 | 57.5 | 90.3 | 66.9
3255.1 | 3016.1 | 66.6 | 221.2 | 57.3 | 90.3 | 66.9
3256.1 | 3017.1 | 66.6 | 221.2 | 57.1 | 90.4 | 67
3257.1 | 3018.1 | 66.6 | 221.1 | 57 | 90.4 | 66.9
3258.1 | 3019.1 | 66.5 | 221.1 | 57 | 90.5 | 66.9
3259.1 | 3020.1 | 66.6 | 221.2 | 57.6 | 90.6 | 67
3260.1 | 3021.1 | 66.5 | 221.1 | 57.6 | 90.8 | 67.1
3261.1 | 3022.1 | 66.5 | 221.2 | 57.4 | 91 | 66.9
3262.1 | 3023.1 | 66.5 | 221.1 | 57.2 | 91.1 | 66.5
3263.1 | 3024.1 | 66.3 | 221.1 | 57.1 | 91.1 | 66.2
3264.1 | 3025.1 | 66.2 | 220.9 | 57 | 91.1 | 66.3
3265.1 | 3026.1 | 66.2 | 220.9 | 56.9 | 91 | 66.6
3266.1 | 3027.1 | 66.2 | 220.9 | 57 | 91 | 66.5
3267.1 | 3028.1 | 66.2 | 220.7 | 56.9 | 91.2 | 66.4
3268.1 | 3029.1 | 66.4 | 220.5 | 56.7 | 91.5 | 66.5
3269.1 | 3030.1 | 66.5 | 220.5 | 56.6 | 91.6 | 66.4
3270.1 | 3031.1 | 66.6 | 220.3 | 56.7 | 91.8 | 66.4
3271.1 | 3032.1 | 66.4 | 220.3 | 56.7 | 91.9 | 66.4
3272.1 | 3033.1 | 66.4 | 220.2 | 56.4 | 91.9 | 66.4
3273.1 | 3034.1 | 66.4 | 220.2 | 56.4 | 92 | 66.1
3274.1 | 3035.1 | 66.1 | 220.2 | 56.6 | 91.9 | 65.9
3275.1 | 3036.1 | 65.8 | 220 | 56.5 | 91.8 | 66
3276.1 | 3037.1 | 65.9 | 220.1 | 56.3 | 91.8 | 66.2
3277.1 | 3038.1 | 66 | 220.2 | 56.4 | 91.8 | 66.3
3278.1 | 3039.1 | 66.2 | 220.3 | 56.5 | 91.9 | 66.1
3279.1 | 3040.1 | 66.2 | 220.3 | 56.6 | 92.1 | 66.1
3280.1 | 3041.1 | 66.1 | 220.5 | 56.7 | 92.2 | 66.4
3281.1 | 3042.1 | 66.1 | 220.8 | 56.8 | 92.5 | 66.5
3282.1 | 3043.1 | 66 | 220.9 | 56.9 | 92.6 | 66.4
3283.1 | 3044.1 | 65.8 | 221.1 | 57 | 92.7 | 66.4
3284.1 | 3045.1 | 65.8 | 221.4 | 57.1 | 92.8 | 66.4
3285.1 | 3046.1 | 65.5 | 221.5 | 57.2 | 92.8 | 66.2
3286.1 | 3047.1 | 65.5 | 221.5 | 57.1 | 92.9 | 66.1
3287.1 | 3048.1 | 65.7 | 221.6 | 57.2 | 92.9 | 66.3
3288.1 | 3049.1 | 65.6 | 221.7 | 57.2 | 93.1 | 66.3
3289.1 | 3050.1 | 65.5 | 221.6 | 57.2 | 93.2 | 66.2
3290.1 | 3051.1 | 65.4 | 221.6 | 57.1 | 93.2 | 66.2
3291.1 | 3052.1 | 65.5 | 221.5 | 57.4 | 93.2 | 65.9
3292.1 | 3053.1 | 65.6 | 221.2 | 57.3 | 93.3 | 66
3293.1 | 3054.1 | 65.3 | 221 | 57.1 | 93.5 | 66.1
3294.1 | 3055.1 | 65.3 | 220.6 | 56.9 | 93.4 | 66
3295.1 | 3056.1 | 65.4 | 220.4 | 57.2 | 93.6 | 66.1
3296.1 | 3057.1 | 65.5 | 220.4 | 57.1 | 93.8 | 66.2
3297.1 | 3058.1 | 65.6 | 220.4 | 57.3 | 94 | 66.2
3298.1 | 3059.1 | 65.5 | 220.2 | 57 | 94.2 | 66.3
3299.1 | 3060.1 | 65.4 | 220.2 | 56.7 | 94.5 | 66
3300.1 | 3061.1 | 65.2 | 220.2 | 56.5 | 94.6 | 65.8
3301.1 | 3062.1 | 65.1 | 220.1 | 56.5 | 94.5 | 65.6
3302.1 | 3063.1 | 65.3 | 220.2 | 56.3 | 94.7 | 65.9
3303.1 | 3064.1 | 65.3 | 220.2 | 56.3 | 94.9 | 65.6
3304.1 | 3065.1 | 65.3 | 220.2 | 56.3 | 95.1 | 65.7
3305.1 | 3066.1 | 65.2 | 220.2 | 56.3 | 95.3 | 65.5
3306.1 | 3067.1 | 65.3 | 220 | 56.3 | 95.4 | 65.7
3307.1 | 3068.1 | 65.3 | 219.9 | 56.3 | 95.7 | 65.9
3308.1 | 3069.1 | 65.2 | 219.9 | 56.5 | 95.9 | 65.8
3309.1 | 3070.1 | 65.2 | 219.9 | 56.5 | 96 | 65.5
3310.1 | 3071.1 | 65.1 | 220.1 | 56.6 | 96.1 | 65.7
3311.1 | 3072.1 | 65 | 220 | 56.7 | 96.2 | 65.9
3312.1 | 3073.1 | 64.9 | 219.9 | 56.8 | 96.2 | 65.9
3313.1 | 3074.1 | 64.9 | 220 | 56.9 | 96.3 | 65.7
3314.1 | 3075.1 | 65.1 | 220 | 56.9 | 96.4 | 65.9
3315.1 | 3076.1 | 65 | 220 | 56.9 | 96.4 | 66
3316.1 | 3077.1 | 64.9 | 220 | 57 | 96.6 | 66.1
3317.1 | 3078.1 | 64.8 | 220 | 57 | 96.7 | 65.7
3318.1 | 3079.1 | 64.9 | 219.9 | 57.2 | 96.8 | 65.5
3319.1 | 3080.1 | 64.8 | 219.8 | 57.4 | 96.8 | 65.9
3320.1 | 3081.1 | 64.7 | 219.6 | 57.5 | 96.9 | 65.9
3321.1 | 3082.1 | 64.5 | 219.3 | 57.7 | 96.9 | 65.9
3322.1 | 3083.1 | 64.5 | 219.1 | 57.7 | 96.7 | 65.9
3323.1 | 3084.1 | 64.4 | 219 | 58 | 96.6 | 65.9
3324.1 | 3085.1 | 64.4 | 219 | 58 | 96.6 | 65.8
3325.1 | 3086.1 | 64.4 | 219.1 | 57.9 | 96.7 | 65.5
3326.1 | 3087.1 | 64.4 | 219.1 | 57.7 | 96.8 | 65.5
3327.1 | 3088.1 | 64.3 | 219.3 | 57.7 | 96.9 | 65.8
3328.1 | 3089.1 | 64.4 | 219.5 | 57.7 | 96.9 | 66
3329.1 | 3090.1 | 64.6 | 219.5 | 57.7 | 97.2 | 65.9
3330.1 | 3091.1 | 64.6 | 219.6 | 57.5 | 97.4 | 65.7
3331.1 | 3092.1 | 64.5 | 219.7 | 57.4 | 97.4 | 65.4
3332.1 | 3093.1 | 64.6 | 219.8 | 57.4 | 97.5 | 65.4
3333.1 | 3094.1 | 64.6 | 219.9 | 57.3 | 97.8 | 65.7
3334.1 | 3095.1 | 64.4 | 219.9 | 57.1 | 97.8 | 65.6
3335.1 | 3096.1 | 64.2 | 220 | 57 | 97.7 | 65.5
3336.1 | 3097.1 | 64.2 | 220.1 | 57.7 | 97.7 | 65.4
3337.1 | 3098.1 | 64.2 | 220 | 57.9 | 97.6 | 65.3
3338.1 | 3099.1 | 64.2 | 220.1 | 57.9 | 97.6 | 65.5
3339.1 | 3100.1 | 64.3 | 220.2 | 58 | 97.8 | 65.4
3340.1 | 3101.1 | 64.2 | 220.3 | 57.8 | 97.9 | 65.2
3341.1 | 3102.1 | 64.2 | 219.9 | 58.2 | 97.9 | 65.2
3342.1 | 3103.1 | 64 | 219.5 | 58.3 | 97.9 | 65.3
3343.1 | 3104.1 | 64 | 219.2 | 58.4 | 97.8 | 65.3
3344.1 | 3105.1 | 63.9 | 219.2 | 58.8 | 97.8 | 65.2
3345.1 | 3106.1 | 63.9 | 219.3 | 58.7 | 97.7 | 65.4
3346.1 | 3107.1 | 63.9 | 219.5 | 58.4 | 97.7 | 65.6
3347.1 | 3108.1 | 64 | 219.6 | 58.2 | 97.8 | 65.5
3348.1 | 3109.1 | 63.8 | 219.5 | 58.3 | 97.7 | 65.1
3349.1 | 3110.1 | 63.7 | 219.4 | 58.5 | 97.5 | 65
3350.1 | 3111.1 | 63.6 | 219.5 | 58.8 | 97.4 | 64.9
3351.1 | 3112.1 | 63.6 | 219.6 | 58.6 | 97.4 | 64.9
3352.1 | 3113.1 | 63.5 | 219.4 | 58.7 | 97.4 | 64.6
3353.1 | 3114.1 | 63.5 | 219.4 | 58.8 | 97.3 | 64.8
3354.1 | 3115.1 | 63.5 | 219.4 | 58.9 | 97.3 | 64.8
3355.1 | 3116.1 | 63.6 | 219.5 | 59 | 97.3 | 64.7
3356.1 | 3117.1 | 63.5 | 219.7 | 59.2 | 97.3 | 65

## Test Facts
Last row in IRMS data sheets: | 82
Time when gas burner was ignited: | 239