## Test Conditions
CAROLFIRE Intermediate Scale Test Number IT-14
Test Date: | 2006-11-29
Ignition Time Relative to Thermal Data: | 236 | s
Ignition Time Relative to Electrical Data: | 236 | s
A Note regarding Propene Gas Flow Reading and calculation of Heat Release Rate:
The indicated flow rate is recorded in Standard Liters per Minute (SLM) of Gas. There is a correction factor of 0.40 applied to reflect the behavior of Propene versus the Flow Controller calibration gas which is Nitrogen. Hence, the actual flow of Propene in SLM is the indicated flow (shown in the data set as "Propene Gas Flow Reading") times 0.40. The heat release rate (HRR) can then be estimated using the gas density at standard conditions, heat of combustion, and the combustion efficiency. The result of this calculation is also shown on the data sheet based on the assumed properties listed below in the rows immediately below. Note that altering the values listed here will result in revised calculations of the HRR.
| Gas Burner Heat Release Rate Calculation Parameters: | Value | Units
| Gas Density At Standard conditions | 1.802 | kg/m3
| Heat of Combustion | 45.79 | MJ/kg
| One liter equals | 0.001 | m3
| Combustion efficiency | 0.85 | %

## Data Plots
Temperatures for random fill tray at C

## Thermal Data
Time |  | Burner |  |  | Hood & Ambient Facility Temperatures | [5 empty] | Stack |  |  | External Wind |  | Random Fill Tray, Location A |  |  |  |  | Location A | Random Fill Tray, Location C |  |  |  |  | Location C | Location E: Conduit with 3-cable bundle |  |  | Location F - 6-cable bundle 13-2 |  |  |  | Location F | Location G - 6-cable bundle 13-2 |  |  |  | Location G | Slug Calorimeters
Time (s) | Offset Time (s) | Raw Gas Flow | Corrected Gas Flow (SLM) | Nominal HRR (kW) | Hood East | Hood West | Hood North | Hood South | Hood Top | Facility Ambient | O2 analyzer | stack temp | diff press stack *10 | wind direction | wind speed (mph) | TC1 Cable Center Row Center | TC2 Above Cable Mass | TC3 Below Cable mass | TC4 Cable Center Row Left | TC5 Cable Center Row Right | Tray Rung | TC1 Cable Center Row Center | TC2 Above Cable Mass | TC3 Below Cable mass | TC4 Cable Center Row Left | TC5 Cable Center Row Right | Tray Rung | Cable Temp | Air Inside Conduit | Conduit Temp | TC-1 Cable E | TC-2 Above Bundle | TC3 Below Bundle | TC4 Bundle Center | Tray Rung | TC-1 Cable E | TC-2 Above Bundle | TC3 Below Bundle | TC4 Bundle Center | Tray Rung | Slug Calorimeter Above Location F | Slug Calorimeter Above Location G
0 | -236 | -6.5 | 0 | 0 | 10.6 | 10.5 | 11 | 11.8 | 12.1 | 7.8 | 21.5 | 7.7 | 1.7 | 251.9 | 5.1 | 8.5 | 6.7 | 7.8 | 9.1 | 8.4 | 9.6 | 9.5 | 9.3 | 8 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.5 | 12 | 10.8 | 10.3 | 12 | 12.1 | 11.8 | 11 | 10.2 | 12.1 | 9.9 | 10.6 | 10.6
1 | -235 | -6.2 | 0 | 0 | 10.6 | 10.5 | 11 | 11.8 | 12.1 | 7.8 | 21.5 | 7.7 | 1.6 | 255.2 | 4.7 | 8.5 | 6.7 | 7.8 | 9.1 | 8.4 | 9.6 | 9.5 | 9.3 | 8 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.5 | 12 | 10.8 | 10.3 | 12 | 12.1 | 11.7 | 11 | 10.2 | 12.1 | 9.9 | 10.6 | 10.6
2 | -234 | -6.2 | 0 | 0 | 10.6 | 10.4 | 11 | 11.8 | 12.1 | 7.8 | 21.5 | 7.7 | 1.6 | 266.8 | 4.2 | 8.5 | 6.7 | 7.8 | 9.1 | 8.4 | 9.6 | 9.5 | 9.3 | 8 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.5 | 12 | 10.8 | 10.3 | 12 | 12.1 | 11.7 | 11 | 10.2 | 12.1 | 9.9 | 10.6 | 10.6
3 | -233 | -6.2 | 0 | 0 | 10.6 | 10.4 | 11.1 | 11.8 | 12.1 | 7.8 | 21.5 | 7.7 | 1.5 | 276.3 | 4.2 | 8.5 | 6.7 | 7.8 | 9.1 | 8.4 | 9.6 | 9.5 | 9.3 | 8 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.5 | 12 | 10.8 | 10.3 | 12 | 12.1 | 11.8 | 11 | 10.2 | 12.1 | 9.9 | 10.6 | 10.6
4 | -232 | -6 | 0 | 0 | 10.6 | 10.4 | 11.1 | 11.8 | 12.1 | 7.8 | 21.5 | 7.8 | 1.6 | 266.2 | 4.7 | 8.5 | 6.7 | 7.8 | 9.1 | 8.4 | 9.6 | 9.5 | 9.3 | 8 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.5 | 12 | 10.8 | 10.3 | 12 | 12.1 | 11.8 | 11 | 10.2 | 12.1 | 9.9 | 10.6 | 10.6
5 | -231 | -6 | 0 | 0 | 10.6 | 10.4 | 11.1 | 11.8 | 12.1 | 7.8 | 21.5 | 7.8 | 1.6 | 267.3 | 5.4 | 8.5 | 6.7 | 7.8 | 9.1 | 8.4 | 9.6 | 9.5 | 9.3 | 8 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.5 | 12 | 10.8 | 10.3 | 12 | 12.1 | 11.8 | 11 | 10.2 | 12.1 | 9.9 | 10.6 | 10.6
6 | -230 | -6.1 | 0 | 0 | 10.6 | 10.4 | 11 | 11.8 | 12.1 | 7.8 | 21.5 | 7.8 | 1.8 | 274.8 | 5.4 | 8.5 | 6.7 | 7.8 | 9.1 | 8.4 | 9.6 | 9.5 | 9.3 | 8 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.5 | 12 | 10.8 | 10.2 | 12 | 12.1 | 11.8 | 11 | 10.2 | 12.1 | 9.9 | 10.6 | 10.6
7 | -229 | -6 | 0 | 0 | 10.6 | 10.4 | 11 | 11.8 | 12.1 | 7.8 | 21.5 | 7.8 | 2 | 250.4 | 5.4 | 8.5 | 6.7 | 7.8 | 9.1 | 8.4 | 9.6 | 9.5 | 9.3 | 8 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.5 | 12 | 10.8 | 10.3 | 12 | 12.1 | 11.8 | 11 | 10.2 | 12.1 | 10 | 10.6 | 10.6
8 | -228 | -6.1 | 0 | 0 | 10.7 | 10.4 | 11 | 11.8 | 12.1 | 7.8 | 21.5 | 7.7 | 2.2 | 259.2 | 5.6 | 8.5 | 6.7 | 7.8 | 9.1 | 8.4 | 9.6 | 9.5 | 9.3 | 8 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.5 | 12 | 10.8 | 10.3 | 12 | 12.1 | 11.8 | 11 | 10.2 | 12.1 | 9.9 | 10.6 | 10.6
9 | -227 | -6.3 | 0 | 0 | 10.7 | 10.4 | 11 | 11.8 | 12.1 | 7.8 | 21.5 | 7.8 | 2.2 | 261 | 5.7 | 8.5 | 6.7 | 7.8 | 9.1 | 8.4 | 9.6 | 9.5 | 9.3 | 8 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.5 | 12 | 10.8 | 10.3 | 12 | 12.1 | 11.7 | 11 | 10.2 | 12.1 | 9.9 | 10.6 | 10.6
10 | -226 | -6.5 | 0 | 0 | 10.7 | 10.4 | 11 | 11.8 | 12.1 | 7.8 | 21.5 | 7.8 | 2.1 | 249.2 | 6.1 | 8.5 | 6.7 | 7.7 | 9.1 | 8.4 | 9.6 | 9.5 | 9.3 | 8 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.5 | 11.9 | 10.8 | 10.3 | 12 | 12.1 | 11.8 | 11 | 10.2 | 12.1 | 9.9 | 10.6 | 10.6
11 | -225 | -6.6 | 0 | 0 | 10.7 | 10.4 | 10.9 | 11.8 | 12.1 | 7.8 | 21.5 | 7.8 | 1.9 | 240 | 5.9 | 8.5 | 6.7 | 7.7 | 9.1 | 8.4 | 9.6 | 9.5 | 9.3 | 8 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.5 | 11.9 | 10.8 | 10.3 | 12 | 12.1 | 11.7 | 11 | 10.2 | 12.1 | 9.9 | 10.6 | 10.6
12 | -224 | -6.4 | 0 | 0 | 10.7 | 10.4 | 10.9 | 11.8 | 12.1 | 7.8 | 21.5 | 7.8 | 1.8 | 238.3 | 5.5 | 8.5 | 6.7 | 7.7 | 9.1 | 8.4 | 9.6 | 9.5 | 9.3 | 8 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.5 | 11.9 | 10.8 | 10.3 | 12 | 12.1 | 11.7 | 11 | 10.2 | 12.1 | 9.9 | 10.6 | 10.6
13 | -223 | -6.2 | 0 | 0 | 10.7 | 10.4 | 10.9 | 11.8 | 12.1 | 7.8 | 21.5 | 7.8 | 1.8 | 228.5 | 4.9 | 8.5 | 6.7 | 7.8 | 9.1 | 8.4 | 9.6 | 9.5 | 9.3 | 8 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.5 | 12 | 10.8 | 10.3 | 12 | 12.1 | 11.7 | 11 | 10.2 | 12.1 | 9.9 | 10.6 | 10.6
14 | -222 | -6.2 | 0 | 0 | 10.7 | 10.4 | 10.9 | 11.8 | 12.1 | 7.8 | 21.5 | 7.8 | 1.6 | 238.4 | 4.6 | 8.5 | 6.7 | 7.8 | 9.1 | 8.4 | 9.6 | 9.5 | 9.4 | 8 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.3 | 12 | 12.1 | 11.7 | 11 | 10.2 | 12.1 | 9.9 | 10.6 | 10.6
15 | -221 | -6.5 | 0 | 0 | 10.7 | 10.4 | 10.9 | 11.8 | 12.1 | 7.7 | 21.5 | 7.8 | 1.5 | 263.1 | 5 | 8.5 | 6.7 | 7.8 | 9.1 | 8.4 | 9.6 | 9.5 | 9.4 | 8 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.3 | 12 | 12.1 | 11.7 | 11 | 10.2 | 12.1 | 9.9 | 10.6 | 10.6
16 | -220 | -6.6 | 0 | 0 | 10.6 | 10.4 | 10.9 | 11.8 | 12.1 | 7.7 | 21.5 | 7.8 | 1.7 | 257 | 5.2 | 8.5 | 6.7 | 7.8 | 9.1 | 8.4 | 9.6 | 9.5 | 9.3 | 8 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.3 | 12 | 12.1 | 11.7 | 11 | 10.2 | 12.1 | 9.9 | 10.6 | 10.6
17 | -219 | -6.5 | 0 | 0 | 10.6 | 10.4 | 10.8 | 11.8 | 12.1 | 7.7 | 21.5 | 7.8 | 1.8 | 250.1 | 5.1 | 8.5 | 6.7 | 7.8 | 9.1 | 8.4 | 9.6 | 9.5 | 9.3 | 8 | 9.5 | 10.1 | 11.6 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.3 | 12 | 12.1 | 11.7 | 11 | 10.2 | 12.1 | 9.9 | 10.6 | 10.6
18 | -218 | -6.6 | 0 | 0 | 10.6 | 10.4 | 10.8 | 11.8 | 12.1 | 7.7 | 21.5 | 7.8 | 1.4 | 264.1 | 5.1 | 8.5 | 6.7 | 7.8 | 9.1 | 8.4 | 9.6 | 9.5 | 9.3 | 8 | 9.5 | 10.1 | 11.6 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.3 | 12 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9 | 10.6 | 10.6
19 | -217 | -6.7 | 0 | 0 | 10.6 | 10.4 | 10.8 | 11.8 | 12.1 | 7.7 | 21.5 | 7.8 | 1.5 | 248.8 | 5.5 | 8.5 | 6.7 | 7.8 | 9.1 | 8.4 | 9.6 | 9.5 | 9.3 | 8 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.3 | 12 | 12.1 | 11.8 | 11.1 | 10.2 | 12.1 | 9.9 | 10.6 | 10.6
20 | -216 | -6.7 | 0 | 0 | 10.5 | 10.4 | 10.8 | 11.8 | 12.1 | 7.7 | 21.5 | 7.8 | 1.8 | 255.9 | 5.8 | 8.5 | 6.7 | 7.8 | 9.1 | 8.4 | 9.6 | 9.5 | 9.3 | 8 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.4 | 12 | 10.8 | 10.3 | 12 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9 | 10.6 | 10.6
21 | -215 | -6.5 | 0 | 0 | 10.5 | 10.4 | 10.8 | 11.8 | 12.1 | 7.7 | 21.5 | 7.8 | 1.5 | 241.8 | 6.2 | 8.5 | 6.7 | 7.8 | 9.1 | 8.4 | 9.6 | 9.5 | 9.3 | 8 | 9.5 | 10.1 | 11.6 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.3 | 12 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9 | 10.6 | 10.6
22 | -214 | -6.3 | 0 | 0 | 10.5 | 10.4 | 10.8 | 11.8 | 12.1 | 7.7 | 21.5 | 7.8 | 1.6 | 250.2 | 6.7 | 8.5 | 6.7 | 7.8 | 9.1 | 8.4 | 9.6 | 9.5 | 9.3 | 8 | 9.5 | 10.1 | 11.6 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.3 | 12 | 12.1 | 11.8 | 11.1 | 10.2 | 12.1 | 9.9 | 10.6 | 10.6
23 | -213 | -6.1 | 0 | 0 | 10.5 | 10.4 | 10.9 | 11.8 | 12.1 | 7.7 | 21.5 | 7.8 | 1.7 | 245.2 | 6.8 | 8.4 | 6.7 | 7.8 | 9.1 | 8.4 | 9.6 | 9.5 | 9.3 | 8 | 9.5 | 10.1 | 11.6 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.3 | 12 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9 | 10.6 | 10.6
24 | -212 | -5.8 | 0 | 0 | 10.5 | 10.4 | 10.9 | 11.8 | 12.1 | 7.7 | 21.5 | 7.8 | 1.8 | 242.7 | 6.9 | 8.5 | 6.7 | 7.7 | 9.1 | 8.4 | 9.6 | 9.5 | 9.3 | 8 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.3 | 12 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9 | 10.6 | 10.6
25 | -211 | -6.1 | 0 | 0 | 10.6 | 10.4 | 10.9 | 11.8 | 12.1 | 7.7 | 21.5 | 7.8 | 1.6 | 246.1 | 6.6 | 8.5 | 6.7 | 7.7 | 9.1 | 8.4 | 9.6 | 9.5 | 9.3 | 8 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.5 | 11.9 | 10.8 | 10.3 | 12 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9 | 10.6 | 10.6
26 | -210 | -6.3 | 0 | 0 | 10.6 | 10.4 | 11 | 11.8 | 12.1 | 7.7 | 21.5 | 7.8 | 1.8 | 249.7 | 6.4 | 8.5 | 6.7 | 7.7 | 9.1 | 8.4 | 9.6 | 9.5 | 9.3 | 7.9 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.3 | 12 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9 | 10.6 | 10.6
27 | -209 | -6.5 | 0 | 0 | 10.6 | 10.4 | 11 | 11.8 | 12.1 | 7.7 | 21.5 | 7.8 | 1.8 | 249 | 6.5 | 8.5 | 6.7 | 7.7 | 9.1 | 8.4 | 9.6 | 9.5 | 9.3 | 7.9 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.3 | 12 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9 | 10.6 | 10.6
28 | -208 | -6.5 | 0 | 0 | 10.6 | 10.4 | 11 | 11.8 | 12.1 | 7.7 | 21.5 | 7.8 | 1.8 | 246.6 | 6.3 | 8.5 | 6.7 | 7.7 | 9.1 | 8.4 | 9.6 | 9.5 | 9.3 | 7.9 | 9.5 | 10.1 | 11.6 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.3 | 12 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9 | 10.6 | 10.6
29 | -207 | -6.6 | 0 | 0 | 10.6 | 10.4 | 11.1 | 11.8 | 12.1 | 7.7 | 21.5 | 7.8 | 1.6 | 246.6 | 6.1 | 8.5 | 6.7 | 7.7 | 9.1 | 8.4 | 9.6 | 9.5 | 9.3 | 7.9 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.3 | 12 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9 | 10.6 | 10.6
30 | -206 | -6.7 | 0 | 0 | 10.6 | 10.4 | 11.1 | 11.8 | 12.1 | 7.7 | 21.5 | 7.8 | 1.7 | 256.2 | 6.2 | 8.5 | 6.7 | 7.7 | 9.1 | 8.4 | 9.6 | 9.5 | 9.3 | 7.9 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.3 | 12 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9 | 10.6 | 10.6
31 | -205 | -6.7 | 0 | 0 | 10.6 | 10.4 | 11.1 | 11.8 | 12.1 | 7.7 | 21.5 | 7.8 | 1.6 | 258.3 | 6.5 | 8.5 | 6.7 | 7.8 | 9.1 | 8.4 | 9.6 | 9.5 | 9.3 | 7.9 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.2 | 12 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9 | 10.6 | 10.6
32 | -204 | -6.8 | 0 | 0 | 10.6 | 10.4 | 11.1 | 11.8 | 12.1 | 7.7 | 21.5 | 7.8 | 1.9 | 244.9 | 6.9 | 8.5 | 6.7 | 7.8 | 9.1 | 8.4 | 9.6 | 9.5 | 9.3 | 7.9 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.3 | 12 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9 | 10.6 | 10.6
33 | -203 | -6.8 | 0 | 0 | 10.6 | 10.4 | 11.1 | 11.8 | 12.1 | 7.7 | 21.5 | 7.8 | 1.9 | 251.2 | 6.7 | 8.5 | 6.7 | 7.8 | 9.1 | 8.4 | 9.6 | 9.5 | 9.3 | 7.9 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.3 | 12 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9 | 10.6 | 10.6
34 | -202 | -6.8 | 0 | 0 | 10.6 | 10.4 | 11.2 | 11.8 | 12.1 | 7.7 | 21.5 | 7.8 | 1.9 | 249.6 | 6.4 | 8.5 | 6.7 | 7.8 | 9.1 | 8.4 | 9.6 | 9.5 | 9.3 | 7.9 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.3 | 12 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9 | 10.6 | 10.6
35 | -201 | -6.4 | 0 | 0 | 10.6 | 10.4 | 11.1 | 11.8 | 12.1 | 7.7 | 21.5 | 7.8 | 1.5 | 240.6 | 6 | 8.5 | 6.7 | 7.7 | 9.1 | 8.4 | 9.6 | 9.5 | 9.3 | 7.9 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.3 | 12 | 12.1 | 11.7 | 11.1 | 10.1 | 12.1 | 9.9 | 10.6 | 10.6
36 | -200 | -6.6 | 0 | 0 | 10.6 | 10.4 | 11.1 | 11.8 | 12.1 | 7.7 | 21.5 | 7.8 | 1.6 | 246.8 | 5.8 | 8.5 | 6.7 | 7.7 | 9.1 | 8.4 | 9.6 | 9.5 | 9.3 | 7.9 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.3 | 12 | 12.1 | 11.7 | 11.1 | 10.1 | 12.1 | 9.9 | 10.6 | 10.6
37 | -199 | -6.5 | 0 | 0 | 10.6 | 10.4 | 11.1 | 11.8 | 12.1 | 7.7 | 21.5 | 7.8 | 1.7 | 252.1 | 5.7 | 8.5 | 6.7 | 7.7 | 9.1 | 8.4 | 9.6 | 9.5 | 9.3 | 7.9 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.3 | 12 | 12.1 | 11.7 | 11.1 | 10.1 | 12.1 | 9.9 | 10.6 | 10.6
38 | -198 | -6.3 | 0 | 0 | 10.6 | 10.3 | 11.1 | 11.8 | 12.1 | 7.7 | 21.5 | 7.8 | 1.8 | 257.3 | 5.7 | 8.5 | 6.7 | 7.7 | 9.1 | 8.4 | 9.6 | 9.5 | 9.3 | 7.9 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.3 | 12 | 12.1 | 11.7 | 11.1 | 10.1 | 12.1 | 9.9 | 10.6 | 10.6
39 | -197 | -6.4 | 0 | 0 | 10.6 | 10.3 | 11.1 | 11.8 | 12.1 | 7.7 | 21.5 | 7.8 | 1.8 | 255.5 | 5.6 | 8.5 | 6.7 | 7.7 | 9.1 | 8.4 | 9.6 | 9.5 | 9.3 | 7.9 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.3 | 12 | 12.1 | 11.7 | 11.1 | 10.1 | 12.1 | 9.9 | 10.6 | 10.6
40 | -196 | -6.5 | 0 | 0 | 10.6 | 10.3 | 11.1 | 11.8 | 12 | 7.7 | 21.5 | 7.8 | 1.8 | 256.8 | 5.4 | 8.5 | 6.7 | 7.7 | 9.1 | 8.4 | 9.6 | 9.5 | 9.3 | 7.9 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.3 | 12 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9 | 10.6 | 10.6
41 | -195 | -6.5 | 0 | 0 | 10.6 | 10.3 | 11.1 | 11.8 | 12 | 7.7 | 21.5 | 7.8 | 1.9 | 267.2 | 5.5 | 8.5 | 6.7 | 7.8 | 9.1 | 8.4 | 9.6 | 9.5 | 9.3 | 7.9 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.3 | 12 | 12.1 | 11.7 | 11.1 | 10.1 | 12.1 | 9.9 | 10.6 | 10.6
42 | -194 | -6.7 | 0 | 0 | 10.6 | 10.3 | 11.1 | 11.8 | 12 | 7.7 | 21.5 | 7.8 | 1.9 | 249.9 | 5.6 | 8.5 | 6.7 | 7.8 | 9.1 | 8.4 | 9.6 | 9.5 | 9.3 | 7.9 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.3 | 12 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9 | 10.6 | 10.6
43 | -193 | -6.6 | 0 | 0 | 10.6 | 10.3 | 11.1 | 11.8 | 12 | 7.7 | 21.5 | 7.8 | 1.9 | 241.1 | 5.6 | 8.5 | 6.7 | 7.7 | 9.1 | 8.4 | 9.6 | 9.5 | 9.3 | 7.9 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.2 | 12 | 12.1 | 11.7 | 11.1 | 10.1 | 12.1 | 9.9 | 10.6 | 10.6
44 | -192 | -6.6 | 0 | 0 | 10.6 | 10.3 | 11.1 | 11.8 | 12 | 7.7 | 21.5 | 7.8 | 1.7 | 267.7 | 5.6 | 8.5 | 6.8 | 7.7 | 9.1 | 8.4 | 9.6 | 9.5 | 9.3 | 7.9 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.3 | 12 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9 | 10.6 | 10.6
45 | -191 | -6.5 | 0 | 0 | 10.6 | 10.3 | 11 | 11.8 | 12 | 7.7 | 21.5 | 7.8 | 1.8 | 264.1 | 5.7 | 8.5 | 6.8 | 7.7 | 9.1 | 8.4 | 9.6 | 9.5 | 9.3 | 7.9 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.5 | 11.9 | 10.8 | 10.2 | 12 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9 | 10.6 | 10.6
46 | -190 | -6.5 | 0 | 0 | 10.6 | 10.3 | 11 | 11.8 | 12 | 7.7 | 21.5 | 7.8 | 1.7 | 261.7 | 5.7 | 8.5 | 6.8 | 7.8 | 9.1 | 8.4 | 9.6 | 9.5 | 9.3 | 7.9 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.2 | 12 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9 | 10.6 | 10.6
47 | -189 | -6.6 | 0 | 0 | 10.5 | 10.3 | 11 | 11.8 | 12 | 7.7 | 21.5 | 7.8 | 1.7 | 250.9 | 5.4 | 8.5 | 6.7 | 7.8 | 9.1 | 8.4 | 9.6 | 9.5 | 9.3 | 7.9 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.7 | 10.2 | 12 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9 | 10.6 | 10.6
48 | -188 | -6.7 | 0 | 0 | 10.5 | 10.3 | 11 | 11.8 | 12 | 7.7 | 21.5 | 7.8 | 1.7 | 247 | 5.1 | 8.5 | 6.7 | 7.8 | 9.1 | 8.4 | 9.6 | 9.5 | 9.3 | 7.9 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.2 | 12 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9 | 10.6 | 10.6
49 | -187 | -5.5 | 0 | 0 | 10.6 | 10.3 | 11 | 11.8 | 12 | 7.8 | 21.5 | 7.8 | 1.7 | 259.8 | 4.8 | 8.5 | 6.8 | 7.8 | 9.1 | 8.4 | 9.6 | 9.5 | 9.3 | 7.9 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.2 | 12 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9 | 10.6 | 10.6
50 | -186 | -6 | 0 | 0 | 10.5 | 10.3 | 11 | 11.8 | 12 | 7.8 | 21.5 | 7.8 | 1.6 | 251.2 | 4.8 | 8.5 | 6.8 | 7.7 | 9.1 | 8.4 | 9.6 | 9.5 | 9.3 | 7.9 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.2 | 12 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9 | 10.6 | 10.6
51 | -185 | -6.8 | 0 | 0 | 10.5 | 10.3 | 11 | 11.8 | 12 | 7.8 | 21.5 | 7.8 | 1.5 | 254.8 | 5.3 | 8.5 | 6.7 | 7.7 | 9.1 | 8.4 | 9.7 | 9.5 | 9.3 | 7.9 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.2 | 12 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9 | 10.6 | 10.6
52 | -184 | -6.6 | 0 | 0 | 10.5 | 10.3 | 11 | 11.8 | 12 | 7.8 | 21.5 | 7.7 | 1.4 | 253.3 | 5.9 | 8.5 | 6.7 | 7.7 | 9.1 | 8.4 | 9.6 | 9.5 | 9.2 | 7.9 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.2 | 12 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9 | 10.6 | 10.6
53 | -183 | -6.6 | 0 | 0 | 10.5 | 10.3 | 10.9 | 11.8 | 12 | 7.8 | 21.5 | 7.7 | 1.4 | 246.4 | 6 | 8.5 | 6.7 | 7.7 | 9.1 | 8.4 | 9.6 | 9.5 | 9.2 | 7.9 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.2 | 12 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9 | 10.6 | 10.6
54 | -182 | -6.5 | 0 | 0 | 10.5 | 10.3 | 10.9 | 11.8 | 12 | 7.8 | 21.5 | 7.7 | 1.6 | 253.6 | 6.2 | 8.5 | 6.7 | 7.7 | 9.1 | 8.4 | 9.6 | 9.5 | 9.2 | 7.9 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.2 | 12 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9 | 10.6 | 10.6
55 | -181 | -6.4 | 0 | 0 | 10.5 | 10.3 | 10.9 | 11.8 | 12 | 7.8 | 21.5 | 7.7 | 1.7 | 257.2 | 6.1 | 8.5 | 6.7 | 7.7 | 9.1 | 8.4 | 9.6 | 9.5 | 9.2 | 7.9 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.7 | 10.2 | 12 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9 | 10.6 | 10.6
56 | -180 | -6.6 | 0 | 0 | 10.5 | 10.3 | 10.9 | 11.8 | 12 | 7.8 | 21.5 | 7.7 | 1.6 | 248 | 5.8 | 8.5 | 6.7 | 7.8 | 9.1 | 8.4 | 9.6 | 9.5 | 9.2 | 7.9 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.3 | 12 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9 | 10.6 | 10.6
57 | -179 | -6.4 | 0 | 0 | 10.5 | 10.3 | 10.9 | 11.8 | 12 | 7.8 | 21.5 | 7.7 | 1.6 | 242.2 | 5.4 | 8.5 | 6.7 | 7.8 | 9.1 | 8.4 | 9.6 | 9.5 | 9.2 | 7.9 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.3 | 12 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 10 | 10.6 | 10.6
58 | -178 | -6.1 | 0 | 0 | 10.5 | 10.3 | 10.9 | 11.8 | 12 | 7.8 | 21.5 | 7.7 | 1.6 | 249.7 | 5.3 | 8.5 | 6.8 | 7.8 | 9.1 | 8.4 | 9.6 | 9.5 | 9.2 | 7.9 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.3 | 12 | 12.1 | 11.7 | 11.1 | 10.3 | 12.1 | 9.9 | 10.6 | 10.6
59 | -177 | -6.3 | 0 | 0 | 10.5 | 10.3 | 10.9 | 11.8 | 12 | 7.8 | 21.5 | 7.7 | 1.6 | 247.8 | 5.7 | 8.5 | 6.8 | 7.8 | 9.1 | 8.4 | 9.6 | 9.5 | 9.2 | 7.9 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.3 | 12 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9 | 10.6 | 10.6
60 | -176 | -6.3 | 0 | 0 | 10.6 | 10.3 | 10.9 | 11.8 | 12 | 7.8 | 21.5 | 7.7 | 1.4 | 240 | 6.3 | 8.5 | 6.8 | 7.8 | 9.1 | 8.4 | 9.6 | 9.5 | 9.2 | 7.9 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.3 | 12 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9 | 10.6 | 10.6
61 | -175 | -6.1 | 0 | 0 | 10.5 | 10.3 | 10.9 | 11.8 | 12 | 7.8 | 21.5 | 7.7 | 1.4 | 244.9 | 6.7 | 8.5 | 6.8 | 7.8 | 9.1 | 8.4 | 9.6 | 9.5 | 9.2 | 7.9 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.3 | 12 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9 | 10.6 | 10.6
62 | -174 | -5.7 | 0 | 0 | 10.6 | 10.3 | 10.9 | 11.8 | 12 | 7.7 | 21.5 | 7.7 | 1.5 | 244.1 | 6.7 | 8.4 | 6.8 | 7.8 | 9.1 | 8.4 | 9.6 | 9.5 | 9.2 | 7.9 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.3 | 12 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9 | 10.6 | 10.6
63 | -173 | -5.8 | 0 | 0 | 10.6 | 10.3 | 10.9 | 11.8 | 12.1 | 7.7 | 21.5 | 7.7 | 1.7 | 239.2 | 6.9 | 8.5 | 6.8 | 7.8 | 9.1 | 8.4 | 9.6 | 9.5 | 9.2 | 7.9 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.3 | 12 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9 | 10.6 | 10.6
64 | -172 | -6.1 | 0 | 0 | 10.6 | 10.4 | 10.9 | 11.8 | 12.1 | 7.8 | 21.5 | 7.7 | 1.7 | 237.2 | 7 | 8.5 | 6.8 | 7.8 | 9.1 | 8.4 | 9.7 | 9.5 | 9.2 | 7.9 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.3 | 12 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 10 | 10.6 | 10.6
65 | -171 | -6.3 | 0 | 0 | 10.6 | 10.4 | 10.9 | 11.8 | 12.1 | 7.7 | 21.5 | 7.7 | 1.7 | 243.8 | 6.9 | 8.5 | 6.8 | 7.8 | 9.1 | 8.4 | 9.6 | 9.5 | 9.2 | 7.9 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.3 | 12 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9 | 10.6 | 10.6
66 | -170 | -6.4 | 0 | 0 | 10.6 | 10.4 | 10.9 | 11.8 | 12.1 | 7.7 | 21.5 | 7.7 | 1.8 | 256.1 | 6.3 | 8.5 | 6.8 | 7.8 | 9.1 | 8.4 | 9.6 | 9.5 | 9.2 | 7.9 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.3 | 12 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9 | 10.6 | 10.6
67 | -169 | -6.5 | 0 | 0 | 10.6 | 10.4 | 10.9 | 11.8 | 12.1 | 7.7 | 21.5 | 7.7 | 1.8 | 252.8 | 5.5 | 8.5 | 6.8 | 7.8 | 9.1 | 8.4 | 9.6 | 9.5 | 9.2 | 7.9 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.3 | 12 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9 | 10.6 | 10.6
68 | -168 | -6.5 | 0 | 0 | 10.5 | 10.4 | 11 | 11.8 | 12.1 | 7.7 | 21.5 | 7.7 | 1.8 | 260.7 | 4.9 | 8.5 | 6.8 | 7.8 | 9.1 | 8.4 | 9.7 | 9.5 | 9.2 | 7.9 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.2 | 12 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9 | 10.6 | 10.6
69 | -167 | -6.6 | 0 | 0 | 10.5 | 10.5 | 11 | 11.8 | 12.1 | 7.7 | 21.5 | 7.7 | 1.5 | 260 | 4.5 | 8.5 | 6.8 | 7.8 | 9.1 | 8.4 | 9.6 | 9.5 | 9.2 | 7.9 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.2 | 12 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9 | 10.6 | 10.6
70 | -166 | -6.7 | 0 | 0 | 10.5 | 10.5 | 11 | 11.8 | 12.1 | 7.7 | 21.5 | 7.8 | 1.6 | 261.4 | 4.2 | 8.5 | 6.8 | 7.8 | 9.1 | 8.4 | 9.7 | 9.5 | 9.2 | 7.9 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.2 | 12 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 10 | 10.6 | 10.6
71 | -165 | -6.7 | 0 | 0 | 10.5 | 10.5 | 11 | 11.8 | 12.1 | 7.7 | 21.5 | 7.8 | 1.5 | 263.6 | 4.1 | 8.5 | 6.8 | 7.8 | 9.1 | 8.4 | 9.7 | 9.5 | 9.2 | 7.9 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.2 | 12 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 10 | 10.6 | 10.6
72 | -164 | -6.7 | 0 | 0 | 10.5 | 10.5 | 11.1 | 11.8 | 12.1 | 7.7 | 21.5 | 7.8 | 1.5 | 269.5 | 4.1 | 8.5 | 6.8 | 7.8 | 9.1 | 8.4 | 9.7 | 9.5 | 9.2 | 7.9 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.2 | 12 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 10 | 10.6 | 10.6
73 | -163 | -6.5 | 0 | 0 | 10.5 | 10.5 | 11.1 | 11.8 | 12.1 | 7.7 | 21.5 | 7.8 | 1.7 | 266.3 | 4.1 | 8.5 | 6.8 | 7.8 | 9.1 | 8.4 | 9.7 | 9.5 | 9.2 | 7.9 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.2 | 12 | 12.1 | 11.7 | 11.1 | 10.1 | 12.1 | 9.9 | 10.6 | 10.6
74 | -162 | -5.9 | 0 | 0 | 10.5 | 10.5 | 11.1 | 11.8 | 12.1 | 7.7 | 21.5 | 7.8 | 1.7 | 263.3 | 4.2 | 8.5 | 6.8 | 7.8 | 9.1 | 8.4 | 9.7 | 9.5 | 9.2 | 7.9 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.2 | 12 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 10 | 10.6 | 10.6
75 | -161 | -6.1 | 0 | 0 | 10.5 | 10.5 | 11.1 | 11.8 | 12.1 | 7.7 | 21.5 | 7.8 | 2 | 255.9 | 4.2 | 8.5 | 6.8 | 7.8 | 9.1 | 8.4 | 9.7 | 9.5 | 9.2 | 7.9 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.2 | 12 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 10 | 10.6 | 10.6
76 | -160 | -6.1 | 0 | 0 | 10.5 | 10.4 | 11.1 | 11.8 | 12.1 | 7.7 | 21.5 | 7.8 | 1.9 | 254.8 | 3.8 | 8.5 | 6.8 | 7.8 | 9.1 | 8.4 | 9.7 | 9.5 | 9.2 | 7.9 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 10 | 10.6 | 10.6
77 | -159 | -6 | 0 | 0 | 10.5 | 10.4 | 11.1 | 11.8 | 12.1 | 7.7 | 21.5 | 7.8 | 2 | 259.9 | 3.4 | 8.5 | 6.8 | 7.8 | 9.1 | 8.4 | 9.7 | 9.5 | 9.2 | 7.9 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.2 | 12 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 10 | 10.6 | 10.6
78 | -158 | -6.4 | 0 | 0 | 10.5 | 10.4 | 11.1 | 11.8 | 12.1 | 7.7 | 21.5 | 7.8 | 2 | 265 | 3.3 | 8.5 | 6.8 | 7.8 | 9.1 | 8.4 | 9.7 | 9.5 | 9.2 | 7.9 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.2 | 12 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9 | 10.6 | 10.6
79 | -157 | -6.5 | 0 | 0 | 10.5 | 10.4 | 11.1 | 11.8 | 12.1 | 7.6 | 21.5 | 7.8 | 1.8 | 266.1 | 3.4 | 8.5 | 6.8 | 7.8 | 9.1 | 8.4 | 9.7 | 9.5 | 9.1 | 7.9 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9 | 10.6 | 10.6
80 | -156 | -6.6 | 0 | 0 | 10.5 | 10.4 | 11.1 | 11.8 | 12.1 | 7.6 | 21.5 | 7.8 | 1.8 | 265 | 3.5 | 8.5 | 6.8 | 7.8 | 9.1 | 8.4 | 9.7 | 9.5 | 9.2 | 7.9 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.2 | 12 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 10 | 10.6 | 10.6
81 | -155 | -6.6 | 0 | 0 | 10.5 | 10.4 | 11.1 | 11.8 | 12.1 | 7.6 | 21.5 | 7.8 | 1.8 | 260 | 3.3 | 8.5 | 6.8 | 7.8 | 9.1 | 8.4 | 9.7 | 9.5 | 9.2 | 7.9 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.2 | 12 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9 | 10.6 | 10.6
82 | -154 | -6.6 | 0 | 0 | 10.4 | 10.4 | 11.1 | 11.8 | 12.1 | 7.6 | 21.5 | 7.8 | 2 | 257.4 | 3.3 | 8.5 | 6.8 | 7.8 | 9.1 | 8.4 | 9.7 | 9.5 | 9.2 | 7.9 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.2 | 12 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9 | 10.6 | 10.6
83 | -153 | -6.4 | 0 | 0 | 10.4 | 10.4 | 11.1 | 11.8 | 12.1 | 7.6 | 21.5 | 7.8 | 2 | 258.4 | 3.5 | 8.5 | 6.8 | 7.8 | 9.1 | 8.4 | 9.7 | 9.5 | 9.2 | 8 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.2 | 12 | 12.1 | 11.7 | 11.1 | 10.1 | 12.1 | 10 | 10.6 | 10.6
84 | -152 | -6.3 | 0 | 0 | 10.5 | 10.4 | 11.1 | 11.8 | 12.1 | 7.6 | 21.5 | 7.8 | 1.9 | 276 | 3.9 | 8.5 | 6.8 | 7.8 | 9.1 | 8.4 | 9.7 | 9.5 | 9.1 | 8 | 9.5 | 10 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.2 | 12 | 12.1 | 11.7 | 11.1 | 10.1 | 12.1 | 9.9 | 10.6 | 10.6
85 | -151 | -6.5 | 0 | 0 | 10.5 | 10.4 | 11.1 | 11.8 | 12.1 | 7.6 | 21.5 | 7.8 | 2 | 283.8 | 4.1 | 8.5 | 6.8 | 7.8 | 9.1 | 8.4 | 9.7 | 9.5 | 9.1 | 8 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.2 | 12 | 12.1 | 11.7 | 11.1 | 10.1 | 12.1 | 9.9 | 10.6 | 10.6
86 | -150 | -6.5 | 0 | 0 | 10.5 | 10.4 | 11.1 | 11.8 | 12.1 | 7.7 | 21.5 | 7.8 | 1.8 | 247.5 | 4.4 | 8.5 | 6.8 | 7.8 | 9.1 | 8.4 | 9.7 | 9.5 | 9.1 | 8 | 9.5 | 10 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1 | 11.7 | 11 | 10.1 | 12.1 | 9.9 | 10.6 | 10.6
87 | -149 | -6.4 | 0 | 0 | 10.5 | 10.4 | 11.1 | 11.8 | 12.1 | 7.7 | 21.5 | 7.8 | 1.8 | 239.7 | 5 | 8.5 | 6.8 | 7.8 | 9.1 | 8.4 | 9.6 | 9.5 | 9.1 | 8 | 9.5 | 10 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.2 | 12 | 12.1 | 11.7 | 11.1 | 10.1 | 12.1 | 9.9 | 10.6 | 10.6
88 | -148 | -6.4 | 0 | 0 | 10.5 | 10.4 | 11.1 | 11.8 | 12.1 | 7.7 | 21.5 | 7.8 | 1.8 | 259.5 | 5.7 | 8.5 | 6.8 | 7.8 | 9.1 | 8.4 | 9.7 | 9.5 | 9.1 | 8 | 9.5 | 10 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.2 | 12 | 12.1 | 11.7 | 11.1 | 10.1 | 12.1 | 10 | 10.6 | 10.6
89 | -147 | -6.2 | 0 | 0 | 10.5 | 10.4 | 11.1 | 11.8 | 12.1 | 7.7 | 21.5 | 7.8 | 1.8 | 254.1 | 5.9 | 8.5 | 6.8 | 7.8 | 9.1 | 8.4 | 9.6 | 9.5 | 9.2 | 8 | 9.5 | 10 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.2 | 12 | 12.1 | 11.7 | 11 | 10.1 | 12.1 | 9.9 | 10.6 | 10.6
90 | -146 | -6 | 0 | 0 | 10.5 | 10.4 | 11.1 | 11.8 | 12.1 | 7.7 | 21.5 | 7.8 | 1.7 | 248.7 | 5.7 | 8.5 | 6.8 | 7.8 | 9.1 | 8.4 | 9.7 | 9.5 | 9.2 | 8 | 9.5 | 10 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.2 | 12 | 12.1 | 11.7 | 11 | 10 | 12.1 | 9.9 | 10.6 | 10.6
91 | -145 | -6 | 0 | 0 | 10.5 | 10.4 | 11.1 | 11.8 | 12.1 | 7.7 | 21.5 | 7.8 | 2 | 249.1 | 5.5 | 8.5 | 6.8 | 7.8 | 9.1 | 8.4 | 9.6 | 9.5 | 9.2 | 8 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.2 | 12 | 12.1 | 11.7 | 11 | 10 | 12.1 | 9.9 | 10.6 | 10.6
92 | -144 | -6.3 | 0 | 0 | 10.5 | 10.4 | 11.1 | 11.8 | 12.1 | 7.7 | 21.5 | 7.8 | 2 | 252.1 | 5.3 | 8.5 | 6.8 | 7.8 | 9.1 | 8.4 | 9.7 | 9.5 | 9.2 | 8 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.2 | 12 | 12.1 | 11.7 | 11 | 10 | 12.1 | 10 | 10.6 | 10.6
93 | -143 | -6.3 | 0 | 0 | 10.5 | 10.5 | 11.1 | 11.8 | 12.1 | 7.7 | 21.5 | 7.8 | 2.1 | 254.9 | 5.1 | 8.5 | 6.8 | 7.8 | 9.1 | 8.4 | 9.7 | 9.5 | 9.2 | 8 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.2 | 12 | 12.1 | 11.7 | 11 | 10 | 12.1 | 9.9 | 10.6 | 10.6
94 | -142 | -6.4 | 0 | 0 | 10.6 | 10.5 | 11.1 | 11.8 | 12.1 | 7.7 | 21.5 | 7.8 | 2.1 | 250.7 | 5 | 8.5 | 6.8 | 7.8 | 9.1 | 8.4 | 9.6 | 9.5 | 9.2 | 8 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.2 | 12 | 12.1 | 11.7 | 11 | 10.1 | 12.1 | 9.9 | 10.6 | 10.6
95 | -141 | -6.4 | 0 | 0 | 10.6 | 10.5 | 11 | 11.8 | 12.1 | 7.7 | 21.5 | 7.8 | 2 | 241.1 | 5.2 | 8.5 | 6.8 | 7.8 | 9.1 | 8.4 | 9.6 | 9.5 | 9.2 | 8 | 9.5 | 10 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1 | 11.7 | 11 | 10.1 | 12.1 | 10 | 10.6 | 10.6
96 | -140 | -6.5 | 0 | 0 | 10.6 | 10.4 | 11 | 11.8 | 12.1 | 7.7 | 21.5 | 7.8 | 1.9 | 248.1 | 5.1 | 8.5 | 6.8 | 7.8 | 9.1 | 8.4 | 9.6 | 9.5 | 9.2 | 8 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.2 | 12 | 12.1 | 11.7 | 11 | 10.1 | 12.1 | 10 | 10.6 | 10.6
97 | -139 | -6.5 | 0 | 0 | 10.6 | 10.4 | 11 | 11.8 | 12.1 | 7.7 | 21.5 | 7.8 | 1.7 | 252.5 | 5 | 8.5 | 6.9 | 7.8 | 9.1 | 8.4 | 9.6 | 9.5 | 9.2 | 8 | 9.5 | 10 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.2 | 12 | 12.1 | 11.7 | 11 | 10.1 | 12.1 | 10 | 10.6 | 10.6
98 | -138 | -6.4 | 0 | 0 | 10.6 | 10.4 | 11 | 11.8 | 12.1 | 7.7 | 21.5 | 7.8 | 1.9 | 253.5 | 4.6 | 8.5 | 6.9 | 7.8 | 9 | 8.4 | 9.6 | 9.5 | 9.2 | 7.9 | 9.5 | 10 | 11.7 | 12.3 | 12.3 | 13.4 | 11.9 | 10.8 | 10.2 | 12 | 12.1 | 11.7 | 11 | 10.1 | 12.1 | 9.9 | 10.6 | 10.6
99 | -137 | -6.3 | 0 | 0 | 10.6 | 10.4 | 10.9 | 11.8 | 12.1 | 7.7 | 21.5 | 7.8 | 2.1 | 249.9 | 4.3 | 8.5 | 6.9 | 7.8 | 9 | 8.4 | 9.6 | 9.5 | 9.2 | 8 | 9.5 | 10 | 11.7 | 12.3 | 12.3 | 13.4 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1 | 11.7 | 11 | 10.1 | 12.1 | 10 | 10.6 | 10.6
100 | -136 | -6.3 | 0 | 0 | 10.6 | 10.4 | 10.9 | 11.8 | 12.1 | 7.8 | 21.5 | 7.9 | 2 | 242.2 | 4.2 | 8.5 | 6.9 | 7.9 | 9.1 | 8.4 | 9.7 | 9.5 | 9.2 | 8 | 9.5 | 10 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.2 | 12 | 12.1 | 11.7 | 11 | 10.2 | 12.1 | 10 | 10.6 | 10.6
101 | -135 | -6.4 | 0 | 0 | 10.6 | 10.4 | 10.9 | 11.8 | 12.1 | 7.8 | 21.5 | 7.8 | 2.1 | 243.7 | 4.2 | 8.5 | 6.9 | 7.9 | 9.1 | 8.4 | 9.6 | 9.5 | 9.2 | 8 | 9.5 | 10 | 11.7 | 12.3 | 12.3 | 13.4 | 11.9 | 10.8 | 10.2 | 12 | 12.1 | 11.7 | 11 | 10.2 | 12.1 | 10 | 10.6 | 10.6
102 | -134 | -6.6 | 0 | 0 | 10.6 | 10.4 | 10.9 | 11.8 | 12.1 | 7.8 | 21.5 | 7.8 | 1.9 | 247.1 | 4.3 | 8.5 | 6.9 | 7.9 | 9.1 | 8.4 | 9.6 | 9.5 | 9.2 | 8 | 9.5 | 10 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.2 | 12 | 12.1 | 11.7 | 11 | 10.2 | 12.1 | 10 | 10.6 | 10.6
103 | -133 | -6.5 | 0 | 0 | 10.6 | 10.4 | 10.9 | 11.8 | 12.1 | 7.8 | 21.5 | 7.8 | 1.9 | 247.3 | 4.5 | 8.5 | 6.9 | 7.9 | 9.1 | 8.4 | 9.6 | 9.5 | 9.2 | 8 | 9.5 | 10 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.2 | 12 | 12.1 | 11.7 | 11 | 10.2 | 12.1 | 10 | 10.6 | 10.6
104 | -132 | -6.5 | 0 | 0 | 10.6 | 10.4 | 10.8 | 11.8 | 12.1 | 7.8 | 21.5 | 7.8 | 2 | 240.1 | 4.5 | 8.5 | 6.8 | 7.9 | 9.1 | 8.4 | 9.7 | 9.5 | 9.2 | 8 | 9.5 | 10 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9 | 10.6 | 10.6
105 | -131 | -6.6 | 0 | 0 | 10.6 | 10.4 | 10.8 | 11.8 | 12.1 | 7.8 | 21.5 | 7.8 | 2.1 | 244.2 | 3.9 | 8.5 | 6.8 | 7.8 | 9.1 | 8.4 | 9.6 | 9.5 | 9.2 | 8 | 9.5 | 10 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.2 | 12 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9 | 10.6 | 10.6
106 | -130 | -6.5 | 0 | 0 | 10.6 | 10.4 | 10.8 | 11.8 | 12.1 | 7.8 | 21.5 | 7.8 | 2.2 | 250.8 | 3.8 | 8.5 | 6.8 | 7.8 | 9.1 | 8.4 | 9.7 | 9.5 | 9.2 | 8 | 9.5 | 10 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.2 | 12 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 10 | 10.6 | 10.6
107 | -129 | -6.7 | 0 | 0 | 10.6 | 10.4 | 10.8 | 11.8 | 12.1 | 7.8 | 21.5 | 7.8 | 1.9 | 241.2 | 3.8 | 8.5 | 6.8 | 7.8 | 9.1 | 8.4 | 9.6 | 9.5 | 9.2 | 8 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.2 | 12 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 10 | 10.6 | 10.6
108 | -128 | -6.5 | 0 | 0 | 10.6 | 10.4 | 10.8 | 11.8 | 12.1 | 7.8 | 21.5 | 7.8 | 1.8 | 234.5 | 3.6 | 8.5 | 6.8 | 7.8 | 9.1 | 8.4 | 9.7 | 9.5 | 9.2 | 8 | 9.5 | 10 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.2 | 12 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 10 | 10.6 | 10.6
109 | -127 | -6.4 | 0 | 0 | 10.6 | 10.4 | 10.8 | 11.8 | 12.1 | 7.8 | 21.5 | 7.8 | 1.9 | 230.9 | 3.2 | 8.5 | 6.8 | 7.8 | 9.1 | 8.4 | 9.7 | 9.5 | 9.2 | 8 | 9.5 | 10 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.3 | 12 | 12.1 | 11.7 | 11 | 10.2 | 12.1 | 10 | 10.6 | 10.6
110 | -126 | -6.5 | 0 | 0 | 10.6 | 10.4 | 10.8 | 11.8 | 12.1 | 7.8 | 21.5 | 7.8 | 1.7 | 246.1 | 2.9 | 8.5 | 6.8 | 7.8 | 9.1 | 8.4 | 9.7 | 9.5 | 9.2 | 8 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.3 | 12 | 12.1 | 11.7 | 11 | 10.2 | 12.1 | 10 | 10.6 | 10.6
111 | -125 | -6.5 | 0 | 0 | 10.6 | 10.4 | 10.8 | 11.8 | 12.1 | 7.8 | 21.5 | 7.8 | 1.7 | 255.3 | 2.9 | 8.5 | 6.8 | 7.7 | 9.1 | 8.4 | 9.7 | 9.5 | 9.2 | 8 | 9.5 | 10 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.2 | 12 | 12.1 | 11.7 | 11 | 10.2 | 12.1 | 10 | 10.6 | 10.6
112 | -124 | -6.4 | 0 | 0 | 10.6 | 10.4 | 10.7 | 11.8 | 12.1 | 7.8 | 21.5 | 7.8 | 1.6 | 245.8 | 3.1 | 8.5 | 6.8 | 7.7 | 9.1 | 8.4 | 9.7 | 9.5 | 9.2 | 7.9 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.2 | 12 | 12.1 | 11.7 | 11 | 10.2 | 12.1 | 10 | 10.6 | 10.6
113 | -123 | -6.2 | 0 | 0 | 10.5 | 10.4 | 10.8 | 11.8 | 12.1 | 7.8 | 21.5 | 7.8 | 1.7 | 236 | 3.1 | 8.5 | 6.9 | 7.7 | 9.1 | 8.4 | 9.7 | 9.5 | 9.2 | 8 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.3 | 12 | 12.1 | 11.7 | 11 | 10.2 | 12.1 | 10 | 10.6 | 10.6
114 | -122 | -6.2 | 0 | 0 | 10.5 | 10.4 | 10.8 | 11.8 | 12.1 | 7.8 | 21.5 | 7.8 | 1.7 | 225.1 | 3.4 | 8.5 | 6.9 | 7.7 | 9.1 | 8.4 | 9.7 | 9.5 | 9.2 | 8 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.3 | 12 | 12.1 | 11.7 | 11 | 10.2 | 12.1 | 10 | 10.6 | 10.6
115 | -121 | -5.9 | 0 | 0 | 10.5 | 10.4 | 10.8 | 11.8 | 12.1 | 7.8 | 21.5 | 7.8 | 1.7 | 234.8 | 3.6 | 8.5 | 6.9 | 7.6 | 9.1 | 8.4 | 9.7 | 9.5 | 9.2 | 8 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.3 | 12 | 12.1 | 11.7 | 11 | 10.2 | 12.1 | 10 | 10.6 | 10.6
116 | -120 | -5.8 | 0 | 0 | 10.5 | 10.4 | 10.8 | 11.8 | 12.1 | 7.8 | 21.5 | 7.8 | 1.7 | 248.4 | 4.8 | 8.5 | 6.9 | 7.6 | 9.1 | 8.4 | 9.7 | 9.5 | 9.2 | 8 | 9.5 | 10 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.2 | 12 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 10 | 10.6 | 10.6
117 | -119 | -6.2 | 0 | 0 | 10.5 | 10.4 | 10.8 | 11.8 | 12.1 | 7.8 | 21.5 | 7.8 | 1.7 | 239 | 4.8 | 8.5 | 6.9 | 7.6 | 9.1 | 8.4 | 9.7 | 9.5 | 9.2 | 8 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.3 | 12 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 10 | 10.6 | 10.6
118 | -118 | -6.5 | 0 | 0 | 10.4 | 10.4 | 10.8 | 11.8 | 12 | 7.8 | 21.5 | 7.8 | 1.8 | 213.3 | 4.1 | 8.5 | 6.9 | 7.6 | 9.1 | 8.4 | 9.7 | 9.5 | 9.2 | 8 | 9.5 | 10 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.2 | 12 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9 | 10.6 | 10.6
119 | -117 | -6.4 | 0 | 0 | 10.4 | 10.4 | 10.9 | 11.8 | 12 | 7.8 | 21.5 | 7.8 | 1.6 | 222.5 | 3.7 | 8.5 | 6.9 | 7.6 | 9.1 | 8.4 | 9.7 | 9.5 | 9.2 | 8 | 9.5 | 10 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.2 | 12 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9 | 10.6 | 10.6
120 | -116 | -6.1 | 0 | 0 | 10.4 | 10.4 | 10.9 | 11.8 | 12 | 7.8 | 21.5 | 7.8 | 1.4 | 248.8 | 3.9 | 8.5 | 6.9 | 7.6 | 9.1 | 8.4 | 9.7 | 9.5 | 9.2 | 8 | 9.5 | 10 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.2 | 12 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 10 | 10.6 | 10.6
121 | -115 | -6.1 | 0 | 0 | 10.4 | 10.4 | 10.9 | 11.8 | 12 | 7.8 | 21.5 | 7.8 | 1.8 | 235.7 | 4.3 | 8.5 | 6.9 | 7.6 | 9.1 | 8.4 | 9.7 | 9.5 | 9.2 | 8 | 9.5 | 10 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.2 | 12 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9 | 10.6 | 10.6
122 | -114 | -6.3 | 0 | 0 | 10.4 | 10.4 | 11 | 11.8 | 12 | 7.8 | 21.5 | 7.8 | 1.7 | 239.1 | 4.1 | 8.5 | 6.9 | 7.6 | 9.1 | 8.4 | 9.7 | 9.5 | 9.2 | 8 | 9.5 | 10 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.2 | 12 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 10 | 10.6 | 10.6
123 | -113 | -6.2 | 0 | 0 | 10.4 | 10.4 | 11 | 11.8 | 12.1 | 7.8 | 21.5 | 7.8 | 1.7 | 239.3 | 3.6 | 8.5 | 6.9 | 7.6 | 9.1 | 8.4 | 9.7 | 9.5 | 9.2 | 8 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.2 | 12 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 10 | 10.6 | 10.6
124 | -112 | -5.7 | 0 | 0 | 10.4 | 10.4 | 11 | 11.8 | 12 | 7.8 | 21.5 | 7.8 | 1.9 | 241 | 3.9 | 8.5 | 6.9 | 7.6 | 9.1 | 8.4 | 9.7 | 9.5 | 9.2 | 8 | 9.5 | 10 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.3 | 12 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 10 | 10.6 | 10.6
125 | -111 | -5.9 | 0 | 0 | 10.4 | 10.4 | 11 | 11.8 | 12 | 7.8 | 21.5 | 7.8 | 1.9 | 234.1 | 4.4 | 8.5 | 6.8 | 7.6 | 9.1 | 8.4 | 9.7 | 9.5 | 9.2 | 8 | 9.5 | 10 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.2 | 12 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9 | 10.6 | 10.6
126 | -110 | -6.1 | 0 | 0 | 10.5 | 10.4 | 11 | 11.8 | 12 | 7.8 | 21.5 | 7.8 | 2 | 257.8 | 4.4 | 8.5 | 6.8 | 7.6 | 9.1 | 8.4 | 9.7 | 9.5 | 9.2 | 8 | 9.5 | 10 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.9 | 10.2 | 12 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9 | 10.6 | 10.6
127 | -109 | -6.3 | 0 | 0 | 10.5 | 10.4 | 11 | 11.8 | 12 | 7.8 | 21.5 | 7.8 | 2 | 269.8 | 4 | 8.5 | 6.8 | 7.5 | 9.1 | 8.4 | 9.7 | 9.5 | 9.2 | 8 | 9.5 | 10 | 11.7 | 12.3 | 12.3 | 13.4 | 11.9 | 10.8 | 10.2 | 12 | 12.1 | 11.7 | 11.1 | 10.1 | 12.1 | 9.9 | 10.6 | 10.6
128 | -108 | -6.4 | 0 | 0 | 10.5 | 10.4 | 11.1 | 11.8 | 12 | 7.9 | 21.5 | 7.8 | 1.8 | 259.6 | 3.5 | 8.5 | 6.8 | 7.5 | 9.1 | 8.4 | 9.7 | 9.5 | 9.2 | 8 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.9 | 10.3 | 12 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 10 | 10.6 | 10.6
129 | -107 | -6.2 | 0 | 0 | 10.5 | 10.4 | 11.1 | 11.8 | 12 | 7.9 | 21.5 | 7.8 | 1.7 | 253.3 | 3.3 | 8.5 | 6.8 | 7.5 | 9.1 | 8.4 | 9.7 | 9.5 | 9.2 | 8 | 9.5 | 10.1 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.9 | 10.3 | 12 | 12.1 | 11.7 | 11 | 10.2 | 12.1 | 10 | 10.6 | 10.6
130 | -106 | -6.2 | 0 | 0 | 10.6 | 10.4 | 11.1 | 11.8 | 12 | 7.9 | 21.5 | 7.9 | 1.6 | 264.1 | 3.4 | 8.5 | 6.8 | 7.5 | 9.1 | 8.4 | 9.7 | 9.5 | 9.2 | 8 | 9.5 | 10 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1 | 11.7 | 11 | 10.1 | 12.1 | 10 | 10.6 | 10.6
131 | -105 | -6 | 0 | 0 | 10.6 | 10.4 | 11.1 | 11.8 | 12 | 7.9 | 21.5 | 7.9 | 1.6 | 260.3 | 3.9 | 8.5 | 6.8 | 7.5 | 9.1 | 8.4 | 9.7 | 9.5 | 9.2 | 8 | 9.5 | 10 | 11.7 | 12.3 | 12.3 | 13.4 | 11.9 | 10.8 | 10.2 | 12 | 12.1 | 11.7 | 11 | 10.1 | 12.1 | 9.9 | 10.6 | 10.6
132 | -104 | -6.2 | 0 | 0 | 10.6 | 10.4 | 11.1 | 11.8 | 12 | 7.8 | 21.5 | 7.9 | 1.5 | 263.4 | 4.2 | 8.5 | 6.8 | 7.5 | 9.1 | 8.4 | 9.7 | 9.5 | 9.2 | 8 | 9.5 | 10 | 11.7 | 12.3 | 12.3 | 13.4 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1 | 11.7 | 11 | 10.1 | 12.1 | 10 | 10.6 | 10.6
133 | -103 | -6.3 | 0 | 0 | 10.6 | 10.4 | 11.1 | 11.8 | 12 | 7.8 | 21.5 | 7.9 | 1.4 | 266.4 | 4.6 | 8.5 | 6.8 | 7.5 | 9.1 | 8.4 | 9.7 | 9.5 | 9.2 | 8 | 9.5 | 10 | 11.7 | 12.3 | 12.3 | 13.4 | 11.9 | 10.8 | 10.2 | 12 | 12.1 | 11.7 | 11 | 10.1 | 12.1 | 9.9 | 10.6 | 10.6
134 | -102 | -6.1 | 0 | 0 | 10.6 | 10.4 | 11.1 | 11.8 | 12 | 7.8 | 21.5 | 7.9 | 1.7 | 255.4 | 4.8 | 8.5 | 6.8 | 7.5 | 9.1 | 8.4 | 9.7 | 9.5 | 9.2 | 8 | 9.5 | 10 | 11.7 | 12.4 | 12.3 | 13.4 | 11.9 | 10.8 | 10.3 | 11.9 | 12.1 | 11.7 | 11 | 10.1 | 12.1 | 10 | 10.6 | 10.6
135 | -101 | -6.2 | 0 | 0 | 10.6 | 10.4 | 11.1 | 11.8 | 12 | 7.8 | 21.5 | 7.9 | 1.7 | 247.2 | 4.7 | 8.5 | 6.8 | 7.5 | 9.1 | 8.4 | 9.7 | 9.5 | 9.2 | 8 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1 | 11.7 | 11 | 10.1 | 12.1 | 10 | 10.6 | 10.6
136 | -100 | -5.7 | 0 | 0 | 10.6 | 10.4 | 11.1 | 11.8 | 12 | 7.8 | 21.5 | 7.8 | 1.7 | 246.1 | 4.2 | 8.5 | 6.8 | 7.4 | 9.1 | 8.4 | 9.7 | 9.5 | 9.2 | 8 | 9.5 | 10.1 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.9 | 10.2 | 12 | 12.1 | 11.7 | 11 | 10.1 | 12.1 | 10 | 10.6 | 10.6
137 | -99 | -5.7 | 0 | 0 | 10.6 | 10.4 | 11.1 | 11.8 | 12.1 | 7.9 | 21.5 | 7.8 | 1.9 | 245 | 3.7 | 8.5 | 6.8 | 7.5 | 9.1 | 8.4 | 9.7 | 9.5 | 9.2 | 8 | 9.5 | 10 | 11.7 | 12.3 | 12.3 | 13.4 | 11.9 | 10.9 | 10.2 | 12 | 12.1 | 11.7 | 11 | 10.1 | 12.1 | 10 | 10.6 | 10.6
138 | -98 | -6 | 0 | 0 | 10.6 | 10.4 | 11.1 | 11.8 | 12.1 | 7.8 | 21.5 | 7.9 | 2 | 245 | 3.7 | 8.5 | 6.9 | 7.4 | 9.1 | 8.4 | 9.7 | 9.5 | 9.2 | 8 | 9.5 | 10 | 11.7 | 12.3 | 12.3 | 13.4 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1 | 11.7 | 11 | 10.1 | 12.1 | 10 | 10.6 | 10.6
139 | -97 | -6.2 | 0 | 0 | 10.6 | 10.4 | 11.1 | 11.8 | 12.1 | 7.8 | 21.5 | 7.9 | 2 | 244.7 | 3.5 | 8.5 | 6.9 | 7.4 | 9.1 | 8.4 | 9.7 | 9.5 | 9.2 | 8 | 9.5 | 10 | 11.7 | 12.3 | 12.3 | 13.4 | 11.9 | 10.8 | 10.2 | 12 | 12.1 | 11.7 | 11 | 10.1 | 12.1 | 10 | 10.6 | 10.6
140 | -96 | -5.7 | 0 | 0 | 10.6 | 10.4 | 11.1 | 11.8 | 12.1 | 7.8 | 21.5 | 7.9 | 2.2 | 250.1 | 3.3 | 8.5 | 6.9 | 7.4 | 9 | 8.4 | 9.7 | 9.5 | 9.2 | 8.1 | 9.5 | 10 | 11.7 | 12.3 | 12.3 | 13.4 | 11.9 | 10.8 | 10.2 | 12 | 12.1 | 11.7 | 11 | 10.1 | 12.1 | 10 | 10.6 | 10.6
141 | -95 | -5.6 | 0 | 0 | 10.7 | 10.4 | 11 | 11.8 | 12.1 | 7.8 | 21.5 | 7.9 | 1.9 | 254.4 | 4 | 8.5 | 6.9 | 7.4 | 9 | 8.4 | 9.7 | 9.5 | 9.2 | 8.1 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1 | 11.7 | 11 | 10.1 | 12.1 | 10 | 10.6 | 10.6
142 | -94 | -6.1 | 0 | 0 | 10.6 | 10.4 | 10.9 | 11.8 | 12.1 | 7.8 | 21.5 | 7.9 | 1.9 | 242 | 4.5 | 8.5 | 6.9 | 7.5 | 9.1 | 8.4 | 9.7 | 9.5 | 9.2 | 8.1 | 9.5 | 10 | 11.7 | 12.3 | 12.3 | 13.4 | 11.9 | 10.8 | 10.2 | 12 | 12.1 | 11.7 | 11 | 10.1 | 12.1 | 10 | 10.6 | 10.6
143 | -93 | -6.4 | 0 | 0 | 10.7 | 10.4 | 10.9 | 11.8 | 12.1 | 7.8 | 21.5 | 7.9 | 1.7 | 241.3 | 4.5 | 8.5 | 6.9 | 7.5 | 9.1 | 8.4 | 9.7 | 9.5 | 9.2 | 8.1 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.9 | 10.2 | 12 | 12.1 | 11.7 | 11 | 10.1 | 12.1 | 10 | 10.6 | 10.6
144 | -92 | -6.4 | 0 | 0 | 10.7 | 10.4 | 10.8 | 11.8 | 12.1 | 7.8 | 21.5 | 7.9 | 1.9 | 246.6 | 4.5 | 8.5 | 6.9 | 7.5 | 9.1 | 8.4 | 9.7 | 9.5 | 9.2 | 8.1 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.9 | 10.2 | 12 | 12.1 | 11.7 | 11 | 10.1 | 12.1 | 10 | 10.6 | 10.6
145 | -91 | -6.3 | 0 | 0 | 10.7 | 10.4 | 10.8 | 11.8 | 12.1 | 7.8 | 21.5 | 7.9 | 2 | 236.7 | 5.1 | 8.5 | 6.9 | 7.5 | 9 | 8.4 | 9.7 | 9.5 | 9.2 | 8.1 | 9.5 | 10 | 11.7 | 12.3 | 12.3 | 13.4 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1 | 11.7 | 11 | 10.1 | 12.1 | 10 | 10.6 | 10.6
146 | -90 | -6.5 | 0 | 0 | 10.7 | 10.4 | 10.7 | 11.8 | 12.1 | 7.8 | 21.5 | 7.9 | 1.9 | 242.3 | 5.7 | 8.5 | 6.9 | 7.5 | 9.1 | 8.4 | 9.7 | 9.5 | 9.2 | 8.1 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.9 | 10.2 | 12 | 12.1 | 11.7 | 11 | 10.2 | 12.1 | 10 | 10.6 | 10.6
147 | -89 | -6.4 | 0 | 0 | 10.7 | 10.4 | 10.7 | 11.8 | 12.1 | 7.8 | 21.5 | 7.9 | 1.6 | 261.7 | 5.7 | 8.5 | 6.9 | 7.5 | 9 | 8.4 | 9.7 | 9.5 | 9.2 | 8.1 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.9 | 10.2 | 11.9 | 12.1 | 11.7 | 11 | 10.1 | 12.1 | 10 | 10.6 | 10.6
148 | -88 | -6.5 | 0 | 0 | 10.7 | 10.4 | 10.8 | 11.8 | 12.1 | 7.8 | 21.5 | 7.9 | 1.7 | 258.3 | 5.4 | 8.5 | 6.9 | 7.5 | 9 | 8.4 | 9.7 | 9.5 | 9.2 | 8.1 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.8 | 10.2 | 12 | 12.1 | 11.7 | 11 | 10.1 | 12.1 | 10 | 10.6 | 10.6
149 | -87 | -6.6 | 0 | 0 | 10.6 | 10.4 | 10.8 | 11.8 | 12.1 | 7.8 | 21.5 | 7.9 | 1.6 | 237.8 | 6.2 | 8.5 | 6.9 | 7.5 | 9 | 8.4 | 9.7 | 9.5 | 9.2 | 8.1 | 9.5 | 10 | 11.7 | 12.3 | 12.3 | 13.4 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1 | 11.7 | 11 | 10.1 | 12.1 | 10 | 10.6 | 10.6
150 | -86 | -6.5 | 0 | 0 | 10.6 | 10.4 | 10.8 | 11.8 | 12.1 | 7.8 | 21.5 | 7.9 | 1.6 | 246.5 | 6.8 | 8.5 | 6.9 | 7.5 | 9 | 8.4 | 9.7 | 9.5 | 9.2 | 8.1 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1 | 11.7 | 11 | 10.2 | 12.1 | 9.9 | 10.6 | 10.6
151 | -85 | -6.3 | 0 | 0 | 10.7 | 10.4 | 10.9 | 11.8 | 12.1 | 7.8 | 21.5 | 7.9 | 1.7 | 243.3 | 7.1 | 8.5 | 6.8 | 7.5 | 9 | 8.4 | 9.7 | 9.5 | 9.2 | 8.1 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.8 | 10.1 | 11.9 | 12.1 | 11.7 | 11 | 10.2 | 12.1 | 9.9 | 10.6 | 10.6
152 | -84 | -6.2 | 0 | 0 | 10.7 | 10.4 | 10.9 | 11.8 | 12.1 | 7.8 | 21.5 | 7.9 | 1.7 | 242.3 | 7.2 | 8.5 | 6.8 | 7.5 | 9.1 | 8.4 | 9.7 | 9.5 | 9.2 | 8.1 | 9.5 | 10 | 11.7 | 12.4 | 12.2 | 13.4 | 11.9 | 10.8 | 10.2 | 12 | 12.1 | 11.7 | 11 | 10.2 | 12.1 | 9.9 | 10.6 | 10.6
153 | -83 | -6.3 | 0 | 0 | 10.7 | 10.4 | 10.9 | 11.8 | 12.1 | 7.8 | 21.5 | 7.9 | 1.3 | 242.5 | 7.2 | 8.5 | 6.8 | 7.6 | 9 | 8.4 | 9.7 | 9.5 | 9.2 | 8.1 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.9 | 10.2 | 12 | 12.1 | 11.7 | 11 | 10.2 | 12.1 | 10 | 10.6 | 10.6
154 | -82 | -6.5 | 0 | 0 | 10.7 | 10.4 | 10.9 | 11.8 | 12.1 | 7.8 | 21.5 | 7.9 | 1.6 | 240.4 | 7.4 | 8.5 | 6.8 | 7.6 | 9 | 8.4 | 9.7 | 9.5 | 9.2 | 8.1 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.8 | 10.2 | 12 | 12.1 | 11.7 | 11 | 10.1 | 12.1 | 10 | 10.6 | 10.6
155 | -81 | -6.5 | 0 | 0 | 10.7 | 10.3 | 10.9 | 11.8 | 12.1 | 7.8 | 21.5 | 7.9 | 1.5 | 246.4 | 7.7 | 8.5 | 6.8 | 7.6 | 9 | 8.4 | 9.7 | 9.5 | 9.2 | 8.1 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1 | 11.7 | 11 | 10.2 | 12.1 | 10 | 10.6 | 10.6
156 | -80 | -6.3 | 0 | 0 | 10.7 | 10.3 | 10.9 | 11.8 | 12.1 | 7.8 | 21.5 | 7.9 | 1.7 | 244.9 | 7.8 | 8.5 | 6.8 | 7.6 | 9 | 8.4 | 9.7 | 9.5 | 9.2 | 8.1 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.8 | 10.2 | 12 | 12.1 | 11.7 | 11 | 10.2 | 12.1 | 9.9 | 10.6 | 10.6
157 | -79 | -6.2 | 0 | 0 | 10.7 | 10.3 | 10.9 | 11.8 | 12.1 | 7.8 | 21.5 | 7.8 | 1.7 | 255.2 | 7.7 | 8.5 | 6.8 | 7.6 | 9 | 8.4 | 9.7 | 9.5 | 9.2 | 8 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.8 | 10.2 | 12 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9 | 10.6 | 10.6
158 | -78 | -6.3 | 0 | 0 | 10.7 | 10.3 | 11 | 11.8 | 12.1 | 7.9 | 21.5 | 7.8 | 1.8 | 255.6 | 7.8 | 8.5 | 6.8 | 7.6 | 9 | 8.4 | 9.7 | 9.5 | 9.2 | 8 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1 | 11.7 | 11.1 | 10.1 | 12.1 | 10 | 10.6 | 10.6
159 | -77 | -6.1 | 0 | 0 | 10.6 | 10.3 | 11 | 11.8 | 12.1 | 7.9 | 21.5 | 7.8 | 1.8 | 255.2 | 7.8 | 8.5 | 6.8 | 7.6 | 9 | 8.4 | 9.7 | 9.5 | 9.2 | 8 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.8 | 10.2 | 12 | 12.1 | 11.7 | 11.1 | 10.1 | 12.1 | 10 | 10.6 | 10.6
160 | -76 | -6.3 | 0 | 0 | 10.6 | 10.3 | 11 | 11.8 | 12.1 | 7.8 | 21.5 | 7.8 | 1.8 | 252.7 | 7.5 | 8.5 | 6.8 | 7.6 | 9 | 8.4 | 9.7 | 9.5 | 9.2 | 8 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.9 | 10.2 | 12 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 10 | 10.6 | 10.6
161 | -75 | -6.5 | 0 | 0 | 10.6 | 10.3 | 11 | 11.8 | 12.1 | 7.9 | 21.5 | 7.8 | 1.7 | 254.4 | 6.9 | 8.5 | 6.8 | 7.6 | 9 | 8.4 | 9.7 | 9.5 | 9.2 | 8 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 10 | 10.6 | 10.6
162 | -74 | -6.5 | 0 | 0 | 10.6 | 10.2 | 11 | 11.8 | 12.1 | 7.9 | 21.5 | 7.8 | 1.6 | 251.3 | 6.5 | 8.5 | 6.8 | 7.6 | 9 | 8.4 | 9.7 | 9.5 | 9.2 | 8 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.9 | 10.2 | 12 | 12.1 | 11.7 | 11 | 10.2 | 12.1 | 10 | 10.6 | 10.6
163 | -73 | -6.5 | 0 | 0 | 10.6 | 10.2 | 10.9 | 11.8 | 12.1 | 7.9 | 21.5 | 7.8 | 1.6 | 264.9 | 6.2 | 8.5 | 6.8 | 7.6 | 9 | 8.4 | 9.7 | 9.5 | 9.3 | 8 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 10 | 10.6 | 10.6
164 | -72 | -6.5 | 0 | 0 | 10.6 | 10.2 | 10.9 | 11.8 | 12.1 | 7.9 | 21.5 | 7.8 | 1.7 | 257.7 | 6.4 | 8.5 | 6.8 | 7.6 | 9 | 8.4 | 9.7 | 9.5 | 9.2 | 8 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.9 | 10.2 | 12 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 10 | 10.6 | 10.6
165 | -71 | -6.5 | 0 | 0 | 10.6 | 10.2 | 10.9 | 11.8 | 12.1 | 7.9 | 21.5 | 7.8 | 2 | 246.6 | 6.5 | 8.5 | 6.8 | 7.6 | 9 | 8.4 | 9.7 | 9.5 | 9.3 | 8 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.9 | 10.2 | 12 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 10 | 10.6 | 10.6
166 | -70 | -6.6 | 0 | 0 | 10.6 | 10.3 | 10.9 | 11.8 | 12.1 | 7.9 | 21.5 | 7.8 | 2 | 251.3 | 6.2 | 8.5 | 6.8 | 7.6 | 9 | 8.4 | 9.7 | 9.5 | 9.3 | 7.9 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.9 | 10.2 | 12 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 10 | 10.6 | 10.6
167 | -69 | -6.6 | 0 | 0 | 10.6 | 10.3 | 10.9 | 11.8 | 12.1 | 7.9 | 21.5 | 7.8 | 1.9 | 255.6 | 6 | 8.5 | 6.8 | 7.6 | 9 | 8.4 | 9.7 | 9.5 | 9.3 | 7.9 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 10 | 10.6 | 10.6
168 | -68 | -6.6 | 0 | 0 | 10.6 | 10.3 | 10.9 | 11.8 | 12.1 | 7.9 | 21.5 | 7.8 | 2 | 252.2 | 5.9 | 8.5 | 6.8 | 7.6 | 9 | 8.4 | 9.7 | 9.5 | 9.3 | 7.9 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.8 | 10.2 | 12 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 10 | 10.6 | 10.6
169 | -67 | -6.6 | 0 | 0 | 10.5 | 10.3 | 10.9 | 11.8 | 12.1 | 7.9 | 21.5 | 7.9 | 2 | 253.5 | 5.5 | 8.5 | 6.8 | 7.6 | 9 | 8.4 | 9.6 | 9.5 | 9.2 | 7.9 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 10 | 10.6 | 10.6
170 | -66 | -6.6 | 0 | 0 | 10.5 | 10.3 | 10.9 | 11.8 | 12.1 | 7.9 | 21.5 | 7.9 | 1.9 | 261.5 | 5 | 8.5 | 6.8 | 7.6 | 9 | 8.4 | 9.7 | 9.5 | 9.2 | 7.9 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 10 | 10.6 | 10.6
171 | -65 | -6.5 | 0 | 0 | 10.4 | 10.3 | 10.9 | 11.8 | 12.1 | 7.9 | 21.5 | 7.9 | 1.7 | 271.7 | 4.6 | 8.5 | 6.8 | 7.6 | 9 | 8.4 | 9.7 | 9.5 | 9.2 | 7.9 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 10 | 10.6 | 10.6
172 | -64 | -6.5 | 0 | 0 | 10.4 | 10.3 | 10.9 | 11.8 | 12 | 7.9 | 21.5 | 7.9 | 1.6 | 238.1 | 4.3 | 8.5 | 6.8 | 7.6 | 9 | 8.4 | 9.7 | 9.5 | 9.1 | 7.9 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 10 | 10.6 | 10.6
173 | -63 | -6.6 | 0 | 0 | 10.3 | 10.3 | 10.9 | 11.8 | 12 | 7.9 | 21.5 | 7.8 | 1.9 | 221.8 | 4 | 8.5 | 6.8 | 7.6 | 9 | 8.4 | 9.7 | 9.5 | 9.1 | 7.9 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 10 | 10.6 | 10.6
174 | -62 | -6.7 | 0 | 0 | 10.3 | 10.3 | 10.8 | 11.8 | 12 | 7.9 | 21.5 | 7.8 | 1.7 | 251.6 | 3.7 | 8.5 | 6.8 | 7.6 | 9 | 8.4 | 9.7 | 9.5 | 9.1 | 7.9 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 10 | 10.6 | 10.6
175 | -61 | -6.6 | 0 | 0 | 10.2 | 10.3 | 10.8 | 11.8 | 12 | 7.9 | 21.5 | 7.8 | 1.8 | 260.2 | 3.9 | 8.5 | 6.8 | 7.6 | 9 | 8.4 | 9.7 | 9.5 | 9.1 | 7.9 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.8 | 10.1 | 11.9 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 10 | 10.6 | 10.6
176 | -60 | -6.5 | 0 | 0 | 10.2 | 10.4 | 10.8 | 11.8 | 12 | 7.9 | 21.5 | 7.8 | 1.8 | 240.4 | 4.1 | 8.5 | 6.8 | 7.7 | 9 | 8.4 | 9.7 | 9.5 | 9.1 | 7.9 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1 | 11.7 | 11.1 | 10.3 | 12.1 | 10 | 10.6 | 10.6
177 | -59 | -6.5 | 0 | 0 | 10.1 | 10.4 | 10.8 | 11.8 | 12 | 7.9 | 21.5 | 7.8 | 1.5 | 230.9 | 4.4 | 8.5 | 6.8 | 7.6 | 9 | 8.4 | 9.7 | 9.5 | 9.1 | 7.9 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.8 | 10.2 | 12 | 12.1 | 11.7 | 11.1 | 10.3 | 12.1 | 10 | 10.6 | 10.6
178 | -58 | -6.4 | 0 | 0 | 10.1 | 10.3 | 10.8 | 11.8 | 12 | 7.9 | 21.5 | 7.8 | 1.7 | 235.9 | 4.8 | 8.5 | 6.9 | 7.6 | 9 | 8.4 | 9.7 | 9.5 | 9.1 | 7.9 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1 | 11.7 | 11.1 | 10.3 | 12.1 | 10 | 10.6 | 10.6
179 | -57 | -6.1 | 0 | 0 | 10.1 | 10.3 | 10.8 | 11.8 | 12 | 7.9 | 21.5 | 7.8 | 1.7 | 243 | 5 | 8.5 | 6.8 | 7.6 | 9 | 8.4 | 9.7 | 9.5 | 9.1 | 7.9 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1 | 11.7 | 11.1 | 10.3 | 12.1 | 10 | 10.6 | 10.6
180 | -56 | -6.4 | 0 | 0 | 10 | 10.3 | 10.8 | 11.8 | 12 | 7.9 | 21.5 | 7.8 | 1.8 | 242.9 | 5.8 | 8.5 | 6.8 | 7.6 | 9 | 8.4 | 9.7 | 9.5 | 9.1 | 7.9 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1 | 11.7 | 11.1 | 10.3 | 12.1 | 10 | 10.6 | 10.6
181 | -55 | -6.5 | 0 | 0 | 10 | 10.3 | 10.8 | 11.8 | 12 | 7.9 | 21.5 | 7.8 | 1.8 | 253.7 | 6 | 8.5 | 6.8 | 7.6 | 9 | 8.4 | 9.7 | 9.5 | 9.1 | 7.9 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1 | 11.7 | 11.1 | 10.3 | 12.1 | 10 | 10.6 | 10.6
182 | -54 | -6.6 | 0 | 0 | 10.1 | 10.3 | 10.8 | 11.8 | 12 | 7.9 | 21.5 | 7.8 | 1.6 | 266.3 | 6.1 | 8.5 | 6.8 | 7.6 | 9 | 8.4 | 9.7 | 9.5 | 9.1 | 7.9 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 10 | 10.6 | 10.6
183 | -53 | -6.6 | 0 | 0 | 10.1 | 10.3 | 10.8 | 11.8 | 12 | 8 | 21.5 | 7.8 | 1.8 | 259.9 | 6.3 | 8.5 | 6.8 | 7.6 | 9 | 8.4 | 9.7 | 9.5 | 9.1 | 7.9 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 10 | 10.6 | 10.6
184 | -52 | -6.7 | 0 | 0 | 10.2 | 10.3 | 10.8 | 11.8 | 12 | 8 | 21.5 | 7.8 | 1.9 | 251.8 | 6.7 | 8.5 | 6.8 | 7.6 | 9 | 8.4 | 9.7 | 9.5 | 9.1 | 7.9 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 10 | 10.6 | 10.6
185 | -51 | -6.6 | 0 | 0 | 10.2 | 10.3 | 10.8 | 11.8 | 12 | 7.9 | 21.5 | 7.8 | 1.8 | 254.6 | 7.2 | 8.5 | 6.8 | 7.6 | 9 | 8.4 | 9.7 | 9.5 | 9.1 | 7.9 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 10 | 10.6 | 10.6
186 | -50 | -6.6 | 0 | 0 | 10.3 | 10.3 | 10.8 | 11.8 | 12 | 8 | 21.5 | 7.8 | 2 | 248.7 | 7.6 | 8.5 | 6.8 | 7.6 | 9 | 8.4 | 9.6 | 9.5 | 9.1 | 7.9 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.7 | 10.2 | 11.9 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 10 | 10.6 | 10.6
187 | -49 | -6.5 | 0 | 0 | 10.3 | 10.3 | 10.8 | 11.8 | 12 | 8 | 21.5 | 7.8 | 1.9 | 247.4 | 7.7 | 8.5 | 6.8 | 7.6 | 9 | 8.4 | 9.7 | 9.5 | 9.1 | 7.9 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 10 | 10.6 | 10.6
188 | -48 | -6.3 | 0 | 0 | 10.3 | 10.3 | 10.9 | 11.8 | 12 | 8 | 21.5 | 7.8 | 1.8 | 246.7 | 7.4 | 8.5 | 6.8 | 7.6 | 9 | 8.4 | 9.7 | 9.5 | 9.1 | 7.9 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.8 | 10.1 | 11.9 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 10 | 10.6 | 10.6
189 | -47 | -6.2 | 0 | 0 | 10.4 | 10.3 | 10.9 | 11.8 | 12 | 7.9 | 21.5 | 7.8 | 1.8 | 251.4 | 7.1 | 8.5 | 6.8 | 7.6 | 9 | 8.4 | 9.6 | 9.5 | 9.1 | 7.9 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.8 | 10.1 | 11.9 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 10 | 10.6 | 10.6
190 | -46 | -6.3 | 0 | 0 | 10.4 | 10.3 | 10.9 | 11.8 | 12 | 7.9 | 21.5 | 7.8 | 1.9 | 246 | 6.5 | 8.5 | 6.8 | 7.6 | 9 | 8.4 | 9.6 | 9.5 | 9.1 | 7.9 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.8 | 10.1 | 11.9 | 12.1 | 11.7 | 11.1 | 10.1 | 12.1 | 10 | 10.6 | 10.6
191 | -45 | -6.5 | 0 | 0 | 10.4 | 10.3 | 11 | 11.8 | 12 | 7.9 | 21.5 | 7.8 | 1.8 | 244.4 | 6.5 | 8.5 | 6.8 | 7.7 | 9 | 8.4 | 9.6 | 9.5 | 9.1 | 7.9 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.8 | 10.1 | 11.9 | 12.1 | 11.7 | 11 | 10.1 | 12.1 | 10 | 10.6 | 10.6
192 | -44 | -6.7 | 0 | 0 | 10.4 | 10.3 | 11 | 11.8 | 12 | 7.9 | 21.5 | 7.9 | 1.7 | 248.6 | 6.8 | 8.5 | 6.8 | 7.7 | 9 | 8.4 | 9.6 | 9.5 | 9.1 | 7.9 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1 | 11.7 | 11 | 10.1 | 12.1 | 10 | 10.6 | 10.6
193 | -43 | -6.8 | 0 | 0 | 10.5 | 10.3 | 11 | 11.8 | 12 | 7.9 | 21.5 | 7.8 | 1.8 | 250.8 | 6.9 | 8.5 | 6.8 | 7.7 | 9 | 8.4 | 9.6 | 9.5 | 9.1 | 7.9 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.7 | 10.1 | 11.9 | 12.1 | 11.7 | 11 | 10.1 | 12.1 | 10 | 10.6 | 10.6
194 | -42 | -6.4 | 0 | 0 | 10.5 | 10.3 | 11.1 | 11.8 | 12 | 7.9 | 21.5 | 7.8 | 1.6 | 260.8 | 6.8 | 8.5 | 6.8 | 7.7 | 9 | 8.4 | 9.6 | 9.5 | 9.1 | 7.9 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.8 | 10.1 | 12 | 12.1 | 11.7 | 11 | 10.1 | 12.1 | 10 | 10.6 | 10.6
195 | -41 | -6.1 | 0 | 0 | 10.5 | 10.3 | 11.1 | 11.8 | 12 | 7.9 | 21.5 | 7.8 | 1.5 | 255.7 | 6.7 | 8.5 | 6.8 | 7.7 | 9 | 8.4 | 9.6 | 9.5 | 9.1 | 7.9 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.7 | 10.1 | 11.9 | 12.1 | 11.7 | 11 | 10.1 | 12.1 | 10 | 10.6 | 10.6
196 | -40 | -6.3 | 0 | 0 | 10.5 | 10.3 | 11.1 | 11.8 | 12 | 7.9 | 21.5 | 7.8 | 1.5 | 243.3 | 6.5 | 8.5 | 6.8 | 7.7 | 9 | 8.4 | 9.6 | 9.5 | 9.1 | 7.9 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.7 | 10.1 | 11.9 | 12.1 | 11.7 | 11 | 10.1 | 12.1 | 10 | 10.6 | 10.6
197 | -39 | -6.4 | 0 | 0 | 10.5 | 10.3 | 11.2 | 11.8 | 12 | 7.9 | 21.5 | 7.8 | 1.6 | 240 | 6.4 | 8.5 | 6.8 | 7.7 | 9 | 8.4 | 9.7 | 9.5 | 9.1 | 7.9 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.7 | 10.1 | 11.9 | 12.1 | 11.7 | 11 | 10.1 | 12.1 | 10 | 10.6 | 10.6
198 | -38 | -6.5 | 0 | 0 | 10.5 | 10.3 | 11.2 | 11.8 | 11.9 | 7.9 | 21.5 | 7.8 | 1.6 | 229.3 | 6.3 | 8.5 | 6.8 | 7.7 | 9 | 8.4 | 9.7 | 9.5 | 9.1 | 7.9 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.7 | 10.2 | 11.9 | 12.1 | 11.7 | 11 | 10.1 | 12.1 | 10 | 10.6 | 10.6
199 | -37 | -6.5 | 0 | 0 | 10.5 | 10.3 | 11.1 | 11.8 | 12 | 7.9 | 21.5 | 7.8 | 1.4 | 232.6 | 5.8 | 8.5 | 6.8 | 7.7 | 9 | 8.4 | 9.6 | 9.5 | 9.1 | 7.9 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.7 | 10.2 | 11.9 | 12.1 | 11.7 | 11 | 10.1 | 12.1 | 10 | 10.6 | 10.6
200 | -36 | -6.4 | 0 | 0 | 10.5 | 10.3 | 11.1 | 11.8 | 12 | 7.9 | 21.5 | 7.8 | 1.5 | 237.2 | 5.4 | 8.5 | 6.8 | 7.7 | 9 | 8.4 | 9.6 | 9.5 | 9.2 | 7.9 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.7 | 10.2 | 11.9 | 12.1 | 11.7 | 11 | 10.1 | 12.1 | 10 | 10.6 | 10.6
201 | -35 | -3.9 | 0 | 0 | 10.5 | 10.3 | 11.1 | 11.8 | 12 | 7.9 | 21.5 | 7.8 | 1.5 | 236.2 | 5.4 | 8.5 | 6.8 | 7.7 | 9 | 8.4 | 9.6 | 9.5 | 9.2 | 7.9 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.7 | 10.2 | 11.9 | 12.1 | 11.7 | 11 | 10.1 | 12.1 | 10 | 10.6 | 10.6
202 | -34 | -6.8 | 0 | 0 | 10.5 | 10.3 | 11 | 11.8 | 12 | 7.9 | 21.5 | 7.8 | 1.4 | 241 | 5.3 | 8.5 | 6.8 | 7.7 | 9 | 8.4 | 9.6 | 9.5 | 9.1 | 7.9 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.7 | 10.2 | 11.9 | 12.1 | 11.7 | 11.1 | 10 | 12.1 | 10 | 10.6 | 10.6
203 | -33 | -6.8 | 0 | 0 | 10.5 | 10.3 | 11 | 11.8 | 12 | 7.9 | 21.5 | 7.8 | 1.5 | 244.3 | 5.2 | 8.5 | 6.8 | 7.7 | 9 | 8.4 | 9.6 | 9.5 | 9.2 | 7.9 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.7 | 10.2 | 11.9 | 12.1 | 11.7 | 11 | 10 | 12.1 | 10 | 10.6 | 10.6
204 | -32 | -6.8 | 0 | 0 | 10.5 | 10.3 | 11 | 11.8 | 12 | 7.9 | 21.5 | 7.8 | 1.5 | 248 | 5.2 | 8.5 | 6.7 | 7.7 | 9 | 8.4 | 9.7 | 9.5 | 9.1 | 7.9 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.7 | 10.2 | 11.9 | 12.1 | 11.7 | 11 | 10 | 12.1 | 10 | 10.6 | 10.6
205 | -31 | -6.8 | 0 | 0 | 10.5 | 10.3 | 11 | 11.8 | 12 | 7.9 | 21.5 | 7.8 | 1.6 | 247.6 | 5.5 | 8.5 | 6.7 | 7.7 | 9 | 8.4 | 9.7 | 9.5 | 9.1 | 7.9 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.7 | 10.2 | 11.9 | 12.1 | 11.7 | 11 | 10 | 12.1 | 10 | 10.6 | 10.6
206 | -30 | -6.8 | 0 | 0 | 10.5 | 10.3 | 11 | 11.8 | 12 | 7.9 | 21.5 | 7.8 | 1.5 | 253 | 5.6 | 8.5 | 6.7 | 7.7 | 9 | 8.4 | 9.7 | 9.5 | 9.2 | 7.9 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1 | 11.7 | 11 | 10.1 | 12.1 | 10 | 10.6 | 10.6
207 | -29 | -6.7 | 0 | 0 | 10.5 | 10.3 | 11 | 11.7 | 12 | 7.9 | 21.5 | 7.8 | 1.6 | 251.7 | 5.5 | 8.5 | 6.7 | 7.7 | 9 | 8.4 | 9.6 | 9.4 | 9.2 | 7.9 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1 | 11.7 | 11 | 10.1 | 12.1 | 10 | 10.6 | 10.6
208 | -28 | -5.9 | 0 | 0 | 10.5 | 10.3 | 11 | 11.8 | 12 | 7.9 | 21.5 | 7.8 | 1.6 | 252.7 | 5.4 | 8.5 | 6.7 | 7.7 | 9 | 8.4 | 9.6 | 9.5 | 9.2 | 7.9 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.7 | 10.2 | 11.9 | 12.1 | 11.7 | 11 | 10.1 | 12.1 | 10 | 10.6 | 10.6
209 | -27 | -5.8 | 0 | 0 | 10.5 | 10.3 | 11 | 11.8 | 12 | 7.9 | 21.5 | 7.8 | 1.7 | 246.4 | 5.1 | 8.5 | 6.7 | 7.7 | 9 | 8.4 | 9.7 | 9.5 | 9.2 | 7.9 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.7 | 10.2 | 11.9 | 12.1 | 11.7 | 11 | 10.1 | 12.1 | 10 | 10.6 | 10.6
210 | -26 | -5.8 | 0 | 0 | 10.5 | 10.2 | 11 | 11.7 | 12 | 7.9 | 21.5 | 7.8 | 1.9 | 247.5 | 4.9 | 8.5 | 6.7 | 7.7 | 9 | 8.4 | 9.6 | 9.5 | 9.2 | 7.9 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.7 | 10.2 | 11.9 | 12.1 | 11.7 | 11 | 10.1 | 12.1 | 10 | 10.6 | 10.6
211 | -25 | -5.8 | 0 | 0 | 10.5 | 10.2 | 11.1 | 11.8 | 12 | 7.9 | 21.5 | 7.8 | 1.7 | 257.2 | 5.1 | 8.5 | 6.7 | 7.7 | 9 | 8.4 | 9.7 | 9.4 | 9.2 | 7.9 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1 | 11.7 | 11 | 10.1 | 12.1 | 10 | 10.6 | 10.6
212 | -24 | -6.7 | 0 | 0 | 10.5 | 10.2 | 11.1 | 11.8 | 12 | 7.9 | 21.5 | 7.8 | 1.6 | 254 | 5.3 | 8.5 | 6.8 | 7.6 | 9 | 8.4 | 9.6 | 9.5 | 9.2 | 7.9 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1 | 11.7 | 11.1 | 10.1 | 12.1 | 10 | 10.6 | 10.6
213 | -23 | -6.8 | 0 | 0 | 10.5 | 10.2 | 11.1 | 11.8 | 12 | 7.9 | 21.5 | 7.8 | 1.8 | 231.9 | 4.9 | 8.5 | 6.7 | 7.6 | 9 | 8.4 | 9.7 | 9.4 | 9.2 | 7.9 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.7 | 10.2 | 11.9 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 10 | 10.6 | 10.6
214 | -22 | -6.8 | 0 | 0 | 10.5 | 10.1 | 11 | 11.8 | 12 | 7.9 | 21.5 | 7.8 | 1.8 | 250.4 | 4.7 | 8.5 | 6.8 | 7.6 | 9 | 8.4 | 9.7 | 9.5 | 9.2 | 7.9 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.8 | 10.3 | 11.9 | 12.1 | 11.7 | 11 | 10.2 | 12.1 | 10 | 10.6 | 10.6
215 | -21 | -6.8 | 0 | 0 | 10.5 | 10.1 | 11 | 11.8 | 12 | 7.9 | 21.5 | 7.8 | 1.8 | 254.7 | 4.8 | 8.5 | 6.8 | 7.7 | 9 | 8.4 | 9.6 | 9.5 | 9.2 | 7.9 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.7 | 10.3 | 11.9 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 10 | 10.6 | 10.6
216 | -20 | -6.8 | 0 | 0 | 10.5 | 10.1 | 11 | 11.8 | 12 | 7.9 | 21.5 | 7.8 | 1.9 | 255.1 | 4.6 | 8.5 | 6.8 | 7.7 | 9 | 8.4 | 9.6 | 9.5 | 9.2 | 7.9 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.8 | 10.3 | 11.9 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 10 | 10.6 | 10.6
217 | -19 | -6.8 | 0 | 0 | 10.5 | 10.1 | 11 | 11.8 | 12 | 7.9 | 21.5 | 7.8 | 2 | 250.7 | 4.6 | 8.5 | 6.7 | 7.7 | 9 | 8.4 | 9.6 | 9.5 | 9.2 | 7.9 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.8 | 10.3 | 11.9 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 10 | 10.6 | 10.6
218 | -18 | -6.8 | 0 | 0 | 10.5 | 10.1 | 11 | 11.8 | 12 | 7.9 | 21.5 | 7.8 | 2.1 | 256.5 | 4.4 | 8.5 | 6.7 | 7.7 | 9 | 8.4 | 9.6 | 9.5 | 9.2 | 7.9 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.8 | 10.3 | 11.9 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 10 | 10.6 | 10.6
219 | -17 | -6.8 | 0 | 0 | 10.5 | 10.1 | 11 | 11.8 | 12 | 7.8 | 21.5 | 7.8 | 2.1 | 277.5 | 4.4 | 8.5 | 6.7 | 7.7 | 9 | 8.4 | 9.6 | 9.5 | 9.2 | 7.9 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.8 | 10.3 | 11.9 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 10 | 10.6 | 10.6
220 | -16 | -6.8 | 0 | 0 | 10.5 | 10.1 | 11 | 11.8 | 12 | 7.9 | 21.5 | 7.8 | 1.9 | 271 | 4.7 | 8.5 | 6.7 | 7.7 | 9 | 8.4 | 9.7 | 9.5 | 9.2 | 7.9 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.8 | 10.3 | 11.9 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 10 | 10.6 | 10.6
221 | -15 | -6.8 | 0 | 0 | 10.5 | 10.1 | 11 | 11.8 | 12 | 7.9 | 21.5 | 7.9 | 1.7 | 255 | 4.7 | 8.5 | 6.7 | 7.7 | 9 | 8.4 | 9.6 | 9.5 | 9.2 | 7.9 | 9.5 | 10 | 11.6 | 12.3 | 12.2 | 13.4 | 11.9 | 10.7 | 10.3 | 11.9 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 10 | 10.6 | 10.6
222 | -14 | -6.8 | 0 | 0 | 10.5 | 10.2 | 11 | 11.8 | 11.9 | 7.9 | 21.5 | 7.9 | 1.8 | 254.8 | 4.3 | 8.5 | 6.7 | 7.7 | 9 | 8.4 | 9.6 | 9.4 | 9.2 | 7.9 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1 | 11.7 | 11.1 | 10.1 | 12.1 | 10 | 10.6 | 10.6
223 | -13 | -6.8 | 0 | 0 | 10.5 | 10.2 | 11 | 11.8 | 11.9 | 7.9 | 21.5 | 7.8 | 1.8 | 246.1 | 4.7 | 8.5 | 6.7 | 7.7 | 9 | 8.4 | 9.7 | 9.5 | 9.2 | 7.9 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.8 | 10.3 | 11.9 | 12.1 | 11.7 | 11.1 | 10.1 | 12.1 | 10 | 10.6 | 10.6
224 | -12 | -6.8 | 0 | 0 | 10.5 | 10.3 | 10.9 | 11.8 | 11.9 | 7.9 | 21.5 | 7.8 | 2 | 245.3 | 5.3 | 8.5 | 6.7 | 7.7 | 9 | 8.4 | 9.6 | 9.5 | 9.2 | 8 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.8 | 10.3 | 11.9 | 12.1 | 11.7 | 11.1 | 10.1 | 12.1 | 10 | 10.6 | 10.6
225 | -11 | -6.8 | 0 | 0 | 10.5 | 10.3 | 10.9 | 11.8 | 11.9 | 7.9 | 21.5 | 7.8 | 1.9 | 246.4 | 5.5 | 8.5 | 6.8 | 7.7 | 9 | 8.4 | 9.6 | 9.5 | 9.2 | 8 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.8 | 10.3 | 11.9 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 10 | 10.6 | 10.6
226 | -10 | -6.8 | 0 | 0 | 10.5 | 10.3 | 11 | 11.8 | 11.9 | 7.9 | 21.5 | 7.8 | 1.8 | 252.7 | 5.4 | 8.5 | 6.7 | 7.7 | 9 | 8.4 | 9.6 | 9.4 | 9.2 | 7.9 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.7 | 10.2 | 11.9 | 12.1 | 11.7 | 11.1 | 10.1 | 12.1 | 10 | 10.6 | 10.6
227 | -9 | -6.8 | 0 | 0 | 10.5 | 10.4 | 11 | 11.8 | 11.9 | 7.9 | 21.5 | 7.8 | 1.8 | 253.5 | 5.3 | 8.5 | 6.8 | 7.7 | 9 | 8.4 | 9.6 | 9.5 | 9.2 | 7.9 | 9.5 | 10 | 11.6 | 12.3 | 12.2 | 13.4 | 11.9 | 10.8 | 10.3 | 11.9 | 12.1 | 11.7 | 11 | 10.2 | 12.1 | 10 | 10.6 | 10.6
228 | -8 | -6.8 | 0 | 0 | 10.5 | 10.4 | 10.9 | 11.8 | 11.9 | 7.9 | 21.5 | 7.8 | 1.8 | 258.5 | 4.9 | 8.5 | 6.8 | 7.7 | 9 | 8.4 | 9.6 | 9.5 | 9.2 | 8 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.7 | 10.2 | 11.9 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 10 | 10.6 | 10.6
229 | -7 | -6.8 | 0 | 0 | 10.5 | 10.4 | 10.9 | 11.8 | 12 | 7.9 | 21.5 | 7.8 | 1.7 | 263.8 | 4.9 | 8.5 | 6.8 | 7.7 | 9 | 8.4 | 9.6 | 9.5 | 9.3 | 8 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 10 | 10.6 | 10.6
230 | -6 | -6.8 | 0 | 0 | 10.4 | 10.4 | 10.9 | 11.8 | 12 | 7.9 | 21.5 | 7.8 | 1.6 | 249.8 | 5.1 | 8.5 | 6.8 | 7.7 | 9 | 8.4 | 9.6 | 9.5 | 9.3 | 8 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1 | 11.7 | 11.1 | 10.2 | 12 | 10 | 10.6 | 10.6
231 | -5 | -6.8 | 0 | 0 | 10.4 | 10.4 | 10.9 | 11.8 | 12 | 7.9 | 21.5 | 7.8 | 1.6 | 253.7 | 5.3 | 8.5 | 6.8 | 7.7 | 9 | 8.4 | 9.7 | 9.5 | 9.2 | 8 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 10 | 10.6 | 10.6
232 | -4 | -6.8 | 0 | 0 | 10.4 | 10.4 | 10.9 | 11.8 | 12 | 7.9 | 21.5 | 7.8 | 1.3 | 252.2 | 5.1 | 8.5 | 6.8 | 7.7 | 9 | 8.4 | 9.7 | 9.5 | 9.3 | 8 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 10 | 10.6 | 10.6
233 | -3 | -6.8 | 0 | 0 | 10.4 | 10.4 | 10.9 | 11.8 | 12 | 7.9 | 21.5 | 7.9 | 1.4 | 255.7 | 5 | 8.5 | 6.8 | 7.7 | 9 | 8.4 | 9.7 | 9.5 | 9.3 | 8 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.8 | 10.3 | 11.9 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 10 | 10.6 | 10.6
234 | -2 | -6.8 | 0 | 0 | 10.4 | 10.4 | 10.9 | 11.8 | 12 | 7.9 | 21.5 | 7.9 | 1.4 | 259.2 | 5 | 8.5 | 6.8 | 7.7 | 9 | 8.4 | 9.7 | 9.5 | 9.3 | 8 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 10 | 10.6 | 10.6
235 | -1 | -6.8 | 0 | 0 | 10.4 | 10.4 | 10.9 | 11.8 | 12 | 7.9 | 21.5 | 7.9 | 1.3 | 252.9 | 4.9 | 8.5 | 6.8 | 7.7 | 9 | 8.4 | 9.7 | 9.4 | 9.3 | 8 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 10 | 10.6 | 10.6
236 | 0 | 141.7 | 56.68 | 66.2557 | 10.4 | 10.4 | 10.9 | 11.8 | 12 | 7.9 | 21.5 | 7.9 | 1.4 | 252.8 | 5.1 | 8.5 | 6.9 | 7.7 | 9 | 8.4 | 9.7 | 9.5 | 9.3 | 8 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 10 | 10.6 | 10.6
237 | 1 | 517.1 | 206.84 | 241.784 | 10.4 | 10.4 | 10.9 | 11.8 | 12 | 7.8 | 21.5 | 7.9 | 1.8 | 252.4 | 6.1 | 8.5 | 6.9 | 7.7 | 9 | 8.4 | 9.7 | 9.5 | 9.3 | 8 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1 | 11.7 | 11.1 | 10.3 | 12.1 | 10 | 10.6 | 10.6
238 | 2 | 652.9 | 261.16 | 305.281 | 10.4 | 10.4 | 10.9 | 11.8 | 12 | 7.8 | 21.5 | 7.9 | 2.2 | 238.5 | 6.3 | 8.5 | 6.9 | 7.6 | 9 | 8.4 | 9.7 | 9.5 | 9.3 | 8 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.8 | 10.3 | 11.9 | 12.1 | 11.7 | 11.1 | 10.2 | 12.1 | 10 | 10.6 | 10.6
239 | 3 | 633.8 | 253.52 | 296.3503 | 10.4 | 10.4 | 10.9 | 11.8 | 12 | 7.8 | 21.5 | 7.9 | 2.6 | 219.3 | 6.7 | 8.5 | 8.7 | 7.8 | 9 | 8.4 | 9.8 | 9.4 | 9.3 | 8 | 9.5 | 10 | 11.7 | 12.3 | 12.2 | 13.4 | 11.9 | 10.8 | 10.3 | 11.9 | 12.1 | 11.7 | 11.1 | 10.3 | 12.1 | 10 | 10.6 | 10.6
240 | 4 | 590.2 | 236.08 | 275.9639 | 10.4 | 10.4 | 11 | 12 | 12 | 7.8 | 21.5 | 7.8 | 2.7 | 227.1 | 6.5 | 8.5 | 33.5 | 12.1 | 9 | 8.4 | 11.3 | 9.5 | 9.3 | 9.2 | 9.5 | 10 | 11.9 | 12.3 | 12.2 | 13.4 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1 | 11.7 | 11.1 | 10.3 | 12.1 | 10.1 | 10.6 | 10.6
241 | 5 | 566.9 | 226.76 | 265.0694 | 10.4 | 10.4 | 11.1 | 12.2 | 12.6 | 7.9 | 21.5 | 7.8 | 2.5 | 235.5 | 5.7 | 8.4 | 94.1 | 26.6 | 9 | 8.4 | 18.6 | 9.5 | 11.7 | 23 | 9.4 | 10 | 14.1 | 12.3 | 12.2 | 13.4 | 11.9 | 10.8 | 10.8 | 11.9 | 12.3 | 11.7 | 11.2 | 10.4 | 12.1 | 10.1 | 10.6 | 10.6
242 | 6 | 556.2 | 222.48 | 260.0663 | 10.5 | 10.4 | 11.3 | 12.6 | 15.1 | 7.9 | 21.5 | 7.9 | 2.5 | 236.4 | 5 | 8.5 | 156.3 | 57.3 | 9 | 8.5 | 30.6 | 9.6 | 16.1 | 45.1 | 9.4 | 10 | 19.5 | 12.3 | 12.2 | 13.4 | 11.9 | 13.2 | 17 | 11.9 | 14.8 | 11.7 | 11.4 | 10.6 | 12.1 | 10.3 | 10.6 | 10.6
243 | 7 | 538.9 | 215.56 | 251.9772 | 10.8 | 10.6 | 11.6 | 13.1 | 21.2 | 8 | 21.5 | 7.9 | 2.2 | 238.6 | 4.5 | 9 | 189.1 | 83.4 | 9.1 | 8.7 | 41.3 | 9.9 | 27 | 63.2 | 9.4 | 10.1 | 25.2 | 12.3 | 12.2 | 13.5 | 11.9 | 18.2 | 23.4 | 12 | 19 | 11.7 | 11.8 | 10.8 | 12.1 | 10.4 | 10.6 | 10.6
244 | 8 | 528.1 | 211.24 | 246.9274 | 11.8 | 11.7 | 12.6 | 13.6 | 28.7 | 8 | 21.5 | 7.9 | 2.4 | 245.8 | 4.6 | 10 | 242.4 | 116.1 | 9.2 | 9.2 | 55.1 | 10.6 | 39.9 | 86.3 | 9.5 | 10.2 | 31.2 | 12.3 | 12.2 | 13.5 | 11.9 | 24.3 | 30.8 | 12 | 21.9 | 11.7 | 12 | 11 | 12.1 | 10.6 | 10.6 | 10.6
245 | 9 | 523.7 | 209.48 | 244.8701 | 13.5 | 13.4 | 13.8 | 14.4 | 38.6 | 8.1 | 21.5 | 7.9 | 2.8 | 267 | 5.4 | 11.5 | 310.4 | 157.5 | 9.4 | 10.1 | 70.7 | 11.9 | 57.2 | 126.7 | 9.7 | 10.3 | 40 | 12.3 | 12.2 | 13.5 | 11.9 | 31.3 | 41.4 | 12.1 | 24.4 | 11.7 | 12.2 | 11.4 | 12.1 | 10.8 | 10.7 | 10.6
246 | 10 | 522.4 | 208.96 | 244.2622 | 15 | 14.7 | 15.1 | 15.3 | 53.2 | 8.2 | 21.5 | 7.9 | 2.4 | 246.4 | 6.1 | 13.7 | 366.9 | 208.8 | 9.8 | 11.2 | 85.7 | 13.7 | 75.3 | 169.3 | 9.9 | 10.6 | 51.1 | 12.3 | 12.2 | 13.6 | 11.9 | 40.7 | 54.9 | 12.2 | 28.9 | 11.7 | 13 | 12.1 | 12.1 | 11 | 10.8 | 10.7
247 | 11 | 523.1 | 209.24 | 244.5895 | 16.3 | 15.1 | 17 | 16.1 | 65.7 | 8.2 | 21.5 | 7.9 | 2.4 | 245 | 6.8 | 16.5 | 412.3 | 258.6 | 10.2 | 12.8 | 102.5 | 16.1 | 98.1 | 220.7 | 10.2 | 10.9 | 65.3 | 12.3 | 12.2 | 13.7 | 11.9 | 47.5 | 63.7 | 12.3 | 32.3 | 11.7 | 14.9 | 13.2 | 12.1 | 11.2 | 10.8 | 10.7
248 | 12 | 524.1 | 209.64 | 245.0571 | 17.9 | 15.9 | 20 | 17.2 | 76 | 8.3 | 21.5 | 7.9 | 2.9 | 239.4 | 7.8 | 20 | 460.1 | 303.1 | 10.9 | 14.7 | 117.9 | 19.3 | 122.8 | 262 | 10.6 | 11.4 | 80.5 | 12.3 | 12.2 | 13.9 | 12 | 60.4 | 79.7 | 12.4 | 36.3 | 11.7 | 18 | 15.1 | 12.1 | 11.6 | 10.9 | 10.8
249 | 13 | 525.5 | 210.2 | 245.7117 | 20.3 | 18.4 | 22.5 | 18.2 | 84.5 | 8.3 | 21.5 | 7.9 | 2.8 | 232.2 | 8.6 | 24 | 480 | 349 | 11.6 | 17.1 | 133.6 | 23.1 | 144.3 | 310.7 | 11.1 | 11.9 | 97.4 | 12.3 | 12.2 | 13.9 | 12.1 | 68.6 | 88.2 | 12.5 | 38.2 | 11.7 | 20.7 | 16.8 | 12.1 | 12 | 11 | 10.9
250 | 14 | 526.7 | 210.68 | 246.2728 | 22.6 | 21.2 | 25.8 | 19.3 | 94.4 | 8.4 | 21.5 | 7.9 | 3 | 240.6 | 7.8 | 28.4 | 509 | 399.8 | 12.6 | 19.8 | 149.3 | 27.5 | 168.4 | 366.7 | 11.7 | 12.6 | 111.7 | 12.3 | 12.2 | 14.1 | 12.1 | 80.4 | 104.8 | 12.6 | 40.8 | 11.7 | 23.4 | 18.4 | 12.1 | 12.3 | 11.2 | 10.9
251 | 15 | 528.4 | 211.36 | 247.0677 | 25.7 | 23.3 | 30.5 | 20.6 | 110 | 8.4 | 21.5 | 7.9 | 3.3 | 246.5 | 6.5 | 33.2 | 560.2 | 445.3 | 13.6 | 22.8 | 164.5 | 32.6 | 190.3 | 405.8 | 12.4 | 13.3 | 124.3 | 12.3 | 12.2 | 14.2 | 12.3 | 92.1 | 120.4 | 12.8 | 45.5 | 11.7 | 28 | 20.4 | 12.1 | 12.6 | 11.3 | 11
252 | 16 | 528.5 | 211.4 | 247.1144 | 28.3 | 25.2 | 35.7 | 22.1 | 120.7 | 8.5 | 21.5 | 8 | 3 | 228.1 | 6.1 | 38 | 604.1 | 491.1 | 14.9 | 26.2 | 178.9 | 38.2 | 209.7 | 442.7 | 13.3 | 14.1 | 136.3 | 12.3 | 12.2 | 14.3 | 12.4 | 102.6 | 133.8 | 12.9 | 52.4 | 11.7 | 31.3 | 22.7 | 12.1 | 12.9 | 11.5 | 11.2
253 | 17 | 529.3 | 211.72 | 247.4885 | 31.4 | 27.4 | 40.7 | 23.6 | 129.3 | 8.6 | 21.5 | 8.1 | 3.2 | 229.5 | 5.9 | 42.8 | 640.6 | 527.1 | 16.3 | 29.7 | 191.6 | 44.2 | 226 | 471.1 | 14.2 | 14.9 | 146.4 | 12.3 | 12.2 | 14.5 | 12.6 | 112.3 | 142.7 | 12.9 | 57.2 | 11.7 | 34.9 | 25.1 | 12.1 | 13.3 | 11.6 | 11.3
254 | 18 | 530.7 | 212.28 | 248.1431 | 34.6 | 31.1 | 45.7 | 25.1 | 139.6 | 8.6 | 21.5 | 8.1 | 3.5 | 234.8 | 5.8 | 47.5 | 671.8 | 554.4 | 17.8 | 33.5 | 204.6 | 50.5 | 239.8 | 492 | 15.3 | 15.7 | 156.9 | 12.3 | 12.2 | 14.7 | 12.9 | 120.8 | 153.9 | 13 | 60.9 | 11.7 | 38 | 27.6 | 12.1 | 13.8 | 11.9 | 11.4
255 | 19 | 533 | 213.2 | 249.2185 | 39 | 35.8 | 50.8 | 26.6 | 152.2 | 8.7 | 21.5 | 8.2 | 3.5 | 216.1 | 5.9 | 51.8 | 694.6 | 577.4 | 19.5 | 37.4 | 217.5 | 57 | 252.2 | 509 | 16.5 | 16.6 | 164 | 12.3 | 12.2 | 14.8 | 13.1 | 127.6 | 160.6 | 13 | 65.7 | 11.7 | 41.3 | 30.2 | 12.1 | 14.2 | 12 | 11.5
256 | 20 | 534 | 213.6 | 249.6861 | 43.3 | 40.1 | 55.8 | 28.3 | 158.8 | 8.7 | 21.5 | 8.4 | 3.1 | 221.6 | 5.6 | 56.2 | 712.3 | 596.5 | 21.4 | 41.4 | 230.6 | 63.5 | 261.9 | 517.9 | 17.8 | 17.5 | 170.1 | 12.3 | 12.2 | 14.9 | 13.4 | 132.8 | 165.5 | 13 | 69 | 11.8 | 46.1 | 32.9 | 12.1 | 14.7 | 12.3 | 11.6
257 | 21 | 535 | 214 | 250.1537 | 47.6 | 44.1 | 61.5 | 29.8 | 162.5 | 8.8 | 21.5 | 8.6 | 3.1 | 251.8 | 5.4 | 60.6 | 731.4 | 617.2 | 23.4 | 45.4 | 244.3 | 70 | 275.9 | 535.3 | 19.2 | 18.4 | 183.1 | 12.3 | 12.2 | 15 | 13.6 | 139.6 | 172.6 | 13.1 | 72.1 | 11.8 | 50.4 | 35.7 | 12.1 | 15.1 | 12.5 | 11.8
258 | 22 | 537.1 | 214.84 | 251.1356 | 52.6 | 47.6 | 66.1 | 31.8 | 165.6 | 8.9 | 21.5 | 9 | 3.2 | 260.5 | 6.7 | 65 | 751.9 | 631.4 | 25.5 | 49.5 | 256 | 76.2 | 278.9 | 542.1 | 20.5 | 19.2 | 187 | 12.3 | 12.2 | 15.1 | 13.9 | 143.5 | 176.1 | 13.1 | 72.3 | 11.7 | 53.6 | 38.5 | 12.1 | 15.7 | 12.7 | 12
259 | 23 | 537 | 214.8 | 251.0888 | 57.2 | 51.6 | 69.4 | 33.4 | 169.5 | 8.9 | 21.5 | 9.5 | 3 | 238.3 | 7.3 | 68.9 | 752.2 | 645.9 | 27.7 | 53.6 | 269 | 82.4 | 280.6 | 558.6 | 21.9 | 20.1 | 195.1 | 12.3 | 12.2 | 15.4 | 14.2 | 147.8 | 181.9 | 13.1 | 73.1 | 11.8 | 56.8 | 41.1 | 12.1 | 16.1 | 12.9 | 12.1
260 | 24 | 535.6 | 214.24 | 250.4342 | 61.5 | 55.8 | 72.6 | 34.9 | 175.7 | 9 | 21.5 | 10 | 2.8 | 249.7 | 7.1 | 72.7 | 762 | 656.5 | 29.9 | 57.7 | 282 | 88.4 | 285 | 573.1 | 23.3 | 20.9 | 206.4 | 12.3 | 12.2 | 15.6 | 14.4 | 153.6 | 189.4 | 13.2 | 77.8 | 11.8 | 59.5 | 43.4 | 12.1 | 16.8 | 13.1 | 12.2
261 | 25 | 536.8 | 214.72 | 250.9953 | 66 | 60.1 | 77.9 | 36.4 | 187.1 | 9 | 21.5 | 10.5 | 2.8 | 235.6 | 7.7 | 76.1 | 771.3 | 661.6 | 32.3 | 61.6 | 296 | 94.2 | 285.6 | 576.6 | 24.7 | 21.7 | 213.3 | 12.3 | 12.3 | 16.1 | 14.7 | 159 | 196.6 | 13.2 | 81.1 | 11.8 | 62 | 45.6 | 12.2 | 17.2 | 13.4 | 12.4
262 | 26 | 538.3 | 215.32 | 251.6967 | 69.5 | 63.8 | 81.9 | 37.7 | 197 | 9.1 | 21.5 | 11 | 2.5 | 236.2 | 8.1 | 79.4 | 770.9 | 669.3 | 34.7 | 65.5 | 309.5 | 99.8 | 287.3 | 604.1 | 26.1 | 22.6 | 225.6 | 12.3 | 12.3 | 16.2 | 14.9 | 164.7 | 204.8 | 13.3 | 83.4 | 11.8 | 64.8 | 48 | 12.1 | 17.5 | 13.6 | 12.5
263 | 27 | 540.5 | 216.2 | 252.7253 | 72.4 | 67.4 | 86.4 | 38.3 | 204.9 | 9.1 | 21.5 | 11.6 | 2.8 | 237.7 | 8.2 | 82.6 | 778.8 | 673.5 | 37.1 | 69.3 | 323.9 | 105.2 | 297.1 | 624.4 | 27.6 | 23.4 | 238.2 | 12.3 | 12.3 | 16.2 | 15.2 | 173 | 213.7 | 13.4 | 86.3 | 11.8 | 68.7 | 50.4 | 12.2 | 18 | 13.8 | 12.6
264 | 28 | 540.6 | 216.24 | 252.7721 | 75.7 | 71.5 | 90.6 | 39 | 213.9 | 9.2 | 21.5 | 12.2 | 2.8 | 236.2 | 8.2 | 85.7 | 773.3 | 684.2 | 39.4 | 73 | 338.2 | 110.4 | 308.1 | 641 | 29 | 24.2 | 248 | 12.3 | 12.3 | 16.5 | 15.4 | 179.9 | 220.6 | 13.5 | 88.7 | 11.8 | 71.6 | 53.4 | 12.2 | 18.4 | 14.1 | 12.8
265 | 29 | 540.7 | 216.28 | 252.8189 | 79 | 75.8 | 94.5 | 39.8 | 221.8 | 9.2 | 21.5 | 12.8 | 2.6 | 245.9 | 7.2 | 88.7 | 778.5 | 688 | 41.7 | 76.8 | 352.7 | 115.5 | 316.2 | 651.1 | 30.5 | 25 | 261.4 | 12.3 | 12.3 | 16.6 | 15.7 | 186.6 | 229.6 | 13.6 | 91 | 11.8 | 74.7 | 56.6 | 12.2 | 18.8 | 14.3 | 12.9
266 | 30 | 540.5 | 216.2 | 252.7253 | 82.8 | 79.3 | 98.9 | 40.9 | 229.1 | 9.3 | 21.5 | 13.2 | 2.9 | 250.4 | 7 | 91.8 | 783.2 | 692.1 | 43.9 | 80.6 | 366.9 | 120.4 | 324.9 | 660.6 | 32 | 25.9 | 271.4 | 12.3 | 12.3 | 16.8 | 15.9 | 192.5 | 237.7 | 13.8 | 92.2 | 11.8 | 78 | 59.4 | 12.2 | 19.3 | 14.6 | 13.1
267 | 31 | 539 | 215.6 | 252.024 | 86.5 | 82.9 | 102.9 | 42.1 | 234.2 | 9.4 | 21.5 | 13.8 | 3 | 246.8 | 7.1 | 95 | 783.4 | 690.4 | 46.2 | 84.4 | 381 | 125.2 | 334.4 | 669 | 33.5 | 26.8 | 283.4 | 12.3 | 12.3 | 17 | 16.2 | 198.2 | 246.5 | 13.9 | 95 | 11.8 | 81 | 62.9 | 12.2 | 20 | 14.8 | 13.3
268 | 32 | 539.9 | 215.96 | 252.4448 | 90.3 | 86.1 | 106.9 | 42.8 | 242.8 | 9.4 | 21.5 | 14.3 | 2.8 | 231.4 | 7 | 98.1 | 783.5 | 690.8 | 48.6 | 88.3 | 394.1 | 129.9 | 342 | 676.7 | 35 | 27.8 | 292.6 | 12.3 | 12.3 | 17.4 | 16.5 | 202.8 | 250.2 | 14 | 98.4 | 11.8 | 84.1 | 65.9 | 12.2 | 20.4 | 15.1 | 13.5
269 | 33 | 540.6 | 216.24 | 252.7721 | 93.9 | 89.4 | 109.8 | 43.3 | 248.4 | 9.4 | 21.5 | 14.8 | 2.7 | 237.7 | 7.3 | 101.3 | 802.5 | 694 | 50.9 | 92 | 404.8 | 134.6 | 345.3 | 672.3 | 36.6 | 28.8 | 300.3 | 12.3 | 12.4 | 17.5 | 16.8 | 207.6 | 253.7 | 14.1 | 102.1 | 11.9 | 87.2 | 68.7 | 12.2 | 20.8 | 15.3 | 13.7
270 | 34 | 542.9 | 217.16 | 253.8475 | 97.6 | 92.4 | 112.7 | 43.8 | 248.9 | 9.5 | 21.5 | 15.3 | 2.5 | 251.5 | 7.2 | 104.6 | 809.5 | 689.7 | 53.3 | 95.8 | 415.6 | 139.2 | 348.9 | 678.7 | 38.1 | 29.8 | 308.8 | 12.3 | 12.4 | 17.7 | 17.1 | 211.2 | 256.5 | 14.2 | 105.4 | 11.9 | 91.3 | 71.1 | 12.2 | 21.3 | 15.5 | 13.8
271 | 35 | 541.4 | 216.56 | 253.1462 | 102.1 | 96.1 | 115.5 | 44.8 | 250 | 9.5 | 21.5 | 15.8 | 2.7 | 229.2 | 7.8 | 107.8 | 796.1 | 691.5 | 55.6 | 99.6 | 427.6 | 143.6 | 354.1 | 688.1 | 39.8 | 30.8 | 317.5 | 12.3 | 12.5 | 18 | 17.4 | 214.7 | 258.3 | 14.3 | 107.2 | 11.9 | 95 | 74.4 | 12.2 | 21.9 | 15.8 | 14
272 | 36 | 543.7 | 217.48 | 254.2216 | 107 | 99.8 | 118.6 | 45.6 | 254 | 9.6 | 21.5 | 16.3 | 2.9 | 241.3 | 7.9 | 110.9 | 787.6 | 698.7 | 57.9 | 103.4 | 439.1 | 147.8 | 358.8 | 687.4 | 41.4 | 31.8 | 326.7 | 12.3 | 12.5 | 18.4 | 17.7 | 219.3 | 262.1 | 14.5 | 108.5 | 11.9 | 98.2 | 76.9 | 12.2 | 22.7 | 16.1 | 14.3
273 | 37 | 545.4 | 218.16 | 255.0165 | 110.7 | 103 | 121.6 | 46.1 | 257.9 | 9.6 | 21.5 | 16.7 | 2.7 | 248.9 | 7.7 | 114.1 | 799.1 | 700.6 | 60.1 | 107.2 | 450.2 | 151.9 | 360.1 | 683.6 | 43 | 32.7 | 334.1 | 12.3 | 12.5 | 18.5 | 18 | 223 | 264.5 | 14.5 | 109.4 | 11.9 | 101 | 79.2 | 12.2 | 23.2 | 16.3 | 14.5
274 | 38 | 547 | 218.8 | 255.7646 | 113.9 | 106 | 124.4 | 46.9 | 259.8 | 9.7 | 21.5 | 17.2 | 2.9 | 239.7 | 7.8 | 117.2 | 798.2 | 702.6 | 62.4 | 111 | 461.4 | 155.8 | 363.9 | 687.5 | 44.5 | 33.7 | 342.8 | 12.3 | 12.6 | 18.6 | 18.3 | 225.8 | 266.9 | 14.7 | 111.1 | 12 | 104.1 | 82.4 | 12.2 | 23.8 | 16.6 | 14.7
275 | 39 | 549.2 | 219.68 | 256.7933 | 116.9 | 110.1 | 126.6 | 47.8 | 260.2 | 9.7 | 21.5 | 17.6 | 2.7 | 231.3 | 8.3 | 120.2 | 791.9 | 696.2 | 64.6 | 114.7 | 472.1 | 159.7 | 367.6 | 681 | 46.1 | 34.7 | 350.3 | 12.3 | 12.6 | 18.8 | 18.6 | 229.9 | 270.2 | 14.8 | 112.7 | 12 | 106.9 | 86.3 | 12.2 | 24.2 | 16.8 | 14.9
276 | 40 | 548.4 | 219.36 | 256.4192 | 120.6 | 113.1 | 128.4 | 48.5 | 259.3 | 9.7 | 21.5 | 18 | 2.8 | 235.5 | 8 | 123.3 | 795 | 695.1 | 66.8 | 118.1 | 481.8 | 163.4 | 373 | 689.1 | 47.7 | 35.7 | 362.1 | 12.3 | 12.6 | 19 | 19 | 233.9 | 274.5 | 14.9 | 115.6 | 12 | 109.5 | 88.7 | 12.2 | 24.7 | 17.1 | 15.1
277 | 41 | 546.7 | 218.68 | 255.6243 | 123.6 | 115.3 | 130 | 49 | 259.5 | 9.7 | 21.5 | 18.5 | 2.9 | 234.6 | 7.8 | 126.7 | 803.4 | 699.7 | 69 | 121.5 | 490.7 | 167.1 | 377.1 | 686.9 | 49.2 | 36.8 | 369.1 | 12.3 | 12.6 | 19.2 | 19.3 | 237.3 | 276.8 | 15 | 118.2 | 12 | 112.2 | 90.8 | 12.2 | 25.6 | 17.3 | 15.3
278 | 42 | 546.1 | 218.44 | 255.3438 | 125.8 | 117.5 | 132.1 | 49.4 | 261.7 | 9.7 | 21.5 | 18.8 | 3 | 235.9 | 7.6 | 130.2 | 808.4 | 697.7 | 71.2 | 124.9 | 500.2 | 170.7 | 378.4 | 686.3 | 50.7 | 37.8 | 375.2 | 12.3 | 12.7 | 19.4 | 19.6 | 240.2 | 279.6 | 15.1 | 120.4 | 12 | 115.3 | 92.8 | 12.3 | 26.1 | 17.6 | 15.6
279 | 43 | 547 | 218.8 | 255.7646 | 129.2 | 120.2 | 135 | 49.8 | 265.1 | 9.8 | 21.5 | 19.2 | 3.1 | 241.5 | 7 | 133.9 | 807.4 | 692 | 73.3 | 128.4 | 510.2 | 174.2 | 381.3 | 691 | 52.1 | 38.8 | 384.2 | 12.3 | 12.7 | 19.6 | 19.9 | 244.2 | 285.3 | 15.3 | 123.1 | 12.1 | 118.3 | 95 | 12.3 | 26.7 | 17.8 | 15.8
280 | 44 | 547.2 | 218.88 | 255.8581 | 132.9 | 122.6 | 137.2 | 50.3 | 269.6 | 9.8 | 21.5 | 19.6 | 2.8 | 243.4 | 7.1 | 137.7 | 806.7 | 687.6 | 75.4 | 131.4 | 519.7 | 177.5 | 386.4 | 700 | 53.5 | 39.7 | 392.4 | 12.3 | 12.8 | 19.9 | 20.2 | 248.1 | 289.2 | 15.5 | 124.5 | 12.1 | 121.3 | 96.9 | 12.3 | 27.5 | 18.1 | 16
281 | 45 | 547.4 | 218.96 | 255.9516 | 136.6 | 124.6 | 138.9 | 50.6 | 274.7 | 9.8 | 21.5 | 19.9 | 3.2 | 237.6 | 6.9 | 141.7 | 819 | 690.3 | 77.4 | 134 | 528.1 | 180.7 | 387.4 | 694.9 | 54.9 | 40.7 | 399.6 | 12.3 | 12.8 | 20 | 20.5 | 252.2 | 293.3 | 15.7 | 126.2 | 12.1 | 124.3 | 98.9 | 12.3 | 28.1 | 18.4 | 16.3
282 | 46 | 547.4 | 218.96 | 255.9516 | 138.6 | 126.4 | 140.4 | 50.9 | 280.7 | 9.8 | 21.5 | 20.3 | 3.4 | 256.2 | 7 | 146.2 | 821.3 | 686.1 | 79.5 | 136.2 | 535.3 | 183.8 | 389.5 | 696.8 | 56.3 | 41.6 | 407.3 | 12.3 | 12.9 | 20.5 | 20.8 | 256.3 | 299.6 | 15.9 | 128.7 | 12.1 | 127.3 | 101.2 | 12.3 | 28.6 | 18.7 | 16.5
283 | 47 | 548.2 | 219.28 | 256.3257 | 141.5 | 128.8 | 142.3 | 51.4 | 287 | 9.8 | 21.5 | 20.7 | 2.9 | 249.3 | 8.1 | 150.8 | 828.6 | 680.7 | 81.6 | 138 | 542.3 | 186.8 | 387.2 | 686.8 | 57.7 | 42.5 | 409.9 | 12.3 | 13 | 21.1 | 21.2 | 260 | 301.4 | 16 | 131.7 | 12.2 | 130 | 103.6 | 12.3 | 29 | 19 | 16.8
284 | 48 | 549.9 | 219.96 | 257.1206 | 144.6 | 131.8 | 145.3 | 51.6 | 287.1 | 9.8 | 21.5 | 21 | 2.7 | 245.8 | 9.4 | 155.4 | 829.5 | 666.8 | 83.7 | 138.7 | 550.3 | 189.7 | 386.9 | 690.6 | 59.1 | 43.4 | 416.8 | 12.3 | 13 | 21.1 | 21.5 | 260.2 | 302.5 | 16.1 | 132.5 | 12.2 | 133.6 | 107.4 | 12.3 | 29.6 | 19.2 | 17
285 | 49 | 548.6 | 219.44 | 256.5127 | 147 | 134.1 | 146.8 | 51.9 | 285.3 | 9.8 | 21.5 | 21.3 | 2.5 | 244.5 | 10.1 | 160.3 | 823.6 | 627.4 | 85.7 | 138.8 | 558.5 | 192.5 | 387 | 694.5 | 60.5 | 44.2 | 422 | 12.3 | 13.1 | 21.2 | 21.8 | 262.8 | 306.8 | 16.2 | 135.3 | 12.3 | 135.3 | 110.4 | 12.3 | 30.2 | 19.5 | 17.3
286 | 50 | 547.4 | 218.96 | 255.9516 | 148.7 | 136.4 | 147.9 | 52.6 | 287 | 9.8 | 21.5 | 21.6 | 2.5 | 241.5 | 9.7 | 165.5 | 822.7 | 594.2 | 87.6 | 139.3 | 566.2 | 195.1 | 387 | 691.2 | 62 | 45.1 | 426.7 | 12.3 | 13.1 | 21.4 | 22.2 | 266.4 | 308.4 | 16.3 | 137.9 | 12.3 | 137.1 | 112.8 | 12.3 | 30.8 | 19.8 | 17.5
287 | 51 | 548.5 | 219.4 | 256.466 | 151.1 | 139.1 | 148.7 | 53.1 | 287.3 | 9.8 | 21.5 | 21.9 | 2.8 | 238.8 | 9.3 | 171 | 826.7 | 562.8 | 89.5 | 139.6 | 573.7 | 197.6 | 389 | 694.6 | 63.4 | 46 | 432.3 | 12.3 | 13.2 | 21.6 | 22.5 | 267.5 | 309.3 | 16.5 | 138.4 | 12.3 | 138.7 | 114.8 | 12.3 | 31.5 | 20.1 | 17.7
288 | 52 | 548.8 | 219.52 | 256.6062 | 153.2 | 140.9 | 149.5 | 53.2 | 290.8 | 9.9 | 21.5 | 22.2 | 3.4 | 225.4 | 8.8 | 176.4 | 832.5 | 534.6 | 91.4 | 139.6 | 580.2 | 200 | 391.5 | 694.2 | 64.8 | 46.8 | 440.4 | 12.3 | 13.2 | 21.8 | 22.9 | 272.1 | 313.3 | 16.7 | 140.7 | 12.4 | 140.5 | 116.2 | 12.4 | 32.3 | 20.3 | 17.9
289 | 53 | 548.2 | 219.28 | 256.3257 | 155.7 | 141.9 | 150.1 | 53.6 | 293.1 | 9.9 | 21.5 | 22.6 | 3 | 228.4 | 7.7 | 181.8 | 841.1 | 510.5 | 93.3 | 139.4 | 586.2 | 202.2 | 391.8 | 694.8 | 66.2 | 47.7 | 443.6 | 12.3 | 13.3 | 22 | 23.2 | 273.3 | 313.3 | 16.8 | 142.1 | 12.4 | 142.4 | 118 | 12.4 | 32.7 | 20.6 | 18.2
290 | 54 | 549.2 | 219.68 | 256.7933 | 158.5 | 144.5 | 150.9 | 54 | 295.1 | 9.9 | 21.5 | 22.9 | 3.4 | 228.7 | 6.6 | 187.2 | 834.9 | 488.9 | 95.1 | 139.1 | 592.8 | 204.3 | 390.2 | 689.5 | 67.6 | 48.5 | 446.4 | 12.3 | 13.3 | 22.6 | 23.6 | 275.2 | 317.4 | 17 | 145.2 | 12.5 | 145.4 | 120.6 | 12.4 | 33.2 | 20.9 | 18.4
291 | 55 | 551.2 | 220.48 | 257.7284 | 159.8 | 147.5 | 151.9 | 54.2 | 298.3 | 10 | 21.5 | 23.2 | 3.6 | 240.2 | 5.6 | 192.5 | 841.9 | 470.4 | 96.9 | 139.1 | 599.4 | 206.3 | 391.2 | 692.3 | 69 | 49.4 | 453.7 | 12.3 | 13.4 | 23.1 | 23.9 | 278.4 | 322.7 | 17.4 | 148.7 | 12.5 | 148.5 | 122.9 | 12.4 | 33.8 | 21.2 | 18.7
292 | 56 | 552.3 | 220.92 | 258.2428 | 160.9 | 150.7 | 152.5 | 54.6 | 303 | 10 | 21.5 | 23.5 | 3 | 258.8 | 5.3 | 197.8 | 844.8 | 452.5 | 98.5 | 139.3 | 605.4 | 208.2 | 395.6 | 696.8 | 70.4 | 50.2 | 461.7 | 12.3 | 13.4 | 23.3 | 24.3 | 281.1 | 329 | 17.8 | 153.1 | 12.5 | 150.3 | 125 | 12.4 | 34.5 | 21.5 | 18.9
293 | 57 | 551.3 | 220.52 | 257.7752 | 161.9 | 153.2 | 154 | 54.7 | 309.3 | 10 | 21.5 | 23.7 | 3 | 226.9 | 5.5 | 203.4 | 845.5 | 436.8 | 100.2 | 139.6 | 612.2 | 210.1 | 400.7 | 710.5 | 71.8 | 51 | 469.4 | 12.3 | 13.5 | 23.8 | 24.6 | 285.1 | 333.9 | 18.4 | 157.8 | 12.6 | 151.8 | 126.8 | 12.4 | 35.1 | 21.9 | 19.2
294 | 58 | 551.2 | 220.48 | 257.7284 | 162.5 | 154.6 | 155.5 | 54.9 | 313.6 | 10 | 21.5 | 23.9 | 2.9 | 238.2 | 5.9 | 209.3 | 842.3 | 421.4 | 101.8 | 140 | 619.4 | 211.8 | 402.2 | 711.2 | 73.2 | 51.9 | 475.2 | 12.3 | 13.5 | 23.9 | 24.9 | 286.6 | 335.1 | 19 | 159.1 | 12.6 | 153 | 127.9 | 12.5 | 35.8 | 22.2 | 19.4
295 | 59 | 551.7 | 220.68 | 257.9622 | 163.4 | 155.7 | 156.3 | 55.1 | 317.1 | 10 | 21.4 | 24.2 | 2.8 | 250.6 | 6.1 | 216 | 849 | 406.7 | 103.5 | 140.6 | 625.7 | 213.3 | 402.3 | 705 | 74.5 | 52.7 | 478.7 | 12.3 | 13.6 | 24.1 | 25.3 | 288.4 | 338.1 | 19.5 | 160.7 | 12.7 | 154.4 | 129 | 12.5 | 36.4 | 22.6 | 19.6
296 | 60 | 550.9 | 220.36 | 257.5881 | 164.5 | 157 | 157.3 | 55.2 | 319.3 | 10.1 | 21.4 | 24.5 | 2.6 | 256.7 | 6.1 | 225.7 | 857.9 | 393.3 | 105 | 141.1 | 631.9 | 214.9 | 403 | 702.8 | 75.9 | 53.6 | 483.6 | 12.3 | 13.6 | 24.7 | 25.7 | 289.9 | 338 | 19.9 | 161.7 | 12.7 | 155.4 | 130.3 | 12.5 | 36.9 | 22.9 | 19.9
297 | 61 | 552 | 220.8 | 258.1025 | 166.1 | 158.7 | 157.8 | 55.2 | 320.8 | 10.1 | 21.4 | 24.8 | 2.7 | 230 | 7.2 | 237.1 | 864.6 | 380.7 | 106.7 | 141.6 | 637.7 | 216.3 | 404.9 | 701.5 | 77.2 | 54.4 | 491.6 | 12.3 | 13.7 | 24.7 | 26.1 | 291.5 | 338.4 | 20.4 | 162.9 | 12.8 | 157.4 | 131.9 | 12.5 | 37.3 | 23.2 | 20.1
298 | 62 | 554.3 | 221.72 | 259.1779 | 167.7 | 160 | 158.3 | 55.4 | 321.6 | 10.2 | 21.4 | 25 | 2.5 | 241.8 | 7.9 | 245.8 | 867.3 | 368.5 | 108.2 | 142.1 | 643.4 | 217.7 | 406.3 | 700.1 | 78.5 | 55.3 | 497 | 12.3 | 13.8 | 25.2 | 26.5 | 291.6 | 339.1 | 20.9 | 163.5 | 12.8 | 159 | 133.6 | 12.5 | 37.9 | 23.5 | 20.4
299 | 63 | 556.5 | 222.6 | 260.2066 | 168.9 | 161 | 158.8 | 55.5 | 322.2 | 10.3 | 21.4 | 25.3 | 2.9 | 252.5 | 8.3 | 252.3 | 855.6 | 356.8 | 109.7 | 142.7 | 648.9 | 219.1 | 405.1 | 690.3 | 79.9 | 56.1 | 500.5 | 12.3 | 13.8 | 25.2 | 26.9 | 292.7 | 337.9 | 21 | 164 | 12.9 | 160 | 134.8 | 12.6 | 38.3 | 23.8 | 20.6
300 | 64 | 557.5 | 223 | 260.6742 | 170.7 | 162.1 | 158.6 | 55.9 | 321.8 | 10.3 | 21.4 | 25.6 | 3.2 | 234.5 | 8 | 256.9 | 835.9 | 345.2 | 111 | 143.4 | 654.1 | 220.5 | 403.3 | 680.2 | 81.2 | 57 | 503.3 | 12.3 | 13.9 | 25.7 | 27.4 | 293.4 | 335.3 | 21.4 | 163.8 | 12.9 | 160.8 | 136.7 | 12.6 | 38.9 | 24 | 20.9
301 | 65 | 554.8 | 221.92 | 259.4117 | 173.7 | 162.2 | 159.6 | 56.5 | 323.7 | 10.3 | 21.4 | 25.9 | 3.3 | 240.5 | 6.9 | 259.5 | 826.9 | 335 | 112 | 144.1 | 659.1 | 221.8 | 399.3 | 668.3 | 82.5 | 57.8 | 505.3 | 12.3 | 14 | 25.9 | 27.9 | 295.3 | 338.3 | 22.1 | 165.1 | 13 | 162.3 | 137.4 | 12.6 | 39.4 | 24.3 | 21.2
302 | 66 | 552.9 | 221.16 | 258.5233 | 175.5 | 161.9 | 159.9 | 56.6 | 325.8 | 10.4 | 21.4 | 26.3 | 3.1 | 232.6 | 7 | 262.4 | 812.2 | 325.7 | 112.8 | 144.7 | 663.6 | 223 | 397.3 | 664.9 | 83.8 | 58.7 | 508.2 | 12.3 | 14.1 | 26.2 | 28.3 | 296.6 | 338.1 | 22.5 | 166.4 | 13.1 | 163.5 | 138.3 | 12.6 | 39.9 | 24.6 | 21.4
303 | 67 | 554.2 | 221.68 | 259.1311 | 176.6 | 162 | 160.4 | 56.6 | 325.2 | 10.4 | 21.4 | 26.5 | 2.9 | 240.7 | 7.7 | 266.6 | 802.1 | 316.8 | 113.7 | 145.6 | 668 | 224.2 | 394.6 | 664.6 | 85.1 | 59.6 | 512.4 | 12.4 | 14.1 | 26.4 | 28.8 | 295 | 334.3 | 22.6 | 165.9 | 13.1 | 164.5 | 139.5 | 12.7 | 40.5 | 24.9 | 21.7
304 | 68 | 555.4 | 222.16 | 259.6922 | 178.3 | 161.5 | 161.3 | 56.5 | 324.4 | 10.4 | 21.4 | 26.8 | 3.2 | 248.8 | 7.8 | 271.6 | 780.9 | 308.4 | 114.6 | 146.7 | 672 | 225.4 | 393.2 | 665.3 | 86.4 | 60.4 | 517.9 | 12.4 | 14.2 | 26.8 | 29.3 | 294.4 | 332 | 22.8 | 166.3 | 13.2 | 165.7 | 141.5 | 12.7 | 41.1 | 25.2 | 21.9
305 | 69 | 556.5 | 222.6 | 260.2066 | 179.5 | 161.3 | 163.1 | 56.6 | 324.3 | 10.4 | 21.4 | 27.1 | 2.9 | 238.4 | 7.1 | 276.8 | 769.7 | 300.4 | 115.7 | 147.9 | 675.5 | 226.6 | 392.7 | 660.2 | 87.6 | 61.2 | 520.5 | 12.4 | 14.3 | 27.1 | 29.8 | 293.1 | 329.3 | 23.1 | 166.6 | 13.2 | 167 | 143.5 | 12.7 | 41.7 | 25.5 | 22.2
306 | 70 | 555.4 | 222.16 | 259.6922 | 180.6 | 161.9 | 164.8 | 56.5 | 324 | 10.4 | 21.4 | 27.3 | 3.2 | 234.3 | 7.1 | 281.8 | 769.9 | 293 | 116.8 | 149.2 | 678.9 | 227.7 | 393 | 663.8 | 88.8 | 62.1 | 524.2 | 12.4 | 14.4 | 27.5 | 30.3 | 292.2 | 330 | 23.4 | 169 | 13.3 | 167.8 | 144.5 | 12.8 | 42.3 | 25.7 | 22.4
307 | 71 | 554.3 | 221.72 | 259.1779 | 181.4 | 162.5 | 166.9 | 56.3 | 325.4 | 10.5 | 21.4 | 27.5 | 3.4 | 248.6 | 7.3 | 286.5 | 768.7 | 284.8 | 117.9 | 150.6 | 682.1 | 228.9 | 391.7 | 663.7 | 90.1 | 62.9 | 527.5 | 12.4 | 14.5 | 28.1 | 30.8 | 292.1 | 330.9 | 23.7 | 173.7 | 13.4 | 168.8 | 145.4 | 12.8 | 42.9 | 26 | 22.7
308 | 72 | 553.7 | 221.48 | 258.8974 | 181.5 | 163 | 168.5 | 56.3 | 327.7 | 10.5 | 21.4 | 27.8 | 3.6 | 249.5 | 7 | 291.2 | 785.9 | 277.9 | 119.1 | 151.9 | 685.8 | 230.2 | 391.7 | 669.6 | 91.3 | 63.7 | 532.3 | 12.4 | 14.5 | 28.4 | 31.3 | 292.6 | 332.6 | 24 | 175.2 | 13.5 | 169.8 | 146.1 | 12.8 | 43.3 | 26.3 | 22.9
309 | 73 | 557.1 | 222.84 | 260.4871 | 182.2 | 164.3 | 170.7 | 56.4 | 339.7 | 10.5 | 21.4 | 28 | 4 | 240.1 | 6.3 | 295.8 | 789 | 271.1 | 120.1 | 153.2 | 689.4 | 231.6 | 392.7 | 681.6 | 92.5 | 64.6 | 534.2 | 12.4 | 14.6 | 29.4 | 31.8 | 295.7 | 337.1 | 24.4 | 177.2 | 13.5 | 171.1 | 146.9 | 12.9 | 43.9 | 26.6 | 23.2
310 | 74 | 556.1 | 222.44 | 260.0195 | 183.4 | 165.9 | 173.1 | 56.4 | 343.1 | 10.5 | 21.3 | 28.2 | 3.6 | 248 | 6.2 | 300 | 785.5 | 265.1 | 121 | 154.7 | 692.2 | 233.1 | 392 | 670.8 | 93.6 | 65.4 | 535.3 | 12.4 | 14.7 | 29.6 | 32.3 | 295.8 | 342.3 | 24.7 | 178.8 | 13.6 | 172.8 | 148.1 | 12.9 | 44.5 | 26.9 | 23.5
311 | 75 | 556.6 | 222.64 | 260.2533 | 183.2 | 167.4 | 175.7 | 56.5 | 349 | 10.5 | 21.3 | 28.3 | 3.2 | 240 | 6.1 | 304.4 | 768.8 | 259.6 | 121.9 | 156 | 694.8 | 234.6 | 390 | 658.8 | 94.8 | 66.2 | 534.3 | 12.4 | 14.8 | 30.3 | 32.8 | 297.7 | 349.1 | 25.1 | 180.7 | 13.7 | 174.1 | 149.2 | 12.9 | 44.9 | 27.2 | 23.7
312 | 76 | 556.9 | 222.76 | 260.3936 | 183.6 | 169.2 | 179.5 | 56.8 | 354.7 | 10.6 | 21.3 | 28.5 | 3.2 | 235.3 | 6.2 | 308.7 | 757 | 254.9 | 122.8 | 157.7 | 696.1 | 236.2 | 387.5 | 654.4 | 96 | 67 | 535.5 | 12.4 | 14.9 | 30.9 | 33.3 | 298.3 | 346.7 | 25.4 | 181.7 | 13.7 | 175.2 | 150.4 | 13 | 45.4 | 27.5 | 24
313 | 77 | 555.4 | 222.16 | 259.6922 | 184.3 | 171.6 | 183.1 | 57.1 | 353.8 | 10.6 | 21.3 | 28.8 | 3.2 | 237.8 | 6.1 | 312.8 | 760 | 250.3 | 123.7 | 159.4 | 697.8 | 237.9 | 385.7 | 651.5 | 97.2 | 67.9 | 536.3 | 12.4 | 15 | 31 | 33.8 | 297.7 | 346.4 | 25.6 | 182 | 13.8 | 176.5 | 151.6 | 13 | 46.1 | 27.8 | 24.3
314 | 78 | 556.2 | 222.48 | 260.0663 | 184.6 | 174 | 183.9 | 57.3 | 350.7 | 10.6 | 21.3 | 29.1 | 2.7 | 231.4 | 5.6 | 316.9 | 783.4 | 244.8 | 124.4 | 161.1 | 700.3 | 239.6 | 384.7 | 656.5 | 98.4 | 68.7 | 539.5 | 12.4 | 15.1 | 30.8 | 34.4 | 297.1 | 348.1 | 26.1 | 182.9 | 13.9 | 177.8 | 153.2 | 13.1 | 46.6 | 28.1 | 24.6
315 | 79 | 559 | 223.6 | 261.3755 | 185.5 | 174.9 | 185 | 57.5 | 348.2 | 10.6 | 21.3 | 29.4 | 2.2 | 232.2 | 4.8 | 320.9 | 787.6 | 240.5 | 125.1 | 162.8 | 703.1 | 241.3 | 384.1 | 664.2 | 99.6 | 69.5 | 541.8 | 12.4 | 15.3 | 30.9 | 34.9 | 297.9 | 348.7 | 26.9 | 184.1 | 13.9 | 179.4 | 155.6 | 13.1 | 47.2 | 28.4 | 24.8
316 | 80 | 558.8 | 223.52 | 261.282 | 187.5 | 175.7 | 185.5 | 57.6 | 347.3 | 10.7 | 21.3 | 29.6 | 3.2 | 235.4 | 4.4 | 325.1 | 792 | 235.4 | 125.9 | 164.5 | 706.9 | 243.1 | 383.9 | 659.3 | 100.8 | 70.4 | 543.7 | 12.4 | 15.4 | 31.4 | 35.5 | 299 | 348.9 | 27.4 | 185.9 | 14 | 180.2 | 157.7 | 13.1 | 47.8 | 28.6 | 25.1
317 | 81 | 560.4 | 224.16 | 262.0301 | 189 | 176.9 | 185.3 | 57.6 | 347.4 | 10.7 | 21.3 | 29.8 | 3.3 | 214.9 | 4.9 | 329.5 | 786.8 | 230.6 | 126.6 | 166.3 | 709.9 | 244.7 | 381.9 | 651.7 | 102 | 71.2 | 544.4 | 12.4 | 15.5 | 32.1 | 36 | 299.1 | 346.5 | 27.6 | 187.4 | 14.1 | 181.3 | 157.9 | 13.2 | 48.2 | 28.9 | 25.4
318 | 82 | 558.8 | 223.52 | 261.282 | 190.4 | 178.2 | 186 | 57.6 | 348.3 | 10.7 | 21.3 | 30 | 3.5 | 212.5 | 4.8 | 333.9 | 768.1 | 227.2 | 127.4 | 168.3 | 711.3 | 246.3 | 382.7 | 665.4 | 103.2 | 72 | 547.3 | 12.4 | 15.6 | 33 | 36.6 | 299.5 | 346.9 | 27.8 | 189 | 14.2 | 182.1 | 158.5 | 13.2 | 48.9 | 29.2 | 25.7
319 | 83 | 558.3 | 223.32 | 261.0482 | 191.6 | 179.2 | 187.3 | 57.7 | 352.9 | 10.7 | 21.3 | 30.2 | 3.6 | 225.1 | 4.3 | 337.9 | 775.2 | 224.8 | 128.3 | 170.2 | 712.3 | 248.1 | 383.2 | 660.6 | 104.3 | 72.8 | 547.6 | 12.4 | 15.7 | 33.2 | 37.1 | 300.7 | 351.4 | 28.5 | 192.6 | 14.2 | 182.3 | 159 | 13.3 | 49.6 | 29.5 | 25.9
320 | 84 | 557.6 | 223.04 | 260.7209 | 191.4 | 180.1 | 188 | 57.7 | 352.2 | 10.7 | 21.3 | 30.4 | 3.4 | 248.2 | 4.1 | 341.5 | 793.4 | 222 | 129 | 172.1 | 714.7 | 249.8 | 383.2 | 662.5 | 105.4 | 73.6 | 549.1 | 12.4 | 15.8 | 33.4 | 37.7 | 300.9 | 352 | 29 | 194.3 | 14.3 | 183 | 159.8 | 13.3 | 49.8 | 29.8 | 26.2
321 | 85 | 559.1 | 223.64 | 261.4223 | 190.9 | 180.1 | 188.1 | 57.8 | 350 | 10.7 | 21.3 | 30.5 | 3.7 | 261.9 | 4 | 345.8 | 794.4 | 218 | 129.8 | 174 | 718.3 | 251.5 | 383.4 | 670.3 | 106.5 | 74.5 | 552.8 | 12.4 | 16 | 33.4 | 38.2 | 301.5 | 353.2 | 29.2 | 195.6 | 14.4 | 183.7 | 160.4 | 13.4 | 50.3 | 30.1 | 26.5
322 | 86 | 560.3 | 224.12 | 261.9834 | 192.3 | 180.8 | 188 | 58 | 348.8 | 10.7 | 21.3 | 30.7 | 3.4 | 239.7 | 4.2 | 350.7 | 807 | 214 | 130.7 | 175.9 | 720.8 | 253.2 | 382.5 | 671.2 | 107.6 | 75.3 | 556.7 | 12.4 | 16.1 | 33.6 | 38.8 | 302.3 | 352.3 | 29.5 | 197.6 | 14.5 | 183.9 | 161.3 | 13.4 | 50.9 | 30.4 | 26.8
323 | 87 | 560.5 | 224.2 | 262.0769 | 193.1 | 181.7 | 187.9 | 58 | 345.5 | 10.8 | 21.2 | 30.8 | 3.4 | 221.5 | 5.4 | 356.6 | 827 | 210.3 | 131.5 | 177.9 | 722.9 | 254.8 | 382 | 673.3 | 108.6 | 76.1 | 559.9 | 12.4 | 16.2 | 33.9 | 39.4 | 302.7 | 353.5 | 29.8 | 199 | 14.6 | 185.3 | 162 | 13.5 | 51.5 | 30.7 | 27.1
324 | 88 | 559.7 | 223.88 | 261.7028 | 193.9 | 181.9 | 187 | 58 | 348.1 | 10.8 | 21.2 | 31 | 3.4 | 221.5 | 5.9 | 363 | 839.7 | 207.9 | 132.3 | 180 | 724.7 | 256.4 | 386.3 | 689.9 | 109.7 | 77 | 563.6 | 12.5 | 16.4 | 34.4 | 40 | 307.1 | 365.1 | 30.7 | 203.5 | 14.6 | 186.2 | 162.7 | 13.5 | 52 | 31 | 27.4
325 | 89 | 558.8 | 223.52 | 261.282 | 194.4 | 182.4 | 185.4 | 58 | 351.8 | 10.9 | 21.2 | 31.1 | 3.3 | 227.4 | 5.9 | 368.8 | 847.3 | 205 | 133 | 182.3 | 727.1 | 257.9 | 390.4 | 706.3 | 110.7 | 77.9 | 567 | 12.5 | 16.5 | 34.6 | 40.5 | 310.7 | 370 | 31.6 | 206.4 | 14.7 | 186.9 | 163.3 | 13.6 | 52.6 | 31.3 | 27.7
326 | 90 | 558.7 | 223.48 | 261.2352 | 194.5 | 183.9 | 184.3 | 58.2 | 357.4 | 10.9 | 21.2 | 31.3 | 2.9 | 213 | 5.1 | 374.3 | 843.4 | 203.4 | 133.7 | 184.6 | 729.8 | 259.4 | 395 | 715.7 | 111.6 | 78.8 | 571.5 | 12.5 | 16.6 | 35 | 41.1 | 316.1 | 379.1 | 32.2 | 210.4 | 14.8 | 188.1 | 164.2 | 13.7 | 53.1 | 31.7 | 28
327 | 91 | 559.9 | 223.96 | 261.7963 | 195.1 | 184.4 | 183.5 | 58.5 | 362.8 | 11 | 21.2 | 31.4 | 3 | 258.3 | 4.5 | 379.8 | 841 | 201.3 | 134.4 | 187 | 732.3 | 260.9 | 397.5 | 714.3 | 112.6 | 79.7 | 574 | 12.5 | 16.8 | 35.6 | 41.7 | 319.8 | 381.8 | 32.5 | 214.2 | 14.9 | 189.2 | 165.5 | 13.7 | 53.4 | 32 | 28.3
328 | 92 | 560 | 224 | 261.8431 | 196.3 | 185.4 | 183 | 58.7 | 364.8 | 11 | 21.2 | 31.5 | 3.2 | 267.5 | 4.6 | 386.3 | 843 | 199.5 | 135 | 191.1 | 734.6 | 262.4 | 399.8 | 721 | 113.6 | 80.7 | 578.8 | 12.5 | 16.9 | 35.8 | 42.3 | 321.3 | 384.5 | 32.6 | 216.6 | 15 | 189.8 | 166.7 | 13.8 | 53.9 | 32.4 | 28.6
329 | 93 | 560.3 | 224.12 | 261.9834 | 197 | 185.6 | 183 | 58.9 | 365.5 | 11.1 | 21.2 | 31.6 | 3.1 | 235.9 | 6 | 392.9 | 844.7 | 197.2 | 135.5 | 194.4 | 736.4 | 263.8 | 400 | 714.9 | 114.5 | 81.7 | 582.5 | 12.5 | 17.1 | 36.2 | 42.9 | 322.5 | 384.5 | 33.1 | 218.1 | 15.1 | 189.9 | 167.4 | 13.8 | 54.5 | 32.8 | 28.9
330 | 94 | 562.5 | 225 | 263.012 | 198.1 | 185.7 | 184.1 | 59.2 | 364.7 | 11.1 | 21.2 | 31.7 | 3.2 | 232.2 | 6.7 | 399.7 | 840.5 | 194.6 | 136 | 196.8 | 737.4 | 264.9 | 400.4 | 715.9 | 115.4 | 82.7 | 587.3 | 12.5 | 17.3 | 36.9 | 43.5 | 322.2 | 386.4 | 33.8 | 217.6 | 15.1 | 190.2 | 168.6 | 13.9 | 55.1 | 33.1 | 29.2
331 | 95 | 563 | 225.2 | 263.2458 | 199.9 | 186.7 | 184.7 | 59.5 | 363.3 | 11.2 | 21.2 | 31.9 | 3.3 | 232.4 | 6.3 | 408 | 834.2 | 191.6 | 136.5 | 199 | 738.8 | 266.3 | 399.3 | 710.1 | 116.3 | 83.8 | 590.8 | 12.5 | 17.4 | 37.2 | 44.2 | 322.1 | 383 | 34.6 | 218.3 | 15.2 | 190.9 | 170.2 | 14 | 55.6 | 33.5 | 29.5
332 | 96 | 561.1 | 224.44 | 262.3574 | 202 | 187.2 | 184.9 | 59.7 | 361 | 11.3 | 21.2 | 32 | 3.1 | 257.2 | 5.6 | 416.5 | 832.8 | 189.3 | 137 | 201 | 740.8 | 267.5 | 398 | 706.8 | 117.3 | 85 | 594.2 | 12.5 | 17.6 | 37.6 | 44.8 | 321.1 | 378.7 | 34.8 | 217.2 | 15.3 | 191.6 | 170.6 | 14.1 | 56.1 | 33.8 | 29.8
333 | 97 | 561 | 224.4 | 262.3107 | 203.5 | 186.9 | 184.9 | 59.7 | 359.6 | 11.4 | 21.2 | 32.3 | 3.1 | 237.6 | 4.8 | 427.2 | 837.6 | 186.9 | 137.6 | 203.1 | 742.6 | 268.8 | 396.9 | 707 | 118.2 | 86.3 | 596.5 | 12.5 | 17.7 | 37.7 | 45.4 | 321.2 | 377.7 | 35.1 | 217.4 | 15.4 | 192.5 | 170.7 | 14.1 | 56.7 | 34.1 | 30.1
334 | 98 | 559 | 223.6 | 261.3755 | 204.8 | 185.9 | 184.3 | 59.8 | 359.4 | 11.5 | 21.2 | 32.5 | 3 | 226.2 | 4.9 | 438.5 | 845.7 | 185.3 | 138.1 | 204.9 | 744.3 | 270.2 | 397 | 709.1 | 119.1 | 87.6 | 601.1 | 12.5 | 17.9 | 38 | 46.1 | 321.9 | 377.9 | 35.6 | 218.3 | 15.5 | 193.7 | 171 | 14.2 | 57.1 | 34.4 | 30.3
335 | 99 | 560.8 | 224.32 | 262.2172 | 205.9 | 185.4 | 184.1 | 59.9 | 360.1 | 11.5 | 21.2 | 32.8 | 3.1 | 238.6 | 5.1 | 449 | 848.3 | 184.1 | 138.8 | 206.7 | 746.1 | 271.7 | 398.5 | 717.2 | 120 | 88.9 | 606.2 | 12.5 | 18 | 38.3 | 46.7 | 321.7 | 375.9 | 36.1 | 219.4 | 15.6 | 194.9 | 171.3 | 14.2 | 57.5 | 34.7 | 30.6
336 | 100 | 561.6 | 224.64 | 262.5912 | 206 | 185.7 | 182.8 | 60 | 362.1 | 11.6 | 21.2 | 33.1 | 3 | 241.2 | 5.2 | 459.6 | 851.1 | 182.9 | 139.4 | 208.4 | 747.7 | 273 | 401.9 | 719.6 | 120.9 | 90.2 | 608.7 | 12.6 | 18.2 | 38.7 | 47.3 | 324 | 380.2 | 36.9 | 223.5 | 15.7 | 195.8 | 172.2 | 14.3 | 58 | 35 | 30.9
337 | 101 | 563.2 | 225.28 | 263.3393 | 206.4 | 185.8 | 182.4 | 60 | 365.3 | 11.6 | 21.2 | 33.3 | 3.1 | 239.5 | 4.9 | 470.9 | 851.3 | 181.5 | 140.1 | 210.1 | 749.3 | 274.2 | 403.1 | 711.2 | 121.8 | 91.6 | 611.1 | 12.6 | 18.3 | 39 | 48 | 324.9 | 379.8 | 37.1 | 226 | 15.8 | 196.4 | 173.2 | 14.4 | 58.5 | 35.4 | 31.2
338 | 102 | 562.3 | 224.92 | 262.9185 | 206.4 | 185.7 | 182.2 | 60.1 | 363.2 | 11.7 | 21.2 | 33.4 | 3.1 | 238.6 | 5.1 | 481.9 | 855.8 | 179.5 | 140.7 | 211.6 | 751 | 275.5 | 401.9 | 708.3 | 122.6 | 93 | 613.9 | 12.6 | 18.5 | 39.2 | 48.6 | 324 | 377 | 37.4 | 225.3 | 15.9 | 197.3 | 174.1 | 14.5 | 59.1 | 35.7 | 31.5
339 | 103 | 561.8 | 224.72 | 262.6847 | 206.6 | 185.4 | 183 | 60.3 | 360.9 | 11.9 | 21.2 | 33.7 | 3.3 | 242 | 5.9 | 492.9 | 846.2 | 178.1 | 141.5 | 213 | 753.2 | 276.7 | 402.5 | 712.7 | 123.5 | 94.4 | 618.4 | 12.6 | 18.7 | 39.3 | 49.2 | 324.4 | 377.4 | 37.6 | 226 | 16 | 199.1 | 175.2 | 14.5 | 59.5 | 36 | 31.8
340 | 104 | 563.1 | 225.24 | 263.2926 | 208.2 | 185 | 183.5 | 60.4 | 360 | 12 | 21.2 | 33.9 | 3.3 | 226.7 | 5.7 | 506 | 844.7 | 176 | 142.3 | 214.4 | 755.6 | 277.6 | 402.8 | 710.3 | 124.3 | 95.8 | 620 | 12.6 | 18.8 | 39.7 | 49.8 | 325.3 | 374.7 | 38.2 | 227.3 | 16.1 | 200 | 176.3 | 14.6 | 60 | 36.3 | 32.1
341 | 105 | 562 | 224.8 | 262.7782 | 209.7 | 185.1 | 183.8 | 60.5 | 357.6 | 12.1 | 21.2 | 34.1 | 3.4 | 215.3 | 5.2 | 518.6 | 836.2 | 174.1 | 143 | 215.7 | 757.7 | 278.6 | 402.2 | 708.1 | 125.3 | 97.3 | 622.9 | 12.6 | 19 | 40 | 50.4 | 324.9 | 373.9 | 38.7 | 228 | 16.2 | 200.6 | 177 | 14.7 | 60.5 | 36.7 | 32.4
342 | 106 | 560.3 | 224.12 | 261.9834 | 210.6 | 184.9 | 183.9 | 60.7 | 357.1 | 12.1 | 21.2 | 34.4 | 3.2 | 219.6 | 4.6 | 530.4 | 815.8 | 172.3 | 143.7 | 217 | 759 | 279.8 | 402 | 703.2 | 126.2 | 98.8 | 624.7 | 12.6 | 19.2 | 40.7 | 51 | 325.7 | 373.8 | 39.2 | 229.2 | 16.3 | 201.7 | 178.5 | 14.8 | 61 | 37 | 32.7
343 | 107 | 562.8 | 225.12 | 263.1523 | 212.4 | 184.6 | 183.6 | 61 | 358.3 | 12.1 | 21.1 | 34.7 | 3.3 | 213.2 | 4.4 | 541.2 | 814.7 | 170.9 | 144.5 | 218.3 | 761.5 | 281.1 | 400.3 | 700.1 | 127.1 | 100.3 | 624.9 | 12.6 | 19.4 | 41.1 | 51.6 | 327.3 | 371.6 | 39.6 | 229.4 | 16.4 | 203 | 179.3 | 14.9 | 61.5 | 37.3 | 33.1
344 | 108 | 563.7 | 225.48 | 263.5731 | 214.2 | 184.5 | 184 | 61.4 | 359 | 12.2 | 21.1 | 34.9 | 3.6 | 228.5 | 4.2 | 551.1 | 812.8 | 169.1 | 145.6 | 219.5 | 763.6 | 282.5 | 399.9 | 698 | 128 | 101.8 | 628 | 12.7 | 19.5 | 41.5 | 52.2 | 326.4 | 372.1 | 39.8 | 229.3 | 16.5 | 203.1 | 180.1 | 14.9 | 61.9 | 37.7 | 33.4
345 | 109 | 564.6 | 225.84 | 263.9939 | 216.1 | 184.8 | 183.7 | 61.6 | 358.7 | 12.3 | 21.1 | 35.1 | 3.3 | 249.1 | 4.4 | 560.9 | 822.9 | 167.9 | 146.5 | 220.7 | 766 | 283.6 | 399.1 | 700.3 | 128.8 | 103.3 | 629 | 12.7 | 19.7 | 41.7 | 52.8 | 326.2 | 373.4 | 40.3 | 229.9 | 16.6 | 203.8 | 181.1 | 15 | 62.2 | 38 | 33.7
346 | 110 | 563 | 225.2 | 263.2458 | 217.2 | 185.2 | 185 | 61.6 | 357 | 12.4 | 21.1 | 35.4 | 3.2 | 241 | 4.3 | 571.7 | 823 | 167 | 147.1 | 221.8 | 767.6 | 284.5 | 399 | 701.8 | 129.7 | 104.7 | 631.8 | 12.7 | 19.9 | 41.8 | 53.4 | 326.3 | 372.6 | 40.8 | 230.6 | 16.7 | 204.4 | 181.6 | 15.2 | 62.8 | 38.3 | 34
347 | 111 | 564 | 225.6 | 263.7134 | 217.8 | 185.2 | 186.3 | 61.6 | 356.3 | 12.5 | 21.1 | 35.7 | 3.4 | 242.9 | 4.4 | 581.3 | 832 | 166.2 | 147.8 | 222.8 | 768.4 | 285.3 | 399.9 | 706.1 | 130.5 | 106.2 | 633.7 | 12.7 | 20 | 42.4 | 54 | 325.8 | 373.1 | 41 | 231.7 | 16.8 | 204.5 | 181.6 | 15.3 | 63.2 | 38.6 | 34.3
348 | 112 | 563.4 | 225.36 | 263.4329 | 218.3 | 185 | 186.6 | 61.7 | 353.9 | 12.5 | 21.1 | 36 | 3.5 | 244.1 | 4.4 | 588.1 | 829.5 | 165.5 | 148.7 | 223.8 | 769.9 | 286.4 | 401.1 | 715.5 | 131.3 | 107.6 | 637.4 | 12.7 | 20.2 | 42.7 | 54.5 | 325.1 | 372.5 | 41.3 | 233.2 | 16.9 | 204.2 | 181.5 | 15.4 | 63.7 | 38.9 | 34.6
349 | 113 | 562.8 | 225.12 | 263.1523 | 219 | 184.9 | 186.1 | 61.8 | 354.7 | 12.6 | 21.1 | 36.2 | 3.7 | 240.6 | 4.4 | 596.9 | 833.6 | 164.2 | 149.8 | 225 | 772.5 | 287.5 | 403.3 | 720.3 | 132.2 | 109.1 | 639.7 | 12.7 | 20.3 | 42.9 | 55.1 | 326.1 | 377.5 | 42.2 | 236.3 | 17 | 204 | 181.7 | 15.5 | 64.1 | 39.2 | 34.8
350 | 114 | 562.3 | 224.92 | 262.9185 | 219.9 | 184.8 | 185.2 | 61.8 | 358 | 12.7 | 21.1 | 36.4 | 3.2 | 242 | 4.5 | 603.8 | 827.1 | 163.8 | 150.7 | 226.1 | 774.7 | 288.5 | 403.6 | 720.6 | 133 | 110.5 | 641.9 | 12.8 | 20.5 | 43.3 | 55.7 | 327.4 | 378.5 | 42.5 | 237.6 | 17.1 | 204.6 | 182 | 15.6 | 64.4 | 39.6 | 35.1
351 | 115 | 563.6 | 225.44 | 263.5264 | 220.3 | 185.7 | 185.8 | 61.8 | 359 | 12.7 | 21.1 | 36.6 | 3.4 | 241.9 | 4.7 | 608.9 | 827.2 | 163.3 | 151.6 | 227.2 | 776.1 | 289.5 | 403.5 | 720.9 | 133.9 | 111.9 | 643 | 12.8 | 20.7 | 43.5 | 56.2 | 328.1 | 379.8 | 43 | 238.9 | 17.3 | 205.6 | 183.1 | 15.7 | 64.9 | 39.9 | 35.4
352 | 116 | 565.9 | 226.36 | 264.6018 | 220.4 | 186.9 | 185.6 | 61.8 | 360.1 | 12.8 | 21.1 | 36.7 | 3.5 | 242.4 | 4.9 | 616.3 | 826.4 | 162.4 | 152.6 | 228.2 | 778 | 290.6 | 403.2 | 725.8 | 134.8 | 113.3 | 643.9 | 12.8 | 20.8 | 43.7 | 56.7 | 328.3 | 378.5 | 43.3 | 239.8 | 17.4 | 206.1 | 183.9 | 15.9 | 65.3 | 40.2 | 35.7
353 | 117 | 564.2 | 225.68 | 263.8069 | 220.1 | 186.9 | 185.5 | 62 | 359.5 | 12.8 | 21.1 | 36.9 | 3.5 | 240 | 4.5 | 622.8 | 834.7 | 161.8 | 153.5 | 229.1 | 778.5 | 291.7 | 404.9 | 733.2 | 135.7 | 114.6 | 646.6 | 12.8 | 21 | 44.1 | 57.3 | 328.5 | 383 | 43.5 | 241.7 | 17.5 | 206.5 | 184.4 | 16 | 65.7 | 40.5 | 36
354 | 118 | 564.2 | 225.68 | 263.8069 | 220.8 | 186.9 | 187.1 | 62.1 | 363.5 | 12.9 | 21.1 | 37 | 3.4 | 241.6 | 4.5 | 628.3 | 845.3 | 161.7 | 154.4 | 229.8 | 780.2 | 293 | 407.4 | 736.6 | 136.6 | 116 | 647.6 | 12.8 | 21.2 | 44.4 | 57.8 | 331.5 | 389.4 | 44.5 | 244.8 | 17.6 | 206.8 | 184.7 | 16.1 | 66.1 | 40.8 | 36.3
355 | 119 | 564.4 | 225.76 | 263.9004 | 220.8 | 186.8 | 187.3 | 62.2 | 366.8 | 13 | 21.1 | 37 | 3.8 | 247 | 5 | 637.8 | 844.8 | 161.5 | 155.4 | 230.3 | 781.8 | 294.5 | 407.5 | 733.1 | 137.5 | 117.4 | 649.1 | 12.8 | 21.3 | 44.9 | 58.4 | 330.6 | 388.1 | 44.7 | 244.9 | 17.7 | 206.9 | 184.8 | 16.2 | 66.5 | 41.1 | 36.6
356 | 120 | 564.5 | 225.8 | 263.9472 | 221.9 | 187.1 | 188 | 62.3 | 365.1 | 13 | 21.1 | 37.2 | 3.3 | 254.7 | 5.2 | 643.8 | 846.4 | 161.1 | 156.2 | 230.9 | 783.3 | 296.1 | 407.7 | 731.6 | 138.4 | 118.7 | 651 | 12.8 | 21.5 | 45.2 | 58.9 | 330.4 | 386.5 | 45.2 | 244.5 | 17.8 | 206.9 | 186 | 16.3 | 67.1 | 41.5 | 36.9
357 | 121 | 564.5 | 225.8 | 263.9472 | 222.8 | 187.7 | 188.4 | 62.2 | 366.3 | 13.1 | 21.1 | 37.3 | 3.5 | 263.4 | 5.1 | 648.4 | 831.7 | 161.4 | 156.8 | 231.6 | 784.6 | 297.8 | 407.6 | 732.9 | 139.4 | 120.1 | 651.9 | 12.8 | 21.7 | 45.7 | 59.4 | 331.3 | 388.5 | 45.6 | 245.9 | 18 | 206.8 | 187.3 | 16.4 | 67.6 | 41.8 | 37.2
358 | 122 | 565.1 | 226.04 | 264.2277 | 223.2 | 188.1 | 188.8 | 62.2 | 367.8 | 13.2 | 21 | 37.4 | 3.4 | 250.1 | 4.7 | 655 | 820.9 | 160.4 | 157.7 | 233.2 | 785.9 | 299.6 | 406.6 | 722.6 | 140.4 | 121.4 | 650.9 | 12.9 | 21.9 | 45.9 | 59.9 | 331.2 | 385.4 | 46 | 246.3 | 18.1 | 206.7 | 187.5 | 16.5 | 68 | 42.1 | 37.4
359 | 123 | 564.8 | 225.92 | 264.0875 | 223.7 | 188.5 | 191.1 | 62.2 | 366.4 | 13.3 | 21 | 37.7 | 3.5 | 228.9 | 4.6 | 660.8 | 819.2 | 159.3 | 158.6 | 234.4 | 787.6 | 301.5 | 404.7 | 717.4 | 141.4 | 122.7 | 652.1 | 12.9 | 22.1 | 46.3 | 60.4 | 329.8 | 380.7 | 46.1 | 245.9 | 18.2 | 207 | 188 | 16.7 | 68.3 | 42.4 | 37.7
360 | 124 | 565.2 | 226.08 | 264.2745 | 224.2 | 189 | 192 | 62.2 | 368 | 13.3 | 21 | 37.8 | 3.4 | 228.1 | 4.4 | 659.7 | 824.3 | 160.8 | 159.5 | 235.4 | 787.7 | 303.6 | 405.6 | 715.9 | 142.4 | 124 | 652.3 | 12.9 | 22.3 | 46.9 | 60.9 | 331.2 | 386.9 | 46.4 | 248 | 18.3 | 207.5 | 188.7 | 16.8 | 68.7 | 42.7 | 38
361 | 125 | 564.5 | 225.8 | 263.9472 | 224.6 | 189.4 | 191 | 62.3 | 375.1 | 13.4 | 21 | 38 | 3.3 | 229.2 | 4.2 | 661.9 | 839.5 | 160.1 | 160.4 | 236.2 | 787 | 305.8 | 408.3 | 721.2 | 143.5 | 125.3 | 654 | 12.9 | 22.5 | 47.6 | 61.4 | 334 | 394.5 | 47 | 251 | 18.5 | 207.7 | 188.4 | 16.9 | 69.2 | 43.1 | 38.3
362 | 126 | 564.7 | 225.88 | 264.0407 | 223.3 | 190.6 | 191.6 | 62.3 | 377.2 | 13.5 | 21 | 38.3 | 3.3 | 237.7 | 4.3 | 666.7 | 849.2 | 160.3 | 161.2 | 236.9 | 787.1 | 307.9 | 410.4 | 729.3 | 144.5 | 126.6 | 655.8 | 12.9 | 22.6 | 47.6 | 61.8 | 336 | 398.6 | 47.5 | 254.3 | 18.6 | 208.1 | 188.2 | 17 | 69.7 | 43.4 | 38.6
363 | 127 | 566.8 | 226.72 | 265.0226 | 222.2 | 192.3 | 192.3 | 62.4 | 377.1 | 13.6 | 21 | 38.5 | 3.8 | 249.1 | 4 | 669.1 | 856.2 | 161.6 | 162.1 | 237.5 | 787.5 | 309.9 | 414.4 | 735.7 | 145.6 | 127.9 | 657.3 | 12.9 | 22.8 | 47.9 | 62.3 | 338 | 406.5 | 47.7 | 259.4 | 18.7 | 208.5 | 189.1 | 17.1 | 70 | 43.8 | 38.9
364 | 128 | 567.3 | 226.92 | 265.2564 | 222 | 193.4 | 191.6 | 62.5 | 378.4 | 13.7 | 21 | 38.7 | 3.4 | 249.3 | 3.8 | 668.7 | 856.7 | 163.4 | 163 | 238 | 787.2 | 311.8 | 416.6 | 739.4 | 146.7 | 129.1 | 657.6 | 13 | 23 | 48.2 | 62.7 | 339.6 | 412.4 | 48.2 | 264.6 | 18.9 | 209.8 | 189.9 | 17.3 | 70.3 | 44.2 | 39.2
365 | 129 | 568.1 | 227.24 | 265.6305 | 223.3 | 194.8 | 191.4 | 62.6 | 379.3 | 13.8 | 21 | 39 | 2.9 | 248 | 3.7 | 671.3 | 864.1 | 164.6 | 163.9 | 238.6 | 787 | 313.7 | 416.6 | 744.7 | 147.8 | 130.3 | 658 | 13 | 23.2 | 48.4 | 63.2 | 341 | 413.6 | 48.6 | 266.9 | 19 | 210.7 | 190.5 | 17.5 | 70.7 | 44.6 | 39.4
366 | 130 | 568.5 | 227.4 | 265.8175 | 223.7 | 197 | 190.9 | 62.7 | 375.8 | 13.8 | 21 | 39.2 | 3.1 | 242.4 | 3.5 | 678.8 | 854 | 165.2 | 164.8 | 239 | 788 | 315.4 | 419.1 | 743.6 | 148.9 | 131.6 | 660.9 | 13 | 23.4 | 48.7 | 63.6 | 341.7 | 411.5 | 49 | 270.1 | 19.1 | 211 | 190.9 | 17.6 | 71.2 | 45 | 39.7
367 | 131 | 567 | 226.8 | 265.1161 | 224.6 | 199.4 | 190.2 | 63 | 373.8 | 13.9 | 21 | 39.3 | 3.4 | 239.9 | 3.6 | 689 | 855.7 | 165.7 | 165.8 | 239.3 | 788.3 | 317 | 421 | 740.6 | 150 | 132.8 | 660.4 | 13 | 23.6 | 49 | 64.1 | 344.1 | 409.7 | 49.4 | 273.9 | 19.3 | 211.9 | 191.5 | 17.7 | 71.7 | 45.4 | 40
368 | 132 | 564.8 | 225.92 | 264.0875 | 224.3 | 201.3 | 188.6 | 63.3 | 369.8 | 14 | 21 | 39.5 | 3.4 | 256.2 | 4 | 693.4 | 860.5 | 166.2 | 166.8 | 239.7 | 789.1 | 318.6 | 422.1 | 736.5 | 151.2 | 134.1 | 660.3 | 13 | 23.7 | 49.1 | 64.5 | 344.9 | 408.7 | 49.8 | 275.9 | 19.4 | 214.8 | 192 | 17.9 | 72.3 | 45.9 | 40.4
369 | 133 | 565.8 | 226.32 | 264.555 | 223.3 | 202.7 | 186 | 63.8 | 368.1 | 14.1 | 21 | 39.7 | 3.7 | 250 | 3.9 | 698.8 | 861.2 | 166 | 167.8 | 240.2 | 789.6 | 320 | 423.5 | 742.3 | 152.4 | 135.5 | 662.2 | 13 | 23.9 | 49.7 | 64.9 | 345.3 | 408.5 | 50.4 | 275.5 | 19.5 | 216.5 | 192.6 | 18 | 72.6 | 46.3 | 40.8
370 | 134 | 564.9 | 225.96 | 264.1342 | 223.5 | 203.8 | 185.8 | 64.2 | 368.5 | 14.1 | 21 | 39.9 | 3.9 | 214.2 | 3.5 | 701 | 855.3 | 165.4 | 168.8 | 240.8 | 788.7 | 321.4 | 424.5 | 746.6 | 153.5 | 136.9 | 663 | 13.1 | 24.1 | 49.9 | 65.3 | 345.6 | 406.2 | 50.6 | 276.3 | 19.7 | 218 | 193.6 | 18.2 | 73.1 | 46.7 | 41.1
371 | 135 | 566.9 | 226.76 | 265.0694 | 222.7 | 204.9 | 185.5 | 64.6 | 366.8 | 14.3 | 21 | 40 | 3.8 | 201.9 | 3.5 | 702.8 | 859 | 166 | 169.8 | 241.3 | 789.2 | 322.7 | 424.2 | 751.1 | 154.7 | 138.3 | 663.9 | 13.1 | 24.3 | 50.1 | 65.8 | 345.1 | 405.6 | 50.9 | 276.6 | 19.8 | 219.1 | 194.6 | 18.3 | 73.5 | 47.1 | 41.5
372 | 136 | 566.8 | 226.72 | 265.0226 | 223.3 | 206.1 | 184.6 | 64.8 | 369.4 | 14.3 | 21 | 40.2 | 3.5 | 202 | 4.1 | 702.6 | 850.7 | 165.9 | 170.9 | 241.9 | 790.8 | 324 | 425.2 | 755.2 | 155.8 | 139.8 | 665.4 | 13.1 | 24.5 | 50.6 | 66.2 | 345.5 | 409.5 | 51.4 | 277.7 | 20 | 219.1 | 195 | 18.4 | 73.8 | 47.5 | 41.9
373 | 137 | 567 | 226.8 | 265.1161 | 223.6 | 206.5 | 184.6 | 64.9 | 375.2 | 14.4 | 21 | 40.4 | 3.8 | 207.2 | 5 | 700.3 | 845.3 | 166.6 | 172 | 242.5 | 791.3 | 325.2 | 426.9 | 756 | 156.9 | 141.4 | 665.6 | 13.1 | 24.7 | 51.2 | 66.7 | 346.7 | 416.9 | 52 | 278.5 | 20.1 | 219 | 195.1 | 18.6 | 74.1 | 47.9 | 42.2
374 | 138 | 566.9 | 226.76 | 265.0694 | 223.9 | 206.4 | 185.6 | 64.9 | 383.4 | 14.4 | 21 | 40.6 | 3.5 | 212.7 | 5.7 | 701.8 | 836.2 | 167.3 | 173 | 243.1 | 790.3 | 326.5 | 429.2 | 754.6 | 158.1 | 142.9 | 665.7 | 13.1 | 24.9 | 51.9 | 67.1 | 348.1 | 426.6 | 52.5 | 281.1 | 20.2 | 219 | 195.9 | 18.8 | 74.4 | 48.3 | 42.5
375 | 139 | 567 | 226.8 | 265.1161 | 223.8 | 206.2 | 189.2 | 64.7 | 388.1 | 14.5 | 20.9 | 40.6 | 3.8 | 202.6 | 6.2 | 706.4 | 839 | 167.6 | 174 | 243.8 | 790.1 | 327.9 | 430.2 | 745.2 | 159.2 | 144.5 | 664.7 | 13.2 | 25.1 | 52.4 | 67.5 | 349.9 | 425.8 | 53 | 281.1 | 20.4 | 218.8 | 195.8 | 18.9 | 74.8 | 48.7 | 42.7
376 | 140 | 566.2 | 226.48 | 264.7421 | 223.4 | 206.6 | 192.6 | 64.6 | 390 | 14.5 | 20.9 | 40.7 | 3.3 | 200.2 | 5.3 | 711.8 | 834.6 | 167.1 | 175 | 244.4 | 792 | 329.3 | 431.1 | 747.1 | 160.3 | 146.1 | 665.2 | 13.2 | 25.3 | 52.4 | 68 | 349.9 | 423.5 | 53.4 | 281.1 | 20.5 | 219 | 196 | 19.1 | 75.2 | 49.1 | 43
377 | 141 | 567.5 | 227 | 265.3499 | 222.8 | 206.3 | 193.6 | 64.6 | 391.6 | 14.6 | 20.9 | 40.8 | 3.5 | 223.2 | 4.7 | 715.8 | 832.4 | 166.1 | 176 | 245.1 | 793.9 | 330.7 | 431.9 | 746.9 | 161.4 | 147.7 | 667.1 | 13.2 | 25.5 | 52.8 | 68.4 | 349.9 | 422 | 53.7 | 280.7 | 20.7 | 219.3 | 196.2 | 19.2 | 75.4 | 49.6 | 43.3
378 | 142 | 566.2 | 226.48 | 264.7421 | 223.6 | 205.9 | 193.7 | 64.6 | 391.6 | 14.8 | 20.9 | 40.9 | 3.5 | 217.5 | 4.7 | 719.1 | 839.2 | 165.3 | 177 | 245.7 | 796 | 332.1 | 433.8 | 748.1 | 162.6 | 149.3 | 668.2 | 13.2 | 25.7 | 53.1 | 68.9 | 349.3 | 420.4 | 53.9 | 280.7 | 20.8 | 219.6 | 196.2 | 19.3 | 75.6 | 49.9 | 43.6
379 | 143 | 565.2 | 226.08 | 264.2745 | 223.8 | 205.8 | 193.4 | 64.7 | 390.2 | 14.9 | 20.9 | 41.1 | 3.5 | 213.8 | 5 | 717.5 | 841 | 165.1 | 178 | 246.1 | 797.5 | 333.6 | 435.6 | 760.2 | 163.7 | 150.8 | 671.5 | 13.2 | 25.9 | 53.6 | 69.3 | 350.8 | 425.4 | 54.2 | 283 | 21 | 220.1 | 196.3 | 19.5 | 76.1 | 50.3 | 43.9
380 | 144 | 566 | 226.4 | 264.6486 | 223.5 | 205.7 | 193.1 | 64.8 | 393.8 | 15 | 20.9 | 41.3 | 3.8 | 228.7 | 4.8 | 715.6 | 837.3 | 164.4 | 179 | 246.5 | 798.8 | 335.2 | 437.8 | 764 | 164.9 | 152.4 | 673.1 | 13.3 | 26.1 | 54.3 | 69.8 | 352.4 | 426.3 | 54.7 | 285.6 | 21.1 | 220 | 197.7 | 19.7 | 76.4 | 50.7 | 44.2
381 | 145 | 565.4 | 226.16 | 264.368 | 223.9 | 206.4 | 193.4 | 65 | 394.8 | 15.1 | 20.9 | 41.5 | 3.9 | 230.7 | 5 | 719.8 | 843 | 164.1 | 180 | 246.7 | 800 | 336.8 | 440.7 | 768.5 | 166 | 153.9 | 674.8 | 13.3 | 26.3 | 54.5 | 70.3 | 353.7 | 425.3 | 55.1 | 287.7 | 21.3 | 220 | 197.7 | 19.8 | 76.6 | 51.1 | 44.5
382 | 146 | 565.9 | 226.36 | 264.6018 | 224.4 | 207.5 | 194.6 | 65.2 | 395.3 | 15.2 | 20.9 | 41.7 | 3.6 | 185.9 | 4.9 | 723.8 | 849.5 | 164.1 | 181.1 | 247 | 801.1 | 338.3 | 441.2 | 767.4 | 167.1 | 155.4 | 675.1 | 13.3 | 26.6 | 54.8 | 70.7 | 354.7 | 431.2 | 55.5 | 288.9 | 21.4 | 220.5 | 198.4 | 20 | 77 | 51.5 | 44.8
383 | 147 | 566.3 | 226.52 | 264.7888 | 224.1 | 208.7 | 194.7 | 65.5 | 396.8 | 15.3 | 20.9 | 41.8 | 4 | 201.8 | 3.6 | 724.6 | 852.3 | 163.3 | 182.1 | 247 | 802.9 | 339.8 | 441 | 772.5 | 168.2 | 156.9 | 676.2 | 13.3 | 26.8 | 55.1 | 71.2 | 358.4 | 436.4 | 56.3 | 291.9 | 21.6 | 220.6 | 198.4 | 20.1 | 77.5 | 51.9 | 45.1
384 | 148 | 564.7 | 225.88 | 264.0407 | 224.2 | 210 | 194 | 65.7 | 400.8 | 15.5 | 20.9 | 41.9 | 3.9 | 239.7 | 3.6 | 722.8 | 855.5 | 164.2 | 183.2 | 245.9 | 803.7 | 341.3 | 442.8 | 779.4 | 169.4 | 158.4 | 678.4 | 13.4 | 27 | 55.5 | 71.7 | 361 | 439.1 | 56.8 | 294.1 | 21.7 | 220.9 | 198.1 | 20.3 | 77.9 | 52.3 | 45.4
385 | 149 | 566.6 | 226.64 | 264.9291 | 223.8 | 210.3 | 194.3 | 66 | 409.6 | 15.6 | 20.9 | 42 | 3.7 | 238.6 | 3.8 | 720 | 849.2 | 164.9 | 184.3 | 245 | 803.5 | 342.8 | 445.2 | 776.3 | 170.5 | 159.9 | 677.3 | 13.4 | 27.2 | 56.4 | 72.2 | 363.8 | 447.1 | 57.4 | 296.9 | 21.9 | 221.2 | 198 | 20.5 | 78.2 | 52.8 | 45.7
386 | 150 | 566.3 | 226.52 | 264.7888 | 223.4 | 210.6 | 195.5 | 66.2 | 418.6 | 15.7 | 20.9 | 42.2 | 3.7 | 222.5 | 3.7 | 721 | 852.3 | 165 | 185.5 | 244.5 | 802.9 | 344.4 | 445.1 | 781.7 | 171.7 | 161.3 | 677.7 | 13.4 | 27.4 | 56.7 | 72.7 | 365.6 | 449.3 | 57.8 | 299.3 | 22 | 221.1 | 198.1 | 20.6 | 78.6 | 53.2 | 46.1
387 | 151 | 565.7 | 226.28 | 264.5083 | 222.4 | 211.2 | 194.9 | 66.3 | 414.5 | 15.8 | 20.9 | 42.4 | 3.3 | 223.3 | 4.2 | 722.5 | 858.9 | 164 | 186.7 | 244.2 | 804.2 | 345.8 | 445.6 | 790.3 | 172.8 | 162.8 | 681.1 | 13.4 | 27.6 | 56.9 | 73.1 | 364.7 | 447.7 | 57.8 | 298.8 | 22.2 | 221.2 | 197.9 | 20.8 | 79 | 53.7 | 46.4
388 | 152 | 564.8 | 225.92 | 264.0875 | 221.7 | 211.9 | 193.9 | 66.4 | 410.3 | 15.8 | 20.9 | 42.6 | 4.3 | 251.9 | 4.3 | 722.4 | 860.2 | 163.1 | 187.9 | 243.9 | 806.2 | 347.2 | 446.1 | 791 | 174 | 164.2 | 682.8 | 13.5 | 27.9 | 57.2 | 73.6 | 365.1 | 446.7 | 58 | 299.7 | 22.3 | 221.7 | 198.1 | 21 | 79.3 | 54.1 | 46.7
389 | 153 | 564.4 | 225.76 | 263.9004 | 223 | 212.3 | 194.3 | 66.6 | 406.5 | 15.9 | 20.9 | 42.8 | 3.9 | 223.8 | 4.1 | 722.3 | 849.4 | 162.4 | 189.1 | 243.9 | 807.8 | 348.6 | 445.4 | 784.8 | 175.1 | 165.5 | 683.4 | 13.5 | 28.1 | 57.6 | 74.1 | 365.9 | 442.4 | 58.2 | 299.3 | 22.5 | 222.8 | 198.4 | 21.2 | 79.4 | 54.5 | 47
390 | 154 | 563.8 | 225.52 | 263.6199 | 225.5 | 212.2 | 195.2 | 66.8 | 403.3 | 15.9 | 20.9 | 42.9 | 3.7 | 204.9 | 4.6 | 726 | 851.2 | 162.2 | 190.3 | 244 | 809.5 | 350 | 445.8 | 784.8 | 176.3 | 166.8 | 683.9 | 13.5 | 28.3 | 58 | 74.6 | 365.2 | 444.5 | 58.5 | 299.3 | 22.6 | 223.4 | 198.9 | 21.3 | 79.7 | 55 | 47.3
391 | 155 | 564.9 | 225.96 | 264.1342 | 226.1 | 212.3 | 193.8 | 67 | 407.7 | 16 | 20.9 | 43 | 3.6 | 220.6 | 4.7 | 727.5 | 851.8 | 162.2 | 191.5 | 244.2 | 811 | 351.4 | 446.4 | 782.5 | 177.4 | 168.2 | 684.3 | 13.5 | 28.5 | 58.4 | 75.1 | 366.4 | 448.9 | 58.9 | 299.3 | 22.8 | 223.8 | 199.3 | 21.5 | 80.1 | 55.4 | 47.7
392 | 156 | 567.6 | 227.04 | 265.3967 | 225.9 | 212.2 | 192.9 | 67.1 | 411.6 | 16.1 | 20.9 | 43.2 | 3.6 | 194 | 5 | 727.8 | 849.9 | 161.8 | 192.8 | 244.4 | 811.9 | 352.6 | 447.8 | 784.6 | 178.5 | 169.4 | 685.3 | 13.6 | 28.7 | 58.8 | 75.6 | 367 | 447.8 | 59.2 | 299.8 | 22.9 | 224.1 | 199.4 | 21.7 | 80.5 | 55.8 | 48
393 | 157 | 566.8 | 226.72 | 265.0226 | 225.4 | 213.2 | 193.7 | 67.2 | 412.2 | 16.1 | 20.9 | 43.3 | 3.3 | 204.1 | 5.4 | 727.6 | 853.7 | 161.8 | 194.1 | 244.8 | 812.9 | 353.9 | 446.9 | 789.2 | 179.6 | 170.7 | 687.3 | 13.6 | 29 | 58.9 | 76.2 | 368.3 | 448.2 | 59.7 | 302 | 23.1 | 223.9 | 199.7 | 21.9 | 80.8 | 56.2 | 48.3
394 | 158 | 566.2 | 226.48 | 264.7421 | 225 | 213.8 | 193.8 | 67.4 | 411.7 | 16.2 | 20.9 | 43.4 | 3.6 | 218.1 | 5.2 | 728.2 | 856.4 | 161.5 | 195.5 | 245.3 | 813.6 | 355.3 | 447 | 790 | 180.6 | 171.9 | 689 | 13.6 | 29.2 | 59.4 | 76.7 | 369.4 | 449.4 | 60.1 | 303 | 23.3 | 223.8 | 199.9 | 22.1 | 80.9 | 56.7 | 48.6
395 | 159 | 566.7 | 226.68 | 264.9759 | 225.1 | 214.6 | 194.7 | 67.6 | 413 | 16.4 | 20.9 | 43.6 | 3.5 | 236.6 | 4.7 | 729.8 | 856.2 | 161.3 | 196.8 | 245.8 | 815.1 | 356.7 | 447.1 | 785.8 | 181.7 | 173.1 | 688.8 | 13.6 | 29.4 | 59.9 | 77.3 | 370.8 | 451.1 | 60.7 | 304.7 | 23.4 | 223.5 | 200.3 | 22.3 | 81.2 | 57 | 48.9
396 | 160 | 566.6 | 226.64 | 264.9291 | 225.6 | 215.4 | 194.6 | 67.7 | 414.6 | 16.5 | 20.8 | 43.7 | 3.8 | 255.8 | 4.6 | 730.3 | 861.4 | 161.2 | 198.2 | 246.3 | 816.2 | 358.1 | 446.5 | 784.4 | 182.8 | 174.3 | 688 | 13.7 | 29.6 | 60.2 | 77.8 | 372.2 | 456.1 | 61.2 | 306 | 23.6 | 223.1 | 201 | 22.5 | 81.7 | 57.5 | 49.2
397 | 161 | 564.7 | 225.88 | 264.0407 | 225.5 | 215.6 | 195.9 | 67.8 | 418.4 | 16.5 | 20.8 | 43.8 | 3.9 | 237.8 | 4.5 | 732 | 860.4 | 160.4 | 199.6 | 246.9 | 816.7 | 359.4 | 447.4 | 784.8 | 183.8 | 175.4 | 688.9 | 13.7 | 29.9 | 60.6 | 78.4 | 374.6 | 462.7 | 61.7 | 309.3 | 23.7 | 223 | 201.8 | 22.6 | 82.1 | 57.9 | 49.5
398 | 162 | 564.6 | 225.84 | 263.9939 | 225.2 | 216.4 | 196.8 | 68 | 420.3 | 16.6 | 20.8 | 43.9 | 3.5 | 222.6 | 5 | 735.5 | 859.9 | 160.4 | 201.1 | 247.4 | 817.5 | 360.6 | 449.5 | 791.3 | 184.8 | 176.5 | 690.2 | 13.7 | 30.1 | 61 | 79 | 378.8 | 471.8 | 62.5 | 313.7 | 23.9 | 222.6 | 202.1 | 22.8 | 82.5 | 58.3 | 49.8
399 | 163 | 565.7 | 226.28 | 264.5083 | 225.1 | 216.7 | 196.7 | 68.2 | 423.9 | 16.6 | 20.8 | 44 | 3.4 | 230.8 | 4.9 | 735.6 | 861 | 161.7 | 202.7 | 247.9 | 817.2 | 361.8 | 451.8 | 790.3 | 185.9 | 177.5 | 691.7 | 13.7 | 30.3 | 61.4 | 79.6 | 383.3 | 485.5 | 63.2 | 319 | 24.1 | 222.5 | 203.3 | 23 | 82.9 | 58.7 | 50.1
400 | 164 | 566.6 | 226.64 | 264.9291 | 225.4 | 216.9 | 197.3 | 68.3 | 430.8 | 16.7 | 20.8 | 44.2 | 3.8 | 215.5 | 4.2 | 738.7 | 857.8 | 162.6 | 204.3 | 248.4 | 817.6 | 362.9 | 451.9 | 788.2 | 186.9 | 178.6 | 692.6 | 13.8 | 30.5 | 61.8 | 80.2 | 387.1 | 492.6 | 63.7 | 325.3 | 24.2 | 222 | 204.3 | 23.2 | 83.3 | 59.1 | 50.4
401 | 165 | 567.2 | 226.88 | 265.2096 | 225.7 | 217.8 | 197.7 | 68.4 | 427.8 | 16.7 | 20.8 | 44.4 | 3.8 | 216.7 | 4 | 741.8 | 849.7 | 162.3 | 206 | 249 | 818.9 | 364 | 449.5 | 786.9 | 187.9 | 179.6 | 694.5 | 13.8 | 30.8 | 62 | 80.7 | 387.2 | 486 | 63.7 | 322.9 | 24.4 | 223.7 | 204.3 | 23.3 | 83.6 | 59.6 | 50.6
402 | 166 | 566.6 | 226.64 | 264.9291 | 227.2 | 219.1 | 196.9 | 68.6 | 420.8 | 16.9 | 20.8 | 44.5 | 3.6 | 232.4 | 4 | 742.2 | 858.3 | 162.4 | 207.6 | 249.5 | 819.2 | 365.1 | 447.6 | 786.4 | 188.9 | 180.6 | 694.6 | 13.8 | 31 | 62.1 | 81.3 | 385 | 479.8 | 63.6 | 320.9 | 24.6 | 223.9 | 204.8 | 23.5 | 84 | 60.1 | 51
403 | 167 | 566.5 | 226.6 | 264.8823 | 229.2 | 219.1 | 196.1 | 68.7 | 417.6 | 17 | 20.8 | 44.8 | 3.9 | 244.9 | 4.5 | 743.9 | 853 | 162.9 | 209.4 | 250 | 819.7 | 366.2 | 447.4 | 786.1 | 190 | 181.7 | 696.3 | 13.9 | 31.2 | 62.5 | 81.9 | 385.3 | 480.3 | 63.9 | 321.8 | 24.7 | 223.9 | 204.8 | 23.7 | 84.6 | 60.6 | 51.3
404 | 168 | 566.1 | 226.44 | 264.6953 | 230.3 | 220 | 195.3 | 68.9 | 415.2 | 17.1 | 20.8 | 44.9 | 4.1 | 240.1 | 4.8 | 744.2 | 852.1 | 163.3 | 211.1 | 250.8 | 820.6 | 367.3 | 447.7 | 786.1 | 191 | 182.7 | 697.4 | 13.9 | 31.5 | 62.8 | 82.5 | 386.3 | 477.3 | 64.3 | 322.4 | 24.9 | 223.8 | 205.3 | 23.9 | 85 | 61 | 51.6
405 | 169 | 566.2 | 226.48 | 264.7421 | 230.8 | 221.3 | 194.1 | 69.1 | 413.8 | 17.1 | 20.8 | 45 | 4.2 | 239.6 | 5.1 | 745.7 | 844.2 | 162.9 | 213.2 | 251.5 | 821.2 | 368.6 | 448.5 | 785.2 | 192 | 183.7 | 698 | 13.9 | 31.7 | 63.3 | 83.1 | 386.9 | 471.3 | 64.8 | 322.4 | 25 | 224.1 | 206.3 | 24.1 | 85.5 | 61.5 | 51.9
406 | 170 | 565.8 | 226.32 | 264.555 | 234.1 | 222.3 | 193.4 | 69.4 | 412.3 | 17.2 | 20.8 | 45.1 | 3.9 | 224 | 5 | 749.2 | 842.4 | 162.5 | 215.3 | 252.3 | 822.5 | 369.9 | 448.1 | 785.1 | 193.1 | 184.7 | 698.7 | 13.9 | 31.9 | 63.6 | 83.7 | 386.2 | 468.8 | 64.8 | 322 | 25.2 | 224.4 | 206.8 | 24.3 | 85.9 | 61.9 | 52.2
407 | 171 | 566 | 226.4 | 264.6486 | 235.6 | 222.8 | 192.6 | 69.8 | 410.5 | 17.3 | 20.8 | 45.2 | 4.1 | 214.2 | 5.1 | 751.2 | 846.4 | 162.8 | 217.3 | 253.1 | 823.3 | 371.2 | 447.9 | 783.1 | 194.1 | 185.7 | 698.1 | 14 | 32.1 | 64.1 | 84.3 | 384.8 | 469 | 65.1 | 321.1 | 25.4 | 224.5 | 206.7 | 24.5 | 86.2 | 62.4 | 52.5
408 | 172 | 566.3 | 226.52 | 264.7888 | 235.8 | 222.7 | 192 | 70.1 | 412.7 | 17.4 | 20.8 | 45.5 | 4.1 | 194.8 | 5 | 750.4 | 856.8 | 163.7 | 219.3 | 253.9 | 822.8 | 372.5 | 448.5 | 783.9 | 195.1 | 186.6 | 699.2 | 14 | 32.4 | 64.5 | 84.9 | 386.6 | 473.6 | 65.8 | 324.7 | 25.5 | 225.1 | 206.6 | 24.7 | 86.5 | 62.8 | 52.9
409 | 173 | 566.1 | 226.44 | 264.6953 | 235.1 | 223.2 | 192.2 | 70.4 | 417.1 | 17.4 | 20.8 | 45.7 | 3.7 | 194.5 | 4.3 | 748.8 | 856.6 | 165.4 | 221.4 | 254.8 | 821.7 | 373.6 | 447.8 | 785.5 | 196.1 | 187.5 | 700.3 | 14 | 32.6 | 65 | 85.6 | 388.2 | 478.9 | 66.3 | 329.3 | 25.7 | 225.1 | 207.1 | 24.9 | 86.9 | 63.3 | 53.2
410 | 174 | 565.5 | 226.2 | 264.4148 | 235 | 224 | 191.9 | 70.6 | 419.1 | 17.5 | 20.8 | 45.9 | 3.7 | 224.7 | 3.5 | 749 | 854.5 | 167.9 | 223.5 | 255.8 | 821 | 374.9 | 445.8 | 784.4 | 197.1 | 188.4 | 699.8 | 14.1 | 32.8 | 65.4 | 86.2 | 388.9 | 482.8 | 66.7 | 333.3 | 25.9 | 225.1 | 206.9 | 25 | 87.1 | 63.8 | 53.5
411 | 175 | 565.8 | 226.32 | 264.555 | 234 | 224.9 | 192.7 | 70.7 | 430.2 | 17.4 | 20.8 | 46.1 | 3.6 | 248.9 | 3.3 | 751.2 | 853.3 | 169.4 | 225.8 | 257 | 820.4 | 376.2 | 446.3 | 779.4 | 198 | 189.3 | 697 | 14.1 | 33.1 | 66.3 | 86.9 | 392.7 | 492.2 | 67.2 | 336.5 | 26 | 225.4 | 206.9 | 25.2 | 87.4 | 64.3 | 53.8
412 | 176 | 565 | 226 | 264.181 | 233.1 | 225.6 | 194.4 | 70.8 | 445.2 | 17.4 | 20.8 | 46.3 | 3.9 | 247.9 | 3.4 | 753.1 | 839.1 | 170.4 | 228 | 258.1 | 818.9 | 377.5 | 447.1 | 771.8 | 199 | 190.2 | 695.4 | 14.1 | 33.3 | 67.3 | 87.5 | 397 | 497.6 | 67.9 | 339.2 | 26.2 | 225.5 | 206.7 | 25.4 | 87.5 | 64.9 | 54.1
413 | 177 | 564.5 | 225.8 | 263.9472 | 233.4 | 226.4 | 195.2 | 70.9 | 455.4 | 17.4 | 20.8 | 46.4 | 3.9 | 243.6 | 3.7 | 758.1 | 833.1 | 171.8 | 230.1 | 259.3 | 816 | 378.9 | 446.3 | 768 | 200 | 191.1 | 695.2 | 14.1 | 33.5 | 67.7 | 88.2 | 398.6 | 504.6 | 68.6 | 341.9 | 26.4 | 225.8 | 206.3 | 25.5 | 87.6 | 65.4 | 54.5
414 | 178 | 566.1 | 226.44 | 264.6953 | 233.9 | 227 | 197.7 | 71.1 | 452.3 | 17.4 | 20.8 | 46.5 | 3.8 | 264.3 | 3.9 | 771.9 | 838.9 | 172.7 | 232.2 | 260.4 | 815.5 | 380.3 | 447 | 765.4 | 201 | 192 | 695.2 | 14.2 | 33.7 | 67.8 | 88.8 | 397.4 | 500.3 | 69.2 | 341.3 | 26.5 | 226.2 | 206.2 | 25.7 | 87.8 | 65.9 | 54.8
415 | 179 | 566.7 | 226.68 | 264.9759 | 233.4 | 226.9 | 199.5 | 71.4 | 445.5 | 17.5 | 20.8 | 46.7 | 3.6 | 266.6 | 3.8 | 796.8 | 845.3 | 173.9 | 234.3 | 261.4 | 816.9 | 381.7 | 446.8 | 769.8 | 202.1 | 192.9 | 695.6 | 14.2 | 33.9 | 68.1 | 89.5 | 395.9 | 495.4 | 69.6 | 339.3 | 26.7 | 226.4 | 206.2 | 25.9 | 88 | 66.4 | 55.1
416 | 180 | 566.5 | 226.6 | 264.8823 | 234.3 | 226.7 | 201.1 | 71.6 | 440.5 | 17.6 | 20.8 | 46.7 | 3.3 | 237.6 | 3.9 | 812.3 | 849.3 | 173.6 | 236.6 | 262.3 | 818 | 383 | 447.4 | 770.8 | 203.1 | 193.7 | 696.4 | 14.2 | 34.1 | 68.5 | 90.1 | 396.7 | 497.3 | 70.3 | 340.8 | 26.9 | 226.6 | 206.2 | 26.1 | 88.2 | 66.9 | 55.4
417 | 181 | 564.9 | 225.96 | 264.1342 | 234.8 | 226.7 | 202.2 | 71.8 | 439.2 | 17.7 | 20.7 | 46.8 | 3.5 | 226.6 | 3.7 | 823.3 | 849.7 | 174.2 | 239.2 | 263.3 | 817.7 | 384.5 | 449.2 | 773.5 | 204.1 | 194.6 | 696.2 | 14.3 | 34.3 | 68.9 | 90.8 | 398.3 | 498.2 | 71.3 | 344.4 | 27 | 227.7 | 206.9 | 26.3 | 88.7 | 67.4 | 55.7
418 | 182 | 565.4 | 226.16 | 264.368 | 234.8 | 227.2 | 201.3 | 71.9 | 443 | 17.8 | 20.7 | 47 | 3.7 | 209.4 | 3.6 | 829.3 | 850 | 174.1 | 241.7 | 264.3 | 817.5 | 385.9 | 449.9 | 775.2 | 205.1 | 195.4 | 696.2 | 14.3 | 34.5 | 69.6 | 91.5 | 400.7 | 498.8 | 72 | 346.9 | 27.2 | 228.1 | 207.3 | 26.5 | 89.1 | 67.8 | 56
419 | 183 | 566 | 226.4 | 264.6486 | 233.5 | 228.2 | 201.6 | 72.1 | 445.9 | 18 | 20.7 | 47.2 | 4 | 211.3 | 3.6 | 832.5 | 850.3 | 175.2 | 244.1 | 265.2 | 817.5 | 387.4 | 450.2 | 776.5 | 206.3 | 196.2 | 696.1 | 14.3 | 34.7 | 70 | 92.2 | 403.1 | 505 | 73 | 348.9 | 27.4 | 228.2 | 207.8 | 26.7 | 89.6 | 68.3 | 56.4
420 | 184 | 565.7 | 226.28 | 264.5083 | 232.7 | 229.5 | 201.2 | 72.4 | 450.4 | 18 | 20.7 | 47.3 | 3.9 | 244.4 | 3.6 | 833.7 | 849.8 | 176.5 | 246.4 | 266.3 | 817.7 | 389 | 451.3 | 781.1 | 207.4 | 196.9 | 697.2 | 14.4 | 34.9 | 70.5 | 92.8 | 407.3 | 514.7 | 73.8 | 352.6 | 27.5 | 228.2 | 208.5 | 26.9 | 90 | 68.9 | 56.7
421 | 185 | 565.8 | 226.32 | 264.555 | 232.2 | 230.9 | 200.5 | 72.6 | 455.3 | 18.1 | 20.7 | 47.4 | 3.7 | 258.4 | 3.7 | 838.3 | 854.8 | 177.9 | 248.6 | 267.4 | 817.4 | 390.7 | 453 | 782.9 | 208.6 | 197.7 | 696.8 | 14.4 | 35.2 | 71.1 | 93.5 | 409.7 | 515.9 | 74.7 | 355.4 | 27.7 | 228.5 | 208.7 | 27.1 | 90.3 | 69.4 | 57
422 | 186 | 565.8 | 226.32 | 264.555 | 231.6 | 231.4 | 201.7 | 72.7 | 452.9 | 18.1 | 20.7 | 47.5 | 3.7 | 237.1 | 3.7 | 844 | 854.4 | 178.9 | 250.6 | 268.6 | 818.6 | 392.5 | 452.5 | 782.7 | 209.9 | 198.5 | 696.5 | 14.5 | 35.4 | 71.4 | 94.2 | 409.9 | 518.4 | 75.4 | 355.7 | 27.9 | 228.5 | 208.8 | 27.3 | 90.7 | 70 | 57.3
423 | 187 | 565.9 | 226.36 | 264.6018 | 231 | 232.1 | 202.6 | 72.8 | 450.7 | 18 | 20.7 | 47.5 | 3.7 | 227.1 | 3.6 | 845.9 | 854.6 | 181.1 | 252.6 | 269.9 | 818.8 | 394.4 | 451.9 | 783 | 211.1 | 199.3 | 696.2 | 14.5 | 35.7 | 71.7 | 94.9 | 410.9 | 522.1 | 76.2 | 357.9 | 28 | 228.4 | 208.8 | 27.4 | 91.1 | 70.5 | 57.6
424 | 188 | 565.7 | 226.28 | 264.5083 | 230.9 | 232.6 | 202.4 | 72.9 | 450.3 | 18.1 | 20.7 | 47.5 | 3.6 | 236.8 | 3.7 | 847.4 | 854.5 | 181.8 | 254.6 | 271.2 | 819.4 | 396.5 | 450.9 | 784.7 | 212.3 | 200 | 697.1 | 14.5 | 35.9 | 72.2 | 95.6 | 411.9 | 522.3 | 77.3 | 360.1 | 28.2 | 228.8 | 208.7 | 27.6 | 91.3 | 71.1 | 57.9
425 | 189 | 565.9 | 226.36 | 264.6018 | 231.2 | 232.3 | 202 | 73 | 448.5 | 18.2 | 20.7 | 47.6 | 3.9 | 236.5 | 4.2 | 849.3 | 854.7 | 181.7 | 256.5 | 272.6 | 819.8 | 398.8 | 451 | 782.6 | 213.4 | 200.7 | 698.7 | 14.6 | 36.2 | 72.2 | 96.4 | 411 | 518.6 | 77.7 | 359.9 | 28.4 | 228.8 | 208.4 | 27.8 | 91.5 | 71.6 | 58.2
426 | 190 | 565.8 | 226.32 | 264.555 | 231.1 | 232 | 202 | 73.1 | 451.1 | 18.2 | 20.7 | 47.7 | 3.9 | 240.3 | 4.7 | 852.3 | 852.5 | 183.1 | 258.4 | 274.1 | 820.3 | 401.1 | 453.6 | 783 | 214.7 | 201.3 | 699.1 | 14.6 | 36.5 | 72.9 | 97.1 | 412.2 | 521.4 | 78.7 | 361.3 | 28.6 | 228.9 | 208.1 | 28 | 91.6 | 72.1 | 58.4
427 | 191 | 565.4 | 226.16 | 264.368 | 230.6 | 233 | 202.3 | 73.2 | 452 | 18.3 | 20.7 | 47.8 | 3.9 | 243.6 | 5 | 857.8 | 850.3 | 184.8 | 260.3 | 275.9 | 821.1 | 403.6 | 453.2 | 786.8 | 216.1 | 201.9 | 700.1 | 14.6 | 36.7 | 73.3 | 97.8 | 414.2 | 521.7 | 79.6 | 364.4 | 28.7 | 229.6 | 208.2 | 28.2 | 91.8 | 72.6 | 58.7
428 | 192 | 565.8 | 226.32 | 264.555 | 230.5 | 233.8 | 202.5 | 73.4 | 449.7 | 18.4 | 20.7 | 48.1 | 3.9 | 235 | 4.9 | 857.3 | 859.2 | 185.5 | 262.1 | 278.2 | 821.2 | 406.5 | 452.6 | 783.7 | 217.5 | 202.5 | 698 | 14.7 | 37 | 73.9 | 98.6 | 413.6 | 522 | 80.6 | 365.5 | 28.9 | 230.3 | 208.2 | 28.3 | 92.3 | 73.2 | 59.1
429 | 193 | 565.5 | 226.2 | 264.4148 | 230.8 | 235.4 | 202.1 | 73.5 | 448.7 | 18.6 | 20.7 | 48.3 | 3.7 | 231.1 | 5 | 862.6 | 863.7 | 185.7 | 263.9 | 281.6 | 822.1 | 409.6 | 451.5 | 786.1 | 218.8 | 203.1 | 698.5 | 14.7 | 37.3 | 74.2 | 99.3 | 412.7 | 520.9 | 81.2 | 366.7 | 29.1 | 230.5 | 208.4 | 28.5 | 92.5 | 73.7 | 59.4
430 | 194 | 565.6 | 226.24 | 264.4615 | 230.9 | 237.1 | 202.9 | 73.7 | 440.4 | 18.7 | 20.7 | 48.4 | 3.1 | 234.2 | 5.1 | 867.4 | 864.7 | 185.7 | 265.6 | 285.4 | 823.6 | 412.3 | 450.9 | 788.5 | 220.1 | 203.4 | 699.3 | 14.7 | 37.5 | 74.2 | 100.1 | 411 | 512.7 | 81.6 | 365.4 | 29.2 | 230.8 | 209.1 | 28.7 | 92.9 | 74.2 | 59.7
431 | 195 | 565.7 | 226.28 | 264.5083 | 231.8 | 239 | 202.7 | 74 | 435.6 | 18.8 | 20.7 | 48.5 | 3.2 | 234.8 | 4.8 | 863.6 | 864.7 | 186.3 | 267.3 | 287.7 | 824.6 | 414.5 | 452.7 | 790.4 | 221.4 | 203.2 | 700.1 | 14.8 | 37.8 | 74.5 | 100.9 | 410.5 | 511.6 | 82.4 | 367.7 | 29.4 | 230.8 | 209.6 | 28.9 | 93.2 | 74.7 | 60
432 | 196 | 564.9 | 225.96 | 264.1342 | 232.4 | 240.1 | 201.7 | 74.2 | 434.4 | 18.8 | 20.7 | 48.7 | 3.5 | 233.4 | 4.3 | 869 | 860 | 185.4 | 269.4 | 290.8 | 826.2 | 416 | 454.7 | 791.7 | 222.7 | 203.1 | 701 | 14.8 | 38.1 | 74.8 | 101.7 | 411.7 | 514.3 | 83.1 | 371.1 | 29.6 | 230.9 | 209.7 | 29.1 | 93.6 | 75.3 | 60.3
433 | 197 | 566.7 | 226.68 | 264.9759 | 232.3 | 240.1 | 200.6 | 74.5 | 434.6 | 18.8 | 20.7 | 48.9 | 3.7 | 217.6 | 4.1 | 877.8 | 856.3 | 185.7 | 272.1 | 294.2 | 827.8 | 415.6 | 457.9 | 793 | 223.9 | 203.4 | 701.8 | 14.9 | 38.3 | 75.2 | 102.6 | 414.3 | 517.2 | 83.8 | 373.7 | 29.8 | 231.2 | 210.1 | 29.2 | 93.9 | 75.8 | 60.7
434 | 198 | 566.9 | 226.76 | 265.0694 | 232.9 | 240.4 | 200 | 74.7 | 437.3 | 18.8 | 20.7 | 49.1 | 3.7 | 218.5 | 4.1 | 883.5 | 851.2 | 185.6 | 275.2 | 297.3 | 828.9 | 414.4 | 460.1 | 793.3 | 225.2 | 203.7 | 703.2 | 14.9 | 38.6 | 75.4 | 103.4 | 415 | 514.2 | 84.9 | 374.5 | 29.9 | 232.1 | 210.1 | 29.4 | 94.2 | 76.3 | 61
435 | 199 | 568.3 | 227.32 | 265.724 | 233.7 | 240.5 | 200.8 | 74.9 | 436.8 | 18.9 | 20.7 | 49.3 | 4 | 217.1 | 4.4 | 882.3 | 851.2 | 186.3 | 278.9 | 299.9 | 830.3 | 413.7 | 461.9 | 795.8 | 226.4 | 204.1 | 705.1 | 14.9 | 38.8 | 75.8 | 104.3 | 414.5 | 510.4 | 85.4 | 372.8 | 30.1 | 232.9 | 210.5 | 29.6 | 94.5 | 76.9 | 61.3
436 | 200 | 567.1 | 226.84 | 265.1629 | 234.5 | 240.9 | 201.7 | 75.1 | 435.6 | 18.9 | 20.7 | 49.5 | 4 | 202.3 | 4.4 | 886.3 | 852.4 | 186.3 | 283.3 | 301 | 831.1 | 413.5 | 463.9 | 801 | 227.8 | 204.5 | 707.4 | 15 | 39.1 | 76.1 | 105.1 | 414.2 | 507.5 | 85.9 | 372.8 | 30.3 | 233.1 | 210.7 | 29.8 | 95 | 77.4 | 61.7
437 | 201 | 565.2 | 226.08 | 264.2745 | 235.7 | 240.8 | 201.2 | 75.2 | 432.2 | 19.1 | 20.6 | 49.6 | 3.6 | 208.4 | 4.5 | 887.6 | 841.7 | 186.1 | 287.9 | 302.6 | 831.9 | 413.5 | 464.3 | 798.9 | 229 | 204.9 | 708.8 | 15 | 39.4 | 76.2 | 106 | 413.8 | 503.8 | 86.6 | 373.8 | 30.5 | 233.9 | 210.9 | 29.9 | 95.3 | 78 | 62
438 | 202 | 566.1 | 226.44 | 264.6953 | 237 | 241.7 | 201.1 | 75.4 | 427.9 | 19.2 | 20.7 | 49.8 | 3.6 | 201.1 | 5 | 886.5 | 835.4 | 185.7 | 292.8 | 303.8 | 832 | 413.8 | 464.3 | 798.6 | 230.2 | 205.3 | 710.4 | 15 | 39.6 | 76.5 | 106.8 | 413.3 | 499.7 | 87.9 | 374.1 | 30.6 | 234.2 | 211.2 | 30.1 | 95.7 | 78.5 | 62.3
439 | 203 | 567.1 | 226.84 | 265.1629 | 239.4 | 241.8 | 199.4 | 75.6 | 426.5 | 19.4 | 20.6 | 49.9 | 3.1 | 214.7 | 4.7 | 883 | 848.6 | 185.9 | 297.9 | 305 | 832.2 | 414 | 465 | 798.3 | 231.4 | 205.8 | 712.8 | 15.1 | 39.9 | 77 | 107.7 | 412.8 | 498.9 | 88.3 | 374.2 | 30.8 | 234.9 | 211.6 | 30.3 | 96 | 79.1 | 62.6
440 | 204 | 566.9 | 226.76 | 265.0694 | 241.6 | 241.5 | 197.9 | 75.8 | 424 | 19.5 | 20.6 | 50 | 3.4 | 232 | 4.3 | 880.9 | 842.4 | 185.6 | 303.3 | 306.7 | 832.7 | 414.3 | 466.2 | 798.3 | 232.4 | 206.3 | 714.3 | 15.1 | 40.1 | 77.5 | 108.6 | 412.2 | 496.7 | 88.8 | 375 | 31 | 234.8 | 212.5 | 30.5 | 96.5 | 79.6 | 63
441 | 205 | 565.5 | 226.2 | 264.4148 | 243.5 | 242.3 | 199.1 | 76.2 | 421.8 | 19.5 | 20.6 | 50.1 | 3.6 | 216.5 | 4.5 | 878.2 | 841.3 | 185 | 308.9 | 308 | 833.1 | 414.6 | 466.6 | 795.4 | 233.4 | 206.9 | 715.7 | 15.2 | 40.4 | 77.8 | 109.4 | 412.4 | 494.4 | 89.4 | 376.5 | 31.2 | 234.5 | 212.4 | 30.6 | 97 | 80.1 | 63.3
442 | 206 | 565.7 | 226.28 | 264.5083 | 244.2 | 242.7 | 199.6 | 76.6 | 419.5 | 19.5 | 20.6 | 50.2 | 4.1 | 220.4 | 4.1 | 885.8 | 841.7 | 184.5 | 314.6 | 310.4 | 833 | 414.6 | 466.3 | 795.8 | 234.4 | 207.4 | 716.2 | 15.2 | 40.7 | 77.8 | 110.3 | 411.1 | 488.3 | 89.9 | 377.8 | 31.3 | 234.9 | 213.2 | 30.8 | 97.3 | 80.6 | 63.6
443 | 207 | 566.5 | 226.6 | 264.8823 | 245.9 | 242.9 | 200 | 77 | 418.9 | 19.5 | 20.6 | 50.4 | 4.2 | 234.4 | 3.9 | 885.5 | 846.6 | 183.6 | 320.4 | 311.3 | 834.2 | 414.7 | 467.5 | 793.6 | 235.4 | 208 | 716.3 | 15.2 | 40.9 | 78.4 | 111.2 | 412.7 | 494.6 | 90.3 | 378.2 | 31.5 | 235.2 | 213.7 | 31 | 97.5 | 81.1 | 64
444 | 208 | 566.9 | 226.76 | 265.0694 | 247.9 | 243.5 | 200.5 | 77.4 | 423.1 | 19.7 | 20.6 | 50.6 | 3.6 | 222 | 3.8 | 884.5 | 849.3 | 184.1 | 326.4 | 312.9 | 834.3 | 415 | 468.3 | 795.2 | 236.4 | 208.6 | 717 | 15.3 | 41.1 | 78.8 | 112.1 | 413 | 491.2 | 91 | 377.9 | 31.7 | 235.6 | 214.5 | 31.2 | 97.8 | 81.6 | 64.3
445 | 209 | 567.3 | 226.92 | 265.2564 | 249.3 | 244.9 | 201.8 | 77.7 | 420.4 | 19.7 | 20.6 | 50.8 | 3.9 | 234.4 | 3.8 | 880.9 | 853.4 | 185 | 332.5 | 314.7 | 833.8 | 415.1 | 468.7 | 795.9 | 237.3 | 209.2 | 717.6 | 15.3 | 41.4 | 79.1 | 113 | 412.5 | 491.5 | 91.5 | 378.2 | 31.8 | 235.6 | 215.5 | 31.4 | 98.4 | 82.1 | 64.7
446 | 210 | 566.2 | 226.48 | 264.7421 | 250.1 | 245.9 | 203.1 | 78 | 417.8 | 19.8 | 20.6 | 51.1 | 3.6 | 238.9 | 4 | 870.4 | 853.8 | 184.4 | 338.3 | 316.6 | 833.7 | 415.5 | 470.2 | 795.3 | 238.2 | 209.8 | 717.8 | 15.4 | 41.6 | 79.4 | 113.8 | 414.2 | 493.6 | 92.1 | 381.5 | 32 | 235.4 | 216.7 | 31.6 | 98.8 | 82.6 | 65.1
447 | 211 | 567.2 | 226.88 | 265.2096 | 250 | 246.3 | 203.1 | 78.2 | 419.4 | 19.9 | 20.6 | 51.4 | 3.6 | 190.6 | 4.7 | 869.9 | 855.3 | 185.2 | 344 | 319.2 | 833.7 | 417 | 473 | 800.5 | 239 | 210.4 | 719.9 | 15.4 | 41.9 | 79.9 | 114.7 | 416.9 | 498.9 | 92.9 | 388.2 | 32.2 | 236.2 | 217.5 | 31.7 | 99.4 | 83.1 | 65.4
448 | 212 | 568.1 | 227.24 | 265.6305 | 250 | 246.4 | 202.9 | 78.3 | 421.7 | 20 | 20.6 | 51.7 | 3.8 | 201.3 | 4.9 | 874.1 | 858 | 184.8 | 349.8 | 321.9 | 834.4 | 419.4 | 474.8 | 800.2 | 239.9 | 211.1 | 720.8 | 15.5 | 42.2 | 80.1 | 115.6 | 418.1 | 498.3 | 93.6 | 390.5 | 32.4 | 237.5 | 218.9 | 31.9 | 99.8 | 83.7 | 65.8
449 | 213 | 568.7 | 227.48 | 265.911 | 249.7 | 246.3 | 202.5 | 78.5 | 421.9 | 19.9 | 20.6 | 51.9 | 3.6 | 211.3 | 5.4 | 884 | 856 | 184.6 | 355.9 | 324.6 | 835.1 | 422.2 | 476.1 | 801.6 | 240.7 | 211.8 | 721.4 | 15.5 | 42.5 | 80.3 | 116.4 | 419.6 | 499.7 | 94.5 | 391.3 | 32.5 | 238.2 | 220.2 | 32.1 | 100.5 | 84.2 | 66.2
450 | 214 | 565.9 | 226.36 | 264.6018 | 249.5 | 246.5 | 201.7 | 78.8 | 419 | 19.9 | 20.6 | 51.9 | 3.9 | 209 | 5.7 | 887.9 | 852.9 | 184.1 | 361.5 | 327.4 | 835.7 | 426.2 | 477.6 | 799.1 | 241.5 | 212.5 | 722.6 | 15.6 | 42.7 | 80.6 | 117.3 | 419.3 | 497.5 | 95.4 | 392.2 | 32.7 | 239 | 221.6 | 32.3 | 101 | 84.8 | 66.5
451 | 215 | 565.5 | 226.2 | 264.4148 | 249.2 | 246.5 | 201.6 | 79.1 | 415.3 | 19.9 | 20.6 | 52 | 3.8 | 227.9 | 5.6 | 880.8 | 853.1 | 183.9 | 367.1 | 328.7 | 835.7 | 430.6 | 477.6 | 801.6 | 242.2 | 213.2 | 725 | 15.6 | 43 | 80.9 | 118.1 | 418.4 | 495.3 | 96.3 | 391.4 | 32.9 | 239.9 | 222.4 | 32.5 | 101.5 | 85.4 | 66.9
452 | 216 | 563.7 | 225.48 | 263.5731 | 250 | 246 | 200.8 | 79.5 | 413.2 | 19.9 | 20.6 | 52.2 | 3.9 | 221.7 | 5.3 | 876.1 | 851.8 | 183.4 | 372.4 | 331.4 | 835.6 | 435.1 | 478.2 | 801 | 243.1 | 213.9 | 726.3 | 15.7 | 43.3 | 81 | 119 | 417.3 | 489.6 | 97 | 391.2 | 33.1 | 239.2 | 222.8 | 32.7 | 101.8 | 85.9 | 67.3
453 | 217 | 565.2 | 226.08 | 264.2745 | 252.3 | 246.2 | 201.8 | 79.8 | 411.6 | 20.1 | 20.6 | 52.4 | 3.9 | 221.9 | 5.7 | 883.7 | 848.1 | 183.7 | 377.7 | 333.9 | 835.8 | 440.5 | 478.7 | 799 | 243.9 | 214.6 | 726.2 | 15.7 | 43.5 | 81.3 | 119.8 | 416.5 | 487 | 97.6 | 391.3 | 33.2 | 239.2 | 222.8 | 32.9 | 102.2 | 86.4 | 67.6
454 | 218 | 565.5 | 226.2 | 264.4148 | 255.2 | 245.9 | 202.3 | 80.1 | 414.6 | 20.2 | 20.6 | 52.6 | 3.9 | 214.8 | 6.1 | 890.4 | 847.8 | 183.1 | 382.6 | 335.1 | 836.2 | 446.5 | 478.5 | 795.9 | 244.6 | 215.3 | 725.5 | 15.7 | 43.8 | 81.7 | 120.7 | 416.8 | 484.2 | 98.1 | 389.9 | 33.4 | 239.1 | 222.5 | 33 | 102.5 | 86.9 | 67.9
455 | 219 | 566 | 226.4 | 264.6486 | 257.5 | 244.5 | 204.4 | 80.6 | 417.7 | 20.4 | 20.6 | 52.6 | 3.8 | 217.7 | 6.6 | 885.8 | 851.6 | 182.8 | 387.3 | 336.9 | 836.6 | 453 | 478.3 | 800 | 245.4 | 216.1 | 726.1 | 15.8 | 44.1 | 82.3 | 121.5 | 416.9 | 486.4 | 98.4 | 389.4 | 33.6 | 238.9 | 222.7 | 33.2 | 102.8 | 87.4 | 68.2
456 | 220 | 565.3 | 226.12 | 264.3213 | 259.8 | 244 | 206.7 | 81 | 422 | 20.5 | 20.6 | 52.7 | 3.9 | 203.6 | 7 | 884.6 | 855.3 | 182.5 | 391.9 | 338.9 | 837 | 459.4 | 480.8 | 803.7 | 246.1 | 216.9 | 727 | 15.8 | 44.3 | 82.7 | 122.4 | 418.8 | 493.2 | 99.4 | 392.7 | 33.8 | 239.2 | 224.1 | 33.4 | 103.1 | 87.9 | 68.6
457 | 221 | 566.2 | 226.48 | 264.7421 | 260.6 | 243.9 | 207.5 | 81.4 | 427.3 | 20.7 | 20.6 | 52.9 | 3.9 | 208.4 | 7.6 | 881.7 | 855 | 182.6 | 396.3 | 340.8 | 836.5 | 465.2 | 482.9 | 812.1 | 246.9 | 217.7 | 729.7 | 15.9 | 44.6 | 83.1 | 123.3 | 421.4 | 498.8 | 100.1 | 394.4 | 33.9 | 240.2 | 225.6 | 33.6 | 103.4 | 88.4 | 68.9
458 | 222 | 565 | 226 | 264.181 | 260.5 | 243.8 | 208.9 | 81.7 | 429 | 20.8 | 20.6 | 53 | 3.9 | 197 | 8 | 886.9 | 860.8 | 182.2 | 400.5 | 342.8 | 836.5 | 470.8 | 483.7 | 814.7 | 247.6 | 218.7 | 731.2 | 15.9 | 44.9 | 83.3 | 124.1 | 422.3 | 497 | 100.7 | 394.9 | 34.1 | 240.3 | 226.7 | 33.7 | 104 | 88.9 | 69.2
459 | 223 | 565.4 | 226.16 | 264.368 | 261 | 244.9 | 207.9 | 82.1 | 427.1 | 20.9 | 20.6 | 53.2 | 3.8 | 201.7 | 7.5 | 891.6 | 860.5 | 181.7 | 404.5 | 344.5 | 836.6 | 476.1 | 483.3 | 814.6 | 248.3 | 219.6 | 732.1 | 16 | 45.2 | 83.6 | 125 | 422.5 | 492.8 | 100.9 | 394.9 | 34.3 | 240.7 | 227.7 | 33.9 | 104.4 | 89.4 | 69.6
460 | 224 | 565.4 | 226.16 | 264.368 | 262.8 | 245.4 | 207.2 | 82.5 | 425.8 | 21 | 20.5 | 53.3 | 4 | 201.8 | 6.6 | 889 | 864.4 | 182.2 | 407.8 | 346.8 | 836.6 | 481.8 | 483.6 | 810.2 | 249 | 220.6 | 731.6 | 16 | 45.4 | 84.1 | 125.8 | 423.2 | 490.4 | 101.4 | 395.5 | 34.5 | 241.2 | 228.3 | 34.1 | 104.7 | 90 | 70
461 | 225 | 564.9 | 225.96 | 264.1342 | 263.4 | 245.7 | 207.4 | 82.8 | 424.6 | 21.2 | 20.5 | 53.4 | 3.9 | 201.7 | 6.1 | 893.5 | 866.8 | 183 | 410.2 | 348.8 | 836.7 | 487.3 | 482.8 | 805.8 | 249.7 | 221.4 | 731.3 | 16.1 | 45.7 | 84.5 | 126.7 | 422.6 | 488.4 | 102.1 | 395.9 | 34.7 | 242.3 | 228.9 | 34.3 | 105.1 | 90.5 | 70.3
462 | 226 | 565.8 | 226.32 | 264.555 | 262.5 | 246.3 | 208.8 | 83.3 | 422.6 | 21.2 | 20.5 | 53.5 | 3.9 | 209.7 | 6.5 | 893.7 | 858 | 183 | 412.8 | 351.1 | 836.5 | 491.9 | 481.9 | 803.1 | 250.3 | 223.9 | 732 | 16.1 | 45.9 | 84.7 | 127.6 | 421.2 | 484.1 | 102.6 | 395.9 | 34.8 | 243.9 | 229.2 | 34.5 | 105.6 | 91 | 70.7
463 | 227 | 564.6 | 225.84 | 263.9939 | 262.1 | 246.3 | 208.8 | 83.8 | 421.6 | 21.3 | 20.5 | 53.7 | 4 | 208.8 | 7 | 893.8 | 853.5 | 182 | 415.4 | 352.4 | 837.6 | 496.9 | 481 | 802.2 | 251 | 227.7 | 733.7 | 16.2 | 46.2 | 84.9 | 128.4 | 420.7 | 480.2 | 103.1 | 394.9 | 35 | 244.2 | 229.3 | 34.7 | 105.9 | 91.6 | 71.1
464 | 228 | 564.8 | 225.92 | 264.0875 | 263.6 | 246.5 | 209.3 | 84.1 | 420.5 | 21.3 | 20.5 | 53.9 | 4.2 | 204.9 | 7 | 893.1 | 855.3 | 181.6 | 418 | 354.2 | 838.2 | 500.9 | 479.8 | 802 | 251.6 | 230.6 | 733.9 | 16.2 | 46.4 | 85.2 | 129.3 | 419.2 | 478.2 | 103.5 | 393.6 | 35.2 | 245.1 | 229.2 | 34.9 | 106.2 | 92.1 | 71.4
465 | 229 | 565 | 226 | 264.181 | 265.1 | 246.1 | 210.1 | 84.4 | 420.6 | 21.5 | 20.5 | 54 | 4.5 | 207.6 | 6.5 | 885.5 | 852 | 182.1 | 420.8 | 356.3 | 838.1 | 504.4 | 481.7 | 808.4 | 252.3 | 233.1 | 735.8 | 16.2 | 46.7 | 85.7 | 130.2 | 419.2 | 483.2 | 104 | 394.8 | 35.4 | 245.4 | 229 | 35.1 | 106.4 | 92.6 | 71.8
466 | 230 | 564.7 | 225.88 | 264.0407 | 267.3 | 246.1 | 211.7 | 84.6 | 426 | 21.7 | 20.5 | 54.2 | 4 | 210.8 | 6.1 | 888.5 | 853.4 | 182.9 | 424 | 358.2 | 838.2 | 507.8 | 483.3 | 813.1 | 252.9 | 234.7 | 737.3 | 16.3 | 46.9 | 86.2 | 131 | 420.9 | 487.6 | 104.6 | 396.9 | 35.5 | 245.9 | 228.8 | 35.2 | 106.8 | 93.1 | 72.1
467 | 231 | 564.9 | 225.96 | 264.1342 | 268.2 | 246.1 | 212.1 | 84.7 | 426.3 | 21.8 | 20.5 | 54.4 | 4.1 | 209 | 5.9 | 891 | 859.4 | 182.1 | 427.2 | 359.9 | 838.3 | 511 | 482.2 | 810.1 | 253.4 | 236.3 | 737.4 | 16.3 | 47.2 | 86.2 | 131.9 | 419.4 | 482 | 105 | 395.6 | 35.7 | 246.4 | 228.4 | 35.4 | 106.8 | 93.6 | 72.5
468 | 232 | 565.9 | 226.36 | 264.6018 | 268.9 | 245.7 | 212.4 | 84.8 | 422 | 21.9 | 20.5 | 54.5 | 4.1 | 203.5 | 5.2 | 889.3 | 852.5 | 182.7 | 430.4 | 361.5 | 838.8 | 514.5 | 482.1 | 808.6 | 254 | 237.9 | 736.8 | 16.4 | 47.4 | 86.5 | 132.7 | 417.5 | 483.1 | 105.3 | 394.6 | 35.9 | 246.7 | 228.2 | 35.6 | 107.2 | 94.1 | 72.8
469 | 233 | 565.5 | 226.2 | 264.4148 | 269.1 | 246.2 | 212.1 | 84.9 | 421.7 | 22 | 20.5 | 54.6 | 4.1 | 222.6 | 4.3 | 886.6 | 847.9 | 182.6 | 433.5 | 362.9 | 839.4 | 517.9 | 482.7 | 804.8 | 254.6 | 239.4 | 737 | 16.4 | 47.7 | 87.1 | 133.5 | 417.6 | 486.8 | 105.8 | 395.6 | 36.1 | 247 | 228.4 | 35.8 | 107.6 | 94.6 | 73.2
470 | 234 | 564.7 | 225.88 | 264.0407 | 270.4 | 246.5 | 211.4 | 85.1 | 421.6 | 22.1 | 20.5 | 54.6 | 4.1 | 251.5 | 3.7 | 889.4 | 842.8 | 181.7 | 436.6 | 364.6 | 839.3 | 520.9 | 482.1 | 798.2 | 255.2 | 240.8 | 738.4 | 16.5 | 47.9 | 87.3 | 134.3 | 417.3 | 482.2 | 106.5 | 396 | 36.3 | 247.6 | 229.4 | 36 | 107.9 | 95.1 | 73.5
471 | 235 | 566.8 | 226.72 | 265.0226 | 270.3 | 246.8 | 211 | 85.3 | 419.5 | 22.2 | 20.5 | 54.7 | 4.3 | 246.1 | 4 | 886.9 | 845.2 | 180.8 | 439.5 | 366.3 | 839.7 | 524 | 481.5 | 795.2 | 255.7 | 242.2 | 740 | 16.5 | 48.2 | 87.6 | 135.2 | 414.7 | 474.7 | 107 | 395.4 | 36.5 | 247.7 | 229.5 | 36.2 | 108.4 | 95.6 | 73.9
472 | 236 | 566.1 | 226.44 | 264.6953 | 270.7 | 246.5 | 211.1 | 85.5 | 417.5 | 22.3 | 20.5 | 54.9 | 3.9 | 226.5 | 4.6 | 890.8 | 837.3 | 180 | 442.6 | 368.2 | 839.6 | 527 | 481.6 | 792.4 | 256.3 | 243.4 | 739 | 16.6 | 48.4 | 88 | 136 | 413.4 | 471.4 | 107.7 | 396.4 | 36.6 | 249.7 | 230.5 | 36.5 | 109 | 96.1 | 74.2
473 | 237 | 566 | 226.4 | 264.6486 | 271.4 | 246 | 211.9 | 85.8 | 416.1 | 22.4 | 20.5 | 55 | 3.9 | 222.1 | 4.8 | 889.6 | 836.9 | 179.5 | 445.5 | 370.6 | 839.6 | 530.2 | 480.9 | 786.6 | 256.8 | 244.6 | 739 | 16.6 | 48.7 | 88.3 | 136.8 | 412.5 | 467.5 | 108.2 | 396.5 | 36.8 | 252.3 | 231.2 | 36.7 | 109.3 | 96.6 | 74.6
474 | 238 | 565.3 | 226.12 | 264.3213 | 271.5 | 245.6 | 212.2 | 86.2 | 415.9 | 22.5 | 20.5 | 55.1 | 3.8 | 247 | 4.7 | 885.3 | 841.6 | 179.5 | 448.3 | 372.3 | 839.4 | 533.9 | 481.2 | 791.7 | 257.3 | 245.7 | 741.1 | 16.7 | 49 | 88.5 | 137.6 | 411.8 | 466 | 108.9 | 396.4 | 37 | 252.2 | 231.4 | 36.9 | 109.6 | 97.1 | 75
475 | 239 | 567.7 | 227.08 | 265.4434 | 271.3 | 245.6 | 212.4 | 86.6 | 416.5 | 22.5 | 20.5 | 55.2 | 3.9 | 234.4 | 4.7 | 879.4 | 833.1 | 178.9 | 451.2 | 374.3 | 838.9 | 537.7 | 484.2 | 798.7 | 257.9 | 246.9 | 742.4 | 16.8 | 49.2 | 88.7 | 138.4 | 413.3 | 472 | 110.1 | 401.5 | 37.2 | 251.9 | 231.7 | 37.1 | 110 | 97.6 | 75.4
476 | 240 | 567.3 | 226.92 | 265.2564 | 271.6 | 245.8 | 212.1 | 86.9 | 420.4 | 22.5 | 20.5 | 55.3 | 4.1 | 227.1 | 4.4 | 879.3 | 828.1 | 178.5 | 454.2 | 376.8 | 839.3 | 541.7 | 486.8 | 793.9 | 258.4 | 248 | 743.3 | 16.8 | 49.5 | 89.4 | 139.2 | 415.1 | 474 | 110.5 | 403.8 | 37.4 | 251.9 | 231.8 | 37.3 | 110.6 | 98.1 | 75.8
477 | 241 | 566.8 | 226.72 | 265.0226 | 272.5 | 245.7 | 211.1 | 87.1 | 422.5 | 22.6 | 20.4 | 55.4 | 4 | 218 | 4.5 | 880.5 | 826.9 | 177.8 | 457 | 378.2 | 839.4 | 546.1 | 486.3 | 791.5 | 258.9 | 249 | 742.7 | 16.9 | 49.8 | 89.6 | 140.1 | 413.5 | 469.6 | 111 | 401.6 | 37.6 | 252.6 | 232.2 | 37.6 | 110.9 | 98.6 | 76.2
478 | 242 | 566.2 | 226.48 | 264.7421 | 273 | 245.1 | 212.1 | 87.3 | 422.3 | 22.7 | 20.4 | 55.5 | 3.9 | 231.2 | 4.8 | 882 | 834.4 | 177.7 | 459.6 | 379.9 | 840 | 550.1 | 486.2 | 784.8 | 259.3 | 249.9 | 743.4 | 16.9 | 50 | 89.9 | 141.1 | 413 | 469 | 111.4 | 400.5 | 37.8 | 253 | 233.5 | 37.9 | 111.4 | 99.1 | 76.5
479 | 243 | 567 | 226.8 | 265.1161 | 273.9 | 244.8 | 213.2 | 87.6 | 423 | 22.7 | 20.5 | 55.6 | 3.9 | 233.2 | 5.6 | 885.6 | 829.4 | 177.8 | 462.3 | 381.7 | 840.3 | 553.8 | 485.8 | 789.8 | 259.8 | 250.8 | 744.5 | 17 | 50.3 | 90.4 | 141.9 | 413.3 | 473.5 | 111.8 | 400.8 | 37.9 | 252.8 | 234.2 | 38.1 | 111.7 | 99.6 | 76.9
480 | 244 | 567.2 | 226.88 | 265.2096 | 275.2 | 244.5 | 213.8 | 87.8 | 424.2 | 22.8 | 20.4 | 55.7 | 3.9 | 218.9 | 5.7 | 879.7 | 827.3 | 177.6 | 465 | 383.3 | 841 | 556.9 | 485 | 788.8 | 260.3 | 251.7 | 745.2 | 17 | 50.6 | 90.7 | 142.8 | 413.2 | 471 | 112.1 | 400.1 | 38.1 | 252.9 | 235.9 | 38.3 | 112 | 100.1 | 77.3
481 | 245 | 567.3 | 226.92 | 265.2564 | 277.6 | 244.2 | 214.4 | 88 | 424.6 | 22.9 | 20.4 | 55.8 | 4 | 218.7 | 5.1 | 879.1 | 834.2 | 176.3 | 467.6 | 383.8 | 841.3 | 561.9 | 485.4 | 783.9 | 260.5 | 252.5 | 744.5 | 17.1 | 50.8 | 90.9 | 143.6 | 413.4 | 469.2 | 112.5 | 399.3 | 38.3 | 252.6 | 237.2 | 38.6 | 112.4 | 100.6 | 77.7
482 | 246 | 566.5 | 226.6 | 264.8823 | 279.6 | 244.9 | 216.3 | 88.2 | 423.9 | 22.9 | 20.4 | 56 | 3.8 | 233.2 | 4.9 | 880.4 | 838.5 | 176.7 | 470.2 | 385.4 | 840.6 | 567.4 | 486.5 | 790.3 | 260.4 | 253.2 | 744.4 | 17.1 | 51.1 | 91 | 144.3 | 413.2 | 470.9 | 112.9 | 400.2 | 38.5 | 252.6 | 238 | 38.9 | 112.8 | 101.1 | 78
483 | 247 | 565.4 | 226.16 | 264.368 | 280.1 | 245.5 | 216.6 | 88.4 | 422.8 | 23.1 | 20.4 | 56.2 | 3.9 | 241.9 | 5.2 | 877.6 | 847.5 | 175.7 | 472.8 | 387.1 | 839.6 | 571.9 | 488.8 | 792.5 | 260.4 | 253.9 | 745.1 | 17.2 | 51.3 | 91.3 | 145.1 | 413 | 470.4 | 113.4 | 400.8 | 38.7 | 253 | 238.5 | 39.1 | 113.2 | 101.5 | 78.3
484 | 248 | 565 | 226 | 264.181 | 279.7 | 246.6 | 217.7 | 88.6 | 423.1 | 23.1 | 20.4 | 56.4 | 4 | 244.7 | 5.3 | 877.9 | 852.5 | 174.8 | 475.7 | 389.5 | 839.7 | 574.8 | 492 | 797.9 | 260.3 | 254.4 | 745.4 | 17.2 | 51.5 | 91.7 | 145.8 | 414.7 | 478.2 | 114 | 404.6 | 38.9 | 253.3 | 239.2 | 39.4 | 113.6 | 102 | 78.7
485 | 249 | 564.5 | 225.8 | 263.9472 | 278.4 | 247.4 | 217.8 | 88.9 | 425.8 | 23.1 | 20.4 | 56.4 | 3.6 | 255.2 | 5.6 | 879.5 | 856.3 | 174.2 | 478.4 | 391.5 | 839.4 | 577 | 494.6 | 799.4 | 260.1 | 255 | 745.1 | 17.3 | 51.8 | 91.8 | 146.6 | 416.9 | 481.3 | 115.1 | 408.3 | 39 | 253.8 | 239.5 | 39.6 | 114 | 102.6 | 79
486 | 250 | 564.4 | 225.76 | 263.9004 | 277.2 | 247.8 | 217.6 | 89.1 | 427.3 | 23.3 | 20.4 | 56.5 | 3.4 | 247.3 | 5.8 | 877.6 | 859.9 | 174 | 481.4 | 393.2 | 840.1 | 579 | 497.5 | 799.6 | 259.8 | 255.5 | 745.4 | 17.4 | 52 | 92.1 | 147.3 | 417.9 | 482.4 | 115.4 | 410.5 | 39.2 | 254 | 239.5 | 39.8 | 114.5 | 103.1 | 79.4
487 | 251 | 564.4 | 225.76 | 263.9004 | 276.3 | 248.9 | 218.2 | 89.3 | 427.4 | 23.4 | 20.4 | 56.7 | 4.1 | 228.6 | 5.8 | 877.6 | 866.9 | 175.6 | 484.5 | 395.4 | 840.5 | 582.4 | 501.1 | 801.4 | 259.5 | 255.9 | 746.5 | 17.4 | 52.3 | 92.5 | 148.1 | 418.6 | 486.6 | 116 | 413.5 | 39.4 | 254.4 | 239.2 | 40 | 114.9 | 103.7 | 79.8
488 | 252 | 565.6 | 226.24 | 264.4615 | 275.7 | 250.3 | 219.4 | 89.5 | 431.5 | 23.5 | 20.4 | 56.8 | 4.2 | 236.2 | 5.5 | 878.4 | 863.5 | 176.4 | 487.9 | 396.9 | 840 | 585.6 | 505 | 802.9 | 258.5 | 256.4 | 745.5 | 17.5 | 52.5 | 93.2 | 149 | 421.2 | 498.8 | 116.7 | 417.6 | 39.6 | 254.3 | 239.4 | 40.3 | 115.3 | 104.2 | 80.2
489 | 253 | 565.9 | 226.36 | 264.6018 | 274.3 | 251.5 | 220.2 | 89.7 | 434.6 | 23.6 | 20.4 | 57 | 3.8 | 249.7 | 5.2 | 883.7 | 864.5 | 177.2 | 491.1 | 398.7 | 839.2 | 588.2 | 508.8 | 802.2 | 256.2 | 256.8 | 745.4 | 17.5 | 52.8 | 93.8 | 149.8 | 423.3 | 504.7 | 117.2 | 418.7 | 39.8 | 254.6 | 239.5 | 40.5 | 115.5 | 104.8 | 80.5
490 | 254 | 566.2 | 226.48 | 264.7421 | 273.4 | 253.4 | 220.9 | 89.9 | 437 | 23.7 | 20.4 | 57 | 3.8 | 245.3 | 5.2 | 887.3 | 861.7 | 179.1 | 494.5 | 400.8 | 838.6 | 589.9 | 512.3 | 802.3 | 255.6 | 257.2 | 745.1 | 17.6 | 53 | 94.1 | 150.6 | 424 | 509.3 | 117.6 | 418.9 | 40 | 256.4 | 240.2 | 40.7 | 115.9 | 105.4 | 80.9
491 | 255 | 566.8 | 226.72 | 265.0226 | 273 | 255.4 | 221 | 90 | 434.8 | 23.8 | 20.4 | 57.1 | 3.8 | 245 | 5.5 | 892.7 | 866.5 | 180.4 | 497.9 | 402.1 | 838.2 | 590.5 | 515.1 | 798.6 | 255.6 | 257.4 | 744.1 | 17.6 | 53.3 | 94.2 | 151.4 | 424.2 | 508.3 | 118.2 | 418.3 | 40.2 | 257.6 | 240.7 | 41 | 116.4 | 106 | 81.3
492 | 256 | 564.6 | 225.84 | 263.9939 | 272.3 | 256 | 220.3 | 90.1 | 433.1 | 23.9 | 20.4 | 57.2 | 4 | 242.9 | 5.3 | 895.7 | 865.2 | 181 | 501.3 | 404 | 839.1 | 591.2 | 518.8 | 799.3 | 255.8 | 257.8 | 745.7 | 17.7 | 53.5 | 94.5 | 152.2 | 427 | 509.7 | 118.6 | 420.6 | 40.4 | 258.3 | 240.9 | 41.2 | 116.7 | 106.6 | 81.7
493 | 257 | 563.8 | 225.52 | 263.6199 | 272.2 | 256.9 | 217.9 | 90.2 | 432.5 | 24 | 20.4 | 57.3 | 3.8 | 237.2 | 5.4 | 890.6 | 861.7 | 181.2 | 504.6 | 405.3 | 839.2 | 591.8 | 523 | 796.9 | 256 | 258.1 | 744.9 | 17.8 | 53.8 | 94.7 | 153 | 427.4 | 509.4 | 119.3 | 421.5 | 40.6 | 258.4 | 240.4 | 41.4 | 117 | 107.2 | 82.1
494 | 258 | 564.3 | 225.72 | 263.8537 | 272.2 | 257.4 | 217.7 | 90.3 | 432.2 | 24.1 | 20.4 | 57.5 | 4.3 | 225.5 | 5.1 | 895.6 | 867 | 181.5 | 507.8 | 407 | 839.3 | 592.4 | 527 | 798.7 | 256.6 | 258.4 | 744.9 | 17.8 | 54 | 95.2 | 153.7 | 427.7 | 508.4 | 120.1 | 422.6 | 40.7 | 258.2 | 240.2 | 41.6 | 117.3 | 107.8 | 82.4
495 | 259 | 565.4 | 226.16 | 264.368 | 272 | 257.5 | 217.7 | 90.5 | 433.4 | 24.2 | 20.4 | 57.8 | 4.2 | 231.3 | 4.7 | 894.9 | 861.7 | 181.6 | 510.9 | 408.5 | 839.2 | 593.8 | 530.9 | 799.3 | 257.2 | 258.7 | 745 | 17.9 | 54.2 | 95.4 | 154.4 | 428.1 | 507.4 | 121.1 | 424.5 | 40.9 | 258 | 240 | 41.9 | 117.6 | 108.3 | 82.8
496 | 260 | 565.7 | 226.28 | 264.5083 | 272.1 | 257.5 | 217.4 | 90.6 | 431.2 | 24.2 | 20.4 | 57.9 | 4.4 | 239 | 4.7 | 883.7 | 864.5 | 181.6 | 514 | 409.1 | 839.4 | 594.5 | 535.7 | 799.2 | 258 | 259 | 744.6 | 17.9 | 54.4 | 95.6 | 155.2 | 427.6 | 504.2 | 121.8 | 425.7 | 41.1 | 258 | 239.7 | 42.1 | 118 | 108.9 | 83.1
497 | 261 | 565.7 | 226.28 | 264.5083 | 270.9 | 257.5 | 217.1 | 90.7 | 430 | 24.4 | 20.4 | 58.1 | 4.3 | 238.1 | 4.9 | 884.9 | 848.7 | 181.3 | 517.3 | 410.8 | 840.7 | 596.1 | 540.5 | 801.4 | 258.7 | 259.4 | 745.1 | 18 | 54.6 | 96 | 155.9 | 427.4 | 502.9 | 122.7 | 425.6 | 41.3 | 258.2 | 239.3 | 42.3 | 118.2 | 109.5 | 83.5
498 | 262 | 566.1 | 226.44 | 264.6953 | 271 | 257.6 | 217.5 | 90.9 | 429.4 | 24.5 | 20.4 | 58.3 | 4.4 | 215.3 | 4.4 | 886.8 | 844.8 | 180.6 | 520.1 | 412.4 | 840.9 | 597.5 | 543.2 | 804.1 | 259.3 | 259.8 | 746.8 | 18 | 54.8 | 96.5 | 156.6 | 428.1 | 502.2 | 123.3 | 425.9 | 41.5 | 259 | 239.2 | 42.6 | 118.4 | 110 | 83.8
499 | 263 | 565.6 | 226.24 | 264.4615 | 272.8 | 257.5 | 217.7 | 91.1 | 430.4 | 24.7 | 20.4 | 58.5 | 4.2 | 229.3 | 4 | 883.5 | 850.8 | 180.8 | 522.9 | 412.9 | 841.2 | 598 | 545.9 | 805.7 | 260 | 260.1 | 746.6 | 18.1 | 55.1 | 96.8 | 157.3 | 430.1 | 510.9 | 123.8 | 427.3 | 41.7 | 258.8 | 239.7 | 42.8 | 119 | 110.6 | 84.2
500 | 264 | 564.6 | 225.84 | 263.9939 | 273.8 | 257.2 | 217.7 | 91.2 | 438 | 24.8 | 20.4 | 58.6 | 4.3 | 246.3 | 3.8 | 889 | 858.3 | 180.9 | 525.6 | 413.2 | 841.6 | 598 | 548 | 804.3 | 260.6 | 260.2 | 746.6 | 18.2 | 55.3 | 97.4 | 158 | 431.3 | 517 | 124.6 | 427.8 | 41.9 | 258.4 | 239.9 | 43.1 | 119.5 | 111.2 | 84.5
501 | 265 | 564.6 | 225.84 | 263.9939 | 273.6 | 257.4 | 217.3 | 91.3 | 442.7 | 24.9 | 20.4 | 58.7 | 4.4 | 230.9 | 3.8 | 890.6 | 864.7 | 181.6 | 528.2 | 414.4 | 841.6 | 598.7 | 548.4 | 800.7 | 261.2 | 260.3 | 746 | 18.2 | 55.6 | 97.7 | 158.7 | 432.7 | 517.5 | 125.1 | 428.4 | 42 | 258.1 | 240 | 43.3 | 119.8 | 111.7 | 84.9
502 | 266 | 564.6 | 225.84 | 263.9939 | 273 | 258.4 | 218 | 91.5 | 443.5 | 25 | 20.4 | 58.8 | 4.3 | 226.8 | 3.5 | 890.4 | 869.3 | 182.1 | 530.8 | 415.7 | 841.7 | 600.5 | 550.3 | 801.7 | 261.8 | 260.4 | 746.5 | 18.3 | 55.8 | 97.8 | 159.4 | 435 | 518 | 125.8 | 429.5 | 42.2 | 257.8 | 239.9 | 43.5 | 120.1 | 112.3 | 85.2
503 | 267 | 564.4 | 225.76 | 263.9004 | 272.3 | 259.8 | 217.4 | 91.7 | 444.3 | 25.2 | 20.4 | 58.9 | 4.4 | 228.8 | 3.5 | 885 | 865 | 181.8 | 533.3 | 416.5 | 842.8 | 603 | 550.5 | 799.9 | 262.3 | 260.2 | 747.1 | 18.4 | 56 | 98.1 | 160.1 | 436 | 515.3 | 126.4 | 430.7 | 42.4 | 258.5 | 240.6 | 43.8 | 120.4 | 112.9 | 85.6
504 | 268 | 564.9 | 225.96 | 264.1342 | 271.7 | 259.8 | 215.9 | 92 | 440.5 | 25.2 | 20.3 | 59 | 4.4 | 237.9 | 3.5 | 885.6 | 865.9 | 182.8 | 535.8 | 417.9 | 843.1 | 605.8 | 552.7 | 797.7 | 262.8 | 260.1 | 746.6 | 18.4 | 56.3 | 98.5 | 160.9 | 435.5 | 515.7 | 127 | 431.5 | 42.6 | 259.2 | 241 | 44 | 120.7 | 113.5 | 85.9
505 | 269 | 564.2 | 225.68 | 263.8069 | 270.3 | 260.4 | 214.6 | 92.4 | 439.9 | 25.3 | 20.3 | 59.1 | 4.2 | 222.5 | 3.2 | 886.7 | 862.2 | 183.9 | 538.6 | 419.7 | 842.6 | 607.2 | 555.2 | 798.4 | 263.3 | 259.9 | 747.3 | 18.5 | 56.5 | 99.1 | 161.6 | 436.2 | 518.8 | 127.6 | 434.1 | 42.8 | 260.2 | 241.5 | 44.2 | 121.2 | 114.2 | 86.3
506 | 270 | 563.8 | 225.52 | 263.6199 | 269.3 | 261.6 | 214.6 | 92.8 | 441.3 | 25.4 | 20.3 | 59.3 | 4.1 | 227 | 3.1 | 892.8 | 862.1 | 184.8 | 541.6 | 421.7 | 842.3 | 607.9 | 557.2 | 796.4 | 263.9 | 260 | 746.6 | 18.5 | 56.7 | 99.4 | 162.3 | 437.1 | 520.8 | 128.5 | 435.8 | 43 | 260.3 | 242.2 | 44.5 | 121.7 | 114.8 | 86.7
507 | 271 | 564.7 | 225.88 | 264.0407 | 269.9 | 262 | 214.3 | 93.2 | 441.2 | 25.5 | 20.3 | 59.4 | 4.1 | 255 | 3.3 | 893.3 | 865.3 | 184.9 | 544.3 | 423.5 | 843.1 | 609.4 | 556.3 | 793 | 264.5 | 260.2 | 746.9 | 18.6 | 57 | 99.5 | 163 | 436.6 | 517 | 129.3 | 434.8 | 43.1 | 260.3 | 242.3 | 44.7 | 122.2 | 115.4 | 87.1
508 | 272 | 566 | 226.4 | 264.6486 | 270.9 | 261.3 | 214.6 | 93.6 | 438.8 | 25.7 | 20.3 | 59.5 | 4 | 262.8 | 3.8 | 894.4 | 869.6 | 186 | 546.2 | 424 | 843.1 | 609.7 | 554.4 | 792.5 | 265.1 | 260.3 | 746.5 | 18.7 | 57.2 | 99.8 | 163.7 | 435.8 | 518.1 | 129.8 | 433.8 | 43.3 | 260.2 | 242.8 | 44.9 | 122.5 | 116 | 87.5
509 | 273 | 566 | 226.4 | 264.6486 | 270.6 | 261.1 | 215.7 | 94 | 439.7 | 25.8 | 20.3 | 59.6 | 3.7 | 259.8 | 4.3 | 889.6 | 868.2 | 186.8 | 548.3 | 424.4 | 842.4 | 609.6 | 554.2 | 794.8 | 265.8 | 260.4 | 746.9 | 18.7 | 57.5 | 100.1 | 164.5 | 436.6 | 523.6 | 130.4 | 436 | 43.5 | 259.6 | 243.4 | 45.2 | 122.9 | 116.5 | 87.8
510 | 274 | 566.1 | 226.44 | 264.6953 | 270.1 | 261.8 | 216.6 | 94.4 | 439.5 | 26 | 20.3 | 59.9 | 3.7 | 251 | 4.5 | 878.1 | 866 | 188.2 | 550.7 | 425.6 | 841.7 | 611.1 | 555.5 | 796.9 | 266.6 | 260.7 | 746.1 | 18.8 | 57.7 | 100.5 | 165.2 | 436.9 | 522.7 | 131.3 | 439.3 | 43.7 | 258.9 | 244.2 | 45.4 | 123.2 | 117.1 | 88.2
511 | 275 | 566 | 226.4 | 264.6486 | 269.4 | 262.8 | 216.1 | 94.8 | 437.5 | 26.1 | 20.3 | 60.1 | 4 | 243.5 | 4.3 | 882.4 | 865.1 | 188.6 | 553.4 | 427.9 | 841.5 | 612 | 559 | 799.7 | 267.5 | 261 | 745.6 | 18.9 | 58 | 101 | 166 | 437 | 522.8 | 132 | 442.7 | 43.9 | 258.8 | 244.4 | 45.6 | 123.7 | 117.7 | 88.5
512 | 276 | 566.5 | 226.6 | 264.8823 | 268.4 | 263.8 | 216.3 | 95.2 | 438.4 | 26.1 | 20.3 | 60.3 | 4.2 | 245.3 | 4.1 | 883.5 | 861 | 188.5 | 555.9 | 429.5 | 841.4 | 611.5 | 558 | 798.3 | 268.3 | 261.4 | 746.3 | 18.9 | 58.2 | 101.3 | 166.7 | 437.9 | 520.7 | 132.7 | 442.5 | 44.1 | 259.2 | 244.5 | 45.9 | 124.3 | 118.3 | 88.9
513 | 277 | 566.4 | 226.56 | 264.8356 | 269 | 264.3 | 217.4 | 95.7 | 439.2 | 26.2 | 20.3 | 60.4 | 4.1 | 244.4 | 4.1 | 884.8 | 860.9 | 188.8 | 558.5 | 430.5 | 841 | 612.3 | 558.2 | 796.4 | 269.1 | 261.7 | 746.1 | 19 | 58.4 | 101.6 | 167.5 | 438.6 | 519.2 | 133.3 | 442.6 | 44.3 | 259.7 | 245.2 | 46.1 | 124.7 | 118.9 | 89.2
514 | 278 | 565.1 | 226.04 | 264.2277 | 269 | 264.3 | 217.4 | 96.2 | 441.9 | 26.2 | 20.3 | 60.4 | 4.1 | 231.7 | 3.9 | 890.4 | 863.1 | 187.7 | 560.6 | 432.7 | 841.5 | 614 | 557.7 | 797.4 | 269.7 | 262.2 | 746.1 | 19.1 | 58.6 | 102.1 | 168.2 | 439.4 | 524 | 134.1 | 443.5 | 44.4 | 259.2 | 246 | 46.3 | 125 | 119.5 | 89.6
515 | 279 | 566.2 | 226.48 | 264.7421 | 269.1 | 263.5 | 217.3 | 96.7 | 446.5 | 26.4 | 20.3 | 60.6 | 4.1 | 219.7 | 3.4 | 888.2 | 862.9 | 188.1 | 563.1 | 433.8 | 842.1 | 615.1 | 558.2 | 794.5 | 270.4 | 262.5 | 746.4 | 19.1 | 58.9 | 102.5 | 169 | 441.4 | 537.9 | 134.8 | 447.7 | 44.6 | 259.7 | 246.4 | 46.5 | 125.6 | 120.1 | 89.9
516 | 280 | 566 | 226.4 | 264.6486 | 269.7 | 264.3 | 217.5 | 97 | 447 | 26.5 | 20.3 | 60.8 | 3.9 | 254 | 3.7 | 880.8 | 866.1 | 188.8 | 565.8 | 435 | 842.3 | 615.3 | 558.9 | 793.2 | 271.2 | 262.7 | 747.3 | 19.2 | 59.1 | 102.8 | 169.8 | 442.3 | 542.6 | 135.4 | 447.6 | 44.8 | 259.9 | 246.4 | 46.7 | 126 | 120.7 | 90.3
517 | 281 | 565.9 | 226.36 | 264.6018 | 270.1 | 265.8 | 219.4 | 97.3 | 445.7 | 26.6 | 20.3 | 61 | 3.9 | 247.2 | 4.5 | 874 | 862.4 | 189.4 | 568.3 | 436.4 | 842.1 | 615.4 | 564.1 | 794.3 | 272 | 263.1 | 748.6 | 19.3 | 59.3 | 103.2 | 170.6 | 444.1 | 547.7 | 136 | 450.5 | 45 | 260.3 | 246.3 | 47 | 126.4 | 121.3 | 90.6
518 | 282 | 566 | 226.4 | 264.6486 | 269.6 | 265.8 | 221 | 97.6 | 446.9 | 26.7 | 20.3 | 61 | 3.7 | 224.1 | 4.3 | 871 | 858.7 | 189.6 | 571.1 | 438.5 | 842.2 | 615.7 | 565.8 | 791.7 | 272.7 | 263.5 | 748.2 | 19.3 | 59.6 | 103.4 | 171.3 | 445.1 | 546.1 | 136.9 | 451.2 | 45.2 | 260.3 | 246.1 | 47.2 | 126.8 | 122 | 91
519 | 283 | 565.9 | 226.36 | 264.6018 | 269.1 | 265.1 | 221 | 98 | 445 | 26.7 | 20.3 | 61.2 | 3.9 | 234.4 | 4 | 868.9 | 855 | 189.7 | 573.4 | 439.8 | 841.8 | 614.9 | 566.1 | 790.8 | 273.3 | 264 | 748 | 19.4 | 59.8 | 103.6 | 172.1 | 445.3 | 541.3 | 137.6 | 452.1 | 45.4 | 261 | 246.3 | 47.4 | 127.1 | 122.6 | 91.4
520 | 284 | 566.2 | 226.48 | 264.7421 | 268.4 | 264.6 | 220.9 | 98.4 | 445.2 | 26.9 | 20.3 | 61.3 | 4.4 | 260 | 3.9 | 874.7 | 854.9 | 189.5 | 576.5 | 441.3 | 841.1 | 616 | 565 | 792.9 | 273.9 | 264.3 | 747.5 | 19.4 | 60 | 104 | 172.9 | 445.7 | 538.3 | 138.3 | 453.7 | 45.6 | 262.1 | 246.5 | 47.6 | 127.5 | 123.3 | 91.8
521 | 285 | 565.7 | 226.28 | 264.5083 | 267.2 | 264 | 221.3 | 98.8 | 446.3 | 26.9 | 20.3 | 61.4 | 4.8 | 245.5 | 3.9 | 874.7 | 849.7 | 190 | 580 | 443.6 | 840.2 | 617.8 | 567.8 | 794.6 | 274.4 | 264.6 | 747.5 | 19.5 | 60.2 | 104.4 | 173.7 | 445.9 | 535.1 | 139.2 | 456.8 | 45.7 | 264 | 247.4 | 47.8 | 127.8 | 123.9 | 92.2
522 | 286 | 565 | 226 | 264.181 | 266.8 | 264.5 | 220.8 | 99.3 | 443.6 | 27 | 20.3 | 61.6 | 4.5 | 222.2 | 3.9 | 871.1 | 854.6 | 189.9 | 583.1 | 445.1 | 839.6 | 616.6 | 567.4 | 791.4 | 274.9 | 264.8 | 746.3 | 19.6 | 60.5 | 104.7 | 174.5 | 445.6 | 533.5 | 139.5 | 457 | 45.9 | 265.2 | 248.2 | 48 | 128.5 | 124.5 | 92.6
523 | 287 | 566.8 | 226.72 | 265.0226 | 266.2 | 266 | 219.7 | 99.8 | 445.2 | 27 | 20.3 | 61.7 | 4.2 | 242.5 | 3.8 | 864.9 | 857 | 189.5 | 586.4 | 447.5 | 839.5 | 616.2 | 566.8 | 789.7 | 275.5 | 265.3 | 746.4 | 19.7 | 60.7 | 105 | 175.3 | 445.7 | 540 | 140 | 458.3 | 46.1 | 265 | 248.7 | 48.3 | 128.9 | 125.2 | 93
524 | 288 | 567.6 | 227.04 | 265.3967 | 265.9 | 267.6 | 218.2 | 100.3 | 449 | 27.1 | 20.2 | 61.8 | 4 | 264.3 | 3.6 | 858.1 | 857.6 | 190 | 588.9 | 448.5 | 839.8 | 615.7 | 564.4 | 787.6 | 276.5 | 265.7 | 747.7 | 19.7 | 61 | 105.3 | 176.2 | 447.5 | 542.5 | 140.7 | 460.3 | 46.3 | 265.1 | 248.4 | 48.5 | 129.2 | 125.8 | 93.4
525 | 289 | 568.4 | 227.36 | 265.7707 | 265.9 | 269 | 216.7 | 100.7 | 448.1 | 27.2 | 20.2 | 61.8 | 4.1 | 276.8 | 3.6 | 858.1 | 859.8 | 190.7 | 591.6 | 450.3 | 839.9 | 616.3 | 563.2 | 788.5 | 277.2 | 265.8 | 747.2 | 19.8 | 61.2 | 105.8 | 177 | 447.7 | 541.4 | 141.3 | 461 | 46.5 | 264.8 | 248.4 | 48.7 | 129.7 | 126.5 | 93.8
526 | 290 | 569.6 | 227.84 | 266.3318 | 266.2 | 270.9 | 215.8 | 101 | 450 | 27.2 | 20.2 | 61.8 | 4.1 | 261 | 3.7 | 866.1 | 862 | 191.8 | 595.1 | 452.7 | 839.4 | 616.7 | 563.4 | 787.1 | 277.9 | 266.1 | 747 | 19.8 | 61.5 | 106.2 | 177.9 | 451.3 | 545.7 | 142 | 463.7 | 46.7 | 265.4 | 248.5 | 48.9 | 130.1 | 127.1 | 94.1
527 | 291 | 568.7 | 227.48 | 265.911 | 265.7 | 272.4 | 215 | 101.3 | 453 | 27.3 | 20.2 | 62 | 4.2 | 241.5 | 3.7 | 869.7 | 858.5 | 191.9 | 598 | 455.8 | 838.4 | 618 | 564.1 | 783.2 | 278.7 | 266.8 | 746.7 | 19.9 | 61.7 | 106.6 | 178.7 | 453.7 | 543 | 142.6 | 465.3 | 46.8 | 266.3 | 248.7 | 49.1 | 130.7 | 127.7 | 94.5
528 | 292 | 566.9 | 226.76 | 265.0694 | 264.7 | 273.5 | 213.8 | 101.6 | 451 | 27.4 | 20.2 | 62.1 | 4.6 | 237.1 | 3.7 | 871 | 863.7 | 193.3 | 600.7 | 457.7 | 838 | 617.5 | 563.3 | 780.5 | 279.4 | 267.6 | 744.7 | 20 | 62 | 106.9 | 179.6 | 453.4 | 539.1 | 143.1 | 464.3 | 47.1 | 267.3 | 248.6 | 49.3 | 131.2 | 128.5 | 94.9
529 | 293 | 566.3 | 226.52 | 264.7888 | 263.5 | 273.9 | 213.2 | 101.9 | 448.9 | 27.5 | 20.2 | 62.3 | 4.6 | 232.7 | 3.5 | 876.3 | 862.8 | 195.1 | 602.9 | 460.3 | 838.1 | 617.9 | 565.1 | 779.5 | 280.3 | 268.4 | 744.1 | 20.1 | 62.2 | 107.4 | 180.5 | 454.1 | 541.7 | 143.5 | 464.4 | 47.2 | 268.5 | 249 | 49.5 | 131.6 | 129.1 | 95.4
530 | 294 | 566.7 | 226.68 | 264.9759 | 263.1 | 275.7 | 214.6 | 102.1 | 448.6 | 27.6 | 20.2 | 62.4 | 4.4 | 206.3 | 3.3 | 875.7 | 852.9 | 196.2 | 605.3 | 462.8 | 837.3 | 618.4 | 569.7 | 781.4 | 281.1 | 269.2 | 744.4 | 20.1 | 62.4 | 108 | 181.4 | 455.3 | 554.1 | 143.8 | 466.4 | 47.4 | 268.5 | 249.6 | 49.7 | 131.7 | 129.8 | 95.7
531 | 295 | 566.6 | 226.64 | 264.9291 | 263.8 | 277.8 | 216.3 | 102.3 | 462 | 27.7 | 20.2 | 62.5 | 4.6 | 199.7 | 3 | 877.6 | 851.2 | 198.5 | 607.8 | 465.2 | 836.8 | 619.7 | 574 | 782.6 | 281.9 | 270.1 | 743 | 20.2 | 62.6 | 109 | 182.3 | 460.6 | 573.1 | 144.6 | 473.2 | 47.6 | 268.9 | 249.8 | 49.9 | 131.9 | 130.5 | 96.1
532 | 296 | 565.7 | 226.28 | 264.5083 | 263.9 | 278.1 | 219.3 | 102.4 | 479.4 | 27.8 | 20.2 | 62.7 | 4.5 | 217.7 | 3.1 | 873.5 | 845.2 | 200.7 | 610.5 | 467.1 | 836.6 | 620.4 | 579.1 | 781.4 | 282.7 | 270.8 | 742.7 | 20.3 | 62.9 | 110.1 | 183.2 | 464.8 | 594.2 | 145.3 | 478.8 | 47.8 | 269.3 | 249.5 | 50.1 | 132.2 | 131.3 | 96.5
533 | 297 | 566.7 | 226.68 | 264.9759 | 263.6 | 278.6 | 222.7 | 102.5 | 496.8 | 27.9 | 20.2 | 62.9 | 4.5 | 210.5 | 3.1 | 867.3 | 839 | 202.8 | 613.1 | 468.3 | 834.4 | 619.8 | 585.3 | 780.5 | 283.6 | 271.3 | 740.4 | 20.3 | 63.1 | 110.5 | 184 | 470.5 | 608.5 | 146.2 | 483.4 | 48 | 269.1 | 249.2 | 50.3 | 132.5 | 132.1 | 96.8
534 | 298 | 566.2 | 226.48 | 264.7421 | 263.7 | 278.3 | 225.8 | 102.5 | 504.1 | 28 | 20.2 | 63 | 4.2 | 201.8 | 2.6 | 869.4 | 848.2 | 204 | 614.7 | 469.4 | 833.4 | 619.4 | 587.6 | 773.1 | 284.5 | 272 | 738.4 | 20.4 | 63.4 | 110.8 | 184.9 | 473.1 | 621.4 | 147.1 | 484.3 | 48.2 | 269 | 249 | 50.5 | 132.8 | 132.8 | 97.1
535 | 299 | 567.2 | 226.88 | 265.2096 | 263.4 | 277.2 | 229 | 102.6 | 512.4 | 28.1 | 20.2 | 63.1 | 4.2 | 252.6 | 2.8 | 871.8 | 845.8 | 205 | 616.5 | 470.9 | 834.4 | 618.8 | 589 | 768 | 285.3 | 272.8 | 737.7 | 20.5 | 63.6 | 111.6 | 185.7 | 476.8 | 637.3 | 148.1 | 488.6 | 48.4 | 269.5 | 249.2 | 50.7 | 133 | 133.6 | 97.5
536 | 300 | 567.6 | 227.04 | 265.3967 | 263 | 276.6 | 230.3 | 102.7 | 522.2 | 28.2 | 20.2 | 63.2 | 4.4 | 265.1 | 3.6 | 865.8 | 844.5 | 206.1 | 617.7 | 472.1 | 834.1 | 619.6 | 589.5 | 764.8 | 286.3 | 273.7 | 736.1 | 20.5 | 63.9 | 112.5 | 186.5 | 481.4 | 646.1 | 149 | 491.3 | 48.5 | 270.2 | 249.3 | 50.9 | 133.4 | 134.3 | 97.8
537 | 301 | 567 | 226.8 | 265.1161 | 261.1 | 276.1 | 233 | 102.8 | 529.5 | 28.3 | 20.2 | 63.2 | 4.2 | 233.8 | 4.6 | 858.9 | 835.1 | 208 | 619.8 | 473.8 | 833.4 | 618.9 | 592.1 | 763.9 | 287.2 | 274.4 | 735 | 20.6 | 64.1 | 113.5 | 187.4 | 485.7 | 654.8 | 150 | 493.8 | 48.7 | 270.9 | 249.2 | 51.1 | 133.9 | 135.1 | 98.2
538 | 302 | 567.1 | 226.84 | 265.1629 | 261.4 | 276.1 | 236.5 | 103.1 | 539.7 | 28.4 | 20.2 | 63.3 | 4.1 | 246.2 | 4.5 | 854 | 826.6 | 209.7 | 622 | 474.7 | 832.2 | 617.1 | 595.9 | 761.2 | 288 | 274.6 | 733.8 | 20.7 | 64.4 | 114 | 188.2 | 491.6 | 664.9 | 151.1 | 496.1 | 48.9 | 270.9 | 249.1 | 51.3 | 134.3 | 135.9 | 98.6
539 | 303 | 565.8 | 226.32 | 264.555 | 262.9 | 276.3 | 239.2 | 103.6 | 544.8 | 28.5 | 20.2 | 63.3 | 4.2 | 268 | 4.4 | 852.4 | 831 | 211.4 | 623.2 | 475.4 | 831.1 | 615.6 | 598.3 | 754.7 | 288.9 | 275.3 | 732.5 | 20.8 | 64.6 | 115 | 189.1 | 494.2 | 665 | 151.9 | 494.6 | 49.1 | 271.3 | 249.3 | 51.5 | 134.4 | 136.7 | 98.9
540 | 304 | 565.8 | 226.32 | 264.555 | 263.4 | 275.6 | 241.5 | 103.8 | 541.5 | 28.5 | 20.2 | 63.3 | 3.7 | 252.4 | 4.5 | 856.7 | 838.8 | 212.7 | 623 | 475.3 | 830.6 | 614.5 | 598.5 | 755.1 | 289.8 | 275.5 | 731.6 | 20.8 | 64.9 | 115 | 190 | 494 | 667.6 | 152.8 | 493.7 | 49.3 | 271.6 | 249.6 | 51.6 | 134.8 | 137.4 | 99.3
541 | 305 | 566.3 | 226.52 | 264.7888 | 263.7 | 274.5 | 244.1 | 104.1 | 536.1 | 28.6 | 20.2 | 63.4 | 4.1 | 222.5 | 4.4 | 863.4 | 843 | 213.2 | 623.9 | 476.7 | 831.1 | 614.9 | 596 | 760.1 | 290.9 | 276.3 | 732.2 | 20.9 | 65.2 | 115.2 | 190.9 | 495.6 | 670.9 | 153.7 | 496.1 | 49.5 | 272 | 249.7 | 51.8 | 135.1 | 138.2 | 99.7
542 | 306 | 565.6 | 226.24 | 264.4615 | 262.9 | 273.8 | 244.2 | 104.3 | 531.8 | 28.7 | 20.2 | 63.6 | 4.3 | 211.2 | 4.1 | 862.5 | 840.9 | 213.3 | 624.2 | 477.5 | 831.2 | 615.7 | 593 | 760.6 | 292 | 276.7 | 732.7 | 21 | 65.4 | 115.8 | 191.9 | 497.8 | 671.4 | 154.4 | 501.2 | 49.7 | 272 | 250.1 | 52 | 135.4 | 138.9 | 100.1
543 | 307 | 567 | 226.8 | 265.1161 | 262.7 | 274 | 244.2 | 104.5 | 532.7 | 28.8 | 20.2 | 63.8 | 4.5 | 212.2 | 4.8 | 860.4 | 832.2 | 213.8 | 626.3 | 479.3 | 832 | 615.5 | 592 | 759.7 | 293.1 | 277.2 | 731.2 | 21.1 | 65.7 | 116.5 | 192.9 | 498.9 | 671.2 | 155.2 | 503.6 | 49.8 | 271.8 | 250.5 | 52.2 | 135.8 | 139.6 | 100.4
544 | 308 | 567.3 | 226.92 | 265.2564 | 264.2 | 273.4 | 245.1 | 104.6 | 536.5 | 29 | 20.2 | 63.9 | 4.5 | 210.5 | 5.9 | 859.2 | 832.1 | 214.9 | 627.6 | 480.7 | 832.7 | 616 | 592.5 | 758.7 | 294.1 | 278 | 731.1 | 21.1 | 66 | 117.8 | 193.8 | 502.3 | 673.6 | 156 | 504.5 | 50 | 273.1 | 250.6 | 52.4 | 136.1 | 140.4 | 100.8
545 | 309 | 566.5 | 226.6 | 264.8823 | 265.8 | 272.8 | 245.4 | 104.7 | 541.7 | 29 | 20.2 | 64 | 4.5 | 220.8 | 5.1 | 849.3 | 826.4 | 215.3 | 628.1 | 482 | 832.1 | 615.9 | 593.6 | 754.6 | 294.9 | 278.1 | 730.8 | 21.2 | 66.2 | 117.9 | 194.8 | 504.1 | 681.5 | 156.9 | 505.2 | 50.2 | 273.9 | 251 | 52.6 | 136.5 | 141.1 | 101.2
546 | 310 | 567 | 226.8 | 265.1161 | 267.3 | 272.1 | 246.4 | 104.8 | 545.5 | 29.1 | 20.2 | 64.1 | 4.4 | 230.2 | 4.5 | 846.7 | 836 | 216.6 | 629.1 | 483.3 | 831.5 | 615.9 | 595.9 | 758.3 | 295.8 | 278.4 | 730.7 | 21.3 | 66.5 | 118.7 | 195.9 | 507.1 | 688.8 | 158.3 | 509.3 | 50.4 | 273.6 | 250.5 | 52.8 | 136.8 | 141.8 | 101.6
547 | 311 | 566.3 | 226.52 | 264.7888 | 268.4 | 271.2 | 246.5 | 105 | 543.3 | 29.2 | 20.2 | 64.2 | 3.7 | 219.6 | 4.9 | 853.9 | 841.6 | 217 | 629.2 | 484 | 832.4 | 614.8 | 591.8 | 757.8 | 296.8 | 278.9 | 729.7 | 21.4 | 66.8 | 119.2 | 196.9 | 509.1 | 687.1 | 159.3 | 510.5 | 50.6 | 274.2 | 250.4 | 53 | 137.3 | 142.5 | 102
548 | 312 | 567.6 | 227.04 | 265.3967 | 269 | 270.7 | 247.1 | 105.1 | 538.7 | 29.2 | 20.2 | 64.3 | 4.3 | 233.8 | 5.5 | 854.7 | 837.7 | 217.1 | 629.4 | 485.4 | 833.1 | 614.8 | 590.4 | 760.1 | 297.9 | 279.2 | 730 | 21.4 | 67.1 | 119.8 | 197.9 | 510.9 | 689.8 | 160.1 | 511.6 | 50.8 | 274.8 | 250.4 | 53.2 | 137.7 | 143.3 | 102.4
549 | 313 | 567.5 | 227 | 265.3499 | 269.5 | 270.5 | 247.8 | 105.2 | 545 | 29.3 | 20.2 | 64.4 | 4.5 | 220.9 | 6.2 | 847.2 | 834.5 | 217.1 | 630.2 | 486.8 | 832.7 | 615.3 | 591.7 | 758.3 | 298.9 | 279.7 | 729 | 21.5 | 67.4 | 120.9 | 198.9 | 514.2 | 692.1 | 161.3 | 512 | 51 | 275.2 | 250.3 | 53.4 | 138.1 | 144 | 102.7
550 | 314 | 567.7 | 227.08 | 265.4434 | 269.6 | 270.3 | 249.3 | 105.4 | 546.8 | 29.3 | 20.2 | 64.5 | 4.2 | 218.7 | 6.5 | 843.3 | 828.2 | 217.7 | 631.2 | 487.9 | 832.1 | 616 | 593.1 | 752.3 | 299.8 | 280.2 | 727.2 | 21.6 | 67.6 | 121.5 | 199.9 | 516.1 | 697.8 | 162.3 | 516 | 51.2 | 275.1 | 250.1 | 53.6 | 138.4 | 144.7 | 103.1
551 | 315 | 567 | 226.8 | 265.1161 | 270 | 269.7 | 249.7 | 105.6 | 545.3 | 29.3 | 20.2 | 64.6 | 4.1 | 228 | 6.6 | 835.6 | 814.8 | 218.4 | 632.2 | 488.9 | 831.3 | 616.3 | 594.7 | 748.4 | 301 | 281 | 726 | 21.7 | 67.9 | 122.1 | 200.9 | 518.3 | 699.5 | 163.3 | 517.9 | 51.4 | 275.8 | 250.7 | 53.8 | 138.6 | 145.4 | 103.4
552 | 316 | 568.7 | 227.48 | 265.911 | 270.2 | 268.7 | 249.6 | 105.7 | 551.1 | 29.4 | 20.2 | 64.7 | 3.9 | 210.1 | 6.5 | 835.3 | 809.9 | 219 | 632.9 | 490.1 | 830.6 | 617.3 | 597.6 | 743.7 | 302.2 | 281.7 | 723.6 | 21.7 | 68.2 | 123 | 201.9 | 521.3 | 703.1 | 164.4 | 517 | 51.5 | 275.6 | 250.8 | 53.9 | 138.9 | 146.2 | 103.8
553 | 317 | 566.7 | 226.68 | 264.9759 | 271 | 268.2 | 251.1 | 106 | 558.7 | 29.5 | 20.1 | 64.9 | 4 | 202.9 | 5.7 | 837.1 | 812.9 | 219.1 | 634 | 491.4 | 830.9 | 618.8 | 599.9 | 742.1 | 303.1 | 282.3 | 724.1 | 21.8 | 68.5 | 123.6 | 202.9 | 522.3 | 705.4 | 165.6 | 517.8 | 51.7 | 275.5 | 250.8 | 54.1 | 139.3 | 146.9 | 104.2
554 | 318 | 564.7 | 225.88 | 264.0407 | 272 | 268.2 | 252 | 106.3 | 565.3 | 29.6 | 20.1 | 65 | 4.1 | 209 | 4.9 | 833.9 | 815.2 | 219.7 | 635.7 | 492.6 | 829.8 | 619.8 | 599.4 | 733.9 | 304.1 | 282.9 | 723.3 | 21.9 | 68.9 | 124.6 | 203.9 | 525 | 701.6 | 166.7 | 519.9 | 51.9 | 275.8 | 251.3 | 54.3 | 139.7 | 147.7 | 104.6
555 | 319 | 569 | 227.6 | 266.0513 | 272.7 | 268.7 | 253.1 | 106.7 | 565.1 | 29.7 | 20.1 | 65.2 | 3.9 | 230.7 | 4 | 840 | 816.4 | 220.4 | 636.8 | 493.7 | 829.9 | 621.6 | 598.5 | 731.2 | 305.3 | 283.6 | 721.2 | 22 | 69.2 | 124.7 | 204.9 | 524.1 | 692.4 | 167.6 | 518.1 | 52.1 | 275.8 | 251.9 | 54.5 | 140.1 | 148.4 | 105
556 | 320 | 562.3 | 224.92 | 262.9185 | 272.6 | 270.4 | 254.2 | 107.1 | 567.2 | 29.8 | 20.1 | 65.3 | 4.6 | 245.9 | 3.4 | 848.9 | 824.8 | 220.6 | 637.8 | 494.9 | 830.5 | 625.2 | 605.7 | 739.2 | 306.5 | 284.5 | 722.4 | 22 | 69.5 | 125.7 | 205.9 | 528.3 | 694.9 | 168.4 | 521.6 | 52.3 | 275.8 | 252.4 | 54.8 | 140.6 | 149.1 | 105.3
557 | 321 | 563.4 | 225.36 | 263.4329 | 272.9 | 272.1 | 255.4 | 107.4 | 570.1 | 29.9 | 20.1 | 65.5 | 4 | 241.5 | 3.3 | 848.8 | 823.8 | 221.3 | 639.5 | 496.7 | 831.2 | 628.8 | 607.3 | 734.9 | 307.8 | 285.1 | 721.4 | 22.1 | 69.8 | 126.5 | 206.9 | 531.4 | 698.7 | 169.4 | 525.2 | 52.5 | 276.5 | 252.3 | 55 | 140.9 | 149.8 | 105.7
558 | 322 | 563.8 | 225.52 | 263.6199 | 273.5 | 272.9 | 256.5 | 107.7 | 567.7 | 29.9 | 20.1 | 65.7 | 4.4 | 217.2 | 3.6 | 834.2 | 808.9 | 221.5 | 641.6 | 498.6 | 831.2 | 632.8 | 608.7 | 732.9 | 309.3 | 285.5 | 720.9 | 22.2 | 70.1 | 126.9 | 207.9 | 532.8 | 713.2 | 170.4 | 532.8 | 52.7 | 278 | 252.3 | 55.2 | 141.4 | 150.5 | 106.1
559 | 323 | 563.9 | 225.56 | 263.6666 | 274.7 | 272.8 | 256.8 | 108.1 | 570.8 | 30 | 20.1 | 65.9 | 4.5 | 203.4 | 4.5 | 824.7 | 801.3 | 220.9 | 643.7 | 500.3 | 828.9 | 634.9 | 608.3 | 734.6 | 310.7 | 285.9 | 720.7 | 22.3 | 70.5 | 127.8 | 209 | 535.6 | 714.9 | 171.5 | 535.8 | 52.9 | 278.9 | 253.1 | 55.4 | 142 | 151.3 | 106.5
560 | 324 | 566.9 | 226.76 | 265.0694 | 276 | 273.1 | 258 | 108.5 | 569.8 | 30.1 | 20.1 | 66.1 | 4.6 | 218.7 | 4.9 | 828 | 812.2 | 222.1 | 645.7 | 501.6 | 827.4 | 636.7 | 604.6 | 728.7 | 312.1 | 286.3 | 717 | 22.4 | 70.8 | 128.7 | 210 | 536.7 | 713.3 | 172.1 | 534.2 | 53.1 | 279.7 | 253.2 | 55.6 | 142.6 | 152 | 106.9
561 | 325 | 564.1 | 225.64 | 263.7602 | 276.3 | 273.4 | 259.6 | 108.9 | 567.7 | 30.2 | 20.1 | 66.1 | 4.1 | 214.4 | 5 | 833.5 | 821.5 | 223.4 | 648.3 | 503.1 | 828.1 | 640.1 | 606.6 | 735.7 | 313.6 | 286.9 | 718.3 | 22.4 | 71.1 | 128.9 | 211.1 | 534 | 717.3 | 172.5 | 537.2 | 53.3 | 280.1 | 253.9 | 55.9 | 142.9 | 152.7 | 107.3
562 | 326 | 564.9 | 225.96 | 264.1342 | 276.4 | 274 | 259.8 | 109.3 | 560.6 | 30.2 | 20.1 | 66.1 | 3.7 | 238.1 | 5 | 844.6 | 837.5 | 224.2 | 649.4 | 504.8 | 829.5 | 641.5 | 611.1 | 738.5 | 315 | 287.4 | 719.7 | 22.5 | 71.4 | 128.9 | 212.3 | 532.9 | 707.7 | 172.9 | 538.3 | 53.5 | 280.3 | 255.2 | 56.1 | 143.4 | 153.5 | 107.7
563 | 327 | 566.4 | 226.56 | 264.8356 | 277.2 | 275 | 258.8 | 109.6 | 555.3 | 30.3 | 20.1 | 66.2 | 4.2 | 249.1 | 5.4 | 848 | 825.7 | 224.5 | 650.6 | 507.7 | 831.3 | 644.1 | 614.8 | 741.6 | 316.7 | 287.9 | 718.8 | 22.6 | 71.8 | 129.6 | 213.4 | 533.1 | 707.2 | 173.4 | 538.3 | 53.6 | 279.8 | 255.7 | 56.4 | 143.9 | 154.2 | 108.1
564 | 328 | 565.1 | 226.04 | 264.2277 | 278 | 276.2 | 258.2 | 109.8 | 556.7 | 30.4 | 20.1 | 66.3 | 4.4 | 228.5 | 5.3 | 848.5 | 822.1 | 224.2 | 652.2 | 510.6 | 833.4 | 646.3 | 616.7 | 740.6 | 318.6 | 288.1 | 720.4 | 22.7 | 72.2 | 130 | 214.5 | 533.8 | 701.9 | 173.9 | 537.6 | 53.8 | 279.6 | 256 | 56.6 | 144.3 | 154.9 | 108.4
565 | 329 | 565.8 | 226.32 | 264.555 | 278.7 | 276.2 | 258.2 | 110 | 555.4 | 30.5 | 20.1 | 66.6 | 4.3 | 220.4 | 5.4 | 845.3 | 814.3 | 223.9 | 653.6 | 512.9 | 834.5 | 649.8 | 618.6 | 734.1 | 320.6 | 287.7 | 719.7 | 22.8 | 72.5 | 130.4 | 215.6 | 533.5 | 699.3 | 174.3 | 537.5 | 54 | 279.5 | 256.4 | 56.8 | 144.9 | 155.7 | 108.8
566 | 330 | 567.6 | 227.04 | 265.3967 | 279.7 | 275.7 | 258 | 110.3 | 556.1 | 30.5 | 20.1 | 66.7 | 4.2 | 218.2 | 5.3 | 835.3 | 803.8 | 222.2 | 654.9 | 514.9 | 835 | 652.1 | 616.8 | 733.8 | 322.5 | 287.6 | 719.5 | 22.9 | 72.9 | 131.1 | 216.6 | 533.3 | 690.5 | 174.8 | 536.9 | 54.2 | 279.8 | 256.4 | 57.1 | 145.2 | 156.4 | 109.1
567 | 331 | 565.4 | 226.16 | 264.368 | 280.6 | 274.5 | 257.8 | 110.5 | 554.4 | 30.6 | 20.1 | 66.9 | 4.2 | 213.5 | 5.4 | 819.2 | 788.7 | 219.7 | 656.7 | 517.6 | 835.8 | 655.1 | 614.5 | 729.5 | 324.5 | 287.8 | 719.3 | 22.9 | 73.2 | 131.9 | 217.7 | 531.9 | 688.2 | 175.3 | 534.8 | 54.4 | 280 | 256.2 | 57.3 | 145.5 | 157.1 | 109.5
568 | 332 | 566.7 | 226.68 | 264.9759 | 281.7 | 273.7 | 257.6 | 110.9 | 558.3 | 30.7 | 20.1 | 67.2 | 4.4 | 215.9 | 5.9 | 810.2 | 784.8 | 218.4 | 658.4 | 520 | 835.4 | 657 | 612.8 | 723.4 | 326.3 | 287.9 | 719 | 23 | 73.5 | 132.8 | 218.7 | 533 | 686.5 | 175.8 | 534 | 54.6 | 280.4 | 256.3 | 57.5 | 145.9 | 157.7 | 109.9
569 | 333 | 566.8 | 226.72 | 265.0226 | 282.2 | 273.1 | 259.5 | 111.3 | 558.5 | 30.7 | 20.1 | 67.4 | 4.1 | 217.8 | 5.3 | 809.8 | 792.2 | 217.4 | 659.6 | 522 | 834.3 | 659.4 | 610.4 | 721.5 | 328 | 288 | 718.2 | 23.1 | 73.8 | 133.1 | 219.7 | 531.4 | 683.8 | 176.3 | 536.4 | 54.8 | 280.7 | 256.4 | 57.8 | 146.2 | 158.4 | 110.3
570 | 334 | 566.9 | 226.76 | 265.0694 | 282.7 | 272.5 | 260.7 | 111.7 | 557.2 | 30.8 | 20.1 | 67.6 | 4.3 | 227.1 | 4.6 | 827.2 | 809.9 | 216.5 | 661.1 | 523.3 | 834.6 | 660.9 | 606.5 | 731.5 | 329.6 | 288.1 | 719.4 | 23.2 | 74.2 | 133.3 | 220.7 | 531.1 | 679.4 | 176.8 | 536.9 | 55 | 281.9 | 256.8 | 58 | 146.7 | 159 | 110.7
571 | 335 | 567.4 | 226.96 | 265.3032 | 283.1 | 271.7 | 260.9 | 112.2 | 548.1 | 30.8 | 20.1 | 67.6 | 4.1 | 232.7 | 4.5 | 846.1 | 820.7 | 215.3 | 662.1 | 525.3 | 836.9 | 662.4 | 602 | 738.3 | 331.2 | 288.2 | 721.7 | 23.3 | 74.5 | 133.5 | 221.6 | 528.9 | 670.6 | 177.2 | 536.2 | 55.1 | 281.5 | 256.5 | 58.2 | 147.2 | 159.7 | 111.1
572 | 336 | 568.9 | 227.56 | 266.0045 | 282.5 | 271.2 | 261.7 | 112.4 | 539.5 | 30.9 | 20 | 67.6 | 4 | 239.7 | 4.5 | 855.5 | 829.7 | 213.9 | 663.3 | 527.3 | 839.3 | 664.4 | 599.7 | 744.1 | 332.8 | 288.2 | 723.7 | 23.4 | 74.8 | 134 | 222.5 | 527.1 | 666.1 | 177.7 | 535.5 | 55.3 | 280.9 | 256.8 | 58.4 | 147.6 | 160.3 | 111.5
573 | 337 | 565.6 | 226.24 | 264.4615 | 283.3 | 271.2 | 262.4 | 112.7 | 533.4 | 30.9 | 20 | 67.9 | 3.8 | 230.4 | 4.7 | 869 | 837.4 | 213.2 | 664.9 | 529.1 | 841.4 | 667.9 | 597.1 | 745 | 334.5 | 288.2 | 725 | 23.5 | 75.1 | 134.6 | 223.4 | 524.6 | 659.4 | 178.1 | 535.1 | 55.5 | 280.9 | 256.9 | 58.6 | 148 | 160.9 | 111.8
574 | 338 | 565.9 | 226.36 | 264.6018 | 283 | 271.7 | 263.2 | 113 | 533.1 | 31 | 20 | 68 | 4.6 | 216.7 | 5.1 | 871.9 | 836.5 | 212.3 | 667.8 | 530.9 | 843.2 | 673 | 596.4 | 745.1 | 336 | 288.2 | 726.2 | 23.6 | 75.5 | 135.2 | 224.3 | 523.9 | 655.9 | 178.5 | 533.2 | 55.7 | 281.2 | 256.8 | 58.9 | 148.2 | 161.6 | 112.2
575 | 339 | 565.2 | 226.08 | 264.2745 | 284 | 271.6 | 263.2 | 113.4 | 532.8 | 31 | 20 | 68.1 | 4.6 | 212 | 5.9 | 874 | 842.5 | 212.2 | 670 | 532.8 | 844.2 | 675.8 | 595.4 | 746.8 | 337.6 | 288.3 | 727.3 | 23.7 | 75.8 | 135.4 | 225.2 | 524.6 | 652.1 | 179 | 533.1 | 55.9 | 281.4 | 256.8 | 59.1 | 148.5 | 162.2 | 112.6
576 | 340 | 565.9 | 226.36 | 264.6018 | 284.8 | 271.3 | 263.7 | 113.8 | 536.4 | 31.1 | 20 | 68.2 | 4.1 | 214.7 | 6.6 | 880.4 | 845.5 | 211.3 | 672.2 | 534.7 | 845.2 | 677.6 | 593.8 | 749.9 | 338.9 | 288.5 | 728.4 | 23.7 | 76.2 | 136.1 | 226.1 | 525.4 | 654.2 | 179.6 | 535.1 | 56.1 | 281.2 | 256.9 | 59.3 | 149 | 162.8 | 112.9
577 | 341 | 566.7 | 226.68 | 264.9759 | 285.9 | 271.1 | 262.1 | 114.2 | 539.2 | 31.1 | 20 | 68.3 | 4.5 | 209.4 | 6.9 | 881.4 | 849.2 | 210.4 | 675 | 536.7 | 846.5 | 678.6 | 592.7 | 754.9 | 340.3 | 288.8 | 729.5 | 23.8 | 76.6 | 136.5 | 227 | 525.9 | 648.7 | 180.1 | 534.8 | 56.3 | 281.6 | 257.5 | 59.5 | 149.3 | 163.4 | 113.3
578 | 342 | 566.1 | 226.44 | 264.6953 | 286 | 270.5 | 262 | 114.5 | 540 | 31.2 | 20 | 68.6 | 4.4 | 211.9 | 6.7 | 884.5 | 853.3 | 210.1 | 677.2 | 538.7 | 847.8 | 680 | 592.1 | 756.9 | 341.7 | 289.2 | 730.6 | 23.9 | 77 | 137 | 227.9 | 526.1 | 644 | 180.6 | 534.9 | 56.5 | 281.9 | 258.2 | 59.7 | 149.8 | 164 | 113.7
579 | 343 | 565.8 | 226.32 | 264.555 | 286.7 | 270.5 | 262.5 | 114.9 | 542.3 | 31.2 | 20 | 68.8 | 4 | 213.7 | 6.5 | 878.3 | 851.8 | 209.6 | 680.8 | 540.7 | 849 | 682.1 | 591.4 | 756.8 | 343 | 289.5 | 731.3 | 24 | 77.3 | 137.7 | 228.7 | 529.8 | 644.6 | 181.2 | 536.1 | 56.7 | 282.9 | 258.8 | 59.9 | 150.2 | 164.6 | 114
580 | 344 | 566.5 | 226.6 | 264.8823 | 287.1 | 270 | 264 | 115.4 | 548.5 | 31.3 | 20 | 68.9 | 4 | 211.3 | 6.3 | 875.4 | 852.4 | 209.1 | 683.2 | 541.2 | 849.5 | 685.6 | 591 | 757 | 344.2 | 289.7 | 729.7 | 24.1 | 77.7 | 138.3 | 229.5 | 531.4 | 648.4 | 181.8 | 536.2 | 56.8 | 283 | 258.9 | 60.2 | 150.5 | 165.3 | 114.5
581 | 345 | 566.4 | 226.56 | 264.8356 | 287.4 | 269.8 | 264.8 | 115.8 | 559.1 | 31.3 | 20 | 69 | 4.4 | 210.3 | 6.5 | 868.9 | 847 | 208.7 | 685.7 | 542.5 | 848.9 | 688.5 | 592.4 | 755 | 345.3 | 290.1 | 728.8 | 24.2 | 78 | 139.4 | 230.3 | 533.8 | 654.2 | 182.5 | 537.7 | 57 | 283.2 | 259.1 | 60.4 | 150.9 | 165.9 | 114.8
582 | 346 | 565.6 | 226.24 | 264.4615 | 288.3 | 270.1 | 265.5 | 116.3 | 568.8 | 31.4 | 20 | 69.2 | 3.9 | 213.1 | 5.6 | 871.1 | 849.1 | 208.5 | 687.7 | 543.5 | 848.6 | 692 | 593.6 | 752.9 | 346.6 | 290.4 | 727.5 | 24.3 | 78.3 | 140.3 | 231.1 | 536.9 | 662.5 | 183.2 | 540.9 | 57.2 | 284 | 259.4 | 60.6 | 151.3 | 166.6 | 115.2
583 | 347 | 567 | 226.8 | 265.1161 | 288.7 | 270.7 | 266.7 | 116.8 | 574.2 | 31.4 | 20 | 69.2 | 4.2 | 220.4 | 5.7 | 856.2 | 838.9 | 208.8 | 689.6 | 544.8 | 849 | 692 | 597.3 | 754.7 | 347.8 | 290.8 | 727.6 | 24.4 | 78.6 | 140.9 | 231.9 | 540.3 | 673 | 183.9 | 546.1 | 57.4 | 284.5 | 259.4 | 60.8 | 151.7 | 167.3 | 115.6
584 | 348 | 566.6 | 226.64 | 264.9291 | 289.2 | 271.2 | 267.8 | 117.3 | 581.2 | 31.5 | 20 | 69.4 | 3.8 | 232.1 | 5.2 | 835.9 | 816.6 | 208.8 | 691.9 | 545.9 | 848.2 | 692.7 | 599.9 | 745.4 | 349 | 291.2 | 727.6 | 24.5 | 79 | 141.7 | 232.6 | 543.6 | 673 | 184.7 | 545.2 | 57.6 | 285.7 | 259.3 | 61 | 152.1 | 168 | 116
585 | 349 | 566.2 | 226.48 | 264.7421 | 291 | 272.2 | 268 | 117.9 | 588.3 | 31.5 | 20 | 69.5 | 4.6 | 250.2 | 4.5 | 823.4 | 804 | 208.3 | 694.4 | 547.2 | 847.2 | 692.9 | 604.1 | 731.6 | 350.2 | 291.5 | 726 | 24.6 | 79.3 | 142.5 | 233.3 | 546.6 | 678.4 | 185.4 | 544.3 | 57.7 | 286.8 | 259.6 | 61.2 | 152.5 | 168.6 | 116.4
586 | 350 | 566.4 | 226.56 | 264.8356 | 293.1 | 272.9 | 270.5 | 118.5 | 598.5 | 31.6 | 20 | 69.8 | 4.3 | 218.6 | 4.1 | 814.3 | 800.5 | 208.1 | 696.8 | 548.4 | 845.5 | 693.6 | 607.7 | 716.3 | 351.3 | 291.9 | 723.1 | 24.7 | 79.6 | 143.5 | 234 | 551.8 | 682 | 186 | 547.9 | 57.9 | 287.9 | 260.1 | 61.5 | 152.9 | 169.3 | 116.8
587 | 351 | 566.5 | 226.6 | 264.8823 | 294.6 | 273.3 | 272.4 | 119.2 | 608.2 | 31.7 | 20 | 69.9 | 4.2 | 187.5 | 4.8 | 817.7 | 807.9 | 208.2 | 699.4 | 549.3 | 843.8 | 692.7 | 608.4 | 715.3 | 352.3 | 292.4 | 721.9 | 24.8 | 80 | 144.5 | 234.7 | 555.6 | 688 | 186.7 | 548.1 | 58.1 | 288.7 | 260.5 | 61.7 | 153.5 | 170 | 117.3
588 | 352 | 565.9 | 226.36 | 264.6018 | 295.8 | 274.1 | 274.7 | 119.9 | 616 | 31.8 | 20 | 70.1 | 4.4 | 185.4 | 4.2 | 810.6 | 797.8 | 208.3 | 701.5 | 550.2 | 842.6 | 691.2 | 609 | 711 | 353.2 | 292.8 | 721.7 | 24.9 | 80.3 | 145.3 | 235.4 | 560.9 | 690.9 | 187.4 | 549.1 | 58.3 | 289.8 | 261.8 | 61.9 | 154.1 | 170.7 | 117.7
589 | 353 | 566 | 226.4 | 264.6486 | 297.7 | 274.5 | 276.3 | 120.6 | 619.1 | 31.9 | 20 | 70.2 | 4.3 | 222.9 | 3.5 | 799.1 | 790.8 | 208.3 | 704.5 | 551.2 | 841.1 | 692.5 | 607.4 | 704.3 | 354.5 | 293.1 | 719.6 | 25 | 80.7 | 145.8 | 236.1 | 562.8 | 688.9 | 188.1 | 549.8 | 58.5 | 290.7 | 263.2 | 62.2 | 154.6 | 171.4 | 118.2
590 | 354 | 567.4 | 226.96 | 265.3032 | 298.6 | 274.9 | 279.5 | 121.2 | 618.8 | 31.9 | 20 | 70.3 | 4.7 | 243.2 | 3.6 | 803.5 | 795.5 | 207.6 | 705.8 | 551.8 | 840.5 | 692 | 606.7 | 704.9 | 355.6 | 293.5 | 718.6 | 25.1 | 81.1 | 146.4 | 236.7 | 564 | 690.2 | 188.7 | 548.7 | 58.6 | 291.7 | 264.3 | 62.4 | 155.1 | 172.1 | 118.7
591 | 355 | 567.7 | 227.08 | 265.4434 | 299.5 | 276.2 | 281.8 | 121.8 | 624.4 | 32 | 20 | 70.4 | 4.7 | 215.8 | 4.3 | 794.9 | 781.2 | 207.4 | 707.1 | 552.6 | 839.3 | 692.5 | 609.2 | 704 | 357 | 293.8 | 718.5 | 25.1 | 81.5 | 147.6 | 237.4 | 567.8 | 701.9 | 189.4 | 552.2 | 58.8 | 292.9 | 264.4 | 62.6 | 155.7 | 172.8 | 119.1
592 | 356 | 568.3 | 227.32 | 265.724 | 300.4 | 277.4 | 282.5 | 122.5 | 631.8 | 32 | 19.9 | 70.5 | 4.6 | 229.7 | 4.6 | 784.5 | 773.4 | 207.1 | 708.7 | 553.3 | 837.7 | 695.5 | 610.9 | 697.2 | 357.9 | 294.2 | 718.2 | 25.2 | 81.8 | 148.2 | 238 | 571 | 704.4 | 190.1 | 556 | 59 | 294.6 | 264.7 | 62.9 | 156.1 | 173.5 | 119.6
593 | 357 | 566.2 | 226.48 | 264.7421 | 302.1 | 277.9 | 283.1 | 123 | 634.4 | 32.1 | 19.9 | 70.6 | 4.7 | 225.3 | 4.7 | 766.8 | 759.4 | 206.4 | 710.7 | 553.9 | 836.1 | 697 | 611.1 | 696.1 | 359.1 | 294.7 | 717 | 25.4 | 82.2 | 148.8 | 238.7 | 572.1 | 698.9 | 190.7 | 554.9 | 59.2 | 296.3 | 266 | 63.1 | 156.5 | 174.3 | 120.1
594 | 358 | 564.6 | 225.84 | 263.9939 | 304.1 | 277.8 | 284.5 | 123.6 | 635 | 32.2 | 20 | 70.8 | 4.9 | 228.1 | 4.4 | 762 | 757.2 | 206.2 | 713.3 | 554.3 | 833.9 | 699.1 | 610.5 | 692.2 | 360.4 | 295.1 | 716.1 | 25.4 | 82.6 | 149.3 | 239.3 | 573.8 | 696.4 | 191.3 | 556.3 | 59.3 | 297.2 | 267.6 | 63.4 | 157 | 175 | 120.6
595 | 359 | 565.2 | 226.08 | 264.2745 | 306.2 | 277.7 | 286.2 | 124.2 | 638.1 | 32.2 | 20 | 71 | 4.8 | 236.2 | 4 | 767.5 | 756.8 | 205.7 | 715.2 | 554.5 | 832.3 | 703.8 | 612.4 | 690.8 | 361.7 | 295.6 | 714.5 | 25.6 | 83 | 150 | 240 | 576.1 | 706.4 | 192 | 558.7 | 59.5 | 297.8 | 269 | 63.6 | 157.7 | 175.7 | 121
596 | 360 | 564.7 | 225.88 | 264.0407 | 308.4 | 278.2 | 288.4 | 124.6 | 637.6 | 32.3 | 20 | 71.3 | 4.5 | 236.7 | 4.4 | 758.4 | 750.6 | 205.7 | 717.2 | 554.8 | 830.6 | 705.6 | 614 | 690.7 | 362.9 | 296.2 | 715.4 | 25.7 | 83.4 | 150.8 | 240.6 | 576.6 | 701.4 | 192.7 | 561.3 | 59.7 | 300.3 | 269.7 | 63.9 | 158.1 | 176.4 | 121.5
597 | 361 | 565.7 | 226.28 | 264.5083 | 309.1 | 279 | 291.3 | 124.9 | 638.8 | 32.3 | 19.9 | 71.5 | 4.7 | 204.9 | 4.8 | 757.6 | 744.3 | 205.6 | 718.9 | 555 | 829.4 | 706 | 613.3 | 693.8 | 364.1 | 296.7 | 714.6 | 25.8 | 83.8 | 151.8 | 241.3 | 576.9 | 700.3 | 193.4 | 559.2 | 59.9 | 301.1 | 270.1 | 64.1 | 158.6 | 177.1 | 121.9
598 | 362 | 566.1 | 226.44 | 264.6953 | 309.8 | 279.8 | 292.7 | 125.3 | 638.3 | 32.4 | 19.9 | 71.8 | 4.3 | 202.7 | 5.3 | 771.5 | 754.6 | 205.8 | 720.4 | 555.6 | 830.8 | 705.6 | 618.8 | 699.1 | 365.3 | 297.3 | 716.9 | 25.9 | 84.2 | 152.5 | 241.9 | 579.3 | 702 | 194.1 | 562.2 | 60.1 | 301.3 | 270.1 | 64.4 | 159.1 | 177.8 | 122.4
599 | 363 | 564 | 225.6 | 263.7134 | 310.7 | 280.2 | 293.3 | 125.7 | 626.3 | 32.5 | 20 | 72 | 4.5 | 209.4 | 5.1 | 786.9 | 770.9 | 205.4 | 721.8 | 556.5 | 832.5 | 707.1 | 620 | 702.2 | 366.5 | 297.9 | 719 | 26 | 84.5 | 152.5 | 242.6 | 579 | 697.4 | 194.7 | 561.5 | 60.2 | 301.1 | 271.5 | 64.7 | 159.6 | 178.5 | 122.8
600 | 364 | 564 | 225.6 | 263.7134 | 309.6 | 280.8 | 293.7 | 126 | 615.7 | 32.6 | 19.9 | 72.1 | 4.5 | 235.9 | 5.1 | 801.8 | 785.6 | 204.8 | 723 | 557.6 | 834.6 | 709.2 | 617.3 | 708.2 | 367.7 | 298.5 | 720.3 | 26.1 | 84.9 | 152.8 | 243.3 | 578.4 | 697.9 | 195.4 | 561.1 | 60.4 | 300.5 | 272.3 | 64.9 | 160.2 | 179.2 | 123.3
601 | 365 | 564 | 225.6 | 263.7134 | 308.6 | 281.5 | 292.6 | 126.3 | 609.4 | 32.7 | 19.9 | 72.2 | 5 | 227.9 | 6 | 820.9 | 803.8 | 204.1 | 724.4 | 558.1 | 836.5 | 712.1 | 612.7 | 717.5 | 368.5 | 299.1 | 722.3 | 26.2 | 85.2 | 153 | 244 | 577.7 | 693 | 196 | 561.1 | 60.6 | 300.3 | 272.6 | 65.2 | 160.8 | 179.9 | 123.7
602 | 366 | 565.3 | 226.12 | 264.3213 | 308.6 | 282 | 290.7 | 126.6 | 599.8 | 32.7 | 19.9 | 72.6 | 4.8 | 204.4 | 6.5 | 838.1 | 817 | 203.5 | 725.5 | 559.3 | 837.9 | 714.3 | 608.6 | 732.8 | 369.2 | 299.8 | 724.1 | 26.3 | 85.6 | 153.3 | 244.8 | 576.6 | 690.9 | 196.6 | 562.3 | 60.8 | 300.3 | 272.8 | 65.4 | 161.3 | 180.6 | 124.1
603 | 367 | 566.2 | 226.48 | 264.7421 | 309.8 | 282.9 | 288.8 | 126.9 | 591.6 | 32.9 | 19.9 | 72.9 | 4.8 | 221.3 | 6.5 | 852.6 | 833.1 | 203.6 | 726.3 | 560.8 | 839 | 715.5 | 606.8 | 742.7 | 370.1 | 300.4 | 726.3 | 26.4 | 86 | 153.7 | 245.5 | 573.3 | 685.9 | 197.2 | 562.2 | 61 | 300.5 | 272.9 | 65.7 | 161.6 | 181.4 | 124.5
604 | 368 | 565.1 | 226.04 | 264.2277 | 309.4 | 285.1 | 286.4 | 127.2 | 585.4 | 33 | 19.9 | 72.9 | 4.4 | 235.1 | 5.2 | 861.1 | 840.1 | 203.4 | 727.3 | 561.8 | 840.9 | 717 | 604.4 | 751 | 371.1 | 301.2 | 728.2 | 26.5 | 86.4 | 154 | 246.2 | 569.5 | 682 | 197.8 | 562.2 | 61.1 | 300.1 | 272.9 | 65.9 | 161.9 | 182.1 | 124.9
605 | 369 | 565.2 | 226.08 | 264.2745 | 309.2 | 286.3 | 283.7 | 127.6 | 576.4 | 33.1 | 19.9 | 73.1 | 4.3 | 248.1 | 5 | 867.7 | 848.3 | 202.8 | 727.9 | 562.5 | 842.6 | 718.8 | 601.3 | 754.9 | 372.2 | 301.9 | 730.2 | 26.6 | 86.8 | 154.2 | 246.8 | 566 | 674.2 | 198.4 | 561.4 | 61.3 | 300.1 | 273.9 | 66.2 | 162.3 | 182.8 | 125.3
606 | 370 | 565.2 | 226.08 | 264.2745 | 309.6 | 286.4 | 281.3 | 128 | 573.8 | 33.2 | 19.9 | 73.2 | 4.2 | 252.6 | 4.7 | 871.2 | 846.4 | 202.6 | 728.7 | 564.1 | 844.7 | 721.5 | 600.1 | 757.1 | 373.3 | 302.6 | 732 | 26.7 | 87.2 | 154.6 | 247.4 | 565.6 | 676.8 | 198.9 | 565.8 | 61.5 | 299.7 | 274.9 | 66.4 | 163 | 183.5 | 125.7
607 | 371 | 565.5 | 226.2 | 264.4148 | 309.9 | 286.6 | 280.8 | 128.5 | 571.2 | 33.3 | 19.9 | 73.2 | 3.9 | 227.8 | 3.9 | 871 | 846.7 | 202.9 | 729.4 | 565 | 846.2 | 724.1 | 599.1 | 759.4 | 374.3 | 303.3 | 733.3 | 26.8 | 87.6 | 155.2 | 247.9 | 562.1 | 668.8 | 199.5 | 561.8 | 61.7 | 300.1 | 275 | 66.7 | 163.4 | 184.2 | 126.1
608 | 372 | 565.4 | 226.16 | 264.368 | 309.7 | 286.3 | 280.1 | 128.9 | 571.9 | 33.4 | 19.9 | 73.2 | 4 | 219 | 3.5 | 871.1 | 850.8 | 203 | 730.4 | 565.6 | 847.5 | 726.5 | 598.1 | 762 | 375.3 | 304 | 734 | 26.9 | 88 | 155.8 | 248.3 | 559.9 | 666.1 | 200 | 559.3 | 61.9 | 299.6 | 275 | 66.9 | 163.6 | 184.9 | 126.5
609 | 373 | 565.3 | 226.12 | 264.3213 | 308.6 | 286 | 279.9 | 129.1 | 576.6 | 33.4 | 19.9 | 73.1 | 4.2 | 254.9 | 3.5 | 878.2 | 851.8 | 203.5 | 731.2 | 566.8 | 848.3 | 727.2 | 597.9 | 763.7 | 376.3 | 304.7 | 735.6 | 27 | 88.5 | 156 | 248.8 | 558.8 | 668.4 | 200.6 | 559.6 | 62.1 | 299.3 | 274.8 | 67.2 | 164 | 185.6 | 126.9
610 | 374 | 565.1 | 226.04 | 264.2277 | 308.6 | 286.3 | 279 | 129.5 | 575.9 | 33.5 | 19.9 | 73.1 | 4.6 | 253.4 | 3.9 | 880.8 | 858.7 | 203.9 | 732 | 567.9 | 850.1 | 729.5 | 597.5 | 764.6 | 377.3 | 305.4 | 736.9 | 27.2 | 88.9 | 156.7 | 249.4 | 557 | 668.3 | 201.1 | 561.4 | 62.2 | 298.8 | 274.7 | 67.4 | 164.3 | 186.3 | 127.3
611 | 375 | 565.3 | 226.12 | 264.3213 | 306.9 | 286.6 | 278.4 | 129.9 | 577.7 | 33.6 | 19.9 | 73.2 | 4.1 | 249.4 | 4.4 | 879.3 | 864.6 | 204.3 | 732.7 | 568.7 | 851.9 | 732.2 | 596.9 | 763.9 | 378.2 | 306.2 | 737.3 | 27.3 | 89.4 | 157.2 | 250.1 | 555.2 | 667.8 | 201.7 | 562.2 | 62.4 | 298.6 | 274.8 | 67.7 | 164.7 | 186.9 | 127.7
612 | 376 | 565.2 | 226.08 | 264.2745 | 306.9 | 287.4 | 278.6 | 130.4 | 579.6 | 33.6 | 19.9 | 73.2 | 4.1 | 251.7 | 4.9 | 873.4 | 865.2 | 204.5 | 732.4 | 568.8 | 853.2 | 734.7 | 598.2 | 767.9 | 379.1 | 307 | 738.2 | 27.4 | 89.8 | 157.9 | 250.7 | 553.9 | 674.4 | 202.2 | 565.9 | 62.6 | 298 | 275 | 67.9 | 165 | 187.6 | 128.1
613 | 377 | 565.7 | 226.28 | 264.5083 | 307.1 | 287.2 | 278.5 | 130.8 | 582.1 | 33.8 | 19.9 | 73.3 | 4.3 | 243.8 | 5 | 870.6 | 857.4 | 204.7 | 732.5 | 569.7 | 853.5 | 737 | 599.5 | 773.9 | 379.8 | 307.6 | 739.5 | 27.5 | 90.2 | 158.4 | 251.4 | 553.7 | 681.6 | 202.7 | 570.6 | 62.8 | 297.3 | 275.1 | 68.2 | 165.4 | 188.3 | 128.5
614 | 378 | 565.9 | 226.36 | 264.6018 | 307.1 | 286.6 | 278.9 | 131.3 | 584.7 | 34 | 19.9 | 73.3 | 4.4 | 236.7 | 4.6 | 875.2 | 854.4 | 205.3 | 733.4 | 570.7 | 854 | 739 | 600.6 | 778 | 380.6 | 308.4 | 740.9 | 27.6 | 90.6 | 159 | 252 | 553.4 | 682.1 | 203.2 | 569.9 | 63 | 297.2 | 274.4 | 68.4 | 165.7 | 189 | 128.8
615 | 379 | 565.7 | 226.28 | 264.5083 | 306.6 | 286.2 | 277.7 | 131.7 | 587.6 | 34.1 | 19.9 | 73.5 | 4.3 | 253.6 | 4.4 | 879.2 | 848.4 | 205.8 | 734.3 | 571.2 | 855.3 | 742.5 | 601.4 | 775.7 | 381.3 | 309.2 | 740.6 | 27.7 | 90.9 | 159.4 | 252.6 | 554 | 679.1 | 203.7 | 567.7 | 63.1 | 297 | 274.5 | 68.7 | 166.1 | 189.7 | 129.2
616 | 380 | 565.5 | 226.2 | 264.4148 | 307.2 | 286.1 | 278.1 | 132.2 | 585.8 | 34.3 | 19.9 | 73.5 | 4.5 | 235.8 | 4.7 | 877.5 | 839.7 | 206.1 | 735.2 | 572.5 | 856.2 | 743.9 | 601.2 | 777.1 | 381.9 | 309.9 | 742.7 | 27.8 | 91.3 | 159.8 | 253 | 554.2 | 678.6 | 204.2 | 567.3 | 63.3 | 296.8 | 274 | 68.9 | 166.6 | 190.4 | 129.6
617 | 381 | 566.4 | 226.56 | 264.8356 | 308.2 | 285.7 | 278.1 | 132.8 | 582.2 | 34.4 | 19.8 | 73.4 | 4.7 | 214.4 | 5.3 | 877.2 | 842.1 | 206.2 | 736.4 | 573.4 | 857.6 | 745.1 | 601.6 | 775.8 | 382.6 | 310.5 | 743.7 | 28 | 91.7 | 160 | 253.6 | 554.9 | 682 | 204.7 | 569.5 | 63.5 | 296.5 | 273.7 | 69.2 | 167 | 191 | 130
618 | 382 | 565 | 226 | 264.181 | 307.7 | 285.1 | 277.6 | 133.4 | 582.7 | 34.5 | 19.8 | 73.4 | 4.9 | 211.3 | 5.2 | 870.7 | 833.7 | 206.2 | 737.3 | 574.5 | 859 | 747.1 | 603.6 | 770.6 | 383.3 | 311.2 | 745.1 | 28.1 | 92 | 160.4 | 254.2 | 555.2 | 686.2 | 205.2 | 571.4 | 63.7 | 297.3 | 274 | 69.4 | 167.4 | 191.7 | 130.4
619 | 383 | 564.9 | 225.96 | 264.1342 | 307 | 284.6 | 277.3 | 133.9 | 578.7 | 34.7 | 19.8 | 73.5 | 5 | 216.4 | 5.7 | 876.5 | 837.3 | 206.1 | 738.3 | 575.7 | 859.6 | 749.5 | 607.2 | 771.2 | 383.9 | 311.9 | 746.5 | 28.2 | 92.4 | 160.5 | 254.8 | 556.1 | 677.3 | 205.7 | 568.7 | 63.9 | 297.8 | 274.1 | 69.7 | 167.9 | 192.4 | 130.8
620 | 384 | 566.8 | 226.72 | 265.0226 | 308.5 | 284.6 | 278 | 134.6 | 576.2 | 34.8 | 19.8 | 73.6 | 5 | 212 | 6.2 | 881.6 | 840.1 | 205 | 738.6 | 576.7 | 860.2 | 750.4 | 608.4 | 773.3 | 384.4 | 312.5 | 746.8 | 28.3 | 92.8 | 160.6 | 255.5 | 557.9 | 672.8 | 206.1 | 567.4 | 64.1 | 298.5 | 274.1 | 70 | 168.3 | 193.1 | 131.2
621 | 385 | 566 | 226.4 | 264.6486 | 308.8 | 285.1 | 277.9 | 135.3 | 576 | 35 | 19.8 | 73.7 | 5.3 | 215.1 | 6.2 | 886.2 | 848.9 | 203.8 | 739.4 | 578 | 861 | 749.2 | 612.5 | 775 | 384.9 | 313.2 | 746.9 | 28.4 | 93.2 | 161.2 | 256 | 559.7 | 679.4 | 206.6 | 569.4 | 64.2 | 298.7 | 274.6 | 70.2 | 168.8 | 193.8 | 131.7
622 | 386 | 565 | 226 | 264.181 | 309.4 | 286.6 | 277.4 | 136 | 576.9 | 35.1 | 19.8 | 73.9 | 5.1 | 238 | 5.3 | 883.8 | 854.3 | 203.2 | 740.2 | 579.4 | 861.4 | 747.2 | 612.8 | 779.2 | 385.4 | 313.8 | 746.5 | 28.5 | 93.6 | 161.7 | 256.7 | 558.6 | 681 | 207.1 | 572.6 | 64.4 | 298.4 | 274.9 | 70.5 | 169.4 | 194.5 | 132.1
623 | 387 | 566 | 226.4 | 264.6486 | 310.8 | 287.2 | 277.2 | 136.5 | 578.1 | 35.2 | 19.8 | 74.2 | 4.7 | 223.7 | 4.6 | 884.8 | 857.5 | 203.3 | 741.5 | 580.9 | 862 | 747.5 | 613 | 773.9 | 386 | 314.6 | 744.7 | 28.6 | 93.9 | 162.4 | 257.3 | 556.9 | 684 | 207.6 | 574.5 | 64.6 | 298.2 | 275.2 | 70.7 | 169.9 | 195.3 | 132.5
624 | 388 | 565.7 | 226.28 | 264.5083 | 309.9 | 287.5 | 276.8 | 136.9 | 581.9 | 35.3 | 19.8 | 74.4 | 4.9 | 223.5 | 4.9 | 882.6 | 857.8 | 203.4 | 742.4 | 581.5 | 862.3 | 747.8 | 612.9 | 774.4 | 386.6 | 315.4 | 745 | 28.8 | 94.3 | 163 | 258 | 555.6 | 687.4 | 208.1 | 572.5 | 64.8 | 297.9 | 275.9 | 71 | 170.4 | 196 | 132.9
625 | 389 | 564.5 | 225.8 | 263.9472 | 309.4 | 287.4 | 277 | 137.3 | 586.4 | 35.3 | 19.8 | 74.5 | 4.6 | 223.2 | 4.9 | 883.6 | 858.3 | 203.7 | 742.7 | 582.5 | 861.6 | 747.5 | 612.5 | 779.9 | 387.2 | 316.1 | 745.5 | 28.9 | 94.7 | 163.8 | 258.6 | 557.6 | 693.5 | 208.6 | 574.5 | 65 | 297.3 | 276.6 | 71.3 | 170.8 | 196.8 | 133.3
626 | 390 | 563.7 | 225.48 | 263.5731 | 308.9 | 287.2 | 278.7 | 137.8 | 600 | 35.4 | 19.8 | 74.7 | 4.5 | 236.7 | 4.7 | 870.1 | 849.6 | 204.2 | 743 | 583.5 | 860.4 | 750.8 | 614.2 | 774.2 | 387.8 | 317 | 744.4 | 29 | 95.1 | 165.2 | 259.2 | 562 | 703.4 | 209.1 | 578.9 | 65.2 | 297.5 | 276.4 | 71.5 | 171.1 | 197.5 | 133.6
627 | 391 | 565.4 | 226.16 | 264.368 | 309.8 | 287.4 | 280.8 | 138.2 | 619.1 | 35.5 | 19.8 | 74.8 | 4.6 | 245.8 | 5 | 856.8 | 842.2 | 204.7 | 744.2 | 584.5 | 858.4 | 753.4 | 617.6 | 763.3 | 388.7 | 318 | 742.3 | 29.1 | 95.4 | 166.1 | 259.8 | 566 | 708.6 | 209.5 | 581.9 | 65.3 | 298.5 | 276.2 | 71.8 | 171.3 | 198.3 | 134
628 | 392 | 565.5 | 226.2 | 264.4148 | 311.9 | 287.4 | 283.6 | 138.8 | 632.3 | 35.6 | 19.8 | 75 | 4.4 | 264.3 | 5.5 | 849.4 | 832 | 205.1 | 745.9 | 585 | 857 | 752.7 | 619.9 | 755.9 | 389.5 | 319.1 | 741.7 | 29.3 | 95.8 | 166.6 | 260.3 | 568.8 | 717.7 | 210 | 584.7 | 65.5 | 299.6 | 276 | 72 | 171.5 | 199 | 134.4
629 | 393 | 564.9 | 225.96 | 264.1342 | 312.6 | 287.4 | 285.8 | 139.6 | 637.3 | 35.6 | 19.8 | 75.1 | 4 | 252.3 | 6.5 | 837.2 | 816.7 | 205.3 | 747.5 | 585.3 | 856.2 | 753.9 | 621.4 | 746.2 | 390.1 | 320.2 | 740.1 | 29.4 | 96.2 | 167.2 | 260.9 | 570.6 | 722.7 | 210.6 | 589.2 | 65.7 | 301 | 276 | 72.3 | 171.9 | 199.8 | 134.8
630 | 394 | 564.8 | 225.92 | 264.0875 | 313.5 | 288.4 | 288.1 | 140.3 | 641.1 | 35.7 | 19.8 | 75.2 | 4.2 | 242.5 | 7.1 | 831 | 803.6 | 205.4 | 749.2 | 585.1 | 854.7 | 756.1 | 624.5 | 733.8 | 390.8 | 321.4 | 738.1 | 29.5 | 96.6 | 168 | 261.4 | 572 | 725.2 | 211.1 | 593.1 | 65.9 | 301.9 | 276.3 | 72.6 | 172.3 | 200.6 | 135.3
631 | 395 | 564.6 | 225.84 | 263.9939 | 313.9 | 289.2 | 289.4 | 140.9 | 646.2 | 35.8 | 19.8 | 75.3 | 4.5 | 232 | 7.5 | 819.5 | 792.8 | 204.9 | 750.8 | 584.8 | 853.2 | 757.2 | 626.7 | 728.9 | 391.5 | 322.5 | 738.3 | 29.6 | 97 | 169 | 262 | 573.7 | 723.2 | 211.6 | 591.3 | 66.1 | 302.6 | 276.7 | 72.8 | 172.8 | 201.4 | 135.7
632 | 396 | 564.7 | 225.88 | 264.0407 | 314.4 | 288.8 | 291.6 | 141.7 | 647.4 | 35.9 | 19.8 | 75.5 | 4.6 | 236.1 | 7.4 | 814.7 | 788 | 204.6 | 752.8 | 584.9 | 852.8 | 759.2 | 629 | 724.3 | 392.2 | 323.7 | 738.9 | 29.8 | 97.4 | 169 | 262.6 | 574.8 | 716.1 | 212.1 | 590.7 | 66.3 | 303.2 | 277.7 | 73.1 | 173.3 | 202.2 | 136.1
633 | 397 | 565 | 226 | 264.181 | 316.3 | 287.8 | 293.5 | 142.2 | 642.7 | 36 | 19.8 | 75.6 | 4.3 | 225.9 | 7.3 | 811.6 | 793.5 | 204.3 | 755 | 585.1 | 852.3 | 762 | 630 | 722.2 | 392.9 | 324.9 | 739.3 | 29.9 | 97.8 | 169.3 | 263.2 | 575.4 | 711.6 | 212.6 | 589.5 | 66.5 | 303.4 | 278.8 | 73.4 | 173.9 | 203 | 136.5
634 | 398 | 565.5 | 226.2 | 264.4148 | 318.2 | 286.6 | 293.6 | 142.8 | 640.2 | 36.1 | 19.8 | 75.8 | 4.6 | 229.8 | 6.7 | 810.7 | 797.7 | 204.4 | 757.3 | 585.3 | 852.5 | 762 | 631.2 | 726.1 | 393.7 | 326.2 | 740 | 30 | 98.1 | 169.8 | 263.7 | 575.3 | 711 | 213.1 | 589.1 | 66.7 | 303.5 | 278.8 | 73.6 | 174.5 | 203.7 | 137
635 | 399 | 565.3 | 226.12 | 264.3213 | 318.9 | 286.4 | 293.9 | 143.2 | 641.4 | 36.2 | 19.8 | 76 | 4.6 | 226.9 | 6.3 | 806.4 | 800 | 204.4 | 759.7 | 585.3 | 852.1 | 759.3 | 631.9 | 731.8 | 394.2 | 327.4 | 740 | 30.1 | 98.5 | 170.5 | 264.2 | 576.8 | 720.1 | 213.6 | 593.4 | 66.9 | 303.1 | 279.1 | 73.9 | 175 | 204.4 | 137.3
636 | 400 | 565.6 | 226.24 | 264.4615 | 318.5 | 286.5 | 293.9 | 143.4 | 644 | 36.3 | 19.8 | 76.2 | 4.6 | 233.1 | 6.4 | 807.7 | 791.3 | 204.2 | 762.4 | 585.5 | 851.5 | 756.4 | 633 | 734 | 395 | 328.5 | 740.1 | 30.3 | 98.9 | 171.2 | 264.6 | 576.5 | 724.5 | 214 | 595.3 | 67.1 | 302.8 | 278.9 | 74.2 | 175.3 | 205.2 | 137.7
637 | 401 | 565.2 | 226.08 | 264.2745 | 318.1 | 286.8 | 293.6 | 143.7 | 641.3 | 36.5 | 19.8 | 76.4 | 4.7 | 233.8 | 5.8 | 803.2 | 775.8 | 203.5 | 764.4 | 585.2 | 851.7 | 755.1 | 632 | 720 | 395.8 | 329.8 | 739.2 | 30.4 | 99.4 | 171.6 | 265 | 576.7 | 732.2 | 214.5 | 597.7 | 67.3 | 302.9 | 278.9 | 74.5 | 175.6 | 205.9 | 138.1
638 | 402 | 565.2 | 226.08 | 264.2745 | 319.6 | 288 | 293.5 | 144.2 | 637.4 | 36.5 | 19.8 | 76.5 | 4.4 | 241.3 | 5.3 | 779.3 | 754.9 | 202.4 | 765.6 | 584.3 | 850.5 | 758.1 | 631 | 705.4 | 396.5 | 330.9 | 737 | 30.5 | 99.8 | 171.7 | 265.4 | 577.9 | 727.3 | 215 | 599.2 | 67.5 | 302.9 | 278.9 | 74.8 | 176.2 | 206.7 | 138.5
639 | 403 | 564.8 | 225.92 | 264.0875 | 321.3 | 290 | 294.1 | 144.7 | 633.5 | 36.6 | 19.8 | 76.7 | 4.8 | 248.6 | 4.5 | 772.9 | 746.3 | 201.3 | 766.6 | 583.5 | 847.7 | 763.2 | 631.2 | 694 | 397.3 | 332 | 733.5 | 30.6 | 100.2 | 172.1 | 265.9 | 577.1 | 725.5 | 215.5 | 599.4 | 67.7 | 304.6 | 279 | 75 | 176.5 | 207.5 | 138.9
640 | 404 | 564.7 | 225.88 | 264.0407 | 322.3 | 290.6 | 295.6 | 145.3 | 638 | 36.7 | 19.8 | 76.7 | 4.4 | 233.2 | 4.5 | 775.9 | 749.9 | 200.5 | 767.6 | 582.6 | 846.2 | 767.4 | 632.7 | 687.1 | 398.5 | 334.1 | 733.2 | 30.8 | 100.6 | 172.8 | 266.3 | 576.9 | 726 | 215.9 | 600.6 | 67.9 | 308.4 | 280.1 | 75.3 | 176.9 | 208.3 | 139.3
641 | 405 | 565.6 | 226.24 | 264.4615 | 322.7 | 290 | 297.5 | 146.2 | 638.6 | 36.9 | 19.8 | 76.9 | 4.9 | 223 | 4.6 | 793.8 | 773.9 | 199.8 | 768.6 | 581.8 | 846 | 771.3 | 631.2 | 689 | 399.3 | 336.6 | 735.6 | 30.9 | 101 | 172.9 | 266.7 | 577.3 | 717.5 | 216.3 | 596.9 | 68.1 | 312.3 | 281.9 | 75.6 | 177.6 | 209 | 139.8
642 | 406 | 565.2 | 226.08 | 264.2745 | 324.3 | 289.2 | 298.5 | 147.1 | 631.6 | 37 | 19.8 | 77.1 | 5.2 | 238.3 | 4.5 | 818.2 | 794.5 | 199.1 | 769.1 | 581.7 | 847.1 | 771.8 | 628.4 | 701.5 | 400 | 338.1 | 737.7 | 31 | 101.4 | 173.2 | 267.2 | 577.4 | 716 | 216.6 | 595.6 | 68.3 | 312.8 | 282.6 | 75.9 | 178.1 | 209.7 | 140.4
643 | 407 | 564.7 | 225.88 | 264.0407 | 325.8 | 289.8 | 298 | 148 | 623.9 | 37.1 | 19.8 | 77.2 | 5 | 244.4 | 4.6 | 834.8 | 813.6 | 198.5 | 769.5 | 582.4 | 848.8 | 771.6 | 625 | 721.6 | 400.8 | 339.3 | 740.3 | 31.1 | 101.8 | 173.5 | 267.5 | 577.7 | 713.7 | 217 | 597.7 | 68.5 | 313.6 | 283.7 | 76.2 | 178.7 | 210.4 | 140.9
644 | 408 | 564.9 | 225.96 | 264.1342 | 326.5 | 289.5 | 297.6 | 148.9 | 618.4 | 37.2 | 19.7 | 77.2 | 4.7 | 236 | 4.6 | 847.6 | 827 | 198.4 | 769.3 | 583.5 | 849.6 | 773.3 | 623.3 | 735.7 | 401.6 | 340.5 | 742.2 | 31.3 | 102.2 | 174.2 | 267.8 | 578.1 | 711.5 | 217.3 | 596.7 | 68.7 | 313.1 | 284.1 | 76.4 | 179.1 | 211.2 | 141.3
645 | 409 | 566.1 | 226.44 | 264.6953 | 327.4 | 289.8 | 297.7 | 149.3 | 609.3 | 37.3 | 19.7 | 77.4 | 5 | 246.3 | 4.3 | 857.3 | 834.3 | 197.8 | 769.4 | 584.5 | 851.2 | 774 | 620.8 | 738 | 402.7 | 341.6 | 742.8 | 31.4 | 102.6 | 174.8 | 268.2 | 576.8 | 710.9 | 217.6 | 594.5 | 68.9 | 313 | 284.3 | 76.7 | 179.5 | 211.9 | 141.7
646 | 410 | 566.4 | 226.56 | 264.8356 | 328.4 | 291.4 | 297.5 | 149.7 | 601.2 | 37.4 | 19.7 | 77.6 | 5.1 | 255.3 | 4 | 856.4 | 835.2 | 196.9 | 769.9 | 585 | 852.9 | 776 | 624.3 | 731.8 | 403.5 | 342.9 | 742.7 | 31.5 | 103 | 174.9 | 268.7 | 576 | 712.8 | 218 | 601.3 | 69.1 | 313.1 | 284.8 | 77 | 180 | 212.7 | 142.1
647 | 411 | 565.8 | 226.32 | 264.555 | 328.7 | 292.5 | 297.6 | 150.2 | 593.8 | 37.6 | 19.7 | 77.7 | 4.4 | 256.1 | 4.1 | 864.7 | 840.1 | 195.4 | 770.7 | 586 | 854.1 | 779.2 | 627.1 | 738.3 | 404.1 | 343.7 | 743.3 | 31.7 | 103.3 | 174.9 | 269.2 | 576.2 | 699.6 | 218.4 | 600.2 | 69.3 | 313.6 | 285.3 | 77.2 | 180.5 | 213.3 | 142.5
648 | 412 | 567.7 | 227.08 | 265.4434 | 329.1 | 292.3 | 296.9 | 151.1 | 593.2 | 37.7 | 19.7 | 77.8 | 5.1 | 245 | 3.8 | 866.8 | 839.2 | 194 | 770.8 | 587.3 | 854.6 | 782.3 | 631.3 | 734 | 404.9 | 344.8 | 743.2 | 31.8 | 103.8 | 175.3 | 269.9 | 579.8 | 695.9 | 218.7 | 603.2 | 69.6 | 314.1 | 286.4 | 77.5 | 181.1 | 214.1 | 142.9
649 | 413 | 564.8 | 225.92 | 264.0875 | 329.5 | 292.5 | 296.1 | 152.3 | 595.2 | 37.8 | 19.7 | 78 | 5 | 239 | 3.8 | 869 | 842.1 | 193.1 | 770.9 | 588.7 | 854.4 | 784.2 | 634.2 | 727.1 | 405.6 | 345.9 | 743.3 | 31.9 | 104.2 | 175.7 | 270.4 | 580.2 | 691.3 | 218.9 | 605 | 69.8 | 314.5 | 286.7 | 77.8 | 181.5 | 214.8 | 143.4
650 | 414 | 564.3 | 225.72 | 263.8537 | 329.9 | 293.5 | 295.9 | 153.3 | 595.7 | 37.9 | 19.7 | 78.2 | 5 | 249.7 | 4.3 | 871.1 | 849 | 193.1 | 772.5 | 590.5 | 854.8 | 785.1 | 635.2 | 735.5 | 406.1 | 347 | 745.8 | 32.1 | 104.7 | 176.2 | 271.2 | 579.8 | 691.5 | 219.2 | 606.6 | 70 | 315.5 | 287.8 | 78.1 | 181.9 | 215.5 | 143.8
651 | 415 | 565.1 | 226.04 | 264.2277 | 330.6 | 295.3 | 295.8 | 154 | 595.5 | 38 | 19.7 | 78.4 | 5.1 | 242.7 | 4.4 | 869.2 | 851.3 | 193.2 | 774 | 592.1 | 855.7 | 783.9 | 634.9 | 745.2 | 406.4 | 348.1 | 747 | 32.2 | 105.1 | 176.5 | 272.1 | 576.9 | 684.5 | 219.6 | 602.8 | 70.2 | 315.9 | 288.8 | 78.3 | 182.4 | 216.3 | 144.3
652 | 416 | 564.8 | 225.92 | 264.0875 | 331.5 | 296.3 | 295.5 | 154.5 | 594 | 38.1 | 19.7 | 78.8 | 5.6 | 200.2 | 4.7 | 866.7 | 852.4 | 193.4 | 775.1 | 593.6 | 855.4 | 782.1 | 635 | 752.1 | 407 | 349.2 | 747.4 | 32.3 | 105.5 | 177.2 | 273.1 | 574.3 | 684.1 | 220 | 599.3 | 70.4 | 316.1 | 289.4 | 78.6 | 182.8 | 217 | 144.7
653 | 417 | 564.9 | 225.96 | 264.1342 | 332 | 297.4 | 296.4 | 155 | 605.8 | 38.3 | 19.7 | 79.3 | 5.6 | 198.8 | 4.8 | 859.9 | 847.5 | 193.3 | 775.8 | 594.1 | 854.7 | 781.3 | 635.7 | 748.2 | 407.7 | 350.3 | 746.3 | 32.5 | 105.9 | 178.4 | 274 | 576.4 | 693.3 | 220.3 | 604.2 | 70.6 | 316.2 | 289 | 78.9 | 183.4 | 217.8 | 145.1
654 | 418 | 566 | 226.4 | 264.6486 | 330.9 | 297.7 | 298.5 | 155.5 | 612.1 | 38.5 | 19.7 | 79.6 | 4.9 | 246.2 | 4.2 | 863.4 | 848 | 192.9 | 776.6 | 594.6 | 855.8 | 782.7 | 635.6 | 743.6 | 408.3 | 351.4 | 746.5 | 32.6 | 106.3 | 178.4 | 274.9 | 577 | 695.5 | 220.7 | 607.1 | 70.8 | 316.2 | 288.9 | 79.2 | 183.8 | 218.5 | 145.5
655 | 419 | 566.7 | 226.68 | 264.9759 | 330.4 | 299 | 299.7 | 156.1 | 609.1 | 38.6 | 19.7 | 79.7 | 5.3 | 243.7 | 3.5 | 865.8 | 845.8 | 193 | 777.1 | 595.5 | 857.1 | 783.5 | 632.1 | 742.3 | 408.9 | 352.4 | 747.8 | 32.8 | 106.7 | 178.5 | 275.6 | 577 | 688.8 | 221.1 | 605.2 | 71 | 316.6 | 289.2 | 79.4 | 184.2 | 219.3 | 145.9
656 | 420 | 565.5 | 226.2 | 264.4148 | 331.7 | 299 | 299.2 | 156.7 | 606.4 | 38.7 | 19.7 | 79.8 | 5.6 | 227.5 | 3.1 | 858.8 | 838 | 193.7 | 778.1 | 596 | 858.4 | 782.9 | 630.3 | 742.5 | 409.5 | 353.5 | 747.8 | 32.9 | 107.1 | 179.2 | 276.4 | 576.8 | 690.4 | 221.5 | 605.8 | 71.2 | 316.6 | 289.5 | 79.7 | 184.6 | 220 | 146.3
657 | 421 | 564.2 | 225.68 | 263.8069 | 332.8 | 298.2 | 299.7 | 157.2 | 617.6 | 38.9 | 19.7 | 79.9 | 5.4 | 234.2 | 2.9 | 845.2 | 820.3 | 194.4 | 779.3 | 595.7 | 858.5 | 783.6 | 629.2 | 736.4 | 410 | 354.6 | 745.6 | 33 | 107.4 | 180.5 | 277.2 | 577.8 | 699.3 | 221.9 | 607.7 | 71.5 | 316.8 | 289.1 | 80 | 184.9 | 220.7 | 146.7
658 | 422 | 564.5 | 225.8 | 263.9472 | 333.9 | 297.6 | 301.9 | 157.9 | 630.2 | 39 | 19.7 | 80 | 5.4 | 244.9 | 3.7 | 842.4 | 821.2 | 195.1 | 780.4 | 595.6 | 857.2 | 787.2 | 629.5 | 730.7 | 410.5 | 355.5 | 745.7 | 33.2 | 107.7 | 181 | 278.1 | 581.5 | 705.9 | 222.2 | 609.7 | 71.7 | 317.6 | 289.5 | 80.2 | 185.4 | 221.5 | 147.1
659 | 423 | 566.9 | 226.76 | 265.0694 | 336.2 | 297.8 | 303 | 158.7 | 631.6 | 39.1 | 19.7 | 80 | 5.2 | 247.4 | 4.9 | 851.7 | 827.1 | 195.1 | 782.1 | 596.4 | 857.6 | 790.5 | 630.1 | 733.4 | 411 | 356.4 | 746.8 | 33.3 | 108 | 181.3 | 279.2 | 582.9 | 706.4 | 222.6 | 611 | 71.9 | 317.3 | 290.3 | 80.5 | 185.9 | 222.2 | 147.5
660 | 424 | 566.8 | 226.72 | 265.0226 | 336.2 | 297.8 | 304.3 | 159.2 | 627.3 | 39.1 | 19.7 | 80 | 4.5 | 242 | 5.6 | 855.5 | 831.5 | 195.3 | 783.5 | 597.6 | 858.6 | 789.9 | 628.5 | 738.8 | 411.4 | 357.2 | 748.2 | 33.4 | 108.4 | 181.5 | 280.1 | 583.1 | 704.8 | 223 | 610.5 | 72.1 | 316.8 | 290.4 | 80.8 | 186.4 | 223 | 148
661 | 425 | 564.3 | 225.72 | 263.8537 | 336.7 | 297.4 | 305.1 | 159.7 | 622.2 | 39.2 | 19.7 | 80.1 | 4.5 | 238.8 | 6 | 861.2 | 834.4 | 195.8 | 785.4 | 599 | 859.5 | 787.9 | 626.8 | 746.8 | 411.9 | 358.2 | 749.6 | 33.6 | 108.8 | 181.8 | 280.8 | 583.1 | 704.6 | 223.3 | 609.2 | 72.3 | 316.5 | 290.9 | 81.1 | 186.9 | 223.7 | 148.4
662 | 426 | 564.2 | 225.68 | 263.8069 | 336.6 | 296.8 | 304.5 | 160.1 | 617.5 | 39.3 | 19.7 | 80.4 | 4.8 | 240.2 | 6.1 | 862.2 | 838.7 | 195.9 | 787.9 | 600.2 | 861 | 788.2 | 624.9 | 745.3 | 412.2 | 359.2 | 751.1 | 33.7 | 109.2 | 182 | 281.5 | 582.7 | 698.3 | 223.7 | 610 | 72.6 | 316.3 | 291.6 | 81.3 | 187.3 | 224.4 | 148.7
663 | 427 | 566 | 226.4 | 264.6486 | 337.4 | 296.5 | 304.2 | 160.5 | 605.9 | 39.5 | 19.7 | 80.6 | 4.5 | 244.3 | 6.3 | 863.6 | 846.2 | 195.6 | 789.7 | 601.9 | 861.9 | 790.7 | 622.8 | 742.1 | 412.8 | 360.2 | 750.5 | 33.9 | 109.7 | 182.2 | 282 | 587 | 693.1 | 224.1 | 610.4 | 72.8 | 315.8 | 292 | 81.6 | 187.7 | 225.1 | 149.1
664 | 428 | 564.7 | 225.88 | 264.0407 | 337.1 | 296.1 | 303 | 161.2 | 605.1 | 39.6 | 19.7 | 80.8 | 5.1 | 238 | 6.5 | 866.7 | 855.7 | 195.2 | 790.8 | 603 | 862.2 | 791.6 | 621.7 | 748.8 | 413.1 | 361.4 | 751.6 | 34 | 110.1 | 182.7 | 282.8 | 586.3 | 700.4 | 224.4 | 613.3 | 73 | 315.8 | 291.7 | 81.9 | 188.2 | 225.9 | 149.5
665 | 429 | 565.7 | 226.28 | 264.5083 | 335.7 | 295.6 | 302.1 | 161.6 | 606.7 | 39.6 | 19.6 | 80.8 | 4.7 | 246.7 | 6.2 | 866.9 | 856.9 | 195.1 | 790.7 | 604.1 | 861.7 | 790 | 621.5 | 755.2 | 413.6 | 362.4 | 752.2 | 34.1 | 110.5 | 183.2 | 283.6 | 583.6 | 709.5 | 224.9 | 616.5 | 73.2 | 316.3 | 291.7 | 82.2 | 188.6 | 226.7 | 149.9
666 | 430 | 565.5 | 226.2 | 264.4148 | 333.9 | 296.2 | 301.1 | 162 | 607.8 | 39.6 | 19.6 | 80.9 | 4.8 | 248.1 | 5.8 | 868.8 | 856.4 | 195.2 | 790.4 | 605.2 | 861.1 | 790.8 | 622.6 | 758 | 414.2 | 363.5 | 754.6 | 34.3 | 110.9 | 183.7 | 284.5 | 582.9 | 710.7 | 225.4 | 618.2 | 73.4 | 316.8 | 291.8 | 82.5 | 189 | 227.4 | 150.3
667 | 431 | 565 | 226 | 264.181 | 332.9 | 296.5 | 300.8 | 162.5 | 608.4 | 39.6 | 19.6 | 81 | 4.8 | 246.8 | 6 | 870.5 | 849 | 195 | 790.4 | 606.8 | 861.9 | 791.7 | 623.7 | 753.6 | 414.7 | 364.6 | 754.7 | 34.4 | 111.3 | 184.3 | 285.4 | 582.7 | 710.2 | 225.9 | 616.3 | 73.6 | 316.7 | 292.2 | 82.7 | 189.5 | 228.1 | 150.7
668 | 432 | 564.2 | 225.68 | 263.8069 | 334.1 | 296.8 | 301.1 | 162.9 | 615.4 | 39.6 | 19.6 | 81.1 | 5.4 | 226.5 | 5.8 | 853.2 | 829.3 | 194.3 | 790.7 | 608.1 | 862.5 | 792.8 | 624.4 | 740.9 | 415.4 | 365.6 | 753.9 | 34.6 | 111.7 | 184.7 | 286.4 | 583.2 | 710.6 | 226.3 | 615.3 | 73.9 | 316.6 | 291.9 | 83 | 189.9 | 228.8 | 151.2
669 | 433 | 566.1 | 226.44 | 264.6953 | 334.3 | 296.5 | 301 | 163.5 | 621.9 | 39.6 | 19.6 | 81.2 | 5.2 | 227.5 | 5.3 | 851.6 | 825.6 | 193.8 | 790.9 | 609.3 | 862 | 796.1 | 624.1 | 723.8 | 415.9 | 366.7 | 751 | 34.7 | 112.2 | 184.9 | 287.4 | 582.9 | 707.8 | 226.7 | 614.9 | 74.1 | 317.6 | 291.9 | 83.3 | 190.3 | 229.5 | 151.6
670 | 434 | 565.9 | 226.36 | 264.6018 | 333.3 | 296.2 | 301.5 | 164.2 | 622.6 | 39.7 | 19.6 | 81.3 | 5 | 244.3 | 4.9 | 856 | 835.3 | 194 | 791.5 | 610.2 | 861.2 | 800.3 | 625 | 726.7 | 416.4 | 367.6 | 752.9 | 34.8 | 112.6 | 185.4 | 288.3 | 581.7 | 709.9 | 227.1 | 614.6 | 74.3 | 321.6 | 292.4 | 83.6 | 190.8 | 230.2 | 152
671 | 435 | 564.3 | 225.72 | 263.8537 | 334 | 296 | 301.6 | 164.9 | 623.4 | 39.8 | 19.6 | 81.4 | 5 | 235.2 | 4.4 | 857.8 | 848.7 | 194.7 | 791.7 | 611.8 | 861.2 | 800.2 | 624.2 | 736.5 | 416.5 | 368.6 | 754.1 | 35 | 113 | 186.2 | 288.8 | 581.5 | 718.7 | 227.5 | 615 | 74.5 | 321.8 | 293.4 | 83.9 | 191.4 | 230.9 | 152.5
672 | 436 | 563.9 | 225.56 | 263.6666 | 334.8 | 296.3 | 301.2 | 165.6 | 619.8 | 39.9 | 19.6 | 81.5 | 4.8 | 241.4 | 3.7 | 856.5 | 852.2 | 195.6 | 791.6 | 613.2 | 861.6 | 796.7 | 622.1 | 744.3 | 417.1 | 369.7 | 755.3 | 35.1 | 113.5 | 186.4 | 289.5 | 580.7 | 716 | 227.9 | 614.6 | 74.8 | 321.5 | 293.7 | 84.1 | 192 | 231.6 | 153
673 | 437 | 565.7 | 226.28 | 264.5083 | 333.6 | 296.2 | 302.3 | 166.1 | 620.5 | 39.9 | 19.6 | 81.6 | 5 | 234.9 | 3.1 | 857 | 852.8 | 196.6 | 790.5 | 615.1 | 861 | 792.9 | 623.3 | 748.8 | 417.3 | 370.7 | 754.6 | 35.3 | 113.9 | 187.2 | 290.4 | 579.7 | 719 | 228.3 | 617.2 | 75 | 321.1 | 293.5 | 84.4 | 192.4 | 232.3 | 153.4
674 | 438 | 567.2 | 226.88 | 265.2096 | 332.2 | 296.4 | 302 | 166.5 | 619.6 | 40 | 19.6 | 81.8 | 4.9 | 234.8 | 2.8 | 857.7 | 856.7 | 196.8 | 789.6 | 616.6 | 860.8 | 790.5 | 623.7 | 751.4 | 418.2 | 372 | 755 | 35.4 | 114.3 | 187.8 | 291.3 | 580.6 | 716.5 | 228.7 | 616.9 | 75.2 | 319.8 | 293.1 | 84.7 | 192.8 | 233 | 153.8
675 | 439 | 565.3 | 226.12 | 264.3213 | 331 | 297.5 | 300.5 | 167 | 618.3 | 40.1 | 19.6 | 81.8 | 4.3 | 239.7 | 2.7 | 859.6 | 857.5 | 197.2 | 789.6 | 617.9 | 860.1 | 788.8 | 625.6 | 756.6 | 418.7 | 373.2 | 756.6 | 35.6 | 114.7 | 187.9 | 292.3 | 579.9 | 725.3 | 229.1 | 616.9 | 75.5 | 319.3 | 292.9 | 85 | 193.3 | 233.8 | 154.2
676 | 440 | 564.9 | 225.96 | 264.1342 | 330.3 | 299.7 | 300.6 | 167.4 | 624.4 | 40.1 | 19.6 | 81.9 | 5 | 245.8 | 2.9 | 861.8 | 853.9 | 198.3 | 789 | 620 | 859.7 | 787.7 | 626.3 | 758.2 | 419.1 | 374.2 | 755.8 | 35.7 | 115.1 | 189.2 | 293.1 | 579.4 | 729.1 | 229.5 | 618.8 | 75.7 | 319.4 | 292.5 | 85.2 | 193.9 | 234.5 | 154.6
677 | 441 | 564.8 | 225.92 | 264.0875 | 330.4 | 301.5 | 300.5 | 167.9 | 634 | 40.2 | 19.6 | 82 | 5.2 | 256.8 | 3.4 | 860.8 | 844.9 | 198.8 | 788.8 | 622.1 | 859.8 | 787.9 | 626 | 753 | 420.2 | 375.1 | 753.1 | 35.9 | 115.5 | 190.1 | 294.1 | 580.2 | 732.3 | 229.9 | 617.9 | 75.9 | 319.5 | 292.2 | 85.5 | 194.1 | 235.2 | 154.9
678 | 442 | 565 | 226 | 264.181 | 330.5 | 301.4 | 300.9 | 168.2 | 641.4 | 40.2 | 19.6 | 82 | 5 | 254.1 | 3.6 | 856.4 | 841.2 | 199.6 | 789.2 | 623.6 | 859.8 | 788.6 | 626.8 | 753.1 | 420.8 | 376.1 | 753.3 | 36 | 115.9 | 190.7 | 295.1 | 582.7 | 739.1 | 230.3 | 622.9 | 76.1 | 320.1 | 292.4 | 85.8 | 194.7 | 236 | 155.3
679 | 443 | 564.5 | 225.8 | 263.9472 | 329.7 | 301.1 | 300.4 | 169 | 642.7 | 40.3 | 19.6 | 81.9 | 5 | 235.5 | 3.5 | 856.5 | 840.7 | 200.4 | 789.8 | 625.2 | 859.2 | 788 | 627.1 | 759.5 | 421.3 | 377 | 754.5 | 36.2 | 116.3 | 190.9 | 296.2 | 583.9 | 740.3 | 230.7 | 626.3 | 76.3 | 320.3 | 292.7 | 86.1 | 195.2 | 236.8 | 155.8
680 | 444 | 564.9 | 225.96 | 264.1342 | 328.6 | 301.7 | 300.8 | 169.9 | 640.2 | 40.4 | 19.6 | 81.9 | 5.2 | 217.7 | 3.3 | 861.7 | 844.9 | 201.3 | 789.7 | 626.6 | 858.8 | 787.5 | 626.8 | 756.9 | 422.1 | 378 | 753.3 | 36.3 | 116.7 | 191.2 | 297.2 | 583.8 | 738.1 | 231.2 | 625.4 | 76.6 | 320.5 | 293.4 | 86.4 | 195.6 | 237.7 | 156.2
681 | 445 | 564.4 | 225.76 | 263.9004 | 328.9 | 301.8 | 301 | 170.6 | 639 | 40.4 | 19.6 | 82 | 5.3 | 213.8 | 3.3 | 862.8 | 846.2 | 202.3 | 789.8 | 628.8 | 859.8 | 787.3 | 626.9 | 760.1 | 423.4 | 379.1 | 753.9 | 36.5 | 117.1 | 191.9 | 298 | 584.1 | 740.4 | 231.6 | 625.1 | 76.8 | 320.4 | 293 | 86.6 | 196 | 238.5 | 156.6
682 | 446 | 565.2 | 226.08 | 264.2745 | 329.5 | 301.8 | 300.8 | 171.1 | 646.5 | 40.5 | 19.6 | 82.1 | 5.5 | 216.5 | 3.4 | 858.3 | 841.4 | 203.8 | 790.9 | 630.7 | 859.8 | 786.4 | 628.6 | 762.1 | 424.1 | 380 | 752.8 | 36.6 | 117.5 | 193.2 | 298.9 | 587.6 | 741.3 | 232 | 629.6 | 77 | 320.7 | 293 | 86.9 | 196.3 | 239.3 | 157
683 | 447 | 565.7 | 226.28 | 264.5083 | 331 | 301.6 | 301.3 | 171.7 | 647.6 | 40.6 | 19.6 | 82.3 | 5.3 | 227.3 | 3.8 | 859.6 | 844.2 | 203.9 | 792.7 | 632.4 | 859.4 | 786.7 | 630.7 | 760 | 424.7 | 380.8 | 753 | 36.8 | 117.8 | 193.6 | 299.8 | 587.7 | 743.3 | 232.5 | 630.8 | 77.3 | 321.2 | 293.3 | 87.2 | 196.7 | 240.1 | 157.4
684 | 448 | 566.4 | 226.56 | 264.8356 | 331.4 | 302.3 | 302.4 | 172.5 | 647.8 | 40.8 | 19.6 | 82.4 | 5 | 231.6 | 4.3 | 860.4 | 842.9 | 204 | 794.1 | 634.1 | 859 | 786.3 | 630.9 | 758.1 | 424.8 | 381.4 | 752.6 | 36.9 | 118.2 | 193.9 | 300.7 | 587.5 | 744.8 | 233 | 630.7 | 77.5 | 321.6 | 293 | 87.5 | 197.1 | 240.9 | 157.8
685 | 449 | 566 | 226.4 | 264.6486 | 330.4 | 302.9 | 303.1 | 173.1 | 649.4 | 40.8 | 19.6 | 82.5 | 5.2 | 211.7 | 5.5 | 851.8 | 831.4 | 204 | 795.5 | 635.9 | 859.6 | 785.4 | 630.7 | 758.6 | 424.9 | 382.2 | 753 | 37.1 | 118.5 | 194.7 | 301.6 | 589.6 | 745.8 | 233.5 | 633.3 | 77.7 | 322.1 | 293.6 | 87.8 | 197.6 | 241.7 | 158.3
686 | 450 | 565 | 226 | 264.181 | 331 | 302.7 | 303 | 173.8 | 654.6 | 40.9 | 19.6 | 82.7 | 5.4 | 215.1 | 6.5 | 850.1 | 826.3 | 204.3 | 796.5 | 637.7 | 860 | 786.4 | 632.7 | 755.8 | 425 | 383 | 754 | 37.2 | 118.9 | 195.7 | 302.5 | 591.5 | 751 | 234 | 636 | 78 | 322.2 | 294.2 | 88 | 198.2 | 242.5 | 158.7
687 | 451 | 565.4 | 226.16 | 264.368 | 332.6 | 303.2 | 303.9 | 174.6 | 656.4 | 41 | 19.6 | 82.8 | 5.4 | 219.7 | 6.8 | 851 | 823 | 205.3 | 797.5 | 638.9 | 860.3 | 788.3 | 634.2 | 744.1 | 425.2 | 383.8 | 753.5 | 37.4 | 119.2 | 196 | 303.5 | 593 | 745.7 | 234.5 | 635 | 78.2 | 322.8 | 294.6 | 88.3 | 198.8 | 243.3 | 159.1
688 | 452 | 564.9 | 225.96 | 264.1342 | 335.4 | 303.9 | 305.3 | 175.3 | 656.5 | 41 | 19.6 | 83 | 5.5 | 216.3 | 7.2 | 859.2 | 832.7 | 205.3 | 798 | 640.1 | 861.1 | 792.6 | 635.9 | 737.3 | 425.3 | 384.4 | 752.1 | 37.5 | 119.6 | 196.5 | 304.3 | 593 | 747.2 | 235.1 | 636.2 | 78.4 | 323.3 | 294.9 | 88.6 | 199.2 | 244.1 | 159.5
689 | 453 | 565.9 | 226.36 | 264.6018 | 337.6 | 304.1 | 307.4 | 176.1 | 656.9 | 41.1 | 19.6 | 83.1 | 5.2 | 221.1 | 6.7 | 860.9 | 834.9 | 205.4 | 798 | 641 | 861.3 | 796.9 | 636.6 | 739.5 | 425.5 | 385.1 | 753 | 37.7 | 119.9 | 196.8 | 305.2 | 593.6 | 746.5 | 235.5 | 634.3 | 78.6 | 323.5 | 295.3 | 88.9 | 199.9 | 244.8 | 160
690 | 454 | 564.2 | 225.68 | 263.8069 | 338.6 | 304 | 308.4 | 176.8 | 655.6 | 41.2 | 19.6 | 83.1 | 5.3 | 215.7 | 5.7 | 862.6 | 830.4 | 205.9 | 798 | 642.7 | 861.8 | 798.7 | 636.2 | 745.5 | 425.8 | 385.8 | 754.7 | 37.9 | 120.3 | 197.3 | 306.2 | 594.2 | 750.7 | 236 | 634.7 | 78.9 | 323.8 | 295.7 | 89.2 | 200.2 | 245.6 | 160.4
691 | 455 | 566.8 | 226.72 | 265.0226 | 339.4 | 304.3 | 307.8 | 177.2 | 653 | 41.3 | 19.6 | 83.3 | 5.2 | 229.4 | 6 | 866.3 | 835.4 | 206.1 | 797.9 | 644 | 862.5 | 799.5 | 634.2 | 745.9 | 426.3 | 386.5 | 755.7 | 38 | 120.6 | 197.9 | 307.2 | 594.2 | 750.7 | 236.5 | 634.5 | 79.1 | 323.7 | 296 | 89.5 | 200.7 | 246.3 | 160.8
692 | 456 | 565.4 | 226.16 | 264.368 | 340 | 305 | 307.9 | 177.2 | 652 | 41.3 | 19.5 | 83.5 | 5.3 | 221.6 | 5.7 | 865.9 | 840.9 | 206.2 | 798.4 | 645.2 | 862.8 | 799.8 | 632.3 | 745.3 | 426.6 | 387 | 755.8 | 38.2 | 121 | 198.3 | 308.4 | 593.2 | 748.3 | 237.1 | 632.4 | 79.3 | 324.1 | 296.2 | 89.8 | 201.1 | 247.1 | 161.3
693 | 457 | 564.5 | 225.8 | 263.9472 | 340.1 | 305.1 | 308.5 | 177.6 | 646.8 | 41.4 | 19.5 | 83.7 | 5.1 | 223.9 | 5.2 | 859.2 | 836.8 | 206.2 | 798.8 | 646.7 | 864.4 | 800.2 | 629.4 | 739.6 | 426.9 | 387.7 | 756 | 38.3 | 121.4 | 198.4 | 309.5 | 592.9 | 744.2 | 237.6 | 628.7 | 79.6 | 324.1 | 297.1 | 90.1 | 201.6 | 247.9 | 161.7
694 | 458 | 564.8 | 225.92 | 264.0875 | 338.9 | 305.6 | 308.6 | 178.3 | 642.8 | 41.5 | 19.5 | 83.9 | 5.1 | 232.5 | 4.5 | 859.1 | 836.6 | 205.8 | 799.8 | 648.1 | 865.4 | 802.2 | 629.9 | 733.4 | 427.2 | 388.5 | 756.2 | 38.5 | 121.8 | 198.7 | 310.7 | 592.4 | 741.9 | 238.1 | 630.5 | 79.8 | 323.9 | 297.5 | 90.3 | 202 | 248.6 | 162.1
695 | 459 | 564.6 | 225.84 | 263.9939 | 338.5 | 306.7 | 308.7 | 178.8 | 633.4 | 41.6 | 19.5 | 84.1 | 4.8 | 235.2 | 4.1 | 865.7 | 843.1 | 205.3 | 800.5 | 649.6 | 866.8 | 803.3 | 628.1 | 728.3 | 427.4 | 389 | 755.2 | 38.6 | 122.2 | 199.1 | 311.7 | 590.6 | 732.4 | 238.6 | 628.8 | 80 | 324.1 | 297.6 | 90.7 | 202.3 | 249.3 | 162.5
696 | 460 | 564.8 | 225.92 | 264.0875 | 338.3 | 307.1 | 309.3 | 179.6 | 624.5 | 41.7 | 19.5 | 84.1 | 4 | 236.3 | 4.3 | 867.3 | 845.3 | 204.5 | 800.8 | 651.4 | 868.5 | 804 | 626.5 | 721.9 | 427.7 | 389.9 | 755.5 | 38.8 | 122.6 | 199.5 | 312.7 | 590.3 | 730.9 | 239.1 | 628.9 | 80.3 | 324.1 | 298.2 | 91 | 203 | 250 | 162.9
697 | 461 | 564.5 | 225.8 | 263.9472 | 340.3 | 307.9 | 309.4 | 180.5 | 618.3 | 41.7 | 19.5 | 84.2 | 4.4 | 246 | 4.5 | 871.8 | 852.3 | 203.1 | 801.2 | 653 | 869.8 | 805 | 625.6 | 718.2 | 427.9 | 390.6 | 755.3 | 38.9 | 123 | 199.8 | 313.8 | 590.9 | 730.5 | 239.7 | 628.7 | 80.5 | 324.5 | 299.6 | 91.3 | 203.6 | 250.7 | 163.3
698 | 462 | 563.5 | 225.4 | 263.4796 | 341.9 | 308.6 | 309.5 | 181 | 611.6 | 41.8 | 19.5 | 84.4 | 5.1 | 216.2 | 5.8 | 876.6 | 858.8 | 202.4 | 801.7 | 654.1 | 871.5 | 805.5 | 624 | 714.1 | 427.9 | 391.3 | 755.4 | 39.1 | 123.4 | 199.9 | 314.8 | 589.5 | 736.8 | 240.3 | 628 | 80.7 | 324.4 | 300.6 | 91.6 | 204.2 | 251.4 | 163.7
699 | 463 | 565.1 | 226.04 | 264.2277 | 342.8 | 308.5 | 309.2 | 181.4 | 608.5 | 42 | 19.5 | 84.6 | 5.3 | 231.7 | 7.7 | 878.2 | 860.6 | 201.4 | 802.4 | 654.6 | 872.6 | 806.1 | 621.5 | 717.2 | 427.9 | 392.1 | 756.2 | 39.3 | 123.8 | 200.2 | 315.8 | 589.5 | 739.8 | 240.8 | 629.3 | 81 | 326.1 | 301.4 | 92 | 204.6 | 252.1 | 164.1
700 | 464 | 567.7 | 227.08 | 265.4434 | 344.7 | 308.4 | 307.8 | 181.7 | 608.5 | 42.1 | 19.5 | 84.8 | 5 | 233 | 8.1 | 876.9 | 865.6 | 200.2 | 803.1 | 655.4 | 872.7 | 806.7 | 621.2 | 719 | 428 | 393 | 755.3 | 39.4 | 124.2 | 200.4 | 316.9 | 594 | 734.1 | 241.3 | 635.7 | 81.2 | 326 | 302.2 | 92.3 | 205.1 | 252.8 | 164.6
701 | 465 | 568.7 | 227.48 | 265.911 | 344.8 | 308.9 | 306.2 | 182.1 | 610.9 | 42.2 | 19.5 | 84.9 | 5.2 | 222.1 | 7.2 | 875.8 | 867.2 | 199.7 | 804.1 | 656.4 | 872.8 | 807.4 | 621.3 | 729.4 | 428.2 | 393.9 | 755.4 | 39.6 | 124.6 | 200.8 | 318 | 595.8 | 728.1 | 241.9 | 636.5 | 81.4 | 326.7 | 302.4 | 92.6 | 205.7 | 253.5 | 165
702 | 466 | 566.7 | 226.68 | 264.9759 | 344.7 | 308.7 | 305.3 | 182.8 | 608 | 42.3 | 19.5 | 85.1 | 5 | 235.6 | 6.4 | 869.5 | 867.3 | 199.7 | 805.3 | 658.1 | 872.2 | 806 | 621 | 741.7 | 428.3 | 395 | 757.3 | 39.8 | 124.9 | 201.2 | 319.1 | 595.5 | 720.4 | 242.5 | 636.5 | 81.6 | 328 | 302.5 | 93 | 206.2 | 254.3 | 165.5
703 | 467 | 566.1 | 226.44 | 264.6953 | 346.6 | 309.2 | 304.3 | 183.8 | 609.2 | 42.4 | 19.5 | 85.1 | 5.3 | 235 | 5.4 | 867.3 | 867.7 | 200.4 | 805.7 | 659.3 | 871.3 | 804.6 | 621.3 | 750.4 | 428.5 | 395.8 | 757 | 39.9 | 125.3 | 201.5 | 320.2 | 595.4 | 718.6 | 243.1 | 637.6 | 81.9 | 328.9 | 302.9 | 93.3 | 206.9 | 255.1 | 166
704 | 468 | 566.5 | 226.6 | 264.8823 | 347.4 | 309 | 304.3 | 184.6 | 613.5 | 42.5 | 19.5 | 85.1 | 5 | 230.7 | 4.7 | 868.5 | 867.7 | 201.5 | 805.8 | 660.6 | 871.1 | 803.9 | 621.1 | 761.1 | 428.8 | 396.6 | 760.2 | 40.1 | 125.7 | 201.9 | 321.3 | 592.6 | 723.2 | 243.7 | 637.7 | 82.1 | 328.8 | 303.3 | 93.7 | 207.4 | 255.9 | 166.4
705 | 469 | 566.4 | 226.56 | 264.8356 | 347.8 | 309.2 | 303.5 | 185.2 | 610.3 | 42.7 | 19.5 | 85.2 | 4.7 | 227.8 | 4.7 | 873.9 | 868.2 | 202.1 | 806.4 | 662.1 | 871.4 | 803.5 | 619.9 | 762.7 | 429.1 | 397.3 | 761.3 | 40.2 | 126.1 | 202.5 | 322.4 | 590.9 | 722.2 | 244.3 | 634.2 | 82.3 | 328.8 | 303.4 | 94 | 207.8 | 256.6 | 166.8
706 | 470 | 565 | 226 | 264.181 | 347.1 | 310.2 | 304 | 185.3 | 604.7 | 42.7 | 19.5 | 85.3 | 5.1 | 225.5 | 4.2 | 872.2 | 868.1 | 202.3 | 806.7 | 662.8 | 870.9 | 804.8 | 619 | 758.3 | 429.4 | 398 | 763 | 40.4 | 126.5 | 202.8 | 323.5 | 589.7 | 713.8 | 245 | 631 | 82.6 | 328.4 | 303.4 | 94.3 | 208.2 | 257.3 | 167.3
707 | 471 | 566.6 | 226.64 | 264.9291 | 348.3 | 310.8 | 304.4 | 185.4 | 601.2 | 42.8 | 19.5 | 85.5 | 5.1 | 220.4 | 4.7 | 874.1 | 866.8 | 202.3 | 807.2 | 663.8 | 870.3 | 807.9 | 618.1 | 760.3 | 429.4 | 398.8 | 763.5 | 40.6 | 126.8 | 203.1 | 324.5 | 591.9 | 712.1 | 245.6 | 632.4 | 82.8 | 328.6 | 303.3 | 94.7 | 208.6 | 258 | 167.7
708 | 472 | 566.1 | 226.44 | 264.6953 | 350.6 | 311.7 | 303.7 | 186 | 602.8 | 42.8 | 19.5 | 85.7 | 5.5 | 214.8 | 6.8 | 875.2 | 867.8 | 202.2 | 807.3 | 665.3 | 870.7 | 808.4 | 618.4 | 755.7 | 429.6 | 399.6 | 763.7 | 40.7 | 127.2 | 203.4 | 325.6 | 593.3 | 702.9 | 246.5 | 631.6 | 83 | 329.1 | 303.9 | 95 | 209.1 | 258.8 | 168.1
709 | 473 | 564.9 | 225.96 | 264.1342 | 350.6 | 311.1 | 304 | 186.9 | 601.8 | 42.9 | 19.4 | 85.9 | 5.1 | 209.3 | 7.2 | 874 | 869.1 | 202.3 | 806.9 | 667 | 871.2 | 808.9 | 618.1 | 757.9 | 429.6 | 400.3 | 764.4 | 40.9 | 127.6 | 203.9 | 326.7 | 594.4 | 705.9 | 247.3 | 632.6 | 83.3 | 330.3 | 303.9 | 95.4 | 209.6 | 259.5 | 168.5
710 | 474 | 566.5 | 226.6 | 264.8823 | 351.3 | 311.5 | 305.2 | 187.7 | 605.1 | 43 | 19.4 | 86 | 4.9 | 213.9 | 6.2 | 871.3 | 868.9 | 202.6 | 805.9 | 668.7 | 870.8 | 808.1 | 617.7 | 761.1 | 429.5 | 401 | 764.5 | 41.1 | 128 | 204.5 | 327.7 | 592 | 707.6 | 248 | 631 | 83.5 | 331 | 303.9 | 95.7 | 210 | 260.3 | 169
711 | 475 | 567.1 | 226.84 | 265.1629 | 350.9 | 312.9 | 306.5 | 187.9 | 615.6 | 43.1 | 19.4 | 86 | 4.6 | 232.2 | 5.3 | 872 | 869.2 | 203 | 804.7 | 670 | 869.9 | 806.6 | 619.6 | 761.9 | 429.5 | 401.9 | 763.2 | 41.2 | 128.3 | 205.6 | 328.8 | 592.3 | 713.5 | 248.6 | 630.8 | 83.7 | 331 | 303.6 | 96 | 210.2 | 261 | 169.4
712 | 476 | 567.7 | 227.08 | 265.4434 | 348.6 | 314.3 | 307 | 187.8 | 628.2 | 43.2 | 19.4 | 86 | 4.5 | 227.6 | 5 | 872.2 | 866.9 | 202.9 | 803.8 | 670.8 | 869.3 | 804.8 | 622 | 760.5 | 429.8 | 402.8 | 762.1 | 41.4 | 128.7 | 206.5 | 329.8 | 594.8 | 722.1 | 249.3 | 634 | 84 | 330.4 | 303.2 | 96.4 | 210.6 | 261.7 | 169.8
713 | 477 | 564.3 | 225.72 | 263.8537 | 347.9 | 314.2 | 307.8 | 188.1 | 641.5 | 43.3 | 19.4 | 86.1 | 4.6 | 220.8 | 4.2 | 863.9 | 857.9 | 203.2 | 803.8 | 672 | 868.4 | 803.8 | 624.9 | 753.6 | 430.3 | 403.8 | 760.3 | 41.6 | 129 | 207 | 330.9 | 598.1 | 728.8 | 249.9 | 637.7 | 84.2 | 330.4 | 303.2 | 96.7 | 211.2 | 262.5 | 170.2
714 | 478 | 562.4 | 224.96 | 262.9653 | 347.1 | 313.8 | 308.6 | 188.6 | 648.4 | 43.3 | 19.4 | 86 | 4.9 | 197 | 4.5 | 861.5 | 852.1 | 203.6 | 804.4 | 673.4 | 867.5 | 805.2 | 627.1 | 751.6 | 430.9 | 404.8 | 760.8 | 41.7 | 129.5 | 207.4 | 331.9 | 598.5 | 733 | 250.6 | 637.7 | 84.4 | 330.8 | 303.3 | 97.1 | 211.4 | 263.3 | 170.6
715 | 479 | 563.4 | 225.36 | 263.4329 | 346.6 | 313.6 | 309 | 189.5 | 650.1 | 43.4 | 19.4 | 86 | 5.2 | 224.9 | 4.3 | 862.9 | 852.9 | 203.9 | 805.2 | 674.6 | 866.9 | 806.3 | 630.3 | 750.3 | 431.6 | 405.8 | 760.1 | 41.9 | 129.8 | 208.2 | 332.9 | 599.4 | 732.6 | 251.2 | 638.8 | 84.6 | 331.7 | 303.1 | 97.5 | 211.7 | 264 | 171.1
716 | 480 | 562.8 | 225.12 | 263.1523 | 346.6 | 313 | 309.7 | 190.5 | 651.5 | 43.5 | 19.4 | 86 | 4.8 | 218.8 | 4.5 | 864 | 852 | 204.1 | 807.3 | 675.9 | 866.3 | 806.5 | 633.6 | 746 | 432.4 | 406.8 | 758.3 | 42.1 | 130.2 | 208.7 | 333.9 | 600.1 | 733 | 252 | 638.9 | 84.9 | 332.2 | 303.6 | 97.8 | 212.1 | 264.8 | 171.5
717 | 481 | 564.1 | 225.64 | 263.7602 | 346.3 | 312.5 | 310.7 | 191.7 | 655.3 | 43.7 | 19.4 | 86 | 5 | 218.3 | 4.3 | 864 | 854.9 | 203.9 | 807.9 | 676.8 | 865.7 | 808.3 | 635.5 | 746.9 | 433.4 | 408 | 758.4 | 42.2 | 130.7 | 209.1 | 334.8 | 600.7 | 735.2 | 252.6 | 639.8 | 85.1 | 332.3 | 303.8 | 98.2 | 212.6 | 265.6 | 171.9
718 | 482 | 564.4 | 225.76 | 263.9004 | 346.8 | 312.6 | 312.8 | 192.4 | 655.6 | 43.8 | 19.4 | 86 | 5.4 | 234.8 | 3.9 | 863.2 | 853.4 | 204.1 | 808 | 677.4 | 865.9 | 807.5 | 634.6 | 743.3 | 434.6 | 408.9 | 757.1 | 42.4 | 131 | 209.7 | 335.7 | 602.2 | 731.7 | 253.3 | 637.1 | 85.3 | 331.9 | 304.5 | 98.6 | 213 | 266.4 | 172.3
719 | 483 | 564.3 | 225.72 | 263.8537 | 347.5 | 312.5 | 313.8 | 193 | 655.4 | 43.9 | 19.4 | 86 | 5 | 207 | 3.5 | 869.4 | 856 | 204.1 | 808.6 | 678.7 | 866.2 | 806.6 | 633.9 | 743.7 | 435.6 | 409.9 | 756.4 | 42.5 | 131.4 | 209.8 | 336.6 | 603.5 | 731.4 | 254 | 636.1 | 85.6 | 332.3 | 304.7 | 99 | 213.6 | 267.1 | 172.8
720 | 484 | 563.4 | 225.36 | 263.4329 | 346.9 | 311.9 | 313.4 | 193.9 | 648.4 | 43.9 | 19.4 | 86.1 | 4.6 | 221.6 | 3.4 | 872.7 | 858.6 | 204.1 | 808.4 | 679.7 | 866.9 | 806.3 | 632.2 | 742.2 | 436.7 | 410.7 | 756.2 | 42.7 | 131.7 | 210.1 | 337.5 | 603.3 | 722.8 | 254.7 | 634.6 | 85.8 | 332.3 | 305.3 | 100.5 | 214 | 267.9 | 173.2
721 | 485 | 564.3 | 225.72 | 263.8537 | 347 | 312.1 | 313.4 | 194.7 | 640.7 | 44 | 19.4 | 86.1 | 5 | 264.8 | 3.2 | 874.1 | 858.1 | 204.5 | 808.9 | 681.3 | 868.7 | 808 | 630.8 | 742.4 | 437.8 | 411.6 | 756.6 | 42.9 | 132.1 | 210.6 | 338.3 | 602.3 | 718 | 255.3 | 630 | 86 | 332.3 | 305.7 | 102.3 | 214.4 | 268.6 | 173.6
722 | 486 | 563.9 | 225.56 | 263.6666 | 348.1 | 313.6 | 314.7 | 195.1 | 638 | 44 | 19.4 | 86.3 | 5.1 | 236.9 | 4.3 | 866.6 | 854.9 | 204.7 | 809.9 | 682.4 | 870.1 | 807.6 | 630.2 | 735.5 | 438.9 | 412.5 | 755.6 | 43 | 132.5 | 211.3 | 339 | 602.9 | 718.8 | 256.1 | 628.6 | 86.3 | 332.1 | 306.5 | 103.9 | 215 | 269.3 | 174
723 | 487 | 563.1 | 225.24 | 263.2926 | 349.9 | 314.5 | 315.9 | 195.6 | 636.2 | 44 | 19.4 | 86.4 | 5 | 239.1 | 5.2 | 868.6 | 859.1 | 205.1 | 810.4 | 683.4 | 871.2 | 807.1 | 628.2 | 727.2 | 439.8 | 413.4 | 753.9 | 43.2 | 132.9 | 211.6 | 339.8 | 600.9 | 718.6 | 256.8 | 629.8 | 86.5 | 331.6 | 307.4 | 105.3 | 215.5 | 270 | 174.4
724 | 488 | 562.9 | 225.16 | 263.1991 | 352.4 | 314.2 | 317.1 | 195.9 | 637.4 | 44.1 | 19.4 | 86.5 | 5.1 | 245.1 | 5.6 | 866.1 | 859.8 | 205.9 | 810.4 | 684.6 | 872.4 | 807.7 | 628 | 719.1 | 440.7 | 414.4 | 752.8 | 43.4 | 133.4 | 212.1 | 340.5 | 601.9 | 718.7 | 257.5 | 631.6 | 86.7 | 330.8 | 308.4 | 106.6 | 216 | 270.7 | 174.8
725 | 489 | 563.5 | 225.4 | 263.4796 | 355.2 | 314.5 | 318.4 | 196.2 | 635.3 | 44.1 | 19.4 | 86.8 | 4.8 | 238.3 | 5.4 | 869.1 | 861.4 | 206.5 | 810.5 | 686.3 | 873 | 810.6 | 630 | 717.4 | 441.7 | 415.3 | 754 | 43.6 | 133.7 | 212.6 | 341.3 | 602.3 | 718.3 | 258.2 | 633 | 87 | 330.6 | 309.1 | 107.8 | 216.3 | 271.4 | 175.2
726 | 490 | 564.6 | 225.84 | 263.9939 | 354.5 | 314.8 | 318.6 | 196.6 | 632.8 | 44.2 | 19.4 | 86.9 | 4.8 | 237 | 4.6 | 875.3 | 866.6 | 206.3 | 810.7 | 687.4 | 873.6 | 809.1 | 629.8 | 715.1 | 442.4 | 416.3 | 753.9 | 43.7 | 134.1 | 212.9 | 342 | 602.1 | 718 | 259 | 633.6 | 87.2 | 330.4 | 308.6 | 109 | 216.7 | 272.2 | 175.6
727 | 491 | 567.4 | 226.96 | 265.3032 | 355 | 314.2 | 317.4 | 196.8 | 627.1 | 44.3 | 19.4 | 87.1 | 4.6 | 246.3 | 4.1 | 878.1 | 869.8 | 206.1 | 810.2 | 688.8 | 874.2 | 807.8 | 628.4 | 714.4 | 443.1 | 417.4 | 753.9 | 43.9 | 134.4 | 212.9 | 342.6 | 600.8 | 718.7 | 259.7 | 634.1 | 87.5 | 330.2 | 308.7 | 110.2 | 217.1 | 272.9 | 176
728 | 492 | 565.2 | 226.08 | 264.2745 | 356.5 | 313.9 | 316.3 | 197.1 | 621.4 | 44.4 | 19.4 | 87.4 | 5 | 237.3 | 4.2 | 879 | 871.4 | 206.3 | 810.2 | 690.8 | 874.8 | 807.2 | 626.8 | 720.3 | 443.8 | 418.4 | 755.8 | 44.1 | 134.8 | 213.3 | 343.3 | 600.4 | 716.5 | 260.5 | 633.1 | 87.7 | 330.1 | 309 | 111.3 | 217.6 | 273.6 | 176.4
729 | 493 | 565.1 | 226.04 | 264.2277 | 360.1 | 313.5 | 315 | 197.3 | 612.5 | 44.5 | 19.4 | 87.5 | 4.8 | 238.2 | 3.9 | 882.1 | 873.9 | 205.9 | 810.6 | 692.5 | 876.2 | 805.5 | 624.6 | 717.5 | 444.4 | 419.6 | 754.8 | 44.2 | 135.3 | 213.4 | 343.9 | 598.2 | 706.5 | 261.2 | 629.6 | 88 | 330.7 | 309.2 | 112.4 | 218.2 | 274.3 | 176.8
730 | 494 | 564 | 225.6 | 263.7134 | 361.5 | 312.3 | 314.5 | 198.1 | 602.4 | 44.7 | 19.4 | 87.7 | 5.4 | 240.8 | 3.5 | 885.1 | 875.3 | 205.2 | 810.5 | 693.7 | 877.1 | 805.2 | 624 | 716.9 | 444.9 | 420.4 | 752.8 | 44.4 | 135.7 | 213.6 | 344.6 | 597.1 | 697.1 | 261.9 | 625.2 | 88.2 | 332.5 | 308.6 | 113.5 | 218.6 | 275.1 | 177.3
731 | 495 | 564.6 | 225.84 | 263.9939 | 360.6 | 311.7 | 314.7 | 199.1 | 606.7 | 44.8 | 19.4 | 87.9 | 5.8 | 238.4 | 3.4 | 887.1 | 874.5 | 204.5 | 810.5 | 695.5 | 876.7 | 805.9 | 626.1 | 718.5 | 445.2 | 421.6 | 753.3 | 44.6 | 136 | 214.1 | 345.2 | 602.1 | 696.7 | 262.6 | 627.3 | 88.5 | 333 | 308.7 | 114.5 | 219.1 | 275.8 | 177.7
732 | 496 | 564.6 | 225.84 | 263.9939 | 359.1 | 311.1 | 314.6 | 200.1 | 608.4 | 44.8 | 19.4 | 88 | 5.3 | 242.2 | 4.5 | 888 | 875.3 | 204.5 | 810.1 | 697.4 | 876.8 | 808.6 | 625.8 | 727.7 | 445.5 | 422.5 | 754.5 | 44.8 | 136.4 | 214.4 | 345.8 | 601 | 696.2 | 263.3 | 627.2 | 88.7 | 333 | 309 | 115.5 | 219.8 | 276.5 | 178.2
733 | 497 | 565.5 | 226.2 | 264.4148 | 358.6 | 312 | 315.8 | 200.3 | 601.9 | 44.9 | 19.4 | 88 | 4.8 | 255.9 | 4.6 | 889.1 | 875.7 | 204.4 | 810.6 | 699.1 | 877.6 | 809.2 | 624.7 | 734.7 | 446.1 | 423.5 | 755 | 44.9 | 136.7 | 214.7 | 346.4 | 597.7 | 687.7 | 264 | 622.8 | 89 | 332.8 | 308.6 | 116.3 | 220 | 277.1 | 178.6
734 | 498 | 565.9 | 226.36 | 264.6018 | 358.7 | 313.1 | 316.3 | 200.3 | 595.8 | 45.1 | 19.4 | 88.2 | 5.1 | 257.7 | 4.3 | 889.3 | 876.6 | 204.8 | 811.3 | 700.7 | 878 | 809.6 | 622.5 | 740.7 | 446.9 | 424.5 | 756.4 | 45.1 | 137.1 | 215 | 347.1 | 594.1 | 686.3 | 264.9 | 619.7 | 89.2 | 332.6 | 309 | 117.1 | 220.2 | 277.6 | 178.9
735 | 499 | 564.6 | 225.84 | 263.9939 | 360.2 | 312.7 | 315.1 | 199.8 | 596.6 | 45.1 | 19.3 | 88.3 | 5.1 | 258.1 | 4 | 885 | 871.9 | 205.2 | 810.9 | 702.4 | 878.3 | 809 | 623 | 742.2 | 447.4 | 425.5 | 757.2 | 45.3 | 137.5 | 215.6 | 347.6 | 591.8 | 686.3 | 265.5 | 620 | 89.5 | 332.2 | 308.5 | 117.9 | 220.6 | 278.4 | 179.4
736 | 500 | 564.3 | 225.72 | 263.8537 | 359.8 | 313.2 | 314.7 | 200 | 603.3 | 45.2 | 19.3 | 88.4 | 5.3 | 253.6 | 4.1 | 879.8 | 867.6 | 205.4 | 811.1 | 704 | 878.1 | 808.6 | 625 | 742.6 | 448.1 | 426.4 | 757 | 45.5 | 137.9 | 216.4 | 348.2 | 590.8 | 689.4 | 266.2 | 620.3 | 89.8 | 332.4 | 307.8 | 118.6 | 220.8 | 278.9 | 179.7
737 | 501 | 563.9 | 225.56 | 263.6666 | 359.5 | 314.4 | 314.7 | 200.2 | 608.1 | 45.3 | 19.3 | 88.4 | 5.5 | 252.3 | 4.6 | 875.6 | 866.6 | 205.9 | 811.4 | 704.9 | 878.7 | 807.1 | 627.1 | 732.8 | 449 | 427.6 | 756.2 | 45.7 | 138.2 | 216.7 | 348.8 | 588.2 | 689.3 | 267 | 622.5 | 90 | 332.5 | 307.1 | 119.3 | 221.1 | 279.6 | 180.1
738 | 502 | 564.4 | 225.76 | 263.9004 | 359.9 | 314.6 | 315.1 | 200.4 | 604.3 | 45.4 | 19.3 | 88.5 | 5.4 | 245.6 | 6 | 880.6 | 870.6 | 206.3 | 811 | 706.3 | 879.1 | 808.1 | 626.4 | 731 | 449.8 | 428.6 | 757.4 | 45.8 | 138.6 | 216.7 | 349.4 | 585.5 | 691.2 | 267.7 | 622.1 | 90.3 | 332.2 | 306.7 | 120 | 221.3 | 280.3 | 180.6
739 | 503 | 563.3 | 225.32 | 263.3861 | 362.2 | 314.4 | 315.3 | 201 | 600.5 | 45.5 | 19.3 | 88.5 | 6.3 | 246.2 | 7.3 | 885 | 873.1 | 206.6 | 810.4 | 707 | 880 | 809.1 | 627.5 | 724.2 | 450.7 | 429.7 | 757.5 | 46 | 139 | 217.1 | 350 | 584.2 | 690.2 | 268.5 | 622.8 | 90.6 | 331.9 | 306.1 | 120.6 | 221.6 | 281 | 181
740 | 504 | 562.8 | 225.12 | 263.1523 | 363.1 | 314 | 314.8 | 201.5 | 595 | 45.5 | 19.3 | 88.6 | 6.5 | 245.2 | 8.3 | 891.9 | 874.3 | 206.5 | 810.3 | 708.1 | 880.6 | 808 | 629.4 | 719.9 | 451.7 | 430.9 | 756.9 | 46.2 | 139.4 | 217.1 | 350.7 | 582.8 | 681.7 | 269.3 | 622.7 | 90.9 | 332.8 | 305.5 | 121.3 | 222 | 281.6 | 181.3
741 | 505 | 564.6 | 225.84 | 263.9939 | 361.8 | 313 | 314.9 | 202.4 | 586.8 | 45.6 | 19.3 | 88.6 | 5.7 | 233.3 | 9.4 | 893.9 | 873.6 | 206.9 | 810 | 709.4 | 881.5 | 807.6 | 626.4 | 724.9 | 452.6 | 432.2 | 755.5 | 46.4 | 139.8 | 217.2 | 351.3 | 582.8 | 676.2 | 270 | 620 | 91.1 | 332.7 | 305.2 | 121.9 | 222.4 | 282.2 | 181.8
742 | 506 | 565.2 | 226.08 | 264.2745 | 358.9 | 312.1 | 315 | 203.4 | 583.2 | 45.7 | 19.3 | 88.6 | 5.5 | 247.1 | 8.7 | 896.7 | 875.4 | 207.4 | 809.8 | 710.4 | 882.8 | 808.8 | 624.3 | 731.1 | 453.6 | 433.4 | 757.4 | 46.5 | 140.1 | 217.5 | 351.9 | 581.1 | 672.8 | 270.8 | 617.3 | 91.4 | 332.7 | 305.7 | 122.5 | 222.9 | 282.8 | 182.2
743 | 507 | 565.8 | 226.32 | 264.555 | 356.5 | 311.6 | 315.6 | 203.7 | 580.2 | 45.7 | 19.3 | 88.7 | 5.4 | 243.8 | 8.2 | 896.3 | 877.9 | 207.3 | 809.6 | 711.4 | 883.2 | 809.3 | 623.1 | 731.2 | 454.7 | 434.6 | 757.2 | 46.7 | 140.5 | 217.8 | 352.7 | 578.7 | 677.1 | 271.5 | 614.8 | 91.7 | 333.5 | 305.5 | 123 | 223.2 | 283.5 | 182.7
744 | 508 | 563.9 | 225.56 | 263.6666 | 357.5 | 310.9 | 315.9 | 203.9 | 577.2 | 45.8 | 19.3 | 88.9 | 5.7 | 236.9 | 7.8 | 897.8 | 878.4 | 207.7 | 809.7 | 712.4 | 883.1 | 809.1 | 621.2 | 731.8 | 455.7 | 435.7 | 758.4 | 46.9 | 140.9 | 218 | 353.5 | 575.5 | 666.1 | 272.2 | 611.4 | 92 | 333.7 | 306.1 | 123.6 | 223.7 | 284.2 | 183.1
745 | 509 | 562.8 | 225.12 | 263.1523 | 358.3 | 310.9 | 315.2 | 204.2 | 574.1 | 45.8 | 19.3 | 89 | 5.2 | 251.3 | 7.5 | 895.9 | 880.7 | 208.1 | 809.9 | 713.4 | 882.8 | 808.3 | 619.4 | 734.6 | 456.4 | 436.7 | 757.8 | 47.1 | 141.3 | 218.3 | 354.3 | 573.8 | 657.1 | 272.8 | 609.5 | 92.2 | 333.6 | 306.2 | 124.1 | 223.9 | 284.7 | 183.5
746 | 510 | 564.7 | 225.88 | 264.0407 | 357.5 | 310.8 | 313.7 | 204.9 | 577.1 | 45.9 | 19.3 | 89.1 | 5.5 | 235.9 | 6.5 | 897.5 | 880 | 207.8 | 809.7 | 714.4 | 883.4 | 809.3 | 619.5 | 742.8 | 457.4 | 438 | 757.8 | 47.3 | 141.7 | 218.7 | 355.2 | 572.2 | 660.6 | 273.2 | 612.4 | 92.5 | 334 | 305.5 | 124.7 | 224.2 | 285.3 | 183.9
747 | 511 | 565.4 | 226.16 | 264.368 | 358.2 | 310.5 | 312.4 | 205.6 | 574.2 | 45.9 | 19.3 | 89.3 | 5.4 | 216.2 | 5.4 | 895.8 | 877.3 | 207.6 | 809.8 | 715.6 | 883.4 | 808.7 | 619.2 | 746 | 458.3 | 439 | 759.7 | 47.4 | 142.1 | 219 | 355.9 | 569.2 | 654.2 | 273.7 | 610 | 92.8 | 333.9 | 304.8 | 125.1 | 224.5 | 285.9 | 184.3
748 | 512 | 563.8 | 225.52 | 263.6199 | 358.6 | 309.9 | 312.2 | 206.1 | 570.7 | 46 | 19.3 | 89.4 | 4.8 | 199 | 4.7 | 892.1 | 880.4 | 207.2 | 810.5 | 716.6 | 883.1 | 808 | 618 | 750.7 | 459 | 440.1 | 760.4 | 47.6 | 142.5 | 219 | 356.6 | 566.2 | 649.5 | 274.3 | 608 | 93.1 | 333.4 | 304.2 | 125.6 | 224.8 | 286.4 | 184.7
749 | 513 | 563.4 | 225.36 | 263.4329 | 356.6 | 310.9 | 312.1 | 206.4 | 572 | 46.1 | 19.3 | 89.4 | 5.1 | 241.8 | 4.4 | 890.5 | 878.5 | 207.2 | 810.5 | 717.6 | 883.3 | 807.2 | 617.6 | 755 | 459.9 | 441.4 | 760.2 | 47.8 | 142.9 | 219.4 | 357.3 | 564.4 | 646.6 | 274.9 | 608.8 | 93.4 | 332.6 | 303.5 | 126.1 | 225.1 | 287 | 185
750 | 514 | 562.8 | 225.12 | 263.1523 | 354.8 | 311.3 | 311.9 | 206.9 | 572.2 | 46.1 | 19.3 | 89.4 | 5.3 | 235.7 | 4.2 | 892.1 | 879.9 | 207.7 | 811.1 | 718.6 | 883.1 | 806.8 | 618.5 | 761.3 | 460.9 | 442.6 | 760.6 | 48 | 143.2 | 219.8 | 357.9 | 563 | 647.3 | 275.5 | 608.5 | 93.7 | 332 | 303.1 | 126.5 | 225.4 | 287.6 | 185.4
751 | 515 | 563.4 | 225.36 | 263.4329 | 355.3 | 311.9 | 310.7 | 207 | 572.5 | 46.2 | 19.3 | 89.5 | 4.8 | 230.5 | 3.9 | 887.9 | 879.5 | 208.1 | 811.2 | 719.3 | 882.9 | 805.2 | 618.5 | 762.6 | 462 | 443.7 | 760.5 | 48.2 | 143.6 | 220.1 | 358.4 | 561.7 | 646.5 | 276.2 | 607.8 | 94 | 331.4 | 302.9 | 126.9 | 225.6 | 288.1 | 185.8
752 | 516 | 562.3 | 224.92 | 262.9185 | 354.8 | 312.1 | 311.4 | 207 | 574.6 | 46.2 | 19.3 | 89.5 | 5.1 | 242.6 | 4.2 | 888.5 | 879.1 | 209 | 810.6 | 719.7 | 882.7 | 805.3 | 619.5 | 763.3 | 463 | 444.9 | 761.5 | 48.3 | 143.9 | 220.6 | 359 | 559.7 | 647.6 | 276.9 | 607.3 | 94.3 | 330.9 | 302.6 | 127.3 | 225.8 | 288.7 | 186.1
753 | 517 | 563.4 | 225.36 | 263.4329 | 354.4 | 312.3 | 312.8 | 207.3 | 581.3 | 46.3 | 19.3 | 89.6 | 5.4 | 215.1 | 4.5 | 888 | 878 | 209.9 | 810.3 | 720.4 | 882.9 | 804.8 | 621.9 | 763.2 | 464.4 | 445.9 | 761.9 | 48.5 | 144.3 | 221.3 | 359.5 | 559.5 | 651.5 | 277.6 | 607.3 | 94.6 | 330.1 | 302.1 | 127.7 | 226.1 | 289.2 | 186.5
754 | 518 | 563.6 | 225.44 | 263.5264 | 354.6 | 312.3 | 313.5 | 207.4 | 583.7 | 46.3 | 19.3 | 89.7 | 5.7 | 186.2 | 5.1 | 892.4 | 880.3 | 210.3 | 810.8 | 721.2 | 882.7 | 803 | 622.3 | 759.2 | 465.6 | 447.1 | 760.5 | 48.7 | 144.7 | 221.4 | 360 | 558.4 | 644.3 | 278.3 | 605 | 94.9 | 329.2 | 301.8 | 128.1 | 226.3 | 289.8 | 186.8
755 | 519 | 563.7 | 225.48 | 263.5731 | 355.1 | 312.9 | 313.3 | 207.7 | 581 | 46.4 | 19.3 | 89.9 | 5.6 | 176.8 | 4.3 | 893.6 | 878 | 210.5 | 810.3 | 721.7 | 883.5 | 801.5 | 619.1 | 750.8 | 466.4 | 448.4 | 761.8 | 48.9 | 145 | 221.4 | 360.4 | 557.7 | 634 | 278.9 | 602.4 | 95.2 | 329.5 | 301.7 | 128.5 | 226.7 | 290.3 | 187.2
756 | 520 | 564.7 | 225.88 | 264.0407 | 356.2 | 314 | 313.1 | 207.9 | 573.5 | 46.5 | 19.3 | 90.2 | 5.6 | 220.3 | 3.5 | 895 | 879.4 | 210.1 | 809.8 | 722 | 883.9 | 799.1 | 616.7 | 743.8 | 467.1 | 449.6 | 759.3 | 49.1 | 145.4 | 221.5 | 360.9 | 555.8 | 622 | 279.6 | 600 | 95.5 | 330.7 | 301.4 | 128.9 | 226.9 | 290.9 | 187.5
757 | 521 | 562.6 | 225.04 | 263.0588 | 356.2 | 314.1 | 313.2 | 208.5 | 576.6 | 46.6 | 19.2 | 90.4 | 5.7 | 260.4 | 4 | 891.8 | 880.2 | 209.4 | 808.7 | 722.3 | 884.3 | 798.5 | 617.3 | 745.7 | 467.8 | 450.5 | 759.4 | 49.2 | 145.7 | 221.8 | 361.3 | 557.7 | 620.4 | 280.3 | 600.3 | 95.8 | 330.7 | 301.6 | 129.3 | 227.4 | 291.4 | 188
758 | 522 | 562.7 | 225.08 | 263.1056 | 353.6 | 314.1 | 313.6 | 209.2 | 572.8 | 46.7 | 19.3 | 90.5 | 5.3 | 223.7 | 4.4 | 890.1 | 881.2 | 209.3 | 808 | 723.2 | 884.2 | 798.5 | 619.1 | 749.6 | 468.9 | 451.5 | 759 | 49.4 | 146.1 | 222 | 361.7 | 557.2 | 624.3 | 281 | 602.3 | 96.1 | 330.8 | 301.6 | 129.7 | 227.8 | 292 | 188.4
759 | 523 | 564.9 | 225.96 | 264.1342 | 351.5 | 314.4 | 314 | 209.8 | 573.3 | 46.8 | 19.2 | 90.5 | 5.2 | 213.3 | 4.6 | 891.7 | 882.5 | 209.8 | 807.1 | 723.8 | 883.3 | 797.1 | 620.6 | 748.1 | 470 | 452.6 | 757.9 | 49.6 | 146.5 | 222.3 | 362.1 | 556.7 | 625.5 | 281.7 | 603.5 | 96.5 | 330.6 | 302.3 | 130.1 | 228 | 292.6 | 188.8
760 | 524 | 566 | 226.4 | 264.6486 | 349.8 | 315.8 | 313.4 | 210 | 575.7 | 46.9 | 19.3 | 90.5 | 5.4 | 233.6 | 4.6 | 887.8 | 881.6 | 210.1 | 806.4 | 724.3 | 883 | 797.8 | 623.3 | 755.2 | 471.2 | 453.7 | 757.6 | 49.8 | 146.8 | 222.8 | 362.5 | 555.4 | 628.4 | 282.4 | 604.2 | 96.8 | 330.4 | 302.8 | 130.5 | 228.2 | 293.2 | 189.1
761 | 525 | 565.3 | 226.12 | 264.3213 | 349.2 | 317.1 | 313 | 210 | 575.2 | 47 | 19.3 | 90.6 | 5.1 | 242.1 | 5.7 | 892.3 | 881.1 | 210.2 | 805.8 | 725 | 883.5 | 799.3 | 622.6 | 757.1 | 472.6 | 454.9 | 759.1 | 50 | 147.1 | 223.3 | 363 | 553.8 | 626.1 | 283.1 | 603.6 | 97.2 | 330.4 | 302.9 | 130.9 | 228.4 | 293.8 | 189.5
762 | 526 | 566.4 | 226.56 | 264.8356 | 350 | 317.6 | 313.5 | 210.3 | 575.1 | 47 | 19.2 | 90.6 | 4.8 | 222.1 | 6.1 | 890.1 | 878.9 | 210.9 | 805.1 | 726.3 | 883.6 | 800 | 622.8 | 759.4 | 473.8 | 456.1 | 761.3 | 50.2 | 147.5 | 223.6 | 363.4 | 552 | 623.9 | 283.8 | 601.4 | 97.5 | 330.1 | 303.2 | 131.2 | 228.8 | 294.3 | 189.8
763 | 527 | 564.8 | 225.92 | 264.0875 | 351.6 | 316.9 | 313.3 | 211.1 | 574.5 | 47 | 19.2 | 90.6 | 4.8 | 235.3 | 6.3 | 892.3 | 876.1 | 211.8 | 804.2 | 727.7 | 883.8 | 800.9 | 623.6 | 759.2 | 475 | 457.2 | 761.7 | 50.4 | 147.8 | 223.9 | 363.8 | 550.5 | 623.8 | 284.5 | 600.3 | 97.9 | 329.9 | 303.3 | 131.6 | 229.2 | 294.9 | 190.2
764 | 528 | 564.2 | 225.68 | 263.8069 | 352.5 | 316.3 | 313.4 | 211.9 | 572.8 | 47 | 19.2 | 90.5 | 4.9 | 234.7 | 5.6 | 892.1 | 876.8 | 212.5 | 804.2 | 729.3 | 883.8 | 800.9 | 624.7 | 759.1 | 476.1 | 458.3 | 762.4 | 50.5 | 148.2 | 224.3 | 364.3 | 549.9 | 621.7 | 285.2 | 597.9 | 98.3 | 329.9 | 303.3 | 131.9 | 229.5 | 295.4 | 190.5
765 | 529 | 564.4 | 225.76 | 263.9004 | 352.1 | 317.1 | 314.4 | 212.4 | 572.9 | 47 | 19.2 | 90.5 | 5.4 | 209.6 | 5.1 | 893.5 | 877.8 | 212.4 | 803.3 | 730.1 | 883.7 | 800.6 | 625.9 | 761.2 | 477.4 | 459.5 | 762.1 | 50.7 | 148.6 | 224.6 | 364.7 | 550.1 | 626.4 | 285.9 | 597.7 | 98.6 | 330 | 303.3 | 132.2 | 229.7 | 296 | 190.9
766 | 530 | 563.9 | 225.56 | 263.6666 | 350.7 | 319 | 316.2 | 212.7 | 577.6 | 47.1 | 19.2 | 90.6 | 5.1 | 230 | 4.9 | 885.9 | 874 | 212.2 | 803.1 | 730.9 | 883.4 | 800.1 | 627.6 | 759.5 | 478.8 | 460.8 | 762.3 | 50.9 | 149 | 225.3 | 365.2 | 550.9 | 629.9 | 286.7 | 597.9 | 99 | 330 | 303.2 | 132.5 | 229.9 | 296.5 | 191.2
767 | 531 | 564.6 | 225.84 | 263.9939 | 349.2 | 319.4 | 317.4 | 212.9 | 581.1 | 47.1 | 19.2 | 90.7 | 5.2 | 218.5 | 5.2 | 886.3 | 873 | 212.2 | 803.2 | 732 | 883.4 | 799.3 | 629 | 754.3 | 479.9 | 462 | 762.2 | 51.1 | 149.3 | 225.8 | 365.7 | 551.3 | 625.2 | 287.4 | 595.4 | 99.4 | 329.8 | 302.5 | 132.9 | 230.4 | 297.1 | 191.6
768 | 532 | 564.9 | 225.96 | 264.1342 | 347.1 | 319.3 | 319.3 | 213.4 | 579.2 | 47.2 | 19.2 | 90.8 | 5.4 | 208.2 | 6.4 | 882.7 | 867.1 | 211.4 | 803.1 | 732.4 | 884.1 | 798.3 | 631.4 | 750.6 | 480.7 | 462.9 | 762.8 | 51.3 | 149.6 | 225.6 | 366.2 | 551.7 | 615.8 | 288.2 | 593.2 | 99.8 | 330.3 | 302.6 | 133.2 | 230.8 | 297.7 | 192
769 | 533 | 565.1 | 226.04 | 264.2277 | 347.6 | 319.6 | 319.5 | 214.2 | 574.5 | 47.3 | 19.2 | 90.9 | 5 | 201.8 | 7.2 | 876.9 | 858.9 | 209.7 | 803.6 | 733.3 | 883.4 | 796.2 | 632.1 | 745.3 | 481.3 | 464.1 | 763.2 | 51.5 | 150 | 225.8 | 366.8 | 552.4 | 608.9 | 288.9 | 592.9 | 100.2 | 331.4 | 302.8 | 133.7 | 231.4 | 298.2 | 192.4
770 | 534 | 564.4 | 225.76 | 263.9004 | 348.4 | 319 | 318.1 | 215.4 | 570.9 | 47.4 | 19.2 | 91 | 4.9 | 203.2 | 7.4 | 881.9 | 859.5 | 208.2 | 803.4 | 733.6 | 882.8 | 793.5 | 632.9 | 734.4 | 481.8 | 465.4 | 761.7 | 51.7 | 150.3 | 226.1 | 367.4 | 553.1 | 602.6 | 289.7 | 593.1 | 100.6 | 332.9 | 303.1 | 134.1 | 231.9 | 298.8 | 192.8
771 | 535 | 564.1 | 225.64 | 263.7602 | 348.8 | 318.4 | 316.6 | 216.6 | 570.5 | 47.5 | 19.2 | 91 | 5.6 | 209 | 7.3 | 883.7 | 865.1 | 207.6 | 803.1 | 734.2 | 883.4 | 793.2 | 636.2 | 734 | 482.6 | 466.4 | 760.5 | 51.8 | 150.7 | 226.4 | 368 | 553.1 | 600.2 | 290.4 | 593.3 | 101 | 333.8 | 303.6 | 134.5 | 232.3 | 299.4 | 193.2
772 | 536 | 565.7 | 226.28 | 264.5083 | 349.2 | 318.7 | 316.7 | 217.6 | 571.3 | 47.6 | 19.2 | 91.1 | 5.4 | 234.9 | 7 | 889.8 | 869.9 | 207.2 | 803.2 | 735 | 884.6 | 794.2 | 636.4 | 730.6 | 483.4 | 467.5 | 761.6 | 52 | 151.1 | 226.6 | 368.7 | 552.8 | 597.1 | 291.1 | 593 | 101.4 | 334.2 | 304.9 | 134.8 | 232.9 | 300 | 193.7
773 | 537 | 565.6 | 226.24 | 264.4615 | 350.8 | 318.6 | 317.7 | 218.3 | 575.6 | 47.7 | 19.2 | 91.2 | 4.8 | 243.1 | 6.9 | 888.3 | 866.6 | 206.3 | 803.5 | 735.4 | 883.3 | 791.1 | 638.2 | 715.5 | 484.6 | 468.7 | 759.7 | 52.2 | 151.5 | 227 | 369.5 | 553.7 | 589.3 | 291.8 | 593.6 | 101.7 | 334.8 | 306.7 | 135.2 | 233.5 | 300.6 | 194.1
774 | 538 | 564.3 | 225.72 | 263.8537 | 350.7 | 318.8 | 318.1 | 219.1 | 580.9 | 47.8 | 19.2 | 91.4 | 5 | 214 | 6.4 | 890.6 | 870.2 | 205.8 | 803.9 | 735.8 | 882.3 | 790.3 | 643.7 | 706.7 | 486.8 | 469.7 | 757.6 | 52.4 | 151.8 | 227.5 | 370.5 | 555.1 | 589.4 | 292.5 | 598 | 102.1 | 335.9 | 308.4 | 135.8 | 234.1 | 301.2 | 194.5
775 | 539 | 564.7 | 225.88 | 264.0407 | 349.2 | 318.6 | 318.8 | 219.9 | 577.1 | 47.9 | 19.2 | 91.5 | 4.8 | 228.9 | 5.4 | 891 | 875.3 | 205.6 | 803.9 | 736.1 | 883.1 | 791 | 644.6 | 702.5 | 488.6 | 470.6 | 758 | 52.6 | 152.1 | 227.6 | 371.6 | 554.8 | 588.9 | 293.1 | 598.5 | 102.5 | 336.4 | 309.7 | 136.2 | 234.4 | 301.9 | 195
776 | 540 | 566.4 | 226.56 | 264.8356 | 349 | 318.5 | 319.1 | 220.4 | 570.9 | 48 | 19.2 | 91.5 | 4.5 | 240.1 | 4.6 | 891.6 | 878.8 | 205.4 | 804.1 | 736.9 | 884 | 792 | 644.7 | 708.8 | 490.1 | 471.5 | 758.3 | 52.8 | 152.5 | 227.9 | 372.9 | 553.2 | 588.4 | 293.8 | 594.3 | 102.9 | 336.2 | 310.6 | 136.7 | 234.8 | 302.6 | 195.4
777 | 541 | 566.2 | 226.48 | 264.7421 | 353.9 | 319.1 | 318.4 | 220.3 | 566.2 | 48.1 | 19.2 | 91.7 | 4.7 | 226 | 3.9 | 894.9 | 880.1 | 205.3 | 804.7 | 737.6 | 884.2 | 792.6 | 647.3 | 717.2 | 491.7 | 472.2 | 759.6 | 53 | 152.8 | 228.2 | 374.4 | 551.8 | 590.3 | 294.5 | 592.1 | 103.3 | 335.9 | 310.6 | 137 | 235 | 303.2 | 195.8
778 | 542 | 567.9 | 227.16 | 265.537 | 355.6 | 320.3 | 318.1 | 220 | 562.3 | 48.2 | 19.2 | 91.7 | 5.2 | 190.1 | 3.4 | 895.8 | 881.9 | 205.5 | 805.1 | 738.6 | 884.5 | 793.1 | 641.9 | 725.5 | 498 | 473.1 | 760.3 | 53.2 | 153.2 | 228.5 | 375.8 | 549.8 | 590.9 | 295.2 | 590.6 | 103.7 | 335.7 | 310.6 | 137.4 | 235.2 | 303.8 | 196.1
779 | 543 | 567.3 | 226.92 | 265.2564 | 355.9 | 322.2 | 317.8 | 219.7 | 560.2 | 48.2 | 19.2 | 91.7 | 5.4 | 194.4 | 3.2 | 897.5 | 883.4 | 205.6 | 805.3 | 739.5 | 884.5 | 793.7 | 620.2 | 733.5 | 506.8 | 473.8 | 760.5 | 53.3 | 153.5 | 228.7 | 377 | 548.2 | 591.9 | 295.9 | 589.3 | 104.1 | 335.7 | 310.4 | 137.8 | 235.6 | 304.4 | 196.5
780 | 544 | 565.7 | 226.28 | 264.5083 | 354.1 | 323.2 | 316.8 | 219.8 | 560.7 | 48.3 | 19.2 | 91.7 | 5.2 | 220.8 | 2.9 | 896.1 | 883.9 | 205.8 | 805.7 | 740 | 884.8 | 793.3 | 616.9 | 732.6 | 515.9 | 474.4 | 760.1 | 53.5 | 153.7 | 229.2 | 378.4 | 548 | 597 | 296.5 | 589.2 | 104.4 | 335.9 | 310.2 | 138.3 | 235.8 | 304.9 | 196.8
781 | 545 | 566.6 | 226.64 | 264.9291 | 353.6 | 322.6 | 316.2 | 219.8 | 563.7 | 48.4 | 19.2 | 91.8 | 4.9 | 229.4 | 2.7 | 892.1 | 882 | 206.2 | 806.2 | 740.4 | 884.6 | 792.1 | 618 | 722.2 | 525.8 | 475.2 | 758.3 | 53.7 | 154 | 229.9 | 380.3 | 547.8 | 600.1 | 297.1 | 588.5 | 104.8 | 336 | 309.4 | 138.7 | 236 | 305.4 | 197.2
782 | 546 | 566.8 | 226.72 | 265.0226 | 352.5 | 321.3 | 318.3 | 220 | 574.5 | 48.5 | 19.2 | 91.9 | 5.1 | 241.6 | 2.7 | 887.7 | 879.9 | 207.3 | 806.9 | 740.9 | 883.7 | 792.4 | 624.3 | 719.7 | 535 | 475.9 | 755.8 | 53.9 | 154.4 | 230.7 | 383.6 | 550 | 610.6 | 297.8 | 588.2 | 105.2 | 336.2 | 308.7 | 139.1 | 236.3 | 305.9 | 197.5
783 | 547 | 566.8 | 226.72 | 265.0226 | 351.7 | 320 | 321.5 | 220.8 | 588.1 | 48.5 | 19.2 | 92 | 5.3 | 250.5 | 2.8 | 877.1 | 870.9 | 208.1 | 808.4 | 741.1 | 881.9 | 791.3 | 631.3 | 712.2 | 543.3 | 476.5 | 755.3 | 54.1 | 154.7 | 231.8 | 387.4 | 552.8 | 628.5 | 298.4 | 590.1 | 105.6 | 337.4 | 308.5 | 139.6 | 236.4 | 306.4 | 197.8
784 | 548 | 565.5 | 226.2 | 264.4148 | 350.4 | 319.6 | 325.6 | 221.9 | 601.8 | 48.6 | 19.2 | 92 | 4.9 | 240.4 | 3.1 | 863.8 | 864.4 | 207.4 | 809.8 | 740.8 | 879.2 | 788.7 | 643.6 | 695.6 | 553.2 | 477.4 | 752.3 | 54.3 | 155.1 | 232.4 | 392.1 | 555.6 | 646 | 299 | 597.5 | 105.9 | 338.3 | 308 | 140.1 | 236.5 | 307 | 198.2
785 | 549 | 563.7 | 225.48 | 263.5731 | 349.7 | 319.2 | 328.8 | 223.1 | 605.8 | 48.6 | 19.1 | 92.1 | 5.4 | 229.3 | 3.8 | 869.6 | 870.9 | 206.5 | 811.2 | 740.8 | 878.6 | 789.1 | 656.5 | 695.8 | 563.1 | 478.5 | 750.5 | 54.5 | 155.4 | 232.7 | 396.8 | 555.3 | 652.6 | 299.5 | 599.5 | 106.3 | 339.1 | 308 | 140.6 | 236.8 | 307.6 | 198.7
786 | 550 | 563.1 | 225.24 | 263.2926 | 349.3 | 319.9 | 331.1 | 224 | 607.4 | 48.7 | 19.1 | 92 | 5.6 | 205.9 | 4.1 | 878.4 | 872.6 | 205.3 | 812.1 | 740.6 | 879 | 788.7 | 666.6 | 691.7 | 569.7 | 479.4 | 751.7 | 54.7 | 155.8 | 232.8 | 400.8 | 555.9 | 654.6 | 300.2 | 598.1 | 106.7 | 339.8 | 308 | 141 | 237 | 308.2 | 199.1
787 | 551 | 563.9 | 225.56 | 263.6666 | 348.6 | 320.4 | 332.8 | 225 | 608.9 | 48.8 | 19.1 | 92 | 5.4 | 205.3 | 4 | 879.3 | 872.4 | 204.6 | 813.1 | 740.8 | 879.3 | 788.9 | 675.7 | 694.5 | 575.7 | 480.1 | 750.5 | 54.9 | 156.1 | 233.4 | 405 | 555.7 | 661.2 | 300.8 | 600 | 107.1 | 340.3 | 308.5 | 141.4 | 237.2 | 308.8 | 199.5
788 | 552 | 565.2 | 226.08 | 264.2745 | 348.4 | 320.3 | 333.5 | 225.4 | 610.8 | 48.8 | 19.1 | 92.1 | 5.6 | 227 | 4.9 | 877.6 | 872.4 | 204.1 | 813.9 | 741 | 879.5 | 789.3 | 684.3 | 694.3 | 581.3 | 480.7 | 750.9 | 55.1 | 156.4 | 233.8 | 408.8 | 555.8 | 662.2 | 301.3 | 599.3 | 107.5 | 340.3 | 308 | 141.8 | 237.6 | 309.5 | 199.9
789 | 553 | 566.4 | 226.56 | 264.8356 | 347.2 | 320.2 | 335.5 | 225.6 | 608 | 48.9 | 19.1 | 92.3 | 5.2 | 236.6 | 5.2 | 880.5 | 873.3 | 203.5 | 814.3 | 740.7 | 879.6 | 790.8 | 688.7 | 703.5 | 586 | 481.5 | 753.7 | 55.2 | 156.7 | 234.1 | 412.4 | 555.4 | 659.9 | 302 | 594.7 | 107.8 | 340.1 | 308.5 | 142.3 | 237.9 | 310.1 | 200.3
790 | 554 | 566.6 | 226.64 | 264.9291 | 347.4 | 319.6 | 336.1 | 226 | 610.7 | 48.9 | 19.1 | 92.5 | 5.4 | 217.7 | 5.4 | 871.1 | 867.8 | 202.8 | 814.9 | 740.8 | 879.8 | 790.2 | 695.2 | 702.5 | 589.9 | 482.3 | 753.6 | 55.4 | 157 | 234.5 | 416.5 | 557.4 | 660.1 | 302.7 | 593.7 | 108.2 | 339.9 | 309 | 142.7 | 238.2 | 310.7 | 200.6
791 | 555 | 566.7 | 226.68 | 264.9759 | 349.1 | 319.9 | 335.4 | 226.2 | 609.2 | 49 | 19.1 | 92.5 | 5.6 | 211.3 | 7.1 | 872.5 | 865.1 | 201.8 | 815.4 | 740.7 | 879.5 | 788.1 | 700.2 | 698.6 | 591.5 | 483.1 | 750.9 | 55.6 | 157.3 | 234.7 | 420.4 | 557.8 | 653.3 | 303.3 | 591.4 | 108.6 | 339.4 | 308.5 | 143.1 | 238.5 | 311.2 | 201
792 | 556 | 565.9 | 226.36 | 264.6018 | 348.7 | 319.5 | 335.2 | 226.5 | 606.1 | 49 | 19.1 | 92.6 | 5.7 | 220.4 | 8.2 | 879.8 | 868.6 | 200.8 | 815.4 | 740.9 | 880.1 | 788.8 | 698.3 | 710.4 | 592.1 | 483.9 | 753.4 | 55.8 | 157.7 | 234.8 | 424 | 557.2 | 644.7 | 303.9 | 589.2 | 108.9 | 339.3 | 308.6 | 143.5 | 238.8 | 311.8 | 201.4
793 | 557 | 566.1 | 226.44 | 264.6953 | 348.1 | 319.4 | 335 | 226.8 | 597.4 | 49.1 | 19.1 | 92.8 | 5.4 | 215.3 | 10 | 881.2 | 864.9 | 200.1 | 815.4 | 740.9 | 880.6 | 788.7 | 695 | 712 | 591.3 | 484.6 | 754.1 | 56 | 158 | 235 | 427.1 | 556.8 | 635.5 | 304.5 | 588.5 | 109.3 | 339 | 308.6 | 143.9 | 239.3 | 312.3 | 201.7
794 | 558 | 566 | 226.4 | 264.6486 | 350.4 | 319.3 | 333.3 | 227.2 | 586.9 | 49.2 | 19.1 | 92.9 | 4.7 | 211.5 | 10.6 | 884 | 867.1 | 199.3 | 815.1 | 740.6 | 881.4 | 787.4 | 693.4 | 707.6 | 590.5 | 485.2 | 752.6 | 56.2 | 158.4 | 235.4 | 429.8 | 556.5 | 625.1 | 305 | 586.3 | 109.7 | 338.5 | 308.4 | 144.3 | 239.6 | 312.9 | 202.1
795 | 559 | 565.7 | 226.28 | 264.5083 | 353.1 | 318.7 | 331.6 | 227.4 | 584 | 49.3 | 19.1 | 93.1 | 4.8 | 216.2 | 9.9 | 882.1 | 864.3 | 198.4 | 814.9 | 740.4 | 882.4 | 787 | 695.1 | 702.1 | 591.2 | 485.9 | 753.1 | 56.4 | 158.7 | 236 | 433 | 557.6 | 619.8 | 305.7 | 584.2 | 110.1 | 338 | 308.2 | 144.8 | 239.8 | 313.4 | 202.4
796 | 560 | 564.4 | 225.76 | 263.9004 | 353 | 318.8 | 330.9 | 227.1 | 585.4 | 49.3 | 19.1 | 93.2 | 5.6 | 199.4 | 9 | 886.9 | 866.8 | 198.2 | 815.1 | 740.6 | 882.3 | 788.6 | 696 | 708.7 | 592.7 | 486.2 | 754.1 | 56.6 | 159 | 236.2 | 436.6 | 558.1 | 619.7 | 306.3 | 584.7 | 110.4 | 337.8 | 308 | 145.1 | 240.1 | 314 | 202.8
797 | 561 | 564.5 | 225.8 | 263.9472 | 352.6 | 318.6 | 329.6 | 227.3 | 585.2 | 49.4 | 19.1 | 93.2 | 5.5 | 213 | 9 | 891.5 | 868 | 198 | 815.3 | 740.9 | 882.9 | 787.6 | 696.8 | 711.6 | 593.2 | 486.6 | 755.8 | 56.8 | 159.3 | 236.2 | 439.8 | 558.6 | 613.4 | 306.9 | 585.3 | 110.8 | 337.4 | 308.2 | 145.6 | 240.4 | 314.5 | 203.1
798 | 562 | 563.6 | 225.44 | 263.5264 | 351.9 | 318.4 | 328 | 227.2 | 578.9 | 49.5 | 19.1 | 93.2 | 5.1 | 215.4 | 8.7 | 889.8 | 865.7 | 197.4 | 815.5 | 740.8 | 883.8 | 785.2 | 696 | 712.3 | 591.8 | 487 | 755.2 | 56.9 | 159.6 | 236.4 | 442.6 | 557.2 | 605.4 | 307.6 | 583 | 111.2 | 337.1 | 308.2 | 146 | 240.6 | 315 | 203.5
799 | 563 | 564 | 225.6 | 263.7134 | 350.8 | 317.6 | 327.5 | 227.3 | 570 | 49.6 | 19.1 | 93.1 | 5.1 | 209.3 | 9.6 | 890.2 | 867.5 | 197 | 815.4 | 740.8 | 884.3 | 783.5 | 694 | 715.7 | 589.7 | 487.7 | 754.2 | 57.1 | 159.9 | 236.6 | 445.1 | 555.5 | 598.2 | 308.2 | 580.5 | 111.6 | 337.2 | 307.9 | 146.4 | 240.8 | 315.6 | 203.8
800 | 564 | 566.4 | 226.56 | 264.8356 | 350.2 | 317 | 327.1 | 227.5 | 565.4 | 49.7 | 19.1 | 93.2 | 5.7 | 212.2 | 9.6 | 890 | 872 | 196.4 | 815 | 741.3 | 884.7 | 783.5 | 695 | 722.4 | 588.7 | 488.4 | 755.5 | 57.3 | 160.3 | 236.9 | 447.9 | 555.6 | 602.6 | 308.8 | 581 | 112 | 337.3 | 308 | 146.9 | 241 | 316.1 | 204.2
801 | 565 | 566.7 | 226.68 | 264.9759 | 350.8 | 317.2 | 325.5 | 228.1 | 564.5 | 49.8 | 19.1 | 93.4 | 5.3 | 200.4 | 9.1 | 889.6 | 873.2 | 196 | 814.5 | 741.6 | 884.5 | 783.7 | 694.4 | 728.8 | 587.7 | 488.9 | 756.2 | 57.5 | 160.6 | 237.1 | 451.3 | 555.1 | 598.8 | 309.4 | 581.7 | 112.4 | 338.1 | 307.9 | 147.2 | 241.3 | 316.6 | 204.5
802 | 566 | 566.4 | 226.56 | 264.8356 | 350.7 | 317.4 | 323.7 | 228.6 | 560.8 | 49.9 | 19.1 | 93.6 | 5.6 | 210.6 | 8.2 | 885.5 | 872.8 | 195.2 | 814.3 | 742 | 884 | 783.6 | 692 | 733.2 | 586.4 | 489.4 | 757.2 | 57.7 | 160.9 | 237.3 | 455.2 | 553.8 | 595 | 310 | 581.3 | 112.8 | 337.7 | 308 | 147.7 | 241.7 | 317.1 | 204.9
803 | 567 | 564.8 | 225.92 | 264.0875 | 350.2 | 317.2 | 322.9 | 229 | 556.9 | 50 | 19.1 | 93.8 | 5.7 | 215 | 6.3 | 884 | 875.9 | 195 | 814.5 | 742.2 | 883.3 | 784.1 | 690.9 | 740.3 | 585.3 | 490.4 | 758.6 | 57.9 | 161.2 | 237.5 | 458.1 | 552.7 | 592.8 | 310.5 | 579.9 | 113.2 | 337.5 | 308 | 148.1 | 241.8 | 317.6 | 205.3
804 | 568 | 564.7 | 225.88 | 264.0407 | 350.9 | 317.4 | 321.8 | 229 | 556.9 | 50 | 19.1 | 93.9 | 5.3 | 223.2 | 5.1 | 885 | 876.6 | 195.4 | 814.3 | 742.6 | 882.7 | 785.5 | 690.7 | 746.8 | 585.7 | 490.9 | 759.9 | 58.1 | 161.6 | 237.9 | 461.1 | 552.1 | 596.5 | 311.2 | 580.4 | 113.5 | 337.3 | 307.8 | 148.6 | 242 | 318.1 | 205.6
805 | 569 | 564.1 | 225.64 | 263.7602 | 351.7 | 317.5 | 321.4 | 229.3 | 561.8 | 50.1 | 19.1 | 94 | 5.7 | 227.1 | 5.2 | 887 | 879.7 | 196 | 814.4 | 743.1 | 882.4 | 786.3 | 690.7 | 751.9 | 587.3 | 491.7 | 760.9 | 58.3 | 161.9 | 238.7 | 464.5 | 553.6 | 603.4 | 311.9 | 582.5 | 113.9 | 337 | 307.8 | 149 | 242.3 | 318.6 | 205.9
806 | 570 | 564.3 | 225.72 | 263.8537 | 351.7 | 317.6 | 322 | 229.6 | 571.1 | 50.1 | 19.1 | 94.1 | 5.5 | 216.9 | 5.2 | 886.8 | 878.2 | 197.2 | 814.7 | 743.4 | 881.7 | 784.7 | 693.3 | 746.2 | 588.8 | 492.5 | 758.7 | 58.5 | 162.2 | 239.7 | 468.6 | 555.2 | 613 | 312.5 | 583.7 | 114.3 | 336.9 | 307.6 | 149.5 | 242.4 | 319.1 | 206.2
807 | 571 | 564.9 | 225.96 | 264.1342 | 350.5 | 317.1 | 323.9 | 229.9 | 581.5 | 50.2 | 19.1 | 94.2 | 5.6 | 216.7 | 4.5 | 889.7 | 874.5 | 197.6 | 815 | 743.8 | 881.1 | 784 | 697.6 | 743.2 | 591.6 | 493.3 | 757.3 | 58.7 | 162.5 | 240.3 | 473.6 | 557.8 | 627.8 | 313.3 | 585 | 114.7 | 337.2 | 307.5 | 150 | 242.6 | 319.6 | 206.6
808 | 572 | 565.4 | 226.16 | 264.368 | 349.1 | 316.9 | 324.9 | 230.7 | 590.9 | 50.2 | 19.1 | 94.2 | 5.3 | 247.4 | 4 | 887.5 | 872.5 | 198.5 | 815.1 | 743.7 | 879.8 | 781.2 | 704 | 729.8 | 593.5 | 494.2 | 756.8 | 58.9 | 162.8 | 241 | 478.2 | 559.5 | 643.6 | 314.1 | 587.4 | 115.1 | 337.4 | 307.2 | 150.5 | 242.8 | 320.1 | 207
809 | 573 | 565.6 | 226.24 | 264.4615 | 349.2 | 317.7 | 326.2 | 231.6 | 604.1 | 50.2 | 19.1 | 94.2 | 5.3 | 258 | 5.2 | 877.7 | 865.8 | 200 | 815 | 743.8 | 878.5 | 778.4 | 715.4 | 717.8 | 597.3 | 495.1 | 754 | 59.1 | 163.1 | 241.9 | 484 | 562.2 | 667.6 | 315 | 596 | 115.4 | 338.5 | 307.2 | 151 | 243.1 | 320.7 | 207.3
810 | 574 | 567.6 | 227.04 | 265.3967 | 350.4 | 318 | 329.2 | 232.8 | 609 | 50.2 | 19.1 | 94.4 | 5.1 | 224.5 | 5 | 871.9 | 863.7 | 200.8 | 816.3 | 744.6 | 878.1 | 777.6 | 722.2 | 714.6 | 600.8 | 496 | 750.9 | 59.2 | 163.4 | 242.2 | 489.3 | 564 | 671.6 | 315.9 | 598.2 | 115.8 | 339.4 | 307.2 | 151.6 | 243.4 | 321.3 | 207.7
811 | 575 | 565.3 | 226.12 | 264.3213 | 350.4 | 318.7 | 331.4 | 233.9 | 608 | 50.2 | 19.1 | 94.5 | 4.8 | 175.9 | 4.1 | 862 | 856.8 | 201 | 816.9 | 744.7 | 877.1 | 776.9 | 722.9 | 707.3 | 602.5 | 496.6 | 752.3 | 59.4 | 163.7 | 242.3 | 493.4 | 565 | 678.7 | 316.8 | 598.4 | 116.2 | 340.1 | 307.7 | 152.1 | 243.6 | 321.8 | 208.1
812 | 576 | 564.1 | 225.64 | 263.7602 | 349.5 | 319.2 | 332.4 | 234.7 | 610.5 | 50.2 | 19.1 | 94.5 | 5 | 207.3 | 3.7 | 851.5 | 847.6 | 200.7 | 817 | 744.3 | 875.8 | 774.4 | 727.8 | 694.7 | 605.1 | 497.5 | 750.3 | 59.6 | 164.1 | 243.1 | 497.9 | 566.4 | 684.7 | 317.6 | 600.1 | 116.6 | 341.1 | 308 | 152.6 | 243.9 | 322.4 | 208.5
813 | 577 | 562.7 | 225.08 | 263.1056 | 349.1 | 319.5 | 334.6 | 235.6 | 612 | 50.3 | 19.1 | 94.6 | 5.6 | 196.5 | 5 | 849.9 | 843 | 200 | 817.1 | 744.3 | 875 | 773.1 | 732.4 | 686.3 | 607.1 | 498.5 | 748.3 | 59.8 | 164.4 | 243.4 | 502.1 | 567.7 | 695.4 | 318.4 | 601.4 | 117 | 342 | 308.3 | 153.2 | 244.3 | 323 | 208.9
814 | 578 | 560.7 | 224.28 | 262.1704 | 349.3 | 319.1 | 335.3 | 236.4 | 611.8 | 50.3 | 19 | 94.6 | 5.8 | 212.5 | 7.1 | 859.7 | 846.3 | 199.1 | 816.9 | 743.9 | 875.1 | 774.5 | 732.8 | 692.3 | 608.9 | 499.2 | 748.2 | 60 | 164.7 | 243.5 | 506 | 567.1 | 698.8 | 319.1 | 600.7 | 117.3 | 342.2 | 308.8 | 153.7 | 244.6 | 323.6 | 209.3
815 | 579 | 561.2 | 224.48 | 262.4042 | 349.6 | 318.8 | 335 | 236.7 | 607.4 | 50.4 | 19.1 | 94.6 | 6.1 | 216.3 | 7.5 | 866.3 | 848.8 | 198 | 816.1 | 743.9 | 875.8 | 776.3 | 728.2 | 700.3 | 608 | 499.8 | 750.1 | 60.2 | 165.1 | 243.7 | 508.5 | 566.5 | 690.1 | 319.8 | 596.7 | 117.7 | 341.9 | 309 | 154.1 | 244.9 | 324.1 | 209.6
816 | 580 | 563.5 | 225.4 | 263.4796 | 350.3 | 318.5 | 334 | 237.1 | 601.4 | 50.5 | 19 | 94.6 | 6.3 | 219.3 | 8.3 | 870.5 | 849.4 | 197.1 | 815.7 | 744 | 876.1 | 777 | 724.8 | 702.8 | 605.6 | 500.5 | 751 | 60.4 | 165.4 | 244 | 510.2 | 565 | 679.7 | 320.5 | 593 | 118.1 | 342.1 | 308.6 | 154.6 | 245.4 | 324.6 | 210
817 | 581 | 563.9 | 225.56 | 263.6666 | 350.3 | 318.1 | 333 | 237.4 | 595.3 | 50.5 | 19 | 94.5 | 6.1 | 208.3 | 9.1 | 873.2 | 846.9 | 196.1 | 815 | 744.1 | 876.3 | 777.2 | 720.8 | 702.3 | 602.9 | 501.3 | 753.4 | 60.6 | 165.8 | 244.2 | 511.7 | 564.9 | 666.4 | 321.1 | 588.9 | 118.5 | 342 | 308.6 | 155.1 | 245.7 | 325.1 | 210.4
818 | 582 | 566.4 | 226.56 | 264.8356 | 349.8 | 318.6 | 331.9 | 237.8 | 592.1 | 50.6 | 19 | 94.4 | 5.9 | 223.2 | 8.5 | 875.5 | 850.5 | 196.3 | 814.3 | 744.3 | 876.1 | 777.1 | 717.6 | 705.8 | 601.4 | 501.9 | 755 | 60.8 | 166.1 | 244.5 | 512.7 | 564.7 | 658.3 | 321.6 | 588.8 | 118.9 | 341.7 | 308.9 | 155.6 | 245.9 | 325.4 | 210.7
819 | 583 | 566.3 | 226.52 | 264.7888 | 350 | 319.3 | 331.7 | 238 | 587.6 | 50.7 | 19 | 94.4 | 5.7 | 212.2 | 7.5 | 876.4 | 853.6 | 195.8 | 814.1 | 744.9 | 876 | 777.6 | 714.5 | 711.7 | 602.2 | 502.7 | 753.8 | 61 | 166.5 | 244.5 | 513.9 | 566.5 | 652.5 | 322.3 | 591.5 | 119.2 | 341.9 | 309.3 | 156.1 | 246.3 | 325.7 | 211
820 | 584 | 563.2 | 225.28 | 263.3393 | 350.4 | 319.6 | 330.8 | 238.6 | 581.7 | 50.7 | 19 | 94.3 | 5.4 | 218.6 | 6.5 | 867.6 | 848.6 | 194.8 | 814.4 | 745.4 | 874.7 | 776.4 | 710.3 | 706.3 | 601.2 | 503.3 | 756.1 | 61.2 | 166.9 | 244.7 | 514.9 | 568.2 | 641.4 | 322.9 | 590.3 | 119.6 | 342.6 | 310.2 | 156.7 | 246.8 | 326 | 211.4
821 | 585 | 563.9 | 225.56 | 263.6666 | 351.6 | 319.7 | 329.4 | 239.3 | 574.9 | 50.8 | 19 | 94.2 | 5.2 | 242.6 | 5.4 | 864.2 | 850.3 | 194.4 | 815.3 | 745.9 | 872.7 | 772.8 | 705.6 | 697.9 | 599.4 | 503.8 | 753.5 | 61.4 | 167.2 | 244.9 | 515.5 | 567.1 | 628.8 | 323.3 | 587.4 | 120 | 343.4 | 310.9 | 157.3 | 247.3 | 326.5 | 211.8
822 | 586 | 563.9 | 225.56 | 263.6666 | 353.1 | 319.5 | 328.4 | 240.5 | 567.6 | 50.9 | 19 | 94.1 | 5.7 | 230.2 | 4.9 | 869 | 853.6 | 193.6 | 816.5 | 745.6 | 872.7 | 769.9 | 703 | 697 | 597.3 | 504.5 | 752.3 | 61.5 | 167.6 | 245.1 | 516.7 | 565.9 | 621.4 | 323.8 | 585.1 | 120.4 | 343.5 | 312 | 157.8 | 247.9 | 327 | 212.2
823 | 587 | 564.8 | 225.92 | 264.0875 | 353.9 | 319.8 | 328 | 241 | 566.4 | 51 | 19 | 94.2 | 5.8 | 206.1 | 4.8 | 874.8 | 855.3 | 193.1 | 817.3 | 745.7 | 872.8 | 768.9 | 701.3 | 699.8 | 596.2 | 504.9 | 752.4 | 61.7 | 167.8 | 245.4 | 518.1 | 567.2 | 616.8 | 324.3 | 584.3 | 120.8 | 343.7 | 313.2 | 158.4 | 248.4 | 327.5 | 212.6
824 | 588 | 563.4 | 225.36 | 263.4329 | 356.8 | 321.7 | 329.3 | 241.1 | 565.9 | 51 | 19 | 94.2 | 4.9 | 203.4 | 5.6 | 880.9 | 855.9 | 191.8 | 817.7 | 745.9 | 873.4 | 767.9 | 699.1 | 693 | 595.5 | 505.4 | 751.9 | 61.9 | 168.1 | 245.7 | 519.2 | 569.4 | 608.7 | 325 | 584.2 | 121.2 | 344.2 | 314.3 | 159 | 248.8 | 328.1 | 212.9
825 | 589 | 564.1 | 225.64 | 263.7602 | 356.5 | 323.1 | 329.3 | 241.2 | 564.1 | 51.1 | 19 | 94.2 | 5 | 199.6 | 5 | 879.1 | 854.2 | 190.8 | 817.9 | 746.3 | 875.1 | 766.3 | 696.7 | 686.2 | 593.8 | 506.3 | 751.2 | 62.1 | 168.5 | 245.9 | 520.5 | 568.8 | 600.4 | 325.5 | 581.5 | 121.6 | 344.5 | 314.3 | 159.6 | 249 | 328.6 | 213.3
826 | 590 | 564.2 | 225.68 | 263.8069 | 356.7 | 323.4 | 327.9 | 241.9 | 562.2 | 51.2 | 19 | 94.3 | 5.8 | 236.8 | 4.6 | 876.9 | 854.8 | 189.9 | 818.3 | 746.5 | 875.9 | 765 | 694.3 | 686.2 | 592.7 | 507 | 751.9 | 62.3 | 168.8 | 246.1 | 521.3 | 567.7 | 592.3 | 326.1 | 580.4 | 122 | 344.8 | 314.9 | 160.2 | 249.2 | 329.2 | 213.7
827 | 591 | 564.9 | 225.96 | 264.1342 | 356.6 | 325 | 327.5 | 242.4 | 558.7 | 51.2 | 19 | 94.4 | 5.5 | 238.3 | 4.7 | 878.5 | 854.8 | 189 | 819 | 746.7 | 875.8 | 763.5 | 692.3 | 683.8 | 592.7 | 507.8 | 751.1 | 62.5 | 169.1 | 246.3 | 521.5 | 568.4 | 583.5 | 326.6 | 579.4 | 122.3 | 345.7 | 315.7 | 160.6 | 249.6 | 329.7 | 214
828 | 592 | 564.2 | 225.68 | 263.8069 | 356.9 | 325 | 326.4 | 243.1 | 555.8 | 51.3 | 19 | 94.6 | 4.6 | 239.4 | 5.3 | 873.6 | 853.2 | 188.3 | 820.2 | 746.7 | 874.4 | 763.3 | 690.6 | 685 | 592.6 | 508.6 | 750.8 | 62.7 | 169.4 | 246.5 | 522.6 | 569.2 | 579 | 327.1 | 579.5 | 122.7 | 345.7 | 316.7 | 161.2 | 250.1 | 330.1 | 214.4
829 | 593 | 566.2 | 226.48 | 264.7421 | 358 | 324.6 | 325.7 | 244.1 | 554 | 51.4 | 19 | 94.7 | 4.9 | 237.8 | 6.1 | 871.7 | 856.7 | 187.5 | 821.5 | 746.4 | 871.6 | 760.9 | 688.1 | 675.9 | 592.6 | 509.2 | 750.8 | 62.9 | 169.7 | 246.7 | 523.7 | 570 | 576.6 | 327.6 | 580.9 | 123.1 | 346.1 | 317.6 | 161.7 | 250.6 | 330.6 | 214.8
830 | 594 | 566.2 | 226.48 | 264.7421 | 359.3 | 325.3 | 326.1 | 245.1 | 555.1 | 51.5 | 19 | 94.8 | 4.5 | 204.5 | 6.2 | 873.9 | 857 | 186.6 | 821.4 | 745.8 | 870.1 | 758 | 685.5 | 666.8 | 592.8 | 509.6 | 748.2 | 63.1 | 170.1 | 247 | 524.5 | 570 | 570.9 | 328.2 | 580.6 | 123.5 | 346.7 | 318.2 | 162.3 | 250.9 | 331.2 | 215.3
831 | 595 | 565.8 | 226.32 | 264.555 | 359.8 | 326.1 | 326.5 | 245.3 | 557.3 | 51.5 | 19 | 94.8 | 5.2 | 207 | 5.7 | 868.5 | 854.5 | 186.3 | 821.3 | 746.2 | 869.4 | 757.2 | 685.6 | 663.6 | 594.1 | 510.1 | 747.1 | 63.3 | 170.4 | 247.4 | 525.8 | 571 | 566.8 | 328.7 | 580.3 | 123.8 | 347.7 | 319.1 | 162.9 | 251.3 | 331.7 | 215.6
832 | 596 | 565.8 | 226.32 | 264.555 | 359.4 | 326.6 | 327.2 | 245.5 | 559.5 | 51.6 | 19 | 94.9 | 5.1 | 223.5 | 5 | 871.8 | 855.8 | 186.4 | 821.3 | 746.7 | 868.7 | 757.1 | 684.3 | 662.1 | 594.3 | 510.5 | 748.1 | 63.5 | 170.7 | 247.6 | 527 | 573.2 | 564.6 | 329.1 | 580.5 | 124.2 | 349.2 | 319.7 | 163.6 | 251.8 | 332.3 | 216.1
833 | 597 | 565.5 | 226.2 | 264.4148 | 358.3 | 326.6 | 328.3 | 246.1 | 556.8 | 51.7 | 19 | 95.2 | 4.5 | 243.3 | 4.7 | 876.3 | 865.4 | 186.6 | 821.5 | 747 | 868.4 | 757.6 | 681.6 | 665.5 | 593.9 | 511.3 | 747 | 63.7 | 171.1 | 247.9 | 527.9 | 573 | 563.5 | 329.7 | 580.2 | 124.6 | 350.3 | 320.3 | 164.2 | 252.2 | 333 | 216.5
834 | 598 | 565 | 226 | 264.181 | 358.6 | 326.7 | 328.6 | 246.8 | 557.6 | 51.7 | 19 | 95.3 | 4.7 | 241.9 | 4.9 | 881.8 | 869.4 | 187 | 821 | 747.5 | 869 | 759.6 | 680.9 | 680.5 | 593.8 | 511.9 | 746.4 | 63.9 | 171.4 | 248.1 | 529.2 | 570.9 | 568.7 | 330.2 | 579.3 | 125 | 350.6 | 321.1 | 164.9 | 252.4 | 333.6 | 216.9
835 | 599 | 564.2 | 225.68 | 263.8069 | 361.2 | 327.8 | 328.3 | 246.8 | 562.2 | 51.8 | 19 | 95.4 | 4.7 | 224.2 | 4.6 | 884.1 | 872.9 | 187.4 | 821.4 | 748.5 | 870.3 | 761.8 | 680.1 | 694.1 | 594 | 512.4 | 749.1 | 64.1 | 171.7 | 248.5 | 530.7 | 568.5 | 573.2 | 330.7 | 580.4 | 125.4 | 351.3 | 321.7 | 165.5 | 252.7 | 334.1 | 217.2
836 | 600 | 563.5 | 225.4 | 263.4796 | 361.6 | 329.5 | 328.1 | 246.5 | 565.6 | 51.8 | 19 | 95.5 | 4.9 | 228.2 | 5.2 | 884 | 874.3 | 187.9 | 821.9 | 749.4 | 871.1 | 762.8 | 678.6 | 698.7 | 593.7 | 513.1 | 749.5 | 64.3 | 172 | 248.7 | 531.4 | 567.6 | 576.5 | 331.1 | 579.6 | 125.8 | 351.1 | 321.4 | 166 | 253.1 | 334.7 | 217.6
837 | 601 | 563.4 | 225.36 | 263.4329 | 360.5 | 330.3 | 328.2 | 246.3 | 565 | 51.9 | 19 | 95.6 | 4.7 | 219.5 | 5.8 | 887 | 874 | 187.4 | 821.6 | 749.8 | 872.5 | 763.4 | 678 | 706.1 | 593.4 | 513.9 | 750 | 64.5 | 172.4 | 248.8 | 531.4 | 566.2 | 577.2 | 331.5 | 578 | 126.1 | 350.5 | 321.2 | 166.5 | 253.3 | 335.2 | 218
838 | 602 | 565.1 | 226.04 | 264.2277 | 362.2 | 331.5 | 328 | 246.1 | 564.1 | 51.9 | 19 | 95.7 | 5 | 208.1 | 6.4 | 888.8 | 875.1 | 187.3 | 820.7 | 750 | 873.7 | 763.3 | 676.6 | 709.8 | 593.3 | 514.5 | 751.4 | 64.7 | 172.8 | 249.1 | 531.4 | 565.9 | 578 | 331.9 | 576.6 | 126.5 | 350.4 | 320.6 | 166.8 | 253.5 | 335.7 | 218.3
839 | 603 | 565.5 | 226.2 | 264.4148 | 362.4 | 332.3 | 327.7 | 246.1 | 562 | 52 | 19 | 95.7 | 5 | 213.3 | 6.8 | 886.9 | 872.7 | 187.3 | 820 | 750.1 | 874.6 | 762.7 | 674.9 | 714.3 | 592.8 | 515.2 | 751.4 | 64.9 | 173.1 | 249.3 | 531 | 563.3 | 575.9 | 332.4 | 574.4 | 126.9 | 350.2 | 320 | 167.3 | 253.8 | 336.1 | 218.6
840 | 604 | 565.4 | 226.16 | 264.368 | 363 | 331.7 | 328.3 | 246.4 | 561 | 52 | 19 | 95.7 | 4.3 | 212.9 | 6.7 | 887.6 | 869.4 | 187 | 820.1 | 751.2 | 875.3 | 762.7 | 674.4 | 716.9 | 592.9 | 516 | 754 | 65.1 | 173.5 | 249.5 | 530.7 | 562.9 | 575.2 | 333 | 573.9 | 127.2 | 349.9 | 320.1 | 167.8 | 254.1 | 336.5 | 219
841 | 605 | 564.8 | 225.92 | 264.0875 | 363.4 | 330.8 | 327.2 | 247 | 559.2 | 52 | 19 | 95.7 | 4.8 | 224.2 | 6.4 | 881.2 | 861 | 186.4 | 820 | 751.3 | 874.2 | 761.2 | 674.1 | 706.5 | 593.9 | 516.9 | 753.8 | 65.3 | 173.8 | 249.8 | 530.3 | 564.5 | 571.7 | 333.5 | 576.5 | 127.6 | 349.9 | 320.9 | 168.3 | 254.7 | 336.9 | 219.3
842 | 606 | 564.2 | 225.68 | 263.8069 | 363.3 | 330.1 | 325.9 | 247.5 | 555.7 | 52.1 | 19 | 95.6 | 4.6 | 231.6 | 6.2 | 876.9 | 856.5 | 186.3 | 820.1 | 750.9 | 873 | 757.2 | 672.8 | 698.7 | 594.7 | 517.9 | 751.7 | 65.5 | 174.1 | 250 | 530 | 566 | 566.3 | 333.9 | 577.6 | 128 | 350.3 | 321.4 | 168.8 | 255.1 | 337.4 | 219.7
843 | 607 | 564.9 | 225.96 | 264.1342 | 362.6 | 329.7 | 325.9 | 248.8 | 553.8 | 52.2 | 18.9 | 95.6 | 5.2 | 230.5 | 6 | 879.4 | 858.9 | 185.9 | 820.1 | 750.9 | 872.6 | 754.2 | 672 | 689.2 | 596.8 | 518.6 | 749.6 | 65.7 | 174.4 | 250.3 | 530.4 | 567.1 | 562.1 | 334.4 | 577.5 | 128.4 | 351.2 | 322.2 | 169.4 | 255.4 | 337.9 | 220.1
844 | 608 | 565 | 226 | 264.181 | 362.3 | 329.9 | 327.2 | 249.9 | 553.4 | 52.2 | 18.9 | 95.5 | 5.4 | 232.5 | 5.3 | 878.3 | 860.7 | 185.4 | 820.5 | 751.2 | 872.3 | 751.6 | 671.1 | 683.4 | 597.4 | 519.2 | 748 | 65.9 | 174.8 | 250.5 | 530.2 | 566.2 | 560.9 | 334.8 | 578.5 | 128.8 | 352.1 | 323 | 170.1 | 255.7 | 338.5 | 220.5
845 | 609 | 565.3 | 226.12 | 264.3213 | 362.1 | 329.7 | 328 | 250.7 | 550.7 | 52.3 | 18.9 | 95.5 | 5.3 | 236.2 | 4.6 | 881.1 | 863.5 | 185.1 | 820.5 | 751 | 873 | 752.9 | 671.3 | 687 | 597.3 | 519.9 | 746.3 | 66.1 | 175.2 | 250.7 | 529.7 | 565.4 | 563.8 | 335.4 | 576.7 | 129.1 | 352.5 | 323.4 | 170.7 | 256 | 339.1 | 220.9
846 | 610 | 566.1 | 226.44 | 264.6953 | 364.7 | 329.8 | 327.1 | 250.1 | 553.9 | 52.4 | 18.9 | 95.7 | 5.4 | 196.6 | 5.7 | 882.2 | 865.9 | 185.7 | 820.5 | 751.7 | 873.5 | 755.3 | 671.9 | 696.8 | 598.3 | 520.8 | 748.2 | 66.3 | 175.5 | 251.2 | 530.1 | 565.8 | 572.5 | 335.9 | 577.2 | 129.5 | 352.3 | 323.9 | 171.2 | 256.2 | 339.7 | 221.3
847 | 611 | 566 | 226.4 | 264.6486 | 365.3 | 331.2 | 325.7 | 250 | 555.5 | 52.4 | 18.9 | 95.9 | 4.9 | 219 | 6.7 | 885.2 | 867.9 | 185.5 | 820.3 | 751.8 | 873.8 | 757.6 | 672.3 | 710.6 | 599 | 521.6 | 749.2 | 66.5 | 175.8 | 251.7 | 530.1 | 565.3 | 576.1 | 336.3 | 576 | 129.9 | 351.8 | 324.7 | 171.7 | 256.3 | 340.2 | 221.6
848 | 612 | 565.7 | 226.28 | 264.5083 | 365.2 | 332 | 325.8 | 250 | 560.3 | 52.5 | 18.9 | 95.9 | 5.3 | 221.3 | 6.5 | 883.6 | 868.2 | 185.3 | 820.5 | 752.4 | 874.3 | 759.4 | 672.2 | 714.3 | 599.1 | 522.4 | 750.8 | 66.7 | 176.1 | 252 | 530.5 | 566.2 | 580.9 | 336.7 | 575.5 | 130.3 | 351.4 | 324.6 | 172.1 | 256.4 | 340.7 | 222
849 | 613 | 564.5 | 225.8 | 263.9472 | 366.2 | 332.8 | 326.8 | 249.9 | 565 | 52.5 | 18.9 | 96 | 5.3 | 214 | 7.8 | 874.4 | 863.1 | 185.4 | 820.8 | 754 | 874.8 | 758.5 | 671.7 | 709.9 | 599.7 | 523.4 | 752.2 | 66.9 | 176.4 | 252.1 | 529.9 | 566.6 | 577.7 | 337.2 | 574.1 | 130.6 | 351.1 | 324.1 | 172.6 | 256.7 | 341.1 | 222.3
850 | 614 | 566.9 | 226.76 | 265.0694 | 368.9 | 332.7 | 326.8 | 250.3 | 563.8 | 52.6 | 18.9 | 96.2 | 5.4 | 207.4 | 9.9 | 865.2 | 859.2 | 185.7 | 821 | 754.3 | 874.8 | 756 | 670.1 | 701.2 | 599.7 | 524.2 | 751.2 | 67.2 | 176.7 | 252.3 | 529.4 | 566.5 | 574.5 | 337.8 | 573.9 | 131 | 351 | 323.7 | 173.1 | 257.2 | 341.6 | 222.6
851 | 615 | 566.6 | 226.64 | 264.9291 | 370.4 | 331.9 | 326.3 | 251.4 | 564 | 52.6 | 18.9 | 96.5 | 5 | 209.2 | 10.1 | 854.4 | 856.1 | 185.7 | 822.1 | 753.9 | 874 | 752.3 | 667.5 | 688.8 | 599.9 | 524.7 | 748.9 | 67.4 | 177 | 252.5 | 528.4 | 566.3 | 570.1 | 338.4 | 572.8 | 131.4 | 352.3 | 324.2 | 173.7 | 257.5 | 342.1 | 223
852 | 616 | 565.6 | 226.24 | 264.4615 | 370.4 | 330.9 | 326.1 | 252.5 | 561.3 | 52.7 | 18.9 | 96.8 | 5.2 | 205.8 | 9.9 | 853.1 | 853.7 | 186 | 823 | 753.6 | 873.8 | 751.1 | 666.2 | 685.7 | 600.1 | 525.2 | 746.5 | 67.6 | 177.3 | 252.7 | 527.7 | 566.7 | 567.3 | 339 | 571.6 | 131.7 | 356.3 | 324.9 | 174.4 | 257.8 | 342.6 | 223.4
853 | 617 | 565.6 | 226.24 | 264.4615 | 373.2 | 330.4 | 327.1 | 253.8 | 560.2 | 52.8 | 18.9 | 97 | 5.3 | 226.1 | 9.4 | 861.8 | 852.4 | 186.2 | 823.3 | 753.3 | 874.6 | 751 | 665 | 682.3 | 600.6 | 525.8 | 747.5 | 67.8 | 177.6 | 252.9 | 527 | 567.8 | 568.7 | 339.7 | 572.2 | 132.1 | 356 | 325.5 | 174.9 | 258.1 | 343.1 | 223.8
854 | 618 | 566.3 | 226.52 | 264.7888 | 374.4 | 330.4 | 327.6 | 254.4 | 556.6 | 52.8 | 18.9 | 97.3 | 5.6 | 232.8 | 8.2 | 867.3 | 852 | 186.6 | 823.9 | 753.4 | 875.9 | 750.4 | 664.7 | 679.6 | 603.1 | 526.8 | 747.6 | 68 | 177.9 | 253.1 | 526.9 | 567.5 | 571.7 | 340.2 | 577.4 | 132.5 | 355.6 | 326.2 | 175.3 | 258.4 | 343.6 | 224.2
855 | 619 | 566.5 | 226.6 | 264.8823 | 375.9 | 330.2 | 327.7 | 254.4 | 554.7 | 52.8 | 18.9 | 97.6 | 5.5 | 225 | 7.2 | 874.9 | 852.5 | 186.5 | 823.8 | 753 | 876.5 | 749.8 | 665.3 | 680.1 | 605.5 | 527.6 | 747.4 | 68.2 | 178.2 | 253.2 | 526.8 | 567.1 | 572.9 | 340.8 | 581.2 | 132.9 | 355.3 | 326.5 | 175.8 | 258.7 | 344.1 | 224.5
856 | 620 | 566.1 | 226.44 | 264.6953 | 376.6 | 329.7 | 327.3 | 254.2 | 555.4 | 52.9 | 18.9 | 97.9 | 5.8 | 220.4 | 6.7 | 858.4 | 850.8 | 186.8 | 823.8 | 752.5 | 877 | 750.3 | 664.7 | 683.4 | 605.3 | 528.2 | 747.3 | 68.4 | 178.5 | 253.5 | 526.1 | 567.1 | 573 | 341.3 | 580 | 133.2 | 355 | 326.4 | 176.3 | 258.9 | 344.6 | 224.9
857 | 621 | 563.8 | 225.52 | 263.6199 | 377.9 | 329.6 | 327.4 | 254.8 | 551.4 | 52.9 | 18.9 | 98.1 | 5 | 228.3 | 6.1 | 851.3 | 849.5 | 186.3 | 823.9 | 752.4 | 876.8 | 749.9 | 663.4 | 682.5 | 605 | 528.6 | 747.1 | 68.6 | 178.8 | 253.8 | 525.1 | 566.5 | 573.4 | 341.8 | 576.3 | 133.6 | 355.1 | 326.6 | 177 | 259.1 | 345.1 | 225.2
858 | 622 | 564.1 | 225.64 | 263.7602 | 381.9 | 329.9 | 327.7 | 254.5 | 548.9 | 53 | 18.9 | 98.4 | 6 | 216.3 | 6.3 | 853.5 | 848.4 | 186.5 | 824.5 | 753 | 877.2 | 749.4 | 661.8 | 682.7 | 605.6 | 529.4 | 747.3 | 68.8 | 179.1 | 253.9 | 524.3 | 566.6 | 571.9 | 342.4 | 574.3 | 134 | 354.9 | 327 | 177.5 | 259.5 | 345.6 | 225.6
859 | 623 | 564.6 | 225.84 | 263.9939 | 385.1 | 329.7 | 327.3 | 255.1 | 548.5 | 53.1 | 18.9 | 98.6 | 6.1 | 206.3 | 6.8 | 849.4 | 845.9 | 186.4 | 824.8 | 753.2 | 877.5 | 748 | 660 | 679.7 | 607.2 | 530 | 746.5 | 69 | 179.5 | 254.2 | 523.2 | 568 | 567.6 | 343 | 571.7 | 134.3 | 355 | 327.3 | 178 | 259.9 | 346.1 | 225.9
860 | 624 | 567 | 226.8 | 265.1161 | 385.5 | 328.7 | 327.1 | 257.1 | 546.9 | 53.2 | 18.9 | 98.7 | 5.3 | 245.6 | 6.5 | 839.2 | 844.9 | 186.1 | 825.2 | 753.3 | 876.2 | 745.2 | 656.9 | 668.7 | 608.8 | 530.6 | 745.3 | 69.2 | 179.8 | 254.5 | 522.2 | 568.5 | 565.1 | 343.7 | 570.5 | 134.7 | 356.1 | 327.6 | 178.6 | 260.3 | 346.5 | 226.3
861 | 625 | 566.7 | 226.68 | 264.9759 | 388.6 | 327.9 | 327.7 | 259.3 | 545.5 | 53.2 | 18.9 | 98.7 | 5.8 | 248 | 6.7 | 843 | 842.1 | 186.3 | 825.4 | 752.8 | 875.1 | 743.5 | 657 | 663.7 | 612.5 | 531.2 | 743.1 | 69.4 | 180.1 | 254.7 | 521.6 | 568.7 | 565.7 | 344.2 | 573.6 | 135.1 | 356.5 | 328.7 | 179.2 | 261 | 347 | 226.7
862 | 626 | 567.6 | 227.04 | 265.3967 | 390 | 328.2 | 329.1 | 260.3 | 544.9 | 53.3 | 18.9 | 98.8 | 6.1 | 240.5 | 6.5 | 843.2 | 841.5 | 186 | 825.7 | 752.2 | 874 | 742 | 657.2 | 661 | 614.5 | 531.9 | 742 | 69.7 | 180.3 | 254.9 | 521.3 | 568.7 | 565.4 | 344.7 | 575.7 | 135.5 | 357 | 329.6 | 179.7 | 261.4 | 347.5 | 227.1
863 | 627 | 566.4 | 226.56 | 264.8356 | 389.4 | 328.9 | 330.2 | 260.4 | 540.3 | 53.3 | 18.9 | 98.9 | 5.6 | 250.2 | 5.9 | 852 | 841.5 | 185.4 | 825.8 | 752.3 | 873.4 | 741.2 | 654.8 | 657.7 | 612.7 | 532.5 | 741.2 | 69.9 | 180.6 | 255 | 520.9 | 566.8 | 567.3 | 345.4 | 574.7 | 135.9 | 356.9 | 329.8 | 180.3 | 261.5 | 348 | 227.5
864 | 628 | 563.9 | 225.56 | 263.6666 | 393.9 | 328.5 | 331.1 | 260.6 | 538.9 | 53.4 | 18.9 | 99 | 5.4 | 226.8 | 5.6 | 858.7 | 846.8 | 185.6 | 825.2 | 752.1 | 874.3 | 741.5 | 654.5 | 660 | 613 | 533.1 | 742 | 70.1 | 180.9 | 255.3 | 520.2 | 415.2 | 569.3 | 345.9 | 574.8 | 136.3 | 357.2 | 330.2 | 180.8 | 261.8 | 348.5 | 227.9
865 | 629 | 564.8 | 225.92 | 264.0875 | 393.6 | 328.8 | 331.6 | 260.7 | 542 | 53.5 | 18.9 | 99 | 5.6 | 264 | 5.9 | 863.7 | 851.4 | 186.1 | 824.8 | 752.6 | 875.3 | 742.5 | 654.9 | 662.7 | 613.8 | 534 | 742.5 | 70.3 | 181.2 | 255.5 | 519.8 | 561.3 | 570.1 | 346.5 | 575.6 | 136.6 | 357.2 | 331.2 | 181.3 | 262 | 349 | 228.2
866 | 630 | 566.3 | 226.52 | 264.7888 | 392.5 | 329.6 | 331.7 | 260.2 | 543 | 53.6 | 18.9 | 99 | 5.3 | 260.3 | 6.3 | 871.4 | 858 | 186.7 | 825 | 753.1 | 875.9 | 743.6 | 655.5 | 673.5 | 614.1 | 534.9 | 743.9 | 70.5 | 181.5 | 255.7 | 519.6 | 565.8 | 572.2 | 347.1 | 575.6 | 137 | 357 | 331.1 | 181.8 | 262.3 | 349.5 | 228.5
867 | 631 | 566.6 | 226.64 | 264.9291 | 394.6 | 330.6 | 331.6 | 259.6 | 547.8 | 53.7 | 18.9 | 99 | 5.3 | 239.4 | 6.2 | 875.9 | 856.7 | 187 | 825.6 | 753.5 | 876.2 | 744.4 | 655.6 | 681.5 | 614.1 | 535.6 | 744.4 | 70.7 | 181.8 | 256 | 519.5 | 566.7 | 571.3 | 347.8 | 574.8 | 137.4 | 357 | 331.1 | 182.3 | 262.7 | 350 | 228.9
868 | 632 | 566.6 | 226.64 | 264.9291 | 395 | 331.4 | 331.5 | 260 | 550 | 53.8 | 18.9 | 99 | 4.9 | 225.9 | 5.6 | 869.6 | 856.2 | 186.6 | 826.5 | 754 | 875.8 | 744.1 | 655.3 | 679.3 | 615.2 | 536.2 | 743.7 | 70.9 | 182.1 | 256.2 | 519.4 | 568.8 | 568.7 | 348.5 | 574.8 | 137.8 | 357.2 | 331.4 | 182.8 | 263 | 350.5 | 229.2
869 | 633 | 566.4 | 226.56 | 264.8356 | 393.4 | 332.2 | 331.1 | 261.1 | 551.4 | 53.9 | 18.9 | 98.9 | 4.9 | 231.3 | 5.2 | 867.5 | 857.7 | 186.9 | 827.2 | 754.1 | 874.4 | 742.5 | 655 | 672.8 | 615.5 | 536.9 | 743.6 | 71.1 | 182.5 | 256.7 | 519.5 | 569.5 | 566.8 | 349.1 | 574.9 | 138.1 | 357.7 | 331.5 | 183.4 | 263.5 | 351 | 229.6
870 | 634 | 566.5 | 226.6 | 264.8823 | 390.9 | 331.4 | 330.7 | 261.8 | 551.5 | 54 | 18.9 | 98.9 | 5.1 | 251.1 | 6.9 | 862.4 | 854 | 187.5 | 828.2 | 754.2 | 874.2 | 742.1 | 654 | 670.8 | 615.5 | 537.2 | 743 | 71.3 | 182.8 | 256.6 | 519.2 | 570.9 | 564.9 | 349.5 | 575.8 | 138.5 | 358.4 | 331.6 | 183.9 | 263.8 | 351.5 | 230
871 | 635 | 566.1 | 226.44 | 264.6953 | 391.2 | 330.7 | 330.6 | 262.1 | 553.5 | 54 | 18.9 | 99 | 5.8 | 246.6 | 7.6 | 864.2 | 855.5 | 188.3 | 828.2 | 754 | 874.3 | 741.7 | 653.3 | 669 | 617.3 | 537.8 | 742.6 | 71.6 | 183.1 | 256.8 | 519.3 | 571.1 | 564.2 | 349.4 | 574.8 | 138.9 | 359 | 331.6 | 184.5 | 264.1 | 352 | 230.3
872 | 636 | 566.1 | 226.44 | 264.6953 | 393 | 330.6 | 330.8 | 262.4 | 554.2 | 54.1 | 18.9 | 99.2 | 5.3 | 245.3 | 7.3 | 864.6 | 854.2 | 188.6 | 828.1 | 753.5 | 874.3 | 741.4 | 653.5 | 672.1 | 618.7 | 538.3 | 742.4 | 71.8 | 183.4 | 257 | 519.7 | 460.4 | 568.1 | 349.8 | 576.9 | 139.3 | 359.9 | 332 | 185 | 264.5 | 352.5 | 230.7
873 | 637 | 565.7 | 226.28 | 264.5083 | 401.4 | 330.3 | 330.3 | 262.9 | 554.9 | 54.1 | 18.9 | 99.3 | 5.2 | 240.8 | 6.9 | 872 | 855.2 | 189.4 | 828.3 | 753.9 | 875.1 | 741.5 | 653.9 | 676 | 619.4 | 538.7 | 741.9 | 72 | 183.7 | 257.4 | 520 | 502.4 | 569 | 350.3 | 577.9 | 139.7 | 361 | 332.2 | 185.6 | 264.8 | 353.1 | 231.1
874 | 638 | 564.4 | 225.76 | 263.9004 | 407.5 | 330 | 330 | 263.4 | 554.6 | 54.2 | 18.9 | 99.4 | 5.9 | 214.2 | 6.4 | 869.7 | 853 | 189.5 | 829.1 | 753.8 | 875.3 | 741.9 | 653.8 | 678 | 620 | 539.3 | 742.2 | 72.2 | 184 | 257.5 | 520.2 | 573.5 | 567.2 | 351.1 | 577 | 140.1 | 361.9 | 332 | 186.1 | 265.1 | 353.6 | 231.6
875 | 639 | 565.2 | 226.08 | 264.2745 | 409.9 | 329.9 | 330.7 | 264.3 | 553.3 | 54.2 | 18.9 | 99.5 | 5.9 | 212.6 | 5.8 | 871.5 | 856.5 | 189.9 | 829.5 | 754.1 | 875.1 | 741.1 | 652.7 | 677.4 | 620.4 | 539.6 | 742.3 | 72.4 | 184.2 | 257.7 | 520.4 | 435.6 | 566.6 | 351.9 | 576.2 | 140.4 | 363.1 | 332.5 | 186.7 | 265.5 | 354.2 | 232
876 | 640 | 565.2 | 226.08 | 264.2745 | 412.1 | 330.6 | 331.1 | 265.7 | 553.5 | 54.3 | 18.9 | 99.6 | 5.3 | 241.3 | 5.6 | 870 | 857.8 | 189.7 | 829.1 | 754.2 | 874.8 | 739.8 | 651.8 | 674.8 | 620.3 | 540.1 | 741.2 | 72.6 | 184.5 | 258 | 520.4 | 536.1 | 565.4 | 352.8 | 575.4 | 140.8 | 365.9 | 333.5 | 187.4 | 265.9 | 354.7 | 232.4
877 | 641 | 565.2 | 226.08 | 264.2745 | 418.3 | 331.8 | 330.9 | 267.1 | 553.9 | 54.4 | 18.9 | 99.8 | 5.1 | 211.5 | 4.9 | 871.4 | 858.4 | 189.4 | 828.8 | 754.5 | 873.8 | 737.7 | 650.3 | 668.9 | 621.8 | 540.8 | 740.7 | 72.8 | 184.8 | 258.4 | 520.5 | 576.1 | 563.7 | 354 | 576.3 | 141.2 | 367.6 | 334.3 | 188.2 | 266.4 | 355.2 | 232.9
878 | 642 | 566.6 | 226.64 | 264.9291 | 425.1 | 332.6 | 330.9 | 268 | 554.4 | 54.5 | 18.8 | 99.9 | 5.5 | 217.8 | 4.8 | 873.9 | 855.7 | 188.5 | 829 | 754.6 | 873.6 | 735.5 | 649 | 661.6 | 624.1 | 541.3 | 740.2 | 73 | 185.1 | 258.6 | 520.2 | 401.2 | 561 | 355 | 576.3 | 141.6 | 369.4 | 334.8 | 188.9 | 266.8 | 355.7 | 233.4
879 | 643 | 566.1 | 226.44 | 264.6953 | 432.4 | 332.8 | 331 | 269.4 | 552.5 | 54.6 | 18.8 | 99.9 | 5.3 | 211.4 | 5.8 | 872.2 | 856.5 | 188.5 | 829.2 | 754.7 | 873.4 | 733.1 | 648.3 | 659.1 | 626.5 | 541.8 | 737.3 | 73.3 | 185.3 | 258.9 | 520.4 | 568.5 | 559.1 | 355.9 | 578.6 | 142 | 370.5 | 335.3 | 189.4 | 267.1 | 356.3 | 233.8
880 | 644 | 566.8 | 226.72 | 265.0226 | 438.4 | 333.7 | 331.6 | 270.5 | 550.6 | 54.7 | 18.8 | 100 | 4.7 | 209.2 | 6.6 | 873.9 | 857.7 | 188.2 | 829.6 | 754.8 | 873.9 | 733 | 648.5 | 665.3 | 627.1 | 542.4 | 737 | 73.5 | 185.6 | 259.1 | 521 | 547 | 561 | 356.9 | 578.8 | 142.3 | 370.4 | 336.8 | 190 | 267.4 | 356.9 | 234.2
881 | 645 | 568.2 | 227.28 | 265.6772 | 442.2 | 334.1 | 333.2 | 270.4 | 553.7 | 54.7 | 18.8 | 100.2 | 5.1 | 222.3 | 6.7 | 877.8 | 860 | 187.9 | 829.4 | 755.1 | 875 | 733.8 | 648.3 | 666.3 | 627.9 | 543.2 | 738.5 | 73.7 | 185.7 | 259.3 | 521.2 | 322.2 | 562.3 | 358 | 577.4 | 142.7 | 370.4 | 337.9 | 190.5 | 267.6 | 357.5 | 234.6
882 | 646 | 567.1 | 226.84 | 265.1629 | 447.8 | 334.1 | 334.2 | 270.2 | 554.6 | 54.8 | 18.8 | 100.3 | 5.4 | 218.2 | 6.1 | 872.5 | 857 | 187.7 | 829.3 | 755.4 | 876 | 735.2 | 647.9 | 671.8 | 628.3 | 544.1 | 738.5 | 73.9 | 185.9 | 259.4 | 520.9 | 355.4 | 561.9 | 359 | 575.6 | 143.1 | 370.1 | 338 | 191 | 267.9 | 358.1 | 235
883 | 647 | 564.8 | 225.92 | 264.0875 | 452 | 334.7 | 335 | 269.6 | 554.1 | 54.8 | 18.8 | 100.5 | 5.4 | 228.1 | 5.5 | 876.2 | 860.1 | 186.9 | 829.5 | 755.4 | 876.9 | 738.4 | 650.3 | 686.9 | 629.1 | 544.8 | 740 | 74.1 | 186.2 | 259.7 | 521.4 | 423.5 | 566.4 | 359.9 | 576 | 143.5 | 369.6 | 338.7 | 191.5 | 268.2 | 358.6 | 235.4
884 | 648 | 564.3 | 225.72 | 263.8537 | 448.3 | 335.4 | 335.6 | 269.2 | 554.2 | 54.8 | 18.8 | 100.8 | 5.2 | 235.2 | 4.8 | 877.8 | 859.4 | 187.2 | 830.3 | 755.5 | 878.3 | 740 | 650.3 | 687 | 628.9 | 545.5 | 742.3 | 74.4 | 186.5 | 260 | 521.5 | 394.7 | 570.1 | 360.8 | 575.8 | 143.9 | 369.2 | 339 | 191.9 | 268.4 | 359.1 | 235.7
885 | 649 | 564.1 | 225.64 | 263.7602 | 442 | 336.1 | 335.6 | 269.4 | 552.7 | 54.8 | 18.8 | 101 | 5.6 | 234.9 | 4.3 | 873.6 | 855.7 | 187.1 | 830 | 755.8 | 878.9 | 740.5 | 650.3 | 686 | 629.4 | 546 | 742.7 | 74.6 | 186.8 | 260.1 | 521.3 | 572.9 | 570.1 | 361.7 | 575.3 | 144.3 | 368.8 | 340.4 | 192.3 | 268.7 | 359.6 | 236.1
886 | 650 | 566.3 | 226.52 | 264.7888 | 439.9 | 336.1 | 335.2 | 269.4 | 553.8 | 54.9 | 18.8 | 101.1 | 5.2 | 222.2 | 4.1 | 857.4 | 852.3 | 187.3 | 830.4 | 755.9 | 877.7 | 739.3 | 649.3 | 682.5 | 630.2 | 546.6 | 744.1 | 74.8 | 187.1 | 260.5 | 521.2 | 385.7 | 567.3 | 362.7 | 575.8 | 144.7 | 368.7 | 340.6 | 192.7 | 269.1 | 360.1 | 236.5
887 | 651 | 565.2 | 226.08 | 264.2745 | 437.3 | 335.3 | 334.6 | 269.6 | 550.9 | 54.9 | 18.8 | 101.2 | 4.6 | 204.1 | 5.8 | 865.5 | 855.3 | 187.6 | 830.3 | 756 | 877.5 | 739 | 649 | 683.1 | 630.9 | 547 | 744.4 | 75 | 187.3 | 260.7 | 521.1 | 434.6 | 568.4 | 363.7 | 577.6 | 145.1 | 368.4 | 340.4 | 193.2 | 269.4 | 360.6 | 236.8
888 | 652 | 564.5 | 225.8 | 263.9472 | 438 | 334.1 | 333.9 | 270.3 | 550.7 | 54.9 | 18.8 | 101.3 | 4.7 | 205.1 | 6.7 | 867.2 | 849.5 | 187.5 | 829.8 | 755.6 | 879.2 | 737.6 | 647.5 | 680.9 | 631.8 | 547.6 | 743.7 | 75.3 | 187.6 | 260.8 | 520.9 | 573.6 | 567.7 | 364.7 | 577.3 | 145.5 | 368.4 | 340.1 | 193.8 | 269.7 | 361.1 | 237.2
889 | 653 | 566.7 | 226.68 | 264.9759 | 440.3 | 333.8 | 333.7 | 270.6 | 550.4 | 55 | 18.8 | 101.4 | 4.8 | 215.7 | 6 | 867.3 | 847.2 | 187.5 | 829.6 | 754.8 | 880.2 | 737.4 | 646.9 | 678.3 | 632.7 | 548.1 | 742.2 | 75.5 | 187.9 | 261 | 520.7 | 572.6 | 568.8 | 365.7 | 578.5 | 145.8 | 368.8 | 339.7 | 194.3 | 269.8 | 361.5 | 237.5
890 | 654 | 566.1 | 226.44 | 264.6953 | 438.1 | 333.4 | 334 | 270.3 | 550.6 | 55 | 18.8 | 101.4 | 4.9 | 228 | 5.1 | 867.6 | 847.3 | 187.7 | 830.1 | 754 | 880.3 | 739.1 | 648.1 | 684.1 | 633.4 | 548.7 | 741.8 | 75.7 | 188.2 | 261.1 | 520.6 | 571.4 | 566.6 | 366.7 | 577.6 | 146.2 | 368.3 | 339.4 | 194.9 | 269.9 | 362 | 237.9
891 | 655 | 564.7 | 225.88 | 264.0407 | 431.9 | 332.8 | 333.9 | 269.6 | 552.4 | 55 | 18.8 | 101.5 | 5 | 250.2 | 4.8 | 868.7 | 849.8 | 188.2 | 830.1 | 754 | 880.6 | 741 | 649.3 | 688.9 | 634.1 | 549.3 | 744.7 | 75.9 | 188.6 | 261.3 | 520.6 | 571.5 | 567.4 | 367.7 | 577.5 | 146.6 | 368.3 | 338.7 | 195.5 | 270.2 | 362.5 | 238.3
892 | 656 | 566.2 | 226.48 | 264.7421 | 425.2 | 332.1 | 333.7 | 268.9 | 554.4 | 55 | 18.8 | 101.5 | 5.7 | 251.2 | 4.5 | 870.6 | 856.5 | 187.8 | 829.8 | 754 | 880.9 | 742.8 | 650.4 | 697 | 635 | 549.8 | 745.6 | 76.2 | 188.9 | 261.6 | 520.7 | 572.2 | 573.3 | 368.7 | 576.5 | 147 | 367.4 | 338.2 | 195.9 | 270.3 | 363 | 238.6
893 | 657 | 565.9 | 226.36 | 264.6018 | 419.7 | 332.3 | 333.2 | 268.8 | 554.1 | 55 | 18.8 | 101.6 | 5.6 | 210.4 | 4.5 | 877.8 | 863.3 | 186.9 | 830 | 754.5 | 881.2 | 745.8 | 652.6 | 706.3 | 635.8 | 550.5 | 746.5 | 76.4 | 189.3 | 262.1 | 521 | 572.6 | 588.6 | 369.8 | 577.2 | 147.4 | 366.3 | 337.8 | 196.4 | 270.3 | 363.5 | 238.9
894 | 658 | 566.1 | 226.44 | 264.6953 | 416 | 334.6 | 334.4 | 268.7 | 555.7 | 55.2 | 18.8 | 101.6 | 6 | 176.1 | 4.8 | 879.5 | 859.5 | 186.9 | 830.1 | 754.5 | 881.6 | 746.3 | 653.5 | 706.8 | 637.2 | 551.2 | 746.5 | 76.6 | 189.6 | 262.4 | 521.2 | 572.9 | 589.3 | 371 | 576.8 | 147.7 | 365.2 | 337.5 | 196.7 | 270.4 | 363.8 | 239.1
895 | 659 | 565.4 | 226.16 | 264.368 | 415.8 | 334.8 | 334.4 | 268.9 | 554 | 55.1 | 18.8 | 101.5 | 6.1 | 223 | 4.5 | 878.1 | 852.8 | 186.7 | 830.3 | 754.4 | 881.1 | 744 | 651.8 | 699.4 | 638.5 | 551.6 | 748.3 | 76.8 | 190 | 262.4 | 520.9 | 572.6 | 585.3 | 371.9 | 575.4 | 148.1 | 364.7 | 337.3 | 197.2 | 270.9 | 364.4 | 239.5
896 | 660 | 563.2 | 225.28 | 263.3393 | 415.4 | 334.5 | 333.5 | 269.5 | 552.5 | 55.1 | 18.8 | 101.5 | 5.7 | 225.3 | 4.7 | 876.9 | 849.8 | 186.9 | 830.5 | 754.1 | 880.6 | 741 | 649 | 689.8 | 641 | 552.3 | 745.8 | 77 | 190.3 | 262.6 | 520.6 | 573.6 | 577.7 | 372.9 | 574.1 | 148.5 | 364.6 | 337.1 | 197.8 | 271.2 | 364.9 | 239.9
897 | 661 | 564.4 | 225.76 | 263.9004 | 414.3 | 333.5 | 332.9 | 271.1 | 552.6 | 55.1 | 18.8 | 101.6 | 5.3 | 210.5 | 6.2 | 882.2 | 854.7 | 187.4 | 830.7 | 754.4 | 881.1 | 739.3 | 647.2 | 689.6 | 644.3 | 553.1 | 744.9 | 77.3 | 190.7 | 262.8 | 520.6 | 575.3 | 574 | 374 | 572.7 | 148.9 | 364.9 | 336.9 | 198.4 | 271.4 | 365.4 | 240.3
898 | 662 | 565.4 | 226.16 | 264.368 | 415.8 | 332.8 | 333.4 | 272.9 | 552 | 55.2 | 18.8 | 101.7 | 6.1 | 218.7 | 6.3 | 882 | 855 | 187.8 | 831 | 754.4 | 881.1 | 736.9 | 645.3 | 684.5 | 648.4 | 553.8 | 743.4 | 77.5 | 191 | 263 | 520.7 | 575 | 571.7 | 375.1 | 572.6 | 149.3 | 365.8 | 337.5 | 199.1 | 271.8 | 365.9 | 240.7
899 | 663 | 565 | 226 | 264.181 | 420.8 | 332.8 | 333.3 | 273.5 | 554.3 | 55.2 | 18.8 | 101.8 | 5.7 | 212.6 | 6.4 | 875.8 | 856.8 | 188 | 832.2 | 754.3 | 880.6 | 734.7 | 645.1 | 680.1 | 652.6 | 554.5 | 742.7 | 77.7 | 191.3 | 263.3 | 521 | 576.3 | 574.6 | 376.2 | 577.5 | 149.7 | 367.8 | 338.5 | 199.8 | 272.2 | 366.4 | 241
900 | 664 | 565.2 | 226.08 | 264.2745 | 423.1 | 333.3 | 333.3 | 274.1 | 555.7 | 55.3 | 18.8 | 101.8 | 5.3 | 218.1 | 6.1 | 873.8 | 855.4 | 187.3 | 833.8 | 755.2 | 880.3 | 735.3 | 645.6 | 685.3 | 654.9 | 555.1 | 742.2 | 78 | 191.6 | 263.5 | 520.7 | 576.4 | 574.7 | 377.3 | 576.2 | 150 | 368.8 | 339 | 200.5 | 272.5 | 366.9 | 241.5
901 | 665 | 565.3 | 226.12 | 264.3213 | 425 | 333.7 | 333.9 | 274.2 | 556.5 | 55.4 | 18.8 | 101.9 | 5 | 225.5 | 5.3 | 880.6 | 856.3 | 186.1 | 835 | 755.6 | 881.1 | 736.5 | 646.2 | 689.4 | 656.1 | 555.6 | 743.9 | 78.2 | 191.9 | 263.8 | 520.9 | 575.9 | 571.9 | 378.4 | 575.6 | 150.4 | 369.4 | 339.7 | 201 | 272.7 | 367.4 | 241.9
902 | 666 | 566.7 | 226.68 | 264.9759 | 426.7 | 334 | 334 | 274.6 | 554.7 | 55.4 | 18.8 | 102 | 4.9 | 240.9 | 4.7 | 883.5 | 853.9 | 185 | 835.1 | 755.6 | 881.6 | 737.3 | 646.8 | 688.9 | 657.5 | 556.3 | 744.1 | 78.4 | 192.2 | 264.1 | 520.6 | 574.8 | 567.4 | 379.5 | 574.7 | 150.8 | 369.7 | 340.1 | 201.6 | 273.1 | 367.9 | 242.3
903 | 667 | 566.9 | 226.76 | 265.0694 | 425.7 | 334 | 333.9 | 275.4 | 552.5 | 55.5 | 18.8 | 102.1 | 5.1 | 272.1 | 4.7 | 881.8 | 853.3 | 184.3 | 835.1 | 755.3 | 881.8 | 737.5 | 647 | 690.3 | 658.9 | 557 | 744.5 | 78.6 | 192.5 | 264.3 | 520.6 | 573.9 | 565.7 | 380.6 | 573.4 | 151.2 | 369.7 | 340.2 | 202.2 | 273.3 | 368.4 | 242.6
904 | 668 | 566.1 | 226.44 | 264.6953 | 426.4 | 334.3 | 333.9 | 275.5 | 554.6 | 55.6 | 18.8 | 102.1 | 5.2 | 261.2 | 4.6 | 880.7 | 855.3 | 184.2 | 835.2 | 755.5 | 882.2 | 738 | 647.8 | 694.7 | 661.1 | 557.5 | 745.5 | 78.9 | 192.8 | 264.5 | 520.4 | 574.7 | 567 | 381.7 | 574.7 | 151.6 | 369.6 | 340.9 | 202.6 | 273.5 | 368.9 | 243
905 | 669 | 567.1 | 226.84 | 265.1629 | 430.7 | 334.2 | 334.8 | 275.2 | 556.1 | 55.6 | 18.8 | 102.1 | 5.1 | 243.1 | 5.2 | 879.3 | 859.2 | 184 | 835 | 755.9 | 882.7 | 738.4 | 648.1 | 695.6 | 663.7 | 558.1 | 743.3 | 79.1 | 193.1 | 264.8 | 520.6 | 575.2 | 569.7 | 382.8 | 575.9 | 152 | 369.3 | 340.9 | 203.1 | 273.7 | 369.4 | 243.3
906 | 670 | 565.8 | 226.32 | 264.555 | 435.3 | 334.4 | 335.4 | 275.3 | 558.6 | 55.6 | 18.8 | 102 | 5.5 | 250.4 | 5.2 | 885.4 | 858.2 | 183.9 | 834.8 | 756.4 | 883.1 | 737.7 | 647.7 | 692.7 | 669.4 | 558.6 | 744.6 | 79.3 | 193.3 | 265 | 520.8 | 339.8 | 568.1 | 383.8 | 575.6 | 152.3 | 369.3 | 341.6 | 203.7 | 274 | 370 | 243.7
907 | 671 | 565.9 | 226.36 | 264.6018 | 445.3 | 334.7 | 336.1 | 275.5 | 560.5 | 55.7 | 18.7 | 102 | 5.6 | 239.1 | 5.5 | 880.3 | 857.4 | 184.3 | 834.8 | 756.8 | 883.6 | 735.8 | 647.3 | 690.9 | 674.8 | 558.6 | 744.2 | 79.5 | 193.6 | 265.3 | 520.6 | 473 | 566.1 | 384.9 | 575.1 | 152.7 | 370.1 | 342.3 | 204.3 | 274.4 | 370.5 | 244
908 | 672 | 564.9 | 225.96 | 264.1342 | 446.5 | 334.5 | 336.8 | 277.1 | 561.2 | 55.8 | 18.7 | 102.1 | 5.4 | 225.2 | 5.3 | 874.5 | 855 | 184 | 834.9 | 756.7 | 883.6 | 734.5 | 647.7 | 687.5 | 681.6 | 559 | 742.9 | 79.8 | 193.9 | 265.6 | 520.8 | 455.4 | 569.1 | 385.9 | 577.4 | 153.1 | 370.5 | 343 | 205.1 | 274.6 | 371 | 244.4
909 | 673 | 564.8 | 225.92 | 264.0875 | 447.6 | 335.1 | 337.9 | 278.6 | 563.7 | 55.8 | 18.7 | 102.2 | 5.3 | 256.9 | 4.5 | 869.6 | 851.9 | 183.6 | 835.6 | 757.3 | 883.1 | 734.2 | 647.1 | 681 | 685.7 | 559.4 | 742.4 | 80 | 194.2 | 265.8 | 521 | 322.6 | 571.7 | 386.9 | 578.6 | 153.5 | 371.7 | 343.8 | 205.8 | 274.9 | 371.5 | 244.8
910 | 674 | 564.8 | 225.92 | 264.0875 | 449.5 | 336 | 338.9 | 279.3 | 565.1 | 55.9 | 18.7 | 102.3 | 5.4 | 289.8 | 4.1 | 853.1 | 845.9 | 184 | 837.2 | 757.6 | 880.9 | 730.7 | 645.9 | 671.4 | 692.6 | 560.1 | 742.9 | 80.2 | 194.4 | 266 | 521.3 | 577.8 | 575.9 | 388 | 580.7 | 153.9 | 373.3 | 344.9 | 206.5 | 275.2 | 372 | 245.2
911 | 675 | 564.2 | 225.68 | 263.8069 | 449.4 | 336.8 | 338.4 | 280.4 | 564.5 | 56 | 18.7 | 102.5 | 5 | 253.2 | 3.9 | 854.9 | 844.5 | 184.3 | 838.7 | 757.4 | 879.8 | 726.9 | 643.9 | 664.2 | 697.1 | 560.5 | 739.2 | 80.4 | 194.7 | 266.5 | 521.5 | 486.8 | 581.4 | 389 | 583.8 | 154.3 | 374.7 | 345.2 | 207.2 | 275.6 | 372.5 | 245.6
912 | 676 | 567.8 | 227.12 | 265.4902 | 451.6 | 337.6 | 338.8 | 281.3 | 564.7 | 56.1 | 18.7 | 102.6 | 6 | 226.9 | 4.4 | 852.4 | 835.8 | 184.4 | 839.2 | 756.9 | 880.1 | 727.3 | 646.5 | 660.1 | 696.9 | 560.9 | 739.1 | 80.7 | 195 | 266.7 | 522.3 | 399.5 | 594 | 390.1 | 588.8 | 154.7 | 375.2 | 346 | 207.9 | 276.2 | 373.1 | 246
913 | 677 | 569 | 227.6 | 266.0513 | 452.1 | 338.3 | 340.3 | 282.1 | 565.1 | 56.2 | 18.7 | 102.7 | 6.1 | 248.2 | 4.9 | 853.1 | 835.6 | 184.7 | 839.9 | 756.7 | 879.2 | 727.4 | 649 | 655.9 | 697.3 | 561.4 | 739.9 | 80.9 | 195.2 | 267 | 522.6 | 580.5 | 599.3 | 391.1 | 592.6 | 155.1 | 376.5 | 346.6 | 208.6 | 276.7 | 373.7 | 246.4
914 | 678 | 569.9 | 227.96 | 266.4721 | 452.9 | 338.8 | 341.7 | 283.5 | 562 | 56.2 | 18.7 | 102.7 | 5.5 | 237.4 | 4.8 | 861.1 | 845.9 | 184.8 | 840.8 | 756.5 | 878.5 | 727.8 | 651.4 | 657.9 | 700.1 | 561.9 | 740 | 81.1 | 195.4 | 267.3 | 522.7 | 401.5 | 600.1 | 392.2 | 596.1 | 155.5 | 378.3 | 346.9 | 209.3 | 277.1 | 374.3 | 246.9
915 | 679 | 571 | 228.4 | 266.9864 | 454.1 | 339 | 342.9 | 284.7 | 560.1 | 56.3 | 18.7 | 102.7 | 5.2 | 244.9 | 4.8 | 859.9 | 842.7 | 184.9 | 841.7 | 756.7 | 878.4 | 729.6 | 652.7 | 663.9 | 700 | 562.4 | 739.2 | 81.3 | 195.7 | 267.5 | 523.1 | 436.3 | 601.1 | 393.2 | 594.6 | 155.9 | 378.8 | 347.4 | 210.1 | 277.3 | 374.9 | 247.4
916 | 680 | 570.2 | 228.08 | 266.6124 | 458.1 | 339.3 | 343.8 | 284.6 | 560.9 | 56.3 | 18.7 | 102.8 | 5.2 | 248.2 | 5.5 | 862.3 | 846.1 | 185.4 | 842.6 | 757.3 | 878.3 | 732.2 | 654 | 671.5 | 695.7 | 562.9 | 742.1 | 81.6 | 196 | 267.7 | 523.1 | 578.1 | 598 | 394.2 | 589.5 | 156.2 | 379.1 | 347.8 | 210.9 | 277.4 | 375.5 | 247.8
917 | 681 | 567 | 226.8 | 265.1161 | 462.4 | 340 | 344.1 | 284.3 | 563.5 | 56.4 | 18.7 | 103 | 5.6 | 243.6 | 6.2 | 864.8 | 852.5 | 185.7 | 842.9 | 757.6 | 878.3 | 733.4 | 654.6 | 679.2 | 692.9 | 563.7 | 743.5 | 81.8 | 196.4 | 267.9 | 522.9 | 277.1 | 598.1 | 395.2 | 588.7 | 156.7 | 378.9 | 348.3 | 211.6 | 277.6 | 376.1 | 248.2
918 | 682 | 565 | 226 | 264.181 | 481.3 | 340.1 | 343.5 | 283.8 | 565.9 | 56.4 | 18.7 | 103.2 | 5.3 | 244.4 | 6.7 | 864.6 | 855.3 | 185.8 | 842.4 | 757.8 | 878.1 | 733.9 | 654.9 | 684.8 | 690 | 564.1 | 743.4 | 82 | 196.7 | 268.1 | 522.9 | 495.1 | 593.6 | 396.2 | 587.8 | 157.1 | 378.9 | 348.4 | 212.2 | 278 | 376.6 | 248.5
919 | 683 | 564.4 | 225.76 | 263.9004 | 481.1 | 340.9 | 343.8 | 284.4 | 564.9 | 56.5 | 18.7 | 103.3 | 4.9 | 243.8 | 6.8 | 864.2 | 854 | 185.5 | 842.6 | 757.7 | 877.6 | 734.1 | 655.1 | 684.8 | 687.1 | 564.5 | 743.3 | 82.2 | 197 | 268.4 | 522.8 | 580.7 | 587.4 | 397.1 | 586.9 | 157.5 | 379.9 | 348.2 | 213 | 278.3 | 377.1 | 248.9
920 | 684 | 565 | 226 | 264.181 | 473.2 | 341.3 | 345.3 | 285 | 561 | 56.5 | 18.7 | 103.2 | 5.3 | 247.1 | 6.8 | 868.3 | 853 | 185.2 | 841.9 | 757.4 | 878 | 733.5 | 654.5 | 684.4 | 685.8 | 565 | 741.8 | 82.5 | 197.3 | 268.6 | 522.9 | 210 | 581.6 | 398.1 | 585.4 | 157.9 | 380.6 | 348.2 | 213.8 | 278.6 | 377.6 | 249.3
921 | 685 | 566.5 | 226.6 | 264.8823 | 465.7 | 341.8 | 345.7 | 285.6 | 561.4 | 56.5 | 18.7 | 103.3 | 5.3 | 250.4 | 6.2 | 869.5 | 850.9 | 184.9 | 842 | 757.5 | 879 | 734.1 | 655 | 681.2 | 683.8 | 565.6 | 742 | 82.7 | 197.6 | 268.9 | 523.5 | 570.6 | 585.7 | 399.1 | 586.4 | 158.3 | 381.1 | 348.4 | 214.4 | 279 | 378.2 | 249.7
922 | 686 | 565.8 | 226.32 | 264.555 | 462.8 | 342.1 | 345.6 | 285.9 | 560.2 | 56.6 | 18.7 | 103.3 | 5.7 | 238.3 | 5.9 | 865.8 | 847.1 | 184.6 | 842 | 757.4 | 879.6 | 733.7 | 654 | 682.1 | 681.8 | 565.7 | 742.2 | 82.9 | 197.8 | 269.1 | 523.5 | 533.5 | 584.9 | 400 | 586 | 158.7 | 381.2 | 348.6 | 215.1 | 279.2 | 378.7 | 250.1
923 | 687 | 566.9 | 226.76 | 265.0694 | 463.3 | 341.7 | 345.8 | 286.5 | 561.4 | 56.6 | 18.7 | 103.3 | 5.3 | 233.1 | 5.9 | 867.3 | 849.2 | 184.6 | 841.7 | 757.8 | 880.5 | 734.9 | 655.3 | 688 | 680.3 | 566 | 741.7 | 83.1 | 198.1 | 269.4 | 523.7 | 226 | 584.5 | 401 | 585.1 | 159.1 | 380.8 | 348.8 | 215.8 | 279.3 | 379.3 | 250.5
924 | 688 | 565.7 | 226.28 | 264.5083 | 461 | 341.7 | 346.1 | 286.2 | 565.1 | 56.5 | 18.7 | 103.3 | 4.9 | 235.3 | 5.6 | 870.7 | 853.4 | 184.9 | 841.7 | 759 | 881.2 | 736.8 | 657.6 | 695 | 678.1 | 566.4 | 744.9 | 83.4 | 198.4 | 269.8 | 524.3 | 268.8 | 588.7 | 401.9 | 585.2 | 159.5 | 380.3 | 349.4 | 216.4 | 279.6 | 379.8 | 250.9
925 | 689 | 566.8 | 226.72 | 265.0226 | 459.3 | 342.5 | 347.5 | 285.9 | 567.1 | 56.5 | 18.7 | 103.4 | 4.7 | 246 | 5.5 | 874.3 | 852.8 | 185.3 | 841 | 759.9 | 881.8 | 737.4 | 660.3 | 701.8 | 675.3 | 567 | 746.1 | 83.6 | 198.7 | 270 | 524.8 | 370.9 | 587.9 | 402.8 | 586.1 | 160 | 380.5 | 350.7 | 217 | 279.8 | 380.3 | 251.3
926 | 690 | 568.1 | 227.24 | 265.6305 | 457.3 | 342.8 | 347.5 | 286 | 567.3 | 56.6 | 18.7 | 103.4 | 4.6 | 249.2 | 5.8 | 873.3 | 851.2 | 185.5 | 841.4 | 760.3 | 882.4 | 736.6 | 659.3 | 696.6 | 672.2 | 567.5 | 747.1 | 83.8 | 199 | 270.2 | 524.8 | 330.5 | 587.8 | 403.8 | 586.5 | 160.4 | 380.6 | 351 | 217.6 | 280.1 | 380.8 | 251.6
927 | 691 | 564.6 | 225.84 | 263.9939 | 454.3 | 343.1 | 347.2 | 286.3 | 562.8 | 56.6 | 18.7 | 103.3 | 4.6 | 220.5 | 6.3 | 876.8 | 857.6 | 185.5 | 842.1 | 759.8 | 882.1 | 734.1 | 656.7 | 690.3 | 669.5 | 568 | 746.3 | 84 | 199.2 | 270.4 | 524.7 | 581.6 | 583.6 | 404.7 | 585.5 | 160.8 | 380.6 | 351.2 | 218.3 | 280.3 | 381.3 | 252
928 | 692 | 564.1 | 225.64 | 263.7602 | 454.1 | 342.9 | 347.1 | 286.6 | 560.7 | 56.7 | 18.7 | 103.4 | 4.9 | 229.8 | 6.1 | 878.3 | 857.1 | 185.4 | 842.3 | 760.1 | 882.2 | 732.3 | 656.4 | 690.6 | 667.5 | 568.5 | 743.6 | 84.3 | 199.5 | 270.7 | 524.6 | 365.1 | 578.7 | 405.7 | 586.1 | 161.2 | 380.9 | 351 | 219 | 280.6 | 381.7 | 252.4
929 | 693 | 564 | 225.6 | 263.7134 | 452.3 | 343.5 | 346.3 | 287.6 | 561 | 56.8 | 18.7 | 103.5 | 5.3 | 247.6 | 5.6 | 863.2 | 847.9 | 185.1 | 841.9 | 759.8 | 881.6 | 730.6 | 656.3 | 683.4 | 665.7 | 568.8 | 743.7 | 84.5 | 199.9 | 271.1 | 524.7 | 411.3 | 579.9 | 406.6 | 590 | 161.7 | 381.4 | 351 | 219.7 | 281 | 382.3 | 252.8
930 | 694 | 565.5 | 226.2 | 264.4148 | 450.1 | 343.5 | 346.8 | 288 | 562 | 56.8 | 18.7 | 103.6 | 5.4 | 241.2 | 5.3 | 852.5 | 841.9 | 185 | 842.3 | 759.7 | 880 | 728.1 | 655.7 | 674.3 | 664.4 | 569.4 | 741.6 | 84.7 | 200.2 | 271.5 | 525.3 | 582.1 | 589 | 407.5 | 593.8 | 162.1 | 382.6 | 351 | 220.4 | 281.5 | 382.8 | 253.2
931 | 695 | 566.6 | 226.64 | 264.9291 | 456.8 | 343.8 | 349 | 288.8 | 562.9 | 56.8 | 18.7 | 103.7 | 5.6 | 222.9 | 5.2 | 854.1 | 845.8 | 184.9 | 843.7 | 759.3 | 878 | 726.4 | 656.8 | 669.7 | 666 | 570.2 | 740.5 | 84.9 | 200.4 | 271.8 | 525.9 | 582.1 | 588.4 | 408.4 | 599.8 | 162.5 | 384.3 | 351.1 | 221.3 | 281.8 | 383.4 | 253.6
932 | 696 | 567.5 | 227 | 265.3499 | 465.1 | 344.1 | 350.5 | 288.5 | 562.8 | 56.9 | 18.7 | 103.9 | 5.5 | 214.6 | 5.2 | 855.2 | 847 | 185 | 844.6 | 759.7 | 878.2 | 728.7 | 660.2 | 673.6 | 667.1 | 570.9 | 741.4 | 85.2 | 200.7 | 271.9 | 526.8 | 582.2 | 592.4 | 409.4 | 599.6 | 163 | 385.2 | 351 | 222.1 | 282.1 | 384 | 254.1
933 | 697 | 568.4 | 227.36 | 265.7707 | 464.6 | 345.3 | 352.4 | 288.3 | 564.3 | 57 | 18.7 | 104.1 | 5.3 | 204.8 | 4.9 | 860.2 | 847.4 | 184.7 | 844.7 | 759.9 | 879.5 | 729 | 660.3 | 672.8 | 666.6 | 571.7 | 742.2 | 85.4 | 201 | 272 | 527.3 | 581.9 | 592.9 | 410.3 | 599.6 | 163.4 | 385.3 | 351.5 | 222.8 | 282.3 | 384.6 | 254.5
934 | 698 | 566.8 | 226.72 | 265.0226 | 463.2 | 345.5 | 352.5 | 288.6 | 563.8 | 57.1 | 18.7 | 104.3 | 5.5 | 232.2 | 4.5 | 865.8 | 850 | 184.7 | 844.3 | 760.5 | 880.3 | 729.3 | 661.4 | 678.5 | 665.1 | 572.3 | 742.2 | 85.6 | 201.3 | 272.3 | 527.6 | 580.4 | 590.1 | 411.3 | 596.8 | 163.8 | 385.6 | 352 | 223.6 | 282.7 | 385.2 | 254.9
935 | 699 | 565.7 | 226.28 | 264.5083 | 464.2 | 345 | 352.1 | 289.4 | 561.2 | 57.2 | 18.7 | 104.5 | 5.8 | 241.1 | 4.8 | 872.3 | 851.1 | 184.5 | 843.8 | 760.5 | 881.1 | 728.7 | 661.3 | 677.7 | 663.6 | 572.8 | 743.3 | 85.8 | 201.6 | 272.6 | 527.8 | 577.8 | 591.1 | 412.2 | 595.2 | 164.3 | 386 | 352.5 | 224.2 | 282.9 | 385.8 | 255.3
936 | 700 | 564.9 | 225.96 | 264.1342 | 463.7 | 346 | 351.2 | 290 | 561 | 57.3 | 18.6 | 104.7 | 4.8 | 224.4 | 5 | 873.4 | 856.1 | 185.1 | 843.4 | 761 | 882 | 730.4 | 663.6 | 688.9 | 662.6 | 573.1 | 741.5 | 86 | 201.9 | 272.8 | 528.2 | 576.4 | 592.1 | 413.2 | 595.3 | 164.7 | 387 | 352.7 | 224.9 | 283.1 | 386.3 | 255.7
937 | 701 | 564.5 | 225.8 | 263.9472 | 457.8 | 347.8 | 350.3 | 290.1 | 565.5 | 57.3 | 18.6 | 104.8 | 4.9 | 202.2 | 4.9 | 875.6 | 860.6 | 185.5 | 844 | 761.6 | 882.8 | 733.6 | 666.7 | 698 | 661.3 | 573.8 | 744 | 86.3 | 202.2 | 273.1 | 528.5 | 578.2 | 594.6 | 414.1 | 597.3 | 165.2 | 387.5 | 352.5 | 225.6 | 283.4 | 386.8 | 256.1
938 | 702 | 565.1 | 226.04 | 264.2277 | 452.4 | 349.1 | 350.1 | 289.7 | 569.7 | 57.3 | 18.6 | 104.9 | 5.1 | 212.5 | 4.9 | 878.2 | 859.2 | 185.2 | 844.4 | 761.7 | 883.2 | 735.6 | 669.2 | 701.7 | 659.2 | 574.2 | 744.1 | 86.5 | 202.4 | 273.2 | 528.6 | 580.1 | 594.7 | 415 | 596.3 | 165.6 | 386.9 | 352.2 | 226.1 | 283.7 | 387.4 | 256.5
939 | 703 | 564.8 | 225.92 | 264.0875 | 450.7 | 349.4 | 349.3 | 289.8 | 570.7 | 57.4 | 18.6 | 105 | 4.9 | 215.4 | 4.9 | 869.5 | 854.9 | 184.9 | 844.9 | 761.7 | 882.7 | 737.4 | 670.5 | 704.2 | 657.9 | 574.7 | 747 | 86.7 | 202.7 | 273.5 | 528.8 | 582 | 595.9 | 416 | 597.7 | 166.1 | 386.8 | 352.2 | 226.7 | 284 | 387.9 | 256.9
940 | 704 | 565.3 | 226.12 | 264.3213 | 451.1 | 348.4 | 348.1 | 290.3 | 569.6 | 57.3 | 18.6 | 105.1 | 4.8 | 234.4 | 4.3 | 866.5 | 852.2 | 184.7 | 846.1 | 761.8 | 881.2 | 735.6 | 668.6 | 696.3 | 656.7 | 575.3 | 747.9 | 86.9 | 203 | 273.8 | 529 | 581.8 | 590.7 | 416.9 | 598.5 | 166.5 | 387 | 352.7 | 227.2 | 284.4 | 388.4 | 257.3
941 | 705 | 566.3 | 226.52 | 264.7888 | 450.8 | 348 | 347.8 | 291.2 | 566.6 | 57.3 | 18.6 | 105.2 | 4.6 | 235.4 | 4.5 | 859.6 | 850.2 | 184.7 | 847.5 | 761.6 | 880.2 | 734.2 | 668 | 688.6 | 655.8 | 575.9 | 746.1 | 87.2 | 203.3 | 274 | 529.3 | 582.5 | 587.4 | 417.8 | 595.2 | 167 | 386.9 | 352.9 | 227.8 | 284.7 | 389 | 257.7
942 | 706 | 565 | 226 | 264.181 | 455.4 | 347.8 | 348.2 | 292 | 565.3 | 57.4 | 18.6 | 105.2 | 4.3 | 238.1 | 5.1 | 863.9 | 854.7 | 184.1 | 847.9 | 760.6 | 878.4 | 731.7 | 667.7 | 682.1 | 656.4 | 576.4 | 743.7 | 87.4 | 203.6 | 274.3 | 529.8 | 582.5 | 593.2 | 418.7 | 597.4 | 167.4 | 388 | 353.7 | 228.5 | 285.1 | 389.5 | 258.1
943 | 707 | 564.5 | 225.8 | 263.9472 | 456.4 | 348 | 348.5 | 294 | 564.1 | 57.4 | 18.6 | 105.2 | 4.7 | 261.6 | 6.8 | 862.6 | 851.6 | 183.7 | 847.7 | 760.8 | 877.7 | 731.7 | 668.4 | 686.1 | 656.8 | 577 | 742 | 87.6 | 203.9 | 274.6 | 530.4 | 582.4 | 595.2 | 419.6 | 600.4 | 167.9 | 388.9 | 354.4 | 229.2 | 285.4 | 390 | 258.5
944 | 708 | 566.4 | 226.56 | 264.8356 | 457.8 | 347.8 | 349.9 | 294.8 | 566.4 | 57.5 | 18.6 | 105.3 | 5.1 | 245.9 | 7.1 | 869 | 855.1 | 183.5 | 848.3 | 761.4 | 877.8 | 733.4 | 669.7 | 687.3 | 656.8 | 577.5 | 743.5 | 87.8 | 204.3 | 275 | 530.9 | 585 | 597 | 420.5 | 598.4 | 168.3 | 389.5 | 355 | 229.9 | 285.6 | 390.6 | 258.9
945 | 709 | 566.7 | 226.68 | 264.9759 | 457.5 | 348.3 | 351.2 | 294.7 | 569 | 57.5 | 18.6 | 105.4 | 5.2 | 224.3 | 7 | 870.4 | 853.5 | 183.4 | 848.9 | 761.6 | 878.4 | 734 | 669.7 | 686.1 | 656.2 | 578.1 | 744.4 | 88 | 204.6 | 275.1 | 531.2 | 586.5 | 597.2 | 421.5 | 597.9 | 168.8 | 389.9 | 356 | 230.7 | 285.8 | 391.2 | 259.4
946 | 710 | 565.2 | 226.08 | 264.2745 | 456.4 | 349.4 | 350.6 | 294.6 | 570 | 57.6 | 18.6 | 105.4 | 6 | 203.4 | 7.1 | 869.2 | 850 | 183 | 849.6 | 761.5 | 879.5 | 734.7 | 669.4 | 686.4 | 655.6 | 578.7 | 745.3 | 88.3 | 204.9 | 275.4 | 531.9 | 588.2 | 595.1 | 422.4 | 597.8 | 169.3 | 390 | 356.6 | 231.6 | 286 | 391.7 | 259.8
947 | 711 | 566.6 | 226.64 | 264.9291 | 458.5 | 350.3 | 349 | 294.5 | 572.1 | 57.7 | 18.6 | 105.5 | 5.5 | 196.3 | 7.8 | 866 | 845.3 | 183.6 | 849.4 | 761.5 | 880.2 | 735.8 | 669.3 | 689 | 655.4 | 579.3 | 747 | 88.5 | 205.2 | 275.8 | 532.8 | 590.3 | 600.2 | 423.3 | 598.7 | 169.8 | 390.4 | 356.8 | 232.4 | 286.1 | 392.3 | 260.1
948 | 712 | 565.5 | 226.2 | 264.4148 | 462.3 | 350.8 | 348.8 | 295.1 | 573.2 | 57.7 | 18.6 | 105.8 | 5.2 | 196.7 | 7.3 | 864.6 | 848.6 | 184.4 | 849.2 | 761.5 | 880.8 | 736.3 | 668.2 | 689.2 | 655.1 | 580 | 746.6 | 88.7 | 205.3 | 276.1 | 533.4 | 297.7 | 600.7 | 424.3 | 598.7 | 170.2 | 390.6 | 356.4 | 233.2 | 286.3 | 392.8 | 260.5
949 | 713 | 566 | 226.4 | 264.6486 | 466.6 | 351.2 | 349.5 | 296.2 | 576.3 | 57.8 | 18.6 | 105.9 | 4.7 | 228.6 | 5.5 | 860.7 | 847.3 | 184.2 | 849.2 | 761.9 | 881.3 | 736.4 | 668.4 | 689.7 | 654.7 | 580.5 | 749.1 | 88.9 | 205.5 | 276.4 | 534.3 | 431.3 | 601.8 | 425.3 | 597.6 | 170.7 | 390.6 | 356.1 | 234 | 286.6 | 393.3 | 261
950 | 714 | 567.2 | 226.88 | 265.2096 | 475.3 | 351.9 | 349.2 | 297.1 | 577.7 | 57.8 | 18.6 | 106 | 5.3 | 240.3 | 5 | 860.8 | 846.8 | 183.7 | 849.2 | 761.6 | 881.1 | 735.1 | 667.8 | 688.5 | 654.2 | 581 | 748.6 | 89.2 | 205.6 | 276.5 | 534.9 | 434.5 | 598 | 426.3 | 596.6 | 171.2 | 391 | 356.1 | 234.8 | 287 | 393.7 | 261.3
951 | 715 | 567.3 | 226.92 | 265.2564 | 476.4 | 351.8 | 348.6 | 298.2 | 578 | 57.9 | 18.6 | 106.1 | 5.7 | 227.7 | 4.5 | 861.8 | 847.3 | 184.5 | 848.7 | 761.6 | 881.3 | 734.2 | 667.4 | 688.7 | 653.3 | 581.7 | 745.8 | 89.4 | 205.9 | 276.7 | 535.9 | 278.4 | 593.4 | 427.3 | 596 | 171.7 | 392.4 | 356 | 235.4 | 287.2 | 394.2 | 261.7
952 | 716 | 566.9 | 226.76 | 265.0694 | 477.5 | 352.1 | 348.2 | 298.8 | 582.3 | 57.9 | 18.6 | 106.2 | 5.8 | 223.8 | 4.4 | 859.9 | 847.6 | 184.3 | 848.6 | 761.5 | 880.6 | 733.7 | 667.4 | 686.2 | 652.9 | 582 | 744.5 | 89.6 | 206.1 | 277 | 536.9 | 597.2 | 595.5 | 428.3 | 597 | 172.2 | 392.1 | 356.2 | 236.1 | 287.5 | 394.7 | 262.2
953 | 717 | 565.8 | 226.32 | 264.555 | 478.9 | 353.1 | 348.7 | 298.9 | 585 | 57.9 | 18.6 | 106.3 | 5.8 | 232.8 | 4.5 | 857 | 842.6 | 183.5 | 848.6 | 761.1 | 879.6 | 732.5 | 666.4 | 683.4 | 652 | 582.3 | 745.5 | 89.8 | 206.4 | 277.2 | 537.5 | 475.7 | 593.8 | 429.2 | 595.9 | 172.7 | 392.5 | 356.5 | 236.8 | 287.9 | 395.2 | 262.6
954 | 718 | 567.2 | 226.88 | 265.2096 | 477.3 | 353.6 | 349.3 | 299.2 | 582.3 | 57.9 | 18.6 | 106.3 | 5.2 | 233.9 | 4.6 | 861.2 | 842.2 | 183.3 | 848.5 | 760.6 | 879.9 | 731.3 | 665.1 | 684.4 | 651.2 | 582.9 | 743.7 | 90.1 | 206.8 | 277.6 | 538.3 | 367 | 592 | 430.2 | 595.9 | 173.1 | 393.1 | 356.6 | 237.4 | 288.2 | 395.7 | 263
955 | 719 | 565.5 | 226.2 | 264.4148 | 475.4 | 354.2 | 349.5 | 299.4 | 588 | 58 | 18.6 | 106.3 | 5.2 | 200.7 | 4.6 | 863.6 | 847.5 | 183.3 | 848.5 | 760 | 880.4 | 731.9 | 667.6 | 686.2 | 653 | 583.3 | 742.8 | 90.3 | 207.1 | 278.1 | 540 | 601.6 | 600.7 | 431.2 | 598.5 | 173.6 | 393.5 | 357.2 | 238.1 | 288.5 | 396.2 | 263.4
956 | 720 | 565.1 | 226.04 | 264.2277 | 476.4 | 354.9 | 350.1 | 299.5 | 589.4 | 58 | 18.6 | 106.4 | 4.9 | 222.3 | 4.8 | 869.8 | 851 | 183.6 | 848.5 | 759.8 | 879.7 | 731.1 | 668.4 | 684.1 | 654 | 583.9 | 743.7 | 90.5 | 207.4 | 278.3 | 541.1 | 466.6 | 598.7 | 432.1 | 601.6 | 174.1 | 393.9 | 358.6 | 238.8 | 288.9 | 396.8 | 263.9
957 | 721 | 567.1 | 226.84 | 265.1629 | 477.5 | 355.4 | 350.5 | 299.4 | 583.2 | 58.1 | 18.6 | 106.4 | 4.9 | 257.7 | 5.1 | 872.1 | 852.4 | 184.3 | 847.6 | 759.6 | 880.2 | 730.6 | 668.5 | 688.4 | 653.8 | 584.5 | 743.4 | 90.7 | 207.7 | 278.5 | 541.8 | 600.8 | 596.9 | 433 | 599.3 | 174.6 | 394.2 | 360.3 | 239.5 | 289 | 397.3 | 264.3
958 | 722 | 567.3 | 226.92 | 265.2564 | 475.7 | 355.5 | 350.4 | 299.4 | 581.4 | 58.2 | 18.6 | 106.4 | 4.8 | 241.4 | 5.1 | 872.8 | 855.4 | 184.8 | 847.3 | 759.9 | 879.7 | 730.1 | 668.2 | 687.5 | 653.3 | 584.9 | 742.7 | 91 | 208 | 278.8 | 542.8 | 603.4 | 592.3 | 434.1 | 599.3 | 175.1 | 395.1 | 361.7 | 240.2 | 289.3 | 397.9 | 264.7
959 | 723 | 568.4 | 227.36 | 265.7707 | 476.5 | 355.3 | 350.2 | 300.9 | 581.3 | 58.2 | 18.6 | 106.4 | 4.8 | 245.6 | 5.2 | 871.5 | 857 | 185.3 | 847.9 | 759.7 | 878.7 | 728.7 | 666.9 | 682 | 652.8 | 585.6 | 741.5 | 91.2 | 208.2 | 279.1 | 543.5 | 603.4 | 592.9 | 435.2 | 601.9 | 175.7 | 395.8 | 364 | 240.9 | 289.7 | 398.4 | 265.1
960 | 724 | 567 | 226.8 | 265.1161 | 478.5 | 355 | 350.2 | 302.7 | 581.7 | 58.2 | 18.6 | 106.4 | 5 | 245 | 5.1 | 866.6 | 855.5 | 185.3 | 848.1 | 759.3 | 877.2 | 726.8 | 665.9 | 677.5 | 653.1 | 586.3 | 738.6 | 91.4 | 208.5 | 279.4 | 544.8 | 604.1 | 601.5 | 436.2 | 605.2 | 176.2 | 397 | 366.1 | 241.6 | 290.1 | 398.9 | 265.6
961 | 725 | 565.6 | 226.24 | 264.4615 | 479.8 | 354.9 | 350.5 | 304.3 | 583.1 | 58.3 | 18.6 | 106.4 | 5 | 235.8 | 5.4 | 871.5 | 858.2 | 184.8 | 847.8 | 759 | 876.7 | 725.7 | 666 | 674.8 | 653.9 | 586.9 | 737.6 | 91.6 | 208.8 | 279.5 | 546.4 | 603.8 | 617.3 | 437.1 | 609.5 | 176.7 | 398 | 367.3 | 242.4 | 290.4 | 399.5 | 266.1
962 | 726 | 568 | 227.2 | 265.5837 | 479.4 | 355.1 | 350.6 | 305 | 580.7 | 58.3 | 18.6 | 106.5 | 5.3 | 254.6 | 5 | 873.3 | 859.7 | 184.8 | 848 | 758.7 | 876.3 | 725.5 | 666 | 675.1 | 653.4 | 587.4 | 737.2 | 91.9 | 209.2 | 279.7 | 546.9 | 602.4 | 608.4 | 438 | 608.7 | 177.2 | 399.1 | 368 | 243.2 | 290.8 | 400.1 | 266.6
963 | 727 | 567.6 | 227.04 | 265.3967 | 477.4 | 355.8 | 351.7 | 305.1 | 577.8 | 58.3 | 18.6 | 106.6 | 5.9 | 240.8 | 4.7 | 871.8 | 864 | 185.7 | 849.1 | 759.2 | 876.8 | 726.7 | 666.6 | 679.8 | 653 | 587.9 | 736.3 | 92.1 | 209.5 | 280.1 | 548 | 600.9 | 611.3 | 438.9 | 605.6 | 177.7 | 399.5 | 368.3 | 243.9 | 291 | 400.6 | 267
964 | 728 | 568.4 | 227.36 | 265.7707 | 476.4 | 356.5 | 352.6 | 304.2 | 578.9 | 58.3 | 18.6 | 106.7 | 6 | 233 | 5 | 872.4 | 867.2 | 186.9 | 850.2 | 759.8 | 876.8 | 729.4 | 668.5 | 688.9 | 653.3 | 588.5 | 738.1 | 92.3 | 209.8 | 280.5 | 549.2 | 600.5 | 614.3 | 440 | 606.8 | 178.3 | 398.9 | 368.5 | 244.5 | 291.2 | 401.1 | 267.5
965 | 729 | 566.5 | 226.6 | 264.8823 | 475.3 | 357.4 | 353.4 | 302.8 | 577.5 | 58.4 | 18.6 | 106.9 | 5.7 | 211.3 | 4.9 | 876.3 | 865.5 | 187.2 | 850.1 | 760.3 | 876.8 | 731.7 | 670.4 | 696.6 | 652.8 | 589.1 | 739.5 | 92.6 | 210.2 | 280.8 | 549.8 | 599.7 | 613 | 441 | 605.5 | 178.8 | 398.1 | 368.4 | 245.1 | 291.4 | 401.7 | 267.8
966 | 730 | 566.1 | 226.44 | 264.6953 | 475.6 | 358.7 | 353.3 | 302.7 | 576.8 | 58.4 | 18.6 | 107.1 | 4.9 | 247.8 | 4.5 | 872.6 | 864.3 | 187 | 849.4 | 760.9 | 876.9 | 732.6 | 670.8 | 697.9 | 651.9 | 589.7 | 740.1 | 92.8 | 210.5 | 281 | 550.7 | 599.5 | 612.9 | 441.9 | 602.9 | 179.4 | 398.5 | 368.7 | 245.8 | 291.6 | 402.2 | 268.2
967 | 731 | 565.3 | 226.12 | 264.3213 | 473.5 | 358.9 | 353.5 | 302.8 | 576.7 | 58.4 | 18.5 | 107.3 | 4.8 | 269.2 | 4.4 | 875.3 | 867.5 | 187.3 | 848.9 | 761.4 | 877.4 | 733.9 | 672.2 | 702.9 | 651.3 | 590.3 | 740.8 | 93 | 210.8 | 281.3 | 551.5 | 599.7 | 614.7 | 442.7 | 602.1 | 179.9 | 397.9 | 368.7 | 246.5 | 291.7 | 402.7 | 268.6
968 | 732 | 565.9 | 226.36 | 264.6018 | 473.3 | 359.3 | 353.7 | 302.7 | 575.6 | 58.4 | 18.5 | 107.4 | 5.4 | 250.4 | 4.5 | 881.6 | 869 | 187.9 | 849.1 | 761.9 | 877.1 | 733.6 | 672.3 | 703.1 | 650.6 | 590.9 | 741.9 | 93.2 | 211.1 | 281.6 | 552.1 | 599.6 | 609.3 | 443.7 | 602.9 | 180.5 | 397.7 | 368.6 | 247.1 | 292 | 403.1 | 269
969 | 733 | 565.7 | 226.28 | 264.5083 | 474.6 | 359.8 | 353.2 | 302.9 | 574.7 | 58.5 | 18.5 | 107.7 | 5.2 | 241.7 | 4.5 | 879.1 | 867.4 | 187.7 | 850.1 | 762.1 | 877.1 | 732.5 | 671.3 | 702.2 | 649.3 | 591.5 | 739.6 | 93.4 | 211.4 | 281.7 | 552.8 | 599 | 603.6 | 444.6 | 601.6 | 181 | 397.7 | 368 | 247.7 | 292.4 | 403.6 | 269.4
970 | 734 | 565 | 226 | 264.181 | 474.2 | 358.7 | 352.3 | 303.7 | 573.4 | 58.5 | 18.5 | 107.9 | 5.5 | 240.9 | 4.3 | 875.9 | 865.8 | 187.7 | 850 | 762.5 | 876.7 | 732.5 | 671.3 | 706.7 | 648.8 | 592.2 | 739.5 | 93.7 | 211.8 | 282 | 553.8 | 598.7 | 601.5 | 445.5 | 601.3 | 181.6 | 397.6 | 367.3 | 248.3 | 292.6 | 404.1 | 269.8
971 | 735 | 564.1 | 225.64 | 263.7602 | 470.7 | 357.9 | 352.2 | 303.3 | 574.8 | 58.5 | 18.5 | 108.2 | 5.3 | 214.1 | 4 | 873.6 | 860.8 | 187.6 | 849.9 | 762.9 | 876.7 | 732.9 | 671.4 | 706.9 | 648.4 | 592.9 | 740.3 | 93.9 | 212.1 | 282.4 | 554.6 | 598.3 | 598.7 | 446.4 | 600.7 | 182.2 | 397.7 | 366.8 | 248.8 | 293 | 404.6 | 270.1
972 | 736 | 565.9 | 226.36 | 264.6018 | 470.3 | 357.5 | 352 | 303.1 | 582.1 | 58.6 | 18.5 | 108.2 | 5.6 | 183.3 | 4.6 | 866.8 | 852.7 | 187.1 | 849.1 | 762.3 | 876.5 | 729.8 | 668.1 | 694.2 | 647.1 | 593.5 | 738.9 | 94.1 | 212.3 | 282.8 | 555.1 | 600.3 | 599.5 | 447.4 | 603.4 | 182.8 | 399 | 367.7 | 249.5 | 293.4 | 405.1 | 270.5
973 | 737 | 566.6 | 226.64 | 264.9291 | 476.7 | 358 | 351.8 | 305.5 | 589.4 | 58.6 | 18.5 | 108.2 | 5.6 | 202.7 | 5.3 | 864.1 | 851.1 | 187.4 | 848.5 | 761.3 | 874.9 | 726 | 663.9 | 679.8 | 646.1 | 593.9 | 735.3 | 94.4 | 212.5 | 283.3 | 553.8 | 601.6 | 593.1 | 448.5 | 603.5 | 183.4 | 401.5 | 368.8 | 250.3 | 293.9 | 405.6 | 271
974 | 738 | 568.4 | 227.36 | 265.7707 | 481.8 | 358 | 353.7 | 309.8 | 591.7 | 58.6 | 18.5 | 108.3 | 5.6 | 241.3 | 4.9 | 855.9 | 847.9 | 187.8 | 848.5 | 760.7 | 874.6 | 723.3 | 662.5 | 671.5 | 646.8 | 594.7 | 733.4 | 94.6 | 212.8 | 283.6 | 553.1 | 599.3 | 592.7 | 449.4 | 607 | 184 | 402.9 | 369.7 | 251.1 | 294.2 | 406.2 | 271.5
975 | 739 | 569.6 | 227.84 | 266.3318 | 482.8 | 357.9 | 357.4 | 310.8 | 587.5 | 58.7 | 18.5 | 108.4 | 5.6 | 259.8 | 4 | 849.9 | 849 | 187.4 | 848.8 | 760.4 | 873.6 | 721.7 | 661.1 | 664.9 | 647.8 | 595.5 | 732.4 | 94.8 | 213 | 283.8 | 552.8 | 596.7 | 592.7 | 450.4 | 607.2 | 184.6 | 404.1 | 371.7 | 251.8 | 294.6 | 406.8 | 272
976 | 740 | 568.3 | 227.32 | 265.724 | 484.6 | 357.7 | 358.6 | 312 | 587.2 | 58.9 | 18.5 | 108.6 | 5.4 | 225 | 3.6 | 853.8 | 855.4 | 186 | 849.3 | 760.4 | 872.5 | 721.8 | 661.9 | 669.7 | 648.3 | 596.3 | 732.7 | 95 | 213.3 | 284 | 553.1 | 596.1 | 591.6 | 451.4 | 606.9 | 185.2 | 404.2 | 372.9 | 252.4 | 295.1 | 407.4 | 272.5
977 | 741 | 566.5 | 226.6 | 264.8823 | 486.2 | 357.7 | 358.3 | 311.3 | 581.8 | 59 | 18.5 | 108.6 | 4.8 | 203.8 | 3.9 | 856.6 | 862 | 185.7 | 849.8 | 760.5 | 873 | 723.8 | 663.1 | 675.7 | 648.8 | 597.2 | 731.9 | 95.2 | 213.5 | 284.5 | 554.2 | 593.3 | 595.1 | 452.4 | 605.8 | 185.8 | 404 | 373.1 | 253 | 295.4 | 408 | 272.9
978 | 742 | 565.2 | 226.08 | 264.2745 | 489.9 | 358.8 | 358.1 | 309.8 | 580.1 | 59.1 | 18.5 | 108.7 | 5.4 | 234 | 4 | 863.8 | 865.5 | 185.7 | 849.8 | 760.5 | 874.2 | 726.8 | 664.3 | 682.1 | 648.4 | 597.9 | 733.4 | 95.5 | 213.9 | 284.6 | 555.1 | 592.5 | 595.6 | 453.2 | 604.5 | 186.4 | 403.4 | 373.7 | 253.6 | 295.6 | 408.5 | 273.3
979 | 743 | 565.5 | 226.2 | 264.4148 | 492 | 360.8 | 359.6 | 308.9 | 578.3 | 59.2 | 18.5 | 108.6 | 5.4 | 202.6 | 4.1 | 870.4 | 867 | 185.3 | 849.6 | 760.4 | 875 | 728 | 664.6 | 686.8 | 647.3 | 598.7 | 734.3 | 95.7 | 214.2 | 284.6 | 555.5 | 591.7 | 590.5 | 454.2 | 601.8 | 187 | 402.9 | 374.6 | 254 | 296 | 409 | 273.6
980 | 744 | 567.1 | 226.84 | 265.1629 | 503.7 | 361.7 | 359.7 | 308.7 | 573.9 | 59.4 | 18.5 | 108.6 | 5.2 | 198.6 | 4.4 | 873.7 | 867.3 | 185.8 | 849.8 | 761.1 | 875.6 | 729.1 | 665.4 | 692.8 | 646.6 | 599.7 | 735.5 | 95.9 | 214.5 | 284.8 | 556.1 | 591.1 | 588 | 455.1 | 602 | 187.6 | 402.4 | 375.4 | 254.5 | 296.4 | 409.5 | 274
981 | 745 | 567.2 | 226.88 | 265.2096 | 508.1 | 361.1 | 359.3 | 309.4 | 570.9 | 59.5 | 18.5 | 108.6 | 5.1 | 220.6 | 4.7 | 875.8 | 866 | 186 | 850.3 | 761.2 | 875.7 | 728 | 665.2 | 690.9 | 645.8 | 600.6 | 735.4 | 96.2 | 214.9 | 285.1 | 556.6 | 590.4 | 583.9 | 455.9 | 602.5 | 188.3 | 401.9 | 375.5 | 255 | 296.7 | 410 | 274.4
982 | 746 | 566.2 | 226.48 | 264.7421 | 512.8 | 361 | 358.8 | 310.1 | 568.7 | 59.5 | 18.5 | 108.6 | 5.5 | 219 | 4.4 | 876.6 | 859.6 | 185.2 | 850.7 | 761.5 | 875.7 | 727.3 | 665.9 | 690.8 | 645.2 | 601.4 | 735.6 | 96.4 | 215.2 | 285.5 | 557 | 590 | 577.8 | 456.8 | 602 | 188.9 | 401.7 | 374.8 | 255.5 | 297.1 | 410.4 | 274.7
983 | 747 | 563.9 | 225.56 | 263.6666 | 508.8 | 361.1 | 358.8 | 309.9 | 565.8 | 59.5 | 18.5 | 108.8 | 5.4 | 208.7 | 4.2 | 877.4 | 861.9 | 184.8 | 850.5 | 761.8 | 876.5 | 727 | 665.6 | 693 | 644.5 | 602.3 | 736 | 96.6 | 215.6 | 285.7 | 557.9 | 588.3 | 574.2 | 457.7 | 600.3 | 189.6 | 401.7 | 373.9 | 256 | 297.3 | 410.9 | 275.1
984 | 748 | 562.3 | 224.92 | 262.9185 | 507.6 | 360.9 | 359 | 309.1 | 565.8 | 59.5 | 18.5 | 109 | 5.3 | 209.3 | 4.5 | 875.1 | 860.7 | 184.2 | 850.5 | 762.1 | 878.1 | 729.5 | 667.6 | 700.4 | 644.3 | 603.4 | 736.9 | 96.9 | 215.9 | 285.9 | 559.4 | 587.5 | 576.8 | 458.5 | 600.5 | 190.2 | 401.5 | 372.9 | 256.6 | 297.4 | 411.4 | 275.5
985 | 749 | 561.7 | 224.68 | 262.638 | 518.7 | 361.8 | 359.7 | 308.4 | 566.3 | 59.5 | 18.5 | 109.1 | 5.3 | 224.6 | 4.5 | 873.2 | 859.5 | 184.3 | 850.6 | 762.2 | 878.8 | 730.5 | 668.1 | 703.9 | 644 | 604.4 | 739 | 97.1 | 216.3 | 286 | 560.4 | 587 | 576.3 | 459.4 | 600 | 190.8 | 401.8 | 373.2 | 257.2 | 297.5 | 411.9 | 275.9
986 | 750 | 563.9 | 225.56 | 263.6666 | 529.2 | 362.7 | 359.2 | 308.5 | 566.2 | 59.5 | 18.5 | 109.3 | 5.5 | 241.8 | 4.2 | 871.1 | 860.1 | 184.4 | 850.4 | 761.8 | 878.8 | 729.6 | 667 | 699.7 | 643.5 | 605.5 | 738.8 | 97.3 | 216.6 | 286.3 | 561.5 | 586.5 | 575 | 460.3 | 599.7 | 191.5 | 401.8 | 373.1 | 257.7 | 297.8 | 412.3 | 276.3
987 | 751 | 565.1 | 226.04 | 264.2277 | 530.4 | 362.4 | 358.5 | 309.5 | 567.9 | 59.6 | 18.5 | 109.4 | 5.9 | 254.9 | 4 | 869.5 | 858.5 | 184.1 | 850.3 | 761.6 | 878.1 | 727.8 | 665.8 | 691.6 | 643.3 | 606.6 | 737.9 | 97.5 | 217 | 286.6 | 563 | 588 | 569.9 | 461.1 | 600.5 | 192.2 | 405 | 373 | 258.4 | 298.2 | 412.8 | 276.7
988 | 752 | 565.8 | 226.32 | 264.555 | 539.6 | 362.3 | 358.2 | 311.4 | 567.3 | 59.6 | 18.5 | 109.4 | 5.8 | 249.1 | 3.9 | 865.2 | 853.2 | 184.1 | 850.6 | 761.5 | 878 | 727.3 | 665.1 | 692.7 | 642.8 | 607.8 | 736.3 | 97.7 | 217.3 | 286.8 | 564.5 | 588.5 | 567.3 | 461.9 | 599.6 | 192.8 | 404.6 | 373.1 | 259 | 298.5 | 413.3 | 277.1
989 | 753 | 565 | 226 | 264.181 | 540.8 | 362.4 | 359 | 311.8 | 571.8 | 59.5 | 18.5 | 109.6 | 5.1 | 237.2 | 3.9 | 861.7 | 849.6 | 184 | 850.6 | 761.2 | 877.2 | 727.1 | 664.6 | 688.7 | 642.4 | 608.9 | 737 | 98 | 217.6 | 287 | 565.7 | 589.5 | 568.3 | 462.7 | 599.6 | 193.5 | 404.6 | 373.5 | 259.5 | 298.9 | 413.7 | 277.6
990 | 754 | 565.1 | 226.04 | 264.2277 | 542.6 | 361.8 | 358.9 | 312.4 | 573.6 | 59.5 | 18.5 | 109.8 | 5.1 | 247.2 | 4 | 844.2 | 842.1 | 183.9 | 850.5 | 760.7 | 876 | 724.3 | 663.1 | 679.4 | 641.8 | 610 | 735.7 | 98.2 | 217.9 | 287.4 | 567 | 590.8 | 569 | 463.6 | 604.5 | 194.2 | 404.8 | 374.4 | 260.2 | 299.4 | 414.2 | 278
991 | 755 | 564.7 | 225.88 | 264.0407 | 545.1 | 360.9 | 359.2 | 314.6 | 572.1 | 59.5 | 18.5 | 109.9 | 5.9 | 254.3 | 4.4 | 840.7 | 837.4 | 183.4 | 850.9 | 760 | 873.8 | 721.6 | 659.1 | 672.2 | 640.7 | 611.2 | 733 | 98.4 | 218.2 | 287.6 | 568 | 590.4 | 563.9 | 464.4 | 601.8 | 194.9 | 405.5 | 375.1 | 260.8 | 299.7 | 414.7 | 278.4
992 | 756 | 564.6 | 225.84 | 263.9939 | 546.5 | 360.4 | 361.3 | 316.6 | 570.2 | 59.5 | 18.5 | 110.1 | 5.3 | 243.3 | 4.5 | 837.8 | 836.7 | 183.3 | 850.9 | 759.4 | 872.9 | 719.6 | 657 | 665.7 | 640.7 | 612.5 | 731.9 | 98.7 | 218.6 | 287.8 | 569.4 | 588.7 | 569.9 | 465.2 | 601.6 | 195.6 | 406.1 | 375 | 261.4 | 300.1 | 415.2 | 278.8
993 | 757 | 565 | 226 | 264.181 | 549.1 | 360.5 | 362.9 | 318.1 | 569.5 | 59.5 | 18.5 | 110.1 | 4.9 | 239.5 | 4.4 | 827.2 | 834.3 | 183.1 | 851.6 | 758.9 | 871.3 | 717.1 | 654 | 661.1 | 640.6 | 613.8 | 729.5 | 98.9 | 218.9 | 288 | 570.5 | 586.6 | 570.5 | 466 | 602.7 | 196.4 | 406.8 | 375.7 | 262.1 | 300.6 | 415.6 | 279.3
994 | 758 | 565.3 | 226.12 | 264.3213 | 548.5 | 360.1 | 364 | 319.1 | 569.9 | 59.5 | 18.5 | 110.2 | 4.9 | 236.4 | 4.2 | 825.2 | 832.3 | 183.1 | 852.2 | 758.5 | 868.7 | 716.5 | 653.2 | 662.1 | 640.8 | 615 | 729.7 | 99.1 | 219.2 | 288.5 | 571.4 | 586.1 | 566.8 | 466.8 | 601.3 | 197.1 | 407.4 | 376.4 | 262.8 | 300.9 | 416.1 | 279.7
995 | 759 | 566.2 | 226.48 | 264.7421 | 544.1 | 360.1 | 365.1 | 319.6 | 569.4 | 59.6 | 18.4 | 110.3 | 5.3 | 236.8 | 4 | 832.3 | 836.5 | 183.1 | 852.3 | 758.3 | 867.8 | 716 | 651.9 | 661.8 | 640.9 | 616.2 | 729.4 | 99.4 | 219.5 | 288.7 | 572.6 | 584.9 | 565.6 | 467.6 | 601.5 | 197.8 | 408.3 | 377.3 | 263.5 | 301.2 | 416.6 | 280.2
996 | 760 | 566 | 226.4 | 264.6486 | 538.9 | 360.2 | 365.9 | 320.5 | 567.5 | 59.6 | 18.4 | 110.4 | 5.3 | 231.1 | 3.6 | 841.6 | 841.8 | 182.8 | 852.4 | 758.3 | 868 | 716.3 | 652 | 663 | 640.8 | 617.3 | 728.8 | 99.6 | 219.8 | 288.9 | 573.8 | 584.4 | 565.8 | 468.3 | 601 | 198.5 | 409.5 | 378.2 | 264.3 | 301.6 | 417.1 | 280.6
997 | 761 | 564.9 | 225.96 | 264.1342 | 534.4 | 360.7 | 366.1 | 322.2 | 570.8 | 59.7 | 18.4 | 110.6 | 5.5 | 236.9 | 3.1 | 848.2 | 848.4 | 182.8 | 852.2 | 758 | 868.2 | 716.8 | 651.5 | 664.4 | 640.8 | 618.4 | 729.5 | 99.8 | 220 | 289.2 | 575.1 | 585.1 | 565.1 | 469.2 | 599.9 | 199.1 | 409.9 | 379 | 265.1 | 301.9 | 417.6 | 281.1
998 | 762 | 564.9 | 225.96 | 264.1342 | 528.5 | 361.2 | 365.5 | 322.4 | 572.3 | 59.8 | 18.4 | 110.8 | 5.2 | 256.3 | 3.1 | 853.6 | 840.9 | 182.1 | 851.4 | 757.8 | 869.5 | 717.3 | 651 | 666.4 | 640.8 | 619.4 | 728.7 | 100 | 220.3 | 289.5 | 576.5 | 585.2 | 565 | 470 | 599.5 | 199.8 | 410.1 | 379.7 | 265.7 | 302.2 | 418.2 | 281.6
999 | 763 | 564.9 | 225.96 | 264.1342 | 527.7 | 362.1 | 364.8 | 321.9 | 573.7 | 59.8 | 18.4 | 110.9 | 5.1 | 243.9 | 2.7 | 854.1 | 835.3 | 181.6 | 850 | 757.9 | 870.5 | 717.6 | 650.9 | 668.1 | 640.5 | 620.5 | 729.5 | 100.3 | 220.5 | 289.7 | 577.5 | 585.8 | 567.4 | 470.7 | 599 | 200.5 | 410 | 379.7 | 266.3 | 302.5 | 418.6 | 282
1000 | 764 | 564.9 | 225.96 | 264.1342 | 524.8 | 362.1 | 364.1 | 321.4 | 569.6 | 59.8 | 18.4 | 110.9 | 4.7 | 233.6 | 2.5 | 853.2 | 837.7 | 182.1 | 849.2 | 758.3 | 870.3 | 717.8 | 651.9 | 668.5 | 639.9 | 621.7 | 729.7 | 100.5 | 220.7 | 290 | 577.9 | 584 | 569.2 | 471.5 | 598.7 | 201.2 | 409.3 | 379.5 | 266.8 | 302.8 | 419.1 | 282.4
1001 | 765 | 565.1 | 226.04 | 264.2277 | 522.8 | 361.2 | 363.4 | 320.8 | 564.9 | 59.9 | 18.4 | 111.1 | 4.9 | 255.2 | 2.6 | 857.7 | 837 | 182.1 | 848.2 | 758.4 | 871.1 | 719.5 | 653.4 | 669.9 | 639.3 | 622.8 | 731.8 | 100.7 | 220.9 | 290.3 | 578.2 | 582.2 | 570.5 | 472.2 | 598.1 | 201.9 | 409 | 379.5 | 267.3 | 303 | 419.5 | 282.8
1002 | 766 | 565.4 | 226.16 | 264.368 | 523.2 | 360.4 | 363.2 | 319.2 | 567.7 | 60.1 | 18.4 | 111.3 | 5.3 | 272 | 3.7 | 854.1 | 836.1 | 182.1 | 847.2 | 758 | 871.7 | 719.3 | 651.7 | 665.3 | 637.9 | 624 | 732.6 | 101 | 221.2 | 290.4 | 578.3 | 581.4 | 572.5 | 473 | 598.3 | 202.6 | 409.3 | 380.3 | 267.9 | 303.3 | 419.9 | 283.1
1003 | 767 | 565.5 | 226.2 | 264.4148 | 524.2 | 359.9 | 363.1 | 318.8 | 567.1 | 60.2 | 18.4 | 111.5 | 5.7 | 270.8 | 4.1 | 849.9 | 833.1 | 181.3 | 846.9 | 758.4 | 872 | 720.1 | 653.4 | 669.4 | 636.5 | 625.1 | 732.7 | 101.2 | 221.4 | 290.8 | 578.4 | 579.8 | 571.5 | 473.7 | 597.5 | 203.3 | 409.2 | 380.8 | 268.4 | 303.6 | 420.3 | 283.5
1004 | 768 | 566.5 | 226.6 | 264.8823 | 525.2 | 359.9 | 363.5 | 318.4 | 565.2 | 60.3 | 18.4 | 111.6 | 5.1 | 274.5 | 4.1 | 848.3 | 831.8 | 180.5 | 846.7 | 758.1 | 872.6 | 720.4 | 654.1 | 671 | 635.5 | 626.2 | 733 | 101.4 | 221.7 | 291.1 | 578.8 | 577.5 | 573 | 474.4 | 598 | 204 | 409.5 | 380.5 | 268.9 | 304 | 420.7 | 283.9
1005 | 769 | 566.7 | 226.68 | 264.9759 | 520 | 359.4 | 364.1 | 318.3 | 566.2 | 60.5 | 18.4 | 111.7 | 5.4 | 259.1 | 3.7 | 847.7 | 835.1 | 179.9 | 846.5 | 757.5 | 872.2 | 719.3 | 652.6 | 666.3 | 634.7 | 627.3 | 732.4 | 101.7 | 221.9 | 291.3 | 579.2 | 576.3 | 572.3 | 475.1 | 597 | 204.7 | 409.4 | 380.4 | 269.5 | 304.3 | 421.2 | 284.3
1006 | 770 | 565.9 | 226.36 | 264.6018 | 515.4 | 359.4 | 363.5 | 319 | 566.4 | 60.6 | 18.4 | 111.8 | 5.6 | 241.4 | 3.3 | 851.2 | 839.1 | 180.2 | 846.1 | 757.1 | 872 | 717.5 | 650.9 | 664.5 | 633.7 | 628.1 | 731.4 | 101.9 | 222.2 | 291.5 | 579.5 | 575.5 | 565.9 | 475.8 | 595.1 | 205.4 | 409.6 | 380.6 | 270 | 304.7 | 421.6 | 284.7
1007 | 771 | 565.6 | 226.24 | 264.4615 | 522.4 | 359.3 | 363 | 320.2 | 567.1 | 60.7 | 18.4 | 111.9 | 5.6 | 238.8 | 3.3 | 860.1 | 840.4 | 180.8 | 845.3 | 757.4 | 872.7 | 716.5 | 652 | 666.6 | 633.3 | 629 | 730.4 | 102.1 | 222.4 | 291.8 | 580.4 | 576.5 | 564.3 | 476.6 | 594.7 | 206.1 | 409.6 | 380.6 | 270.6 | 304.9 | 422 | 285.1
1008 | 772 | 565.4 | 226.16 | 264.368 | 530.9 | 360.2 | 363.7 | 321.1 | 568 | 60.8 | 18.4 | 112 | 6 | 240 | 3.1 | 857.4 | 841.5 | 180.5 | 844.9 | 757.5 | 873.7 | 717 | 652.8 | 671.6 | 632.7 | 629.8 | 730.9 | 102.4 | 222.6 | 291.9 | 581.4 | 576.6 | 562.8 | 477.3 | 594 | 206.8 | 409.4 | 380.4 | 271.1 | 305.3 | 422.5 | 285.6
1009 | 773 | 566 | 226.4 | 264.6486 | 529.4 | 361.6 | 364.1 | 321.7 | 568 | 60.8 | 18.4 | 112.1 | 5.5 | 246.2 | 3.3 | 862.4 | 845 | 180.5 | 844.9 | 757.1 | 874.2 | 717.7 | 652.7 | 675.1 | 632.1 | 630.7 | 730.6 | 102.6 | 222.8 | 292.2 | 582.5 | 577.4 | 562.1 | 478 | 593.3 | 207.5 | 409 | 380.3 | 271.6 | 305.5 | 422.9 | 286
1010 | 774 | 565.4 | 226.16 | 264.368 | 531.6 | 362.3 | 364.2 | 321.9 | 568.1 | 60.8 | 18.4 | 112.2 | 5.5 | 256.1 | 4.5 | 870.5 | 846.9 | 181.1 | 844.7 | 756.8 | 875.4 | 718.7 | 653.2 | 678.8 | 631.7 | 631.5 | 730 | 102.8 | 223.1 | 292.4 | 583.8 | 578.9 | 563.9 | 478.8 | 593.3 | 208.2 | 408.1 | 379.9 | 272.1 | 305.8 | 423.3 | 286.3
1011 | 775 | 565.5 | 226.2 | 264.4148 | 537 | 363.7 | 363.5 | 321.8 | 569.3 | 60.7 | 18.4 | 112.3 | 6.4 | 249.7 | 5 | 860.7 | 844 | 181.6 | 844.8 | 756.9 | 876.2 | 720.6 | 654.6 | 680.1 | 631.7 | 632.4 | 729.8 | 103 | 223.4 | 292.9 | 585.5 | 580.6 | 570.7 | 479.7 | 593.7 | 208.9 | 406.9 | 379.4 | 272.5 | 306 | 423.7 | 286.7
1012 | 776 | 565.6 | 226.24 | 264.4615 | 537.1 | 364.2 | 363.5 | 321.7 | 573.6 | 60.7 | 18.4 | 112.4 | 6.1 | 245.4 | 5.2 | 840.6 | 835 | 181.8 | 845.7 | 756.3 | 874.7 | 720.3 | 654 | 675.7 | 631.1 | 633.4 | 730 | 103.3 | 223.6 | 293 | 586.3 | 582.8 | 570.4 | 480.4 | 593.7 | 209.7 | 405.9 | 379.2 | 272.8 | 306.2 | 424.2 | 287
1013 | 777 | 564.8 | 225.92 | 264.0875 | 532.4 | 363.8 | 364.1 | 321.5 | 568.8 | 60.6 | 18.4 | 112.6 | 5.9 | 228.7 | 5.2 | 844.1 | 833.8 | 182.3 | 846.3 | 755.9 | 873.2 | 719.1 | 652.6 | 673 | 630.1 | 634.4 | 728.8 | 103.5 | 223.9 | 293.2 | 586.3 | 582.5 | 566.9 | 481.3 | 592.5 | 210.4 | 405.4 | 379.1 | 273.1 | 306.4 | 424.5 | 287.4
1014 | 778 | 564.2 | 225.68 | 263.8069 | 531.1 | 365.2 | 363.9 | 321.9 | 567.3 | 60.6 | 18.4 | 112.9 | 6.3 | 218.7 | 4.8 | 852.7 | 839.9 | 181.2 | 846.7 | 755.7 | 873.2 | 718.9 | 652.4 | 671.2 | 629.9 | 635.3 | 728.4 | 103.7 | 224.2 | 293.5 | 586.7 | 584.3 | 566.3 | 482.3 | 592.9 | 211.1 | 405.4 | 378.9 | 273.3 | 306.7 | 424.9 | 287.7
1015 | 779 | 563.2 | 225.28 | 263.3393 | 527.6 | 366 | 364.7 | 321.8 | 568.9 | 60.7 | 18.4 | 113.1 | 5.9 | 244.6 | 4.7 | 853.9 | 837 | 181.1 | 847.2 | 755.4 | 874.1 | 719.2 | 652 | 670.7 | 629.6 | 636.3 | 728.1 | 104 | 224.4 | 293.9 | 587.9 | 586 | 566.8 | 483.2 | 592.8 | 211.7 | 404.6 | 378.1 | 273.6 | 306.9 | 425.3 | 288.1
1016 | 780 | 565.5 | 226.2 | 264.4148 | 529.3 | 366.5 | 364.7 | 322.5 | 569 | 60.7 | 18.4 | 113.2 | 5.1 | 242.9 | 4.6 | 853.5 | 834 | 181.6 | 847.2 | 754.9 | 874.7 | 718 | 650.6 | 667.6 | 628.9 | 637.3 | 727.9 | 104.2 | 224.7 | 294.2 | 588.4 | 586.9 | 569.2 | 484 | 592.8 | 212.4 | 403.6 | 377.9 | 273.8 | 307.1 | 425.7 | 288.5
1017 | 781 | 566 | 226.4 | 264.6486 | 535.8 | 367.2 | 365.4 | 322.5 | 567.1 | 60.7 | 18.3 | 113.4 | 5.8 | 237.2 | 4.1 | 849.6 | 834.2 | 182.4 | 847.1 | 754.6 | 874.8 | 716 | 648.1 | 663.3 | 627.9 | 638.3 | 726.6 | 104.4 | 225.1 | 294.2 | 588.2 | 587.4 | 564.5 | 484.7 | 592.5 | 213 | 402.8 | 377.2 | 274 | 307.3 | 426.1 | 288.9
1018 | 782 | 565.2 | 226.08 | 264.2745 | 536.1 | 367.6 | 365.1 | 322.1 | 567 | 60.8 | 18.3 | 113.5 | 6 | 224.9 | 3.6 | 840.4 | 830.9 | 181.6 | 847.2 | 754.2 | 875.1 | 715 | 645.6 | 660.9 | 627.4 | 639.2 | 725.6 | 104.7 | 225.4 | 294.6 | 588.5 | 589.5 | 564.2 | 485.7 | 592.5 | 213.5 | 402.4 | 376.4 | 274.2 | 307.5 | 426.4 | 289.2
1019 | 783 | 565.4 | 226.16 | 264.368 | 537.6 | 368.3 | 364.8 | 322 | 567.5 | 60.9 | 18.3 | 113.5 | 5.9 | 215.8 | 3.4 | 836.1 | 829.3 | 182.1 | 847.5 | 753.7 | 875.1 | 714.2 | 644.1 | 660.2 | 626.9 | 639.9 | 724.9 | 104.9 | 225.7 | 294.9 | 588.5 | 590.7 | 564.8 | 486.6 | 591.5 | 214.1 | 401.5 | 376 | 274.5 | 307.6 | 426.8 | 289.5
1020 | 784 | 564.7 | 225.88 | 264.0407 | 538.9 | 368.5 | 364.8 | 322.2 | 567.5 | 61 | 18.3 | 113.5 | 6 | 226.2 | 3.6 | 838.2 | 825.8 | 181.9 | 847.8 | 753.1 | 874.8 | 713.6 | 642.2 | 656.2 | 626.5 | 640.5 | 723.7 | 105.1 | 226.1 | 295.2 | 588.6 | 591.9 | 565.3 | 487.5 | 590.8 | 214.6 | 401.1 | 375.9 | 274.7 | 307.7 | 427.2 | 289.9
1021 | 785 | 564.2 | 225.68 | 263.8069 | 541.3 | 369.4 | 365.8 | 322.1 | 563.9 | 61.1 | 18.3 | 113.5 | 6.3 | 253.3 | 4.2 | 848.6 | 833.1 | 181.8 | 848 | 752.7 | 874.6 | 713.2 | 641.3 | 657.9 | 625.9 | 641.2 | 723.8 | 105.3 | 226.5 | 295.3 | 588.7 | 591.8 | 563.9 | 488.3 | 590.9 | 215 | 400.7 | 375.9 | 275 | 308 | 427.5 | 290.2
1022 | 786 | 565 | 226 | 264.181 | 540.9 | 369 | 366 | 322.2 | 564.2 | 61.1 | 18.3 | 113.6 | 6.9 | 253.7 | 4.4 | 857.1 | 841.7 | 181.8 | 848.3 | 752.6 | 874 | 713 | 642.3 | 663.6 | 625.9 | 642 | 724.3 | 105.6 | 226.8 | 295.4 | 589 | 593.3 | 561 | 489.2 | 592.5 | 215.5 | 400.5 | 375.9 | 275.3 | 308.4 | 427.9 | 290.6
1023 | 787 | 564.9 | 225.96 | 264.1342 | 538.3 | 368.8 | 365.7 | 322.7 | 561.2 | 61.2 | 18.3 | 113.7 | 7.2 | 245.1 | 4.8 | 856.6 | 841.1 | 182.2 | 848.6 | 752.1 | 873.4 | 711.9 | 642.4 | 662.4 | 625.9 | 642.7 | 723.8 | 105.8 | 227.1 | 295.6 | 589.7 | 594 | 559.6 | 490 | 593.5 | 215.9 | 400.8 | 376.3 | 275.5 | 308.7 | 428.3 | 291
1024 | 788 | 565.6 | 226.24 | 264.4615 | 533.5 | 368.8 | 365.1 | 322.5 | 559.8 | 61.2 | 18.3 | 113.8 | 6.3 | 240.6 | 4.6 | 842.2 | 833.8 | 181.6 | 848.6 | 752.1 | 872.4 | 710 | 641.2 | 657 | 625.7 | 643.4 | 722.9 | 106 | 227.4 | 295.9 | 590.6 | 594.3 | 555.7 | 490.8 | 592.9 | 216.3 | 402.6 | 376.9 | 275.9 | 309.1 | 428.7 | 291.4
1025 | 789 | 567.1 | 226.84 | 265.1629 | 528.9 | 368.4 | 365 | 323.7 | 558.1 | 61.2 | 18.3 | 114 | 6.2 | 234 | 4.9 | 834 | 830.2 | 181.3 | 848.3 | 751.5 | 871.8 | 708.2 | 638.5 | 652.2 | 624.6 | 644 | 721.2 | 106.3 | 227.7 | 296.1 | 591.5 | 594 | 550.2 | 491.4 | 590.7 | 216.7 | 403.8 | 377.5 | 276.2 | 309.5 | 429.1 | 291.8
1026 | 790 | 568.4 | 227.36 | 265.7707 | 526.3 | 368.2 | 365.2 | 324.2 | 557.4 | 61.3 | 18.3 | 114.3 | 6.1 | 221.4 | 5.8 | 831.2 | 826.4 | 182 | 847.8 | 750.9 | 872.1 | 706.9 | 634.3 | 649.1 | 623.3 | 644.6 | 719.5 | 106.5 | 228.1 | 296.4 | 592.4 | 594.5 | 549 | 492 | 587.9 | 217.1 | 404 | 378 | 276.5 | 309.8 | 429.5 | 292.2
1027 | 791 | 565.8 | 226.32 | 264.555 | 531.6 | 367.8 | 365 | 324 | 561.8 | 61.4 | 18.3 | 114.6 | 5.2 | 233.7 | 6.9 | 837.3 | 829.4 | 182.1 | 847.1 | 750.7 | 872.9 | 705.8 | 632.7 | 649.1 | 623 | 645.3 | 719.6 | 106.7 | 228.4 | 296.6 | 592.7 | 596.4 | 548.7 | 493 | 588.3 | 217.5 | 404.5 | 378.2 | 276.9 | 310.1 | 429.9 | 292.6
1028 | 792 | 562.9 | 225.16 | 263.1991 | 530.5 | 367.4 | 364.9 | 323.9 | 559.8 | 61.4 | 18.3 | 114.7 | 5.2 | 221.9 | 6.4 | 843.9 | 834 | 181.4 | 846.1 | 750.8 | 873.6 | 705.7 | 632.8 | 652.7 | 622.9 | 646.1 | 719.8 | 107 | 228.8 | 296.8 | 593.1 | 595.5 | 546.2 | 493.8 | 587.5 | 217.8 | 404.4 | 378.3 | 277.3 | 310.4 | 430.4 | 293
1029 | 793 | 562.9 | 225.16 | 263.1991 | 534.2 | 367 | 364.6 | 324.4 | 557.2 | 61.5 | 18.3 | 114.7 | 5.4 | 238.8 | 6.2 | 844.5 | 832.1 | 181.9 | 845.9 | 750.4 | 873.3 | 706.3 | 633.4 | 654 | 622.9 | 646.8 | 719.7 | 107.2 | 229.1 | 297 | 593.6 | 595.2 | 544.7 | 494.5 | 586.9 | 218.2 | 404.1 | 378.6 | 277.6 | 310.6 | 430.8 | 293.4
1030 | 794 | 564.3 | 225.72 | 263.8537 | 543.7 | 368.6 | 365.1 | 325.8 | 558.4 | 61.5 | 18.3 | 114.8 | 5.5 | 226.2 | 7.2 | 852.1 | 828.3 | 182.5 | 846 | 749.9 | 873.8 | 707.4 | 635.8 | 658.1 | 623.5 | 647.6 | 720.7 | 107.4 | 229.3 | 297.2 | 594.4 | 595.2 | 545.8 | 495.3 | 587.5 | 218.6 | 404.1 | 378.7 | 277.9 | 310.8 | 431.1 | 293.8
1031 | 795 | 566.1 | 226.44 | 264.6953 | 539.5 | 368.6 | 365.2 | 326.1 | 563.4 | 61.5 | 18.3 | 114.8 | 5.8 | 250.2 | 6.4 | 850 | 822.1 | 183.3 | 846.3 | 749.8 | 875.3 | 709.1 | 635.9 | 657.2 | 623.7 | 648.4 | 719.9 | 107.7 | 229.6 | 297.6 | 595.6 | 595.5 | 550.5 | 496.1 | 587.8 | 219 | 403.6 | 378.1 | 278.3 | 311 | 431.5 | 294.2
1032 | 796 | 565.6 | 226.24 | 264.4615 | 535.7 | 367.5 | 365.7 | 325.4 | 568.7 | 61.7 | 18.3 | 114.9 | 6 | 247.7 | 6.3 | 849.6 | 823 | 183.3 | 846.7 | 749.7 | 876.6 | 711.4 | 637.7 | 659.9 | 624.4 | 649.2 | 721.1 | 107.9 | 229.9 | 298 | 597 | 595.1 | 555.9 | 496.8 | 587.9 | 219.4 | 402.7 | 378 | 278.6 | 311.2 | 431.9 | 294.5
1033 | 797 | 565.5 | 226.2 | 264.4148 | 533.9 | 367.9 | 366.1 | 325.4 | 570.7 | 61.7 | 18.3 | 114.9 | 5.9 | 251.4 | 5.7 | 837.7 | 821.2 | 183.4 | 847 | 749 | 877 | 711.2 | 636.9 | 653.9 | 624.5 | 649.8 | 720.9 | 108.1 | 230.2 | 298.1 | 598.1 | 594.2 | 556 | 497.5 | 587.5 | 219.8 | 402.7 | 377.8 | 278.9 | 311.4 | 432.3 | 294.8
1034 | 798 | 565.1 | 226.04 | 264.2277 | 541.3 | 369.1 | 366 | 325.5 | 567.5 | 61.8 | 18.3 | 114.9 | 6.1 | 193.1 | 5.2 | 840.4 | 825.4 | 185.3 | 847.3 | 748 | 876.4 | 710 | 635.6 | 650.2 | 624.4 | 650.4 | 720.4 | 108.4 | 230.6 | 298.2 | 598.6 | 592.6 | 554.9 | 498.1 | 587.2 | 220.1 | 402.3 | 377.9 | 279.2 | 311.6 | 432.6 | 295.2
1035 | 799 | 565.1 | 226.04 | 264.2277 | 545.9 | 369.6 | 366 | 325.7 | 566.2 | 61.8 | 18.3 | 115 | 5.7 | 200.2 | 4.8 | 840.3 | 827.9 | 188.7 | 847.1 | 747.8 | 875.5 | 709.6 | 637.2 | 656.1 | 624.7 | 651.1 | 721 | 108.6 | 230.9 | 298.5 | 599.5 | 591.8 | 550.6 | 498.8 | 587.7 | 220.5 | 402 | 378 | 279.5 | 311.8 | 433 | 295.5
1036 | 800 | 565.6 | 226.24 | 264.4615 | 543.8 | 369.9 | 366.5 | 326.6 | 564 | 61.9 | 18.3 | 115.2 | 5.6 | 250.7 | 4.6 | 846.7 | 831.1 | 189.4 | 846.9 | 747.8 | 875.1 | 710 | 639.3 | 660 | 624.6 | 651.8 | 721.7 | 108.8 | 231.2 | 298.7 | 600.1 | 590.8 | 548.4 | 499.5 | 587.1 | 220.9 | 401.9 | 378.3 | 279.9 | 312.1 | 433.4 | 295.9
1037 | 801 | 566.4 | 226.56 | 264.8356 | 536.2 | 369.6 | 366.5 | 326.9 | 560.3 | 61.9 | 18.3 | 115.3 | 5.6 | 251.6 | 4.7 | 851.4 | 832 | 190.1 | 846.7 | 747.8 | 875.2 | 708.9 | 640.1 | 657.9 | 624.5 | 652.5 | 720.2 | 109.1 | 231.5 | 298.8 | 601 | 589.5 | 546.4 | 500.1 | 587.4 | 221.3 | 402.3 | 379.2 | 280.2 | 312.5 | 433.7 | 296.3
1038 | 802 | 566.2 | 226.48 | 264.7421 | 531.7 | 370.1 | 366.4 | 327.3 | 558.1 | 61.9 | 18.3 | 115.4 | 5.4 | 236.7 | 5.1 | 840.6 | 827.4 | 191.1 | 846.1 | 747.6 | 875.1 | 708.5 | 639.1 | 654.5 | 624.1 | 653.3 | 720.4 | 109.3 | 231.7 | 299.1 | 601.8 | 588.3 | 543.6 | 500.8 | 586.6 | 221.7 | 403.1 | 380.2 | 280.6 | 312.8 | 434.1 | 296.6
1039 | 803 | 565.6 | 226.24 | 264.4615 | 528.1 | 370.5 | 366.5 | 328.1 | 553.2 | 61.9 | 18.3 | 115.6 | 5.5 | 230.5 | 5.1 | 838.4 | 823.9 | 191.8 | 845.6 | 747.1 | 875.3 | 707 | 636 | 651.3 | 623.5 | 653.9 | 718.9 | 109.5 | 231.9 | 299.2 | 601.9 | 585.7 | 542.4 | 501.3 | 585.7 | 222.1 | 403.6 | 381.6 | 280.9 | 312.9 | 434.5 | 297
1040 | 804 | 565.1 | 226.04 | 264.2277 | 527.1 | 369.9 | 366.5 | 328.8 | 552.7 | 61.9 | 18.3 | 115.6 | 5.8 | 227 | 4.8 | 823.7 | 814.1 | 192.9 | 844.7 | 746.6 | 874.4 | 705.7 | 633.3 | 647.9 | 623.1 | 654.5 | 718 | 109.7 | 232.1 | 299.5 | 602 | 584.3 | 542.8 | 501.9 | 585 | 222.5 | 403.6 | 382.4 | 281.3 | 313.2 | 434.8 | 297.4
1041 | 805 | 565 | 226 | 264.181 | 526.1 | 369.3 | 366.4 | 329.4 | 554.5 | 62 | 18.2 | 115.8 | 5.6 | 215.8 | 4.9 | 816.2 | 809.6 | 193.9 | 843.9 | 746.3 | 873.2 | 705 | 632.8 | 647.9 | 622.8 | 655 | 718.8 | 110 | 232.4 | 299.8 | 602.2 | 583.3 | 541.7 | 502.4 | 584.6 | 222.9 | 404.2 | 383.1 | 281.6 | 313.6 | 435.2 | 297.8
1042 | 806 | 564.9 | 225.96 | 264.1342 | 526.6 | 368.8 | 367 | 329.7 | 556.4 | 62 | 18.2 | 115.9 | 5.5 | 211.2 | 4.5 | 819.6 | 806.5 | 192.2 | 842.8 | 746 | 872.8 | 704 | 631.4 | 645.2 | 622.4 | 655.5 | 718.2 | 110.2 | 232.7 | 300 | 602.3 | 581.8 | 542.5 | 503 | 584.4 | 223.3 | 404.6 | 384.1 | 282 | 313.9 | 435.6 | 298.2
1043 | 807 | 564.7 | 225.88 | 264.0407 | 526.9 | 368.1 | 368 | 329.5 | 555.8 | 62 | 18.2 | 116.1 | 5.8 | 232.7 | 4.5 | 809.3 | 795.7 | 192.7 | 841.5 | 745.3 | 870.7 | 702.8 | 630.5 | 640.2 | 622.3 | 656.2 | 716.9 | 110.4 | 233 | 300.2 | 602.4 | 580.2 | 544.6 | 503.6 | 585.4 | 223.7 | 404.9 | 385.2 | 282.4 | 314.3 | 435.9 | 298.6
1044 | 808 | 564.9 | 225.96 | 264.1342 | 533 | 367.5 | 368.6 | 330.1 | 557.7 | 62.1 | 18.2 | 116.1 | 5.9 | 247.2 | 4.9 | 810.7 | 791.9 | 192.9 | 840.2 | 744.5 | 868.7 | 701.6 | 630.3 | 637.9 | 622.8 | 656.9 | 716.3 | 110.7 | 233.3 | 300.6 | 602.4 | 579.2 | 549.7 | 504.3 | 589.2 | 224.1 | 406.3 | 386.4 | 282.8 | 314.6 | 436.2 | 299
1045 | 809 | 565.2 | 226.08 | 264.2745 | 528.2 | 367.1 | 369.9 | 330.5 | 557.8 | 62.1 | 18.2 | 116.2 | 5.8 | 247.2 | 5.2 | 819.4 | 798.8 | 193.1 | 839.4 | 744 | 868 | 701.5 | 631.3 | 637.9 | 622.9 | 657.6 | 715.7 | 110.9 | 233.6 | 300.7 | 602.3 | 578.4 | 550.9 | 504.9 | 590.8 | 224.5 | 407.6 | 386.4 | 283.3 | 314.9 | 436.6 | 299.4
1046 | 810 | 566 | 226.4 | 264.6486 | 530.4 | 366.8 | 371.5 | 330.6 | 554.3 | 62.3 | 18.2 | 116.2 | 5.5 | 246 | 5.3 | 827.5 | 806.7 | 193 | 838.9 | 744 | 868.7 | 702.7 | 632.3 | 643.4 | 622.7 | 658.1 | 716.9 | 111.1 | 233.9 | 300.9 | 602.1 | 577.9 | 552.3 | 505.4 | 590.8 | 224.9 | 408.9 | 386.7 | 283.7 | 315.2 | 437 | 299.8
1047 | 811 | 566.5 | 226.6 | 264.8823 | 552 | 366.7 | 372 | 330.9 | 553.4 | 62.4 | 18.2 | 116.2 | 5.7 | 245.1 | 5.4 | 834.4 | 805.3 | 195.5 | 838.7 | 744.2 | 870 | 706.7 | 636.4 | 658.5 | 622.9 | 658.6 | 719 | 111.4 | 234.2 | 301.1 | 602.6 | 577.5 | 556.6 | 506.1 | 589.1 | 225.3 | 409.2 | 386.7 | 284.1 | 315.3 | 437.3 | 300.3
1048 | 812 | 567.5 | 227 | 265.3499 | 564.3 | 367.1 | 372.1 | 330.4 | 556.2 | 62.6 | 18.2 | 116.2 | 5.8 | 245.1 | 5.6 | 830.8 | 797.4 | 195.9 | 839 | 743.7 | 870.3 | 707.8 | 636.4 | 654.5 | 623 | 659.3 | 719.1 | 111.6 | 234.5 | 301.5 | 603.4 | 578.3 | 559.6 | 506.9 | 587.8 | 225.7 | 408.9 | 386.4 | 284.5 | 315.4 | 437.7 | 300.6
1049 | 813 | 567.2 | 226.88 | 265.2096 | 564.7 | 367.2 | 372.4 | 329.1 | 560.1 | 62.7 | 18.2 | 116.1 | 5.5 | 243.4 | 5.2 | 834 | 795.4 | 196.1 | 838 | 743.2 | 870.1 | 707.8 | 636.3 | 649.9 | 622.5 | 659.8 | 720.9 | 111.8 | 234.8 | 301.7 | 603.5 | 578.3 | 556.7 | 507.7 | 585 | 226.1 | 408.3 | 386 | 284.8 | 315.6 | 438 | 301
1050 | 814 | 567.3 | 226.92 | 265.2564 | 567.8 | 366.8 | 372.4 | 329.3 | 560.6 | 62.8 | 18.2 | 116.1 | 6.2 | 243.2 | 5.5 | 820.7 | 790.5 | 195.9 | 837 | 742.6 | 869.3 | 708.1 | 636.8 | 651.4 | 622.5 | 660.6 | 721.1 | 112.1 | 235.1 | 301.8 | 603.7 | 577.9 | 556.8 | 508.5 | 584.5 | 226.6 | 407.7 | 385.7 | 285.1 | 315.8 | 438.4 | 301.3
1051 | 815 | 566.3 | 226.52 | 264.7888 | 557.2 | 366.8 | 371.7 | 328.9 | 561 | 62.9 | 18.2 | 115.9 | 5.8 | 246.2 | 5.6 | 814.9 | 784 | 195.7 | 836 | 742.3 | 868.2 | 707.1 | 636.3 | 646.7 | 623.1 | 661.5 | 721.7 | 112.3 | 235.4 | 302.2 | 604.1 | 578.1 | 563.3 | 509.3 | 587.7 | 227 | 407.5 | 385.9 | 285.5 | 316 | 438.7 | 301.6
1052 | 816 | 567.2 | 226.88 | 265.2096 | 556.5 | 366.6 | 371.5 | 328.5 | 566.7 | 62.9 | 18.2 | 115.8 | 5 | 248 | 5.1 | 816.4 | 783.2 | 196.6 | 834.7 | 742.1 | 867.3 | 706.7 | 637.2 | 643.6 | 622.9 | 662.5 | 720.5 | 112.5 | 235.7 | 302.4 | 603.8 | 578.1 | 560.1 | 509.9 | 588.1 | 227.4 | 407.7 | 386 | 285.8 | 316.3 | 439.1 | 301.9
1053 | 817 | 566.4 | 226.56 | 264.8356 | 551.9 | 365.6 | 371.2 | 328.6 | 566.5 | 63 | 18.2 | 115.7 | 5.8 | 240.1 | 5 | 818.5 | 786.3 | 197.4 | 833.7 | 742.2 | 867 | 707.5 | 638.4 | 646.5 | 623.1 | 663.3 | 721.2 | 112.8 | 236 | 302.6 | 603.5 | 577.1 | 560.6 | 510.5 | 588.4 | 227.8 | 407.8 | 385.6 | 286.2 | 316.5 | 439.4 | 302.3
1054 | 818 | 565.7 | 226.28 | 264.5083 | 544.1 | 365.8 | 371.8 | 329.1 | 566.1 | 63 | 18.2 | 115.8 | 5.6 | 235.2 | 5.7 | 820 | 790.7 | 198.3 | 832.8 | 742.3 | 866.5 | 709.1 | 642 | 649.9 | 624 | 664.3 | 722.5 | 113 | 236.3 | 302.9 | 603.5 | 576.8 | 564 | 511.2 | 590.6 | 228.3 | 408.2 | 385.4 | 286.6 | 316.8 | 439.7 | 302.6
1055 | 819 | 566.2 | 226.48 | 264.7421 | 539.1 | 366.9 | 372.3 | 330.4 | 565.3 | 63 | 18.2 | 115.8 | 5.2 | 236.9 | 6.2 | 825.5 | 800.5 | 198.3 | 832.4 | 742.3 | 866.1 | 710.1 | 645 | 659.9 | 624.4 | 665.1 | 723.7 | 113.2 | 236.6 | 303.1 | 603.2 | 575.9 | 566.7 | 511.9 | 591.6 | 228.7 | 409 | 385.3 | 287 | 317.1 | 440.1 | 303
1056 | 820 | 566.1 | 226.44 | 264.6953 | 536.9 | 366.5 | 372.1 | 330.4 | 561.6 | 63 | 18.2 | 115.7 | 5.8 | 239.1 | 6.2 | 838.7 | 811.4 | 199.3 | 832.4 | 742.5 | 865.6 | 711.5 | 647.7 | 673.1 | 624.6 | 665.9 | 724.8 | 113.4 | 236.9 | 303.2 | 603.5 | 575.1 | 565.7 | 512.5 | 590.8 | 229.1 | 409.2 | 385.4 | 287.4 | 317.4 | 440.5 | 303.4
1057 | 821 | 565 | 226 | 264.181 | 547.7 | 366.8 | 371.5 | 329.9 | 557.9 | 63 | 18.2 | 115.6 | 5.4 | 213.8 | 5.4 | 843.5 | 820.6 | 198.2 | 832.6 | 743 | 866 | 713 | 650.5 | 677.9 | 624.9 | 666.6 | 725.4 | 113.7 | 237.2 | 303.4 | 604.1 | 574.8 | 562.1 | 513.2 | 588.5 | 229.5 | 409.1 | 385.3 | 287.7 | 317.7 | 440.9 | 303.8
1058 | 822 | 564.7 | 225.88 | 264.0407 | 554.6 | 368 | 370.4 | 330.2 | 555.7 | 63.1 | 18.2 | 115.5 | 5 | 206.5 | 6.1 | 849.2 | 826.5 | 196.7 | 833.3 | 743.4 | 866.4 | 714.1 | 652.9 | 684.5 | 625.2 | 667.2 | 726 | 113.9 | 237.6 | 303.7 | 605.1 | 575.1 | 564.2 | 513.7 | 588 | 229.9 | 409.3 | 385.4 | 288.1 | 318 | 441.2 | 304.1
1059 | 823 | 564.1 | 225.64 | 263.7602 | 549.7 | 368.6 | 369.3 | 330.4 | 555.6 | 63 | 18.2 | 115.4 | 5.3 | 217.1 | 7 | 858.4 | 832.2 | 196.8 | 833.5 | 743.7 | 866.9 | 714 | 654.1 | 687.4 | 625.3 | 667.9 | 725.7 | 114.1 | 237.9 | 303.8 | 606.2 | 575.1 | 563.3 | 514.4 | 588.6 | 230.3 | 409.6 | 385.4 | 288.5 | 318.3 | 441.6 | 304.5
1060 | 824 | 565.1 | 226.04 | 264.2277 | 541.7 | 369 | 368.3 | 331.1 | 554.8 | 63.1 | 18.2 | 115.4 | 5.1 | 228.5 | 6.4 | 861.3 | 831.7 | 195.3 | 833.1 | 743.9 | 867.9 | 713.3 | 654.4 | 689.8 | 625.2 | 668.5 | 725.4 | 114.3 | 238.2 | 304.1 | 607.3 | 575.9 | 560.3 | 515.2 | 588.6 | 230.7 | 409.9 | 385.4 | 288.8 | 318.6 | 442 | 304.8
1061 | 825 | 565.3 | 226.12 | 264.3213 | 532.4 | 369.8 | 367.7 | 331.9 | 555.1 | 63.2 | 18.2 | 115.4 | 5.3 | 225.9 | 5.8 | 859.7 | 828.8 | 196.3 | 833 | 744 | 868.4 | 713.5 | 655.2 | 689.5 | 625.3 | 669 | 724.9 | 114.6 | 238.5 | 304.3 | 608.4 | 576.5 | 557.5 | 516.1 | 587.6 | 231.1 | 410.2 | 385.1 | 289.2 | 318.8 | 442.3 | 305.2
1062 | 826 | 564.4 | 225.76 | 263.9004 | 532.1 | 370.7 | 367.3 | 332.2 | 553.9 | 63.4 | 18.2 | 115.4 | 5.2 | 227 | 5.5 | 846.6 | 821 | 196.8 | 832.7 | 743.8 | 867.8 | 711.3 | 652.9 | 680.8 | 625.1 | 669.6 | 724 | 114.8 | 238.8 | 304.5 | 608.7 | 576.6 | 554.9 | 516.6 | 587.7 | 231.5 | 410.8 | 385.3 | 289.6 | 319.1 | 442.7 | 305.5
1063 | 827 | 564.6 | 225.84 | 263.9939 | 526.8 | 370.4 | 366.7 | 333 | 553.5 | 63.5 | 18.2 | 115.5 | 5.6 | 230.4 | 5.4 | 833.8 | 813.5 | 195.7 | 831.8 | 743.2 | 866.8 | 707.8 | 648.9 | 671.5 | 624.5 | 670.3 | 721.5 | 115 | 239.1 | 304.8 | 608.7 | 576.1 | 551.9 | 517.1 | 587.3 | 231.9 | 411.3 | 385.7 | 290 | 319.4 | 443.1 | 305.9
1064 | 828 | 564.7 | 225.88 | 264.0407 | 528.5 | 369.5 | 366.2 | 334.6 | 553 | 63.6 | 18.2 | 115.7 | 6 | 233.5 | 4.9 | 821 | 808.8 | 196.6 | 830.7 | 742.4 | 865.4 | 706.2 | 647.1 | 664.1 | 624.4 | 670.8 | 720 | 115.3 | 239.3 | 305.1 | 608.7 | 575.9 | 551.5 | 517.5 | 589.4 | 232.3 | 412.1 | 386.6 | 290.5 | 319.8 | 443.5 | 306.3
1065 | 829 | 564.7 | 225.88 | 264.0407 | 528.1 | 368.6 | 367 | 336 | 551 | 63.7 | 18.2 | 116 | 6.1 | 225.7 | 4.6 | 823.3 | 806.8 | 195.5 | 829.8 | 741.9 | 865.7 | 705.2 | 646.4 | 659.9 | 624.1 | 671.4 | 719.6 | 115.5 | 239.5 | 305.3 | 608.5 | 575.3 | 548.5 | 518.1 | 589.3 | 232.7 | 412.4 | 387.7 | 290.9 | 320.2 | 443.8 | 306.8
1066 | 830 | 565.4 | 226.16 | 264.368 | 519 | 368.3 | 368.4 | 336.1 | 547 | 63.7 | 18.2 | 116.1 | 5.5 | 215.1 | 4.2 | 819.1 | 803.2 | 196.6 | 829.1 | 741.2 | 865.1 | 704.4 | 645.3 | 655.1 | 623.2 | 672.3 | 718.8 | 115.7 | 239.6 | 305.5 | 607.5 | 575.1 | 546.7 | 518.6 | 588.2 | 233.1 | 412.7 | 388.3 | 291.3 | 320.4 | 444.2 | 307.2
1067 | 831 | 566.7 | 226.68 | 264.9759 | 513.2 | 368.5 | 368.7 | 336.1 | 549.9 | 63.7 | 18.2 | 116.3 | 5.7 | 213.7 | 4.1 | 813.9 | 799.8 | 197.2 | 828.2 | 740.7 | 864.5 | 703.2 | 643.8 | 648.6 | 623.3 | 672.9 | 718.5 | 115.9 | 239.7 | 305.7 | 607.2 | 575.5 | 546.1 | 519.2 | 588.3 | 233.5 | 413.5 | 389.5 | 291.8 | 320.9 | 444.5 | 307.6
1068 | 832 | 567.4 | 226.96 | 265.3032 | 506.4 | 368.6 | 369.2 | 337 | 556.2 | 63.7 | 18.2 | 116.6 | 6 | 224.8 | 4.2 | 811.4 | 794.7 | 197.2 | 827.4 | 740.3 | 863.2 | 701.5 | 641.6 | 645.4 | 623.6 | 673.7 | 717.2 | 116.2 | 240 | 306 | 607.2 | 576.1 | 549 | 519.9 | 589.7 | 233.9 | 415.1 | 391.1 | 292.2 | 321.3 | 444.9 | 308
1069 | 833 | 567 | 226.8 | 265.1161 | 501.7 | 368.3 | 369.7 | 337.7 | 558.4 | 63.8 | 18.2 | 116.7 | 6.3 | 227.9 | 4.1 | 822.8 | 804.7 | 195.4 | 826.8 | 739.9 | 863.6 | 700.6 | 638.1 | 644.6 | 622.9 | 674.7 | 715.8 | 116.4 | 240.3 | 306.2 | 607 | 576 | 545.3 | 520.6 | 588.9 | 234.3 | 415.5 | 392.2 | 292.6 | 321.6 | 445.4 | 308.4
1070 | 834 | 563.4 | 225.36 | 263.4329 | 501 | 368.3 | 370.2 | 337.1 | 558.8 | 63.8 | 18.2 | 116.9 | 5.7 | 227.8 | 4 | 830.9 | 810.3 | 196.3 | 826.9 | 740 | 865 | 703.3 | 640.1 | 657.5 | 622.9 | 675.4 | 717.8 | 116.6 | 240.6 | 306.4 | 607.3 | 575.4 | 546 | 520.8 | 586.6 | 234.7 | 415.6 | 392.1 | 293 | 321.8 | 445.7 | 308.8
1071 | 835 | 563.1 | 225.24 | 263.2926 | 510.7 | 369 | 370.8 | 336.3 | 559 | 63.9 | 18.1 | 117.1 | 5.8 | 225.8 | 3.6 | 836.7 | 815.9 | 197.4 | 827.2 | 739.9 | 865.4 | 704.5 | 641.7 | 660.4 | 623.1 | 676 | 718.4 | 116.8 | 240.9 | 306.6 | 607.6 | 576 | 545.5 | 521.2 | 587.1 | 235.1 | 415.1 | 391.8 | 293.3 | 322.2 | 446.1 | 309.1
1072 | 836 | 564.6 | 225.84 | 263.9939 | 516 | 370.6 | 370.5 | 335.6 | 556.3 | 64 | 18.1 | 117.3 | 5.9 | 222.1 | 3.4 | 843.8 | 819 | 197.6 | 827.5 | 739.7 | 866 | 704.5 | 641.1 | 658.5 | 622.6 | 676.5 | 717.9 | 117.1 | 241.2 | 306.8 | 608.1 | 576.2 | 544.4 | 521.8 | 586.8 | 235.6 | 414.8 | 391.2 | 293.7 | 322.5 | 446.5 | 309.5
1073 | 837 | 567.4 | 226.96 | 265.3032 | 519.3 | 371.5 | 370.1 | 335.6 | 555.2 | 64 | 18.1 | 117.4 | 5.6 | 225.3 | 3.4 | 847.9 | 819.1 | 199.1 | 827.5 | 739.6 | 866.4 | 704.6 | 640 | 660.1 | 622.1 | 677.1 | 717.1 | 117.3 | 241.5 | 307 | 608.6 | 576.1 | 544.3 | 522.2 | 585.8 | 236 | 414.6 | 390.5 | 294 | 322.7 | 446.8 | 309.8
1074 | 838 | 566.9 | 226.76 | 265.0694 | 514.6 | 372.2 | 369.4 | 335.5 | 553.3 | 64.1 | 18.1 | 117.4 | 5.5 | 228.7 | 3.7 | 855.7 | 821.3 | 200.3 | 827.1 | 739.4 | 867.4 | 704.7 | 639.9 | 663.5 | 622.1 | 677.6 | 717.4 | 117.5 | 241.8 | 307.1 | 609.1 | 576.1 | 544 | 522.4 | 585.2 | 236.5 | 414.3 | 390.5 | 294.3 | 323 | 447.2 | 310.2
1075 | 839 | 566.6 | 226.64 | 264.9291 | 511.4 | 372.7 | 368.4 | 335 | 554.2 | 64.2 | 18.1 | 117.6 | 5.5 | 218.3 | 3.6 | 854.1 | 820.6 | 200.9 | 827.3 | 739.8 | 869.3 | 705.4 | 640.4 | 665.9 | 622 | 678.2 | 717.9 | 117.7 | 242.1 | 307.3 | 609.9 | 576.6 | 543.3 | 523 | 584.4 | 236.9 | 413.4 | 390.2 | 294.6 | 323.1 | 447.5 | 310.5
1076 | 840 | 566.6 | 226.64 | 264.9291 | 506.1 | 372.5 | 366.8 | 334.4 | 555.6 | 64.3 | 18.1 | 117.8 | 6 | 193.9 | 3.6 | 856.9 | 821.2 | 200.2 | 827.2 | 740.1 | 870 | 704.5 | 639.8 | 661 | 622.2 | 679.2 | 718.2 | 118 | 242.4 | 307.5 | 610.5 | 577.1 | 546.9 | 523.5 | 584.2 | 237.4 | 413 | 390.3 | 294.9 | 323.3 | 447.8 | 310.8
1077 | 841 | 566.4 | 226.56 | 264.8356 | 499.5 | 372 | 365.5 | 334 | 554.2 | 64.3 | 18.1 | 117.9 | 6.1 | 205.6 | 3.8 | 861.4 | 824.1 | 197.4 | 826.9 | 740 | 870.6 | 704.4 | 641 | 661.4 | 622.8 | 680.1 | 717.3 | 118.2 | 242.7 | 307.8 | 610.7 | 577.8 | 548.5 | 524.1 | 586.7 | 237.8 | 413.1 | 390.4 | 295.3 | 323.6 | 448.1 | 311.1
1078 | 842 | 565.2 | 226.08 | 264.2745 | 494.3 | 371.9 | 364.2 | 334.2 | 554.2 | 64.4 | 18.1 | 118 | 5.4 | 228.3 | 3.8 | 861.2 | 822.6 | 198.5 | 826.3 | 740 | 871.6 | 707 | 642.2 | 668.9 | 622.6 | 680.8 | 717.3 | 118.4 | 243 | 308 | 611.8 | 577.8 | 553.8 | 524.7 | 586.2 | 238.2 | 413.2 | 390.3 | 295.6 | 323.7 | 448.5 | 311.5
1079 | 843 | 565 | 226 | 264.181 | 495.4 | 371.7 | 364 | 334.5 | 554.7 | 64.4 | 18.1 | 118 | 5.9 | 234.6 | 3.9 | 861.3 | 828 | 199.3 | 826.6 | 740.5 | 872.6 | 709.5 | 643.4 | 677.1 | 622.8 | 681.7 | 718.4 | 118.6 | 243.3 | 308.1 | 613.2 | 577.8 | 555.8 | 525.6 | 585.2 | 238.6 | 413.7 | 390.8 | 296 | 324.1 | 448.8 | 311.8
1080 | 844 | 565.6 | 226.24 | 264.4615 | 494.4 | 371.4 | 363.8 | 334.3 | 557.5 | 64.5 | 18.1 | 118.1 | 5.7 | 232.7 | 4.1 | 865.4 | 835.2 | 198.9 | 827.7 | 741 | 873.5 | 711.3 | 644.6 | 682.5 | 623.1 | 682.4 | 719.7 | 118.9 | 243.6 | 308.3 | 614.2 | 579.1 | 557.9 | 527 | 584.4 | 239.1 | 414.1 | 390.8 | 296.4 | 324.3 | 449.1 | 312.2
1081 | 845 | 565.2 | 226.08 | 264.2745 | 492.8 | 371.5 | 363.1 | 334.1 | 560.1 | 64.6 | 18.1 | 118.2 | 5.6 | 226.7 | 4.1 | 864.9 | 840.3 | 198.8 | 827.6 | 741.4 | 874.1 | 714.5 | 646.2 | 688.4 | 623.8 | 683.3 | 720.9 | 119.1 | 243.8 | 308.6 | 615.4 | 579.8 | 561.7 | 527.6 | 584.8 | 239.5 | 413.8 | 390.5 | 296.7 | 324.3 | 449.5 | 312.5
1082 | 846 | 564.7 | 225.88 | 264.0407 | 492.6 | 371.4 | 362.7 | 334.3 | 560.1 | 64.6 | 18.1 | 118.1 | 5.7 | 209.9 | 3.9 | 869.5 | 845.8 | 200 | 828.6 | 741.8 | 874.3 | 715.8 | 647.4 | 690.4 | 624.6 | 684.1 | 721.4 | 119.3 | 244.1 | 308.9 | 616.5 | 579.8 | 567 | 528.8 | 585.4 | 239.9 | 413.3 | 389.6 | 297 | 324.5 | 449.8 | 312.8
1083 | 847 | 565.1 | 226.04 | 264.2277 | 494.8 | 371.5 | 362.9 | 334.1 | 561.4 | 64.6 | 18.1 | 118.1 | 6.1 | 210.4 | 3.5 | 865.8 | 845.6 | 200.9 | 830 | 742.2 | 874.4 | 715.4 | 648.5 | 689.9 | 625.1 | 684.8 | 722.5 | 119.5 | 244.4 | 309 | 616.8 | 580.5 | 567.7 | 530.3 | 585.9 | 240.4 | 413 | 389.1 | 297.4 | 324.6 | 450.1 | 313.2
1084 | 848 | 565 | 226 | 264.181 | 498.2 | 371.1 | 363.4 | 334.2 | 561 | 64.6 | 18.1 | 118.1 | 6.2 | 214.8 | 3.2 | 867.3 | 846.9 | 201.9 | 829.5 | 742.1 | 874.8 | 714.9 | 649 | 687.8 | 625 | 685.4 | 721.7 | 119.8 | 244.7 | 309.2 | 617.8 | 580.5 | 568.6 | 531.2 | 586 | 240.8 | 412.6 | 388.4 | 297.6 | 324.8 | 450.4 | 313.5
1085 | 849 | 565 | 226 | 264.181 | 500.5 | 369.9 | 363.4 | 334 | 560.3 | 64.6 | 18.1 | 118 | 5.9 | 229.4 | 3.1 | 868.7 | 840.3 | 201.1 | 830.3 | 741.9 | 875.8 | 714.9 | 649.3 | 688.2 | 624.7 | 685.8 | 722.7 | 120 | 245 | 309.4 | 618 | 580.4 | 567.7 | 532.3 | 585.5 | 241.2 | 412.3 | 387.8 | 297.9 | 324.9 | 450.8 | 313.8
1086 | 850 | 565 | 226 | 264.181 | 499.5 | 369.2 | 363.1 | 333.7 | 560.3 | 64.6 | 18.1 | 118 | 5.8 | 248.4 | 3.3 | 869.9 | 844.5 | 202.2 | 830.9 | 742.7 | 876.8 | 717.3 | 652.2 | 700 | 625.2 | 686.1 | 723.5 | 120.2 | 245.2 | 309.6 | 618.5 | 580.3 | 569.2 | 533.7 | 584.8 | 241.7 | 412.2 | 387.2 | 298.3 | 325.1 | 451.1 | 314.1
1087 | 851 | 565.6 | 226.24 | 264.4615 | 497 | 369.6 | 362.9 | 334.4 | 562.3 | 64.7 | 18.1 | 117.9 | 5.6 | 247.5 | 3.7 | 875.8 | 843.6 | 203.5 | 830.7 | 742.8 | 877.9 | 717.3 | 653.2 | 696.6 | 625.6 | 686.4 | 724.8 | 120.4 | 245.4 | 309.9 | 619.1 | 581.1 | 569 | 535.1 | 585.4 | 242.1 | 412.4 | 387.1 | 298.6 | 325.4 | 451.4 | 314.4
1088 | 852 | 565.7 | 226.28 | 264.5083 | 494.4 | 370.3 | 362.9 | 335.5 | 561.7 | 64.7 | 18.1 | 117.8 | 5.8 | 243.7 | 4.2 | 874.6 | 839.1 | 203.6 | 830.9 | 742.9 | 878.2 | 715.3 | 651.8 | 691.4 | 625.4 | 687.1 | 724.4 | 120.7 | 245.6 | 310.2 | 619.6 | 581.2 | 564.6 | 536.4 | 585 | 242.4 | 412.7 | 386.5 | 299 | 325.6 | 451.7 | 314.8
1089 | 853 | 566.8 | 226.72 | 265.0226 | 494.2 | 370.3 | 362.9 | 335.8 | 561.6 | 64.7 | 18.1 | 117.8 | 5.4 | 239.4 | 4.4 | 866.2 | 833.8 | 204.1 | 830.8 | 742.7 | 878.2 | 714.9 | 652 | 691.5 | 625.2 | 687.6 | 724.6 | 120.9 | 245.8 | 310.4 | 619.6 | 581.2 | 563.7 | 537.4 | 584.6 | 242.8 | 412.9 | 386.5 | 299.4 | 325.8 | 452 | 315.1
1090 | 854 | 565.4 | 226.16 | 264.368 | 492.4 | 370.3 | 363.1 | 336 | 559.6 | 64.7 | 18.1 | 117.8 | 5.4 | 234.3 | 4.2 | 860.4 | 829.6 | 203.7 | 829.7 | 742.2 | 877.4 | 714.5 | 652 | 689.3 | 625.2 | 688 | 724.9 | 121.1 | 246 | 310.6 | 619.6 | 581.3 | 561.3 | 538.7 | 583.9 | 243.2 | 413.4 | 386.5 | 299.8 | 326.1 | 452.3 | 315.5
1091 | 855 | 565.8 | 226.32 | 264.555 | 489.5 | 370.1 | 363.4 | 337.1 | 559 | 64.7 | 18.1 | 117.8 | 5.5 | 223.3 | 3.8 | 842.4 | 819.7 | 201.8 | 828.8 | 741.6 | 875.6 | 713.5 | 651.9 | 685.1 | 625.1 | 688.7 | 723.4 | 121.3 | 246.2 | 310.7 | 619.3 | 582 | 557.9 | 539.8 | 583.6 | 243.6 | 414.5 | 387.3 | 300.1 | 326.5 | 452.6 | 315.9
1092 | 856 | 566.2 | 226.48 | 264.7421 | 491.8 | 369.5 | 364 | 338.3 | 557.5 | 64.7 | 18.1 | 117.9 | 5.2 | 219.6 | 3.8 | 836.4 | 815.7 | 200.5 | 827.8 | 740.8 | 874.2 | 711.6 | 649.3 | 675.8 | 624.5 | 689.7 | 722.7 | 121.5 | 246.5 | 310.9 | 619.4 | 582.6 | 553.6 | 540.7 | 582.9 | 243.9 | 415 | 388.6 | 300.5 | 326.6 | 452.9 | 316.3
1093 | 857 | 564.4 | 225.76 | 263.9004 | 494.2 | 369.1 | 364.9 | 338.9 | 553.3 | 64.6 | 18.1 | 118.1 | 5.3 | 207.4 | 4.7 | 846.5 | 816.3 | 201.8 | 827.1 | 740.5 | 873 | 709.2 | 646.4 | 669.9 | 624.4 | 690.3 | 721.3 | 121.7 | 246.7 | 311.2 | 618.7 | 583 | 553.2 | 541.7 | 583.9 | 244.3 | 415.4 | 389.9 | 301 | 326.9 | 453.2 | 316.6
1094 | 858 | 564.7 | 225.88 | 264.0407 | 492 | 369 | 364.9 | 339 | 552.4 | 64.7 | 18.1 | 118.2 | 5.3 | 198.5 | 5.3 | 849.5 | 807.4 | 200 | 825.9 | 740.5 | 873.2 | 707.9 | 645 | 665.5 | 624.4 | 690.9 | 720.6 | 121.8 | 247 | 311.3 | 618.8 | 584.7 | 551.2 | 542.4 | 584.8 | 244.6 | 415.7 | 389.7 | 301.4 | 327.1 | 453.5 | 317
1095 | 859 | 563.7 | 225.48 | 263.5731 | 489.8 | 368.7 | 365.4 | 338.9 | 552.3 | 64.7 | 18.1 | 118.2 | 5.6 | 216.5 | 4.4 | 843.1 | 805.3 | 199.3 | 825.2 | 739.9 | 873.3 | 707.5 | 643.7 | 662.8 | 623.6 | 691.4 | 720.7 | 122 | 247.3 | 311.5 | 619.3 | 585.4 | 548.3 | 543 | 583.5 | 244.8 | 415.5 | 390.1 | 301.8 | 327.3 | 453.9 | 317.3
1096 | 860 | 563.6 | 225.44 | 263.5264 | 485 | 368.4 | 365.6 | 338.4 | 550.1 | 64.8 | 18.1 | 118.2 | 5.6 | 235.3 | 4 | 847.2 | 809.9 | 199.8 | 825.3 | 740.1 | 873.3 | 707.5 | 642.8 | 663.3 | 622.9 | 692.2 | 720.5 | 122.2 | 247.6 | 311.7 | 619.7 | 584.4 | 546.4 | 543.2 | 582.4 | 245 | 415 | 390.4 | 302.1 | 327.5 | 454.2 | 317.7
1097 | 861 | 565.6 | 226.24 | 264.4615 | 489.8 | 368.3 | 366.8 | 337.6 | 550.2 | 64.9 | 18.1 | 118.2 | 5.2 | 239.6 | 3.9 | 852.9 | 817.2 | 199.8 | 825.4 | 740.7 | 872.9 | 708.7 | 645 | 673.2 | 623.1 | 692.8 | 721.9 | 122.4 | 247.8 | 312 | 620.4 | 584.4 | 545.8 | 543.7 | 583.6 | 245.2 | 414.9 | 390.8 | 302.5 | 327.8 | 454.5 | 318
1098 | 862 | 565 | 226 | 264.181 | 507.4 | 368.9 | 366.9 | 337.4 | 548.8 | 65.1 | 18.1 | 118.2 | 4.7 | 224.7 | 3.8 | 855.8 | 819.7 | 199 | 825.6 | 741.1 | 873.3 | 711.6 | 648.2 | 684.5 | 623.2 | 693 | 723.6 | 122.6 | 248.1 | 312.1 | 621.5 | 583.9 | 546.1 | 544.1 | 584.2 | 245.6 | 415 | 390.8 | 302.8 | 328.1 | 454.8 | 318.3
1099 | 863 | 564.8 | 225.92 | 264.0875 | 519.1 | 369.8 | 366.8 | 337.1 | 548.6 | 65.3 | 18.1 | 118.1 | 5.2 | 220.9 | 3.7 | 859.2 | 823.6 | 198.8 | 826 | 741.6 | 874 | 713.6 | 650.3 | 686 | 623.4 | 693.5 | 724.3 | 122.7 | 248.4 | 312.3 | 622.3 | 582.8 | 548.4 | 544.5 | 585.2 | 246 | 415.1 | 390.7 | 303.2 | 328.3 | 455.1 | 318.6
1100 | 864 | 563.9 | 225.56 | 263.6666 | 514.9 | 371.2 | 367.2 | 337.2 | 549.2 | 65.4 | 18.1 | 118.1 | 5.9 | 232.3 | 3.2 | 864.1 | 827.2 | 199.7 | 826 | 742 | 875 | 715.1 | 651.9 | 687.3 | 623.4 | 694.2 | 725.1 | 122.9 | 248.8 | 312.5 | 622.7 | 582.2 | 549.5 | 544.9 | 585.6 | 246.4 | 414.8 | 390.5 | 303.6 | 328.5 | 455.4 | 319
1101 | 865 | 564.3 | 225.72 | 263.8537 | 514 | 371.8 | 366.8 | 337.5 | 553.2 | 65.5 | 18 | 118.1 | 5.6 | 261.2 | 3.1 | 856.8 | 823.7 | 201.7 | 826.7 | 742.3 | 874.7 | 716.5 | 653.7 | 688.2 | 623.8 | 694.9 | 726 | 123.1 | 249.1 | 312.7 | 622.7 | 582.6 | 552.2 | 545.3 | 586.1 | 246.8 | 414.8 | 390.4 | 303.9 | 328.8 | 455.7 | 319.3
1102 | 866 | 566.5 | 226.6 | 264.8823 | 511.3 | 371.1 | 366.1 | 338.1 | 555.8 | 65.5 | 18 | 118.1 | 5.5 | 254.6 | 3 | 855.7 | 827.7 | 202.3 | 827.4 | 742.2 | 874.8 | 716 | 652.1 | 687.3 | 623 | 695.7 | 725.1 | 123.2 | 249.3 | 312.9 | 623.5 | 582.3 | 552.3 | 545.6 | 584.4 | 247.3 | 414.6 | 389.9 | 304.3 | 328.9 | 456 | 319.6
1103 | 867 | 566.6 | 226.64 | 264.9291 | 509.5 | 370.5 | 366.3 | 337.9 | 551.8 | 65.5 | 18 | 118 | 5.5 | 241 | 2.9 | 857 | 832.3 | 203.3 | 828.4 | 742.8 | 875 | 717.7 | 653.6 | 695.3 | 622.6 | 696.2 | 726.2 | 123.4 | 249.6 | 313 | 624.2 | 580.7 | 552.7 | 545.9 | 583.3 | 247.9 | 414.6 | 389.8 | 304.7 | 329 | 456.3 | 319.9
1104 | 868 | 566.6 | 226.64 | 264.9291 | 506.2 | 371.5 | 366.3 | 337.8 | 550.4 | 65.5 | 18 | 117.9 | 5.7 | 236.9 | 2.6 | 863.3 | 829.8 | 204.6 | 828.7 | 742.5 | 875.1 | 718 | 654.6 | 691.6 | 622.3 | 696.6 | 728.3 | 123.5 | 249.9 | 313.1 | 624 | 580.4 | 551.6 | 546.7 | 584.3 | 248.5 | 414.8 | 389.2 | 305 | 329.1 | 456.6 | 320.2
1105 | 869 | 564.8 | 225.92 | 264.0875 | 502.4 | 372.7 | 366 | 338.5 | 547.6 | 65.5 | 18 | 117.9 | 5.8 | 221.3 | 2.7 | 867 | 828.7 | 206.2 | 828.8 | 742 | 876 | 716.4 | 652.8 | 684.6 | 621.4 | 696.8 | 726.9 | 123.6 | 250.2 | 313.2 | 624.7 | 579.5 | 548.8 | 547.2 | 582.8 | 249.1 | 414.5 | 388.6 | 305.4 | 329.3 | 456.9 | 320.5
1106 | 870 | 564.7 | 225.88 | 264.0407 | 498.7 | 372.4 | 365.4 | 339.6 | 549.1 | 65.5 | 18 | 117.9 | 6.4 | 206.4 | 3.2 | 866.8 | 830.1 | 204.7 | 829.4 | 741.9 | 876.3 | 715.8 | 652.2 | 684.9 | 621.1 | 697.1 | 726.9 | 123.8 | 250.5 | 313.4 | 625.3 | 579.5 | 549.9 | 547.4 | 583.1 | 249.7 | 414.3 | 388.1 | 305.7 | 329.5 | 457.1 | 320.8
1107 | 871 | 564.6 | 225.84 | 263.9939 | 497.4 | 372 | 364.9 | 340.1 | 553.2 | 65.6 | 18 | 118 | 6.6 | 205.3 | 3.7 | 864.9 | 830 | 203.9 | 829.8 | 741.7 | 875.9 | 715.7 | 653.2 | 685.7 | 621.9 | 697.6 | 726.5 | 123.9 | 250.8 | 313.6 | 625.9 | 579.9 | 552.8 | 547.8 | 583.9 | 250.4 | 414.5 | 387.7 | 306.1 | 329.7 | 457.4 | 321.1
1108 | 872 | 564.8 | 225.92 | 264.0875 | 496.1 | 371.5 | 364.4 | 340.4 | 554.6 | 65.6 | 18 | 118 | 6.2 | 209 | 4.2 | 860.7 | 834.4 | 204.1 | 830.3 | 741.2 | 876.1 | 716.3 | 654.2 | 690.6 | 622.2 | 698.2 | 727.1 | 124 | 251.1 | 313.8 | 627 | 579.7 | 556.1 | 548 | 584 | 251.1 | 414.9 | 387.8 | 306.4 | 329.8 | 457.7 | 321.4
1109 | 873 | 564.4 | 225.76 | 263.9004 | 493.1 | 371.6 | 364 | 341 | 551.2 | 65.6 | 18 | 118 | 6.4 | 203.8 | 4.6 | 859.9 | 832.9 | 205.6 | 830.2 | 741.2 | 875.5 | 715.2 | 654.4 | 684.1 | 622.4 | 698.9 | 727.6 | 124.1 | 251.3 | 314 | 627.8 | 578.9 | 552.7 | 548.3 | 584.4 | 251.8 | 415.4 | 388.7 | 306.8 | 330.2 | 458 | 321.8
1110 | 874 | 566.5 | 226.6 | 264.8823 | 491.3 | 371.6 | 364.1 | 342.2 | 549.1 | 65.5 | 18 | 117.9 | 5.5 | 203.7 | 4.9 | 851.2 | 828.8 | 206.4 | 829.9 | 740.2 | 873.4 | 711.9 | 651.3 | 675.7 | 621.9 | 699.5 | 724.5 | 124.2 | 251.6 | 314.3 | 628.1 | 578.4 | 547.3 | 548.4 | 583.9 | 252.4 | 416.7 | 389.2 | 307.3 | 330.6 | 458.3 | 322.1
1111 | 875 | 567.9 | 227.16 | 265.537 | 489.4 | 371.1 | 364.5 | 345.1 | 550.8 | 65.4 | 18 | 117.9 | 5.3 | 210.3 | 5.6 | 857.6 | 832.7 | 205.7 | 830.1 | 739.7 | 873.1 | 710.5 | 649.2 | 673.2 | 621.4 | 699.9 | 722.3 | 124.3 | 251.8 | 314.4 | 629 | 578.5 | 546.8 | 548.7 | 582.8 | 253.1 | 417.7 | 389.1 | 307.7 | 330.8 | 458.6 | 322.5
1112 | 876 | 568.4 | 227.36 | 265.7707 | 487.8 | 370.7 | 364.7 | 346 | 552.1 | 65.4 | 18 | 117.9 | 5.4 | 210.5 | 5.6 | 863.4 | 837.8 | 203.8 | 830.5 | 740 | 874 | 712.9 | 650.4 | 682.8 | 621.6 | 700.1 | 724 | 124.4 | 252 | 314.6 | 630 | 578.2 | 551.3 | 548.9 | 582.5 | 253.8 | 417.9 | 389.2 | 308.2 | 331 | 458.9 | 322.9
1113 | 877 | 566.4 | 226.56 | 264.8356 | 486.1 | 370.9 | 364.6 | 345.1 | 552.2 | 65.4 | 18 | 118 | 5.1 | 215 | 5.4 | 856.6 | 832.2 | 203.1 | 830.6 | 739.7 | 874.6 | 714.1 | 650.1 | 683.6 | 621.8 | 700.4 | 724.4 | 124.5 | 252.3 | 314.8 | 630.7 | 577.8 | 551.9 | 549.2 | 582.5 | 254.5 | 418 | 389.8 | 308.6 | 331.2 | 459.2 | 323.2
1114 | 878 | 565.8 | 226.32 | 264.555 | 486.2 | 371.7 | 364.4 | 344.7 | 548.7 | 65.4 | 18 | 118 | 5.7 | 220.7 | 5.2 | 836.9 | 819.9 | 203.7 | 829.9 | 739 | 873.4 | 711.9 | 647.5 | 674.1 | 621.4 | 700.9 | 723.3 | 124.6 | 252.6 | 315 | 631 | 577.2 | 550.6 | 549.3 | 582.2 | 255.1 | 418.6 | 391.6 | 309 | 331.7 | 459.4 | 323.5
1115 | 879 | 566.2 | 226.48 | 264.7421 | 488.3 | 371.9 | 364.3 | 345.4 | 550.7 | 65.3 | 18 | 118 | 6.1 | 233 | 4.8 | 824.2 | 807.4 | 203.2 | 828.7 | 737.8 | 870.6 | 709.3 | 645.1 | 666.1 | 621 | 701.5 | 722 | 124.7 | 252.9 | 315.3 | 630.8 | 577.3 | 549.6 | 549.6 | 581.7 | 255.7 | 419.4 | 393.2 | 309.5 | 332.2 | 459.7 | 323.8
1116 | 880 | 566.3 | 226.52 | 264.7888 | 488.4 | 371.8 | 365.7 | 348.3 | 550.9 | 65.2 | 18 | 118 | 5.5 | 237.3 | 4.1 | 815.3 | 801.1 | 202.6 | 827.7 | 736.7 | 868.5 | 706.6 | 641.9 | 656.6 | 620.3 | 702.2 | 720.1 | 124.7 | 253.1 | 315.5 | 630.3 | 577.2 | 546.8 | 549.8 | 580.8 | 256.3 | 420.2 | 394 | 310 | 332.5 | 460 | 324.1
1117 | 881 | 566 | 226.4 | 264.6486 | 490.7 | 371.1 | 367.9 | 350.3 | 547.2 | 65.2 | 18 | 118.1 | 5.4 | 240.4 | 3.5 | 815.2 | 801.1 | 201.5 | 827 | 736.4 | 867.8 | 704.6 | 638.9 | 654.3 | 619.7 | 702.6 | 719.1 | 124.8 | 253.3 | 315.6 | 629.7 | 576.1 | 542.9 | 549.9 | 580 | 256.8 | 420.6 | 394.5 | 310.4 | 332.8 | 460.2 | 324.4
1118 | 882 | 565.1 | 226.04 | 264.2277 | 491.3 | 370.2 | 369.4 | 350.7 | 547.3 | 65.2 | 18 | 118 | 5.6 | 250.3 | 3.2 | 816.1 | 802.3 | 202.7 | 826.7 | 735.8 | 868 | 704.9 | 636.9 | 655.4 | 619.3 | 703 | 719 | 124.8 | 253.5 | 315.8 | 629.6 | 575 | 540.1 | 549.8 | 578.8 | 257.3 | 419.9 | 394.3 | 310.9 | 332.9 | 460.5 | 324.7
1119 | 883 | 564.6 | 225.84 | 263.9939 | 489.2 | 368.6 | 370.2 | 349.9 | 547.9 | 65.1 | 18 | 118.1 | 5.6 | 252.4 | 2.9 | 822.8 | 810.1 | 203 | 826.9 | 736.2 | 868.1 | 706.4 | 635.3 | 660.8 | 618.5 | 703.4 | 720.9 | 124.9 | 253.7 | 315.9 | 629.8 | 574.2 | 541.5 | 549.6 | 578.1 | 257.8 | 419.3 | 394.4 | 311.3 | 333.2 | 460.8 | 324.9
1120 | 884 | 565.8 | 226.32 | 264.555 | 489.7 | 367.5 | 370.6 | 348 | 548.9 | 65.1 | 18 | 118.2 | 5.6 | 237.7 | 2.6 | 822.5 | 813.8 | 203 | 827.6 | 736.8 | 868.4 | 708.6 | 635.7 | 672 | 618.5 | 703.8 | 721 | 124.9 | 254 | 316.2 | 630.6 | 573.7 | 548 | 549.9 | 578.7 | 258.3 | 418.7 | 394.3 | 311.7 | 333.3 | 461 | 325
1121 | 885 | 567.5 | 227 | 265.3499 | 493.6 | 366.9 | 370.2 | 347.1 | 550.3 | 65.1 | 18 | 118.2 | 5.5 | 209.8 | 2.5 | 832.9 | 815 | 203.4 | 827.8 | 737.2 | 868.9 | 712.4 | 638.8 | 682.8 | 619.5 | 704.3 | 722.4 | 124.9 | 254.3 | 316.5 | 630.4 | 573.1 | 552.1 | 549.9 | 579.4 | 258.7 | 418.1 | 394.3 | 312 | 333.3 | 461.3 | 325.2
1122 | 886 | 568.7 | 227.48 | 265.911 | 495.1 | 367.9 | 370.4 | 346.4 | 554.3 | 65 | 18 | 118.1 | 5.7 | 192.4 | 2.5 | 847.6 | 818.4 | 204.4 | 827.9 | 737.6 | 869.6 | 716.1 | 642 | 689.4 | 620.7 | 704.9 | 723.8 | 124.8 | 254.5 | 316.8 | 630.8 | 573.1 | 562.9 | 550 | 581.1 | 259.2 | 417.2 | 393.7 | 312.3 | 333.3 | 461.5 | 325.4
1123 | 887 | 566.5 | 226.6 | 264.8823 | 492.7 | 370.5 | 370.5 | 345.6 | 559.1 | 65 | 18 | 118 | 6.1 | 198.4 | 2.2 | 854.1 | 825.4 | 205.8 | 828.3 | 737.9 | 870.2 | 718.1 | 644.6 | 692.8 | 621.2 | 705.5 | 725.6 | 124.8 | 254.8 | 317.1 | 631.1 | 573.8 | 566 | 550.1 | 581.9 | 259.7 | 417.4 | 393.4 | 312.6 | 333.4 | 461.7 | 325.6
1124 | 888 | 564.4 | 225.76 | 263.9004 | 493.1 | 373.1 | 370.6 | 345.4 | 559 | 65 | 18 | 118 | 5.7 | 229.2 | 2.2 | 855.9 | 826.7 | 204.8 | 829.9 | 737.8 | 870 | 718 | 646.1 | 693.8 | 621.5 | 706 | 725.8 | 124.5 | 255 | 317.1 | 632 | 574.5 | 566.3 | 550.4 | 582.8 | 260.3 | 417.7 | 393.4 | 313 | 333.7 | 462 | 325.9
1125 | 889 | 562.3 | 224.92 | 262.9185 | 491.9 | 375.1 | 369.8 | 345.8 | 557.2 | 65 | 18 | 118 | 5.3 | 244.2 | 2.2 | 851.3 | 822.9 | 203.7 | 830.3 | 737.8 | 869.7 | 717.7 | 647.5 | 691.1 | 622.1 | 706.1 | 727 | 124.4 | 255.3 | 317.3 | 632.7 | 575.1 | 564.8 | 550.8 | 584.2 | 260.8 | 418.3 | 393.3 | 313.4 | 333.9 | 462.3 | 326.2
1126 | 890 | 562 | 224.8 | 262.7782 | 487.1 | 374.7 | 368.5 | 346 | 555.7 | 65 | 18 | 118.1 | 5.5 | 233.3 | 2 | 856.5 | 828.5 | 203.6 | 829.8 | 738.1 | 869.9 | 717.2 | 647.4 | 693 | 621.5 | 706.5 | 726 | 124.3 | 255.6 | 317.5 | 633.3 | 574.8 | 563.8 | 551.1 | 583.2 | 261.3 | 418.2 | 392.7 | 313.8 | 334 | 462.6 | 326.6
1127 | 891 | 564.3 | 225.72 | 263.8537 | 487.5 | 374.4 | 367.7 | 346.2 | 553.9 | 64.9 | 17.9 | 118.1 | 5.7 | 213 | 2.1 | 861.1 | 836 | 203.1 | 829.6 | 738.3 | 870.3 | 718.2 | 648.9 | 696.3 | 621.9 | 706.9 | 727 | 124.3 | 255.8 | 317.7 | 633.7 | 574.5 | 564.8 | 551.8 | 582.9 | 261.8 | 418.1 | 392.2 | 314.2 | 334.2 | 462.9 | 326.9
1128 | 892 | 564.5 | 225.8 | 263.9472 | 495.9 | 374.4 | 367.4 | 345.6 | 555.1 | 64.9 | 18 | 118 | 5.6 | 201.7 | 2.4 | 866.5 | 839.3 | 203.7 | 829.3 | 738.4 | 870.3 | 718.3 | 650.3 | 695.7 | 622.3 | 707.1 | 727.7 | 124.3 | 256 | 317.9 | 634.3 | 575.1 | 565.6 | 552.3 | 583.9 | 262.2 | 417.9 | 392 | 314.6 | 334.4 | 463.1 | 327.2
1129 | 893 | 565 | 226 | 264.181 | 498.6 | 375.2 | 366.6 | 346.6 | 553.5 | 65 | 18 | 117.9 | 5.2 | 204.9 | 3.1 | 861.5 | 835.1 | 204.2 | 829.9 | 737.9 | 869.1 | 715.4 | 650 | 685.3 | 622.8 | 707.6 | 726.7 | 124.3 | 256.1 | 318.1 | 634.8 | 575.7 | 564.5 | 552.6 | 586.2 | 262.6 | 418.2 | 392.4 | 315 | 334.8 | 463.4 | 327.5
1130 | 894 | 566.6 | 226.64 | 264.9291 | 496.6 | 375.3 | 365.5 | 348.2 | 550.7 | 65.1 | 17.9 | 117.9 | 4.6 | 211.4 | 3.5 | 862.7 | 837 | 203.7 | 829.5 | 737.7 | 867.8 | 712.9 | 648.2 | 679.8 | 622.4 | 708.1 | 725.2 | 124.3 | 256.1 | 318.3 | 634.6 | 575.7 | 560 | 552.9 | 585.4 | 263 | 419.3 | 392.1 | 315.5 | 335.1 | 463.7 | 327.8
1131 | 895 | 567.1 | 226.84 | 265.1629 | 492 | 375.2 | 365.6 | 348.8 | 546 | 65.1 | 17.9 | 117.9 | 5.7 | 196.8 | 4.1 | 867.6 | 841.5 | 203.4 | 829 | 737.5 | 868.8 | 712.7 | 645.2 | 680.5 | 621.6 | 708.6 | 724.2 | 124.4 | 256.3 | 318.4 | 634.4 | 574.2 | 561.2 | 553.1 | 583.9 | 263.5 | 419.9 | 392.2 | 316 | 335.2 | 464 | 328.2
1132 | 896 | 566.7 | 226.68 | 264.9759 | 489.3 | 375.7 | 365.8 | 349.1 | 547.3 | 65.2 | 17.9 | 118 | 6 | 193.6 | 5.5 | 873 | 841 | 202.7 | 829.1 | 737.3 | 869.9 | 713.1 | 645.1 | 685.6 | 621.9 | 709.2 | 724.9 | 124.6 | 256.5 | 318.6 | 635.2 | 574.5 | 562.2 | 553.6 | 583.4 | 263.9 | 419.8 | 393.2 | 316.4 | 335.6 | 464.3 | 328.6
1133 | 897 | 565.3 | 226.12 | 264.3213 | 488.9 | 376.2 | 365.5 | 348.9 | 547 | 65.3 | 17.9 | 118.1 | 6 | 190 | 6.3 | 872.5 | 840.4 | 202.8 | 829.5 | 737.1 | 870.3 | 712.5 | 645.9 | 682.3 | 622 | 709.5 | 724.7 | 124.7 | 256.7 | 318.7 | 635.7 | 574.5 | 560.8 | 553.7 | 583.6 | 264.3 | 419.9 | 393.6 | 316.9 | 335.8 | 464.5 | 328.9
1134 | 898 | 565.1 | 226.04 | 264.2277 | 489.2 | 376.6 | 365.1 | 348.8 | 544.6 | 65.3 | 17.9 | 118.2 | 5.6 | 200.6 | 6 | 868.7 | 834.8 | 202.1 | 828.6 | 736.8 | 870.9 | 712 | 647.1 | 678.4 | 621.8 | 709.5 | 723.9 | 124.9 | 257 | 318.9 | 636.1 | 574 | 559.6 | 553.9 | 584 | 264.7 | 420.3 | 393.5 | 317.3 | 336 | 464.8 | 329.2
1135 | 899 | 565.5 | 226.2 | 264.4148 | 489.9 | 375.9 | 364.9 | 349 | 543.4 | 65.4 | 17.9 | 118.2 | 5.4 | 213.3 | 5.9 | 864.6 | 835.9 | 201.3 | 828.1 | 736.3 | 871.4 | 712.3 | 647.5 | 679.1 | 621.4 | 709.4 | 723.2 | 125.1 | 257.3 | 319.1 | 636.6 | 573.7 | 556.5 | 554 | 583.5 | 265.1 | 419.7 | 393.1 | 317.7 | 336.2 | 465 | 329.6
1136 | 900 | 565 | 226 | 264.181 | 489.2 | 375 | 365 | 349.3 | 543.8 | 65.6 | 17.9 | 118.2 | 5.9 | 207.2 | 6.4 | 871.1 | 842.1 | 200.9 | 827.9 | 736.5 | 871.5 | 712.8 | 647.3 | 684.9 | 621.1 | 709.1 | 723.3 | 125.3 | 257.5 | 319.3 | 637.9 | 573.1 | 556.7 | 554 | 582.6 | 265.5 | 418.6 | 392.7 | 318 | 336.4 | 465.3 | 329.9
1137 | 901 | 563.3 | 225.32 | 263.3861 | 485 | 374.3 | 364.7 | 348.5 | 544 | 65.8 | 17.9 | 118.3 | 5.9 | 202.1 | 6.4 | 874.8 | 846 | 201.8 | 828.1 | 736.4 | 871.6 | 712.9 | 646.8 | 682.6 | 621.4 | 709.1 | 723.1 | 125.5 | 257.7 | 319.5 | 639 | 572.6 | 558.8 | 554.2 | 583.1 | 265.9 | 417.5 | 392.6 | 318.3 | 336.6 | 465.5 | 330.1
1138 | 902 | 564.2 | 225.68 | 263.8069 | 483 | 374.3 | 364.6 | 347.7 | 547.4 | 65.9 | 17.9 | 118.5 | 6 | 213.5 | 6.8 | 874.3 | 841.4 | 201.7 | 827.7 | 736.4 | 871 | 710.2 | 645.5 | 673.7 | 621.6 | 709.3 | 721.8 | 125.7 | 258 | 319.6 | 639.1 | 573.3 | 558.2 | 554.3 | 584.2 | 266.4 | 417.5 | 393.5 | 318.7 | 336.8 | 465.8 | 330.4
1139 | 903 | 563.9 | 225.56 | 263.6666 | 482.1 | 374.6 | 364.7 | 347.3 | 546 | 66 | 17.9 | 118.5 | 6.1 | 211.6 | 7.2 | 857 | 825.8 | 201 | 827 | 736 | 868.9 | 706.8 | 642.7 | 662.5 | 621.3 | 709.3 | 719.6 | 125.9 | 258.3 | 319.9 | 638.7 | 574.1 | 555.2 | 554.4 | 585.1 | 267 | 418.4 | 395.8 | 319.2 | 337.4 | 466.1 | 330.7
1140 | 904 | 565.9 | 226.36 | 264.6018 | 479.4 | 374.9 | 364 | 348 | 545.8 | 66.1 | 17.9 | 118.6 | 5.3 | 207.4 | 7 | 838.7 | 817.6 | 201.1 | 826.5 | 735.7 | 866.6 | 704.7 | 638.6 | 655.9 | 620.1 | 709.4 | 718.3 | 126.1 | 258.6 | 320.2 | 638 | 574.4 | 553.1 | 554.7 | 584.5 | 267.4 | 419.4 | 398 | 319.7 | 338 | 466.4 | 331.1
1141 | 905 | 565.2 | 226.08 | 264.2745 | 477.7 | 374.1 | 364.7 | 350 | 547.3 | 66.2 | 17.9 | 118.7 | 5 | 209 | 6.9 | 837.1 | 820.1 | 201.6 | 826.2 | 735.3 | 865.8 | 704.8 | 637.3 | 659 | 619.2 | 709.9 | 719.1 | 126.3 | 258.8 | 320.3 | 637.7 | 574.3 | 552 | 554.7 | 584 | 267.9 | 420 | 398.6 | 320.1 | 338.2 | 466.7 | 331.5
1142 | 906 | 564.4 | 225.76 | 263.9004 | 477.2 | 373.8 | 366.4 | 350.3 | 548.3 | 66.3 | 17.9 | 118.8 | 5.9 | 217.5 | 6.4 | 835.3 | 821.7 | 201.9 | 826.7 | 735.4 | 866 | 704.9 | 637.3 | 659.5 | 619.6 | 710.5 | 718.8 | 126.5 | 259.1 | 320.4 | 637.8 | 574.3 | 557.2 | 555 | 585.8 | 268.3 | 420.9 | 399 | 320.6 | 338.4 | 467 | 331.8
1143 | 907 | 566 | 226.4 | 264.6486 | 477.6 | 375.5 | 366.8 | 349.4 | 547.8 | 66.4 | 17.9 | 118.9 | 6.1 | 222 | 5.8 | 843.5 | 825.6 | 202 | 827 | 735.7 | 866.3 | 704.5 | 638.1 | 657.3 | 619.9 | 711.1 | 718.6 | 126.7 | 259.4 | 320.5 | 637.7 | 574.1 | 560.4 | 555.2 | 587.5 | 268.7 | 421 | 399.8 | 321 | 338.7 | 467.3 | 332.1
1144 | 908 | 566.9 | 226.76 | 265.0694 | 479.5 | 375.9 | 366 | 349.6 | 545.6 | 66.4 | 17.9 | 118.9 | 4.9 | 212.5 | 5.2 | 849.4 | 833.7 | 202.6 | 827.8 | 736.1 | 866.2 | 704.3 | 638 | 663.4 | 619.7 | 711.3 | 717 | 126.9 | 259.7 | 320.7 | 637.5 | 573.8 | 558.7 | 555.5 | 586.4 | 269.2 | 420.6 | 400.3 | 321.4 | 338.9 | 467.6 | 332.4
1145 | 909 | 568.2 | 227.28 | 265.6772 | 479 | 376.6 | 365.3 | 349.6 | 543.6 | 66.4 | 17.9 | 118.8 | 5.1 | 196.5 | 5.2 | 856.2 | 841.8 | 202.9 | 828.3 | 736.2 | 866.6 | 705.8 | 638.8 | 670.5 | 619.7 | 711.3 | 716.5 | 127.2 | 260 | 320.9 | 638 | 572.8 | 562.4 | 555.6 | 586.1 | 269.6 | 419.8 | 400 | 321.8 | 339.1 | 467.9 | 332.7
1146 | 910 | 565.2 | 226.08 | 264.2745 | 478.9 | 377.2 | 365.5 | 348.1 | 543.6 | 66.4 | 17.9 | 119 | 5.6 | 207.3 | 5.1 | 861.4 | 848.9 | 202.5 | 828.6 | 736.6 | 866.7 | 708.5 | 642.1 | 683.4 | 620.4 | 711.4 | 717.7 | 127.4 | 260.2 | 321 | 638.3 | 572.4 | 565.3 | 555.7 | 586.8 | 269.9 | 419.2 | 400.2 | 322.1 | 339.3 | 468.2 | 333
1147 | 911 | 563.4 | 225.36 | 263.4329 | 478.3 | 377.1 | 365.3 | 347.5 | 544.4 | 66.4 | 17.9 | 119.1 | 5.5 | 212.2 | 5.7 | 860.3 | 847.9 | 202 | 828.6 | 736.8 | 865.8 | 708.6 | 643.5 | 683.2 | 620.8 | 711.7 | 717 | 127.6 | 260.5 | 321.3 | 638.4 | 572.7 | 563.5 | 556 | 587.8 | 270.3 | 419.2 | 400.9 | 322.5 | 339.6 | 468.4 | 333.3
1148 | 912 | 563.6 | 225.44 | 263.5264 | 478.8 | 377.5 | 364.3 | 348.1 | 543.8 | 66.3 | 17.9 | 119.2 | 5.2 | 196.2 | 5.9 | 861.1 | 851.4 | 201.8 | 829.1 | 737.3 | 865.4 | 710.1 | 645.2 | 691.4 | 620.7 | 712.1 | 716.2 | 127.8 | 260.8 | 321.5 | 639.4 | 572.8 | 566 | 556.1 | 588.2 | 270.7 | 418.9 | 401 | 322.9 | 339.8 | 468.7 | 333.6
1149 | 913 | 565.4 | 226.16 | 264.368 | 478.3 | 377.2 | 363.6 | 348.2 | 546.6 | 66.3 | 17.9 | 119.3 | 5.1 | 200.9 | 5.8 | 865.5 | 857.2 | 202.2 | 829.6 | 737.7 | 865.8 | 712.5 | 646.1 | 697.7 | 621.1 | 712.5 | 716.4 | 128.1 | 261 | 321.9 | 639.7 | 573.2 | 574.6 | 556.3 | 588.7 | 271 | 418.6 | 400.9 | 323.2 | 339.9 | 469 | 333.9
1150 | 914 | 565.5 | 226.2 | 264.4148 | 479 | 377.9 | 363.9 | 347.5 | 548.1 | 66.3 | 17.9 | 119.3 | 6 | 207.9 | 6 | 866 | 857.5 | 202.1 | 830.2 | 738.1 | 865.7 | 714.6 | 648.7 | 699.6 | 622.1 | 712.9 | 718.4 | 128.3 | 261.3 | 322 | 639.6 | 574.3 | 577.3 | 556.6 | 591 | 271.4 | 418.5 | 400.5 | 323.6 | 340.2 | 469.3 | 334.2
1151 | 915 | 565.9 | 226.36 | 264.6018 | 481.1 | 380 | 364.2 | 347 | 547.7 | 66.3 | 17.9 | 119.3 | 5.8 | 199.2 | 6.9 | 866.3 | 853.2 | 201.5 | 830.2 | 738.2 | 865.9 | 713.9 | 648.8 | 694.7 | 622.2 | 713.3 | 718.1 | 128.6 | 261.6 | 322.1 | 640 | 575.4 | 572.6 | 557.3 | 589.7 | 271.7 | 418.6 | 400.2 | 324 | 340.4 | 469.6 | 334.5
1152 | 916 | 565.7 | 226.28 | 264.5083 | 480.4 | 379.5 | 363.9 | 348.1 | 545.6 | 66.2 | 17.9 | 119.4 | 5.7 | 201.9 | 7.7 | 864.5 | 848.9 | 201.4 | 830.2 | 738 | 865.2 | 712.4 | 648.1 | 689.7 | 621.9 | 713.8 | 717 | 128.8 | 261.8 | 322.2 | 640.5 | 575.4 | 568.7 | 557.6 | 588 | 272.1 | 418.7 | 399.9 | 324.4 | 340.6 | 469.8 | 334.8
1153 | 917 | 565 | 226 | 264.181 | 478.8 | 378.8 | 364 | 349.7 | 544.5 | 66.2 | 17.9 | 119.5 | 5.7 | 201.1 | 7.6 | 868.5 | 849.3 | 200.6 | 830.5 | 738.2 | 865.9 | 712.5 | 647.9 | 694.3 | 621.7 | 714.3 | 716.8 | 129.1 | 262 | 322.4 | 641.6 | 574.8 | 566.7 | 557.8 | 587.2 | 272.5 | 418.6 | 399.4 | 324.7 | 340.8 | 470.1 | 335.2
1154 | 918 | 565.7 | 226.28 | 264.5083 | 477.6 | 377.9 | 363.5 | 350 | 542.6 | 66.3 | 17.9 | 119.5 | 5 | 204.5 | 7.2 | 867.7 | 841 | 199.9 | 830.2 | 738 | 867.5 | 712.8 | 648.2 | 690 | 621.3 | 714.7 | 717.2 | 129.3 | 262.1 | 322.5 | 642.2 | 573.9 | 565.4 | 558.1 | 586.9 | 272.9 | 418.2 | 399 | 325.1 | 341 | 470.3 | 335.5
1155 | 919 | 565 | 226 | 264.181 | 477.9 | 377.4 | 363 | 349.7 | 540.8 | 66.3 | 17.9 | 119.6 | 5.3 | 218.2 | 7 | 861.2 | 839.3 | 199.4 | 830.5 | 737.7 | 868.5 | 712.7 | 647.5 | 687 | 620.4 | 715 | 717.2 | 129.6 | 262.1 | 322.6 | 642.1 | 573.2 | 563.3 | 558.2 | 585.9 | 273.3 | 417.9 | 398.3 | 325.4 | 341.1 | 470.6 | 335.8
1156 | 920 | 565.2 | 226.08 | 264.2745 | 476.5 | 377.3 | 362.8 | 349.6 | 541.4 | 66.4 | 17.9 | 119.6 | 5.9 | 218.5 | 6.5 | 855.6 | 825.5 | 199.2 | 830.5 | 737.4 | 868.4 | 713 | 647.5 | 686.4 | 620.2 | 715.3 | 719.4 | 129.8 | 262.2 | 322.8 | 642.5 | 572.6 | 562.4 | 558.3 | 585.2 | 273.7 | 417.6 | 398.5 | 325.7 | 341.3 | 470.8 | 336
1157 | 921 | 565.1 | 226.04 | 264.2277 | 477.2 | 377 | 362.6 | 349.5 | 540.8 | 66.5 | 17.9 | 119.6 | 5.4 | 207.6 | 6.2 | 848.9 | 822.2 | 198.2 | 829.6 | 736.5 | 867 | 710.2 | 644.6 | 672.1 | 619.7 | 715.6 | 717 | 130.1 | 262.4 | 323.1 | 642.1 | 572.5 | 561.1 | 558.5 | 585.1 | 274 | 418.5 | 399.4 | 326.1 | 341.8 | 471 | 336.4
1158 | 922 | 565.1 | 226.04 | 264.2277 | 481.6 | 375.9 | 362.5 | 351.1 | 539.7 | 66.5 | 17.9 | 119.6 | 5.7 | 200.9 | 5.9 | 840.6 | 816.4 | 197.1 | 828.7 | 735.9 | 866.6 | 707.4 | 641.1 | 665 | 618.4 | 716.2 | 715.4 | 130.3 | 262.5 | 323.2 | 641.5 | 571.9 | 557.3 | 558.6 | 584.1 | 274.3 | 419.2 | 399.7 | 326.5 | 341.9 | 471.2 | 336.7
1159 | 923 | 565.4 | 226.16 | 264.368 | 483.2 | 374.6 | 364.3 | 352.4 | 537.4 | 66.5 | 17.9 | 119.6 | 5.9 | 185.8 | 5.8 | 845.6 | 816.8 | 196.1 | 828.1 | 735.5 | 866.8 | 705.9 | 638.5 | 662.2 | 617.6 | 716.8 | 715.3 | 130.6 | 262.7 | 323.4 | 641.2 | 571.3 | 554.3 | 558.6 | 583.3 | 274.6 | 419.6 | 399.9 | 326.9 | 342.1 | 471.4 | 337
1160 | 924 | 565.4 | 226.16 | 264.368 | 481.8 | 373.2 | 366.2 | 352.8 | 534.9 | 66.5 | 17.9 | 119.5 | 6.1 | 188.8 | 5.2 | 845.6 | 818 | 196.4 | 829 | 735.6 | 867.5 | 706.7 | 637.5 | 667.9 | 616.9 | 717.1 | 715.8 | 130.8 | 262.8 | 323.5 | 640.8 | 569.4 | 553.6 | 558.7 | 582.4 | 274.9 | 419.4 | 399.4 | 327.3 | 342.1 | 471.7 | 337.4
1161 | 925 | 564.7 | 225.88 | 264.0407 | 479 | 372.2 | 367.7 | 352.6 | 536.8 | 66.5 | 17.9 | 119.4 | 6.1 | 203.3 | 4.5 | 851.8 | 819.3 | 195.2 | 830.2 | 735.9 | 868.3 | 708.8 | 638 | 674.1 | 617.2 | 717.4 | 715.8 | 131.1 | 262.9 | 323.7 | 641 | 569.3 | 557.3 | 559 | 583.3 | 275.2 | 418.7 | 398.9 | 327.6 | 342.2 | 471.9 | 337.6
1162 | 926 | 566.2 | 226.48 | 264.7421 | 478.3 | 372.4 | 368.1 | 351.9 | 541.3 | 66.7 | 17.8 | 119.4 | 6.1 | 220.9 | 3.9 | 855.5 | 820.7 | 194.7 | 831.2 | 736.1 | 869.7 | 711.4 | 639.9 | 675.8 | 618 | 717.5 | 717.4 | 131.3 | 263.1 | 323.8 | 641.8 | 569.7 | 561.3 | 559.1 | 584.7 | 275.5 | 417.9 | 398.4 | 327.9 | 342.3 | 472.1 | 337.9
1163 | 927 | 566.3 | 226.52 | 264.7888 | 480.9 | 372.3 | 368 | 351 | 544.2 | 66.8 | 17.8 | 119.5 | 6 | 196.7 | 4.5 | 853.3 | 817.9 | 195 | 832.1 | 736.6 | 870.4 | 712.6 | 639.8 | 679.4 | 618.1 | 718 | 718.3 | 131.6 | 263.4 | 324 | 642.5 | 569.9 | 563 | 559.4 | 584.3 | 275.8 | 417.5 | 397.6 | 328.3 | 342.3 | 472.3 | 338.2
1164 | 928 | 567 | 226.8 | 265.1161 | 485.7 | 372.1 | 368 | 349.6 | 546.4 | 66.9 | 17.8 | 119.5 | 5.5 | 194.8 | 5.5 | 854.1 | 819.5 | 195.1 | 832.5 | 737.4 | 870.2 | 717.7 | 643.8 | 695.2 | 619.5 | 718.7 | 721.1 | 131.9 | 263.8 | 324.4 | 643.8 | 569.8 | 569.1 | 559.6 | 584.3 | 276.1 | 417.1 | 396.8 | 328.6 | 342.3 | 472.5 | 338.5
1165 | 929 | 568 | 227.2 | 265.5837 | 488.4 | 372.4 | 368.3 | 348.4 | 548.5 | 66.9 | 17.8 | 119.5 | 5.8 | 196.6 | 5.9 | 850.6 | 814.3 | 194.9 | 833.9 | 737 | 870.2 | 719.2 | 644.3 | 693.2 | 620.7 | 719.2 | 720.8 | 132.1 | 264.1 | 325 | 644 | 569.7 | 575.6 | 559.8 | 585.3 | 276.5 | 416.4 | 396.2 | 328.9 | 342.2 | 472.7 | 338.7
1166 | 930 | 568.1 | 227.24 | 265.6305 | 488.7 | 374.1 | 367.9 | 347.2 | 549.7 | 66.9 | 17.8 | 119.4 | 5.8 | 199 | 6.2 | 851.6 | 819.3 | 194.8 | 835.4 | 737.3 | 868.9 | 720.4 | 645.4 | 703.4 | 621.4 | 719.5 | 721.9 | 132.4 | 264.5 | 325 | 644.2 | 569.6 | 577.2 | 560.1 | 584.4 | 276.8 | 415.7 | 396.1 | 329.2 | 342.3 | 472.9 | 339
1167 | 931 | 566.6 | 226.64 | 264.9291 | 488.9 | 374.5 | 368.2 | 346.4 | 550.9 | 67 | 17.8 | 119.4 | 5.7 | 197.7 | 6.4 | 857 | 828 | 194.5 | 837.8 | 737.8 | 868.1 | 721.9 | 648.3 | 711.5 | 622.6 | 719.9 | 725 | 132.6 | 264.8 | 325 | 644.5 | 570.1 | 577.7 | 560.2 | 585.3 | 277.1 | 415.1 | 396 | 329.4 | 342.4 | 473.1 | 339.2
1168 | 932 | 566.3 | 226.52 | 264.7888 | 488.9 | 375.1 | 368.3 | 346.3 | 550.9 | 67 | 17.8 | 119.3 | 6.2 | 207.7 | 6.7 | 860.4 | 831.8 | 194.1 | 838.8 | 738.1 | 867.8 | 721.3 | 649.4 | 704.5 | 622.9 | 720.1 | 724.6 | 132.9 | 265.1 | 325.1 | 644.8 | 570.8 | 573.6 | 560.7 | 585.8 | 277.4 | 415.3 | 395.2 | 329.7 | 342.6 | 473.3 | 339.5
1169 | 933 | 566.1 | 226.44 | 264.6953 | 485.6 | 376.7 | 367.8 | 347.9 | 548.9 | 66.9 | 17.8 | 119.4 | 5.9 | 214.9 | 6.8 | 859 | 832.9 | 194.2 | 838 | 737.6 | 867.7 | 719.9 | 649.7 | 697 | 623 | 720.4 | 724.4 | 133.1 | 265.4 | 325.2 | 644.9 | 571.3 | 569.3 | 561 | 585.3 | 277.6 | 415.8 | 395 | 330.1 | 342.7 | 473.5 | 339.8
1170 | 934 | 565 | 226 | 264.181 | 484 | 376.2 | 367 | 349.1 | 546.6 | 66.9 | 17.8 | 119.4 | 6 | 190.1 | 6.7 | 861.8 | 835.9 | 193.8 | 837.7 | 737.9 | 867.2 | 718.7 | 648.8 | 697.6 | 622.5 | 720.4 | 724.1 | 133.4 | 265.6 | 325.4 | 644.6 | 571 | 567.8 | 561.1 | 585.2 | 277.9 | 416 | 394.6 | 330.4 | 342.9 | 473.8 | 340.1
1171 | 935 | 567 | 226.8 | 265.1161 | 481.8 | 376 | 366.2 | 350.3 | 545.3 | 66.9 | 17.8 | 119.4 | 5.9 | 205.4 | 6.3 | 867.1 | 841 | 192.9 | 837.8 | 737.8 | 867.5 | 719.4 | 649.1 | 699 | 622.6 | 720.4 | 724.1 | 133.6 | 265.9 | 325.6 | 644.7 | 570.7 | 571.3 | 561.5 | 585.6 | 278.2 | 416.3 | 394.5 | 330.8 | 343 | 474 | 340.4
1172 | 936 | 567.4 | 226.96 | 265.3032 | 483.8 | 376.2 | 365.8 | 350.7 | 546 | 66.9 | 17.8 | 119.4 | 5.9 | 205.6 | 5.7 | 870.8 | 843.8 | 192.8 | 837.8 | 738 | 867.7 | 718.5 | 649 | 697.2 | 622.4 | 720.6 | 723.1 | 133.8 | 266.1 | 325.7 | 644.7 | 570.8 | 571.6 | 561.8 | 586.4 | 278.5 | 416.3 | 395.1 | 331.1 | 343.2 | 474.3 | 340.7
1173 | 937 | 567.3 | 226.92 | 265.2564 | 483.3 | 376.3 | 365.5 | 350.3 | 545.4 | 66.9 | 17.8 | 119.4 | 5.3 | 199.8 | 5.7 | 871.2 | 846.7 | 193.5 | 837.6 | 737.9 | 868 | 717.7 | 648.7 | 697.9 | 622.1 | 720.6 | 722 | 134.1 | 266.3 | 325.8 | 644.7 | 571.2 | 569.6 | 562.1 | 587.6 | 278.7 | 416.4 | 395.3 | 331.4 | 343.4 | 474.5 | 341
1174 | 938 | 568.3 | 227.32 | 265.724 | 479.2 | 376.2 | 364.7 | 350.3 | 543.8 | 67 | 17.8 | 119.5 | 5.6 | 203.5 | 5.8 | 875.2 | 849.8 | 193.5 | 837.5 | 738.3 | 868.2 | 718.9 | 650.6 | 704.8 | 622 | 720.5 | 722.4 | 134.3 | 266.6 | 326 | 645.1 | 571.5 | 569.7 | 562.3 | 588.4 | 279 | 416.6 | 394.9 | 331.8 | 343.5 | 474.7 | 341.3
1175 | 939 | 565.1 | 226.04 | 264.2277 | 478.4 | 376 | 363.5 | 350.8 | 543.8 | 67.1 | 17.8 | 119.5 | 6 | 208.7 | 5.8 | 875.4 | 846.5 | 193.4 | 837.4 | 738.6 | 868.7 | 721.4 | 651.8 | 705.2 | 621.9 | 720.4 | 723.7 | 134.6 | 266.8 | 326.2 | 645.4 | 571.5 | 572.1 | 562.4 | 587.9 | 279.2 | 416.7 | 394.9 | 332.1 | 343.6 | 475 | 341.6
1176 | 940 | 565.6 | 226.24 | 264.4615 | 481.7 | 376.3 | 363.4 | 350.5 | 543.1 | 67.1 | 17.8 | 119.5 | 6.1 | 199 | 5.7 | 872.5 | 840.4 | 193 | 837.9 | 738.2 | 869 | 720.8 | 652 | 699.6 | 621.8 | 720.4 | 724 | 134.8 | 267 | 326.3 | 645.6 | 571.4 | 570.3 | 562.5 | 587.5 | 279.4 | 417 | 395.5 | 332.4 | 343.8 | 475.2 | 341.9
1177 | 941 | 565.6 | 226.24 | 264.4615 | 486.5 | 375.9 | 363.4 | 350.6 | 540.7 | 67.2 | 17.8 | 119.7 | 5.6 | 201.3 | 5.6 | 854.4 | 833.7 | 193 | 836.6 | 737.2 | 868.1 | 717.3 | 649.5 | 683.7 | 620.9 | 720.7 | 721.8 | 135.1 | 267.3 | 326.5 | 645.7 | 571.4 | 567.2 | 562.5 | 586.8 | 279.6 | 417.6 | 396.3 | 332.9 | 344.1 | 475.4 | 342.2
1178 | 942 | 567 | 226.8 | 265.1161 | 487.2 | 375.6 | 363.3 | 353 | 539 | 67.2 | 17.8 | 119.7 | 5.4 | 205.1 | 5.3 | 857.9 | 836 | 193 | 835 | 736.8 | 866.9 | 712.8 | 645.6 | 676.5 | 619.5 | 721 | 718.9 | 135.3 | 267.6 | 326.6 | 645.1 | 571 | 560.7 | 562.5 | 585.1 | 279.9 | 418.6 | 396.5 | 333.4 | 344.4 | 475.6 | 342.5
1179 | 943 | 565.9 | 226.36 | 264.6018 | 486.4 | 375.8 | 363.8 | 355.2 | 536 | 67.3 | 17.8 | 119.6 | 6.1 | 205.3 | 5.1 | 861.4 | 836.7 | 193.2 | 833.9 | 736.4 | 867.4 | 711.5 | 644 | 678.7 | 618.7 | 721.3 | 718.3 | 135.6 | 267.8 | 326.7 | 645 | 570.3 | 555.7 | 562.5 | 584.4 | 280.2 | 419.2 | 396.7 | 334 | 344.5 | 475.9 | 342.9
1180 | 944 | 565.9 | 226.36 | 264.6018 | 485.7 | 375.5 | 364.9 | 356.7 | 535.8 | 67.3 | 17.8 | 119.7 | 6.1 | 207.3 | 4.8 | 861.9 | 831.5 | 192.5 | 833.4 | 736.4 | 868.3 | 711.4 | 643.4 | 676.3 | 618.8 | 721.7 | 719.3 | 135.8 | 267.9 | 326.9 | 645 | 569.9 | 553.7 | 562.5 | 584.3 | 280.4 | 419.8 | 397.5 | 334.6 | 344.8 | 476.1 | 343.2
1181 | 945 | 566.2 | 226.48 | 264.7421 | 482.9 | 375.2 | 366 | 357.2 | 536.7 | 67.3 | 17.8 | 119.9 | 5.9 | 208.2 | 4.3 | 853.2 | 825.1 | 192.2 | 832.4 | 736 | 867.7 | 709.5 | 642.2 | 666.8 | 619 | 722.4 | 717.8 | 136.1 | 268.1 | 327.2 | 644.9 | 570.4 | 555 | 562.6 | 587.2 | 280.7 | 420.7 | 398.9 | 335.1 | 345.1 | 476.4 | 343.6
1182 | 946 | 567 | 226.8 | 265.1161 | 481 | 374.6 | 366.1 | 357.5 | 536.3 | 67.2 | 17.8 | 120 | 5.6 | 215.8 | 3.7 | 854.4 | 823.3 | 192.3 | 831.4 | 735.6 | 867.6 | 709.1 | 640.4 | 667.9 | 618.3 | 722.7 | 717.8 | 136.4 | 268.3 | 327.4 | 644.3 | 570.4 | 552 | 562.8 | 587 | 281 | 421.2 | 400.2 | 335.6 | 345.4 | 476.7 | 343.9
1183 | 947 | 565.5 | 226.2 | 264.4148 | 487.6 | 373.7 | 367.1 | 357.7 | 533.7 | 67.2 | 17.8 | 120 | 5.5 | 216.9 | 3.3 | 853.8 | 818.2 | 192.4 | 830.8 | 735.8 | 868 | 710.8 | 640.6 | 676.6 | 617.9 | 722.9 | 719.6 | 136.6 | 268.5 | 327.5 | 644.3 | 569.6 | 550.6 | 562.8 | 585.9 | 281.2 | 421.4 | 400.6 | 336 | 345.7 | 477 | 344.3
1184 | 948 | 564.2 | 225.68 | 263.8069 | 489.3 | 372.4 | 368.1 | 357.4 | 532.3 | 67.1 | 17.8 | 120.1 | 5.2 | 217 | 3.3 | 856.2 | 819.4 | 192.6 | 831.2 | 735.9 | 868.6 | 714.2 | 641.6 | 687.9 | 617.7 | 723.6 | 721.8 | 136.9 | 268.7 | 327.7 | 644.3 | 569 | 550.4 | 562.8 | 584.5 | 281.5 | 421.2 | 400.9 | 336.4 | 345.8 | 477.2 | 344.6
1185 | 949 | 565.2 | 226.08 | 264.2745 | 486.4 | 371.2 | 368.7 | 356.3 | 536.5 | 67.1 | 17.8 | 120 | 5.3 | 207.9 | 3.3 | 860.7 | 820.5 | 193 | 832.5 | 736.3 | 868.4 | 717.5 | 642.9 | 695.5 | 618 | 724.1 | 722.3 | 137.1 | 268.9 | 327.9 | 644.4 | 568.8 | 556.7 | 562.8 | 584.2 | 281.8 | 420.7 | 400.7 | 336.8 | 346 | 477.5 | 344.8
1186 | 950 | 566.3 | 226.52 | 264.7888 | 487.4 | 370.6 | 368.7 | 354.9 | 539.4 | 67.1 | 17.8 | 119.8 | 5.4 | 204.8 | 3.7 | 859.8 | 822.3 | 193.7 | 832.9 | 736.5 | 867.8 | 720.1 | 644.5 | 700.5 | 618.3 | 724.4 | 725.1 | 137.4 | 269.1 | 328.1 | 644.2 | 568.8 | 560.1 | 563 | 584.7 | 282 | 420.1 | 400.7 | 337.1 | 346.3 | 477.6 | 345.1
1187 | 951 | 566.2 | 226.48 | 264.7421 | 487.7 | 370.5 | 367.8 | 353.7 | 542.2 | 67 | 17.8 | 119.8 | 5.6 | 208.2 | 4.4 | 859.2 | 824.8 | 193.3 | 832.9 | 737 | 867.2 | 721.2 | 646.1 | 705.2 | 618.5 | 724.3 | 727.6 | 137.6 | 269.4 | 328.3 | 644 | 570 | 558.7 | 563.2 | 586 | 282.3 | 419.8 | 400.9 | 337.4 | 346.5 | 477.8 | 345.3
1188 | 952 | 565.5 | 226.2 | 264.4148 | 487.2 | 369.9 | 367.2 | 353 | 539.9 | 67 | 17.8 | 119.7 | 5.7 | 188.9 | 5.2 | 864.9 | 827.9 | 193.8 | 832.4 | 737 | 867.1 | 721.8 | 646.8 | 704.3 | 618.3 | 724.1 | 727.8 | 137.9 | 269.7 | 328.4 | 644.4 | 569.9 | 557.3 | 563.4 | 586 | 282.5 | 419.5 | 400.5 | 337.8 | 346.5 | 478.1 | 345.6
1189 | 953 | 565.2 | 226.08 | 264.2745 | 483.9 | 369.3 | 367.1 | 352.8 | 539.4 | 67 | 17.8 | 119.6 | 5.7 | 197.7 | 5.4 | 865.1 | 832.3 | 193.7 | 832.4 | 737.3 | 867.3 | 722.8 | 647.6 | 706.2 | 618.4 | 724.1 | 727.8 | 138.2 | 269.9 | 328.5 | 645 | 569.9 | 560.6 | 563.5 | 585.9 | 282.8 | 419.3 | 400 | 338.1 | 346.7 | 478.2 | 345.8
1190 | 954 | 565.1 | 226.04 | 264.2277 | 479.8 | 369.5 | 367.4 | 352.6 | 542.1 | 67 | 17.8 | 119.7 | 5.5 | 197.5 | 5.7 | 864.7 | 836.4 | 193.8 | 833.2 | 738 | 867.5 | 724.8 | 650.1 | 715.2 | 618.8 | 724 | 727.9 | 138.4 | 270.2 | 328.7 | 645.6 | 570.2 | 564.4 | 563.6 | 585.9 | 283 | 418.6 | 399.3 | 338.4 | 346.9 | 478.5 | 346.1
1191 | 955 | 564.9 | 225.96 | 264.1342 | 477.8 | 369.9 | 366.5 | 352.2 | 542.2 | 67.1 | 17.8 | 119.9 | 5.6 | 194 | 5.8 | 861.2 | 838.5 | 194.3 | 834 | 738.5 | 867.7 | 725.6 | 651.3 | 718.3 | 618.6 | 723.8 | 728.4 | 138.7 | 270.4 | 328.8 | 645.4 | 570.2 | 564.3 | 563.7 | 586.3 | 283.3 | 418.7 | 399.2 | 338.8 | 347 | 478.7 | 346.3
1192 | 956 | 564.6 | 225.84 | 263.9939 | 478.8 | 370 | 365.9 | 351.9 | 542.5 | 67.2 | 17.8 | 119.9 | 6.1 | 199.6 | 5.8 | 861.5 | 836.9 | 193.6 | 834.7 | 738.4 | 868.4 | 728.6 | 653.6 | 724.8 | 619.1 | 723.9 | 729.7 | 139 | 270.7 | 329.1 | 645.9 | 570.4 | 568.9 | 563.9 | 586.9 | 283.5 | 419.6 | 399.4 | 339.2 | 347.2 | 478.9 | 346.6
1193 | 957 | 566.6 | 226.64 | 264.9291 | 478.5 | 370.8 | 365.2 | 352.1 | 544.8 | 67.3 | 17.8 | 119.9 | 6 | 208.6 | 5.7 | 860.5 | 838 | 192.9 | 836.5 | 738.8 | 868.9 | 731.1 | 655.5 | 727.4 | 619.4 | 724.3 | 731.7 | 139.2 | 270.9 | 329.3 | 645.9 | 570.2 | 571.6 | 564 | 587.4 | 283.7 | 419.3 | 399.2 | 339.4 | 347.3 | 479.1 | 346.9
1194 | 958 | 566.5 | 226.6 | 264.8823 | 482.2 | 373 | 364.6 | 351.9 | 544.9 | 67.4 | 17.8 | 119.8 | 5.7 | 200.6 | 5.5 | 861 | 838.5 | 192.9 | 837.2 | 739 | 869 | 732.9 | 657.5 | 731.7 | 619.6 | 724.5 | 733 | 139.5 | 271.2 | 329.3 | 645.9 | 569.7 | 573.1 | 564.2 | 587.5 | 283.9 | 418.8 | 399 | 339.8 | 347.5 | 479.3 | 347.2
1195 | 959 | 565.8 | 226.32 | 264.555 | 485.1 | 375.5 | 364.4 | 351 | 545 | 67.5 | 17.8 | 119.8 | 5.8 | 206.7 | 5.3 | 862.9 | 836.8 | 192.4 | 837.9 | 739.6 | 869 | 734.1 | 659.2 | 733.9 | 620.3 | 724.8 | 734.5 | 139.8 | 271.4 | 329.6 | 646.2 | 569.6 | 573.7 | 564.4 | 587.6 | 284.1 | 418.2 | 398.4 | 340 | 347.6 | 479.4 | 347.4
1196 | 960 | 566.8 | 226.72 | 265.0226 | 484.7 | 376.3 | 364.2 | 350.7 | 544.9 | 67.6 | 17.8 | 119.8 | 5.5 | 215.5 | 5.4 | 859.7 | 837.7 | 192.6 | 840 | 739.5 | 869.3 | 733.3 | 659.6 | 725.2 | 620.5 | 725.3 | 735.5 | 140.1 | 271.5 | 329.8 | 646.4 | 570 | 574.2 | 564.9 | 587.4 | 284.3 | 417.7 | 397.6 | 340.3 | 347.6 | 479.6 | 347.6
1197 | 961 | 566.7 | 226.68 | 264.9759 | 482.8 | 376.6 | 364.1 | 350.6 | 543.8 | 67.7 | 17.8 | 119.9 | 5.6 | 204.6 | 5.3 | 860.9 | 844.1 | 193.3 | 840.4 | 739.3 | 869.6 | 732.5 | 658.9 | 725.3 | 620 | 725.6 | 735.5 | 140.4 | 271.7 | 329.9 | 646.6 | 570 | 570.6 | 565.6 | 586 | 284.6 | 418.6 | 397.1 | 340.6 | 347.6 | 479.8 | 347.9
1198 | 962 | 567 | 226.8 | 265.1161 | 482.2 | 377.2 | 364.5 | 350.6 | 541.4 | 67.8 | 17.8 | 119.8 | 5.9 | 202.6 | 5.2 | 863.4 | 845.4 | 193.6 | 840.5 | 739.3 | 869.9 | 731.7 | 657 | 723.5 | 619.2 | 725.9 | 735.9 | 140.6 | 271.9 | 330 | 647 | 569.1 | 568.5 | 566.5 | 584.5 | 284.8 | 418.7 | 396.4 | 340.9 | 347.7 | 480 | 348.2
1199 | 963 | 568 | 227.2 | 265.5837 | 481.9 | 378.2 | 364.5 | 351.1 | 540.6 | 67.8 | 17.8 | 119.8 | 5.9 | 215.5 | 5 | 862.6 | 843.2 | 193.5 | 841.1 | 738.9 | 869.9 | 729.6 | 655.2 | 716.2 | 619 | 726.1 | 734.1 | 140.9 | 272.1 | 330.2 | 647.3 | 569.1 | 568 | 567.3 | 584.5 | 285 | 418.5 | 396 | 341.2 | 347.8 | 480.2 | 348.4
1200 | 964 | 566.7 | 226.68 | 264.9759 | 480.8 | 378.4 | 363.7 | 351.1 | 539.5 | 67.8 | 17.8 | 119.8 | 5.4 | 215 | 4.9 | 852 | 841.7 | 193.1 | 840 | 738.2 | 868.6 | 725.8 | 652.4 | 705.5 | 618.4 | 726.4 | 732.7 | 141.2 | 272.3 | 330.3 | 647.3 | 568.7 | 561.1 | 567.8 | 584 | 285.2 | 418.2 | 395.7 | 341.4 | 347.9 | 480.4 | 348.7
1201 | 965 | 566.9 | 226.76 | 265.0694 | 480.3 | 378.4 | 362.7 | 351.2 | 536.2 | 67.9 | 17.8 | 119.8 | 5.5 | 192.2 | 5 | 851.7 | 838.7 | 192.5 | 839.1 | 737.7 | 868.7 | 723.3 | 649.4 | 700.2 | 617.3 | 726.8 | 731 | 141.4 | 272.5 | 330.4 | 647.5 | 568.1 | 558 | 568 | 583.2 | 285.4 | 417.4 | 395 | 341.8 | 347.9 | 480.6 | 349
1202 | 966 | 568.3 | 227.32 | 265.724 | 479.7 | 378.2 | 362.1 | 351.7 | 535 | 67.9 | 17.8 | 119.9 | 5.8 | 210.3 | 5.1 | 856.3 | 835.2 | 192.6 | 838.4 | 737.1 | 870.2 | 721.7 | 647.9 | 694.4 | 617.1 | 726.7 | 730.5 | 141.7 | 272.7 | 330.5 | 648.2 | 568 | 555.1 | 568.3 | 582.8 | 285.6 | 416.7 | 394.7 | 342.1 | 347.9 | 480.8 | 349.2
1203 | 967 | 566.6 | 226.64 | 264.9291 | 481.6 | 378.1 | 361.8 | 352.3 | 535.5 | 67.9 | 17.8 | 120.1 | 5.4 | 224 | 5.5 | 848.6 | 830.4 | 192.9 | 837.3 | 736.5 | 870.5 | 719.2 | 645.3 | 686.1 | 616.5 | 727 | 729 | 142 | 273 | 330.6 | 648.6 | 568.4 | 552.6 | 568.7 | 584.2 | 285.8 | 416.9 | 395.2 | 342.4 | 348.2 | 480.9 | 349.5
1204 | 968 | 566.4 | 226.56 | 264.8356 | 482.2 | 377.2 | 361.8 | 353.5 | 532.9 | 67.9 | 17.8 | 120.3 | 5.5 | 224.9 | 5.6 | 843.6 | 826.3 | 193.3 | 836.5 | 735.5 | 870.9 | 717.7 | 642.4 | 681.2 | 615.2 | 727.1 | 726.8 | 142.3 | 273.3 | 330.8 | 648.4 | 567.7 | 548.5 | 568.8 | 582.8 | 286 | 417.2 | 395.1 | 342.7 | 348.3 | 481.1 | 349.8
1205 | 969 | 566.3 | 226.52 | 264.7888 | 482.5 | 376.3 | 362 | 354.8 | 531.2 | 67.9 | 17.8 | 120.4 | 5.6 | 220.8 | 5.3 | 846.6 | 824 | 192.4 | 836.4 | 734.7 | 871.5 | 717.1 | 639.4 | 679.5 | 614.5 | 727.5 | 726.1 | 142.6 | 273.6 | 331 | 648.6 | 566.7 | 548.3 | 569 | 581.3 | 286.2 | 416.9 | 395.3 | 343 | 348.4 | 481.3 | 350
1206 | 970 | 566.8 | 226.72 | 265.0226 | 482.1 | 375.8 | 361.8 | 355.5 | 530.6 | 67.9 | 17.8 | 120.4 | 6.1 | 219.9 | 5.6 | 836.9 | 816.8 | 191.8 | 835.5 | 733.6 | 870.9 | 715.1 | 637.7 | 669.2 | 614.4 | 727.7 | 725.2 | 142.9 | 273.8 | 331 | 648.8 | 566.2 | 548.8 | 569.4 | 581.3 | 286.4 | 416.9 | 396.2 | 343.4 | 348.7 | 481.4 | 350.3
1207 | 971 | 567 | 226.8 | 265.1161 | 486.8 | 376.1 | 361.3 | 356.5 | 528.7 | 67.9 | 17.8 | 120.5 | 6.2 | 241.4 | 6.2 | 837.9 | 819.8 | 191.6 | 834.5 | 732.8 | 869.7 | 712.9 | 635.3 | 663.6 | 612.5 | 728 | 723.5 | 143.2 | 274 | 331.1 | 648.3 | 566.6 | 545.4 | 569.5 | 580.3 | 286.6 | 417.4 | 396.5 | 343.7 | 348.9 | 481.5 | 350.6
1208 | 972 | 567.8 | 227.12 | 265.4902 | 485.6 | 375.7 | 361.9 | 357.6 | 526.2 | 67.9 | 17.8 | 120.5 | 5.9 | 254.7 | 5.7 | 836.9 | 819.8 | 191.4 | 833.4 | 732.3 | 869.5 | 710.4 | 632.5 | 659.7 | 612.1 | 728.1 | 721.6 | 143.5 | 274.1 | 331.3 | 648.2 | 566.5 | 541.2 | 569.6 | 580.1 | 286.8 | 418.2 | 397.3 | 344.1 | 349.2 | 481.7 | 350.8
1209 | 973 | 567 | 226.8 | 265.1161 | 485.6 | 375.6 | 363.2 | 359 | 526.9 | 67.8 | 17.8 | 120.6 | 5.5 | 255.8 | 5.1 | 835.6 | 813.4 | 191.1 | 832.1 | 731.9 | 870.1 | 709.2 | 631.4 | 656.4 | 612.1 | 728.5 | 720.6 | 143.7 | 274.3 | 331.4 | 648.1 | 566.7 | 541 | 569.7 | 580.6 | 287.1 | 418.8 | 397.9 | 344.5 | 349.4 | 481.9 | 351.1
1210 | 974 | 565.6 | 226.24 | 264.4615 | 488.6 | 375.1 | 364.4 | 360.6 | 525.1 | 67.8 | 17.8 | 120.7 | 5.4 | 232.6 | 4.5 | 842.2 | 814.6 | 191 | 831.2 | 731.5 | 870.1 | 708.5 | 630.6 | 655.4 | 611.8 | 728.8 | 720.7 | 144 | 274.5 | 331.6 | 647.8 | 566.7 | 539.6 | 569.7 | 582.3 | 287.3 | 419.4 | 398.1 | 344.8 | 349.6 | 482.1 | 351.4
1211 | 975 | 565 | 226 | 264.181 | 487.7 | 374.3 | 365.3 | 360.9 | 524.2 | 67.8 | 17.8 | 120.7 | 6.1 | 212.1 | 4.2 | 847.5 | 814.5 | 190.8 | 830.5 | 731.6 | 870.2 | 708.1 | 630.8 | 658.2 | 612.4 | 728.8 | 719.9 | 144.3 | 274.7 | 331.7 | 647.2 | 566.1 | 537.6 | 569.7 | 582.5 | 287.5 | 419.3 | 398.4 | 345.2 | 349.8 | 482.4 | 351.7
1212 | 976 | 564.9 | 225.96 | 264.1342 | 487.3 | 373.7 | 365.6 | 360.8 | 523.5 | 67.8 | 17.8 | 120.7 | 6.5 | 217.5 | 3.9 | 848.9 | 819.8 | 190.6 | 829.7 | 731.3 | 869.8 | 708.3 | 630.7 | 662.2 | 612.5 | 729.1 | 719.9 | 144.6 | 275 | 331.8 | 647.1 | 566.2 | 535.4 | 569.8 | 582.2 | 287.8 | 419.1 | 398.8 | 345.5 | 350.1 | 482.6 | 352
1213 | 977 | 568.3 | 227.32 | 265.724 | 486.6 | 374 | 365.5 | 361 | 524 | 67.8 | 17.7 | 120.8 | 5.6 | 214.9 | 3.6 | 849.2 | 821.7 | 190.1 | 828.8 | 731.1 | 869.1 | 708.3 | 630.5 | 660.5 | 612.6 | 729.1 | 719.7 | 144.9 | 275.3 | 332.2 | 647.3 | 566.2 | 535.5 | 570 | 582.6 | 288 | 419.3 | 399.6 | 345.9 | 350.4 | 482.9 | 352.2
1214 | 978 | 568.6 | 227.44 | 265.8643 | 485.3 | 374.1 | 365.2 | 362 | 525.3 | 67.8 | 17.8 | 120.8 | 5.3 | 228.6 | 3.3 | 856.2 | 831.4 | 189.7 | 828.2 | 730.8 | 868.5 | 708.1 | 630.2 | 662.1 | 612.4 | 729.4 | 719.1 | 145.2 | 275.6 | 332.2 | 647.4 | 566.1 | 534.5 | 570.1 | 582.8 | 288.2 | 419.7 | 400.5 | 346.3 | 350.6 | 483.1 | 352.5
1215 | 979 | 567.8 | 227.12 | 265.4902 | 483.5 | 374.1 | 365.3 | 363 | 528.2 | 67.9 | 17.8 | 120.8 | 5.7 | 219.6 | 3.3 | 851.4 | 831 | 189.4 | 827.8 | 730.8 | 867.6 | 708 | 630.7 | 663.3 | 612.8 | 729.3 | 718.7 | 145.5 | 275.8 | 332.4 | 647.5 | 566.6 | 536 | 570.4 | 582.9 | 288.4 | 420.3 | 401.7 | 346.7 | 350.8 | 483.3 | 352.8
1216 | 980 | 566.8 | 226.72 | 265.0226 | 484.1 | 374 | 365 | 363.5 | 528 | 67.8 | 17.7 | 120.8 | 5.8 | 196.6 | 3.3 | 855.8 | 827.6 | 188.3 | 827 | 730.8 | 867.7 | 708.5 | 632.6 | 668.8 | 613.2 | 728.7 | 718.9 | 145.8 | 276 | 332.5 | 647.5 | 567 | 534.6 | 570.6 | 582.8 | 288.7 | 421.5 | 402.9 | 347.2 | 351 | 483.6 | 353.1
1217 | 981 | 566.4 | 226.56 | 264.8356 | 483.4 | 374.2 | 364.7 | 363 | 527.1 | 67.8 | 17.7 | 120.9 | 5.5 | 196.1 | 3.2 | 858.6 | 832.6 | 188.3 | 826.7 | 730.7 | 868.6 | 711.3 | 634.7 | 679.9 | 613.4 | 728.3 | 720.5 | 146.1 | 276.3 | 332.7 | 647.5 | 566.6 | 535.1 | 570.7 | 582.9 | 288.9 | 422.5 | 403.8 | 347.6 | 351.3 | 483.8 | 353.4
1218 | 982 | 565.4 | 226.16 | 264.368 | 481.3 | 374.8 | 364.9 | 362.8 | 528.5 | 67.7 | 17.7 | 121 | 5.4 | 205.3 | 2.9 | 863.3 | 835.4 | 188.9 | 825.9 | 730.6 | 868.9 | 715.3 | 636.6 | 692.7 | 613.2 | 728.3 | 721.9 | 146.4 | 276.5 | 332.9 | 647.7 | 565.9 | 538.3 | 570.9 | 582.5 | 289.1 | 422.5 | 404.2 | 348 | 351.5 | 484.1 | 353.8
1219 | 983 | 566.9 | 226.76 | 265.0694 | 484.5 | 375.7 | 365.9 | 362.6 | 529 | 67.7 | 17.7 | 121.1 | 5.6 | 217.9 | 3.2 | 860.9 | 839.3 | 189.3 | 826.4 | 731.2 | 868.1 | 721.5 | 641 | 709.6 | 614.2 | 728.5 | 724.1 | 146.7 | 276.7 | 333.1 | 648 | 565.4 | 545.6 | 571.3 | 582.8 | 289.4 | 422.1 | 404.3 | 348.3 | 351.5 | 484.2 | 354
1220 | 984 | 567.3 | 226.92 | 265.2564 | 488 | 377.5 | 366.6 | 361.5 | 531.6 | 67.8 | 17.7 | 121.2 | 5.6 | 214.4 | 3.9 | 860.7 | 841.6 | 189.9 | 827 | 732.1 | 867.7 | 724.5 | 645.9 | 720.7 | 616 | 728.2 | 725.2 | 147 | 277 | 333.2 | 648.7 | 566.5 | 554.1 | 571.7 | 586.7 | 289.6 | 421.8 | 404.6 | 348.6 | 351.6 | 484.4 | 354.2
1221 | 985 | 565.6 | 226.24 | 264.4615 | 484 | 378.7 | 367.2 | 360.2 | 535.2 | 67.9 | 17.7 | 121.2 | 5.3 | 204 | 4.2 | 862.6 | 845.4 | 190.3 | 827.9 | 732.8 | 868.1 | 726.7 | 649.4 | 727 | 616.6 | 727.9 | 728 | 147.3 | 277.2 | 333.4 | 649.1 | 567.2 | 558.3 | 572.1 | 587.4 | 289.9 | 421.5 | 404.1 | 348.8 | 351.6 | 484.6 | 354.5
1222 | 986 | 565.7 | 226.28 | 264.5083 | 481 | 379.4 | 366.8 | 358.9 | 536.2 | 67.9 | 17.7 | 121.3 | 5 | 203.2 | 4.2 | 859.8 | 848.1 | 190.9 | 829.7 | 733.2 | 868 | 728.9 | 651.3 | 731.5 | 616.8 | 728.1 | 729.3 | 147.6 | 277.4 | 333.6 | 649.5 | 567.1 | 563.7 | 572.4 | 586.1 | 290.2 | 420.8 | 403.5 | 349 | 351.6 | 484.8 | 354.7
1223 | 987 | 567.2 | 226.88 | 265.2096 | 479.6 | 380.2 | 366.5 | 358.1 | 537.8 | 68 | 17.7 | 121.3 | 5.8 | 209.7 | 4.3 | 866.4 | 854.3 | 192.4 | 831.3 | 733.9 | 867.1 | 731.2 | 655 | 738.8 | 618.2 | 728 | 730.1 | 147.9 | 277.6 | 333.8 | 650 | 567.5 | 571 | 572.5 | 587.9 | 290.4 | 420.1 | 403.2 | 349.3 | 351.6 | 484.9 | 354.9
1224 | 988 | 567.9 | 227.16 | 265.537 | 475.4 | 381.7 | 366.3 | 357.4 | 542.3 | 67.9 | 17.7 | 121.3 | 5.8 | 218.9 | 4.4 | 869.8 | 860.7 | 193 | 832.4 | 734.4 | 866.7 | 732.2 | 657.6 | 743.1 | 619.1 | 727.8 | 731.1 | 148.2 | 277.8 | 334 | 649.6 | 570 | 576.2 | 572.8 | 590.4 | 290.6 | 419.7 | 402.5 | 349.5 | 351.7 | 485.1 | 355.1
1225 | 989 | 565.8 | 226.32 | 264.555 | 473.6 | 383.6 | 365.6 | 356.6 | 543.4 | 67.9 | 17.7 | 121.4 | 5.8 | 220.8 | 4.4 | 871.8 | 861.6 | 193 | 833.6 | 734.8 | 867.1 | 733.6 | 659.9 | 743.9 | 619.1 | 728 | 732.5 | 148.5 | 278 | 334.1 | 649.2 | 570.7 | 576.9 | 573.1 | 589.8 | 290.8 | 419.5 | 401.6 | 349.7 | 351.7 | 485.3 | 355.4
1226 | 990 | 566 | 226.4 | 264.6486 | 473.2 | 384.9 | 364.6 | 355.8 | 541.4 | 67.9 | 17.7 | 121.5 | 5.7 | 222.1 | 4.5 | 875.1 | 857.7 | 193.5 | 836.1 | 734.4 | 867.6 | 731.4 | 658.4 | 732.6 | 618.1 | 728.3 | 731.1 | 148.8 | 278.1 | 334.1 | 648.3 | 570.6 | 573.4 | 573.6 | 587.3 | 291 | 419.4 | 400.6 | 349.9 | 351.8 | 485.5 | 355.6
1227 | 991 | 566.9 | 226.76 | 265.0694 | 473.4 | 385.7 | 364 | 355.6 | 540 | 68 | 17.7 | 121.7 | 6.1 | 205.6 | 4.8 | 874.3 | 857.9 | 193.1 | 838.8 | 734.4 | 867.7 | 731.1 | 657.7 | 734 | 617.6 | 728.5 | 729.8 | 149.1 | 278.3 | 334.2 | 648.1 | 570.7 | 571.9 | 574.3 | 585.7 | 291.3 | 419.1 | 399.6 | 350.2 | 351.9 | 485.7 | 355.8
1228 | 992 | 566.5 | 226.6 | 264.8823 | 471.9 | 385.4 | 363.6 | 356.1 | 540.4 | 68.1 | 17.7 | 121.8 | 5.8 | 197.1 | 5.2 | 868.2 | 853.2 | 192.5 | 840.8 | 734.1 | 867.1 | 730.2 | 656.2 | 725.3 | 617 | 729 | 729.4 | 149.3 | 278.5 | 334.4 | 648.1 | 570.9 | 571.2 | 574.8 | 584.9 | 291.5 | 418.8 | 399 | 350.4 | 351.9 | 485.8 | 356.1
1229 | 993 | 566.7 | 226.68 | 264.9759 | 468.2 | 384.9 | 363.4 | 356.1 | 538.5 | 68.1 | 17.7 | 121.8 | 5.7 | 211.4 | 5.3 | 864.6 | 846.4 | 191.7 | 842 | 733.7 | 866.8 | 728.8 | 655.1 | 722.1 | 616.6 | 729.3 | 730 | 149.6 | 278.7 | 334.5 | 648.3 | 570.2 | 568.5 | 575.3 | 584.3 | 291.7 | 419 | 398.6 | 350.6 | 352 | 486 | 356.3
1230 | 994 | 568.2 | 227.28 | 265.6772 | 465.4 | 384 | 362.9 | 355.6 | 538.2 | 68.1 | 17.7 | 121.8 | 6.3 | 211.1 | 5 | 861.2 | 839.8 | 190.9 | 841.5 | 733.5 | 866.5 | 727.6 | 655.4 | 714.2 | 617.1 | 729.8 | 730 | 149.9 | 278.9 | 334.7 | 648.5 | 570.7 | 566.3 | 575.7 | 585 | 291.9 | 419 | 398.5 | 350.9 | 352.2 | 486.2 | 356.5
1231 | 995 | 566.8 | 226.72 | 265.0226 | 462.7 | 383 | 362.1 | 355.7 | 535.6 | 68.2 | 17.7 | 121.8 | 6.2 | 230.5 | 4.7 | 866.3 | 835.8 | 190.4 | 840 | 733.2 | 866.9 | 725.8 | 654 | 705.3 | 616.8 | 730.1 | 729.1 | 150.2 | 279 | 334.8 | 648.7 | 571.2 | 561.5 | 576.1 | 585.5 | 292.1 | 418.9 | 398.6 | 351.2 | 352.3 | 486.3 | 356.8
1232 | 996 | 567.6 | 227.04 | 265.3967 | 460.6 | 382.3 | 361.8 | 356.6 | 533.8 | 68.2 | 17.7 | 121.7 | 5.7 | 225.3 | 4.1 | 866.7 | 831.6 | 190.8 | 839.1 | 732.7 | 867.8 | 725.8 | 652.6 | 706.4 | 616.4 | 730.3 | 728.5 | 150.5 | 279.2 | 334.9 | 649.3 | 570.9 | 559.9 | 576.3 | 586.8 | 292.3 | 418.7 | 398.4 | 351.5 | 352.5 | 486.5 | 357
1233 | 997 | 566.6 | 226.64 | 264.9291 | 457.7 | 381.3 | 362.1 | 357.6 | 533.6 | 68.3 | 17.7 | 121.7 | 5.5 | 231.7 | 3.7 | 864.4 | 837.9 | 191.8 | 839.7 | 732.9 | 867.9 | 727.2 | 652.4 | 713.3 | 616.3 | 730.4 | 729.5 | 150.8 | 279.3 | 335 | 649.9 | 570 | 559.7 | 576.6 | 586.3 | 292.6 | 418.5 | 398 | 351.8 | 352.5 | 486.7 | 357.2
1234 | 998 | 565.6 | 226.24 | 264.4615 | 454.3 | 380.3 | 362.2 | 357.3 | 533.5 | 68.3 | 17.7 | 121.7 | 6 | 247.9 | 3.8 | 868.6 | 846.5 | 192.9 | 840.1 | 733.2 | 867.2 | 726.4 | 652.9 | 711.8 | 616.9 | 729.8 | 729.3 | 151.1 | 279.5 | 335.1 | 650 | 570.1 | 559.9 | 577 | 587.1 | 292.8 | 418.4 | 398.9 | 352.1 | 352.8 | 486.9 | 357.4
1235 | 999 | 565.2 | 226.08 | 264.2745 | 451.2 | 379.4 | 362 | 356.4 | 532.7 | 68.3 | 17.7 | 121.7 | 6.1 | 248.9 | 4.7 | 871.3 | 842.4 | 192.8 | 840.1 | 733.5 | 866.1 | 724.4 | 651.9 | 705.7 | 616.8 | 729.1 | 727.9 | 151.4 | 279.6 | 335.3 | 649.9 | 571 | 554.7 | 577.3 | 586.5 | 293 | 418.6 | 399.6 | 352.4 | 353 | 487.1 | 357.7
1236 | 1000 | 564.7 | 225.88 | 264.0407 | 449.7 | 378.8 | 361.2 | 355.8 | 532.4 | 68.2 | 17.7 | 121.6 | 5.4 | 247 | 5.2 | 868.5 | 832.5 | 191.3 | 839.9 | 733.5 | 866.5 | 724.1 | 650.7 | 707.1 | 616 | 728.8 | 728.1 | 151.7 | 279.9 | 335.4 | 650.5 | 570.8 | 556.5 | 577.6 | 585.3 | 293.2 | 418.5 | 399.7 | 352.6 | 353.1 | 487.3 | 357.9
1237 | 1001 | 566.1 | 226.44 | 264.6953 | 448.6 | 378.5 | 361 | 355.1 | 533.7 | 68.2 | 17.7 | 121.5 | 5.2 | 246.2 | 5.6 | 866.7 | 832.5 | 190.7 | 839.9 | 733.3 | 866.3 | 726.6 | 651.8 | 711.6 | 616.3 | 729.2 | 730.5 | 152 | 280.1 | 335.6 | 650.9 | 570.6 | 560.7 | 577.8 | 586.7 | 293.4 | 418.5 | 400.1 | 352.9 | 353.3 | 487.6 | 358.1
1238 | 1002 | 568.9 | 227.56 | 266.0045 | 446.7 | 377.9 | 360.8 | 355.3 | 537.1 | 68.2 | 17.7 | 121.6 | 5.8 | 248.6 | 5.8 | 864.2 | 832.5 | 191 | 840.6 | 733.2 | 866.4 | 728.7 | 653.4 | 715.6 | 617.1 | 729.6 | 732.8 | 152.3 | 280.2 | 335.8 | 651.1 | 570.9 | 561.5 | 578.2 | 587.3 | 293.6 | 418.7 | 400.6 | 353.2 | 353.5 | 487.7 | 358.4
1239 | 1003 | 568.6 | 227.44 | 265.8643 | 444.4 | 377.1 | 361.5 | 355.4 | 538.5 | 68.3 | 17.7 | 121.7 | 5.6 | 248.6 | 5.9 | 862.4 | 835 | 190.5 | 842 | 733.5 | 866.9 | 730.4 | 654.5 | 721.3 | 617.1 | 729.8 | 732.7 | 152.6 | 280.4 | 335.9 | 651.5 | 570.9 | 561.3 | 578.6 | 586.5 | 293.8 | 419.3 | 400.9 | 353.5 | 353.7 | 487.9 | 358.6
1240 | 1004 | 568 | 227.2 | 265.5837 | 442 | 376.3 | 362.3 | 356.1 | 537.4 | 68.3 | 17.7 | 121.6 | 5.3 | 240.7 | 6 | 862.9 | 837.9 | 190.9 | 842.8 | 733.3 | 867.8 | 730.6 | 654.8 | 720.4 | 617.3 | 730.3 | 733.4 | 152.9 | 280.6 | 336 | 651.7 | 570.6 | 559.9 | 578.8 | 585.6 | 294 | 419.6 | 400.9 | 353.8 | 353.8 | 488.1 | 358.9
1241 | 1005 | 568.5 | 227.4 | 265.8175 | 441.7 | 375.9 | 362.6 | 357 | 538.2 | 68.4 | 17.7 | 121.5 | 5.5 | 237.3 | 6.1 | 865.1 | 838.1 | 191.8 | 843.9 | 733.3 | 867.5 | 730.7 | 656 | 720.1 | 617.7 | 730.8 | 734.6 | 153.2 | 280.9 | 336.1 | 651.9 | 570.4 | 558 | 578.9 | 585.5 | 294.3 | 419.9 | 401 | 354 | 354 | 488.3 | 359.2
1242 | 1006 | 566.1 | 226.44 | 264.6953 | 444.8 | 375.9 | 362.5 | 357.5 | 538.8 | 68.4 | 17.7 | 121.5 | 5.6 | 242.7 | 6 | 864.8 | 839.4 | 191.6 | 844.5 | 732.9 | 867.3 | 730 | 656.7 | 714.9 | 618.1 | 731.1 | 734.2 | 153.6 | 281.1 | 336.3 | 652.3 | 570.4 | 555.4 | 579.2 | 586 | 294.5 | 420.5 | 401.3 | 354.3 | 354.2 | 488.4 | 359.4
1243 | 1007 | 567.8 | 227.12 | 265.4902 | 445.9 | 375.8 | 362.1 | 358.5 | 537.3 | 68.5 | 17.7 | 121.4 | 5.7 | 245.4 | 6.3 | 862.6 | 833.2 | 191 | 844.5 | 732.5 | 867.5 | 728.7 | 656.3 | 707.9 | 618.1 | 731.6 | 734.2 | 154 | 281.2 | 336.3 | 652.5 | 570.9 | 555.3 | 579.4 | 586.8 | 294.7 | 421.3 | 402.4 | 354.7 | 354.4 | 488.6 | 359.7
1244 | 1008 | 565.3 | 226.12 | 264.3213 | 446 | 375.7 | 361.4 | 359.5 | 532.9 | 68.5 | 17.7 | 121.4 | 5.7 | 242.5 | 6.4 | 861.5 | 826.5 | 190.5 | 844 | 731.6 | 867.2 | 726.2 | 654.6 | 696.9 | 617.4 | 731.9 | 732.9 | 154.4 | 281.3 | 336.5 | 652.2 | 570.6 | 552.5 | 579.6 | 587 | 294.9 | 422.1 | 403.4 | 355.1 | 354.8 | 488.8 | 359.9
1245 | 1009 | 563.5 | 225.4 | 263.4796 | 445.6 | 375.6 | 361.2 | 359.7 | 529.8 | 68.5 | 17.7 | 121.3 | 5.6 | 242.9 | 5.7 | 861.1 | 830.6 | 189.9 | 844.3 | 731.6 | 867.2 | 724.3 | 652.4 | 699.3 | 616.3 | 732.3 | 731.8 | 154.7 | 281.5 | 336.6 | 652.2 | 570.2 | 550.4 | 579.8 | 585.7 | 295.1 | 422.7 | 403.7 | 355.5 | 354.9 | 489 | 360.2
1246 | 1010 | 565.4 | 226.16 | 264.368 | 445.2 | 375.7 | 360.9 | 359.6 | 529.3 | 68.4 | 17.7 | 121.3 | 5.2 | 224.5 | 5.1 | 864.2 | 837.2 | 189.6 | 844.6 | 730.8 | 866.3 | 722.6 | 650.2 | 693.6 | 615.7 | 732.4 | 730.9 | 155.1 | 281.7 | 336.7 | 652.4 | 570 | 545.6 | 580 | 584.6 | 295.4 | 423.3 | 404.1 | 355.9 | 355.1 | 489.1 | 360.4
1247 | 1011 | 565.1 | 226.04 | 264.2277 | 443.6 | 376.3 | 361.3 | 359.7 | 527.1 | 68.5 | 17.7 | 121.2 | 5.7 | 219.2 | 4.9 | 873.1 | 839.7 | 189.3 | 845.1 | 730.4 | 867.1 | 722.7 | 649.2 | 694.5 | 615.6 | 733 | 730.9 | 155.5 | 281.9 | 336.8 | 652.9 | 568.7 | 545.3 | 580.2 | 583.1 | 295.6 | 423.6 | 404.6 | 356.2 | 355.3 | 489.3 | 360.7
1248 | 1012 | 565.8 | 226.32 | 264.555 | 443.3 | 376.4 | 361.8 | 359.9 | 526.1 | 68.6 | 17.7 | 121.2 | 5.7 | 235.4 | 4.6 | 872.2 | 838.7 | 188.7 | 845.8 | 730.1 | 868.4 | 723 | 647.4 | 694.4 | 615.2 | 733.4 | 731 | 155.9 | 282.2 | 336.9 | 652.8 | 567.6 | 544.2 | 580.4 | 582.5 | 295.9 | 423.9 | 405.1 | 356.5 | 355.6 | 489.5 | 361
1249 | 1013 | 566.3 | 226.52 | 264.7888 | 442.7 | 376.5 | 362.1 | 360.3 | 526.6 | 68.6 | 17.7 | 121.2 | 6 | 260.9 | 4.4 | 866.9 | 824.3 | 187.3 | 846.5 | 729.7 | 869.1 | 723.6 | 645.7 | 691.4 | 614.6 | 733.6 | 730.9 | 156.4 | 282.4 | 337 | 653.2 | 567.5 | 543.8 | 580.6 | 581.5 | 296.1 | 423.7 | 404.7 | 356.8 | 355.8 | 489.6 | 361.3
1250 | 1014 | 565 | 226 | 264.181 | 445.8 | 376.4 | 361.9 | 360.3 | 527.2 | 68.7 | 17.7 | 121.1 | 6.1 | 257.6 | 4.2 | 852.8 | 813.4 | 187 | 846.5 | 728.9 | 870 | 722.5 | 642.1 | 682.5 | 613.3 | 733.6 | 731.3 | 156.9 | 282.6 | 337.2 | 653.2 | 566.6 | 543 | 580.8 | 580.5 | 296.4 | 423.3 | 404.3 | 357.1 | 355.9 | 489.7 | 361.5
1251 | 1015 | 564.3 | 225.72 | 263.8537 | 447 | 376.7 | 362.3 | 359.3 | 526.7 | 68.7 | 17.7 | 121.1 | 6 | 253.4 | 3.9 | 840.5 | 803.7 | 188.1 | 846.2 | 728.1 | 869.7 | 721 | 637.6 | 674.4 | 611.6 | 733.4 | 730 | 157.5 | 282.9 | 337.3 | 653 | 565.6 | 540 | 581 | 579.1 | 296.6 | 422.4 | 403.9 | 357.3 | 356 | 489.8 | 361.7
1252 | 1016 | 566.5 | 226.6 | 264.8823 | 446.3 | 375.8 | 362.6 | 358.2 | 525.7 | 68.8 | 17.7 | 121.1 | 5.6 | 251 | 3.6 | 841.7 | 803.5 | 188.9 | 846 | 727.5 | 869.3 | 718.7 | 632.6 | 668.5 | 609.7 | 733.4 | 729.1 | 158 | 283.1 | 337.3 | 652.8 | 564.5 | 536.1 | 581.3 | 577.9 | 296.9 | 421.4 | 403.4 | 357.4 | 356.2 | 489.9 | 361.9
1253 | 1017 | 566 | 226.4 | 264.6486 | 444.5 | 374.9 | 362.9 | 357.5 | 523.8 | 68.9 | 17.7 | 121.2 | 5.8 | 248.8 | 3.5 | 839.1 | 798.4 | 189.2 | 846 | 727.2 | 869.1 | 718.2 | 629.7 | 668.1 | 609.5 | 733.6 | 728.6 | 158.5 | 283.3 | 337.5 | 653.1 | 563.7 | 535.2 | 581.7 | 577.8 | 297.1 | 420.2 | 402.6 | 357.6 | 356.3 | 490 | 362.1
1254 | 1018 | 566.7 | 226.68 | 264.9759 | 444.7 | 374.5 | 362.4 | 356.3 | 524.5 | 68.9 | 17.7 | 121.2 | 5.6 | 245.7 | 3.4 | 830.2 | 797.2 | 189.5 | 846.1 | 726.9 | 868.3 | 717.7 | 627 | 664.2 | 609.2 | 734 | 728.8 | 159.1 | 283.5 | 337.7 | 653.1 | 563.4 | 536.1 | 582 | 577.2 | 297.3 | 419.5 | 402.1 | 357.7 | 356.3 | 490.1 | 362.2
1255 | 1019 | 565.3 | 226.12 | 264.3213 | 448 | 374.1 | 362 | 355.8 | 525.9 | 68.9 | 17.7 | 121.2 | 6.1 | 238.6 | 3.4 | 834.7 | 809.1 | 190.1 | 846.9 | 727.1 | 867.8 | 716.6 | 625.2 | 666.8 | 608.8 | 734.2 | 729.2 | 159.6 | 283.8 | 337.8 | 652.8 | 563 | 533.5 | 582.8 | 577.5 | 297.5 | 419 | 402 | 357.8 | 356.4 | 490.2 | 362.4
1256 | 1020 | 564.4 | 225.76 | 263.9004 | 447.4 | 373.4 | 362.7 | 355.6 | 525.9 | 68.9 | 17.7 | 121.2 | 5.5 | 236 | 3.4 | 843.2 | 813 | 190 | 847.3 | 726.9 | 867.7 | 716.2 | 624.6 | 669.4 | 608.6 | 734.6 | 728.3 | 160.2 | 284 | 337.9 | 653 | 563.4 | 532.4 | 583.5 | 577.8 | 297.7 | 418.6 | 401.9 | 358 | 356.4 | 490.3 | 362.6
1257 | 1021 | 563.7 | 225.48 | 263.5731 | 444.3 | 373.3 | 362.7 | 355.7 | 526.2 | 68.9 | 17.7 | 121.1 | 5.7 | 244.1 | 3.3 | 846.6 | 817.3 | 188.9 | 847.1 | 726.9 | 867.9 | 717.1 | 624.7 | 671.2 | 608.8 | 734.8 | 728.1 | 160.7 | 284.3 | 338 | 653.5 | 563.5 | 534.5 | 583.9 | 578 | 297.9 | 418.3 | 401.7 | 358.2 | 356.4 | 490.4 | 362.8
1258 | 1022 | 564.1 | 225.64 | 263.7602 | 442.6 | 373.2 | 362.4 | 355.8 | 528.4 | 68.8 | 17.7 | 121 | 5.9 | 247 | 3.3 | 842.2 | 815.2 | 188.1 | 847.5 | 726.8 | 868.4 | 718.5 | 624.4 | 674.4 | 608.2 | 735.2 | 729 | 161.3 | 284.5 | 338.2 | 654 | 564 | 536.6 | 584.2 | 577.8 | 298.1 | 418.1 | 401.9 | 358.4 | 356.6 | 490.5 | 363
1259 | 1023 | 565 | 226 | 264.181 | 443 | 373 | 362 | 356 | 529.8 | 68.7 | 17.7 | 120.9 | 6.2 | 244.2 | 4 | 835.5 | 810.1 | 187.8 | 848.1 | 726.6 | 868.4 | 720.5 | 624.6 | 681.5 | 608.3 | 735.5 | 729.1 | 161.8 | 284.8 | 338.4 | 654.5 | 563.7 | 538.6 | 584.7 | 577 | 298.3 | 417.7 | 401.4 | 358.6 | 356.7 | 490.6 | 363.2
1260 | 1024 | 566.2 | 226.48 | 264.7421 | 443.4 | 373.3 | 361.9 | 356.4 | 533.8 | 68.7 | 17.7 | 120.8 | 5.9 | 239.1 | 4.1 | 840.9 | 814.5 | 187.5 | 849.1 | 726.2 | 868.9 | 720.6 | 623.5 | 680.5 | 608.2 | 735.9 | 729.3 | 162.4 | 285 | 338.8 | 654.8 | 564.2 | 542.2 | 585 | 576.8 | 298.5 | 417.4 | 400.8 | 358.7 | 356.7 | 490.7 | 363.4
1261 | 1025 | 565.3 | 226.12 | 264.3213 | 443.5 | 373.4 | 362.6 | 355.6 | 535.4 | 68.7 | 17.7 | 120.8 | 5.7 | 230.2 | 4.2 | 848.7 | 815 | 187.1 | 850.3 | 726.1 | 869.5 | 720.7 | 623.3 | 683.4 | 608.1 | 736.3 | 730.1 | 162.9 | 285.3 | 338.7 | 655.1 | 565.1 | 543 | 585.1 | 576.4 | 298.7 | 416.9 | 400.5 | 358.9 | 356.7 | 490.8 | 363.6
1262 | 1026 | 564.8 | 225.92 | 264.0875 | 442.9 | 374.7 | 363.7 | 355 | 538.1 | 68.6 | 17.7 | 120.8 | 5.3 | 230.9 | 4.7 | 850.2 | 811.1 | 186.4 | 851 | 725.9 | 870.2 | 719.8 | 624.1 | 683.6 | 608.8 | 736.6 | 729.9 | 163.6 | 285.5 | 338.8 | 655.1 | 566.4 | 542.9 | 585.5 | 577 | 298.9 | 416.8 | 400.2 | 359.1 | 356.8 | 490.9 | 363.7
1263 | 1027 | 566.3 | 226.52 | 264.7888 | 443.1 | 375.1 | 364.1 | 354.7 | 539.2 | 68.6 | 17.7 | 120.7 | 5.6 | 232.3 | 4.7 | 839.7 | 805.4 | 185.2 | 850.8 | 725.6 | 870.6 | 718.3 | 623.7 | 681.7 | 608.8 | 736.9 | 729.5 | 164.2 | 285.7 | 338.9 | 654.9 | 567.5 | 539.3 | 586 | 576.7 | 299.1 | 417 | 400.2 | 359.3 | 357.1 | 491 | 363.9
1264 | 1028 | 567.2 | 226.88 | 265.2096 | 443.4 | 374.8 | 363.1 | 355.4 | 536.3 | 68.6 | 17.7 | 120.7 | 5.4 | 232 | 4.3 | 832.4 | 801.8 | 184.7 | 849.7 | 724.9 | 871.2 | 716.4 | 622.5 | 675.3 | 607.5 | 737.1 | 728.4 | 164.9 | 285.9 | 339 | 654.9 | 566.9 | 535.4 | 586.3 | 575.5 | 299.3 | 417.5 | 400.3 | 359.6 | 357.2 | 491.1 | 364.1
1265 | 1029 | 565.5 | 226.2 | 264.4148 | 444.8 | 374.3 | 362.3 | 356.5 | 533.9 | 68.5 | 17.7 | 120.8 | 5.6 | 231.1 | 4 | 823.9 | 808.3 | 184.2 | 848.7 | 724.2 | 870.6 | 713.5 | 620.8 | 670.9 | 606.2 | 737 | 727 | 165.4 | 286.1 | 339.1 | 654.8 | 566.8 | 532.4 | 586.6 | 574.3 | 299.5 | 417.6 | 400.7 | 359.8 | 357.5 | 491.2 | 364.4
1266 | 1030 | 565.4 | 226.16 | 264.368 | 443.8 | 374 | 361.8 | 358.1 | 531 | 68.5 | 17.7 | 120.9 | 5.6 | 230.1 | 3.7 | 828.4 | 814.9 | 184.2 | 847.7 | 723.8 | 869.3 | 711.9 | 620.4 | 667.8 | 606 | 736.8 | 726.2 | 166.1 | 286.3 | 339.1 | 654.6 | 566.2 | 532.6 | 586.7 | 575 | 299.7 | 417.5 | 400.8 | 360.1 | 357.6 | 491.3 | 364.6
1267 | 1031 | 565.6 | 226.24 | 264.4615 | 442.1 | 373.9 | 361.1 | 359.6 | 527 | 68.4 | 17.7 | 121.2 | 6.3 | 229 | 3.4 | 839.2 | 819.8 | 184.9 | 847.1 | 723.3 | 870.2 | 710.8 | 619 | 664.6 | 605.8 | 736.7 | 725.3 | 166.7 | 286.5 | 339.2 | 654.5 | 565.5 | 530.8 | 586.8 | 574.7 | 299.9 | 417.8 | 400.9 | 360.3 | 357.6 | 491.4 | 364.8
1268 | 1032 | 565.9 | 226.36 | 264.6018 | 441.5 | 373.8 | 360.5 | 360.5 | 526 | 68.3 | 17.7 | 121.4 | 5.9 | 228.1 | 3.2 | 839.8 | 821.2 | 185.8 | 846.8 | 722.8 | 870.4 | 709.6 | 617.9 | 663.3 | 605.7 | 736.8 | 725.5 | 167.3 | 286.7 | 339.3 | 654.5 | 565.5 | 531.3 | 586.8 | 575.2 | 300.1 | 418.5 | 401.6 | 360.6 | 357.8 | 491.5 | 365
1269 | 1033 | 566.2 | 226.48 | 264.7421 | 440.8 | 373.6 | 360.2 | 361.3 | 524.4 | 68.2 | 17.7 | 121.6 | 5.9 | 233.9 | 3.4 | 842.7 | 820.6 | 185.4 | 846.2 | 722.4 | 869.8 | 708.1 | 617.5 | 659.8 | 605.6 | 737 | 724 | 167.9 | 286.9 | 339.4 | 654.3 | 564.2 | 528.2 | 586.9 | 575.5 | 300.4 | 418.9 | 402.1 | 360.9 | 358 | 491.6 | 365.3
1270 | 1034 | 565.7 | 226.28 | 264.5083 | 440.4 | 373.8 | 360.3 | 362.7 | 524 | 68.3 | 17.7 | 121.7 | 6.3 | 248.6 | 3.9 | 844.9 | 821.7 | 186.6 | 846 | 722.2 | 870.1 | 708.4 | 618.1 | 666.1 | 606 | 737.1 | 723.5 | 168.5 | 287.1 | 339.6 | 654.4 | 563.4 | 528.6 | 587.2 | 576.1 | 300.6 | 418.9 | 401.4 | 361.2 | 358.1 | 491.7 | 365.5
1271 | 1035 | 566.4 | 226.56 | 264.8356 | 442.5 | 375.4 | 360.4 | 363.1 | 524.2 | 68.4 | 17.7 | 121.8 | 5.5 | 242 | 3.9 | 852.6 | 827.8 | 187.5 | 846.5 | 722.2 | 870.9 | 708.7 | 617.7 | 667.2 | 605.8 | 737.3 | 723.3 | 169.1 | 287.3 | 339.6 | 654.4 | 562.8 | 531.8 | 587.8 | 576.3 | 300.8 | 419 | 401.1 | 361.4 | 358.1 | 491.8 | 365.7
1272 | 1036 | 566.8 | 226.72 | 265.0226 | 444.9 | 375.7 | 360 | 361.9 | 525.9 | 68.4 | 17.6 | 122 | 6 | 226.9 | 3.9 | 849.2 | 826.4 | 187.9 | 847.7 | 721.9 | 871 | 708.7 | 616.7 | 667.5 | 605.4 | 737.3 | 722.2 | 169.6 | 287.3 | 339.8 | 654.5 | 563.1 | 530.9 | 588.6 | 575.6 | 301 | 418.7 | 400.6 | 361.6 | 358.1 | 491.9 | 365.9
1273 | 1037 | 566.2 | 226.48 | 264.7421 | 444.5 | 375.5 | 359.8 | 360.8 | 528 | 68.4 | 17.6 | 122.2 | 6 | 210.8 | 3.5 | 850.8 | 831.1 | 189.1 | 848.5 | 721.9 | 870.3 | 708.6 | 616.8 | 674.2 | 605.8 | 737.1 | 722.4 | 170 | 287.4 | 339.9 | 654.3 | 563.4 | 531.9 | 589.2 | 576.4 | 301.3 | 418.8 | 400.9 | 361.8 | 358.2 | 492 | 366
1274 | 1038 | 565.1 | 226.04 | 264.2277 | 442.9 | 375.5 | 360.3 | 360.3 | 529.3 | 68.5 | 17.6 | 122.3 | 5.8 | 215.2 | 3.5 | 849.7 | 833 | 189.7 | 849.1 | 721.9 | 869.1 | 705.9 | 616.6 | 669 | 605.7 | 736.6 | 719.9 | 170.4 | 287.5 | 340 | 654.3 | 564.3 | 531.3 | 589.8 | 577.1 | 301.5 | 419.4 | 401 | 362.1 | 358.4 | 492.1 | 366.3
1275 | 1039 | 565.1 | 226.04 | 264.2277 | 440.7 | 376.2 | 360 | 360.6 | 526.2 | 68.6 | 17.6 | 122.4 | 6.6 | 214.1 | 3.5 | 848.3 | 835.7 | 190.1 | 849.4 | 722.1 | 867.8 | 703.5 | 616.3 | 666 | 605.5 | 735.8 | 718.1 | 171 | 287.7 | 340.1 | 654.2 | 564.6 | 530.3 | 590.1 | 577.3 | 301.7 | 419.5 | 401.8 | 362.3 | 358.7 | 492.3 | 366.5
1276 | 1040 | 565 | 226 | 264.181 | 439.7 | 376.6 | 359.9 | 361.8 | 522.5 | 68.7 | 17.6 | 122.5 | 6.4 | 192.6 | 3.6 | 841.3 | 836.1 | 189.9 | 849.6 | 722.1 | 865.4 | 701.4 | 615.9 | 661.8 | 605.5 | 735.2 | 717.1 | 171.5 | 287.9 | 340.3 | 654.1 | 565.2 | 529.7 | 590.4 | 577.6 | 301.9 | 419.6 | 403 | 362.5 | 359.1 | 492.4 | 366.7
1277 | 1041 | 565.2 | 226.08 | 264.2745 | 438.8 | 376.9 | 360.2 | 362.7 | 520.4 | 68.8 | 17.6 | 122.6 | 6.5 | 196.4 | 3.9 | 841.5 | 839.5 | 189.8 | 849.3 | 722.1 | 863 | 698.6 | 615 | 656.5 | 604.9 | 734.9 | 714.6 | 171.9 | 288.1 | 340.4 | 653.9 | 565.3 | 528.5 | 590.7 | 578.3 | 302.2 | 420.1 | 404.3 | 362.8 | 359.4 | 492.6 | 366.9
1278 | 1042 | 564.8 | 225.92 | 264.0875 | 437.3 | 376.4 | 360.6 | 363 | 516.7 | 68.9 | 17.6 | 122.7 | 6.2 | 239.4 | 3.5 | 853.5 | 844.7 | 189.8 | 849.6 | 722 | 863 | 697.8 | 614.2 | 659.3 | 604.3 | 734.9 | 713.5 | 172 | 288.1 | 340.5 | 653.6 | 564.6 | 528 | 590.8 | 576.7 | 302.4 | 420.4 | 405.4 | 363.1 | 359.7 | 492.8 | 367.2
1279 | 1043 | 565.5 | 226.2 | 264.4148 | 435.7 | 375.8 | 361.4 | 363.9 | 516.9 | 69 | 17.6 | 122.8 | 6.5 | 260.2 | 3.4 | 860.2 | 847.2 | 190.3 | 850.2 | 722.1 | 863 | 698.2 | 615.1 | 663.6 | 604.8 | 734.6 | 713.9 | 172.2 | 288.1 | 340.5 | 653.3 | 564.8 | 528.9 | 591 | 577.4 | 302.6 | 420.5 | 406.4 | 363.4 | 359.9 | 492.9 | 367.4
1280 | 1044 | 565 | 226 | 264.181 | 433.9 | 375.3 | 361.5 | 364.6 | 518 | 69.1 | 17.6 | 122.9 | 5.9 | 241.6 | 3.2 | 866.7 | 847.5 | 190.9 | 851 | 722.2 | 863.2 | 700.4 | 617 | 674.3 | 604.9 | 733.9 | 714.2 | 172.5 | 288.2 | 340.6 | 653.5 | 565.1 | 532.2 | 591.1 | 577.4 | 302.9 | 420.9 | 406.1 | 363.6 | 360.1 | 493.1 | 367.6
1281 | 1045 | 564 | 225.6 | 263.7134 | 433.2 | 375.5 | 361 | 364.9 | 520.2 | 69.1 | 17.6 | 122.9 | 6 | 226.9 | 3.5 | 868.1 | 849.2 | 190.3 | 851.8 | 722.1 | 863.1 | 702 | 619.5 | 678.2 | 605.5 | 733.4 | 714.7 | 172.8 | 288.2 | 340.7 | 653.5 | 565.5 | 534.5 | 591.2 | 577.9 | 303.1 | 421.1 | 406.2 | 363.9 | 360.3 | 493.2 | 367.9
1282 | 1046 | 565 | 226 | 264.181 | 432.6 | 376.3 | 360.5 | 365 | 519.3 | 69.1 | 17.6 | 122.9 | 6 | 208.9 | 4 | 867.4 | 852.4 | 190.1 | 852.8 | 722.6 | 863.4 | 703.7 | 621.6 | 684.2 | 606.1 | 733.2 | 715.2 | 173 | 288.3 | 340.9 | 653.5 | 565.4 | 534.2 | 591.4 | 578 | 303.3 | 421.6 | 406.6 | 364.2 | 360.5 | 493.3 | 368.1
1283 | 1047 | 566.7 | 226.68 | 264.9759 | 431.7 | 377 | 360.6 | 365.1 | 519.7 | 69.2 | 17.6 | 122.9 | 6.4 | 202.6 | 4 | 869.9 | 853.6 | 189.8 | 853.6 | 723 | 863.9 | 705.6 | 623.7 | 691.5 | 606.5 | 733.1 | 715.8 | 173.2 | 288.5 | 341 | 653.6 | 565.3 | 536.8 | 591.7 | 579.6 | 303.6 | 421.8 | 406.5 | 364.5 | 360.7 | 493.5 | 368.3
1284 | 1048 | 566.7 | 226.68 | 264.9759 | 432.1 | 377.8 | 360.3 | 365.2 | 520.4 | 69.2 | 17.6 | 123 | 6.5 | 223.1 | 3.9 | 868.6 | 849.2 | 189.9 | 854 | 722.6 | 864.3 | 705.8 | 624.2 | 685.4 | 606.1 | 733.3 | 716.2 | 173.5 | 288.7 | 341.1 | 653.6 | 564.8 | 535.7 | 592 | 578.3 | 303.8 | 421.8 | 406.4 | 364.8 | 361 | 493.6 | 368.5
1285 | 1049 | 566.7 | 226.68 | 264.9759 | 431.8 | 377.9 | 360.4 | 364.8 | 522.5 | 69.3 | 17.6 | 123 | 5.9 | 231.4 | 4.1 | 859.6 | 841.9 | 190.6 | 854.5 | 721.9 | 864.6 | 705.9 | 623.7 | 683.3 | 605.4 | 733.8 | 715.5 | 174 | 288.8 | 341.2 | 653.9 | 564.6 | 538.8 | 592.5 | 577.1 | 304.1 | 421.8 | 406.2 | 365.1 | 361.2 | 493.7 | 368.7
1286 | 1050 | 567 | 226.8 | 265.1161 | 432.1 | 377.8 | 360.6 | 364.1 | 525 | 69.3 | 17.6 | 123 | 6.3 | 209 | 4.5 | 854.3 | 838 | 191 | 855.2 | 721.4 | 864.9 | 705.8 | 622.7 | 683.3 | 604.7 | 734 | 714.7 | 174.5 | 289.1 | 341.3 | 653.9 | 564.8 | 537.6 | 593.1 | 575.9 | 304.3 | 421.5 | 406.1 | 365.4 | 361.4 | 493.8 | 369
1287 | 1051 | 567.2 | 226.88 | 265.2096 | 433 | 377.4 | 360.8 | 363.5 | 524.8 | 69.3 | 17.6 | 123 | 6.6 | 196.8 | 4.7 | 858.4 | 838 | 191.4 | 855.5 | 720.8 | 866 | 706.3 | 622.2 | 682.9 | 604.1 | 734.2 | 715.8 | 175 | 289.3 | 341.3 | 653.9 | 564.6 | 536.2 | 593.4 | 574.8 | 304.6 | 421.1 | 406.3 | 365.6 | 361.7 | 493.9 | 369.2
1288 | 1052 | 567.3 | 226.92 | 265.2564 | 434.1 | 377.4 | 360.6 | 363.4 | 523.9 | 69.2 | 17.6 | 122.9 | 5.9 | 206.3 | 4.9 | 853.9 | 833.2 | 190.5 | 854.8 | 720.4 | 865.8 | 705.2 | 622.2 | 681.5 | 604.1 | 734.2 | 714.8 | 175.8 | 289.5 | 341.4 | 653.9 | 564.7 | 536.3 | 593.7 | 575.7 | 304.8 | 421.5 | 406.7 | 365.9 | 361.9 | 493.9 | 369.4
1289 | 1053 | 566.6 | 226.64 | 264.9291 | 434.8 | 377.6 | 359.8 | 363.5 | 523.9 | 69.2 | 17.6 | 122.9 | 6.4 | 206.4 | 5.6 | 851.9 | 830.9 | 190.1 | 853.5 | 719.8 | 863.8 | 702.6 | 621.3 | 676.1 | 603.9 | 734.5 | 712.7 | 176.4 | 289.8 | 341.6 | 653.7 | 565.6 | 533.2 | 593.9 | 575.8 | 305.1 | 422.4 | 407.4 | 366.2 | 362.2 | 494 | 369.6
1290 | 1054 | 566.3 | 226.52 | 264.7888 | 433.3 | 378.1 | 359.3 | 364.5 | 520.8 | 69.2 | 17.6 | 123 | 6.2 | 212.8 | 6 | 857.7 | 835 | 190.4 | 852.5 | 719.4 | 862.1 | 701 | 620.5 | 674.5 | 603.2 | 734.5 | 711.3 | 176.9 | 290 | 341.7 | 653.4 | 566.3 | 529.7 | 594.1 | 576.6 | 305.3 | 423.5 | 407.9 | 366.6 | 362.4 | 494.1 | 369.8
1291 | 1055 | 565.3 | 226.12 | 264.3213 | 432.5 | 378.3 | 359.2 | 365.5 | 518 | 69.2 | 17.6 | 123 | 5.5 | 220.4 | 5.3 | 861.8 | 840.9 | 190.8 | 851.9 | 719.2 | 860.8 | 699.1 | 619.4 | 672.4 | 603.1 | 734.2 | 709.8 | 177.2 | 290.2 | 341.8 | 653.3 | 566.1 | 526.8 | 594.3 | 576.2 | 305.6 | 425 | 408.2 | 366.9 | 362.6 | 494.3 | 370.1
1292 | 1056 | 565.9 | 226.36 | 264.6018 | 432.1 | 377.9 | 359.7 | 366.5 | 517.9 | 69.2 | 17.6 | 123 | 5.5 | 240.8 | 4.7 | 860.7 | 847 | 191.3 | 851.6 | 719.3 | 860.8 | 698.4 | 619.7 | 671.8 | 603.7 | 733.9 | 709.2 | 177.5 | 290.5 | 341.9 | 653.3 | 565.9 | 526.1 | 594.4 | 576.3 | 305.9 | 426.3 | 408.5 | 367.3 | 362.8 | 494.5 | 370.4
1293 | 1057 | 564.7 | 225.88 | 264.0407 | 431.7 | 377.8 | 359.9 | 367.2 | 519.8 | 69.2 | 17.6 | 123 | 6.2 | 253 | 4.3 | 855.8 | 840.6 | 191.7 | 850.7 | 719.3 | 860.6 | 697.5 | 619.6 | 668 | 604.5 | 733.8 | 708.4 | 177.8 | 290.7 | 342 | 653.5 | 566.5 | 527.9 | 594.7 | 578.6 | 306.1 | 427.3 | 408.9 | 367.6 | 363.1 | 494.6 | 370.7
1294 | 1058 | 565.5 | 226.2 | 264.4148 | 431.3 | 377.5 | 359.2 | 367.7 | 520.4 | 69.3 | 17.6 | 122.9 | 6.5 | 220.5 | 4 | 851.8 | 838.2 | 192.1 | 849.6 | 719.6 | 859.5 | 695.1 | 618 | 662.4 | 604.3 | 733.7 | 707.2 | 178.3 | 290.9 | 342.1 | 653.3 | 566.8 | 525.8 | 594.8 | 579.2 | 306.4 | 427.7 | 409 | 368 | 363.4 | 494.8 | 370.9
1295 | 1059 | 565.3 | 226.12 | 264.3213 | 430.4 | 376.9 | 358.9 | 368.1 | 519.3 | 69.2 | 17.6 | 122.8 | 6 | 184.2 | 4.2 | 855.8 | 840.8 | 192.4 | 849.2 | 720 | 858.9 | 694.9 | 617.7 | 668.8 | 604.6 | 733.7 | 707.4 | 178.6 | 291.2 | 342.2 | 653.3 | 566.6 | 527.1 | 594.9 | 578.7 | 306.6 | 428.1 | 408.6 | 368.4 | 363.5 | 494.9 | 371.2
1296 | 1060 | 566.1 | 226.44 | 264.6953 | 429.4 | 376.4 | 359 | 368.2 | 519.7 | 69.2 | 17.6 | 122.7 | 5.6 | 201.4 | 4.7 | 855.9 | 845.5 | 193 | 849.6 | 720.5 | 859.3 | 697.1 | 619.1 | 677.4 | 605.5 | 733.6 | 709.7 | 178.9 | 291.4 | 342.3 | 653.3 | 567.1 | 529.2 | 595 | 578.8 | 306.9 | 428.3 | 408.4 | 368.7 | 363.6 | 495.1 | 371.4
1297 | 1061 | 566.3 | 226.52 | 264.7888 | 429.2 | 376.4 | 359 | 367.5 | 521.4 | 69.2 | 17.6 | 122.6 | 5.3 | 219.2 | 5.1 | 862.5 | 847.6 | 193 | 850.1 | 720.9 | 859.5 | 699.3 | 621.1 | 684.2 | 606.3 | 733.5 | 711.4 | 179.2 | 291.7 | 342.4 | 653.3 | 567.2 | 531.9 | 595.2 | 578.8 | 307.2 | 428 | 408 | 369 | 363.8 | 495.3 | 371.7
1298 | 1062 | 567.5 | 227 | 265.3499 | 428.4 | 376.5 | 358.8 | 366.3 | 523.2 | 69.2 | 17.6 | 122.5 | 5.6 | 228 | 5 | 863.1 | 845.6 | 192.9 | 850.6 | 721.3 | 859.6 | 702.1 | 624.1 | 691.8 | 607.5 | 733 | 711.6 | 179.4 | 291.9 | 342.5 | 653.3 | 567.3 | 534.8 | 595.4 | 580 | 307.5 | 428 | 408.2 | 369.3 | 364 | 495.4 | 371.9
1299 | 1063 | 569 | 227.6 | 266.0513 | 428.3 | 377.7 | 358.5 | 365.2 | 526.5 | 69.2 | 17.6 | 122.4 | 5.3 | 227.6 | 4.4 | 864.4 | 844.6 | 193.1 | 851 | 721.8 | 859.7 | 703 | 625.2 | 691.3 | 607.5 | 732.8 | 711.4 | 179.7 | 292.1 | 342.7 | 653.2 | 567.7 | 534.9 | 595.7 | 579.8 | 307.7 | 428.2 | 408.3 | 369.7 | 364.1 | 495.5 | 372.1
1300 | 1064 | 566.5 | 226.6 | 264.8823 | 427.8 | 378.8 | 358.5 | 365.9 | 528.7 | 69.1 | 17.6 | 122.4 | 5.9 | 226.7 | 4.6 | 864.3 | 845.1 | 192.6 | 851.1 | 722.3 | 860.4 | 706.8 | 627.6 | 700.8 | 607.8 | 733.1 | 713.1 | 179.9 | 292.3 | 342.9 | 653.5 | 568.1 | 538.2 | 596 | 578.6 | 308 | 428.6 | 408.2 | 370 | 364.1 | 495.7 | 372.3
1301 | 1065 | 565 | 226 | 264.181 | 426.7 | 378.5 | 358.8 | 365.9 | 532.1 | 69.1 | 17.6 | 122.4 | 5.9 | 240.9 | 4.5 | 865.1 | 840.4 | 192.3 | 851.9 | 722.6 | 861.7 | 710.1 | 629.2 | 704.7 | 607.9 | 733.1 | 714.9 | 180.2 | 292.5 | 343.1 | 653.7 | 568.3 | 541.5 | 596.3 | 577.9 | 308.3 | 428.2 | 407.5 | 370.2 | 364.2 | 495.8 | 372.5
1302 | 1066 | 566.5 | 226.6 | 264.8823 | 426.8 | 378.5 | 359.8 | 365.6 | 533.8 | 69.1 | 17.6 | 122.4 | 6.4 | 238.6 | 4.4 | 860.6 | 842.5 | 192.7 | 853.2 | 723 | 862.9 | 714.1 | 631.2 | 714.5 | 607.9 | 733.2 | 716.9 | 180.6 | 292.7 | 343.2 | 653.8 | 568.2 | 542.2 | 596.7 | 577.1 | 308.5 | 428 | 406.7 | 370.5 | 364.2 | 495.9 | 372.7
1303 | 1067 | 567.5 | 227 | 265.3499 | 427.1 | 378.7 | 360.3 | 364.2 | 535.6 | 69.1 | 17.6 | 122.3 | 6.2 | 232.2 | 4.4 | 858.2 | 848.2 | 193.8 | 853.9 | 723.6 | 863 | 719.1 | 634.2 | 726.2 | 608.6 | 733.1 | 718.5 | 181 | 292.8 | 343.3 | 654.2 | 568.6 | 548.1 | 597.1 | 578.1 | 308.8 | 427.1 | 406.1 | 370.6 | 364.2 | 496 | 372.9
1304 | 1068 | 568.4 | 227.36 | 265.7707 | 426.1 | 378.9 | 360.2 | 362.6 | 537 | 69 | 17.6 | 122.2 | 6 | 229.9 | 4.3 | 859.7 | 849.2 | 194.5 | 854.9 | 724.2 | 863.1 | 723 | 638.3 | 734.8 | 609.5 | 732.9 | 720.8 | 181.4 | 293 | 343.4 | 654.4 | 569 | 549.3 | 597.9 | 579.1 | 309.1 | 426.2 | 406.2 | 370.8 | 364.2 | 496.1 | 373.1
1305 | 1069 | 566.9 | 226.76 | 265.0694 | 425.8 | 378.8 | 360.5 | 361.9 | 536.8 | 68.8 | 17.6 | 122.1 | 5.8 | 234.8 | 4.1 | 864.3 | 850.5 | 194.6 | 855.2 | 724.5 | 864.2 | 725.8 | 640.9 | 737 | 609.7 | 733 | 722.2 | 181.8 | 293.2 | 343.5 | 654.5 | 568.6 | 550.4 | 598.4 | 579.8 | 309.3 | 425.9 | 406.3 | 371 | 364.2 | 496.2 | 373.2
1306 | 1070 | 566.7 | 226.68 | 264.9759 | 425.7 | 378.9 | 360.1 | 361.2 | 536.4 | 68.7 | 17.6 | 122.1 | 5.7 | 237.5 | 3.9 | 865.6 | 850.8 | 195.9 | 854.6 | 724.9 | 864.5 | 728.9 | 642.1 | 742.4 | 610 | 733.3 | 721.9 | 182.3 | 293.4 | 343.8 | 654.8 | 569.1 | 554.9 | 598.7 | 579.4 | 309.6 | 425.7 | 405.5 | 371.2 | 364.1 | 496.3 | 373.4
1307 | 1071 | 566 | 226.4 | 264.6486 | 425.3 | 380.3 | 359.8 | 360.6 | 540.7 | 68.6 | 17.6 | 122 | 6 | 202.8 | 3.8 | 872 | 854.6 | 196.7 | 853.9 | 725.1 | 864.8 | 730.6 | 642.8 | 742.8 | 611 | 733.8 | 722.7 | 182.6 | 293.5 | 344.1 | 655.5 | 569.7 | 564 | 599.2 | 580.7 | 309.8 | 425.1 | 404.5 | 371.4 | 364.1 | 496.4 | 373.6
1308 | 1072 | 567.1 | 226.84 | 265.1629 | 424.9 | 381.4 | 360.2 | 360 | 542 | 68.6 | 17.6 | 121.9 | 5.9 | 196.2 | 3.9 | 873.4 | 850.5 | 196.5 | 855.6 | 725 | 865.4 | 731.5 | 644 | 739.4 | 611.2 | 734.1 | 724.2 | 183 | 293.7 | 344.1 | 655.6 | 569.8 | 566 | 599.3 | 580.3 | 310 | 424.3 | 403.5 | 371.5 | 364 | 496.5 | 373.8
1309 | 1073 | 566.5 | 226.6 | 264.8823 | 425.3 | 381.1 | 359.9 | 359.4 | 543.3 | 68.6 | 17.6 | 121.8 | 6 | 243.9 | 3.6 | 874.3 | 845.3 | 196.7 | 858.3 | 724.8 | 865.6 | 730.2 | 644.3 | 731.4 | 610.8 | 734.3 | 724.6 | 183.3 | 293.8 | 344.1 | 655.5 | 570.7 | 562.6 | 599.6 | 580 | 310.3 | 423.9 | 403 | 371.7 | 364.1 | 496.6 | 373.9
1310 | 1074 | 567.9 | 227.16 | 265.537 | 425.1 | 382 | 359.5 | 359.4 | 542.2 | 68.6 | 17.6 | 121.6 | 5.7 | 237.1 | 3.6 | 875.9 | 850.3 | 197.3 | 858.6 | 725 | 866 | 729.8 | 644.6 | 729.6 | 611.1 | 734.5 | 724.7 | 183.6 | 294 | 344.3 | 656 | 570.9 | 563.4 | 599.8 | 579.8 | 310.5 | 423.5 | 402.2 | 371.9 | 364.1 | 496.7 | 374.1
1311 | 1075 | 566.5 | 226.6 | 264.8823 | 423.7 | 382.8 | 358.6 | 359.7 | 542.5 | 68.6 | 17.6 | 121.5 | 5.8 | 212.5 | 4.4 | 875.5 | 853.6 | 197.8 | 858.1 | 725.3 | 866.6 | 731.8 | 646.6 | 736.9 | 612.2 | 734.7 | 726.4 | 183.9 | 294.1 | 344.5 | 656.6 | 570.9 | 569.7 | 599.8 | 580.8 | 310.7 | 423.1 | 401.3 | 372.1 | 363.9 | 496.8 | 374.3
1312 | 1076 | 565.7 | 226.28 | 264.5083 | 422.2 | 383.5 | 358.3 | 359.8 | 543.4 | 68.6 | 17.6 | 121.4 | 6 | 216.3 | 5.3 | 877.3 | 852.7 | 197.9 | 859.4 | 725.3 | 867.2 | 732.5 | 646.5 | 733.3 | 611.2 | 734.8 | 726.9 | 184.3 | 294.3 | 344.7 | 656.5 | 570.6 | 570.4 | 599.8 | 580.3 | 310.9 | 422.9 | 400.9 | 372.3 | 363.9 | 496.9 | 374.5
1313 | 1077 | 564.4 | 225.76 | 263.9004 | 421.9 | 385.2 | 358.3 | 359.1 | 540.9 | 68.7 | 17.6 | 121.4 | 6.2 | 228.8 | 5.3 | 872.2 | 848.1 | 197.9 | 861.3 | 725.1 | 867.9 | 730.6 | 644.1 | 725.7 | 609.7 | 735.4 | 728.5 | 184.6 | 294.4 | 344.6 | 656.2 | 569.5 | 566 | 600 | 578.3 | 311.2 | 422.6 | 400.6 | 372.4 | 364 | 497 | 374.6
1314 | 1078 | 565.4 | 226.16 | 264.368 | 421.5 | 385 | 358.7 | 358.5 | 539 | 68.7 | 17.6 | 121.4 | 5.5 | 236.7 | 5.2 | 874 | 845 | 197.5 | 860.5 | 724.8 | 869 | 727.8 | 642.2 | 713.4 | 608.8 | 735.7 | 728.1 | 184.9 | 294.5 | 344.6 | 655.7 | 569 | 558.9 | 600.9 | 577 | 311.4 | 422.2 | 400.3 | 372.6 | 364 | 497.1 | 374.8
1315 | 1079 | 565 | 226 | 264.181 | 420.2 | 383.8 | 358.2 | 359.4 | 537 | 68.8 | 17.6 | 121.4 | 5.5 | 206.6 | 5.1 | 869.8 | 840.7 | 196.9 | 859.8 | 724.4 | 869.6 | 725.7 | 639.6 | 705.4 | 607.9 | 736.2 | 727.2 | 185.1 | 294.7 | 344.8 | 655.8 | 568.5 | 555.3 | 601.5 | 576.2 | 311.6 | 421.6 | 399.6 | 372.8 | 363.9 | 497.1 | 375
1316 | 1080 | 566.2 | 226.48 | 264.7421 | 418.8 | 383.1 | 358.4 | 360.7 | 540.1 | 68.9 | 17.6 | 121.5 | 5.5 | 210.6 | 4.6 | 864.7 | 841.2 | 196.3 | 862.5 | 722.8 | 868.7 | 726.5 | 637.3 | 704.9 | 607.1 | 736.1 | 726.4 | 185.3 | 294.7 | 345.4 | 656.8 | 568 | 554.5 | 603.6 | 575.2 | 311.5 | 421.3 | 400 | 372.8 | 363.6 | 496.3 | 375
1317 | 1081 | 566.6 | 226.64 | 264.9291 | 421.1 | 381.3 | 356.7 | 360.8 | 540.4 | 68.9 | 17.6 | 121.5 | 5.6 | 254.2 | 3.9 | 864.5 | 840.7 | 196.9 | 859.2 | 723.9 | 870.2 | 724.2 | 634.7 | 700 | 606.7 | 736.5 | 726.8 | 185.8 | 294.8 | 345 | 655.9 | 569.8 | 553.6 | 602.9 | 576.2 | 312.1 | 421 | 399 | 373.2 | 364.1 | 497.3 | 375.3
1318 | 1082 | 565.6 | 226.24 | 264.4615 | 421.6 | 380.9 | 356 | 361.6 | 540.8 | 69 | 17.6 | 121.5 | 6 | 262.5 | 3.9 | 862.3 | 841.3 | 197.3 | 859.1 | 723.8 | 869.7 | 722.6 | 633.9 | 697.7 | 607.6 | 736.6 | 726.5 | 186.1 | 294.9 | 345.1 | 656 | 570.8 | 552.8 | 603.1 | 577.2 | 312.3 | 420.9 | 399.2 | 373.4 | 364.2 | 497.4 | 375.5
1319 | 1083 | 566.5 | 226.6 | 264.8823 | 421.3 | 380.8 | 355.9 | 362.5 | 538.3 | 69 | 17.6 | 121.6 | 5.8 | 216.6 | 4.5 | 860.1 | 836.4 | 197.8 | 858 | 723.5 | 869.8 | 719.2 | 632 | 688.2 | 607.5 | 736.9 | 724.2 | 186.4 | 295 | 345.2 | 655.9 | 571.2 | 549.7 | 603.3 | 577.9 | 312.5 | 420.8 | 399.9 | 373.7 | 364.4 | 497.4 | 375.7
1320 | 1084 | 565.3 | 226.12 | 264.3213 | 420.9 | 381.7 | 355.9 | 363.5 | 535.3 | 69.1 | 17.6 | 121.6 | 6 | 226.4 | 4.8 | 859.9 | 833.5 | 197.3 | 856.6 | 723.2 | 869.6 | 716.5 | 630.5 | 684.4 | 606.2 | 736.7 | 722.1 | 186.8 | 295.1 | 345.3 | 655.5 | 570.7 | 546.9 | 603.5 | 578.5 | 312.8 | 421.2 | 400.6 | 373.9 | 364.6 | 497.5 | 375.9
1321 | 1085 | 567.4 | 226.96 | 265.3032 | 420.3 | 381.2 | 355.8 | 363.9 | 531.4 | 69.1 | 17.6 | 121.7 | 6.4 | 243.3 | 5.1 | 863.6 | 834.3 | 197.3 | 855.8 | 723.1 | 868.8 | 720.4 | 630.7 | 696.1 | 606.2 | 736.4 | 723.3 | 187.1 | 295.3 | 345.4 | 655.7 | 569.6 | 547.3 | 603.6 | 577.9 | 313.1 | 421.3 | 400.3 | 374.1 | 364.5 | 497.6 | 376.1
1322 | 1086 | 567.8 | 227.12 | 265.4902 | 419.8 | 380.8 | 356 | 363.9 | 533.2 | 69.2 | 17.6 | 121.7 | 6.1 | 243.3 | 5.5 | 862.4 | 839.4 | 198.2 | 855.3 | 723.1 | 868.1 | 724.2 | 630.4 | 703.5 | 606.7 | 736.4 | 723.2 | 187.4 | 295.5 | 345.9 | 656.3 | 568.7 | 553.6 | 603.8 | 577.4 | 313.3 | 421.1 | 399.6 | 374.3 | 364.4 | 497.7 | 376.3
1323 | 1087 | 565.8 | 226.32 | 264.555 | 420.2 | 380 | 357 | 363.3 | 538.3 | 69.3 | 17.6 | 121.8 | 5.7 | 244.8 | 5.4 | 862.1 | 843.8 | 198.7 | 855.6 | 723.4 | 867.3 | 727.6 | 632.3 | 714.8 | 607.8 | 736.5 | 724.1 | 187.7 | 295.6 | 346.2 | 656.9 | 567.8 | 563.1 | 604.1 | 577.7 | 313.5 | 420.8 | 399.3 | 374.4 | 364.4 | 497.8 | 376.4
1324 | 1088 | 566.3 | 226.52 | 264.7888 | 420.4 | 379.3 | 358.7 | 361.6 | 538.8 | 69.4 | 17.6 | 121.9 | 5.5 | 244.1 | 5.5 | 863.3 | 850.2 | 199.2 | 856.3 | 723.7 | 867 | 731 | 635.2 | 725.1 | 608.9 | 735.9 | 726.9 | 187.9 | 295.8 | 346.2 | 657.1 | 567.5 | 564.3 | 604.3 | 578.7 | 313.8 | 420.1 | 399.5 | 374.4 | 364.6 | 497.9 | 376.6
1325 | 1089 | 565.7 | 226.28 | 264.5083 | 421.2 | 379.5 | 358.9 | 360.2 | 539.2 | 69.4 | 17.6 | 121.9 | 6 | 244.1 | 5.5 | 868.3 | 852.5 | 198.3 | 858 | 724.2 | 866.2 | 731.3 | 638.3 | 722 | 609.8 | 735.1 | 728.9 | 188.2 | 296 | 346.2 | 656.5 | 568.5 | 560.7 | 604.7 | 580.4 | 314 | 419.9 | 399.6 | 374.6 | 364.7 | 497.9 | 376.8
1326 | 1090 | 566.7 | 226.68 | 264.9759 | 420.5 | 380 | 358.3 | 360.6 | 533.8 | 69.5 | 17.6 | 121.9 | 6.3 | 225.9 | 4.9 | 871.9 | 851.7 | 198.2 | 860.5 | 724.6 | 866.4 | 732.1 | 641.2 | 726.9 | 610.1 | 734.1 | 731.4 | 188.5 | 296.1 | 346.2 | 656.4 | 568.3 | 557.5 | 605.2 | 580.6 | 314.2 | 419.9 | 398.8 | 374.8 | 364.6 | 498.1 | 376.9
1327 | 1091 | 566.4 | 226.56 | 264.8356 | 420.2 | 380.6 | 357.5 | 361.7 | 530.3 | 69.5 | 17.5 | 121.9 | 6.5 | 230.5 | 4.3 | 873.3 | 851.6 | 198.9 | 862.9 | 724.7 | 866.8 | 731.5 | 642.7 | 724.4 | 610.2 | 733.7 | 731.6 | 188.8 | 296.2 | 346.3 | 656.3 | 568 | 558.4 | 605.4 | 580.9 | 314.4 | 420 | 398.8 | 375 | 364.6 | 498.2 | 377.1
1328 | 1092 | 567 | 226.8 | 265.1161 | 420.5 | 380.8 | 356.5 | 361.6 | 528.8 | 69.5 | 17.5 | 121.9 | 5.9 | 243.2 | 4.4 | 862.4 | 843.4 | 198.6 | 862.6 | 724.7 | 866.8 | 728.8 | 642.5 | 714.2 | 609.8 | 733.8 | 730.1 | 189.1 | 296.3 | 346.3 | 656 | 567.5 | 555.7 | 605.7 | 581 | 314.7 | 420.4 | 399.1 | 375.2 | 364.9 | 498.3 | 377.3
1329 | 1093 | 566.8 | 226.72 | 265.0226 | 420.2 | 380.7 | 356.1 | 362.1 | 528.8 | 69.5 | 17.5 | 121.8 | 5.6 | 246.5 | 4.7 | 849.6 | 833.3 | 197.7 | 859.6 | 724.4 | 864.7 | 724.9 | 640.8 | 698.4 | 609.1 | 734.1 | 727.8 | 189.3 | 296.4 | 346.5 | 655.8 | 568.1 | 551.1 | 606 | 579.8 | 314.9 | 421.2 | 399.9 | 375.5 | 365 | 498.4 | 377.5
1330 | 1094 | 565.5 | 226.2 | 264.4148 | 420 | 380.6 | 355.3 | 362.8 | 528.1 | 69.5 | 17.5 | 121.7 | 5.3 | 247.2 | 5 | 840.1 | 828.1 | 196.4 | 856.3 | 724 | 862.2 | 720.2 | 636.9 | 682.8 | 607.4 | 734.3 | 726.2 | 189.6 | 296.6 | 346.6 | 655.4 | 568.3 | 547.6 | 606.1 | 578 | 315.2 | 422.1 | 400.9 | 375.9 | 365.2 | 498.5 | 377.7
1331 | 1095 | 564.9 | 225.96 | 264.1342 | 420.2 | 380.4 | 355.2 | 364.6 | 527.1 | 69.5 | 17.5 | 121.6 | 5.7 | 246.5 | 5.4 | 834.7 | 822.9 | 196.2 | 853.4 | 723.7 | 860.5 | 715.8 | 633.3 | 672.3 | 606.6 | 734.6 | 723.7 | 189.9 | 296.8 | 346.8 | 654.9 | 567.8 | 542.8 | 606.4 | 577.2 | 315.4 | 423.2 | 401.7 | 376.3 | 365.4 | 498.6 | 378
1332 | 1096 | 566.6 | 226.64 | 264.9291 | 420.2 | 380.3 | 356.5 | 366.9 | 524.4 | 69.5 | 17.5 | 121.5 | 5.7 | 245.3 | 6.2 | 825.4 | 814 | 196.1 | 851.1 | 723.2 | 859.6 | 712.2 | 630.3 | 664.7 | 606.2 | 734.9 | 721.5 | 190.2 | 296.9 | 346.8 | 654.7 | 568.2 | 540.8 | 606.5 | 577.1 | 315.7 | 425 | 402.8 | 376.7 | 365.7 | 498.7 | 378.2
1333 | 1097 | 566.3 | 226.52 | 264.7888 | 420.5 | 380.3 | 358.2 | 369.8 | 521.8 | 69.6 | 17.5 | 121.5 | 5.5 | 248.3 | 6.4 | 828.9 | 817.7 | 195.3 | 849.2 | 722.9 | 858.9 | 709.8 | 628.4 | 662.1 | 606.4 | 735 | 720 | 190.5 | 297 | 347 | 654.5 | 568.6 | 538.8 | 606.7 | 577.3 | 316 | 426.7 | 403.6 | 377.2 | 366 | 498.8 | 378.5
1334 | 1098 | 566.7 | 226.68 | 264.9759 | 420.5 | 380.1 | 359.5 | 372.2 | 519.6 | 69.6 | 17.5 | 121.3 | 5.2 | 251.6 | 5.9 | 837.8 | 821.2 | 195.6 | 848.5 | 722.9 | 858.6 | 708.7 | 627.5 | 668 | 606.4 | 734.6 | 718.8 | 190.8 | 297.1 | 347 | 654.5 | 568.5 | 538.2 | 606.8 | 577.4 | 316.3 | 427.5 | 403.7 | 377.6 | 366.1 | 498.9 | 378.8
1335 | 1099 | 565.1 | 226.04 | 264.2277 | 420.5 | 380.4 | 360.7 | 372.4 | 520.2 | 69.5 | 17.5 | 121.2 | 5.4 | 236.6 | 5.1 | 834.2 | 817.4 | 196.1 | 847.7 | 722.8 | 857.4 | 707.2 | 627.6 | 662.5 | 607.1 | 733.9 | 717.8 | 191 | 297 | 347.2 | 654.6 | 569.4 | 540 | 607.1 | 579.4 | 316.6 | 428.6 | 404.3 | 378 | 366.3 | 499.1 | 379.1
1336 | 1100 | 564.8 | 225.92 | 264.0875 | 420.2 | 382.1 | 361.3 | 372.9 | 521.1 | 69.6 | 17.5 | 121.2 | 6.2 | 227.3 | 4.8 | 834.3 | 818.5 | 196.5 | 846.6 | 722.5 | 855.5 | 703.6 | 625.5 | 656 | 607 | 733.5 | 715.3 | 191.3 | 296.9 | 347.4 | 654.5 | 570.3 | 538.7 | 607.3 | 581.2 | 317 | 429.9 | 405.4 | 378.4 | 366.7 | 499.2 | 379.3
1337 | 1101 | 565.1 | 226.04 | 264.2277 | 418.9 | 383 | 361.3 | 373.7 | 519.3 | 69.6 | 17.5 | 121.2 | 6.5 | 225 | 4.7 | 848.4 | 828.8 | 196.6 | 847.1 | 722.5 | 855.5 | 704.5 | 626.2 | 672.4 | 606.7 | 733.2 | 715.3 | 191.6 | 297 | 347.4 | 654.2 | 569.7 | 536.8 | 607.4 | 580.6 | 317.3 | 430.1 | 406.1 | 378.7 | 367.1 | 499.4 | 379.6
1338 | 1102 | 563.5 | 225.4 | 263.4796 | 418.4 | 383 | 361.5 | 374.3 | 520.4 | 69.6 | 17.5 | 121.3 | 5.7 | 233.4 | 4.6 | 856.3 | 836.8 | 197 | 847.9 | 722.6 | 856.9 | 706.5 | 626.5 | 676.2 | 606.5 | 733.2 | 715.1 | 191.9 | 297.1 | 347.5 | 654.1 | 569.7 | 537.1 | 607.6 | 580.6 | 317.6 | 430.5 | 406.5 | 379 | 367.3 | 499.6 | 379.8
1339 | 1103 | 564 | 225.6 | 263.7134 | 418.4 | 383.1 | 361.4 | 374.7 | 520.2 | 69.5 | 17.5 | 121.3 | 5.8 | 243.7 | 5.4 | 862.1 | 836.2 | 197.1 | 848.7 | 722.6 | 858.6 | 709.4 | 625.9 | 680.9 | 605.7 | 733.3 | 715.9 | 192.1 | 297.3 | 347.5 | 654.1 | 568.6 | 537.7 | 607.8 | 578.8 | 317.9 | 430.3 | 406.5 | 379.2 | 367.4 | 499.7 | 380
1340 | 1104 | 563.7 | 225.48 | 263.5731 | 417.9 | 383 | 361.3 | 373.7 | 521.7 | 69.4 | 17.5 | 121.2 | 5.9 | 229 | 5.6 | 869.7 | 835.5 | 197.4 | 849.6 | 722.8 | 859.7 | 712.5 | 626.4 | 692.3 | 605.4 | 733.4 | 717.1 | 192.4 | 297.5 | 347.7 | 654.3 | 568.1 | 539.6 | 607.9 | 577.9 | 318.2 | 429.6 | 406.4 | 379.4 | 367.5 | 499.8 | 380.2
1341 | 1105 | 566.1 | 226.44 | 264.6953 | 417.6 | 382.6 | 361.1 | 371.7 | 525.6 | 69.4 | 17.5 | 121.2 | 6.2 | 226.7 | 5.5 | 866.9 | 835.3 | 197.1 | 851 | 723.1 | 860.7 | 715.4 | 628.2 | 700.4 | 606.3 | 733.6 | 718.8 | 192.8 | 297.6 | 347.8 | 654.5 | 568.5 | 542.9 | 608.3 | 578.7 | 318.5 | 430.2 | 406.8 | 379.7 | 367.7 | 499.9 | 380.3
1342 | 1106 | 566.2 | 226.48 | 264.7421 | 417.3 | 382.3 | 360.9 | 370.8 | 528 | 69.3 | 17.5 | 121.4 | 5.7 | 223.5 | 5.1 | 868.6 | 835.1 | 197.5 | 851.7 | 723.4 | 861.2 | 716.3 | 630.8 | 704.8 | 606.8 | 733.5 | 719.1 | 193.1 | 297.7 | 347.9 | 654.6 | 568.7 | 542.1 | 608.6 | 579.3 | 318.7 | 429.6 | 407.1 | 379.9 | 367.9 | 500 | 380.5
1343 | 1107 | 566.2 | 226.48 | 264.7421 | 416.9 | 382.4 | 360.5 | 370.1 | 528.3 | 69.3 | 17.5 | 121.5 | 5.4 | 229.5 | 5 | 867 | 834.6 | 197.1 | 851.9 | 723.6 | 861.5 | 716.4 | 632 | 702.5 | 607.6 | 733.8 | 718.8 | 193.3 | 297.8 | 348 | 654.7 | 568.5 | 542.4 | 608.8 | 579.2 | 319 | 429.3 | 407.6 | 380.1 | 368.1 | 500 | 380.7
1344 | 1108 | 565.8 | 226.32 | 264.555 | 416.8 | 382.9 | 360 | 369.4 | 527.9 | 69.3 | 17.5 | 121.7 | 5.7 | 235.5 | 5 | 864.1 | 831.1 | 196.7 | 851.6 | 723.7 | 861.1 | 717 | 634 | 706.3 | 607.5 | 733.6 | 719.2 | 193.6 | 297.9 | 348.1 | 654.6 | 568.6 | 541.9 | 608.9 | 580.5 | 319.3 | 429.3 | 407.8 | 380.4 | 368.2 | 500 | 380.9
1345 | 1109 | 566.3 | 226.52 | 264.7888 | 416.3 | 383.1 | 359.7 | 369.5 | 526.2 | 69.3 | 17.5 | 122 | 5.9 | 213 | 5 | 861.3 | 831.4 | 197.1 | 851.9 | 723.9 | 862.1 | 717.5 | 634.3 | 709.7 | 606.7 | 733.7 | 720.1 | 193.9 | 297.9 | 348.2 | 654.5 | 567.9 | 541.4 | 608.9 | 579.9 | 319.5 | 429.2 | 407.9 | 380.5 | 368.4 | 500.1 | 381.1
1346 | 1110 | 566.5 | 226.6 | 264.8823 | 416 | 383.2 | 359.5 | 369.3 | 526.7 | 69.4 | 17.5 | 122.1 | 5.6 | 234.1 | 4.9 | 865.4 | 839.3 | 197.6 | 851.8 | 724.3 | 862.7 | 717.3 | 633.5 | 711.5 | 606 | 734.1 | 719.1 | 194.2 | 298 | 348.3 | 654.3 | 567.7 | 540.9 | 609 | 578.1 | 319.8 | 428.9 | 407.8 | 380.7 | 368.5 | 500.2 | 381.3
1347 | 1111 | 566.7 | 226.68 | 264.9759 | 415.4 | 383.1 | 359 | 369.8 | 525.9 | 69.4 | 17.5 | 122.2 | 5.6 | 243.3 | 4.4 | 868.6 | 842 | 198.4 | 852.1 | 724.4 | 863.9 | 719.8 | 634.7 | 719.9 | 605.8 | 734.3 | 720.5 | 194.5 | 298 | 348.4 | 654.3 | 566.7 | 543.3 | 609.2 | 577.2 | 320.1 | 428.6 | 407.4 | 380.9 | 368.5 | 500.3 | 381.5
1348 | 1112 | 564.7 | 225.88 | 264.0407 | 415.8 | 384.3 | 359 | 369.6 | 525.9 | 69.4 | 17.5 | 122.2 | 5.8 | 232.3 | 4.3 | 870.3 | 842 | 199 | 852.6 | 724.7 | 865.3 | 720.9 | 634.8 | 720.6 | 605.6 | 734.2 | 721.3 | 194.8 | 297.9 | 348.4 | 654.2 | 565.9 | 544.3 | 609.8 | 577.1 | 320.4 | 428.5 | 406.8 | 381 | 368.7 | 500.3 | 381.6
1349 | 1113 | 562 | 224.8 | 262.7782 | 416.4 | 385.7 | 358.7 | 368.2 | 527.1 | 69.4 | 17.5 | 122.2 | 5.7 | 234.8 | 4.2 | 870.2 | 843.4 | 198.9 | 853.4 | 725 | 865.9 | 721.6 | 634.1 | 722.9 | 605.2 | 734.1 | 721.7 | 195.1 | 297.9 | 348.5 | 654.4 | 565.7 | 544.5 | 610.4 | 576.4 | 320.6 | 428.3 | 406.4 | 381.2 | 368.8 | 500.4 | 381.8
1350 | 1114 | 560.3 | 224.12 | 261.9834 | 416.3 | 384.9 | 358.4 | 367.2 | 527.1 | 69.5 | 17.5 | 122.3 | 6.1 | 216.2 | 4.2 | 869.1 | 840.9 | 199.4 | 854.5 | 725.3 | 867.3 | 722.4 | 634.6 | 724.3 | 605.4 | 733.7 | 722.7 | 195.4 | 297.9 | 348.6 | 654.7 | 565.3 | 544.2 | 610.7 | 576.3 | 320.9 | 428 | 406.2 | 381.3 | 368.9 | 500.5 | 382
1351 | 1115 | 560.7 | 224.28 | 262.1704 | 416 | 384 | 357 | 366.3 | 528.8 | 69.5 | 17.5 | 122.3 | 6.1 | 209.5 | 4.4 | 870.9 | 839.8 | 200.2 | 855.7 | 725.5 | 868.3 | 724.3 | 634.4 | 719.9 | 604.8 | 733.6 | 723.2 | 195.7 | 298 | 348.8 | 655.1 | 565.1 | 545.5 | 611.1 | 576.1 | 321.2 | 427.8 | 405.8 | 381.4 | 369.1 | 500.5 | 382.2
1352 | 1116 | 562.3 | 224.92 | 262.9185 | 417.1 | 383 | 356.5 | 365.4 | 529.2 | 69.6 | 17.5 | 122.4 | 6.5 | 209.5 | 4.4 | 870.6 | 843.9 | 201 | 856.5 | 725.6 | 868.3 | 726.8 | 633.1 | 724.9 | 603.2 | 733.8 | 723 | 196 | 298 | 349 | 655.3 | 564.4 | 551.6 | 611.9 | 575.8 | 321.4 | 427.4 | 405.1 | 381.6 | 369.1 | 500.6 | 382.3
1353 | 1117 | 564.6 | 225.84 | 263.9939 | 417.4 | 382.2 | 357.3 | 364.7 | 533.5 | 69.6 | 17.5 | 122.4 | 6.8 | 234.5 | 4.3 | 872.8 | 846.7 | 201.5 | 856.4 | 725.6 | 868.6 | 727.7 | 634.1 | 728 | 604.6 | 734 | 724.8 | 196.3 | 298.1 | 349.3 | 655.8 | 565.6 | 558.5 | 612.1 | 577 | 321.7 | 426.7 | 404.4 | 381.7 | 369.2 | 500.6 | 382.5
1354 | 1118 | 563.6 | 225.44 | 263.5264 | 417.5 | 383.6 | 358.2 | 364 | 536.1 | 69.5 | 17.5 | 122.4 | 6.5 | 240.1 | 4.3 | 874.1 | 850.8 | 202.9 | 857.5 | 725.6 | 868.6 | 727.4 | 634.6 | 724.6 | 604.8 | 733.8 | 725.3 | 196.7 | 298.2 | 349.2 | 655.7 | 566.4 | 556.6 | 612.1 | 578 | 321.9 | 426.1 | 404.3 | 381.8 | 369.4 | 500.7 | 382.6
1355 | 1119 | 564.4 | 225.76 | 263.9004 | 417 | 384.6 | 358.8 | 363 | 534.4 | 69.4 | 17.5 | 122.4 | 5.6 | 219.2 | 4.6 | 871.8 | 856.8 | 204.7 | 858.4 | 725.7 | 868.7 | 727.9 | 635.3 | 730.8 | 605 | 733.8 | 725.1 | 197 | 298.3 | 349.2 | 655.7 | 565.8 | 555.4 | 612.3 | 576.7 | 322.2 | 425.4 | 403.8 | 381.9 | 369.3 | 500.8 | 382.7
1356 | 1120 | 565.7 | 226.28 | 264.5083 | 416.9 | 384.5 | 358.6 | 362.8 | 533.5 | 69.3 | 17.5 | 122.5 | 5.8 | 216.9 | 5 | 874.6 | 859.9 | 207.4 | 859.8 | 726 | 868.8 | 729.5 | 637.7 | 740.7 | 606.5 | 733.6 | 726.7 | 197.2 | 298.5 | 349.4 | 656.2 | 565.6 | 561.4 | 612.9 | 578.7 | 322.4 | 425 | 403.4 | 382 | 369.3 | 500.8 | 382.9
1357 | 1121 | 565.7 | 226.28 | 264.5083 | 416.7 | 385.3 | 357.8 | 362.2 | 535.5 | 69.2 | 17.5 | 122.6 | 6.4 | 223.1 | 5.2 | 873.2 | 859.7 | 209.4 | 862.7 | 726.4 | 867.4 | 729.8 | 640.7 | 739.5 | 607.7 | 733.2 | 727.6 | 197.5 | 298.7 | 349.5 | 656.3 | 567.1 | 564.5 | 613.6 | 580.4 | 322.7 | 424.9 | 402.9 | 382.1 | 369.5 | 500.9 | 383.1
1358 | 1122 | 566.9 | 226.76 | 265.0694 | 417.2 | 388.3 | 357.1 | 361.9 | 535.5 | 69.3 | 17.5 | 122.7 | 5.9 | 223.9 | 4.8 | 872.3 | 863.7 | 210 | 863.8 | 726.9 | 866.2 | 729.7 | 641.2 | 740.4 | 607.6 | 732.9 | 727 | 197.8 | 298.8 | 349.6 | 656.5 | 567.2 | 566.1 | 613.7 | 580.2 | 322.9 | 424.8 | 402.9 | 382.3 | 369.6 | 501 | 383.2
1359 | 1123 | 565.2 | 226.08 | 264.2745 | 417.8 | 388.8 | 355.9 | 361.9 | 534.3 | 69.3 | 17.5 | 122.8 | 6 | 227.7 | 4.1 | 875.7 | 865.5 | 210.9 | 864.4 | 727.2 | 865.5 | 728.6 | 641.7 | 733.3 | 607.5 | 732.8 | 726.6 | 198.1 | 298.9 | 349.7 | 656.7 | 567.2 | 563.1 | 613.9 | 580.1 | 323.1 | 425.2 | 403.2 | 382.5 | 369.7 | 501.1 | 383.4
1360 | 1124 | 565 | 226 | 264.181 | 417.9 | 388.7 | 355.3 | 362.8 | 530.8 | 69.3 | 17.5 | 122.8 | 6.8 | 233.8 | 3.5 | 875.4 | 862.6 | 211.6 | 864.3 | 727.2 | 864.5 | 726.8 | 641 | 726.2 | 607.3 | 732.8 | 725.6 | 198.4 | 298.9 | 349.7 | 656.8 | 567.7 | 558.9 | 614 | 579.8 | 323.4 | 425.8 | 403.3 | 382.7 | 369.8 | 501.2 | 383.6
1361 | 1125 | 565.3 | 226.12 | 264.3213 | 417.4 | 387.8 | 354.4 | 364.4 | 528.6 | 69.3 | 17.5 | 122.7 | 6 | 238.9 | 3.5 | 873.3 | 861.5 | 212.7 | 863.1 | 727.2 | 864.8 | 725.3 | 639.7 | 723.1 | 606.6 | 732.5 | 724.5 | 198.7 | 298.8 | 349.8 | 656.8 | 567.3 | 555.9 | 614.1 | 578.4 | 323.6 | 426.1 | 403.4 | 382.9 | 369.9 | 501.3 | 383.8
1362 | 1126 | 564.7 | 225.88 | 264.0407 | 417.4 | 386.4 | 353.8 | 365.7 | 527.6 | 69.3 | 17.5 | 122.9 | 6 | 241.6 | 3.6 | 870.3 | 862.6 | 214.9 | 863.2 | 727.5 | 865.5 | 726.1 | 639.6 | 735.2 | 606.3 | 732.4 | 725.4 | 199 | 298.7 | 349.9 | 657.2 | 567.1 | 556.8 | 614.1 | 577.3 | 323.9 | 426.1 | 403.5 | 383.1 | 370 | 501.4 | 384
1363 | 1127 | 564.2 | 225.68 | 263.8069 | 417.3 | 385.4 | 354 | 366 | 527.1 | 69.2 | 17.5 | 123.1 | 6.2 | 236 | 3.8 | 870.8 | 863.3 | 215.4 | 863.7 | 727.9 | 865.7 | 727.4 | 640.9 | 737.2 | 606.9 | 731.9 | 725.3 | 199.3 | 298.7 | 350 | 657.3 | 566.8 | 556.4 | 614.1 | 578.4 | 324.2 | 426 | 403.6 | 383.3 | 370.1 | 501.4 | 384.1
1364 | 1128 | 563.7 | 225.48 | 263.5731 | 417 | 385.5 | 354 | 365.3 | 525.4 | 69.1 | 17.5 | 123.2 | 6.4 | 218.4 | 4.2 | 871.6 | 860.1 | 216.2 | 863.8 | 728.3 | 865.7 | 726 | 641.6 | 727.9 | 607.1 | 731.2 | 724.8 | 199.5 | 298.8 | 350.1 | 657.4 | 566.4 | 552.5 | 614.2 | 580.4 | 324.4 | 426.3 | 403.9 | 383.4 | 370.2 | 501.5 | 384.3
1365 | 1129 | 565.2 | 226.08 | 264.2745 | 416.6 | 385.3 | 353.6 | 364.7 | 523.2 | 69 | 17.5 | 123.3 | 6.5 | 222.7 | 4 | 870 | 852.3 | 216 | 863.4 | 728.6 | 865.2 | 723.7 | 641.6 | 721.3 | 606.5 | 730.6 | 724.5 | 199.8 | 298.7 | 350.3 | 657.2 | 567 | 550.7 | 614.2 | 580.9 | 324.7 | 426.8 | 404.5 | 383.6 | 370.3 | 501.6 | 384.4
1366 | 1130 | 565 | 226 | 264.181 | 415.9 | 384.9 | 353.7 | 364.7 | 523.5 | 69.1 | 17.5 | 123.5 | 6.2 | 246.2 | 4.4 | 872.1 | 851.6 | 215.7 | 862.2 | 728.8 | 864.9 | 721.7 | 641.4 | 712.9 | 606.6 | 730.7 | 724.2 | 200 | 298.7 | 350.4 | 657.3 | 567.9 | 550.8 | 614.5 | 581.6 | 324.9 | 427.3 | 405.5 | 383.8 | 370.5 | 501.7 | 384.6
1367 | 1131 | 564 | 225.6 | 263.7134 | 415.7 | 384.7 | 354.6 | 365.2 | 522.5 | 69.1 | 17.5 | 123.6 | 6.1 | 257.3 | 4.5 | 872.6 | 857.2 | 216.4 | 860.9 | 729.1 | 863.7 | 720.6 | 642.2 | 716.3 | 607.2 | 730.6 | 723.3 | 200.3 | 298.7 | 350.6 | 657.3 | 568.4 | 549 | 614.7 | 582.8 | 325.2 | 427.8 | 406.6 | 384.1 | 370.6 | 501.8 | 384.8
1368 | 1132 | 564.2 | 225.68 | 263.8069 | 415.6 | 385 | 355 | 366.5 | 523.3 | 69.1 | 17.5 | 123.7 | 5.9 | 244.2 | 4.8 | 870.1 | 859.9 | 218.2 | 861.2 | 729.8 | 862.4 | 722.5 | 643.8 | 728.8 | 608 | 730.1 | 724.1 | 200.6 | 298.8 | 350.7 | 657.6 | 568.2 | 553.3 | 614.8 | 584.1 | 325.5 | 428.4 | 406.9 | 384.4 | 370.8 | 502 | 385
1369 | 1133 | 566 | 226.4 | 264.6486 | 415.6 | 384.8 | 355.4 | 366.3 | 524.1 | 69.1 | 17.5 | 123.8 | 5.4 | 240.6 | 5.2 | 875.6 | 862.7 | 219.7 | 861.9 | 730.5 | 862 | 724.5 | 645 | 734.7 | 608.4 | 730.1 | 723.8 | 200.8 | 298.9 | 350.8 | 657.6 | 568 | 558.4 | 615 | 584.1 | 325.8 | 429.1 | 406.6 | 384.5 | 370.9 | 502.1 | 385.2
1370 | 1134 | 566 | 226.4 | 264.6486 | 416.3 | 386.7 | 355.3 | 365.7 | 526.3 | 69.1 | 17.5 | 123.7 | 5.4 | 244.6 | 5.6 | 876.9 | 865.9 | 222.1 | 862.7 | 730.8 | 862.1 | 725.5 | 645.8 | 733.7 | 608.7 | 730.1 | 723.6 | 201.1 | 299.1 | 350.8 | 657.5 | 568.4 | 560.8 | 615.1 | 583.7 | 326.1 | 429.7 | 406.5 | 384.8 | 371 | 502.2 | 385.4
1371 | 1135 | 567.4 | 226.96 | 265.3032 | 417.9 | 388.4 | 355.3 | 365.9 | 525.4 | 69.1 | 17.5 | 123.7 | 6 | 239.3 | 5.5 | 877.9 | 864.1 | 223.8 | 863.2 | 730.9 | 861.6 | 723.6 | 645.2 | 726.4 | 608.5 | 730.1 | 722.8 | 201.4 | 299.2 | 350.9 | 657.2 | 568.4 | 555.7 | 615.3 | 583.2 | 326.3 | 430.8 | 407.3 | 385 | 371.4 | 502.3 | 385.7
1372 | 1136 | 566.1 | 226.44 | 264.6953 | 418.8 | 389.7 | 355.5 | 366.7 | 525.7 | 69.2 | 17.5 | 123.7 | 6.1 | 238.3 | 5.4 | 874.5 | 862.5 | 225.9 | 863.4 | 730.9 | 860.5 | 721.7 | 643.7 | 719.4 | 608 | 729.9 | 720.9 | 201.7 | 299.3 | 351 | 657.2 | 569 | 554.5 | 615.5 | 582.8 | 326.6 | 431.4 | 408 | 385.3 | 371.6 | 502.4 | 385.9
1373 | 1137 | 564 | 225.6 | 263.7134 | 418.6 | 390.1 | 354.9 | 367.7 | 525.2 | 69.3 | 17.5 | 123.7 | 6.5 | 240.2 | 5.1 | 874.3 | 862.5 | 227.2 | 863.8 | 730.7 | 860 | 721.9 | 642.9 | 723.1 | 607.2 | 730.1 | 721.2 | 202 | 299.4 | 351 | 657.1 | 567.9 | 553.4 | 615.9 | 581.7 | 326.9 | 431.6 | 407.9 | 385.6 | 371.7 | 502.5 | 386.1
1374 | 1138 | 563.8 | 225.52 | 263.6199 | 418.5 | 389.9 | 354.7 | 367.9 | 524.6 | 69.4 | 17.5 | 123.7 | 6.4 | 224.1 | 4.7 | 877.1 | 867 | 229.6 | 864.5 | 730.8 | 860.6 | 723.3 | 642.5 | 729.5 | 607.1 | 730.4 | 721.8 | 202.3 | 299.4 | 351.2 | 657.2 | 567.5 | 554.9 | 616 | 581.8 | 327.1 | 431.9 | 407.9 | 385.8 | 371.9 | 502.7 | 386.3
1375 | 1139 | 565.4 | 226.16 | 264.368 | 418.7 | 390.3 | 354.5 | 368 | 527.2 | 69.4 | 17.5 | 123.6 | 6.5 | 235.2 | 4.4 | 874.4 | 869.3 | 232.2 | 864.4 | 731.1 | 861.6 | 726.6 | 644.3 | 740.4 | 607.9 | 730.6 | 722.2 | 202.5 | 299.5 | 351.4 | 657.3 | 567.7 | 560.6 | 616.1 | 583.3 | 327.4 | 432 | 407.9 | 386.1 | 372.2 | 502.7 | 386.5
1376 | 1140 | 567.1 | 226.84 | 265.1629 | 419.1 | 389.7 | 354.4 | 367.6 | 529.5 | 69.5 | 17.5 | 123.5 | 6.3 | 255.6 | 4.2 | 871.8 | 869.2 | 232.1 | 864 | 731.6 | 862.2 | 730.3 | 646.7 | 750.4 | 608.9 | 730.4 | 724 | 202.8 | 299.6 | 351.5 | 657.6 | 568 | 565.7 | 616.3 | 584.1 | 327.7 | 432.5 | 407.9 | 386.2 | 372.3 | 502.8 | 386.7
1377 | 1141 | 566.1 | 226.44 | 264.6953 | 418.8 | 389.5 | 355 | 367.3 | 532.7 | 69.6 | 17.5 | 123.5 | 6.2 | 239.7 | 3.6 | 873.7 | 872.8 | 234.3 | 864.3 | 731.8 | 862.1 | 733 | 648.9 | 753.1 | 610 | 730.2 | 723.4 | 203 | 299.7 | 351.7 | 658.1 | 568.3 | 573.6 | 616.5 | 584.8 | 328 | 432.1 | 407.5 | 386.4 | 372.4 | 502.9 | 386.8
1378 | 1142 | 564.9 | 225.96 | 264.1342 | 418.6 | 390 | 356 | 366.6 | 535.6 | 69.6 | 17.5 | 123.5 | 5.8 | 221.1 | 3.7 | 880.6 | 872.4 | 237.1 | 866 | 731.9 | 862.3 | 734.4 | 649.7 | 751.5 | 610.6 | 730.2 | 723.9 | 203.3 | 299.8 | 351.9 | 658.1 | 568.5 | 578.7 | 616.7 | 585.4 | 328.2 | 431.2 | 407.3 | 386.5 | 372.6 | 503 | 387
1379 | 1143 | 565.3 | 226.12 | 264.3213 | 417.8 | 391 | 356.6 | 365.7 | 535.7 | 69.6 | 17.5 | 123.5 | 5.8 | 226.6 | 3.5 | 880.4 | 868.2 | 239.4 | 868.7 | 732 | 862.9 | 732.3 | 649.5 | 742.4 | 610.3 | 730.2 | 724.7 | 203.5 | 299.9 | 351.9 | 657.3 | 568.4 | 573.5 | 617.1 | 584.4 | 328.5 | 430.4 | 407.2 | 386.6 | 372.6 | 503.1 | 387.1
1380 | 1144 | 566.7 | 226.68 | 264.9759 | 417.8 | 391.8 | 357.6 | 364.9 | 533.9 | 69.6 | 17.5 | 123.4 | 6 | 240.8 | 3.2 | 879.1 | 872.3 | 241.7 | 868.6 | 732.1 | 862.9 | 729.6 | 649.2 | 738.5 | 609.9 | 730.1 | 723.5 | 203.8 | 300.1 | 352 | 657 | 568.8 | 569.8 | 617.3 | 584 | 328.8 | 430.2 | 407.4 | 386.8 | 372.7 | 503.2 | 387.2
1381 | 1145 | 567.7 | 227.08 | 265.4434 | 417.8 | 392.1 | 357.4 | 365.4 | 531.6 | 69.5 | 17.4 | 123.3 | 5.7 | 247 | 3 | 883.4 | 871.9 | 242.7 | 869 | 732.3 | 863 | 727.3 | 648.6 | 732.7 | 609.6 | 729.9 | 721.3 | 204 | 300.2 | 352.1 | 656.6 | 568.7 | 567 | 617.5 | 583.8 | 329 | 430.2 | 407.9 | 387 | 372.9 | 503.3 | 387.4
1382 | 1146 | 566.7 | 226.68 | 264.9759 | 417.6 | 392 | 356.4 | 366.6 | 529.5 | 69.5 | 17.4 | 123.3 | 5.5 | 246.7 | 3 | 883.3 | 871 | 246.8 | 871.4 | 732.2 | 863.8 | 726 | 647.5 | 729.7 | 609 | 730.1 | 720.8 | 204.3 | 300.4 | 352.1 | 656.4 | 568.5 | 563.6 | 617.7 | 583.1 | 329.3 | 430.9 | 408.1 | 387.2 | 373 | 503.4 | 387.5
1383 | 1147 | 565.9 | 226.36 | 264.6018 | 417.9 | 392.3 | 356 | 367.7 | 527 | 69.5 | 17.4 | 123.2 | 5.7 | 240.8 | 3.4 | 882.1 | 872.7 | 246.1 | 871.8 | 732.3 | 864.1 | 726.3 | 646.5 | 733.8 | 608.5 | 730.1 | 720.8 | 204.5 | 300.5 | 352.2 | 656.3 | 567.8 | 560.7 | 617.7 | 582.5 | 329.6 | 431.1 | 408 | 387.4 | 373.1 | 503.6 | 387.7
1384 | 1148 | 566.9 | 226.76 | 265.0694 | 418.9 | 392.1 | 355.7 | 368.3 | 526.7 | 69.6 | 17.4 | 123.2 | 6 | 219.3 | 3.3 | 875.9 | 869.8 | 248.8 | 871.8 | 732.3 | 865 | 728.5 | 646.3 | 734.2 | 609.1 | 730.3 | 722.6 | 204.8 | 300.5 | 352.4 | 656.5 | 567.3 | 561.2 | 617.8 | 583 | 329.9 | 431.3 | 407.6 | 387.5 | 373.2 | 503.7 | 387.9
1385 | 1149 | 565.1 | 226.04 | 264.2277 | 419.5 | 391.7 | 355.7 | 368.3 | 529.5 | 69.6 | 17.4 | 123.3 | 5.7 | 216.8 | 3.3 | 876.4 | 873.2 | 249.9 | 870.7 | 732.5 | 864.8 | 730.9 | 646 | 739.4 | 609.7 | 730.5 | 723.3 | 205.1 | 300.6 | 352.7 | 656.8 | 567.4 | 566.7 | 617.8 | 582.9 | 330.2 | 431.9 | 407 | 387.7 | 373.2 | 503.8 | 388
1386 | 1150 | 565.7 | 226.28 | 264.5083 | 419.9 | 392 | 356.6 | 367.6 | 533.8 | 69.6 | 17.4 | 123.5 | 5.2 | 243.4 | 3.6 | 875.7 | 875 | 250.7 | 870.5 | 732.5 | 865 | 731.9 | 645.4 | 742.5 | 610.1 | 730.7 | 723.5 | 205.3 | 300.8 | 353 | 657 | 567.6 | 574.3 | 617.9 | 582.7 | 330.5 | 432.9 | 406.1 | 387.8 | 373.3 | 503.8 | 388.2
1387 | 1151 | 566.3 | 226.52 | 264.7888 | 419.8 | 393.9 | 356.8 | 366.6 | 539.9 | 69.6 | 17.4 | 123.6 | 5.5 | 249 | 3.9 | 876.2 | 873.8 | 252.2 | 870.5 | 732.3 | 865.1 | 732.3 | 644.9 | 744.9 | 611.1 | 731.2 | 722.7 | 205.6 | 300.9 | 353.6 | 657.7 | 568 | 584.2 | 618 | 583.2 | 330.7 | 433.2 | 405.4 | 387.9 | 373.2 | 503.9 | 388.4
1388 | 1152 | 566.3 | 226.52 | 264.7888 | 419.8 | 394 | 357 | 365.3 | 543.9 | 69.6 | 17.4 | 123.6 | 6.2 | 231.6 | 4 | 879.9 | 872.8 | 253.7 | 870.8 | 732.1 | 865.8 | 734.5 | 646.3 | 749 | 612 | 731.4 | 724.1 | 205.8 | 301.1 | 353.5 | 658 | 568.2 | 586.8 | 618.2 | 583.6 | 331 | 432.7 | 405.7 | 388 | 373.4 | 504 | 388.5
1389 | 1153 | 566 | 226.4 | 264.6486 | 420.3 | 393.5 | 359.1 | 364.4 | 543.6 | 69.7 | 17.4 | 123.5 | 5.9 | 223.3 | 3.9 | 879.8 | 875 | 255.6 | 873.2 | 732.2 | 866 | 734.1 | 645.9 | 748.2 | 612.2 | 731.5 | 725.9 | 206.1 | 301.2 | 353.4 | 657.8 | 568.4 | 583.3 | 618.5 | 583.4 | 331.2 | 432.2 | 406.9 | 388.1 | 373.5 | 504 | 388.6
1390 | 1154 | 565.5 | 226.2 | 264.4148 | 420.4 | 395 | 360.1 | 364.1 | 540.8 | 69.8 | 17.4 | 123.3 | 5.5 | 224.7 | 3.7 | 880.9 | 870.5 | 255.2 | 875.9 | 732.2 | 866 | 732.2 | 646.4 | 742.7 | 612.4 | 731.3 | 725.9 | 206.3 | 301.3 | 353.5 | 657.5 | 568.4 | 580 | 618.8 | 583.7 | 331.5 | 431.3 | 407.9 | 388.2 | 373.6 | 504.1 | 388.8
1391 | 1155 | 565 | 226 | 264.181 | 419.2 | 395.9 | 359.4 | 364.4 | 537.2 | 69.9 | 17.4 | 123.2 | 6 | 214.3 | 4 | 880 | 868.2 | 255.8 | 875.5 | 732.4 | 865.7 | 729.2 | 645.6 | 735.7 | 611.7 | 730.9 | 724.3 | 206.5 | 301.4 | 353.6 | 657.2 | 568.2 | 573.5 | 619.2 | 584.6 | 331.7 | 430.8 | 409 | 388.3 | 373.8 | 504.2 | 388.9
1392 | 1156 | 564.3 | 225.72 | 263.8537 | 418.2 | 395 | 358.3 | 364.8 | 534.9 | 69.9 | 17.4 | 123.2 | 5.9 | 216.7 | 4 | 888 | 871.4 | 257.6 | 873.9 | 732.6 | 865.6 | 728.2 | 646.6 | 739.9 | 611.8 | 730.7 | 723 | 206.8 | 301.6 | 353.7 | 656.8 | 567.7 | 569.8 | 619.3 | 584.8 | 332 | 430.6 | 409.6 | 388.5 | 374 | 504.3 | 389.1
1393 | 1157 | 564.2 | 225.68 | 263.8069 | 417.7 | 394.9 | 357.7 | 365.6 | 535.1 | 70 | 17.4 | 123.2 | 5.9 | 226 | 3.7 | 889.8 | 868.1 | 257.4 | 874.8 | 732.7 | 866 | 729.5 | 647.6 | 742.6 | 611.9 | 730.6 | 723.3 | 207.1 | 301.7 | 353.8 | 656.9 | 567.7 | 570.1 | 619.4 | 585.3 | 332.3 | 430.6 | 409.9 | 388.8 | 374.1 | 504.4 | 389.3
1394 | 1158 | 566.7 | 226.68 | 264.9759 | 417.2 | 396.1 | 357.4 | 367.6 | 534.5 | 70.1 | 17.4 | 123.2 | 5.8 | 232.9 | 3.7 | 884.6 | 855.9 | 257.7 | 874.6 | 732.5 | 866.9 | 728.6 | 646.4 | 737.3 | 611.3 | 730.9 | 723.5 | 207.4 | 301.8 | 353.8 | 656.6 | 568 | 564.6 | 619.4 | 584.4 | 332.5 | 430.7 | 410.8 | 389 | 374.2 | 504.6 | 389.5
1395 | 1159 | 566.3 | 226.52 | 264.7888 | 416.7 | 396.1 | 357.4 | 368.3 | 532.7 | 70.2 | 17.4 | 123.1 | 5.9 | 237.8 | 3.3 | 877.1 | 847 | 258.5 | 875.5 | 732.3 | 866.8 | 728.8 | 646.6 | 733.6 | 611.2 | 731 | 724.9 | 207.6 | 301.9 | 353.9 | 656.6 | 566.8 | 562.6 | 619.5 | 583.3 | 332.8 | 430.7 | 412.4 | 389.2 | 374.4 | 504.7 | 389.6
1396 | 1160 | 564.4 | 225.76 | 263.9004 | 416.5 | 395 | 356.8 | 368.6 | 533 | 70.2 | 17.4 | 123 | 5.9 | 251.3 | 3.6 | 881 | 850.6 | 259.2 | 874.3 | 732.3 | 866.3 | 729.4 | 646.3 | 736 | 610.6 | 730.9 | 724.9 | 207.8 | 302.1 | 354.1 | 656.6 | 567 | 561.2 | 619.5 | 582.4 | 333 | 430.9 | 412.7 | 389.4 | 374.7 | 504.7 | 389.8
1397 | 1161 | 565.9 | 226.36 | 264.6018 | 417 | 394.1 | 356.2 | 368.9 | 532.9 | 70.3 | 17.4 | 123 | 5.7 | 257.4 | 3.6 | 880.2 | 845.5 | 258.6 | 872.4 | 732.1 | 866.6 | 729.6 | 644.4 | 729.7 | 609.8 | 731 | 725.3 | 208 | 302.2 | 354.2 | 656.6 | 566.7 | 560.5 | 619.5 | 581.4 | 333.3 | 431.2 | 412.2 | 389.6 | 374.7 | 504.8 | 390
1398 | 1162 | 566.3 | 226.52 | 264.7888 | 417.2 | 394.3 | 356 | 369.1 | 533.3 | 70.4 | 17.4 | 123 | 5.8 | 248.7 | 4 | 877.3 | 843.2 | 259.1 | 871.5 | 732 | 866.7 | 731.7 | 644.5 | 739.7 | 610.1 | 731.1 | 727.3 | 208.2 | 302.2 | 354.4 | 656.8 | 565.5 | 561.5 | 619.8 | 580.6 | 333.6 | 432.2 | 411.4 | 389.7 | 374.7 | 504.9 | 390.1
1399 | 1163 | 567.9 | 227.16 | 265.537 | 417.4 | 393.8 | 355.8 | 368.3 | 533.6 | 70.4 | 17.4 | 123 | 5.8 | 231.3 | 4.2 | 871.8 | 840 | 259.9 | 872.1 | 731.8 | 867.9 | 733.6 | 644.6 | 737.1 | 610.2 | 731 | 728.3 | 208.5 | 302.3 | 354.6 | 656.6 | 565.4 | 560.4 | 620.2 | 580.8 | 333.9 | 432.2 | 410.9 | 389.8 | 374.8 | 504.9 | 390.2
1400 | 1164 | 566.6 | 226.64 | 264.9291 | 418.2 | 393.6 | 355.3 | 367.1 | 535.1 | 70.5 | 17.4 | 123 | 5.9 | 209.8 | 4.3 | 870.2 | 836.4 | 259.8 | 871.9 | 731.6 | 868.7 | 734.3 | 643.2 | 737.5 | 609.6 | 731.3 | 728.8 | 208.7 | 302.3 | 354.8 | 656.5 | 565.6 | 558.9 | 620.5 | 579.5 | 334.2 | 430.7 | 410.6 | 389.9 | 374.9 | 504.9 | 390.4
1401 | 1165 | 566.3 | 226.52 | 264.7888 | 419 | 394.1 | 354.8 | 365.9 | 537.1 | 70.5 | 17.4 | 123 | 5.8 | 204.6 | 5.1 | 860.8 | 832.3 | 262.6 | 872.7 | 731.2 | 868.9 | 737.2 | 643 | 740.3 | 609.4 | 731.5 | 729.9 | 209 | 302.4 | 354.8 | 656.9 | 566.1 | 561.3 | 621 | 578.9 | 334.4 | 429.7 | 409.7 | 390 | 374.8 | 505 | 390.5
1402 | 1166 | 566.6 | 226.64 | 264.9291 | 418.8 | 393.9 | 355.7 | 365.7 | 539.3 | 70.5 | 17.4 | 123 | 5.4 | 217 | 5.3 | 854.5 | 831.1 | 263.4 | 873.2 | 730.9 | 868.9 | 739.4 | 641.3 | 735.4 | 609 | 731.6 | 729.8 | 209.3 | 302.5 | 355.1 | 657.2 | 566.5 | 564.5 | 621.4 | 578.4 | 334.7 | 428.6 | 409.4 | 390 | 374.7 | 505 | 390.6
1403 | 1167 | 565.9 | 226.36 | 264.6018 | 419.5 | 393 | 355.6 | 365.2 | 539.9 | 70.4 | 17.4 | 123.1 | 5.6 | 218.8 | 5.4 | 853.1 | 830.6 | 263 | 873 | 730.6 | 869.2 | 738.1 | 638.8 | 728.8 | 607.5 | 731.7 | 730.2 | 209.5 | 302.7 | 355.1 | 657.4 | 566.9 | 563.7 | 621.5 | 577.6 | 334.9 | 427.6 | 410.2 | 390.1 | 374.6 | 505.1 | 390.7
1404 | 1168 | 565.6 | 226.24 | 264.4615 | 420 | 391.5 | 355.6 | 364.5 | 539.8 | 70.3 | 17.4 | 123.2 | 6 | 210.3 | 5.3 | 853.3 | 831.2 | 262.7 | 872.4 | 730.3 | 868.7 | 736.7 | 636.6 | 731.8 | 606.3 | 731.8 | 730.3 | 209.7 | 302.9 | 355.3 | 657.5 | 566.9 | 563.6 | 621.6 | 576.9 | 335.2 | 426.6 | 409.4 | 390.1 | 374.5 | 505.1 | 390.8
1405 | 1169 | 566.3 | 226.52 | 264.7888 | 418.7 | 390.7 | 356.6 | 363.9 | 540.1 | 70.2 | 17.4 | 123.2 | 6.2 | 217.4 | 4.9 | 860.8 | 835.4 | 263.4 | 872.5 | 730.2 | 868.1 | 737 | 638.6 | 739.8 | 606.4 | 731.6 | 732.5 | 209.9 | 303.1 | 355.3 | 657.4 | 566.9 | 564.4 | 621.7 | 577.9 | 335.4 | 425.8 | 408.4 | 390.2 | 374.5 | 505.1 | 390.9
1406 | 1170 | 565.4 | 226.16 | 264.368 | 417.7 | 390.2 | 357.4 | 363.4 | 538.4 | 70.1 | 17.4 | 123.2 | 6 | 218.7 | 4.7 | 860.5 | 842 | 265.4 | 873.6 | 729.9 | 868.4 | 737.3 | 638.7 | 746.1 | 606.4 | 731.4 | 732.8 | 210.1 | 303.3 | 355.4 | 657.2 | 567.2 | 564.7 | 621.6 | 578.1 | 335.7 | 425.5 | 407.2 | 390.2 | 374.4 | 505.1 | 391
1407 | 1171 | 564.9 | 225.96 | 264.1342 | 418.7 | 389.8 | 356.7 | 363 | 537.3 | 70 | 17.4 | 123.1 | 6 | 203.9 | 5.1 | 860.6 | 851.4 | 268.1 | 872.8 | 730 | 868.5 | 739 | 640 | 755.6 | 607.3 | 731.3 | 733.1 | 210.4 | 303.5 | 355.5 | 657.6 | 567.1 | 567.3 | 621.8 | 578.5 | 335.9 | 425.6 | 406.6 | 390.2 | 374.5 | 505.2 | 391.2
1408 | 1172 | 564.1 | 225.64 | 263.7602 | 420.6 | 389.8 | 356.4 | 362.8 | 539.5 | 69.9 | 17.4 | 123.1 | 5.6 | 195.3 | 5.4 | 866.9 | 849.1 | 270.7 | 872.1 | 730 | 869 | 739.2 | 642.2 | 758.1 | 608.9 | 731 | 732.9 | 210.7 | 303.7 | 355.9 | 658.5 | 567.6 | 577.2 | 622.1 | 581 | 336.2 | 425.1 | 406 | 390.3 | 374.4 | 505.2 | 391.3
1409 | 1173 | 568.5 | 227.4 | 265.8175 | 419.1 | 389.9 | 357.4 | 362.1 | 542.8 | 69.9 | 17.4 | 123.1 | 5.7 | 211.6 | 5.2 | 860.7 | 843.9 | 271 | 873.1 | 729.8 | 870.3 | 738.1 | 641.5 | 751.6 | 609.5 | 730.9 | 732.2 | 211 | 303.9 | 356.1 | 658.4 | 568 | 579 | 622.1 | 581.7 | 336.4 | 424.3 | 405.7 | 390.3 | 374.3 | 505.3 | 391.4
1410 | 1174 | 567.4 | 226.96 | 265.3032 | 418.4 | 389.4 | 358.7 | 361.6 | 543.3 | 69.8 | 17.4 | 123.1 | 5.9 | 211.5 | 4.7 | 858.5 | 839.5 | 271.6 | 875.8 | 729.6 | 871 | 736.5 | 640.8 | 744.2 | 608.7 | 731 | 733 | 211.3 | 304.1 | 356.1 | 657.9 | 567.9 | 576.3 | 622.2 | 580.8 | 336.6 | 423.5 | 405.4 | 390.3 | 374.4 | 505.4 | 391.5
1411 | 1175 | 565.8 | 226.32 | 264.555 | 418.8 | 389.2 | 358.3 | 361.1 | 541 | 69.8 | 17.4 | 123.1 | 5.9 | 186.9 | 4.4 | 856.4 | 838.4 | 272.7 | 878.7 | 729 | 870 | 733.8 | 640.4 | 735.2 | 607.7 | 730.7 | 732.9 | 211.5 | 304.4 | 356 | 657.3 | 568 | 570.4 | 622.1 | 580.3 | 336.8 | 423.1 | 406.3 | 390.4 | 374.7 | 505.4 | 391.6
1412 | 1176 | 565.7 | 226.28 | 264.5083 | 419.6 | 388.9 | 358.2 | 362.1 | 537.4 | 69.9 | 17.4 | 123.2 | 5.7 | 184.3 | 4.2 | 861 | 843.4 | 272.7 | 876.9 | 728.5 | 869.2 | 730.7 | 639.2 | 730.9 | 606.4 | 730.4 | 730.7 | 211.8 | 304.5 | 356.2 | 657.1 | 567.8 | 563.3 | 622.1 | 579.6 | 337 | 423.3 | 406.7 | 390.5 | 374.8 | 505.5 | 391.7
1413 | 1177 | 566.3 | 226.52 | 264.7888 | 418.2 | 388.3 | 357.6 | 363.5 | 532.5 | 69.9 | 17.4 | 123.3 | 5.2 | 196.7 | 4.3 | 865.9 | 842.3 | 272.8 | 874.4 | 728.2 | 870 | 731.2 | 639 | 733.7 | 606 | 730.2 | 731.5 | 212 | 304.7 | 356.3 | 656.8 | 566.7 | 561.4 | 622 | 579 | 337.3 | 423.1 | 406.4 | 390.6 | 374.8 | 505.5 | 391.9
1414 | 1178 | 565.2 | 226.08 | 264.2745 | 417.4 | 388 | 357.6 | 363.9 | 532.6 | 69.9 | 17.4 | 123.3 | 5.5 | 208.9 | 3.9 | 867.9 | 845.4 | 273.9 | 873.8 | 728 | 870.1 | 729.6 | 639.6 | 730.1 | 606.3 | 729.9 | 730.7 | 212.2 | 304.9 | 356.3 | 656.2 | 566.5 | 559.5 | 622 | 579.5 | 337.5 | 423 | 407.2 | 390.7 | 375 | 505.6 | 392
1415 | 1179 | 565.8 | 226.32 | 264.555 | 418.1 | 388.5 | 357.8 | 364.6 | 531.7 | 69.9 | 17.4 | 123.4 | 6.2 | 243.4 | 3.6 | 866.3 | 852.1 | 275.7 | 873.8 | 728 | 868.7 | 727.2 | 639.9 | 728.5 | 606.7 | 729.4 | 729.3 | 212.5 | 305 | 356.4 | 656.2 | 566.7 | 557.7 | 622 | 579.8 | 337.7 | 423.8 | 408.5 | 390.8 | 375.3 | 505.6 | 392.2
1416 | 1180 | 566.8 | 226.72 | 265.0226 | 417.7 | 388.8 | 357.5 | 366.4 | 530.3 | 69.9 | 17.4 | 123.4 | 6.1 | 235.9 | 3.5 | 866.9 | 858.1 | 276 | 872.1 | 728.1 | 867.5 | 725.4 | 640.1 | 733.7 | 606.8 | 729.2 | 728.6 | 212.7 | 305.2 | 356.5 | 655.9 | 566.5 | 556.5 | 621.9 | 579.9 | 338 | 424.3 | 409 | 390.9 | 375.4 | 505.7 | 392.3
1417 | 1181 | 567 | 226.8 | 265.1161 | 416.9 | 388.6 | 357.6 | 367.5 | 527.7 | 70 | 17.4 | 123.5 | 6.1 | 204.8 | 4 | 875.9 | 862.8 | 277.3 | 871 | 728.5 | 867.4 | 725 | 640.4 | 737.9 | 606.5 | 728.9 | 728.5 | 213 | 305.3 | 356.5 | 655.8 | 565.9 | 555.8 | 621.9 | 579.6 | 338.2 | 424.9 | 408.7 | 391 | 375.6 | 505.8 | 392.4
1418 | 1182 | 566.8 | 226.72 | 265.0226 | 415.8 | 389 | 357.4 | 367.5 | 527 | 70 | 17.4 | 123.6 | 6.2 | 203.6 | 4.2 | 877.4 | 861.4 | 278.4 | 871.7 | 728.8 | 868.6 | 726.2 | 640.7 | 741.9 | 606.1 | 728.8 | 729.7 | 213.3 | 305.4 | 356.7 | 655.8 | 565.1 | 556.3 | 622 | 578.9 | 338.5 | 425.7 | 408.8 | 391.1 | 375.7 | 505.9 | 392.6
1419 | 1183 | 566.6 | 226.64 | 264.9291 | 414.7 | 389.8 | 356.8 | 367.3 | 528.1 | 70 | 17.4 | 123.6 | 6.2 | 208.4 | 4.1 | 880.5 | 863 | 278.3 | 871 | 728.9 | 869.5 | 727.7 | 641.1 | 748.7 | 606.5 | 728.9 | 730.5 | 213.5 | 305.4 | 356.8 | 656.1 | 565.3 | 558.7 | 622 | 579 | 338.7 | 426.3 | 408.8 | 391.1 | 375.7 | 505.9 | 392.7
1420 | 1184 | 566.9 | 226.76 | 265.0694 | 414.2 | 390.8 | 356.3 | 366.8 | 530.4 | 70 | 17.4 | 123.6 | 6 | 228.8 | 3.8 | 881.9 | 861.2 | 277.9 | 870.6 | 728.9 | 870.2 | 729 | 642.1 | 752.7 | 606.7 | 728.7 | 730.9 | 213.7 | 305.5 | 356.9 | 656.1 | 565.7 | 558.9 | 622.1 | 579.9 | 338.9 | 426.5 | 409 | 391.2 | 375.9 | 506 | 392.9
1421 | 1185 | 566.7 | 226.68 | 264.9759 | 413 | 391.3 | 356.5 | 367.3 | 530 | 70.1 | 17.4 | 123.6 | 5.9 | 219.7 | 3.8 | 883.7 | 854.3 | 277.3 | 870.5 | 728.7 | 871.6 | 728.2 | 641.3 | 748.5 | 606.1 | 728.8 | 731.1 | 213.9 | 305.6 | 356.9 | 655.9 | 565.1 | 556.5 | 622.1 | 579.1 | 339.1 | 426.4 | 409.2 | 391.3 | 376 | 506 | 393
1422 | 1186 | 566.5 | 226.6 | 264.8823 | 412.2 | 391.1 | 356 | 368.6 | 527.1 | 70.2 | 17.4 | 123.7 | 5.9 | 220.2 | 4.3 | 880.7 | 853.3 | 277.6 | 872.1 | 728.4 | 872.6 | 726.4 | 640.3 | 743.4 | 605.5 | 728.9 | 730.5 | 214.1 | 305.7 | 357 | 655.5 | 564.2 | 552.8 | 622 | 578.3 | 339.3 | 426.5 | 409.2 | 391.4 | 376.2 | 506.1 | 393.1
1423 | 1187 | 566.6 | 226.64 | 264.9291 | 410.7 | 391.2 | 355.2 | 369.2 | 526.3 | 70.2 | 17.4 | 123.8 | 5.6 | 209.6 | 4.5 | 877.8 | 853.3 | 279 | 871.5 | 728.5 | 872.8 | 727.1 | 640.3 | 746 | 605.6 | 728.9 | 731.3 | 214.4 | 305.9 | 357.1 | 655.5 | 563.8 | 550.7 | 622.2 | 578.1 | 339.5 | 426.2 | 409 | 391.4 | 376.2 | 506.1 | 393.3
1424 | 1188 | 566.2 | 226.48 | 264.7421 | 409.5 | 391.6 | 355.5 | 369.5 | 526.3 | 70.3 | 17.4 | 123.9 | 5.9 | 198.5 | 4.9 | 875.3 | 849.1 | 278.2 | 870.5 | 728.6 | 872.5 | 727.3 | 641 | 747.2 | 605.6 | 728.8 | 731.9 | 214.7 | 306 | 357.1 | 655.4 | 563.4 | 549.4 | 622.3 | 577.8 | 339.8 | 426.3 | 409 | 391.5 | 376.4 | 506.2 | 393.4
1425 | 1189 | 565.6 | 226.24 | 264.4615 | 408.9 | 392.3 | 356.2 | 369 | 526 | 70.3 | 17.4 | 123.9 | 6.1 | 204.3 | 4.9 | 878.1 | 849.1 | 280.8 | 871 | 728.7 | 872.2 | 727.2 | 641 | 748.4 | 605.6 | 728.7 | 732 | 214.9 | 306.1 | 357.2 | 655.4 | 562.9 | 548.1 | 622.5 | 577.5 | 340.1 | 427 | 409 | 391.6 | 376.5 | 506.2 | 393.5
1426 | 1190 | 565.1 | 226.04 | 264.2277 | 409.1 | 393.5 | 356.1 | 367.9 | 528.4 | 70.3 | 17.4 | 123.8 | 6.4 | 212.5 | 4.9 | 876.3 | 848.6 | 282.7 | 872.5 | 728.7 | 871.9 | 725.9 | 641.9 | 743.8 | 606.4 | 728.7 | 730.9 | 215.2 | 306.3 | 357.4 | 655.4 | 563.8 | 547.6 | 622.6 | 579.8 | 340.3 | 427.9 | 409.9 | 391.7 | 376.7 | 506.2 | 393.6
1427 | 1191 | 566.9 | 226.76 | 265.0694 | 409.7 | 394 | 355.4 | 367.9 | 528.8 | 70.4 | 17.4 | 123.9 | 6.5 | 211.5 | 4.7 | 867 | 845.8 | 283.7 | 870.7 | 728.6 | 869.3 | 723.4 | 642.6 | 733.1 | 607 | 728.5 | 728.6 | 215.5 | 306.4 | 357.5 | 655.4 | 565 | 546.1 | 622.8 | 580.9 | 340.5 | 428.7 | 410.8 | 391.8 | 377 | 506.3 | 393.8
1428 | 1192 | 566.5 | 226.6 | 264.8823 | 409.7 | 393.5 | 355.3 | 369.4 | 527.4 | 70.5 | 17.4 | 124 | 6.8 | 209.6 | 4.5 | 868 | 848.4 | 283.7 | 867.6 | 728.5 | 867.8 | 718.8 | 640 | 720.3 | 605.7 | 728.4 | 725.7 | 215.9 | 306.5 | 357.6 | 655.3 | 565.8 | 544.3 | 622.7 | 580.8 | 340.8 | 429.2 | 411.5 | 392 | 377.2 | 506.4 | 394
1429 | 1193 | 565.9 | 226.36 | 264.6018 | 409.5 | 393 | 355.3 | 371.6 | 526.2 | 70.5 | 17.4 | 124 | 5.8 | 208.8 | 4.3 | 864 | 843.3 | 284.1 | 865.7 | 728.5 | 866.9 | 716.6 | 640.1 | 716.8 | 604.9 | 728.2 | 725.3 | 216.2 | 306.7 | 357.7 | 654.8 | 565.5 | 541.7 | 622.6 | 580.7 | 341.1 | 429.7 | 412.5 | 392.1 | 377.4 | 506.5 | 394.2
1430 | 1194 | 565.6 | 226.24 | 264.4615 | 409.6 | 393 | 355.2 | 374 | 526.3 | 70.6 | 17.4 | 124 | 5.4 | 208.7 | 3.9 | 863.3 | 838.5 | 283.9 | 863.5 | 728.2 | 866.3 | 713.3 | 638 | 708.9 | 604.4 | 728.3 | 723.2 | 216.4 | 306.8 | 357.8 | 654.5 | 565.5 | 542.6 | 622.7 | 581.4 | 341.3 | 430.9 | 413.7 | 392.4 | 377.8 | 506.7 | 394.4
1431 | 1195 | 566.5 | 226.6 | 264.8823 | 409.5 | 392.7 | 355.2 | 377 | 522.8 | 70.7 | 17.4 | 124 | 5.4 | 213.7 | 3.9 | 868.7 | 844.3 | 284.1 | 861.8 | 727.7 | 867.4 | 711.6 | 635.5 | 710.1 | 603.2 | 728.5 | 722.5 | 216.6 | 307 | 357.8 | 654.2 | 564.7 | 539.6 | 622.6 | 580.1 | 341.6 | 431.8 | 414.6 | 392.5 | 377.9 | 506.8 | 394.6
1432 | 1196 | 566.8 | 226.72 | 265.0226 | 409.4 | 392.2 | 355.3 | 378.9 | 521.5 | 70.7 | 17.4 | 124 | 5.6 | 228.9 | 3.9 | 865.3 | 842.1 | 284.8 | 861.2 | 727.3 | 868.5 | 712.8 | 635.1 | 713.7 | 603.2 | 728.8 | 722.7 | 216.8 | 307.1 | 357.9 | 654 | 564.3 | 541 | 622.4 | 579.9 | 341.8 | 432.4 | 415.1 | 392.7 | 378.1 | 506.9 | 394.8
1433 | 1197 | 567.2 | 226.88 | 265.2096 | 409.3 | 393.2 | 355.6 | 378.6 | 522.3 | 70.8 | 17.4 | 124 | 6 | 215.4 | 4 | 868.9 | 838.5 | 286.2 | 860.7 | 726.8 | 869.7 | 712.1 | 633.2 | 713.7 | 603 | 729 | 721.9 | 217.1 | 307.2 | 357.9 | 653.9 | 563.6 | 542.5 | 622.4 | 579.2 | 342.1 | 432.7 | 415.3 | 392.8 | 378.3 | 507 | 394.9
1434 | 1198 | 567.2 | 226.88 | 265.2096 | 409.3 | 394.8 | 355.4 | 378.5 | 524.6 | 70.8 | 17.4 | 124 | 6.2 | 223.2 | 4 | 861.4 | 832.2 | 287.7 | 860.7 | 726.4 | 870.7 | 713.4 | 631.3 | 716.3 | 602.5 | 729.1 | 722.5 | 217.4 | 307.3 | 358.1 | 654.1 | 563.8 | 545.7 | 622.6 | 578.5 | 342.3 | 432.7 | 414.6 | 392.8 | 378.4 | 507 | 395.1
1435 | 1199 | 566.8 | 226.72 | 265.0226 | 410.4 | 395.4 | 354.7 | 378.5 | 526.1 | 70.9 | 17.4 | 124 | 6.1 | 212.6 | 4.4 | 856.4 | 828.1 | 288.6 | 861.1 | 725.9 | 871.1 | 713.8 | 629.5 | 716 | 601.2 | 729.2 | 722.7 | 217.6 | 307.5 | 358.2 | 654 | 564 | 546.9 | 622.9 | 577.7 | 342.6 | 432.6 | 413.7 | 392.9 | 378.6 | 507.1 | 395.2
1436 | 1200 | 566.9 | 226.76 | 265.0694 | 412.9 | 395 | 354.5 | 377.5 | 528.1 | 71 | 17.4 | 124 | 6.4 | 196.3 | 4.8 | 855.3 | 830.3 | 288.9 | 861.2 | 726 | 871.2 | 715.5 | 631.6 | 727.8 | 601.3 | 729.2 | 723.7 | 217.9 | 307.8 | 358.3 | 654.1 | 563.1 | 547.5 | 623.4 | 577.2 | 342.8 | 432.7 | 413.3 | 392.9 | 378.7 | 507.1 | 395.3
1437 | 1201 | 566.8 | 226.72 | 265.0226 | 412.3 | 395.1 | 354.4 | 375.9 | 529.6 | 71 | 17.4 | 124 | 5.6 | 210.4 | 5.2 | 860.9 | 835.3 | 289.5 | 861.5 | 726 | 870.8 | 718.5 | 633.5 | 737.2 | 602.1 | 729.1 | 725.9 | 218.2 | 308 | 358.4 | 654.3 | 563.7 | 551.3 | 623.7 | 578.5 | 343 | 432.8 | 413.5 | 393 | 378.9 | 507.2 | 395.5
1438 | 1202 | 566.3 | 226.52 | 264.7888 | 411.3 | 395.1 | 354.2 | 374.7 | 528.1 | 71 | 17.4 | 124 | 5.7 | 202 | 5 | 864.5 | 836.3 | 290.4 | 861.3 | 726 | 870.5 | 719.3 | 634.2 | 739.7 | 602.7 | 729.1 | 726.6 | 218.5 | 308.2 | 358.4 | 653.9 | 563.5 | 548 | 623.9 | 578.4 | 343.3 | 432.5 | 413.9 | 393 | 379.2 | 507.2 | 395.6
1439 | 1203 | 566 | 226.4 | 264.6486 | 410 | 394.5 | 353.5 | 373.7 | 526.6 | 71 | 17.4 | 124.2 | 6.3 | 194.1 | 4.1 | 863.9 | 836.5 | 291.8 | 862 | 726.3 | 870.5 | 720.7 | 634.9 | 744.7 | 602.9 | 729.1 | 727.8 | 218.6 | 308.3 | 358.6 | 654.2 | 563.6 | 549.6 | 624.1 | 578.6 | 343.5 | 432 | 414 | 393.1 | 379.2 | 507.3 | 395.8
1440 | 1204 | 566.2 | 226.48 | 264.7421 | 409 | 394.3 | 353.1 | 373.1 | 528.2 | 71 | 17.4 | 124.3 | 6.4 | 195.4 | 4 | 858.9 | 832.5 | 293.3 | 862.9 | 726.5 | 870.7 | 724.1 | 637 | 749 | 603.4 | 729.3 | 729.4 | 218.9 | 308.5 | 358.7 | 654.1 | 563.9 | 552.7 | 624.6 | 578.2 | 343.7 | 431.3 | 413.8 | 393.1 | 379.3 | 507.3 | 395.9
1441 | 1205 | 566.9 | 226.76 | 265.0694 | 408.8 | 393.6 | 353.9 | 372.2 | 528.8 | 70.9 | 17.4 | 124.4 | 6.3 | 212.9 | 4 | 860 | 831.1 | 293.6 | 862.9 | 726.5 | 871.2 | 726.5 | 638.5 | 752.3 | 603.5 | 729.3 | 731.5 | 219.1 | 308.6 | 358.8 | 653.9 | 563.6 | 553.6 | 625 | 577.7 | 343.9 | 430.5 | 413.8 | 393.2 | 379.4 | 507.4 | 396
1442 | 1206 | 565.7 | 226.28 | 264.5083 | 408.6 | 392.8 | 355.1 | 371.4 | 528.8 | 70.9 | 17.4 | 124.3 | 6.2 | 220.6 | 3.8 | 862.7 | 829.7 | 294.3 | 862.9 | 726.5 | 871.8 | 727.9 | 638.6 | 753.8 | 602.6 | 729.4 | 732.6 | 219.4 | 308.8 | 358.8 | 653.3 | 563.8 | 553 | 625.4 | 576.9 | 344.1 | 429.7 | 413.3 | 393.2 | 379.4 | 507.4 | 396.1
1443 | 1207 | 567.4 | 226.96 | 265.3032 | 408.5 | 392.3 | 356 | 370.5 | 526.7 | 70.8 | 17.4 | 124.3 | 6.1 | 207.1 | 3.6 | 861.3 | 824.8 | 295.7 | 863.3 | 726.5 | 871.8 | 729.7 | 639.9 | 755.2 | 602.3 | 729.2 | 733.8 | 219.6 | 309 | 358.9 | 653 | 562.8 | 551.3 | 625.3 | 576.1 | 344.3 | 428.8 | 412.9 | 393.2 | 379.4 | 507.4 | 396.2
1444 | 1208 | 567.5 | 227 | 265.3499 | 409 | 391.7 | 356.6 | 369.5 | 526.3 | 70.8 | 17.4 | 124.3 | 6 | 195.9 | 3.4 | 855.6 | 821 | 297.3 | 863.5 | 726.6 | 871.8 | 729 | 639.8 | 747.8 | 602.4 | 729.1 | 734.2 | 219.9 | 309.2 | 359 | 653 | 562.6 | 551.2 | 625.4 | 576.1 | 344.5 | 427.8 | 412.7 | 393.3 | 379.5 | 507.4 | 396.4
1445 | 1209 | 568.9 | 227.56 | 266.0045 | 408.4 | 391.7 | 356.5 | 368.6 | 527.3 | 70.8 | 17.4 | 124.4 | 6.2 | 208.5 | 3 | 862.1 | 826.3 | 299.2 | 862.9 | 726.8 | 870.6 | 726.4 | 639.3 | 741.9 | 602.1 | 729 | 733.4 | 220.2 | 309.5 | 359.1 | 652.9 | 563 | 551.8 | 625.3 | 577.4 | 344.8 | 427.3 | 412.1 | 393.3 | 379.5 | 507.5 | 396.5
1446 | 1210 | 567.3 | 226.92 | 265.2564 | 407.4 | 392 | 356.3 | 368.8 | 525.5 | 70.8 | 17.4 | 124.6 | 6.4 | 216.2 | 3.5 | 861 | 827.1 | 300.3 | 862.1 | 726.9 | 870.5 | 724.3 | 640.3 | 745.5 | 602.5 | 728.9 | 732.9 | 220.5 | 309.9 | 359.1 | 652.7 | 563.2 | 549.1 | 625.2 | 578.4 | 345 | 427.1 | 411.6 | 393.4 | 379.5 | 507.5 | 396.6
1447 | 1211 | 564.9 | 225.96 | 264.1342 | 406.4 | 391.7 | 356.5 | 369.4 | 525.1 | 70.8 | 17.4 | 124.7 | 6 | 203.5 | 4 | 865.2 | 829.5 | 301.2 | 861.9 | 726.9 | 870.6 | 724.4 | 640.8 | 751.3 | 602.4 | 729 | 731.8 | 220.8 | 310.3 | 359.2 | 652.6 | 562.7 | 549.2 | 625.1 | 578.8 | 345.3 | 426.7 | 411.2 | 393.5 | 379.5 | 507.5 | 396.7
1448 | 1212 | 564 | 225.6 | 263.7134 | 407 | 391.6 | 355.9 | 370.1 | 524.3 | 70.8 | 17.3 | 124.8 | 6.4 | 216.5 | 3.7 | 864.4 | 832 | 302.6 | 862.4 | 727 | 870.9 | 726.4 | 642.9 | 757.9 | 603.6 | 728.6 | 733.5 | 221.1 | 310.7 | 359.3 | 652.6 | 562.7 | 549.7 | 625.1 | 578.8 | 345.6 | 426.2 | 411.2 | 393.5 | 379.7 | 507.6 | 396.8
1449 | 1213 | 565.7 | 226.28 | 264.5083 | 408.6 | 391.9 | 355.5 | 370.2 | 525.1 | 70.8 | 17.3 | 124.9 | 6.2 | 260.4 | 3.3 | 860.4 | 833.1 | 303.1 | 862.7 | 727.2 | 870.8 | 728.2 | 643.4 | 763.6 | 603.9 | 728.5 | 732.8 | 221.4 | 310.9 | 359.4 | 652.9 | 562.9 | 551.9 | 625 | 578.1 | 345.8 | 425.9 | 411.1 | 393.6 | 379.8 | 507.6 | 396.9
1450 | 1214 | 565 | 226 | 264.181 | 408 | 392.1 | 355.8 | 370.1 | 527 | 70.8 | 17.4 | 124.9 | 6.2 | 271.2 | 2.7 | 862.1 | 837.5 | 305.3 | 863.4 | 727.4 | 870.8 | 731.6 | 645.5 | 769.1 | 604.8 | 728.5 | 735.1 | 221.7 | 310.9 | 359.6 | 653.3 | 563.4 | 555.7 | 625 | 578.4 | 346.1 | 425.5 | 411.1 | 393.6 | 379.8 | 507.7 | 397.1
1451 | 1215 | 567.1 | 226.84 | 265.1629 | 407.7 | 392.9 | 356.6 | 369.6 | 528.4 | 70.7 | 17.3 | 124.9 | 6.1 | 242 | 2.1 | 862.5 | 845.3 | 306.8 | 864.5 | 727.8 | 871.1 | 734.1 | 648.1 | 775.9 | 605.8 | 728.5 | 736.6 | 222.1 | 310.9 | 359.7 | 653.6 | 563.3 | 558.8 | 625.3 | 579.2 | 346.4 | 425 | 411.3 | 393.7 | 379.8 | 507.7 | 397.1
1452 | 1216 | 566.4 | 226.56 | 264.8356 | 408.3 | 394.4 | 356.6 | 368.9 | 529.5 | 70.7 | 17.3 | 124.9 | 6.1 | 200.9 | 2.7 | 868.6 | 852.7 | 308.2 | 866 | 728.1 | 870.5 | 735.4 | 651.2 | 777.7 | 606.9 | 728.2 | 737.3 | 222.4 | 310.9 | 359.8 | 653 | 564 | 560.1 | 625.4 | 580.8 | 346.7 | 424.9 | 411.5 | 393.7 | 379.9 | 507.7 | 397.3
1453 | 1217 | 566.4 | 226.56 | 264.8356 | 409.3 | 395 | 356.1 | 368.4 | 531 | 70.6 | 17.3 | 125 | 5.8 | 211.3 | 3.6 | 868.8 | 852.7 | 310.6 | 866.8 | 728.3 | 870 | 734.5 | 651.6 | 775 | 607.4 | 728.1 | 737 | 222.6 | 310.8 | 359.9 | 653 | 565 | 559.8 | 625.6 | 581.2 | 347 | 425.4 | 410.9 | 393.8 | 379.9 | 507.8 | 397.4
1454 | 1218 | 567.3 | 226.92 | 265.2564 | 409.7 | 395.1 | 356.3 | 368.7 | 530.4 | 70.5 | 17.3 | 125 | 5.8 | 215.8 | 4.3 | 869.7 | 853 | 312.6 | 866.6 | 728.3 | 869.8 | 732.5 | 652.2 | 764.8 | 607.8 | 727.8 | 735.6 | 222.9 | 310.7 | 360 | 652.6 | 565.4 | 556.7 | 625.7 | 581.6 | 347.3 | 425.5 | 410.5 | 393.9 | 379.9 | 507.9 | 397.6
1455 | 1219 | 566 | 226.4 | 264.6486 | 409.5 | 395.3 | 356.7 | 369.3 | 529 | 70.5 | 17.3 | 125 | 5.7 | 196.1 | 4.8 | 870.6 | 856.7 | 312.2 | 865.6 | 727.9 | 870.4 | 730 | 650.3 | 763.4 | 606.7 | 727.7 | 733.8 | 223.2 | 310.7 | 360 | 652.5 | 564.9 | 554.1 | 625.8 | 579.4 | 347.5 | 425.5 | 410.2 | 394 | 380 | 508 | 397.7
1456 | 1220 | 565.3 | 226.12 | 264.3213 | 408.4 | 394.7 | 356.2 | 369.5 | 528.9 | 70.5 | 17.3 | 124.9 | 5.7 | 208.8 | 5 | 870.7 | 853.5 | 312.4 | 864.9 | 727.6 | 871.1 | 728 | 648.4 | 757.7 | 606.4 | 727.9 | 732.9 | 223.5 | 310.8 | 360.1 | 652.5 | 564.7 | 554 | 625.8 | 579 | 347.8 | 425.7 | 410 | 394.2 | 380.1 | 508 | 397.8
1457 | 1221 | 564.9 | 225.96 | 264.1342 | 408 | 395.1 | 356 | 369.8 | 526.9 | 70.4 | 17.3 | 125 | 5.8 | 215.4 | 4.9 | 864.8 | 845.4 | 314.5 | 864 | 727.4 | 871.7 | 725 | 646.7 | 749.6 | 606 | 728 | 731.6 | 223.8 | 310.9 | 360.1 | 652.1 | 564.6 | 550.5 | 625.8 | 578.1 | 348.1 | 425.9 | 409.8 | 394.3 | 380.2 | 508.1 | 398
1458 | 1222 | 564.1 | 225.64 | 263.7602 | 407.8 | 396 | 356 | 370.2 | 525.3 | 70.4 | 17.3 | 125.1 | 6.2 | 214 | 4.9 | 859.5 | 835.1 | 313.4 | 862.4 | 727.2 | 871 | 722.6 | 645.4 | 741.7 | 605.5 | 727.9 | 730.5 | 224.2 | 311.1 | 360.2 | 652 | 564.6 | 546.2 | 625.8 | 578 | 348.4 | 426.3 | 410.4 | 394.5 | 380.3 | 508.1 | 398.1
1459 | 1223 | 564.4 | 225.76 | 263.9004 | 407.6 | 396.2 | 355.8 | 370.4 | 523.6 | 70.4 | 17.3 | 125.3 | 6.7 | 217.3 | 5 | 857.6 | 820.7 | 313.5 | 860.9 | 727.1 | 870.7 | 722.8 | 645.4 | 741.1 | 604.8 | 727.8 | 731.3 | 224.6 | 311.3 | 360.3 | 652.2 | 564.5 | 544.5 | 625.8 | 576.9 | 348.7 | 426.5 | 410.1 | 394.6 | 380.4 | 508.2 | 398.3
1460 | 1224 | 567.3 | 226.92 | 265.2564 | 407.4 | 395.6 | 356 | 370.4 | 523.4 | 70.4 | 17.3 | 125.2 | 6.3 | 228.3 | 5.2 | 853.5 | 811.9 | 315.6 | 860.2 | 726.8 | 870.3 | 726.1 | 643.9 | 739.3 | 603.9 | 727.9 | 733.6 | 225 | 311.7 | 360.4 | 652.2 | 563.8 | 544.6 | 625.8 | 575.8 | 348.9 | 426 | 409.9 | 394.7 | 380.5 | 508.3 | 398.4
1461 | 1225 | 568.6 | 227.44 | 265.8643 | 408.1 | 395.7 | 356.2 | 370.2 | 524.5 | 70.5 | 17.3 | 125.2 | 5.5 | 209.1 | 5.4 | 855.9 | 816.8 | 317.1 | 859.6 | 726.4 | 869.6 | 726.6 | 641.2 | 740.1 | 602.4 | 727.8 | 734.8 | 225.3 | 312 | 360.5 | 651.9 | 563.1 | 543.1 | 625.8 | 574.8 | 349.2 | 426.1 | 410.1 | 394.8 | 380.6 | 508.3 | 398.5
1462 | 1226 | 568 | 227.2 | 265.5837 | 408.9 | 396.4 | 356.1 | 369.1 | 525.5 | 70.6 | 17.3 | 125.2 | 5.5 | 217.2 | 6.2 | 859.1 | 818.9 | 316.4 | 859.2 | 726.6 | 868.8 | 728.8 | 642.2 | 749.6 | 602.7 | 727.6 | 735.7 | 225.7 | 312.2 | 360.6 | 651.8 | 563.2 | 542.1 | 626 | 574.9 | 349.5 | 426.3 | 410.6 | 394.9 | 380.7 | 508.3 | 398.6
1463 | 1227 | 564.7 | 225.88 | 264.0407 | 408.5 | 396.3 | 356.4 | 368.4 | 525.1 | 70.7 | 17.3 | 125.1 | 6 | 224.1 | 6.6 | 862.6 | 830.3 | 318.1 | 858.8 | 726.6 | 868.3 | 727.9 | 642.6 | 745.2 | 603.4 | 727.5 | 734.8 | 226 | 312.3 | 360.7 | 652.3 | 563.6 | 542.2 | 626.1 | 578.9 | 349.7 | 426.5 | 411.1 | 395 | 380.8 | 508.4 | 398.7
1464 | 1228 | 565.8 | 226.32 | 264.555 | 408.2 | 396 | 356.4 | 369.2 | 524.1 | 70.8 | 17.3 | 125.1 | 5.8 | 207.9 | 6.5 | 861.4 | 834.5 | 321.2 | 858.4 | 726.9 | 868.5 | 726.9 | 644.3 | 740.3 | 604 | 726.9 | 735.2 | 226.3 | 312.3 | 360.9 | 652.6 | 564.2 | 545.6 | 626 | 582 | 350 | 426.6 | 411.9 | 395.1 | 380.8 | 508.4 | 398.8
1465 | 1229 | 566.8 | 226.72 | 265.0226 | 408.4 | 396.8 | 356.5 | 370.3 | 524.3 | 70.9 | 17.3 | 125 | 6.1 | 176.1 | 6.4 | 865.7 | 839.4 | 323.8 | 857.3 | 727 | 867.8 | 723 | 643.4 | 734.4 | 604 | 726.7 | 733 | 226.7 | 312.2 | 360.9 | 652.5 | 564.7 | 544.8 | 626 | 582.4 | 350.2 | 427.7 | 413 | 395.2 | 381.1 | 508.5 | 398.9
1466 | 1230 | 567.2 | 226.88 | 265.2096 | 408.4 | 397.5 | 357.2 | 372 | 522 | 71 | 17.3 | 124.9 | 5.9 | 212 | 6.3 | 871.5 | 842.9 | 323.8 | 856.5 | 727.1 | 867.5 | 721.9 | 644.5 | 737.6 | 604.1 | 726.6 | 732.1 | 227 | 312.1 | 361 | 652.4 | 564.3 | 543.1 | 626 | 581.3 | 350.5 | 429 | 413.4 | 395.3 | 381.4 | 508.6 | 399.1
1467 | 1231 | 567.7 | 227.08 | 265.4434 | 408.1 | 397.5 | 357.9 | 373.5 | 521.4 | 71 | 17.3 | 124.9 | 6.4 | 215.5 | 5.9 | 867.1 | 839.5 | 325.3 | 855.5 | 726.8 | 867.3 | 719.8 | 643.2 | 736.5 | 603.9 | 726.8 | 730.8 | 227.2 | 312 | 361.1 | 652.5 | 564.2 | 543.3 | 625.9 | 580.8 | 350.7 | 430 | 413.6 | 395.5 | 381.6 | 508.7 | 399.3
1468 | 1232 | 567.9 | 227.16 | 265.537 | 408 | 398 | 357.9 | 374.1 | 521.1 | 71.1 | 17.3 | 124.8 | 6.4 | 221 | 6.3 | 869.2 | 834.4 | 323.8 | 854.3 | 726.6 | 867.6 | 716.9 | 642.6 | 737.8 | 604.1 | 727 | 729.6 | 227.5 | 311.8 | 361.2 | 652.3 | 563.8 | 542 | 625.8 | 579.7 | 350.9 | 431 | 414.1 | 395.6 | 381.9 | 508.8 | 399.5
1469 | 1233 | 568.6 | 227.44 | 265.8643 | 407.7 | 398 | 357.8 | 375.2 | 521.5 | 71.2 | 17.3 | 124.8 | 6.3 | 220.7 | 6.2 | 866.1 | 837.4 | 323.7 | 854.3 | 726.5 | 868.6 | 717 | 642.2 | 739.8 | 603.9 | 726.8 | 729.1 | 227.8 | 311.7 | 361.2 | 652.3 | 563.6 | 542.6 | 626 | 579.2 | 351.2 | 431.6 | 414.8 | 395.8 | 382.1 | 508.9 | 399.6
1470 | 1234 | 567.4 | 226.96 | 265.3032 | 407.1 | 397.8 | 357.9 | 376 | 522.6 | 71.3 | 17.3 | 124.8 | 6 | 216.5 | 6 | 871.8 | 841.9 | 325.2 | 854.7 | 726.6 | 870.1 | 717.2 | 640.5 | 737.8 | 603.5 | 726.9 | 728.8 | 228.1 | 311.5 | 361.3 | 652.3 | 563.6 | 545.4 | 625.9 | 580.2 | 351.4 | 432.1 | 415 | 395.9 | 382.2 | 509 | 399.7
1471 | 1235 | 565.2 | 226.08 | 264.2745 | 406.3 | 398.2 | 357.4 | 376 | 521.8 | 71.4 | 17.3 | 125 | 6.1 | 214.9 | 6 | 870.9 | 842.1 | 324.4 | 855 | 726.4 | 870.7 | 716.2 | 639.4 | 732.9 | 603 | 727 | 727.8 | 228.5 | 311.5 | 361.4 | 652.2 | 562.5 | 543.1 | 626.1 | 579.3 | 351.7 | 432.1 | 415.3 | 396 | 382.4 | 509.1 | 399.9
1472 | 1236 | 566.5 | 226.6 | 264.8823 | 406 | 398.6 | 357.3 | 376 | 522.5 | 71.4 | 17.3 | 125.1 | 5.5 | 232.6 | 5.4 | 869.8 | 838.5 | 323.3 | 855.3 | 726.3 | 871.4 | 717.7 | 640.2 | 741.9 | 602.8 | 726.8 | 729.3 | 228.8 | 311.4 | 361.4 | 652.1 | 562.2 | 542.5 | 626.4 | 578.7 | 351.9 | 431.7 | 415.6 | 396.1 | 382.6 | 509.1 | 400
1473 | 1237 | 567.6 | 227.04 | 265.3967 | 406.4 | 398.7 | 357.4 | 376.1 | 523.8 | 71.4 | 17.3 | 125.1 | 5.7 | 239.1 | 5 | 856.9 | 828.2 | 323.6 | 855.1 | 726.3 | 872.5 | 719.1 | 639.6 | 740.6 | 602.9 | 726.7 | 729.3 | 229.1 | 311.4 | 361.6 | 652.1 | 561.8 | 543.7 | 626.7 | 578.8 | 352.2 | 431.3 | 415.7 | 396.2 | 382.6 | 509.2 | 400.1
1474 | 1238 | 567.6 | 227.04 | 265.3967 | 406.4 | 398.6 | 357.6 | 376.6 | 523.9 | 71.4 | 17.3 | 125.2 | 6 | 211.8 | 5.1 | 849.4 | 816.2 | 322.1 | 854.6 | 726 | 873.1 | 719.1 | 637.1 | 732 | 602.2 | 727 | 728.8 | 229.4 | 311.2 | 361.6 | 651.8 | 561 | 543.3 | 626.7 | 577.3 | 352.4 | 430.7 | 415.3 | 396.3 | 382.7 | 509.2 | 400.2
1475 | 1239 | 567.5 | 227 | 265.3499 | 406.4 | 399.2 | 358.4 | 376.3 | 524.4 | 71.4 | 17.3 | 125.3 | 5.8 | 206.8 | 4.3 | 850.3 | 817.4 | 323.5 | 854.2 | 725.3 | 873.2 | 717 | 635.1 | 726.3 | 601.2 | 727.2 | 729.4 | 229.7 | 311 | 361.7 | 651.3 | 560.4 | 541.1 | 626.6 | 576.2 | 352.6 | 430.2 | 415.6 | 396.4 | 382.9 | 509.3 | 400.3
1476 | 1240 | 565.7 | 226.28 | 264.5083 | 406.9 | 399.8 | 359.4 | 375.6 | 524 | 71.5 | 17.3 | 125.5 | 5.8 | 237.3 | 3.8 | 855.6 | 822.1 | 324.9 | 854.1 | 725.3 | 873.3 | 716.6 | 635.5 | 732 | 600.8 | 727 | 728.6 | 230 | 310.8 | 361.9 | 651.2 | 560.2 | 539.5 | 626.6 | 575.7 | 352.9 | 430.3 | 415.8 | 396.4 | 383.1 | 509.3 | 400.4
1477 | 1241 | 565.5 | 226.2 | 264.4148 | 406.7 | 400.1 | 359.4 | 375.1 | 521 | 71.5 | 17.3 | 125.7 | 5.9 | 241.8 | 3.7 | 857.2 | 828.4 | 325.2 | 854.3 | 725.3 | 873.4 | 716 | 635.2 | 732.6 | 600.4 | 726.9 | 728.4 | 230.3 | 310.5 | 361.9 | 651.1 | 559.7 | 538.5 | 626.4 | 576.1 | 353.1 | 430 | 413.6 | 396.5 | 383.2 | 509.3 | 400.5
1478 | 1242 | 565.8 | 226.32 | 264.555 | 406.9 | 400.5 | 359.8 | 373.3 | 518.1 | 71.6 | 17.3 | 125.8 | 6.2 | 212.2 | 4.4 | 855.3 | 833.3 | 327.2 | 855.1 | 725.1 | 874 | 718.4 | 635.3 | 741.9 | 600 | 726.8 | 729 | 230.6 | 310.4 | 362 | 651 | 559.3 | 539.3 | 626.3 | 576.2 | 353.3 | 428.9 | 412.9 | 396.5 | 383 | 509.4 | 400.6
1479 | 1243 | 565.5 | 226.2 | 264.4148 | 408.3 | 400.1 | 360.9 | 371.9 | 520 | 71.6 | 17.3 | 125.9 | 6.3 | 207 | 4.9 | 860.1 | 840.3 | 330.1 | 856 | 724.8 | 874.9 | 721.2 | 635.7 | 746.1 | 600.6 | 726.7 | 729.5 | 230.9 | 310.3 | 362.2 | 651.4 | 559.5 | 542.9 | 626.2 | 576.1 | 353.5 | 427.9 | 412.6 | 396.5 | 383.1 | 509.4 | 400.7
1480 | 1244 | 565.3 | 226.12 | 264.3213 | 410.2 | 399.8 | 361.8 | 371 | 521.8 | 71.7 | 17.3 | 126 | 6.5 | 205.8 | 5.5 | 864.1 | 841.2 | 330.9 | 856.6 | 724.7 | 875.5 | 721.4 | 637 | 744.3 | 601.8 | 726.7 | 729.7 | 231.3 | 310.2 | 362.3 | 651.6 | 560 | 545.5 | 626.3 | 577.6 | 353.7 | 427.3 | 412.9 | 396.6 | 383.4 | 509.5 | 400.8
1481 | 1245 | 565.6 | 226.24 | 264.4615 | 410.3 | 399.8 | 362.5 | 369.7 | 522.6 | 71.8 | 17.3 | 126 | 6 | 207.4 | 5.8 | 869.6 | 844.3 | 331.3 | 856.6 | 724.5 | 875.7 | 720 | 638.4 | 745.9 | 601.9 | 726.4 | 728.9 | 231.6 | 310.3 | 362.3 | 651.4 | 560.1 | 544 | 626.3 | 577.6 | 353.9 | 428 | 413.2 | 396.7 | 383.6 | 509.5 | 400.9
1482 | 1246 | 565.8 | 226.32 | 264.555 | 409.8 | 399.7 | 362.7 | 369 | 520 | 71.9 | 17.3 | 126 | 6 | 210.3 | 5.8 | 874.5 | 842.5 | 333.3 | 856.4 | 724.4 | 876.6 | 721.3 | 640.4 | 752.2 | 602.5 | 726.4 | 729.7 | 232 | 310.2 | 362.3 | 651.5 | 559.3 | 544 | 626.3 | 577.7 | 354.1 | 428.5 | 413.6 | 396.8 | 383.7 | 509.6 | 401
1483 | 1247 | 566.9 | 226.76 | 265.0694 | 409.4 | 400 | 361.5 | 369.6 | 520.3 | 72 | 17.3 | 126 | 6.3 | 235.7 | 5.4 | 874.2 | 838.8 | 334.3 | 856.6 | 724.3 | 877.3 | 723.9 | 643.4 | 757.3 | 603.7 | 726.3 | 731.3 | 232.3 | 310.1 | 362.4 | 651.9 | 559.6 | 547.7 | 626.2 | 578.9 | 354.4 | 429.2 | 414.1 | 397 | 383.8 | 509.7 | 401.1
1484 | 1248 | 566.1 | 226.44 | 264.6953 | 408.5 | 400.6 | 360.9 | 370.1 | 522 | 72.1 | 17.3 | 126.1 | 5.9 | 265.2 | 4.6 | 871.2 | 837.1 | 336 | 856.6 | 724.3 | 877.1 | 721.7 | 644.7 | 748.7 | 604.2 | 726.1 | 731 | 232.7 | 310 | 362.6 | 652 | 560.7 | 549.6 | 626.2 | 581.5 | 354.6 | 429.8 | 414.6 | 397.1 | 384 | 509.7 | 401.3
1485 | 1249 | 564.6 | 225.84 | 263.9939 | 408.2 | 400.8 | 361.2 | 370.8 | 522.4 | 72.2 | 17.3 | 126.3 | 5.3 | 269.9 | 4 | 869.1 | 837.3 | 335.9 | 856.2 | 724.5 | 876.9 | 720.6 | 645.8 | 747.4 | 604.7 | 726.1 | 731.2 | 233.1 | 309.8 | 362.7 | 652 | 561.2 | 550.2 | 626.1 | 582.1 | 354.9 | 430.6 | 415.2 | 397.3 | 384.2 | 509.8 | 401.4
1486 | 1250 | 563.8 | 225.52 | 263.6199 | 407.7 | 401.2 | 361.6 | 371.3 | 524.6 | 72.2 | 17.3 | 126.4 | 6 | 248.2 | 3.5 | 868.9 | 835.8 | 336.6 | 855.6 | 724.6 | 876.7 | 718.8 | 646.1 | 746.4 | 604.8 | 726.1 | 731.3 | 233.5 | 309.6 | 362.8 | 651.7 | 562 | 548.7 | 626.2 | 582 | 355.1 | 431.8 | 416 | 397.5 | 384.4 | 509.9 | 401.5
1487 | 1251 | 564.3 | 225.72 | 263.8537 | 406.6 | 401.4 | 361.7 | 371.3 | 525.1 | 72.2 | 17.3 | 126.4 | 6.1 | 232.9 | 3.3 | 872.4 | 838.7 | 338.3 | 854.8 | 724.9 | 875.9 | 719.1 | 648.1 | 751 | 605.5 | 725.9 | 731.8 | 233.9 | 309.7 | 362.9 | 651.8 | 562.1 | 549.4 | 626.3 | 582.1 | 355.4 | 432.2 | 416.6 | 397.7 | 384.7 | 510 | 401.7
1488 | 1252 | 564.8 | 225.92 | 264.0875 | 405.5 | 401.7 | 362.3 | 372.1 | 525.7 | 72.2 | 17.3 | 126.3 | 6.6 | 238.4 | 3.1 | 875.1 | 844.4 | 337.6 | 855.1 | 725.2 | 876.2 | 721.5 | 649.8 | 755.9 | 605.8 | 725.8 | 733 | 234.2 | 309.8 | 363.1 | 652.1 | 561.9 | 551.8 | 626.4 | 582 | 355.7 | 432.3 | 416.9 | 397.9 | 384.9 | 510.1 | 401.9
1489 | 1253 | 566.2 | 226.48 | 264.7421 | 406.4 | 402.6 | 363.5 | 372.9 | 528.4 | 72.2 | 17.3 | 126.3 | 5.9 | 243.9 | 3.3 | 875.7 | 845.4 | 338.9 | 855.9 | 725.4 | 876.7 | 723.4 | 649.3 | 757 | 606.5 | 725.8 | 732.3 | 234.6 | 309.9 | 363.4 | 652.7 | 562.1 | 554.8 | 626.4 | 581.2 | 356 | 432.4 | 416.9 | 398.1 | 385 | 510.2 | 402
1490 | 1254 | 565.9 | 226.36 | 264.6018 | 407.3 | 402.6 | 364 | 372.8 | 530.5 | 72.2 | 17.3 | 126.3 | 6 | 239.6 | 3.4 | 876.8 | 843 | 340.5 | 856.7 | 725.5 | 876.9 | 725.8 | 649.8 | 764.3 | 607.2 | 725.6 | 733.4 | 235 | 309.9 | 363.5 | 652.7 | 562 | 559.9 | 626.6 | 580.2 | 356.2 | 432.4 | 416.8 | 398.3 | 385.2 | 510.3 | 402.2
1491 | 1255 | 566.3 | 226.52 | 264.7888 | 407.1 | 403.8 | 364.2 | 372.3 | 532.1 | 72.2 | 17.3 | 126.2 | 5.9 | 199.4 | 3 | 876.3 | 839.2 | 342.4 | 858 | 725.6 | 877.1 | 726.6 | 650.2 | 765.2 | 607.7 | 725.3 | 734.2 | 235.3 | 310 | 363.6 | 653 | 562.5 | 563.4 | 626.7 | 580 | 356.5 | 432.6 | 417 | 398.4 | 385.4 | 510.3 | 402.2
1492 | 1256 | 564.7 | 225.88 | 264.0407 | 406.7 | 405.9 | 363.7 | 371.7 | 531.5 | 72.2 | 17.3 | 126.3 | 6.1 | 178.6 | 2.6 | 868 | 834.4 | 343.6 | 858.5 | 725.5 | 876.8 | 727.6 | 649.8 | 762.5 | 606.9 | 725 | 735.7 | 235.7 | 310.1 | 363.6 | 652.8 | 562 | 562.2 | 626.8 | 579.4 | 356.8 | 433.2 | 417.3 | 398.6 | 385.6 | 510.4 | 402.4
1493 | 1257 | 564 | 225.6 | 263.7134 | 407.1 | 408 | 363.6 | 371.1 | 530.2 | 72.3 | 17.3 | 126.3 | 5.8 | 193.9 | 2.7 | 866.6 | 834.2 | 343.3 | 859.6 | 725.6 | 876.4 | 730.2 | 649.4 | 767.7 | 606.6 | 725 | 736.7 | 236 | 310.2 | 363.8 | 652.8 | 561.8 | 563.9 | 626.9 | 579.1 | 357.1 | 433.2 | 417.9 | 398.7 | 385.6 | 510.4 | 402.5
1494 | 1258 | 564.3 | 225.72 | 263.8537 | 407.1 | 413.5 | 363.3 | 370.5 | 532.4 | 72.4 | 17.3 | 126.3 | 5.8 | 214.1 | 3.3 | 870 | 836.5 | 344.6 | 859.9 | 725.5 | 876.6 | 730.2 | 649.6 | 763.4 | 606.8 | 724.7 | 737.5 | 236.3 | 310.3 | 363.9 | 653.1 | 562.7 | 564.5 | 627 | 580.4 | 357.3 | 433.5 | 417.6 | 398.8 | 385.6 | 510.4 | 402.6
1495 | 1259 | 565 | 226 | 264.181 | 406.7 | 415.8 | 363 | 370.9 | 533.1 | 72.4 | 17.3 | 126.3 | 6.7 | 227.3 | 3.4 | 868.9 | 837.6 | 345 | 860.3 | 725.4 | 876.7 | 729.4 | 649.8 | 764.3 | 606.8 | 724.7 | 737.6 | 236.7 | 310.4 | 364 | 653.3 | 562.8 | 563 | 627 | 580.9 | 357.6 | 433.7 | 418.4 | 398.9 | 385.7 | 510.5 | 402.8
1496 | 1260 | 564.9 | 225.96 | 264.1342 | 406.3 | 416.3 | 362.7 | 371.4 | 534.2 | 72.4 | 17.3 | 126.3 | 6.5 | 220.9 | 3.2 | 871.3 | 841.2 | 345.5 | 860.2 | 725.7 | 876.3 | 728.8 | 650.6 | 765.1 | 607.2 | 724.7 | 737.3 | 237.1 | 310.5 | 364.1 | 653.2 | 562.9 | 564.2 | 627.2 | 582.2 | 357.9 | 433.8 | 418.5 | 399.1 | 385.8 | 510.5 | 402.9
1497 | 1261 | 564 | 225.6 | 263.7134 | 407.6 | 416.3 | 362.9 | 373.5 | 533.7 | 72.4 | 17.3 | 126.3 | 6.1 | 208.7 | 3.1 | 865.9 | 835.5 | 347.2 | 859.9 | 725.9 | 876.4 | 727.6 | 650.9 | 760.3 | 607.6 | 724.7 | 737.1 | 237.6 | 310.7 | 364.2 | 653.2 | 563.2 | 565 | 627.3 | 583.9 | 358.2 | 434 | 418.4 | 399.3 | 385.9 | 510.6 | 403.1
1498 | 1262 | 563.9 | 225.56 | 263.6666 | 407.9 | 415.8 | 364.1 | 375.9 | 532.4 | 72.5 | 17.3 | 126.2 | 6.1 | 205.9 | 3.1 | 866.2 | 838.7 | 348.1 | 859.4 | 725.8 | 876.6 | 728.6 | 650.4 | 762.8 | 607.5 | 724.6 | 738.6 | 238.3 | 310.8 | 364.3 | 653.3 | 562.7 | 562.9 | 627.3 | 582.6 | 358.4 | 433.8 | 418.2 | 399.5 | 386 | 510.7 | 403.2
1499 | 1263 | 566.2 | 226.48 | 264.7421 | 409 | 416.1 | 365.2 | 376.7 | 532.1 | 72.5 | 17.3 | 126.2 | 6.2 | 207.3 | 3.2 | 867.3 | 841.8 | 350.9 | 859.2 | 726 | 876.2 | 730.3 | 650.6 | 767.5 | 608.7 | 724.5 | 739.5 | 239 | 310.9 | 364.5 | 653.4 | 562.3 | 563.9 | 627.5 | 581.6 | 358.7 | 433.8 | 418.5 | 399.7 | 386.3 | 510.8 | 403.3
1500 | 1264 | 566.2 | 226.48 | 264.7421 | 411.6 | 416.2 | 365.8 | 376.7 | 533.7 | 72.5 | 17.3 | 126.1 | 6.4 | 206.7 | 3.3 | 860.6 | 840.5 | 352.2 | 857.8 | 726 | 874.7 | 726.3 | 649.1 | 752.5 | 608.8 | 724.3 | 737.6 | 239.5 | 311 | 364.6 | 653.1 | 563.5 | 561.9 | 627.7 | 582.7 | 359.1 | 434 | 418.9 | 399.9 | 386.6 | 510.9 | 403.5
1501 | 1265 | 566.4 | 226.56 | 264.8356 | 410.8 | 415.9 | 366.7 | 376.8 | 530.2 | 72.6 | 17.3 | 126.1 | 6.1 | 208.8 | 3.3 | 860.8 | 838 | 354 | 856 | 725.6 | 874.5 | 720.9 | 646.3 | 743.1 | 607.4 | 724.1 | 734.6 | 240.1 | 311.1 | 364.6 | 652.7 | 563.5 | 557.8 | 627.7 | 582.2 | 359.4 | 434.2 | 418.9 | 400.1 | 386.6 | 511 | 403.6
1502 | 1266 | 566.2 | 226.48 | 264.7421 | 410.3 | 418 | 366.9 | 377.2 | 528.1 | 72.6 | 17.3 | 126.1 | 5.9 | 209.8 | 3.1 | 864.8 | 832.9 | 353.1 | 855.3 | 725.1 | 875.6 | 718.8 | 644.9 | 739.1 | 606.5 | 724 | 733.9 | 240.6 | 311.2 | 364.6 | 652.6 | 562.5 | 557.3 | 627.7 | 580.8 | 359.7 | 434.6 | 419 | 400.4 | 386.7 | 511.1 | 403.8
1503 | 1267 | 566.4 | 226.56 | 264.8356 | 411.5 | 419.2 | 366.4 | 377.4 | 527.3 | 72.7 | 17.3 | 126.2 | 5.7 | 210.9 | 3 | 859.8 | 827.5 | 352.9 | 853.5 | 724.4 | 876.1 | 715.2 | 642.2 | 724.6 | 604.7 | 724 | 732.7 | 241.2 | 311.2 | 364.7 | 652 | 561.9 | 553.1 | 627.8 | 579.3 | 360 | 435.1 | 419.9 | 400.6 | 387.1 | 511.1 | 404
1504 | 1268 | 565.7 | 226.28 | 264.5083 | 414.2 | 422.2 | 365.8 | 377.8 | 523.2 | 72.7 | 17.3 | 126.2 | 6.2 | 212 | 3 | 842.7 | 814.1 | 351.7 | 850.6 | 723.8 | 874.6 | 710.5 | 638.5 | 711.7 | 602.2 | 723.9 | 730.5 | 241.8 | 311.4 | 364.8 | 651.6 | 560.8 | 547.9 | 627.7 | 577.3 | 360.4 | 436.1 | 420.9 | 400.8 | 387.5 | 511.2 | 404.1
1505 | 1269 | 565.7 | 226.28 | 264.5083 | 415.8 | 426.9 | 364.8 | 380 | 519.2 | 72.6 | 17.3 | 126.2 | 6.4 | 212.6 | 2.9 | 841 | 815 | 351.5 | 847.5 | 723.4 | 872.5 | 705.6 | 635.4 | 701.7 | 599.8 | 723.9 | 728.1 | 242.3 | 311.5 | 365 | 651.3 | 560.7 | 545.7 | 627.5 | 576.7 | 360.7 | 436.9 | 421.7 | 401.1 | 387.9 | 511.3 | 404.3
1506 | 1270 | 566.5 | 226.6 | 264.8823 | 415 | 429.2 | 364 | 382.9 | 517.5 | 72.5 | 17.3 | 126.2 | 5.8 | 206.8 | 3 | 833.5 | 805.1 | 352.2 | 845 | 722.7 | 872.1 | 701.9 | 633.3 | 695.2 | 597.9 | 723.7 | 726.3 | 242.8 | 311.4 | 365.1 | 650.9 | 562.1 | 545 | 627.2 | 578.8 | 361.1 | 438.6 | 422.2 | 401.4 | 388.1 | 511.3 | 404.5
1507 | 1271 | 567.6 | 227.04 | 265.3967 | 414.5 | 430.9 | 364.5 | 385.7 | 517.4 | 72.5 | 17.3 | 126.3 | 5.7 | 198.7 | 3.3 | 831.1 | 801.3 | 353.5 | 842.8 | 722.1 | 871.2 | 698.9 | 630.7 | 689.6 | 594.5 | 723.7 | 724.7 | 243.6 | 311.6 | 365.2 | 650.6 | 562.6 | 543.5 | 627 | 579.9 | 361.5 | 439.4 | 422.3 | 401.7 | 388.2 | 511.4 | 404.7
1508 | 1272 | 567.9 | 227.16 | 265.537 | 413.6 | 431.1 | 365.6 | 386.3 | 515.1 | 72.4 | 17.3 | 126.4 | 5.6 | 201.1 | 3.4 | 845 | 812.1 | 354.9 | 841.7 | 721.7 | 871.2 | 699.5 | 629.1 | 699.6 | 592.4 | 723.7 | 724.3 | 245 | 311.8 | 365.3 | 650.1 | 561.5 | 542.1 | 626.7 | 578.2 | 361.8 | 439.9 | 422.1 | 402 | 388.3 | 511.5 | 404.9
1509 | 1273 | 567.2 | 226.88 | 265.2096 | 413 | 431.4 | 365.8 | 385.3 | 514.3 | 72.4 | 17.3 | 126.5 | 6.1 | 195.6 | 3.2 | 850.2 | 812.2 | 358.2 | 842 | 721.2 | 871.4 | 705.4 | 629.7 | 715.8 | 593.7 | 723.5 | 727.3 | 246.4 | 312 | 365.4 | 650.3 | 560.4 | 546.6 | 626.4 | 578.1 | 362.2 | 439.9 | 421.7 | 402.3 | 388.4 | 511.7 | 405.1
1510 | 1274 | 566.5 | 226.6 | 264.8823 | 412.9 | 434.9 | 367.1 | 383.5 | 516 | 72.4 | 17.3 | 126.6 | 6.1 | 189.5 | 3.1 | 853.7 | 807.1 | 358.3 | 842.9 | 720.5 | 871.6 | 709 | 630.3 | 718.7 | 594.6 | 723.4 | 727.9 | 247.7 | 312 | 365.5 | 650.3 | 560 | 547.4 | 626.3 | 577.7 | 362.6 | 439.8 | 421.4 | 402.5 | 388.5 | 511.7 | 405.2
1511 | 1275 | 567.2 | 226.88 | 265.2096 | 413.1 | 440.6 | 368.1 | 381.6 | 519 | 72.4 | 17.3 | 126.7 | 5.9 | 201.4 | 3.2 | 853.6 | 810.2 | 360.5 | 843.4 | 720.4 | 871.6 | 711.2 | 632.7 | 724.3 | 595.4 | 723.5 | 730 | 249 | 312.2 | 365.6 | 650.3 | 559.7 | 548 | 626.3 | 577.3 | 362.9 | 439.5 | 421.6 | 402.7 | 388.6 | 511.8 | 405.3
1512 | 1276 | 567.1 | 226.84 | 265.1629 | 412.4 | 443.2 | 369 | 380.3 | 520.8 | 72.4 | 17.3 | 126.7 | 6.2 | 209 | 3.3 | 848.2 | 808.5 | 362.6 | 844.2 | 720.3 | 871.7 | 714.1 | 634.2 | 732.7 | 595.9 | 723.5 | 730.7 | 250.2 | 312.2 | 365.7 | 650.3 | 559.2 | 548 | 626.1 | 576.8 | 363.3 | 439.1 | 421.7 | 402.8 | 388.7 | 511.8 | 405.4
1513 | 1277 | 565.8 | 226.32 | 264.555 | 411.4 | 448.1 | 369.6 | 380 | 522.5 | 72.4 | 17.3 | 126.7 | 5.7 | 209.3 | 3.4 | 854.3 | 811.1 | 363.3 | 844.4 | 720.2 | 871.8 | 716.2 | 635.2 | 739.6 | 596.6 | 723.3 | 732.3 | 251.3 | 312.4 | 365.8 | 650.6 | 559.2 | 549.1 | 626.2 | 577 | 363.7 | 439.1 | 422 | 403 | 388.8 | 511.8 | 405.5
1514 | 1278 | 565.7 | 226.28 | 264.5083 | 411.2 | 453.9 | 370 | 379.3 | 525.2 | 72.4 | 17.3 | 126.7 | 6.4 | 216.4 | 3.5 | 862.3 | 819.9 | 364.3 | 844.8 | 720.4 | 871.5 | 717.8 | 637.1 | 747.4 | 598 | 723.1 | 733.4 | 252.3 | 312.6 | 366 | 650.7 | 559.5 | 551.1 | 626.3 | 578 | 364 | 438.7 | 422.1 | 403.2 | 389.2 | 511.9 | 405.6
1515 | 1279 | 565.8 | 226.32 | 264.555 | 411.5 | 462.1 | 370.5 | 377.9 | 527.5 | 72.3 | 17.3 | 126.8 | 6 | 212.9 | 3.4 | 860.5 | 816.5 | 364.1 | 844.7 | 720.4 | 871.1 | 717.2 | 638.2 | 740.6 | 599 | 723.1 | 733.2 | 253.3 | 312.8 | 366.1 | 651 | 560.3 | 552.6 | 626.4 | 580.2 | 364.4 | 439.2 | 422.2 | 403.4 | 389.4 | 511.9 | 405.7
1516 | 1280 | 565.8 | 226.32 | 264.555 | 412.7 | 476.3 | 371.4 | 377.7 | 527.9 | 72.2 | 17.2 | 126.8 | 6 | 200.8 | 3.7 | 864.3 | 816.5 | 365.8 | 843.4 | 720.2 | 870.6 | 713.4 | 637.2 | 729.3 | 599.1 | 722.9 | 731.9 | 254.2 | 313 | 366.3 | 650.7 | 561.1 | 550.3 | 626.6 | 581.4 | 364.7 | 439.4 | 422.4 | 403.6 | 389.6 | 512 | 405.9
1517 | 1281 | 565.9 | 226.36 | 264.6018 | 412.5 | 478.7 | 371.7 | 379.3 | 526.4 | 72.2 | 17.2 | 126.7 | 5.6 | 201.3 | 3.8 | 867.6 | 820.9 | 369.2 | 842.2 | 719.8 | 870.7 | 709.2 | 636.4 | 723.2 | 598 | 722.9 | 730.6 | 255.1 | 313.2 | 366.3 | 650.4 | 560.8 | 547.2 | 626.5 | 581.3 | 365.1 | 439.5 | 422.6 | 403.8 | 389.8 | 512.1 | 406.1
1518 | 1282 | 565.9 | 226.36 | 264.6018 | 411.6 | 476.7 | 372 | 380.4 | 524.8 | 72.1 | 17.2 | 126.7 | 6 | 210.7 | 4 | 870.7 | 831.2 | 373 | 841.9 | 719.5 | 870.9 | 709.5 | 637 | 727.9 | 599 | 722.9 | 731.7 | 256 | 313.4 | 366.4 | 650.1 | 560.4 | 545.8 | 626.3 | 580.7 | 365.5 | 439.6 | 423.7 | 404 | 390 | 512.3 | 406.2
1519 | 1283 | 567.4 | 226.96 | 265.3032 | 411.4 | 477.2 | 372.1 | 380.4 | 523.6 | 72.1 | 17.2 | 126.6 | 6 | 219.5 | 4.2 | 869.6 | 837.5 | 376.6 | 842.2 | 719.7 | 870.7 | 709.8 | 638.5 | 730.6 | 600.6 | 722.9 | 731.1 | 256.8 | 313.6 | 366.5 | 649.9 | 560.3 | 546.8 | 626 | 581.2 | 365.8 | 440.1 | 424.3 | 404.3 | 390.3 | 512.4 | 406.4
1520 | 1284 | 567.1 | 226.84 | 265.1629 | 412.6 | 475.2 | 372 | 380.9 | 523.9 | 72.1 | 17.2 | 126.6 | 6.2 | 208.6 | 4.4 | 873.4 | 838 | 380 | 841.9 | 720 | 870.6 | 707.8 | 639.6 | 726.2 | 601.9 | 723 | 729.9 | 257.7 | 313.8 | 366.6 | 649.7 | 560.8 | 547.7 | 626 | 580.9 | 366.2 | 441.3 | 425.2 | 404.6 | 390.6 | 512.5 | 406.6
1521 | 1285 | 566 | 226.4 | 264.6486 | 413.2 | 475.5 | 371.7 | 381.9 | 524.9 | 72 | 17.2 | 126.6 | 6.1 | 191.2 | 4.5 | 873.1 | 840 | 383.7 | 841.2 | 719.9 | 870.4 | 704.6 | 639.7 | 721.6 | 602.6 | 723 | 728.1 | 258.6 | 314 | 366.7 | 649.7 | 561.3 | 545.5 | 626.1 | 581.6 | 366.6 | 442.9 | 426.2 | 404.8 | 390.9 | 512.6 | 406.7
1522 | 1286 | 565.8 | 226.32 | 264.555 | 412.4 | 475.2 | 371.6 | 383.5 | 523.7 | 71.9 | 17.2 | 126.7 | 6.2 | 188.4 | 4.5 | 870.5 | 841.2 | 387.4 | 841.3 | 720 | 870.3 | 701.5 | 639.6 | 721 | 602.3 | 723 | 726 | 259.4 | 314.2 | 366.8 | 649.2 | 561.4 | 543.3 | 626.1 | 581 | 367 | 443.7 | 426.6 | 405.1 | 391 | 512.7 | 406.9
1523 | 1287 | 566 | 226.4 | 264.6486 | 411.9 | 478.3 | 371.9 | 384.3 | 523.7 | 71.9 | 17.2 | 126.7 | 6 | 200.3 | 4 | 869.4 | 844.3 | 390.9 | 842.1 | 720.1 | 871.2 | 704.2 | 640.3 | 732.4 | 602.5 | 723 | 726.4 | 260.1 | 314.2 | 367 | 649.4 | 560.9 | 546.6 | 625.9 | 580.3 | 367.4 | 443.3 | 426.7 | 405.4 | 391 | 512.9 | 407.1
1524 | 1288 | 566 | 226.4 | 264.6486 | 411.4 | 477.5 | 372.2 | 383.3 | 527.2 | 71.9 | 17.2 | 126.7 | 6 | 216.8 | 3.4 | 869.7 | 851.5 | 393.5 | 843.1 | 720.3 | 871.9 | 709.3 | 641.5 | 743.4 | 603.7 | 722.8 | 728.5 | 260.8 | 314.2 | 367.3 | 649.7 | 561 | 552.1 | 625.6 | 580 | 367.8 | 443 | 426.3 | 405.7 | 391 | 513 | 407.2
1525 | 1289 | 566.2 | 226.48 | 264.7421 | 410.9 | 476.2 | 372.6 | 382.2 | 530.4 | 71.9 | 17.2 | 126.8 | 5.8 | 219 | 3.2 | 869.2 | 852.6 | 396.6 | 843.8 | 720.5 | 872.7 | 714.3 | 644.4 | 755 | 605.3 | 722.7 | 729.8 | 261.5 | 314.6 | 367.5 | 650.1 | 561.2 | 558 | 625.5 | 581.2 | 368.3 | 442.5 | 426 | 405.9 | 391.2 | 513.1 | 407.3
1526 | 1290 | 566.6 | 226.64 | 264.9291 | 411.2 | 480.1 | 373.2 | 381.7 | 533.4 | 72 | 17.2 | 127 | 5.7 | 215.7 | 3.4 | 869.2 | 844.1 | 398.6 | 846.1 | 720.6 | 872 | 715.7 | 647 | 756.4 | 606.8 | 722.8 | 730.5 | 262.2 | 314.9 | 367.8 | 649.7 | 562.8 | 557.6 | 625.6 | 582.5 | 368.8 | 442.7 | 426.4 | 406.2 | 391.3 | 513.1 | 407.4
1527 | 1291 | 566.3 | 226.52 | 264.7888 | 411.6 | 487.7 | 373.9 | 381.4 | 531.3 | 72.1 | 17.2 | 127 | 5.9 | 210.2 | 3.6 | 871.4 | 842.7 | 401.5 | 845.5 | 720.6 | 871.7 | 715.6 | 648.4 | 751.9 | 606.7 | 722.7 | 730.9 | 262.9 | 315.3 | 367.7 | 649.5 | 562.6 | 554.9 | 625.5 | 581.9 | 369.2 | 443.9 | 426.9 | 406.5 | 391.4 | 513.2 | 407.6
1528 | 1292 | 566.6 | 226.64 | 264.9291 | 410.8 | 495.2 | 374.6 | 381 | 529.1 | 72.2 | 17.2 | 127 | 5.7 | 199.2 | 3.8 | 873.1 | 849.4 | 405.5 | 844.7 | 720.5 | 871.8 | 715.2 | 648.8 | 749.1 | 606.8 | 722.6 | 731.6 | 263.5 | 315.5 | 367.7 | 649.4 | 561.9 | 552 | 625.5 | 581.1 | 369.7 | 444.9 | 426.8 | 406.8 | 391.4 | 513.3 | 407.8
1529 | 1293 | 565.5 | 226.2 | 264.4148 | 410.7 | 499.9 | 374.1 | 380.8 | 527.8 | 72.2 | 17.2 | 127 | 5.7 | 196.8 | 3.8 | 865.6 | 849.4 | 408.7 | 843.9 | 721 | 871.9 | 716.6 | 650.2 | 755.3 | 607.6 | 722.4 | 732.8 | 264.1 | 315.6 | 367.8 | 649.3 | 561.9 | 551.1 | 625.2 | 581.8 | 370.2 | 445.6 | 426.5 | 407.1 | 391.5 | 513.4 | 408
1530 | 1294 | 566.6 | 226.64 | 264.9291 | 410.7 | 502.2 | 373.4 | 380.3 | 526.3 | 72.3 | 17.2 | 127 | 5.8 | 203 | 3.6 | 866.6 | 850 | 411.3 | 843.5 | 721.4 | 872 | 715.8 | 649.8 | 751.1 | 607.7 | 722.4 | 732.5 | 264.7 | 316 | 367.9 | 649.2 | 562.3 | 552.9 | 625.1 | 582.8 | 370.7 | 445.8 | 426.2 | 407.4 | 391.6 | 513.5 | 408.2
1531 | 1295 | 566.9 | 226.76 | 265.0694 | 410.9 | 499.8 | 373.3 | 380.5 | 525.6 | 72.3 | 17.2 | 127.1 | 6 | 210.3 | 4 | 867.2 | 846.9 | 412.7 | 843.1 | 721.5 | 871.9 | 714.5 | 649.7 | 745.3 | 607.1 | 722.4 | 731.1 | 265.2 | 316.5 | 368 | 649.1 | 562.4 | 553.4 | 625.1 | 582.9 | 371.1 | 446.2 | 426.6 | 407.7 | 391.8 | 513.6 | 408.3
1532 | 1296 | 566.5 | 226.6 | 264.8823 | 410.5 | 498.9 | 373.1 | 380.9 | 524.5 | 72.4 | 17.2 | 127.5 | 6.5 | 217.8 | 4.2 | 861.4 | 842.2 | 414.6 | 842.6 | 721.2 | 872.5 | 712.6 | 647.1 | 738.6 | 606.2 | 722.3 | 730.7 | 265.7 | 317 | 368 | 648.8 | 561.9 | 552.3 | 624.9 | 581.5 | 371.6 | 446.8 | 427.5 | 408 | 391.9 | 513.7 | 408.5
1533 | 1297 | 567 | 226.8 | 265.1161 | 410.8 | 497.6 | 373 | 381.5 | 524.2 | 72.5 | 17.2 | 127.7 | 6 | 197.7 | 4.2 | 855.1 | 837.4 | 416.4 | 841.5 | 720.8 | 872.3 | 710.6 | 646.2 | 729.1 | 606.3 | 722.1 | 730 | 266.1 | 317.2 | 368.1 | 648.4 | 561.6 | 550.1 | 625 | 580.7 | 372.1 | 447.8 | 429.3 | 408.2 | 392.2 | 513.8 | 408.7
1534 | 1298 | 565.3 | 226.12 | 264.3213 | 411.7 | 500 | 373.1 | 382.4 | 524.1 | 72.5 | 17.2 | 127.8 | 6.2 | 192.5 | 4 | 846.7 | 830.5 | 418.4 | 839.6 | 720.5 | 870.2 | 708 | 644.6 | 713.3 | 605.8 | 721.9 | 728.1 | 266.6 | 317.5 | 368.3 | 648.5 | 562 | 548.1 | 625.1 | 581 | 372.6 | 449.1 | 429.8 | 408.5 | 392.4 | 513.9 | 408.9
1535 | 1299 | 564.8 | 225.92 | 264.0875 | 412.8 | 501.4 | 373.1 | 383.4 | 523.9 | 72.5 | 17.2 | 127.9 | 6.1 | 201.8 | 3.8 | 850.3 | 833.6 | 420.5 | 837.5 | 720.6 | 868.3 | 703.6 | 643.1 | 699.2 | 604.9 | 721.8 | 724.9 | 267.1 | 317.8 | 368.5 | 648.2 | 563.2 | 545.4 | 625.2 | 581.2 | 373 | 449.5 | 430.8 | 408.8 | 392.7 | 514 | 409.1
1536 | 1300 | 564.1 | 225.64 | 263.7602 | 411.5 | 504 | 374 | 384.9 | 520.4 | 72.5 | 17.2 | 128 | 5.9 | 203.9 | 4.2 | 857.4 | 837.7 | 422.2 | 836.9 | 720.2 | 867.6 | 702 | 642.3 | 703.1 | 603.9 | 721.7 | 723.9 | 267.6 | 318.1 | 368.6 | 647.9 | 563 | 543.5 | 625.2 | 580.5 | 373.5 | 449.9 | 431.2 | 409.1 | 393 | 514.2 | 409.3
1537 | 1301 | 566.3 | 226.52 | 264.7888 | 410.2 | 505.1 | 374.8 | 385.9 | 519.2 | 72.6 | 17.2 | 128.1 | 6.6 | 198.4 | 4.6 | 862.9 | 840.5 | 423.6 | 837.1 | 720.3 | 868 | 700.9 | 641.7 | 708.7 | 603.5 | 721.7 | 723.7 | 268.1 | 318.3 | 368.6 | 648 | 562.3 | 542.7 | 625.3 | 581.6 | 374 | 449.6 | 431.3 | 409.3 | 393.1 | 514.4 | 409.5
1538 | 1302 | 566.8 | 226.72 | 265.0226 | 409.7 | 509.4 | 375 | 386.3 | 518.3 | 72.7 | 17.2 | 128.3 | 6.4 | 201.8 | 5.2 | 865.7 | 840.5 | 425.8 | 837.9 | 720.7 | 868.7 | 704.4 | 642.4 | 718.1 | 602.3 | 721.6 | 725.1 | 268.6 | 318.7 | 368.7 | 647.9 | 561.7 | 542.8 | 625.2 | 581.5 | 374.5 | 449.8 | 431.2 | 409.6 | 393.3 | 514.5 | 409.6
1539 | 1303 | 567.8 | 227.12 | 265.4902 | 409.5 | 513.5 | 375.3 | 386.4 | 519.5 | 72.8 | 17.2 | 128.6 | 5.8 | 207.8 | 5.5 | 864.7 | 846.7 | 426.8 | 839.1 | 721.4 | 868.4 | 706.2 | 644.3 | 721.5 | 604 | 721.5 | 725.2 | 269.2 | 318.9 | 368.9 | 647.9 | 561.6 | 547 | 625 | 582.6 | 375 | 450.1 | 431.1 | 409.9 | 393.4 | 514.7 | 409.8
1540 | 1304 | 567.4 | 226.96 | 265.3032 | 408.9 | 515.3 | 375.5 | 386.3 | 521 | 72.9 | 17.2 | 128.7 | 5.4 | 219.5 | 5.6 | 858.7 | 852.1 | 428.6 | 840.1 | 722 | 867.7 | 709.7 | 646.4 | 730.3 | 604.6 | 721.5 | 725.6 | 269.7 | 319.1 | 369 | 648 | 561.6 | 550.9 | 625 | 583.4 | 375.4 | 450.3 | 430.6 | 410.1 | 393.5 | 514.8 | 409.9
1541 | 1305 | 567.7 | 227.08 | 265.4434 | 408.5 | 512.8 | 375.5 | 386.1 | 524.9 | 72.9 | 17.2 | 128.8 | 6.2 | 210.9 | 5.4 | 859.2 | 853.7 | 429.6 | 840.3 | 722.1 | 867.8 | 717.1 | 648.6 | 746.4 | 606.5 | 721.3 | 727.5 | 270.2 | 319.3 | 369.3 | 648.8 | 561.5 | 560.3 | 625 | 584.5 | 375.9 | 450.2 | 430 | 410.3 | 393.4 | 514.9 | 410.1
1542 | 1306 | 566.1 | 226.44 | 264.6953 | 408.9 | 518.5 | 375.6 | 385.3 | 529.7 | 73 | 17.2 | 128.8 | 5.7 | 210.6 | 5 | 863.3 | 845.8 | 431.6 | 840.7 | 722.2 | 867.7 | 723.4 | 650.3 | 752.5 | 607.8 | 721.3 | 729.6 | 270.7 | 319.5 | 369.6 | 649.2 | 561.7 | 565 | 625.2 | 584.3 | 376.3 | 450.4 | 429.4 | 410.5 | 393.4 | 515 | 410.2
1543 | 1307 | 565.2 | 226.08 | 264.2745 | 409 | 526.6 | 376.5 | 384.3 | 532.2 | 73 | 17.2 | 128.9 | 5.5 | 211.7 | 4.6 | 863.6 | 842.7 | 434 | 841.6 | 722.1 | 867.7 | 725 | 651 | 752.9 | 608.1 | 721.1 | 732.8 | 271.2 | 319.7 | 369.6 | 648.9 | 561.7 | 563.8 | 625.3 | 582.3 | 376.8 | 450 | 429 | 410.6 | 393.6 | 515.1 | 410.3
1544 | 1308 | 566.9 | 226.76 | 265.0694 | 409.4 | 534.1 | 376.1 | 383.4 | 532.4 | 73.1 | 17.2 | 128.9 | 5.8 | 206.8 | 4.6 | 866 | 854.3 | 436.3 | 841.9 | 722.7 | 867.7 | 727.1 | 654.3 | 758.7 | 609.7 | 721 | 734.6 | 271.6 | 320 | 369.7 | 648.8 | 561.3 | 566.4 | 625.2 | 583 | 377.2 | 448.9 | 429 | 410.7 | 393.7 | 515.1 | 410.4
1545 | 1309 | 567.5 | 227 | 265.3499 | 409.5 | 542.3 | 375.7 | 382.6 | 533.2 | 73.1 | 17.2 | 129 | 5.9 | 205.9 | 4.7 | 870.6 | 857.7 | 438.5 | 842.2 | 723.1 | 868.4 | 729.4 | 655 | 758.6 | 610.4 | 720.8 | 734.1 | 272.1 | 320.3 | 370 | 649.5 | 561.3 | 570.4 | 625.5 | 583.7 | 377.6 | 448 | 428.3 | 410.9 | 393.7 | 515.2 | 410.5
1546 | 1310 | 567.5 | 227 | 265.3499 | 410.4 | 552.7 | 376.1 | 381.6 | 536.5 | 73.2 | 17.2 | 129.1 | 6 | 209.6 | 4.7 | 870.5 | 855.9 | 440.6 | 842.9 | 723.1 | 868.7 | 731.4 | 655.2 | 759.9 | 610.8 | 720.4 | 734.3 | 272.5 | 320.6 | 370.2 | 649.6 | 561.9 | 575.8 | 625.6 | 584.1 | 378.1 | 447.1 | 427.6 | 411.1 | 393.6 | 515.2 | 410.6
1547 | 1311 | 565 | 226 | 264.181 | 410.4 | 550.9 | 376.3 | 381.3 | 537.8 | 73.2 | 17.2 | 129.1 | 5.6 | 214.8 | 4.2 | 871.1 | 848.4 | 441.7 | 843.4 | 723.5 | 868.1 | 734.1 | 657.1 | 766.5 | 611.2 | 720.5 | 736.4 | 273 | 321 | 370.2 | 649.6 | 561.8 | 576.5 | 625.6 | 583.9 | 378.5 | 446.5 | 427.2 | 411.2 | 393.5 | 515.3 | 410.7
1548 | 1312 | 566.2 | 226.48 | 264.7421 | 409.7 | 545.6 | 376.9 | 380.8 | 537.5 | 73.3 | 17.2 | 129.1 | 6.3 | 210.3 | 3.6 | 866.2 | 851.8 | 442.1 | 844.6 | 723.9 | 867.2 | 736.9 | 657.9 | 780.9 | 611.4 | 720.5 | 738.8 | 273.4 | 321.4 | 370.4 | 649.6 | 561.7 | 578.8 | 625.6 | 583.6 | 378.9 | 446.9 | 426 | 411.3 | 393.4 | 515.4 | 410.8
1549 | 1313 | 568.4 | 227.36 | 265.7707 | 411.3 | 542.3 | 376.8 | 381 | 539.2 | 73.3 | 17.2 | 129.1 | 6.6 | 187 | 3.1 | 863.3 | 854.3 | 441.2 | 845.3 | 724.4 | 866.7 | 740 | 660.3 | 783.8 | 613 | 720.6 | 739 | 273.8 | 321.7 | 370.6 | 650 | 563.3 | 582.1 | 625.6 | 585.9 | 379.3 | 447.1 | 424.8 | 411.4 | 393.5 | 515.4 | 411
1550 | 1314 | 567.2 | 226.88 | 265.2096 | 412.4 | 545 | 376.9 | 380.9 | 542.5 | 73.4 | 17.2 | 129.1 | 6.5 | 172.6 | 3.2 | 870.7 | 863.8 | 439.9 | 846.7 | 724.4 | 866.6 | 742.3 | 662.1 | 786.2 | 615.1 | 720.2 | 739.9 | 274.3 | 322 | 370.9 | 651.2 | 564.7 | 588.3 | 625.7 | 587.9 | 379.7 | 446.9 | 423.7 | 411.6 | 393.4 | 515.5 | 411.1
1551 | 1315 | 565.9 | 226.36 | 264.6018 | 413.5 | 544.7 | 377.5 | 381.4 | 545.9 | 73.3 | 17.2 | 129.2 | 6.8 | 184.7 | 3.3 | 875.7 | 868.8 | 439.8 | 849.1 | 724.5 | 866.2 | 741.5 | 661.6 | 786.1 | 615.6 | 720.2 | 739.2 | 274.7 | 322.4 | 371.1 | 651.7 | 565.3 | 589.5 | 625.9 | 587.8 | 380.2 | 446.3 | 422.8 | 411.7 | 393.4 | 515.6 | 411.2
1552 | 1316 | 567.8 | 227.12 | 265.4902 | 415.7 | 543.6 | 379.3 | 382.1 | 545.8 | 73.3 | 17.2 | 129.3 | 6.4 | 196.8 | 4 | 877.2 | 865.3 | 441.6 | 852.2 | 724.7 | 864.9 | 740.9 | 662.3 | 783.2 | 616.3 | 719.7 | 738.7 | 275 | 322.7 | 371.2 | 652.2 | 565.8 | 590.2 | 626.3 | 588.5 | 380.6 | 445.5 | 422 | 411.9 | 393.4 | 515.7 | 411.4
1553 | 1317 | 567.2 | 226.88 | 265.2096 | 416.3 | 548.4 | 380.6 | 382.3 | 545.2 | 73.3 | 17.2 | 129.4 | 6 | 198.5 | 4.5 | 874.3 | 863.8 | 442.6 | 855 | 725.1 | 863.9 | 738.2 | 663.2 | 776.5 | 616.6 | 719.2 | 738.1 | 275.4 | 323 | 371.3 | 651.7 | 566.5 | 589.8 | 626.5 | 589.5 | 381 | 445.2 | 421.7 | 412 | 393.5 | 515.8 | 411.5
1554 | 1318 | 565.5 | 226.2 | 264.4148 | 418.6 | 548.5 | 381.3 | 383.3 | 544.3 | 73.4 | 17.2 | 129.5 | 6.5 | 193.3 | 4.7 | 868.5 | 857.5 | 441 | 858.5 | 724.9 | 862.8 | 730.6 | 661.3 | 757.1 | 615.4 | 718.6 | 735.9 | 275.6 | 323.1 | 371.4 | 650.6 | 567.3 | 581.4 | 626.7 | 588.6 | 381.5 | 445.8 | 421.9 | 412.3 | 393.8 | 515.9 | 411.6
1555 | 1319 | 565.8 | 226.32 | 264.555 | 418.5 | 546.5 | 381.6 | 384.5 | 540.5 | 73.5 | 17.2 | 129.6 | 6.3 | 188.1 | 4.6 | 859.8 | 853.4 | 440.6 | 858.9 | 724.4 | 862.8 | 722.8 | 657.9 | 744 | 613.2 | 718.2 | 732.5 | 275.9 | 323.4 | 371.5 | 650 | 566.4 | 575.4 | 626.7 | 585.4 | 381.9 | 446.5 | 422.3 | 412.5 | 393.9 | 516 | 411.8
1556 | 1320 | 565.5 | 226.2 | 264.4148 | 417.9 | 542.6 | 380.8 | 386.9 | 536.3 | 73.5 | 17.2 | 129.7 | 6.5 | 196.9 | 4.4 | 868.7 | 859.4 | 438.9 | 856 | 724 | 863.1 | 719.7 | 656 | 741.9 | 611.9 | 717.5 | 730.8 | 276.2 | 323.7 | 371.6 | 649.6 | 565.5 | 571.2 | 626.6 | 584.2 | 382.4 | 446.9 | 422.3 | 412.8 | 394 | 516.1 | 411.9
1557 | 1321 | 564.3 | 225.72 | 263.8537 | 418.8 | 537.1 | 381.3 | 388.3 | 533.9 | 73.5 | 17.2 | 129.7 | 6.2 | 209.4 | 3.9 | 871.5 | 861.9 | 439.9 | 855 | 724 | 863.8 | 717.8 | 654.1 | 738.9 | 611.1 | 716.5 | 730.7 | 276.4 | 324 | 371.6 | 649.8 | 564.5 | 570 | 626.6 | 583.5 | 382.8 | 447.3 | 421.8 | 413 | 394 | 516.3 | 412.1
1558 | 1322 | 565.6 | 226.24 | 264.4615 | 419.2 | 536 | 381.4 | 387.8 | 531.7 | 73.5 | 17.2 | 129.6 | 6.7 | 220.5 | 3.5 | 869.5 | 860 | 442 | 854.1 | 724.1 | 864.3 | 719.2 | 653.5 | 743.9 | 611 | 716.1 | 730.2 | 276.7 | 324.5 | 371.8 | 650.1 | 564 | 569.9 | 626.7 | 583.1 | 383.3 | 447.3 | 421.3 | 413.2 | 394.1 | 516.3 | 412.2
1559 | 1323 | 567.8 | 227.12 | 265.4902 | 419 | 539.5 | 381.3 | 387.4 | 534.9 | 73.6 | 17.2 | 129.7 | 7.7 | 222.6 | 3.3 | 870.4 | 858.4 | 442.8 | 853.7 | 724.5 | 865.1 | 723.2 | 653 | 754.4 | 611.5 | 715.8 | 731.4 | 276.9 | 324.8 | 372.1 | 650.8 | 564.7 | 576.2 | 626.7 | 584.1 | 383.7 | 447.1 | 420.6 | 413.4 | 394.2 | 516.4 | 412.4
1560 | 1324 | 567 | 226.8 | 265.1161 | 420.5 | 538.6 | 382 | 387.1 | 541 | 73.7 | 17.2 | 129.8 | 7.2 | 216.9 | 3.2 | 875.7 | 860.7 | 444.1 | 855.3 | 724.5 | 865.7 | 724 | 651.8 | 751.1 | 611.8 | 715.5 | 731.5 | 277.2 | 325.1 | 372.3 | 651 | 565.8 | 581.2 | 626.9 | 584.7 | 384.1 | 446.8 | 419.9 | 413.6 | 394.1 | 516.5 | 412.5
1561 | 1325 | 566.8 | 226.72 | 265.0226 | 422.7 | 536.6 | 382.6 | 387 | 542 | 73.8 | 17.2 | 129.9 | 7.3 | 215.1 | 3.5 | 867 | 855.5 | 443.9 | 856.6 | 724.4 | 866.2 | 721.9 | 649.5 | 745.5 | 610.6 | 714.9 | 730.9 | 277.5 | 325.4 | 372.3 | 650.6 | 565.3 | 579.2 | 627 | 583.9 | 384.6 | 446.8 | 419.8 | 413.8 | 394.2 | 516.5 | 412.6
1562 | 1326 | 566.7 | 226.68 | 264.9759 | 423.6 | 530.1 | 383 | 386.8 | 543.9 | 73.9 | 17.2 | 129.9 | 6.9 | 192.9 | 3.9 | 863.8 | 848.7 | 442.8 | 856.9 | 724.1 | 867.1 | 718.5 | 647.9 | 736.7 | 609.7 | 714.3 | 729.7 | 277.8 | 325.6 | 372.3 | 649.6 | 565.7 | 574.5 | 627 | 583.4 | 385 | 446.6 | 419.7 | 414 | 394.2 | 516.6 | 412.7
1563 | 1327 | 565 | 226 | 264.181 | 425 | 532.3 | 382.5 | 387.6 | 542.3 | 74 | 17.2 | 130 | 6.6 | 198.3 | 4.4 | 862.9 | 852.6 | 442 | 855.9 | 723.9 | 866.6 | 714.3 | 646.4 | 730.8 | 608.8 | 713.7 | 728.1 | 278 | 325.8 | 372.4 | 649.4 | 565.7 | 572.1 | 627 | 583.2 | 385.4 | 446.7 | 419.7 | 414.2 | 394.3 | 516.7 | 412.9
1564 | 1328 | 565.6 | 226.24 | 264.4615 | 424.7 | 530.9 | 381.4 | 388.6 | 539.9 | 74.1 | 17.2 | 130 | 6.4 | 209.3 | 4.7 | 858.1 | 848.5 | 442.5 | 854.8 | 723.7 | 864.8 | 709.2 | 645.1 | 721.6 | 608.9 | 713.6 | 726.9 | 278.3 | 326 | 372.6 | 649.3 | 565.7 | 570.6 | 627.1 | 584.1 | 385.9 | 447.3 | 420.7 | 414.3 | 394.6 | 516.7 | 413
1565 | 1329 | 566 | 226.4 | 264.6486 | 424.6 | 527 | 381.2 | 389.2 | 537.9 | 74.2 | 17.2 | 130.1 | 6.3 | 208.5 | 5 | 854.3 | 851.1 | 442.4 | 852.9 | 723.7 | 863 | 702.8 | 643.2 | 710.9 | 608.9 | 713.2 | 723.9 | 278.6 | 326.2 | 372.7 | 649 | 565.9 | 567.6 | 627.4 | 586.3 | 386.3 | 448.2 | 421.8 | 414.5 | 394.8 | 516.8 | 413.2
1566 | 1330 | 565.9 | 226.36 | 264.6018 | 423.8 | 523.1 | 380.7 | 390.8 | 533.7 | 74.2 | 17.2 | 130.1 | 7.1 | 212.1 | 5.4 | 859.9 | 854.3 | 441.5 | 850.7 | 723.6 | 862.1 | 697.9 | 643.6 | 706.5 | 608.2 | 712.7 | 721.6 | 278.9 | 326.5 | 372.9 | 648.9 | 566 | 564.8 | 627.4 | 587.1 | 386.7 | 449.1 | 422 | 414.8 | 395.1 | 517 | 413.4
1567 | 1331 | 565.7 | 226.28 | 264.5083 | 422.9 | 524.5 | 381 | 392.4 | 532.5 | 74.2 | 17.2 | 130.2 | 6.7 | 222.4 | 5.5 | 864.8 | 856.8 | 440 | 850.1 | 723.6 | 862.4 | 696.5 | 644.4 | 709.3 | 607.8 | 711.8 | 720.8 | 279.1 | 326.8 | 372.9 | 649 | 566.3 | 561.2 | 627.4 | 586.2 | 387.2 | 449.9 | 422.6 | 415.1 | 395.4 | 517.1 | 413.6
1568 | 1332 | 565.6 | 226.24 | 264.4615 | 421.8 | 518.2 | 381.7 | 393.1 | 530 | 74 | 17.2 | 130.4 | 6.7 | 220.7 | 5.5 | 864.2 | 854.7 | 438.7 | 849.7 | 724 | 863.1 | 697.4 | 644.5 | 714.2 | 607.6 | 711.4 | 721.6 | 279.4 | 327 | 373 | 648.9 | 565.7 | 559.1 | 627.4 | 584.8 | 387.6 | 450.7 | 423.3 | 415.4 | 395.5 | 517.3 | 413.8
1569 | 1333 | 566.9 | 226.76 | 265.0694 | 420.6 | 511.5 | 381.4 | 393.6 | 528.1 | 73.8 | 17.2 | 130.5 | 6.7 | 212.3 | 5.4 | 872.6 | 853 | 438 | 849.8 | 724.3 | 863.3 | 700.4 | 644.8 | 723.7 | 607.8 | 710.2 | 723.3 | 279.7 | 327.2 | 373 | 648.8 | 564.9 | 559.2 | 627.3 | 583.9 | 388.1 | 451.1 | 423.9 | 415.7 | 395.7 | 517.5 | 414
1570 | 1334 | 567.3 | 226.92 | 265.2564 | 419 | 512.9 | 381.3 | 393.5 | 528.4 | 73.7 | 17.2 | 130.6 | 6.4 | 253.9 | 5.5 | 873.7 | 844.1 | 438.1 | 850.1 | 724.6 | 864 | 703.9 | 644.9 | 729.8 | 607.8 | 708.9 | 724.1 | 280 | 327.3 | 373.2 | 649.1 | 564.9 | 560.1 | 627.2 | 583.5 | 388.5 | 451.3 | 424.7 | 415.9 | 395.9 | 517.6 | 414.1
1571 | 1335 | 566.1 | 226.44 | 264.6953 | 417.7 | 515.8 | 380.4 | 393.3 | 530 | 73.5 | 17.2 | 130.6 | 5.9 | 249.8 | 5.4 | 871.6 | 846.8 | 438.6 | 851.2 | 724.6 | 864.5 | 708 | 645.4 | 737.9 | 608 | 708.6 | 725.3 | 280.3 | 327.6 | 373.3 | 649.5 | 564.7 | 560.7 | 627.3 | 582.5 | 389 | 450.9 | 425.2 | 416.1 | 395.9 | 517.6 | 414.3
1572 | 1336 | 568.1 | 227.24 | 265.6305 | 418.6 | 519.3 | 380 | 391.8 | 531.2 | 73.5 | 17.1 | 130.5 | 6.4 | 239.1 | 5.1 | 871.7 | 856.3 | 439.9 | 852.1 | 724.9 | 864.5 | 711.5 | 645.6 | 742.4 | 608.6 | 708.5 | 726.1 | 280.6 | 327.8 | 373.5 | 649.8 | 564.2 | 563.1 | 627.6 | 582.7 | 389.4 | 451.1 | 425.3 | 416.3 | 396.1 | 517.7 | 414.4
1573 | 1337 | 569.4 | 227.76 | 266.2383 | 420.6 | 522.6 | 380.1 | 390.3 | 532.9 | 73.5 | 17.1 | 130.4 | 6.3 | 247.4 | 4.8 | 879.1 | 867 | 439.7 | 853.9 | 725.3 | 864.6 | 713.8 | 646.5 | 746.1 | 609.5 | 707.1 | 726.2 | 280.9 | 328.1 | 373.6 | 649.5 | 565.3 | 566.6 | 628 | 585.7 | 389.8 | 451.6 | 425.6 | 416.4 | 396.3 | 517.7 | 414.5
1574 | 1338 | 565.3 | 226.12 | 264.3213 | 421.7 | 529.4 | 380.4 | 389.9 | 533.6 | 73.4 | 17.1 | 130.3 | 6.3 | 246.1 | 4.1 | 880.8 | 866.6 | 439 | 855 | 725.5 | 865.3 | 714.4 | 648 | 749.2 | 609.9 | 706.9 | 725 | 281.2 | 328.4 | 373.7 | 648.5 | 565.9 | 566.7 | 628.2 | 586.1 | 390.1 | 451.8 | 425.6 | 416.6 | 396.5 | 517.8 | 414.6
1575 | 1339 | 566.8 | 226.72 | 265.0226 | 421.2 | 536 | 381.1 | 391 | 531.6 | 73.4 | 17.1 | 130.4 | 5.3 | 246.2 | 3.5 | 881.3 | 871.4 | 439.2 | 854.5 | 725.3 | 864.9 | 711.5 | 647.1 | 741.8 | 609.5 | 706.7 | 723.1 | 281.4 | 328.6 | 373.7 | 648.2 | 565.7 | 564.7 | 628.1 | 585.8 | 390.5 | 451.9 | 425.6 | 416.7 | 396.6 | 517.9 | 414.8
1576 | 1340 | 567 | 226.8 | 265.1161 | 420.2 | 537.1 | 381.9 | 392.2 | 529.7 | 73.4 | 17.1 | 130.5 | 5.6 | 253.1 | 3.4 | 877.7 | 863.4 | 439 | 853.9 | 724.9 | 864.4 | 706.7 | 645.5 | 730.3 | 608.1 | 706.2 | 721.1 | 281.6 | 328.8 | 373.9 | 648 | 565.3 | 561.3 | 628 | 585.5 | 390.9 | 451.7 | 426.5 | 416.9 | 396.9 | 518 | 414.9
1577 | 1341 | 566.5 | 226.6 | 264.8823 | 419.2 | 538.9 | 381.9 | 393.1 | 526.1 | 73.4 | 17.1 | 130.8 | 5.7 | 252.7 | 3.5 | 875.6 | 859.3 | 438.5 | 852.2 | 724.4 | 864.3 | 701.8 | 644.1 | 726 | 607 | 705.5 | 719.5 | 281.8 | 329 | 374 | 647.1 | 564.9 | 556.7 | 627.9 | 583.7 | 391.3 | 451.6 | 426.2 | 417.1 | 397 | 518.1 | 415.1
1578 | 1342 | 566.1 | 226.44 | 264.6953 | 418.7 | 539.2 | 381.9 | 393.6 | 522 | 73.5 | 17.1 | 131 | 5.9 | 233.4 | 3.7 | 878.5 | 856.6 | 438 | 851.1 | 724.1 | 864.6 | 701.4 | 646.9 | 728.2 | 606.8 | 705.1 | 720.4 | 282.1 | 329.2 | 374.1 | 647 | 564.4 | 554.3 | 627.8 | 583.4 | 391.7 | 451.5 | 425.6 | 417.3 | 397.1 | 518.2 | 415.2
1579 | 1343 | 566.1 | 226.44 | 264.6953 | 418 | 538.3 | 382.4 | 393.1 | 521.1 | 73.5 | 17.1 | 131.1 | 6.6 | 240.1 | 4 | 876.2 | 852.7 | 437.5 | 850.2 | 723.6 | 864.9 | 701.6 | 646.6 | 732 | 606.4 | 705.4 | 720.6 | 282.4 | 329.4 | 374.1 | 647.1 | 564.4 | 551.9 | 627.6 | 583.4 | 392 | 451.5 | 425.8 | 417.4 | 397.3 | 518.3 | 415.4
1580 | 1344 | 566.1 | 226.44 | 264.6953 | 417.4 | 533 | 382.5 | 392.6 | 520.6 | 73.6 | 17.1 | 131.3 | 6.2 | 235.2 | 3.8 | 870.7 | 847.1 | 436.5 | 848.8 | 723.2 | 865.2 | 699.2 | 645.3 | 723.7 | 606.1 | 704.6 | 720.2 | 282.6 | 329.5 | 374.3 | 646.9 | 564.9 | 549.7 | 627.5 | 583.7 | 392.4 | 452.1 | 427.1 | 417.6 | 397.6 | 518.5 | 415.5
1581 | 1345 | 567.7 | 227.08 | 265.4434 | 417 | 533.9 | 382.1 | 392.3 | 518.3 | 73.6 | 17.1 | 131.3 | 5.9 | 209.9 | 3.8 | 864.8 | 833.4 | 436.1 | 847.5 | 723.1 | 866.6 | 701.1 | 644.2 | 723.9 | 603.8 | 703.8 | 721.2 | 282.8 | 329.8 | 374.4 | 646.5 | 564.4 | 547.5 | 627.3 | 582.3 | 392.7 | 452.2 | 427.5 | 417.8 | 397.6 | 518.6 | 415.7
1582 | 1346 | 566.4 | 226.56 | 264.8356 | 416.5 | 534 | 381.1 | 392.7 | 517.3 | 73.5 | 17.1 | 131.3 | 5.8 | 186.8 | 4.1 | 853.8 | 827.1 | 436 | 846.3 | 722.7 | 866.7 | 700.4 | 640.2 | 714.8 | 602.3 | 703.4 | 721.4 | 283 | 330 | 374.4 | 646.2 | 563.3 | 547.4 | 627.1 | 580.2 | 393.1 | 452.4 | 428.1 | 417.9 | 397.7 | 518.7 | 415.8
1583 | 1347 | 565.7 | 226.28 | 264.5083 | 417 | 540.2 | 381.2 | 392.2 | 516.7 | 73.4 | 17.1 | 131.2 | 5.9 | 217.4 | 4.2 | 857.7 | 832.8 | 436.7 | 845.4 | 722.4 | 865.3 | 702.8 | 638.9 | 726.5 | 601.3 | 702.2 | 722 | 283.1 | 330.1 | 374.5 | 646.2 | 562.3 | 549.1 | 627 | 579 | 393.4 | 452.2 | 428.1 | 418 | 397.9 | 518.7 | 415.9
1584 | 1348 | 564.8 | 225.92 | 264.0875 | 417 | 548.4 | 381.4 | 391.3 | 522.8 | 73.5 | 17.1 | 131.1 | 6.2 | 222.8 | 4.3 | 865.6 | 837.3 | 437.4 | 845.4 | 722.5 | 864.7 | 708.8 | 640.7 | 735.4 | 603.7 | 701 | 721.7 | 283.3 | 330.4 | 375.2 | 648 | 563 | 563.6 | 627.1 | 581.5 | 393.7 | 451.2 | 427.7 | 418.1 | 398 | 518.8 | 416
1585 | 1349 | 566.6 | 226.64 | 264.9291 | 416.4 | 551.7 | 382.1 | 390.1 | 533.2 | 73.4 | 17.1 | 131.1 | 5.9 | 203.9 | 4 | 867.8 | 841.9 | 437.7 | 845.9 | 722.5 | 864.3 | 712.9 | 641.7 | 742.2 | 605.6 | 699.9 | 722.3 | 283.6 | 330.6 | 375.6 | 648.8 | 564.5 | 574.2 | 627.4 | 583.6 | 394 | 450.3 | 427.2 | 418.2 | 397.9 | 518.8 | 416.1
1586 | 1350 | 567.6 | 227.04 | 265.3967 | 416.1 | 553.4 | 383.7 | 387.9 | 537.2 | 73.4 | 17.1 | 131.2 | 5.6 | 212.5 | 4 | 862.6 | 848.1 | 438 | 848.1 | 722.3 | 863.8 | 715.9 | 644.2 | 750.8 | 606.5 | 700.5 | 723.9 | 283.8 | 330.9 | 375.5 | 649.4 | 565.1 | 575 | 627.6 | 583.3 | 394.3 | 449.6 | 426.9 | 418.2 | 398 | 518.9 | 416.2
1587 | 1351 | 568.2 | 227.28 | 265.6772 | 416.9 | 559 | 384.6 | 386.4 | 537.1 | 73.5 | 17.1 | 131 | 5.4 | 211.6 | 4.7 | 864.6 | 856.1 | 438.1 | 849.2 | 722.7 | 864.1 | 719.6 | 647.4 | 759.9 | 607.3 | 700.1 | 726 | 284.1 | 331.1 | 375.5 | 649.4 | 564.8 | 574.3 | 628.1 | 583.1 | 394.6 | 449.2 | 426.3 | 418.3 | 398.1 | 519 | 416.3
1588 | 1352 | 568 | 227.2 | 265.5837 | 417.4 | 562.9 | 384.7 | 386 | 537.2 | 73.5 | 17.1 | 130.8 | 6.2 | 180.8 | 4.8 | 871.7 | 863 | 438.1 | 851.1 | 723 | 864.5 | 721.1 | 649.9 | 762 | 608.6 | 700.1 | 726.6 | 284.4 | 331.2 | 375.5 | 648.7 | 565.5 | 573.9 | 628.7 | 583.2 | 395 | 449.4 | 426.6 | 418.5 | 398.2 | 519 | 416.4
1589 | 1353 | 566.3 | 226.52 | 264.7888 | 418.5 | 562.5 | 384.6 | 385.5 | 537.6 | 73.5 | 17.1 | 130.7 | 6.3 | 206 | 5.1 | 877.8 | 866.8 | 438.3 | 852.7 | 722.8 | 865.2 | 721.5 | 650.2 | 762.5 | 608.6 | 700.2 | 727 | 284.7 | 331.4 | 375.6 | 648.8 | 565.6 | 573.3 | 628.8 | 582.6 | 395.3 | 449.2 | 426.6 | 418.6 | 398.2 | 519.1 | 416.5
1590 | 1354 | 566.7 | 226.68 | 264.9759 | 420.4 | 551.8 | 384.6 | 385.8 | 537.3 | 73.6 | 17.1 | 130.7 | 6 | 223.4 | 5.2 | 877.1 | 872.9 | 438.9 | 854.1 | 722.7 | 865.7 | 723.3 | 650.3 | 759.5 | 608.7 | 699.8 | 727.1 | 285 | 331.6 | 376.1 | 649.3 | 565.8 | 576.1 | 628.8 | 582.6 | 395.6 | 449.3 | 426.2 | 418.7 | 398.2 | 519.2 | 416.6
1591 | 1355 | 565.9 | 226.36 | 264.6018 | 422 | 546.7 | 384.5 | 386.1 | 539.6 | 73.6 | 17.1 | 130.7 | 5.9 | 235.7 | 4.9 | 876.9 | 866 | 439.1 | 857 | 722.9 | 866.2 | 722.5 | 649.9 | 757.6 | 609 | 698.7 | 727.5 | 285.2 | 331.9 | 376.1 | 649.3 | 566.5 | 575.6 | 628.7 | 583.4 | 395.9 | 449.6 | 425.6 | 418.9 | 398.1 | 519.3 | 416.8
1592 | 1356 | 566.5 | 226.6 | 264.8823 | 422.6 | 548.7 | 384.3 | 386.2 | 538.8 | 73.6 | 17.1 | 130.8 | 6.3 | 231.5 | 4.5 | 876.8 | 861 | 440 | 862.4 | 722.7 | 866.1 | 717.3 | 649.4 | 752.3 | 608.9 | 697.3 | 726.1 | 285.5 | 332.1 | 376.1 | 648 | 567.1 | 570.6 | 628.9 | 583.1 | 396.3 | 449.7 | 425.6 | 419.1 | 398.2 | 519.3 | 416.9
1593 | 1357 | 568.3 | 227.32 | 265.724 | 421.4 | 545.7 | 384.5 | 386.5 | 533.8 | 73.7 | 17.1 | 130.8 | 6.1 | 218.3 | 4.5 | 876.4 | 861.1 | 440.2 | 862.3 | 722.6 | 865.3 | 713.5 | 649.7 | 749.6 | 608.2 | 698 | 724.7 | 285.7 | 332.4 | 376.1 | 647.3 | 566.8 | 565.7 | 629 | 582.5 | 396.6 | 449.7 | 425.6 | 419.2 | 398.2 | 519.4 | 417
1594 | 1358 | 567.8 | 227.12 | 265.4902 | 420 | 536.9 | 384.5 | 387.1 | 529.8 | 73.7 | 17.1 | 130.8 | 6 | 203.2 | 5.4 | 875.4 | 857 | 440.2 | 860 | 722.6 | 865.6 | 712 | 649.5 | 750.3 | 607.8 | 697.5 | 725.3 | 285.9 | 332.6 | 376.2 | 647.2 | 565.5 | 564 | 629.1 | 581.8 | 396.9 | 449.4 | 425.9 | 419.4 | 398.2 | 519.4 | 417.2
1595 | 1359 | 566.9 | 226.76 | 265.0694 | 419.2 | 539.6 | 383.9 | 387.4 | 528.1 | 73.6 | 17.1 | 131 | 6.4 | 216.5 | 5.5 | 872.2 | 853.9 | 440.5 | 857.6 | 722.7 | 866 | 711.6 | 650.1 | 751.6 | 607.8 | 697.3 | 726 | 286.2 | 332.9 | 376.3 | 646.9 | 564.6 | 561.3 | 629.2 | 581.9 | 397.2 | 449.9 | 426.3 | 419.6 | 398.4 | 519.5 | 417.3
1596 | 1360 | 567.9 | 227.16 | 265.537 | 418.8 | 549.8 | 383 | 387.1 | 526.4 | 73.6 | 17.1 | 131.1 | 6.4 | 234.8 | 5.4 | 866.8 | 838.7 | 439.7 | 855.3 | 722.9 | 867 | 710.9 | 650.3 | 751.5 | 607.3 | 696.7 | 725.8 | 286.4 | 333.1 | 376.4 | 646.8 | 564.4 | 559 | 629.1 | 581.9 | 397.6 | 451 | 425.9 | 419.8 | 398.5 | 519.6 | 417.5
1597 | 1361 | 566.2 | 226.48 | 264.7421 | 418.3 | 548.1 | 382.4 | 387.2 | 526.1 | 73.6 | 17.1 | 131.2 | 6.7 | 228.4 | 4.8 | 861.1 | 831.2 | 439.8 | 854.4 | 723.1 | 867.4 | 712.2 | 647.4 | 746.7 | 606.2 | 696.2 | 726.4 | 286.7 | 333.4 | 376.5 | 646.5 | 563.8 | 558.7 | 628.7 | 580.2 | 397.9 | 451.5 | 425 | 420 | 398.5 | 519.7 | 417.6
1598 | 1362 | 567.3 | 226.92 | 265.2564 | 418.6 | 556.7 | 382.7 | 386.9 | 526.8 | 73.7 | 17.1 | 131.4 | 7.3 | 242.1 | 4.7 | 858 | 828 | 440.2 | 854.1 | 723 | 867.1 | 713.4 | 645.5 | 742.8 | 605.3 | 695.9 | 727.3 | 287 | 333.6 | 376.7 | 646.6 | 563.8 | 559.1 | 628.6 | 578.7 | 398.2 | 451.4 | 424.3 | 420.1 | 398.5 | 519.7 | 417.7
1599 | 1363 | 568 | 227.2 | 265.5837 | 419.3 | 571.7 | 382.7 | 386 | 526.9 | 73.6 | 17.1 | 131.6 | 7.1 | 217.2 | 4.5 | 860 | 834.2 | 440.2 | 854.8 | 723.1 | 867.6 | 714 | 646.4 | 742.2 | 604.1 | 695.2 | 728.9 | 287.2 | 333.8 | 376.8 | 647 | 563.2 | 558.9 | 629 | 578 | 398.6 | 451.3 | 424.2 | 420.3 | 398.6 | 519.7 | 417.8
1600 | 1364 | 566.3 | 226.52 | 264.7888 | 419.1 | 583.1 | 382.9 | 384.8 | 526.4 | 73.6 | 17.1 | 131.6 | 6.9 | 215.2 | 3.9 | 861.2 | 837.2 | 440.4 | 854.8 | 722.8 | 868.1 | 717.7 | 646.6 | 745 | 603.8 | 694.4 | 730.2 | 287.5 | 334.1 | 376.9 | 647.4 | 562.8 | 561.9 | 629.4 | 578.2 | 398.8 | 451 | 423.9 | 420.4 | 398.7 | 519.8 | 417.9
1601 | 1365 | 564.7 | 225.88 | 264.0407 | 420.1 | 585 | 383.2 | 384 | 528.2 | 73.7 | 17.1 | 131.5 | 6.5 | 226.1 | 3.3 | 862.4 | 842.8 | 442.3 | 855.3 | 722.6 | 868.4 | 720.5 | 646.7 | 750.8 | 604.2 | 693.6 | 729.9 | 287.8 | 334.3 | 377.3 | 647.7 | 563 | 565.7 | 629.6 | 578.7 | 399.1 | 450.7 | 423.6 | 420.5 | 398.8 | 519.8 | 418
1602 | 1366 | 564.5 | 225.8 | 263.9472 | 422.1 | 582 | 383.7 | 383.6 | 533.2 | 73.7 | 17.1 | 131.3 | 6 | 244.6 | 3.4 | 861.5 | 845.3 | 443.4 | 856.8 | 722.6 | 868.2 | 722 | 646.2 | 750.9 | 604.5 | 693.4 | 730.4 | 288 | 334.5 | 377.5 | 647.7 | 563.8 | 569.5 | 629.8 | 579 | 399.4 | 450.3 | 423.2 | 420.6 | 398.8 | 519.8 | 418.1
1603 | 1367 | 566.1 | 226.44 | 264.6953 | 421.9 | 577.1 | 384.7 | 382.8 | 534.6 | 73.8 | 17.1 | 131.2 | 6 | 247.1 | 3.8 | 862.7 | 842 | 443.4 | 858.5 | 722.7 | 868.5 | 722.5 | 647.7 | 755.6 | 604.6 | 693.7 | 732.6 | 288.3 | 334.7 | 377.4 | 648.4 | 563.5 | 570.2 | 629.9 | 579.1 | 399.7 | 450 | 423.3 | 420.7 | 398.9 | 519.8 | 418.2
1604 | 1368 | 568.1 | 227.24 | 265.6305 | 422.1 | 576.7 | 385.1 | 382.2 | 534.5 | 73.8 | 17.1 | 131.1 | 5.9 | 234.8 | 3.9 | 863.9 | 837.8 | 443.8 | 860.9 | 722.6 | 868.4 | 722 | 650.7 | 753.7 | 604.8 | 692.6 | 734.4 | 288.5 | 334.9 | 377.5 | 647.8 | 564.4 | 567.1 | 629.9 | 579.8 | 400 | 450 | 423.6 | 420.8 | 399.1 | 519.9 | 418.3
1605 | 1369 | 566.1 | 226.44 | 264.6953 | 422.8 | 572.5 | 384.8 | 383 | 532.7 | 73.7 | 17.1 | 131.1 | 6.2 | 229.7 | 3.7 | 862.6 | 834.5 | 444 | 859.9 | 722.5 | 867.6 | 722.6 | 650.7 | 758.7 | 604.6 | 692.8 | 735.6 | 288.8 | 335.1 | 377.5 | 647.7 | 564.3 | 566.9 | 629.6 | 580.2 | 400.2 | 450.3 | 423.2 | 420.9 | 399.2 | 520 | 418.4
1606 | 1370 | 565.3 | 226.12 | 264.3213 | 422.6 | 562.3 | 384.6 | 383.9 | 532 | 73.7 | 17.1 | 131.2 | 6.1 | 230.9 | 3.6 | 862 | 831.1 | 445.2 | 859 | 723 | 867.1 | 726.5 | 651.4 | 766.1 | 604.8 | 692 | 737.3 | 289 | 335.4 | 377.7 | 647.6 | 564 | 568.4 | 629.5 | 579.7 | 400.6 | 451.2 | 422.8 | 421.2 | 399 | 520 | 418.6
1607 | 1371 | 567.4 | 226.96 | 265.3032 | 422.7 | 554.2 | 383.9 | 384.6 | 531.9 | 73.8 | 17.1 | 131.1 | 6.1 | 230.1 | 3.4 | 861.3 | 832 | 446.1 | 859.6 | 723.4 | 867 | 728.4 | 652 | 768.7 | 605.1 | 692.5 | 738.6 | 289.3 | 335.6 | 377.7 | 647.3 | 564 | 569.6 | 629.2 | 580.1 | 400.9 | 451.6 | 422.4 | 421.3 | 399.1 | 520 | 418.7
1608 | 1372 | 567 | 226.8 | 265.1161 | 424.1 | 551.8 | 383.4 | 385.1 | 532.6 | 73.7 | 17.1 | 130.9 | 6.2 | 212.8 | 3.4 | 866 | 836.8 | 448.2 | 859.1 | 723.7 | 866.5 | 725.5 | 652.9 | 761.7 | 605.5 | 692.3 | 737.2 | 289.5 | 335.8 | 377.9 | 647.3 | 564.4 | 568.9 | 629.2 | 581.7 | 401.2 | 452.4 | 422.4 | 421.4 | 399.3 | 520.1 | 418.9
1609 | 1373 | 567.3 | 226.92 | 265.2564 | 424.2 | 555.7 | 382.8 | 386.5 | 531.5 | 73.6 | 17.1 | 130.7 | 6.5 | 205.5 | 3.4 | 869.2 | 844.7 | 448.9 | 858.4 | 724 | 866.1 | 720.6 | 653.2 | 751.5 | 603.8 | 693.2 | 734.3 | 289.7 | 336 | 378 | 647.4 | 564.5 | 567.1 | 629.1 | 583 | 401.5 | 453.1 | 422.6 | 421.6 | 399.4 | 520.1 | 419.1
1610 | 1374 | 566.8 | 226.72 | 265.0226 | 423.1 | 556.5 | 382.2 | 388.8 | 529.7 | 73.6 | 17.1 | 130.6 | 6.5 | 228.2 | 4.3 | 865.4 | 847.8 | 449.9 | 857.2 | 724.3 | 865.4 | 715.3 | 653.8 | 744.6 | 603.6 | 693.4 | 732.1 | 289.9 | 336.1 | 378.1 | 646.9 | 564.4 | 564.8 | 629 | 583 | 401.8 | 454.4 | 423 | 421.8 | 399.5 | 520.3 | 419.3
1611 | 1375 | 565.5 | 226.2 | 264.4148 | 421.6 | 555.4 | 383.3 | 390.1 | 529.1 | 73.6 | 17.1 | 130.6 | 6.4 | 202.6 | 5.1 | 865.8 | 851.8 | 451.3 | 856.5 | 724.7 | 865.7 | 717 | 656 | 751.8 | 603.9 | 693.1 | 732.3 | 290.2 | 336.4 | 378.2 | 647.2 | 564.2 | 568.5 | 628.7 | 582.7 | 402.1 | 454.8 | 422.8 | 422.1 | 399.5 | 520.4 | 419.4
1612 | 1376 | 564.5 | 225.8 | 263.9472 | 420.5 | 550.6 | 384.1 | 390.2 | 530.8 | 73.6 | 17.1 | 130.5 | 6.4 | 216.7 | 6.1 | 870.9 | 861.6 | 452.5 | 855.3 | 725 | 866.4 | 723.3 | 656.8 | 757.6 | 605.3 | 693.4 | 734.1 | 290.4 | 336.6 | 378.5 | 647.5 | 563.9 | 572.5 | 628.7 | 582.3 | 402.5 | 454.7 | 422.4 | 422.3 | 399.6 | 520.5 | 419.6
1613 | 1377 | 565.7 | 226.28 | 264.5083 | 421 | 550.9 | 384.2 | 389.9 | 535.5 | 73.6 | 17.1 | 130.5 | 7.2 | 206.1 | 6.3 | 870.4 | 863.3 | 453.9 | 856.2 | 725.1 | 867.4 | 725.9 | 655.1 | 751.1 | 606.4 | 693.1 | 733.6 | 290.6 | 336.8 | 378.9 | 647.9 | 564.2 | 578.4 | 628.7 | 582.1 | 402.8 | 454.5 | 423 | 422.6 | 399.7 | 520.6 | 419.7
1614 | 1378 | 565.7 | 226.28 | 264.5083 | 421.6 | 559.2 | 384.2 | 389.7 | 536.9 | 73.7 | 17.1 | 130.4 | 7 | 213.7 | 6.5 | 871.1 | 866.5 | 454.6 | 857 | 725 | 867.6 | 727.1 | 654 | 753.4 | 606.2 | 693.1 | 733.7 | 290.8 | 337 | 378.9 | 648 | 564 | 577.4 | 628.6 | 580.7 | 403.2 | 454.3 | 423.8 | 422.7 | 399.7 | 520.6 | 419.8
1615 | 1379 | 566.6 | 226.64 | 264.9291 | 421.8 | 561 | 384.9 | 389 | 536.5 | 73.8 | 17.1 | 130.3 | 6.3 | 221.4 | 6 | 870.9 | 862.2 | 456.3 | 857.2 | 725.8 | 868.2 | 728.6 | 655 | 756.4 | 606.7 | 692.4 | 735 | 291 | 337.2 | 379 | 648 | 563.3 | 580.5 | 628.6 | 581.2 | 403.5 | 453.7 | 424.6 | 422.9 | 399.8 | 520.7 | 419.9
1616 | 1380 | 566.6 | 226.64 | 264.9291 | 423.3 | 558 | 385.3 | 388.3 | 536 | 73.8 | 17.1 | 130.2 | 6.3 | 214 | 6.1 | 870.8 | 858.2 | 457.3 | 858.8 | 726.3 | 868.4 | 729.1 | 655.2 | 761.4 | 607.2 | 691.3 | 736.5 | 291.2 | 337.4 | 379 | 647.9 | 563.2 | 579.9 | 628.7 | 581.5 | 403.7 | 453.5 | 424.9 | 422.9 | 399.8 | 520.7 | 420
1617 | 1381 | 567 | 226.8 | 265.1161 | 424.5 | 557.6 | 385.5 | 387.6 | 536.5 | 73.8 | 17.1 | 130.1 | 5.8 | 208.2 | 6.4 | 865.6 | 861.5 | 458.5 | 860.2 | 726.5 | 868.3 | 728.9 | 655.6 | 771.3 | 607.4 | 690.9 | 737.7 | 291.4 | 337.5 | 379.1 | 646.6 | 563.6 | 580.9 | 628.8 | 581.4 | 404 | 453 | 424.5 | 423 | 399.8 | 520.8 | 420.1
1618 | 1382 | 566.7 | 226.68 | 264.9759 | 424.7 | 556.5 | 385.3 | 387.4 | 534.9 | 73.9 | 17.1 | 130 | 5.8 | 201.7 | 7.1 | 862.4 | 859.6 | 459.5 | 859.1 | 726.9 | 867.9 | 728.9 | 657.2 | 775 | 607.8 | 691.2 | 738.6 | 291.6 | 337.8 | 379.1 | 646.5 | 563.6 | 579.9 | 628.9 | 582.4 | 404.2 | 452.3 | 424 | 423.1 | 399.8 | 520.8 | 420.2
1619 | 1383 | 564.8 | 225.92 | 264.0875 | 423.9 | 558.5 | 384.8 | 386.7 | 533.2 | 73.9 | 17.1 | 130.1 | 5.8 | 199.7 | 7.8 | 858.8 | 847.4 | 461.1 | 858.9 | 726.9 | 867.8 | 730.6 | 657.4 | 774.1 | 607.4 | 691.1 | 739.1 | 291.8 | 338 | 379.3 | 646.7 | 563.4 | 577.7 | 629 | 581.1 | 404.5 | 451.8 | 423.2 | 423.2 | 399.7 | 520.9 | 420.3
1620 | 1384 | 564.9 | 225.96 | 264.1342 | 422.9 | 556.2 | 384.5 | 386.3 | 534.9 | 74 | 17.1 | 130.1 | 6.3 | 207.3 | 7.7 | 854.7 | 839.4 | 462.5 | 861.1 | 726.8 | 867.8 | 734.2 | 657.3 | 770.6 | 607.2 | 690.4 | 739.5 | 292 | 338.2 | 379.6 | 646.7 | 563 | 579.2 | 629 | 579.8 | 404.7 | 451.4 | 422.3 | 423.2 | 399.6 | 520.9 | 420.4
1621 | 1385 | 565.4 | 226.16 | 264.368 | 422.6 | 548.8 | 384.4 | 386.2 | 537 | 74 | 17.1 | 130.3 | 5.9 | 215.7 | 7.4 | 855.4 | 837.9 | 463.4 | 861.7 | 726.1 | 868.1 | 735.9 | 656.2 | 766.3 | 606.6 | 691.1 | 740.4 | 292.2 | 338.4 | 379.7 | 647.1 | 563.1 | 579.8 | 629 | 578.8 | 405 | 451.3 | 421.3 | 423.3 | 399.5 | 520.9 | 420.5
1622 | 1386 | 566.9 | 226.76 | 265.0694 | 422 | 558.7 | 385.4 | 385.9 | 538.8 | 74 | 17.1 | 130.3 | 6.3 | 235.6 | 6.1 | 859.8 | 838.7 | 465.2 | 861.6 | 725.9 | 868.2 | 736.3 | 656.7 | 768.4 | 607 | 690.7 | 741.2 | 292.3 | 338.6 | 379.9 | 647.1 | 563.4 | 582.7 | 629.2 | 579.3 | 405.2 | 450.7 | 420.6 | 423.4 | 399.5 | 520.9 | 420.6
1623 | 1387 | 567 | 226.8 | 265.1161 | 422.2 | 563.2 | 386.2 | 385 | 541.5 | 74 | 17.1 | 130.2 | 6.1 | 252.5 | 4.9 | 867.7 | 840.3 | 466.4 | 862.5 | 725.9 | 869 | 733.9 | 656.7 | 774.7 | 606.9 | 690.6 | 741.6 | 292.5 | 338.7 | 380 | 646.9 | 564 | 584.4 | 629.9 | 580.3 | 405.4 | 449.8 | 420.3 | 423.4 | 399.5 | 520.9 | 420.6
1624 | 1388 | 568.7 | 227.48 | 265.911 | 423 | 568.8 | 387.1 | 384.7 | 540.6 | 73.9 | 17.1 | 130.3 | 6.1 | 245.4 | 4.9 | 872.3 | 841.9 | 467.6 | 862.6 | 725.4 | 869.9 | 731.4 | 655.4 | 759.6 | 606.2 | 690.3 | 741.4 | 292.7 | 338.8 | 380 | 647.7 | 563.9 | 582.4 | 630.4 | 580 | 405.6 | 448.8 | 420 | 423.5 | 399.4 | 521 | 420.7
1625 | 1389 | 567.2 | 226.88 | 265.2096 | 424.3 | 572.1 | 387.7 | 384.5 | 539.9 | 73.8 | 17 | 130.3 | 6.3 | 204.1 | 5.5 | 870.3 | 844.1 | 469.3 | 862.5 | 725.3 | 870.4 | 728.9 | 655.8 | 759.4 | 606.4 | 689.4 | 741.3 | 292.9 | 338.9 | 380.1 | 646.9 | 564.1 | 580.5 | 630.7 | 580.5 | 405.9 | 448.2 | 419.9 | 423.6 | 399.4 | 521 | 420.8
1626 | 1390 | 567.1 | 226.84 | 265.1629 | 426 | 571.7 | 387.7 | 384.6 | 540 | 73.7 | 17 | 130.3 | 5.8 | 196.3 | 6.5 | 869.7 | 843.5 | 470.2 | 866.1 | 724.7 | 870.8 | 724.3 | 653.8 | 750.9 | 605.5 | 689 | 738.8 | 293.1 | 338.9 | 380.1 | 645.9 | 565 | 577.1 | 630.8 | 580.4 | 406.1 | 448.2 | 420.4 | 423.7 | 399.5 | 521 | 420.9
1627 | 1391 | 567.5 | 227 | 265.3499 | 426 | 575.9 | 386.9 | 386.6 | 535.7 | 73.7 | 17 | 130.3 | 6 | 222.4 | 6.8 | 869.3 | 833.8 | 471.7 | 864.9 | 724.6 | 871.3 | 719.4 | 653.1 | 739.8 | 604.8 | 688.7 | 738 | 293.2 | 339 | 380.2 | 645.6 | 564.9 | 571.8 | 630.6 | 579.7 | 406.4 | 448.3 | 420.6 | 423.9 | 399.6 | 521.1 | 421
1628 | 1392 | 568.3 | 227.32 | 265.724 | 425.7 | 578.6 | 386.1 | 388.2 | 533.1 | 73.6 | 17 | 130.3 | 6.6 | 220.5 | 6.6 | 867.8 | 830.4 | 473.5 | 862.4 | 724.4 | 871.2 | 712.6 | 651.7 | 726.3 | 604.2 | 688.2 | 735.6 | 293.4 | 339.2 | 380.3 | 645.1 | 564.9 | 567.9 | 630.5 | 580.7 | 406.6 | 448.6 | 421.1 | 424 | 399.8 | 521.1 | 421.1
1629 | 1393 | 567.7 | 227.08 | 265.4434 | 424.8 | 570 | 386 | 388.4 | 530.4 | 73.6 | 17 | 130.4 | 6.5 | 213.8 | 7 | 865.7 | 832.8 | 474.6 | 858.6 | 724.3 | 871.2 | 707.6 | 649.8 | 718.9 | 602.2 | 687.3 | 733.5 | 293.5 | 339.3 | 380.3 | 644.7 | 564.6 | 564.2 | 630.2 | 579.5 | 406.9 | 448.7 | 420.9 | 424.2 | 399.9 | 521.2 | 421.3
1630 | 1394 | 566.1 | 226.44 | 264.6953 | 423.9 | 566.2 | 385.7 | 388.5 | 526.7 | 73.6 | 17 | 130.4 | 6 | 222.3 | 7.3 | 865.8 | 839.3 | 475.5 | 855.1 | 724.1 | 871 | 703.5 | 647.5 | 713.4 | 601.9 | 685.7 | 732.5 | 293.7 | 339.4 | 380.4 | 644.2 | 563.7 | 562.6 | 629.8 | 578.6 | 407.1 | 449 | 421.1 | 424.3 | 400.1 | 521.2 | 421.4
1631 | 1395 | 565.9 | 226.36 | 264.6018 | 422.6 | 561.5 | 385.1 | 389.1 | 523.9 | 73.7 | 17 | 130.4 | 6.3 | 249.1 | 6.8 | 867.6 | 846 | 476.7 | 854.6 | 724.7 | 870.5 | 700.9 | 647.1 | 713.1 | 601.7 | 686.6 | 730.6 | 293.8 | 339.5 | 380.4 | 644.3 | 563.5 | 560.8 | 629.4 | 579 | 407.3 | 449.1 | 422 | 424.5 | 400.3 | 521.3 | 421.5
1632 | 1396 | 565.7 | 226.28 | 264.5083 | 421.6 | 557.3 | 384.9 | 389.5 | 523 | 73.7 | 17 | 130.3 | 6.4 | 246 | 6.6 | 869.3 | 840.4 | 478.5 | 851.9 | 725.3 | 870.5 | 698.7 | 647.2 | 721.8 | 601.1 | 686.4 | 729.9 | 294 | 339.6 | 380.5 | 643.8 | 563.8 | 559.3 | 629.3 | 580.5 | 407.5 | 449.1 | 422.7 | 424.6 | 400.5 | 521.4 | 421.7
1633 | 1397 | 564.2 | 225.68 | 263.8069 | 420.8 | 550.3 | 384.8 | 389.4 | 522.4 | 73.8 | 17 | 130.4 | 5.7 | 210.8 | 5.9 | 859.2 | 837.1 | 479.2 | 850.7 | 725.5 | 870.5 | 699.8 | 647.2 | 726 | 601.8 | 686.9 | 730.7 | 294.2 | 339.8 | 380.6 | 643.6 | 563.4 | 557.9 | 628.9 | 581 | 407.8 | 449.3 | 423.7 | 424.7 | 400.7 | 521.5 | 421.8
1634 | 1398 | 565.9 | 226.36 | 264.6018 | 419.7 | 543.5 | 384.1 | 389.5 | 522.2 | 73.9 | 17 | 130.6 | 6.2 | 232.6 | 4.8 | 862.5 | 832.8 | 480.4 | 849.4 | 725.7 | 870.3 | 703.3 | 648 | 732.7 | 602.5 | 687.7 | 731.5 | 294.3 | 340 | 380.7 | 643.5 | 562.8 | 558.7 | 628.6 | 581 | 408 | 449.6 | 424.2 | 424.9 | 400.8 | 521.6 | 421.9
1635 | 1399 | 567 | 226.8 | 265.1161 | 418.9 | 535.8 | 383.9 | 388.9 | 523 | 74 | 17 | 130.7 | 6.6 | 256 | 5.3 | 866.8 | 830.4 | 481.5 | 847.9 | 725.5 | 870.4 | 703 | 647.4 | 726 | 603.1 | 688.1 | 730.8 | 294.5 | 340.1 | 380.8 | 643.5 | 563 | 557.3 | 628.5 | 581.9 | 408.2 | 450.2 | 424.9 | 425 | 400.9 | 521.6 | 422
1636 | 1400 | 566.7 | 226.68 | 264.9759 | 418.3 | 531.7 | 383.7 | 389.5 | 521.7 | 74 | 17 | 130.6 | 6.6 | 239.6 | 6.4 | 870.5 | 834 | 483.3 | 846 | 725.3 | 870.3 | 701.5 | 646.1 | 720.2 | 603.3 | 687.1 | 730.2 | 294.6 | 340.1 | 380.9 | 643.3 | 563.2 | 555.7 | 628.2 | 582 | 408.5 | 450.5 | 425.6 | 425.2 | 401 | 521.7 | 422.2
1637 | 1401 | 566.7 | 226.68 | 264.9759 | 417.7 | 543.2 | 383.1 | 389.8 | 521.3 | 74.1 | 17 | 130.5 | 6.3 | 247.5 | 6.6 | 870.4 | 832.1 | 484.9 | 844.3 | 725.2 | 870.3 | 700.4 | 644.7 | 718.5 | 603.9 | 687.1 | 730.2 | 294.8 | 340.2 | 380.9 | 642.9 | 562.9 | 555 | 627.9 | 581.8 | 408.7 | 451.1 | 426.8 | 425.3 | 401.2 | 521.8 | 422.3
1638 | 1402 | 565 | 226 | 264.181 | 416.9 | 550.1 | 383 | 389.6 | 520.9 | 74.2 | 17 | 130.5 | 6.4 | 240.1 | 6.5 | 869.1 | 835.7 | 486.3 | 843 | 725 | 870.2 | 700.3 | 643.6 | 720.4 | 603.9 | 688.6 | 729.7 | 294.9 | 340.2 | 381 | 643 | 563.1 | 555.3 | 627.6 | 582.1 | 409 | 452.2 | 427.3 | 425.5 | 401.4 | 521.8 | 422.5
1639 | 1403 | 565.3 | 226.12 | 264.3213 | 416 | 554.1 | 383.2 | 389.9 | 521.4 | 74.3 | 17 | 130.5 | 6.5 | 245.9 | 6 | 872.8 | 840 | 487.6 | 842.5 | 724.7 | 870.6 | 703.5 | 646 | 725.9 | 604.7 | 689.4 | 731 | 295.1 | 340.4 | 381.1 | 642.9 | 563 | 557.2 | 627.5 | 582.2 | 409.2 | 453.2 | 427.8 | 425.7 | 401.6 | 521.9 | 422.6
1640 | 1404 | 566.8 | 226.72 | 265.0226 | 415.7 | 551.7 | 383.1 | 390.7 | 523.4 | 74.4 | 17 | 130.5 | 5.8 | 237.5 | 5.4 | 871.8 | 842.7 | 489.4 | 842 | 725 | 869.5 | 703.2 | 647.6 | 720 | 605.6 | 690.1 | 730.4 | 295.2 | 340.5 | 381.4 | 642.9 | 563.9 | 556.6 | 627.6 | 583.6 | 409.5 | 454.5 | 428.8 | 425.9 | 401.9 | 522 | 422.8
1641 | 1405 | 567.1 | 226.84 | 265.1629 | 416.2 | 548.7 | 383.7 | 391.6 | 524.3 | 74.4 | 17 | 130.5 | 6.5 | 236.1 | 5 | 875.1 | 850.8 | 490.2 | 842.3 | 725.4 | 869.7 | 703.6 | 648.5 | 722.1 | 605.3 | 690.4 | 729.9 | 295.4 | 340.6 | 381.4 | 643 | 564.2 | 557.1 | 627.5 | 582.4 | 409.8 | 455.6 | 429.7 | 426.2 | 402.1 | 522.1 | 422.9
1642 | 1406 | 567.1 | 226.84 | 265.1629 | 416.3 | 553.8 | 383.9 | 392.2 | 525.3 | 74.4 | 17 | 130.5 | 6.4 | 214.4 | 4.8 | 875.3 | 850.4 | 491.5 | 841 | 725.3 | 871.2 | 705.6 | 648.5 | 724.7 | 605.1 | 690.2 | 730.8 | 295.6 | 340.7 | 381.4 | 642.9 | 563.8 | 559.1 | 627.4 | 581.7 | 410 | 455.9 | 429.8 | 426.4 | 402.2 | 522.2 | 423.1
1643 | 1407 | 567.1 | 226.84 | 265.1629 | 416.2 | 557 | 383.8 | 392.3 | 525.6 | 74.4 | 17 | 130.5 | 6.6 | 218.4 | 4.4 | 869.6 | 843 | 492 | 841.6 | 725.1 | 871.8 | 706.1 | 646.6 | 727.6 | 605 | 690.6 | 731.5 | 295.7 | 340.8 | 381.4 | 642.8 | 563.1 | 557.7 | 627.4 | 580.7 | 410.3 | 455.6 | 430.2 | 426.6 | 402.2 | 522.2 | 423.2
1644 | 1408 | 566.7 | 226.68 | 264.9759 | 416.5 | 557.2 | 383.9 | 392.6 | 524.6 | 74.4 | 17 | 130.5 | 6.6 | 257.2 | 4.7 | 865.7 | 837.5 | 491.9 | 842.3 | 724.7 | 871.1 | 705.1 | 646.1 | 726.5 | 604.7 | 690 | 731.4 | 295.9 | 340.8 | 381.5 | 642.7 | 562.5 | 556.1 | 627.3 | 579.5 | 410.6 | 456 | 430.4 | 426.8 | 402.3 | 522.3 | 423.3
1645 | 1409 | 566.7 | 226.68 | 264.9759 | 416.5 | 566.4 | 383.6 | 392.8 | 524 | 74.6 | 17 | 130.5 | 6.3 | 244.7 | 4.7 | 859.6 | 825.6 | 492.5 | 842.5 | 724.2 | 871.1 | 704.3 | 643.5 | 721.4 | 603.5 | 689.4 | 731.9 | 296 | 340.9 | 381.6 | 642.6 | 561.9 | 555.7 | 627.3 | 577.9 | 410.9 | 456.4 | 430 | 426.9 | 402.4 | 522.3 | 423.5
1646 | 1410 | 566.5 | 226.6 | 264.8823 | 417.8 | 578.2 | 382.9 | 392.9 | 524.6 | 74.8 | 17 | 130.5 | 6.4 | 230.9 | 4.5 | 852.7 | 823.6 | 493 | 842.1 | 723.3 | 871.4 | 705.5 | 642.2 | 723.6 | 601.6 | 688.5 | 733.1 | 296.1 | 340.9 | 381.7 | 642.4 | 561.2 | 555.4 | 627.4 | 576.9 | 411.2 | 456.1 | 429.9 | 427.1 | 402.7 | 522.3 | 423.6
1647 | 1411 | 566.2 | 226.48 | 264.7421 | 420.3 | 587.1 | 382.9 | 392 | 525.3 | 74.8 | 17 | 130.4 | 6.5 | 236.5 | 4.5 | 853 | 818.7 | 493.7 | 840.9 | 722.8 | 870.3 | 704.7 | 641.8 | 717.1 | 601.1 | 687.9 | 732.6 | 296.3 | 340.9 | 381.9 | 642.2 | 561.1 | 555.7 | 628 | 578 | 411.5 | 455.9 | 430.1 | 427.3 | 403 | 522.4 | 423.7
1648 | 1412 | 566.4 | 226.56 | 264.8356 | 421.6 | 590.7 | 382.8 | 391.7 | 524.3 | 74.8 | 17 | 130.3 | 6.8 | 248.6 | 4.6 | 854.9 | 822.9 | 494.3 | 839.7 | 722.8 | 868.9 | 701.7 | 640.6 | 705.3 | 600.1 | 687.7 | 730 | 296.4 | 341 | 381.9 | 642.2 | 561.4 | 552.6 | 627.8 | 578.8 | 411.9 | 456.6 | 430.4 | 427.6 | 403.3 | 522.4 | 423.8
1649 | 1413 | 566.7 | 226.68 | 264.9759 | 420.9 | 587.4 | 382.9 | 392.8 | 523 | 74.9 | 17 | 130.3 | 6.7 | 249.8 | 4.8 | 859.8 | 829.1 | 495.5 | 839.9 | 723.1 | 869.3 | 703.6 | 641.9 | 714.1 | 600.4 | 687.8 | 730.4 | 296.5 | 341.1 | 382.1 | 642.5 | 560.9 | 555.4 | 628.2 | 577.8 | 412.2 | 456.9 | 430 | 427.8 | 403.5 | 522.4 | 423.9
1650 | 1414 | 565.4 | 226.16 | 264.368 | 420 | 579 | 383.8 | 393.4 | 527 | 75 | 17 | 130.2 | 6.3 | 245.9 | 5.1 | 864.8 | 834.7 | 496.5 | 840.4 | 723.6 | 869.5 | 706.8 | 642.5 | 726.6 | 601.3 | 687.5 | 732 | 296.7 | 341.2 | 382.3 | 643.4 | 561.4 | 559.8 | 628.3 | 578.3 | 412.6 | 456.6 | 429.8 | 428 | 403.7 | 522.5 | 424.1
1651 | 1415 | 567 | 226.8 | 265.1161 | 419.8 | 574.2 | 384.7 | 393.1 | 528.2 | 75 | 17 | 130.1 | 6.6 | 220.2 | 5 | 870 | 829 | 496.7 | 840.6 | 724.1 | 870.1 | 708.2 | 642.7 | 733.1 | 601.4 | 687 | 732.8 | 296.8 | 341.3 | 382.2 | 643.2 | 561 | 560.6 | 628.6 | 577.6 | 412.9 | 456.1 | 430.1 | 428.2 | 403.9 | 522.6 | 424.2
1652 | 1416 | 567.3 | 226.92 | 265.2564 | 420.7 | 578.1 | 385.3 | 392.8 | 529.3 | 75.1 | 17 | 130.1 | 6.5 | 194.1 | 5.6 | 866.8 | 828.4 | 496.6 | 841.6 | 724.5 | 869.7 | 708.6 | 643.2 | 735.6 | 601.9 | 686.2 | 733.7 | 297 | 341.4 | 382.3 | 642.9 | 561.1 | 562.5 | 629.4 | 577.8 | 413.3 | 456 | 430.2 | 428.5 | 404.2 | 522.6 | 424.3
1653 | 1417 | 567.2 | 226.88 | 265.2096 | 422.5 | 590.6 | 385 | 392.4 | 531.8 | 75.3 | 17 | 130.2 | 6.4 | 231.9 | 5.5 | 870.2 | 827.8 | 497.1 | 841.7 | 725.2 | 870.1 | 708.6 | 644.2 | 735.3 | 602.8 | 685.3 | 733.9 | 297.1 | 341.5 | 382.4 | 642.9 | 562.8 | 562.6 | 629.1 | 578.8 | 413.6 | 456.4 | 431.3 | 428.7 | 404.5 | 522.6 | 424.4
1654 | 1418 | 567.2 | 226.88 | 265.2096 | 422.8 | 599.1 | 384.7 | 392.7 | 531.4 | 75.3 | 17 | 130.3 | 6.2 | 233.7 | 5.9 | 866.2 | 824.1 | 497.2 | 841.5 | 725.7 | 870.5 | 708.6 | 644 | 738.4 | 602.7 | 684.6 | 733.8 | 297.3 | 341.6 | 382.5 | 642.9 | 563.6 | 561.2 | 629.3 | 578.4 | 414 | 456.9 | 431.3 | 428.9 | 404.5 | 522.7 | 424.5
1655 | 1419 | 566.2 | 226.48 | 264.7421 | 422.1 | 601.9 | 384.3 | 393.9 | 532.2 | 75.3 | 17 | 130.4 | 5.9 | 254.3 | 5.4 | 863.1 | 821 | 497.4 | 840.9 | 726.5 | 870.6 | 707.5 | 642.6 | 733.5 | 601.9 | 684.4 | 734 | 297.4 | 341.7 | 382.5 | 642.7 | 563.4 | 558.4 | 629.3 | 577.2 | 414.3 | 457.7 | 431 | 429.1 | 404.5 | 522.7 | 424.6
1656 | 1420 | 566.3 | 226.52 | 264.7888 | 421.6 | 600.5 | 383.7 | 394.8 | 530.3 | 75.2 | 17 | 130.4 | 6.2 | 243.7 | 5 | 864.1 | 823.9 | 498 | 841.2 | 726.8 | 870.9 | 707.9 | 641.7 | 737.7 | 600.8 | 683.3 | 734.1 | 297.6 | 341.8 | 382.6 | 643 | 562.5 | 559.1 | 629.1 | 575.6 | 414.6 | 458.2 | 430.5 | 429.3 | 404.5 | 522.7 | 424.8
1657 | 1421 | 566.8 | 226.72 | 265.0226 | 423 | 599.6 | 383.1 | 394.9 | 531.6 | 75.1 | 17 | 130.4 | 6.3 | 239.2 | 4.9 | 869.9 | 830.5 | 498.4 | 842.4 | 726.8 | 871.2 | 709.6 | 639.9 | 739 | 601.1 | 683.5 | 733 | 297.7 | 341.9 | 383 | 643.3 | 562.4 | 565.9 | 628.9 | 575.8 | 414.9 | 458.1 | 429.8 | 429.5 | 404.7 | 522.7 | 424.9
1658 | 1422 | 567.2 | 226.88 | 265.2096 | 424.1 | 592.5 | 383.6 | 394 | 534.2 | 75.1 | 17 | 130.4 | 6.6 | 233.4 | 4.7 | 868.9 | 830.6 | 499.3 | 843 | 726.7 | 871.3 | 709.5 | 637.7 | 736.9 | 600.8 | 683.7 | 733.5 | 297.8 | 342 | 383.2 | 643.3 | 562.9 | 568.9 | 628.8 | 575.6 | 415.2 | 457.8 | 429.4 | 429.6 | 404.8 | 522.7 | 425
1659 | 1423 | 567.8 | 227.12 | 265.4902 | 423.7 | 589.1 | 384.5 | 392.6 | 533.7 | 75.1 | 17 | 130.4 | 6.6 | 232.7 | 4.4 | 869.9 | 834.2 | 499.6 | 843.9 | 726.9 | 871.8 | 711.4 | 639.1 | 743.8 | 601.1 | 683.7 | 735.2 | 297.9 | 342.1 | 383.1 | 643.8 | 563 | 566.2 | 628.8 | 575.1 | 415.5 | 457.2 | 429.1 | 429.8 | 404.7 | 522.8 | 425.1
1660 | 1424 | 567.7 | 227.08 | 265.4434 | 424.6 | 596 | 384.8 | 391 | 533 | 75.1 | 17 | 130.5 | 6.2 | 246.5 | 4.1 | 862.9 | 832.8 | 500.1 | 844.2 | 727.8 | 872.5 | 711 | 639.7 | 742.6 | 601 | 683.4 | 735.6 | 298 | 342.1 | 383 | 643.2 | 562.9 | 563.5 | 628.6 | 575 | 415.8 | 457 | 428.3 | 430 | 404.7 | 522.8 | 425.2
1661 | 1425 | 566.5 | 226.6 | 264.8823 | 424.4 | 613.5 | 384.8 | 390.2 | 532 | 75 | 17 | 130.5 | 6.2 | 240 | 3.9 | 867.8 | 837.8 | 500.8 | 844.5 | 727.8 | 873.1 | 711.3 | 640.2 | 744.7 | 600.1 | 683.9 | 735.7 | 298.2 | 342.2 | 383.1 | 643.1 | 562.7 | 563 | 629 | 574.7 | 416.1 | 457.5 | 427.6 | 430.1 | 404.7 | 522.8 | 425.3
1662 | 1426 | 565.8 | 226.32 | 264.555 | 423.5 | 611.3 | 384.4 | 390.6 | 530.7 | 75 | 17 | 130.5 | 6.1 | 223.8 | 3.6 | 869.7 | 844.7 | 501.5 | 844.7 | 727.3 | 873.7 | 711.2 | 640.4 | 747.6 | 599.5 | 683.2 | 735.7 | 298.3 | 342.3 | 383.2 | 643 | 562.3 | 562.1 | 629.3 | 574.5 | 416.3 | 457.8 | 427.4 | 430.3 | 404.7 | 522.8 | 425.4
1663 | 1427 | 566.5 | 226.6 | 264.8823 | 423.8 | 600.5 | 383.8 | 390.7 | 532 | 74.9 | 17 | 130.7 | 5.8 | 214.7 | 3.6 | 870.6 | 841.4 | 501.9 | 844.5 | 727.3 | 873 | 709.7 | 641.4 | 740.1 | 599.4 | 684 | 735 | 298.4 | 342.4 | 383.3 | 642.9 | 563.1 | 562.2 | 629.1 | 576.4 | 416.6 | 458.2 | 428 | 430.4 | 404.9 | 522.8 | 425.5
1664 | 1428 | 567.5 | 227 | 265.3499 | 424.4 | 593.7 | 383.5 | 390.8 | 531.9 | 74.9 | 17 | 130.8 | 6.5 | 229.1 | 4.2 | 869.7 | 846.2 | 502.4 | 843 | 727.5 | 871.2 | 704.7 | 641.1 | 724.1 | 599.5 | 683.1 | 733.1 | 298.5 | 342.3 | 383.4 | 642.6 | 564.3 | 559.9 | 629.1 | 577.9 | 416.9 | 459.3 | 428.8 | 430.7 | 405.1 | 522.9 | 425.7
1665 | 1429 | 566 | 226.4 | 264.6486 | 424.2 | 593.8 | 383.8 | 391.9 | 530.4 | 75 | 17 | 130.8 | 6.4 | 223.5 | 4.4 | 872.7 | 849.2 | 503 | 841.8 | 727.7 | 870.4 | 701.6 | 640.6 | 719.5 | 599.5 | 683.6 | 731.7 | 298.6 | 342.3 | 383.5 | 642.6 | 564.2 | 559.8 | 629 | 577.3 | 417.2 | 460.8 | 428.9 | 430.9 | 405.2 | 523 | 425.8
1666 | 1430 | 564.2 | 225.68 | 263.8069 | 423.3 | 588.5 | 384.1 | 392.9 | 528 | 75 | 17 | 130.9 | 6.2 | 196.9 | 5.5 | 873.2 | 851.8 | 503.8 | 841.1 | 728 | 871 | 702.7 | 640.7 | 724.4 | 599.2 | 683.8 | 731.1 | 298.7 | 342.3 | 383.5 | 642.5 | 563.6 | 557.8 | 629.1 | 575.9 | 417.5 | 462.1 | 428.5 | 431.2 | 405.3 | 523 | 426
1667 | 1431 | 567.3 | 226.92 | 265.2564 | 422 | 575.1 | 384.4 | 393.3 | 526.2 | 75.1 | 17 | 131 | 5.7 | 212.5 | 6.7 | 872.7 | 855.3 | 504.7 | 841 | 728.4 | 871.5 | 706.9 | 642.9 | 735.9 | 600.1 | 683.3 | 732.1 | 298.7 | 342.4 | 383.6 | 642.7 | 562.9 | 560.7 | 629.2 | 576.1 | 417.8 | 462 | 428.9 | 431.5 | 405.5 | 523.1 | 426.2
1668 | 1432 | 566.6 | 226.64 | 264.9291 | 420.9 | 566.1 | 384.4 | 393.9 | 527.9 | 75.1 | 17 | 131 | 6 | 230.5 | 7 | 872.4 | 862.8 | 505.6 | 843 | 728.8 | 871.4 | 712.8 | 646.8 | 746.3 | 601.6 | 684.1 | 734 | 298.7 | 342.4 | 383.8 | 643.2 | 563 | 564.9 | 629.3 | 577.9 | 418 | 462 | 429.4 | 431.7 | 405.6 | 523.1 | 426.3
1669 | 1433 | 566.3 | 226.52 | 264.7888 | 420.9 | 566 | 384.3 | 394.3 | 530.3 | 75.1 | 17 | 131.1 | 5.5 | 216.5 | 6.4 | 873.9 | 865.1 | 505.8 | 844.5 | 729.2 | 870.7 | 713.4 | 648.6 | 745.7 | 602.5 | 684.3 | 732.8 | 298.8 | 342.5 | 383.8 | 643.3 | 563.3 | 566.1 | 629.1 | 578.7 | 418.3 | 462.4 | 429.4 | 431.9 | 405.7 | 523.1 | 426.4
1670 | 1434 | 565.6 | 226.24 | 264.4615 | 420.4 | 573.2 | 384.8 | 394.2 | 530.3 | 75 | 17 | 131 | 5.4 | 229 | 5.2 | 872.6 | 866.1 | 507.1 | 844.7 | 729.6 | 870.3 | 715.1 | 650.9 | 748.7 | 603.2 | 684.5 | 731.9 | 299 | 342.5 | 383.9 | 643.8 | 562.8 | 571.1 | 629.1 | 578.4 | 418.5 | 462.6 | 429.5 | 432 | 405.7 | 523.2 | 426.5
1671 | 1435 | 564.8 | 225.92 | 264.0875 | 419.7 | 566.2 | 384.8 | 394 | 534.2 | 75 | 17 | 130.9 | 5.8 | 236.3 | 5.2 | 872.9 | 864.1 | 508.2 | 845.3 | 729.7 | 870.2 | 718.1 | 651.4 | 749.1 | 604.6 | 685.6 | 732.2 | 299.1 | 342.5 | 384.4 | 644.7 | 563.5 | 578.6 | 629.1 | 579.4 | 418.7 | 462.8 | 429.2 | 432.1 | 405.7 | 523.2 | 426.7
1672 | 1436 | 566.6 | 226.64 | 264.9291 | 419.7 | 560.3 | 385.2 | 393.6 | 539.1 | 75 | 17 | 131 | 6.2 | 234 | 6.2 | 874.8 | 864.9 | 509 | 847 | 730 | 870.8 | 719.4 | 651.6 | 751.7 | 605.4 | 685 | 733.2 | 299.2 | 342.6 | 384.4 | 644.8 | 564.4 | 580 | 629.5 | 579.2 | 419 | 462.8 | 428.7 | 432.2 | 405.7 | 523.3 | 426.8
1673 | 1437 | 567.2 | 226.88 | 265.2096 | 420.5 | 575.4 | 386.6 | 392.5 | 540.2 | 74.9 | 17 | 131.1 | 6.6 | 221 | 7.1 | 873.4 | 867.6 | 509.6 | 848.4 | 730.1 | 871.1 | 720.1 | 653 | 752.8 | 605.7 | 684.9 | 734.5 | 299.2 | 342.6 | 384.4 | 645 | 564.3 | 579.6 | 629.4 | 578.9 | 419.1 | 462 | 428.9 | 432.2 | 405.8 | 523.3 | 426.9
1674 | 1438 | 565 | 226 | 264.181 | 420.8 | 580.4 | 386.7 | 391.6 | 538.6 | 74.8 | 17 | 131.2 | 6.4 | 235.4 | 7 | 874.7 | 864.1 | 510.3 | 849 | 729.9 | 871.6 | 720.9 | 655.3 | 753.7 | 605.6 | 685.1 | 734.8 | 299.4 | 342.7 | 384.4 | 645 | 563.8 | 579.2 | 629.9 | 578.9 | 419.3 | 461.3 | 429 | 432.3 | 405.9 | 523.3 | 427
1675 | 1439 | 565.1 | 226.04 | 264.2277 | 422.3 | 581.8 | 385.9 | 391.3 | 536.9 | 74.7 | 17 | 131.2 | 6.3 | 230.4 | 6.4 | 878.2 | 854.6 | 510.2 | 849.6 | 729.1 | 872.1 | 722.8 | 656.1 | 757.2 | 605.8 | 684.9 | 735.8 | 299.5 | 342.8 | 384.7 | 645.2 | 563.1 | 581.1 | 630 | 578.7 | 419.5 | 460.3 | 428.7 | 432.3 | 405.9 | 523.4 | 427
1676 | 1440 | 567 | 226.8 | 265.1161 | 423.7 | 585.4 | 386.4 | 390.7 | 538.8 | 74.8 | 17 | 131.1 | 6.1 | 254 | 5.5 | 875.4 | 847.6 | 510.3 | 850.5 | 729 | 872 | 724.2 | 655.6 | 757.5 | 605.9 | 685.3 | 735.8 | 299.7 | 342.8 | 385.1 | 645.2 | 563.1 | 584.2 | 630.1 | 578 | 419.7 | 459.5 | 427.8 | 432.5 | 405.7 | 523.4 | 427.1
1677 | 1441 | 567.7 | 227.08 | 265.4434 | 423.5 | 591.6 | 387.5 | 390.1 | 542.7 | 74.8 | 17 | 130.9 | 5.9 | 242.9 | 5 | 874.5 | 840 | 510.2 | 850.9 | 728.6 | 871.5 | 726.6 | 654.3 | 750.8 | 606.2 | 685.1 | 735.8 | 299.8 | 342.8 | 385.4 | 645.5 | 563.5 | 588.2 | 630.2 | 577.9 | 419.9 | 459.1 | 427.1 | 432.6 | 405.5 | 523.4 | 427.2
1678 | 1442 | 568 | 227.2 | 265.5837 | 422.4 | 590.5 | 388.1 | 389.4 | 546.4 | 74.7 | 17 | 130.8 | 5.9 | 232.3 | 4.5 | 875.2 | 835.3 | 510.3 | 852.6 | 728.1 | 871.4 | 726.4 | 653.3 | 747.3 | 605.8 | 684.4 | 736 | 299.9 | 342.8 | 385.6 | 645.8 | 563.7 | 588.7 | 630.2 | 576.8 | 420.1 | 458.7 | 426.5 | 432.7 | 405.4 | 523.4 | 427.3
1679 | 1443 | 566.2 | 226.48 | 264.7421 | 420.1 | 585.5 | 388.6 | 388.2 | 545.2 | 74.7 | 17 | 130.7 | 6.1 | 242.3 | 4.4 | 870.6 | 846.1 | 510.7 | 854 | 729.1 | 870.8 | 727.5 | 655.2 | 755 | 605.7 | 683.2 | 738.1 | 300.1 | 342.8 | 385.5 | 646 | 562.9 | 585.8 | 630.3 | 576.1 | 420.4 | 458 | 426.5 | 432.9 | 405.3 | 523.4 | 427.4
1680 | 1444 | 563.7 | 225.48 | 263.5731 | 420.2 | 574.9 | 388.1 | 387.9 | 543.4 | 74.7 | 17 | 130.7 | 6.2 | 241.7 | 4.3 | 875.4 | 851.1 | 511.4 | 854.8 | 729.6 | 870.6 | 727.4 | 656.9 | 757.2 | 606.6 | 682.9 | 739.1 | 300.2 | 342.9 | 385.4 | 645.7 | 563.6 | 583.7 | 630 | 577.4 | 420.6 | 457.5 | 425.8 | 433 | 405.2 | 523.4 | 427.4
1681 | 1445 | 564.2 | 225.68 | 263.8069 | 421.7 | 568.2 | 387.5 | 387.5 | 543 | 74.7 | 17 | 130.6 | 5.7 | 241.7 | 4.2 | 876.5 | 858.3 | 511.9 | 856.7 | 729.3 | 870.7 | 726 | 655.8 | 752.4 | 606.3 | 684.5 | 738.8 | 300.3 | 342.9 | 385.5 | 645.8 | 563.7 | 582.4 | 630 | 577.6 | 420.8 | 457.2 | 424.9 | 433.2 | 405 | 523.4 | 427.5
1682 | 1446 | 563.2 | 225.28 | 263.3393 | 421.6 | 562.5 | 387.4 | 387.1 | 540.2 | 74.8 | 17 | 130.5 | 6.2 | 250.8 | 4.1 | 882.9 | 866.5 | 512.8 | 857.4 | 728.8 | 870.8 | 723.5 | 655 | 748.7 | 605.5 | 685.3 | 738 | 300.5 | 342.9 | 385.5 | 645.5 | 563.3 | 579.5 | 629.9 | 577.9 | 421 | 456.9 | 424.6 | 433.3 | 404.9 | 523.5 | 427.6
1683 | 1447 | 564.6 | 225.84 | 263.9939 | 421.3 | 578.7 | 387.6 | 387.7 | 535.6 | 74.8 | 17 | 130.5 | 6.3 | 255 | 4.2 | 884 | 870.1 | 513.8 | 857.6 | 728.3 | 870.9 | 722.4 | 656.4 | 749.2 | 605.4 | 685.7 | 737.1 | 300.6 | 342.9 | 385.6 | 645.4 | 562.9 | 578.5 | 629.7 | 578.1 | 421.2 | 456.8 | 424.3 | 433.4 | 404.9 | 523.5 | 427.7
1684 | 1448 | 567.6 | 227.04 | 265.3967 | 420.6 | 582.4 | 387.1 | 388.2 | 536.5 | 74.8 | 17 | 130.7 | 6.2 | 225.1 | 4.3 | 881.5 | 870.5 | 514.4 | 858.4 | 727.6 | 870.4 | 721.2 | 657.4 | 748.1 | 605.8 | 686 | 736.5 | 300.8 | 343 | 385.7 | 645.4 | 563.5 | 580.5 | 629.5 | 579 | 421.3 | 456.6 | 424 | 433.5 | 404.9 | 523.5 | 427.9
1685 | 1449 | 567.3 | 226.92 | 265.2564 | 419.7 | 585.5 | 386.2 | 388.8 | 535.9 | 74.9 | 17 | 130.9 | 5.8 | 203.2 | 4.2 | 882.2 | 873.4 | 515.2 | 855.5 | 727.4 | 869.7 | 721.9 | 658.4 | 750.3 | 605.5 | 685.3 | 736.7 | 300.9 | 343 | 385.7 | 645.4 | 562.7 | 581.5 | 629.7 | 578.5 | 421.4 | 456.1 | 423.2 | 433.6 | 404.7 | 523.5 | 428
1686 | 1450 | 567.5 | 227 | 265.3499 | 419.1 | 590.2 | 385.7 | 389.1 | 535.2 | 74.9 | 17 | 131 | 6.2 | 225.7 | 4.2 | 881.5 | 873.5 | 515.2 | 853.5 | 727.7 | 870 | 724.9 | 659.2 | 755.9 | 606 | 685.8 | 737.4 | 301 | 343 | 385.8 | 645.7 | 561.9 | 584.2 | 629.8 | 579.5 | 421.6 | 455.7 | 422.6 | 433.6 | 404.7 | 523.6 | 428
1687 | 1451 | 567.2 | 226.88 | 265.2096 | 419.5 | 597.3 | 386 | 388.7 | 534.9 | 75 | 17 | 131.1 | 6 | 246.4 | 4.6 | 875.4 | 872.9 | 515.7 | 852 | 728.4 | 869.8 | 728.9 | 662 | 761.2 | 607.9 | 685.6 | 739 | 301.2 | 343.1 | 386.1 | 646.3 | 561.7 | 589.9 | 629.9 | 581.9 | 421.7 | 455.5 | 422.4 | 433.7 | 404.7 | 523.6 | 428.1
1688 | 1452 | 567.4 | 226.96 | 265.3032 | 420 | 602.9 | 386.2 | 388.3 | 538.4 | 75 | 17 | 131.1 | 6.4 | 248.8 | 4.5 | 874.5 | 871.8 | 517.3 | 851.4 | 728.6 | 869.5 | 732 | 662.7 | 763.2 | 609.4 | 685.3 | 739.8 | 301.3 | 343.2 | 386.4 | 646.3 | 563 | 594.5 | 630 | 582.5 | 421.8 | 455.5 | 422.6 | 433.8 | 404.7 | 523.6 | 428.2
1689 | 1453 | 567.7 | 227.08 | 265.4434 | 420.6 | 594.6 | 386.3 | 387.9 | 539 | 75 | 17 | 131.1 | 6 | 244.1 | 4.8 | 878.7 | 868.2 | 518.4 | 851.2 | 729.5 | 869.7 | 732.1 | 662.8 | 762.8 | 609.2 | 684.6 | 740.3 | 301.5 | 343.3 | 386.5 | 646.1 | 563 | 593.1 | 629.7 | 581 | 422 | 455 | 422.5 | 433.9 | 404.8 | 523.7 | 428.2
1690 | 1454 | 566 | 226.4 | 264.6486 | 420.1 | 592.7 | 386.6 | 387.6 | 537.6 | 75 | 17 | 131 | 6 | 221.3 | 4.8 | 878.8 | 861 | 518.6 | 851.7 | 729.5 | 870.8 | 733.7 | 663.1 | 761.6 | 607.8 | 684.1 | 740.8 | 301.7 | 343.4 | 386.4 | 645.6 | 562.7 | 589.3 | 629.4 | 579 | 422.1 | 454.4 | 422.3 | 434 | 404.8 | 523.7 | 428.3
1691 | 1455 | 565.1 | 226.04 | 264.2277 | 419.8 | 594.1 | 386.6 | 387.2 | 537.5 | 75 | 17 | 131.1 | 6.2 | 231.3 | 4.7 | 877.3 | 857.7 | 518.1 | 853.2 | 729.5 | 871 | 735.3 | 662 | 761.7 | 606.7 | 683.6 | 740.9 | 301.8 | 343.4 | 386.7 | 645.6 | 562.4 | 588.2 | 629.4 | 577.6 | 422.2 | 453.8 | 422.2 | 434 | 404.7 | 523.7 | 428.4
1692 | 1456 | 564.9 | 225.96 | 264.1342 | 419 | 590.3 | 386.6 | 386.9 | 538.9 | 75 | 17 | 131.2 | 5.4 | 259.2 | 5.1 | 868.2 | 841.8 | 517.5 | 858.1 | 728.7 | 871.5 | 732.3 | 658.5 | 747.4 | 605.3 | 683.7 | 739.9 | 302 | 343.4 | 387 | 645.7 | 562.5 | 586.6 | 629.5 | 576.3 | 422.3 | 453.3 | 421.9 | 434.1 | 404.6 | 523.7 | 428.4
1693 | 1457 | 565.9 | 226.36 | 264.6018 | 418.7 | 589 | 386.6 | 386.4 | 539 | 75 | 17 | 131.2 | 6.1 | 253.9 | 5.1 | 853.5 | 830.2 | 517.3 | 860.8 | 728 | 870.6 | 728.7 | 653.9 | 735.3 | 603.1 | 684.2 | 738.8 | 302.1 | 343.5 | 387.1 | 645.7 | 562.1 | 583.1 | 629.6 | 574.7 | 422.4 | 453.2 | 421.7 | 434.2 | 404.6 | 523.7 | 428.5
1694 | 1458 | 566.4 | 226.56 | 264.8356 | 418.1 | 593.6 | 386.6 | 385.9 | 539.8 | 75 | 17 | 131.1 | 6.4 | 241.8 | 5.1 | 848.2 | 817.7 | 516.7 | 859.8 | 727.3 | 869.5 | 727.6 | 650.4 | 729.5 | 599.5 | 683.7 | 739.2 | 302.2 | 343.5 | 387.1 | 645.9 | 562.1 | 580.1 | 629.8 | 573.8 | 422.5 | 453.2 | 421.3 | 434.2 | 404.6 | 523.7 | 428.5
1695 | 1459 | 565 | 226 | 264.181 | 417.4 | 597.3 | 386.9 | 385.7 | 541.8 | 75 | 17 | 131.2 | 6.2 | 240.7 | 5.2 | 851.7 | 820 | 516.7 | 857.6 | 727.5 | 868.7 | 725.7 | 648.2 | 727.9 | 597.1 | 682.4 | 739.7 | 302.3 | 343.6 | 387.1 | 645.6 | 563 | 578.7 | 629.5 | 573.5 | 422.6 | 453 | 420.8 | 434.3 | 404.6 | 523.7 | 428.6
1696 | 1460 | 565 | 226 | 264.181 | 418.2 | 598.5 | 386.9 | 385.3 | 542.7 | 74.9 | 17 | 131.1 | 6.4 | 245.2 | 5.2 | 857.1 | 828.4 | 516.9 | 857.4 | 728 | 868.7 | 725.8 | 649.9 | 735.5 | 597 | 681.5 | 742.1 | 302.4 | 343.6 | 387.1 | 645 | 563.6 | 576.8 | 629.7 | 574.1 | 422.7 | 452.9 | 420.6 | 434.4 | 404.6 | 523.6 | 428.7
1697 | 1461 | 566 | 226.4 | 264.6486 | 420.8 | 596.9 | 386.4 | 385 | 542.8 | 74.9 | 17 | 131 | 6.3 | 243 | 5.3 | 859.7 | 835.1 | 517 | 857 | 728.4 | 868.8 | 725.9 | 652.1 | 738.9 | 598 | 681.5 | 742.2 | 302.5 | 343.7 | 387.2 | 645.1 | 563.7 | 577 | 629.7 | 575.3 | 422.8 | 453.5 | 420.4 | 434.6 | 404.6 | 523.6 | 428.7
1698 | 1462 | 565.8 | 226.32 | 264.555 | 419.9 | 599.1 | 385.9 | 384.9 | 541.6 | 74.8 | 17 | 130.9 | 5.7 | 242.1 | 5 | 863.4 | 838.4 | 517.4 | 854.2 | 728.8 | 869 | 729.4 | 654.7 | 742.1 | 599.8 | 682.3 | 741.7 | 302.6 | 343.8 | 387.4 | 645.9 | 564.1 | 585.5 | 629.7 | 576.8 | 423 | 453.6 | 420.1 | 434.7 | 404.5 | 523.7 | 428.8
1699 | 1463 | 564.8 | 225.92 | 264.0875 | 420.2 | 598.1 | 385.7 | 385.1 | 543.1 | 74.8 | 17 | 130.8 | 5.8 | 226.2 | 4.4 | 862 | 834.1 | 517.7 | 854.1 | 728.8 | 870.1 | 730.9 | 654 | 738.7 | 599.9 | 682.6 | 741.8 | 302.7 | 343.9 | 387.6 | 646.4 | 564.4 | 587.1 | 629.8 | 577.3 | 423.1 | 453.3 | 419.7 | 434.9 | 404.4 | 523.7 | 428.9
1700 | 1464 | 566.7 | 226.68 | 264.9759 | 420.7 | 598.9 | 385.6 | 385.3 | 543.5 | 74.8 | 17 | 130.8 | 6 | 200.5 | 4.2 | 860.6 | 837.2 | 517.6 | 853.3 | 728.7 | 869.3 | 733.2 | 655.2 | 744.4 | 600.1 | 681.2 | 741.4 | 302.7 | 344 | 387.9 | 646.7 | 564.3 | 589.3 | 629.8 | 576.8 | 423.3 | 453.1 | 419.3 | 435 | 404.4 | 523.7 | 429
1701 | 1465 | 567.2 | 226.88 | 265.2096 | 420.6 | 602.9 | 386 | 384.6 | 545.3 | 74.8 | 17 | 130.9 | 5.9 | 190.5 | 3.7 | 864.3 | 837.5 | 517.9 | 853.4 | 728.7 | 868.8 | 734.7 | 655.9 | 746 | 601.2 | 681.2 | 741.5 | 302.9 | 344.1 | 388 | 647.4 | 564.5 | 590.5 | 629.8 | 576.7 | 423.4 | 453.2 | 419.3 | 435.1 | 404.4 | 523.7 | 429
1702 | 1466 | 568.1 | 227.24 | 265.6305 | 420.2 | 598.5 | 386.3 | 384 | 545.5 | 74.8 | 17 | 130.9 | 6.4 | 223.4 | 3.2 | 863.5 | 837.1 | 518.5 | 853.7 | 728.5 | 867.9 | 736.3 | 656.8 | 749.6 | 602.1 | 681.3 | 743.9 | 303 | 344.2 | 388.2 | 647.5 | 564.4 | 591.8 | 630 | 576 | 423.5 | 453 | 418.6 | 435.1 | 404.2 | 523.7 | 429.1
1703 | 1467 | 568.4 | 227.36 | 265.7707 | 420.1 | 593.9 | 386.6 | 383.4 | 544.1 | 74.9 | 16.9 | 130.9 | 6.3 | 250.7 | 3.5 | 863.2 | 837.2 | 519.1 | 853.2 | 728.6 | 866.4 | 737.6 | 658.9 | 753.3 | 602.9 | 680.9 | 745.7 | 303.1 | 344.3 | 388.2 | 647.6 | 563.9 | 592.2 | 630 | 576 | 423.6 | 452.5 | 417.9 | 435.2 | 404.1 | 523.7 | 429.2
1704 | 1468 | 568.1 | 227.24 | 265.6305 | 420.1 | 582.9 | 386.9 | 383 | 544.5 | 74.9 | 16.9 | 130.9 | 6.1 | 238.9 | 4 | 870.7 | 845.8 | 519.3 | 853.9 | 729.1 | 865.2 | 738 | 662.1 | 756.1 | 604.2 | 681 | 747.5 | 303.1 | 344.4 | 388.3 | 647.5 | 564.5 | 592.8 | 630.2 | 577.1 | 423.6 | 452.1 | 418 | 435.2 | 404.1 | 523.7 | 429.2
1705 | 1469 | 568 | 227.2 | 265.5837 | 420.4 | 578.5 | 386.9 | 382.6 | 545.2 | 74.9 | 16.9 | 130.9 | 6.1 | 224.5 | 3.9 | 871.3 | 851.3 | 519.7 | 854.2 | 729.5 | 864.8 | 739.6 | 664 | 761.2 | 605.1 | 681.1 | 747.4 | 303.2 | 344.5 | 388.4 | 647.6 | 564.6 | 592.6 | 630.4 | 577.3 | 423.7 | 451.9 | 417.6 | 435.3 | 404.1 | 523.7 | 429.3
1706 | 1470 | 568.4 | 227.36 | 265.7707 | 421.4 | 580.5 | 386.7 | 381.8 | 547.8 | 74.9 | 16.9 | 131 | 6 | 212.9 | 3.9 | 869.9 | 848.4 | 521.1 | 854.4 | 730 | 864.8 | 739.1 | 663.5 | 759.6 | 606.5 | 680.5 | 745.6 | 303.4 | 344.6 | 389 | 647.8 | 565.6 | 596.1 | 630.8 | 576.9 | 423.8 | 451.4 | 417.7 | 435.3 | 404.1 | 523.7 | 429.3
1707 | 1471 | 567.7 | 227.08 | 265.4434 | 421.4 | 581.3 | 387.1 | 381.1 | 550.7 | 74.9 | 16.9 | 131 | 6.1 | 220.9 | 4.2 | 866.4 | 846.4 | 521.4 | 854.4 | 729.9 | 865.1 | 737.7 | 663.1 | 759 | 606.6 | 680.6 | 745 | 303.5 | 344.7 | 389 | 648.1 | 565.7 | 598.2 | 630.7 | 576.5 | 423.8 | 450.8 | 418.6 | 435.4 | 404.2 | 523.8 | 429.4
1708 | 1472 | 565.7 | 226.28 | 264.5083 | 420.5 | 577.6 | 388.6 | 380.7 | 549.3 | 74.7 | 16.9 | 131 | 6.3 | 221.6 | 4.4 | 869.9 | 847.3 | 521.2 | 855.6 | 729.5 | 865.6 | 737 | 663.2 | 757.8 | 605.9 | 680.4 | 745.6 | 303.6 | 344.8 | 388.8 | 648 | 565.3 | 596.7 | 630.5 | 576.3 | 423.9 | 450.1 | 419.3 | 435.4 | 404.4 | 523.8 | 429.4
1709 | 1473 | 565.6 | 226.24 | 264.4615 | 421.1 | 577.7 | 389.1 | 380.5 | 545.9 | 74.7 | 16.9 | 131.1 | 5.9 | 211.4 | 4.8 | 868.3 | 852 | 520.6 | 856.7 | 728.9 | 865.8 | 735.3 | 663.9 | 759.9 | 605.2 | 680.9 | 745.2 | 303.7 | 344.9 | 388.8 | 647.8 | 564 | 593.1 | 630.8 | 575.9 | 424 | 449.6 | 420.7 | 435.5 | 404.5 | 523.8 | 429.4
1710 | 1474 | 565.6 | 226.24 | 264.4615 | 422.8 | 586.9 | 388.8 | 379.8 | 542.5 | 74.6 | 16.9 | 131.1 | 6 | 215.4 | 5 | 865.2 | 859.9 | 521 | 857.7 | 729 | 865.3 | 734.5 | 666.6 | 759.4 | 605.5 | 681.4 | 745 | 303.8 | 345 | 388.9 | 647.3 | 564 | 592.3 | 631 | 576.8 | 424 | 449.2 | 422.3 | 435.5 | 404.7 | 523.8 | 429.5
1711 | 1475 | 564.3 | 225.72 | 263.8537 | 422.7 | 586 | 388.4 | 379.5 | 539.6 | 74.5 | 16.9 | 131.1 | 5.9 | 222.8 | 4.9 | 859.9 | 860.8 | 521.6 | 858.9 | 729.8 | 864.9 | 732.5 | 669.1 | 756.7 | 605.1 | 682.1 | 743.6 | 304 | 345.1 | 388.9 | 646.9 | 564.5 | 588.7 | 631 | 578.3 | 424 | 449.5 | 423.1 | 435.5 | 404.7 | 523.8 | 429.6
1712 | 1476 | 564.9 | 225.96 | 264.1342 | 421 | 575.7 | 387.8 | 380.1 | 537.6 | 74.5 | 16.9 | 131.1 | 5.9 | 226.7 | 4.8 | 856.5 | 857.9 | 521.9 | 857.8 | 729.6 | 864.4 | 735.5 | 671.9 | 765.8 | 606 | 682.8 | 745.3 | 304.2 | 345.2 | 389 | 646.9 | 564.2 | 588.4 | 630.6 | 578.5 | 424.1 | 450.1 | 423.5 | 435.6 | 404.7 | 523.9 | 429.7
1713 | 1477 | 566.8 | 226.72 | 265.0226 | 420.1 | 572.9 | 387.8 | 380.9 | 538.6 | 74.5 | 16.9 | 131 | 5.5 | 223 | 4.9 | 857.5 | 846.6 | 522.2 | 857.2 | 729.4 | 864.2 | 739.1 | 673.5 | 769.6 | 607 | 683.4 | 746.5 | 304.3 | 345.1 | 389.2 | 647 | 564.2 | 589.3 | 630.3 | 578.7 | 424.1 | 450.4 | 423.4 | 435.7 | 404.7 | 523.9 | 429.8
1714 | 1478 | 567.5 | 227 | 265.3499 | 421.7 | 570.5 | 387.8 | 381.8 | 538.9 | 74.4 | 16.9 | 131 | 6.2 | 236.5 | 4.7 | 843.6 | 827.4 | 521.8 | 860 | 727.8 | 864.8 | 735.3 | 668.9 | 751 | 605.6 | 682.6 | 745 | 304.4 | 345.1 | 389.4 | 646.4 | 563.6 | 585.2 | 630.3 | 576.8 | 424.1 | 450.7 | 423.2 | 435.8 | 404.7 | 523.9 | 429.9
1715 | 1479 | 566.9 | 226.76 | 265.0694 | 424.3 | 572.7 | 388.2 | 382.1 | 536.7 | 74.4 | 16.9 | 131 | 5.7 | 246.9 | 4.2 | 838.1 | 827.4 | 520.8 | 862.4 | 725.9 | 864.9 | 727.9 | 661.8 | 731.9 | 600.3 | 681.8 | 742.7 | 304.5 | 345.1 | 389.3 | 645.7 | 562.1 | 577.5 | 630.1 | 573.7 | 424.2 | 450.1 | 422.6 | 435.8 | 404.7 | 523.9 | 429.9
1716 | 1480 | 567.2 | 226.88 | 265.2096 | 424.6 | 582.3 | 388.4 | 381.7 | 534.4 | 74.5 | 16.9 | 130.9 | 6 | 244.6 | 3.5 | 842.9 | 834.4 | 520.7 | 858.7 | 724.3 | 864.8 | 725.3 | 656.8 | 728 | 597.1 | 681.2 | 742 | 304.6 | 345.1 | 389.5 | 645.2 | 561.1 | 575.9 | 629.9 | 571.8 | 424.2 | 449.4 | 422 | 435.9 | 404.7 | 523.9 | 429.9
1717 | 1481 | 566.6 | 226.64 | 264.9291 | 423.5 | 587.2 | 388 | 381.8 | 536 | 74.5 | 16.9 | 130.8 | 6.6 | 241.4 | 3 | 853 | 839.4 | 520.2 | 854.6 | 723.1 | 865 | 727.6 | 657 | 736.4 | 598 | 681.2 | 743.4 | 304.8 | 345.1 | 389.7 | 645.8 | 561.2 | 582 | 630 | 572.7 | 424.3 | 448.9 | 422.1 | 436 | 404.8 | 523.8 | 430
1718 | 1482 | 566.5 | 226.6 | 264.8823 | 422.2 | 592.2 | 386.9 | 381.4 | 536.4 | 74.5 | 16.9 | 130.8 | 6.6 | 215.1 | 2.7 | 860.4 | 842.3 | 520.2 | 853.4 | 722.4 | 865.4 | 729.5 | 658.4 | 742.7 | 598.9 | 681.8 | 745 | 304.9 | 345.2 | 389.6 | 645.9 | 561.1 | 580.9 | 629.9 | 573.8 | 424.4 | 448.6 | 423.2 | 436.2 | 405.1 | 523.8 | 430
1719 | 1483 | 565.9 | 226.36 | 264.6018 | 420.8 | 593.1 | 385.7 | 381.5 | 535.3 | 74.5 | 16.9 | 131 | 6 | 195.4 | 3.1 | 866.2 | 851.8 | 520.3 | 853.3 | 722 | 866.6 | 730.9 | 660.7 | 747.2 | 599.7 | 682 | 745.5 | 305.1 | 345.3 | 389.7 | 645.5 | 560.8 | 579.5 | 630.4 | 574.6 | 424.5 | 449.2 | 424.5 | 436.3 | 405.3 | 523.8 | 430
1720 | 1484 | 565.6 | 226.24 | 264.4615 | 420.4 | 592 | 384.4 | 382.3 | 534.6 | 74.6 | 16.9 | 131 | 5.7 | 204.1 | 4.5 | 865.9 | 856.2 | 520.6 | 853 | 721.9 | 867.2 | 733.2 | 663.2 | 753.5 | 600.5 | 682.3 | 746.7 | 305.2 | 345.4 | 389.8 | 645.3 | 560.6 | 580.5 | 630.4 | 575.8 | 424.6 | 449.6 | 425 | 436.4 | 405.5 | 523.8 | 430.1
1721 | 1485 | 565.1 | 226.04 | 264.2277 | 420.6 | 591.4 | 384.3 | 382.2 | 534.7 | 74.6 | 16.9 | 130.9 | 6.2 | 217.7 | 5.7 | 867 | 850.8 | 519.9 | 854.2 | 721.4 | 867.9 | 735.2 | 665 | 755.5 | 601.6 | 681.9 | 748.2 | 305.4 | 345.6 | 389.9 | 645.1 | 560.7 | 579.8 | 630 | 576 | 424.6 | 450 | 424.8 | 436.5 | 405.4 | 523.8 | 430.2
1722 | 1486 | 567 | 226.8 | 265.1161 | 421.3 | 590.6 | 384.7 | 382.2 | 534 | 74.6 | 16.9 | 130.9 | 6.3 | 201.9 | 6.1 | 866.2 | 847.2 | 519.8 | 854.6 | 721 | 867.9 | 734.6 | 664.9 | 753.6 | 601.6 | 680.9 | 748.9 | 305.5 | 345.7 | 389.9 | 644.8 | 560.2 | 576.8 | 630.1 | 574.7 | 424.7 | 449.9 | 423.9 | 436.5 | 405.4 | 523.8 | 430.2
1723 | 1487 | 567.3 | 226.92 | 265.2564 | 422.4 | 588.1 | 384.3 | 382.1 | 532.8 | 74.5 | 16.9 | 130.8 | 6 | 202.6 | 6.2 | 866.2 | 846.6 | 519.4 | 854.8 | 720.6 | 866.7 | 736.4 | 667.1 | 759.8 | 602.2 | 679.7 | 751.4 | 305.7 | 345.8 | 390 | 644.8 | 559.9 | 578.2 | 630.1 | 574.6 | 424.7 | 449.5 | 423.8 | 436.6 | 405.4 | 523.8 | 430.3
1724 | 1488 | 567.4 | 226.96 | 265.3032 | 423.2 | 594.5 | 384 | 382.1 | 532.2 | 74.5 | 16.9 | 130.7 | 6.1 | 201.5 | 6.3 | 866.3 | 847.8 | 519.6 | 854.9 | 720.1 | 865.9 | 739.4 | 669.3 | 767 | 603.2 | 680 | 752.3 | 305.8 | 345.9 | 390.1 | 644.7 | 559.5 | 578.7 | 630 | 575.3 | 424.8 | 449 | 423.9 | 436.7 | 405.5 | 523.8 | 430.4
1725 | 1489 | 567.5 | 227 | 265.3499 | 424.5 | 594.1 | 384.3 | 382.4 | 532.6 | 74.5 | 16.9 | 130.8 | 6 | 206.4 | 6.3 | 868.5 | 850.2 | 519.4 | 854.3 | 719.8 | 866.1 | 740.3 | 670.8 | 768.9 | 604.1 | 680 | 752.8 | 305.9 | 346 | 390.2 | 644.7 | 559.8 | 580 | 630.3 | 575.5 | 424.8 | 449 | 423.2 | 436.8 | 405.4 | 523.8 | 430.4
1726 | 1490 | 567.8 | 227.12 | 265.4902 | 423.9 | 589.1 | 384.5 | 382.9 | 532.4 | 74.5 | 16.9 | 130.9 | 6.7 | 206.6 | 6.1 | 870.4 | 853.5 | 519.9 | 855.4 | 719.5 | 866.2 | 738.2 | 672 | 766.8 | 604 | 679.5 | 753.4 | 306.1 | 346.2 | 390.2 | 644.2 | 559.9 | 575.9 | 630.2 | 575.6 | 424.9 | 448.5 | 423.1 | 436.9 | 405.5 | 523.8 | 430.5
1727 | 1491 | 565.7 | 226.28 | 264.5083 | 423.1 | 580.2 | 384.4 | 383.2 | 530.7 | 74.4 | 16.9 | 130.8 | 6.6 | 210.8 | 6 | 876 | 861.7 | 519.9 | 857.5 | 719.7 | 866.4 | 735.3 | 671.8 | 763.1 | 603.8 | 679.1 | 752.2 | 306.2 | 346.3 | 390.2 | 643.7 | 559.3 | 572.5 | 630.2 | 575 | 425 | 448.1 | 423.1 | 437 | 405.5 | 523.8 | 430.5
1728 | 1492 | 565 | 226 | 264.181 | 422.4 | 576.2 | 384.3 | 384.3 | 528.6 | 74.4 | 16.9 | 130.7 | 6.9 | 209.4 | 5.9 | 878.6 | 862.6 | 520.4 | 857.9 | 720.1 | 866.9 | 730.7 | 672.4 | 757.5 | 603.7 | 679.1 | 750.4 | 306.3 | 346.4 | 390.2 | 643.3 | 559.3 | 570.2 | 630 | 576.2 | 425.1 | 448.2 | 423 | 437.1 | 405.6 | 523.8 | 430.6
1729 | 1493 | 566.6 | 226.64 | 264.9291 | 421.2 | 575.6 | 383.8 | 385.5 | 525.7 | 74.4 | 16.9 | 130.7 | 6.2 | 206.6 | 6.1 | 874.9 | 855.2 | 520.8 | 855.8 | 720.1 | 866.8 | 729.4 | 673.5 | 757.2 | 603.9 | 679.7 | 750.6 | 306.4 | 346.5 | 390.3 | 642.8 | 559.3 | 567.8 | 629.7 | 576.5 | 425.1 | 448.8 | 423.3 | 437.3 | 405.7 | 523.8 | 430.7
1730 | 1494 | 567.6 | 227.04 | 265.3967 | 419.6 | 573.6 | 383.8 | 386.6 | 524.9 | 74.4 | 16.9 | 130.7 | 6 | 203.2 | 6.2 | 866.8 | 852.4 | 521.1 | 854.3 | 720.6 | 866.8 | 732 | 675.1 | 763.4 | 604.3 | 680.7 | 752.1 | 306.6 | 346.6 | 390.4 | 642.9 | 558.9 | 570.1 | 629.5 | 576.7 | 425.2 | 449.4 | 423.4 | 437.4 | 405.8 | 523.9 | 430.8
1731 | 1495 | 567 | 226.8 | 265.1161 | 419 | 575.1 | 384.2 | 386.9 | 526.7 | 74.4 | 16.9 | 130.7 | 5.9 | 200.8 | 6 | 867.9 | 856 | 522.2 | 854.7 | 721.4 | 866.2 | 732.9 | 676.8 | 766.4 | 604.6 | 680.8 | 751.9 | 306.8 | 346.7 | 390.5 | 642.7 | 559.4 | 569.9 | 629.5 | 576.3 | 425.3 | 450.1 | 424.1 | 437.6 | 406 | 523.9 | 430.8
1732 | 1496 | 567.8 | 227.12 | 265.4902 | 419.4 | 576.8 | 384.8 | 387.3 | 528.1 | 74.5 | 16.9 | 130.8 | 5.9 | 206.4 | 5.8 | 871.4 | 859.1 | 522.4 | 852.8 | 721.6 | 866.3 | 732.4 | 677 | 766 | 604.3 | 680.6 | 751.8 | 307 | 346.8 | 390.5 | 642.5 | 559.2 | 568.4 | 629.3 | 575.9 | 425.3 | 450.6 | 424.8 | 437.8 | 406.2 | 523.9 | 430.9
1733 | 1497 | 566.9 | 226.76 | 265.0694 | 419.1 | 568.5 | 385.3 | 387.5 | 528.5 | 74.7 | 16.9 | 130.8 | 5.6 | 203.5 | 5.7 | 873 | 851.8 | 522.5 | 852.2 | 721.5 | 866.5 | 733.3 | 675.1 | 764.6 | 603.8 | 681.1 | 751.9 | 307.1 | 346.9 | 390.6 | 642.2 | 558.6 | 567.5 | 629.1 | 574.5 | 425.4 | 450.4 | 424.5 | 437.9 | 406.3 | 523.9 | 431
1734 | 1498 | 566.1 | 226.44 | 264.6953 | 420.1 | 569.9 | 385.3 | 387.4 | 531 | 74.9 | 16.9 | 130.8 | 6.4 | 201.6 | 5.6 | 867.7 | 841.5 | 522 | 853.5 | 721.3 | 866.3 | 734.5 | 674.7 | 760 | 602.5 | 681 | 753 | 307.3 | 347 | 390.6 | 641.9 | 558.8 | 566.1 | 629 | 573.4 | 425.5 | 450.4 | 425 | 438 | 406.5 | 523.9 | 431
1735 | 1499 | 566.2 | 226.48 | 264.7421 | 421.2 | 566.2 | 384.8 | 387.2 | 530.8 | 75 | 16.9 | 130.9 | 5.7 | 206.3 | 5.6 | 865.2 | 838.7 | 521.2 | 854.6 | 721.1 | 866.2 | 733.7 | 675.5 | 759.1 | 601.5 | 680.7 | 754.1 | 307.4 | 347.1 | 390.7 | 641.7 | 558.5 | 561.8 | 629 | 572.3 | 425.6 | 450.6 | 426.1 | 438.1 | 406.6 | 523.9 | 431.1
1736 | 1500 | 565.7 | 226.28 | 264.5083 | 421.1 | 566.2 | 384.7 | 386.8 | 529.1 | 75 | 16.9 | 131 | 6 | 209.5 | 5.4 | 860.9 | 831.1 | 519.8 | 854.4 | 720.7 | 866.1 | 732.3 | 673.3 | 751.6 | 600.2 | 681.2 | 753.9 | 307.6 | 347.2 | 390.7 | 641.4 | 557.5 | 559.3 | 629.1 | 570.7 | 425.6 | 450.8 | 425.9 | 438.2 | 406.7 | 523.9 | 431.1
1737 | 1501 | 565.4 | 226.16 | 264.368 | 420.9 | 561.4 | 384.5 | 386.7 | 528.4 | 75.1 | 16.9 | 131 | 6.1 | 207.8 | 4.9 | 859.6 | 830.7 | 519.1 | 852.9 | 720.4 | 866.2 | 732 | 669.7 | 744 | 598.7 | 681.5 | 753.8 | 307.8 | 347.3 | 390.8 | 641 | 556.9 | 558.2 | 629.1 | 570 | 425.7 | 451 | 425.8 | 438.3 | 406.7 | 523.9 | 431.2
1738 | 1502 | 565.8 | 226.32 | 264.555 | 420.4 | 565.8 | 384.3 | 386.6 | 526.9 | 75.2 | 16.9 | 131.1 | 6.3 | 208.2 | 4.4 | 854.3 | 822.3 | 518.7 | 851.8 | 720 | 866.1 | 731.7 | 668.3 | 740.5 | 597.6 | 680.5 | 754.1 | 307.9 | 347.4 | 390.8 | 640.8 | 556.3 | 558.5 | 629.1 | 570.1 | 425.7 | 450.9 | 425.7 | 438.4 | 406.8 | 523.8 | 431.2
1739 | 1503 | 565.8 | 226.32 | 264.555 | 419.8 | 573.8 | 384.2 | 386.1 | 527 | 75.3 | 16.9 | 131.1 | 6 | 209.1 | 4.2 | 859 | 828 | 517.8 | 851 | 719.5 | 865.7 | 729 | 664.9 | 730.4 | 596.2 | 679.7 | 754.4 | 308.1 | 347.5 | 390.8 | 640 | 556 | 554.7 | 629.1 | 569.5 | 425.8 | 450.5 | 425.4 | 438.5 | 407.1 | 523.8 | 431.3
1740 | 1504 | 566.3 | 226.52 | 264.7888 | 419.4 | 572.4 | 383.8 | 385 | 524.8 | 75.3 | 16.9 | 131.1 | 6.3 | 208.3 | 4.3 | 861.7 | 837.2 | 517.3 | 849.6 | 719.3 | 866.1 | 727.3 | 663 | 727.2 | 595.1 | 679.3 | 754.3 | 308.3 | 347.6 | 390.9 | 639.6 | 555.5 | 551.4 | 628.7 | 567.9 | 425.8 | 450.7 | 425.6 | 438.5 | 407.1 | 523.8 | 431.3
1741 | 1505 | 565.8 | 226.32 | 264.555 | 419 | 572.1 | 383.7 | 384.6 | 524 | 75.4 | 16.9 | 131.1 | 6.3 | 204.5 | 4.2 | 859.9 | 833.7 | 516.6 | 847.2 | 719 | 866.5 | 727.2 | 661.8 | 728.7 | 594.8 | 678.7 | 754 | 308.4 | 347.7 | 391 | 639.2 | 554.8 | 551.4 | 628.7 | 567.1 | 425.8 | 452.1 | 425.4 | 438.6 | 407.1 | 523.7 | 431.3
1742 | 1506 | 566.1 | 226.44 | 264.6953 | 420.4 | 566.3 | 382.9 | 384.4 | 523.5 | 75.4 | 16.9 | 131 | 6.4 | 200.9 | 3.7 | 862.9 | 832.4 | 516.6 | 845.5 | 719.1 | 866.7 | 723.3 | 658.4 | 722.2 | 593.4 | 679.4 | 753.7 | 308.6 | 347.8 | 390.9 | 639 | 554 | 550.1 | 628.9 | 567.4 | 425.8 | 452.3 | 425.4 | 438.6 | 407.1 | 523.7 | 431.4
1743 | 1507 | 565.6 | 226.24 | 264.4615 | 420.6 | 570.3 | 382.2 | 384.3 | 522.3 | 75.3 | 16.9 | 131 | 5.7 | 209.2 | 3.6 | 866.8 | 833.8 | 515.8 | 844.3 | 719.5 | 867 | 721.6 | 660.6 | 727.2 | 595 | 679.3 | 753.1 | 308.8 | 347.9 | 391 | 638.8 | 553.9 | 550.8 | 628.7 | 569.6 | 425.9 | 452.5 | 425.8 | 438.7 | 407.2 | 523.6 | 431.4
1744 | 1508 | 565.6 | 226.24 | 264.4615 | 418.8 | 580.1 | 382 | 385.7 | 523.8 | 75.2 | 16.9 | 131 | 5.7 | 211.2 | 4.3 | 867.6 | 834.8 | 515.5 | 843.7 | 719.8 | 866.9 | 721.7 | 662.7 | 731.7 | 595.6 | 679.3 | 754.1 | 308.9 | 348 | 391 | 638.6 | 554.4 | 551.2 | 628.5 | 571.2 | 425.9 | 452.5 | 425.5 | 438.8 | 407.3 | 523.6 | 431.5
1745 | 1509 | 563.5 | 225.4 | 263.4796 | 417.4 | 584.5 | 381.7 | 386.9 | 524.6 | 75.2 | 16.9 | 131 | 6.5 | 213.8 | 4.7 | 870.5 | 835.2 | 515.9 | 843.3 | 719.9 | 866.2 | 721.8 | 665 | 731.5 | 597 | 678.9 | 755 | 309 | 348.1 | 391.1 | 638.6 | 555.4 | 553.7 | 628.2 | 573 | 426 | 452.6 | 425.8 | 438.9 | 407.4 | 523.7 | 431.6
1746 | 1510 | 565.9 | 226.36 | 264.6018 | 417.3 | 590.2 | 381.6 | 387.1 | 526.6 | 75.1 | 16.9 | 131 | 6.7 | 200.7 | 4.7 | 869.8 | 847.9 | 516.7 | 841.8 | 720.1 | 865.3 | 721 | 666.8 | 732.1 | 598.3 | 678.9 | 754.7 | 309.1 | 348.2 | 391.1 | 638.3 | 556.8 | 553 | 628 | 573.5 | 426 | 452.5 | 426.2 | 439 | 407.4 | 523.7 | 431.7
1747 | 1511 | 565.1 | 226.04 | 264.2277 | 416.2 | 593.8 | 381.8 | 387.2 | 526.6 | 75.1 | 16.9 | 131 | 6.8 | 204.1 | 4.8 | 870.7 | 859.6 | 517 | 841.4 | 720.8 | 865.5 | 724.1 | 669 | 739.5 | 598.6 | 679.1 | 754.9 | 309.3 | 348.3 | 391.3 | 638.6 | 556.1 | 558.1 | 627.9 | 573.9 | 426.1 | 452.1 | 426.2 | 439.2 | 407.4 | 523.7 | 431.7
1748 | 1512 | 563.8 | 225.52 | 263.6199 | 415.7 | 595.8 | 381.6 | 387.7 | 526.6 | 75.1 | 16.9 | 131 | 6.6 | 215.6 | 4.9 | 875.4 | 864.5 | 517.5 | 842.1 | 721.4 | 866.4 | 726.7 | 671.5 | 744.8 | 599.9 | 679.6 | 755.4 | 309.4 | 348.3 | 391.4 | 638.9 | 555.9 | 560.7 | 628.2 | 573.9 | 426.1 | 451.7 | 426.2 | 439.3 | 407.4 | 523.7 | 431.8
1749 | 1513 | 565.9 | 226.36 | 264.6018 | 416.6 | 587.1 | 381.9 | 387.9 | 527.6 | 75.1 | 16.9 | 131 | 6 | 212.5 | 4.7 | 876.5 | 857.6 | 517.8 | 842.2 | 721.6 | 866.3 | 728.1 | 671.6 | 748.5 | 600.8 | 679.9 | 755.9 | 309.5 | 348.4 | 391.4 | 639 | 556.3 | 562.1 | 628.4 | 573.3 | 426.2 | 451.8 | 426.2 | 439.5 | 407.3 | 523.8 | 431.8
1750 | 1514 | 565.4 | 226.16 | 264.368 | 418.7 | 582.3 | 382.2 | 387.3 | 529.3 | 75 | 16.9 | 131.1 | 6.2 | 195.2 | 4.5 | 875.4 | 848 | 517.8 | 842.9 | 721.5 | 866.3 | 729.8 | 671.2 | 746.9 | 599.9 | 679.7 | 757.3 | 309.6 | 348.5 | 391.5 | 639 | 556.3 | 562.5 | 628.5 | 571.8 | 426.3 | 452.4 | 426.2 | 439.6 | 407.3 | 523.7 | 431.9
1751 | 1515 | 564.6 | 225.84 | 263.9939 | 420.4 | 581.1 | 382.5 | 386.9 | 529.3 | 75 | 16.9 | 131.1 | 6.3 | 197.6 | 4.6 | 873.5 | 841.8 | 517.6 | 844.4 | 721.7 | 866.2 | 730.2 | 671.4 | 749.6 | 599.5 | 680 | 758.7 | 309.7 | 348.6 | 391.5 | 638.7 | 556.1 | 560.8 | 628.8 | 570.6 | 426.3 | 452.7 | 426.8 | 439.6 | 407.5 | 523.7 | 432
1752 | 1516 | 564.9 | 225.96 | 264.1342 | 422.2 | 578.2 | 382.7 | 386.3 | 529.5 | 75 | 16.9 | 131.2 | 6.5 | 205.2 | 4.7 | 862.4 | 830.3 | 517.4 | 844.9 | 721.7 | 866.3 | 733.2 | 672 | 751.5 | 599.2 | 680.5 | 758.1 | 309.8 | 348.7 | 391.6 | 638.7 | 555.7 | 561.9 | 629.2 | 569.8 | 426.3 | 452.5 | 426.8 | 439.7 | 407.5 | 523.7 | 432
1753 | 1517 | 567.1 | 226.84 | 265.1629 | 423.6 | 571.1 | 382.4 | 385.9 | 530.5 | 75 | 16.9 | 131.1 | 6.6 | 195 | 4.9 | 837.7 | 814.7 | 516.9 | 847.9 | 721.2 | 866.5 | 731.7 | 669.2 | 742.1 | 598.6 | 679.3 | 755.7 | 310 | 348.8 | 391.8 | 638.5 | 555.4 | 561.4 | 628.9 | 568.7 | 426.3 | 452.2 | 426 | 439.7 | 407.4 | 523.7 | 432.1
1754 | 1518 | 567.6 | 227.04 | 265.3967 | 423.2 | 562.7 | 382.9 | 385.9 | 531.2 | 74.9 | 16.9 | 131.1 | 6.6 | 194.9 | 4.7 | 825.3 | 801.2 | 516.3 | 847.7 | 720.6 | 865.4 | 727.7 | 663.6 | 725.5 | 595.1 | 678.1 | 754.4 | 310.1 | 348.9 | 392 | 638.3 | 555.1 | 558.5 | 628.8 | 566.8 | 426.4 | 451.8 | 425.8 | 439.8 | 407.4 | 523.6 | 432.1
1755 | 1519 | 565 | 226 | 264.181 | 422 | 566.9 | 383.6 | 385.3 | 530.1 | 75 | 16.9 | 131.2 | 6.3 | 200.1 | 4.6 | 820.3 | 800.3 | 516.1 | 844.9 | 720.2 | 865.1 | 722.3 | 658.8 | 716.4 | 591 | 677.2 | 753.6 | 310.2 | 349 | 391.9 | 637.8 | 554.8 | 554.5 | 628.6 | 565 | 426.4 | 451.4 | 425.6 | 439.9 | 407.5 | 523.6 | 432.1
1756 | 1520 | 564.8 | 225.92 | 264.0875 | 422 | 576.6 | 384.7 | 384.4 | 528.8 | 75 | 16.9 | 131.3 | 6.3 | 207.5 | 4.7 | 826.7 | 796.1 | 515.7 | 842 | 719.9 | 865.7 | 720.4 | 657.6 | 719.9 | 589 | 677.2 | 753.8 | 310.3 | 349.1 | 391.9 | 637.6 | 554 | 553.1 | 628.8 | 564.9 | 426.5 | 451.5 | 425.5 | 440 | 407.6 | 523.5 | 432.1
1757 | 1521 | 566.2 | 226.48 | 264.7421 | 423.8 | 576 | 384.2 | 383.7 | 528.4 | 75 | 16.9 | 131.4 | 6.3 | 205.5 | 5 | 828 | 801.4 | 515.8 | 840.8 | 719.6 | 865.4 | 716.6 | 657.8 | 711.2 | 589.8 | 676.9 | 753.7 | 310.4 | 349.1 | 391.9 | 637.3 | 554.3 | 552.9 | 628.9 | 567.3 | 426.5 | 453.2 | 426.7 | 440.1 | 407.9 | 523.5 | 432.2
1758 | 1522 | 566.4 | 226.56 | 264.8356 | 423.1 | 583.4 | 383.5 | 384.8 | 526.7 | 74.9 | 16.9 | 131.5 | 6.3 | 211.1 | 5.1 | 821.9 | 796.7 | 515.7 | 838.4 | 719.3 | 865.2 | 711.7 | 657.2 | 705.8 | 589.5 | 676.3 | 752.3 | 310.6 | 349.2 | 392 | 637.2 | 555.4 | 551.6 | 628.6 | 569.2 | 426.5 | 454.9 | 427.3 | 440.2 | 408.2 | 523.5 | 432.3
1759 | 1523 | 567.6 | 227.04 | 265.3967 | 421.8 | 589.6 | 382.8 | 386.6 | 525.9 | 74.9 | 16.9 | 131.5 | 6.3 | 221.4 | 4.9 | 821.3 | 790.7 | 515.7 | 834.9 | 718.9 | 864.7 | 707.8 | 654.7 | 698.6 | 588.5 | 678.3 | 750.3 | 310.6 | 349.3 | 392.1 | 637 | 556.2 | 551.5 | 628.3 | 569.6 | 426.5 | 456.3 | 428 | 440.3 | 408.4 | 523.5 | 432.5
1760 | 1524 | 568.3 | 227.32 | 265.724 | 421.6 | 592.9 | 382.3 | 387.7 | 525.1 | 74.8 | 16.9 | 131.6 | 6 | 217.7 | 5 | 825.6 | 795.4 | 516 | 831.4 | 718.6 | 865.1 | 705.2 | 653.1 | 695.8 | 588.7 | 678.9 | 749.6 | 310.7 | 349.3 | 392.1 | 636.7 | 556.6 | 548.8 | 628.1 | 569 | 426.6 | 457.7 | 428.8 | 440.4 | 408.4 | 523.5 | 432.7
1761 | 1525 | 568.2 | 227.28 | 265.6772 | 421 | 596.7 | 382.8 | 388.7 | 524.1 | 74.8 | 16.9 | 131.6 | 5.9 | 204.1 | 5.1 | 831 | 794.5 | 515.6 | 829.3 | 718.5 | 865.2 | 704.2 | 651.1 | 696.5 | 588.1 | 679.9 | 749.8 | 310.8 | 349.4 | 392 | 636.5 | 555.3 | 547.5 | 627.7 | 567.4 | 426.6 | 458.4 | 429.2 | 440.5 | 408.5 | 523.5 | 432.8
1762 | 1526 | 566 | 226.4 | 264.6486 | 420.6 | 593.2 | 382.6 | 389.1 | 523.4 | 74.7 | 16.9 | 131.8 | 5.8 | 203.7 | 5.2 | 829 | 801.1 | 515.8 | 828 | 718.5 | 865.5 | 703.8 | 648.7 | 701.7 | 585.9 | 681.2 | 750 | 310.9 | 349.5 | 392 | 636.1 | 554.4 | 546.6 | 627.5 | 565.9 | 426.7 | 458.4 | 429.1 | 440.7 | 408.5 | 523.5 | 432.9
1763 | 1527 | 565.6 | 226.24 | 264.4615 | 419.9 | 584.7 | 382 | 389.5 | 523.5 | 74.7 | 16.9 | 131.8 | 5.9 | 214.8 | 4.8 | 838.3 | 806.8 | 515.2 | 827.6 | 718.4 | 864.8 | 704.9 | 649.5 | 712.6 | 584.8 | 679.9 | 750.9 | 311 | 349.6 | 392 | 635.8 | 554.3 | 545.9 | 627.3 | 565.4 | 426.8 | 458.3 | 429.1 | 440.9 | 408.4 | 523.5 | 432.9
1764 | 1528 | 565.7 | 226.28 | 264.5083 | 420 | 581.5 | 381.1 | 389.3 | 524.9 | 74.8 | 16.9 | 131.8 | 6.4 | 234.8 | 4.4 | 844 | 808.2 | 515 | 828.8 | 718.4 | 865.3 | 708.7 | 652.9 | 726.4 | 586.3 | 678.7 | 752.8 | 311 | 349.7 | 392.1 | 635.9 | 554.3 | 547 | 627.2 | 566 | 426.9 | 457.6 | 428.1 | 441.1 | 408.4 | 523.4 | 433
1765 | 1529 | 565.9 | 226.36 | 264.6018 | 420.5 | 579.2 | 380.7 | 388.8 | 527 | 75 | 16.9 | 131.8 | 6.4 | 227.2 | 4.3 | 840.6 | 803.1 | 515.2 | 830.3 | 718.3 | 866 | 713.7 | 654 | 730.4 | 587.7 | 678.7 | 751.7 | 311 | 349.8 | 392.4 | 636.3 | 554.8 | 549.5 | 627.1 | 566.2 | 426.9 | 457 | 427.3 | 441.2 | 408.2 | 523.4 | 433
1766 | 1530 | 567.4 | 226.96 | 265.3032 | 421.7 | 577.4 | 380.4 | 388.7 | 530 | 75.1 | 16.9 | 131.9 | 6.2 | 213 | 4.5 | 845.3 | 803 | 515.9 | 830.3 | 718.1 | 866 | 711.8 | 650.2 | 718.5 | 586.7 | 678.3 | 748.9 | 311.1 | 349.9 | 392.6 | 636.4 | 555 | 548.7 | 626.9 | 565.2 | 427 | 456.9 | 427 | 441.3 | 408.1 | 523.4 | 433.1
1767 | 1531 | 566 | 226.4 | 264.6486 | 420.3 | 577.7 | 380.9 | 388 | 528.7 | 75.1 | 16.9 | 132 | 6.1 | 216.9 | 4.3 | 844 | 803.6 | 516.6 | 830.2 | 717.7 | 866.5 | 709.7 | 646.7 | 714.3 | 584.1 | 678.1 | 747.4 | 311.2 | 349.9 | 392.5 | 636.4 | 554.3 | 548.6 | 626.8 | 563.9 | 427 | 456.1 | 426.4 | 441.4 | 408.1 | 523.4 | 433.1
1768 | 1532 | 565.7 | 226.28 | 264.5083 | 419.8 | 573.7 | 381 | 387.4 | 527 | 75.2 | 16.9 | 132.1 | 5.8 | 218.9 | 4.5 | 847.6 | 812.8 | 518.2 | 830.6 | 717.6 | 866.2 | 711.5 | 648 | 721.9 | 584.2 | 677.5 | 748.8 | 311.3 | 350 | 392.5 | 636.1 | 553.5 | 548 | 626.8 | 563.5 | 427.1 | 455.5 | 426.4 | 441.5 | 408.2 | 523.3 | 433.1
1769 | 1533 | 565.7 | 226.28 | 264.5083 | 419.4 | 577.9 | 380.6 | 387.1 | 526.8 | 75.3 | 16.9 | 132.2 | 6.1 | 214.9 | 4.7 | 855.4 | 822.7 | 518.6 | 830.9 | 717.9 | 866 | 716.4 | 651.7 | 733.6 | 585.7 | 678.3 | 750.3 | 311.4 | 350.1 | 392.5 | 636 | 554.1 | 551.4 | 626.8 | 564.5 | 427.2 | 455.2 | 426.5 | 441.7 | 408.3 | 523.3 | 433.2
1770 | 1534 | 565.5 | 226.2 | 264.4148 | 418.8 | 575 | 380.3 | 387.1 | 528 | 75.4 | 16.9 | 132.3 | 6.3 | 199.8 | 5 | 864.8 | 823.8 | 517.6 | 831.2 | 717.7 | 865.9 | 719.1 | 653.9 | 734.5 | 587.7 | 679.4 | 751.9 | 311.6 | 350.1 | 392.6 | 636.2 | 554.1 | 554 | 627.2 | 565.9 | 427.3 | 455.5 | 426.5 | 441.8 | 408.3 | 523.3 | 433.2
1771 | 1535 | 565.6 | 226.24 | 264.4615 | 418.7 | 574 | 380.3 | 386.1 | 529.3 | 75.5 | 16.9 | 132.4 | 6.3 | 187.9 | 4.3 | 867 | 820.7 | 517.2 | 832.2 | 718 | 865.6 | 719 | 655.7 | 737.1 | 588.1 | 680 | 752 | 311.7 | 350.2 | 392.8 | 636.3 | 554.6 | 555.6 | 627.5 | 566.3 | 427.4 | 455.4 | 427.1 | 442 | 408.3 | 523.3 | 433.2
1772 | 1536 | 565.4 | 226.16 | 264.368 | 418.7 | 576.9 | 380.4 | 385.1 | 529.5 | 75.6 | 16.9 | 132.5 | 6.1 | 200.9 | 3.8 | 864.9 | 820.7 | 517.2 | 833.6 | 718.5 | 865 | 719.8 | 659 | 734.6 | 589.5 | 680.1 | 753.5 | 311.8 | 350.3 | 392.8 | 636.3 | 555 | 555.9 | 627.5 | 567.2 | 427.4 | 456.5 | 427.2 | 442.1 | 408.4 | 523.2 | 433.3
1773 | 1537 | 565.6 | 226.24 | 264.4615 | 420 | 573.7 | 380.5 | 385 | 530.1 | 75.7 | 16.9 | 132.5 | 6.3 | 210.4 | 3.6 | 860.8 | 814.8 | 517.4 | 833.4 | 718.9 | 864.5 | 716.1 | 659.3 | 726.1 | 590.6 | 680.6 | 752.9 | 312 | 350.4 | 392.8 | 636 | 556 | 554.3 | 627.3 | 567.3 | 427.5 | 458.2 | 427.3 | 442.2 | 408.4 | 523.2 | 433.4
1774 | 1538 | 567.7 | 227.08 | 265.4434 | 420.3 | 575 | 380.4 | 385.2 | 527.9 | 75.8 | 16.9 | 132.5 | 6.4 | 213.1 | 3.3 | 860.1 | 813.7 | 517.7 | 832.3 | 719.1 | 864.2 | 715.7 | 660.8 | 729 | 590.3 | 680.5 | 753.8 | 312.1 | 350.5 | 392.7 | 635.6 | 556.4 | 551.8 | 627.1 | 567 | 427.5 | 459.6 | 427.5 | 442.3 | 408.5 | 523.3 | 433.5
1775 | 1539 | 568 | 227.2 | 265.5837 | 420.7 | 578.5 | 380.6 | 385.4 | 525.6 | 75.9 | 16.9 | 132.4 | 6.4 | 210.1 | 2.8 | 862 | 820.6 | 519.1 | 831.4 | 719.2 | 863 | 720.2 | 664.1 | 739.5 | 590.3 | 680.9 | 754.3 | 312.2 | 350.6 | 392.9 | 635.8 | 555.3 | 554.3 | 627.1 | 565.7 | 427.6 | 460.5 | 427.1 | 442.4 | 408.4 | 523.3 | 433.6
1776 | 1540 | 568.9 | 227.56 | 266.0045 | 420.6 | 575.9 | 380.5 | 385.3 | 527.3 | 76.1 | 16.9 | 132.4 | 6.4 | 208.4 | 2.5 | 862.3 | 821.8 | 520.1 | 831.5 | 719.4 | 861.8 | 726.3 | 669.5 | 749.4 | 593.1 | 681.9 | 756.1 | 312.4 | 350.6 | 393.1 | 636.8 | 555 | 566.2 | 627.5 | 567 | 427.6 | 460.2 | 427 | 442.4 | 408.4 | 523.2 | 433.6
1777 | 1541 | 567.6 | 227.04 | 265.3967 | 420 | 572.6 | 380.5 | 385.1 | 532.1 | 76.1 | 16.9 | 132.4 | 6.4 | 207.1 | 2.5 | 857.8 | 824.2 | 519.9 | 832.2 | 719.7 | 861.1 | 730.5 | 671.8 | 753.1 | 595.1 | 682.5 | 756.1 | 312.5 | 350.8 | 393.4 | 637.5 | 556.1 | 573 | 627.4 | 568.7 | 427.7 | 459.4 | 427.5 | 442.5 | 408.4 | 523.2 | 433.7
1778 | 1542 | 565.6 | 226.24 | 264.4615 | 419.1 | 570 | 381.2 | 384.4 | 534.8 | 76.1 | 16.9 | 132.4 | 6.2 | 206.5 | 2.6 | 857.1 | 820.3 | 520.5 | 832.6 | 719.8 | 860.7 | 732.3 | 671.9 | 748.9 | 594.7 | 682.6 | 757.2 | 312.6 | 350.8 | 393.4 | 637.8 | 556.8 | 571.6 | 627.4 | 567.5 | 427.8 | 458.9 | 427 | 442.7 | 408.4 | 523.2 | 433.7
1779 | 1543 | 565.5 | 226.2 | 264.4148 | 418.5 | 566.4 | 382.3 | 384.1 | 537.3 | 76.1 | 16.9 | 132.4 | 6.2 | 209.1 | 3.1 | 856.5 | 822.3 | 520 | 832.3 | 720.1 | 860 | 734.2 | 672.3 | 750.6 | 594.5 | 682.1 | 758.5 | 312.7 | 350.9 | 393.7 | 638.3 | 557.4 | 574.2 | 627.4 | 566.2 | 427.8 | 458.4 | 426.6 | 442.7 | 408.3 | 523.2 | 433.7
1780 | 1544 | 565.7 | 226.28 | 264.5083 | 418.3 | 567 | 383.1 | 383.9 | 540.3 | 76 | 16.9 | 132.3 | 5.8 | 216.6 | 3.9 | 860.5 | 827.4 | 520.3 | 831.4 | 720.4 | 860.2 | 736.4 | 675.1 | 755.6 | 596.3 | 682 | 759.9 | 312.9 | 351 | 393.7 | 638.9 | 558 | 580.4 | 627.5 | 566.9 | 427.9 | 457.3 | 426.6 | 442.8 | 408.4 | 523.2 | 433.7
1781 | 1545 | 567.4 | 226.96 | 265.3032 | 417.8 | 564.8 | 383.2 | 383.4 | 541.3 | 75.9 | 16.9 | 132.3 | 5.9 | 223 | 4.7 | 861.7 | 829.3 | 522 | 831.9 | 720.6 | 860.3 | 734.2 | 676.4 | 748.9 | 596.8 | 682.7 | 760.1 | 313 | 351.1 | 393.5 | 638.9 | 558.5 | 578.8 | 627.5 | 567.8 | 427.9 | 456.2 | 426.9 | 442.9 | 408.5 | 523.1 | 433.7
1782 | 1546 | 567.4 | 226.96 | 265.3032 | 417.9 | 572.7 | 382.4 | 382.8 | 540.1 | 75.8 | 16.9 | 132.3 | 5.9 | 225.3 | 4.9 | 864.3 | 833 | 522.4 | 833.1 | 720.8 | 861.3 | 731.5 | 677.2 | 747.9 | 597.1 | 683.3 | 760.1 | 313.1 | 351.2 | 393.5 | 638.6 | 558.6 | 577 | 627.5 | 567.5 | 428 | 456.3 | 427 | 443 | 408.6 | 523.2 | 433.8
1783 | 1547 | 568.6 | 227.44 | 265.8643 | 417.7 | 580.4 | 382.6 | 382.5 | 538.1 | 75.8 | 16.9 | 132.4 | 6 | 222.8 | 5 | 868.8 | 829.6 | 523.6 | 833.8 | 720.9 | 862 | 730.6 | 676.7 | 748.5 | 596.8 | 684.1 | 759.3 | 313.3 | 351.3 | 393.5 | 638.7 | 558.2 | 576.1 | 627.4 | 566.8 | 428 | 456.4 | 427.1 | 443.1 | 408.5 | 523.2 | 433.8
1784 | 1548 | 567.8 | 227.12 | 265.4902 | 418.8 | 575.9 | 383.1 | 382.4 | 536.3 | 75.8 | 16.9 | 132.2 | 5.6 | 216.1 | 5.1 | 863.4 | 827.2 | 524.1 | 833.3 | 721.2 | 861.4 | 732.6 | 678 | 752.9 | 596.7 | 683.7 | 761.4 | 313.4 | 351.4 | 393.6 | 638.6 | 557.8 | 574.9 | 627.7 | 566.4 | 428.1 | 455.7 | 426.7 | 443.1 | 408.5 | 523.2 | 433.9
1785 | 1549 | 566.7 | 226.68 | 264.9759 | 419.7 | 577.5 | 383.4 | 382 | 535.3 | 75.9 | 16.9 | 132.2 | 5.5 | 204.5 | 5.2 | 862.3 | 824.1 | 524.1 | 835.3 | 721.4 | 861.4 | 734.6 | 680.6 | 756 | 597.3 | 683.3 | 762.4 | 313.5 | 351.5 | 393.7 | 638.5 | 558 | 573.5 | 627.6 | 566.9 | 428.1 | 454.8 | 427 | 443.2 | 408.5 | 523.2 | 433.9
1786 | 1550 | 566.4 | 226.56 | 264.8356 | 421 | 578 | 383.2 | 381.4 | 535.4 | 75.9 | 16.9 | 132.2 | 6.1 | 200 | 5.3 | 854.5 | 821 | 523.2 | 839 | 721.6 | 860.9 | 734.6 | 682.2 | 755.9 | 598.1 | 684.7 | 763 | 313.6 | 351.5 | 393.7 | 638.6 | 558.8 | 573.1 | 627.3 | 568 | 428.1 | 453.7 | 427.5 | 443.2 | 408.6 | 523.1 | 433.9
1787 | 1551 | 566.9 | 226.76 | 265.0694 | 422.2 | 580.3 | 383.5 | 381.3 | 534.4 | 75.9 | 16.9 | 132.1 | 6.3 | 204.3 | 5.1 | 856.6 | 819.1 | 524.1 | 839.7 | 721.9 | 860.7 | 734.4 | 684.5 | 754.2 | 598.9 | 685.1 | 764.5 | 313.7 | 351.6 | 393.8 | 638.4 | 559 | 570.6 | 627.2 | 568.5 | 428.2 | 453 | 427.8 | 443.3 | 408.6 | 523.1 | 434
1788 | 1552 | 568.4 | 227.36 | 265.7707 | 421.5 | 582.2 | 384 | 381.8 | 532.7 | 75.9 | 16.9 | 132.1 | 6.1 | 199.5 | 5 | 860.6 | 825 | 524.9 | 837.9 | 722.4 | 860.8 | 733 | 684 | 749.2 | 598.6 | 685.6 | 764 | 313.8 | 351.7 | 393.8 | 638 | 558.5 | 567.4 | 627.5 | 568.3 | 428.2 | 452.2 | 428 | 443.4 | 408.5 | 523.1 | 434
1789 | 1553 | 567.5 | 227 | 265.3499 | 420.4 | 586.3 | 383.8 | 382.7 | 529.5 | 75.9 | 16.8 | 132 | 6.1 | 202.2 | 5 | 859.8 | 824.4 | 525.7 | 835.1 | 722.6 | 861.7 | 732.5 | 683.4 | 751.4 | 597.8 | 687.1 | 764.1 | 313.9 | 351.7 | 393.7 | 637.9 | 557.8 | 565.8 | 627.4 | 567.4 | 428.3 | 451.4 | 427.8 | 443.6 | 408.5 | 523.1 | 434.1
1790 | 1554 | 566.4 | 226.56 | 264.8356 | 419.4 | 591.5 | 383.6 | 383.2 | 528.4 | 75.9 | 16.8 | 132 | 5.5 | 216.9 | 4.9 | 865.4 | 833.8 | 525.5 | 833.5 | 722.8 | 862.2 | 730.7 | 681.2 | 748.3 | 596.8 | 686.9 | 763.4 | 314.1 | 351.8 | 393.8 | 637.6 | 557.2 | 565.2 | 627.2 | 567.2 | 428.4 | 451.5 | 428.2 | 443.7 | 408.6 | 523.1 | 434.1
1791 | 1555 | 565.8 | 226.32 | 264.555 | 419.3 | 596.1 | 383.1 | 383.4 | 528 | 76 | 16.9 | 131.9 | 5.7 | 217.5 | 4.7 | 870 | 842.7 | 526.2 | 832.2 | 723.1 | 863.1 | 728.6 | 680.7 | 747.3 | 596.7 | 686.6 | 762.6 | 314.2 | 351.9 | 393.8 | 637.4 | 557.1 | 564.3 | 627 | 567.5 | 428.4 | 452.4 | 428.6 | 443.8 | 408.7 | 523.1 | 434.2
1792 | 1556 | 564.9 | 225.96 | 264.1342 | 418.6 | 596.6 | 383 | 384.4 | 526.8 | 76 | 16.9 | 131.9 | 6.2 | 206.3 | 4.4 | 870.8 | 845.6 | 526.1 | 832 | 723.4 | 863.3 | 724.8 | 678.8 | 742.6 | 596.2 | 686.6 | 760.5 | 314.3 | 351.9 | 393.8 | 637.2 | 557.2 | 560.8 | 627 | 567.1 | 428.5 | 453.8 | 428.2 | 443.9 | 408.8 | 523.1 | 434.3
1793 | 1557 | 566 | 226.4 | 264.6486 | 418.2 | 595.9 | 383.1 | 385.1 | 525.6 | 76 | 16.8 | 131.9 | 6.2 | 195.9 | 4.3 | 876.1 | 847.2 | 525.7 | 830.6 | 723.7 | 863.3 | 724 | 680.3 | 744.9 | 597.2 | 687.4 | 760.6 | 314.5 | 352 | 393.9 | 637.1 | 557 | 560 | 626.8 | 567.5 | 428.5 | 453.7 | 428.4 | 444 | 408.9 | 523.2 | 434.3
1794 | 1558 | 565.3 | 226.12 | 264.3213 | 418.2 | 593.1 | 383.2 | 385.9 | 526.9 | 76.1 | 16.8 | 131.8 | 6.3 | 197.4 | 4.3 | 881.2 | 854.9 | 526.5 | 829.5 | 723.6 | 863.4 | 723.3 | 679 | 742.5 | 597.4 | 688.2 | 760.1 | 314.6 | 352.1 | 393.9 | 637.1 | 557.2 | 561.6 | 626.7 | 568.4 | 428.5 | 454.3 | 428.2 | 444 | 409 | 523.2 | 434.4
1795 | 1559 | 566 | 226.4 | 264.6486 | 418.1 | 591.5 | 383.2 | 386.3 | 528.2 | 76.2 | 16.8 | 131.9 | 6.7 | 196.1 | 4.7 | 882.1 | 850.4 | 527.1 | 830.4 | 723.4 | 864.6 | 723.1 | 677.4 | 743.1 | 597.3 | 688.7 | 760.2 | 314.8 | 352.1 | 394 | 637.1 | 557.4 | 561.9 | 627.1 | 568.4 | 428.6 | 455.5 | 427.1 | 444.1 | 409 | 523.2 | 434.5
1796 | 1560 | 566.4 | 226.56 | 264.8356 | 417.8 | 590.5 | 383.5 | 386.8 | 528.1 | 76.2 | 16.8 | 131.9 | 6.3 | 207.3 | 5.2 | 882 | 853.2 | 527.2 | 830.2 | 723.4 | 865.2 | 722.6 | 678 | 742.9 | 597.5 | 687 | 760.6 | 314.9 | 352.2 | 393.9 | 636.9 | 557.2 | 561.3 | 627.2 | 568.8 | 428.6 | 457 | 427 | 444.1 | 409.1 | 523.2 | 434.5
1797 | 1561 | 565 | 226 | 264.181 | 417.8 | 585.3 | 383.8 | 387.6 | 527.1 | 76.2 | 16.8 | 131.9 | 6.6 | 215.1 | 5.2 | 878.6 | 855.2 | 528.2 | 829.8 | 723.3 | 865.3 | 721.1 | 677.8 | 740.9 | 597.9 | 687 | 758.8 | 315 | 352.3 | 394 | 636.6 | 557.2 | 558.7 | 627.2 | 570.2 | 428.6 | 457.7 | 427.9 | 444.2 | 409.2 | 523.2 | 434.6
1798 | 1562 | 564.9 | 225.96 | 264.1342 | 417.8 | 586.6 | 383.3 | 388.3 | 525.8 | 76.1 | 16.8 | 131.9 | 6.3 | 207.4 | 5.1 | 876.8 | 850.9 | 528.8 | 828.7 | 723.1 | 865.5 | 719 | 676.9 | 736.7 | 597.8 | 686.2 | 757.6 | 315.2 | 352.3 | 394 | 636.4 | 557 | 557.5 | 627.2 | 569.5 | 428.6 | 458.1 | 428.3 | 444.3 | 409.3 | 523.3 | 434.7
1799 | 1563 | 566.3 | 226.52 | 264.7888 | 417 | 582.1 | 382.8 | 389 | 524.8 | 76 | 16.8 | 132 | 6 | 203.1 | 5.1 | 878.4 | 852.2 | 529.6 | 827.8 | 722.9 | 865.7 | 718.2 | 676.5 | 734.4 | 598 | 684.1 | 758.2 | 315.3 | 352.4 | 394.1 | 636.3 | 556.9 | 555.7 | 627.2 | 568.6 | 428.7 | 458.1 | 428.9 | 444.4 | 409.5 | 523.3 | 434.8
1800 | 1564 | 567.2 | 226.88 | 265.2096 | 416.7 | 584.5 | 383.7 | 389.3 | 524.8 | 76 | 16.8 | 132.1 | 6.4 | 205.6 | 5 | 874.9 | 847.4 | 530.3 | 826.6 | 722.8 | 866.3 | 716 | 675.1 | 727.6 | 598.4 | 683.3 | 757.1 | 315.4 | 352.5 | 394.1 | 636 | 557.1 | 553.2 | 627.1 | 568.7 | 428.7 | 458.4 | 429.5 | 444.5 | 409.7 | 523.3 | 434.8
1801 | 1565 | 567.6 | 227.04 | 265.3967 | 417.4 | 578.2 | 384.1 | 390.1 | 523.1 | 75.8 | 16.8 | 132.3 | 6.3 | 201.8 | 4.9 | 862.4 | 839.3 | 531.5 | 824.7 | 722.6 | 866.8 | 712.6 | 671.8 | 720.9 | 595.4 | 685.5 | 756.1 | 315.6 | 352.6 | 394.1 | 635.7 | 557 | 549.3 | 627 | 567.8 | 428.8 | 459.4 | 429.9 | 444.7 | 409.8 | 523.3 | 434.9
1802 | 1566 | 567.8 | 227.12 | 265.4902 | 416.9 | 567.7 | 384 | 390.8 | 519.6 | 75.8 | 16.8 | 132.3 | 6.2 | 193.2 | 4.6 | 856.1 | 834.6 | 531.2 | 823 | 722.2 | 866.7 | 712.3 | 667.1 | 718.5 | 592.9 | 686.2 | 754.3 | 315.7 | 352.7 | 394.1 | 635.5 | 556.2 | 549.3 | 627 | 565.7 | 428.9 | 459.8 | 429.4 | 444.8 | 409.7 | 523.3 | 435
1803 | 1567 | 566.9 | 226.76 | 265.0694 | 416.4 | 562.1 | 383.7 | 390.9 | 521.7 | 75.8 | 16.8 | 132.3 | 6.1 | 216.3 | 4.7 | 855.2 | 827.3 | 531.6 | 822.5 | 721.5 | 866.9 | 714 | 663.4 | 713.9 | 592.1 | 686 | 754.2 | 315.8 | 352.8 | 394.4 | 635.5 | 555.7 | 550.7 | 627.2 | 564.4 | 428.9 | 459.4 | 428.7 | 444.9 | 409.6 | 523.3 | 435.1
1804 | 1568 | 564 | 225.6 | 263.7134 | 416.6 | 564.3 | 383.2 | 390.2 | 523.4 | 75.9 | 16.8 | 132.4 | 5.9 | 217.4 | 5.4 | 859.7 | 827.9 | 531.9 | 821.7 | 721 | 866.7 | 715.9 | 661.4 | 717.5 | 591.4 | 685.3 | 756 | 316 | 352.9 | 394.4 | 635.8 | 555 | 553.7 | 627.4 | 564.4 | 429 | 458.7 | 428.1 | 445 | 409.6 | 523.3 | 435.1
1805 | 1569 | 562.8 | 225.12 | 263.1523 | 416.8 | 572.5 | 383 | 389.1 | 525.7 | 75.9 | 16.8 | 132.4 | 6 | 200.6 | 5.5 | 860.3 | 832.9 | 531.6 | 821.6 | 720.9 | 866.9 | 717.6 | 661.6 | 725.4 | 591.7 | 684.7 | 757.1 | 316.1 | 352.9 | 394.4 | 635.8 | 555 | 554.5 | 628 | 564.9 | 429 | 457.8 | 428.4 | 445.1 | 409.6 | 523.3 | 435.1
1806 | 1570 | 563.9 | 225.56 | 263.6666 | 417.9 | 574.8 | 382.7 | 388.3 | 527.1 | 76 | 16.8 | 132.3 | 6.1 | 208.7 | 5.6 | 863.4 | 835.4 | 531.3 | 823.2 | 721.2 | 867.1 | 720.9 | 664.1 | 732.3 | 593.1 | 685.6 | 758.2 | 316.3 | 353 | 394.4 | 635.9 | 555.4 | 557.3 | 628 | 565.6 | 429.1 | 457.6 | 427.8 | 445.1 | 409.6 | 523.2 | 435.1
1807 | 1571 | 563.9 | 225.56 | 263.6666 | 418.9 | 576.1 | 382.5 | 388.7 | 529.5 | 76 | 16.8 | 132.3 | 6.5 | 223.2 | 5.5 | 867 | 839.5 | 531.7 | 824.2 | 721.6 | 866.8 | 722.4 | 666.5 | 736.7 | 594.5 | 686.9 | 758.3 | 316.4 | 353.1 | 394.5 | 635.9 | 556.2 | 559.5 | 628 | 567.1 | 429.1 | 458.5 | 427.9 | 445.2 | 409.6 | 523.2 | 435.2
1808 | 1572 | 564.6 | 225.84 | 263.9939 | 418.4 | 574.9 | 382.3 | 388.9 | 528.7 | 76.1 | 16.8 | 132.2 | 5.6 | 226.8 | 5.1 | 873.4 | 839.8 | 531.5 | 825.1 | 722.2 | 867.1 | 722.9 | 666.2 | 738 | 595.3 | 687.1 | 759.2 | 316.6 | 353.1 | 394.5 | 636 | 556.3 | 559.6 | 627.7 | 567.9 | 429.1 | 458.6 | 428.6 | 445.2 | 409.7 | 523.3 | 435.2
1809 | 1573 | 565.3 | 226.12 | 264.3213 | 417.2 | 582.8 | 382.3 | 389.6 | 528.7 | 76.1 | 16.8 | 132.1 | 5.8 | 221.7 | 4.7 | 874.3 | 844.2 | 532 | 824.9 | 722.6 | 867.4 | 724.3 | 668.4 | 740.4 | 596.1 | 686.2 | 760.5 | 316.7 | 353.2 | 394.5 | 635.9 | 556 | 559.3 | 627.7 | 567.8 | 429.2 | 458.5 | 428.3 | 445.3 | 409.7 | 523.3 | 435.3
1810 | 1574 | 567.1 | 226.84 | 265.1629 | 416.2 | 590.2 | 382.5 | 389.8 | 527.2 | 76.1 | 16.8 | 132.1 | 5.9 | 215.4 | 4.2 | 878.2 | 846.8 | 532.6 | 825.4 | 722.9 | 868.6 | 722.3 | 668.9 | 738.9 | 596.3 | 684.5 | 760.1 | 316.9 | 353.3 | 394.5 | 635.6 | 555.5 | 558.1 | 627.7 | 567.6 | 429.2 | 458.9 | 428.1 | 445.4 | 409.8 | 523.3 | 435.3
1811 | 1575 | 567 | 226.8 | 265.1161 | 415.7 | 592.3 | 382.5 | 390 | 525.8 | 76.2 | 16.8 | 132.1 | 6.3 | 226 | 3.4 | 878.3 | 843.8 | 533.1 | 826.5 | 722.8 | 869.1 | 722.2 | 671.9 | 740.1 | 597 | 684.4 | 760.2 | 317 | 353.3 | 394.5 | 635.6 | 555.5 | 557.4 | 627.5 | 567.9 | 429.3 | 458.8 | 428.3 | 445.5 | 409.9 | 523.3 | 435.4
1812 | 1576 | 568.1 | 227.24 | 265.6305 | 415.5 | 593.3 | 382.1 | 390.2 | 526.1 | 76.2 | 16.8 | 132.1 | 6.8 | 251.5 | 2.9 | 873.8 | 838.8 | 533.9 | 826 | 722.8 | 869.7 | 719.6 | 671.9 | 732.9 | 596.9 | 683.9 | 757.9 | 317.1 | 353.4 | 394.6 | 635.4 | 555.9 | 554.5 | 627.4 | 568.1 | 429.3 | 458.9 | 429 | 445.6 | 410 | 523.3 | 435.5
1813 | 1577 | 565.5 | 226.2 | 264.4148 | 415.5 | 597.2 | 381.3 | 390.8 | 523.1 | 76.2 | 16.8 | 132.1 | 6.6 | 263.1 | 3.1 | 868.4 | 830.7 | 533.4 | 824.2 | 722.5 | 870.3 | 714.1 | 669.7 | 721.5 | 595.4 | 685.1 | 755.5 | 317.2 | 353.5 | 394.5 | 635 | 555.3 | 551.4 | 627.2 | 566.9 | 429.4 | 459.9 | 429.9 | 445.7 | 410.2 | 523.3 | 435.6
1814 | 1578 | 565.1 | 226.04 | 264.2277 | 415.8 | 589.8 | 381.3 | 391.8 | 520.2 | 76.2 | 16.8 | 132.1 | 6.3 | 252.4 | 3.7 | 863.5 | 818.9 | 532.4 | 821.8 | 722 | 870.2 | 709.8 | 667.5 | 716.7 | 594.4 | 686.9 | 754.7 | 317.4 | 353.6 | 394.5 | 634.7 | 554.2 | 549.9 | 627.4 | 566.3 | 429.5 | 460.5 | 429.5 | 445.8 | 410.3 | 523.3 | 435.7
1815 | 1579 | 564.1 | 225.64 | 263.7602 | 416.6 | 583.6 | 381.4 | 392.9 | 519.3 | 76.2 | 16.8 | 132.1 | 5.5 | 230.2 | 4.2 | 861.9 | 822.7 | 532 | 819.9 | 721.7 | 870.5 | 706.8 | 665.9 | 714.3 | 593.7 | 685.8 | 754.1 | 317.5 | 353.7 | 394.5 | 634.4 | 553.2 | 549.6 | 627.5 | 566.4 | 429.5 | 460.6 | 429 | 446 | 410.3 | 523.3 | 435.7
1816 | 1580 | 566.1 | 226.44 | 264.6953 | 416.9 | 577.9 | 381.2 | 393 | 517.8 | 76.3 | 16.8 | 132.1 | 6 | 217.6 | 4.4 | 850.4 | 815.1 | 531.4 | 817.1 | 721.3 | 870.2 | 703.3 | 663.2 | 707.3 | 592.9 | 685.4 | 752.4 | 317.6 | 353.7 | 394.6 | 633.9 | 553.4 | 547.5 | 627.5 | 565.6 | 429.6 | 461.3 | 429.6 | 446.1 | 410.5 | 523.3 | 435.8
1817 | 1581 | 566.3 | 226.52 | 264.7888 | 416.7 | 578.8 | 380.9 | 393.4 | 515.9 | 76.4 | 16.8 | 132.1 | 6.5 | 204.6 | 4.5 | 828.1 | 796.7 | 532 | 813.9 | 720.5 | 868.5 | 700 | 659.2 | 698.2 | 591.8 | 684.9 | 750.5 | 317.7 | 353.8 | 394.6 | 633.6 | 553.8 | 546.5 | 627.7 | 565.8 | 429.7 | 463.2 | 430.3 | 446.2 | 410.8 | 523.3 | 435.9
1818 | 1582 | 565.6 | 226.24 | 264.4615 | 417.6 | 579.1 | 380.2 | 394.3 | 515.7 | 76.4 | 16.8 | 132.2 | 6.5 | 195.9 | 4.8 | 820.3 | 790.7 | 531.3 | 810.3 | 720 | 866.4 | 695.5 | 653.6 | 685.6 | 588.9 | 683.6 | 748.1 | 317.9 | 353.9 | 394.7 | 633.3 | 554.1 | 544.9 | 627.3 | 564.8 | 429.8 | 465 | 431.8 | 446.5 | 411 | 523.3 | 436
1819 | 1583 | 565.8 | 226.32 | 264.555 | 418.5 | 582.2 | 380 | 395.3 | 514.5 | 76.5 | 16.8 | 132.3 | 6.5 | 196.4 | 4.5 | 817.6 | 782 | 529.8 | 807 | 719.5 | 865.2 | 691.8 | 649.8 | 681.7 | 587.4 | 683.1 | 746.3 | 318 | 353.9 | 394.7 | 633 | 554.1 | 543.8 | 627.2 | 564.5 | 429.9 | 466.5 | 433.9 | 446.8 | 411.2 | 523.3 | 436.2
1820 | 1584 | 565.9 | 226.36 | 264.6018 | 418.5 | 580 | 380.4 | 396.8 | 515.1 | 76.5 | 16.8 | 132.4 | 6.3 | 208.3 | 4 | 817 | 787.1 | 528.8 | 804 | 719.2 | 863.3 | 688.6 | 647.5 | 679 | 587 | 683.8 | 744.6 | 318.1 | 354 | 394.7 | 632.7 | 554.7 | 540.6 | 627.2 | 564.7 | 430 | 468.4 | 434.3 | 447 | 411.3 | 523.3 | 436.3
1821 | 1585 | 565.5 | 226.2 | 264.4148 | 418 | 573.8 | 380.6 | 397.9 | 513.7 | 76.6 | 16.8 | 132.5 | 6.5 | 245.9 | 3.7 | 817.7 | 793.4 | 527.9 | 802.2 | 719 | 863 | 686.6 | 644.4 | 678.9 | 585.8 | 683.1 | 743.4 | 318.2 | 354.1 | 394.7 | 632.3 | 554.1 | 538.6 | 627 | 564.6 | 430.2 | 469.3 | 435 | 447.3 | 411.4 | 523.3 | 436.5
1822 | 1586 | 566.2 | 226.48 | 264.7421 | 417.2 | 566.9 | 380.8 | 399 | 513.3 | 76.6 | 16.8 | 132.7 | 5.9 | 266.9 | 3.6 | 823.2 | 796.5 | 528.1 | 801.8 | 718.6 | 863.6 | 684.8 | 642 | 682.1 | 585.7 | 682 | 741.9 | 318.3 | 354.1 | 394.7 | 632.1 | 553.6 | 538.8 | 627.2 | 564.2 | 430.3 | 469.4 | 434.9 | 447.6 | 411.4 | 523.4 | 436.6
1823 | 1587 | 566.9 | 226.76 | 265.0694 | 416.5 | 578.5 | 381.1 | 400.1 | 513.5 | 76.6 | 16.8 | 132.7 | 5.9 | 249.1 | 3.6 | 829.1 | 800 | 528 | 802.6 | 718.5 | 864 | 687.4 | 641 | 689 | 585.5 | 682.7 | 742.6 | 318.4 | 354.2 | 394.7 | 631.8 | 553.1 | 539.6 | 627 | 562.9 | 430.5 | 468.9 | 435.2 | 447.8 | 411.4 | 523.3 | 436.7
1824 | 1588 | 566.9 | 226.76 | 265.0694 | 415.8 | 586.7 | 381.1 | 400 | 516.2 | 76.6 | 16.8 | 132.7 | 6.3 | 246.4 | 3.7 | 831.6 | 798.1 | 529.1 | 803.9 | 718.5 | 864.5 | 694.3 | 640.6 | 696.1 | 584.6 | 684.2 | 744.5 | 318.5 | 354.3 | 394.9 | 632 | 553.2 | 543.7 | 627.1 | 562.5 | 430.7 | 468.1 | 435 | 448.1 | 411.3 | 523.3 | 436.7
1825 | 1589 | 567.2 | 226.88 | 265.2096 | 417.7 | 587.8 | 380.9 | 399.3 | 519 | 76.6 | 16.8 | 132.8 | 6.1 | 246.4 | 3.7 | 823.8 | 789.3 | 530 | 804.5 | 718.5 | 864.6 | 696.9 | 639.6 | 698.8 | 583.5 | 684.6 | 745.8 | 318.6 | 354.4 | 394.8 | 632 | 553.4 | 544.6 | 627.8 | 561.6 | 430.8 | 467.5 | 435 | 448.3 | 411.3 | 523.3 | 436.8
1826 | 1590 | 566.5 | 226.6 | 264.8823 | 420.4 | 590.2 | 381.4 | 398.1 | 519.5 | 76.6 | 16.8 | 132.8 | 6.6 | 245.4 | 3.7 | 821.6 | 786.1 | 530.8 | 804.6 | 718.3 | 864.4 | 697.5 | 637.8 | 699.6 | 582.9 | 683.8 | 746.4 | 318.7 | 354.4 | 395 | 631.9 | 552.6 | 545 | 627.9 | 560.7 | 431 | 467.4 | 434.4 | 448.4 | 411.3 | 523.3 | 436.8
1827 | 1591 | 566.4 | 226.56 | 264.8356 | 423.2 | 592 | 381.3 | 396.6 | 522.1 | 76.5 | 16.8 | 132.8 | 6.5 | 255.8 | 4 | 824.7 | 783.8 | 530.9 | 804.6 | 718.1 | 865 | 698.2 | 637.5 | 699 | 581.5 | 682.2 | 747.2 | 318.8 | 354.5 | 395 | 631.9 | 553.1 | 545.2 | 628.5 | 560.5 | 431.1 | 467.5 | 434.5 | 448.5 | 411.3 | 523.2 | 436.8
1828 | 1592 | 566.4 | 226.56 | 264.8356 | 425.2 | 590.1 | 380.8 | 395.4 | 524.1 | 76.5 | 16.8 | 132.7 | 6.3 | 272.5 | 4.1 | 824.6 | 782 | 531.2 | 803.9 | 718 | 864.7 | 697.4 | 637.5 | 697.1 | 580.6 | 681.8 | 747.1 | 318.9 | 354.6 | 395 | 631.6 | 553.1 | 543.7 | 629.1 | 560.7 | 431.2 | 467.2 | 434.5 | 448.6 | 411.4 | 523.2 | 436.8
1829 | 1593 | 565.5 | 226.2 | 264.4148 | 425.6 | 584.7 | 380.2 | 394.4 | 523 | 76.5 | 16.8 | 132.7 | 6.2 | 265.9 | 4 | 822.2 | 781.8 | 531 | 802.8 | 718.1 | 864.7 | 694.3 | 636.5 | 689 | 580.2 | 682.2 | 744.9 | 319 | 354.7 | 395 | 631.1 | 552.8 | 541.3 | 628.9 | 561.2 | 431.3 | 466.5 | 434.5 | 448.7 | 411.5 | 523.2 | 436.9
1830 | 1594 | 566.9 | 226.76 | 265.0694 | 424.5 | 586.5 | 379.5 | 394.6 | 519.3 | 76.5 | 16.8 | 132.8 | 6.3 | 244.1 | 3.7 | 829.7 | 784.3 | 531.2 | 802.6 | 718.1 | 865.3 | 691.8 | 634.5 | 685.3 | 579.3 | 681 | 743.5 | 319.1 | 354.8 | 395 | 630.7 | 552.4 | 540.4 | 628.8 | 560 | 431.4 | 465.5 | 434.5 | 448.8 | 411.4 | 523.2 | 436.9
1831 | 1595 | 566.9 | 226.76 | 265.0694 | 423.6 | 588.3 | 379 | 395 | 520.2 | 76.4 | 16.8 | 132.7 | 6.6 | 213.7 | 3.6 | 832 | 789 | 531.7 | 803 | 718.1 | 865.6 | 693.5 | 633.5 | 689.7 | 579 | 681.9 | 744.1 | 319.3 | 354.8 | 395.2 | 631.1 | 552.3 | 544 | 628.8 | 559.3 | 431.5 | 464.7 | 434.4 | 448.8 | 411.2 | 523.2 | 437
1832 | 1596 | 567 | 226.8 | 265.1161 | 424.9 | 592.2 | 379 | 394.4 | 523.9 | 76.4 | 16.8 | 132.7 | 6.2 | 199 | 3.6 | 833.6 | 795.9 | 531.7 | 803.6 | 717.8 | 864.7 | 695 | 633.7 | 696.1 | 578.6 | 683.3 | 745 | 319.4 | 354.9 | 395.2 | 631.1 | 552.6 | 544.9 | 629.2 | 558.9 | 431.5 | 463.6 | 433.5 | 448.8 | 411.1 | 523.1 | 437
1833 | 1597 | 567.3 | 226.92 | 265.2564 | 425 | 589.5 | 378.8 | 393 | 523.8 | 76.4 | 16.8 | 132.7 | 6.3 | 207.9 | 3.6 | 841.4 | 795.9 | 531.7 | 804.6 | 718.3 | 863.1 | 697.6 | 635.4 | 703.7 | 579.2 | 684.3 | 747.6 | 319.5 | 355 | 395.1 | 630.9 | 552.8 | 545.1 | 629.7 | 559 | 431.6 | 462.8 | 433.9 | 448.9 | 411.1 | 523.1 | 437.1
1834 | 1598 | 567.9 | 227.16 | 265.537 | 424.2 | 589.3 | 378.3 | 391.5 | 524.1 | 76.4 | 16.8 | 132.6 | 6.4 | 210.7 | 3.3 | 853.7 | 800.2 | 530.9 | 806 | 718.9 | 863.1 | 702.3 | 640.2 | 713 | 580.4 | 684.9 | 749.9 | 319.7 | 355.1 | 395.2 | 631.1 | 553.3 | 548.8 | 629.4 | 560.2 | 431.6 | 462 | 433.7 | 448.9 | 411.2 | 523.1 | 437.1
1835 | 1599 | 564.8 | 225.92 | 264.0875 | 423.3 | 590.8 | 378.3 | 391.2 | 524 | 76.4 | 16.8 | 132.5 | 6.4 | 217 | 3.6 | 861.9 | 803.6 | 530.8 | 807.2 | 719.4 | 863.9 | 705.5 | 645.2 | 719.3 | 581.9 | 685.2 | 750.5 | 319.8 | 355.2 | 395.2 | 631.2 | 553.2 | 549 | 629 | 561.3 | 431.6 | 461.3 | 434.3 | 448.9 | 411.3 | 523.1 | 437.1
1836 | 1600 | 563.5 | 225.4 | 263.4796 | 421.8 | 593.1 | 379.2 | 390.9 | 525.6 | 76.4 | 16.8 | 132.5 | 5.8 | 215.6 | 4.3 | 861.4 | 804.2 | 529.6 | 808.5 | 719.8 | 865.8 | 706.1 | 647.2 | 719.4 | 583.2 | 685.6 | 751.3 | 320 | 355.3 | 395.3 | 631.4 | 553.3 | 549.6 | 629 | 561.2 | 431.7 | 460.9 | 434.8 | 448.9 | 411.3 | 523 | 437.2
1837 | 1601 | 562.7 | 225.08 | 263.1056 | 421.4 | 593.6 | 379.9 | 390.1 | 525.3 | 76.5 | 16.8 | 132.4 | 6 | 218.1 | 4.8 | 846.1 | 794.1 | 529.1 | 808.4 | 719.6 | 866.6 | 704.7 | 645.7 | 713.5 | 582.7 | 686.2 | 750.5 | 320.1 | 355.4 | 395.3 | 631.4 | 552.8 | 550.1 | 629.2 | 560 | 431.7 | 461.1 | 434.1 | 448.9 | 411.2 | 523 | 437.2
1838 | 1602 | 564.9 | 225.96 | 264.1342 | 422.3 | 592.8 | 380.4 | 389.4 | 524.4 | 76.5 | 16.8 | 132.4 | 6.1 | 223 | 4.6 | 846.4 | 789.7 | 529.7 | 807.4 | 719.2 | 866.5 | 702 | 643.8 | 707 | 582.1 | 685.7 | 750.3 | 320.2 | 355.4 | 395.3 | 631.1 | 552.4 | 548 | 629.5 | 559.1 | 431.7 | 461 | 434.1 | 448.9 | 411.3 | 523 | 437.2
1839 | 1603 | 565.8 | 226.32 | 264.555 | 424 | 594.5 | 380.4 | 388.3 | 522.7 | 76.5 | 16.8 | 132.6 | 6.6 | 251.6 | 4 | 849 | 788.9 | 529.8 | 807.1 | 719.1 | 866 | 702.2 | 643.9 | 710.8 | 581.4 | 684 | 750.9 | 320.4 | 355.4 | 395.3 | 631.1 | 551.9 | 547.6 | 629.7 | 558.6 | 431.7 | 460.8 | 433.8 | 449 | 411.3 | 523 | 437.3
1840 | 1604 | 564.6 | 225.84 | 263.9939 | 424.2 | 595.2 | 380.5 | 388.2 | 523.8 | 76.6 | 16.8 | 132.7 | 6.7 | 265.3 | 3.5 | 849.3 | 785.2 | 529.8 | 807.1 | 718.8 | 866.2 | 701.1 | 645.1 | 711.4 | 581.5 | 682.6 | 751.4 | 320.5 | 355.5 | 395.3 | 631.4 | 552.2 | 549.4 | 629.6 | 559.2 | 431.8 | 460.1 | 433.9 | 449.1 | 411.3 | 522.9 | 437.3
1841 | 1605 | 564.9 | 225.96 | 264.1342 | 423.4 | 587 | 381 | 388.3 | 523.5 | 76.6 | 16.8 | 132.7 | 6.8 | 257.6 | 3.5 | 850.7 | 794.6 | 529.3 | 807.3 | 719.2 | 866.4 | 698.5 | 643.5 | 706.4 | 580.6 | 682 | 749.9 | 320.6 | 355.6 | 395.4 | 631.5 | 552.2 | 550 | 629.2 | 560.4 | 431.8 | 459.4 | 433.5 | 449.2 | 411.4 | 522.9 | 437.4
1842 | 1606 | 565.9 | 226.36 | 264.6018 | 422.5 | 582.6 | 381.4 | 388.1 | 522.4 | 76.6 | 16.8 | 132.7 | 6.5 | 235.2 | 3.9 | 850.8 | 805.5 | 529.1 | 807.5 | 719.7 | 866.2 | 697 | 644 | 706.9 | 580.4 | 682.4 | 749.7 | 320.8 | 355.7 | 395.4 | 631.3 | 551.9 | 548.3 | 628.9 | 559.8 | 431.9 | 458.4 | 433.9 | 449.3 | 411.5 | 522.8 | 437.4
1843 | 1607 | 566.5 | 226.6 | 264.8823 | 421.7 | 585.6 | 381.5 | 388.1 | 520.7 | 76.6 | 16.8 | 132.6 | 6.5 | 216 | 4.6 | 860 | 817.5 | 529.4 | 807.9 | 720 | 865.6 | 698.5 | 646.4 | 710.5 | 581.8 | 683.6 | 749.2 | 320.9 | 355.7 | 395.4 | 631.1 | 550.9 | 548.9 | 628.5 | 559.6 | 431.9 | 457.8 | 434.1 | 449.4 | 411.5 | 522.8 | 437.4
1844 | 1608 | 565.6 | 226.24 | 264.4615 | 420.7 | 598.2 | 381.6 | 388.2 | 521.9 | 76.6 | 16.8 | 132.6 | 6.6 | 199.8 | 5.1 | 867.8 | 824.7 | 529.7 | 808.4 | 720.3 | 865.7 | 700.9 | 648.2 | 715.2 | 583.2 | 682.6 | 748.4 | 321.1 | 355.8 | 395.5 | 631.3 | 551.1 | 555.7 | 628.7 | 560.7 | 432 | 457.8 | 433.4 | 449.5 | 411.5 | 522.8 | 437.5
1845 | 1609 | 564.7 | 225.88 | 264.0407 | 421.2 | 601.8 | 382.1 | 388.5 | 525.1 | 76.5 | 16.8 | 132.6 | 6.5 | 220.5 | 5.1 | 866.3 | 833.1 | 528.3 | 809.5 | 720.6 | 866 | 703.4 | 650.8 | 719.2 | 585.2 | 680.8 | 748.7 | 321.2 | 355.9 | 395.7 | 631.7 | 551.4 | 561.7 | 628.5 | 561.8 | 432.1 | 458.8 | 433.3 | 449.6 | 411.4 | 522.8 | 437.5
1846 | 1610 | 567 | 226.8 | 265.1161 | 421.8 | 604.9 | 382.6 | 388.1 | 527.7 | 76.4 | 16.8 | 132.6 | 6.2 | 241.6 | 4.7 | 868.5 | 838.6 | 527.8 | 812.3 | 721.1 | 865.6 | 705.5 | 654.6 | 722.7 | 587.1 | 681.2 | 748.7 | 321.4 | 356 | 395.6 | 631.6 | 552.5 | 561.7 | 628.8 | 563 | 432.1 | 458.8 | 433.2 | 449.6 | 411.5 | 522.8 | 437.5
1847 | 1611 | 567.1 | 226.84 | 265.1629 | 422 | 608 | 383 | 387.6 | 526.5 | 76.3 | 16.8 | 132.7 | 5.6 | 236.3 | 4.4 | 868.8 | 838.6 | 528.4 | 813.5 | 721.2 | 865.7 | 706 | 656.3 | 727.2 | 587.5 | 681.3 | 747.8 | 321.5 | 356.1 | 395.6 | 631.1 | 552.9 | 560.2 | 629.1 | 562.3 | 432.2 | 458.9 | 433.2 | 449.8 | 411.5 | 522.8 | 437.5
1848 | 1612 | 565.7 | 226.28 | 264.5083 | 421.4 | 619 | 383 | 387.8 | 526.3 | 76.3 | 16.8 | 132.9 | 5.5 | 234.3 | 4.6 | 874.8 | 841.4 | 529.2 | 814.4 | 721.3 | 866.6 | 707.4 | 657.9 | 731.6 | 587.9 | 680.1 | 749.6 | 321.6 | 356.1 | 395.7 | 631.3 | 552.9 | 562.1 | 629.3 | 561.9 | 432.3 | 459.1 | 432.9 | 449.9 | 411.5 | 522.8 | 437.6
1849 | 1613 | 566.7 | 226.68 | 264.9759 | 422.3 | 620.9 | 383.1 | 388.3 | 528.2 | 76.3 | 16.8 | 133 | 6.2 | 230.5 | 4.2 | 875.1 | 847.4 | 531.4 | 817.5 | 721.8 | 867.6 | 707.2 | 659.3 | 728.8 | 588.4 | 681.1 | 748.7 | 321.8 | 356.2 | 395.7 | 631.2 | 553.3 | 561 | 629.1 | 561.4 | 432.4 | 458.7 | 433.2 | 450 | 411.6 | 522.9 | 437.6
1850 | 1614 | 564.6 | 225.84 | 263.9939 | 423.4 | 631.5 | 383.4 | 388.5 | 528.6 | 76.3 | 16.8 | 133.1 | 5.8 | 222 | 4.5 | 877.9 | 848.2 | 533.8 | 818.1 | 722.3 | 867.5 | 703.1 | 658.7 | 723.9 | 588.8 | 680.1 | 746.9 | 321.9 | 356.3 | 395.7 | 631 | 553.1 | 560.2 | 629.3 | 561.6 | 432.4 | 458.4 | 433.5 | 450.1 | 411.7 | 522.8 | 437.7
1851 | 1615 | 564.7 | 225.88 | 264.0407 | 422.9 | 630.3 | 383.8 | 388.5 | 527.6 | 76.2 | 16.8 | 133.3 | 6.3 | 239.8 | 5.3 | 880.1 | 845.3 | 535.4 | 818.4 | 722.6 | 868.3 | 703.8 | 658.8 | 727.5 | 588.5 | 680.2 | 745.9 | 322 | 356.4 | 395.8 | 631.1 | 552.6 | 561.5 | 629 | 560.6 | 432.5 | 458.8 | 432.9 | 450.1 | 411.5 | 522.9 | 437.7
1852 | 1616 | 569.1 | 227.64 | 266.098 | 422.6 | 616.3 | 384.3 | 388.9 | 530.4 | 76.2 | 16.8 | 133.4 | 6.2 | 234.6 | 6.2 | 874.8 | 850.3 | 535.7 | 820 | 722.9 | 868.8 | 705 | 660.1 | 731.2 | 589.6 | 679.2 | 745.8 | 322.2 | 356.4 | 396.1 | 631.8 | 552.9 | 566.4 | 629.1 | 560.9 | 432.5 | 460.4 | 432 | 450.1 | 411.4 | 522.8 | 437.8
1853 | 1617 | 569 | 227.6 | 266.0513 | 423.4 | 605.6 | 384.7 | 389.2 | 532.7 | 76.2 | 16.8 | 133.5 | 6.6 | 222.6 | 6.6 | 879 | 846.8 | 534.3 | 822.1 | 723 | 869 | 706.1 | 661.5 | 733.6 | 590.7 | 678.3 | 746 | 322.3 | 356.5 | 396.1 | 632.1 | 553 | 569.6 | 628.9 | 561.5 | 432.5 | 461.1 | 431.4 | 450.1 | 411.3 | 522.8 | 437.8
1854 | 1618 | 567.1 | 226.84 | 265.1629 | 423.4 | 601.2 | 384.7 | 389 | 532 | 76.1 | 16.8 | 133.7 | 6.6 | 236.6 | 6.7 | 876.5 | 842.4 | 533.3 | 825 | 723 | 869 | 707.2 | 664.8 | 738 | 591.4 | 677.5 | 747.2 | 322.5 | 356.6 | 396 | 632 | 553.2 | 566.9 | 628.5 | 562.6 | 432.5 | 460.6 | 432 | 450 | 411.4 | 522.8 | 437.9
1855 | 1619 | 567.5 | 227 | 265.3499 | 422.8 | 599.9 | 384.9 | 388.5 | 531.4 | 76.2 | 16.8 | 133.8 | 6.6 | 233.6 | 6.6 | 871.7 | 835.6 | 537.3 | 825.9 | 723.1 | 869.5 | 705.1 | 665.9 | 733.1 | 591.7 | 676.8 | 746.3 | 322.6 | 356.6 | 396 | 631.8 | 554.5 | 563.8 | 628.4 | 562.9 | 432.6 | 459.7 | 432.6 | 450 | 411.5 | 522.9 | 437.9
1856 | 1620 | 567.6 | 227.04 | 265.3967 | 422.4 | 611.6 | 384.6 | 388.4 | 529.1 | 76.1 | 16.8 | 133.8 | 6.5 | 227.9 | 6.8 | 865.8 | 835.5 | 541.3 | 825.8 | 723 | 869.7 | 703.9 | 665.3 | 730.9 | 590.9 | 677.2 | 746.2 | 322.7 | 356.7 | 396 | 631.7 | 554 | 561.2 | 628.3 | 561.9 | 432.6 | 459.3 | 433 | 450.1 | 411.7 | 522.9 | 438
1857 | 1621 | 568.1 | 227.24 | 265.6305 | 421.4 | 610.5 | 384.3 | 388.6 | 527.8 | 76.1 | 16.8 | 133.7 | 6 | 240.8 | 6.7 | 867.5 | 841 | 542.7 | 826.5 | 723.6 | 869.3 | 706.8 | 666.7 | 733.4 | 591.5 | 678.6 | 747.4 | 322.9 | 356.8 | 396.1 | 631.9 | 553.8 | 563.1 | 628.2 | 562.1 | 432.6 | 459.8 | 432.8 | 450.2 | 411.7 | 522.9 | 438
1858 | 1622 | 566 | 226.4 | 264.6486 | 420.3 | 606.1 | 384.5 | 388.6 | 532.3 | 76.2 | 16.8 | 133.6 | 6.4 | 227.6 | 6.4 | 873.7 | 838.6 | 543.7 | 828 | 724 | 869.5 | 708.6 | 667.9 | 735.9 | 592.6 | 678.9 | 747 | 323 | 356.9 | 396.4 | 632.8 | 554.9 | 571.1 | 628.1 | 562.9 | 432.7 | 460 | 432.9 | 450.3 | 411.7 | 522.9 | 438
1859 | 1623 | 566.2 | 226.48 | 264.7421 | 420.3 | 606.5 | 385.1 | 388.4 | 535.1 | 76.3 | 16.8 | 133.5 | 6.3 | 230.1 | 5.7 | 871.2 | 833.1 | 544.4 | 829.5 | 724 | 869.4 | 709.3 | 665.5 | 734.9 | 592.6 | 679.1 | 748.6 | 323.2 | 356.9 | 396.4 | 632.9 | 555.5 | 569.6 | 628.3 | 562.4 | 432.8 | 459.6 | 432.1 | 450.4 | 411.6 | 522.9 | 438.1
1860 | 1624 | 567.7 | 227.08 | 265.4434 | 421.1 | 609.2 | 385.7 | 388.3 | 535.4 | 76.3 | 16.8 | 133.5 | 6.4 | 241.3 | 5.6 | 870.8 | 832 | 544.1 | 831 | 724.3 | 869.3 | 709.9 | 665.5 | 735.2 | 592 | 678.2 | 749.4 | 323.3 | 357 | 396.4 | 632.8 | 555.5 | 567.1 | 628.2 | 561.3 | 432.9 | 459.5 | 431.8 | 450.6 | 411.7 | 522.9 | 438.1
1861 | 1625 | 566.1 | 226.44 | 264.6953 | 423.2 | 616.4 | 385.9 | 388.4 | 535.1 | 76.3 | 16.8 | 133.4 | 6.2 | 244.1 | 5.3 | 869.2 | 836.8 | 543.6 | 832.5 | 724.5 | 869.1 | 710.2 | 663.8 | 733.6 | 591.4 | 678.1 | 749.4 | 323.4 | 357.1 | 396.4 | 632.7 | 555.4 | 566.8 | 628.2 | 560.4 | 433 | 459.7 | 432.4 | 450.8 | 411.7 | 522.9 | 438.1
1862 | 1626 | 567.2 | 226.88 | 265.2096 | 423.8 | 612.3 | 385.9 | 388.9 | 533.2 | 76.3 | 16.8 | 133.3 | 6 | 240.8 | 5.4 | 867.5 | 840.1 | 542.3 | 833 | 724.8 | 869.3 | 712.2 | 665.5 | 736.2 | 591.6 | 678.9 | 750 | 323.6 | 357.1 | 396.5 | 632.8 | 554.9 | 568.3 | 628.4 | 560.5 | 433.1 | 459.6 | 432.5 | 451 | 411.8 | 522.9 | 438.1
1863 | 1627 | 568.2 | 227.28 | 265.6772 | 424.6 | 605.8 | 386.2 | 388.9 | 534.1 | 76.3 | 16.8 | 133 | 5.6 | 228.4 | 5.3 | 869.2 | 843 | 541.1 | 832.8 | 725.3 | 869.8 | 716.5 | 668.2 | 740.5 | 593.2 | 679.5 | 752.1 | 323.7 | 357.2 | 396.7 | 633.3 | 555.3 | 573.9 | 628.1 | 562.4 | 433.2 | 458.8 | 433 | 451.1 | 411.7 | 522.9 | 438.2
1864 | 1628 | 566.8 | 226.72 | 265.0226 | 424.4 | 605.8 | 386.3 | 388.5 | 535.7 | 76.4 | 16.8 | 132.9 | 6.5 | 223.5 | 4.7 | 869.1 | 840.6 | 540.2 | 834.2 | 725.5 | 870.3 | 717.3 | 669.9 | 741.2 | 594.3 | 679 | 753.2 | 323.9 | 357.3 | 396.6 | 633.4 | 555.6 | 574.4 | 627.9 | 563.9 | 433.3 | 457.6 | 432.7 | 451.1 | 411.7 | 522.9 | 438.2
1865 | 1629 | 565.8 | 226.32 | 264.555 | 424.6 | 605.4 | 385.5 | 388.1 | 535 | 76.4 | 16.8 | 132.8 | 6.6 | 256.6 | 4.7 | 870.9 | 837.3 | 539.4 | 836.8 | 725.8 | 870.8 | 716.1 | 670.9 | 740.4 | 594.2 | 679.9 | 753.7 | 324 | 357.3 | 396.6 | 633.2 | 555.6 | 571.8 | 627.8 | 563.7 | 433.4 | 456.7 | 432.3 | 451.3 | 411.8 | 522.9 | 438.2
1866 | 1630 | 565.6 | 226.24 | 264.4615 | 425.4 | 606.9 | 385.1 | 387.9 | 535.3 | 76.4 | 16.8 | 132.9 | 6.5 | 245.6 | 5.3 | 877.3 | 839.1 | 537.8 | 837.3 | 726.2 | 871 | 715.7 | 671.9 | 740.3 | 593.9 | 679.2 | 753.7 | 324.1 | 357.4 | 396.7 | 633.1 | 555.9 | 570.3 | 628 | 563.1 | 433.6 | 455.9 | 432 | 451.5 | 411.8 | 522.9 | 438.2
1867 | 1631 | 565.6 | 226.24 | 264.4615 | 425.1 | 606.7 | 385.1 | 388.5 | 535.7 | 76.4 | 16.8 | 132.9 | 6.1 | 244 | 6.1 | 873.4 | 836.8 | 537.3 | 837.1 | 726.4 | 871.1 | 716 | 672 | 740.4 | 593.5 | 677.6 | 754.9 | 324.3 | 357.5 | 396.7 | 632.9 | 555.7 | 569 | 628.2 | 561.9 | 433.7 | 455.3 | 431.6 | 451.7 | 411.7 | 522.9 | 438.3
1868 | 1632 | 565 | 226 | 264.181 | 424 | 601.9 | 385 | 388.6 | 534.9 | 76.4 | 16.8 | 132.9 | 6.2 | 224.4 | 5.9 | 870.8 | 839.7 | 537.9 | 839.6 | 726.7 | 871 | 715.7 | 672.2 | 739 | 593.6 | 677.1 | 754.8 | 324.4 | 357.6 | 396.7 | 632.8 | 555.2 | 569 | 628.3 | 561.4 | 433.9 | 455 | 431.5 | 451.8 | 411.8 | 522.9 | 438.3
1869 | 1633 | 566.4 | 226.56 | 264.8356 | 423.4 | 597.7 | 384.6 | 388.5 | 532.9 | 76.3 | 16.8 | 132.9 | 6.6 | 203.5 | 5.5 | 873.5 | 844.9 | 537.4 | 839.3 | 726.7 | 870.8 | 712.9 | 670.7 | 735.5 | 593.1 | 677.7 | 753.5 | 324.5 | 357.6 | 396.7 | 632.3 | 555 | 565.7 | 628.7 | 561.5 | 434 | 454.9 | 432.4 | 452 | 411.9 | 522.8 | 438.3
1870 | 1634 | 567.6 | 227.04 | 265.3967 | 422.4 | 594.7 | 383.9 | 389.1 | 529.6 | 76.2 | 16.8 | 132.9 | 6.3 | 219.6 | 5.5 | 872.3 | 850 | 537.2 | 838 | 727.1 | 870.3 | 714.2 | 671.8 | 739.9 | 593.8 | 677.1 | 753.7 | 324.7 | 357.7 | 396.8 | 632.3 | 554.3 | 565.7 | 628.6 | 561.5 | 434.1 | 455.2 | 432 | 452.1 | 411.9 | 522.8 | 438.4
1871 | 1635 | 565.8 | 226.32 | 264.555 | 421.7 | 598.8 | 383.8 | 389.8 | 530.9 | 76.2 | 16.8 | 132.9 | 6.6 | 234.9 | 5.4 | 871 | 853.1 | 536.3 | 838.4 | 727.5 | 870 | 714.3 | 672.6 | 739.3 | 595.3 | 678.2 | 753 | 324.8 | 357.8 | 396.9 | 632.4 | 555 | 568.5 | 628.4 | 563.3 | 434.3 | 455.5 | 431.4 | 452.1 | 412 | 522.8 | 438.4
1872 | 1636 | 565.7 | 226.28 | 264.5083 | 422 | 596.8 | 383.1 | 389.6 | 531 | 76.2 | 16.8 | 133 | 6.2 | 244.1 | 5.4 | 873.8 | 842.7 | 536.2 | 837.8 | 727.6 | 870.2 | 711.7 | 671.4 | 731.6 | 595.3 | 678.2 | 752.2 | 324.9 | 357.8 | 396.8 | 632.1 | 555.8 | 566.1 | 628.3 | 563.7 | 434.4 | 456.1 | 432.9 | 452.2 | 412.2 | 522.8 | 438.5
1873 | 1637 | 565.1 | 226.04 | 264.2277 | 421.5 | 591.6 | 382.5 | 389.9 | 529.9 | 76.2 | 16.8 | 133.1 | 6.2 | 237.4 | 5.9 | 864.9 | 827.2 | 535.2 | 836.3 | 727.2 | 870.4 | 707.6 | 670.6 | 720.8 | 594.8 | 678 | 750.3 | 325.1 | 357.9 | 396.9 | 632 | 556.1 | 563.4 | 628.3 | 563.2 | 434.4 | 457.7 | 433.1 | 452.2 | 412.3 | 522.9 | 438.5
1874 | 1638 | 565.6 | 226.24 | 264.4615 | 420.8 | 583.4 | 382.2 | 390.8 | 526.5 | 76.3 | 16.8 | 133.2 | 6.4 | 243 | 5.8 | 857.3 | 819.5 | 534.7 | 834.1 | 727.2 | 870.8 | 705.5 | 669 | 717 | 593.6 | 677.6 | 750.4 | 325.2 | 358 | 396.9 | 631.6 | 555.3 | 558.8 | 628.2 | 561.7 | 434.5 | 460.3 | 433.2 | 452.2 | 412.4 | 522.9 | 438.7
1875 | 1639 | 565.9 | 226.36 | 264.6018 | 419.4 | 580.3 | 381.5 | 391.9 | 522.8 | 76.3 | 16.8 | 133.3 | 6.7 | 276.2 | 5.4 | 857.9 | 814.4 | 533.9 | 832.4 | 727.2 | 871.1 | 706.6 | 666.6 | 715.6 | 592.3 | 677.9 | 751.6 | 325.3 | 358 | 396.9 | 631.5 | 553.3 | 556.2 | 628.1 | 559.8 | 434.5 | 461.7 | 433.4 | 452.3 | 412.3 | 522.9 | 438.8
1876 | 1640 | 565.8 | 226.32 | 264.555 | 418.9 | 574 | 380.4 | 392.4 | 522.1 | 76.3 | 16.8 | 133.3 | 6.3 | 271.8 | 4.7 | 863.1 | 808.3 | 532.8 | 830.9 | 727.2 | 871 | 708 | 667.8 | 724.4 | 591.7 | 678.3 | 753.3 | 325.5 | 358.1 | 396.9 | 631.4 | 552.7 | 556.2 | 628.3 | 559.7 | 434.6 | 462.3 | 433 | 452.3 | 412.3 | 522.8 | 438.9
1877 | 1641 | 566 | 226.4 | 264.6486 | 420.6 | 564.9 | 379.6 | 392.2 | 524.5 | 76.3 | 16.8 | 133.4 | 6.4 | 233.4 | 5 | 851.4 | 805.5 | 532.8 | 830.2 | 727.1 | 870.3 | 706.7 | 667.4 | 720.4 | 591.9 | 677.8 | 752.6 | 325.6 | 358.1 | 397 | 631.3 | 553.5 | 555.6 | 628.4 | 561.2 | 434.6 | 461.9 | 433.7 | 452.4 | 412.5 | 522.8 | 439
1878 | 1642 | 566.5 | 226.6 | 264.8823 | 422.1 | 564.2 | 379 | 392.1 | 524.2 | 76.3 | 16.8 | 133.5 | 6.4 | 225.4 | 5.1 | 842.9 | 802.1 | 533.7 | 827.2 | 727.1 | 868.6 | 701.8 | 664.5 | 707.2 | 591.1 | 677 | 749.1 | 325.7 | 358.2 | 397 | 631.1 | 554.1 | 553.6 | 627.9 | 562.3 | 434.8 | 462.9 | 434.6 | 452.6 | 412.6 | 522.8 | 439
1879 | 1643 | 568 | 227.2 | 265.5837 | 421.9 | 569.8 | 379.2 | 392.6 | 522 | 76.3 | 16.8 | 133.6 | 6.6 | 235.3 | 5 | 847.7 | 802.2 | 534.2 | 824.9 | 726.9 | 868.6 | 698.4 | 661 | 706.4 | 589.7 | 676.2 | 748.5 | 325.8 | 358.2 | 397 | 630.6 | 553.7 | 548.6 | 627.6 | 560.5 | 434.9 | 464.5 | 433.9 | 452.8 | 412.6 | 522.8 | 439.2
1880 | 1644 | 565.8 | 226.32 | 264.555 | 420.3 | 577 | 379.4 | 393.4 | 518 | 76.4 | 16.8 | 133.6 | 6.7 | 252.5 | 5.1 | 849.5 | 804.8 | 533.3 | 824.7 | 726.7 | 869 | 702.4 | 659.6 | 711.3 | 589.2 | 675.6 | 749.5 | 326 | 358.3 | 397.1 | 630.5 | 552.1 | 550.8 | 627.2 | 558.6 | 434.9 | 464.6 | 433 | 452.9 | 412.5 | 522.8 | 439.2
1881 | 1645 | 565.7 | 226.28 | 264.5083 | 418.9 | 593.7 | 379.1 | 393.7 | 518.8 | 76.5 | 16.8 | 133.7 | 6.3 | 253.3 | 4.8 | 849.8 | 803.7 | 533 | 825.3 | 726.9 | 868.7 | 705.9 | 657.1 | 716.2 | 588 | 675.3 | 750.3 | 326.1 | 358.3 | 397.2 | 630.7 | 551.4 | 554.4 | 627.4 | 558.4 | 435.1 | 463.1 | 433.3 | 453.1 | 412.4 | 522.8 | 439.3
1882 | 1646 | 567.1 | 226.84 | 265.1629 | 419.4 | 594.1 | 379 | 393.3 | 520.8 | 76.6 | 16.8 | 133.6 | 6 | 250.3 | 4.5 | 844.4 | 791.5 | 533.2 | 825.6 | 726.8 | 868.4 | 709.6 | 655.6 | 713.6 | 586.4 | 676.4 | 750.7 | 326.2 | 358.4 | 397.2 | 630.7 | 551.3 | 554.5 | 627.3 | 557.6 | 435.2 | 463.3 | 432.5 | 453.2 | 412.4 | 522.7 | 439.3
1883 | 1647 | 566.4 | 226.56 | 264.8356 | 420.1 | 588.9 | 379.7 | 392.8 | 520.9 | 76.6 | 16.8 | 133.6 | 6 | 247.2 | 4.5 | 830.9 | 777.3 | 534.5 | 825.7 | 726.7 | 868.2 | 705.4 | 651.7 | 704.6 | 585.6 | 675.6 | 750.4 | 326.3 | 358.5 | 397.2 | 630.5 | 550.8 | 552.8 | 627.1 | 556.5 | 435.4 | 463.1 | 432.4 | 453.3 | 412.4 | 522.7 | 439.3
1884 | 1648 | 566.1 | 226.44 | 264.6953 | 421.7 | 585 | 380.3 | 392.1 | 521.7 | 76.7 | 16.8 | 133.6 | 6.2 | 226 | 4.1 | 813.8 | 766.3 | 533.7 | 824.8 | 726.4 | 867.1 | 702.3 | 647.4 | 695.5 | 583.9 | 675.4 | 749.6 | 326.5 | 358.6 | 397.2 | 630.2 | 550.7 | 550.1 | 627.2 | 555.5 | 435.5 | 463 | 432.3 | 453.4 | 412.4 | 522.7 | 439.3
1885 | 1649 | 565.5 | 226.2 | 264.4148 | 423.3 | 584.9 | 380.5 | 391.3 | 521.1 | 76.7 | 16.8 | 133.6 | 6.1 | 216.3 | 3.7 | 791.7 | 757.6 | 533.5 | 822.1 | 726.3 | 865.2 | 696.5 | 640.9 | 683.9 | 580.9 | 674.8 | 747.1 | 326.6 | 358.7 | 397.2 | 629.7 | 549.8 | 546 | 627.3 | 554.1 | 435.5 | 463 | 433.2 | 453.4 | 412.5 | 522.6 | 439.3
1886 | 1650 | 565.3 | 226.12 | 264.3213 | 424.4 | 582.9 | 380.1 | 391.7 | 519 | 76.8 | 16.8 | 133.4 | 6.1 | 233.2 | 3.5 | 796.4 | 759.6 | 534.1 | 819.6 | 726 | 863.8 | 691.3 | 634.9 | 676.4 | 577.8 | 674.8 | 745.9 | 326.7 | 358.7 | 397.2 | 629.2 | 548.6 | 542.4 | 627.2 | 552.9 | 435.6 | 462.5 | 433.7 | 453.5 | 412.5 | 522.6 | 439.3
1887 | 1651 | 566.2 | 226.48 | 264.7421 | 425.6 | 586.5 | 379.6 | 391.7 | 519 | 76.9 | 16.8 | 133.3 | 6.3 | 235.6 | 3.5 | 814.1 | 782.9 | 533.6 | 818.9 | 725.8 | 863.4 | 692.6 | 634.2 | 684 | 577.2 | 675.5 | 747.9 | 326.8 | 358.8 | 397.2 | 629.2 | 548.2 | 541.5 | 627.4 | 553.1 | 435.7 | 461.8 | 433.8 | 453.5 | 412.5 | 522.5 | 439.3
1888 | 1652 | 565 | 226 | 264.181 | 425.8 | 587.3 | 379.9 | 391.4 | 520.1 | 76.9 | 16.8 | 133.2 | 6.4 | 229.1 | 3.8 | 831.6 | 793.6 | 533.9 | 819.9 | 725.9 | 863.6 | 696.7 | 636.9 | 693.5 | 578.6 | 676.1 | 748.9 | 327 | 358.9 | 397.3 | 629.2 | 548.4 | 546.9 | 627.6 | 554.5 | 435.7 | 461.2 | 433.3 | 453.5 | 412.4 | 522.4 | 439.4
1889 | 1653 | 564.5 | 225.8 | 263.9472 | 424.1 | 589.8 | 380 | 391.3 | 520.3 | 76.9 | 16.8 | 133.1 | 6.7 | 233 | 3.6 | 840 | 790.5 | 533.6 | 820.7 | 725.6 | 864 | 698.3 | 637.6 | 695.1 | 579.5 | 677.7 | 749.8 | 327.1 | 359 | 397.3 | 629.4 | 547.9 | 546.9 | 627.7 | 555.4 | 435.8 | 460.8 | 433.3 | 453.5 | 412.3 | 522.4 | 439.4
1890 | 1654 | 563.4 | 225.36 | 263.4329 | 423.7 | 590 | 379.6 | 391.3 | 522.1 | 77 | 16.8 | 133.1 | 6.6 | 240.6 | 4.1 | 840.2 | 793 | 533.6 | 821.3 | 725.9 | 864.1 | 699.5 | 639.8 | 697.4 | 579.8 | 677.8 | 750.6 | 327.2 | 359.1 | 397.4 | 629.4 | 548.9 | 546.4 | 628 | 556.1 | 435.9 | 460.1 | 432.8 | 453.5 | 412.4 | 522.3 | 439.4
1891 | 1655 | 563.2 | 225.28 | 263.3393 | 424.6 | 588.4 | 380 | 390.9 | 524.1 | 77 | 16.8 | 133 | 6.3 | 247.6 | 4.3 | 835 | 790.6 | 533.6 | 821.8 | 726.3 | 863.1 | 699.5 | 640.6 | 698.8 | 579.6 | 677.6 | 751 | 327.3 | 359.2 | 397.4 | 629.4 | 549.8 | 546.2 | 628.1 | 557.3 | 436 | 459.8 | 433 | 453.6 | 412.4 | 522.3 | 439.4
1892 | 1656 | 565.1 | 226.04 | 264.2277 | 424.7 | 590.2 | 380.1 | 391.4 | 524.8 | 77 | 16.8 | 133 | 6.2 | 236.5 | 4.3 | 835.6 | 789.7 | 533.5 | 820.9 | 726.7 | 862.1 | 696.7 | 643.1 | 696.6 | 580.7 | 677.5 | 749.5 | 327.4 | 359.2 | 397.4 | 629.3 | 550.8 | 543.8 | 628.3 | 558 | 436 | 459.8 | 433.3 | 453.6 | 412.5 | 522.3 | 439.5
1893 | 1657 | 564.9 | 225.96 | 264.1342 | 423.7 | 598.2 | 379.6 | 392.7 | 523.3 | 76.9 | 16.8 | 133 | 6.3 | 223.6 | 4.2 | 840.1 | 796 | 535.3 | 820 | 726.8 | 862.1 | 697 | 645.6 | 700.3 | 582 | 678.6 | 749.8 | 327.6 | 359.3 | 397.4 | 629 | 551.1 | 542.1 | 628.2 | 557.5 | 436.1 | 460.1 | 433.3 | 453.8 | 412.5 | 522.3 | 439.5
1894 | 1658 | 565.9 | 226.36 | 264.6018 | 422.7 | 589.4 | 378.9 | 393.7 | 523.4 | 76.9 | 16.8 | 133.1 | 6.1 | 228.9 | 4 | 848.5 | 805.4 | 535.8 | 820.2 | 727.3 | 862.4 | 697.9 | 648.4 | 706.7 | 583.1 | 677.9 | 750.2 | 327.7 | 359.3 | 397.4 | 628.8 | 551.1 | 542 | 628.1 | 557.8 | 436.2 | 460.1 | 433.3 | 453.9 | 412.5 | 522.3 | 439.6
1895 | 1659 | 566.4 | 226.56 | 264.8356 | 421.4 | 578.4 | 378.1 | 394.4 | 523 | 76.9 | 16.8 | 133.1 | 6.2 | 245.3 | 3.8 | 852.4 | 804.8 | 535.5 | 821.5 | 727.8 | 863 | 699.1 | 647.6 | 708.3 | 582.4 | 677.5 | 750.7 | 327.8 | 359.4 | 397.5 | 628.7 | 550.6 | 542.6 | 627.8 | 556.4 | 436.3 | 459.3 | 433.3 | 454.1 | 412.4 | 522.3 | 439.6
1896 | 1660 | 566.4 | 226.56 | 264.8356 | 420.7 | 581 | 378.5 | 394.7 | 524.4 | 76.8 | 16.8 | 133.2 | 6.3 | 251.7 | 3.8 | 838 | 786.9 | 535.4 | 822.4 | 727.7 | 864.3 | 698.7 | 645 | 705.2 | 581.7 | 677 | 749.7 | 328 | 359.4 | 397.8 | 629 | 550 | 545.8 | 627.3 | 555.6 | 436.5 | 458.9 | 433.9 | 454.2 | 412.4 | 522.3 | 439.7
1897 | 1661 | 567.3 | 226.92 | 265.2564 | 421.2 | 582.2 | 379.4 | 394.4 | 525.8 | 76.7 | 16.8 | 133.2 | 6.6 | 241.2 | 3.7 | 829.7 | 781 | 534.8 | 823.2 | 728 | 864.2 | 697 | 641.2 | 697.2 | 579.4 | 676.6 | 748.8 | 328.1 | 359.5 | 397.8 | 629 | 549.4 | 547.3 | 627.5 | 554.6 | 436.6 | 458.9 | 435.5 | 454.2 | 412.4 | 522.3 | 439.7
1898 | 1662 | 568.1 | 227.24 | 265.6305 | 420.1 | 580.4 | 380.3 | 393.6 | 525.4 | 76.8 | 16.8 | 133.2 | 6.3 | 231.6 | 3.7 | 824.7 | 775.7 | 534.1 | 823.6 | 727.5 | 864.1 | 694.9 | 637.7 | 691.8 | 577.2 | 676.7 | 749.1 | 328.2 | 359.6 | 397.7 | 628.9 | 548.9 | 546.2 | 627.3 | 553.5 | 436.6 | 458.7 | 436.4 | 454.2 | 412.3 | 522.2 | 439.7
1899 | 1663 | 567.1 | 226.84 | 265.1629 | 421.1 | 583.9 | 380.1 | 392.1 | 525.2 | 76.9 | 16.8 | 133.2 | 6.4 | 218.6 | 4.4 | 829.4 | 779 | 534.8 | 823.2 | 727.6 | 864.5 | 695.1 | 635.2 | 691.8 | 576 | 676.5 | 749.5 | 328.4 | 359.6 | 397.8 | 629 | 548.3 | 546 | 627.8 | 553.2 | 436.6 | 458.8 | 436.2 | 454.1 | 412.2 | 522.2 | 439.7
1900 | 1664 | 564.5 | 225.8 | 263.9472 | 422.5 | 585.7 | 379.3 | 391.2 | 525.3 | 76.9 | 16.8 | 133.1 | 6.2 | 206.4 | 5 | 815.5 | 768.7 | 534.4 | 820.8 | 727.3 | 863.7 | 690.7 | 631.8 | 686.3 | 574.6 | 676.8 | 748.6 | 328.5 | 359.7 | 397.8 | 628.6 | 548.2 | 544.2 | 628.3 | 553.2 | 436.7 | 459.1 | 436.5 | 454.2 | 412.3 | 522.1 | 439.7
1901 | 1665 | 564.3 | 225.72 | 263.8537 | 422.8 | 579.9 | 378.8 | 390.6 | 525.8 | 76.9 | 16.8 | 133 | 6.4 | 221.5 | 5.2 | 813.9 | 767.6 | 535.9 | 818 | 727.1 | 861.8 | 686.5 | 630.5 | 678.8 | 573.9 | 676.9 | 746.4 | 328.7 | 359.7 | 397.9 | 628.2 | 548.9 | 541.8 | 628.3 | 555 | 436.7 | 458.8 | 437.7 | 454.2 | 412.4 | 522.1 | 439.8
1902 | 1666 | 565.1 | 226.04 | 264.2277 | 422 | 573.2 | 378.2 | 391.5 | 522 | 76.9 | 16.8 | 132.9 | 6.5 | 217.2 | 5.2 | 811.1 | 762.9 | 537.6 | 816 | 727.1 | 861.2 | 684.7 | 630 | 682.8 | 573.9 | 676.8 | 746.6 | 328.8 | 359.8 | 397.8 | 627.7 | 548.1 | 538.9 | 628.2 | 554.2 | 436.8 | 458.5 | 437.8 | 454.4 | 412.3 | 522.1 | 439.8
1903 | 1667 | 565.1 | 226.04 | 264.2277 | 420.9 | 573 | 378.1 | 392.6 | 519 | 77 | 16.8 | 132.9 | 6.5 | 214.5 | 5.3 | 803.9 | 761.6 | 537.5 | 813.9 | 726.6 | 861.5 | 684.7 | 627.8 | 677.6 | 572.3 | 678.1 | 746 | 328.9 | 359.8 | 397.8 | 627.5 | 547.4 | 538.9 | 628.1 | 552.5 | 436.9 | 458.5 | 437.3 | 454.6 | 412.2 | 522 | 439.9
1904 | 1668 | 565.4 | 226.16 | 264.368 | 421 | 575.7 | 377.7 | 392.2 | 517.7 | 76.9 | 16.8 | 132.9 | 6 | 227.3 | 5 | 810.7 | 772.4 | 537.4 | 813 | 726.3 | 861.2 | 684.1 | 624.2 | 675.5 | 571 | 678.3 | 744.7 | 329 | 359.9 | 397.9 | 627.1 | 546.4 | 536.8 | 628.1 | 551.1 | 437 | 458.1 | 436.1 | 454.6 | 412.1 | 522 | 439.9
1905 | 1669 | 566.6 | 226.64 | 264.9291 | 420.9 | 572.7 | 377.3 | 391.2 | 517.5 | 76.9 | 16.8 | 132.9 | 6.5 | 240.5 | 4.4 | 819.4 | 777.5 | 536.8 | 814.5 | 725.9 | 861.6 | 688.2 | 624.4 | 686.5 | 568.8 | 678.7 | 746.1 | 329.1 | 359.9 | 398 | 627.3 | 545.9 | 537.9 | 628 | 550.7 | 437.1 | 457.7 | 436.3 | 454.7 | 412.2 | 521.9 | 439.9
1906 | 1670 | 567.2 | 226.88 | 265.2096 | 421.2 | 574.9 | 377.6 | 390.5 | 519.7 | 76.8 | 16.8 | 133.1 | 6.1 | 238.6 | 3.9 | 825.7 | 772.8 | 536.2 | 815.2 | 726.1 | 861.8 | 690.1 | 625.1 | 689.3 | 570 | 679.5 | 746.5 | 329.3 | 360 | 398 | 627.3 | 546.2 | 540.7 | 628.1 | 551.1 | 437.2 | 457 | 437.6 | 454.7 | 412.1 | 521.9 | 439.9
1907 | 1671 | 565.1 | 226.04 | 264.2277 | 422 | 579.1 | 378.4 | 390.2 | 521.6 | 76.8 | 16.8 | 133.1 | 7.1 | 216 | 3.9 | 829.7 | 773.8 | 535.7 | 816.2 | 725.9 | 862.2 | 692 | 624.8 | 686.5 | 570 | 679.6 | 746.2 | 329.4 | 360 | 398.1 | 627.4 | 546.3 | 541.4 | 628.4 | 550.9 | 437.3 | 456.3 | 438 | 454.7 | 412 | 521.8 | 439.9
1908 | 1672 | 563.7 | 225.48 | 263.5731 | 421.6 | 579.4 | 379 | 390 | 522 | 76.7 | 16.8 | 133.1 | 6.5 | 215.7 | 4 | 836.5 | 790.2 | 534.8 | 818.2 | 725.9 | 862.2 | 694.8 | 626.4 | 691.9 | 570.4 | 679.7 | 747.3 | 329.5 | 360.1 | 398.1 | 627.4 | 546.5 | 544.4 | 628.2 | 551 | 437.3 | 456.2 | 437.2 | 454.7 | 411.9 | 521.8 | 439.9
1909 | 1673 | 565.9 | 226.36 | 264.6018 | 421.7 | 567.3 | 378.7 | 389.6 | 523.2 | 76.6 | 16.8 | 133 | 6 | 217.7 | 3.7 | 847.8 | 806.9 | 534.2 | 819.5 | 726 | 861.7 | 699.2 | 630.9 | 705.3 | 571.8 | 680 | 748.7 | 329.6 | 360.1 | 398.2 | 627.7 | 547 | 546.9 | 628.5 | 551.6 | 437.4 | 456 | 436.6 | 454.8 | 411.9 | 521.7 | 439.9
1910 | 1674 | 566.2 | 226.48 | 264.7421 | 421.2 | 571.3 | 379.1 | 389 | 528.9 | 76.5 | 16.8 | 132.9 | 6.5 | 229.3 | 3.6 | 855.2 | 816.2 | 534.7 | 820.5 | 726.5 | 861.9 | 703.9 | 637.5 | 713.7 | 575.7 | 679.5 | 749.6 | 329.8 | 360.2 | 398.5 | 628.1 | 548.6 | 554.1 | 628.5 | 553.2 | 437.5 | 455.3 | 435.2 | 454.8 | 411.8 | 521.7 | 439.9
1911 | 1675 | 567.9 | 227.16 | 265.537 | 420.3 | 569.1 | 380.3 | 389 | 531.5 | 76.3 | 16.8 | 132.9 | 6.2 | 255.9 | 4.5 | 858.7 | 815.9 | 535.1 | 821.6 | 726.6 | 861.8 | 707 | 642.9 | 717.3 | 578.9 | 681 | 751.5 | 329.9 | 360.3 | 398.5 | 628.4 | 549.3 | 556.8 | 628.4 | 554.8 | 437.6 | 454.5 | 434.4 | 454.9 | 411.7 | 521.7 | 439.9
1912 | 1676 | 567.6 | 227.04 | 265.3967 | 419.6 | 567.5 | 381.6 | 388.9 | 533 | 76.3 | 16.7 | 132.9 | 5.8 | 249.3 | 4.5 | 860.7 | 817.5 | 535.2 | 824.2 | 727.4 | 862 | 709.8 | 648.4 | 725.9 | 581.1 | 681.1 | 753.6 | 330 | 360.3 | 398.6 | 628.9 | 549.4 | 561.3 | 628.6 | 555.4 | 437.7 | 453.8 | 434.5 | 455 | 411.7 | 521.7 | 439.9
1913 | 1677 | 566.8 | 226.72 | 265.0226 | 419.7 | 557.7 | 382.1 | 388.5 | 532.3 | 76.2 | 16.7 | 132.9 | 6 | 228.3 | 4.3 | 858.7 | 812 | 535.5 | 825.8 | 727.9 | 862.1 | 710.1 | 652.6 | 727.7 | 582.4 | 681.1 | 753.4 | 330.1 | 360.4 | 398.5 | 628.8 | 549.3 | 560 | 628.8 | 555.7 | 437.8 | 453.4 | 434.7 | 455.1 | 411.7 | 521.6 | 439.9
1914 | 1678 | 565.1 | 226.04 | 264.2277 | 421.2 | 551.3 | 382.7 | 388.6 | 531.2 | 76.2 | 16.7 | 132.9 | 6.3 | 248.2 | 4.2 | 859.2 | 811 | 535.2 | 826.6 | 728.1 | 863 | 709.6 | 655.1 | 729.6 | 583.1 | 680.8 | 753.7 | 330.2 | 360.4 | 398.6 | 628.9 | 549.4 | 561.5 | 628.8 | 555.6 | 437.9 | 453 | 434.8 | 455.2 | 411.6 | 521.6 | 439.9
1915 | 1679 | 565.3 | 226.12 | 264.3213 | 422.7 | 558.1 | 383.3 | 389.3 | 532.4 | 76.2 | 16.8 | 133 | 6.8 | 210.5 | 3.9 | 850.6 | 801.3 | 535.5 | 830 | 728.7 | 863.6 | 710.3 | 655.8 | 726.5 | 583.1 | 680.6 | 753.2 | 330.3 | 360.5 | 398.8 | 629 | 550 | 563 | 629.1 | 555.1 | 437.9 | 452.4 | 433.6 | 455.2 | 411.5 | 521.6 | 439.9
1916 | 1680 | 566.8 | 226.72 | 265.0226 | 422 | 552.4 | 384.1 | 389.5 | 532.5 | 76.2 | 16.7 | 133 | 6.4 | 199.4 | 4.2 | 846.4 | 792.9 | 535.6 | 830.6 | 729 | 863.3 | 707.1 | 655.2 | 720.2 | 583.2 | 680.4 | 753.9 | 330.4 | 360.6 | 398.6 | 628.8 | 549.5 | 560.3 | 628.9 | 554.1 | 438 | 451.6 | 433 | 455.3 | 411.5 | 521.6 | 439.9
1917 | 1681 | 567.2 | 226.88 | 265.2096 | 422.4 | 547 | 385.5 | 389 | 532.4 | 76.2 | 16.7 | 133 | 6.4 | 236.2 | 4.6 | 843.2 | 789.9 | 537.1 | 830.4 | 729.5 | 863 | 705.8 | 655 | 721.6 | 582.9 | 680.6 | 755 | 330.5 | 360.6 | 398.6 | 628.4 | 549.8 | 558.3 | 628.5 | 553.6 | 438.1 | 450.8 | 432.3 | 455.4 | 411.5 | 521.5 | 439.9
1918 | 1682 | 567.4 | 226.96 | 265.3032 | 423.4 | 542.2 | 385.3 | 388.5 | 530.3 | 76.3 | 16.7 | 133.1 | 6.3 | 220.2 | 5 | 850.9 | 793.3 | 538.5 | 830 | 729.9 | 863.3 | 708.3 | 656.3 | 724.9 | 582.3 | 680.3 | 756 | 330.7 | 360.7 | 398.7 | 628.1 | 548.9 | 557.6 | 628.5 | 552.7 | 438.2 | 450 | 431.7 | 455.5 | 411.5 | 521.5 | 439.9
1919 | 1683 | 566 | 226.4 | 264.6486 | 423.5 | 540.8 | 384.1 | 388.4 | 527.9 | 76.4 | 16.7 | 133 | 5.8 | 233.2 | 5.3 | 852.4 | 797.6 | 539 | 829.8 | 730.5 | 863.6 | 708.1 | 657.9 | 727.1 | 582.2 | 680.9 | 756 | 330.8 | 360.7 | 398.7 | 627.8 | 548.3 | 555.7 | 628.2 | 552.4 | 438.4 | 449.6 | 431.4 | 455.7 | 411.5 | 521.5 | 439.9
1920 | 1684 | 564.6 | 225.84 | 263.9939 | 423.9 | 544.6 | 383.4 | 388.4 | 525.1 | 76.5 | 16.7 | 132.9 | 6.4 | 245.6 | 4.9 | 858.2 | 797 | 538.4 | 829.7 | 730.9 | 862.8 | 709.6 | 658.7 | 726.8 | 582.2 | 681.4 | 756.6 | 330.9 | 360.8 | 398.6 | 627.4 | 547.9 | 553.5 | 627.9 | 551.9 | 438.4 | 449.3 | 431 | 455.6 | 411.6 | 521.4 | 439.9
1921 | 1685 | 562.6 | 225.04 | 263.0588 | 423.6 | 539.6 | 383.5 | 388.9 | 525.1 | 76.6 | 16.7 | 132.9 | 6.5 | 261 | 4.2 | 851.9 | 791.9 | 538.2 | 830.3 | 731.1 | 862.8 | 708.3 | 658.4 | 725.1 | 581.5 | 681.1 | 757.1 | 331 | 360.9 | 398.8 | 627.6 | 547.9 | 555.6 | 627.7 | 552.4 | 438.5 | 448.8 | 430.5 | 455.5 | 411.5 | 521.4 | 439.8
1922 | 1686 | 566.3 | 226.52 | 264.7888 | 424.7 | 534.4 | 383.3 | 388.7 | 526.1 | 76.7 | 16.7 | 132.9 | 6.4 | 259.6 | 4.3 | 843.6 | 785.1 | 538 | 829.8 | 730.9 | 863.3 | 703.4 | 655.1 | 716 | 579.2 | 679.9 | 756.6 | 331.2 | 361 | 398.8 | 627.4 | 548 | 554.2 | 627.9 | 552.5 | 438.5 | 448.5 | 430.4 | 455.5 | 411.5 | 521.3 | 439.8
1923 | 1687 | 566.4 | 226.56 | 264.8356 | 426.6 | 533.2 | 383.1 | 388.1 | 526.6 | 76.7 | 16.7 | 132.8 | 6.4 | 246 | 4.9 | 829.8 | 778.3 | 536.7 | 828.6 | 730.5 | 863.2 | 702.6 | 654 | 710.4 | 578.5 | 680.5 | 756.2 | 331.3 | 361 | 398.8 | 627.1 | 548.2 | 549.9 | 628 | 552.4 | 438.5 | 448.6 | 431.2 | 455.4 | 411.6 | 521.3 | 439.8
1924 | 1688 | 567.4 | 226.96 | 265.3032 | 426.4 | 530.9 | 382.4 | 388.2 | 527.7 | 76.7 | 16.7 | 132.8 | 6.1 | 237.7 | 4.8 | 816.8 | 771.9 | 535.5 | 826 | 730.1 | 863 | 698.1 | 651.5 | 701.2 | 576.8 | 680.9 | 754.6 | 331.4 | 361.1 | 398.8 | 626.7 | 548.8 | 546.5 | 627.9 | 552.1 | 438.5 | 449.6 | 431.3 | 455.4 | 411.7 | 521.3 | 439.8
1925 | 1689 | 566.4 | 226.56 | 264.8356 | 424.2 | 534.5 | 381.3 | 389.3 | 524.2 | 76.8 | 16.7 | 132.9 | 6.2 | 239.8 | 4.6 | 814.4 | 762.2 | 534.2 | 822.9 | 729.9 | 862.3 | 696.3 | 649.2 | 694.1 | 575.6 | 681.1 | 754.4 | 331.6 | 361.1 | 398.7 | 626.2 | 548.1 | 542.4 | 627.5 | 550.9 | 438.5 | 451.7 | 431.9 | 455.4 | 411.7 | 521.2 | 439.8
1926 | 1690 | 565.9 | 226.36 | 264.6018 | 423.3 | 541.4 | 380.9 | 390.2 | 521.1 | 76.8 | 16.7 | 132.9 | 5.7 | 246.4 | 4.9 | 808.8 | 758.2 | 533 | 820.8 | 729.5 | 862.5 | 692.8 | 644.4 | 687.9 | 573.7 | 680.5 | 752.3 | 331.7 | 361.2 | 398.8 | 625.7 | 547 | 539.4 | 627.4 | 549.4 | 438.6 | 453.3 | 432.1 | 455.3 | 411.6 | 521.2 | 439.9
1927 | 1691 | 565.3 | 226.12 | 264.3213 | 421.7 | 549.1 | 380.9 | 390.7 | 518.5 | 76.8 | 16.7 | 132.9 | 5.8 | 251 | 5.6 | 817.4 | 758.2 | 532 | 818.5 | 729.1 | 863.1 | 689.8 | 639.7 | 683.8 | 571.1 | 679.4 | 750.9 | 331.8 | 361.3 | 398.8 | 625.5 | 546.1 | 539.4 | 627.2 | 548.2 | 438.6 | 454.6 | 432.3 | 455.3 | 411.5 | 521.1 | 440
1928 | 1692 | 565.3 | 226.12 | 264.3213 | 420.9 | 550.6 | 380.3 | 390.8 | 518.6 | 76.9 | 16.7 | 133 | 6.2 | 251.3 | 5.5 | 817.6 | 761.1 | 531.2 | 816.1 | 728.5 | 863.3 | 688.7 | 636.5 | 680.5 | 570.1 | 679.4 | 749.4 | 332 | 361.3 | 398.8 | 625.4 | 545.8 | 538 | 627.4 | 548.5 | 438.6 | 455.1 | 432.2 | 455.3 | 411.6 | 521.1 | 440
1929 | 1693 | 564.6 | 225.84 | 263.9939 | 419.5 | 550.3 | 379.9 | 390.2 | 517.6 | 76.9 | 16.7 | 133 | 6.3 | 232.9 | 5.1 | 817.3 | 765.6 | 530.9 | 815.5 | 728.4 | 862.6 | 690.7 | 634.8 | 683.8 | 570.5 | 679.4 | 749.8 | 332.1 | 361.4 | 398.8 | 625 | 545.5 | 536.2 | 627.4 | 548.4 | 438.6 | 456.3 | 432 | 455.2 | 411.5 | 521 | 440
1930 | 1694 | 565.8 | 226.32 | 264.555 | 419.7 | 552.1 | 379.8 | 390 | 518.5 | 76.9 | 16.7 | 133.1 | 6.6 | 238.7 | 4.7 | 814.1 | 768.4 | 531.1 | 816.1 | 728.4 | 862.4 | 691.9 | 632.7 | 682.9 | 570.3 | 679.2 | 749.3 | 332.2 | 361.4 | 399 | 625.1 | 545.4 | 535.9 | 627.4 | 547.8 | 438.6 | 457.9 | 431.1 | 455.1 | 411.4 | 520.9 | 440
1931 | 1695 | 568 | 227.2 | 265.5837 | 422 | 554.1 | 379.5 | 390.3 | 522.1 | 76.8 | 16.7 | 133 | 6.6 | 238.6 | 4.4 | 819.4 | 776 | 531.6 | 816.4 | 728.2 | 862.4 | 691.6 | 631.6 | 686.8 | 569.6 | 679.9 | 749.8 | 332.3 | 361.5 | 399 | 625.2 | 545.8 | 536.2 | 627.6 | 546.9 | 438.6 | 458.6 | 430.5 | 455 | 411.4 | 520.9 | 440
1932 | 1696 | 568 | 227.2 | 265.5837 | 421.6 | 549.3 | 378.9 | 390.1 | 522 | 76.8 | 16.7 | 133.1 | 6.5 | 222.7 | 4.4 | 826.9 | 787.1 | 532 | 817 | 728.1 | 863 | 693.8 | 631.7 | 691.4 | 568.5 | 679.8 | 751 | 332.5 | 361.6 | 399 | 625.1 | 545.4 | 536.5 | 627.6 | 547 | 438.6 | 459.7 | 430.7 | 455.2 | 411.4 | 520.8 | 440
1933 | 1697 | 567.1 | 226.84 | 265.1629 | 420.6 | 549.8 | 378.6 | 390.3 | 522.1 | 76.8 | 16.7 | 133.1 | 6.2 | 218.5 | 4.7 | 837 | 795.5 | 531.9 | 819.1 | 728.4 | 863.2 | 697.2 | 634.3 | 698.8 | 570.4 | 680.9 | 751.1 | 332.6 | 361.6 | 399.1 | 625.2 | 545.7 | 542 | 628 | 548.2 | 438.7 | 459.4 | 430.9 | 455.5 | 411.3 | 520.8 | 440.1
1934 | 1698 | 564.3 | 225.72 | 263.8537 | 420.7 | 543.3 | 378.9 | 390.5 | 523.1 | 76.8 | 16.7 | 133.1 | 6.4 | 209.3 | 4.9 | 847 | 797.7 | 531.5 | 821.1 | 729.2 | 863.1 | 700.8 | 639.1 | 707 | 573.2 | 681 | 752.4 | 332.7 | 361.7 | 399.1 | 625.5 | 546.3 | 546.9 | 628.2 | 549.8 | 438.9 | 458.7 | 430.8 | 455.8 | 411.3 | 520.7 | 440.1
1935 | 1699 | 565.1 | 226.04 | 264.2277 | 421.1 | 537.5 | 379.3 | 390.4 | 525 | 76.9 | 16.7 | 133.2 | 6.1 | 216.3 | 4.4 | 854.4 | 799.9 | 531 | 822.6 | 729.6 | 863.3 | 702.2 | 643.4 | 711.2 | 575.8 | 681.7 | 753.6 | 332.8 | 361.7 | 399.2 | 625.7 | 547.2 | 548.6 | 628.2 | 551.6 | 439.1 | 458 | 430.9 | 456.1 | 411.4 | 520.7 | 440.1
1936 | 1700 | 566.2 | 226.48 | 264.7421 | 421.7 | 527.3 | 379.2 | 390.8 | 527.4 | 76.9 | 16.7 | 133.2 | 6.1 | 221.4 | 4.1 | 857.4 | 800.1 | 530.2 | 823.5 | 729.8 | 863.4 | 701.8 | 647.7 | 714.2 | 577.7 | 681.2 | 754.1 | 332.9 | 361.8 | 399.2 | 625.6 | 548.2 | 547.5 | 627.9 | 552.4 | 439.3 | 457.8 | 431 | 456.3 | 411.4 | 520.7 | 440.2
1937 | 1701 | 566.8 | 226.72 | 265.0226 | 420.8 | 523.7 | 379.5 | 392.1 | 526 | 77 | 16.7 | 133.2 | 6.1 | 239.6 | 4 | 859.4 | 805.1 | 529.6 | 824.1 | 730.3 | 863.3 | 702.5 | 648.6 | 710.5 | 578.1 | 681.2 | 754 | 333.1 | 361.8 | 399.2 | 625.3 | 547.9 | 547 | 627.7 | 551.2 | 439.5 | 458.3 | 430.5 | 456.5 | 411.4 | 520.7 | 440.2
1938 | 1702 | 566.9 | 226.76 | 265.0694 | 420.3 | 524.1 | 379.8 | 393.1 | 524.3 | 77 | 16.7 | 133.2 | 6 | 250.4 | 4.1 | 858.9 | 815.9 | 530 | 824.9 | 730.8 | 863.5 | 705 | 650.6 | 716 | 578.9 | 681.5 | 754.9 | 333.2 | 361.9 | 399.3 | 625.4 | 547.7 | 548.9 | 627.6 | 551.6 | 439.7 | 458.4 | 430.2 | 456.6 | 411.4 | 520.6 | 440.2
1939 | 1703 | 567.8 | 227.12 | 265.4902 | 420.9 | 520.9 | 379.5 | 393.6 | 524.6 | 77.1 | 16.7 | 133.3 | 6.3 | 249.1 | 4.1 | 859.6 | 821.2 | 530 | 824.2 | 731.5 | 863.2 | 709.5 | 653.8 | 722.6 | 580.3 | 680.7 | 755.6 | 333.3 | 361.9 | 399.4 | 625.7 | 547.9 | 552.7 | 627.9 | 551.9 | 439.8 | 458.6 | 429.6 | 456.7 | 411.4 | 520.6 | 440.3
1940 | 1704 | 566.1 | 226.44 | 264.6953 | 422.5 | 516.4 | 380.1 | 394 | 526.2 | 77 | 16.7 | 133.3 | 6.1 | 248.2 | 4.1 | 860.3 | 825.3 | 529.4 | 824.2 | 732 | 863.1 | 712.4 | 658.8 | 730.4 | 582.4 | 679.8 | 757.6 | 333.4 | 362 | 399.4 | 625.8 | 548.2 | 554.5 | 628.1 | 552.9 | 439.9 | 460 | 429.6 | 456.8 | 411.5 | 520.6 | 440.3
1941 | 1705 | 566.9 | 226.76 | 265.0694 | 423.3 | 512.8 | 380.2 | 394.4 | 527 | 76.9 | 16.7 | 133.3 | 6.1 | 242.9 | 4.3 | 862.1 | 824.9 | 529.2 | 825.8 | 732.5 | 862.9 | 713.9 | 661.7 | 733.4 | 583.6 | 679.8 | 758.9 | 333.6 | 362 | 399.5 | 625.7 | 548.5 | 554.1 | 627.9 | 552.9 | 440.1 | 461.1 | 429.5 | 457 | 411.5 | 520.5 | 440.3
1942 | 1706 | 568.5 | 227.4 | 265.8175 | 423.7 | 513.8 | 380.6 | 394.8 | 529.4 | 76.9 | 16.7 | 133.5 | 5.9 | 242.3 | 4.3 | 864.8 | 821.6 | 530.2 | 829.1 | 732.9 | 863.4 | 715.6 | 664.8 | 734.9 | 585.6 | 679.6 | 758.8 | 333.7 | 362.1 | 399.7 | 626.3 | 549.3 | 563.4 | 627.8 | 554.2 | 440.2 | 462.9 | 429.8 | 457.1 | 411.5 | 520.5 | 440.4
1943 | 1707 | 567.2 | 226.88 | 265.2096 | 424.1 | 510.1 | 380.3 | 395.5 | 531.6 | 76.8 | 16.7 | 133.6 | 5.7 | 257.4 | 4.4 | 864.3 | 812.6 | 530.1 | 833.5 | 733 | 863.4 | 715.2 | 663.8 | 730.3 | 585.4 | 679.3 | 757.9 | 333.8 | 362.1 | 399.7 | 626.5 | 549.9 | 562.5 | 627.7 | 553.3 | 440.4 | 463.2 | 434.9 | 457.2 | 412 | 520.5 | 440.4
1944 | 1708 | 566.1 | 226.44 | 264.6953 | 424.9 | 506.5 | 380.1 | 395.8 | 532.7 | 76.9 | 16.7 | 133.7 | 6.3 | 246 | 4.9 | 864.7 | 810.7 | 530.3 | 834.2 | 733.5 | 863.3 | 713.6 | 665.1 | 726.1 | 586.1 | 679.5 | 758.2 | 333.9 | 362.2 | 399.7 | 626.8 | 550.4 | 562.5 | 627.6 | 554.2 | 440.5 | 464.2 | 439.6 | 457.4 | 415.5 | 520.5 | 440.5
1945 | 1709 | 565.3 | 226.12 | 264.3213 | 426.2 | 502 | 380.4 | 396.3 | 531.3 | 77 | 16.7 | 133.7 | 5.8 | 233.3 | 5 | 864.6 | 814.3 | 531 | 832.1 | 734.1 | 863 | 708.4 | 664.3 | 717.4 | 586 | 680.1 | 756.6 | 334 | 362.2 | 399.7 | 626.3 | 552.3 | 558.4 | 627.1 | 555.3 | 440.6 | 465.8 | 441.1 | 457.5 | 415.1 | 520.5 | 440.6
1946 | 1710 | 564.8 | 225.92 | 264.0875 | 426.4 | 505.3 | 380.4 | 397.2 | 525.9 | 77 | 16.7 | 133.7 | 5.7 | 235.2 | 4.7 | 869.7 | 818.6 | 530.9 | 829.6 | 734.3 | 863.3 | 702.6 | 660.3 | 712.6 | 585.1 | 680.6 | 753.9 | 334.1 | 362.3 | 399.6 | 625.8 | 551.1 | 553.5 | 626.8 | 554.1 | 440.8 | 466.9 | 441.5 | 457.8 | 414.7 | 520.5 | 440.7
1947 | 1711 | 566.1 | 226.44 | 264.6953 | 424.9 | 513.9 | 380.3 | 398.6 | 521 | 77.1 | 16.7 | 133.7 | 5.6 | 239.3 | 5.2 | 867 | 828 | 531.5 | 828.4 | 734.3 | 863.7 | 703.9 | 660.6 | 719.2 | 584.5 | 679.7 | 753.9 | 334.2 | 362.3 | 399.6 | 625.2 | 549.7 | 551.5 | 626.5 | 552.2 | 441.1 | 466.7 | 440.9 | 458.1 | 414.6 | 520.5 | 440.8
1948 | 1712 | 566.2 | 226.48 | 264.7421 | 423.9 | 513.5 | 380.7 | 399.6 | 519.5 | 77.1 | 16.7 | 133.7 | 5.7 | 228.6 | 5.8 | 864.3 | 830.6 | 532.2 | 828.6 | 734.4 | 863.8 | 708 | 663.5 | 727.2 | 585.2 | 679.5 | 754.9 | 334.3 | 362.4 | 399.7 | 625.2 | 549.3 | 557.7 | 626.5 | 552.9 | 441.3 | 466.2 | 440.3 | 458.3 | 414.5 | 520.5 | 440.9
1949 | 1713 | 561.2 | 224.48 | 262.4042 | 424.1 | 509.6 | 381 | 400 | 522 | 77.1 | 16.7 | 133.6 | 5.6 | 236.9 | 5.8 | 860.3 | 836.8 | 531.8 | 830 | 734.9 | 863.7 | 712.5 | 666.8 | 735 | 586.7 | 678.8 | 756.3 | 334.5 | 362.5 | 400 | 626 | 549.7 | 563.3 | 626.5 | 555.3 | 441.5 | 465.6 | 439.4 | 458.4 | 414.5 | 520.4 | 440.9
1950 | 1714 | 191.4 | 76.56 | 89.4942 | 425.3 | 504.4 | 381.2 | 399.8 | 525.2 | 77.1 | 16.7 | 133.7 | 5.7 | 248.8 | 5.5 | 859.9 | 843.4 | 534 | 830.7 | 735.2 | 864 | 713.9 | 669.7 | 740.1 | 588.9 | 678.3 | 757.2 | 334.6 | 362.5 | 400 | 626.1 | 550.4 | 564.7 | 626.3 | 556 | 441.6 | 465.1 | 439.2 | 458.4 | 414.5 | 520.4 | 441
1951 | 1715 | -6.7 | 0 | 0 | 425.4 | 499.2 | 381.8 | 399.7 | 525.9 | 77.1 | 16.7 | 133.8 | 5.8 | 251.7 | 5.4 | 868 | 844.7 | 534.1 | 832.5 | 735.6 | 864 | 714.8 | 671.7 | 740.2 | 589.5 | 679 | 757.8 | 334.7 | 362.6 | 399.9 | 626 | 550.9 | 566.5 | 626 | 555.5 | 441.7 | 466.6 | 438.8 | 458.4 | 414.4 | 520.4 | 441
1952 | 1716 | -6.7 | 0 | 0 | 424.8 | 494.2 | 382.4 | 399.2 | 523.2 | 77 | 16.7 | 133.8 | 4.9 | 249.9 | 5.5 | 841.3 | 822.4 | 533.6 | 835.9 | 735.2 | 862.5 | 708.9 | 667.6 | 726.3 | 588.1 | 678.9 | 752.6 | 334.8 | 362.7 | 399.7 | 625.3 | 550 | 562.2 | 625.8 | 553.1 | 441.8 | 476.5 | 437.6 | 458.6 | 414.2 | 520.4 | 441.1
1953 | 1717 | -6.7 | 0 | 0 | 423.7 | 496.9 | 382 | 398.6 | 517 | 76.9 | 16.7 | 133.7 | 5 | 244.5 | 5.2 | 783.1 | 784.8 | 533 | 832 | 734.3 | 855.3 | 699 | 658.2 | 705.6 | 583.5 | 680 | 746 | 334.9 | 362.7 | 399.5 | 624.3 | 547.6 | 553.5 | 625.6 | 549.1 | 441.9 | 477.9 | 436.7 | 458.7 | 413.9 | 520.4 | 441.4
1954 | 1718 | -6.7 | 0 | 0 | 421.6 | 500.2 | 380.8 | 397.5 | 509.1 | 76.9 | 16.7 | 133.7 | 5.1 | 241.2 | 5.2 | 736.4 | 754.8 | 532.5 | 825.7 | 732.7 | 846.3 | 687.6 | 647.7 | 684.8 | 576.9 | 679.2 | 740 | 335 | 362.8 | 399.3 | 623.1 | 545.2 | 545.5 | 625.2 | 545.6 | 442 | 476.7 | 435.6 | 458.8 | 413.5 | 520.3 | 441.6
1955 | 1719 | -6.7 | 0 | 0 | 418.8 | 499.3 | 378.9 | 395.3 | 502.8 | 77 | 16.7 | 133.7 | 5.2 | 220.8 | 4.7 | 700.7 | 730.6 | 531.8 | 819.1 | 731.2 | 838.4 | 679.2 | 636.3 | 667.5 | 570.5 | 679.8 | 734.5 | 335.1 | 362.9 | 399.2 | 622.1 | 541.9 | 538.2 | 624.7 | 542.5 | 442.1 | 474.5 | 433.8 | 458.9 | 413.1 | 520.2 | 441.6
1956 | 1720 | -6.7 | 0 | 0 | 416.1 | 502.8 | 376.4 | 392.2 | 497.2 | 77 | 16.7 | 133.7 | 5 | 222.9 | 4.1 | 671.2 | 709.1 | 531 | 812.8 | 729.6 | 830.9 | 672.7 | 624.9 | 650.8 | 565.3 | 679.9 | 729.6 | 335.2 | 362.9 | 399.1 | 621 | 538.9 | 531.4 | 624.1 | 540.7 | 442.3 | 472.1 | 431.9 | 459 | 412.6 | 520.1 | 441.6
1957 | 1721 | -6.7 | 0 | 0 | 413.7 | 508.4 | 373.6 | 388.7 | 491.5 | 77 | 16.7 | 133.5 | 4.5 | 235.5 | 4 | 644 | 690.6 | 529.6 | 806.8 | 728 | 823.4 | 665.4 | 613.8 | 636.2 | 560.7 | 680.3 | 724.2 | 335.3 | 363 | 398.9 | 619.8 | 537.1 | 524.8 | 623.4 | 539 | 442.4 | 469.8 | 428.8 | 458.9 | 412.1 | 520 | 441.6
1958 | 1722 | -6.7 | 0 | 0 | 411.3 | 505.4 | 370.9 | 385.1 | 486.7 | 77 | 16.7 | 133.3 | 4.4 | 222.7 | 3.7 | 620.3 | 674 | 529.5 | 801.2 | 726.5 | 815.4 | 658.4 | 603.2 | 624 | 557 | 680.8 | 719.2 | 335.4 | 363.1 | 398.8 | 618.6 | 534.8 | 518.9 | 622.8 | 537.6 | 442.3 | 468.1 | 426.7 | 458.7 | 411.5 | 519.8 | 441.6
1959 | 1723 | -6.7 | 0 | 0 | 408.8 | 504 | 368.2 | 381.2 | 481.8 | 77 | 16.7 | 133 | 4.7 | 211.1 | 3.5 | 599.7 | 656.2 | 528.5 | 795.9 | 724.8 | 807.9 | 650.2 | 593 | 613.5 | 552.2 | 680.2 | 714.3 | 335.5 | 363.1 | 398.6 | 617.5 | 533.3 | 514.1 | 622.1 | 536.2 | 442.3 | 466.5 | 423.8 | 458.4 | 411 | 519.7 | 441.5
1960 | 1724 | -6.7 | 0 | 0 | 406.1 | 515 | 366 | 377.2 | 479 | 76.9 | 16.7 | 132.6 | 5 | 229.7 | 3.9 | 581.9 | 638.1 | 527.3 | 790.5 | 723.7 | 801 | 643.1 | 583.6 | 604 | 548.2 | 680.9 | 709.9 | 335.6 | 363.2 | 398.5 | 616.6 | 531.9 | 510 | 621.5 | 535.3 | 442.3 | 465.2 | 420.7 | 458.2 | 410.4 | 519.6 | 441.5
1961 | 1725 | -6.7 | 0 | 0 | 403.4 | 512.9 | 363.9 | 373.9 | 477 | 76.9 | 16.7 | 132 | 5.2 | 238.2 | 4.1 | 564.6 | 623.2 | 525.4 | 785.3 | 722.5 | 794.4 | 638 | 574.3 | 595.3 | 543.7 | 681.7 | 705.3 | 335.7 | 363.2 | 398.3 | 615.7 | 529.9 | 505.9 | 621 | 533.9 | 442.2 | 463.3 | 417.9 | 458 | 409.8 | 519.4 | 441.4
1962 | 1726 | -6.7 | 0 | 0 | 400.6 | 509.7 | 361.7 | 371.2 | 474.5 | 76.9 | 16.7 | 131.5 | 5.3 | 242.6 | 4.1 | 549.7 | 608.8 | 525 | 780.6 | 720.9 | 787.8 | 631.6 | 565.8 | 587.8 | 540.3 | 681.1 | 700.9 | 335.8 | 363.3 | 398.2 | 614.8 | 528.4 | 501.8 | 620.6 | 532.7 | 442.1 | 461 | 415.1 | 457.8 | 409.3 | 519.3 | 441.4
1963 | 1727 | -6.7 | 0 | 0 | 398 | 503.6 | 359.9 | 368.4 | 472.6 | 77 | 16.7 | 130.9 | 5 | 247.2 | 3.9 | 536.6 | 596.1 | 524.6 | 775.9 | 719.5 | 781.4 | 627.1 | 557.6 | 581.8 | 538.1 | 681.6 | 696.2 | 335.9 | 363.3 | 398 | 613.8 | 526.9 | 497.7 | 620.2 | 531.7 | 442.1 | 458.6 | 412.8 | 457.7 | 408.8 | 519.1 | 441.3
1964 | 1728 | -6.7 | 0 | 0 | 395.7 | 503 | 358.1 | 365.5 | 471.8 | 77 | 16.7 | 130.4 | 5 | 234 | 4 | 524 | 583.4 | 523.5 | 771.8 | 718.2 | 775.5 | 623.1 | 550.3 | 575.9 | 537.2 | 682.2 | 691.5 | 336 | 363.4 | 397.8 | 613 | 525.4 | 494.1 | 619.8 | 530.4 | 442 | 456.3 | 410 | 457.5 | 408.2 | 518.9 | 441.2
1965 | 1729 | -6.7 | 0 | 0 | 393.4 | 513.6 | 356.4 | 362.6 | 468.5 | 76.9 | 16.7 | 129.9 | 4.9 | 227.1 | 3.7 | 513.8 | 571.7 | 522.5 | 767.5 | 716.7 | 769.6 | 619.2 | 543.5 | 568.8 | 534.8 | 682.9 | 687.7 | 336.1 | 363.4 | 397.7 | 612.2 | 524 | 490.6 | 619.5 | 529 | 441.8 | 455.6 | 407.3 | 457.2 | 407.6 | 518.8 | 441.1
1966 | 1730 | -6.7 | 0 | 0 | 391 | 505.7 | 355.1 | 359.9 | 465.3 | 76.9 | 16.7 | 129.4 | 5 | 232 | 3.4 | 503.3 | 560.8 | 521.6 | 763.2 | 715.4 | 763.9 | 614.4 | 536.6 | 562.8 | 531.5 | 683.6 | 683.5 | 336.2 | 363.5 | 397.5 | 611.3 | 522.2 | 487.2 | 619 | 528.2 | 441.7 | 455.5 | 405.2 | 456.8 | 407.1 | 518.6 | 441
1967 | 1731 | -6.6 | 0 | 0 | 388.8 | 504.2 | 353.9 | 357.7 | 462 | 76.8 | 16.7 | 128.9 | 5 | 239.6 | 3.4 | 496.2 | 551.8 | 520.3 | 758.8 | 714 | 758.9 | 610.9 | 529.9 | 558.3 | 528.9 | 683.9 | 679.6 | 336.3 | 363.5 | 397.3 | 610.5 | 520.6 | 484.4 | 618.6 | 527.3 | 441.5 | 454.3 | 403.1 | 456.4 | 406.6 | 518.4 | 440.9
1968 | 1732 | -6.6 | 0 | 0 | 386.9 | 502.7 | 352.5 | 355.7 | 458.4 | 76.7 | 16.7 | 128.4 | 5.3 | 242.4 | 3.5 | 489.4 | 543.4 | 519.1 | 754 | 712.7 | 754.2 | 607.5 | 523.6 | 555.1 | 527 | 684.5 | 676.1 | 336.3 | 363.5 | 397.2 | 609.8 | 518.9 | 482.3 | 618.3 | 526.5 | 441.3 | 451.5 | 401 | 456 | 406.1 | 518.2 | 440.9
1969 | 1733 | -6.6 | 0 | 0 | 385.3 | 500.8 | 351 | 353.7 | 454.8 | 76.6 | 16.7 | 128 | 5.1 | 245.4 | 3.5 | 481.9 | 535.4 | 518.7 | 749.3 | 711.2 | 749.2 | 604.6 | 518.7 | 550.9 | 525.1 | 685 | 672.7 | 336.4 | 363.5 | 397 | 608.9 | 516.9 | 479.5 | 617.9 | 525.7 | 441.1 | 449.5 | 399.3 | 455.8 | 405.6 | 518.1 | 440.8
1970 | 1734 | -6.6 | 0 | 0 | 383.8 | 499.8 | 349.5 | 351.7 | 452.5 | 76.4 | 16.7 | 127.5 | 5.1 | 247.5 | 3.4 | 474.4 | 527.1 | 518.5 | 745 | 709.9 | 744.7 | 601.2 | 513.5 | 546.8 | 524.7 | 686.4 | 669.2 | 336.5 | 363.5 | 396.8 | 608 | 515.5 | 477.1 | 617.4 | 524.7 | 441 | 448.1 | 397.4 | 455.6 | 405 | 517.9 | 440.7
1971 | 1735 | -6.6 | 0 | 0 | 382.3 | 494.2 | 348.2 | 350 | 451 | 76.3 | 16.7 | 127.1 | 4.6 | 247.5 | 3.7 | 468.3 | 520.3 | 517.7 | 740.6 | 708.6 | 740.8 | 596.8 | 508.7 | 542.7 | 524.8 | 687.2 | 665.8 | 336.6 | 363.5 | 396.7 | 607.3 | 514.2 | 475.3 | 616.9 | 523 | 440.8 | 445.8 | 395.6 | 455.4 | 404.5 | 517.7 | 440.6
1972 | 1736 | -6.6 | 0 | 0 | 380.7 | 488.9 | 347 | 348.4 | 450.8 | 76.1 | 16.7 | 126.7 | 4.8 | 247.4 | 3.7 | 463.6 | 514.1 | 516.8 | 736 | 707.4 | 737.7 | 592.5 | 504.3 | 539.6 | 522.6 | 688.1 | 662.7 | 336.6 | 363.5 | 396.5 | 606.7 | 512.7 | 473 | 616.6 | 521.6 | 440.7 | 444.3 | 393.9 | 455.2 | 404 | 517.5 | 440.5
1973 | 1737 | -6.6 | 0 | 0 | 379.2 | 485.6 | 345.6 | 346.8 | 449.1 | 75.9 | 16.7 | 126.3 | 5 | 221.2 | 3.5 | 457.3 | 507.3 | 515.7 | 730.9 | 705.9 | 734.5 | 589.1 | 500.1 | 537.6 | 520.2 | 688.2 | 659 | 336.7 | 363.5 | 396.3 | 606 | 511.6 | 471 | 616.2 | 520.8 | 440.5 | 444.8 | 392 | 455 | 403.6 | 517.4 | 440.4
1974 | 1738 | -6.6 | 0 | 0 | 377.9 | 481.7 | 344.5 | 345.4 | 446.7 | 75.8 | 16.7 | 126 | 4.6 | 220.2 | 3.5 | 450.3 | 500.6 | 514.9 | 726.2 | 704.4 | 731.2 | 585.5 | 496.3 | 536.6 | 519.6 | 688.8 | 655.5 | 336.8 | 363.6 | 396.2 | 605.1 | 510 | 469.3 | 615.8 | 520.3 | 440.3 | 443.2 | 390.1 | 454.7 | 403.1 | 517.2 | 440.3
1975 | 1739 | -6.6 | 0 | 0 | 376.5 | 478.2 | 343.5 | 344.1 | 446.4 | 75.7 | 16.7 | 125.7 | 4.9 | 238.5 | 3.5 | 443.9 | 494.9 | 513.8 | 722.2 | 703.2 | 728.2 | 582.3 | 492.8 | 534.4 | 519.6 | 689.6 | 651.9 | 336.9 | 363.6 | 396 | 604.3 | 509 | 467.4 | 615.3 | 519.5 | 440.2 | 442.2 | 388.8 | 454.5 | 402.6 | 517 | 440.1
1976 | 1740 | -6.6 | 0 | 0 | 375.1 | 472.4 | 342.4 | 343.1 | 444.4 | 75.5 | 16.7 | 125.3 | 4.7 | 243.5 | 3.5 | 437.7 | 487.8 | 513.1 | 718.1 | 701.9 | 725.3 | 579.2 | 489 | 531.4 | 517.5 | 689.7 | 648.7 | 337 | 363.6 | 395.8 | 603.6 | 507.6 | 465.7 | 614.8 | 518.6 | 440 | 441.3 | 387.9 | 454.2 | 402.1 | 516.9 | 440
1977 | 1741 | -6.6 | 0 | 0 | 373.6 | 465.9 | 341.5 | 341.9 | 442.4 | 75.4 | 16.7 | 125.1 | 5.1 | 231.2 | 3.2 | 431.7 | 481.7 | 512 | 714.5 | 700.6 | 722.5 | 575.9 | 485.3 | 529.7 | 517.7 | 689.5 | 645.6 | 337 | 363.6 | 395.6 | 602.8 | 506.3 | 464.5 | 614.6 | 517.7 | 439.9 | 439.4 | 386.3 | 454 | 401.7 | 516.7 | 439.9
1978 | 1742 | -6.6 | 0 | 0 | 372.3 | 460.5 | 340.5 | 340.8 | 441.1 | 75.2 | 16.7 | 124.8 | 5.1 | 201.7 | 2.9 | 426.9 | 476.1 | 511.8 | 711.3 | 699.3 | 719.6 | 571.4 | 482.1 | 527.4 | 517.2 | 689.9 | 642.3 | 337.1 | 363.6 | 395.4 | 602.1 | 505.5 | 463.6 | 614.3 | 516.6 | 439.8 | 438.9 | 384.6 | 453.8 | 401.2 | 516.5 | 439.8
1979 | 1743 | -6.6 | 0 | 0 | 371.3 | 456.8 | 339.6 | 339.7 | 441 | 75.1 | 16.7 | 124.5 | 4.6 | 205.2 | 2.8 | 422.4 | 470.9 | 511 | 708.2 | 698.1 | 716.7 | 568.1 | 479 | 524.9 | 515.5 | 689.4 | 639 | 337.2 | 363.5 | 395.3 | 601.6 | 504.9 | 462.2 | 614 | 515.3 | 439.6 | 438.2 | 383.3 | 453.5 | 400.7 | 516.3 | 439.7
1980 | 1744 | -6.6 | 0 | 0 | 370.3 | 458.4 | 338.7 | 338.7 | 440.4 | 75 | 16.7 | 124.2 | 4.7 | 215.1 | 2.9 | 416.7 | 466 | 510 | 704.6 | 697 | 713.6 | 566.1 | 476.5 | 522.9 | 514 | 689.9 | 635.6 | 337.2 | 363.5 | 395.1 | 601 | 503.7 | 461 | 613.8 | 514.3 | 439.4 | 436.5 | 381.8 | 453.2 | 400.2 | 516.1 | 439.5
1981 | 1745 | -6.6 | 0 | 0 | 369.5 | 455.8 | 338 | 337.8 | 438.9 | 74.8 | 16.7 | 123.8 | 4.8 | 214.1 | 3.1 | 411.6 | 460.9 | 509.8 | 701.3 | 695.9 | 710.2 | 563.3 | 473.8 | 520.7 | 512.9 | 691.1 | 632.6 | 337.3 | 363.5 | 394.9 | 600.5 | 502.6 | 459 | 613.5 | 513.3 | 439.3 | 434.3 | 380.4 | 452.9 | 399.8 | 516 | 439.4
1982 | 1746 | -6.6 | 0 | 0 | 368.6 | 456.2 | 337.2 | 337.1 | 436.9 | 74.6 | 16.7 | 123.5 | 4.8 | 210.7 | 3.2 | 407.5 | 455.7 | 508.1 | 698.4 | 695.2 | 707.1 | 560 | 471.7 | 520.2 | 511.3 | 690.3 | 629.9 | 337.3 | 363.5 | 394.7 | 600.1 | 501.8 | 457.5 | 613.2 | 512.3 | 439.1 | 433.1 | 379.4 | 452.6 | 399.3 | 515.8 | 439.3
1983 | 1747 | -6.6 | 0 | 0 | 367.9 | 457.8 | 336.4 | 336.5 | 435.2 | 74.4 | 16.7 | 123.2 | 4.7 | 224.3 | 3 | 404.5 | 451 | 507 | 695.1 | 693.8 | 703.8 | 558.6 | 469.4 | 518.2 | 511.2 | 690.9 | 626.9 | 337.4 | 363.5 | 394.6 | 599.6 | 501.4 | 456.5 | 613.1 | 511.4 | 438.9 | 432.7 | 378 | 452.3 | 398.9 | 515.6 | 439.2
1984 | 1748 | -6.6 | 0 | 0 | 367.1 | 455.9 | 335.6 | 335.9 | 433.8 | 74.3 | 16.7 | 122.9 | 4.7 | 243.1 | 2.7 | 401.3 | 446.6 | 506 | 691.2 | 692.8 | 700.5 | 555.5 | 467.3 | 515.2 | 510.5 | 691.8 | 623.8 | 337.4 | 363.4 | 394.4 | 599.1 | 500.8 | 455.5 | 612.8 | 510.7 | 438.7 | 431.2 | 376.7 | 452 | 398.4 | 515.4 | 439.1
1985 | 1749 | -6.6 | 0 | 0 | 366.1 | 458.3 | 335.1 | 335.4 | 432 | 74.1 | 16.7 | 122.5 | 4.6 | 254.9 | 2.6 | 397.4 | 443 | 504.6 | 687.6 | 691.9 | 697.1 | 553.1 | 464.2 | 512.9 | 510.7 | 692 | 620.6 | 337.5 | 363.4 | 394.2 | 598.6 | 500 | 454.1 | 612.5 | 510.1 | 438.5 | 431.7 | 375.5 | 451.7 | 397.9 | 515.2 | 439
1986 | 1750 | -6.6 | 0 | 0 | 365.4 | 461.2 | 334.5 | 335 | 432.4 | 73.9 | 16.7 | 122.2 | 5 | 242.2 | 2.4 | 393.1 | 438.8 | 503.6 | 684.2 | 691 | 693.9 | 551.1 | 461.8 | 512.5 | 511.7 | 691.8 | 617.5 | 337.5 | 363.4 | 394 | 598.1 | 498.9 | 452.8 | 612.4 | 509.1 | 438.3 | 433.2 | 374.5 | 451.4 | 397.5 | 515 | 438.8
1987 | 1751 | -6.6 | 0 | 0 | 364.8 | 459 | 334.3 | 334.7 | 434.4 | 73.6 | 16.7 | 121.9 | 4.9 | 216.5 | 2.4 | 389.2 | 434 | 504 | 681.6 | 689.9 | 690.6 | 549.2 | 459.6 | 511.9 | 508.5 | 691.3 | 614.5 | 337.6 | 363.4 | 393.9 | 597.5 | 498 | 451.5 | 612.3 | 508.1 | 438.1 | 434.2 | 373.8 | 451 | 397.1 | 514.8 | 438.7
1988 | 1752 | -6.6 | 0 | 0 | 364.2 | 459.4 | 333.8 | 334 | 435.4 | 73.4 | 16.7 | 121.6 | 4.8 | 207 | 2.4 | 385.6 | 430 | 503.7 | 679.2 | 688.6 | 687.5 | 547.7 | 457.7 | 510.2 | 507.8 | 690.9 | 611.6 | 337.6 | 363.3 | 393.7 | 596.9 | 497.7 | 450.1 | 612 | 507.1 | 437.9 | 434.3 | 372.7 | 450.7 | 396.7 | 514.6 | 438.6
1989 | 1753 | -6.6 | 0 | 0 | 363.6 | 458.7 | 333 | 333.4 | 434.1 | 73.1 | 16.7 | 121.3 | 4.8 | 226.4 | 2.6 | 380.7 | 425.3 | 503.2 | 676.5 | 687.7 | 684 | 545.3 | 455.9 | 508.8 | 507.6 | 689.9 | 609 | 337.7 | 363.3 | 393.5 | 596.5 | 497.5 | 448.6 | 611.8 | 506.4 | 437.7 | 433.9 | 371.9 | 450.5 | 396.3 | 514.4 | 438.5
1990 | 1754 | -6.6 | 0 | 0 | 363 | 456.2 | 332.5 | 332.5 | 430.5 | 72.9 | 16.7 | 121 | 4.7 | 238.2 | 2.5 | 376.3 | 420.2 | 502.7 | 673.6 | 686.8 | 680.4 | 543.2 | 453.7 | 506.4 | 507.1 | 690.9 | 605.9 | 337.7 | 363.3 | 393.3 | 596 | 497 | 447.5 | 611.6 | 506 | 437.5 | 434.9 | 371 | 450.3 | 395.8 | 514.3 | 438.3
1991 | 1755 | -6.6 | 0 | 0 | 362.4 | 455.2 | 332.1 | 331.6 | 428.5 | 72.7 | 16.7 | 120.7 | 5 | 241 | 2.4 | 371.7 | 415.5 | 502.3 | 670.9 | 685.9 | 677 | 541.7 | 451.5 | 505 | 505.4 | 691.3 | 603.1 | 337.8 | 363.2 | 393.2 | 595.5 | 496.5 | 446.6 | 611.2 | 505 | 437.4 | 435.8 | 370.1 | 450.1 | 395.4 | 514.1 | 438.2
1992 | 1756 | -6.6 | 0 | 0 | 361.7 | 455 | 331.5 | 331 | 427.4 | 72.5 | 16.7 | 120.4 | 4.8 | 235.5 | 2.3 | 367.9 | 411.5 | 501.2 | 668.3 | 684.9 | 673.6 | 538.7 | 449.2 | 502.4 | 503.7 | 691.4 | 600.6 | 337.8 | 363.2 | 393 | 595 | 495.7 | 445.3 | 610.9 | 504.2 | 437.2 | 435.9 | 369.6 | 449.8 | 395 | 513.9 | 438.1
1993 | 1757 | -6.6 | 0 | 0 | 361 | 449.4 | 330.8 | 330.8 | 427.1 | 72.3 | 16.7 | 120.1 | 4.9 | 210.6 | 2.5 | 364.8 | 407.3 | 500.1 | 666 | 683.7 | 670.6 | 536 | 446.8 | 500.4 | 503.8 | 690.9 | 597.8 | 337.9 | 363.2 | 392.8 | 594.4 | 495.2 | 443.9 | 610.5 | 502.9 | 437.1 | 434.9 | 369.2 | 449.4 | 394.6 | 513.7 | 438
1994 | 1758 | -6.6 | 0 | 0 | 360.5 | 445 | 330.4 | 330.1 | 425.8 | 72.1 | 16.7 | 119.8 | 5.1 | 195.4 | 2.8 | 361.3 | 402.9 | 499.3 | 663.4 | 682.4 | 667.4 | 534.2 | 444.5 | 500 | 501 | 691.5 | 594.8 | 338 | 363.1 | 392.6 | 593.9 | 494.7 | 443.1 | 610.2 | 501.9 | 436.9 | 433.3 | 368.2 | 449.1 | 394.2 | 513.5 | 437.9
1995 | 1759 | -6.6 | 0 | 0 | 359.9 | 443.5 | 329.8 | 329.3 | 424.6 | 71.9 | 16.7 | 119.6 | 4.5 | 208.1 | 2.8 | 357.3 | 398.7 | 499 | 660.6 | 681.3 | 664.1 | 530.8 | 442.3 | 500.1 | 499.9 | 690.8 | 592.4 | 338 | 363.1 | 392.4 | 593.4 | 494.4 | 442 | 609.9 | 501.3 | 436.7 | 432.8 | 367.2 | 448.8 | 393.8 | 513.3 | 437.8
1996 | 1760 | -6.6 | 0 | 0 | 359.2 | 447.4 | 329.2 | 328.5 | 423.9 | 71.8 | 16.7 | 119.4 | 4.6 | 211.6 | 3.1 | 353.6 | 394.7 | 497.8 | 657.9 | 680 | 661 | 528.7 | 440.6 | 498.4 | 498.8 | 690.8 | 589.9 | 338 | 363.1 | 392.3 | 593 | 493.6 | 441.2 | 609.6 | 500.6 | 436.6 | 431.3 | 366.2 | 448.7 | 393.4 | 513.1 | 437.7
1997 | 1761 | -6.6 | 0 | 0 | 358.7 | 447.3 | 328.7 | 327.6 | 423.1 | 71.7 | 16.7 | 119.2 | 4.8 | 201.9 | 3.7 | 350.3 | 390.4 | 496.8 | 655.4 | 679 | 657.8 | 525.5 | 438.7 | 497 | 498.6 | 690.6 | 587.3 | 338 | 363 | 392.1 | 592.5 | 493 | 440.3 | 609.3 | 500 | 436.4 | 429.4 | 365.3 | 448.6 | 393 | 512.9 | 437.5
1998 | 1762 | -6.6 | 0 | 0 | 358.3 | 449.8 | 328.3 | 326.9 | 422.4 | 71.6 | 16.7 | 119 | 4.6 | 203.6 | 3.9 | 346.2 | 386.2 | 496.3 | 652.8 | 678 | 654.9 | 521.6 | 437.2 | 495.3 | 498.2 | 690.3 | 585.3 | 338.1 | 363 | 391.9 | 591.8 | 492.4 | 439.2 | 609 | 499.7 | 436.3 | 428.5 | 364.3 | 448.4 | 392.7 | 512.7 | 437.4
1999 | 1763 | -6.6 | 0 | 0 | 357.9 | 453.1 | 327.9 | 326.5 | 421.6 | 71.4 | 16.8 | 118.7 | 4.9 | 217.6 | 4.1 | 342.5 | 382.9 | 495.6 | 650 | 677.3 | 652.4 | 516.4 | 435.7 | 492.9 | 496.9 | 689.7 | 583.3 | 338.1 | 362.9 | 391.7 | 591.2 | 491.6 | 438.1 | 608.7 | 498.8 | 436.1 | 428.9 | 363.3 | 448.1 | 392.3 | 512.5 | 437.2
2000 | 1764 | -6.6 | 0 | 0 | 357.6 | 454.9 | 327.4 | 326 | 421.4 | 71.3 | 16.7 | 118.5 | 4.6 | 213.5 | 4.2 | 339.5 | 379.2 | 495.2 | 647.3 | 676.1 | 650.6 | 511 | 434.7 | 491 | 495.2 | 687.6 | 581 | 338.1 | 362.9 | 391.5 | 590.6 | 490.7 | 437.1 | 608.4 | 497.9 | 435.9 | 428.6 | 362.3 | 447.8 | 391.8 | 512.3 | 437.1
2001 | 1765 | -6.6 | 0 | 0 | 357.2 | 455.2 | 327 | 325.6 | 419.1 | 71.1 | 16.7 | 118.2 | 4.5 | 196.7 | 4.5 | 336.1 | 375.8 | 495 | 644.5 | 675.3 | 649.4 | 510.3 | 432.8 | 490.1 | 493 | 688.3 | 579 | 338.1 | 362.9 | 391.3 | 590 | 490.4 | 436.2 | 608 | 497.3 | 435.8 | 427.6 | 361.4 | 447.7 | 391.4 | 512.1 | 437
2002 | 1766 | -6.6 | 0 | 0 | 356.9 | 451.8 | 326.6 | 325.2 | 417.7 | 71 | 16.8 | 117.9 | 4.8 | 197.2 | 4.8 | 332.1 | 373 | 493.6 | 642 | 674.5 | 647.7 | 508 | 431.5 | 488.5 | 491.5 | 686.3 | 576.8 | 338.1 | 362.8 | 391.1 | 589.4 | 489.8 | 435.1 | 607.5 | 496.5 | 435.6 | 426.1 | 360.9 | 447.5 | 391.1 | 511.9 | 436.8
2003 | 1767 | -6.6 | 0 | 0 | 356.4 | 447.1 | 326.3 | 324.7 | 417.5 | 70.8 | 16.8 | 117.7 | 4.6 | 202.4 | 4.8 | 328.7 | 369.8 | 492.8 | 639.9 | 673.6 | 645.7 | 506 | 430 | 486.6 | 489.8 | 687 | 573.8 | 338.2 | 362.8 | 391 | 588.8 | 489.4 | 434.3 | 607.2 | 495.4 | 435.5 | 424.9 | 360 | 447.3 | 390.7 | 511.6 | 436.7
2004 | 1768 | -6.6 | 0 | 0 | 356.1 | 441.1 | 326 | 324.3 | 416.7 | 70.7 | 16.8 | 117.4 | 4.6 | 201.6 | 4.6 | 325.4 | 367.3 | 492.3 | 638.2 | 672.5 | 643.4 | 500.7 | 428.6 | 485.1 | 488.5 | 687.2 | 571.1 | 338.2 | 362.8 | 390.8 | 588.3 | 488.8 | 433.7 | 607 | 494.4 | 435.3 | 423.6 | 359 | 447.1 | 390.3 | 511.4 | 436.6
2005 | 1769 | -6.6 | 0 | 0 | 355.8 | 437.2 | 325.8 | 323.9 | 415.2 | 70.5 | 16.8 | 117.1 | 4.8 | 212.3 | 4.6 | 321.7 | 364.5 | 491.5 | 636.6 | 671.2 | 640.7 | 498.2 | 427.3 | 483.5 | 489.9 | 686.1 | 568.9 | 338.2 | 362.7 | 390.6 | 587.7 | 488.3 | 432.9 | 606.7 | 493.4 | 435.1 | 422.1 | 357.9 | 446.8 | 389.9 | 511.2 | 436.4
2006 | 1770 | -6.6 | 0 | 0 | 355.6 | 432.5 | 325.5 | 323 | 414.5 | 70.4 | 16.8 | 116.8 | 4.6 | 212.7 | 4.7 | 318.5 | 361.1 | 490.4 | 634.3 | 670.3 | 638 | 495.8 | 425.6 | 483 | 489 | 685.8 | 566.8 | 338.3 | 362.7 | 390.4 | 587.2 | 487.6 | 432.4 | 606.4 | 492.6 | 435 | 421.4 | 357.1 | 446.6 | 389.5 | 511 | 436.3
2007 | 1771 | -6.6 | 0 | 0 | 355.3 | 428.7 | 325.1 | 322.1 | 413.5 | 70.2 | 16.8 | 116.4 | 4.7 | 204.2 | 4.9 | 315.5 | 358 | 489.5 | 632.3 | 669.4 | 635.3 | 494.5 | 424.1 | 482.5 | 488.3 | 686.2 | 564.6 | 338.3 | 362.6 | 390.2 | 586.7 | 486.9 | 431.5 | 606.1 | 492 | 434.8 | 422.3 | 356.4 | 446.4 | 389.1 | 510.8 | 436.1
2008 | 1772 | -6.6 | 0 | 0 | 355.1 | 425.2 | 324.7 | 321.4 | 414.2 | 70.1 | 16.8 | 116.1 | 4.9 | 217.5 | 4.7 | 312.9 | 355.2 | 488.8 | 630.2 | 668.7 | 632.5 | 493.5 | 422.1 | 481.6 | 487.8 | 686.4 | 562.3 | 338.3 | 362.6 | 390 | 586.1 | 485.8 | 430.8 | 605.8 | 491.2 | 434.6 | 423.1 | 355.7 | 446.2 | 388.8 | 510.6 | 436
2009 | 1773 | -6.6 | 0 | 0 | 354.7 | 422.5 | 324.2 | 321 | 414.2 | 70 | 16.8 | 115.8 | 4.7 | 223.1 | 4.4 | 309.8 | 352.5 | 488.2 | 627.9 | 668 | 629.2 | 491.1 | 420.3 | 480.9 | 488.8 | 686.4 | 559.9 | 338.4 | 362.5 | 389.8 | 585.5 | 485 | 430.2 | 605.6 | 491 | 434.5 | 422.2 | 355 | 445.9 | 388.4 | 510.4 | 435.9
2010 | 1774 | -6.6 | 0 | 0 | 354.4 | 420 | 324 | 320.5 | 412.5 | 69.9 | 16.8 | 115.7 | 4.8 | 205.6 | 4.3 | 307.8 | 349.2 | 487.3 | 625.9 | 667.1 | 626.4 | 489.6 | 418.9 | 479.7 | 488.6 | 686 | 558 | 338.4 | 362.4 | 389.6 | 584.9 | 484.9 | 429.4 | 605.3 | 490.3 | 434.3 | 421.7 | 354.2 | 445.6 | 388 | 510.2 | 435.7
2011 | 1775 | -6.6 | 0 | 0 | 354.1 | 417.5 | 323.8 | 320.4 | 411.3 | 69.7 | 16.8 | 115.5 | 4.9 | 197.9 | 4.2 | 305.1 | 346.5 | 486.5 | 623.6 | 667 | 623.8 | 488.9 | 417.4 | 479.3 | 488.8 | 686.1 | 555.6 | 338.4 | 362.4 | 389.4 | 584.3 | 484.6 | 428.7 | 604.9 | 489.5 | 434.1 | 420.8 | 353.3 | 445.5 | 387.6 | 510 | 435.6
2012 | 1776 | -6.6 | 0 | 0 | 353.7 | 414.6 | 323.5 | 320 | 410.8 | 69.6 | 16.8 | 115.3 | 4.3 | 212 | 4.1 | 302.1 | 344.3 | 485.6 | 621.6 | 666.1 | 620.6 | 487.4 | 416.1 | 478.4 | 488 | 686.1 | 553.4 | 338.4 | 362.3 | 389.2 | 583.8 | 483.9 | 428.2 | 604.7 | 488.8 | 434 | 419.4 | 352.5 | 445.3 | 387.2 | 509.8 | 435.5
2013 | 1777 | -6.6 | 0 | 0 | 353.2 | 413.3 | 323.1 | 319.2 | 410.7 | 69.5 | 16.8 | 115.1 | 4.7 | 224.9 | 4 | 299.1 | 341.7 | 484.1 | 619.8 | 665.2 | 617.7 | 485.9 | 414.4 | 477.4 | 487.9 | 686.2 | 551.4 | 338.5 | 362.3 | 389.1 | 583.2 | 483.4 | 427.6 | 604.4 | 488.3 | 433.8 | 419.1 | 352 | 445.1 | 386.9 | 509.6 | 435.3
2014 | 1778 | -6.6 | 0 | 0 | 352.7 | 413.9 | 322.9 | 318.5 | 409.5 | 69.4 | 16.8 | 115 | 4.5 | 220 | 3.7 | 296 | 340.1 | 483 | 617.8 | 664.1 | 614.4 | 484.7 | 413.4 | 476.1 | 488 | 685 | 549.4 | 338.5 | 362.2 | 388.9 | 582.6 | 483 | 426.8 | 604 | 487.9 | 433.7 | 420 | 351.4 | 444.8 | 386.5 | 509.3 | 435.2
2015 | 1779 | -6.6 | 0 | 0 | 352.3 | 414.5 | 322.6 | 317.9 | 408.6 | 69.3 | 16.8 | 114.7 | 4.8 | 226.3 | 3.3 | 293.4 | 337.5 | 482.4 | 615.9 | 663.2 | 611.2 | 483.6 | 412 | 475.4 | 488.2 | 686.4 | 547.7 | 338.5 | 362.2 | 388.7 | 582.1 | 482.5 | 426 | 603.6 | 487.3 | 433.5 | 420.9 | 350.9 | 444.6 | 386.1 | 509.1 | 435
2016 | 1780 | -6.6 | 0 | 0 | 351.8 | 413.2 | 322.3 | 317.4 | 407.9 | 69.2 | 16.8 | 114.6 | 4.7 | 249.5 | 3.4 | 291.3 | 334.8 | 481.1 | 614.2 | 662.6 | 608.4 | 480.7 | 410.8 | 475.1 | 489 | 685 | 545.8 | 338.5 | 362.1 | 388.5 | 581.6 | 482 | 425.4 | 603.4 | 486.1 | 433.3 | 420.7 | 350.3 | 444.4 | 385.7 | 508.9 | 434.9
2017 | 1781 | -6.6 | 0 | 0 | 351.5 | 411.2 | 321.9 | 317 | 408 | 69.1 | 16.8 | 114.4 | 4.7 | 261.7 | 3.1 | 289.8 | 332.3 | 480.2 | 612.6 | 661.7 | 605.9 | 480.7 | 409.5 | 475.7 | 490.5 | 684.9 | 543.4 | 338.5 | 362.1 | 388.3 | 581.1 | 481.6 | 424.7 | 603 | 485.1 | 433.2 | 419.5 | 349.6 | 444.2 | 385.3 | 508.7 | 434.7
2018 | 1782 | -6.6 | 0 | 0 | 351 | 410.4 | 321.7 | 316.8 | 407.9 | 69.1 | 16.8 | 114.2 | 4.6 | 260.5 | 2.8 | 287.6 | 329.9 | 479.1 | 610.7 | 660.9 | 603.3 | 480.2 | 408.2 | 474.6 | 491.3 | 686.1 | 541.1 | 338.5 | 362 | 388.1 | 580.5 | 480.8 | 424.1 | 602.8 | 484.4 | 433 | 418.8 | 349 | 444.1 | 384.9 | 508.5 | 434.6
2019 | 1783 | -6.6 | 0 | 0 | 350.6 | 408.7 | 321.3 | 316.6 | 406.8 | 69 | 16.8 | 113.9 | 4.8 | 250.3 | 3.2 | 285.2 | 327.6 | 477.8 | 608.6 | 660.3 | 600.5 | 478.8 | 406.7 | 473.8 | 491.3 | 686 | 538.7 | 338.5 | 361.9 | 387.9 | 580 | 480.1 | 423.2 | 602.5 | 483.4 | 432.9 | 417.5 | 348.3 | 444 | 384.5 | 508.2 | 434.4
2020 | 1784 | -6.6 | 0 | 0 | 350 | 408.3 | 320.6 | 316.3 | 406.3 | 68.9 | 16.8 | 113.7 | 5 | 236.5 | 2.9 | 282.4 | 325.2 | 477.4 | 606.5 | 659.8 | 597.5 | 477.9 | 405.6 | 473.1 | 490.2 | 685.5 | 537.1 | 338.5 | 361.9 | 387.7 | 579.5 | 479.4 | 422.2 | 602.4 | 482.7 | 432.8 | 415.8 | 347.6 | 443.9 | 384.2 | 508 | 434.3
2021 | 1785 | -6.6 | 0 | 0 | 349.6 | 408.7 | 320.1 | 316 | 407 | 68.8 | 16.8 | 113.5 | 5.2 | 199.9 | 2.8 | 280.1 | 322.1 | 476.7 | 604.2 | 659 | 594.8 | 475.7 | 404.5 | 474 | 490.9 | 685 | 535.1 | 338.5 | 361.8 | 387.5 | 578.9 | 477.8 | 421.4 | 602.4 | 482.2 | 432.7 | 414 | 347.1 | 443.7 | 383.8 | 507.8 | 434.1
2022 | 1786 | -6.6 | 0 | 0 | 349.2 | 408.3 | 320 | 315.5 | 406.5 | 68.7 | 16.8 | 113.3 | 5.1 | 171 | 2.9 | 278.2 | 318.9 | 475.8 | 601.9 | 658.1 | 592.1 | 474.3 | 403.4 | 473.6 | 490.6 | 684.8 | 533.7 | 338.5 | 361.8 | 387.3 | 578.3 | 477.4 | 421 | 602.3 | 481.8 | 432.6 | 412.2 | 346.6 | 443.5 | 383.4 | 507.6 | 434
2023 | 1787 | -6.6 | 0 | 0 | 348.9 | 407.4 | 320 | 314.9 | 405 | 68.6 | 16.8 | 113.1 | 4.9 | 182.9 | 3.3 | 277.2 | 316.6 | 476 | 599.7 | 657 | 589.4 | 472.6 | 402.3 | 472.5 | 490.2 | 684.7 | 531.9 | 338.5 | 361.7 | 387.1 | 577.7 | 476.4 | 420.3 | 602 | 481.3 | 432.4 | 411.2 | 346 | 443.2 | 383 | 507.4 | 433.8
2024 | 1788 | -6.6 | 0 | 0 | 348.6 | 406.2 | 319.8 | 314.5 | 404.7 | 68.5 | 16.8 | 113 | 4.5 | 208.9 | 3.9 | 275.1 | 314 | 475.6 | 597.5 | 656 | 586.7 | 470.4 | 401.1 | 472.3 | 491.1 | 684.6 | 529.7 | 338.5 | 361.6 | 387 | 577.1 | 476 | 419.6 | 601.7 | 480.3 | 432.3 | 411.1 | 345.4 | 443 | 382.7 | 507.1 | 433.7
2025 | 1789 | -6.6 | 0 | 0 | 348.3 | 405.9 | 319.4 | 314.5 | 404.8 | 68.4 | 16.8 | 112.8 | 4.7 | 209.8 | 4.4 | 272.7 | 311.7 | 475.2 | 595.5 | 655.2 | 583.8 | 467.3 | 400.4 | 471.1 | 491.3 | 684.6 | 528.1 | 338.5 | 361.6 | 386.8 | 576.6 | 475.3 | 418.7 | 601.5 | 479.5 | 432.1 | 412.4 | 344.8 | 442.6 | 382.3 | 506.9 | 433.6
2026 | 1790 | -6.6 | 0 | 0 | 348.1 | 406.9 | 319.1 | 314.1 | 404.7 | 68.3 | 16.8 | 112.7 | 4.8 | 207.3 | 4.6 | 270.8 | 309.4 | 474.5 | 593.7 | 654.4 | 580.9 | 464.2 | 400 | 470.2 | 490.8 | 684.6 | 526.3 | 338.5 | 361.5 | 386.6 | 576 | 475.5 | 418 | 601.2 | 478.9 | 432 | 413.2 | 344.2 | 442.3 | 381.9 | 506.7 | 433.4
2027 | 1791 | -6.6 | 0 | 0 | 347.9 | 406.2 | 318.9 | 313.5 | 404.3 | 68.2 | 16.8 | 112.5 | 4.7 | 208.5 | 5 | 268.5 | 307 | 474.5 | 592.1 | 653.5 | 578.1 | 461.2 | 399.3 | 469 | 491.1 | 684 | 524.9 | 338.5 | 361.4 | 386.4 | 575.4 | 475 | 417.4 | 601 | 478.5 | 431.8 | 412.4 | 343.6 | 442 | 381.5 | 506.4 | 433.3
2028 | 1792 | -6.6 | 0 | 0 | 347.6 | 404.6 | 318.6 | 312.9 | 403.6 | 68 | 16.8 | 112.2 | 4.6 | 209.4 | 5.4 | 266.2 | 304.8 | 474.5 | 590.4 | 652.6 | 575.5 | 461.1 | 398.6 | 468.1 | 491.7 | 684 | 523.2 | 338.5 | 361.3 | 386.2 | 574.7 | 474.2 | 417.1 | 600.8 | 477.8 | 431.6 | 412.4 | 343 | 441.7 | 381.2 | 506.2 | 433.2
2029 | 1793 | -6.6 | 0 | 0 | 347.3 | 404.5 | 318.4 | 312.7 | 402.8 | 67.8 | 16.8 | 112 | 4.4 | 215.7 | 5.2 | 263.7 | 302.9 | 473.9 | 588.5 | 652.4 | 573.1 | 458.3 | 397.6 | 467.7 | 491.8 | 682.1 | 521.8 | 338.4 | 361.3 | 386 | 574 | 473.6 | 416.2 | 600.5 | 477 | 431.5 | 412.6 | 342.5 | 441.4 | 380.8 | 506 | 433
2030 | 1794 | -6.6 | 0 | 0 | 347 | 403.3 | 318.4 | 312.5 | 402.3 | 67.7 | 16.8 | 111.8 | 4.7 | 215.6 | 4.9 | 261.8 | 301.2 | 472.7 | 586.6 | 651.7 | 570.8 | 457 | 396.8 | 467.4 | 491.5 | 682.2 | 519.3 | 338.4 | 361.2 | 385.8 | 573.5 | 473.7 | 415.6 | 600.4 | 476.2 | 431.3 | 412.7 | 341.9 | 441.2 | 380.4 | 505.7 | 432.9
2031 | 1795 | -6.6 | 0 | 0 | 346.6 | 400.6 | 318.1 | 312.1 | 403 | 67.5 | 16.8 | 111.5 | 4.8 | 213 | 4.6 | 260 | 299.2 | 471.9 | 584.9 | 651.5 | 568.5 | 454.6 | 395.7 | 466.8 | 490.4 | 682.7 | 517.8 | 338.4 | 361.1 | 385.6 | 572.9 | 472.8 | 415 | 600.4 | 475.3 | 431.2 | 413.1 | 341.5 | 441 | 380.1 | 505.5 | 432.8
2032 | 1796 | -6.6 | 0 | 0 | 346.1 | 399.2 | 317.5 | 311.6 | 402 | 67.4 | 16.8 | 111.4 | 5 | 209.8 | 4.4 | 258.8 | 297.2 | 470.9 | 582.9 | 650.8 | 565.9 | 451.2 | 394.4 | 465.2 | 490.7 | 682.7 | 516.5 | 338.3 | 361.1 | 385.4 | 572.5 | 473 | 414.3 | 600.4 | 474.8 | 431 | 413.1 | 340.9 | 440.8 | 379.7 | 505.3 | 432.6
2033 | 1797 | -6.6 | 0 | 0 | 345.7 | 398.1 | 316.9 | 311.1 | 399.8 | 67.3 | 16.8 | 111.3 | 5.1 | 197.3 | 4.8 | 256.5 | 295.3 | 471.4 | 580.6 | 649.8 | 563.4 | 450.5 | 393.2 | 464.4 | 491.6 | 681.7 | 514.6 | 338.3 | 361 | 385.2 | 572.1 | 473 | 414 | 600 | 474.3 | 430.9 | 412.8 | 340.4 | 440.6 | 379.3 | 505 | 432.5
2034 | 1798 | -6.6 | 0 | 0 | 345.3 | 395.8 | 316.5 | 310.6 | 398.3 | 67.2 | 16.8 | 111.1 | 4.8 | 207.4 | 5.2 | 254.6 | 292.3 | 470.8 | 578.6 | 649.3 | 560.9 | 447 | 391.9 | 463.2 | 490.9 | 682.8 | 513 | 338.3 | 360.9 | 385 | 571.7 | 472.8 | 413.7 | 599.6 | 473.5 | 430.8 | 411.6 | 339.9 | 440.5 | 378.9 | 504.8 | 432.3
2035 | 1799 | -6.6 | 0 | 0 | 344.8 | 395.6 | 316.1 | 310.1 | 397.4 | 67.1 | 16.8 | 110.9 | 4.8 | 211 | 5.2 | 252.9 | 290 | 469.9 | 576.6 | 648.5 | 558.6 | 444.9 | 390.6 | 462.9 | 489.4 | 683.7 | 511.2 | 338.3 | 360.9 | 384.8 | 571.3 | 472.1 | 413.2 | 599.3 | 472.7 | 430.6 | 410.8 | 339.4 | 440.3 | 378.5 | 504.6 | 432.1
2036 | 1800 | -6.6 | 0 | 0 | 344.6 | 397 | 315.6 | 309.5 | 397.9 | 67.1 | 16.8 | 110.7 | 4.4 | 218.1 | 4.8 | 251 | 288.1 | 468.6 | 574.8 | 648 | 556.3 | 444.8 | 389.9 | 462.3 | 487.2 | 683.2 | 509.8 | 338.3 | 360.8 | 384.6 | 570.8 | 471.5 | 412.7 | 599.1 | 472.1 | 430.5 | 410.9 | 338.9 | 440.1 | 378.2 | 504.4 | 432
2037 | 1801 | -6.6 | 0 | 0 | 344.4 | 399.2 | 315.3 | 308.9 | 397.8 | 66.9 | 16.8 | 110.5 | 4.5 | 216.6 | 4.6 | 249 | 286 | 467.2 | 573.1 | 647.3 | 553.9 | 443.6 | 388.8 | 461.6 | 486.7 | 683.6 | 507.9 | 338.3 | 360.7 | 384.4 | 570.4 | 470.8 | 412.1 | 599 | 471.5 | 430.3 | 410.1 | 338.4 | 439.9 | 377.8 | 504.1 | 431.8
2038 | 1802 | -6.6 | 0 | 0 | 344.2 | 397.5 | 315.3 | 308.4 | 397.3 | 66.9 | 16.8 | 110.3 | 4.6 | 208.6 | 4.8 | 247 | 283.7 | 466.7 | 571.1 | 646.4 | 551.6 | 442.8 | 388 | 461.6 | 486.4 | 683 | 506.2 | 338.3 | 360.6 | 384.2 | 570 | 470.1 | 411.6 | 599 | 470.7 | 430.2 | 409.8 | 338 | 439.7 | 377.5 | 503.9 | 431.7
2039 | 1803 | -6.5 | 0 | 0 | 343.9 | 396.4 | 315.1 | 308 | 396.6 | 66.8 | 16.8 | 110.1 | 4.8 | 206 | 5.1 | 246 | 281.7 | 466.4 | 568.7 | 646.2 | 549.6 | 442.2 | 387.2 | 460.7 | 486.3 | 681.7 | 504.6 | 338.3 | 360.5 | 384 | 569.5 | 470.1 | 410.8 | 599 | 470.2 | 430.1 | 408.8 | 337.5 | 439.6 | 377.1 | 503.6 | 431.5
2040 | 1804 | -6.5 | 0 | 0 | 343.6 | 394.7 | 314.7 | 307.7 | 396.6 | 66.7 | 16.8 | 109.9 | 4.3 | 218.1 | 5.6 | 244.9 | 279.4 | 466.7 | 566.1 | 645.8 | 547.5 | 439.6 | 386.3 | 459.3 | 485 | 683.5 | 503 | 338.3 | 360.5 | 383.8 | 569.1 | 469.7 | 410.3 | 598.5 | 469.9 | 430 | 408.3 | 336.9 | 439.4 | 376.7 | 503.4 | 431.4
2041 | 1805 | -6.5 | 0 | 0 | 343.1 | 392.2 | 314.2 | 307.3 | 396.2 | 66.5 | 16.8 | 109.7 | 4.2 | 210.2 | 6 | 243.4 | 277.6 | 466.6 | 564 | 645.5 | 545.1 | 438.8 | 385.6 | 458.7 | 484.4 | 682.6 | 502 | 338.3 | 360.4 | 383.6 | 568.7 | 469.8 | 410 | 598.2 | 469.7 | 429.8 | 407.5 | 336.3 | 439.2 | 376.4 | 503.2 | 431.2
2042 | 1806 | -6.5 | 0 | 0 | 342.7 | 390.1 | 313.7 | 306.8 | 394.6 | 66.3 | 16.8 | 109.4 | 4.2 | 207.2 | 6 | 242 | 276 | 465.8 | 562.1 | 645 | 542.6 | 438.1 | 385.2 | 458.1 | 483.7 | 682.3 | 500.7 | 338.2 | 360.3 | 383.4 | 568.2 | 469.4 | 409.5 | 597.8 | 469.4 | 429.7 | 406.9 | 335.8 | 439 | 376 | 502.9 | 431.1
2043 | 1807 | -6.6 | 0 | 0 | 342.3 | 388.6 | 313.3 | 306.2 | 392.9 | 66.1 | 16.8 | 109.2 | 4.5 | 206.1 | 5.2 | 240.5 | 274 | 465 | 560.2 | 644.4 | 540.2 | 437.2 | 385.1 | 457.5 | 482.9 | 681.8 | 499.3 | 338.2 | 360.2 | 383.2 | 567.8 | 469.3 | 409.2 | 597.4 | 468.6 | 429.6 | 407 | 335.5 | 438.7 | 375.7 | 502.7 | 430.9
2044 | 1808 | -6.4 | 0 | 0 | 341.8 | 390.6 | 312.9 | 305.6 | 391.9 | 65.9 | 16.8 | 109 | 4.6 | 204.5 | 4.8 | 238.7 | 271.8 | 464.9 | 558.1 | 643.6 | 538.1 | 436.9 | 384.1 | 457.5 | 484.1 | 681.9 | 497.6 | 338.2 | 360.1 | 383 | 567.2 | 469.1 | 408.8 | 597 | 467.9 | 429.4 | 406.7 | 335.1 | 438.5 | 375.3 | 502.5 | 430.8
2045 | 1809 | -6.5 | 0 | 0 | 341.4 | 391.9 | 312.5 | 305 | 391.2 | 65.7 | 16.8 | 108.8 | 4.8 | 206.9 | 4.9 | 237.3 | 268.8 | 464.4 | 556.2 | 643 | 536.3 | 436.2 | 383 | 457.3 | 483.6 | 682.2 | 495.9 | 338.2 | 360 | 382.8 | 566.8 | 468.2 | 408.3 | 596.8 | 467.2 | 429.3 | 406.6 | 334.7 | 438.3 | 374.9 | 502.2 | 430.6
2046 | 1810 | -6.6 | 0 | 0 | 340.9 | 391.1 | 312.4 | 304.5 | 390.9 | 65.5 | 16.8 | 108.6 | 5 | 210.3 | 5.1 | 235.8 | 266.3 | 463.9 | 554.6 | 642.3 | 534.3 | 434.4 | 381.6 | 457.8 | 483.6 | 681.6 | 494.2 | 338.2 | 360 | 382.6 | 566.4 | 467.8 | 408 | 596.7 | 466.2 | 429.1 | 406.9 | 334.3 | 438 | 374.6 | 502 | 430.5
2047 | 1811 | -6.5 | 0 | 0 | 340.6 | 389.5 | 312.2 | 304.1 | 389.8 | 65.4 | 16.8 | 108.4 | 4.6 | 200.4 | 6.1 | 235 | 264.5 | 463.3 | 552.5 | 641.5 | 532 | 433.6 | 380.8 | 457.1 | 482.3 | 680.5 | 492.9 | 338.2 | 359.9 | 382.4 | 565.9 | 467.2 | 407.2 | 596.4 | 465.5 | 429 | 406.8 | 333.9 | 437.8 | 374.2 | 501.7 | 430.3
2048 | 1812 | -6.4 | 0 | 0 | 340.2 | 387.8 | 312.1 | 303.6 | 390.2 | 65.2 | 16.8 | 108.2 | 4.5 | 210.7 | 6.3 | 234.4 | 263.3 | 462.3 | 550.5 | 640.7 | 529.9 | 433.2 | 380.2 | 456 | 480.6 | 679.7 | 492 | 338.1 | 359.8 | 382.3 | 565.5 | 466.8 | 406.3 | 596 | 465.4 | 428.8 | 406.4 | 333.5 | 437.7 | 373.9 | 501.5 | 430.2
2049 | 1813 | -6.4 | 0 | 0 | 339.8 | 386.3 | 311.9 | 303.1 | 389.5 | 65.1 | 16.8 | 108 | 4.4 | 223.4 | 5.7 | 232.6 | 260.9 | 460.9 | 548.8 | 640.1 | 527.5 | 431.9 | 379.8 | 455.5 | 480.8 | 680.4 | 490.8 | 338.1 | 359.7 | 382.1 | 565 | 466.1 | 405.9 | 595.7 | 465 | 428.7 | 405.4 | 333.1 | 437.5 | 373.5 | 501.3 | 430
2050 | 1814 | -6.2 | 0 | 0 | 339.4 | 384.5 | 311.6 | 302.6 | 389.7 | 65 | 16.8 | 107.9 | 4.5 | 221.2 | 5.8 | 230.8 | 258.5 | 459.8 | 547.2 | 639.3 | 525.3 | 430.6 | 379.9 | 454.5 | 480.6 | 680.9 | 489.6 | 338.1 | 359.6 | 381.9 | 564.5 | 465.6 | 405.6 | 595.4 | 464.2 | 428.5 | 405.2 | 332.6 | 437.3 | 373.2 | 501 | 429.8
2051 | 1815 | -6 | 0 | 0 | 338.9 | 383 | 311.1 | 302.1 | 389.9 | 64.9 | 16.8 | 107.8 | 4.5 | 212.6 | 6.5 | 229.4 | 256.5 | 459.3 | 545.6 | 638.6 | 523.2 | 427.7 | 379.6 | 454.2 | 480.1 | 680.1 | 488.7 | 338.1 | 359.5 | 381.7 | 564 | 465.4 | 405.1 | 595.1 | 463.1 | 428.4 | 405 | 332.1 | 437.1 | 372.8 | 500.8 | 429.7
2052 | 1816 | -5.9 | 0 | 0 | 338.6 | 381.3 | 310.6 | 301.8 | 388.7 | 64.9 | 16.8 | 107.8 | 4.8 | 211.6 | 6.7 | 228.1 | 254.6 | 459 | 544 | 638.1 | 521.1 | 427.7 | 379.2 | 453.9 | 478.9 | 679.7 | 487.1 | 338.1 | 359.5 | 381.5 | 563.4 | 465.2 | 404.5 | 595 | 462.6 | 428.2 | 404.6 | 331.7 | 436.9 | 372.5 | 500.5 | 429.5
2053 | 1817 | -6 | 0 | 0 | 338.3 | 379.8 | 310.1 | 301.2 | 388.3 | 64.8 | 16.8 | 107.6 | 5.1 | 209.5 | 6.5 | 226.4 | 252.1 | 459.5 | 542 | 637.3 | 518.9 | 426.4 | 379.3 | 453.3 | 477.4 | 679.1 | 485.7 | 338.1 | 359.4 | 381.3 | 562.9 | 465 | 403.7 | 594.7 | 462.3 | 428.1 | 403.9 | 331.3 | 436.7 | 372.1 | 500.3 | 429.4
2054 | 1818 | -6.4 | 0 | 0 | 338 | 378.5 | 309.7 | 300.5 | 387.6 | 64.7 | 16.9 | 107.4 | 4.5 | 218.4 | 6.2 | 225.1 | 250 | 462.3 | 540 | 636.6 | 516.7 | 424.8 | 379.1 | 452.4 | 476.5 | 678.9 | 484.1 | 338 | 359.3 | 381.1 | 562.4 | 464.1 | 403.2 | 594.4 | 462.1 | 427.9 | 404.2 | 330.9 | 436.5 | 371.7 | 500 | 429.2
2055 | 1819 | -6.3 | 0 | 0 | 337.6 | 377.3 | 309.2 | 300.2 | 387.5 | 64.6 | 16.8 | 107.3 | 4 | 227.5 | 5.5 | 224.8 | 248.6 | 462.9 | 537.9 | 636 | 514.5 | 422.6 | 378.7 | 451.9 | 475.2 | 678.3 | 482.9 | 338 | 359.2 | 380.9 | 561.9 | 463.6 | 402.7 | 594.3 | 461.7 | 427.8 | 404.2 | 330.5 | 436.2 | 371.4 | 499.9 | 429.1
2056 | 1820 | -5.7 | 0 | 0 | 337.2 | 376.5 | 308.9 | 299.9 | 387.2 | 64.4 | 16.8 | 107.2 | 4.2 | 185.1 | 6.3 | 222.4 | 246 | 461.3 | 536.1 | 635.3 | 512.3 | 420.8 | 378 | 451.2 | 474.8 | 677.2 | 481.8 | 338 | 359.1 | 380.7 | 561.5 | 463.6 | 401.8 | 594 | 460.9 | 427.6 | 403.6 | 330.2 | 436 | 371.1 | 499.7 | 428.9
2057 | 1821 | -5.8 | 0 | 0 | 336.8 | 375.3 | 308.6 | 299.6 | 388.5 | 64.3 | 16.9 | 107 | 4.7 | 208.3 | 7.7 | 220.1 | 243.6 | 459.9 | 534.6 | 634.9 | 510.1 | 418.9 | 377.4 | 450.3 | 473.6 | 677.5 | 480.1 | 338 | 359 | 380.5 | 561.1 | 463.2 | 401.5 | 593.8 | 460.3 | 427.4 | 404.1 | 329.9 | 435.8 | 370.7 | 499.5 | 428.8
2058 | 1822 | -5.9 | 0 | 0 | 336.4 | 374.1 | 308.3 | 299.3 | 389 | 64.2 | 16.9 | 106.8 | 4.9 | 208.6 | 7.4 | 218 | 240.8 | 459.3 | 533.4 | 634.5 | 507.9 | 415.5 | 376.2 | 450.1 | 472.4 | 676.9 | 479.2 | 337.9 | 358.9 | 380.3 | 560.7 | 463.1 | 401 | 593.6 | 459.6 | 427.3 | 403.7 | 329.5 | 435.6 | 370.3 | 499.2 | 428.6
2059 | 1823 | -6 | 0 | 0 | 336.1 | 372.3 | 307.9 | 298.9 | 387.1 | 64.1 | 16.9 | 106.8 | 4.3 | 218.3 | 7.2 | 217.6 | 238.1 | 458.3 | 532.2 | 634 | 505.9 | 415.5 | 375 | 449 | 472.2 | 676.4 | 477.8 | 337.9 | 358.8 | 380.1 | 560.3 | 462.4 | 400.5 | 593.4 | 459.1 | 427.1 | 404.1 | 329.1 | 435.3 | 370 | 499 | 428.5
2060 | 1824 | -5.7 | 0 | 0 | 335.9 | 370.6 | 307.8 | 298.7 | 385.3 | 63.9 | 16.9 | 106.6 | 4.3 | 202.1 | 6.7 | 216.6 | 235.3 | 456.9 | 531 | 633.3 | 503.9 | 414.2 | 374.1 | 447.8 | 472.5 | 677.3 | 476.4 | 337.9 | 358.7 | 379.9 | 559.9 | 461.1 | 399.8 | 593.3 | 458.5 | 426.9 | 404.4 | 328.8 | 435.1 | 369.7 | 498.7 | 428.3
2061 | 1825 | -5.6 | 0 | 0 | 335.7 | 368.8 | 307.4 | 298.5 | 383.8 | 63.8 | 16.9 | 106.5 | 4.3 | 233.1 | 6 | 215.6 | 233.6 | 456.1 | 529.7 | 632.5 | 502 | 411.1 | 373.7 | 446.6 | 471.6 | 676.2 | 475.1 | 337.8 | 358.6 | 379.7 | 559.4 | 460 | 399.6 | 593.3 | 458.2 | 426.8 | 403.4 | 328.4 | 434.9 | 369.3 | 498.5 | 428.2
2062 | 1826 | -5.9 | 0 | 0 | 335.4 | 367.5 | 306.9 | 298.1 | 382.6 | 63.6 | 16.9 | 106.4 | 4.5 | 232.5 | 5.3 | 215.4 | 231.6 | 455.3 | 528.3 | 631.9 | 500.3 | 409.6 | 372.8 | 445.5 | 470.9 | 675.4 | 473.9 | 337.8 | 358.5 | 379.5 | 558.9 | 459.3 | 399.2 | 593.1 | 457.3 | 426.7 | 403.4 | 328 | 434.7 | 369 | 498.2 | 428
2063 | 1827 | -5.9 | 0 | 0 | 335 | 366.5 | 306.3 | 297.7 | 381.9 | 63.5 | 16.9 | 106.2 | 4.8 | 193.8 | 6.1 | 214.2 | 229.7 | 454.3 | 526.9 | 631.4 | 498.7 | 408.8 | 372.9 | 444.7 | 469 | 675.2 | 472.8 | 337.7 | 358.4 | 379.3 | 558.4 | 459.1 | 398.4 | 592.9 | 456.6 | 426.5 | 403.4 | 327.6 | 434.5 | 368.6 | 498 | 427.8
2064 | 1828 | -5.9 | 0 | 0 | 334.7 | 365.2 | 306.1 | 297.4 | 382.2 | 63.3 | 16.9 | 106 | 5.3 | 217.6 | 6.9 | 212.6 | 228 | 453.6 | 525.3 | 630.8 | 496.7 | 408.9 | 372.5 | 443.3 | 468.4 | 675.5 | 471.4 | 337.7 | 358.3 | 379.1 | 557.9 | 459 | 397.7 | 592.8 | 455.9 | 426.4 | 402.8 | 327.2 | 434.4 | 368.3 | 497.7 | 427.7
2065 | 1829 | -6.1 | 0 | 0 | 334.3 | 364.7 | 306.1 | 297.2 | 382.9 | 63.1 | 16.9 | 105.8 | 5.2 | 198.1 | 7.2 | 211.5 | 226.1 | 452.6 | 523.6 | 630.2 | 494.7 | 407.8 | 371.9 | 441.6 | 468.1 | 675.9 | 470.2 | 337.7 | 358.2 | 378.9 | 557.4 | 458.8 | 397.4 | 592.6 | 455.3 | 426.3 | 403.3 | 326.8 | 434.3 | 367.9 | 497.5 | 427.5
2066 | 1830 | -6.1 | 0 | 0 | 334.1 | 364.2 | 305.9 | 297 | 382.6 | 63 | 16.9 | 105.7 | 6.1 | 200.4 | 7.3 | 210.1 | 224.4 | 451.4 | 522.1 | 629.8 | 492.9 | 404.9 | 371.9 | 439.5 | 468.1 | 675.9 | 469 | 337.6 | 358.2 | 378.7 | 557 | 458.6 | 396.9 | 592.4 | 454.9 | 426.1 | 403 | 326.5 | 434.2 | 367.6 | 497.2 | 427.3
2067 | 1831 | -6.1 | 0 | 0 | 333.7 | 363.3 | 305.6 | 296.7 | 382.2 | 62.9 | 16.9 | 105.6 | 5.8 | 212.4 | 7.1 | 208.6 | 222.2 | 450.7 | 520.5 | 629.2 | 491.1 | 403 | 371.8 | 437.8 | 466.8 | 675.5 | 468 | 337.6 | 358.1 | 378.5 | 556.4 | 458.3 | 396.4 | 592.1 | 454.1 | 426 | 403.4 | 326.1 | 434.1 | 367.3 | 497 | 427.1
2068 | 1832 | -6 | 0 | 0 | 333.2 | 362.5 | 305.2 | 296.4 | 382 | 62.8 | 16.9 | 105.5 | 5.4 | 229.3 | 6.2 | 206.6 | 220.5 | 450.2 | 519.2 | 628.6 | 489.3 | 403.4 | 371.4 | 436.4 | 466.5 | 675.3 | 466.6 | 337.6 | 358 | 378.3 | 555.9 | 457.6 | 395.8 | 591.8 | 453.6 | 425.9 | 402.6 | 325.7 | 434.1 | 366.9 | 496.8 | 427
2069 | 1833 | -6 | 0 | 0 | 332.7 | 361.5 | 305.1 | 295.9 | 382.4 | 62.7 | 16.9 | 105.3 | 5.2 | 212 | 6.4 | 205.6 | 218.2 | 449.3 | 517.7 | 628 | 487.6 | 402.5 | 369.7 | 435.6 | 465.9 | 675 | 465.3 | 337.5 | 357.9 | 378.1 | 555.5 | 457.5 | 395.2 | 591.6 | 453.4 | 425.8 | 401.2 | 325.4 | 434.1 | 366.6 | 496.5 | 426.8
2070 | 1834 | -5.9 | 0 | 0 | 332.5 | 360.5 | 304.8 | 295.3 | 382.4 | 62.6 | 16.9 | 105.1 | 5.2 | 194.6 | 7.2 | 204.4 | 215.5 | 449.2 | 516.2 | 627.6 | 486.1 | 402.2 | 368.8 | 434.5 | 467.2 | 674.6 | 464.3 | 337.5 | 357.8 | 377.9 | 555 | 457.4 | 394.6 | 591.5 | 453.2 | 425.7 | 399.8 | 325 | 434.1 | 366.2 | 496.3 | 426.6
2071 | 1835 | -5.7 | 0 | 0 | 332.3 | 359.7 | 304.4 | 294.9 | 381.2 | 62.5 | 16.9 | 104.9 | 5.1 | 192.4 | 7.3 | 202.7 | 213.1 | 449.6 | 514.9 | 626.9 | 484.4 | 400.6 | 368.3 | 432.8 | 466.4 | 674.7 | 463.2 | 337.4 | 357.7 | 377.7 | 554.6 | 457 | 394.2 | 591.5 | 452.6 | 425.6 | 398.2 | 324.7 | 434 | 365.9 | 496 | 426.4
2072 | 1836 | -5.8 | 0 | 0 | 331.9 | 359.3 | 304.2 | 294.7 | 380.3 | 62.4 | 16.9 | 104.7 | 5 | 194.4 | 6.9 | 201.6 | 210.4 | 448.5 | 513.6 | 626.4 | 482.6 | 398 | 367.4 | 431.1 | 466 | 674 | 461.4 | 337.4 | 357.6 | 377.5 | 554.2 | 455.8 | 393.9 | 591.4 | 451.9 | 425.5 | 398.1 | 324.2 | 433.8 | 365.6 | 495.8 | 426.3
2073 | 1837 | -5.9 | 0 | 0 | 331.6 | 359.2 | 303.9 | 294.5 | 380.8 | 62.4 | 16.9 | 104.6 | 4.8 | 207.2 | 7.3 | 200.4 | 208.9 | 447.1 | 512.5 | 626.2 | 480.6 | 397.9 | 367 | 429.4 | 466 | 673.5 | 460.5 | 337.3 | 357.5 | 377.3 | 553.8 | 455.1 | 393.4 | 591.2 | 451.6 | 425.4 | 397.8 | 323.8 | 433.6 | 365.2 | 495.5 | 426.1
2074 | 1838 | -6 | 0 | 0 | 331.4 | 358.6 | 303.8 | 294.3 | 380.7 | 62.2 | 16.9 | 104.5 | 4.6 | 215.4 | 7.3 | 199.2 | 207.1 | 445.8 | 511.3 | 625.7 | 478.7 | 394.4 | 366.4 | 427.5 | 465.5 | 673.1 | 459.1 | 337.3 | 357.4 | 377.1 | 553.3 | 455.3 | 393 | 590.9 | 450.7 | 425.3 | 397.8 | 323.5 | 433.5 | 364.9 | 495.3 | 425.9
2075 | 1839 | -6 | 0 | 0 | 331 | 357.9 | 303.7 | 293.8 | 379.2 | 62.2 | 16.9 | 104.3 | 5.4 | 216.9 | 7 | 198 | 205.3 | 444.9 | 510.2 | 625.3 | 477.1 | 396.3 | 365.4 | 426.1 | 464.8 | 673.8 | 458.2 | 337.2 | 357.3 | 377 | 552.9 | 455.3 | 392.7 | 590.5 | 450 | 425.2 | 397.7 | 323.2 | 433.4 | 364.6 | 495 | 425.8
2076 | 1840 | -6 | 0 | 0 | 330.7 | 357.3 | 303.4 | 293.3 | 377.9 | 62.1 | 16.9 | 104.3 | 5.3 | 265 | 6.8 | 196.9 | 202.9 | 444.7 | 508.8 | 624.8 | 475.4 | 396.2 | 364.7 | 424.4 | 464.2 | 674 | 456.4 | 337.2 | 357.2 | 376.8 | 552.5 | 455.3 | 392.6 | 590.3 | 449.5 | 425.1 | 397.6 | 322.9 | 433.3 | 364.2 | 494.8 | 425.6
2077 | 1841 | -6 | 0 | 0 | 330.5 | 356.9 | 303.2 | 292.9 | 377 | 62 | 16.9 | 104.2 | 5.2 | 256 | 6 | 195.6 | 201.2 | 444.4 | 507.2 | 624.4 | 473.7 | 396.1 | 364.1 | 422.5 | 463.6 | 673.1 | 454.6 | 337.1 | 357.1 | 376.6 | 552 | 454.3 | 391.8 | 590.1 | 449.6 | 425 | 397.2 | 322.6 | 433 | 363.9 | 494.5 | 425.4
2078 | 1842 | -5.6 | 0 | 0 | 330.2 | 356.2 | 302.9 | 292.7 | 376.3 | 61.9 | 16.9 | 104.1 | 5.2 | 211.9 | 6.3 | 194.1 | 199.5 | 443.8 | 505.8 | 623.9 | 471.8 | 395.1 | 363.1 | 421 | 462.4 | 673.2 | 453.4 | 337.1 | 357 | 376.4 | 551.6 | 454.4 | 391.5 | 589.8 | 448.7 | 424.9 | 397.1 | 322.2 | 432.8 | 363.6 | 494.3 | 425.2
2079 | 1843 | -5.7 | 0 | 0 | 330 | 355.9 | 302.7 | 292.3 | 375.2 | 61.8 | 16.9 | 104 | 5.2 | 220.2 | 6.8 | 193 | 197.6 | 443 | 504.2 | 623.4 | 470 | 395.2 | 362.4 | 419.8 | 461.6 | 672.5 | 452.4 | 337 | 356.9 | 376.2 | 551 | 454.4 | 391.3 | 589.8 | 448.2 | 424.8 | 397.1 | 321.9 | 432.7 | 363.2 | 494 | 425
2080 | 1844 | -6.1 | 0 | 0 | 329.7 | 355.3 | 302.5 | 292 | 374.2 | 61.7 | 16.9 | 103.8 | 5 | 218.8 | 6.8 | 192.4 | 195.9 | 442.4 | 502.5 | 622.7 | 468.3 | 394.6 | 361.5 | 419.2 | 462.4 | 673.1 | 451.3 | 337 | 356.8 | 376 | 550.6 | 453.6 | 390.8 | 589.9 | 447.9 | 424.7 | 397.3 | 321.5 | 432.5 | 362.9 | 493.8 | 424.9
2081 | 1845 | -6.1 | 0 | 0 | 329.5 | 354.9 | 302.1 | 291.8 | 373.7 | 61.6 | 16.9 | 103.6 | 5 | 219.4 | 5.7 | 191.4 | 194.6 | 441.6 | 500.8 | 622.1 | 466.6 | 393.3 | 360.7 | 417.8 | 461.9 | 672.1 | 450.4 | 336.9 | 356.7 | 375.8 | 550.2 | 453 | 390 | 589.8 | 447 | 424.6 | 397 | 321.1 | 432.4 | 362.5 | 493.5 | 424.7
2082 | 1846 | -5.6 | 0 | 0 | 329.3 | 354.2 | 301.5 | 291.5 | 373.3 | 61.5 | 16.9 | 103.4 | 5.1 | 239 | 4.5 | 189.9 | 192.7 | 440.7 | 499.3 | 621.9 | 465.1 | 392 | 360.5 | 415.7 | 460.8 | 671.9 | 448.9 | 336.9 | 356.6 | 375.6 | 549.8 | 453 | 389.2 | 589.5 | 446 | 424.5 | 396.4 | 320.7 | 432.2 | 362.2 | 493.3 | 424.5
2083 | 1847 | -5.4 | 0 | 0 | 329 | 353.5 | 301.2 | 291.3 | 372.9 | 61.5 | 16.9 | 103.3 | 5.3 | 236.9 | 4.7 | 188.5 | 190.9 | 440.5 | 497.7 | 621.6 | 463.5 | 390 | 359.6 | 413.8 | 459.4 | 671.5 | 448 | 336.8 | 356.5 | 375.4 | 549.3 | 452.8 | 388.7 | 589.2 | 445.5 | 424.4 | 395.4 | 320.2 | 432 | 361.9 | 493 | 424.4
2084 | 1848 | -5.5 | 0 | 0 | 328.7 | 352.9 | 301.2 | 291 | 372.6 | 61.4 | 16.9 | 103.1 | 5 | 220.4 | 5.5 | 187.3 | 189.4 | 439.8 | 496.3 | 621.1 | 462 | 386.8 | 358.9 | 412.1 | 459.6 | 671 | 446.8 | 336.8 | 356.4 | 375.2 | 548.8 | 451.9 | 388.1 | 589 | 445.2 | 424.3 | 394.9 | 319.8 | 431.9 | 361.5 | 492.8 | 424.2
2085 | 1849 | -5.4 | 0 | 0 | 328.3 | 352.5 | 301.1 | 290.7 | 372 | 61.3 | 16.9 | 102.9 | 4.6 | 230.9 | 5.9 | 186 | 188.2 | 439.8 | 494.8 | 620.7 | 460.2 | 387.3 | 358.2 | 410.5 | 458.4 | 670.6 | 445.6 | 336.7 | 356.3 | 375 | 548.3 | 451.4 | 387.7 | 588.8 | 445 | 424.2 | 395 | 319.7 | 431.7 | 361.2 | 492.5 | 424
2086 | 1850 | -5.5 | 0 | 0 | 328 | 351.6 | 301 | 290.3 | 371.3 | 61.3 | 16.9 | 102.8 | 4.7 | 238.3 | 5.2 | 185.1 | 187.1 | 440.2 | 493.2 | 620.2 | 458.6 | 383.6 | 357.3 | 408.4 | 457 | 670.6 | 444.4 | 336.7 | 356.2 | 374.8 | 548 | 451.7 | 387.1 | 588.5 | 444.4 | 424.1 | 394.2 | 319.2 | 431.5 | 360.9 | 492.3 | 423.9
2087 | 1851 | -5.5 | 0 | 0 | 327.6 | 350.7 | 300.7 | 290 | 371 | 61.1 | 16.9 | 102.6 | 5 | 245.9 | 4.7 | 184.2 | 186 | 440.1 | 491.6 | 619.6 | 456.9 | 382.8 | 356.7 | 406.7 | 457 | 670.2 | 443 | 336.7 | 356.1 | 374.6 | 547.6 | 451.4 | 386.6 | 588.2 | 443.6 | 424 | 393.8 | 318.9 | 431.4 | 360.6 | 492 | 423.7
2088 | 1852 | -5.5 | 0 | 0 | 327.3 | 350.4 | 300.2 | 289.8 | 371.3 | 61.1 | 16.9 | 102.5 | 4.6 | 243.8 | 4.5 | 183.3 | 185 | 439.4 | 490.2 | 619.3 | 455.3 | 382.2 | 356.6 | 403.8 | 457.2 | 670.3 | 442.6 | 336.6 | 356 | 374.4 | 547.2 | 450.9 | 386.2 | 588.1 | 443.3 | 423.9 | 393.3 | 318.8 | 431.2 | 360.3 | 491.8 | 423.5
2089 | 1853 | -5.7 | 0 | 0 | 327.1 | 350.2 | 299.7 | 289.5 | 370.8 | 61 | 16.9 | 102.3 | 4.6 | 242.9 | 4.3 | 182.2 | 183.9 | 439.8 | 489 | 618.7 | 453.7 | 382 | 356 | 401.6 | 454.9 | 669.8 | 441.5 | 336.6 | 355.9 | 374.2 | 546.8 | 450.8 | 385.8 | 588.2 | 443.1 | 423.8 | 393 | 318.3 | 431 | 359.9 | 491.5 | 423.4
2090 | 1854 | -5.6 | 0 | 0 | 326.8 | 349.5 | 299.4 | 289.2 | 370 | 60.9 | 16.9 | 102.2 | 4.8 | 237.4 | 4.6 | 181.5 | 182.6 | 439.8 | 487.9 | 618.3 | 452.2 | 384.4 | 355.5 | 399.4 | 453.8 | 670.1 | 440.6 | 336.5 | 355.8 | 374 | 546.5 | 449.6 | 385.6 | 588.2 | 442.6 | 423.7 | 392.7 | 318 | 430.9 | 359.6 | 491.3 | 423.2
2091 | 1855 | -5.5 | 0 | 0 | 326.6 | 348.9 | 299.1 | 289 | 369.8 | 60.9 | 16.9 | 102.1 | 4.9 | 242 | 5.1 | 180.8 | 181.3 | 438.9 | 486.7 | 617.9 | 450.7 | 382.6 | 355 | 397.8 | 453.1 | 670.2 | 439.5 | 336.5 | 355.7 | 373.8 | 546 | 448.9 | 385 | 588.1 | 441.9 | 423.6 | 391.9 | 317.7 | 430.7 | 359.3 | 491 | 423
2092 | 1856 | -5.5 | 0 | 0 | 326.3 | 347.9 | 298.7 | 288.7 | 370 | 60.8 | 16.9 | 102 | 5.2 | 258.2 | 5.6 | 179.7 | 179.9 | 438 | 485.4 | 617.5 | 449 | 379.2 | 355.8 | 394.9 | 451.3 | 669.1 | 438.5 | 336.4 | 355.6 | 373.6 | 545.6 | 448.9 | 384.8 | 588 | 441.5 | 423.5 | 391.4 | 317.4 | 430.6 | 359 | 490.8 | 422.8
2093 | 1857 | -5.5 | 0 | 0 | 326 | 347.7 | 298.3 | 288.5 | 370.7 | 60.7 | 16.9 | 101.8 | 5.1 | 246.2 | 5.9 | 178.7 | 178.9 | 436.9 | 484 | 617.2 | 447.3 | 379.9 | 356.2 | 393.1 | 449.9 | 668.3 | 437.8 | 336.4 | 355.5 | 373.4 | 545.2 | 448.5 | 384.2 | 587.8 | 440.6 | 423.4 | 391.2 | 317.1 | 430.4 | 358.7 | 490.5 | 422.7
2094 | 1858 | -5.6 | 0 | 0 | 325.8 | 347.1 | 298.1 | 288.2 | 369.7 | 60.6 | 16.9 | 101.6 | 5 | 242 | 6.2 | 177.5 | 177.7 | 436.2 | 482.9 | 616.7 | 445.6 | 382.8 | 356.4 | 390.6 | 450.3 | 668 | 436.9 | 336.3 | 355.3 | 373.3 | 544.7 | 448.8 | 384.1 | 587.4 | 440.1 | 423.3 | 390.6 | 316.8 | 430.3 | 358.3 | 490.2 | 422.5
2095 | 1859 | -5.5 | 0 | 0 | 325.5 | 346.7 | 297.7 | 287.9 | 369 | 60.5 | 16.9 | 101.5 | 4.9 | 244.8 | 6.1 | 176.6 | 176.1 | 435.7 | 481.8 | 616.1 | 444.1 | 381.7 | 356.6 | 389.2 | 449.2 | 667.9 | 436 | 336.3 | 355.2 | 373.1 | 544.2 | 448.5 | 383.6 | 587.2 | 440.1 | 423.2 | 389.9 | 316.4 | 430.1 | 358 | 490 | 422.3
2096 | 1860 | -5.6 | 0 | 0 | 325.1 | 346.1 | 297.2 | 287.8 | 369 | 60.4 | 16.9 | 101.3 | 4.8 | 232.4 | 5.9 | 175.8 | 175 | 435 | 480.5 | 615.9 | 442.7 | 380.5 | 356.9 | 387.2 | 448.3 | 667.9 | 435.2 | 336.2 | 355.1 | 372.9 | 543.8 | 448.2 | 383 | 587 | 440 | 423.2 | 389.5 | 316.1 | 430 | 357.7 | 489.7 | 422.1
2097 | 1861 | -5.7 | 0 | 0 | 324.7 | 345.5 | 296.7 | 287.7 | 367.9 | 60.3 | 16.9 | 101.1 | 4.7 | 234.7 | 5.6 | 174.5 | 174.1 | 434.7 | 479.3 | 615.5 | 441.4 | 381.1 | 356.4 | 385.4 | 448 | 667.3 | 434.2 | 336.2 | 355 | 372.7 | 543.4 | 447.5 | 382.4 | 586.6 | 439.9 | 423.1 | 389.1 | 315.8 | 429.8 | 357.4 | 489.5 | 422
2098 | 1862 | -5.6 | 0 | 0 | 324.3 | 344.9 | 296.2 | 287.6 | 367 | 60.2 | 16.9 | 100.9 | 4.7 | 239.7 | 5.6 | 173.6 | 173.5 | 434.7 | 478.2 | 615 | 439.9 | 384.4 | 355.7 | 384.4 | 447.6 | 666.9 | 433.2 | 336.1 | 354.9 | 372.5 | 543.1 | 446.8 | 382.2 | 586.4 | 439.8 | 423 | 389.3 | 315.5 | 429.7 | 357.1 | 489.2 | 421.8
2099 | 1863 | -5.5 | 0 | 0 | 324 | 344.5 | 295.7 | 287.5 | 366 | 60.1 | 17 | 100.8 | 4.4 | 241.3 | 5.6 | 172.6 | 172.2 | 434.2 | 477.3 | 614.7 | 438.4 | 383.8 | 355.3 | 381.8 | 447.6 | 667.3 | 432.1 | 336.1 | 354.8 | 372.3 | 542.7 | 446.4 | 382.3 | 586.3 | 439.1 | 422.9 | 389.4 | 315.5 | 429.7 | 356.8 | 489 | 421.6
2100 | 1864 | -5.5 | 0 | 0 | 323.8 | 344.1 | 295.4 | 287.2 | 365.4 | 60.1 | 17 | 100.6 | 4.8 | 236.2 | 5 | 171.8 | 171.1 | 433.3 | 476.1 | 614.3 | 437 | 382.4 | 354.4 | 380.1 | 447.6 | 666.3 | 430.8 | 336 | 354.7 | 372.1 | 542.4 | 446 | 381.9 | 586.2 | 438.3 | 422.9 | 389.6 | 314.9 | 429.6 | 356.5 | 488.7 | 421.4
2101 | 1865 | -5.3 | 0 | 0 | 323.6 | 343.9 | 295.1 | 287 | 366.3 | 60 | 17 | 100.5 | 4.9 | 231.7 | 4.1 | 171.2 | 170.2 | 432.5 | 474.8 | 613.7 | 435.3 | 381.6 | 353 | 379.2 | 447.1 | 666.6 | 430 | 336 | 354.6 | 371.9 | 542 | 445.9 | 381.3 | 585.9 | 437.4 | 422.8 | 389.6 | 314.7 | 429.5 | 356.2 | 488.5 | 421.2
2102 | 1866 | -5.2 | 0 | 0 | 323.4 | 343.7 | 294.9 | 286.8 | 365.8 | 59.9 | 17 | 100.3 | 4.8 | 234.4 | 4.6 | 170.2 | 168.4 | 431.9 | 473.8 | 613.3 | 433.9 | 380.4 | 351.8 | 377.5 | 447.9 | 667.3 | 428.8 | 335.9 | 354.5 | 371.7 | 541.6 | 445.7 | 380.5 | 585.7 | 436.8 | 422.7 | 388.9 | 314.5 | 429.4 | 355.9 | 488.2 | 421.1
2103 | 1867 | -5.3 | 0 | 0 | 323.2 | 343.4 | 294.8 | 286.6 | 364.9 | 59.9 | 17 | 100.2 | 5.1 | 224.1 | 5.3 | 169.2 | 166.7 | 431.4 | 472.6 | 613.1 | 432.7 | 377.8 | 350.6 | 376.6 | 448.2 | 666.5 | 427.3 | 335.8 | 354.4 | 371.5 | 541.1 | 445 | 379.9 | 585.6 | 436.4 | 422.6 | 388.6 | 313.9 | 429.1 | 355.6 | 487.9 | 420.9
2104 | 1868 | -5.3 | 0 | 0 | 322.9 | 342.9 | 294.6 | 286.3 | 364.2 | 59.8 | 17 | 100 | 4.9 | 233.1 | 5.4 | 168.3 | 165.5 | 431.1 | 471.3 | 612.6 | 431.3 | 375.7 | 349.4 | 375.2 | 448.7 | 666 | 426.2 | 335.8 | 354.3 | 371.3 | 540.7 | 444 | 379.8 | 585.5 | 436.1 | 422.5 | 388.8 | 313.7 | 429 | 355.2 | 487.7 | 420.7
2105 | 1869 | -5.2 | 0 | 0 | 322.6 | 342.7 | 294.7 | 285.9 | 363.6 | 59.8 | 17 | 99.9 | 4.9 | 240.5 | 5 | 167.6 | 164.9 | 430.7 | 470.2 | 612 | 430 | 374.3 | 348.7 | 373 | 449 | 665.6 | 425.5 | 335.7 | 354.2 | 371.2 | 540.3 | 443.4 | 379.5 | 585.5 | 435.5 | 422.4 | 388.3 | 313.4 | 428.8 | 354.9 | 487.4 | 420.5
2106 | 1870 | -5.4 | 0 | 0 | 322.3 | 342.1 | 294.6 | 285.7 | 362.9 | 59.7 | 17 | 99.8 | 4.3 | 246.2 | 4.6 | 166.5 | 163.8 | 430.3 | 469 | 611.4 | 428.7 | 373.7 | 348.1 | 370.8 | 448.9 | 664.9 | 424.8 | 335.7 | 354.1 | 371 | 539.8 | 443 | 378.7 | 585.4 | 434.9 | 422.3 | 388.5 | 313.1 | 428.7 | 354.6 | 487.2 | 420.3
2107 | 1871 | -5.6 | 0 | 0 | 322.1 | 341.8 | 294.3 | 285.5 | 362.2 | 59.6 | 17 | 99.7 | 5 | 250 | 4.8 | 166.1 | 161.7 | 428.7 | 467.8 | 610.8 | 427.6 | 375.6 | 347.1 | 369 | 448 | 664 | 423.8 | 335.6 | 354 | 370.8 | 539.3 | 442 | 378.3 | 585.3 | 434.5 | 422.2 | 388.3 | 312.8 | 428.6 | 354.3 | 486.9 | 420.2
2108 | 1872 | -5.4 | 0 | 0 | 322 | 341.3 | 293.7 | 285.2 | 361.6 | 59.5 | 17 | 99.5 | 4.9 | 243.1 | 4.4 | 165.3 | 159.8 | 427.1 | 466.4 | 610.1 | 426.2 | 373.2 | 346.5 | 367.8 | 448 | 664.5 | 422.6 | 335.6 | 353.8 | 370.6 | 538.8 | 441.5 | 377.8 | 585.1 | 434.2 | 422.1 | 387 | 312.6 | 428.5 | 354 | 486.7 | 420
2109 | 1873 | -5.2 | 0 | 0 | 321.8 | 340.4 | 293.6 | 284.8 | 361.4 | 59.5 | 17 | 99.4 | 4.8 | 240.2 | 3.8 | 164.9 | 158.4 | 426.3 | 465.1 | 609.7 | 425.1 | 372.5 | 345.9 | 366.6 | 448 | 664.5 | 421.9 | 335.5 | 353.7 | 370.4 | 538.2 | 441.6 | 377.7 | 585 | 433.9 | 422 | 387.1 | 312.4 | 428.3 | 353.7 | 486.4 | 419.8
2110 | 1874 | -4.9 | 0 | 0 | 321.5 | 339.8 | 293.5 | 284.4 | 361 | 59.4 | 17 | 99.3 | 4.9 | 239.4 | 3.5 | 164.1 | 157.2 | 425.8 | 464 | 609.2 | 423.9 | 371.7 | 345.2 | 365.6 | 447.7 | 663.9 | 420.8 | 335.5 | 353.6 | 370.2 | 537.7 | 440.6 | 376.9 | 584.8 | 433.4 | 422 | 387.2 | 312.3 | 428.2 | 353.4 | 486.1 | 419.6
2111 | 1875 | -4.9 | 0 | 0 | 321.4 | 339.7 | 293.2 | 284.3 | 360.4 | 59.3 | 17 | 99.2 | 4.8 | 236.1 | 3.4 | 163.2 | 156.2 | 425.3 | 462.8 | 608.7 | 422.6 | 371.2 | 344.1 | 364.2 | 446.1 | 663.9 | 420 | 335.4 | 353.5 | 370 | 537.4 | 439.9 | 376 | 584.9 | 432.5 | 421.9 | 386.6 | 311.9 | 428 | 353.1 | 485.9 | 419.5
2112 | 1876 | -5 | 0 | 0 | 321.3 | 339.3 | 292.8 | 284.2 | 359.8 | 59.2 | 17 | 99.1 | 4.9 | 230.8 | 3.3 | 162.6 | 155.8 | 424.5 | 461.8 | 608.4 | 421.1 | 370.1 | 343.3 | 362 | 444.4 | 662.4 | 418.9 | 335.4 | 353.4 | 369.8 | 537.1 | 439.7 | 375.7 | 584.8 | 432.3 | 421.8 | 386.2 | 311.6 | 427.9 | 352.8 | 485.6 | 419.3
2113 | 1877 | -5 | 0 | 0 | 321.1 | 338.8 | 292.4 | 283.9 | 359.4 | 59.1 | 17 | 99 | 5 | 228.2 | 3.1 | 161.9 | 155.1 | 423.7 | 460.6 | 608.1 | 419.7 | 370 | 342 | 361 | 443.1 | 662.5 | 417.6 | 335.3 | 353.3 | 369.6 | 536.7 | 439.3 | 375.5 | 584.6 | 432.2 | 421.7 | 385.9 | 311.6 | 427.7 | 352.5 | 485.4 | 419.1
2114 | 1878 | -5 | 0 | 0 | 320.9 | 338.3 | 292.1 | 283.8 | 359.1 | 59 | 17 | 98.9 | 4.8 | 228 | 3.1 | 161.7 | 154.1 | 422.6 | 459.4 | 607.8 | 418.6 | 369.6 | 340.8 | 360.4 | 442.5 | 663 | 416.4 | 335.2 | 353.2 | 369.4 | 536.3 | 438.4 | 375 | 584.5 | 431.8 | 421.6 | 385.1 | 311.1 | 427.5 | 352.2 | 485.1 | 418.9
2115 | 1879 | -5.1 | 0 | 0 | 320.7 | 337.7 | 291.8 | 283.6 | 358.7 | 58.9 | 17 | 98.8 | 5 | 242 | 3.4 | 161.4 | 153.4 | 421.2 | 458.4 | 607.5 | 417.2 | 369.5 | 340 | 358.8 | 441.4 | 663 | 415.8 | 335.2 | 353.1 | 369.2 | 536 | 438.5 | 374.1 | 584.1 | 431.1 | 421.5 | 385.2 | 310.8 | 427.4 | 351.9 | 484.8 | 418.7
2116 | 1880 | -5.2 | 0 | 0 | 320.4 | 337.3 | 291.6 | 283.5 | 358.4 | 58.8 | 17 | 98.7 | 4.7 | 260 | 4.2 | 160.9 | 152.7 | 420.2 | 457.2 | 607.1 | 416.1 | 369.9 | 339.3 | 357.2 | 439.5 | 662.8 | 415 | 335.1 | 352.9 | 369.1 | 535.7 | 437.6 | 374 | 583.9 | 430.6 | 421.4 | 385.2 | 310.5 | 427.3 | 351.6 | 484.6 | 418.5
2117 | 1881 | -5.2 | 0 | 0 | 320.2 | 336.8 | 291.2 | 283.2 | 358.2 | 58.7 | 17 | 98.6 | 5.2 | 251.8 | 4.6 | 160.2 | 152 | 418.7 | 456 | 606.9 | 415.1 | 366.9 | 338.8 | 355.5 | 438.5 | 662.6 | 413.9 | 335.1 | 352.8 | 368.9 | 535.4 | 437.2 | 373.9 | 583.8 | 430.2 | 421.3 | 385.8 | 310.2 | 427.1 | 351.3 | 484.3 | 418.3
2118 | 1882 | -5.1 | 0 | 0 | 319.9 | 336 | 290.6 | 282.9 | 357.6 | 58.6 | 17 | 98.5 | 4.9 | 244 | 4.8 | 159.6 | 151.6 | 417.4 | 454.8 | 606.5 | 414 | 365 | 338 | 354 | 437.5 | 662.3 | 413.2 | 335 | 352.7 | 368.7 | 535.1 | 436.7 | 373.5 | 583.5 | 430 | 421.2 | 385.9 | 310.1 | 427 | 351 | 484.1 | 418.1
2119 | 1883 | -5 | 0 | 0 | 319.6 | 335.8 | 290.2 | 282.6 | 357.5 | 58.4 | 17 | 98.4 | 4.7 | 246.5 | 5.3 | 158.8 | 150.5 | 416.1 | 453.9 | 606 | 412.9 | 363.3 | 337.2 | 353 | 436.9 | 661.3 | 412.1 | 335 | 352.6 | 368.5 | 534.8 | 436.6 | 373 | 583.3 | 429.6 | 421.1 | 385.7 | 309.8 | 426.8 | 350.7 | 483.8 | 417.9
2120 | 1884 | -4.8 | 0 | 0 | 319.2 | 336.3 | 290.1 | 282.3 | 357.2 | 58.3 | 17 | 98.3 | 4.9 | 248 | 5.6 | 158.6 | 150 | 414.9 | 452.9 | 605.6 | 411.7 | 361 | 336.5 | 351.6 | 437.5 | 661.5 | 411.2 | 334.9 | 352.5 | 368.3 | 534.5 | 436.7 | 372.7 | 583.4 | 428.8 | 421 | 385.5 | 309.4 | 426.8 | 350.4 | 483.5 | 417.8
2121 | 1885 | -4.8 | 0 | 0 | 318.9 | 336.8 | 290.1 | 282 | 356.9 | 58.2 | 17 | 98.1 | 4.5 | 252.1 | 5.6 | 158.5 | 149.6 | 413.4 | 451.7 | 605 | 410.5 | 364.1 | 335.9 | 350.4 | 437.2 | 661.1 | 410.7 | 334.9 | 352.4 | 368.1 | 534.2 | 436.9 | 372.2 | 583.5 | 428.2 | 420.9 | 385.2 | 309.2 | 426.7 | 350.1 | 483.3 | 417.6
2122 | 1886 | -4.9 | 0 | 0 | 318.6 | 336.7 | 289.8 | 281.9 | 356.5 | 58.1 | 17 | 98 | 4.8 | 251.6 | 5.4 | 157.8 | 149 | 412.1 | 450.5 | 604.6 | 409.4 | 363.4 | 335.4 | 348.8 | 437 | 660.3 | 409.6 | 334.8 | 352.3 | 367.9 | 533.8 | 435.6 | 372.2 | 583.5 | 427.9 | 420.8 | 384.3 | 308.8 | 426.6 | 349.8 | 483 | 417.4
2123 | 1887 | -4.9 | 0 | 0 | 318.4 | 336.4 | 289.8 | 281.8 | 356.9 | 58 | 17 | 97.9 | 4.6 | 235 | 5.3 | 157.1 | 148.2 | 410.8 | 449.4 | 604.3 | 408 | 359.6 | 335.3 | 347.7 | 435.6 | 660.5 | 408.6 | 334.8 | 352.1 | 367.7 | 533.5 | 435.8 | 372.1 | 583.3 | 427.6 | 420.7 | 383.6 | 308.4 | 426.4 | 349.5 | 482.8 | 417.2
2124 | 1888 | -4.5 | 0 | 0 | 318.1 | 335.8 | 289.6 | 281.6 | 356.4 | 57.9 | 17 | 97.7 | 4.5 | 240.9 | 5.1 | 156.5 | 147.2 | 409.3 | 448.2 | 603.8 | 406.9 | 356.8 | 334.7 | 346.9 | 434.6 | 660.5 | 407.9 | 334.7 | 352 | 367.6 | 533.1 | 436.2 | 371.6 | 583.3 | 427.3 | 420.6 | 383.2 | 308.4 | 426.2 | 349.3 | 482.5 | 417
2125 | 1889 | -4.2 | 0 | 0 | 317.8 | 335.4 | 289.4 | 281.4 | 355.9 | 57.8 | 17 | 97.6 | 4.6 | 251.2 | 4.8 | 155.6 | 146.8 | 408.1 | 447 | 603.3 | 405.8 | 358.3 | 334.1 | 346 | 433.3 | 660.6 | 406.8 | 334.7 | 351.9 | 367.4 | 532.8 | 436.9 | 371.5 | 583.4 | 427 | 420.4 | 383.5 | 307.9 | 426 | 349 | 482.2 | 416.9
2126 | 1890 | -4.1 | 0 | 0 | 317.4 | 334.9 | 288.9 | 281.3 | 355.6 | 57.7 | 17 | 97.5 | 4.7 | 260 | 4.6 | 155.3 | 146.2 | 407.8 | 445.9 | 602.7 | 404.6 | 357.8 | 333.5 | 344.9 | 432.1 | 660.4 | 405.9 | 334.6 | 351.8 | 367.2 | 532.4 | 436.7 | 371.3 | 583.8 | 426.6 | 420.3 | 383.6 | 307.6 | 425.9 | 348.7 | 482 | 416.7
2127 | 1891 | -4.6 | 0 | 0 | 317.2 | 334.3 | 288.3 | 281 | 355.9 | 57.5 | 17 | 97.3 | 4.2 | 249.6 | 4.4 | 154.6 | 145.1 | 406.7 | 444.6 | 602.1 | 403.4 | 357 | 332.9 | 343.9 | 431.9 | 660.2 | 405 | 334.5 | 351.7 | 367 | 532.1 | 436.3 | 370.9 | 583.9 | 426.5 | 420.2 | 383.1 | 307.5 | 425.9 | 348.4 | 481.7 | 416.5
2128 | 1892 | -4.8 | 0 | 0 | 317 | 334.3 | 287.9 | 280.7 | 356.4 | 57.5 | 17.1 | 97.2 | 4.7 | 252.9 | 3.9 | 153.9 | 144.2 | 405 | 443.2 | 601.5 | 402.2 | 353.7 | 332.7 | 342.7 | 431.4 | 660.2 | 404.2 | 334.5 | 351.6 | 366.8 | 531.8 | 435.6 | 370.3 | 583.6 | 426.3 | 420.1 | 382.5 | 307.1 | 425.8 | 348.1 | 481.5 | 416.3
2129 | 1893 | -4.7 | 0 | 0 | 316.8 | 334.4 | 287.9 | 280.3 | 356.2 | 57.4 | 17 | 97 | 4.8 | 254.4 | 3.8 | 153.2 | 144 | 403.6 | 442 | 601.1 | 401.5 | 350.9 | 332.2 | 341.4 | 431.7 | 659 | 403.5 | 334.4 | 351.5 | 366.6 | 531.4 | 435.6 | 370.1 | 583.4 | 426 | 420 | 382.3 | 306.8 | 425.6 | 347.8 | 481.2 | 416.1
2130 | 1894 | -4.6 | 0 | 0 | 316.7 | 334.1 | 287.8 | 280.1 | 355.5 | 57.4 | 17.1 | 96.9 | 4.7 | 259.1 | 3.9 | 152.7 | 143.8 | 402.6 | 440.8 | 600.8 | 400.8 | 350.5 | 331 | 341.3 | 431.6 | 659.6 | 402.4 | 334.3 | 351.4 | 366.4 | 530.9 | 435.7 | 370.1 | 583.4 | 425.5 | 419.9 | 381.4 | 306.5 | 425.5 | 347.5 | 481 | 415.9
2131 | 1895 | -4.5 | 0 | 0 | 316.6 | 333.7 | 287.7 | 279.9 | 354.8 | 57.3 | 17.1 | 96.7 | 4.9 | 263 | 3.9 | 152.5 | 143.1 | 400.6 | 439.5 | 600.5 | 399.8 | 349 | 330.4 | 340 | 431.4 | 659.4 | 401.8 | 334.3 | 351.3 | 366.3 | 530.6 | 435.9 | 370 | 583.2 | 424.9 | 419.8 | 380.2 | 306.1 | 425.4 | 347.2 | 480.7 | 415.7
2132 | 1896 | -4.7 | 0 | 0 | 316.6 | 333.2 | 287.6 | 279.6 | 354.1 | 57.2 | 17.1 | 96.5 | 5.1 | 244.8 | 4.3 | 152 | 142.6 | 399.4 | 438.4 | 600 | 398.7 | 347.8 | 329.6 | 339.7 | 432.2 | 659.3 | 400.7 | 334.2 | 351.2 | 366.1 | 530.1 | 435.1 | 369.1 | 582.9 | 424 | 419.7 | 379.9 | 305.8 | 425.3 | 346.9 | 480.4 | 415.5
2133 | 1897 | -5 | 0 | 0 | 316.4 | 332.7 | 287.1 | 279.3 | 353.7 | 57.1 | 17.1 | 96.4 | 4.7 | 239.7 | 4.3 | 152.1 | 142.1 | 397.6 | 437.2 | 599.5 | 397.6 | 346.2 | 328.8 | 338.9 | 431.2 | 659.4 | 399.4 | 334.2 | 351 | 365.9 | 529.6 | 433.9 | 368.5 | 582.8 | 423 | 419.6 | 379.7 | 305.5 | 425.2 | 346.6 | 480.2 | 415.3
2134 | 1898 | -5 | 0 | 0 | 316 | 332.3 | 286.5 | 279.1 | 353.2 | 57 | 17.1 | 96.3 | 4.8 | 247.8 | 3.9 | 152.2 | 142 | 396.1 | 435.8 | 599 | 396.7 | 347.2 | 327.9 | 338.4 | 430.9 | 659.1 | 398.5 | 334.1 | 350.9 | 365.7 | 529.2 | 432.6 | 368.2 | 582.9 | 422.8 | 419.5 | 378.8 | 305.1 | 425.2 | 346.3 | 479.9 | 415.1
2135 | 1899 | -4.7 | 0 | 0 | 315.7 | 331.9 | 286 | 278.9 | 352.6 | 56.9 | 17.1 | 96.2 | 4.6 | 242.9 | 3.7 | 151.6 | 141.6 | 394.7 | 434.4 | 598.6 | 395.7 | 346.4 | 326.8 | 337 | 430.5 | 659.1 | 397.7 | 334 | 350.8 | 365.5 | 528.7 | 432.2 | 367.7 | 583 | 422.2 | 419.4 | 378.9 | 304.7 | 425 | 346 | 479.6 | 415
2136 | 1900 | -4.8 | 0 | 0 | 315.5 | 331.4 | 285.8 | 278.7 | 352.1 | 56.7 | 17.1 | 96.2 | 4.5 | 235.2 | 3.9 | 150.8 | 140.8 | 393.5 | 433.3 | 598.3 | 394.8 | 346.4 | 326.3 | 336.1 | 430.6 | 658.7 | 397 | 334 | 350.7 | 365.3 | 528.4 | 430.4 | 367.1 | 583.4 | 421.6 | 419.3 | 378.8 | 304.3 | 424.9 | 345.7 | 479.4 | 414.8
2137 | 1901 | -5 | 0 | 0 | 315.3 | 330.7 | 285.8 | 278.6 | 351.8 | 56.6 | 17.1 | 96.1 | 4.6 | 253.5 | 3.9 | 149.7 | 139.9 | 391.7 | 432.3 | 598 | 393.7 | 345.5 | 325.9 | 334.6 | 428.6 | 658.3 | 396.2 | 333.9 | 350.6 | 365.1 | 528 | 430.9 | 366.4 | 583.5 | 421.2 | 419.3 | 378.8 | 304 | 424.8 | 345.4 | 479.1 | 414.6
2138 | 1902 | -5.2 | 0 | 0 | 315.1 | 330.2 | 285.6 | 278.5 | 351.2 | 56.5 | 17.1 | 96 | 5 | 256.2 | 3.5 | 148.8 | 138.9 | 390 | 430.7 | 597.7 | 392.6 | 343.8 | 324.9 | 333.2 | 426.4 | 658 | 395.6 | 333.9 | 350.5 | 364.9 | 527.7 | 430.8 | 365.9 | 583.7 | 420.4 | 419.2 | 378.5 | 303.8 | 424.7 | 345.1 | 478.9 | 414.4
2139 | 1903 | -5.2 | 0 | 0 | 314.8 | 329.8 | 285.3 | 278.2 | 350.8 | 56.4 | 17.1 | 95.8 | 4.9 | 244 | 3.2 | 148.4 | 138.2 | 388.9 | 429.3 | 597.2 | 391.3 | 341.1 | 324.3 | 332.2 | 426.5 | 657.7 | 395 | 333.8 | 350.4 | 364.7 | 527.5 | 429.5 | 365.6 | 583.6 | 420.2 | 419 | 379.2 | 303.6 | 424.5 | 344.9 | 478.6 | 414.2
2140 | 1904 | -5.1 | 0 | 0 | 314.6 | 329.9 | 285.2 | 277.8 | 350.7 | 56.3 | 17.1 | 95.7 | 4.8 | 219.7 | 3.1 | 147.8 | 137.7 | 387.8 | 428.1 | 596.6 | 390.1 | 342.2 | 323.3 | 332.1 | 425.5 | 657.3 | 394.1 | 333.7 | 350.3 | 364.6 | 527.2 | 429.9 | 365.2 | 583.2 | 420 | 418.9 | 378.8 | 303.4 | 424.4 | 344.6 | 478.3 | 414
2141 | 1905 | -4.8 | 0 | 0 | 314.3 | 329.7 | 285 | 277.2 | 350.8 | 56.2 | 17.1 | 95.6 | 4.8 | 195.2 | 2.9 | 147.3 | 136.7 | 386.3 | 426.9 | 596.1 | 389.1 | 340.6 | 322.1 | 331.6 | 425.4 | 657.1 | 393.1 | 333.6 | 350.2 | 364.4 | 527 | 428.6 | 365.1 | 583.2 | 419.4 | 418.8 | 378.1 | 303.3 | 424.3 | 344.3 | 478.1 | 413.8
2142 | 1906 | -4.6 | 0 | 0 | 314.1 | 329.4 | 284.7 | 276.9 | 350.3 | 56.1 | 17.1 | 95.6 | 4.7 | 216.9 | 2.7 | 146.6 | 135.9 | 385.1 | 425.7 | 595.5 | 388.1 | 339.7 | 321.2 | 330.7 | 424.6 | 656.5 | 392.2 | 333.6 | 350.1 | 364.2 | 526.6 | 428.5 | 364.6 | 583.1 | 419.3 | 418.7 | 377 | 302.8 | 424.1 | 344 | 477.8 | 413.6
2143 | 1907 | -4.7 | 0 | 0 | 313.9 | 329.2 | 284.1 | 276.6 | 349.9 | 56 | 17.1 | 95.5 | 4.5 | 248 | 2.8 | 146.2 | 135.6 | 383.7 | 424.7 | 595 | 387.1 | 338.9 | 319.9 | 331.1 | 424.2 | 656.4 | 391.4 | 333.5 | 350 | 364 | 526.2 | 428.1 | 363.9 | 582.7 | 419.1 | 418.5 | 376.1 | 302.5 | 423.9 | 343.7 | 477.6 | 413.4
2144 | 1908 | -4.7 | 0 | 0 | 313.6 | 329 | 283.3 | 276.5 | 349.7 | 55.9 | 17.1 | 95.4 | 4.4 | 258.8 | 2.9 | 145.6 | 135.4 | 382.7 | 423.6 | 594.4 | 386.1 | 338.8 | 319.1 | 330.1 | 424 | 656.4 | 390.5 | 333.4 | 349.9 | 363.8 | 525.7 | 427.9 | 363.3 | 582.6 | 418.6 | 418.4 | 375.9 | 302.3 | 423.8 | 343.4 | 477.3 | 413.2
2145 | 1909 | -4.5 | 0 | 0 | 313.3 | 328.5 | 282.6 | 276.2 | 349.4 | 55.8 | 17.1 | 95.2 | 4.1 | 256.9 | 2.9 | 145 | 134.7 | 382 | 422.5 | 594.1 | 385 | 336.7 | 318.8 | 328.6 | 423.9 | 656.2 | 389.9 | 333.4 | 349.8 | 363.7 | 525.2 | 427.3 | 363 | 582.3 | 418.3 | 418.2 | 375.7 | 301.8 | 423.6 | 343.1 | 477.1 | 413
2146 | 1910 | -4.5 | 0 | 0 | 313 | 328.1 | 282.3 | 276 | 348.7 | 55.7 | 17.1 | 95.1 | 4.2 | 259.1 | 3.3 | 144.5 | 134.1 | 381.2 | 421.4 | 593.7 | 383.9 | 337.2 | 318.1 | 328.1 | 423.3 | 656 | 389.5 | 333.3 | 349.7 | 363.5 | 524.7 | 426.8 | 362.9 | 582.2 | 418.1 | 418.1 | 375.4 | 301.4 | 423.5 | 342.8 | 476.8 | 412.8
2147 | 1911 | -4.3 | 0 | 0 | 312.7 | 327.6 | 282.1 | 275.8 | 348.4 | 55.7 | 17.1 | 95 | 4.3 | 246.5 | 3.5 | 143.9 | 133.2 | 380 | 420.4 | 593.3 | 382.9 | 337.3 | 317.6 | 327.4 | 422.8 | 655.7 | 388.4 | 333.2 | 349.5 | 363.3 | 524.3 | 426.4 | 362.7 | 582.1 | 417.4 | 417.9 | 374.9 | 301.1 | 423.4 | 342.6 | 476.6 | 412.6
2148 | 1912 | -4.4 | 0 | 0 | 312.4 | 327 | 282.2 | 275.7 | 348.5 | 55.6 | 17.1 | 94.8 | 4.6 | 227.5 | 3.5 | 143.2 | 132.8 | 378.7 | 419.5 | 593 | 382 | 337.1 | 316.8 | 326.8 | 423.3 | 655.5 | 387.2 | 333.1 | 349.4 | 363.1 | 523.7 | 427.1 | 362.3 | 582 | 416.5 | 417.8 | 374.9 | 300.9 | 423.2 | 342.3 | 476.3 | 412.4
2149 | 1913 | -4.7 | 0 | 0 | 312.2 | 326.7 | 282.3 | 275.6 | 348.5 | 55.6 | 17.1 | 94.8 | 4.4 | 227.9 | 3.4 | 143.2 | 132.4 | 377.4 | 418.2 | 592.7 | 381 | 337.3 | 316.5 | 325.9 | 422.9 | 655.6 | 386.3 | 333 | 349.3 | 362.9 | 523.3 | 427 | 361.8 | 582.3 | 416 | 417.6 | 375.5 | 300.6 | 423.1 | 342 | 476.1 | 412.2
2150 | 1914 | -4.8 | 0 | 0 | 312 | 326 | 282.2 | 275.5 | 348.3 | 55.5 | 17.1 | 94.7 | 4.6 | 252.1 | 3.1 | 142.4 | 131.7 | 376.3 | 417.1 | 592.3 | 380.1 | 336.1 | 316 | 324.7 | 422 | 655.2 | 385.8 | 332.9 | 349.2 | 362.8 | 523.1 | 427.1 | 361.2 | 582 | 416.1 | 417.5 | 375.5 | 300.3 | 423 | 341.7 | 475.8 | 412.1
2151 | 1915 | -4.7 | 0 | 0 | 311.8 | 325.2 | 281.9 | 275.3 | 347.9 | 55.4 | 17.1 | 94.7 | 4.4 | 244 | 2.9 | 141.9 | 131.1 | 375.3 | 416.3 | 591.7 | 379.3 | 337.1 | 315.2 | 324.1 | 421.2 | 655.2 | 385 | 332.9 | 349.1 | 362.6 | 522.9 | 426.6 | 360.7 | 582 | 416 | 417.3 | 376 | 300 | 422.9 | 341.4 | 475.5 | 411.9
2152 | 1916 | -4.7 | 0 | 0 | 311.6 | 324.9 | 282.1 | 275.1 | 347.7 | 55.3 | 17.1 | 94.6 | 4.6 | 233.4 | 3 | 142 | 130.7 | 373.7 | 415.5 | 591.4 | 378.5 | 336.1 | 314.7 | 323.2 | 419.9 | 655.3 | 383.8 | 332.8 | 349 | 362.4 | 522.7 | 426.5 | 360.4 | 581.7 | 415.3 | 417.2 | 375.6 | 299.8 | 422.8 | 341.1 | 475.3 | 411.7
2153 | 1917 | -4.6 | 0 | 0 | 311.3 | 324.6 | 282.2 | 274.9 | 347.6 | 55.3 | 17.1 | 94.5 | 4.8 | 242.7 | 3.3 | 142.2 | 130.5 | 372.1 | 414.4 | 591 | 377.6 | 334.7 | 314 | 322.5 | 418.7 | 654.8 | 382.8 | 332.7 | 348.9 | 362.2 | 522.5 | 425.6 | 360.3 | 581.6 | 415.1 | 417 | 375 | 299.4 | 422.6 | 340.9 | 475 | 411.5
2154 | 1918 | -4.6 | 0 | 0 | 310.9 | 324.4 | 281.9 | 274.6 | 347.5 | 55.2 | 17.1 | 94.4 | 4.4 | 254.3 | 3.4 | 141.7 | 130 | 370.9 | 413.1 | 590.7 | 376.9 | 334.1 | 313.2 | 321.1 | 418.5 | 654.9 | 382.2 | 332.7 | 348.8 | 362 | 522.2 | 425.6 | 360.4 | 581.6 | 415.2 | 416.9 | 375 | 299 | 422.4 | 340.6 | 474.8 | 411.3
2155 | 1919 | -4.6 | 0 | 0 | 310.8 | 324 | 281.9 | 274.3 | 347.2 | 55.2 | 17.1 | 94.3 | 4.5 | 245.2 | 3.5 | 140.9 | 129.6 | 369.8 | 411.7 | 590.4 | 376.1 | 332.2 | 313 | 320.1 | 417.1 | 654.7 | 381.9 | 332.6 | 348.7 | 361.8 | 522 | 426 | 360 | 581.5 | 415 | 416.7 | 375.1 | 298.8 | 422.2 | 340.3 | 474.5 | 411.1
2156 | 1920 | -4.6 | 0 | 0 | 310.7 | 323.8 | 281.6 | 274.2 | 346.8 | 55.2 | 17.1 | 94.1 | 4.9 | 240.9 | 3.6 | 139.9 | 128.5 | 368.6 | 410.7 | 590 | 375.1 | 332.5 | 312.4 | 319.4 | 416.7 | 654.5 | 381.3 | 332.5 | 348.6 | 361.6 | 521.7 | 425.8 | 359.7 | 581.5 | 414.5 | 416.6 | 374.7 | 298.3 | 422.1 | 340 | 474.2 | 410.9
2157 | 1921 | -4.6 | 0 | 0 | 310.5 | 323.8 | 281.6 | 274 | 346.5 | 55.1 | 17.1 | 94.1 | 5 | 241.8 | 3.8 | 139.2 | 127.6 | 367.7 | 409.7 | 589.6 | 374.1 | 332.9 | 312.1 | 318 | 416.4 | 654.3 | 380.5 | 332.5 | 348.5 | 361.4 | 521.3 | 425.6 | 359.1 | 581.8 | 413.6 | 416.5 | 374.4 | 298 | 422 | 339.7 | 474 | 410.7
2158 | 1922 | -4.7 | 0 | 0 | 310.4 | 323.1 | 281.6 | 273.8 | 346.3 | 55 | 17.1 | 94 | 4.5 | 241.4 | 4.2 | 138.6 | 126.9 | 366.7 | 408.5 | 589 | 373.5 | 329.7 | 312.1 | 316.5 | 415.5 | 654.4 | 379.5 | 332.4 | 348.3 | 361.3 | 521 | 424.9 | 358 | 581.7 | 412.6 | 416.3 | 373.6 | 297.8 | 421.9 | 339.4 | 473.7 | 410.5
2159 | 1923 | -4.5 | 0 | 0 | 310.1 | 322.8 | 281.1 | 273.6 | 346.1 | 55 | 17.2 | 93.9 | 4.2 | 240.6 | 3.9 | 138.1 | 126 | 366.7 | 407.3 | 588.6 | 372.8 | 331 | 312.3 | 315.4 | 413 | 654.6 | 379.1 | 332.3 | 348.2 | 361.1 | 520.7 | 423.4 | 357.7 | 581.3 | 412 | 416.2 | 373.4 | 297.6 | 421.8 | 339.2 | 473.5 | 410.3
2160 | 1924 | -3.8 | 0 | 0 | 309.8 | 322.8 | 280.5 | 273.2 | 345.9 | 54.9 | 17.2 | 93.8 | 4.3 | 234.5 | 3.6 | 137.6 | 125.1 | 366.6 | 406.2 | 588.2 | 372.3 | 333.1 | 311.7 | 314.9 | 411.9 | 654.9 | 378.5 | 332.2 | 348.1 | 360.9 | 520.3 | 422.7 | 357.3 | 581.4 | 411.4 | 416.1 | 372.5 | 297.4 | 421.7 | 338.9 | 473.2 | 410.1
2161 | 1925 | -3.6 | 0 | 0 | 309.4 | 322 | 280 | 272.9 | 345.5 | 54.8 | 17.2 | 93.7 | 4.3 | 233 | 3.2 | 136.9 | 124.1 | 365.9 | 405.6 | 587.9 | 371.6 | 333.4 | 311.6 | 314.2 | 411.3 | 654.9 | 377.6 | 332.2 | 348 | 360.7 | 519.9 | 422.2 | 357.2 | 581.3 | 410.9 | 415.9 | 372.7 | 297.3 | 421.6 | 338.6 | 473 | 409.9
2162 | 1926 | -4 | 0 | 0 | 309 | 321.2 | 279.8 | 272.8 | 345.1 | 54.8 | 17.2 | 93.6 | 4.3 | 234.3 | 2.9 | 136.2 | 123.7 | 365.2 | 404.7 | 587.5 | 371.1 | 334.2 | 312 | 313.6 | 410.6 | 654.8 | 377.1 | 332.1 | 347.9 | 360.5 | 519.5 | 421.4 | 356.9 | 581.2 | 410.5 | 415.8 | 372.8 | 297 | 421.5 | 338.3 | 472.7 | 409.7
2163 | 1927 | -4.2 | 0 | 0 | 308.7 | 321.1 | 279.6 | 272.5 | 344.8 | 54.7 | 17.2 | 93.5 | 4.7 | 235.2 | 3.1 | 136.1 | 123.1 | 364.4 | 403.9 | 587.2 | 370.6 | 333.3 | 312 | 312.5 | 409.3 | 655.1 | 376.6 | 332 | 347.8 | 360.4 | 519.2 | 420.9 | 356.2 | 581 | 410.3 | 415.6 | 371.7 | 296.8 | 421.3 | 338.1 | 472.4 | 409.5
2164 | 1928 | -4.4 | 0 | 0 | 308.4 | 321.1 | 279.2 | 272.2 | 344.6 | 54.6 | 17.2 | 93.3 | 4.6 | 242.1 | 3.7 | 136.4 | 122.5 | 363.4 | 403.1 | 587.1 | 369.8 | 331.4 | 311.8 | 311.6 | 408.8 | 655.1 | 375.8 | 331.9 | 347.7 | 360.2 | 518.8 | 421.2 | 355.7 | 580.8 | 410.1 | 415.5 | 370.9 | 296.5 | 421.1 | 337.8 | 472.2 | 409.3
2165 | 1929 | -4.5 | 0 | 0 | 308.1 | 320.7 | 278.6 | 271.9 | 344.5 | 54.5 | 17.2 | 93.2 | 4.5 | 228.9 | 4.6 | 136.4 | 121.5 | 362.2 | 402.3 | 586.9 | 369.1 | 330.6 | 311.8 | 310.5 | 408.2 | 655.3 | 375.2 | 331.8 | 347.6 | 360 | 518.6 | 421 | 355.1 | 580.7 | 409.4 | 415.3 | 370.4 | 296.3 | 421.1 | 337.5 | 471.9 | 409.1
2166 | 1930 | -4.7 | 0 | 0 | 307.8 | 320.2 | 278.3 | 271.6 | 344.5 | 54.4 | 17.2 | 93.2 | 4.8 | 219.8 | 5.1 | 136.5 | 120.9 | 360.7 | 401.6 | 586.7 | 368.4 | 331.5 | 312.2 | 309.7 | 405.9 | 654.9 | 374.7 | 331.8 | 347.5 | 359.8 | 518.4 | 420.7 | 354.7 | 580.6 | 408.7 | 415.1 | 370.1 | 296.2 | 420.9 | 337.3 | 471.7 | 408.9
2167 | 1931 | -4.6 | 0 | 0 | 307.8 | 320.1 | 278.4 | 271.3 | 344.4 | 54.3 | 17.2 | 93.1 | 4.6 | 227.5 | 5 | 136.7 | 120.5 | 359.8 | 401.7 | 586.2 | 367.6 | 331.5 | 312.8 | 308.9 | 404.3 | 654.9 | 374.5 | 331.7 | 347.4 | 359.6 | 518.2 | 421.5 | 354.5 | 580.3 | 408.6 | 414.9 | 369.8 | 295.9 | 420.7 | 337 | 471.4 | 408.7
2168 | 1932 | -4.6 | 0 | 0 | 307.8 | 320.2 | 278.7 | 271.3 | 344.4 | 54.2 | 17.2 | 93 | 4.9 | 240.6 | 4.6 | 136.6 | 119.8 | 359.4 | 401.4 | 585.8 | 366.9 | 332.9 | 313.2 | 308.4 | 403.8 | 655.1 | 374 | 331.7 | 347.2 | 359.5 | 517.9 | 421.6 | 354.4 | 580 | 408.5 | 414.7 | 370.1 | 295.5 | 420.4 | 336.7 | 471.2 | 408.5
2169 | 1933 | -4.6 | 0 | 0 | 307.7 | 319.6 | 278.7 | 271.2 | 344.3 | 54.1 | 17.2 | 92.9 | 4.7 | 233.2 | 4.3 | 136.1 | 119 | 359.4 | 400.7 | 585.2 | 365.9 | 331.4 | 313.4 | 307.5 | 402.3 | 655.2 | 373.8 | 331.6 | 347.1 | 359.3 | 517.6 | 421.9 | 354.4 | 579.9 | 408.3 | 414.5 | 370.7 | 295.4 | 420.2 | 336.5 | 470.9 | 408.3
2170 | 1934 | -4.5 | 0 | 0 | 307.5 | 319.2 | 278.5 | 270.9 | 344.2 | 54 | 17.2 | 92.8 | 4.5 | 233.2 | 4.1 | 135.8 | 118.3 | 358.5 | 400.3 | 584.7 | 365.2 | 329.7 | 314.1 | 307.2 | 401.6 | 655 | 373.4 | 331.5 | 347 | 359.1 | 517.4 | 421.4 | 354.6 | 579.8 | 408 | 414.3 | 370.4 | 295.2 | 420 | 336.2 | 470.7 | 408.1
2171 | 1935 | -4.5 | 0 | 0 | 307.4 | 318.5 | 278.4 | 270.6 | 344 | 53.9 | 17.2 | 92.7 | 4.5 | 240 | 3.9 | 135.5 | 118.2 | 358 | 399.9 | 584.5 | 364.5 | 329.9 | 314.8 | 306.4 | 401.4 | 655.2 | 373.1 | 331.5 | 346.9 | 358.9 | 517.1 | 421.3 | 354.5 | 579.6 | 407.7 | 414.1 | 370.3 | 294.9 | 419.8 | 335.9 | 470.4 | 407.9
2172 | 1936 | -4.2 | 0 | 0 | 307.2 | 317.7 | 278.5 | 270.2 | 344.1 | 53.9 | 17.2 | 92.7 | 4.8 | 245.8 | 4.1 | 135.6 | 117.9 | 357.2 | 399.7 | 584.3 | 363.8 | 331 | 315.3 | 306.3 | 401 | 655.1 | 373 | 331.4 | 346.8 | 358.8 | 516.8 | 420.1 | 353.8 | 579.3 | 407.6 | 413.9 | 369.7 | 294.6 | 419.6 | 335.7 | 470.1 | 407.8
2173 | 1937 | -4 | 0 | 0 | 307.1 | 317.4 | 278.3 | 270 | 344.8 | 53.8 | 17.2 | 92.6 | 4.5 | 258.3 | 4.3 | 134.8 | 117 | 356.3 | 399.3 | 583.7 | 362.9 | 329.8 | 315.7 | 305.8 | 400.5 | 655.1 | 372.7 | 331.3 | 346.7 | 358.6 | 516.5 | 421.3 | 353.7 | 579.1 | 407.5 | 413.7 | 369.3 | 294.2 | 419.3 | 335.4 | 469.9 | 407.6
2174 | 1938 | -3.9 | 0 | 0 | 307 | 317.3 | 278.1 | 269.8 | 344.3 | 53.7 | 17.2 | 92.6 | 4.5 | 254.8 | 4 | 134.2 | 116.4 | 355.5 | 398.7 | 583.5 | 361.9 | 329.1 | 316.2 | 304.8 | 399.3 | 655.2 | 372 | 331.3 | 346.6 | 358.4 | 516.1 | 421.6 | 353.7 | 578.8 | 407.1 | 413.6 | 369.1 | 293.9 | 419.2 | 335.1 | 469.6 | 407.4
2175 | 1939 | -3.8 | 0 | 0 | 306.7 | 317 | 277.9 | 269.6 | 344 | 53.7 | 17.2 | 92.5 | 4.8 | 223.3 | 3.8 | 133.9 | 116 | 354.6 | 398.1 | 583 | 361 | 329 | 316.5 | 304 | 398.6 | 654.8 | 371.5 | 331.2 | 346.5 | 358.2 | 515.7 | 421.1 | 353.3 | 578.4 | 406.9 | 413.4 | 368.1 | 293.6 | 419.1 | 334.8 | 469.4 | 407.2
2176 | 1940 | -4.3 | 0 | 0 | 306.4 | 317 | 277.6 | 269.4 | 343.6 | 53.6 | 17.2 | 92.4 | 4.6 | 223.5 | 4.1 | 133.7 | 115.2 | 353.5 | 397.3 | 582.6 | 360.2 | 328.2 | 316.9 | 303.1 | 397.6 | 655 | 371 | 331.1 | 346.3 | 358.1 | 515.3 | 418.3 | 352.6 | 578 | 406.4 | 413.2 | 367 | 293.3 | 419 | 334.6 | 469.1 | 407
2177 | 1941 | -4.3 | 0 | 0 | 306 | 316.9 | 277.6 | 269 | 342.8 | 53.5 | 17.2 | 92.3 | 4.4 | 243.5 | 4.5 | 133.4 | 114.5 | 352.7 | 396.6 | 582.1 | 359.4 | 328.7 | 317.1 | 302.6 | 397.7 | 654.8 | 370.9 | 331 | 346.2 | 357.9 | 515 | 418.1 | 352.5 | 577.7 | 405.9 | 413.1 | 367 | 293.1 | 418.9 | 334.3 | 468.9 | 406.8
2178 | 1942 | -4.3 | 0 | 0 | 305.3 | 316.8 | 277.5 | 268.9 | 342.3 | 53.5 | 17.2 | 92.2 | 4.4 | 239.9 | 4.7 | 133 | 113.8 | 351.5 | 395.7 | 581.5 | 358.6 | 328.6 | 316.8 | 301.7 | 397.2 | 654.6 | 370.3 | 331 | 346.1 | 357.7 | 514.6 | 418.7 | 352.4 | 577.3 | 405.2 | 413 | 366.9 | 292.8 | 418.8 | 334 | 468.6 | 406.6
2179 | 1943 | -4.6 | 0 | 0 | 304.7 | 317 | 276.8 | 268.8 | 342 | 53.4 | 17.2 | 92.1 | 4.5 | 235.8 | 4.5 | 132.4 | 112.9 | 350.8 | 394.9 | 581 | 357.9 | 327.1 | 316.7 | 300.9 | 395.8 | 654.1 | 369.9 | 330.9 | 346 | 357.5 | 514.3 | 418.9 | 352.6 | 577.1 | 404.9 | 412.8 | 366.5 | 292.4 | 418.7 | 333.8 | 468.4 | 406.4
2180 | 1944 | -4.6 | 0 | 0 | 304.4 | 316.6 | 276.3 | 268.5 | 341.6 | 53.3 | 17.2 | 92 | 4.5 | 240.3 | 4 | 131.7 | 112.1 | 349.7 | 394 | 580.7 | 357 | 326.4 | 316.2 | 300.5 | 394.3 | 653.8 | 369.2 | 330.8 | 345.9 | 357.3 | 514 | 417 | 352.4 | 576.9 | 404.9 | 412.7 | 366.2 | 292.1 | 418.6 | 333.5 | 468.1 | 406.2
2181 | 1945 | -4.4 | 0 | 0 | 304.1 | 315.9 | 275.9 | 268.3 | 341.4 | 53.3 | 17.2 | 91.9 | 4.5 | 239.6 | 3.6 | 131.2 | 111.6 | 349.1 | 393 | 580.4 | 355.9 | 326.9 | 315 | 300 | 395.4 | 653.7 | 368.4 | 330.8 | 345.8 | 357.2 | 513.6 | 416.8 | 351.8 | 576.5 | 404.4 | 412.6 | 365.6 | 291.8 | 418.4 | 333.2 | 467.8 | 406
2182 | 1946 | -4.5 | 0 | 0 | 303.6 | 315.6 | 275.5 | 268.2 | 341.2 | 53.2 | 17.2 | 91.9 | 4.7 | 230.9 | 3.3 | 130.7 | 111.1 | 348.2 | 391.9 | 580 | 354.9 | 326.3 | 313.8 | 299.5 | 395 | 653.6 | 367.3 | 330.7 | 345.7 | 357 | 513.2 | 417.6 | 351.6 | 576.3 | 404 | 412.4 | 365.2 | 291.5 | 418.1 | 332.9 | 467.6 | 405.8
2183 | 1947 | -4.4 | 0 | 0 | 303 | 315.3 | 275.4 | 267.9 | 341.1 | 53.2 | 17.2 | 91.8 | 4.7 | 215 | 3.1 | 130.2 | 110.6 | 347.5 | 390.5 | 579.5 | 353.9 | 324.7 | 312.8 | 298.8 | 394.5 | 653.7 | 366.5 | 330.7 | 345.6 | 356.8 | 512.8 | 417.8 | 351 | 575.9 | 403.2 | 412.3 | 364.5 | 291.4 | 417.9 | 332.7 | 467.3 | 405.6
2184 | 1948 | -4.1 | 0 | 0 | 302.6 | 315.2 | 275.3 | 267.6 | 342.1 | 53.1 | 17.2 | 91.7 | 4.4 | 206.7 | 3.1 | 129.2 | 110.2 | 346.8 | 389.3 | 579.1 | 352.8 | 325.9 | 312.2 | 298 | 392.2 | 652.9 | 365.8 | 330.6 | 345.5 | 356.6 | 512.5 | 417.8 | 350.5 | 575.5 | 402.6 | 412.1 | 364.1 | 291.2 | 417.7 | 332.4 | 467.1 | 405.4
2185 | 1949 | -4.2 | 0 | 0 | 302.5 | 315.4 | 275.5 | 267.5 | 342.1 | 53.1 | 17.2 | 91.6 | 4.4 | 205.9 | 2.7 | 128.6 | 109.6 | 346.4 | 388.2 | 578.7 | 352 | 322.2 | 311.1 | 297 | 390.9 | 652.5 | 365.1 | 330.5 | 345.3 | 356.5 | 512.2 | 417.8 | 350.1 | 575.2 | 402.5 | 411.9 | 363.3 | 291 | 417.5 | 332.2 | 466.8 | 405.2
2186 | 1950 | -4.3 | 0 | 0 | 302.5 | 315.2 | 275.5 | 267.3 | 341.6 | 53 | 17.2 | 91.6 | 4.3 | 225.9 | 2.4 | 128.3 | 109.2 | 345.4 | 386.8 | 578.2 | 350.9 | 321.4 | 310.1 | 296.6 | 390.3 | 652.2 | 363.8 | 330.5 | 345.2 | 356.3 | 511.8 | 417.7 | 349.8 | 575 | 402.5 | 411.7 | 362.9 | 290.7 | 417.3 | 331.9 | 466.6 | 405
2187 | 1951 | -4.4 | 0 | 0 | 302.5 | 315.6 | 275.5 | 267.1 | 341.4 | 53 | 17.3 | 91.5 | 4.2 | 248.4 | 2.4 | 127.8 | 108.8 | 344.7 | 385.6 | 577.7 | 350.2 | 323.3 | 308.9 | 296.7 | 391.2 | 652.2 | 363.1 | 330.4 | 345.1 | 356.1 | 511.5 | 417.8 | 349.5 | 574.7 | 401.9 | 411.4 | 362 | 290.2 | 417.1 | 331.6 | 466.3 | 404.8
2188 | 1952 | -4.2 | 0 | 0 | 302.4 | 315.5 | 275.4 | 266.8 | 341 | 52.9 | 17.3 | 91.5 | 4 | 230.5 | 2.4 | 127.4 | 108.4 | 343.9 | 384.6 | 577.4 | 349.4 | 322.5 | 308.5 | 295.4 | 391.3 | 651.8 | 362.6 | 330.4 | 345 | 356 | 511 | 418.3 | 349 | 574.3 | 401.5 | 411.2 | 361 | 289.9 | 416.9 | 331.4 | 466.1 | 404.6
2189 | 1953 | -4.1 | 0 | 0 | 302.2 | 315.2 | 275.6 | 266.6 | 340.8 | 52.8 | 17.3 | 91.4 | 4.4 | 214.2 | 2.8 | 127 | 107.8 | 343.2 | 383.4 | 577.3 | 348.4 | 320.9 | 307.9 | 294.6 | 390.5 | 651.4 | 361.9 | 330.3 | 344.9 | 355.8 | 510.5 | 415.8 | 348.9 | 573.8 | 401.3 | 411 | 360.8 | 289.6 | 416.7 | 331.1 | 465.8 | 404.4
2190 | 1954 | -4.4 | 0 | 0 | 301.8 | 314.5 | 275.8 | 266.4 | 340.6 | 52.8 | 17.3 | 91.3 | 4.3 | 221.9 | 3.1 | 126.7 | 107.4 | 342.7 | 382.4 | 577.2 | 347.5 | 321.4 | 307.1 | 293.6 | 389.6 | 651.6 | 361 | 330.2 | 344.8 | 355.6 | 510 | 415.9 | 348.7 | 573.4 | 400.7 | 410.8 | 360.7 | 289.3 | 416.5 | 330.9 | 465.6 | 404.2
2191 | 1955 | -4.3 | 0 | 0 | 301.3 | 313.6 | 276.1 | 266.2 | 340.3 | 52.7 | 17.3 | 91.3 | 4 | 220.4 | 3.1 | 126.3 | 106.9 | 341.7 | 381.3 | 576.9 | 346.5 | 319 | 306.1 | 292.8 | 389.4 | 651.5 | 360.3 | 330.1 | 344.7 | 355.4 | 509.6 | 416.5 | 348.7 | 573.1 | 400.4 | 410.6 | 361.1 | 289.1 | 416.2 | 330.6 | 465.3 | 404
2192 | 1956 | -4.1 | 0 | 0 | 300.9 | 313.2 | 276.2 | 265.8 | 339.8 | 52.7 | 17.3 | 91.2 | 4.4 | 212.7 | 4.3 | 125.9 | 106.5 | 340.9 | 380 | 576.7 | 345.5 | 321.1 | 305.3 | 292.2 | 388.7 | 651.1 | 359.7 | 330.1 | 344.6 | 355.2 | 509.3 | 416.3 | 348.2 | 573 | 400.6 | 410.3 | 361.4 | 288.9 | 416 | 330.4 | 465 | 403.8
2193 | 1957 | -4.2 | 0 | 0 | 300.5 | 312.6 | 275.4 | 265.6 | 339.5 | 52.6 | 17.3 | 91.1 | 4.5 | 209.9 | 5.7 | 125.6 | 106.3 | 340.4 | 378.4 | 576.5 | 344.6 | 319.7 | 304.3 | 291.9 | 389.2 | 651.4 | 358.9 | 330 | 344.5 | 355.1 | 509.1 | 414.8 | 347.9 | 572.8 | 399.9 | 410.1 | 361.2 | 288.7 | 415.9 | 330.1 | 464.8 | 403.6
2194 | 1958 | -4.4 | 0 | 0 | 300.1 | 312.1 | 274.8 | 265.6 | 339.4 | 52.5 | 17.3 | 90.9 | 4.5 | 199.9 | 6.4 | 125.4 | 106.1 | 339.7 | 376.7 | 576.3 | 343.8 | 320 | 303.1 | 292 | 388.2 | 651.6 | 357.8 | 329.9 | 344.4 | 354.9 | 508.8 | 413.8 | 347.5 | 572.8 | 399.7 | 409.9 | 360.9 | 288.5 | 415.7 | 329.9 | 464.5 | 403.4
2195 | 1959 | -4.3 | 0 | 0 | 299.5 | 312.1 | 274 | 265.4 | 339.9 | 52.5 | 17.3 | 90.7 | 4.7 | 195.7 | 6.5 | 124.9 | 105.7 | 338.9 | 375.3 | 575.7 | 343 | 316.9 | 302.3 | 291.4 | 386.3 | 651.4 | 357.2 | 329.9 | 344.2 | 354.7 | 508.5 | 414.2 | 346.9 | 572.5 | 399.4 | 409.7 | 360.9 | 288.2 | 415.5 | 329.6 | 464.3 | 403.2
2196 | 1960 | -4.3 | 0 | 0 | 299 | 312.2 | 273.6 | 265.1 | 340.3 | 52.5 | 17.3 | 90.6 | 4.9 | 199.4 | 6.5 | 124.4 | 105.6 | 338.6 | 373.7 | 575.1 | 342 | 317.3 | 301.6 | 290.9 | 385.9 | 651.2 | 356.6 | 329.8 | 344.1 | 354.6 | 508.2 | 413.7 | 346.8 | 572.3 | 399.4 | 409.5 | 360.8 | 288 | 415.3 | 329.4 | 464 | 403
2197 | 1961 | -4 | 0 | 0 | 299 | 312.3 | 274 | 264.8 | 340 | 52.4 | 17.3 | 90.4 | 4.3 | 208.1 | 6.6 | 124 | 105.5 | 338 | 372.1 | 574.6 | 341.1 | 315.3 | 300.7 | 290.8 | 386.1 | 650.7 | 356.1 | 329.7 | 344 | 354.4 | 507.8 | 414.4 | 345.8 | 571.9 | 398.9 | 409.3 | 361 | 287.8 | 415 | 329.1 | 463.8 | 402.8
2198 | 1962 | -3.9 | 0 | 0 | 299.1 | 312.4 | 274.1 | 264.6 | 339.4 | 52.4 | 17.3 | 90.4 | 4.1 | 215.8 | 6.7 | 123.5 | 105 | 337.3 | 370.9 | 574.4 | 340.2 | 316 | 299.7 | 290.4 | 386.6 | 650.6 | 355.4 | 329.7 | 343.9 | 354.2 | 507.5 | 414.2 | 345.4 | 571.6 | 398.6 | 409.1 | 361.1 | 287.3 | 414.7 | 328.9 | 463.5 | 402.6
2199 | 1963 | -3.9 | 0 | 0 | 298.6 | 312.1 | 274.1 | 264.3 | 338.8 | 52.4 | 17.3 | 90.3 | 4.7 | 197.8 | 6.9 | 123.1 | 104.5 | 336.6 | 369.6 | 574.2 | 339.5 | 315.1 | 299 | 290.1 | 386.3 | 650.6 | 355 | 329.6 | 343.8 | 354 | 507 | 414.2 | 344.8 | 571.2 | 398 | 408.9 | 360.5 | 287 | 414.5 | 328.6 | 463.3 | 402.4
2200 | 1964 | -4 | 0 | 0 | 298.3 | 312 | 273.8 | 264 | 338.3 | 52.3 | 17.3 | 90.4 | 4.3 | 203.9 | 6.8 | 122.9 | 104.1 | 335.9 | 368.6 | 573.9 | 338.5 | 313.9 | 299.1 | 289 | 385.5 | 649.8 | 354.2 | 329.6 | 343.7 | 353.8 | 506.5 | 413.8 | 344.4 | 571 | 397.6 | 408.7 | 360 | 286.9 | 414.4 | 328.4 | 463 | 402.3
2201 | 1965 | -4.1 | 0 | 0 | 298.4 | 312.2 | 273 | 263.8 | 338.1 | 52.2 | 17.3 | 90.3 | 4.4 | 199.1 | 6.3 | 122.2 | 103.8 | 335.9 | 367.7 | 573.6 | 337.6 | 311.6 | 299.5 | 288.1 | 383.9 | 649.2 | 353.8 | 329.5 | 343.5 | 353.7 | 506.1 | 413.7 | 344 | 570.7 | 396.8 | 408.5 | 359.8 | 286.7 | 414.3 | 328.1 | 462.8 | 402.1
2202 | 1966 | -4.2 | 0 | 0 | 298.7 | 312.4 | 272.3 | 263.7 | 337.8 | 52.1 | 17.3 | 90.2 | 4.5 | 208.4 | 5.7 | 122 | 103.7 | 335.7 | 366.8 | 573 | 337 | 312.3 | 299.6 | 287.4 | 382.2 | 648.8 | 353.5 | 329.5 | 343.4 | 353.5 | 505.8 | 413.5 | 343.5 | 570.5 | 396.7 | 408.4 | 359 | 286.6 | 414.1 | 327.9 | 462.5 | 401.9
2203 | 1967 | -4.3 | 0 | 0 | 298.6 | 312.1 | 272.2 | 263.2 | 337.6 | 52.1 | 17.3 | 90.1 | 4.5 | 229.2 | 4.7 | 121.6 | 103.7 | 334.9 | 365.8 | 572.3 | 336.2 | 313.7 | 299.2 | 287.3 | 382 | 648.4 | 353 | 329.4 | 343.3 | 353.3 | 505.4 | 413.6 | 343.3 | 570.4 | 396.4 | 408.2 | 358.5 | 286.3 | 413.9 | 327.6 | 462.3 | 401.7
2204 | 1968 | -4.4 | 0 | 0 | 298 | 311.7 | 272.2 | 262.8 | 337.2 | 52 | 17.3 | 90 | 4.6 | 247.3 | 3.8 | 121.1 | 103.5 | 334 | 365 | 571.6 | 335.2 | 313.5 | 298.8 | 287.2 | 382.2 | 648.6 | 352.4 | 329.4 | 343.2 | 353.2 | 505.2 | 413.6 | 343.3 | 570.4 | 395.9 | 408 | 357.9 | 285.9 | 413.7 | 327.4 | 462 | 401.5
2205 | 1969 | -4.4 | 0 | 0 | 297.5 | 311.6 | 271.9 | 262.7 | 336.8 | 51.9 | 17.3 | 90 | 4.8 | 269.8 | 3.7 | 120.6 | 103.3 | 333.3 | 364.1 | 571.1 | 334.2 | 312.4 | 298.7 | 286.3 | 382.2 | 648.4 | 351.8 | 329.3 | 343.1 | 353 | 504.9 | 413.2 | 343.5 | 570.3 | 395.3 | 407.8 | 357 | 285.7 | 413.5 | 327.2 | 461.8 | 401.3
2206 | 1970 | -4.3 | 0 | 0 | 297.1 | 311.2 | 271.9 | 262.8 | 336.4 | 51.9 | 17.3 | 90 | 4.6 | 254.3 | 3.9 | 120.1 | 103.1 | 332.8 | 363.3 | 570.9 | 333.3 | 309.4 | 298.4 | 285.8 | 381.6 | 648.1 | 351.1 | 329.2 | 343 | 352.8 | 504.6 | 413.6 | 343.3 | 570.1 | 394.7 | 407.6 | 356.5 | 285.5 | 413.2 | 326.9 | 461.5 | 401.1
2207 | 1971 | -4.2 | 0 | 0 | 296.8 | 310.7 | 271.6 | 262.7 | 336.1 | 51.9 | 17.3 | 89.9 | 4.5 | 243.9 | 4.2 | 119.4 | 102.7 | 332.5 | 362.6 | 570.5 | 332.3 | 309.9 | 298.2 | 285.1 | 380.9 | 647.7 | 350.6 | 329.2 | 342.9 | 352.6 | 504.2 | 413.4 | 342.8 | 569.9 | 394.6 | 407.3 | 355.9 | 285.4 | 413 | 326.7 | 461.2 | 400.9
2208 | 1972 | -4 | 0 | 0 | 296.7 | 310.2 | 271.4 | 262.6 | 335.6 | 51.8 | 17.3 | 89.8 | 4.3 | 244.4 | 4.4 | 119 | 102.2 | 332.5 | 362.1 | 570.2 | 331.5 | 311.4 | 298.1 | 284.2 | 380.8 | 647.3 | 350.1 | 329.1 | 342.7 | 352.4 | 503.9 | 412 | 342.5 | 569.6 | 394.7 | 407.1 | 355.4 | 285.3 | 412.9 | 326.4 | 461 | 400.7