## IS Test Matrix
Intermediate Scale Test Matrix - Revision F (12-06-06)
|  | Comments: 1) All tests were conducted as open burns with a Propene (Propylene) gas sand burner 2) Colors identify test conditions grouped into the same test run | [14 empty] | ACTUAL TEST CONDITIONS
Burn Test # | Rev. E Test # | Loc. | Cable Insulation Material | [8 empty] | Number of Conductors |  |  |  | Conductor Size (AWG) |  |  |  |  | Cable Bundle Size |  |  |  |  | Water Spary Optionsl | Raceway Type
|  |  | Thermoset | [5 empty] | Thermoplastic
|  |  | XLPE | EPR | Silicone | XLPO | TS/TP | Vita-Link | PE | PVC | Tefzel | 3 | 2 | 7 | 12 | 8 | 12 | 14 | 16 | 18 | 1 | 3 | 6 | 12 | Load Tr | * | 12" Tray | 2.5" Cnd | Air Drop
Prelim 1 | Prelim 1 | A | X | [8 empty] | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | A | X | [10 empty] | X |  |  | X |  |  |  | X | [5 empty] | X
Prelim 2 | Prelim 2 | A | X | [8 empty] | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | A | X | [10 empty] | X |  |  | X |  |  |  | X | [5 empty] | X
Prelim 3 | Prelim 3 | A | [7 empty] | X |  | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | A | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [5 empty] | X
Prelim 4 | Prelim 4 | A | [7 empty] | X |  | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | A | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [5 empty] | X
1 | 15 | A | X | [9 empty] | X | X | X |  | X |  | X | X |  |  |  |  | X |  | X
|  | B | X | [10 empty] | X |  |  | X | [6 empty] | X |  |  | X
|  | D | X | [10 empty] | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | E | X | [10 empty] | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | [10 empty] | X |  |  | X | [6 empty] | X |  |  | X
2 | 1 | A | X | [10 empty] | X |  |  | X | [6 empty] | X |  |  | X
|  | C | X | [10 empty] | X |  |  | X | [5 empty] | X |  |  |  | X
|  | A | X | [5 empty] | X |  |  |  |  | X |  |  | X | [6 empty] | X |  |  | X
|  | C | X | [5 empty] | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
| 11 | C - A | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [7 empty] | X
|  | E | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [5 empty] | X
|  | G | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [5 empty] | X
3 | 2 | A | X | X | [9 empty] | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X | [9 empty] | X |  |  | X | [5 empty] | X |  |  |  | X
| 3 | A |  | X |  |  |  |  | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C |  | X |  |  |  |  | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
| 10 | E | [7 empty] | X |  | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | [7 empty] | X |  | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
4 | 5 | A | X | X |  | X | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X |  | X | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
| 6 | A | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
| 9 | C - A | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [7 empty] | X
|  | E | X | [8 empty] | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | [8 empty] | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
5 | 4 | A | X | X | X | X |  |  | X |  | X |  |  | X |  |  | X | [6 empty] | X |  | X | X
|  | C | X | X | X | X |  |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
| 7 | A | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | X | [5 empty] | X |  | X | X
|  | C | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | X |  |  |  |  | X |  |  | X | X
|  | C - A | X | [10 empty] | X |  |  | X |  |  |  | X | [7 empty] | X
|  | E |  | X | [9 empty] | X |  |  | X |  |  |  | X | [5 empty] | X
|  | G |  | X | [9 empty] | X |  |  | X |  |  |  | X | [5 empty] | X
6 | 12 | A | X | X | X | X |  |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | C | X | X | X | X |  |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | E | X | [5 empty] | X |  | X |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
| 13 | C - A | X | [5 empty] | X |  | X |  |  | X |  |  | X |  |  |  |  | X | [6 empty] | X
|  | A |  | X | X | X | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | C |  | X | X | X | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | G |  |  |  |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  |  |  | X
7 | 14 | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | A | X | X |  | X | X |  |  | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C |  | X |  | X | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | E | X | [5 empty] | X | X |  |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G |  | X |  | X | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
8 | 16 | A | X | [5 empty] | X | X |  |  | X | X | X |  | X |  | X | X |  |  | X |  |  |  | X
|  | A | X | [5 empty] | X | X |  |  | X | X | X |  | X |  | X | X |  |  | X |  |  |  | X
|  | C | X | [5 empty] | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | E | X | [5 empty] | X |  |  |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | [5 empty] | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
9 | 19 | A | X | X | X |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | A | X | X | X |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | C | X | X | X |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | E | X | [5 empty] | X |  | X |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | X | X |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
10 | 20 | A | X | X | X | X | X |  |  |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | A | X | X | X | X | X |  |  |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | C | X | X | X | X | X |  |  | X |  |  |  | X | X |  | X |  |  | X |  |  | X |  |  | X | X
|  | E |  |  |  |  | X |  | X |  | X |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | X |  |  | X |  | X | X | X |  | X | X |  |  | X |  | X |  |  |  | X |  |  |  | X
11 | 21 | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X |  | X | X |  |  | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | E |  |  |  |  | X |  | X | X |  |  |  | X |  |  | X |  |  |  |  | X | [6 empty] | X
|  | G | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
12 | 24 | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X |  | X | X |  |  | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | E |  |  |  |  | X |  | X | X |  |  |  | X |  |  | X |  |  |  |  | X | [6 empty] | X
|  | G | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
13 | 25 | A | X | X |  | X | X | X | X |  | X |  |  | X |  |  | X | [7 empty] | X | X | X
|  | C | X | X |  | X | X | X | X |  | X |  |  | X |  |  | X | [7 empty] | X | X | X
|  | E | X | X | [9 empty] | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | F | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | F | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | G | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | G | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
14 | 27 | A | X | X |  | X | X |  | X | X | X |  |  | X |  |  | X | [7 empty] | X |  | X
|  | C | X | X |  | X | X |  | X | X | X |  |  | X |  |  | X | [7 empty] | X |  | X
|  | E |  |  |  |  | X |  | X | X |  |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | F | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | F | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | G | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | G | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X

## Shorting Summary
Shorting Sequence for Open Burn Test 2, Location C, IRMS #1
Test conditions: Cable: Bundle of 6, 7-conductor, 12 AWG, XLPE/CSPE Rocbestos Firewall III control cables (Item 10). Cable specimens present: Six lengths of cable were monitored for electrical performance (A, B, C, D, E, & F [See Elect. Conn. Map]), a second bundle of 6 cables was monitored for temperature response. Raceway: 12" B-Line Series 2 tray (part number 248P09-12-144) located at position C in the Test Cell chamber with chamber end walls open and un-heated. Exposure conditions: Gas burner flow rate set to a nominal 250 kW heat release rate. Electrical repsonse monitoring: IRMS system using 12 channels - two for each cable (see electrical connection map), cable tray was grounded. Thermal response monitoring: Four cable bundle temperatures (see thermocouple map) and the cable tray rung temperature. Gas burner initiated: Following 221 seconds of baseline data monitoring.
DAQ Time | Burner Time | Event | Interpretation
221 |  | Ignited Gas Burner
858-864 |  | Conductors D7 & D8 both short to ground at less than 100 ohms (26 & 8) | Cable D shorts to ground
883 |  | Conductors D7 & D8 short together at less than 100 ohms (75) | Cable D shorted internally
1246-1249 |  | Conductors E9 & E10 both short to ground at less than 100 ohms (6 & 8) | Cable E shorts to ground
1267 |  | Conductor F11 shorts to ground at less than 1000 ohms (608)
1277 |  | Conductors E9 & E10 short together at less than 100 ohms (28) | Cable E shorted internally
1451 |  | The existing ground fault on conductor F11 decreases to less than 100 ohms (5)
1479 |  | Conductors A1 & A2 short together at less than 100 ohms (14) | Cable A shorted internally
1535 |  | Conductor B3 shorts to ground at less than 100 ohms (51)
1538 |  | Conductors B3 & B4 short together at less than 100 ohms (52) | Cable B shorted internally
1550 |  | Conductor B4 shorts to ground at less than 100 ohms (38) | Cable B shorts to ground
1585 |  | Conductors C5 & C6 short together at less than 1000 ohms (235) | Cable C shorted internally
1749-1758 |  | Conductors C5 & C6 both short to ground at less than 100 ohms (33 & 43) | Cable C shorts to ground
1770 |  | The existing internal fault on conductors C5 & C6 decreases to less than 100 ohms (10)
1854-1876 |  | Conductors A1 & A2 both short to ground (108 & 68) | Cable A shorts to ground
1994 |  | Gas burner is shut off
2039 |  | The existing ground fault on conductor A1 decreases to less than 100 ohms (31)
Additional Observations
Observation 1 | The progression of cable failure began with the bottom three cables (D, E & F) and moved up the bundle to the top cables.
Observation 2 | No cable to cable interactions took place during this test.

## Thermocouple Map
Thermocouple map for TC's on and within the cable
|  |  |  | All Cables = | XLPE | (Item #10)
Translation to data file names used in "PenTemps" WorkSheet:
| Map Name |  | Location
| C1 | = | Center of bundle, under jacket
| C2 | = | Air above bundle
| C3 | = | Air below bundle
| C4 | = | Intra-bundle, center

## Elect Conn Map
Electrical connection map within the cables
|  |  |  | All Cables = | XLPE | (Item #10)
Cable tray rung below D-E-F
Cable Bundle Arrangement
Cable 7-Conductor Arrangement
| Lt Blue = | Even conductor set
| Lt Red = | Odd conductor set
| Gray = | Center conductor (not connected)
IRMS Electrical Connections

## C-C Individuals
Conductor to Conductor Resistances
Open Burn Test 2 |  |  | 2006-10-24 | 13:08
XLPE | 7-C | Tray C | IRMS | 1
0 | 250 kW
Burner Time | A1-A2 | Burner Time | A1-B3 | Burner Time | A1-B4 | Burner Time | A1-C5 | Burner Time | A1-C6 | Burner Time | A2-B3 | Burner Time | A2-B4 | Burner Time | A2-C5 | Burner Time | A2-C6 | Burner Time | B3-B4 | Burner Time | B3-C5 | Burner Time | B3-C6 | Burner Time | B3-D7 | Burner Time | B3-D8 | Burner Time | B3-E9 | Burner Time | B3-E10 | Burner Time | B4-C5 | Burner Time | B4-C6 | Burner Time | B4-D7 | Burner Time | B4-D8 | Burner Time | B4-E9 | Burner Time | B4-E10 | Burner Time | C5-C6 | Burner Time | C5-E9 | Burner Time | C5-E10 | Burner Time | C5-F11 | Burner Time | C5-F12 | Burner Time | C6-E9 | Burner Time | C6-E10 | Burner Time | C6-F11 | Burner Time | C6-F12 | Burner Time | D7-D8 | Burner Time | D7-E9 | Burner Time | D7-E10 | Burner Time | D8-E9 | Burner Time | D8-E10 | Burner Time | E9-E10 | Burner Time | E9-F11 | Burner Time | E9-F12 | Burner Time | E10-F11 | Burner Time | E10-F12 | Burner Time | F11-F12
-220.5 | 231937.9994 | -217.5 | 257137.9994 | -215 | 252137.9994 | -212 | 241637.9994 | -209.5 | 236137.9994 | -189.5 | 250037.9994 | -186.5 | 225237.9994 | -184 | 231337.9994 | -181.5 | 237337.9994 | -161.5 | 250337.9994 | -159 | 254337.9994 | -156 | 253337.9994 | -153.5 | 261537.9994 | -150.5 | 255037.9994 | -147.5 | 254037.9994 | -145 | 261737.9994 | -136.5 | 255437.9994 | -133.5 | 253337.9994 | -131 | 253137.9994 | -128 | 258837.9994 | -125.5 | 255837.9994 | -122.5 | 257337.9994 | -114 | 239837.9994 | -105.5 | 259337.9994 | -103 | 259837.9994 | -100 | 258537.9994 | -97.5 | 235237.9994 | -89 | 249337.9994 | -86 | 260737.9994 | -83.5 | 256937.9994 | -80.5 | 238337.9994 | -77.5 | 258637.9994 | -75 | 258237.9994 | -72 | 253037.9994 | -63.5 | 260237.9994 | -61 | 260837.9994 | -52.5 | 261337.9994 | -49.5 | 261637.9994 | -47 | 261437.9994 | -44 | 255037.9994 | -41.5 | 257037.9994 | -38.5 | 254737.9994
-35.5 | 231937.9994 | -33 | 257137.9994 | -30 | 252137.9994 | -27.5 | 241637.9994 | -24.5 | 236137.9994 | -5 | 250037.9994 | -2 | 225237.9994 | 0.5 | 231337.9994 | 3.5 | 237337.9994 | 23 | 250337.9994 | 26 | 254337.9994 | 28.5 | 253337.9994 | 31.5 | 261537.9994 | 34.5 | 127468.9988 | 37 | 254037.9994 | 40 | 261737.9994 | 48.5 | 255437.9994 | 51 | 253337.9994 | 54 | 253137.9994 | 56.5 | 258837.9994 | 59.5 | 255837.9994 | 62.5 | 257337.9994 | 70.5 | 239837.9994 | 79 | 259337.9994 | 81.5 | 259837.9994 | 84.5 | 258537.9994 | 87.5 | 235237.9994 | 96 | 249337.9994 | 98.5 | 260737.9994 | 101.5 | 256937.9994 | 104.5 | 238337.9994 | 107 | 258637.9994 | 110 | 258237.9994 | 112.5 | 253037.9994 | 121 | 260237.9994 | 124 | 260837.9994 | 132.5 | 261337.9994 | 135 | 261637.9994 | 138 | 261437.9994 | 140.5 | 255037.9994 | 143.5 | 257037.9994 | 146 | 254737.9994
149 | 231937.9994 | 151.5 | 257137.9994 | 154.5 | 252137.9994 | 157.5 | 241637.9994 | 160.5 | 236137.9994 | 180 | 250037.9994 | 182.5 | 225237.9994 | 185.5 | 231337.9994 | 188.5 | 237337.9994 | 207.5 | 250337.9994 | 210.5 | 254337.9994 | 213.5 | 253337.9994 | 216.5 | 261537.9994 | 219 | 255037.9994 | 222 | 254037.9994 | 224.5 | 261737.9994 | 233 | 255437.9994 | 236 | 253337.9994 | 238.5 | 253137.9994 | 241.5 | 258837.9994 | 244.5 | 255837.9994 | 247 | 257337.9994 | 255.5 | 239837.9994 | 264 | 259337.9994 | 266.5 | 259837.9994 | 269.5 | 258537.9994 | 272.5 | 235237.9994 | 280.5 | 249337.9994 | 283.5 | 260737.9994 | 286.5 | 256937.9994 | 289 | 238337.9994 | 291.5 | 258637.9994 | 294.5 | 258237.9994 | 297.5 | 253037.9994 | 306 | 260237.9994 | 308.5 | 260837.9994 | 317 | 261337.9994 | 320 | 261637.9994 | 322.5 | 261437.9994 | 325.5 | 255037.9994 | 328 | 257037.9994 | 331 | 254737.9994
333.5 | 231937.9994 | 336.5 | 257137.9994 | 339.5 | 252137.9994 | 342 | 241637.9994 | 345 | 236137.9994 | 364.5 | 250037.9994 | 367.5 | 225237.9994 | 370 | 231337.9994 | 373 | 237337.9994 | 392.5 | 250337.9994 | 395.5 | 254337.9994 | 398.5 | 253337.9994 | 401 | 261537.9994 | 403.5 | 255037.9994 | 406.5 | 254037.9994 | 409.5 | 261737.9994 | 418 | 255437.9994 | 420.5 | 253337.9994 | 423.5 | 253137.9994 | 426.5 | 258837.9994 | 429 | 255837.9994 | 431.5 | 257337.9994 | 440 | 239837.9994 | 448.5 | 259337.9994 | 451.5 | 259837.9994 | 454.5 | 258537.9994 | 457 | 235237.9994 | 465.5 | 249337.9994 | 468.5 | 260737.9994 | 471 | 256937.9994 | 473.5 | 238337.9994 | 476.5 | 258637.9994 | 479.5 | 258237.9994 | 482 | 253037.9994 | 490.5 | 260237.9994 | 493.5 | 260837.9994 | 502 | 261337.9994 | 504.5 | 261637.9994 | 507.5 | 261437.9994 | 510.5 | 255037.9994 | 513 | 257037.9994 | 515.5 | 254737.9994
518.5 | 231937.9994 | 521.5 | 257137.9994 | 524 | 252137.9994 | 527 | 241637.9994 | 530 | 236137.9994 | 549.5 | 250037.9994 | 552.5 | 225237.9994 | 555 | 231337.9994 | 558 | 237337.9994 | 577.5 | 250337.9994 | 580.5 | 254337.9994 | 583 | 253337.9994 | 585.5 | 261537.9994 | 588.5 | 255037.9994 | 591.5 | 254037.9994 | 594 | 261737.9994 | 602.5 | 510975.9997 | 605.5 | 253337.9994 | 608.5 | 253137.9994 | 611 | 258837.9994 | 614 | 255837.9994 | 616.5 | 257337.9994 | 625 | 239837.9994 | 633.5 | 259337.9994 | 636 | 259837.9994 | 639 | 258537.9994 | 642 | 235237.9994 | 650.5 | 249337.9994 | 653 | 260737.9994 | 656 | 256937.9994 | 658.5 | 238337.9994 | 661.5 | 74.7545 | 664.5 | 52917.5082 | 667 | 54316.5342 | 675.5 | 65912.6722 | 678 | 19030.704 | 686.5 | 261337.9994 | 689.5 | 261637.9994 | 692.5 | 261437.9994 | 695 | 255037.9994 | 698 | 257037.9994 | 700.5 | 254737.9994
703.5 | 231937.9994 | 706 | 257137.9994 | 709 | 252137.9994 | 712 | 241637.9994 | 714.5 | 236137.9994 | 734 | 250037.9994 | 737 | 225237.9994 | 739.5 | 231337.9994 | 742.5 | 237337.9994 | 762.5 | 250337.9994 | 765 | 254337.9994 | 767.5 | 253337.9994 | 770.5 | 261537.9994 | 773.5 | 127468.9988 | 776.5 | 254037.9994 | 779 | 261737.9994 | 787.5 | 255437.9994 | 790 | 253337.9994 | 793 | 253137.9994 | 795.5 | 258837.9994 | 798.5 | 255837.9994 | 801.5 | 257337.9994 | 809.5 | 239837.9994 | 818 | 259337.9994 | 821 | 259837.9994 | 823.5 | 258537.9994 | 826.5 | 235237.9994 | 835 | 249337.9994 | 838 | 260737.9994 | 840.5 | 256937.9994 | 843.5 | 238337.9994 | 846 | 1.4672 | 849 | 15126.2805 | 851.5 | 1537.3924 | 860 | 7931.9018 | 863 | 21921.1853 | 871.5 | 261337.9994 | 874 | 261637.9994 | 877 | 261437.9994 | 879.5 | 255037.9994 | 882.5 | 257037.9994 | 885.5 | 254737.9994
888 | 231937.9994 | 891 | 257137.9994 | 893.5 | 252137.9994 | 896.5 | 241637.9994 | 899.5 | 236137.9994 | 919 | 250037.9994 | 921.5 | 225237.9994 | 924.5 | 231337.9994 | 927.5 | 237337.9994 | 947 | 250337.9994 | 949.5 | 254337.9994 | 952.5 | 253337.9994 | 955.5 | 261537.9994 | 958 | 255037.9994 | 961 | 254037.9994 | 963.5 | 261737.9994 | 972 | 255437.9994 | 975 | 253337.9994 | 977.5 | 253137.9994 | 980.5 | 129368.9988 | 983.5 | 255837.9994 | 986 | 257337.9994 | 994.5 | 239837.9994 | 1003 | 259337.9994 | 1005.5 | 259837.9994 | 1008.5 | 258537.9994 | 1011.5 | 235237.9994 | 1019.5 | 249337.9994 | 1022.5 | 260737.9994 | 1025.5 | 256937.9994 | 1028 | 238337.9994 | 1031 | 7962.192 | 1033.5 | 20.6214 | 1036.5 | 0.065083 | 1045 | 24.7494 | 1047.5 | 7.9984 | 1056 | 27.9978 | 1059 | 21.4648 | 1061.5 | 26.3909 | 1064.5 | 7.0879 | 1067.5 | 12.5001 | 1070 | 607.6636
1073 | 231937.9994 | 1075.5 | 257137.9994 | 1078.5 | 252137.9994 | 1081.5 | 241637.9994 | 1084 | 236137.9994 | 1103.5 | 250037.9994 | 1106.5 | 225237.9994 | 1109.5 | 231337.9994 | 1112 | 237337.9994 | 1131.5 | 14631.6367 | 1134.5 | 254337.9994 | 1137.5 | 253038.1184 | 1140 | 87112.6648 | 1143 | 50927.5969 | 1145.5 | 31667.2451 | 1148.5 | 23703.4478 | 1157 | 253738.6653 | 1159.5 | 251938.5524 | 1162.5 | 15727.3652 | 1165.5 | 14285.4335 | 1168 | 12087.511 | 1171 | 8481.2484 | 1179.5 | 239837.9994 | 1187.5 | 259337.9994 | 1190.5 | 259837.9994 | 1193.5 | 258537.9994 | 1196 | 235237.9994 | 1204.5 | 249337.9994 | 1207.5 | 260737.9994 | 1210 | 256937.9994 | 1213 | 238337.9994 | 1215.5 | 20.2305 | 1218.5 | 22.8106 | 1221.5 | 8.1253 | 1229.5 | 26.9422 | 1232.5 | 27.4296 | 1241 | 19.2659 | 1243.5 | 1.7848 | 1246.5 | 28.4355 | 1249.5 | 4.8423 | 1252 | 5.6756 | 1255 | 21.4869
1257.5 | 13.5804 | 1260.5 | 128518.9988 | 1263.5 | 252137.9994 | 1266 | 241637.9994 | 1269 | 236137.9994 | 1288.5 | 250037.9994 | 1291.5 | 225237.9994 | 1294 | 231337.9994 | 1297 | 237337.9994 | 1316.5 | 51.597 | 1319.5 | 85370.8418 | 1322 | 155976.4315 | 1325 | 123.2921 | 1327.5 | 61.5498 | 1330.5 | 63.7618 | 1333.5 | 70.6529 | 1341.5 | 71210.1223 | 1344.5 | 69710.4832 | 1347.5 | 52.9398 | 1350 | 61.2675 | 1353 | 58.1837 | 1355.5 | 45.7011 | 1364 | 235.4886 | 1372.5 | 129618.9988 | 1375.5 | 86545.9982 | 1378 | 86112.6648 | 1381 | 46967.5969 | 1389.5 | 19087.5305 | 1392 | 15243.4014 | 1395 | 11583.532 | 1397.5 | 9834.902 | 1400.5 | 17.6322 | 1403.5 | 19.8127 | 1406 | 4.5913 | 1414.5 | 1.937 | 1417.5 | 23.5748 | 1425.5 | 14.5083 | 1428.5 | 1.2903 | 1431.5 | 12.4584 | 1434 | 15.5422 | 1437 | 3.9386 | 1439.5 | 5.8045
1442.5 | 24.9046 | 1445.5 | 42772.9963 | 1448 | 27926.4389 | 1451 | 11986.8878 | 1453.5 | 10171.2033 | 1473.5 | 5111.179 | 1476 | 4318.361 | 1479 | 2622.7481 | 1481.5 | 2693.3363 | 1501.5 | 241.9176 | 1504 | 37827.8136 | 1507 | 33.7321 | 1509.5 | 8.0129 | 1512.5 | 15.326 | 1515.5 | 25.848 | 1518 | 19.2256 | 1526.5 | 42777.7428 | 1529.5 | 35.0476 | 1532 | 5.2677 | 1535 | 5.6115 | 1537.5 | 33.9027 | 1540.5 | 6.6682 | 1549 | 9.5183 | 1557.5 | 108.4672 | 1560 | 61.5867 | 1563 | 85.4912 | 1565.5 | 35.8546 | 1574 | 42.0443 | 1576.5 | 44.9556 | 1579.5 | 72.183 | 1582.5 | 43.0609 | 1585.5 | 7.4459 | 1588 | 4.7398 | 1591 | 24.7122 | 1599.5 | 0.9462 | 1602 | 21.2057 | 1610.5 | 14.0424 | 1613.5 | 0.88166 | 1616 | 16.08 | 1619 | 25.0727 | 1621.5 | 8.5547 | 1624.5 | 6.1257
1627 | 26.6698 | 1630 | 158.7069 | 1633 | 146.1843 | 1635.5 | 10205.2667 | 1638.5 | 7812.2332 | 1658 | 135.7794 | 1661 | 84.5685 | 1663.5 | 5607.5363 | 1666.5 | 4362.8571 | 1686 | 10.1831 | 1689 | 0.20362 | 1691.5 | 16.1787 | 1694.5 | 1.251 | 1697.5 | 4.2172 | 1700 | 15.626 | 1703 | 17.8385 | 1711 | 28.0485 | 1714 | 13.0145 | 1716.5 | 5.2677 | 1719.5 | 21.2552 | 1722 | 23.2283 | 1725 | 9.3066 | 1733.5 | 106.5644 | 1742 | 29.6204 | 1744.5 | 12.9713 | 1747.5 | 7.126 | 1750.5 | 0.2429 | 1759 | 28.403 | 1761.5 | 11.5066 | 1764.5 | 29.6757 | 1767 | 7.0877 | 1770 | 21.8673 | 1773 | 0.44907 | 1775.5 | 5.5913 | 1784 | 7.2845 | 1786.5 | 10.3737 | 1795 | 0.9556 | 1798 | 0.95815 | 1801 | 22.6635 | 1803.5 | 1.7444 | 1806.5 | 0.0095047 | 1809 | 21.5467
1812 | 30.1789 | 1815 | 32.2452 | 1817.5 | 32.448 | 1820.5 | 48.232 | 1823.5 | 30.2916 | 1842.5 | 42.7785 | 1845.5 | 32.3043 | 1848.5 | 35.1829 | 1851 | 37.2383 | 1870.5 | 20.4933 | 1873.5 | 20.5236 | 1876.5 | 0.88672 | 1879.5 | 14.8577 | 1882 | 0.45612 | 1884.5 | 22.4744 | 1887.5 | 23.1035 | 1896 | 0.90493 | 1898.5 | 0.88672 | 1901.5 | 26.5589 | 1904.5 | 12.2783 | 1907 | 13.201 | 1910 | 0.92132 | 1918.5 | 6.2719 | 1926.5 | 32.6858 | 1929.5 | 8.4195 | 1932.5 | 15.0952 | 1935.5 | 9.0297 | 1943.5 | 18.6523 | 1946.5 | 7.6319 | 1949 | 4.3818 | 1952 | 20.2053 | 1954.5 | 10.3037 | 1957.5 | 0.92906 | 1960.5 | 12.8269 | 1968.5 | 20.003 | 1971.5 | 26.6654 | 1980 | 3.9045 | 1983 | 0.67852 | 1985.5 | 0.95645 | 1988.5 | 8.7975 | 1991 | 6.6342 | 1994 | 5.3035
1996.5 | 28.5461 | 1999.5 | 22.9452 | 2002.5 | 30.9655 | 2005 | 9.3526 | 2008 | 36.7011 | 2027.5 | 13.7316 | 2030.5 | 1.1305 | 2033.5 | 20.6495 | 2036 | 24.6763 | 2055.5 | 9.6823 | 2058.5 | 21.7733 | 2061 | 8.3513 | 2064 | 12.3015 | 2066.5 | 26.0268 | 2069.5 | 5.6012 | 2072.5 | 6.4489 | 2080.5 | 7.634 | 2083.5 | 24.1685 | 2086.5 | 15.702 | 2089 | 19.4644 | 2092 | 0.42388 | 2094.5 | 7.0376 | 2103 | 214.9521 | 2111.5 | 14.0879 | 2114.5 | 17.411 | 2117 | 18.5895 | 2120 | 13.0964 | 2128.5 | 14.3786 | 2131 | 22.8071 | 2134 | 28.7409 | 2137 | 0.75394 | 2139.5 | 2.3907 | 2142.5 | 23.1729 | 2145 | 17.6002 | 2153.5 | 28.3594 | 2156.5 | 18.5879 | 2164.5 | 3.1764 | 2167.5 | 0.35513 | 2170.5 | 6.7321 | 2173 | 15.2721 | 2176 | 0.4365 | 2178.5 | 0.81808
2181.5 | 47.3736 | 2184.5 | 31.1373 | 2187 | 25.5379 | 2190 | 15.12 | 2192.5 | 33.8471 | 2212.5 | 40.6437 | 2215 | 28.9697 | 2218 | 24.3829 | 2220.5 | 5.4526 | 2240.5 | 15.6654 | 2243 | 0.8954 | 2246 | 6.1793 | 2248.5 | 30.7299 | 2251.5 | 27.5831 | 2254.5 | 1.9343 | 2257 | 2.7434 | 2265.5 | 29.8547 | 2268.5 | 28.7777 | 2271 | 0.88499 | 2274 | 17.9459 | 2276.5 | 6.7288 | 2279.5 | 28.2823 | 2288 | 138.7592 | 2296.5 | 8.7744 | 2299 | 22.8563 | 2302 | 5.6671 | 2304.5 | 18.0137 | 2313 | 23.8136 | 2316 | 27.7656 | 2318.5 | 4.8257 | 2321.5 | 13.6991 | 2324.5 | 0.39618 | 2327 | 0.56948 | 2330 | 14.5723 | 2338.5 | 7.1925 | 2341 | 26.6654 | 2349.5 | 3.219 | 2352.5 | 0.40503 | 2355 | 17.4832 | 2358 | 6.6221 | 2360.5 | 7.4225 | 2363.5 | 10.578
2366.5 | 14.108 | 2369 | 20.5089 | 2372 | 41.3457 | 2374.5 | 15.6321 | 2377.5 | 22.7152 | 2397 | 38.7278 | 2400 | 0.63346 | 2402.5 | 16.7017 | 2405.5 | 8.968 | 2425 | 0.86057 | 2428 | 3.2672 | 2430.5 | 16.8434 | 2433.5 | 9.9967 | 2436.5 | 14.5754 | 2439 | 5.3732 | 2442 | 5.5098 | 2450.5 | 30.7421 | 2453 | 0.43838 | 2456 | 1.3556 | 2458.5 | 5.2535 | 2461.5 | 25.279 | 2464.5 | 2.1644 | 2472.5 | 35.3368 | 2481 | 7.1384 | 2484 | 25.2359 | 2486.5 | 38.5227 | 2489.5 | 3.6466 | 2498 | 27.7945 | 2500.5 | 8.8943 | 2503.5 | 37.7344 | 2506.5 | 14.3188 | 2509 | 4.3745 | 2512 | 11.1148 | 2514.5 | 15.492 | 2523 | 0.50976 | 2526 | 0.95133 | 2534.5 | 9.0061 | 2537 | 17.3559 | 2540 | 28.9567 | 2542.5 | 7.3692 | 2545.5 | 2.298 | 2548.5 | 1.4117
2551 | 3.8441 | 2554 | 12.3405 | 2556.5 | 34.6972 | 2559.5 | 13.1699 | 2562.5 | 24.9847 | 2582 | 35.1199 | 2584.5 | 20.1456 | 2587.5 | 32.3344 | 2590.5 | 31.9287 | 2610 | 12.5972 | 2612.5 | 15.2756 | 2615.5 | 26.9208 | 2618.5 | 3.6839 | 2621 | 20.3879 | 2625 | 12.2923 | 2626.5 | 7.9111 | 2635 | 15.834 | 2638 | 3.2052 | 2640.5 | 0.18186 | 2643.5 | 2.6408 | 2646.5 | 4.1493 | 2649 | 10.5254 | 2657.5 | 1.4865 | 2666 | 18.0095 | 2668.5 | 17.3562 | 2671.5 | 9.2442 | 2674.5 | 0.72584 | 2682.5 | 11.3638 | 2685.5 | 24.0114 | 2688.5 | 30.4196 | 2691 | 1.5837 | 2694 | 6.7995 | 2696.5 | 24.767 | 2699.5 | 5.6831 | 2708 | 20.8082 | 2710.5 | 17.8128 | 2719 | 11.8657 | 2722 | 13.9172 | 2724.5 | 22.8418 | 2727.5 | 0.41544 | 2730.5 | 12.7559 | 2733 | 0.89887
2736 | 1.6163 | 2738.5 | 15.2616 | 2741.5 | 28.8352 | 2744.5 | 9525.9812 | 2747 | 3501.4538 | 2766.5 | 35.0451 | 2769.5 | 0.03671 | 2772.5 | 2941.8429 | 2775 | 3076.0091 | 2794.5 | 1720.0561 | 2797.5 | 15.2756 | 2800.5 | 10.5104 | 2803 | 18.1324 | 2806 | 15.6506 | 2808.5 | 20.1451 | 2811.5 | 32.8081 | 2819.5 | 24.2668 | 2822.5 | 16.0687 | 2825.5 | 9.1374 | 2828.5 | 4.9421 | 2831 | 24.1523 | 2834 | 6.4386 | 2842.5 | 6.4078 | 2850.5 | 21.4331 | 2853.5 | 37.043 | 2856.5 | 12.4501 | 2859 | 7.1259 | 2867.5 | 19.6509 | 2870.5 | 45.4515 | 2873 | 14.4276 | 2876 | 4.5035 | 2878.5 | 0.93249 | 2881.5 | 10.4734 | 2884.5 | 1.3574 | 2892.5 | 28.0346 | 2895.5 | 10.9098 | 2904 | 3.3042 | 2906.5 | 23.5352 | 2909.5 | 23.5601 | 2912.5 | 0.98669 | 2915 | 0.91873 | 2917.5 | 1.0753
2920.5 | 3.6078 | 2923.5 | 16.8875 | 2926.5 | 25.4094 | 2929 | 383.9127 | 2932 | 599.4633 | 2951.5 | 34.8212 | 2954.5 | 31.5139 | 2957 | 562.5608 | 2960 | 1843.7577 | 2979.5 | 152.2345 | 2982 | 26.1266 | 2985 | 25.7544 | 2988 | 13.5657 | 2990.5 | 22.1118 | 2993.5 | 18.8686 | 2996.5 | 7.0383 | 3004.5 | 21.8241 | 3007.5 | 25.8186 | 3010.5 | 17.141 | 3013 | 19.807 | 3016 | 33.0455 | 3018.5 | 12.633 | 3027 | 27.4633 | 3035.5 | 26.4991 | 3038.5 | 24.4943 | 3041 | 39.2102 | 3044 | 24.5719 | 3052 | 30.8239 | 3055 | 20.8111 | 3058 | 22.2461 | 3060.5 | 11.8784 | 3063.5 | 5.082 | 3066.5 | 27.1703 | 3069 | 17.7698 | 3077.5 | 18.8706 | 3080.5 | 0.73113 | 3088.5 | 2.2904 | 3091.5 | 5.7801 | 3094.5 | 5.4315 | 3097 | 0.17072 | 3100 | 16.5676 | 3102.5 | 9.1516

## C-G Min
Minimum Conductor to Ground Resistances
Open Burn Test 2 |  |  | 2006-10-24 | 13:08
XLPE | 7-C | Tray C | IRMS | 1
0 | 250 kW
Burner Time | A1-G |  | Burner Time | A2-G | Burner Time | B3-G | Burner Time | B4-G | Burner Time | C5-G | Burner Time | C6-G | Burner Time | D7-G | Burner Time | D8-G | Burner Time | E9-G | Burner Time | E10-G | Burner Time | F11-G | Burner Time | F12-G
-214.9 | 231938 |  | -192.4 | 225238 | -164.4444 | 250038 | -148.8889 | 225238 | -134.6111 | 231338 | -125.9444 | 236138 | -101.8 | 253038 | -96.1 | 255038 | -83.8889 | 249338 | -80.8333 | 253038 | -63.1 | 254738 | -61 | 235238
-30.1 | 231938 |  | -7.7 | 225238 | 20.2778 | 127469 | 35.8889 | 225238 | 50.0556 | 231338 | 58.8333 | 236138 | 83 | 253038 | 88.6 | 255038 | 100.8889 | 249338 | 103.9444 | 253038 | 121.5 | 254738 | 123.9 | 235238
154.6 | 231938 |  | 177.1 | 225238 | 205 | 250038 | 220.5556 | 225238 | 234.9444 | 231338 | 243.7222 | 236138 | 267.7 | 253038 | 273.3 | 255038 | 285.6667 | 249338 | 288.6667 | 253038 | 306.5 | 254738 | 308.6 | 235238
339.3 | 231938 |  | 361.7 | 225238 | 389.7778 | 250038 | 405.3889 | 225238 | 419.6667 | 231338 | 428.3889 | 236138 | 452.5 | 253038 | 458.1 | 255038 | 470.3889 | 249338 | 473.5556 | 253038 | 491.2 | 254738 | 493.3 | 235238
524.2 | 231938 |  | 546.7 | 225238 | 574.6111 | 250038 | 590.2222 | 225238 | 604.5 | 231338 | 613.2778 | 236138 | 637.4 | 25.847 | 642.9 | 7.9181 | 655.3333 | 249338 | 658.2222 | 253037.9999 | 676 | 254738 | 678.3 | 235238
709 | 231938 |  | 731.3 | 225238 | 759.3889 | 127469 | 774.9444 | 225238 | 789.1667 | 231338 | 797.8889 | 236138 | 822 | 0.65155 | 827.6 | 3.1872 | 839.9444 | 129069 | 843.0556 | 130368.9999 | 860.6 | 254738 | 863 | 235238
893.7 | 231938 |  | 916.1 | 225238 | 944.1111 | 250038 | 959.6111 | 129369 | 973.9444 | 231338 | 982.7222 | 236138 | 1006.8 | 1.4581 | 1012.4 | 6.0424 | 1024.6667 | 6.2171 | 1027.7222 | 8.408 | 1045.5 | 607.8833 | 1047.7 | 130669
1078.5 | 231938 |  | 1100.9 | 225238 | 1128.8333 | 14631.6471 | 1144.4444 | 8481.2667 | 1158.8333 | 231338 | 1167.5 | 236138 | 1191.6 | 3.578 | 1197.2 | 25.9941 | 1209.3889 | 2.6072 | 1212.6667 | 4.0584 | 1230.3 | 4.9992 | 1232.5 | 235238
1263.3 | 5849.6923 |  | 1285.7 | 5849.6923 | 1313.7222 | 50.6742 | 1329.2778 | 38.0589 | 1343.5556 | 3646.7227 | 1352.2778 | 4261.0536 | 1376.5 | 6.0486 | 1382 | 3.473 | 1394.3333 | 0.64412 | 1397.3889 | 2.3781 | 1415 | 6.6143 | 1417.3 | 128469
1448.1 | 5313.3638 |  | 1470.5 | 1552.176 | 1498.5556 | 9.472 | 1514.0556 | 6.7164 | 1528.3889 | 33.0315 | 1537 | 43.1084 | 1561.2 | 4.8605 | 1566.9 | 0.63317 | 1579.1111 | 0.64871 | 1582.1111 | 5.1766 | 1599.9 | 5.255 | 1602 | 128469
1632.8 | 107.5554 |  | 1655.2 | 68.284 | 1683.2778 | 1.3294 | 1698.6667 | 6.7164 | 1713 | 1.1771 | 1721.7778 | 8.4302 | 1745.9 | 1.1108 | 1751.5 | 8.746 | 1763.7778 | 0.62976 | 1766.7778 | 0.63194 | 1784.5 | 15.2385 | 1786.8 | 127319
1817.7 | 31.3893 |  | 1839.9 | 33.3361 | 1867.9444 | 0.65052 | 1883.4444 | 0.64034 | 1897.8889 | 0.69377 | 1906.5556 | 0.69821 | 1930.7 | 0.6381 | 1936.2 | 1.4261 | 1948.4444 | 0.63024 | 1951.6667 | 0.62952 | 1969.4 | 0.64615 | 1971.6 | 117569
2002.3 | 10.6859 |  | 2024.8 | 2.4729 | 2052.7222 | 0.64085 | 2068.2778 | 1.1213 | 2082.6111 | 6.1642 | 2091.3333 | 0.69172 | 2115.5 | 0.63 | 2121 | 3.6581 | 2133.3333 | 0.63538 | 2136.3889 | 0.63415 | 2154 | 0.64135 | 2156.4 | 130669
2187.1 | 16.3881 |  | 2209.5 | 6.8097 | 2237.5556 | 0.64794 | 2253.0556 | 0.65103 | 2267.3889 | 4.4395 | 2276.0556 | 5.3796 | 2300.2 | 0.99218 | 2305.9 | 4.8332 | 2318.1111 | 1.1743 | 2321.1667 | 5.6503 | 2338.9 | 0.63735 | 2341 | 117569
2371.9 | 15.2782 |  | 2394.3 | 0.73223 | 2422.2778 | 0.65836 | 2437.8889 | 1.0921 | 2452.1111 | 0.68222 | 2460.8333 | 3.0478 | 2485 | 5.8666 | 2490.6 | 0.6317 | 2502.8889 | 8.9098 | 2506 | 3.2229 | 2523.6 | 2.4816 | 2526 | 117569
2556.7 | 13.7215 |  | 2579.1 | 4.8089 | 2607.2222 | 5.2023 | 2622.6111 | 0.65363 | 2636.9444 | 0.7009 | 2645.7222 | 0.69466 | 2669.8 | 7.1257 | 2675.4 | 2.3489 | 2687.7778 | 0.66102 | 2690.7222 | 1.1249 | 2708.5 | 0.64692 | 2710.7 | 119119
2741.5 | 14.6281 |  | 2763.9 | 1.321 | 2791.8333 | 10.9259 | 2807.3889 | 4.906 | 2821.7778 | 6.9012 | 2830.5 | 5.8783 | 2854.6 | 0.63711 | 2860.2 | 4.078 | 2872.3889 | 2.7477 | 2875.6667 | 0.6411 | 2893.2 | 2.5918 | 2895.4 | 117569
2926.3 | 1.3209 |  | 2948.7 | 6.243 | 2976.6667 | 2.2904 | 2992.2778 | 6.6436 | 3006.5 | 12.9158 | 3015.2222 | 13.1647 | 3039.5 | 3.1099 | 3045 | 2.2885 | 3057.2778 | 0.64871 | 3060.3889 | 1.3659 | 3078 | 5.2115 | 3080.3 | 117569

## F11-F12
Open Burn Test 2 |  |  | 2006-10-24 | 13:08 |  |  | Vs = |  | 155.5788 |  | R = | 100
XLPE | 7-C | Tray C | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 11 & 12 | Cable F | Odd -Even
Time-131 | N11 | N12 | Time-132 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R11-G | R12-G | R11-12
39014.5448 | 1 | 0 | 39014.5448 | 1 | 0 |  | -38.5 | 182.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254738 | 254738 | 254737.9994
39014.5469 | 1 | 0 | 39014.5469 | 1 | 0 |  | 146 | 367 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254738 | 254738 | 254737.9994
39014.549 | 1 | 0 | 39014.5491 | 1 | 0 |  | 331 | 552 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254738 | 254738 | 254737.9994
39014.5512 | 1 | 0 | 39014.5512 | 1 | 0 |  | 515.5 | 736.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254738 | 254738 | 254737.9994
39014.5533 | 1 | 0 | 39014.5533 | 1 | 0 |  | 700.5 | 921.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254738 | 254738 | 254737.9994
39014.5555 | 1 | 0 | 39014.5555 | 1 | 0 |  | 885.5 | 1106.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254738 | 254738 | 254737.9994
39014.5576 | 360 | 0 | 39014.5576 | 1 | 0 |  | 1070 | 1291 | 21.978 | 0 | 0.06105 | 0 | 0.21978 | 0 | 0.0006105 | 0 | 0.21978 | 0.0006105 | 607.8833 | 254738 | 607.6636
39014.5597 | 2076 | 0 | 39014.5597 | 1 | 0 |  | 1255 | 1476 | 126.7399 | 0 | 0.06105 | 0 | 1.2674 | 0 | 0.0006105 | 0 | 1.2674 | 0.0006105 | 22.7543 | 254738 | 21.4869
39014.5619 | 2376 | 0 | 39014.5619 | 1 | 0 |  | 1439.5 | 1660.5 | 145.0549 | 0 | 0.06105 | 0 | 1.4505 | 0 | 0.0006105 | 0 | 1.4505 | 0.0006105 | 7.2551 | 254738 | 5.8045
39014.564 | 2369 | 0 | 39014.564 | 1 | 0 |  | 1624.5 | 1845.5 | 144.6276 | 0 | 0.06105 | 0 | 1.4463 | 0 | 0.0006105 | 0 | 1.4463 | 0.0006105 | 7.572 | 254738 | 6.1257
39014.5661 | 2075 | 0 | 39014.5662 | 2 | 0 |  | 1809 | 2030 | 126.6789 | 0 | 0.1221 | 0 | 1.2668 | 0 | 0.001221 | 0 | 1.2668 | 0.001221 | 22.8135 | 127319 | 21.5467
39014.5683 | 2387 | 0 | 39014.5683 | 1 | 0 |  | 1994 | 2215 | 145.7265 | 0 | 0.06105 | 0 | 1.4573 | 0 | 0.0006105 | 0 | 1.4573 | 0.0006105 | 6.7608 | 254738 | 5.3035
39014.5704 | 2530 | 0 | 39014.5704 | 1 | 0 |  | 2178.5 | 2399.5 | 154.4567 | 0 | 0.06105 | 0 | 1.5446 | 0 | 0.0006105 | 0 | 1.5446 | 0.0006105 | 0.72648 | 254738 | 0.81808
39014.5726 | 2276 | 0 | 39014.5726 | 1 | 0 |  | 2363.5 | 2584.5 | 138.9499 | 0 | 0.06105 | 0 | 1.3895 | 0 | 0.0006105 | 0 | 1.3895 | 0.0006105 | 11.9675 | 254738 | 10.578
39014.5747 | 2476 | 0 | 39014.5747 | 1 | 0 |  | 2548.5 | 2769.5 | 151.16 | 0 | 0.06105 | 0 | 1.5116 | 0 | 0.0006105 | 0 | 1.5116 | 0.0006105 | 2.9233 | 254738 | 1.4117
39014.5768 | 2532 | 0 | 39014.5769 | 1 | 0 |  | 2733 | 2954 | 154.5788 | 0 | 0.06105 | 0 | 1.5458 | 0 | 0.0006105 | 0 | 1.5458 | 0.0006105 | 0.64692 | 254738 | 0.89887
39014.579 | 2484 | 0 | 39014.579 | 2 | 0 |  | 2917.5 | 3138.5 | 151.6484 | 0 | 0.1221 | 0 | 1.5165 | 0 | 0.001221 | 0 | 1.5165 | 0.001221 | 2.5918 | 127319 | 1.0753
39014.5811 | 2305 | 0 | 39014.5811 | 1 | 0 |  | 3102.5 | 3323.5 | 140.7204 | 0 | 0.06105 | 0 | 1.4072 | 0 | 0.0006105 | 0 | 1.4072 | 0.0006105 | 10.5588 | 254738 | 9.1516

## E10-F12
Open Burn Test 2 |  |  | 2006-10-24 | 13:08 |  |  | Vs = |  | 156.9829 |  | R = | 100
XLPE | 7-C | Tray C | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 10 & 12 | Cable E | Even - | Cable F |  | Even
Time-129 | N11 | N12 | Time-130 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R10-G | R12-G | R10-12
39014.5447 | 1 | 0 | 39014.5447 | 1 | 0 |  | -41.5 | 179.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257038 | 257038 | 257037.9994
39014.5469 | 1 | 0 | 39014.5469 | 1 | 0 |  | 143.5 | 364.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257038 | 257038 | 257037.9994
39014.549 | 1 | 0 | 39014.549 | 1 | 0 |  | 328 | 549 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257038 | 257038 | 257037.9994
39014.5511 | 1 | 0 | 39014.5512 | 1 | 0 |  | 513 | 734 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257038 | 257038 | 257037.9994
39014.5533 | 1 | 0 | 39014.5533 | 1 | 0 |  | 698 | 919 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257038 | 257038 | 257037.9994
39014.5554 | 1 | 0 | 39014.5554 | 1 | 0 |  | 882.5 | 1103.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257038 | 257038 | 257037.9994
39014.5576 | 2258 | 0 | 39014.5576 | 1 | 0 |  | 1067.5 | 1288.5 | 137.851 | 0 | 0.06105 | 0 | 1.3785 | 0 | 0.0006105 | 0 | 1.3785 | 0.0006105 | 13.8787 | 257038 | 12.5001
39014.5597 | 2400 | 0 | 39014.5597 | 1 | 0 |  | 1252 | 1473 | 146.5201 | 0 | 0.06105 | 0 | 1.4652 | 0 | 0.0006105 | 0 | 1.4652 | 0.0006105 | 7.1408 | 257038 | 5.6756
39014.5618 | 2439 | 0 | 39014.5619 | 2 | 0 |  | 1437 | 1658 | 148.9011 | 0 | 0.1221 | 0 | 1.489 | 0 | 0.001221 | 0 | 1.489 | 0.001221 | 5.4276 | 128469 | 3.9386
39014.564 | 2338 | 0 | 39014.564 | 2 | 0 |  | 1621.5 | 1842.5 | 142.735 | 0 | 0.1221 | 0 | 1.4274 | 0 | 0.001221 | 0 | 1.4274 | 0.001221 | 9.982 | 128469 | 8.5547
39014.5661 | 2532 | 0 | 39014.5661 | 2 | 0 |  | 1806.5 | 2027.5 | 154.5788 | 0 | 0.1221 | 0 | 1.5458 | 0 | 0.001221 | 0 | 1.5458 | 0.001221 | 1.5553 | 128469 | 0.0095047
39014.5682 | 2379 | 0 | 39014.5683 | 2 | 0 |  | 1991 | 2212 | 145.2381 | 0 | 0.1221 | 0 | 1.4524 | 0 | 0.001221 | 0 | 1.4524 | 0.001221 | 8.0866 | 128469 | 6.6342
39014.5704 | 2543 | 0 | 39014.5704 | 1 | 0 |  | 2176 | 2397 | 155.2503 | 0 | 0.06105 | 0 | 1.5525 | 0 | 0.0006105 | 0 | 1.5525 | 0.0006105 | 1.116 | 257038 | 0.4365
39014.5725 | 2362 | 0 | 39014.5725 | 1 | 0 |  | 2360.5 | 2581.5 | 144.2002 | 0 | 0.06105 | 0 | 1.442 | 0 | 0.0006105 | 0 | 1.442 | 0.0006105 | 8.8645 | 257038 | 7.4225
39014.5747 | 2477 | 0 | 39014.5747 | 2 | 0 |  | 2545.5 | 2766.5 | 151.221 | 0 | 0.1221 | 0 | 1.5122 | 0 | 0.001221 | 0 | 1.5122 | 0.001221 | 3.8103 | 128469 | 2.298
39014.5768 | 2253 | 0 | 39014.5768 | 2 | 0 |  | 2730.5 | 2951.5 | 137.5458 | 0 | 0.1221 | 0 | 1.3755 | 0 | 0.001221 | 0 | 1.3755 | 0.001221 | 14.1314 | 128469 | 12.7559
39014.5789 | 2555 | 0 | 39014.579 | 1 | 0 |  | 2915 | 3136 | 155.9829 | 0 | 0.06105 | 0 | 1.5598 | 0 | 0.0006105 | 0 | 1.5598 | 0.0006105 | 0.6411 | 257038 | 0.91873
39014.5811 | 2181 | 0 | 39014.5811 | 1 | 0 |  | 3100 | 3321 | 133.1502 | 0 | 0.06105 | 0 | 1.3315 | 0 | 0.0006105 | 0 | 1.3315 | 0.0006105 | 17.8991 | 257038 | 16.5676

## E10-F11
Open Burn Test 2 |  |  | 2006-10-24 | 13:08 |  |  | Vs = |  | 155.7619 |  | R = | 100
XLPE | 7-C | Tray C | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 10 & 11 | Cable E | Even - | Cable F |  | Odd
Time-127 | N11 | N12 | Time-128 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R10-G | R11-G | R10-11
39014.5447 | 1 | 0 | 39014.5447 | 1 | 0 |  | -44 | 177 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255038 | 255038 | 255037.9994
39014.5468 | 1 | 0 | 39014.5468 | 1 | 0 |  | 140.5 | 361.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255038 | 255038 | 255037.9994
39014.549 | 1 | 0 | 39014.549 | 1 | 0 |  | 325.5 | 546.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255038 | 255038 | 255037.9994
39014.5511 | 1 | 0 | 39014.5511 | 1 | 0 |  | 510.5 | 731.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255038 | 255038 | 255037.9994
39014.5532 | 1 | 0 | 39014.5533 | 1 | 0 |  | 695 | 916 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255038 | 255038 | 255037.9994
39014.5554 | 1 | 0 | 39014.5554 | 1 | 0 |  | 879.5 | 1100.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255038 | 255038 | 255037.9994
39014.5575 | 2351 | 0 | 39014.5575 | 293 | 0 |  | 1064.5 | 1285.5 | 143.5287 | 0 | 17.8877 | 0 | 1.4353 | 0 | 0.17888 | 0 | 1.4353 | 0.17888 | 8.5232 | 770.7782 | 7.0879
39014.5597 | 2400 | 0 | 39014.5597 | 2427 | 0 |  | 1249.5 | 1470.5 | 146.5201 | 0 | 148.1685 | 0 | 1.4652 | 0 | 1.4817 | 0 | 1.4652 | 1.4817 | 6.3075 | 5.1248 | 4.8423
39014.5618 | 2183 | 0 | 39014.5618 | 2053 | 0 |  | 1434 | 1655 | 133.2723 | 0 | 125.3358 | 0 | 1.3327 | 0 | 1.2534 | 0 | 1.3327 | 1.2534 | 16.8749 | 24.2757 | 15.5422
39014.5639 | 2020 | 0 | 39014.564 | 2424 | 0 |  | 1619 | 1840 | 123.3211 | 0 | 147.9853 | 0 | 1.2332 | 0 | 1.4799 | 0 | 1.2332 | 1.4799 | 26.3059 | 5.255 | 25.0727
39014.5661 | 2471 | 0 | 39014.5661 | 2214 | 0 |  | 1803.5 | 2024.5 | 150.8547 | 0 | 135.1648 | 0 | 1.5085 | 0 | 1.3516 | 0 | 1.5085 | 1.3516 | 3.2529 | 15.2385 | 1.7444
39014.5682 | 2315 | 0 | 39014.5682 | 2535 | 0 |  | 1988.5 | 2209.5 | 141.3309 | 0 | 154.7619 | 0 | 1.4133 | 0 | 1.5476 | 0 | 1.4133 | 1.5476 | 10.2108 | 0.64615 | 8.7975
39014.5703 | 2188 | 0 | 39014.5704 | 2291 | 0 |  | 2173 | 2394 | 133.5775 | 0 | 139.8657 | 0 | 1.3358 | 0 | 1.3987 | 0 | 1.3358 | 1.3987 | 16.6079 | 11.3653 | 15.2721
39014.5725 | 2361 | 0 | 39014.5725 | 2387 | 0 |  | 2358 | 2579 | 144.1392 | 0 | 145.7265 | 0 | 1.4414 | 0 | 1.4573 | 0 | 1.4414 | 1.4573 | 8.0635 | 6.8865 | 6.6221
39014.5746 | 2345 | 0 | 39014.5746 | 2273 | 0 |  | 2542.5 | 2763.5 | 143.1624 | 0 | 138.7668 | 0 | 1.4316 | 0 | 1.3877 | 0 | 1.4316 | 1.3877 | 8.8009 | 12.2473 | 7.3692
39014.5768 | 2523 | 0 | 39014.5768 | 1960 | 0 |  | 2727.5 | 2948.5 | 154.0293 | 0 | 119.6581 | 0 | 1.5403 | 0 | 1.1966 | 0 | 1.5403 | 1.1966 | 1.1249 | 30.1724 | 0.41544
39014.5789 | 2489 | 0 | 39014.5789 | 2336 | 0 |  | 2912.5 | 3133.5 | 151.9536 | 0 | 142.6129 | 0 | 1.5195 | 0 | 1.4261 | 0 | 1.5195 | 1.4261 | 2.5062 | 9.22 | 0.98669
39014.581 | 2517 | 0 | 39014.5811 | 2425 | 0 |  | 3097 | 3318 | 153.663 | 0 | 148.0464 | 0 | 1.5366 | 0 | 1.4805 | 0 | 1.5366 | 1.4805 | 1.3659 | 5.2115 | 0.17072

## E9-F12
Open Burn Test 2 |  |  | 2006-10-24 | 13:08 |  |  | Vs = |  | 159.6691 |  | R = | 100
XLPE | 7-C | Tray C | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 9 & 12 | Cable E | Odd - | Cable F |  | Even
Time-125 | N11 | N12 | Time-126 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R9-G | R12-G | R9-12
39014.5447 | 1 | 0 | 39014.5447 | 1 | 0 |  | -47 | 174 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261438 | 261438 | 261437.9994
39014.5468 | 1 | 0 | 39014.5468 | 1 | 0 |  | 138 | 359 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261438 | 261438 | 261437.9994
39014.5489 | 1 | 0 | 39014.5489 | 1 | 0 |  | 322.5 | 543.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261438 | 261438 | 261437.9994
39014.5511 | 1 | 0 | 39014.5511 | 1 | 0 |  | 507.5 | 728.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261438 | 261438 | 261437.9994
39014.5532 | 1 | 0 | 39014.5532 | 1 | 0 |  | 692.5 | 913.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261438 | 261438 | 261437.9994
39014.5553 | 1 | 0 | 39014.5554 | 1 | 0 |  | 877 | 1098 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261438 | 261438 | 261437.9994
39014.5575 | 2049 | 0 | 39014.5575 | 2 | 0 |  | 1061.5 | 1282.5 | 125.0916 | 0 | 0.1221 | 0 | 1.2509 | 0 | 0.001221 | 0 | 1.2509 | 0.001221 | 27.6418 | 130669 | 26.3909
39014.5596 | 2017 | 0 | 39014.5596 | 1 | 0 |  | 1246.5 | 1467.5 | 123.138 | 0 | 0.06105 | 0 | 1.2314 | 0 | 0.0006105 | 0 | 1.2314 | 0.0006105 | 29.6668 | 261438 | 28.4355
39014.5618 | 2297 | 0 | 39014.5618 | 2 | 0 |  | 1431.5 | 1652.5 | 140.232 | 0 | 0.1221 | 0 | 1.4023 | 0 | 0.001221 | 0 | 1.4023 | 0.001221 | 13.8607 | 130669 | 12.4584
39014.5639 | 2227 | 0 | 39014.5639 | 1 | 0 |  | 1616 | 1837 | 135.9585 | 0 | 0.06105 | 0 | 1.3596 | 0 | 0.0006105 | 0 | 1.3596 | 0.0006105 | 17.4396 | 261438 | 16.08
39014.566 | 2110 | 0 | 39014.5661 | 2 | 0 |  | 1801 | 2022 | 128.8156 | 0 | 0.1221 | 0 | 1.2882 | 0 | 0.001221 | 0 | 1.2882 | 0.001221 | 23.9517 | 130669 | 22.6635
39014.5682 | 2599 | 0 | 39014.5682 | 1 | 0 |  | 1985.5 | 2206.5 | 158.6691 | 0 | 0.06105 | 0 | 1.5867 | 0 | 0.0006105 | 0 | 1.5867 | 0.0006105 | 0.63024 | 261438 | 0.95645
39014.5703 | 2417 | 0 | 39014.5703 | 2 | 0 |  | 2170.5 | 2391.5 | 147.558 | 0 | 0.1221 | 0 | 1.4756 | 0 | 0.001221 | 0 | 1.4756 | 0.001221 | 8.2077 | 130669 | 6.7321
39014.5725 | 2201 | 0 | 39014.5725 | 1 | 0 |  | 2355 | 2576 | 134.3712 | 0 | 0.06105 | 0 | 1.3437 | 0 | 0.0006105 | 0 | 1.3437 | 0.0006105 | 18.8269 | 261438 | 17.4832
39014.5746 | 2009 | 0 | 39014.5746 | 2 | 0 |  | 2540 | 2761 | 122.6496 | 0 | 0.1221 | 0 | 1.2265 | 0 | 0.001221 | 0 | 1.2265 | 0.001221 | 30.1832 | 130669 | 28.9567
39014.5767 | 2107 | 0 | 39014.5767 | 2 | 0 |  | 2724.5 | 2945.5 | 128.6325 | 0 | 0.1221 | 0 | 1.2863 | 0 | 0.001221 | 0 | 1.2863 | 0.001221 | 24.1281 | 130669 | 22.8418
39014.5789 | 2095 | 0 | 39014.5789 | 2 | 0 |  | 2909.5 | 3130.5 | 127.8999 | 0 | 0.1221 | 0 | 1.279 | 0 | 0.001221 | 0 | 1.279 | 0.001221 | 24.8391 | 130669 | 23.5601
39014.581 | 2446 | 0 | 39014.581 | 2 | 0 |  | 3094.5 | 3315.5 | 149.3284 | 0 | 0.1221 | 0 | 1.4933 | 0 | 0.001221 | 0 | 1.4933 | 0.001221 | 6.9248 | 130669 | 5.4315

## E9-F11
Open Burn Test 2 |  |  | 2006-10-24 | 13:08 |  |  | Vs = |  | 159.7912 |  | R = | 100
XLPE | 7-C | Tray C | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 9 & 11 | Cable E | Odd - | Cable F |  | Odd
Time-123 | N11 | N12 | Time-124 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R9-G | R11-G | R9-11
39014.5446 | 1 | 0 | 39014.5446 | 1 | 0 |  | -49.5 | 171.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261638 | 261638 | 261637.9994
39014.5468 | 1 | 0 | 39014.5468 | 1 | 0 |  | 135 | 356 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261638 | 261638 | 261637.9994
39014.5489 | 1 | 0 | 39014.5489 | 1 | 0 |  | 320 | 541 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261638 | 261638 | 261637.9994
39014.551 | 1 | 0 | 39014.5511 | 1 | 0 |  | 504.5 | 725.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261638 | 261638 | 261637.9994
39014.5532 | 1 | 0 | 39014.5532 | 1 | 0 |  | 689.5 | 910.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261638 | 261638 | 261637.9994
39014.5553 | 1 | 0 | 39014.5553 | 1 | 0 |  | 874 | 1095 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261638 | 261638 | 261637.9994
39014.5575 | 2132 | 0 | 39014.5575 | 265 | 0 |  | 1059 | 1280 | 130.1587 | 0 | 16.1783 | 0 | 1.3016 | 0 | 0.16178 | 0 | 1.3016 | 0.16178 | 22.7664 | 887.6906 | 21.4648
39014.5596 | 2533 | 0 | 39014.5596 | 2000 | 0 |  | 1243.5 | 1464.5 | 154.6398 | 0 | 122.1001 | 0 | 1.5464 | 0 | 1.221 | 0 | 1.5464 | 1.221 | 3.3312 | 30.869 | 1.7848
39014.5617 | 2545 | 0 | 39014.5617 | 2455 | 0 |  | 1428.5 | 1649.5 | 155.3724 | 0 | 149.8779 | 0 | 1.5537 | 0 | 1.4988 | 0 | 1.5537 | 1.4988 | 2.844 | 6.6143 | 1.2903
39014.5639 | 2555 | 0 | 39014.5639 | 2080 | 0 |  | 1613.5 | 1834.5 | 155.9829 | 0 | 126.9841 | 0 | 1.5598 | 0 | 1.2698 | 0 | 1.5598 | 1.2698 | 2.4415 | 25.8356 | 0.88166
39014.566 | 2601 | 0 | 39014.566 | 2178 | 0 |  | 1798 | 2019 | 158.7912 | 0 | 132.967 | 0 | 1.5879 | 0 | 1.3297 | 0 | 1.5879 | 1.3297 | 0.62976 | 20.1736 | 0.95815
39014.5681 | 2560 | 0 | 39014.5682 | 2384 | 0 |  | 1983 | 2204 | 156.2882 | 0 | 145.5433 | 0 | 1.5629 | 0 | 1.4554 | 0 | 1.5629 | 1.4554 | 2.2414 | 9.7894 | 0.67852
39014.5703 | 2568 | 0 | 39014.5703 | 2515 | 0 |  | 2167.5 | 2388.5 | 156.7766 | 0 | 153.5409 | 0 | 1.5678 | 0 | 1.5354 | 0 | 1.5678 | 1.5354 | 1.9229 | 4.0708 | 0.35513
39014.5724 | 2587 | 0 | 39014.5724 | 2080 | 0 |  | 2352.5 | 2573.5 | 157.9365 | 0 | 126.9841 | 0 | 1.5794 | 0 | 1.2698 | 0 | 1.5794 | 1.2698 | 1.1743 | 25.8356 | 0.40503
39014.5746 | 2205 | 0 | 39014.5746 | 2554 | 0 |  | 2537 | 2758 | 134.6154 | 0 | 155.9219 | 0 | 1.3462 | 0 | 1.5592 | 0 | 1.3462 | 1.5592 | 18.702 | 2.4816 | 17.3559
39014.5767 | 2270 | 0 | 39014.5767 | 2249 | 0 |  | 2722 | 2943 | 138.5836 | 0 | 137.3016 | 0 | 1.3858 | 0 | 1.373 | 0 | 1.3858 | 1.373 | 15.3031 | 16.3797 | 13.9172
39014.5788 | 2097 | 0 | 39014.5789 | 2516 | 0 |  | 2906.5 | 3127.5 | 128.022 | 0 | 153.602 | 0 | 1.2802 | 0 | 1.536 | 0 | 1.2802 | 1.536 | 24.8155 | 4.0294 | 23.5352
39014.581 | 2440 | 0 | 39014.581 | 2461 | 0 |  | 3091.5 | 3312.5 | 148.9621 | 0 | 150.2442 | 0 | 1.4896 | 0 | 1.5024 | 0 | 1.4896 | 1.5024 | 7.2697 | 6.3543 | 5.7801

## E9-E10
Open Burn Test 2 |  |  | 2006-10-24 | 13:08 |  |  | Vs = |  | 159.6081 |  | R = | 100
XLPE | 7-C | Tray C | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 9 & 10 | Cable E | Odd -Even
Time-121 | N11 | N12 | Time-122 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R9-G | R10-G | R9-10
39014.5446 | 1 | 0 | 39014.5446 | 1 | 0 |  | -52.5 | 168.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261338 | 261338 | 261337.9994
39014.5467 | 1 | 0 | 39014.5467 | 1 | 0 |  | 132.5 | 353.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261338 | 261338 | 261337.9994
39014.5489 | 1 | 0 | 39014.5489 | 1 | 0 |  | 317 | 538 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261338 | 261338 | 261337.9994
39014.551 | 1 | 0 | 39014.551 | 1 | 0 |  | 502 | 723 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261338 | 261338 | 261337.9994
39014.5531 | 1 | 0 | 39014.5532 | 1 | 0 |  | 686.5 | 907.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261338 | 261338 | 261337.9994
39014.5553 | 1 | 0 | 39014.5553 | 1 | 0 |  | 871.5 | 1092.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261338 | 261338 | 261337.9994
39014.5574 | 2023 | 0 | 39014.5574 | 2305 | 0 |  | 1056 | 1277 | 123.5043 | 0 | 140.7204 | 0 | 1.235 | 0 | 1.4072 | 0 | 1.235 | 1.4072 | 29.2328 | 13.4221 | 27.9978
39014.5596 | 2168 | 0 | 39014.5596 | 2114 | 0 |  | 1241 | 1462 | 132.3565 | 0 | 129.0598 | 0 | 1.3236 | 0 | 1.2906 | 0 | 1.3236 | 1.2906 | 20.5895 | 23.6698 | 19.2659
39014.5617 | 2256 | 0 | 39014.5617 | 2448 | 0 |  | 1425.5 | 1646.5 | 137.7289 | 0 | 149.4505 | 0 | 1.3773 | 0 | 1.4945 | 0 | 1.3773 | 1.4945 | 15.8856 | 6.7966 | 14.5083
39014.5638 | 2265 | 0 | 39014.5639 | 2007 | 0 |  | 1610.5 | 1831.5 | 138.2784 | 0 | 122.5275 | 0 | 1.3828 | 0 | 1.2253 | 0 | 1.3828 | 1.2253 | 15.4252 | 30.2631 | 14.0424
39014.566 | 2598 | 0 | 39014.566 | 2071 | 0 |  | 1795 | 2016 | 158.6081 | 0 | 126.4347 | 0 | 1.5861 | 0 | 1.2643 | 0 | 1.5861 | 1.2643 | 0.63048 | 26.2376 | 0.9556
39014.5681 | 2480 | 0 | 39014.5681 | 2404 | 0 |  | 1980 | 2201 | 151.4042 | 0 | 146.7643 | 0 | 1.514 | 0 | 1.4676 | 0 | 1.514 | 1.4676 | 5.4185 | 8.7512 | 3.9045
39014.5703 | 2497 | 0 | 39014.5703 | 2155 | 0 |  | 2164.5 | 2385.5 | 152.442 | 0 | 131.5629 | 0 | 1.5244 | 0 | 1.3156 | 0 | 1.5244 | 1.3156 | 4.7008 | 21.3169 | 3.1764
39014.5724 | 2496 | 0 | 39014.5724 | 2460 | 0 |  | 2349.5 | 2570.5 | 152.381 | 0 | 150.1832 | 0 | 1.5238 | 0 | 1.5018 | 0 | 1.5238 | 1.5018 | 4.7428 | 6.2756 | 3.219
39014.5745 | 2367 | 0 | 39014.5745 | 2209 | 0 |  | 2534.5 | 2755.5 | 144.5055 | 0 | 134.8596 | 0 | 1.4451 | 0 | 1.3486 | 0 | 1.4451 | 1.3486 | 10.4512 | 18.3513 | 9.0061
39014.5767 | 2308 | 0 | 39014.5767 | 2565 | 0 |  | 2719 | 2940 | 140.9035 | 0 | 156.5934 | 0 | 1.409 | 0 | 1.5659 | 0 | 1.409 | 1.5659 | 13.2747 | 1.9251 | 11.8657
39014.5788 | 2494 | 0 | 39014.5788 | 2257 | 0 |  | 2904 | 3125 | 152.2589 | 0 | 137.79 | 0 | 1.5226 | 0 | 1.3779 | 0 | 1.5226 | 1.3779 | 4.8268 | 15.8343 | 3.3042
39014.5809 | 2518 | 0 | 39014.581 | 2426 | 0 |  | 3088.5 | 3309.5 | 153.7241 | 0 | 148.1074 | 0 | 1.5372 | 0 | 1.4811 | 0 | 1.5372 | 1.4811 | 3.8276 | 7.765 | 2.2904

## D8-E10
Open Burn Test 2 |  |  | 2006-10-24 | 13:08 |  |  | Vs = |  | 159.3028 |  | R = | 100
XLPE | 7-C | Tray C | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 8 & 10 | Cable D | Even - | Cable E |  | Even
Time-115 | N11 | N12 | Time-116 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R8-G | R10-G | R8-10
39014.5445 | 1 | 0 | 39014.5445 | 1 | 0 |  | -61 | 160 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260838 | 260838 | 260837.9994
39014.5466 | 1 | 0 | 39014.5467 | 1 | 0 |  | 124 | 345 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260838 | 260838 | 260837.9994
39014.5488 | 1 | 0 | 39014.5488 | 1 | 0 |  | 308.5 | 529.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260838 | 260838 | 260837.9994
39014.5509 | 1 | 0 | 39014.5509 | 1 | 0 |  | 493.5 | 714.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260838 | 260838 | 260837.9994
39014.553 | 2418 | 1 | 39014.5531 | 1 | 0 |  | 678 | 899 | 147.619 | 0.06105 | 0.06105 | 0 | 1.4762 | 0.0006105 | 0.0006105 | 0 | 1.4756 | 0.0006105 | 7.9181 | 260837.9997 | 19030.704
39014.5552 | 2389 | 1 | 39014.5552 | 2 | 0 |  | 863 | 1084 | 145.8486 | 0.06105 | 0.1221 | 0 | 1.4585 | 0.0006105 | 0.001221 | 0 | 1.4579 | 0.001221 | 9.2286 | 130368.9999 | 21921.1853
39014.5573 | 2384 | 0 | 39014.5573 | 2407 | 0 |  | 1047.5 | 1268.5 | 145.5433 | 0 | 146.9475 | 0 | 1.4554 | 0 | 1.4695 | 0 | 1.4554 | 1.4695 | 9.4539 | 8.408 | 7.9984
39014.5595 | 2028 | 0 | 39014.5595 | 2281 | 0 |  | 1232.5 | 1453.5 | 123.8095 | 0 | 139.2552 | 0 | 1.2381 | 0 | 1.3926 | 0 | 1.2381 | 1.3926 | 28.6677 | 14.3963 | 27.4296
39014.5616 | 2090 | 0 | 39014.5616 | 2048 | 0 |  | 1417.5 | 1638.5 | 127.5946 | 0 | 125.0305 | 0 | 1.2759 | 0 | 1.2503 | 0 | 1.2759 | 1.2503 | 24.8507 | 27.4111 | 23.5748
39014.5637 | 2130 | 0 | 39014.5638 | 2140 | 0 |  | 1602 | 1823 | 130.0366 | 0 | 130.6471 | 0 | 1.3004 | 0 | 1.3065 | 0 | 1.3004 | 1.3065 | 22.5061 | 21.9336 | 21.2057
39014.5659 | 2334 | 0 | 39014.5659 | 2037 | 0 |  | 1786.5 | 2007.5 | 142.4908 | 0 | 124.359 | 0 | 1.4249 | 0 | 1.2436 | 0 | 1.4249 | 1.2436 | 11.7986 | 28.0992 | 10.3737
39014.568 | 2040 | 0 | 39014.568 | 2206 | 0 |  | 1971.5 | 2192.5 | 124.5421 | 0 | 134.6764 | 0 | 1.2454 | 0 | 1.3468 | 0 | 1.2454 | 1.3468 | 27.9108 | 18.2856 | 26.6654
39014.5702 | 2176 | 0 | 39014.5702 | 2479 | 0 |  | 2156.5 | 2377.5 | 132.8449 | 0 | 151.3431 | 0 | 1.3284 | 0 | 1.5134 | 0 | 1.3284 | 1.5134 | 19.9164 | 5.2594 | 18.5879
39014.5723 | 2040 | 0 | 39014.5723 | 2092 | 0 |  | 2341 | 2562 | 124.5421 | 0 | 127.7167 | 0 | 1.2454 | 0 | 1.2772 | 0 | 1.2454 | 1.2772 | 27.9108 | 24.7314 | 26.6654
39014.5744 | 2593 | 0 | 39014.5745 | 2216 | 0 |  | 2526 | 2747 | 158.3028 | 0 | 135.2869 | 0 | 1.583 | 0 | 1.3529 | 0 | 1.583 | 1.3529 | 0.6317 | 17.7518 | 0.95133
39014.5766 | 2190 | 0 | 39014.5766 | 2396 | 0 |  | 2710.5 | 2931.5 | 133.6996 | 0 | 146.2759 | 0 | 1.337 | 0 | 1.4628 | 0 | 1.337 | 1.4628 | 19.1498 | 8.9057 | 17.8128
39014.5787 | 2323 | 0 | 39014.5787 | 2568 | 0 |  | 2895.5 | 3116.5 | 141.8193 | 0 | 156.7766 | 0 | 1.4182 | 0 | 1.5678 | 0 | 1.4182 | 1.5678 | 12.328 | 1.6114 | 10.9098
39014.5809 | 2551 | 0 | 39014.5809 | 2459 | 0 |  | 3080.5 | 3301.5 | 155.7387 | 0 | 150.1221 | 0 | 1.5574 | 0 | 1.5012 | 0 | 1.5574 | 1.5012 | 2.2885 | 6.1155 | 0.73113

## D8-E9
Open Burn Test 2 |  |  | 2006-10-24 | 13:08 |  |  | Vs = |  | 158.9365 |  | R = | 100
XLPE | 7-C | Tray C | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 8 & 9 | Cable D | Even - | Cable E |  | Odd
Time-113 | N11 | N12 | Time-114 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R8-G | R9-G | R8-9
39014.5445 | 1 | 0 | 39014.5445 | 1 | 0 |  | -63.5 | 157.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260238 | 260238 | 260237.9994
39014.5466 | 1 | 0 | 39014.5466 | 1 | 0 |  | 121 | 342 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260238 | 260238 | 260237.9994
39014.5487 | 1 | 0 | 39014.5488 | 1 | 0 |  | 306 | 527 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260238 | 260238 | 260237.9994
39014.5509 | 1 | 0 | 39014.5509 | 1 | 0 |  | 490.5 | 711.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260238 | 260238 | 260237.9994
39014.553 | 1943 | 1 | 39014.553 | 1 | 0 |  | 675.5 | 896.5 | 118.6203 | 0.06105 | 0.06105 | 0 | 1.1862 | 0.0006105 | 0.0006105 | 0 | 1.1856 | 0.0006105 | 34.0052 | 260238.0001 | 65912.6722
39014.5552 | 2523 | 1 | 39014.5552 | 2 | 0 |  | 860 | 1081 | 154.0293 | 0.06105 | 0.1221 | 0 | 1.5403 | 0.0006105 | 0.001221 | 0 | 1.5397 | 0.001221 | 3.1872 | 130069 | 7931.9018
39014.5573 | 2066 | 0 | 39014.5573 | 2451 | 0 |  | 1045 | 1266 | 126.1294 | 0 | 149.6337 | 0 | 1.2613 | 0 | 1.4963 | 0 | 1.2613 | 1.4963 | 26.0106 | 6.2171 | 24.7494
39014.5594 | 2031 | 0 | 39014.5594 | 2157 | 0 |  | 1229.5 | 1450.5 | 123.9927 | 0 | 131.685 | 0 | 1.2399 | 0 | 1.3168 | 0 | 1.2399 | 1.3168 | 28.1822 | 20.6945 | 26.9422
39014.5616 | 2516 | 0 | 39014.5616 | 2309 | 0 |  | 1414.5 | 1635.5 | 153.602 | 0 | 140.9646 | 0 | 1.536 | 0 | 1.4096 | 0 | 1.536 | 1.4096 | 3.473 | 12.7492 | 1.937
39014.5637 | 2587 | 0 | 39014.5637 | 2322 | 0 |  | 1599.5 | 1820.5 | 157.9365 | 0 | 141.7582 | 0 | 1.5794 | 0 | 1.4176 | 0 | 1.5794 | 1.4176 | 0.63317 | 12.118 | 0.9462
39014.5658 | 2394 | 0 | 39014.5659 | 2048 | 0 |  | 1784 | 2005 | 146.1538 | 0 | 125.0305 | 0 | 1.4615 | 0 | 1.2503 | 0 | 1.4615 | 1.2503 | 8.746 | 27.1182 | 7.2845
39014.568 | 2146 | 0 | 39014.568 | 2082 | 0 |  | 1968.5 | 2189.5 | 131.0134 | 0 | 127.1062 | 0 | 1.3101 | 0 | 1.2711 | 0 | 1.3101 | 1.2711 | 21.3131 | 25.0423 | 20.003
39014.5701 | 2009 | 0 | 39014.5701 | 2552 | 0 |  | 2153.5 | 2374.5 | 122.6496 | 0 | 155.7998 | 0 | 1.2265 | 0 | 1.558 | 0 | 1.2265 | 1.558 | 29.5859 | 2.0133 | 28.3594
39014.5723 | 2396 | 0 | 39014.5723 | 2054 | 0 |  | 2338.5 | 2559.5 | 146.2759 | 0 | 125.3968 | 0 | 1.4628 | 0 | 1.254 | 0 | 1.4628 | 1.254 | 8.6553 | 26.7468 | 7.1925
39014.5744 | 2576 | 0 | 39014.5744 | 2005 | 0 |  | 2523 | 2744 | 157.265 | 0 | 122.4054 | 0 | 1.5726 | 0 | 1.2241 | 0 | 1.5726 | 1.2241 | 1.0629 | 29.8444 | 0.50976
39014.5765 | 2132 | 0 | 39014.5766 | 2396 | 0 |  | 2708 | 2929 | 130.1587 | 0 | 146.2759 | 0 | 1.3016 | 0 | 1.4628 | 0 | 1.3016 | 1.4628 | 22.1098 | 8.6553 | 20.8082
39014.5787 | 2014 | 0 | 39014.5787 | 2081 | 0 |  | 2892.5 | 3113.5 | 122.9548 | 0 | 127.0452 | 0 | 1.2295 | 0 | 1.2705 | 0 | 1.2295 | 1.2705 | 29.2642 | 25.1024 | 28.0346
39014.5808 | 2166 | 0 | 39014.5808 | 2334 | 0 |  | 3077.5 | 3298.5 | 132.2344 | 0 | 142.4908 | 0 | 1.3223 | 0 | 1.4249 | 0 | 1.3223 | 1.4249 | 20.193 | 11.5416 | 18.8706

## D7-E10
Open Burn Test 2 |  |  | 2006-10-24 | 13:08 |  |  | Vs = |  | 154.5409 |  | R = | 100
XLPE | 7-C | Tray C | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 7 & 10 | Cable D | Odd - | Cable E |  | Even
Time-107 | N11 | N12 | Time-108 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R7-G | R10-G | R7-10
39014.5444 | 1 | 0 | 39014.5444 | 1 | 0 |  | -72 | 149 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253038 | 253038 | 253037.9994
39014.5465 | 1 | 0 | 39014.5465 | 1 | 0 |  | 112.5 | 333.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253038 | 253038 | 253037.9994
39014.5486 | 1 | 0 | 39014.5487 | 1 | 0 |  | 297.5 | 518.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253038 | 253038 | 253037.9994
39014.5508 | 1 | 0 | 39014.5508 | 1 | 0 |  | 482 | 703 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253038 | 253038 | 253037.9994
39014.5529 | 1987 | 1 | 39014.5529 | 1 | 0 |  | 667 | 888 | 121.3065 | 0.06105 | 0.06105 | 0 | 1.2131 | 0.0006105 | 0.0006105 | 0 | 1.2125 | 0.0006105 | 27.4109 | 253037.9999 | 54316.5342
39014.5551 | 2515 | 1 | 39014.5551 | 1 | 0 |  | 851.5 | 1072.5 | 153.5409 | 0.06105 | 0.06105 | 0 | 1.5354 | 0.0006105 | 0.0006105 | 0 | 1.5348 | 0.0006105 | 0.65155 | 253038.0001 | 1537.3924
39014.5572 | 2495 | 0 | 39014.5572 | 2033 | 0 |  | 1036.5 | 1257.5 | 152.3199 | 0 | 124.1148 | 0 | 1.5232 | 0 | 1.2411 | 0 | 1.5232 | 1.2411 | 1.4581 | 24.5145 | 0.065083
39014.5593 | 2311 | 0 | 39014.5594 | 1963 | 0 |  | 1221.5 | 1442.5 | 141.0867 | 0 | 119.8413 | 0 | 1.4109 | 0 | 1.1984 | 0 | 1.4109 | 1.1984 | 9.5361 | 28.9547 | 8.1253
39014.5615 | 2387 | 0 | 39014.5615 | 2306 | 0 |  | 1406 | 1627 | 145.7265 | 0 | 140.7814 | 0 | 1.4573 | 0 | 1.4078 | 0 | 1.4573 | 1.4078 | 6.0486 | 9.7736 | 4.5913
39014.5636 | 2010 | 0 | 39014.5636 | 2240 | 0 |  | 1591 | 1812 | 122.7106 | 0 | 136.7521 | 0 | 1.2271 | 0 | 1.3675 | 0 | 1.2271 | 1.3675 | 25.9393 | 13.008 | 24.7122
39014.5658 | 2365 | 0 | 39014.5658 | 2294 | 0 |  | 1775.5 | 1996.5 | 144.3834 | 0 | 140.0488 | 0 | 1.4438 | 0 | 1.4005 | 0 | 1.4438 | 1.4005 | 7.0351 | 10.3479 | 5.5913
39014.5679 | 2217 | 0 | 39014.5679 | 2104 | 0 |  | 1960.5 | 2181.5 | 135.348 | 0 | 128.4493 | 0 | 1.3535 | 0 | 1.2845 | 0 | 1.3535 | 1.2845 | 14.1804 | 20.3127 | 12.8269
39014.57 | 2129 | 0 | 39014.57 | 2429 | 0 |  | 2145 | 2366 | 129.9756 | 0 | 148.2906 | 0 | 1.2998 | 0 | 1.4829 | 0 | 1.2998 | 1.4829 | 18.9 | 4.2149 | 17.6002
39014.5722 | 2184 | 0 | 39014.5722 | 2396 | 0 |  | 2330 | 2551 | 133.3333 | 0 | 146.2759 | 0 | 1.3333 | 0 | 1.4628 | 0 | 1.3333 | 1.4628 | 15.9057 | 5.6503 | 14.5723
39014.5743 | 2167 | 0 | 39014.5743 | 2357 | 0 |  | 2514.5 | 2735.5 | 132.2955 | 0 | 143.895 | 0 | 1.323 | 0 | 1.4389 | 0 | 1.323 | 1.4389 | 16.815 | 7.3984 | 15.492
39014.5764 | 2363 | 0 | 39014.5765 | 2301 | 0 |  | 2699.5 | 2920.5 | 144.2613 | 0 | 140.4762 | 0 | 1.4426 | 0 | 1.4048 | 0 | 1.4426 | 1.4048 | 7.1257 | 10.0122 | 5.6831
39014.5786 | 2461 | 0 | 39014.5786 | 2072 | 0 |  | 2884.5 | 3105.5 | 150.2442 | 0 | 126.4957 | 0 | 1.5024 | 0 | 1.265 | 0 | 1.5024 | 1.265 | 2.8598 | 22.1708 | 1.3574
39014.5807 | 2126 | 0 | 39014.5807 | 1997 | 0 |  | 3069 | 3290 | 129.7924 | 0 | 121.917 | 0 | 1.2979 | 0 | 1.2192 | 0 | 1.2979 | 1.2192 | 19.0677 | 26.7591 | 17.7698

## D7-E9
Open Burn Test 2 |  |  | 2006-10-24 | 13:08 |  |  | Vs = |  | 157.7155 |  | R = | 100
XLPE | 7-C | Tray C | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 7 & 9 | Cable D | Odd - | Cable E |  | Odd
Time-105 | N11 | N12 | Time-106 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R7-G | R9-G | R7-9
39014.5443 | 1 | 0 | 39014.5444 | 1 | 0 |  | -75 | 146 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258238 | 258238 | 258237.9994
39014.5465 | 1 | 0 | 39014.5465 | 1 | 0 |  | 110 | 331 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258238 | 258238 | 258237.9994
39014.5486 | 1 | 0 | 39014.5486 | 1 | 0 |  | 294.5 | 515.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258238 | 258238 | 258237.9994
39014.5508 | 1 | 0 | 39014.5508 | 1 | 0 |  | 479.5 | 700.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258238 | 258238 | 258237.9994
39014.5529 | 2053 | 1 | 39014.5529 | 1 | 0 |  | 664.5 | 885.5 | 125.3358 | 0.06105 | 0.06105 | 0 | 1.2534 | 0.0006105 | 0.0006105 | 0 | 1.2527 | 0.0006105 | 25.847 | 258238.0002 | 52917.5082
39014.555 | 2431 | 1 | 39014.555 | 2 | 0 |  | 849 | 1070 | 148.4127 | 0.06105 | 0.1221 | 0 | 1.4841 | 0.0006105 | 0.001221 | 0 | 1.4835 | 0.001221 | 6.2708 | 129069 | 15126.2805
39014.5572 | 2119 | 0 | 39014.5572 | 2238 | 0 |  | 1033.5 | 1254.5 | 129.3651 | 0 | 136.63 | 0 | 1.2937 | 0 | 1.3663 | 0 | 1.2937 | 1.3663 | 21.9151 | 15.4325 | 20.6214
39014.5593 | 2082 | 0 | 39014.5593 | 2008 | 0 |  | 1218.5 | 1439.5 | 127.1062 | 0 | 122.5885 | 0 | 1.2711 | 0 | 1.2259 | 0 | 1.2711 | 1.2259 | 24.0817 | 28.6544 | 22.8106
39014.5614 | 2133 | 0 | 39014.5615 | 2499 | 0 |  | 1403.5 | 1624.5 | 130.2198 | 0 | 152.5641 | 0 | 1.3022 | 0 | 1.5256 | 0 | 1.3022 | 1.5256 | 21.1149 | 3.3766 | 19.8127
39014.5636 | 2432 | 0 | 39014.5636 | 2427 | 0 |  | 1588 | 1809 | 148.4737 | 0 | 148.1685 | 0 | 1.4847 | 0 | 1.4817 | 0 | 1.4847 | 1.4817 | 6.2245 | 6.4433 | 4.7398
39014.5657 | 2555 | 0 | 39014.5657 | 2369 | 0 |  | 1773 | 1994 | 155.9829 | 0 | 144.6276 | 0 | 1.5598 | 0 | 1.4463 | 0 | 1.5598 | 1.4463 | 1.1108 | 9.0494 | 0.44907
39014.5679 | 2567 | 0 | 39014.5679 | 2425 | 0 |  | 1957.5 | 2178.5 | 156.7155 | 0 | 148.0464 | 0 | 1.5672 | 0 | 1.4805 | 0 | 1.5672 | 1.4805 | 0.6381 | 6.5311 | 0.92906
39014.57 | 2076 | 0 | 39014.57 | 2098 | 0 |  | 2142.5 | 2363.5 | 126.7399 | 0 | 128.083 | 0 | 1.2674 | 0 | 1.2808 | 0 | 1.2674 | 1.2808 | 24.4403 | 23.1354 | 23.1729
39014.5721 | 2558 | 0 | 39014.5722 | 1998 | 0 |  | 2327 | 2548 | 156.1661 | 0 | 121.978 | 0 | 1.5617 | 0 | 1.2198 | 0 | 1.5617 | 1.2198 | 0.99218 | 29.2983 | 0.56948
39014.5743 | 2296 | 0 | 39014.5743 | 2303 | 0 |  | 2512 | 2733 | 140.1709 | 0 | 140.5983 | 0 | 1.4017 | 0 | 1.406 | 0 | 1.4017 | 1.406 | 12.5166 | 12.1746 | 11.1148
39014.5764 | 2050 | 0 | 39014.5764 | 2553 | 0 |  | 2696.5 | 2917.5 | 125.1526 | 0 | 155.8608 | 0 | 1.2515 | 0 | 1.5586 | 0 | 1.2515 | 1.5586 | 26.0185 | 1.19 | 24.767
39014.5786 | 2309 | 0 | 39014.5786 | 2002 | 0 |  | 2881.5 | 3102.5 | 140.9646 | 0 | 122.2222 | 0 | 1.4096 | 0 | 1.2222 | 0 | 1.4096 | 1.2222 | 11.8831 | 29.04 | 10.4734
39014.5807 | 2012 | 0 | 39014.5807 | 2061 | 0 |  | 3066.5 | 3287.5 | 122.8327 | 0 | 125.8242 | 0 | 1.2283 | 0 | 1.2582 | 0 | 1.2283 | 1.2582 | 28.3986 | 25.3459 | 27.1703

## D7-D8
Open Burn Test 2 |  |  | 2006-10-24 | 13:08 |  |  | Vs = |  | 157.9597 |  | R = | 100
XLPE | 7-C | Tray C | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 7 & 8 | Cable D | Odd -Even
Time-103 | N11 | N12 | Time-104 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R7-G | R8-G | R7-8
39014.5443 | 1 | 0 | 39014.5443 | 1 | 0 |  | -77.5 | 143.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258638 | 258638 | 258637.9994
39014.5464 | 1 | 0 | 39014.5465 | 1 | 0 |  | 107 | 328 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258638 | 258638 | 258637.9994
39014.5486 | 1 | 0 | 39014.5486 | 1 | 0 |  | 291.5 | 512.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258638 | 258638 | 258637.9994
39014.5507 | 1 | 0 | 39014.5507 | 1 | 0 |  | 476.5 | 697.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258638 | 258638 | 258637.9994
39014.5529 | 1473 | 0 | 39014.5529 | 2223 | 0 |  | 661.5 | 882.5 | 89.9267 | 0 | 135.7143 | 0 | 0.89927 | 0 | 1.3571 | 0 | 0.89927 | 1.3571 | 75.6538 | 16.3914 | 74.7545
39014.555 | 2512 | 0 | 39014.555 | 2282 | 0 |  | 846 | 1067 | 153.3578 | 0 | 139.3162 | 0 | 1.5336 | 0 | 1.3932 | 0 | 1.5336 | 1.3932 | 3.0008 | 13.3821 | 1.4672
39014.5571 | 2223 | 1 | 39014.5572 | 2022 | 1 |  | 1031 | 1252 | 135.7143 | 0.06105 | 123.4432 | 0.06105 | 1.3571 | 0.0006105 | 1.2344 | 0.0006105 | 1.3565 | 1.2338 | 16.4251 | 28.0598 | 7962.192
39014.5593 | 2129 | 0 | 39014.5593 | 2012 | 0 |  | 1215.5 | 1436.5 | 129.9756 | 0 | 122.8327 | 0 | 1.2998 | 0 | 1.2283 | 0 | 1.2998 | 1.2283 | 21.5303 | 28.5974 | 20.2305
39014.5614 | 2175 | 0 | 39014.5614 | 2408 | 0 |  | 1400.5 | 1621.5 | 132.7839 | 0 | 147.0085 | 0 | 1.3278 | 0 | 1.4701 | 0 | 1.3278 | 1.4701 | 18.96 | 7.4493 | 17.6322
39014.5636 | 2376 | 0 | 39014.5636 | 2136 | 0 |  | 1585.5 | 1806.5 | 145.0549 | 0 | 130.4029 | 0 | 1.4505 | 0 | 1.304 | 0 | 1.4505 | 1.304 | 8.8965 | 21.132 | 7.4459
39014.5657 | 2101 | 0 | 39014.5657 | 2101 | 0 |  | 1770 | 1991 | 128.2662 | 0 | 128.2662 | 0 | 1.2827 | 0 | 1.2827 | 0 | 1.2827 | 1.2827 | 23.1499 | 23.1499 | 21.8673
39014.5678 | 2316 | 0 | 39014.5678 | 2551 | 0 |  | 1954.5 | 2175.5 | 141.3919 | 0 | 155.7387 | 0 | 1.4139 | 0 | 1.5574 | 0 | 1.4139 | 1.5574 | 11.7176 | 1.4261 | 10.3037
39014.57 | 2490 | 0 | 39014.57 | 2040 | 0 |  | 2139.5 | 2360.5 | 152.0147 | 0 | 124.5421 | 0 | 1.5201 | 0 | 1.2454 | 0 | 1.5201 | 1.2454 | 3.9108 | 26.8324 | 2.3907
39014.5721 | 2538 | 0 | 39014.5721 | 2265 | 0 |  | 2324.5 | 2545.5 | 154.9451 | 0 | 138.2784 | 0 | 1.5495 | 0 | 1.3828 | 0 | 1.5495 | 1.3828 | 1.9456 | 14.2331 | 0.39618
39014.5742 | 2444 | 0 | 39014.5743 | 2414 | 0 |  | 2509 | 2730 | 149.2063 | 0 | 147.3748 | 0 | 1.4921 | 0 | 1.4737 | 0 | 1.4921 | 1.4737 | 5.8666 | 7.1823 | 4.3745
39014.5764 | 2390 | 0 | 39014.5764 | 2528 | 0 |  | 2694 | 2915 | 145.9096 | 0 | 154.3346 | 0 | 1.4591 | 0 | 1.5433 | 0 | 1.4591 | 1.5433 | 8.2586 | 2.3489 | 6.7995
39014.5785 | 2571 | 0 | 39014.5785 | 2486 | 0 |  | 2878.5 | 3099.5 | 156.9597 | 0 | 151.7705 | 0 | 1.5696 | 0 | 1.5177 | 0 | 1.5696 | 1.5177 | 0.63711 | 4.078 | 0.93249
39014.5807 | 2428 | 0 | 39014.5807 | 2112 | 0 |  | 3063.5 | 3284.5 | 148.2295 | 0 | 128.9377 | 0 | 1.4823 | 0 | 1.2894 | 0 | 1.4823 | 1.2894 | 6.5643 | 22.5085 | 5.082

## Raw IRMS Data
Time | DL1.V2000:B | DL1.V2001:B | DL1.V1500:B | Open Burn Test 2 |  |  | 2006-10-24 | 13:08
39014.5427 | 1 | 0 | 1 | XLPE | 7-C | Tray C | IRMS | 1
39014.5448 | 1 | 0 | 1 |  | 250 kW |  | Bundle
39014.5469 | 1 | 0 | 1
39014.5491 | 1 | 0 | 1
39014.5512 | 1 | 0 | 1
39014.5533 | 1 | 0 | 1
39014.5555 | 1 | 0 | 1
39014.5576 | 1 | 0 | 1
39014.5598 | 1106 | 1067 | 1
39014.5619 | 1073 | 986 | 1
39014.564 | 1360 | 734 | 1
39014.5662 | 1819 | 293 | 1
39014.5683 | 1976 | 170 | 1
39014.5705 | 1823 | 139 | 1
39014.5726 | 2094 | 140 | 1
39014.5747 | 2304 | 101 | 1
39014.5769 | 2216 | 139 | 1
39014.579 | 2259 | 159 | 1
1
39014.5427 | 1 | 0 | 2
39014.5448 | 1 | 0 | 2
39014.5469 | 1 | 0 | 2
39014.5491 | 1 | 0 | 2
39014.5512 | 1 | 0 | 2
39014.5534 | 1 | 0 | 2
39014.5555 | 1 | 0 | 2
39014.5576 | 1 | 0 | 2
39014.5598 | 1149 | 1110 | 2
39014.5619 | 1178 | 1084 | 2
39014.5641 | 1552 | 773 | 2
39014.5662 | 1762 | 309 | 2
39014.5683 | 1886 | 153 | 2
39014.5705 | 1983 | 154 | 2
39014.5726 | 2021 | 134 | 2
39014.5747 | 2200 | 104 | 2
39014.5769 | 2185 | 137 | 2
39014.579 | 1816 | 129 | 2
2
39014.5427 | 1 | 0 | 3
39014.5448 | 1 | 0 | 3
39014.547 | 1 | 0 | 3
39014.5491 | 1 | 0 | 3
39014.5512 | 1 | 0 | 3
39014.5534 | 1 | 0 | 3
39014.5555 | 1 | 0 | 3
39014.5577 | 1 | 0 | 3
39014.5598 | 2 | 0 | 3
39014.5619 | 6 | 0 | 3
39014.5641 | 992 | 0 | 3
39014.5662 | 1928 | 0 | 3
39014.5683 | 2071 | 0 | 3
39014.5705 | 1944 | 0 | 3
39014.5726 | 2112 | 0 | 3
39014.5748 | 2262 | 0 | 3
39014.5769 | 2206 | 0 | 3
39014.579 | 2176 | 0 | 3
3
39014.5427 | 1 | 0 | 4
39014.5448 | 1 | 0 | 4
39014.547 | 1 | 0 | 4
39014.5491 | 1 | 0 | 4
39014.5512 | 1 | 0 | 4
39014.5534 | 1 | 0 | 4
39014.5555 | 1 | 0 | 4
39014.5577 | 1 | 0 | 4
39014.5598 | 464 | 0 | 4
39014.5619 | 2285 | 0 | 4
39014.5641 | 2152 | 0 | 4
39014.5662 | 2164 | 0 | 4
39014.5684 | 2556 | 0 | 4
39014.5705 | 2535 | 0 | 4
39014.5726 | 2505 | 0 | 4
39014.5748 | 2036 | 0 | 4
39014.5769 | 1973 | 0 | 4
39014.5791 | 1940 | 0 | 4
4
39014.5427 | 1 | 0 | 5
39014.5448 | 1 | 0 | 5
39014.547 | 1 | 0 | 5
39014.5491 | 1 | 0 | 5
39014.5513 | 1 | 0 | 5
39014.5534 | 1 | 0 | 5
39014.5555 | 1 | 0 | 5
39014.5577 | 1 | 0 | 5
39014.5598 | 1 | 0 | 5
39014.562 | 9 | 0 | 5
39014.5641 | 1022 | 0 | 5
39014.5662 | 1888 | 0 | 5
39014.5684 | 1909 | 0 | 5
39014.5705 | 1990 | 0 | 5
39014.5727 | 1771 | 0 | 5
39014.5748 | 1857 | 0 | 5
39014.5769 | 1940 | 0 | 5
39014.5791 | 1992 | 0 | 5
5
39014.5427 | 1 | 0 | 6
39014.5449 | 1 | 0 | 6
39014.547 | 1 | 0 | 6
39014.5491 | 1 | 0 | 6
39014.5513 | 1 | 0 | 6
39014.5534 | 1 | 0 | 6
39014.5556 | 1 | 0 | 6
39014.5577 | 1 | 0 | 6
39014.5598 | 465 | 0 | 6
39014.562 | 1920 | 0 | 6
39014.5641 | 2340 | 0 | 6
39014.5663 | 2036 | 0 | 6
39014.5684 | 2370 | 0 | 6
39014.5705 | 2477 | 0 | 6
39014.5727 | 2230 | 0 | 6
39014.5748 | 2506 | 0 | 6
39014.5769 | 1920 | 0 | 6
39014.5791 | 2278 | 0 | 6
6
39014.5427 | 1 | 0 | 7
39014.5449 | 1 | 0 | 7
39014.547 | 1 | 0 | 7
39014.5492 | 1 | 0 | 7
39014.5513 | 1 | 0 | 7
39014.5534 | 1 | 0 | 7
39014.5556 | 1 | 0 | 7
39014.5577 | 1 | 0 | 7
39014.5598 | 1 | 0 | 7
39014.562 | 20 | 0 | 7
39014.5641 | 1171 | 4 | 7
39014.5663 | 1620 | 0 | 7
39014.5684 | 2184 | 0 | 7
39014.5705 | 2077 | 0 | 7
39014.5727 | 2068 | 0 | 7
39014.5748 | 2112 | 0 | 7
39014.577 | 1829 | 1 | 7
39014.5791 | 2210 | 6 | 7
7
39014.5428 | 1 | 0 | 8
39014.5449 | 1 | 0 | 8
39014.547 | 1 | 0 | 8
39014.5492 | 1 | 0 | 8
39014.5513 | 1 | 0 | 8
39014.5535 | 1 | 0 | 8
39014.5556 | 1 | 0 | 8
39014.5577 | 1 | 0 | 8
39014.5599 | 1 | 0 | 8
39014.562 | 219 | 0 | 8
39014.5641 | 1625 | 3 | 8
39014.5663 | 2151 | 0 | 8
39014.5684 | 1949 | 0 | 8
39014.5706 | 2196 | 0 | 8
39014.5727 | 2401 | 0 | 8
39014.5748 | 2281 | 0 | 8
39014.577 | 2026 | 1 | 8
39014.5791 | 2150 | 7 | 8
8
39014.5428 | 1 | 0 | 9
39014.5449 | 1 | 0 | 9
39014.5471 | 1 | 0 | 9
39014.5492 | 1 | 0 | 9
39014.5513 | 1 | 0 | 9
39014.5535 | 1 | 0 | 9
39014.5556 | 1 | 0 | 9
39014.5577 | 1 | 0 | 9
39014.5599 | 1 | 0 | 9
39014.562 | 23 | 0 | 9
39014.5642 | 1023 | 3 | 9
39014.5663 | 1798 | 0 | 9
39014.5684 | 1715 | 0 | 9
39014.5706 | 1751 | 0 | 9
39014.5727 | 1907 | 0 | 9
39014.5749 | 1873 | 0 | 9
39014.577 | 2062 | 1 | 9
39014.5791 | 2202 | 7 | 9
9
39014.5428 | 1 | 0 | 10
39014.5449 | 1 | 0 | 10
39014.5471 | 1 | 0 | 10
39014.5492 | 1 | 0 | 10
39014.5514 | 1 | 0 | 10
39014.5535 | 1 | 0 | 10
39014.5556 | 1 | 0 | 10
39014.5578 | 1 | 0 | 10
39014.5599 | 1 | 0 | 10
39014.562 | 233 | 0 | 10
39014.5642 | 1949 | 3 | 10
39014.5663 | 2346 | 0 | 10
39014.5685 | 2002 | 0 | 10
39014.5706 | 1886 | 0 | 10
39014.5727 | 1916 | 0 | 10
39014.5749 | 2069 | 0 | 10
39014.577 | 2087 | 1 | 10
39014.5792 | 1736 | 5 | 10
10
39014.5428 | 1 | 0 | 11
39014.545 | 1 | 0 | 11
39014.5471 | 1 | 0 | 11
39014.5492 | 1 | 0 | 11
39014.5514 | 1 | 0 | 11
39014.5535 | 1 | 0 | 11
39014.5556 | 1 | 0 | 11
39014.5578 | 1 | 0 | 11
39014.5599 | 1 | 0 | 11
39014.5621 | 14 | 0 | 11
39014.5642 | 1036 | 0 | 11
39014.5663 | 2027 | 0 | 11
39014.5685 | 1699 | 0 | 11
39014.5706 | 2184 | 0 | 11
39014.5728 | 1839 | 0 | 11
39014.5749 | 2077 | 0 | 11
39014.577 | 1755 | 0 | 11
39014.5792 | 1935 | 0 | 11
11
39014.5428 | 1 | 0 | 12
39014.545 | 1 | 0 | 12
39014.5471 | 1 | 0 | 12
39014.5492 | 1 | 0 | 12
39014.5514 | 1 | 0 | 12
39014.5535 | 2022 | 0 | 12
39014.5557 | 2047 | 0 | 12
39014.5578 | 2400 | 0 | 12
39014.5599 | 2300 | 0 | 12
39014.5621 | 2164 | 0 | 12
39014.5642 | 2325 | 0 | 12
39014.5664 | 2495 | 0 | 12
39014.5685 | 2203 | 0 | 12
39014.5706 | 2583 | 0 | 12
39014.5728 | 2256 | 0 | 12
39014.5749 | 2593 | 0 | 12
39014.577 | 2183 | 0 | 12
39014.5792 | 2359 | 0 | 12
12
39014.5428 | 1 | 0 | 13
39014.545 | 1 | 0 | 13
39014.5471 | 1 | 0 | 13
39014.5493 | 1 | 0 | 13
39014.5514 | 1 | 0 | 13
39014.5535 | 1 | 0 | 13
39014.5557 | 1 | 0 | 13
39014.5578 | 1 | 0 | 13
39014.56 | 1 | 0 | 13
39014.5621 | 19 | 0 | 13
39014.5642 | 981 | 0 | 13
39014.5664 | 1849 | 0 | 13
39014.5685 | 1762 | 0 | 13
39014.5706 | 2174 | 0 | 13
39014.5728 | 2118 | 0 | 13
39014.5749 | 2019 | 0 | 13
39014.5771 | 1755 | 0 | 13
39014.5792 | 2132 | 0 | 13
13
39014.5429 | 1 | 0 | 14
39014.545 | 1 | 0 | 14
39014.5471 | 1 | 0 | 14
39014.5493 | 1 | 0 | 14
39014.5514 | 1 | 0 | 14
39014.5536 | 2512 | 0 | 14
39014.5557 | 2392 | 0 | 14
39014.5578 | 2378 | 0 | 14
39014.56 | 2027 | 0 | 14
39014.5621 | 2492 | 0 | 14
39014.5642 | 2289 | 0 | 14
39014.5664 | 2257 | 0 | 14
39014.5685 | 2280 | 0 | 14
39014.5707 | 2414 | 0 | 14
39014.5728 | 2043 | 0 | 14
39014.5749 | 2261 | 0 | 14
39014.5771 | 2227 | 0 | 14
39014.5792 | 2411 | 0 | 14
14
39014.5429 | 1 | 0 | 15
39014.545 | 1 | 0 | 15
39014.5472 | 1 | 0 | 15
39014.5493 | 1 | 0 | 15
39014.5514 | 1 | 0 | 15
39014.5536 | 1 | 0 | 15
39014.5557 | 1 | 0 | 15
39014.5578 | 1 | 0 | 15
39014.56 | 1 | 0 | 15
39014.5621 | 23 | 0 | 15
39014.5643 | 1222 | 0 | 15
39014.5664 | 1577 | 0 | 15
39014.5685 | 1793 | 0 | 15
39014.5707 | 1908 | 0 | 15
39014.5728 | 2029 | 0 | 15
39014.575 | 2113 | 0 | 15
39014.5771 | 2240 | 0 | 15
39014.5792 | 2203 | 0 | 15
15
39014.5429 | 1 | 0 | 16
39014.545 | 1 | 0 | 16
39014.5472 | 1 | 0 | 16
39014.5493 | 1 | 0 | 16
39014.5514 | 1 | 0 | 16
39014.5536 | 1 | 0 | 16
39014.5557 | 1 | 0 | 16
39014.5579 | 1982 | 0 | 16
39014.56 | 2393 | 0 | 16
39014.5621 | 2089 | 0 | 16
39014.5643 | 2563 | 0 | 16
39014.5664 | 2042 | 0 | 16
39014.5686 | 2006 | 0 | 16
39014.5707 | 2365 | 0 | 16
39014.5728 | 2574 | 0 | 16
39014.575 | 2241 | 0 | 16
39014.5771 | 2213 | 0 | 16
39014.5792 | 2545 | 0 | 16
16
39014.5429 | 1 | 0 | 17
39014.545 | 1 | 0 | 17
39014.5472 | 1 | 0 | 17
39014.5493 | 1 | 0 | 17
39014.5515 | 1 | 0 | 17
39014.5536 | 1 | 0 | 17
39014.5557 | 1 | 0 | 17
39014.5579 | 1 | 0 | 17
39014.56 | 2 | 0 | 17
39014.5622 | 29 | 0 | 17
39014.5643 | 996 | 0 | 17
39014.5664 | 1870 | 0 | 17
39014.5686 | 1907 | 0 | 17
39014.5707 | 2091 | 0 | 17
39014.5728 | 1879 | 0 | 17
39014.575 | 2242 | 0 | 17
39014.5771 | 1848 | 0 | 17
39014.5793 | 2053 | 0 | 17
17
39014.5429 | 1 | 0 | 18
39014.5451 | 1 | 0 | 18
39014.5472 | 1 | 0 | 18
39014.5493 | 1 | 0 | 18
39014.5515 | 1 | 0 | 18
39014.5536 | 1 | 0 | 18
39014.5558 | 1 | 0 | 18
39014.5579 | 2021 | 0 | 18
39014.56 | 1992 | 0 | 18
39014.5622 | 2385 | 0 | 18
39014.5643 | 2303 | 0 | 18
39014.5664 | 2296 | 0 | 18
39014.5686 | 2350 | 0 | 18
39014.5707 | 2332 | 0 | 18
39014.5729 | 2251 | 0 | 18
39014.575 | 2394 | 0 | 18
39014.5771 | 2004 | 0 | 18
39014.5793 | 2067 | 0 | 18
18
39014.5429 | 1 | 0 | 19
39014.5451 | 1 | 0 | 19
39014.5472 | 1 | 0 | 19
39014.5494 | 1 | 0 | 19
39014.5515 | 1 | 0 | 19
39014.5536 | 1 | 0 | 19
39014.5558 | 1 | 0 | 19
39014.5579 | 1 | 0 | 19
39014.56 | 2 | 0 | 19
39014.5622 | 35 | 0 | 19
39014.5643 | 1270 | 0 | 19
39014.5665 | 1966 | 0 | 19
39014.5686 | 1911 | 0 | 19
39014.5707 | 2177 | 0 | 19
39014.5729 | 1865 | 0 | 19
39014.575 | 2181 | 0 | 19
39014.5772 | 2025 | 0 | 19
39014.5793 | 1961 | 0 | 19
19
39014.543 | 1 | 0 | 20
39014.5451 | 1 | 0 | 20
39014.5472 | 1 | 0 | 20
39014.5494 | 1 | 0 | 20
39014.5515 | 1 | 0 | 20
39014.5536 | 1 | 0 | 20
39014.5558 | 1 | 0 | 20
39014.5579 | 646 | 0 | 20
39014.5601 | 2222 | 0 | 20
39014.5622 | 2397 | 0 | 20
39014.5643 | 2306 | 0 | 20
39014.5665 | 2304 | 0 | 20
39014.5686 | 2354 | 0 | 20
39014.5708 | 2091 | 0 | 20
39014.5729 | 2562 | 0 | 20
39014.575 | 2206 | 0 | 20
39014.5772 | 2166 | 0 | 20
39014.5793 | 1947 | 0 | 20
20
39014.543 | 1 | 0 | 21
39014.5451 | 1 | 0 | 21
39014.5472 | 1 | 0 | 21
39014.5494 | 1 | 0 | 21
39014.5515 | 1 | 0 | 21
39014.5537 | 1 | 0 | 21
39014.5558 | 1 | 0 | 21
39014.5579 | 1 | 0 | 21
39014.5601 | 2 | 0 | 21
39014.5622 | 38 | 0 | 21
39014.5644 | 1306 | 0 | 21
39014.5665 | 1664 | 0 | 21
39014.5686 | 1910 | 0 | 21
39014.5708 | 2220 | 0 | 21
39014.5729 | 2191 | 0 | 21
39014.575 | 2221 | 0 | 21
39014.5772 | 1834 | 0 | 21
39014.5793 | 2196 | 0 | 21
21
39014.543 | 1 | 0 | 22
39014.5451 | 1 | 0 | 22
39014.5473 | 1 | 0 | 22
39014.5494 | 1 | 0 | 22
39014.5515 | 1 | 0 | 22
39014.5537 | 1 | 0 | 22
39014.5558 | 1 | 0 | 22
39014.558 | 1 | 0 | 22
39014.5601 | 1 | 0 | 22
39014.5622 | 1 | 0 | 22
39014.5644 | 1 | 0 | 22
39014.5665 | 2 | 0 | 22
39014.5686 | 1 | 0 | 22
39014.5708 | 1 | 0 | 22
39014.5729 | 2 | 0 | 22
39014.5751 | 2 | 0 | 22
39014.5772 | 2 | 0 | 22
39014.5793 | 2 | 0 | 22
22
39014.543 | 1 | 0 | 23
39014.5451 | 1 | 0 | 23
39014.5473 | 1 | 0 | 23
39014.5494 | 1 | 0 | 23
39014.5516 | 1 | 0 | 23
39014.5537 | 1 | 0 | 23
39014.5558 | 1 | 0 | 23
39014.558 | 1 | 0 | 23
39014.5601 | 1 | 0 | 23
39014.5623 | 48 | 0 | 23
39014.5644 | 1058 | 0 | 23
39014.5665 | 1739 | 0 | 23
39014.5687 | 2174 | 0 | 23
39014.5708 | 1765 | 0 | 23
39014.5729 | 1789 | 0 | 23
39014.5751 | 1836 | 0 | 23
39014.5772 | 1837 | 0 | 23
39014.5794 | 1840 | 0 | 23
23
39014.543 | 1 | 0 | 24
39014.5452 | 1 | 0 | 24
39014.5473 | 1 | 0 | 24
39014.5494 | 1 | 0 | 24
39014.5516 | 1 | 0 | 24
39014.5537 | 1 | 0 | 24
39014.5559 | 1 | 0 | 24
39014.558 | 1 | 0 | 24
39014.5601 | 859 | 0 | 24
39014.5623 | 2036 | 0 | 24
39014.5644 | 1999 | 0 | 24
39014.5665 | 2188 | 0 | 24
39014.5687 | 2485 | 0 | 24
39014.5708 | 1982 | 0 | 24
39014.573 | 2342 | 0 | 24
39014.5751 | 2240 | 0 | 24
39014.5772 | 2255 | 0 | 24
39014.5794 | 2399 | 0 | 24
24
39014.543 | 1 | 0 | 25
39014.5452 | 1 | 0 | 25
39014.5473 | 1 | 0 | 25
39014.5495 | 1 | 0 | 25
39014.5516 | 1 | 0 | 25
39014.5537 | 1 | 0 | 25
39014.5559 | 1 | 0 | 25
39014.558 | 1 | 0 | 25
39014.5602 | 1 | 0 | 25
39014.5623 | 51 | 0 | 25
39014.5644 | 1216 | 0 | 25
39014.5666 | 1690 | 0 | 25
39014.5687 | 2199 | 0 | 25
39014.5708 | 1733 | 0 | 25
39014.573 | 2237 | 0 | 25
39014.5751 | 1858 | 0 | 25
39014.5773 | 2224 | 0 | 25
39014.5794 | 1700 | 0 | 25
25
39014.5431 | 1 | 0 | 26
39014.5452 | 1 | 0 | 26
39014.5473 | 1 | 0 | 26
39014.5495 | 1 | 0 | 26
39014.5516 | 1 | 0 | 26
39014.5537 | 1 | 0 | 26
39014.5559 | 1 | 0 | 26
39014.558 | 1 | 0 | 26
39014.5602 | 1 | 0 | 26
39014.5623 | 51 | 0 | 26
39014.5644 | 1087 | 0 | 26
39014.5666 | 1621 | 0 | 26
39014.5687 | 1940 | 0 | 26
39014.5709 | 1792 | 0 | 26
39014.573 | 1822 | 0 | 26
39014.5751 | 2224 | 0 | 26
39014.5773 | 2148 | 0 | 26
39014.5794 | 2113 | 0 | 26
26
39014.5431 | 1 | 0 | 27
39014.5452 | 1 | 0 | 27
39014.5473 | 1 | 0 | 27
39014.5495 | 1 | 0 | 27
39014.5516 | 1 | 0 | 27
39014.5538 | 1 | 0 | 27
39014.5559 | 1 | 0 | 27
39014.558 | 1 | 0 | 27
39014.5602 | 1 | 0 | 27
39014.5623 | 85 | 0 | 27
39014.5645 | 1382 | 4 | 27
39014.5666 | 1699 | 0 | 27
39014.5687 | 1900 | 0 | 27
39014.5709 | 1844 | 0 | 27
39014.573 | 1963 | 0 | 27
39014.5752 | 1735 | 0 | 27
39014.5773 | 1939 | 1 | 27
39014.5794 | 2055 | 8 | 27
27
39014.5431 | 1 | 0 | 28
39014.5452 | 1 | 0 | 28
39014.5474 | 1 | 0 | 28
39014.5495 | 1 | 0 | 28
39014.5516 | 1 | 0 | 28
39014.5538 | 1 | 0 | 28
39014.5559 | 1 | 0 | 28
39014.5581 | 1 | 0 | 28
39014.5602 | 1 | 0 | 28
39014.5623 | 509 | 0 | 28
39014.5645 | 1757 | 3 | 28
39014.5666 | 1888 | 0 | 28
39014.5687 | 2180 | 0 | 28
39014.5709 | 2216 | 0 | 28
39014.573 | 2021 | 0 | 28
39014.5752 | 2298 | 0 | 28
39014.5773 | 2133 | 1 | 28
39014.5794 | 1911 | 7 | 28
28
39014.5431 | 1 | 0 | 29
39014.5452 | 1 | 0 | 29
39014.5474 | 1 | 0 | 29
39014.5495 | 1 | 0 | 29
39014.5517 | 1 | 0 | 29
39014.5538 | 1 | 0 | 29
39014.5559 | 1 | 0 | 29
39014.5581 | 1 | 0 | 29
39014.5602 | 1 | 0 | 29
39014.5623 | 85 | 0 | 29
39014.5645 | 1112 | 3 | 29
39014.5666 | 1717 | 0 | 29
39014.5688 | 1887 | 0 | 29
39014.5709 | 2223 | 0 | 29
39014.573 | 2153 | 0 | 29
39014.5752 | 1785 | 0 | 29
39014.5773 | 2247 | 1 | 29
39014.5795 | 1891 | 7 | 29
29
39014.5431 | 1 | 0 | 30
39014.5453 | 1 | 0 | 30
39014.5474 | 1 | 0 | 30
39014.5495 | 1 | 0 | 30
39014.5517 | 1 | 0 | 30
39014.5538 | 1 | 0 | 30
39014.5559 | 1 | 0 | 30
39014.5581 | 1 | 0 | 30
39014.5602 | 1 | 0 | 30
39014.5624 | 542 | 0 | 30
39014.5645 | 2128 | 2 | 30
39014.5666 | 2216 | 0 | 30
39014.5688 | 2189 | 0 | 30
39014.5709 | 2189 | 0 | 30
39014.5731 | 2152 | 0 | 30
39014.5752 | 2358 | 0 | 30
39014.5773 | 1801 | 1 | 30
39014.5795 | 1739 | 6 | 30
30
39014.5431 | 1 | 0 | 31
39014.5453 | 1 | 0 | 31
39014.5474 | 1 | 0 | 31
39014.5495 | 1 | 0 | 31
39014.5517 | 1 | 0 | 31
39014.5538 | 1 | 0 | 31
39014.556 | 1 | 0 | 31
39014.5581 | 1 | 0 | 31
39014.5602 | 1 | 0 | 31
39014.5624 | 77 | 0 | 31
39014.5645 | 1124 | 0 | 31
39014.5667 | 2088 | 0 | 31
39014.5688 | 2161 | 0 | 31
39014.5709 | 2197 | 0 | 31
39014.5731 | 1784 | 0 | 31
39014.5752 | 2186 | 0 | 31
39014.5773 | 1984 | 0 | 31
39014.5795 | 2201 | 0 | 31
31
39014.5431 | 1 | 0 | 32
39014.5453 | 1 | 0 | 32
39014.5474 | 1 | 0 | 32
39014.5496 | 1 | 0 | 32
39014.5517 | 1 | 0 | 32
39014.5538 | 1956 | 0 | 32
39014.556 | 2449 | 0 | 32
39014.5581 | 2068 | 0 | 32
39014.5603 | 2482 | 0 | 32
39014.5624 | 2564 | 0 | 32
39014.5645 | 2594 | 0 | 32
39014.5667 | 2062 | 0 | 32
39014.5688 | 2091 | 0 | 32
39014.5709 | 2080 | 0 | 32
39014.5731 | 2275 | 0 | 32
39014.5752 | 2092 | 0 | 32
39014.5774 | 2468 | 0 | 32
39014.5795 | 2001 | 0 | 32
32
39014.5432 | 1 | 0 | 33
39014.5453 | 1 | 0 | 33
39014.5474 | 1 | 0 | 33
39014.5496 | 1 | 0 | 33
39014.5517 | 1 | 0 | 33
39014.5539 | 2 | 0 | 33
39014.556 | 2 | 0 | 33
39014.5581 | 1 | 0 | 33
39014.5603 | 1 | 0 | 33
39014.5624 | 88 | 0 | 33
39014.5645 | 1329 | 0 | 33
39014.5667 | 1753 | 0 | 33
39014.5688 | 1959 | 0 | 33
39014.571 | 1829 | 0 | 33
39014.5731 | 1784 | 0 | 33
39014.5752 | 1751 | 0 | 33
39014.5774 | 1747 | 0 | 33
39014.5795 | 2165 | 0 | 33
33
39014.5432 | 1 | 0 | 34
39014.5453 | 1 | 0 | 34
39014.5475 | 1 | 0 | 34
39014.5496 | 1 | 0 | 34
39014.5517 | 1 | 0 | 34
39014.5539 | 1972 | 0 | 34
39014.556 | 2092 | 0 | 34
39014.5581 | 2187 | 0 | 34
39014.5603 | 2360 | 0 | 34
39014.5624 | 2339 | 0 | 34
39014.5646 | 2153 | 0 | 34
39014.5667 | 2257 | 0 | 34
39014.5688 | 2401 | 0 | 34
39014.571 | 2101 | 0 | 34
39014.5731 | 2400 | 0 | 34
39014.5753 | 2326 | 0 | 34
39014.5774 | 2034 | 0 | 34
39014.5795 | 2314 | 0 | 34
34
39014.5432 | 1 | 0 | 35
39014.5453 | 1 | 0 | 35
39014.5475 | 1 | 0 | 35
39014.5496 | 1 | 0 | 35
39014.5518 | 1 | 0 | 35
39014.5539 | 2 | 0 | 35
39014.556 | 1 | 0 | 35
39014.5582 | 1 | 0 | 35
39014.5603 | 1 | 0 | 35
39014.5624 | 100 | 0 | 35
39014.5646 | 1470 | 0 | 35
39014.5667 | 1926 | 0 | 35
39014.5689 | 1897 | 0 | 35
39014.571 | 1716 | 0 | 35
39014.5731 | 2168 | 0 | 35
39014.5753 | 1809 | 0 | 35
39014.5774 | 2067 | 0 | 35
39014.5796 | 1865 | 0 | 35
35
39014.5432 | 1 | 0 | 36
39014.5454 | 1 | 0 | 36
39014.5475 | 1 | 0 | 36
39014.5496 | 1 | 0 | 36
39014.5518 | 1 | 0 | 36
39014.5539 | 1 | 0 | 36
39014.556 | 1 | 0 | 36
39014.5582 | 2371 | 0 | 36
39014.5603 | 2095 | 0 | 36
39014.5625 | 2057 | 0 | 36
39014.5646 | 2547 | 0 | 36
39014.5667 | 2590 | 0 | 36
39014.5689 | 2028 | 0 | 36
39014.571 | 2078 | 0 | 36
39014.5732 | 2039 | 0 | 36
39014.5753 | 2438 | 0 | 36
39014.5774 | 2546 | 0 | 36
39014.5796 | 2411 | 0 | 36
36
39014.5432 | 1 | 0 | 37
39014.5454 | 1 | 0 | 37
39014.5475 | 1 | 0 | 37
39014.5497 | 1 | 0 | 37
39014.5518 | 1 | 0 | 37
39014.5539 | 1 | 0 | 37
39014.5561 | 1 | 0 | 37
39014.5582 | 1 | 0 | 37
39014.5603 | 1 | 0 | 37
39014.5625 | 101 | 0 | 37
39014.5646 | 1313 | 0 | 37
39014.5668 | 1829 | 0 | 37
39014.5689 | 1981 | 0 | 37
39014.571 | 1719 | 0 | 37
39014.5732 | 1955 | 0 | 37
39014.5753 | 2158 | 0 | 37
39014.5775 | 1768 | 0 | 37
39014.5796 | 1866 | 0 | 37
37
39014.5433 | 1 | 0 | 38
39014.5454 | 1 | 0 | 38
39014.5475 | 1 | 0 | 38
39014.5497 | 1 | 0 | 38
39014.5518 | 1 | 0 | 38
39014.5539 | 1 | 0 | 38
39014.5561 | 1 | 0 | 38
39014.5582 | 2363 | 0 | 38
39014.5604 | 2074 | 0 | 38
39014.5625 | 2370 | 0 | 38
39014.5646 | 2478 | 0 | 38
39014.5668 | 2252 | 0 | 38
39014.5689 | 2298 | 0 | 38
39014.5711 | 2583 | 0 | 38
39014.5732 | 2443 | 0 | 38
39014.5753 | 2036 | 0 | 38
39014.5775 | 2205 | 0 | 38
39014.5796 | 2077 | 0 | 38
38
39014.5433 | 1 | 0 | 39
39014.5454 | 1 | 0 | 39
39014.5475 | 1 | 0 | 39
39014.5497 | 1 | 0 | 39
39014.5518 | 1 | 0 | 39
39014.554 | 1 | 0 | 39
39014.5561 | 1 | 0 | 39
39014.5582 | 2 | 0 | 39
39014.5604 | 1 | 0 | 39
39014.5625 | 109 | 0 | 39
39014.5647 | 1538 | 0 | 39
39014.5668 | 1970 | 0 | 39
39014.5689 | 2178 | 0 | 39
39014.5711 | 2037 | 0 | 39
39014.5732 | 2126 | 0 | 39
39014.5753 | 2064 | 0 | 39
39014.5775 | 2125 | 0 | 39
39014.5796 | 2198 | 0 | 39
39
39014.5433 | 1 | 0 | 40
39014.5454 | 1 | 0 | 40
39014.5476 | 1 | 0 | 40
39014.5497 | 1 | 0 | 40
39014.5518 | 1 | 0 | 40
39014.554 | 1 | 0 | 40
39014.5561 | 1 | 0 | 40
39014.5583 | 1866 | 0 | 40
39014.5604 | 2071 | 0 | 40
39014.5625 | 1988 | 0 | 40
39014.5647 | 2343 | 0 | 40
39014.5668 | 2592 | 0 | 40
39014.5689 | 2181 | 0 | 40
39014.5711 | 2259 | 0 | 40
39014.5732 | 2304 | 0 | 40
39014.5754 | 2465 | 0 | 40
39014.5775 | 2176 | 0 | 40
39014.5796 | 2273 | 0 | 40
40
39014.5433 | 1 | 0 | 41
39014.5454 | 1 | 0 | 41
39014.5476 | 1 | 0 | 41
39014.5497 | 1 | 0 | 41
39014.5519 | 1 | 0 | 41
39014.554 | 1 | 0 | 41
39014.5561 | 1 | 0 | 41
39014.5583 | 1 | 0 | 41
39014.5604 | 1 | 0 | 41
39014.5625 | 133 | 0 | 41
39014.5647 | 1615 | 0 | 41
39014.5668 | 2009 | 0 | 41
39014.569 | 1976 | 0 | 41
39014.5711 | 2028 | 0 | 41
39014.5732 | 2215 | 0 | 41
39014.5754 | 2111 | 0 | 41
39014.5775 | 2199 | 0 | 41
39014.5797 | 1944 | 0 | 41
41
39014.5433 | 1 | 0 | 42
39014.5455 | 1 | 0 | 42
39014.5476 | 1 | 0 | 42
39014.5497 | 1 | 0 | 42
39014.5519 | 1 | 0 | 42
39014.554 | 1 | 0 | 42
39014.5561 | 1 | 0 | 42
39014.5583 | 1 | 0 | 42
39014.5604 | 1 | 0 | 42
39014.5626 | 1 | 0 | 42
39014.5647 | 1 | 0 | 42
39014.5668 | 1 | 0 | 42
39014.569 | 1 | 0 | 42
39014.5711 | 1 | 0 | 42
39014.5733 | 2 | 0 | 42
39014.5754 | 2 | 0 | 42
39014.5775 | 1 | 0 | 42
39014.5797 | 2 | 0 | 42
42
39014.5433 | 1 | 0 | 43
39014.5455 | 1 | 0 | 43
39014.5476 | 1 | 0 | 43
39014.5497 | 1 | 0 | 43
39014.5519 | 1 | 0 | 43
39014.554 | 1 | 0 | 43
39014.5562 | 1 | 0 | 43
39014.5583 | 17 | 0 | 43
39014.5604 | 1339 | 678 | 43
39014.5626 | 2171 | 27 | 43
39014.5647 | 2245 | 0 | 43
39014.5669 | 2057 | 0 | 43
39014.569 | 2255 | 0 | 43
39014.5711 | 2141 | 0 | 43
39014.5733 | 2488 | 0 | 43
39014.5754 | 2198 | 0 | 43
39014.5775 | 2163 | 2 | 43
39014.5797 | 2449 | 8 | 43
43
39014.5433 | 1 | 0 | 44
39014.5455 | 1 | 0 | 44
39014.5476 | 1 | 0 | 44
39014.5498 | 1 | 0 | 44
39014.5519 | 1 | 0 | 44
39014.554 | 1 | 0 | 44
39014.5562 | 1 | 0 | 44
39014.5583 | 11 | 0 | 44
39014.5605 | 1362 | 682 | 44
39014.5626 | 2010 | 26 | 44
39014.5647 | 1971 | 0 | 44
39014.5669 | 2380 | 0 | 44
39014.569 | 2194 | 0 | 44
39014.5711 | 2328 | 0 | 44
39014.5733 | 2346 | 0 | 44
39014.5754 | 2481 | 1 | 44
39014.5776 | 2252 | 2 | 44
39014.5797 | 1941 | 7 | 44
44
39014.5434 | 1 | 0 | 45
39014.5455 | 1 | 0 | 45
39014.5476 | 1 | 0 | 45
39014.5498 | 1 | 0 | 45
39014.5519 | 1 | 0 | 45
39014.5541 | 1 | 0 | 45
39014.5562 | 1 | 0 | 45
39014.5583 | 1 | 0 | 45
39014.5605 | 1689 | 0 | 45
39014.5626 | 1975 | 0 | 45
39014.5647 | 2511 | 0 | 45
39014.5669 | 2089 | 0 | 45
39014.569 | 2068 | 0 | 45
39014.5712 | 2528 | 0 | 45
39014.5733 | 2429 | 0 | 45
39014.5754 | 2182 | 0 | 45
39014.5776 | 2182 | 0 | 45
39014.5797 | 1998 | 0 | 45
45
39014.5434 | 1 | 0 | 46
39014.5455 | 1 | 0 | 46
39014.5477 | 1 | 0 | 46
39014.5498 | 1 | 0 | 46
39014.5519 | 1 | 0 | 46
39014.5541 | 1 | 0 | 46
39014.5562 | 1 | 0 | 46
39014.5583 | 1 | 0 | 46
39014.5605 | 2 | 0 | 46
39014.5626 | 851 | 0 | 46
39014.5648 | 1813 | 0 | 46
39014.5669 | 2216 | 0 | 46
39014.569 | 2012 | 0 | 46
39014.5712 | 2413 | 0 | 46
39014.5733 | 2175 | 0 | 46
39014.5755 | 2005 | 0 | 46
39014.5776 | 2276 | 0 | 46
39014.5797 | 1705 | 0 | 46
46
39014.5434 | 1 | 0 | 47
39014.5455 | 1 | 0 | 47
39014.5477 | 1 | 0 | 47
39014.5498 | 1 | 0 | 47
39014.5519 | 1 | 0 | 47
39014.5541 | 1 | 0 | 47
39014.5562 | 1 | 0 | 47
39014.5584 | 2 | 0 | 47
39014.5605 | 973 | 0 | 47
39014.5626 | 1879 | 0 | 47
39014.5648 | 2157 | 0 | 47
39014.5669 | 2518 | 0 | 47
39014.5691 | 2309 | 0 | 47
39014.5712 | 2355 | 0 | 47
39014.5733 | 2145 | 0 | 47
39014.5755 | 1978 | 0 | 47
39014.5776 | 2265 | 0 | 47
39014.5797 | 1996 | 0 | 47
47
39014.5434 | 1 | 0 | 48
39014.5455 | 1 | 0 | 48
39014.5477 | 1 | 0 | 48
39014.5498 | 1 | 0 | 48
39014.552 | 1 | 0 | 48
39014.5541 | 1 | 0 | 48
39014.5562 | 1 | 0 | 48
39014.5584 | 1 | 0 | 48
39014.5605 | 1 | 0 | 48
39014.5627 | 1443 | 0 | 48
39014.5648 | 1848 | 0 | 48
39014.5669 | 1952 | 0 | 48
39014.5691 | 2151 | 0 | 48
39014.5712 | 2405 | 0 | 48
39014.5733 | 1855 | 0 | 48
39014.5755 | 2341 | 0 | 48
39014.5776 | 1819 | 0 | 48
39014.5798 | 2020 | 0 | 48
48
39014.5434 | 1 | 0 | 49
39014.5456 | 1 | 0 | 49
39014.5477 | 1 | 0 | 49
39014.5498 | 1 | 0 | 49
39014.552 | 1 | 0 | 49
39014.5541 | 1 | 0 | 49
39014.5563 | 1 | 0 | 49
39014.5584 | 3 | 0 | 49
39014.5605 | 1168 | 0 | 49
39014.5627 | 2390 | 0 | 49
39014.5648 | 2545 | 0 | 49
39014.567 | 2251 | 0 | 49
39014.5691 | 2301 | 0 | 49
39014.5712 | 1983 | 0 | 49
39014.5734 | 2348 | 0 | 49
39014.5755 | 2487 | 0 | 49
39014.5776 | 2190 | 0 | 49
39014.5798 | 2276 | 0 | 49
49
39014.5434 | 1 | 0 | 50
39014.5456 | 1 | 0 | 50
39014.5477 | 1 | 0 | 50
39014.5499 | 1 | 0 | 50
39014.552 | 2 | 0 | 50
39014.5541 | 2068 | 0 | 50
39014.5563 | 2174 | 0 | 50
39014.5584 | 2526 | 0 | 50
39014.5606 | 1986 | 0 | 50
39014.5627 | 2327 | 0 | 50
39014.5648 | 2568 | 0 | 50
39014.567 | 2457 | 0 | 50
39014.5691 | 2600 | 0 | 50
39014.5712 | 2384 | 0 | 50
39014.5734 | 2434 | 0 | 50
39014.5755 | 2279 | 0 | 50
39014.5777 | 2338 | 0 | 50
39014.5798 | 2251 | 0 | 50
50
39014.5435 | 1 | 0 | 51
39014.5456 | 2 | 0 | 51
39014.5477 | 1 | 0 | 51
39014.5499 | 1 | 0 | 51
39014.552 | 1 | 0 | 51
39014.5542 | 2 | 0 | 51
39014.5563 | 1 | 0 | 51
39014.5584 | 5 | 0 | 51
39014.5606 | 1570 | 0 | 51
39014.5627 | 2187 | 0 | 51
39014.5648 | 2414 | 0 | 51
39014.567 | 2524 | 0 | 51
39014.5691 | 2005 | 0 | 51
39014.5713 | 1981 | 0 | 51
39014.5734 | 2201 | 0 | 51
39014.5755 | 2097 | 0 | 51
39014.5777 | 2181 | 0 | 51
39014.5798 | 2068 | 0 | 51
51
39014.5435 | 1 | 0 | 52
39014.5456 | 1 | 0 | 52
39014.5478 | 1 | 0 | 52
39014.5499 | 1 | 0 | 52
39014.552 | 1 | 0 | 52
39014.5542 | 2161 | 0 | 52
39014.5563 | 2406 | 0 | 52
39014.5584 | 2025 | 0 | 52
39014.5606 | 2284 | 0 | 52
39014.5627 | 2535 | 0 | 52
39014.5649 | 2036 | 0 | 52
39014.567 | 2316 | 0 | 52
39014.5691 | 2180 | 0 | 52
39014.5713 | 2292 | 0 | 52
39014.5734 | 2126 | 0 | 52
39014.5756 | 2402 | 0 | 52
39014.5777 | 2029 | 0 | 52
39014.5798 | 2412 | 0 | 52
52
39014.5435 | 1 | 0 | 53
39014.5456 | 1 | 0 | 53
39014.5478 | 1 | 0 | 53
39014.5499 | 1 | 0 | 53
39014.552 | 1 | 0 | 53
39014.5542 | 1 | 0 | 53
39014.5563 | 1 | 0 | 53
39014.5585 | 8 | 0 | 53
39014.5606 | 1543 | 0 | 53
39014.5627 | 2000 | 0 | 53
39014.5649 | 2173 | 0 | 53
39014.567 | 2054 | 0 | 53
39014.5692 | 2374 | 0 | 53
39014.5713 | 2457 | 0 | 53
39014.5734 | 2379 | 0 | 53
39014.5777 | 2093 | 0 | 53
39014.5798 | 2115 | 0 | 53
53
39014.5435 | 1 | 0 | 54
39014.5456 | 1 | 0 | 54
39014.5478 | 1 | 0 | 54
39014.5499 | 1 | 0 | 54
39014.5521 | 1 | 0 | 54
39014.5542 | 1 | 0 | 54
39014.5563 | 1 | 0 | 54
39014.5585 | 1998 | 0 | 54
39014.5606 | 2255 | 0 | 54
39014.5628 | 2525 | 0 | 54
39014.5649 | 2504 | 0 | 54
39014.567 | 2169 | 0 | 54
39014.5692 | 2311 | 0 | 54
39014.5713 | 2476 | 0 | 54
39014.5734 | 2217 | 0 | 54
39014.5756 | 2206 | 0 | 54
39014.5777 | 2405 | 0 | 54
39014.5799 | 2525 | 0 | 54
54
39014.5435 | 1 | 0 | 55
39014.5457 | 1 | 0 | 55
39014.5478 | 1 | 0 | 55
39014.5499 | 1 | 0 | 55
39014.5521 | 1 | 0 | 55
39014.5542 | 1 | 0 | 55
39014.5564 | 1 | 0 | 55
39014.5585 | 11 | 0 | 55
39014.5606 | 1526 | 0 | 55
39014.5628 | 2172 | 0 | 55
39014.5649 | 2197 | 0 | 55
39014.567 | 2105 | 0 | 55
39014.5692 | 2426 | 0 | 55
39014.5713 | 2511 | 0 | 55
39014.5735 | 2447 | 0 | 55
39014.5756 | 2394 | 0 | 55
39014.5777 | 1954 | 0 | 55
39014.5799 | 2413 | 0 | 55
55
39014.5435 | 1 | 0 | 56
39014.5457 | 1 | 0 | 56
39014.5478 | 1 | 0 | 56
39014.55 | 1 | 0 | 56
39014.5521 | 1 | 0 | 56
39014.5542 | 1 | 0 | 56
39014.5564 | 1572 | 0 | 56
39014.5585 | 2323 | 0 | 56
39014.5606 | 2372 | 0 | 56
39014.5628 | 2264 | 0 | 56
39014.5649 | 2145 | 0 | 56
39014.5671 | 2602 | 0 | 56
39014.5692 | 2447 | 0 | 56
39014.5713 | 2182 | 0 | 56
39014.5735 | 2147 | 0 | 56
39014.5756 | 2177 | 0 | 56
39014.5778 | 2384 | 0 | 56
39014.5799 | 2370 | 0 | 56
56
39014.5436 | 1 | 0 | 57
39014.5457 | 1 | 0 | 57
39014.5478 | 1 | 0 | 57
39014.55 | 1 | 0 | 57
39014.5521 | 1 | 0 | 57
39014.5542 | 1 | 0 | 57
39014.5564 | 1 | 0 | 57
39014.5585 | 15 | 0 | 57
39014.5607 | 1726 | 0 | 57
39014.5628 | 1868 | 0 | 57
39014.5649 | 2114 | 0 | 57
39014.5671 | 2565 | 0 | 57
39014.5692 | 2155 | 0 | 57
39014.5714 | 2186 | 0 | 57
39014.5735 | 2229 | 0 | 57
39014.5756 | 2365 | 0 | 57
39014.5778 | 2128 | 0 | 57
39014.5799 | 2364 | 0 | 57
57
39014.5436 | 1 | 0 | 58
39014.5457 | 1 | 0 | 58
39014.5478 | 1 | 0 | 58
39014.55 | 1 | 0 | 58
39014.5521 | 1 | 0 | 58
39014.5543 | 1 | 0 | 58
39014.5564 | 2 | 0 | 58
39014.5585 | 1937 | 0 | 58
39014.5607 | 1924 | 0 | 58
39014.5628 | 2164 | 0 | 58
39014.565 | 2501 | 0 | 58
39014.5671 | 2259 | 0 | 58
39014.5692 | 2269 | 0 | 58
39014.5714 | 2260 | 0 | 58
39014.5735 | 2058 | 0 | 58
39014.5756 | 2180 | 0 | 58
39014.5778 | 1970 | 0 | 58
39014.5799 | 2216 | 0 | 58
58
39014.5436 | 1 | 0 | 59
39014.5457 | 1 | 0 | 59
39014.5479 | 1 | 0 | 59
39014.55 | 1 | 0 | 59
39014.5521 | 1 | 0 | 59
39014.5543 | 1 | 0 | 59
39014.5564 | 1 | 0 | 59
39014.5586 | 17 | 0 | 59
39014.5607 | 1546 | 0 | 59
39014.5628 | 2326 | 0 | 59
39014.565 | 1996 | 0 | 59
39014.5671 | 2133 | 0 | 59
39014.5692 | 2044 | 0 | 59
39014.5714 | 1975 | 0 | 59
39014.5735 | 2432 | 0 | 59
39014.5757 | 2142 | 0 | 59
39014.5778 | 2462 | 0 | 59
39014.5799 | 2142 | 0 | 59
59
39014.5436 | 1 | 0 | 60
39014.5457 | 1 | 0 | 60
39014.5479 | 1 | 0 | 60
39014.55 | 1 | 0 | 60
39014.5522 | 1 | 0 | 60
39014.5543 | 1 | 0 | 60
39014.5564 | 1 | 0 | 60
39014.5586 | 1 | 0 | 60
39014.5607 | 2 | 0 | 60
39014.5628 | 1 | 0 | 60
39014.565 | 1 | 0 | 60
39014.5671 | 2 | 0 | 60
39014.5693 | 1 | 0 | 60
39014.5714 | 2 | 0 | 60
39014.5735 | 1 | 0 | 60
39014.5757 | 1 | 0 | 60
39014.5778 | 1 | 0 | 60
39014.58 | 2 | 0 | 60
60
39014.5436 | 1 | 0 | 61
39014.5458 | 1 | 0 | 61
39014.5479 | 1 | 0 | 61
39014.55 | 1 | 0 | 61
39014.5522 | 0 | 0 | 61
39014.5543 | 1 | 0 | 61
39014.5564 | 1 | 0 | 61
39014.5586 | 16 | 0 | 61
39014.5607 | 1842 | 0 | 61
39014.5629 | 1864 | 0 | 61
39014.565 | 1977 | 0 | 61
39014.5671 | 2539 | 0 | 61
39014.5693 | 2343 | 0 | 61
39014.5714 | 1950 | 0 | 61
39014.5736 | 1937 | 0 | 61
39014.5757 | 2181 | 0 | 61
39014.5778 | 2036 | 0 | 61
39014.58 | 2076 | 0 | 61
61
39014.5436 | 1 | 0 | 62
39014.5458 | 1 | 0 | 62
39014.5479 | 1 | 0 | 62
39014.5501 | 1 | 0 | 62
39014.5522 | 1 | 0 | 62
39014.5543 | 1 | 0 | 62
39014.5565 | 1 | 0 | 62
39014.5586 | 1 | 0 | 62
39014.5607 | 1 | 0 | 62
39014.5629 | 972 | 0 | 62
39014.565 | 2239 | 0 | 62
39014.5672 | 2110 | 0 | 62
39014.5693 | 2335 | 0 | 62
39014.5714 | 2229 | 0 | 62
39014.5736 | 2058 | 0 | 62
39014.5757 | 2056 | 0 | 62
39014.5778 | 1970 | 0 | 62
39014.58 | 1999 | 0 | 62
62
39014.5437 | 1 | 0 | 63
39014.5458 | 1 | 0 | 63
39014.5479 | 1 | 0 | 63
39014.5501 | 1 | 0 | 63
39014.5522 | 1 | 0 | 63
39014.5543 | 1 | 0 | 63
39014.5565 | 1 | 0 | 63
39014.5586 | 13 | 0 | 63
39014.5608 | 1836 | 0 | 63
39014.5629 | 1861 | 0 | 63
39014.565 | 2216 | 0 | 63
39014.5672 | 2518 | 0 | 63
39014.5693 | 2021 | 0 | 63
39014.5715 | 1950 | 0 | 63
39014.5736 | 2507 | 0 | 63
39014.5757 | 2421 | 0 | 63
39014.5779 | 2159 | 0 | 63
39014.58 | 1995 | 0 | 63
63
39014.5437 | 1 | 0 | 64
39014.5458 | 1 | 0 | 64
39014.548 | 1 | 0 | 64
39014.5501 | 1 | 0 | 64
39014.5522 | 1 | 0 | 64
39014.5544 | 1 | 0 | 64
39014.5565 | 1 | 0 | 64
39014.5586 | 1 | 0 | 64
39014.5608 | 1 | 0 | 64
39014.5629 | 1174 | 0 | 64
39014.5651 | 1918 | 0 | 64
39014.5672 | 2372 | 0 | 64
39014.5693 | 2249 | 0 | 64
39014.5715 | 2375 | 0 | 64
39014.5736 | 1880 | 0 | 64
39014.5758 | 2194 | 0 | 64
39014.5779 | 2142 | 0 | 64
39014.58 | 1937 | 0 | 64
64
39014.5437 | 1 | 0 | 65
39014.5458 | 1 | 0 | 65
39014.548 | 1 | 0 | 65
39014.5501 | 1 | 0 | 65
39014.5522 | 1 | 0 | 65
39014.5544 | 1 | 0 | 65
39014.5565 | 1 | 0 | 65
39014.5587 | 16 | 0 | 65
39014.5608 | 1645 | 0 | 65
39014.5629 | 2373 | 0 | 65
39014.5651 | 2373 | 0 | 65
39014.5672 | 1982 | 0 | 65
39014.5694 | 2164 | 0 | 65
39014.5715 | 2516 | 0 | 65
39014.5736 | 2462 | 0 | 65
39014.5758 | 2490 | 0 | 65
39014.5779 | 2291 | 0 | 65
39014.58 | 2138 | 0 | 65
65
39014.5437 | 1 | 0 | 66
39014.5458 | 1 | 0 | 66
39014.548 | 1 | 0 | 66
39014.5501 | 1 | 0 | 66
39014.5523 | 25 | 0 | 66
39014.5544 | 2265 | 0 | 66
39014.5565 | 2026 | 0 | 66
39014.5587 | 2260 | 0 | 66
39014.5608 | 2179 | 0 | 66
39014.563 | 2415 | 0 | 66
39014.5651 | 2215 | 0 | 66
39014.5672 | 2366 | 0 | 66
39014.5694 | 2130 | 0 | 66
39014.5715 | 2070 | 0 | 66
39014.5736 | 2063 | 0 | 66
39014.5758 | 2058 | 0 | 66
39014.5779 | 2325 | 0 | 66
39014.5801 | 2456 | 0 | 66
66
39014.5437 | 1 | 0 | 67
39014.5459 | 1 | 0 | 67
39014.548 | 1 | 0 | 67
39014.5501 | 1 | 0 | 67
39014.5523 | 1 | 0 | 67
39014.5544 | 1 | 0 | 67
39014.5566 | 2 | 0 | 67
39014.5587 | 18 | 0 | 67
39014.5608 | 1596 | 0 | 67
39014.563 | 2418 | 0 | 67
39014.5651 | 2113 | 0 | 67
39014.5672 | 2278 | 0 | 67
39014.5694 | 2144 | 0 | 67
39014.5715 | 2171 | 0 | 67
39014.5737 | 2426 | 0 | 67
39014.5758 | 2486 | 0 | 67
39014.5779 | 2433 | 0 | 67
39014.5801 | 2138 | 0 | 67
67
39014.5437 | 1 | 0 | 68
39014.5459 | 1 | 0 | 68
39014.548 | 1 | 0 | 68
39014.5502 | 1 | 0 | 68
39014.5523 | 17 | 0 | 68
39014.5544 | 1955 | 0 | 68
39014.5566 | 2005 | 0 | 68
39014.5587 | 1968 | 0 | 68
39014.5608 | 2362 | 0 | 68
39014.563 | 2573 | 0 | 68
39014.5651 | 2224 | 0 | 68
39014.5673 | 2532 | 0 | 68
39014.5694 | 2498 | 0 | 68
39014.5715 | 2470 | 0 | 68
39014.5737 | 2389 | 0 | 68
39014.5758 | 2187 | 0 | 68
39014.578 | 2199 | 0 | 68
39014.5801 | 2515 | 0 | 68
68
39014.5437 | 1 | 0 | 69
39014.5459 | 1 | 0 | 69
39014.548 | 1 | 0 | 69
39014.5502 | 1 | 0 | 69
39014.5523 | 1 | 0 | 69
39014.5544 | 1 | 0 | 69
39014.5566 | 1 | 0 | 69
39014.5587 | 21 | 0 | 69
39014.5609 | 1608 | 0 | 69
39014.563 | 1895 | 0 | 69
39014.5651 | 2056 | 0 | 69
39014.5673 | 2234 | 0 | 69
39014.5694 | 2531 | 0 | 69
39014.5716 | 2366 | 0 | 69
39014.5737 | 2023 | 0 | 69
39014.5758 | 2423 | 0 | 69
39014.578 | 2041 | 0 | 69
39014.5801 | 1907 | 0 | 69
69
39014.5438 | 1 | 0 | 70
39014.5459 | 1 | 0 | 70
39014.548 | 1 | 0 | 70
39014.5502 | 1 | 0 | 70
39014.5523 | 1 | 0 | 70
39014.5545 | 1 | 0 | 70
39014.5566 | 4 | 0 | 70
39014.5587 | 2129 | 0 | 70
39014.5609 | 2543 | 0 | 70
39014.563 | 2528 | 0 | 70
39014.5673 | 2520 | 0 | 70
39014.5694 | 2114 | 0 | 70
39014.5716 | 2249 | 0 | 70
39014.5737 | 2350 | 0 | 70
39014.5758 | 2004 | 0 | 70
39014.578 | 2445 | 0 | 70
39014.5801 | 2078 | 0 | 70
70
39014.5438 | 1 | 0 | 71
39014.5459 | 1 | 0 | 71
39014.5481 | 1 | 0 | 71
39014.5502 | 1 | 0 | 71
39014.5523 | 1 | 0 | 71
39014.5545 | 1 | 0 | 71
39014.5566 | 1 | 0 | 71
39014.5587 | 30 | 0 | 71
39014.5609 | 1754 | 0 | 71
39014.563 | 2381 | 0 | 71
39014.5652 | 2325 | 0 | 71
39014.5673 | 2558 | 0 | 71
39014.5694 | 2373 | 0 | 71
39014.5716 | 1988 | 0 | 71
39014.5737 | 2483 | 0 | 71
39014.5759 | 2300 | 0 | 71
39014.578 | 2386 | 0 | 71
39014.5801 | 2258 | 0 | 71
71
39014.5438 | 1 | 0 | 72
39014.5459 | 1 | 0 | 72
39014.5481 | 1 | 0 | 72
39014.5502 | 1 | 0 | 72
39014.5523 | 1 | 0 | 72
39014.5545 | 1 | 0 | 72
39014.5566 | 1817 | 0 | 72
39014.5588 | 2433 | 0 | 72
39014.5609 | 2426 | 0 | 72
39014.563 | 2232 | 0 | 72
39014.5652 | 2249 | 0 | 72
39014.5673 | 2472 | 0 | 72
39014.5695 | 2484 | 0 | 72
39014.5716 | 2216 | 0 | 72
39014.5737 | 2494 | 0 | 72
39014.5759 | 2134 | 0 | 72
39014.578 | 2034 | 0 | 72
39014.5802 | 2431 | 0 | 72
72
39014.5438 | 1 | 0 | 73
39014.5459 | 1 | 0 | 73
39014.5481 | 1 | 0 | 73
39014.5502 | 1 | 0 | 73
39014.5524 | 1 | 0 | 73
39014.5545 | 1 | 0 | 73
39014.5566 | 1 | 0 | 73
39014.5588 | 39 | 0 | 73
39014.5609 | 2082 | 0 | 73
39014.5631 | 2373 | 0 | 73
39014.5652 | 2415 | 0 | 73
39014.5673 | 2205 | 0 | 73
39014.5695 | 2385 | 0 | 73
39014.5716 | 2480 | 0 | 73
39014.5738 | 2361 | 0 | 73
39014.5759 | 2250 | 0 | 73
39014.578 | 2459 | 0 | 73
39014.5802 | 2191 | 0 | 73
73
39014.5438 | 1 | 0 | 74
39014.546 | 1 | 0 | 74
39014.5481 | 1 | 0 | 74
39014.5502 | 1 | 0 | 74
39014.5524 | 1 | 0 | 74
39014.5545 | 1 | 0 | 74
39014.5567 | 7 | 0 | 74
39014.5588 | 2055 | 0 | 74
39014.5609 | 2016 | 0 | 74
39014.5631 | 2257 | 0 | 74
39014.5652 | 2483 | 0 | 74
39014.5673 | 2015 | 0 | 74
39014.5695 | 2203 | 0 | 74
39014.5716 | 2544 | 0 | 74
39014.5738 | 2433 | 0 | 74
39014.5759 | 2519 | 0 | 74
39014.578 | 2189 | 0 | 74
39014.5802 | 2478 | 0 | 74
74
39014.5438 | 1 | 0 | 75
39014.546 | 1 | 0 | 75
39014.5481 | 1 | 0 | 75
39014.5503 | 1 | 0 | 75
39014.5524 | 1 | 0 | 75
39014.5545 | 1 | 0 | 75
39014.5567 | 1 | 0 | 75
39014.5588 | 50 | 0 | 75
39014.5609 | 2092 | 0 | 75
39014.5631 | 2019 | 0 | 75
39014.5652 | 2042 | 0 | 75
39014.5674 | 2173 | 0 | 75
39014.5695 | 2406 | 0 | 75
39014.5716 | 2367 | 0 | 75
39014.5738 | 2362 | 0 | 75
39014.5759 | 2448 | 0 | 75
39014.5781 | 2035 | 0 | 75
39014.5802 | 1876 | 0 | 75
75
39014.5439 | 1 | 0 | 76
39014.546 | 1 | 0 | 76
39014.5481 | 1 | 0 | 76
39014.5503 | 1 | 0 | 76
39014.5524 | 1 | 0 | 76
39014.5546 | 1 | 0 | 76
39014.5567 | 1 | 0 | 76
39014.5588 | 1 | 0 | 76
39014.561 | 1 | 0 | 76
39014.5631 | 2 | 0 | 76
39014.5653 | 2 | 0 | 76
39014.5674 | 2 | 0 | 76
39014.5695 | 1 | 0 | 76
39014.5717 | 2 | 0 | 76
39014.5738 | 2 | 0 | 76
39014.5759 | 2 | 0 | 76
39014.5781 | 1 | 0 | 76
39014.5802 | 1 | 0 | 76
76
39014.5439 | 1 | 0 | 77
39014.546 | 1 | 0 | 77
39014.5482 | 1 | 0 | 77
39014.5503 | 1 | 0 | 77
39014.5524 | 1 | 0 | 77
39014.5546 | 1 | 0 | 77
39014.5567 | 1 | 0 | 77
39014.5589 | 1 | 0 | 77
39014.561 | 592 | 530 | 77
39014.5631 | 1820 | 492 | 77
39014.5653 | 1939 | 54 | 77
39014.5674 | 2383 | 15 | 77
39014.5695 | 2191 | 17 | 77
39014.5717 | 2231 | 20 | 77
39014.5738 | 1998 | 31 | 77
39014.576 | 2357 | 63 | 77
39014.5781 | 2263 | 118 | 77
39014.5802 | 2088 | 181 | 77
77
39014.5439 | 1 | 0 | 78
39014.546 | 1 | 0 | 78
39014.5482 | 1 | 0 | 78
39014.5503 | 1 | 0 | 78
39014.5525 | 1 | 0 | 78
39014.5546 | 1 | 0 | 78
39014.5567 | 1 | 0 | 78
39014.5589 | 1 | 0 | 78
39014.561 | 570 | 513 | 78
39014.5631 | 1934 | 484 | 78
39014.5653 | 2095 | 57 | 78
39014.5674 | 1951 | 12 | 78
39014.5696 | 1973 | 15 | 78
39014.5717 | 1999 | 19 | 78
39014.5738 | 2332 | 36 | 78
39014.576 | 2187 | 77 | 78
39014.5781 | 2177 | 120 | 78
39014.5803 | 1864 | 161 | 78
78
39014.5439 | 1 | 0 | 79
39014.5461 | 1 | 0 | 79
39014.5482 | 1 | 0 | 79
39014.5503 | 1 | 0 | 79
39014.5525 | 1 | 0 | 79
39014.5546 | 1 | 0 | 79
39014.5567 | 1 | 0 | 79
39014.5589 | 1 | 0 | 79
39014.561 | 2 | 0 | 79
39014.5632 | 1785 | 0 | 79
39014.5653 | 2341 | 0 | 79
39014.5674 | 2056 | 0 | 79
39014.5696 | 2144 | 0 | 79
39014.5717 | 2011 | 0 | 79
39014.5739 | 2284 | 0 | 79
39014.576 | 1913 | 0 | 79
39014.5781 | 1936 | 0 | 79
39014.5803 | 1982 | 0 | 79
79
39014.5439 | 1 | 0 | 80
39014.5461 | 1 | 0 | 80
39014.5482 | 1 | 0 | 80
39014.5503 | 1 | 0 | 80
39014.5525 | 114 | 0 | 80
39014.5546 | 2009 | 0 | 80
39014.5568 | 1984 | 0 | 80
39014.5589 | 1979 | 0 | 80
39014.561 | 2514 | 0 | 80
39014.5632 | 2207 | 0 | 80
39014.5653 | 2549 | 0 | 80
39014.5675 | 2012 | 0 | 80
39014.5696 | 2058 | 0 | 80
39014.5717 | 2276 | 0 | 80
39014.5739 | 2539 | 0 | 80
39014.576 | 2362 | 0 | 80
39014.5781 | 2015 | 0 | 80
39014.5803 | 2567 | 0 | 80
80
39014.5439 | 1 | 0 | 81
39014.5461 | 1 | 0 | 81
39014.5482 | 1 | 0 | 81
39014.5504 | 1 | 0 | 81
39014.5525 | 1 | 0 | 81
39014.5546 | 2 | 0 | 81
39014.5568 | 1 | 0 | 81
39014.5589 | 1 | 0 | 81
39014.5611 | 2 | 0 | 81
39014.5632 | 1459 | 0 | 81
39014.5653 | 2364 | 0 | 81
39014.5675 | 2042 | 0 | 81
39014.5696 | 2418 | 0 | 81
39014.5717 | 2389 | 0 | 81
39014.5739 | 2299 | 0 | 81
39014.576 | 2312 | 0 | 81
39014.5782 | 2240 | 0 | 81
39014.5803 | 2042 | 0 | 81
81
39014.544 | 1 | 0 | 82
39014.5461 | 1 | 0 | 82
39014.5482 | 1 | 0 | 82
39014.5504 | 1 | 0 | 82
39014.5525 | 1762 | 0 | 82
39014.5547 | 1976 | 0 | 82
39014.5568 | 2494 | 0 | 82
39014.5589 | 2360 | 0 | 82
39014.5611 | 2138 | 0 | 82
39014.5632 | 2494 | 0 | 82
39014.5653 | 2011 | 0 | 82
39014.5675 | 2542 | 0 | 82
39014.5696 | 2359 | 0 | 82
39014.5718 | 2152 | 0 | 82
39014.5739 | 2111 | 0 | 82
39014.576 | 2318 | 0 | 82
39014.5782 | 2253 | 0 | 82
39014.5803 | 2492 | 0 | 82
82
39014.544 | 1 | 0 | 83
39014.5461 | 1 | 0 | 83
39014.5483 | 1 | 0 | 83
39014.5504 | 1 | 0 | 83
39014.5525 | 1 | 0 | 83
39014.5547 | 1 | 0 | 83
39014.5568 | 1 | 0 | 83
39014.5589 | 1 | 0 | 83
39014.5611 | 2 | 0 | 83
39014.5632 | 1240 | 0 | 83
39014.5654 | 1983 | 0 | 83
39014.5675 | 1938 | 0 | 83
39014.5696 | 2247 | 0 | 83
39014.5718 | 2354 | 0 | 83
39014.5739 | 2389 | 0 | 83
39014.5761 | 2174 | 0 | 83
39014.5782 | 2114 | 0 | 83
39014.5803 | 2031 | 0 | 83
83
39014.544 | 1 | 0 | 84
39014.5461 | 1 | 0 | 84
39014.5483 | 1 | 0 | 84
39014.5504 | 1 | 0 | 84
39014.5525 | 1 | 0 | 84
39014.5547 | 1 | 0 | 84
39014.5568 | 11 | 0 | 84
39014.559 | 2015 | 0 | 84
39014.5611 | 2237 | 0 | 84
39014.5632 | 2133 | 0 | 84
39014.5654 | 2504 | 0 | 84
39014.5675 | 2026 | 0 | 84
39014.5697 | 2578 | 0 | 84
39014.5718 | 2055 | 0 | 84
39014.5739 | 2003 | 0 | 84
39014.5761 | 2302 | 0 | 84
39014.5782 | 2525 | 0 | 84
39014.5803 | 2506 | 0 | 84
84
39014.544 | 1 | 0 | 85
39014.5461 | 1 | 0 | 85
39014.5483 | 1 | 0 | 85
39014.5504 | 1 | 0 | 85
39014.5526 | 1 | 0 | 85
39014.5547 | 1 | 0 | 85
39014.5568 | 1 | 0 | 85
39014.559 | 1 | 0 | 85
39014.5611 | 3 | 0 | 85
39014.5633 | 1599 | 0 | 85
39014.5654 | 2273 | 0 | 85
39014.5675 | 2366 | 0 | 85
39014.5697 | 2189 | 0 | 85
39014.5718 | 2094 | 0 | 85
39014.5739 | 2055 | 0 | 85
39014.5761 | 2190 | 0 | 85
39014.5782 | 1881 | 0 | 85
39014.5804 | 2067 | 0 | 85
85
39014.544 | 1 | 0 | 86
39014.5462 | 1 | 0 | 86
39014.5483 | 1 | 0 | 86
39014.5504 | 1 | 0 | 86
39014.5526 | 1 | 0 | 86
39014.5547 | 1 | 0 | 86
39014.5569 | 1945 | 0 | 86
39014.559 | 2498 | 0 | 86
39014.5611 | 2539 | 0 | 86
39014.5633 | 2222 | 0 | 86
39014.5654 | 2434 | 0 | 86
39014.5675 | 2013 | 0 | 86
39014.5697 | 2583 | 0 | 86
39014.5718 | 2167 | 0 | 86
39014.574 | 2498 | 0 | 86
39014.5761 | 2542 | 0 | 86
39014.5782 | 2123 | 0 | 86
39014.5804 | 2132 | 0 | 86
86
39014.544 | 1 | 0 | 87
39014.5462 | 1 | 0 | 87
39014.5483 | 1 | 0 | 87
39014.5505 | 1 | 0 | 87
39014.5526 | 1 | 0 | 87
39014.5547 | 1 | 0 | 87
39014.5569 | 1 | 0 | 87
39014.559 | 1 | 0 | 87
39014.5611 | 3 | 0 | 87
39014.5633 | 1388 | 0 | 87
39014.5654 | 2382 | 0 | 87
39014.5676 | 2221 | 0 | 87
39014.5697 | 2157 | 0 | 87
39014.5718 | 2414 | 0 | 87
39014.574 | 1852 | 0 | 87
39014.5761 | 2337 | 0 | 87
39014.5783 | 2272 | 0 | 87
39014.5804 | 1843 | 0 | 87
87
39014.5441 | 1 | 0 | 88
39014.5462 | 1 | 0 | 88
39014.5483 | 1 | 0 | 88
39014.5505 | 1 | 0 | 88
39014.5526 | 1 | 0 | 88
39014.5547 | 1 | 0 | 88
39014.5569 | 55 | 0 | 88
39014.559 | 2075 | 0 | 88
39014.5612 | 2179 | 0 | 88
39014.5633 | 2251 | 0 | 88
39014.5654 | 2087 | 0 | 88
39014.5676 | 2102 | 0 | 88
39014.5697 | 1995 | 0 | 88
39014.5719 | 2570 | 0 | 88
39014.574 | 2171 | 0 | 88
39014.5761 | 2154 | 0 | 88
39014.5783 | 2117 | 0 | 88
39014.5804 | 2034 | 0 | 88
88
39014.5441 | 1 | 0 | 89
39014.5462 | 1 | 0 | 89
39014.5484 | 1 | 0 | 89
39014.5505 | 1 | 0 | 89
39014.5526 | 1 | 0 | 89
39014.5548 | 1 | 0 | 89
39014.5569 | 1 | 0 | 89
39014.559 | 1 | 0 | 89
39014.5612 | 5 | 0 | 89
39014.5633 | 1719 | 0 | 89
39014.5655 | 2326 | 0 | 89
39014.5676 | 2133 | 0 | 89
39014.5697 | 2058 | 0 | 89
39014.5719 | 1974 | 0 | 89
39014.574 | 2241 | 0 | 89
39014.5762 | 2337 | 0 | 89
39014.5783 | 2170 | 0 | 89
39014.5804 | 1872 | 0 | 89
89
39014.5441 | 1 | 0 | 90
39014.5462 | 1 | 0 | 90
39014.5484 | 1 | 0 | 90
39014.5505 | 1 | 0 | 90
39014.5527 | 1 | 0 | 90
39014.5548 | 1 | 0 | 90
39014.5569 | 1 | 0 | 90
39014.5591 | 1 | 0 | 90
39014.5612 | 1 | 0 | 90
39014.5633 | 1 | 0 | 90
39014.5655 | 1 | 0 | 90
39014.5676 | 2 | 0 | 90
39014.5698 | 1 | 0 | 90
39014.5719 | 2 | 0 | 90
39014.574 | 2 | 0 | 90
39014.5762 | 1 | 0 | 90
39014.5783 | 2 | 0 | 90
39014.5805 | 2 | 0 | 90
90
39014.5441 | 1 | 0 | 91
39014.5462 | 1 | 0 | 91
39014.5484 | 1 | 0 | 91
39014.5505 | 1 | 0 | 91
39014.5527 | 1 | 0 | 91
39014.5548 | 1 | 0 | 91
39014.5569 | 1 | 0 | 91
39014.5591 | 1 | 0 | 91
39014.5612 | 6 | 0 | 91
39014.5634 | 1966 | 0 | 91
39014.5655 | 2289 | 0 | 91
39014.5676 | 1911 | 0 | 91
39014.5698 | 2420 | 0 | 91
39014.5719 | 2080 | 0 | 91
39014.5741 | 1898 | 0 | 91
39014.5762 | 2319 | 0 | 91
39014.5783 | 2177 | 0 | 91
39014.5805 | 1751 | 0 | 91
91
39014.5441 | 1 | 0 | 92
39014.5463 | 1 | 0 | 92
39014.5484 | 1 | 0 | 92
39014.5505 | 1 | 0 | 92
39014.5527 | 351 | 0 | 92
39014.5548 | 2117 | 0 | 92
39014.557 | 2064 | 0 | 92
39014.5591 | 2528 | 0 | 92
39014.5612 | 2499 | 0 | 92
39014.5634 | 2585 | 0 | 92
39014.5655 | 2282 | 0 | 92
39014.5677 | 2500 | 0 | 92
39014.5698 | 2117 | 0 | 92
39014.5719 | 2258 | 0 | 92
39014.5741 | 2224 | 0 | 92
39014.5762 | 2555 | 0 | 92
39014.5783 | 2388 | 0 | 92
39014.5805 | 2240 | 0 | 92
92
39014.5441 | 1 | 0 | 93
39014.5463 | 1 | 0 | 93
39014.5484 | 1 | 0 | 93
39014.5506 | 1 | 0 | 93
39014.5527 | 1 | 0 | 93
39014.5548 | 1 | 0 | 93
39014.557 | 1 | 0 | 93
39014.5591 | 1 | 0 | 93
39014.5612 | 8 | 0 | 93
39014.5634 | 1995 | 0 | 93
39014.5655 | 1869 | 0 | 93
39014.5677 | 2427 | 0 | 93
39014.5698 | 1934 | 0 | 93
39014.5719 | 2281 | 0 | 93
39014.5741 | 2320 | 0 | 93
39014.5762 | 2333 | 0 | 93
39014.5784 | 2249 | 0 | 93
39014.5805 | 1728 | 0 | 93
93
39014.5442 | 1 | 0 | 94
39014.5463 | 1 | 0 | 94
39014.5484 | 1 | 0 | 94
39014.5506 | 1 | 0 | 94
39014.5527 | 2385 | 0 | 94
39014.5548 | 2150 | 0 | 94
39014.557 | 2499 | 0 | 94
39014.5591 | 2082 | 0 | 94
39014.5613 | 2336 | 0 | 94
39014.5634 | 2270 | 0 | 94
39014.5655 | 2307 | 0 | 94
39014.5677 | 2464 | 0 | 94
39014.5698 | 2390 | 0 | 94
39014.572 | 2547 | 0 | 94
39014.5741 | 2547 | 0 | 94
39014.5762 | 2083 | 0 | 94
39014.5784 | 2465 | 0 | 94
39014.5805 | 2304 | 0 | 94
94
39014.5442 | 1 | 0 | 95
39014.5463 | 1 | 0 | 95
39014.5484 | 1 | 0 | 95
39014.5506 | 1 | 0 | 95
39014.5527 | 1 | 0 | 95
39014.5549 | 1 | 0 | 95
39014.557 | 1 | 0 | 95
39014.5591 | 1 | 0 | 95
39014.5613 | 13 | 0 | 95
39014.5634 | 1743 | 0 | 95
39014.5656 | 1925 | 0 | 95
39014.5677 | 2080 | 0 | 95
39014.5698 | 2156 | 0 | 95
39014.572 | 1995 | 0 | 95
39014.5741 | 1934 | 0 | 95
39014.5762 | 2213 | 0 | 95
39014.5784 | 2063 | 0 | 95
39014.5805 | 1890 | 0 | 95
95
39014.5442 | 1 | 0 | 96
39014.5463 | 1 | 0 | 96
39014.5485 | 1 | 0 | 96
39014.5506 | 1 | 0 | 96
39014.5527 | 1 | 0 | 96
39014.5549 | 1 | 0 | 96
39014.557 | 2171 | 0 | 96
39014.5592 | 2431 | 0 | 96
39014.5613 | 2253 | 0 | 96
39014.5634 | 2310 | 0 | 96
39014.5656 | 2339 | 0 | 96
39014.5677 | 2419 | 0 | 96
39014.5698 | 2266 | 0 | 96
39014.572 | 1998 | 0 | 96
39014.5741 | 2129 | 0 | 96
39014.5763 | 2478 | 0 | 96
39014.5784 | 2080 | 0 | 96
39014.5805 | 2449 | 0 | 96
96
39014.5442 | 1 | 0 | 97
39014.5463 | 1 | 0 | 97
39014.5485 | 1 | 0 | 97
39014.5506 | 1 | 0 | 97
39014.5528 | 1 | 0 | 97
39014.5549 | 1 | 0 | 97
39014.557 | 1 | 0 | 97
39014.5592 | 1 | 0 | 97
39014.5613 | 17 | 0 | 97
39014.5634 | 1786 | 0 | 97
39014.5656 | 2310 | 0 | 97
39014.5677 | 2391 | 0 | 97
39014.5699 | 2102 | 0 | 97
39014.572 | 2022 | 0 | 97
39014.5741 | 2364 | 0 | 97
39014.5763 | 2082 | 0 | 97
39014.5784 | 1780 | 0 | 97
39014.5806 | 2136 | 0 | 97
97
39014.5442 | 1 | 0 | 98
39014.5464 | 1 | 0 | 98
39014.5485 | 1 | 0 | 98
39014.5506 | 1 | 0 | 98
39014.5528 | 1 | 0 | 98
39014.5549 | 1 | 0 | 98
39014.557 | 1912 | 0 | 98
39014.5592 | 2099 | 0 | 98
39014.5613 | 2059 | 0 | 98
39014.5635 | 2480 | 0 | 98
39014.5656 | 2592 | 0 | 98
39014.5677 | 2444 | 0 | 98
39014.5699 | 2178 | 0 | 98
39014.572 | 2138 | 0 | 98
39014.5742 | 2494 | 0 | 98
39014.5763 | 2077 | 0 | 98
39014.5784 | 2064 | 0 | 98
39014.5806 | 2476 | 0 | 98
98
39014.5442 | 1 | 0 | 99
39014.5464 | 1 | 0 | 99
39014.5485 | 1 | 0 | 99
39014.5506 | 1 | 0 | 99
39014.5528 | 1 | 0 | 99
39014.5549 | 1 | 0 | 99
39014.5571 | 1 | 0 | 99
39014.5592 | 1 | 0 | 99
39014.5613 | 22 | 0 | 99
39014.5635 | 1485 | 0 | 99
39014.5656 | 1964 | 0 | 99
39014.5678 | 2428 | 0 | 99
39014.5699 | 1978 | 0 | 99
39014.572 | 2418 | 0 | 99
39014.5742 | 1851 | 0 | 99
39014.5763 | 1953 | 0 | 99
39014.5784 | 2220 | 0 | 99
39014.5806 | 2081 | 0 | 99
99
39014.5442 | 1 | 0 | 100
39014.5464 | 1 | 0 | 100
39014.5485 | 1 | 0 | 100
39014.5507 | 1 | 0 | 100
39014.5528 | 1 | 0 | 100
39014.5549 | 1 | 0 | 100
39014.5571 | 156 | 0 | 100
39014.5592 | 2448 | 0 | 100
39014.5614 | 1966 | 0 | 100
39014.5635 | 2334 | 0 | 100
39014.5656 | 2209 | 0 | 100
39014.5678 | 2001 | 0 | 100
39014.5699 | 2554 | 0 | 100
39014.572 | 2360 | 0 | 100
39014.5742 | 2221 | 0 | 100
39014.5763 | 2067 | 0 | 100
39014.5785 | 1951 | 0 | 100
39014.5806 | 2263 | 0 | 100
100
39014.5443 | 1 | 0 | 101
39014.5464 | 1 | 0 | 101
39014.5485 | 1 | 0 | 101
39014.5507 | 1 | 0 | 101
39014.5528 | 1 | 0 | 101
39014.555 | 1 | 0 | 101
39014.5571 | 1 | 0 | 101
39014.5592 | 1 | 0 | 101
39014.5614 | 24 | 0 | 101
39014.5635 | 1655 | 0 | 101
39014.5656 | 2199 | 0 | 101
39014.5678 | 1964 | 0 | 101
39014.5699 | 2368 | 0 | 101
39014.5721 | 2074 | 0 | 101
39014.5742 | 2063 | 0 | 101
39014.5763 | 2315 | 0 | 101
39014.5785 | 2252 | 0 | 101
39014.5806 | 2107 | 0 | 101
101
39014.5443 | 1 | 0 | 102
39014.5464 | 1 | 0 | 102
39014.5486 | 1 | 0 | 102
39014.5507 | 1 | 0 | 102
39014.5528 | 1 | 0 | 102
39014.555 | 1 | 0 | 102
39014.5571 | 1 | 0 | 102
39014.5593 | 1 | 0 | 102
39014.5614 | 1 | 0 | 102
39014.5635 | 1 | 0 | 102
39014.5657 | 1 | 0 | 102
39014.5678 | 2 | 0 | 102
39014.57 | 1 | 0 | 102
39014.5721 | 2 | 0 | 102
39014.5742 | 2 | 0 | 102
39014.5764 | 2 | 0 | 102
39014.5785 | 1 | 0 | 102
39014.5806 | 2 | 0 | 102
102
39014.5443 | 1 | 0 | 103
39014.5464 | 1 | 0 | 103
39014.5486 | 1 | 0 | 103
39014.5507 | 1 | 0 | 103
39014.5529 | 1473 | 0 | 103
39014.555 | 2512 | 0 | 103
39014.5571 | 2223 | 1 | 103
39014.5593 | 2129 | 0 | 103
39014.5614 | 2175 | 0 | 103
39014.5636 | 2376 | 0 | 103
39014.5657 | 2101 | 0 | 103
39014.5678 | 2316 | 0 | 103
39014.57 | 2490 | 0 | 103
39014.5721 | 2538 | 0 | 103
39014.5742 | 2444 | 0 | 103
39014.5764 | 2390 | 0 | 103
39014.5785 | 2571 | 0 | 103
39014.5807 | 2428 | 0 | 103
103
39014.5443 | 1 | 0 | 104
39014.5465 | 1 | 0 | 104
39014.5486 | 1 | 0 | 104
39014.5507 | 1 | 0 | 104
39014.5529 | 2223 | 0 | 104
39014.555 | 2282 | 0 | 104
39014.5572 | 2022 | 1 | 104
39014.5593 | 2012 | 0 | 104
39014.5614 | 2408 | 0 | 104
39014.5636 | 2136 | 0 | 104
39014.5657 | 2101 | 0 | 104
39014.5678 | 2551 | 0 | 104
39014.57 | 2040 | 0 | 104
39014.5721 | 2265 | 0 | 104
39014.5743 | 2414 | 0 | 104
39014.5764 | 2528 | 0 | 104
39014.5785 | 2486 | 0 | 104
39014.5807 | 2112 | 0 | 104
104
39014.5443 | 1 | 0 | 105
39014.5465 | 1 | 0 | 105
39014.5486 | 1 | 0 | 105
39014.5508 | 1 | 0 | 105
39014.5529 | 2053 | 0 | 105
39014.555 | 2431 | 0 | 105
39014.5572 | 2119 | 0 | 105
39014.5593 | 2082 | 0 | 105
39014.5614 | 2133 | 0 | 105
39014.5636 | 2432 | 0 | 105
39014.5657 | 2555 | 0 | 105
39014.5679 | 2567 | 0 | 105
39014.57 | 2076 | 0 | 105
39014.5721 | 2558 | 0 | 105
39014.5743 | 2296 | 0 | 105
39014.5764 | 2050 | 0 | 105
39014.5786 | 2309 | 0 | 105
39014.5807 | 2012 | 0 | 105
105
39014.5444 | 1 | 0 | 106
39014.5465 | 1 | 0 | 106
39014.5486 | 1 | 0 | 106
39014.5508 | 1 | 0 | 106
39014.5529 | 1 | 0 | 106
39014.555 | 2 | 0 | 106
39014.5572 | 2238 | 0 | 106
39014.5593 | 2008 | 0 | 106
39014.5615 | 2499 | 0 | 106
39014.5636 | 2427 | 0 | 106
39014.5657 | 2369 | 0 | 106
39014.5679 | 2425 | 0 | 106
39014.57 | 2098 | 0 | 106
39014.5722 | 1998 | 0 | 106
39014.5743 | 2303 | 0 | 106
39014.5764 | 2553 | 0 | 106
39014.5786 | 2002 | 0 | 106
39014.5807 | 2061 | 0 | 106
106
39014.5444 | 1 | 0 | 107
39014.5465 | 1 | 0 | 107
39014.5486 | 1 | 0 | 107
39014.5508 | 1 | 0 | 107
39014.5529 | 1987 | 0 | 107
39014.5551 | 2515 | 0 | 107
39014.5572 | 2495 | 0 | 107
39014.5593 | 2311 | 0 | 107
39014.5615 | 2387 | 0 | 107
39014.5636 | 2010 | 0 | 107
39014.5658 | 2365 | 0 | 107
39014.5679 | 2217 | 0 | 107
39014.57 | 2129 | 0 | 107
39014.5722 | 2184 | 0 | 107
39014.5743 | 2167 | 0 | 107
39014.5764 | 2363 | 0 | 107
39014.5786 | 2461 | 0 | 107
39014.5807 | 2126 | 0 | 107
107
39014.5444 | 1 | 0 | 108
39014.5465 | 1 | 0 | 108
39014.5487 | 1 | 0 | 108
39014.5508 | 1 | 0 | 108
39014.5529 | 1 | 0 | 108
39014.5551 | 1 | 0 | 108
39014.5572 | 2033 | 0 | 108
39014.5594 | 1963 | 0 | 108
39014.5615 | 2306 | 0 | 108
39014.5636 | 2240 | 0 | 108
39014.5658 | 2294 | 0 | 108
39014.5679 | 2104 | 0 | 108
39014.57 | 2429 | 0 | 108
39014.5722 | 2396 | 0 | 108
39014.5743 | 2357 | 0 | 108
39014.5765 | 2301 | 0 | 108
39014.5786 | 2072 | 0 | 108
39014.5807 | 1997 | 0 | 108
108
39014.5444 | 1 | 0 | 109
39014.5465 | 1 | 0 | 109
39014.5487 | 1 | 0 | 109
39014.5508 | 1 | 0 | 109
39014.553 | 2340 | 0 | 109
39014.5551 | 2223 | 0 | 109
39014.5572 | 2357 | 0 | 109
39014.5594 | 2345 | 0 | 109
39014.5615 | 2020 | 0 | 109
39014.5636 | 2293 | 0 | 109
39014.5658 | 2069 | 0 | 109
39014.5679 | 2323 | 0 | 109
39014.5701 | 2131 | 0 | 109
39014.5722 | 2527 | 0 | 109
39014.5743 | 2412 | 0 | 109
39014.5765 | 2068 | 0 | 109
39014.5786 | 2176 | 0 | 109
39014.5808 | 2285 | 0 | 109
109
39014.5444 | 1 | 0 | 110
39014.5466 | 1 | 0 | 110
39014.5487 | 1 | 0 | 110
39014.5508 | 1 | 0 | 110
39014.553 | 1 | 0 | 110
39014.5551 | 2 | 0 | 110
39014.5572 | 176 | 0 | 110
39014.5594 | 2422 | 0 | 110
39014.5615 | 2017 | 0 | 110
39014.5637 | 2054 | 0 | 110
39014.5658 | 2580 | 0 | 110
39014.5679 | 2446 | 0 | 110
39014.5701 | 2402 | 0 | 110
39014.5722 | 2550 | 0 | 110
39014.5744 | 2019 | 0 | 110
39014.5765 | 2165 | 0 | 110
39014.5786 | 2100 | 0 | 110
39014.5808 | 1982 | 0 | 110
110
39014.5444 | 1 | 0 | 111
39014.5466 | 1 | 0 | 111
39014.5487 | 1 | 0 | 111
39014.5508 | 1 | 0 | 111
39014.553 | 2177 | 0 | 111
39014.5551 | 2197 | 0 | 111
39014.5573 | 2272 | 0 | 111
39014.5594 | 2524 | 0 | 111
39014.5615 | 2098 | 0 | 111
39014.5637 | 2138 | 0 | 111
39014.5658 | 2433 | 0 | 111
39014.568 | 2334 | 0 | 111
39014.5701 | 2592 | 0 | 111
39014.5722 | 2572 | 0 | 111
39014.5744 | 2183 | 0 | 111
39014.5765 | 2310 | 0 | 111
39014.5786 | 2109 | 0 | 111
39014.5808 | 2001 | 0 | 111
111
39014.5444 | 1 | 0 | 112
39014.5466 | 1 | 0 | 112
39014.5487 | 1 | 0 | 112
39014.5509 | 1 | 0 | 112
39014.553 | 2 | 0 | 112
39014.5551 | 1 | 0 | 112
39014.5573 | 2 | 0 | 112
39014.5594 | 1 | 0 | 112
39014.5616 | 2 | 0 | 112
39014.5637 | 2 | 0 | 112
39014.5658 | 1 | 0 | 112
39014.568 | 1 | 0 | 112
39014.5701 | 1 | 0 | 112
39014.5722 | 1 | 0 | 112
39014.5744 | 1 | 0 | 112
39014.5765 | 2 | 0 | 112
39014.5787 | 1 | 0 | 112
39014.5808 | 1 | 0 | 112
112
39014.5445 | 1 | 0 | 113
39014.5466 | 1 | 0 | 113
39014.5487 | 1 | 0 | 113
39014.5509 | 1 | 0 | 113
39014.553 | 1943 | 0 | 113
39014.5552 | 2523 | 0 | 113
39014.5573 | 2066 | 0 | 113
39014.5594 | 2031 | 0 | 113
39014.5616 | 2516 | 0 | 113
39014.5637 | 2587 | 0 | 113
39014.5658 | 2394 | 0 | 113
39014.568 | 2146 | 0 | 113
39014.5701 | 2009 | 0 | 113
39014.5723 | 2396 | 0 | 113
39014.5744 | 2576 | 0 | 113
39014.5765 | 2132 | 0 | 113
39014.5787 | 2014 | 0 | 113
39014.5808 | 2166 | 0 | 113
113
39014.5445 | 1 | 0 | 114
39014.5466 | 1 | 0 | 114
39014.5488 | 1 | 0 | 114
39014.5509 | 1 | 0 | 114
39014.553 | 1 | 0 | 114
39014.5552 | 2 | 0 | 114
39014.5573 | 2451 | 0 | 114
39014.5594 | 2157 | 0 | 114
39014.5616 | 2309 | 0 | 114
39014.5637 | 2322 | 0 | 114
39014.5659 | 2048 | 0 | 114
39014.568 | 2082 | 0 | 114
39014.5701 | 2552 | 0 | 114
39014.5723 | 2054 | 0 | 114
39014.5744 | 2005 | 0 | 114
39014.5766 | 2396 | 0 | 114
39014.5787 | 2081 | 0 | 114
39014.5808 | 2334 | 0 | 114
114
39014.5445 | 1 | 0 | 115
39014.5466 | 1 | 0 | 115
39014.5488 | 1 | 0 | 115
39014.5509 | 1 | 0 | 115
39014.553 | 2418 | 0 | 115
39014.5552 | 2389 | 0 | 115
39014.5573 | 2384 | 0 | 115
39014.5595 | 2028 | 0 | 115
39014.5616 | 2090 | 0 | 115
39014.5637 | 2130 | 0 | 115
39014.5659 | 2334 | 0 | 115
39014.568 | 2040 | 0 | 115
39014.5702 | 2176 | 0 | 115
39014.5723 | 2040 | 0 | 115
39014.5744 | 2593 | 0 | 115
39014.5766 | 2190 | 0 | 115
39014.5787 | 2323 | 0 | 115
39014.5809 | 2551 | 0 | 115
115
39014.5445 | 1 | 0 | 116
39014.5467 | 1 | 0 | 116
39014.5488 | 1 | 0 | 116
39014.5509 | 1 | 0 | 116
39014.5531 | 1 | 0 | 116
39014.5552 | 2 | 0 | 116
39014.5573 | 2407 | 0 | 116
39014.5595 | 2281 | 0 | 116
39014.5616 | 2048 | 0 | 116
39014.5638 | 2140 | 0 | 116
39014.5659 | 2037 | 0 | 116
39014.568 | 2206 | 0 | 116
39014.5702 | 2479 | 0 | 116
39014.5723 | 2092 | 0 | 116
39014.5745 | 2216 | 0 | 116
39014.5766 | 2396 | 0 | 116
39014.5787 | 2568 | 0 | 116
39014.5809 | 2459 | 0 | 116
116
39014.5445 | 1 | 0 | 117
39014.5467 | 1 | 0 | 117
39014.5488 | 1 | 0 | 117
39014.5509 | 1 | 0 | 117
39014.5531 | 2360 | 0 | 117
39014.5552 | 2132 | 0 | 117
39014.5574 | 1993 | 0 | 117
39014.5595 | 2047 | 0 | 117
39014.5616 | 2087 | 0 | 117
39014.5638 | 2125 | 0 | 117
39014.5659 | 2539 | 0 | 117
39014.5681 | 2111 | 0 | 117
39014.5702 | 2336 | 0 | 117
39014.5723 | 2118 | 0 | 117
39014.5745 | 2218 | 0 | 117
39014.5766 | 2150 | 0 | 117
39014.5788 | 2239 | 0 | 117
39014.5809 | 2388 | 0 | 117
117
39014.5445 | 1 | 0 | 118
39014.5467 | 1 | 0 | 118
39014.5488 | 1 | 0 | 118
39014.551 | 1 | 0 | 118
39014.5531 | 1 | 0 | 118
39014.5552 | 1 | 0 | 118
39014.5574 | 226 | 0 | 118
39014.5595 | 2329 | 0 | 118
39014.5617 | 2243 | 0 | 118
39014.5638 | 2006 | 0 | 118
39014.5659 | 2520 | 0 | 118
39014.5681 | 2124 | 0 | 118
39014.5702 | 1984 | 0 | 118
39014.5723 | 2234 | 0 | 118
39014.5745 | 2484 | 0 | 118
39014.5766 | 2051 | 0 | 118
39014.5788 | 2519 | 0 | 118
39014.5809 | 2479 | 0 | 118
118
39014.5446 | 1 | 0 | 119
39014.5467 | 1 | 0 | 119
39014.5488 | 1 | 0 | 119
39014.551 | 1 | 0 | 119
39014.5531 | 2017 | 0 | 119
39014.5553 | 2382 | 0 | 119
39014.5574 | 2095 | 0 | 119
39014.5595 | 2492 | 0 | 119
39014.5617 | 2396 | 0 | 119
39014.5638 | 2442 | 0 | 119
39014.5659 | 2581 | 0 | 119
39014.5681 | 2421 | 0 | 119
39014.5702 | 2024 | 0 | 119
39014.5724 | 2503 | 0 | 119
39014.5745 | 2322 | 0 | 119
39014.5766 | 2305 | 0 | 119
39014.5788 | 2294 | 0 | 119
39014.5809 | 2410 | 0 | 119
119
39014.5446 | 1 | 0 | 120
39014.5467 | 1 | 0 | 120
39014.5489 | 1 | 0 | 120
39014.551 | 1 | 0 | 120
39014.5531 | 1 | 0 | 120
39014.5553 | 1 | 0 | 120
39014.5574 | 1 | 0 | 120
39014.5595 | 2 | 0 | 120
39014.5617 | 2 | 0 | 120
39014.5638 | 2 | 0 | 120
39014.566 | 1 | 0 | 120
39014.5681 | 2 | 0 | 120
39014.5702 | 1 | 0 | 120
39014.5724 | 1 | 0 | 120
39014.5745 | 2 | 0 | 120
39014.5767 | 2 | 0 | 120
39014.5788 | 1 | 0 | 120
39014.5809 | 1 | 0 | 120
120
39014.5446 | 1 | 0 | 121
39014.5467 | 1 | 0 | 121
39014.5489 | 1 | 0 | 121
39014.551 | 1 | 0 | 121
39014.5531 | 1 | 0 | 121
39014.5553 | 1 | 0 | 121
39014.5574 | 2023 | 0 | 121
39014.5596 | 2168 | 0 | 121
39014.5617 | 2256 | 0 | 121
39014.5638 | 2265 | 0 | 121
39014.566 | 2598 | 0 | 121
39014.5681 | 2480 | 0 | 121
39014.5703 | 2497 | 0 | 121
39014.5724 | 2496 | 0 | 121
39014.5745 | 2367 | 0 | 121
39014.5767 | 2308 | 0 | 121
39014.5788 | 2494 | 0 | 121
39014.5809 | 2518 | 0 | 121
121
39014.5446 | 1 | 0 | 122
39014.5467 | 1 | 0 | 122
39014.5489 | 1 | 0 | 122
39014.551 | 1 | 0 | 122
39014.5532 | 1 | 0 | 122
39014.5553 | 1 | 0 | 122
39014.5574 | 2305 | 0 | 122
39014.5596 | 2114 | 0 | 122
39014.5617 | 2448 | 0 | 122
39014.5639 | 2007 | 0 | 122
39014.566 | 2071 | 0 | 122
39014.5681 | 2404 | 0 | 122
39014.5703 | 2155 | 0 | 122
39014.5724 | 2460 | 0 | 122
39014.5745 | 2209 | 0 | 122
39014.5767 | 2565 | 0 | 122
39014.5788 | 2257 | 0 | 122
39014.581 | 2426 | 0 | 122
122
39014.5446 | 1 | 0 | 123
39014.5468 | 1 | 0 | 123
39014.5489 | 1 | 0 | 123
39014.551 | 1 | 0 | 123
39014.5532 | 1 | 0 | 123
39014.5553 | 1 | 0 | 123
39014.5575 | 2132 | 0 | 123
39014.5596 | 2533 | 0 | 123
39014.5617 | 2545 | 0 | 123
39014.5639 | 2555 | 0 | 123
39014.566 | 2601 | 0 | 123
39014.5681 | 2560 | 0 | 123
39014.5703 | 2568 | 0 | 123
39014.5724 | 2587 | 0 | 123
39014.5746 | 2205 | 0 | 123
39014.5767 | 2270 | 0 | 123
39014.5788 | 2097 | 0 | 123
39014.581 | 2440 | 0 | 123
123
39014.5446 | 1 | 0 | 124
39014.5468 | 1 | 0 | 124
39014.5489 | 1 | 0 | 124
39014.5511 | 1 | 0 | 124
39014.5532 | 1 | 0 | 124
39014.5553 | 1 | 0 | 124
39014.5575 | 265 | 0 | 124
39014.5596 | 2000 | 0 | 124
39014.5617 | 2455 | 0 | 124
39014.5639 | 2080 | 0 | 124
39014.566 | 2178 | 0 | 124
39014.5682 | 2384 | 0 | 124
39014.5703 | 2515 | 0 | 124
39014.5724 | 2080 | 0 | 124
39014.5746 | 2554 | 0 | 124
39014.5767 | 2249 | 0 | 124
39014.5789 | 2516 | 0 | 124
39014.581 | 2461 | 0 | 124
124
39014.5447 | 1 | 0 | 125
39014.5468 | 1 | 0 | 125
39014.5489 | 1 | 0 | 125
39014.5511 | 1 | 0 | 125
39014.5532 | 1 | 0 | 125
39014.5553 | 1 | 0 | 125
39014.5575 | 2049 | 0 | 125
39014.5596 | 2017 | 0 | 125
39014.5618 | 2297 | 0 | 125
39014.5639 | 2227 | 0 | 125
39014.566 | 2110 | 0 | 125
39014.5682 | 2599 | 0 | 125
39014.5703 | 2417 | 0 | 125
39014.5725 | 2201 | 0 | 125
39014.5746 | 2009 | 0 | 125
39014.5767 | 2107 | 0 | 125
39014.5789 | 2095 | 0 | 125
39014.581 | 2446 | 0 | 125
125
39014.5447 | 1 | 0 | 126
39014.5468 | 1 | 0 | 126
39014.5489 | 1 | 0 | 126
39014.5511 | 1 | 0 | 126
39014.5532 | 1 | 0 | 126
39014.5554 | 1 | 0 | 126
39014.5575 | 2 | 0 | 126
39014.5596 | 1 | 0 | 126
39014.5618 | 2 | 0 | 126
39014.5639 | 1 | 0 | 126
39014.5661 | 2 | 0 | 126
39014.5682 | 1 | 0 | 126
39014.5703 | 2 | 0 | 126
39014.5725 | 1 | 0 | 126
39014.5746 | 2 | 0 | 126
39014.5767 | 2 | 0 | 126
39014.5789 | 2 | 0 | 126
39014.581 | 2 | 0 | 126
126
39014.5447 | 1 | 0 | 127
39014.5468 | 1 | 0 | 127
39014.549 | 1 | 0 | 127
39014.5511 | 1 | 0 | 127
39014.5532 | 1 | 0 | 127
39014.5554 | 1 | 0 | 127
39014.5575 | 2351 | 0 | 127
39014.5597 | 2400 | 0 | 127
39014.5618 | 2183 | 0 | 127
39014.5639 | 2020 | 0 | 127
39014.5661 | 2471 | 0 | 127
39014.5682 | 2315 | 0 | 127
39014.5703 | 2188 | 0 | 127
39014.5725 | 2361 | 0 | 127
39014.5746 | 2345 | 0 | 127
39014.5768 | 2523 | 0 | 127
39014.5789 | 2489 | 0 | 127
39014.581 | 2517 | 0 | 127
127
39014.5447 | 1 | 0 | 128
39014.5468 | 1 | 0 | 128
39014.549 | 1 | 0 | 128
39014.5511 | 1 | 0 | 128
39014.5533 | 1 | 0 | 128
39014.5554 | 1 | 0 | 128
39014.5575 | 293 | 0 | 128
39014.5597 | 2427 | 0 | 128
39014.5618 | 2053 | 0 | 128
39014.564 | 2424 | 0 | 128
39014.5661 | 2214 | 0 | 128
39014.5682 | 2535 | 0 | 128
39014.5704 | 2291 | 0 | 128
39014.5725 | 2387 | 0 | 128
39014.5746 | 2273 | 0 | 128
39014.5768 | 1960 | 0 | 128
39014.5789 | 2336 | 0 | 128
39014.5811 | 2425 | 0 | 128
128
39014.5447 | 1 | 0 | 129
39014.5469 | 1 | 0 | 129
39014.549 | 1 | 0 | 129
39014.5511 | 1 | 0 | 129
39014.5533 | 1 | 0 | 129
39014.5554 | 1 | 0 | 129
39014.5576 | 2258 | 0 | 129
39014.5597 | 2400 | 0 | 129
39014.5618 | 2439 | 0 | 129
39014.564 | 2338 | 0 | 129
39014.5661 | 2532 | 0 | 129
39014.5682 | 2379 | 0 | 129
39014.5704 | 2543 | 0 | 129
39014.5725 | 2362 | 0 | 129
39014.5747 | 2477 | 0 | 129
39014.5768 | 2253 | 0 | 129
39014.5789 | 2555 | 0 | 129
39014.5811 | 2181 | 0 | 129
129
39014.5447 | 1 | 0 | 130
39014.5469 | 1 | 0 | 130
39014.549 | 1 | 0 | 130
39014.5512 | 1 | 0 | 130
39014.5533 | 1 | 0 | 130
39014.5554 | 1 | 0 | 130
39014.5576 | 1 | 0 | 130
39014.5597 | 1 | 0 | 130
39014.5619 | 2 | 0 | 130
39014.564 | 2 | 0 | 130
39014.5661 | 2 | 0 | 130
39014.5683 | 2 | 0 | 130
39014.5704 | 1 | 0 | 130
39014.5725 | 1 | 0 | 130
39014.5747 | 2 | 0 | 130
39014.5768 | 2 | 0 | 130
39014.579 | 1 | 0 | 130
39014.5811 | 1 | 0 | 130
130
39014.5448 | 1 | 0 | 131
39014.5469 | 1 | 0 | 131
39014.549 | 1 | 0 | 131
39014.5512 | 1 | 0 | 131
39014.5533 | 1 | 0 | 131
39014.5555 | 1 | 0 | 131
39014.5576 | 360 | 0 | 131
39014.5597 | 2076 | 0 | 131
39014.5619 | 2376 | 0 | 131
39014.564 | 2369 | 0 | 131
39014.5661 | 2075 | 0 | 131
39014.5683 | 2387 | 0 | 131
39014.5704 | 2530 | 0 | 131
39014.5726 | 2276 | 0 | 131
39014.5747 | 2476 | 0 | 131
39014.5768 | 2532 | 0 | 131
39014.579 | 2484 | 0 | 131
39014.5811 | 2305 | 0 | 131
131
39014.5448 | 1 | 0 | 132
39014.5469 | 1 | 0 | 132
39014.5491 | 1 | 0 | 132
39014.5512 | 1 | 0 | 132
39014.5533 | 1 | 0 | 132
39014.5555 | 1 | 0 | 132
39014.5576 | 1 | 0 | 132
39014.5597 | 1 | 0 | 132
39014.5619 | 1 | 0 | 132
39014.564 | 1 | 0 | 132
39014.5662 | 2 | 0 | 132
39014.5683 | 1 | 0 | 132
39014.5704 | 1 | 0 | 132
39014.5726 | 1 | 0 | 132
39014.5747 | 1 | 0 | 132
39014.5769 | 1 | 0 | 132
39014.579 | 2 | 0 | 132
39014.5811 | 1 | 0 | 132
132

## C6-F12
Open Burn Test 2 |  |  | 2006-10-24 | 13:08 |  |  | Vs = |  | 145.5665 |  | R = | 100
XLPE | 7-C | Tray C | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 6 & 12 | Cable C | Even - | Cable F |  | Even
Time-101 | N11 | N12 | Time-102 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R12-G | R6-12
39014.5443 | 1 | 0 | 39014.5443 | 1 | 0 |  | -80.5 | 140.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238338 | 238338 | 238337.9994
39014.5464 | 1 | 0 | 39014.5464 | 1 | 0 |  | 104.5 | 325.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238338 | 238338 | 238337.9994
39014.5485 | 1 | 0 | 39014.5486 | 1 | 0 |  | 289 | 510 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238338 | 238338 | 238337.9994
39014.5507 | 1 | 0 | 39014.5507 | 1 | 0 |  | 473.5 | 694.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238338 | 238338 | 238337.9994
39014.5528 | 1 | 0 | 39014.5528 | 1 | 0 |  | 658.5 | 879.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238338 | 238338 | 238337.9994
39014.555 | 1 | 0 | 39014.555 | 1 | 0 |  | 843.5 | 1064.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238338 | 238338 | 238337.9994
39014.5571 | 1 | 0 | 39014.5571 | 1 | 0 |  | 1028 | 1249 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238338 | 238338 | 238337.9994
39014.5592 | 1 | 0 | 39014.5593 | 1 | 0 |  | 1213 | 1434 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238338 | 238338 | 238337.9994
39014.5614 | 24 | 0 | 39014.5614 | 1 | 0 |  | 1397.5 | 1618.5 | 1.4652 | 0 | 0.06105 | 0 | 0.014652 | 0 | 0.0006105 | 0 | 0.014652 | 0.0006105 | 9834.9167 | 238338 | 9834.902
39014.5635 | 1655 | 0 | 39014.5635 | 1 | 0 |  | 1582.5 | 1803.5 | 101.0379 | 0 | 0.06105 | 0 | 1.0104 | 0 | 0.0006105 | 0 | 1.0104 | 0.0006105 | 44.0713 | 238338 | 43.0609
39014.5656 | 2199 | 0 | 39014.5657 | 1 | 0 |  | 1767 | 1988 | 134.2491 | 0 | 0.06105 | 0 | 1.3425 | 0 | 0.0006105 | 0 | 1.3425 | 0.0006105 | 8.4302 | 238338 | 7.0877
39014.5678 | 1964 | 0 | 39014.5678 | 2 | 0 |  | 1952 | 2173 | 119.9023 | 0 | 0.1221 | 0 | 1.199 | 0 | 0.001221 | 0 | 1.199 | 0.001221 | 21.4043 | 119119 | 20.2053
39014.5699 | 2368 | 0 | 39014.57 | 1 | 0 |  | 2137 | 2358 | 144.5665 | 0 | 0.06105 | 0 | 1.4457 | 0 | 0.0006105 | 0 | 1.4457 | 0.0006105 | 0.69172 | 238338 | 0.75394
39014.5721 | 2074 | 0 | 39014.5721 | 2 | 0 |  | 2321.5 | 2542.5 | 126.6178 | 0 | 0.1221 | 0 | 1.2662 | 0 | 0.001221 | 0 | 1.2662 | 0.001221 | 14.9653 | 119119 | 13.6991
39014.5742 | 2063 | 0 | 39014.5742 | 2 | 0 |  | 2506.5 | 2727.5 | 125.9463 | 0 | 0.1221 | 0 | 1.2595 | 0 | 0.001221 | 0 | 1.2595 | 0.001221 | 15.5783 | 119119 | 14.3188
39014.5763 | 2315 | 0 | 39014.5764 | 2 | 0 |  | 2691 | 2912 | 141.3309 | 0 | 0.1221 | 0 | 1.4133 | 0 | 0.001221 | 0 | 1.4133 | 0.001221 | 2.997 | 119119 | 1.5837
39014.5785 | 2252 | 0 | 39014.5785 | 1 | 0 |  | 2876 | 3097 | 137.4847 | 0 | 0.06105 | 0 | 1.3748 | 0 | 0.0006105 | 0 | 1.3748 | 0.0006105 | 5.8783 | 238338 | 4.5035
39014.5806 | 2107 | 0 | 39014.5806 | 2 | 0 |  | 3060.5 | 3281.5 | 128.6325 | 0 | 0.1221 | 0 | 1.2863 | 0 | 0.001221 | 0 | 1.2863 | 0.001221 | 13.1647 | 119119 | 11.8784

## C6-F11
Open Burn Test 2 |  |  | 2006-10-24 | 13:08 |  |  | Vs = |  | 156.9219 |  | R = | 100
XLPE | 7-C | Tray C | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 6 & 11 | Cable C | Even - | Cable F |  | Odd
Time-99 | N11 | N12 | Time-100 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R11-G | R6-11
39014.5442 | 1 | 0 | 39014.5442 | 1 | 0 |  | -83.5 | 137.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
39014.5464 | 1 | 0 | 39014.5464 | 1 | 0 |  | 101.5 | 322.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
39014.5485 | 1 | 0 | 39014.5485 | 1 | 0 |  | 286.5 | 507.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
39014.5506 | 1 | 0 | 39014.5507 | 1 | 0 |  | 471 | 692 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
39014.5528 | 1 | 0 | 39014.5528 | 1 | 0 |  | 656 | 877 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
39014.5549 | 1 | 0 | 39014.5549 | 1 | 0 |  | 840.5 | 1061.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
39014.5571 | 1 | 0 | 39014.5571 | 156 | 0 |  | 1025.5 | 1246.5 | 0.06105 | 0 | 9.5238 | 0 | 0.0006105 | 0 | 0.095238 | 0 | 0.0006105 | 0.095238 | 256938 | 1547.6795 | 256937.9994
39014.5592 | 1 | 0 | 39014.5592 | 2448 | 0 |  | 1210 | 1431 | 0.06105 | 0 | 149.4505 | 0 | 0.0006105 | 0 | 1.4945 | 0 | 0.0006105 | 1.4945 | 256938 | 4.9992 | 256937.9994
39014.5613 | 22 | 0 | 39014.5614 | 1966 | 0 |  | 1395 | 1616 | 1.3431 | 0 | 120.0244 | 0 | 0.013431 | 0 | 1.2002 | 0 | 0.013431 | 1.2002 | 11583.5455 | 30.7416 | 11583.532
39014.5635 | 1485 | 0 | 39014.5635 | 2334 | 0 |  | 1579.5 | 1800.5 | 90.6593 | 0 | 142.4908 | 0 | 0.90659 | 0 | 1.4249 | 0 | 0.90659 | 1.4249 | 73.0896 | 10.1277 | 72.183
39014.5656 | 1964 | 0 | 39014.5656 | 2209 | 0 |  | 1764.5 | 1985.5 | 119.9023 | 0 | 134.8596 | 0 | 1.199 | 0 | 1.3486 | 0 | 1.199 | 1.3486 | 30.8747 | 16.3594 | 29.6757
39014.5678 | 2428 | 0 | 39014.5678 | 2001 | 0 |  | 1949 | 2170 | 148.2295 | 0 | 122.1612 | 0 | 1.4823 | 0 | 1.2216 | 0 | 1.4823 | 1.2216 | 5.8641 | 28.4548 | 4.3818
39014.5699 | 1978 | 0 | 39014.5699 | 2554 | 0 |  | 2134 | 2355 | 120.757 | 0 | 155.9219 | 0 | 1.2076 | 0 | 1.5592 | 0 | 1.2076 | 1.5592 | 29.9484 | 0.64135 | 28.7409
39014.572 | 2418 | 0 | 39014.572 | 2360 | 0 |  | 2318.5 | 2539.5 | 147.619 | 0 | 144.0781 | 0 | 1.4762 | 0 | 1.4408 | 0 | 1.4762 | 1.4408 | 6.3019 | 8.9144 | 4.8257
39014.5742 | 1851 | 0 | 39014.5742 | 2221 | 0 |  | 2503.5 | 2724.5 | 113.0037 | 0 | 135.5922 | 0 | 1.13 | 0 | 1.3559 | 0 | 1.13 | 1.3559 | 38.8644 | 15.7308 | 37.7344
39014.5763 | 1953 | 0 | 39014.5763 | 2067 | 0 |  | 2688.5 | 2909.5 | 119.2308 | 0 | 126.1905 | 0 | 1.1923 | 0 | 1.2619 | 0 | 1.1923 | 1.2619 | 31.6119 | 24.3532 | 30.4196
39014.5784 | 2220 | 0 | 39014.5785 | 1951 | 0 |  | 2873 | 3094 | 135.5311 | 0 | 119.1087 | 0 | 1.3553 | 0 | 1.1911 | 0 | 1.3553 | 1.1911 | 15.7829 | 31.7468 | 14.4276
39014.5806 | 2081 | 0 | 39014.5806 | 2263 | 0 |  | 3058 | 3279 | 127.0452 | 0 | 138.1563 | 0 | 1.2705 | 0 | 1.3816 | 0 | 1.2705 | 1.3816 | 23.5166 | 13.5829 | 22.2461

## C6-E10
Open Burn Test 2 |  |  | 2006-10-24 | 13:08 |  |  | Vs = |  | 159.2418 |  | R = | 100
XLPE | 7-C | Tray C | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 6 & 10 | Cable C | Even - | Cable E |  | Even
Time-97 | N11 | N12 | Time-98 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R10-G | R6-10
39014.5442 | 1 | 0 | 39014.5442 | 1 | 0 |  | -86 | 135 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260738 | 260738 | 260737.9994
39014.5463 | 1 | 0 | 39014.5464 | 1 | 0 |  | 98.5 | 319.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260738 | 260738 | 260737.9994
39014.5485 | 1 | 0 | 39014.5485 | 1 | 0 |  | 283.5 | 504.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260738 | 260738 | 260737.9994
39014.5506 | 1 | 0 | 39014.5506 | 1 | 0 |  | 468.5 | 689.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260738 | 260738 | 260737.9994
39014.5528 | 1 | 0 | 39014.5528 | 1 | 0 |  | 653 | 874 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260738 | 260738 | 260737.9994
39014.5549 | 1 | 0 | 39014.5549 | 1 | 0 |  | 838 | 1059 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260738 | 260738 | 260737.9994
39014.557 | 1 | 0 | 39014.557 | 1912 | 0 |  | 1022.5 | 1243.5 | 0.06105 | 0 | 116.7277 | 0 | 0.0006105 | 0 | 1.1673 | 0 | 0.0006105 | 1.1673 | 260738 | 36.4215 | 260737.9994
39014.5592 | 1 | 0 | 39014.5592 | 2099 | 0 |  | 1207.5 | 1428.5 | 0.06105 | 0 | 128.1441 | 0 | 0.0006105 | 0 | 1.2814 | 0 | 0.0006105 | 1.2814 | 260738 | 24.2677 | 260737.9994
39014.5613 | 17 | 0 | 39014.5613 | 2059 | 0 |  | 1392 | 1613 | 1.0379 | 0 | 125.7021 | 0 | 0.010379 | 0 | 1.257 | 0 | 0.010379 | 1.257 | 15243.4118 | 26.6819 | 15243.4014
39014.5634 | 1786 | 0 | 39014.5635 | 2480 | 0 |  | 1576.5 | 1797.5 | 109.0354 | 0 | 151.4042 | 0 | 1.0904 | 0 | 1.514 | 0 | 1.0904 | 1.514 | 46.0459 | 5.1766 | 44.9556
39014.5656 | 2310 | 0 | 39014.5656 | 2592 | 0 |  | 1761.5 | 1982.5 | 141.0256 | 0 | 158.2418 | 0 | 1.4103 | 0 | 1.5824 | 0 | 1.4103 | 1.5824 | 12.9169 | 0.63194 | 11.5066
39014.5677 | 2391 | 0 | 39014.5677 | 2444 | 0 |  | 1946.5 | 2167.5 | 145.9707 | 0 | 149.2063 | 0 | 1.4597 | 0 | 1.4921 | 0 | 1.4597 | 1.4921 | 9.0916 | 6.7259 | 7.6319
39014.5699 | 2102 | 0 | 39014.5699 | 2178 | 0 |  | 2131 | 2352 | 128.3272 | 0 | 132.967 | 0 | 1.2833 | 0 | 1.3297 | 0 | 1.2833 | 1.3297 | 24.0904 | 19.7603 | 22.8071
39014.572 | 2022 | 0 | 39014.572 | 2138 | 0 |  | 2316 | 2537 | 123.4432 | 0 | 130.525 | 0 | 1.2344 | 0 | 1.3053 | 0 | 1.2344 | 1.3053 | 29 | 22.0009 | 27.7656
39014.5741 | 2364 | 0 | 39014.5742 | 2494 | 0 |  | 2500.5 | 2721.5 | 144.3223 | 0 | 152.2589 | 0 | 1.4432 | 0 | 1.5226 | 0 | 1.4432 | 1.5226 | 10.3376 | 4.5862 | 8.8943
39014.5763 | 2082 | 0 | 39014.5763 | 2077 | 0 |  | 2685.5 | 2906.5 | 127.1062 | 0 | 126.801 | 0 | 1.2711 | 0 | 1.268 | 0 | 1.2711 | 1.268 | 25.2824 | 25.584 | 24.0114
39014.5784 | 1780 | 0 | 39014.5784 | 2064 | 0 |  | 2870.5 | 3091.5 | 108.6691 | 0 | 126.0073 | 0 | 1.0867 | 0 | 1.2601 | 0 | 1.0867 | 1.2601 | 46.5382 | 26.375 | 45.4515
39014.5806 | 2136 | 0 | 39014.5806 | 2476 | 0 |  | 3055 | 3276 | 130.4029 | 0 | 151.16 | 0 | 1.304 | 0 | 1.5116 | 0 | 1.304 | 1.5116 | 22.1152 | 5.3465 | 20.8111

## C6-E9
Open Burn Test 2 |  |  | 2006-10-24 | 13:08 |  |  | Vs = |  | 152.2821 |  | R = | 100
XLPE | 7-C | Tray C | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 6 & 9 | Cable C | Even - | Cable E |  | Odd
Time-95 | N11 | N12 | Time-96 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R9-G | R6-9
39014.5442 | 1 | 0 | 39014.5442 | 1 | 0 |  | -89 | 132 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249338 | 249338 | 249337.9994
39014.5463 | 1 | 0 | 39014.5463 | 1 | 0 |  | 96 | 317 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249338 | 249338 | 249337.9994
39014.5484 | 1 | 0 | 39014.5485 | 1 | 0 |  | 280.5 | 501.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249338 | 249338 | 249337.9994
39014.5506 | 1 | 0 | 39014.5506 | 1 | 0 |  | 465.5 | 686.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249338 | 249338 | 249337.9994
39014.5527 | 1 | 0 | 39014.5527 | 1 | 0 |  | 650.5 | 871.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249338 | 249338 | 249337.9994
39014.5549 | 1 | 0 | 39014.5549 | 1 | 0 |  | 835 | 1056 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249338 | 249338 | 249337.9994
39014.557 | 1 | 0 | 39014.557 | 2171 | 0 |  | 1019.5 | 1240.5 | 0.06105 | 0 | 132.5397 | 0 | 0.0006105 | 0 | 1.3254 | 0 | 0.0006105 | 1.3254 | 249338 | 14.8954 | 249337.9994
39014.5591 | 1 | 0 | 39014.5592 | 2431 | 0 |  | 1204.5 | 1425.5 | 0.06105 | 0 | 148.4127 | 0 | 0.0006105 | 0 | 1.4841 | 0 | 0.0006105 | 1.4841 | 249338 | 2.6072 | 249337.9994
39014.5613 | 13 | 0 | 39014.5613 | 2253 | 0 |  | 1389.5 | 1610.5 | 0.79365 | 0 | 137.5458 | 0 | 0.0079365 | 0 | 1.3755 | 0 | 0.0079365 | 1.3755 | 19087.5385 | 10.7137 | 19087.5305
39014.5634 | 1743 | 0 | 39014.5634 | 2310 | 0 |  | 1574 | 1795 | 106.4103 | 0 | 141.0256 | 0 | 1.0641 | 0 | 1.4103 | 0 | 1.0641 | 1.4103 | 43.1084 | 7.9818 | 42.0443
39014.5656 | 1925 | 0 | 39014.5656 | 2339 | 0 |  | 1759 | 1980 | 117.5214 | 0 | 142.7961 | 0 | 1.1752 | 0 | 1.428 | 0 | 1.1752 | 1.428 | 29.5782 | 6.643 | 28.403
39014.5677 | 2080 | 0 | 39014.5677 | 2419 | 0 |  | 1943.5 | 2164.5 | 126.9841 | 0 | 147.6801 | 0 | 1.2698 | 0 | 1.4768 | 0 | 1.2698 | 1.4768 | 19.9221 | 3.1162 | 18.6523
39014.5698 | 2156 | 0 | 39014.5698 | 2266 | 0 |  | 2128.5 | 2349.5 | 131.6239 | 0 | 138.3394 | 0 | 1.3162 | 0 | 1.3834 | 0 | 1.3162 | 1.3834 | 15.6948 | 10.0786 | 14.3786
39014.572 | 1995 | 0 | 39014.572 | 1998 | 0 |  | 2313 | 2534 | 121.7949 | 0 | 121.978 | 0 | 1.2179 | 0 | 1.2198 | 0 | 1.2179 | 1.2198 | 25.0316 | 24.8438 | 23.8136
39014.5741 | 1934 | 0 | 39014.5741 | 2129 | 0 |  | 2498 | 2719 | 118.0708 | 0 | 129.9756 | 0 | 1.1807 | 0 | 1.2998 | 0 | 1.1807 | 1.2998 | 28.9752 | 17.162 | 27.7945
39014.5762 | 2213 | 0 | 39014.5763 | 2478 | 0 |  | 2682.5 | 2903.5 | 135.1038 | 0 | 151.2821 | 0 | 1.351 | 0 | 1.5128 | 0 | 1.351 | 1.5128 | 12.7149 | 0.66102 | 11.3638
39014.5784 | 2063 | 0 | 39014.5784 | 2080 | 0 |  | 2867.5 | 3088.5 | 125.9463 | 0 | 126.9841 | 0 | 1.2595 | 0 | 1.2698 | 0 | 1.2595 | 1.2698 | 20.9103 | 19.9221 | 19.6509
39014.5805 | 1890 | 0 | 39014.5805 | 2449 | 0 |  | 3052 | 3273 | 115.3846 | 0 | 149.5116 | 0 | 1.1538 | 0 | 1.4951 | 0 | 1.1538 | 1.4951 | 31.9778 | 1.853 | 30.8239

## C5-F12
Open Burn Test 2 |  |  | 2006-10-24 | 13:08 |  |  | Vs = |  | 143.674 |  | R = | 100
XLPE | 7-C | Tray C | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 5 & 12 | Cable C | Odd - | Cable F |  | Even
Time-89 | N11 | N12 | Time-90 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R12-G | R5-12
39014.5441 | 1 | 0 | 39014.5441 | 1 | 0 |  | -97.5 | 123.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235238 | 235238 | 235237.9994
39014.5462 | 1 | 0 | 39014.5462 | 1 | 0 |  | 87.5 | 308.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235238 | 235238 | 235237.9994
39014.5484 | 1 | 0 | 39014.5484 | 1 | 0 |  | 272.5 | 493.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235238 | 235238 | 235237.9994
39014.5505 | 1 | 0 | 39014.5505 | 1 | 0 |  | 457 | 678 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235238 | 235238 | 235237.9994
39014.5526 | 1 | 0 | 39014.5527 | 1 | 0 |  | 642 | 863 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235238 | 235238 | 235237.9994
39014.5548 | 1 | 0 | 39014.5548 | 1 | 0 |  | 826.5 | 1047.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235238 | 235238 | 235237.9994
39014.5569 | 1 | 0 | 39014.5569 | 1 | 0 |  | 1011.5 | 1232.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235238 | 235238 | 235237.9994
39014.559 | 1 | 0 | 39014.5591 | 1 | 0 |  | 1196 | 1417 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235238 | 235238 | 235237.9994
39014.5612 | 5 | 0 | 39014.5612 | 1 | 0 |  | 1381 | 1602 | 0.30525 | 0 | 0.06105 | 0 | 0.0030525 | 0 | 0.0006105 | 0 | 0.0030525 | 0.0006105 | 46967.6 | 235238 | 46967.5969
39014.5633 | 1719 | 0 | 39014.5633 | 1 | 0 |  | 1565.5 | 1786.5 | 104.9451 | 0 | 0.06105 | 0 | 1.0495 | 0 | 0.0006105 | 0 | 1.0495 | 0.0006105 | 36.904 | 235238 | 35.8546
39014.5655 | 2326 | 0 | 39014.5655 | 1 | 0 |  | 1750.5 | 1971.5 | 142.0024 | 0 | 0.06105 | 0 | 1.42 | 0 | 0.0006105 | 0 | 1.42 | 0.0006105 | 1.1771 | 235238 | 0.2429
39014.5676 | 2133 | 0 | 39014.5676 | 2 | 0 |  | 1935.5 | 2156.5 | 130.2198 | 0 | 0.1221 | 0 | 1.3022 | 0 | 0.001221 | 0 | 1.3022 | 0.001221 | 10.3319 | 117569 | 9.0297
39014.5697 | 2058 | 0 | 39014.5698 | 1 | 0 |  | 2120 | 2341 | 125.641 | 0 | 0.06105 | 0 | 1.2564 | 0 | 0.0006105 | 0 | 1.2564 | 0.0006105 | 14.3528 | 235238 | 13.0964
39014.5719 | 1974 | 0 | 39014.5719 | 2 | 0 |  | 2304.5 | 2525.5 | 120.5128 | 0 | 0.1221 | 0 | 1.2051 | 0 | 0.001221 | 0 | 1.2051 | 0.001221 | 19.2188 | 117569 | 18.0137
39014.574 | 2241 | 0 | 39014.574 | 2 | 0 |  | 2489.5 | 2710.5 | 136.8132 | 0 | 0.1221 | 0 | 1.3681 | 0 | 0.001221 | 0 | 1.3681 | 0.001221 | 5.0147 | 117569 | 3.6466
39014.5762 | 2337 | 0 | 39014.5762 | 1 | 0 |  | 2674.5 | 2895.5 | 142.674 | 0 | 0.06105 | 0 | 1.4267 | 0 | 0.0006105 | 0 | 1.4267 | 0.0006105 | 0.7009 | 235238 | 0.72584
39014.5783 | 2170 | 0 | 39014.5783 | 2 | 0 |  | 2859 | 3080 | 132.4786 | 0 | 0.1221 | 0 | 1.3248 | 0 | 0.001221 | 0 | 1.3248 | 0.001221 | 8.4507 | 117569 | 7.1259
39014.5804 | 1872 | 0 | 39014.5805 | 2 | 0 |  | 3044 | 3265 | 114.2857 | 0 | 0.1221 | 0 | 1.1429 | 0 | 0.001221 | 0 | 1.1429 | 0.001221 | 25.7147 | 117569 | 24.5719

## C5-F11
Open Burn Test 2 |  |  | 2006-10-24 | 13:08 |  |  | Vs = |  | 157.8987 |  | R = | 100
XLPE | 7-C | Tray C | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 5 & 11 | Cable C | Odd - | Cable F |  | Odd
Time-87 | N11 | N12 | Time-88 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R11-G | R5-11
39014.544 | 1 | 0 | 39014.5441 | 1 | 0 |  | -100 | 121 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258538 | 258538 | 258537.9994
39014.5462 | 1 | 0 | 39014.5462 | 1 | 0 |  | 84.5 | 305.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258538 | 258538 | 258537.9994
39014.5483 | 1 | 0 | 39014.5483 | 1 | 0 |  | 269.5 | 490.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258538 | 258538 | 258537.9994
39014.5505 | 1 | 0 | 39014.5505 | 1 | 0 |  | 454.5 | 675.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258538 | 258538 | 258537.9994
39014.5526 | 1 | 0 | 39014.5526 | 1 | 0 |  | 639 | 860 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258538 | 258538 | 258537.9994
39014.5547 | 1 | 0 | 39014.5547 | 1 | 0 |  | 823.5 | 1044.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258538 | 258538 | 258537.9994
39014.5569 | 1 | 0 | 39014.5569 | 55 | 0 |  | 1008.5 | 1229.5 | 0.06105 | 0 | 3.3578 | 0 | 0.0006105 | 0 | 0.033578 | 0 | 0.0006105 | 0.033578 | 258538 | 4602.5091 | 258537.9994
39014.559 | 1 | 0 | 39014.559 | 2075 | 0 |  | 1193.5 | 1414.5 | 0.06105 | 0 | 126.6789 | 0 | 0.0006105 | 0 | 1.2668 | 0 | 0.0006105 | 1.2668 | 258538 | 24.6448 | 258537.9994
39014.5611 | 3 | 0 | 39014.5612 | 2179 | 0 |  | 1378 | 1599 | 0.18315 | 0 | 133.0281 | 0 | 0.0018315 | 0 | 1.3303 | 0 | 0.0018315 | 1.3303 | 86112.6667 | 18.6957 | 86112.6648
39014.5633 | 1388 | 0 | 39014.5633 | 2251 | 0 |  | 1563 | 1784 | 84.7375 | 0 | 137.4237 | 0 | 0.84737 | 0 | 1.3742 | 0 | 0.84737 | 1.3742 | 86.3386 | 14.8992 | 85.4912
39014.5654 | 2382 | 0 | 39014.5654 | 2087 | 0 |  | 1747.5 | 1968.5 | 145.4212 | 0 | 127.4115 | 0 | 1.4542 | 0 | 1.2741 | 0 | 1.4542 | 1.2741 | 8.5802 | 23.9281 | 7.126
39014.5676 | 2221 | 0 | 39014.5676 | 2102 | 0 |  | 1932.5 | 2153.5 | 135.5922 | 0 | 128.3272 | 0 | 1.3559 | 0 | 1.2833 | 0 | 1.3559 | 1.2833 | 16.4511 | 23.0438 | 15.0952
39014.5697 | 2157 | 0 | 39014.5697 | 1995 | 0 |  | 2117 | 2338 | 131.685 | 0 | 121.7949 | 0 | 1.3168 | 0 | 1.2179 | 0 | 1.3168 | 1.2179 | 19.9064 | 29.6431 | 18.5895
39014.5718 | 2414 | 0 | 39014.5719 | 2570 | 0 |  | 2302 | 2523 | 147.3748 | 0 | 156.8987 | 0 | 1.4737 | 0 | 1.569 | 0 | 1.4737 | 1.569 | 7.1408 | 0.63735 | 5.6671
39014.574 | 1852 | 0 | 39014.574 | 2171 | 0 |  | 2486.5 | 2707.5 | 113.0647 | 0 | 132.5397 | 0 | 1.1306 | 0 | 1.3254 | 0 | 1.1306 | 1.3254 | 39.6533 | 19.1331 | 38.5227
39014.5761 | 2337 | 0 | 39014.5761 | 2154 | 0 |  | 2671.5 | 2892.5 | 142.674 | 0 | 131.5018 | 0 | 1.4267 | 0 | 1.315 | 0 | 1.4267 | 1.315 | 10.6709 | 20.0734 | 9.2442
39014.5783 | 2272 | 0 | 39014.5783 | 2117 | 0 |  | 2856.5 | 3077.5 | 138.7057 | 0 | 129.243 | 0 | 1.3871 | 0 | 1.2924 | 0 | 1.3871 | 1.2924 | 13.8371 | 22.1719 | 12.4501
39014.5804 | 1843 | 0 | 39014.5804 | 2034 | 0 |  | 3041 | 3262 | 112.5153 | 0 | 124.1758 | 0 | 1.1252 | 0 | 1.2418 | 0 | 1.1252 | 1.2418 | 40.3353 | 27.1573 | 39.2102

## C5-E10
Open Burn Test 2 |  |  | 2006-10-24 | 13:08 |  |  | Vs = |  | 158.6923 |  | R = | 100
XLPE | 7-C | Tray C | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 5 & 10 | Cable C | Odd - | Cable E |  | Even
Time-85 | N11 | N12 | Time-86 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R10-G | R5-10
39014.544 | 1 | 0 | 39014.544 | 1 | 0 |  | -103 | 118 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259838 | 259838 | 259837.9994
39014.5461 | 1 | 0 | 39014.5462 | 1 | 0 |  | 81.5 | 302.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259838 | 259838 | 259837.9994
39014.5483 | 1 | 0 | 39014.5483 | 1 | 0 |  | 266.5 | 487.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259838 | 259838 | 259837.9994
39014.5504 | 1 | 0 | 39014.5504 | 1 | 0 |  | 451.5 | 672.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259838 | 259838 | 259837.9994
39014.5526 | 1 | 0 | 39014.5526 | 1 | 0 |  | 636 | 857 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259838 | 259838 | 259837.9994
39014.5547 | 1 | 0 | 39014.5547 | 1 | 0 |  | 821 | 1042 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259838 | 259838 | 259837.9994
39014.5568 | 1 | 0 | 39014.5569 | 1945 | 0 |  | 1005.5 | 1226.5 | 0.06105 | 0 | 118.7424 | 0 | 0.0006105 | 0 | 1.1874 | 0 | 0.0006105 | 1.1874 | 259838 | 33.6442 | 259837.9994
39014.559 | 1 | 0 | 39014.559 | 2498 | 0 |  | 1190.5 | 1411.5 | 0.06105 | 0 | 152.5031 | 0 | 0.0006105 | 0 | 1.525 | 0 | 0.0006105 | 1.525 | 259838 | 4.0584 | 259837.9994
39014.5611 | 3 | 0 | 39014.5611 | 2539 | 0 |  | 1375.5 | 1596.5 | 0.18315 | 0 | 155.0061 | 0 | 0.0018315 | 0 | 1.5501 | 0 | 0.0018315 | 1.5501 | 86546 | 2.3781 | 86545.9982
39014.5633 | 1599 | 0 | 39014.5633 | 2222 | 0 |  | 1560 | 1781 | 97.619 | 0 | 135.6532 | 0 | 0.97619 | 0 | 1.3565 | 0 | 0.97619 | 1.3565 | 62.5629 | 16.9838 | 61.5867
39014.5654 | 2273 | 0 | 39014.5654 | 2434 | 0 |  | 1744.5 | 1965.5 | 138.7668 | 0 | 148.5958 | 0 | 1.3877 | 0 | 1.486 | 0 | 1.3877 | 1.486 | 14.359 | 6.7946 | 12.9713
39014.5675 | 2366 | 0 | 39014.5675 | 2013 | 0 |  | 1929.5 | 2150.5 | 144.4444 | 0 | 122.8938 | 0 | 1.4444 | 0 | 1.2289 | 0 | 1.4444 | 1.2289 | 9.8639 | 29.1297 | 8.4195
39014.5697 | 2189 | 0 | 39014.5697 | 2583 | 0 |  | 2114.5 | 2335.5 | 133.6386 | 0 | 157.6923 | 0 | 1.3364 | 0 | 1.5769 | 0 | 1.3364 | 1.5769 | 18.7474 | 0.63415 | 17.411
39014.5718 | 2094 | 0 | 39014.5718 | 2167 | 0 |  | 2299 | 2520 | 127.8388 | 0 | 132.2955 | 0 | 1.2784 | 0 | 1.323 | 0 | 1.2784 | 1.323 | 24.1347 | 19.9529 | 22.8563
39014.5739 | 2055 | 0 | 39014.574 | 2498 | 0 |  | 2484 | 2705 | 125.4579 | 0 | 152.5031 | 0 | 1.2546 | 0 | 1.525 | 0 | 1.2546 | 1.525 | 26.4905 | 4.0584 | 25.2359
39014.5761 | 2190 | 0 | 39014.5761 | 2542 | 0 |  | 2668.5 | 2889.5 | 133.6996 | 0 | 155.1893 | 0 | 1.337 | 0 | 1.5519 | 0 | 1.337 | 1.5519 | 18.6932 | 2.2573 | 17.3562
39014.5782 | 1881 | 0 | 39014.5782 | 2123 | 0 |  | 2853.5 | 3074.5 | 114.8352 | 0 | 129.6093 | 0 | 1.1484 | 0 | 1.2961 | 0 | 1.1484 | 1.2961 | 38.1914 | 22.439 | 37.043
39014.5804 | 2067 | 0 | 39014.5804 | 2132 | 0 |  | 3038.5 | 3259.5 | 126.1905 | 0 | 130.1587 | 0 | 1.2619 | 0 | 1.3016 | 0 | 1.2619 | 1.3016 | 25.7562 | 21.9221 | 24.4943

## C5-E9
Open Burn Test 2 |  |  | 2006-10-24 | 13:08 |  |  | Vs = |  | 158.3871 |  | R = | 100
XLPE | 7-C | Tray C | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 5 & 9 | Cable C | Odd - | Cable E |  | Odd
Time-83 | N11 | N12 | Time-84 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R9-G | R5-9
39014.544 | 1 | 0 | 39014.544 | 1 | 0 |  | -105.5 | 115.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259338 | 259338 | 259337.9994
39014.5461 | 1 | 0 | 39014.5461 | 1 | 0 |  | 79 | 300 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259338 | 259338 | 259337.9994
39014.5483 | 1 | 0 | 39014.5483 | 1 | 0 |  | 264 | 485 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259338 | 259338 | 259337.9994
39014.5504 | 1 | 0 | 39014.5504 | 1 | 0 |  | 448.5 | 669.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259338 | 259338 | 259337.9994
39014.5525 | 1 | 0 | 39014.5525 | 1 | 0 |  | 633.5 | 854.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259338 | 259338 | 259337.9994
39014.5547 | 1 | 0 | 39014.5547 | 1 | 0 |  | 818 | 1039 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259338 | 259338 | 259337.9994
39014.5568 | 1 | 0 | 39014.5568 | 11 | 0 |  | 1003 | 1224 | 0.06105 | 0 | 0.67155 | 0 | 0.0006105 | 0 | 0.0067155 | 0 | 0.0006105 | 0.0067155 | 259338 | 23485.2727 | 259337.9994
39014.5589 | 1 | 0 | 39014.559 | 2015 | 0 |  | 1187.5 | 1408.5 | 0.06105 | 0 | 123.0159 | 0 | 0.0006105 | 0 | 1.2302 | 0 | 0.0006105 | 1.2302 | 259338 | 28.7533 | 259337.9994
39014.5611 | 2 | 0 | 39014.5611 | 2237 | 0 |  | 1372.5 | 1593.5 | 0.1221 | 0 | 136.569 | 0 | 0.001221 | 0 | 1.3657 | 0 | 0.001221 | 1.3657 | 129619 | 15.9759 | 129618.9988
39014.5632 | 1240 | 0 | 39014.5632 | 2133 | 0 |  | 1557.5 | 1778.5 | 75.7021 | 0 | 130.2198 | 0 | 0.75702 | 0 | 1.3022 | 0 | 0.75702 | 1.3022 | 109.2242 | 21.6306 | 108.4672
39014.5654 | 1983 | 0 | 39014.5654 | 2504 | 0 |  | 1742 | 1963 | 121.0623 | 0 | 152.8694 | 0 | 1.2106 | 0 | 1.5287 | 0 | 1.2106 | 1.5287 | 30.8311 | 3.6094 | 29.6204
39014.5675 | 1938 | 0 | 39014.5675 | 2026 | 0 |  | 1926.5 | 2147.5 | 118.315 | 0 | 123.6874 | 0 | 1.1832 | 0 | 1.2369 | 0 | 1.1832 | 1.2369 | 33.8689 | 28.0543 | 32.6858
39014.5696 | 2247 | 0 | 39014.5697 | 2578 | 0 |  | 2111.5 | 2332.5 | 137.1795 | 0 | 157.3871 | 0 | 1.3718 | 0 | 1.5739 | 0 | 1.3718 | 1.5739 | 15.4597 | 0.63538 | 14.0879
39014.5718 | 2354 | 0 | 39014.5718 | 2055 | 0 |  | 2296.5 | 2517.5 | 143.7118 | 0 | 125.4579 | 0 | 1.4371 | 0 | 1.2546 | 0 | 1.4371 | 1.2546 | 10.2116 | 26.2472 | 8.7744
39014.5739 | 2389 | 0 | 39014.5739 | 2003 | 0 |  | 2481 | 2702 | 145.8486 | 0 | 122.2833 | 0 | 1.4585 | 0 | 1.2228 | 0 | 1.4585 | 1.2228 | 8.5969 | 29.5247 | 7.1384
39014.5761 | 2174 | 0 | 39014.5761 | 2302 | 0 |  | 2666 | 2887 | 132.7228 | 0 | 140.5372 | 0 | 1.3272 | 0 | 1.4054 | 0 | 1.3272 | 1.4054 | 19.3367 | 12.7011 | 18.0095
39014.5782 | 2114 | 0 | 39014.5782 | 2525 | 0 |  | 2850.5 | 3071.5 | 129.0598 | 0 | 154.1514 | 0 | 1.2906 | 0 | 1.5415 | 0 | 1.2906 | 1.5415 | 22.7237 | 2.7477 | 21.4331
39014.5803 | 2031 | 0 | 39014.5803 | 2506 | 0 |  | 3035.5 | 3256.5 | 123.9927 | 0 | 152.9915 | 0 | 1.2399 | 0 | 1.5299 | 0 | 1.2399 | 1.5299 | 27.739 | 3.5267 | 26.4991

## C5-C6
Open Burn Test 2 |  |  | 2006-10-24 | 13:08 |  |  | Vs = |  | 146.4823 |  | R = | 100
XLPE | 7-C | Tray C | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 5 & 6 | Cable C | Odd-Even
Time-77 | N11 | N12 | Time-78 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R6-G | R5-6
39014.5439 | 1 | 0 | 39014.5439 | 1 | 0 |  | -114 | 107 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239838 | 239838 | 239837.9994
39014.546 | 1 | 0 | 39014.546 | 1 | 0 |  | 70.5 | 291.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239838 | 239838 | 239837.9994
39014.5482 | 1 | 0 | 39014.5482 | 1 | 0 |  | 255.5 | 476.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239838 | 239838 | 239837.9994
39014.5503 | 1 | 0 | 39014.5503 | 1 | 0 |  | 440 | 661 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239838 | 239838 | 239837.9994
39014.5524 | 1 | 0 | 39014.5525 | 1 | 0 |  | 625 | 846 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239838 | 239838 | 239837.9994
39014.5546 | 1 | 0 | 39014.5546 | 1 | 0 |  | 809.5 | 1030.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239838 | 239838 | 239837.9994
39014.5567 | 1 | 0 | 39014.5567 | 1 | 0 |  | 994.5 | 1215.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239838 | 239838 | 239837.9994
39014.5589 | 1 | 0 | 39014.5589 | 1 | 0 |  | 1179.5 | 1400.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239838 | 239838 | 239837.9994
39014.561 | 592 | 530 | 39014.561 | 570 | 513 |  | 1364 | 1585 | 36.1416 | 32.3565 | 34.7985 | 31.3187 | 0.36142 | 0.32357 | 0.34799 | 0.31319 | 0.037851 | 0.034799 | 3646.7227 | 4261.0536 | 235.4886
39014.5631 | 1820 | 492 | 39014.5631 | 1934 | 484 |  | 1549 | 1770 | 111.1111 | 30.0366 | 118.0708 | 29.5482 | 1.1111 | 0.30037 | 1.1807 | 0.29548 | 0.81074 | 0.88523 | 33.0315 | 115.4861 | 9.5183
39014.5653 | 1939 | 54 | 39014.5653 | 2095 | 57 |  | 1733.5 | 1954.5 | 118.3761 | 3.2967 | 127.8999 | 3.4799 | 1.1838 | 0.032967 | 1.279 | 0.034799 | 1.1508 | 1.2442 | 29.556 | 16.4963 | 106.5644
39014.5674 | 2383 | 15 | 39014.5674 | 1951 | 12 |  | 1918.5 | 2139.5 | 145.4823 | 0.91575 | 119.1087 | 0.7326 | 1.4548 | 0.0091575 | 1.1911 | 0.007326 | 1.4457 | 1.1838 | 0.69377 | 214.1958 | 6.2719
39014.5695 | 2191 | 17 | 39014.5696 | 1973 | 15 |  | 2103 | 2324 | 133.7607 | 1.0379 | 120.4518 | 0.91575 | 1.3376 | 0.010379 | 1.2045 | 0.0091575 | 1.3272 | 1.1954 | 9.9136 | 23.6 | 214.9521
39014.5717 | 2231 | 20 | 39014.5717 | 1999 | 19 |  | 2288 | 2509 | 136.2027 | 1.221 | 122.0391 | 1.16 | 1.362 | 0.01221 | 1.2204 | 0.0116 | 1.3498 | 1.2088 | 7.9272 | 23.0061 | 138.7592
39014.5738 | 1998 | 31 | 39014.5738 | 2332 | 36 |  | 2472.5 | 2693.5 | 121.978 | 1.8926 | 142.3687 | 2.1978 | 1.2198 | 0.018926 | 1.4237 | 0.021978 | 1.2009 | 1.4017 | 42.2568 | 3.0478 | 35.3368
39014.576 | 2357 | 63 | 39014.576 | 2187 | 77 |  | 2657.5 | 2878.5 | 143.895 | 3.8462 | 133.5165 | 4.7009 | 1.4389 | 0.038462 | 1.3352 | 0.047009 | 1.4005 | 1.2882 | 1.1713 | 4.7579 | 1.4865
39014.5781 | 2263 | 118 | 39014.5781 | 2177 | 120 |  | 2842.5 | 3063.5 | 138.1563 | 7.2039 | 132.906 | 7.326 | 1.3816 | 0.072039 | 1.3291 | 0.07326 | 1.3095 | 1.2558 | 6.9012 | 69.8903 | 6.4078
39014.5802 | 2088 | 181 | 39014.5803 | 1864 | 161 |  | 3027 | 3248 | 127.4725 | 11.0501 | 113.7973 | 9.8291 | 1.2747 | 0.1105 | 1.138 | 0.098291 | 1.1642 | 1.0397 | 19.3013 | 61.6187 | 27.4633

## B4-E10
Open Burn Test 2 |  |  | 2006-10-24 | 13:08 |  |  | Vs = |  | 157.1661 |  | R = | 100
XLPE | 7-C | Tray C | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 4 & 10 | Cable B | Even - | Cable E |  | Even
Time-71 | N11 | N12 | Time-72 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R10-G | R4-10
39014.5438 | 1 | 0 | 39014.5438 | 1 | 0 |  | -122.5 | 98.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257338 | 257338 | 257337.9994
39014.5459 | 1 | 0 | 39014.5459 | 1 | 0 |  | 62.5 | 283.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257338 | 257338 | 257337.9994
39014.5481 | 1 | 0 | 39014.5481 | 1 | 0 |  | 247 | 468 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257338 | 257338 | 257337.9994
39014.5502 | 1 | 0 | 39014.5502 | 1 | 0 |  | 431.5 | 652.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257338 | 257338 | 257337.9994
39014.5523 | 1 | 0 | 39014.5523 | 1 | 0 |  | 616.5 | 837.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257338 | 257338 | 257337.9994
39014.5545 | 1 | 0 | 39014.5545 | 1 | 0 |  | 801.5 | 1022.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257338 | 257338 | 257337.9994
39014.5566 | 1 | 0 | 39014.5566 | 1817 | 0 |  | 986 | 1207 | 0.06105 | 0 | 110.928 | 0 | 0.0006105 | 0 | 1.1093 | 0 | 0.0006105 | 1.1093 | 257338 | 41.683 | 257337.9994
39014.5587 | 30 | 0 | 39014.5588 | 2433 | 0 |  | 1171 | 1392 | 1.8315 | 0 | 148.5348 | 0 | 0.018315 | 0 | 1.4853 | 0 | 0.018315 | 1.4853 | 8481.2667 | 5.8109 | 8481.2484
39014.5609 | 1754 | 0 | 39014.5609 | 2426 | 0 |  | 1355.5 | 1576.5 | 107.0818 | 0 | 148.1074 | 0 | 1.0708 | 0 | 1.4811 | 0 | 1.0708 | 1.4811 | 46.7719 | 6.1162 | 45.7011
39014.563 | 2381 | 0 | 39014.563 | 2232 | 0 |  | 1540.5 | 1761.5 | 145.3602 | 0 | 136.2637 | 0 | 1.4536 | 0 | 1.3626 | 0 | 1.4536 | 1.3626 | 8.1218 | 15.3396 | 6.6682
39014.5652 | 2325 | 0 | 39014.5652 | 2249 | 0 |  | 1725 | 1946 | 141.9414 | 0 | 137.3016 | 0 | 1.4194 | 0 | 1.373 | 0 | 1.4194 | 1.373 | 10.726 | 14.4678 | 9.3066
39014.5673 | 2558 | 0 | 39014.5673 | 2472 | 0 |  | 1910 | 2131 | 156.1661 | 0 | 150.9158 | 0 | 1.5617 | 0 | 1.5092 | 0 | 1.5617 | 1.5092 | 0.64034 | 4.1416 | 0.92132
39014.5694 | 2373 | 0 | 39014.5695 | 2484 | 0 |  | 2094.5 | 2315.5 | 144.8718 | 0 | 151.6484 | 0 | 1.4487 | 0 | 1.5165 | 0 | 1.4487 | 1.5165 | 8.4863 | 3.6385 | 7.0376
39014.5716 | 1988 | 0 | 39014.5716 | 2216 | 0 |  | 2279.5 | 2500.5 | 121.3675 | 0 | 135.2869 | 0 | 1.2137 | 0 | 1.3529 | 0 | 1.2137 | 1.3529 | 29.496 | 16.1724 | 28.2823
39014.5737 | 2483 | 0 | 39014.5737 | 2494 | 0 |  | 2464.5 | 2685.5 | 151.5873 | 0 | 152.2589 | 0 | 1.5159 | 0 | 1.5226 | 0 | 1.5159 | 1.5226 | 3.6802 | 3.2229 | 2.1644
39014.5759 | 2300 | 0 | 39014.5759 | 2134 | 0 |  | 2649 | 2870 | 140.4151 | 0 | 130.2808 | 0 | 1.4042 | 0 | 1.3028 | 0 | 1.4042 | 1.3028 | 11.9296 | 20.6364 | 10.5254
39014.578 | 2386 | 0 | 39014.578 | 2034 | 0 |  | 2834 | 3055 | 145.6654 | 0 | 124.1758 | 0 | 1.4567 | 0 | 1.2418 | 0 | 1.4567 | 1.2418 | 7.8952 | 26.5674 | 6.4386
39014.5801 | 2258 | 0 | 39014.5802 | 2431 | 0 |  | 3018.5 | 3239.5 | 137.851 | 0 | 148.4127 | 0 | 1.3785 | 0 | 1.4841 | 0 | 1.3785 | 1.4841 | 14.0115 | 5.898 | 12.633

## B4-E9
Open Burn Test 2 |  |  | 2006-10-24 | 13:08 |  |  | Vs = |  | 156.2503 |  | R = | 100
XLPE | 7-C | Tray C | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 4 & 9 | Cable B | Even - | Cable E |  | Odd
Time-69 | N11 | N12 | Time-70 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R9-G | R4-9
39014.5437 | 1 | 0 | 39014.5438 | 1 | 0 |  | -125.5 | 95.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
39014.5459 | 1 | 0 | 39014.5459 | 1 | 0 |  | 59.5 | 280.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
39014.548 | 1 | 0 | 39014.548 | 1 | 0 |  | 244.5 | 465.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
39014.5502 | 1 | 0 | 39014.5502 | 1 | 0 |  | 429 | 650 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
39014.5523 | 1 | 0 | 39014.5523 | 1 | 0 |  | 614 | 835 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
39014.5544 | 1 | 0 | 39014.5545 | 1 | 0 |  | 798.5 | 1019.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
39014.5566 | 1 | 0 | 39014.5566 | 4 | 0 |  | 983.5 | 1204.5 | 0.06105 | 0 | 0.2442 | 0 | 0.0006105 | 0 | 0.002442 | 0 | 0.0006105 | 0.002442 | 255838 | 63884.5 | 255837.9994
39014.5587 | 21 | 0 | 39014.5587 | 2129 | 0 |  | 1168 | 1389 | 1.2821 | 0 | 129.9756 | 0 | 0.012821 | 0 | 1.2998 | 0 | 0.012821 | 1.2998 | 12087.5238 | 20.2151 | 12087.511
39014.5609 | 1608 | 0 | 39014.5609 | 2543 | 0 |  | 1353 | 1574 | 98.1685 | 0 | 155.2503 | 0 | 0.98168 | 0 | 1.5525 | 0 | 0.98168 | 1.5525 | 59.1654 | 0.64412 | 58.1837
39014.563 | 1895 | 0 | 39014.563 | 2528 | 0 |  | 1537.5 | 1758.5 | 115.6899 | 0 | 154.3346 | 0 | 1.1569 | 0 | 1.5433 | 0 | 1.1569 | 1.5433 | 35.0596 | 1.2413 | 33.9027
39014.5651 | 2056 | 0 |  | 2524 | 0 |  | 1722 | 1943 | 125.5189 | 0 | 154.0904 | 0 | 1.2552 | 0 | 1.5409 | 0 | 1.2552 | 1.5409 | 24.4835 | 1.4017 | 23.2283
39014.5673 | 2234 | 0 | 39014.5673 | 2520 | 0 |  | 1907 | 2128 | 136.3858 | 0 | 153.8462 | 0 | 1.3639 | 0 | 1.5385 | 0 | 1.3639 | 1.5385 | 14.5649 | 1.5627 | 13.201
39014.5694 | 2531 | 0 | 39014.5694 | 2114 | 0 |  | 2092 | 2313 | 154.5177 | 0 | 129.0598 | 0 | 1.5452 | 0 | 1.2906 | 0 | 1.5452 | 1.2906 | 1.1213 | 21.0681 | 0.42388
39014.5716 | 2366 | 0 | 39014.5716 | 2249 | 0 |  | 2276.5 | 2497.5 | 144.4444 | 0 | 137.3016 | 0 | 1.4444 | 0 | 1.373 | 0 | 1.4444 | 1.373 | 8.1733 | 13.8008 | 6.7288
39014.5737 | 2023 | 0 | 39014.5737 | 2350 | 0 |  | 2461.5 | 2682.5 | 123.5043 | 0 | 143.4676 | 0 | 1.235 | 0 | 1.4347 | 0 | 1.235 | 1.4347 | 26.5141 | 8.9098 | 25.279
39014.5758 | 2423 | 0 | 39014.5758 | 2004 | 0 |  | 2646.5 | 2867.5 | 147.9243 | 0 | 122.3443 | 0 | 1.4792 | 0 | 1.2234 | 0 | 1.4792 | 1.2234 | 5.6286 | 27.7136 | 4.1493
39014.578 | 2041 | 0 | 39014.578 | 2445 | 0 |  | 2831 | 3052 | 124.6032 | 0 | 149.2674 | 0 | 1.246 | 0 | 1.4927 | 0 | 1.246 | 1.4927 | 25.3983 | 4.6781 | 24.1523
39014.5801 | 1907 | 0 | 39014.5801 | 2078 | 0 |  | 3016 | 3237 | 116.4225 | 0 | 126.862 | 0 | 1.1642 | 0 | 1.2686 | 0 | 1.1642 | 1.2686 | 34.2098 | 23.1655 | 33.0455

## B4-D8
Open Burn Test 2 |  |  | 2006-10-24 | 13:08 |  |  | Vs = |  | 158.0818 |  | R = | 100
XLPE | 7-C | Tray C | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 4 & 8 | Cable B | Even - | Cable D |  | Even
Time-67 | N11 | N12 | Time-68 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R8-G | R4-8
39014.5437 | 1 | 0 | 39014.5437 | 1 | 0 |  | -128 | 93 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258838 | 258838 | 258837.9994
39014.5459 | 1 | 0 | 39014.5459 | 1 | 0 |  | 56.5 | 277.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258838 | 258838 | 258837.9994
39014.548 | 1 | 0 | 39014.548 | 1 | 0 |  | 241.5 | 462.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258838 | 258838 | 258837.9994
39014.5501 | 1 | 0 | 39014.5502 | 1 | 0 |  | 426.5 | 647.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258838 | 258838 | 258837.9994
39014.5523 | 1 | 0 | 39014.5523 | 17 | 0 |  | 611 | 832 | 0.06105 | 0 | 1.0379 | 0 | 0.0006105 | 0 | 0.010379 | 0 | 0.0006105 | 0.010379 | 258838 | 15131.6471 | 258837.9994
39014.5544 | 1 | 0 | 39014.5544 | 1955 | 0 |  | 795.5 | 1016.5 | 0.06105 | 0 | 119.3529 | 0 | 0.0006105 | 0 | 1.1935 | 0 | 0.0006105 | 1.1935 | 258838 | 32.4491 | 258837.9994
39014.5566 | 2 | 0 | 39014.5566 | 2005 | 0 |  | 980.5 | 1201.5 | 0.1221 | 0 | 122.4054 | 0 | 0.001221 | 0 | 1.2241 | 0 | 0.001221 | 1.2241 | 129369 | 29.1461 | 129368.9988
39014.5587 | 18 | 0 | 39014.5587 | 1968 | 0 |  | 1165.5 | 1386.5 | 1.0989 | 0 | 120.1465 | 0 | 0.010989 | 0 | 1.2015 | 0 | 0.010989 | 1.2015 | 14285.4444 | 31.5742 | 14285.4335
39014.5608 | 1596 | 0 | 39014.5608 | 2362 | 0 |  | 1350 | 1571 | 97.4359 | 0 | 144.2002 | 0 | 0.97436 | 0 | 1.442 | 0 | 0.97436 | 1.442 | 62.2419 | 9.6266 | 61.2675
39014.563 | 2418 | 0 | 39014.563 | 2573 | 0 |  | 1535 | 1756 | 147.619 | 0 | 157.0818 | 0 | 1.4762 | 0 | 1.5708 | 0 | 1.4762 | 1.5708 | 7.0877 | 0.63661 | 5.6115
39014.5651 | 2113 | 0 | 39014.5651 | 2224 | 0 |  | 1719.5 | 1940.5 | 128.9988 | 0 | 135.7753 | 0 | 1.29 | 0 | 1.3578 | 0 | 1.29 | 1.3578 | 22.5452 | 16.429 | 21.2552
39014.5672 | 2278 | 0 | 39014.5673 | 2532 | 0 |  | 1904.5 | 2125.5 | 139.072 | 0 | 154.5788 | 0 | 1.3907 | 0 | 1.5458 | 0 | 1.3907 | 1.5458 | 13.669 | 2.2662 | 12.2783
39014.5694 | 2144 | 0 | 39014.5694 | 2498 | 0 |  | 2089 | 2310 | 130.8913 | 0 | 152.5031 | 0 | 1.3089 | 0 | 1.525 | 0 | 1.3089 | 1.525 | 20.7733 | 3.6581 | 19.4644
39014.5715 | 2171 | 0 | 39014.5715 | 2470 | 0 |  | 2274 | 2495 | 132.5397 | 0 | 150.7937 | 0 | 1.3254 | 0 | 1.5079 | 0 | 1.3254 | 1.5079 | 19.2713 | 4.8332 | 17.9459
39014.5737 | 2426 | 0 | 39014.5737 | 2389 | 0 |  | 2458.5 | 2679.5 | 148.1074 | 0 | 145.8486 | 0 | 1.4811 | 0 | 1.4585 | 0 | 1.4811 | 1.4585 | 6.7345 | 8.3876 | 5.2535
39014.5758 | 2486 | 0 | 39014.5758 | 2187 | 0 |  | 2643.5 | 2864.5 | 151.7705 | 0 | 133.5165 | 0 | 1.5177 | 0 | 1.3352 | 0 | 1.5177 | 1.3352 | 4.1585 | 18.3987 | 2.6408
39014.5779 | 2433 | 0 | 39014.578 | 2199 | 0 |  | 2828.5 | 3049.5 | 148.5348 | 0 | 134.2491 | 0 | 1.4853 | 0 | 1.3425 | 0 | 1.4853 | 1.3425 | 6.4275 | 17.7526 | 4.9421
39014.5801 | 2138 | 0 | 39014.5801 | 2515 | 0 |  | 3013 | 3234 | 130.525 | 0 | 153.5409 | 0 | 1.3053 | 0 | 1.5354 | 0 | 1.3053 | 1.5354 | 21.1123 | 2.9575 | 19.807

## B4-D7
Open Burn Test 2 |  |  | 2006-10-24 | 13:08 |  |  | Vs = |  | 154.602 |  | R = | 100
XLPE | 7-C | Tray C | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 4 & 7 | Cable B | Even - | Cable D |  | Odd
Time-65 | N11 | N12 | Time-66 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R7-G | R4-7
39014.5437 | 1 | 0 | 39014.5437 | 1 | 0 |  | -131 | 90 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253138 | 253138 | 253137.9994
39014.5458 | 1 | 0 | 39014.5458 | 1 | 0 |  | 54 | 275 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253138 | 253138 | 253137.9994
39014.548 | 1 | 0 | 39014.548 | 1 | 0 |  | 238.5 | 459.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253138 | 253138 | 253137.9994
39014.5501 | 1 | 0 | 39014.5501 | 1 | 0 |  | 423.5 | 644.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253138 | 253138 | 253137.9994
39014.5522 | 1 | 0 | 39014.5523 | 25 | 0 |  | 608.5 | 829.5 | 0.06105 | 0 | 1.5263 | 0 | 0.0006105 | 0 | 0.015263 | 0 | 0.0006105 | 0.015263 | 253138 | 10029.52 | 253137.9994
39014.5544 | 1 | 0 | 39014.5544 | 2265 | 0 |  | 793 | 1014 | 0.06105 | 0 | 138.2784 | 0 | 0.0006105 | 0 | 1.3828 | 0 | 0.0006105 | 1.3828 | 253138 | 11.8049 | 253137.9994
39014.5565 | 1 | 0 | 39014.5565 | 2026 | 0 |  | 977.5 | 1198.5 | 0.06105 | 0 | 123.6874 | 0 | 0.0006105 | 0 | 1.2369 | 0 | 0.0006105 | 1.2369 | 253138 | 24.9941 | 253137.9994
39014.5587 | 16 | 0 | 39014.5587 | 2260 | 0 |  | 1162.5 | 1383.5 | 0.9768 | 0 | 137.9731 | 0 | 0.009768 | 0 | 1.3797 | 0 | 0.009768 | 1.3797 | 15727.375 | 12.0522 | 15727.3652
39014.5608 | 1645 | 0 | 39014.5608 | 2179 | 0 |  | 1347.5 | 1568.5 | 100.4274 | 0 | 133.0281 | 0 | 1.0043 | 0 | 1.3303 | 0 | 1.0043 | 1.3303 | 53.9441 | 16.2175 | 52.9398
39014.5629 | 2373 | 0 | 39014.563 | 2415 | 0 |  | 1532 | 1753 | 144.8718 | 0 | 147.4359 | 0 | 1.4487 | 0 | 1.4744 | 0 | 1.4487 | 1.4744 | 6.7164 | 4.8605 | 5.2677
39014.5651 | 2373 | 0 | 39014.5651 | 2215 | 0 |  | 1716.5 | 1937.5 | 144.8718 | 0 | 135.2259 | 0 | 1.4487 | 0 | 1.3523 | 0 | 1.4487 | 1.3523 | 6.7164 | 14.3287 | 5.2677
39014.5672 | 1982 | 0 | 39014.5672 | 2366 | 0 |  | 1901.5 | 2122.5 | 121.0012 | 0 | 144.4444 | 0 | 1.21 | 0 | 1.4444 | 0 | 1.21 | 1.4444 | 27.7689 | 7.0321 | 26.5589
39014.5694 | 2164 | 0 | 39014.5694 | 2130 | 0 |  | 2086.5 | 2307.5 | 132.1123 | 0 | 130.0366 | 0 | 1.3211 | 0 | 1.3004 | 0 | 1.3211 | 1.3004 | 17.0231 | 18.8911 | 15.702
39014.5715 | 2516 | 0 | 39014.5715 | 2070 | 0 |  | 2271 | 2492 | 153.602 | 0 | 126.3736 | 0 | 1.536 | 0 | 1.2637 | 0 | 1.536 | 1.2637 | 0.65103 | 22.3372 | 0.88499
39014.5736 | 2462 | 0 | 39014.5736 | 2063 | 0 |  | 2456 | 2677 | 150.3053 | 0 | 125.9463 | 0 | 1.5031 | 0 | 1.2595 | 0 | 1.5031 | 1.2595 | 2.8587 | 22.7523 | 1.3556
39014.5758 | 2490 | 0 | 39014.5758 | 2058 | 0 |  | 2640.5 | 2861.5 | 152.0147 | 0 | 125.641 | 0 | 1.5201 | 0 | 1.2564 | 0 | 1.5201 | 1.2564 | 1.702 | 23.0505 | 0.18186
39014.5779 | 2291 | 0 | 39014.5779 | 2325 | 0 |  | 2825.5 | 3046.5 | 139.8657 | 0 | 141.9414 | 0 | 1.3987 | 0 | 1.4194 | 0 | 1.3987 | 1.4194 | 10.536 | 8.9196 | 9.1374
39014.58 | 2138 | 0 | 39014.5801 | 2456 | 0 |  | 3010.5 | 3231.5 | 130.525 | 0 | 149.9389 | 0 | 1.3053 | 0 | 1.4994 | 0 | 1.3053 | 1.4994 | 18.4462 | 3.1099 | 17.141

## B4-C6
Open Burn Test 2 |  |  | 2006-10-24 | 13:08 |  |  | Vs = |  | 154.7241 |  | R = | 100
XLPE | 7-C | Tray C | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 4 & 6 | Cable B | Even - | Cable C |  | Even
Time-63 | N11 | N12 | Time-64 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R6-G | R4-6
39014.5437 | 1 | 0 | 39014.5437 | 1 | 0 |  | -133.5 | 87.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
39014.5458 | 1 | 0 | 39014.5458 | 1 | 0 |  | 51 | 272 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
39014.5479 | 1 | 0 | 39014.548 | 1 | 0 |  | 236 | 457 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
39014.5501 | 1 | 0 | 39014.5501 | 1 | 0 |  | 420.5 | 641.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
39014.5522 | 1 | 0 | 39014.5522 | 1 | 0 |  | 605.5 | 826.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
39014.5543 | 1 | 0 | 39014.5544 | 1 | 0 |  | 790 | 1011 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
39014.5565 | 1 | 0 | 39014.5565 | 1 | 0 |  | 975 | 1196 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
39014.5586 | 13 | 1 | 39014.5586 | 1 | 0 |  | 1159.5 | 1380.5 | 0.79365 | 0.06105 | 0.06105 | 0 | 0.0079365 | 0.0006105 | 0.0006105 | 0 | 0.007326 | 0.0006105 | 21012.1912 | 253338 | 251938.5524
39014.5608 | 1836 | 1 | 39014.5608 | 1 | 0 |  | 1344.5 | 1565.5 | 112.0879 | 0.06105 | 0.06105 | 0 | 1.1209 | 0.0006105 | 0.0006105 | 0 | 1.1203 | 0.0006105 | 38.0589 | 253338.0001 | 69710.4832
39014.5629 | 1861 | 0 | 39014.5629 | 1174 | 0 |  | 1529.5 | 1750.5 | 113.6142 | 0 | 71.6728 | 0 | 1.1361 | 0 | 0.71673 | 0 | 1.1361 | 0.71673 | 36.1838 | 115.8756 | 35.0476
39014.565 | 2216 | 0 | 39014.5651 | 1918 | 0 |  | 1714 | 1935 | 135.2869 | 0 | 117.094 | 0 | 1.3529 | 0 | 1.1709 | 0 | 1.3529 | 1.1709 | 14.3673 | 32.1366 | 13.0145
39014.5672 | 2518 | 0 | 39014.5672 | 2372 | 0 |  | 1898.5 | 2119.5 | 153.7241 | 0 | 144.8107 | 0 | 1.5372 | 0 | 1.4481 | 0 | 1.5372 | 1.4481 | 0.65052 | 6.8457 | 0.88672
39014.5693 | 2021 | 0 | 39014.5693 | 2249 | 0 |  | 2083.5 | 2304.5 | 123.3822 | 0 | 137.3016 | 0 | 1.2338 | 0 | 1.373 | 0 | 1.2338 | 1.373 | 25.4023 | 12.6892 | 24.1685
39014.5715 | 1950 | 0 | 39014.5715 | 2375 | 0 |  | 2268.5 | 2489.5 | 119.0476 | 0 | 144.9939 | 0 | 1.1905 | 0 | 1.4499 | 0 | 1.1905 | 1.4499 | 29.9682 | 6.7107 | 28.7777
39014.5736 | 2507 | 0 | 39014.5736 | 1880 | 0 |  | 2453 | 2674 | 153.0525 | 0 | 114.7741 | 0 | 1.5305 | 0 | 1.1477 | 0 | 1.5305 | 1.1477 | 1.0921 | 34.8074 | 0.43838
39014.5757 | 2421 | 0 | 39014.5758 | 2194 | 0 |  | 2638 | 2859 | 147.8022 | 0 | 133.9438 | 0 | 1.478 | 0 | 1.3394 | 0 | 1.478 | 1.3394 | 4.6832 | 15.5141 | 3.2052
39014.5779 | 2159 | 0 | 39014.5779 | 2142 | 0 |  | 2822.5 | 3043.5 | 131.8071 | 0 | 130.7692 | 0 | 1.3181 | 0 | 1.3077 | 0 | 1.3181 | 1.3077 | 17.3868 | 18.3184 | 16.0687
39014.58 | 1995 | 0 | 39014.58 | 1937 | 0 |  | 3007.5 | 3228.5 | 121.7949 | 0 | 118.254 | 0 | 1.2179 | 0 | 1.1825 | 0 | 1.2179 | 1.1825 | 27.0366 | 30.8405 | 25.8186

## B4-C5
Open Burn Test 2 |  |  | 2006-10-24 | 13:08 |  |  | Vs = |  | 156.0061 |  | R = | 100
XLPE | 7-C | Tray C | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 4 & 5 | Cable B | Even - | Cable C |  | Odd
Time-61 | N11 | N12 | Time-62 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R5-G | R4-5
39014.5436 | 1 | 0 | 39014.5436 | 1 | 0 |  | -136.5 | 84.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255438 | 255438 | 255437.9994
39014.5458 | 1 | 0 | 39014.5458 | 1 | 0 |  | 48.5 | 269.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255438 | 255438 | 255437.9994
39014.5479 | 1 | 0 | 39014.5479 | 1 | 0 |  | 233 | 454 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255438 | 255438 | 255437.9994
39014.55 | 1 | 0 | 39014.5501 | 1 | 0 |  | 418 | 639 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255438 | 255438 | 255437.9994
39014.5522 | 0 | 0 | 39014.5522 | 1 | 0 |  | 602.5 | 823.5 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 510976 | 255438 | 510975.9997
39014.5543 | 1 | 0 | 39014.5543 | 1 | 0 |  | 787.5 | 1008.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255438 | 255438 | 255437.9994
39014.5564 | 1 | 0 | 39014.5565 | 1 | 0 |  | 972 | 1193 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255438 | 255438 | 255437.9994
39014.5586 | 16 | 1 | 39014.5586 | 1 | 0 |  | 1157 | 1378 | 0.9768 | 0.06105 | 0.06105 | 0 | 0.009768 | 0.0006105 | 0.0006105 | 0 | 0.0091575 | 0.0006105 | 16929.6418 | 255438 | 253738.6653
39014.5607 | 1842 | 1 | 39014.5607 | 1 | 0 |  | 1341.5 | 1562.5 | 112.4542 | 0.06105 | 0.06105 | 0 | 1.1245 | 0.0006105 | 0.0006105 | 0 | 1.1239 | 0.0006105 | 38.7496 | 255438 | 71210.1223
39014.5629 | 1864 | 1 | 39014.5629 | 972 | 0 |  | 1526.5 | 1747.5 | 113.7973 | 0.06105 | 59.3407 | 0 | 1.138 | 0.0006105 | 0.59341 | 0 | 1.1374 | 0.59341 | 37.1233 | 162.8992 | 42777.7428
39014.565 | 1977 | 0 | 39014.565 | 2239 | 0 |  | 1711 | 1932 | 120.696 | 0 | 136.6911 | 0 | 1.207 | 0 | 1.3669 | 0 | 1.207 | 1.3669 | 29.2554 | 14.1304 | 28.0485
39014.5671 | 2539 | 0 | 39014.5672 | 2110 | 0 |  | 1896 | 2117 | 155.0061 | 0 | 128.8156 | 0 | 1.5501 | 0 | 1.2882 | 0 | 1.5501 | 1.2882 | 0.64514 | 21.1081 | 0.90493
39014.5693 | 2343 | 0 | 39014.5693 | 2335 | 0 |  | 2080.5 | 2301.5 | 143.0403 | 0 | 142.5519 | 0 | 1.4304 | 0 | 1.4255 | 0 | 1.4304 | 1.4255 | 9.0644 | 9.4381 | 7.634
39014.5714 | 1950 | 0 | 39014.5714 | 2229 | 0 |  | 2265.5 | 2486.5 | 119.0476 | 0 | 136.0806 | 0 | 1.1905 | 0 | 1.3608 | 0 | 1.1905 | 1.3608 | 31.0451 | 14.6424 | 29.8547
39014.5736 | 1937 | 0 | 39014.5736 | 2058 | 0 |  | 2450.5 | 2671.5 | 118.254 | 0 | 125.641 | 0 | 1.1825 | 0 | 1.2564 | 0 | 1.1825 | 1.2564 | 31.9246 | 24.1681 | 30.7421
39014.5757 | 2181 | 0 | 39014.5757 | 2056 | 0 |  | 2635 | 2856 | 133.1502 | 0 | 125.5189 | 0 | 1.3315 | 0 | 1.2552 | 0 | 1.3315 | 1.2552 | 17.1655 | 24.2889 | 15.834
39014.5778 | 2036 | 0 | 39014.5778 | 1970 | 0 |  | 2819.5 | 3040.5 | 124.2979 | 0 | 120.2686 | 0 | 1.243 | 0 | 1.2027 | 0 | 1.243 | 1.2027 | 25.5098 | 29.7147 | 24.2668
39014.58 | 2076 | 0 | 39014.58 | 1999 | 0 |  | 3004.5 | 3225.5 | 126.7399 | 0 | 122.0391 | 0 | 1.2674 | 0 | 1.2204 | 0 | 1.2674 | 1.2204 | 23.0915 | 27.8329 | 21.8241

## B3-E10
Open Burn Test 2 |  |  | 2006-10-24 | 13:08 |  |  | Vs = |  | 159.8523 |  | R = | 100
XLPE | 7-C | Tray C | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 3 & 10 | Ch. 3 & 9 | Cable B | Odd - |  | Cable E | Even
Time-55 | N11 | N12 | Time-56 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R10-G | R3-10
39014.5435 | 1 | 0 | 39014.5435 | 1 | 0 |  | -145 | 76 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261738 | 261738 | 261737.9994
39014.5457 | 1 | 0 | 39014.5457 | 1 | 0 |  | 40 | 261 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261738 | 261738 | 261737.9994
39014.5478 | 1 | 0 | 39014.5478 | 1 | 0 |  | 224.5 | 445.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261738 | 261738 | 261737.9994
39014.5499 | 1 | 0 | 39014.55 | 1 | 0 |  | 409.5 | 630.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261738 | 261738 | 261737.9994
39014.5521 | 1 | 0 | 39014.5521 | 1 | 0 |  | 594 | 815 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261738 | 261738 | 261737.9994
39014.5542 | 1 | 0 | 39014.5542 | 1 | 0 |  | 779 | 1000 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261738 | 261738 | 261737.9994
39014.5564 | 1 | 0 | 39014.5564 | 1572 | 0 |  | 963.5 | 1184.5 | 0.06105 | 0 | 95.9707 | 0 | 0.0006105 | 0 | 0.95971 | 0 | 0.0006105 | 0.95971 | 261738 | 66.5636 | 261737.9994
39014.5585 | 11 | 0 | 39014.5585 | 2323 | 0 |  | 1148.5 | 1369.5 | 0.67155 | 0 | 141.8193 | 0 | 0.0067155 | 0 | 1.4182 | 0 | 0.0067155 | 1.4182 | 23703.4545 | 12.7155 | 23703.4478
39014.5606 | 1526 | 0 | 39014.5606 | 2372 | 0 |  | 1333.5 | 1554.5 | 93.1624 | 0 | 144.8107 | 0 | 0.93162 | 0 | 1.4481 | 0 | 0.93162 | 1.4481 | 71.5845 | 10.387 | 70.6529
39014.5628 | 2172 | 0 | 39014.5628 | 2264 | 0 |  | 1518 | 1739 | 132.6007 | 0 | 138.2173 | 0 | 1.326 | 0 | 1.3822 | 0 | 1.326 | 1.3822 | 20.5516 | 15.6528 | 19.2256
39014.5649 | 2197 | 0 | 39014.5649 | 2145 | 0 |  | 1703 | 1924 | 134.127 | 0 | 130.9524 | 0 | 1.3413 | 0 | 1.3095 | 0 | 1.3413 | 1.3095 | 19.1798 | 22.069 | 17.8385
39014.567 | 2105 | 0 | 39014.5671 | 2602 | 0 |  | 1887.5 | 2108.5 | 128.5104 | 0 | 158.8523 | 0 | 1.2851 | 0 | 1.5885 | 0 | 1.2851 | 1.5885 | 24.3886 | 0.62952 | 23.1035
39014.5692 | 2426 | 0 | 39014.5692 | 2447 | 0 |  | 2072.5 | 2293.5 | 148.1074 | 0 | 149.3895 | 0 | 1.4811 | 0 | 1.4939 | 0 | 1.4811 | 1.4939 | 7.9299 | 7.0037 | 6.4489
39014.5713 | 2511 | 0 | 39014.5713 | 2182 | 0 |  | 2257 | 2478 | 153.2967 | 0 | 133.2112 | 0 | 1.533 | 0 | 1.3321 | 0 | 1.533 | 1.3321 | 4.2764 | 19.9991 | 2.7434
39014.5735 | 2447 | 0 | 39014.5735 | 2147 | 0 |  | 2442 | 2663 | 149.3895 | 0 | 131.0745 | 0 | 1.4939 | 0 | 1.3107 | 0 | 1.4939 | 1.3107 | 7.0037 | 21.9553 | 5.5098
39014.5756 | 2394 | 0 | 39014.5756 | 2177 | 0 |  | 2626.5 | 2847.5 | 146.1538 | 0 | 132.906 | 0 | 1.4615 | 0 | 1.3291 | 0 | 1.4615 | 1.3291 | 9.3726 | 20.2747 | 7.9111
39014.5777 | 1954 | 0 | 39014.5778 | 2384 | 0 |  | 2811.5 | 3032.5 | 119.2918 | 0 | 145.5433 | 0 | 1.1929 | 0 | 1.4554 | 0 | 1.1929 | 1.4554 | 34.001 | 9.8314 | 32.8081
39014.5799 | 2413 | 0 | 39014.5799 | 2370 | 0 |  | 2996.5 | 3217.5 | 147.3138 | 0 | 144.6886 | 0 | 1.4731 | 0 | 1.4469 | 0 | 1.4731 | 1.4469 | 8.5114 | 10.4802 | 7.0383

## B3-E9
Open Burn Test 2 |  |  | 2006-10-24 | 13:08 |  |  | Vs = |  | 155.1514 |  | R = | 100
XLPE | 7-C | Tray C | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 3 & 9 | Cable B | Odd - | Cable E |  | Odd
Time-53 | N11 | N12 | Time-54 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R9-G | R3-9
39014.5435 | 1 | 0 | 39014.5435 | 1 | 0 |  | -147.5 | 73.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254038 | 254038 | 254037.9994
39014.5456 | 1 | 0 | 39014.5456 | 1 | 0 |  | 37 | 258 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254038 | 254038 | 254037.9994
39014.5478 | 1 | 0 | 39014.5478 | 1 | 0 |  | 222 | 443 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254038 | 254038 | 254037.9994
39014.5499 | 1 | 0 | 39014.5499 | 1 | 0 |  | 406.5 | 627.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254038 | 254038 | 254037.9994
39014.552 | 1 | 0 | 39014.5521 | 1 | 0 |  | 591.5 | 812.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254038 | 254038 | 254037.9994
39014.5542 | 1 | 0 | 39014.5542 | 1 | 0 |  | 776.5 | 997.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254038 | 254038 | 254037.9994
39014.5563 | 1 | 0 | 39014.5563 | 1 | 0 |  | 961 | 1182 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254038 | 254038 | 254037.9994
39014.5585 | 8 | 0 | 39014.5585 | 1998 | 0 |  | 1145.5 | 1366.5 | 0.4884 | 0 | 121.978 | 0 | 0.004884 | 0 | 1.2198 | 0 | 0.004884 | 1.2198 | 31667.25 | 27.1962 | 31667.2451
39014.5606 | 1543 | 0 | 39014.5606 | 2255 | 0 |  | 1330.5 | 1551.5 | 94.2002 | 0 | 137.6679 | 0 | 0.942 | 0 | 1.3767 | 0 | 0.942 | 1.3767 | 64.7038 | 12.6998 | 63.7618
39014.5627 | 2000 | 0 | 39014.5628 | 2525 | 0 |  | 1515.5 | 1736.5 | 122.1001 | 0 | 154.1514 | 0 | 1.221 | 0 | 1.5415 | 0 | 1.221 | 1.5415 | 27.069 | 0.64871 | 25.848
39014.5649 | 2173 | 0 | 39014.5649 | 2504 | 0 |  | 1700 | 1921 | 132.6618 | 0 | 152.8694 | 0 | 1.3266 | 0 | 1.5287 | 0 | 1.3266 | 1.5287 | 16.9526 | 1.4928 | 15.626
39014.567 | 2054 | 0 | 39014.567 | 2169 | 0 |  | 1884.5 | 2105.5 | 125.3968 | 0 | 132.4176 | 0 | 1.254 | 0 | 1.3242 | 0 | 1.254 | 1.3242 | 23.7283 | 17.1683 | 22.4744
39014.5692 | 2374 | 0 | 39014.5692 | 2311 | 0 |  | 2069.5 | 2290.5 | 144.9328 | 0 | 141.0867 | 0 | 1.4493 | 0 | 1.4109 | 0 | 1.4493 | 1.4109 | 7.0505 | 9.9688 | 5.6012
39014.5713 | 2457 | 0 | 39014.5713 | 2476 | 0 |  | 2254.5 | 2475.5 | 150 | 0 | 151.16 | 0 | 1.5 | 0 | 1.5116 | 0 | 1.5 | 1.5116 | 3.4343 | 2.6405 | 1.9343
39014.5734 | 2379 | 0 | 39014.5734 | 2217 | 0 |  | 2439 | 2660 | 145.2381 | 0 | 135.348 | 0 | 1.4524 | 0 | 1.3535 | 0 | 1.4524 | 1.3535 | 6.8256 | 14.6315 | 5.3732
| 2236 | 0 | 39014.5756 | 2206 | 0 |  | 2625 | 2846 | 136.5079 | 0 | 134.6764 | 0 | 1.3651 | 0 | 1.3468 | 0 | 1.3651 | 1.3468 | 13.6574 | 15.2031 | 12.2923
39014.5777 | 2093 | 0 | 39014.5777 | 2405 | 0 |  | 2808.5 | 3029.5 | 127.7778 | 0 | 146.8254 | 0 | 1.2778 | 0 | 1.4683 | 0 | 1.2778 | 1.4683 | 21.4228 | 5.6707 | 20.1451
39014.5798 | 2115 | 0 | 39014.5799 | 2525 | 0 |  | 2993.5 | 3214.5 | 129.1209 | 0 | 154.1514 | 0 | 1.2912 | 0 | 1.5415 | 0 | 1.2912 | 1.5415 | 20.1598 | 0.64871 | 18.8686

## B3-D8
Open Burn Test 2 |  |  | 2006-10-24 | 13:08 |  |  | Vs = |  | 155.7619 |  | R = | 100
XLPE | 7-C | Tray C | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 3 & 8 | Cable B | Odd - | Cable D |  | Even
Time-51 | N11 | N12 | Time-52 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R8-G | R3-8
39014.5435 | 1 | 0 | 39014.5435 | 1 | 0 |  | -150.5 | 70.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255038 | 255038 | 255037.9994
39014.5456 | 2 | 0 | 39014.5456 | 1 | 0 |  | 34.5 | 255.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 127469 | 255038 | 127468.9988
39014.5477 | 1 | 0 | 39014.5478 | 1 | 0 |  | 219 | 440 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255038 | 255038 | 255037.9994
39014.5499 | 1 | 0 | 39014.5499 | 1 | 0 |  | 403.5 | 624.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255038 | 255038 | 255037.9994
39014.552 | 1 | 0 | 39014.552 | 1 | 0 |  | 588.5 | 809.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255038 | 255038 | 255037.9994
39014.5542 | 2 | 0 | 39014.5542 | 2161 | 0 |  | 773.5 | 994.5 | 0.1221 | 0 | 131.9292 | 0 | 0.001221 | 0 | 1.3193 | 0 | 0.001221 | 1.3193 | 127469 | 18.0648 | 127468.9988
39014.5563 | 1 | 0 | 39014.5563 | 2406 | 0 |  | 958 | 1179 | 0.06105 | 0 | 146.8864 | 0 | 0.0006105 | 0 | 1.4689 | 0 | 0.0006105 | 1.4689 | 255038 | 6.0424 | 255037.9994
39014.5584 | 5 | 0 | 39014.5584 | 2025 | 0 |  | 1143 | 1364 | 0.30525 | 0 | 123.6264 | 0 | 0.0030525 | 0 | 1.2363 | 0 | 0.0030525 | 1.2363 | 50927.6 | 25.9941 | 50927.5969
39014.5606 | 1570 | 0 | 39014.5606 | 2284 | 0 |  | 1327.5 | 1548.5 | 95.8486 | 0 | 139.4383 | 0 | 0.95849 | 0 | 1.3944 | 0 | 0.95849 | 1.3944 | 62.5083 | 11.7067 | 61.5498
39014.5627 | 2187 | 0 | 39014.5627 | 2535 | 0 |  | 1512.5 | 1733.5 | 133.5165 | 0 | 154.7619 | 0 | 1.3352 | 0 | 1.5476 | 0 | 1.3352 | 1.5476 | 16.6612 | 0.64615 | 15.326
39014.5648 | 2414 | 0 | 39014.5649 | 2036 | 0 |  | 1697.5 | 1918.5 | 147.3748 | 0 | 124.2979 | 0 | 1.4737 | 0 | 1.243 | 0 | 1.4737 | 1.243 | 5.691 | 25.3134 | 4.2172
39014.567 | 2524 | 0 | 39014.567 | 2316 | 0 |  | 1882 | 2103 | 154.0904 | 0 | 141.3919 | 0 | 1.5409 | 0 | 1.4139 | 0 | 1.5409 | 1.4139 | 1.0848 | 10.1632 | 0.45612
39014.5691 | 2005 | 0 | 39014.5691 | 2180 | 0 |  | 2066.5 | 2287.5 | 122.4054 | 0 | 133.0891 | 0 | 1.2241 | 0 | 1.3309 | 0 | 1.2241 | 1.3309 | 27.2509 | 17.0358 | 26.0268
39014.5713 | 1981 | 0 | 39014.5713 | 2292 | 0 |  | 2251.5 | 2472.5 | 120.9402 | 0 | 139.9267 | 0 | 1.2094 | 0 | 1.3993 | 0 | 1.2094 | 1.3993 | 28.7925 | 11.3168 | 27.5831
39014.5734 | 2201 | 0 | 39014.5734 | 2126 | 0 |  | 2436.5 | 2657.5 | 134.3712 | 0 | 129.7924 | 0 | 1.3437 | 0 | 1.2979 | 0 | 1.3437 | 1.2979 | 15.9191 | 20.0085 | 14.5754
39014.5755 | 2097 | 0 | 39014.5756 | 2402 | 0 |  | 2621 | 2842 | 128.022 | 0 | 146.6422 | 0 | 1.2802 | 0 | 1.4664 | 0 | 1.2802 | 1.4664 | 21.6681 | 6.219 | 20.3879
39014.5777 | 2181 | 0 | 39014.5777 | 2029 | 0 |  | 2806 | 3027 | 133.1502 | 0 | 123.8706 | 0 | 1.3315 | 0 | 1.2387 | 0 | 1.3315 | 1.2387 | 16.9821 | 25.7457 | 15.6506
39014.5798 | 2068 | 0 | 39014.5798 | 2412 | 0 |  | 2990.5 | 3211.5 | 126.2515 | 0 | 147.2527 | 0 | 1.2625 | 0 | 1.4725 | 0 | 1.2625 | 1.4725 | 23.3743 | 5.7786 | 22.1118

## B3-D7
Open Burn Test 2 |  |  | 2006-10-24 | 13:08 |  |  | Vs = |  | 159.7302 |  | R = | 100
XLPE | 7-C | Tray C | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 3 & 7 | Cable B | Odd - | Cable D |  | Odd
Time-49 | N11 | N12 | Time-50 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R7-G | R3-7
39014.5434 | 1 | 0 | 39014.5434 | 1 | 0 |  | -153.5 | 67.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261538 | 261538 | 261537.9994
39014.5456 | 1 | 0 | 39014.5456 | 1 | 0 |  | 31.5 | 252.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261538 | 261538 | 261537.9994
39014.5477 | 1 | 0 | 39014.5477 | 1 | 0 |  | 216.5 | 437.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261538 | 261538 | 261537.9994
39014.5498 | 1 | 0 | 39014.5499 | 1 | 0 |  | 401 | 622 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261538 | 261538 | 261537.9994
39014.552 | 1 | 0 | 39014.552 | 2 | 0 |  | 585.5 | 806.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 261538 | 130719 | 261537.9994
39014.5541 | 1 | 0 | 39014.5541 | 2068 | 0 |  | 770.5 | 991.5 | 0.06105 | 0 | 126.2515 | 0 | 0.0006105 | 0 | 1.2625 | 0 | 0.0006105 | 1.2625 | 261538 | 26.5174 | 261537.9994
39014.5563 | 1 | 0 | 39014.5563 | 2174 | 0 |  | 955.5 | 1176.5 | 0.06105 | 0 | 132.7228 | 0 | 0.0006105 | 0 | 1.3272 | 0 | 0.0006105 | 1.3272 | 261538 | 20.3487 | 261537.9994
39014.5584 | 3 | 0 | 39014.5584 | 2526 | 0 |  | 1140 | 1361 | 0.18315 | 0 | 154.2125 | 0 | 0.0018315 | 0 | 1.5421 | 0 | 0.0018315 | 1.5421 | 87112.6667 | 3.578 | 87112.6648
39014.5605 | 1168 | 0 | 39014.5606 | 1986 | 0 |  | 1325 | 1546 | 71.3065 | 0 | 121.2454 | 0 | 0.71306 | 0 | 1.2125 | 0 | 0.71306 | 1.2125 | 124.0051 | 31.7412 | 123.2921
39014.5627 | 2390 | 0 | 39014.5627 | 2327 | 0 |  | 1509.5 | 1730.5 | 145.9096 | 0 | 142.0635 | 0 | 1.4591 | 0 | 1.4206 | 0 | 1.4591 | 1.4206 | 9.472 | 12.4358 | 8.0129
39014.5648 | 2545 | 0 | 39014.5648 | 2568 | 0 |  | 1694.5 | 1915.5 | 155.3724 | 0 | 156.7766 | 0 | 1.5537 | 0 | 1.5678 | 0 | 1.5537 | 1.5678 | 2.8047 | 1.884 | 1.251
39014.567 | 2251 | 0 | 39014.567 | 2457 | 0 |  | 1879.5 | 2100.5 | 137.4237 | 0 | 150 | 0 | 1.3742 | 0 | 1.5 | 0 | 1.3742 | 1.5 | 16.2319 | 6.4868 | 14.8577
39014.5691 | 2301 | 0 | 39014.5691 | 2600 | 0 |  | 2064 | 2285 | 140.4762 | 0 | 158.7302 | 0 | 1.4048 | 0 | 1.5873 | 0 | 1.4048 | 1.5873 | 13.7062 | 0.63 | 12.3015
39014.5712 | 1983 | 0 | 39014.5712 | 2384 | 0 |  | 2248.5 | 2469.5 | 121.0623 | 0 | 145.5433 | 0 | 1.2106 | 0 | 1.4554 | 0 | 1.2106 | 1.4554 | 31.9405 | 9.7475 | 30.7299
39014.5734 | 2348 | 0 | 39014.5734 | 2434 | 0 |  | 2433.5 | 2654.5 | 143.3455 | 0 | 148.5958 | 0 | 1.4335 | 0 | 1.486 | 0 | 1.4335 | 1.486 | 11.4302 | 7.493 | 9.9967
39014.5755 | 2487 | 0 | 39014.5755 | 2279 | 0 |  | 2618.5 | 2839.5 | 151.8315 | 0 | 139.1331 | 0 | 1.5183 | 0 | 1.3913 | 0 | 1.5183 | 1.3913 | 5.2023 | 14.8039 | 3.6839
39014.5776 | 2190 | 0 | 39014.5777 | 2338 | 0 |  | 2803 | 3024 | 133.6996 | 0 | 142.735 | 0 | 1.337 | 0 | 1.4274 | 0 | 1.337 | 1.4274 | 19.4694 | 11.9068 | 18.1324
39014.5798 | 2276 | 0 | 39014.5798 | 2251 | 0 |  | 2988 | 3209 | 138.9499 | 0 | 137.4237 | 0 | 1.3895 | 0 | 1.3742 | 0 | 1.3895 | 1.3742 | 14.9552 | 16.2319 | 13.5657

## B3-C6
Open Burn Test 2 |  |  | 2006-10-24 | 13:08 |  |  | Vs = |  | 154.7241 |  | R = | 100
XLPE | 7-C | Tray C | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 3 & 6 | Cable B | Odd - | Cable C |  | Even
Time-47 | N11 | N12 | Time-48 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R6-G | R3-6
39014.5434 | 1 | 0 | 39014.5434 | 1 | 0 |  | -156 | 65 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
39014.5455 | 1 | 0 | 39014.5455 | 1 | 0 |  | 28.5 | 249.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
39014.5477 | 1 | 0 | 39014.5477 | 1 | 0 |  | 213.5 | 434.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
39014.5498 | 1 | 0 | 39014.5498 | 1 | 0 |  | 398.5 | 619.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
39014.5519 | 1 | 0 | 39014.552 | 1 | 0 |  | 583 | 804 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
39014.5541 | 1 | 0 | 39014.5541 | 1 | 0 |  | 767.5 | 988.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
39014.5562 | 1 | 0 | 39014.5562 | 1 | 0 |  | 952.5 | 1173.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
39014.5584 | 2 | 1 | 39014.5584 | 1 | 0 |  | 1137.5 | 1358.5 | 0.1221 | 0.06105 | 0.06105 | 0 | 0.001221 | 0.0006105 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253038.1184
39014.5605 | 973 | 1 | 39014.5605 | 1 | 0 |  | 1322 | 1543 | 59.4017 | 0.06105 | 0.06105 | 0 | 0.59402 | 0.0006105 | 0.0006105 | 0 | 0.59341 | 0.0006105 | 160.6359 | 253338 | 155976.4315
39014.5626 | 1879 | 0 | 39014.5627 | 1443 | 0 |  | 1507 | 1728 | 114.7131 | 0 | 88.0952 | 0 | 1.1471 | 0 | 0.88095 | 0 | 1.1471 | 0.88095 | 34.8792 | 75.6327 | 33.7321
39014.5648 | 2157 | 0 | 39014.5648 | 1848 | 0 |  | 1691.5 | 1912.5 | 131.685 | 0 | 112.8205 | 0 | 1.3168 | 0 | 1.1282 | 0 | 1.3168 | 1.1282 | 17.4956 | 37.1418 | 16.1787
39014.5669 | 2518 | 0 | 39014.5669 | 1952 | 0 |  | 1876.5 | 2097.5 | 153.7241 | 0 | 119.1697 | 0 | 1.5372 | 0 | 1.1917 | 0 | 1.5372 | 1.1917 | 0.65052 | 29.835 | 0.88672
39014.5691 | 2309 | 0 | 39014.5691 | 2151 | 0 |  | 2061 | 2282 | 140.9646 | 0 | 131.3187 | 0 | 1.4096 | 0 | 1.3132 | 0 | 1.4096 | 1.3132 | 9.7609 | 17.8233 | 8.3513
39014.5712 | 2355 | 0 | 39014.5712 | 2405 | 0 |  | 2246 | 2467 | 143.7729 | 0 | 146.8254 | 0 | 1.4377 | 0 | 1.4683 | 0 | 1.4377 | 1.4683 | 7.617 | 5.3796 | 6.1793
39014.5733 | 2145 | 0 | 39014.5733 | 1855 | 0 |  | 2430.5 | 2651.5 | 130.9524 | 0 | 113.2479 | 0 | 1.3095 | 0 | 1.1325 | 0 | 1.3095 | 1.1325 | 18.1529 | 36.6243 | 16.8434
39014.5755 | 1978 | 0 | 39014.5755 | 2341 | 0 |  | 2615.5 | 2836.5 | 120.757 | 0 | 142.9182 | 0 | 1.2076 | 0 | 1.4292 | 0 | 1.2076 | 1.4292 | 28.1284 | 8.2606 | 26.9208
39014.5776 | 2265 | 0 | 39014.5776 | 1819 | 0 |  | 2800.5 | 3021.5 | 138.2784 | 0 | 111.0501 | 0 | 1.3828 | 0 | 1.1105 | 0 | 1.3828 | 1.1105 | 11.8932 | 39.3282 | 10.5104
39014.5797 | 1996 | 0 | 39014.5798 | 2020 | 0 |  | 2985 | 3206 | 121.8559 | 0 | 123.3211 | 0 | 1.2186 | 0 | 1.2332 | 0 | 1.2186 | 1.2332 | 26.9729 | 25.4644 | 25.7544

## B3-C5
Open Burn Test 2 |  |  | 2006-10-24 | 13:08 |  |  | Vs = |  | 155.3346 |  | R = | 100
XLPE | 7-C | Tray C | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 3 & 5 | Cable B | Odd - | Cable C |  | Odd
Time-45 | N11 | N12 | Time-46 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R5-G | R3-5
39014.5434 | 1 | 0 | 39014.5434 | 1 | 0 |  | -159 | 62 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254338 | 254338 | 254337.9994
39014.5455 | 1 | 0 | 39014.5455 | 1 | 0 |  | 26 | 247 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254338 | 254338 | 254337.9994
39014.5476 | 1 | 0 | 39014.5477 | 1 | 0 |  | 210.5 | 431.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254338 | 254338 | 254337.9994
39014.5498 | 1 | 0 | 39014.5498 | 1 | 0 |  | 395.5 | 616.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254338 | 254338 | 254337.9994
39014.5519 | 1 | 0 | 39014.5519 | 1 | 0 |  | 580.5 | 801.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254338 | 254338 | 254337.9994
39014.5541 | 1 | 0 | 39014.5541 | 1 | 0 |  | 765 | 986 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254338 | 254338 | 254337.9994
39014.5562 | 1 | 0 | 39014.5562 | 1 | 0 |  | 949.5 | 1170.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254338 | 254338 | 254337.9994
39014.5583 | 1 | 0 | 39014.5583 | 1 | 0 |  | 1134.5 | 1355.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254338 | 254338 | 254337.9994
39014.5605 | 1689 | 1 | 39014.5605 | 2 | 0 |  | 1319.5 | 1540.5 | 103.1136 | 0.06105 | 0.1221 | 0 | 1.0311 | 0.0006105 | 0.001221 | 0 | 1.0305 | 0.001221 | 50.6742 | 127119 | 85370.8418
39014.5626 | 1975 | 1 | 39014.5626 | 851 | 0 |  | 1504 | 1725 | 120.5739 | 0.06105 | 51.9536 | 0 | 1.2057 | 0.0006105 | 0.51954 | 0 | 1.2051 | 0.51954 | 28.8513 | 198.9871 | 37827.8136
39014.5647 | 2511 | 0 | 39014.5648 | 1813 | 0 |  | 1689 | 1910 | 153.2967 | 0 | 110.6838 | 0 | 1.533 | 0 | 1.1068 | 0 | 1.533 | 1.1068 | 1.3294 | 40.3409 | 0.20362
39014.5669 | 2089 | 0 | 39014.5669 | 2216 | 0 |  | 1873.5 | 2094.5 | 127.5336 | 0 | 135.2869 | 0 | 1.2753 | 0 | 1.3529 | 0 | 1.2753 | 1.3529 | 21.7989 | 14.8186 | 20.5236
39014.569 | 2068 | 0 | 39014.569 | 2012 | 0 |  | 2058.5 | 2279.5 | 126.2515 | 0 | 122.8327 | 0 | 1.2625 | 0 | 1.2283 | 0 | 1.2625 | 1.2283 | 23.0358 | 26.4602 | 21.7733
39014.5712 | 2528 | 0 | 39014.5712 | 2413 | 0 |  | 2243 | 2464 | 154.3346 | 0 | 147.3138 | 0 | 1.5433 | 0 | 1.4731 | 0 | 1.5433 | 1.4731 | 0.64794 | 5.4447 | 0.8954
39014.5733 | 2429 | 0 | 39014.5733 | 2175 | 0 |  | 2428 | 2649 | 148.2906 | 0 | 132.7839 | 0 | 1.4829 | 0 | 1.3278 | 0 | 1.4829 | 1.3278 | 4.7501 | 16.983 | 3.2672
39014.5754 | 2182 | 0 | 39014.5755 | 2005 | 0 |  | 2612.5 | 2833.5 | 133.2112 | 0 | 122.4054 | 0 | 1.3321 | 0 | 1.2241 | 0 | 1.3321 | 1.2241 | 16.6077 | 26.9017 | 15.2756
39014.5776 | 2182 | 0 | 39014.5776 | 2276 | 0 |  | 2797.5 | 3018.5 | 133.2112 | 0 | 138.9499 | 0 | 1.3321 | 0 | 1.3895 | 0 | 1.3321 | 1.3895 | 16.6077 | 11.7917 | 15.2756
39014.5797 | 1998 | 0 | 39014.5797 | 1705 | 0 |  | 2982 | 3203 | 121.978 | 0 | 104.0904 | 0 | 1.2198 | 0 | 1.0409 | 0 | 1.2198 | 1.0409 | 27.3463 | 49.2305 | 26.1266

## B3-B4
Open Burn Test 2 |  |  | 2006-10-24 | 13:08 |  |  | Vs = |  | 152.8926 |  | R = | 100
XLPE | 7-C | Tray C | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 3 & 4 | Cable B | Odd -Even
Time-43 | N11 | N12 | Time-44 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R4-G | R3-4
39014.5433 | 1 | 0 | 39014.5433 | 1 | 0 |  | -161.5 | 59.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
39014.5455 | 1 | 0 | 39014.5455 | 1 | 0 |  | 23 | 244 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
39014.5476 | 1 | 0 | 39014.5476 | 1 | 0 |  | 207.5 | 428.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
39014.5497 | 1 | 0 | 39014.5498 | 1 | 0 |  | 392.5 | 613.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
39014.5519 | 1 | 0 | 39014.5519 | 1 | 0 |  | 577.5 | 798.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
39014.554 | 1 | 0 | 39014.554 | 1 | 0 |  | 762.5 | 983.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
39014.5562 | 1 | 0 | 39014.5562 | 1 | 0 |  | 947 | 1168 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
39014.5583 | 17 | 0 | 39014.5583 | 11 | 0 |  | 1131.5 | 1352.5 | 1.0379 | 0 | 0.67155 | 0 | 0.010379 | 0 | 0.0067155 | 0 | 0.010379 | 0.0067155 | 14631.6471 | 22667.0909 | 14631.6367
39014.5604 | 1339 | 678 | 39014.5605 | 1362 | 682 |  | 1316.5 | 1537.5 | 81.746 | 41.3919 | 83.1502 | 41.6361 | 0.81746 | 0.41392 | 0.8315 | 0.41636 | 0.40354 | 0.41514 | 295.4743 | 254.323 | 51.597
39014.5626 | 2171 | 27 | 39014.5626 | 2010 | 26 |  | 1501.5 | 1722.5 | 132.5397 | 1.6484 | 122.7106 | 1.5873 | 1.3254 | 0.016484 | 1.2271 | 0.015873 | 1.3089 | 1.2112 | 16.3074 | 27.0958 | 241.9176
39014.5647 | 2245 | 0 | 39014.5647 | 1971 | 0 |  | 1686 | 1907 | 137.0574 | 0 | 120.3297 | 0 | 1.3706 | 0 | 1.2033 | 0 | 1.3706 | 1.2033 | 11.5537 | 27.0614 | 10.1831
39014.5669 | 2057 | 0 | 39014.5669 | 2380 | 0 |  | 1870.5 | 2091.5 | 125.58 | 0 | 145.2991 | 0 | 1.2558 | 0 | 1.453 | 0 | 1.2558 | 1.453 | 21.7491 | 5.2261 | 20.4933
39014.569 | 2255 | 0 | 39014.569 | 2194 | 0 |  | 2055.5 | 2276.5 | 137.6679 | 0 | 133.9438 | 0 | 1.3767 | 0 | 1.3394 | 0 | 1.3767 | 1.3394 | 11.059 | 14.1468 | 9.6823
39014.5711 | 2141 | 0 | 39014.5711 | 2328 | 0 |  | 2240.5 | 2461.5 | 130.7082 | 0 | 142.1245 | 0 | 1.3071 | 0 | 1.4212 | 0 | 1.3071 | 1.4212 | 16.9724 | 7.5765 | 15.6654
39014.5733 | 2488 | 0 | 39014.5733 | 2346 | 0 |  | 2425 | 2646 | 151.8926 | 0 | 143.2234 | 0 | 1.5189 | 0 | 1.4322 | 0 | 1.5189 | 1.4322 | 0.65836 | 6.7511 | 0.86057
39014.5754 | 2198 | 0 | 39014.5754 | 2481 | 1 |  | 2610 | 2831 | 134.188 | 0 | 151.4652 | 0.06105 | 1.3419 | 0 | 1.5147 | 0.0006105 | 1.3419 | 1.514 | 13.939 | 0.98306 | 12.5972
39014.5775 | 2163 | 2 | 39014.5776 | 2252 | 2 |  | 2794.5 | 3015.5 | 132.0513 | 0.1221 | 137.4847 | 0.1221 | 1.3205 | 0.001221 | 1.3748 | 0.001221 | 1.3193 | 1.3736 | 15.928 | 11.2798 | 1720.0561
39014.5797 | 2449 | 8 | 39014.5797 | 1941 | 7 |  | 2979.5 | 3200.5 | 149.5116 | 0.4884 | 118.4982 | 0.42735 | 1.4951 | 0.004884 | 1.185 | 0.0042735 | 1.4902 | 1.1807 | 2.2904 | 34.5975 | 152.2345

## A2-C6
Open Burn Test 2 |  |  | 2006-10-24 | 13:08 |  |  | Vs = |  | 144.956 |  | R = | 100
XLPE | 7-C | Tray C | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 2 & 6 | Cable A | Even - | Cable C |  | Even
Time-29 | N11 | N12 | Time-30 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R6-G | R2-6
39014.5431 | 1 | 0 | 39014.5431 | 1 | 0 |  | -181.5 | 39.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237338 | 237338 | 237337.9994
39014.5452 | 1 | 0 | 39014.5453 | 1 | 0 |  | 3.5 | 224.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237338 | 237338 | 237337.9994
39014.5474 | 1 | 0 | 39014.5474 | 1 | 0 |  | 188.5 | 409.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237338 | 237338 | 237337.9994
39014.5495 | 1 | 0 | 39014.5495 | 1 | 0 |  | 373 | 594 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237338 | 237338 | 237337.9994
39014.5517 | 1 | 0 | 39014.5517 | 1 | 0 |  | 558 | 779 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237338 | 237338 | 237337.9994
39014.5538 | 1 | 0 | 39014.5538 | 1 | 0 |  | 742.5 | 963.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237338 | 237338 | 237337.9994
39014.5559 | 1 | 0 | 39014.5559 | 1 | 0 |  | 927.5 | 1148.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237338 | 237338 | 237337.9994
39014.5581 | 1 | 0 | 39014.5581 | 1 | 0 |  | 1112 | 1333 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237338 | 237338 | 237337.9994
39014.5602 | 1 | 0 | 39014.5602 | 1 | 0 |  | 1297 | 1518 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237338 | 237338 | 237337.9994
39014.5623 | 85 | 0 | 39014.5624 | 542 | 0 |  | 1481.5 | 1702.5 | 5.1893 | 0 | 33.0891 | 0 | 0.051893 | 0 | 0.33089 | 0 | 0.051893 | 0.33089 | 2693.3882 | 338.0775 | 2693.3363
39014.5645 | 1112 | 3 | 39014.5645 | 2128 | 2 |  | 1666.5 | 1887.5 | 67.8877 | 0.18315 | 129.9145 | 0.1221 | 0.67888 | 0.0018315 | 1.2991 | 0.001221 | 0.67705 | 1.2979 | 116.5488 | 11.5983 | 4362.8571
39014.5666 | 1717 | 0 | 39014.5666 | 2216 | 0 |  | 1851 | 2072 | 104.823 | 0 | 135.2869 | 0 | 1.0482 | 0 | 1.3529 | 0 | 1.0482 | 1.3529 | 38.2865 | 7.1471 | 37.2383
39014.5688 | 1887 | 0 | 39014.5688 | 2189 | 0 |  | 2036 | 2257 | 115.2015 | 0 | 133.6386 | 0 | 1.152 | 0 | 1.3364 | 0 | 1.152 | 1.3364 | 25.8283 | 8.4687 | 24.6763
39014.5709 | 2223 | 0 | 39014.5709 | 2189 | 0 |  | 2220.5 | 2441.5 | 135.7143 | 0 | 133.6386 | 0 | 1.3571 | 0 | 1.3364 | 0 | 1.3571 | 1.3364 | 6.8097 | 8.4687 | 5.4526
39014.573 | 2153 | 0 | 39014.5731 | 2152 | 0 |  | 2405.5 | 2626.5 | 131.4408 | 0 | 131.3797 | 0 | 1.3144 | 0 | 1.3138 | 0 | 1.3144 | 1.3138 | 10.2824 | 10.3336 | 8.968
39014.5752 | 1785 | 0 | 39014.5752 | 2358 | 0 |  | 2590.5 | 2811.5 | 108.9744 | 0 | 143.956 | 0 | 1.0897 | 0 | 1.4396 | 0 | 1.0897 | 1.4396 | 33.0185 | 0.69466 | 31.9287
39014.5773 | 2247 | 1 | 39014.5773 | 1801 | 1 |  | 2775 | 2996 | 137.1795 | 0.06105 | 109.9512 | 0.06105 | 1.3718 | 0.0006105 | 1.0995 | 0.0006105 | 1.3712 | 1.0989 | 5.6793 | 32.1691 | 3076.0091
39014.5795 | 1891 | 7 | 39014.5795 | 1739 | 6 |  | 2960 | 3181 | 115.4457 | 0.42735 | 106.1661 | 0.3663 | 1.1545 | 0.0042735 | 1.0617 | 0.003663 | 1.1502 | 1.058 | 25.9162 | 37.16 | 1843.7577

## A2-C5
Open Burn Test 2 |  |  | 2006-10-24 | 13:08 |  |  | Vs = |  | 141.293 |  | R = | 100
XLPE | 7-C | Tray C | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 2 & 5 | Cable A | Even - | Cable C |  | Odd
Time-27 | N11 | N12 | Time-28 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R5-G | R2-5
39014.5431 | 1 | 0 | 39014.5431 | 1 | 0 |  | -184 | 37 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 231338 | 231338 | 231337.9994
39014.5452 | 1 | 0 | 39014.5452 | 1 | 0 |  | 0.5 | 221.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 231338 | 231338 | 231337.9994
39014.5473 | 1 | 0 | 39014.5474 | 1 | 0 |  | 185.5 | 406.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 231338 | 231338 | 231337.9994
39014.5495 | 1 | 0 | 39014.5495 | 1 | 0 |  | 370 | 591 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 231338 | 231338 | 231337.9994
39014.5516 | 1 | 0 | 39014.5516 | 1 | 0 |  | 555 | 776 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 231338 | 231338 | 231337.9994
39014.5538 | 1 | 0 | 39014.5538 | 1 | 0 |  | 739.5 | 960.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 231338 | 231338 | 231337.9994
39014.5559 | 1 | 0 | 39014.5559 | 1 | 0 |  | 924.5 | 1145.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 231338 | 231338 | 231337.9994
39014.558 | 1 | 0 | 39014.5581 | 1 | 0 |  | 1109.5 | 1330.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 231338 | 231338 | 231337.9994
39014.5602 | 1 | 0 | 39014.5602 | 1 | 0 |  | 1294 | 1515 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 231338 | 231338 | 231337.9994
39014.5623 | 85 | 0 | 39014.5623 | 509 | 0 |  | 1479 | 1700 | 5.1893 | 0 | 31.0745 | 0 | 0.051893 | 0 | 0.31074 | 0 | 0.051893 | 0.31074 | 2622.8 | 354.6916 | 2622.7481
39014.5645 | 1382 | 4 | 39014.5645 | 1757 | 3 |  | 1663.5 | 1884.5 | 84.3712 | 0.2442 | 107.265 | 0.18315 | 0.84371 | 0.002442 | 1.0726 | 0.0018315 | 0.84127 | 1.0708 | 68.284 | 31.8574 | 5607.5363
39014.5666 | 1699 | 0 | 39014.5666 | 1888 | 0 |  | 1848.5 | 2069.5 | 103.7241 | 0 | 115.2625 | 0 | 1.0372 | 0 | 1.1526 | 0 | 1.0372 | 1.1526 | 36.2201 | 22.5837 | 35.1829
39014.5687 | 1900 | 0 | 39014.5687 | 2180 | 0 |  | 2033.5 | 2254.5 | 115.9951 | 0 | 133.0891 | 0 | 1.16 | 0 | 1.3309 | 0 | 1.16 | 1.3309 | 21.8095 | 6.1642 | 20.6495
39014.5709 | 1844 | 0 | 39014.5709 | 2216 | 0 |  | 2218 | 2439 | 112.5763 | 0 | 135.2869 | 0 | 1.1258 | 0 | 1.3529 | 0 | 1.1258 | 1.3529 | 25.5087 | 4.4395 | 24.3829
39014.573 | 1963 | 0 | 39014.573 | 2021 | 0 |  | 2402.5 | 2623.5 | 119.8413 | 0 | 123.3822 | 0 | 1.1984 | 0 | 1.2338 | 0 | 1.1984 | 1.2338 | 17.9002 | 14.5166 | 16.7017
39014.5752 | 1735 | 0 | 39014.5752 | 2298 | 0 |  | 2587.5 | 2808.5 | 105.9219 | 0 | 140.293 | 0 | 1.0592 | 0 | 1.4029 | 0 | 1.0592 | 1.4029 | 33.3937 | 0.71279 | 32.3344
39014.5773 | 1939 | 1 | 39014.5773 | 2133 | 1 |  | 2772.5 | 2993.5 | 118.3761 | 0.06105 | 130.2198 | 0.06105 | 1.1838 | 0.0006105 | 1.3022 | 0.0006105 | 1.1832 | 1.3016 | 19.4874 | 8.528 | 2941.8429
39014.5794 | 2055 | 8 | 39014.5794 | 1911 | 7 |  | 2957 | 3178 | 125.4579 | 0.4884 | 116.6667 | 0.42735 | 1.2546 | 0.004884 | 1.1667 | 0.0042735 | 1.2497 | 1.1624 | 12.9025 | 21.8073 | 562.5608

## A2-B4
Open Burn Test 2 |  |  | 2006-10-24 | 13:08 |  |  | Vs = |  | 137.569 |  | R = | 100
XLPE | 7-C | Tray C | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 2 & 4 | Cable A | Even - | Cable B |  | Even
Time-25 | N11 | N12 | Time-26 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R4-G | R2-4
39014.543 | 1 | 0 | 39014.5431 | 1 | 0 |  | -186.5 | 34.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 225238 | 225238 | 225237.9994
39014.5452 | 1 | 0 | 39014.5452 | 1 | 0 |  | -2 | 219 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 225238 | 225238 | 225237.9994
39014.5473 | 1 | 0 | 39014.5473 | 1 | 0 |  | 182.5 | 403.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 225238 | 225238 | 225237.9994
39014.5495 | 1 | 0 | 39014.5495 | 1 | 0 |  | 367.5 | 588.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 225238 | 225238 | 225237.9994
39014.5516 | 1 | 0 | 39014.5516 | 1 | 0 |  | 552.5 | 773.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 225238 | 225238 | 225237.9994
39014.5537 | 1 | 0 | 39014.5537 | 1 | 0 |  | 737 | 958 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 225238 | 225238 | 225237.9994
39014.5559 | 1 | 0 | 39014.5559 | 1 | 0 |  | 921.5 | 1142.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 225238 | 225238 | 225237.9994
39014.558 | 1 | 0 | 39014.558 | 1 | 0 |  | 1106.5 | 1327.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 225238 | 225238 | 225237.9994
39014.5602 | 1 | 0 | 39014.5602 | 1 | 0 |  | 1291.5 | 1512.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 225238 | 225238 | 225237.9994
39014.5623 | 51 | 0 | 39014.5623 | 51 | 0 |  | 1476 | 1697 | 3.1136 | 0 | 3.1136 | 0 | 0.031136 | 0 | 0.031136 | 0 | 0.031136 | 0.031136 | 4318.3922 | 4318.3922 | 4318.361
39014.5644 | 1216 | 0 | 39014.5644 | 1087 | 0 |  | 1661 | 1882 | 74.2369 | 0 | 66.3614 | 0 | 0.74237 | 0 | 0.66361 | 0 | 0.74237 | 0.66361 | 85.3109 | 107.3027 | 84.5685
39014.5666 | 1690 | 0 | 39014.5666 | 1621 | 0 |  | 1845.5 | 2066.5 | 103.1746 | 0 | 98.9621 | 0 | 1.0317 | 0 | 0.98962 | 0 | 1.0317 | 0.98962 | 33.3361 | 39.0117 | 32.3043
39014.5687 | 2199 | 0 | 39014.5687 | 1940 | 0 |  | 2030.5 | 2251.5 | 134.2491 | 0 | 118.4371 | 0 | 1.3425 | 0 | 1.1844 | 0 | 1.3425 | 1.1844 | 2.4729 | 16.1536 | 1.1305
39014.5708 | 1733 | 0 | 39014.5709 | 1792 | 0 |  | 2215 | 2436 | 105.7998 | 0 | 109.4017 | 0 | 1.058 | 0 | 1.094 | 0 | 1.058 | 1.094 | 30.0277 | 25.7467 | 28.9697
39014.573 | 2237 | 0 | 39014.573 | 1822 | 0 |  | 2400 | 2621 | 136.569 | 0 | 111.2332 | 0 | 1.3657 | 0 | 1.1123 | 0 | 1.3657 | 1.1123 | 0.73223 | 23.6762 | 0.63346
39014.5751 | 1858 | 0 | 39014.5751 | 2224 | 0 |  | 2584.5 | 2805.5 | 113.431 | 0 | 135.7753 | 0 | 1.1343 | 0 | 1.3578 | 0 | 1.1343 | 1.3578 | 21.2799 | 1.321 | 20.1456
39014.5773 | 2224 | 0 | 39014.5773 | 2148 | 0 |  | 2769.5 | 2990.5 | 135.7753 | 0 | 131.1355 | 0 | 1.3578 | 0 | 1.3114 | 0 | 1.3578 | 1.3114 | 1.321 | 4.906 | 0.03671
39014.5794 | 1700 | 0 | 39014.5794 | 2113 | 0 |  | 2954.5 | 3175.5 | 103.7851 | 0 | 128.9988 | 0 | 1.0379 | 0 | 1.29 | 0 | 1.0379 | 1.29 | 32.5518 | 6.6436 | 31.5139

## A2-B3
Open Burn Test 2 |  |  | 2006-10-24 | 13:08 |  |  | Vs = |  | 152.7094 |  | R = | 100
XLPE | 7-C | Tray C | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 2 & 3 | Cable A | Even - | Cable B |  | Odd
Time-23 | N11 | N12 | Time-24 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R3-G | R2-3
39014.543 | 1 | 0 | 39014.543 | 1 | 0 |  | -189.5 | 31.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
39014.5451 | 1 | 0 | 39014.5452 | 1 | 0 |  | -5 | 216 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
39014.5473 | 1 | 0 | 39014.5473 | 1 | 0 |  | 180 | 401 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
39014.5494 | 1 | 0 | 39014.5494 | 1 | 0 |  | 364.5 | 585.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
39014.5516 | 1 | 0 | 39014.5516 | 1 | 0 |  | 549.5 | 770.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
39014.5537 | 1 | 0 | 39014.5537 | 1 | 0 |  | 734 | 955 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
39014.5558 | 1 | 0 | 39014.5559 | 1 | 0 |  | 919 | 1140 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
39014.558 | 1 | 0 | 39014.558 | 1 | 0 |  | 1103.5 | 1324.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
39014.5601 | 1 | 0 | 39014.5601 | 859 | 0 |  | 1288.5 | 1509.5 | 0.06105 | 0 | 52.442 | 0 | 0.0006105 | 0 | 0.52442 | 0 | 0.0006105 | 0.52442 | 250038 | 191.1967 | 250037.9994
39014.5623 | 48 | 0 | 39014.5623 | 2036 | 0 |  | 1473.5 | 1694.5 | 2.9304 | 0 | 124.2979 | 0 | 0.029304 | 0 | 1.243 | 0 | 0.029304 | 1.243 | 5111.2083 | 22.8576 | 5111.179
39014.5644 | 1058 | 0 | 39014.5644 | 1999 | 0 |  | 1658 | 1879 | 64.591 | 0 | 122.0391 | 0 | 0.64591 | 0 | 1.2204 | 0 | 0.64591 | 1.2204 | 136.4253 | 25.1316 | 135.7794
39014.5665 | 1739 | 0 | 39014.5665 | 2188 | 0 |  | 1842.5 | 2063.5 | 106.1661 | 0 | 133.5775 | 0 | 1.0617 | 0 | 1.3358 | 0 | 1.0617 | 1.3358 | 43.8401 | 14.3227 | 42.7785
39014.5687 | 2174 | 0 | 39014.5687 | 2485 | 0 |  | 2027.5 | 2248.5 | 132.7228 | 0 | 151.7094 | 0 | 1.3272 | 0 | 1.5171 | 0 | 1.3272 | 1.5171 | 15.0589 | 0.65915 | 13.7316
39014.5708 | 1765 | 0 | 39014.5708 | 1982 | 0 |  | 2212.5 | 2433.5 | 107.7534 | 0 | 121.0012 | 0 | 1.0775 | 0 | 1.21 | 0 | 1.0775 | 1.21 | 41.7212 | 26.2048 | 40.6437
39014.5729 | 1789 | 0 | 39014.573 | 2342 | 0 |  | 2397 | 2618 | 109.2186 | 0 | 142.9792 | 0 | 1.0922 | 0 | 1.4298 | 0 | 1.0922 | 1.4298 | 39.82 | 6.8053 | 38.7278
39014.5751 | 1836 | 0 | 39014.5751 | 2240 | 0 |  | 2582 | 2803 | 112.0879 | 0 | 136.7521 | 0 | 1.1209 | 0 | 1.3675 | 0 | 1.1209 | 1.3675 | 36.2407 | 11.6687 | 35.1199
39014.5772 | 1837 | 0 | 39014.5772 | 2255 | 0 |  | 2766.5 | 2987.5 | 112.149 | 0 | 137.6679 | 0 | 1.1215 | 0 | 1.3767 | 0 | 1.1215 | 1.3767 | 36.1666 | 10.9259 | 35.0451
39014.5794 | 1840 | 0 | 39014.5794 | 2399 | 0 |  | 2951.5 | 3172.5 | 112.3321 | 0 | 146.4591 | 0 | 1.1233 | 0 | 1.4646 | 0 | 1.1233 | 1.4646 | 35.9446 | 4.2676 | 34.8212

## A1-C6
Open Burn Test 2 |  |  | 2006-10-24 | 13:08 |  |  | Vs = |  | 144.2234 |  | R = | 100
XLPE | 7-C | Tray C | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 1 & 6 | Cable A | Odd - | Cable C |  | Even
Time-9 | N11 | N12 | Time-10 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R6-G | R1-6
39014.5428 | 1 | 0 | 39014.5428 | 1 | 0 |  | -209.5 | 11.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236138 | 236138 | 236137.9994
39014.5449 | 1 | 0 | 39014.5449 | 1 | 0 |  | -24.5 | 196.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236138 | 236138 | 236137.9994
39014.5471 | 1 | 0 | 39014.5471 | 1 | 0 |  | 160.5 | 381.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236138 | 236138 | 236137.9994
39014.5492 | 1 | 0 | 39014.5492 | 1 | 0 |  | 345 | 566 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236138 | 236138 | 236137.9994
39014.5513 | 1 | 0 | 39014.5514 | 1 | 0 |  | 530 | 751 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236138 | 236138 | 236137.9994
39014.5535 | 1 | 0 | 39014.5535 | 1 | 0 |  | 714.5 | 935.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236138 | 236138 | 236137.9994
39014.5556 | 1 | 0 | 39014.5556 | 1 | 0 |  | 899.5 | 1120.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236138 | 236138 | 236137.9994
39014.5577 | 1 | 0 | 39014.5578 | 1 | 0 |  | 1084 | 1305 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236138 | 236138 | 236137.9994
39014.5599 | 1 | 0 | 39014.5599 | 1 | 0 |  | 1269 | 1490 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236138 | 236138 | 236137.9994
39014.562 | 23 | 0 | 39014.562 | 233 | 0 |  | 1453.5 | 1674.5 | 1.4042 | 0 | 14.2247 | 0 | 0.014042 | 0 | 0.14225 | 0 | 0.014042 | 0.14225 | 10171.2174 | 913.897 | 10171.2033
39014.5642 | 1023 | 3 | 39014.5642 | 1949 | 3 |  | 1638.5 | 1859.5 | 62.4542 | 0.18315 | 118.9866 | 0.18315 | 0.62454 | 0.0018315 | 1.1899 | 0.0018315 | 0.62271 | 1.188 | 133.1532 | 21.2672 | 7812.2332
39014.5663 | 1798 | 0 | 39014.5663 | 2346 | 0 |  | 1823.5 | 2044.5 | 109.768 | 0 | 143.2234 | 0 | 1.0977 | 0 | 1.4322 | 0 | 1.0977 | 1.4322 | 31.3893 | 0.69821 | 30.2916
39014.5684 | 1715 | 0 | 39014.5685 | 2002 | 0 |  | 2008 | 2229 | 104.7009 | 0 | 122.2222 | 0 | 1.047 | 0 | 1.2222 | 0 | 1.047 | 1.2222 | 37.7481 | 18.001 | 36.7011
39014.5706 | 1751 | 0 | 39014.5706 | 1886 | 0 |  | 2192.5 | 2413.5 | 106.8987 | 0 | 115.1404 | 0 | 1.069 | 0 | 1.1514 | 0 | 1.069 | 1.1514 | 34.916 | 25.2587 | 33.8471
39014.5727 | 1907 | 0 | 39014.5727 | 1916 | 0 |  | 2377.5 | 2598.5 | 116.4225 | 0 | 116.9719 | 0 | 1.1642 | 0 | 1.1697 | 0 | 1.1642 | 1.1697 | 23.8794 | 23.2975 | 22.7152
39014.5749 | 1873 | 0 | 39014.5749 | 2069 | 0 |  | 2562.5 | 2783.5 | 114.3468 | 0 | 126.3126 | 0 | 1.1435 | 0 | 1.2631 | 0 | 1.1435 | 1.2631 | 26.1281 | 14.1798 | 24.9847
39014.577 | 2062 | 1 | 39014.577 | 2087 | 1 |  | 2747 | 2968 | 125.8852 | 0.06105 | 127.4115 | 0.06105 | 1.2589 | 0.0006105 | 1.2741 | 0.0006105 | 1.2582 | 1.2735 | 14.6281 | 13.2447 | 3501.4538
39014.5791 | 2202 | 7 | 39014.5792 | 1736 | 5 |  | 2932 | 3153 | 134.4322 | 0.42735 | 105.9829 | 0.30525 | 1.3443 | 0.0042735 | 1.0598 | 0.0030525 | 1.34 | 1.0568 | 7.369 | 37.6623 | 599.4633

## A1-C5
Open Burn Test 2 |  |  | 2006-10-24 | 13:08 |  |  | Vs = |  | 147.5812 |  | R = | 100
XLPE | 7-C | Tray C | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 1 & 5 | Cable A | Odd - | Cable C |  | Odd
Time-7 | N11 | N12 | Time-8 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R5-G | R1-5
39014.5427 | 1 | 0 | 39014.5428 | 1 | 0 |  | -212 | 9 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241638 | 241638 | 241637.9994
39014.5449 | 1 | 0 | 39014.5449 | 1 | 0 |  | -27.5 | 193.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241638 | 241638 | 241637.9994
39014.547 | 1 | 0 | 39014.547 | 1 | 0 |  | 157.5 | 378.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241638 | 241638 | 241637.9994
39014.5492 | 1 | 0 | 39014.5492 | 1 | 0 |  | 342 | 563 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241638 | 241638 | 241637.9994
39014.5513 | 1 | 0 | 39014.5513 | 1 | 0 |  | 527 | 748 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241638 | 241638 | 241637.9994
39014.5534 | 1 | 0 | 39014.5535 | 1 | 0 |  | 712 | 933 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241638 | 241638 | 241637.9994
39014.5556 | 1 | 0 | 39014.5556 | 1 | 0 |  | 896.5 | 1117.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241638 | 241638 | 241637.9994
39014.5577 | 1 | 0 | 39014.5577 | 1 | 0 |  | 1081.5 | 1302.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241638 | 241638 | 241637.9994
39014.5598 | 1 | 0 | 39014.5599 | 1 | 0 |  | 1266 | 1487 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241638 | 241638 | 241637.9994
39014.562 | 20 | 0 | 39014.562 | 219 | 0 |  | 1451 | 1672 | 1.221 | 0 | 13.37 | 0 | 0.01221 | 0 | 0.1337 | 0 | 0.01221 | 0.1337 | 11986.9 | 1003.8265 | 11986.8878
39014.5641 | 1171 | 4 | 39014.5641 | 1625 | 3 |  | 1635.5 | 1856.5 | 71.4896 | 0.2442 | 99.2063 | 0.18315 | 0.7149 | 0.002442 | 0.99206 | 0.0018315 | 0.71245 | 0.99023 | 107.5554 | 48.9362 | 10205.2667
39014.5663 | 1620 | 0 | 39014.5663 | 2151 | 0 |  | 1820.5 | 2041.5 | 98.9011 | 0 | 131.3187 | 0 | 0.98901 | 0 | 1.3132 | 0 | 0.98901 | 1.3132 | 49.221 | 12.384 | 48.232
39014.5684 | 2184 | 0 | 39014.5684 | 1949 | 0 |  | 2005 | 2226 | 133.3333 | 0 | 118.9866 | 0 | 1.3333 | 0 | 1.1899 | 0 | 1.3333 | 1.1899 | 10.6859 | 24.0318 | 9.3526
39014.5705 | 2077 | 0 | 39014.5706 | 2196 | 0 |  | 2190 | 2411 | 126.801 | 0 | 134.0659 | 0 | 1.268 | 0 | 1.3407 | 0 | 1.268 | 1.3407 | 16.3881 | 10.0811 | 15.12
39014.5727 | 2068 | 0 | 39014.5727 | 2401 | 0 |  | 2374.5 | 2595.5 | 126.2515 | 0 | 146.5812 | 0 | 1.2625 | 0 | 1.4658 | 0 | 1.2625 | 1.4658 | 16.8946 | 0.68222 | 15.6321
39014.5748 | 2112 | 0 | 39014.5748 | 2281 | 0 |  | 2559.5 | 2780.5 | 128.9377 | 0 | 139.2552 | 0 | 1.2894 | 0 | 1.3926 | 0 | 1.2894 | 1.3926 | 14.4593 | 5.979 | 13.1699
39014.577 | 1829 | 1 | 39014.577 | 2026 | 1 |  | 2744.5 | 2965.5 | 111.6606 | 0.06105 | 123.6874 | 0.06105 | 1.1166 | 0.0006105 | 1.2369 | 0.0006105 | 1.116 | 1.2363 | 32.2783 | 19.357 | 9525.9812
39014.5791 | 2210 | 6 | 39014.5791 | 2150 | 7 |  | 2929 | 3150 | 134.9206 | 0.3663 | 131.2576 | 0.42735 | 1.3492 | 0.003663 | 1.3126 | 0.0042735 | 1.3455 | 1.3083 | 9.6118 | 12.9158 | 383.9127

## A1-B4
Open Burn Test 2 |  |  | 2006-10-24 | 13:08 |  |  | Vs = |  | 153.9915 |  | R = | 100
XLPE | 7-C | Tray C | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 1 & 4 | Cable A | Odd - | Cable B |  | Even
Time-5 | N11 | N12 | Time-6 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R4-G | R1-4
39014.5427 | 1 | 0 | 39014.5427 | 1 | 0 |  | -215 | 6 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252138 | 252138 | 252137.9994
39014.5448 | 1 | 0 | 39014.5449 | 1 | 0 |  | -30 | 191 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252138 | 252138 | 252137.9994
39014.547 | 1 | 0 | 39014.547 | 1 | 0 |  | 154.5 | 375.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252138 | 252138 | 252137.9994
39014.5491 | 1 | 0 | 39014.5491 | 1 | 0 |  | 339.5 | 560.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252138 | 252138 | 252137.9994
39014.5513 | 1 | 0 | 39014.5513 | 1 | 0 |  | 524 | 745 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252138 | 252138 | 252137.9994
39014.5534 | 1 | 0 | 39014.5534 | 1 | 0 |  | 709 | 930 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252138 | 252138 | 252137.9994
39014.5555 | 1 | 0 | 39014.5556 | 1 | 0 |  | 893.5 | 1114.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252138 | 252138 | 252137.9994
39014.5577 | 1 | 0 | 39014.5577 | 1 | 0 |  | 1078.5 | 1299.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252138 | 252138 | 252137.9994
39014.5598 | 1 | 0 | 39014.5598 | 465 | 0 |  | 1263.5 | 1484.5 | 0.06105 | 0 | 28.3883 | 0 | 0.0006105 | 0 | 0.28388 | 0 | 0.0006105 | 0.28388 | 252138 | 442.4473 | 252137.9994
39014.562 | 9 | 0 | 39014.562 | 1920 | 0 |  | 1448 | 1669 | 0.54945 | 0 | 117.2161 | 0 | 0.0054945 | 0 | 1.1722 | 0 | 0.0054945 | 1.1722 | 27926.4444 | 31.374 | 27926.4389
39014.5641 | 1022 | 0 | 39014.5641 | 2340 | 0 |  | 1633 | 1854 | 62.3932 | 0 | 142.8571 | 0 | 0.62393 | 0 | 1.4286 | 0 | 0.62393 | 1.4286 | 146.8082 | 7.794 | 146.1843
39014.5662 | 1888 | 0 | 39014.5663 | 2036 | 0 |  | 1817.5 | 2038.5 | 115.2625 | 0 | 124.2979 | 0 | 1.1526 | 0 | 1.243 | 0 | 1.1526 | 1.243 | 33.6006 | 23.889 | 32.448
39014.5684 | 1909 | 0 | 39014.5684 | 2370 | 0 |  | 2002.5 | 2223.5 | 116.5446 | 0 | 144.6886 | 0 | 1.1654 | 0 | 1.4469 | 0 | 1.1654 | 1.4469 | 32.131 | 6.4295 | 30.9655
39014.5705 | 1990 | 0 | 39014.5705 | 2477 | 0 |  | 2187 | 2408 | 121.4896 | 0 | 151.221 | 0 | 1.2149 | 0 | 1.5122 | 0 | 1.2149 | 1.5122 | 26.7528 | 1.8321 | 25.5379
39014.5727 | 1771 | 0 | 39014.5727 | 2230 | 0 |  | 2372 | 2593 | 108.1197 | 0 | 136.1416 | 0 | 1.0812 | 0 | 1.3614 | 0 | 1.0812 | 1.3614 | 42.4269 | 13.1112 | 41.3457
39014.5748 | 1857 | 0 | 39014.5748 | 2506 | 0 |  | 2556.5 | 2777.5 | 113.37 | 0 | 152.9915 | 0 | 1.1337 | 0 | 1.5299 | 0 | 1.1337 | 1.5299 | 35.8309 | 0.65363 | 34.6972
39014.5769 | 1940 | 0 | 39014.5769 | 1920 | 0 |  | 2741.5 | 2962.5 | 118.4371 | 0 | 117.2161 | 0 | 1.1844 | 0 | 1.1722 | 0 | 1.1844 | 1.1722 | 30.0196 | 31.374 | 28.8352
39014.5791 | 1992 | 0 | 39014.5791 | 2278 | 0 |  | 2926.5 | 3147.5 | 121.6117 | 0 | 139.072 | 0 | 1.2161 | 0 | 1.3907 | 0 | 1.2161 | 1.3907 | 26.6255 | 10.7278 | 25.4094

## A1-B3
Open Burn Test 2 |  |  | 2006-10-24 | 13:08 |  |  | Vs = |  | 157.044 |  | R = | 100
XLPE | 7-C | Tray C | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 1 & 3 | Cable A | Odd - | Cable B |  | Odd
Time-3 | N11 | N12 | Time-4 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R3-G | R1-3
39014.5427 | 1 | 0 | 39014.5427 | 1 | 0 |  | -217.5 | 3.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257138 | 257138 | 257137.9994
39014.5448 | 1 | 0 | 39014.5448 | 1 | 0 |  | -33 | 188 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257138 | 257138 | 257137.9994
39014.547 | 1 | 0 | 39014.547 | 1 | 0 |  | 151.5 | 372.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257138 | 257138 | 257137.9994
39014.5491 | 1 | 0 | 39014.5491 | 1 | 0 |  | 336.5 | 557.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257138 | 257138 | 257137.9994
39014.5512 | 1 | 0 | 39014.5512 | 1 | 0 |  | 521.5 | 742.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257138 | 257138 | 257137.9994
39014.5534 | 1 | 0 | 39014.5534 | 1 | 0 |  | 706 | 927 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257138 | 257138 | 257137.9994
39014.5555 | 1 | 0 | 39014.5555 | 1 | 0 |  | 891 | 1112 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257138 | 257138 | 257137.9994
39014.5577 | 1 | 0 | 39014.5577 | 1 | 0 |  | 1075.5 | 1296.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257138 | 257138 | 257137.9994
39014.5598 | 2 | 0 | 39014.5598 | 464 | 0 |  | 1260.5 | 1481.5 | 0.1221 | 0 | 28.3272 | 0 | 0.001221 | 0 | 0.28327 | 0 | 0.001221 | 0.28327 | 128519 | 454.3922 | 128518.9988
39014.5619 | 6 | 0 | 39014.5619 | 2285 | 0 |  | 1445.5 | 1666.5 | 0.3663 | 0 | 139.4994 | 0 | 0.003663 | 0 | 1.395 | 0 | 0.003663 | 1.395 | 42773 | 12.5768 | 42772.9963
39014.5641 | 992 | 0 | 39014.5641 | 2152 | 0 |  | 1630 | 1851 | 60.5617 | 0 | 131.3797 | 0 | 0.60562 | 0 | 1.3138 | 0 | 0.60562 | 1.3138 | 159.3125 | 19.5344 | 158.7069
39014.5662 | 1928 | 0 | 39014.5662 | 2164 | 0 |  | 1815 | 2036 | 117.7045 | 0 | 132.1123 | 0 | 1.177 | 0 | 1.3211 | 0 | 1.177 | 1.3211 | 33.4222 | 18.8715 | 32.2452
39014.5683 | 2071 | 0 | 39014.5684 | 2556 | 0 |  | 1999.5 | 2220.5 | 126.4347 | 0 | 156.044 | 0 | 1.2643 | 0 | 1.5604 | 0 | 1.2643 | 1.5604 | 24.2096 | 0.64085 | 22.9452
39014.5705 | 1944 | 0 | 39014.5705 | 2535 | 0 |  | 2184.5 | 2405.5 | 118.6813 | 0 | 154.7619 | 0 | 1.1868 | 0 | 1.5476 | 0 | 1.1868 | 1.5476 | 32.3241 | 1.4746 | 31.1373
39014.5726 | 2112 | 0 | 39014.5726 | 2505 | 0 |  | 2369 | 2590 | 128.9377 | 0 | 152.9304 | 0 | 1.2894 | 0 | 1.5293 | 0 | 1.2894 | 1.5293 | 21.7983 | 2.6898 | 20.5089
39014.5748 | 2262 | 0 | 39014.5748 | 2036 | 0 |  | 2554 | 2775 | 138.0952 | 0 | 124.2979 | 0 | 1.381 | 0 | 1.243 | 0 | 1.381 | 1.243 | 13.7215 | 26.3448 | 12.3405
39014.5769 | 2206 | 0 | 39014.5769 | 1973 | 0 |  | 2738.5 | 2959.5 | 134.6764 | 0 | 120.4518 | 0 | 1.3468 | 0 | 1.2045 | 0 | 1.3468 | 1.2045 | 16.6083 | 30.3791 | 15.2616
39014.579 | 2176 | 0 | 39014.5791 | 1940 | 0 |  | 2923.5 | 3144.5 | 132.8449 | 0 | 118.4371 | 0 | 1.3284 | 0 | 1.1844 | 0 | 1.3284 | 1.1844 | 18.216 | 32.5969 | 16.8875

## A1-A2
Open Burn Test 2 |  |  | 2006-10-24 | 13:08 |  |  | Vs = |  | 141.6593 |  | R = | 100
XLPE | 7-C | Tray C | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 1 & 2 | Cable A | Odd-Even
Time-1 | N11 | N12 | Time-2 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R2-G | R1-2
39014.5427 | 1 | 0 | 39014.5427 | 1 | 0 |  | -220.5 | 0.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 231938 | 231938 | 231937.9994
39014.5448 | 1 | 0 | 39014.5448 | 1 | 0 |  | -35.5 | 185.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 231938 | 231938 | 231937.9994
39014.5469 | 1 | 0 | 39014.5469 | 1 | 0 |  | 149 | 370 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 231938 | 231938 | 231937.9994
39014.5491 | 1 | 0 | 39014.5491 | 1 | 0 |  | 333.5 | 554.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 231938 | 231938 | 231937.9994
39014.5512 | 1 | 0 | 39014.5512 | 1 | 0 |  | 518.5 | 739.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 231938 | 231938 | 231937.9994
39014.5533 | 1 | 0 | 39014.5534 | 1 | 0 |  | 703.5 | 924.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 231938 | 231938 | 231937.9994
39014.5555 | 1 | 0 | 39014.5555 | 1 | 0 |  | 888 | 1109 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 231938 | 231938 | 231937.9994
39014.5576 | 1 | 0 | 39014.5576 | 1 | 0 |  | 1073 | 1294 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 231938 | 231938 | 231937.9994
39014.5598 | 1106 | 1067 | 39014.5598 | 1149 | 1110 |  | 1257.5 | 1478.5 | 67.5214 | 65.1404 | 70.1465 | 67.7656 | 0.67521 | 0.6514 | 0.70147 | 0.67766 | 0.02381 | 0.02381 | 5849.6923 | 5849.6923 | 13.5804
39014.5619 | 1073 | 986 | 39014.5619 | 1178 | 1084 |  | 1442.5 | 1663.5 | 65.5067 | 60.1954 | 71.917 | 66.1783 | 0.65507 | 0.60195 | 0.71917 | 0.66178 | 0.053114 | 0.057387 | 5313.3638 | 1552.176 | 24.9046
39014.564 | 1360 | 734 | 39014.5641 | 1552 | 773 |  | 1627 | 1848 | 83.0281 | 44.8107 | 94.7497 | 47.1917 | 0.83028 | 0.44811 | 0.9475 | 0.47192 | 0.38217 | 0.47558 | 187.8768 | 639.2359 | 26.6698
39014.5662 | 1819 | 293 | 39014.5662 | 1762 | 309 |  | 1812 | 2033 | 111.0501 | 17.8877 | 107.5702 | 18.8645 | 1.1105 | 0.17888 | 1.0757 | 0.18864 | 0.93162 | 0.88706 | 44.4282 | 73.7139 | 30.1789
39014.5683 | 1976 | 170 | 39014.5683 | 1886 | 153 |  | 1996.5 | 2217.5 | 120.6349 | 10.3785 | 115.1404 | 9.3407 | 1.2063 | 0.10379 | 1.1514 | 0.093407 | 1.1026 | 1.058 | 25.2269 | 38.56 | 28.5461
39014.5705 | 1823 | 139 | 39014.5705 | 1983 | 154 |  | 2181.5 | 2402.5 | 111.2943 | 8.486 | 121.0623 | 9.4017 | 1.1129 | 0.08486 | 1.2106 | 0.094017 | 1.0281 | 1.1166 | 46.6366 | 22.5102 | 47.3736
39014.5726 | 2094 | 140 | 39014.5726 | 2021 | 134 |  | 2366.5 | 2587.5 | 127.8388 | 8.547 | 123.3822 | 8.1807 | 1.2784 | 0.08547 | 1.2338 | 0.081807 | 1.1929 | 1.152 | 15.2782 | 29.6436 | 14.108
39014.5747 | 2304 | 101 | 39014.5747 | 2200 | 104 |  | 2551 | 2772 | 140.6593 | 6.1661 | 134.3101 | 6.3492 | 1.4066 | 0.061661 | 1.3431 | 0.063492 | 1.3449 | 1.2796 | 15.9477 | 4.8089 | 3.8441
39014.5769 | 2216 | 139 | 39014.5769 | 2185 | 137 |  | 2736 | 2957 | 135.2869 | 8.486 | 133.3944 | 8.3639 | 1.3529 | 0.08486 | 1.3339 | 0.083639 | 1.268 | 1.2503 | 140.8372 | 6.94 | 1.6163
39014.579 | 2259 | 159 | 39014.579 | 1816 | 129 |  | 2920.5 | 3141.5 | 137.9121 | 9.707 | 110.8669 | 7.8755 | 1.3791 | 0.09707 | 1.1087 | 0.078755 | 1.2821 | 1.0299 | 1.3209 | 6.243 | 3.6078

## Temps
DAQ Time | Burner Time | Bundle center | Air above bundle | Air below bundle | Intra-bundle | TRAY C
0 | -221 | 17.5 | 17.4 | 17.3 | 18.2 | 18.8
1 | -220 | 17.5 | 17.4 | 17.3 | 18.2 | 18.8
2 | -219 | 17.5 | 17.4 | 17.3 | 18.2 | 18.8
3 | -218 | 17.5 | 17.4 | 17.3 | 18.2 | 18.7
4 | -217 | 17.5 | 17.4 | 17.3 | 18.2 | 18.8
5 | -216 | 17.5 | 17.4 | 17.3 | 18.2 | 18.8
6 | -215 | 17.5 | 17.4 | 17.3 | 18.2 | 18.8
7 | -214 | 17.5 | 17.4 | 17.3 | 18.2 | 18.8
8 | -213 | 17.5 | 17.4 | 17.3 | 18.2 | 18.8
9 | -212 | 17.5 | 17.4 | 17.3 | 18.2 | 18.7
10 | -211 | 17.5 | 17.4 | 17.3 | 18.2 | 18.7
11 | -210 | 17.5 | 17.4 | 17.3 | 18.2 | 18.7
12 | -209 | 17.5 | 17.4 | 17.3 | 18.2 | 18.7
13 | -208 | 17.5 | 17.4 | 17.3 | 18.2 | 18.8
14 | -207 | 17.5 | 17.4 | 17.3 | 18.2 | 18.7
15 | -206 | 17.5 | 17.4 | 17.3 | 18.2 | 18.8
16 | -205 | 17.5 | 17.4 | 17.3 | 18.2 | 18.7
17 | -204 | 17.5 | 17.4 | 17.3 | 18.2 | 18.8
18 | -203 | 17.5 | 17.4 | 17.3 | 18.2 | 18.7
19 | -202 | 17.5 | 17.4 | 17.3 | 18.2 | 18.8
20 | -201 | 17.5 | 17.4 | 17.3 | 18.2 | 18.7
21 | -200 | 17.5 | 17.4 | 17.3 | 18.2 | 18.8
22 | -199 | 17.5 | 17.4 | 17.3 | 18.2 | 18.8
23 | -198 | 17.5 | 17.4 | 17.3 | 18.2 | 18.8
24 | -197 | 17.5 | 17.4 | 17.3 | 18.2 | 18.8
25 | -196 | 17.5 | 17.4 | 17.3 | 18.2 | 18.7
26 | -195 | 17.5 | 17.4 | 17.3 | 18.2 | 18.7
27 | -194 | 17.5 | 17.4 | 17.3 | 18.2 | 18.7
28 | -193 | 17.5 | 17.4 | 17.3 | 18.2 | 18.7
29 | -192 | 17.5 | 17.4 | 17.3 | 18.2 | 18.7
30 | -191 | 17.5 | 17.4 | 17.3 | 18.2 | 18.7
31 | -190 | 17.5 | 17.4 | 17.3 | 18.2 | 18.7
32 | -189 | 17.5 | 17.4 | 17.3 | 18.2 | 18.8
33 | -188 | 17.5 | 17.4 | 17.3 | 18.2 | 18.7
34 | -187 | 17.5 | 17.4 | 17.3 | 18.2 | 18.7
35 | -186 | 17.5 | 17.4 | 17.3 | 18.2 | 18.8
36 | -185 | 17.5 | 17.4 | 17.3 | 18.2 | 18.8
37 | -184 | 17.5 | 17.4 | 17.3 | 18.2 | 18.7
38 | -183 | 17.5 | 17.4 | 17.3 | 18.2 | 18.7
39 | -182 | 17.5 | 17.4 | 17.3 | 18.2 | 18.8
40 | -181 | 17.5 | 17.4 | 17.3 | 18.2 | 18.7
41 | -180 | 17.5 | 17.4 | 17.3 | 18.2 | 18.7
42 | -179 | 17.5 | 17.4 | 17.3 | 18.2 | 18.7
43 | -178 | 17.5 | 17.4 | 17.3 | 18.2 | 18.8
44 | -177 | 17.5 | 17.4 | 17.3 | 18.2 | 18.7
45 | -176 | 17.5 | 17.4 | 17.3 | 18.2 | 18.7
46 | -175 | 17.5 | 17.4 | 17.3 | 18.2 | 18.7
47 | -174 | 17.5 | 17.4 | 17.3 | 18.2 | 18.7
48 | -173 | 17.5 | 17.4 | 17.3 | 18.2 | 18.7
49 | -172 | 17.5 | 17.4 | 17.3 | 18.2 | 18.8
50 | -171 | 17.5 | 17.4 | 17.3 | 18.2 | 18.7
51 | -170 | 17.5 | 17.4 | 17.3 | 18.2 | 18.7
52 | -169 | 17.5 | 17.4 | 17.3 | 18.2 | 18.7
53 | -168 | 17.5 | 17.5 | 17.3 | 18.2 | 18.7
54 | -167 | 17.5 | 17.4 | 17.3 | 18.2 | 18.8
55 | -166 | 17.5 | 17.5 | 17.3 | 18.2 | 18.7
56 | -165 | 17.5 | 17.5 | 17.3 | 18.2 | 18.7
57 | -164 | 17.5 | 17.4 | 17.2 | 18.2 | 18.7
58 | -163 | 17.5 | 17.5 | 17.2 | 18.2 | 18.8
59 | -162 | 17.5 | 17.4 | 17.2 | 18.2 | 18.7
60 | -161 | 17.5 | 17.4 | 17.2 | 18.2 | 18.7
61 | -160 | 17.5 | 17.4 | 17.2 | 18.2 | 18.7
62 | -159 | 17.5 | 17.4 | 17.2 | 18.2 | 18.7
63 | -158 | 17.5 | 17.5 | 17.2 | 18.2 | 18.7
64 | -157 | 17.5 | 17.5 | 17.2 | 18.2 | 18.7
65 | -156 | 17.5 | 17.4 | 17.2 | 18.2 | 18.7
66 | -155 | 17.5 | 17.5 | 17.2 | 18.2 | 18.7
67 | -154 | 17.5 | 17.4 | 17.2 | 18.2 | 18.7
68 | -153 | 17.5 | 17.4 | 17.2 | 18.2 | 18.7
69 | -152 | 17.5 | 17.4 | 17.2 | 18.2 | 18.7
70 | -151 | 17.5 | 17.4 | 17.2 | 18.2 | 18.7
71 | -150 | 17.5 | 17.4 | 17.2 | 18.2 | 18.7
72 | -149 | 17.5 | 17.4 | 17.2 | 18.2 | 18.7
73 | -148 | 17.5 | 17.4 | 17.2 | 18.2 | 18.7
74 | -147 | 17.5 | 17.4 | 17.2 | 18.2 | 18.7
75 | -146 | 17.5 | 17.4 | 17.2 | 18.2 | 18.7
76 | -145 | 17.5 | 17.4 | 17.2 | 18.2 | 18.7
77 | -144 | 17.5 | 17.4 | 17.2 | 18.2 | 18.7
78 | -143 | 17.5 | 17.4 | 17.2 | 18.2 | 18.7
79 | -142 | 17.5 | 17.4 | 17.2 | 18.2 | 18.7
80 | -141 | 17.5 | 17.4 | 17.2 | 18.2 | 18.7
81 | -140 | 17.5 | 17.4 | 17.2 | 18.2 | 18.7
82 | -139 | 17.5 | 17.4 | 17.3 | 18.2 | 18.7
83 | -138 | 17.5 | 17.4 | 17.3 | 18.2 | 18.7
84 | -137 | 17.5 | 17.4 | 17.2 | 18.2 | 18.7
85 | -136 | 17.5 | 17.4 | 17.3 | 18.2 | 18.8
86 | -135 | 17.5 | 17.4 | 17.3 | 18.2 | 18.7
87 | -134 | 17.5 | 17.4 | 17.3 | 18.2 | 18.7
88 | -133 | 17.5 | 17.4 | 17.3 | 18.2 | 18.7
89 | -132 | 17.5 | 17.4 | 17.3 | 18.2 | 18.8
90 | -131 | 17.5 | 17.4 | 17.2 | 18.2 | 18.7
91 | -130 | 17.5 | 17.4 | 17.2 | 18.2 | 18.7
92 | -129 | 17.5 | 17.4 | 17.2 | 18.2 | 18.7
93 | -128 | 17.5 | 17.4 | 17.3 | 18.2 | 18.7
94 | -127 | 17.5 | 17.4 | 17.2 | 18.2 | 18.8
95 | -126 | 17.5 | 17.4 | 17.2 | 18.2 | 18.7
96 | -125 | 17.5 | 17.4 | 17.2 | 18.2 | 18.7
97 | -124 | 17.5 | 17.4 | 17.2 | 18.2 | 18.8
98 | -123 | 17.5 | 17.4 | 17.2 | 18.2 | 18.7
99 | -122 | 17.5 | 17.4 | 17.2 | 18.2 | 18.7
100 | -121 | 17.5 | 17.4 | 17.2 | 18.2 | 18.7
101 | -120 | 17.5 | 17.4 | 17.2 | 18.2 | 18.7
102 | -119 | 17.5 | 17.4 | 17.2 | 18.2 | 18.7
103 | -118 | 17.5 | 17.4 | 17.2 | 18.2 | 18.7
104 | -117 | 17.5 | 17.4 | 17.2 | 18.2 | 18.7
105 | -116 | 17.5 | 17.4 | 17.2 | 18.2 | 18.7
106 | -115 | 17.5 | 17.4 | 17.2 | 18.2 | 18.7
107 | -114 | 17.5 | 17.4 | 17.2 | 18.2 | 18.7
108 | -113 | 17.5 | 17.4 | 17.2 | 18.2 | 18.7
109 | -112 | 17.5 | 17.4 | 17.2 | 18.2 | 18.7
110 | -111 | 17.5 | 17.4 | 17.2 | 18.2 | 18.7
111 | -110 | 17.5 | 17.4 | 17.2 | 18.2 | 18.7
112 | -109 | 17.5 | 17.4 | 17.2 | 18.2 | 18.7
113 | -108 | 17.5 | 17.4 | 17.2 | 18.2 | 18.7
114 | -107 | 17.5 | 17.4 | 17.2 | 18.2 | 18.7
115 | -106 | 17.5 | 17.4 | 17.2 | 18.1 | 18.7
116 | -105 | 17.5 | 17.4 | 17.2 | 18.1 | 18.7
117 | -104 | 17.5 | 17.4 | 17.2 | 18.2 | 18.7
118 | -103 | 17.5 | 17.4 | 17.2 | 18.2 | 18.7
119 | -102 | 17.5 | 17.4 | 17.2 | 18.2 | 18.7
120 | -101 | 17.5 | 17.4 | 17.2 | 18.2 | 18.7
121 | -100 | 17.5 | 17.4 | 17.2 | 18.2 | 18.7
122 | -99 | 17.5 | 17.4 | 17.2 | 18.2 | 18.7
123 | -98 | 17.5 | 17.4 | 17.2 | 18.2 | 18.7
124 | -97 | 17.5 | 17.4 | 17.2 | 18.2 | 18.7
125 | -96 | 17.5 | 17.4 | 17.2 | 18.2 | 18.7
126 | -95 | 17.5 | 17.4 | 17.2 | 18.2 | 18.7
127 | -94 | 17.5 | 17.4 | 17.2 | 18.2 | 18.7
128 | -93 | 17.5 | 17.4 | 17.2 | 18.2 | 18.7
129 | -92 | 17.5 | 17.4 | 17.2 | 18.2 | 18.7
130 | -91 | 17.5 | 17.4 | 17.2 | 18.2 | 18.7
131 | -90 | 17.5 | 17.4 | 17.2 | 18.1 | 18.7
132 | -89 | 17.5 | 17.4 | 17.2 | 18.2 | 18.7
133 | -88 | 17.5 | 17.4 | 17.2 | 18.2 | 18.7
134 | -87 | 17.5 | 17.4 | 17.2 | 18.2 | 18.7
135 | -86 | 17.5 | 17.4 | 17.2 | 18.2 | 18.7
136 | -85 | 17.5 | 17.4 | 17.2 | 18.2 | 18.7
137 | -84 | 17.5 | 17.4 | 17.2 | 18.2 | 18.7
138 | -83 | 17.5 | 17.4 | 17.2 | 18.2 | 18.7
139 | -82 | 17.5 | 17.4 | 17.2 | 18.2 | 18.7
140 | -81 | 17.5 | 17.4 | 17.2 | 18.2 | 18.7
141 | -80 | 17.5 | 17.4 | 17.2 | 18.2 | 18.7
142 | -79 | 17.5 | 17.4 | 17.2 | 18.2 | 18.7
143 | -78 | 17.5 | 17.4 | 17.2 | 18.2 | 18.7
144 | -77 | 17.5 | 17.4 | 17.2 | 18.2 | 18.7
145 | -76 | 17.5 | 17.4 | 17.2 | 18.2 | 18.7
146 | -75 | 17.5 | 17.4 | 17.2 | 18.2 | 18.7
147 | -74 | 17.5 | 17.4 | 17.2 | 18.2 | 18.7
148 | -73 | 17.5 | 17.4 | 17.2 | 18.2 | 18.7
149 | -72 | 17.5 | 17.4 | 17.2 | 18.2 | 18.7
150 | -71 | 17.5 | 17.4 | 17.2 | 18.2 | 18.7
151 | -70 | 17.5 | 17.4 | 17.2 | 18.2 | 18.7
152 | -69 | 17.5 | 17.4 | 17.2 | 18.2 | 18.7
153 | -68 | 17.5 | 17.4 | 17.2 | 18.2 | 18.7
154 | -67 | 17.5 | 17.4 | 17.2 | 18.1 | 18.7
155 | -66 | 17.5 | 17.4 | 17.2 | 18.2 | 18.7
156 | -65 | 17.5 | 17.4 | 17.2 | 18.2 | 18.7
157 | -64 | 17.5 | 17.3 | 17.2 | 18.2 | 18.7
158 | -63 | 17.5 | 17.3 | 17.2 | 18.1 | 18.7
159 | -62 | 17.5 | 17.3 | 17.2 | 18.1 | 18.7
160 | -61 | 17.5 | 17.3 | 17.2 | 18.1 | 18.7
161 | -60 | 17.5 | 17.3 | 17.2 | 18.1 | 18.7
162 | -59 | 17.5 | 17.3 | 17.1 | 18.1 | 18.7
163 | -58 | 17.5 | 17.3 | 17.2 | 18.1 | 18.7
164 | -57 | 17.5 | 17.3 | 17.2 | 18.1 | 18.7
165 | -56 | 17.5 | 17.3 | 17.2 | 18.1 | 18.7
166 | -55 | 17.5 | 17.3 | 17.2 | 18.1 | 18.7
167 | -54 | 17.5 | 17.3 | 17.2 | 18.1 | 18.7
168 | -53 | 17.5 | 17.3 | 17.2 | 18.1 | 18.7
169 | -52 | 17.5 | 17.3 | 17.2 | 18.1 | 18.7
170 | -51 | 17.5 | 17.3 | 17.2 | 18.1 | 18.7
171 | -50 | 17.5 | 17.3 | 17.2 | 18.1 | 18.7
172 | -49 | 17.5 | 17.3 | 17.2 | 18.1 | 18.7
173 | -48 | 17.5 | 17.3 | 17.2 | 18.2 | 18.7
174 | -47 | 17.5 | 17.3 | 17.2 | 18.1 | 18.7
175 | -46 | 17.5 | 17.3 | 17.2 | 18.2 | 18.7
176 | -45 | 17.5 | 17.3 | 17.2 | 18.2 | 18.7
177 | -44 | 17.5 | 17.3 | 17.2 | 18.2 | 18.7
178 | -43 | 17.5 | 17.3 | 17.2 | 18.1 | 18.7
179 | -42 | 17.5 | 17.3 | 17.2 | 18.1 | 18.7
180 | -41 | 17.5 | 17.3 | 17.2 | 18.2 | 18.7
181 | -40 | 17.5 | 17.3 | 17.2 | 18.2 | 18.7
182 | -39 | 17.5 | 17.3 | 17.2 | 18.1 | 18.7
183 | -38 | 17.5 | 17.3 | 17.2 | 18.1 | 18.7
184 | -37 | 17.5 | 17.3 | 17.2 | 18.2 | 18.7
185 | -36 | 17.5 | 17.3 | 17.2 | 18.1 | 18.7
186 | -35 | 17.5 | 17.3 | 17.2 | 18.1 | 18.7
187 | -34 | 17.5 | 17.3 | 17.2 | 18.2 | 18.7
188 | -33 | 17.5 | 17.3 | 17.2 | 18.2 | 18.7
189 | -32 | 17.5 | 17.3 | 17.2 | 18.2 | 18.7
190 | -31 | 17.5 | 17.3 | 17.2 | 18.2 | 18.7
191 | -30 | 17.5 | 17.3 | 17.2 | 18.1 | 18.7
192 | -29 | 17.5 | 17.3 | 17.2 | 18.1 | 18.7
193 | -28 | 17.5 | 17.3 | 17.2 | 18.1 | 18.7
194 | -27 | 17.5 | 17.3 | 17.2 | 18.1 | 18.7
195 | -26 | 17.5 | 17.3 | 17.2 | 18.1 | 18.7
196 | -25 | 17.5 | 17.3 | 17.2 | 18.1 | 18.7
197 | -24 | 17.5 | 17.3 | 17.2 | 18.1 | 18.7
198 | -23 | 17.5 | 17.3 | 17.2 | 18.1 | 18.7
199 | -22 | 17.5 | 17.3 | 17.2 | 18.1 | 18.7
200 | -21 | 17.5 | 17.3 | 17.2 | 18.1 | 18.7
201 | -20 | 17.5 | 17.3 | 17.2 | 18.1 | 18.7
202 | -19 | 17.5 | 17.3 | 17.2 | 18.1 | 18.7
203 | -18 | 17.5 | 17.3 | 17.2 | 18.1 | 18.7
204 | -17 | 17.5 | 17.3 | 17.2 | 18.1 | 18.7
205 | -16 | 17.5 | 17.3 | 17.2 | 18.1 | 18.7
206 | -15 | 17.5 | 17.3 | 17.2 | 18.1 | 18.7
207 | -14 | 17.5 | 17.3 | 17.2 | 18.2 | 18.7
208 | -13 | 17.5 | 17.3 | 17.2 | 18.1 | 18.7
209 | -12 | 17.5 | 17.3 | 17.2 | 18.1 | 18.7
210 | -11 | 17.5 | 17.3 | 17.2 | 18.1 | 18.7
211 | -10 | 17.5 | 17.3 | 17.2 | 18.1 | 18.7
212 | -9 | 17.5 | 17.3 | 17.2 | 18.1 | 18.7
213 | -8 | 17.5 | 17.3 | 17.2 | 18.1 | 18.7
214 | -7 | 17.5 | 17.3 | 17.2 | 18.1 | 18.7
215 | -6 | 17.5 | 17.3 | 17.2 | 18.1 | 18.7
216 | -5 | 17.5 | 17.3 | 17.2 | 18.1 | 18.7
217 | -4 | 17.5 | 17.4 | 17.2 | 18.1 | 18.7
218 | -3 | 17.5 | 17.4 | 17.2 | 18.1 | 18.7
219 | -2 | 17.5 | 17.4 | 17.2 | 18.1 | 18.7
220 | -1 | 17.5 | 17.4 | 17.2 | 18.1 | 18.7
221 | 0 | 17.5 | 17.4 | 17.2 | 18.1 | 18.7
222 | 1 | 17.5 | 17.4 | 17.2 | 18.1 | 18.7
223 | 2 | 17.5 | 17.4 | 17.2 | 18.1 | 18.7
224 | 3 | 17.5 | 17.4 | 17.2 | 18.1 | 18.7
225 | 4 | 17.5 | 17.4 | 17.2 | 18.1 | 18.7
226 | 5 | 17.5 | 17.4 | 17.3 | 18.2 | 18.8
227 | 6 | 17.5 | 18.6 | 21.5 | 18.2 | 19.3
228 | 7 | 17.5 | 23.1 | 30.1 | 18.2 | 20.3
229 | 8 | 17.5 | 30.8 | 44.5 | 18.2 | 21.7
230 | 9 | 17.5 | 43.4 | 63.5 | 18.2 | 23.7
231 | 10 | 17.6 | 55.4 | 79.8 | 18.2 | 26.3
232 | 11 | 17.6 | 72.2 | 107.8 | 18.2 | 31
233 | 12 | 17.7 | 96.9 | 138.2 | 18.2 | 39.2
234 | 13 | 17.8 | 125 | 178.3 | 18.2 | 43.1
235 | 14 | 18 | 143.4 | 202.5 | 18.2 | 46.7
236 | 15 | 18.1 | 156.8 | 222.8 | 18.2 | 49.6
237 | 16 | 18.4 | 167 | 233.3 | 18.2 | 53.1
238 | 17 | 18.7 | 181.4 | 255.3 | 18.3 | 55.5
239 | 18 | 18.9 | 195 | 271.3 | 18.3 | 61.5
240 | 19 | 19.2 | 209 | 296 | 18.3 | 67.2
241 | 20 | 19.6 | 226.7 | 324.7 | 18.3 | 73.3
242 | 21 | 19.9 | 243.8 | 353.1 | 18.3 | 79
243 | 22 | 20.2 | 262.2 | 382.7 | 18.3 | 85.2
244 | 23 | 20.6 | 275.4 | 405.9 | 18.3 | 90.5
245 | 24 | 21 | 286.9 | 426.9 | 18.3 | 98.2
246 | 25 | 21.4 | 302.3 | 446.5 | 18.4 | 103.8
247 | 26 | 21.8 | 310.6 | 447.8 | 18.4 | 108.1
248 | 27 | 22.3 | 314.5 | 454.7 | 18.4 | 111.7
249 | 28 | 22.7 | 319.7 | 458.5 | 18.5 | 117.4
250 | 29 | 23.1 | 330.3 | 467.7 | 18.5 | 123.1
251 | 30 | 23.4 | 334.4 | 480.7 | 18.5 | 128.6
252 | 31 | 23.7 | 336.1 | 466.1 | 18.5 | 133.2
253 | 32 | 24 | 337.6 | 459.2 | 18.6 | 135.9
254 | 33 | 24.3 | 342.7 | 457.9 | 18.8 | 139.6
255 | 34 | 24.6 | 346.3 | 461.5 | 19 | 142.5
256 | 35 | 24.8 | 355.1 | 472.5 | 19.2 | 148.4
257 | 36 | 25.1 | 359.4 | 471.1 | 19.4 | 154.6
258 | 37 | 25.4 | 358.7 | 466.3 | 19.7 | 157.5
259 | 38 | 25.7 | 360.7 | 472.2 | 19.9 | 160.7
260 | 39 | 26 | 366.3 | 488.6 | 20.2 | 164.5
261 | 40 | 26.3 | 369.7 | 500.8 | 20.5 | 168.7
262 | 41 | 26.7 | 370.3 | 509.6 | 20.9 | 171.5
263 | 42 | 27 | 370.5 | 514 | 21.3 | 174.6
264 | 43 | 27.4 | 373.7 | 529.3 | 21.8 | 181.8
265 | 44 | 27.9 | 376.3 | 531.1 | 22.3 | 184.9
266 | 45 | 28.3 | 377.3 | 530.6 | 22.9 | 187.2
267 | 46 | 28.7 | 380.3 | 543.3 | 23.6 | 190.5
268 | 47 | 29.2 | 380.7 | 541 | 24.2 | 193.2
269 | 48 | 29.7 | 383.6 | 547.1 | 25 | 196.8
270 | 49 | 30.2 | 389.4 | 552.8 | 26 | 201.5
271 | 50 | 30.7 | 389 | 552.5 | 27 | 206.5
272 | 51 | 31.3 | 389.1 | 542.7 | 28.1 | 210.3
273 | 52 | 31.8 | 390.5 | 543.8 | 29.3 | 214.3
274 | 53 | 32.4 | 397.7 | 552.6 | 30.7 | 220.1
275 | 54 | 33 | 399.6 | 552.8 | 31.9 | 224.2
276 | 55 | 33.6 | 400.7 | 552.7 | 33 | 229.9
277 | 56 | 34.3 | 400.7 | 549 | 34.2 | 233.6
278 | 57 | 34.9 | 397.1 | 550.3 | 35.1 | 234.6
279 | 58 | 35.6 | 396.4 | 543.3 | 36 | 236.8
280 | 59 | 36.3 | 390.8 | 522.7 | 36.9 | 238.1
281 | 60 | 36.9 | 384.5 | 504.3 | 37.4 | 238
282 | 61 | 37.6 | 377.8 | 487.7 | 38.1 | 238.1
283 | 62 | 38.3 | 372.6 | 486.8 | 38.8 | 239.1
284 | 63 | 39 | 373.8 | 505.8 | 39.6 | 241.9
285 | 64 | 39.6 | 377.5 | 529.4 | 40.3 | 246.6
286 | 65 | 40.3 | 377.1 | 534.1 | 40.8 | 249.3
287 | 66 | 41 | 376.7 | 523.4 | 41.4 | 251.2
288 | 67 | 41.6 | 378.5 | 521.7 | 42 | 253.6
289 | 68 | 42.3 | 375.9 | 520.3 | 42.5 | 254.3
290 | 69 | 43 | 371.5 | 502.8 | 42.9 | 255
291 | 70 | 43.7 | 364.7 | 488.1 | 43.1 | 253.6
292 | 71 | 44.4 | 361.8 | 480.4 | 43.4 | 254.2
293 | 72 | 45 | 360.5 | 479.9 | 43.6 | 255.4
294 | 73 | 45.7 | 363.1 | 485.4 | 44.1 | 258.7
295 | 74 | 46.3 | 361.8 | 485.2 | 44.5 | 262
296 | 75 | 47 | 360.7 | 480.8 | 44.9 | 262.9
297 | 76 | 47.6 | 359.6 | 474.4 | 45.3 | 265.1
298 | 77 | 48.2 | 357.7 | 478.7 | 45.8 | 266.3
299 | 78 | 48.8 | 358.3 | 473.3 | 46.2 | 268.6
300 | 79 | 49.4 | 358.9 | 467.4 | 46.7 | 272
301 | 80 | 50 | 360.8 | 479.5 | 47.4 | 276.4
302 | 81 | 50.6 | 365 | 492.8 | 48.1 | 279.9
303 | 82 | 51.2 | 376.5 | 497.1 | 48.9 | 283.3
304 | 83 | 51.7 | 381.9 | 492.1 | 49.4 | 284.5
305 | 84 | 52.3 | 379.9 | 481.5 | 49.8 | 286
306 | 85 | 52.9 | 373.3 | 467 | 50 | 286.8
307 | 86 | 53.4 | 367.3 | 456.7 | 50.1 | 286.4
308 | 87 | 54 | 363.7 | 461.8 | 50.1 | 288.2
309 | 88 | 54.6 | 362.9 | 467.8 | 50.3 | 293.1
310 | 89 | 55.1 | 366.6 | 486.3 | 50.5 | 297.9
311 | 90 | 55.7 | 371.2 | 488.2 | 50.8 | 303
312 | 91 | 56.3 | 370.9 | 485.2 | 51 | 307.2
313 | 92 | 56.8 | 370.5 | 487.9 | 51.2 | 309.5
314 | 93 | 57.4 | 369.6 | 487.4 | 51.3 | 313
315 | 94 | 58 | 368.8 | 492.3 | 51.4 | 315.1
316 | 95 | 58.6 | 369.5 | 495.8 | 51.6 | 316.9
317 | 96 | 59.3 | 367.5 | 488 | 51.6 | 316.5
318 | 97 | 59.9 | 366.3 | 489 | 51.7 | 316.3
319 | 98 | 60.6 | 369.4 | 489.5 | 51.9 | 318
320 | 99 | 61.3 | 369.6 | 483.9 | 52.1 | 319.1
321 | 100 | 62 | 373.6 | 489.9 | 52.4 | 321.6
322 | 101 | 62.8 | 378.2 | 501.6 | 52.6 | 324.4
323 | 102 | 63.5 | 380.1 | 504.6 | 52.9 | 325.4
324 | 103 | 64.4 | 379.8 | 511.9 | 53 | 325.7
325 | 104 | 65.3 | 383 | 519.6 | 53.2 | 328.9
326 | 105 | 66.3 | 382 | 505.8 | 53.4 | 329.9
327 | 106 | 67.6 | 381.1 | 501.3 | 53.7 | 330.9
328 | 107 | 69.2 | 381.2 | 505.5 | 53.9 | 331.8
329 | 108 | 71.1 | 380.4 | 506.9 | 54 | 333.2
330 | 109 | 73.4 | 379.2 | 498.6 | 54.2 | 333.8
331 | 110 | 75.8 | 376.7 | 488.4 | 54.4 | 334.9
332 | 111 | 78.7 | 376.2 | 489.2 | 54.6 | 336.5
333 | 112 | 81.2 | 377 | 487.8 | 54.8 | 338.4
334 | 113 | 83 | 374.1 | 478.5 | 55 | 337.4
335 | 114 | 84.2 | 370.8 | 477.6 | 55.1 | 337.8
336 | 115 | 85 | 368.8 | 477.9 | 55.2 | 339.2
337 | 116 | 85.4 | 369 | 482.4 | 55.3 | 340.8
338 | 117 | 85.6 | 367.2 | 475.2 | 55.6 | 341.1
339 | 118 | 86 | 364.9 | 474.2 | 55.9 | 342.7
340 | 119 | 86.2 | 363 | 468.6 | 56.2 | 344.3
341 | 120 | 86.3 | 362.7 | 467.8 | 56.5 | 344.8
342 | 121 | 86.4 | 367.2 | 476.4 | 56.8 | 345.7
343 | 122 | 86.6 | 371.3 | 488.3 | 57.2 | 348.1
344 | 123 | 87.1 | 375.6 | 500.1 | 57.7 | 350.8
345 | 124 | 88.1 | 379.8 | 517.7 | 58.2 | 352.9
346 | 125 | 89.8 | 382.2 | 518.3 | 58.7 | 354.8
347 | 126 | 91.2 | 393.6 | 535.2 | 59.3 | 358.9
348 | 127 | 92.4 | 400.4 | 550.7 | 59.9 | 361.9
349 | 128 | 93.6 | 414.2 | 557.9 | 60.6 | 365.8
350 | 129 | 94.7 | 415.4 | 554.7 | 61.1 | 366.1
351 | 130 | 95.5 | 420.8 | 557.9 | 61.3 | 366.9
352 | 131 | 96.2 | 420.8 | 559.1 | 61.5 | 367.9
353 | 132 | 96.8 | 423.9 | 568.5 | 61.7 | 368.9
354 | 133 | 97.2 | 422.1 | 560.1 | 62 | 370.7
355 | 134 | 97.4 | 423 | 549.8 | 62.2 | 373.3
356 | 135 | 97.5 | 426.2 | 557.8 | 62.6 | 376.2
357 | 136 | 97.5 | 428.6 | 566.3 | 63 | 379.9
358 | 137 | 97.4 | 437 | 575.1 | 63.6 | 383.2
359 | 138 | 97.2 | 441.1 | 583 | 64.3 | 386.4
360 | 139 | 97.1 | 448.9 | 590.1 | 64.9 | 389.3
361 | 140 | 96.9 | 454.8 | 585.7 | 65.7 | 389.7
362 | 141 | 96.9 | 454.6 | 587.4 | 66.1 | 391.4
363 | 142 | 96.8 | 455.3 | 586.5 | 66.4 | 393.1
364 | 143 | 96.7 | 454.5 | 578.7 | 66.6 | 393.6
365 | 144 | 96.6 | 449.1 | 567.9 | 67 | 394.3
366 | 145 | 96.5 | 442.6 | 556.4 | 67.2 | 395
367 | 146 | 96.4 | 435.7 | 538.8 | 67.3 | 394.1
368 | 147 | 96.5 | 425.2 | 519.8 | 67.4 | 392.4
369 | 148 | 96.6 | 416.2 | 502 | 67.6 | 391.1
370 | 149 | 96.6 | 407.6 | 494.3 | 67.6 | 391.3
371 | 150 | 96.6 | 401.9 | 491.5 | 67.6 | 390.6
372 | 151 | 96.7 | 397.3 | 491.1 | 67.6 | 389.9
373 | 152 | 96.8 | 394.7 | 483.4 | 67.9 | 389.3
374 | 153 | 96.9 | 390.9 | 485.4 | 68.2 | 388.3
375 | 154 | 97.2 | 387.6 | 483.6 | 68.3 | 387.8
376 | 155 | 97.5 | 384.1 | 479.3 | 68.4 | 386.4
377 | 156 | 97.7 | 381.9 | 487.4 | 68.5 | 386.1
378 | 157 | 97.9 | 382.7 | 503.2 | 68.7 | 385.8
379 | 158 | 98.1 | 383.6 | 508.1 | 69 | 386.3
380 | 159 | 98.3 | 384 | 512.8 | 69.3 | 386.4
381 | 160 | 98.5 | 387.1 | 528.4 | 69.6 | 388.8
382 | 161 | 98.6 | 388.4 | 532.3 | 70.1 | 390.7
383 | 162 | 98.7 | 396.4 | 538.4 | 70.5 | 392.2
384 | 163 | 98.8 | 399.7 | 532.6 | 71 | 393.4
385 | 164 | 99 | 400.2 | 529.7 | 71.4 | 394.4
386 | 165 | 99.2 | 400.2 | 527.3 | 72.1 | 395.9
387 | 166 | 99.4 | 399.1 | 519.1 | 72.6 | 397.4
388 | 167 | 99.7 | 397.6 | 513.1 | 73.2 | 397.9
389 | 168 | 99.9 | 397.5 | 513.5 | 73.9 | 399.8
390 | 169 | 100.1 | 398.8 | 515.5 | 74.6 | 401
391 | 170 | 100.3 | 399.1 | 522 | 75.6 | 402.4
392 | 171 | 100.5 | 400.5 | 528.8 | 76.6 | 403.7
393 | 172 | 100.8 | 397.2 | 520.3 | 77.4 | 402.6
394 | 173 | 101.1 | 403.9 | 545.4 | 78.7 | 406.5
395 | 174 | 101.3 | 405.4 | 544.9 | 79.9 | 410.3
396 | 175 | 101.6 | 402.6 | 540.5 | 81.2 | 409.8
397 | 176 | 101.9 | 399.6 | 527 | 82.4 | 409.9
398 | 177 | 102.1 | 399 | 521.3 | 83.8 | 410.1
399 | 178 | 102.4 | 399 | 516.3 | 85 | 409.9
400 | 179 | 102.7 | 397.4 | 507.6 | 86 | 409.4
401 | 180 | 102.9 | 395.3 | 505.3 | 87.4 | 409.2
402 | 181 | 103.3 | 393.5 | 508.7 | 88.7 | 409.9
403 | 182 | 103.7 | 392.3 | 511.6 | 90.9 | 412.1
404 | 183 | 104.1 | 395 | 521.9 | 93.9 | 415.2
405 | 184 | 104.6 | 404.1 | 537.2 | 96.5 | 418.2
406 | 185 | 105 | 406.4 | 547.8 | 98.5 | 418.6
407 | 186 | 105.5 | 404.7 | 542.6 | 100.1 | 418.2
408 | 187 | 106 | 404.3 | 544.4 | 102 | 418.9
409 | 188 | 106.6 | 410.1 | 548.5 | 104.3 | 420.7
410 | 189 | 107.1 | 408.9 | 544.9 | 106.1 | 420.8
411 | 190 | 107.6 | 409 | 553.3 | 107.6 | 421.7
412 | 191 | 108 | 413.1 | 561.4 | 109.1 | 423.2
413 | 192 | 108.5 | 409.9 | 543.2 | 110.8 | 422.2
414 | 193 | 108.9 | 403.2 | 528.1 | 111.7 | 421
415 | 194 | 109.2 | 398.7 | 515.3 | 112.6 | 419.6
416 | 195 | 109.6 | 397.5 | 514 | 114 | 419.3
417 | 196 | 110 | 398.9 | 512.2 | 116.4 | 420.1
418 | 197 | 110.5 | 400.8 | 515.4 | 118.1 | 420
419 | 198 | 110.8 | 403.7 | 518.9 | 119.2 | 420.1
420 | 199 | 111.2 | 402.4 | 522 | 120.2 | 420.7
421 | 200 | 111.7 | 405.5 | 535.3 | 121.9 | 422.9
422 | 201 | 112.1 | 410.4 | 548.8 | 124.1 | 425.7
423 | 202 | 112.6 | 410 | 543.8 | 125.8 | 426.5
424 | 203 | 113.1 | 409.1 | 542.5 | 127.8 | 428.5
425 | 204 | 113.5 | 408.3 | 541.7 | 130.1 | 431.9
426 | 205 | 114 | 407 | 533.6 | 132.5 | 433.9
427 | 206 | 114.4 | 404.7 | 524.5 | 134.6 | 434.6
428 | 207 | 114.9 | 404.6 | 521 | 137.1 | 436.6
429 | 208 | 115.3 | 405.7 | 522.1 | 139.6 | 438.6
430 | 209 | 115.7 | 407.7 | 517.5 | 141.7 | 438.5
431 | 210 | 116.1 | 412.9 | 523 | 143.6 | 439.4
432 | 211 | 116.6 | 412.4 | 523 | 144.8 | 439.4
433 | 212 | 117 | 412.3 | 521.9 | 145.9 | 439.3
434 | 213 | 117.5 | 413.6 | 528.6 | 147.3 | 440.4
435 | 214 | 118 | 412.2 | 525.1 | 148.2 | 440.2
436 | 215 | 118.4 | 409.9 | 527.8 | 148.8 | 439.8
437 | 216 | 118.9 | 409 | 525.9 | 149.5 | 439.8
438 | 217 | 119.5 | 408.7 | 518.8 | 149.7 | 439.7
439 | 218 | 120 | 411.7 | 526.4 | 150.1 | 440.3
440 | 219 | 120.5 | 414 | 520.5 | 150.8 | 441.3
441 | 220 | 121.1 | 410.2 | 521.1 | 151.2 | 442
442 | 221 | 121.6 | 412.9 | 532.6 | 151.5 | 445.7
443 | 222 | 122.2 | 415.3 | 534.7 | 151.5 | 447.2
444 | 223 | 122.8 | 415.6 | 532.4 | 151.3 | 447.2
445 | 224 | 123.5 | 417 | 530.8 | 150.9 | 448.4
446 | 225 | 124.1 | 414.2 | 521.8 | 150.5 | 447.9
447 | 226 | 124.7 | 408.9 | 510.8 | 150 | 447
448 | 227 | 125.3 | 405.4 | 507.4 | 149.2 | 446.8
449 | 228 | 125.9 | 403.3 | 509.7 | 148.7 | 447.2
450 | 229 | 126.4 | 404 | 517.8 | 148.6 | 449.2
451 | 230 | 127 | 410.3 | 533.1 | 148.6 | 451.7
452 | 231 | 127.5 | 410.5 | 539.7 | 148.4 | 453
453 | 232 | 128.1 | 408.9 | 548.1 | 148.4 | 455.5
454 | 233 | 128.6 | 411.4 | 545 | 148.5 | 456.7
455 | 234 | 129.1 | 411.4 | 548.4 | 148.5 | 456.9
456 | 235 | 129.6 | 409.1 | 542.4 | 148.5 | 456.6
457 | 236 | 130.1 | 407.9 | 534.6 | 148.7 | 458
458 | 237 | 130.7 | 403.9 | 536.3 | 148.4 | 458.5
459 | 238 | 131.3 | 406.4 | 552.1 | 148.4 | 459.7
460 | 239 | 131.8 | 417.1 | 562 | 148.6 | 460.9
461 | 240 | 132.3 | 418.6 | 567.5 | 148.4 | 463
462 | 241 | 132.8 | 419.7 | 567.5 | 148.3 | 464.3
463 | 242 | 133.4 | 420.2 | 565 | 148.3 | 465.2
464 | 243 | 133.9 | 420.7 | 569.3 | 148.3 | 467.8
465 | 244 | 134.4 | 416.7 | 553.5 | 148.2 | 468.6
466 | 245 | 134.9 | 413.2 | 546.9 | 148.5 | 468.5
467 | 246 | 135.4 | 411.7 | 534.9 | 148.4 | 467.5
468 | 247 | 135.9 | 410 | 529.1 | 147.9 | 467.5
469 | 248 | 136.4 | 408.7 | 523.6 | 147.8 | 467.4
470 | 249 | 136.9 | 406.9 | 519.3 | 147.6 | 467.7
471 | 250 | 137.4 | 408.5 | 521.6 | 147.9 | 469.7
472 | 251 | 138 | 408.9 | 515.9 | 147.9 | 471.4
473 | 252 | 138.5 | 407 | 508.9 | 147.7 | 471.3
474 | 253 | 139 | 403.6 | 502.7 | 147.5 | 470.7
475 | 254 | 139.5 | 404.2 | 503 | 147.6 | 471.9
476 | 255 | 140.1 | 403.4 | 504.4 | 147.6 | 472.4
477 | 256 | 140.6 | 399 | 491.9 | 147.4 | 471.2
478 | 257 | 141.1 | 395.4 | 489.6 | 147.5 | 472.1
479 | 258 | 141.6 | 397.7 | 501 | 147.7 | 474.6
480 | 259 | 142.1 | 398.6 | 500 | 147.9 | 475.8
481 | 260 | 142.7 | 399.4 | 499.5 | 148.6 | 478.1
482 | 261 | 143.2 | 398.4 | 504 | 149.3 | 479.4
483 | 262 | 143.7 | 397.5 | 510.1 | 150.2 | 481.2
484 | 263 | 144.2 | 400 | 526.4 | 151.3 | 484.1
485 | 264 | 144.7 | 409.1 | 542 | 152.1 | 486.5
486 | 265 | 145.2 | 415 | 561.8 | 152.8 | 489.1
487 | 266 | 145.7 | 422.1 | 569.3 | 153.3 | 493.2
488 | 267 | 146.2 | 425.1 | 584.1 | 154 | 496.4
489 | 268 | 146.7 | 429.6 | 595.8 | 154.7 | 498.8
490 | 269 | 147.2 | 435 | 610 | 155.5 | 501.2
491 | 270 | 147.7 | 442.4 | 629 | 156.3 | 504.1
492 | 271 | 148.3 | 441.8 | 632.8 | 156.9 | 506.4
493 | 272 | 148.8 | 437.6 | 626.5 | 157.2 | 506.3
494 | 273 | 149.4 | 431.6 | 609.7 | 157.2 | 505
495 | 274 | 149.9 | 428.7 | 601.3 | 157.5 | 504.9
496 | 275 | 150.5 | 425.5 | 589.5 | 157.7 | 505
497 | 276 | 151 | 419.6 | 575.7 | 158.1 | 504.7
498 | 277 | 151.6 | 414.6 | 567 | 158.3 | 504.8
499 | 278 | 152.1 | 411.5 | 562.2 | 159 | 506.4
500 | 279 | 152.6 | 412.2 | 575.2 | 160.2 | 509.4
501 | 280 | 153.2 | 413.7 | 575.7 | 161.3 | 511.1
502 | 281 | 153.7 | 412.9 | 570.3 | 161.9 | 510.2
503 | 282 | 154.2 | 413.4 | 569.9 | 162.6 | 509.8
504 | 283 | 154.7 | 411.3 | 563 | 162.9 | 510
505 | 284 | 155.3 | 412.4 | 559.6 | 163.3 | 511.1
506 | 285 | 155.8 | 411 | 555.9 | 163.7 | 511.3
507 | 286 | 156.3 | 409.6 | 547.4 | 164.1 | 511
508 | 287 | 156.8 | 409.1 | 542.9 | 164.6 | 511.7
509 | 288 | 157.4 | 408.2 | 539.5 | 164.7 | 511.5
510 | 289 | 157.9 | 406.1 | 539.5 | 165.2 | 512.9
511 | 290 | 158.4 | 405.9 | 538 | 165.5 | 514.9
512 | 291 | 159 | 406.5 | 540.7 | 165.9 | 515.8
513 | 292 | 159.5 | 412.7 | 547.6 | 166.4 | 517.9
514 | 293 | 160 | 415.3 | 552.6 | 166.8 | 519
515 | 294 | 160.5 | 417.3 | 557.2 | 167.2 | 519.5
516 | 295 | 161 | 418.4 | 566 | 167.8 | 521.6
517 | 296 | 161.5 | 415.1 | 554.5 | 168.7 | 521.9
518 | 297 | 162.1 | 414.4 | 550.7 | 169.6 | 523.1
519 | 298 | 162.6 | 415.3 | 559.2 | 170.3 | 524.4
520 | 299 | 163.1 | 418.8 | 565 | 170.9 | 524.8
521 | 300 | 163.6 | 422.8 | 577.7 | 171.6 | 526
522 | 301 | 164.1 | 423.3 | 578.6 | 171.8 | 526.3
523 | 302 | 164.7 | 424.4 | 579.7 | 172 | 526.9
524 | 303 | 165.2 | 425.4 | 589.4 | 171.9 | 528.4
525 | 304 | 165.7 | 426.1 | 592.8 | 172.1 | 530.4
526 | 305 | 166.2 | 429.4 | 593.8 | 172.7 | 531.8
527 | 306 | 166.7 | 429.8 | 597.6 | 172.9 | 532.4
528 | 307 | 167.3 | 432.1 | 615.9 | 173.4 | 534.4
529 | 308 | 167.8 | 442 | 623.5 | 174.4 | 535.2
530 | 309 | 168.3 | 447.3 | 631.8 | 174.9 | 535.8
531 | 310 | 168.8 | 447.5 | 627.8 | 175.3 | 536.8
532 | 311 | 169.3 | 444.2 | 625.1 | 175.6 | 537.9
533 | 312 | 169.9 | 449.1 | 633.4 | 176.4 | 539.2
534 | 313 | 170.4 | 458.5 | 653.4 | 177.1 | 541.3
535 | 314 | 170.9 | 458.4 | 650.2 | 177.5 | 543.5
536 | 315 | 171.5 | 454.5 | 636 | 177.5 | 544.2
537 | 316 | 172 | 448.7 | 625.7 | 177.4 | 544.2
538 | 317 | 172.5 | 444.2 | 614.1 | 177.4 | 544.1
539 | 318 | 173.1 | 441.5 | 607.3 | 177.2 | 543.4
540 | 319 | 173.6 | 437.6 | 590.4 | 176.8 | 542
541 | 320 | 174.1 | 434.3 | 582.5 | 176.9 | 540.8
542 | 321 | 174.7 | 433.1 | 579.9 | 176.5 | 540.7
543 | 322 | 175.2 | 435.4 | 591.6 | 176.6 | 541.5
544 | 323 | 175.7 | 436.7 | 592.7 | 176.5 | 541.2
545 | 324 | 176.3 | 439 | 597.9 | 176.5 | 541.1
546 | 325 | 176.8 | 445.4 | 613.1 | 176.6 | 542
547 | 326 | 177.3 | 447.3 | 601.1 | 176.9 | 542.7
548 | 327 | 177.9 | 448.7 | 595.2 | 177.2 | 542
549 | 328 | 178.4 | 447.5 | 584.8 | 177.6 | 541.9
550 | 329 | 179 | 449.6 | 586.4 | 178.1 | 542.2
551 | 330 | 179.5 | 450.4 | 597.3 | 178.5 | 543.6
552 | 331 | 180 | 450.4 | 594.1 | 178.8 | 544.6
553 | 332 | 180.6 | 453.2 | 597 | 179.1 | 545.7
554 | 333 | 181.1 | 454.3 | 591.4 | 179.7 | 547.5
555 | 334 | 181.7 | 455.1 | 595.4 | 180.1 | 548.9
556 | 335 | 182.3 | 454.7 | 592.3 | 180.6 | 549.6
557 | 336 | 182.8 | 453.5 | 588.5 | 181.1 | 549.4
558 | 337 | 183.3 | 448.5 | 574.4 | 181.3 | 547.8
559 | 338 | 183.9 | 446.4 | 572.1 | 181.3 | 547.7
560 | 339 | 184.4 | 444.8 | 559.6 | 181.5 | 546.9
561 | 340 | 185 | 440.6 | 547 | 181.6 | 546.5
562 | 341 | 185.5 | 434.7 | 536 | 181.9 | 546.5
563 | 342 | 186.1 | 428.9 | 525.2 | 181.9 | 545.5
564 | 343 | 186.7 | 424.9 | 510.3 | 181.9 | 543.6
565 | 344 | 187.2 | 418.3 | 496.4 | 182.1 | 542.8
566 | 345 | 187.8 | 415.1 | 500.5 | 182.3 | 542.7
567 | 346 | 188.3 | 418.4 | 513.9 | 183 | 544.6
568 | 347 | 188.9 | 419.6 | 515.3 | 183.5 | 545.6
569 | 348 | 189.4 | 417.8 | 509.2 | 183.8 | 546.5
570 | 349 | 190 | 415.6 | 512.3 | 184.3 | 545.6
571 | 350 | 190.6 | 420.1 | 530.5 | 184.8 | 546.2
572 | 351 | 191.1 | 420.8 | 529.5 | 185.3 | 546.6
573 | 352 | 191.7 | 419.5 | 520.6 | 185.6 | 547.4
574 | 353 | 192.3 | 418.1 | 523.3 | 186 | 548.9
575 | 354 | 192.8 | 417.6 | 521.3 | 186.5 | 549.3
576 | 355 | 193.4 | 418 | 536 | 186.8 | 549.8
577 | 356 | 193.9 | 423 | 553.3 | 187.3 | 550.7
578 | 357 | 194.5 | 424.7 | 547.9 | 187.8 | 551.1
579 | 358 | 195.1 | 421.6 | 534.2 | 188.4 | 551
580 | 359 | 195.6 | 419.4 | 528.8 | 188.9 | 550
581 | 360 | 196.2 | 417.8 | 526.1 | 189.2 | 550.7
582 | 361 | 196.7 | 420 | 538 | 189.8 | 551.5
583 | 362 | 197.3 | 421 | 542.5 | 190.4 | 552.3
584 | 363 | 197.8 | 419.8 | 534.8 | 190.9 | 552.4
585 | 364 | 198.4 | 419.5 | 530.2 | 191.6 | 552
586 | 365 | 199 | 417.7 | 528.8 | 192.4 | 551.8
587 | 366 | 199.5 | 417.9 | 534.9 | 193.1 | 552.2
588 | 367 | 200.1 | 418.2 | 540.6 | 194 | 552.8
589 | 368 | 200.6 | 419.9 | 548 | 195.3 | 553.7
590 | 369 | 201.2 | 422.9 | 572.9 | 196.6 | 555.1
591 | 370 | 201.8 | 426.8 | 581.1 | 198 | 556.5
592 | 371 | 202.3 | 426.4 | 571.5 | 199.4 | 557.1
593 | 372 | 202.9 | 428.9 | 577.5 | 201.2 | 558.9
594 | 373 | 203.4 | 433 | 595 | 202.5 | 559
595 | 374 | 204 | 438.1 | 612.8 | 203.7 | 558.9
596 | 375 | 204.5 | 440.1 | 615.7 | 204.8 | 559.3
597 | 376 | 205.1 | 440.7 | 620.2 | 205.8 | 561
598 | 377 | 205.6 | 441.7 | 625.5 | 206.3 | 562.2
599 | 378 | 206.1 | 444 | 629.4 | 206.7 | 563.9
600 | 379 | 206.7 | 445.3 | 631.9 | 207.1 | 563.9
601 | 380 | 207.2 | 446.4 | 629 | 207.2 | 563.9
602 | 381 | 207.7 | 451 | 649.6 | 207.3 | 566.3
603 | 382 | 208.3 | 453.3 | 642.2 | 207.1 | 565.8
604 | 383 | 208.8 | 451.3 | 636.3 | 206.9 | 565.7
605 | 384 | 209.3 | 452.7 | 634.9 | 206.9 | 566.6
606 | 385 | 209.8 | 449.7 | 624.6 | 206.7 | 566
607 | 386 | 210.3 | 448.9 | 613.1 | 206.8 | 566.5
608 | 387 | 210.8 | 446.1 | 597.7 | 206.8 | 567.1
609 | 388 | 211.3 | 442.2 | 583 | 207.3 | 566.3
610 | 389 | 211.9 | 438.8 | 570.5 | 207.8 | 565.2
611 | 390 | 212.4 | 435.9 | 572.3 | 208 | 565.5
612 | 391 | 212.9 | 441.1 | 585.8 | 208 | 565.4
613 | 392 | 213.4 | 448.1 | 599 | 207.8 | 564.9
614 | 393 | 213.9 | 448.8 | 599.1 | 207.5 | 564.1
615 | 394 | 214.4 | 447.4 | 601.7 | 207.1 | 562.2
616 | 395 | 214.9 | 446.6 | 598 | 206.7 | 560.6
617 | 396 | 215.4 | 442.4 | 591.3 | 206.1 | 559
618 | 397 | 215.9 | 439.9 | 583.3 | 205.6 | 557.4
619 | 398 | 216.4 | 438.3 | 580.2 | 205.1 | 555.3
620 | 399 | 216.9 | 436.1 | 584.4 | 204.7 | 553.5
621 | 400 | 217.4 | 435.8 | 591.3 | 204.3 | 552.7
622 | 401 | 217.9 | 438.4 | 596 | 204.1 | 552.2
623 | 402 | 218.4 | 441.2 | 595.9 | 203.8 | 551.5
624 | 403 | 218.9 | 440.9 | 599.3 | 203.6 | 550.7
625 | 404 | 219.4 | 441.6 | 597.8 | 203.4 | 550.2
626 | 405 | 219.9 | 438 | 588.6 | 203.3 | 549.5
627 | 406 | 220.4 | 438.6 | 591 | 203.1 | 549.5
628 | 407 | 220.9 | 440.4 | 595.9 | 203 | 550
629 | 408 | 221.4 | 441.6 | 602.7 | 202.9 | 549.7
630 | 409 | 221.9 | 441.8 | 603.5 | 202.7 | 548.7
631 | 410 | 222.4 | 442.7 | 598.4 | 202.6 | 547
632 | 411 | 222.9 | 444.2 | 593 | 202.5 | 545.7
633 | 412 | 223.4 | 446 | 594.2 | 202.4 | 544.8
634 | 413 | 223.9 | 446 | 596.7 | 202.3 | 543.6
635 | 414 | 224.4 | 444.7 | 605.5 | 202.1 | 543.7
636 | 415 | 224.9 | 446.1 | 606.3 | 202.1 | 543.6
637 | 416 | 225.3 | 447.5 | 598.9 | 202 | 542.2
638 | 417 | 225.8 | 447.8 | 591 | 201.9 | 540.8
639 | 418 | 226.3 | 444 | 578.7 | 201.7 | 539
640 | 419 | 226.8 | 442.6 | 573.5 | 201.6 | 537.8
641 | 420 | 227.3 | 444.4 | 580.7 | 201.5 | 538.1
642 | 421 | 227.8 | 441.5 | 581 | 201.3 | 537.7
643 | 422 | 228.3 | 440.8 | 592.7 | 201.3 | 539.7
644 | 423 | 228.8 | 445.7 | 609.7 | 201.2 | 541.4
645 | 424 | 229.2 | 448.6 | 608.5 | 201.1 | 541.7
646 | 425 | 229.7 | 451.1 | 612.1 | 201.1 | 542.5
647 | 426 | 230.2 | 449.7 | 609.8 | 201 | 542
648 | 427 | 230.7 | 448.5 | 618.7 | 200.9 | 544.2
649 | 428 | 231.2 | 448.3 | 617 | 200.9 | 546
650 | 429 | 231.7 | 445.7 | 611.7 | 200.8 | 545.7
651 | 430 | 232.1 | 442.9 | 597.7 | 200.7 | 546.3
652 | 431 | 232.6 | 441.8 | 593.2 | 200.7 | 547.1
653 | 432 | 233.1 | 440.2 | 587 | 200.6 | 546.7
654 | 433 | 233.6 | 442.4 | 591.3 | 200.5 | 546.2
655 | 434 | 234.1 | 445.1 | 596.4 | 200.5 | 546.8
656 | 435 | 234.6 | 448.4 | 603.2 | 200.5 | 547.8
657 | 436 | 235 | 447.1 | 600.5 | 200.5 | 546.9
658 | 437 | 235.5 | 443.6 | 596.4 | 200.5 | 546.1
659 | 438 | 236 | 439.4 | 588.2 | 200.4 | 545.5
660 | 439 | 236.5 | 436.8 | 588.6 | 200.5 | 545.1
661 | 440 | 237 | 436 | 579.1 | 200.5 | 544.6
662 | 441 | 237.5 | 434.4 | 574.7 | 200.6 | 545.5
663 | 442 | 238 | 438 | 586.6 | 200.7 | 546.3
664 | 443 | 238.5 | 437.6 | 576.4 | 200.8 | 545.2
665 | 444 | 239 | 434.8 | 559.5 | 200.9 | 543.4
666 | 445 | 239.5 | 429.4 | 547.6 | 200.9 | 541.3
667 | 446 | 240 | 423.6 | 538 | 201 | 539.4
668 | 447 | 240.5 | 420.4 | 536.3 | 201 | 537.5
669 | 448 | 241 | 418.5 | 533 | 201 | 535.9
670 | 449 | 241.6 | 417.4 | 535.8 | 201 | 533.9
671 | 450 | 242.1 | 419.8 | 535.5 | 201.1 | 532.5
672 | 451 | 242.6 | 421.5 | 546.1 | 201.1 | 532.4
673 | 452 | 243.1 | 421.4 | 553 | 201.2 | 531.8
674 | 453 | 243.7 | 422.5 | 556.3 | 201.2 | 530.8
675 | 454 | 244.2 | 428.6 | 575.1 | 201.3 | 531.4
676 | 455 | 244.7 | 433.1 | 573.8 | 201.4 | 531.3
677 | 456 | 245.2 | 429.4 | 561.5 | 201.4 | 529.9
678 | 457 | 245.7 | 430.5 | 571.2 | 201.5 | 529
679 | 458 | 246.2 | 430.4 | 574.1 | 201.6 | 528.5
680 | 459 | 246.7 | 429.6 | 566.2 | 201.6 | 527.3
681 | 460 | 247.2 | 429.4 | 558.3 | 201.7 | 526.7
682 | 461 | 247.7 | 427.2 | 550.3 | 201.7 | 524.8
683 | 462 | 248.3 | 428.4 | 549 | 201.8 | 523.5
684 | 463 | 248.8 | 428 | 541.3 | 201.9 | 522.1
685 | 464 | 249.3 | 432.4 | 558.3 | 202 | 521.6
686 | 465 | 249.9 | 435.1 | 561 | 202.1 | 520.5
687 | 466 | 250.5 | 434.2 | 564.9 | 202.2 | 519.7
688 | 467 | 251 | 430.5 | 564.6 | 202.2 | 519
689 | 468 | 251.6 | 426.7 | 559.2 | 202.3 | 517.9
690 | 469 | 252.1 | 423.4 | 550.7 | 202.4 | 516.2
691 | 470 | 252.6 | 421.6 | 548.2 | 202.5 | 515.1
692 | 471 | 253.1 | 419.8 | 548.6 | 202.6 | 513.7
693 | 472 | 253.6 | 419.5 | 544.3 | 202.7 | 512.5
694 | 473 | 254.1 | 420 | 546.9 | 202.8 | 512.1
695 | 474 | 254.5 | 420 | 546.9 | 202.9 | 511.3
696 | 475 | 255 | 419.9 | 547.6 | 203 | 510.3
697 | 476 | 255.5 | 418.3 | 544.6 | 203.1 | 510
698 | 477 | 256 | 418 | 548.1 | 203.2 | 509.4
699 | 478 | 256.4 | 417.8 | 542.4 | 203.3 | 508.6
700 | 479 | 256.9 | 414.2 | 534.9 | 203.4 | 507.2
701 | 480 | 257.3 | 414 | 540 | 203.6 | 506.6
702 | 481 | 257.8 | 416.1 | 548.9 | 203.7 | 506.9
703 | 482 | 258.2 | 415.8 | 547.1 | 203.9 | 506.7
704 | 483 | 258.7 | 417 | 548.5 | 204 | 506.4
705 | 484 | 259.1 | 418.2 | 546.7 | 204.2 | 505.8
706 | 485 | 259.5 | 417.8 | 550.7 | 204.3 | 505
707 | 486 | 259.9 | 418.9 | 553.3 | 204.4 | 504.9
708 | 487 | 260.4 | 421.5 | 554.3 | 204.6 | 505.4
709 | 488 | 260.8 | 421.9 | 557.4 | 204.7 | 505.8
710 | 489 | 261.2 | 420.5 | 543.8 | 204.9 | 506
711 | 490 | 261.6 | 419.6 | 540.6 | 205 | 508.1
712 | 491 | 262 | 421.4 | 549.9 | 205.2 | 510.1
713 | 492 | 262.4 | 425.9 | 564.3 | 205.4 | 512.6
714 | 493 | 262.9 | 427.8 | 574 | 205.5 | 513.9
715 | 494 | 263.3 | 427.9 | 578 | 205.7 | 513.6
716 | 495 | 263.7 | 427.3 | 576 | 205.9 | 512.9
717 | 496 | 264.1 | 424.2 | 573.1 | 206 | 511.8
718 | 497 | 264.5 | 424.4 | 576.6 | 206.2 | 511.3
719 | 498 | 265 | 424.4 | 578.1 | 206.4 | 512
720 | 499 | 265.4 | 427.3 | 579.8 | 206.6 | 512.8
721 | 500 | 265.8 | 431.7 | 584.1 | 206.7 | 513.4
722 | 501 | 266.2 | 433.8 | 578.1 | 206.9 | 513.5
723 | 502 | 266.7 | 434.9 | 569.8 | 207.1 | 512.6
724 | 503 | 267.1 | 431.8 | 558.7 | 207.3 | 511.4
725 | 504 | 267.5 | 430.6 | 560.2 | 207.5 | 510.3
726 | 505 | 267.9 | 431.7 | 568.2 | 207.7 | 509.7
727 | 506 | 268.3 | 430.4 | 563.2 | 207.9 | 508.7
728 | 507 | 268.8 | 432.4 | 569.1 | 208.1 | 508.3
729 | 508 | 269.2 | 436.2 | 567.1 | 208.4 | 507.8
730 | 509 | 269.6 | 434.9 | 563.7 | 208.6 | 506.9
731 | 510 | 270 | 433.6 | 562.4 | 208.8 | 505.9
732 | 511 | 270.5 | 433.2 | 564.2 | 209 | 505.2
733 | 512 | 270.9 | 432.5 | 567.5 | 209.2 | 505.3
734 | 513 | 271.3 | 430.8 | 566.1 | 209.4 | 505.2
735 | 514 | 271.8 | 429.6 | 565.9 | 209.6 | 505.8
736 | 515 | 272.2 | 431.1 | 570.3 | 209.7 | 507.4
737 | 516 | 272.6 | 432.2 | 578.9 | 209.9 | 508.3
738 | 517 | 273 | 431.7 | 573.2 | 210.1 | 508.5
739 | 518 | 273.4 | 431 | 570.3 | 210.3 | 510.1
740 | 519 | 273.9 | 431 | 568.4 | 210.4 | 511.1
741 | 520 | 274.3 | 430.1 | 566.7 | 210.6 | 511.2
742 | 521 | 274.7 | 429.2 | 562.5 | 210.8 | 512.6
743 | 522 | 275.1 | 427.9 | 568.8 | 211 | 513
744 | 523 | 275.6 | 430.5 | 584.1 | 211.2 | 514.4
745 | 524 | 276 | 431.5 | 579 | 211.4 | 515.8
746 | 525 | 276.4 | 431.2 | 570.7 | 211.6 | 517.3
747 | 526 | 276.9 | 432.2 | 569.2 | 211.8 | 519
748 | 527 | 277.3 | 434.9 | 584.2 | 212 | 521.4
749 | 528 | 277.7 | 438.9 | 583.5 | 212.1 | 522.2
750 | 529 | 278.1 | 436.6 | 566.7 | 212.3 | 520.9
751 | 530 | 278.5 | 432.9 | 554.6 | 212.5 | 519.5
752 | 531 | 278.9 | 429.2 | 544.6 | 212.7 | 518.2
753 | 532 | 279.4 | 426.2 | 546.3 | 212.8 | 517.3
754 | 533 | 279.8 | 427.5 | 556.9 | 213 | 517.1
755 | 534 | 280.2 | 426.5 | 555.9 | 213.2 | 517
756 | 535 | 280.6 | 426.9 | 555.9 | 213.3 | 517.1
757 | 536 | 281 | 426.5 | 551.4 | 213.4 | 517.3
758 | 537 | 281.4 | 425.6 | 546.9 | 213.6 | 516.9
759 | 538 | 281.8 | 425.4 | 537.8 | 213.7 | 516.2
760 | 539 | 282.2 | 423.9 | 532.4 | 213.8 | 515.4
761 | 540 | 282.6 | 421.1 | 523.7 | 214 | 514.4
762 | 541 | 283.1 | 416.8 | 513 | 214.1 | 512.8
763 | 542 | 283.5 | 412.1 | 502.8 | 214.2 | 511.2
764 | 543 | 283.9 | 409.7 | 501.3 | 214.4 | 510.4
765 | 544 | 284.3 | 408.7 | 500 | 214.5 | 509.8
766 | 545 | 284.7 | 404.7 | 487.5 | 214.7 | 508.4
767 | 546 | 285.1 | 399.5 | 474.3 | 214.8 | 507.3
768 | 547 | 285.5 | 394.5 | 463.1 | 215 | 505.5
769 | 548 | 285.9 | 391.6 | 457.7 | 215.1 | 504.8
770 | 549 | 286.3 | 389.9 | 457 | 215.3 | 504.5
771 | 550 | 286.7 | 387.7 | 450.6 | 215.4 | 503.4
772 | 551 | 287.1 | 385 | 442 | 215.6 | 501.9
773 | 552 | 287.5 | 383 | 435.8 | 215.7 | 500.7
774 | 553 | 288 | 381.3 | 438.4 | 215.8 | 499.4
775 | 554 | 288.4 | 381.1 | 447.3 | 216 | 498.7
776 | 555 | 288.8 | 381.5 | 455.4 | 216.1 | 498.4
777 | 556 | 289.2 | 381.4 | 465.6 | 216.3 | 498.4
778 | 557 | 289.6 | 381.8 | 474.8 | 216.5 | 498.1
779 | 558 | 290.1 | 385.2 | 488.1 | 216.6 | 498.1
780 | 559 | 290.5 | 387.5 | 499.1 | 216.8 | 497.8
781 | 560 | 290.9 | 390.9 | 522.4 | 217 | 498.4
782 | 561 | 291.3 | 393.2 | 531.6 | 217.1 | 500
783 | 562 | 291.7 | 398.2 | 534.7 | 217.3 | 502.4
784 | 563 | 292.1 | 397.8 | 525.1 | 217.4 | 502.3
785 | 564 | 292.5 | 397.2 | 519.8 | 217.6 | 501.8
786 | 565 | 292.9 | 396.1 | 514.5 | 217.7 | 501.1
787 | 566 | 293.3 | 395.8 | 519.2 | 217.9 | 501.5
788 | 567 | 293.7 | 395.3 | 518.8 | 218.1 | 502.3
789 | 568 | 294.1 | 396 | 520.8 | 218.2 | 502.2
790 | 569 | 294.5 | 398.6 | 537.9 | 218.4 | 502.9
791 | 570 | 294.9 | 399.8 | 533.5 | 218.6 | 503.2
792 | 571 | 295.3 | 399.3 | 527.9 | 218.7 | 503.3
793 | 572 | 295.7 | 400.7 | 529.4 | 218.9 | 503.7
794 | 573 | 296.1 | 398.6 | 528.3 | 219 | 503.4
795 | 574 | 296.5 | 396.7 | 527.7 | 219.2 | 503
796 | 575 | 296.9 | 395.2 | 527 | 219.3 | 502.9
797 | 576 | 297.3 | 395.7 | 535.8 | 219.5 | 503.8
798 | 577 | 297.7 | 397.8 | 545.3 | 219.6 | 505.8
799 | 578 | 298.1 | 398.1 | 535.9 | 219.8 | 505.5
800 | 579 | 298.5 | 396.3 | 531.5 | 219.9 | 504.8
801 | 580 | 298.8 | 394.3 | 528.4 | 220.1 | 504.8
802 | 581 | 299.2 | 396.5 | 535.5 | 220.3 | 505.3
803 | 582 | 299.6 | 399.5 | 545 | 220.4 | 505.9
804 | 583 | 300 | 403.5 | 569.9 | 220.6 | 508.6
805 | 584 | 300.4 | 403.7 | 579.7 | 220.8 | 511.5
806 | 585 | 300.8 | 404.1 | 600.7 | 221 | 515.1
807 | 586 | 301.2 | 407.6 | 608.2 | 221.2 | 518.9
808 | 587 | 301.6 | 408.9 | 599.4 | 221.3 | 520
809 | 588 | 302 | 408.5 | 590.8 | 221.5 | 520
810 | 589 | 302.4 | 409.8 | 590.1 | 221.7 | 520.7
811 | 590 | 302.8 | 409.8 | 583.4 | 221.9 | 520.5
812 | 591 | 303.2 | 411 | 583.6 | 222 | 520
813 | 592 | 303.6 | 409.9 | 572.4 | 222.2 | 519.5
814 | 593 | 304 | 407.5 | 554.1 | 222.4 | 518.9
815 | 594 | 304.4 | 404.8 | 537.3 | 222.6 | 517.5
816 | 595 | 304.8 | 401 | 522.8 | 222.7 | 516
817 | 596 | 305.2 | 401.8 | 520.5 | 222.9 | 515.9
818 | 597 | 305.7 | 405.1 | 518.8 | 223 | 515.4
819 | 598 | 306 | 405.9 | 526.5 | 223.1 | 514.5
820 | 599 | 306.4 | 408.1 | 530.6 | 223.3 | 515.6
821 | 600 | 306.8 | 405.9 | 526.1 | 223.4 | 514.7
822 | 601 | 307.1 | 404.6 | 528.9 | 223.6 | 514.6
823 | 602 | 307.5 | 404.8 | 528.1 | 223.7 | 514.2
824 | 603 | 307.9 | 403.6 | 525.2 | 223.9 | 514.3
825 | 604 | 308.3 | 402.7 | 525.4 | 224.1 | 514
826 | 605 | 308.7 | 401.8 | 525.9 | 224.2 | 513.7
827 | 606 | 309 | 401.7 | 529 | 224.4 | 513.8
828 | 607 | 309.4 | 401.9 | 539.7 | 224.5 | 514.6
829 | 608 | 309.8 | 402.3 | 542.3 | 224.7 | 514.1
830 | 609 | 310.2 | 405.6 | 557.8 | 224.8 | 514.6
831 | 610 | 310.6 | 410.1 | 566.6 | 225 | 515
832 | 611 | 311 | 414.1 | 585 | 225.1 | 516.6
833 | 612 | 311.4 | 416.5 | 592.2 | 225.2 | 518.1
834 | 613 | 311.7 | 416.4 | 578.7 | 225.4 | 518.1
835 | 614 | 312.1 | 414.1 | 569.6 | 225.5 | 517.6
836 | 615 | 312.6 | 416.9 | 555.4 | 225.7 | 517
837 | 616 | 312.9 | 429.2 | 551.8 | 225.8 | 517.2
838 | 617 | 313.3 | 429.9 | 571 | 226 | 519.7
839 | 618 | 313.7 | 429 | 569.8 | 226.1 | 521.8
840 | 619 | 314.1 | 427.8 | 553.8 | 226.3 | 521.9
841 | 620 | 314.6 | 448.1 | 543.7 | 226.4 | 521.2
842 | 621 | 315 | 469 | 545.4 | 226.6 | 522.6
843 | 622 | 315.4 | 465.2 | 547.8 | 226.7 | 522.8
844 | 623 | 315.8 | 464.1 | 555.6 | 226.9 | 523
845 | 624 | 316.2 | 462.2 | 553.4 | 227.1 | 522.2
846 | 625 | 316.7 | 463.7 | 553.6 | 227.2 | 521.4
847 | 626 | 317 | 469.4 | 551.7 | 227.4 | 520.2
848 | 627 | 317.5 | 469.5 | 555.2 | 227.5 | 519.7
849 | 628 | 317.9 | 468.7 | 563 | 227.7 | 519.8
850 | 629 | 318.3 | 476.6 | 559.6 | 227.8 | 519.2
851 | 630 | 318.7 | 476.1 | 563.4 | 228 | 518.8
852 | 631 | 319.1 | 478.8 | 573.6 | 228.1 | 519.6
853 | 632 | 319.6 | 482.8 | 587.4 | 228.3 | 520.8
854 | 633 | 320.1 | 487.4 | 604.7 | 228.5 | 521.5
855 | 634 | 320.5 | 491.1 | 615.1 | 228.6 | 522.3
856 | 635 | 321 | 494.6 | 607.3 | 228.8 | 523.1
857 | 636 | 321.4 | 502.2 | 600.1 | 229 | 524.7
858 | 637 | 321.9 | 502.1 | 598.2 | 229.1 | 524.5
859 | 638 | 322.3 | 502.5 | 604.9 | 229.3 | 525.5
860 | 639 | 322.6 | 506.6 | 612.4 | 229.4 | 526.7
861 | 640 | 323.1 | 516 | 612.6 | 229.6 | 527.4
862 | 641 | 323.4 | 519.7 | 621.7 | 229.8 | 528.3
863 | 642 | 323.8 | 521.8 | 622.7 | 229.9 | 529.2
864 | 643 | 324.2 | 518.9 | 617.1 | 230.1 | 529.1
865 | 644 | 324.7 | 513.1 | 609.7 | 230.2 | 529.4
866 | 645 | 325.1 | 511 | 623.2 | 230.4 | 530.1
867 | 646 | 325.6 | 520.6 | 630.8 | 230.5 | 531.1
868 | 647 | 326.1 | 539.9 | 642.4 | 230.7 | 531.2
869 | 648 | 326.5 | 544.7 | 653.5 | 230.8 | 532.3
870 | 649 | 327 | 551.5 | 647.4 | 231 | 534.1
871 | 650 | 327.5 | 556.9 | 634.6 | 231.2 | 533.1
872 | 651 | 328 | 561.8 | 634.2 | 231.3 | 533.3
873 | 652 | 328.4 | 565.9 | 633.1 | 231.5 | 533.5
874 | 653 | 328.9 | 565.5 | 637 | 231.7 | 534.9
875 | 654 | 329.5 | 559.8 | 631.8 | 231.9 | 534.5
876 | 655 | 329.9 | 566.6 | 627.2 | 232.1 | 534
877 | 656 | 330.4 | 564.6 | 608.9 | 232.3 | 533.8
878 | 657 | 330.9 | 558.3 | 597 | 232.5 | 533.5
879 | 658 | 331.5 | 563.7 | 605.3 | 232.7 | 535.8
880 | 659 | 332.2 | 561.5 | 608.5 | 232.9 | 538.6
881 | 660 | 332.8 | 553.9 | 601.4 | 233.1 | 537.5
882 | 661 | 333.3 | 542.6 | 594.3 | 233.2 | 536.8
883 | 662 | 333.8 | 535.1 | 594.2 | 233.4 | 536.9
884 | 663 | 334.5 | 539.7 | 613.7 | 233.6 | 538.1
885 | 664 | 335.2 | 541.8 | 630.3 | 233.8 | 539.6
886 | 665 | 335.8 | 553.3 | 636.8 | 234 | 541.3
887 | 666 | 336.4 | 559.3 | 626.5 | 234.2 | 540.5
888 | 667 | 337.1 | 551.4 | 609 | 234.3 | 539.4
889 | 668 | 337.8 | 545.4 | 607.7 | 234.5 | 539
890 | 669 | 338.4 | 542.5 | 614.7 | 234.6 | 540.4
891 | 670 | 339.1 | 533.2 | 604.7 | 234.8 | 540.1
892 | 671 | 339.7 | 531.1 | 591.3 | 235 | 539
893 | 672 | 340.4 | 534 | 575.3 | 235.1 | 537.5
894 | 673 | 341.1 | 539.9 | 558 | 235.3 | 535.5
895 | 674 | 341.7 | 541.8 | 544.1 | 235.5 | 534
896 | 675 | 342.3 | 562.5 | 532.1 | 235.8 | 532.3
897 | 676 | 343 | 571.7 | 521.2 | 236 | 530.4
898 | 677 | 343.6 | 564.9 | 512.4 | 236.2 | 528.8
899 | 678 | 344.2 | 548.5 | 505.5 | 236.4 | 527.3
900 | 679 | 344.9 | 533.8 | 495.2 | 236.6 | 526
901 | 680 | 345.6 | 519.8 | 486.8 | 236.9 | 524.3
902 | 681 | 346.2 | 505.8 | 478.2 | 237.1 | 522.6
903 | 682 | 346.8 | 493.6 | 473.8 | 237.3 | 521.1
904 | 683 | 347.4 | 485.2 | 482.6 | 237.5 | 520.4
905 | 684 | 348 | 477.3 | 493.6 | 237.7 | 520.8
906 | 685 | 348.6 | 471.4 | 492.6 | 237.9 | 520.5
907 | 686 | 349.1 | 464.2 | 484.7 | 238.2 | 519.1
908 | 687 | 349.7 | 456.5 | 475.8 | 238.4 | 517.2
909 | 688 | 350.3 | 450.9 | 479 | 238.6 | 516.3
910 | 689 | 350.9 | 443.4 | 472.4 | 238.9 | 515
911 | 690 | 351.4 | 436.8 | 470.1 | 239.1 | 513.6
912 | 691 | 352 | 432.8 | 469.4 | 239.3 | 512.9
913 | 692 | 352.5 | 429.8 | 467 | 239.6 | 512.5
914 | 693 | 353.1 | 424.6 | 463.3 | 239.8 | 511.4
915 | 694 | 353.6 | 420 | 461.6 | 240.1 | 510.6
916 | 695 | 354.1 | 415.5 | 461.2 | 240.3 | 509.9
917 | 696 | 354.6 | 413.1 | 467.8 | 240.5 | 509
918 | 697 | 355.1 | 411.8 | 475.2 | 240.8 | 508.9
919 | 698 | 355.6 | 411.6 | 482.4 | 241 | 508.3
920 | 699 | 356.1 | 410.1 | 474.3 | 241.2 | 507.2
921 | 700 | 356.5 | 406.8 | 477.6 | 241.4 | 506.4
922 | 701 | 357 | 407.4 | 480.6 | 241.6 | 506
923 | 702 | 357.4 | 408.5 | 482.7 | 241.9 | 505.3
924 | 703 | 357.8 | 411.1 | 481.1 | 242.1 | 504.6
925 | 704 | 358.3 | 408.4 | 478.4 | 242.4 | 504.1
926 | 705 | 358.7 | 405.8 | 484.4 | 242.6 | 503.2
927 | 706 | 359 | 404.2 | 489.7 | 242.9 | 502
928 | 707 | 359.4 | 403.5 | 502.9 | 243.1 | 502.7
929 | 708 | 359.8 | 401.4 | 501.6 | 243.4 | 502.5
930 | 709 | 360.2 | 399.6 | 502.1 | 243.6 | 502.8
931 | 710 | 360.5 | 398.1 | 502.6 | 243.9 | 502.6
932 | 711 | 360.8 | 396.6 | 496.8 | 244.1 | 502
933 | 712 | 361.1 | 393.3 | 490.4 | 244.4 | 501.5
934 | 713 | 361.3 | 390.9 | 485.9 | 244.6 | 500.7
935 | 714 | 361.6 | 389.9 | 482.8 | 244.9 | 500.1
936 | 715 | 361.8 | 388.4 | 487.2 | 245.1 | 499.8
937 | 716 | 362.1 | 386.9 | 492.5 | 245.4 | 499.6
938 | 717 | 362.3 | 386.2 | 490.8 | 245.6 | 499.4
939 | 718 | 362.5 | 384.2 | 489.7 | 245.8 | 498.6
940 | 719 | 362.8 | 381.1 | 487.6 | 246.1 | 498
941 | 720 | 363.1 | 381.5 | 493.3 | 246.3 | 498
942 | 721 | 363.3 | 383.8 | 505.3 | 246.5 | 499
943 | 722 | 363.7 | 387.4 | 524.9 | 246.8 | 502.5
944 | 723 | 364 | 389.6 | 537.5 | 247 | 502.9
945 | 724 | 364.3 | 389.7 | 534.8 | 247.2 | 503.7
946 | 725 | 364.6 | 388 | 522.5 | 247.4 | 503.4
947 | 726 | 364.9 | 386 | 510 | 247.7 | 502.2
948 | 727 | 365.2 | 381.7 | 500.6 | 247.9 | 501.2
949 | 728 | 365.5 | 378.3 | 492.4 | 248.2 | 500.7
950 | 729 | 365.8 | 375.6 | 483.6 | 248.4 | 499.9
951 | 730 | 366 | 374.1 | 486.2 | 248.6 | 499.3
952 | 731 | 366.3 | 373.6 | 497.9 | 248.9 | 499.6
953 | 732 | 366.6 | 373.7 | 515 | 249.1 | 501.4
954 | 733 | 366.9 | 375.8 | 527.6 | 249.4 | 503.5
955 | 734 | 367.1 | 376.9 | 522.6 | 249.6 | 505.1
956 | 735 | 367.4 | 378.5 | 506.3 | 249.9 | 505.1
957 | 736 | 367.7 | 378.2 | 506.3 | 250.1 | 505.1
958 | 737 | 368 | 378.2 | 519.8 | 250.3 | 505.6
959 | 738 | 368.3 | 380.5 | 531.4 | 250.6 | 506.3
960 | 739 | 368.5 | 384.2 | 541.6 | 250.8 | 506.7
961 | 740 | 368.8 | 389.9 | 565.2 | 251.1 | 508.8
962 | 741 | 369.2 | 395.2 | 584.1 | 251.3 | 509.5
963 | 742 | 369.5 | 398.2 | 603.2 | 251.5 | 510.7
964 | 743 | 369.8 | 401 | 611.9 | 251.8 | 512.2
965 | 744 | 370.2 | 402.7 | 616.1 | 252 | 513.8
966 | 745 | 370.6 | 402.1 | 605 | 252.3 | 514.3
967 | 746 | 371 | 401 | 591.9 | 252.6 | 514.2
968 | 747 | 371.4 | 399.3 | 591 | 252.8 | 514.7
969 | 748 | 371.8 | 396.4 | 578.1 | 253.1 | 515
970 | 749 | 372.2 | 393.3 | 567.9 | 253.4 | 514.9
971 | 750 | 372.7 | 392.7 | 566.3 | 253.6 | 515.3
972 | 751 | 373.1 | 393 | 565.7 | 253.9 | 516.2
973 | 752 | 373.6 | 393.6 | 563.5 | 254.1 | 516.7
974 | 753 | 374.1 | 394.9 | 570.7 | 254.4 | 518.1
975 | 754 | 374.5 | 396.5 | 590.4 | 254.6 | 519.2
976 | 755 | 375 | 398.3 | 612.7 | 254.9 | 522.3
977 | 756 | 375.5 | 398.9 | 627.7 | 255.2 | 524.3
978 | 757 | 376 | 398.1 | 634.8 | 255.5 | 526.7
979 | 758 | 376.5 | 398.3 | 633.8 | 255.7 | 529.2
980 | 759 | 377 | 399.5 | 634.5 | 256 | 530.2
981 | 760 | 377.6 | 401.6 | 631.8 | 256.3 | 531.9
982 | 761 | 378.1 | 403.3 | 610.3 | 256.5 | 531.1
983 | 762 | 378.7 | 401.4 | 596.7 | 256.8 | 529.7
984 | 763 | 379.2 | 400 | 591.1 | 257 | 529.7
985 | 764 | 379.8 | 402.5 | 584.7 | 257.3 | 530.7
986 | 765 | 380.3 | 402 | 575.8 | 257.6 | 532.1
987 | 766 | 380.9 | 402.4 | 580.8 | 257.8 | 533.8
988 | 767 | 381.4 | 402.4 | 570.4 | 258.1 | 534.2
989 | 768 | 382 | 402.9 | 560.6 | 258.4 | 533.5
990 | 769 | 382.6 | 401.7 | 544.3 | 258.7 | 531.8
991 | 770 | 383.3 | 399.4 | 533.9 | 258.9 | 531.1
992 | 771 | 383.9 | 397.9 | 531 | 259.2 | 532.3
993 | 772 | 384.5 | 399.8 | 533.7 | 259.4 | 533.7
994 | 773 | 385.1 | 400.5 | 523.5 | 259.7 | 534.6
995 | 774 | 385.7 | 416.2 | 515.3 | 259.9 | 534.1
996 | 775 | 386.2 | 419.9 | 518.7 | 260.2 | 534.7
997 | 776 | 386.8 | 419.6 | 517.8 | 260.5 | 535
998 | 777 | 387.3 | 423.5 | 509.7 | 260.7 | 534.6
999 | 778 | 387.8 | 431.1 | 511.4 | 261 | 534.2
1000 | 779 | 388.3 | 455.2 | 521.9 | 261.2 | 534.4
1001 | 780 | 388.9 | 459.2 | 537.3 | 261.5 | 534.9
1002 | 781 | 389.4 | 469.1 | 546.1 | 261.7 | 535.1
1003 | 782 | 389.9 | 464.1 | 554.3 | 262 | 535.6
1004 | 783 | 390.5 | 462.4 | 539.2 | 262.2 | 535
1005 | 784 | 391 | 469.2 | 526 | 262.5 | 533.4
1006 | 785 | 391.6 | 460.7 | 511.9 | 262.7 | 532.2
1007 | 786 | 392.1 | 453.9 | 505.7 | 263 | 531.3
1008 | 787 | 392.6 | 446.6 | 510.5 | 263.2 | 530.8
1009 | 788 | 393.2 | 441.6 | 515 | 263.5 | 531.5
1010 | 789 | 393.7 | 437.2 | 504.5 | 263.7 | 531.9
1011 | 790 | 394.3 | 431.9 | 497.8 | 264 | 531.2
1012 | 791 | 394.8 | 429 | 494.7 | 264.3 | 531
1013 | 792 | 395.4 | 427.5 | 495.8 | 264.5 | 531.6
1014 | 793 | 396 | 426.7 | 493.7 | 264.8 | 532.1
1015 | 794 | 396.5 | 426.8 | 495.7 | 265 | 532.9
1016 | 795 | 397.1 | 427.7 | 501.7 | 265.3 | 534.8
1017 | 796 | 397.7 | 429.4 | 525 | 265.6 | 538.2
1018 | 797 | 398.3 | 432.4 | 550.1 | 265.8 | 539.8
1019 | 798 | 398.8 | 435.5 | 567.9 | 266.1 | 541
1020 | 799 | 399.4 | 437.1 | 561.9 | 266.3 | 541.3
1021 | 800 | 400 | 444.5 | 566.8 | 266.6 | 542.1
1022 | 801 | 400.7 | 447.5 | 568.9 | 266.9 | 543
1023 | 802 | 401.3 | 446.9 | 557.4 | 267.1 | 543.3
1024 | 803 | 402 | 448.1 | 542.3 | 267.4 | 542.5
1025 | 804 | 402.6 | 443.9 | 533 | 267.7 | 542
1026 | 805 | 403.3 | 439.7 | 524 | 267.9 | 539.8
1027 | 806 | 404 | 436.6 | 516.1 | 268.2 | 538.3
1028 | 807 | 404.7 | 431.1 | 505.4 | 268.5 | 536.8
1029 | 808 | 405.4 | 426.5 | 499.2 | 268.7 | 535
1030 | 809 | 406.1 | 424.7 | 490.5 | 269 | 533.5
1031 | 810 | 406.8 | 422.5 | 486.1 | 269.3 | 532.3
1032 | 811 | 407.6 | 420.3 | 490.4 | 269.5 | 531.2
1033 | 812 | 408.3 | 418.1 | 487.2 | 269.8 | 530.1
1034 | 813 | 409 | 416.5 | 484.1 | 270 | 529.5
1035 | 814 | 409.7 | 414 | 477 | 270.3 | 528.4
1036 | 815 | 410.4 | 409.9 | 473.9 | 270.5 | 527.3
1037 | 816 | 411.2 | 407.5 | 470.8 | 270.8 | 526.9
1038 | 817 | 411.9 | 404.9 | 467.3 | 271.1 | 526.3
1039 | 818 | 412.6 | 404.2 | 466.4 | 271.3 | 525.2
1040 | 819 | 413.4 | 403.1 | 464 | 271.6 | 524.6
1041 | 820 | 414.1 | 403.2 | 461.4 | 271.8 | 523.7
1042 | 821 | 414.8 | 405.1 | 464.7 | 272.1 | 523.5
1043 | 822 | 415.6 | 411.6 | 481 | 272.3 | 523.6
1044 | 823 | 416.3 | 425.7 | 504.4 | 272.6 | 524.6
1045 | 824 | 417.1 | 434.4 | 529.1 | 272.8 | 526.1
1046 | 825 | 417.8 | 434 | 547 | 273.1 | 527.8
1047 | 826 | 418.6 | 435.1 | 556.6 | 273.3 | 529.3
1048 | 827 | 419.3 | 437.5 | 559.4 | 273.5 | 530.1
1049 | 828 | 420.1 | 438.2 | 549.9 | 273.8 | 530.5
1050 | 829 | 420.9 | 434.6 | 544.9 | 274 | 530
1051 | 830 | 421.6 | 430 | 532.6 | 274.2 | 529.6
1052 | 831 | 422.4 | 426 | 527.9 | 274.4 | 529.2
1053 | 832 | 423.2 | 421 | 520.8 | 274.7 | 528.5
1054 | 833 | 424 | 419.1 | 514.4 | 274.9 | 527.5
1055 | 834 | 424.8 | 415.3 | 515 | 275.1 | 526.8
1056 | 835 | 425.6 | 412.8 | 506.8 | 275.3 | 525.9
1057 | 836 | 426.4 | 411.6 | 496.3 | 275.5 | 525
1058 | 837 | 427.2 | 411.5 | 495 | 275.7 | 524.6
1059 | 838 | 427.9 | 412.3 | 495.7 | 275.9 | 524.1
1060 | 839 | 428.7 | 414.1 | 486.5 | 276.1 | 522.7
1061 | 840 | 429.5 | 413.6 | 479.8 | 276.3 | 521.5
1062 | 841 | 430.3 | 415.2 | 473.5 | 276.5 | 520.3
1063 | 842 | 431.1 | 417 | 469.1 | 276.7 | 519
1064 | 843 | 431.9 | 424.4 | 473 | 276.9 | 518.1
1065 | 844 | 432.7 | 435.5 | 489.7 | 277.1 | 518.3
1066 | 845 | 433.4 | 438.4 | 507.1 | 277.3 | 519.3
1067 | 846 | 434.2 | 438 | 506.9 | 277.4 | 519.7
1068 | 847 | 435 | 454 | 499.8 | 277.6 | 519
1069 | 848 | 435.7 | 467.6 | 490.3 | 277.8 | 518.2
1070 | 849 | 436.5 | 478.5 | 484.3 | 278 | 518.4
1071 | 850 | 437.3 | 481.5 | 480.5 | 278.1 | 518.6
1072 | 851 | 438 | 474.7 | 477.9 | 278.3 | 518.4
1073 | 852 | 438.8 | 468.5 | 476 | 278.5 | 517.9
1074 | 853 | 439.6 | 460.9 | 471.5 | 278.7 | 517.2
1075 | 854 | 440.3 | 456.4 | 470.5 | 278.8 | 517.5
1076 | 855 | 441.1 | 452.1 | 464.8 | 279 | 517.3
1077 | 856 | 441.9 | 446.8 | 462.6 | 279.2 | 517.1
1078 | 857 | 442.7 | 444.8 | 466.5 | 279.4 | 517.1
1079 | 858 | 443.5 | 442.9 | 464.3 | 279.6 | 516.9
1080 | 859 | 444.3 | 438.4 | 459.6 | 279.7 | 516.2
1081 | 860 | 445.2 | 434.9 | 466.3 | 279.9 | 515.2
1082 | 861 | 446 | 433.4 | 466.2 | 280.1 | 514.7
1083 | 862 | 446.9 | 430.3 | 471.2 | 280.3 | 514.4
1084 | 863 | 447.8 | 427.4 | 476.1 | 280.5 | 514.7
1085 | 864 | 448.7 | 425.5 | 477 | 280.7 | 515.4
1086 | 865 | 449.7 | 423.3 | 481.3 | 280.9 | 515.6
1087 | 866 | 450.8 | 422.7 | 483.2 | 281.1 | 515.6
1088 | 867 | 451.9 | 420.9 | 480.6 | 281.3 | 516.2
1089 | 868 | 453.2 | 419.6 | 483.3 | 281.5 | 516.3
1090 | 869 | 454.8 | 417.6 | 484.8 | 281.7 | 516
1091 | 870 | 456.4 | 413.9 | 479.1 | 281.9 | 515.1
1092 | 871 | 458.4 | 411.5 | 479.2 | 282.1 | 514.2
1093 | 872 | 460.7 | 411.5 | 478.3 | 282.3 | 513.5
1094 | 873 | 462.9 | 412 | 475.5 | 282.5 | 512.8
1095 | 874 | 465 | 410.8 | 474.7 | 282.7 | 512.1
1096 | 875 | 467 | 409.2 | 472.1 | 282.9 | 511.3
1097 | 876 | 468.8 | 409.9 | 483.4 | 283.1 | 511.1
1098 | 877 | 470.6 | 413.8 | 507 | 283.3 | 512.8
1099 | 878 | 472.3 | 415.9 | 522.1 | 283.5 | 513.8
1100 | 879 | 474 | 422.7 | 537 | 283.7 | 514.6
1101 | 880 | 475.8 | 424.6 | 544.7 | 283.9 | 514.9
1102 | 881 | 477.3 | 423.7 | 534.8 | 284.1 | 515
1103 | 882 | 478.8 | 420.9 | 530.8 | 284.3 | 514.6
1104 | 883 | 480.3 | 421.7 | 544.6 | 284.5 | 516.7
1105 | 884 | 481.7 | 423.3 | 535.8 | 284.7 | 518.2
1106 | 885 | 482.8 | 423.3 | 520.4 | 285 | 517.6
1107 | 886 | 483.8 | 422.1 | 506.5 | 285.2 | 516.5
1108 | 887 | 484.6 | 420 | 495.9 | 285.4 | 515.2
1109 | 888 | 485.3 | 419.7 | 489.6 | 285.6 | 514.8
1110 | 889 | 486 | 417.9 | 481.9 | 285.8 | 514.6
1111 | 890 | 486.8 | 417.1 | 482.4 | 286 | 514.7
1112 | 891 | 487.7 | 417.3 | 488.9 | 286.2 | 515.4
1113 | 892 | 488.7 | 416.2 | 498.6 | 286.4 | 516.3
1114 | 893 | 489.5 | 418.1 | 508.3 | 286.7 | 516.8
1115 | 894 | 490.6 | 418.4 | 524 | 286.9 | 518
1116 | 895 | 491.8 | 417 | 522.3 | 287.1 | 518.1
1117 | 896 | 492.9 | 415.6 | 515.9 | 287.3 | 517.5
1118 | 897 | 494 | 413.7 | 511.4 | 287.6 | 516.8
1119 | 898 | 494.8 | 413.1 | 510.3 | 287.8 | 516.3
1120 | 899 | 495.9 | 412.4 | 512 | 288 | 516
1121 | 900 | 496.9 | 411.5 | 503.6 | 288.2 | 516.5
1122 | 901 | 498 | 411.6 | 506.8 | 288.5 | 516.2
1123 | 902 | 499.3 | 413.9 | 512.9 | 288.7 | 516.2
1124 | 903 | 500.5 | 413.7 | 511.6 | 288.9 | 516.1
1125 | 904 | 501.6 | 414.3 | 503.1 | 289.2 | 516.1
1126 | 905 | 502.2 | 414.1 | 501.4 | 289.4 | 516.4
1127 | 906 | 502.9 | 414.3 | 504.7 | 289.6 | 517.4
1128 | 907 | 503.8 | 416.9 | 519 | 289.9 | 518.6
1129 | 908 | 505 | 419.2 | 523.1 | 290.1 | 519
1130 | 909 | 506.1 | 422.1 | 530.7 | 290.4 | 518.6
1131 | 910 | 507.1 | 426.2 | 537.6 | 290.6 | 518.8
1132 | 911 | 508.1 | 430.2 | 541.9 | 290.8 | 519.1
1133 | 912 | 509.4 | 430.8 | 543 | 291.1 | 518.8
1134 | 913 | 510.7 | 429.9 | 546 | 291.3 | 519
1135 | 914 | 511.7 | 430.1 | 544.3 | 291.6 | 518.4
1136 | 915 | 512.7 | 430.8 | 543.1 | 291.8 | 518.5
1137 | 916 | 513.7 | 430.5 | 540.6 | 292 | 518.8
1138 | 917 | 514.4 | 427.4 | 530 | 292.3 | 518.1
1139 | 918 | 515 | 425.5 | 527 | 292.5 | 517.5
1140 | 919 | 515.7 | 424.6 | 534.7 | 292.8 | 517.5
1141 | 920 | 516.4 | 423.7 | 533 | 293 | 517.8
1142 | 921 | 517.1 | 422.4 | 531.8 | 293.3 | 517.8
1143 | 922 | 517.7 | 422.7 | 528.8 | 293.5 | 517.5
1144 | 923 | 518.5 | 423.5 | 528.7 | 293.8 | 517.3
1145 | 924 | 519.3 | 426.8 | 537.9 | 294.1 | 517.4
1146 | 925 | 519.9 | 425.3 | 542.4 | 294.3 | 517.3
1147 | 926 | 520.4 | 426.7 | 549.7 | 294.6 | 517.7
1148 | 927 | 521 | 428.5 | 548.3 | 294.8 | 517.5
1149 | 928 | 521.6 | 430 | 543.2 | 295.1 | 516.9
1150 | 929 | 522.2 | 430.3 | 541.2 | 295.4 | 516.4
1151 | 930 | 522.6 | 431.3 | 537.4 | 295.6 | 516.5
1152 | 931 | 522.8 | 430.2 | 526.2 | 295.9 | 515.5
1153 | 932 | 523.1 | 428.8 | 520.7 | 296.2 | 514.4
1154 | 933 | 523.4 | 427.5 | 519.1 | 296.4 | 513.6
1155 | 934 | 523.8 | 427.7 | 526.5 | 296.7 | 513.3
1156 | 935 | 524.3 | 426.7 | 524.3 | 297 | 513
1157 | 936 | 524.8 | 423.8 | 513.9 | 297.2 | 512.2
1158 | 937 | 525.5 | 422.3 | 517.3 | 297.5 | 511.6
1159 | 938 | 526.1 | 421.1 | 513.9 | 297.8 | 511.8
1160 | 939 | 526.6 | 419.6 | 511.2 | 298.1 | 511.3
1161 | 940 | 527.2 | 419.1 | 513.8 | 298.3 | 510.5
1162 | 941 | 527.7 | 418.1 | 513 | 298.6 | 510.3
1163 | 942 | 528.2 | 418.3 | 516.3 | 298.9 | 509.9
1164 | 943 | 528.6 | 418.1 | 521.4 | 299.2 | 509.5
1165 | 944 | 528.9 | 417.9 | 529.8 | 299.4 | 509.1
1166 | 945 | 529.1 | 416.7 | 521.7 | 299.7 | 508.6
1167 | 946 | 529.3 | 415.5 | 513.9 | 300 | 508.5
1168 | 947 | 529.6 | 414.9 | 508.5 | 300.3 | 508
1169 | 948 | 529.9 | 414.6 | 506.4 | 300.6 | 507.3
1170 | 949 | 530.2 | 414.1 | 503.3 | 300.9 | 507.2
1171 | 950 | 530.6 | 412.5 | 501.2 | 301.2 | 507.3
1172 | 951 | 530.9 | 409.5 | 496.3 | 301.5 | 507.3
1173 | 952 | 531.1 | 406.9 | 486.3 | 301.7 | 506.7
1174 | 953 | 531.6 | 404.2 | 485.8 | 302 | 506.1
1175 | 954 | 532 | 403.5 | 492.4 | 302.3 | 505.5
1176 | 955 | 532.6 | 403.6 | 497.8 | 302.6 | 505.8
1177 | 956 | 533.2 | 405.3 | 505 | 302.9 | 506.7
1178 | 957 | 533.8 | 407.7 | 514.1 | 303.2 | 508.7
1179 | 958 | 534.5 | 410.5 | 518.2 | 303.5 | 509.8
1180 | 959 | 535 | 412.2 | 523.5 | 303.8 | 511
1181 | 960 | 535.6 | 413.3 | 519.7 | 304.1 | 512.1
1182 | 961 | 536.2 | 412.5 | 516.6 | 304.4 | 512.8
1183 | 962 | 536.7 | 411.1 | 504.2 | 304.7 | 511.6
1184 | 963 | 535.7 | 409.2 | 492.7 | 305.1 | 510.8
1185 | 964 | 534.8 | 409.3 | 494.8 | 305.4 | 510
1186 | 965 | 534.7 | 410.3 | 503.1 | 305.7 | 510
1187 | 966 | 534.7 | 412 | 514.6 | 306 | 509.5
1188 | 967 | 534.9 | 412.5 | 519.9 | 306.3 | 509.4
1189 | 968 | 535.3 | 414 | 539.4 | 306.6 | 510.8
1190 | 969 | 535.8 | 415.3 | 549.3 | 306.9 | 512.5
1191 | 970 | 536.4 | 417.4 | 553.2 | 307.2 | 513.9
1192 | 971 | 537.1 | 419.6 | 559.6 | 307.5 | 515.8
1193 | 972 | 537.8 | 426.1 | 572.7 | 307.8 | 517.9
1194 | 973 | 538.8 | 428.5 | 574 | 308.2 | 518.9
1195 | 974 | 539.8 | 431 | 574.3 | 308.5 | 519.2
1196 | 975 | 540.7 | 433.8 | 581.1 | 308.8 | 519.3
1197 | 976 | 541.7 | 439.4 | 588.3 | 309.1 | 519.4
1198 | 977 | 542.7 | 442.8 | 597.3 | 309.4 | 519.8
1199 | 978 | 543.6 | 446.5 | 612.8 | 309.8 | 521.7
1200 | 979 | 544.6 | 451.6 | 625.7 | 310.1 | 524.1
1201 | 980 | 545.6 | 464.2 | 647.4 | 310.4 | 526.8
1202 | 981 | 546.6 | 475.1 | 656.8 | 310.7 | 528.6
1203 | 982 | 547.5 | 476 | 656 | 311.1 | 529.2
1204 | 983 | 548.3 | 476 | 639.7 | 311.4 | 529.4
1205 | 984 | 549 | 478.7 | 620.7 | 311.7 | 528.6
1206 | 985 | 549.7 | 477.3 | 602.9 | 312 | 527.3
1207 | 986 | 550.3 | 474.3 | 589.7 | 312.4 | 526.2
1208 | 987 | 550.8 | 470.3 | 572 | 312.7 | 525.2
1209 | 988 | 551.3 | 468.9 | 558.4 | 313.1 | 524.5
1210 | 989 | 551.6 | 463.4 | 545.9 | 313.4 | 523.4
1211 | 990 | 551.9 | 458 | 541.5 | 313.8 | 523.4
1212 | 991 | 552.1 | 451.9 | 530.9 | 314.1 | 522.8
1213 | 992 | 552.4 | 449.1 | 528.3 | 314.5 | 522.3
1214 | 993 | 552.7 | 446.1 | 521.5 | 314.8 | 522.4
1215 | 994 | 552.9 | 442.3 | 510.9 | 315.2 | 521.5
1216 | 995 | 553.2 | 440.9 | 504.5 | 315.5 | 521.1
1217 | 996 | 553.4 | 438.7 | 495 | 315.9 | 520
1218 | 997 | 553.8 | 435.2 | 488.8 | 316.3 | 519
1219 | 998 | 554 | 431.2 | 485.7 | 316.6 | 518.5
1220 | 999 | 554.3 | 427.2 | 479.7 | 317 | 517.7
1221 | 1000 | 554.5 | 424 | 472.5 | 317.4 | 516.6
1222 | 1001 | 554.6 | 421.7 | 463.4 | 317.7 | 515.2
1223 | 1002 | 554.7 | 417.7 | 454.2 | 318.1 | 513.5
1224 | 1003 | 554.9 | 414.6 | 449.7 | 318.5 | 512.4
1225 | 1004 | 555 | 411.8 | 443 | 318.9 | 511
1226 | 1005 | 555.4 | 411 | 448.3 | 319.2 | 510.3
1227 | 1006 | 555.9 | 415.4 | 466.7 | 319.6 | 510.8
1228 | 1007 | 556.5 | 423.5 | 496.9 | 320 | 512.6
1229 | 1008 | 557.2 | 437.1 | 538.6 | 320.4 | 515
1230 | 1009 | 558 | 448.8 | 570.4 | 320.7 | 518.5
1231 | 1010 | 558.8 | 459.7 | 599.3 | 321.1 | 522.4
1232 | 1011 | 559.5 | 472.3 | 605.6 | 321.5 | 525
1233 | 1012 | 560.2 | 469.3 | 610.5 | 321.9 | 526.2
1234 | 1013 | 560.9 | 465.7 | 593.4 | 322.3 | 526.5
1235 | 1014 | 561.7 | 462.2 | 587 | 322.7 | 525.5
1236 | 1015 | 562.3 | 459.4 | 581.2 | 323.1 | 524.9
1237 | 1016 | 563.1 | 454.7 | 576.8 | 323.5 | 525
1238 | 1017 | 563.8 | 451.4 | 564.6 | 323.9 | 524.3
1239 | 1018 | 564.4 | 446.6 | 555.6 | 324.3 | 523.8
1240 | 1019 | 565.1 | 447 | 545.4 | 324.7 | 524
1241 | 1020 | 565.6 | 447.9 | 541.1 | 325.1 | 523.8
1242 | 1021 | 566 | 445.6 | 534 | 325.5 | 524.1
1243 | 1022 | 566.5 | 441.3 | 526.4 | 325.9 | 523.6
1244 | 1023 | 566.9 | 438.7 | 515.6 | 326.4 | 522.8
1245 | 1024 | 567.2 | 436.1 | 504 | 326.8 | 521.8
1246 | 1025 | 567.4 | 431.3 | 490.4 | 327.2 | 520.6
1247 | 1026 | 567.5 | 429.3 | 481 | 327.7 | 519.6
1248 | 1027 | 567.6 | 428 | 473.5 | 328.1 | 518.9
1249 | 1028 | 567.6 | 424.7 | 464.9 | 328.5 | 517.5
1250 | 1029 | 567.7 | 422.5 | 457.9 | 329 | 516.3
1251 | 1030 | 567.7 | 421.4 | 452.5 | 329.4 | 515.3
1252 | 1031 | 567.6 | 418.9 | 445.2 | 329.9 | 514.1
1253 | 1032 | 567.5 | 417.2 | 440.4 | 330.3 | 512.7
1254 | 1033 | 567.3 | 415.1 | 433.5 | 330.8 | 511.3
1255 | 1034 | 567 | 413 | 429.1 | 331.2 | 509.9
1256 | 1035 | 566.7 | 413 | 423.4 | 331.7 | 508.7
1257 | 1036 | 566.2 | 414.2 | 419.2 | 332.2 | 507.9
1258 | 1037 | 565.8 | 416.1 | 428.8 | 332.7 | 508.1
1259 | 1038 | 565.6 | 416.7 | 440.6 | 333.1 | 508.4
1260 | 1039 | 565.5 | 417 | 436.8 | 333.6 | 508.2
1261 | 1040 | 565.2 | 417.8 | 430.3 | 334.1 | 507.5
1262 | 1041 | 565 | 417.4 | 427.7 | 334.6 | 506.8
1263 | 1042 | 564.9 | 424.7 | 438 | 335.1 | 508
1264 | 1043 | 564.9 | 432.3 | 438.9 | 335.5 | 509
1265 | 1044 | 564.8 | 433.2 | 438.6 | 336 | 509.7
1266 | 1045 | 564.7 | 433.3 | 436.9 | 336.5 | 510.3
1267 | 1046 | 564.6 | 430.9 | 437.6 | 337 | 510
1268 | 1047 | 564.6 | 430.4 | 451.7 | 337.5 | 510.3
1269 | 1048 | 564.6 | 431.6 | 449.4 | 338 | 510.5
1270 | 1049 | 564.6 | 433 | 445.4 | 338.5 | 510.5
1271 | 1050 | 564.6 | 432.3 | 440 | 339.1 | 510.2
1272 | 1051 | 564.6 | 431.6 | 435.1 | 339.6 | 509.7
1273 | 1052 | 564.5 | 447.4 | 429.8 | 340.1 | 509.1
1274 | 1053 | 564.3 | 464.9 | 423.1 | 340.7 | 508
1275 | 1054 | 564.1 | 466.3 | 418.3 | 341.2 | 507
1276 | 1055 | 563.9 | 470.8 | 414.5 | 341.8 | 506.2
1277 | 1056 | 563.6 | 473.4 | 413.4 | 342.3 | 505.3
1278 | 1057 | 563.5 | 468.5 | 424.3 | 342.9 | 505.7
1279 | 1058 | 563.5 | 465.5 | 439.1 | 343.5 | 506.1
1280 | 1059 | 563.5 | 461.9 | 436.3 | 344 | 505.4
1281 | 1060 | 563.5 | 455.5 | 432.2 | 344.6 | 504.4
1282 | 1061 | 563.5 | 450.9 | 440.5 | 345.2 | 503.9
1283 | 1062 | 563.6 | 449.2 | 447.2 | 345.7 | 505.1
1284 | 1063 | 563.7 | 447.3 | 447.8 | 346.3 | 506.4
1285 | 1064 | 563.8 | 456.8 | 453.8 | 346.9 | 507.6
1286 | 1065 | 564.1 | 479.5 | 459.7 | 347.5 | 508.1
1287 | 1066 | 564.3 | 490.8 | 468.9 | 348.1 | 510.1
1288 | 1067 | 564.6 | 502.4 | 477.9 | 348.7 | 512.2
1289 | 1068 | 565 | 500.5 | 490.7 | 349.3 | 514.3
1290 | 1069 | 565.4 | 498.2 | 509.9 | 350 | 516.8
1291 | 1070 | 566 | 495.3 | 518.7 | 350.6 | 517.7
1292 | 1071 | 566.5 | 492.3 | 526.6 | 351.2 | 518.8
1293 | 1072 | 567.2 | 490.6 | 522.3 | 351.8 | 518.9
1294 | 1073 | 567.8 | 496.3 | 518.5 | 352.5 | 519.3
1295 | 1074 | 568.4 | 491.8 | 514.4 | 353.1 | 519.6
1296 | 1075 | 568.7 | 484.9 | 502.5 | 353.8 | 518.8
1297 | 1076 | 568.9 | 476.4 | 490.6 | 354.4 | 517.6
1298 | 1077 | 569.1 | 469.2 | 480.1 | 355.1 | 516.3
1299 | 1078 | 569.2 | 463.1 | 474.3 | 355.7 | 515.4
1300 | 1079 | 569.2 | 457.7 | 467.2 | 356.4 | 514.5
1301 | 1080 | 569.2 | 451.7 | 464.3 | 357 | 513.7
1302 | 1081 | 569.2 | 446.8 | 461.6 | 357.7 | 513.4
1303 | 1082 | 569.2 | 442.6 | 456.6 | 358.4 | 512.8
1304 | 1083 | 569.3 | 440.6 | 454.7 | 359 | 511.7
1305 | 1084 | 569.4 | 438.8 | 461.8 | 359.7 | 511.9
1306 | 1085 | 569.5 | 440.6 | 465.8 | 360.4 | 513.2
1307 | 1086 | 569.6 | 442.7 | 475.5 | 361.1 | 513.6
1308 | 1087 | 569.8 | 462.6 | 477.8 | 361.8 | 514.2
1309 | 1088 | 570 | 477.1 | 471 | 362.5 | 514
1310 | 1089 | 570.1 | 470.5 | 466.2 | 363.2 | 513.1
1311 | 1090 | 570.1 | 466 | 461.2 | 363.9 | 512.4
1312 | 1091 | 570.2 | 460.5 | 462.4 | 364.6 | 512.1
1313 | 1092 | 570.3 | 456 | 461.1 | 365.3 | 511.9
1314 | 1093 | 570.5 | 452.2 | 468.8 | 366 | 512.6
1315 | 1094 | 570.8 | 449.4 | 475.8 | 366.8 | 513.5
1316 | 1095 | 571 | 448.8 | 486.2 | 367.5 | 515
1317 | 1096 | 571.4 | 447.6 | 503 | 368.2 | 517.1
1318 | 1097 | 571.6 | 448 | 501.2 | 369 | 519
1319 | 1098 | 571.8 | 450.1 | 492.4 | 369.7 | 519
1320 | 1099 | 571.9 | 465.1 | 484.7 | 370.5 | 518.6
1321 | 1100 | 572 | 484.9 | 483 | 371.2 | 519.3
1322 | 1101 | 572.2 | 495.8 | 483.1 | 371.9 | 519.5
1323 | 1102 | 572.3 | 508.8 | 482.6 | 372.7 | 519.4
1324 | 1103 | 572.5 | 535 | 478.6 | 373.4 | 518.4
1325 | 1104 | 572.8 | 544.5 | 481.5 | 374.3 | 518.5
1326 | 1105 | 573.1 | 542 | 480.9 | 375 | 518.9
1327 | 1106 | 573.4 | 546.1 | 474.8 | 375.7 | 518.5
1328 | 1107 | 573.6 | 542.7 | 466.5 | 376.5 | 517.8
1329 | 1108 | 573.6 | 538.8 | 459.3 | 377.3 | 516.5
1330 | 1109 | 573.4 | 530.9 | 450.1 | 378.1 | 515.5
1331 | 1110 | 573.1 | 524.9 | 443 | 378.8 | 514.3
1332 | 1111 | 572.7 | 538.2 | 437.7 | 379.6 | 513.5
1333 | 1112 | 572.4 | 554 | 434.3 | 380.3 | 513.4
1334 | 1113 | 572.1 | 572.4 | 433 | 381.1 | 512.9
1335 | 1114 | 572.1 | 600.3 | 446.3 | 381.8 | 513.4
1336 | 1115 | 572.2 | 617.8 | 451.5 | 382.6 | 513.6
1337 | 1116 | 572.3 | 623.1 | 460.7 | 383.4 | 513.5
1338 | 1117 | 572.6 | 631.1 | 474.1 | 384.2 | 514.9
1339 | 1118 | 572.9 | 632.3 | 482.3 | 385 | 515.8
1340 | 1119 | 573.3 | 638.6 | 495.1 | 385.8 | 516.7
1341 | 1120 | 573.6 | 655.3 | 491.2 | 386.7 | 517.3
1342 | 1121 | 573.9 | 663.1 | 484 | 387.6 | 517.4
1343 | 1122 | 574 | 660 | 479 | 388.5 | 517.7
1344 | 1123 | 574 | 657.1 | 474 | 389.4 | 519
1345 | 1124 | 574 | 664.7 | 472.8 | 390.4 | 518.9
1346 | 1125 | 574.1 | 658.8 | 484.9 | 391.2 | 519.6
1347 | 1126 | 574.3 | 652.9 | 493.8 | 392.1 | 520.4
1348 | 1127 | 574.6 | 648.9 | 491 | 393.2 | 521
1349 | 1128 | 574.8 | 647 | 486.5 | 394.1 | 521
1350 | 1129 | 575.1 | 658.9 | 484.2 | 395.1 | 521
1351 | 1130 | 575.4 | 673.7 | 483.5 | 396 | 520.8
1352 | 1131 | 575.7 | 682.8 | 488 | 396.9 | 520.9
1353 | 1132 | 576.1 | 692 | 483.9 | 397.8 | 521.3
1354 | 1133 | 576.3 | 701.9 | 476.4 | 398.8 | 520.4
1355 | 1134 | 576.6 | 704.6 | 470.1 | 399.7 | 519.2
1356 | 1135 | 576.7 | 702.2 | 466 | 400.7 | 518.8
1357 | 1136 | 576.8 | 696.8 | 466.4 | 401.6 | 518.1
1358 | 1137 | 576.9 | 687.1 | 464.2 | 402.5 | 517.8
1359 | 1138 | 577 | 684.5 | 462.9 | 403.4 | 517.8
1360 | 1139 | 577 | 688.5 | 461.9 | 404.4 | 517.3
1361 | 1140 | 577.1 | 688.7 | 465.6 | 405.3 | 517.3
1362 | 1141 | 577.2 | 679.1 | 475.6 | 406.2 | 518.9
1363 | 1142 | 577.4 | 665.9 | 491.1 | 407.1 | 520.1
1364 | 1143 | 577.8 | 659.4 | 506.1 | 407.9 | 521.9
1365 | 1144 | 578.2 | 651.4 | 526 | 408.8 | 523.7
1366 | 1145 | 578.8 | 649.2 | 530.4 | 409.7 | 525.2
1367 | 1146 | 579.2 | 646.4 | 526.1 | 410.8 | 525.1
1368 | 1147 | 579.7 | 662.2 | 521.5 | 411.9 | 525
1369 | 1148 | 580.2 | 669.1 | 520 | 413 | 525
1370 | 1149 | 580.5 | 663.8 | 511.5 | 413.7 | 524.6
1371 | 1150 | 580.9 | 662.4 | 502.4 | 414.9 | 524.2
1372 | 1151 | 581.2 | 681 | 513 | 415.3 | 525.2
1373 | 1152 | 581.5 | 683.5 | 507.3 | 416.4 | 525.2
1374 | 1153 | 581.7 | 691 | 498.7 | 417.4 | 524.3
1375 | 1154 | 581.8 | 689.5 | 491.8 | 418.3 | 523.2
1376 | 1155 | 581.8 | 684.7 | 487 | 419.5 | 522.3
1377 | 1156 | 581.7 | 683.9 | 479.1 | 420.4 | 521.9
1378 | 1157 | 581.5 | 684.1 | 471.8 | 421.8 | 521.4
1379 | 1158 | 581.2 | 682.5 | 469.2 | 422.7 | 520.7
1380 | 1159 | 580.8 | 684.4 | 464.5 | 423.7 | 519.6
1381 | 1160 | 580.4 | 684.7 | 457.5 | 425 | 518.5
1382 | 1161 | 579.8 | 683.4 | 451.8 | 426.4 | 516.8
1383 | 1162 | 579.1 | 682.8 | 447.1 | 427.7 | 515.2
1384 | 1163 | 578.3 | 680.5 | 441.6 | 428.8 | 514
1385 | 1164 | 577.5 | 681 | 437.4 | 429.9 | 513.2
1386 | 1165 | 576.8 | 685.8 | 436.1 | 430.3 | 512.8
1387 | 1166 | 576.2 | 692.5 | 438.8 | 431.5 | 513.2
1388 | 1167 | 575.9 | 687.9 | 448.9 | 432.4 | 514.7
1389 | 1168 | 575.7 | 681.9 | 450.9 | 432.6 | 515
1390 | 1169 | 575.4 | 680.2 | 449.1 | 433.4 | 514.9
1391 | 1170 | 575.2 | 681.6 | 448.7 | 435 | 514.6
1392 | 1171 | 574.8 | 678.9 | 443.5 | 435.6 | 514.9
1393 | 1172 | 574.5 | 678.8 | 438.5 | 436.9 | 514.3
1394 | 1173 | 574.4 | 673 | 443.6 | 438.2 | 514.3
1395 | 1174 | 574.2 | 673 | 442.4 | 439.2 | 514.5
1396 | 1175 | 574.1 | 677.4 | 442.8 | 440.5 | 514.1
1397 | 1176 | 574.1 | 675.4 | 446 | 441.7 | 514.3
1398 | 1177 | 574.2 | 668.8 | 447.4 | 443 | 514.5
1399 | 1178 | 574.3 | 666.6 | 447 | 443.9 | 514.4
1400 | 1179 | 574.4 | 666.5 | 444.2 | 445.1 | 513.5
1401 | 1180 | 574.4 | 665.6 | 441.5 | 446 | 512.7
1402 | 1181 | 574.2 | 660.8 | 438.7 | 447 | 511.8
1403 | 1182 | 573.9 | 649.6 | 435.1 | 448 | 510.7
1404 | 1183 | 573.5 | 635.6 | 431.9 | 448.5 | 509.7
1405 | 1184 | 573 | 634.9 | 428.3 | 449.2 | 508.9
1406 | 1185 | 572.5 | 630.8 | 423.6 | 449.6 | 508
1407 | 1186 | 571.9 | 619.3 | 418 | 449.9 | 507.2
1408 | 1187 | 571.4 | 605.2 | 415.4 | 450.6 | 506.2
1409 | 1188 | 570.7 | 531.2 | 412.7 | 450.8 | 505.3
1410 | 1189 | 569.9 | 436 | 409.8 | 451.7 | 504.4
1411 | 1190 | 569.1 | 589.7 | 405.8 | 451.2 | 503.4
1412 | 1191 | 568.5 | 462.2 | 404.1 | 451.2 | 502.7
1413 | 1192 | 567.8 | 478.9 | 399.9 | 450.7 | 502.3
1414 | 1193 | 567.2 | 602 | 399.2 | 451.1 | 501.8
1415 | 1194 | 566.9 | 429.4 | 407.6 | 452 | 502.1
1416 | 1195 | 566.8 | 562.9 | 423.5 | 450.8 | 503.3
1417 | 1196 | 566.9 | 633.2 | 434.7 | 450.2 | 503.1
1418 | 1197 | 567.2 | 376.6 | 455.5 | 450.3 | 503.7
1419 | 1198 | 567.6 | 632.6 | 492.6 | 449.3 | 505.8
1420 | 1199 | 568.1 | 631.9 | 502.9 | 448 | 507.8
1421 | 1200 | 568.6 | 453.3 | 506.8 | 448 | 508.2
1422 | 1201 | 569.1 | 654.7 | 503.5 | 448.1 | 509.1
1423 | 1202 | 569.4 | 580.2 | 500.8 | 448.1 | 510
1424 | 1203 | 569.7 | 479.8 | 497.1 | 447.6 | 510.3
1425 | 1204 | 570.1 | 664.9 | 495.7 | 447 | 510.6
1426 | 1205 | 570.6 | 529.3 | 492 | 446.7 | 510.5
1427 | 1206 | 571.2 | 542.3 | 509.5 | 446.7 | 512.1
1428 | 1207 | 571.8 | 680.9 | 514 | 446.7 | 514.9
1429 | 1208 | 572.5 | 462.6 | 509 | 447.1 | 515.5
1430 | 1209 | 573.1 | 608 | 510.7 | 447.6 | 515.8
1431 | 1210 | 573.7 | 692.5 | 501 | 448 | 515.9
1432 | 1211 | 574 | 427.1 | 490 | 448.4 | 515.3
1433 | 1212 | 574.2 | 672.5 | 486 | 448.8 | 515
1434 | 1213 | 574.4 | 659.1 | 482.7 | 449.3 | 515.3
1435 | 1214 | 574.4 | 443.4 | 479.8 | 449.7 | 516.6
1436 | 1215 | 574.5 | 691.2 | 486.3 | 450.2 | 517.6
1437 | 1216 | 574.7 | 602.9 | 489.7 | 450.5 | 518.3
1438 | 1217 | 574.9 | 493.6 | 509.7 | 450.9 | 519.4
1439 | 1218 | 575.3 | 705.3 | 529.6 | 451.4 | 521.7
1440 | 1219 | 575.8 | 554.5 | 541 | 451.8 | 523
1441 | 1220 | 576.4 | 570.3 | 552.3 | 452.2 | 524.7
1442 | 1221 | 577 | 701.9 | 570 | 452.7 | 527.3
1443 | 1222 | 577.7 | 498.6 | 592 | 453.1 | 529.8
1444 | 1223 | 578.5 | 631.9 | 613.8 | 453.5 | 533
1445 | 1224 | 579.3 | 696.2 | 623.6 | 454 | 535.3
1446 | 1225 | 580.1 | 438.2 | 630.5 | 454.4 | 536.6
1447 | 1226 | 580.9 | 682 | 624.2 | 454.9 | 537.8
1448 | 1227 | 581.8 | 672.4 | 617.6 | 455.3 | 539.9
1449 | 1228 | 582.5 | 447.8 | 601.6 | 455.7 | 539.4
1450 | 1229 | 583.3 | 708 | 597.5 | 456.2 | 539.6
1451 | 1230 | 583.9 | 619.3 | 591.6 | 456.6 | 540.7
1452 | 1231 | 584.5 | 509.2 | 581.5 | 457.1 | 541.6
1453 | 1232 | 584.9 | 719.2 | 572.9 | 457.5 | 541.3
1454 | 1233 | 585.5 | 722.9 | 563.9 | 457.9 | 541
1455 | 1234 | 585.9 | 724.5 | 564.2 | 458.4 | 542.2
1456 | 1235 | 586.3 | 712.7 | 561.8 | 458.8 | 543.9
1457 | 1236 | 586.5 | 708.3 | 551.4 | 459.3 | 543.8
1458 | 1237 | 586.7 | 716.4 | 545.2 | 459.7 | 544.1
1459 | 1238 | 586.9 | 720.7 | 535.2 | 460.2 | 543.9
1460 | 1239 | 587.2 | 725 | 534.2 | 460.6 | 543.9
1461 | 1240 | 587.4 | 719.7 | 530.3 | 461.1 | 543.8
1462 | 1241 | 587.7 | 717.6 | 525.1 | 461.5 | 543
1463 | 1242 | 588 | 723.8 | 537 | 461.9 | 543.7
1464 | 1243 | 588.3 | 731.4 | 543.3 | 462.3 | 545.1
1465 | 1244 | 588.7 | 736.1 | 535.5 | 462.7 | 544.3
1466 | 1245 | 588.9 | 737.7 | 525.4 | 463.1 | 543.6
1467 | 1246 | 588.9 | 736.6 | 514.4 | 463.4 | 542.8
1468 | 1247 | 588.8 | 733.6 | 508.7 | 463.8 | 543.5
1469 | 1248 | 588.6 | 736.8 | 507.4 | 464.1 | 544.6
1470 | 1249 | 588.4 | 733.9 | 509.7 | 464.5 | 545.7
1471 | 1250 | 588.4 | 726.3 | 515.8 | 464.9 | 545.9
1472 | 1251 | 588.5 | 724.6 | 530.8 | 465.3 | 547.5
1473 | 1252 | 588.7 | 702.4 | 537.1 | 465.7 | 548.2
1474 | 1253 | 588.7 | 690.4 | 542.4 | 466.1 | 549
1475 | 1254 | 588.8 | 688.9 | 553.1 | 466.5 | 550.7
1476 | 1255 | 588.9 | 688.1 | 561.4 | 466.9 | 551.7
1477 | 1256 | 589.2 | 685.5 | 571.1 | 467.3 | 552.5
1478 | 1257 | 589.4 | 683.6 | 576.3 | 467.6 | 555.1
1479 | 1258 | 589.7 | 685 | 573.1 | 468 | 555.9
1480 | 1259 | 590 | 689 | 565.6 | 468.3 | 556
1481 | 1260 | 590.2 | 696.3 | 559.8 | 468.7 | 557.7
1482 | 1261 | 590.3 | 702.1 | 545.5 | 469.1 | 558.4
1483 | 1262 | 590.3 | 704.1 | 533.9 | 469.5 | 558.5
1484 | 1263 | 590.1 | 707.5 | 539 | 469.9 | 559.1
1485 | 1264 | 590 | 700.3 | 545.8 | 470.3 | 560.1
1486 | 1265 | 590 | 697.4 | 540.2 | 470.6 | 560.7
1487 | 1266 | 589.8 | 693 | 531.4 | 471 | 561.3
1488 | 1267 | 589.7 | 695.2 | 520.3 | 471.4 | 562.4
1489 | 1268 | 589.4 | 692.3 | 513.8 | 471.8 | 562.7
1490 | 1269 | 589 | 687.4 | 507.7 | 472.2 | 563.4
1491 | 1270 | 588.4 | 687.5 | 504 | 472.7 | 564.8
1492 | 1271 | 587.9 | 687.7 | 494.5 | 473.1 | 564.3
1493 | 1272 | 587.4 | 689.8 | 485.6 | 473.5 | 563.6
1494 | 1273 | 586.8 | 687 | 485.9 | 474 | 563.9
1495 | 1274 | 586.1 | 680.4 | 483 | 474.5 | 565.4
1496 | 1275 | 585.6 | 679.9 | 481.8 | 475 | 565.4
1497 | 1276 | 585.1 | 680.2 | 483.5 | 475.5 | 565.3
1498 | 1277 | 584.7 | 676.4 | 479.5 | 475.9 | 564.4
1499 | 1278 | 584.2 | 682.3 | 477.2 | 476.2 | 563.6
1500 | 1279 | 583.7 | 682.2 | 476.2 | 476.7 | 563.3
1501 | 1280 | 583.3 | 684.3 | 472.4 | 477.1 | 562.8
1502 | 1281 | 583 | 690.1 | 483.2 | 477.6 | 563.4
1503 | 1282 | 583 | 699 | 496 | 478 | 564.2
1504 | 1283 | 583.3 | 709.1 | 492 | 478.3 | 563.6
1505 | 1284 | 583.5 | 704.7 | 493.6 | 478.8 | 564
1506 | 1285 | 583.7 | 697.5 | 511.4 | 479.2 | 564.7
1507 | 1286 | 584 | 690.6 | 512 | 479.5 | 565
1508 | 1287 | 584.4 | 696.6 | 512.7 | 479.7 | 564.7
1509 | 1288 | 584.8 | 700.7 | 520.2 | 479.9 | 565.4
1510 | 1289 | 585.1 | 705.7 | 517.8 | 479.8 | 565.2
1511 | 1290 | 585.4 | 706.8 | 516.9 | 479.7 | 565.5
1512 | 1291 | 585.6 | 707.2 | 510.2 | 479.6 | 565.5
1513 | 1292 | 585.5 | 700.9 | 500.4 | 479.6 | 564.9
1514 | 1293 | 585.3 | 701.4 | 490.6 | 479.7 | 564.3
1515 | 1294 | 585.1 | 702.3 | 486.6 | 479.8 | 563.9
1516 | 1295 | 584.9 | 705.8 | 481.1 | 479.9 | 564.3
1517 | 1296 | 584.5 | 702.6 | 479.7 | 480.1 | 564.5
1518 | 1297 | 584.2 | 698.8 | 490.2 | 480.3 | 564.9
1519 | 1298 | 584.1 | 688.1 | 494.4 | 480.5 | 565.6
1520 | 1299 | 584 | 689.5 | 502 | 480.7 | 566
1521 | 1300 | 584.2 | 688.7 | 516.8 | 481 | 567.2
1522 | 1301 | 584.6 | 692.5 | 517.5 | 481.2 | 567.4
1523 | 1302 | 584.9 | 696.6 | 516.9 | 481.5 | 568
1524 | 1303 | 585.1 | 697.8 | 526.8 | 481.9 | 569.1
1525 | 1304 | 585.5 | 700.1 | 533.3 | 482.3 | 569.6
1526 | 1305 | 585.8 | 704.3 | 552.1 | 482.7 | 571.4
1527 | 1306 | 586.3 | 706.1 | 573.1 | 483.1 | 573.4
1528 | 1307 | 586.8 | 707.3 | 570 | 483.3 | 574
1529 | 1308 | 587.2 | 711.1 | 557.7 | 483.6 | 573.3
1530 | 1309 | 587.7 | 708.6 | 563 | 484 | 573.3
1531 | 1310 | 588.1 | 702 | 561.9 | 484.3 | 574.2
1532 | 1311 | 588.4 | 702.4 | 549.8 | 484.7 | 574.9
1533 | 1312 | 588.6 | 697.1 | 544.2 | 485.2 | 575.4
1534 | 1313 | 588.8 | 691.5 | 536.4 | 485.6 | 575.7
1535 | 1314 | 589.1 | 686.1 | 527.1 | 486 | 575.3
1536 | 1315 | 589.1 | 686.7 | 520.9 | 486.4 | 575.8
1537 | 1316 | 589.2 | 478.9 | 518.6 | 487 | 576.4
1538 | 1317 | 589.2 | 674.4 | 518 | 487.5 | 576
1539 | 1318 | 589.3 | 652.8 | 518.2 | 487.9 | 575.7
1540 | 1319 | 589.4 | 478.6 | 514.1 | 488.4 | 576.1
1541 | 1320 | 589.5 | 676.7 | 509.9 | 489 | 575.7
1542 | 1321 | 589.6 | 673.6 | 503 | 489.5 | 575.8
1543 | 1322 | 589.6 | 669.5 | 507.3 | 490 | 576.3
1544 | 1323 | 589.8 | 666.8 | 515.1 | 490.5 | 577.5
1545 | 1324 | 590 | 661.1 | 510.3 | 490.9 | 577.6
1546 | 1325 | 590.1 | 658 | 501.8 | 491.3 | 576
1547 | 1326 | 590.2 | 662.2 | 497.3 | 491.9 | 575.4
1548 | 1327 | 590 | 660.1 | 498.7 | 492.5 | 575.2
1549 | 1328 | 590 | 664.1 | 497 | 493.1 | 575
1550 | 1329 | 589.8 | 659.4 | 488.9 | 493.9 | 575.2
1551 | 1330 | 589.5 | 649.4 | 482.5 | 494.4 | 575.4
1552 | 1331 | 589.1 | 643.1 | 474.5 | 495 | 575.5
1553 | 1332 | 588.5 | 637.8 | 466.4 | 495.7 | 575.6
1554 | 1333 | 588 | 641.9 | 461.3 | 496.3 | 575.9
1555 | 1334 | 587.4 | 646.6 | 458.3 | 496.9 | 575.8
1556 | 1335 | 586.9 | 652.8 | 459.5 | 497.6 | 576.3
1557 | 1336 | 586.5 | 657.7 | 466.7 | 498 | 578.3
1558 | 1337 | 586.4 | 661.7 | 478.3 | 498.6 | 579.5
1559 | 1338 | 586.4 | 655.9 | 486.3 | 499.1 | 580.5
1560 | 1339 | 586.4 | 650 | 485.7 | 499.6 | 581.1
1561 | 1340 | 586.6 | 652.3 | 500 | 500.3 | 583
1562 | 1341 | 586.7 | 646.1 | 515 | 500.5 | 584.9
1563 | 1342 | 587.1 | 638.1 | 518.7 | 501.2 | 585.7
1564 | 1343 | 587.5 | 636.5 | 521.2 | 501.7 | 585.4
1565 | 1344 | 588.1 | 546.5 | 530.1 | 502 | 586.5
1566 | 1345 | 588.6 | 637 | 527.6 | 502.6 | 587.1
1567 | 1346 | 589.3 | 638.8 | 521.9 | 503.3 | 587.4
1568 | 1347 | 590 | 638.9 | 521.2 | 504 | 587.5
1569 | 1348 | 590.8 | 642.3 | 528.6 | 504.7 | 587.7
1570 | 1349 | 591.6 | 646.8 | 541.6 | 505.3 | 588.7
1571 | 1350 | 592.4 | 647.7 | 537.9 | 505.7 | 588.1
1572 | 1351 | 593.1 | 651.5 | 533.3 | 506.3 | 586.9
1573 | 1352 | 593.7 | 660.7 | 534.6 | 506.7 | 585.7
1574 | 1353 | 594.4 | 661.1 | 545.2 | 507.4 | 585.7
1575 | 1354 | 595.1 | 655.3 | 542.9 | 508.3 | 586.2
1576 | 1355 | 595.7 | 655 | 542.1 | 509.3 | 586.6
1577 | 1356 | 596.4 | 649.7 | 549 | 510.1 | 587.9
1578 | 1357 | 597 | 642.5 | 540.5 | 510.8 | 587.9
1579 | 1358 | 597.8 | 646.6 | 531.5 | 511.6 | 587.8
1580 | 1359 | 598.4 | 645.6 | 527.4 | 512.3 | 588.4
1581 | 1360 | 599.1 | 650.1 | 527.8 | 513 | 588.9
1582 | 1361 | 599.7 | 657.4 | 539.2 | 513.7 | 590.4
1583 | 1362 | 600.3 | 653.4 | 547 | 514.8 | 591.5
1584 | 1363 | 600.9 | 648.4 | 547.1 | 515.6 | 591.7
1585 | 1364 | 601.6 | 645.4 | 547.8 | 516.5 | 592.9
1586 | 1365 | 602 | 640.8 | 543 | 517.4 | 593.9
1587 | 1366 | 602.3 | 640 | 539.7 | 518.4 | 594.5
1588 | 1367 | 602.4 | 640 | 529.8 | 519.4 | 594.5
1589 | 1368 | 602.4 | 643.2 | 520.9 | 520.6 | 593.1
1590 | 1369 | 602.4 | 651.6 | 512.8 | 521.4 | 592.6
1591 | 1370 | 602.3 | 658.6 | 508.1 | 522.4 | 592.1
1592 | 1371 | 602.1 | 659.3 | 509.1 | 523.5 | 592.3
1593 | 1372 | 602 | 658.7 | 503.4 | 524.2 | 592.4
1594 | 1373 | 601.8 | 652 | 499.5 | 524.9 | 592.3
1595 | 1374 | 601.9 | 651.7 | 509 | 525.7 | 592.7
1596 | 1375 | 602.1 | 650 | 528.3 | 526.3 | 593.4
1597 | 1376 | 602.3 | 651 | 551.5 | 527.2 | 594.5
1598 | 1377 | 602.6 | 656.1 | 570.4 | 528.1 | 596.8
1599 | 1378 | 602.8 | 655.8 | 584.3 | 528.8 | 597.4
1600 | 1379 | 602.9 | 654.1 | 605 | 529.6 | 598.7
1601 | 1380 | 603.4 | 660 | 636.8 | 530.4 | 600.8
1602 | 1381 | 604.2 | 663.9 | 655.9 | 531.3 | 601.8
1603 | 1382 | 605.1 | 666.9 | 660.1 | 532.4 | 601.8
1604 | 1383 | 605.9 | 670.9 | 649 | 533.3 | 601.4
1605 | 1384 | 606.6 | 671.3 | 639.3 | 534.1 | 601.1
1606 | 1385 | 607.4 | 674 | 624.1 | 535 | 600.3
1607 | 1386 | 608 | 676.4 | 609.6 | 535.9 | 599.2
1608 | 1387 | 608.4 | 674.8 | 590.4 | 536.8 | 598.2
1609 | 1388 | 608.7 | 676.9 | 574.5 | 537.7 | 596.9
1610 | 1389 | 608.8 | 683.7 | 559.5 | 538.5 | 595.8
1611 | 1390 | 608.9 | 682.2 | 547.2 | 539.5 | 594.8
1612 | 1391 | 609.1 | 683.1 | 541.9 | 540.4 | 594.4
1613 | 1392 | 609.4 | 686.1 | 534.4 | 541.2 | 593.7
1614 | 1393 | 609.8 | 685.3 | 531 | 542 | 592.9
1615 | 1394 | 610.2 | 683.5 | 531.8 | 543.1 | 592.6
1616 | 1395 | 610.6 | 682.1 | 524.5 | 544.1 | 591.7
1617 | 1396 | 611.1 | 686.2 | 532.3 | 544.6 | 592.2
1618 | 1397 | 611.6 | 683.5 | 545.2 | 545.6 | 593.1
1619 | 1398 | 612.2 | 677.2 | 585.1 | 546.6 | 596.4
1620 | 1399 | 613.1 | 675.4 | 607.1 | 547.5 | 597.6
1621 | 1400 | 614 | 675.9 | 626 | 548.4 | 598.4
1622 | 1401 | 614.9 | 676.2 | 625.4 | 549 | 597.8
1623 | 1402 | 616 | 680.8 | 621.1 | 549.9 | 598
1624 | 1403 | 617.1 | 681.4 | 619.2 | 550.8 | 600.2
1625 | 1404 | 618.1 | 677.4 | 604.6 | 551.6 | 600.8
1626 | 1405 | 618.9 | 675.8 | 594.1 | 552.5 | 602.4
1627 | 1406 | 619.6 | 672.5 | 592.9 | 553.2 | 603.3
1628 | 1407 | 620.6 | 672.2 | 612.6 | 554 | 605.8
1629 | 1408 | 621.5 | 673.4 | 629.4 | 554.5 | 607.1
1630 | 1409 | 622.3 | 675 | 649.9 | 555.3 | 608.9
1631 | 1410 | 623.2 | 677.6 | 654.6 | 555.9 | 609.4
1632 | 1411 | 624.1 | 676.3 | 653.8 | 556.5 | 609.6
1633 | 1412 | 625 | 674.4 | 642.4 | 557.2 | 609.3
1634 | 1413 | 625.7 | 668.2 | 625.1 | 558.1 | 607.8
1635 | 1414 | 626.6 | 668.7 | 611 | 558.9 | 607
1636 | 1415 | 627.1 | 670.8 | 595.6 | 559.5 | 605.9
1637 | 1416 | 627.4 | 662.1 | 581.9 | 560.2 | 605
1638 | 1417 | 627.5 | 653.2 | 569.4 | 560.9 | 604.1
1639 | 1418 | 627.4 | 644.2 | 556.5 | 561.6 | 603
1640 | 1419 | 627.2 | 636 | 550.1 | 562.4 | 602.3
1641 | 1420 | 627.1 | 634 | 546.2 | 563.2 | 601.6
1642 | 1421 | 627.3 | 634.6 | 551.3 | 563.9 | 603.3
1643 | 1422 | 627.5 | 632.8 | 562.2 | 564.3 | 604.8
1644 | 1423 | 627.9 | 633.1 | 581.6 | 564.7 | 606.6
1645 | 1424 | 628.5 | 634.1 | 602.7 | 565.3 | 608.5
1646 | 1425 | 629.3 | 639.3 | 630.5 | 565.9 | 611.6
1647 | 1426 | 630.3 | 642.1 | 643.4 | 566.6 | 612.4
1648 | 1427 | 631.3 | 642.9 | 645.4 | 567.1 | 612.9
1649 | 1428 | 632.5 | 648 | 639.8 | 567.7 | 612
1650 | 1429 | 633.8 | 654.3 | 632 | 568.5 | 612.2
1651 | 1430 | 634.9 | 652.4 | 629.2 | 569.5 | 613
1652 | 1431 | 636 | 653.1 | 634.4 | 570.1 | 614
1653 | 1432 | 637.2 | 652.6 | 639.3 | 570.9 | 614.8
1654 | 1433 | 638.3 | 652.7 | 619.3 | 571.5 | 613.6
1655 | 1434 | 639.4 | 654.8 | 614.1 | 572.1 | 612.9
1656 | 1435 | 640.6 | 659.6 | 605.4 | 572.7 | 612.8
1657 | 1436 | 641.6 | 659 | 608.1 | 573.3 | 613.2
1658 | 1437 | 642.6 | 661.6 | 604.4 | 574 | 613.1
1659 | 1438 | 643.6 | 664.7 | 601.5 | 574.7 | 613.3
1660 | 1439 | 644.4 | 663.8 | 594.8 | 575.3 | 613.2
1661 | 1440 | 645.3 | 662.6 | 591 | 575.9 | 614.1
1662 | 1441 | 646.1 | 665 | 598.1 | 576.5 | 614.9
1663 | 1442 | 647 | 670.5 | 614.5 | 576.9 | 615.5
1664 | 1443 | 647.9 | 669.5 | 622 | 577.4 | 616.5
1665 | 1444 | 648.7 | 668.1 | 611.2 | 577.9 | 616.3
1666 | 1445 | 649.8 | 667.3 | 602 | 578.8 | 615.3
1667 | 1446 | 650.9 | 673.6 | 605.3 | 579.5 | 616
1668 | 1447 | 652 | 675.9 | 627.9 | 580.2 | 619
1669 | 1448 | 653 | 670.1 | 631 | 580.8 | 620.1
1670 | 1449 | 654 | 669.8 | 629.6 | 581.5 | 620.2
1671 | 1450 | 655 | 676.3 | 637.8 | 582 | 621.5
1672 | 1451 | 655.9 | 674.3 | 620.9 | 582.6 | 621.1
1673 | 1452 | 656.6 | 678.9 | 607.6 | 583.1 | 620
1674 | 1453 | 657.4 | 683.9 | 601.5 | 583.5 | 620.2
1675 | 1454 | 658.1 | 683.2 | 598.5 | 584.3 | 620.4
1676 | 1455 | 658.6 | 673.7 | 586.5 | 584.9 | 619
1677 | 1456 | 658.9 | 668.1 | 573.1 | 585.5 | 618.3
1678 | 1457 | 658.9 | 664.6 | 559.3 | 586.3 | 617.2
1679 | 1458 | 658.9 | 662.2 | 549.3 | 587.1 | 615.5
1680 | 1459 | 658.8 | 662.8 | 540.7 | 587.9 | 614.3
1681 | 1460 | 658.6 | 664.2 | 530.7 | 588.4 | 613
1682 | 1461 | 658.3 | 656.3 | 522.2 | 588.9 | 611.4
1683 | 1462 | 657.7 | 643.1 | 514.8 | 589.7 | 609.9
1684 | 1463 | 657 | 633.2 | 506.8 | 590.6 | 608.6
1685 | 1464 | 656.5 | 633 | 496.8 | 591.4 | 607.3
1686 | 1465 | 655.9 | 626.9 | 491.1 | 591.9 | 606.6
1687 | 1466 | 655.2 | 631 | 484.8 | 592.6 | 605.5
1688 | 1467 | 654.5 | 625 | 483.4 | 593.3 | 605.3
1689 | 1468 | 654.1 | 626.6 | 487.1 | 594.2 | 605.7
1690 | 1469 | 653.9 | 629.7 | 497.2 | 594.9 | 606.3
1691 | 1470 | 653.9 | 632.9 | 522.8 | 595.6 | 608.3
1692 | 1471 | 654.1 | 636.1 | 556.8 | 596 | 611.6
1693 | 1472 | 654.6 | 636.8 | 582.8 | 596.6 | 614.2
1694 | 1473 | 655.3 | 637.6 | 614.1 | 597.1 | 617.2
1695 | 1474 | 656.1 | 637.4 | 639.4 | 597.6 | 620.2
1696 | 1475 | 656.7 | 635.8 | 640.7 | 598.2 | 621.2
1697 | 1476 | 657.3 | 631.6 | 631.6 | 598.9 | 621.7
1698 | 1477 | 658.1 | 629.1 | 620.8 | 599.6 | 621.4
1699 | 1478 | 658.9 | 628.9 | 610.8 | 600.3 | 620.6
1700 | 1479 | 659.6 | 631.9 | 597.2 | 601 | 620.1
1701 | 1480 | 660.1 | 638.1 | 591.2 | 601.7 | 619.5
1702 | 1481 | 660.7 | 640.4 | 590.2 | 602.5 | 620.1
1703 | 1482 | 661.2 | 638.2 | 582.5 | 603.1 | 619.6
1704 | 1483 | 661.5 | 630.2 | 572 | 603.8 | 618.8
1705 | 1484 | 661.7 | 627.1 | 562.5 | 604.4 | 618.4
1706 | 1485 | 661.8 | 632.4 | 551.9 | 605.1 | 617.7
1707 | 1486 | 661.8 | 636.2 | 546.4 | 605.6 | 617
1708 | 1487 | 661.7 | 632.1 | 534.6 | 606.4 | 616.1
1709 | 1488 | 661.4 | 625.5 | 527 | 607 | 614.6
1710 | 1489 | 660.9 | 621.1 | 521 | 607.6 | 613.5
1711 | 1490 | 660.4 | 618.5 | 516 | 608.2 | 614.1
1712 | 1491 | 659.8 | 615.9 | 512.5 | 608.8 | 615.4
1713 | 1492 | 659.6 | 616.5 | 519.3 | 609.5 | 615.1
1714 | 1493 | 659.4 | 620.2 | 515.6 | 610 | 613.9
1715 | 1494 | 659.4 | 624.7 | 526.4 | 610.7 | 614.3
1716 | 1495 | 659.7 | 623.1 | 531.1 | 611.2 | 614
1717 | 1496 | 659.9 | 626 | 533.3 | 611.9 | 614.4
1718 | 1497 | 660.2 | 625.6 | 539.9 | 612.6 | 615.1
1719 | 1498 | 660.6 | 627.6 | 542.5 | 613.4 | 615.2
1720 | 1499 | 661.2 | 630.5 | 547.2 | 614 | 615.3
1721 | 1500 | 661.5 | 627.3 | 541.5 | 614.5 | 613.7
1722 | 1501 | 661.9 | 625.5 | 542.6 | 615.1 | 613.3
1723 | 1502 | 662.4 | 632.5 | 543.5 | 615.6 | 613.1
1724 | 1503 | 663.1 | 639.1 | 547.5 | 616.3 | 613.6
1725 | 1504 | 663.5 | 630.7 | 539.4 | 616.8 | 613.1
1726 | 1505 | 663.7 | 629.9 | 533.6 | 617.3 | 613
1727 | 1506 | 664.2 | 630.1 | 546 | 617.9 | 614.2
1728 | 1507 | 664.8 | 633.4 | 555.6 | 618.6 | 615.1
1729 | 1508 | 665.2 | 638.1 | 552.4 | 619.2 | 614.7
1730 | 1509 | 665.8 | 637.5 | 548.9 | 619.8 | 615.1
1731 | 1510 | 665.8 | 630.7 | 538.5 | 620.4 | 614.3
1732 | 1511 | 665.7 | 635 | 532.8 | 621.1 | 613.7
1733 | 1512 | 665.8 | 638.3 | 531.5 | 621.7 | 613.2
1734 | 1513 | 665.6 | 634.3 | 525 | 622.4 | 613.3
1735 | 1514 | 665.8 | 632.6 | 522 | 623 | 613
1736 | 1515 | 666 | 634.5 | 526.2 | 623.6 | 613.2
1737 | 1516 | 666.1 | 637.7 | 520.2 | 624.2 | 613.2
1738 | 1517 | 666.1 | 639.4 | 516.2 | 624.8 | 613.5
1739 | 1518 | 665.8 | 639.1 | 512.9 | 625.5 | 613.9
1740 | 1519 | 665.8 | 642.9 | 523.4 | 626.2 | 614.6
1741 | 1520 | 665.8 | 645.7 | 539.2 | 626.8 | 615.7
1742 | 1521 | 666.1 | 648.3 | 547.6 | 627.4 | 616.4
1743 | 1522 | 666.4 | 649.4 | 542.5 | 628 | 616.8
1744 | 1523 | 666.8 | 646.8 | 539.5 | 628.7 | 616.2
1745 | 1524 | 667.3 | 643.4 | 541 | 629.5 | 616.3
1746 | 1525 | 667.4 | 637.2 | 535.5 | 630.2 | 615.5
1747 | 1526 | 667.1 | 634.8 | 526.2 | 630.9 | 614.7
1748 | 1527 | 666.9 | 628.3 | 516.1 | 631.6 | 614.1
1749 | 1528 | 666.5 | 619.3 | 510.3 | 632.4 | 613.6
1750 | 1529 | 666.1 | 615.2 | 506.4 | 633.1 | 612
1751 | 1530 | 665.5 | 608.7 | 502.8 | 633.9 | 610.5
1752 | 1531 | 664.8 | 606.8 | 499.4 | 634.6 | 609.2
1753 | 1532 | 664.5 | 606.2 | 493.3 | 635.3 | 608.1
1754 | 1533 | 664 | 609.4 | 487.4 | 635.9 | 607.2
1755 | 1534 | 663.6 | 612.7 | 484.1 | 636.6 | 606.3
1756 | 1535 | 663.3 | 608.4 | 485.3 | 637.1 | 606
1757 | 1536 | 663.1 | 615.4 | 488.8 | 637.7 | 606
1758 | 1537 | 663.2 | 621 | 505.4 | 638.3 | 607.2
1759 | 1538 | 663.3 | 620.1 | 515.8 | 638.9 | 609.2
1760 | 1539 | 663.6 | 619.5 | 543.6 | 639.4 | 611.2
1761 | 1540 | 664 | 624.9 | 565.6 | 640 | 613.4
1762 | 1541 | 664.3 | 637.2 | 572.1 | 640.6 | 614.2
1763 | 1542 | 665 | 643.9 | 577.8 | 641.2 | 614.7
1764 | 1543 | 665.7 | 644.9 | 583 | 641.8 | 616.4
1765 | 1544 | 666.2 | 652.5 | 582.8 | 642.4 | 617.2
1766 | 1545 | 666.7 | 654.7 | 572.9 | 643.1 | 616.6
1767 | 1546 | 667 | 651.2 | 565.8 | 643.7 | 616.2
1768 | 1547 | 667.2 | 643.7 | 553.7 | 644.3 | 615.1
1769 | 1548 | 667.1 | 635 | 545.1 | 644.9 | 614.1
1770 | 1549 | 667 | 627.8 | 535.4 | 645.4 | 613.6
1771 | 1550 | 666.7 | 628.7 | 529.3 | 646 | 612.1
1772 | 1551 | 666.3 | 626.4 | 522.5 | 646.6 | 610.3
1773 | 1552 | 665.8 | 619.1 | 518.8 | 647.1 | 609.4
1774 | 1553 | 665.2 | 612.8 | 511.1 | 647.5 | 607.6
1775 | 1554 | 664.5 | 612.8 | 504.7 | 648.2 | 606
1776 | 1555 | 663.6 | 610.5 | 499.7 | 648.8 | 604.5
1777 | 1556 | 662.9 | 603.7 | 494.2 | 649.4 | 603.2
1778 | 1557 | 662.1 | 598.4 | 491.4 | 649.9 | 602.5
1779 | 1558 | 661.3 | 592.8 | 489.8 | 650.4 | 601.6
1780 | 1559 | 660.5 | 594.1 | 488.5 | 650.8 | 601.1
1781 | 1560 | 659.8 | 593.1 | 485.7 | 651.3 | 601.4
1782 | 1561 | 659.4 | 594.7 | 489.9 | 651.8 | 602.4
1783 | 1562 | 659.1 | 597.3 | 494.3 | 652.2 | 603.2
1784 | 1563 | 658.8 | 599.5 | 511.4 | 652.6 | 604.6
1785 | 1564 | 658.7 | 596.8 | 535.8 | 652.9 | 606.1
1786 | 1565 | 659 | 598.6 | 541.8 | 653.2 | 607.2
1787 | 1566 | 659.4 | 619.7 | 547.6 | 653.5 | 607.7
1788 | 1567 | 660.3 | 633 | 555.9 | 653.8 | 608.8
1789 | 1568 | 661.3 | 638 | 579.7 | 654.2 | 612.3
1790 | 1569 | 662.5 | 644.5 | 597.6 | 654.6 | 615.4
1791 | 1570 | 663.5 | 655.8 | 603.9 | 655 | 616
1792 | 1571 | 664.7 | 657.2 | 615.7 | 655.4 | 617.7
1793 | 1572 | 666 | 650.7 | 623.7 | 655.8 | 620.2
1794 | 1573 | 667.8 | 653.2 | 634.7 | 656.1 | 621.4
1795 | 1574 | 669.2 | 651.9 | 651.3 | 656.4 | 625.2
1796 | 1575 | 670.6 | 649.7 | 661.7 | 656.8 | 627
1797 | 1576 | 671.8 | 648.4 | 676.7 | 657.1 | 628.6
1798 | 1577 | 672.9 | 655.9 | 685.5 | 657.4 | 630.1
1799 | 1578 | 674 | 661.4 | 684.3 | 657.8 | 631.5
1800 | 1579 | 675 | 661 | 704.4 | 658.1 | 635.3
1801 | 1580 | 676.4 | 659.1 | 724.1 | 658.4 | 637.6
1802 | 1581 | 678 | 655.9 | 726.9 | 658.7 | 639.3
1803 | 1582 | 679.5 | 657.5 | 720.6 | 659 | 640
1804 | 1583 | 680.9 | 666.1 | 726.6 | 659.3 | 643.5
1805 | 1584 | 681.9 | 668.3 | 726.8 | 659.6 | 643.7
1806 | 1585 | 682.8 | 669.8 | 710.6 | 659.9 | 642.4
1807 | 1586 | 683.4 | 674.3 | 688.5 | 660.2 | 640.6
1808 | 1587 | 684.3 | 678.2 | 673.8 | 660.5 | 639.1
1809 | 1588 | 685.3 | 674.3 | 662.1 | 660.9 | 638.1
1810 | 1589 | 686.4 | 670.6 | 653 | 661.3 | 637.6
1811 | 1590 | 687.4 | 671.2 | 646.3 | 661.7 | 637.4
1812 | 1591 | 688 | 678.4 | 647.4 | 662 | 639.1
1813 | 1592 | 688.9 | 677.5 | 651.5 | 662.4 | 640.8
1814 | 1593 | 690.2 | 675.2 | 668.1 | 662.8 | 643.3
1815 | 1594 | 691.2 | 668.5 | 680.5 | 663.2 | 646.6
1816 | 1595 | 692.1 | 663.8 | 682.5 | 663.6 | 647.8
1817 | 1596 | 693.1 | 658.1 | 693 | 663.9 | 648.7
1818 | 1597 | 693.7 | 651.8 | 704.3 | 664.1 | 649.6
1819 | 1598 | 694.9 | 652.1 | 699 | 664.3 | 649.1
1820 | 1599 | 695.7 | 663.4 | 691.5 | 664.4 | 649.1
1821 | 1600 | 696.2 | 677.5 | 693.4 | 664.6 | 649.1
1822 | 1601 | 696.9 | 680.8 | 699.5 | 664.9 | 649.8
1823 | 1602 | 697.7 | 674 | 708.4 | 665.1 | 652.1
1824 | 1603 | 698.5 | 670.8 | 703.7 | 665.4 | 652.1
1825 | 1604 | 699.9 | 663 | 686.5 | 665.6 | 650.1
1826 | 1605 | 700.6 | 675.4 | 669.4 | 665.8 | 648.5
1827 | 1606 | 701.5 | 671.7 | 652.9 | 666.1 | 646.8
1828 | 1607 | 701.6 | 664.7 | 636 | 666.3 | 644.8
1829 | 1608 | 701.7 | 655.3 | 619.2 | 666.7 | 643.7
1830 | 1609 | 702.1 | 648.4 | 606.6 | 666.9 | 641.7
1831 | 1610 | 702.8 | 646.7 | 600.3 | 667.1 | 640.5
1832 | 1611 | 703.5 | 652.6 | 593.2 | 667.4 | 639.8
1833 | 1612 | 703.6 | 651.7 | 594.9 | 667.6 | 639.2
1834 | 1613 | 704 | 658.8 | 594.2 | 667.8 | 638.5
1835 | 1614 | 704 | 650.2 | 585.5 | 668 | 637.5
1836 | 1615 | 704.1 | 647.9 | 573.7 | 668.3 | 636.2
1837 | 1616 | 704.1 | 642.8 | 563.7 | 668.6 | 634.3
1838 | 1617 | 704.4 | 642.3 | 558.5 | 668.8 | 633.3
1839 | 1618 | 704.6 | 644.2 | 560 | 668.8 | 632.9
1840 | 1619 | 705.3 | 646.3 | 572.7 | 669 | 633
1841 | 1620 | 705.5 | 642.3 | 568.1 | 669.2 | 632.7
1842 | 1621 | 705.3 | 631.9 | 554.8 | 669.4 | 630.8
1843 | 1622 | 705.4 | 627.9 | 545.3 | 669.6 | 629.3
1844 | 1623 | 705.6 | 628.1 | 543.9 | 669.7 | 628.5
1845 | 1624 | 705.9 | 627.7 | 543.6 | 669.9 | 628.4
1846 | 1625 | 706.5 | 631.6 | 547.7 | 670 | 627.6
1847 | 1626 | 706.8 | 637.5 | 558.9 | 670.2 | 627.5
1848 | 1627 | 706.9 | 646.6 | 576.3 | 670.4 | 627.9
1849 | 1628 | 707.3 | 652.3 | 583.7 | 670.6 | 628.1
1850 | 1629 | 707.6 | 653.8 | 603 | 670.7 | 630.4
1851 | 1630 | 707.9 | 655.6 | 613.3 | 670.8 | 632.3
1852 | 1631 | 708.1 | 650 | 610 | 671 | 632.7
1853 | 1632 | 708.4 | 647.6 | 607 | 671.2 | 632.7
1854 | 1633 | 709 | 646.7 | 601 | 671.3 | 632
1855 | 1634 | 709 | 644.4 | 598 | 671.6 | 630.9
1856 | 1635 | 709.2 | 647.6 | 600 | 671.7 | 630.4
1857 | 1636 | 709.3 | 648.7 | 600.6 | 671.9 | 630.1
1858 | 1637 | 709.3 | 649.5 | 594.3 | 672 | 629
1859 | 1638 | 709.7 | 648.9 | 592.8 | 672.2 | 628.9
1860 | 1639 | 710 | 651.2 | 598.8 | 672.4 | 628.7
1861 | 1640 | 710.5 | 646.6 | 593.9 | 672.4 | 628.3
1862 | 1641 | 711.1 | 649.6 | 588 | 672.6 | 628
1863 | 1642 | 711.6 | 652.9 | 592.1 | 672.7 | 628.4
1864 | 1643 | 711.7 | 652.2 | 601.4 | 673 | 629.5
1865 | 1644 | 712 | 648.3 | 604.9 | 673.2 | 629.7
1866 | 1645 | 712.2 | 644.1 | 607.2 | 673.3 | 630.7
1867 | 1646 | 712.2 | 639.5 | 599.2 | 673.7 | 630.2
1868 | 1647 | 712.9 | 639.2 | 608.6 | 673.8 | 631.7
1869 | 1648 | 712.8 | 646.3 | 613.7 | 674 | 632.1
1870 | 1649 | 713.1 | 657.2 | 609.3 | 674.1 | 631.5
1871 | 1650 | 714.1 | 656 | 613.2 | 674.4 | 631.3
1872 | 1651 | 714.5 | 658.4 | 607 | 674.7 | 631.4
1873 | 1652 | 714.7 | 658.8 | 602.1 | 674.8 | 630.7
1874 | 1653 | 714.7 | 656.9 | 602 | 674.9 | 631.8
1875 | 1654 | 714.6 | 648.7 | 592.3 | 675.4 | 631.9
1876 | 1655 | 714.4 | 642.8 | 579.5 | 675.4 | 630.1
1877 | 1656 | 714.2 | 634.7 | 569.9 | 675.7 | 628.5
1878 | 1657 | 713.4 | 629.3 | 562.7 | 675.8 | 626.6
1879 | 1658 | 712.6 | 620.1 | 553 | 675.9 | 624.2
1880 | 1659 | 711.7 | 610.6 | 543.6 | 676.2 | 622
1881 | 1660 | 710.6 | 602.8 | 538.3 | 676.2 | 620.3
1882 | 1661 | 709.5 | 597 | 529.4 | 676.2 | 618.4
1883 | 1662 | 708.4 | 589.3 | 524.1 | 676.7 | 617.3
1884 | 1663 | 707.3 | 584.9 | 522.4 | 677 | 617.1
1885 | 1664 | 706.5 | 592.5 | 525.6 | 677.1 | 617.4
1886 | 1665 | 706.4 | 598 | 534.9 | 677.1 | 617.7
1887 | 1666 | 706.1 | 603.3 | 540.3 | 677.3 | 617.8
1888 | 1667 | 705.7 | 607.1 | 538.3 | 677.1 | 617.2
1889 | 1668 | 705.7 | 607.3 | 535.8 | 677.3 | 616.8
1890 | 1669 | 706 | 609.8 | 541.4 | 677.7 | 617
1891 | 1670 | 705.8 | 606.8 | 542.8 | 677.6 | 616.5
1892 | 1671 | 705.5 | 605.7 | 544.4 | 677.5 | 616.1
1893 | 1672 | 705.3 | 612.3 | 541.6 | 677.3 | 615.2
1894 | 1673 | 705.1 | 609.9 | 540.3 | 676.9 | 614.3
1895 | 1674 | 704.9 | 605.7 | 536.7 | 677.6 | 614.4
1896 | 1675 | 704.5 | 608.3 | 536.2 | 677.6 | 614.7
1897 | 1676 | 704.1 | 603.8 | 533.5 | 677.4 | 614
1898 | 1677 | 703.2 | 599.1 | 529 | 677 | 612.5
1899 | 1678 | 702.6 | 599.6 | 521.7 | 676.9 | 611
1900 | 1679 | 702 | 597.4 | 518.6 | 676.9 | 610.2
1901 | 1680 | 701.4 | 590.6 | 512.3 | 677.1 | 609.1
1902 | 1681 | 700.9 | 584.2 | 509.1 | 676.9 | 608.2
1903 | 1682 | 700.6 | 589.2 | 520.7 | 676.9 | 608.8
1904 | 1683 | 700.9 | 597.5 | 539.3 | 677.1 | 610.6
1905 | 1684 | 701.2 | 601.2 | 546.1 | 677.1 | 611.1
1906 | 1685 | 701.9 | 605.4 | 543.5 | 676.7 | 610.6
1907 | 1686 | 702.4 | 606.2 | 543.5 | 677.1 | 610.6
1908 | 1687 | 702.4 | 607.1 | 539.6 | 677.2 | 610.4
1909 | 1688 | 702.5 | 607.1 | 541 | 677.3 | 610.4
1910 | 1689 | 702.8 | 607.9 | 542 | 677.4 | 611.3
1911 | 1690 | 702.9 | 609.4 | 541.7 | 677.4 | 611.6
1912 | 1691 | 703.1 | 606.9 | 537.5 | 677.6 | 611.7
1913 | 1692 | 703.1 | 604.2 | 531.3 | 677.7 | 611.3
1914 | 1693 | 703 | 600.2 | 531.5 | 677.6 | 610.1
1915 | 1694 | 702.8 | 603 | 531 | 677.6 | 610.2
1916 | 1695 | 702.4 | 600.2 | 525.6 | 677.6 | 608.7
1917 | 1696 | 701.9 | 594.1 | 522.1 | 677.6 | 607.4
1918 | 1697 | 701.2 | 588.6 | 523.4 | 677.6 | 607.9
1919 | 1698 | 700.7 | 586.6 | 525.1 | 677.7 | 608.5
1920 | 1699 | 700.2 | 596.7 | 533.1 | 678 | 609.1
1921 | 1700 | 699.8 | 602.5 | 542.6 | 678.2 | 610
1922 | 1701 | 699.9 | 606.2 | 565.1 | 678.3 | 611.5
1923 | 1702 | 700.4 | 610.6 | 577.4 | 678.4 | 614.3
1924 | 1703 | 700.7 | 610 | 571 | 678.6 | 613.7
1925 | 1704 | 700.7 | 609.8 | 571.2 | 678.8 | 615.4
1926 | 1705 | 701 | 610.1 | 578.3 | 679 | 616.8
1927 | 1706 | 702.1 | 612.4 | 580.1 | 679.1 | 617.1
1928 | 1707 | 703 | 612.5 | 575.5 | 679.2 | 617.1
1929 | 1708 | 703.4 | 606.2 | 566.7 | 679.3 | 616.6
1930 | 1709 | 703.4 | 597.8 | 560.4 | 679.4 | 616.5
1931 | 1710 | 703.3 | 593.1 | 557.8 | 679.5 | 616.9
1932 | 1711 | 703.4 | 589.9 | 551.4 | 679.6 | 616.3
1933 | 1712 | 703.5 | 590.4 | 557.1 | 679.7 | 617.8
1934 | 1713 | 703.8 | 598.8 | 585.5 | 679.9 | 621.5
1935 | 1714 | 704.1 | 601.7 | 601.1 | 680 | 623.7
1936 | 1715 | 704.5 | 600.6 | 594 | 680.2 | 623.2
1937 | 1716 | 705.3 | 603.2 | 591.7 | 680.3 | 623.1
1938 | 1717 | 706 | 607.4 | 590.2 | 680.4 | 623.8
1939 | 1718 | 706.5 | 607.6 | 595.4 | 680.5 | 624.7
1940 | 1719 | 707.3 | 607.8 | 599.2 | 680.7 | 625.8
1941 | 1720 | 708.1 | 609.8 | 597.5 | 680.9 | 625.5
1942 | 1721 | 709 | 610.7 | 602.3 | 681 | 625.4
1943 | 1722 | 709.7 | 614.2 | 604.6 | 681 | 626.5
1944 | 1723 | 710.6 | 618.9 | 606.7 | 681.1 | 626.5
1945 | 1724 | 711.2 | 621.8 | 608.4 | 681.1 | 626.7
1946 | 1725 | 711.6 | 626 | 605.1 | 681.2 | 626.8
1947 | 1726 | 712.4 | 625.4 | 608.3 | 681.4 | 627.4
1948 | 1727 | 713.3 | 626 | 608.8 | 681.4 | 628.5
1949 | 1728 | 714.3 | 627.8 | 601.5 | 681.4 | 627.1
1950 | 1729 | 715.4 | 621.2 | 595.2 | 681.5 | 625.7
1951 | 1730 | 716.1 | 619.3 | 591.1 | 681.5 | 624.7
1952 | 1731 | 716.8 | 624 | 599.1 | 681.8 | 625.1
1953 | 1732 | 717.6 | 627.8 | 618.8 | 681.7 | 626.1
1954 | 1733 | 718.6 | 632.2 | 630.6 | 681.5 | 627.2
1955 | 1734 | 719.4 | 637.5 | 628.8 | 681.5 | 626.3
1956 | 1735 | 720.3 | 643.6 | 634 | 681.6 | 626.6
1957 | 1736 | 720.8 | 645.1 | 643.5 | 681.8 | 628.7
1958 | 1737 | 721.5 | 643.2 | 648.9 | 681.7 | 630.8
1959 | 1738 | 722.3 | 639.8 | 654.4 | 681.7 | 632.9
1960 | 1739 | 722.9 | 636.6 | 654.5 | 681.7 | 634.4
1961 | 1740 | 723.6 | 632.3 | 653 | 682 | 634.4
1962 | 1741 | 724.2 | 629.9 | 660.2 | 682.1 | 637
1963 | 1742 | 725 | 627.3 | 662.9 | 682.3 | 639.1
1964 | 1743 | 726.1 | 624.3 | 670.7 | 682.4 | 642.6
1965 | 1744 | 727 | 622.6 | 671.2 | 682.5 | 644
1966 | 1745 | 727.7 | 622.8 | 669.9 | 682.6 | 644.1
1967 | 1746 | 728.4 | 622.8 | 674.2 | 682.8 | 646.2
1968 | 1747 | 729 | 621.9 | 669.9 | 683 | 646.1
1969 | 1748 | 729.6 | 619.5 | 658.7 | 683.1 | 645.1
1970 | 1749 | 730.4 | 617.3 | 642.8 | 683.2 | 644.2
1971 | 1750 | 730.8 | 617.3 | 630.9 | 683.4 | 642.4
1972 | 1751 | 731.3 | 619 | 627.1 | 683.4 | 641.8
1973 | 1752 | 732 | 624.3 | 626.2 | 683.6 | 641.7
1974 | 1753 | 732.8 | 626 | 637.3 | 683.6 | 640.9
1975 | 1754 | 733.4 | 630.9 | 658.1 | 683.7 | 642.7
1976 | 1755 | 733.8 | 635.2 | 680.8 | 683.7 | 646.8
1977 | 1756 | 734.3 | 636.3 | 690.6 | 683.7 | 647.5
1978 | 1757 | 734.9 | 636.6 | 689 | 683.8 | 647.5
1979 | 1758 | 735.3 | 636.5 | 686.8 | 683.9 | 647.3
1980 | 1759 | 735.6 | 634.8 | 685.8 | 683.9 | 646.4
1981 | 1760 | 735.8 | 636.3 | 691.1 | 684 | 648
1982 | 1761 | 736.5 | 635.5 | 687.2 | 684 | 647.1
1983 | 1762 | 737.1 | 635.9 | 682.5 | 684 | 646.5
1984 | 1763 | 737.7 | 640.5 | 685.7 | 684.1 | 647
1985 | 1764 | 738.2 | 644.3 | 682.6 | 684.2 | 646.7
1986 | 1765 | 738.8 | 649.3 | 684.8 | 684.3 | 646.2
1987 | 1766 | 739.2 | 646.6 | 675.2 | 684.3 | 645.4
1988 | 1767 | 739.8 | 646.8 | 661.8 | 684.4 | 643.9
1989 | 1768 | 740.1 | 647.8 | 659.8 | 684.4 | 642.9
1990 | 1769 | 740.4 | 647 | 661.6 | 684.4 | 642.3
1991 | 1770 | 740.8 | 648.9 | 662.6 | 684.5 | 642.8
1992 | 1771 | 741.2 | 649.4 | 665.9 | 684.6 | 643.6
1993 | 1772 | 741.9 | 644.7 | 668.2 | 684.7 | 645.2
1994 | 1773 | 742.4 | 641.7 | 659 | 684.8 | 645.7
1995 | 1774 | 742.6 | 635.1 | 647.2 | 684.8 | 645.4
1996 | 1775 | 742.9 | 629.8 | 639.2 | 685 | 644.1
1997 | 1776 | 742.7 | 619.2 | 622.3 | 685 | 641.1
1998 | 1777 | 742 | 610.4 | 609.1 | 684.8 | 638.5
1999 | 1778 | 740.9 | 600.5 | 595.7 | 684.8 | 635.3
2000 | 1779 | 739.8 | 590.4 | 584.4 | 684.3 | 632.3
2001 | 1780 | 738.5 | 580.6 | 575.9 | 684.1 | 629.9
2002 | 1781 | 737.1 | 572.5 | 567.1 | 683.9 | 627.4
2003 | 1782 | 735.9 | 565.3 | 561.3 | 683.7 | 625.3
2004 | 1783 | 734.5 | 560.9 | 555.8 | 683.5 | 623.9
2005 | 1784 | 733.1 | 557.5 | 550.9 | 683.4 | 622.3
2006 | 1785 | 731.9 | 552.9 | 548.4 | 683.1 | 621.7
2007 | 1786 | 730.8 | 549.8 | 548.3 | 682.7 | 620.7
2008 | 1787 | 729.7 | 546 | 542.5 | 682.3 | 618.6
2009 | 1788 | 728.4 | 540.2 | 538.9 | 682.1 | 616.8
2010 | 1789 | 727.2 | 537 | 537.6 | 681.8 | 615.2
2011 | 1790 | 726.1 | 535 | 538.5 | 681.7 | 614.3
2012 | 1791 | 725 | 532.1 | 535.1 | 681.3 | 612.6
2013 | 1792 | 724.1 | 528.7 | 537.7 | 681.1 | 612
2014 | 1793 | 723.2 | 528 | 540.1 | 680.8 | 611.1
2015 | 1794 | 722.4 | 526.8 | 541 | 680.4 | 609.4
2016 | 1795 | 721.6 | 524.8 | 544.6 | 680 | 610
2017 | 1796 | 720.8 | 522.1 | 544.5 | 679.6 | 608.4
2018 | 1797 | 719.9 | 519.6 | 539.6 | 679.2 | 606.7
2019 | 1798 | 718.9 | 515.4 | 536.6 | 678.9 | 605.5
2020 | 1799 | 718 | 513.4 | 533.4 | 678.6 | 604.4
2021 | 1800 | 717.1 | 513.8 | 534.6 | 678.3 | 604
2022 | 1801 | 716.3 | 513.6 | 536.6 | 678 | 603.4
2023 | 1802 | 715.5 | 512.1 | 534.6 | 677.6 | 602.1
2024 | 1803 | 714.8 | 509.9 | 535 | 677.2 | 601.9
2025 | 1804 | 714.1 | 507.9 | 529 | 676.7 | 599.6
2026 | 1805 | 713.4 | 505 | 526.3 | 676.2 | 597.4
2027 | 1806 | 712.7 | 502.1 | 526.1 | 675.7 | 596.7
2028 | 1807 | 712.1 | 500.7 | 524.9 | 675.4 | 595.8
2029 | 1808 | 711.3 | 502 | 525.1 | 675 | 594.6
2030 | 1809 | 710.4 | 502.2 | 530.7 | 674.7 | 594
2031 | 1810 | 709.6 | 504.9 | 527.9 | 674.3 | 593.4
2032 | 1811 | 708.9 | 505.5 | 525.7 | 674 | 592.4
2033 | 1812 | 708.3 | 504.2 | 522 | 673.6 | 590.5
2034 | 1813 | 708 | 501.3 | 522.3 | 673.3 | 589.2
2035 | 1814 | 707.4 | 501.2 | 518.3 | 673 | 587.9
2036 | 1815 | 706.6 | 498.7 | 515.1 | 672.6 | 586.3
2037 | 1816 | 705.9 | 496.1 | 513.7 | 672.3 | 585
2038 | 1817 | 705.4 | 495.6 | 513.5 | 671.9 | 583.7
2039 | 1818 | 704.8 | 495.7 | 511.9 | 671.4 | 582.6
2040 | 1819 | 704.2 | 494.9 | 511.6 | 671.1 | 582.1
2041 | 1820 | 703.6 | 493.9 | 511.2 | 670.6 | 581.4
2042 | 1821 | 702.9 | 491.6 | 513.7 | 670.3 | 581.7
2043 | 1822 | 702.1 | 488.7 | 512.6 | 669.8 | 580.5
2044 | 1823 | 701.3 | 486 | 512.9 | 669.3 | 578.9
2045 | 1824 | 700.7 | 486.6 | 512.7 | 669 | 578.2
2046 | 1825 | 700.1 | 487.2 | 511.1 | 668.6 | 576.9
2047 | 1826 | 699.7 | 485.9 | 510.5 | 668.1 | 575.9
2048 | 1827 | 699.3 | 484.8 | 509.8 | 667.7 | 574.7
2049 | 1828 | 699 | 484.3 | 511.8 | 667.3 | 573.9
2050 | 1829 | 698.7 | 483.2 | 511.7 | 666.9 | 573
2051 | 1830 | 698.2 | 482.4 | 510 | 666.4 | 572.7
2052 | 1831 | 697.7 | 481.1 | 510.4 | 666 | 571.9
2053 | 1832 | 697.3 | 481.5 | 514.7 | 665.5 | 571.2
2054 | 1833 | 697.1 | 482.6 | 518 | 665.1 | 570.8
2055 | 1834 | 696.8 | 481.4 | 516 | 664.6 | 569.9
2056 | 1835 | 696.6 | 481.1 | 514.8 | 664.2 | 569.3
2057 | 1836 | 696.6 | 480.6 | 514.2 | 663.8 | 569.1
2058 | 1837 | 696.3 | 478.9 | 515.1 | 663.5 | 568.8
2059 | 1838 | 696 | 476.6 | 512.8 | 663.1 | 567.9
2060 | 1839 | 695.7 | 473.5 | 510.6 | 662.7 | 566.7
2061 | 1840 | 695.3 | 471.8 | 508.8 | 662.3 | 566
2062 | 1841 | 694.9 | 469 | 507.7 | 661.8 | 565.4
2063 | 1842 | 694.5 | 468.4 | 509.1 | 661.4 | 565.7
2064 | 1843 | 694.2 | 469.1 | 512.8 | 661.1 | 565.8
2065 | 1844 | 693.8 | 470.4 | 514.2 | 660.6 | 565.6
2066 | 1845 | 693.5 | 472 | 515.3 | 660.2 | 565.3
2067 | 1846 | 693.1 | 471.5 | 515 | 659.7 | 563.9
2068 | 1847 | 692.5 | 469.3 | 514.1 | 659.4 | 563.4
2069 | 1848 | 692 | 468.1 | 514.1 | 659.1 | 563.1
2070 | 1849 | 691.4 | 467.6 | 515 | 658.7 | 563.8
2071 | 1850 | 691.1 | 467.3 | 515.4 | 658.4 | 563.8
2072 | 1851 | 690.6 | 467.9 | 515.9 | 658 | 563.2
2073 | 1852 | 690.1 | 465.3 | 512.7 | 657.5 | 562
2074 | 1853 | 689.7 | 463.2 | 511.3 | 657.2 | 561.1
2075 | 1854 | 689.2 | 461.5 | 510.8 | 656.8 | 560.4
2076 | 1855 | 688.8 | 460.4 | 510 | 656.5 | 559.3
2077 | 1856 | 688.6 | 459.2 | 508.5 | 656.1 | 558.4
2078 | 1857 | 688.4 | 458.2 | 507.1 | 655.7 | 557.5
2079 | 1858 | 688 | 459 | 507.1 | 655.4 | 556.9
2080 | 1859 | 687.6 | 459.9 | 509.7 | 655.1 | 556.6
2081 | 1860 | 687.3 | 462 | 516.4 | 654.6 | 556.7
2082 | 1861 | 687 | 464.6 | 519.7 | 654.2 | 556.6
2083 | 1862 | 686.6 | 466.6 | 518.7 | 653.9 | 555.9
2084 | 1863 | 686.1 | 465.8 | 518.5 | 653.6 | 556
2085 | 1864 | 685.7 | 465.4 | 520.1 | 653.2 | 555.8
2086 | 1865 | 685.4 | 465.9 | 520.3 | 652.8 | 555.6
2087 | 1866 | 685.3 | 464.1 | 518.9 | 652.4 | 555.1
2088 | 1867 | 685 | 462.2 | 516.3 | 652.1 | 553.9
2089 | 1868 | 684.5 | 460.3 | 513.4 | 651.8 | 552.8
2090 | 1869 | 684.1 | 459.8 | 511.7 | 651.4 | 552.1
2091 | 1870 | 683.8 | 459.2 | 511.5 | 651 | 551.5
2092 | 1871 | 683.5 | 458.4 | 511.3 | 650.7 | 551
2093 | 1872 | 683.4 | 457.8 | 512.6 | 650.4 | 550.6
2094 | 1873 | 683.1 | 457.2 | 512.8 | 650 | 550.8
2095 | 1874 | 682.7 | 456.6 | 512.2 | 649.6 | 550.4
2096 | 1875 | 682.5 | 456.8 | 511.1 | 649.2 | 549.4
2097 | 1876 | 682.2 | 455.7 | 509.8 | 648.7 | 548.7
2098 | 1877 | 682.1 | 456.2 | 509.7 | 648.4 | 548.1
2099 | 1878 | 681.9 | 454.6 | 509.8 | 648 | 548
2100 | 1879 | 681.7 | 454.1 | 510 | 647.8 | 547.9
2101 | 1880 | 681.3 | 453 | 507.4 | 647.5 | 547.2
2102 | 1881 | 680.9 | 450.8 | 505 | 647.2 | 546.2
2103 | 1882 | 680.5 | 450.9 | 504.7 | 647.1 | 546.3
2104 | 1883 | 680.2 | 450.1 | 504.2 | 646.7 | 546.1
2105 | 1884 | 679.7 | 450.6 | 502.7 | 646.3 | 545.1
2106 | 1885 | 679.2 | 449.4 | 501.1 | 645.9 | 544
2107 | 1886 | 678.8 | 450.2 | 501.3 | 645.6 | 543.9
2108 | 1887 | 678.7 | 449.7 | 500.6 | 645.2 | 544.4
2109 | 1888 | 678.6 | 448.2 | 500.2 | 644.7 | 544.4
2110 | 1889 | 678.6 | 446.7 | 499.9 | 644.3 | 543.4
2111 | 1890 | 678.6 | 445.6 | 497 | 643.9 | 543.8
2112 | 1891 | 678.1 | 444.1 | 495.5 | 643.4 | 543
2113 | 1892 | 677.6 | 442.2 | 492.6 | 643 | 542.1
2114 | 1893 | 677.2 | 439.3 | 491.4 | 642.7 | 541.7
2115 | 1894 | 676.7 | 437.7 | 490.4 | 642.3 | 541.7
2116 | 1895 | 676.2 | 437.3 | 489.9 | 641.9 | 541.5
2117 | 1896 | 675.9 | 436.3 | 489.7 | 641.6 | 541.4
2118 | 1897 | 675.6 | 435.6 | 489.2 | 641.4 | 540.8
2119 | 1898 | 675.3 | 434.8 | 488.6 | 641 | 540.4
2120 | 1899 | 675.1 | 435.5 | 487.1 | 640.6 | 539.4
2121 | 1900 | 674.6 | 435 | 488 | 640.3 | 539.4
2122 | 1901 | 674.2 | 434.1 | 488 | 639.9 | 539.4
2123 | 1902 | 673.8 | 432.7 | 487.8 | 639.6 | 539
2124 | 1903 | 673.4 | 431.7 | 490.7 | 639.3 | 538.6
2125 | 1904 | 673 | 431 | 490.3 | 639 | 538.9
2126 | 1905 | 672.8 | 430.4 | 490 | 638.7 | 537.7
2127 | 1906 | 672.7 | 428.9 | 489.4 | 638.3 | 537.8
2128 | 1907 | 672.3 | 426.9 | 492.2 | 637.9 | 538.9
2129 | 1908 | 671.9 | 427 | 491.4 | 637.5 | 538.6
2130 | 1909 | 671.5 | 427.4 | 490.2 | 637.1 | 537.9
2131 | 1910 | 671.1 | 429 | 488.7 | 636.6 | 537.1
2132 | 1911 | 670.6 | 429.6 | 488.5 | 636.2 | 537
2133 | 1912 | 670 | 429.1 | 488.1 | 635.8 | 536.5
2134 | 1913 | 669.4 | 428.5 | 486.3 | 635.4 | 535.5
2135 | 1914 | 668.8 | 428.1 | 484.2 | 635 | 535
2136 | 1915 | 668.1 | 427.2 | 483.1 | 634.5 | 534.2
2137 | 1916 | 667.5 | 426.3 | 481.6 | 634.2 | 534.4
2138 | 1917 | 667 | 425.1 | 480.7 | 633.8 | 533.6
2139 | 1918 | 666.4 | 424.6 | 480.6 | 633.5 | 533.1
2140 | 1919 | 665.9 | 423.4 | 481.7 | 633.2 | 532.6
2141 | 1920 | 665.7 | 421.3 | 481.9 | 632.9 | 531.9
2142 | 1921 | 665.7 | 420.8 | 481.7 | 632.5 | 532.2
2143 | 1922 | 665.5 | 421.5 | 479 | 632.2 | 531.5
2144 | 1923 | 665.1 | 420.9 | 477.6 | 631.8 | 530.2
2145 | 1924 | 664.6 | 419.7 | 475.6 | 631.5 | 529.6
2146 | 1925 | 664.2 | 418.2 | 473.8 | 631.2 | 529.1
2147 | 1926 | 663.8 | 417.4 | 472.1 | 630.8 | 527.9
2148 | 1927 | 663.4 | 415.4 | 470.8 | 630.4 | 527.8
2149 | 1928 | 663 | 415 | 470.3 | 630 | 528.3
2150 | 1929 | 662.7 | 414.5 | 468.2 | 629.6 | 527.6
2151 | 1930 | 662.4 | 413.7 | 468.5 | 629.2 | 527.7
2152 | 1931 | 662.2 | 413.1 | 469.2 | 628.8 | 527.1
2153 | 1932 | 662.1 | 411.7 | 469 | 628.4 | 526.7
2154 | 1933 | 661.7 | 410.9 | 468.1 | 628 | 526
2155 | 1934 | 661 | 409.3 | 467.7 | 627.5 | 525.7
2156 | 1935 | 660.4 | 408.5 | 466.6 | 627.2 | 525.6
2157 | 1936 | 660.1 | 407.9 | 466.6 | 626.8 | 525.1
2158 | 1937 | 659.7 | 408.1 | 464.6 | 626.4 | 524.4
2159 | 1938 | 659.1 | 406.8 | 463.3 | 626 | 523.9
2160 | 1939 | 658.5 | 407.1 | 462.7 | 625.6 | 523.3
2161 | 1940 | 657.9 | 407.2 | 463.8 | 625.2 | 523.1
2162 | 1941 | 657.6 | 406.4 | 465.7 | 624.8 | 523.4
2163 | 1942 | 657.3 | 405.6 | 465.4 | 624.4 | 522.7
2164 | 1943 | 656.6 | 406.3 | 464.6 | 624 | 522.1
2165 | 1944 | 655.9 | 405.2 | 463.7 | 623.7 | 521.7
2166 | 1945 | 655.3 | 404.2 | 463.4 | 623.4 | 521
2167 | 1946 | 654.7 | 403.6 | 464.3 | 623.1 | 520.6
2168 | 1947 | 654 | 404.8 | 466.5 | 622.8 | 520.8
2169 | 1948 | 653.4 | 406.4 | 466.9 | 622.6 | 520.4
2170 | 1949 | 652.8 | 406.2 | 468.1 | 622.4 | 520.3
2171 | 1950 | 652.3 | 407.2 | 469.2 | 622.2 | 520.1
2172 | 1951 | 651.8 | 408.8 | 470.4 | 622 | 519.8
2173 | 1952 | 651.3 | 408.3 | 470.8 | 621.8 | 519.6
2174 | 1953 | 650.8 | 408.5 | 471.5 | 621.6 | 519.3
2175 | 1954 | 650.6 | 408.4 | 471.6 | 621.4 | 518.9
2176 | 1955 | 650.2 | 407.5 | 471.6 | 621.2 | 518.4
2177 | 1956 | 649.8 | 407.6 | 471 | 621 | 517.4
2178 | 1957 | 649.4 | 407 | 471.3 | 620.8 | 517
2179 | 1958 | 649 | 406.8 | 470.9 | 620.6 | 517.3
2180 | 1959 | 648.5 | 407 | 470.5 | 620.4 | 516.7
2181 | 1960 | 647.9 | 406.1 | 471.5 | 620.2 | 516.6
2182 | 1961 | 647.5 | 407.7 | 471.4 | 620 | 516.3
2183 | 1962 | 647 | 408.7 | 471.4 | 619.8 | 515.9
2184 | 1963 | 646.5 | 409 | 471.1 | 619.6 | 514.9
2185 | 1964 | 646.1 | 408.9 | 470.4 | 619.4 | 514.3
2186 | 1965 | 645.8 | 409.2 | 469.9 | 619.1 | 514.2
2187 | 1966 | 645.4 | 409.7 | 467.8 | 618.8 | 513.4
2188 | 1967 | 645.1 | 407.4 | 466 | 618.5 | 512.5
2189 | 1968 | 644.8 | 405 | 464.2 | 618.1 | 511.7
2190 | 1969 | 644.8 | 403.2 | 462.3 | 617.8 | 511.2
2191 | 1970 | 644.7 | 402.4 | 459.8 | 617.4 | 510.3
2192 | 1971 | 644.6 | 400 | 459.2 | 617.1 | 510.1
2193 | 1972 | 644.6 | 398.8 | 458.5 | 616.8 | 510.6
2194 | 1973 | 644.6 | 398.2 | 457.9 | 616.4 | 510.4
2195 | 1974 | 644.4 | 398.9 | 457.1 | 616.1 | 510
2196 | 1975 | 644.2 | 398.3 | 456.9 | 615.9 | 509.4
2197 | 1976 | 643.8 | 398.5 | 456.6 | 615.6 | 508.8
2198 | 1977 | 643.5 | 398.3 | 456.4 | 615.4 | 510.1
2199 | 1978 | 643.1 | 398.7 | 457.2 | 615.2 | 510.1
2200 | 1979 | 642.8 | 397.6 | 457.2 | 615 | 509.4
2201 | 1980 | 642.5 | 397.3 | 455.7 | 614.7 | 509.5
2202 | 1981 | 642 | 396.3 | 454.2 | 614.5 | 509.3
2203 | 1982 | 641.5 | 394.5 | 453.2 | 614.2 | 508.6
2204 | 1983 | 640.9 | 393 | 453.1 | 613.9 | 508.2
2205 | 1984 | 640.5 | 392.6 | 453.1 | 613.6 | 508.2
2206 | 1985 | 640.1 | 393 | 453.7 | 613.3 | 507.9
2207 | 1986 | 639.7 | 393.3 | 454.1 | 613.1 | 508
2208 | 1987 | 639.2 | 393.1 | 453.9 | 612.9 | 508
2209 | 1988 | 638.8 | 393 | 453.5 | 612.7 | 507.8
2210 | 1989 | 638.3 | 392.7 | 452.9 | 612.5 | 507.4
2211 | 1990 | 637.8 | 391.3 | 452.2 | 612.3 | 507.2
2212 | 1991 | 637.3 | 391.1 | 451.9 | 612 | 506.9
2213 | 1992 | 636.9 | 391.3 | 451.4 | 611.7 | 506
2214 | 1993 | 636.5 | 391.8 | 450.5 | 611.4 | 505.4
2215 | 1994 | 636.1 | 391.1 | 451.2 | 611.1 | 504.7
2216 | 1995 | 635.6 | 390.7 | 451 | 610.9 | 504
2217 | 1996 | 635.2 | 390.2 | 450.9 | 610.6 | 503.5
2218 | 1997 | 634.7 | 388.9 | 449.9 | 610.4 | 502.6
2219 | 1998 | 634.3 | 388.3 | 449.5 | 610.2 | 501.9
2220 | 1999 | 633.9 | 387.6 | 450.1 | 610 | 501.4
2221 | 2000 | 633.4 | 386.8 | 450.3 | 609.7 | 500.9
2222 | 2001 | 633 | 386.6 | 450.7 | 609.4 | 500.5
2223 | 2002 | 632.8 | 387.1 | 450.9 | 609.2 | 500.1
2224 | 2003 | 632.6 | 387.6 | 450.5 | 609 | 499.8
2225 | 2004 | 632.5 | 388.4 | 450.6 | 608.7 | 499
2226 | 2005 | 632.2 | 388.3 | 452.5 | 608.5 | 499.2
2227 | 2006 | 632 | 387.8 | 452.4 | 608.3 | 499.5
2228 | 2007 | 631.8 | 388 | 451.7 | 608.1 | 499.9
2229 | 2008 | 631.7 | 387.7 | 451.4 | 607.9 | 500
2230 | 2009 | 631.6 | 387.6 | 450.4 | 607.7 | 499.8
2231 | 2010 | 631.4 | 386.7 | 449.9 | 607.4 | 499.4
2232 | 2011 | 631.3 | 386.7 | 450.1 | 607.2 | 499.3
2233 | 2012 | 631.1 | 386.9 | 451.6 | 607 | 499.1
2234 | 2013 | 631 | 386.1 | 450.9 | 606.7 | 499.5
2235 | 2014 | 630.8 | 385.7 | 449.9 | 606.5 | 499.4
2236 | 2015 | 630.6 | 385 | 449 | 606.3 | 499.6
2237 | 2016 | 630.5 | 384.5 | 448.2 | 606 | 499.2
2238 | 2017 | 630.3 | 383.7 | 448 | 605.7 | 499
2239 | 2018 | 630.2 | 383.8 | 447.2 | 605.5 | 498.9
2240 | 2019 | 630.3 | 384.7 | 446.6 | 605.2 | 499.1
2241 | 2020 | 630.3 | 384.7 | 447 | 605 | 498.5
2242 | 2021 | 630.4 | 383.9 | 447 | 604.7 | 497.8
2243 | 2022 | 630.5 | 383.1 | 447.3 | 604.5 | 498
2244 | 2023 | 630.5 | 382.5 | 446.2 | 604.2 | 498.8
2245 | 2024 | 630.5 | 382.4 | 444.9 | 603.9 | 498.5
2246 | 2025 | 630.5 | 381.5 | 445.6 | 603.7 | 498.3
2247 | 2026 | 630.3 | 381.4 | 444 | 603.4 | 497.8
2248 | 2027 | 630.1 | 379.8 | 441.8 | 603.1 | 496.6
2249 | 2028 | 629.9 | 378.4 | 440.4 | 602.8 | 495.6
2250 | 2029 | 629.5 | 377.4 | 438.4 | 602.5 | 494.7
2251 | 2030 | 629 | 375.5 | 436.9 | 602.2 | 493.6
2252 | 2031 | 628.4 | 373.5 | 435.2 | 601.9 | 492.6
2253 | 2032 | 627.8 | 373 | 434.2 | 601.6 | 491.7
2254 | 2033 | 627 | 373.1 | 433.5 | 601.4 | 490.8
2255 | 2034 | 626.3 | 372.2 | 433.1 | 601.1 | 490.1
2256 | 2035 | 625.6 | 371.6 | 433.7 | 600.9 | 489.9
2257 | 2036 | 625.2 | 371.8 | 434 | 600.7 | 489.3
2258 | 2037 | 624.8 | 371.7 | 433.6 | 600.6 | 488.8
2259 | 2038 | 624.5 | 372.2 | 433.2 | 600.4 | 488.3
2260 | 2039 | 624.1 | 371.4 | 432.8 | 600.3 | 487.6
2261 | 2040 | 623.7 | 371.8 | 433 | 600.2 | 487
2262 | 2041 | 623.3 | 372.2 | 433.1 | 600.1 | 486.6
2263 | 2042 | 623 | 372.6 | 431.9 | 599.9 | 485.9
2264 | 2043 | 622.7 | 372.6 | 431.3 | 599.7 | 485.3
2265 | 2044 | 622.5 | 372 | 430.8 | 599.5 | 484.8
2266 | 2045 | 622.2 | 370.8 | 429 | 599.3 | 484.4
2267 | 2046 | 621.9 | 370.2 | 428.9 | 599.1 | 484.2
2268 | 2047 | 621.6 | 370.7 | 429.8 | 599 | 483.8
2269 | 2048 | 621.5 | 371.3 | 430.7 | 598.9 | 483.6
2270 | 2049 | 621.3 | 371.5 | 430.7 | 598.8 | 483.2
2271 | 2050 | 621.4 | 372.4 | 432.2 | 598.7 | 483.1
2272 | 2051 | 621.4 | 373.1 | 431.4 | 598.5 | 482.6
2273 | 2052 | 621.2 | 373.1 | 430 | 598.3 | 481.9
2274 | 2053 | 621.1 | 370.8 | 428.3 | 598.1 | 481.3
2275 | 2054 | 620.9 | 367.9 | 426.3 | 597.8 | 481.1
2276 | 2055 | 620.6 | 366.2 | 426.4 | 597.6 | 480.8
2277 | 2056 | 620.1 | 364.4 | 425.8 | 597.3 | 480.3
2278 | 2057 | 619.6 | 362.9 | 425.1 | 597 | 479.7
2279 | 2058 | 619.1 | 362.5 | 424.4 | 596.8 | 479
2280 | 2059 | 618.9 | 360.7 | 424 | 596.6 | 478.7
2281 | 2060 | 618.9 | 360.2 | 423 | 596.4 | 478.1
2282 | 2061 | 618.8 | 360.3 | 422.1 | 596.2 | 477.8
2283 | 2062 | 618.5 | 359.3 | 420.4 | 595.9 | 477.4
2284 | 2063 | 618.1 | 359.3 | 419.2 | 595.7 | 477.5
2285 | 2064 | 617.9 | 358.8 | 418.7 | 595.4 | 477.1
2286 | 2065 | 617.6 | 359.2 | 417.8 | 595.2 | 476.4
2287 | 2066 | 617.3 | 358.4 | 416.9 | 595.1 | 475.8
2288 | 2067 | 617 | 358.2 | 416.2 | 594.9 | 475.4
2289 | 2068 | 616.6 | 357.7 | 415.5 | 594.8 | 475.2
2290 | 2069 | 616.1 | 357.3 | 415.5 | 594.7 | 474.8
2291 | 2070 | 615.7 | 357.7 | 414.8 | 594.5 | 474.5
2292 | 2071 | 615.3 | 356.2 | 413.7 | 594.4 | 473.9
2293 | 2072 | 614.8 | 355.6 | 414.3 | 594.2 | 473.6
2294 | 2073 | 614.4 | 356.3 | 414.9 | 594.1 | 473.3
2295 | 2074 | 614 | 356.1 | 415.1 | 594.1 | 473.2
2296 | 2075 | 613.7 | 356 | 415.3 | 593.9 | 472.8
2297 | 2076 | 613.2 | 356.1 | 414.5 | 593.8 | 472.3
2298 | 2077 | 612.8 | 354.8 | 412.8 | 593.6 | 472
2299 | 2078 | 612.3 | 353.3 | 412.8 | 593.4 | 471.5
2300 | 2079 | 611.9 | 352.5 | 411.7 | 593.2 | 471
2301 | 2080 | 611.7 | 352.2 | 410.9 | 593.1 | 470.5
2302 | 2081 | 611.6 | 351.3 | 411.4 | 593 | 470.7
2303 | 2082 | 611.6 | 351.8 | 413 | 592.9 | 471
2304 | 2083 | 611.6 | 352.4 | 412.9 | 592.8 | 470.3
2305 | 2084 | 611.6 | 351.9 | 412.1 | 592.6 | 469.6
2306 | 2085 | 611.4 | 352.2 | 411.7 | 592.4 | 469.2
2307 | 2086 | 611.1 | 352 | 410.7 | 592.3 | 468.5
2308 | 2087 | 610.8 | 351.2 | 410.1 | 592 | 467.9
2309 | 2088 | 610.5 | 351.5 | 408.4 | 591.8 | 467.4
2310 | 2089 | 610.3 | 351.1 | 407.3 | 591.6 | 467.2
2311 | 2090 | 610.1 | 350.3 | 405.8 | 591.3 | 467.3
2312 | 2091 | 609.7 | 350 | 405.1 | 591.1 | 467
2313 | 2092 | 609.2 | 349.5 | 405.1 | 591 | 466.4
2314 | 2093 | 608.7 | 348.7 | 404.6 | 590.8 | 466.1
2315 | 2094 | 608.3 | 346.9 | 403.7 | 590.6 | 465.9
2316 | 2095 | 608 | 345.7 | 403.3 | 590.4 | 465.9
2317 | 2096 | 607.7 | 345.2 | 402.8 | 590.3 | 465.6
2318 | 2097 | 607.4 | 344 | 402.9 | 590.1 | 465.2
2319 | 2098 | 607 | 344.4 | 402.8 | 589.9 | 464.8
2320 | 2099 | 606.5 | 345 | 402.6 | 589.8 | 464.3
2321 | 2100 | 605.9 | 345.8 | 402.6 | 589.6 | 464
2322 | 2101 | 605.4 | 345.5 | 401.8 | 589.5 | 463.2
2323 | 2102 | 605 | 345.7 | 401.4 | 589.3 | 462.8
2324 | 2103 | 604.6 | 344.6 | 401.6 | 589.2 | 462.4
2325 | 2104 | 604.2 | 344.3 | 402.1 | 589.1 | 461.9
2326 | 2105 | 603.9 | 344.2 | 402.5 | 589.1 | 461.6
2327 | 2106 | 603.5 | 343.8 | 402.4 | 589 | 461.3
2328 | 2107 | 603.3 | 343.9 | 402.1 | 588.9 | 460.8
2329 | 2108 | 602.9 | 344.4 | 401.8 | 588.9 | 460.3
2330 | 2109 | 602.5 | 344.2 | 402.1 | 588.9 | 459.6
2331 | 2110 | 602.2 | 344.9 | 401.9 | 588.8 | 459.1
2332 | 2111 | 601.9 | 345.7 | 401.8 | 588.6 | 458.5
2333 | 2112 | 601.7 | 346.5 | 401.8 | 588.5 | 458.1
2334 | 2113 | 601.5 | 346.4 | 402.3 | 588.4 | 457.8
2335 | 2114 | 601.4 | 346.6 | 401.9 | 588.5 | 457.4
2336 | 2115 | 601.3 | 346.6 | 401.4 | 588.5 | 456.8
2337 | 2116 | 601.2 | 347.9 | 401.5 | 588.4 | 456.4
2338 | 2117 | 601.1 | 347.7 | 400.7 | 588.3 | 456.4
2339 | 2118 | 600.9 | 346.4 | 400.5 | 588.2 | 455.6
2340 | 2119 | 600.7 | 346.1 | 399.6 | 588 | 455.1
2341 | 2120 | 600.4 | 345.9 | 399.6 | 587.8 | 454.9
2342 | 2121 | 600.1 | 346 | 400.2 | 587.6 | 454.5
2343 | 2122 | 599.7 | 345 | 400.6 | 587.5 | 454.2
2344 | 2123 | 599.3 | 344.2 | 400.4 | 587.4 | 453.6
2345 | 2124 | 599 | 343.5 | 400.2 | 587.4 | 453.4
2346 | 2125 | 598.6 | 343.9 | 399.5 | 587.3 | 452.7
2347 | 2126 | 598.2 | 344.3 | 399.2 | 587.2 | 452.3
2348 | 2127 | 597.9 | 344.2 | 398.7 | 587 | 452.3
2349 | 2128 | 597.7 | 342.9 | 398.3 | 586.8 | 452.3
2350 | 2129 | 597.4 | 342.6 | 398.1 | 586.7 | 452.3
2351 | 2130 | 597.1 | 342.8 | 397.8 | 586.6 | 452
2352 | 2131 | 596.9 | 342.5 | 397.3 | 586.6 | 451.9
2353 | 2132 | 596.7 | 342.3 | 397 | 586.4 | 451.6
2354 | 2133 | 596.6 | 343.3 | 396.5 | 586.2 | 451.6
2355 | 2134 | 596.4 | 343.3 | 396.7 | 586.1 | 451.6
2356 | 2135 | 596.1 | 343.7 | 396.9 | 586.1 | 451.4
2357 | 2136 | 595.9 | 342.2 | 397.1 | 586 | 451.2
2358 | 2137 | 595.7 | 341.6 | 396.3 | 586.2 | 451.2
2359 | 2138 | 595.6 | 340.4 | 396.9 | 586.2 | 451.2
2360 | 2139 | 595.5 | 340.5 | 397.2 | 586.2 | 450.6
2361 | 2140 | 595.3 | 341.2 | 396.7 | 586.3 | 450.2
2362 | 2141 | 595 | 340.6 | 395.9 | 586 | 449.8
2363 | 2142 | 594.8 | 340.4 | 396.1 | 585.9 | 449.6
2364 | 2143 | 594.4 | 340.9 | 396.4 | 585.8 | 449.3
2365 | 2144 | 594.1 | 341.2 | 397 | 585.6 | 448.9
2366 | 2145 | 593.8 | 339.9 | 397.2 | 585.5 | 448.7
2367 | 2146 | 593.6 | 338.9 | 396.7 | 585.4 | 448.2
2368 | 2147 | 593.5 | 339.3 | 396.5 | 585.3 | 447.8
2369 | 2148 | 593.5 | 340.3 | 395.9 | 585.2 | 447.4
2370 | 2149 | 593.3 | 340.8 | 395.6 | 585.1 | 446.8
2371 | 2150 | 593.1 | 340.5 | 395.9 | 585 | 446.8
2372 | 2151 | 592.9 | 341.7 | 397.1 | 584.9 | 446.5
2373 | 2152 | 592.6 | 341.6 | 397.1 | 584.8 | 446.1
2374 | 2153 | 592.5 | 341.2 | 396.5 | 584.7 | 445.8
2375 | 2154 | 592.5 | 342.4 | 395.7 | 584.7 | 445.4
2376 | 2155 | 592.3 | 342.8 | 396 | 584.5 | 445.4
2377 | 2156 | 592.1 | 342.7 | 396.2 | 584.6 | 445.4
2378 | 2157 | 591.8 | 341.6 | 395.8 | 584.5 | 445.5
2379 | 2158 | 591.6 | 341.8 | 395.4 | 584.4 | 445.2
2380 | 2159 | 591.5 | 341.2 | 395 | 584.4 | 445.3
2381 | 2160 | 591.4 | 340.9 | 394.2 | 584.2 | 444.9
2382 | 2161 | 591.2 | 341.4 | 394.2 | 584.2 | 444.9
2383 | 2162 | 591 | 342.1 | 394.4 | 584.2 | 444.6
2384 | 2163 | 590.7 | 343.2 | 394.6 | 584.1 | 444.3
2385 | 2164 | 590.5 | 342.8 | 394.4 | 583.9 | 444.1
2386 | 2165 | 590.3 | 341.2 | 393.5 | 583.8 | 444
2387 | 2166 | 590.1 | 339.5 | 392.7 | 583.8 | 443.6
2388 | 2167 | 589.9 | 338.4 | 391.5 | 583.7 | 443.2
2389 | 2168 | 589.8 | 338 | 391.6 | 583.7 | 443
2390 | 2169 | 589.7 | 336.3 | 390.8 | 583.7 | 442.6
2391 | 2170 | 589.8 | 336.8 | 389.7 | 583.6 | 442.2
2392 | 2171 | 589.9 | 335.5 | 389.1 | 583.6 | 441.7
2393 | 2172 | 589.9 | 335 | 389 | 583.7 | 441.4
2394 | 2173 | 589.9 | 337.9 | 389.6 | 583.7 | 441.4
2395 | 2174 | 589.9 | 338.1 | 389.7 | 583.8 | 441.3
2396 | 2175 | 590 | 338.8 | 390.1 | 583.9 | 441
2397 | 2176 | 590 | 338.8 | 390.5 | 583.7 | 441.1
2398 | 2177 | 590 | 338.9 | 390.2 | 583.5 | 441.1
2399 | 2178 | 590.1 | 339.2 | 389.7 | 583.4 | 441.2
2400 | 2179 | 590.1 | 339 | 389.6 | 583.5 | 441.2
2401 | 2180 | 589.9 | 338.9 | 389.8 | 583.4 | 440.8
2402 | 2181 | 589.8 | 339.1 | 389.2 | 583.3 | 440.8
2403 | 2182 | 589.7 | 339.6 | 389.8 | 583.2 | 440.8
2404 | 2183 | 589.7 | 339.8 | 390.6 | 583 | 440.8
2405 | 2184 | 589.5 | 340.1 | 391.1 | 582.8 | 440.4
2406 | 2185 | 589.4 | 340.5 | 391.5 | 582.7 | 440.1
2407 | 2186 | 589.1 | 340.6 | 391.7 | 582.8 | 440.2
2408 | 2187 | 588.9 | 339.8 | 391 | 582.7 | 440
2409 | 2188 | 588.6 | 339.5 | 391 | 582.8 | 439.6
2410 | 2189 | 588.3 | 340 | 390.5 | 582.7 | 439.4
2411 | 2190 | 588 | 339.8 | 391.4 | 582.7 | 439.1
2412 | 2191 | 587.8 | 340.8 | 392.6 | 582.7 | 438.7
2413 | 2192 | 587.6 | 340.9 | 392.1 | 582.8 | 438.3
2414 | 2193 | 587.4 | 340.1 | 391.4 | 582.6 | 437.8
2415 | 2194 | 587.2 | 338.1 | 390.2 | 582.5 | 437.3
2416 | 2195 | 586.9 | 338.2 | 390.6 | 582.6 | 437
2417 | 2196 | 586.6 | 338.9 | 390.1 | 582.6 | 437.1
2418 | 2197 | 586.2 | 338.9 | 389.7 | 582.7 | 437.1
2419 | 2198 | 585.8 | 339.1 | 390.5 | 582.9 | 436.8
2420 | 2199 | 585.6 | 341 | 391.1 | 582.9 | 436.9
2421 | 2200 | 585.4 | 340.9 | 390.8 | 582.6 | 436.8
2422 | 2201 | 585.2 | 341.9 | 391.1 | 582.2 | 436.3
2423 | 2202 | 585 | 341.6 | 391.1 | 582.1 | 436
2424 | 2203 | 584.8 | 341.5 | 390.5 | 582 | 435.7
2425 | 2204 | 584.7 | 341.8 | 389.6 | 582.2 | 435.4
2426 | 2205 | 584.6 | 342 | 390.3 | 582 | 435.4
2427 | 2206 | 584.4 | 340.9 | 390.6 | 581.8 | 435
2428 | 2207 | 584.3 | 342.2 | 390.5 | 581.6 | 435
2429 | 2208 | 584.2 | 343.5 | 390.9 | 581.2 | 434.8
2430 | 2209 | 584.1 | 344.9 | 390.4 | 581.3 | 434.4
2431 | 2210 | 584 | 345.9 | 389.4 | 581.3 | 434
2432 | 2211 | 583.9 | 345.1 | 389 | 581.4 | 433.8
2433 | 2212 | 583.8 | 344.5 | 389.1 | 581.5 | 433.6
2434 | 2213 | 583.7 | 345.3 | 389.1 | 581.4 | 433
2435 | 2214 | 583.7 | 344.8 | 389 | 581.4 | 432.5
2436 | 2215 | 583.6 | 344.7 | 388.4 | 581.4 | 432.4
2437 | 2216 | 583.5 | 344.1 | 387.8 | 581.3 | 432.1
2438 | 2217 | 583.4 | 344.3 | 387.4 | 581.2 | 431.6
2439 | 2218 | 583.2 | 344.5 | 387 | 581.2 | 431.1
2440 | 2219 | 583 | 343.9 | 386.7 | 581.1 | 430.8
2441 | 2220 | 582.8 | 343.3 | 386.1 | 580.9 | 430.6
2442 | 2221 | 582.4 | 342.5 | 385.5 | 580.9 | 430.6
2443 | 2222 | 582 | 342.1 | 385.5 | 580.9 | 430.3
2444 | 2223 | 581.5 | 340.4 | 385.6 | 580.7 | 430.3
2445 | 2224 | 581.2 | 339.5 | 385.8 | 580.2 | 430.2
2446 | 2225 | 580.9 | 340.7 | 385 | 580 | 429.7
2447 | 2226 | 580.6 | 338.9 | 383.8 | 579.8 | 429
2448 | 2227 | 580.4 | 337.8 | 382.3 | 579.9 | 428.6
2449 | 2228 | 580.4 | 337 | 381.5 | 580 | 428.2
2450.1 | 2229.1 | 580.4 | 337.8 | 381.3 | 580 | 427.9
2451.1 | 2230.1 | 580.5 | 337.8 | 379.7 | 580 | 427.4
2452.1 | 2231.1 | 580.5 | 336.2 | 379 | 580.1 | 427.2
2453.1 | 2232.1 | 580.4 | 334.5 | 377.6 | 580.2 | 426.9
2454.1 | 2233.1 | 580.2 | 332 | 376.7 | 580.3 | 426.6
2455.1 | 2234.1 | 579.9 | 331.1 | 376.7 | 580.1 | 426.4
2456.1 | 2235.1 | 579.6 | 331.5 | 376.1 | 579.8 | 426.2
2457.1 | 2236.1 | 579.3 | 331.2 | 375.9 | 579.6 | 425.9
2458.1 | 2237.1 | 579 | 330 | 375.9 | 579.6 | 425.4
2459.1 | 2238.1 | 578.7 | 330.3 | 375.3 | 579.5 | 425
2460.1 | 2239.1 | 578.5 | 330.8 | 374.7 | 579.4 | 424.8
2461.1 | 2240.1 | 578.4 | 332.1 | 375 | 579.1 | 424.4
2462.1 | 2241.1 | 578.1 | 332.6 | 374.9 | 579.2 | 424.2
2463.1 | 2242.1 | 577.9 | 333.2 | 375.5 | 579.3 | 423.9
2464.1 | 2243.1 | 577.6 | 334.3 | 375.3 | 579.2 | 423.9
2465.1 | 2244.1 | 577.5 | 333.4 | 375.3 | 578.9 | 423.6
2466.1 | 2245.1 | 577.4 | 333.8 | 375.2 | 578.6 | 423.3
2467.1 | 2246.1 | 577.3 | 333.5 | 375.2 | 578.2 | 423
2468.1 | 2247.1 | 577.2 | 332.2 | 375 | 577.9 | 422.6
2469.1 | 2248.1 | 577 | 332.1 | 375.1 | 578 | 422.5
2470.1 | 2249.1 | 576.8 | 332.9 | 374.9 | 578.2 | 422.1
2471.1 | 2250.1 | 576.7 | 332.3 | 374.4 | 578.1 | 422
2472.1 | 2251.1 | 576.5 | 332.6 | 373.7 | 577.8 | 421.6
2473.1 | 2252.1 | 576.4 | 332.8 | 373.1 | 578 | 421.3
2474.1 | 2253.1 | 576.2 | 332.3 | 372.9 | 578 | 421.2
2475.1 | 2254.1 | 575.9 | 332.1 | 373.3 | 578 | 421.1
2476.1 | 2255.1 | 575.6 | 331.5 | 374 | 577.8 | 420.7
2477.1 | 2256.1 | 575.3 | 333.2 | 373.6 | 577.8 | 420.5
2478.1 | 2257.1 | 575.1 | 332.1 | 373.8 | 577.7 | 420.3
2479.1 | 2258.1 | 574.9 | 331 | 373.2 | 577.5 | 420.1
2480.1 | 2259.1 | 574.7 | 330.2 | 372.9 | 577.4 | 419.9
2481.1 | 2260.1 | 574.5 | 330.1 | 372.9 | 577.4 | 419.5
2482.1 | 2261.1 | 574.2 | 328.8 | 373.3 | 577.2 | 419.4
2483.1 | 2262.1 | 573.9 | 328.7 | 373.4 | 577 | 418.9
2484.1 | 2263.1 | 573.7 | 330.2 | 373.5 | 576.9 | 418.7
2485.1 | 2264.1 | 573.4 | 330 | 373 | 577 | 418.3
2486.1 | 2265.1 | 573.1 | 328.3 | 372.4 | 576.9 | 418.4
2487.1 | 2266.1 | 572.8 | 326.3 | 371.9 | 576.8 | 418.3
2488.1 | 2267.1 | 572.5 | 325.4 | 371.4 | 576.8 | 417.9
2489.1 | 2268.1 | 572.3 | 326.4 | 370.8 | 576.4 | 417.7
2490.1 | 2269.1 | 572.2 | 326.7 | 369.6 | 576 | 417.1
2491.1 | 2270.1 | 572.1 | 325.4 | 368.9 | 575.8 | 416.6
2492.1 | 2271.1 | 572.2 | 323.5 | 368.3 | 575.4 | 416.5
2493.1 | 2272.1 | 572.2 | 321.6 | 368.5 | 575.5 | 416.5
2494.1 | 2273.1 | 572.1 | 321.1 | 368.6 | 575.5 | 416
2495.1 | 2274.1 | 571.9 | 322.3 | 369.2 | 575.5 | 415.7
2496.1 | 2275.1 | 571.7 | 322.8 | 369.2 | 575.5 | 415.4
2497.1 | 2276.1 | 571.5 | 323.1 | 369.2 | 575.7 | 414.9
2498.1 | 2277.1 | 571.1 | 321.8 | 369.3 | 575.8 | 414.7
2499.1 | 2278.1 | 570.8 | 320.6 | 369.5 | 575.6 | 414.5
2500.1 | 2279.1 | 570.5 | 321.1 | 369.1 | 575.5 | 414.1
2501.1 | 2280.1 | 570.2 | 321.1 | 368.2 | 575.3 | 413.8
2502.1 | 2281.1 | 570.1 | 319.8 | 366.8 | 575.3 | 413.7
2503.1 | 2282.1 | 570.1 | 319.5 | 365.8 | 575.2 | 413.5
2504.1 | 2283.1 | 570.2 | 319.3 | 365.7 | 575.1 | 413
2505.1 | 2284.1 | 570.2 | 319.9 | 364.8 | 575.1 | 412.8
2506.1 | 2285.1 | 570.3 | 320.6 | 364.4 | 574.8 | 412.5
2507.1 | 2286.1 | 570.3 | 321.3 | 364.9 | 574.3 | 412.3
2508.1 | 2287.1 | 570.2 | 322.1 | 364.7 | 574.1 | 411.9
2509.1 | 2288.1 | 570.1 | 322.4 | 364.3 | 574 | 411.4
2510.1 | 2289.1 | 570 | 322.3 | 364 | 573.9 | 410.8
2511.1 | 2290.1 | 570 | 321.4 | 362.9 | 573.8 | 410.5
2512.1 | 2291.1 | 570 | 320.9 | 362.1 | 574.1 | 410.2
2513.1 | 2292.1 | 570 | 321.1 | 361.8 | 573.9 | 410
2514.1 | 2293.1 | 570.1 | 320.4 | 361.3 | 573.7 | 409.7
2515.1 | 2294.1 | 570.1 | 319.2 | 361.2 | 573.8 | 409.2
2516.1 | 2295.1 | 569.9 | 318.8 | 360.9 | 573.7 | 408.9
2517.1 | 2296.1 | 569.8 | 318.9 | 360.3 | 573.4 | 409
2518.1 | 2297.1 | 569.6 | 319 | 359.9 | 573.4 | 408.8
2519.1 | 2298.1 | 569.4 | 319.3 | 359.5 | 573 | 408.4
2520.1 | 2299.1 | 569.2 | 320.5 | 359.5 | 572.7 | 408.2
2521.1 | 2300.1 | 569.1 | 321.8 | 359.5 | 572.3 | 407.9
2522.1 | 2301.1 | 568.9 | 322 | 359.6 | 572.1 | 407.6
2523.1 | 2302.1 | 568.6 | 321.7 | 360.4 | 571.9 | 407.5
2524.1 | 2303.1 | 568.4 | 321.8 | 359.4 | 571.8 | 407
2525.1 | 2304.1 | 568.3 | 321 | 358.5 | 571.6 | 406.8
2526.1 | 2305.1 | 568.1 | 320.5 | 358 | 571.3 | 406.3
2527.1 | 2306.1 | 568 | 319.9 | 357.5 | 571.1 | 405.8
2528.1 | 2307.1 | 567.9 | 320 | 357.5 | 571.2 | 405.5
2529.1 | 2308.1 | 567.7 | 320.3 | 357.1 | 571.3 | 405.4
2530.1 | 2309.1 | 567.6 | 319.6 | 357 | 571.2 | 405.2
2531.1 | 2310.1 | 567.4 | 318.7 | 356.1 | 571.3 | 405.2
2532.1 | 2311.1 | 567.3 | 318.3 | 355.5 | 571.3 | 404.8
2533.1 | 2312.1 | 567.2 | 317.3 | 355.2 | 571.3 | 404.6
2534.1 | 2313.1 | 566.9 | 316.2 | 355.5 | 571.2 | 404.5
2535.1 | 2314.1 | 566.7 | 315.3 | 355.9 | 571.2 | 404.5
2536.1 | 2315.1 | 566.5 | 314.9 | 355.8 | 571 | 404.3
2537.1 | 2316.1 | 566.2 | 315 | 355.7 | 570.9 | 404
2538.1 | 2317.1 | 566 | 314.5 | 355.1 | 570.6 | 403.8
2539.1 | 2318.1 | 565.7 | 313.2 | 355.2 | 570.5 | 403.6
2540.1 | 2319.1 | 565.4 | 312.9 | 354.8 | 570.6 | 403.3
2541.1 | 2320.1 | 565.2 | 312.1 | 354.2 | 570.3 | 402.9
2542.1 | 2321.1 | 565 | 311.3 | 353.2 | 570.3 | 402.6
2543.1 | 2322.1 | 564.9 | 310.1 | 352.7 | 570.1 | 402.5
2544.1 | 2323.1 | 564.7 | 309.1 | 351.7 | 570.2 | 402.2
2545.1 | 2324.1 | 564.6 | 308.1 | 351.4 | 569.8 | 401.9
2546.1 | 2325.1 | 564.4 | 306.7 | 351.3 | 569.7 | 401.8
2547.1 | 2326.1 | 564.2 | 306.5 | 351.1 | 569.8 | 401.7
2548.1 | 2327.1 | 564 | 307.1 | 351.2 | 570.1 | 401.6
2549.1 | 2328.1 | 563.7 | 306.4 | 351 | 570 | 401.4
2550.1 | 2329.1 | 563.4 | 306.1 | 350.7 | 569.7 | 400.8
2551.1 | 2330.1 | 563.2 | 305.8 | 350.6 | 569.7 | 400.5
2552.1 | 2331.1 | 562.9 | 305.3 | 350.4 | 569.8 | 400.2
2553.1 | 2332.1 | 562.6 | 304.2 | 350.1 | 569.8 | 400.1
2554.1 | 2333.1 | 562.3 | 303.6 | 350 | 569.9 | 399.7
2555.1 | 2334.1 | 562 | 304.6 | 350.1 | 570 | 399.5
2556.1 | 2335.1 | 561.8 | 305.5 | 349.9 | 569.9 | 399.5
2557.1 | 2336.1 | 561.5 | 304.9 | 349.7 | 569.4 | 399.3
2558.1 | 2337.1 | 561.2 | 304.5 | 349.9 | 568.9 | 399.1
2559.1 | 2338.1 | 560.9 | 304.6 | 350.9 | 568.9 | 399.1
2560.1 | 2339.1 | 560.6 | 305 | 350.8 | 568.6 | 399
2561.1 | 2340.1 | 560.4 | 305.2 | 350.6 | 568.6 | 399
2562.1 | 2341.1 | 560.2 | 305.4 | 350.9 | 568.3 | 398.7
2563.1 | 2342.1 | 560 | 306.6 | 350.7 | 568.2 | 398.7
2564.1 | 2343.1 | 559.8 | 306.7 | 350.5 | 568.1 | 398.5
2565.1 | 2344.1 | 559.6 | 306.7 | 349.9 | 567.9 | 398.3
2566.1 | 2345.1 | 559.4 | 307 | 350.4 | 567.4 | 397.9
2567.1 | 2346.1 | 559.2 | 307.2 | 351 | 567 | 397.6
2568.1 | 2347.1 | 559 | 308.1 | 350.5 | 566.6 | 397.2
2569.1 | 2348.1 | 558.9 | 307.8 | 350.5 | 566.7 | 397.1
2570.1 | 2349.1 | 558.8 | 308.9 | 349.5 | 566.7 | 397
2571.1 | 2350.1 | 558.7 | 309.3 | 349.1 | 566.6 | 396.8
2572.1 | 2351.1 | 558.5 | 310.6 | 349.3 | 566.6 | 396.9
2573.1 | 2352.1 | 558.4 | 310.6 | 348.7 | 566.6 | 397
2574.1 | 2353.1 | 558.2 | 310.6 | 348.7 | 566.7 | 396.8
2575.1 | 2354.1 | 558 | 311.5 | 348.1 | 566.7 | 396.7
2576.1 | 2355.1 | 557.8 | 312.8 | 347.6 | 566.5 | 396.4
2577.1 | 2356.1 | 557.6 | 312.2 | 346.1 | 566.6 | 396.3
2578.1 | 2357.1 | 557.4 | 311.4 | 345.9 | 566.4 | 396.1
2579.1 | 2358.1 | 557.1 | 310.3 | 345.2 | 566.3 | 395.8
2580.1 | 2359.1 | 556.9 | 310.1 | 344.8 | 565.8 | 395.3
2581.1 | 2360.1 | 556.7 | 309.5 | 344.5 | 565.5 | 394.7
2582.1 | 2361.1 | 556.5 | 308.2 | 343.9 | 565.7 | 394.5
2583.1 | 2362.1 | 556.3 | 307 | 344.1 | 565.8 | 394.3
2584.1 | 2363.1 | 556 | 307.6 | 343.8 | 565.7 | 393.8
2585.1 | 2364.1 | 555.8 | 307.5 | 343.5 | 565.9 | 393.4
2586.1 | 2365.1 | 555.6 | 306.5 | 343.1 | 566 | 393.1
2587.1 | 2366.1 | 555.3 | 305.8 | 343.1 | 565.8 | 393.2
2588.1 | 2367.1 | 555 | 305.5 | 343 | 565.8 | 393.2
2589.1 | 2368.1 | 554.7 | 305 | 342.9 | 565.7 | 393.3
2590.1 | 2369.1 | 554.5 | 304.5 | 343.1 | 565.5 | 393.4
2591.1 | 2370.1 | 554.3 | 303.5 | 343.6 | 565.2 | 393.4
2592.1 | 2371.1 | 554.1 | 302.7 | 342.3 | 565.1 | 393.2
2593.1 | 2372.1 | 554 | 302.8 | 341.7 | 564.9 | 392.9
2594.1 | 2373.1 | 553.9 | 303.2 | 342 | 564.8 | 392.9
2595.1 | 2374.1 | 553.7 | 303.1 | 342.4 | 564.6 | 392.7
2596.1 | 2375.1 | 553.6 | 303.4 | 342.9 | 564.7 | 392.4
2597.1 | 2376.1 | 553.5 | 304.4 | 342.9 | 564.5 | 392
2598.1 | 2377.1 | 553.4 | 304.7 | 342.7 | 564.6 | 391.6
2599.1 | 2378.1 | 553.3 | 304.6 | 342 | 564.6 | 391.2
2600.1 | 2379.1 | 553.2 | 304.2 | 341.9 | 564.9 | 391.1
2601.1 | 2380.1 | 553.1 | 304.8 | 341.1 | 564.9 | 390.8
2602.1 | 2381.1 | 553 | 304.3 | 341 | 564.9 | 390.3
2603.1 | 2382.1 | 552.8 | 304.1 | 340 | 564.7 | 389.9
2604.1 | 2383.1 | 552.7 | 303.3 | 339.5 | 564.6 | 389.8
2605.1 | 2384.1 | 552.7 | 303 | 338.8 | 564.8 | 389.6
2606.1 | 2385.1 | 552.7 | 302.6 | 336.9 | 564.7 | 389.1
2607.1 | 2386.1 | 552.7 | 301.6 | 336 | 564.6 | 388.6
2608.1 | 2387.1 | 552.7 | 300.6 | 335.2 | 564.6 | 388.2
2609.1 | 2388.1 | 552.6 | 299.9 | 335.3 | 564.4 | 388.2
2610.1 | 2389.1 | 552.5 | 301.4 | 335.5 | 564.3 | 388.4
2611.1 | 2390.1 | 552.3 | 302 | 336 | 564.2 | 388.3
2612.1 | 2391.1 | 552.2 | 301.9 | 336.1 | 564.3 | 388.1
2613.1 | 2392.1 | 552.1 | 301.1 | 336.7 | 564.4 | 388.2
2614.1 | 2393.1 | 552 | 300.3 | 336.7 | 564 | 388
2615.1 | 2394.1 | 551.9 | 299.6 | 335.8 | 563.8 | 387.7
2616.1 | 2395.1 | 551.7 | 299.2 | 336.2 | 563.6 | 387.2
2617.1 | 2396.1 | 551.6 | 300.3 | 335.7 | 563.2 | 387.2
2618.1 | 2397.1 | 551.5 | 300.8 | 334.8 | 563 | 386.8
2619.1 | 2398.1 | 551.4 | 300.2 | 334.1 | 563 | 386.4
2620.1 | 2399.1 | 551.2 | 298.7 | 333.4 | 562.8 | 386.2
2621.1 | 2400.1 | 551.1 | 297.6 | 332.8 | 562.9 | 386
2622.1 | 2401.1 | 550.9 | 296.9 | 331.7 | 562.8 | 385.8
2623.1 | 2402.1 | 550.7 | 295.5 | 331.1 | 562.6 | 385.5
2624.1 | 2403.1 | 550.6 | 294.7 | 330.5 | 562.8 | 385.2
2625.1 | 2404.1 | 550.5 | 294.3 | 330.1 | 562.8 | 385
2626.1 | 2405.1 | 550.3 | 293.2 | 329.3 | 562.7 | 384.8
2627.1 | 2406.1 | 550.2 | 291.9 | 329 | 562.3 | 384.6
2628.1 | 2407.1 | 550 | 291.4 | 328.7 | 562.3 | 384.3
2629.1 | 2408.1 | 549.9 | 290.7 | 328.5 | 562.6 | 384.3
2630.1 | 2409.1 | 549.7 | 290.9 | 327.8 | 562.6 | 384.1
2631.1 | 2410.1 | 549.5 | 290.9 | 327.5 | 562.6 | 383.9
2632.1 | 2411.1 | 549.3 | 291.3 | 327.2 | 562.6 | 383.7
2633.1 | 2412.1 | 549 | 290.6 | 327 | 562.7 | 383.4
2634.1 | 2413.1 | 548.7 | 290.5 | 326.3 | 562.6 | 383
2635.1 | 2414.1 | 548.5 | 289.9 | 325.7 | 562.6 | 382.7
2636.1 | 2415.1 | 548.4 | 289.4 | 325 | 562.3 | 382.3
2637.1 | 2416.1 | 548.2 | 288.4 | 325.1 | 562 | 382.2
2638.1 | 2417.1 | 548 | 288 | 324.5 | 562 | 382
2639.1 | 2418.1 | 547.9 | 288.6 | 323.5 | 561.5 | 381.8
2640.1 | 2419.1 | 547.7 | 289.2 | 323.1 | 561.1 | 381.5
2641.1 | 2420.1 | 547.5 | 289.3 | 322.7 | 561.2 | 381.4
2642.1 | 2421.1 | 547.2 | 288.7 | 322.4 | 561.3 | 381.2
2643.1 | 2422.1 | 547 | 288.2 | 322.7 | 561 | 381.1
2644.1 | 2423.1 | 546.9 | 287.6 | 322.1 | 560.5 | 381
2645.1 | 2424.1 | 546.7 | 286.9 | 321.9 | 560.3 | 381
2646.1 | 2425.1 | 546.7 | 286.6 | 321.5 | 560 | 380.9
2647.1 | 2426.1 | 546.6 | 288.6 | 322 | 559.9 | 380.7
2648.1 | 2427.1 | 546.5 | 289 | 321.7 | 559.8 | 380.7
2649.1 | 2428.1 | 546.5 | 288.6 | 321.4 | 559.3 | 380.4
2650.1 | 2429.1 | 546.4 | 288.4 | 320.4 | 559.2 | 380.2
2651.1 | 2430.1 | 546.2 | 287.3 | 320.4 | 558.7 | 379.9
2652.1 | 2431.1 | 546 | 286.9 | 320.4 | 558.8 | 379.7
2653.1 | 2432.1 | 545.8 | 287 | 321 | 558.7 | 379.6
2654.1 | 2433.1 | 545.6 | 287.2 | 321.1 | 558.7 | 379.5
2655.1 | 2434.1 | 545.4 | 286.9 | 320.9 | 558.9 | 379.2
2656.1 | 2435.1 | 545.3 | 287.5 | 320.5 | 558.8 | 379
2657.1 | 2436.1 | 545.1 | 287.4 | 319.1 | 558.7 | 378.8
2658.1 | 2437.1 | 544.9 | 289 | 317.5 | 558.7 | 378.6
2659.1 | 2438.1 | 544.7 | 289 | 316.4 | 558.5 | 378.4
2660.1 | 2439.1 | 544.5 | 288.9 | 315.4 | 558.5 | 378.2
2661.1 | 2440.1 | 544.3 | 287.8 | 315 | 558.7 | 377.8
2662.1 | 2441.1 | 544.1 | 285.6 | 314.2 | 558.6 | 377.3
2663.1 | 2442.1 | 543.9 | 285.5 | 314 | 558.3 | 377
2664.1 | 2443.1 | 543.8 | 286.1 | 314 | 558.2 | 377
2665.1 | 2444.1 | 543.5 | 285.9 | 314.3 | 558.2 | 376.9
2666.1 | 2445.1 | 543.2 | 285.8 | 315 | 558.2 | 376.6
2667.1 | 2446.1 | 543 | 286.2 | 316 | 558.5 | 376.5
2668.1 | 2447.1 | 542.9 | 287.3 | 316.8 | 558.5 | 376.5
2669.1 | 2448.1 | 542.7 | 288.9 | 317.8 | 558.3 | 376.5
2670.1 | 2449.1 | 542.5 | 289.9 | 318.7 | 558.3 | 376.3
2671.1 | 2450.1 | 542.4 | 290.7 | 319.1 | 558.2 | 376.1
2672.1 | 2451.1 | 542.3 | 290 | 319.6 | 558.1 | 375.7
2673.1 | 2452.1 | 542.1 | 289.7 | 319.6 | 558.1 | 375.3
2674.1 | 2453.1 | 542 | 288.7 | 319.6 | 558.1 | 375.2
2675.1 | 2454.1 | 541.9 | 289.3 | 320 | 558.2 | 375.1
2676.1 | 2455.1 | 541.7 | 288.2 | 319.9 | 558.3 | 375
2677.1 | 2456.1 | 541.6 | 288 | 319.4 | 558.5 | 374.6
2678.1 | 2457.1 | 541.4 | 287 | 319.1 | 558.5 | 374.2
2679.1 | 2458.1 | 541.3 | 286.5 | 318 | 558.4 | 373.9
2680.1 | 2459.1 | 541.2 | 286.6 | 317.4 | 558 | 373.8
2681.1 | 2460.1 | 541.1 | 285.7 | 317.3 | 557.6 | 373.7
2682.1 | 2461.1 | 540.9 | 284.8 | 316.9 | 557.4 | 373.6
2683.1 | 2462.1 | 540.7 | 285 | 316.5 | 557.4 | 373.4
2684.1 | 2463.1 | 540.5 | 285.6 | 316.3 | 557.3 | 373.3
2685.1 | 2464.1 | 540.2 | 284.8 | 316.3 | 557.2 | 373.3
2686.1 | 2465.1 | 540 | 284.2 | 316.7 | 557.1 | 373.4
2687.1 | 2466.1 | 539.8 | 285.2 | 317.1 | 556.8 | 373.2
2688.1 | 2467.1 | 539.6 | 286.2 | 316.5 | 557.1 | 373.1
2689.1 | 2468.1 | 539.5 | 284.9 | 316 | 557 | 372.7
2690.1 | 2469.1 | 539.4 | 284.6 | 315.1 | 557.2 | 372.5
2691.1 | 2470.1 | 539.3 | 284.7 | 314.2 | 557.1 | 372.5
2692.1 | 2471.1 | 539.2 | 285 | 313.8 | 556.6 | 372.3
2693.1 | 2472.1 | 539 | 284 | 313.7 | 556.2 | 372.2
2694.1 | 2473.1 | 538.7 | 283.7 | 313.8 | 556.1 | 372.1
2695.1 | 2474.1 | 538.5 | 283.2 | 313.8 | 556.1 | 371.9
2696.1 | 2475.1 | 538.3 | 282.3 | 313.6 | 555.9 | 371.8
2697.1 | 2476.1 | 538.2 | 282.7 | 312.2 | 555.8 | 371.2
2698.1 | 2477.1 | 538 | 283.3 | 311.6 | 555.7 | 370.8
2699.1 | 2478.1 | 537.8 | 282.1 | 310.7 | 555.4 | 370.5
2700.1 | 2479.1 | 537.7 | 281.5 | 309.9 | 555.3 | 370.1
2701.1 | 2480.1 | 537.5 | 280.1 | 309.7 | 555.3 | 370
2702.1 | 2481.1 | 537.2 | 278.1 | 308.2 | 555.2 | 369.8
2703.1 | 2482.1 | 536.9 | 278.2 | 307.6 | 555.2 | 369.5
2704.1 | 2483.1 | 536.7 | 278.5 | 307.8 | 554.7 | 369.3
2705.1 | 2484.1 | 536.5 | 280.1 | 307.7 | 554.5 | 368.8
2706.1 | 2485.1 | 536.4 | 280 | 308.2 | 554.3 | 368.8
2707.1 | 2486.1 | 536.2 | 279.7 | 308.3 | 554.4 | 368.6
2708.1 | 2487.1 | 536 | 280.7 | 308.6 | 554.4 | 368.3
2709.1 | 2488.1 | 535.8 | 282.3 | 308.6 | 554.2 | 368
2710.1 | 2489.1 | 535.7 | 281.4 | 308.8 | 553.9 | 367.8
2711.1 | 2490.1 | 535.6 | 280.8 | 309 | 553.7 | 367.8
2712.1 | 2491.1 | 535.4 | 279.1 | 309.2 | 553.5 | 367.6
2713.1 | 2492.1 | 535.2 | 278.3 | 308.7 | 553.5 | 367.4
2714.1 | 2493.1 | 534.9 | 277.9 | 308.3 | 553.5 | 367.4
2715.1 | 2494.1 | 534.7 | 277.5 | 308.5 | 553.5 | 367.3
2716.1 | 2495.1 | 534.4 | 277.4 | 307.9 | 553.3 | 367.3
2717.1 | 2496.1 | 534.1 | 279.2 | 307.2 | 553.4 | 367.2
2718.1 | 2497.1 | 533.8 | 278 | 306.1 | 553.5 | 366.6
2719.1 | 2498.1 | 533.6 | 277.4 | 305.5 | 553.5 | 366.4
2720.1 | 2499.1 | 533.3 | 275.4 | 304.7 | 553.2 | 366.3
2721.1 | 2500.1 | 533.1 | 274.7 | 304.2 | 553.2 | 366.2
2722.1 | 2501.1 | 532.8 | 274.5 | 304.1 | 553.1 | 365.9
2723.1 | 2502.1 | 532.6 | 273.9 | 303.9 | 553 | 365.8
2724.1 | 2503.1 | 532.3 | 273.8 | 303.9 | 552.8 | 365.8
2725.1 | 2504.1 | 532.1 | 272.8 | 303.7 | 552.6 | 365.4
2726.1 | 2505.1 | 531.8 | 272.2 | 303.2 | 552.6 | 365
2727.1 | 2506.1 | 531.6 | 273.3 | 303.4 | 552.7 | 364.9
2728.1 | 2507.1 | 531.4 | 274.6 | 302.6 | 552.9 | 364.5
2729.1 | 2508.1 | 531.1 | 273 | 301.8 | 552.8 | 364.3
2730.1 | 2509.1 | 530.8 | 272.1 | 301.3 | 552.8 | 364.3
2731.1 | 2510.1 | 530.6 | 270.6 | 301 | 552.9 | 364.1
2732.1 | 2511.1 | 530.4 | 270.5 | 300 | 552.9 | 364
2733.1 | 2512.1 | 530.2 | 270.3 | 299.4 | 552.9 | 364
2734.1 | 2513.1 | 529.9 | 270.4 | 298.9 | 552.9 | 363.7
2735.1 | 2514.1 | 529.6 | 268.9 | 298.9 | 552.5 | 363.6
2736.1 | 2515.1 | 529.2 | 268.8 | 298.8 | 551.9 | 363.6
2737.1 | 2516.1 | 528.9 | 268.9 | 298.7 | 551.5 | 363.6
2738.1 | 2517.1 | 528.6 | 270.4 | 299 | 551.2 | 363.4
2739.1 | 2518.1 | 528.2 | 271.2 | 299 | 551 | 363.3
2740.1 | 2519.1 | 527.9 | 270.6 | 298.7 | 550.6 | 363
2741.1 | 2520.1 | 527.5 | 270.4 | 298.4 | 550.3 | 362.9
2742.1 | 2521.1 | 527.1 | 270.5 | 298.3 | 550.2 | 362.8
2743.1 | 2522.1 | 526.8 | 270.9 | 298.3 | 550.2 | 362.5
2744.1 | 2523.1 | 526.5 | 271.2 | 298.5 | 550.3 | 362.3
2745.1 | 2524.1 | 526.1 | 271.1 | 298.4 | 550.4 | 362.3
2746.1 | 2525.1 | 525.8 | 271 | 297.9 | 550.6 | 362.1
2747.1 | 2526.1 | 525.6 | 271.4 | 297.8 | 550.8 | 361.9
2748.1 | 2527.1 | 525.4 | 270.1 | 297.9 | 551 | 361.7
2749.1 | 2528.1 | 525.2 | 270 | 297.9 | 551.2 | 361.6
2750.1 | 2529.1 | 524.9 | 270.5 | 297.1 | 551.2 | 361.4
2751.1 | 2530.1 | 524.7 | 269.4 | 297 | 551.1 | 361.3
2752.1 | 2531.1 | 524.5 | 269.5 | 296.9 | 551.1 | 361.2
2753.1 | 2532.1 | 524.2 | 269.5 | 296.9 | 551 | 361.1
2754.1 | 2533.1 | 524 | 270.6 | 297 | 551 | 361
2755.1 | 2534.1 | 523.8 | 270.7 | 297.5 | 550.8 | 360.7
2756.1 | 2535.1 | 523.5 | 272 | 297.5 | 550.5 | 360.6
2757.1 | 2536.1 | 523.2 | 273.2 | 297 | 550.5 | 360.4
2758.1 | 2537.1 | 523 | 274.1 | 297.2 | 550.3 | 360.2
2759.1 | 2538.1 | 522.8 | 274 | 297.4 | 550.4 | 360.1
2760.1 | 2539.1 | 522.6 | 273.9 | 297.7 | 550.5 | 359.8
2761.1 | 2540.1 | 522.4 | 272.9 | 297.8 | 550.6 | 359.5
2762.1 | 2541.1 | 522.3 | 271.9 | 297.1 | 550.8 | 359.1
2763.1 | 2542.1 | 522.1 | 271.9 | 295.5 | 550.7 | 358.4
2764.1 | 2543.1 | 522 | 271.3 | 294.5 | 550.7 | 358.1
2765.1 | 2544.1 | 521.8 | 270.1 | 293.8 | 550.5 | 357.9
2766.1 | 2545.1 | 521.7 | 270.3 | 292.7 | 550.5 | 357.7
2767.1 | 2546.1 | 521.5 | 270.2 | 292.7 | 550.5 | 357.5
2768.1 | 2547.1 | 521.3 | 270.7 | 292.4 | 550.5 | 357.3
2769.1 | 2548.1 | 521.1 | 270.3 | 292.2 | 550.6 | 357.1
2770.1 | 2549.1 | 520.8 | 269.6 | 292.4 | 550.7 | 356.9
2771.1 | 2550.1 | 520.6 | 268.7 | 292.3 | 550.6 | 356.6
2772.1 | 2551.1 | 520.4 | 268.8 | 291.9 | 550.3 | 356.5
2773.1 | 2552.1 | 520.1 | 268.1 | 291.2 | 550.3 | 356.4
2774.1 | 2553.1 | 519.9 | 268.3 | 290.8 | 550.2 | 356.4
2775.1 | 2554.1 | 519.7 | 268 | 290.4 | 550.3 | 356.3
2776.1 | 2555.1 | 519.5 | 267.4 | 290.5 | 550.2 | 356.3
2777.1 | 2556.1 | 519.2 | 266.4 | 290 | 550.1 | 356
2778.1 | 2557.1 | 519.1 | 266 | 289.1 | 550.1 | 355.5
2779.1 | 2558.1 | 519 | 266.5 | 287.8 | 550 | 355.3
2780.1 | 2559.1 | 518.8 | 265.8 | 287.2 | 549.9 | 355
2781.1 | 2560.1 | 518.5 | 265.6 | 287.6 | 549.7 | 354.6
2782.1 | 2561.1 | 518.3 | 266.6 | 287.2 | 549.5 | 354.3
2783.1 | 2562.1 | 518 | 267.3 | 286.2 | 549.6 | 354.2
2784.1 | 2563.1 | 517.6 | 266.8 | 286.3 | 549.8 | 354.1
2785.1 | 2564.1 | 517.4 | 268.5 | 286.8 | 549.5 | 354.1
2786.1 | 2565.1 | 517.1 | 269.2 | 287.2 | 549.2 | 353.9
2787.1 | 2566.1 | 516.8 | 269.6 | 287.5 | 549 | 353.8
2788.1 | 2567.1 | 516.6 | 270.2 | 287.6 | 548.9 | 353.7
2789.1 | 2568.1 | 516.4 | 271.4 | 287.7 | 548.8 | 353.6
2790.1 | 2569.1 | 516.2 | 271.6 | 287.1 | 548.8 | 353.6
2791.1 | 2570.1 | 516 | 272.2 | 287.3 | 548.6 | 353.4
2792.1 | 2571.1 | 515.9 | 273.1 | 287.1 | 548.6 | 353.1
2793.1 | 2572.1 | 515.8 | 272.8 | 287.4 | 548.6 | 352.8
2794.1 | 2573.1 | 515.7 | 271.6 | 287 | 548.8 | 352.4
2795.1 | 2574.1 | 515.6 | 270.5 | 286.2 | 548.9 | 352.1
2796.1 | 2575.1 | 515.5 | 269.8 | 285.4 | 548.7 | 351.9
2797.1 | 2576.1 | 515.2 | 269.2 | 284.6 | 548.4 | 351.8
2798.1 | 2577.1 | 514.9 | 268.5 | 283.3 | 548.2 | 351.6
2799.1 | 2578.1 | 514.8 | 268.3 | 282.6 | 548.2 | 351.4
2800.1 | 2579.1 | 514.6 | 267.2 | 282.8 | 548.3 | 351.2
2801.1 | 2580.1 | 514.5 | 266.5 | 282.3 | 548.4 | 350.9
2802.1 | 2581.1 | 514.4 | 265.8 | 282 | 548.4 | 350.7
2803.1 | 2582.1 | 514.2 | 264.9 | 281.7 | 548.5 | 350.7
2804.1 | 2583.1 | 514 | 263.5 | 280.9 | 548.5 | 350.6
2805.1 | 2584.1 | 513.8 | 262.9 | 280 | 548.4 | 350.5
2806.1 | 2585.1 | 513.6 | 261.8 | 279.2 | 548.3 | 350.4
2807.1 | 2586.1 | 513.4 | 261.6 | 278.8 | 548.3 | 350.2
2808.1 | 2587.1 | 513.1 | 260.9 | 278.9 | 548.4 | 350
2809.1 | 2588.1 | 512.8 | 260.4 | 278.8 | 548.4 | 349.7
2810.1 | 2589.1 | 512.6 | 260.3 | 278.6 | 548.1 | 349.4
2811.1 | 2590.1 | 512.3 | 259.8 | 278.1 | 547.9 | 349
2812.1 | 2591.1 | 512 | 259.9 | 277.2 | 547.8 | 348.8
2813.1 | 2592.1 | 511.7 | 260.1 | 277.3 | 547.8 | 348.5
2814.1 | 2593.1 | 511.5 | 260.1 | 277.7 | 547.6 | 348.3
2815.1 | 2594.1 | 511.3 | 260.5 | 278.3 | 547.4 | 348.3
2816.1 | 2595.1 | 511.1 | 259.6 | 278.5 | 547.4 | 348.1
2817.1 | 2596.1 | 510.8 | 258.9 | 278 | 547.2 | 347.9
2818.1 | 2597.1 | 510.5 | 257.7 | 277.5 | 547 | 347.9
2819.1 | 2598.1 | 510.3 | 257.5 | 277.7 | 546.9 | 347.7
2820.1 | 2599.1 | 510.1 | 257.1 | 277.6 | 546.7 | 347.5
2821.1 | 2600.1 | 509.9 | 257 | 277.2 | 546.4 | 347.3
2822.1 | 2601.1 | 509.6 | 257.4 | 276.8 | 546.2 | 347.2
2823.1 | 2602.1 | 509.3 | 257.1 | 276 | 546.1 | 347.1
2824.1 | 2603.1 | 509.1 | 256.3 | 275.5 | 546 | 346.9
2825.1 | 2604.1 | 508.8 | 255.3 | 275.3 | 546 | 346.7
2826.1 | 2605.1 | 508.6 | 254.4 | 274.9 | 546.1 | 346.5
2827.1 | 2606.1 | 508.4 | 254.3 | 273.2 | 546.1 | 346.3
2828.1 | 2607.1 | 508.1 | 254.9 | 271.8 | 546.1 | 346
2829.1 | 2608.1 | 507.8 | 255.1 | 271.2 | 546.1 | 345.8
2830.1 | 2609.1 | 507.5 | 255.3 | 271 | 546.2 | 345.6
2831.1 | 2610.1 | 507.3 | 255 | 271 | 546.1 | 345.5
2832.1 | 2611.1 | 507.1 | 255 | 271.1 | 546.1 | 345.3
2833.1 | 2612.1 | 506.8 | 255.9 | 271.5 | 546.1 | 345
2834.1 | 2613.1 | 506.6 | 255.7 | 271.7 | 546.1 | 344.8
2835.1 | 2614.1 | 506.4 | 255.9 | 271.9 | 546.2 | 344.6
2836.1 | 2615.1 | 506.1 | 255.8 | 272.1 | 546.3 | 344.4
2837.1 | 2616.1 | 505.9 | 257 | 272.5 | 546.4 | 344.3
2838.1 | 2617.1 | 505.7 | 257 | 272.3 | 546.5 | 344.2
2839.1 | 2618.1 | 505.4 | 257.2 | 271.3 | 546.4 | 344.1
2840.1 | 2619.1 | 505.2 | 256.8 | 271 | 546.2 | 344
2841.1 | 2620.1 | 504.9 | 256.1 | 271.1 | 546 | 343.8
2842.1 | 2621.1 | 504.7 | 255.3 | 271.1 | 546 | 343.6
2843.1 | 2622.1 | 504.5 | 255 | 270.7 | 546.1 | 343.4
2844.1 | 2623.1 | 504.2 | 254.3 | 270 | 546.1 | 343.2
2845.1 | 2624.1 | 503.9 | 253.5 | 269.4 | 545.9 | 342.9
2846.1 | 2625.1 | 503.6 | 252.8 | 269.4 | 545.9 | 342.7
2847.1 | 2626.1 | 503.4 | 254 | 269.2 | 545.8 | 342.6
2848.1 | 2627.1 | 503.1 | 253.9 | 269.2 | 545.8 | 342.4
2849.1 | 2628.1 | 502.9 | 254.9 | 268.9 | 545.9 | 342.2
2850.1 | 2629.1 | 502.6 | 254.5 | 268.7 | 545.8 | 342
2851.1 | 2630.1 | 502.4 | 255.1 | 268.6 | 545.8 | 341.8
2852.1 | 2631.1 | 502.1 | 254.5 | 268.3 | 545.7 | 341.5
2853.1 | 2632.1 | 501.9 | 254 | 267.8 | 545.7 | 341.3
2854.1 | 2633.1 | 501.6 | 254.4 | 267.3 | 545.7 | 341.1
2855.1 | 2634.1 | 501.3 | 254 | 267.1 | 545.7 | 340.9
2856.1 | 2635.1 | 501.1 | 253.5 | 266.8 | 545.6 | 340.6
2857.1 | 2636.1 | 500.8 | 253.5 | 266.5 | 545.5 | 340.5
2858.1 | 2637.1 | 500.6 | 253.9 | 266.1 | 545.5 | 340.2
2859.1 | 2638.1 | 500.3 | 253.6 | 266 | 545.7 | 340
2860.1 | 2639.1 | 500.1 | 253.1 | 265.8 | 545.7 | 339.7
2861.1 | 2640.1 | 500 | 253.6 | 265.5 | 545.7 | 339.5
2862.1 | 2641.1 | 499.8 | 253 | 265.4 | 545.7 | 339.4
2863.1 | 2642.1 | 499.7 | 252 | 265.5 | 545.5 | 339.2
2864.1 | 2643.1 | 499.5 | 251.6 | 265.1 | 545.4 | 338.9
2865.1 | 2644.1 | 499.3 | 251 | 264.7 | 545.4 | 338.7
2866.1 | 2645.1 | 499.2 | 251 | 264.8 | 545.4 | 338.6
2867.1 | 2646.1 | 499 | 250.2 | 264.5 | 545.3 | 338.5
2868.1 | 2647.1 | 498.8 | 250.1 | 264.6 | 545.2 | 338.5
2869.1 | 2648.1 | 498.6 | 249.7 | 264.6 | 545 | 338.3
2870.1 | 2649.1 | 498.4 | 249.8 | 264.7 | 544.8 | 338.2
2871.1 | 2650.1 | 498.2 | 250.1 | 264.8 | 544.7 | 338
2872.1 | 2651.1 | 498 | 251.1 | 264.6 | 544.6 | 338
2873.1 | 2652.1 | 497.8 | 250.4 | 264.5 | 544.6 | 337.7
2874.1 | 2653.1 | 497.6 | 249.8 | 264 | 544.5 | 337.6
2875.1 | 2654.1 | 497.4 | 249.4 | 263.5 | 544.4 | 337.4
2876.1 | 2655.1 | 497.2 | 249 | 262.9 | 544.3 | 337.3
2877.1 | 2656.1 | 496.9 | 248.8 | 263.1 | 544.2 | 337.2
2878.1 | 2657.1 | 496.7 | 248.8 | 262.6 | 544.1 | 336.9
2879.1 | 2658.1 | 496.5 | 248.7 | 261.3 | 544.2 | 336.8
2880.1 | 2659.1 | 496.3 | 248.2 | 261.1 | 544.2 | 336.6
2881.1 | 2660.1 | 496.1 | 247.9 | 260.9 | 544.2 | 336.3
2882.1 | 2661.1 | 495.9 | 248.3 | 260.8 | 544.2 | 336
2883.1 | 2662.1 | 495.7 | 248.9 | 261.2 | 544.3 | 335.8
2884.1 | 2663.1 | 495.5 | 249 | 261.4 | 544.3 | 335.6
2885.1 | 2664.1 | 495.4 | 249.9 | 261.4 | 544.3 | 335.4
2886.1 | 2665.1 | 495.2 | 250.8 | 261.6 | 544.3 | 335
2887.1 | 2666.1 | 495.1 | 250.4 | 261.5 | 544.2 | 334.8
2888.1 | 2667.1 | 494.9 | 250 | 261.4 | 544.1 | 334.7
2889.1 | 2668.1 | 494.7 | 249.1 | 260.8 | 543.9 | 334.5
2890.1 | 2669.1 | 494.5 | 248.3 | 260.6 | 543.7 | 334.3
2891.1 | 2670.1 | 494.3 | 247.7 | 260.3 | 543.6 | 334.1
2892.1 | 2671.1 | 494.1 | 247.9 | 260 | 543.5 | 334
2893.1 | 2672.1 | 493.9 | 247.3 | 259.7 | 543.5 | 333.8
2894.1 | 2673.1 | 493.6 | 247 | 259.8 | 543.4 | 333.6
2895.1 | 2674.1 | 493.4 | 247.2 | 259.8 | 543.3 | 333.5
2896.1 | 2675.1 | 493.3 | 247.1 | 258.7 | 543.1 | 333.3
2897.1 | 2676.1 | 493 | 247.6 | 258.5 | 542.8 | 333.1
2898.1 | 2677.1 | 492.8 | 246.8 | 258.1 | 542.6 | 333.1
2899.1 | 2678.1 | 492.6 | 246.5 | 257.9 | 542.5 | 332.9
2900.1 | 2679.1 | 492.5 | 245.9 | 257.8 | 542.5 | 332.7
2901.1 | 2680.1 | 492.3 | 246 | 257.7 | 542.5 | 332.7
2902.1 | 2681.1 | 492.1 | 246.4 | 257.6 | 542.3 | 332.5
2903.1 | 2682.1 | 491.9 | 245.9 | 256.6 | 542.2 | 332.3
2904.1 | 2683.1 | 491.7 | 245.5 | 256.1 | 542.1 | 332.1
2905.1 | 2684.1 | 491.5 | 245.7 | 255.9 | 542 | 332
2906.1 | 2685.1 | 491.2 | 245.3 | 254.9 | 542 | 331.9
2907.1 | 2686.1 | 491 | 244.7 | 254.3 | 541.9 | 331.6
2908.1 | 2687.1 | 490.9 | 245 | 253.7 | 541.9 | 331.1
2909.1 | 2688.1 | 490.7 | 245 | 253.8 | 541.7 | 330.7
2910.1 | 2689.1 | 490.5 | 245.4 | 253.7 | 541.8 | 330.6
2911.1 | 2690.1 | 490.3 | 245 | 253.5 | 541.9 | 330.4
2912.1 | 2691.1 | 490.1 | 244.9 | 253.8 | 541.8 | 330.4
2913.1 | 2692.1 | 490 | 244.8 | 253.5 | 541.7 | 330.2
2914.1 | 2693.1 | 489.8 | 244.9 | 253.2 | 541.6 | 330
2915.1 | 2694.1 | 489.6 | 244.9 | 252.8 | 541.5 | 329.9
2916.1 | 2695.1 | 489.5 | 244.5 | 252 | 541.4 | 329.7
2917.1 | 2696.1 | 489.2 | 243.9 | 250.7 | 541.2 | 329.5
2918.1 | 2697.1 | 489 | 243.6 | 249.3 | 541.2 | 329.3
2919.1 | 2698.1 | 488.8 | 243.1 | 248.9 | 541.2 | 328.9
2920.1 | 2699.1 | 488.6 | 243 | 248.4 | 541.1 | 328.7
2921.1 | 2700.1 | 488.5 | 242.6 | 248.2 | 540.9 | 328.6
2922.1 | 2701.1 | 488.3 | 242.4 | 248 | 540.9 | 328.4
2923.1 | 2702.1 | 488.1 | 243.1 | 248.1 | 541 | 328.2
2924.1 | 2703.1 | 487.9 | 243 | 248.3 | 540.8 | 328.1
2925.1 | 2704.1 | 487.9 | 243.5 | 248.5 | 540.7 | 327.7
2926.1 | 2705.1 | 487.8 | 243.1 | 248.5 | 540.6 | 327.6
2927.1 | 2706.1 | 487.7 | 243.9 | 248.8 | 540.5 | 327.4
2928.1 | 2707.1 | 487.5 | 244.1 | 248.8 | 540.5 | 327.3
2929.1 | 2708.1 | 487.4 | 243.3 | 248.6 | 540.4 | 327.1
2930.1 | 2709.1 | 487.2 | 243.4 | 247.9 | 540.4 | 326.9
2931.1 | 2710.1 | 487.1 | 242.4 | 248.5 | 540.2 | 326.8
2932.1 | 2711.1 | 487.1 | 241.7 | 248.7 | 540.1 | 326.6
2933.1 | 2712.1 | 487 | 241.4 | 248.3 | 540 | 326.1
2934.1 | 2713.1 | 486.9 | 241.3 | 248.2 | 539.8 | 326
2935.1 | 2714.1 | 486.8 | 241.5 | 248 | 539.7 | 325.9
2936.1 | 2715.1 | 486.6 | 241 | 248 | 539.8 | 325.8
2937.1 | 2716.1 | 486.5 | 240.7 | 247.8 | 540 | 325.7
2938.1 | 2717.1 | 486.3 | 240.7 | 247.7 | 540 | 325.6
2939.1 | 2718.1 | 486.1 | 240.6 | 247.4 | 540 | 325.3
2940.1 | 2719.1 | 485.9 | 239.7 | 247.1 | 540.2 | 325.1
2941.1 | 2720.1 | 485.8 | 238.6 | 246.8 | 540.3 | 325
2942.1 | 2721.1 | 485.6 | 238.3 | 246.9 | 540.5 | 324.9
2943.1 | 2722.1 | 485.5 | 238.2 | 247 | 540.5 | 324.6
2944.1 | 2723.1 | 485.3 | 238.1 | 247 | 540.5 | 324.1
2945.1 | 2724.1 | 485 | 238 | 247 | 540.6 | 323.5
2946.1 | 2725.1 | 484.8 | 237.4 | 246.6 | 540.7 | 323.5
2947.1 | 2726.1 | 484.6 | 237 | 246.1 | 540.7 | 323.4
2948.1 | 2727.1 | 484.5 | 237.1 | 246.1 | 540.5 | 323.1
2949.1 | 2728.1 | 484.3 | 237.3 | 246 | 540.3 | 322.9
2950.1 | 2729.1 | 484.1 | 237.5 | 246 | 540.3 | 322.8
2951.1 | 2730.1 | 483.9 | 236.9 | 245.8 | 540.2 | 322.6
2952.1 | 2731.1 | 483.7 | 237 | 245.6 | 540 | 322.5
2953.1 | 2732.1 | 483.5 | 238.2 | 245.5 | 539.8 | 322.5
2954.1 | 2733.1 | 483.3 | 237.8 | 245.3 | 539.7 | 322.4
2955.1 | 2734.1 | 483.1 | 237.7 | 244.9 | 539.8 | 322.2
2956.1 | 2735.1 | 482.9 | 238.1 | 244.8 | 539.8 | 321.8
2957.1 | 2736.1 | 482.7 | 239.4 | 244.6 | 539.7 | 321.6
2958.1 | 2737.1 | 482.4 | 240.1 | 243.4 | 539.7 | 321.2
2959.1 | 2738.1 | 482.2 | 239.7 | 243.1 | 539.9 | 321.1
2960.1 | 2739.1 | 482 | 240.1 | 243 | 539.9 | 320.9
2961.1 | 2740.1 | 481.9 | 240.5 | 243.2 | 539.8 | 320.7
2962.1 | 2741.1 | 481.7 | 239.6 | 243 | 539.8 | 320.6
2963.1 | 2742.1 | 481.5 | 239.2 | 242.2 | 539.8 | 320.5
2964.1 | 2743.1 | 481.2 | 238.4 | 242 | 539.8 | 320.4
2965.1 | 2744.1 | 481 | 238.4 | 241.7 | 539.8 | 320.3
2966.1 | 2745.1 | 480.8 | 239.2 | 241.5 | 539.8 | 320.1
2967.1 | 2746.1 | 480.6 | 238.3 | 241.6 | 539.8 | 320.1
2968.1 | 2747.1 | 480.4 | 237.6 | 241.8 | 539.7 | 320.1
2969.1 | 2748.1 | 480.2 | 237.7 | 242.3 | 539.5 | 319.8
2970.1 | 2749.1 | 480 | 238.2 | 242.4 | 539.4 | 319.7
2971.1 | 2750.1 | 479.7 | 238.2 | 242.3 | 539.5 | 319.6
2972.1 | 2751.1 | 479.5 | 238 | 242.1 | 539.7 | 319.5
2973.1 | 2752.1 | 479.3 | 238.1 | 242 | 539.6 | 319.3
2974.1 | 2753.1 | 479.1 | 238.2 | 241.6 | 539.5 | 319.1
2975.1 | 2754.1 | 478.9 | 238.8 | 241 | 539.6 | 318.8
2976.1 | 2755.1 | 478.7 | 238 | 240.5 | 539.7 | 318.6
2977.1 | 2756.1 | 478.4 | 238 | 240 | 539.8 | 318.4
2978.1 | 2757.1 | 478.2 | 237.5 | 239.7 | 539.8 | 318.2
2979.1 | 2758.1 | 478 | 237.7 | 239.7 | 539.8 | 318.1
2980.1 | 2759.1 | 477.7 | 238.4 | 239.7 | 539.7 | 318
2981.1 | 2760.1 | 477.5 | 238.7 | 239.7 | 539.7 | 317.9
2982.1 | 2761.1 | 477.3 | 237.9 | 239.6 | 539.6 | 317.8
2983.1 | 2762.1 | 477 | 237.1 | 239.4 | 539.3 | 317.8
2984.1 | 2763.1 | 476.8 | 236.6 | 239.4 | 539.2 | 317.6
2985.1 | 2764.1 | 476.6 | 235.7 | 239.2 | 538.9 | 317.6
2986.1 | 2765.1 | 476.4 | 235.6 | 238.8 | 538.6 | 317.4
2987.1 | 2766.1 | 476.1 | 235.2 | 238.7 | 538.6 | 317.2
2988.1 | 2767.1 | 475.9 | 234.2 | 238.1 | 538.6 | 317
2989.1 | 2768.1 | 475.7 | 233.3 | 237.9 | 538.7 | 316.8
2990.1 | 2769.1 | 475.5 | 232.4 | 237.7 | 538.7 | 316.6
2991.1 | 2770.1 | 475.3 | 231.5 | 237.1 | 538.8 | 316
2992.1 | 2771.1 | 475.1 | 230.7 | 236.8 | 539 | 315.9
2993.1 | 2772.1 | 474.9 | 230.8 | 236.1 | 539.1 | 315.6
2994.1 | 2773.1 | 474.7 | 230.2 | 235.7 | 539 | 315.2
2995.1 | 2774.1 | 474.5 | 230.2 | 235.4 | 538.8 | 315.2
2996.1 | 2775.1 | 474.4 | 229.7 | 235 | 538.6 | 315
2997.1 | 2776.1 | 474.2 | 229.3 | 233.9 | 538.6 | 314.8
2998.1 | 2777.1 | 474.1 | 230 | 233.3 | 538.6 | 314.6
2999.1 | 2778.1 | 473.9 | 229.7 | 232.3 | 538.6 | 314.5
3000.1 | 2779.1 | 473.7 | 229.2 | 231 | 538.4 | 314.4
3001.1 | 2780.1 | 473.6 | 228.6 | 229.9 | 538.4 | 314.2
3002.1 | 2781.1 | 473.4 | 227.9 | 228.4 | 538.5 | 313.9
3003.1 | 2782.1 | 473.2 | 228.3 | 227.4 | 538.4 | 313.7
3004.1 | 2783.1 | 473 | 228.5 | 226.9 | 538.4 | 313.6
3005.1 | 2784.1 | 472.9 | 227.6 | 226.6 | 538.3 | 313.4
3006.1 | 2785.1 | 472.7 | 227.1 | 226.3 | 538.1 | 313.2
3007.1 | 2786.1 | 472.5 | 226.3 | 226.2 | 538.1 | 313
3008.1 | 2787.1 | 472.4 | 225.6 | 225.6 | 538.1 | 312.8
3009.1 | 2788.1 | 472.2 | 225.2 | 225.3 | 537.9 | 312.6
3010.1 | 2789.1 | 472 | 224.7 | 224.6 | 537.9 | 312.2
3011.1 | 2790.1 | 471.9 | 224.4 | 223.9 | 537.7 | 312.1
3012.1 | 2791.1 | 471.7 | 224.1 | 222.9 | 537.7 | 311.8
3013.1 | 2792.1 | 471.5 | 223.7 | 222.2 | 537.8 | 311.6
3014.1 | 2793.1 | 471.3 | 223.3 | 221.6 | 537.8 | 311.4
3015.1 | 2794.1 | 471.1 | 223.1 | 221.3 | 537.6 | 311.2
3016.1 | 2795.1 | 470.9 | 223.4 | 221 | 537.4 | 311.1
3017.1 | 2796.1 | 470.8 | 223 | 221 | 537.1 | 311
3018.1 | 2797.1 | 470.6 | 223.2 | 220.8 | 537.1 | 310.8
3019.1 | 2798.1 | 470.4 | 223 | 219.8 | 537.2 | 310.5
3020.1 | 2799.1 | 470.2 | 222.8 | 219.8 | 537.1 | 310.3
3021.1 | 2800.1 | 470.1 | 222.2 | 220 | 537 | 310.2
3022.1 | 2801.1 | 469.9 | 222.3 | 220 | 536.9 | 310
3023.1 | 2802.1 | 469.7 | 222.7 | 220.2 | 536.7 | 309.8
3024.1 | 2803.1 | 469.6 | 223.7 | 220.6 | 536.5 | 309.7
3025.1 | 2804.1 | 469.4 | 224.7 | 220.6 | 536.4 | 309.6
3026.1 | 2805.1 | 469.2 | 225 | 220.8 | 536.3 | 309.3
3027.1 | 2806.1 | 469 | 225.3 | 220.5 | 536.4 | 309.2
3028.1 | 2807.1 | 468.8 | 226.4 | 219.7 | 536.5 | 309.1
3029.1 | 2808.1 | 468.6 | 227.1 | 219.8 | 536.3 | 309
3030.1 | 2809.1 | 468.5 | 227.5 | 219.5 | 536.2 | 308.7
3031.1 | 2810.1 | 468.3 | 227.8 | 219.5 | 536.1 | 308.5
3032.1 | 2811.1 | 468.1 | 226.9 | 219.6 | 536 | 308.5
3033.1 | 2812.1 | 467.9 | 226.5 | 219.2 | 536.1 | 308.2
3034.1 | 2813.1 | 467.7 | 226.3 | 218.6 | 536.1 | 307.6
3035.1 | 2814.1 | 467.5 | 225.7 | 218.7 | 536 | 307.6
3036.1 | 2815.1 | 467.3 | 225.2 | 218.8 | 535.9 | 307.5
3037.1 | 2816.1 | 467.1 | 225.2 | 218.5 | 535.9 | 307.2
3038.1 | 2817.1 | 467 | 225.2 | 218 | 535.7 | 306.9
3039.1 | 2818.1 | 466.8 | 224.8 | 217.8 | 535.6 | 306.6
3040.1 | 2819.1 | 466.6 | 224 | 217.5 | 535.6 | 306.1
3041.1 | 2820.1 | 466.4 | 224 | 218 | 535.7 | 306.2
3042.1 | 2821.1 | 466.2 | 224.7 | 218.4 | 535.6 | 306.1
3043.1 | 2822.1 | 466.1 | 224 | 218.4 | 535.7 | 305.9
3044.1 | 2823.1 | 465.9 | 223 | 218.4 | 535.8 | 305.8
3045.1 | 2824.1 | 465.7 | 222.4 | 218.2 | 535.9 | 305.6
3046.1 | 2825.1 | 465.5 | 222.3 | 217.7 | 535.9 | 305.3
3047.1 | 2826.1 | 465.2 | 221.8 | 217.1 | 536 | 305
3048.1 | 2827.1 | 465 | 221.4 | 216.4 | 535.9 | 304.6
3049.1 | 2828.1 | 464.8 | 221.7 | 216.2 | 535.9 | 304.5
3050.1 | 2829.1 | 464.6 | 221.4 | 215.3 | 536 | 304.4
3051.1 | 2830.1 | 464.4 | 221.1 | 214.8 | 535.9 | 304.2
3052.1 | 2831.1 | 464.2 | 221 | 214.5 | 535.9 | 304
3053.1 | 2832.1 | 464 | 220.9 | 214.2 | 535.7 | 304
3054.1 | 2833.1 | 463.8 | 221.1 | 213.5 | 535.8 | 303.8
3055.1 | 2834.1 | 463.6 | 220.5 | 213.8 | 535.9 | 303.5
3056.1 | 2835.1 | 463.4 | 220.3 | 213.8 | 535.8 | 303.3
3057.1 | 2836.1 | 463.2 | 220 | 213.6 | 535.8 | 303.1
3058.1 | 2837.1 | 463 | 219.6 | 213.5 | 535.8 | 303
3059.1 | 2838.1 | 462.8 | 219.3 | 213.2 | 535.9 | 302.9
3060.1 | 2839.1 | 462.6 | 219 | 213.1 | 535.9 | 302.7
3061.1 | 2840.1 | 462.4 | 218.9 | 212.6 | 535.8 | 302.1
3062.1 | 2841.1 | 462.2 | 219.3 | 212.1 | 535.6 | 301.7
3063.1 | 2842.1 | 462 | 220.3 | 212 | 535.5 | 301.6
3064.1 | 2843.1 | 461.8 | 220.5 | 211.8 | 535.5 | 301.5
3065.1 | 2844.1 | 461.6 | 220.4 | 211.1 | 535.4 | 301.3
3066.1 | 2845.1 | 461.4 | 220.1 | 211.5 | 535.4 | 301.2
3067.1 | 2846.1 | 461.3 | 220 | 211.2 | 535.4 | 300.9
3068.1 | 2847.1 | 461.1 | 220.9 | 211.3 | 535.3 | 300.8
3069.1 | 2848.1 | 461 | 220.7 | 211.6 | 535.3 | 300.7
3070.1 | 2849.1 | 460.8 | 220.2 | 211.6 | 535.3 | 300.6
3071.1 | 2850.1 | 460.7 | 219.7 | 211.4 | 535.4 | 300.4
3072.1 | 2851.1 | 460.5 | 219.1 | 211.3 | 535.3 | 300.1
3073.1 | 2852.1 | 460.4 | 218.6 | 211.1 | 535.3 | 299.9
3074.1 | 2853.1 | 460.2 | 218.3 | 211 | 535.2 | 299.6
3075.1 | 2854.1 | 460 | 218.1 | 210.6 | 535 | 299.6
3076.1 | 2855.1 | 459.9 | 217.5 | 210.3 | 534.9 | 299.4
3077.1 | 2856.1 | 459.7 | 217 | 210.1 | 534.7 | 299
3078.1 | 2857.1 | 459.5 | 217.6 | 209.5 | 534.5 | 298.9
3079.1 | 2858.1 | 459.4 | 217.2 | 208.7 | 534.3 | 298.7
3080.1 | 2859.1 | 459.2 | 216.6 | 208.1 | 534.2 | 298.6
3081.1 | 2860.1 | 459 | 216.3 | 208.1 | 534.2 | 298.5
3082.1 | 2861.1 | 458.8 | 216.3 | 208.1 | 534 | 298.4
3083.1 | 2862.1 | 458.6 | 216.8 | 207.8 | 533.8 | 298.1
3084.1 | 2863.1 | 458.5 | 216.8 | 207.9 | 533.8 | 297.6
3085.1 | 2864.1 | 458.3 | 216.4 | 207.7 | 533.8 | 297.5
3086.1 | 2865.1 | 458.1 | 216.3 | 207.9 | 533.7 | 297.4
3087.1 | 2866.1 | 457.9 | 217.2 | 208.1 | 533.6 | 297.4
3088.1 | 2867.1 | 457.8 | 217.1 | 207.9 | 533.5 | 296.9
3089.1 | 2868.1 | 457.6 | 216.6 | 207.8 | 533.6 | 296.8
3090.1 | 2869.1 | 457.4 | 216.1 | 207.3 | 533.7 | 296.7
3091.1 | 2870.1 | 457.2 | 215.6 | 206.1 | 534 | 296.4
3092.1 | 2871.1 | 457 | 215.4 | 205.2 | 534.3 | 296.2
3093.1 | 2872.1 | 456.9 | 215.5 | 204.3 | 534.4 | 295.9
3094.1 | 2873.1 | 456.7 | 214.7 | 203.4 | 534.3 | 295.7
3095.1 | 2874.1 | 456.5 | 214.4 | 203.1 | 534.3 | 295.6
3096.1 | 2875.1 | 456.3 | 214.5 | 202.9 | 534.3 | 295.5
3097.1 | 2876.1 | 456.1 | 214.7 | 202.6 | 534.2 | 295.4
3098.1 | 2877.1 | 456 | 214.4 | 202.7 | 534.1 | 295.3
3099.1 | 2878.1 | 455.8 | 215.1 | 202.7 | 534 | 295.2
3100.1 | 2879.1 | 455.6 | 215.4 | 203.1 | 533.7 | 295.1
3101.1 | 2880.1 | 455.5 | 215.9 | 203.2 | 533.4 | 295
3102.1 | 2881.1 | 455.3 | 215.5 | 203 | 533.2 | 294.8
3103.1 | 2882.1 | 455.1 | 215.6 | 202.5 | 533.2 | 294.7
3104.1 | 2883.1 | 454.9 | 216.4 | 201.9 | 533.1 | 294.6
3105.1 | 2884.1 | 454.7 | 216.5 | 201.8 | 533 | 294.4
3106.1 | 2885.1 | 454.5 | 217.5 | 201.3 | 532.8 | 293.6
3107.1 | 2886.1 | 454.3 | 218.1 | 201.3 | 532.6 | 293.2
3108.1 | 2887.1 | 454.1 | 218.1 | 201.2 | 532.5 | 293.3
3109.1 | 2888.1 | 453.9 | 217.8 | 200.5 | 532.4 | 293.2
3110.1 | 2889.1 | 453.7 | 217.1 | 200.3 | 532.3 | 293.1
3111.1 | 2890.1 | 453.5 | 216.4 | 200.1 | 532.3 | 292.8
3112.1 | 2891.1 | 453.3 | 216.4 | 200 | 532.2 | 292.3
3113.1 | 2892.1 | 453.1 | 216.1 | 199.9 | 532.2 | 292.2
3114.1 | 2893.1 | 452.9 | 215.5 | 199.6 | 532.2 | 292.1
3115.1 | 2894.1 | 452.7 | 215 | 199.3 | 532.2 | 291.9
3116.1 | 2895.1 | 452.5 | 214.5 | 199.1 | 532.5 | 291.7
3117.1 | 2896.1 | 452.4 | 214.7 | 198.6 | 532.5 | 291.3
3118.1 | 2897.1 | 452.2 | 214.5 | 198.4 | 532.6 | 290.8
3119.1 | 2898.1 | 452 | 213.9 | 198.3 | 532.7 | 290.7
3120.1 | 2899.1 | 451.8 | 213.5 | 198.2 | 533 | 290.6
3121.1 | 2900.1 | 451.6 | 212.6 | 197.9 | 533.2 | 290.3
3122.1 | 2901.1 | 451.4 | 211.7 | 197.7 | 533.4 | 290
3123.1 | 2902.1 | 451.2 | 211.3 | 197.4 | 533.6 | 289.9
3124.1 | 2903.1 | 451.1 | 211.1 | 196.9 | 533.6 | 289.7
3125.1 | 2904.1 | 450.9 | 211.2 | 196.8 | 533.5 | 289.6
3126.1 | 2905.1 | 450.7 | 211.5 | 196.9 | 533.4 | 289.6
3127.1 | 2906.1 | 450.5 | 212 | 197 | 533.3 | 289.5
3128.1 | 2907.1 | 450.3 | 212.8 | 197.3 | 533.3 | 289.4
3129.1 | 2908.1 | 450.1 | 213.9 | 197.4 | 533.4 | 289.3
3130.1 | 2909.1 | 450 | 213.4 | 197.3 | 533.4 | 289.1
3131.1 | 2910.1 | 449.8 | 213.8 | 197.2 | 533.1 | 289
3132.1 | 2911.1 | 449.6 | 213.8 | 197.3 | 532.8 | 288.9
3133.1 | 2912.1 | 449.4 | 213.2 | 197.6 | 532.6 | 288.7
3134.1 | 2913.1 | 449.2 | 214 | 197.4 | 532.4 | 288.7
3135.1 | 2914.1 | 449.1 | 214 | 197.1 | 532.3 | 288.6
3136.1 | 2915.1 | 448.9 | 214 | 196.8 | 532.2 | 288.6
3137.1 | 2916.1 | 448.7 | 213.4 | 196.5 | 532.1 | 288.5
3138.1 | 2917.1 | 448.5 | 213.5 | 196.1 | 532.1 | 288.4
3139.1 | 2918.1 | 448.4 | 213.6 | 195.3 | 532.3 | 288.2
3140.1 | 2919.1 | 448.2 | 214 | 194.3 | 532.2 | 287.9
3141.1 | 2920.1 | 448 | 213.9 | 193.3 | 532.1 | 287.5
3142.1 | 2921.1 | 447.9 | 214 | 193 | 532 | 287.1
3143.1 | 2922.1 | 447.7 | 214.7 | 192.1 | 531.9 | 286.9
3144.1 | 2923.1 | 447.5 | 214.4 | 191.8 | 532 | 286.6
3145.1 | 2924.1 | 447.3 | 214.6 | 191.9 | 532.1 | 286.4
3146.1 | 2925.1 | 447.2 | 213.5 | 192 | 532.1 | 286.3
3147.1 | 2926.1 | 447 | 212.1 | 192.1 | 532.1 | 286.2
3148.1 | 2927.1 | 446.9 | 211.6 | 192.3 | 532 | 285.9
3149.1 | 2928.1 | 446.7 | 211.1 | 192.6 | 531.9 | 285.7
3150.1 | 2929.1 | 446.6 | 211.6 | 192.6 | 531.8 | 285.4
3151.1 | 2930.1 | 446.4 | 211.3 | 192.5 | 531.7 | 284.9
3152.1 | 2931.1 | 446.3 | 210.5 | 192.6 | 531.7 | 284.7
3153.1 | 2932.1 | 446.1 | 209.7 | 192.3 | 531.7 | 284.7
3154.1 | 2933.1 | 445.9 | 209.5 | 192 | 531.7 | 284.4
3155.1 | 2934.1 | 445.8 | 210.5 | 191.7 | 531.6 | 284.1
3156.1 | 2935.1 | 445.7 | 210.4 | 191.5 | 531.5 | 283.8
3157.1 | 2936.1 | 445.5 | 209.6 | 191.2 | 531.4 | 283.9
3158.1 | 2937.1 | 445.4 | 209.4 | 190.8 | 531.3 | 283.7
3159.1 | 2938.1 | 445.2 | 208.9 | 191.2 | 531.3 | 283
3160.1 | 2939.1 | 445.1 | 208.4 | 191.4 | 531.2 | 282.9
3161.1 | 2940.1 | 444.9 | 207.6 | 190.9 | 531 | 283
3162.1 | 2941.1 | 444.8 | 206.8 | 190.4 | 530.8 | 282.8
3163.1 | 2942.1 | 444.6 | 206 | 190.2 | 530.7 | 282.2
3164.1 | 2943.1 | 444.4 | 205 | 189.9 | 530.6 | 282.1
3165.1 | 2944.1 | 444.3 | 204.6 | 189.7 | 530.4 | 282.1
3166.1 | 2945.1 | 444.1 | 204.2 | 189.5 | 530.4 | 281.9
3167.1 | 2946.1 | 444 | 204 | 189.5 | 530.3 | 281.6
3168.1 | 2947.1 | 443.9 | 204.7 | 189.3 | 530.3 | 281.5
3169.1 | 2948.1 | 443.7 | 205.5 | 189.1 | 530.2 | 281.4
3170.1 | 2949.1 | 443.5 | 206.8 | 188.7 | 530.2 | 281.2
3171.1 | 2950.1 | 443.4 | 207.6 | 188.4 | 530.2 | 281
3172.1 | 2951.1 | 443.2 | 208.1 | 188.4 | 530.3 | 280.9
3173.1 | 2952.1 | 443.1 | 208.4 | 188.2 | 530.4 | 280.8
3174.1 | 2953.1 | 442.9 | 209.4 | 187.9 | 530.4 | 280.6
3175.1 | 2954.1 | 442.8 | 210.5 | 187.6 | 530.5 | 280.3
3176.1 | 2955.1 | 442.6 | 210.8 | 187.5 | 530.6 | 279.8
3177.1 | 2956.1 | 442.4 | 211.3 | 187.1 | 530.7 | 279.8
3178.1 | 2957.1 | 442.3 | 211.6 | 186.7 | 530.9 | 279.7
3179.1 | 2958.1 | 442.1 | 211.8 | 186.3 | 530.9 | 279.5
3180.1 | 2959.1 | 441.9 | 211.8 | 186.1 | 530.9 | 279.4
3181.1 | 2960.1 | 441.8 | 212.7 | 185.9 | 530.8 | 279.1
3182.1 | 2961.1 | 441.6 | 212.8 | 185.8 | 530.7 | 278.9
3183.1 | 2962.1 | 441.4 | 213.1 | 185.7 | 530.6 | 278.7
3184.1 | 2963.1 | 441.2 | 213.3 | 185.8 | 530.5 | 278.6
3185.1 | 2964.1 | 441.1 | 214.1 | 185.7 | 530.4 | 278.6
3186.1 | 2965.1 | 440.9 | 213.9 | 185.4 | 530.3 | 278.5
3187.1 | 2966.1 | 440.7 | 213 | 185 | 530.2 | 278.3
3188.1 | 2967.1 | 440.5 | 212.7 | 184.5 | 530.1 | 278.2
3189.1 | 2968.1 | 440.3 | 213 | 183.9 | 530 | 277.8
3190.1 | 2969.1 | 440.2 | 212.7 | 183.4 | 529.9 | 277.5
3191.1 | 2970.1 | 440 | 212.3 | 183 | 529.9 | 277.5
3192.1 | 2971.1 | 439.8 | 211.4 | 182.7 | 530.2 | 277.2
3193.1 | 2972.1 | 439.6 | 211.2 | 182.2 | 530.1 | 276.8
3194.1 | 2973.1 | 439.4 | 211 | 182 | 530.1 | 276.4
3195.1 | 2974.1 | 439.3 | 211.1 | 181.8 | 530.2 | 276
3196.1 | 2975.1 | 439.1 | 211.1 | 181.5 | 530.2 | 275.8
3197.1 | 2976.1 | 438.9 | 210.8 | 181.3 | 530.4 | 275.6
3198.1 | 2977.1 | 438.7 | 209.8 | 181.1 | 530.5 | 275.5
3199.1 | 2978.1 | 438.5 | 208.9 | 180.7 | 530.7 | 275.3
3200.1 | 2979.1 | 438.3 | 208.1 | 180.2 | 530.8 | 274.9
3201.1 | 2980.1 | 438.1 | 207.7 | 180 | 530.8 | 274.8
3202.1 | 2981.1 | 437.9 | 208.2 | 179.5 | 530.8 | 274.7
3203.1 | 2982.1 | 437.7 | 209 | 179 | 530.8 | 274.5
3204.1 | 2983.1 | 437.5 | 208.3 | 178.6 | 531.1 | 274
3205.1 | 2984.1 | 437.4 | 207.8 | 178.1 | 531.3 | 273.7
3206.1 | 2985.1 | 437.2 | 208.6 | 177.7 | 531.2 | 273.5
3207.1 | 2986.1 | 437 | 208.5 | 177.3 | 531.1 | 273.2
3208.1 | 2987.1 | 436.8 | 208.7 | 176.9 | 531.1 | 272.8
3209.1 | 2988.1 | 436.6 | 209.3 | 176.5 | 530.9 | 272.7
3210.1 | 2989.1 | 436.5 | 209.6 | 176.3 | 530.7 | 272.2
3211.1 | 2990.1 | 436.3 | 209 | 175.6 | 530.7 | 271.9
3212.1 | 2991.1 | 436.1 | 207.7 | 174.8 | 530.5 | 271.4
3213.1 | 2992.1 | 435.9 | 207.9 | 174.4 | 530.3 | 271.2
3214.1 | 2993.1 | 435.7 | 207.6 | 173.9 | 530.3 | 270.8
3215.1 | 2994.1 | 435.6 | 207.9 | 173.5 | 530.2 | 270.5
3216.1 | 2995.1 | 435.4 | 208.2 | 173 | 530 | 270.2
3217.1 | 2996.1 | 435.2 | 208.2 | 172.5 | 529.9 | 269.7
3218.1 | 2997.1 | 435.1 | 208.7 | 172.2 | 529.8 | 269.4
3219.1 | 2998.1 | 434.9 | 209.1 | 172 | 529.7 | 269.1
3220.1 | 2999.1 | 434.7 | 209.9 | 171.8 | 529.7 | 268.8
3221.1 | 3000.1 | 434.5 | 210.4 | 171.5 | 529.6 | 268.8
3222.1 | 3001.1 | 434.4 | 210.8 | 171.6 | 529.6 | 268.8
3223.1 | 3002.1 | 434.2 | 210.8 | 171.8 | 529.4 | 268.8
3224.1 | 3003.1 | 434 | 210.9 | 172 | 529.2 | 268.6
3225.1 | 3004.1 | 433.9 | 210.2 | 172.2 | 528.9 | 268.3
3226.1 | 3005.1 | 433.7 | 209.4 | 172.5 | 528.7 | 268.3
3227.1 | 3006.1 | 433.6 | 208.7 | 172.7 | 528.6 | 268.3
3228.1 | 3007.1 | 433.4 | 207.4 | 173 | 528.5 | 268.2
3229.1 | 3008.1 | 433.3 | 206.4 | 173 | 528.4 | 268.2
3230.1 | 3009.1 | 433.1 | 206.3 | 173.3 | 528.2 | 268
3231.1 | 3010.1 | 432.9 | 206 | 173.4 | 528.1 | 267.9
3232.1 | 3011.1 | 432.8 | 205.8 | 173.1 | 527.9 | 267.8
3233.1 | 3012.1 | 432.6 | 205.4 | 173.1 | 527.8 | 267.8
3234.1 | 3013.1 | 432.5 | 206.4 | 173.2 | 527.6 | 267.7
3235.1 | 3014.1 | 432.3 | 207.2 | 173.3 | 527.3 | 267.7
3236.1 | 3015.1 | 432.2 | 207.1 | 173.4 | 527 | 267.5
3237.1 | 3016.1 | 432 | 206.8 | 173.3 | 526.8 | 267.5
3238.1 | 3017.1 | 431.9 | 206.5 | 173.1 | 526.5 | 267.3
3239.1 | 3018.1 | 431.7 | 207 | 173 | 526.3 | 267.1
3240.1 | 3019.1 | 431.5 | 206.3 | 172.9 | 526.1 | 267.1
3241.1 | 3020.1 | 431.4 | 205.8 | 172.7 | 525.9 | 267.1
3242.1 | 3021.1 | 431.2 | 206.2 | 172.7 | 525.7 | 266.9
3243.1 | 3022.1 | 431.1 | 206.9 | 173 | 525.6 | 266.5
3244.1 | 3023.1 | 430.9 | 207.5 | 173.2 | 525.5 | 266.3
3245.1 | 3024.1 | 430.8 | 207.5 | 173.4 | 525.4 | 266.1
3246.1 | 3025.1 | 430.6 | 207.8 | 173.8 | 525.4 | 265.8
3247.1 | 3026.1 | 430.4 | 208.1 | 173.6 | 525.4 | 265.6
3248.1 | 3027.1 | 430.2 | 207.4 | 173.6 | 525.3 | 265.6
3249.1 | 3028.1 | 430.1 | 207.3 | 173.3 | 525.3 | 265.1
3250.1 | 3029.1 | 429.9 | 207.2 | 172.7 | 525.4 | 264.4
3251.1 | 3030.1 | 429.7 | 207.5 | 172.4 | 525.4 | 263.8
3252.1 | 3031.1 | 429.5 | 206.9 | 172.6 | 525.3 | 263.7
3253.1 | 3032.1 | 429.3 | 206.3 | 172.3 | 525.1 | 263.6
3254.1 | 3033.1 | 429.2 | 207.1 | 171.9 | 524.9 | 263.6
3255.1 | 3034.1 | 429 | 207.3 | 171.9 | 524.7 | 263.6
3256.1 | 3035.1 | 428.8 | 206.7 | 171.7 | 524.6 | 263.4
3257.1 | 3036.1 | 428.6 | 206.1 | 171.5 | 524.6 | 263
3258.1 | 3037.1 | 428.5 | 206.3 | 171.1 | 524.6 | 262.7
3259.1 | 3038.1 | 428.3 | 206.5 | 171 | 524.5 | 262.4
3260.1 | 3039.1 | 428.1 | 206.9 | 170.7 | 524.3 | 262.3
3261.1 | 3040.1 | 428 | 206 | 170.4 | 524.2 | 262.3
3262.1 | 3041.1 | 427.8 | 205.4 | 170.5 | 523.9 | 262.2
3263.1 | 3042.1 | 427.6 | 205.1 | 170.3 | 523.7 | 262.1
3264.1 | 3043.1 | 427.4 | 203.9 | 169.6 | 523.5 | 261.7
3265.1 | 3044.1 | 427.3 | 203.3 | 169 | 523.2 | 261.4
3266.1 | 3045.1 | 427.1 | 202.7 | 168.5 | 522.9 | 260.8
3267.1 | 3046.1 | 426.9 | 202.2 | 168.6 | 522.7 | 260.9
3268.1 | 3047.1 | 426.7 | 202.1 | 168.3 | 522.4 | 260.7
3269.1 | 3048.1 | 426.6 | 202.1 | 167.8 | 522.2 | 260.3
3270.1 | 3049.1 | 426.4 | 201.8 | 167.4 | 522.1 | 260.1
3271.1 | 3050.1 | 426.2 | 201.3 | 166.9 | 521.9 | 259.8
3272.1 | 3051.1 | 426 | 200.9 | 166.5 | 521.6 | 259.6
3273.1 | 3052.1 | 425.8 | 201.3 | 166.4 | 521.4 | 259.1
3274.1 | 3053.1 | 425.6 | 202.4 | 166.3 | 521.1 | 259.1
3275.1 | 3054.1 | 425.4 | 202.8 | 166.6 | 520.9 | 259
3276.1 | 3055.1 | 425.2 | 202.2 | 166.7 | 520.7 | 258.6
3277.1 | 3056.1 | 425.1 | 201.6 | 167 | 520.4 | 258.5
3278.1 | 3057.1 | 424.9 | 202 | 167.3 | 520.2 | 258.4
3279.1 | 3058.1 | 424.7 | 202.4 | 167.4 | 519.9 | 258
3280.1 | 3059.1 | 424.6 | 202.2 | 167.3 | 519.6 | 257.9
3281.1 | 3060.1 | 424.4 | 201.1 | 167.5 | 519.4 | 258.1
3282.1 | 3061.1 | 424.3 | 200.5 | 167.2 | 519.2 | 258
3283.1 | 3062.1 | 424.1 | 200.8 | 167.2 | 518.9 | 258
3284.1 | 3063.1 | 423.9 | 200.5 | 166.8 | 518.8 | 257.8
3285.1 | 3064.1 | 423.7 | 200.8 | 166.2 | 518.6 | 257.4
3286.1 | 3065.1 | 423.6 | 200.5 | 165.8 | 518.4 | 257.2
3287.1 | 3066.1 | 423.4 | 201 | 165.4 | 518.2 | 256.8
3288.1 | 3067.1 | 423.2 | 201.7 | 164.9 | 517.9 | 256.2
3289.1 | 3068.1 | 423 | 202 | 164.6 | 517.8 | 256
3290.1 | 3069.1 | 422.9 | 202.1 | 164.8 | 517.7 | 256.1
3291.1 | 3070.1 | 422.7 | 202.3 | 165 | 517.6 | 256.2
3292.1 | 3071.1 | 422.5 | 201.9 | 165.1 | 517.4 | 256.2
3293.1 | 3072.1 | 422.3 | 201.1 | 165.1 | 517.2 | 256.1
3294.1 | 3073.1 | 422.2 | 200.3 | 165.1 | 517 | 256
3295.1 | 3074.1 | 422 | 198.9 | 164.5 | 516.8 | 255.6
3296.1 | 3075.1 | 421.8 | 197.8 | 164.4 | 516.5 | 255.3
3297.1 | 3076.1 | 421.7 | 197.4 | 164.3 | 516.3 | 255.2
3298.1 | 3077.1 | 421.5 | 197.7 | 163.8 | 516.1 | 254.9
3299.1 | 3078.1 | 421.3 | 198.3 | 163.5 | 515.9 | 254.8
3300.1 | 3079.1 | 421.1 | 198 | 163.5 | 515.6 | 254.7
3301.1 | 3080.1 | 421 | 197.8 | 163.6 | 515.3 | 254.7
3302.1 | 3081.1 | 420.8 | 197.8 | 163.7 | 515.2 | 254.4
3303.1 | 3082.1 | 420.6 | 197.9 | 163.7 | 515 | 253.9
3304.1 | 3083.1 | 420.4 | 197.7 | 163.5 | 514.8 | 253.9
3305.1 | 3084.1 | 420.2 | 197.9 | 163.3 | 514.7 | 253.8
3306.1 | 3085.1 | 420.1 | 198.1 | 163.3 | 514.5 | 253.6
3307.1 | 3086.1 | 419.9 | 197.5 | 162.8 | 514.2 | 253.5
3308.1 | 3087.1 | 419.7 | 196.9 | 162.7 | 514 | 253.6
3309.1 | 3088.1 | 419.5 | 197.1 | 162.4 | 513.8 | 253.5
3310.1 | 3089.1 | 419.3 | 196.9 | 162.2 | 513.5 | 253.4
3311.1 | 3090.1 | 419.2 | 196.8 | 162.2 | 513.3 | 253.2
3312.1 | 3091.1 | 419 | 197 | 162.3 | 513 | 253.2
3313.1 | 3092.1 | 418.8 | 196.8 | 162.4 | 512.8 | 253.2
3314.1 | 3093.1 | 418.6 | 196.5 | 162.4 | 512.5 | 253.1
3315.1 | 3094.1 | 418.4 | 196.3 | 162 | 512.4 | 253
3316.1 | 3095.1 | 418.3 | 195.9 | 161.6 | 512.2 | 252.6
3317.1 | 3096.1 | 418.1 | 195.3 | 161.2 | 512 | 252.3
3318.1 | 3097.1 | 417.9 | 194.9 | 160.8 | 511.8 | 252.1
3319.1 | 3098.1 | 417.7 | 194.5 | 160.6 | 511.6 | 251.7
3320.1 | 3099.1 | 417.5 | 194.4 | 160.3 | 511.4 | 251.3
3321.1 | 3100.1 | 417.3 | 194.8 | 160 | 511.2 | 251.1
3322.1 | 3101.1 | 417.2 | 195 | 159.5 | 511 | 251
3323.1 | 3102.1 | 417 | 195.5 | 159.4 | 510.7 | 250.6
3324.1 | 3103.1 | 416.8 | 196.2 | 159.6 | 510.4 | 250.4
3325.1 | 3104.1 | 416.6 | 196.5 | 159.8 | 510.2 | 250.2
3326.1 | 3105.1 | 416.4 | 197.2 | 159.7 | 509.9 | 250.2
3327.1 | 3106.1 | 416.2 | 197.5 | 159.7 | 509.6 | 250
3328.1 | 3107.1 | 416.1 | 198 | 159.9 | 509.4 | 249.9
3329.1 | 3108.1 | 415.9 | 197.9 | 159.9 | 509.1 | 249.5
3330.1 | 3109.1 | 415.7 | 197.8 | 160.1 | 508.8 | 249.4
3331.1 | 3110.1 | 415.5 | 197.9 | 160.1 | 508.6 | 249.3
3332.1 | 3111.1 | 415.3 | 197.3 | 160 | 508.2 | 249
3333.1 | 3112.1 | 415.1 | 196.3 | 159.7 | 507.9 | 248.6
3334.1 | 3113.1 | 415 | 196 | 159.5 | 507.6 | 248.2
3335.1 | 3114.1 | 414.8 | 196.1 | 159.7 | 507.4 | 247.9
3336.1 | 3115.1 | 414.6 | 195.4 | 159.5 | 507 | 247.8
3337.1 | 3116.1 | 414.4 | 195.5 | 159.6 | 506.8 | 247.5
3338.1 | 3117.1 | 414.2 | 195.4 | 159.3 | 506.5 | 247.3
3339.1 | 3118.1 | 414.1 | 195.7 | 159.3 | 506.1 | 247.3
3340.1 | 3119.1 | 413.9 | 195.8 | 159.2 | 505.8 | 247.2
3341.1 | 3120.1 | 413.7 | 196.1 | 158.7 | 505.4 | 247.1
3342.1 | 3121.1 | 413.5 | 195.5 | 158.4 | 505.1 | 246.9
3343.1 | 3122.1 | 413.3 | 195.2 | 158.5 | 504.8 | 246.7
3344.1 | 3123.1 | 413.2 | 194.7 | 158.5 | 504.5 | 246.4
3345.1 | 3124.1 | 413 | 194.3 | 158 | 504.2 | 246
3346.1 | 3125.1 | 412.9 | 193.8 | 157.9 | 504 | 245.7
3347.1 | 3126.1 | 412.7 | 192.4 | 157.8 | 503.7 | 245.4
3348.1 | 3127.1 | 412.5 | 192.1 | 157.7 | 503.3 | 245.2
3349.1 | 3128.1 | 412.4 | 192.4 | 157.2 | 502.9 | 245.1
3350.1 | 3129.1 | 412.2 | 193 | 156.8 | 502.6 | 244.7
3351.1 | 3130.1 | 412 | 193.3 | 156.8 | 502.2 | 244.6
3352.1 | 3131.1 | 411.8 | 192.6 | 156.6 | 501.9 | 244.5
3353.1 | 3132.1 | 411.6 | 192.3 | 156.3 | 501.5 | 244.2
3354.1 | 3133.1 | 411.5 | 192.2 | 156.3 | 501.2 | 244.1
3355.1 | 3134.1 | 411.3 | 191.7 | 156.2 | 500.8 | 244.2
3356.1 | 3135.1 | 411.1 | 192.6 | 156 | 500.4 | 244
3357.1 | 3136.1 | 410.9 | 193.2 | 155.9 | 500.1 | 243.7
3358.1 | 3137.1 | 410.7 | 193.6 | 155.8 | 499.6 | 243.3
3359.1 | 3138.1 | 410.5 | 193.3 | 155.8 | 499.2 | 243.1
3360.1 | 3139.1 | 410.3 | 192.6 | 155.6 | 498.8 | 242.9
3361.1 | 3140.1 | 410.2 | 192.1 | 155.5 | 498.4 | 242.9
3362.1 | 3141.1 | 410 | 192 | 155.3 | 498 | 242.5
3363.1 | 3142.1 | 409.8 | 192 | 155.1 | 497.7 | 241.9
3364.1 | 3143.1 | 409.6 | 191.6 | 154.8 | 497.3 | 241.7
3365.1 | 3144.1 | 409.5 | 191.4 | 154.6 | 497 | 241.5
3366.1 | 3145.1 | 409.3 | 192 | 154.4 | 496.5 | 241.4
3367.1 | 3146.1 | 409.1 | 192 | 154 | 496.1 | 241.3
3368.1 | 3147.1 | 409 | 191.5 | 154 | 495.7 | 241.2
3369.1 | 3148.1 | 408.8 | 191.9 | 153.6 | 495.2 | 241
3370.1 | 3149.1 | 408.6 | 191.8 | 153.4 | 494.8 | 240.7
3371.1 | 3150.1 | 408.4 | 192.1 | 153.3 | 494.4 | 240.7
3372.1 | 3151.1 | 408.3 | 191.9 | 153.1 | 494.1 | 240.2
3373.1 | 3152.1 | 408.1 | 191.6 | 152.9 | 493.9 | 239.9
3374.1 | 3153.1 | 407.9 | 191.3 | 152.6 | 493.5 | 239.9
3375.1 | 3154.1 | 407.7 | 191.1 | 152.2 | 493.1 | 239.7
3376.1 | 3155.1 | 407.5 | 190.5 | 151.8 | 492.8 | 239.5
3377.1 | 3156.1 | 407.3 | 190.2 | 151.3 | 492.5 | 239.1
3378.1 | 3157.1 | 407.1 | 190.6 | 150.6 | 492.2 | 238.6
3379.1 | 3158.1 | 407 | 190.9 | 150.6 | 491.9 | 238.3
3380.1 | 3159.1 | 406.7 | 190.6 | 150.2 | 491.5 | 238.3
3381.1 | 3160.1 | 406.6 | 190.8 | 149.9 | 491.2 | 238
3382.1 | 3161.1 | 406.3 | 190.7 | 149.6 | 490.8 | 237.7
3383.1 | 3162.1 | 406.2 | 190.9 | 149.6 | 490.4 | 237.5
3384.1 | 3163.1 | 406 | 191.5 | 149.4 | 489.9 | 237.4
3385.1 | 3164.1 | 405.8 | 192.3 | 149.3 | 489.4 | 237
3386.1 | 3165.1 | 405.7 | 192.5 | 149.3 | 489 | 236.7
3387.1 | 3166.1 | 405.5 | 193 | 149.2 | 488.5 | 236.6
3388.1 | 3167.1 | 405.3 | 192.3 | 149.4 | 488.1 | 236.6
3389.1 | 3168.1 | 405.2 | 191.8 | 149.4 | 487.6 | 236.5
3390.1 | 3169.1 | 405 | 191.8 | 149.5 | 487.1 | 236.2
3391.1 | 3170.1 | 404.8 | 191.1 | 149.4 | 486.7 | 235.9
3392.1 | 3171.1 | 404.7 | 190.4 | 149.5 | 486.2 | 235.9
3393.1 | 3172.1 | 404.5 | 189.5 | 149.4 | 485.7 | 236
3394.1 | 3173.1 | 404.3 | 188.4 | 149.3 | 485.2 | 236.1
3395.1 | 3174.1 | 404.2 | 187.3 | 149.3 | 484.7 | 236
3396.1 | 3175.1 | 404 | 187.1 | 149.4 | 484.1 | 235.6
3397.1 | 3176.1 | 403.8 | 186.6 | 149.3 | 483.6 | 235.1
3398.1 | 3177.1 | 403.6 | 187.3 | 149 | 483.1 | 235.1
3399.1 | 3178.1 | 403.5 | 187.8 | 148.9 | 482.5 | 234.8
3400.1 | 3179.1 | 403.3 | 186.9 | 148.7 | 482.1 | 234.4
3401.1 | 3180.1 | 403.1 | 186.7 | 148.5 | 481.6 | 234.1
3402.1 | 3181.1 | 403 | 187.3 | 148.4 | 481.1 | 234
3403.1 | 3182.1 | 402.8 | 186.9 | 148.4 | 480.6 | 233.6
3404.1 | 3183.1 | 402.6 | 187.1 | 148.2 | 480.2 | 233.2
3405.1 | 3184.1 | 402.4 | 186.6 | 147.9 | 479.7 | 233
3406.1 | 3185.1 | 402.2 | 186.3 | 147.8 | 479.3 | 232.9
3407.1 | 3186.1 | 402 | 186.5 | 147.5 | 478.8 | 232.7
3408.1 | 3187.1 | 401.9 | 186.2 | 147.3 | 478.4 | 232.6
3409.1 | 3188.1 | 401.7 | 186.5 | 147.2 | 478 | 232.4
3410.1 | 3189.1 | 401.5 | 186 | 147.3 | 477.5 | 232.4
3411.1 | 3190.1 | 401.3 | 185.4 | 147.4 | 477 | 232.3
3412.1 | 3191.1 | 401.1 | 185.3 | 147.4 | 476.5 | 232.1
3413.1 | 3192.1 | 401 | 185.3 | 147.3 | 476 | 231.8
3414.1 | 3193.1 | 400.8 | 184.9 | 147.4 | 475.5 | 231.6
3415.1 | 3194.1 | 400.6 | 184.7 | 147.4 | 474.9 | 231.2
3416.1 | 3195.1 | 400.5 | 185.1 | 147.6 | 474.4 | 230.8
3417.1 | 3196.1 | 400.3 | 185.6 | 147.6 | 473.9 | 230.5
3418.1 | 3197.1 | 400.1 | 185.7 | 147.5 | 473.4 | 230.3
3419.1 | 3198.1 | 399.9 | 185.4 | 147.4 | 472.9 | 230.2
3420.1 | 3199.1 | 399.7 | 185.2 | 147.4 | 472.4 | 230.1
3421.1 | 3200.1 | 399.5 | 185.8 | 147.4 | 471.9 | 229.8
3422.1 | 3201.1 | 399.4 | 185.9 | 147.4 | 471.3 | 230
3423.1 | 3202.1 | 399.2 | 186.2 | 147.2 | 470.8 | 230.1
3424.1 | 3203.1 | 399.1 | 186.8 | 147.1 | 470.2 | 230.1
3425.1 | 3204.1 | 398.9 | 187.3 | 146.9 | 469.7 | 230.1
3426.1 | 3205.1 | 398.8 | 186.7 | 146.6 | 469.1 | 230.1
3427.1 | 3206.1 | 398.6 | 186.3 | 146.5 | 468.5 | 230
3428.1 | 3207.1 | 398.4 | 185.9 | 146.4 | 468 | 229.8
3429.1 | 3208.1 | 398.2 | 185.8 | 146.5 | 467.4 | 229.9
3430.1 | 3209.1 | 398.1 | 185.7 | 146.4 | 466.9 | 230.1
3431.1 | 3210.1 | 397.9 | 185.3 | 146.4 | 466.3 | 229.8
3432.1 | 3211.1 | 397.7 | 185 | 145.9 | 465.8 | 229.7
3433.1 | 3212.1 | 397.5 | 185.5 | 145.4 | 465.2 | 229.4
3434.1 | 3213.1 | 397.4 | 185.3 | 145.1 | 464.7 | 229.1
3435.1 | 3214.1 | 397.2 | 185.6 | 144.6 | 464.2 | 228.8
3436.1 | 3215.1 | 397 | 185.6 | 144.3 | 463.6 | 228.5
3437.1 | 3216.1 | 396.8 | 186.1 | 143.9 | 463.1 | 228.4
3438.1 | 3217.1 | 396.7 | 186.3 | 143.2 | 462.6 | 228
3439.1 | 3218.1 | 396.5 | 186.1 | 142.8 | 462.1 | 227.6
3440.1 | 3219.1 | 396.3 | 186 | 142.7 | 461.6 | 227.5
3441.1 | 3220.1 | 396.1 | 185.9 | 142.8 | 461.2 | 227.5
3442.1 | 3221.1 | 395.9 | 185.1 | 142.8 | 460.7 | 227.5
3443.1 | 3222.1 | 395.7 | 184.6 | 142.7 | 460.2 | 227.4
3444.1 | 3223.1 | 395.5 | 183.8 | 142.6 | 459.6 | 227.2
3445.1 | 3224.1 | 395.3 | 183.4 | 142.8 | 459.1 | 226.9
3446.1 | 3225.1 | 395.2 | 183.3 | 142.9 | 458.5 | 226.8
3447.1 | 3226.1 | 395 | 183.6 | 142.9 | 458 | 226.6
3448.1 | 3227.1 | 394.8 | 183.6 | 142.8 | 457.4 | 226.2
3449.1 | 3228.1 | 394.6 | 183.9 | 142.9 | 456.8 | 226.1
3450.1 | 3229.1 | 394.4 | 183.8 | 143 | 456.2 | 226
3451.1 | 3230.1 | 394.3 | 183.2 | 142.9 | 455.6 | 225.7
3452.1 | 3231.1 | 394.1 | 183 | 142.8 | 455 | 225.4
3453.1 | 3232.1 | 393.9 | 183.2 | 142.8 | 454.4 | 225.4
3454.1 | 3233.1 | 393.7 | 183.2 | 143 | 453.8 | 225.4
3455.1 | 3234.1 | 393.6 | 183 | 143.1 | 453.2 | 225.3
3456.1 | 3235.1 | 393.4 | 182.4 | 143.1 | 452.6 | 225.2
3457.1 | 3236.1 | 393.2 | 181.8 | 143 | 452 | 225
3458.1 | 3237.1 | 393.1 | 181.7 | 142.9 | 451.3 | 224.5
3459.1 | 3238.1 | 392.9 | 182.2 | 142.9 | 450.7 | 224
3460.1 | 3239.1 | 392.7 | 182 | 142.8 | 450 | 223.9
3461.1 | 3240.1 | 392.6 | 182.3 | 142.8 | 449.4 | 224.1
3462.1 | 3241.1 | 392.4 | 182.5 | 142.8 | 448.7 | 224
3463.1 | 3242.1 | 392.3 | 182.4 | 142.7 | 448 | 223.6
3464.1 | 3243.1 | 392.1 | 182.1 | 142.7 | 447.3 | 223.2
3465.1 | 3244.1 | 391.9 | 181.3 | 142.7 | 446.6 | 223
3466.1 | 3245.1 | 391.7 | 181 | 142.8 | 445.9 | 223.2
3467.1 | 3246.1 | 391.6 | 181 | 142.7 | 445.2 | 223.1
3468.1 | 3247.1 | 391.4 | 181 | 142.5 | 444.5 | 222.8
3469.1 | 3248.1 | 391.3 | 181.2 | 142.3 | 443.8 | 222.5
3470.1 | 3249.1 | 391.1 | 181.4 | 141.9 | 443.1 | 222.5
3471.1 | 3250.1 | 390.9 | 180.3 | 141.6 | 442.3 | 222.4
3472.1 | 3251.1 | 390.8 | 180.3 | 141.5 | 441.6 | 222.3
3473.1 | 3252.1 | 390.6 | 179.8 | 141.2 | 440.8 | 222.1
3474.1 | 3253.1 | 390.4 | 179 | 141.1 | 440.1 | 221.7
3475.1 | 3254.1 | 390.2 | 178.2 | 140.9 | 439.3 | 221.3
3476.1 | 3255.1 | 390 | 177.2 | 140.7 | 438.5 | 221.2
3477.1 | 3256.1 | 389.9 | 177.2 | 140.6 | 437.7 | 221.1
3478.1 | 3257.1 | 389.6 | 176.4 | 140.5 | 436.9 | 220.9
3479.1 | 3258.1 | 389.5 | 175.5 | 140.4 | 436 | 220.9
3480.1 | 3259.1 | 389.2 | 175.6 | 140.2 | 435.2 | 220.8
3481.1 | 3260.1 | 389.1 | 176.4 | 139.8 | 434.3 | 220.5
3482.1 | 3261.1 | 388.9 | 176.6 | 139.3 | 433.5 | 220.2
3483.1 | 3262.1 | 388.7 | 176.3 | 139 | 432.6 | 219.9
3484.1 | 3263.1 | 388.5 | 175.6 | 138.5 | 431.7 | 219.7
3485.1 | 3264.1 | 388.3 | 174.5 | 138.5 | 430.8 | 219.6
3486.1 | 3265.1 | 388.1 | 173.6 | 138.8 | 429.8 | 219.3
3487.1 | 3266.1 | 387.9 | 173.4 | 139.2 | 428.8 | 219.3
3488.1 | 3267.1 | 387.7 | 173.9 | 139.2 | 427.7 | 219.5
3489.1 | 3268.1 | 387.5 | 173.7 | 139 | 426.7 | 219.3
3490.1 | 3269.1 | 387.3 | 173.1 | 139.1 | 425.6 | 219.2
3491.1 | 3270.1 | 387.1 | 173.3 | 139.2 | 424.5 | 219.2
3492.1 | 3271.1 | 387 | 173 | 139.2 | 423.5 | 219
3493.1 | 3272.1 | 386.8 | 173.1 | 139.1 | 422.5 | 218.7
3494.1 | 3273.1 | 386.6 | 172.9 | 139.1 | 421.4 | 218.4
3495.1 | 3274.1 | 386.4 | 173.1 | 139.1 | 420.4 | 218.4
3496.1 | 3275.1 | 386.3 | 173.5 | 138.9 | 419.5 | 218.1
3497.1 | 3276.1 | 386.1 | 174.1 | 138.9 | 418.6 | 217.9
3498.1 | 3277.1 | 385.9 | 174.8 | 138.8 | 417.7 | 217.8
3499.1 | 3278.1 | 385.8 | 173.8 | 138.5 | 416.9 | 217.8
3500.1 | 3279.1 | 385.6 | 173.7 | 138 | 416 | 217.5
3501.1 | 3280.1 | 385.5 | 174 | 137.8 | 415.3 | 217.4
3502.1 | 3281.1 | 385.3 | 174.3 | 137.6 | 414.5 | 217.1
3503.1 | 3282.1 | 385.1 | 174 | 137.4 | 413.8 | 216.9
3504.1 | 3283.1 | 385 | 174 | 137.5 | 413 | 216.9
3505.1 | 3284.1 | 384.8 | 174.5 | 137.5 | 412.3 | 217
3506.1 | 3285.1 | 384.6 | 174.1 | 137.4 | 411.6 | 216.9
3507.1 | 3286.1 | 384.5 | 173.8 | 137.5 | 411 | 216.8
3508.1 | 3287.1 | 384.3 | 174.4 | 137.5 | 410.3 | 216.4
3509.1 | 3288.1 | 384.2 | 174.4 | 137.4 | 409.6 | 216.3
3510.1 | 3289.1 | 384.1 | 174.7 | 137.5 | 409 | 216.1
3511.1 | 3290.1 | 383.9 | 174.6 | 137.6 | 408.3 | 216
3512.1 | 3291.1 | 383.7 | 174.8 | 137.8 | 407.7 | 215.8
3513.1 | 3292.1 | 383.6 | 174.4 | 137.9 | 407.1 | 215.5
3514.1 | 3293.1 | 383.5 | 173.8 | 137.8 | 406.5 | 215.3
3515.1 | 3294.1 | 383.3 | 173.3 | 137.6 | 405.9 | 215.3
3516.1 | 3295.1 | 383.1 | 173.8 | 137.8 | 405.3 | 215.1
3517.1 | 3296.1 | 383 | 173.6 | 138.1 | 404.7 | 215.1
3518.1 | 3297.1 | 382.9 | 173.3 | 138.1 | 404.1 | 215
3519.1 | 3298.1 | 382.7 | 173.2 | 138.1 | 403.5 | 214.9
3520.1 | 3299.1 | 382.5 | 172.9 | 137.9 | 403 | 214.9
3521.1 | 3300.1 | 382.4 | 172.4 | 137.7 | 402.4 | 214.7
3522.1 | 3301.1 | 382.2 | 172.5 | 137.7 | 401.9 | 214.8
3523.1 | 3302.1 | 382.1 | 172.4 | 137.7 | 401.3 | 214.6
3524.1 | 3303.1 | 381.9 | 172.7 | 137.9 | 400.8 | 214.3
3525.1 | 3304.1 | 381.8 | 172.9 | 137.8 | 400.2 | 214
3526.1 | 3305.1 | 381.6 | 173.2 | 137.8 | 399.7 | 213.8
3527.1 | 3306.1 | 381.4 | 173.5 | 137.8 | 399.1 | 213.7
3528.1 | 3307.1 | 381.3 | 173.7 | 137.6 | 398.6 | 213.4
3529.1 | 3308.1 | 381.1 | 173.6 | 137.6 | 398.1 | 213.3
3530.1 | 3309.1 | 380.9 | 173.9 | 137.7 | 397.6 | 213.1
3531.1 | 3310.1 | 380.8 | 173.4 | 137.6 | 397.1 | 213.2
3532.1 | 3311.1 | 380.6 | 173.6 | 137.5 | 396.6 | 213
3533.1 | 3312.1 | 380.4 | 173.7 | 137.3 | 396 | 212.9
3534.1 | 3313.1 | 380.3 | 173.4 | 137 | 395.5 | 212.8
3535.1 | 3314.1 | 380.1 | 172.8 | 136.8 | 395 | 212.7
3536.1 | 3315.1 | 379.9 | 173.1 | 136.7 | 394.5 | 212.5
3537.1 | 3316.1 | 379.8 | 172.9 | 136.3 | 394 | 212.3
3538.1 | 3317.1 | 379.6 | 172.9 | 136 | 393.5 | 212.3
3539.1 | 3318.1 | 379.4 | 172.9 | 135.9 | 393 | 211.9
3540.1 | 3319.1 | 379.2 | 172.8 | 135.8 | 392.5 | 211.7
3541.1 | 3320.1 | 379.1 | 172.8 | 135.7 | 392 | 211.7
3542.1 | 3321.1 | 378.9 | 173.2 | 135.5 | 391.5 | 211.7
3543.1 | 3322.1 | 378.7 | 173 | 135.4 | 391.1 | 211.8
3544.1 | 3323.1 | 378.5 | 172.6 | 135.2 | 390.5 | 211.5
3545.1 | 3324.1 | 378.3 | 172 | 135 | 390 | 211.2
3546.1 | 3325.1 | 378.2 | 172 | 134.9 | 389.6 | 211
3547.1 | 3326.1 | 378 | 171.8 | 134.4 | 389.1 | 210.8
3548.1 | 3327.1 | 377.8 | 171.9 | 134 | 388.6 | 210.6
3549.1 | 3328.1 | 377.6 | 172 | 133.8 | 388.1 | 210.3
3550.1 | 3329.1 | 377.5 | 171.9 | 133.7 | 387.7 | 210.1
3551.1 | 3330.1 | 377.3 | 171.8 | 133.5 | 387.2 | 209.9
3552.1 | 3331.1 | 377.1 | 172.5 | 133.4 | 386.7 | 209.8
3553.1 | 3332.1 | 376.9 | 172.7 | 132.9 | 386.2 | 209.8
3554.1 | 3333.1 | 376.7 | 172.8 | 132.7 | 385.8 | 209.4
3555.1 | 3334.1 | 376.5 | 171.9 | 132.7 | 385.3 | 209.4
3556.1 | 3335.1 | 376.3 | 171.8 | 132.6 | 384.8 | 209.4
3557.1 | 3336.1 | 376.1 | 171.8 | 132.3 | 384.4 | 209.1
3558.1 | 3337.1 | 376 | 171.4 | 132.1 | 383.9 | 208.9
3559.1 | 3338.1 | 375.8 | 170.9 | 132.2 | 383.5 | 208.9
3560.1 | 3339.1 | 375.6 | 170.6 | 132.2 | 383 | 208.8
3561.1 | 3340.1 | 375.4 | 170.4 | 132.2 | 382.6 | 208.9
3562.1 | 3341.1 | 375.2 | 170.2 | 132 | 382.1 | 208.8
3563.1 | 3342.1 | 375 | 169.9 | 131.9 | 381.7 | 208.7
3564.1 | 3343.1 | 374.8 | 169.3 | 131.6 | 381.2 | 208.5
3565.1 | 3344.1 | 374.7 | 168.6 | 131.4 | 380.8 | 208.3
3566.1 | 3345.1 | 374.5 | 168.5 | 131.1 | 380.3 | 208.1
3567.1 | 3346.1 | 374.3 | 168.3 | 130.9 | 379.9 | 207.9
3568.1 | 3347.1 | 374.1 | 167.9 | 130.6 | 379.4 | 207.6
3569.1 | 3348.1 | 373.9 | 167.6 | 130.5 | 379 | 207.6
3570.1 | 3349.1 | 373.7 | 167.7 | 130.3 | 378.5 | 207.6
3571.1 | 3350.1 | 373.5 | 167.7 | 130.2 | 378 | 207.5
3572.1 | 3351.1 | 373.3 | 167.4 | 129.7 | 377.6 | 207.3
3573.1 | 3352.1 | 373.1 | 166.6 | 129.1 | 377.1 | 207
3574.1 | 3353.1 | 373 | 166.3 | 128.8 | 376.7 | 206.7
3575.1 | 3354.1 | 372.8 | 165.9 | 128.9 | 376.2 | 206.5
3576.1 | 3355.1 | 372.6 | 166.4 | 129.1 | 375.8 | 206.4
3577.1 | 3356.1 | 372.3 | 167 | 129.3 | 375.3 | 206.5
3578.1 | 3357.1 | 372.2 | 167.4 | 129.1 | 374.9 | 206.3
3579.1 | 3358.1 | 372 | 167.2 | 129.1 | 374.5 | 206.1
3580.1 | 3359.1 | 371.8 | 166.6 | 129.2 | 374 | 205.7
3581.1 | 3360.1 | 371.6 | 166.6 | 129.2 | 373.6 | 205.5
3582.1 | 3361.1 | 371.4 | 166.5 | 128.9 | 373.1 | 205.3
3583.1 | 3362.1 | 371.3 | 167 | 128.9 | 372.7 | 205.3
3584.1 | 3363.1 | 371.1 | 167 | 128.8 | 372.2 | 205.2
3585.1 | 3364.1 | 370.9 | 167.2 | 128.8 | 371.8 | 205.1
3586.1 | 3365.1 | 370.7 | 167.2 | 128.9 | 371.3 | 204.9
3587.1 | 3366.1 | 370.5 | 167.5 | 129.1 | 370.9 | 204.6
3588.1 | 3367.1 | 370.4 | 167.8 | 129.2 | 370.4 | 204.4
3589.1 | 3368.1 | 370.2 | 168 | 129.3 | 370 | 204.4
3590.1 | 3369.1 | 370 | 168.1 | 129.5 | 369.6 | 204.3
3591.1 | 3370.1 | 369.9 | 167.7 | 129.4 | 369.2 | 204.1
3592.1 | 3371.1 | 369.7 | 167.4 | 129.5 | 368.7 | 203.9
3593.1 | 3372.1 | 369.5 | 166.9 | 129.5 | 368.3 | 203.6
3594.1 | 3373.1 | 369.3 | 165.9 | 129.4 | 367.9 | 203.5
3595.1 | 3374.1 | 369.1 | 165.9 | 129.5 | 367.5 | 203.5
3596.1 | 3375.1 | 369 | 166.2 | 129.3 | 367.1 | 203.5
3597.1 | 3376.1 | 368.8 | 165.9 | 129.1 | 366.7 | 203.1
3598.1 | 3377.1 | 368.6 | 165.9 | 129 | 366.2 | 203
3599.1 | 3378.1 | 368.5 | 166 | 128.8 | 365.8 | 202.8
3600.1 | 3379.1 | 368.3 | 166.1 | 128.8 | 365.4 | 202.9
3601.1 | 3380.1 | 368.1 | 165.9 | 128.6 | 365 | 203
3602.1 | 3381.1 | 367.9 | 165.4 | 128.8 | 364.6 | 202.9
3603.1 | 3382.1 | 367.8 | 164.5 | 128.7 | 364.2 | 202.7
3604.1 | 3383.1 | 367.6 | 163.7 | 128.7 | 363.8 | 202.4
3605.1 | 3384.1 | 367.4 | 163.9 | 128.5 | 363.4 | 202.5
3606.1 | 3385.1 | 367.3 | 164 | 128.4 | 363 | 202.4
3607.1 | 3386.1 | 367.1 | 163.5 | 128.6 | 362.5 | 202.4
3608.1 | 3387.1 | 366.9 | 162.6 | 128.8 | 362.1 | 202.4
3609.1 | 3388.1 | 366.7 | 162.2 | 128.8 | 361.7 | 202.2
3610.1 | 3389.1 | 366.5 | 162 | 128.7 | 361.2 | 202.1
3611.1 | 3390.1 | 366.3 | 162.3 | 128.9 | 360.8 | 202.1
3612.1 | 3391.1 | 366.2 | 162 | 128.8 | 360.4 | 201.9
3613.1 | 3392.1 | 366 | 161.7 | 128.8 | 360 | 201.7
3614.1 | 3393.1 | 365.8 | 161.6 | 128.9 | 359.5 | 201.5
3615.1 | 3394.1 | 365.6 | 161.4 | 129 | 359.1 | 201.6
3616.1 | 3395.1 | 365.4 | 161.7 | 129.2 | 358.7 | 201.6
3617.1 | 3396.1 | 365.3 | 161.7 | 129.3 | 358.3 | 201.7
3618.1 | 3397.1 | 365.1 | 161.6 | 129.3 | 357.8 | 201.6
3619.1 | 3398.1 | 364.9 | 161.6 | 129.3 | 357.4 | 201.4
3620.1 | 3399.1 | 364.7 | 162.3 | 129.3 | 357 | 201.1
3621.1 | 3400.1 | 364.6 | 162 | 129.2 | 356.6 | 200.9
3622.1 | 3401.1 | 364.4 | 161.7 | 129.2 | 356.1 | 200.8
3623.1 | 3402.1 | 364.2 | 161.6 | 129.6 | 355.7 | 200.9
3624.1 | 3403.1 | 364 | 161.5 | 129.8 | 355.3 | 201.1
3625.1 | 3404.1 | 363.8 | 161 | 129.6 | 354.9 | 201.1
3626.1 | 3405.1 | 363.7 | 161.1 | 129.6 | 354.4 | 200.7
3627.1 | 3406.1 | 363.5 | 161.2 | 129.6 | 354 | 200.5
3628.1 | 3407.1 | 363.3 | 160.9 | 129.8 | 353.6 | 200.4
3629.1 | 3408.1 | 363.1 | 161 | 129.9 | 353.2 | 200.3
3630.1 | 3409.1 | 362.9 | 160.8 | 130 | 352.7 | 200.2
3631.1 | 3410.1 | 362.8 | 161 | 129.9 | 352.3 | 200.2
3632.1 | 3411.1 | 362.6 | 161.2 | 129.6 | 351.9 | 200.2
3633.1 | 3412.1 | 362.4 | 161.4 | 129.2 | 351.4 | 200.1
3634.1 | 3413.1 | 362.2 | 161.9 | 128.8 | 351 | 199.9
3635.1 | 3414.1 | 362 | 161.4 | 128.5 | 350.6 | 199.6
3636.1 | 3415.1 | 361.8 | 161.1 | 128.2 | 350.1 | 199.3
3637.1 | 3416.1 | 361.6 | 161.1 | 127.9 | 349.7 | 199.1
3638.1 | 3417.1 | 361.4 | 161.1 | 127.6 | 349.3 | 198.9
3639.1 | 3418.1 | 361.2 | 161 | 127.7 | 348.8 | 198.8
3640.1 | 3419.1 | 361 | 160.4 | 127.6 | 348.4 | 198.7
3641.1 | 3420.1 | 360.8 | 159.9 | 127.2 | 348 | 198.7
3642.1 | 3421.1 | 360.6 | 159.8 | 126.8 | 347.5 | 198.5
3643.1 | 3422.1 | 360.4 | 159.4 | 126.6 | 347.1 | 198.3
3644.1 | 3423.1 | 360.2 | 159.4 | 126.3 | 346.7 | 198.1
3645.1 | 3424.1 | 360 | 159.2 | 126.2 | 346.2 | 198
3646.1 | 3425.1 | 359.8 | 159.2 | 126.2 | 345.8 | 197.8
3647.1 | 3426.1 | 359.6 | 159.1 | 126.2 | 345.4 | 197.7
3648.1 | 3427.1 | 359.4 | 159.3 | 126 | 345 | 197.6
3649.1 | 3428.1 | 359.2 | 158.9 | 125.7 | 344.5 | 197.5
3650.1 | 3429.1 | 359 | 158.1 | 125.6 | 344.1 | 197.3
3651.1 | 3430.1 | 358.8 | 157.4 | 125.8 | 343.7 | 197.2
3652.1 | 3431.1 | 358.6 | 157.6 | 125.8 | 343.2 | 197.1
3653.1 | 3432.1 | 358.4 | 157.7 | 125.8 | 342.8 | 196.8
3654.1 | 3433.1 | 358.2 | 157.8 | 125.6 | 342.4 | 196.8
3655.1 | 3434.1 | 358.1 | 157.5 | 125.5 | 342 | 196.8
3656.1 | 3435.1 | 357.9 | 157.4 | 125.3 | 341.5 | 196.6
3657.1 | 3436.1 | 357.7 | 156.9 | 125.3 | 341.1 | 196.5
3658.1 | 3437.1 | 357.5 | 156.6 | 125.1 | 340.7 | 196.3
3659.1 | 3438.1 | 357.3 | 156.2 | 125.1 | 340.3 | 196.1
3660.1 | 3439.1 | 357.2 | 156.3 | 124.9 | 339.8 | 195.8
3661.1 | 3440.1 | 357 | 157.1 | 124.9 | 339.4 | 195.8
3662.1 | 3441.1 | 356.8 | 157 | 124.8 | 339 | 195.7
3663.1 | 3442.1 | 356.7 | 156.7 | 124.8 | 338.5 | 195.5
3664.1 | 3443.1 | 356.5 | 156.9 | 124.6 | 338.1 | 195.4
3665.1 | 3444.1 | 356.3 | 157.2 | 124.6 | 337.6 | 195.5
3666.1 | 3445.1 | 356.2 | 157.3 | 124.4 | 337.2 | 195.5
3667.1 | 3446.1 | 356 | 157.1 | 124.3 | 336.8 | 195.3
3668.1 | 3447.1 | 355.8 | 157 | 124.1 | 336.3 | 195.1
3669.1 | 3448.1 | 355.7 | 157.4 | 124 | 335.9 | 194.9
3670.1 | 3449.1 | 355.5 | 157.6 | 123.8 | 335.4 | 194.7
3671.1 | 3450.1 | 355.3 | 157.6 | 123.5 | 335 | 194.6
3672.1 | 3451.1 | 355.1 | 157.6 | 123.1 | 334.5 | 194.5
3673.1 | 3452.1 | 355 | 157.3 | 122.7 | 334.1 | 194.3
3674.1 | 3453.1 | 354.8 | 157.3 | 122.4 | 333.6 | 194.2
3675.1 | 3454.1 | 354.6 | 157.9 | 122.2 | 333.2 | 194.1
3676.1 | 3455.1 | 354.4 | 158 | 121.9 | 332.7 | 194.1
3677.1 | 3456.1 | 354.2 | 157.9 | 121.7 | 332.3 | 194
3678.1 | 3457.1 | 353.9 | 158 | 121.6 | 331.9 | 194
3679.1 | 3458.1 | 353.7 | 158 | 121.4 | 331.4 | 193.9
3680.1 | 3459.1 | 353.5 | 157.8 | 121.3 | 331 | 193.8
3681.1 | 3460.1 | 353.3 | 157.4 | 121.3 | 330.5 | 193.6
3682.1 | 3461.1 | 353.1 | 156.6 | 121.4 | 330.1 | 193.3
3683.1 | 3462.1 | 352.9 | 156.7 | 121.1 | 329.6 | 193.2
3684.1 | 3463.1 | 352.7 | 156.8 | 121 | 329.2 | 193.1
3685.1 | 3464.1 | 352.5 | 156.5 | 120.9 | 328.7 | 192.9
3686.1 | 3465.1 | 352.3 | 156.3 | 120.8 | 328.3 | 192.8
3687.1 | 3466.1 | 352.1 | 156.5 | 120.7 | 327.8 | 192.8
3688.1 | 3467.1 | 351.9 | 156.2 | 120.6 | 327.4 | 192.8
3689.1 | 3468.1 | 351.7 | 156.7 | 120.5 | 326.9 | 192.8
3690.1 | 3469.1 | 351.5 | 156.8 | 120.6 | 326.5 | 192.5
3691.1 | 3470.1 | 351.3 | 156.8 | 120.4 | 326.1 | 192.4
3692.1 | 3471.1 | 351.1 | 156.7 | 120.2 | 325.6 | 192.1
3693.1 | 3472.1 | 350.9 | 156.4 | 120 | 325.2 | 192.1
3694.1 | 3473.1 | 350.7 | 156.2 | 119.9 | 324.7 | 192.1
3695.1 | 3474.1 | 350.5 | 156.1 | 119.8 | 324.3 | 191.9
3696.1 | 3475.1 | 350.3 | 155.8 | 119.8 | 323.8 | 191.7
3697.1 | 3476.1 | 350.1 | 155.3 | 119.6 | 323.4 | 191.4
3698.1 | 3477.1 | 349.9 | 154.9 | 119.3 | 322.9 | 191.2
3699.1 | 3478.1 | 349.7 | 155.2 | 118.9 | 322.5 | 191
3700.1 | 3479.1 | 349.5 | 155.3 | 119.1 | 322 | 190.9
3701.1 | 3480.1 | 349.3 | 155.9 | 119.1 | 321.6 | 191
3702.1 | 3481.1 | 349.1 | 156 | 118.6 | 321.1 | 190.8
3703.1 | 3482.1 | 348.9 | 155.9 | 118.1 | 320.6 | 190.5
3704.1 | 3483.1 | 348.8 | 155.3 | 117.8 | 320.2 | 190.3
3705.1 | 3484.1 | 348.6 | 154.7 | 117.5 | 319.7 | 190.3
3706.1 | 3485.1 | 348.4 | 154.1 | 117.4 | 319.3 | 190.2
3707.1 | 3486.1 | 348.2 | 154.5 | 117.2 | 318.8 | 190.2
3708.1 | 3487.1 | 348 | 154.1 | 117.1 | 318.4 | 189.8
3709.1 | 3488.1 | 347.8 | 154.2 | 116.9 | 317.9 | 189.8
3710.1 | 3489.1 | 347.7 | 153.9 | 116.6 | 317.4 | 189.8
3711.1 | 3490.1 | 347.5 | 153.2 | 116.5 | 317 | 189.5
3712.1 | 3491.1 | 347.3 | 152.3 | 116.6 | 316.5 | 189.4
3713.1 | 3492.1 | 347.1 | 152.1 | 116.5 | 316 | 189.3
3714.1 | 3493.1 | 346.9 | 152.4 | 116.4 | 315.6 | 189.2
3715.1 | 3494.1 | 346.8 | 152.3 | 116.4 | 315.1 | 188.9
3716.1 | 3495.1 | 346.6 | 152.2 | 116 | 314.6 | 188.7
3717.1 | 3496.1 | 346.4 | 152.3 | 115.9 | 314.1 | 188.5
3718.1 | 3497.1 | 346.2 | 152.8 | 115.8 | 313.6 | 188.3
3719.1 | 3498.1 | 346 | 152.9 | 115.7 | 313.1 | 188.1
3720.1 | 3499.1 | 345.8 | 153 | 115.8 | 312.6 | 188
3721.1 | 3500.1 | 345.6 | 153.5 | 116 | 312.1 | 188
3722.1 | 3501.1 | 345.4 | 153.4 | 116.1 | 311.6 | 187.9
3723.1 | 3502.1 | 345.2 | 153.7 | 115.9 | 311.2 | 187.6
3724.1 | 3503.1 | 345 | 153.6 | 115.8 | 310.7 | 187.6
3725.1 | 3504.1 | 344.8 | 153.5 | 115.8 | 310.2 | 187.6
3726.1 | 3505.1 | 344.6 | 153.6 | 115.7 | 309.6 | 187.3
3727.1 | 3506.1 | 344.4 | 154 | 115.9 | 309.1 | 187.3
3728.1 | 3507.1 | 344.2 | 153.6 | 115.9 | 308.6 | 187.3
3729.1 | 3508.1 | 344 | 153 | 115.8 | 308.1 | 187.3
3730.1 | 3509.1 | 343.8 | 152.1 | 116 | 307.6 | 187.3
3731.1 | 3510.1 | 343.6 | 151.9 | 116 | 307.1 | 187.2
3732.1 | 3511.1 | 343.4 | 151.9 | 116 | 306.6 | 187
3733.1 | 3512.1 | 343.2 | 151.5 | 116.1 | 306.1 | 186.9
3734.1 | 3513.1 | 343 | 151.2 | 116.2 | 305.5 | 186.7
3735.1 | 3514.1 | 342.9 | 150.8 | 116.2 | 305 | 186.8
3736.1 | 3515.1 | 342.7 | 150.7 | 116.2 | 304.5 | 186.8
3737.1 | 3516.1 | 342.5 | 150.8 | 116.3 | 303.9 | 186.8
3738.1 | 3517.1 | 342.3 | 150.4 | 116.1 | 303.4 | 186.6
3739.1 | 3518.1 | 342.2 | 150.2 | 116.1 | 302.8 | 186.6
3740.1 | 3519.1 | 342 | 149.7 | 116.1 | 302.3 | 186.4
3741.1 | 3520.1 | 341.8 | 149.4 | 116 | 301.8 | 186.2
3742.1 | 3521.1 | 341.6 | 149.1 | 116 | 301.2 | 186.2
3743.1 | 3522.1 | 341.5 | 148.4 | 116 | 300.6 | 186.1
3744.1 | 3523.1 | 341.3 | 148.1 | 116.1 | 300.1 | 186
3745.1 | 3524.1 | 341.1 | 147.8 | 116.2 | 299.5 | 186
3746.1 | 3525.1 | 341 | 147.8 | 116.2 | 298.9 | 185.8
3747.1 | 3526.1 | 340.8 | 147.9 | 116.1 | 298.3 | 185.6
3748.1 | 3527.1 | 340.6 | 147.9 | 116.1 | 297.8 | 185.4
3749.1 | 3528.1 | 340.5 | 148.2 | 116.3 | 297.2 | 185.4
3750.1 | 3529.1 | 340.3 | 147.8 | 116.3 | 296.6 | 185.4
3751.1 | 3530.1 | 340.1 | 147.6 | 116.2 | 296 | 185.3
3752.1 | 3531.1 | 340 | 147.1 | 116.4 | 295.4 | 185.3
3753.1 | 3532.1 | 339.8 | 146.7 | 116.4 | 294.8 | 185.3
3754.1 | 3533.1 | 339.6 | 146.1 | 116.6 | 294.2 | 185.1
3755.1 | 3534.1 | 339.5 | 145.9 | 116.7 | 293.7 | 185
3756.1 | 3535.1 | 339.3 | 145.3 | 116.6 | 293.1 | 184.9
3757.1 | 3536.1 | 339.1 | 144.9 | 116.5 | 292.5 | 185
3758.1 | 3537.1 | 338.9 | 145 | 116.2 | 291.9 | 184.9
3759.1 | 3538.1 | 338.8 | 145 | 116.2 | 291.3 | 184.8
3760.1 | 3539.1 | 338.6 | 144.8 | 116.1 | 290.7 | 184.6
3761.1 | 3540.1 | 338.4 | 144.9 | 115.8 | 290.1 | 184.4
3762.1 | 3541.1 | 338.3 | 145 | 115.7 | 289.6 | 184.3
3763.1 | 3542.1 | 338.1 | 145.7 | 115.7 | 289 | 184.3
3764.1 | 3543.1 | 337.9 | 146.1 | 115.8 | 288.4 | 184.2
3765.1 | 3544.1 | 337.7 | 146.3 | 115.9 | 287.8 | 184.1
3766.1 | 3545.1 | 337.5 | 146.6 | 115.9 | 287.3 | 184.1
3767.1 | 3546.1 | 337.3 | 146.9 | 115.8 | 286.7 | 183.9
3768.1 | 3547.1 | 337.1 | 146.8 | 115.7 | 286.2 | 183.6
3769.1 | 3548.1 | 336.9 | 146.5 | 115.5 | 285.6 | 183.5
3770.1 | 3549.1 | 336.8 | 145.9 | 115.3 | 285.1 | 183.3
3771.1 | 3550.1 | 336.6 | 145.8 | 115.1 | 284.5 | 183.3
3772.1 | 3551.1 | 336.4 | 146.3 | 114.9 | 284 | 183.2
3773.1 | 3552.1 | 336.2 | 146.7 | 114.9 | 283.4 | 183.1
3774.1 | 3553.1 | 336 | 146.7 | 115.1 | 282.9 | 182.9
3775.1 | 3554.1 | 335.8 | 146.7 | 115 | 282.3 | 182.9
3776.1 | 3555.1 | 335.6 | 146.4 | 114.9 | 281.8 | 182.8
3777.1 | 3556.1 | 335.4 | 146.2 | 114.7 | 281.3 | 182.6
3778.1 | 3557.1 | 335.2 | 146.4 | 114.7 | 280.8 | 182.4
3779.1 | 3558.1 | 335 | 146.7 | 114.4 | 280.3 | 182.4
3780.1 | 3559.1 | 334.8 | 146.4 | 114.4 | 279.8 | 182.3
3781.1 | 3560.1 | 334.6 | 145.9 | 114.3 | 279.3 | 182.1
3782.1 | 3561.1 | 334.4 | 145.8 | 114 | 278.8 | 182.2
3783.1 | 3562.1 | 334.1 | 145.8 | 113.8 | 278.3 | 182.1
3784.1 | 3563.1 | 333.9 | 145.7 | 113.4 | 277.8 | 181.8
3785.1 | 3564.1 | 333.7 | 146.4 | 113.2 | 277.3 | 181.5
3786.1 | 3565.1 | 333.5 | 146.8 | 113.1 | 276.8 | 181.3
3787.1 | 3566.1 | 333.3 | 147.1 | 112.9 | 276.4 | 181.1
3788.1 | 3567.1 | 333.1 | 146.9 | 112.8 | 275.9 | 180.8
3789.1 | 3568.1 | 332.8 | 146.9 | 112.6 | 275.4 | 180.8
3790.1 | 3569.1 | 332.6 | 147.1 | 112.3 | 275 | 180.6
3791.1 | 3570.1 | 332.4 | 147.2 | 112.1 | 274.5 | 180.6
3792.1 | 3571.1 | 332.2 | 147.8 | 111.9 | 274.1 | 180.4
3793.1 | 3572.1 | 331.9 | 147.6 | 111.6 | 273.7 | 180.3
3794.1 | 3573.1 | 331.7 | 146.9 | 111.5 | 273.2 | 180.3
3795.1 | 3574.1 | 331.5 | 146.6 | 111.3 | 272.8 | 180.2
3796.1 | 3575.1 | 331.2 | 146 | 111.1 | 272.4 | 179.9
3797.1 | 3576.1 | 331 | 146.2 | 111 | 272 | 179.8
3798.1 | 3577.1 | 330.8 | 145.9 | 110.8 | 271.5 | 179.7
3799.1 | 3578.1 | 330.6 | 145.8 | 110.6 | 271.1 | 179.5
3800.1 | 3579.1 | 330.3 | 145.3 | 110.6 | 270.7 | 179.4
3801.1 | 3580.1 | 330.1 | 145.3 | 110.5 | 270.3 | 179.2
3802.1 | 3581.1 | 329.9 | 144.8 | 110.3 | 269.9 | 179
3803.1 | 3582.1 | 329.7 | 144.3 | 110.3 | 269.5 | 179
3804.1 | 3583.1 | 329.5 | 144.1 | 110.3 | 269.1 | 178.9
3805.1 | 3584.1 | 329.3 | 143.6 | 110.1 | 268.7 | 178.6
3806.1 | 3585.1 | 329.1 | 143.6 | 110 | 268.4 | 178.4
3807.1 | 3586.1 | 328.8 | 143.7 | 110 | 268 | 178.4
3808.1 | 3587.1 | 328.6 | 143.6 | 109.8 | 267.6 | 178.4
3809.1 | 3588.1 | 328.4 | 143.3 | 109.7 | 267.2 | 178.2
3810.1 | 3589.1 | 328.2 | 143.2 | 109.4 | 266.8 | 178.1
3811.1 | 3590.1 | 328 | 143.1 | 109 | 266.5 | 178
3812.1 | 3591.1 | 327.8 | 143.2 | 108.7 | 266.1 | 178
3813.1 | 3592.1 | 327.6 | 143.6 | 108.7 | 265.7 | 178
3814.1 | 3593.1 | 327.4 | 143.7 | 108.5 | 265.4 | 178.1
3815.1 | 3594.1 | 327.2 | 143.5 | 108.4 | 265 | 178
3816.1 | 3595.1 | 327 | 143.5 | 108.5 | 264.6 | 177.8
3817.1 | 3596.1 | 326.8 | 143.1 | 108.5 | 264.3 | 177.7
3818.1 | 3597.1 | 326.6 | 143.5 | 108.5 | 263.9 | 177.8
3819.1 | 3598.1 | 326.4 | 143.7 | 108.7 | 263.6 | 177.8
3820.1 | 3599.1 | 326.2 | 143.2 | 108.7 | 263.2 | 177.8
3821.1 | 3600.1 | 326 | 143.1 | 108.8 | 262.9 | 177.6
3822.1 | 3601.1 | 325.7 | 142.8 | 108.7 | 262.5 | 177.5
3823.1 | 3602.1 | 325.5 | 142.7 | 108.6 | 262.2 | 177.4
3824.1 | 3603.1 | 325.3 | 142.1 | 108.5 | 261.9 | 177.1
3825.1 | 3604.1 | 325.1 | 142.5 | 108.5 | 261.5 | 176.9
3826.1 | 3605.1 | 324.9 | 142.8 | 108.2 | 261.2 | 176.8
3827.1 | 3606.1 | 324.7 | 142.6 | 107.9 | 260.9 | 176.9
3828.1 | 3607.1 | 324.5 | 142.2 | 107.8 | 260.6 | 176.7
3829.1 | 3608.1 | 324.3 | 142.1 | 107.6 | 260.2 | 176.6
3830.1 | 3609.1 | 324.1 | 142 | 107.4 | 259.9 | 176.6
3831.1 | 3610.1 | 323.8 | 142.2 | 107.1 | 259.6 | 176.6
3832.1 | 3611.1 | 323.6 | 142.7 | 106.8 | 259.3 | 176.6
3833.1 | 3612.1 | 323.4 | 142 | 106.5 | 259 | 176.5
3834.1 | 3613.1 | 323.2 | 141.3 | 106.3 | 258.7 | 176.4
3835.1 | 3614.1 | 323 | 141.4 | 106.1 | 258.4 | 176.2
3836.1 | 3615.1 | 322.7 | 141.3 | 106 | 258 | 176.2
3837.1 | 3616.1 | 322.5 | 141.1 | 105.9 | 257.7 | 176.2
3838.1 | 3617.1 | 322.3 | 140.4 | 105.8 | 257.4 | 175.9
3839.1 | 3618.1 | 322.1 | 139.5 | 105.8 | 257.1 | 175.8
3840.1 | 3619.1 | 321.8 | 138.9 | 105.6 | 256.8 | 175.9
3841.1 | 3620.1 | 321.6 | 138.6 | 105.6 | 256.5 | 175.8
3842.1 | 3621.1 | 321.4 | 137.9 | 105.6 | 256.2 | 175.8
3843.1 | 3622.1 | 321.1 | 137.2 | 105.5 | 255.9 | 175.6
3844.1 | 3623.1 | 320.9 | 136.8 | 105.6 | 255.6 | 175.5
3845.1 | 3624.1 | 320.7 | 135.9 | 105.8 | 255.3 | 175.4
3846.1 | 3625.1 | 320.5 | 135.1 | 105.8 | 255.1 | 175.3
3847.1 | 3626.1 | 320.2 | 134.6 | 105.9 | 254.8 | 175.3
3848.1 | 3627.1 | 320 | 135.1 | 105.9 | 254.5 | 175.3
3849.1 | 3628.1 | 319.8 | 135.2 | 105.9 | 254.2 | 175.2
3850.1 | 3629.1 | 319.6 | 135.4 | 106 | 253.9 | 175.1
3851.1 | 3630.1 | 319.4 | 135.2 | 106.1 | 253.6 | 175
3852.1 | 3631.1 | 319.2 | 134.9 | 106.1 | 253.3 | 174.8
3853.1 | 3632.1 | 318.9 | 134.4 | 106.1 | 253.1 | 174.8
3854.1 | 3633.1 | 318.7 | 134.1 | 106.1 | 252.8 | 174.8
3855.1 | 3634.1 | 318.5 | 134.1 | 106.1 | 252.5 | 174.7
3856.1 | 3635.1 | 318.3 | 134.2 | 106.1 | 252.2 | 174.7
3857.1 | 3636.1 | 318.1 | 134.4 | 106.1 | 252 | 174.5
3858.1 | 3637.1 | 317.9 | 134.3 | 106.1 | 251.7 | 174.6
3859.1 | 3638.1 | 317.7 | 134.3 | 105.9 | 251.4 | 174.5
3860.1 | 3639.1 | 317.5 | 134.4 | 105.7 | 251.2 | 174.5
3861.1 | 3640.1 | 317.3 | 134.4 | 105.5 | 250.9 | 174.5
3862.1 | 3641.1 | 317.1 | 134.1 | 105.4 | 250.6 | 174.4
3863.1 | 3642.1 | 316.9 | 134.1 | 105.3 | 250.4 | 174.3
3864.1 | 3643.1 | 316.7 | 134.5 | 105.3 | 250.1 | 174.3
3865.1 | 3644.1 | 316.5 | 134 | 105.2 | 249.8 | 174.1
3866.1 | 3645.1 | 316.3 | 133.9 | 105.1 | 249.6 | 174.1
3867.1 | 3646.1 | 316.1 | 133.8 | 105 | 249.3 | 174.1
3868.1 | 3647.1 | 315.9 | 133.4 | 104.9 | 249.1 | 173.9
3869.1 | 3648.1 | 315.7 | 132.7 | 104.6 | 248.8 | 173.8
3870.1 | 3649.1 | 315.5 | 132.4 | 104.5 | 248.5 | 173.7
3871.1 | 3650.1 | 315.3 | 131.8 | 104.5 | 248.3 | 173.5
3872.1 | 3651.1 | 315.1 | 131.9 | 104.3 | 248 | 173.3
3873.1 | 3652.1 | 314.9 | 131.8 | 104.2 | 247.7 | 173.2
3874.1 | 3653.1 | 314.7 | 131.6 | 104 | 247.5 | 173.1
3875.1 | 3654.1 | 314.5 | 131.2 | 103.8 | 247.2 | 172.9
3876.1 | 3655.1 | 314.3 | 131.4 | 103.5 | 247 | 173
3877.1 | 3656.1 | 314 | 131.6 | 103.2 | 246.7 | 172.9
3878.1 | 3657.1 | 313.8 | 131.6 | 103 | 246.5 | 172.8
3879.1 | 3658.1 | 313.6 | 131.9 | 102.7 | 246.2 | 172.7
3880.1 | 3659.1 | 313.4 | 132.6 | 102.6 | 246 | 172.5
3881.1 | 3660.1 | 313.2 | 132.7 | 102.5 | 245.7 | 172.2
3882.1 | 3661.1 | 312.9 | 132.7 | 102.5 | 245.5 | 172
3883.1 | 3662.1 | 312.7 | 132.3 | 102.5 | 245.2 | 172.1
3884.1 | 3663.1 | 312.5 | 132.4 | 102.3 | 245 | 172
3885.1 | 3664.1 | 312.3 | 132.7 | 102.2 | 244.7 | 172
3886.1 | 3665.1 | 312.1 | 132.8 | 101.9 | 244.5 | 171.8
3887.1 | 3666.1 | 311.9 | 133.5 | 101.9 | 244.3 | 171.9
3888.1 | 3667.1 | 311.6 | 133.5 | 101.8 | 244 | 171.8
3889.1 | 3668.1 | 311.4 | 133.2 | 101.8 | 243.8 | 171.8
3890.1 | 3669.1 | 311.2 | 133 | 101.8 | 243.5 | 171.5
3891.1 | 3670.1 | 311 | 132.9 | 101.8 | 243.3 | 171.6
3892.1 | 3671.1 | 310.8 | 132.6 | 101.7 | 243 | 171.4
3893.1 | 3672.1 | 310.6 | 133 | 101.8 | 242.8 | 171.2
3894.1 | 3673.1 | 310.4 | 133.2 | 101.7 | 242.5 | 171.2
3895.1 | 3674.1 | 310.2 | 133 | 101.5 | 242.3 | 171
3896.1 | 3675.1 | 310 | 133.1 | 101.4 | 242 | 170.9
3897.1 | 3676.1 | 309.9 | 132.7 | 101.4 | 241.8 | 170.7
3898.1 | 3677.1 | 309.7 | 132.9 | 101.3 | 241.6 | 170.6
3899.1 | 3678.1 | 309.4 | 133.1 | 101.1 | 241.3 | 170.7
3900.1 | 3679.1 | 309.2 | 133.3 | 100.8 | 241.1 | 170.5
3901.1 | 3680.1 | 309 | 133.1 | 100.6 | 240.9 | 170.3
3902.1 | 3681.1 | 308.8 | 133.6 | 100.4 | 240.6 | 170.2
3903.1 | 3682.1 | 308.6 | 134 | 100.2 | 240.4 | 170.2
3904.1 | 3683.1 | 308.4 | 134.1 | 100.2 | 240.1 | 170.2
3905.1 | 3684.1 | 308.2 | 133.9 | 100.2 | 239.9 | 170.1
3906.1 | 3685.1 | 308 | 133.6 | 100.1 | 239.7 | 170.1
3907.1 | 3686.1 | 307.8 | 133.5 | 100.1 | 239.5 | 170
3908.1 | 3687.1 | 307.6 | 133.7 | 100 | 239.2 | 169.9
3909.1 | 3688.1 | 307.4 | 133.9 | 100 | 239 | 169.6
3910.1 | 3689.1 | 307.2 | 134.4 | 100 | 238.8 | 169.4
3911.1 | 3690.1 | 307 | 134.6 | 99.7 | 238.5 | 169.4
3912.1 | 3691.1 | 306.8 | 134.7 | 99.5 | 238.3 | 169.1
3913.1 | 3692.1 | 306.5 | 134.5 | 99.3 | 238.1 | 169.1
3914.1 | 3693.1 | 306.3 | 134.6 | 99 | 237.8 | 169.1
3915.1 | 3694.1 | 306.1 | 134.7 | 98.6 | 237.6 | 168.9
3916.1 | 3695.1 | 305.9 | 134.5 | 98.3 | 237.4 | 168.8
3917.1 | 3696.1 | 305.6 | 134.5 | 98.2 | 237.2 | 168.6
3918.1 | 3697.1 | 305.4 | 134.5 | 98.2 | 236.9 | 168.6
3919.1 | 3698.1 | 305.2 | 134.1 | 97.9 | 236.7 | 168.5
3920.1 | 3699.1 | 304.9 | 133.5 | 97.7 | 236.5 | 168.3
3921.1 | 3700.1 | 304.7 | 132.8 | 97.7 | 236.2 | 168.3
3922.1 | 3701.1 | 304.5 | 132.2 | 97.2 | 236 | 168.2
3923.1 | 3702.1 | 304.2 | 131.8 | 96.9 | 235.8 | 168
3924.1 | 3703.1 | 304 | 131.1 | 96.6 | 235.6 | 167.8
3925.1 | 3704.1 | 303.8 | 131.2 | 96.4 | 235.3 | 167.7
3926.1 | 3705.1 | 303.6 | 131 | 96.2 | 235.1 | 167.7
3927.1 | 3706.1 | 303.3 | 130.9 | 96 | 234.9 | 167.7
3928.1 | 3707.1 | 303.1 | 130.7 | 95.8 | 234.7 | 167.6
3929.1 | 3708.1 | 302.9 | 130.2 | 95.9 | 234.4 | 167.3
3930.1 | 3709.1 | 302.7 | 129.7 | 95.8 | 234.2 | 167.2
3931.1 | 3710.1 | 302.5 | 129.7 | 95.6 | 234 | 167.1
3932.1 | 3711.1 | 302.2 | 129.7 | 95.4 | 233.8 | 166.9
3933.1 | 3712.1 | 302 | 129.6 | 95.3 | 233.6 | 166.9
3934.1 | 3713.1 | 301.8 | 129.4 | 95.1 | 233.3 | 166.7
3935.1 | 3714.1 | 301.6 | 129.3 | 94.8 | 233.1 | 166.5
3936.1 | 3715.1 | 301.3 | 128.9 | 94.6 | 232.9 | 166.4
3937.1 | 3716.1 | 301.1 | 128.4 | 94.3 | 232.7 | 166.2
3938.1 | 3717.1 | 300.9 | 128.1 | 94.1 | 232.5 | 166.2
3939.1 | 3718.1 | 300.6 | 128 | 94 | 232.3 | 166.1
3940.1 | 3719.1 | 300.4 | 127.7 | 94 | 232 | 166.1
3941.1 | 3720.1 | 300.2 | 127.4 | 93.8 | 231.8 | 166
3942.1 | 3721.1 | 299.9 | 127 | 93.8 | 231.6 | 165.8
3943.1 | 3722.1 | 299.7 | 126.2 | 93.7 | 231.3 | 165.6
3944.1 | 3723.1 | 299.5 | 125.9 | 93.6 | 231.1 | 165.5
3945.1 | 3724.1 | 299.2 | 125.1 | 93.5 | 230.9 | 165.5
3946.1 | 3725.1 | 299 | 124.7 | 93.2 | 230.7 | 165.2
3947.1 | 3726.1 | 298.7 | 124.6 | 93.1 | 230.5 | 165.2
3948.1 | 3727.1 | 298.5 | 124.7 | 93.1 | 230.3 | 165.1
3949.1 | 3728.1 | 298.3 | 124.4 | 93 | 230 | 165
3950.1 | 3729.1 | 298 | 124.5 | 93 | 229.8 | 165.1
3951.1 | 3730.1 | 297.8 | 124.5 | 92.8 | 229.6 | 164.8
3952.1 | 3731.1 | 297.6 | 124.6 | 92.8 | 229.4 | 164.8
3953.1 | 3732.1 | 297.4 | 124.8 | 92.8 | 229.2 | 164.6
3954.1 | 3733.1 | 297.2 | 124.8 | 92.5 | 229 | 164.4
3955.1 | 3734.1 | 296.9 | 124.6 | 92.3 | 228.7 | 164.4
3956.1 | 3735.1 | 296.7 | 124.9 | 92.3 | 228.5 | 164.3
3957.1 | 3736.1 | 296.5 | 125.2 | 92.2 | 228.3 | 164.3
3958.1 | 3737.1 | 296.2 | 125.3 | 92.1 | 228.1 | 164.3
3959.1 | 3738.1 | 296 | 125.5 | 91.7 | 227.9 | 164.3
3960.1 | 3739.1 | 295.7 | 124.7 | 91.5 | 227.7 | 164.4
3961.1 | 3740.1 | 295.5 | 123.9 | 91.3 | 227.5 | 164.4
3962.1 | 3741.1 | 295.2 | 123.4 | 91.2 | 227.3 | 164.3
3963.1 | 3742.1 | 295 | 122.6 | 91.2 | 227.1 | 164.3
3964.1 | 3743.1 | 294.8 | 122.3 | 91 | 226.9 | 164.3
3965.1 | 3744.1 | 294.5 | 121.7 | 91 | 226.7 | 164.2
3966.1 | 3745.1 | 294.3 | 120.9 | 90.9 | 226.4 | 164.1
3967.1 | 3746.1 | 294 | 120.1 | 91 | 226.2 | 163.9
3968.1 | 3747.1 | 293.7 | 119.3 | 90.9 | 226 | 163.9
3969.1 | 3748.1 | 293.5 | 118.7 | 91 | 225.8 | 163.9
3970.1 | 3749.1 | 293.2 | 118.2 | 91 | 225.6 | 164
3971.1 | 3750.1 | 292.9 | 118.3 | 90.7 | 225.4 | 164
3972.1 | 3751.1 | 292.7 | 118.2 | 90.6 | 225.2 | 163.8
3973.1 | 3752.1 | 292.4 | 117.8 | 90.5 | 225 | 163.8
3974.1 | 3753.1 | 292.1 | 117.7 | 90.4 | 224.8 | 163.7
3975.1 | 3754.1 | 291.8 | 117.2 | 90.4 | 224.6 | 163.7
3976.1 | 3755.1 | 291.6 | 116.6 | 90.1 | 224.4 | 163.8
3977.1 | 3756.1 | 291.3 | 116 | 89.8 | 224.2 | 163.7
3978.1 | 3757.1 | 291 | 116 | 89.8 | 224 | 163.6
3979.1 | 3758.1 | 290.8 | 115.9 | 89.8 | 223.8 | 163.5
3980.1 | 3759.1 | 290.5 | 115.5 | 89.9 | 223.6 | 163.3
3981.1 | 3760.1 | 290.2 | 115.1 | 89.9 | 223.4 | 163.3
3982.1 | 3761.1 | 290 | 114.8 | 89.9 | 223.1 | 163.2
3983.1 | 3762.1 | 289.7 | 114.7 | 89.8 | 222.9 | 163.2
3984.1 | 3763.1 | 289.4 | 114.6 | 89.6 | 222.7 | 163.1
3985.1 | 3764.1 | 289.2 | 114.4 | 89.6 | 222.5 | 163.1
3986.1 | 3765.1 | 288.9 | 114.2 | 89.5 | 222.4 | 163.1
3987.1 | 3766.1 | 288.7 | 114.1 | 89.5 | 222.2 | 163.1
3988.1 | 3767.1 | 288.4 | 113.5 | 89.7 | 222 | 163
3989.1 | 3768.1 | 288.1 | 113.2 | 89.4 | 221.8 | 163
3990.1 | 3769.1 | 287.8 | 112.7 | 89.3 | 221.6 | 162.9
3991.1 | 3770.1 | 287.6 | 112.5 | 89.1 | 221.4 | 162.8
3992.1 | 3771.1 | 287.3 | 112.8 | 89.1 | 221.2 | 162.7
3993.1 | 3772.1 | 287.1 | 112.7 | 89 | 220.9 | 162.5
3994.1 | 3773.1 | 286.8 | 112.4 | 89.1 | 220.8 | 162.4
3995.1 | 3774.1 | 286.6 | 112 | 89.2 | 220.5 | 162.4
3996.1 | 3775.1 | 286.4 | 112.7 | 89.1 | 220.4 | 162.3
3997.1 | 3776.1 | 286.1 | 112.6 | 89.1 | 220.2 | 162.2
3998.1 | 3777.1 | 285.9 | 112.9 | 89 | 220 | 162.2
3999.1 | 3778.1 | 285.7 | 114 | 88.7 | 219.8 | 162.1
4000.1 | 3779.1 | 285.4 | 114 | 88.5 | 219.6 | 161.9
4001.1 | 3780.1 | 285.2 | 114.1 | 88.5 | 219.4 | 161.9
4002.1 | 3781.1 | 285 | 114.1 | 88.5 | 219.2 | 161.9
4003.1 | 3782.1 | 284.8 | 114.5 | 88.6 | 219 | 161.8
4004.1 | 3783.1 | 284.5 | 114.7 | 88.6 | 218.8 | 161.7
4005.1 | 3784.1 | 284.3 | 114.8 | 88.6 | 218.6 | 161.7
4006.1 | 3785.1 | 284.1 | 114.5 | 88.7 | 218.4 | 161.7
4007.1 | 3786.1 | 283.9 | 114.9 | 88.8 | 218.2 | 161.4
4008.1 | 3787.1 | 283.7 | 116.1 | 88.9 | 218 | 161.4
4009.1 | 3788.1 | 283.5 | 116.8 | 88.5 | 217.8 | 161.2
4010.1 | 3789.1 | 283.3 | 117.1 | 88.3 | 217.6 | 161.2
4011.1 | 3790.1 | 283 | 117.4 | 88.1 | 217.4 | 161
4012.1 | 3791.1 | 282.8 | 116.9 | 87.9 | 217.2 | 161
4013.1 | 3792.1 | 282.6 | 116.3 | 87.8 | 217 | 161
4014.1 | 3793.1 | 282.3 | 115.6 | 87.7 | 216.8 | 160.9
4015.1 | 3794.1 | 282.1 | 115 | 87.7 | 216.6 | 160.8
4016.1 | 3795.1 | 281.9 | 115.3 | 87.5 | 216.4 | 160.7
4017.1 | 3796.1 | 281.6 | 116.3 | 87.4 | 216.2 | 160.7
4018.1 | 3797.1 | 281.4 | 116.9 | 87.2 | 216 | 160.6
4019.1 | 3798.1 | 281.2 | 117.5 | 86.9 | 215.8 | 160.5
4020.1 | 3799.1 | 280.9 | 117.7 | 86.8 | 215.6 | 160.4
4021.1 | 3800.1 | 280.7 | 117.8 | 86.4 | 215.5 | 160.4
4022.1 | 3801.1 | 280.5 | 117.6 | 86.3 | 215.3 | 160.2
4023.1 | 3802.1 | 280.2 | 117.2 | 86.4 | 215.1 | 160.2
4024.1 | 3803.1 | 280 | 116.5 | 86.3 | 214.9 | 160.3
4025.1 | 3804.1 | 279.7 | 115.7 | 86.4 | 214.7 | 160.3
4026.1 | 3805.1 | 279.5 | 115.6 | 86.6 | 214.5 | 160.3
4027.1 | 3806.1 | 279.2 | 116 | 86.9 | 214.3 | 160.2
4028.1 | 3807.1 | 279 | 116.1 | 87.2 | 214.1 | 160.2
4029.1 | 3808.1 | 278.8 | 115.9 | 87.5 | 213.9 | 160.1
4030.1 | 3809.1 | 278.5 | 115.6 | 87.6 | 213.7 | 160
4031.1 | 3810.1 | 278.3 | 115.1 | 87.7 | 213.5 | 159.9
4032.1 | 3811.1 | 278.1 | 114.9 | 87.8 | 213.3 | 159.9
4033.1 | 3812.1 | 277.9 | 115.5 | 87.8 | 213.1 | 159.9
4034.1 | 3813.1 | 277.7 | 116.5 | 87.7 | 212.9 | 159.8
4035.1 | 3814.1 | 277.5 | 116.9 | 87.6 | 212.7 | 159.6
4036.1 | 3815.1 | 277.3 | 117 | 87.5 | 212.5 | 159.7
4037.1 | 3816.1 | 277.1 | 117.1 | 87.2 | 212.3 | 159.6
4038.1 | 3817.1 | 276.8 | 116.6 | 87.2 | 212.1 | 159.5
4039.1 | 3818.1 | 276.6 | 116.5 | 87 | 212 | 159.4
4040.1 | 3819.1 | 276.4 | 116.3 | 87 | 211.8 | 159.3
4041.1 | 3820.1 | 276.2 | 116.2 | 87.2 | 211.6 | 159.3
4042.1 | 3821.1 | 276 | 116.8 | 87 | 211.4 | 159.2
4043.1 | 3822.1 | 275.8 | 117.3 | 86.8 | 211.2 | 159.1
4044.1 | 3823.1 | 275.6 | 117.8 | 86.6 | 211 | 159.1
4045.1 | 3824.1 | 275.4 | 118.3 | 86.6 | 210.8 | 159.1
4046.1 | 3825.1 | 275.2 | 118.6 | 86.7 | 210.6 | 159.1
4047.1 | 3826.1 | 275 | 118.6 | 86.8 | 210.4 | 159.2
4048.1 | 3827.1 | 274.8 | 118.8 | 86.8 | 210.2 | 159
4049.1 | 3828.1 | 274.6 | 119 | 86.7 | 210 | 158.8
4050.1 | 3829.1 | 274.4 | 119.4 | 86.5 | 209.8 | 158.8
4051.1 | 3830.1 | 274.2 | 120.1 | 86.4 | 209.6 | 158.7
4052.1 | 3831.1 | 274 | 120.6 | 86.3 | 209.5 | 158.6
4053.1 | 3832.1 | 273.8 | 121.1 | 86.1 | 209.3 | 158.5
4054.1 | 3833.1 | 273.6 | 121.2 | 86 | 209.1 | 158.4
4055.1 | 3834.1 | 273.4 | 121.3 | 85.8 | 208.9 | 158.3
4056.1 | 3835.1 | 273.2 | 120.8 | 85.7 | 208.7 | 158.4
4057.1 | 3836.1 | 272.9 | 120.6 | 85.4 | 208.5 | 158.4
4058.1 | 3837.1 | 272.7 | 120.4 | 85.4 | 208.3 | 158.2
4059.1 | 3838.1 | 272.5 | 119.8 | 85.4 | 208.1 | 158.1
4060.1 | 3839.1 | 272.3 | 119.5 | 85.5 | 207.9 | 158.2
4061.1 | 3840.1 | 272 | 119.5 | 85.4 | 207.7 | 158.3
4062.1 | 3841.1 | 271.8 | 119 | 85.4 | 207.5 | 158.3
4063.1 | 3842.1 | 271.6 | 118.2 | 85.4 | 207.4 | 158.1
4064.1 | 3843.1 | 271.4 | 117.5 | 85.2 | 207.2 | 157.8
4065.1 | 3844.1 | 271.1 | 116.7 | 85.2 | 207 | 157.8
4066.1 | 3845.1 | 270.9 | 116.2 | 85.1 | 206.8 | 157.7
4067.1 | 3846.1 | 270.7 | 116 | 85.1 | 206.6 | 157.7
4068.1 | 3847.1 | 270.5 | 116 | 85.1 | 206.4 | 157.6
4069.1 | 3848.1 | 270.3 | 116.3 | 84.9 | 206.2 | 157.4
4070.1 | 3849.1 | 270 | 116.1 | 84.7 | 206 | 157.5
4071.1 | 3850.1 | 269.8 | 115.8 | 84.6 | 205.9 | 157.5
4072.1 | 3851.1 | 269.6 | 115.8 | 84.6 | 205.7 | 157.4
4073.1 | 3852.1 | 269.3 | 115.1 | 84.8 | 205.5 | 157.4
4074.1 | 3853.1 | 269.1 | 114.3 | 84.8 | 205.3 | 157.2
4075.1 | 3854.1 | 268.9 | 113.7 | 84.7 | 205.1 | 157.2
4076.1 | 3855.1 | 268.6 | 113.2 | 84.6 | 204.9 | 157.2
4077.1 | 3856.1 | 268.4 | 112.9 | 84.6 | 204.7 | 157
4078.1 | 3857.1 | 268.2 | 112.4 | 84.6 | 204.5 | 156.9
4079.1 | 3858.1 | 267.9 | 112.9 | 84.5 | 204.3 | 156.8
4080.1 | 3859.1 | 267.7 | 112.7 | 84.3 | 204.1 | 156.7
4081.1 | 3860.1 | 267.4 | 112.4 | 84.2 | 203.9 | 156.8
4082.1 | 3861.1 | 267.2 | 112 | 84 | 203.8 | 156.6
4083.1 | 3862.1 | 266.9 | 112.3 | 83.8 | 203.6 | 156.5
4084.1 | 3863.1 | 266.7 | 112.1 | 83.6 | 203.4 | 156.5
4085.1 | 3864.1 | 266.4 | 111.8 | 83.5 | 203.2 | 156.5
4086.1 | 3865.1 | 266.2 | 112 | 83.4 | 203 | 156.2
4087.1 | 3866.1 | 265.9 | 112.4 | 83.3 | 202.8 | 156.1
4088.1 | 3867.1 | 265.7 | 112.3 | 83.1 | 202.7 | 156
4089.1 | 3868.1 | 265.5 | 112.6 | 83 | 202.5 | 155.9
4090.1 | 3869.1 | 265.3 | 113.3 | 83 | 202.3 | 155.8
4091.1 | 3870.1 | 265 | 113.7 | 82.8 | 202.1 | 155.7
4092.1 | 3871.1 | 264.8 | 113.9 | 82.7 | 201.9 | 155.6
4093.1 | 3872.1 | 264.6 | 114 | 82.8 | 201.7 | 155.6
4094.1 | 3873.1 | 264.4 | 114.4 | 83 | 201.6 | 155.7
4095.1 | 3874.1 | 264.2 | 114.4 | 83 | 201.4 | 155.7
4096.1 | 3875.1 | 263.9 | 114.6 | 82.8 | 201.2 | 155.6
4097.1 | 3876.1 | 263.7 | 114.7 | 82.9 | 201 | 155.6
4098.1 | 3877.1 | 263.5 | 114.5 | 82.9 | 200.8 | 155.7
4099.1 | 3878.1 | 263.3 | 114.5 | 82.9 | 200.7 | 155.6
4100.1 | 3879.1 | 263.1 | 114.4 | 82.7 | 200.5 | 155.6
4101.1 | 3880.1 | 262.9 | 114.4 | 82.4 | 200.3 | 155.5
4102.1 | 3881.1 | 262.7 | 114.9 | 82.2 | 200.1 | 155.4
4103.1 | 3882.1 | 262.6 | 114.9 | 82 | 199.9 | 155.2
4104.1 | 3883.1 | 262.3 | 114.9 | 81.8 | 199.7 | 155.1
4105.1 | 3884.1 | 262.1 | 115.1 | 81.6 | 199.5 | 155.1
4106.1 | 3885.1 | 262 | 115.2 | 81.3 | 199.4 | 155.1
4107.1 | 3886.1 | 261.7 | 114.8 | 81.1 | 199.2 | 155
4108.1 | 3887.1 | 261.6 | 114.3 | 81 | 199 | 155
4109.1 | 3888.1 | 261.4 | 113.5 | 81.2 | 198.8 | 155
4110.1 | 3889.1 | 261.2 | 113.1 | 81.3 | 198.6 | 154.9
4111.1 | 3890.1 | 261 | 113.1 | 81.3 | 198.5 | 154.8
4112.1 | 3891.1 | 260.8 | 112.6 | 81.3 | 198.3 | 154.7
4113.1 | 3892.1 | 260.6 | 112.2 | 81.1 | 198.1 | 154.5
4114.1 | 3893.1 | 260.4 | 111.4 | 81 | 197.9 | 154.5
4115.1 | 3894.1 | 260.2 | 110.9 | 80.8 | 197.7 | 154.5
4116.1 | 3895.1 | 259.9 | 110.1 | 80.6 | 197.5 | 154.5
4117.1 | 3896.1 | 259.7 | 109.6 | 80.3 | 197.4 | 154.3
4118.1 | 3897.1 | 259.5 | 109.2 | 79.9 | 197.2 | 154.2
4119.1 | 3898.1 | 259.3 | 109 | 79.7 | 197 | 154.1
4120.1 | 3899.1 | 259.1 | 109.3 | 79.5 | 196.8 | 154
4121.1 | 3900.1 | 258.9 | 109.7 | 79.3 | 196.7 | 153.9
4122.1 | 3901.1 | 258.6 | 109.2 | 79.2 | 196.5 | 153.8
4123.1 | 3902.1 | 258.4 | 108.7 | 79.2 | 196.3 | 153.6
4124.1 | 3903.1 | 258.2 | 108.3 | 79.1 | 196.1 | 153.5
4125.1 | 3904.1 | 258 | 107.9 | 79.3 | 195.9 | 153.5
4126.1 | 3905.1 | 257.8 | 108.4 | 79.3 | 195.7 | 153.4
4127.1 | 3906.1 | 257.6 | 109 | 79.4 | 195.5 | 153.5
4128.1 | 3907.1 | 257.4 | 109 | 79.4 | 195.4 | 153.3
4129.1 | 3908.1 | 257.2 | 109.1 | 79.3 | 195.2 | 153.1
4130.1 | 3909.1 | 257 | 108.7 | 79.4 | 195 | 152.9
4131.1 | 3910.1 | 256.8 | 108.2 | 79.3 | 194.8 | 153
4132.1 | 3911.1 | 256.5 | 107.8 | 79.1 | 194.6 | 153
4133.1 | 3912.1 | 256.3 | 107.7 | 79 | 194.5 | 152.9
4134.1 | 3913.1 | 256.1 | 107.6 | 78.9 | 194.3 | 153
4135.1 | 3914.1 | 255.9 | 108.1 | 78.9 | 194.1 | 152.9
4136.1 | 3915.1 | 255.7 | 108.3 | 78.8 | 193.9 | 152.8
4137.1 | 3916.1 | 255.5 | 107.9 | 78.8 | 193.8 | 152.7
4138.1 | 3917.1 | 255.3 | 107.8 | 78.9 | 193.6 | 152.6
4139.1 | 3918.1 | 255.1 | 107.8 | 79 | 193.4 | 152.7
4140.1 | 3919.1 | 254.9 | 107.9 | 78.8 | 193.2 | 152.5
4141.1 | 3920.1 | 254.7 | 108.2 | 78.8 | 193 | 152.5
4142.1 | 3921.1 | 254.5 | 108.5 | 78.7 | 192.9 | 152.5
4143.1 | 3922.1 | 254.3 | 108.8 | 78.6 | 192.7 | 152.4
4144.1 | 3923.1 | 254.1 | 109.7 | 78.4 | 192.5 | 152.2
4145.1 | 3924.1 | 253.9 | 110 | 78.2 | 192.3 | 152.2
4146.1 | 3925.1 | 253.7 | 109.8 | 78.1 | 192.2 | 152.3
4147.1 | 3926.1 | 253.5 | 109.4 | 78 | 192 | 152.3
4148.1 | 3927.1 | 253.3 | 109 | 77.8 | 191.8 | 152.2
4149.1 | 3928.1 | 253.1 | 108.5 | 77.7 | 191.6 | 152.3
4150.1 | 3929.1 | 252.9 | 107.9 | 77.7 | 191.5 | 152.2
4151.1 | 3930.1 | 252.7 | 107.4 | 77.8 | 191.3 | 152.1
4152.1 | 3931.1 | 252.5 | 106.8 | 77.9 | 191.1 | 152.1
4153.1 | 3932.1 | 252.3 | 106.4 | 78.2 | 190.9 | 152.1
4154.1 | 3933.1 | 252.1 | 106.1 | 78.3 | 190.7 | 152.3
4155.1 | 3934.1 | 252 | 106.2 | 78.2 | 190.6 | 152.3
4156.1 | 3935.1 | 251.8 | 106.4 | 78.2 | 190.4 | 152.2
4157.1 | 3936.1 | 251.6 | 106.8 | 78 | 190.2 | 152.1
4158.1 | 3937.1 | 251.4 | 106.7 | 77.8 | 190 | 152.2
4159.1 | 3938.1 | 251.2 | 106.7 | 77.6 | 189.9 | 152.1
4160.1 | 3939.1 | 251.1 | 107.1 | 77.3 | 189.7 | 152.1
4161.1 | 3940.1 | 250.9 | 106.9 | 76.9 | 189.5 | 151.9
4162.1 | 3941.1 | 250.7 | 106.8 | 76.5 | 189.3 | 151.7
4163.1 | 3942.1 | 250.5 | 107.1 | 76.2 | 189.2 | 151.7
4164.1 | 3943.1 | 250.4 | 107.1 | 76 | 189 | 151.8
4165.1 | 3944.1 | 250.2 | 107.4 | 75.9 | 188.8 | 151.7
4166.1 | 3945.1 | 250 | 107.6 | 75.8 | 188.6 | 151.7
4167.1 | 3946.1 | 249.8 | 107.5 | 75.9 | 188.5 | 151.8
4168.1 | 3947.1 | 249.6 | 107.5 | 76.1 | 188.3 | 151.6
4169.1 | 3948.1 | 249.4 | 107.6 | 76 | 188.1 | 151.6
4170.1 | 3949.1 | 249.3 | 107 | 75.8 | 187.9 | 151.5
4171.1 | 3950.1 | 249.1 | 106.4 | 75.8 | 187.8 | 151.4
4172.1 | 3951.1 | 248.9 | 105.8 | 75.7 | 187.6 | 151.4
4173.1 | 3952.1 | 248.7 | 105.3 | 75.8 | 187.4 | 151.4
4174.1 | 3953.1 | 248.5 | 104.9 | 75.7 | 187.2 | 151.5
4175.1 | 3954.1 | 248.4 | 104.8 | 75.8 | 187 | 151.5
4176.1 | 3955.1 | 248.2 | 104.6 | 76 | 186.9 | 151.5
4177.1 | 3956.1 | 248 | 104.3 | 75.9 | 186.7 | 151.5
4178.1 | 3957.1 | 247.9 | 103.9 | 75.7 | 186.5 | 151.3
4179.1 | 3958.1 | 247.7 | 103.6 | 75.5 | 186.3 | 151.2
4180.1 | 3959.1 | 247.5 | 103.4 | 75.7 | 186.2 | 151.1
4181.1 | 3960.1 | 247.3 | 103.2 | 75.9 | 186 | 151
4182.1 | 3961.1 | 247.1 | 103 | 76 | 185.8 | 150.7
4183.1 | 3962.1 | 246.9 | 102.8 | 76.1 | 185.7 | 150.6
4184.1 | 3963.1 | 246.8 | 103.1 | 76.2 | 185.5 | 150.6
4185.1 | 3964.1 | 246.6 | 103.7 | 76.2 | 185.3 | 150.6
4186.1 | 3965.1 | 246.4 | 104.1 | 76.2 | 185.1 | 150.4
4187.1 | 3966.1 | 246.2 | 104.5 | 76.1 | 185 | 150.2
4188.1 | 3967.1 | 246 | 104.8 | 75.9 | 184.8 | 150.2
4189.1 | 3968.1 | 245.8 | 104.8 | 75.6 | 184.6 | 150.1
4190.1 | 3969.1 | 245.7 | 104.9 | 75.5 | 184.5 | 149.8
4191.1 | 3970.1 | 245.5 | 105.4 | 75.2 | 184.3 | 149.7
4192.1 | 3971.1 | 245.3 | 106 | 75 | 184.1 | 149.7
4193.1 | 3972.1 | 245.1 | 106.5 | 74.9 | 184 | 149.7
4194.1 | 3973.1 | 244.9 | 106.6 | 75.1 | 183.8 | 149.6
4195.1 | 3974.1 | 244.7 | 107.1 | 75.2 | 183.6 | 149.6
4196.1 | 3975.1 | 244.5 | 107.5 | 75.1 | 183.5 | 149.6
4197.1 | 3976.1 | 244.3 | 107.7 | 75 | 183.3 | 149.4
4198.1 | 3977.1 | 244.1 | 107.7 | 74.9 | 183.1 | 149.3
4199.1 | 3978.1 | 243.9 | 108 | 74.9 | 183 | 149.3
4200.1 | 3979.1 | 243.7 | 107.4 | 75 | 182.8 | 149.2
4201.1 | 3980.1 | 243.5 | 107 | 74.9 | 182.6 | 149.1
4202.1 | 3981.1 | 243.3 | 106.9 | 74.7 | 182.5 | 149.1
4203.1 | 3982.1 | 243.1 | 106.2 | 74.9 | 182.3 | 149
4204.1 | 3983.1 | 242.9 | 105.5 | 75 | 182.1 | 148.9
4205.1 | 3984.1 | 242.7 | 105 | 75 | 182 | 148.8
4206.1 | 3985.1 | 242.5 | 104.6 | 75.1 | 181.8 | 148.7
4207.1 | 3986.1 | 242.3 | 104 | 75.1 | 181.6 | 148.8
4208.1 | 3987.1 | 242.1 | 103.5 | 75.2 | 181.5 | 148.8
4209.1 | 3988.1 | 241.9 | 102.7 | 75.3 | 181.3 | 148.7
4210.1 | 3989.1 | 241.7 | 102.4 | 75.4 | 181.1 | 148.5
4211.1 | 3990.1 | 241.5 | 102.3 | 75.5 | 181 | 148.3
4212.1 | 3991.1 | 241.2 | 102 | 75.5 | 180.8 | 148.2
4213.1 | 3992.1 | 241 | 102.2 | 75.4 | 180.7 | 148.2
4214.1 | 3993.1 | 240.8 | 102.2 | 75.3 | 180.5 | 148.2
4215.1 | 3994.1 | 240.6 | 101.7 | 75.3 | 180.3 | 147.9
4216.1 | 3995.1 | 240.4 | 101.1 | 75 | 180.2 | 147.8
4217.1 | 3996.1 | 240.2 | 100.7 | 74.7 | 180 | 147.7
4218.1 | 3997.1 | 240 | 100.4 | 75 | 179.9 | 147.6
4219.1 | 3998.1 | 239.8 | 100.3 | 75 | 179.7 | 147.6
4220.1 | 3999.1 | 239.6 | 100.6 | 75.1 | 179.5 | 147.7
4221.1 | 4000.1 | 239.4 | 101.5 | 75.4 | 179.4 | 147.6
4222.1 | 4001.1 | 239.2 | 101.9 | 75.6 | 179.2 | 147.5
4223.1 | 4002.1 | 239 | 102.3 | 75.6 | 179 | 147.4
4224.1 | 4003.1 | 238.8 | 102.5 | 75.8 | 178.9 | 147.5
4225.1 | 4004.1 | 238.6 | 102.2 | 75.8 | 178.7 | 147.4
4226.1 | 4005.1 | 238.4 | 101.9 | 75.6 | 178.6 | 147.4
4227.1 | 4006.1 | 238.2 | 101.9 | 75.7 | 178.4 | 147.1
4228.1 | 4007.1 | 238 | 102 | 75.7 | 178.3 | 147
4229.1 | 4008.1 | 237.8 | 102.5 | 75.6 | 178.1 | 146.9
4230.1 | 4009.1 | 237.7 | 102.6 | 75.4 | 177.9 | 146.8
4231.1 | 4010.1 | 237.5 | 102.4 | 75.3 | 177.8 | 146.8
4232.1 | 4011.1 | 237.3 | 102.2 | 75.3 | 177.6 | 146.8
4233.1 | 4012.1 | 237.1 | 101.7 | 75.2 | 177.5 | 146.8
4234.1 | 4013.1 | 236.9 | 101.5 | 75 | 177.3 | 146.6
4235.1 | 4014.1 | 236.7 | 101.5 | 74.9 | 177.2 | 146.6
4236.1 | 4015.1 | 236.5 | 101.3 | 74.8 | 177 | 146.6
4237.2 | 4016.2 | 236.4 | 101 | 74.8 | 176.9 | 146.4
4238.2 | 4017.2 | 236.2 | 100.5 | 74.7 | 176.7 | 146.3
4239.2 | 4018.2 | 236 | 100.3 | 74.8 | 176.5 | 146.2
4240.2 | 4019.2 | 235.8 | 100.5 | 74.7 | 176.4 | 146.2
4241.2 | 4020.2 | 235.7 | 100 | 74.7 | 176.2 | 146.2
4242.2 | 4021.2 | 235.5 | 99.7 | 74.6 | 176.1 | 145.9
4243.2 | 4022.2 | 235.3 | 100 | 74.4 | 175.9 | 145.7
4244.2 | 4023.2 | 235.1 | 100.5 | 74.1 | 175.8 | 145.6
4245.2 | 4024.2 | 235 | 100.8 | 74.1 | 175.6 | 145.7
4246.2 | 4025.2 | 234.8 | 100.9 | 74.3 | 175.5 | 145.7
4247.2 | 4026.2 | 234.6 | 100.6 | 74.1 | 175.3 | 145.7
4248.2 | 4027.2 | 234.5 | 100.3 | 73.8 | 175.1 | 145.6
4249.2 | 4028.2 | 234.3 | 100 | 73.6 | 175 | 145.4
4250.2 | 4029.2 | 234.1 | 100 | 73.4 | 174.9 | 145.2
4251.2 | 4030.2 | 233.9 | 99.4 | 73.1 | 174.7 | 145.1
4252.2 | 4031.2 | 233.8 | 98.8 | 73 | 174.6 | 145.1
4253.2 | 4032.2 | 233.6 | 99 | 72.9 | 174.4 | 145.1
4254.2 | 4033.2 | 233.4 | 98.7 | 72.8 | 174.3 | 145.1
4255.2 | 4034.2 | 233.2 | 98.6 | 73 | 174.1 | 145
4256.2 | 4035.2 | 233 | 98.3 | 73.1 | 173.9 | 144.9
4257.2 | 4036.2 | 232.9 | 97.9 | 72.8 | 173.8 | 145
4258.2 | 4037.2 | 232.7 | 97.3 | 72.7 | 173.7 | 144.9
4259.2 | 4038.2 | 232.5 | 97.3 | 72.7 | 173.5 | 144.7
4260.2 | 4039.2 | 232.3 | 97.3 | 72.7 | 173.4 | 144.7
4261.2 | 4040.2 | 232.1 | 96.7 | 72.8 | 173.2 | 144.7
4262.2 | 4041.2 | 231.9 | 96.3 | 72.8 | 173 | 144.6
4263.2 | 4042.2 | 231.7 | 96 | 72.9 | 172.9 | 144.7
4264.2 | 4043.2 | 231.5 | 95.8 | 73.1 | 172.7 | 144.6
4265.2 | 4044.2 | 231.4 | 96.3 | 73.1 | 172.6 | 144.4
4266.2 | 4045.2 | 231.2 | 96.1 | 73.1 | 172.5 | 144.4
4267.2 | 4046.2 | 231 | 96.4 | 73.4 | 172.3 | 144.4
4268.2 | 4047.2 | 230.8 | 96.8 | 73.5 | 172.1 | 144.3
4269.2 | 4048.2 | 230.6 | 97.3 | 73.5 | 172 | 144
4270.2 | 4049.2 | 230.4 | 97.7 | 73.3 | 171.8 | 143.8
4271.2 | 4050.2 | 230.2 | 97.8 | 72.8 | 171.7 | 143.8
4272.2 | 4051.2 | 230 | 97.7 | 72.6 | 171.5 | 143.8
4273.2 | 4052.2 | 229.8 | 97.8 | 72.4 | 171.4 | 143.8
4274.2 | 4053.2 | 229.6 | 97.2 | 72.1 | 171.3 | 143.9
4275.2 | 4054.2 | 229.4 | 96.9 | 71.8 | 171.1 | 143.9
4276.2 | 4055.2 | 229.2 | 96.7 | 71.9 | 171 | 143.9
4277.2 | 4056.2 | 229 | 96.8 | 71.9 | 170.8 | 143.9
4278.2 | 4057.2 | 228.8 | 97 | 71.9 | 170.7 | 143.9
4279.2 | 4058.2 | 228.6 | 97.1 | 71.9 | 170.5 | 143.9
4280.2 | 4059.2 | 228.4 | 96.5 | 71.8 | 170.4 | 143.8
4281.2 | 4060.2 | 228.2 | 96 | 71.8 | 170.3 | 143.8
4282.2 | 4061.2 | 228 | 95.8 | 71.9 | 170.1 | 143.8
4283.2 | 4062.2 | 227.8 | 95.5 | 71.7 | 170 | 143.8
4284.2 | 4063.2 | 227.6 | 95.1 | 71.4 | 169.9 | 143.8
4285.2 | 4064.2 | 227.4 | 95.1 | 71.4 | 169.7 | 143.6
4286.2 | 4065.2 | 227.2 | 94.8 | 71.5 | 169.6 | 143.5
4287.2 | 4066.2 | 226.9 | 94.6 | 71.4 | 169.4 | 143.4
4288.2 | 4067.2 | 226.7 | 94.4 | 71.3 | 169.3 | 143.2
4289.2 | 4068.2 | 226.5 | 94.1 | 71.1 | 169.1 | 143.1
4290.2 | 4069.2 | 226.3 | 94 | 71.2 | 169 | 143.1
4291.2 | 4070.2 | 226.1 | 94.1 | 71.3 | 168.8 | 143.2
4292.2 | 4071.2 | 225.9 | 93.9 | 71.3 | 168.7 | 143.3
4293.2 | 4072.2 | 225.7 | 93.7 | 71.3 | 168.6 | 143.2
4294.2 | 4073.2 | 225.5 | 93.5 | 71.5 | 168.4 | 143
4295.2 | 4074.2 | 225.3 | 93.4 | 71.5 | 168.3 | 142.8
4296.2 | 4075.2 | 225.1 | 93.4 | 71.6 | 168.1 | 142.6
4297.2 | 4076.2 | 224.9 | 93.3 | 71.6 | 168 | 142.5
4298.2 | 4077.2 | 224.7 | 93.1 | 71.5 | 167.8 | 142.5
4299.2 | 4078.2 | 224.5 | 92.9 | 71.5 | 167.7 | 142.4
4300.2 | 4079.2 | 224.3 | 92.8 | 71.5 | 167.6 | 142.3
4301.2 | 4080.2 | 224.1 | 92.7 | 71.6 | 167.4 | 142.1
4302.2 | 4081.2 | 223.8 | 92.5 | 71.7 | 167.3 | 141.9
4303.2 | 4082.2 | 223.6 | 92.3 | 71.8 | 167.2 | 141.8
4304.2 | 4083.2 | 223.4 | 92.3 | 71.9 | 167 | 141.8
4305.2 | 4084.2 | 223.2 | 92.3 | 72 | 166.9 | 141.9
4306.2 | 4085.2 | 223 | 92.8 | 71.8 | 166.7 | 141.7
4307.2 | 4086.2 | 222.8 | 92.5 | 71.7 | 166.6 | 141.6
4308.2 | 4087.2 | 222.5 | 92.3 | 71.3 | 166.5 | 141.5
4309.2 | 4088.2 | 222.3 | 92.3 | 71 | 166.3 | 141.4
4310.2 | 4089.2 | 222.1 | 92.2 | 70.7 | 166.2 | 141.3
4311.2 | 4090.2 | 221.9 | 92.1 | 70.4 | 166.1 | 141.3
4312.2 | 4091.2 | 221.7 | 92 | 70.2 | 165.9 | 141.1
4313.2 | 4092.2 | 221.5 | 91.8 | 70.2 | 165.8 | 141.1
4314.2 | 4093.2 | 221.3 | 91.6 | 70.3 | 165.6 | 141.1
4315.2 | 4094.2 | 221.1 | 91.5 | 70.3 | 165.5 | 140.9
4316.2 | 4095.2 | 220.9 | 91.3 | 70.2 | 165.4 | 140.8
4317.2 | 4096.2 | 220.7 | 90.9 | 70.2 | 165.2 | 140.7
4318.2 | 4097.2 | 220.5 | 90.6 | 70.3 | 165.1 | 140.6
4319.2 | 4098.2 | 220.3 | 90.8 | 70.2 | 165 | 140.7
4320.2 | 4099.2 | 220.1 | 90.9 | 70.3 | 164.8 | 140.6
4321.2 | 4100.2 | 219.9 | 91 | 70.2 | 164.7 | 140.4
4322.2 | 4101.2 | 219.7 | 91.4 | 70.2 | 164.6 | 140.3
4323.2 | 4102.2 | 219.5 | 91.6 | 70.1 | 164.4 | 140.2
4324.2 | 4103.2 | 219.2 | 91.4 | 70.2 | 164.3 | 140
4325.2 | 4104.2 | 219 | 91.3 | 70.2 | 164.2 | 139.8
4326.2 | 4105.2 | 218.8 | 91.2 | 70.2 | 164 | 139.7
4327.2 | 4106.2 | 218.6 | 91 | 70.3 | 163.9 | 139.7
4328.2 | 4107.2 | 218.4 | 90.5 | 70.5 | 163.7 | 139.7
4329.2 | 4108.2 | 218.1 | 90.2 | 70.4 | 163.6 | 139.7
4330.2 | 4109.2 | 217.9 | 90 | 70.2 | 163.5 | 139.6
4331.2 | 4110.2 | 217.7 | 89.8 | 70.1 | 163.3 | 139.4
4332.2 | 4111.2 | 217.5 | 89.8 | 70.4 | 163.2 | 139.3
4333.2 | 4112.2 | 217.3 | 89.7 | 70.5 | 163.1 | 139.2
4334.2 | 4113.2 | 217 | 90 | 70.5 | 163 | 139.2
4335.2 | 4114.2 | 216.8 | 90.4 | 70.3 | 162.8 | 139.1
4336.2 | 4115.2 | 216.6 | 90.5 | 70.2 | 162.7 | 139
4337.2 | 4116.2 | 216.4 | 90.5 | 70.2 | 162.6 | 138.9
4338.2 | 4117.2 | 216.2 | 90.3 | 70.3 | 162.4 | 138.7
4339.2 | 4118.2 | 216 | 90.1 | 70.4 | 162.3 | 138.7
4340.2 | 4119.2 | 215.8 | 89.8 | 70.5 | 162.1 | 138.6
4341.2 | 4120.2 | 215.6 | 89.6 | 70.5 | 162 | 138.5
4342.2 | 4121.2 | 215.4 | 89.4 | 70.4 | 161.9 | 138.4
4343.2 | 4122.2 | 215.2 | 89.5 | 70.5 | 161.7 | 138.3
4344.2 | 4123.2 | 215 | 89.6 | 70.5 | 161.6 | 138.2
4345.2 | 4124.2 | 214.8 | 89.6 | 70.4 | 161.5 | 138
4346.2 | 4125.2 | 214.6 | 90.3 | 70.3 | 161.3 | 138
4347.2 | 4126.2 | 214.4 | 90.7 | 70.4 | 161.2 | 138
4348.2 | 4127.2 | 214.2 | 90.8 | 70.4 | 161.1 | 138
4349.2 | 4128.2 | 214 | 90.6 | 70.3 | 161 | 137.9
4350.2 | 4129.2 | 213.8 | 90.6 | 70.2 | 160.8 | 137.7
4351.2 | 4130.2 | 213.6 | 90.7 | 69.9 | 160.7 | 137.5
4352.2 | 4131.2 | 213.5 | 91.2 | 69.8 | 160.6 | 137.4
4353.2 | 4132.2 | 213.3 | 92.1 | 69.8 | 160.4 | 137.2
4354.2 | 4133.2 | 213.1 | 92.7 | 69.8 | 160.3 | 137.2
4355.2 | 4134.2 | 212.9 | 93.3 | 69.9 | 160.2 | 137.1
4356.2 | 4135.2 | 212.7 | 93.2 | 69.7 | 160.1 | 137
4357.2 | 4136.2 | 212.5 | 93.1 | 69.5 | 159.9 | 137
4358.2 | 4137.2 | 212.3 | 92.8 | 69.3 | 159.8 | 136.9
4359.2 | 4138.2 | 212.1 | 92.5 | 69.2 | 159.6 | 136.8
4360.2 | 4139.2 | 211.9 | 92.3 | 69.1 | 159.5 | 136.7
4361.2 | 4140.2 | 211.7 | 92 | 69.1 | 159.4 | 136.6
4362.2 | 4141.2 | 211.5 | 91.9 | 69.3 | 159.2 | 136.6
4363.2 | 4142.2 | 211.3 | 92 | 69.3 | 159.1 | 136.5
4364.2 | 4143.2 | 211.1 | 92 | 69.3 | 159 | 136.3
4365.2 | 4144.2 | 211 | 92.2 | 69.5 | 158.9 | 136.2
4366.2 | 4145.2 | 210.8 | 92 | 69.6 | 158.7 | 136.1
4367.2 | 4146.2 | 210.6 | 91.9 | 69.5 | 158.6 | 136
4368.2 | 4147.2 | 210.4 | 92.2 | 69.5 | 158.5 | 135.9
4369.2 | 4148.2 | 210.2 | 92.5 | 69.3 | 158.3 | 135.9
4370.2 | 4149.2 | 210 | 92.4 | 69.1 | 158.2 | 135.9
4371.2 | 4150.2 | 209.8 | 92.5 | 68.9 | 158.1 | 135.9
4372.2 | 4151.2 | 209.6 | 92.2 | 68.9 | 158 | 135.9
4373.2 | 4152.2 | 209.4 | 91.9 | 68.6 | 157.8 | 135.8
4374.2 | 4153.2 | 209.2 | 92.1 | 68.6 | 157.7 | 135.8
4375.2 | 4154.2 | 209 | 92.1 | 68.7 | 157.6 | 135.7
4376.2 | 4155.2 | 208.8 | 92.2 | 68.7 | 157.5 | 135.6
4377.2 | 4156.2 | 208.6 | 92 | 68.7 | 157.3 | 135.5
4378.2 | 4157.2 | 208.4 | 91.7 | 68.7 | 157.2 | 135.4
4379.2 | 4158.2 | 208.2 | 91.2 | 68.7 | 157.1 | 135.3
4380.2 | 4159.2 | 208 | 90.9 | 68.7 | 156.9 | 135.2
4381.2 | 4160.2 | 207.8 | 90.5 | 68.7 | 156.8 | 135.1
4382.2 | 4161.2 | 207.6 | 90.4 | 68.7 | 156.7 | 134.9
4383.2 | 4162.2 | 207.3 | 90.5 | 68.8 | 156.6 | 134.8
4384.2 | 4163.2 | 207.1 | 90.4 | 68.9 | 156.4 | 134.8
4385.2 | 4164.2 | 206.9 | 90 | 69.1 | 156.3 | 134.8
4386.2 | 4165.2 | 206.7 | 89.6 | 69 | 156.2 | 134.7
4387.2 | 4166.2 | 206.5 | 89.3 | 68.8 | 156.1 | 134.6
4388.2 | 4167.2 | 206.3 | 89.2 | 68.6 | 155.9 | 134.5
4389.2 | 4168.2 | 206 | 88.9 | 68.5 | 155.8 | 134.5
4390.2 | 4169.2 | 205.8 | 88.8 | 68.7 | 155.7 | 134.5
4391.2 | 4170.2 | 205.6 | 88.5 | 68.7 | 155.6 | 134.4
4392.2 | 4171.2 | 205.4 | 88.1 | 68.5 | 155.4 | 134.2
4393.2 | 4172.2 | 205.1 | 87.7 | 68.3 | 155.3 | 134.2
4394.2 | 4173.2 | 204.9 | 87.6 | 68.1 | 155.2 | 134.2
4395.2 | 4174.2 | 204.7 | 87.7 | 68.1 | 155.1 | 134.2
4396.2 | 4175.2 | 204.5 | 87.7 | 67.9 | 154.9 | 134.2
4397.2 | 4176.2 | 204.3 | 87.5 | 67.6 | 154.8 | 134.1
4398.2 | 4177.2 | 204.1 | 87.3 | 67.5 | 154.7 | 134
4399.2 | 4178.2 | 203.9 | 87.4 | 67.3 | 154.6 | 133.9
4400.2 | 4179.2 | 203.7 | 87.1 | 67.1 | 154.4 | 133.8
4401.2 | 4180.2 | 203.5 | 87.2 | 67 | 154.3 | 133.6
4402.2 | 4181.2 | 203.2 | 87.1 | 66.8 | 154.2 | 133.5
4403.2 | 4182.2 | 203 | 87 | 66.7 | 154.1 | 133.4
4404.2 | 4183.2 | 202.8 | 87 | 66.7 | 154 | 133.2
4405.2 | 4184.2 | 202.6 | 86.9 | 66.6 | 153.8 | 133.2
4406.2 | 4185.2 | 202.4 | 87.3 | 66.7 | 153.7 | 133.2
4407.2 | 4186.2 | 202.3 | 87.3 | 66.7 | 153.6 | 133.2
4408.2 | 4187.2 | 202.1 | 87.2 | 66.7 | 153.5 | 133.2
4409.2 | 4188.2 | 201.9 | 87.4 | 66.6 | 153.4 | 133.2
4410.2 | 4189.2 | 201.7 | 87.2 | 66.7 | 153.2 | 133.2
4411.2 | 4190.2 | 201.5 | 87.1 | 66.7 | 153.1 | 133.2
4412.2 | 4191.2 | 201.3 | 87 | 66.7 | 153 | 133.2
4413.2 | 4192.2 | 201.1 | 87 | 66.7 | 152.9 | 133.2
4414.2 | 4193.2 | 200.9 | 86.9 | 66.7 | 152.7 | 133.1
4415.2 | 4194.2 | 200.7 | 86.5 | 66.8 | 152.6 | 133.2
4416.2 | 4195.2 | 200.5 | 86.1 | 66.6 | 152.5 | 133.2
4417.2 | 4196.2 | 200.3 | 85.9 | 66.5 | 152.4 | 133.2
4418.2 | 4197.2 | 200.1 | 85.7 | 66.5 | 152.3 | 133.1
4419.2 | 4198.2 | 199.9 | 85.3 | 66.5 | 152.1 | 132.9
4420.2 | 4199.2 | 199.7 | 85.1 | 66.6 | 152 | 132.9
4421.2 | 4200.2 | 199.5 | 85 | 66.4 | 151.9 | 132.7
4422.2 | 4201.2 | 199.3 | 84.9 | 66.2 | 151.8 | 132.7
4423.2 | 4202.2 | 199.1 | 84.7 | 66 | 151.7 | 132.7
4424.2 | 4203.2 | 199 | 84.5 | 65.7 | 151.5 | 132.7
4425.2 | 4204.2 | 198.8 | 84.3 | 65.7 | 151.4 | 132.6
4426.2 | 4205.2 | 198.6 | 84.1 | 65.5 | 151.3 | 132.6
4427.2 | 4206.2 | 198.4 | 84 | 65.6 | 151.2 | 132.6
4428.2 | 4207.2 | 198.2 | 83.8 | 65.6 | 151.1 | 132.5
4429.2 | 4208.2 | 198 | 83.4 | 65.7 | 151 | 132.4
4430.2 | 4209.2 | 197.8 | 83.1 | 65.7 | 150.8 | 132.3
4431.2 | 4210.2 | 197.7 | 83.1 | 65.7 | 150.7 | 132.1
4432.2 | 4211.2 | 197.5 | 82.9 | 65.6 | 150.6 | 132.1
4433.2 | 4212.2 | 197.3 | 82.7 | 65.6 | 150.5 | 132
4434.2 | 4213.2 | 197.1 | 82.6 | 65.7 | 150.4 | 131.8
4435.2 | 4214.2 | 196.9 | 82.5 | 65.6 | 150.2 | 131.6
4436.2 | 4215.2 | 196.7 | 82.2 | 65.6 | 150.1 | 131.6
4437.2 | 4216.2 | 196.5 | 81.9 | 65.2 | 150 | 131.6
4438.2 | 4217.2 | 196.3 | 81.8 | 65.1 | 149.9 | 131.5
4439.2 | 4218.2 | 196.1 | 82 | 65 | 149.7 | 131.4
4440.2 | 4219.2 | 195.9 | 82.5 | 64.9 | 149.6 | 131.3
4441.2 | 4220.2 | 195.7 | 82.8 | 64.8 | 149.5 | 131.2
4442.2 | 4221.2 | 195.5 | 83.1 | 64.6 | 149.4 | 131.1
4443.2 | 4222.2 | 195.3 | 83.7 | 64.5 | 149.3 | 131
4444.2 | 4223.2 | 195.1 | 83.9 | 64.5 | 149.2 | 131
4445.2 | 4224.2 | 195 | 84.1 | 64.5 | 149.1 | 130.8
4446.2 | 4225.2 | 194.8 | 84.4 | 64.6 | 149 | 130.7
4447.2 | 4226.2 | 194.6 | 84.8 | 64.7 | 148.9 | 130.6
4448.2 | 4227.2 | 194.4 | 84.7 | 64.7 | 148.7 | 130.6
4449.2 | 4228.2 | 194.2 | 84.7 | 64.7 | 148.6 | 130.5
4450.2 | 4229.2 | 194 | 85 | 64.7 | 148.5 | 130.4
4451.2 | 4230.2 | 193.8 | 84.7 | 64.7 | 148.4 | 130.3
4452.2 | 4231.2 | 193.6 | 84.3 | 64.5 | 148.3 | 130.4
4453.2 | 4232.2 | 193.4 | 84 | 64.5 | 148.2 | 130.2
4454.2 | 4233.2 | 193.2 | 84 | 64.4 | 148.1 | 130
4455.2 | 4234.2 | 193 | 84 | 64.4 | 147.9 | 130.1
4456.2 | 4235.2 | 192.8 | 84.2 | 64.4 | 147.8 | 130.2
4457.2 | 4236.2 | 192.6 | 84 | 64.5 | 147.7 | 130.2
4458.2 | 4237.2 | 192.4 | 84 | 64.4 | 147.6 | 130
4459.2 | 4238.2 | 192.2 | 84.3 | 64.1 | 147.5 | 129.8
4460.2 | 4239.2 | 192 | 84.8 | 64.2 | 147.4 | 129.8
4461.2 | 4240.2 | 191.9 | 84.9 | 64.3 | 147.3 | 129.8
4462.2 | 4241.2 | 191.7 | 85.1 | 64 | 147.1 | 129.7
4463.2 | 4242.2 | 191.5 | 85.3 | 63.8 | 147 | 129.7
4464.2 | 4243.2 | 191.3 | 85.2 | 63.4 | 146.9 | 129.5
4465.2 | 4244.2 | 191.1 | 84.7 | 63 | 146.8 | 129.4
4466.2 | 4245.2 | 190.9 | 84.3 | 62.8 | 146.7 | 129.3
4467.2 | 4246.2 | 190.7 | 84.1 | 62.9 | 146.6 | 129.3
4468.2 | 4247.2 | 190.5 | 83.9 | 62.9 | 146.4 | 129.2
4469.2 | 4248.2 | 190.4 | 84.4 | 62.7 | 146.3 | 129.2
4470.2 | 4249.2 | 190.2 | 84.2 | 62.6 | 146.2 | 129.1
4471.2 | 4250.2 | 190 | 84.1 | 62.5 | 146.1 | 129.1
4472.2 | 4251.2 | 189.8 | 84.4 | 62.1 | 146 | 129

## Test Facts
Last row in IRMS data sheets: | 23
Time when Penlight power was initiated: | 221