## Test Conditions
CAROLFIRE Intermediate Scale Preliminary Test Number IP-4 - Circuit Simulator Data Only
Test Date: 10/17/2006
Circuit Simulator Configurations and connections:
|  | Circuit #1 | Circuit#2 | Circuit #3 | Circuit #4
| CPT Size: | 150 VA | 150 VA | 200 VA | 100 VA
| CPT Grounding: | NOT Grounded | Grounded | Grounded | Grounded
| General Config. | Generic MOV-1a | Generic MOV-1a | Generic MOV-1a | Generic MOV-1a
| Cable Type | PVC/PVC 7/C 12 AWG (Cable Item #1) in a 6-cable bundle at location A (all circuits co-located) | PVC/PVC 7/C 12 AWG (Cable Item #1) in a 6-cable bundle at location A (all circuits co-located) | PVC/PVC 7/C 12 AWG (Cable Item #1) in a 6-cable bundle at location A (all circuits co-located) | PVC/PVC 7/C 12 AWG (Cable Item #1) in a 6-cable bundle at location A (all circuits co-located)
| Wiring Config: | Source Centered | Source Centered | Source Centered | Source Centered
| Circuit Path 1: | Switch Closed: Energized source (connected to fused side of CPT) | Switch Closed: Energized source (connected to fused side of CPT) | Switch Closed: Energized source (connected to fused side of CPT) | Switch Closed: Energized source (connected to fused side of CPT)
| Circuit Path 2: | Switch Closed: Energized source. Conductor is also connected ( at far end of cable) through 1.75 k-ohm resistor to conductor on Circuit Path 4 (indicator simulation). Note that this is an error versus intent to wire this to Path 7. | Switch Closed: Energized source. Conductor is also connected ( at far end of cable) through 1.75 k-ohm resistor to conductor on Circuit Path 4 (indicator simulation). Note that this is an error versus intent to wire this to Path 7. | Switch Closed: Energized source. Conductor is also connected ( at far end of cable) through 1.75 k-ohm resistor to conductor on Circuit Path 4 (indicator simulation). Note that this is an error versus intent to wire this to Path 7. | Switch Closed: Energized source. Conductor is also connected ( at far end of cable) through 1.75 k-ohm resistor to conductor on Circuit Path 4 (indicator simulation). Note that this is an error versus intent to wire this to Path 7.
| Circuit Path 3: | Switch open: not connected | Switch open: not connected | Switch open: not connected | Switch open: not connected
| Circuit Path 4: | Passive Target: Connected to CPT neutral return through 1.75 k-ohm resistor (un-lit indicator light simulation). Also in this circuit path is a 1.75Kohme resistor on the far end of the cable (this is an error versus intent to connect return resistor to Path 7). | Passive Target: Connected to CPT neutral return through 1.75 k-ohm resistor (un-lit indicator light simulation). Also in this circuit path is a 1.75Kohme resistor on the far end of the cable (this is an error versus intent to connect return resistor to Path 7). | Passive Target: Connected to CPT neutral return through 1.75 k-ohm resistor (un-lit indicator light simulation). Also in this circuit path is a 1.75Kohme resistor on the far end of the cable (this is an error versus intent to connect return resistor to Path 7). | Passive Target: Connected to CPT neutral return through 1.75 k-ohm resistor (un-lit indicator light simulation). Also in this circuit path is a 1.75Kohme resistor on the far end of the cable (this is an error versus intent to connect return resistor to Path 7).
| Circuit Path 5: | Active Target: Connected to Motor Starter | Active Target: Connected to Motor Starter | Active Target: Connected to Motor Starter | Active Target: Connected to Motor Starter
| Circuit Path 6: | Active Target: Connected to Motor Starter | Active Target: Connected to Motor Starter | Active Target: Connected to Motor Starter | Active Target: Connected to Motor Starter
| Circuit Path 7: | Switch Closed - Connects conductor to CPT neutral return. | Switch Closed - Connects conductor to CPT neutral return. | Switch Closed - Connects conductor to CPT neutral return. | Switch Closed - Connects conductor to CPT neutral return.
| Circuit Path 8: | Switch Open: Path is connected to cable's last conductor (spare conductor simulation) | Switch Open: Path is connected to cable's last conductor (spare conductor simulation) | Switch Open: Path is connected to cable's last conductor (spare conductor simulation) | Switch Open: Path is connected to cable's last conductor (spare conductor simulation)
| Circuit Path 9: | Switch Open: not connected | Switch Open: not connected | Switch Open: not connected | Switch Open: not connected
A Note on Data Conversion and Accuracy:
Each of the voltage and current transducers used produces a 4-20mA signal which is routed through 477ohm precision resistors converting the signal to a nominal 2-10 VDC signal. This DC voltage signal was monitored using a National Instruments PCI-6071E data aquisition (DAQ) card. These data as recorded are presented in the "Raw Test Data" worksheet. The raw data were converted to actual values as shown on the "Converted Test Data" worksheet. The conversion is based on the fact that the 4-20 mA signal corresponds to a full scale reading on the voltage transducers of 0-300 VAC and on the current transducers of 0-5A. Nominal zero point readings for each transducer were taken in a separate test run in order to establish more accurately the zero points for current and voltage measurement. The Zero Point values are provided, and the full run is documented in a separate data file (see 'Zero Points' worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Circuit Fault Summary
Summary of Circuit Faulting Behavior for all Tested Circuits
Circuit 1 | Test Circuit 1 experienced a momentary hot short to both targets 5 and 6 sustained for less than 0.4 s. A fuse blow occured about 29 s later. After loss of circuit power, there are clear indications of inter-cable hot shorts involving essentially all four of the circuits present with Circuit 2 acting as the likely source of these hot shorts. In the case of Circuit 1 the target conductor on Path 6 was hit. The hot short lasted about 1 s.
Circuit 2 | This circuit did experience spurious actuation of both motor starters. The spurious actuations lasted a total of about 6 s. It also appears that this circuit acted as the energizing source for inter-cable hot shorts to all three of the other circuits present.
Circuit 3 | This circuit shorted to ground causing a fuse blow. However, after the fuse blow, the circuit also experienced inter-cable hot shorts twice. In both cases, the shorts were of momentary duration. In the first case, Circuit 2 acted as the energizing source. In the second case, Circuit 4 acted as the energizing source. Both of the two active target paths were impacted (Paths 5 and 6).
Circuit 4 | This was the target of two separate inter-cable hot shorts of momentary duration. It was also the apparent source of momentary inter-cable hot shorts impacting Circuit #3. Following the inter-cable interactions, the circuit experienced a spurious actuation due to intra-cable shorting on T6 that lasted 1.2 s before fuse blow.
Note: | All four circuits were mis-wired in a minor way. The resistor simulating the energized indicator lamp was mis-wired to return on Circuit Path 4 rather than Circuit Path 7. This had essentially no impact on circuit response because Path 7 was still connected to the return path on the CPT. The only minor impact was to cut the base load on the circuit in the un-faulted condition in half (0.036 A versus 0.072A) This represents only a small fraction of the overall CPT power, and would have had little or no impact on circuit fault behavior.

## Circuit 1 Faulting
Summary of Observed Faulting Behavior for Circuit #1
DAQ Time | Burner Time | Event | Discussion
191 |  | Ignited Gas Burner
283 |  | Short voltage spike on Paths 5, 6 and 7 | Indicates that a momentary hot short involving one of the two source conductors occurred, although the short was of insufficient duration to trip the fuse.
284 |  | Drop in voltage on Path 4 | As noted in test conditions, Path 4 was somewhat mis-wired and was acting as a voltage divider. The conductor on Path 4 likely shorted to that on Path 7 which was grounded taking the Path 4 voltage to near zero (about 10 volts indicating a somewhat poor quality short).
312 |  | Loss of source voltage | A short between circuit Paths 1 and/or 2 to Path 7 occurs and trips the circuit fuse.
314 |  | Voltage spike on Paths 4, 6, 7 and 8 | Because the fuse for Circuit 1 had already opened, this spike had to have been caused by an intercable short circuit. The most likely source is circuit #2 which shows a concurrent source voltage drop. Note also that circuit 3 shows similar concurrent voltage spikes and that circuit 4 (the only other still-powered circuit) also shows a voltage spike well in excess of that circuits nominal voltage (172 V). This indicates that multiple concurrent inter-cable hot shorts did occur.
Summary observations |  | Test Circuit 1 experienced a momentary hot short to both targets 5 and 6 sustained for less than 0.4 s. A fuse blow occured about 29 s later. After loss of circuit power, there are clear indications of inter-cable hot shorts involving essentially all four of the circuits present with Circuit 2 acting as the likely source of these hot shorts. In the case of Circuit 1 the target conductor on Path 6 was hit. The hot short lasted about 1 s.

## Circuit 2 Faulting
Summary of Observed Faulting Behavior for Circuit #2
DAQ Time | Burner Time | Event | Discussion
283 |  | voltage/current spike to circuit paths 5, 6, 7 and 8 | Paths 5 and 6 are connected to a motor starter. The spike lasted only a single data scan (e.g., less than 0.4 seconds). The source of the spike is not apparent from the data as none of the source conductors for any of the four circuits shows a concurrent current spike. Likely the data logging missed the spike in the source conductors but caught it in the target conductors simply due to sequencing of the measurements. The spike could have come from any of the three grounded CPT circuits (2, 3 or 4).
283-312 |  | increasing voltage on Path 8 | The data show a slowly and steadily increasing voltage signal impressed on circuit path 8 (the spare conductor). This reflects a short to one of the source conductors of poor, but improving quality.
310 |  | Voltage jump on Path 5 | A spurious actuation of the motor starter on Path 5 occurs. The source appears to be the conductor on Path 1 as this conductor shows a concurrent increase in current flow (whereas Path 2 does not)
312 |  | Voltage jump on Path 8 | Indicates a hot short to the conductor on Path 8 (the spare conductor)
313 |  | voltage jump on Path 6 | Spurious actuation of the motor starter on Path 6 occurs.
314 |  | Voltage jump on Path 4 | This indicates that a hot short to the conductor on Path 4 occurred. As noted, Path 4 had been mis-wired as a voltage divider, and the spike in voltage indicates that a hot short to one of the two energizing conductors resulted in by-passing of the second resistor and application of full voltage to this circuit path.
314 |  | Momentary voltage drop on circuit source and spike in source current (Paths 1 and 2) | This appears to have been the result of inter-cable hot shorts between the various circuits, with circuit 2 acting as the energizing source. Concurrent voltage spikes are observed on both circuits 1 and 3 which had already experience fuse blows on their own CPTs. Circuit 4 also shows a concurrent spike in source voltage well above the nominal circuit voltage (172 V).
316 |  | Voltage on source conductors drops to zero | The fuse on the CPT blows open terminating the hot shorts.
Summary Observations |  | This circuit did experience spurious actuation of both motor starters. The spurious actuations lasted a total of about 6 s. It also appears that this circuit acted as the energizing source for inter-cable hot shorts to all three of the other circuits present.

## Circuit 3 Faulting
Summary of Observed Faulting Behavior for Circuit #3
DAQ Time | Burner Time | Event | Discussion
240.8 |  | Loss of circuit power | There was a short to ground apparently impacting the conductor on Path 2 (one of the two source conductors) that cause the fuse to blow and a loss of circuit power.
283.6 |  | Voltage Spike on conductors 5, 6, 7 and 8 | This is a clear indication of an intercable hot short. The hot short did impact the two target motor starters (Paths 5 and 6) but also cleared within a single scan cycle. The source of the hot short appears to have been Circuit 2.
313.8 |  | Voltage spikes on 5, 6, 7, and 8 | This is another indication of inter-cable hot shorts, in this case with Circuit 4 acting as the energizing source.
Summary Observations |  | This circuit shorted to ground causing a fuse blow. However, after the fuse blow, the circuit also experienced inter-cable hot shorts twice. In both cases, the shorts were of momentary duration. In the first case, Circuit 2 acted as the energizing source. In the second case, Circuit 4 acted as the energizing source. Both of the two active target paths were impacted (Paths 5 and 6).

## Circuit 4 Faulting
Summary of Observed Faulting Behavior for Circuit #4
DAQ Time | Burner Time | Event | Discussion
283.6 |  | Voltage spike on Paths 5,6,7 and 8 | This is an apparent intercable short to Circuit #1 as there is a matching current spike on Circuit 1 path 1
313-314 |  | Voltage spikes on various paths including target paths 5 and 6 | This is an apparent intercable short, the source appears to have been Circuit #2 as there is a corresponding current spike on Circuit 2 Path 2 which is a source conductor.
320 |  | Hot short to Path 6 | The motor starter on path 6 actuates and locks in. This appears to be an intra-cable short as there is a concurrent increase in current on both paths 1 and 2 for Circuit 4, and all other circuits had already lost power.
321.2 |  | Loss of circuit power | Shorts to ground apparently trip circuit power mitigating spurious operation of motor starter on path 6
Summary Observations |  | This was the target of two separate inter-cable hot shorts of momentary duration. It was also the apparent source of momentary inter-cable hot shorts impacting Circuit #3. Following the inter-cable interactions, the circuit experienced a spurious actuation due to intra-cable shorting on T6 that lasted 1.2 s before fuse blow.

## Converted Test Data
DAQ Time | Burner Time | C1 V1 | C1 A1 | C1 V2 | C1 A2 | C1 V3 | C1 A3 | C1 V4 | C1 A4 | C1 V5 | C1 A5 | C1 V6 | C1 A6 | C1 V7 | C1 A7 | C1 V8 | C1 A8 | C2 V1 | C2 A1 | C2 V2 | C2 A2 | C2 V3 | C2 A3 | C2 V4 | C2 A4 | C2 V5 | C2 A5 | C2 V6 | C2 A6 | C2 V7 | C2 A7 | C2 V8 | C2 A8 | C3 V1 | C3 A1 | C3 V2 | C3 A2 | C3 V3 | C3 A3 | C3 V4 | C3 A4 | C3 V5 | C3 A5 | C3 V6 | C3 A6 | C3 V7 | C3 A7 | C3 V8 | C3 A8 | C4 V1 | C4 A1 | C4 V2 | C4 A2 | C4 V3 | C4 A3 | C4 V4 | C4 A4 | C4 V5 | C4 A5 | C4 V6 | C4 A6 | C4 V7 | C4 A7 | C4 V8 | C4 A8
0 | -191 | 132.3787 | 0.046423 | 131.9783 | 0.0064758 | 0.10277 | 0.0016399 | 65.4457 | 0.036324 | 0.046856 | 0.00012922 | 0.093675 | 0.0019208 | 0.10349 | 0.0016967 | 2.7234 | 0.0019433 | 132.3278 | 0.039801 | 131.6713 | 0.0080546 | -0.0023597 | 8.4239e-05 | 65.7214 | 0.036049 | 0.01988 | 0.00064048 | 0.018196 | 0.0013085 | -0.03538 | 0.0014439 | 2.505 | 7.2982e-05 | 133.4424 | 0.040436 | 133.0416 | 0.0067236 | 0.017185 | -8.9855e-05 | 65.649 | 0.032258 | -0.019206 | -0.00011232 | 0.086261 | 0.0009884 | 0.018878 | 0.0012074 | 2.6024 | 0.0011574 | 129.2556 | 0.048575 | 129.3268 | 0.0074705 | 0.04313 | 0.00041557 | 63.8011 | 0.028764 | 0.064722 | 0.0011513 | 0.11153 | -0.00034817 | 0.030326 | -5.0495e-05 | 2.8804 | 0.0012636
60 | -131 | 131.7944 | 0.046423 | 131.394 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.8614 | 0.033078 | 0.14424 | 0.00012922 | 0.19109 | 0.00029777 | 0.10349 | 7.2991e-05 | 2.5286 | 0.0019433 | 131.6461 | 0.038178 | 130.9896 | 0.0048085 | 0.095061 | 8.4239e-05 | 65.0397 | 0.034426 | 0.01988 | 0.00064048 | 0.018196 | -0.00031449 | 0.062 | -0.00017979 | 2.3102 | 7.2982e-05 | 132.858 | 0.037189 | 132.4573 | 0.0050999 | 0.017185 | -8.9855e-05 | 65.0646 | 0.030635 | 0.078174 | -0.00011232 | -0.011119 | -0.0006346 | 0.018878 | 0.0012074 | 2.4076 | 0.0027804 | 128.7686 | 0.046952 | 128.8398 | 0.0058469 | 0.14051 | 0.00041557 | 63.2167 | 0.02714 | 0.064722 | 0.0011513 | 0.11153 | -0.00034817 | 0.12771 | 0.0015725 | 2.5883 | 0.0012636
120 | -71 | 131.5996 | 0.041554 | 131.2966 | 0.0016062 | 0.10277 | 1.6859e-05 | 64.8614 | 0.033078 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 7.2991e-05 | 2.7234 | 0.0019433 | 131.3539 | 0.031685 | 130.6974 | 0.0015619 | 0.095061 | 8.4239e-05 | 64.8449 | 0.031179 | 0.01988 | 0.00064048 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 2.2128 | 7.2982e-05 | 132.5658 | 0.032319 | 132.165 | 0.0018533 | 0.017185 | 0.0015332 | 64.8698 | 0.029011 | 0.078174 | -0.00011232 | -0.011119 | 0.0009884 | 0.018878 | -0.00041558 | 2.4076 | 0.0027804 | 128.5738 | 0.043705 | 128.5476 | 0.0026002 | 0.14051 | 0.00041557 | 63.022 | 0.02714 | 0.064722 | -0.00047174 | 0.11153 | -0.00034817 | 0.12771 | 0.0031962 | 2.5883 | 0.0012636
180 | -11 | 132.3787 | 0.046423 | 131.9783 | 0.0032298 | 0.0053935 | 1.6859e-05 | 65.0562 | 0.033078 | 0.14424 | 0.00012922 | 0.19109 | 0.00029777 | 0.10349 | 7.2991e-05 | 2.5286 | 0.00032025 | 132.2304 | 0.038178 | 131.574 | 0.0048085 | 0.095061 | 8.4239e-05 | 65.2344 | 0.032803 | 0.01988 | 0.00064048 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 2.2128 | 7.2982e-05 | 133.5397 | 0.038813 | 133.0416 | 0.0050999 | 0.017185 | -8.9855e-05 | 65.162 | 0.032258 | 0.17559 | -0.00011232 | -0.011119 | -0.0006346 | 0.018878 | -0.00041558 | 2.3102 | 0.0027804 | 129.4504 | 0.048575 | 129.5215 | 0.0058469 | 0.14051 | 0.00041557 | 63.3141 | 0.028764 | 0.1621 | -0.00047174 | 0.11153 | -0.0019718 | 0.12771 | 0.0031962 | 2.4908 | -0.0003594
185 | -6 | 132.5735 | 0.048047 | 132.1731 | 0.0048528 | 0.0053935 | 1.6859e-05 | 65.0562 | 0.033078 | 0.14424 | 0.00012922 | 0.093675 | -0.0013259 | 0.0060648 | 7.2991e-05 | 2.4312 | 0.00032025 | 132.4252 | 0.039801 | 131.7687 | 0.0064315 | 0.095061 | 8.4239e-05 | 65.3318 | 0.034426 | 0.01988 | 0.00064048 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 2.2128 | 7.2982e-05 | 133.7345 | 0.038813 | 133.2364 | 0.0067236 | -0.080196 | -8.9855e-05 | 65.2594 | 0.030635 | 0.078174 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | -0.00041558 | 2.3102 | 0.0027804 | 129.6452 | 0.048575 | 129.6189 | 0.0090935 | 0.14051 | 0.00041557 | 63.4115 | 0.028764 | 0.1621 | -0.00047174 | 0.11153 | -0.00034817 | 0.12771 | 0.0015725 | 2.3935 | -0.0003594
190 | -1 | 132.6709 | 0.048047 | 132.2706 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.033078 | 0.14424 | 0.00012922 | 0.19109 | 0.00029777 | 0.10349 | 7.2991e-05 | 2.4312 | 0.00032025 | 132.62 | 0.041425 | 131.9635 | 0.0080546 | 0.095061 | 8.4239e-05 | 65.3318 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.2568 | -0.00017979 | 2.2128 | 7.2982e-05 | 133.832 | 0.042059 | 133.4312 | 0.0083466 | 0.017185 | -8.9855e-05 | 65.3568 | 0.033881 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 2.3102 | 0.0027804 | 129.84 | 0.050198 | 129.7163 | 0.0090935 | 0.14051 | 0.00041557 | 63.5089 | 0.028764 | 0.1621 | 0.0011513 | 0.11153 | -0.00034817 | 0.22513 | 0.0048192 | 2.5883 | 0.0012636
195 | 4 | 132.6709 | 0.048047 | 132.2706 | 0.0048528 | 0.0053935 | 1.6859e-05 | 65.0562 | 0.034701 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | 2.4312 | 0.00032025 | 132.62 | 0.041425 | 131.9635 | 0.0080546 | 0.095061 | 0.0017072 | 65.3318 | 0.036049 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 2.2128 | 7.2982e-05 | 133.832 | 0.040436 | 133.3338 | 0.0083466 | 0.017185 | -8.9855e-05 | 65.2594 | 0.033881 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 2.4076 | 0.004404 | 129.1582 | 0.051821 | 129.3268 | 0.010717 | 0.14051 | 0.00041557 | 63.5089 | 0.028764 | 0.1621 | 0.0011513 | 0.11153 | 0.0012748 | 0.22513 | 0.0031962 | 2.5883 | 0.0012636
200 | 9 | 132.6709 | 0.04967 | 132.2706 | 0.0064758 | 0.0053935 | 1.6859e-05 | 65.0562 | 0.034701 | 0.14424 | 0.0017522 | 0.19109 | 0.0019208 | 0.10349 | 7.2991e-05 | 2.4312 | 0.00032025 | 132.3278 | 0.039801 | 131.7687 | 0.0080546 | 0.095061 | 8.4239e-05 | 65.2344 | 0.036049 | 0.01988 | 0.00064048 | 0.018196 | 0.0013085 | 0.15942 | 0.0014439 | 2.2128 | 7.2982e-05 | 133.6372 | 0.042059 | 133.2364 | 0.0083466 | 0.017185 | 0.0015332 | 65.2594 | 0.033881 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.21368 | 0.0012074 | 2.3102 | 0.0027804 | 129.6452 | 0.050198 | 129.6189 | 0.0090935 | 0.23793 | 0.00041557 | 63.5089 | 0.030387 | 0.1621 | 0.0011513 | 0.20895 | -0.00034817 | 0.32251 | 0.0031962 | 2.4908 | 0.0012636
201 | 10 | 132.7683 | 0.04967 | 132.2706 | 0.0064758 | 0.0053935 | 1.6859e-05 | 65.0562 | 0.036324 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 7.2991e-05 | 2.4312 | 0.00032025 | 132.3278 | 0.039801 | 131.8661 | 0.0080546 | 0.095061 | 8.4239e-05 | 65.2344 | 0.036049 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | 0.0014439 | 2.2128 | 7.2982e-05 | 133.832 | 0.042059 | 133.3338 | 0.0083466 | 0.017185 | -8.9855e-05 | 65.3568 | 0.032258 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 2.4076 | 0.004404 | 129.7426 | 0.050198 | 129.7163 | 0.0090935 | 0.23793 | 0.00041557 | 63.4115 | 0.028764 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 2.5883 | 0.0012636
202 | 11 | 132.8657 | 0.04967 | 132.2706 | 0.0064758 | 0.10277 | 1.6859e-05 | 65.0562 | 0.034701 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | 2.4312 | 0.0019433 | 131.9382 | 0.041425 | 131.6713 | 0.0080546 | 0.095061 | 8.4239e-05 | 65.2344 | 0.036049 | 0.01988 | 0.00064048 | 0.018196 | 0.0013085 | 0.15942 | 0.0014439 | 2.3102 | 7.2982e-05 | 133.7345 | 0.042059 | 133.3338 | 0.0083466 | -0.080196 | -8.9855e-05 | 65.3568 | 0.033881 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 2.4076 | 0.004404 | 129.6452 | 0.050198 | 129.6189 | 0.0090935 | 0.23793 | 0.00041557 | 63.5089 | 0.030387 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 2.5883 | -0.0003594
203 | 12 | 132.9631 | 0.04967 | 132.2706 | 0.0064758 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.034701 | 0.14424 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | 2.4312 | 0.00032025 | 131.8409 | 0.041425 | 131.7687 | 0.0080546 | 0.095061 | 8.4239e-05 | 65.3318 | 0.036049 | 0.01988 | 0.00064048 | 0.018196 | 0.0013085 | 0.15942 | -0.00017979 | 2.2128 | 7.2982e-05 | 133.7345 | 0.042059 | 133.3338 | 0.0083466 | 0.017185 | -8.9855e-05 | 65.3568 | 0.033881 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.21368 | 0.0012074 | 2.3102 | 0.004404 | 129.6452 | 0.050198 | 129.7163 | 0.0090935 | 0.14051 | 0.00041557 | 63.5089 | 0.030387 | 0.1621 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 2.4908 | 0.0012636
204 | 13 | 132.9631 | 0.04967 | 132.1731 | 0.0064758 | 0.0053935 | 1.6859e-05 | 64.5692 | 0.034701 | 0.14424 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | 2.4312 | 0.00032025 | 132.2304 | 0.041425 | 131.7687 | 0.0096782 | 0.19244 | 8.4239e-05 | 65.3318 | 0.036049 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | 0.0014439 | 2.2128 | 7.2982e-05 | 133.7345 | 0.040436 | 133.2364 | 0.0083466 | 0.017185 | -8.9855e-05 | 65.2594 | 0.033881 | 0.17559 | 0.0015107 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 2.4076 | 0.004404 | 129.6452 | 0.050198 | 129.6189 | 0.0090935 | 0.23793 | 0.00041557 | 63.4115 | 0.030387 | 0.25952 | 0.0011513 | 0.11153 | 0.0012748 | 0.22513 | 0.0031962 | 2.4908 | 0.0012636
205 | 14 | 133.1579 | 0.048047 | 131.9783 | 0.0048528 | 0.0053935 | 0.0016399 | 64.4718 | 0.034701 | 0.14424 | 0.0017522 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | 2.4312 | 0.00032025 | 132.5226 | 0.041425 | 131.8661 | 0.0080546 | 0.19244 | 8.4239e-05 | 65.3318 | 0.036049 | 0.01988 | 0.00064048 | 0.018196 | 0.0013085 | 0.15942 | -0.00017979 | 2.2128 | 7.2982e-05 | 133.9293 | 0.042059 | 133.4312 | 0.0083466 | 0.017185 | -8.9855e-05 | 65.3568 | 0.032258 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 2.4076 | 0.004404 | 129.7426 | 0.050198 | 129.7163 | 0.0090935 | 0.23793 | 0.00041557 | 63.5089 | 0.030387 | 0.1621 | 0.0011513 | 0.20895 | 0.0012748 | 0.22513 | 0.0031962 | 2.5883 | 0.0012636
206 | 15 | 133.7423 | 0.04967 | 131.9783 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.8614 | 0.034701 | 0.24166 | 0.00012922 | 0.19109 | 0.00029777 | 0.10349 | 7.2991e-05 | 2.4312 | 0.0019433 | 132.5226 | 0.039801 | 131.8661 | 0.0080546 | 0.19244 | 8.4239e-05 | 65.3318 | 0.036049 | 0.01988 | 0.00064048 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 2.3102 | 7.2982e-05 | 133.7345 | 0.040436 | 133.2364 | 0.0083466 | 0.017185 | 0.0015332 | 65.3568 | 0.033881 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 2.4076 | 0.004404 | 129.6452 | 0.050198 | 129.6189 | 0.0090935 | 0.23793 | 0.00041557 | 63.4115 | 0.030387 | 0.1621 | 0.0011513 | 0.11153 | 0.0012748 | 0.22513 | 0.0031962 | 2.5883 | 0.0012636
207 | 16 | 132.7683 | 0.04967 | 132.1731 | 0.0064758 | 0.0053935 | 1.6859e-05 | 65.0562 | 0.034701 | 0.14424 | 0.00012922 | 0.28848 | 0.0019208 | 0.10349 | 0.0016967 | 2.4312 | 0.00032025 | 132.5226 | 0.041425 | 131.8661 | 0.0080546 | 0.19244 | 8.4239e-05 | 65.3318 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 2.2128 | 7.2982e-05 | 133.832 | 0.040436 | 133.3338 | 0.0083466 | 0.017185 | -8.9855e-05 | 65.3568 | 0.032258 | 0.17559 | 0.0015107 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 2.4076 | 0.004404 | 129.6452 | 0.050198 | 129.7163 | 0.0090935 | 0.23793 | 0.00041557 | 63.5089 | 0.030387 | 0.1621 | 0.0011513 | 0.11153 | -0.00034817 | 0.22513 | 0.0031962 | 2.5883 | 0.0012636
208 | 17 | 132.5735 | 0.048047 | 132.2706 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.034701 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | 2.4312 | 0.0019433 | 132.5226 | 0.039801 | 131.8661 | 0.0080546 | 0.095061 | 8.4239e-05 | 65.3318 | 0.036049 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | 0.0014439 | 2.2128 | 7.2982e-05 | 133.832 | 0.042059 | 133.3338 | 0.0067236 | 0.017185 | -8.9855e-05 | 65.2594 | 0.032258 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.21368 | 0.0012074 | 2.4076 | 0.004404 | 129.6452 | 0.050198 | 129.6189 | 0.010717 | 0.23793 | 0.00041557 | 63.4115 | 0.030387 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748 | 0.22513 | 0.0031962 | 2.5883 | 0.0012636
209 | 18 | 132.6709 | 0.04967 | 132.2706 | 0.0064758 | 0.0053935 | 1.6859e-05 | 65.0562 | 0.034701 | 0.14424 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 7.2991e-05 | 2.5286 | 0.00032025 | 132.5226 | 0.041425 | 131.9635 | 0.0080546 | 0.095061 | 8.4239e-05 | 65.3318 | 0.036049 | 0.01988 | 0.00064048 | 0.018196 | 0.0013085 | 0.15942 | -0.00017979 | 2.2128 | 7.2982e-05 | 133.832 | 0.042059 | 133.3338 | 0.0083466 | -0.080196 | -8.9855e-05 | 65.3568 | 0.033881 | 0.17559 | 0.0015107 | -0.011119 | 0.0009884 | 0.21368 | -0.00041558 | 2.4076 | 0.004404 | 129.7426 | 0.050198 | 129.7163 | 0.0090935 | 0.23793 | 0.00041557 | 63.5089 | 0.030387 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 2.4908 | 0.0012636
210 | 19 | 132.5735 | 0.04967 | 132.1731 | 0.0048528 | 0.0053935 | 1.6859e-05 | 65.0562 | 0.034701 | 0.24166 | 0.0017522 | 0.19109 | 0.00029777 | 0.10349 | 7.2991e-05 | 2.4312 | 0.0019433 | 132.5226 | 0.041425 | 131.8661 | 0.0080546 | 0.19244 | 8.4239e-05 | 65.3318 | 0.034426 | 0.01988 | 0.00064048 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 2.2128 | 7.2982e-05 | 133.7345 | 0.042059 | 133.2364 | 0.0083466 | 0.017185 | -8.9855e-05 | 65.3568 | 0.033881 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 2.4076 | 0.004404 | 129.6452 | 0.050198 | 129.6189 | 0.0090935 | 0.23793 | 0.00041557 | 63.4115 | 0.028764 | 0.1621 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 2.4908 | 0.0012636
211 | 20 | 132.5735 | 0.048047 | 132.1731 | 0.0064758 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.034701 | 0.14424 | 0.00012922 | 0.28848 | 0.0019208 | 0.20087 | 7.2991e-05 | 2.5286 | 0.00032025 | 132.5226 | 0.041425 | 131.7687 | 0.0080546 | 0.095061 | 8.4239e-05 | 65.3318 | 0.036049 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 2.2128 | 7.2982e-05 | 133.7345 | 0.042059 | 133.2364 | 0.0083466 | 0.017185 | -8.9855e-05 | 65.2594 | 0.032258 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | -0.00041558 | 2.4076 | 0.004404 | 129.5478 | 0.050198 | 129.6189 | 0.0090935 | 0.23793 | 0.00041557 | 63.4115 | 0.028764 | 0.1621 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 2.5883 | 0.0012636
212 | 21 | 132.4761 | 0.048047 | 132.0758 | 0.0048528 | -0.092027 | 1.6859e-05 | 64.9588 | 0.034701 | 0.14424 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | 2.5286 | 0.00032025 | 132.3278 | 0.041425 | 131.7687 | 0.0080546 | 0.19244 | 8.4239e-05 | 65.137 | 0.036049 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | 0.0014439 | 2.2128 | 7.2982e-05 | 133.6372 | 0.042059 | 133.1391 | 0.0067236 | 0.017185 | -8.9855e-05 | 65.2594 | 0.032258 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.21368 | 0.0012074 | 2.4076 | 0.004404 | 129.4504 | 0.050198 | 129.5215 | 0.0090935 | 0.23793 | 0.00041557 | 63.4115 | 0.028764 | 0.1621 | 0.0011513 | 0.11153 | 0.0012748 | 0.22513 | 0.0031962 | 2.5883 | 0.0012636
213 | 22 | 132.4761 | 0.04967 | 132.1731 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.034701 | 0.14424 | 0.00012922 | 0.19109 | 0.00029777 | 0.10349 | 0.0016967 | 2.4312 | 0.0019433 | 132.4252 | 0.041425 | 131.7687 | 0.0080546 | 0.19244 | 8.4239e-05 | 65.2344 | 0.036049 | 0.01988 | 0.00064048 | 0.018196 | 0.0013085 | 0.15942 | 0.0014439 | 2.3102 | 7.2982e-05 | 133.6372 | 0.040436 | 133.2364 | 0.0067236 | -0.080196 | -8.9855e-05 | 65.2594 | 0.032258 | 0.17559 | 0.0015107 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 2.4076 | 0.004404 | 129.5478 | 0.050198 | 129.5215 | 0.0090935 | 0.23793 | 0.00041557 | 63.4115 | 0.030387 | 0.1621 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 2.5883 | 0.0012636
214 | 23 | 132.4761 | 0.04967 | 132.0758 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.034701 | 0.14424 | 0.00012922 | 0.19109 | 0.00029777 | 0.10349 | 0.0016967 | 2.5286 | 0.00032025 | 132.4252 | 0.039801 | 131.6713 | 0.0080546 | 0.095061 | 8.4239e-05 | 65.3318 | 0.036049 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 2.3102 | 7.2982e-05 | 133.6372 | 0.040436 | 133.1391 | 0.0083466 | 0.017185 | 0.0015332 | 65.162 | 0.033881 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 2.4076 | 0.004404 | 129.5478 | 0.050198 | 129.4241 | 0.0090935 | 0.14051 | 0.00041557 | 63.4115 | 0.030387 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748 | 0.22513 | 0.0031962 | 2.5883 | 0.0012636
215 | 24 | 132.4761 | 0.048047 | 132.1731 | 0.0048528 | 0.0053935 | 1.6859e-05 | 65.0562 | 0.034701 | 0.14424 | 0.00012922 | 0.19109 | 0.00029777 | 0.10349 | 7.2991e-05 | 2.5286 | 0.00032025 | 132.3278 | 0.039801 | 131.7687 | 0.0080546 | 0.095061 | 8.4239e-05 | 65.3318 | 0.036049 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | -0.00017979 | 2.3102 | 0.0016967 | 133.6372 | 0.042059 | 133.1391 | 0.0083466 | 0.017185 | -8.9855e-05 | 65.2594 | 0.033881 | 0.17559 | 0.0015107 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 2.4076 | 0.004404 | 129.5478 | 0.048575 | 129.5215 | 0.0090935 | 0.23793 | -0.0012074 | 63.4115 | 0.028764 | 0.1621 | 0.0011513 | 0.11153 | 0.0012748 | 0.22513 | 0.0031962 | 2.5883 | 0.0012636
216 | 25 | 132.4761 | 0.04967 | 132.0758 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.034701 | 0.24166 | 0.00012922 | 0.19109 | 0.00029777 | 0.20087 | 0.0016967 | 2.5286 | 0.0019433 | 132.3278 | 0.039801 | 131.6713 | 0.0080546 | 0.19244 | 8.4239e-05 | 65.2344 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.062 | 0.0014439 | 2.2128 | 7.2982e-05 | 133.6372 | 0.040436 | 133.1391 | 0.0067236 | 0.017185 | -8.9855e-05 | 65.162 | 0.032258 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 2.4076 | 0.004404 | 129.4504 | 0.050198 | 129.4241 | 0.0090935 | 0.14051 | 0.00041557 | 63.4115 | 0.028764 | 0.1621 | 0.0011513 | 0.11153 | 0.0012748 | 0.22513 | 0.0031962 | 2.4908 | -0.0003594
217 | 26 | 132.4761 | 0.048047 | 132.0758 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.034701 | 0.14424 | 0.00012922 | 0.28848 | 0.0019208 | 0.10349 | 0.0016967 | 2.5286 | 0.00032025 | 132.3278 | 0.039801 | 131.6713 | 0.0080546 | 0.19244 | 8.4239e-05 | 65.2344 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.2568 | -0.00017979 | 2.2128 | 7.2982e-05 | 133.6372 | 0.040436 | 133.1391 | 0.0067236 | 0.017185 | -8.9855e-05 | 65.162 | 0.032258 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 2.4076 | 0.004404 | 129.4504 | 0.048575 | 129.4241 | 0.0074705 | 0.14051 | 0.00041557 | 63.4115 | 0.028764 | 0.1621 | 0.0011513 | 0.11153 | 0.0012748 | 0.12771 | 0.0031962 | 2.5883 | 0.0012636
218 | 27 | 132.4761 | 0.048047 | 132.0758 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.034701 | 0.24166 | 0.00012922 | 0.19109 | 0.00029777 | 0.10349 | 7.2991e-05 | 2.5286 | 0.00032025 | 132.3278 | 0.039801 | 131.6713 | 0.0080546 | 0.19244 | 8.4239e-05 | 65.2344 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 2.3102 | 7.2982e-05 | 133.5397 | 0.040436 | 133.1391 | 0.0067236 | 0.017185 | -8.9855e-05 | 65.2594 | 0.032258 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 2.4076 | 0.004404 | 129.5478 | 0.048575 | 129.4241 | 0.0090935 | 0.23793 | 0.00041557 | 63.4115 | 0.028764 | 0.1621 | -0.00047174 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 2.5883 | -0.0003594
219 | 28 | 132.4761 | 0.04967 | 132.0758 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.8614 | 0.034701 | 0.14424 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | 2.5286 | 0.00032025 | 132.3278 | 0.039801 | 131.6713 | 0.0064315 | 0.19244 | 8.4239e-05 | 65.2344 | 0.036049 | -0.0775 | 0.00064048 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 2.3102 | 7.2982e-05 | 133.6372 | 0.040436 | 133.0416 | 0.0067236 | 0.017185 | -8.9855e-05 | 65.162 | 0.032258 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 2.4076 | 0.004404 | 129.4504 | 0.048575 | 129.4241 | 0.0074705 | 0.23793 | 0.00041557 | 63.3141 | 0.028764 | 0.1621 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0015725 | 2.5883 | 0.0012636
220 | 29 | 132.3787 | 0.04967 | 131.9783 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.034701 | 0.24166 | 0.00012922 | 0.19109 | 0.00029777 | 0.20087 | 0.0016967 | 2.5286 | 0.00032025 | 132.2304 | 0.038178 | 131.574 | 0.0080546 | 0.095061 | 8.4239e-05 | 65.137 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 2.2128 | 7.2982e-05 | 133.5397 | 0.040436 | 133.0416 | 0.0067236 | 0.017185 | -8.9855e-05 | 65.162 | 0.032258 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 2.505 | 0.0027804 | 129.353 | 0.048575 | 129.4241 | 0.0074705 | 0.14051 | 0.00041557 | 63.3141 | 0.028764 | 0.1621 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 2.5883 | 0.0012636
221 | 30 | 132.4761 | 0.048047 | 132.0758 | 0.0048528 | 0.0053935 | 1.6859e-05 | 65.0562 | 0.034701 | 0.24166 | 0.0017522 | 0.19109 | 0.00029777 | 0.10349 | 7.2991e-05 | 2.626 | 0.0019433 | 132.3278 | 0.039801 | 131.6713 | 0.0080546 | 0.19244 | -0.0015388 | 65.2344 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | -0.00017979 | 2.2128 | 7.2982e-05 | 133.6372 | 0.040436 | 133.0416 | 0.0067236 | 0.017185 | -8.9855e-05 | 65.162 | 0.033881 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 2.505 | 0.0027804 | 129.4504 | 0.046952 | 129.5215 | 0.0074705 | 0.23793 | 0.00041557 | 63.4115 | 0.028764 | 0.1621 | 0.0011513 | 0.20895 | 0.0012748 | 0.22513 | 0.0031962 | 2.5883 | 0.0012636
222 | 31 | 132.3787 | 0.048047 | 131.9783 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.8614 | 0.034701 | 0.14424 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | 2.626 | 0.00032025 | 132.3278 | 0.038178 | 131.574 | 0.0064315 | 0.19244 | 8.4239e-05 | 65.2344 | 0.034426 | 0.01988 | 0.00064048 | 0.018196 | 0.0013085 | 0.15942 | 0.0014439 | 2.2128 | 7.2982e-05 | 133.5397 | 0.038813 | 132.9443 | 0.0050999 | -0.080196 | -8.9855e-05 | 65.162 | 0.032258 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 2.505 | 0.004404 | 129.353 | 0.046952 | 129.3268 | 0.0058469 | 0.14051 | 0.00041557 | 63.3141 | 0.028764 | 0.1621 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 2.5883 | 0.0012636
223 | 32 | 132.4761 | 0.048047 | 132.0758 | 0.0048528 | 0.10277 | 1.6859e-05 | 64.9588 | 0.034701 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | 2.626 | 0.00032025 | 132.3278 | 0.038178 | 131.6713 | 0.0064315 | 0.19244 | 8.4239e-05 | 65.2344 | 0.034426 | 0.01988 | 0.00064048 | 0.11562 | 0.0013085 | 0.15942 | 0.0014439 | 2.3102 | 0.0016967 | 133.5397 | 0.038813 | 133.0416 | 0.0050999 | 0.017185 | -8.9855e-05 | 65.162 | 0.032258 | 0.17559 | -0.00011232 | -0.011119 | -0.0006346 | 0.11626 | 0.0012074 | 2.505 | 0.004404 | 129.4504 | 0.046952 | 129.4241 | 0.0058469 | 0.23793 | 0.00041557 | 63.3141 | 0.02714 | 0.1621 | 0.0011513 | 0.20895 | 0.0012748 | 0.22513 | 0.0031962 | 2.5883 | 0.0012636
224 | 33 | 132.3787 | 0.048047 | 131.9783 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.034701 | 0.14424 | 0.00012922 | 0.19109 | 0.00029777 | 0.10349 | 0.0016967 | 2.626 | 0.00032025 | 132.2304 | 0.038178 | 131.574 | 0.0048085 | 0.19244 | 8.4239e-05 | 65.137 | 0.034426 | 0.01988 | 0.00064048 | 0.018196 | 0.0013085 | 0.15942 | -0.00017979 | 2.3102 | 7.2982e-05 | 133.5397 | 0.038813 | 132.9443 | 0.0050999 | 0.017185 | -8.9855e-05 | 65.162 | 0.032258 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 2.505 | 0.0027804 | 129.2556 | 0.046952 | 129.3268 | 0.0058469 | 0.14051 | 0.00041557 | 63.3141 | 0.02714 | 0.1621 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 2.5883 | 0.0012636
225 | 34 | 132.2813 | 0.048047 | 131.9783 | 0.0048528 | 0.0053935 | 0.0016399 | 64.9588 | 0.034701 | 0.14424 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | 2.626 | 0.00032025 | 132.133 | 0.038178 | 131.574 | 0.0064315 | 0.19244 | 8.4239e-05 | 65.137 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | -0.00017979 | 2.3102 | 7.2982e-05 | 133.5397 | 0.038813 | 133.0416 | 0.0050999 | 0.017185 | -8.9855e-05 | 65.162 | 0.032258 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 2.505 | 0.0027804 | 129.353 | 0.046952 | 129.3268 | 0.0058469 | 0.23793 | 0.00041557 | 63.3141 | 0.028764 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 2.6856 | 0.0012636
226 | 35 | 132.2813 | 0.048047 | 131.9783 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.033078 | 0.14424 | 0.00012922 | 0.19109 | 0.00029777 | 0.10349 | 0.0016967 | 2.7234 | 0.00032025 | 132.133 | 0.038178 | 131.4765 | 0.0064315 | 0.095061 | 8.4239e-05 | 65.137 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | -0.00017979 | 2.4076 | 7.2982e-05 | 133.4424 | 0.038813 | 132.9443 | 0.0050999 | 0.017185 | -8.9855e-05 | 65.162 | 0.032258 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.11626 | -0.00041558 | 2.6024 | 0.0027804 | 129.2556 | 0.048575 | 129.3268 | 0.0074705 | 0.23793 | 0.00041557 | 63.2167 | 0.028764 | 0.1621 | -0.00047174 | 0.11153 | -0.00034817 | 0.22513 | 0.0031962 | 2.6856 | 0.0012636
227 | 36 | 132.3787 | 0.048047 | 131.9783 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.8614 | 0.034701 | 0.14424 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | 2.7234 | 0.00032025 | 132.2304 | 0.038178 | 131.574 | 0.0064315 | 0.095061 | 8.4239e-05 | 65.137 | 0.034426 | 0.01988 | 0.00064048 | -0.079185 | 0.0013085 | 0.15942 | -0.00017979 | 2.3102 | 7.2982e-05 | 133.4424 | 0.038813 | 132.9443 | 0.0050999 | -0.080196 | -8.9855e-05 | 65.162 | 0.032258 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 2.6024 | 0.004404 | 129.353 | 0.048575 | 129.3268 | 0.0058469 | 0.14051 | 0.00041557 | 63.2167 | 0.02714 | 0.1621 | 0.0011513 | 0.11153 | 0.0012748 | 0.22513 | 0.0031962 | 2.6856 | 0.0012636
228 | 37 | 132.2813 | 0.048047 | 131.881 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.033078 | 0.14424 | 0.00012922 | 0.19109 | 0.00029777 | 0.10349 | 7.2991e-05 | 2.8208 | 0.00032025 | 132.133 | 0.038178 | 131.4765 | 0.0048085 | 0.095061 | 8.4239e-05 | 65.137 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | -0.00017979 | 2.3102 | 7.2982e-05 | 133.345 | 0.038813 | 132.8468 | 0.0050999 | 0.017185 | -8.9855e-05 | 65.0646 | 0.032258 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 2.6024 | 0.004404 | 129.1582 | 0.048575 | 129.2293 | 0.0058469 | 0.23793 | 0.00041557 | 63.2167 | 0.02714 | 0.1621 | 0.0011513 | 0.11153 | 0.0012748 | 0.22513 | 0.0031962 | 2.6856 | 0.0012636
229 | 38 | 132.2813 | 0.046423 | 131.9783 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.034701 | 0.14424 | 0.00012922 | 0.19109 | 0.00029777 | 0.10349 | 0.0016967 | 2.7234 | 0.0019433 | 132.133 | 0.036554 | 131.4765 | 0.0048085 | 0.19244 | 8.4239e-05 | 65.137 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | 0.0014439 | 2.3102 | 0.0016967 | 133.4424 | 0.038813 | 132.9443 | 0.0050999 | 0.017185 | -8.9855e-05 | 65.162 | 0.032258 | 0.17559 | 0.0015107 | -0.011119 | -0.0006346 | 0.11626 | 0.0012074 | 2.6024 | 0.0027804 | 129.2556 | 0.045329 | 129.3268 | 0.0058469 | 0.23793 | 0.00041557 | 63.3141 | 0.02714 | 0.1621 | 0.0011513 | 0.20895 | 0.0012748 | 0.22513 | 0.0031962 | 2.6856 | 0.0012636
230 | 39 | 132.2813 | 0.046423 | 131.9783 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.8614 | 0.034701 | 0.14424 | 0.00012922 | 0.19109 | 0.0019208 | 0.10349 | 0.0016967 | 2.7234 | 0.00032025 | 132.133 | 0.038178 | 131.574 | 0.0048085 | 0.095061 | 0.0017072 | 65.137 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 2.4076 | 7.2982e-05 | 133.4424 | 0.037189 | 132.8468 | 0.0050999 | -0.080196 | 0.0015332 | 65.162 | 0.032258 | 0.17559 | 0.0015107 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 2.6998 | 0.004404 | 129.2556 | 0.046952 | 129.2293 | 0.0058469 | 0.23793 | 0.00041557 | 63.3141 | 0.02714 | 0.1621 | 0.0011513 | 0.11153 | 0.0012748 | 0.22513 | 0.0031962 | 2.5883 | 0.0012636
230.2 | 39.2 | 132.3787 | 0.046423 | 131.9783 | 0.0032298 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.034701 | 0.14424 | 0.00012922 | 0.19109 | 0.00029777 | 0.20087 | 0.0016967 | 2.7234 | 0.00032025 | 132.133 | 0.038178 | 131.574 | 0.0048085 | 0.19244 | 8.4239e-05 | 65.137 | 0.034426 | 0.01988 | 0.00064048 | 0.018196 | 0.0013085 | 0.15942 | -0.00017979 | 2.4076 | 7.2982e-05 | 133.4424 | 0.038813 | 132.9443 | 0.0050999 | 0.017185 | -8.9855e-05 | 65.162 | 0.032258 | 0.17559 | 0.0015107 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 2.6998 | 0.004404 | 129.353 | 0.046952 | 129.3268 | 0.0058469 | 0.23793 | 0.00041557 | 63.3141 | 0.02714 | 0.1621 | 0.0011513 | 0.20895 | 0.0012748 | 0.22513 | 0.0031962 | 2.6856 | 0.0012636
230.4 | 39.4 | 132.3787 | 0.048047 | 131.881 | 0.0032298 | 0.10277 | 1.6859e-05 | 64.9588 | 0.033078 | 0.24166 | 0.00012922 | 0.19109 | 0.00029777 | 0.10349 | 7.2991e-05 | 2.7234 | 0.00032025 | 132.133 | 0.038178 | 131.4765 | 0.0048085 | 0.19244 | 8.4239e-05 | 65.137 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | -0.00017979 | 2.4076 | 7.2982e-05 | 133.4424 | 0.038813 | 132.9443 | 0.0050999 | 0.017185 | -8.9855e-05 | 65.162 | 0.032258 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 2.6024 | 0.004404 | 129.353 | 0.046952 | 129.3268 | 0.0058469 | 0.14051 | 0.00041557 | 63.3141 | 0.02714 | 0.25952 | -0.00047174 | 0.11153 | 0.0012748 | 0.32251 | 0.0048192 | 2.5883 | 0.0012636
230.6 | 39.6 | 132.2813 | 0.048047 | 131.9783 | 0.0032298 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.033078 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.0060648 | 0.0016967 | 2.8208 | 0.0019433 | 132.133 | 0.038178 | 131.4765 | 0.0048085 | 0.19244 | 8.4239e-05 | 65.137 | 0.034426 | 0.01988 | 0.00064048 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 2.4076 | 7.2982e-05 | 133.345 | 0.038813 | 132.9443 | 0.0050999 | 0.017185 | -8.9855e-05 | 65.162 | 0.032258 | 0.17559 | 0.0015107 | -0.011119 | 0.0009884 | 0.11626 | -0.00041558 | 2.6024 | 0.004404 | 129.2556 | 0.046952 | 129.3268 | 0.0058469 | 0.23793 | 0.00041557 | 63.2167 | 0.028764 | 0.1621 | -0.00047174 | 0.20895 | 0.0012748 | 0.22513 | 0.0031962 | 2.6856 | 0.0012636
230.8 | 39.8 | 132.3787 | 0.048047 | 131.9783 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.034701 | 0.24166 | 0.0017522 | 0.19109 | 0.00029777 | 0.10349 | 0.0016967 | 2.8208 | 0.00032025 | 132.2304 | 0.038178 | 131.574 | 0.0064315 | 0.19244 | 8.4239e-05 | 65.137 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 2.4076 | 7.2982e-05 | 133.4424 | 0.038813 | 132.9443 | 0.0050999 | 0.017185 | -8.9855e-05 | 65.162 | 0.032258 | 0.27297 | 0.0015107 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 2.6998 | 0.004404 | 129.2556 | 0.046952 | 129.3268 | 0.0058469 | 0.23793 | -0.0012074 | 63.2167 | 0.02714 | 0.1621 | 0.0011513 | 0.11153 | 0.0012748 | 0.22513 | 0.0031962 | 2.6856 | 0.0012636
231 | 40 | 132.2813 | 0.046423 | 131.881 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.034701 | 0.24166 | 0.00012922 | 0.28848 | -0.0013259 | 0.10349 | 0.0016967 | 2.7234 | 0.00032025 | 132.133 | 0.038178 | 131.4765 | 0.0064315 | 0.095061 | 8.4239e-05 | 65.137 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | 0.0014439 | 2.4076 | 0.0016967 | 133.4424 | 0.038813 | 132.9443 | 0.0050999 | 0.017185 | 0.0015332 | 65.162 | 0.032258 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 2.6024 | 0.0027804 | 129.2556 | 0.045329 | 129.2293 | 0.0042238 | 0.23793 | 0.00041557 | 63.3141 | 0.02714 | 0.1621 | 0.0011513 | 0.11153 | 0.0012748 | 0.22513 | 0.0031962 | 2.6856 | 0.0012636
231.2 | 40.2 | 132.3787 | 0.048047 | 131.9783 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.034701 | 0.14424 | 0.00012922 | 0.19109 | 0.0019208 | 0.10349 | 7.2991e-05 | 2.7234 | 0.00032025 | 132.133 | 0.038178 | 131.574 | 0.0048085 | 0.19244 | 8.4239e-05 | 65.137 | 0.034426 | 0.01988 | 0.00064048 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 2.4076 | 7.2982e-05 | 133.4424 | 0.038813 | 132.9443 | 0.0050999 | 0.017185 | -8.9855e-05 | 65.162 | 0.032258 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 2.6024 | 0.004404 | 129.353 | 0.045329 | 129.3268 | 0.0058469 | 0.23793 | 0.00041557 | 63.3141 | 0.02714 | 0.1621 | -0.00047174 | 0.20895 | 0.0012748 | 0.22513 | 0.0031962 | 2.6856 | 0.0012636
231.4 | 40.4 | 132.2813 | 0.046423 | 131.9783 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.033078 | 0.24166 | 0.00012922 | 0.19109 | 0.00029777 | 0.10349 | 0.0016967 | 2.8208 | 0.00032025 | 132.133 | 0.038178 | 131.574 | 0.0064315 | 0.19244 | 0.0017072 | 65.137 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.062 | 0.0014439 | 2.4076 | 0.0016967 | 133.4424 | 0.038813 | 132.9443 | 0.0034769 | -0.080196 | -8.9855e-05 | 65.162 | 0.032258 | 0.17559 | -0.00011232 | 0.086261 | -0.0006346 | 0.11626 | 0.0012074 | 2.6998 | 0.0027804 | 129.2556 | 0.045329 | 129.3268 | 0.0058469 | 0.23793 | 0.00041557 | 63.3141 | 0.02714 | 0.1621 | -0.00047174 | 0.20895 | 0.0012748 | 0.22513 | 0.0031962 | 2.6856 | 0.0012636
231.6 | 40.6 | 132.2813 | 0.046423 | 131.9783 | 0.0032298 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.034701 | 0.14424 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | 2.8208 | 0.00032025 | 132.133 | 0.038178 | 131.574 | 0.0048085 | 0.19244 | 8.4239e-05 | 65.137 | 0.032803 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | -0.00017979 | 2.4076 | 7.2982e-05 | 133.4424 | 0.038813 | 132.9443 | 0.0034769 | -0.080196 | -8.9855e-05 | 65.162 | 0.032258 | 0.17559 | -0.00011232 | -0.011119 | -0.0006346 | 0.11626 | 0.0012074 | 2.6024 | 0.004404 | 129.353 | 0.045329 | 129.3268 | 0.0058469 | 0.23793 | 0.00041557 | 63.3141 | 0.02714 | 0.1621 | 0.0011513 | 0.20895 | 0.0012748 | 0.22513 | 0.0031962 | 2.6856 | 0.0012636
231.8 | 40.8 | 132.3787 | 0.046423 | 131.9783 | 0.0032298 | 0.0053935 | 0.0016399 | 64.9588 | 0.034701 | 0.14424 | 0.00012922 | 0.19109 | 0.0019208 | 0.10349 | 7.2991e-05 | 2.8208 | 0.00032025 | 132.133 | 0.038178 | 131.4765 | 0.0064315 | 0.095061 | 8.4239e-05 | 65.137 | 0.034426 | 0.01988 | 0.0022635 | 0.11562 | -0.00031449 | 0.15942 | 0.0014439 | 2.4076 | 7.2982e-05 | 133.4424 | 0.038813 | 133.0416 | 0.0050999 | -0.080196 | 0.0015332 | 65.162 | 0.032258 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 2.6998 | 0.004404 | 129.353 | 0.045329 | 129.3268 | 0.0058469 | 0.23793 | 0.00041557 | 63.3141 | 0.02714 | 0.1621 | 0.0011513 | 0.11153 | -0.00034817 | 0.22513 | 0.0031962 | 2.6856 | -0.0003594
232 | 41 | 132.3787 | 0.046423 | 131.881 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.033078 | 0.24166 | 0.00012922 | 0.19109 | 0.00029777 | 0.10349 | 0.0016967 | 2.8208 | 0.00032025 | 132.133 | 0.038178 | 131.574 | 0.0048085 | 0.095061 | 8.4239e-05 | 65.137 | 0.032803 | 0.01988 | 0.00064048 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 2.4076 | 7.2982e-05 | 133.4424 | 0.038813 | 132.8468 | 0.0050999 | 0.017185 | -8.9855e-05 | 65.0646 | 0.030635 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 2.6024 | 0.004404 | 129.2556 | 0.045329 | 129.2293 | 0.0058469 | 0.14051 | 0.00041557 | 63.3141 | 0.02714 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748 | 0.22513 | 0.0031962 | 2.6856 | 0.0012636
232.2 | 41.2 | 132.3787 | 0.048047 | 131.9783 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.034701 | 0.14424 | 0.00012922 | 0.19109 | 0.00029777 | 0.10349 | 0.0016967 | 2.8208 | 0.00032025 | 132.2304 | 0.036554 | 131.574 | 0.0048085 | 0.19244 | 8.4239e-05 | 65.137 | 0.034426 | 0.01988 | 0.00064048 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 2.4076 | 7.2982e-05 | 133.4424 | 0.038813 | 132.9443 | 0.0050999 | -0.080196 | 0.0015332 | 65.162 | 0.032258 | 0.27297 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 2.6024 | 0.004404 | 129.353 | 0.045329 | 129.3268 | 0.0058469 | 0.23793 | 0.00041557 | 63.3141 | 0.02714 | 0.1621 | -0.00047174 | 0.20895 | 0.0012748 | 0.22513 | 0.0031962 | 2.6856 | -0.0003594
232.4 | 41.4 | 132.3787 | 0.048047 | 131.9783 | 0.0032298 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.033078 | 0.24166 | 0.00012922 | 0.19109 | 0.00029777 | 0.20087 | 0.0016967 | 2.8208 | 0.00032025 | 132.133 | 0.038178 | 131.574 | 0.0048085 | 0.19244 | 8.4239e-05 | 65.137 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 2.4076 | 0.0016967 | 133.4424 | 0.038813 | 132.9443 | 0.0050999 | 0.017185 | -8.9855e-05 | 65.162 | 0.032258 | 0.17559 | 0.0015107 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 2.6998 | 0.004404 | 129.2556 | 0.045329 | 129.3268 | 0.0058469 | 0.14051 | 0.00041557 | 63.3141 | 0.02714 | 0.1621 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 2.7831 | 0.0012636
232.6 | 41.6 | 132.3787 | 0.046423 | 131.9783 | 0.0032298 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.033078 | 0.14424 | 0.00012922 | 0.28848 | 0.0019208 | 0.10349 | 0.0016967 | 2.8208 | 0.0019433 | 132.2304 | 0.038178 | 131.574 | 0.0048085 | 0.095061 | 8.4239e-05 | 65.137 | 0.034426 | -0.0775 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | -0.00017979 | 2.4076 | 7.2982e-05 | 133.4424 | 0.038813 | 132.9443 | 0.0050999 | 0.017185 | -8.9855e-05 | 65.162 | 0.032258 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 2.6024 | 0.004404 | 129.353 | 0.045329 | 129.3268 | 0.0042238 | 0.23793 | 0.00041557 | 63.3141 | 0.02714 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748 | 0.22513 | 0.0031962 | 2.7831 | 0.0012636
232.8 | 41.8 | 132.3787 | 0.046423 | 131.9783 | 0.0032298 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.033078 | 0.24166 | 0.00012922 | 0.19109 | 0.00029777 | 0.10349 | 0.0016967 | 2.8208 | 0.00032025 | 132.2304 | 0.038178 | 131.574 | 0.0048085 | 0.095061 | 8.4239e-05 | 65.137 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | 0.0014439 | 2.4076 | 7.2982e-05 | 133.4424 | 0.038813 | 132.9443 | 0.0050999 | 0.017185 | 0.0015332 | 65.162 | 0.032258 | 0.17559 | 0.0015107 | -0.011119 | 0.0009884 | 0.21368 | 0.0012074 | 2.6998 | 0.004404 | 129.353 | 0.045329 | 129.3268 | 0.0042238 | 0.14051 | 0.00041557 | 63.2167 | 0.02714 | 0.1621 | 0.0011513 | 0.11153 | 0.0012748 | 0.22513 | 0.0031962 | 2.6856 | 0.0012636
233 | 42 | 132.3787 | 0.046423 | 131.9783 | 0.0032298 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.034701 | 0.14424 | 0.00012922 | 0.19109 | 0.00029777 | 0.0060648 | 0.0016967 | 2.8208 | 0.00032025 | 132.2304 | 0.036554 | 131.574 | 0.0048085 | 0.095061 | 8.4239e-05 | 65.137 | 0.034426 | 0.01988 | 0.00064048 | 0.11562 | 0.0013085 | 0.2568 | 0.0014439 | 2.4076 | -0.00155 | 133.4424 | 0.037189 | 132.9443 | 0.0050999 | -0.080196 | -8.9855e-05 | 65.162 | 0.032258 | 0.17559 | -0.00011232 | 0.086261 | -0.0006346 | 0.11626 | 0.0012074 | 2.6998 | 0.004404 | 129.353 | 0.045329 | 129.3268 | 0.0042238 | 0.23793 | 0.00041557 | 63.3141 | 0.028764 | 0.1621 | 0.0011513 | 0.11153 | -0.00034817 | 0.22513 | 0.0031962 | 2.7831 | 0.0012636
233.2 | 42.2 | 132.3787 | 0.048047 | 131.9783 | 0.0032298 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.033078 | 0.14424 | 0.0017522 | 0.19109 | 0.00029777 | 0.10349 | 0.0016967 | 2.8208 | 0.0019433 | 132.2304 | 0.038178 | 131.6713 | 0.0048085 | 0.095061 | 8.4239e-05 | 65.137 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 2.4076 | 7.2982e-05 | 133.4424 | 0.038813 | 133.0416 | 0.0034769 | -0.080196 | -8.9855e-05 | 65.162 | 0.032258 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 2.6998 | 0.004404 | 129.353 | 0.045329 | 129.3268 | 0.0042238 | 0.23793 | 0.00041557 | 63.3141 | 0.02714 | 0.1621 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 2.7831 | -0.0003594
233.4 | 42.4 | 132.3787 | 0.046423 | 131.9783 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.034701 | 0.24166 | 0.00012922 | 0.19109 | 0.00029777 | 0.10349 | 0.0016967 | 2.8208 | 0.00032025 | 132.133 | 0.038178 | 131.4765 | 0.0064315 | 0.095061 | 8.4239e-05 | 65.137 | 0.034426 | 0.01988 | 0.00064048 | 0.018196 | 0.0013085 | 0.15942 | -0.00017979 | 2.4076 | 7.2982e-05 | 133.4424 | 0.037189 | 132.9443 | 0.0034769 | 0.017185 | -8.9855e-05 | 65.162 | 0.030635 | 0.17559 | 0.0015107 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 2.6998 | 0.004404 | 129.353 | 0.046952 | 129.3268 | 0.0042238 | 0.23793 | 0.00041557 | 63.3141 | 0.02714 | 0.1621 | 0.0011513 | 0.20895 | 0.0012748 | 0.22513 | 0.0031962 | 2.7831 | 0.0012636
233.6 | 42.6 | 132.3787 | 0.046423 | 131.9783 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.034701 | 0.14424 | 0.00012922 | 0.19109 | 0.00029777 | 0.10349 | 7.2991e-05 | 2.8208 | 0.0019433 | 132.2304 | 0.038178 | 131.574 | 0.0064315 | 0.095061 | 8.4239e-05 | 65.137 | 0.034426 | 0.01988 | 0.00064048 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 2.4076 | 7.2982e-05 | 133.4424 | 0.037189 | 132.9443 | 0.0050999 | 0.017185 | -8.9855e-05 | 65.162 | 0.032258 | 0.17559 | -0.00011232 | -0.011119 | -0.0006346 | 0.11626 | 0.0012074 | 2.6024 | 0.0027804 | 129.353 | 0.045329 | 129.3268 | 0.0042238 | 0.14051 | 0.00041557 | 63.3141 | 0.02714 | 0.1621 | 0.0011513 | 0.20895 | 0.0012748 | 0.22513 | 0.0031962 | 2.6856 | 0.0012636
233.8 | 42.8 | 132.2813 | 0.046423 | 131.9783 | 0.0032298 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.034701 | 0.14424 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | 2.8208 | 0.00032025 | 132.133 | 0.038178 | 131.574 | 0.0048085 | 0.095061 | 8.4239e-05 | 65.137 | 0.034426 | -0.0775 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | 0.0014439 | 2.4076 | 7.2982e-05 | 133.4424 | 0.038813 | 132.9443 | 0.0050999 | 0.017185 | -8.9855e-05 | 65.162 | 0.030635 | 0.17559 | -0.00011232 | -0.011119 | -0.0006346 | 0.11626 | 0.0012074 | 2.6024 | 0.004404 | 129.353 | 0.045329 | 129.3268 | 0.0042238 | 0.23793 | 0.00041557 | 63.2167 | 0.028764 | 0.1621 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 2.7831 | 0.0012636
234 | 43 | 132.2813 | 0.046423 | 131.881 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.8614 | 0.033078 | 0.14424 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | 2.8208 | 0.00032025 | 132.133 | 0.038178 | 131.4765 | 0.0048085 | 0.095061 | 8.4239e-05 | 65.137 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 2.4076 | 7.2982e-05 | 133.345 | 0.038813 | 132.8468 | 0.0034769 | 0.017185 | -8.9855e-05 | 65.162 | 0.032258 | 0.17559 | 0.0015107 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 2.6024 | 0.0027804 | 129.2556 | 0.046952 | 129.2293 | 0.0058469 | 0.23793 | 0.00041557 | 63.2167 | 0.028764 | 0.25952 | 0.0011513 | 0.11153 | 0.0012748 | 0.22513 | 0.0031962 | 2.6856 | 0.0012636
234.2 | 43.2 | 132.3787 | 0.048047 | 131.9783 | 0.0032298 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.033078 | 0.24166 | -0.0014944 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | 2.8208 | 0.00032025 | 132.133 | 0.038178 | 131.574 | 0.0048085 | 0.095061 | 8.4239e-05 | 65.137 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 2.4076 | 0.0016967 | 133.4424 | 0.038813 | 132.9443 | 0.0050999 | 0.017185 | -8.9855e-05 | 65.162 | 0.030635 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.21368 | 0.0012074 | 2.6024 | 0.004404 | 129.353 | 0.046952 | 129.3268 | 0.0058469 | 0.23793 | 0.00041557 | 63.3141 | 0.028764 | 0.1621 | 0.0011513 | 0.11153 | -0.00034817 | 0.22513 | 0.0031962 | 2.7831 | 0.0012636
234.4 | 43.4 | 132.3787 | 0.048047 | 131.9783 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.034701 | 0.24166 | 0.00012922 | 0.19109 | 0.00029777 | 0.10349 | 7.2991e-05 | 2.8208 | 0.0019433 | 132.133 | 0.038178 | 131.574 | 0.0048085 | 0.095061 | 8.4239e-05 | 65.137 | 0.034426 | 0.01988 | 0.00064048 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 2.4076 | 7.2982e-05 | 133.4424 | 0.038813 | 132.9443 | 0.0050999 | -0.080196 | -8.9855e-05 | 65.162 | 0.032258 | 0.17559 | 0.0015107 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 2.6024 | 0.004404 | 129.2556 | 0.048575 | 129.2293 | 0.0058469 | 0.23793 | 0.00041557 | 63.3141 | 0.02714 | 0.1621 | -0.00047174 | 0.20895 | 0.0012748 | 0.22513 | 0.0031962 | 2.7831 | 0.0012636
234.6 | 43.6 | 132.3787 | 0.046423 | 131.9783 | 0.0048528 | 0.10277 | 0.0016399 | 64.9588 | 0.034701 | 0.24166 | 0.00012922 | 0.19109 | 0.00029777 | 0.10349 | 0.0016967 | 2.8208 | 0.00032025 | 132.133 | 0.038178 | 131.574 | 0.0064315 | 0.095061 | 8.4239e-05 | 65.2344 | 0.034426 | 0.01988 | 0.00064048 | -0.079185 | -0.00031449 | 0.15942 | -0.00017979 | 2.4076 | 7.2982e-05 | 133.4424 | 0.038813 | 133.0416 | 0.0050999 | 0.017185 | -8.9855e-05 | 65.162 | 0.030635 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 2.6024 | 0.004404 | 129.353 | 0.046952 | 129.3268 | 0.0074705 | 0.23793 | 0.00041557 | 63.3141 | 0.02714 | 0.1621 | -0.00047174 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 2.7831 | 0.0012636
234.8 | 43.8 | 132.3787 | 0.046423 | 131.9783 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.033078 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 7.2991e-05 | 2.8208 | 0.00032025 | 132.133 | 0.038178 | 131.574 | 0.0064315 | 0.19244 | 8.4239e-05 | 65.137 | 0.034426 | 0.01988 | 0.00064048 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 2.4076 | 7.2982e-05 | 133.5397 | 0.038813 | 132.9443 | 0.0050999 | 0.017185 | 0.0015332 | 65.162 | 0.030635 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 2.505 | 0.004404 | 129.353 | 0.048575 | 129.3268 | 0.0074705 | 0.23793 | 0.00041557 | 63.3141 | 0.02714 | 0.1621 | -0.00047174 | 0.11153 | 0.0012748 | 0.22513 | 0.0031962 | 2.7831 | 0.0012636
235 | 44 | 132.3787 | 0.046423 | 131.9783 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.033078 | 0.14424 | 0.00012922 | 0.19109 | 0.0019208 | 0.20087 | 7.2991e-05 | 2.8208 | 0.00032025 | 132.2304 | 0.038178 | 131.574 | 0.0048085 | 0.19244 | 8.4239e-05 | 65.137 | 0.034426 | 0.01988 | 0.00064048 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 2.4076 | 7.2982e-05 | 133.5397 | 0.037189 | 133.0416 | 0.0050999 | -0.080196 | -8.9855e-05 | 65.162 | 0.032258 | 0.17559 | 0.0015107 | -0.011119 | 0.0009884 | 0.11626 | -0.00041558 | 2.6024 | 0.004404 | 129.353 | 0.048575 | 129.3268 | 0.0058469 | 0.14051 | -0.0012074 | 63.2167 | 0.02714 | 0.1621 | -0.00047174 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 2.7831 | 0.0012636
235.2 | 44.2 | 132.2813 | 0.046423 | 131.9783 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.033078 | 0.24166 | 0.00012922 | 0.19109 | 0.00029777 | 0.10349 | 0.0016967 | 2.8208 | 0.00032025 | 132.133 | 0.038178 | 131.574 | 0.0048085 | 0.095061 | 8.4239e-05 | 65.137 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | -0.00017979 | 2.4076 | 7.2982e-05 | 133.4424 | 0.038813 | 132.9443 | 0.0050999 | 0.017185 | 0.0015332 | 65.162 | 0.032258 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 2.505 | 0.004404 | 129.353 | 0.046952 | 129.3268 | 0.0058469 | 0.23793 | 0.00041557 | 63.3141 | 0.028764 | 0.1621 | 0.0011513 | 0.11153 | -0.00034817 | 0.22513 | 0.0048192 | 2.7831 | 0.0012636
235.4 | 44.4 | 132.1839 | 0.048047 | 131.881 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.033078 | 0.24166 | 0.00012922 | 0.19109 | 0.00029777 | 0.10349 | 7.2991e-05 | 2.8208 | 0.00032025 | 132.133 | 0.038178 | 131.4765 | 0.0064315 | 0.19244 | 8.4239e-05 | 65.137 | 0.034426 | 0.01988 | 0.0022635 | 0.11562 | -0.00031449 | 0.15942 | -0.00017979 | 2.4076 | 7.2982e-05 | 133.4424 | 0.038813 | 132.9443 | 0.0050999 | 0.017185 | 0.0015332 | 65.162 | 0.032258 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 2.6024 | 0.004404 | 129.353 | 0.046952 | 129.2293 | 0.0074705 | 0.23793 | 0.00041557 | 63.3141 | 0.028764 | 0.1621 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 2.7831 | 0.0012636
235.6 | 44.6 | 132.3787 | 0.046423 | 131.881 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.034701 | 0.14424 | 0.00012922 | 0.19109 | 0.00029777 | 0.10349 | 0.0016967 | 2.8208 | 0.00032025 | 132.2304 | 0.038178 | 131.574 | 0.0048085 | 0.095061 | 8.4239e-05 | 65.137 | 0.034426 | 0.01988 | 0.00064048 | 0.018196 | -0.00031449 | 0.062 | -0.00017979 | 2.4076 | 7.2982e-05 | 133.4424 | 0.038813 | 132.9443 | 0.0050999 | 0.017185 | -8.9855e-05 | 65.162 | 0.032258 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 2.505 | 0.004404 | 129.2556 | 0.046952 | 129.2293 | 0.0058469 | 0.23793 | 0.00041557 | 63.3141 | 0.028764 | 0.1621 | -0.00047174 | 0.11153 | -0.00034817 | 0.22513 | 0.0031962 | 2.7831 | 0.0012636
235.8 | 44.8 | 132.2813 | 0.048047 | 131.881 | 0.0048528 | 0.10277 | 1.6859e-05 | 64.9588 | 0.033078 | 0.14424 | 0.00012922 | 0.19109 | 0.00029777 | 0.10349 | 7.2991e-05 | 2.8208 | 0.00032025 | 132.133 | 0.036554 | 131.574 | 0.0064315 | 0.19244 | 8.4239e-05 | 65.137 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 2.505 | 7.2982e-05 | 133.4424 | 0.038813 | 132.9443 | 0.0050999 | 0.017185 | -8.9855e-05 | 65.162 | 0.032258 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.11626 | -0.00041558 | 2.6024 | 0.004404 | 129.2556 | 0.046952 | 129.3268 | 0.0058469 | 0.23793 | 0.00041557 | 63.3141 | 0.028764 | 0.1621 | 0.0011513 | 0.20895 | 0.0012748 | 0.22513 | 0.0031962 | 2.7831 | 0.0012636
236 | 45 | 132.2813 | 0.048047 | 131.7836 | 0.0048528 | 0.0053935 | 0.0016399 | 64.8614 | 0.034701 | 0.14424 | 0.00012922 | 0.28848 | 0.00029777 | 0.20087 | 0.0016967 | 2.8208 | 0.0019433 | 132.0357 | 0.038178 | 131.3792 | 0.0064315 | 0.095061 | 8.4239e-05 | 65.137 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.062 | -0.00017979 | 2.505 | 7.2982e-05 | 133.345 | 0.038813 | 132.8468 | 0.0050999 | 0.017185 | -8.9855e-05 | 65.0646 | 0.032258 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 2.505 | 0.004404 | 129.2556 | 0.046952 | 129.2293 | 0.0058469 | 0.23793 | 0.00041557 | 63.2167 | 0.028764 | 0.1621 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 2.7831 | 0.0012636
236.2 | 45.2 | 132.2813 | 0.048047 | 131.9783 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.8614 | 0.034701 | 0.14424 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | 2.8208 | 0.00032025 | 132.133 | 0.036554 | 131.4765 | 0.0064315 | 0.095061 | 8.4239e-05 | 65.137 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | -0.00017979 | 2.505 | 7.2982e-05 | 133.4424 | 0.038813 | 132.9443 | 0.0050999 | 0.017185 | -8.9855e-05 | 65.0646 | 0.032258 | 0.17559 | -0.00011232 | -0.011119 | -0.0006346 | 0.11626 | 0.0012074 | 2.505 | 0.004404 | 129.353 | 0.046952 | 129.3268 | 0.0058469 | 0.23793 | 0.00041557 | 63.3141 | 0.028764 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 2.6856 | 0.0012636
236.4 | 45.4 | 132.2813 | 0.046423 | 131.881 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.034701 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | 2.8208 | 0.00032025 | 132.133 | 0.038178 | 131.4765 | 0.0064315 | 0.19244 | 8.4239e-05 | 65.137 | 0.034426 | 0.01988 | 0.00064048 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 2.505 | 7.2982e-05 | 133.4424 | 0.038813 | 132.9443 | 0.0050999 | 0.017185 | -8.9855e-05 | 65.162 | 0.032258 | 0.17559 | 0.0015107 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 2.505 | 0.004404 | 129.2556 | 0.046952 | 129.3268 | 0.0058469 | 0.14051 | 0.00041557 | 63.3141 | 0.028764 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 2.7831 | 0.0012636
236.6 | 45.6 | 132.3787 | 0.048047 | 131.881 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.8614 | 0.034701 | 0.24166 | 0.00012922 | 0.19109 | 0.00029777 | 0.10349 | 0.0016967 | 2.8208 | 0.0019433 | 132.133 | 0.038178 | 131.574 | 0.0064315 | 0.19244 | 8.4239e-05 | 65.137 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.2568 | 0.0014439 | 2.4076 | 7.2982e-05 | 133.4424 | 0.038813 | 132.9443 | 0.0050999 | 0.017185 | -8.9855e-05 | 65.162 | 0.032258 | 0.17559 | -0.00011232 | 0.086261 | -0.0006346 | 0.11626 | 0.0012074 | 2.505 | 0.006027 | 129.2556 | 0.046952 | 129.3268 | 0.0058469 | 0.23793 | 0.00041557 | 63.3141 | 0.02714 | 0.1621 | 0.0011513 | 0.11153 | 0.0012748 | 0.22513 | 0.0031962 | 2.7831 | 0.0012636
236.8 | 45.8 | 132.3787 | 0.048047 | 131.881 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.8614 | 0.034701 | 0.14424 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | 2.8208 | 0.00032025 | 132.133 | 0.038178 | 131.574 | 0.0064315 | 0.19244 | 8.4239e-05 | 65.137 | 0.034426 | 0.01988 | 0.00064048 | 0.11562 | -0.00031449 | 0.15942 | 0.0014439 | 2.4076 | 0.0016967 | 133.4424 | 0.038813 | 132.9443 | 0.0050999 | 0.017185 | -8.9855e-05 | 65.162 | 0.032258 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 2.6024 | 0.004404 | 129.353 | 0.046952 | 129.3268 | 0.0058469 | 0.23793 | 0.00041557 | 63.2167 | 0.028764 | 0.1621 | -0.00047174 | 0.20895 | 0.0012748 | 0.22513 | 0.0031962 | 2.7831 | -0.0003594
237 | 46 | 132.3787 | 0.048047 | 131.9783 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.034701 | 0.14424 | 0.00012922 | 0.19109 | 0.00029777 | 0.10349 | 0.0016967 | 2.8208 | 0.0019433 | 132.2304 | 0.038178 | 131.6713 | 0.0064315 | 0.095061 | 8.4239e-05 | 65.137 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | 0.0014439 | 2.505 | 7.2982e-05 | 133.5397 | 0.038813 | 133.0416 | 0.0050999 | 0.017185 | -8.9855e-05 | 65.162 | 0.032258 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 2.505 | 0.004404 | 129.353 | 0.046952 | 129.4241 | 0.0058469 | 0.14051 | 0.00041557 | 63.3141 | 0.028764 | 0.1621 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 2.7831 | 0.0012636
237.2 | 46.2 | 132.2813 | 0.048047 | 131.881 | 0.0048528 | -0.092027 | 1.6859e-05 | 64.8614 | 0.034701 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | 2.7234 | 0.00032025 | 132.2304 | 0.038178 | 131.6713 | 0.0064315 | 0.19244 | 8.4239e-05 | 65.2344 | 0.034426 | 0.01988 | 0.00064048 | 0.018196 | 0.0013085 | 0.15942 | -0.00017979 | 2.4076 | 7.2982e-05 | 133.5397 | 0.038813 | 132.9443 | 0.0050999 | 0.017185 | 0.0015332 | 65.162 | 0.032258 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 2.505 | 0.004404 | 129.353 | 0.048575 | 129.4241 | 0.0058469 | 0.23793 | 0.00041557 | 63.3141 | 0.02714 | 0.25952 | -0.00047174 | 0.20895 | 0.0012748 | 0.22513 | 0.0031962 | 2.7831 | 0.0012636
237.4 | 46.4 | 132.2813 | 0.048047 | 132.0758 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.8614 | 0.034701 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | 2.8208 | 0.00032025 | 132.2304 | 0.038178 | 131.574 | 0.0064315 | 0.095061 | 8.4239e-05 | 65.137 | 0.032803 | 0.01988 | 0.00064048 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 2.505 | 7.2982e-05 | 133.5397 | 0.038813 | 132.9443 | 0.0050999 | 0.017185 | -8.9855e-05 | 65.0646 | 0.030635 | 0.17559 | 0.0015107 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 2.6024 | 0.004404 | 129.353 | 0.046952 | 129.3268 | 0.0058469 | 0.23793 | 0.00041557 | 63.3141 | 0.028764 | 0.1621 | -0.00047174 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 2.7831 | 0.0012636
237.6 | 46.6 | 132.2813 | 0.048047 | 131.9783 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.034701 | 0.24166 | 0.00012922 | 0.19109 | 0.00029777 | 0.10349 | 0.0016967 | 2.8208 | 0.00032025 | 132.2304 | 0.038178 | 131.574 | 0.0064315 | 0.095061 | 8.4239e-05 | 65.2344 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 2.505 | 0.0016967 | 133.5397 | 0.038813 | 132.9443 | 0.0050999 | -0.080196 | -8.9855e-05 | 65.162 | 0.030635 | 0.17559 | 0.0015107 | 0.086261 | 0.0009884 | 0.21368 | 0.0012074 | 2.505 | 0.004404 | 129.353 | 0.048575 | 129.3268 | 0.0058469 | 0.23793 | 0.00041557 | 63.3141 | 0.02714 | 0.1621 | 0.0011513 | 0.11153 | -0.00034817 | 0.22513 | 0.0031962 | 2.7831 | 0.0012636
237.8 | 46.8 | 132.2813 | 0.048047 | 131.9783 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.034701 | 0.14424 | 0.00012922 | 0.19109 | 0.00029777 | 0.10349 | 7.2991e-05 | 2.8208 | 0.00032025 | 132.2304 | 0.038178 | 131.574 | 0.0064315 | 0.19244 | 8.4239e-05 | 65.137 | 0.034426 | 0.01988 | 0.00064048 | 0.018196 | 0.0013085 | 0.15942 | -0.00017979 | 2.4076 | 0.0016967 | 133.4424 | 0.038813 | 132.9443 | 0.0050999 | 0.017185 | -8.9855e-05 | 65.162 | 0.032258 | 0.17559 | 0.0015107 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 2.505 | 0.004404 | 129.353 | 0.046952 | 129.3268 | 0.0058469 | 0.23793 | 0.00041557 | 63.3141 | 0.02714 | 0.1621 | -0.00047174 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 2.8804 | 0.0012636
238 | 47 | 132.2813 | 0.048047 | 131.9783 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.8614 | 0.034701 | 0.14424 | 0.00012922 | 0.19109 | 0.00029777 | 0.10349 | 7.2991e-05 | 2.8208 | 0.00032025 | 132.2304 | 0.038178 | 131.574 | 0.0064315 | 0.19244 | 8.4239e-05 | 65.2344 | 0.034426 | 0.01988 | 0.00064048 | 0.018196 | -0.00031449 | 0.2568 | 0.0014439 | 2.505 | 7.2982e-05 | 133.4424 | 0.038813 | 132.9443 | 0.0050999 | 0.017185 | 0.0015332 | 65.162 | 0.032258 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 2.505 | 0.004404 | 129.353 | 0.046952 | 129.3268 | 0.0074705 | 0.14051 | 0.00041557 | 63.3141 | 0.02714 | 0.1621 | 0.0011513 | 0.20895 | 0.0012748 | 0.22513 | 0.0031962 | 2.7831 | 0.0012636
238.2 | 47.2 | 132.2813 | 0.04967 | 131.9783 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.8614 | 0.034701 | 0.14424 | 0.00012922 | 0.19109 | 0.00029777 | 0.10349 | 7.2991e-05 | 2.8208 | 0.00032025 | 132.2304 | 0.038178 | 131.574 | 0.0064315 | 0.19244 | 8.4239e-05 | 65.137 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 2.505 | 7.2982e-05 | 133.5397 | 0.038813 | 133.0416 | 0.0050999 | 0.017185 | -8.9855e-05 | 65.162 | 0.032258 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.21368 | 0.0012074 | 2.505 | 0.004404 | 129.353 | 0.046952 | 129.3268 | 0.0058469 | 0.23793 | 0.00041557 | 63.3141 | 0.02714 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 2.7831 | 0.0012636
238.4 | 47.4 | 132.3787 | 0.048047 | 131.9783 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.034701 | 0.24166 | 0.00012922 | 0.19109 | 0.00029777 | 0.10349 | 7.2991e-05 | 2.8208 | 0.00032025 | 132.3278 | 0.039801 | 131.6713 | 0.0064315 | 0.095061 | 0.0017072 | 65.137 | 0.034426 | 0.01988 | 0.00064048 | 0.018196 | 0.0013085 | 0.15942 | 0.0014439 | 2.6024 | 0.0016967 | 133.5397 | 0.038813 | 133.0416 | 0.0050999 | 0.017185 | 0.0015332 | 65.162 | 0.032258 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.21368 | 0.0012074 | 2.505 | 0.004404 | 129.353 | 0.046952 | 129.3268 | 0.0074705 | 0.23793 | 0.00041557 | 63.3141 | 0.02714 | 0.25952 | -0.00047174 | 0.20895 | 0.0012748 | 0.22513 | 0.0031962 | 2.8804 | 0.0012636
238.6 | 47.6 | 132.3787 | 0.048047 | 131.9783 | 0.0048528 | 0.10277 | 1.6859e-05 | 64.9588 | 0.034701 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | 2.8208 | 0.00032025 | 132.2304 | 0.039801 | 131.574 | 0.0064315 | 0.19244 | 8.4239e-05 | 65.137 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 2.505 | 7.2982e-05 | 133.5397 | 0.038813 | 133.0416 | 0.0050999 | 0.017185 | -8.9855e-05 | 65.162 | 0.032258 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 2.505 | 0.004404 | 129.353 | 0.046952 | 129.3268 | 0.0074705 | 0.14051 | 0.00041557 | 63.3141 | 0.028764 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 2.7831 | 0.0012636
238.8 | 47.8 | 132.3787 | 0.048047 | 131.9783 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.8614 | 0.034701 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | 2.8208 | 0.0019433 | 132.3278 | 0.039801 | 131.6713 | 0.0064315 | 0.095061 | 8.4239e-05 | 65.137 | 0.034426 | 0.01988 | 0.0022635 | 0.11562 | 0.0013085 | 0.15942 | 0.0014439 | 2.505 | 7.2982e-05 | 133.5397 | 0.038813 | 133.0416 | 0.0050999 | 0.017185 | 0.0015332 | 65.162 | 0.032258 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 2.505 | 0.004404 | 129.353 | 0.048575 | 129.3268 | 0.0074705 | 0.23793 | 0.00041557 | 63.3141 | 0.028764 | 0.1621 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 2.8804 | -0.0003594
239 | 48 | 132.3787 | 0.048047 | 131.9783 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.8614 | 0.033078 | 0.24166 | 0.00012922 | 0.19109 | 0.00029777 | 0.10349 | 0.0016967 | 2.8208 | 0.00032025 | 132.3278 | 0.039801 | 131.574 | 0.0064315 | 0.19244 | 8.4239e-05 | 65.137 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 2.505 | 0.0016967 | 133.5397 | 0.038813 | 133.0416 | 0.0050999 | 0.017185 | -8.9855e-05 | 65.162 | 0.032258 | 0.17559 | 0.0015107 | 0.086261 | -0.0006346 | 0.11626 | 0.0012074 | 2.505 | 0.0027804 | 129.4504 | 0.048575 | 129.3268 | 0.0074705 | 0.23793 | 0.00041557 | 63.3141 | 0.02714 | 0.25952 | -0.00047174 | 0.11153 | 0.0012748 | 0.22513 | 0.0031962 | 2.7831 | 0.0012636
239.2 | 48.2 | 132.3787 | 0.048047 | 131.9783 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.034701 | 0.14424 | 0.00012922 | 0.19109 | 0.00029777 | 0.10349 | 0.0016967 | 2.8208 | 0.0019433 | 132.2304 | 0.039801 | 131.574 | 0.0064315 | 0.19244 | 8.4239e-05 | 65.137 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | -0.00017979 | 2.505 | 7.2982e-05 | 133.5397 | 0.038813 | 133.0416 | 0.0050999 | 0.017185 | 0.0015332 | 65.162 | 0.032258 | 0.17559 | 0.0015107 | -0.011119 | 0.0009884 | 0.21368 | 0.0012074 | 2.505 | 0.004404 | 129.353 | 0.046952 | 129.3268 | 0.0058469 | 0.23793 | 0.00041557 | 63.3141 | 0.028764 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 2.7831 | 0.0012636
239.4 | 48.4 | 132.3787 | 0.048047 | 131.9783 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.8614 | 0.034701 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 7.2991e-05 | 2.8208 | 0.00032025 | 132.2304 | 0.039801 | 131.6713 | 0.0064315 | 0.19244 | 8.4239e-05 | 65.2344 | 0.034426 | 0.01988 | 0.00064048 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 2.505 | 7.2982e-05 | 133.5397 | 0.038813 | 133.0416 | 0.0067236 | 0.017185 | -8.9855e-05 | 65.162 | 0.032258 | 0.17559 | 0.0015107 | -0.011119 | 0.0009884 | 0.21368 | 0.0012074 | 2.505 | 0.004404 | 129.4504 | 0.046952 | 129.3268 | 0.0058469 | 0.23793 | 0.00041557 | 63.3141 | 0.028764 | 0.1621 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 2.8804 | -0.0003594
239.6 | 48.6 | 132.3787 | 0.048047 | 131.9783 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.8614 | 0.033078 | 0.14424 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 7.2991e-05 | 2.8208 | 0.00032025 | 132.2304 | 0.039801 | 131.6713 | 0.0064315 | 0.095061 | 8.4239e-05 | 65.2344 | 0.034426 | 0.01988 | 0.00064048 | 0.018196 | 0.0013085 | 0.15942 | -0.00017979 | 2.6024 | 7.2982e-05 | 133.5397 | 0.038813 | 133.0416 | 0.0050999 | -0.080196 | -8.9855e-05 | 65.162 | 0.032258 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 2.505 | 0.004404 | 129.353 | 0.046952 | 129.3268 | 0.0058469 | 0.14051 | 0.00041557 | 63.3141 | 0.028764 | 0.1621 | -0.00047174 | 0.11153 | -0.00034817 | 0.22513 | 0.0031962 | 2.8804 | 0.0012636
239.8 | 48.8 | 132.3787 | 0.048047 | 131.9783 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.8614 | 0.034701 | 0.24166 | 0.00012922 | 0.19109 | 0.00029777 | 0.10349 | 0.0016967 | 2.8208 | 0.00032025 | 132.2304 | 0.039801 | 131.6713 | 0.0064315 | 0.095061 | 8.4239e-05 | 65.137 | 0.034426 | 0.01988 | 0.0022635 | 0.11562 | 0.0013085 | 0.15942 | -0.00017979 | 2.505 | 7.2982e-05 | 133.5397 | 0.038813 | 133.0416 | 0.0067236 | 0.017185 | 0.0015332 | 65.162 | 0.032258 | 0.17559 | -0.00011232 | -0.011119 | -0.0006346 | 0.21368 | 0.0012074 | 2.505 | 0.004404 | 129.4504 | 0.046952 | 129.4241 | 0.0074705 | 0.23793 | 0.00041557 | 63.3141 | 0.028764 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 2.7831 | 0.0012636
240 | 49 | 132.3787 | 0.048047 | 131.881 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.8614 | 0.034701 | 0.14424 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 7.2991e-05 | 2.8208 | 0.00032025 | 132.2304 | 0.039801 | 131.574 | 0.0064315 | 0.095061 | 8.4239e-05 | 65.137 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.062 | 0.0014439 | 2.505 | 7.2982e-05 | 133.4424 | 0.040436 | 132.9443 | 0.0050999 | 0.017185 | 0.0015332 | 65.162 | 0.032258 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 2.505 | 0.004404 | 129.353 | 0.046952 | 129.3268 | 0.0074705 | 0.14051 | 0.00041557 | 63.3141 | 0.028764 | 0.25952 | -0.00047174 | 0.20895 | -0.00034817 | 0.12771 | 0.0031962 | 2.8804 | 0.0012636
240.2 | 49.2 | 132.2813 | 0.04967 | 131.9783 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.8614 | 0.034701 | 0.14424 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 7.2991e-05 | 2.8208 | 0.0019433 | 132.2304 | 0.038178 | 131.6713 | 0.0064315 | 0.095061 | 8.4239e-05 | 65.2344 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 2.505 | 7.2982e-05 | 133.5397 | 0.040436 | 133.0416 | 0.0067236 | -0.080196 | -8.9855e-05 | 65.162 | 0.032258 | 0.17559 | -0.00011232 | -0.011119 | -0.0006346 | 0.21368 | 0.0012074 | 2.505 | 0.004404 | 129.353 | 0.048575 | 129.4241 | 0.0058469 | 0.23793 | 0.00041557 | 63.3141 | 0.028764 | 0.1621 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 2.8804 | 0.0012636
240.4 | 49.4 | 132.3787 | 0.048047 | 132.0758 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.8614 | 0.034701 | 0.24166 | 0.00012922 | 0.19109 | 0.00029777 | 0.10349 | 7.2991e-05 | 2.8208 | 0.00032025 | 132.3278 | 0.039801 | 131.6713 | 0.0064315 | 0.19244 | 8.4239e-05 | 65.2344 | 0.034426 | 0.01988 | 0.00064048 | 0.018196 | 0.0013085 | 0.15942 | 0.0014439 | 2.6024 | 7.2982e-05 | 133.6372 | 0.040436 | 133.0416 | 0.0067236 | 0.017185 | -8.9855e-05 | 65.2594 | 0.032258 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 2.505 | 0.004404 | 129.4504 | 0.048575 | 129.4241 | 0.0074705 | 0.23793 | 0.00041557 | 63.3141 | 0.028764 | 0.1621 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 2.8804 | 0.0012636
240.6 | 49.6 | 132.3787 | 0.048047 | 132.0758 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.8614 | 0.034701 | 0.24166 | 0.00012922 | 0.19109 | 0.00029777 | 0.10349 | 0.0016967 | 2.8208 | 0.0019433 | 132.2304 | 0.039801 | 131.6713 | 0.0064315 | 0.19244 | 8.4239e-05 | 65.137 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | 0.0014439 | 2.505 | 7.2982e-05 | 133.5397 | 0.040436 | 133.0416 | 0.0067236 | -0.080196 | -8.9855e-05 | 65.162 | 0.032258 | 0.17559 | -0.00011232 | -0.011119 | -0.0006346 | 0.21368 | 0.0012074 | 2.505 | 0.004404 | 129.4504 | 0.046952 | 129.3268 | 0.0058469 | 0.23793 | 0.00041557 | 63.3141 | 0.02714 | 0.1621 | -0.00047174 | 0.11153 | -0.00034817 | 0.22513 | 0.0031962 | 2.7831 | 0.0012636
240.8 | 49.8 | 130.9178 | 0.048047 | 130.5174 | 0.0048528 | 0.10277 | 1.6859e-05 | 64.1796 | 0.033078 | 0.14424 | 0.00012922 | 0.28848 | 0.00029777 | 0.20087 | 7.2991e-05 | 2.7234 | 0.00032025 | 130.7695 | 0.038178 | 130.2104 | 0.0064315 | 0.095061 | 8.4239e-05 | 64.4553 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | -0.00017979 | 2.505 | 7.2982e-05 | 45.5907 | 0.024203 | 43.3394 | 3.0422 | 0.1146 | -8.9855e-05 | 22.7945 | 0.020895 | 0.17559 | -0.00011232 | 0.086261 | -0.0006346 | 0.21368 | -0.00041558 | 1.7258 | 0.0027804 | 127.9895 | 0.046952 | 127.9632 | 0.0058469 | 0.23793 | 0.00041557 | 62.6324 | 0.028764 | 0.1621 | 0.0011513 | 0.20895 | 0.0012748 | 0.22513 | 0.0031962 | 2.7831 | 0.0012636
241 | 50 | 132.2813 | 0.048047 | 131.881 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.8614 | 0.033078 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | 2.8208 | 0.00032025 | 132.3278 | 0.039801 | 131.574 | 0.0064315 | 0.095061 | 8.4239e-05 | 65.137 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | 0.0014439 | 2.505 | 7.2982e-05 | 5.8529 | 0.0095933 | 5.0626 | 0.18204 | 0.017185 | -8.9855e-05 | 3.3152 | 0.0095316 | 0.17559 | 0.0015107 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.75187 | 0.004404 | 129.353 | 0.048575 | 129.4241 | 0.0058469 | 0.23793 | 0.00041557 | 63.3141 | 0.028764 | 0.25952 | 0.0011513 | 0.11153 | 0.0012748 | 0.22513 | 0.0031962 | 2.7831 | 0.0012636
241.2 | 50.2 | 132.3787 | 0.048047 | 132.0758 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.8614 | 0.034701 | 0.14424 | 0.0017522 | 0.19109 | 0.00029777 | 0.10349 | 7.2991e-05 | 2.8208 | 0.00032025 | 132.3278 | 0.039801 | 131.6713 | 0.0064315 | 0.095061 | -0.0015388 | 65.2344 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | 0.0014439 | 2.505 | 7.2982e-05 | 1.7623 | 0.0063473 | 1.5563 | 0.027826 | 0.017185 | 0.0015332 | 1.2699 | 0.0062856 | 0.078174 | -0.00011232 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 0.45969 | 0.004404 | 129.4504 | 0.048575 | 129.4241 | 0.0074705 | 0.23793 | 0.00041557 | 63.3141 | 0.028764 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748 | 0.22513 | 0.0031962 | 2.7831 | 0.0012636
241.4 | 50.4 | 132.3787 | 0.048047 | 132.0758 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.8614 | 0.034701 | 0.24166 | 0.00012922 | 0.28848 | 0.0019208 | 0.10349 | 0.0016967 | 2.8208 | 0.0019433 | 132.3278 | 0.039801 | 131.6713 | 0.0064315 | 0.095061 | 8.4239e-05 | 65.2344 | 0.036049 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.062 | -0.00017979 | 2.505 | 7.2982e-05 | 1.0805 | 0.0047237 | 0.87456 | 0.011593 | -0.080196 | -8.9855e-05 | 0.78287 | 0.0046619 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.36227 | 0.004404 | 129.4504 | 0.048575 | 129.4241 | 0.0074705 | 0.23793 | 0.00041557 | 63.3141 | 0.02714 | 0.1621 | -0.00047174 | 0.20895 | 0.0012748 | 0.22513 | 0.0031962 | 2.7831 | 0.0012636
241.6 | 50.6 | 132.4761 | 0.048047 | 131.9783 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.033078 | 0.14424 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | 2.8208 | 0.00032025 | 132.3278 | 0.039801 | 131.6713 | 0.0064315 | 0.095061 | 8.4239e-05 | 65.2344 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | -0.00017979 | 2.505 | 0.0016967 | 0.88568 | 0.0031007 | 0.67976 | 0.0067236 | 0.017185 | -8.9855e-05 | 0.58807 | 0.0030389 | 0.17559 | 0.0015107 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 0.36227 | 0.004404 | 129.4504 | 0.048575 | 129.4241 | 0.0058469 | 0.23793 | 0.00041557 | 63.4115 | 0.028764 | 0.25952 | -0.00047174 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 2.7831 | 0.0012636
241.8 | 50.8 | 132.4761 | 0.048047 | 132.0758 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.034701 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | 2.8208 | 0.00032025 | 132.4252 | 0.039801 | 131.6713 | 0.0080546 | 0.19244 | 8.4239e-05 | 65.2344 | 0.034426 | 0.01988 | 0.00064048 | 0.018196 | 0.0013085 | 0.15942 | 0.0014439 | 2.505 | 7.2982e-05 | 0.69088 | 0.0031007 | 0.58238 | 0.0050999 | 0.017185 | -8.9855e-05 | 0.49069 | 0.0030389 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 0.26489 | 0.0027804 | 129.4504 | 0.048575 | 129.5215 | 0.0074705 | 0.23793 | 0.00041557 | 63.4115 | 0.028764 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0015725 | 2.7831 | 0.0012636
242 | 51 | 132.3787 | 0.04967 | 131.9783 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.8614 | 0.034701 | 0.14424 | 0.00012922 | 0.19109 | 0.00029777 | 0.10349 | 7.2991e-05 | 2.8208 | 0.00032025 | 132.3278 | 0.039801 | 131.6713 | 0.0064315 | 0.095061 | 8.4239e-05 | 65.137 | 0.036049 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 2.6024 | 7.2982e-05 | 0.5935 | 0.0031007 | 0.48496 | 0.0034769 | -0.080196 | 0.0015332 | 0.39327 | 0.0030389 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.21368 | 0.0012074 | 0.16751 | 0.004404 | 129.4504 | 0.048575 | 129.4241 | 0.0074705 | 0.23793 | 0.00041557 | 63.3141 | 0.028764 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 2.7831 | 0.0012636
242.2 | 51.2 | 132.3787 | 0.048047 | 132.0758 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.8614 | 0.034701 | 0.14424 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | 2.8208 | 0.0019433 | 132.3278 | 0.039801 | 131.7687 | 0.0080546 | 0.19244 | 8.4239e-05 | 65.2344 | 0.036049 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | -0.00017979 | 2.505 | 7.2982e-05 | 0.5935 | 0.001477 | 0.38758 | 0.0034769 | 0.017185 | -8.9855e-05 | 0.49069 | 0.0014152 | 0.078174 | 0.0015107 | -0.011119 | 0.0009884 | 0.11626 | -0.00041558 | 0.16751 | 0.004404 | 129.5478 | 0.048575 | 129.5215 | 0.0074705 | 0.14051 | 0.00041557 | 63.3141 | 0.028764 | 0.1621 | 0.0011513 | 0.11153 | -0.00034817 | 0.22513 | 0.0031962 | 2.7831 | -0.0003594
242.4 | 51.4 | 132.3787 | 0.048047 | 132.0758 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.8614 | 0.034701 | 0.24166 | 0.00012922 | 0.28848 | 0.0019208 | 0.10349 | 0.0016967 | 2.8208 | 0.0019433 | 132.3278 | 0.039801 | 131.6713 | 0.0080546 | 0.19244 | 8.4239e-05 | 65.2344 | 0.036049 | 0.01988 | 0.00064048 | 0.018196 | 0.0013085 | 0.15942 | 0.0014439 | 2.6024 | 7.2982e-05 | 0.5935 | 0.001477 | 0.38758 | 0.0018533 | 0.017185 | -8.9855e-05 | 0.39327 | 0.0014152 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.21368 | 0.0012074 | 0.16751 | 0.004404 | 129.4504 | 0.048575 | 129.5215 | 0.0074705 | 0.23793 | 0.00041557 | 63.4115 | 0.028764 | 0.1621 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 2.8804 | 0.0012636
242.6 | 51.6 | 132.3787 | 0.04967 | 131.9783 | 0.0064758 | 0.0053935 | 1.6859e-05 | 64.8614 | 0.034701 | 0.24166 | 0.00012922 | 0.19109 | 0.00029777 | 0.10349 | 0.0016967 | 2.8208 | 0.00032025 | 132.3278 | 0.039801 | 131.6713 | 0.0080546 | 0.19244 | 8.4239e-05 | 65.2344 | 0.034426 | 0.01988 | 0.00064048 | 0.018196 | 0.0013085 | 0.15942 | 0.0014439 | 2.505 | 7.2982e-05 | 0.3987 | 0.001477 | 0.38758 | 0.0018533 | -0.080196 | 0.0015332 | 0.39327 | 0.0014152 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.21368 | 0.0012074 | 0.16751 | 0.004404 | 129.4504 | 0.048575 | 129.4241 | 0.0074705 | 0.23793 | 0.00041557 | 63.3141 | 0.030387 | 0.1621 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 2.7831 | 0.0012636
242.8 | 51.8 | 132.4761 | 0.048047 | 131.9783 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.8614 | 0.034701 | 0.14424 | 0.00012922 | 0.28848 | 0.0019208 | 0.20087 | 0.0016967 | 2.8208 | 0.00032025 | 132.3278 | 0.039801 | 131.6713 | 0.0080546 | 0.19244 | 8.4239e-05 | 65.2344 | 0.036049 | 0.01988 | 0.00064048 | 0.018196 | 0.0013085 | 0.2568 | 0.0014439 | 2.505 | 7.2982e-05 | 0.49608 | 0.001477 | 0.29015 | 0.0018533 | 0.017185 | -8.9855e-05 | 0.29589 | 0.0014152 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 129.5478 | 0.048575 | 129.4241 | 0.0090935 | 0.23793 | 0.00041557 | 63.4115 | 0.028764 | 0.1621 | 0.0011513 | 0.11153 | -0.00034817 | 0.32251 | 0.0031962 | 2.8804 | 0.0012636
243 | 52 | 132.4761 | 0.04967 | 132.0758 | 0.0048528 | 0.0053935 | 0.0016399 | 64.8614 | 0.034701 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | 2.8208 | 0.00032025 | 132.3278 | 0.039801 | 131.6713 | 0.0080546 | 0.19244 | 8.4239e-05 | 65.2344 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.2568 | 0.0014439 | 2.505 | 7.2982e-05 | 0.3987 | 0.001477 | 0.38758 | 0.0018533 | 0.017185 | -8.9855e-05 | 0.29589 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 129.5478 | 0.048575 | 129.5215 | 0.0090935 | 0.23793 | 0.00041557 | 63.4115 | 0.028764 | 0.25952 | -0.00047174 | 0.20895 | -0.00034817 | 0.22513 | 0.0048192 | 2.8804 | 0.0012636
243.2 | 52.2 | 132.4761 | 0.04967 | 132.0758 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.034701 | 0.24166 | 0.00012922 | 0.19109 | 0.00029777 | 0.10349 | 0.0016967 | 2.8208 | 0.00032025 | 132.4252 | 0.039801 | 131.7687 | 0.0080546 | 0.19244 | 8.4239e-05 | 65.2344 | 0.034426 | 0.11726 | 0.00064048 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 2.505 | 0.0016967 | 0.3987 | 0.001477 | 0.38758 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.39327 | 0.0014152 | 0.17559 | 0.0015107 | 0.086261 | 0.0009884 | 0.21368 | 0.0012074 | 0.16751 | 0.004404 | 129.5478 | 0.048575 | 129.5215 | 0.0090935 | 0.23793 | 0.00041557 | 63.4115 | 0.028764 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 2.8804 | 0.0012636
243.4 | 52.4 | 132.4761 | 0.048047 | 132.0758 | 0.0048528 | 0.0053935 | 0.0016399 | 64.9588 | 0.034701 | 0.24166 | 0.00012922 | 0.19109 | 0.00029777 | 0.10349 | 0.0033197 | 2.8208 | 0.00032025 | 132.4252 | 0.039801 | 131.7687 | 0.0080546 | 0.095061 | 8.4239e-05 | 65.2344 | 0.036049 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | 0.0014439 | 2.6024 | 7.2982e-05 | 0.3987 | 0.001477 | 0.38758 | 0.0018533 | -0.080196 | 0.0015332 | 0.29589 | 0.0014152 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.0027804 | 129.5478 | 0.048575 | 129.5215 | 0.0074705 | 0.14051 | 0.00041557 | 63.3141 | 0.028764 | 0.25952 | 0.0011513 | 0.11153 | 0.0012748 | 0.32251 | 0.0031962 | 2.8804 | 0.0012636
243.6 | 52.6 | 132.4761 | 0.048047 | 132.1731 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.034701 | 0.24166 | 0.0017522 | 0.19109 | 0.00029777 | 0.20087 | 0.0016967 | 2.9182 | 0.0019433 | 132.4252 | 0.039801 | 131.7687 | 0.0080546 | 0.19244 | 8.4239e-05 | 65.2344 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 2.6024 | 7.2982e-05 | 0.3987 | 0.001477 | 0.29015 | 0.00023025 | -0.080196 | -8.9855e-05 | 0.29589 | 0.0014152 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.070087 | 0.004404 | 129.5478 | 0.048575 | 129.5215 | 0.0090935 | 0.14051 | 0.00041557 | 63.4115 | 0.028764 | 0.1621 | -0.00047174 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 2.8804 | -0.0003594
243.8 | 52.8 | 132.4761 | 0.048047 | 132.1731 | 0.0048528 | 0.10277 | 1.6859e-05 | 64.9588 | 0.034701 | 0.14424 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | 2.8208 | 0.0019433 | 132.5226 | 0.041425 | 131.7687 | 0.0080546 | 0.095061 | 8.4239e-05 | 65.3318 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | 0.0014439 | 2.6024 | 7.2982e-05 | 0.3987 | 0.001477 | 0.29015 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.29589 | 0.0014152 | 0.078174 | -0.00011232 | 0.086261 | 0.0009884 | 0.21368 | 0.0012074 | 0.16751 | 0.004404 | 129.5478 | 0.048575 | 129.5215 | 0.0090935 | 0.14051 | 0.00041557 | 63.4115 | 0.028764 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 2.8804 | 0.0012636
244 | 53 | 132.4761 | 0.04967 | 132.0758 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.8614 | 0.034701 | 0.14424 | 0.00012922 | 0.19109 | 0.00029777 | 0.10349 | 7.2991e-05 | 2.9182 | 0.0019433 | 132.4252 | 0.039801 | 131.6713 | 0.0080546 | 0.19244 | 8.4239e-05 | 65.2344 | 0.034426 | 0.01988 | 0.00064048 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 2.505 | 0.0016967 | 0.3987 | 0.001477 | 0.29015 | 0.00023025 | -0.080196 | -8.9855e-05 | 0.29589 | 0.0014152 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.006027 | 129.4504 | 0.050198 | 129.5215 | 0.0090935 | 0.23793 | 0.00041557 | 63.4115 | 0.028764 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 2.8804 | 0.0012636
244.2 | 53.2 | 132.4761 | 0.04967 | 132.0758 | 0.0064758 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.034701 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | 2.8208 | 0.00032025 | 132.4252 | 0.039801 | 131.7687 | 0.0080546 | 0.095061 | 8.4239e-05 | 65.2344 | 0.036049 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | -0.00017979 | 2.505 | 0.0016967 | 0.3987 | 0.001477 | 0.29015 | 0.00023025 | -0.080196 | -8.9855e-05 | 0.29589 | 0.0014152 | 0.27297 | -0.00011232 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 0.070087 | 0.004404 | 129.5478 | 0.050198 | 129.6189 | 0.0090935 | 0.23793 | 0.00041557 | 63.4115 | 0.028764 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748 | 0.22513 | 0.0031962 | 2.7831 | 0.0012636
244.4 | 53.4 | 132.4761 | 0.04967 | 132.0758 | 0.0064758 | 0.0053935 | 1.6859e-05 | 64.8614 | 0.034701 | 0.24166 | 0.00012922 | 0.19109 | 0.00029777 | 0.20087 | 7.2991e-05 | 2.8208 | 0.0019433 | 132.4252 | 0.041425 | 131.7687 | 0.0080546 | 0.19244 | 8.4239e-05 | 65.2344 | 0.036049 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | 0.0014439 | 2.6024 | 7.2982e-05 | 0.3987 | 0.001477 | 0.29015 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.29589 | -0.00020779 | 0.17559 | 0.0015107 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.070087 | 0.004404 | 129.5478 | 0.050198 | 129.6189 | 0.0090935 | 0.23793 | 0.00041557 | 63.3141 | 0.030387 | 0.1621 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 2.8804 | 0.0012636
244.6 | 53.6 | 132.5735 | 0.04967 | 132.1731 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.034701 | 0.14424 | 0.0017522 | 0.19109 | 0.00029777 | 0.10349 | 0.0016967 | 2.8208 | 0.00032025 | 132.5226 | 0.041425 | 131.8661 | 0.0080546 | 0.19244 | 8.4239e-05 | 65.3318 | 0.036049 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 2.6024 | 0.0016967 | 0.3987 | 0.001477 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.29589 | 0.0014152 | 0.17559 | 0.0015107 | -0.011119 | 0.0009884 | 0.21368 | 0.0012074 | 0.16751 | 0.004404 | 129.6452 | 0.050198 | 129.6189 | 0.0090935 | 0.23793 | 0.00041557 | 63.5089 | 0.028764 | 0.1621 | 0.0011513 | 0.20895 | 0.0012748 | 0.22513 | 0.0031962 | 2.8804 | 0.0012636
244.8 | 53.8 | 132.5735 | 0.04967 | 132.1731 | 0.0064758 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.033078 | 0.14424 | 0.00012922 | 0.19109 | 0.00029777 | 0.10349 | 0.0016967 | 2.8208 | 0.0019433 | 132.5226 | 0.041425 | 131.7687 | 0.0080546 | 0.095061 | 8.4239e-05 | 65.2344 | 0.036049 | 0.11726 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | -0.00017979 | 2.505 | 7.2982e-05 | 0.3987 | 0.001477 | 0.29015 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.21368 | 0.0012074 | 0.070087 | 0.004404 | 129.6452 | 0.050198 | 129.5215 | 0.0090935 | 0.23793 | 0.00041557 | 63.4115 | 0.030387 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748 | 0.22513 | 0.0031962 | 2.7831 | 0.0012636
245 | 54 | 132.4761 | 0.04967 | 132.1731 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.034701 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | 2.8208 | 0.0019433 | 132.5226 | 0.041425 | 131.7687 | 0.0080546 | 0.19244 | 8.4239e-05 | 65.2344 | 0.036049 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.2568 | 0.0014439 | 2.6024 | 7.2982e-05 | 0.3987 | -0.00014601 | 0.29015 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.29589 | -0.00020779 | 0.17559 | 0.0015107 | -0.011119 | 0.0009884 | 0.21368 | 0.0012074 | 0.070087 | 0.004404 | 129.5478 | 0.050198 | 129.5215 | 0.0074705 | 0.23793 | 0.00041557 | 63.4115 | 0.030387 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748 | 0.22513 | 0.0031962 | 2.8804 | 0.0012636
245.2 | 54.2 | 132.5735 | 0.04967 | 132.1731 | 0.0064758 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.034701 | 0.14424 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | 2.8208 | 0.0019433 | 132.5226 | 0.039801 | 131.7687 | 0.0080546 | 0.19244 | 8.4239e-05 | 65.3318 | 0.036049 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.2568 | 0.0014439 | 2.6024 | 7.2982e-05 | 0.30132 | -0.00014601 | 0.29015 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.29589 | 0.0014152 | 0.17559 | 0.0015107 | -0.011119 | 0.0009884 | 0.21368 | 0.0012074 | 0.16751 | 0.004404 | 129.6452 | 0.051821 | 129.5215 | 0.0090935 | 0.23793 | 0.00041557 | 63.4115 | 0.028764 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 2.8804 | 0.0012636
245.4 | 54.4 | 132.4761 | 0.048047 | 132.1731 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.034701 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | 2.8208 | 0.0019433 | 132.5226 | 0.041425 | 131.8661 | 0.0080546 | 0.095061 | 8.4239e-05 | 65.3318 | 0.036049 | 0.01988 | 0.0022635 | 0.11562 | 0.0013085 | 0.15942 | -0.00017979 | 2.6024 | 7.2982e-05 | 0.30132 | -0.00014601 | 0.29015 | 0.00023025 | 0.017185 | 0.0015332 | 0.29589 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.070087 | 0.004404 | 129.6452 | 0.050198 | 129.6189 | 0.0090935 | 0.14051 | 0.00041557 | 63.4115 | 0.028764 | 0.1621 | 0.0011513 | 0.11153 | -0.00034817 | 0.22513 | 0.0031962 | 2.8804 | 0.0012636
245.6 | 54.6 | 132.4761 | 0.04967 | 132.1731 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.034701 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | 2.8208 | 0.0019433 | 132.5226 | 0.041425 | 131.8661 | 0.0080546 | 0.19244 | 8.4239e-05 | 65.3318 | 0.036049 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | -0.00017979 | 2.6024 | 7.2982e-05 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.29589 | -0.00020779 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 129.6452 | 0.050198 | 129.6189 | 0.0090935 | 0.23793 | 0.0020392 | 63.4115 | 0.028764 | 0.1621 | -0.00047174 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 2.8804 | 0.0012636
245.8 | 54.8 | 132.4761 | 0.04967 | 132.1731 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.034701 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | 2.9182 | 0.00032025 | 132.5226 | 0.039801 | 131.8661 | 0.0064315 | 0.095061 | 8.4239e-05 | 65.3318 | 0.036049 | 0.01988 | 0.00064048 | 0.018196 | 0.0013085 | 0.15942 | 0.0014439 | 2.6998 | 7.2982e-05 | 0.3987 | -0.00014601 | 0.29015 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.29589 | 0.0014152 | 0.17559 | 0.0015107 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 0.070087 | 0.006027 | 129.6452 | 0.050198 | 129.6189 | 0.0090935 | 0.23793 | 0.00041557 | 63.4115 | 0.030387 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 2.8804 | 0.0012636
246 | 55 | 132.4761 | 0.04967 | 132.1731 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.8614 | 0.034701 | 0.24166 | 0.0017522 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | 2.8208 | 0.00032025 | 132.62 | 0.039801 | 131.8661 | 0.0080546 | 0.095061 | 8.4239e-05 | 65.2344 | 0.036049 | 0.11726 | 0.00064048 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 2.6024 | 0.0016967 | 0.3987 | -0.00014601 | 0.29015 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.21368 | 0.0012074 | 0.16751 | 0.004404 | 129.6452 | 0.050198 | 129.6189 | 0.010717 | 0.14051 | 0.00041557 | 63.4115 | 0.028764 | 0.1621 | 0.0011513 | 0.11153 | -0.00034817 | 0.22513 | 0.0048192 | 2.8804 | 0.0012636
246.2 | 55.2 | 132.5735 | 0.048047 | 132.1731 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.033078 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | 2.8208 | 0.00032025 | 132.5226 | 0.041425 | 131.8661 | 0.0080546 | 0.095061 | 8.4239e-05 | 65.3318 | 0.036049 | 0.01988 | 0.00064048 | 0.018196 | 0.0013085 | 0.2568 | -0.00017979 | 2.6024 | 0.0016967 | 0.30132 | 0.001477 | 0.29015 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.17559 | 0.0015107 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 129.6452 | 0.050198 | 129.6189 | 0.0090935 | 0.23793 | 0.00041557 | 63.4115 | 0.028764 | 0.25952 | 0.0011513 | 0.11153 | 0.0012748 | 0.22513 | 0.0031962 | 2.8804 | 0.0012636
246.4 | 55.4 | 132.5735 | 0.04967 | 132.1731 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.034701 | 0.14424 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | 2.8208 | 0.00032025 | 132.5226 | 0.041425 | 131.8661 | 0.0080546 | 0.19244 | 8.4239e-05 | 65.2344 | 0.036049 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 2.6024 | 7.2982e-05 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.29589 | 0.0014152 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 0.070087 | 0.004404 | 129.6452 | 0.050198 | 129.6189 | 0.0090935 | 0.23793 | 0.00041557 | 63.4115 | 0.028764 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817 | 0.32251 | 0.0031962 | 2.8804 | 0.0012636
246.6 | 55.6 | 132.6709 | 0.04967 | 132.2706 | 0.0048528 | 0.0053935 | -0.0016068 | 64.9588 | 0.033078 | 0.24166 | 0.00012922 | 0.19109 | 0.00029777 | 0.20087 | 0.0016967 | 2.9182 | 0.00032025 | 132.62 | 0.041425 | 131.8661 | 0.0080546 | 0.19244 | 8.4239e-05 | 65.3318 | 0.036049 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 2.6024 | 7.2982e-05 | 0.30132 | -0.00014601 | 0.29015 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.29589 | 0.0014152 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.070087 | 0.004404 | 129.7426 | 0.050198 | 129.7163 | 0.0090935 | 0.23793 | 0.00041557 | 63.5089 | 0.030387 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 2.8804 | 0.0012636
246.8 | 55.8 | 132.8657 | 0.04967 | 132.1731 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.034701 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.20087 | 0.0016967 | 2.9182 | 0.00032025 | 132.5226 | 0.039801 | 131.8661 | 0.0064315 | 0.19244 | 0.0017072 | 65.3318 | 0.036049 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.2568 | 0.0014439 | 2.6998 | 0.0016967 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.29589 | -0.00020779 | 0.17559 | 0.0015107 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 129.7426 | 0.050198 | 129.7163 | 0.0090935 | 0.23793 | 0.00041557 | 63.4115 | 0.028764 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748 | 0.32251 | 0.0048192 | 2.8804 | 0.0012636
247 | 56 | 133.6449 | 0.048047 | 132.0758 | 0.0064758 | 0.0053935 | 1.6859e-05 | 64.8614 | 0.034701 | 0.24166 | 0.00012922 | 0.19109 | 0.00029777 | 0.10349 | 0.0016967 | 2.8208 | 0.00032025 | 132.62 | 0.039801 | 131.9635 | 0.0080546 | 0.19244 | 8.4239e-05 | 65.3318 | 0.036049 | 0.01988 | 0.0022635 | 0.11562 | -0.00031449 | 0.15942 | 0.0014439 | 2.6998 | 7.2982e-05 | 0.30132 | -0.00014601 | 0.29015 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 129.7426 | 0.050198 | 129.7163 | 0.0090935 | 0.23793 | 0.00041557 | 63.4115 | 0.030387 | 0.1621 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 2.8804 | 0.0012636
247.2 | 56.2 | 133.3527 | 0.04967 | 131.881 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.4718 | 0.036324 | 0.14424 | 0.00012922 | 0.19109 | 0.00029777 | 0.10349 | 0.0016967 | 2.8208 | 0.0019433 | 132.5226 | 0.043048 | 131.9635 | 0.0080546 | 0.19244 | 8.4239e-05 | 65.3318 | 0.034426 | 0.01988 | 0.00064048 | 0.018196 | 0.0013085 | 0.15942 | 0.0014439 | 2.6024 | 7.2982e-05 | 0.30132 | 0.001477 | 0.29015 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.29589 | 0.0014152 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.21368 | 0.0012074 | 0.070087 | 0.004404 | 129.7426 | 0.050198 | 129.7163 | 0.0090935 | 0.23793 | 0.00041557 | 63.4115 | 0.028764 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 2.8804 | 0.0012636
247.4 | 56.4 | 133.0605 | 0.048047 | 132.2706 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.5692 | 0.034701 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | 2.9182 | 0.0019433 | 132.4252 | 0.041425 | 131.8661 | 0.0096782 | 0.19244 | 8.4239e-05 | 65.3318 | 0.036049 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | 0.0014439 | 2.6998 | 0.0016967 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | 0.0015107 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.070087 | 0.0027804 | 129.7426 | 0.050198 | 129.7163 | 0.0090935 | 0.23793 | 0.00041557 | 63.5089 | 0.028764 | 0.1621 | -0.00047174 | 0.20895 | 0.0012748 | 0.32251 | 0.0031962 | 2.8804 | 0.0012636
247.6 | 56.6 | 132.9631 | 0.048047 | 132.2706 | 0.0048528 | 0.0053935 | 1.6859e-05 | 65.0562 | 0.034701 | 0.24166 | 0.0017522 | 0.19109 | 0.00029777 | 0.20087 | 0.0016967 | 2.9182 | 0.00032025 | 131.8409 | 0.041425 | 131.7687 | 0.0080546 | 0.19244 | 8.4239e-05 | 65.3318 | 0.036049 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.2568 | 0.0014439 | 2.6998 | 7.2982e-05 | 0.30132 | -0.00014601 | 0.29015 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 0.070087 | 0.004404 | 129.7426 | 0.050198 | 129.7163 | 0.0090935 | 0.23793 | 0.00041557 | 63.5089 | 0.028764 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748 | 0.22513 | 0.0048192 | 2.9778 | 0.0012636
247.8 | 56.8 | 132.7683 | 0.04967 | 132.2706 | 0.0048528 | 0.0053935 | 1.6859e-05 | 65.0562 | 0.034701 | 0.14424 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 7.2991e-05 | 2.8208 | 0.0019433 | 132.3278 | 0.041425 | 131.8661 | 0.0080546 | 0.095061 | 8.4239e-05 | 65.2344 | 0.036049 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | 0.0014439 | 2.6024 | 7.2982e-05 | 0.30132 | 0.001477 | 0.29015 | 0.00023025 | -0.080196 | -8.9855e-05 | 0.29589 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.006027 | 129.7426 | 0.050198 | 129.7163 | 0.0090935 | 0.23793 | 0.00041557 | 63.5089 | 0.030387 | 0.25952 | -0.00047174 | 0.20895 | -0.00034817 | 0.32251 | 0.0048192 | 2.8804 | 0.0012636
248 | 57 | 132.6709 | 0.04967 | 132.2706 | 0.0048528 | 0.0053935 | 0.0016399 | 64.9588 | 0.034701 | 0.24166 | 0.0017522 | 0.19109 | 0.00029777 | 0.10349 | 0.0016967 | 2.9182 | 0.00032025 | 132.4252 | 0.041425 | 131.8661 | 0.0080546 | 0.19244 | 8.4239e-05 | 65.3318 | 0.036049 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | -0.00017979 | 2.6998 | 7.2982e-05 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.29589 | 0.0014152 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.070087 | 0.004404 | 129.84 | 0.050198 | 129.7163 | 0.0090935 | 0.14051 | 0.00041557 | 63.4115 | 0.028764 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748 | 0.22513 | 0.0031962 | 2.8804 | 0.0012636
248.2 | 57.2 | 132.6709 | 0.04967 | 132.2706 | 0.0048528 | 0.0053935 | 1.6859e-05 | 65.0562 | 0.033078 | 0.14424 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | 2.9182 | 0.0019433 | 132.5226 | 0.041425 | 131.8661 | 0.0080546 | 0.19244 | 8.4239e-05 | 65.2344 | 0.036049 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | 0.0014439 | 2.6998 | 7.2982e-05 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | -0.080196 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.078174 | 0.0015107 | -0.011119 | 0.0009884 | 0.21368 | 0.0012074 | 0.070087 | 0.004404 | 129.84 | 0.050198 | 129.8137 | 0.0090935 | 0.23793 | 0.00041557 | 63.4115 | 0.030387 | 0.1621 | 0.0011513 | 0.20895 | 0.0012748 | 0.22513 | 0.0031962 | 2.8804 | 0.0012636
248.4 | 57.4 | 132.6709 | 0.048047 | 132.3679 | 0.0048528 | 0.0053935 | 1.6859e-05 | 65.0562 | 0.034701 | 0.24166 | 0.00012922 | 0.19109 | 0.00029777 | 0.10349 | 0.0016967 | 2.8208 | 0.00032025 | 132.62 | 0.041425 | 131.9635 | 0.0080546 | 0.19244 | 8.4239e-05 | 65.3318 | 0.036049 | 0.11726 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 2.6998 | 7.2982e-05 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.21368 | 0.0012074 | 0.070087 | 0.004404 | 129.7426 | 0.050198 | 129.7163 | 0.0090935 | 0.23793 | 0.00041557 | 63.5089 | 0.028764 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748 | 0.22513 | 0.0031962 | 2.8804 | 0.0012636
248.6 | 57.6 | 132.6709 | 0.04967 | 132.2706 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.034701 | 0.24166 | 0.00012922 | 0.19109 | 0.00029777 | 0.10349 | 0.0016967 | 2.8208 | 0.00032025 | 132.62 | 0.039801 | 131.9635 | 0.0080546 | 0.19244 | 8.4239e-05 | 65.3318 | 0.036049 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 2.6998 | 0.0016967 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 129.353 | 0.050198 | 129.5215 | 0.0090935 | 0.23793 | 0.00041557 | 63.5089 | 0.030387 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748 | 0.32251 | 0.0031962 | 2.8804 | 0.0028873
248.8 | 57.8 | 132.5735 | 0.048047 | 132.2706 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.034701 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | 2.9182 | 0.0019433 | 132.62 | 0.041425 | 131.9635 | 0.0080546 | 0.19244 | 8.4239e-05 | 65.4292 | 0.036049 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 2.6998 | 0.0016967 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.21368 | 0.0012074 | 0.070087 | 0.004404 | 129.5478 | 0.050198 | 129.5215 | 0.0090935 | 0.23793 | 0.00041557 | 63.3141 | 0.030387 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748 | 0.22513 | 0.0031962 | 2.8804 | 0.0012636
249 | 58 | 132.6709 | 0.04967 | 132.2706 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.034701 | 0.14424 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | 2.8208 | 0.00032025 | 132.62 | 0.039801 | 131.9635 | 0.0080546 | 0.19244 | 8.4239e-05 | 65.3318 | 0.036049 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | 0.0014439 | 2.6024 | 7.2982e-05 | 0.30132 | -0.00014601 | 0.19277 | -0.0013928 | 0.017185 | -8.9855e-05 | 0.29589 | 0.0014152 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.21368 | 0.0012074 | 0.16751 | 0.004404 | 129.5478 | 0.050198 | 129.6189 | 0.0090935 | 0.23793 | 0.00041557 | 63.4115 | 0.028764 | 0.1621 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 2.8804 | 0.0012636
249.2 | 58.2 | 132.6709 | 0.04967 | 132.2706 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.034701 | 0.14424 | 0.00012922 | 0.19109 | 0.00029777 | 0.10349 | 0.0016967 | 2.9182 | 0.0019433 | 132.62 | 0.039801 | 131.9635 | 0.0080546 | 0.095061 | 8.4239e-05 | 65.3318 | 0.036049 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | -0.00017979 | 2.6998 | 0.0016967 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 0.070087 | 0.004404 | 129.7426 | 0.050198 | 129.6189 | 0.0090935 | 0.23793 | 0.00041557 | 63.3141 | 0.030387 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748 | 0.32251 | 0.0031962 | 2.8804 | 0.0012636
249.4 | 58.4 | 132.6709 | 0.048047 | 132.2706 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.033078 | 0.14424 | 0.0017522 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | 2.9182 | 0.00032025 | 132.62 | 0.041425 | 131.9635 | 0.0080546 | 0.19244 | 8.4239e-05 | 65.3318 | 0.034426 | 0.01988 | 0.00064048 | 0.018196 | 0.0013085 | 0.15942 | 0.0014439 | 2.6998 | 0.0016967 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 0.070087 | 0.0027804 | 129.7426 | 0.050198 | 129.7163 | 0.0090935 | 0.23793 | 0.00041557 | 63.4115 | 0.030387 | 0.1621 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0048192 | 2.9778 | 0.0012636
249.6 | 58.6 | 132.5735 | 0.04967 | 132.2706 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.033078 | 0.24166 | 0.00012922 | 0.19109 | 0.00029777 | 0.10349 | 0.0016967 | 2.8208 | 0.00032025 | 132.62 | 0.041425 | 131.9635 | 0.0080546 | 0.095061 | 8.4239e-05 | 65.3318 | 0.036049 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | -0.00017979 | 2.6998 | 0.0016967 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | -0.080196 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.21368 | 0.0012074 | 0.16751 | 0.004404 | 129.7426 | 0.050198 | 129.7163 | 0.0090935 | 0.23793 | 0.00041557 | 63.4115 | 0.030387 | 0.1621 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 2.8804 | 0.0012636
249.8 | 58.8 | 132.5735 | 0.048047 | 132.2706 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.034701 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | 2.9182 | 0.00032025 | 132.62 | 0.041425 | 131.9635 | 0.0064315 | 0.19244 | 8.4239e-05 | 65.3318 | 0.036049 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | -0.00017979 | 2.6998 | 0.0016967 | 0.30132 | 0.001477 | 0.19277 | 0.00023025 | -0.080196 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.21368 | 0.0012074 | 0.070087 | 0.004404 | 129.84 | 0.050198 | 129.8137 | 0.0090935 | 0.23793 | 0.00041557 | 63.5089 | 0.030387 | 0.25952 | -0.00047174 | 0.20895 | 0.0012748 | 0.22513 | 0.0031962 | 2.8804 | 0.0012636
250 | 59 | 132.5735 | 0.04967 | 132.1731 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.034701 | 0.14424 | 0.00012922 | 0.19109 | 0.00029777 | 0.10349 | 0.0016967 | 2.8208 | 0.00032025 | 132.62 | 0.039801 | 131.8661 | 0.0080546 | 0.095061 | 8.4239e-05 | 65.3318 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.2568 | 0.0014439 | 2.6024 | 7.2982e-05 | 0.30132 | 0.001477 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.21368 | 0.0012074 | 0.070087 | 0.004404 | 129.7426 | 0.050198 | 129.7163 | 0.0090935 | 0.23793 | 0.00041557 | 63.4115 | 0.030387 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 2.8804 | 0.0012636
250.2 | 59.2 | 132.6709 | 0.04967 | 132.2706 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.034701 | 0.14424 | 0.00012922 | 0.19109 | 0.00029777 | 0.10349 | 0.0016967 | 2.9182 | 0.00032025 | 132.62 | 0.041425 | 131.9635 | 0.0080546 | 0.19244 | 8.4239e-05 | 65.3318 | 0.036049 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 2.6998 | 7.2982e-05 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | 0.0015332 | 0.19851 | -0.00020779 | 0.17559 | 0.0015107 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.070087 | 0.004404 | 129.84 | 0.051821 | 129.8137 | 0.0090935 | 0.23793 | 0.00041557 | 63.5089 | 0.030387 | 0.25952 | -0.00047174 | 0.20895 | 0.0012748 | 0.22513 | 0.0031962 | 2.8804 | 0.0012636
250.4 | 59.4 | 132.5735 | 0.04967 | 132.2706 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.034701 | 0.14424 | 0.00012922 | 0.19109 | 0.00029777 | 0.10349 | 7.2991e-05 | 2.9182 | 0.00032025 | 132.62 | 0.041425 | 131.9635 | 0.0080546 | 0.19244 | 8.4239e-05 | 65.3318 | 0.036049 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 2.6998 | 7.2982e-05 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.070087 | 0.004404 | 129.84 | 0.051821 | 129.8137 | 0.0090935 | 0.23793 | 0.00041557 | 63.5089 | 0.030387 | 0.1621 | 0.0011513 | 0.20895 | 0.0012748 | 0.32251 | 0.0048192 | 2.8804 | 0.0012636
250.6 | 59.6 | 132.5735 | 0.048047 | 132.1731 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.034701 | 0.14424 | 0.00012922 | 0.28848 | -0.0013259 | 0.10349 | 0.0016967 | 2.8208 | 0.00032025 | 132.62 | 0.039801 | 131.8661 | 0.0080546 | 0.095061 | 8.4239e-05 | 65.3318 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 2.6024 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | 0.0015332 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 129.7426 | 0.051821 | 129.7163 | 0.0090935 | 0.23793 | 0.00041557 | 63.4115 | 0.030387 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748 | 0.22513 | 0.0031962 | 2.8804 | 0.0012636
250.8 | 59.8 | 132.5735 | 0.048047 | 132.2706 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.034701 | 0.24166 | 0.00012922 | 0.19109 | 0.00029777 | 0.20087 | 0.0016967 | 2.8208 | 0.00032025 | 132.62 | 0.039801 | 131.8661 | 0.0080546 | 0.19244 | 8.4239e-05 | 65.3318 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.062 | 0.0014439 | 2.6024 | 7.2982e-05 | 0.30132 | -0.00014601 | 0.19277 | -0.0013928 | -0.080196 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | 0.086261 | -0.0006346 | 0.11626 | -0.00041558 | 0.070087 | 0.004404 | 129.7426 | 0.050198 | 129.8137 | 0.0090935 | 0.23793 | 0.00041557 | 63.5089 | 0.030387 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 2.9778 | 0.0012636
251 | 60 | 132.5735 | 0.048047 | 132.1731 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.033078 | 0.14424 | 0.00012922 | 0.19109 | 0.00029777 | 0.20087 | 0.0016967 | 2.9182 | 0.00032025 | 132.5226 | 0.041425 | 131.8661 | 0.0080546 | 0.19244 | 8.4239e-05 | 65.2344 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 2.6998 | 7.2982e-05 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.078174 | 0.0015107 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.070087 | 0.0027804 | 129.7426 | 0.050198 | 129.7163 | 0.0090935 | 0.33531 | 0.00041557 | 63.5089 | 0.028764 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0048192 | 2.8804 | 0.0012636
251.2 | 60.2 | 132.5735 | 0.04967 | 132.2706 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.033078 | 0.14424 | 0.00012922 | 0.19109 | 0.00029777 | 0.10349 | 7.2991e-05 | 2.9182 | 0.00032025 | 132.5226 | 0.039801 | 131.8661 | 0.0080546 | 0.19244 | 8.4239e-05 | 65.3318 | 0.034426 | -0.0775 | 0.0022635 | -0.079185 | -0.00031449 | 0.15942 | -0.00017979 | 2.6998 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | -0.080196 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.21368 | 0.0012074 | 0.16751 | 0.0027804 | 129.7426 | 0.050198 | 129.7163 | 0.0090935 | 0.23793 | 0.00041557 | 63.5089 | 0.028764 | 0.25952 | 0.0011513 | 0.11153 | -0.00034817 | 0.22513 | 0.0048192 | 2.9778 | 0.0012636
251.4 | 60.4 | 132.5735 | 0.04967 | 132.1731 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.033078 | 0.14424 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | 2.9182 | 0.00032025 | 132.5226 | 0.039801 | 131.8661 | 0.0080546 | 0.19244 | 8.4239e-05 | 65.3318 | 0.036049 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 2.6998 | 7.2982e-05 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | -0.080196 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.070087 | 0.004404 | 129.7426 | 0.050198 | 129.7163 | 0.0090935 | 0.23793 | 0.00041557 | 63.5089 | 0.028764 | 0.1621 | 0.0011513 | 0.20895 | -0.00034817 | 0.32251 | 0.0031962 | 2.8804 | 0.0012636
251.6 | 60.6 | 132.4761 | 0.048047 | 132.1731 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.033078 | 0.14424 | 0.00012922 | 0.19109 | -0.0013259 | 0.10349 | 7.2991e-05 | 2.9182 | -0.0013034 | 132.5226 | 0.039801 | 131.8661 | 0.0080546 | 0.095061 | 8.4239e-05 | 65.2344 | 0.036049 | 0.01988 | 0.00064048 | 0.018196 | -0.00031449 | 0.2568 | 0.0014439 | 2.6998 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | -0.080196 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.070087 | 0.004404 | 129.7426 | 0.050198 | 129.7163 | 0.0090935 | 0.14051 | 0.00041557 | 63.4115 | 0.028764 | 0.1621 | 0.0011513 | 0.11153 | -0.00034817 | 0.22513 | 0.0031962 | 2.8804 | 0.0012636
251.8 | 60.8 | 132.4761 | 0.04967 | 132.1731 | 0.0048528 | -0.092027 | 1.6859e-05 | 64.9588 | 0.033078 | 0.14424 | 0.00012922 | 0.19109 | 0.00029777 | 0.10349 | 0.0016967 | 2.9182 | 0.00032025 | 132.5226 | 0.039801 | 131.8661 | 0.0064315 | 0.19244 | 8.4239e-05 | 65.2344 | 0.034426 | 0.01988 | 0.00064048 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 2.6024 | 7.2982e-05 | 0.30132 | -0.00014601 | 0.19277 | -0.0013928 | 0.017185 | 0.0015332 | 0.19851 | -0.00020779 | 0.17559 | 0.0015107 | -0.011119 | -0.0006346 | 0.11626 | 0.0012074 | 0.070087 | 0.004404 | 129.7426 | 0.050198 | 129.7163 | 0.0090935 | 0.23793 | 0.00041557 | 63.4115 | 0.028764 | 0.1621 | -0.00047174 | 0.11153 | -0.00034817 | 0.22513 | 0.0031962 | 2.8804 | -0.0003594
252 | 61 | 132.4761 | 0.048047 | 132.1731 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.034701 | 0.14424 | 0.00012922 | 0.19109 | 0.00029777 | 0.10349 | 7.2991e-05 | 2.9182 | 0.00032025 | 132.4252 | 0.039801 | 131.8661 | 0.0080546 | 0.095061 | 8.4239e-05 | 65.2344 | 0.034426 | -0.0775 | 0.0022635 | 0.018196 | -0.00031449 | 0.062 | -0.00017979 | 2.6998 | 7.2982e-05 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.0017353 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.070087 | 0.0027804 | 129.6452 | 0.050198 | 129.6189 | 0.0090935 | 0.23793 | 0.00041557 | 63.4115 | 0.028764 | 0.1621 | -0.00047174 | 0.11153 | -0.00034817 | 0.22513 | 0.0031962 | 2.8804 | 0.0012636
252.2 | 61.2 | 132.5735 | 0.048047 | 132.1731 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.034701 | 0.14424 | 0.00012922 | 0.19109 | -0.0013259 | 0.0060648 | 7.2991e-05 | 2.9182 | 0.00032025 | 132.5226 | 0.039801 | 131.8661 | 0.0080546 | 0.19244 | -0.0015388 | 65.3318 | 0.034426 | 0.01988 | 0.00064048 | 0.018196 | 0.0013085 | 0.15942 | -0.00017979 | 2.6998 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | -0.080196 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | -0.00041558 | 0.070087 | 0.0027804 | 129.7426 | 0.050198 | 129.8137 | 0.0090935 | 0.23793 | 0.00041557 | 63.5089 | 0.028764 | 0.25952 | 0.0011513 | 0.11153 | -0.00034817 | 0.22513 | 0.0031962 | 2.9778 | 0.0012636
252.4 | 61.4 | 132.5735 | 0.048047 | 132.1731 | 0.0048528 | -0.092027 | 1.6859e-05 | 64.9588 | 0.033078 | 0.14424 | 0.00012922 | 0.19109 | -0.0013259 | 0.10349 | 7.2991e-05 | 2.9182 | 0.00032025 | 132.5226 | 0.039801 | 131.8661 | 0.0080546 | 0.19244 | 8.4239e-05 | 65.2344 | 0.034426 | -0.0775 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 2.6998 | 7.2982e-05 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | -0.080196 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.070087 | 0.0027804 | 129.7426 | 0.050198 | 129.7163 | 0.0090935 | 0.14051 | 0.00041557 | 63.4115 | 0.028764 | 0.1621 | 0.0011513 | 0.11153 | -0.00034817 | 0.22513 | 0.0031962 | 2.8804 | 0.0012636
252.6 | 61.6 | 132.6709 | 0.048047 | 132.1731 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.033078 | 0.14424 | 0.00012922 | 0.19109 | 0.00029777 | 0.0060648 | 7.2991e-05 | 2.9182 | -0.0013034 | 132.5226 | 0.039801 | 131.9635 | 0.0080546 | 0.095061 | -0.0015388 | 65.2344 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | -0.00017979 | 2.6998 | 7.2982e-05 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | 0.0015332 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | -0.0006346 | 0.11626 | 0.0012074 | 0.070087 | 0.0027804 | 129.7426 | 0.050198 | 129.8137 | 0.0090935 | 0.23793 | 0.00041557 | 63.5089 | 0.028764 | 0.1621 | 0.0011513 | 0.11153 | -0.00034817 | 0.22513 | 0.0031962 | 2.8804 | 0.0012636
252.8 | 61.8 | 132.5735 | 0.048047 | 132.1731 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.034701 | 0.14424 | 0.00012922 | 0.19109 | -0.0013259 | 0.10349 | 7.2991e-05 | 2.9182 | -0.0013034 | 132.5226 | 0.039801 | 131.8661 | 0.0080546 | 0.095061 | 8.4239e-05 | 65.3318 | 0.036049 | 0.01988 | 0.00064048 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 2.6998 | 7.2982e-05 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | -0.080196 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.078174 | -0.00011232 | -0.011119 | -0.0006346 | 0.11626 | -0.00041558 | 0.070087 | 0.004404 | 129.7426 | 0.048575 | 129.7163 | 0.0090935 | 0.23793 | -0.0012074 | 63.4115 | 0.028764 | 0.1621 | 0.0011513 | 0.11153 | -0.00034817 | 0.22513 | 0.0031962 | 2.8804 | 0.0012636
253 | 62 | 132.5735 | 0.048047 | 132.1731 | 0.0048528 | 0.0053935 | 1.6859e-05 | 65.0562 | 0.034701 | 0.24166 | 0.00012922 | 0.19109 | 0.00029777 | 0.10349 | 7.2991e-05 | 2.9182 | 0.00032025 | 132.5226 | 0.039801 | 131.8661 | 0.0064315 | 0.095061 | 8.4239e-05 | 65.3318 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.2568 | -0.00017979 | 2.6998 | 7.2982e-05 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.070087 | 0.0027804 | 129.7426 | 0.048575 | 129.7163 | 0.0074705 | 0.23793 | -0.0012074 | 63.5089 | 0.028764 | 0.1621 | -0.00047174 | 0.11153 | -0.00034817 | 0.22513 | 0.0031962 | 2.8804 | -0.0003594
253.2 | 62.2 | 132.5735 | 0.048047 | 132.1731 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.034701 | 0.14424 | 0.00012922 | 0.19109 | 0.00029777 | 0.0060648 | 7.2991e-05 | 2.9182 | 0.00032025 | 132.4252 | 0.039801 | 131.8661 | 0.0064315 | 0.095061 | 8.4239e-05 | 65.2344 | 0.036049 | 0.01988 | 0.00064048 | -0.079185 | -0.00031449 | 0.15942 | -0.00017979 | 2.6998 | 7.2982e-05 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.21368 | 0.0012074 | 0.070087 | 0.004404 | 129.7426 | 0.048575 | 129.7163 | 0.0090935 | 0.14051 | 0.00041557 | 63.4115 | 0.028764 | 0.1621 | 0.0011513 | 0.11153 | -0.00034817 | 0.22513 | 0.0031962 | 2.8804 | -0.0003594
253.4 | 62.4 | 132.4761 | 0.048047 | 132.1731 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.033078 | 0.24166 | 0.00012922 | 0.19109 | 0.00029777 | 0.10349 | 7.2991e-05 | 2.9182 | -0.0013034 | 132.4252 | 0.038178 | 131.8661 | 0.0064315 | 0.095061 | 8.4239e-05 | 65.2344 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 2.6998 | 7.2982e-05 | 0.30132 | 0.001477 | 0.19277 | 0.00023025 | 0.017185 | 0.0015332 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | -0.00041558 | 0.070087 | 0.0027804 | 129.7426 | 0.048575 | 129.7163 | 0.0090935 | 0.23793 | 0.00041557 | 63.4115 | 0.028764 | 0.1621 | -0.00047174 | 0.20895 | -0.00034817 | 0.12771 | 0.0031962 | 2.8804 | -0.0003594
253.6 | 62.6 | 132.5735 | 0.048047 | 132.1731 | 0.0048528 | 0.0053935 | 0.0016399 | 65.0562 | 0.033078 | 0.14424 | 0.00012922 | 0.19109 | 0.00029777 | 0.10349 | 7.2991e-05 | 2.9182 | 0.00032025 | 132.5226 | 0.038178 | 131.8661 | 0.0064315 | 0.19244 | 8.4239e-05 | 65.2344 | 0.034426 | 0.01988 | 0.00064048 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 2.6998 | 7.2982e-05 | 0.30132 | -0.00014601 | 0.19277 | -0.0013928 | 0.017185 | -8.9855e-05 | 0.29589 | -0.00020779 | 0.078174 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.070087 | 0.004404 | 129.7426 | 0.050198 | 129.7163 | 0.0090935 | 0.14051 | 0.00041557 | 63.4115 | 0.030387 | 0.1621 | -0.00047174 | 0.11153 | -0.00034817 | 0.12771 | 0.0015725 | 2.8804 | -0.0003594
253.8 | 62.8 | 132.4761 | 0.048047 | 132.1731 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.033078 | 0.14424 | 0.00012922 | 0.19109 | -0.0013259 | 0.0060648 | 7.2991e-05 | 2.9182 | 0.00032025 | 132.4252 | 0.038178 | 131.7687 | 0.0064315 | 0.19244 | 8.4239e-05 | 65.2344 | 0.034426 | -0.0775 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 2.6998 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.070087 | 0.0027804 | 129.6452 | 0.048575 | 129.6189 | 0.0074705 | 0.23793 | 0.00041557 | 63.4115 | 0.028764 | 0.1621 | -0.00047174 | 0.11153 | -0.00034817 | 0.12771 | 0.0015725 | 2.8804 | -0.0003594
254 | 63 | 132.4761 | 0.04967 | 132.0758 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.033078 | 0.14424 | 0.00012922 | 0.093675 | 0.00029777 | 0.0060648 | -0.00155 | 2.9182 | -0.0013034 | 132.4252 | 0.038178 | 131.7687 | 0.0064315 | 0.095061 | 8.4239e-05 | 65.2344 | 0.034426 | 0.01988 | 0.00064048 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 2.6998 | 7.2982e-05 | 0.30132 | -0.00014601 | 0.29015 | -0.0013928 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | -0.0006346 | 0.11626 | 0.0012074 | 0.070087 | 0.0027804 | 129.5478 | 0.048575 | 129.6189 | 0.0090935 | 0.23793 | 0.00041557 | 63.4115 | 0.028764 | 0.1621 | -0.00047174 | 0.11153 | -0.00034817 | 0.22513 | 0.0031962 | 2.8804 | -0.0003594
254.2 | 63.2 | 132.4761 | 0.048047 | 132.0758 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.033078 | 0.14424 | 0.00012922 | 0.19109 | 0.00029777 | 0.0060648 | 7.2991e-05 | 2.9182 | 0.00032025 | 132.4252 | 0.039801 | 131.7687 | 0.0064315 | 0.19244 | 8.4239e-05 | 65.2344 | 0.036049 | 0.01988 | 0.00064048 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 2.6998 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | -0.0006346 | 0.11626 | 0.0012074 | 0.070087 | 0.0027804 | 129.6452 | 0.048575 | 129.6189 | 0.0074705 | 0.23793 | 0.00041557 | 63.4115 | 0.02714 | 0.1621 | -0.00047174 | 0.11153 | -0.00034817 | 0.22513 | 0.0015725 | 2.8804 | -0.0003594
254.4 | 63.4 | 132.4761 | 0.048047 | 132.0758 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.033078 | 0.14424 | 0.00012922 | 0.19109 | -0.0013259 | 0.10349 | 7.2991e-05 | 2.9182 | -0.0013034 | 132.4252 | 0.038178 | 131.7687 | 0.0064315 | 0.19244 | 8.4239e-05 | 65.2344 | 0.034426 | -0.0775 | 0.00064048 | -0.079185 | -0.00031449 | 0.062 | -0.00017979 | 2.6998 | 7.2982e-05 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | -0.080196 | 0.0015332 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | 0.086261 | -0.0006346 | 0.11626 | 0.0012074 | 0.070087 | 0.0027804 | 129.6452 | 0.048575 | 129.6189 | 0.0074705 | 0.14051 | -0.0012074 | 63.4115 | 0.028764 | 0.1621 | -0.00047174 | 0.11153 | -0.0019718 | 0.12771 | 0.0015725 | 2.8804 | -0.0003594
254.6 | 63.6 | 132.4761 | 0.048047 | 132.1731 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.033078 | 0.14424 | -0.0014944 | 0.19109 | 0.00029777 | 0.10349 | 7.2991e-05 | 2.9182 | 0.00032025 | 132.4252 | 0.038178 | 131.7687 | 0.0064315 | 0.19244 | 8.4239e-05 | 65.2344 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.062 | -0.00017979 | 2.6998 | 7.2982e-05 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.078174 | -0.00011232 | -0.011119 | -0.0006346 | 0.11626 | -0.00041558 | 0.070087 | 0.0027804 | 129.6452 | 0.048575 | 129.6189 | 0.0074705 | 0.23793 | -0.0012074 | 63.4115 | 0.02714 | 0.1621 | -0.00047174 | 0.11153 | -0.00034817 | 0.12771 | 0.0015725 | 2.8804 | -0.0003594
254.8 | 63.8 | 132.4761 | 0.048047 | 132.0758 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.033078 | 0.14424 | 0.00012922 | 0.19109 | 0.00029777 | 0.10349 | 7.2991e-05 | 3.0156 | -0.0013034 | 132.4252 | 0.038178 | 131.7687 | 0.0064315 | 0.095061 | 8.4239e-05 | 65.2344 | 0.034426 | -0.0775 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 2.6998 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | 0.0015332 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.070087 | 0.0027804 | 129.5478 | 0.048575 | 129.6189 | 0.0074705 | 0.23793 | -0.0012074 | 63.4115 | 0.02714 | 0.1621 | -0.00047174 | 0.11153 | -0.00034817 | 0.12771 | 0.0031962 | 2.9778 | -0.0003594
255 | 64 | 132.4761 | 0.048047 | 132.1731 | 0.0048528 | 0.0053935 | 1.6859e-05 | 65.0562 | 0.033078 | 0.14424 | 0.00012922 | 0.093675 | 0.00029777 | 0.10349 | 7.2991e-05 | 2.9182 | -0.0013034 | 132.4252 | 0.039801 | 131.8661 | 0.0064315 | 0.095061 | 8.4239e-05 | 65.2344 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.062 | -0.00017979 | 2.6998 | -0.00155 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.078174 | -0.00011232 | -0.011119 | -0.0006346 | 0.11626 | 0.0012074 | 0.070087 | 0.0027804 | 129.6452 | 0.048575 | 129.6189 | 0.0074705 | 0.14051 | 0.00041557 | 63.4115 | 0.02714 | 0.1621 | -0.00047174 | 0.11153 | -0.00034817 | 0.12771 | 0.0015725 | 2.8804 | -0.0003594
255.2 | 64.2 | 132.4761 | 0.048047 | 132.0758 | 0.0032298 | 0.0053935 | -0.0016068 | 64.9588 | 0.033078 | 0.14424 | 0.00012922 | 0.19109 | 0.00029777 | 0.10349 | 7.2991e-05 | 2.9182 | 0.00032025 | 132.3278 | 0.039801 | 131.7687 | 0.0064315 | 0.19244 | 8.4239e-05 | 65.2344 | 0.034426 | -0.0775 | 0.00064048 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 2.6998 | 7.2982e-05 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | -0.00041558 | 0.070087 | 0.0027804 | 129.6452 | 0.048575 | 129.6189 | 0.0074705 | 0.14051 | -0.0012074 | 63.4115 | 0.02714 | 0.1621 | -0.00047174 | 0.20895 | -0.00034817 | 0.22513 | 0.0015725 | 2.8804 | -0.0003594
255.4 | 64.4 | 132.4761 | 0.048047 | 132.1731 | 0.0032298 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.033078 | 0.14424 | 0.00012922 | 0.19109 | 0.00029777 | 0.10349 | 7.2991e-05 | 3.0156 | -0.0013034 | 132.3278 | 0.039801 | 131.7687 | 0.0064315 | 0.19244 | 8.4239e-05 | 65.2344 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 2.6998 | 7.2982e-05 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | -0.0006346 | 0.11626 | -0.00041558 | 0.070087 | 0.0027804 | 129.5478 | 0.048575 | 129.5215 | 0.0074705 | 0.14051 | 0.00041557 | 63.4115 | 0.028764 | 0.1621 | -0.00047174 | 0.11153 | -0.00034817 | 0.32251 | 0.0015725 | 2.8804 | -0.0003594
255.6 | 64.6 | 132.4761 | 0.048047 | 132.0758 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.033078 | 0.14424 | -0.0014944 | 0.19109 | 0.00029777 | 0.0060648 | 0.0016967 | 2.9182 | 0.00032025 | 132.4252 | 0.038178 | 131.6713 | 0.0064315 | 0.095061 | 8.4239e-05 | 65.2344 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.062 | -0.00017979 | 2.6998 | 7.2982e-05 | 0.2039 | 0.001477 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | -0.0006346 | 0.11626 | 0.0012074 | 0.070087 | 0.004404 | 129.6452 | 0.048575 | 129.5215 | 0.0074705 | 0.23793 | 0.00041557 | 63.4115 | 0.02714 | 0.1621 | -0.00047174 | 0.11153 | -0.00034817 | 0.22513 | 0.0031962 | 2.8804 | 0.0012636
255.8 | 64.8 | 132.3787 | 0.048047 | 132.0758 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.034701 | 0.14424 | -0.0014944 | 0.19109 | 0.00029777 | 0.10349 | 7.2991e-05 | 2.9182 | -0.0013034 | 132.3278 | 0.038178 | 131.7687 | 0.0064315 | 0.19244 | 8.4239e-05 | 65.2344 | 0.034426 | 0.01988 | 0.00064048 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 2.6998 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | -0.0013928 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | -0.0006346 | 0.11626 | -0.00041558 | 0.070087 | 0.0027804 | 129.5478 | 0.048575 | 129.5215 | 0.0074705 | 0.14051 | 0.00041557 | 63.4115 | 0.028764 | 0.1621 | -0.00047174 | 0.11153 | -0.00034817 | 0.12771 | 0.0031962 | 2.8804 | -0.0003594
256 | 65 | 132.3787 | 0.046423 | 131.9783 | 0.0048528 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.033078 | 0.24166 | 0.00012922 | 0.19109 | 0.00029777 | 0.10349 | 7.2991e-05 | 3.0156 | 0.00032025 | 132.3278 | 0.038178 | 131.6713 | 0.0064315 | 0.19244 | 8.4239e-05 | 65.2344 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 2.6998 | -0.00155 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | 0.0015107 | -0.011119 | -0.0006346 | 0.11626 | 0.0012074 | 0.070087 | 0.0027804 | 129.5478 | 0.048575 | 129.5215 | 0.0074705 | 0.14051 | 0.00041557 | 63.3141 | 0.02714 | 0.1621 | -0.00047174 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 2.8804 | -0.0003594
256.2 | 65.2 | 132.3787 | 0.048047 | 132.0758 | 0.0032298 | -0.092027 | 1.6859e-05 | 64.9588 | 0.033078 | 0.14424 | 0.00012922 | 0.19109 | 0.00029777 | 0.10349 | 7.2991e-05 | 2.9182 | 0.00032025 | 132.3278 | 0.038178 | 131.6713 | 0.0064315 | 0.19244 | 8.4239e-05 | 65.137 | 0.032803 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.062 | -0.00017979 | 2.6998 | -0.00155 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.078174 | -0.00011232 | -0.011119 | -0.0006346 | 0.11626 | -0.00041558 | 0.070087 | 0.0027804 | 129.5478 | 0.048575 | 129.5215 | 0.0074705 | 0.14051 | 0.00041557 | 63.3141 | 0.028764 | 0.1621 | -0.00047174 | 0.11153 | -0.00034817 | 0.22513 | 0.0031962 | 2.8804 | 0.0012636
256.4 | 65.4 | 132.3787 | 0.046423 | 132.0758 | 0.0032298 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.033078 | 0.14424 | 0.00012922 | 0.19109 | 0.00029777 | 0.10349 | 7.2991e-05 | 3.0156 | 0.00032025 | 132.3278 | 0.038178 | 131.6713 | 0.0064315 | 0.19244 | 8.4239e-05 | 65.2344 | 0.034426 | 0.01988 | 0.00064048 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 2.6998 | -0.00155 | 0.30132 | -0.00014601 | 0.095394 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.078174 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | -0.00041558 | 0.070087 | 0.004404 | 129.5478 | 0.048575 | 129.5215 | 0.0074705 | 0.14051 | -0.0012074 | 63.4115 | 0.02714 | 0.1621 | -0.00047174 | 0.11153 | -0.00034817 | 0.12771 | 0.0031962 | 2.8804 | -0.0003594
256.6 | 65.6 | 132.3787 | 0.046423 | 131.9783 | 0.0032298 | 0.0053935 | 0.0016399 | 64.8614 | 0.031455 | 0.14424 | 0.00012922 | 0.19109 | 0.00029777 | 0.10349 | 7.2991e-05 | 2.9182 | 0.00032025 | 132.2304 | 0.038178 | 131.6713 | 0.0048085 | 0.095061 | 8.4239e-05 | 65.2344 | 0.034426 | 0.01988 | 0.00064048 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 2.6998 | 7.2982e-05 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.10109 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | -0.00041558 | 0.070087 | 0.0027804 | 129.5478 | 0.048575 | 129.5215 | 0.0074705 | 0.23793 | -0.0012074 | 63.4115 | 0.028764 | 0.1621 | -0.00047174 | 0.11153 | -0.00034817 | 0.12771 | 0.0031962 | 2.8804 | -0.0003594
256.8 | 65.8 | 132.3787 | 0.046423 | 131.9783 | 0.0032298 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.033078 | 0.14424 | 0.00012922 | 0.19109 | 0.00029777 | 0.0060648 | 0.0016967 | 2.9182 | 0.00032025 | 132.3278 | 0.038178 | 131.574 | 0.0064315 | 0.19244 | 8.4239e-05 | 65.137 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 2.7972 | 7.2982e-05 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | 0.0015332 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | -0.0006346 | 0.11626 | -0.00041558 | 0.070087 | 0.0027804 | 129.5478 | 0.046952 | 129.5215 | 0.0074705 | 0.23793 | -0.0012074 | 63.3141 | 0.02714 | 0.1621 | -0.00047174 | 0.11153 | -0.00034817 | 0.22513 | 0.0031962 | 2.9778 | -0.0003594
257 | 66 | 132.3787 | 0.048047 | 132.0758 | 0.0032298 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.033078 | 0.14424 | 0.00012922 | 0.19109 | 0.00029777 | 0.10349 | 7.2991e-05 | 2.9182 | 0.00032025 | 132.2304 | 0.036554 | 131.6713 | 0.0048085 | 0.095061 | 8.4239e-05 | 65.2344 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 2.6998 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | -0.080196 | 0.0015332 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | -0.00041558 | 0.070087 | 0.0027804 | 129.4504 | 0.046952 | 129.5215 | 0.0074705 | 0.23793 | -0.0012074 | 63.3141 | 0.028764 | 0.1621 | 0.0011513 | 0.11153 | -0.00034817 | 0.22513 | 0.0031962 | 2.8804 | -0.0003594
257.2 | 66.2 | 132.3787 | 0.046423 | 132.0758 | 0.0032298 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.033078 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | 3.0156 | 0.00032025 | 132.2304 | 0.038178 | 131.6713 | 0.0064315 | 0.095061 | 8.4239e-05 | 65.137 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 2.6998 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | -0.080196 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | -0.0006346 | 0.11626 | -0.00041558 | 0.070087 | 0.004404 | 129.4504 | 0.048575 | 129.5215 | 0.0058469 | 0.23793 | 0.00041557 | 63.3141 | 0.02714 | 0.1621 | -0.00047174 | 0.11153 | -0.00034817 | 0.22513 | 0.0015725 | 2.8804 | -0.0003594
257.4 | 66.4 | 132.3787 | 0.046423 | 132.0758 | 0.0032298 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.033078 | 0.14424 | 0.00012922 | 0.19109 | -0.0013259 | 0.10349 | 0.0016967 | 3.0156 | 0.00032025 | 132.3278 | 0.038178 | 131.6713 | 0.0048085 | 0.095061 | 8.4239e-05 | 65.2344 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 2.6998 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | 0.0015107 | 0.086261 | -0.0006346 | 0.11626 | -0.00041558 | 0.070087 | 0.004404 | 129.4504 | 0.046952 | 129.5215 | 0.0074705 | 0.23793 | -0.0012074 | 63.3141 | 0.02714 | 0.064722 | -0.00047174 | 0.11153 | -0.00034817 | 0.22513 | 0.0031962 | 2.9778 | -0.0003594
257.6 | 66.6 | 132.3787 | 0.046423 | 131.9783 | 0.0032298 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.033078 | 0.14424 | 0.00012922 | 0.19109 | 0.00029777 | 0.10349 | 0.0016967 | 3.0156 | 0.00032025 | 132.2304 | 0.036554 | 131.574 | 0.0048085 | 0.19244 | 8.4239e-05 | 65.137 | 0.032803 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 2.6998 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | -0.0006346 | 0.11626 | 0.0012074 | 0.070087 | 0.0027804 | 129.4504 | 0.046952 | 129.5215 | 0.0058469 | 0.23793 | 0.00041557 | 63.3141 | 0.028764 | 0.1621 | -0.00047174 | 0.11153 | -0.00034817 | 0.22513 | 0.0031962 | 2.8804 | 0.0012636
257.8 | 66.8 | 132.3787 | 0.046423 | 131.9783 | 0.0016062 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.033078 | 0.14424 | 0.00012922 | 0.19109 | -0.0013259 | 0.20087 | 7.2991e-05 | 3.0156 | 0.00032025 | 132.2304 | 0.036554 | 131.6713 | 0.0048085 | 0.19244 | 8.4239e-05 | 65.137 | 0.032803 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.062 | -0.00017979 | 2.7972 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | -0.0006346 | 0.018878 | -0.00041558 | 0.070087 | 0.004404 | 129.4504 | 0.046952 | 129.4241 | 0.0074705 | 0.23793 | 0.00041557 | 63.3141 | 0.028764 | 0.1621 | -0.00047174 | 0.11153 | -0.00034817 | 0.22513 | 0.0031962 | 2.9778 | -0.0003594
258 | 67 | 132.2813 | 0.046423 | 131.881 | 0.0016062 | 0.0053935 | 1.6859e-05 | 64.8614 | 0.033078 | 0.14424 | -0.0014944 | 0.28848 | 0.00029777 | 0.10349 | 7.2991e-05 | 3.0156 | 0.00032025 | 132.2304 | 0.036554 | 131.574 | 0.0048085 | 0.19244 | 8.4239e-05 | 65.137 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.2568 | -0.00017979 | 2.7972 | -0.00155 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | -0.080196 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.018878 | 0.0012074 | 0.070087 | 0.004404 | 129.4504 | 0.046952 | 129.4241 | 0.0058469 | 0.14051 | -0.0012074 | 63.2167 | 0.028764 | 0.1621 | -0.00047174 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 2.8804 | 0.0012636
258.2 | 67.2 | 132.2813 | 0.046423 | 131.9783 | 0.0032298 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.033078 | 0.24166 | -0.0014944 | 0.28848 | -0.0013259 | 0.10349 | 7.2991e-05 | 3.0156 | 0.00032025 | 132.2304 | 0.038178 | 131.574 | 0.0048085 | 0.19244 | 8.4239e-05 | 65.137 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | -0.00017979 | 2.7972 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.21368 | -0.00041558 | 0.070087 | 0.004404 | 129.4504 | 0.046952 | 129.4241 | 0.0058469 | 0.23793 | 0.00041557 | 63.3141 | 0.028764 | 0.1621 | -0.00047174 | 0.11153 | -0.00034817 | 0.22513 | 0.0031962 | 2.9778 | -0.0003594
258.4 | 67.4 | 132.3787 | 0.0448 | 131.9783 | 0.0016062 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.033078 | 0.14424 | 0.00012922 | 0.19109 | 0.00029777 | 0.10349 | 7.2991e-05 | 3.113 | 0.00032025 | 132.2304 | 0.036554 | 131.6713 | 0.0031849 | 0.19244 | 8.4239e-05 | 65.137 | 0.032803 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | -0.00017979 | 2.7972 | 7.2982e-05 | 0.30132 | -0.00014601 | 0.095394 | 0.00023025 | 0.017185 | 0.0015332 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.070087 | 0.0027804 | 129.4504 | 0.046952 | 129.4241 | 0.0058469 | 0.23793 | 0.00041557 | 63.2167 | 0.02714 | 0.1621 | -0.00047174 | 0.11153 | -0.00034817 | 0.22513 | 0.0031962 | 2.9778 | -0.0003594
258.6 | 67.6 | 132.3787 | 0.0448 | 131.9783 | 0.0016062 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.033078 | 0.14424 | 0.00012922 | 0.19109 | 0.00029777 | 0.10349 | 0.0016967 | 2.9182 | 0.00032025 | 132.2304 | 0.036554 | 131.574 | 0.0031849 | 0.19244 | 8.4239e-05 | 65.137 | 0.032803 | -0.0775 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 2.7972 | 7.2982e-05 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | -0.080196 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | -0.0006346 | 0.11626 | -0.00041558 | 0.070087 | 0.004404 | 129.4504 | 0.045329 | 129.4241 | 0.0058469 | 0.23793 | -0.0012074 | 63.3141 | 0.02714 | 0.1621 | -0.00047174 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 2.9778 | -0.0003594
258.8 | 67.8 | 132.3787 | 0.0448 | 131.9783 | 0.0016062 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.033078 | 0.14424 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 7.2991e-05 | 3.0156 | 0.00032025 | 132.2304 | 0.036554 | 131.574 | 0.0031849 | 0.19244 | 8.4239e-05 | 65.137 | 0.032803 | 0.01988 | 0.00064048 | -0.079185 | -0.00031449 | 0.15942 | -0.00017979 | 2.7972 | 7.2982e-05 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | 0.0015107 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.070087 | 0.0027804 | 129.4504 | 0.046952 | 129.4241 | 0.0058469 | 0.23793 | 0.00041557 | 63.3141 | 0.02714 | 0.25952 | -0.00047174 | 0.11153 | -0.00034817 | 0.22513 | 0.0031962 | 2.9778 | -0.0003594
259 | 68 | 132.3787 | 0.046423 | 131.9783 | 0.0016062 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.033078 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | 3.0156 | 0.00032025 | 132.2304 | 0.036554 | 131.574 | 0.0031849 | 0.19244 | 8.4239e-05 | 65.137 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 2.6998 | 7.2982e-05 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | 0.086261 | -0.0006346 | 0.11626 | -0.00041558 | 0.070087 | 0.004404 | 129.4504 | 0.046952 | 129.3268 | 0.0058469 | 0.23793 | 0.00041557 | 63.2167 | 0.02714 | 0.1621 | -0.00047174 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 2.9778 | 0.0012636
259.2 | 68.2 | 132.3787 | 0.043177 | 131.9783 | 0.0016062 | 0.0053935 | 1.6859e-05 | 65.0562 | 0.031455 | 0.14424 | 0.00012922 | 0.19109 | 0.0019208 | 0.10349 | 0.0016967 | 3.0156 | 0.00032025 | 132.2304 | 0.034931 | 131.574 | 0.0031849 | 0.19244 | 8.4239e-05 | 65.137 | 0.032803 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 2.7972 | 0.0016967 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | 0.0015332 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | -0.0006346 | 0.11626 | -0.00041558 | 0.070087 | 0.004404 | 129.353 | 0.045329 | 129.4241 | 0.0042238 | 0.14051 | 0.00041557 | 63.3141 | 0.02714 | 0.1621 | -0.00047174 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 2.9778 | 0.0012636
259.4 | 68.4 | 132.3787 | 0.043177 | 131.9783 | 0.0016062 | 0.0053935 | 1.6859e-05 | 65.0562 | 0.033078 | 0.14424 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 7.2991e-05 | 2.9182 | 0.00032025 | 132.133 | 0.034931 | 131.574 | 0.0031849 | 0.095061 | 8.4239e-05 | 65.137 | 0.032803 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 2.6998 | 7.2982e-05 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.10109 | -0.00020779 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.018878 | 0.0012074 | 0.070087 | 0.004404 | 129.353 | 0.045329 | 129.4241 | 0.0042238 | 0.23793 | -0.0012074 | 63.3141 | 0.02714 | 0.1621 | -0.00047174 | 0.11153 | -0.00034817 | 0.22513 | 0.0015725 | 2.9778 | -0.0003594
259.6 | 68.6 | 132.3787 | 0.0448 | 131.9783 | 0.0016062 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.033078 | 0.24166 | 0.00012922 | 0.19109 | 0.00029777 | 0.10349 | 0.0016967 | 3.0156 | 0.00032025 | 132.2304 | 0.034931 | 131.574 | 0.0031849 | 0.095061 | 8.4239e-05 | 65.137 | 0.032803 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 2.7972 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | -0.0013928 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.078174 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | -0.00041558 | 0.070087 | 0.0027804 | 129.353 | 0.045329 | 129.3268 | 0.0042238 | 0.23793 | 0.00041557 | 63.3141 | 0.02714 | 0.1621 | -0.00047174 | 0.11153 | -0.00034817 | 0.12771 | 0.0031962 | 2.9778 | -0.0003594
259.8 | 68.8 | 132.3787 | 0.0448 | 131.9783 | 0.0016062 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.033078 | 0.24166 | 0.00012922 | 0.28848 | -0.0013259 | 0.10349 | 0.0016967 | 3.0156 | 0.00032025 | 132.133 | 0.034931 | 131.4765 | 0.0015619 | 0.19244 | 8.4239e-05 | 65.137 | 0.032803 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.2568 | -0.00017979 | 2.6998 | 7.2982e-05 | 0.30132 | 0.001477 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.17559 | 0.0015107 | -0.011119 | -0.0006346 | 0.11626 | -0.00041558 | 0.070087 | 0.004404 | 129.353 | 0.045329 | 129.3268 | 0.0042238 | 0.23793 | -0.0012074 | 63.3141 | 0.02714 | 0.1621 | 0.0011513 | 0.11153 | -0.00034817 | 0.22513 | 0.0031962 | 2.9778 | 0.0012636
260 | 69 | 132.1839 | 0.043177 | 131.7836 | 0.0016062 | 0.0053935 | 1.6859e-05 | 64.8614 | 0.031455 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 7.2991e-05 | 3.113 | 0.00032025 | 131.9382 | 0.034931 | 131.3792 | 0.0015619 | 0.19244 | 8.4239e-05 | 65.0397 | 0.032803 | -0.0775 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 2.7972 | 7.2982e-05 | 0.30132 | -0.00014601 | 0.29015 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.070087 | 0.004404 | 129.2556 | 0.045329 | 129.2293 | 0.0026002 | 0.23793 | 0.00041557 | 63.2167 | 0.02714 | 0.1621 | 0.0011513 | 0.11153 | -0.00034817 | 0.22513 | 0.0031962 | 2.8804 | 0.0012636
260.2 | 69.2 | 132.2813 | 0.0448 | 131.9783 | 0.0016062 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.031455 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | 3.113 | 0.00032025 | 132.0357 | 0.034931 | 131.4765 | 0.0015619 | 0.19244 | 8.4239e-05 | 65.137 | 0.032803 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 2.7972 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.078174 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.070087 | 0.0027804 | 129.2556 | 0.045329 | 129.3268 | 0.0026002 | 0.23793 | 0.00041557 | 63.2167 | 0.02714 | 0.1621 | 0.0011513 | 0.11153 | -0.00034817 | 0.22513 | 0.0031962 | 2.9778 | 0.0012636
260.4 | 69.4 | 132.2813 | 0.043177 | 131.881 | 0.0016062 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.031455 | 0.14424 | 0.00012922 | 0.19109 | 0.00029777 | 0.10349 | 0.0016967 | 3.0156 | 0.00032025 | 132.133 | 0.033308 | 131.4765 | 0.0015619 | 0.19244 | 8.4239e-05 | 65.137 | 0.032803 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 2.6998 | 7.2982e-05 | 0.30132 | -0.00014601 | 0.29015 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.29589 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.070087 | 0.0027804 | 129.2556 | 0.045329 | 129.3268 | 0.0026002 | 0.23793 | 0.00041557 | 63.3141 | 0.025517 | 0.1621 | -0.00047174 | 0.11153 | -0.00034817 | 0.22513 | 0.0031962 | 2.9778 | -0.0003594
260.6 | 69.6 | 132.3787 | 0.043177 | 131.9783 | 0.0016062 | 0.0053935 | 1.6859e-05 | 65.0562 | 0.031455 | 0.14424 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | 3.0156 | 0.00032025 | 132.0357 | 0.034931 | 131.4765 | 0.0015619 | 0.095061 | 8.4239e-05 | 65.137 | 0.032803 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 2.7972 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.095394 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.29589 | -0.00020779 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.11626 | -0.00041558 | 0.070087 | 0.0027804 | 129.353 | 0.043705 | 129.3268 | 0.0026002 | 0.23793 | 0.00041557 | 63.3141 | 0.02714 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 2.9778 | -0.0003594
260.8 | 69.8 | 132.3787 | 0.043177 | 131.9783 | 0.0016062 | 0.0053935 | 1.6859e-05 | 65.0562 | 0.031455 | 0.24166 | 0.00012922 | 0.19109 | 0.00029777 | 0.10349 | 0.0016967 | 3.113 | 0.00032025 | 132.133 | 0.033308 | 131.4765 | 0.0015619 | 0.095061 | 8.4239e-05 | 65.137 | 0.032803 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | -0.00017979 | 2.7972 | 7.2982e-05 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.29589 | -0.00020779 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 0.070087 | 0.004404 | 129.2556 | 0.043705 | 129.2293 | 0.0026002 | 0.23793 | 0.00041557 | 63.2167 | 0.028764 | 0.1621 | 0.0011513 | 0.11153 | -0.00034817 | 0.22513 | 0.0031962 | 2.9778 | 0.0012636
261 | 70 | 132.3787 | 0.041554 | 131.9783 | 0.0016062 | 0.0053935 | 1.6859e-05 | 65.0562 | 0.033078 | 0.24166 | 0.00012922 | 0.28848 | 0.0019208 | 0.10349 | 0.0016967 | 3.113 | 0.00032025 | 132.0357 | 0.033308 | 131.4765 | 0.0015619 | 0.19244 | 8.4239e-05 | 65.137 | 0.032803 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 2.7972 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | 0.0015107 | -0.011119 | -0.0006346 | 0.11626 | 0.0012074 | -0.027293 | 0.004404 | 129.353 | 0.043705 | 129.3268 | 0.00097717 | 0.23793 | 0.00041557 | 63.3141 | 0.02714 | 0.1621 | 0.0011513 | 0.20895 | -0.00034817 | 0.12771 | 0.0015725 | 2.9778 | -0.0003594
261.2 | 70.2 | 132.3787 | 0.043177 | 131.9783 | 0.0016062 | 0.0053935 | 1.6859e-05 | 65.0562 | 0.031455 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 7.2991e-05 | 3.113 | 0.00032025 | 132.133 | 0.031685 | 131.4765 | 0.0015619 | 0.19244 | 8.4239e-05 | 65.137 | 0.031179 | -0.0775 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 2.7972 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.070087 | 0.004404 | 129.2556 | 0.042082 | 129.2293 | 0.00097717 | 0.23793 | 0.00041557 | 63.2167 | 0.02714 | 0.1621 | -0.00047174 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 2.9778 | 0.0012636
261.4 | 70.4 | 132.2813 | 0.043177 | 131.9783 | 0.0016062 | 0.0053935 | 1.6859e-05 | 64.9588 | 0.031455 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | 3.113 | 0.00032025 | 132.133 | 0.033308 | 131.4765 | 0.0015619 | 0.19244 | 8.4239e-05 | 65.0397 | 0.032803 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 2.7972 | 7.2982e-05 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | 0.0015332 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.070087 | 0.004404 | 129.2556 | 0.043705 | 129.3268 | 0.0026002 | 0.23793 | -0.0012074 | 63.2167 | 0.02714 | 0.1621 | -0.00047174 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 2.9778 | -0.0003594
261.6 | 70.6 | 132.3787 | 0.043177 | 131.9783 | 0.0016062 | 0.0053935 | 1.6859e-05 | 65.0562 | 0.033078 | 0.14424 | 0.00012922 | 0.19109 | 0.00029777 | 0.10349 | 7.2991e-05 | 3.0156 | -0.0013034 | 132.133 | 0.033308 | 131.574 | 0.0015619 | 0.19244 | 8.4239e-05 | 65.137 | 0.031179 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 2.7972 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | 0.0015332 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | -0.00041558 | 0.070087 | 0.0027804 | 129.353 | 0.043705 | 129.3268 | 0.00097717 | 0.23793 | 0.00041557 | 63.3141 | 0.025517 | 0.25952 | -0.00047174 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 3.0752 | 0.0012636
261.8 | 70.8 | 132.3787 | 0.043177 | 131.9783 | 0.0016062 | 0.0053935 | 1.6859e-05 | 65.0562 | 0.033078 | 0.14424 | 0.00012922 | 0.19109 | -0.0013259 | 0.20087 | 7.2991e-05 | 3.113 | -0.0013034 | 132.133 | 0.033308 | 131.4765 | 0.0015619 | 0.19244 | 8.4239e-05 | 65.137 | 0.031179 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 2.8946 | 7.2982e-05 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | 0.0015332 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | -0.00041558 | 0.070087 | 0.004404 | 129.353 | 0.042082 | 129.3268 | 0.00097717 | 0.14051 | -0.0012074 | 63.2167 | 0.025517 | 0.1621 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 2.9778 | 0.0012636
262 | 71 | 132.3787 | 0.043177 | 131.9783 | 0.0016062 | 0.0053935 | 1.6859e-05 | 65.0562 | 0.033078 | 0.24166 | 0.00012922 | 0.19109 | 0.00029777 | 0.10349 | 7.2991e-05 | 3.113 | 0.00032025 | 132.133 | 0.031685 | 131.4765 | -6.1803e-05 | 0.19244 | 8.4239e-05 | 65.137 | 0.031179 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | 0.0014439 | 2.7972 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | 0.0015332 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | 0.086261 | -0.0006346 | 0.21368 | 0.0012074 | 0.070087 | 0.004404 | 129.2556 | 0.042082 | 129.2293 | 0.00097717 | 0.23793 | 0.00041557 | 63.3141 | 0.02714 | 0.1621 | -0.00047174 | 0.20895 | -0.00034817 | 0.22513 | 0.0048192 | 2.9778 | 0.0012636
262.2 | 71.2 | 132.3787 | 0.041554 | 132.0758 | 0.0016062 | -0.092027 | 1.6859e-05 | 65.0562 | 0.033078 | 0.24166 | 0.00012922 | 0.19109 | 0.00029777 | 0.10349 | 0.0016967 | 3.0156 | 0.00032025 | 132.133 | 0.031685 | 131.574 | 0.0015619 | 0.19244 | 8.4239e-05 | 65.137 | 0.031179 | 0.01988 | 0.0022635 | 0.11562 | 0.0013085 | 0.15942 | -0.00017979 | 2.7972 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.29589 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.070087 | 0.0027804 | 129.2556 | 0.042082 | 129.3268 | 0.00097717 | 0.23793 | 0.00041557 | 63.3141 | 0.025517 | 0.1621 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 2.9778 | 0.0012636
262.4 | 71.4 | 132.4761 | 0.043177 | 131.9783 | 0.0016062 | 0.0053935 | 1.6859e-05 | 65.0562 | 0.031455 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | 3.0156 | 0.00032025 | 132.133 | 0.031685 | 131.574 | 0.0015619 | 0.19244 | 8.4239e-05 | 65.137 | 0.031179 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 2.7972 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | 0.0015107 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.070087 | 0.004404 | 129.353 | 0.043705 | 129.3268 | 0.0026002 | 0.23793 | 0.00041557 | 63.3141 | 0.025517 | 0.1621 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 2.9778 | 0.0012636
262.6 | 71.6 | 132.4761 | 0.041554 | 131.9783 | 0.0016062 | 0.0053935 | 1.6859e-05 | 65.1536 | 0.033078 | 0.14424 | 0.00012922 | 0.19109 | 0.00029777 | 0.10349 | 0.0016967 | 3.0156 | 0.00032025 | 132.2304 | 0.031685 | 131.574 | 0.0015619 | 0.095061 | 8.4239e-05 | 65.137 | 0.032803 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 2.7972 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.070087 | 0.004404 | 129.353 | 0.042082 | 129.3268 | 0.0026002 | 0.23793 | 0.00041557 | 63.3141 | 0.025517 | 0.1621 | -0.00047174 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 2.9778 | -0.0003594
262.8 | 71.8 | 132.3787 | 0.041554 | 131.9783 | 0.0016062 | 0.0053935 | 1.6859e-05 | 65.0562 | 0.031455 | 0.14424 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | 3.0156 | -0.0013034 | 132.133 | 0.031685 | 131.574 | 0.0015619 | 0.095061 | 8.4239e-05 | 65.137 | 0.031179 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | -0.00017979 | 2.8946 | 7.2982e-05 | 0.2039 | 0.001477 | 0.19277 | 0.00023025 | 0.017185 | 0.0015332 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 0.070087 | 0.0027804 | 129.2556 | 0.042082 | 129.3268 | 0.00097717 | 0.23793 | 0.00041557 | 63.2167 | 0.025517 | 0.1621 | -0.00047174 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 2.9778 | -0.0003594
263 | 72 | 132.3787 | 0.041554 | 132.0758 | 0.0016062 | 0.0053935 | 1.6859e-05 | 65.0562 | 0.031455 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | 3.0156 | 0.00032025 | 132.133 | 0.030062 | 131.574 | 0.0015619 | 0.19244 | 8.4239e-05 | 65.137 | 0.031179 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 2.7972 | 7.2982e-05 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | -0.080196 | -8.9855e-05 | 0.29589 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.070087 | 0.004404 | 129.2556 | 0.042082 | 129.3268 | 0.00097717 | 0.23793 | 0.00041557 | 63.3141 | 0.025517 | 0.1621 | -0.00047174 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 3.0752 | 0.0012636
263.2 | 72.2 | 132.3787 | 0.043177 | 132.0758 | 0.0016062 | 0.0053935 | 1.6859e-05 | 65.0562 | 0.031455 | 0.24166 | 0.00012922 | 0.19109 | 0.00029777 | 0.10349 | 0.0016967 | 3.0156 | 0.00032025 | 132.133 | 0.031685 | 131.4765 | 0.0015619 | 0.19244 | 8.4239e-05 | 65.137 | 0.031179 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 2.7972 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.070087 | 0.004404 | 129.2556 | 0.042082 | 129.3268 | 0.00097717 | 0.23793 | 0.00041557 | 63.2167 | 0.025517 | 0.1621 | 0.0011513 | 0.11153 | 0.0012748 | 0.22513 | 0.0031962 | 2.9778 | 0.0012636
263.4 | 72.4 | 132.3787 | 0.041554 | 132.0758 | 0.0016062 | 0.0053935 | 1.6859e-05 | 65.0562 | 0.031455 | 0.24166 | 0.00012922 | 0.19109 | 0.00029777 | 0.20087 | 0.0016967 | 3.0156 | 0.00032025 | 132.133 | 0.031685 | 131.574 | 0.0015619 | 0.095061 | 0.0017072 | 65.137 | 0.031179 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 2.7972 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | -0.080196 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | 0.0015107 | -0.011119 | 0.0009884 | 0.11626 | -0.00041558 | 0.070087 | 0.0027804 | 129.353 | 0.042082 | 129.3268 | 0.00097717 | 0.23793 | 0.00041557 | 63.2167 | 0.025517 | 0.25952 | -0.00047174 | 0.11153 | -0.00034817 | 0.22513 | 0.0031962 | 2.9778 | -0.0003594
263.6 | 72.6 | 132.4761 | 0.041554 | 131.9783 | 0.0016062 | 0.0053935 | 1.6859e-05 | 65.0562 | 0.031455 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | 3.113 | -0.0013034 | 132.2304 | 0.031685 | 131.574 | 0.0015619 | 0.19244 | 8.4239e-05 | 65.137 | 0.031179 | 0.01988 | 0.00064048 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 2.7972 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | -0.0006346 | 0.11626 | 0.0012074 | 0.070087 | 0.004404 | 129.2556 | 0.042082 | 129.3268 | 0.00097717 | 0.23793 | 0.00041557 | 63.2167 | 0.025517 | 0.25952 | 0.0011513 | 0.11153 | -0.00034817 | 0.22513 | 0.0031962 | 3.0752 | -0.0003594
263.8 | 72.8 | 132.3787 | 0.041554 | 132.0758 | 0.0016062 | 0.0053935 | 0.0016399 | 65.0562 | 0.031455 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.20087 | 0.0016967 | 3.113 | 0.00032025 | 132.133 | 0.031685 | 131.574 | 0.0015619 | 0.19244 | 8.4239e-05 | 65.137 | 0.031179 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 2.7972 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.070087 | 0.004404 | 129.353 | 0.040458 | 129.3268 | 0.00097717 | 0.23793 | 0.00041557 | 63.3141 | 0.025517 | 0.1621 | -0.00047174 | 0.11153 | -0.00034817 | 0.22513 | 0.0031962 | 3.0752 | 0.0012636
264 | 73 | 132.4761 | 0.039931 | 132.0758 | 0.0016062 | 0.0053935 | 1.6859e-05 | 65.0562 | 0.031455 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.20087 | 0.0016967 | 3.113 | 0.00032025 | 132.2304 | 0.031685 | 131.574 | 0.0015619 | 0.19244 | 8.4239e-05 | 65.137 | 0.031179 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 2.7972 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | -0.00041558 | 0.16751 | 0.0027804 | 129.353 | 0.040458 | 129.2293 | 0.00097717 | 0.23793 | 0.00041557 | 63.3141 | 0.025517 | 0.1621 | -0.00047174 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 2.9778 | 0.0012636
264.2 | 73.2 | 132.4761 | 0.039931 | 132.0758 | 0.0016062 | 0.0053935 | 1.6859e-05 | 65.0562 | 0.031455 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | 3.0156 | 0.00032025 | 132.2304 | 0.031685 | 131.574 | 0.0015619 | 0.095061 | 8.4239e-05 | 65.137 | 0.031179 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 2.7972 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | 0.0015332 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 129.353 | 0.042082 | 129.3268 | 0.00097717 | 0.33531 | -0.0012074 | 63.3141 | 0.023894 | 0.1621 | -0.00047174 | 0.11153 | -0.00034817 | 0.22513 | 0.0015725 | 2.9778 | -0.0003594
264.4 | 73.4 | 132.5735 | 0.039931 | 132.1731 | 0.0016062 | 0.0053935 | 1.6859e-05 | 65.1536 | 0.031455 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | 3.0156 | 0.00032025 | 132.2304 | 0.030062 | 131.574 | 0.0015619 | 0.095061 | 8.4239e-05 | 65.137 | 0.029556 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 2.7972 | 7.2982e-05 | 0.30132 | 0.001477 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.070087 | 0.004404 | 129.353 | 0.042082 | 129.4241 | 0.00097717 | 0.14051 | 0.00041557 | 63.3141 | 0.025517 | 0.1621 | -0.00047174 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 3.0752 | 0.0012636
264.6 | 73.6 | 132.5735 | 0.039931 | 132.1731 | 0.0016062 | 0.0053935 | 1.6859e-05 | 65.2509 | 0.029831 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | 3.0156 | 0.00032025 | 132.2304 | 0.030062 | 131.574 | 0.0015619 | 0.19244 | 8.4239e-05 | 65.137 | 0.031179 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 2.7972 | 7.2982e-05 | 0.2039 | 0.001477 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | 0.0015107 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.070087 | 0.004404 | 129.353 | 0.040458 | 129.3268 | 0.00097717 | 0.14051 | 0.00041557 | 63.3141 | 0.025517 | 0.1621 | -0.00047174 | 0.11153 | 0.0012748 | 0.22513 | 0.0031962 | 3.0752 | 0.0012636
264.8 | 73.8 | 132.5735 | 0.039931 | 132.1731 | 0.0016062 | 0.0053935 | 1.6859e-05 | 65.2509 | 0.031455 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.20087 | 0.0016967 | 3.0156 | 0.00032025 | 132.2304 | 0.030062 | 131.6713 | 0.0015619 | 0.19244 | 8.4239e-05 | 65.137 | 0.029556 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 2.8946 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.10109 | -0.00020779 | 0.078174 | -0.00011232 | -0.011119 | -0.0006346 | 0.11626 | 0.0012074 | 0.070087 | 0.0027804 | 129.4504 | 0.040458 | 129.4241 | 0.00097717 | 0.14051 | -0.0012074 | 63.3141 | 0.025517 | 0.1621 | 0.0011513 | 0.11153 | -0.00034817 | 0.22513 | 0.0031962 | 3.0752 | 0.0012636
265 | 74 | 132.6709 | 0.039931 | 132.1731 | 0.0016062 | 0.10277 | 1.6859e-05 | 65.2509 | 0.031455 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.20087 | 0.0016967 | 3.0156 | 0.0019433 | 132.3278 | 0.030062 | 131.6713 | 0.0015619 | 0.095061 | 8.4239e-05 | 65.137 | 0.029556 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 2.7972 | 7.2982e-05 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | -0.080196 | 0.0015332 | 0.29589 | -0.00020779 | 0.17559 | -0.00011232 | 0.086261 | -0.0006346 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 129.4504 | 0.040458 | 129.4241 | 0.00097717 | 0.14051 | 0.00041557 | 63.3141 | 0.025517 | 0.25952 | 0.0011513 | 0.11153 | -0.00034817 | 0.12771 | 0.0031962 | 2.9778 | 0.0012636
265.2 | 74.2 | 132.6709 | 0.038307 | 132.1731 | 0.0016062 | 0.0053935 | 0.0016399 | 65.1536 | 0.031455 | 0.24166 | 0.00012922 | 0.28848 | -0.0013259 | 0.20087 | 0.0016967 | 3.113 | 0.00032025 | 132.3278 | 0.030062 | 131.6713 | 0.0015619 | 0.19244 | 8.4239e-05 | 65.137 | 0.029556 | 0.01988 | 0.00064048 | 0.018196 | 0.0013085 | 0.15942 | -0.00017979 | 2.7972 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.21368 | -0.00041558 | 0.070087 | 0.004404 | 129.4504 | 0.040458 | 129.4241 | 0.00097717 | 0.23793 | 0.00041557 | 63.3141 | 0.025517 | 0.1621 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 3.0752 | -0.0003594
265.4 | 74.4 | 132.6709 | 0.038307 | 132.2706 | 0.0016062 | 0.0053935 | 0.0016399 | 65.2509 | 0.031455 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | 3.113 | 0.00032025 | 132.3278 | 0.030062 | 131.6713 | -6.1803e-05 | 0.095061 | 8.4239e-05 | 65.137 | 0.029556 | 0.01988 | 0.00064048 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 2.7972 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | -0.011119 | -0.0006346 | 0.11626 | -0.00041558 | 0.070087 | 0.0027804 | 129.4504 | 0.040458 | 129.4241 | 0.00097717 | 0.23793 | 0.00041557 | 63.3141 | 0.025517 | 0.1621 | 0.0011513 | 0.11153 | -0.00034817 | 0.12771 | 0.0031962 | 3.0752 | 0.0012636
265.6 | 74.6 | 132.5735 | 0.039931 | 132.2706 | 0.0016062 | 0.10277 | 1.6859e-05 | 65.2509 | 0.029831 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 7.2991e-05 | 3.0156 | 0.00032025 | 132.3278 | 0.028438 | 131.6713 | 0.0015619 | 0.19244 | 8.4239e-05 | 65.2344 | 0.029556 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 2.7972 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.078174 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.070087 | 0.0027804 | 129.4504 | 0.040458 | 129.4241 | 0.00097717 | 0.14051 | 0.00041557 | 63.3141 | 0.023894 | 0.1621 | -0.00047174 | 0.11153 | -0.00034817 | 0.22513 | 0.0031962 | 3.0752 | -0.0003594
265.8 | 74.8 | 132.6709 | 0.039931 | 132.2706 | 0.0016062 | 0.0053935 | 1.6859e-05 | 65.2509 | 0.029831 | 0.24166 | 0.0017522 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | 3.0156 | 0.00032025 | 132.3278 | 0.028438 | 131.7687 | 0.0015619 | 0.095061 | 8.4239e-05 | 65.2344 | 0.029556 | 0.01988 | 0.00064048 | 0.018196 | -0.00031449 | 0.062 | -0.00017979 | 2.7972 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.070087 | 0.004404 | 129.4504 | 0.038835 | 129.4241 | 0.00097717 | 0.23793 | -0.0012074 | 63.3141 | 0.023894 | 0.1621 | -0.00047174 | 0.11153 | -0.00034817 | 0.22513 | 0.0031962 | 3.0752 | -0.0003594
266 | 75 | 132.5735 | 0.038307 | 132.2706 | 0.0016062 | 0.0053935 | 1.6859e-05 | 65.2509 | 0.031455 | 0.24166 | -0.0014944 | 0.28848 | 0.00029777 | 0.20087 | 0.0016967 | 3.113 | 0.00032025 | 132.3278 | 0.028438 | 131.6713 | 0.0015619 | 0.19244 | 8.4239e-05 | 65.137 | 0.029556 | 0.01988 | 0.00064048 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 2.7972 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.070087 | 0.004404 | 129.4504 | 0.038835 | 129.4241 | 0.0026002 | 0.23793 | 0.00041557 | 63.3141 | 0.023894 | 0.1621 | -0.00047174 | 0.11153 | -0.00034817 | 0.22513 | 0.0031962 | 3.0752 | -0.0003594
266.2 | 75.2 | 132.6709 | 0.039931 | 132.2706 | 0.0032298 | 0.10277 | 0.0016399 | 65.2509 | 0.031455 | 0.24166 | 0.0017522 | 0.28848 | 0.00029777 | 0.20087 | 0.0016967 | 3.0156 | 0.00032025 | 132.3278 | 0.028438 | 131.6713 | 0.0015619 | 0.095061 | 8.4239e-05 | 65.2344 | 0.031179 | -0.0775 | 0.0022635 | 0.11562 | -0.00031449 | 0.15942 | -0.00017979 | 2.7972 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.078174 | -0.00011232 | -0.011119 | -0.0006346 | 0.11626 | -0.00041558 | 0.070087 | 0.0027804 | 129.4504 | 0.038835 | 129.4241 | 0.0026002 | 0.23793 | 0.00041557 | 63.3141 | 0.023894 | 0.1621 | -0.00047174 | 0.11153 | -0.00034817 | 0.12771 | 0.0031962 | 3.0752 | 0.0012636
266.4 | 75.4 | 132.7683 | 0.038307 | 132.3679 | 0.0016062 | 0.10277 | 1.6859e-05 | 65.2509 | 0.031455 | 0.24166 | 0.0017522 | 0.28848 | 0.00029777 | 0.20087 | 7.2991e-05 | 3.113 | 0.00032025 | 132.4252 | 0.030062 | 131.6713 | 0.0015619 | 0.19244 | 8.4239e-05 | 65.2344 | 0.029556 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 2.7972 | 7.2982e-05 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | -0.080196 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 0.070087 | 0.004404 | 129.5478 | 0.038835 | 129.5215 | 0.00097717 | 0.23793 | 0.00041557 | 63.4115 | 0.023894 | 0.1621 | 0.0011513 | 0.11153 | -0.00034817 | 0.22513 | 0.0015725 | 3.0752 | -0.0003594
266.6 | 75.6 | 132.6709 | 0.038307 | 132.3679 | 0.0016062 | 0.10277 | 1.6859e-05 | 65.3484 | 0.031455 | 0.24166 | 0.00012922 | 0.38586 | 0.00029777 | 0.20087 | 7.2991e-05 | 3.0156 | 0.0019433 | 132.3278 | 0.028438 | 131.7687 | 0.0015619 | 0.19244 | 8.4239e-05 | 65.2344 | 0.029556 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.2568 | -0.00017979 | 2.7972 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | 0.0015332 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | -0.00041558 | 0.070087 | 0.0027804 | 129.4504 | 0.038835 | 129.5215 | 0.00097717 | 0.14051 | 0.00041557 | 63.3141 | 0.023894 | 0.1621 | -0.00047174 | 0.11153 | -0.00034817 | 0.22513 | 0.0015725 | 3.0752 | -0.0003594
266.8 | 75.8 | 132.7683 | 0.038307 | 132.3679 | 0.0016062 | 0.10277 | 0.0016399 | 65.2509 | 0.029831 | 0.24166 | 0.0017522 | 0.28848 | 0.00029777 | 0.20087 | 0.0016967 | 3.0156 | 0.00032025 | 132.4252 | 0.028438 | 131.6713 | 0.0015619 | 0.19244 | 8.4239e-05 | 65.2344 | 0.029556 | -0.0775 | 0.00064048 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 2.7972 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | -0.080196 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | -0.00041558 | 0.070087 | 0.004404 | 129.5478 | 0.038835 | 129.5215 | 0.00097717 | 0.23793 | 0.00041557 | 63.4115 | 0.023894 | 0.1621 | -0.00047174 | 0.11153 | -0.00034817 | 0.22513 | 0.0015725 | 3.0752 | -0.0003594
267 | 76 | 132.7683 | 0.038307 | 132.3679 | 0.0016062 | 0.10277 | 1.6859e-05 | 65.2509 | 0.029831 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.20087 | 0.0016967 | 3.113 | 0.00032025 | 132.4252 | 0.028438 | 131.7687 | 0.0015619 | 0.19244 | 8.4239e-05 | 65.2344 | 0.029556 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 2.7972 | 7.2982e-05 | 0.30132 | 0.001477 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.10109 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | -0.00041558 | 0.070087 | 0.0027804 | 129.5478 | 0.037212 | 129.5215 | 0.00097717 | 0.23793 | 0.00041557 | 63.4115 | 0.023894 | 0.1621 | -0.00047174 | 0.11153 | -0.00034817 | 0.22513 | 0.0031962 | 2.9778 | -0.0003594
267.2 | 76.2 | 132.7683 | 0.039931 | 132.4653 | 0.0016062 | 0.10277 | 0.0016399 | 65.3484 | 0.029831 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.20087 | 0.0016967 | 3.0156 | 0.00032025 | 132.4252 | 0.028438 | 131.7687 | 0.0015619 | 0.19244 | 8.4239e-05 | 65.2344 | 0.029556 | -0.0775 | 0.00064048 | 0.018196 | 0.0013085 | 0.15942 | -0.00017979 | 2.7972 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | -0.080196 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | -0.0006346 | 0.11626 | 0.0012074 | 0.070087 | 0.004404 | 129.6452 | 0.038835 | 129.5215 | 0.00097717 | 0.23793 | 0.00041557 | 63.4115 | 0.023894 | 0.1621 | 0.0011513 | 0.11153 | -0.00034817 | 0.22513 | 0.0015725 | 3.0752 | -0.0003594
267.4 | 76.4 | 132.7683 | 0.038307 | 132.3679 | 0.0016062 | -0.092027 | 0.0016399 | 65.2509 | 0.031455 | 0.24166 | -0.0014944 | 0.19109 | 0.00029777 | 0.20087 | 0.0033197 | 2.9182 | 0.00032025 | 132.4252 | 0.028438 | 131.7687 | 0.0015619 | 0.19244 | -0.0015388 | 65.2344 | 0.029556 | -0.0775 | 0.00064048 | 0.018196 | -0.00031449 | 0.062 | -0.00017979 | 2.7972 | 7.2982e-05 | 0.2039 | -0.001769 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | 0.0015107 | -0.011119 | -0.0022576 | 0.018878 | 0.0012074 | 0.070087 | 0.004404 | 129.5478 | 0.038835 | 129.5215 | 0.00097717 | 0.23793 | -0.0028304 | 63.4115 | 0.023894 | 0.064722 | -0.00047174 | 0.11153 | 0.0012748 | 0.22513 | 0.0015725 | 3.0752 | -0.0003594
267.6 | 76.6 | 132.7683 | 0.038307 | 132.3679 | 0.0016062 | 0.0053935 | 1.6859e-05 | 65.2509 | 0.029831 | 0.24166 | 0.00012922 | 0.28848 | 0.0019208 | 0.0060648 | 0.0016967 | 3.113 | 0.00032025 | 132.4252 | 0.028438 | 131.6713 | 0.0015619 | 0.19244 | 8.4239e-05 | 65.2344 | 0.029556 | 0.01988 | 0.00064048 | 0.018196 | 0.0013085 | 0.15942 | -0.00017979 | 2.7972 | 7.2982e-05 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.29589 | 0.0014152 | 0.17559 | 0.0015107 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 0.070087 | 0.0027804 | 129.5478 | 0.038835 | 129.4241 | 0.00097717 | 0.23793 | -0.0012074 | 63.3141 | 0.023894 | 0.1621 | -0.00047174 | 0.20895 | -0.00034817 | 0.12771 | 0.0031962 | 3.0752 | -0.0003594
267.8 | 76.8 | 132.7683 | 0.039931 | 132.4653 | 0.0016062 | 0.0053935 | 1.6859e-05 | 65.3484 | 0.031455 | 0.33904 | 0.00012922 | 0.28848 | 0.00029777 | 0.20087 | 0.0016967 | 2.9182 | -0.0013034 | 132.4252 | 0.026815 | 131.7687 | 0.0015619 | 0.095061 | 8.4239e-05 | 65.2344 | 0.027933 | 0.01988 | 0.0022635 | -0.079185 | -0.00031449 | 0.062 | -0.00017979 | 2.7972 | 7.2982e-05 | 0.30132 | -0.00014601 | 0.19277 | 0.0018533 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.27297 | 0.0015107 | 0.086261 | -0.0006346 | 0.11626 | 0.0012074 | 0.070087 | 0.0027804 | 129.6452 | 0.040458 | 129.5215 | 0.00097717 | 0.33531 | -0.0012074 | 63.3141 | 0.022271 | 0.1621 | -0.00047174 | 0.20895 | -0.0019718 | 0.22513 | 0.0015725 | 3.0752 | -0.0003594
268 | 77 | 132.6709 | 0.039931 | 132.3679 | 0.0016062 | 0.10277 | 1.6859e-05 | 65.3484 | 0.031455 | 0.24166 | 0.0017522 | 0.38586 | 0.00029777 | 0.20087 | 7.2991e-05 | 3.0156 | 0.00032025 | 132.4252 | 0.026815 | 131.7687 | 0.0015619 | 0.19244 | 8.4239e-05 | 65.2344 | 0.029556 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.2568 | 0.0014439 | 2.7972 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | 0.0015107 | -0.011119 | 0.0026121 | 0.11626 | -0.00041558 | 0.070087 | 0.0027804 | 129.5478 | 0.038835 | 129.5215 | 0.00097717 | 0.23793 | 0.00041557 | 63.4115 | 0.023894 | 0.25952 | -0.00047174 | 0.014152 | 0.0012748 | 0.12771 | 0.0015725 | 3.0752 | 0.0012636
268.2 | 77.2 | 132.3787 | 0.038307 | 132.5627 | 0.0016062 | 0.10277 | 0.0016399 | 65.3484 | 0.029831 | 0.24166 | 0.00012922 | 0.38586 | 0.00029777 | 0.29825 | 7.2991e-05 | 2.9182 | 0.00032025 | 132.62 | 0.028438 | 131.8661 | 0.0015619 | 0.19244 | 8.4239e-05 | 65.2344 | 0.029556 | 0.01988 | 0.00064048 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 2.8946 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.10854 | 0.0009884 | 0.11626 | 0.0028311 | -0.027293 | 0.0027804 | 129.5478 | 0.038835 | 129.6189 | 0.00097717 | 0.23793 | 0.00041557 | 63.4115 | 0.023894 | 0.1621 | -0.00047174 | 0.11153 | -0.00034817 | 0.22513 | 0.0031962 | 3.0752 | 0.0012636
268.4 | 77.4 | 131.6969 | 0.039931 | 132.8549 | 0.0016062 | 0.10277 | 1.6859e-05 | 65.6405 | 0.029831 | 0.24166 | 0.00012922 | 0.38586 | 0.00029777 | 0.20087 | 0.0016967 | 3.0156 | 0.00032025 | 132.5226 | 0.028438 | 131.7687 | 0.0015619 | 0.19244 | 8.4239e-05 | 65.3318 | 0.029556 | 0.01988 | 0.00064048 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 2.7972 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | -0.080196 | 0.0015332 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.070087 | 0.004404 | 129.6452 | 0.038835 | 129.6189 | 0.00097717 | 0.23793 | 0.00041557 | 63.4115 | 0.023894 | 0.1621 | -0.00047174 | 0.11153 | -0.00034817 | 0.22513 | 0.0031962 | 3.0752 | 0.0012636
268.6 | 77.6 | 132.4761 | 0.039931 | 132.5627 | 0.0016062 | 0.10277 | 1.6859e-05 | 65.6405 | 0.029831 | 0.33904 | 0.0017522 | 0.28848 | 0.00029777 | 0.20087 | 0.0016967 | 3.0156 | 0.00032025 | 132.7174 | 0.028438 | 131.8661 | 0.0015619 | 0.095061 | 8.4239e-05 | 65.3318 | 0.031179 | 0.01988 | 0.0022635 | -0.079185 | -0.00031449 | 0.15942 | -0.00017979 | 2.7972 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | -0.0006346 | 0.11626 | -0.00041558 | 0.070087 | 0.004404 | 129.6452 | 0.037212 | 129.6189 | 0.00097717 | 0.23793 | -0.0012074 | 63.4115 | 0.022271 | 0.1621 | -0.00047174 | 0.11153 | -0.00034817 | 0.12771 | 0.0031962 | 3.0752 | -0.0003594
268.8 | 77.8 | 132.5735 | 0.039931 | 132.4653 | 0.0016062 | 0.10277 | 0.0016399 | 65.3484 | 0.029831 | 0.24166 | 0.00012922 | 0.38586 | 0.00029777 | 0.20087 | 0.0016967 | 3.113 | 0.00032025 | 133.3018 | 0.028438 | 132.0609 | 0.0015619 | 0.095061 | 8.4239e-05 | 65.3318 | 0.027933 | -0.0775 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 2.8946 | 7.2982e-05 | 0.2039 | 0.001477 | 0.095394 | 0.00023025 | -0.080196 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.0027804 | 129.6452 | 0.038835 | 129.6189 | 0.00097717 | 0.14051 | -0.0012074 | 63.4115 | 0.023894 | 0.1621 | -0.00047174 | 0.11153 | -0.00034817 | 0.22513 | 0.0031962 | 2.9778 | -0.0003594
269 | 78 | 132.7683 | 0.039931 | 132.4653 | 0.0016062 | 0.10277 | 1.6859e-05 | 65.3484 | 0.031455 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.20087 | 7.2991e-05 | 3.0156 | 0.00032025 | 132.7174 | 0.028438 | 131.9635 | -6.1803e-05 | 0.19244 | 8.4239e-05 | 65.3318 | 0.029556 | -0.0775 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 2.8946 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | 0.0015332 | 0.29589 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | -0.0006346 | 0.11626 | -0.00041558 | 0.070087 | 0.0027804 | 129.5478 | 0.038835 | 129.6189 | 0.00097717 | 0.14051 | -0.0012074 | 63.4115 | 0.023894 | 0.1621 | -0.00047174 | 0.11153 | -0.00034817 | 0.12771 | 0.0031962 | 3.0752 | -0.0003594
269.2 | 78.2 | 132.8657 | 0.039931 | 132.4653 | 0.0016062 | 0.10277 | 1.6859e-05 | 65.3484 | 0.031455 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.20087 | 0.0016967 | 3.0156 | 0.00032025 | 132.62 | 0.028438 | 131.9635 | 0.0015619 | 0.095061 | 8.4239e-05 | 65.3318 | 0.029556 | 0.01988 | 0.00064048 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 2.7972 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | -0.080196 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | -0.0006346 | 0.11626 | -0.00041558 | 0.070087 | 0.004404 | 129.6452 | 0.038835 | 129.6189 | 0.0026002 | 0.14051 | 0.00041557 | 63.4115 | 0.025517 | 0.1621 | -0.00047174 | 0.11153 | -0.00034817 | 0.22513 | 0.0031962 | 3.0752 | -0.0003594
269.4 | 78.4 | 132.7683 | 0.038307 | 132.4653 | 0.0016062 | 0.10277 | 1.6859e-05 | 65.3484 | 0.031455 | 0.24166 | 0.00012922 | 0.28848 | -0.0013259 | 0.29825 | 7.2991e-05 | 3.0156 | 0.00032025 | 132.62 | 0.028438 | 131.8661 | 0.0015619 | 0.095061 | 8.4239e-05 | 65.3318 | 0.029556 | 0.01988 | 0.00064048 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 2.7972 | 7.2982e-05 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.070087 | 0.0027804 | 129.7426 | 0.038835 | 129.7163 | 0.0026002 | 0.23793 | 0.00041557 | 63.4115 | 0.023894 | 0.1621 | -0.00047174 | 0.11153 | -0.00034817 | 0.22513 | 0.0015725 | 3.0752 | -0.0003594
269.6 | 78.6 | 132.8657 | 0.039931 | 132.4653 | 0.0016062 | 0.10277 | 1.6859e-05 | 65.4457 | 0.029831 | 0.33904 | 0.00012922 | 0.28848 | 0.00029777 | 0.20087 | 0.0016967 | 3.0156 | 0.00032025 | 132.5226 | 0.028438 | 131.8661 | 0.0015619 | 0.19244 | 8.4239e-05 | 65.2344 | 0.027933 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 2.7972 | -0.00155 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | -0.080196 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.070087 | 0.004404 | 130.2296 | 0.037212 | 129.9111 | 0.00097717 | 0.23793 | 0.00041557 | 63.5089 | 0.023894 | 0.1621 | -0.00047174 | 0.11153 | -0.00034817 | 0.22513 | 0.0031962 | 3.0752 | -0.0003594
269.8 | 78.8 | 132.8657 | 0.038307 | 132.4653 | 0.0016062 | 0.10277 | 0.0016399 | 65.3484 | 0.031455 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.20087 | 7.2991e-05 | 3.0156 | 0.00032025 | 132.5226 | 0.028438 | 131.8661 | 0.0015619 | 0.095061 | 8.4239e-05 | 65.3318 | 0.029556 | 0.01988 | 0.0022635 | -0.079185 | -0.00031449 | 0.15942 | -0.00017979 | 2.8946 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | -0.011119 | -0.0006346 | 0.11626 | 0.0012074 | 0.070087 | 0.0027804 | 129.9374 | 0.037212 | 129.8137 | 0.00097717 | 0.23793 | 0.00041557 | 63.7037 | 0.023894 | 0.1621 | 0.0011513 | 0.11153 | -0.00034817 | 0.22513 | 0.0015725 | 3.0752 | -0.0003594
270 | 79 | 132.8657 | 0.038307 | 132.4653 | 0.0016062 | 0.10277 | 1.6859e-05 | 65.3484 | 0.029831 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.29825 | 0.0016967 | 3.0156 | 0.00032025 | 132.5226 | 0.028438 | 131.8661 | 0.0015619 | 0.095061 | 8.4239e-05 | 65.2344 | 0.029556 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 2.8946 | 7.2982e-05 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | 0.0015332 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | -0.011119 | -0.0006346 | 0.11626 | 0.0012074 | 0.070087 | 0.0027804 | 129.84 | 0.037212 | 129.7163 | 0.00097717 | 0.23793 | 0.00041557 | 63.5089 | 0.022271 | 0.1621 | -0.00047174 | 0.11153 | -0.00034817 | 0.22513 | 0.0031962 | 3.0752 | -0.0003594
270.2 | 79.2 | 132.8657 | 0.038307 | 132.4653 | 0.0016062 | 0.10277 | 1.6859e-05 | 65.3484 | 0.029831 | 0.33904 | 0.00012922 | 0.38586 | 0.00029777 | 0.20087 | 0.0016967 | 3.0156 | 0.00032025 | 132.5226 | 0.028438 | 131.8661 | 0.0015619 | 0.19244 | 8.4239e-05 | 65.3318 | 0.029556 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 2.8946 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.070087 | 0.004404 | 129.7426 | 0.038835 | 129.7163 | 0.00097717 | 0.14051 | -0.0012074 | 63.5089 | 0.023894 | 0.1621 | -0.00047174 | 0.11153 | -0.00034817 | 0.12771 | 0.0015725 | 3.0752 | -0.0003594
270.4 | 79.4 | 132.8657 | 0.038307 | 132.4653 | 0.0016062 | 0.10277 | 1.6859e-05 | 65.3484 | 0.031455 | 0.24166 | 0.0017522 | 0.38586 | 0.00029777 | 0.20087 | 0.0016967 | 3.0156 | 0.00032025 | 132.5226 | 0.028438 | 131.8661 | 0.0015619 | 0.19244 | 8.4239e-05 | 65.2344 | 0.029556 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 2.8946 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | -0.0006346 | 0.11626 | -0.00041558 | 0.070087 | 0.004404 | 129.6452 | 0.038835 | 129.6189 | 0.00097717 | 0.14051 | 0.00041557 | 63.5089 | 0.023894 | 0.25952 | 0.0011513 | 0.11153 | -0.00034817 | 0.22513 | 0.0031962 | 3.0752 | -0.0003594
270.6 | 79.6 | 132.8657 | 0.038307 | 132.5627 | 0.0016062 | 0.10277 | 1.6859e-05 | 65.3484 | 0.029831 | 0.33904 | 0.0017522 | 0.38586 | 0.0019208 | 0.20087 | 0.0016967 | 3.0156 | 0.00032025 | 132.5226 | 0.028438 | 131.8661 | 0.0015619 | 0.19244 | 8.4239e-05 | 65.2344 | 0.029556 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | 0.0014439 | 2.8946 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | 0.086261 | -0.0006346 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 129.7426 | 0.037212 | 129.7163 | 0.00097717 | 0.23793 | 0.00041557 | 63.4115 | 0.023894 | 0.1621 | -0.00047174 | 0.11153 | -0.00034817 | 0.22513 | 0.0031962 | 3.0752 | -0.0003594
270.8 | 79.8 | 132.8657 | 0.039931 | 132.4653 | 0.0016062 | 0.10277 | 0.0016399 | 65.3484 | 0.031455 | 0.33904 | 0.00012922 | 0.38586 | 0.00029777 | 0.29825 | 0.0016967 | 3.113 | 0.00032025 | 132.5226 | 0.028438 | 131.8661 | 0.0015619 | 0.19244 | 8.4239e-05 | 65.2344 | 0.029556 | -0.0775 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 2.8946 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.29589 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | -0.0006346 | 0.11626 | 0.0012074 | 0.070087 | 0.004404 | 129.7426 | 0.037212 | 129.7163 | 0.00097717 | 0.23793 | 0.00041557 | 63.4115 | 0.023894 | 0.1621 | 0.0011513 | 0.11153 | -0.00034817 | 0.22513 | 0.0031962 | 3.0752 | -0.0003594
271 | 80 | 132.9631 | 0.039931 | 132.4653 | 0.0016062 | 0.10277 | 1.6859e-05 | 65.4457 | 0.031455 | 0.24166 | 0.00012922 | 0.38586 | 0.00029777 | 0.20087 | 0.0016967 | 3.113 | 0.00032025 | 132.5226 | 0.028438 | 131.8661 | 0.0015619 | 0.19244 | 8.4239e-05 | 65.2344 | 0.029556 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | 0.0014439 | 2.8946 | 7.2982e-05 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.070087 | 0.004404 | 129.7426 | 0.037212 | 129.7163 | 0.00097717 | 0.23793 | 0.00041557 | 63.4115 | 0.023894 | 0.1621 | -0.00047174 | 0.11153 | -0.00034817 | 0.22513 | 0.0031962 | 3.0752 | 0.0012636
271.2 | 80.2 | 132.7683 | 0.039931 | 132.4653 | 0.0016062 | 0.10277 | 1.6859e-05 | 65.3484 | 0.031455 | 0.33904 | 0.00012922 | 0.38586 | 0.00029777 | 0.20087 | 0.0016967 | 3.0156 | 0.00032025 | 132.5226 | 0.028438 | 131.8661 | 0.0015619 | 0.095061 | 8.4239e-05 | 65.2344 | 0.029556 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 2.8946 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.29589 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.070087 | 0.004404 | 129.6452 | 0.038835 | 129.6189 | 0.0026002 | 0.23793 | -0.0012074 | 63.5089 | 0.023894 | 0.1621 | -0.00047174 | 0.11153 | -0.00034817 | 0.22513 | 0.0015725 | 3.0752 | -0.0003594
271.4 | 80.4 | 132.8657 | 0.039931 | 132.4653 | 0.0016062 | 0.10277 | 1.6859e-05 | 65.3484 | 0.031455 | 0.33904 | 0.0017522 | 0.38586 | 0.00029777 | 0.29825 | 0.0016967 | 3.0156 | 0.0019433 | 132.62 | 0.028438 | 131.8661 | 0.0015619 | 0.19244 | 8.4239e-05 | 65.3318 | 0.029556 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | -0.00017979 | 2.8946 | 7.2982e-05 | 0.2039 | 0.001477 | 0.19277 | 0.00023025 | 0.017185 | 0.0015332 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 129.7426 | 0.038835 | 129.7163 | 0.00097717 | 0.23793 | 0.00041557 | 63.4115 | 0.023894 | 0.25952 | -0.00047174 | 0.11153 | -0.00034817 | 0.22513 | 0.0031962 | 3.0752 | 0.0012636
271.6 | 80.6 | 132.8657 | 0.039931 | 132.4653 | 0.0016062 | 0.0053935 | 1.6859e-05 | 65.3484 | 0.031455 | 0.33904 | 0.0017522 | 0.38586 | 0.00029777 | 0.29825 | 0.0016967 | 3.0156 | 0.0019433 | 132.5226 | 0.028438 | 131.8661 | 0.0015619 | 0.19244 | 8.4239e-05 | 65.3318 | 0.029556 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 2.8946 | 0.0016967 | 0.2039 | 0.001477 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | -0.0006346 | 0.21368 | 0.0012074 | 0.16751 | 0.004404 | 129.6452 | 0.038835 | 129.7163 | 0.0026002 | 0.23793 | 0.00041557 | 63.4115 | 0.023894 | 0.1621 | 0.0011513 | 0.20895 | -0.00034817 | 0.12771 | 0.0031962 | 3.0752 | -0.0003594
271.8 | 80.8 | 132.7683 | 0.038307 | 132.3679 | 0.0016062 | 0.10277 | 0.0016399 | 65.3484 | 0.031455 | 0.33904 | 0.0017522 | 0.28848 | 0.00029777 | 0.29825 | 0.0016967 | 3.0156 | 0.0019433 | 132.62 | 0.028438 | 131.8661 | 0.0015619 | 0.19244 | 0.0017072 | 65.3318 | 0.029556 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | -0.00017979 | 2.8946 | 7.2982e-05 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.27297 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 129.7426 | 0.038835 | 129.6189 | 0.00097717 | 0.23793 | 0.00041557 | 63.5089 | 0.023894 | 0.1621 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 3.1726 | 0.0012636
272 | 81 | 132.8657 | 0.038307 | 132.3679 | 0.0016062 | 0.10277 | 0.0016399 | 65.2509 | 0.031455 | 0.24166 | 0.0017522 | 0.28848 | 0.00029777 | 0.29825 | 0.0033197 | 3.0156 | 0.0019433 | 132.4252 | 0.028438 | 131.7687 | 0.0015619 | 0.19244 | 8.4239e-05 | 65.2344 | 0.029556 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | -0.00017979 | 2.8946 | 0.0016967 | 0.2039 | 0.001477 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 129.7426 | 0.038835 | 129.7163 | 0.00097717 | 0.23793 | 0.00041557 | 63.5089 | 0.023894 | 0.1621 | -0.00047174 | 0.11153 | -0.00034817 | 0.22513 | 0.0031962 | 3.0752 | 0.0012636
272.2 | 81.2 | 132.8657 | 0.039931 | 132.4653 | 0.0016062 | 0.10277 | 0.0016399 | 65.3484 | 0.031455 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.29825 | 0.0033197 | 2.9182 | 0.0019433 | 132.5226 | 0.028438 | 131.7687 | 0.0015619 | 0.19244 | 8.4239e-05 | 65.3318 | 0.029556 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 2.8946 | 7.2982e-05 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | 0.0015332 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.21368 | 0.0012074 | 0.070087 | 0.004404 | 129.7426 | 0.038835 | 129.7163 | 0.0026002 | 0.23793 | 0.00041557 | 63.5089 | 0.023894 | 0.25952 | -0.00047174 | 0.11153 | -0.00034817 | 0.22513 | 0.0031962 | 3.1726 | 0.0012636
272.4 | 81.4 | 132.8657 | 0.039931 | 132.4653 | 0.0016062 | 0.10277 | 0.0016399 | 65.3484 | 0.031455 | 0.33904 | 0.0017522 | 0.28848 | 0.00029777 | 0.20087 | 0.0016967 | 3.0156 | 0.0019433 | 132.5226 | 0.028438 | 131.8661 | 0.0015619 | 0.19244 | 8.4239e-05 | 65.3318 | 0.029556 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 2.8946 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.17559 | 0.0015107 | 0.086261 | 0.0009884 | 0.21368 | 0.0012074 | 0.070087 | 0.004404 | 129.7426 | 0.038835 | 129.7163 | 0.00097717 | 0.23793 | 0.00041557 | 63.5089 | 0.023894 | 0.1621 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 3.0752 | 0.0012636
272.6 | 81.6 | 132.8657 | 0.039931 | 132.4653 | 0.0016062 | 0.10277 | 0.0016399 | 65.3484 | 0.031455 | 0.33904 | 0.0017522 | 0.28848 | 0.0019208 | 0.29825 | 0.0033197 | 3.0156 | 0.0019433 | 132.5226 | 0.028438 | 131.8661 | 0.0015619 | 0.19244 | 8.4239e-05 | 65.3318 | 0.031179 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | 0.0014439 | 2.8946 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | -0.080196 | 0.0015332 | 0.19851 | -0.00020779 | 0.27297 | -0.00011232 | -0.011119 | -0.0006346 | 0.11626 | 0.0012074 | 0.070087 | 0.004404 | 129.7426 | 0.038835 | 129.6189 | 0.0026002 | 0.23793 | 0.00041557 | 63.4115 | 0.023894 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748 | 0.22513 | 0.0048192 | 3.0752 | 0.0012636
272.8 | 81.8 | 132.7683 | 0.039931 | 132.4653 | 0.0016062 | 0.10277 | 1.6859e-05 | 65.3484 | 0.031455 | 0.33904 | 0.0017522 | 0.38586 | 0.0019208 | 0.20087 | 0.0033197 | 3.0156 | 0.0019433 | 132.5226 | 0.028438 | 131.7687 | 0.0015619 | 0.19244 | 8.4239e-05 | 65.3318 | 0.031179 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 2.8946 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | -0.080196 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.17559 | 0.0015107 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 0.070087 | 0.004404 | 129.7426 | 0.038835 | 129.7163 | 0.0026002 | 0.23793 | 0.00041557 | 63.5089 | 0.023894 | 0.25952 | 0.0011513 | 0.11153 | 0.0012748 | 0.22513 | 0.0031962 | 3.1726 | -0.0003594
273 | 82 | 132.8657 | 0.039931 | 132.3679 | 0.0016062 | 0.10277 | 0.0016399 | 65.1536 | 0.031455 | 0.33904 | 0.0017522 | 0.28848 | 0.00029777 | 0.29825 | 0.0016967 | 3.0156 | 0.00032025 | 132.4252 | 0.028438 | 131.8661 | 0.0015619 | 0.19244 | 8.4239e-05 | 65.2344 | 0.031179 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.2568 | 0.0014439 | 2.8946 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.21368 | 0.0012074 | 0.16751 | 0.004404 | 129.7426 | 0.038835 | 129.7163 | 0.00097717 | 0.23793 | 0.00041557 | 63.4115 | 0.023894 | 0.25952 | -0.00047174 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 3.1726 | 0.0012636
273.2 | 82.2 | 133.0605 | 0.043177 | 132.5627 | 0.0016062 | 0.29757 | 0.0032635 | 64.1796 | 0.033078 | 0.53384 | 0.0033759 | 0.67808 | 0.0035444 | 0.59047 | 0.0049427 | 3.7948 | 0.0035663 | 132.4252 | 0.028438 | 131.7687 | 0.0015619 | 0.095061 | 8.4239e-05 | 65.2344 | 0.029556 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.2568 | -0.00017979 | 2.8946 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | 0.0015332 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 0.070087 | 0.004404 | 129.6452 | 0.038835 | 129.6189 | 0.0026002 | 0.23793 | 0.00041557 | 63.4115 | 0.023894 | 0.1621 | 0.0011513 | 0.20895 | -0.00034817 | 0.32251 | 0.0031962 | 3.0752 | 0.0012636
273.4 | 82.4 | 133.0605 | 0.046423 | 132.6601 | 0.0016062 | 0.29757 | 0.0016399 | 63.303 | 0.031455 | 0.43642 | 0.0017522 | 0.77546 | 0.0035444 | 0.49305 | 7.2991e-05 | 4.0869 | 0.0035663 | 132.5226 | 0.030062 | 131.8661 | 0.0015619 | 0.19244 | 8.4239e-05 | 65.2344 | 0.031179 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | 0.0014439 | 2.8946 | 7.2982e-05 | 0.30132 | -0.001769 | 0.19277 | -0.0013928 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.21368 | 0.0012074 | 0.070087 | 0.004404 | 129.7426 | 0.038835 | 129.7163 | 0.0026002 | 0.23793 | 0.00041557 | 63.5089 | 0.023894 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817 | 0.32251 | 0.0031962 | 3.0752 | 0.0012636
273.6 | 82.6 | 133.0605 | 0.0448 | 132.5627 | 0.0016062 | 0.29757 | 0.0032635 | 64.277 | 0.031455 | 0.53384 | 0.0033759 | 0.67808 | 0.0035444 | 0.59047 | 0.0049427 | 4.1843 | 0.0035663 | 132.4252 | 0.030062 | 131.8661 | 0.0015619 | 0.19244 | 8.4239e-05 | 65.3318 | 0.029556 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.2568 | 0.0014439 | 2.8946 | 0.0016967 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | 0.0015332 | 0.19851 | 0.0014152 | 0.17559 | 0.0015107 | -0.011119 | 0.0009884 | 0.21368 | 0.0012074 | 0.070087 | 0.004404 | 129.6452 | 0.038835 | 129.7163 | 0.0026002 | 0.23793 | 0.00041557 | 63.4115 | 0.023894 | 0.1621 | 0.0011513 | 0.20895 | 0.0012748 | 0.22513 | 0.0031962 | 3.0752 | 0.0012636
273.8 | 82.8 | 133.1579 | 0.0448 | 132.5627 | 0.0016062 | 0.29757 | 0.0032635 | 62.6212 | 0.031455 | 0.53384 | 0.0017522 | 0.77546 | 0.0035444 | 0.59047 | 0.0049427 | 4.1843 | 0.0019433 | 132.5226 | 0.030062 | 131.7687 | 0.0015619 | 0.19244 | 8.4239e-05 | 65.3318 | 0.029556 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | 0.0014439 | 2.8946 | 0.0016967 | 0.2039 | 0.001477 | 0.19277 | 0.00023025 | 0.017185 | 0.0015332 | 0.19851 | 0.0014152 | 0.27297 | -0.00011232 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 129.7426 | 0.040458 | 129.7163 | 0.0026002 | 0.33531 | 0.00041557 | 63.4115 | 0.025517 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 3.0752 | 0.0012636
274 | 83 | 133.0605 | 0.0448 | 132.5627 | 0.0016062 | 0.29757 | 0.0032635 | 64.3744 | 0.031455 | 0.53384 | 0.0033759 | 0.77546 | 0.0035444 | 0.59047 | 0.0049427 | 4.2817 | 0.0035663 | 132.4252 | 0.030062 | 131.7687 | 0.0015619 | 0.19244 | 8.4239e-05 | 65.2344 | 0.029556 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 2.8946 | 0.0016967 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | 0.0015332 | 0.19851 | -0.00020779 | 0.17559 | 0.0015107 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 129.6452 | 0.038835 | 129.6189 | 0.00097717 | 0.23793 | 0.00041557 | 63.4115 | 0.023894 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 3.0752 | 0.0012636
274.2 | 83.2 | 133.1579 | 0.043177 | 132.5627 | 0.0016062 | 0.39495 | 0.0032635 | 62.5239 | 0.031455 | 0.63122 | 0.0033759 | 0.97026 | 0.0035444 | 0.59047 | 0.0033197 | 4.0869 | 0.0035663 | 132.5226 | 0.030062 | 131.7687 | 0.0015619 | 0.19244 | 0.0017072 | 65.2344 | 0.031179 | 0.01988 | 0.0038865 | 0.11562 | 0.0013085 | 0.15942 | 0.0014439 | 2.992 | 0.0016967 | 0.30132 | 0.001477 | 0.19277 | 0.00023025 | 0.017185 | 0.0015332 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.21368 | 0.0012074 | 0.070087 | 0.004404 | 129.6452 | 0.038835 | 129.6189 | 0.0026002 | 0.23793 | 0.00041557 | 63.4115 | 0.023894 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748 | 0.22513 | 0.0048192 | 3.1726 | 0.0012636
274.4 | 83.4 | 133.0605 | 0.043177 | 132.6601 | 0.0016062 | 0.39495 | 0.0016399 | 64.4718 | 0.033078 | 0.53384 | 0.0033759 | 1.0676 | 0.0035444 | 0.59047 | 0.0049427 | 4.2817 | 0.0035663 | 132.5226 | 0.030062 | 131.7687 | 0.0015619 | 0.19244 | 8.4239e-05 | 65.2344 | 0.029556 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 2.992 | 0.0016967 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | -0.080196 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 129.6452 | 0.040458 | 129.7163 | 0.0026002 | 0.23793 | 0.00041557 | 63.4115 | 0.023894 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 3.1726 | 0.0012636
274.6 | 83.6 | 133.0605 | 0.043177 | 132.5627 | 0.0016062 | 0.29757 | 0.0032635 | 63.5952 | 0.033078 | 0.63122 | 0.0033759 | 0.97026 | 0.0035444 | 0.59047 | 0.0049427 | 4.1843 | 0.0035663 | 132.4252 | 0.030062 | 131.7687 | 0.0015619 | 0.19244 | 8.4239e-05 | 65.2344 | 0.031179 | 0.01988 | 0.0022635 | 0.11562 | -0.00031449 | 0.2568 | 0.0014439 | 2.8946 | 7.2982e-05 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.29589 | 0.0014152 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 129.6452 | 0.040458 | 129.6189 | 0.00097717 | 0.23793 | 0.00041557 | 63.4115 | 0.023894 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817 | 0.32251 | 0.0048192 | 3.1726 | 0.0012636
274.8 | 83.8 | 133.0605 | 0.043177 | 132.5627 | 0.0016062 | 0.39495 | 0.0016399 | 64.1796 | 0.033078 | 0.63122 | 0.0033759 | 0.97026 | 0.0035444 | 0.59047 | 0.0049427 | 4.1843 | 0.0035663 | 132.4252 | 0.030062 | 131.7687 | 0.0015619 | 0.19244 | 8.4239e-05 | 65.2344 | 0.031179 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | 0.0014439 | 2.992 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 129.6452 | 0.038835 | 129.6189 | 0.00097717 | 0.23793 | 0.00041557 | 63.4115 | 0.025517 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748 | 0.22513 | 0.0031962 | 3.1726 | 0.0012636
275 | 84 | 132.9631 | 0.043177 | 132.4653 | 0.0016062 | 0.29757 | 0.0032635 | 64.764 | 0.033078 | 0.63122 | 0.0033759 | 1.0676 | 0.0035444 | 0.59047 | 0.0049427 | 4.2817 | 0.0035663 | 132.4252 | 0.030062 | 131.6713 | 0.0015619 | 0.19244 | 8.4239e-05 | 65.2344 | 0.031179 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.2568 | 0.0014439 | 2.992 | 7.2982e-05 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.21368 | 0.0028311 | 0.16751 | 0.004404 | 129.6452 | 0.040458 | 129.6189 | 0.0026002 | 0.23793 | 0.00041557 | 63.4115 | 0.025517 | 0.1621 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0048192 | 3.27 | 0.0012636
275.2 | 84.2 | 133.0605 | 0.0448 | 132.5627 | 0.0016062 | 0.39495 | 0.0032635 | 64.4718 | 0.033078 | 0.63122 | 0.0033759 | 0.97026 | 0.0035444 | 0.68785 | 0.0049427 | 4.2817 | 0.0035663 | 132.4252 | 0.030062 | 131.6713 | 0.0015619 | 0.095061 | 0.0017072 | 65.2344 | 0.031179 | 0.11726 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | -0.00017979 | 3.0894 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 129.6452 | 0.040458 | 129.6189 | 0.0026002 | 0.23793 | 0.00041557 | 63.4115 | 0.025517 | 0.1621 | 0.0011513 | 0.20895 | 0.0012748 | 0.32251 | 0.0031962 | 3.27 | 0.0012636
275.4 | 84.4 | 133.0605 | 0.043177 | 132.5627 | 0.0016062 | 0.29757 | 0.0032635 | 64.1796 | 0.033078 | 0.63122 | 0.0033759 | 0.97026 | 0.0035444 | 0.59047 | 0.0049427 | 4.2817 | 0.0035663 | 132.4252 | 0.030062 | 131.6713 | 0.0015619 | 0.19244 | 8.4239e-05 | 65.2344 | 0.031179 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | 0.0014439 | 3.1868 | 0.0016967 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | 0.0015107 | 0.086261 | 0.0009884 | 0.21368 | 0.0012074 | 0.16751 | 0.004404 | 129.6452 | 0.040458 | 129.6189 | 0.00097717 | 0.23793 | 0.00041557 | 63.4115 | 0.023894 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748 | 0.32251 | 0.0048192 | 3.27 | 0.0012636
275.6 | 84.6 | 132.9631 | 0.0448 | 132.4653 | 0.0016062 | 0.29757 | 0.0016399 | 63.303 | 0.033078 | 0.53384 | 0.0017522 | 1.0676 | 0.0035444 | 0.59047 | 0.0049427 | 4.2817 | 0.0019433 | 132.4252 | 0.030062 | 131.6713 | 0.0015619 | 0.19244 | 8.4239e-05 | 65.2344 | 0.031179 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.2568 | -0.00017979 | 3.1868 | 0.0016967 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.29589 | 0.0014152 | 0.17559 | 0.0015107 | 0.086261 | 0.0009884 | 0.21368 | 0.0028311 | 0.16751 | 0.006027 | 129.6452 | 0.040458 | 129.5215 | 0.00097717 | 0.23793 | 0.00041557 | 63.4115 | 0.025517 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748 | 0.32251 | 0.0048192 | 3.27 | 0.0012636
275.8 | 84.8 | 132.9631 | 0.043177 | 132.4653 | 0.0016062 | 0.39495 | 0.0016399 | 62.9135 | 0.033078 | 0.63122 | 0.0017522 | 1.0676 | 0.0035444 | 0.59047 | 0.0033197 | 4.1843 | 0.0035663 | 132.3278 | 0.030062 | 131.6713 | 0.0015619 | 0.19244 | 8.4239e-05 | 65.2344 | 0.031179 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 3.1868 | 0.0016967 | 0.2039 | 0.001477 | 0.19277 | 0.00023025 | 0.017185 | 0.0015332 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.21368 | 0.0012074 | 0.16751 | 0.004404 | 129.6452 | 0.040458 | 129.5215 | 0.0026002 | 0.23793 | 0.00041557 | 63.4115 | 0.025517 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748 | 0.22513 | 0.0048192 | 3.27 | 0.0012636
276 | 85 | 132.8657 | 0.0448 | 132.3679 | 0.0016062 | 0.29757 | 0.0032635 | 63.6926 | 0.031455 | 0.63122 | 0.0017522 | 1.2624 | 0.0035444 | 0.59047 | 0.0033197 | 4.2817 | 0.0051899 | 132.3278 | 0.031685 | 131.6713 | 0.0015619 | 0.19244 | 8.4239e-05 | 65.2344 | 0.031179 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 3.1868 | 0.0016967 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | -0.080196 | 0.0015332 | 0.29589 | 0.0014152 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.21368 | 0.0012074 | 0.16751 | 0.004404 | 129.5478 | 0.040458 | 129.5215 | 0.0026002 | 0.23793 | 0.00041557 | 63.4115 | 0.025517 | 0.25952 | -0.00047174 | 0.20895 | 0.0012748 | 0.32251 | 0.0048192 | 3.3674 | 0.0012636
276.2 | 85.2 | 132.9631 | 0.043177 | 132.4653 | 0.0016062 | 0.39495 | 0.0032635 | 62.7187 | 0.031455 | 0.63122 | 0.0033759 | 1.2624 | 0.0035444 | 0.59047 | 0.0049427 | 4.1843 | 0.0035663 | 132.3278 | 0.030062 | 131.7687 | 0.0015619 | 0.19244 | 8.4239e-05 | 65.2344 | 0.031179 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | 0.0014439 | 3.1868 | 0.0016967 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | -0.080196 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.21368 | 0.0012074 | 0.16751 | 0.004404 | 129.6452 | 0.040458 | 129.6189 | 0.00097717 | 0.23793 | 0.00041557 | 63.4115 | 0.025517 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817 | 0.32251 | 0.0031962 | 3.3674 | 0.0012636
276.4 | 85.4 | 132.9631 | 0.043177 | 132.4653 | 0.0016062 | 0.29757 | 0.0032635 | 64.1796 | 0.031455 | 0.63122 | 0.0033759 | 1.0676 | 0.0035444 | 0.59047 | 0.0049427 | 4.1843 | 0.0035663 | 132.3278 | 0.030062 | 131.6713 | 0.0015619 | 0.19244 | 8.4239e-05 | 65.2344 | 0.031179 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | 0.0014439 | 3.1868 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.27297 | -0.00011232 | 0.086261 | 0.0009884 | 0.11626 | 0.0028311 | 0.16751 | 0.004404 | 129.6452 | 0.040458 | 129.6189 | 0.0026002 | 0.23793 | 0.00041557 | 63.4115 | 0.025517 | 0.1621 | 0.0011513 | 0.20895 | 0.0012748 | 0.22513 | 0.0048192 | 3.3674 | 0.0012636
276.6 | 85.6 | 132.8657 | 0.0448 | 132.3679 | 0.0016062 | 0.39495 | 0.0032635 | 62.3291 | 0.031455 | 0.53384 | 0.0017522 | 1.2624 | 0.0019208 | 0.59047 | 0.0049427 | 4.2817 | 0.0035663 | 132.4252 | 0.031685 | 131.7687 | 0.0015619 | 0.19244 | 8.4239e-05 | 65.2344 | 0.031179 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 3.1868 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | 0.0015107 | 0.086261 | 0.0009884 | 0.21368 | 0.0012074 | 0.16751 | 0.004404 | 129.6452 | 0.040458 | 129.5215 | 0.0026002 | 0.23793 | 0.00041557 | 63.5089 | 0.025517 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748 | 0.32251 | 0.0031962 | 3.3674 | 0.0012636
276.8 | 85.8 | 128.1907 | 0.0042186 | 128.3747 | 0.019463 | 0.10277 | 0.0016399 | 53.6608 | 0.0087285 | 0.14424 | 0.0017522 | 0.19109 | 0.00029777 | 0.20087 | 0.0065663 | 0.28848 | 0.011683 | 132.3278 | 0.030062 | 131.6713 | 0.0015619 | 0.19244 | 8.4239e-05 | 65.2344 | 0.029556 | 0.01988 | 0.0038865 | -0.079185 | 0.0013085 | 0.2568 | 0.0046906 | 3.1868 | 7.2982e-05 | 0.2039 | -0.00014601 | -0.78119 | -0.0095091 | -0.17758 | 0.0047798 | 0.19851 | 0.0014152 | 0.37035 | 0.0015107 | 0.086261 | 0.0042351 | 0.018878 | 0.0012074 | 0.16751 | 0.004404 | 128.1843 | 0.040458 | 129.6189 | 0.0042238 | 0.23793 | 0.00041557 | 63.4115 | 0.028764 | 0.25952 | 0.0011513 | 0.11153 | -0.016581 | 0.32251 | 0.0048192 | 3.3674 | 0.0012636
277 | 86 | 131.5996 | 0.025321 | 130.6148 | 0.0016062 | 0.10277 | -0.021086 | 57.8488 | 0.023338 | 0.53384 | 0.00012922 | 1.0676 | 0.0019208 | 0.20087 | 0.0016967 | 3.113 | 0.0051899 | 132.2304 | 0.031685 | 131.6713 | -6.1803e-05 | 0.19244 | 8.4239e-05 | 65.2344 | 0.031179 | 0.01988 | 0.0038865 | 0.11562 | -0.00031449 | 0.15942 | -0.00017979 | 3.1868 | 0.0016967 | 0.2039 | -0.00014601 | 0.095394 | -0.0013928 | 0.017185 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.17559 | 0.0015107 | 0.086261 | 0.0009884 | 0.21368 | 0.0028311 | 0.16751 | 0.004404 | 129.5478 | 0.040458 | 129.5215 | 0.00097717 | 0.23793 | 0.00041557 | 63.3141 | 0.023894 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748 | 0.32251 | 0.0048192 | 3.3674 | 0.0012636
277.2 | 86.2 | 132.9631 | 0.046423 | 132.3679 | 0.0016062 | 0.39495 | 0.0032635 | 62.4265 | 0.031455 | 0.72864 | 0.0033759 | 2.4312 | 0.00029777 | 0.78523 | 0.0033197 | 4.1843 | 0.0035663 | 132.4252 | 0.031685 | 131.6713 | 0.0015619 | 0.19244 | 8.4239e-05 | 65.2344 | 0.031179 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | -0.00017979 | 3.1868 | 7.2982e-05 | 0.30132 | 0.001477 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.27297 | 0.0015107 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 129.5478 | 0.040458 | 129.6189 | 0.0026002 | 0.23793 | 0.00041557 | 63.4115 | 0.025517 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748 | 0.22513 | 0.0031962 | 3.3674 | 0.0012636
277.4 | 86.4 | 132.8657 | 0.0448 | 132.3679 | 0.0016062 | 0.39495 | 0.0016399 | 63.4978 | 0.031455 | 0.63122 | 0.0017522 | 1.4572 | 0.0019208 | 1.0774 | 0.0049427 | 3.9895 | 0.0035663 | 132.3278 | 0.030062 | 131.6713 | 0.0015619 | 0.19244 | 8.4239e-05 | 65.2344 | 0.031179 | 0.11726 | 0.00064048 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 3.1868 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.17559 | 0.0015107 | 0.086261 | 0.0009884 | 0.21368 | 0.0012074 | 0.16751 | 0.004404 | 129.4504 | 0.040458 | 129.5215 | 0.0026002 | 0.23793 | 0.00041557 | 63.4115 | 0.025517 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748 | 0.32251 | 0.0031962 | 3.27 | 0.0012636
277.6 | 86.6 | 132.8657 | 0.0448 | 132.3679 | 0.0016062 | 0.39495 | 0.0016399 | 63.8874 | 0.031455 | 0.63122 | 0.0033759 | 1.0676 | 0.0035444 | 0.68785 | 0.0049427 | 4.1843 | 0.0035663 | 132.3278 | 0.030062 | 131.6713 | 0.0015619 | 0.19244 | 8.4239e-05 | 65.2344 | 0.031179 | 0.01988 | 0.0022635 | 0.11562 | 0.0013085 | 0.2568 | 0.0014439 | 3.0894 | 0.0016967 | 0.2039 | -0.00014601 | 0.29015 | 0.00023025 | 0.017185 | 0.0015332 | 0.19851 | 0.0014152 | 0.27297 | 0.0015107 | 0.086261 | 0.0009884 | 0.11626 | 0.0028311 | 0.16751 | 0.004404 | 129.5478 | 0.040458 | 129.5215 | 0.0026002 | 0.23793 | 0.00041557 | 63.4115 | 0.025517 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817 | 0.32251 | 0.0048192 | 3.3674 | 0.0012636
277.8 | 86.8 | 132.9631 | 0.0448 | 132.3679 | 0.0016062 | 0.29757 | 0.0016399 | 62.816 | 0.033078 | 0.63122 | 0.0017522 | 1.0676 | 0.0019208 | 0.59047 | 0.0049427 | 4.0869 | 0.0019433 | 132.3278 | 0.030062 | 131.6713 | 0.0015619 | 0.19244 | 8.4239e-05 | 65.137 | 0.031179 | 0.01988 | 0.0022635 | 0.11562 | 0.0013085 | 0.15942 | -0.00017979 | 3.0894 | 0.0016967 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.21368 | 0.0012074 | 0.16751 | 0.004404 | 129.5478 | 0.040458 | 129.5215 | 0.0026002 | 0.23793 | 0.00041557 | 63.4115 | 0.025517 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748 | 0.32251 | 0.0031962 | 3.27 | 0.0012636
278 | 87 | 132.7683 | 0.0448 | 132.2706 | 0.0016062 | 0.29757 | 0.0016399 | 62.0369 | 0.031455 | 0.63122 | 0.0033759 | 1.0676 | 0.0035444 | 0.59047 | 0.0049427 | 4.1843 | 0.0035663 | 132.2304 | 0.031685 | 131.6713 | 0.0015619 | 0.19244 | 0.0017072 | 65.137 | 0.031179 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.2568 | 0.0014439 | 3.0894 | 0.0016967 | 0.30132 | 0.001477 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.17559 | 0.0015107 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 129.4504 | 0.040458 | 129.4241 | 0.0026002 | 0.23793 | 0.00041557 | 63.4115 | 0.025517 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748 | 0.32251 | 0.0031962 | 3.27 | 0.0012636
278.2 | 87.2 | 132.8657 | 0.0448 | 132.2706 | 0.0016062 | 0.29757 | 0.0016399 | 63.303 | 0.031455 | 0.53384 | 0.0033759 | 1.0676 | 0.0035444 | 0.59047 | 0.0033197 | 4.1843 | 0.0035663 | 132.2304 | 0.031685 | 131.574 | 0.0015619 | 0.19244 | 8.4239e-05 | 65.2344 | 0.031179 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.2568 | 0.0014439 | 3.0894 | 0.0016967 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | -0.080196 | -8.9855e-05 | 0.29589 | -0.00020779 | 0.27297 | -0.00011232 | -0.011119 | 0.0009884 | 0.21368 | 0.0012074 | 0.16751 | 0.004404 | 129.4504 | 0.040458 | 129.5215 | 0.0026002 | 0.23793 | 0.00041557 | 63.3141 | 0.025517 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748 | 0.22513 | 0.0048192 | 3.27 | 0.0012636
278.4 | 87.4 | 132.7683 | 0.0448 | 132.2706 | 0.0016062 | 0.29757 | 0.0016399 | 63.79 | 0.033078 | 0.53384 | 0.0017522 | 0.87284 | 0.0019208 | 0.59047 | 0.0033197 | 4.0869 | 0.0019433 | 132.2304 | 0.031685 | 131.574 | 0.0015619 | 0.19244 | 0.0017072 | 65.137 | 0.031179 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | 0.0014439 | 3.0894 | 7.2982e-05 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | 0.0015332 | 0.19851 | 0.0014152 | 0.17559 | 0.0015107 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 0.070087 | 0.004404 | 129.4504 | 0.042082 | 129.5215 | 0.00097717 | 0.23793 | 0.00041557 | 63.4115 | 0.025517 | 0.25952 | 0.0011513 | 0.30633 | 0.0012748 | 0.22513 | 0.0048192 | 3.27 | 0.0028873
278.6 | 87.6 | 132.7683 | 0.0448 | 132.3679 | 0.0016062 | 0.29757 | 0.0016399 | 63.79 | 0.031455 | 0.53384 | 0.0017522 | 0.87284 | 0.0035444 | 0.59047 | 0.0033197 | 4.0869 | 0.0035663 | 132.2304 | 0.031685 | 131.574 | 0.0015619 | 0.19244 | 8.4239e-05 | 65.137 | 0.031179 | 0.01988 | 0.0022635 | 0.11562 | 0.0013085 | 0.15942 | -0.00017979 | 3.0894 | 7.2982e-05 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.29589 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 129.5478 | 0.042082 | 129.5215 | 0.0026002 | 0.23793 | 0.00041557 | 63.4115 | 0.025517 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817 | 0.32251 | 0.0048192 | 3.27 | 0.0012636
278.8 | 87.8 | 132.6709 | 0.0448 | 132.2706 | 0.0016062 | 0.20015 | 1.6859e-05 | 63.4004 | 0.033078 | 0.53384 | 0.0017522 | 0.77546 | 0.0019208 | 0.49305 | 0.0033197 | 4.0869 | 0.0019433 | 132.2304 | 0.031685 | 131.574 | 0.0015619 | 0.19244 | 8.4239e-05 | 65.2344 | 0.031179 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.2568 | 0.0014439 | 3.0894 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | 0.0015332 | 0.19851 | 0.0014152 | 0.27297 | 0.0015107 | 0.086261 | 0.0009884 | 0.21368 | 0.0012074 | 0.16751 | 0.004404 | 129.4504 | 0.040458 | 129.5215 | 0.0026002 | 0.23793 | 0.00041557 | 63.3141 | 0.025517 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0048192 | 3.3674 | 0.0012636
279 | 88 | 132.7683 | 0.046423 | 132.2706 | 0.0016062 | 0.20015 | 0.0016399 | 63.79 | 0.033078 | 0.63122 | 0.0033759 | 0.87284 | 0.010037 | 0.39567 | 0.0033197 | 3.8921 | 0.0019433 | 132.3278 | 0.031685 | 131.6713 | 0.0015619 | 0.19244 | 8.4239e-05 | 65.2344 | 0.031179 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.2568 | 0.0014439 | 3.1868 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.0018533 | 0.017185 | -8.9855e-05 | 0.29589 | 0.0014152 | 0.17559 | 0.0015107 | 0.086261 | 0.0009884 | 0.21368 | 0.0012074 | 0.16751 | 0.004404 | 129.5478 | 0.040458 | 129.5215 | 0.0026002 | 0.23793 | 0.00041557 | 63.4115 | 0.023894 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748 | 0.32251 | 0.0048192 | 3.27 | 0.0012636
279.2 | 88.2 | 132.7683 | 0.0448 | 132.2706 | 0.0016062 | 0.29757 | 0.0016399 | 63.4978 | 0.031455 | 0.53384 | 0.0017522 | 0.77546 | 0.0035444 | 0.49305 | 0.0033197 | 4.0869 | 0.0019433 | 132.2304 | 0.031685 | 131.574 | 0.0015619 | 0.19244 | 8.4239e-05 | 65.2344 | 0.031179 | 0.01988 | 0.0022635 | 0.11562 | -0.00031449 | 0.2568 | 0.0014439 | 3.0894 | 7.2982e-05 | 0.30132 | -0.00014601 | 0.19277 | 0.0018533 | 0.017185 | 0.0015332 | 0.19851 | 0.0014152 | 0.17559 | 0.0015107 | 0.086261 | 0.0009884 | 0.21368 | 0.0012074 | 0.16751 | 0.004404 | 129.4504 | 0.040458 | 129.4241 | 0.0026002 | 0.23793 | 0.00041557 | 63.4115 | 0.025517 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817 | 0.32251 | 0.0048192 | 3.3674 | 0.0012636
279.4 | 88.4 | 132.6709 | 0.0448 | 132.2706 | 0.0016062 | 0.29757 | 0.0016399 | 62.7187 | 0.033078 | 0.53384 | 0.0017522 | 1.0676 | 0.0035444 | 0.49305 | 0.0033197 | 4.1843 | 0.0019433 | 132.2304 | 0.031685 | 131.574 | 0.0015619 | 0.19244 | 8.4239e-05 | 65.137 | 0.031179 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 3.1868 | 0.0016967 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | -0.080196 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.27297 | -0.00011232 | 0.086261 | 0.0009884 | 0.21368 | 0.0012074 | 0.16751 | 0.006027 | 129.4504 | 0.042082 | 129.4241 | 0.0026002 | 0.23793 | 0.00041557 | 63.4115 | 0.025517 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748 | 0.32251 | 0.0031962 | 3.3674 | 0.0012636
279.6 | 88.6 | 132.7683 | 0.0448 | 132.2706 | 0.0016062 | 0.29757 | 1.6859e-05 | 63.303 | 0.033078 | 0.53384 | 0.0017522 | 0.87284 | 0.0019208 | 0.49305 | 0.0033197 | 4.1843 | 0.0019433 | 132.2304 | 0.033308 | 131.574 | 0.0015619 | 0.19244 | 0.0017072 | 65.137 | 0.031179 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | -0.00017979 | 3.0894 | 7.2982e-05 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.27297 | 0.0015107 | -0.011119 | 0.0009884 | 0.21368 | 0.0012074 | 0.16751 | 0.004404 | 129.4504 | 0.040458 | 129.4241 | 0.0026002 | 0.23793 | 0.00041557 | 63.4115 | 0.025517 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748 | 0.22513 | 0.0031962 | 3.3674 | 0.0012636
279.8 | 88.8 | 132.6709 | 0.0448 | 132.1731 | 0.0016062 | 0.20015 | 0.0016399 | 63.2056 | 0.031455 | 0.43642 | 0.0017522 | 0.77546 | 0.0035444 | 0.49305 | 0.0033197 | 4.1843 | 0.0019433 | 132.2304 | 0.031685 | 131.574 | 0.0015619 | 0.19244 | 8.4239e-05 | 65.137 | 0.031179 | 0.11726 | 0.0022635 | 0.018196 | 0.0013085 | 0.2568 | 0.0014439 | 3.0894 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.29015 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.27297 | 0.0015107 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 129.4504 | 0.040458 | 129.3268 | 0.0026002 | 0.23793 | 0.00041557 | 63.3141 | 0.025517 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748 | 0.22513 | 0.0064422 | 3.27 | 0.0012636
280 | 89 | 131.3074 | 0.036684 | 131.2966 | 0.0016062 | -0.092027 | 0.0016399 | 59.0176 | 0.021715 | 0.14424 | 0.0066219 | 0.77546 | 0.042503 | 0.39567 | 0.0016967 | 2.9182 | -0.0029264 | 132.2304 | 0.031685 | 131.6713 | 0.0015619 | -0.78152 | 8.4239e-05 | 65.137 | 0.032803 | 0.01988 | 0.00064048 | 0.018196 | 0.0029322 | -2.1781 | -0.044008 | 3.1868 | 0.0016967 | 0.3987 | -0.00014601 | 0.19277 | 0.0067236 | 0.017185 | 0.0015332 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | 0.086261 | -0.0006346 | 0.21368 | 0.0012074 | 0.16751 | 0.006027 | 129.4504 | 0.040458 | 129.5215 | 0.00097717 | 0.33531 | 0.00041557 | 63.4115 | 0.025517 | 0.1621 | -0.00047174 | 0.50113 | 0.0012748 | 0.22513 | 0.0031962 | 3.27 | 0.0012636
280.2 | 89.2 | 133.0605 | 0.0090883 | 127.1085 | 0.0048528 | 0.20015 | -0.01784 | 53.5634 | 0.021715 | -0.14794 | -0.0014944 | 0.38586 | -0.0013259 | 0.10349 | -0.050248 | 1.652 | 0.0019433 | 132.133 | 0.049541 | 131.3792 | 0.0080546 | -0.09974 | 8.4239e-05 | 64.1631 | 0.032803 | 0.11726 | 0.0022635 | -0.079185 | -0.00031449 | 0.35418 | -0.029399 | 3.1868 | 0.0016967 | 0.0090945 | -0.00014601 | 0.19277 | 0.027826 | -0.76198 | 0.0064028 | 0.39327 | 0.0030389 | 0.078174 | 0.008004 | -0.011119 | 0.028584 | 0.31106 | 0.0028311 | 0.16751 | 0.004404 | 129.4504 | 0.042082 | 128.5476 | 0.023703 | 0.04313 | 0.00041557 | 63.2167 | 0.030387 | 0.25952 | -0.0020947 | 0.30633 | -0.00034817 | 0.51731 | 0.0031962 | 3.3674 | 0.0012636
280.4 | 89.4 | 132.5735 | 0.0448 | 132.2706 | 0.0016062 | 0.20015 | 0.0016399 | 63.0108 | 0.031455 | 0.43642 | 0.0017522 | 1.5546 | 0.0035444 | 0.49305 | 0.0016967 | 4.0869 | 0.0019433 | 132.2304 | 0.031685 | 131.574 | 0.0015619 | 0.19244 | 8.4239e-05 | 65.137 | 0.031179 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.2568 | 0.0014439 | 3.1868 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.27297 | 0.0015107 | -0.011119 | 0.0009884 | 0.11626 | 0.0028311 | 0.16751 | 0.006027 | 129.4504 | 0.042082 | 129.4241 | 0.00097717 | 0.23793 | 0.00041557 | 63.3141 | 0.02714 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0048192 | 3.3674 | 0.0012636
280.6 | 89.6 | 132.5735 | 0.0448 | 132.1731 | 0.0016062 | 0.20015 | 0.0016399 | 63.4004 | 0.031455 | 0.43642 | 0.0017522 | 0.87284 | 0.0035444 | 0.39567 | 0.0033197 | 4.0869 | 0.0019433 | 132.2304 | 0.033308 | 131.574 | 0.0015619 | 0.19244 | 8.4239e-05 | 65.137 | 0.031179 | 0.01988 | 0.0022635 | 0.11562 | 0.0013085 | 0.2568 | -0.00017979 | 3.0894 | 7.2982e-05 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | 0.0015332 | 0.19851 | -0.00020779 | 0.17559 | 0.0015107 | 0.086261 | 0.0009884 | 0.21368 | 0.0012074 | 0.16751 | 0.004404 | 129.4504 | 0.042082 | 129.4241 | 0.0026002 | 0.23793 | 0.00041557 | 63.3141 | 0.025517 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748 | 0.22513 | 0.0048192 | 3.3674 | 0.0012636
280.8 | 89.8 | 132.4761 | 0.0448 | 132.0758 | 0.0016062 | 0.20015 | 1.6859e-05 | 63.4004 | 0.033078 | 0.43642 | 0.0017522 | 0.67808 | 0.0035444 | 0.39567 | 0.0033197 | 4.1843 | 0.0019433 | 132.133 | 0.031685 | 131.4765 | 0.0015619 | 0.19244 | 8.4239e-05 | 65.137 | 0.031179 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 3.1868 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | 0.0015332 | 0.19851 | 0.0014152 | 0.17559 | 0.0015107 | -0.011119 | 0.0009884 | 0.21368 | 0.0012074 | 0.16751 | 0.004404 | 129.4504 | 0.042082 | 129.4241 | 0.0026002 | 0.23793 | 0.00041557 | 63.3141 | 0.025517 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817 | 0.32251 | 0.0048192 | 3.27 | 0.0012636
281 | 90 | 132.5735 | 0.0448 | 132.0758 | 0.0016062 | 0.10277 | 1.6859e-05 | 63.303 | 0.031455 | 0.43642 | 0.0017522 | 0.67808 | 0.0035444 | 0.39567 | 0.0033197 | 4.1843 | 0.0019433 | 132.2304 | 0.031685 | 131.574 | 0.0015619 | 0.095061 | 8.4239e-05 | 65.137 | 0.031179 | 0.01988 | 0.0038865 | 0.11562 | 0.0013085 | 0.15942 | -0.00017979 | 3.0894 | 7.2982e-05 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.17559 | 0.0015107 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 129.353 | 0.042082 | 129.4241 | 0.0026002 | 0.23793 | 0.00041557 | 63.3141 | 0.025517 | 0.25952 | 0.0011513 | 0.11153 | 0.0012748 | 0.22513 | 0.0031962 | 3.3674 | 0.0012636
281.2 | 90.2 | 132.4761 | 0.046423 | 131.9783 | 0.0016062 | 0.10277 | 0.0016399 | 63.1082 | 0.031455 | 0.33904 | 0.00012922 | 0.58066 | 0.0035444 | 0.39567 | 0.0033197 | 4.0869 | 0.0019433 | 132.133 | 0.031685 | 131.4765 | 0.0015619 | 0.19244 | 8.4239e-05 | 65.137 | 0.031179 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 3.1868 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | -0.0013928 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | 0.0015107 | -0.011119 | 0.0009884 | 0.21368 | 0.0012074 | 0.16751 | 0.004404 | 129.353 | 0.042082 | 129.3268 | 0.0026002 | 0.23793 | 0.00041557 | 63.3141 | 0.02714 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 3.27 | 0.0012636
281.4 | 90.4 | 132.6709 | 0.046423 | 131.9783 | 0.0016062 | 0.10277 | 1.6859e-05 | 62.7187 | 0.033078 | 0.24166 | 0.00012922 | 0.58066 | 0.0019208 | 0.29825 | 0.0033197 | 4.0869 | 0.0019433 | 132.2304 | 0.031685 | 131.574 | 0.0015619 | 0.19244 | 8.4239e-05 | 65.2344 | 0.031179 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.2568 | 0.0014439 | 3.1868 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | 0.0015107 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.006027 | 129.353 | 0.042082 | 129.3268 | 0.00097717 | 0.23793 | 0.00041557 | 63.3141 | 0.025517 | 0.1621 | 0.0011513 | 0.20895 | 0.0012748 | 0.22513 | 0.0048192 | 3.3674 | 0.0012636
281.6 | 90.6 | 132.5735 | 0.0448 | 132.0758 | 0.0016062 | 0.10277 | 1.6859e-05 | 62.5239 | 0.033078 | 0.24166 | 0.0033759 | 0.67808 | 0.0035444 | 0.29825 | 0.0016967 | 4.1843 | 0.0035663 | 132.133 | 0.033308 | 131.574 | 0.0015619 | 0.19244 | 8.4239e-05 | 65.137 | 0.032803 | 0.01988 | 0.0022635 | 0.11562 | 0.0013085 | 0.15942 | 0.0014439 | 3.1868 | 0.0016967 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.21368 | 0.0012074 | 0.16751 | 0.004404 | 129.4504 | 0.043705 | 129.3268 | 0.0026002 | 0.23793 | 0.00041557 | 63.3141 | 0.02714 | 0.25952 | 0.0011513 | 0.11153 | 0.0012748 | 0.22513 | 0.0031962 | 3.27 | 0.0012636
281.8 | 90.8 | 132.4761 | 0.046423 | 131.9783 | 0.0016062 | 0.10277 | 0.0016399 | 62.2317 | 0.031455 | 0.33904 | 0.00012922 | 0.77546 | 0.0019208 | 0.29825 | 0.0016967 | 4.0869 | 0.00032025 | 132.133 | 0.033308 | 131.4765 | 0.0015619 | 0.19244 | 8.4239e-05 | 65.137 | 0.031179 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | 0.0014439 | 3.1868 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | 0.0015332 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.21368 | 0.0012074 | 0.16751 | 0.004404 | 129.353 | 0.042082 | 129.4241 | 0.0026002 | 0.23793 | 0.00041557 | 63.3141 | 0.025517 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748 | 0.22513 | 0.0048192 | 3.27 | 0.0012636
282 | 91 | 132.4761 | 0.046423 | 131.9783 | 0.0016062 | 0.10277 | 1.6859e-05 | 62.5239 | 0.031455 | 0.33904 | 0.0017522 | 0.97026 | 0.0019208 | 0.29825 | 0.0033197 | 4.1843 | 0.0019433 | 132.133 | 0.033308 | 131.4765 | 0.0015619 | 0.19244 | 8.4239e-05 | 65.137 | 0.032803 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | -0.00017979 | 3.0894 | 7.2982e-05 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | 0.0015107 | 0.086261 | 0.0009884 | 0.11626 | -0.00041558 | 0.070087 | 0.004404 | 129.353 | 0.040458 | 129.3268 | 0.0026002 | 0.23793 | 0.00041557 | 63.3141 | 0.02714 | 0.25952 | -0.00047174 | 0.20895 | 0.0012748 | 0.22513 | 0.0048192 | 3.27 | 0.0012636
282.2 | 91.2 | 132.0865 | 0.026944 | 129.8357 | 0.0016062 | 0.10277 | 0.0016399 | 59.7968 | 0.028208 | 0.33904 | 0.0017522 | 0.67808 | 0.00029777 | 0.20087 | 0.0016967 | 2.8208 | 0.0019433 | 132.133 | 0.034931 | 131.4765 | 0.0015619 | 0.19244 | 8.4239e-05 | 65.137 | 0.031179 | 0.01988 | 0.0022635 | 0.018196 | -0.0051842 | 0.062 | 0.0014439 | 3.1868 | 7.2982e-05 | 0.2039 | 0.001477 | 0.095394 | 0.00023025 | 0.017185 | 0.0015332 | 0.19851 | 0.0014152 | 0.27297 | 0.0031344 | -0.011119 | 0.0009884 | 0.11626 | 0.0028311 | 0.070087 | 0.004404 | 129.4504 | 0.043705 | 129.4241 | 0.0026002 | 0.23793 | 0.00041557 | 63.3141 | 0.025517 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817 | 0.32251 | 0.0031962 | 3.4648 | 0.0012636
282.4 | 91.4 | 131.5996 | 0.030191 | 129.4461 | -1.6843e-05 | 0.10277 | -0.047058 | 55.4139 | 0.018468 | 0.14424 | 0.00012922 | 1.5546 | 0.0019208 | 0.20087 | 0.0016967 | 2.0416 | 0.0019433 | 132.2304 | 0.038178 | 131.574 | -0.03415 | 0.19244 | 8.4239e-05 | 65.2344 | 0.031179 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.062 | -0.00017979 | 3.0894 | 7.2982e-05 | 0.2039 | 0.0031007 | -0.002026 | 0.00023025 | 0.017185 | 0.0015332 | 0.29589 | 0.0030389 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.21368 | 0.0012074 | 0.16751 | 0.004404 | 129.4504 | 0.042082 | 129.4241 | 0.00097717 | 0.23793 | 0.00041557 | 63.3141 | 0.025517 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748 | 0.22513 | 0.0031962 | 3.3674 | 0.0012636
282.6 | 91.6 | 132.0865 | 0.0448 | 131.881 | 0.0016062 | 0.10277 | 0.0016399 | 61.3551 | 0.036324 | 0.63122 | 0.00012922 | 1.2624 | 0.00029777 | 0.49305 | 0.0016967 | 4.1843 | 0.0035663 | 132.133 | 0.033308 | 131.4765 | 0.0031849 | 0.095061 | 8.4239e-05 | 65.137 | 0.032803 | 0.01988 | 0.0038865 | 0.018196 | 0.0013085 | 0.15942 | 0.0014439 | 3.1868 | 7.2982e-05 | 0.0090945 | 0.001477 | 0.095394 | 0.00023025 | -0.080196 | 0.0015332 | 0.19851 | 0.0014152 | 0.17559 | -0.037447 | 0.086261 | 0.0009884 | 0.21368 | 0.0012074 | 0.16751 | 0.004404 | 129.353 | 0.045329 | 129.3268 | 0.00097717 | 0.14051 | 0.00041557 | 63.3141 | 0.025517 | 1.7205 | 0.0011513 | 0.11153 | 0.0012748 | 0.32251 | 0.0064422 | 3.3674 | 0.0012636
282.8 | 91.8 | 131.5996 | 0.020451 | 128.3747 | 0.0048528 | 0.10277 | 0.0016399 | 54.2451 | 0.011975 | 0.33904 | 0.00012922 | 17.625 | 0.010037 | 0.10349 | 0.0033197 | 0.38586 | 0.0019433 | 132.0357 | 0.031685 | 131.574 | -6.1803e-05 | 0.19244 | 8.4239e-05 | 65.137 | 0.031179 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | 0.0030669 | 3.1868 | 7.2982e-05 | 0.30132 | 0.001477 | 0.19277 | 0.00023025 | 0.017185 | 0.0031562 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | 0.086261 | -0.0006346 | 0.11626 | 0.0012074 | 0.070087 | 0.006027 | 130.9114 | 0.040458 | 129.4241 | 0.0026002 | -1.8074 | 0.00041557 | 63.3141 | 0.023894 | 0.1621 | 0.0011513 | 0.20895 | 0.0028978 | 0.22513 | 0.0031962 | 3.3674 | 0.0012636
283 | 92 | 132.5735 | 0.048047 | 131.7836 | 0.0032298 | 0.0053935 | -0.0032298 | 59.0176 | 0.028208 | 0.43642 | 0.00012922 | 2.7234 | 0.0019208 | 0.49305 | 0.0016967 | 4.3791 | 0.00032025 | 132.133 | 0.031685 | 131.4765 | 0.0015619 | 0.19244 | 8.4239e-05 | 65.137 | 0.031179 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | -0.00017979 | 3.2842 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | 0.0015332 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 129.353 | 0.042082 | 129.4241 | 0.0026002 | 0.14051 | 0.00041557 | 63.3141 | 0.025517 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748 | 0.22513 | 0.0031962 | 3.27 | 0.0012636
283.2 | 92.2 | 129.8464 | 0.018828 | 128.6669 | -1.6843e-05 | -0.092027 | -0.0032298 | 47.0378 | 0.013598 | 0.33904 | -0.0063641 | 1.1651 | -0.11658 | 0.39567 | -0.0047967 | 0.67808 | 0.0019433 | 132.3278 | 0.031685 | 131.3792 | 0.0015619 | 0.38724 | -0.0015388 | 65.7214 | 0.032803 | -0.17492 | 0.00064048 | 0.69998 | -0.00031449 | 0.2568 | 0.0030669 | 3.2842 | 0.021176 | 0.10651 | -0.0033927 | 0.38758 | 0.00023025 | -0.4698 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | 0.0031344 | 2.229 | 0.0026121 | 0.70066 | 0.0012074 | 0.26489 | 0.015766 | 129.2556 | 0.042082 | 129.3268 | 0.010717 | 0.14051 | -0.0060771 | 63.022 | 0.025517 | 0.25952 | 0.0011513 | 0.11153 | -0.00034817 | 0.71211 | 0.0031962 | 2.9778 | 0.0012636
283.4 | 92.4 | 130.0412 | 0.012335 | 128.9591 | 0.017839 | -0.38421 | 0.0048865 | 54.5374 | 0.0054818 | -8.524 | 0.0082456 | 0.87284 | -0.0013259 | -0.091316 | 0.0016967 | -0.10113 | -0.12143 | 132.133 | 0.036554 | 131.4765 | 0.0015619 | -0.39192 | 8.4239e-05 | 65.2344 | 0.034426 | 0.21468 | 0.0022635 | -0.1766 | -0.0019375 | -0.03538 | -0.0034258 | 3.2842 | 0.0033197 | 0.2039 | 0.001477 | 0.38758 | 0.00023025 | -0.080196 | 0.0015332 | 0.29589 | 0.0014152 | 0.17559 | 0.040469 | -0.40072 | 0.0009884 | -1.3447 | 0.0060771 | 0.070087 | 0.0027804 | 129.2556 | 0.043705 | 129.3268 | 0.00097717 | 0.23793 | 0.00041557 | 63.6063 | 0.025517 | 0.064722 | -0.0085881 | 0.79331 | 0.0012748 | 0.51731 | 0.0048192 | 0.54291 | 0.012627
283.6 | 92.6 | 122.0547 | 0.00097195 | 106.3631 | -0.0032635 | 1.0767 | 0.013003 | 26.2924 | 0.0071055 | 117.6044 | 1.9383 | 127.6831 | 5.3977 | 324.2391 | 5.404 | 116.0929 | 1.9596 | 131.2565 | 0.033308 | 129.2364 | -0.0016848 | -1.7555 | -0.0096551 | 65.137 | 0.057152 | 117.6749 | 1.9145 | 120.4003 | 2.0012 | 113.6264 | 2.1361 | 144.2169 | 2.4285 | 0.10651 | 0.001477 | -0.099406 | -0.012756 | -0.37238 | -0.0033365 | 0.58807 | -0.022934 | 158.9319 | 2.8844 | 172.4781 | 2.8563 | 170.8524 | 2.6082 | 159.8004 | 2.613 | 129.2556 | 0.079417 | 131.0799 | 0.030196 | 0.53011 | -0.010947 | 63.5089 | 0.038503 | 117.9145 | 1.9718 | 115.1368 | 1.9427 | 117.4905 | 2.1216 | 138.1642 | 2.4297
283.8 | 92.8 | 120.6912 | -0.037987 | 120.3882 | 0.012969 | 0.58976 | -0.0064765 | 31.6492 | -0.0042575 | -2.0959 | 0.00012922 | 18.2094 | 5.3977 | 18.6088 | -0.0096664 | 3.0156 | 0.013306 | 132.2304 | 0.072267 | 132.0609 | 0.011301 | 0.38724 | -0.0031624 | 65.8188 | 0.010077 | -0.17492 | -0.00098319 | -0.079185 | -0.0051842 | 0.15942 | 0.071244 | 17.1145 | 0.27116 | -0.28309 | -0.0050157 | 0.095394 | 0.0067236 | -4.0735 | 0.024259 | 1.1725 | 0.0030389 | 34.7514 | 0.55342 | 31.2531 | 0.63894 | 30.3092 | 0.60831 | 37.7625 | 0.61963 | 128.8661 | 0.050198 | 128.5476 | -0.0038925 | 0.72491 | -0.010947 | 59.6131 | 0.038503 | 37.952 | 0.61475 | 38.9727 | 0.69766 | 42.9822 | 0.48044 | 27.327 | 0.42007
284 | 93 | 132.1839 | 0.077266 | 131.7836 | 0.0032298 | 0.29757 | 1.6859e-05 | 18.6954 | 0.011975 | 0.63122 | 0.0017522 | 7.301 | 0.024647 | 0.88265 | 0.0033197 | 3.6973 | 0.0019433 | 132.0357 | 0.034931 | 131.4765 | 0.0031849 | 0.19244 | 8.4239e-05 | 65.0397 | 0.032803 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | 0.0014439 | 3.2842 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.27297 | 0.0015107 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 129.353 | 0.043705 | 129.2293 | 0.0026002 | 0.23793 | -0.0028304 | 63.2167 | 0.028764 | 0.1621 | 0.0027749 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 3.3674 | 0.0012636
284.2 | 93.2 | 132.1839 | 0.078889 | 131.881 | 0.0032298 | 0.20015 | 1.6859e-05 | 13.0464 | 0.011975 | 0.33904 | 0.0017522 | 7.4958 | 0.058735 | 0.49305 | 0.0033197 | 3.4052 | 0.0019433 | 132.133 | 0.034931 | 131.4765 | 0.0031849 | 0.095061 | 8.4239e-05 | 65.137 | 0.032803 | 0.01988 | -0.00098319 | 0.11562 | -0.00031449 | 0.2568 | 0.0063136 | 2.992 | 7.2982e-05 | 0.30132 | -0.00014601 | 0.095394 | 0.00023025 | 0.017185 | 0.0015332 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 129.353 | 0.043705 | 129.3268 | 0.0026002 | 0.23793 | 0.00041557 | 63.2167 | 0.02714 | 0.25952 | 0.0011513 | 0.11153 | 0.0012748 | 0.22513 | 0.0048192 | 3.4648 | 0.0012636
284.4 | 93.4 | 132.1839 | 0.078889 | 131.5888 | 0.0016062 | 0.0053935 | 0.0016399 | 12.2672 | 0.0054818 | 0.33904 | -0.0047405 | 7.4958 | 0.060359 | 0.49305 | 0.0049427 | 3.4052 | -0.0013034 | 132.133 | 0.034931 | 131.4765 | 0.0015619 | 0.095061 | -0.0096551 | 65.137 | 0.032803 | -0.17492 | 0.0022635 | 0.018196 | -0.00031449 | 0.2568 | -0.0018028 | 3.2842 | 7.2982e-05 | 0.3987 | -0.00014601 | 0.095394 | 0.00023025 | 0.017185 | 0.0015332 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 0.070087 | 0.004404 | 129.2556 | 0.045329 | 129.3268 | 0.0026002 | 0.23793 | 0.0020392 | 63.3141 | 0.02714 | 0.1621 | -0.00047174 | 0.20895 | -0.00034817 | 0.22513 | 0.0048192 | 3.3674 | 0.0012636
284.6 | 93.6 | 132.1839 | 0.078889 | 131.6862 | 0.0048528 | 0.0053935 | -0.0016068 | 11.9751 | 0.016845 | 0.24166 | 0.00012922 | 7.2036 | 0.060359 | 0.39567 | 0.021175 | 2.8208 | 0.0051899 | 132.2304 | 0.034931 | 131.4765 | 0.0015619 | 0.19244 | 0.0017072 | 65.0397 | 0.031179 | 0.01988 | 0.0022635 | -0.079185 | 0.0045552 | 0.15942 | -0.00017979 | 3.3816 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.17559 | 0.0015107 | 0.086261 | 0.0026121 | 0.11626 | 0.0012074 | 0.070087 | 0.004404 | 129.2556 | 0.045329 | 129.4241 | 0.0042238 | 0.23793 | 0.00041557 | 63.1193 | 0.028764 | 0.3569 | 0.0027749 | 0.11153 | -0.00034817 | 0.32251 | 0.0048192 | 3.3674 | 0.0028873
284.8 | 93.8 | 132.2813 | 0.080513 | 131.881 | 0.0048528 | 0.10277 | 0.0016399 | 12.2672 | 0.0022351 | 0.33904 | 0.00012922 | 7.6906 | 0.060359 | 0.39567 | 0.0033197 | 3.3078 | 0.0019433 | 132.133 | 0.034931 | 131.574 | 0.0031849 | 0.19244 | 8.4239e-05 | 65.137 | 0.032803 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 3.5764 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.095394 | 0.00023025 | -0.080196 | 0.0015332 | 0.19851 | -0.00020779 | 0.27297 | -0.00011232 | 0.086261 | 0.0009884 | 0.21368 | 0.0012074 | 0.16751 | 0.004404 | 129.4504 | 0.043705 | 129.3268 | 0.0026002 | 0.23793 | 0.00041557 | 63.2167 | 0.02714 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748 | 0.22513 | -5.0495e-05 | 3.27 | -0.0003594
285 | 94 | 132.2813 | 0.080513 | 131.7836 | 0.0016062 | 0.10277 | -0.0032298 | 12.0725 | 0.00061214 | 0.33904 | 0.0033759 | 7.5932 | 0.058735 | 0.39567 | 0.0033197 | 3.2104 | 0.0019433 | 132.133 | 0.034931 | 131.4765 | 0.0031849 | 0.19244 | 0.0017072 | 65.0397 | 0.032803 | -0.0775 | 0.00064048 | 0.018196 | 0.0013085 | 0.15942 | -0.00017979 | 3.5764 | 0.0016967 | 0.30132 | -0.00014601 | 0.095394 | 0.00023025 | -0.080196 | 0.0015332 | 0.10109 | -0.00020779 | 0.17559 | 0.0031344 | -0.011119 | 0.0009884 | 0.018878 | 0.0028311 | 0.16751 | 0.004404 | 129.2556 | 0.045329 | 129.3268 | 0.0026002 | 0.23793 | 0.00041557 | 63.3141 | 0.02714 | 0.1621 | -0.00047174 | 0.20895 | 0.0012748 | 0.22513 | 0.0031962 | 3.3674 | 0.0012636
285.2 | 94.2 | 132.2813 | 0.080513 | 131.881 | 0.0032298 | 0.10277 | 1.6859e-05 | 11.9751 | 0.0022351 | 0.33904 | 0.0017522 | 7.6906 | 0.061982 | 0.29825 | 0.0016967 | 3.3078 | 0.0019433 | 132.133 | 0.034931 | 131.574 | 0.0031849 | 0.095061 | 8.4239e-05 | 65.137 | 0.032803 | -0.0775 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 3.479 | 7.2982e-05 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 0.070087 | 0.004404 | 129.353 | 0.043705 | 129.3268 | 0.0026002 | 0.23793 | 0.00041557 | 63.3141 | 0.02714 | 0.25952 | -0.00047174 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 3.3674 | 0.0012636
285.4 | 94.4 | 132.1839 | 0.080513 | 131.881 | 0.0032298 | 0.10277 | 1.6859e-05 | 11.8777 | 0.0022351 | 0.33904 | 0.0017522 | 7.6906 | 0.061982 | 0.29825 | 0.0016967 | 3.3078 | 0.0019433 | 132.2304 | 0.034931 | 131.4765 | 0.0031849 | 0.19244 | 8.4239e-05 | 65.2344 | 0.032803 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 3.5764 | 7.2982e-05 | 0.30132 | 0.001477 | 0.19277 | 0.00023025 | 0.017185 | 0.0015332 | 0.19851 | -0.00020779 | 0.17559 | 0.0015107 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 129.353 | 0.043705 | 129.3268 | 0.0026002 | 0.33531 | 0.00041557 | 63.3141 | 0.02714 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 3.4648 | 0.0012636
285.6 | 94.6 | 132.2813 | 0.080513 | 131.7836 | 0.0048528 | 0.10277 | 1.6859e-05 | 11.8777 | 0.0022351 | 0.24166 | 0.00012922 | 7.5932 | 0.060359 | 0.20087 | 0.0016967 | 3.3078 | 0.00032025 | 132.133 | 0.034931 | 131.4765 | 0.0031849 | 0.095061 | 8.4239e-05 | 65.0397 | 0.032803 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 3.5764 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | -0.080196 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.21368 | 0.0012074 | 0.16751 | 0.004404 | 129.353 | 0.043705 | 129.3268 | 0.0026002 | 0.23793 | 0.00041557 | 63.3141 | 0.02714 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817 | 0.32251 | 0.0031962 | 3.4648 | 0.0012636
285.8 | 94.8 | 132.2813 | 0.080513 | 131.7836 | 0.0032298 | 0.10277 | 1.6859e-05 | 11.7803 | 0.00061214 | 0.24166 | 0.00012922 | 7.5932 | 0.061982 | 0.20087 | 0.0016967 | 3.3078 | 0.0019433 | 132.133 | 0.034931 | 131.4765 | 0.0031849 | 0.19244 | 8.4239e-05 | 65.137 | 0.032803 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | 0.0014439 | 3.5764 | 0.0016967 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.21368 | 0.0012074 | 0.070087 | 0.004404 | 129.353 | 0.045329 | 129.3268 | 0.0026002 | 0.23793 | 0.00041557 | 63.3141 | 0.02714 | 0.1621 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 3.3674 | 0.0012636
286 | 95 | 132.1839 | 0.078889 | 131.7836 | 0.0032298 | 0.10277 | 1.6859e-05 | 11.7803 | 0.00061214 | 0.24166 | 0.00012922 | 7.5932 | 0.061982 | 0.20087 | 0.0016967 | 3.3078 | 0.0019433 | 132.133 | 0.036554 | 131.4765 | 0.0048085 | 0.19244 | 8.4239e-05 | 65.137 | 0.032803 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | 0.0014439 | 3.6738 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.17559 | 0.0015107 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.070087 | 0.004404 | 129.353 | 0.045329 | 129.2293 | 0.0042238 | 0.23793 | 0.00041557 | 63.3141 | 0.02714 | 0.1621 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 3.3674 | 0.0012636
286.2 | 95.2 | 132.2813 | 0.082136 | 131.7836 | 0.0032298 | 0.10277 | 1.6859e-05 | 11.7803 | 0.00061214 | 0.24166 | 0.00012922 | 7.5932 | 0.061982 | 0.10349 | 0.0016967 | 3.3078 | 0.00032025 | 132.2304 | 0.036554 | 131.574 | 0.0031849 | 0.19244 | 8.4239e-05 | 65.137 | 0.032803 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.2568 | 0.0014439 | 3.6738 | 7.2982e-05 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | -0.080196 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | 0.0015107 | 0.086261 | 0.0009884 | 0.21368 | 0.0012074 | 0.16751 | 0.004404 | 129.353 | 0.045329 | 129.3268 | 0.0026002 | 0.23793 | 0.00041557 | 63.3141 | 0.02714 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0048192 | 3.3674 | -0.0003594
286.4 | 95.4 | 132.1839 | 0.082136 | 131.7836 | 0.0048528 | 0.0053935 | 1.6859e-05 | 11.5855 | 0.0022351 | 0.24166 | 0.00012922 | 7.6906 | 0.061982 | 0.20087 | 0.0016967 | 3.4052 | 0.00032025 | 132.133 | 0.036554 | 131.4765 | 0.0031849 | 0.19244 | 8.4239e-05 | 65.137 | 0.032803 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | -0.00017979 | 3.5764 | 0.0016967 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 129.353 | 0.045329 | 129.2293 | 0.0026002 | 0.23793 | 0.00041557 | 63.2167 | 0.02714 | 0.1621 | 0.0011513 | 0.20895 | 0.0012748 | 0.22513 | 0.0031962 | 3.3674 | 0.0012636
286.6 | 95.6 | 132.2813 | 0.080513 | 131.881 | 0.0032298 | 0.0053935 | 1.6859e-05 | 11.5855 | 0.00061214 | 0.33904 | 0.00012922 | 7.6906 | 0.061982 | 0.20087 | 0.0016967 | 3.4052 | 0.0019433 | 132.133 | 0.036554 | 131.4765 | 0.0048085 | 0.19244 | 8.4239e-05 | 65.137 | 0.032803 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | -0.00017979 | 3.6738 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.070087 | 0.004404 | 129.353 | 0.045329 | 129.3268 | 0.0042238 | 0.23793 | 0.00041557 | 63.3141 | 0.02714 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 3.3674 | 0.0012636
286.8 | 95.8 | 132.2813 | 0.082136 | 131.7836 | 0.0032298 | 0.0053935 | 1.6859e-05 | 11.5855 | 0.00061214 | 0.24166 | 0.00012922 | 7.6906 | 0.061982 | 0.20087 | 0.0016967 | 3.4052 | 0.0019433 | 132.133 | 0.036554 | 131.4765 | 0.0048085 | 0.19244 | 0.0017072 | 65.0397 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 3.6738 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.10109 | 0.0014152 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 129.353 | 0.045329 | 129.3268 | 0.0026002 | 0.23793 | 0.00041557 | 63.2167 | 0.02714 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748 | 0.22513 | 0.0048192 | 3.3674 | 0.0012636
287 | 96 | 132.0865 | 0.078889 | 131.6862 | 0.0032298 | 0.29757 | 1.6859e-05 | 11.6829 | 0.00061214 | -0.14794 | 0.0017522 | 7.6906 | 0.068475 | 0.20087 | 7.2991e-05 | 3.4052 | -0.0013034 | 132.133 | 0.036554 | 131.574 | 0.0048085 | 0.19244 | 8.4239e-05 | 65.137 | 0.032803 | -0.0775 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | -0.00017979 | 3.7712 | 7.2982e-05 | 0.2039 | 0.0031007 | 0.095394 | 0.00023025 | 0.1146 | 0.0015332 | 0.19851 | 0.0014152 | -0.019206 | -0.0017353 | -0.011119 | 0.0009884 | 0.21368 | 0.0012074 | 0.16751 | 0.004404 | 129.353 | 0.045329 | 129.2293 | 0.0042238 | 0.23793 | 0.00041557 | 63.2167 | 0.02714 | 0.1621 | -0.0020947 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 3.4648 | -0.0003594
287.2 | 96.2 | 132.3787 | 0.082136 | 131.881 | 0.0048528 | 0.0053935 | 1.6859e-05 | 11.4881 | 0.00061214 | 0.24166 | 0.00012922 | 7.6906 | 0.061982 | 0.20087 | 0.0016967 | 3.5025 | 0.00032025 | 132.133 | 0.036554 | 131.574 | 0.0031849 | 0.19244 | 0.0017072 | 65.0397 | 0.032803 | -0.0775 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | -0.00017979 | 3.8686 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.29589 | 0.0014152 | 0.27297 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 129.4504 | 0.045329 | 129.3268 | 0.0042238 | 0.23793 | 0.00041557 | 63.2167 | 0.02714 | 0.1621 | 0.0011513 | 0.20895 | 0.0012748 | 0.22513 | 0.0031962 | 3.3674 | 0.0012636
287.4 | 96.4 | 132.2813 | 0.082136 | 131.7836 | 0.0032298 | 0.0053935 | 1.6859e-05 | 11.4881 | 0.00061214 | 0.14424 | 0.00012922 | 7.6906 | 0.063606 | 0.20087 | 0.0033197 | 3.5025 | 0.00032025 | 132.133 | 0.036554 | 131.574 | 0.0048085 | 0.19244 | 8.4239e-05 | 65.0397 | 0.032803 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.2568 | 0.0014439 | 3.8686 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.095394 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.006027 | 129.353 | 0.045329 | 129.4241 | 0.0042238 | 0.23793 | 0.00041557 | 63.3141 | 0.02714 | 0.1621 | -0.00047174 | 0.20895 | 0.0012748 | 0.22513 | 0.0031962 | 3.3674 | 0.0012636
287.6 | 96.6 | 132.3787 | 0.080513 | 131.881 | 0.0032298 | 0.0053935 | 0.0016399 | 11.4881 | 0.00061214 | 0.24166 | 0.00012922 | 7.6906 | 0.063606 | 0.10349 | 0.0016967 | 3.5025 | 0.00032025 | 132.2304 | 0.036554 | 131.4765 | 0.0048085 | 0.19244 | 8.4239e-05 | 65.137 | 0.032803 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | -0.00017979 | 3.9659 | -0.00155 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 129.353 | 0.045329 | 129.3268 | 0.0042238 | 0.23793 | 0.00041557 | 63.2167 | 0.025517 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0048192 | 3.4648 | 0.0012636
287.8 | 96.8 | 132.2813 | 0.080513 | 131.7836 | 0.0032298 | 0.0053935 | 1.6859e-05 | 11.3907 | 0.0022351 | 0.24166 | 0.00012922 | 7.788 | 0.065229 | 0.20087 | 0.0016967 | 3.6 | 0.0019433 | 132.133 | 0.036554 | 131.4765 | 0.0048085 | 0.19244 | 8.4239e-05 | 65.0397 | 0.032803 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.2568 | 0.0014439 | 4.0634 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.095394 | 0.00023025 | 0.017185 | 0.0015332 | 0.29589 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 129.2556 | 0.045329 | 129.3268 | 0.0042238 | 0.23793 | 0.00041557 | 63.2167 | 0.02714 | 0.25952 | -0.00047174 | 0.20895 | 0.0012748 | 0.22513 | 0.0031962 | 3.3674 | 0.0012636
288 | 97 | 132.2813 | 0.082136 | 131.7836 | 0.0048528 | 0.0053935 | 1.6859e-05 | 11.3907 | 0.0022351 | 0.24166 | 0.00012922 | 7.788 | 0.061982 | 0.20087 | 0.0033197 | 3.6 | 0.0019433 | 132.0357 | 0.036554 | 131.4765 | 0.0048085 | 0.19244 | 8.4239e-05 | 65.0397 | 0.032803 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 4.0634 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.095394 | 0.00023025 | -0.080196 | -8.9855e-05 | 0.29589 | 0.0014152 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.070087 | 0.004404 | 129.2556 | 0.045329 | 129.2293 | 0.0042238 | 0.23793 | 0.00041557 | 63.2167 | 0.02714 | 0.25952 | 0.0011513 | 0.11153 | -0.00034817 | 0.22513 | 0.0031962 | 3.3674 | 0.0012636
288.2 | 97.2 | 132.2813 | 0.080513 | 131.881 | 0.0048528 | 0.0053935 | 1.6859e-05 | 11.3907 | 0.00061214 | 0.24166 | 0.00012922 | 7.788 | 0.063606 | 0.20087 | 0.0016967 | 3.6973 | 0.0019433 | 132.2304 | 0.036554 | 131.574 | 0.0031849 | 0.19244 | 8.4239e-05 | 65.137 | 0.032803 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 4.2582 | 7.2982e-05 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.070087 | 0.004404 | 129.353 | 0.045329 | 129.3268 | 0.0042238 | 0.14051 | 0.00041557 | 63.2167 | 0.02714 | 0.1621 | 0.0011513 | 0.11153 | 0.0012748 | 0.22513 | 0.0048192 | 3.3674 | 0.0012636
288.4 | 97.4 | 132.2813 | 0.080513 | 131.881 | 0.0032298 | 0.0053935 | 1.6859e-05 | 11.2933 | 0.00061214 | 0.24166 | 0.00012922 | 7.788 | 0.061982 | 0.20087 | 0.0016967 | 3.6973 | 0.00032025 | 132.2304 | 0.036554 | 131.4765 | 0.0048085 | 0.19244 | 8.4239e-05 | 65.0397 | 0.032803 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 4.1607 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.095394 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.21368 | 0.0012074 | 0.16751 | 0.004404 | 129.353 | 0.045329 | 129.3268 | 0.0042238 | 0.23793 | 0.00041557 | 63.3141 | 0.02714 | 0.25952 | -0.00047174 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 3.3674 | 0.0012636
288.6 | 97.6 | 132.2813 | 0.082136 | 131.881 | 0.0032298 | 0.0053935 | 1.6859e-05 | 11.2933 | 0.00061214 | 0.14424 | 0.00012922 | 7.788 | 0.063606 | 0.20087 | 0.0016967 | 3.7948 | 0.00032025 | 132.2304 | 0.036554 | 131.574 | 0.0031849 | 0.19244 | 8.4239e-05 | 65.137 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 4.0634 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 129.4504 | 0.045329 | 129.4241 | 0.0058469 | 0.23793 | -0.0012074 | 63.3141 | 0.02714 | 0.25952 | -0.00047174 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 3.3674 | 0.0012636
288.8 | 97.8 | 132.2813 | 0.082136 | 131.881 | 0.0048528 | 0.0053935 | 1.6859e-05 | 11.2933 | 0.00061214 | 0.24166 | 0.00012922 | 7.788 | 0.061982 | 0.20087 | 0.0016967 | 3.7948 | 0.00032025 | 132.133 | 0.036554 | 131.574 | 0.0031849 | 0.19244 | 8.4239e-05 | 65.137 | 0.032803 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 4.0634 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | -0.080196 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.21368 | 0.0012074 | 0.16751 | 0.004404 | 129.353 | 0.045329 | 129.3268 | 0.0042238 | 0.23793 | 0.00041557 | 63.3141 | 0.02714 | 0.3569 | -0.00047174 | 0.20895 | -0.00034817 | 0.32251 | 0.0031962 | 3.3674 | 0.0012636
289 | 98 | 132.2813 | 0.082136 | 131.9783 | 0.0048528 | 0.0053935 | 1.6859e-05 | 11.2933 | 0.00061214 | 0.24166 | 0.00012922 | 7.788 | 0.063606 | 0.10349 | 0.0016967 | 3.7948 | 0.00032025 | 132.2304 | 0.036554 | 131.574 | 0.0031849 | 0.19244 | 8.4239e-05 | 65.137 | 0.034426 | 0.01988 | 0.00064048 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 4.0634 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | -0.0013928 | 0.017185 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.27297 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.006027 | 129.353 | 0.045329 | 129.4241 | 0.0042238 | 0.23793 | 0.00041557 | 63.2167 | 0.02714 | 0.1621 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0048192 | 3.3674 | 0.0012636
289.2 | 98.2 | 132.2813 | 0.082136 | 131.881 | 0.0032298 | 0.0053935 | 1.6859e-05 | 11.1959 | 0.00061214 | 0.14424 | 0.0017522 | 7.6906 | 0.061982 | 0.10349 | 0.0016967 | 3.8921 | 0.00032025 | 132.133 | 0.036554 | 131.574 | 0.0031849 | 0.19244 | 8.4239e-05 | 65.0397 | 0.032803 | 0.01988 | 0.0022635 | 0.11562 | -0.00031449 | 0.15942 | -0.00017979 | 3.9659 | 0.0016967 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.21368 | 0.0012074 | 0.16751 | 0.004404 | 129.4504 | 0.045329 | 129.3268 | 0.0042238 | 0.23793 | 0.00041557 | 63.2167 | 0.02714 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748 | 0.22513 | 0.0031962 | 3.3674 | 0.0012636
289.4 | 98.4 | 132.2813 | 0.082136 | 131.881 | 0.0048528 | 0.10277 | 1.6859e-05 | 11.2933 | 0.00061214 | 0.24166 | 0.00012922 | 7.788 | 0.061982 | 0.20087 | 0.0016967 | 3.8921 | 0.00032025 | 132.2304 | 0.036554 | 131.574 | 0.0048085 | 0.19244 | 8.4239e-05 | 65.137 | 0.032803 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 3.7712 | 7.2982e-05 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 129.353 | 0.045329 | 129.3268 | 0.0042238 | 0.14051 | 0.00041557 | 63.3141 | 0.02714 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 3.4648 | 0.0012636
289.6 | 98.6 | 132.2813 | 0.082136 | 131.881 | 0.0032298 | 0.0053935 | 1.6859e-05 | 11.2933 | 0.00061214 | 0.24166 | 0.00012922 | 7.788 | 0.063606 | 0.20087 | 0.0016967 | 3.9895 | 0.00032025 | 132.2304 | 0.036554 | 131.574 | 0.0031849 | 0.19244 | 8.4239e-05 | 65.0397 | 0.032803 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | -0.00017979 | 3.8686 | 7.2982e-05 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.21368 | 0.0012074 | 0.16751 | 0.004404 | 129.353 | 0.045329 | 129.4241 | 0.0042238 | 0.23793 | 0.00041557 | 63.2167 | 0.028764 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748 | 0.22513 | 0.0031962 | 3.4648 | 0.0012636
289.8 | 98.8 | 132.2813 | 0.080513 | 131.881 | 0.0032298 | 0.0053935 | 1.6859e-05 | 11.2933 | 0.00061214 | 0.14424 | 0.00012922 | 7.788 | 0.063606 | 0.20087 | 0.0016967 | 3.9895 | 0.00032025 | 132.2304 | 0.036554 | 131.574 | 0.0048085 | 0.19244 | 8.4239e-05 | 65.0397 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.2568 | -0.00017979 | 3.8686 | 7.2982e-05 | 0.2039 | 0.001477 | 0.19277 | 0.00023025 | 0.017185 | 0.0015332 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.21368 | 0.0012074 | 0.16751 | 0.004404 | 129.353 | 0.046952 | 129.3268 | 0.0042238 | 0.23793 | 0.00041557 | 63.3141 | 0.02714 | 0.1621 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 3.4648 | 0.0012636
290 | 99 | 132.2813 | 0.082136 | 131.881 | 0.0048528 | 0.0053935 | 1.6859e-05 | 11.2933 | 0.00061214 | 0.24166 | 0.00012922 | 7.6906 | 0.063606 | 0.20087 | 0.0016967 | 3.9895 | -0.0013034 | 132.133 | 0.036554 | 131.574 | 0.0048085 | 0.19244 | 8.4239e-05 | 65.0397 | 0.032803 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 3.8686 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 129.353 | 0.045329 | 129.4241 | 0.0042238 | 0.23793 | 0.00041557 | 63.3141 | 0.028764 | 0.1621 | -0.00047174 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 3.4648 | 0.0012636
290.2 | 99.2 | 132.2813 | 0.080513 | 131.881 | 0.0048528 | 0.0053935 | 1.6859e-05 | 11.1959 | 0.00061214 | 0.24166 | 0.00012922 | 7.788 | 0.063606 | 0.20087 | 0.0016967 | 4.0869 | 0.00032025 | 132.133 | 0.036554 | 131.4765 | 0.0048085 | 0.19244 | 8.4239e-05 | 64.9422 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 3.8686 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.21368 | 0.0012074 | 0.070087 | 0.004404 | 129.353 | 0.045329 | 129.3268 | 0.0042238 | 0.23793 | 0.00041557 | 63.2167 | 0.02714 | 0.25952 | -0.00047174 | 0.11153 | 0.0012748 | 0.22513 | 0.0031962 | 3.4648 | 0.0012636
290.4 | 99.4 | 132.2813 | 0.080513 | 131.881 | 0.0048528 | 0.0053935 | 1.6859e-05 | 11.1959 | 0.00061214 | 0.24166 | 0.00012922 | 7.788 | 0.063606 | 0.10349 | 0.0016967 | 4.0869 | 0.00032025 | 132.133 | 0.036554 | 131.4765 | 0.0048085 | 0.095061 | 8.4239e-05 | 65.0397 | 0.032803 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | -0.00017979 | 3.8686 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | 0.0015332 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | -0.011119 | -0.0006346 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 129.2556 | 0.045329 | 129.3268 | 0.0042238 | 0.14051 | 0.00041557 | 63.2167 | 0.02714 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 3.4648 | 0.0012636
290.6 | 99.6 | 132.2813 | 0.082136 | 131.881 | 0.0048528 | 0.10277 | 1.6859e-05 | 11.1959 | 0.00061214 | 0.24166 | 0.00012922 | 7.8854 | 0.063606 | 0.10349 | 0.0016967 | 4.1843 | 0.00032025 | 132.2304 | 0.036554 | 131.574 | 0.0048085 | 0.19244 | 8.4239e-05 | 65.0397 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 3.8686 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | 0.0015332 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | -0.0006346 | 0.11626 | 0.0012074 | 0.070087 | 0.004404 | 129.353 | 0.045329 | 129.3268 | 0.0042238 | 0.14051 | 0.00041557 | 63.2167 | 0.02714 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817 | 0.32251 | 0.0031962 | 3.4648 | 0.0012636
290.8 | 99.8 | 132.2813 | 0.082136 | 131.881 | 0.0048528 | 0.0053935 | 1.6859e-05 | 11.0985 | 0.00061214 | 0.24166 | 0.0017522 | 7.8854 | 0.061982 | 0.10349 | 0.0016967 | 4.2817 | 0.0019433 | 132.133 | 0.036554 | 131.574 | 0.0048085 | 0.19244 | 0.0017072 | 65.0397 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | 0.0014439 | 3.8686 | 0.0016967 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.21368 | 0.0012074 | 0.16751 | 0.004404 | 129.353 | 0.046952 | 129.3268 | 0.0042238 | 0.23793 | 0.00041557 | 63.2167 | 0.02714 | 0.25952 | -0.00047174 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 3.4648 | 0.0012636
291 | 100 | 132.2813 | 0.082136 | 131.881 | 0.0048528 | 0.0053935 | 1.6859e-05 | 11.1959 | 0.00061214 | 0.24166 | 0.00012922 | 7.788 | 0.063606 | 0.20087 | 0.0016967 | 4.3791 | 0.00032025 | 132.2304 | 0.036554 | 131.574 | 0.0048085 | 0.19244 | 8.4239e-05 | 65.0397 | 0.034426 | -0.0775 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 3.8686 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 0.070087 | 0.004404 | 129.353 | 0.045329 | 129.3268 | 0.0042238 | 0.23793 | 0.00041557 | 63.2167 | 0.028764 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748 | 0.22513 | 0.0031962 | 3.4648 | 0.0012636
291.2 | 100.2 | 132.2813 | 0.082136 | 131.881 | 0.0048528 | 0.0053935 | 1.6859e-05 | 11.1959 | 0.00061214 | 0.24166 | 0.00012922 | 7.788 | 0.063606 | 0.20087 | 0.0016967 | 4.4765 | 0.00032025 | 132.133 | 0.036554 | 131.574 | 0.0048085 | 0.19244 | 8.4239e-05 | 65.0397 | 0.032803 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.2568 | -0.00017979 | 3.8686 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.0018533 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 129.353 | 0.045329 | 129.3268 | 0.0042238 | 0.23793 | 0.00041557 | 63.2167 | 0.02714 | 0.25952 | -0.00047174 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 3.4648 | 0.0012636
291.4 | 100.4 | 132.3787 | 0.082136 | 131.881 | 0.0048528 | 0.0053935 | 1.6859e-05 | 11.0985 | 0.00061214 | 0.24166 | 0.00012922 | 7.8854 | 0.063606 | 0.20087 | 0.0016967 | 4.4765 | 0.00032025 | 132.133 | 0.038178 | 131.4765 | 0.0031849 | 0.19244 | 8.4239e-05 | 65.0397 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.2568 | 0.0014439 | 3.8686 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | -0.080196 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | 0.086261 | -0.0006346 | 0.21368 | 0.0012074 | 0.070087 | 0.004404 | 129.353 | 0.045329 | 129.3268 | 0.0042238 | 0.23793 | 0.00041557 | 63.3141 | 0.02714 | 0.1621 | -0.00047174 | 0.20895 | -0.00034817 | 0.22513 | 0.0048192 | 3.4648 | 0.0012636
291.6 | 100.6 | 132.2813 | 0.082136 | 131.7836 | 0.0032298 | 0.0053935 | 0.0016399 | 11.0011 | 0.00061214 | 0.24166 | 0.00012922 | 7.8854 | 0.063606 | 0.10349 | 0.0016967 | 4.6713 | 0.00032025 | 132.133 | 0.038178 | 131.4765 | 0.0048085 | 0.19244 | 8.4239e-05 | 65.0397 | 0.032803 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.2568 | -0.00017979 | 4.0634 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 0.070087 | 0.004404 | 129.353 | 0.045329 | 129.2293 | 0.0042238 | 0.23793 | 0.00041557 | 63.2167 | 0.02714 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 3.4648 | -0.0003594
291.8 | 100.8 | 132.2813 | 0.082136 | 131.881 | 0.0032298 | 0.10277 | 1.6859e-05 | 11.0011 | 0.00061214 | 0.24166 | 0.00012922 | 7.8854 | 0.063606 | 0.20087 | 0.0016967 | 4.7687 | 0.00032025 | 132.133 | 0.036554 | 131.574 | 0.0031849 | 0.095061 | 8.4239e-05 | 64.9422 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.2568 | 0.0014439 | 4.0634 | 7.2982e-05 | 0.2039 | 0.001477 | 0.19277 | 0.00023025 | -0.080196 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.17559 | 0.0015107 | -0.011119 | 0.0009884 | 0.21368 | 0.0012074 | 0.070087 | 0.004404 | 129.353 | 0.045329 | 129.2293 | 0.0042238 | 0.23793 | 0.00041557 | 63.2167 | 0.02714 | 0.25952 | -0.00047174 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 3.4648 | 0.0012636
292 | 101 | 132.1839 | 0.082136 | 131.7836 | 0.0032298 | 0.0053935 | 1.6859e-05 | 11.0011 | 0.00061214 | 0.24166 | 0.00012922 | 7.8854 | 0.063606 | 0.20087 | 0.0016967 | 4.8661 | 0.00032025 | 132.133 | 0.036554 | 131.4765 | 0.0048085 | 0.19244 | 8.4239e-05 | 64.9422 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | 0.0014439 | 3.9659 | 7.2982e-05 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | 0.0015332 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 129.2556 | 0.045329 | 129.3268 | 0.0042238 | 0.23793 | 0.00041557 | 63.2167 | 0.02714 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748 | 0.22513 | 0.0048192 | 3.5622 | 0.0012636
292.2 | 101.2 | 132.2813 | 0.082136 | 131.881 | 0.0032298 | 0.0053935 | 1.6859e-05 | 11.0011 | 0.00061214 | 0.24166 | 0.00012922 | 7.8854 | 0.063606 | 0.10349 | 0.0016967 | 4.9635 | 0.0019433 | 132.133 | 0.036554 | 131.4765 | 0.0048085 | 0.19244 | 8.4239e-05 | 64.9422 | 0.034426 | 0.01988 | 0.0022635 | 0.11562 | -0.00031449 | 0.15942 | -0.00017979 | 4.1607 | 7.2982e-05 | 0.2039 | 0.001477 | 0.19277 | 0.00023025 | 0.017185 | 0.0015332 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 129.353 | 0.045329 | 129.3268 | 0.0058469 | 0.23793 | 0.00041557 | 63.2167 | 0.02714 | 0.25952 | -0.00047174 | 0.11153 | 0.0012748 | 0.22513 | 0.0031962 | 3.5622 | 0.0012636
292.4 | 101.4 | 132.2813 | 0.082136 | 131.9783 | 0.0048528 | 0.0053935 | 1.6859e-05 | 11.0011 | 0.00061214 | 0.33904 | 0.00012922 | 7.8854 | 0.063606 | 0.10349 | 0.0016967 | 5.1583 | 0.00032025 | 132.2304 | 0.036554 | 131.574 | 0.0031849 | 0.095061 | 8.4239e-05 | 64.9422 | 0.032803 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 4.1607 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.095394 | 0.00023025 | 0.017185 | 0.0015332 | 0.29589 | -0.00020779 | 0.27297 | 0.0015107 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.070087 | 0.004404 | 129.353 | 0.045329 | 129.3268 | 0.0042238 | 0.23793 | 0.00041557 | 63.2167 | 0.02714 | 0.25952 | 0.0011513 | 0.11153 | -0.00034817 | 0.22513 | 0.0048192 | 3.5622 | 0.0012636
292.6 | 101.6 | 132.2813 | 0.082136 | 131.881 | 0.0048528 | -0.092027 | 1.6859e-05 | 11.0011 | 0.00061214 | 0.24166 | 0.00012922 | 7.8854 | 0.063606 | 0.10349 | 0.0016967 | 5.2557 | 0.0019433 | 132.133 | 0.036554 | 131.4765 | 0.0048085 | 0.19244 | 8.4239e-05 | 64.9422 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 4.3555 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | 0.0015332 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.070087 | 0.004404 | 129.353 | 0.045329 | 129.2293 | 0.0042238 | 0.23793 | 0.00041557 | 63.2167 | 0.028764 | 0.1621 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 3.5622 | 0.0012636
292.8 | 101.8 | 132.2813 | 0.082136 | 131.881 | 0.0048528 | 0.0053935 | 1.6859e-05 | 11.0011 | 0.00061214 | 0.24166 | 0.0017522 | 7.8854 | 0.063606 | 0.20087 | 0.0016967 | 5.3531 | 0.00032025 | 132.133 | 0.036554 | 131.4765 | 0.0048085 | 0.095061 | 8.4239e-05 | 64.9422 | 0.032803 | 0.01988 | 0.0022635 | 0.11562 | 0.0013085 | 0.15942 | 0.0014439 | 4.3555 | 7.2982e-05 | 0.2039 | 0.001477 | 0.19277 | 0.00023025 | 0.017185 | 0.0015332 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.21368 | 0.0012074 | 0.070087 | 0.004404 | 129.353 | 0.045329 | 129.3268 | 0.0058469 | 0.23793 | 0.00041557 | 63.2167 | 0.02714 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748 | 0.22513 | 0.0048192 | 3.5622 | 0.0012636
293 | 102 | 132.2813 | 0.082136 | 131.9783 | 0.0032298 | 0.0053935 | 1.6859e-05 | 10.9037 | 0.00061214 | 0.24166 | 0.00012922 | 7.8854 | 0.063606 | 0.20087 | 0.0016967 | 5.5479 | 0.0019433 | 132.133 | 0.036554 | 131.574 | 0.0048085 | 0.095061 | 8.4239e-05 | 64.9422 | 0.032803 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 4.5503 | 7.2982e-05 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | 0.0015332 | 0.29589 | 0.0014152 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 129.353 | 0.045329 | 129.3268 | 0.0058469 | 0.23793 | 0.00041557 | 63.2167 | 0.02714 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 3.6596 | 0.0012636
293.2 | 102.2 | 132.2813 | 0.083759 | 131.881 | 0.0048528 | 0.0053935 | 1.6859e-05 | 10.9037 | 0.00061214 | 0.14424 | 0.0017522 | 7.8854 | 0.063606 | 0.20087 | 0.0016967 | 5.6453 | 0.00032025 | 132.133 | 0.036554 | 131.574 | 0.0048085 | 0.19244 | 8.4239e-05 | 64.9422 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | 0.0014439 | 4.7451 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | 0.0015332 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.21368 | 0.0012074 | 0.070087 | 0.004404 | 129.353 | 0.045329 | 129.3268 | 0.0042238 | 0.23793 | 0.00041557 | 63.2167 | 0.028764 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817 | 0.32251 | 0.0031962 | 3.5622 | 0.0012636
293.4 | 102.4 | 132.2813 | 0.082136 | 131.881 | 0.0048528 | 0.0053935 | 1.6859e-05 | 10.9037 | 0.00061214 | 0.24166 | 0.00012922 | 7.8854 | 0.063606 | 0.10349 | 0.0016967 | 5.7427 | 0.00032025 | 132.133 | 0.036554 | 131.574 | 0.0031849 | 0.19244 | 8.4239e-05 | 64.9422 | 0.032803 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | -0.00017979 | 4.8425 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.17559 | 0.0015107 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 0.070087 | 0.004404 | 129.353 | 0.045329 | 129.3268 | 0.0042238 | 0.23793 | 0.00041557 | 63.2167 | 0.028764 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 3.757 | 0.0012636
293.6 | 102.6 | 132.3787 | 0.082136 | 131.881 | 0.0048528 | 0.0053935 | 1.6859e-05 | 11.0011 | 0.00061214 | 0.24166 | 0.00012922 | 7.8854 | 0.063606 | 0.10349 | 0.0016967 | 6.0349 | 0.00032025 | 132.133 | 0.036554 | 131.574 | 0.0048085 | 0.19244 | 8.4239e-05 | 64.9422 | 0.032803 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 5.0373 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.27297 | 0.0015107 | -0.011119 | 0.0009884 | 0.21368 | 0.0012074 | 0.070087 | 0.004404 | 129.2556 | 0.045329 | 129.3268 | 0.0058469 | 0.14051 | 0.00041557 | 63.2167 | 0.02714 | 0.25952 | 0.0011513 | 0.11153 | -0.00034817 | 0.22513 | 0.0031962 | 3.757 | 0.0012636
293.8 | 102.8 | 132.3787 | 0.082136 | 131.881 | 0.0048528 | 0.0053935 | 1.6859e-05 | 10.9037 | 0.00061214 | 0.24166 | 0.00012922 | 7.8854 | 0.065229 | 0.20087 | 0.0033197 | 6.1323 | 0.0019433 | 132.133 | 0.036554 | 131.574 | 0.0031849 | 0.19244 | 8.4239e-05 | 64.9422 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.2568 | 0.0014439 | 5.1347 | -0.00155 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | 0.0015332 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | 0.086261 | -0.0006346 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 129.353 | 0.046952 | 129.3268 | 0.0042238 | 0.23793 | 0.00041557 | 63.2167 | 0.02714 | 0.25952 | -0.00047174 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 3.8544 | 0.0012636
294 | 103 | 132.2813 | 0.082136 | 131.9783 | 0.0032298 | 0.0053935 | 1.6859e-05 | 10.8063 | 0.00061214 | 0.24166 | 0.00012922 | 7.8854 | 0.063606 | 0.10349 | 0.0016967 | 6.2297 | 0.00032025 | 132.133 | 0.036554 | 131.4765 | 0.0031849 | 0.19244 | 8.4239e-05 | 64.8449 | 0.032803 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | -0.00017979 | 5.0373 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | -0.0013928 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.21368 | 0.0012074 | 0.070087 | 0.004404 | 129.2556 | 0.046952 | 129.2293 | 0.0058469 | 0.23793 | -0.0012074 | 63.2167 | 0.02714 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 3.8544 | 0.0012636
294.2 | 103.2 | 132.2813 | 0.083759 | 131.881 | 0.0048528 | 0.0053935 | 1.6859e-05 | 10.9037 | 0.00061214 | 0.14424 | 0.00012922 | 7.9828 | 0.063606 | 0.20087 | 0.0016967 | 6.3271 | 0.00032025 | 132.133 | 0.036554 | 131.4765 | 0.0048085 | 0.19244 | 8.4239e-05 | 64.8449 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 4.8425 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | 0.0015332 | 0.19851 | 0.0014152 | 0.17559 | 0.0015107 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.070087 | 0.004404 | 129.353 | 0.046952 | 129.2293 | 0.0042238 | 0.23793 | 0.00041557 | 63.2167 | 0.02714 | 0.25952 | -0.00047174 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 3.8544 | 0.0012636
294.4 | 103.4 | 132.3787 | 0.083759 | 131.881 | 0.0048528 | 0.0053935 | 1.6859e-05 | 10.9037 | 0.00061214 | 0.24166 | 0.00012922 | 7.9828 | 0.063606 | 0.20087 | 0.0016967 | 6.3271 | 0.00032025 | 132.2304 | 0.036554 | 131.574 | 0.0031849 | 0.19244 | 8.4239e-05 | 64.8449 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 4.9399 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.095394 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | 0.0015107 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 129.353 | 0.045329 | 129.3268 | 0.0058469 | 0.23793 | 0.00041557 | 63.2167 | 0.02714 | 0.25952 | -0.00047174 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 4.0492 | -0.0003594
294.6 | 103.6 | 132.2813 | 0.082136 | 131.7836 | 0.0048528 | 0.0053935 | 1.6859e-05 | 11.0011 | 0.00061214 | 0.24166 | 0.00012922 | 7.8854 | 0.063606 | 0.10349 | 0.0016967 | 6.3271 | 0.00032025 | 132.133 | 0.036554 | 131.574 | 0.0031849 | 0.19244 | 8.4239e-05 | 64.8449 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 5.1347 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 0.070087 | 0.004404 | 129.353 | 0.046952 | 129.3268 | 0.0058469 | 0.23793 | 0.00041557 | 63.2167 | 0.02714 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 4.1466 | 0.0012636
294.8 | 103.8 | 132.2813 | 0.083759 | 131.881 | 0.0048528 | 0.0053935 | 1.6859e-05 | 11.0011 | 0.00061214 | 0.24166 | 0.0017522 | 7.8854 | 0.063606 | 0.20087 | 0.0016967 | 6.4245 | 0.0019433 | 132.2304 | 0.036554 | 131.574 | 0.0048085 | 0.095061 | 8.4239e-05 | 64.9422 | 0.032803 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | 0.0014439 | 5.2321 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.095394 | 0.00023025 | 0.017185 | 0.0015332 | 0.19851 | 0.0014152 | 0.17559 | 0.0015107 | -0.011119 | -0.0006346 | 0.21368 | 0.0012074 | 0.070087 | 0.004404 | 129.2556 | 0.046952 | 129.3268 | 0.0058469 | 0.23793 | 0.00041557 | 63.1193 | 0.028764 | 0.1621 | -0.00047174 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 4.1466 | 0.0012636
295 | 104 | 132.1839 | 0.083759 | 131.881 | 0.0048528 | 0.10277 | 1.6859e-05 | 10.8063 | 0.00061214 | 0.24166 | 0.00012922 | 7.8854 | 0.065229 | 0.10349 | 0.0016967 | 6.4245 | 0.00032025 | 132.2304 | 0.036554 | 131.4765 | 0.0048085 | 0.19244 | 8.4239e-05 | 64.8449 | 0.032803 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | -0.00017979 | 5.5243 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | 0.0015332 | 0.19851 | -0.00020779 | 0.17559 | 0.0015107 | -0.011119 | 0.0009884 | 0.21368 | 0.0012074 | 0.16751 | 0.004404 | 129.353 | 0.046952 | 129.3268 | 0.0058469 | 0.23793 | 0.00041557 | 63.2167 | 0.02714 | 0.1621 | 0.0011513 | 0.11153 | -0.00034817 | 0.22513 | 0.0031962 | 4.244 | 0.0012636
295.2 | 104.2 | 132.2813 | 0.083759 | 131.881 | 0.0048528 | 0.0053935 | 1.6859e-05 | 10.8063 | 0.00061214 | 0.24166 | 0.00012922 | 7.9828 | 0.063606 | 0.20087 | 0.0016967 | 6.5219 | 0.0019433 | 132.2304 | 0.038178 | 131.574 | 0.0048085 | 0.19244 | 8.4239e-05 | 64.8449 | 0.032803 | 0.01988 | 0.0022635 | 0.11562 | 0.0013085 | 0.15942 | 0.0014439 | 5.6217 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | 0.0015332 | 0.19851 | 0.0014152 | 0.27297 | 0.0015107 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 129.353 | 0.046952 | 129.3268 | 0.0058469 | 0.23793 | 0.00041557 | 63.2167 | 0.02714 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 4.3414 | 0.0012636
295.4 | 104.4 | 132.2813 | 0.083759 | 131.881 | 0.0048528 | 0.0053935 | 1.6859e-05 | 10.8063 | 0.00061214 | 0.24166 | 0.00012922 | 7.9828 | 0.063606 | 0.10349 | 0.0016967 | 6.5219 | 0.0019433 | 132.2304 | 0.036554 | 131.574 | 0.0048085 | 0.19244 | 8.4239e-05 | 64.8449 | 0.032803 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 5.7191 | 7.2982e-05 | 0.2039 | 0.001477 | 0.095394 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | -0.0006346 | 0.21368 | 0.0012074 | 0.16751 | 0.004404 | 129.353 | 0.046952 | 129.3268 | 0.0058469 | 0.23793 | 0.00041557 | 63.1193 | 0.02714 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748 | 0.22513 | 0.0031962 | 4.3414 | 0.0012636
295.6 | 104.6 | 132.2813 | 0.082136 | 131.7836 | 0.0048528 | 0.0053935 | 1.6859e-05 | 10.7089 | 0.00061214 | 0.24166 | 0.00012922 | 7.8854 | 0.065229 | 0.10349 | 0.0016967 | 6.5219 | 0.00032025 | 132.2304 | 0.036554 | 131.574 | 0.0048085 | 0.19244 | 8.4239e-05 | 64.8449 | 0.032803 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | 0.0014439 | 5.7191 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 129.353 | 0.046952 | 129.3268 | 0.0058469 | 0.23793 | 0.00041557 | 63.1193 | 0.028764 | 0.1621 | 0.0011513 | 0.20895 | -0.00034817 | 0.32251 | 0.0031962 | 4.244 | 0.0012636
295.8 | 104.8 | 132.2813 | 0.083759 | 131.881 | 0.0048528 | 0.10277 | 1.6859e-05 | 10.8063 | 0.00061214 | 0.24166 | 0.00012922 | 7.8854 | 0.063606 | 0.20087 | 7.2991e-05 | 6.7167 | 0.00032025 | 132.2304 | 0.038178 | 131.4765 | 0.0048085 | 0.095061 | 8.4239e-05 | 64.7474 | 0.032803 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 5.9139 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | 0.0015107 | -0.011119 | 0.0009884 | 0.21368 | 0.0012074 | 0.16751 | 0.004404 | 129.353 | 0.046952 | 129.3268 | 0.0042238 | 0.23793 | 0.00041557 | 63.2167 | 0.02714 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 4.3414 | 0.0012636
296 | 105 | 132.1839 | 0.083759 | 131.7836 | 0.0048528 | 0.0053935 | 1.6859e-05 | 10.8063 | 0.00061214 | 0.24166 | 0.00012922 | 7.8854 | 0.065229 | 0.10349 | 0.0016967 | 6.7167 | 0.0019433 | 132.133 | 0.038178 | 131.4765 | 0.0048085 | 0.095061 | 8.4239e-05 | 64.7474 | 0.032803 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.2568 | 0.0014439 | 5.9139 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | 0.0015332 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 129.2556 | 0.046952 | 129.2293 | 0.0058469 | 0.23793 | 0.00041557 | 63.1193 | 0.02714 | 0.1621 | 0.0011513 | 0.20895 | 0.0012748 | 0.22513 | 0.0048192 | 4.3414 | 0.0012636
296.2 | 105.2 | 132.2813 | 0.083759 | 131.881 | 0.0048528 | 0.0053935 | 1.6859e-05 | 10.9037 | 0.00061214 | 0.14424 | 0.00012922 | 7.8854 | 0.063606 | 0.10349 | 0.0016967 | 6.7167 | 0.00032025 | 132.133 | 0.034931 | 131.574 | 0.0048085 | 0.19244 | 8.4239e-05 | 64.7474 | 0.032803 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | -0.00017979 | 6.0113 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.21368 | 0.0012074 | 0.070087 | 0.004404 | 129.353 | 0.046952 | 129.3268 | 0.0042238 | 0.23793 | 0.00041557 | 63.1193 | 0.02714 | 0.25952 | 0.0011513 | 0.11153 | -0.00034817 | 0.32251 | 0.0031962 | 4.3414 | 0.0012636
296.4 | 105.4 | 132.2813 | 0.083759 | 131.881 | 0.0048528 | 0.10277 | 1.6859e-05 | 10.8063 | 0.00061214 | 0.24166 | 0.00012922 | 7.8854 | 0.065229 | 0.20087 | 0.0016967 | 6.814 | 0.00032025 | 132.133 | 0.036554 | 131.574 | 0.0048085 | 0.095061 | 8.4239e-05 | 64.7474 | 0.032803 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | -0.00017979 | 6.0113 | 0.0016967 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 129.353 | 0.046952 | 129.3268 | 0.0058469 | 0.23793 | 0.00041557 | 63.1193 | 0.02714 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 4.3414 | -0.0003594
296.6 | 105.6 | 132.2813 | 0.082136 | 131.881 | 0.0048528 | 0.0053935 | 1.6859e-05 | 10.9037 | 0.00061214 | 0.24166 | 0.00012922 | 7.9828 | 0.063606 | 0.20087 | 0.0016967 | 7.1062 | 0.00032025 | 132.133 | 0.038178 | 131.4765 | 0.0048085 | 0.19244 | 8.4239e-05 | 64.7474 | 0.032803 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | 0.0014439 | 6.1087 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | 0.0015332 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.21368 | 0.0012074 | 0.070087 | 0.004404 | 129.353 | 0.045329 | 129.3268 | 0.0042238 | 0.14051 | 0.00041557 | 63.1193 | 0.02714 | 0.1621 | 0.0011513 | 0.20895 | 0.0012748 | 0.22513 | 0.0031962 | 4.3414 | -0.0003594
296.8 | 105.8 | 132.2813 | 0.082136 | 131.881 | 0.0048528 | 0.0053935 | 0.0016399 | 10.9037 | 0.00061214 | 0.24166 | 0.00012922 | 7.9828 | 0.063606 | 0.20087 | 0.0016967 | 7.301 | 0.0019433 | 132.2304 | 0.038178 | 131.574 | 0.0048085 | 0.19244 | 8.4239e-05 | 64.7474 | 0.032803 | 0.01988 | 0.0022635 | 0.11562 | -0.00031449 | 0.15942 | -0.00017979 | 6.1087 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.095394 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | 0.0015107 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.070087 | 0.004404 | 129.353 | 0.046952 | 129.3268 | 0.0058469 | 0.14051 | 0.00041557 | 63.2167 | 0.028764 | 0.1621 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 4.4388 | 0.0012636
297 | 106 | 132.2813 | 0.082136 | 131.881 | 0.0048528 | 0.0053935 | 1.6859e-05 | 11.0011 | 0.00061214 | 0.24166 | 0.00012922 | 7.9828 | 0.065229 | 0.10349 | 7.2991e-05 | 7.3984 | 0.00032025 | 132.133 | 0.038178 | 131.4765 | 0.0048085 | 0.19244 | 0.0017072 | 64.7474 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | -0.00017979 | 6.2061 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | -0.080196 | 0.0015332 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 129.353 | 0.046952 | 129.3268 | 0.0042238 | 0.23793 | 0.00041557 | 63.1193 | 0.02714 | 0.25952 | 0.0011513 | 0.11153 | -0.00034817 | 0.22513 | 0.0031962 | 4.4388 | 0.0012636
297.2 | 106.2 | 132.2813 | 0.082136 | 131.881 | 0.0048528 | 0.0053935 | 1.6859e-05 | 10.9037 | 0.00061214 | 0.24166 | 0.00012922 | 7.9828 | 0.063606 | 0.10349 | 0.0016967 | 7.6906 | 0.00032025 | 132.133 | 0.038178 | 131.574 | 0.0048085 | 0.19244 | 8.4239e-05 | 64.7474 | 0.032803 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.2568 | 0.0014439 | 6.2061 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.21368 | 0.0012074 | 0.070087 | 0.004404 | 129.353 | 0.046952 | 129.3268 | 0.0058469 | 0.23793 | -0.0012074 | 63.1193 | 0.028764 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 4.4388 | 0.0012636
297.4 | 106.4 | 132.2813 | 0.083759 | 131.7836 | 0.0048528 | 0.0053935 | 1.6859e-05 | 11.0011 | 0.00061214 | 0.24166 | 0.00012922 | 8.0802 | 0.065229 | 0.10349 | 0.0016967 | 7.8854 | 0.0019433 | 132.133 | 0.038178 | 131.4765 | 0.0048085 | 0.19244 | 8.4239e-05 | 64.7474 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | 0.0014439 | 6.3035 | 7.2982e-05 | 0.30132 | -0.00014601 | 0.095394 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.27297 | -0.00011232 | -0.011119 | 0.0009884 | 0.21368 | 0.0012074 | 0.070087 | 0.0027804 | 129.353 | 0.046952 | 129.3268 | 0.0058469 | 0.23793 | 0.00041557 | 63.1193 | 0.028764 | 0.25952 | -0.00047174 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 4.6336 | 0.0012636
297.6 | 106.6 | 132.3787 | 0.082136 | 131.881 | 0.0048528 | 0.0053935 | 1.6859e-05 | 11.0011 | 0.00061214 | 0.24166 | 0.00012922 | 8.0802 | 0.065229 | 0.20087 | 0.0016967 | 7.9828 | 0.00032025 | 132.133 | 0.038178 | 131.4765 | 0.0064315 | 0.095061 | 8.4239e-05 | 64.6501 | 0.032803 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.2568 | 0.0014439 | 6.4009 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | -0.080196 | 0.0015332 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | 0.086261 | -0.0006346 | 0.21368 | 0.0012074 | 0.16751 | 0.004404 | 129.2556 | 0.046952 | 129.3268 | 0.0058469 | 0.23793 | 0.00041557 | 63.2167 | 0.02714 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 4.731 | 0.0012636
297.8 | 106.8 | 132.2813 | 0.083759 | 131.881 | 0.0048528 | 0.0053935 | 1.6859e-05 | 10.9037 | 0.00061214 | 0.24166 | 0.00012922 | 7.9828 | 0.065229 | 0.10349 | 0.0016967 | 8.1776 | 0.00032025 | 132.133 | 0.038178 | 131.574 | 0.0048085 | 0.095061 | 8.4239e-05 | 64.6501 | 0.032803 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.2568 | 0.0014439 | 6.4983 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | -0.080196 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.21368 | 0.0012074 | 0.070087 | 0.004404 | 129.353 | 0.046952 | 129.3268 | 0.0058469 | 0.23793 | 0.00041557 | 63.1193 | 0.02714 | 0.25952 | -0.00047174 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 4.9257 | 0.0012636
298 | 107 | 132.2813 | 0.082136 | 131.881 | 0.0048528 | 0.0053935 | 1.6859e-05 | 11.0011 | 0.00061214 | 0.24166 | 0.00012922 | 7.9828 | 0.065229 | 0.10349 | 0.0016967 | 8.3724 | 0.0019433 | 132.133 | 0.038178 | 131.574 | 0.0048085 | 0.19244 | 8.4239e-05 | 64.6501 | 0.032803 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 6.6931 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 129.353 | 0.045329 | 129.3268 | 0.0058469 | 0.23793 | 0.00041557 | 63.2167 | 0.02714 | 0.1621 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 5.218 | 0.0012636
298.2 | 107.2 | 132.3787 | 0.082136 | 131.881 | 0.0048528 | 0.0053935 | 1.6859e-05 | 11.0011 | -0.0010109 | 0.24166 | 0.00012922 | 8.0802 | 0.065229 | 0.20087 | 0.0016967 | 8.5672 | 0.00032025 | 132.2304 | 0.038178 | 131.6713 | 0.0048085 | 0.19244 | 8.4239e-05 | 64.7474 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | 0.0014439 | 6.8879 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | 0.0015332 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.21368 | 0.0012074 | 0.070087 | 0.004404 | 129.4504 | 0.045329 | 129.3268 | 0.0058469 | 0.23793 | 0.00041557 | 63.2167 | 0.02714 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0048192 | 5.8023 | 0.0012636
298.4 | 107.4 | 132.3787 | 0.083759 | 131.881 | 0.0032298 | 0.10277 | 1.6859e-05 | 11.0011 | 0.00061214 | 0.24166 | 0.00012922 | 8.0802 | 0.065229 | 0.10349 | 0.0016967 | 8.6646 | 0.00032025 | 132.2304 | 0.038178 | 131.574 | 0.0064315 | 0.19244 | 8.4239e-05 | 64.6501 | 0.032803 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 6.8879 | 7.2982e-05 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | 0.0015332 | 0.29589 | 0.0014152 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 0.070087 | 0.004404 | 129.2556 | 0.046952 | 129.3268 | 0.0058469 | 0.23793 | 0.00041557 | 63.1193 | 0.02714 | 0.25952 | -0.00047174 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 6.1919 | 0.0012636
298.6 | 107.6 | 132.3787 | 0.083759 | 131.881 | 0.0048528 | 0.0053935 | 1.6859e-05 | 11.0011 | 0.00061214 | 0.24166 | 0.00012922 | 7.9828 | 0.065229 | 0.20087 | 0.0016967 | 8.5672 | 0.00032025 | 132.2304 | 0.038178 | 131.574 | 0.0048085 | 0.19244 | 8.4239e-05 | 64.6501 | 0.032803 | 0.01988 | 0.0022635 | 0.11562 | -0.00031449 | 0.15942 | 0.0014439 | 6.9852 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.17559 | 0.0015107 | 0.086261 | 0.0009884 | 0.21368 | 0.0012074 | 0.070087 | 0.004404 | 129.353 | 0.046952 | 129.3268 | 0.0042238 | 0.23793 | 0.00041557 | 63.1193 | 0.02714 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 6.3867 | 0.0012636
298.8 | 107.8 | 132.2813 | 0.083759 | 131.881 | 0.0048528 | 0.0053935 | 1.6859e-05 | 11.0011 | 0.00061214 | 0.24166 | 0.00012922 | 8.0802 | 0.065229 | 0.10349 | 0.0016967 | 8.5672 | 0.0019433 | 132.133 | 0.038178 | 131.574 | 0.0064315 | 0.19244 | 8.4239e-05 | 64.6501 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 6.9852 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | 0.0015107 | 0.086261 | -0.0006346 | 0.21368 | 0.0012074 | 0.16751 | 0.004404 | 129.353 | 0.046952 | 129.3268 | 0.0042238 | 0.23793 | 0.00041557 | 63.1193 | 0.02714 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748 | 0.22513 | 0.0031962 | 6.5815 | -0.0003594
299 | 108 | 132.2813 | 0.083759 | 131.881 | 0.0048528 | 0.0053935 | 0.0016399 | 11.0011 | 0.00061214 | 0.24166 | 0.0017522 | 8.0802 | 0.065229 | 0.20087 | 7.2991e-05 | 8.6646 | 0.00032025 | 132.133 | 0.039801 | 131.4765 | 0.0048085 | 0.095061 | 8.4239e-05 | 64.6501 | 0.032803 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 6.8879 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.095394 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.17559 | 0.0015107 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.0027804 | 129.353 | 0.046952 | 129.3268 | 0.0058469 | 0.23793 | 0.00041557 | 63.1193 | 0.02714 | 0.25952 | -0.00047174 | 0.20895 | 0.0012748 | 0.22513 | 0.0031962 | 6.9711 | 0.0012636
299.2 | 108.2 | 132.2813 | 0.083759 | 131.881 | 0.0048528 | 0.0053935 | 1.6859e-05 | 11.0011 | 0.00061214 | 0.24166 | 0.00012922 | 8.0802 | 0.065229 | 0.10349 | 7.2991e-05 | 8.6646 | 0.00032025 | 132.133 | 0.038178 | 131.574 | 0.0048085 | 0.095061 | 8.4239e-05 | 64.6501 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.2568 | 0.0014439 | 6.8879 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | 0.0015107 | 0.086261 | 0.0009884 | 0.21368 | 0.0028311 | 0.070087 | 0.004404 | 129.353 | 0.046952 | 129.2293 | 0.0042238 | 0.23793 | 0.00041557 | 63.2167 | 0.02714 | 0.1621 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 7.9451 | 0.0012636
299.4 | 108.4 | 132.2813 | 0.082136 | 131.881 | 0.0048528 | 0.0053935 | 1.6859e-05 | 11.0011 | -0.0010109 | 0.24166 | 0.00012922 | 8.0802 | 0.065229 | 0.10349 | 0.0016967 | 8.6646 | 0.00032025 | 132.133 | 0.038178 | 131.4765 | 0.0048085 | 0.19244 | 8.4239e-05 | 64.6501 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 6.9852 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | 0.0015332 | 0.29589 | 0.0014152 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 0.070087 | 0.004404 | 129.353 | 0.046952 | 129.2293 | 0.0058469 | 0.23793 | 0.00041557 | 63.1193 | 0.02714 | 0.1621 | 0.0011513 | 0.20895 | 0.0012748 | 0.22513 | 0.0031962 | 9.0164 | 0.0012636
299.6 | 108.6 | 132.2813 | 0.082136 | 131.881 | 0.0048528 | 0.0053935 | 1.6859e-05 | 11.0011 | 0.00061214 | 0.24166 | -0.0014944 | 8.1776 | 0.065229 | 0.10349 | 0.0016967 | 8.8594 | 0.00032025 | 132.2304 | 0.038178 | 131.574 | 0.0064315 | 0.19244 | 8.4239e-05 | 64.6501 | 0.034426 | 0.01988 | 0.00064048 | 0.018196 | -0.00031449 | 0.2568 | 0.0014439 | 6.9852 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.21368 | 0.0012074 | 0.16751 | 0.004404 | 129.353 | 0.046952 | 129.3268 | 0.0058469 | 0.23793 | 0.00041557 | 63.1193 | 0.028764 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 9.6008 | 0.0012636
299.8 | 108.8 | 132.3787 | 0.083759 | 131.881 | 0.0048528 | 0.0053935 | 1.6859e-05 | 11.0011 | 0.00061214 | 0.24166 | 0.0017522 | 8.0802 | 0.065229 | 0.20087 | 0.0016967 | 8.762 | 0.00032025 | 132.2304 | 0.038178 | 131.4765 | 0.0048085 | 0.19244 | 8.4239e-05 | 64.6501 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 7.0826 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.21368 | 0.0012074 | 0.070087 | 0.004404 | 129.2556 | 0.046952 | 129.3268 | 0.0058469 | 0.23793 | 0.00041557 | 63.1193 | 0.02714 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 10.2826 | 0.0012636
300 | 109 | 132.2813 | 0.083759 | 131.7836 | 0.0048528 | 0.0053935 | 1.6859e-05 | 11.0011 | 0.00061214 | 0.24166 | 0.00012922 | 8.0802 | 0.065229 | 0.20087 | 0.0016967 | 8.8594 | 0.00032025 | 132.133 | 0.038178 | 131.4765 | 0.0064315 | 0.19244 | 8.4239e-05 | 64.5527 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | -0.00017979 | 7.18 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | -0.080196 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.070087 | 0.0027804 | 129.2556 | 0.045329 | 129.2293 | 0.0058469 | 0.23793 | 0.00041557 | 63.1193 | 0.02714 | 0.1621 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 10.8669 | 0.0012636
300.2 | 109.2 | 132.1839 | 0.083759 | 131.881 | 0.0048528 | 0.0053935 | 1.6859e-05 | 10.9037 | 0.00061214 | 0.24166 | 0.00012922 | 8.0802 | 0.065229 | 0.10349 | 0.0016967 | 8.9568 | 0.0019433 | 132.133 | 0.038178 | 131.4765 | 0.0064315 | 0.095061 | 8.4239e-05 | 64.5527 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 7.2774 | 7.2982e-05 | 0.10651 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | 0.0015332 | 0.19851 | -0.00020779 | 0.27297 | 0.0015107 | -0.011119 | 0.0009884 | 0.21368 | 0.0012074 | 0.070087 | 0.004404 | 129.353 | 0.046952 | 129.3268 | 0.0042238 | 0.23793 | 0.00041557 | 63.2167 | 0.02714 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748 | 0.32251 | 0.0031962 | 11.0617 | -0.0019831
300.4 | 109.4 | 132.2813 | 0.082136 | 131.881 | 0.0048528 | 0.10277 | 1.6859e-05 | 10.9037 | 0.00061214 | 0.24166 | -0.0014944 | 8.0802 | 0.065229 | 0.10349 | 0.0016967 | 8.8594 | 0.0084366 | 132.133 | 0.038178 | 131.4765 | 0.0048085 | 0.19244 | 8.4239e-05 | 64.5527 | 0.034426 | 0.01988 | 0.00064048 | 0.018196 | 0.0013085 | 0.15942 | 0.0014439 | 7.18 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | 0.086261 | -0.0006346 | 0.21368 | 0.0012074 | 0.36227 | 0.004404 | 129.353 | 0.045329 | 129.3268 | 0.0042238 | 0.14051 | 0.00041557 | 63.022 | 0.028764 | 0.25952 | -0.00047174 | 0.20895 | 0.0012748 | 0.22513 | 0.0015725 | 10.6721 | 0.0012636
300.6 | 109.6 | 132.3787 | 0.082136 | 131.9783 | 0.0048528 | 0.10277 | 1.6859e-05 | 11.0011 | 0.00061214 | 0.24166 | 0.00012922 | 8.1776 | 0.065229 | 0.10349 | 0.0016967 | 8.9568 | 0.00032025 | 132.2304 | 0.038178 | 131.574 | 0.0048085 | 0.19244 | 8.4239e-05 | 64.5527 | 0.032803 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.2568 | 0.0014439 | 7.0826 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.095394 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.27297 | -0.00011232 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 129.353 | 0.046952 | 129.3268 | 0.0042238 | 0.23793 | 0.00041557 | 63.1193 | 0.02714 | 0.1621 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 10.1852 | 0.0012636
300.8 | 109.8 | 132.2813 | 0.083759 | 131.881 | 0.0048528 | 0.0053935 | 1.6859e-05 | 11.0011 | 0.00061214 | 0.24166 | 0.00012922 | 8.0802 | 0.066852 | 0.20087 | 0.0016967 | 9.1516 | 0.0019433 | 132.2304 | 0.038178 | 131.574 | 0.0048085 | 0.19244 | 8.4239e-05 | 64.5527 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | 0.0014439 | 6.9852 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | 0.086261 | -0.0006346 | 0.21368 | 0.0012074 | 0.16751 | 0.0027804 | 129.353 | 0.046952 | 129.3268 | 0.0042238 | 0.23793 | 0.00041557 | 63.1193 | 0.02714 | 0.1621 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 10.38 | 0.0012636
301 | 110 | 132.3787 | 0.082136 | 131.881 | 0.0048528 | 0.0053935 | 1.6859e-05 | 11.0011 | 0.00061214 | 0.24166 | 0.00012922 | 8.1776 | 0.066852 | 0.10349 | 0.0016967 | 9.2489 | 0.0019433 | 132.2304 | 0.038178 | 131.574 | 0.0048085 | 0.095061 | 8.4239e-05 | 64.5527 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | -0.00017979 | 7.2774 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.070087 | 0.004404 | 129.353 | 0.046952 | 129.3268 | 0.0058469 | 0.23793 | 0.00041557 | 63.1193 | 0.02714 | 0.1621 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 10.6721 | 0.0012636
301.2 | 110.2 | 132.2813 | 0.083759 | 131.881 | 0.0048528 | 0.0053935 | 1.6859e-05 | 11.0011 | -0.0010109 | 0.24166 | 0.00012922 | 8.1776 | 0.066852 | 0.10349 | 0.0016967 | 9.2489 | 0.0019433 | 132.2304 | 0.038178 | 131.574 | 0.0048085 | 0.19244 | 8.4239e-05 | 64.5527 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 7.3748 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 129.353 | 0.046952 | 129.3268 | 0.0058469 | 0.23793 | 0.00041557 | 63.1193 | 0.028764 | 0.1621 | 0.0011513 | 0.20895 | 0.0012748 | 0.22513 | 0.0031962 | 10.7696 | 0.0012636
301.4 | 110.4 | 132.2813 | 0.083759 | 131.881 | 0.0048528 | 0.0053935 | 1.6859e-05 | 11.0011 | 0.00061214 | 0.24166 | 0.00012922 | 8.1776 | 0.065229 | 0.10349 | 0.0016967 | 9.2489 | 0.00032025 | 132.2304 | 0.038178 | 131.574 | 0.0048085 | 0.19244 | 8.4239e-05 | 64.5527 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | -0.00017979 | 7.2774 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 129.353 | 0.046952 | 129.3268 | 0.0058469 | 0.23793 | 0.00041557 | 63.1193 | 0.02714 | 0.1621 | 0.0011513 | 0.20895 | 0.0012748 | 0.22513 | 0.0031962 | 10.9644 | 0.0012636
301.6 | 110.6 | 132.2813 | 0.082136 | 131.881 | 0.0048528 | 0.0053935 | 1.6859e-05 | 11.0011 | 0.00061214 | 0.24166 | 0.00012922 | 8.0802 | 0.065229 | 0.20087 | 0.0016967 | 9.3464 | 0.0019433 | 132.2304 | 0.038178 | 131.574 | 0.0064315 | 0.19244 | 8.4239e-05 | 64.4553 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | 0.0014439 | 7.4722 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.21368 | 0.0012074 | 0.16751 | 0.004404 | 129.353 | 0.046952 | 129.3268 | 0.0042238 | 0.23793 | 0.00041557 | 63.1193 | 0.02714 | 0.25952 | -0.00047174 | 0.11153 | -0.00034817 | 0.32251 | 0.0031962 | 10.9644 | 0.0012636
301.8 | 110.8 | 132.2813 | 0.083759 | 131.881 | 0.0048528 | 0.0053935 | 1.6859e-05 | 11.0011 | 0.00061214 | 0.24166 | 0.00012922 | 8.0802 | 0.066852 | 0.10349 | 0.0016967 | 9.3464 | 0.00032025 | 132.133 | 0.038178 | 131.4765 | 0.0048085 | 0.19244 | 8.4239e-05 | 64.4553 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 7.5696 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.070087 | 0.004404 | 129.353 | 0.045329 | 129.3268 | 0.0058469 | 0.23793 | 0.00041557 | 63.1193 | 0.028764 | 0.25952 | -0.00047174 | 0.11153 | -0.00034817 | 0.22513 | 0.0031962 | 10.9644 | 0.0012636
302 | 111 | 132.2813 | 0.083759 | 131.7836 | 0.0048528 | 0.0053935 | 1.6859e-05 | 11.0011 | 0.00061214 | 0.24166 | 0.00012922 | 8.275 | 0.066852 | 0.20087 | 0.0016967 | 9.3464 | 0.00032025 | 132.133 | 0.038178 | 131.4765 | 0.0048085 | 0.19244 | 8.4239e-05 | 64.4553 | 0.032803 | 0.01988 | 0.0022635 | 0.11562 | -0.00031449 | 0.15942 | 0.0014439 | 7.667 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | 0.0015107 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.070087 | 0.004404 | 129.353 | 0.046952 | 129.2293 | 0.0042238 | 0.23793 | 0.00041557 | 63.1193 | 0.02714 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 11.1591 | 0.0012636
302.2 | 111.2 | 132.1839 | 0.082136 | 131.881 | 0.0048528 | 0.0053935 | 0.0016399 | 11.0011 | 0.00061214 | 0.24166 | 0.00012922 | 8.1776 | 0.065229 | 0.10349 | 0.0016967 | 9.2489 | 0.0019433 | 132.133 | 0.038178 | 131.574 | 0.0064315 | 0.19244 | 8.4239e-05 | 64.4553 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | 0.0014439 | 7.8618 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.29589 | 0.0014152 | 0.17559 | -0.00011232 | -0.011119 | -0.0006346 | 0.21368 | 0.0012074 | 0.070087 | 0.004404 | 129.353 | 0.046952 | 129.2293 | 0.0042238 | 0.23793 | 0.00041557 | 63.1193 | 0.02714 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0048192 | 11.2565 | 0.0012636
302.4 | 111.4 | 132.3787 | 0.082136 | 131.881 | 0.0048528 | 0.0053935 | 0.0016399 | 11.0011 | 0.00061214 | 0.14424 | 0.00012922 | 8.1776 | 0.065229 | 0.10349 | 0.0016967 | 9.3464 | 0.0019433 | 132.2304 | 0.038178 | 131.574 | 0.0048085 | 0.19244 | 8.4239e-05 | 64.4553 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.2568 | -0.00017979 | 8.0566 | 0.0016967 | 0.30132 | 0.001477 | 0.095394 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.27297 | 0.0015107 | -0.011119 | 0.0009884 | 0.21368 | 0.0012074 | 0.16751 | 0.004404 | 129.353 | 0.046952 | 129.3268 | 0.0042238 | 0.23793 | 0.00041557 | 63.1193 | 0.02714 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 11.3539 | 0.0012636
302.6 | 111.6 | 132.2813 | 0.083759 | 131.881 | 0.0048528 | 0.0053935 | 1.6859e-05 | 11.0011 | -0.0010109 | 0.24166 | 0.0017522 | 8.275 | 0.066852 | 0.10349 | 0.0016967 | 9.6385 | 0.00032025 | 132.133 | 0.038178 | 131.574 | 0.0064315 | 0.19244 | 8.4239e-05 | 64.3579 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 8.154 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | -0.080196 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.17559 | 0.0015107 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 129.2556 | 0.046952 | 129.3268 | 0.0042238 | 0.23793 | 0.00041557 | 63.1193 | 0.02714 | 0.1621 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0048192 | 11.3539 | 0.0012636
302.8 | 111.8 | 132.2813 | 0.083759 | 131.881 | 0.0048528 | 0.10277 | 0.0016399 | 11.0011 | 0.00061214 | 0.24166 | 0.00012922 | 8.275 | 0.066852 | 0.10349 | 7.2991e-05 | 9.6385 | 0.00032025 | 132.2304 | 0.038178 | 131.4765 | 0.0048085 | 0.095061 | 8.4239e-05 | 64.4553 | 0.032803 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 8.2514 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | 0.0015332 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | -0.0006346 | 0.21368 | 0.0012074 | 0.16751 | 0.004404 | 129.353 | 0.046952 | 129.3268 | 0.0042238 | 0.23793 | 0.00041557 | 63.1193 | 0.02714 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 11.5487 | 0.0012636
303 | 112 | 132.3787 | 0.083759 | 131.881 | 0.0048528 | 0.10277 | 1.6859e-05 | 11.0985 | 0.00061214 | 0.24166 | 0.00012922 | 8.275 | 0.066852 | 0.20087 | 7.2991e-05 | 9.6385 | 0.0019433 | 132.2304 | 0.038178 | 131.574 | 0.0064315 | 0.19244 | 8.4239e-05 | 64.3579 | 0.034426 | -0.0775 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | -0.00017979 | 8.3488 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.095394 | 0.00023025 | -0.080196 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | 0.0015107 | -0.011119 | 0.0009884 | 0.21368 | 0.0012074 | 0.16751 | 0.006027 | 129.353 | 0.046952 | 129.3268 | 0.0042238 | 0.23793 | 0.00041557 | 63.1193 | 0.028764 | 0.25952 | -0.00047174 | 0.11153 | -0.00034817 | 0.32251 | 0.0031962 | 11.5487 | 0.0012636
303.2 | 112.2 | 132.2813 | 0.083759 | 131.7836 | 0.0048528 | 0.0053935 | 1.6859e-05 | 11.0011 | 0.00061214 | 0.24166 | 0.00012922 | 8.275 | 0.066852 | 0.20087 | 0.0016967 | 9.6385 | 0.00032025 | 132.133 | 0.038178 | 131.574 | 0.0064315 | 0.095061 | 8.4239e-05 | 64.3579 | 0.032803 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | 0.0014439 | 8.5436 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | 0.0015332 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.21368 | 0.0028311 | 0.070087 | 0.004404 | 129.353 | 0.045329 | 129.2293 | 0.0042238 | 0.23793 | 0.00041557 | 63.022 | 0.02714 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 11.7435 | 0.0012636
303.4 | 112.4 | 132.2813 | 0.083759 | 131.881 | 0.0048528 | 0.0053935 | 1.6859e-05 | 11.0011 | 0.00061214 | 0.33904 | 0.00012922 | 8.275 | 0.068475 | 0.10349 | 0.0016967 | 9.5412 | 0.00032025 | 132.133 | 0.038178 | 131.574 | 0.0048085 | 0.19244 | 8.4239e-05 | 64.2605 | 0.032803 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | 0.0014439 | 8.641 | 7.2982e-05 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 129.353 | 0.045329 | 129.2293 | 0.0042238 | 0.23793 | 0.00041557 | 63.1193 | 0.02714 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748 | 0.22513 | 0.0031962 | 11.6461 | 0.0012636
303.6 | 112.6 | 132.2813 | 0.083759 | 131.881 | 0.0048528 | 0.10277 | 1.6859e-05 | 11.0011 | 0.00061214 | 0.24166 | 0.00012922 | 8.275 | 0.066852 | 0.10349 | 0.0016967 | 9.5412 | 0.0019433 | 132.133 | 0.038178 | 131.574 | 0.0064315 | 0.19244 | 8.4239e-05 | 64.2605 | 0.032803 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 8.7384 | 0.0016967 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.21368 | 0.0012074 | 0.16751 | 0.004404 | 129.2556 | 0.046952 | 129.3268 | 0.0058469 | 0.23793 | 0.00041557 | 63.1193 | 0.028764 | 0.1621 | -0.00047174 | 0.20895 | -0.00034817 | 0.22513 | 0.0048192 | 11.7435 | 0.0012636
303.8 | 112.8 | 132.2813 | 0.082136 | 131.881 | 0.0048528 | 0.0053935 | 1.6859e-05 | 11.0985 | 0.00061214 | 0.14424 | 0.00012922 | 8.3724 | 0.068475 | 0.20087 | 0.0016967 | 9.6385 | 0.00032025 | 132.2304 | 0.038178 | 131.574 | 0.0048085 | 0.19244 | 8.4239e-05 | 64.2605 | 0.034426 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | 0.0014439 | 8.5436 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | -0.080196 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.21368 | 0.0028311 | 0.16751 | 0.004404 | 129.353 | 0.046952 | 129.2293 | 0.0058469 | 0.23793 | 0.00041557 | 63.1193 | 0.028764 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817 | 0.32251 | 0.0031962 | 11.7435 | 0.0012636
304 | 113 | 132.2813 | 0.083759 | 131.881 | 0.0048528 | 0.0053935 | 1.6859e-05 | 11.0985 | -0.0010109 | 0.24166 | 0.00012922 | 8.3724 | 0.066852 | 0.20087 | 0.0016967 | 9.7359 | 0.00032025 | 132.133 | 0.038178 | 131.4765 | 0.0064315 | 0.19244 | 8.4239e-05 | 64.2605 | 0.032803 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | 0.0014439 | 8.4462 | 7.2982e-05 | 0.30132 | 0.001477 | 0.19277 | 0.00023025 | 0.017185 | 0.0015332 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.21368 | 0.0012074 | 0.070087 | 0.004404 | 129.353 | 0.046952 | 129.3268 | 0.0058469 | 0.23793 | 0.00041557 | 63.022 | 0.028764 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817 | 0.32251 | 0.0031962 | 11.9383 | -0.0003594
304.2 | 113.2 | 132.2813 | 0.083759 | 131.881 | 0.0048528 | 0.0053935 | 1.6859e-05 | 11.0985 | 0.00061214 | 0.24166 | 0.00012922 | 8.3724 | 0.068475 | 0.20087 | 0.0016967 | 9.8333 | 0.00032025 | 132.133 | 0.038178 | 131.574 | 0.0048085 | 0.19244 | 8.4239e-05 | 64.1631 | 0.032803 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 8.7384 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | 0.0015332 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | -0.011119 | -0.0006346 | 0.21368 | 0.0012074 | 0.070087 | 0.004404 | 129.353 | 0.046952 | 129.3268 | 0.0042238 | 0.23793 | 0.00041557 | 63.022 | 0.02714 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0048192 | 12.0357 | 0.0012636
304.4 | 113.4 | 132.2813 | 0.082136 | 131.881 | 0.0048528 | 0.0053935 | 1.6859e-05 | 11.0985 | 0.00061214 | 0.24166 | 0.00012922 | 8.3724 | 0.068475 | 0.20087 | 0.0016967 | 9.9307 | 0.0019433 | 132.2304 | 0.038178 | 131.4765 | 0.0064315 | 0.19244 | 8.4239e-05 | 64.0657 | 0.032803 | 0.01988 | 0.0022635 | 0.11562 | -0.00031449 | 0.2568 | -0.00017979 | 8.9332 | 7.2982e-05 | 0.2039 | 0.001477 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.10109 | -0.00020779 | 0.17559 | 0.0015107 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.070087 | 0.004404 | 129.353 | 0.046952 | 129.3268 | 0.0058469 | 0.23793 | 0.00041557 | 63.022 | 0.028764 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748 | 0.22513 | 0.0031962 | 12.0357 | 0.0012636
304.6 | 113.6 | 132.2813 | 0.082136 | 131.881 | 0.0048528 | 0.0053935 | 1.6859e-05 | 11.0985 | 0.00061214 | 0.24166 | 0.00012922 | 8.4698 | 0.068475 | 0.20087 | 0.0016967 | 10.0281 | 0.00032025 | 132.133 | 0.038178 | 131.4765 | 0.0048085 | 0.19244 | 8.4239e-05 | 64.0657 | 0.031179 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | -0.00017979 | 9.128 | 0.0016967 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | 0.0015332 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 129.353 | 0.045329 | 129.2293 | 0.0058469 | 0.23793 | -0.0012074 | 63.022 | 0.02714 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748 | 0.22513 | 0.0031962 | 11.9383 | 0.0012636
304.8 | 113.8 | 132.2813 | 0.083759 | 131.7836 | 0.0048528 | 0.0053935 | 1.6859e-05 | 11.0985 | 0.00061214 | 0.24166 | 0.00012922 | 8.4698 | 0.068475 | 0.10349 | 0.0016967 | 10.0281 | 0.0019433 | 132.133 | 0.039801 | 131.4765 | 0.0048085 | 0.19244 | 8.4239e-05 | 63.9683 | 0.032803 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.2568 | 0.0014439 | 9.128 | 0.0016967 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.21368 | 0.0012074 | 0.16751 | 0.0027804 | 129.2556 | 0.046952 | 129.2293 | 0.0042238 | 0.14051 | 0.00041557 | 63.022 | 0.02714 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 11.9383 | -0.0003594
305 | 114 | 132.2813 | 0.083759 | 131.7836 | 0.0048528 | 0.0053935 | 1.6859e-05 | 8.3714 | 0.00061214 | 0.14424 | 0.00012922 | 6.5219 | 0.058735 | 0.10349 | 0.0016967 | 8.9568 | 0.00032025 | 132.133 | 0.038178 | 131.4765 | 0.0064315 | 0.19244 | 8.4239e-05 | 63.8709 | 0.032803 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 9.3228 | 7.2982e-05 | 0.2039 | 0.001477 | 0.095394 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | -0.0006346 | 0.21368 | 0.0012074 | 0.16751 | 0.004404 | 129.353 | 0.046952 | 129.3268 | 0.0042238 | 0.23793 | 0.00041557 | 63.022 | 0.028764 | 0.25952 | -0.00047174 | 0.20895 | 0.0012748 | 0.22513 | 0.0031962 | 12.0357 | 0.0012636
305.2 | 114.2 | 132.1839 | 0.085382 | 131.7836 | 0.0048528 | 0.10277 | 1.6859e-05 | 5.8391 | -0.0010109 | 2.6766 | 0.0017522 | 4.1843 | 0.034386 | 0.20087 | 0.0016967 | 7.788 | 0.00032025 | 132.0357 | 0.038178 | 131.4765 | 0.0064315 | 0.19244 | 8.4239e-05 | 63.9683 | 0.032803 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 9.615 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.27297 | -0.00011232 | 0.086261 | 0.0009884 | 0.21368 | 0.0012074 | 0.16751 | 0.006027 | 129.2556 | 0.046952 | 129.2293 | 0.0042238 | 0.23793 | 0.00041557 | 63.022 | 0.02714 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0048192 | 12.3279 | 0.0012636
305.4 | 114.4 | 132.2813 | 0.087005 | 131.881 | 0.0048528 | 0.0053935 | 1.6859e-05 | 5.5469 | 0.00061214 | 4.6245 | 0.011492 | 3.8921 | 0.029517 | 0.20087 | 0.0016967 | 7.4958 | 0.00032025 | 132.133 | 0.038178 | 131.4765 | 0.0048085 | 0.19244 | 8.4239e-05 | 63.9683 | 0.032803 | -0.0775 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 9.615 | 7.2982e-05 | 0.2039 | 0.001477 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.21368 | 0.0012074 | 0.070087 | 0.004404 | 129.353 | 0.046952 | 129.3268 | 0.0042238 | 0.23793 | 0.00041557 | 63.022 | 0.02714 | 0.1621 | 0.0011513 | 0.20895 | 0.0012748 | 0.22513 | 0.0031962 | 12.2305 | -0.0003594
305.6 | 114.6 | 132.1839 | 0.087005 | 131.7836 | 0.0032298 | 0.0053935 | 1.6859e-05 | 5.4495 | 0.00061214 | 5.0141 | 0.030972 | 3.7948 | 0.027894 | 0.20087 | 0.0016967 | 7.3984 | 0.00032025 | 132.133 | 0.038178 | 131.574 | 0.0048085 | 0.19244 | 8.4239e-05 | 63.9683 | 0.032803 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.2568 | -0.00017979 | 9.7123 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.095394 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.29589 | -0.00020779 | 0.17559 | 0.0015107 | -0.011119 | 0.0009884 | 0.21368 | 0.0012074 | 0.16751 | 0.004404 | 129.2556 | 0.045329 | 129.2293 | 0.0058469 | 0.23793 | 0.00041557 | 63.022 | 0.02714 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 12.6201 | 0.0012636
305.8 | 114.8 | 132.2813 | 0.087005 | 131.881 | 0.0048528 | 0.0053935 | 1.6859e-05 | 5.3521 | 0.00061214 | 5.2089 | 0.039088 | 3.6973 | 0.027894 | 0.20087 | 0.0016967 | 7.4958 | 0.00032025 | 132.133 | 0.038178 | 131.574 | 0.0048085 | 0.19244 | 8.4239e-05 | 64.0657 | 0.032803 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | 0.0014439 | 9.7123 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.29589 | 0.0014152 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.21368 | 0.0012074 | 0.16751 | 0.004404 | 129.353 | 0.046952 | 129.3268 | 0.0042238 | 0.23793 | 0.00041557 | 63.022 | 0.02714 | 0.25952 | -0.00047174 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 13.0097 | 0.0012636
306 | 115 | 132.1839 | 0.085382 | 131.7836 | 0.0048528 | 0.0053935 | 1.6859e-05 | 9.8323 | 0.00061214 | 2.4818 | 0.022855 | 7.2036 | 0.048996 | 0.10349 | 0.0016967 | 9.7359 | 0.00032025 | 132.133 | 0.038178 | 131.4765 | 0.0048085 | 0.19244 | 8.4239e-05 | 64.0657 | 0.032803 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | -0.00017979 | 9.8098 | 7.2982e-05 | 0.2039 | 0.001477 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.21368 | 0.0012074 | 0.16751 | 0.004404 | 129.2556 | 0.046952 | 129.2293 | 0.0042238 | 0.23793 | 0.00041557 | 63.022 | 0.02714 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748 | 0.22513 | 0.0031962 | 13.0097 | 0.0012636
306.2 | 115.2 | 132.2813 | 0.083759 | 131.7836 | 0.0048528 | 0.0053935 | 1.6859e-05 | 11.0985 | -0.0010109 | 0.9234 | 0.0098686 | 8.5672 | 0.070098 | 0.20087 | 0.0016967 | 10.5151 | 0.00032025 | 132.133 | 0.036554 | 131.4765 | 0.0048085 | 0.095061 | 8.4239e-05 | 63.9683 | 0.032803 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | -0.00017979 | 9.9071 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.27297 | 0.0015107 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 129.2556 | 0.046952 | 129.2293 | 0.0042238 | 0.33531 | 0.00041557 | 63.022 | 0.02714 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 12.9123 | 0.0012636
306.4 | 115.4 | 132.2813 | 0.083759 | 131.881 | 0.0048528 | 0.0053935 | 1.6859e-05 | 11.3907 | -0.0010109 | 0.63122 | 0.0049989 | 8.6646 | 0.071722 | 0.10349 | 0.0016967 | 10.7099 | 0.00032025 | 132.133 | 0.036554 | 131.4765 | 0.0048085 | 0.095061 | 8.4239e-05 | 63.9683 | 0.032803 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.2568 | -0.00017979 | 10.0046 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.095394 | -0.0013928 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.21368 | 0.0012074 | 0.070087 | 0.004404 | 129.353 | 0.046952 | 129.2293 | 0.0042238 | 0.23793 | 0.00041557 | 63.022 | 0.02714 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748 | 0.22513 | 0.0048192 | 13.0097 | 0.0012636
306.6 | 115.6 | 132.1839 | 0.082136 | 131.7836 | 0.0048528 | 0.0053935 | 1.6859e-05 | 11.5855 | 0.00061214 | 0.43642 | 0.0049989 | 8.8594 | 0.071722 | 0.10349 | 0.0016967 | 11.3917 | 0.00032025 | 132.133 | 0.038178 | 131.4765 | 0.0048085 | 0.19244 | 8.4239e-05 | 63.9683 | 0.032803 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | -0.00017979 | 10.1019 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.29589 | 0.0014152 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 0.070087 | 0.004404 | 129.2556 | 0.046952 | 129.2293 | 0.0042238 | 0.23793 | 0.00041557 | 63.022 | 0.02714 | 0.1621 | 0.0011513 | 0.20895 | 0.0012748 | 0.22513 | 0.0048192 | 13.0097 | 0.0012636
306.8 | 115.8 | 132.1839 | 0.083759 | 131.7836 | 0.0048528 | 0.0053935 | 1.6859e-05 | 11.7803 | 0.00061214 | 0.43642 | 0.0033759 | 9.1516 | 0.073345 | 0.10349 | 0.0016967 | 12.2682 | 0.0019433 | 132.133 | 0.038178 | 131.4765 | 0.0031849 | 0.19244 | 8.4239e-05 | 63.9683 | 0.032803 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 10.2967 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | 0.0015332 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 129.2556 | 0.046952 | 129.3268 | 0.0042238 | 0.33531 | 0.00041557 | 63.022 | 0.02714 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748 | 0.22513 | 0.0031962 | 13.0097 | 0.0012636
307 | 116 | 132.1839 | 0.085382 | 131.7836 | 0.0048528 | 0.0053935 | 0.0016399 | 6.8131 | 0.00061214 | 3.6505 | 0.013115 | 5.2557 | 0.044126 | 0.20087 | 0.0016967 | 9.9307 | 0.0019433 | 132.133 | 0.038178 | 131.4765 | 0.0048085 | 0.19244 | 8.4239e-05 | 63.9683 | 0.032803 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.2568 | -0.00017979 | 10.4915 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | 0.0015107 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 129.2556 | 0.046952 | 129.2293 | 0.0042238 | 0.23793 | 0.00041557 | 63.022 | 0.028764 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 13.2045 | 0.0012636
307.2 | 116.2 | 132.0865 | 0.085382 | 131.6862 | 0.0064758 | 0.0053935 | -0.0016068 | 5.9365 | 0.00061214 | 5.1115 | 0.034218 | 4.5739 | 0.037633 | 0.10349 | 0.0016967 | 9.5412 | 0.0019433 | 132.133 | 0.038178 | 131.4765 | 0.0048085 | 0.19244 | 8.4239e-05 | 63.9683 | 0.032803 | -0.0775 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 10.3941 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | 0.0015332 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | -0.011119 | -0.0006346 | 0.21368 | 0.0012074 | 0.16751 | 0.006027 | 129.2556 | 0.046952 | 129.2293 | 0.0042238 | 0.33531 | 0.00041557 | 62.9245 | 0.02714 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 13.4967 | 0.0012636
307.4 | 116.4 | 132.2813 | 0.085382 | 131.7836 | 0.0080995 | 0.0053935 | 1.6859e-05 | 6.0339 | 0.00061214 | 5.6958 | 0.040711 | 4.6713 | 0.034386 | 0.20087 | 0.0016967 | 9.1516 | 0.0019433 | 132.133 | 0.038178 | 131.3792 | 0.0048085 | 0.19244 | 0.0017072 | 63.9683 | 0.032803 | 0.01988 | 0.0022635 | 0.11562 | 0.0013085 | 0.15942 | -0.00017979 | 10.5889 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.095394 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.018878 | 0.0012074 | 0.070087 | 0.004404 | 129.2556 | 0.046952 | 129.2293 | 0.0042238 | 0.14051 | 0.00041557 | 63.022 | 0.02714 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 13.9836 | 0.0012636
307.6 | 116.6 | 132.3787 | 0.087005 | 131.7836 | 0.0097225 | 0.10277 | 1.6859e-05 | 6.3261 | 0.00061214 | 5.5011 | 0.039088 | 4.8661 | 0.03601 | 0.29825 | 0.0016967 | 9.3464 | 0.00032025 | 132.133 | 0.038178 | 131.4765 | 0.0048085 | 0.19244 | 8.4239e-05 | 63.8709 | 0.032803 | 0.01988 | 0.0022635 | 0.11562 | 0.0013085 | 0.15942 | -0.00017979 | 10.4915 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.095394 | 0.00023025 | -0.080196 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.17559 | 0.0015107 | -0.011119 | 0.0009884 | 0.11626 | 0.0028311 | 0.070087 | 0.006027 | 129.2556 | 0.046952 | 129.2293 | 0.0058469 | 0.23793 | 0.00041557 | 63.022 | 0.02714 | 0.25952 | -0.00047174 | 0.20895 | -0.00034817 | 0.32251 | 0.0048192 | 13.7888 | 0.0012636
307.8 | 116.8 | 132.0865 | 0.085382 | 131.5888 | 0.012969 | 0.10277 | 1.6859e-05 | 6.7156 | 0.00061214 | 5.0141 | 0.037464 | 4.9635 | 0.032763 | 0.59047 | 0.0049427 | 8.3724 | 0.0019433 | 132.133 | 0.038178 | 131.4765 | 0.0048085 | 0.19244 | 8.4239e-05 | 63.8709 | 0.032803 | 0.01988 | 0.0038865 | 0.018196 | 0.0013085 | 0.15942 | -0.00017979 | 10.4915 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | 0.0015332 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | 0.086261 | 0.0026121 | 0.21368 | 0.0012074 | 0.070087 | 0.004404 | 129.2556 | 0.046952 | 129.2293 | 0.0042238 | 0.23793 | 0.00041557 | 63.022 | 0.02714 | 0.1621 | -0.00047174 | 0.20895 | 0.0012748 | 0.22513 | 0.0031962 | 13.3993 | 0.0012636
308 | 117 | 132.0865 | 0.085382 | 131.5888 | 0.0097225 | 0.0053935 | 1.6859e-05 | 6.0339 | 0.00061214 | 5.5011 | 0.039088 | 4.5739 | 0.032763 | 0.20087 | 0.0016967 | 9.1516 | 0.00032025 | 132.0357 | 0.038178 | 131.3792 | 0.0048085 | 0.095061 | 8.4239e-05 | 63.7735 | 0.032803 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.2568 | -0.00017979 | 10.4915 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | 0.0015332 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.21368 | 0.0012074 | 0.16751 | 0.004404 | 129.1582 | 0.046952 | 129.2293 | 0.0042238 | 0.23793 | 0.00041557 | 62.9245 | 0.028764 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748 | 0.22513 | 0.0031962 | 13.3993 | 0.0012636
308.2 | 117.2 | 131.8917 | 0.085382 | 131.4914 | 0.056798 | 0.0053935 | 1.6859e-05 | 7.6896 | 0.00061214 | 7.5464 | 0.061813 | 7.0088 | 0.060359 | 0.10349 | 0.0016967 | 7.5932 | 0.00032025 | 132.0357 | 0.036554 | 131.3792 | 0.0048085 | 0.19244 | 8.4239e-05 | 63.7735 | 0.032803 | 0.01988 | 0.0022635 | 0.11562 | 0.0013085 | 0.2568 | -0.00017979 | 10.4915 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | 0.0015332 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.21368 | 0.0012074 | 0.16751 | 0.004404 | 129.2556 | 0.046952 | 129.2293 | 0.0042238 | 0.23793 | 0.00041557 | 63.022 | 0.02714 | 0.1621 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 13.3019 | 0.0012636
308.4 | 117.4 | 132.0865 | 0.085382 | 131.6862 | 0.019463 | 0.10277 | 1.6859e-05 | 5.1573 | 0.00061214 | 5.1115 | 0.039088 | 4.4765 | 0.034386 | 0.20087 | 0.0016967 | 4.1843 | 0.00032025 | 132.0357 | 0.038178 | 131.3792 | 0.0048085 | 0.19244 | 8.4239e-05 | 63.7735 | 0.032803 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 10.6863 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.095394 | 0.00023025 | 0.017185 | 0.0015332 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0028311 | 0.070087 | 0.004404 | 129.1582 | 0.046952 | 129.2293 | 0.0042238 | 0.23793 | 0.00041557 | 62.9245 | 0.02714 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748 | 0.22513 | 0.0031962 | 13.4967 | 0.0012636
308.6 | 117.6 | 132.0865 | 0.085382 | 131.6862 | 0.012969 | 0.0053935 | 1.6859e-05 | 4.9625 | 0.00061214 | 5.1115 | 0.035841 | 4.2817 | 0.03114 | 0.20087 | 0.0016967 | 3.8921 | 0.00032025 | 132.0357 | 0.038178 | 131.3792 | 0.0048085 | 0.19244 | 8.4239e-05 | 63.8709 | 0.032803 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 10.7837 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | 0.0015332 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.21368 | 0.0012074 | 0.070087 | 0.004404 | 129.2556 | 0.046952 | 129.2293 | 0.0058469 | 0.23793 | 0.0020392 | 62.9245 | 0.02714 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748 | 0.22513 | 0.0031962 | 13.4967 | 0.0012636
308.8 | 117.8 | 132.0865 | 0.087005 | 131.6862 | 0.0097225 | 0.0053935 | 1.6859e-05 | 5.0599 | 0.00061214 | 5.1115 | 0.037464 | 4.1843 | 0.03114 | 0.10349 | 0.0016967 | 3.8921 | 0.00032025 | 132.133 | 0.038178 | 131.4765 | 0.0048085 | 0.19244 | 8.4239e-05 | 63.7735 | 0.032803 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | 0.0014439 | 10.8811 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.21368 | 0.0012074 | 0.16751 | 0.004404 | 129.2556 | 0.046952 | 129.2293 | 0.0058469 | 0.23793 | 0.00041557 | 62.9245 | 0.028764 | 0.1621 | 0.0011513 | 0.20895 | -0.00034817 | 0.32251 | 0.0031962 | 13.6915 | 0.0012636
309 | 118 | 132.0865 | 0.087005 | 131.6862 | 0.0080995 | 0.0053935 | 1.6859e-05 | 5.0599 | 0.00061214 | 5.1115 | 0.037464 | 4.1843 | 0.03114 | 0.20087 | 0.0016967 | 3.8921 | 0.0019433 | 132.0357 | 0.038178 | 131.4765 | 0.0048085 | 0.19244 | 8.4239e-05 | 63.7735 | 0.032803 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | -0.00017979 | 10.9785 | 7.2982e-05 | 0.30132 | -0.00014601 | 0.095394 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.29589 | 0.0014152 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.21368 | 0.0012074 | 0.16751 | 0.004404 | 129.2556 | 0.046952 | 129.2293 | 0.0058469 | 0.23793 | 0.00041557 | 62.9245 | 0.02714 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748 | 0.22513 | 0.0031962 | 13.8863 | 0.0012636
309.2 | 118.2 | 132.0865 | 0.087005 | 131.6862 | 0.0064758 | 0.0053935 | 1.6859e-05 | 5.2547 | 0.00061214 | 5.1115 | 0.037464 | 4.0869 | 0.03114 | 0.10349 | 0.0016967 | 3.8921 | 0.00032025 | 132.133 | 0.038178 | 131.4765 | 0.0048085 | 0.19244 | 8.4239e-05 | 63.7735 | 0.032803 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | -0.00017979 | 11.1733 | 7.2982e-05 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 129.2556 | 0.046952 | 129.2293 | 0.0058469 | 0.23793 | 0.00041557 | 62.9245 | 0.02714 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 13.8863 | 0.0012636
309.4 | 118.4 | 132.0865 | 0.087005 | 131.6862 | 0.0064758 | 0.0053935 | 1.6859e-05 | 5.2547 | 0.00061214 | 5.2089 | 0.037464 | 4.0869 | 0.03114 | 0.20087 | 0.0016967 | 3.7948 | 0.00032025 | 132.0357 | 0.038178 | 131.4765 | 0.0048085 | 0.19244 | 8.4239e-05 | 63.7735 | 0.032803 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 11.2707 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 129.2556 | 0.046952 | 129.2293 | 0.0042238 | 0.33531 | 0.00041557 | 62.9245 | 0.028764 | 0.1621 | -0.00047174 | 0.20895 | 0.0012748 | 0.32251 | 0.0048192 | 13.7888 | 0.0012636
309.6 | 118.6 | 132.0865 | 0.088629 | 131.6862 | 0.0064758 | 0.0053935 | 0.0016399 | 5.2547 | 0.00061214 | 5.1115 | 0.039088 | 4.1843 | 0.03114 | 0.20087 | 0.0016967 | 3.8921 | 0.0019433 | 132.133 | 0.038178 | 131.4765 | 0.0048085 | 0.19244 | 8.4239e-05 | 63.7735 | 0.032803 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 11.1733 | 7.2982e-05 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.29589 | 0.0014152 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.21368 | 0.0012074 | 0.16751 | 0.004404 | 129.2556 | 0.046952 | 129.2293 | 0.0058469 | 0.23793 | 0.00041557 | 62.9245 | 0.02714 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 13.8863 | 0.0012636
309.8 | 118.8 | 132.0865 | 0.085382 | 131.6862 | 0.0064758 | 0.0053935 | 1.6859e-05 | 5.3521 | 0.00061214 | 5.2089 | 0.039088 | 4.0869 | 0.029517 | 0.10349 | 0.0016967 | 3.8921 | 0.00032025 | 132.133 | 0.036554 | 131.4765 | 0.0048085 | 0.19244 | 0.0017072 | 63.7735 | 0.032803 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 11.0759 | 7.2982e-05 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.27297 | 0.0015107 | 0.086261 | 0.0009884 | 0.21368 | 0.0012074 | 0.16751 | 0.004404 | 129.1582 | 0.046952 | 129.3268 | 0.0058469 | 0.23793 | 0.00041557 | 62.9245 | 0.02714 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0048192 | 13.9836 | 0.0012636
310 | 119 | 132.0865 | 0.087005 | 131.6862 | 0.0064758 | 0.0053935 | 1.6859e-05 | 5.4495 | -0.0010109 | 5.2089 | 0.037464 | 4.1843 | 0.03114 | 0.20087 | 0.0016967 | 3.8921 | 0.0019433 | 132.0357 | 0.038178 | 131.3792 | 0.0048085 | 0.19244 | 8.4239e-05 | 63.6761 | 0.032803 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | 0.0014439 | 11.1733 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.21368 | 0.0012074 | 0.16751 | 0.004404 | 129.2556 | 0.046952 | 129.132 | 0.0058469 | 0.23793 | 0.00041557 | 62.8272 | 0.02714 | 0.1621 | 0.0011513 | 0.20895 | 0.0012748 | 0.22513 | 0.0031962 | 14.2758 | 0.0012636
310.2 | 119.2 | 132.1839 | 0.085382 | 131.6862 | 0.0048528 | 0.0053935 | 1.6859e-05 | 5.2547 | -0.0010109 | 5.1115 | 0.039088 | 4.1843 | 0.03114 | 0.20087 | 0.0016967 | 3.7948 | 0.00032025 | 131.6461 | 0.14856 | 130.9896 | 0.0048085 | 0.19244 | 8.4239e-05 | 63.7735 | 0.032803 | 91.7674 | 0.0055102 | 0.018196 | 0.0013085 | 0.15942 | -0.00017979 | 12.7316 | 0.0016967 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.21368 | 0.0012074 | 0.070087 | 0.004404 | 129.2556 | 0.046952 | 129.2293 | 0.0058469 | 0.23793 | 0.00041557 | 62.9245 | 0.02714 | 0.1621 | 0.0011513 | 0.20895 | 0.0012748 | 0.22513 | 0.0031962 | 15.055 | 0.0012636
310.4 | 119.4 | 132.1839 | 0.085382 | 131.6862 | 0.0048528 | 0.10277 | 1.6859e-05 | 5.2547 | 0.00061214 | 5.2089 | 0.039088 | 4.1843 | 0.03114 | 0.20087 | 0.0033197 | 3.8921 | 0.00032025 | 131.7434 | 0.12584 | 131.087 | 0.0048085 | 0.19244 | 8.4239e-05 | 63.9683 | 0.032803 | 127.8041 | 0.0055102 | 0.11562 | 0.0013085 | 0.15942 | 0.0014439 | 13.5108 | 7.2982e-05 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.27297 | -0.00011232 | -0.011119 | 0.0009884 | 0.21368 | 0.0012074 | 0.16751 | 0.006027 | 129.2556 | 0.046952 | 129.132 | 0.0058469 | 0.23793 | 0.00041557 | 62.9245 | 0.02714 | 0.25952 | -0.00047174 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 15.2498 | 0.0012636
310.6 | 119.6 | 132.0865 | 0.069149 | 131.7836 | 0.0080995 | 0.0053935 | 1.6859e-05 | 5.3521 | 0.00061214 | 5.2089 | 0.039088 | 4.1843 | 0.03114 | 0.20087 | 0.0016967 | 3.8921 | 0.00032025 | 131.7434 | 0.12421 | 131.087 | 0.0048085 | 0.19244 | 8.4239e-05 | 63.9683 | 0.032803 | 130.3364 | 0.0055102 | 0.018196 | 0.0013085 | 0.15942 | -0.00017979 | 13.4134 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | -0.080196 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 0.070087 | 0.004404 | 129.2556 | 0.046952 | 129.132 | 0.0042238 | 0.23793 | 0.00041557 | 62.8272 | 0.02714 | 0.1621 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 15.2498 | 0.0012636
310.8 | 119.8 | 132.0865 | 0.056163 | 131.7836 | 0.025955 | 0.0053935 | 1.6859e-05 | 5.3521 | 0.00061214 | 5.2089 | 0.039088 | 4.1843 | 0.03114 | 0.20087 | 0.0016967 | 3.8921 | 0.00032025 | 131.7434 | 0.12259 | 131.087 | 0.0048085 | 0.19244 | 8.4239e-05 | 63.9683 | 0.032803 | 130.6286 | 0.059078 | 0.018196 | 0.0013085 | 0.15942 | 0.0014439 | 13.4134 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.27297 | -0.00011232 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 129.2556 | 0.046952 | 129.2293 | 0.0058469 | 0.23793 | 0.00041557 | 62.8272 | 0.02714 | 0.25952 | -0.00047174 | 0.11153 | -0.00034817 | 0.22513 | 0.0031962 | 15.2498 | 0.0012636
311 | 120 | 131.8917 | 0.052917 | 131.6862 | 0.038942 | 0.0053935 | 1.6859e-05 | 5.3521 | 0.00061214 | 5.5011 | 0.039088 | 4.4765 | 0.032763 | 0.20087 | 0.0016967 | 4.0869 | 0.00032025 | 131.7434 | 0.12259 | 131.087 | 0.0048085 | 0.19244 | 0.0017072 | 63.8709 | 0.032803 | 130.726 | 0.09479 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 13.4134 | 7.2982e-05 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | 0.0015332 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.21368 | 0.0012074 | 0.16751 | 0.004404 | 129.1582 | 0.046952 | 129.132 | 0.0058469 | 0.23793 | 0.00041557 | 62.7297 | 0.02714 | 0.25952 | 0.0011513 | 0.11153 | -0.00034817 | 0.22513 | 0.0048192 | 15.4446 | 0.0012636
311.2 | 120.2 | 132.1839 | 0.061033 | 131.6862 | 0.051928 | 0.0053935 | 1.6859e-05 | 6.6183 | 0.00061214 | 6.475 | 0.047204 | 5.7427 | 0.042503 | 0.10349 | 0.0016967 | 5.5479 | 0.00032025 | 131.7434 | 0.12421 | 131.087 | 0.0048085 | 0.19244 | 8.4239e-05 | 63.8709 | 0.034426 | 130.726 | 0.096414 | 0.018196 | -0.00031449 | 0.2568 | -0.00017979 | 13.316 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.095394 | 0.00023025 | 0.017185 | 0.0015332 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.21368 | 0.0012074 | 0.16751 | 0.004404 | 129.2556 | 0.046952 | 129.2293 | 0.0042238 | 0.23793 | 0.00041557 | 62.8272 | 0.02714 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0048192 | 15.6394 | 0.0012636
311.4 | 120.4 | 132.2813 | 0.05454 | 131.5888 | 0.043812 | 0.20015 | 0.0016399 | 5.4495 | -0.0010109 | 5.3063 | 0.040711 | 4.4765 | 0.03601 | 0.10349 | 0.0016967 | 4.1843 | 0.00032025 | 131.6461 | 0.12421 | 130.9896 | 0.0048085 | 0.19244 | 8.4239e-05 | 63.8709 | 0.032803 | 130.8234 | 0.096414 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 13.4134 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | -0.080196 | 0.0015332 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.11626 | 0.0028311 | 0.070087 | 0.004404 | 129.2556 | 0.046952 | 129.2293 | 0.0042238 | 0.14051 | 0.00041557 | 62.8272 | 0.02714 | 0.25952 | 0.0011513 | 0.11153 | -0.00034817 | 0.32251 | 0.0031962 | 15.8342 | 0.0012636
311.6 | 120.6 | 132.0865 | 0.059409 | 131.5888 | 0.048681 | 0.0053935 | 1.6859e-05 | 6.9104 | 0.00061214 | 6.7672 | 0.043958 | 5.9375 | 0.037633 | 0.20087 | 0.0016967 | 5.7427 | 0.0019433 | 131.6461 | 0.12259 | 131.087 | 0.0031849 | 0.19244 | 8.4239e-05 | 63.8709 | 0.032803 | 130.8234 | 0.096414 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 13.9978 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.095394 | 0.00023025 | 0.017185 | 0.0015332 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.11626 | 0.0028311 | 0.16751 | 0.004404 | 129.1582 | 0.045329 | 129.2293 | 0.0042238 | 0.23793 | 0.00041557 | 62.8272 | 0.02714 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 15.8342 | 0.0012636
311.8 | 120.8 | 132.1839 | 0.05454 | 131.5888 | 0.045435 | 0.10277 | 1.6859e-05 | 5.6443 | 0.00061214 | 5.5011 | 0.040711 | 4.5739 | 0.034386 | 0.10349 | 0.0016967 | 4.3791 | 0.0019433 | 131.6461 | 0.12421 | 131.087 | 0.0031849 | 0.19244 | 8.4239e-05 | 63.8709 | 0.032803 | 130.8234 | 0.09479 | 0.018196 | 0.0013085 | 0.15942 | -0.00017979 | 13.9004 | 0.0016967 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 129.1582 | 0.046952 | 129.132 | 0.0042238 | 0.23793 | 0.00041557 | 62.8272 | 0.02714 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817 | 0.32251 | 0.0048192 | 15.8342 | 0.0012636
312 | 121 | 131.9892 | 0.052917 | 131.5888 | 0.043812 | 0.0053935 | 1.6859e-05 | 5.4495 | -0.0010109 | 5.3063 | 0.040711 | 4.3791 | 0.034386 | 0.20087 | 0.0016967 | 4.1843 | 0.00032025 | 131.6461 | 0.12421 | 130.9896 | 0.0048085 | 0.19244 | 8.4239e-05 | 63.8709 | 0.032803 | 130.726 | 0.096414 | 0.018196 | 0.0013085 | 0.15942 | 0.0014439 | 14.29 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.095394 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.21368 | 0.0012074 | 0.070087 | 0.004404 | 129.1582 | 0.045329 | 129.132 | 0.0058469 | 0.23793 | 0.00041557 | 62.7297 | 0.02714 | 0.1621 | -0.00047174 | 0.20895 | 0.0012748 | 0.22513 | 0.0031962 | 15.8342 | 0.0012636
312.2 | 121.2 | 129.6516 | 0.26232 | 129.2513 | 0.25971 | 0.0053935 | 1.6859e-05 | 4.0859 | 0.00061214 | 4.0401 | 0.027725 | 2.139 | 0.019777 | 0.10349 | 0.43836 | 1.9442 | 0.00032025 | 131.4513 | 0.12421 | 130.7947 | 0.0048085 | 0.19244 | 8.4239e-05 | 63.7735 | 0.032803 | 130.6286 | 0.09479 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 14.5822 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | -0.080196 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 128.9634 | 0.045329 | 128.9372 | 0.0058469 | 0.23793 | 0.00041557 | 62.6324 | 0.02714 | 0.25952 | -0.00047174 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 16.1264 | 0.0012636
312.4 | 121.4 | 100.8223 | 1.7736 | 99.8375 | 1.7823 | 0.29757 | 0.0048865 | 2.0406 | 0.0038588 | 3.1635 | 0.029348 | 0.87284 | 0.019777 | 0.39567 | 3.7255 | 0.97026 | 0.00032025 | 128.8216 | 0.12584 | 128.3598 | 0.0048085 | 0.19244 | 8.4239e-05 | 62.6047 | 0.036049 | 128.1937 | 0.096414 | -0.1766 | -0.0019375 | 0.35418 | -0.00017979 | 98.1484 | 0.0016967 | 0.10651 | 0.001477 | 0.19277 | 0.00023025 | -0.37238 | -0.0017135 | 0.19851 | -0.00020779 | 0.37035 | 0.0015107 | -0.011119 | 0.0009884 | 0.018878 | 0.0028311 | 0.070087 | 0.006027 | 126.7233 | 0.045329 | 126.5996 | 0.0026002 | 0.14051 | -0.0012074 | 61.1714 | 0.025517 | 0.3569 | -0.00047174 | 0.014152 | -0.0019718 | 0.61469 | 0.0031962 | 15.8342 | 0.0028873
312.6 | 121.6 | 10.4383 | 0.26232 | 9.6483 | 0.26458 | 0.0053935 | 0.0016399 | 1.0667 | 0.00061214 | 1.1182 | 0.011492 | 0.77546 | 0.0067905 | 0.10349 | 0.48219 | 0.48328 | 0.00032025 | 131.4513 | 0.12584 | 130.7947 | 0.0048085 | 0.19244 | 8.4239e-05 | 63.8709 | 0.032803 | 130.6286 | 0.09479 | 0.018196 | -0.00031449 | 0.2568 | 0.0014439 | 128.5361 | 0.0033197 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | -0.080196 | 0.0015332 | 0.19851 | -0.00020779 | 0.17559 | 0.0015107 | 0.086261 | 0.0009884 | 0.21368 | 0.0012074 | 0.16751 | 0.004404 | 128.9634 | 0.046952 | 128.9372 | 0.0042238 | 0.23793 | 0.00041557 | 62.6324 | 0.025517 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748 | 0.22513 | 0.0031962 | 14.8602 | 0.0012636
312.8 | 121.8 | 2.4518 | 0.036684 | 2.0514 | 0.034072 | 0.0053935 | 1.6859e-05 | 0.67706 | 0.00061214 | 0.72864 | 0.0049989 | 0.67808 | 0.0051674 | 0.10349 | 0.050395 | 0.28848 | 0.00032025 | 131.7434 | 0.12746 | 131.087 | 0.0048085 | 0.19244 | 8.4239e-05 | 63.9683 | 0.032803 | 130.9208 | 0.096414 | 0.11562 | -0.00031449 | 0.15942 | -0.00017979 | 130.8736 | 0.0033197 | 0.2039 | -0.00014601 | 0.19277 | -0.0013928 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.21368 | 0.0012074 | 0.16751 | 0.004404 | 129.2556 | 0.046952 | 129.2293 | 0.0042238 | 0.23793 | 0.00041557 | 62.7297 | 0.02714 | 0.25952 | -0.00047174 | 0.20895 | -0.00034817 | 0.22513 | 0.0048192 | 14.9576 | 0.0028873
313 | 122 | 1.1856 | 0.015581 | 0.88265 | 0.011346 | 0.0053935 | 1.6859e-05 | 0.48226 | -0.0010109 | 0.53384 | 0.0049989 | 0.48328 | 0.0035444 | 0.10349 | 0.016306 | 0.19109 | 0.0019433 | 131.7434 | 0.12908 | 131.087 | 0.0048085 | 0.19244 | 8.4239e-05 | 63.9683 | 0.032803 | 130.9208 | 0.096414 | 0.11562 | 0.0013085 | 0.15942 | 0.0014439 | 131.1658 | 0.0033197 | 0.2039 | -0.00014601 | 0.095394 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.21368 | 0.0012074 | 0.16751 | 0.004404 | 129.2556 | 0.046952 | 129.2293 | 0.0042238 | 0.23793 | 0.00041557 | 62.8272 | 0.02714 | 0.25952 | 0.0011513 | 0.11153 | -0.00034817 | 0.22513 | 0.0031962 | 15.9316 | 0.0012636
313.2 | 122.2 | 0.79601 | 0.010711 | 0.59043 | 0.0064758 | 0.0053935 | 1.6859e-05 | 0.38488 | -0.0010109 | 0.43642 | 0.0033759 | 0.48328 | 0.0035444 | 0.10349 | 0.009813 | 0.28848 | 0.00032025 | 131.7434 | 0.12746 | 131.087 | 0.0048085 | 0.19244 | 0.0017072 | 63.9683 | 0.032803 | 130.9208 | 0.096414 | 0.018196 | 0.0013085 | 0.2568 | 0.0014439 | 131.2632 | 0.0033197 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | 0.0015107 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.070087 | 0.004404 | 129.2556 | 0.046952 | 129.3268 | 0.0058469 | 0.23793 | 0.00041557 | 62.7297 | 0.02714 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 16.1264 | 0.0012636
313.4 | 122.4 | 0.69863 | 0.0074646 | 0.49305 | 0.0048528 | 0.0053935 | 1.6859e-05 | 0.38488 | 0.00061214 | 0.33904 | 0.0033759 | 0.38586 | 0.0019208 | 0.10349 | 0.0065663 | 0.093675 | 0.00032025 | 131.7434 | 0.12746 | 131.087 | 0.0048085 | 0.19244 | 8.4239e-05 | 63.9683 | 0.032803 | 130.9208 | 0.096414 | 0.018196 | 0.0013085 | 0.15942 | -0.00017979 | 131.2632 | 0.0033197 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.21368 | 0.0012074 | 0.16751 | 0.006027 | 129.2556 | 0.046952 | 129.2293 | 0.0058469 | 0.23793 | 0.00041557 | 62.7297 | 0.02714 | 0.1621 | -0.00047174 | 0.20895 | 0.0012748 | 0.22513 | 0.0031962 | 15.8342 | 0.0012636
313.6 | 122.6 | 0.60125 | 0.0074646 | 0.39567 | 0.0048528 | 0.0053935 | 1.6859e-05 | 0.28746 | 0.00061214 | 0.43642 | 0.0017522 | 0.38586 | 0.0019208 | 0.20087 | 0.0049427 | 0.19109 | 0.00032025 | 131.7434 | 0.12908 | 131.087 | 0.0048085 | 0.19244 | 8.4239e-05 | 64.0657 | 0.032803 | 130.9208 | 0.096414 | 0.018196 | -0.00031449 | 0.2568 | 0.0014439 | 131.3606 | 0.0033197 | 0.2039 | -0.00014601 | 0.095394 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 129.2556 | 0.046952 | 129.2293 | 0.0042238 | 0.23793 | 0.00041557 | 62.7297 | 0.02714 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0048192 | 16.2238 | 0.0012636
313.8 | 122.8 | 3.8153 | -0.0055214 | -1.1627 | 0.048681 | 5.557 | -0.058421 | 66.9067 | -0.026984 | 8.8125 | 0.16733 | 36.6174 | 0.10906 | 16.0765 | 0.40914 | 17.3329 | 0.61392 | 96.6807 | 5.3999 | 94.0763 | 5.399 | 4.8675 | 0.0098236 | 15.0752 | -0.012649 | 113.779 | 1.5038 | 324.2513 | 5.4003 | 16.035 | 0.21247 | 115.2902 | 0.20461 | 0.98306 | -0.0033927 | -0.58639 | -0.051715 | 13.3605 | 0.3197 | -1.3599 | 0.035504 | 30.7581 | 0.30506 | 16.6437 | 0.39057 | 15.9919 | 0.10672 | 12.2447 | 0.93454 | 176.2981 | 0.15409 | 135.6575 | 0.082141 | 4.8156 | 0.82179 | 112.1098 | -0.11895 | 83.1439 | 0.30308 | 51.6343 | 0.24964 | 8.9908 | 0.085983 | 27.327 | 0.23826
314 | 123 | 0.60125 | 0.0058416 | 0.39567 | 0.0032298 | 0.0053935 | 1.6859e-05 | 0.38488 | -0.0010109 | 0.43642 | 0.0033759 | 0.48328 | 0.0019208 | 0.10349 | 0.0049427 | 0.19109 | 0.00032025 | 131.1591 | 0.27842 | 130.5026 | 0.0031849 | 0.19244 | 8.4239e-05 | 63.7735 | 0.037673 | 130.3364 | 0.14024 | 122.4456 | 0.26103 | 0.15942 | -0.00017979 | 130.7762 | 0.0033197 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.17559 | 0.0015107 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 129.1582 | 0.046952 | 129.132 | 0.0042238 | 0.23793 | 0.00041557 | 62.7297 | 0.02714 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 17.0029 | 0.0012636
314.2 | 123.2 | 0.60125 | 0.0058416 | 0.29825 | 0.0032298 | 0.0053935 | 1.6859e-05 | 0.38488 | 0.00061214 | 0.33904 | 0.0017522 | 0.48328 | 0.0019208 | 0.20087 | 0.0033197 | 0.19109 | 0.00032025 | 131.3539 | 0.19564 | 130.6974 | 0.0048085 | 0.19244 | 8.4239e-05 | 63.8709 | 0.034426 | 130.5312 | 0.10128 | 130.3348 | 0.11494 | 0.2568 | -0.00017979 | 130.971 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | 0.0015107 | -0.011119 | 0.0009884 | 0.21368 | 0.0012074 | 0.070087 | 0.004404 | 129.1582 | -0.0033703 | 129.0345 | 0.0042238 | 0.23793 | 0.00041557 | 62.6324 | 0.022271 | 0.25952 | 0.0011513 | -0.66763 | -0.00034817 | 0.22513 | 0.025922 | 16.9055 | 0.0012636
314.4 | 123.4 | -0.56752 | 0.00097195 | 0.29825 | -0.0097569 | 0.20015 | -0.0048528 | 0.38488 | 0.0087285 | 21.7663 | 0.33452 | 21.034 | 0.32333 | 22.4073 | 0.43836 | 18.7938 | 0.30225 | 126.484 | 0.13395 | 130.7947 | 0.094088 | -1.0737 | -0.0015388 | 62.8969 | 0.055528 | 153.9064 | 0.46165 | 151.9568 | 0.45096 | 24.8981 | 0.35856 | 152.0087 | 0.38966 | 4.0024 | -0.052091 | 1.9459 | 0.021333 | -1.6386 | 0.011273 | 0.10109 | -0.0067011 | 17.4147 | 0.22552 | 8.9493 | 0.34025 | 10.2455 | 0.17165 | 10.4915 | 0.21056 | 126.1389 | -0.024473 | 127.9632 | 0.048052 | 0.33531 | -0.03692 | 48.6072 | -0.021558 | 24.8034 | 5.4002 | 324.5394 | 0.3584 | 18.8278 | 0.20611 | 20.3144 | 0.035353
314.6 | 123.6 | 0.89343 | 0.0074646 | -0.18874 | -0.0016405 | 0.49237 | 0.047092 | 0.38488 | 0.0054818 | 5.1115 | 0.095902 | 4.8661 | 0.10581 | 3.8045 | 0.060134 | -2.6334 | 0.0051899 | 130.8669 | 0.12584 | 129.3338 | 0.12818 | 0.095061 | -0.021018 | 122.7958 | 0.034426 | 126.7328 | 0.075311 | 129.4582 | 0.12143 | 0.54898 | 0.033909 | 129.8023 | 0.0049433 | -4.0816 | -0.0050157 | 1.0694 | 0.032696 | 0.40679 | -0.019569 | 1.3672 | -0.016441 | 0.37035 | -0.022838 | -1.3747 | -0.011998 | 0.018878 | -0.021519 | -0.41689 | 0.041739 | 126.5285 | -0.00824 | 126.697 | 0.09675 | 3.452 | -0.02718 | 37.6989 | 0.044997 | 0.94126 | 4.0691 | 5.5657 | 0.0012748 | -0.26185 | -0.064981 | 14.2758 | -0.016592
314.8 | 123.8 | 0.50383 | 0.0042186 | 0.29825 | 0.0016062 | 0.10277 | 0.0016399 | 0.28746 | 0.00061214 | 0.33904 | 0.0017522 | 0.38586 | 0.00029777 | 0.20087 | 0.0033197 | 0.093675 | 0.00032025 | 131.1591 | 0.13233 | 130.4052 | 0.13142 | 0.19244 | 8.4239e-05 | 130.3927 | 0.078255 | 130.239 | 0.096414 | 131.0165 | 0.10358 | 0.15942 | 0.0014439 | 130.6788 | 0.0033197 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 0.070087 | 0.004404 | 128.9634 | 0.079417 | 128.9372 | 0.0058469 | 0.23793 | 0.00041557 | 12.2784 | 0.014154 | 2.9866 | -0.00047174 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 15.6394 | 0.0012636
315 | 124 | 0.40645 | 0.0042186 | 0.20087 | 0.0016062 | 0.10277 | 1.6859e-05 | 0.28746 | 0.00061214 | 0.24166 | 0.0017522 | 0.38586 | 0.00029777 | 0.10349 | 0.0033197 | 0.093675 | 0.00032025 | 131.1591 | 0.13233 | 130.4052 | 0.13142 | 0.19244 | 8.4239e-05 | 131.0745 | 0.079878 | 130.3364 | 0.096414 | 131.1139 | 0.10358 | 0.2568 | 0.0014439 | 130.6788 | 0.0033197 | 0.2039 | -0.00014601 | 0.19277 | -0.0013928 | 0.017185 | 0.0015332 | 0.19851 | 0.0014152 | 0.17559 | 0.0015107 | 0.086261 | 0.0009884 | 0.21368 | 0.0012074 | 0.16751 | 0.0027804 | 128.9634 | 0.082664 | 128.8398 | 0.0042238 | 0.23793 | 0.00041557 | 8.9669 | 0.0092845 | 8.5382 | 0.0011513 | 0.11153 | -0.00034817 | 0.32251 | 0.0031962 | 15.9316 | 0.0012636
315.2 | 124.2 | 0.40645 | 0.0042186 | 0.20087 | 0.0016062 | -0.092027 | 1.6859e-05 | 0.28746 | -0.0010109 | 0.24166 | 0.00012922 | 0.28848 | 0.0019208 | 0.20087 | 0.0016967 | 0.093675 | 0.00032025 | 131.0617 | 0.13233 | 130.4052 | 0.13142 | 0.095061 | 8.4239e-05 | 131.1719 | 0.079878 | 130.3364 | 0.096414 | 131.1139 | 0.10358 | 0.2568 | -0.00017979 | 130.6788 | 0.0033197 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | 0.0015107 | -0.011119 | -0.0006346 | 0.21368 | 0.0012074 | 0.070087 | 0.004404 | 128.9634 | 0.082664 | 128.9372 | 0.0058469 | 0.23793 | 0.00041557 | 8.6747 | 0.0044148 | 8.6356 | 0.0011513 | 0.20895 | 0.0012748 | 0.22513 | 0.0031962 | 15.6394 | 0.0012636
315.4 | 124.4 | 0.30903 | 0.0042186 | 0.20087 | -1.6843e-05 | 0.0053935 | 1.6859e-05 | 0.19008 | 0.00061214 | 0.24166 | 0.0017522 | 0.28848 | 0.0019208 | 0.20087 | 0.0033197 | 0.093675 | 0.00032025 | 131.0617 | 0.13233 | 130.4052 | 0.13305 | 0.19244 | 0.0017072 | 131.0745 | 0.079878 | 130.239 | 0.09479 | 131.1139 | 0.10358 | 0.2568 | -0.00017979 | 130.6788 | 0.0033197 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | 0.0015107 | -0.011119 | 0.0009884 | 0.21368 | 0.0012074 | 0.070087 | 0.004404 | 128.8661 | 0.082664 | 128.8398 | 0.0058469 | 0.23793 | 0.00041557 | 8.6747 | 0.0044148 | 8.733 | 0.014138 | 0.20895 | -0.00034817 | 0.22513 | 0.0048192 | 15.3472 | 0.0012636
315.6 | 124.6 | 0.40645 | 0.0042186 | 0.10345 | 0.0016062 | 0.0053935 | 1.6859e-05 | 0.28746 | -0.0010109 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 0.0033197 | 0.093675 | 0.00032025 | 131.0617 | 0.13233 | 130.5026 | 0.13142 | 0.19244 | 8.4239e-05 | 131.1719 | 0.078255 | 130.3364 | 0.09479 | 131.1139 | 0.10358 | 0.15942 | 0.0014439 | 130.6788 | 0.0033197 | 0.30132 | -0.00014601 | 0.29015 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | 0.086261 | -0.0006346 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 128.8661 | 0.082664 | 128.9372 | 0.0058469 | 0.23793 | 0.00041557 | 8.5773 | 0.0027911 | 8.733 | 0.067706 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 15.3472 | 0.0012636
315.8 | 124.8 | 0.30903 | 0.0042186 | 0.10345 | -1.6843e-05 | 0.0053935 | 1.6859e-05 | 0.28746 | 0.00061214 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.20087 | 0.0033197 | 0.093675 | 0.00032025 | 131.0617 | 0.13233 | 130.4052 | 0.13305 | 0.19244 | 8.4239e-05 | 131.1719 | 0.079878 | 130.239 | 0.096414 | 131.1139 | 0.10358 | 0.2568 | 0.0014439 | 130.6788 | 0.0033197 | 0.2039 | 0.001477 | 0.19277 | 0.00023025 | 0.017185 | 0.0015332 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 128.8661 | 0.082664 | 128.9372 | 0.0058469 | 0.23793 | 0.00041557 | 8.6747 | 0.0027911 | 8.733 | 0.070952 | 0.20895 | 0.0012748 | 0.22513 | 0.0031962 | 16.029 | 0.0012636
316 | 125 | 0.30903 | 0.0042186 | 0.20087 | 0.0016062 | 0.0053935 | 1.6859e-05 | 0.19008 | 0.00061214 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.20087 | 0.0033197 | 0.093675 | 0.00032025 | 130.9643 | 0.13233 | 130.4052 | 0.13305 | 0.19244 | 8.4239e-05 | 131.1719 | 0.078255 | 130.1416 | 0.096414 | 131.1139 | 0.10358 | 0.15942 | -0.00017979 | 130.6788 | 0.0033197 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | 0.0015332 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 128.8661 | 0.082664 | 128.8398 | 0.0058469 | 0.23793 | 0.00041557 | 8.6747 | 0.0011681 | 8.733 | 0.070952 | 0.20895 | 0.0012748 | 0.22513 | 0.0031962 | 16.3212 | 0.0012636
316.2 | 125.2 | 0.30903 | 0.0042186 | 0.20087 | 0.0016062 | 0.0053935 | 1.6859e-05 | 0.19008 | 0.00061214 | 0.24166 | 0.0017522 | 0.28848 | 0.00029777 | 0.10349 | 0.0033197 | -0.0037056 | 0.00032025 | 130.9643 | 0.13233 | 130.4052 | 0.13305 | 0.095061 | 8.4239e-05 | 131.1719 | 0.079878 | 130.239 | 0.09479 | 131.0165 | 0.10358 | 0.15942 | 0.0014439 | 130.6788 | 0.0033197 | 0.2039 | -0.00014601 | 0.095394 | 0.00023025 | 0.017185 | 0.0015332 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 128.8661 | 0.082664 | 128.8398 | 0.0058469 | 0.23793 | 0.00041557 | 8.6747 | 0.0027911 | 8.8304 | 0.070952 | 0.20895 | 0.0012748 | 0.22513 | 0.0048192 | 16.029 | 0.0012636
316.4 | 125.4 | 0.30903 | 0.0042186 | 0.20087 | -1.6843e-05 | 0.10277 | 1.6859e-05 | 0.19008 | 0.00061214 | 0.24166 | 0.00012922 | 0.19109 | 0.00029777 | 0.10349 | 0.0016967 | -0.0037056 | 0.00032025 | 100.2844 | 1.8108 | 100.5044 | 1.7726 | 0.19244 | 8.4239e-05 | 101.0764 | 0.063645 | 99.8513 | 0.076934 | 100.3366 | 0.084096 | 0.15942 | 2.0078 | 100.5833 | 0.0016967 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.21368 | 0.0012074 | 0.070087 | 0.006027 | 126.3337 | 0.084287 | 126.3074 | 0.0058469 | 0.04313 | 0.0020392 | 8.5773 | 0.0011681 | 8.6356 | 0.069329 | 0.20895 | -0.0019718 | 0.22513 | -5.0495e-05 | 14.6654 | 0.0012636
316.6 | 125.6 | 0.21165 | 0.002595 | 0.10345 | 0.0016062 | 0.0053935 | 1.6859e-05 | 0.19008 | -0.0010109 | 0.24166 | 0.0017522 | 0.28848 | 0.0019208 | 0.10349 | 0.0033197 | 0.093675 | 0.00032025 | 9.316 | 0.27355 | 9.5361 | 0.27103 | 0.19244 | 8.4239e-05 | 10.3028 | 0.019816 | 9.4673 | 0.02499 | 9.6604 | 0.024035 | 0.15942 | 0.49167 | 9.7123 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.095394 | 0.00023025 | -0.080196 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.21368 | 0.0012074 | 0.16751 | 0.004404 | 128.6713 | 0.082664 | 128.645 | 0.0058469 | 0.14051 | 0.00041557 | 8.5773 | 0.0011681 | 8.733 | 0.070952 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 11.7435 | 0.0012636
316.8 | 125.8 | 0.30903 | 0.0042186 | 0.10345 | -1.6843e-05 | 0.0053935 | 1.6859e-05 | 0.19008 | 0.00061214 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.20087 | 0.0016967 | -0.0037056 | 0.0019433 | 2.2061 | 0.034931 | 2.0365 | 0.03565 | 0.19244 | 8.4239e-05 | 2.2189 | 0.0084533 | 1.8704 | 0.012003 | 1.9661 | 0.0094249 | 0.15942 | 0.050142 | 2.018 | 7.2982e-05 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 0.070087 | 0.004404 | 128.9634 | 0.082664 | 128.9372 | 0.0058469 | 0.23793 | 0.00041557 | 8.5773 | 0.0011681 | 8.733 | 0.070952 | 0.20895 | -0.00034817 | 0.32251 | 0.0048192 | 11.4513 | -0.0003594
317 | 126 | 0.30903 | 0.0042186 | 0.10345 | -1.6843e-05 | 0.0053935 | 1.6859e-05 | 0.19008 | 0.00061214 | 0.24166 | 0.0017522 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | -0.0037056 | 0.00032025 | 1.0373 | 0.012205 | 0.9652 | 0.011301 | 0.19244 | 8.4239e-05 | 1.0501 | 0.0052073 | 0.89646 | 0.0087568 | 0.79736 | 0.0078019 | 0.15942 | 0.01443 | 0.94667 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 128.9634 | 0.082664 | 129.0345 | 0.0074705 | 0.23793 | 0.00041557 | 8.6747 | 0.0011681 | 8.733 | 0.070952 | 0.20895 | 0.0012748 | 0.22513 | 0.0031962 | 11.5487 | 0.0012636
317.2 | 126.2 | 0.30903 | 0.0042186 | 0.10345 | -1.6843e-05 | 0.0053935 | 1.6859e-05 | 0.19008 | 0.00061214 | 0.24166 | 0.0017522 | 0.38586 | 0.00029777 | 0.10349 | 0.0016967 | -0.0037056 | 0.00032025 | 0.74513 | 0.0073357 | 0.67302 | 0.0064315 | 0.19244 | 8.4239e-05 | 0.66054 | 0.0035836 | 0.50686 | 0.0071332 | 0.6026 | 0.0045552 | 0.15942 | 0.0079366 | 0.55707 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.21368 | 0.0012074 | 0.16751 | 0.004404 | 128.9634 | 0.082664 | 128.9372 | 0.0074705 | 0.23793 | 0.00041557 | 8.6747 | 0.0011681 | 8.8304 | 0.070952 | 0.20895 | 0.0012748 | 0.32251 | 0.0031962 | 11.3539 | -0.0003594
317.4 | 126.4 | 0.30903 | 0.0042186 | 0.10345 | -1.6843e-05 | 0.0053935 | 1.6859e-05 | 0.19008 | 0.00061214 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | -0.0037056 | 0.00032025 | 0.64775 | 0.0040891 | 0.47822 | 0.0048085 | 0.19244 | 8.4239e-05 | 0.56316 | 0.0035836 | 0.40948 | 0.0055102 | 0.4078 | 0.0029322 | 0.15942 | 0.0063136 | 0.45969 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | 0.0015332 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.21368 | 0.0012074 | 0.070087 | 0.004404 | 129.0608 | 0.084287 | 129.0345 | 0.0074705 | 0.23793 | 0.00041557 | 8.6747 | 0.0011681 | 8.8304 | 0.070952 | 0.20895 | 0.0012748 | 0.32251 | 0.0031962 | 11.3539 | 0.0012636
317.6 | 126.6 | 0.30903 | 0.0042186 | 0.10345 | 0.0016062 | 0.0053935 | 1.6859e-05 | 0.19008 | 0.00061214 | 0.24166 | 0.0017522 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | 0.093675 | 0.00032025 | 0.64775 | 0.0040891 | 0.47822 | 0.0031849 | 0.19244 | 8.4239e-05 | 0.56316 | 0.0019606 | 0.31206 | 0.0055102 | 0.31038 | 0.0029322 | 0.15942 | 0.0046906 | 0.36227 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.095394 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | -0.0006346 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 128.9634 | 0.082664 | 128.9372 | 0.0074705 | 0.23793 | 0.00041557 | 8.6747 | 0.0011681 | 8.8304 | 0.070952 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 11.2565 | 0.0012636
317.8 | 126.8 | 0.30903 | 0.0042186 | 0.10345 | -1.6843e-05 | 0.0053935 | 1.6859e-05 | 0.28746 | 0.00061214 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | -0.0037056 | 0.00032025 | 0.45295 | 0.0040891 | 0.3808 | 0.0031849 | 0.19244 | 8.4239e-05 | 0.46574 | 0.0019606 | 0.21468 | 0.0038865 | 0.31038 | 0.0029322 | 0.15942 | 0.0046906 | 0.36227 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.27297 | -0.00011232 | -0.011119 | 0.0009884 | 0.21368 | 0.0028311 | 0.070087 | 0.004404 | 128.9634 | 0.082664 | 128.9372 | 0.0090935 | 0.14051 | 0.00041557 | 8.6747 | 0.0011681 | 8.8304 | 0.070952 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 10.9644 | 0.0012636
318 | 127 | 0.30903 | 0.0042186 | 0.10345 | 0.0016062 | 0.0053935 | 1.6859e-05 | 0.19008 | 0.00061214 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | -0.0037056 | 0.00032025 | 0.45295 | 0.0024661 | 0.3808 | 0.0015619 | 0.19244 | 8.4239e-05 | 0.36836 | 0.0019606 | 0.21468 | 0.0055102 | 0.31038 | 0.0013085 | 0.15942 | 0.0030669 | 0.26489 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | 0.0015332 | 0.29589 | 0.0014152 | 0.27297 | 0.0015107 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 128.9634 | 0.082664 | 128.9372 | 0.0090935 | 0.23793 | 0.00041557 | 8.6747 | 0.0011681 | 8.8304 | 0.070952 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 10.9644 | 0.0012636
318.2 | 127.2 | 0.30903 | 0.0042186 | 0.10345 | -1.6843e-05 | 0.0053935 | 1.6859e-05 | 0.19008 | 0.00061214 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | -0.0037056 | 0.00032025 | 0.45295 | 0.0024661 | 0.28342 | 0.0015619 | 0.19244 | 8.4239e-05 | 0.36836 | 0.0019606 | 0.11726 | 0.0038865 | 0.213 | 0.0013085 | 0.15942 | 0.0030669 | 0.26489 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.27297 | -0.00011232 | -0.011119 | 0.0009884 | 0.21368 | 0.0012074 | 0.070087 | 0.004404 | 128.9634 | 0.082664 | 128.9372 | 0.0090935 | 0.23793 | 0.00041557 | 8.6747 | 0.0011681 | 8.9278 | 0.072575 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 10.8669 | 0.0012636
318.4 | 127.4 | 0.30903 | 0.0042186 | 0.10345 | -1.6843e-05 | 0.0053935 | 1.6859e-05 | 0.19008 | 0.00061214 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.20087 | 0.0016967 | -0.0037056 | 0.0019433 | 0.45295 | 0.0024661 | 0.28342 | 0.0015619 | 0.19244 | 8.4239e-05 | 0.36836 | 0.0019606 | 0.11726 | 0.0038865 | 0.213 | 0.0013085 | 0.15942 | 0.0014439 | 0.26489 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | 0.0015332 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.21368 | 0.0012074 | 0.070087 | 0.004404 | 129.0608 | 0.08104 | 129.0345 | 0.0090935 | 0.23793 | 0.00041557 | 8.7721 | 0.0011681 | 8.9278 | 0.072575 | 0.20895 | -0.00034817 | 0.32251 | 0.0048192 | 10.9644 | 0.0012636
318.6 | 127.6 | 0.21165 | 0.0042186 | 0.10345 | -1.6843e-05 | 0.0053935 | 1.6859e-05 | 0.19008 | 0.00061214 | 0.14424 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | -0.0037056 | 0.00032025 | 0.45295 | 0.0024661 | 0.28342 | 0.0015619 | 0.19244 | 0.0017072 | 0.36836 | 0.00033696 | 0.11726 | 0.0038865 | 0.213 | 0.0013085 | 0.2568 | 0.0014439 | 0.26489 | 7.2982e-05 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.29589 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0028311 | 0.16751 | 0.004404 | 128.9634 | 0.077794 | 128.9372 | 0.010717 | 0.23793 | 0.00041557 | 8.7721 | 0.0011681 | 8.9278 | 0.072575 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 10.9644 | 0.0012636
318.8 | 127.8 | 0.30903 | 0.002595 | 0.10345 | -1.6843e-05 | 0.0053935 | 1.6859e-05 | 0.19008 | 0.00061214 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.20087 | 0.0016967 | -0.0037056 | 0.00032025 | 0.45295 | 0.00084239 | 0.28342 | 0.0015619 | 0.19244 | 8.4239e-05 | 0.27094 | 0.0019606 | 0.11726 | 0.0055102 | 0.213 | 0.0013085 | 0.2568 | 0.0014439 | 0.16751 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 128.9634 | 0.07617 | 128.9372 | 0.013963 | 0.23793 | 0.00041557 | 8.7721 | 0.0011681 | 8.9278 | 0.072575 | 0.11153 | 0.0012748 | 0.22513 | 0.0031962 | 11.0617 | 0.0012636
319 | 128 | 0.30903 | 0.0042186 | 0.10345 | -1.6843e-05 | 0.0053935 | 1.6859e-05 | 0.19008 | 0.00061214 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | -0.0037056 | 0.00032025 | 0.35553 | 0.0024661 | 0.28342 | 0.0015619 | 0.095061 | 8.4239e-05 | 0.27094 | 0.0019606 | 0.11726 | 0.0038865 | 0.213 | 0.0013085 | 0.15942 | 0.0014439 | 0.26489 | -0.00155 | 0.2039 | -0.00014601 | 0.095394 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.29589 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.21368 | 0.0012074 | 0.070087 | 0.0027804 | 128.9634 | 0.068054 | 128.9372 | 0.020457 | 0.23793 | 0.00041557 | 8.7721 | 0.0011681 | 8.9278 | 0.070952 | 0.20895 | -0.00034817 | 0.22513 | 0.0048192 | 11.0617 | -0.0003594
319.2 | 128.2 | 0.21165 | 0.002595 | 0.10345 | -1.6843e-05 | 0.0053935 | 1.6859e-05 | 0.19008 | 0.00061214 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | -0.0037056 | 0.00032025 | 0.35553 | 0.00084239 | 0.18604 | 0.0015619 | 0.19244 | 8.4239e-05 | 0.27094 | 0.0019606 | 0.11726 | 0.0022635 | 0.11562 | 0.0013085 | 0.15942 | 0.0014439 | 0.26489 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.006027 | 128.9634 | 0.059938 | 128.9372 | 0.033443 | 0.23793 | 0.00041557 | 8.7721 | 0.0011681 | 8.9278 | 0.070952 | 0.20895 | -0.00034817 | 0.22513 | 0.0031962 | 11.1591 | 0.0012636
319.4 | 128.4 | 0.30903 | 0.0042186 | 0.10345 | -1.6843e-05 | 0.0053935 | 1.6859e-05 | 0.19008 | 0.00061214 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | -0.0037056 | 0.00032025 | 0.45295 | 0.00084239 | 0.18604 | -6.1803e-05 | 0.19244 | 8.4239e-05 | 0.27094 | 0.00033696 | 0.01988 | 0.0022635 | 0.11562 | 0.0013085 | 0.15942 | 0.0014439 | 0.16751 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.095394 | 0.00023025 | -0.080196 | 0.0015332 | 0.29589 | -0.00020779 | 0.17559 | 0.0015107 | -0.011119 | 0.0009884 | 0.21368 | 0.0012074 | 0.070087 | 0.004404 | 128.9634 | 0.059938 | 128.9372 | 0.038312 | 0.23793 | 0.00041557 | 8.7721 | 0.0011681 | 8.8304 | 0.072575 | 0.20895 | -0.00034817 | 0.32251 | 0.0048192 | 8.919 | 0.0012636
319.6 | 128.6 | 0.30903 | 0.0042186 | 0.10345 | -1.6843e-05 | 0.0053935 | 1.6859e-05 | 0.19008 | 0.00061214 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | -0.0037056 | 0.00032025 | 0.35553 | 0.00084239 | 0.28342 | 0.0015619 | 0.19244 | 8.4239e-05 | 0.17356 | 0.0019606 | 0.01988 | 0.0038865 | 0.11562 | 0.0013085 | 0.15942 | 0.0030669 | 0.16751 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.21368 | 0.0012074 | 0.070087 | 0.004404 | 128.9634 | 0.058315 | 128.9372 | 0.038312 | 0.23793 | 0.00041557 | 8.7721 | 0.0011681 | 9.0252 | 0.072575 | 0.11153 | -0.00034817 | 0.32251 | 0.0031962 | 2.5883 | 0.0012636
319.8 | 128.8 | 0.21165 | 0.002595 | 0.10345 | -1.6843e-05 | 0.0053935 | 1.6859e-05 | 0.19008 | 0.00061214 | 0.24166 | 0.00012922 | 0.19109 | 0.00029777 | 0.20087 | 0.0016967 | -0.0037056 | 0.00032025 | 0.35553 | 0.0024661 | 0.18604 | -6.1803e-05 | 0.19244 | 8.4239e-05 | 0.27094 | 0.0019606 | 0.01988 | 0.0022635 | 0.213 | 0.0013085 | 0.15942 | 0.0014439 | 0.16751 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | 0.0015332 | 0.19851 | 0.0014152 | 0.27297 | -0.00011232 | 0.086261 | 0.0009884 | 0.21368 | 0.0012074 | 0.16751 | 0.004404 | 128.9634 | 0.055068 | 128.9372 | 0.038312 | 0.23793 | 0.00041557 | 8.7721 | 0.0011681 | 8.9278 | 0.070952 | 0.20895 | 0.0045215 | 0.22513 | 0.0031962 | 1.9065 | 0.0012636
320 | 129 | 0.30903 | 0.002595 | 0.10345 | 0.0016062 | 0.0053935 | 1.6859e-05 | 0.19008 | 0.00061214 | 0.24166 | 0.00012922 | 0.28848 | 0.0019208 | 0.10349 | 0.0033197 | -0.0037056 | 0.00032025 | 0.35553 | 0.00084239 | 0.28342 | -6.1803e-05 | 0.19244 | 0.0017072 | 0.27094 | 0.00033696 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | 0.0014439 | 0.16751 | 7.2982e-05 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | 0.0015332 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | -0.0006346 | 0.21368 | 0.0012074 | 0.16751 | 0.004404 | 128.3791 | 0.10052 | 128.3528 | 0.085387 | 0.23793 | 0.00041557 | 8.4799 | 0.0011681 | 8.6356 | 0.074199 | 117.4744 | 0.0028978 | 0.22513 | 0.0031962 | 118.2953 | 0.0045103
320.2 | 129.2 | 0.21165 | 0.0042186 | 0.10345 | -1.6843e-05 | 0.0053935 | 1.6859e-05 | 0.19008 | 0.00061214 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | -0.0037056 | 0.00032025 | 0.35553 | 0.00084239 | 0.18604 | -6.1803e-05 | 0.19244 | 8.4239e-05 | 0.27094 | 0.00033696 | 0.11726 | 0.0022635 | 0.11562 | -0.00031449 | 0.15942 | 0.0014439 | 0.16751 | 7.2982e-05 | 0.2039 | 0.001477 | 0.095394 | 0.00023025 | 0.017185 | 0.0015332 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 128.4765 | 0.09565 | 128.4502 | 0.082141 | 0.23793 | 0.00041557 | 8.5773 | 0.0011681 | 8.733 | 0.074199 | 127.1166 | 0.0028978 | 0.22513 | 0.0048192 | 127.4506 | 0.0028873
320.4 | 129.4 | 0.21165 | 0.002595 | 0.0060652 | -1.6843e-05 | 0.0053935 | 1.6859e-05 | 0.19008 | 0.00061214 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | -0.0037056 | 0.00032025 | 0.35553 | 0.00084239 | 0.18604 | -6.1803e-05 | 0.19244 | 8.4239e-05 | 0.27094 | 0.00033696 | 0.01988 | 0.0038865 | 0.11562 | 0.0013085 | 0.15942 | 0.0014439 | 0.16751 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.095394 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | 0.086261 | -0.0006346 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 128.5738 | 0.09565 | 128.4502 | 0.082141 | 0.23793 | 0.00041557 | 8.5773 | 0.0011681 | 8.733 | 0.074199 | 128.0906 | 0.0077682 | 0.22513 | 0.0031962 | 128.3272 | 0.0028873
320.6 | 129.6 | 0.21165 | 0.002595 | 0.10345 | -1.6843e-05 | 0.0053935 | 1.6859e-05 | 0.19008 | 0.00061214 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | -0.0037056 | 0.00032025 | 0.35553 | 0.00084239 | 0.18604 | 0.0015619 | 0.19244 | 8.4239e-05 | 0.17356 | 0.00033696 | 0.01988 | 0.0022635 | 0.11562 | 0.0013085 | 0.15942 | -0.00017979 | 0.16751 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | 0.0015332 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.21368 | 0.0028311 | 0.16751 | 0.004404 | 128.4765 | 0.09565 | 128.5476 | 0.082141 | 0.23793 | 0.00041557 | 8.5773 | 0.0011681 | 8.733 | 0.074199 | 128.188 | 0.087309 | 0.22513 | 0.0048192 | 128.4246 | 0.0045103
320.8 | 129.8 | 0.21165 | 0.0042186 | 0.10345 | -1.6843e-05 | 0.0053935 | 1.6859e-05 | 0.19008 | 0.00061214 | 0.24166 | -0.0014944 | 0.19109 | 0.00029777 | 0.20087 | 0.0016967 | 0.093675 | 0.00032025 | 0.35553 | 0.00084239 | 0.18604 | 0.0015619 | 0.19244 | 8.4239e-05 | 0.17356 | 0.00033696 | 0.01988 | 0.0022635 | 0.11562 | 0.0013085 | 0.15942 | 0.0014439 | 0.16751 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | -0.080196 | 0.0015332 | 0.19851 | -0.00020779 | 0.27297 | 0.0015107 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 128.4765 | 0.09565 | 128.5476 | 0.082141 | 0.23793 | 0.00041557 | 8.5773 | 0.0011681 | 8.733 | 0.074199 | 128.2854 | 0.093801 | 0.22513 | 0.0031962 | 128.522 | 0.0028873
321 | 130 | 0.21165 | 0.0042186 | 0.10345 | -1.6843e-05 | 0.10277 | 1.6859e-05 | 0.19008 | -0.0010109 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | -0.0037056 | 0.00032025 | 0.25815 | 0.00084239 | 0.18604 | -6.1803e-05 | 0.19244 | 0.0017072 | 0.17356 | 0.00033696 | 0.01988 | 0.0022635 | 0.11562 | 0.0013085 | 0.15942 | 0.0014439 | 0.16751 | 7.2982e-05 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | 0.0015332 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | 0.086261 | -0.0006346 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 128.4765 | 0.094027 | 128.4502 | 0.082141 | 0.23793 | 0.00041557 | 8.5773 | -0.00045489 | 8.8304 | 0.074199 | 128.2854 | 0.093801 | 0.22513 | 0.0031962 | 128.522 | 0.0045103
321.2 | 130.2 | 0.21165 | 0.0042186 | 0.10345 | -1.6843e-05 | 0.0053935 | 1.6859e-05 | 0.19008 | 0.00061214 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 0.0033197 | -0.0037056 | 0.00032025 | 0.35553 | 0.00084239 | 0.088619 | 0.0015619 | 0.19244 | 8.4239e-05 | 0.17356 | 0.00033696 | 0.01988 | 0.0022635 | 0.11562 | 0.0013085 | 0.15942 | 0.0014439 | 0.16751 | 7.2982e-05 | 0.2039 | 0.001477 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.070087 | 0.004404 | 54.2603 | 3.0029 | 54.9158 | 2.7946 | 0.33531 | 0.00041557 | 4.7788 | 0.0011681 | 5.0319 | 0.048226 | 53.5822 | 0.072699 | 0.22513 | 0.0031962 | 54.111 | 0.0012636
321.4 | 130.4 | 0.21165 | 0.0042186 | 0.10345 | -1.6843e-05 | 0.0053935 | 1.6859e-05 | 0.19008 | 0.00061214 | 0.24166 | 0.00012922 | 0.19109 | 0.00029777 | 0.10349 | 0.0016967 | -0.0037056 | 0.00032025 | 0.25815 | 0.00084239 | 0.18604 | 0.0015619 | 0.19244 | 8.4239e-05 | 0.27094 | 0.00033696 | 0.01988 | 0.0022635 | 0.11562 | 0.0013085 | 0.15942 | 0.0014439 | 0.16751 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | -0.080196 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 6.1464 | 0.20928 | 6.5097 | 0.19902 | 0.14051 | -0.0012074 | 1.2725 | -0.00045489 | 1.3309 | 0.015761 | 5.9553 | 0.019131 | 0.22513 | 0.0031962 | 6.1919 | 0.0012636
321.6 | 130.6 | 0.21165 | 0.0042186 | 0.10345 | 0.0016062 | 0.0053935 | 1.6859e-05 | 0.19008 | 0.00061214 | 0.24166 | 0.00012922 | 0.19109 | 0.00029777 | 0.20087 | 0.0016967 | -0.0037056 | 0.00032025 | 0.35553 | 0.00084239 | 0.18604 | -6.1803e-05 | 0.19244 | 8.4239e-05 | 0.17356 | 0.0019606 | 0.01988 | 0.0038865 | 0.11562 | -0.00031449 | 0.15942 | 0.0014439 | 0.070087 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.17559 | 0.0015107 | -0.011119 | 0.0009884 | 0.11626 | 0.0028311 | 0.070087 | 0.004404 | 1.7636 | 0.030719 | 1.7373 | 0.030196 | 0.23793 | 0.00041557 | 0.68819 | 0.0011681 | 0.7465 | 0.0076446 | 1.5725 | 0.0093912 | 0.22513 | 0.0031962 | 1.6143 | 0.0012636
321.8 | 130.8 | 0.30903 | 0.002595 | 0.0060652 | -1.6843e-05 | 0.0053935 | 1.6859e-05 | 0.19008 | 0.00061214 | 0.14424 | 0.00012922 | 0.28848 | 0.00029777 | 0.20087 | 0.0016967 | -0.0037056 | 0.00032025 | 0.35553 | 0.00084239 | 0.088619 | -6.1803e-05 | 0.19244 | 8.4239e-05 | 0.17356 | 0.00033696 | 0.01988 | 0.0022635 | 0.11562 | 0.0013085 | 0.15942 | 0.0014439 | 0.16751 | 0.0016967 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.21368 | 0.0012074 | 0.16751 | 0.004404 | 0.88702 | 0.011239 | 0.95811 | 0.010717 | 0.23793 | -0.0012074 | 0.49339 | -0.00045489 | 0.5517 | 0.0043979 | 0.89073 | 0.0061445 | 0.22513 | 0.0048192 | 0.73772 | 0.0012636
322 | 131 | 0.21165 | 0.0042186 | 0.0060652 | -1.6843e-05 | 0.0053935 | 1.6859e-05 | 0.19008 | 0.00061214 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | -0.0037056 | 0.0019433 | 0.35553 | 0.00084239 | 0.18604 | 0.0015619 | 0.19244 | 8.4239e-05 | 0.17356 | 0.00033696 | 0.01988 | 0.0022635 | 0.11562 | 0.0013085 | 0.2568 | 0.0014439 | 0.070087 | 0.0016967 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.17559 | 0.0015107 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 0.69222 | 0.0079928 | 0.66593 | 0.0074705 | 0.23793 | 0.00041557 | 0.39597 | 0.0011681 | 0.5517 | 0.0043979 | 0.69593 | 0.0045215 | 0.32251 | 0.0031962 | 0.54291 | -0.0003594
322.2 | 131.2 | 0.30903 | 0.0042186 | 0.10345 | 0.0016062 | 0.0053935 | 1.6859e-05 | 0.19008 | 0.00061214 | 0.14424 | 0.00012922 | 0.19109 | 0.00029777 | 0.20087 | 0.0016967 | -0.0037056 | 0.0019433 | 0.25815 | 0.00084239 | 0.088619 | -6.1803e-05 | 0.19244 | 8.4239e-05 | 0.17356 | 0.00033696 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.2568 | -0.00017979 | 0.16751 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | 0.0015332 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.21368 | 0.0012074 | 0.070087 | 0.004404 | 0.49742 | 0.0047461 | 0.56855 | 0.0058469 | 0.23793 | 0.00041557 | 0.29859 | 0.0011681 | 0.3569 | 0.0027749 | 0.50113 | 0.0028978 | 0.22513 | 0.0031962 | 0.44553 | 0.0012636
322.4 | 131.4 | 0.21165 | 0.002595 | 0.10345 | -1.6843e-05 | 0.0053935 | 1.6859e-05 | 0.19008 | -0.0010109 | 0.24166 | 0.0017522 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | 0.093675 | 0.00032025 | 0.25815 | 0.00084239 | 0.18604 | -6.1803e-05 | 0.19244 | 8.4239e-05 | 0.17356 | 0.00033696 | 0.01988 | 0.0022635 | 0.11562 | -0.00031449 | 0.15942 | 0.0014439 | 0.070087 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.095394 | 0.00023025 | -0.080196 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0028311 | 0.070087 | 0.004404 | 0.49742 | 0.0047461 | 0.56855 | 0.0042238 | 0.23793 | -0.0012074 | 0.39597 | 0.0011681 | 0.3569 | 0.0027749 | 0.50113 | 0.0028978 | 0.22513 | 0.0031962 | 0.34811 | 0.0012636
322.6 | 131.6 | 0.30903 | 0.0042186 | 0.10345 | 0.0016062 | 0.0053935 | 1.6859e-05 | 0.19008 | 0.00061214 | 0.24166 | 0.00012922 | 0.19109 | 0.00029777 | 0.20087 | 0.0016967 | -0.0037056 | 0.00032025 | 0.25815 | 0.00084239 | 0.18604 | -6.1803e-05 | 0.19244 | 8.4239e-05 | 0.17356 | 0.00033696 | 0.01988 | 0.0038865 | 0.11562 | 0.0013085 | 0.15942 | 0.0014439 | 0.16751 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.21368 | 0.0012074 | 0.070087 | 0.004404 | 0.30262 | 0.0031231 | 0.47113 | 0.0026002 | 0.23793 | 0.00041557 | 0.29859 | 0.0011681 | 0.25952 | 0.0011513 | 0.40375 | 0.0028978 | 0.22513 | 0.0048192 | 0.25073 | 0.0012636
322.8 | 131.8 | 0.21165 | 0.002595 | 0.10345 | 0.0016062 | 0.0053935 | 1.6859e-05 | 0.19008 | 0.00061214 | 0.24166 | 0.00012922 | 0.28848 | -0.0013259 | 0.20087 | 0.0016967 | -0.0037056 | 0.00032025 | 0.25815 | 0.00084239 | 0.18604 | -6.1803e-05 | 0.19244 | 8.4239e-05 | 0.17356 | 0.00033696 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.2568 | -0.00017979 | 0.16751 | 7.2982e-05 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | -0.011119 | -0.0006346 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 0.30262 | 0.0031231 | 0.47113 | 0.0026002 | 0.23793 | 0.00041557 | 0.29859 | 0.0011681 | 0.25952 | 0.0027749 | 0.40375 | 0.0028978 | 0.32251 | 0.0031962 | 0.25073 | 0.0012636
323 | 132 | 0.21165 | 0.002595 | 0.10345 | -1.6843e-05 | 0.0053935 | 1.6859e-05 | 0.092701 | 0.00061214 | 0.14424 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | -0.0037056 | 0.00032025 | 0.25815 | 0.00084239 | 0.18604 | -6.1803e-05 | 0.19244 | 8.4239e-05 | 0.17356 | 0.00033696 | 0.01988 | 0.0022635 | 0.11562 | -0.00031449 | 0.15942 | -0.00017979 | 0.16751 | 7.2982e-05 | 0.2039 | 0.001477 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.21368 | 0.0012074 | 0.16751 | 0.004404 | 0.40004 | 0.0031231 | 0.37375 | 0.0026002 | 0.23793 | 0.00041557 | 0.29859 | 0.0011681 | 0.3569 | 0.0011513 | 0.30633 | 0.0028978 | 0.22513 | 0.0048192 | 0.15335 | 0.0012636
323.2 | 132.2 | 0.21165 | 0.0042186 | 0.0060652 | -1.6843e-05 | -0.092027 | 1.6859e-05 | 0.19008 | 0.00061214 | 0.14424 | 0.00012922 | 0.19109 | 0.00029777 | 0.10349 | 0.0016967 | -0.0037056 | 0.00032025 | 0.35553 | 0.00084239 | 0.18604 | 0.0015619 | 0.19244 | 8.4239e-05 | 0.17356 | 0.00033696 | 0.01988 | 0.0022635 | 0.11562 | -0.00031449 | 0.15942 | 0.0014439 | 0.16751 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 0.30262 | 0.0031231 | 0.37375 | 0.0026002 | 0.23793 | 0.00041557 | 0.20121 | 0.0011681 | 0.3569 | 0.0011513 | 0.30633 | 0.0012748 | 0.22513 | 0.0048192 | 0.15335 | 0.0012636
323.4 | 132.4 | 0.21165 | 0.0042186 | 0.0060652 | 0.0016062 | 0.0053935 | 1.6859e-05 | 0.19008 | 0.00061214 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.20087 | 0.0016967 | -0.0037056 | 0.00032025 | 0.25815 | 0.00084239 | 0.088619 | -6.1803e-05 | 0.19244 | 8.4239e-05 | 0.17356 | 0.00033696 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 0.16751 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | 0.0015107 | -0.011119 | -0.0006346 | 0.21368 | 0.0028311 | 0.16751 | 0.004404 | 0.30262 | 0.0015001 | 0.37375 | 0.00097717 | 0.23793 | 0.00041557 | 0.29859 | -0.00045489 | 0.25952 | 0.0011513 | 0.30633 | 0.0012748 | 0.22513 | 0.0031962 | 0.25073 | 0.0012636
323.6 | 132.6 | 0.21165 | 0.0042186 | 0.0060652 | 0.0016062 | 0.0053935 | 1.6859e-05 | 0.19008 | 0.00061214 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | -0.0037056 | 0.0019433 | 0.25815 | 0.00084239 | 0.088619 | -6.1803e-05 | 0.19244 | 8.4239e-05 | 0.17356 | 0.00033696 | 0.01988 | 0.0022635 | 0.11562 | 0.0013085 | 0.15942 | 0.0014439 | 0.070087 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | 0.0015332 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.21368 | 0.0012074 | 0.070087 | 0.004404 | 0.30262 | 0.0031231 | 0.27633 | 0.00097717 | 0.23793 | 0.00041557 | 0.20121 | 0.0011681 | 0.25952 | 0.0011513 | 0.30633 | 0.0012748 | 0.32251 | 0.0048192 | 0.25073 | 0.0012636
323.8 | 132.8 | 0.30903 | 0.0042186 | 0.0060652 | 0.0016062 | 0.0053935 | 1.6859e-05 | 0.092701 | -0.0010109 | 0.14424 | 0.00012922 | 0.28848 | 0.00029777 | 0.20087 | 0.0016967 | -0.0037056 | 0.0019433 | 0.25815 | 0.00084239 | 0.088619 | -6.1803e-05 | 0.19244 | 8.4239e-05 | 0.17356 | 0.00033696 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | -0.00017979 | 0.070087 | 0.0016967 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 0.30262 | 0.0015001 | 0.27633 | 0.0026002 | 0.23793 | 0.00041557 | 0.20121 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748 | 0.22513 | 0.0031962 | 0.15335 | 0.0012636
324 | 133 | 0.21165 | 0.0042186 | 0.0060652 | -1.6843e-05 | 0.0053935 | 1.6859e-05 | 0.19008 | 0.00061214 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.20087 | 0.0016967 | -0.0037056 | 0.00032025 | 0.35553 | 0.00084239 | 0.088619 | -6.1803e-05 | 0.19244 | 8.4239e-05 | 0.17356 | 0.00033696 | 0.01988 | 0.0038865 | 0.11562 | -0.00031449 | 0.15942 | -0.00017979 | 0.070087 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.095394 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | 0.0015107 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 0.30262 | 0.0015001 | 0.27633 | 0.0026002 | 0.14051 | 0.00041557 | 0.20121 | -0.00045489 | 0.25952 | 0.0011513 | 0.30633 | 0.0012748 | 0.22513 | 0.0031962 | 0.15335 | 0.0012636
324.2 | 133.2 | 0.21165 | 0.0042186 | 0.0060652 | 0.0016062 | 0.0053935 | 1.6859e-05 | 0.19008 | 0.00061214 | 0.14424 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | -0.0037056 | 0.00032025 | 0.25815 | -0.00078062 | 0.088619 | -6.1803e-05 | 0.095061 | 8.4239e-05 | 0.17356 | 0.00033696 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 0.070087 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | 0.0015332 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 0.30262 | 0.0015001 | 0.27633 | 0.0026002 | 0.23793 | 0.00041557 | 0.20121 | 0.0011681 | 0.25952 | 0.0011513 | 0.30633 | 0.0028978 | 0.22513 | 0.0031962 | 0.25073 | 0.0012636
324.4 | 133.4 | 0.21165 | 0.0042186 | 0.10345 | -1.6843e-05 | 0.0053935 | 1.6859e-05 | 0.19008 | 0.00061214 | 0.14424 | 0.00012922 | 0.28848 | 0.00029777 | 0.20087 | 0.0016967 | -0.0037056 | 0.00032025 | 0.25815 | 0.00084239 | 0.18604 | -6.1803e-05 | 0.19244 | 8.4239e-05 | 0.17356 | 0.00033696 | 0.01988 | 0.0022635 | 0.11562 | 0.0013085 | 0.15942 | -0.00017979 | 0.16751 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | -0.080196 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | 0.0015107 | -0.011119 | 0.0009884 | 0.11626 | 0.0028311 | 0.16751 | 0.004404 | 0.20523 | 0.0031231 | 0.27633 | 0.00097717 | 0.33531 | 0.00041557 | 0.20121 | -0.00045489 | 0.25952 | 0.0011513 | 0.30633 | 0.0012748 | 0.22513 | 0.0031962 | 0.15335 | 0.0012636
324.6 | 133.6 | 0.21165 | 0.0042186 | 0.10345 | -1.6843e-05 | 0.0053935 | 1.6859e-05 | 0.19008 | 0.00061214 | 0.24166 | 0.0017522 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | -0.0037056 | 0.00032025 | 0.25815 | 0.00084239 | 0.088619 | -6.1803e-05 | 0.19244 | 8.4239e-05 | 0.17356 | 0.00033696 | 0.01988 | 0.0038865 | 0.018196 | 0.0013085 | 0.15942 | 0.0014439 | 0.16751 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.27297 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 0.20523 | 0.0015001 | 0.27633 | 0.0026002 | 0.23793 | 0.00041557 | 0.20121 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748 | 0.32251 | 0.0031962 | 0.15335 | 0.0012636
324.8 | 133.8 | 0.21165 | 0.0042186 | 0.0060652 | -1.6843e-05 | 0.0053935 | 0.0016399 | 0.19008 | -0.0010109 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | -0.0037056 | 0.00032025 | 0.25815 | -0.00078062 | 0.088619 | 0.0015619 | 0.19244 | 8.4239e-05 | 0.17356 | 0.00033696 | 0.01988 | 0.0038865 | 0.018196 | 0.0013085 | 0.15942 | 0.0014439 | 0.16751 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.095394 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.21368 | 0.0012074 | 0.16751 | 0.004404 | 0.20523 | 0.0015001 | 0.27633 | 0.00097717 | 0.23793 | 0.00041557 | 0.20121 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748 | 0.32251 | 0.0048192 | 0.15335 | 0.0012636
325 | 134 | 0.30903 | 0.002595 | 0.0060652 | -1.6843e-05 | 0.0053935 | 1.6859e-05 | 0.19008 | 0.00061214 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.20087 | 0.0016967 | -0.0037056 | 0.00032025 | 0.25815 | -0.00078062 | 0.18604 | -6.1803e-05 | 0.19244 | 8.4239e-05 | 0.17356 | 0.00033696 | 0.01988 | 0.0022635 | 0.11562 | -0.00031449 | 0.15942 | 0.0014439 | 0.070087 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | 0.0015332 | 0.19851 | -0.00020779 | 0.27297 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | -0.00041558 | 0.16751 | 0.004404 | 0.20523 | 0.0031231 | 0.27633 | 0.00097717 | 0.23793 | 0.00041557 | 0.20121 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748 | 0.32251 | 0.019429 | 0.15335 | 0.0012636
325.2 | 134.2 | 0.21165 | 0.0042186 | 0.10345 | -1.6843e-05 | 0.0053935 | 1.6859e-05 | 0.19008 | 0.00061214 | 0.24166 | 0.00012922 | 0.19109 | 0.00029777 | 0.20087 | 0.0016967 | -0.0037056 | 0.00032025 | 0.35553 | 0.00084239 | 0.088619 | -6.1803e-05 | 0.19244 | 8.4239e-05 | 0.17356 | 0.00033696 | 0.01988 | 0.0022635 | 0.11562 | -0.00031449 | 0.15942 | -0.00017979 | 0.070087 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | 0.0015332 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | 0.086261 | -0.0006346 | 0.21368 | 0.0012074 | 0.16751 | 0.004404 | 0.20523 | 0.0015001 | 0.27633 | 0.00097717 | 0.23793 | 0.00041557 | 0.20121 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748 | 0.22513 | 0.085983 | 0.15335 | 0.0012636
325.4 | 134.4 | 0.21165 | 0.0042186 | 0.0060652 | -1.6843e-05 | 0.0053935 | 1.6859e-05 | 0.19008 | 0.00061214 | 0.24166 | 0.0017522 | 0.28848 | 0.00029777 | 0.20087 | 0.0016967 | -0.0037056 | 0.00032025 | 0.25815 | 0.00084239 | 0.18604 | -6.1803e-05 | 0.095061 | 8.4239e-05 | 0.17356 | 0.00033696 | 0.01988 | 0.0038865 | 0.11562 | 0.0013085 | 0.15942 | -0.00017979 | 0.070087 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.27297 | -0.00011232 | 0.086261 | 0.0009884 | 0.21368 | 0.0012074 | 0.16751 | 0.004404 | 0.20523 | 0.0015001 | 0.27633 | 0.0026002 | 0.23793 | 0.00041557 | 0.20121 | -0.00045489 | 0.25952 | 0.0011513 | 0.30633 | -0.00034817 | 0.22513 | 0.089229 | 0.15335 | 0.0012636
325.6 | 134.6 | 0.21165 | 0.0042186 | 0.0060652 | -1.6843e-05 | 0.0053935 | 1.6859e-05 | 0.092701 | -0.0010109 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | -0.0037056 | 0.00032025 | 0.25815 | 0.00084239 | 0.18604 | -6.1803e-05 | 0.19244 | 8.4239e-05 | 0.17356 | 0.00033696 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | 0.0014439 | 0.16751 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | -0.080196 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 0.20523 | 0.0015001 | 0.27633 | 0.00097717 | 0.23793 | 0.00041557 | 0.20121 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748 | 0.22513 | 0.089229 | 0.055933 | 0.0012636
325.8 | 134.8 | 0.21165 | 0.002595 | 0.0060652 | -1.6843e-05 | 0.0053935 | 0.0016399 | 0.19008 | 0.00061214 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.20087 | 0.0016967 | -0.0037056 | 0.00032025 | 0.25815 | 0.00084239 | 0.18604 | -6.1803e-05 | 0.19244 | 8.4239e-05 | 0.17356 | 0.00033696 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 0.070087 | 0.0016967 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.29589 | 0.0014152 | 0.27297 | 0.0015107 | -0.011119 | -0.0006346 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 0.20523 | 0.0015001 | 0.27633 | 0.00097717 | 0.23793 | 0.00041557 | 0.20121 | 0.0011681 | 0.25952 | 0.0011513 | 0.30633 | 0.0012748 | 0.22513 | 0.035662 | 0.15335 | 0.0012636
326 | 135 | 0.21165 | 0.0042186 | 0.10345 | 0.0016062 | 0.0053935 | 1.6859e-05 | 0.19008 | 0.00061214 | 0.14424 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | -0.0037056 | 0.00032025 | 0.25815 | 0.00084239 | 0.088619 | -6.1803e-05 | 0.19244 | 8.4239e-05 | 0.17356 | 0.00033696 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 0.16751 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 0.20523 | 0.0015001 | 0.27633 | 0.00097717 | 0.23793 | 0.00041557 | 0.20121 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748 | 0.22513 | 0.014559 | 0.055933 | 0.0012636
326.2 | 135.2 | 0.21165 | 0.0042186 | 0.10345 | -1.6843e-05 | 0.0053935 | 1.6859e-05 | 0.19008 | 0.00061214 | 0.24166 | 0.00012922 | 0.19109 | 0.00029777 | 0.20087 | 0.0016967 | -0.0037056 | 0.00032025 | 0.25815 | 0.00084239 | 0.088619 | -6.1803e-05 | 0.19244 | 8.4239e-05 | 0.17356 | 0.00033696 | 0.01988 | 0.0022635 | 0.11562 | -0.00031449 | 0.15942 | -0.00017979 | 0.16751 | 7.2982e-05 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | 0.0015332 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | -0.011119 | -0.0006346 | 0.11626 | 0.0028311 | 0.16751 | 0.004404 | 0.20523 | 0.0015001 | 0.27633 | 0.00097717 | 0.23793 | 0.00041557 | 0.20121 | 0.0011681 | 0.25952 | 0.0011513 | 0.30633 | -0.00034817 | 0.22513 | 0.016182 | 0.15335 | 0.0012636
326.4 | 135.4 | 0.21165 | 0.002595 | 0.0060652 | -1.6843e-05 | 0.0053935 | 1.6859e-05 | 0.19008 | 0.00061214 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.20087 | 0.0016967 | -0.0037056 | 0.00032025 | 0.35553 | 0.00084239 | 0.088619 | -6.1803e-05 | 0.095061 | 8.4239e-05 | 0.076183 | 0.00033696 | 0.01988 | 0.0022635 | 0.11562 | 0.0013085 | 0.15942 | 0.0014439 | 0.070087 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | -0.080196 | 0.0015332 | 0.29589 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.070087 | 0.0027804 | 0.20523 | 0.0015001 | 0.27633 | 0.00097717 | 0.23793 | 0.00041557 | 0.20121 | 0.0011681 | 0.25952 | -0.00047174 | 0.30633 | -0.00034817 | 0.22513 | 0.081113 | 0.055933 | 0.0012636
326.6 | 135.6 | 0.21165 | 0.0042186 | 0.0060652 | -1.6843e-05 | 0.0053935 | 0.0016399 | 0.19008 | 0.00061214 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.20087 | 0.0016967 | -0.0037056 | 0.0019433 | 0.25815 | 0.00084239 | 0.088619 | -6.1803e-05 | 0.19244 | 8.4239e-05 | 0.076183 | 0.00033696 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.15942 | 0.0014439 | 0.070087 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.10109 | 0.0014152 | 0.17559 | -0.00011232 | 0.086261 | -0.0006346 | 0.11626 | 0.0028311 | 0.070087 | 0.004404 | 0.20523 | 0.0015001 | 0.27633 | 0.00097717 | 0.23793 | 0.00041557 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.30633 | -0.00034817 | 0.22513 | 0.089229 | 0.15335 | 0.0012636
326.8 | 135.8 | 0.21165 | 0.0042186 | 0.0060652 | -1.6843e-05 | 0.0053935 | 1.6859e-05 | 0.19008 | 0.00061214 | 0.14424 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | -0.0037056 | 0.0019433 | 0.25815 | 0.00084239 | 0.088619 | -6.1803e-05 | 0.19244 | 8.4239e-05 | 0.17356 | 0.00033696 | 0.01988 | 0.0022635 | 0.11562 | -0.00031449 | 0.15942 | 0.0014439 | 0.070087 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | 0.0015332 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.21368 | 0.0012074 | 0.16751 | 0.004404 | 0.10785 | 0.0015001 | 0.17895 | 0.00097717 | 0.23793 | 0.00041557 | 0.20121 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748 | 0.22513 | 0.089229 | 0.15335 | 0.0012636
327 | 136 | 0.21165 | 0.0042186 | 0.0060652 | -1.6843e-05 | 0.0053935 | 1.6859e-05 | 0.19008 | 0.00061214 | 0.24166 | 0.0017522 | 0.28848 | 0.00029777 | 0.20087 | 0.0016967 | -0.0037056 | 0.00032025 | 0.25815 | 0.00084239 | 0.088619 | -6.1803e-05 | 0.19244 | 8.4239e-05 | 0.17356 | 0.00033696 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | -0.00017979 | 0.16751 | 7.2982e-05 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.17559 | 0.0015107 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.070087 | 0.006027 | 0.10785 | 0.0031231 | 0.27633 | 0.00097717 | 0.23793 | 0.00041557 | 0.20121 | -0.00045489 | 0.25952 | 0.0011513 | 0.30633 | 0.0012748 | 0.22513 | 0.089229 | 0.055933 | 0.0012636
327.2 | 136.2 | 0.21165 | 0.0042186 | 0.10345 | 0.0016062 | 0.0053935 | 1.6859e-05 | 0.19008 | 0.00061214 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | -0.0037056 | 0.00032025 | 0.25815 | 0.00084239 | 0.088619 | 0.0015619 | 0.095061 | 8.4239e-05 | 0.17356 | 0.00033696 | 0.01988 | 0.0038865 | 0.018196 | 0.0013085 | 0.15942 | 0.0014439 | 0.070087 | 7.2982e-05 | 0.30132 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | -0.0006346 | 0.21368 | 0.0012074 | 0.16751 | 0.004404 | 0.20523 | 0.0015001 | 0.27633 | 0.00097717 | 0.23793 | 0.00041557 | 0.20121 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.035662 | 0.055933 | 0.0012636
327.4 | 136.4 | 0.21165 | 0.0042186 | 0.0060652 | -1.6843e-05 | 0.0053935 | 1.6859e-05 | 0.19008 | 0.00061214 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | 0.093675 | 0.0019433 | 0.25815 | 0.00084239 | 0.088619 | -6.1803e-05 | 0.19244 | 8.4239e-05 | 0.17356 | -0.001286 | 0.01988 | 0.0022635 | 0.11562 | 0.0013085 | 0.15942 | 0.0014439 | 0.070087 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.21368 | 0.0012074 | 0.16751 | 0.004404 | 0.20523 | 0.0015001 | 0.27633 | 0.00097717 | 0.23793 | 0.00041557 | 0.20121 | 0.0011681 | 0.25952 | 0.0011513 | 0.30633 | 0.0012748 | 0.32251 | 0.014559 | 0.15335 | 0.0012636
327.6 | 136.6 | 0.21165 | 0.0042186 | 0.10345 | -1.6843e-05 | 0.0053935 | 1.6859e-05 | 0.19008 | 0.00061214 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.20087 | 0.0016967 | -0.0037056 | 0.00032025 | 0.25815 | 0.00084239 | 0.088619 | -6.1803e-05 | 0.19244 | 0.0017072 | 0.17356 | 0.00033696 | 0.01988 | 0.0038865 | 0.018196 | 0.0013085 | 0.15942 | 0.0014439 | 0.070087 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 0.20523 | 0.0015001 | 0.27633 | 0.00097717 | 0.23793 | 0.00041557 | 0.20121 | 0.0011681 | 0.1621 | 0.0011513 | 0.30633 | 0.0012748 | 0.22513 | 0.016182 | 0.055933 | 0.0012636
327.8 | 136.8 | 0.21165 | 0.0042186 | 0.0060652 | -1.6843e-05 | 0.0053935 | 1.6859e-05 | 0.092701 | 0.00061214 | 0.24166 | 0.0017522 | 0.28848 | 0.00029777 | 0.20087 | 0.0016967 | -0.0037056 | 0.00032025 | 0.25815 | 0.00084239 | 0.18604 | 0.0015619 | 0.19244 | 8.4239e-05 | 0.076183 | 0.00033696 | 0.01988 | 0.0022635 | 0.11562 | -0.00031449 | 0.15942 | -0.00017979 | 0.16751 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | -0.080196 | -8.9855e-05 | 0.29589 | -0.00020779 | 0.27297 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 0.20523 | -0.0001236 | 0.27633 | 0.00097717 | 0.23793 | 0.00041557 | 0.20121 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748 | 0.22513 | 0.08436 | 0.15335 | 0.0012636
328 | 137 | 0.21165 | 0.002595 | 0.0060652 | -1.6843e-05 | 0.0053935 | 1.6859e-05 | 0.092701 | 0.00061214 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | -0.0037056 | 0.00032025 | 0.25815 | 0.00084239 | 0.18604 | -6.1803e-05 | 0.19244 | 8.4239e-05 | 0.17356 | 0.00033696 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | -0.00017979 | 0.070087 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | -0.0013928 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 0.070087 | 0.004404 | 0.20523 | 0.0015001 | 0.17895 | 0.00097717 | 0.23793 | 0.00041557 | 0.10379 | 0.0011681 | 0.25952 | -0.00047174 | 0.20895 | -0.00034817 | 0.32251 | 0.090853 | 0.055933 | 0.0012636
328.2 | 137.2 | 0.21165 | 0.002595 | 0.0060652 | -1.6843e-05 | 0.0053935 | 1.6859e-05 | 0.19008 | 0.00061214 | 0.14424 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | -0.0037056 | 0.0019433 | 0.25815 | 0.00084239 | 0.088619 | -6.1803e-05 | 0.19244 | 8.4239e-05 | 0.17356 | 0.00033696 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | 0.0014439 | 0.070087 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 0.10785 | 0.0015001 | 0.27633 | 0.00097717 | 0.23793 | 0.00041557 | 0.20121 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748 | 0.32251 | 0.089229 | 0.15335 | 0.0012636
328.4 | 137.4 | 0.21165 | 0.0042186 | 0.10345 | -1.6843e-05 | 0.0053935 | 1.6859e-05 | 0.19008 | -0.0010109 | 0.14424 | 0.00012922 | 0.28848 | -0.0013259 | 0.10349 | 0.0016967 | -0.0037056 | 0.00032025 | 0.25815 | 0.00084239 | 0.088619 | -6.1803e-05 | 0.19244 | 8.4239e-05 | 0.17356 | 0.00033696 | 0.01988 | 0.0038865 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 0.070087 | 7.2982e-05 | 0.2039 | 0.001477 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | 0.0015107 | -0.011119 | 0.0009884 | 0.21368 | 0.0012074 | 0.16751 | 0.004404 | 0.10785 | 0.0015001 | 0.17895 | 0.00097717 | 0.23793 | 0.00041557 | 0.20121 | 0.0011681 | 0.1621 | 0.0011513 | 0.20895 | -0.00034817 | 0.22513 | 0.090853 | 0.15335 | 0.0012636
328.6 | 137.6 | 0.21165 | 0.0042186 | 0.0060652 | -1.6843e-05 | 0.0053935 | 1.6859e-05 | 0.19008 | -0.0010109 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | -0.0037056 | 0.00032025 | 0.25815 | 0.00084239 | 0.088619 | -6.1803e-05 | 0.19244 | 8.4239e-05 | 0.17356 | 0.00033696 | 0.01988 | 0.0038865 | 0.018196 | -0.00031449 | 0.15942 | -0.00017979 | 0.070087 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | 0.0015332 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 0.10785 | 0.0015001 | 0.27633 | 0.00097717 | 0.23793 | 0.00041557 | 0.20121 | -0.00045489 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748 | 0.32251 | 0.035662 | 0.055933 | 0.0012636
328.8 | 137.8 | 0.21165 | 0.0042186 | 0.0060652 | -1.6843e-05 | 0.0053935 | 1.6859e-05 | 0.19008 | 0.00061214 | 0.24166 | 0.00012922 | 0.19109 | 0.00029777 | 0.10349 | 0.0016967 | -0.0037056 | 0.00032025 | 0.25815 | 0.00084239 | 0.088619 | -6.1803e-05 | 0.19244 | 8.4239e-05 | 0.17356 | 0.00033696 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.2568 | 0.0014439 | 0.070087 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.21368 | 0.0012074 | 0.16751 | 0.004404 | 0.20523 | 0.0015001 | 0.27633 | 0.00097717 | 0.23793 | 0.00041557 | 0.20121 | -0.00045489 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817 | 0.32251 | 0.014559 | 0.15335 | 0.0012636
329 | 138 | 0.30903 | 0.0042186 | 0.0060652 | 0.0016062 | 0.10277 | 1.6859e-05 | 0.19008 | 0.00061214 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 0.0016967 | -0.0037056 | 0.00032025 | 0.25815 | 0.00084239 | 0.088619 | -6.1803e-05 | 0.19244 | 8.4239e-05 | 0.17356 | 0.00033696 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | 0.0014439 | 0.16751 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.27297 | 0.0015107 | -0.011119 | -0.0006346 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 0.20523 | 0.0015001 | 0.27633 | 0.00097717 | 0.33531 | 0.00041557 | 0.10379 | -0.00045489 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748 | 0.32251 | 0.016182 | 0.055933 | 0.0012636
329.2 | 138.2 | 0.21165 | 0.002595 | 0.0060652 | -1.6843e-05 | 0.0053935 | 1.6859e-05 | 0.19008 | 0.00061214 | 0.14424 | 0.00012922 | 0.19109 | 0.00029777 | 0.10349 | 0.0016967 | -0.0037056 | 0.00032025 | 0.25815 | 0.00084239 | 0.088619 | -6.1803e-05 | 0.19244 | 8.4239e-05 | 0.17356 | 0.00033696 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.2568 | 0.0014439 | 0.16751 | 0.0016967 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 0.10785 | -0.0001236 | 0.27633 | -0.00064583 | 0.23793 | 0.00041557 | 0.20121 | 0.0011681 | 0.25952 | -0.00047174 | 0.20895 | 0.0012748 | 0.22513 | 0.082736 | 0.055933 | 0.0012636
329.4 | 138.4 | 0.21165 | 0.002595 | 0.0060652 | -1.6843e-05 | 0.0053935 | 1.6859e-05 | 0.19008 | 0.00061214 | 0.24166 | 0.00012922 | 0.28848 | 0.0019208 | 0.10349 | 0.0016967 | -0.0037056 | 0.00032025 | 0.25815 | -0.00078062 | 0.088619 | -6.1803e-05 | 0.19244 | 8.4239e-05 | 0.17356 | 0.00033696 | 0.01988 | 0.0038865 | 0.11562 | -0.00031449 | 0.2568 | -0.00017979 | 0.16751 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.21368 | 0.0012074 | 0.16751 | 0.004404 | 0.10785 | 0.0015001 | 0.17895 | -0.00064583 | 0.23793 | 0.00041557 | 0.20121 | -0.00045489 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748 | 0.22513 | 0.090853 | 0.15335 | 0.0012636
329.6 | 138.6 | 0.21165 | 0.0042186 | 0.0060652 | -1.6843e-05 | 0.0053935 | 1.6859e-05 | 0.19008 | 0.00061214 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.20087 | 0.0016967 | -0.0037056 | 0.00032025 | 0.25815 | 0.00084239 | 0.088619 | -6.1803e-05 | 0.19244 | 8.4239e-05 | 0.17356 | 0.00033696 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449 | 0.2568 | -0.00017979 | 0.070087 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | -0.011119 | 0.0009884 | 0.11626 | 0.0012074 | 0.070087 | 0.004404 | 0.20523 | 0.0015001 | 0.17895 | 0.00097717 | 0.23793 | 0.00041557 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748 | 0.22513 | 0.090853 | 0.055933 | 0.0012636
329.8 | 138.8 | 0.21165 | 0.002595 | 0.0060652 | -1.6843e-05 | 0.0053935 | 1.6859e-05 | 0.19008 | -0.0010109 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.20087 | 0.0016967 | 0.093675 | 0.0019433 | 0.25815 | -0.00078062 | 0.088619 | -6.1803e-05 | 0.19244 | 8.4239e-05 | 0.17356 | 0.00033696 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.2568 | 0.0014439 | 0.070087 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | -0.080196 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | 0.086261 | -0.0006346 | 0.11626 | 0.0012074 | 0.16751 | 0.004404 | 0.20523 | -0.0001236 | 0.27633 | 0.00097717 | 0.23793 | 0.00041557 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748 | 0.22513 | 0.089229 | 0.055933 | 0.0012636
330 | 139 | 0.21165 | 0.0042186 | 0.0060652 | -1.6843e-05 | 0.0053935 | 1.6859e-05 | 0.092701 | 0.00061214 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.20087 | 0.0016967 | -0.0037056 | 0.00032025 | 0.25815 | 0.00084239 | 0.088619 | -6.1803e-05 | 0.19244 | 0.0017072 | 0.17356 | 0.00033696 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085 | 0.15942 | -0.00017979 | 0.070087 | 7.2982e-05 | 0.2039 | -0.00014601 | 0.19277 | 0.00023025 | 0.017185 | -8.9855e-05 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884 | 0.21368 | 0.0012074 | 0.16751 | 0.004404 | 0.10785 | -0.0001236 | 0.17895 | 0.00097717 | 0.23793 | 0.00041557 | 0.10379 | -0.00045489 | 0.1621 | 0.0011513 | 0.20895 | -0.00034817 | 0.32251 | 0.037285 | 0.055933 | 0.0012636