## IS Test Matrix
Intermediate Scale Test Matrix - Revision F (12-06-06)
|  | Comments: 1) All tests were conducted as open burns with a Propene (Propylene) gas sand burner 2) Colors identify test conditions grouped into the same test run | [14 empty] | ACTUAL TEST CONDITIONS
Burn Test # | Rev. E Test # | Loc. | Cable Insulation Material | [8 empty] | Number of Conductors |  |  |  | Conductor Size (AWG) |  |  |  |  | Cable Bundle Size |  |  |  |  | Water Spary Optionsl | Raceway Type
|  |  | Thermoset | [5 empty] | Thermoplastic
|  |  | XLPE | EPR | Silicone | XLPO | TS/TP | Vita-Link | PE | PVC | Tefzel | 3 | 2 | 7 | 12 | 8 | 12 | 14 | 16 | 18 | 1 | 3 | 6 | 12 | Load Tr | * | 12" Tray | 2.5" Cnd | Air Drop
Prelim 1 | Prelim 1 | A | X | [8 empty] | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | A | X | [10 empty] | X |  |  | X |  |  |  | X | [5 empty] | X
Prelim 2 | Prelim 2 | A | X | [8 empty] | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | A | X | [10 empty] | X |  |  | X |  |  |  | X | [5 empty] | X
Prelim 3 | Prelim 3 | A | [7 empty] | X |  | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | A | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [5 empty] | X
Prelim 4 | Prelim 4 | A | [7 empty] | X |  | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | A | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [5 empty] | X
1 | 15 | A | X | [9 empty] | X | X | X |  | X |  | X | X |  |  |  |  | X |  | X
|  | B | X | [10 empty] | X |  |  | X | [6 empty] | X |  |  | X
|  | D | X | [10 empty] | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | E | X | [10 empty] | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | [10 empty] | X |  |  | X | [6 empty] | X |  |  | X
2 | 1 | A | X | [10 empty] | X |  |  | X | [6 empty] | X |  |  | X
|  | C | X | [10 empty] | X |  |  | X | [5 empty] | X |  |  |  | X
|  | A | X | [5 empty] | X |  |  |  |  | X |  |  | X | [6 empty] | X |  |  | X
|  | C | X | [5 empty] | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
| 11 | C - A | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [7 empty] | X
|  | E | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [5 empty] | X
|  | G | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [5 empty] | X
3 | 2 | A | X | X | [9 empty] | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X | [9 empty] | X |  |  | X | [5 empty] | X |  |  |  | X
| 3 | A |  | X |  |  |  |  | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C |  | X |  |  |  |  | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
| 10 | E | [7 empty] | X |  | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | [7 empty] | X |  | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
4 | 5 | A | X | X |  | X | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X |  | X | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
| 6 | A | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
| 9 | C - A | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [7 empty] | X
|  | E | X | [8 empty] | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | [8 empty] | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
5 | 4 | A | X | X | X | X |  |  | X |  | X |  |  | X |  |  | X | [6 empty] | X |  | X | X
|  | C | X | X | X | X |  |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
| 7 | A | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | X | [5 empty] | X |  | X | X
|  | C | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | X |  |  |  |  | X |  |  | X | X
|  | C - A | X | [10 empty] | X |  |  | X |  |  |  | X | [7 empty] | X
|  | E |  | X | [9 empty] | X |  |  | X |  |  |  | X | [5 empty] | X
|  | G |  | X | [9 empty] | X |  |  | X |  |  |  | X | [5 empty] | X
6 | 12 | A | X | X | X | X |  |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | C | X | X | X | X |  |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | E | X | [5 empty] | X |  | X |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
| 13 | C - A | X | [5 empty] | X |  | X |  |  | X |  |  | X |  |  |  |  | X | [6 empty] | X
|  | A |  | X | X | X | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | C |  | X | X | X | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | G |  |  |  |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  |  |  | X
7 | 14 | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | A | X | X |  | X | X |  |  | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C |  | X |  | X | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | E | X | [5 empty] | X | X |  |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G |  | X |  | X | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
8 | 16 | A | X | [5 empty] | X | X |  |  | X | X | X |  | X |  | X | X |  |  | X |  |  |  | X
|  | A | X | [5 empty] | X | X |  |  | X | X | X |  | X |  | X | X |  |  | X |  |  |  | X
|  | C | X | [5 empty] | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | E | X | [5 empty] | X |  |  |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | [5 empty] | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
9 | 19 | A | X | X | X |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | A | X | X | X |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | C | X | X | X |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | E | X | [5 empty] | X |  | X |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | X | X |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
10 | 20 | A | X | X | X | X | X |  |  |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | A | X | X | X | X | X |  |  |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | C | X | X | X | X | X |  |  | X |  |  |  | X | X |  | X |  |  | X |  |  | X |  |  | X | X
|  | E |  |  |  |  | X |  | X |  | X |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | X |  |  | X |  | X | X | X |  | X | X |  |  | X |  | X |  |  |  | X |  |  |  | X
11 | 21 | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X |  | X | X |  |  | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | E |  |  |  |  | X |  | X | X |  |  |  | X |  |  | X |  |  |  |  | X | [6 empty] | X
|  | G | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
12 | 24 | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X |  | X | X |  |  | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | E |  |  |  |  | X |  | X | X |  |  |  | X |  |  | X |  |  |  |  | X | [6 empty] | X
|  | G | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
13 | 25 | A | X | X |  | X | X | X | X |  | X |  |  | X |  |  | X | [7 empty] | X | X | X
|  | C | X | X |  | X | X | X | X |  | X |  |  | X |  |  | X | [7 empty] | X | X | X
|  | E | X | X | [9 empty] | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | F | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | F | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | G | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | G | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
14 | 27 | A | X | X |  | X | X |  | X | X | X |  |  | X |  |  | X | [7 empty] | X |  | X
|  | C | X | X |  | X | X |  | X | X | X |  |  | X |  |  | X | [7 empty] | X |  | X
|  | E |  |  |  |  | X |  | X | X |  |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | F | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | F | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | G | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | G | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X

## Shorting Summary
Shorting Sequence for Open Burn Test 14, Location F, IRMS #1
Test conditions: Cable: Bundle of 6, 7-conductor, 12 AWG, XLPE/CSPE, EPR/CPE, PE/PVC, PVC/PVC, XLPE/PVC & Tefzel/Tefzel control cables (Items 10, 2, 15, 1, 3 & 12). Cable specimens present: Three lengths of cable were monitored for electrical performance (A, B & C [See Elect. Conn. Map]), a second bundle of 6 cables was monitored for temperature response. Raceway: 12" B-Line Series 2 tray (part number 248P09-12-144) located at position F in the Test Cell chamber with chamber end walls open and un-heated. Exposure conditions: Gas burner flow rate set to a nominal 300 kW heat release rate. Electrical repsonse monitoring: IRMS system using 6 channels - two for each cable (see electrical connection map), cable tray was grounded. Thermal response monitoring: Two cable bundle temperatures (see thermocouple map), air temperatures above and below the cable bundle, and the cable tray rung temperature. Gas burner initiated: Following 236 seconds of baseline data monitoring.
DAQ Time | Burner Time | Event | Interpretation
236 | 0 | Ignited Gas Burner
615 | 379 | Conductor C5 shorts to ground at less than 100 ohms (34)
628 | 392 | Conductors C5 & C6 short together at less than 100 ohms (34) | Cable C shorts internally
659 | 423 | Conductor C6 shorts to ground at less than 100 ohms (19) | Cable C shorted to ground
693 | 457 | Conductor B3 shorts to ground at less than 100 ohms (15)
698 | 462 | Conductors B3 & B4 short together at less than 100 ohms (80) | Cable B shorts internally
738 | 502 | Conductor B4 shorts to ground at less than 100 ohms (93) | Cable B shorted to ground
883 | 647 | Conductors A1 & A2 short together at less than 1000 ohms (497) | Cable A shorts internally
888-897 | 652-661 | Conductors A1 & A2 short to ground at less than 1000 ohms (999 & 435) | Cable A shorted to ground
925 | 689 | The existing short between conductors A1 & A2 decreases to less than 100 ohms (82)
930-940 | 694-704 | The existing ground faults on conductors A1 & A2 decrease to less than 100 ohms (48 & 22)
1949 | 1713 | Extinguished Gas Burner
Additional Observations
Observation 1 | The cables shorted internally prior to shorting to ground.
Observation 2 | The progression of cable failure was that the lower cables failed before the top cable.
Observation 3 | There was no evidence of cable-to-cable interactions prior to internal cable shorting or shorting to ground.

## Thermocouple Map
Thermocouple map for TC's on and within the cable
|  |  |  | Cable A = | XLPE | (Item #10)
|  |  |  | Cable B = | EPR | (Item #2)
|  |  |  | Cable C = | PE | (Item #15)
|  |  |  | Cable D = | PVC | (Item #1)
|  |  |  | Cable E = | TS/TP | (Item #3)
|  |  |  | Cable F = | TEFZEL | (Item #12)
Translation to data file names used in "Temperatures" WorkSheet:
| Map Name |  | Location
| F1 | = | Center of bundle, under jacket
| F2 | = | Air above bundle
| F3 | = | Air below bundle
| F4 | = | Intra-bundle, center

## Elect Conn Map
Electrical connection map within the cables
|  |  |  | Cable A = | XLPE | (Item #10)
|  |  |  | Cable B = | EPR | (Item #2)
|  |  |  | Cable C = | PE | (Item #15)
Tray rung under D-E-F
Cable Bundle Arrangement
Cable 7-Conductor Arrangement
| Lt Blue = | Even conductor set
| Lt Red = | Odd conductor set
| Gray = | Center conductor (not connected)
IRMS Electrical Connections

## C-C Individuals
Conductor to Conductor Resistances
Open Burn Test 14 |  |  | 2006-11-29 | 11:22
Mixed | 7-C | Tray F | IRMS | 1
0 | 300 kW
Burner Time | A1-A2 | Burner Time | A1-B3 | Burner Time | A1-B4 | Burner Time | A1-C5 | Burner Time | A1-C6 | Burner Time | A2-B3 | Burner Time | A2-B4 | Burner Time | A2-C5 | Burner Time | A2-C6 | Burner Time | B3-B4 | Burner Time | B3-C5 | Burner Time | B3-C6 | Burner Time | B4-C5 | Burner Time | B4-C6 | Burner Time | C5-C6
-235 | 253637.9994 | -232.5 | 249737.9994 | -229.5 | 253537.9994 | -226.5 | 259837.9994 | -224 | 262637.9994 | -221 | 257637.9994 | -218 | 252237.9994 | -215.5 | 261437.9994 | -212.5 | 262637.9994 | -209.5 | 254837.9994 | -207 | 261337.9994 | -204 | 259937.9994 | -201.5 | 259937.9994 | -198.5 | 261337.9994 | -195.5 | 261637.9994
-193 | 253637.9994 | -190 | 249737.9994 | -187.5 | 253537.9994 | -184.5 | 259837.9994 | -182 | 262637.9994 | -179 | 257637.9994 | -176.5 | 252237.9994 | -173.5 | 261437.9994 | -170.5 | 262637.9994 | -168 | 254837.9994 | -165 | 261337.9994 | -162.5 | 259937.9994 | -159.5 | 259937.9994 | -156.5 | 261337.9994 | -154 | 261637.9994
-151 | 253637.9994 | -148.5 | 249737.9994 | -145.5 | 253537.9994 | -142.5 | 259837.9994 | -139.5 | 262637.9994 | -137 | 257637.9994 | -134.5 | 252237.9994 | -131.5 | 261437.9994 | -128.5 | 262637.9994 | -126 | 254837.9994 | -123 | 261337.9994 | -120.5 | 259937.9994 | -117.5 | 259937.9994 | -114.5 | 261337.9994 | -112 | 261637.9994
-109 | 253637.9994 | -106.5 | 249737.9994 | -103.5 | 253537.9994 | -100.5 | 259837.9994 | -97.5 | 262637.9994 | -95 | 257637.9994 | -92.5 | 252237.9994 | -89.5 | 261437.9994 | -86.5 | 262637.9994 | -84 | 254837.9994 | -81 | 261337.9994 | -78.5 | 259937.9994 | -75.5 | 259937.9994 | -72.5 | 261337.9994 | -70 | 261637.9994
-67 | 253637.9994 | -64.5 | 249737.9994 | -61.5 | 253537.9994 | -58.5 | 259837.9994 | -56 | 262637.9994 | -53 | 257637.9994 | -50.5 | 252237.9994 | -47.5 | 261437.9994 | -44.5 | 262637.9994 | -42 | 254837.9994 | -39 | 261337.9994 | -36.5 | 259937.9994 | -33.5 | 259937.9994 | -30.5 | 261337.9994 | -27.5 | 261637.9994
-25 | 253637.9994 | -22.5 | 249737.9994 | -19.5 | 253537.9994 | -16.5 | 259837.9994 | -14 | 262637.9994 | -11 | 257637.9994 | -8.5 | 252237.9994 | -5.5 | 261437.9994 | -2.5 | 262637.9994 | -1.5274e-07 | 254837.9994 | 3 | 261337.9994 | 5.5 | 259937.9994 | 8.5 | 259937.9994 | 11.5 | 261337.9994 | 14 | 261637.9994
17 | 253637.9994 | 19.5 | 249737.9994 | 22.5 | 253537.9994 | 25.5 | 259837.9994 | 28 | 262637.9994 | 31 | 257637.9994 | 33.5 | 252237.9994 | 36.5 | 261437.9994 | 39.5 | 262637.9994 | 42 | 254837.9994 | 45 | 261337.9994 | 47.5 | 259937.9994 | 50.5 | 259937.9994 | 53.5 | 261337.9994 | 56 | 261637.9994
59 | 253637.9994 | 61.5 | 249737.9994 | 64.5 | 253537.9994 | 67.5 | 259837.9994 | 70 | 262637.9994 | 73 | 257637.9994 | 75.5 | 252237.9994 | 78.5 | 261437.9994 | 81.5 | 262637.9994 | 84 | 254837.9994 | 87 | 261337.9994 | 89.5 | 259937.9994 | 92.5 | 259937.9994 | 95.5 | 261337.9994 | 98 | 261637.9994
101 | 253637.9994 | 103.5 | 249737.9994 | 106.5 | 253537.9994 | 109.5 | 259837.9994 | 112 | 262637.9994 | 115 | 257637.9994 | 117.5 | 252237.9994 | 120.5 | 261437.9994 | 123.5 | 262637.9994 | 126 | 254837.9994 | 129 | 261337.9994 | 131.5 | 259937.9994 | 134.5 | 259937.9994 | 137.5 | 261337.9994 | 140 | 261637.9994
143 | 253637.9994 | 145.5 | 249737.9994 | 148.5 | 253537.9994 | 151.5 | 259837.9994 | 154 | 262637.9994 | 157 | 257637.9994 | 159.5 | 252237.9994 | 162.5 | 261437.9994 | 165.5 | 262637.9994 | 168 | 254837.9994 | 171 | 261337.9994 | 173.5 | 259937.9994 | 176.5 | 259937.9994 | 179.5 | 261337.9994 | 182 | 261637.9994
185 | 253637.9994 | 187.5 | 249737.9994 | 190.5 | 253537.9994 | 193.5 | 259837.9994 | 196 | 262637.9994 | 199 | 257637.9994 | 201.5 | 252237.9994 | 204.5 | 261437.9994 | 207.5 | 262637.9994 | 210 | 254837.9994 | 213 | 261337.9994 | 215.5 | 259937.9994 | 218.5 | 259937.9994 | 221.5 | 261337.9994 | 224 | 261637.9994
227 | 253637.9994 | 229.5 | 249737.9994 | 232.5 | 253537.9994 | 235.5 | 259837.9994 | 238 | 262637.9994 | 241 | 257637.9994 | 243.5 | 252237.9994 | 246.5 | 261437.9994 | 249.5 | 262637.9994 | 252 | 254837.9994 | 255 | 261337.9994 | 257.5 | 259937.9994 | 260.5 | 259937.9994 | 263.5 | 261337.9994 | 266 | 261637.9994
270 | 253637.9994 | 271.5 | 249737.9994 | 274.5 | 253537.9994 | 277.5 | 259837.9994 | 280 | 262637.9994 | 283 | 257637.9994 | 285.5 | 252237.9994 | 288.5 | 261437.9994 | 291.5 | 262637.9994 | 294 | 254837.9994 | 297 | 261337.9994 | 299.5 | 259937.9994 | 302.5 | 259937.9994 | 305.5 | 261337.9994 | 308 | 261637.9994
311 | 253637.9994 | 313.5 | 249737.9994 | 316.5 | 253537.9994 | 319.5 | 259837.9994 | 322 | 262637.9994 | 325 | 257637.9994 | 327.5 | 252237.9994 | 330.5 | 261437.9994 | 333.5 | 262637.9994 | 336 | 254837.9994 | 339 | 261337.9994 | 341.5 | 259937.9994 | 344.5 | 259937.9994 | 347.5 | 261337.9994 | 350 | 261637.9994
353 | 253637.9994 | 355.5 | 249737.9994 | 358.5 | 253537.9994 | 361.5 | 259837.9994 | 364 | 262637.9994 | 367 | 257637.9994 | 369.5 | 252237.9994 | 372.5 | 261437.9994 | 375.5 | 262637.9994 | 378 | 254837.9994 | 381 | 261337.9994 | 383.5 | 259937.9994 | 386.5 | 259937.9994 | 389.5 | 261337.9994 | 392 | 33.8726
395 | 253637.9994 | 397.5 | 249737.9994 | 400.5 | 253537.9994 | 403.5 | 259837.9994 | 406 | 262637.9994 | 409 | 257637.9994 | 411.5 | 252237.9994 | 414.5 | 261437.9994 | 417.5 | 262637.9994 | 420 | 254837.9994 | 423 | 261337.9994 | 425.5 | 259937.9994 | 428.5 | 259937.9994 | 431.5 | 261337.9994 | 434 | 26.5515
437 | 253637.9994 | 439.5 | 249737.9994 | 442.5 | 253537.9994 | 445.5 | 259837.9994 | 448 | 262637.9994 | 451 | 257637.9994 | 453.5 | 252237.9994 | 456.5 | 261437.9994 | 459.5 | 262637.9994 | 462 | 79.8175 | 465 | 13.5289 | 467.5 | 34.1932 | 470.5 | 259937.9994 | 473.5 | 261337.9994 | 476 | 7.088
479 | 253637.9994 | 481.5 | 249737.9994 | 484.5 | 253537.9994 | 487.5 | 259837.9994 | 490 | 262637.9994 | 493 | 257637.9994 | 495.5 | 252237.9994 | 498.5 | 261437.9994 | 501.5 | 262637.9994 | 504 | 579.6057 | 507 | 57.2469 | 509.5 | 772.4288 | 512.5 | 154.0662 | 515.5 | 91.6879 | 518 | 20.598
521 | 253637.9994 | 523.5 | 249737.9994 | 526.5 | 253537.9994 | 529.5 | 259837.9994 | 532 | 262637.9994 | 535 | 257637.9994 | 537.5 | 252237.9994 | 540.5 | 261437.9994 | 543.5 | 131268.9988 | 546 | 8317.5089 | 549 | 24.5437 | 551.5 | 28.7324 | 554.5 | 14.6161 | 557 | 17.7113 | 560 | 6.3175
563 | 126768.9988 | 565.5 | 249737.9994 | 568.5 | 253537.9994 | 571.5 | 259837.9994 | 574 | 262637.9994 | 577 | 128768.9988 | 579.5 | 252237.9994 | 582.5 | 261437.9994 | 585.5 | 262637.9994 | 588 | 1642.1825 | 591 | 9.7197 | 593.5 | 13.3218 | 596.5 | 34.6925 | 599.5 | 32.6034 | 602 | 30.3117
604.5 | 15258.2774 | 607.5 | 249737.9994 | 610.5 | 63309.4976 | 613.5 | 43222.9963 | 616 | 131268.9988 | 619 | 257637.9994 | 621.5 | 62984.4976 | 624.5 | 87079.3315 | 627 | 37433.9957 | 630 | 17.2075 | 633 | 27.356 | 635.5 | 3.8139 | 638.5 | 5.172 | 641.5 | 21.9668 | 644 | 20.426
646.5 | 497.0595 | 649.5 | 2349.3299 | 652.5 | 1187.3823 | 655.5 | 1034.9606 | 658 | 999.1763 | 661 | 804.1699 | 663.5 | 791.4809 | 666.5 | 640.6853 | 669.5 | 434.8082 | 672 | 6.0759 | 675 | 13.1213 | 677.5 | 29.6566 | 680.5 | 21.7758 | 683.5 | 34.9935 | 686 | 29.582
689 | 82.3225 | 691.5 | 533.8661 | 694.5 | 453.5152 | 697 | 65.6745 | 700 | 46.6862 | 703 | 35.2155 | 705.5 | 26.5603 | 708.5 | 46.3454 | 711.5 | 20.719 | 714 | 1514.1349 | 716.5 | 25.0965 | 719.5 | 18.5084 | 722.5 | 40.512 | 725.5 | 11.1741 | 728 | 21.815
731 | 223.6146 | 733.5 | 25.3592 | 736.5 | 9.263 | 739.5 | 9.464 | 742 | 17.2112 | 745 | 7.8171 | 747.5 | 10.8271 | 750.5 | 37.3739 | 753.5 | 31.0826 | 756 | 2.2599 | 759 | 4.1638 | 761.5 | 17.6766 | 764.5 | 16.0464 | 767 | 9.8155 | 770 | 14.5373
773 | 214.5671 | 775.5 | 23.1329 | 778.5 | 5.4819 | 781 | 36.6 | 784 | 28.9001 | 787 | 11.7013 | 789.5 | 30.2539 | 792.5 | 6.5961 | 795.5 | 28.0597 | 798 | 1.5365 | 801 | 7.0092 | 803.5 | 23.2645 | 806.5 | 6.2018 | 809 | 8.5354 | 812 | 25.6752
815 | 342.9419 | 817.5 | 10.1169 | 820.5 | 18.1186 | 823.5 | 10.1389 | 826 | 20.7764 | 828.5 | 36.2417 | 831.5 | 7.5403 | 834.5 | 14.5007 | 837.5 | 28.0597 | 840 | 1.4943 | 843 | 23.814 | 845.5 | 6.9756 | 848.5 | 27.7563 | 851 | 3.7323 | 854 | 0.48441
856.5 | 1077.9566 | 859.5 | 0.69056 | 862.5 | 7.1047 | 865 | 4.6014 | 868 | 12.379 | 871 | 34.925 | 873.5 | 10.1743 | 876.5 | 28.3058 | 879 | 30.7473 | 882 | 25.0368 | 885 | 6.5096 | 887.5 | 3.8571 | 890.5 | 27.4342 | 893.5 | 8.5823 | 896 | 13.5585
898.5 | 798.6605 | 901.5 | 5.6179 | 904.5 | 22.8412 | 907.5 | 7.951 | 910 | 4.7764 | 913 | 4.3607 | 915.5 | 26.1697 | 918.5 | 7.0507 | 921.5 | 11.9317 | 924 | 24.7219 | 926.5 | 19.8308 | 929.5 | 11.1603 | 932.5 | 16.1 | 935 | 0.1627 | 938 | 6.543
941 | 6346.2329 | 943.5 | 26.8653 | 946.5 | 25.215 | 949.5 | 3.5575 | 952 | 24.8016 | 955 | 2.3276 | 957.5 | 19.9287 | 960.5 | 20.0477 | 963.5 | 11.4878 | 966 | 7.0964 | 969 | 26.091 | 971.5 | 18.8443 | 974.5 | 31.0673 | 977.5 | 8.9589 | 980 | 13.9172
983 | 0.79967 | 985.5 | 12.4289 | 988.5 | 27.812 | 991.5 | 17.192 | 994 | 3.8683 | 997 | 6.3354 | 999.5 | 0.77926 | 1002.5 | 20.6196 | 1005.5 | 13.9464 | 1008 | 0.24235 | 1011 | 23.5124 | 1013.5 | 18.9005 | 1016.5 | 14.8258 | 1019.5 | 11.816 | 1022 | 0.40503
1025 | 9.8967 | 1027.5 | 3.5657 | 1030.5 | 13.577 | 1033.5 | 28.4208 | 1036 | 33.0607 | 1039 | 3.0972 | 1041.5 | 30.047 | 1044.5 | 7.971 | 1047 | 31.0154 | 1050 | 21.237 | 1053 | 7.0548 | 1055.5 | 5.3497 | 1058.5 | 5.3497 | 1061 | 24.2386 | 1064 | 1.537
1066.5 | 17.9386 | 1069.5 | 11.7514 | 1072.5 | 13.6824 | 1075 | 20.7363 | 1078 | 18.524 | 1080.5 | 7.3033 | 1083.5 | 19.8112 | 1086.5 | 7.509 | 1089.5 | 10.9986 | 1092 | 2.3027 | 1094.5 | 21.266 | 1097.5 | 19.8632 | 1100.5 | 4.7742 | 1103.5 | 29.498 | 1106 | 13.6608
1108.5 | 18.6795 | 1111.5 | 6.3195 | 1114.5 | 30.2404 | 1117 | 9.1772 | 1120 | 8.6131 | 1122.5 | 1.5689 | 1125.5 | 0.87715 | 1128.5 | 6.5509 | 1131 | 6.3243 | 1134 | 30.5009 | 1136.5 | 22.6755 | 1139.5 | 6.4283 | 1142.5 | 9.8915 | 1145.5 | 27.1647 | 1148 | 2.5354
1150.5 | 6.0753 | 1153.5 | 0.35242 | 1156.5 | 8.2455 | 1159 | 7.8112 | 1162 | 22.4618 | 1164.5 | 16.0264 | 1167 | 29.5668 | 1170.5 | 5.6981 | 1173 | 33.2687 | 1176 | 11.4247 | 1178.5 | 44.1444 | 1181.5 | 28.4054 | 1184.5 | 7.1592 | 1187.5 | 12.5152 | 1190 | 5.0275
1193 | 3.3291 | 1195.5 | 8.0403 | 1198.5 | 1.9871 | 1201 | 24.1877 | 1204 | 24.6186 | 1206.5 | 0.94491 | 1209.5 | 1.1593 | 1212.5 | 21.7794 | 1215 | 15.5566 | 1218 | 31.1907 | 1220.5 | 49.8883 | 1223.5 | 22.6052 | 1226.5 | 17.4018 | 1229 | 12.2145 | 1232 | 23.9575
1234.5 | 0.56403 | 1237.5 | 0.98822 | 1240.5 | 17.1041 | 1243 | 16.2698 | 1246 | 34.5298 | 1248.5 | 10.3116 | 1251.5 | 4.8884 | 1254.5 | 4.0744 | 1257 | 33.1993 | 1260 | 45.5387 | 1262.5 | 16.7324 | 1265.5 | 43.9349 | 1268.5 | 23.6877 | 1271 | 38.1391 | 1274 | 9.2751
1276.5 | 25.4561 | 1279.5 | 15.1651 | 1282.5 | 0.8073 | 1285 | 1.1565 | 1288 | 34.7423 | 1290.5 | 5.9256 | 1293.5 | 1.542 | 1296.5 | 11.4633 | 1299 | 13.284 | 1302 | 42.9522 | 1304.5 | 43.1752 | 1307.5 | 38.5185 | 1310.5 | 6.7469 | 1313 | 7.6516 | 1316 | 20.0267
1318.5 | 1.7715 | 1321.5 | 0.18417 | 1324.5 | 21.6266 | 1327 | 9.897 | 1330 | 9.8889 | 1332.5 | 5.3391 | 1335.5 | 16.1092 | 1338.5 | 30.6794 | 1341 | 34.318 | 1344 | 28.9408 | 1346.5 | 47.3 | 1349.5 | 23.024 | 1352.5 | 33.6269 | 1355 | 9.9596 | 1358 | 21.3486
1360.5 | 24.2542 | 1363.5 | 13.6472 | 1366.5 | 7.6722 | 1369 | 2.4912 | 1372 | 14.2547 | 1374.5 | 12.2058 | 1377.5 | 22.0833 | 1380.5 | 5.2545 | 1383 | 7.183 | 1386 | 35.4835 | 1388.5 | 19.7174 | 1391.5 | 36.653 | 1394.5 | 26.922 | 1397 | 35.2084 | 1400 | 6.4527
1402.5 | 0.9674 | 1405.5 | 21.5281 | 1408.5 | 0.96901 | 1411 | 31.9045 | 1414 | 25.1693 | 1416.5 | 20.629 | 1419.5 | 10.2743 | 1422.5 | 17.2652 | 1425 | 14.1517 | 1428 | 12.3413 | 1430.5 | 9.7197 | 1433.5 | 35.9933 | 1436.5 | 18.1743 | 1439 | 13.9393 | 1442 | 10.8626
1444.5 | 11.0448 | 1447.5 | 3.4763 | 1450.5 | 0.88504 | 1453 | 7.8577 | 1456 | 32.3036 | 1458.5 | 6.2897 | 1461.5 | 24.8207 | 1464.5 | 8.0639 | 1467 | 7.3198 | 1470 | 19.4777 | 1472.5 | 40.0346 | 1475.5 | 36.2857 | 1478.5 | 12.0554 | 1481 | 37.8405 | 1484 | 28.9254
1486.5 | 10.6428 | 1489.5 | 22.8211 | 1492.5 | 7.5772 | 1495 | 1.6531 | 1498 | 26.7872 | 1500.5 | 10.4589 | 1503.5 | 1.3716 | 1506.5 | 7.0963 | 1509 | 6.9104 | 1512 | 10.5721 | 1514.5 | 30.0279 | 1517.5 | 22.8442 | 1520.5 | 8.8869 | 1523 | 5.2137 | 1526 | 21.4648
1528.5 | 29.4046 | 1531.5 | 0.85531 | 1534.5 | 2.5902 | 1537 | 24.1266 | 1540 | 25.3539 | 1542.5 | 3.4428 | 1545.5 | 19.1687 | 1548.5 | 24.5307 | 1551 | 8.5664 | 1554 | 13.5864 | 1556.5 | 15.0829 | 1559.5 | 18.0079 | 1562.5 | 21.9526 | 1565 | 8.5823 | 1568 | 22.8177
1570.5 | 2.5014 | 1573.5 | 0.44201 | 1576.5 | 21.4464 | 1579 | 7.4401 | 1582 | 9.5554 | 1584.5 | 28.0394 | 1587.5 | 14.4205 | 1590.5 | 28.8913 | 1593 | 30.3472 | 1596 | 9.683 | 1598.5 | 16.9485 | 1601.5 | 19.2951 | 1604.5 | 30.6612 | 1607 | 37.3209 | 1610 | 12.2449
1612.5 | 4.1251 | 1615.5 | 5.1552 | 1618.5 | 10.349 | 1621 | 10.6259 | 1624 | 28.7052 | 1626.5 | 9.1466 | 1629.5 | 28.8191 | 1632.5 | 8.9539 | 1635 | 24.9852 | 1638 | 13929.594 | 1640.5 | 9.1008 | 1643.5 | 29.8563 | 1646.5 | 40.047 | 1649 | 18.8735 | 1652 | 14.1748
1654.5 | 12.6293 | 1657.5 | 8.43 | 1660.5 | 10.0012 | 1663 | 6.0251 | 1666 | 2.8067 | 1668.5 | 14.9549 | 1671.5 | 15.614 | 1674.5 | 19.3683 | 1677 | 25.2923 | 1680 | 9670.8409 | 1682.5 | 13.0706 | 1685.5 | 29.923 | 1688.5 | 8.6503 | 1691 | 9.6719 | 1694 | 4.1551
1696.5 | 10.0451 | 1699.5 | 25.8139 | 1702.5 | 5.5734 | 1705 | 9.2727 | 1708 | 34.0366 | 1710.5 | 7.2104 | 1713.5 | 29.4302 | 1716.5 | 13.216 | 1719 | 22.2266 | 1722 | 6.6302 | 1724.5 | 32.3276 | 1727.5 | 16.5849 | 1730.5 | 20.9572 | 1733 | 38.9669 | 1736 | 22.462
1738.5 | 11.9084 | 1741.5 | 4.5594 | 1744.5 | 25.4062 | 1747 | 10.236 | 1750 | 3.5263 | 1752.5 | 17.2275 | 1755.5 | 0.15194 | 1758.5 | 24.4085 | 1761 | 6.9558 | 1764 | 1445.4164 | 1766.5 | 12.6662 | 1769.5 | 42.4026 | 1772.5 | 44.1798 | 1775 | 22.4384 | 1778 | 9.4652
1780.5 | 12.6812 | 1783.5 | 2.3707 | 1786.5 | 24.6448 | 1789 | 3.2997 | 1792 | 4.7764 | 1794.5 | 2.9682 | 1797.5 | 13.9924 | 1800.5 | 17.2652 | 1803 | 8.6599 | 1806 | 915.4399 | 1808.5 | 27.4839 | 1811.5 | 23.2645 | 1814.5 | 47.7818 | 1817 | 26.1537 | 1820 | 2.1171
1822.5 | 1002.5637 | 1825.5 | 18.7863 | 1828.5 | 23.1485 | 1831 | 5.5762 | 1834 | 30.7473 | 1836.5 | 31.3945 | 1839.5 | 3.3656 | 1842.5 | 34.4754 | 1845 | 35.2406 | 1848 | 447.7968 | 1850.5 | 33.7178 | 1853.5 | 39.5083 | 1856.5 | 22.0116 | 1859 | 45.5396 | 1862 | 22.8772
1864.5 | 335.7509 | 1867.5 | 22.079 | 1870.5 | 7.2932 | 1873 | 11.2157 | 1876 | 18.524 | 1878.5 | 36.835 | 1881.5 | 17.5631 | 1884.5 | 12.9623 | 1887 | 26.5985 | 1890 | 192.6159 | 1892.5 | 47.8961 | 1895.5 | 32.0934 | 1898 | 43.6908 | 1901 | 19.8308 | 1904 | 23.4151
1906.5 | 100.1489 | 1909.5 | 16.4977 | 1912.5 | 11.9149 | 1915 | 28.6169 | 1918 | 22.1094 | 1920.5 | 35.5071 | 1923.5 | 25.3954 | 1926.5 | 15.1274 | 1929 | 17.5368 | 1932 | 240.5975 | 1934.5 | 40.8848 | 1937.5 | 31.8869 | 1940.5 | 26.9858 | 1943 | 56.0983 | 1946 | 23.2952
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!

## C-G Min
Average Conductor to Ground Resistances
Open Burn Test 14 |  |  | 2006-11-29 | 11:22
Mixed | 7-C | Tray F | IRMS | 1
0 | 300 kW
Burner Time | A1-G |  | Burner Time | A2-G | Burner Time | B3-G | Burner Time | B4-G | Burner Time | C5-G | Burner Time | C6-G
-229.5 | 249738 |  | -220.4 | 252238 | -214.8 | 249738 | -211.4 | 252238 | -209.2 | 259838 | -206.9 | 259938
-187.4 | 249738 |  | -178.5 | 252238 | -172.9 | 249738 | -169.6 | 252238 | -167.3 | 259838 | -165.1 | 259938
-145.4 | 249738 |  | -136.5 | 252238 | -131 | 249738 | -127.6 | 252238 | -125.3 | 259838 | -123 | 259938
-103.4 | 249738 |  | -94.5 | 252238 | -89 | 249738 | -85.6 | 252238 | -83.3 | 259838 | -81 | 259938
-61.5 | 249738 |  | -52.5 | 252238 | -47 | 249738 | -43.6 | 252238 | -41.2 | 259838 | -39 | 259938
-19.5 | 249738 |  | -10.5 | 252238 | -5 | 249738 | -1.6 | 252238 | 0.7 | 259838 | 2.9 | 259938
22.5 | 249738 |  | 31.5 | 252238 | 37 | 249738 | 40.4 | 252238 | 42.7 | 259838 | 44.9 | 259938
64.5 | 249738 |  | 73.5 | 252238 | 79 | 249738 | 82.4 | 252238 | 84.7 | 259838 | 86.9 | 259938
106.5 | 249738 |  | 115.5 | 252238 | 121 | 249738 | 124.4 | 252238 | 126.7 | 259838 | 128.9 | 259938
148.5 | 249738 |  | 157.5 | 252238 | 163 | 249738 | 166.4 | 252238 | 168.7 | 259838 | 170.9 | 259938
190.5 | 249738 |  | 199.5 | 252238 | 205 | 249738 | 208.4 | 252238 | 210.7 | 259838 | 212.9 | 259938
232.5 | 249738 |  | 241.5 | 252238 | 247 | 249738 | 250.4 | 252238 | 252.7 | 259838 | 254.9 | 259938
274.7 | 249738 |  | 283.7 | 252238 | 289 | 249738 | 292.4 | 252238 | 294.7 | 259838 | 296.9 | 259938
316.5 | 249738 |  | 325.5 | 252238 | 331 | 249738 | 334.4 | 252238 | 336.7 | 259838 | 338.9 | 259938
358.5 | 249738 |  | 367.5 | 252238 | 373 | 249738 | 376.4 | 252238 | 378.7 | 34.3171 | 380.9 | 259938
400.5 | 249738 |  | 409.5 | 252238 | 415 | 249738 | 418.4 | 252238 | 420.7 | 4.7428 | 422.9 | 18.7559
442.5 | 249738 |  | 451.5 | 252238 | 457 | 14.9178 | 460.4 | 252238 | 462.7 | 8.5599 | 464.9 | 10.1627
484.5 | 249738 |  | 493.5 | 252238 | 499 | 39.9989 | 502.4 | 92.5169 | 504.7 | 6.2299 | 506.9 | 13.6902
526.5 | 249738 |  | 535.5 | 131269 | 541 | 6.997 | 544.3 | 15.0808 | 546.7 | 0.63024 | 548.8 | 5.2359
568.5 | 126769 |  | 577.5 | 128769 | 583 | 3.9692 | 586.4 | 18.7444 | 588.7 | 0.63048 | 590.9 | 15.7267
610.4 | 5518.3817 |  | 619.3 | 12811.5751 | 625 | 5.3212 | 628.4 | 6.6604 | 630.7 | 0.63415 | 632.8 | 3.6851
652.4 | 999.3222 |  | 661.4 | 435.1079 | 667 | 7.5234 | 670.4 | 6.2684 | 672.7 | 6.0971 | 674.9 | 2.632
694.4 | 47.7717 |  | 703.5 | 22.0334 | 708.9 | 19.8332 | 712.4 | 12.5917 | 714.5 | 0.86309 | 716.9 | 4.1784
736.5 | 10.6623 |  | 745.5 | 9.2573 | 751 | 3.7599 | 754.3 | 6.9371 | 756.7 | 4.8118 | 758.8 | 2.3123
778.4 | 6.93 |  | 787.5 | 6.4751 | 793 | 3.0469 | 796.3 | 0.65 | 798.6 | 1.3398 | 800.8 | 2.0157
820.5 | 11.4851 |  | 829.4 | 7.4377 | 834.9 | 0.63959 | 838.3 | 4.3348 | 840.7 | 1.0962 | 842.8 | 3.4809
862.3 | 2.1832 |  | 871.3 | 11.4316 | 877 | 5.3639 | 880.4 | 2.7435 | 882.6 | 1.058 | 884.8 | 2.1929
904.4 | 5.3641 |  | 913.4 | 5.8472 | 918.9 | 7.1346 | 922.3 | 1.4112 | 924.6 | 0.66898 | 926.8 | 0.62735
946.5 | 5.0679 |  | 955.5 | 3.8429 | 961 | 8.5304 | 964.4 | 0.64666 | 966.7 | 6.4028 | 968.9 | 0.62976
988.5 | 2.3137 |  | 997.5 | 2.2854 | 1003 | 1.7717 | 1006.4 | 9.7924 | 1008.7 | 1.1743 | 1010.9 | 2.4816
1030.5 | 5.0181 |  | 1039.4 | 4.6015 | 1045 | 1.9747 | 1048.3 | 1.8937 | 1050.7 | 3.087 | 1052.7 | 2.1532
1072.3 | 13.1 |  | 1081.3 | 8.7502 | 1086.8 | 2.6436 | 1090.4 | 5.2003 | 1092.5 | 15.0497 | 1094.9 | 2.4578
1114.3 | 7.7352 |  | 1123.2 | 0.65337 | 1128.8 | 7.8996 | 1132.4 | 5.1567 | 1134.5 | 0.78536 | 1136.8 | 2.8036
1156.3 | 1.85 |  | 1165.1 | 7.1877 | 1170.8 | 12.8044 | 1174.3 | 7.9752 | 1176.5 | 6.2731 | 1178.8 | 0.78566
1198.4 | 3.4835 |  | 1207.3 | 2.4803 | 1212.8 | 19.4337 | 1216.3 | 6.9682 | 1218.5 | 1.0584 | 1220.7 | 4.0547
1240.3 | 0.97016 |  | 1249.2 | 5.5866 | 1254.8 | 18.084 | 1258.3 | 14.9604 | 1260.5 | 0.82933 | 1262.7 | 0.62735
1282.3 | 0.72994 |  | 1291.2 | 3.0372 | 1296.8 | 25.2371 | 1300.3 | 2.2854 | 1302.5 | 2.4033 | 1304.7 | 0.78174
1324.3 | 1.6842 |  | 1333.2 | 6.8123 | 1338.8 | 11.4302 | 1342.3 | 11.3266 | 1344.5 | 20.8586 | 1346.7 | 3.849
1366.3 | 4.0168 |  | 1375.2 | 3.6088 | 1380.8 | 11.1379 | 1384.3 | 6.6067 | 1386.5 | 5.8002 | 1388.7 | 1.1698
1408.3 | 2.479 |  | 1417.2 | 7.2888 | 1422.8 | 11.1556 | 1426.3 | 15.3233 | 1428.5 | 6.9714 | 1430.7 | 8.304
1450.3 | 2.3973 |  | 1459.2 | 2.9363 | 1464.8 | 20.7665 | 1468.3 | 1.2999 | 1470.5 | 0.6339 | 1472.7 | 2.5247
1492.3 | 3.1909 |  | 1501.2 | 2.8691 | 1506.8 | 11.9622 | 1510.3 | 3.7177 | 1512.5 | 15.215 | 1514.7 | 6.1462
1534.3 | 0.65995 |  | 1543.2 | 4.9422 | 1548.8 | 5.7292 | 1552.3 | 10.0328 | 1554.5 | 6.5293 | 1556.7 | 0.63048
1576.3 | 1.0672 |  | 1585.2 | 15.7514 | 1590.8 | 11.0841 | 1594.3 | 7.2012 | 1596.5 | 0.98601 | 1598.7 | 3.6997
1618.3 | 5.5922 |  | 1627.2 | 10.4002 | 1632.8 | 6.4593 | 1636.3 | 19.5842 | 1638.5 | 1.9757 | 1640.7 | 1.092
1660.3 | 4.3439 |  | 1669.2 | 0.64974 | 1674.8 | 10.4989 | 1678.3 | 0.81422 | 1680.5 | 5.6673 | 1682.7 | 3.6997
1702.3 | 7.0203 |  | 1711.2 | 8.6585 | 1716.8 | 6.9896 | 1720.3 | 1.8313 | 1722.5 | 1.058 | 1724.7 | 4.821
1744.3 | 5.0532 |  | 1753.2 | 1.6672 | 1758.8 | 12.1106 | 1762.3 | 13.0547 | 1764.5 | 10.2605 | 1766.7 | 0.6339
1786.3 | 3.8396 |  | 1795.2 | 4.4743 | 1800.8 | 7.5034 | 1804.3 | 11.5383 | 1806.5 | 3.6586 | 1808.7 | 3.2497
1828.3 | 3.7925 |  | 1837.2 | 4.8351 | 1842.8 | 14.7625 | 1846.3 | 18.4685 | 1848.5 | 12.7169 | 1850.7 | 3.2369
1870.3 | 5.9559 |  | 1879.2 | 14.3585 | 1884.8 | 25.3996 | 1888.2 | 4.3581 | 1890.4 | 4.2815 | 1892.7 | 3.3588
1912.3 | 13.2818 |  | 1921.2 | 5.2652 | 1926.8 | 19.8839 | 1930.3 | 4.8786 | 1932.5 | 11.9406 | 1934.7 | 2.5791
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!

## C5-C6
Open Burn Test 14 |  |  | 2006-11-29 | 11:22 |  |  | Vs = |  | 159.7912 |  | R = | 100
Mixed | 7-C | Tray F | IRMS | 1
0 | 300 kW |  | Bundle | Ch. 5 & 6 | Cable C | Odd-Even
Time-29 | N11 | N12 | Time-30 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R6-G | R5-6
39050.469 | 1 | 0 | 39050.469 | 1 | 0 |  | -195.5 | 40.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261638 | 261638 | 261637.9994
39050.4695 | 1 | 0 | 39050.4695 | 1 | 0 |  | -154 | 82 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261638 | 261638 | 261637.9994
39050.47 | 1 | 0 | 39050.47 | 1 | 0 |  | -112 | 124 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261638 | 261638 | 261637.9994
39050.4704 | 1 | 0 | 39050.4705 | 1 | 0 |  | -70 | 166 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261638 | 261638 | 261637.9994
39050.4709 | 1 | 0 | 39050.4709 | 1 | 0 |  | -27.5 | 208.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261638 | 261638 | 261637.9994
39050.4714 | 1 | 0 | 39050.4714 | 1 | 0 |  | 14 | 250 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261638 | 261638 | 261637.9994
39050.4719 | 1 | 0 | 39050.4719 | 1 | 0 |  | 56 | 292 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261638 | 261638 | 261637.9994
39050.4724 | 1 | 0 | 39050.4724 | 1 | 0 |  | 98 | 334 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261638 | 261638 | 261637.9994
39050.4729 | 1 | 0 | 39050.4729 | 1 | 0 |  | 140 | 376 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261638 | 261638 | 261637.9994
39050.4734 | 1 | 0 | 39050.4734 | 1 | 0 |  | 182 | 418 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261638 | 261638 | 261637.9994
39050.4738 | 1 | 0 | 39050.4739 | 1 | 0 |  | 224 | 460 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261638 | 261638 | 261637.9994
39050.4743 | 1 | 0 | 39050.4744 | 1 | 0 |  | 266 | 502 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261638 | 261638 | 261637.9994
39050.4748 | 1 | 0 | 39050.4748 | 1 | 0 |  | 308 | 544 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261638 | 261638 | 261637.9994
39050.4753 | 1 | 0 | 39050.4753 | 1 | 0 |  | 350 | 586 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261638 | 261638 | 261637.9994
39050.4758 | 1938 | 0 | 39050.4758 | 1 | 0 |  | 392 | 628 | 118.315 | 0 | 0.06105 | 0 | 1.1832 | 0 | 0.0006105 | 0 | 1.1832 | 0.0006105 | 35.0557 | 261638 | 33.8726
39050.4763 | 2048 | 0 | 39050.4763 | 2204 | 0 |  | 434 | 670 | 125.0305 | 0 | 134.5543 | 0 | 1.2503 | 0 | 1.3455 | 0 | 1.2503 | 1.3455 | 27.8018 | 18.7559 | 26.5515
39050.4768 | 2411 | 0 | 39050.4768 | 409 | 0 |  | 476 | 712 | 147.1917 | 0 | 24.9695 | 0 | 1.4719 | 0 | 0.24969 | 0 | 1.4719 | 0.24969 | 8.5599 | 539.9462 | 7.088
39050.4772 | 2147 | 0 | 39050.4773 | 2076 | 0 |  | 518 | 754 | 131.0745 | 0 | 126.7399 | 0 | 1.3107 | 0 | 1.2674 | 0 | 1.3107 | 1.2674 | 21.9087 | 26.078 | 20.598
39050.4777 | 2428 | 0 | 39050.4778 | 2125 | 0 |  | 560 | 796 | 148.2295 | 0 | 129.7314 | 0 | 1.4823 | 0 | 1.2973 | 0 | 1.4823 | 1.2973 | 7.7998 | 23.1708 | 6.3175
39050.4782 | 1990 | 0 | 39050.4782 | 2080 | 0 |  | 602 | 838 | 121.4896 | 0 | 126.9841 | 0 | 1.2149 | 0 | 1.2698 | 0 | 1.2149 | 1.2698 | 31.5266 | 25.8356 | 30.3117
39050.4787 | 2150 | 0 | 39050.4787 | 2323 | 0 |  | 644 | 880 | 131.2576 | 0 | 141.8193 | 0 | 1.3126 | 0 | 1.4182 | 0 | 1.3126 | 1.4182 | 21.7386 | 12.6724 | 20.426
39050.4792 | 2001 | 0 | 39050.4792 | 2200 | 0 |  | 686 | 922 | 122.1612 | 0 | 134.3101 | 0 | 1.2216 | 0 | 1.3431 | 0 | 1.2216 | 1.3431 | 30.8036 | 18.9718 | 29.582
39050.4797 | 2126 | 0 | 39050.4797 | 2031 | 0 |  | 728 | 964 | 129.7924 | 0 | 123.9927 | 0 | 1.2979 | 0 | 1.2399 | 0 | 1.2979 | 1.2399 | 23.1129 | 28.8715 | 21.815
39050.4802 | 2258 | 0 | 39050.4802 | 2441 | 0 |  | 770 | 1006 | 137.851 | 0 | 149.0232 | 0 | 1.3785 | 0 | 1.4902 | 0 | 1.3785 | 1.4902 | 15.9159 | 7.2257 | 14.5373
39050.4806 | 2062 | 0 | 39050.4807 | 2341 | 0 |  | 812 | 1048 | 125.8852 | 0 | 142.9182 | 0 | 1.2589 | 0 | 1.4292 | 0 | 1.2589 | 1.4292 | 26.934 | 11.8061 | 25.6752
39050.4811 | 2589 | 0 | 39050.4812 | 2350 | 0 |  | 854 | 1090 | 158.0586 | 0 | 143.4676 | 0 | 1.5806 | 0 | 1.4347 | 0 | 1.5806 | 1.4347 | 1.0962 | 11.3779 | 0.48441
39050.4816 | 2277 | 0 | 39050.4816 | 2546 | 0 |  | 896 | 1132 | 139.011 | 0 | 155.4335 | 0 | 1.3901 | 0 | 1.5543 | 0 | 1.3901 | 1.5543 | 14.9486 | 2.8036 | 13.5585
39050.4821 | 2423 | 0 | 39050.4821 | 2132 | 0 |  | 938 | 1174 | 147.9243 | 0 | 130.1587 | 0 | 1.4792 | 0 | 1.3016 | 0 | 1.4792 | 1.3016 | 8.0223 | 22.7664 | 6.543
39050.4826 | 2270 | 0 | 39050.4826 | 2601 | 0 |  | 980 | 1216 | 138.5836 | 0 | 158.7912 | 0 | 1.3858 | 0 | 1.5879 | 0 | 1.3858 | 1.5879 | 15.3031 | 0.62976 | 13.9172
39050.4831 | 2587 | 0 | 39050.4831 | 2554 | 0 |  | 1022 | 1258 | 157.9365 | 0 | 155.9219 | 0 | 1.5794 | 0 | 1.5592 | 0 | 1.5794 | 1.5592 | 1.1743 | 2.4816 | 0.40503
39050.4836 | 2539 | 0 | 39050.4836 | 2502 | 0 |  | 1064 | 1300 | 155.0061 | 0 | 152.7473 | 0 | 1.5501 | 0 | 1.5275 | 0 | 1.5501 | 1.5275 | 3.087 | 4.6115 | 1.537
39050.4841 | 2275 | 0 | 39050.4841 | 2511 | 0 |  | 1106 | 1342 | 138.8889 | 0 | 153.2967 | 0 | 1.3889 | 0 | 1.533 | 0 | 1.3889 | 1.533 | 15.0497 | 4.2366 | 13.6608
39050.4845 | 2515 | 0 | 39050.4846 | 2546 | 0 |  | 1148 | 1384 | 153.5409 | 0 | 155.4335 | 0 | 1.5354 | 0 | 1.5543 | 0 | 1.5354 | 1.5543 | 4.0708 | 2.8036 | 2.5354
39050.485 | 2457 | 0 | 39050.485 | 2596 | 0 |  | 1190 | 1426 | 150 | 0 | 158.486 | 0 | 1.5 | 0 | 1.5849 | 0 | 1.5 | 1.5849 | 6.5275 | 0.82357 | 5.0275
39050.4855 | 2090 | 0 | 39050.4855 | 2104 | 0 |  | 1232 | 1468 | 127.5946 | 0 | 128.4493 | 0 | 1.2759 | 0 | 1.2845 | 0 | 1.2759 | 1.2845 | 25.2335 | 24.4002 | 23.9575
39050.486 | 2364 | 0 | 39050.486 | 2556 | 0 |  | 1274 | 1510 | 144.3223 | 0 | 156.044 | 0 | 1.4432 | 0 | 1.5604 | 0 | 1.4432 | 1.5604 | 10.7183 | 2.4014 | 9.2751
39050.4865 | 2157 | 0 | 39050.4865 | 2338 | 0 |  | 1316 | 1552 | 131.685 | 0 | 142.735 | 0 | 1.3168 | 0 | 1.4274 | 0 | 1.3168 | 1.4274 | 21.3435 | 11.9495 | 20.0267
39050.487 | 2134 | 0 | 39050.487 | 2056 | 0 |  | 1358 | 1594 | 130.2808 | 0 | 125.5189 | 0 | 1.3028 | 0 | 1.2552 | 0 | 1.3028 | 1.2552 | 22.6514 | 27.3045 | 21.3486
39050.4875 | 2425 | 0 | 39050.4875 | 2357 | 0 |  | 1400 | 1636 | 148.0464 | 0 | 143.895 | 0 | 1.4805 | 0 | 1.4389 | 0 | 1.4805 | 1.4389 | 7.9332 | 11.0471 | 6.4527
39050.4879 | 2331 | 0 | 39050.488 | 2023 | 0 |  | 1442 | 1678 | 142.3077 | 0 | 123.5043 | 0 | 1.4231 | 0 | 1.235 | 0 | 1.4231 | 1.235 | 12.2857 | 29.3811 | 10.8626
39050.4884 | 2011 | 0 | 39050.4884 | 2108 | 0 |  | 1484 | 1720 | 122.7717 | 0 | 128.6935 | 0 | 1.2277 | 0 | 1.2869 | 0 | 1.2277 | 1.2869 | 30.1532 | 24.1641 | 28.9254
39050.4889 | 2132 | 0 | 39050.4889 | 2014 | 0 |  | 1526 | 1762 | 130.1587 | 0 | 122.9548 | 0 | 1.3016 | 0 | 1.2295 | 0 | 1.3016 | 1.2295 | 22.7664 | 29.9593 | 21.4648
39050.4894 | 2109 | 0 | 39050.4894 | 2320 | 0 |  | 1568 | 1804 | 128.7546 | 0 | 141.6361 | 0 | 1.2875 | 0 | 1.4164 | 0 | 1.2875 | 1.4164 | 24.1053 | 12.8181 | 22.8177
39050.4899 | 2303 | 0 | 39050.4899 | 2524 | 0 |  | 1610 | 1846 | 140.5983 | 0 | 154.0904 | 0 | 1.406 | 0 | 1.5409 | 0 | 1.406 | 1.5409 | 13.6509 | 3.6997 | 12.2449
39050.4904 | 2265 | 0 | 39050.4904 | 2320 | 0 |  | 1652 | 1888 | 138.2784 | 0 | 141.6361 | 0 | 1.3828 | 0 | 1.4164 | 0 | 1.3828 | 1.4164 | 15.5576 | 12.8181 | 14.1748
39050.4909 | 2477 | 0 | 39050.4909 | 2524 | 0 |  | 1694 | 1930 | 151.221 | 0 | 154.0904 | 0 | 1.5122 | 0 | 1.5409 | 0 | 1.5122 | 1.5409 | 5.6673 | 3.6997 | 4.1551
39050.4913 | 2115 | 0 | 39050.4914 | 2497 | 0 |  | 1736 | 1972 | 129.1209 | 0 | 152.442 | 0 | 1.2912 | 0 | 1.5244 | 0 | 1.2912 | 1.5244 | 23.7532 | 4.821 | 22.462
39050.4918 | 2360 | 0 | 39050.4919 | 2140 | 0 |  | 1778 | 2014 | 144.0781 | 0 | 130.6471 | 0 | 1.4408 | 0 | 1.3065 | 0 | 1.4408 | 1.3065 | 10.9059 | 22.3075 | 9.4652
39050.4923 | 2525 | 0 | 39050.4923 | 2535 | 0 |  | 1820 | 2056 | 154.1514 | 0 | 154.7619 | 0 | 1.5415 | 0 | 1.5476 | 0 | 1.5415 | 1.5476 | 3.6586 | 3.2497 | 2.1171
39050.4928 | 2108 | 0 | 39050.4928 | 2233 | 0 |  | 1862 | 2098 | 128.6935 | 0 | 136.3248 | 0 | 1.2869 | 0 | 1.3632 | 0 | 1.2869 | 1.3632 | 24.1641 | 17.2136 | 22.8772
39050.4933 | 2099 | 0 | 39050.4933 | 2174 | 0 |  | 1904 | 2140 | 128.1441 | 0 | 132.7228 | 0 | 1.2814 | 0 | 1.3272 | 0 | 1.2814 | 1.3272 | 24.6965 | 20.3947 | 23.4151
39050.4938 | 2101 | 0 | 39050.4938 | 1994 | 0 |  | 1946 | 2182 | 128.2662 | 0 | 121.7338 | 0 | 1.2827 | 0 | 1.2173 | 0 | 1.2827 | 1.2173 | 24.5778 | 31.2628 | 23.2952

## B4-C6
Open Burn Test 14 |  |  | 2006-11-29 | 11:22 |  |  | Vs = |  | 159.6081 |  | R = | 100
Mixed | 7-C | Tray F | IRMS | 1
0 | 300 kW |  | Bundle | Ch. 4 & 6 | Cable B | Even - | Cable C |  | Even
Time-27 | N11 | N12 | Time-28 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R6-G | R4-6
39050.469 | 1 | 0 | 39050.469 | 1 | 0 |  | -198.5 | 37.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261338 | 261338 | 261337.9994
39050.4694 | 1 | 0 | 39050.4695 | 1 | 0 |  | -156.5 | 79.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261338 | 261338 | 261337.9994
39050.4699 | 1 | 0 | 39050.4699 | 1 | 0 |  | -114.5 | 121.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261338 | 261338 | 261337.9994
39050.4704 | 1 | 0 | 39050.4704 | 1 | 0 |  | -72.5 | 163.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261338 | 261338 | 261337.9994
39050.4709 | 1 | 0 | 39050.4709 | 1 | 0 |  | -30.5 | 205.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261338 | 261338 | 261337.9994
39050.4714 | 1 | 0 | 39050.4714 | 1 | 0 |  | 11.5 | 247.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261338 | 261338 | 261337.9994
39050.4719 | 1 | 0 | 39050.4719 | 1 | 0 |  | 53.5 | 289.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261338 | 261338 | 261337.9994
39050.4724 | 1 | 0 | 39050.4724 | 1 | 0 |  | 95.5 | 331.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261338 | 261338 | 261337.9994
39050.4728 | 1 | 0 | 39050.4729 | 1 | 0 |  | 137.5 | 373.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261338 | 261338 | 261337.9994
39050.4733 | 1 | 0 | 39050.4733 | 1 | 0 |  | 179.5 | 415.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261338 | 261338 | 261337.9994
39050.4738 | 1 | 0 | 39050.4738 | 1 | 0 |  | 221.5 | 457.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261338 | 261338 | 261337.9994
39050.4743 | 1 | 0 | 39050.4743 | 1 | 0 |  | 263.5 | 499.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261338 | 261338 | 261337.9994
39050.4748 | 1 | 0 | 39050.4748 | 1 | 0 |  | 305.5 | 541.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261338 | 261338 | 261337.9994
39050.4753 | 1 | 0 | 39050.4753 | 1 | 0 |  | 347.5 | 583.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261338 | 261338 | 261337.9994
39050.4758 | 1 | 0 | 39050.4758 | 1 | 0 |  | 389.5 | 625.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261338 | 261338 | 261337.9994
39050.4762 | 1 | 0 | 39050.4763 | 2011 | 0 |  | 431.5 | 667.5 | 0.06105 | 0 | 122.7717 | 0 | 0.0006105 | 0 | 1.2277 | 0 | 0.0006105 | 1.2277 | 261338 | 30.004 | 261337.9994
39050.4767 | 1 | 0 | 39050.4767 | 1559 | 0 |  | 473.5 | 709.5 | 0.06105 | 0 | 95.177 | 0 | 0.0006105 | 0 | 0.95177 | 0 | 0.0006105 | 0.95177 | 261338 | 67.696 | 261337.9994
39050.4772 | 1358 | 0 | 39050.4772 | 2231 | 0 |  | 515.5 | 751.5 | 82.906 | 0 | 136.2027 | 0 | 0.82906 | 0 | 1.362 | 0 | 0.82906 | 1.362 | 92.5169 | 17.1842 | 91.6879
39050.4777 | 2196 | 0 | 39050.4777 | 2473 | 0 |  | 557 | 793 | 134.0659 | 0 | 150.9768 | 0 | 1.3407 | 0 | 1.5098 | 0 | 1.3407 | 1.5098 | 19.0519 | 5.7169 | 17.7113
39050.4782 | 1954 | 0 | 39050.4782 | 2228 | 0 |  | 599.5 | 835.5 | 119.2918 | 0 | 136.0195 | 0 | 1.1929 | 0 | 1.3602 | 0 | 1.1929 | 1.3602 | 33.7963 | 17.342 | 32.6034
39050.4787 | 2121 | 0 | 39050.4787 | 2034 | 0 |  | 641.5 | 877.5 | 129.4872 | 0 | 124.1758 | 0 | 1.2949 | 0 | 1.2418 | 0 | 1.2949 | 1.2418 | 23.2617 | 28.5339 | 21.9668
39050.4792 | 1920 | 0 | 39050.4792 | 2532 | 0 |  | 683.5 | 919.5 | 117.2161 | 0 | 154.5788 | 0 | 1.1722 | 0 | 1.5458 | 0 | 1.1722 | 1.5458 | 36.1656 | 3.2536 | 34.9935
39050.4797 | 2322 | 0 | 39050.4797 | 2263 | 0 |  | 725.5 | 961.5 | 141.7582 | 0 | 138.1563 | 0 | 1.4176 | 0 | 1.3816 | 0 | 1.4176 | 1.3816 | 12.5917 | 15.5272 | 11.1741
39050.4801 | 2350 | 0 | 39050.4802 | 2027 | 0 |  | 767 | 1003 | 143.4676 | 0 | 123.7485 | 0 | 1.4347 | 0 | 1.2375 | 0 | 1.4347 | 1.2375 | 11.2502 | 28.9778 | 9.8155
39050.4806 | 2377 | 0 | 39050.4806 | 2000 | 0 |  | 809 | 1045 | 145.116 | 0 | 122.1001 | 0 | 1.4512 | 0 | 1.221 | 0 | 1.4512 | 1.221 | 9.9865 | 30.719 | 8.5354
39050.4811 | 2484 | 0 | 39050.4811 | 1999 | 0 |  | 851 | 1087 | 151.6484 | 0 | 122.0391 | 0 | 1.5165 | 0 | 1.2204 | 0 | 1.5165 | 1.2204 | 5.2488 | 30.7844 | 3.7323
39050.4816 | 2376 | 0 | 39050.4816 | 2168 | 0 |  | 893.5 | 1129.5 | 145.0549 | 0 | 132.3565 | 0 | 1.4505 | 0 | 1.3236 | 0 | 1.4505 | 1.3236 | 10.0328 | 20.5895 | 8.5823
39050.4821 | 2578 | 0 | 39050.4821 | 2591 | 0 |  | 935 | 1171 | 157.3871 | 0 | 158.1807 | 0 | 1.5739 | 0 | 1.5818 | 0 | 1.5739 | 1.5818 | 1.4112 | 0.90235 | 0.1627
39050.4826 | 2368 | 0 | 39050.4826 | 2142 | 0 |  | 977.5 | 1213.5 | 144.5665 | 0 | 130.7692 | 0 | 1.4457 | 0 | 1.3077 | 0 | 1.4457 | 1.3077 | 10.4046 | 22.0532 | 8.9589
39050.4831 | 2309 | 0 | 39050.4831 | 2199 | 0 |  | 1019.5 | 1255.5 | 140.9646 | 0 | 134.2491 | 0 | 1.4096 | 0 | 1.3425 | 0 | 1.4096 | 1.3425 | 13.2256 | 18.8895 | 11.816
39050.4835 | 2083 | 0 | 39050.4836 | 2297 | 0 |  | 1061 | 1297 | 127.1673 | 0 | 140.232 | 0 | 1.2717 | 0 | 1.4023 | 0 | 1.2717 | 1.4023 | 25.5103 | 13.8172 | 24.2386
39050.484 | 2000 | 0 | 39050.484 | 1996 | 0 |  | 1103.5 | 1339.5 | 122.1001 | 0 | 121.8559 | 0 | 1.221 | 0 | 1.2186 | 0 | 1.221 | 1.2186 | 30.719 | 30.981 | 29.498
39050.4845 | 2036 | 0 | 39050.4845 | 2279 | 0 |  | 1145.5 | 1381.5 | 124.2979 | 0 | 139.1331 | 0 | 1.243 | 0 | 1.3913 | 0 | 1.243 | 1.3913 | 28.4077 | 14.7161 | 27.1647
39050.485 | 2295 | 0 | 39050.485 | 2594 | 0 |  | 1187.5 | 1423.5 | 140.1099 | 0 | 158.3639 | 0 | 1.4011 | 0 | 1.5836 | 0 | 1.4011 | 1.5836 | 13.9163 | 0.78566 | 12.5152
39050.4855 | 2301 | 0 | 39050.4855 | 2464 | 0 |  | 1229 | 1465 | 140.4762 | 0 | 150.4274 | 0 | 1.4048 | 0 | 1.5043 | 0 | 1.4048 | 1.5043 | 13.6193 | 6.1031 | 12.2145
39050.486 | 1877 | 0 | 39050.486 | 2446 | 0 |  | 1271 | 1507 | 114.591 | 0 | 149.3284 | 0 | 1.1459 | 0 | 1.4933 | 0 | 1.1459 | 1.4933 | 39.285 | 6.8839 | 38.1391
39050.4864 | 2396 | 0 | 39050.4865 | 2089 | 0 |  | 1313 | 1549 | 146.2759 | 0 | 127.5336 | 0 | 1.4628 | 0 | 1.2753 | 0 | 1.4628 | 1.2753 | 9.1144 | 25.1498 | 7.6516
39050.4869 | 2347 | 0 | 39050.487 | 2365 | 0 |  | 1355 | 1591 | 143.2845 | 0 | 144.3834 | 0 | 1.4328 | 0 | 1.4438 | 0 | 1.4328 | 1.4438 | 11.3924 | 10.5446 | 9.9596
39050.4874 | 1917 | 0 | 39050.4874 | 1983 | 0 |  | 1397 | 1633 | 117.033 | 0 | 121.0623 | 0 | 1.1703 | 0 | 1.2106 | 0 | 1.1703 | 1.2106 | 36.3787 | 31.8396 | 35.2084
39050.4879 | 2267 | 0 | 39050.4879 | 2108 | 0 |  | 1439 | 1675 | 138.4005 | 0 | 128.6935 | 0 | 1.384 | 0 | 1.2869 | 0 | 1.384 | 1.2869 | 15.3233 | 24.0218 | 13.9393
39050.4884 | 1881 | 0 | 39050.4884 | 2550 | 0 |  | 1481 | 1717 | 114.8352 | 0 | 155.6777 | 0 | 1.1484 | 0 | 1.5568 | 0 | 1.1484 | 1.5568 | 38.9888 | 2.5247 | 37.8405
39050.4889 | 2450 | 0 | 39050.4889 | 2463 | 0 |  | 1523 | 1759 | 149.5726 | 0 | 150.3663 | 0 | 1.4957 | 0 | 1.5037 | 0 | 1.4957 | 1.5037 | 6.7094 | 6.1462 | 5.2137
39050.4894 | 2376 | 0 | 39050.4894 | 2598 | 0 |  | 1565 | 1801 | 145.0549 | 0 | 158.6081 | 0 | 1.4505 | 0 | 1.5861 | 0 | 1.4505 | 1.5861 | 10.0328 | 0.63048 | 8.5823
39050.4898 | 1888 | 0 | 39050.4899 | 2155 | 0 |  | 1607 | 1843 | 115.2625 | 0 | 131.5629 | 0 | 1.1526 | 0 | 1.3156 | 0 | 1.1526 | 1.3156 | 38.4735 | 21.3169 | 37.3209
39050.4903 | 2175 | 0 | 39050.4904 | 2537 | 0 |  | 1649 | 1885 | 132.7839 | 0 | 154.884 | 0 | 1.3278 | 0 | 1.5488 | 0 | 1.3278 | 1.5488 | 20.2014 | 3.0501 | 18.8735
39050.4908 | 2353 | 0 | 39050.4908 | 2154 | 0 |  | 1691 | 1927 | 143.6508 | 0 | 131.5018 | 0 | 1.4365 | 0 | 1.315 | 0 | 1.4365 | 1.315 | 11.1084 | 21.3733 | 9.6719
39050.4913 | 1866 | 0 | 39050.4913 | 2074 | 0 |  | 1733 | 1969 | 113.9194 | 0 | 126.6178 | 0 | 1.1392 | 0 | 1.2662 | 0 | 1.1392 | 1.2662 | 40.1061 | 26.055 | 38.9669
39050.4918 | 2113 | 0 | 39050.4918 | 2284 | 0 |  | 1775 | 2011 | 128.9988 | 0 | 139.4383 | 0 | 1.29 | 0 | 1.3944 | 0 | 1.29 | 1.3944 | 23.7283 | 14.465 | 22.4384
39050.4923 | 2052 | 0 | 39050.4923 | 2463 | 0 |  | 1817 | 2053 | 125.2747 | 0 | 150.3663 | 0 | 1.2527 | 0 | 1.5037 | 0 | 1.2527 | 1.5037 | 27.4064 | 6.1462 | 26.1537
39050.4928 | 1783 | 0 | 39050.4928 | 2284 | 0 |  | 1859 | 2095 | 108.8523 | 0 | 139.4383 | 0 | 1.0885 | 0 | 1.3944 | 0 | 1.0885 | 1.3944 | 46.6282 | 14.465 | 45.5396
39050.4933 | 2158 | 0 | 39050.4933 | 1995 | 0 |  | 1901 | 2137 | 131.746 | 0 | 121.7949 | 0 | 1.3175 | 0 | 1.2179 | 0 | 1.3175 | 1.2179 | 21.1483 | 31.0466 | 19.8308
39050.4937 | 1664 | 0 | 39050.4938 | 2173 | 0 |  | 1943 | 2179 | 101.5873 | 0 | 132.6618 | 0 | 1.0159 | 0 | 1.3266 | 0 | 1.0159 | 1.3266 | 57.1142 | 20.312 | 56.0983

## B4-C5
Open Burn Test 14 |  |  | 2006-11-29 | 11:22 |  |  | Vs = |  | 158.7534 |  | R = | 100
Mixed | 7-C | Tray F | IRMS | 1
0 | 300 kW |  | Bundle | Ch. 4 & 5 | Cable B | Even - | Cable C |  | Odd
Time-25 | N11 | N12 | Time-26 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R5-G | R4-5
39050.4689 | 1 | 0 | 39050.4689 | 1 | 0 |  | -201.5 | 34.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259938 | 259938 | 259937.9994
39050.4694 | 1 | 0 | 39050.4694 | 1 | 0 |  | -159.5 | 76.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259938 | 259938 | 259937.9994
39050.4699 | 1 | 0 | 39050.4699 | 1 | 0 |  | -117.5 | 118.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259938 | 259938 | 259937.9994
39050.4704 | 1 | 0 | 39050.4704 | 1 | 0 |  | -75.5 | 160.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259938 | 259938 | 259937.9994
39050.4709 | 1 | 0 | 39050.4709 | 1 | 0 |  | -33.5 | 202.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259938 | 259938 | 259937.9994
39050.4714 | 1 | 0 | 39050.4714 | 1 | 0 |  | 8.5 | 244.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259938 | 259938 | 259937.9994
39050.4718 | 1 | 0 | 39050.4719 | 1 | 0 |  | 50.5 | 286.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259938 | 259938 | 259937.9994
39050.4723 | 1 | 0 | 39050.4723 | 1 | 0 |  | 92.5 | 328.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259938 | 259938 | 259937.9994
39050.4728 | 1 | 0 | 39050.4728 | 1 | 0 |  | 134.5 | 370.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259938 | 259938 | 259937.9994
39050.4733 | 1 | 0 | 39050.4733 | 1 | 0 |  | 176.5 | 412.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259938 | 259938 | 259937.9994
39050.4738 | 1 | 0 | 39050.4738 | 1 | 0 |  | 218.5 | 454.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259938 | 259938 | 259937.9994
39050.4743 | 1 | 0 | 39050.4743 | 1 | 0 |  | 260.5 | 496.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259938 | 259938 | 259937.9994
39050.4748 | 1 | 0 | 39050.4748 | 1 | 0 |  | 302.5 | 538.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259938 | 259938 | 259937.9994
39050.4752 | 1 | 0 | 39050.4753 | 1 | 0 |  | 344.5 | 580.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259938 | 259938 | 259937.9994
39050.4757 | 1 | 0 | 39050.4757 | 1936 | 0 |  | 386.5 | 622.5 | 0.06105 | 0 | 118.1929 | 0 | 0.0006105 | 0 | 1.1819 | 0 | 0.0006105 | 1.1819 | 259938 | 34.3171 | 259937.9994
39050.4762 | 1 | 0 | 39050.4762 | 2291 | 0 |  | 428.5 | 664.5 | 0.06105 | 0 | 139.8657 | 0 | 0.0006105 | 0 | 1.3987 | 0 | 0.0006105 | 1.3987 | 259938 | 13.5041 | 259937.9994
39050.4767 | 1 | 0 | 39050.4767 | 2092 | 0 |  | 470.5 | 706.5 | 0.06105 | 0 | 127.7167 | 0 | 0.0006105 | 0 | 1.2772 | 0 | 0.0006105 | 1.2772 | 259938 | 24.3011 | 259937.9994
39050.4772 | 1021 | 0 | 39050.4772 | 2197 | 0 |  | 512.5 | 748.5 | 62.3321 | 0 | 134.127 | 0 | 0.62332 | 0 | 1.3413 | 0 | 0.62332 | 1.3413 | 154.6895 | 18.3605 | 154.0662
39050.4777 | 2242 | 0 | 39050.4777 | 2181 | 0 |  | 554.5 | 790.5 | 136.8742 | 0 | 133.1502 | 0 | 1.3687 | 0 | 1.3315 | 0 | 1.3687 | 1.3315 | 15.9848 | 19.2288 | 14.6161
39050.4782 | 1914 | 0 | 39050.4782 | 2158 | 0 |  | 596.5 | 832.5 | 116.8498 | 0 | 131.746 | 0 | 1.1685 | 0 | 1.3175 | 0 | 1.1685 | 1.3175 | 35.861 | 20.4995 | 34.6925
39050.4786 | 2438 | 0 | 39050.4787 | 2014 | 0 |  | 638.5 | 874.5 | 148.84 | 0 | 122.9548 | 0 | 1.4884 | 0 | 1.2295 | 0 | 1.4884 | 1.2295 | 6.6604 | 29.1152 | 5.172
39050.4791 | 2113 | 0 | 39050.4791 | 2449 | 0 |  | 680.5 | 916.5 | 128.9988 | 0 | 149.5116 | 0 | 1.29 | 0 | 1.4951 | 0 | 1.29 | 1.4951 | 23.0658 | 6.1813 | 21.7758
39050.4796 | 1836 | 0 | 39050.4796 | 2270 | 0 |  | 722.5 | 958.5 | 112.0879 | 0 | 138.5836 | 0 | 1.1209 | 0 | 1.3858 | 0 | 1.1209 | 1.3858 | 41.6329 | 14.5542 | 40.512
39050.4801 | 2215 | 0 | 39050.4801 | 2481 | 0 |  | 764.5 | 1000.5 | 135.2259 | 0 | 151.4652 | 0 | 1.3523 | 0 | 1.5147 | 0 | 1.3523 | 1.5147 | 17.3986 | 4.8118 | 16.0464
39050.4806 | 2415 | 0 | 39050.4806 | 2566 | 0 |  | 806.5 | 1042.5 | 147.4359 | 0 | 156.6545 | 0 | 1.4744 | 0 | 1.5665 | 0 | 1.4744 | 1.5665 | 7.6762 | 1.3398 | 6.2018
39050.4811 | 2016 | 0 | 39050.4811 | 2266 | 0 |  | 848.5 | 1084.5 | 123.0769 | 0 | 138.3394 | 0 | 1.2308 | 0 | 1.3834 | 0 | 1.2308 | 1.3834 | 28.9871 | 14.7564 | 27.7563
39050.4816 | 2021 | 0 | 39050.4816 | 2100 | 0 |  | 890.5 | 1126.5 | 123.3822 | 0 | 128.2051 | 0 | 1.2338 | 0 | 1.2821 | 0 | 1.2338 | 1.2821 | 28.668 | 23.8276 | 27.4342
39050.482 | 2214 | 0 | 39050.4821 | 2169 | 0 |  | 932.5 | 1168.5 | 135.1648 | 0 | 132.4176 | 0 | 1.3516 | 0 | 1.3242 | 0 | 1.3516 | 1.3242 | 17.4517 | 19.8884 | 16.1
39050.4825 | 1966 | 0 | 39050.4825 | 2184 | 0 |  | 974.5 | 1210.5 | 120.0244 | 0 | 133.3333 | 0 | 1.2002 | 0 | 1.3333 | 0 | 1.2002 | 1.3333 | 32.2675 | 19.065 | 31.0673
39050.483 | 2238 | 0 | 39050.483 | 2483 | 0 |  | 1016.5 | 1252.5 | 136.63 | 0 | 151.5873 | 0 | 1.3663 | 0 | 1.5159 | 0 | 1.3663 | 1.5159 | 16.1921 | 4.7273 | 14.8258
39050.4835 | 2434 | 0 | 39050.4835 | 2404 | 0 |  | 1058.5 | 1294.5 | 148.5958 | 0 | 146.7643 | 0 | 1.486 | 0 | 1.4676 | 0 | 1.486 | 1.4676 | 6.8357 | 8.1689 | 5.3497
39050.484 | 2447 | 0 | 39050.484 | 2087 | 0 |  | 1100.5 | 1336.5 | 149.3895 | 0 | 127.4115 | 0 | 1.4939 | 0 | 1.2741 | 0 | 1.4939 | 1.2741 | 6.2681 | 24.5989 | 4.7742
39050.4845 | 2336 | 0 | 39050.4845 | 2316 | 0 |  | 1142.5 | 1378.5 | 142.6129 | 0 | 141.3919 | 0 | 1.4261 | 0 | 1.4139 | 0 | 1.4261 | 1.4139 | 11.3176 | 12.2789 | 9.8915
39050.485 | 2394 | 0 | 39050.485 | 2055 | 0 |  | 1184.5 | 1420.5 | 146.1538 | 0 | 125.4579 | 0 | 1.4615 | 0 | 1.2546 | 0 | 1.4615 | 1.2546 | 8.6207 | 26.5392 | 7.1592
39050.4855 | 2190 | 0 | 39050.4855 | 2568 | 0 |  | 1226.5 | 1462.5 | 133.6996 | 0 | 156.7766 | 0 | 1.337 | 0 | 1.5678 | 0 | 1.337 | 1.5678 | 18.7388 | 1.2609 | 17.4018
39050.4859 | 2081 | 0 | 39050.4859 | 2553 | 0 |  | 1268.5 | 1504.5 | 127.0452 | 0 | 155.8608 | 0 | 1.2705 | 0 | 1.5586 | 0 | 1.2705 | 1.5586 | 24.9582 | 1.8559 | 23.6877
39050.4864 | 2403 | 0 | 39050.4864 | 2321 | 0 |  | 1310.5 | 1546.5 | 146.7033 | 0 | 141.6972 | 0 | 1.467 | 0 | 1.417 | 0 | 1.467 | 1.417 | 8.2139 | 12.0371 | 6.7469
39050.4869 | 1929 | 0 | 39050.4869 | 2053 | 0 |  | 1352.5 | 1588.5 | 117.7656 | 0 | 125.3358 | 0 | 1.1777 | 0 | 1.2534 | 0 | 1.1777 | 1.2534 | 34.8046 | 26.6624 | 33.6269
39050.4874 | 2029 | 0 | 39050.4874 | 2400 | 0 |  | 1394.5 | 1630.5 | 123.8706 | 0 | 146.5201 | 0 | 1.2387 | 0 | 1.4652 | 0 | 1.2387 | 1.4652 | 28.1607 | 8.3492 | 26.922
39050.4879 | 2176 | 0 | 39050.4879 | 2233 | 0 |  | 1436.5 | 1672.5 | 132.8449 | 0 | 136.3248 | 0 | 1.3284 | 0 | 1.3632 | 0 | 1.3284 | 1.3632 | 19.5028 | 16.4523 | 18.1743
39050.4884 | 2292 | 0 | 39050.4884 | 2584 | 0 |  | 1478.5 | 1714.5 | 139.9267 | 0 | 157.7534 | 0 | 1.3993 | 0 | 1.5775 | 0 | 1.3993 | 1.5775 | 13.4546 | 0.6339 | 12.0554
39050.4889 | 2357 | 0 | 39050.4889 | 2218 | 0 |  | 1520.5 | 1756.5 | 143.895 | 0 | 135.409 | 0 | 1.4389 | 0 | 1.3541 | 0 | 1.4389 | 1.3541 | 10.3258 | 17.2399 | 8.8869
39050.4893 | 2110 | 0 | 39050.4894 | 2441 | 0 |  | 1562.5 | 1798.5 | 128.8156 | 0 | 149.0232 | 0 | 1.2882 | 0 | 1.4902 | 0 | 1.2882 | 1.4902 | 23.2408 | 6.5293 | 21.9526
39050.4898 | 1972 | 0 | 39050.4898 | 2153 | 0 |  | 1604.5 | 1840.5 | 120.3907 | 0 | 131.4408 | 0 | 1.2039 | 0 | 1.3144 | 0 | 1.2039 | 1.3144 | 31.8651 | 20.7794 | 30.6612
39050.4903 | 1842 | 0 | 39050.4903 | 2550 | 0 |  | 1646.5 | 1882.5 | 112.4542 | 0 | 155.6777 | 0 | 1.1245 | 0 | 1.5568 | 0 | 1.1245 | 1.5568 | 41.1716 | 1.9757 | 40.047
39050.4908 | 2362 | 0 | 39050.4908 | 2023 | 0 |  | 1688.5 | 1924.5 | 144.2002 | 0 | 123.5043 | 0 | 1.442 | 0 | 1.235 | 0 | 1.442 | 1.235 | 10.0923 | 28.5408 | 8.6503
39050.4913 | 2127 | 0 | 39050.4913 | 2500 | 0 |  | 1730.5 | 1966.5 | 129.8535 | 0 | 152.6252 | 0 | 1.2985 | 0 | 1.5263 | 0 | 1.2985 | 1.5263 | 22.2558 | 4.0152 | 20.9572
39050.4918 | 1790 | 0 | 39050.4918 | 2155 | 0 |  | 1772.5 | 2008.5 | 109.2796 | 0 | 131.5629 | 0 | 1.0928 | 0 | 1.3156 | 0 | 1.0928 | 1.3156 | 45.2726 | 20.6673 | 44.1798
39050.4923 | 1747 | 0 | 39050.4923 | 2146 | 0 |  | 1814.5 | 2050.5 | 106.6545 | 0 | 131.0134 | 0 | 1.0665 | 0 | 1.3101 | 0 | 1.0665 | 1.3101 | 48.8483 | 21.1733 | 47.7818
39050.4927 | 2109 | 0 | 39050.4928 | 2307 | 0 |  | 1856.5 | 2092.5 | 128.7546 | 0 | 140.8425 | 0 | 1.2875 | 0 | 1.4084 | 0 | 1.2875 | 1.4084 | 23.2992 | 12.7169 | 22.0116
39050.4932 | 1796 | 0 | 39050.4932 | 2096 | 0 |  | 1898 | 2134 | 109.6459 | 0 | 127.9609 | 0 | 1.0965 | 0 | 1.2796 | 0 | 1.0965 | 1.2796 | 44.7873 | 24.0639 | 43.6908
39050.4937 | 2028 | 0 | 39050.4937 | 2323 | 0 |  | 1940.5 | 2176.5 | 123.8095 | 0 | 141.8193 | 0 | 1.2381 | 0 | 1.4182 | 0 | 1.2381 | 1.4182 | 28.2239 | 11.9406 | 26.9858

## B3-C6
Open Burn Test 14 |  |  | 2006-11-29 | 11:22 |  |  | Vs = |  | 158.7534 |  | R = | 100
Mixed | 7-C | Tray F | IRMS | 1
0 | 300 kW |  | Bundle | Ch. 3 & 6 | Cable B | Odd - | Cable C |  | Even
Time-23 | N11 | N12 | Time-24 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R6-G | R3-6
39050.4689 | 1 | 0 | 39050.4689 | 1 | 0 |  | -204 | 32 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259938 | 259938 | 259937.9994
39050.4694 | 1 | 0 | 39050.4694 | 1 | 0 |  | -162.5 | 73.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259938 | 259938 | 259937.9994
39050.4699 | 1 | 0 | 39050.4699 | 1 | 0 |  | -120.5 | 115.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259938 | 259938 | 259937.9994
39050.4703 | 1 | 0 | 39050.4704 | 1 | 0 |  | -78.5 | 157.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259938 | 259938 | 259937.9994
39050.4708 | 1 | 0 | 39050.4708 | 1 | 0 |  | -36.5 | 199.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259938 | 259938 | 259937.9994
39050.4713 | 1 | 0 | 39050.4713 | 1 | 0 |  | 5.5 | 241.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259938 | 259938 | 259937.9994
39050.4718 | 1 | 0 | 39050.4718 | 1 | 0 |  | 47.5 | 283.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259938 | 259938 | 259937.9994
39050.4723 | 1 | 0 | 39050.4723 | 1 | 0 |  | 89.5 | 325.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259938 | 259938 | 259937.9994
39050.4728 | 1 | 0 | 39050.4728 | 1 | 0 |  | 131.5 | 367.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259938 | 259938 | 259937.9994
39050.4733 | 1 | 0 | 39050.4733 | 1 | 0 |  | 173.5 | 409.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259938 | 259938 | 259937.9994
39050.4737 | 1 | 0 | 39050.4738 | 1 | 0 |  | 215.5 | 451.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259938 | 259938 | 259937.9994
39050.4742 | 1 | 0 | 39050.4742 | 1 | 0 |  | 257.5 | 493.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259938 | 259938 | 259937.9994
39050.4747 | 1 | 0 | 39050.4747 | 1 | 0 |  | 299.5 | 535.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259938 | 259938 | 259937.9994
39050.4752 | 1 | 0 | 39050.4752 | 1 | 0 |  | 341.5 | 577.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259938 | 259938 | 259937.9994
39050.4757 | 1 | 0 | 39050.4757 | 1 | 0 |  | 383.5 | 619.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259938 | 259938 | 259937.9994
39050.4762 | 1 | 0 | 39050.4762 | 1982 | 0 |  | 425.5 | 661.5 | 0.06105 | 0 | 121.0012 | 0 | 0.0006105 | 0 | 1.21 | 0 | 0.0006105 | 1.21 | 259938 | 31.1998 | 259937.9994
39050.4767 | 1921 | 0 | 39050.4767 | 2242 | 0 |  | 467.5 | 703.5 | 117.2772 | 0 | 136.8742 | 0 | 1.1728 | 0 | 1.3687 | 0 | 1.1728 | 1.3687 | 35.366 | 15.9848 | 34.1932
39050.4772 | 298 | 0 | 39050.4772 | 2146 | 0 |  | 509.5 | 745.5 | 18.1929 | 0 | 131.0134 | 0 | 0.18193 | 0 | 1.3101 | 0 | 0.18193 | 1.3101 | 772.6107 | 21.1733 | 772.4288
39050.4776 | 2001 | 0 | 39050.4777 | 2471 | 0 |  | 551.5 | 787.5 | 122.1612 | 0 | 150.8547 | 0 | 1.2216 | 0 | 1.5085 | 0 | 1.2216 | 1.5085 | 29.954 | 5.2359 | 28.7324
39050.4781 | 2267 | 0 | 39050.4781 | 2247 | 0 |  | 593.5 | 829.5 | 138.4005 | 0 | 137.1795 | 0 | 1.384 | 0 | 1.3718 | 0 | 1.384 | 1.3718 | 14.7058 | 15.7267 | 13.3218
39050.4786 | 2469 | 0 | 39050.4786 | 2336 | 0 |  | 635.5 | 871.5 | 150.7326 | 0 | 142.6129 | 0 | 1.5073 | 0 | 1.4261 | 0 | 1.5073 | 1.4261 | 5.3212 | 11.3176 | 3.8139
39050.4791 | 1987 | 0 | 39050.4791 | 2515 | 0 |  | 677.5 | 913.5 | 121.3065 | 0 | 153.5409 | 0 | 1.2131 | 0 | 1.5354 | 0 | 1.2131 | 1.5354 | 30.8697 | 3.3948 | 29.6566
39050.4796 | 2170 | 0 | 39050.4796 | 2284 | 0 |  | 719.5 | 955.5 | 132.4786 | 0 | 139.4383 | 0 | 1.3248 | 0 | 1.3944 | 0 | 1.3248 | 1.3944 | 19.8332 | 13.852 | 18.5084
39050.4801 | 2185 | 0 | 39050.4801 | 2043 | 0 |  | 761.5 | 997.5 | 133.3944 | 0 | 124.7253 | 0 | 1.3339 | 0 | 1.2473 | 0 | 1.3339 | 1.2473 | 19.0105 | 27.2824 | 17.6766
39050.4806 | 2088 | 0 | 39050.4806 | 2549 | 0 |  | 803.5 | 1039.5 | 127.4725 | 0 | 155.6166 | 0 | 1.2747 | 0 | 1.5562 | 0 | 1.2747 | 1.5562 | 24.5393 | 2.0157 | 23.2645
39050.481 | 2398 | 0 | 39050.4811 | 2256 | 0 |  | 845.5 | 1081.5 | 146.398 | 0 | 137.7289 | 0 | 1.464 | 0 | 1.3773 | 0 | 1.464 | 1.3773 | 8.4395 | 15.2651 | 6.9756
39050.4815 | 2468 | 0 | 39050.4815 | 2528 | 0 |  | 887.5 | 1123.5 | 150.6716 | 0 | 154.3346 | 0 | 1.5067 | 0 | 1.5433 | 0 | 1.5067 | 1.5433 | 5.3639 | 2.8631 | 3.8571
39050.482 | 2310 | 0 | 39050.482 | 2212 | 0 |  | 929.5 | 1165.5 | 141.0256 | 0 | 135.0427 | 0 | 1.4103 | 0 | 1.3504 | 0 | 1.4103 | 1.3504 | 12.5706 | 17.5579 | 11.1603
39050.4825 | 2164 | 0 | 39050.4825 | 2081 | 0 |  | 971.5 | 1207.5 | 132.1123 | 0 | 127.0452 | 0 | 1.3211 | 0 | 1.2705 | 0 | 1.3211 | 1.2705 | 20.1654 | 24.9582 | 18.8443
39050.483 | 2163 | 0 | 39050.483 | 2139 | 0 |  | 1013.5 | 1249.5 | 132.0513 | 0 | 130.5861 | 0 | 1.3205 | 0 | 1.3059 | 0 | 1.3205 | 1.3059 | 20.221 | 21.5699 | 18.9005
39050.4835 | 2434 | 0 | 39050.4835 | 2017 | 0 |  | 1055.5 | 1291.5 | 148.5958 | 0 | 123.138 | 0 | 1.486 | 0 | 1.2314 | 0 | 1.486 | 1.2314 | 6.8357 | 28.9232 | 5.3497
39050.484 | 2146 | 0 | 39050.484 | 2538 | 0 |  | 1097.5 | 1333.5 | 131.0134 | 0 | 154.9451 | 0 | 1.3101 | 0 | 1.5495 | 0 | 1.3101 | 1.5495 | 21.1733 | 2.4578 | 19.8632
39050.4844 | 2410 | 0 | 39050.4845 | 2030 | 0 |  | 1139.5 | 1375.5 | 147.1306 | 0 | 123.9316 | 0 | 1.4713 | 0 | 1.2393 | 0 | 1.4713 | 1.2393 | 7.8996 | 28.0975 | 6.4283
39050.4849 | 2006 | 0 | 39050.4849 | 2560 | 0 |  | 1181.5 | 1417.5 | 122.4664 | 0 | 156.2882 | 0 | 1.2247 | 0 | 1.5629 | 0 | 1.2247 | 1.5629 | 29.6301 | 1.5773 | 28.4054
39050.4854 | 2099 | 0 | 39050.4854 | 2042 | 0 |  | 1223.5 | 1459.5 | 128.1441 | 0 | 124.6642 | 0 | 1.2814 | 0 | 1.2466 | 0 | 1.2814 | 1.2466 | 23.8866 | 27.3448 | 22.6052
39050.4859 | 1793 | 0 | 39050.4859 | 2260 | 0 |  | 1265.5 | 1501.5 | 109.4628 | 0 | 137.9731 | 0 | 1.0946 | 0 | 1.3797 | 0 | 1.0946 | 1.3797 | 45.0296 | 15.0611 | 43.9349
39050.4864 | 1862 | 0 | 39050.4864 | 2400 | 0 |  | 1307.5 | 1543.5 | 113.6752 | 0 | 146.5201 | 0 | 1.1368 | 0 | 1.4652 | 0 | 1.1368 | 1.4652 | 39.6552 | 8.3492 | 38.5185
39050.4869 | 2092 | 0 | 39050.4869 | 1991 | 0 |  | 1349.5 | 1585.5 | 127.7167 | 0 | 121.5507 | 0 | 1.2772 | 0 | 1.2155 | 0 | 1.2772 | 1.2155 | 24.3011 | 30.6067 | 23.024
39050.4874 | 1887 | 0 | 39050.4874 | 1986 | 0 |  | 1391.5 | 1627.5 | 115.2015 | 0 | 121.2454 | 0 | 1.152 | 0 | 1.2125 | 0 | 1.152 | 1.2125 | 37.805 | 30.9355 | 36.653
39050.4878 | 1896 | 0 | 39050.4879 | 2401 | 0 |  | 1433.5 | 1669.5 | 115.7509 | 0 | 146.5812 | 0 | 1.1575 | 0 | 1.4658 | 0 | 1.1575 | 1.4658 | 37.1508 | 8.304 | 35.9933
39050.4883 | 1892 | 0 | 39050.4883 | 2200 | 0 |  | 1475.5 | 1711.5 | 115.5067 | 0 | 134.3101 | 0 | 1.1551 | 0 | 1.3431 | 0 | 1.1551 | 1.3431 | 37.4408 | 18.1991 | 36.2857
39050.4888 | 2095 | 0 | 39050.4888 | 2327 | 0 |  | 1517.5 | 1753.5 | 127.8999 | 0 | 142.0635 | 0 | 1.279 | 0 | 1.4206 | 0 | 1.279 | 1.4206 | 24.1232 | 11.7482 | 22.8442
39050.4893 | 2179 | 0 | 39050.4893 | 2577 | 0 |  | 1559.5 | 1795.5 | 133.0281 | 0 | 157.326 | 0 | 1.3303 | 0 | 1.5733 | 0 | 1.3303 | 1.5733 | 19.3382 | 0.90726 | 18.0079
39050.4898 | 2156 | 0 | 39050.4898 | 2153 | 0 |  | 1601.5 | 1837.5 | 131.6239 | 0 | 131.4408 | 0 | 1.3162 | 0 | 1.3144 | 0 | 1.3162 | 1.3144 | 20.6113 | 20.7794 | 19.2951
39050.4903 | 1984 | 0 | 39050.4903 | 2195 | 0 |  | 1643.5 | 1879.5 | 121.1233 | 0 | 134.0049 | 0 | 1.2112 | 0 | 1.34 | 0 | 1.2112 | 1.34 | 31.0675 | 18.4683 | 29.8563
39050.4908 | 1983 | 0 | 39050.4908 | 2000 | 0 |  | 1685.5 | 1921.5 | 121.0623 | 0 | 122.1001 | 0 | 1.2106 | 0 | 1.221 | 0 | 1.2106 | 1.221 | 31.1336 | 30.019 | 29.923
39050.4912 | 2205 | 0 | 39050.4913 | 2246 | 0 |  | 1727.5 | 1963.5 | 134.6154 | 0 | 137.1184 | 0 | 1.3462 | 0 | 1.3712 | 0 | 1.3462 | 1.3712 | 17.9311 | 15.7783 | 16.5849
39050.4917 | 1812 | 0 | 39050.4917 | 2584 | 0 |  | 1769.5 | 2005.5 | 110.6227 | 0 | 157.7534 | 0 | 1.1062 | 0 | 1.5775 | 0 | 1.1062 | 1.5775 | 43.5088 | 0.6339 | 42.4026
39050.4922 | 2088 | 0 | 39050.4922 | 2211 | 0 |  | 1811.5 | 2047.5 | 127.4725 | 0 | 134.9817 | 0 | 1.2747 | 0 | 1.3498 | 0 | 1.2747 | 1.3498 | 24.5393 | 17.611 | 23.2645
39050.4927 | 1849 | 0 | 39050.4927 | 2366 | 0 |  | 1853.5 | 2089.5 | 112.8816 | 0 | 144.4444 | 0 | 1.1288 | 0 | 1.4444 | 0 | 1.1288 | 1.4444 | 40.6371 | 9.9062 | 39.5083
39050.4932 | 1951 | 0 | 39050.4932 | 2032 | 0 |  | 1895.5 | 2131.5 | 119.1087 | 0 | 124.0537 | 0 | 1.1911 | 0 | 1.2405 | 0 | 1.1911 | 1.2405 | 33.2845 | 27.9715 | 32.0934
39050.4937 | 1954 | 0 | 39050.4937 | 2535 | 0 |  | 1937.5 | 2173.5 | 119.2918 | 0 | 154.7619 | 0 | 1.1929 | 0 | 1.5476 | 0 | 1.1929 | 1.5476 | 33.0798 | 2.5791 | 31.8869

## B3-C5
Open Burn Test 14 |  |  | 2006-11-29 | 11:22 |  |  | Vs = |  | 159.6081 |  | R = | 100
Mixed | 7-C | Tray F | IRMS | 1
0 | 300 kW |  | Bundle | Ch. 3 & 5 | Cable B | Odd - | Cable C |  | Odd
Time-21 | N11 | N12 | Time-22 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R5-G | R3-5
39050.4689 | 1 | 0 | 39050.4689 | 1 | 0 |  | -207 | 29 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261338 | 261338 | 261337.9994
39050.4693 | 1 | 0 | 39050.4694 | 1 | 0 |  | -165 | 71 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261338 | 261338 | 261337.9994
39050.4698 | 1 | 0 | 39050.4698 | 1 | 0 |  | -123 | 113 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261338 | 261338 | 261337.9994
39050.4703 | 1 | 0 | 39050.4703 | 1 | 0 |  | -81 | 155 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261338 | 261338 | 261337.9994
39050.4708 | 1 | 0 | 39050.4708 | 1 | 0 |  | -39 | 197 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261338 | 261338 | 261337.9994
39050.4713 | 1 | 0 | 39050.4713 | 1 | 0 |  | 3 | 239 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261338 | 261338 | 261337.9994
39050.4718 | 1 | 0 | 39050.4718 | 1 | 0 |  | 45 | 281 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261338 | 261338 | 261337.9994
39050.4723 | 1 | 0 | 39050.4723 | 1 | 0 |  | 87 | 323 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261338 | 261338 | 261337.9994
39050.4727 | 1 | 0 | 39050.4728 | 1 | 0 |  | 129 | 365 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261338 | 261338 | 261337.9994
39050.4732 | 1 | 0 | 39050.4733 | 1 | 0 |  | 171 | 407 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261338 | 261338 | 261337.9994
39050.4737 | 1 | 0 | 39050.4737 | 1 | 0 |  | 213 | 449 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261338 | 261338 | 261337.9994
39050.4742 | 1 | 0 | 39050.4742 | 1 | 0 |  | 255 | 491 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261338 | 261338 | 261337.9994
39050.4747 | 1 | 0 | 39050.4747 | 1 | 0 |  | 297 | 533 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261338 | 261338 | 261337.9994
39050.4752 | 1 | 0 | 39050.4752 | 1 | 0 |  | 339 | 575 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261338 | 261338 | 261337.9994
39050.4757 | 1 | 0 | 39050.4757 | 3 | 0 |  | 381 | 617 | 0.06105 | 0 | 0.18315 | 0 | 0.0006105 | 0 | 0.0018315 | 0 | 0.0006105 | 0.0018315 | 261338 | 87046 | 261337.9994
39050.4761 | 1 | 0 | 39050.4762 | 2496 | 0 |  | 423 | 659 | 0.06105 | 0 | 152.381 | 0 | 0.0006105 | 0 | 1.5238 | 0 | 0.0006105 | 1.5238 | 261338 | 4.7428 | 261337.9994
39050.4766 | 2275 | 0 | 39050.4767 | 2007 | 0 |  | 465 | 701 | 138.8889 | 0 | 122.5275 | 0 | 1.3889 | 0 | 1.2253 | 0 | 1.3889 | 1.2253 | 14.9178 | 30.2631 | 13.5289
39050.4771 | 1652 | 0 | 39050.4771 | 2207 | 0 |  | 507 | 743 | 100.8547 | 0 | 134.7375 | 0 | 1.0085 | 0 | 1.3474 | 0 | 1.0085 | 1.3474 | 58.2554 | 18.4585 | 57.2469
39050.4776 | 2078 | 0 | 39050.4776 | 1987 | 0 |  | 549 | 785 | 126.862 | 0 | 121.3065 | 0 | 1.2686 | 0 | 1.2131 | 0 | 1.2686 | 1.2131 | 25.8123 | 31.5742 | 24.5437
39050.4781 | 2352 | 0 | 39050.4781 | 2598 | 0 |  | 591 | 827 | 143.5897 | 0 | 158.6081 | 0 | 1.4359 | 0 | 1.5861 | 0 | 1.4359 | 1.5861 | 11.1556 | 0.63048 | 9.7197
39050.4786 | 2033 | 0 | 39050.4786 | 2430 | 0 |  | 633 | 869 | 124.1148 | 0 | 148.3516 | 0 | 1.2411 | 0 | 1.4835 | 0 | 1.2411 | 1.4835 | 28.5971 | 7.5877 | 27.356
39050.4791 | 2283 | 0 | 39050.4791 | 2265 | 0 |  | 675 | 911 | 139.3773 | 0 | 138.2784 | 0 | 1.3938 | 0 | 1.3828 | 0 | 1.3938 | 1.3828 | 14.5151 | 15.4252 | 13.1213
39050.4795 | 2069 | 0 | 39050.4796 | 2169 | 0 |  | 716.5 | 952.5 | 126.3126 | 0 | 132.4176 | 0 | 1.2631 | 0 | 1.3242 | 0 | 1.2631 | 1.3242 | 26.3596 | 20.5339 | 25.0965
39050.48 | 2474 | 0 | 39050.4801 | 2426 | 0 |  | 759 | 995 | 151.0379 | 0 | 148.1074 | 0 | 1.5104 | 0 | 1.4811 | 0 | 1.5104 | 1.4811 | 5.6742 | 7.765 | 4.1638
39050.4805 | 2410 | 0 | 39050.4805 | 2423 | 0 |  | 801 | 1037 | 147.1306 | 0 | 147.9243 | 0 | 1.4713 | 0 | 1.4792 | 0 | 1.4713 | 1.4792 | 8.4805 | 7.8985 | 7.0092
39050.481 | 2090 | 0 | 39050.481 | 2223 | 0 |  | 843 | 1079 | 127.5946 | 0 | 135.7143 | 0 | 1.2759 | 0 | 1.3571 | 0 | 1.2759 | 1.3571 | 25.09 | 17.6059 | 23.814
39050.4815 | 2421 | 0 | 39050.4815 | 2440 | 0 |  | 885 | 1121 | 147.8022 | 0 | 148.9621 | 0 | 1.478 | 0 | 1.4896 | 0 | 1.478 | 1.4896 | 7.9876 | 7.1467 | 6.5096
39050.482 | 2158 | 0 | 39050.482 | 2259 | 0 |  | 926.5 | 1162.5 | 131.746 | 0 | 137.9121 | 0 | 1.3175 | 0 | 1.3791 | 0 | 1.3175 | 1.3791 | 21.1483 | 15.7317 | 19.8308
39050.4825 | 2053 | 0 | 39050.4825 | 2285 | 0 |  | 969 | 1205 | 125.3358 | 0 | 139.4994 | 0 | 1.2534 | 0 | 1.395 | 0 | 1.2534 | 1.395 | 27.3444 | 14.4149 | 26.091
39050.483 | 2095 | 0 | 39050.483 | 2232 | 0 |  | 1011 | 1247 | 127.8999 | 0 | 136.2637 | 0 | 1.279 | 0 | 1.3626 | 0 | 1.279 | 1.3626 | 24.7914 | 17.1317 | 23.5124
39050.4834 | 2409 | 0 | 39050.4835 | 2385 | 0 |  | 1053 | 1289 | 147.0696 | 0 | 145.6044 | 0 | 1.4707 | 0 | 1.456 | 0 | 1.4707 | 1.456 | 8.5255 | 9.6176 | 7.0548
39050.4839 | 2133 | 0 | 39050.4839 | 2010 | 0 |  | 1094.5 | 1330.5 | 130.2198 | 0 | 122.7106 | 0 | 1.3022 | 0 | 1.2271 | 0 | 1.3022 | 1.2271 | 22.5682 | 30.0687 | 21.266
39050.4844 | 2109 | 0 | 39050.4844 | 2471 | 0 |  | 1136.5 | 1372.5 | 128.7546 | 0 | 150.8547 | 0 | 1.2875 | 0 | 1.5085 | 0 | 1.2875 | 1.5085 | 23.963 | 5.8025 | 22.6755
39050.4849 | 1800 | 0 | 39050.4849 | 2439 | 0 |  | 1178.5 | 1414.5 | 109.8901 | 0 | 148.9011 | 0 | 1.0989 | 0 | 1.489 | 0 | 1.0989 | 1.489 | 45.2433 | 7.1907 | 44.1444
39050.4854 | 1732 | 0 | 39050.4854 | 2587 | 0 |  | 1220.5 | 1456.5 | 105.7387 | 0 | 157.9365 | 0 | 1.0574 | 0 | 1.5794 | 0 | 1.0574 | 1.5794 | 50.9457 | 1.0584 | 49.8883
39050.4859 | 2214 | 0 | 39050.4859 | 2537 | 0 |  | 1262.5 | 1498.5 | 135.1648 | 0 | 154.884 | 0 | 1.3516 | 0 | 1.5488 | 0 | 1.3516 | 1.5488 | 18.084 | 3.0501 | 16.7324
39050.4864 | 1812 | 0 | 39050.4864 | 2016 | 0 |  | 1304.5 | 1540.5 | 110.6227 | 0 | 123.0769 | 0 | 1.1062 | 0 | 1.2308 | 0 | 1.1062 | 1.2308 | 44.2815 | 29.6815 | 43.1752
39050.4868 | 1762 | 0 | 39050.4869 | 2052 | 0 |  | 1346.5 | 1582.5 | 107.5702 | 0 | 125.2747 | 0 | 1.0757 | 0 | 1.2527 | 0 | 1.0757 | 1.2527 | 48.3757 | 27.4064 | 47.3
39050.4873 | 2160 | 0 | 39050.4873 | 2345 | 0 |  | 1388.5 | 1624.5 | 131.8681 | 0 | 143.1624 | 0 | 1.3187 | 0 | 1.4316 | 0 | 1.3187 | 1.4316 | 21.0361 | 11.4874 | 19.7174
39050.4878 | 2352 | 0 | 39050.4878 | 2444 | 0 |  | 1430.5 | 1666.5 | 143.5897 | 0 | 149.2063 | 0 | 1.4359 | 0 | 1.4921 | 0 | 1.4359 | 1.4921 | 11.1556 | 6.9714 | 9.7197
39050.4883 | 1852 | 0 | 39050.4883 | 2123 | 0 |  | 1472.5 | 1708.5 | 113.0647 | 0 | 129.6093 | 0 | 1.1306 | 0 | 1.2961 | 0 | 1.1306 | 1.2961 | 41.1652 | 23.1455 | 40.0346
39050.4888 | 1992 | 0 | 39050.4888 | 2014 | 0 |  | 1514.5 | 1750.5 | 121.6117 | 0 | 122.9548 | 0 | 1.2161 | 0 | 1.2295 | 0 | 1.2161 | 1.2295 | 31.244 | 29.8103 | 30.0279
39050.4893 | 2245 | 0 | 39050.4893 | 2450 | 0 |  | 1556.5 | 1792.5 | 137.0574 | 0 | 149.5726 | 0 | 1.3706 | 0 | 1.4957 | 0 | 1.3706 | 1.4957 | 16.4535 | 6.7094 | 15.0829
39050.4898 | 2210 | 0 | 39050.4898 | 2469 | 0 |  | 1598.5 | 1834.5 | 134.9206 | 0 | 150.7326 | 0 | 1.3492 | 0 | 1.5073 | 0 | 1.3492 | 1.5073 | 18.2977 | 5.8882 | 16.9485
39050.4902 | 2365 | 0 | 39050.4903 | 2118 | 0 |  | 1640.5 | 1876.5 | 144.3834 | 0 | 129.304 | 0 | 1.4438 | 0 | 1.293 | 0 | 1.4438 | 1.293 | 10.5446 | 23.4363 | 9.1008
39050.4907 | 2284 | 0 | 39050.4907 | 2107 | 0 |  | 1682.5 | 1918.5 | 139.4383 | 0 | 128.6325 | 0 | 1.3944 | 0 | 1.2863 | 0 | 1.3944 | 1.2863 | 14.465 | 24.0807 | 13.0706
39050.4912 | 1958 | 0 | 39050.4912 | 2150 | 0 |  | 1724.5 | 1960.5 | 119.536 | 0 | 131.2576 | 0 | 1.1954 | 0 | 1.3126 | 0 | 1.1954 | 1.3126 | 33.523 | 21.5991 | 32.3276
39050.4917 | 2292 | 0 | 39050.4917 | 2011 | 0 |  | 1766.5 | 2002.5 | 139.9267 | 0 | 122.7717 | 0 | 1.3993 | 0 | 1.2277 | 0 | 1.3993 | 1.2277 | 14.0654 | 30.004 | 12.6662
39050.4922 | 2031 | 0 | 39050.4922 | 2521 | 0 |  | 1808.5 | 2044.5 | 123.9927 | 0 | 153.9072 | 0 | 1.2399 | 0 | 1.5391 | 0 | 1.2399 | 1.5391 | 28.7238 | 3.7041 | 27.4839
39050.4927 | 1938 | 0 | 39050.4927 | 2212 | 0 |  | 1850.5 | 2086.5 | 118.315 | 0 | 135.0427 | 0 | 1.1832 | 0 | 1.3504 | 0 | 1.1832 | 1.3504 | 34.9009 | 18.1908 | 33.7178
39050.4932 | 1755 | 0 | 39050.4932 | 2024 | 0 |  | 1892.5 | 2128.5 | 107.1429 | 0 | 123.5653 | 0 | 1.0714 | 0 | 1.2357 | 0 | 1.0714 | 1.2357 | 48.9675 | 29.169 | 47.8961
39050.4936 | 1841 | 0 | 39050.4937 | 2151 | 0 |  | 1934.5 | 2170.5 | 112.3932 | 0 | 131.3187 | 0 | 1.1239 | 0 | 1.3132 | 0 | 1.1239 | 1.3132 | 42.0087 | 21.5425 | 40.8848

## B3-B4
Open Burn Test 14 |  |  | 2006-11-29 | 11:22 |  |  | Vs = |  | 155.6398 |  | R = | 100
Mixed | 7-C | Tray F | IRMS | 1
0 | 300 kW |  | Bundle | Ch. 3 & 4 | Cable B | Odd -Even
Time-19 | N11 | N12 | Time-20 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R4-G | R3-4
39050.4688 | 1 | 0 | 39050.4688 | 1 | 0 |  | -209.5 | 26.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254838 | 254838 | 254837.9994
39050.4693 | 1 | 0 | 39050.4693 | 1 | 0 |  | -168 | 68 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254838 | 254838 | 254837.9994
39050.4698 | 1 | 0 | 39050.4698 | 1 | 0 |  | -126 | 110 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254838 | 254838 | 254837.9994
39050.4703 | 1 | 0 | 39050.4703 | 1 | 0 |  | -84 | 152 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254838 | 254838 | 254837.9994
39050.4708 | 1 | 0 | 39050.4708 | 1 | 0 |  | -42 | 194 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254838 | 254838 | 254837.9994
39050.4713 | 1 | 0 | 39050.4713 | 1 | 0 |  | -1.5274e-07 | 236 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254838 | 254838 | 254837.9994
39050.4717 | 1 | 0 | 39050.4718 | 1 | 0 |  | 42 | 278 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254838 | 254838 | 254837.9994
39050.4722 | 1 | 0 | 39050.4722 | 1 | 0 |  | 84 | 320 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254838 | 254838 | 254837.9994
39050.4727 | 1 | 0 | 39050.4727 | 1 | 0 |  | 126 | 362 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254838 | 254838 | 254837.9994
39050.4732 | 1 | 0 | 39050.4732 | 1 | 0 |  | 168 | 404 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254838 | 254838 | 254837.9994
39050.4737 | 1 | 0 | 39050.4737 | 1 | 0 |  | 210 | 446 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254838 | 254838 | 254837.9994
39050.4742 | 1 | 0 | 39050.4742 | 1 | 0 |  | 252 | 488 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254838 | 254838 | 254837.9994
39050.4747 | 1 | 0 | 39050.4747 | 1 | 0 |  | 294 | 530 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254838 | 254838 | 254837.9994
39050.4751 | 1 | 0 | 39050.4752 | 1 | 0 |  | 336 | 572 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254838 | 254838 | 254837.9994
39050.4756 | 1 | 0 | 39050.4756 | 1 | 0 |  | 378 | 614 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254838 | 254838 | 254837.9994
39050.4761 | 1 | 0 | 39050.4761 | 1 | 0 |  | 420 | 656 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254838 | 254838 | 254837.9994
39050.4766 | 1411 | 0 | 39050.4766 | 1 | 0 |  | 462 | 698 | 86.1416 | 0 | 0.06105 | 0 | 0.86142 | 0 | 0.0006105 | 0 | 0.86142 | 0.0006105 | 80.679 | 254838 | 79.8175
39050.4771 | 375 | 0 | 39050.4771 | 1304 | 0 |  | 504 | 740 | 22.8938 | 0 | 79.6093 | 0 | 0.22894 | 0 | 0.79609 | 0 | 0.22894 | 0.79609 | 579.8347 | 95.5046 | 579.6057
39050.4776 | 2163 | 1 | 39050.4776 | 2002 | 2 |  | 546 | 782 | 132.0513 | 0.06105 | 122.2222 | 0.1221 | 1.3205 | 0.0006105 | 1.2222 | 0.001221 | 1.3199 | 1.221 | 17.9015 | 27.5227 | 8317.5089
39050.4781 | 2038 | 5 | 39050.4781 | 2136 | 0 |  | 588 | 824 | 124.42 | 0.30525 | 130.4029 | 0 | 1.2442 | 0.0030525 | 1.304 | 0 | 1.2411 | 1.304 | 25.4777 | 19.353 | 1642.1825
39050.4785 | 2151 | 0 | 39050.4786 | 2269 | 0 |  | 630 | 866 | 131.3187 | 0 | 138.5226 | 0 | 1.3132 | 0 | 1.3852 | 0 | 1.3132 | 1.3852 | 18.5207 | 12.357 | 17.2075
39050.479 | 2371 | 0 | 39050.4791 | 2399 | 0 |  | 672 | 908 | 144.7497 | 0 | 146.4591 | 0 | 1.4475 | 0 | 1.4646 | 0 | 1.4475 | 1.4646 | 7.5234 | 6.2684 | 6.0759
39050.4795 | 1867 | 12 | 39050.4795 | 1940 | 82 |  | 714 | 950 | 113.9805 | 0.7326 | 118.4371 | 5.0061 | 1.1398 | 0.007326 | 1.1844 | 0.050061 | 1.1325 | 1.1343 | 37.4373 | 37.1807 | 1514.1349
39050.48 | 2457 | 0 | 39050.48 | 2384 | 0 |  | 756 | 992 | 150 | 0 | 145.5433 | 0 | 1.5 | 0 | 1.4554 | 0 | 1.5 | 1.4554 | 3.7599 | 6.9371 | 2.2599
39050.4805 | 2474 | 0 | 39050.4805 | 2376 | 0 |  | 798 | 1034 | 151.0379 | 0 | 145.0549 | 0 | 1.5104 | 0 | 1.4505 | 0 | 1.5104 | 1.4505 | 3.0469 | 7.2971 | 1.5365
39050.481 | 2475 | 0 | 39050.481 | 1999 | 0 |  | 840 | 1076 | 151.0989 | 0 | 122.0391 | 0 | 1.511 | 0 | 1.2204 | 0 | 1.511 | 1.2204 | 3.0053 | 27.5328 | 1.4943
39050.4815 | 2019 | 0 | 39050.4815 | 2402 | 0 |  | 882 | 1118 | 123.2601 | 0 | 146.6422 | 0 | 1.2326 | 0 | 1.4664 | 0 | 1.2326 | 1.4664 | 26.2694 | 6.1357 | 25.0368
39050.4819 | 2024 | 0 | 39050.482 | 2205 | 0 |  | 924 | 1160 | 123.5653 | 0 | 134.6154 | 0 | 1.2357 | 0 | 1.3462 | 0 | 1.2357 | 1.3462 | 25.9575 | 15.6181 | 24.7219
39050.4824 | 2349 | 0 | 39050.4825 | 2533 | 0 |  | 966 | 1202 | 143.4066 | 0 | 154.6398 | 0 | 1.4341 | 0 | 1.5464 | 0 | 1.4341 | 1.5464 | 8.5304 | 0.64666 | 7.0964
39050.4829 | 2505 | 0 | 39050.4829 | 2322 | 0 |  | 1008 | 1244 | 152.9304 | 0 | 141.7582 | 0 | 1.5293 | 0 | 1.4176 | 0 | 1.5293 | 1.4176 | 1.7717 | 9.7924 | 0.24235
39050.4834 | 2081 | 0 | 39050.4834 | 2502 | 0 |  | 1050 | 1286 | 127.0452 | 0 | 152.7473 | 0 | 1.2705 | 0 | 1.5275 | 0 | 1.2705 | 1.5275 | 22.5074 | 1.8937 | 21.237
39050.4839 | 2456 | 0 | 39050.4839 | 1926 | 0 |  | 1092 | 1328 | 149.9389 | 0 | 117.5824 | 0 | 1.4994 | 0 | 1.1758 | 0 | 1.4994 | 1.1758 | 3.8021 | 32.3666 | 2.3027
39050.4844 | 1936 | 0 | 39050.4844 | 2030 | 0 |  | 1134 | 1370 | 118.1929 | 0 | 123.9316 | 0 | 1.1819 | 0 | 1.2393 | 0 | 1.1819 | 1.2393 | 31.6829 | 25.5852 | 30.5009
39050.4849 | 2260 | 0 | 39050.4849 | 2307 | 0 |  | 1176 | 1412 | 137.9731 | 0 | 140.8425 | 0 | 1.3797 | 0 | 1.4084 | 0 | 1.3797 | 1.4084 | 12.8044 | 10.5063 | 11.4247
39050.4853 | 1926 | 0 | 39050.4854 | 1968 | 0 |  | 1218 | 1454 | 117.5824 | 0 | 120.1465 | 0 | 1.1758 | 0 | 1.2015 | 0 | 1.1758 | 1.2015 | 32.3666 | 29.5417 | 31.1907
39050.4858 | 1739 | 0 | 39050.4859 | 2095 | 0 |  | 1260 | 1496 | 106.1661 | 0 | 127.8999 | 0 | 1.0617 | 0 | 1.279 | 0 | 1.0617 | 1.279 | 46.6003 | 21.6888 | 45.5387
39050.4863 | 1770 | 0 | 39050.4863 | 2392 | 0 |  | 1302 | 1538 | 108.0586 | 0 | 146.0317 | 0 | 1.0806 | 0 | 1.4603 | 0 | 1.0806 | 1.4603 | 44.0328 | 6.5794 | 42.9522
39050.4868 | 1959 | 0 | 39050.4868 | 2290 | 0 |  | 1344 | 1580 | 119.5971 | 0 | 139.8046 | 0 | 1.196 | 0 | 1.398 | 0 | 1.196 | 1.398 | 30.1368 | 11.3266 | 28.9408
39050.4873 | 1866 | 0 | 39050.4873 | 2233 | 0 |  | 1386 | 1622 | 113.9194 | 0 | 136.3248 | 0 | 1.1392 | 0 | 1.3632 | 0 | 1.1392 | 1.3632 | 36.6227 | 14.1684 | 35.4835
39050.4878 | 2242 | 0 | 39050.4878 | 2022 | 0 |  | 1428 | 1664 | 136.8742 | 0 | 123.4432 | 0 | 1.3687 | 0 | 1.2344 | 0 | 1.3687 | 1.2344 | 13.7101 | 26.0821 | 12.3413
39050.4883 | 2111 | 0 | 39050.4883 | 2085 | 0 |  | 1470 | 1706 | 128.8767 | 0 | 127.2894 | 0 | 1.2888 | 0 | 1.2729 | 0 | 1.2888 | 1.2729 | 20.7665 | 22.2724 | 19.4777
39050.4887 | 2277 | 0 | 39050.4888 | 2458 | 0 |  | 1512 | 1748 | 139.011 | 0 | 150.0611 | 0 | 1.3901 | 0 | 1.5006 | 0 | 1.3901 | 1.5006 | 11.9622 | 3.7177 | 10.5721
39050.4892 | 2218 | 0 | 39050.4893 | 1938 | 0 |  | 1554 | 1790 | 135.409 | 0 | 118.315 | 0 | 1.3541 | 0 | 1.1832 | 0 | 1.3541 | 1.1832 | 14.9405 | 31.547 | 13.5864
39050.4897 | 2295 | 0 | 39050.4897 | 2354 | 0 |  | 1596 | 1832 | 140.1099 | 0 | 143.7118 | 0 | 1.4011 | 0 | 1.4371 | 0 | 1.4011 | 1.4371 | 11.0841 | 8.2999 | 9.683
39050.4902 | 2032 | 1 | 39050.4902 | 1863 | 1 |  | 1638 | 1874 | 124.0537 | 0.06105 | 113.7363 | 0.06105 | 1.2405 | 0.0006105 | 1.1374 | 0.0006105 | 1.2399 | 1.1368 | 25.5081 | 36.9403 | 13929.594
39050.4907 | 2034 | 1 | 39050.4907 | 2071 | 1 |  | 1680 | 1916 | 124.1758 | 0.06105 | 126.4347 | 0.06105 | 1.2418 | 0.0006105 | 1.2643 | 0.0006105 | 1.2411 | 1.2637 | 25.4047 | 23.1542 | 9670.8409
39050.4912 | 2359 | 0 | 39050.4912 | 1987 | 0 |  | 1722 | 1958 | 144.0171 | 0 | 121.3065 | 0 | 1.4402 | 0 | 1.2131 | 0 | 1.4402 | 1.2131 | 8.0704 | 28.303 | 6.6302
39050.4917 | 2276 | 4 | 39050.4917 | 2034 | 16 |  | 1764 | 2000 | 138.9499 | 0.2442 | 124.1758 | 0.9768 | 1.3895 | 0.002442 | 1.2418 | 0.009768 | 1.3871 | 1.232 | 12.1106 | 27.3283 | 1445.4164
39050.4922 | 1812 | 24 | 39050.4922 | 1789 | 24 |  | 1806 | 2042 | 110.6227 | 1.4652 | 109.2186 | 1.4652 | 1.1062 | 0.014652 | 1.0922 | 0.014652 | 1.0916 | 1.0775 | 42.523 | 44.5041 | 915.4399
39050.4926 | 1771 | 41 | 39050.4927 | 1952 | 49 |  | 1848 | 2084 | 108.1197 | 2.5031 | 119.1697 | 2.9915 | 1.0812 | 0.025031 | 1.1917 | 0.029915 | 1.0562 | 1.1618 | 48.457 | 33.1532 | 447.7968
39050.4931 | 2077 | 54 | 39050.4931 | 1988 | 59 |  | 1890 | 2126 | 126.801 | 3.2967 | 121.3675 | 3.602 | 1.268 | 0.032967 | 1.2137 | 0.03602 | 1.235 | 1.1777 | 25.3996 | 33.0863 | 192.6159
39050.4936 | 1681 | 78 | 39050.4936 | 2006 | 102 |  | 1932 | 2168 | 102.6252 | 4.7619 | 122.4664 | 6.2271 | 1.0263 | 0.047619 | 1.2247 | 0.062271 | 0.97863 | 1.1624 | 64.2059 | 31.1368 | 240.5975

## A2-C6
Open Burn Test 14 |  |  | 2006-11-29 | 11:22 |  |  | Vs = |  | 160.4017 |  | R = | 100
Mixed | 7-C | Tray F | IRMS | 1
0 | 300 kW |  | Bundle | Ch. 2 & 6 | Cable A | Even - | Cable C |  | Even
Time-17 | N11 | N12 | Time-18 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R6-G | R2-6
39050.4688 | 1 | 0 | 39050.4688 | 1 | 0 |  | -212.5 | 23.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262638 | 262638 | 262637.9994
39050.4693 | 1 | 0 | 39050.4693 | 1 | 0 |  | -170.5 | 65.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262638 | 262638 | 262637.9994
39050.4698 | 1 | 0 | 39050.4698 | 1 | 0 |  | -128.5 | 107.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262638 | 262638 | 262637.9994
39050.4703 | 1 | 0 | 39050.4703 | 1 | 0 |  | -86.5 | 149.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262638 | 262638 | 262637.9994
39050.4707 | 1 | 0 | 39050.4708 | 1 | 0 |  | -44.5 | 191.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262638 | 262638 | 262637.9994
39050.4712 | 1 | 0 | 39050.4712 | 1 | 0 |  | -2.5 | 233.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262638 | 262638 | 262637.9994
39050.4717 | 1 | 0 | 39050.4717 | 1 | 0 |  | 39.5 | 275.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262638 | 262638 | 262637.9994
39050.4722 | 1 | 0 | 39050.4722 | 1 | 0 |  | 81.5 | 317.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262638 | 262638 | 262637.9994
39050.4727 | 1 | 0 | 39050.4727 | 1 | 0 |  | 123.5 | 359.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262638 | 262638 | 262637.9994
39050.4732 | 1 | 0 | 39050.4732 | 1 | 0 |  | 165.5 | 401.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262638 | 262638 | 262637.9994
39050.4737 | 1 | 0 | 39050.4737 | 1 | 0 |  | 207.5 | 443.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262638 | 262638 | 262637.9994
39050.4741 | 1 | 0 | 39050.4742 | 1 | 0 |  | 249.5 | 485.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262638 | 262638 | 262637.9994
39050.4746 | 1 | 0 | 39050.4746 | 1 | 0 |  | 291.5 | 527.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262638 | 262638 | 262637.9994
39050.4751 | 1 | 0 | 39050.4751 | 1 | 0 |  | 333.5 | 569.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262638 | 262638 | 262637.9994
39050.4756 | 1 | 0 | 39050.4756 | 1 | 0 |  | 375.5 | 611.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262638 | 262638 | 262637.9994
39050.4761 | 1 | 0 | 39050.4761 | 2085 | 0 |  | 417.5 | 653.5 | 0.06105 | 0 | 127.2894 | 0 | 0.0006105 | 0 | 1.2729 | 0 | 0.0006105 | 1.2729 | 262638 | 26.0134 | 262637.9994
39050.4766 | 1 | 0 | 39050.4766 | 2385 | 0 |  | 459.5 | 695.5 | 0.06105 | 0 | 145.6044 | 0 | 0.0006105 | 0 | 1.456 | 0 | 0.0006105 | 1.456 | 262638 | 10.1627 | 262637.9994
39050.4771 | 1 | 0 | 39050.4771 | 2054 | 0 |  | 501.5 | 737.5 | 0.06105 | 0 | 125.3968 | 0 | 0.0006105 | 0 | 1.254 | 0 | 0.0006105 | 1.254 | 262638 | 27.9153 | 262637.9994
39050.4775 | 2 | 0 | 39050.4776 | 2445 | 0 |  | 543.5 | 779.5 | 0.1221 | 0 | 149.2674 | 0 | 0.001221 | 0 | 1.4927 | 0 | 0.001221 | 1.4927 | 131269 | 7.4593 | 131268.9988
39050.478 | 1 | 0 | 39050.478 | 2028 | 0 |  | 585.5 | 821.5 | 0.06105 | 0 | 123.8095 | 0 | 0.0006105 | 0 | 1.2381 | 0 | 0.0006105 | 1.2381 | 262638 | 29.5552 | 262637.9994
39050.4785 | 7 | 0 | 39050.4785 | 2534 | 0 |  | 627 | 863 | 0.42735 | 0 | 154.7009 | 0 | 0.0042735 | 0 | 1.547 | 0 | 0.0042735 | 1.547 | 37434 | 3.6851 | 37433.9957
39050.479 | 491 | 0 | 39050.479 | 2560 | 0 |  | 669.5 | 905.5 | 29.9756 | 0 | 156.2882 | 0 | 0.29976 | 0 | 1.5629 | 0 | 0.29976 | 1.5629 | 435.1079 | 2.632 | 434.8082
39050.4795 | 2153 | 0 | 39050.4795 | 2522 | 0 |  | 711.5 | 947.5 | 131.4408 | 0 | 153.9683 | 0 | 1.3144 | 0 | 1.5397 | 0 | 1.3144 | 1.5397 | 22.0334 | 4.1784 | 20.719
39050.48 | 1986 | 0 | 39050.48 | 2282 | 0 |  | 753.5 | 989.5 | 121.2454 | 0 | 139.3162 | 0 | 1.2125 | 0 | 1.3932 | 0 | 1.2125 | 1.3932 | 32.2951 | 15.135 | 31.0826
39050.4805 | 2032 | 0 | 39050.4805 | 2377 | 0 |  | 795.5 | 1031.5 | 124.0537 | 0 | 145.116 | 0 | 1.2405 | 0 | 1.4512 | 0 | 1.2405 | 1.4512 | 29.3002 | 10.5334 | 28.0597
39050.4809 | 2032 | 0 | 39050.481 | 2264 | 0 |  | 837.5 | 1073.5 | 124.0537 | 0 | 138.2173 | 0 | 1.2405 | 0 | 1.3822 | 0 | 1.2405 | 1.3822 | 29.3002 | 16.0504 | 28.0597
39050.4814 | 1991 | 0 | 39050.4814 | 2517 | 0 |  | 879 | 1115 | 121.5507 | 0 | 153.663 | 0 | 1.2155 | 0 | 1.5366 | 0 | 1.2155 | 1.5366 | 31.9628 | 4.3854 | 30.7473
39050.4819 | 2318 | 0 | 39050.4819 | 2611 | 0 |  | 921.5 | 1157.5 | 141.514 | 0 | 159.4017 | 0 | 1.4151 | 0 | 1.594 | 0 | 1.4151 | 1.594 | 13.3469 | 0.62735 | 11.9317
39050.4824 | 2327 | 0 | 39050.4824 | 2512 | 0 |  | 963.5 | 1199.5 | 142.0635 | 0 | 153.3578 | 0 | 1.4206 | 0 | 1.5336 | 0 | 1.4206 | 1.5336 | 12.9085 | 4.5932 | 11.4878
39050.4829 | 2278 | 0 | 39050.4829 | 2117 | 0 |  | 1005.5 | 1241.5 | 139.072 | 0 | 129.243 | 0 | 1.3907 | 0 | 1.2924 | 0 | 1.3907 | 1.2924 | 15.3371 | 24.1086 | 13.9464
39050.4834 | 1987 | 0 | 39050.4834 | 2101 | 0 |  | 1047 | 1283 | 121.3065 | 0 | 128.2662 | 0 | 1.2131 | 0 | 1.2827 | 0 | 1.2131 | 1.2827 | 32.2285 | 25.0538 | 31.0154
39050.4839 | 2337 | 0 | 39050.4839 | 2373 | 0 |  | 1089.5 | 1325.5 | 142.674 | 0 | 144.8718 | 0 | 1.4267 | 0 | 1.4487 | 0 | 1.4267 | 1.4487 | 12.4253 | 10.7198 | 10.9986
39050.4843 | 2437 | 0 | 39050.4844 | 2452 | 0 |  | 1131 | 1367 | 148.779 | 0 | 149.6947 | 0 | 1.4878 | 0 | 1.4969 | 0 | 1.4878 | 1.4969 | 7.8121 | 7.1525 | 6.3243
39050.4848 | 1954 | 0 | 39050.4848 | 2004 | 0 |  | 1173 | 1409 | 119.2918 | 0 | 122.3443 | 0 | 1.1929 | 0 | 1.2234 | 0 | 1.1929 | 1.2234 | 34.4616 | 31.1068 | 33.2687
39050.4853 | 2247 | 0 | 39050.4853 | 2260 | 0 |  | 1215 | 1451 | 137.1795 | 0 | 137.9731 | 0 | 1.3718 | 0 | 1.3797 | 0 | 1.3718 | 1.3797 | 16.9283 | 16.2558 | 15.5566
39050.4858 | 1955 | 0 | 39050.4858 | 2546 | 0 |  | 1257 | 1493 | 119.3529 | 0 | 155.4335 | 0 | 1.1935 | 0 | 1.5543 | 0 | 1.1935 | 1.5543 | 34.3928 | 3.1964 | 33.1993
39050.4863 | 2291 | 0 | 39050.4863 | 2607 | 0 |  | 1299 | 1535 | 139.8657 | 0 | 159.1575 | 0 | 1.3987 | 0 | 1.5916 | 0 | 1.3987 | 1.5916 | 14.6827 | 0.78174 | 13.284
39050.4868 | 1939 | 0 | 39050.4868 | 2380 | 0 |  | 1341 | 1577 | 118.3761 | 0 | 145.2991 | 0 | 1.1838 | 0 | 1.453 | 0 | 1.1838 | 1.453 | 35.5018 | 10.3941 | 34.318
39050.4873 | 2418 | 0 | 39050.4873 | 2146 | 0 |  | 1383 | 1619 | 147.619 | 0 | 131.0134 | 0 | 1.4762 | 0 | 1.3101 | 0 | 1.4762 | 1.3101 | 8.6592 | 22.4315 | 7.183
39050.4877 | 2274 | 0 | 39050.4878 | 2379 | 0 |  | 1425 | 1661 | 138.8278 | 0 | 145.2381 | 0 | 1.3883 | 0 | 1.4524 | 0 | 1.3883 | 1.4524 | 15.54 | 10.4405 | 14.1517
39050.4882 | 2415 | 0 | 39050.4883 | 2271 | 0 |  | 1467 | 1703 | 147.4359 | 0 | 138.6447 | 0 | 1.4744 | 0 | 1.3864 | 0 | 1.4744 | 1.3864 | 8.7942 | 15.6926 | 7.3198
39050.4887 | 2424 | 0 | 39050.4887 | 2372 | 0 |  | 1509 | 1745 | 147.9853 | 0 | 144.8107 | 0 | 1.4799 | 0 | 1.4481 | 0 | 1.4799 | 1.4481 | 8.3903 | 10.7664 | 6.9104
39050.4892 | 2388 | 0 | 39050.4892 | 2534 | 0 |  | 1551 | 1787 | 145.7875 | 0 | 154.7009 | 0 | 1.4579 | 0 | 1.547 | 0 | 1.4579 | 1.547 | 10.0243 | 3.6851 | 8.5664
39050.4897 | 1997 | 0 | 39050.4897 | 2221 | 0 |  | 1593 | 1829 | 121.917 | 0 | 135.5922 | 0 | 1.2192 | 0 | 1.3559 | 0 | 1.2192 | 1.3559 | 31.5663 | 18.2972 | 30.3472
39050.4902 | 2081 | 0 | 39050.4902 | 2255 | 0 |  | 1635 | 1871 | 127.0452 | 0 | 137.6679 | 0 | 1.2705 | 0 | 1.3767 | 0 | 1.2705 | 1.3767 | 26.2556 | 16.5135 | 24.9852
39050.4907 | 2076 | 0 | 39050.4907 | 2248 | 0 |  | 1677 | 1913 | 126.7399 | 0 | 137.2405 | 0 | 1.2674 | 0 | 1.3724 | 0 | 1.2674 | 1.3724 | 26.5597 | 16.8763 | 25.2923
39050.4911 | 2127 | 0 | 39050.4912 | 2138 | 0 |  | 1719 | 1955 | 129.8535 | 0 | 130.525 | 0 | 1.2985 | 0 | 1.3053 | 0 | 1.2985 | 1.3053 | 23.5252 | 22.8896 | 22.2266
39050.4916 | 2423 | 0 | 39050.4917 | 2353 | 0 |  | 1761 | 1997 | 147.9243 | 0 | 143.6508 | 0 | 1.4792 | 0 | 1.4365 | 0 | 1.4792 | 1.4365 | 8.435 | 11.6609 | 6.9558
39050.4921 | 2386 | 0 | 39050.4921 | 2070 | 0 |  | 1803 | 2039 | 145.6654 | 0 | 126.3736 | 0 | 1.4567 | 0 | 1.2637 | 0 | 1.4567 | 1.2637 | 10.1165 | 26.9266 | 8.6599
39050.4926 | 1926 | 0 | 39050.4926 | 2545 | 0 |  | 1845 | 2081 | 117.5824 | 0 | 155.3724 | 0 | 1.1758 | 0 | 1.5537 | 0 | 1.1758 | 1.5537 | 36.4164 | 3.2369 | 35.2406
39050.4931 | 2055 | 0 | 39050.4931 | 2135 | 0 |  | 1887 | 2123 | 125.4579 | 0 | 130.3419 | 0 | 1.2546 | 0 | 1.3034 | 0 | 1.2546 | 1.3034 | 27.853 | 23.0623 | 26.5985
39050.4936 | 2210 | 0 | 39050.4936 | 2496 | 0 |  | 1929 | 2165 | 134.9206 | 0 | 152.381 | 0 | 1.3492 | 0 | 1.5238 | 0 | 1.3492 | 1.5238 | 18.886 | 5.2636 | 17.5368

## A2-C5
Open Burn Test 14 |  |  | 2006-11-29 | 11:22 |  |  | Vs = |  | 159.6691 |  | R = | 100
Mixed | 7-C | Tray F | IRMS | 1
0 | 300 kW |  | Bundle | Ch. 2 & 5 | Cable A | Even - | Cable C |  | Odd
Time-15 | N11 | N12 | Time-16 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R5-G | R2-5
39050.4688 | 1 | 0 | 39050.4688 | 1 | 0 |  | -215.5 | 20.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261438 | 261438 | 261437.9994
39050.4692 | 1 | 0 | 39050.4693 | 1 | 0 |  | -173.5 | 62.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261438 | 261438 | 261437.9994
39050.4697 | 1 | 0 | 39050.4697 | 1 | 0 |  | -131.5 | 104.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261438 | 261438 | 261437.9994
39050.4702 | 1 | 0 | 39050.4702 | 1 | 0 |  | -89.5 | 146.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261438 | 261438 | 261437.9994
39050.4707 | 1 | 0 | 39050.4707 | 1 | 0 |  | -47.5 | 188.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261438 | 261438 | 261437.9994
39050.4712 | 1 | 0 | 39050.4712 | 1 | 0 |  | -5.5 | 230.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261438 | 261438 | 261437.9994
39050.4717 | 1 | 0 | 39050.4717 | 1 | 0 |  | 36.5 | 272.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261438 | 261438 | 261437.9994
39050.4722 | 1 | 0 | 39050.4722 | 1 | 0 |  | 78.5 | 314.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261438 | 261438 | 261437.9994
39050.4727 | 1 | 0 | 39050.4727 | 1 | 0 |  | 120.5 | 356.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261438 | 261438 | 261437.9994
39050.4731 | 1 | 0 | 39050.4731 | 1 | 0 |  | 162.5 | 398.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261438 | 261438 | 261437.9994
39050.4736 | 1 | 0 | 39050.4736 | 1 | 0 |  | 204.5 | 440.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261438 | 261438 | 261437.9994
39050.4741 | 1 | 0 | 39050.4741 | 1 | 0 |  | 246.5 | 482.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261438 | 261438 | 261437.9994
39050.4746 | 1 | 0 | 39050.4746 | 1 | 0 |  | 288.5 | 524.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261438 | 261438 | 261437.9994
39050.4751 | 1 | 0 | 39050.4751 | 1 | 0 |  | 330.5 | 566.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261438 | 261438 | 261437.9994
39050.4756 | 1 | 0 | 39050.4756 | 1 | 0 |  | 372.5 | 608.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261438 | 261438 | 261437.9994
39050.4761 | 1 | 0 | 39050.4761 | 418 | 0 |  | 414.5 | 650.5 | 0.06105 | 0 | 25.5189 | 0 | 0.0006105 | 0 | 0.25519 | 0 | 0.0006105 | 0.25519 | 261438 | 525.689 | 261437.9994
39050.4765 | 1 | 0 | 39050.4766 | 2269 | 0 |  | 456.5 | 692.5 | 0.06105 | 0 | 138.5226 | 0 | 0.0006105 | 0 | 1.3852 | 0 | 0.0006105 | 1.3852 | 261438 | 15.2658 | 261437.9994
39050.477 | 1 | 0 | 39050.477 | 2462 | 0 |  | 498.5 | 734.5 | 0.06105 | 0 | 150.3053 | 0 | 0.0006105 | 0 | 1.5031 | 0 | 0.0006105 | 1.5031 | 261438 | 6.2299 | 261437.9994
39050.4775 | 1 | 0 | 39050.4775 | 2599 | 0 |  | 540.5 | 776.5 | 0.06105 | 0 | 158.6691 | 0 | 0.0006105 | 0 | 1.5867 | 0 | 0.0006105 | 1.5867 | 261438 | 0.63024 | 261437.9994
39050.478 | 1 | 0 | 39050.478 | 2585 | 0 |  | 582.5 | 818.5 | 0.06105 | 0 | 157.8144 | 0 | 0.0006105 | 0 | 1.5781 | 0 | 0.0006105 | 1.5781 | 261438 | 1.1752 | 261437.9994
39050.4785 | 3 | 0 | 39050.4785 | 2129 | 0 |  | 624.5 | 860.5 | 0.18315 | 0 | 129.9756 | 0 | 0.0018315 | 0 | 1.2998 | 0 | 0.0018315 | 1.2998 | 87079.3333 | 22.8455 | 87079.3315
39050.479 | 353 | 0 | 39050.479 | 2239 | 0 |  | 666.5 | 902.5 | 21.5507 | 0 | 136.6911 | 0 | 0.21551 | 0 | 1.3669 | 0 | 0.21551 | 1.3669 | 640.9008 | 16.8102 | 640.6853
39050.4795 | 1774 | 0 | 39050.4795 | 2593 | 0 |  | 708.5 | 944.5 | 108.3028 | 0 | 158.3028 | 0 | 1.083 | 0 | 1.583 | 0 | 1.083 | 1.583 | 47.4284 | 0.86309 | 46.3454
39050.4799 | 1888 | 0 | 39050.48 | 2202 | 0 |  | 750.5 | 986.5 | 115.2625 | 0 | 134.4322 | 0 | 1.1526 | 0 | 1.3443 | 0 | 1.1526 | 1.3443 | 38.5265 | 18.7729 | 37.3739
39050.4804 | 2420 | 0 | 39050.4804 | 2578 | 0 |  | 792.5 | 1028.5 | 147.7411 | 0 | 157.3871 | 0 | 1.4774 | 0 | 1.5739 | 0 | 1.4774 | 1.5739 | 8.0736 | 1.45 | 6.5961
39050.4809 | 2257 | 0 | 39050.4809 | 2018 | 0 |  | 834.5 | 1070.5 | 137.79 | 0 | 123.199 | 0 | 1.3779 | 0 | 1.232 | 0 | 1.3779 | 1.232 | 15.8786 | 29.6026 | 14.5007
39050.4814 | 2019 | 0 | 39050.4814 | 2588 | 0 |  | 876.5 | 1112.5 | 123.2601 | 0 | 157.9976 | 0 | 1.2326 | 0 | 1.58 | 0 | 1.2326 | 1.58 | 29.5384 | 1.058 | 28.3058
39050.4819 | 2410 | 0 | 39050.4819 | 2598 | 0 |  | 918.5 | 1154.5 | 147.1306 | 0 | 158.6081 | 0 | 1.4713 | 0 | 1.5861 | 0 | 1.4713 | 1.5861 | 8.522 | 0.66898 | 7.0507
39050.4824 | 2155 | 0 | 39050.4824 | 2458 | 0 |  | 960.5 | 1196.5 | 131.5629 | 0 | 150.0611 | 0 | 1.3156 | 0 | 1.5006 | 0 | 1.3156 | 1.5006 | 21.3633 | 6.4028 | 20.0477
39050.4829 | 2145 | 0 | 39050.4829 | 2134 | 0 |  | 1002.5 | 1238.5 | 130.9524 | 0 | 130.2808 | 0 | 1.3095 | 0 | 1.3028 | 0 | 1.3095 | 1.3028 | 21.9291 | 22.5576 | 20.6196
39050.4833 | 2390 | 0 | 39050.4834 | 2371 | 0 |  | 1044.5 | 1280.5 | 145.9096 | 0 | 144.7497 | 0 | 1.4591 | 0 | 1.4475 | 0 | 1.4591 | 1.4475 | 9.4301 | 10.307 | 7.971
39050.4838 | 2400 | 0 | 39050.4838 | 2049 | 0 |  | 1086.5 | 1322.5 | 146.5201 | 0 | 125.0916 | 0 | 1.4652 | 0 | 1.2509 | 0 | 1.4652 | 1.2509 | 8.9742 | 27.6418 | 7.509
39050.4843 | 2421 | 0 | 39050.4843 | 2595 | 0 |  | 1128.5 | 1364.5 | 147.8022 | 0 | 158.4249 | 0 | 1.478 | 0 | 1.5842 | 0 | 1.478 | 1.5842 | 8.0289 | 0.78536 | 6.5509
39050.4848 | 2440 | 0 | 39050.4848 | 2461 | 0 |  | 1170.5 | 1406.5 | 148.9621 | 0 | 150.2442 | 0 | 1.4896 | 0 | 1.5024 | 0 | 1.4896 | 1.5024 | 7.1877 | 6.2731 | 5.6981
39050.4853 | 2125 | 0 | 39050.4853 | 2495 | 0 |  | 1212.5 | 1448.5 | 129.7314 | 0 | 152.3199 | 0 | 1.2973 | 0 | 1.5232 | 0 | 1.2973 | 1.5232 | 23.0767 | 4.8248 | 21.7794
39050.4858 | 2477 | 0 | 39050.4858 | 2180 | 0 |  | 1254.5 | 1490.5 | 151.221 | 0 | 133.0891 | 0 | 1.5122 | 0 | 1.3309 | 0 | 1.5122 | 1.3309 | 5.5866 | 19.9716 | 4.0744
39050.4863 | 2317 | 0 | 39050.4863 | 2554 | 0 |  | 1296.5 | 1532.5 | 141.453 | 0 | 155.9219 | 0 | 1.4145 | 0 | 1.5592 | 0 | 1.4145 | 1.5592 | 12.8779 | 2.4033 | 11.4633
39050.4867 | 1983 | 0 | 39050.4868 | 2164 | 0 |  | 1338.5 | 1574.5 | 121.0623 | 0 | 132.1123 | 0 | 1.2106 | 0 | 1.3211 | 0 | 1.2106 | 1.3211 | 31.8901 | 20.8586 | 30.6794
39050.4872 | 2450 | 0 | 39050.4872 | 2472 | 0 |  | 1380.5 | 1616.5 | 149.5726 | 0 | 150.9158 | 0 | 1.4957 | 0 | 1.5092 | 0 | 1.4957 | 1.5092 | 6.7502 | 5.8002 | 5.2545
39050.4877 | 2205 | 0 | 39050.4877 | 2055 | 0 |  | 1422.5 | 1658.5 | 134.6154 | 0 | 125.4579 | 0 | 1.3462 | 0 | 1.2546 | 0 | 1.3462 | 1.2546 | 18.6113 | 27.2691 | 17.2652
39050.4882 | 2388 | 0 | 39050.4882 | 2593 | 0 |  | 1464.5 | 1700.5 | 145.7875 | 0 | 158.3028 | 0 | 1.4579 | 0 | 1.583 | 0 | 1.4579 | 1.583 | 9.5218 | 0.86309 | 8.0639
39050.4887 | 2409 | 0 | 39050.4887 | 2270 | 0 |  | 1506.5 | 1742.5 | 147.0696 | 0 | 138.5836 | 0 | 1.4707 | 0 | 1.3858 | 0 | 1.4707 | 1.3858 | 8.567 | 15.215 | 7.0963
39050.4892 | 2079 | 0 | 39050.4892 | 2296 | 0 |  | 1548.5 | 1784.5 | 126.9231 | 0 | 140.1709 | 0 | 1.2692 | 0 | 1.4017 | 0 | 1.2692 | 1.4017 | 25.7999 | 13.9103 | 24.5307
39050.4897 | 2010 | 0 | 39050.4897 | 2271 | 0 |  | 1590.5 | 1826.5 | 122.7106 | 0 | 138.6447 | 0 | 1.2271 | 0 | 1.3864 | 0 | 1.2271 | 1.3864 | 30.1184 | 15.1642 | 28.8913
39050.4902 | 2369 | 0 | 39050.4902 | 2558 | 0 |  | 1632.5 | 1868.5 | 144.6276 | 0 | 156.1661 | 0 | 1.4463 | 0 | 1.5617 | 0 | 1.4463 | 1.5617 | 10.4002 | 2.2432 | 8.9539
39050.4906 | 2167 | 0 | 39050.4906 | 2347 | 0 |  | 1674.5 | 1910.5 | 132.2955 | 0 | 143.2845 | 0 | 1.323 | 0 | 1.4328 | 0 | 1.323 | 1.4328 | 20.6913 | 11.435 | 19.3683
39050.4911 | 2282 | 0 | 39050.4911 | 2588 | 0 |  | 1716.5 | 1952.5 | 139.3162 | 0 | 157.9976 | 0 | 1.3932 | 0 | 1.58 | 0 | 1.3932 | 1.58 | 14.6091 | 1.058 | 13.216
39050.4916 | 2081 | 0 | 39050.4916 | 2372 | 0 |  | 1758.5 | 1994.5 | 127.0452 | 0 | 144.8107 | 0 | 1.2705 | 0 | 1.4481 | 0 | 1.2705 | 1.4481 | 25.679 | 10.2605 | 24.4085
39050.4921 | 2205 | 0 | 39050.4921 | 2505 | 0 |  | 1800.5 | 2036.5 | 134.6154 | 0 | 152.9304 | 0 | 1.3462 | 0 | 1.5293 | 0 | 1.3462 | 1.5293 | 18.6113 | 4.4064 | 17.2652
39050.4926 | 1928 | 0 | 39050.4926 | 2055 | 0 |  | 1842.5 | 2078.5 | 117.7045 | 0 | 125.4579 | 0 | 1.177 | 0 | 1.2546 | 0 | 1.177 | 1.2546 | 35.6525 | 27.2691 | 34.4754
39050.4931 | 2287 | 0 | 39050.4931 | 2508 | 0 |  | 1884.5 | 2120.5 | 139.6215 | 0 | 153.1136 | 0 | 1.3962 | 0 | 1.5311 | 0 | 1.3962 | 1.5311 | 14.3585 | 4.2815 | 12.9623
39050.4936 | 2245 | 0 | 39050.4936 | 2165 | 0 |  | 1926.5 | 2162.5 | 137.0574 | 0 | 132.1734 | 0 | 1.3706 | 0 | 1.3217 | 0 | 1.3706 | 1.3217 | 16.498 | 20.8028 | 15.1274

## A2-B4
Open Burn Test 14 |  |  | 2006-11-29 | 11:22 |  |  | Vs = |  | 154.0525 |  | R = | 100
Mixed | 7-C | Tray F | IRMS | 1
0 | 300 kW |  | Bundle | Ch. 2 & 4 | Cable A | Even - | Cable B |  | Even
Time-13 | N11 | N12 | Time-14 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R4-G | R2-4
39050.4687 | 1 | 0 | 39050.4688 | 1 | 0 |  | -218 | 18 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252238 | 252238 | 252237.9994
39050.4692 | 1 | 0 | 39050.4692 | 1 | 0 |  | -176.5 | 59.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252238 | 252238 | 252237.9994
39050.4697 | 1 | 0 | 39050.4697 | 1 | 0 |  | -134.5 | 101.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252238 | 252238 | 252237.9994
39050.4702 | 1 | 0 | 39050.4702 | 1 | 0 |  | -92.5 | 143.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252238 | 252238 | 252237.9994
39050.4707 | 1 | 0 | 39050.4707 | 1 | 0 |  | -50.5 | 185.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252238 | 252238 | 252237.9994
39050.4712 | 1 | 0 | 39050.4712 | 1 | 0 |  | -8.5 | 227.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252238 | 252238 | 252237.9994
39050.4716 | 1 | 0 | 39050.4717 | 1 | 0 |  | 33.5 | 269.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252238 | 252238 | 252237.9994
39050.4721 | 1 | 0 | 39050.4721 | 1 | 0 |  | 75.5 | 311.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252238 | 252238 | 252237.9994
39050.4726 | 1 | 0 | 39050.4726 | 1 | 0 |  | 117.5 | 353.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252238 | 252238 | 252237.9994
39050.4731 | 1 | 0 | 39050.4731 | 1 | 0 |  | 159.5 | 395.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252238 | 252238 | 252237.9994
39050.4736 | 1 | 0 | 39050.4736 | 1 | 0 |  | 201.5 | 437.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252238 | 252238 | 252237.9994
39050.4741 | 1 | 0 | 39050.4741 | 1 | 0 |  | 243.5 | 479.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252238 | 252238 | 252237.9994
39050.4746 | 1 | 0 | 39050.4746 | 1 | 0 |  | 285.5 | 521.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252238 | 252238 | 252237.9994
39050.475 | 1 | 0 | 39050.4751 | 1 | 0 |  | 327.5 | 563.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252238 | 252238 | 252237.9994
39050.4755 | 1 | 0 | 39050.4755 | 1 | 0 |  | 369.5 | 605.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252238 | 252238 | 252237.9994
39050.476 | 1 | 0 | 39050.476 | 1 | 0 |  | 411.5 | 647.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252238 | 252238 | 252237.9994
39050.4765 | 1 | 0 | 39050.4765 | 1 | 0 |  | 453.5 | 689.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252238 | 252238 | 252237.9994
39050.477 | 1 | 0 | 39050.477 | 1 | 0 |  | 495.5 | 731.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252238 | 252238 | 252237.9994
39050.4775 | 1 | 0 | 39050.4775 | 1 | 0 |  | 537.5 | 773.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252238 | 252238 | 252237.9994
39050.478 | 1 | 0 | 39050.478 | 1 | 0 |  | 579.5 | 815.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252238 | 252238 | 252237.9994
39050.4784 | 4 | 0 | 39050.4785 | 2 | 0 |  | 621.5 | 857.5 | 0.2442 | 0 | 0.1221 | 0 | 0.002442 | 0 | 0.001221 | 0 | 0.002442 | 0.001221 | 62984.5 | 126069 | 62984.4976
39050.4789 | 283 | 0 | 39050.4789 | 364 | 0 |  | 663.5 | 899.5 | 17.2772 | 0 | 22.2222 | 0 | 0.17277 | 0 | 0.22222 | 0 | 0.17277 | 0.22222 | 791.6537 | 593.2363 | 791.4809
39050.4794 | 1975 | 0 | 39050.4794 | 2123 | 0 |  | 705.5 | 941.5 | 120.5739 | 0 | 129.6093 | 0 | 1.2057 | 0 | 1.2961 | 0 | 1.2057 | 1.2961 | 27.7661 | 18.8592 | 26.5603
39050.4799 | 2249 | 0 | 39050.4799 | 2009 | 0 |  | 747.5 | 983.5 | 137.3016 | 0 | 122.6496 | 0 | 1.373 | 0 | 1.2265 | 0 | 1.373 | 1.2265 | 12.2001 | 25.6038 | 10.8271
39050.4804 | 1920 | 0 | 39050.4804 | 2123 | 0 |  | 789.5 | 1025.5 | 117.2161 | 0 | 129.6093 | 0 | 1.1722 | 0 | 1.2961 | 0 | 1.1722 | 1.2961 | 31.426 | 18.8592 | 30.2539
39050.4809 | 2316 | 0 | 39050.4809 | 1886 | 0 |  | 831.5 | 1067.5 | 141.3919 | 0 | 115.1404 | 0 | 1.4139 | 0 | 1.1514 | 0 | 1.4139 | 1.1514 | 8.9542 | 33.7953 | 7.5403
39050.4814 | 2262 | 0 | 39050.4814 | 2456 | 0 |  | 873.5 | 1109.5 | 138.0952 | 0 | 149.9389 | 0 | 1.381 | 0 | 1.4994 | 0 | 1.381 | 1.4994 | 11.5553 | 2.7435 | 10.1743
39050.4819 | 1981 | 0 | 39050.4819 | 2182 | 0 |  | 915.5 | 1151.5 | 120.9402 | 0 | 133.2112 | 0 | 1.2094 | 0 | 1.3321 | 0 | 1.2094 | 1.3321 | 27.3791 | 15.6453 | 26.1697
39050.4823 | 2082 | 0 | 39050.4823 | 2137 | 0 |  | 957.5 | 1193.5 | 127.1062 | 0 | 130.464 | 0 | 1.2711 | 0 | 1.3046 | 0 | 1.2711 | 1.3046 | 21.1998 | 18.0805 | 19.9287
39050.4828 | 2467 | 0 | 39050.4828 | 1992 | 0 |  | 999.5 | 1235.5 | 150.6105 | 0 | 121.6117 | 0 | 1.5061 | 0 | 1.2161 | 0 | 1.5061 | 1.2161 | 2.2854 | 26.6757 | 0.77926
39050.4833 | 1923 | 0 | 39050.4833 | 2251 | 0 |  | 1041.5 | 1277.5 | 117.3993 | 0 | 137.4237 | 0 | 1.174 | 0 | 1.3742 | 0 | 1.174 | 1.3742 | 31.221 | 12.1004 | 30.047
39050.4838 | 2084 | 0 | 39050.4838 | 2119 | 0 |  | 1083.5 | 1319.5 | 127.2283 | 0 | 129.3651 | 0 | 1.2723 | 0 | 1.2937 | 0 | 1.2723 | 1.2937 | 21.0835 | 19.0835 | 19.8112
39050.4843 | 2507 | 0 | 39050.4843 | 2315 | 0 |  | 1125.5 | 1361.5 | 153.0525 | 0 | 141.3309 | 0 | 1.5305 | 0 | 1.4133 | 0 | 1.5305 | 1.4133 | 0.65337 | 9.0013 | 0.87715
39050.4848 | 1930 | 0 |  | 2337 | 0 |  | 1167 | 1403 | 117.8266 | 0 | 142.674 | 0 | 1.1783 | 0 | 1.4267 | 0 | 1.1783 | 1.4267 | 30.7451 | 7.9752 | 29.5668
39050.4853 | 2458 | 0 | 39050.4853 | 2359 | 0 |  | 1209.5 | 1445.5 | 150.0611 | 0 | 144.0171 | 0 | 1.5006 | 0 | 1.4402 | 0 | 1.5006 | 1.4402 | 2.6599 | 6.9682 | 1.1593
39050.4857 | 2373 | 0 | 39050.4858 | 2195 | 0 |  | 1251.5 | 1487.5 | 144.8718 | 0 | 134.0049 | 0 | 1.4487 | 0 | 1.34 | 0 | 1.4487 | 1.34 | 6.3371 | 14.9604 | 4.8884
39050.4862 | 2449 | 0 | 39050.4862 | 2467 | 0 |  | 1293.5 | 1529.5 | 149.5116 | 0 | 150.6105 | 0 | 1.4951 | 0 | 1.5061 | 0 | 1.4951 | 1.5061 | 3.0372 | 2.2854 | 1.542
39050.4867 | 2149 | 0 | 39050.4867 | 1985 | 0 |  | 1335.5 | 1571.5 | 131.1966 | 0 | 121.1844 | 0 | 1.312 | 0 | 1.2118 | 0 | 1.312 | 1.2118 | 17.4211 | 27.1224 | 16.1092
39050.4872 | 2046 | 0 | 39050.4872 | 2367 | 0 |  | 1377.5 | 1613.5 | 124.9084 | 0 | 144.5055 | 0 | 1.2491 | 0 | 1.4451 | 0 | 1.2491 | 1.4451 | 23.3324 | 6.6067 | 22.0833
39050.4877 | 2260 | 0 | 39050.4877 | 2178 | 0 |  | 1419.5 | 1655.5 | 137.9731 | 0 | 132.967 | 0 | 1.3797 | 0 | 1.3297 | 0 | 1.3797 | 1.3297 | 11.654 | 15.8577 | 10.2743
39050.4882 | 2002 | 0 | 39050.4882 | 2491 | 0 |  | 1461.5 | 1697.5 | 122.2222 | 0 | 152.0757 | 0 | 1.2222 | 0 | 1.5208 | 0 | 1.2222 | 1.5208 | 26.043 | 1.2999 | 24.8207
39050.4887 | 2453 | 0 | 39050.4887 | 2039 | 0 |  | 1503.5 | 1739.5 | 149.7558 | 0 | 124.4811 | 0 | 1.4976 | 0 | 1.2448 | 0 | 1.4976 | 1.2448 | 2.8691 | 23.7558 | 1.3716
39050.4891 | 2095 | 0 | 39050.4892 | 1994 | 0 |  | 1545.5 | 1781.5 | 127.8999 | 0 | 121.7338 | 0 | 1.279 | 0 | 1.2173 | 0 | 1.279 | 1.2173 | 20.4477 | 26.5486 | 19.1687
39050.4896 | 2180 | 0 | 39050.4896 | 2235 | 0 |  | 1587.5 | 1823.5 | 133.0891 | 0 | 136.4469 | 0 | 1.3309 | 0 | 1.3645 | 0 | 1.3309 | 1.3645 | 15.7514 | 12.9029 | 14.4205
39050.4901 | 1941 | 0 | 39050.4901 | 1990 | 0 |  | 1629.5 | 1865.5 | 118.4982 | 0 | 121.4896 | 0 | 1.185 | 0 | 1.2149 | 0 | 1.185 | 1.2149 | 30.0041 | 26.803 | 28.8191
39050.4906 | 2158 | 0 | 39050.4906 | 2503 | 0 |  | 1671.5 | 1907.5 | 131.746 | 0 | 152.8083 | 0 | 1.3175 | 0 | 1.5281 | 0 | 1.3175 | 1.5281 | 16.9314 | 0.81422 | 15.614
39050.4911 | 1932 | 0 | 39050.4911 | 2478 | 0 |  | 1713.5 | 1949.5 | 117.9487 | 0 | 151.2821 | 0 | 1.1795 | 0 | 1.5128 | 0 | 1.1795 | 1.5128 | 30.6097 | 1.8313 | 29.4302
39050.4916 | 2482 | 0 | 39050.4916 | 2232 | 0 |  | 1755.5 | 1991.5 | 151.5263 | 0 | 136.2637 | 0 | 1.5153 | 0 | 1.3626 | 0 | 1.5153 | 1.3626 | 1.6672 | 13.0547 | 0.15194
39050.4921 | 2188 | 0 | 39050.4921 | 2113 | 0 |  | 1797.5 | 2033.5 | 133.5775 | 0 | 128.9988 | 0 | 1.3358 | 0 | 1.29 | 0 | 1.3358 | 1.29 | 15.3282 | 19.4217 | 13.9924
39050.4925 | 2407 | 0 | 39050.4926 | 2130 | 0 |  | 1839.5 | 2075.5 | 146.9475 | 0 | 130.0366 | 0 | 1.4695 | 0 | 1.3004 | 0 | 1.4695 | 1.3004 | 4.8351 | 18.4685 | 3.3656
39050.493 | 2123 | 0 | 39050.493 | 2418 | 0 |  | 1881.5 | 2117.5 | 129.6093 | 0 | 147.619 | 0 | 1.2961 | 0 | 1.4762 | 0 | 1.2961 | 1.4762 | 18.8592 | 4.3581 | 17.5631
39050.4935 | 1993 | 0 | 39050.4935 | 2406 | 0 |  | 1923.5 | 2159.5 | 121.6728 | 0 | 146.8864 | 0 | 1.2167 | 0 | 1.4689 | 0 | 1.2167 | 1.4689 | 26.6121 | 4.8786 | 25.3954

## A2-B3
Open Burn Test 14 |  |  | 2006-11-29 | 11:22 |  |  | Vs = |  | 157.3492 |  | R = | 100
Mixed | 7-C | Tray F | IRMS | 1
0 | 300 kW |  | Bundle | Ch. 2 & 3 | Cable A | Even - | Cable B |  | Odd
Time-11 | N11 | N12 | Time-12 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R3-G | R2-3
39050.4687 | 1 | 0 | 39050.4687 | 1 | 0 |  | -221 | 15 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257638 | 257638 | 257637.9994
39050.4692 | 1 | 0 | 39050.4692 | 1 | 0 |  | -179 | 57 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257638 | 257638 | 257637.9994
39050.4697 | 1 | 0 | 39050.4697 | 1 | 0 |  | -137 | 99 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257638 | 257638 | 257637.9994
39050.4702 | 1 | 0 | 39050.4702 | 1 | 0 |  | -95 | 141 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257638 | 257638 | 257637.9994
39050.4706 | 1 | 0 | 39050.4707 | 1 | 0 |  | -53 | 183 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257638 | 257638 | 257637.9994
39050.4711 | 1 | 0 | 39050.4711 | 1 | 0 |  | -11 | 225 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257638 | 257638 | 257637.9994
39050.4716 | 1 | 0 | 39050.4716 | 1 | 0 |  | 31 | 267 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257638 | 257638 | 257637.9994
39050.4721 | 1 | 0 | 39050.4721 | 1 | 0 |  | 73 | 309 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257638 | 257638 | 257637.9994
39050.4726 | 1 | 0 | 39050.4726 | 1 | 0 |  | 115 | 351 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257638 | 257638 | 257637.9994
39050.4731 | 1 | 0 | 39050.4731 | 1 | 0 |  | 157 | 393 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257638 | 257638 | 257637.9994
39050.4736 | 1 | 0 | 39050.4736 | 1 | 0 |  | 199 | 435 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257638 | 257638 | 257637.9994
39050.474 | 1 | 0 | 39050.4741 | 1 | 0 |  | 241 | 477 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257638 | 257638 | 257637.9994
39050.4745 | 1 | 0 | 39050.4745 | 1 | 0 |  | 283 | 519 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257638 | 257638 | 257637.9994
39050.475 | 1 | 0 | 39050.475 | 1 | 0 |  | 325 | 561 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257638 | 257638 | 257637.9994
39050.4755 | 1 | 0 | 39050.4755 | 1 | 0 |  | 367 | 603 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257638 | 257638 | 257637.9994
39050.476 | 1 | 0 | 39050.476 | 1 | 0 |  | 409 | 645 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257638 | 257638 | 257637.9994
39050.4765 | 1 | 0 | 39050.4765 | 1275 | 0 |  | 451 | 687 | 0.06105 | 0 | 77.8388 | 0 | 0.0006105 | 0 | 0.77839 | 0 | 0.0006105 | 0.77839 | 257638 | 102.1475 | 257637.9994
39050.477 | 1 | 0 | 39050.477 | 1841 | 0 |  | 493 | 729 | 0.06105 | 0 | 112.3932 | 0 | 0.0006105 | 0 | 1.1239 | 0 | 0.0006105 | 1.1239 | 257638 | 39.9989 | 257637.9994
39050.4774 | 1 | 0 | 39050.4775 | 1967 | 0 |  | 535 | 771 | 0.06105 | 0 | 120.0855 | 0 | 0.0006105 | 0 | 1.2009 | 0 | 0.0006105 | 1.2009 | 257638 | 31.031 | 257637.9994
39050.4779 | 2 | 0 | 39050.478 | 2463 | 0 |  | 577 | 813 | 0.1221 | 0 | 150.3663 | 0 | 0.001221 | 0 | 1.5037 | 0 | 0.001221 | 1.5037 | 128769 | 4.6439 | 128768.9988
39050.4784 | 1 | 0 | 39050.4784 | 1912 | 0 |  | 619 | 855 | 0.06105 | 0 | 116.7277 | 0 | 0.0006105 | 0 | 1.1673 | 0 | 0.0006105 | 1.1673 | 257638 | 34.8002 | 257637.9994
39050.4789 | 285 | 0 | 39050.4789 | 2156 | 0 |  | 661 | 897 | 17.3993 | 0 | 131.6239 | 0 | 0.17399 | 0 | 1.3162 | 0 | 0.17399 | 1.3162 | 804.3439 | 19.5445 | 804.1699
39050.4794 | 1890 | 0 | 39050.4794 | 1870 | 0 |  | 703 | 939 | 115.3846 | 0 | 114.1636 | 0 | 1.1538 | 0 | 1.1416 | 0 | 1.1538 | 1.1416 | 36.3693 | 37.8278 | 35.2155
39050.4799 | 2359 | 0 | 39050.4799 | 2014 | 0 |  | 745 | 981 | 144.0171 | 0 | 122.9548 | 0 | 1.4402 | 0 | 1.2295 | 0 | 1.4402 | 1.2295 | 9.2573 | 27.9732 | 7.8171
39050.4804 | 2279 | 0 | 39050.4804 | 2443 | 0 |  | 787 | 1023 | 139.1331 | 0 | 149.1453 | 0 | 1.3913 | 0 | 1.4915 | 0 | 1.3913 | 1.4915 | 13.0926 | 5.5006 | 11.7013
39050.4808 | 1876 | 0 | 39050.4809 | 2561 | 0 |  | 828.5 | 1064.5 | 114.5299 | 0 | 156.3492 | 0 | 1.1453 | 0 | 1.5635 | 0 | 1.1453 | 1.5635 | 37.387 | 0.63959 | 36.2417
39050.4813 | 1894 | 0 | 39050.4814 | 2070 | 0 |  | 871 | 1107 | 115.6288 | 0 | 126.3736 | 0 | 1.1563 | 0 | 1.2637 | 0 | 1.1563 | 1.2637 | 36.0813 | 24.5111 | 34.925
39050.4818 | 2435 | 0 | 39050.4818 | 2015 | 0 |  | 913 | 1149 | 148.6569 | 0 | 123.0159 | 0 | 1.4866 | 0 | 1.2302 | 0 | 1.4866 | 1.2302 | 5.8472 | 27.9097 | 4.3607
39050.4823 | 2482 | 0 | 39050.4823 | 2115 | 0 |  | 955 | 1191 | 151.5263 | 0 | 129.1209 | 0 | 1.5153 | 0 | 1.2912 | 0 | 1.5153 | 1.2912 | 3.8429 | 21.8619 | 2.3276
39050.4828 | 2391 | 0 | 39050.4828 | 2028 | 0 |  | 997 | 1233 | 145.9707 | 0 | 123.8095 | 0 | 1.4597 | 0 | 1.2381 | 0 | 1.4597 | 1.2381 | 7.7951 | 27.0897 | 6.3354
39050.4833 | 2464 | 0 | 39050.4833 | 2284 | 0 |  | 1039 | 1275 | 150.4274 | 0 | 139.4383 | 0 | 1.5043 | 0 | 1.3944 | 0 | 1.5043 | 1.3944 | 4.6015 | 12.845 | 3.0972
39050.4838 | 2370 | 0 | 39050.4838 | 2511 | 0 |  | 1080.5 | 1316.5 | 144.6886 | 0 | 153.2967 | 0 | 1.4469 | 0 | 1.533 | 0 | 1.4469 | 1.533 | 8.7502 | 2.6436 | 7.3033
39050.4842 | 2500 | 0 | 39050.4843 | 2199 | 0 |  | 1122.5 | 1358.5 | 152.6252 | 0 | 134.2491 | 0 | 1.5263 | 0 | 1.3425 | 0 | 1.5263 | 1.3425 | 3.0952 | 17.2069 | 1.5689
39050.4847 | 2196 | 0 | 39050.4847 | 1955 | 0 |  | 1164.5 | 1400.5 | 134.0659 | 0 | 119.3529 | 0 | 1.3407 | 0 | 1.1935 | 0 | 1.3407 | 1.1935 | 17.367 | 31.8353 | 16.0264
39050.4852 | 2515 | 0 | 39050.4852 | 2158 | 0 |  | 1206.5 | 1442.5 | 153.5409 | 0 | 131.746 | 0 | 1.5354 | 0 | 1.3175 | 0 | 1.5354 | 1.3175 | 2.4803 | 19.4337 | 0.94491
39050.4857 | 2307 | 0 | 39050.4857 | 1938 | 0 |  | 1248.5 | 1484.5 | 140.8425 | 0 | 118.315 | 0 | 1.4084 | 0 | 1.1832 | 0 | 1.4084 | 1.1832 | 11.72 | 32.9917 | 10.3116
39050.4862 | 2400 | 0 | 39050.4862 | 2058 | 0 |  | 1290.5 | 1526.5 | 146.5201 | 0 | 125.641 | 0 | 1.4652 | 0 | 1.2564 | 0 | 1.4652 | 1.2564 | 7.3908 | 25.2371 | 5.9256
39050.4867 | 2413 | 0 | 39050.4867 | 2313 | 0 |  | 1332.5 | 1568.5 | 147.3138 | 0 | 141.2088 | 0 | 1.4731 | 0 | 1.4121 | 0 | 1.4731 | 1.4121 | 6.8123 | 11.4302 | 5.3391
39050.4872 | 2269 | 0 | 39050.4872 | 2108 | 0 |  | 1374.5 | 1610.5 | 138.5226 | 0 | 128.6935 | 0 | 1.3852 | 0 | 1.2869 | 0 | 1.3852 | 1.2869 | 13.591 | 22.2666 | 12.2058
39050.4877 | 2114 | 0 | 39050.4877 | 2051 | 0 |  | 1416.5 | 1652.5 | 129.0598 | 0 | 125.2137 | 0 | 1.2906 | 0 | 1.2521 | 0 | 1.2906 | 1.2521 | 21.9196 | 25.6646 | 20.629
39050.4881 | 2392 | 0 | 39050.4881 | 1972 | 0 |  | 1458.5 | 1694.5 | 146.0317 | 0 | 120.3907 | 0 | 1.4603 | 0 | 1.2039 | 0 | 1.4603 | 1.2039 | 7.75 | 30.6988 | 6.2897
39050.4886 | 2304 | 0 | 39050.4886 | 1877 | 0 |  | 1500.5 | 1736.5 | 140.6593 | 0 | 114.591 | 0 | 1.4066 | 0 | 1.1459 | 0 | 1.4066 | 1.1459 | 11.8655 | 37.3138 | 10.4589
39050.4891 | 2456 | 0 | 39050.4891 | 2010 | 0 |  | 1542.5 | 1778.5 | 149.9389 | 0 | 122.7106 | 0 | 1.4994 | 0 | 1.2271 | 0 | 1.4994 | 1.2271 | 4.9422 | 28.2279 | 3.4428
39050.4896 | 1994 | 0 | 39050.4896 | 1893 | 0 |  | 1584.5 | 1820.5 | 121.7338 | 0 | 115.5678 | 0 | 1.2173 | 0 | 1.1557 | 0 | 1.2173 | 1.1557 | 29.2568 | 36.1532 | 28.0394
39050.4901 | 2331 | 0 | 39050.4901 | 2421 | 0 |  | 1626.5 | 1862.5 | 142.3077 | 0 | 147.8022 | 0 | 1.4231 | 0 | 1.478 | 0 | 1.4231 | 1.478 | 10.5697 | 6.4593 | 9.1466
39050.4906 | 2216 | 0 | 39050.4906 | 1844 | 0 |  | 1668.5 | 1904.5 | 135.2869 | 0 | 112.5763 | 0 | 1.3529 | 0 | 1.1258 | 0 | 1.3529 | 1.1258 | 16.3078 | 39.7711 | 14.9549
39050.4911 | 2372 | 0 | 39050.4911 | 2409 | 0 |  | 1710.5 | 1946.5 | 144.8107 | 0 | 147.0696 | 0 | 1.4481 | 0 | 1.4707 | 0 | 1.4481 | 1.4707 | 8.6585 | 6.9896 | 7.2104
39050.4915 | 2174 | 0 | 39050.4916 | 2008 | 0 |  | 1752.5 | 1988.5 | 132.7228 | 0 | 122.5885 | 0 | 1.3272 | 0 | 1.2259 | 0 | 1.3272 | 1.2259 | 18.5547 | 28.3556 | 17.2275
39050.492 | 2467 | 0 | 39050.492 | 2098 | 0 |  | 1794.5 | 2030.5 | 150.6105 | 0 | 128.083 | 0 | 1.5061 | 0 | 1.2808 | 0 | 1.5061 | 1.2808 | 4.4743 | 22.8494 | 2.9682
39050.4925 | 1944 | 0 | 39050.4925 | 2224 | 0 |  | 1836.5 | 2072.5 | 118.6813 | 0 | 135.7753 | 0 | 1.1868 | 0 | 1.3578 | 0 | 1.1868 | 1.3578 | 32.5813 | 15.8894 | 31.3945
39050.493 | 1868 | 0 | 39050.493 | 1787 | 0 |  | 1878.5 | 2114.5 | 114.0415 | 0 | 109.0965 | 0 | 1.1404 | 0 | 1.091 | 0 | 1.1404 | 1.091 | 37.9754 | 44.2294 | 36.835
39050.4935 | 1886 | 0 | 39050.4935 | 1830 | 0 |  | 1920.5 | 2156.5 | 115.1404 | 0 | 111.7216 | 0 | 1.1514 | 0 | 1.1172 | 0 | 1.1514 | 1.1172 | 36.6585 | 40.8404 | 35.5071

## A1-C6
Open Burn Test 14 |  |  | 2006-11-29 | 11:22 |  |  | Vs = |  | 160.4017 |  | R = | 100
Mixed | 7-C | Tray F | IRMS | 1
0 | 300 kW |  | Bundle | Ch. 1 & 6 | Cable A | Odd - | Cable C |  | Even
Time-9 | N11 | N12 | Time-10 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R6-G | R1-6
39050.4687 | 1 | 0 | 39050.4687 | 1 | 0 |  | -224 | 12 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262638 | 262638 | 262637.9994
39050.4691 | 1 | 0 | 39050.4692 | 1 | 0 |  | -182 | 54 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262638 | 262638 | 262637.9994
39050.4696 | 1 | 0 | 39050.4697 | 1 | 0 |  | -139.5 | 96.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262638 | 262638 | 262637.9994
39050.4701 | 1 | 0 | 39050.4701 | 1 | 0 |  | -97.5 | 138.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262638 | 262638 | 262637.9994
39050.4706 | 1 | 0 | 39050.4706 | 1 | 0 |  | -56 | 180 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262638 | 262638 | 262637.9994
39050.4711 | 1 | 0 | 39050.4711 | 1 | 0 |  | -14 | 222 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262638 | 262638 | 262637.9994
39050.4716 | 1 | 0 | 39050.4716 | 1 | 0 |  | 28 | 264 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262638 | 262638 | 262637.9994
39050.4721 | 1 | 0 | 39050.4721 | 1 | 0 |  | 70 | 306 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262638 | 262638 | 262637.9994
39050.4725 | 1 | 0 | 39050.4726 | 1 | 0 |  | 112 | 348 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262638 | 262638 | 262637.9994
39050.473 | 1 | 0 | 39050.4731 | 1 | 0 |  | 154 | 390 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262638 | 262638 | 262637.9994
39050.4735 | 1 | 0 | 39050.4735 | 1 | 0 |  | 196 | 432 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262638 | 262638 | 262637.9994
39050.474 | 1 | 0 | 39050.474 | 1 | 0 |  | 238 | 474 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262638 | 262638 | 262637.9994
39050.4745 | 1 | 0 | 39050.4745 | 1 | 0 |  | 280 | 516 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262638 | 262638 | 262637.9994
39050.475 | 1 | 0 | 39050.475 | 1 | 0 |  | 322 | 558 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262638 | 262638 | 262637.9994
39050.4755 | 1 | 0 | 39050.4755 | 1 | 0 |  | 364 | 600 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262638 | 262638 | 262637.9994
39050.4759 | 1 | 0 | 39050.476 | 1887 | 0 |  | 406 | 642 | 0.06105 | 0 | 115.2015 | 0 | 0.0006105 | 0 | 1.152 | 0 | 0.0006105 | 1.152 | 262638 | 39.2358 | 262637.9994
39050.4764 | 1 | 0 | 39050.4765 | 1974 | 0 |  | 448 | 684 | 0.06105 | 0 | 120.5128 | 0 | 0.0006105 | 0 | 1.2051 | 0 | 0.0006105 | 1.2051 | 262638 | 33.0993 | 262637.9994
39050.4769 | 1 | 0 | 39050.4769 | 2311 | 0 |  | 490 | 726 | 0.06105 | 0 | 141.0867 | 0 | 0.0006105 | 0 | 1.4109 | 0 | 0.0006105 | 1.4109 | 262638 | 13.6902 | 262637.9994
39050.4774 | 1 | 0 | 39050.4774 | 2341 | 0 |  | 532 | 768 | 0.06105 | 0 | 142.9182 | 0 | 0.0006105 | 0 | 1.4292 | 0 | 0.0006105 | 1.4292 | 262638 | 12.2332 | 262637.9994
39050.4779 | 1 | 0 | 39050.4779 | 2199 | 0 |  | 574 | 810 | 0.06105 | 0 | 134.2491 | 0 | 0.0006105 | 0 | 1.3425 | 0 | 0.0006105 | 1.3425 | 262638 | 19.4807 | 262637.9994
39050.4784 | 2 | 0 | 39050.4784 | 2376 | 0 |  | 616 | 852 | 0.1221 | 0 | 145.0549 | 0 | 0.001221 | 0 | 1.4505 | 0 | 0.001221 | 1.4505 | 131269 | 10.58 | 131268.9988
39050.4789 | 239 | 0 | 39050.4789 | 2006 | 0 |  | 658 | 894 | 14.591 | 0 | 122.4664 | 0 | 0.14591 | 0 | 1.2247 | 0 | 0.14591 | 1.2247 | 999.3222 | 30.9761 | 999.1763
39050.4794 | 1778 | 0 | 39050.4794 | 2054 | 0 |  | 700 | 936 | 108.547 | 0 | 125.3968 | 0 | 1.0855 | 0 | 1.254 | 0 | 1.0855 | 1.254 | 47.7717 | 27.9153 | 46.6862
39050.4798 | 2216 | 0 | 39050.4799 | 2568 | 0 |  | 742 | 978 | 135.2869 | 0 | 156.7766 | 0 | 1.3529 | 0 | 1.5678 | 0 | 1.3529 | 1.5678 | 18.5641 | 2.3123 | 17.2112
39050.4803 | 2019 | 0 | 39050.4803 | 2269 | 0 |  | 784 | 1020 | 123.2601 | 0 | 138.5226 | 0 | 1.2326 | 0 | 1.3852 | 0 | 1.2326 | 1.3852 | 30.1327 | 15.7946 | 28.9001
39050.4808 | 2152 | 0 | 39050.4808 | 2539 | 0 |  | 826 | 1062 | 131.3797 | 0 | 155.0061 | 0 | 1.3138 | 0 | 1.5501 | 0 | 1.3138 | 1.5501 | 22.0901 | 3.4809 | 20.7764
39050.4813 | 2309 | 0 | 39050.4813 | 2571 | 0 |  | 868 | 1104 | 140.9646 | 0 | 156.9597 | 0 | 1.4096 | 0 | 1.5696 | 0 | 1.4096 | 1.5696 | 13.7887 | 2.1929 | 12.379
39050.4818 | 2472 | 0 | 39050.4818 | 2007 | 0 |  | 910 | 1146 | 150.9158 | 0 | 122.5275 | 0 | 1.5092 | 0 | 1.2253 | 0 | 1.5092 | 1.2253 | 6.2856 | 30.9108 | 4.7764
39050.4823 | 2084 | 0 | 39050.4823 | 2407 | 0 |  | 952 | 1188 | 127.2283 | 0 | 146.9475 | 0 | 1.2723 | 0 | 1.4695 | 0 | 1.2723 | 1.4695 | 26.0739 | 9.1558 | 24.8016
39050.4828 | 2493 | 0 | 39050.4828 | 2032 | 0 |  | 994 | 1230 | 152.1978 | 0 | 124.0537 | 0 | 1.522 | 0 | 1.2405 | 0 | 1.522 | 1.2405 | 5.3903 | 29.3002 | 3.8683
39050.4832 | 1957 | 0 | 39050.4833 | 2572 | 0 |  | 1036 | 1272 | 119.475 | 0 | 157.0208 | 0 | 1.1947 | 0 | 1.5702 | 0 | 1.1947 | 1.5702 | 34.2555 | 2.1532 | 33.0607
39050.4837 | 2192 | 0 | 39050.4837 | 2478 | 0 |  | 1078 | 1314 | 133.8217 | 0 | 151.2821 | 0 | 1.3382 | 0 | 1.5128 | 0 | 1.3382 | 1.5128 | 19.8622 | 6.0282 | 18.524
39050.4842 | 2387 | 0 | 39050.4842 | 2346 | 0 |  | 1120 | 1356 | 145.7265 | 0 | 143.2234 | 0 | 1.4573 | 0 | 1.4322 | 0 | 1.4573 | 1.4322 | 10.0704 | 11.994 | 8.6131
39050.4847 | 2123 | 0 | 39050.4847 | 2047 | 0 |  | 1162 | 1398 | 129.6093 | 0 | 124.9695 | 0 | 1.2961 | 0 | 1.2497 | 0 | 1.2961 | 1.2497 | 23.7579 | 28.3527 | 22.4618
39050.4852 | 2087 | 0 | 39050.4852 | 2525 | 0 |  | 1204 | 1440 | 127.4115 | 0 | 154.1514 | 0 | 1.2741 | 0 | 1.5415 | 0 | 1.2741 | 1.5415 | 25.8927 | 4.0547 | 24.6186
39050.4857 | 1936 | 0 | 39050.4857 | 2611 | 0 |  | 1246 | 1482 | 118.1929 | 0 | 159.4017 | 0 | 1.1819 | 0 | 1.594 | 0 | 1.1819 | 1.594 | 35.7118 | 0.62735 | 34.5298
39050.4862 | 1933 | 0 | 39050.4862 | 2085 | 0 |  | 1288 | 1524 | 118.0098 | 0 | 127.2894 | 0 | 1.1801 | 0 | 1.2729 | 0 | 1.1801 | 1.2729 | 35.9224 | 26.0134 | 34.7423
39050.4866 | 2360 | 0 | 39050.4867 | 2530 | 0 |  | 1330 | 1566 | 144.0781 | 0 | 154.4567 | 0 | 1.4408 | 0 | 1.5446 | 0 | 1.4408 | 1.5446 | 11.3297 | 3.849 | 9.8889
39050.4871 | 2272 | 0 | 39050.4872 | 2597 | 0 |  | 1372 | 1608 | 138.7057 | 0 | 158.547 | 0 | 1.3871 | 0 | 1.5855 | 0 | 1.3871 | 1.5855 | 15.6417 | 1.1698 | 14.2547
39050.4876 | 2078 | 0 | 39050.4876 | 2109 | 0 |  | 1414 | 1650 | 126.862 | 0 | 128.7546 | 0 | 1.2686 | 0 | 1.2875 | 0 | 1.2686 | 1.2875 | 26.4379 | 24.5794 | 25.1693
39050.4881 | 1968 | 0 | 39050.4881 | 2293 | 0 |  | 1456 | 1692 | 120.1465 | 0 | 139.9878 | 0 | 1.2015 | 0 | 1.3999 | 0 | 1.2015 | 1.3999 | 33.5051 | 14.5826 | 32.3036
39050.4886 | 2052 | 0 | 39050.4886 | 2314 | 0 |  | 1498 | 1734 | 125.2747 | 0 | 141.2698 | 0 | 1.2527 | 0 | 1.4127 | 0 | 1.2527 | 1.4127 | 28.04 | 13.5428 | 26.7872
39050.4891 | 2075 | 0 | 39050.4891 | 2508 | 0 |  | 1540 | 1776 | 126.6789 | 0 | 153.1136 | 0 | 1.2668 | 0 | 1.5311 | 0 | 1.2668 | 1.5311 | 26.6207 | 4.76 | 25.3539
39050.4896 | 2367 | 0 | 39050.4896 | 2384 | 0 |  | 1582 | 1818 | 144.5055 | 0 | 145.5433 | 0 | 1.4451 | 0 | 1.4554 | 0 | 1.4451 | 1.4554 | 11.0004 | 10.2089 | 9.5554
39050.49 | 2022 | 0 | 39050.4901 | 2599 | 0 |  | 1624 | 1860 | 123.4432 | 0 | 158.6691 | 0 | 1.2344 | 0 | 1.5867 | 0 | 1.2344 | 1.5867 | 29.9397 | 1.092 | 28.7052
39050.4905 | 2518 | 0 | 39050.4906 | 2065 | 0 |  | 1666 | 1902 | 153.7241 | 0 | 126.0684 | 0 | 1.5372 | 0 | 1.2607 | 0 | 1.5372 | 1.2607 | 4.3439 | 27.2339 | 2.8067
39050.491 | 1943 | 0 | 39050.491 | 2478 | 0 |  | 1708 | 1944 | 118.6203 | 0 | 151.2821 | 0 | 1.1862 | 0 | 1.5128 | 0 | 1.1862 | 1.5128 | 35.2229 | 6.0282 | 34.0366
39050.4915 | 2501 | 0 | 39050.4915 | 2006 | 0 |  | 1750 | 1986 | 152.6862 | 0 | 122.4664 | 0 | 1.5269 | 0 | 1.2247 | 0 | 1.5269 | 1.2247 | 5.0532 | 30.9761 | 3.5263
39050.492 | 2472 | 0 | 39050.492 | 2069 | 0 |  | 1792 | 2028 | 150.9158 | 0 | 126.3126 | 0 | 1.5092 | 0 | 1.2631 | 0 | 1.5092 | 1.2631 | 6.2856 | 26.9879 | 4.7764
39050.4925 | 1991 | 0 | 39050.4925 | 2260 | 0 |  | 1834 | 2070 | 121.5507 | 0 | 137.9731 | 0 | 1.2155 | 0 | 1.3797 | 0 | 1.2155 | 1.3797 | 31.9628 | 16.2558 | 30.7473
39050.493 | 2192 | 0 | 39050.493 | 2542 | 0 |  | 1876 | 2112 | 133.8217 | 0 | 155.1893 | 0 | 1.3382 | 0 | 1.5519 | 0 | 1.3382 | 1.5519 | 19.8622 | 3.3588 | 18.524
39050.4934 | 2129 | 0 | 39050.4935 | 2250 | 0 |  | 1918 | 2154 | 129.9756 | 0 | 137.3626 | 0 | 1.2998 | 0 | 1.3736 | 0 | 1.2998 | 1.3736 | 23.4091 | 16.7724 | 22.1094

## A1-C5
Open Burn Test 14 |  |  | 2006-11-29 | 11:22 |  |  | Vs = |  | 158.6923 |  | R = | 100
Mixed | 7-C | Tray F | IRMS | 1
0 | 300 kW |  | Bundle | Ch. 1 & 5 | Cable A | Odd - | Cable C |  | Odd
Time-7 | N11 | N12 | Time-8 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R5-G | R1-5
39050.4686 | 1 | 0 | 39050.4686 | 1 | 0 |  | -226.5 | 9.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259838 | 259838 | 259837.9994
39050.4691 | 1 | 0 | 39050.4691 | 1 | 0 |  | -184.5 | 51.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259838 | 259838 | 259837.9994
39050.4696 | 1 | 0 | 39050.4696 | 1 | 0 |  | -142.5 | 93.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259838 | 259838 | 259837.9994
39050.4701 | 1 | 0 | 39050.4701 | 1 | 0 |  | -100.5 | 135.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259838 | 259838 | 259837.9994
39050.4706 | 1 | 0 | 39050.4706 | 1 | 0 |  | -58.5 | 177.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259838 | 259838 | 259837.9994
39050.4711 | 1 | 0 | 39050.4711 | 1 | 0 |  | -16.5 | 219.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259838 | 259838 | 259837.9994
39050.4716 | 1 | 0 | 39050.4716 | 1 | 0 |  | 25.5 | 261.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259838 | 259838 | 259837.9994
39050.472 | 1 | 0 | 39050.472 | 1 | 0 |  | 67.5 | 303.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259838 | 259838 | 259837.9994
39050.4725 | 1 | 0 | 39050.4725 | 1 | 0 |  | 109.5 | 345.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259838 | 259838 | 259837.9994
39050.473 | 1 | 0 | 39050.473 | 1 | 0 |  | 151.5 | 387.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259838 | 259838 | 259837.9994
39050.4735 | 1 | 0 | 39050.4735 | 1 | 0 |  | 193.5 | 429.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259838 | 259838 | 259837.9994
39050.474 | 1 | 0 | 39050.474 | 1 | 0 |  | 235.5 | 471.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259838 | 259838 | 259837.9994
39050.4745 | 1 | 0 | 39050.4745 | 1 | 0 |  | 277.5 | 513.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259838 | 259838 | 259837.9994
39050.475 | 1 | 0 | 39050.475 | 1 | 0 |  | 319.5 | 555.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259838 | 259838 | 259837.9994
39050.4754 | 1 | 0 | 39050.4755 | 1 | 0 |  | 361.5 | 597.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259838 | 259838 | 259837.9994
39050.4759 | 1 | 0 | 39050.4759 | 2043 | 0 |  | 403.5 | 639.5 | 0.06105 | 0 | 124.7253 | 0 | 0.0006105 | 0 | 1.2473 | 0 | 0.0006105 | 1.2473 | 259838 | 27.2335 | 259837.9994
39050.4764 | 1 | 0 | 39050.4764 | 1353 | 0 |  | 445.5 | 681.5 | 0.06105 | 0 | 82.6007 | 0 | 0.0006105 | 0 | 0.82601 | 0 | 0.0006105 | 0.82601 | 259838 | 92.1197 | 259837.9994
39050.4769 | 1 | 0 | 39050.4769 | 1988 | 0 |  | 487.5 | 723.5 | 0.06105 | 0 | 121.3675 | 0 | 0.0006105 | 0 | 1.2137 | 0 | 0.0006105 | 1.2137 | 259838 | 30.7535 | 259837.9994
39050.4774 | 1 | 0 | 39050.4774 | 2449 | 0 |  | 529.5 | 765.5 | 0.06105 | 0 | 149.5116 | 0 | 0.0006105 | 0 | 1.4951 | 0 | 0.0006105 | 1.4951 | 259838 | 6.1405 | 259837.9994
39050.4779 | 1 | 0 | 39050.4779 | 2532 | 0 |  | 571.5 | 807.5 | 0.06105 | 0 | 154.5788 | 0 | 0.0006105 | 0 | 1.5458 | 0 | 0.0006105 | 1.5458 | 259838 | 2.6611 | 259837.9994
39050.4784 | 6 | 0 | 39050.4784 | 2583 | 0 |  | 613.5 | 849.5 | 0.3663 | 0 | 157.6923 | 0 | 0.003663 | 0 | 1.5769 | 0 | 0.003663 | 1.5769 | 43223 | 0.63415 | 43222.9963
39050.4788 | 229 | 0 | 39050.4789 | 2450 | 0 |  | 655.5 | 891.5 | 13.9805 | 0 | 149.5726 | 0 | 0.1398 | 0 | 1.4957 | 0 | 0.1398 | 1.4957 | 1035.1004 | 6.0971 | 1034.9606
39050.4793 | 1560 | 0 | 39050.4793 | 2299 | 0 |  | 697 | 933 | 95.2381 | 0 | 140.3541 | 0 | 0.95238 | 0 | 1.4035 | 0 | 0.95238 | 1.4035 | 66.6269 | 13.0657 | 65.6745
39050.4798 | 2344 | 0 | 39050.4798 | 2331 | 0 |  | 739.5 | 975.5 | 143.1013 | 0 | 142.3077 | 0 | 1.431 | 0 | 1.4231 | 0 | 1.431 | 1.4231 | 10.8951 | 11.5135 | 9.464
39050.4803 | 1887 | 0 | 39050.4803 | 2529 | 0 |  | 781 | 1017 | 115.2015 | 0 | 154.3956 | 0 | 1.152 | 0 | 1.544 | 0 | 1.152 | 1.544 | 37.752 | 2.7829 | 36.6
39050.4808 | 2330 | 0 | 39050.4808 | 2212 | 0 |  | 823.5 | 1059.5 | 142.2466 | 0 | 135.0427 | 0 | 1.4225 | 0 | 1.3504 | 0 | 1.4225 | 1.3504 | 11.5614 | 17.5127 | 10.1389
39050.4813 | 2450 | 0 | 39050.4813 | 2516 | 0 |  | 865 | 1101 | 149.5726 | 0 | 153.602 | 0 | 1.4957 | 0 | 1.536 | 0 | 1.4957 | 1.536 | 6.0971 | 3.314 | 4.6014
39050.4818 | 2376 | 0 | 39050.4818 | 2303 | 0 |  | 907.5 | 1143.5 | 145.0549 | 0 | 140.5983 | 0 | 1.4505 | 0 | 1.406 | 0 | 1.4505 | 1.406 | 9.4015 | 12.8693 | 7.951
39050.4822 | 2474 | 0 | 39050.4823 | 2352 | 0 |  | 949.5 | 1185.5 | 151.0379 | 0 | 143.5897 | 0 | 1.5104 | 0 | 1.4359 | 0 | 1.5104 | 1.4359 | 5.0679 | 10.5179 | 3.5575
39050.4827 | 2193 | 0 | 39050.4827 | 2080 | 0 |  | 991.5 | 1227.5 | 133.8828 | 0 | 126.9841 | 0 | 1.3388 | 0 | 1.2698 | 0 | 1.3388 | 1.2698 | 18.5308 | 24.9702 | 17.192
39050.4832 | 2005 | 0 | 39050.4832 | 2183 | 0 |  | 1033.5 | 1269.5 | 122.4054 | 0 | 133.2723 | 0 | 1.2241 | 0 | 1.3327 | 0 | 1.2241 | 1.3327 | 29.6449 | 19.0738 | 28.4208
39050.4837 | 2130 | 0 | 39050.4837 | 2257 | 0 |  | 1075 | 1311 | 130.0366 | 0 | 137.79 | 0 | 1.3004 | 0 | 1.3779 | 0 | 1.3004 | 1.3779 | 22.0366 | 15.1697 | 20.7363
39050.4842 | 2350 | 0 | 39050.4842 | 2559 | 0 |  | 1117 | 1353 | 143.4676 | 0 | 156.2271 | 0 | 1.4347 | 0 | 1.5623 | 0 | 1.4347 | 1.5623 | 10.6119 | 1.578 | 9.1772
39050.4847 | 2379 | 0 | 39050.4847 | 2423 | 0 |  | 1159 | 1395 | 145.2381 | 0 | 147.9243 | 0 | 1.4524 | 0 | 1.4792 | 0 | 1.4524 | 1.4792 | 9.2636 | 7.2794 | 7.8112
39050.4852 | 2072 | 0 | 39050.4852 | 2309 | 0 |  | 1201 | 1437 | 126.4957 | 0 | 140.9646 | 0 | 1.265 | 0 | 1.4096 | 0 | 1.265 | 1.4096 | 25.4527 | 12.576 | 24.1877
39050.4856 | 2210 | 0 | 39050.4857 | 2578 | 0 |  | 1243 | 1479 | 134.9206 | 0 | 157.3871 | 0 | 1.3492 | 0 | 1.5739 | 0 | 1.3492 | 1.5739 | 17.619 | 0.82933 | 16.2698
39050.4861 | 2531 | 0 | 39050.4861 | 2054 | 0 |  | 1285 | 1521 | 154.5177 | 0 | 125.3968 | 0 | 1.5452 | 0 | 1.254 | 0 | 1.5452 | 1.254 | 2.7017 | 26.5521 | 1.1565
39050.4866 | 2335 | 0 | 39050.4866 | 2081 | 0 |  | 1327 | 1563 | 142.5519 | 0 | 127.0452 | 0 | 1.4255 | 0 | 1.2705 | 0 | 1.4255 | 1.2705 | 11.3225 | 24.9101 | 9.897
39050.4871 | 2499 | 0 | 39050.4871 | 2024 | 0 |  | 1369 | 1605 | 152.5641 | 0 | 123.5653 | 0 | 1.5256 | 0 | 1.2357 | 0 | 1.5256 | 1.2357 | 4.0168 | 28.4279 | 2.4912
39050.4876 | 1953 | 0 | 39050.4876 | 2164 | 0 |  | 1411 | 1647 | 119.2308 | 0 | 132.1123 | 0 | 1.1923 | 0 | 1.3211 | 0 | 1.1923 | 1.3211 | 33.0968 | 20.1192 | 31.9045
39050.4881 | 2378 | 0 | 39050.4881 | 2322 | 0 |  | 1453 | 1689 | 145.177 | 0 | 141.7582 | 0 | 1.4518 | 0 | 1.4176 | 0 | 1.4518 | 1.4176 | 9.3095 | 11.9457 | 7.8577
39050.4886 | 2519 | 0 | 39050.4886 | 2231 | 0 |  | 1495 | 1731 | 153.7851 | 0 | 136.2027 | 0 | 1.5379 | 0 | 1.362 | 0 | 1.5379 | 1.362 | 3.1909 | 16.5119 | 1.6531
39050.489 | 2073 | 0 | 39050.4891 | 2364 | 0 |  | 1537 | 1773 | 126.5568 | 0 | 144.3223 | 0 | 1.2656 | 0 | 1.4432 | 0 | 1.2656 | 1.4432 | 25.3922 | 9.9569 | 24.1266
39050.4895 | 2387 | 0 | 39050.4895 | 2574 | 0 |  | 1579 | 1815 | 145.7265 | 0 | 157.1429 | 0 | 1.4573 | 0 | 1.5714 | 0 | 1.4573 | 1.5714 | 8.8974 | 0.98601 | 7.4401
39050.49 | 2320 | 0 | 39050.49 | 2526 | 0 |  | 1621 | 1857 | 141.6361 | 0 | 154.2125 | 0 | 1.4164 | 0 | 1.5421 | 0 | 1.4164 | 1.5421 | 12.0422 | 2.905 | 10.6259
39050.4905 | 2418 | 0 | 39050.4905 | 2100 | 0 |  | 1663 | 1899 | 147.619 | 0 | 128.2051 | 0 | 1.4762 | 0 | 1.2821 | 0 | 1.4762 | 1.2821 | 7.5012 | 23.78 | 6.0251
39050.491 | 2348 | 0 | 39050.491 | 2126 | 0 |  | 1705 | 1941 | 143.3455 | 0 | 129.7924 | 0 | 1.4335 | 0 | 1.2979 | 0 | 1.4335 | 1.2979 | 10.7061 | 22.2662 | 9.2727
39050.4915 | 2328 | 0 | 39050.4915 | 2156 | 0 |  | 1747 | 1983 | 142.1245 | 0 | 131.6239 | 0 | 1.4212 | 0 | 1.3162 | 0 | 1.4212 | 1.3162 | 11.6572 | 20.5649 | 10.236
39050.492 | 2480 | 0 | 39050.492 | 2481 | 0 |  | 1789 | 2025 | 151.4042 | 0 | 151.4652 | 0 | 1.514 | 0 | 1.5147 | 0 | 1.514 | 1.5147 | 4.8137 | 4.7715 | 3.2997
39050.4924 | 2428 | 0 | 39050.4925 | 2163 | 0 |  | 1831 | 2067 | 148.2295 | 0 | 132.0513 | 0 | 1.4823 | 0 | 1.3205 | 0 | 1.4823 | 1.3205 | 7.0585 | 20.1748 | 5.5762
39050.4929 | 2308 | 0 | 39050.493 | 2366 | 0 |  | 1873 | 2109 | 140.9035 | 0 | 144.4444 | 0 | 1.409 | 0 | 1.4444 | 0 | 1.409 | 1.4444 | 12.6248 | 9.8639 | 11.2157
39050.4934 | 2002 | 0 | 39050.4934 | 2022 | 0 |  | 1915 | 2151 | 122.2222 | 0 | 123.4432 | 0 | 1.2222 | 0 | 1.2344 | 0 | 1.2222 | 1.2344 | 29.8392 | 28.5549 | 28.6169

## A1-B4
Open Burn Test 14 |  |  | 2006-11-29 | 11:22 |  |  | Vs = |  | 154.8462 |  | R = | 100
Mixed | 7-C | Tray F | IRMS | 1
0 | 300 kW |  | Bundle | Ch. 1 & 4 | Cable A | Odd - | Cable B |  | Even
Time-5 | N11 | N12 | Time-6 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R4-G | R1-4
39050.4686 | 1 | 0 | 39050.4686 | 1 | 0 |  | -229.5 | 6.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253538 | 253538 | 253537.9994
39050.4691 | 1 | 0 | 39050.4691 | 1 | 0 |  | -187.5 | 48.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253538 | 253538 | 253537.9994
39050.4696 | 1 | 0 | 39050.4696 | 1 | 0 |  | -145.5 | 90.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253538 | 253538 | 253537.9994
39050.4701 | 1 | 0 | 39050.4701 | 1 | 0 |  | -103.5 | 132.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253538 | 253538 | 253537.9994
39050.4705 | 1 | 0 | 39050.4706 | 1 | 0 |  | -61.5 | 174.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253538 | 253538 | 253537.9994
39050.471 | 1 | 0 | 39050.471 | 1 | 0 |  | -19.5 | 216.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253538 | 253538 | 253537.9994
39050.4715 | 1 | 0 | 39050.4715 | 1 | 0 |  | 22.5 | 258.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253538 | 253538 | 253537.9994
39050.472 | 1 | 0 | 39050.472 | 1 | 0 |  | 64.5 | 300.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253538 | 253538 | 253537.9994
39050.4725 | 1 | 0 | 39050.4725 | 1 | 0 |  | 106.5 | 342.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253538 | 253538 | 253537.9994
39050.473 | 1 | 0 | 39050.473 | 1 | 0 |  | 148.5 | 384.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253538 | 253538 | 253537.9994
39050.4735 | 1 | 0 | 39050.4735 | 1 | 0 |  | 190.5 | 426.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253538 | 253538 | 253537.9994
39050.4739 | 1 | 0 | 39050.474 | 1 | 0 |  | 232.5 | 468.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253538 | 253538 | 253537.9994
39050.4744 | 1 | 0 | 39050.4744 | 1 | 0 |  | 274.5 | 510.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253538 | 253538 | 253537.9994
39050.4749 | 1 | 0 | 39050.4749 | 1 | 0 |  | 316.5 | 552.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253538 | 253538 | 253537.9994
39050.4754 | 1 | 0 | 39050.4754 | 1 | 0 |  | 358.5 | 594.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253538 | 253538 | 253537.9994
39050.4759 | 1 | 0 | 39050.4759 | 1 | 0 |  | 400.5 | 636.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253538 | 253538 | 253537.9994
39050.4764 | 1 | 0 | 39050.4764 | 1 | 0 |  | 442.5 | 678.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253538 | 253538 | 253537.9994
39050.4769 | 1 | 0 | 39050.4769 | 77 | 0 |  | 484.5 | 720.5 | 0.06105 | 0 | 4.7009 | 0 | 0.0006105 | 0 | 0.047009 | 0 | 0.0006105 | 0.047009 | 253538 | 3194 | 253537.9994
39050.4773 | 1 | 0 | 39050.4774 | 2204 | 0 |  | 526.5 | 762.5 | 0.06105 | 0 | 134.5543 | 0 | 0.0006105 | 0 | 1.3455 | 0 | 0.0006105 | 1.3455 | 253538 | 15.0808 | 253537.9994
39050.4778 | 1 | 0 | 39050.4778 | 2136 | 0 |  | 568.5 | 804.5 | 0.06105 | 0 | 130.4029 | 0 | 0.0006105 | 0 | 1.304 | 0 | 0.0006105 | 1.304 | 253538 | 18.7444 | 253537.9994
39050.4783 | 4 | 0 | 39050.4783 | 2167 | 0 |  | 610.5 | 846.5 | 0.2442 | 0 | 132.2955 | 0 | 0.002442 | 0 | 1.323 | 0 | 0.002442 | 1.323 | 63309.5 | 17.0457 | 63309.4976
39050.4788 | 197 | 0 | 39050.4788 | 2266 | 0 |  | 652.5 | 888.5 | 12.0269 | 0 | 138.3394 | 0 | 0.12027 | 0 | 1.3834 | 0 | 0.12027 | 1.3834 | 1187.5025 | 11.932 | 1187.3823
39050.4793 | 458 | 0 | 39050.4793 | 2129 | 0 |  | 694.5 | 930.5 | 27.9609 | 0 | 129.9756 | 0 | 0.27961 | 0 | 1.2998 | 0 | 0.27961 | 1.2998 | 453.7948 | 19.1348 | 453.5152
39050.4798 | 2292 | 0 | 39050.4798 | 2199 | 0 |  | 736.5 | 972.5 | 139.9267 | 0 | 134.2491 | 0 | 1.3993 | 0 | 1.3425 | 0 | 1.3993 | 1.3425 | 10.6623 | 15.3424 | 9.263
39050.4803 | 2372 | 0 | 39050.4803 | 2520 | 0 |  | 778.5 | 1014.5 | 144.8107 | 0 | 153.8462 | 0 | 1.4481 | 0 | 1.5385 | 0 | 1.4481 | 1.5385 | 6.93 | 0.65 | 5.4819
39050.4808 | 2124 | 0 | 39050.4808 | 2431 | 0 |  | 820.5 | 1056.5 | 129.6703 | 0 | 148.4127 | 0 | 1.2967 | 0 | 1.4841 | 0 | 1.2967 | 1.4841 | 19.4153 | 4.3348 | 18.1186
39050.4812 | 2337 | 0 | 39050.4812 | 2425 | 0 |  | 862.5 | 1098.5 | 142.674 | 0 | 148.0464 | 0 | 1.4267 | 0 | 1.4805 | 0 | 1.4267 | 1.4805 | 8.5315 | 4.593 | 7.1047
39050.4817 | 2044 | 0 | 39050.4817 | 2268 | 0 |  | 904.5 | 1140.5 | 124.7863 | 0 | 138.4615 | 0 | 1.2479 | 0 | 1.3846 | 0 | 1.2479 | 1.3846 | 24.089 | 11.8333 | 22.8412
39050.4822 | 2006 | 0 | 39050.4822 | 1985 | 0 |  | 946.5 | 1182.5 | 122.4664 | 0 | 121.1844 | 0 | 1.2247 | 0 | 1.2118 | 0 | 1.2247 | 1.2118 | 26.4397 | 27.7773 | 25.215
39050.4827 | 1966 | 0 | 39050.4827 | 2149 | 0 |  | 988.5 | 1224.5 | 120.0244 | 0 | 131.1966 | 0 | 1.2002 | 0 | 1.312 | 0 | 1.2002 | 1.312 | 29.0122 | 18.0261 | 27.812
39050.4832 | 2207 | 0 | 39050.4832 | 2139 | 0 |  | 1030.5 | 1266.5 | 134.7375 | 0 | 130.5861 | 0 | 1.3474 | 0 | 1.3059 | 0 | 1.3474 | 1.3059 | 14.9243 | 18.5778 | 13.577
39050.4837 | 2205 | 0 | 39050.4837 | 2411 | 0 |  | 1072.5 | 1308.5 | 134.6154 | 0 | 147.1917 | 0 | 1.3462 | 0 | 1.4719 | 0 | 1.3462 | 1.4719 | 15.0286 | 5.2003 | 13.6824
39050.4842 | 1930 | 0 | 39050.4842 | 2412 | 0 |  | 1114.5 | 1350.5 | 117.8266 | 0 | 147.2527 | 0 | 1.1783 | 0 | 1.4725 | 0 | 1.1783 | 1.4725 | 31.4187 | 5.1567 | 30.2404
39050.4846 | 2313 | 0 | 39050.4847 | 1951 | 0 |  | 1156.5 | 1392.5 | 141.2088 | 0 | 119.1087 | 0 | 1.4121 | 0 | 1.1911 | 0 | 1.4121 | 1.1911 | 9.6576 | 30.0041 | 8.2455
39050.4851 | 2451 | 0 | 39050.4851 | 1990 | 0 |  | 1198.5 | 1434.5 | 149.6337 | 0 | 121.4896 | 0 | 1.4963 | 0 | 1.2149 | 0 | 1.4963 | 1.2149 | 3.4835 | 27.4563 | 1.9871
39050.4856 | 2142 | 0 | 39050.4856 | 2078 | 0 |  | 1240.5 | 1476.5 | 130.7692 | 0 | 126.862 | 0 | 1.3077 | 0 | 1.2686 | 0 | 1.3077 | 1.2686 | 18.4118 | 22.0587 | 17.1041
39050.4861 | 2518 | 0 | 39050.4861 | 2398 | 0 |  | 1282.5 | 1518.5 | 153.7241 | 0 | 146.398 | 0 | 1.5372 | 0 | 1.464 | 0 | 1.5372 | 1.464 | 0.72994 | 5.7706 | 0.8073
39050.4866 | 2064 | 0 | 39050.4866 | 1978 | 0 |  | 1324.5 | 1560.5 | 126.0073 | 0 | 120.757 | 0 | 1.2601 | 0 | 1.2076 | 0 | 1.2601 | 1.2076 | 22.8866 | 28.2295 | 21.6266
39050.4871 | 2325 | 0 | 39050.4871 | 2134 | 0 |  | 1366.5 | 1602.5 | 141.9414 | 0 | 130.2808 | 0 | 1.4194 | 0 | 1.3028 | 0 | 1.4194 | 1.3028 | 9.0916 | 18.8557 | 7.6722
39050.4876 | 2475 | 0 | 39050.4876 | 2132 | 0 |  | 1408.5 | 1644.5 | 151.0989 | 0 | 130.1587 | 0 | 1.511 | 0 | 1.3016 | 0 | 1.511 | 1.3016 | 2.48 | 18.9672 | 0.96901
39050.488 | 2477 | 0 | 39050.4881 | 2107 | 0 |  | 1450.5 | 1686.5 | 151.221 | 0 | 128.6325 | 0 | 1.5122 | 0 | 1.2863 | 0 | 1.5122 | 1.2863 | 2.3973 | 20.3787 | 0.88504
39050.4885 | 2327 | 0 | 39050.4885 | 2199 | 0 |  | 1492.5 | 1728.5 | 142.0635 | 0 | 134.2491 | 0 | 1.4206 | 0 | 1.3425 | 0 | 1.4206 | 1.3425 | 8.9979 | 15.3424 | 7.5772
39050.489 | 2437 | 0 | 39050.489 | 1905 | 0 |  | 1534.5 | 1770.5 | 148.779 | 0 | 116.3004 | 0 | 1.4878 | 0 | 1.163 | 0 | 1.4878 | 1.163 | 4.078 | 33.1433 | 2.5902
39050.4895 | 2067 | 0 | 39050.4895 | 2366 | 0 |  | 1576.5 | 1812.5 | 126.1905 | 0 | 144.4444 | 0 | 1.2619 | 0 | 1.4444 | 0 | 1.2619 | 1.4444 | 22.7083 | 7.2012 | 21.4464
39050.49 | 2270 | 0 | 39050.49 | 2121 | 0 |  | 1618.5 | 1854.5 | 138.5836 | 0 | 129.4872 | 0 | 1.3858 | 0 | 1.2949 | 0 | 1.3858 | 1.2949 | 11.7348 | 19.5842 | 10.349
39050.4905 | 2277 | 0 | 39050.4905 | 2185 | 0 |  | 1660.5 | 1896.5 | 139.011 | 0 | 133.3944 | 0 | 1.3901 | 0 | 1.3339 | 0 | 1.3901 | 1.3339 | 11.3913 | 16.0815 | 10.0012
39050.491 | 2370 | 0 | 39050.491 | 2373 | 0 |  | 1702.5 | 1938.5 | 144.6886 | 0 | 144.8718 | 0 | 1.4469 | 0 | 1.4487 | 0 | 1.4469 | 1.4487 | 7.0203 | 6.885 | 5.5734
39050.4914 | 2003 | 0 | 39050.4915 | 2045 | 0 |  | 1744.5 | 1980.5 | 122.2833 | 0 | 124.8474 | 0 | 1.2228 | 0 | 1.2485 | 0 | 1.2228 | 1.2485 | 26.6291 | 24.0284 | 25.4062
39050.4919 | 2015 | 0 | 39050.4919 | 2274 | 0 |  | 1786.5 | 2022.5 | 123.0159 | 0 | 138.8278 | 0 | 1.2302 | 0 | 1.3883 | 0 | 1.2302 | 1.3883 | 25.8749 | 11.5383 | 24.6448
39050.4924 | 2039 | 0 | 39050.4924 | 1752 | 0 |  | 1828.5 | 2064.5 | 124.4811 | 0 | 106.9597 | 0 | 1.2448 | 0 | 1.0696 | 0 | 1.2448 | 1.0696 | 24.3933 | 44.7705 | 23.1485
39050.4929 | 2333 | 0 | 39050.4929 | 1968 | 0 |  | 1870.5 | 2106.5 | 142.4298 | 0 | 120.1465 | 0 | 1.4243 | 0 | 1.2015 | 0 | 1.4243 | 1.2015 | 8.7175 | 28.8811 | 7.2932
39050.4934 | 2239 | 0 | 39050.4934 | 1754 | 0 |  | 1912.5 | 2148.5 | 136.6911 | 0 | 107.0818 | 0 | 1.3669 | 0 | 1.0708 | 0 | 1.3669 | 1.0708 | 13.2818 | 44.6055 | 11.9149

## A1-B3
Open Burn Test 14 |  |  | 2006-11-29 | 11:22 |  |  | Vs = |  | 152.5263 |  | R = | 100
Mixed | 7-C | Tray F | IRMS | 1
0 | 300 kW |  | Bundle | Ch. 1 & 3 | Cable A | Odd - | Cable B |  | Odd
Time-3 | N11 | N12 | Time-4 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R3-G | R1-3
39050.4686 | 1 | 0 | 39050.4686 | 1 | 0 |  | -232.5 | 3.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
39050.4691 | 1 | 0 | 39050.4691 | 1 | 0 |  | -190 | 46 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
39050.4695 | 1 | 0 | 39050.4695 | 1 | 0 |  | -148.5 | 87.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
39050.47 | 1 | 0 | 39050.47 | 1 | 0 |  | -106.5 | 129.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
39050.4705 | 1 | 0 | 39050.4705 | 1 | 0 |  | -64.5 | 171.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
39050.471 | 1 | 0 | 39050.471 | 1 | 0 |  | -22.5 | 213.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
39050.4715 | 1 | 0 | 39050.4715 | 1 | 0 |  | 19.5 | 255.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
39050.472 | 1 | 0 | 39050.472 | 1 | 0 |  | 61.5 | 297.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
39050.4725 | 1 | 0 | 39050.4725 | 1 | 0 |  | 103.5 | 339.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
39050.4729 | 1 | 0 | 39050.473 | 1 | 0 |  | 145.5 | 381.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
39050.4734 | 1 | 0 | 39050.4734 | 1 | 0 |  | 187.5 | 423.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
39050.4739 | 1 | 0 | 39050.4739 | 1 | 0 |  | 229.5 | 465.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
39050.4744 | 1 | 0 | 39050.4744 | 1 | 0 |  | 271.5 | 507.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
39050.4749 | 1 | 0 | 39050.4749 | 1 | 0 |  | 313.5 | 549.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
39050.4754 | 1 | 0 | 39050.4754 | 1 | 0 |  | 355.5 | 591.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
39050.4759 | 1 | 0 | 39050.4759 | 1 | 0 |  | 397.5 | 633.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
39050.4763 | 1 | 0 | 39050.4764 | 61 | 0 |  | 439.5 | 675.5 | 0.06105 | 0 | 3.7241 | 0 | 0.0006105 | 0 | 0.037241 | 0 | 0.0006105 | 0.037241 | 249738 | 3995.7049 | 249737.9994
39050.4768 | 1 | 0 | 39050.4768 | 1741 | 0 |  | 481.5 | 717.5 | 0.06105 | 0 | 106.2882 | 0 | 0.0006105 | 0 | 1.0629 | 0 | 0.0006105 | 1.0629 | 249738 | 43.5026 | 249737.9994
39050.4773 | 1 | 0 | 39050.4773 | 2335 | 0 |  | 523.5 | 759.5 | 0.06105 | 0 | 142.5519 | 0 | 0.0006105 | 0 | 1.4255 | 0 | 0.0006105 | 1.4255 | 249738 | 6.997 | 249737.9994
39050.4778 | 1 | 0 | 39050.4778 | 2403 | 0 |  | 565.5 | 801.5 | 0.06105 | 0 | 146.7033 | 0 | 0.0006105 | 0 | 1.467 | 0 | 0.0006105 | 1.467 | 249738 | 3.9692 | 249737.9994
39050.4783 | 1 | 0 | 39050.4783 | 2267 | 0 |  | 607.5 | 843.5 | 0.06105 | 0 | 138.4005 | 0 | 0.0006105 | 0 | 1.384 | 0 | 0.0006105 | 1.384 | 249738 | 10.2064 | 249737.9994
39050.4788 | 102 | 0 | 39050.4788 | 2276 | 0 |  | 649.5 | 885.5 | 6.2271 | 0 | 138.9499 | 0 | 0.062271 | 0 | 1.3895 | 0 | 0.062271 | 1.3895 | 2349.3922 | 9.7707 | 2349.3299
39050.4793 | 394 | 0 | 39050.4793 | 1920 | 0 |  | 691.5 | 927.5 | 24.0537 | 0 | 117.2161 | 0 | 0.24054 | 0 | 1.1722 | 0 | 0.24054 | 1.1722 | 534.1066 | 30.124 | 533.8661
39050.4797 | 1974 | 0 | 39050.4798 | 2099 | 0 |  | 733.5 | 969.5 | 120.5128 | 0 | 128.1441 | 0 | 1.2051 | 0 | 1.2814 | 0 | 1.2051 | 1.2814 | 26.5643 | 19.0272 | 25.3592
39050.4802 | 2009 | 0 | 39050.4802 | 1976 | 0 |  | 775.5 | 1011.5 | 122.6496 | 0 | 120.6349 | 0 | 1.2265 | 0 | 1.2063 | 0 | 1.2265 | 1.2063 | 24.3594 | 26.4362 | 23.1329
39050.4807 | 2241 | 0 | 39050.4807 | 2463 | 0 |  | 817.5 | 1053.5 | 136.8132 | 0 | 150.3663 | 0 | 1.3681 | 0 | 1.5037 | 0 | 1.3681 | 1.5037 | 11.4851 | 1.4365 | 10.1169
39050.4812 | 2445 | 0 | 39050.4812 | 2340 | 0 |  | 859.5 | 1095.5 | 149.2674 | 0 | 142.8571 | 0 | 1.4927 | 0 | 1.4286 | 0 | 1.4927 | 1.4286 | 2.1832 | 6.7684 | 0.69056
39050.4817 | 2334 | 0 | 39050.4817 | 2332 | 0 |  | 901.5 | 1137.5 | 142.4908 | 0 | 142.3687 | 0 | 1.4249 | 0 | 1.4237 | 0 | 1.4249 | 1.4237 | 7.0428 | 7.1346 | 5.6179
39050.4822 | 1951 | 0 | 39050.4822 | 2258 | 0 |  | 943.5 | 1179.5 | 119.1087 | 0 | 137.851 | 0 | 1.1911 | 0 | 1.3785 | 0 | 1.1911 | 1.3785 | 28.0564 | 10.6457 | 26.8653
39050.4827 | 2196 | 0 | 39050.4827 | 2453 | 0 |  | 985.5 | 1221.5 | 134.0659 | 0 | 149.7558 | 0 | 1.3407 | 0 | 1.4976 | 0 | 1.3407 | 1.4976 | 13.7696 | 1.85 | 12.4289
39050.4831 | 2379 | 0 | 39050.4832 | 2450 | 0 |  | 1027.5 | 1263.5 | 145.2381 | 0 | 149.5726 | 0 | 1.4524 | 0 | 1.4957 | 0 | 1.4524 | 1.4957 | 5.0181 | 1.9747 | 3.5657
39050.4836 | 2209 | 0 | 39050.4836 | 2019 | 0 |  | 1069.5 | 1305.5 | 134.8596 | 0 | 123.2601 | 0 | 1.3486 | 0 | 1.2326 | 0 | 1.3486 | 1.2326 | 13.1 | 23.7434 | 11.7514
39050.4841 | 2319 | 0 | 39050.4841 | 2293 | 0 |  | 1111.5 | 1347.5 | 141.5751 | 0 | 139.9878 | 0 | 1.4158 | 0 | 1.3999 | 0 | 1.4158 | 1.3999 | 7.7352 | 8.9568 | 6.3195
39050.4846 | 2453 | 0 | 39050.4846 | 2009 | 0 |  | 1153.5 | 1389.5 | 149.7558 | 0 | 122.6496 | 0 | 1.4976 | 0 | 1.2265 | 0 | 1.4976 | 1.2265 | 1.85 | 24.3594 | 0.35242
39050.4851 | 2283 | 0 | 39050.4851 | 1989 | 0 |  | 1195.5 | 1431.5 | 139.3773 | 0 | 121.4286 | 0 | 1.3938 | 0 | 1.2143 | 0 | 1.3938 | 1.2143 | 9.4341 | 25.6099 | 8.0403
39050.4856 | 2438 | 0 | 39050.4856 | 1785 | 0 |  | 1237.5 | 1473.5 | 148.84 | 0 | 108.9744 | 0 | 1.4884 | 0 | 1.0897 | 0 | 1.4884 | 1.0897 | 2.4766 | 39.9653 | 0.98822
39050.4861 | 2145 | 0 | 39050.4861 | 1861 | 0 |  | 1279.5 | 1515.5 | 130.9524 | 0 | 113.6142 | 0 | 1.3095 | 0 | 1.1361 | 0 | 1.3095 | 1.1361 | 16.4746 | 34.2493 | 15.1651
39050.4866 | 2457 | 0 | 39050.4866 | 1858 | 0 |  | 1321.5 | 1557.5 | 150 | 0 | 113.431 | 0 | 1.5 | 0 | 1.1343 | 0 | 1.5 | 1.1343 | 1.6842 | 34.4661 | 0.18417
39050.487 | 2173 | 0 | 39050.487 | 2248 | 0 |  | 1363.5 | 1599.5 | 132.6618 | 0 | 137.2405 | 0 | 1.3266 | 0 | 1.3724 | 0 | 1.3266 | 1.3724 | 14.9738 | 11.1379 | 13.6472
39050.4875 | 2035 | 0 | 39050.4875 | 2118 | 0 |  | 1405.5 | 1641.5 | 124.2369 | 0 | 129.304 | 0 | 1.2424 | 0 | 1.293 | 0 | 1.2424 | 1.293 | 22.7705 | 17.9594 | 21.5281
39050.488 | 2381 | 0 | 39050.488 | 1956 | 0 |  | 1447.5 | 1683.5 | 145.3602 | 0 | 119.4139 | 0 | 1.4536 | 0 | 1.1941 | 0 | 1.4536 | 1.1941 | 4.9299 | 27.729 | 3.4763
39050.4885 | 2014 | 0 | 39050.4885 | 2120 | 0 |  | 1489.5 | 1725.5 | 122.9548 | 0 | 129.4261 | 0 | 1.2295 | 0 | 1.2943 | 0 | 1.2295 | 1.2943 | 24.0506 | 17.8481 | 22.8211
39050.489 | 2482 | 0 | 39050.489 | 2363 | 0 |  | 1531.5 | 1767.5 | 151.5263 | 0 | 144.2613 | 0 | 1.5153 | 0 | 1.4426 | 0 | 1.5153 | 1.4426 | 0.65995 | 5.7292 | 0.85531
39050.4895 | 2472 | 0 | 39050.4895 | 1986 | 0 |  | 1573.5 | 1809.5 | 150.9158 | 0 | 121.2454 | 0 | 1.5092 | 0 | 1.2125 | 0 | 1.5092 | 1.2125 | 1.0672 | 25.7996 | 0.44201
39050.49 | 2344 | 0 | 39050.49 | 1953 | 0 |  | 1615.5 | 1851.5 | 143.1013 | 0 | 119.2308 | 0 | 1.431 | 0 | 1.1923 | 0 | 1.431 | 1.1923 | 6.5862 | 27.9252 | 5.1552
39050.4904 | 2275 | 0 | 39050.4905 | 2261 | 0 |  | 1657.5 | 1893.5 | 138.8889 | 0 | 138.0342 | 0 | 1.3889 | 0 | 1.3803 | 0 | 1.3889 | 1.3803 | 9.8189 | 10.4989 | 8.43
39050.4909 | 1967 | 0 | 39050.4909 | 1983 | 0 |  | 1699.5 | 1935.5 | 120.0855 | 0 | 121.0623 | 0 | 1.2009 | 0 | 1.2106 | 0 | 1.2009 | 1.2106 | 27.0147 | 25.9899 | 25.8139
39050.4914 | 2357 | 0 | 39050.4914 | 2148 | 0 |  | 1741.5 | 1977.5 | 143.895 | 0 | 131.1355 | 0 | 1.4389 | 0 | 1.3114 | 0 | 1.4389 | 1.3114 | 5.9983 | 16.3119 | 4.5594
39050.4919 | 2406 | 0 | 39050.4919 | 2324 | 0 |  | 1783.5 | 2019.5 | 146.8864 | 0 | 141.8803 | 0 | 1.4689 | 0 | 1.4188 | 0 | 1.4689 | 1.4188 | 3.8396 | 7.5034 | 2.3707
39050.4924 | 2081 | 0 | 39050.4924 | 2177 | 0 |  | 1825.5 | 2061.5 | 127.0452 | 0 | 132.906 | 0 | 1.2705 | 0 | 1.3291 | 0 | 1.2705 | 1.3291 | 20.0567 | 14.7625 | 18.7863
39050.4929 | 2026 | 0 | 39050.4929 | 1951 | 0 |  | 1867.5 | 2103.5 | 123.6874 | 0 | 119.1087 | 0 | 1.2369 | 0 | 1.1911 | 0 | 1.2369 | 1.1911 | 23.3159 | 28.0564 | 22.079
39050.4934 | 2121 | 0 | 39050.4934 | 2084 | 0 |  | 1909.5 | 2145.5 | 129.4872 | 0 | 127.2283 | 0 | 1.2949 | 0 | 1.2723 | 0 | 1.2949 | 1.2723 | 17.7926 | 19.8839 | 16.4977

## A1-A2
Open Burn Test 14 |  |  | 2006-11-29 | 11:22 |  |  | Vs = |  | 154.9072 |  | R = | 100
Mixed | 7-C | Tray F | IRMS | 1
0 | 300 kW |  | Bundle | Ch. 1 & 2 | Cable A | Odd-Even
Time-1 | N11 | N12 | Time-2 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R2-G | R1-2
39050.4685 | 1 | 0 | 39050.4686 | 1 | 0 |  | -235 | 1 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253638 | 253638 | 253637.9994
39050.469 | 1 | 0 | 39050.469 | 1 | 0 |  | -193 | 43 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253638 | 253638 | 253637.9994
39050.4695 | 1 | 0 | 39050.4695 | 1 | 0 |  | -151 | 85 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253638 | 253638 | 253637.9994
39050.47 | 1 | 0 | 39050.47 | 1 | 0 |  | -109 | 127 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253638 | 253638 | 253637.9994
39050.4705 | 1 | 0 | 39050.4705 | 1 | 0 |  | -67 | 169 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253638 | 253638 | 253637.9994
39050.471 | 1 | 0 | 39050.471 | 1 | 0 |  | -25 | 211 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253638 | 253638 | 253637.9994
39050.4714 | 1 | 0 | 39050.4715 | 1 | 0 |  | 17 | 253 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253638 | 253638 | 253637.9994
39050.4719 | 1 | 0 | 39050.472 | 1 | 0 |  | 59 | 295 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253638 | 253638 | 253637.9994
39050.4724 | 1 | 0 | 39050.4724 | 1 | 0 |  | 101 | 337 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253638 | 253638 | 253637.9994
39050.4729 | 1 | 0 | 39050.4729 | 1 | 0 |  | 143 | 379 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253638 | 253638 | 253637.9994
39050.4734 | 1 | 0 | 39050.4734 | 1 | 0 |  | 185 | 421 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253638 | 253638 | 253637.9994
39050.4739 | 1 | 0 | 39050.4739 | 1 | 0 |  | 227 | 463 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253638 | 253638 | 253637.9994
| 1 | 0 | 39050.4744 | 1 | 0 |  | 270 | 506 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253638 | 253638 | 253637.9994
39050.4748 | 1 | 0 | 39050.4749 | 1 | 0 |  | 311 | 547 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253638 | 253638 | 253637.9994
39050.4753 | 1 | 0 | 39050.4754 | 1 | 0 |  | 353 | 589 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253638 | 253638 | 253637.9994
39050.4758 | 1 | 0 | 39050.4758 | 1 | 0 |  | 395 | 631 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253638 | 253638 | 253637.9994
39050.4763 | 1 | 0 | 39050.4763 | 1 | 0 |  | 437 | 673 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253638 | 253638 | 253637.9994
39050.4768 | 1 | 0 | 39050.4768 | 1 | 0 |  | 479 | 715 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253638 | 253638 | 253637.9994
39050.4773 | 1 | 0 | 39050.4773 | 1 | 0 |  | 521 | 757 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253638 | 253638 | 253637.9994
39050.4778 | 2 | 0 | 39050.4778 | 1 | 0 |  | 563 | 799 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 126769 | 253638 | 126768.9988
39050.4783 | 61 | 16 | 39050.4783 | 54 | 34 |  | 604.5 | 840.5 | 3.7241 | 0.9768 | 3.2967 | 2.0757 | 0.037241 | 0.009768 | 0.032967 | 0.020757 | 0.027473 | 0.01221 | 5518.3817 | 12811.5751 | 15258.2774
39050.4787 | 525 | 325 | 39050.4788 | 425 | 303 |  | 646.5 | 882.5 | 32.0513 | 19.8413 | 25.9463 | 18.4982 | 0.32051 | 0.19841 | 0.25946 | 0.18498 | 0.1221 | 0.074481 | 1084.6798 | 2245.6483 | 497.0595
39050.4792 | 1054 | 773 | 39050.4792 | 860 | 589 |  | 689 | 925 | 64.3468 | 47.1917 | 52.5031 | 35.9585 | 0.64347 | 0.47192 | 0.52503 | 0.35958 | 0.17155 | 0.16545 | 776.3266 | 859.6224 | 82.3225
39050.4797 | 1924 | 74 | 39050.4797 | 1829 | 61 |  | 731 | 967 | 117.4603 | 4.5177 | 111.6606 | 3.7241 | 1.1746 | 0.045177 | 1.1166 | 0.037241 | 1.1294 | 1.0794 | 36.4502 | 44.2558 | 223.6146
39050.4802 | 1848 | 19 | 39050.4802 | 2387 | 20 |  | 773 | 1009 | 112.8205 | 1.16 | 145.7265 | 1.221 | 1.1282 | 0.0116 | 1.4573 | 0.01221 | 1.1166 | 1.4451 | 44.8942 | 6.4751 | 214.5671
39050.4807 | 2032 | 10 | 39050.4807 | 2365 | 10 |  | 815 | 1051 | 124.0537 | 0.6105 | 144.3834 | 0.6105 | 1.2405 | 0.006105 | 1.4438 | 0.006105 | 1.2344 | 1.4377 | 26.7744 | 7.4377 | 342.9419
39050.4812 | 2007 | 5 | 39050.4812 | 2279 | 4 |  | 856.5 | 1092.5 | 122.5275 | 0.30525 | 139.1331 | 0.2442 | 1.2253 | 0.0030525 | 1.3913 | 0.002442 | 1.2222 | 1.3889 | 27.0842 | 11.4316 | 1077.9566
39050.4817 | 2409 | 3 | 39050.4817 | 2060 | 2 |  | 898.5 | 1134.5 | 147.0696 | 0.18315 | 125.7631 | 0.1221 | 1.4707 | 0.0018315 | 1.2576 | 0.001221 | 1.4689 | 1.2564 | 5.3641 | 23.6243 | 798.6605
39050.4821 | 1961 | 1 | 39050.4822 | 2258 | 1 |  | 941 | 1177 | 119.7192 | 0.06105 | 137.851 | 0.06105 | 1.1972 | 0.0006105 | 1.3785 | 0.0006105 | 1.1966 | 1.3779 | 29.5287 | 12.397 | 6346.2329
39050.4826 | 2480 | 0 | 39050.4827 | 2426 | 0 |  | 983 | 1219 | 151.4042 | 0 | 148.1074 | 0 | 1.514 | 0 | 1.4811 | 0 | 1.514 | 1.4811 | 2.3137 | 4.5911 | 0.79967
39050.4831 | 2280 | 0 | 39050.4831 | 2077 | 0 |  | 1025 | 1261 | 139.1941 | 0 | 126.801 | 0 | 1.3919 | 0 | 1.268 | 0 | 1.3919 | 1.268 | 11.2886 | 22.1656 | 9.8967
39050.4836 | 2128 | 0 | 39050.4836 | 2042 | 0 |  | 1066.5 | 1302.5 | 129.9145 | 0 | 124.6642 | 0 | 1.2991 | 0 | 1.2466 | 0 | 1.2991 | 1.2466 | 19.2378 | 24.2595 | 17.9386
39050.4841 | 2115 | 0 | 39050.4841 | 2369 | 0 |  | 1108.5 | 1344.5 | 129.1209 | 0 | 144.6276 | 0 | 1.2912 | 0 | 1.4463 | 0 | 1.2912 | 1.4463 | 19.9707 | 7.1076 | 18.6795
39050.4846 | 2360 | 0 | 39050.4846 | 2059 | 0 |  | 1150.5 | 1386.5 | 144.0781 | 0 | 125.7021 | 0 | 1.4408 | 0 | 1.257 | 0 | 1.4408 | 1.257 | 7.5161 | 23.2336 | 6.0753
39050.4851 | 2421 | 0 | 39050.4851 | 2218 | 0 |  | 1193 | 1429 | 147.8022 | 0 | 135.409 | 0 | 1.478 | 0 | 1.3541 | 0 | 1.478 | 1.3541 | 4.8071 | 14.3995 | 3.3291
39050.4855 | 2513 | 0 | 39050.4856 | 2303 | 0 |  | 1234.5 | 1470.5 | 153.4188 | 0 | 140.5983 | 0 | 1.5342 | 0 | 1.406 | 0 | 1.5342 | 1.406 | 0.97016 | 10.1772 | 0.56403
39050.486 | 2003 | 0 | 39050.486 | 2395 | 0 |  | 1276.5 | 1512.5 | 122.2833 | 0 | 146.2149 | 0 | 1.2228 | 0 | 1.4621 | 0 | 1.2228 | 1.4621 | 26.679 | 5.9449 | 25.4561
39050.4865 | 2457 | 0 | 39050.4865 | 2195 | 0 |  | 1318.5 | 1554.5 | 150 | 0 | 134.0049 | 0 | 1.5 | 0 | 1.34 | 0 | 1.5 | 1.34 | 3.2715 | 15.5982 | 1.7715
39050.487 | 2022 | 0 | 39050.487 | 2449 | 0 |  | 1360.5 | 1596.5 | 123.4432 | 0 | 149.5116 | 0 | 1.2344 | 0 | 1.4951 | 0 | 1.2344 | 1.4951 | 25.4886 | 3.6088 | 24.2542
39050.4875 | 2476 | 0 | 39050.4875 | 2365 | 0 |  | 1402.5 | 1638.5 | 151.16 | 0 | 144.3834 | 0 | 1.5116 | 0 | 1.4438 | 0 | 1.5116 | 1.4438 | 2.479 | 7.2888 | 0.9674
39050.488 | 2257 | 0 | 39050.488 | 2465 | 0 |  | 1444.5 | 1680.5 | 137.79 | 0 | 150.4884 | 0 | 1.3779 | 0 | 1.5049 | 0 | 1.3779 | 1.5049 | 12.4227 | 2.9363 | 11.0448
39050.4885 | 2265 | 0 | 39050.4885 | 2160 | 0 |  | 1486.5 | 1722.5 | 138.2784 | 0 | 131.8681 | 0 | 1.3828 | 0 | 1.3187 | 0 | 1.3828 | 1.3187 | 12.0256 | 17.4713 | 10.6428
39050.4889 | 1943 | 0 | 39050.489 | 2059 | 0 |  | 1528.5 | 1764.5 | 118.6203 | 0 | 125.7021 | 0 | 1.1862 | 0 | 1.257 | 0 | 1.1862 | 1.257 | 30.5908 | 23.2336 | 29.4046
39050.4894 | 2440 | 0 | 39050.4894 | 2154 | 0 |  | 1570.5 | 1806.5 | 148.9621 | 0 | 131.5018 | 0 | 1.4896 | 0 | 1.315 | 0 | 1.4896 | 1.315 | 3.991 | 17.7985 | 2.5014
39050.4899 | 2403 | 0 | 39050.4899 | 2059 | 0 |  | 1612.5 | 1848.5 | 146.7033 | 0 | 125.7021 | 0 | 1.467 | 0 | 1.257 | 0 | 1.467 | 1.257 | 5.5922 | 23.2336 | 4.1251
39050.4904 | 2226 | 0 | 39050.4904 | 2521 | 0 |  | 1654.5 | 1890.5 | 135.8974 | 0 | 153.9072 | 0 | 1.359 | 0 | 1.5391 | 0 | 1.359 | 1.5391 | 13.9883 | 0.64974 | 12.6293
39050.4909 | 2277 | 0 | 39050.4909 | 2221 | 0 |  | 1696.5 | 1932.5 | 139.011 | 0 | 135.5922 | 0 | 1.3901 | 0 | 1.3559 | 0 | 1.3901 | 1.3559 | 11.4352 | 14.2449 | 10.0451
39050.4914 | 2240 | 0 | 39050.4914 | 2018 | 0 |  | 1738.5 | 1974.5 | 136.7521 | 0 | 123.199 | 0 | 1.3675 | 0 | 1.232 | 0 | 1.3675 | 1.232 | 13.2759 | 25.7374 | 11.9084
39050.4919 | 2225 | 0 | 39050.4919 | 2151 | 0 |  | 1780.5 | 2016.5 | 135.8364 | 0 | 131.3187 | 0 | 1.3584 | 0 | 1.3132 | 0 | 1.3584 | 1.3132 | 14.0396 | 17.9628 | 12.6812
39050.4923 | 2445 | 1 | 39050.4924 | 2265 | 2 |  | 1822.5 | 2058.5 | 149.2674 | 0.06105 | 138.2784 | 0.1221 | 1.4927 | 0.0006105 | 1.3828 | 0.001221 | 1.4921 | 1.3816 | 3.7925 | 12.3234 | 1002.5637
39050.4928 | 2397 | 6 | 39050.4928 | 2173 | 6 |  | 1864.5 | 2100.5 | 146.337 | 0.3663 | 132.6618 | 0.3663 | 1.4634 | 0.003663 | 1.3266 | 0.003663 | 1.4597 | 1.323 | 5.9559 | 17.6348 | 335.7509
39050.4933 | 2180 | 17 | 39050.4933 | 2416 | 18 |  | 1906.5 | 2142.5 | 133.0891 | 1.0379 | 147.4969 | 1.0989 | 1.3309 | 0.010379 | 1.475 | 0.010989 | 1.3205 | 1.464 | 19.4215 | 5.2652 | 100.1489

## Temperatures
DAQ Time | Burner Time | Bundle center | Air above bundle | Air below bundle | Intra-bundle | TRAY F
0 | -236 | 12 | 10.8 | 10.3 | 12 | 12.1
1 | -235 | 12 | 10.8 | 10.3 | 12 | 12.1
2 | -234 | 12 | 10.8 | 10.3 | 12 | 12.1
3 | -233 | 12 | 10.8 | 10.3 | 12 | 12.1
4 | -232 | 12 | 10.8 | 10.3 | 12 | 12.1
5 | -231 | 12 | 10.8 | 10.3 | 12 | 12.1
6 | -230 | 12 | 10.8 | 10.2 | 12 | 12.1
7 | -229 | 12 | 10.8 | 10.3 | 12 | 12.1
8 | -228 | 12 | 10.8 | 10.3 | 12 | 12.1
9 | -227 | 12 | 10.8 | 10.3 | 12 | 12.1
10 | -226 | 11.9 | 10.8 | 10.3 | 12 | 12.1
11 | -225 | 11.9 | 10.8 | 10.3 | 12 | 12.1
12 | -224 | 11.9 | 10.8 | 10.3 | 12 | 12.1
13 | -223 | 12 | 10.8 | 10.3 | 12 | 12.1
14 | -222 | 11.9 | 10.8 | 10.3 | 12 | 12.1
15 | -221 | 11.9 | 10.8 | 10.3 | 12 | 12.1
16 | -220 | 11.9 | 10.8 | 10.3 | 12 | 12.1
17 | -219 | 11.9 | 10.8 | 10.3 | 12 | 12.1
18 | -218 | 11.9 | 10.8 | 10.3 | 12 | 12.1
19 | -217 | 11.9 | 10.8 | 10.3 | 12 | 12.1
20 | -216 | 12 | 10.8 | 10.3 | 12 | 12.1
21 | -215 | 11.9 | 10.8 | 10.3 | 12 | 12.1
22 | -214 | 11.9 | 10.8 | 10.3 | 12 | 12.1
23 | -213 | 11.9 | 10.8 | 10.3 | 12 | 12.1
24 | -212 | 11.9 | 10.8 | 10.3 | 12 | 12.1
25 | -211 | 11.9 | 10.8 | 10.3 | 12 | 12.1
26 | -210 | 11.9 | 10.8 | 10.3 | 12 | 12.1
27 | -209 | 11.9 | 10.8 | 10.3 | 12 | 12.1
28 | -208 | 11.9 | 10.8 | 10.3 | 12 | 12.1
29 | -207 | 11.9 | 10.8 | 10.3 | 12 | 12.1
30 | -206 | 11.9 | 10.8 | 10.3 | 12 | 12.1
31 | -205 | 11.9 | 10.8 | 10.2 | 12 | 12.1
32 | -204 | 11.9 | 10.8 | 10.3 | 12 | 12.1
33 | -203 | 11.9 | 10.8 | 10.3 | 12 | 12.1
34 | -202 | 11.9 | 10.8 | 10.3 | 12 | 12.1
35 | -201 | 11.9 | 10.8 | 10.3 | 12 | 12.1
36 | -200 | 11.9 | 10.8 | 10.3 | 12 | 12.1
37 | -199 | 11.9 | 10.8 | 10.3 | 12 | 12.1
38 | -198 | 11.9 | 10.8 | 10.3 | 12 | 12.1
39 | -197 | 11.9 | 10.8 | 10.3 | 12 | 12.1
40 | -196 | 11.9 | 10.8 | 10.3 | 12 | 12.1
41 | -195 | 11.9 | 10.8 | 10.3 | 12 | 12.1
42 | -194 | 11.9 | 10.8 | 10.3 | 12 | 12.1
43 | -193 | 11.9 | 10.8 | 10.2 | 12 | 12.1
44 | -192 | 11.9 | 10.8 | 10.3 | 12 | 12.1
45 | -191 | 11.9 | 10.8 | 10.2 | 12 | 12.1
46 | -190 | 11.9 | 10.8 | 10.2 | 12 | 12.1
47 | -189 | 11.9 | 10.7 | 10.2 | 12 | 12.1
48 | -188 | 11.9 | 10.8 | 10.2 | 12 | 12.1
49 | -187 | 11.9 | 10.8 | 10.2 | 12 | 12.1
50 | -186 | 11.9 | 10.8 | 10.2 | 12 | 12.1
51 | -185 | 11.9 | 10.8 | 10.2 | 12 | 12.1
52 | -184 | 11.9 | 10.8 | 10.2 | 12 | 12.1
53 | -183 | 11.9 | 10.8 | 10.2 | 12 | 12.1
54 | -182 | 11.9 | 10.8 | 10.2 | 12 | 12.1
55 | -181 | 11.9 | 10.7 | 10.2 | 12 | 12.1
56 | -180 | 11.9 | 10.8 | 10.3 | 12 | 12.1
57 | -179 | 11.9 | 10.8 | 10.3 | 12 | 12.1
58 | -178 | 11.9 | 10.8 | 10.3 | 12 | 12.1
59 | -177 | 11.9 | 10.8 | 10.3 | 12 | 12.1
60 | -176 | 11.9 | 10.8 | 10.3 | 12 | 12.1
61 | -175 | 11.9 | 10.8 | 10.3 | 12 | 12.1
62 | -174 | 11.9 | 10.8 | 10.3 | 12 | 12.1
63 | -173 | 11.9 | 10.8 | 10.3 | 12 | 12.1
64 | -172 | 11.9 | 10.8 | 10.3 | 12 | 12.1
65 | -171 | 11.9 | 10.8 | 10.3 | 12 | 12.1
66 | -170 | 11.9 | 10.8 | 10.3 | 12 | 12.1
67 | -169 | 11.9 | 10.8 | 10.3 | 12 | 12.1
68 | -168 | 11.9 | 10.8 | 10.2 | 12 | 12.1
69 | -167 | 11.9 | 10.8 | 10.2 | 12 | 12.1
70 | -166 | 11.9 | 10.8 | 10.2 | 12 | 12.1
71 | -165 | 11.9 | 10.8 | 10.2 | 12 | 12.1
72 | -164 | 11.9 | 10.8 | 10.2 | 12 | 12.1
73 | -163 | 11.9 | 10.8 | 10.2 | 12 | 12.1
74 | -162 | 11.9 | 10.8 | 10.2 | 12 | 12.1
75 | -161 | 11.9 | 10.8 | 10.2 | 12 | 12.1
76 | -160 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1
77 | -159 | 11.9 | 10.8 | 10.2 | 12 | 12.1
78 | -158 | 11.9 | 10.8 | 10.2 | 12 | 12.1
79 | -157 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1
80 | -156 | 11.9 | 10.8 | 10.2 | 12 | 12.1
81 | -155 | 11.9 | 10.8 | 10.2 | 12 | 12.1
82 | -154 | 11.9 | 10.8 | 10.2 | 12 | 12.1
83 | -153 | 11.9 | 10.8 | 10.2 | 12 | 12.1
84 | -152 | 11.9 | 10.8 | 10.2 | 12 | 12.1
85 | -151 | 11.9 | 10.8 | 10.2 | 12 | 12.1
86 | -150 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1
87 | -149 | 11.9 | 10.8 | 10.2 | 12 | 12.1
88 | -148 | 11.9 | 10.8 | 10.2 | 12 | 12.1
89 | -147 | 11.9 | 10.8 | 10.2 | 12 | 12.1
90 | -146 | 11.9 | 10.8 | 10.2 | 12 | 12.1
91 | -145 | 11.9 | 10.8 | 10.2 | 12 | 12.1
92 | -144 | 11.9 | 10.8 | 10.2 | 12 | 12.1
93 | -143 | 11.9 | 10.8 | 10.2 | 12 | 12.1
94 | -142 | 11.9 | 10.8 | 10.2 | 12 | 12.1
95 | -141 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1
96 | -140 | 11.9 | 10.8 | 10.2 | 12 | 12.1
97 | -139 | 11.9 | 10.8 | 10.2 | 12 | 12.1
98 | -138 | 11.9 | 10.8 | 10.2 | 12 | 12.1
99 | -137 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1
100 | -136 | 11.9 | 10.8 | 10.2 | 12 | 12.1
101 | -135 | 11.9 | 10.8 | 10.2 | 12 | 12.1
102 | -134 | 11.9 | 10.8 | 10.2 | 12 | 12.1
103 | -133 | 11.9 | 10.8 | 10.2 | 12 | 12.1
104 | -132 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1
105 | -131 | 11.9 | 10.8 | 10.2 | 12 | 12.1
106 | -130 | 11.9 | 10.8 | 10.2 | 12 | 12.1
107 | -129 | 11.9 | 10.8 | 10.2 | 12 | 12.1
108 | -128 | 11.9 | 10.8 | 10.2 | 12 | 12.1
109 | -127 | 11.9 | 10.8 | 10.3 | 12 | 12.1
110 | -126 | 11.9 | 10.8 | 10.3 | 12 | 12.1
111 | -125 | 11.9 | 10.8 | 10.2 | 12 | 12.1
112 | -124 | 11.9 | 10.8 | 10.2 | 12 | 12.1
113 | -123 | 11.9 | 10.8 | 10.3 | 12 | 12.1
114 | -122 | 11.9 | 10.8 | 10.3 | 12 | 12.1
115 | -121 | 11.9 | 10.8 | 10.3 | 12 | 12.1
116 | -120 | 11.9 | 10.8 | 10.2 | 12 | 12.1
117 | -119 | 11.9 | 10.8 | 10.3 | 12 | 12.1
118 | -118 | 11.9 | 10.8 | 10.2 | 12 | 12.1
119 | -117 | 11.9 | 10.8 | 10.2 | 12 | 12.1
120 | -116 | 11.9 | 10.8 | 10.2 | 12 | 12.1
121 | -115 | 11.9 | 10.8 | 10.2 | 12 | 12.1
122 | -114 | 11.9 | 10.8 | 10.2 | 12 | 12.1
123 | -113 | 11.9 | 10.8 | 10.2 | 12 | 12.1
124 | -112 | 11.9 | 10.8 | 10.3 | 12 | 12.1
125 | -111 | 11.9 | 10.8 | 10.2 | 12 | 12.1
126 | -110 | 11.9 | 10.9 | 10.2 | 12 | 12.1
127 | -109 | 11.9 | 10.8 | 10.2 | 12 | 12.1
128 | -108 | 11.9 | 10.9 | 10.3 | 12 | 12.1
129 | -107 | 11.9 | 10.9 | 10.3 | 12 | 12.1
130 | -106 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1
131 | -105 | 11.9 | 10.8 | 10.2 | 12 | 12.1
132 | -104 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1
133 | -103 | 11.9 | 10.8 | 10.2 | 12 | 12.1
134 | -102 | 11.9 | 10.8 | 10.3 | 11.9 | 12.1
135 | -101 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1
136 | -100 | 11.9 | 10.9 | 10.2 | 12 | 12.1
137 | -99 | 11.9 | 10.9 | 10.2 | 12 | 12.1
138 | -98 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1
139 | -97 | 11.9 | 10.8 | 10.2 | 12 | 12.1
140 | -96 | 11.9 | 10.8 | 10.2 | 12 | 12.1
141 | -95 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1
142 | -94 | 11.9 | 10.8 | 10.2 | 12 | 12.1
143 | -93 | 11.9 | 10.9 | 10.2 | 12 | 12.1
144 | -92 | 11.9 | 10.9 | 10.2 | 12 | 12.1
145 | -91 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1
146 | -90 | 11.9 | 10.9 | 10.2 | 12 | 12.1
147 | -89 | 11.9 | 10.9 | 10.2 | 11.9 | 12.1
148 | -88 | 11.9 | 10.8 | 10.2 | 12 | 12.1
149 | -87 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1
150 | -86 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1
151 | -85 | 11.9 | 10.8 | 10.1 | 11.9 | 12.1
152 | -84 | 11.9 | 10.8 | 10.2 | 12 | 12.1
153 | -83 | 11.9 | 10.9 | 10.2 | 12 | 12.1
154 | -82 | 11.9 | 10.8 | 10.2 | 12 | 12.1
155 | -81 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1
156 | -80 | 11.9 | 10.8 | 10.2 | 12 | 12.1
157 | -79 | 11.9 | 10.8 | 10.2 | 12 | 12.1
158 | -78 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1
159 | -77 | 11.9 | 10.8 | 10.2 | 12 | 12.1
160 | -76 | 11.9 | 10.9 | 10.2 | 12 | 12.1
161 | -75 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1
162 | -74 | 11.9 | 10.9 | 10.2 | 12 | 12.1
163 | -73 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1
164 | -72 | 11.9 | 10.9 | 10.2 | 12 | 12.1
165 | -71 | 11.9 | 10.9 | 10.2 | 12 | 12.1
166 | -70 | 11.9 | 10.9 | 10.2 | 12 | 12.1
167 | -69 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1
168 | -68 | 11.9 | 10.8 | 10.2 | 12 | 12.1
169 | -67 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1
170 | -66 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1
171 | -65 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1
172 | -64 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1
173 | -63 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1
174 | -62 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1
175 | -61 | 11.9 | 10.8 | 10.1 | 11.9 | 12.1
176 | -60 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1
177 | -59 | 11.9 | 10.8 | 10.2 | 12 | 12.1
178 | -58 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1
179 | -57 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1
180 | -56 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1
181 | -55 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1
182 | -54 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1
183 | -53 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1
184 | -52 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1
185 | -51 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1
186 | -50 | 11.9 | 10.7 | 10.2 | 11.9 | 12.1
187 | -49 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1
188 | -48 | 11.9 | 10.8 | 10.1 | 11.9 | 12.1
189 | -47 | 11.9 | 10.8 | 10.1 | 11.9 | 12.1
190 | -46 | 11.9 | 10.8 | 10.1 | 11.9 | 12.1
191 | -45 | 11.9 | 10.8 | 10.1 | 11.9 | 12.1
192 | -44 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1
193 | -43 | 11.9 | 10.7 | 10.1 | 11.9 | 12.1
194 | -42 | 11.9 | 10.8 | 10.1 | 12 | 12.1
195 | -41 | 11.9 | 10.7 | 10.1 | 11.9 | 12.1
196 | -40 | 11.9 | 10.7 | 10.1 | 11.9 | 12.1
197 | -39 | 11.9 | 10.7 | 10.1 | 11.9 | 12.1
198 | -38 | 11.9 | 10.7 | 10.2 | 11.9 | 12.1
199 | -37 | 11.9 | 10.7 | 10.2 | 11.9 | 12.1
200 | -36 | 11.9 | 10.7 | 10.2 | 11.9 | 12.1
201 | -35 | 11.9 | 10.7 | 10.2 | 11.9 | 12.1
202 | -34 | 11.9 | 10.7 | 10.2 | 11.9 | 12.1
203 | -33 | 11.9 | 10.7 | 10.2 | 11.9 | 12.1
204 | -32 | 11.9 | 10.7 | 10.2 | 11.9 | 12.1
205 | -31 | 11.9 | 10.7 | 10.2 | 11.9 | 12.1
206 | -30 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1
207 | -29 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1
208 | -28 | 11.9 | 10.7 | 10.2 | 11.9 | 12.1
209 | -27 | 11.9 | 10.7 | 10.2 | 11.9 | 12.1
210 | -26 | 11.9 | 10.7 | 10.2 | 11.9 | 12.1
211 | -25 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1
212 | -24 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1
213 | -23 | 11.9 | 10.7 | 10.2 | 11.9 | 12.1
214 | -22 | 11.9 | 10.8 | 10.3 | 11.9 | 12.1
215 | -21 | 11.9 | 10.7 | 10.3 | 11.9 | 12.1
216 | -20 | 11.9 | 10.8 | 10.3 | 11.9 | 12.1
217 | -19 | 11.9 | 10.8 | 10.3 | 11.9 | 12.1
218 | -18 | 11.9 | 10.8 | 10.3 | 11.9 | 12.1
219 | -17 | 11.9 | 10.8 | 10.3 | 11.9 | 12.1
220 | -16 | 11.9 | 10.8 | 10.3 | 11.9 | 12.1
221 | -15 | 11.9 | 10.7 | 10.3 | 11.9 | 12.1
222 | -14 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1
223 | -13 | 11.9 | 10.8 | 10.3 | 11.9 | 12.1
224 | -12 | 11.9 | 10.8 | 10.3 | 11.9 | 12.1
225 | -11 | 11.9 | 10.8 | 10.3 | 11.9 | 12.1
226 | -10 | 11.9 | 10.7 | 10.2 | 11.9 | 12.1
227 | -9 | 11.9 | 10.8 | 10.3 | 11.9 | 12.1
228 | -8 | 11.9 | 10.7 | 10.2 | 11.9 | 12.1
229 | -7 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1
230 | -6 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1
231 | -5 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1
232 | -4 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1
233 | -3 | 11.9 | 10.8 | 10.3 | 11.9 | 12.1
234 | -2 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1
235 | -1 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1
236 | 0 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1
237 | 1 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1
238 | 2 | 11.9 | 10.8 | 10.3 | 11.9 | 12.1
239 | 3 | 11.9 | 10.8 | 10.3 | 11.9 | 12.1
240 | 4 | 11.9 | 10.8 | 10.2 | 11.9 | 12.1
241 | 5 | 11.9 | 10.8 | 10.8 | 11.9 | 12.3
242 | 6 | 11.9 | 13.2 | 17 | 11.9 | 14.8
243 | 7 | 11.9 | 18.2 | 23.4 | 12 | 19
244 | 8 | 11.9 | 24.3 | 30.8 | 12 | 21.9
245 | 9 | 11.9 | 31.3 | 41.4 | 12.1 | 24.4
246 | 10 | 11.9 | 40.7 | 54.9 | 12.2 | 28.9
247 | 11 | 11.9 | 47.5 | 63.7 | 12.3 | 32.3
248 | 12 | 12 | 60.4 | 79.7 | 12.4 | 36.3
249 | 13 | 12.1 | 68.6 | 88.2 | 12.5 | 38.2
250 | 14 | 12.1 | 80.4 | 104.8 | 12.6 | 40.8
251 | 15 | 12.3 | 92.1 | 120.4 | 12.8 | 45.5
252 | 16 | 12.4 | 102.6 | 133.8 | 12.9 | 52.4
253 | 17 | 12.6 | 112.3 | 142.7 | 12.9 | 57.2
254 | 18 | 12.9 | 120.8 | 153.9 | 13 | 60.9
255 | 19 | 13.1 | 127.6 | 160.6 | 13 | 65.7
256 | 20 | 13.4 | 132.8 | 165.5 | 13 | 69
257 | 21 | 13.6 | 139.6 | 172.6 | 13.1 | 72.1
258 | 22 | 13.9 | 143.5 | 176.1 | 13.1 | 72.3
259 | 23 | 14.2 | 147.8 | 181.9 | 13.1 | 73.1
260 | 24 | 14.4 | 153.6 | 189.4 | 13.2 | 77.8
261 | 25 | 14.7 | 159 | 196.6 | 13.2 | 81.1
262 | 26 | 14.9 | 164.7 | 204.8 | 13.3 | 83.4
263 | 27 | 15.2 | 173 | 213.7 | 13.4 | 86.3
264 | 28 | 15.4 | 179.9 | 220.6 | 13.5 | 88.7
265 | 29 | 15.7 | 186.6 | 229.6 | 13.6 | 91
266 | 30 | 15.9 | 192.5 | 237.7 | 13.8 | 92.2
267 | 31 | 16.2 | 198.2 | 246.5 | 13.9 | 95
268 | 32 | 16.5 | 202.8 | 250.2 | 14 | 98.4
269 | 33 | 16.8 | 207.6 | 253.7 | 14.1 | 102.1
270 | 34 | 17.1 | 211.2 | 256.5 | 14.2 | 105.4
271 | 35 | 17.4 | 214.7 | 258.3 | 14.3 | 107.2
272 | 36 | 17.7 | 219.3 | 262.1 | 14.5 | 108.5
273 | 37 | 18 | 223 | 264.5 | 14.5 | 109.4
274 | 38 | 18.3 | 225.8 | 266.9 | 14.7 | 111.1
275 | 39 | 18.6 | 229.9 | 270.2 | 14.8 | 112.7
276 | 40 | 19 | 233.9 | 274.5 | 14.9 | 115.6
277 | 41 | 19.3 | 237.3 | 276.8 | 15 | 118.2
278 | 42 | 19.6 | 240.2 | 279.6 | 15.1 | 120.4
279 | 43 | 19.9 | 244.2 | 285.3 | 15.3 | 123.1
280 | 44 | 20.2 | 248.1 | 289.2 | 15.5 | 124.5
281 | 45 | 20.5 | 252.2 | 293.3 | 15.7 | 126.2
282 | 46 | 20.8 | 256.3 | 299.6 | 15.9 | 128.7
283 | 47 | 21.2 | 260 | 301.4 | 16 | 131.7
284 | 48 | 21.5 | 260.2 | 302.5 | 16.1 | 132.5
285 | 49 | 21.8 | 262.8 | 306.8 | 16.2 | 135.3
286 | 50 | 22.2 | 266.4 | 308.4 | 16.3 | 137.9
287 | 51 | 22.5 | 267.5 | 309.3 | 16.5 | 138.4
288 | 52 | 22.9 | 272.1 | 313.3 | 16.7 | 140.7
289 | 53 | 23.2 | 273.3 | 313.3 | 16.8 | 142.1
290 | 54 | 23.6 | 275.2 | 317.4 | 17 | 145.2
291 | 55 | 23.9 | 278.4 | 322.7 | 17.4 | 148.7
292 | 56 | 24.3 | 281.1 | 329 | 17.8 | 153.1
293 | 57 | 24.6 | 285.1 | 333.9 | 18.4 | 157.8
294 | 58 | 24.9 | 286.6 | 335.1 | 19 | 159.1
295 | 59 | 25.3 | 288.4 | 338.1 | 19.5 | 160.7
296 | 60 | 25.7 | 289.9 | 338 | 19.9 | 161.7
297 | 61 | 26.1 | 291.5 | 338.4 | 20.4 | 162.9
298 | 62 | 26.5 | 291.6 | 339.1 | 20.9 | 163.5
299 | 63 | 26.9 | 292.7 | 337.9 | 21 | 164
300 | 64 | 27.4 | 293.4 | 335.3 | 21.4 | 163.8
301 | 65 | 27.9 | 295.3 | 338.3 | 22.1 | 165.1
302 | 66 | 28.3 | 296.6 | 338.1 | 22.5 | 166.4
303 | 67 | 28.8 | 295 | 334.3 | 22.6 | 165.9
304 | 68 | 29.3 | 294.4 | 332 | 22.8 | 166.3
305 | 69 | 29.8 | 293.1 | 329.3 | 23.1 | 166.6
306 | 70 | 30.3 | 292.2 | 330 | 23.4 | 169
307 | 71 | 30.8 | 292.1 | 330.9 | 23.7 | 173.7
308 | 72 | 31.3 | 292.6 | 332.6 | 24 | 175.2
309 | 73 | 31.8 | 295.7 | 337.1 | 24.4 | 177.2
310 | 74 | 32.3 | 295.8 | 342.3 | 24.7 | 178.8
311 | 75 | 32.8 | 297.7 | 349.1 | 25.1 | 180.7
312 | 76 | 33.3 | 298.3 | 346.7 | 25.4 | 181.7
313 | 77 | 33.8 | 297.7 | 346.4 | 25.6 | 182
314 | 78 | 34.4 | 297.1 | 348.1 | 26.1 | 182.9
315 | 79 | 34.9 | 297.9 | 348.7 | 26.9 | 184.1
316 | 80 | 35.5 | 299 | 348.9 | 27.4 | 185.9
317 | 81 | 36 | 299.1 | 346.5 | 27.6 | 187.4
318 | 82 | 36.6 | 299.5 | 346.9 | 27.8 | 189
319 | 83 | 37.1 | 300.7 | 351.4 | 28.5 | 192.6
320 | 84 | 37.7 | 300.9 | 352 | 29 | 194.3
321 | 85 | 38.2 | 301.5 | 353.2 | 29.2 | 195.6
322 | 86 | 38.8 | 302.3 | 352.3 | 29.5 | 197.6
323 | 87 | 39.4 | 302.7 | 353.5 | 29.8 | 199
324 | 88 | 40 | 307.1 | 365.1 | 30.7 | 203.5
325 | 89 | 40.5 | 310.7 | 370 | 31.6 | 206.4
326 | 90 | 41.1 | 316.1 | 379.1 | 32.2 | 210.4
327 | 91 | 41.7 | 319.8 | 381.8 | 32.5 | 214.2
328 | 92 | 42.3 | 321.3 | 384.5 | 32.6 | 216.6
329 | 93 | 42.9 | 322.5 | 384.5 | 33.1 | 218.1
330 | 94 | 43.5 | 322.2 | 386.4 | 33.8 | 217.6
331 | 95 | 44.2 | 322.1 | 383 | 34.6 | 218.3
332 | 96 | 44.8 | 321.1 | 378.7 | 34.8 | 217.2
333 | 97 | 45.4 | 321.2 | 377.7 | 35.1 | 217.4
334 | 98 | 46.1 | 321.9 | 377.9 | 35.6 | 218.3
335 | 99 | 46.7 | 321.7 | 375.9 | 36.1 | 219.4
336 | 100 | 47.3 | 324 | 380.2 | 36.9 | 223.5
337 | 101 | 48 | 324.9 | 379.8 | 37.1 | 226
338 | 102 | 48.6 | 324 | 377 | 37.4 | 225.3
339 | 103 | 49.2 | 324.4 | 377.4 | 37.6 | 226
340 | 104 | 49.8 | 325.3 | 374.7 | 38.2 | 227.3
341 | 105 | 50.4 | 324.9 | 373.9 | 38.7 | 228
342 | 106 | 51 | 325.7 | 373.8 | 39.2 | 229.2
343 | 107 | 51.6 | 327.3 | 371.6 | 39.6 | 229.4
344 | 108 | 52.2 | 326.4 | 372.1 | 39.8 | 229.3
345 | 109 | 52.8 | 326.2 | 373.4 | 40.3 | 229.9
346 | 110 | 53.4 | 326.3 | 372.6 | 40.8 | 230.6
347 | 111 | 54 | 325.8 | 373.1 | 41 | 231.7
348 | 112 | 54.5 | 325.1 | 372.5 | 41.3 | 233.2
349 | 113 | 55.1 | 326.1 | 377.5 | 42.2 | 236.3
350 | 114 | 55.7 | 327.4 | 378.5 | 42.5 | 237.6
351 | 115 | 56.2 | 328.1 | 379.8 | 43 | 238.9
352 | 116 | 56.7 | 328.3 | 378.5 | 43.3 | 239.8
353 | 117 | 57.3 | 328.5 | 383 | 43.5 | 241.7
354 | 118 | 57.8 | 331.5 | 389.4 | 44.5 | 244.8
355 | 119 | 58.4 | 330.6 | 388.1 | 44.7 | 244.9
356 | 120 | 58.9 | 330.4 | 386.5 | 45.2 | 244.5
357 | 121 | 59.4 | 331.3 | 388.5 | 45.6 | 245.9
358 | 122 | 59.9 | 331.2 | 385.4 | 46 | 246.3
359 | 123 | 60.4 | 329.8 | 380.7 | 46.1 | 245.9
360 | 124 | 60.9 | 331.2 | 386.9 | 46.4 | 248
361 | 125 | 61.4 | 334 | 394.5 | 47 | 251
362 | 126 | 61.8 | 336 | 398.6 | 47.5 | 254.3
363 | 127 | 62.3 | 338 | 406.5 | 47.7 | 259.4
364 | 128 | 62.7 | 339.6 | 412.4 | 48.2 | 264.6
365 | 129 | 63.2 | 341 | 413.6 | 48.6 | 266.9
366 | 130 | 63.6 | 341.7 | 411.5 | 49 | 270.1
367 | 131 | 64.1 | 344.1 | 409.7 | 49.4 | 273.9
368 | 132 | 64.5 | 344.9 | 408.7 | 49.8 | 275.9
369 | 133 | 64.9 | 345.3 | 408.5 | 50.4 | 275.5
370 | 134 | 65.3 | 345.6 | 406.2 | 50.6 | 276.3
371 | 135 | 65.8 | 345.1 | 405.6 | 50.9 | 276.6
372 | 136 | 66.2 | 345.5 | 409.5 | 51.4 | 277.7
373 | 137 | 66.7 | 346.7 | 416.9 | 52 | 278.5
374 | 138 | 67.1 | 348.1 | 426.6 | 52.5 | 281.1
375 | 139 | 67.5 | 349.9 | 425.8 | 53 | 281.1
376 | 140 | 68 | 349.9 | 423.5 | 53.4 | 281.1
377 | 141 | 68.4 | 349.9 | 422 | 53.7 | 280.7
378 | 142 | 68.9 | 349.3 | 420.4 | 53.9 | 280.7
379 | 143 | 69.3 | 350.8 | 425.4 | 54.2 | 283
380 | 144 | 69.8 | 352.4 | 426.3 | 54.7 | 285.6
381 | 145 | 70.3 | 353.7 | 425.3 | 55.1 | 287.7
382 | 146 | 70.7 | 354.7 | 431.2 | 55.5 | 288.9
383 | 147 | 71.2 | 358.4 | 436.4 | 56.3 | 291.9
384 | 148 | 71.7 | 361 | 439.1 | 56.8 | 294.1
385 | 149 | 72.2 | 363.8 | 447.1 | 57.4 | 296.9
386 | 150 | 72.7 | 365.6 | 449.3 | 57.8 | 299.3
387 | 151 | 73.1 | 364.7 | 447.7 | 57.8 | 298.8
388 | 152 | 73.6 | 365.1 | 446.7 | 58 | 299.7
389 | 153 | 74.1 | 365.9 | 442.4 | 58.2 | 299.3
390 | 154 | 74.6 | 365.2 | 444.5 | 58.5 | 299.3
391 | 155 | 75.1 | 366.4 | 448.9 | 58.9 | 299.3
392 | 156 | 75.6 | 367 | 447.8 | 59.2 | 299.8
393 | 157 | 76.2 | 368.3 | 448.2 | 59.7 | 302
394 | 158 | 76.7 | 369.4 | 449.4 | 60.1 | 303
395 | 159 | 77.3 | 370.8 | 451.1 | 60.7 | 304.7
396 | 160 | 77.8 | 372.2 | 456.1 | 61.2 | 306
397 | 161 | 78.4 | 374.6 | 462.7 | 61.7 | 309.3
398 | 162 | 79 | 378.8 | 471.8 | 62.5 | 313.7
399 | 163 | 79.6 | 383.3 | 485.5 | 63.2 | 319
400 | 164 | 80.2 | 387.1 | 492.6 | 63.7 | 325.3
401 | 165 | 80.7 | 387.2 | 486 | 63.7 | 322.9
402 | 166 | 81.3 | 385 | 479.8 | 63.6 | 320.9
403 | 167 | 81.9 | 385.3 | 480.3 | 63.9 | 321.8
404 | 168 | 82.5 | 386.3 | 477.3 | 64.3 | 322.4
405 | 169 | 83.1 | 386.9 | 471.3 | 64.8 | 322.4
406 | 170 | 83.7 | 386.2 | 468.8 | 64.8 | 322
407 | 171 | 84.3 | 384.8 | 469 | 65.1 | 321.1
408 | 172 | 84.9 | 386.6 | 473.6 | 65.8 | 324.7
409 | 173 | 85.6 | 388.2 | 478.9 | 66.3 | 329.3
410 | 174 | 86.2 | 388.9 | 482.8 | 66.7 | 333.3
411 | 175 | 86.9 | 392.7 | 492.2 | 67.2 | 336.5
412 | 176 | 87.5 | 397 | 497.6 | 67.9 | 339.2
413 | 177 | 88.2 | 398.6 | 504.6 | 68.6 | 341.9
414 | 178 | 88.8 | 397.4 | 500.3 | 69.2 | 341.3
415 | 179 | 89.5 | 395.9 | 495.4 | 69.6 | 339.3
416 | 180 | 90.1 | 396.7 | 497.3 | 70.3 | 340.8
417 | 181 | 90.8 | 398.3 | 498.2 | 71.3 | 344.4
418 | 182 | 91.5 | 400.7 | 498.8 | 72 | 346.9
419 | 183 | 92.2 | 403.1 | 505 | 73 | 348.9
420 | 184 | 92.8 | 407.3 | 514.7 | 73.8 | 352.6
421 | 185 | 93.5 | 409.7 | 515.9 | 74.7 | 355.4
422 | 186 | 94.2 | 409.9 | 518.4 | 75.4 | 355.7
423 | 187 | 94.9 | 410.9 | 522.1 | 76.2 | 357.9
424 | 188 | 95.6 | 411.9 | 522.3 | 77.3 | 360.1
425 | 189 | 96.4 | 411 | 518.6 | 77.7 | 359.9
426 | 190 | 97.1 | 412.2 | 521.4 | 78.7 | 361.3
427 | 191 | 97.8 | 414.2 | 521.7 | 79.6 | 364.4
428 | 192 | 98.6 | 413.6 | 522 | 80.6 | 365.5
429 | 193 | 99.3 | 412.7 | 520.9 | 81.2 | 366.7
430 | 194 | 100.1 | 411 | 512.7 | 81.6 | 365.4
431 | 195 | 100.9 | 410.5 | 511.6 | 82.4 | 367.7
432 | 196 | 101.7 | 411.7 | 514.3 | 83.1 | 371.1
433 | 197 | 102.6 | 414.3 | 517.2 | 83.8 | 373.7
434 | 198 | 103.4 | 415 | 514.2 | 84.9 | 374.5
435 | 199 | 104.3 | 414.5 | 510.4 | 85.4 | 372.8
436 | 200 | 105.1 | 414.2 | 507.5 | 85.9 | 372.8
437 | 201 | 106 | 413.8 | 503.8 | 86.6 | 373.8
438 | 202 | 106.8 | 413.3 | 499.7 | 87.9 | 374.1
439 | 203 | 107.7 | 412.8 | 498.9 | 88.3 | 374.2
440 | 204 | 108.6 | 412.2 | 496.7 | 88.8 | 375
441 | 205 | 109.4 | 412.4 | 494.4 | 89.4 | 376.5
442 | 206 | 110.3 | 411.1 | 488.3 | 89.9 | 377.8
443 | 207 | 111.2 | 412.7 | 494.6 | 90.3 | 378.2
444 | 208 | 112.1 | 413 | 491.2 | 91 | 377.9
445 | 209 | 113 | 412.5 | 491.5 | 91.5 | 378.2
446 | 210 | 113.8 | 414.2 | 493.6 | 92.1 | 381.5
447 | 211 | 114.7 | 416.9 | 498.9 | 92.9 | 388.2
448 | 212 | 115.6 | 418.1 | 498.3 | 93.6 | 390.5
449 | 213 | 116.4 | 419.6 | 499.7 | 94.5 | 391.3
450 | 214 | 117.3 | 419.3 | 497.5 | 95.4 | 392.2
451 | 215 | 118.1 | 418.4 | 495.3 | 96.3 | 391.4
452 | 216 | 119 | 417.3 | 489.6 | 97 | 391.2
453 | 217 | 119.8 | 416.5 | 487 | 97.6 | 391.3
454 | 218 | 120.7 | 416.8 | 484.2 | 98.1 | 389.9
455 | 219 | 121.5 | 416.9 | 486.4 | 98.4 | 389.4
456 | 220 | 122.4 | 418.8 | 493.2 | 99.4 | 392.7
457 | 221 | 123.3 | 421.4 | 498.8 | 100.1 | 394.4
458 | 222 | 124.1 | 422.3 | 497 | 100.7 | 394.9
459 | 223 | 125 | 422.5 | 492.8 | 100.9 | 394.9
460 | 224 | 125.8 | 423.2 | 490.4 | 101.4 | 395.5
461 | 225 | 126.7 | 422.6 | 488.4 | 102.1 | 395.9
462 | 226 | 127.6 | 421.2 | 484.1 | 102.6 | 395.9
463 | 227 | 128.4 | 420.7 | 480.2 | 103.1 | 394.9
464 | 228 | 129.3 | 419.2 | 478.2 | 103.5 | 393.6
465 | 229 | 130.2 | 419.2 | 483.2 | 104 | 394.8
466 | 230 | 131 | 420.9 | 487.6 | 104.6 | 396.9
467 | 231 | 131.9 | 419.4 | 482 | 105 | 395.6
468 | 232 | 132.7 | 417.5 | 483.1 | 105.3 | 394.6
469 | 233 | 133.5 | 417.6 | 486.8 | 105.8 | 395.6
470 | 234 | 134.3 | 417.3 | 482.2 | 106.5 | 396
471 | 235 | 135.2 | 414.7 | 474.7 | 107 | 395.4
472 | 236 | 136 | 413.4 | 471.4 | 107.7 | 396.4
473 | 237 | 136.8 | 412.5 | 467.5 | 108.2 | 396.5
474 | 238 | 137.6 | 411.8 | 466 | 108.9 | 396.4
475 | 239 | 138.4 | 413.3 | 472 | 110.1 | 401.5
476 | 240 | 139.2 | 415.1 | 474 | 110.5 | 403.8
477 | 241 | 140.1 | 413.5 | 469.6 | 111 | 401.6
478 | 242 | 141.1 | 413 | 469 | 111.4 | 400.5
479 | 243 | 141.9 | 413.3 | 473.5 | 111.8 | 400.8
480 | 244 | 142.8 | 413.2 | 471 | 112.1 | 400.1
481 | 245 | 143.6 | 413.4 | 469.2 | 112.5 | 399.3
482 | 246 | 144.3 | 413.2 | 470.9 | 112.9 | 400.2
483 | 247 | 145.1 | 413 | 470.4 | 113.4 | 400.8
484 | 248 | 145.8 | 414.7 | 478.2 | 114 | 404.6
485 | 249 | 146.6 | 416.9 | 481.3 | 115.1 | 408.3
486 | 250 | 147.3 | 417.9 | 482.4 | 115.4 | 410.5
487 | 251 | 148.1 | 418.6 | 486.6 | 116 | 413.5
488 | 252 | 149 | 421.2 | 498.8 | 116.7 | 417.6
489 | 253 | 149.8 | 423.3 | 504.7 | 117.2 | 418.7
490 | 254 | 150.6 | 424 | 509.3 | 117.6 | 418.9
491 | 255 | 151.4 | 424.2 | 508.3 | 118.2 | 418.3
492 | 256 | 152.2 | 427 | 509.7 | 118.6 | 420.6
493 | 257 | 153 | 427.4 | 509.4 | 119.3 | 421.5
494 | 258 | 153.7 | 427.7 | 508.4 | 120.1 | 422.6
495 | 259 | 154.4 | 428.1 | 507.4 | 121.1 | 424.5
496 | 260 | 155.2 | 427.6 | 504.2 | 121.8 | 425.7
497 | 261 | 155.9 | 427.4 | 502.9 | 122.7 | 425.6
498 | 262 | 156.6 | 428.1 | 502.2 | 123.3 | 425.9
499 | 263 | 157.3 | 430.1 | 510.9 | 123.8 | 427.3
500 | 264 | 158 | 431.3 | 517 | 124.6 | 427.8
501 | 265 | 158.7 | 432.7 | 517.5 | 125.1 | 428.4
502 | 266 | 159.4 | 435 | 518 | 125.8 | 429.5
503 | 267 | 160.1 | 436 | 515.3 | 126.4 | 430.7
504 | 268 | 160.9 | 435.5 | 515.7 | 127 | 431.5
505 | 269 | 161.6 | 436.2 | 518.8 | 127.6 | 434.1
506 | 270 | 162.3 | 437.1 | 520.8 | 128.5 | 435.8
507 | 271 | 163 | 436.6 | 517 | 129.3 | 434.8
508 | 272 | 163.7 | 435.8 | 518.1 | 129.8 | 433.8
509 | 273 | 164.5 | 436.6 | 523.6 | 130.4 | 436
510 | 274 | 165.2 | 436.9 | 522.7 | 131.3 | 439.3
511 | 275 | 166 | 437 | 522.8 | 132 | 442.7
512 | 276 | 166.7 | 437.9 | 520.7 | 132.7 | 442.5
513 | 277 | 167.5 | 438.6 | 519.2 | 133.3 | 442.6
514 | 278 | 168.2 | 439.4 | 524 | 134.1 | 443.5
515 | 279 | 169 | 441.4 | 537.9 | 134.8 | 447.7
516 | 280 | 169.8 | 442.3 | 542.6 | 135.4 | 447.6
517 | 281 | 170.6 | 444.1 | 547.7 | 136 | 450.5
518 | 282 | 171.3 | 445.1 | 546.1 | 136.9 | 451.2
519 | 283 | 172.1 | 445.3 | 541.3 | 137.6 | 452.1
520 | 284 | 172.9 | 445.7 | 538.3 | 138.3 | 453.7
521 | 285 | 173.7 | 445.9 | 535.1 | 139.2 | 456.8
522 | 286 | 174.5 | 445.6 | 533.5 | 139.5 | 457
523 | 287 | 175.3 | 445.7 | 540 | 140 | 458.3
524 | 288 | 176.2 | 447.5 | 542.5 | 140.7 | 460.3
525 | 289 | 177 | 447.7 | 541.4 | 141.3 | 461
526 | 290 | 177.9 | 451.3 | 545.7 | 142 | 463.7
527 | 291 | 178.7 | 453.7 | 543 | 142.6 | 465.3
528 | 292 | 179.6 | 453.4 | 539.1 | 143.1 | 464.3
529 | 293 | 180.5 | 454.1 | 541.7 | 143.5 | 464.4
530 | 294 | 181.4 | 455.3 | 554.1 | 143.8 | 466.4
531 | 295 | 182.3 | 460.6 | 573.1 | 144.6 | 473.2
532 | 296 | 183.2 | 464.8 | 594.2 | 145.3 | 478.8
533 | 297 | 184 | 470.5 | 608.5 | 146.2 | 483.4
534 | 298 | 184.9 | 473.1 | 621.4 | 147.1 | 484.3
535 | 299 | 185.7 | 476.8 | 637.3 | 148.1 | 488.6
536 | 300 | 186.5 | 481.4 | 646.1 | 149 | 491.3
537 | 301 | 187.4 | 485.7 | 654.8 | 150 | 493.8
538 | 302 | 188.2 | 491.6 | 664.9 | 151.1 | 496.1
539 | 303 | 189.1 | 494.2 | 665 | 151.9 | 494.6
540 | 304 | 190 | 494 | 667.6 | 152.8 | 493.7
541 | 305 | 190.9 | 495.6 | 670.9 | 153.7 | 496.1
542 | 306 | 191.9 | 497.8 | 671.4 | 154.4 | 501.2
543 | 307 | 192.9 | 498.9 | 671.2 | 155.2 | 503.6
544 | 308 | 193.8 | 502.3 | 673.6 | 156 | 504.5
545 | 309 | 194.8 | 504.1 | 681.5 | 156.9 | 505.2
546 | 310 | 195.9 | 507.1 | 688.8 | 158.3 | 509.3
547 | 311 | 196.9 | 509.1 | 687.1 | 159.3 | 510.5
548 | 312 | 197.9 | 510.9 | 689.8 | 160.1 | 511.6
549 | 313 | 198.9 | 514.2 | 692.1 | 161.3 | 512
550 | 314 | 199.9 | 516.1 | 697.8 | 162.3 | 516
551 | 315 | 200.9 | 518.3 | 699.5 | 163.3 | 517.9
552 | 316 | 201.9 | 521.3 | 703.1 | 164.4 | 517
553 | 317 | 202.9 | 522.3 | 705.4 | 165.6 | 517.8
554 | 318 | 203.9 | 525 | 701.6 | 166.7 | 519.9
555 | 319 | 204.9 | 524.1 | 692.4 | 167.6 | 518.1
556 | 320 | 205.9 | 528.3 | 694.9 | 168.4 | 521.6
557 | 321 | 206.9 | 531.4 | 698.7 | 169.4 | 525.2
558 | 322 | 207.9 | 532.8 | 713.2 | 170.4 | 532.8
559 | 323 | 209 | 535.6 | 714.9 | 171.5 | 535.8
560 | 324 | 210 | 536.7 | 713.3 | 172.1 | 534.2
561 | 325 | 211.1 | 534 | 717.3 | 172.5 | 537.2
562 | 326 | 212.3 | 532.9 | 707.7 | 172.9 | 538.3
563 | 327 | 213.4 | 533.1 | 707.2 | 173.4 | 538.3
564 | 328 | 214.5 | 533.8 | 701.9 | 173.9 | 537.6
565 | 329 | 215.6 | 533.5 | 699.3 | 174.3 | 537.5
566 | 330 | 216.6 | 533.3 | 690.5 | 174.8 | 536.9
567 | 331 | 217.7 | 531.9 | 688.2 | 175.3 | 534.8
568 | 332 | 218.7 | 533 | 686.5 | 175.8 | 534
569 | 333 | 219.7 | 531.4 | 683.8 | 176.3 | 536.4
570 | 334 | 220.7 | 531.1 | 679.4 | 176.8 | 536.9
571 | 335 | 221.6 | 528.9 | 670.6 | 177.2 | 536.2
572 | 336 | 222.5 | 527.1 | 666.1 | 177.7 | 535.5
573 | 337 | 223.4 | 524.6 | 659.4 | 178.1 | 535.1
574 | 338 | 224.3 | 523.9 | 655.9 | 178.5 | 533.2
575 | 339 | 225.2 | 524.6 | 652.1 | 179 | 533.1
576 | 340 | 226.1 | 525.4 | 654.2 | 179.6 | 535.1
577 | 341 | 227 | 525.9 | 648.7 | 180.1 | 534.8
578 | 342 | 227.9 | 526.1 | 644 | 180.6 | 534.9
579 | 343 | 228.7 | 529.8 | 644.6 | 181.2 | 536.1
580 | 344 | 229.5 | 531.4 | 648.4 | 181.8 | 536.2
581 | 345 | 230.3 | 533.8 | 654.2 | 182.5 | 537.7
582 | 346 | 231.1 | 536.9 | 662.5 | 183.2 | 540.9
583 | 347 | 231.9 | 540.3 | 673 | 183.9 | 546.1
584 | 348 | 232.6 | 543.6 | 673 | 184.7 | 545.2
585 | 349 | 233.3 | 546.6 | 678.4 | 185.4 | 544.3
586 | 350 | 234 | 551.8 | 682 | 186 | 547.9
587 | 351 | 234.7 | 555.6 | 688 | 186.7 | 548.1
588 | 352 | 235.4 | 560.9 | 690.9 | 187.4 | 549.1
589 | 353 | 236.1 | 562.8 | 688.9 | 188.1 | 549.8
590 | 354 | 236.7 | 564 | 690.2 | 188.7 | 548.7
591 | 355 | 237.4 | 567.8 | 701.9 | 189.4 | 552.2
592 | 356 | 238 | 571 | 704.4 | 190.1 | 556
593 | 357 | 238.7 | 572.1 | 698.9 | 190.7 | 554.9
594 | 358 | 239.3 | 573.8 | 696.4 | 191.3 | 556.3
595 | 359 | 240 | 576.1 | 706.4 | 192 | 558.7
596 | 360 | 240.6 | 576.6 | 701.4 | 192.7 | 561.3
597 | 361 | 241.3 | 576.9 | 700.3 | 193.4 | 559.2
598 | 362 | 241.9 | 579.3 | 702 | 194.1 | 562.2
599 | 363 | 242.6 | 579 | 697.4 | 194.7 | 561.5
600 | 364 | 243.3 | 578.4 | 697.9 | 195.4 | 561.1
601 | 365 | 244 | 577.7 | 693 | 196 | 561.1
602 | 366 | 244.8 | 576.6 | 690.9 | 196.6 | 562.3
603 | 367 | 245.5 | 573.3 | 685.9 | 197.2 | 562.2
604 | 368 | 246.2 | 569.5 | 682 | 197.8 | 562.2
605 | 369 | 246.8 | 566 | 674.2 | 198.4 | 561.4
606 | 370 | 247.4 | 565.6 | 676.8 | 198.9 | 565.8
607 | 371 | 247.9 | 562.1 | 668.8 | 199.5 | 561.8
608 | 372 | 248.3 | 559.9 | 666.1 | 200 | 559.3
609 | 373 | 248.8 | 558.8 | 668.4 | 200.6 | 559.6
610 | 374 | 249.4 | 557 | 668.3 | 201.1 | 561.4
611 | 375 | 250.1 | 555.2 | 667.8 | 201.7 | 562.2
612 | 376 | 250.7 | 553.9 | 674.4 | 202.2 | 565.9
613 | 377 | 251.4 | 553.7 | 681.6 | 202.7 | 570.6
614 | 378 | 252 | 553.4 | 682.1 | 203.2 | 569.9
615 | 379 | 252.6 | 554 | 679.1 | 203.7 | 567.7
616 | 380 | 253 | 554.2 | 678.6 | 204.2 | 567.3
617 | 381 | 253.6 | 554.9 | 682 | 204.7 | 569.5
618 | 382 | 254.2 | 555.2 | 686.2 | 205.2 | 571.4
619 | 383 | 254.8 | 556.1 | 677.3 | 205.7 | 568.7
620 | 384 | 255.5 | 557.9 | 672.8 | 206.1 | 567.4
621 | 385 | 256 | 559.7 | 679.4 | 206.6 | 569.4
622 | 386 | 256.7 | 558.6 | 681 | 207.1 | 572.6
623 | 387 | 257.3 | 556.9 | 684 | 207.6 | 574.5
624 | 388 | 258 | 555.6 | 687.4 | 208.1 | 572.5
625 | 389 | 258.6 | 557.6 | 693.5 | 208.6 | 574.5
626 | 390 | 259.2 | 562 | 703.4 | 209.1 | 578.9
627 | 391 | 259.8 | 566 | 708.6 | 209.5 | 581.9
628 | 392 | 260.3 | 568.8 | 717.7 | 210 | 584.7
629 | 393 | 260.9 | 570.6 | 722.7 | 210.6 | 589.2
630 | 394 | 261.4 | 572 | 725.2 | 211.1 | 593.1
631 | 395 | 262 | 573.7 | 723.2 | 211.6 | 591.3
632 | 396 | 262.6 | 574.8 | 716.1 | 212.1 | 590.7
633 | 397 | 263.2 | 575.4 | 711.6 | 212.6 | 589.5
634 | 398 | 263.7 | 575.3 | 711 | 213.1 | 589.1
635 | 399 | 264.2 | 576.8 | 720.1 | 213.6 | 593.4
636 | 400 | 264.6 | 576.5 | 724.5 | 214 | 595.3
637 | 401 | 265 | 576.7 | 732.2 | 214.5 | 597.7
638 | 402 | 265.4 | 577.9 | 727.3 | 215 | 599.2
639 | 403 | 265.9 | 577.1 | 725.5 | 215.5 | 599.4
640 | 404 | 266.3 | 576.9 | 726 | 215.9 | 600.6
641 | 405 | 266.7 | 577.3 | 717.5 | 216.3 | 596.9
642 | 406 | 267.2 | 577.4 | 716 | 216.6 | 595.6
643 | 407 | 267.5 | 577.7 | 713.7 | 217 | 597.7
644 | 408 | 267.8 | 578.1 | 711.5 | 217.3 | 596.7
645 | 409 | 268.2 | 576.8 | 710.9 | 217.6 | 594.5
646 | 410 | 268.7 | 576 | 712.8 | 218 | 601.3
647 | 411 | 269.2 | 576.2 | 699.6 | 218.4 | 600.2
648 | 412 | 269.9 | 579.8 | 695.9 | 218.7 | 603.2
649 | 413 | 270.4 | 580.2 | 691.3 | 218.9 | 605
650 | 414 | 271.2 | 579.8 | 691.5 | 219.2 | 606.6
651 | 415 | 272.1 | 576.9 | 684.5 | 219.6 | 602.8
652 | 416 | 273.1 | 574.3 | 684.1 | 220 | 599.3
653 | 417 | 274 | 576.4 | 693.3 | 220.3 | 604.2
654 | 418 | 274.9 | 577 | 695.5 | 220.7 | 607.1
655 | 419 | 275.6 | 577 | 688.8 | 221.1 | 605.2
656 | 420 | 276.4 | 576.8 | 690.4 | 221.5 | 605.8
657 | 421 | 277.2 | 577.8 | 699.3 | 221.9 | 607.7
658 | 422 | 278.1 | 581.5 | 705.9 | 222.2 | 609.7
659 | 423 | 279.2 | 582.9 | 706.4 | 222.6 | 611
660 | 424 | 280.1 | 583.1 | 704.8 | 223 | 610.5
661 | 425 | 280.8 | 583.1 | 704.6 | 223.3 | 609.2
662 | 426 | 281.5 | 582.7 | 698.3 | 223.7 | 610
663 | 427 | 282 | 587 | 693.1 | 224.1 | 610.4
664 | 428 | 282.8 | 586.3 | 700.4 | 224.4 | 613.3
665 | 429 | 283.6 | 583.6 | 709.5 | 224.9 | 616.5
666 | 430 | 284.5 | 582.9 | 710.7 | 225.4 | 618.2
667 | 431 | 285.4 | 582.7 | 710.2 | 225.9 | 616.3
668 | 432 | 286.4 | 583.2 | 710.6 | 226.3 | 615.3
669 | 433 | 287.4 | 582.9 | 707.8 | 226.7 | 614.9
670 | 434 | 288.3 | 581.7 | 709.9 | 227.1 | 614.6
671 | 435 | 288.8 | 581.5 | 718.7 | 227.5 | 615
672 | 436 | 289.5 | 580.7 | 716 | 227.9 | 614.6
673 | 437 | 290.4 | 579.7 | 719 | 228.3 | 617.2
674 | 438 | 291.3 | 580.6 | 716.5 | 228.7 | 616.9
675 | 439 | 292.3 | 579.9 | 725.3 | 229.1 | 616.9
676 | 440 | 293.1 | 579.4 | 729.1 | 229.5 | 618.8
677 | 441 | 294.1 | 580.2 | 732.3 | 229.9 | 617.9
678 | 442 | 295.1 | 582.7 | 739.1 | 230.3 | 622.9
679 | 443 | 296.2 | 583.9 | 740.3 | 230.7 | 626.3
680 | 444 | 297.2 | 583.8 | 738.1 | 231.2 | 625.4
681 | 445 | 298 | 584.1 | 740.4 | 231.6 | 625.1
682 | 446 | 298.9 | 587.6 | 741.3 | 232 | 629.6
683 | 447 | 299.8 | 587.7 | 743.3 | 232.5 | 630.8
684 | 448 | 300.7 | 587.5 | 744.8 | 233 | 630.7
685 | 449 | 301.6 | 589.6 | 745.8 | 233.5 | 633.3
686 | 450 | 302.5 | 591.5 | 751 | 234 | 636
687 | 451 | 303.5 | 593 | 745.7 | 234.5 | 635
688 | 452 | 304.3 | 593 | 747.2 | 235.1 | 636.2
689 | 453 | 305.2 | 593.6 | 746.5 | 235.5 | 634.3
690 | 454 | 306.2 | 594.2 | 750.7 | 236 | 634.7
691 | 455 | 307.2 | 594.2 | 750.7 | 236.5 | 634.5
692 | 456 | 308.4 | 593.2 | 748.3 | 237.1 | 632.4
693 | 457 | 309.5 | 592.9 | 744.2 | 237.6 | 628.7
694 | 458 | 310.7 | 592.4 | 741.9 | 238.1 | 630.5
695 | 459 | 311.7 | 590.6 | 732.4 | 238.6 | 628.8
696 | 460 | 312.7 | 590.3 | 730.9 | 239.1 | 628.9
697 | 461 | 313.8 | 590.9 | 730.5 | 239.7 | 628.7
698 | 462 | 314.8 | 589.5 | 736.8 | 240.3 | 628
699 | 463 | 315.8 | 589.5 | 739.8 | 240.8 | 629.3
700 | 464 | 316.9 | 594 | 734.1 | 241.3 | 635.7
701 | 465 | 318 | 595.8 | 728.1 | 241.9 | 636.5
702 | 466 | 319.1 | 595.5 | 720.4 | 242.5 | 636.5
703 | 467 | 320.2 | 595.4 | 718.6 | 243.1 | 637.6
704 | 468 | 321.3 | 592.6 | 723.2 | 243.7 | 637.7
705 | 469 | 322.4 | 590.9 | 722.2 | 244.3 | 634.2
706 | 470 | 323.5 | 589.7 | 713.8 | 245 | 631
707 | 471 | 324.5 | 591.9 | 712.1 | 245.6 | 632.4
708 | 472 | 325.6 | 593.3 | 702.9 | 246.5 | 631.6
709 | 473 | 326.7 | 594.4 | 705.9 | 247.3 | 632.6
710 | 474 | 327.7 | 592 | 707.6 | 248 | 631
711 | 475 | 328.8 | 592.3 | 713.5 | 248.6 | 630.8
712 | 476 | 329.8 | 594.8 | 722.1 | 249.3 | 634
713 | 477 | 330.9 | 598.1 | 728.8 | 249.9 | 637.7
714 | 478 | 331.9 | 598.5 | 733 | 250.6 | 637.7
715 | 479 | 332.9 | 599.4 | 732.6 | 251.2 | 638.8
716 | 480 | 333.9 | 600.1 | 733 | 252 | 638.9
717 | 481 | 334.8 | 600.7 | 735.2 | 252.6 | 639.8
718 | 482 | 335.7 | 602.2 | 731.7 | 253.3 | 637.1
719 | 483 | 336.6 | 603.5 | 731.4 | 254 | 636.1
720 | 484 | 337.5 | 603.3 | 722.8 | 254.7 | 634.6
721 | 485 | 338.3 | 602.3 | 718 | 255.3 | 630
722 | 486 | 339 | 602.9 | 718.8 | 256.1 | 628.6
723 | 487 | 339.8 | 600.9 | 718.6 | 256.8 | 629.8
724 | 488 | 340.5 | 601.9 | 718.7 | 257.5 | 631.6
725 | 489 | 341.3 | 602.3 | 718.3 | 258.2 | 633
726 | 490 | 342 | 602.1 | 718 | 259 | 633.6
727 | 491 | 342.6 | 600.8 | 718.7 | 259.7 | 634.1
728 | 492 | 343.3 | 600.4 | 716.5 | 260.5 | 633.1
729 | 493 | 343.9 | 598.2 | 706.5 | 261.2 | 629.6
730 | 494 | 344.6 | 597.1 | 697.1 | 261.9 | 625.2
731 | 495 | 345.2 | 602.1 | 696.7 | 262.6 | 627.3
732 | 496 | 345.8 | 601 | 696.2 | 263.3 | 627.2
733 | 497 | 346.4 | 597.7 | 687.7 | 264 | 622.8
734 | 498 | 347.1 | 594.1 | 686.3 | 264.9 | 619.7
735 | 499 | 347.6 | 591.8 | 686.3 | 265.5 | 620
736 | 500 | 348.2 | 590.8 | 689.4 | 266.2 | 620.3
737 | 501 | 348.8 | 588.2 | 689.3 | 267 | 622.5
738 | 502 | 349.4 | 585.5 | 691.2 | 267.7 | 622.1
739 | 503 | 350 | 584.2 | 690.2 | 268.5 | 622.8
740 | 504 | 350.7 | 582.8 | 681.7 | 269.3 | 622.7
741 | 505 | 351.3 | 582.8 | 676.2 | 270 | 620
742 | 506 | 351.9 | 581.1 | 672.8 | 270.8 | 617.3
743 | 507 | 352.7 | 578.7 | 677.1 | 271.5 | 614.8
744 | 508 | 353.5 | 575.5 | 666.1 | 272.2 | 611.4
745 | 509 | 354.3 | 573.8 | 657.1 | 272.8 | 609.5
746 | 510 | 355.2 | 572.2 | 660.6 | 273.2 | 612.4
747 | 511 | 355.9 | 569.2 | 654.2 | 273.7 | 610
748 | 512 | 356.6 | 566.2 | 649.5 | 274.3 | 608
749 | 513 | 357.3 | 564.4 | 646.6 | 274.9 | 608.8
750 | 514 | 357.9 | 563 | 647.3 | 275.5 | 608.5
751 | 515 | 358.4 | 561.7 | 646.5 | 276.2 | 607.8
752 | 516 | 359 | 559.7 | 647.6 | 276.9 | 607.3
753 | 517 | 359.5 | 559.5 | 651.5 | 277.6 | 607.3
754 | 518 | 360 | 558.4 | 644.3 | 278.3 | 605
755 | 519 | 360.4 | 557.7 | 634 | 278.9 | 602.4
756 | 520 | 360.9 | 555.8 | 622 | 279.6 | 600
757 | 521 | 361.3 | 557.7 | 620.4 | 280.3 | 600.3
758 | 522 | 361.7 | 557.2 | 624.3 | 281 | 602.3
759 | 523 | 362.1 | 556.7 | 625.5 | 281.7 | 603.5
760 | 524 | 362.5 | 555.4 | 628.4 | 282.4 | 604.2
761 | 525 | 363 | 553.8 | 626.1 | 283.1 | 603.6
762 | 526 | 363.4 | 552 | 623.9 | 283.8 | 601.4
763 | 527 | 363.8 | 550.5 | 623.8 | 284.5 | 600.3
764 | 528 | 364.3 | 549.9 | 621.7 | 285.2 | 597.9
765 | 529 | 364.7 | 550.1 | 626.4 | 285.9 | 597.7
766 | 530 | 365.2 | 550.9 | 629.9 | 286.7 | 597.9
767 | 531 | 365.7 | 551.3 | 625.2 | 287.4 | 595.4
768 | 532 | 366.2 | 551.7 | 615.8 | 288.2 | 593.2
769 | 533 | 366.8 | 552.4 | 608.9 | 288.9 | 592.9
770 | 534 | 367.4 | 553.1 | 602.6 | 289.7 | 593.1
771 | 535 | 368 | 553.1 | 600.2 | 290.4 | 593.3
772 | 536 | 368.7 | 552.8 | 597.1 | 291.1 | 593
773 | 537 | 369.5 | 553.7 | 589.3 | 291.8 | 593.6
774 | 538 | 370.5 | 555.1 | 589.4 | 292.5 | 598
775 | 539 | 371.6 | 554.8 | 588.9 | 293.1 | 598.5
776 | 540 | 372.9 | 553.2 | 588.4 | 293.8 | 594.3
777 | 541 | 374.4 | 551.8 | 590.3 | 294.5 | 592.1
778 | 542 | 375.8 | 549.8 | 590.9 | 295.2 | 590.6
779 | 543 | 377 | 548.2 | 591.9 | 295.9 | 589.3
780 | 544 | 378.4 | 548 | 597 | 296.5 | 589.2
781 | 545 | 380.3 | 547.8 | 600.1 | 297.1 | 588.5
782 | 546 | 383.6 | 550 | 610.6 | 297.8 | 588.2
783 | 547 | 387.4 | 552.8 | 628.5 | 298.4 | 590.1
784 | 548 | 392.1 | 555.6 | 646 | 299 | 597.5
785 | 549 | 396.8 | 555.3 | 652.6 | 299.5 | 599.5
786 | 550 | 400.8 | 555.9 | 654.6 | 300.2 | 598.1
787 | 551 | 405 | 555.7 | 661.2 | 300.8 | 600
788 | 552 | 408.8 | 555.8 | 662.2 | 301.3 | 599.3
789 | 553 | 412.4 | 555.4 | 659.9 | 302 | 594.7
790 | 554 | 416.5 | 557.4 | 660.1 | 302.7 | 593.7
791 | 555 | 420.4 | 557.8 | 653.3 | 303.3 | 591.4
792 | 556 | 424 | 557.2 | 644.7 | 303.9 | 589.2
793 | 557 | 427.1 | 556.8 | 635.5 | 304.5 | 588.5
794 | 558 | 429.8 | 556.5 | 625.1 | 305 | 586.3
795 | 559 | 433 | 557.6 | 619.8 | 305.7 | 584.2
796 | 560 | 436.6 | 558.1 | 619.7 | 306.3 | 584.7
797 | 561 | 439.8 | 558.6 | 613.4 | 306.9 | 585.3
798 | 562 | 442.6 | 557.2 | 605.4 | 307.6 | 583
799 | 563 | 445.1 | 555.5 | 598.2 | 308.2 | 580.5
800 | 564 | 447.9 | 555.6 | 602.6 | 308.8 | 581
801 | 565 | 451.3 | 555.1 | 598.8 | 309.4 | 581.7
802 | 566 | 455.2 | 553.8 | 595 | 310 | 581.3
803 | 567 | 458.1 | 552.7 | 592.8 | 310.5 | 579.9
804 | 568 | 461.1 | 552.1 | 596.5 | 311.2 | 580.4
805 | 569 | 464.5 | 553.6 | 603.4 | 311.9 | 582.5
806 | 570 | 468.6 | 555.2 | 613 | 312.5 | 583.7
807 | 571 | 473.6 | 557.8 | 627.8 | 313.3 | 585
808 | 572 | 478.2 | 559.5 | 643.6 | 314.1 | 587.4
809 | 573 | 484 | 562.2 | 667.6 | 315 | 596
810 | 574 | 489.3 | 564 | 671.6 | 315.9 | 598.2
811 | 575 | 493.4 | 565 | 678.7 | 316.8 | 598.4
812 | 576 | 497.9 | 566.4 | 684.7 | 317.6 | 600.1
813 | 577 | 502.1 | 567.7 | 695.4 | 318.4 | 601.4
814 | 578 | 506 | 567.1 | 698.8 | 319.1 | 600.7
815 | 579 | 508.5 | 566.5 | 690.1 | 319.8 | 596.7
816 | 580 | 510.2 | 565 | 679.7 | 320.5 | 593
817 | 581 | 511.7 | 564.9 | 666.4 | 321.1 | 588.9
818 | 582 | 512.7 | 564.7 | 658.3 | 321.6 | 588.8
819 | 583 | 513.9 | 566.5 | 652.5 | 322.3 | 591.5
820 | 584 | 514.9 | 568.2 | 641.4 | 322.9 | 590.3
821 | 585 | 515.5 | 567.1 | 628.8 | 323.3 | 587.4
822 | 586 | 516.7 | 565.9 | 621.4 | 323.8 | 585.1
823 | 587 | 518.1 | 567.2 | 616.8 | 324.3 | 584.3
824 | 588 | 519.2 | 569.4 | 608.7 | 325 | 584.2
825 | 589 | 520.5 | 568.8 | 600.4 | 325.5 | 581.5
826 | 590 | 521.3 | 567.7 | 592.3 | 326.1 | 580.4
827 | 591 | 521.5 | 568.4 | 583.5 | 326.6 | 579.4
828 | 592 | 522.6 | 569.2 | 579 | 327.1 | 579.5
829 | 593 | 523.7 | 570 | 576.6 | 327.6 | 580.9
830 | 594 | 524.5 | 570 | 570.9 | 328.2 | 580.6
831 | 595 | 525.8 | 571 | 566.8 | 328.7 | 580.3
832 | 596 | 527 | 573.2 | 564.6 | 329.1 | 580.5
833 | 597 | 527.9 | 573 | 563.5 | 329.7 | 580.2
834 | 598 | 529.2 | 570.9 | 568.7 | 330.2 | 579.3
835 | 599 | 530.7 | 568.5 | 573.2 | 330.7 | 580.4
836 | 600 | 531.4 | 567.6 | 576.5 | 331.1 | 579.6
837 | 601 | 531.4 | 566.2 | 577.2 | 331.5 | 578
838 | 602 | 531.4 | 565.9 | 578 | 331.9 | 576.6
839 | 603 | 531 | 563.3 | 575.9 | 332.4 | 574.4
840 | 604 | 530.7 | 562.9 | 575.2 | 333 | 573.9
841 | 605 | 530.3 | 564.5 | 571.7 | 333.5 | 576.5
842 | 606 | 530 | 566 | 566.3 | 333.9 | 577.6
843 | 607 | 530.4 | 567.1 | 562.1 | 334.4 | 577.5
844 | 608 | 530.2 | 566.2 | 560.9 | 334.8 | 578.5
845 | 609 | 529.7 | 565.4 | 563.8 | 335.4 | 576.7
846 | 610 | 530.1 | 565.8 | 572.5 | 335.9 | 577.2
847 | 611 | 530.1 | 565.3 | 576.1 | 336.3 | 576
848 | 612 | 530.5 | 566.2 | 580.9 | 336.7 | 575.5
849 | 613 | 529.9 | 566.6 | 577.7 | 337.2 | 574.1
850 | 614 | 529.4 | 566.5 | 574.5 | 337.8 | 573.9
851 | 615 | 528.4 | 566.3 | 570.1 | 338.4 | 572.8
852 | 616 | 527.7 | 566.7 | 567.3 | 339 | 571.6
853 | 617 | 527 | 567.8 | 568.7 | 339.7 | 572.2
854 | 618 | 526.9 | 567.5 | 571.7 | 340.2 | 577.4
855 | 619 | 526.8 | 567.1 | 572.9 | 340.8 | 581.2
856 | 620 | 526.1 | 567.1 | 573 | 341.3 | 580
857 | 621 | 525.1 | 566.5 | 573.4 | 341.8 | 576.3
858 | 622 | 524.3 | 566.6 | 571.9 | 342.4 | 574.3
859 | 623 | 523.2 | 568 | 567.6 | 343 | 571.7
860 | 624 | 522.2 | 568.5 | 565.1 | 343.7 | 570.5
861 | 625 | 521.6 | 568.7 | 565.7 | 344.2 | 573.6
862 | 626 | 521.3 | 568.7 | 565.4 | 344.7 | 575.7
863 | 627 | 520.9 | 566.8 | 567.3 | 345.4 | 574.7
864 | 628 | 520.2 | 415.2 | 569.3 | 345.9 | 574.8
865 | 629 | 519.8 | 561.3 | 570.1 | 346.5 | 575.6
866 | 630 | 519.6 | 565.8 | 572.2 | 347.1 | 575.6
867 | 631 | 519.5 | 566.7 | 571.3 | 347.8 | 574.8
868 | 632 | 519.4 | 568.8 | 568.7 | 348.5 | 574.8
869 | 633 | 519.5 | 569.5 | 566.8 | 349.1 | 574.9
870 | 634 | 519.2 | 570.9 | 564.9 | 349.5 | 575.8
871 | 635 | 519.3 | 571.1 | 564.2 | 349.4 | 574.8
872 | 636 | 519.7 | 460.4 | 568.1 | 349.8 | 576.9
873 | 637 | 520 | 502.4 | 569 | 350.3 | 577.9
874 | 638 | 520.2 | 573.5 | 567.2 | 351.1 | 577
875 | 639 | 520.4 | 435.6 | 566.6 | 351.9 | 576.2
876 | 640 | 520.4 | 536.1 | 565.4 | 352.8 | 575.4
877 | 641 | 520.5 | 576.1 | 563.7 | 354 | 576.3
878 | 642 | 520.2 | 401.2 | 561 | 355 | 576.3
879 | 643 | 520.4 | 568.5 | 559.1 | 355.9 | 578.6
880 | 644 | 521 | 547 | 561 | 356.9 | 578.8
881 | 645 | 521.2 | 322.2 | 562.3 | 358 | 577.4
882 | 646 | 520.9 | 355.4 | 561.9 | 359 | 575.6
883 | 647 | 521.4 | 423.5 | 566.4 | 359.9 | 576
884 | 648 | 521.5 | 394.7 | 570.1 | 360.8 | 575.8
885 | 649 | 521.3 | 572.9 | 570.1 | 361.7 | 575.3
886 | 650 | 521.2 | 385.7 | 567.3 | 362.7 | 575.8
887 | 651 | 521.1 | 434.6 | 568.4 | 363.7 | 577.6
888 | 652 | 520.9 | 573.6 | 567.7 | 364.7 | 577.3
889 | 653 | 520.7 | 572.6 | 568.8 | 365.7 | 578.5
890 | 654 | 520.6 | 571.4 | 566.6 | 366.7 | 577.6
891 | 655 | 520.6 | 571.5 | 567.4 | 367.7 | 577.5
892 | 656 | 520.7 | 572.2 | 573.3 | 368.7 | 576.5
893 | 657 | 521 | 572.6 | 588.6 | 369.8 | 577.2
894 | 658 | 521.2 | 572.9 | 589.3 | 371 | 576.8
895 | 659 | 520.9 | 572.6 | 585.3 | 371.9 | 575.4
896 | 660 | 520.6 | 573.6 | 577.7 | 372.9 | 574.1
897 | 661 | 520.6 | 575.3 | 574 | 374 | 572.7
898 | 662 | 520.7 | 575 | 571.7 | 375.1 | 572.6
899 | 663 | 521 | 576.3 | 574.6 | 376.2 | 577.5
900 | 664 | 520.7 | 576.4 | 574.7 | 377.3 | 576.2
901 | 665 | 520.9 | 575.9 | 571.9 | 378.4 | 575.6
902 | 666 | 520.6 | 574.8 | 567.4 | 379.5 | 574.7
903 | 667 | 520.6 | 573.9 | 565.7 | 380.6 | 573.4
904 | 668 | 520.4 | 574.7 | 567 | 381.7 | 574.7
905 | 669 | 520.6 | 575.2 | 569.7 | 382.8 | 575.9
906 | 670 | 520.8 | 339.8 | 568.1 | 383.8 | 575.6
907 | 671 | 520.6 | 473 | 566.1 | 384.9 | 575.1
908 | 672 | 520.8 | 455.4 | 569.1 | 385.9 | 577.4
909 | 673 | 521 | 322.6 | 571.7 | 386.9 | 578.6
910 | 674 | 521.3 | 577.8 | 575.9 | 388 | 580.7
911 | 675 | 521.5 | 486.8 | 581.4 | 389 | 583.8
912 | 676 | 522.3 | 399.5 | 594 | 390.1 | 588.8
913 | 677 | 522.6 | 580.5 | 599.3 | 391.1 | 592.6
914 | 678 | 522.7 | 401.5 | 600.1 | 392.2 | 596.1
915 | 679 | 523.1 | 436.3 | 601.1 | 393.2 | 594.6
916 | 680 | 523.1 | 578.1 | 598 | 394.2 | 589.5
917 | 681 | 522.9 | 277.1 | 598.1 | 395.2 | 588.7
918 | 682 | 522.9 | 495.1 | 593.6 | 396.2 | 587.8
919 | 683 | 522.8 | 580.7 | 587.4 | 397.1 | 586.9
920 | 684 | 522.9 | 210 | 581.6 | 398.1 | 585.4
921 | 685 | 523.5 | 570.6 | 585.7 | 399.1 | 586.4
922 | 686 | 523.5 | 533.5 | 584.9 | 400 | 586
923 | 687 | 523.7 | 226 | 584.5 | 401 | 585.1
924 | 688 | 524.3 | 268.8 | 588.7 | 401.9 | 585.2
925 | 689 | 524.8 | 370.9 | 587.9 | 402.8 | 586.1
926 | 690 | 524.8 | 330.5 | 587.8 | 403.8 | 586.5
927 | 691 | 524.7 | 581.6 | 583.6 | 404.7 | 585.5
928 | 692 | 524.6 | 365.1 | 578.7 | 405.7 | 586.1
929 | 693 | 524.7 | 411.3 | 579.9 | 406.6 | 590
930 | 694 | 525.3 | 582.1 | 589 | 407.5 | 593.8
931 | 695 | 525.9 | 582.1 | 588.4 | 408.4 | 599.8
932 | 696 | 526.8 | 582.2 | 592.4 | 409.4 | 599.6
933 | 697 | 527.3 | 581.9 | 592.9 | 410.3 | 599.6
934 | 698 | 527.6 | 580.4 | 590.1 | 411.3 | 596.8
935 | 699 | 527.8 | 577.8 | 591.1 | 412.2 | 595.2
936 | 700 | 528.2 | 576.4 | 592.1 | 413.2 | 595.3
937 | 701 | 528.5 | 578.2 | 594.6 | 414.1 | 597.3
938 | 702 | 528.6 | 580.1 | 594.7 | 415 | 596.3
939 | 703 | 528.8 | 582 | 595.9 | 416 | 597.7
940 | 704 | 529 | 581.8 | 590.7 | 416.9 | 598.5
941 | 705 | 529.3 | 582.5 | 587.4 | 417.8 | 595.2
942 | 706 | 529.8 | 582.5 | 593.2 | 418.7 | 597.4
943 | 707 | 530.4 | 582.4 | 595.2 | 419.6 | 600.4
944 | 708 | 530.9 | 585 | 597 | 420.5 | 598.4
945 | 709 | 531.2 | 586.5 | 597.2 | 421.5 | 597.9
946 | 710 | 531.9 | 588.2 | 595.1 | 422.4 | 597.8
947 | 711 | 532.8 | 590.3 | 600.2 | 423.3 | 598.7
948 | 712 | 533.4 | 297.7 | 600.7 | 424.3 | 598.7
949 | 713 | 534.3 | 431.3 | 601.8 | 425.3 | 597.6
950 | 714 | 534.9 | 434.5 | 598 | 426.3 | 596.6
951 | 715 | 535.9 | 278.4 | 593.4 | 427.3 | 596
952 | 716 | 536.9 | 597.2 | 595.5 | 428.3 | 597
953 | 717 | 537.5 | 475.7 | 593.8 | 429.2 | 595.9
954 | 718 | 538.3 | 367 | 592 | 430.2 | 595.9
955 | 719 | 540 | 601.6 | 600.7 | 431.2 | 598.5
956 | 720 | 541.1 | 466.6 | 598.7 | 432.1 | 601.6
957 | 721 | 541.8 | 600.8 | 596.9 | 433 | 599.3
958 | 722 | 542.8 | 603.4 | 592.3 | 434.1 | 599.3
959 | 723 | 543.5 | 603.4 | 592.9 | 435.2 | 601.9
960 | 724 | 544.8 | 604.1 | 601.5 | 436.2 | 605.2
961 | 725 | 546.4 | 603.8 | 617.3 | 437.1 | 609.5
962 | 726 | 546.9 | 602.4 | 608.4 | 438 | 608.7
963 | 727 | 548 | 600.9 | 611.3 | 438.9 | 605.6
964 | 728 | 549.2 | 600.5 | 614.3 | 440 | 606.8
965 | 729 | 549.8 | 599.7 | 613 | 441 | 605.5
966 | 730 | 550.7 | 599.5 | 612.9 | 441.9 | 602.9
967 | 731 | 551.5 | 599.7 | 614.7 | 442.7 | 602.1
968 | 732 | 552.1 | 599.6 | 609.3 | 443.7 | 602.9
969 | 733 | 552.8 | 599 | 603.6 | 444.6 | 601.6
970 | 734 | 553.8 | 598.7 | 601.5 | 445.5 | 601.3
971 | 735 | 554.6 | 598.3 | 598.7 | 446.4 | 600.7
972 | 736 | 555.1 | 600.3 | 599.5 | 447.4 | 603.4
973 | 737 | 553.8 | 601.6 | 593.1 | 448.5 | 603.5
974 | 738 | 553.1 | 599.3 | 592.7 | 449.4 | 607
975 | 739 | 552.8 | 596.7 | 592.7 | 450.4 | 607.2
976 | 740 | 553.1 | 596.1 | 591.6 | 451.4 | 606.9
977 | 741 | 554.2 | 593.3 | 595.1 | 452.4 | 605.8
978 | 742 | 555.1 | 592.5 | 595.6 | 453.2 | 604.5
979 | 743 | 555.5 | 591.7 | 590.5 | 454.2 | 601.8
980 | 744 | 556.1 | 591.1 | 588 | 455.1 | 602
981 | 745 | 556.6 | 590.4 | 583.9 | 455.9 | 602.5
982 | 746 | 557 | 590 | 577.8 | 456.8 | 602
983 | 747 | 557.9 | 588.3 | 574.2 | 457.7 | 600.3
984 | 748 | 559.4 | 587.5 | 576.8 | 458.5 | 600.5
985 | 749 | 560.4 | 587 | 576.3 | 459.4 | 600
986 | 750 | 561.5 | 586.5 | 575 | 460.3 | 599.7
987 | 751 | 563 | 588 | 569.9 | 461.1 | 600.5
988 | 752 | 564.5 | 588.5 | 567.3 | 461.9 | 599.6
989 | 753 | 565.7 | 589.5 | 568.3 | 462.7 | 599.6
990 | 754 | 567 | 590.8 | 569 | 463.6 | 604.5
991 | 755 | 568 | 590.4 | 563.9 | 464.4 | 601.8
992 | 756 | 569.4 | 588.7 | 569.9 | 465.2 | 601.6
993 | 757 | 570.5 | 586.6 | 570.5 | 466 | 602.7
994 | 758 | 571.4 | 586.1 | 566.8 | 466.8 | 601.3
995 | 759 | 572.6 | 584.9 | 565.6 | 467.6 | 601.5
996 | 760 | 573.8 | 584.4 | 565.8 | 468.3 | 601
997 | 761 | 575.1 | 585.1 | 565.1 | 469.2 | 599.9
998 | 762 | 576.5 | 585.2 | 565 | 470 | 599.5
999 | 763 | 577.5 | 585.8 | 567.4 | 470.7 | 599
1000 | 764 | 577.9 | 584 | 569.2 | 471.5 | 598.7
1001 | 765 | 578.2 | 582.2 | 570.5 | 472.2 | 598.1
1002 | 766 | 578.3 | 581.4 | 572.5 | 473 | 598.3
1003 | 767 | 578.4 | 579.8 | 571.5 | 473.7 | 597.5
1004 | 768 | 578.8 | 577.5 | 573 | 474.4 | 598
1005 | 769 | 579.2 | 576.3 | 572.3 | 475.1 | 597
1006 | 770 | 579.5 | 575.5 | 565.9 | 475.8 | 595.1
1007 | 771 | 580.4 | 576.5 | 564.3 | 476.6 | 594.7
1008 | 772 | 581.4 | 576.6 | 562.8 | 477.3 | 594
1009 | 773 | 582.5 | 577.4 | 562.1 | 478 | 593.3
1010 | 774 | 583.8 | 578.9 | 563.9 | 478.8 | 593.3
1011 | 775 | 585.5 | 580.6 | 570.7 | 479.7 | 593.7
1012 | 776 | 586.3 | 582.8 | 570.4 | 480.4 | 593.7
1013 | 777 | 586.3 | 582.5 | 566.9 | 481.3 | 592.5
1014 | 778 | 586.7 | 584.3 | 566.3 | 482.3 | 592.9
1015 | 779 | 587.9 | 586 | 566.8 | 483.2 | 592.8
1016 | 780 | 588.4 | 586.9 | 569.2 | 484 | 592.8
1017 | 781 | 588.2 | 587.4 | 564.5 | 484.7 | 592.5
1018 | 782 | 588.5 | 589.5 | 564.2 | 485.7 | 592.5
1019 | 783 | 588.5 | 590.7 | 564.8 | 486.6 | 591.5
1020 | 784 | 588.6 | 591.9 | 565.3 | 487.5 | 590.8
1021 | 785 | 588.7 | 591.8 | 563.9 | 488.3 | 590.9
1022 | 786 | 589 | 593.3 | 561 | 489.2 | 592.5
1023 | 787 | 589.7 | 594 | 559.6 | 490 | 593.5
1024 | 788 | 590.6 | 594.3 | 555.7 | 490.8 | 592.9
1025 | 789 | 591.5 | 594 | 550.2 | 491.4 | 590.7
1026 | 790 | 592.4 | 594.5 | 549 | 492 | 587.9
1027 | 791 | 592.7 | 596.4 | 548.7 | 493 | 588.3
1028 | 792 | 593.1 | 595.5 | 546.2 | 493.8 | 587.5
1029 | 793 | 593.6 | 595.2 | 544.7 | 494.5 | 586.9
1030 | 794 | 594.4 | 595.2 | 545.8 | 495.3 | 587.5
1031 | 795 | 595.6 | 595.5 | 550.5 | 496.1 | 587.8
1032 | 796 | 597 | 595.1 | 555.9 | 496.8 | 587.9
1033 | 797 | 598.1 | 594.2 | 556 | 497.5 | 587.5
1034 | 798 | 598.6 | 592.6 | 554.9 | 498.1 | 587.2
1035 | 799 | 599.5 | 591.8 | 550.6 | 498.8 | 587.7
1036 | 800 | 600.1 | 590.8 | 548.4 | 499.5 | 587.1
1037 | 801 | 601 | 589.5 | 546.4 | 500.1 | 587.4
1038 | 802 | 601.8 | 588.3 | 543.6 | 500.8 | 586.6
1039 | 803 | 601.9 | 585.7 | 542.4 | 501.3 | 585.7
1040 | 804 | 602 | 584.3 | 542.8 | 501.9 | 585
1041 | 805 | 602.2 | 583.3 | 541.7 | 502.4 | 584.6
1042 | 806 | 602.3 | 581.8 | 542.5 | 503 | 584.4
1043 | 807 | 602.4 | 580.2 | 544.6 | 503.6 | 585.4
1044 | 808 | 602.4 | 579.2 | 549.7 | 504.3 | 589.2
1045 | 809 | 602.3 | 578.4 | 550.9 | 504.9 | 590.8
1046 | 810 | 602.1 | 577.9 | 552.3 | 505.4 | 590.8
1047 | 811 | 602.6 | 577.5 | 556.6 | 506.1 | 589.1
1048 | 812 | 603.4 | 578.3 | 559.6 | 506.9 | 587.8
1049 | 813 | 603.5 | 578.3 | 556.7 | 507.7 | 585
1050 | 814 | 603.7 | 577.9 | 556.8 | 508.5 | 584.5
1051 | 815 | 604.1 | 578.1 | 563.3 | 509.3 | 587.7
1052 | 816 | 603.8 | 578.1 | 560.1 | 509.9 | 588.1
1053 | 817 | 603.5 | 577.1 | 560.6 | 510.5 | 588.4
1054 | 818 | 603.5 | 576.8 | 564 | 511.2 | 590.6
1055 | 819 | 603.2 | 575.9 | 566.7 | 511.9 | 591.6
1056 | 820 | 603.5 | 575.1 | 565.7 | 512.5 | 590.8
1057 | 821 | 604.1 | 574.8 | 562.1 | 513.2 | 588.5
1058 | 822 | 605.1 | 575.1 | 564.2 | 513.7 | 588
1059 | 823 | 606.2 | 575.1 | 563.3 | 514.4 | 588.6
1060 | 824 | 607.3 | 575.9 | 560.3 | 515.2 | 588.6
1061 | 825 | 608.4 | 576.5 | 557.5 | 516.1 | 587.6
1062 | 826 | 608.7 | 576.6 | 554.9 | 516.6 | 587.7
1063 | 827 | 608.7 | 576.1 | 551.9 | 517.1 | 587.3
1064 | 828 | 608.7 | 575.9 | 551.5 | 517.5 | 589.4
1065 | 829 | 608.5 | 575.3 | 548.5 | 518.1 | 589.3
1066 | 830 | 607.5 | 575.1 | 546.7 | 518.6 | 588.2
1067 | 831 | 607.2 | 575.5 | 546.1 | 519.2 | 588.3
1068 | 832 | 607.2 | 576.1 | 549 | 519.9 | 589.7
1069 | 833 | 607 | 576 | 545.3 | 520.6 | 588.9
1070 | 834 | 607.3 | 575.4 | 546 | 520.8 | 586.6
1071 | 835 | 607.6 | 576 | 545.5 | 521.2 | 587.1
1072 | 836 | 608.1 | 576.2 | 544.4 | 521.8 | 586.8
1073 | 837 | 608.6 | 576.1 | 544.3 | 522.2 | 585.8
1074 | 838 | 609.1 | 576.1 | 544 | 522.4 | 585.2
1075 | 839 | 609.9 | 576.6 | 543.3 | 523 | 584.4
1076 | 840 | 610.5 | 577.1 | 546.9 | 523.5 | 584.2
1077 | 841 | 610.7 | 577.8 | 548.5 | 524.1 | 586.7
1078 | 842 | 611.8 | 577.8 | 553.8 | 524.7 | 586.2
1079 | 843 | 613.2 | 577.8 | 555.8 | 525.6 | 585.2
1080 | 844 | 614.2 | 579.1 | 557.9 | 527 | 584.4
1081 | 845 | 615.4 | 579.8 | 561.7 | 527.6 | 584.8
1082 | 846 | 616.5 | 579.8 | 567 | 528.8 | 585.4
1083 | 847 | 616.8 | 580.5 | 567.7 | 530.3 | 585.9
1084 | 848 | 617.8 | 580.5 | 568.6 | 531.2 | 586
1085 | 849 | 618 | 580.4 | 567.7 | 532.3 | 585.5
1086 | 850 | 618.5 | 580.3 | 569.2 | 533.7 | 584.8
1087 | 851 | 619.1 | 581.1 | 569 | 535.1 | 585.4
1088 | 852 | 619.6 | 581.2 | 564.6 | 536.4 | 585
1089 | 853 | 619.6 | 581.2 | 563.7 | 537.4 | 584.6
1090 | 854 | 619.6 | 581.3 | 561.3 | 538.7 | 583.9
1091 | 855 | 619.3 | 582 | 557.9 | 539.8 | 583.6
1092 | 856 | 619.4 | 582.6 | 553.6 | 540.7 | 582.9
1093 | 857 | 618.7 | 583 | 553.2 | 541.7 | 583.9
1094 | 858 | 618.8 | 584.7 | 551.2 | 542.4 | 584.8
1095 | 859 | 619.3 | 585.4 | 548.3 | 543 | 583.5
1096 | 860 | 619.7 | 584.4 | 546.4 | 543.2 | 582.4
1097 | 861 | 620.4 | 584.4 | 545.8 | 543.7 | 583.6
1098 | 862 | 621.5 | 583.9 | 546.1 | 544.1 | 584.2
1099 | 863 | 622.3 | 582.8 | 548.4 | 544.5 | 585.2
1100 | 864 | 622.7 | 582.2 | 549.5 | 544.9 | 585.6
1101 | 865 | 622.7 | 582.6 | 552.2 | 545.3 | 586.1
1102 | 866 | 623.5 | 582.3 | 552.3 | 545.6 | 584.4
1103 | 867 | 624.2 | 580.7 | 552.7 | 545.9 | 583.3
1104 | 868 | 624 | 580.4 | 551.6 | 546.7 | 584.3
1105 | 869 | 624.7 | 579.5 | 548.8 | 547.2 | 582.8
1106 | 870 | 625.3 | 579.5 | 549.9 | 547.4 | 583.1
1107 | 871 | 625.9 | 579.9 | 552.8 | 547.8 | 583.9
1108 | 872 | 627 | 579.7 | 556.1 | 548 | 584
1109 | 873 | 627.8 | 578.9 | 552.7 | 548.3 | 584.4
1110 | 874 | 628.1 | 578.4 | 547.3 | 548.4 | 583.9
1111 | 875 | 629 | 578.5 | 546.8 | 548.7 | 582.8
1112 | 876 | 630 | 578.2 | 551.3 | 548.9 | 582.5
1113 | 877 | 630.7 | 577.8 | 551.9 | 549.2 | 582.5
1114 | 878 | 631 | 577.2 | 550.6 | 549.3 | 582.2
1115 | 879 | 630.8 | 577.3 | 549.6 | 549.6 | 581.7
1116 | 880 | 630.3 | 577.2 | 546.8 | 549.8 | 580.8
1117 | 881 | 629.7 | 576.1 | 542.9 | 549.9 | 580
1118 | 882 | 629.6 | 575 | 540.1 | 549.8 | 578.8
1119 | 883 | 629.8 | 574.2 | 541.5 | 549.6 | 578.1
1120 | 884 | 630.6 | 573.7 | 548 | 549.9 | 578.7
1121 | 885 | 630.4 | 573.1 | 552.1 | 549.9 | 579.4
1122 | 886 | 630.8 | 573.1 | 562.9 | 550 | 581.1
1123 | 887 | 631.1 | 573.8 | 566 | 550.1 | 581.9
1124 | 888 | 632 | 574.5 | 566.3 | 550.4 | 582.8
1125 | 889 | 632.7 | 575.1 | 564.8 | 550.8 | 584.2
1126 | 890 | 633.3 | 574.8 | 563.8 | 551.1 | 583.2
1127 | 891 | 633.7 | 574.5 | 564.8 | 551.8 | 582.9
1128 | 892 | 634.3 | 575.1 | 565.6 | 552.3 | 583.9
1129 | 893 | 634.8 | 575.7 | 564.5 | 552.6 | 586.2
1130 | 894 | 634.6 | 575.7 | 560 | 552.9 | 585.4
1131 | 895 | 634.4 | 574.2 | 561.2 | 553.1 | 583.9
1132 | 896 | 635.2 | 574.5 | 562.2 | 553.6 | 583.4
1133 | 897 | 635.7 | 574.5 | 560.8 | 553.7 | 583.6
1134 | 898 | 636.1 | 574 | 559.6 | 553.9 | 584
1135 | 899 | 636.6 | 573.7 | 556.5 | 554 | 583.5
1136 | 900 | 637.9 | 573.1 | 556.7 | 554 | 582.6
1137 | 901 | 639 | 572.6 | 558.8 | 554.2 | 583.1
1138 | 902 | 639.1 | 573.3 | 558.2 | 554.3 | 584.2
1139 | 903 | 638.7 | 574.1 | 555.2 | 554.4 | 585.1
1140 | 904 | 638 | 574.4 | 553.1 | 554.7 | 584.5
1141 | 905 | 637.7 | 574.3 | 552 | 554.7 | 584
1142 | 906 | 637.8 | 574.3 | 557.2 | 555 | 585.8
1143 | 907 | 637.7 | 574.1 | 560.4 | 555.2 | 587.5
1144 | 908 | 637.5 | 573.8 | 558.7 | 555.5 | 586.4
1145 | 909 | 638 | 572.8 | 562.4 | 555.6 | 586.1
1146 | 910 | 638.3 | 572.4 | 565.3 | 555.7 | 586.8
1147 | 911 | 638.4 | 572.7 | 563.5 | 556 | 587.8
1148 | 912 | 639.4 | 572.8 | 566 | 556.1 | 588.2
1149 | 913 | 639.7 | 573.2 | 574.6 | 556.3 | 588.7
1150 | 914 | 639.6 | 574.3 | 577.3 | 556.6 | 591
1151 | 915 | 640 | 575.4 | 572.6 | 557.3 | 589.7
1152 | 916 | 640.5 | 575.4 | 568.7 | 557.6 | 588
1153 | 917 | 641.6 | 574.8 | 566.7 | 557.8 | 587.2
1154 | 918 | 642.2 | 573.9 | 565.4 | 558.1 | 586.9
1155 | 919 | 642.1 | 573.2 | 563.3 | 558.2 | 585.9
1156 | 920 | 642.5 | 572.6 | 562.4 | 558.3 | 585.2
1157 | 921 | 642.1 | 572.5 | 561.1 | 558.5 | 585.1
1158 | 922 | 641.5 | 571.9 | 557.3 | 558.6 | 584.1
1159 | 923 | 641.2 | 571.3 | 554.3 | 558.6 | 583.3
1160 | 924 | 640.8 | 569.4 | 553.6 | 558.7 | 582.4
1161 | 925 | 641 | 569.3 | 557.3 | 559 | 583.3
1162 | 926 | 641.8 | 569.7 | 561.3 | 559.1 | 584.7
1163 | 927 | 642.5 | 569.9 | 563 | 559.4 | 584.3
1164 | 928 | 643.8 | 569.8 | 569.1 | 559.6 | 584.3
1165 | 929 | 644 | 569.7 | 575.6 | 559.8 | 585.3
1166 | 930 | 644.2 | 569.6 | 577.2 | 560.1 | 584.4
1167 | 931 | 644.5 | 570.1 | 577.7 | 560.2 | 585.3
1168 | 932 | 644.8 | 570.8 | 573.6 | 560.7 | 585.8
1169 | 933 | 644.9 | 571.3 | 569.3 | 561 | 585.3
1170 | 934 | 644.6 | 571 | 567.8 | 561.1 | 585.2
1171 | 935 | 644.7 | 570.7 | 571.3 | 561.5 | 585.6
1172 | 936 | 644.7 | 570.8 | 571.6 | 561.8 | 586.4
1173 | 937 | 644.7 | 571.2 | 569.6 | 562.1 | 587.6
1174 | 938 | 645.1 | 571.5 | 569.7 | 562.3 | 588.4
1175 | 939 | 645.4 | 571.5 | 572.1 | 562.4 | 587.9
1176 | 940 | 645.6 | 571.4 | 570.3 | 562.5 | 587.5
1177 | 941 | 645.7 | 571.4 | 567.2 | 562.5 | 586.8
1178 | 942 | 645.1 | 571 | 560.7 | 562.5 | 585.1
1179 | 943 | 645 | 570.3 | 555.7 | 562.5 | 584.4
1180 | 944 | 645 | 569.9 | 553.7 | 562.5 | 584.3
1181 | 945 | 644.9 | 570.4 | 555 | 562.6 | 587.2
1182 | 946 | 644.3 | 570.4 | 552 | 562.8 | 587
1183 | 947 | 644.3 | 569.6 | 550.6 | 562.8 | 585.9
1184 | 948 | 644.3 | 569 | 550.4 | 562.8 | 584.5
1185 | 949 | 644.4 | 568.8 | 556.7 | 562.8 | 584.2
1186 | 950 | 644.2 | 568.8 | 560.1 | 563 | 584.7
1187 | 951 | 644 | 570 | 558.7 | 563.2 | 586
1188 | 952 | 644.4 | 569.9 | 557.3 | 563.4 | 586
1189 | 953 | 645 | 569.9 | 560.6 | 563.5 | 585.9
1190 | 954 | 645.6 | 570.2 | 564.4 | 563.6 | 585.9
1191 | 955 | 645.4 | 570.2 | 564.3 | 563.7 | 586.3
1192 | 956 | 645.9 | 570.4 | 568.9 | 563.9 | 586.9
1193 | 957 | 645.9 | 570.2 | 571.6 | 564 | 587.4
1194 | 958 | 645.9 | 569.7 | 573.1 | 564.2 | 587.5
1195 | 959 | 646.2 | 569.6 | 573.7 | 564.4 | 587.6
1196 | 960 | 646.4 | 570 | 574.2 | 564.9 | 587.4
1197 | 961 | 646.6 | 570 | 570.6 | 565.6 | 586
1198 | 962 | 647 | 569.1 | 568.5 | 566.5 | 584.5
1199 | 963 | 647.3 | 569.1 | 568 | 567.3 | 584.5
1200 | 964 | 647.3 | 568.7 | 561.1 | 567.8 | 584
1201 | 965 | 647.5 | 568.1 | 558 | 568 | 583.2
1202 | 966 | 648.2 | 568 | 555.1 | 568.3 | 582.8
1203 | 967 | 648.6 | 568.4 | 552.6 | 568.7 | 584.2
1204 | 968 | 648.4 | 567.7 | 548.5 | 568.8 | 582.8
1205 | 969 | 648.6 | 566.7 | 548.3 | 569 | 581.3
1206 | 970 | 648.8 | 566.2 | 548.8 | 569.4 | 581.3
1207 | 971 | 648.3 | 566.6 | 545.4 | 569.5 | 580.3
1208 | 972 | 648.2 | 566.5 | 541.2 | 569.6 | 580.1
1209 | 973 | 648.1 | 566.7 | 541 | 569.7 | 580.6
1210 | 974 | 647.8 | 566.7 | 539.6 | 569.7 | 582.3
1211 | 975 | 647.2 | 566.1 | 537.6 | 569.7 | 582.5
1212 | 976 | 647.1 | 566.2 | 535.4 | 569.8 | 582.2
1213 | 977 | 647.3 | 566.2 | 535.5 | 570 | 582.6
1214 | 978 | 647.4 | 566.1 | 534.5 | 570.1 | 582.8
1215 | 979 | 647.5 | 566.6 | 536 | 570.4 | 582.9
1216 | 980 | 647.5 | 567 | 534.6 | 570.6 | 582.8
1217 | 981 | 647.5 | 566.6 | 535.1 | 570.7 | 582.9
1218 | 982 | 647.7 | 565.9 | 538.3 | 570.9 | 582.5
1219 | 983 | 648 | 565.4 | 545.6 | 571.3 | 582.8
1220 | 984 | 648.7 | 566.5 | 554.1 | 571.7 | 586.7
1221 | 985 | 649.1 | 567.2 | 558.3 | 572.1 | 587.4
1222 | 986 | 649.5 | 567.1 | 563.7 | 572.4 | 586.1
1223 | 987 | 650 | 567.5 | 571 | 572.5 | 587.9
1224 | 988 | 649.6 | 570 | 576.2 | 572.8 | 590.4
1225 | 989 | 649.2 | 570.7 | 576.9 | 573.1 | 589.8
1226 | 990 | 648.3 | 570.6 | 573.4 | 573.6 | 587.3
1227 | 991 | 648.1 | 570.7 | 571.9 | 574.3 | 585.7
1228 | 992 | 648.1 | 570.9 | 571.2 | 574.8 | 584.9
1229 | 993 | 648.3 | 570.2 | 568.5 | 575.3 | 584.3
1230 | 994 | 648.5 | 570.7 | 566.3 | 575.7 | 585
1231 | 995 | 648.7 | 571.2 | 561.5 | 576.1 | 585.5
1232 | 996 | 649.3 | 570.9 | 559.9 | 576.3 | 586.8
1233 | 997 | 649.9 | 570 | 559.7 | 576.6 | 586.3
1234 | 998 | 650 | 570.1 | 559.9 | 577 | 587.1
1235 | 999 | 649.9 | 571 | 554.7 | 577.3 | 586.5
1236 | 1000 | 650.5 | 570.8 | 556.5 | 577.6 | 585.3
1237 | 1001 | 650.9 | 570.6 | 560.7 | 577.8 | 586.7
1238 | 1002 | 651.1 | 570.9 | 561.5 | 578.2 | 587.3
1239 | 1003 | 651.5 | 570.9 | 561.3 | 578.6 | 586.5
1240 | 1004 | 651.7 | 570.6 | 559.9 | 578.8 | 585.6
1241 | 1005 | 651.9 | 570.4 | 558 | 578.9 | 585.5
1242 | 1006 | 652.3 | 570.4 | 555.4 | 579.2 | 586
1243 | 1007 | 652.5 | 570.9 | 555.3 | 579.4 | 586.8
1244 | 1008 | 652.2 | 570.6 | 552.5 | 579.6 | 587
1245 | 1009 | 652.2 | 570.2 | 550.4 | 579.8 | 585.7
1246 | 1010 | 652.4 | 570 | 545.6 | 580 | 584.6
1247 | 1011 | 652.9 | 568.7 | 545.3 | 580.2 | 583.1
1248 | 1012 | 652.8 | 567.6 | 544.2 | 580.4 | 582.5
1249 | 1013 | 653.2 | 567.5 | 543.8 | 580.6 | 581.5
1250 | 1014 | 653.2 | 566.6 | 543 | 580.8 | 580.5
1251 | 1015 | 653 | 565.6 | 540 | 581 | 579.1
1252 | 1016 | 652.8 | 564.5 | 536.1 | 581.3 | 577.9
1253 | 1017 | 653.1 | 563.7 | 535.2 | 581.7 | 577.8
1254 | 1018 | 653.1 | 563.4 | 536.1 | 582 | 577.2
1255 | 1019 | 652.8 | 563 | 533.5 | 582.8 | 577.5
1256 | 1020 | 653 | 563.4 | 532.4 | 583.5 | 577.8
1257 | 1021 | 653.5 | 563.5 | 534.5 | 583.9 | 578
1258 | 1022 | 654 | 564 | 536.6 | 584.2 | 577.8
1259 | 1023 | 654.5 | 563.7 | 538.6 | 584.7 | 577
1260 | 1024 | 654.8 | 564.2 | 542.2 | 585 | 576.8
1261 | 1025 | 655.1 | 565.1 | 543 | 585.1 | 576.4
1262 | 1026 | 655.1 | 566.4 | 542.9 | 585.5 | 577
1263 | 1027 | 654.9 | 567.5 | 539.3 | 586 | 576.7
1264 | 1028 | 654.9 | 566.9 | 535.4 | 586.3 | 575.5
1265 | 1029 | 654.8 | 566.8 | 532.4 | 586.6 | 574.3
1266 | 1030 | 654.6 | 566.2 | 532.6 | 586.7 | 575
1267 | 1031 | 654.5 | 565.5 | 530.8 | 586.8 | 574.7
1268 | 1032 | 654.5 | 565.5 | 531.3 | 586.8 | 575.2
1269 | 1033 | 654.3 | 564.2 | 528.2 | 586.9 | 575.5
1270 | 1034 | 654.4 | 563.4 | 528.6 | 587.2 | 576.1
1271 | 1035 | 654.4 | 562.8 | 531.8 | 587.8 | 576.3
1272 | 1036 | 654.5 | 563.1 | 530.9 | 588.6 | 575.6
1273 | 1037 | 654.3 | 563.4 | 531.9 | 589.2 | 576.4
1274 | 1038 | 654.3 | 564.3 | 531.3 | 589.8 | 577.1
1275 | 1039 | 654.2 | 564.6 | 530.3 | 590.1 | 577.3
1276 | 1040 | 654.1 | 565.2 | 529.7 | 590.4 | 577.6
1277 | 1041 | 653.9 | 565.3 | 528.5 | 590.7 | 578.3
1278 | 1042 | 653.6 | 564.6 | 528 | 590.8 | 576.7
1279 | 1043 | 653.3 | 564.8 | 528.9 | 591 | 577.4
1280 | 1044 | 653.5 | 565.1 | 532.2 | 591.1 | 577.4
1281 | 1045 | 653.5 | 565.5 | 534.5 | 591.2 | 577.9
1282 | 1046 | 653.5 | 565.4 | 534.2 | 591.4 | 578
1283 | 1047 | 653.6 | 565.3 | 536.8 | 591.7 | 579.6
1284 | 1048 | 653.6 | 564.8 | 535.7 | 592 | 578.3
1285 | 1049 | 653.9 | 564.6 | 538.8 | 592.5 | 577.1
1286 | 1050 | 653.9 | 564.8 | 537.6 | 593.1 | 575.9
1287 | 1051 | 653.9 | 564.6 | 536.2 | 593.4 | 574.8
1288 | 1052 | 653.9 | 564.7 | 536.3 | 593.7 | 575.7
1289 | 1053 | 653.7 | 565.6 | 533.2 | 593.9 | 575.8
1290 | 1054 | 653.4 | 566.3 | 529.7 | 594.1 | 576.6
1291 | 1055 | 653.3 | 566.1 | 526.8 | 594.3 | 576.2
1292 | 1056 | 653.3 | 565.9 | 526.1 | 594.4 | 576.3
1293 | 1057 | 653.5 | 566.5 | 527.9 | 594.7 | 578.6
1294 | 1058 | 653.3 | 566.8 | 525.8 | 594.8 | 579.2
1295 | 1059 | 653.3 | 566.6 | 527.1 | 594.9 | 578.7
1296 | 1060 | 653.3 | 567.1 | 529.2 | 595 | 578.8
1297 | 1061 | 653.3 | 567.2 | 531.9 | 595.2 | 578.8
1298 | 1062 | 653.3 | 567.3 | 534.8 | 595.4 | 580
1299 | 1063 | 653.2 | 567.7 | 534.9 | 595.7 | 579.8
1300 | 1064 | 653.5 | 568.1 | 538.2 | 596 | 578.6
1301 | 1065 | 653.7 | 568.3 | 541.5 | 596.3 | 577.9
1302 | 1066 | 653.8 | 568.2 | 542.2 | 596.7 | 577.1
1303 | 1067 | 654.2 | 568.6 | 548.1 | 597.1 | 578.1
1304 | 1068 | 654.4 | 569 | 549.3 | 597.9 | 579.1
1305 | 1069 | 654.5 | 568.6 | 550.4 | 598.4 | 579.8
1306 | 1070 | 654.8 | 569.1 | 554.9 | 598.7 | 579.4
1307 | 1071 | 655.5 | 569.7 | 564 | 599.2 | 580.7
1308 | 1072 | 655.6 | 569.8 | 566 | 599.3 | 580.3
1309 | 1073 | 655.5 | 570.7 | 562.6 | 599.6 | 580
1310 | 1074 | 656 | 570.9 | 563.4 | 599.8 | 579.8
1311 | 1075 | 656.6 | 570.9 | 569.7 | 599.8 | 580.8
1312 | 1076 | 656.5 | 570.6 | 570.4 | 599.8 | 580.3
1313 | 1077 | 656.2 | 569.5 | 566 | 600 | 578.3
1314 | 1078 | 655.7 | 569 | 558.9 | 600.9 | 577
1315 | 1079 | 655.8 | 568.5 | 555.3 | 601.5 | 576.2
1316 | 1080 | 656.8 | 568 | 554.5 | 603.6 | 575.2
1317 | 1081 | 655.9 | 569.8 | 553.6 | 602.9 | 576.2
1318 | 1082 | 656 | 570.8 | 552.8 | 603.1 | 577.2
1319 | 1083 | 655.9 | 571.2 | 549.7 | 603.3 | 577.9
1320 | 1084 | 655.5 | 570.7 | 546.9 | 603.5 | 578.5
1321 | 1085 | 655.7 | 569.6 | 547.3 | 603.6 | 577.9
1322 | 1086 | 656.3 | 568.7 | 553.6 | 603.8 | 577.4
1323 | 1087 | 656.9 | 567.8 | 563.1 | 604.1 | 577.7
1324 | 1088 | 657.1 | 567.5 | 564.3 | 604.3 | 578.7
1325 | 1089 | 656.5 | 568.5 | 560.7 | 604.7 | 580.4
1326 | 1090 | 656.4 | 568.3 | 557.5 | 605.2 | 580.6
1327 | 1091 | 656.3 | 568 | 558.4 | 605.4 | 580.9
1328 | 1092 | 656 | 567.5 | 555.7 | 605.7 | 581
1329 | 1093 | 655.8 | 568.1 | 551.1 | 606 | 579.8
1330 | 1094 | 655.4 | 568.3 | 547.6 | 606.1 | 578
1331 | 1095 | 654.9 | 567.8 | 542.8 | 606.4 | 577.2
1332 | 1096 | 654.7 | 568.2 | 540.8 | 606.5 | 577.1
1333 | 1097 | 654.5 | 568.6 | 538.8 | 606.7 | 577.3
1334 | 1098 | 654.5 | 568.5 | 538.2 | 606.8 | 577.4
1335 | 1099 | 654.6 | 569.4 | 540 | 607.1 | 579.4
1336 | 1100 | 654.5 | 570.3 | 538.7 | 607.3 | 581.2
1337 | 1101 | 654.2 | 569.7 | 536.8 | 607.4 | 580.6
1338 | 1102 | 654.1 | 569.7 | 537.1 | 607.6 | 580.6
1339 | 1103 | 654.1 | 568.6 | 537.7 | 607.8 | 578.8
1340 | 1104 | 654.3 | 568.1 | 539.6 | 607.9 | 577.9
1341 | 1105 | 654.5 | 568.5 | 542.9 | 608.3 | 578.7
1342 | 1106 | 654.6 | 568.7 | 542.1 | 608.6 | 579.3
1343 | 1107 | 654.7 | 568.5 | 542.4 | 608.8 | 579.2
1344 | 1108 | 654.6 | 568.6 | 541.9 | 608.9 | 580.5
1345 | 1109 | 654.5 | 567.9 | 541.4 | 608.9 | 579.9
1346 | 1110 | 654.3 | 567.7 | 540.9 | 609 | 578.1
1347 | 1111 | 654.3 | 566.7 | 543.3 | 609.2 | 577.2
1348 | 1112 | 654.2 | 565.9 | 544.3 | 609.8 | 577.1
1349 | 1113 | 654.4 | 565.7 | 544.5 | 610.4 | 576.4
1350 | 1114 | 654.7 | 565.3 | 544.2 | 610.7 | 576.3
1351 | 1115 | 655.1 | 565.1 | 545.5 | 611.1 | 576.1
1352 | 1116 | 655.3 | 564.4 | 551.6 | 611.9 | 575.8
1353 | 1117 | 655.8 | 565.6 | 558.5 | 612.1 | 577
1354 | 1118 | 655.7 | 566.4 | 556.6 | 612.1 | 578
1355 | 1119 | 655.7 | 565.8 | 555.4 | 612.3 | 576.7
1356 | 1120 | 656.2 | 565.6 | 561.4 | 612.9 | 578.7
1357 | 1121 | 656.3 | 567.1 | 564.5 | 613.6 | 580.4
1358 | 1122 | 656.5 | 567.2 | 566.1 | 613.7 | 580.2
1359 | 1123 | 656.7 | 567.2 | 563.1 | 613.9 | 580.1
1360 | 1124 | 656.8 | 567.7 | 558.9 | 614 | 579.8
1361 | 1125 | 656.8 | 567.3 | 555.9 | 614.1 | 578.4
1362 | 1126 | 657.2 | 567.1 | 556.8 | 614.1 | 577.3
1363 | 1127 | 657.3 | 566.8 | 556.4 | 614.1 | 578.4
1364 | 1128 | 657.4 | 566.4 | 552.5 | 614.2 | 580.4
1365 | 1129 | 657.2 | 567 | 550.7 | 614.2 | 580.9
1366 | 1130 | 657.3 | 567.9 | 550.8 | 614.5 | 581.6
1367 | 1131 | 657.3 | 568.4 | 549 | 614.7 | 582.8
1368 | 1132 | 657.6 | 568.2 | 553.3 | 614.8 | 584.1
1369 | 1133 | 657.6 | 568 | 558.4 | 615 | 584.1
1370 | 1134 | 657.5 | 568.4 | 560.8 | 615.1 | 583.7
1371 | 1135 | 657.2 | 568.4 | 555.7 | 615.3 | 583.2
1372 | 1136 | 657.2 | 569 | 554.5 | 615.5 | 582.8
1373 | 1137 | 657.1 | 567.9 | 553.4 | 615.9 | 581.7
1374 | 1138 | 657.2 | 567.5 | 554.9 | 616 | 581.8
1375 | 1139 | 657.3 | 567.7 | 560.6 | 616.1 | 583.3
1376 | 1140 | 657.6 | 568 | 565.7 | 616.3 | 584.1
1377 | 1141 | 658.1 | 568.3 | 573.6 | 616.5 | 584.8
1378 | 1142 | 658.1 | 568.5 | 578.7 | 616.7 | 585.4
1379 | 1143 | 657.3 | 568.4 | 573.5 | 617.1 | 584.4
1380 | 1144 | 657 | 568.8 | 569.8 | 617.3 | 584
1381 | 1145 | 656.6 | 568.7 | 567 | 617.5 | 583.8
1382 | 1146 | 656.4 | 568.5 | 563.6 | 617.7 | 583.1
1383 | 1147 | 656.3 | 567.8 | 560.7 | 617.7 | 582.5
1384 | 1148 | 656.5 | 567.3 | 561.2 | 617.8 | 583
1385 | 1149 | 656.8 | 567.4 | 566.7 | 617.8 | 582.9
1386 | 1150 | 657 | 567.6 | 574.3 | 617.9 | 582.7
1387 | 1151 | 657.7 | 568 | 584.2 | 618 | 583.2
1388 | 1152 | 658 | 568.2 | 586.8 | 618.2 | 583.6
1389 | 1153 | 657.8 | 568.4 | 583.3 | 618.5 | 583.4
1390 | 1154 | 657.5 | 568.4 | 580 | 618.8 | 583.7
1391 | 1155 | 657.2 | 568.2 | 573.5 | 619.2 | 584.6
1392 | 1156 | 656.8 | 567.7 | 569.8 | 619.3 | 584.8
1393 | 1157 | 656.9 | 567.7 | 570.1 | 619.4 | 585.3
1394 | 1158 | 656.6 | 568 | 564.6 | 619.4 | 584.4
1395 | 1159 | 656.6 | 566.8 | 562.6 | 619.5 | 583.3
1396 | 1160 | 656.6 | 567 | 561.2 | 619.5 | 582.4
1397 | 1161 | 656.6 | 566.7 | 560.5 | 619.5 | 581.4
1398 | 1162 | 656.8 | 565.5 | 561.5 | 619.8 | 580.6
1399 | 1163 | 656.6 | 565.4 | 560.4 | 620.2 | 580.8
1400 | 1164 | 656.5 | 565.6 | 558.9 | 620.5 | 579.5
1401 | 1165 | 656.9 | 566.1 | 561.3 | 621 | 578.9
1402 | 1166 | 657.2 | 566.5 | 564.5 | 621.4 | 578.4
1403 | 1167 | 657.4 | 566.9 | 563.7 | 621.5 | 577.6
1404 | 1168 | 657.5 | 566.9 | 563.6 | 621.6 | 576.9
1405 | 1169 | 657.4 | 566.9 | 564.4 | 621.7 | 577.9
1406 | 1170 | 657.2 | 567.2 | 564.7 | 621.6 | 578.1
1407 | 1171 | 657.6 | 567.1 | 567.3 | 621.8 | 578.5
1408 | 1172 | 658.5 | 567.6 | 577.2 | 622.1 | 581
1409 | 1173 | 658.4 | 568 | 579 | 622.1 | 581.7
1410 | 1174 | 657.9 | 567.9 | 576.3 | 622.2 | 580.8
1411 | 1175 | 657.3 | 568 | 570.4 | 622.1 | 580.3
1412 | 1176 | 657.1 | 567.8 | 563.3 | 622.1 | 579.6
1413 | 1177 | 656.8 | 566.7 | 561.4 | 622 | 579
1414 | 1178 | 656.2 | 566.5 | 559.5 | 622 | 579.5
1415 | 1179 | 656.2 | 566.7 | 557.7 | 622 | 579.8
1416 | 1180 | 655.9 | 566.5 | 556.5 | 621.9 | 579.9
1417 | 1181 | 655.8 | 565.9 | 555.8 | 621.9 | 579.6
1418 | 1182 | 655.8 | 565.1 | 556.3 | 622 | 578.9
1419 | 1183 | 656.1 | 565.3 | 558.7 | 622 | 579
1420 | 1184 | 656.1 | 565.7 | 558.9 | 622.1 | 579.9
1421 | 1185 | 655.9 | 565.1 | 556.5 | 622.1 | 579.1
1422 | 1186 | 655.5 | 564.2 | 552.8 | 622 | 578.3
1423 | 1187 | 655.5 | 563.8 | 550.7 | 622.2 | 578.1
1424 | 1188 | 655.4 | 563.4 | 549.4 | 622.3 | 577.8
1425 | 1189 | 655.4 | 562.9 | 548.1 | 622.5 | 577.5
1426 | 1190 | 655.4 | 563.8 | 547.6 | 622.6 | 579.8
1427 | 1191 | 655.4 | 565 | 546.1 | 622.8 | 580.9
1428 | 1192 | 655.3 | 565.8 | 544.3 | 622.7 | 580.8
1429 | 1193 | 654.8 | 565.5 | 541.7 | 622.6 | 580.7
1430 | 1194 | 654.5 | 565.5 | 542.6 | 622.7 | 581.4
1431 | 1195 | 654.2 | 564.7 | 539.6 | 622.6 | 580.1
1432 | 1196 | 654 | 564.3 | 541 | 622.4 | 579.9
1433 | 1197 | 653.9 | 563.6 | 542.5 | 622.4 | 579.2
1434 | 1198 | 654.1 | 563.8 | 545.7 | 622.6 | 578.5
1435 | 1199 | 654 | 564 | 546.9 | 622.9 | 577.7
1436 | 1200 | 654.1 | 563.1 | 547.5 | 623.4 | 577.2
1437 | 1201 | 654.3 | 563.7 | 551.3 | 623.7 | 578.5
1438 | 1202 | 653.9 | 563.5 | 548 | 623.9 | 578.4
1439 | 1203 | 654.2 | 563.6 | 549.6 | 624.1 | 578.6
1440 | 1204 | 654.1 | 563.9 | 552.7 | 624.6 | 578.2
1441 | 1205 | 653.9 | 563.6 | 553.6 | 625 | 577.7
1442 | 1206 | 653.3 | 563.8 | 553 | 625.4 | 576.9
1443 | 1207 | 653 | 562.8 | 551.3 | 625.3 | 576.1
1444 | 1208 | 653 | 562.6 | 551.2 | 625.4 | 576.1
1445 | 1209 | 652.9 | 563 | 551.8 | 625.3 | 577.4
1446 | 1210 | 652.7 | 563.2 | 549.1 | 625.2 | 578.4
1447 | 1211 | 652.6 | 562.7 | 549.2 | 625.1 | 578.8
1448 | 1212 | 652.6 | 562.7 | 549.7 | 625.1 | 578.8
1449 | 1213 | 652.9 | 562.9 | 551.9 | 625 | 578.1
1450 | 1214 | 653.3 | 563.4 | 555.7 | 625 | 578.4
1451 | 1215 | 653.6 | 563.3 | 558.8 | 625.3 | 579.2
1452 | 1216 | 653 | 564 | 560.1 | 625.4 | 580.8
1453 | 1217 | 653 | 565 | 559.8 | 625.6 | 581.2
1454 | 1218 | 652.6 | 565.4 | 556.7 | 625.7 | 581.6
1455 | 1219 | 652.5 | 564.9 | 554.1 | 625.8 | 579.4
1456 | 1220 | 652.5 | 564.7 | 554 | 625.8 | 579
1457 | 1221 | 652.1 | 564.6 | 550.5 | 625.8 | 578.1
1458 | 1222 | 652 | 564.6 | 546.2 | 625.8 | 578
1459 | 1223 | 652.2 | 564.5 | 544.5 | 625.8 | 576.9
1460 | 1224 | 652.2 | 563.8 | 544.6 | 625.8 | 575.8
1461 | 1225 | 651.9 | 563.1 | 543.1 | 625.8 | 574.8
1462 | 1226 | 651.8 | 563.2 | 542.1 | 626 | 574.9
1463 | 1227 | 652.3 | 563.6 | 542.2 | 626.1 | 578.9
1464 | 1228 | 652.6 | 564.2 | 545.6 | 626 | 582
1465 | 1229 | 652.5 | 564.7 | 544.8 | 626 | 582.4
1466 | 1230 | 652.4 | 564.3 | 543.1 | 626 | 581.3
1467 | 1231 | 652.5 | 564.2 | 543.3 | 625.9 | 580.8
1468 | 1232 | 652.3 | 563.8 | 542 | 625.8 | 579.7
1469 | 1233 | 652.3 | 563.6 | 542.6 | 626 | 579.2
1470 | 1234 | 652.3 | 563.6 | 545.4 | 625.9 | 580.2
1471 | 1235 | 652.2 | 562.5 | 543.1 | 626.1 | 579.3
1472 | 1236 | 652.1 | 562.2 | 542.5 | 626.4 | 578.7
1473 | 1237 | 652.1 | 561.8 | 543.7 | 626.7 | 578.8
1474 | 1238 | 651.8 | 561 | 543.3 | 626.7 | 577.3
1475 | 1239 | 651.3 | 560.4 | 541.1 | 626.6 | 576.2
1476 | 1240 | 651.2 | 560.2 | 539.5 | 626.6 | 575.7
1477 | 1241 | 651.1 | 559.7 | 538.5 | 626.4 | 576.1
1478 | 1242 | 651 | 559.3 | 539.3 | 626.3 | 576.2
1479 | 1243 | 651.4 | 559.5 | 542.9 | 626.2 | 576.1
1480 | 1244 | 651.6 | 560 | 545.5 | 626.3 | 577.6
1481 | 1245 | 651.4 | 560.1 | 544 | 626.3 | 577.6
1482 | 1246 | 651.5 | 559.3 | 544 | 626.3 | 577.7
1483 | 1247 | 651.9 | 559.6 | 547.7 | 626.2 | 578.9
1484 | 1248 | 652 | 560.7 | 549.6 | 626.2 | 581.5
1485 | 1249 | 652 | 561.2 | 550.2 | 626.1 | 582.1
1486 | 1250 | 651.7 | 562 | 548.7 | 626.2 | 582
1487 | 1251 | 651.8 | 562.1 | 549.4 | 626.3 | 582.1
1488 | 1252 | 652.1 | 561.9 | 551.8 | 626.4 | 582
1489 | 1253 | 652.7 | 562.1 | 554.8 | 626.4 | 581.2
1490 | 1254 | 652.7 | 562 | 559.9 | 626.6 | 580.2
1491 | 1255 | 653 | 562.5 | 563.4 | 626.7 | 580
1492 | 1256 | 652.8 | 562 | 562.2 | 626.8 | 579.4
1493 | 1257 | 652.8 | 561.8 | 563.9 | 626.9 | 579.1
1494 | 1258 | 653.1 | 562.7 | 564.5 | 627 | 580.4
1495 | 1259 | 653.3 | 562.8 | 563 | 627 | 580.9
1496 | 1260 | 653.2 | 562.9 | 564.2 | 627.2 | 582.2
1497 | 1261 | 653.2 | 563.2 | 565 | 627.3 | 583.9
1498 | 1262 | 653.3 | 562.7 | 562.9 | 627.3 | 582.6
1499 | 1263 | 653.4 | 562.3 | 563.9 | 627.5 | 581.6
1500 | 1264 | 653.1 | 563.5 | 561.9 | 627.7 | 582.7
1501 | 1265 | 652.7 | 563.5 | 557.8 | 627.7 | 582.2
1502 | 1266 | 652.6 | 562.5 | 557.3 | 627.7 | 580.8
1503 | 1267 | 652 | 561.9 | 553.1 | 627.8 | 579.3
1504 | 1268 | 651.6 | 560.8 | 547.9 | 627.7 | 577.3
1505 | 1269 | 651.3 | 560.7 | 545.7 | 627.5 | 576.7
1506 | 1270 | 650.9 | 562.1 | 545 | 627.2 | 578.8
1507 | 1271 | 650.6 | 562.6 | 543.5 | 627 | 579.9
1508 | 1272 | 650.1 | 561.5 | 542.1 | 626.7 | 578.2
1509 | 1273 | 650.3 | 560.4 | 546.6 | 626.4 | 578.1
1510 | 1274 | 650.3 | 560 | 547.4 | 626.3 | 577.7
1511 | 1275 | 650.3 | 559.7 | 548 | 626.3 | 577.3
1512 | 1276 | 650.3 | 559.2 | 548 | 626.1 | 576.8
1513 | 1277 | 650.6 | 559.2 | 549.1 | 626.2 | 577
1514 | 1278 | 650.7 | 559.5 | 551.1 | 626.3 | 578
1515 | 1279 | 651 | 560.3 | 552.6 | 626.4 | 580.2
1516 | 1280 | 650.7 | 561.1 | 550.3 | 626.6 | 581.4
1517 | 1281 | 650.4 | 560.8 | 547.2 | 626.5 | 581.3
1518 | 1282 | 650.1 | 560.4 | 545.8 | 626.3 | 580.7
1519 | 1283 | 649.9 | 560.3 | 546.8 | 626 | 581.2
1520 | 1284 | 649.7 | 560.8 | 547.7 | 626 | 580.9
1521 | 1285 | 649.7 | 561.3 | 545.5 | 626.1 | 581.6
1522 | 1286 | 649.2 | 561.4 | 543.3 | 626.1 | 581
1523 | 1287 | 649.4 | 560.9 | 546.6 | 625.9 | 580.3
1524 | 1288 | 649.7 | 561 | 552.1 | 625.6 | 580
1525 | 1289 | 650.1 | 561.2 | 558 | 625.5 | 581.2
1526 | 1290 | 649.7 | 562.8 | 557.6 | 625.6 | 582.5
1527 | 1291 | 649.5 | 562.6 | 554.9 | 625.5 | 581.9
1528 | 1292 | 649.4 | 561.9 | 552 | 625.5 | 581.1
1529 | 1293 | 649.3 | 561.9 | 551.1 | 625.2 | 581.8
1530 | 1294 | 649.2 | 562.3 | 552.9 | 625.1 | 582.8
1531 | 1295 | 649.1 | 562.4 | 553.4 | 625.1 | 582.9
1532 | 1296 | 648.8 | 561.9 | 552.3 | 624.9 | 581.5
1533 | 1297 | 648.4 | 561.6 | 550.1 | 625 | 580.7
1534 | 1298 | 648.5 | 562 | 548.1 | 625.1 | 581
1535 | 1299 | 648.2 | 563.2 | 545.4 | 625.2 | 581.2
1536 | 1300 | 647.9 | 563 | 543.5 | 625.2 | 580.5
1537 | 1301 | 648 | 562.3 | 542.7 | 625.3 | 581.6
1538 | 1302 | 647.9 | 561.7 | 542.8 | 625.2 | 581.5
1539 | 1303 | 647.9 | 561.6 | 547 | 625 | 582.6
1540 | 1304 | 648 | 561.6 | 550.9 | 625 | 583.4
1541 | 1305 | 648.8 | 561.5 | 560.3 | 625 | 584.5
1542 | 1306 | 649.2 | 561.7 | 565 | 625.2 | 584.3
1543 | 1307 | 648.9 | 561.7 | 563.8 | 625.3 | 582.3
1544 | 1308 | 648.8 | 561.3 | 566.4 | 625.2 | 583
1545 | 1309 | 649.5 | 561.3 | 570.4 | 625.5 | 583.7
1546 | 1310 | 649.6 | 561.9 | 575.8 | 625.6 | 584.1
1547 | 1311 | 649.6 | 561.8 | 576.5 | 625.6 | 583.9
1548 | 1312 | 649.6 | 561.7 | 578.8 | 625.6 | 583.6
1549 | 1313 | 650 | 563.3 | 582.1 | 625.6 | 585.9
1550 | 1314 | 651.2 | 564.7 | 588.3 | 625.7 | 587.9
1551 | 1315 | 651.7 | 565.3 | 589.5 | 625.9 | 587.8
1552 | 1316 | 652.2 | 565.8 | 590.2 | 626.3 | 588.5
1553 | 1317 | 651.7 | 566.5 | 589.8 | 626.5 | 589.5
1554 | 1318 | 650.6 | 567.3 | 581.4 | 626.7 | 588.6
1555 | 1319 | 650 | 566.4 | 575.4 | 626.7 | 585.4
1556 | 1320 | 649.6 | 565.5 | 571.2 | 626.6 | 584.2
1557 | 1321 | 649.8 | 564.5 | 570 | 626.6 | 583.5
1558 | 1322 | 650.1 | 564 | 569.9 | 626.7 | 583.1
1559 | 1323 | 650.8 | 564.7 | 576.2 | 626.7 | 584.1
1560 | 1324 | 651 | 565.8 | 581.2 | 626.9 | 584.7
1561 | 1325 | 650.6 | 565.3 | 579.2 | 627 | 583.9
1562 | 1326 | 649.6 | 565.7 | 574.5 | 627 | 583.4
1563 | 1327 | 649.4 | 565.7 | 572.1 | 627 | 583.2
1564 | 1328 | 649.3 | 565.7 | 570.6 | 627.1 | 584.1
1565 | 1329 | 649 | 565.9 | 567.6 | 627.4 | 586.3
1566 | 1330 | 648.9 | 566 | 564.8 | 627.4 | 587.1
1567 | 1331 | 649 | 566.3 | 561.2 | 627.4 | 586.2
1568 | 1332 | 648.9 | 565.7 | 559.1 | 627.4 | 584.8
1569 | 1333 | 648.8 | 564.9 | 559.2 | 627.3 | 583.9
1570 | 1334 | 649.1 | 564.9 | 560.1 | 627.2 | 583.5
1571 | 1335 | 649.5 | 564.7 | 560.7 | 627.3 | 582.5
1572 | 1336 | 649.8 | 564.2 | 563.1 | 627.6 | 582.7
1573 | 1337 | 649.5 | 565.3 | 566.6 | 628 | 585.7
1574 | 1338 | 648.5 | 565.9 | 566.7 | 628.2 | 586.1
1575 | 1339 | 648.2 | 565.7 | 564.7 | 628.1 | 585.8
1576 | 1340 | 648 | 565.3 | 561.3 | 628 | 585.5
1577 | 1341 | 647.1 | 564.9 | 556.7 | 627.9 | 583.7
1578 | 1342 | 647 | 564.4 | 554.3 | 627.8 | 583.4
1579 | 1343 | 647.1 | 564.4 | 551.9 | 627.6 | 583.4
1580 | 1344 | 646.9 | 564.9 | 549.7 | 627.5 | 583.7
1581 | 1345 | 646.5 | 564.4 | 547.5 | 627.3 | 582.3
1582 | 1346 | 646.2 | 563.3 | 547.4 | 627.1 | 580.2
1583 | 1347 | 646.2 | 562.3 | 549.1 | 627 | 579
1584 | 1348 | 648 | 563 | 563.6 | 627.1 | 581.5
1585 | 1349 | 648.8 | 564.5 | 574.2 | 627.4 | 583.6
1586 | 1350 | 649.4 | 565.1 | 575 | 627.6 | 583.3
1587 | 1351 | 649.4 | 564.8 | 574.3 | 628.1 | 583.1
1588 | 1352 | 648.7 | 565.5 | 573.9 | 628.7 | 583.2
1589 | 1353 | 648.8 | 565.6 | 573.3 | 628.8 | 582.6
1590 | 1354 | 649.3 | 565.8 | 576.1 | 628.8 | 582.6
1591 | 1355 | 649.3 | 566.5 | 575.6 | 628.7 | 583.4
1592 | 1356 | 648 | 567.1 | 570.6 | 628.9 | 583.1
1593 | 1357 | 647.3 | 566.8 | 565.7 | 629 | 582.5
1594 | 1358 | 647.2 | 565.5 | 564 | 629.1 | 581.8
1595 | 1359 | 646.9 | 564.6 | 561.3 | 629.2 | 581.9
1596 | 1360 | 646.8 | 564.4 | 559 | 629.1 | 581.9
1597 | 1361 | 646.5 | 563.8 | 558.7 | 628.7 | 580.2
1598 | 1362 | 646.6 | 563.8 | 559.1 | 628.6 | 578.7
1599 | 1363 | 647 | 563.2 | 558.9 | 629 | 578
1600 | 1364 | 647.4 | 562.8 | 561.9 | 629.4 | 578.2
1601 | 1365 | 647.7 | 563 | 565.7 | 629.6 | 578.7
1602 | 1366 | 647.7 | 563.8 | 569.5 | 629.8 | 579
1603 | 1367 | 648.4 | 563.5 | 570.2 | 629.9 | 579.1
1604 | 1368 | 647.8 | 564.4 | 567.1 | 629.9 | 579.8
1605 | 1369 | 647.7 | 564.3 | 566.9 | 629.6 | 580.2
1606 | 1370 | 647.6 | 564 | 568.4 | 629.5 | 579.7
1607 | 1371 | 647.3 | 564 | 569.6 | 629.2 | 580.1
1608 | 1372 | 647.3 | 564.4 | 568.9 | 629.2 | 581.7
1609 | 1373 | 647.4 | 564.5 | 567.1 | 629.1 | 583
1610 | 1374 | 646.9 | 564.4 | 564.8 | 629 | 583
1611 | 1375 | 647.2 | 564.2 | 568.5 | 628.7 | 582.7
1612 | 1376 | 647.5 | 563.9 | 572.5 | 628.7 | 582.3
1613 | 1377 | 647.9 | 564.2 | 578.4 | 628.7 | 582.1
1614 | 1378 | 648 | 564 | 577.4 | 628.6 | 580.7
1615 | 1379 | 648 | 563.3 | 580.5 | 628.6 | 581.2
1616 | 1380 | 647.9 | 563.2 | 579.9 | 628.7 | 581.5
1617 | 1381 | 646.6 | 563.6 | 580.9 | 628.8 | 581.4
1618 | 1382 | 646.5 | 563.6 | 579.9 | 628.9 | 582.4
1619 | 1383 | 646.7 | 563.4 | 577.7 | 629 | 581.1
1620 | 1384 | 646.7 | 563 | 579.2 | 629 | 579.8
1621 | 1385 | 647.1 | 563.1 | 579.8 | 629 | 578.8
1622 | 1386 | 647.1 | 563.4 | 582.7 | 629.2 | 579.3
1623 | 1387 | 646.9 | 564 | 584.4 | 629.9 | 580.3
1624 | 1388 | 647.7 | 563.9 | 582.4 | 630.4 | 580
1625 | 1389 | 646.9 | 564.1 | 580.5 | 630.7 | 580.5
1626 | 1390 | 645.9 | 565 | 577.1 | 630.8 | 580.4
1627 | 1391 | 645.6 | 564.9 | 571.8 | 630.6 | 579.7
1628 | 1392 | 645.1 | 564.9 | 567.9 | 630.5 | 580.7
1629 | 1393 | 644.7 | 564.6 | 564.2 | 630.2 | 579.5
1630 | 1394 | 644.2 | 563.7 | 562.6 | 629.8 | 578.6
1631 | 1395 | 644.3 | 563.5 | 560.8 | 629.4 | 579
1632 | 1396 | 643.8 | 563.8 | 559.3 | 629.3 | 580.5
1633 | 1397 | 643.6 | 563.4 | 557.9 | 628.9 | 581
1634 | 1398 | 643.5 | 562.8 | 558.7 | 628.6 | 581
1635 | 1399 | 643.5 | 563 | 557.3 | 628.5 | 581.9
1636 | 1400 | 643.3 | 563.2 | 555.7 | 628.2 | 582
1637 | 1401 | 642.9 | 562.9 | 555 | 627.9 | 581.8
1638 | 1402 | 643 | 563.1 | 555.3 | 627.6 | 582.1
1639 | 1403 | 642.9 | 563 | 557.2 | 627.5 | 582.2
1640 | 1404 | 642.9 | 563.9 | 556.6 | 627.6 | 583.6
1641 | 1405 | 643 | 564.2 | 557.1 | 627.5 | 582.4
1642 | 1406 | 642.9 | 563.8 | 559.1 | 627.4 | 581.7
1643 | 1407 | 642.8 | 563.1 | 557.7 | 627.4 | 580.7
1644 | 1408 | 642.7 | 562.5 | 556.1 | 627.3 | 579.5
1645 | 1409 | 642.6 | 561.9 | 555.7 | 627.3 | 577.9
1646 | 1410 | 642.4 | 561.2 | 555.4 | 627.4 | 576.9
1647 | 1411 | 642.2 | 561.1 | 555.7 | 628 | 578
1648 | 1412 | 642.2 | 561.4 | 552.6 | 627.8 | 578.8
1649 | 1413 | 642.5 | 560.9 | 555.4 | 628.2 | 577.8
1650 | 1414 | 643.4 | 561.4 | 559.8 | 628.3 | 578.3
1651 | 1415 | 643.2 | 561 | 560.6 | 628.6 | 577.6
1652 | 1416 | 642.9 | 561.1 | 562.5 | 629.4 | 577.8
1653 | 1417 | 642.9 | 562.8 | 562.6 | 629.1 | 578.8
1654 | 1418 | 642.9 | 563.6 | 561.2 | 629.3 | 578.4
1655 | 1419 | 642.7 | 563.4 | 558.4 | 629.3 | 577.2
1656 | 1420 | 643 | 562.5 | 559.1 | 629.1 | 575.6
1657 | 1421 | 643.3 | 562.4 | 565.9 | 628.9 | 575.8
1658 | 1422 | 643.3 | 562.9 | 568.9 | 628.8 | 575.6
1659 | 1423 | 643.8 | 563 | 566.2 | 628.8 | 575.1
1660 | 1424 | 643.2 | 562.9 | 563.5 | 628.6 | 575
1661 | 1425 | 643.1 | 562.7 | 563 | 629 | 574.7
1662 | 1426 | 643 | 562.3 | 562.1 | 629.3 | 574.5
1663 | 1427 | 642.9 | 563.1 | 562.2 | 629.1 | 576.4
1664 | 1428 | 642.6 | 564.3 | 559.9 | 629.1 | 577.9
1665 | 1429 | 642.6 | 564.2 | 559.8 | 629 | 577.3
1666 | 1430 | 642.5 | 563.6 | 557.8 | 629.1 | 575.9
1667 | 1431 | 642.7 | 562.9 | 560.7 | 629.2 | 576.1
1668 | 1432 | 643.2 | 563 | 564.9 | 629.3 | 577.9
1669 | 1433 | 643.3 | 563.3 | 566.1 | 629.1 | 578.7
1670 | 1434 | 643.8 | 562.8 | 571.1 | 629.1 | 578.4
1671 | 1435 | 644.7 | 563.5 | 578.6 | 629.1 | 579.4
1672 | 1436 | 644.8 | 564.4 | 580 | 629.5 | 579.2
1673 | 1437 | 645 | 564.3 | 579.6 | 629.4 | 578.9
1674 | 1438 | 645 | 563.8 | 579.2 | 629.9 | 578.9
1675 | 1439 | 645.2 | 563.1 | 581.1 | 630 | 578.7
1676 | 1440 | 645.2 | 563.1 | 584.2 | 630.1 | 578
1677 | 1441 | 645.5 | 563.5 | 588.2 | 630.2 | 577.9
1678 | 1442 | 645.8 | 563.7 | 588.7 | 630.2 | 576.8
1679 | 1443 | 646 | 562.9 | 585.8 | 630.3 | 576.1
1680 | 1444 | 645.7 | 563.6 | 583.7 | 630 | 577.4
1681 | 1445 | 645.8 | 563.7 | 582.4 | 630 | 577.6
1682 | 1446 | 645.5 | 563.3 | 579.5 | 629.9 | 577.9
1683 | 1447 | 645.4 | 562.9 | 578.5 | 629.7 | 578.1
1684 | 1448 | 645.4 | 563.5 | 580.5 | 629.5 | 579
1685 | 1449 | 645.4 | 562.7 | 581.5 | 629.7 | 578.5
1686 | 1450 | 645.7 | 561.9 | 584.2 | 629.8 | 579.5
1687 | 1451 | 646.3 | 561.7 | 589.9 | 629.9 | 581.9
1688 | 1452 | 646.3 | 563 | 594.5 | 630 | 582.5
1689 | 1453 | 646.1 | 563 | 593.1 | 629.7 | 581
1690 | 1454 | 645.6 | 562.7 | 589.3 | 629.4 | 579
1691 | 1455 | 645.6 | 562.4 | 588.2 | 629.4 | 577.6
1692 | 1456 | 645.7 | 562.5 | 586.6 | 629.5 | 576.3
1693 | 1457 | 645.7 | 562.1 | 583.1 | 629.6 | 574.7
1694 | 1458 | 645.9 | 562.1 | 580.1 | 629.8 | 573.8
1695 | 1459 | 645.6 | 563 | 578.7 | 629.5 | 573.5
1696 | 1460 | 645 | 563.6 | 576.8 | 629.7 | 574.1
1697 | 1461 | 645.1 | 563.7 | 577 | 629.7 | 575.3
1698 | 1462 | 645.9 | 564.1 | 585.5 | 629.7 | 576.8
1699 | 1463 | 646.4 | 564.4 | 587.1 | 629.8 | 577.3
1700 | 1464 | 646.7 | 564.3 | 589.3 | 629.8 | 576.8
1701 | 1465 | 647.4 | 564.5 | 590.5 | 629.8 | 576.7
1702 | 1466 | 647.5 | 564.4 | 591.8 | 630 | 576
1703 | 1467 | 647.6 | 563.9 | 592.2 | 630 | 576
1704 | 1468 | 647.5 | 564.5 | 592.8 | 630.2 | 577.1
1705 | 1469 | 647.6 | 564.6 | 592.6 | 630.4 | 577.3
1706 | 1470 | 647.8 | 565.6 | 596.1 | 630.8 | 576.9
1707 | 1471 | 648.1 | 565.7 | 598.2 | 630.7 | 576.5
1708 | 1472 | 648 | 565.3 | 596.7 | 630.5 | 576.3
1709 | 1473 | 647.8 | 564 | 593.1 | 630.8 | 575.9
1710 | 1474 | 647.3 | 564 | 592.3 | 631 | 576.8
1711 | 1475 | 646.9 | 564.5 | 588.7 | 631 | 578.3
1712 | 1476 | 646.9 | 564.2 | 588.4 | 630.6 | 578.5
1713 | 1477 | 647 | 564.2 | 589.3 | 630.3 | 578.7
1714 | 1478 | 646.4 | 563.6 | 585.2 | 630.3 | 576.8
1715 | 1479 | 645.7 | 562.1 | 577.5 | 630.1 | 573.7
1716 | 1480 | 645.2 | 561.1 | 575.9 | 629.9 | 571.8
1717 | 1481 | 645.8 | 561.2 | 582 | 630 | 572.7
1718 | 1482 | 645.9 | 561.1 | 580.9 | 629.9 | 573.8
1719 | 1483 | 645.5 | 560.8 | 579.5 | 630.4 | 574.6
1720 | 1484 | 645.3 | 560.6 | 580.5 | 630.4 | 575.8
1721 | 1485 | 645.1 | 560.7 | 579.8 | 630 | 576
1722 | 1486 | 644.8 | 560.2 | 576.8 | 630.1 | 574.7
1723 | 1487 | 644.8 | 559.9 | 578.2 | 630.1 | 574.6
1724 | 1488 | 644.7 | 559.5 | 578.7 | 630 | 575.3
1725 | 1489 | 644.7 | 559.8 | 580 | 630.3 | 575.5
1726 | 1490 | 644.2 | 559.9 | 575.9 | 630.2 | 575.6
1727 | 1491 | 643.7 | 559.3 | 572.5 | 630.2 | 575
1728 | 1492 | 643.3 | 559.3 | 570.2 | 630 | 576.2
1729 | 1493 | 642.8 | 559.3 | 567.8 | 629.7 | 576.5
1730 | 1494 | 642.9 | 558.9 | 570.1 | 629.5 | 576.7
1731 | 1495 | 642.7 | 559.4 | 569.9 | 629.5 | 576.3
1732 | 1496 | 642.5 | 559.2 | 568.4 | 629.3 | 575.9
1733 | 1497 | 642.2 | 558.6 | 567.5 | 629.1 | 574.5
1734 | 1498 | 641.9 | 558.8 | 566.1 | 629 | 573.4
1735 | 1499 | 641.7 | 558.5 | 561.8 | 629 | 572.3
1736 | 1500 | 641.4 | 557.5 | 559.3 | 629.1 | 570.7
1737 | 1501 | 641 | 556.9 | 558.2 | 629.1 | 570
1738 | 1502 | 640.8 | 556.3 | 558.5 | 629.1 | 570.1
1739 | 1503 | 640 | 556 | 554.7 | 629.1 | 569.5
1740 | 1504 | 639.6 | 555.5 | 551.4 | 628.7 | 567.9
1741 | 1505 | 639.2 | 554.8 | 551.4 | 628.7 | 567.1
1742 | 1506 | 639 | 554 | 550.1 | 628.9 | 567.4
1743 | 1507 | 638.8 | 553.9 | 550.8 | 628.7 | 569.6
1744 | 1508 | 638.6 | 554.4 | 551.2 | 628.5 | 571.2
1745 | 1509 | 638.6 | 555.4 | 553.7 | 628.2 | 573
1746 | 1510 | 638.3 | 556.8 | 553 | 628 | 573.5
1747 | 1511 | 638.6 | 556.1 | 558.1 | 627.9 | 573.9
1748 | 1512 | 638.9 | 555.9 | 560.7 | 628.2 | 573.9
1749 | 1513 | 639 | 556.3 | 562.1 | 628.4 | 573.3
1750 | 1514 | 639 | 556.3 | 562.5 | 628.5 | 571.8
1751 | 1515 | 638.7 | 556.1 | 560.8 | 628.8 | 570.6
1752 | 1516 | 638.7 | 555.7 | 561.9 | 629.2 | 569.8
1753 | 1517 | 638.5 | 555.4 | 561.4 | 628.9 | 568.7
1754 | 1518 | 638.3 | 555.1 | 558.5 | 628.8 | 566.8
1755 | 1519 | 637.8 | 554.8 | 554.5 | 628.6 | 565
1756 | 1520 | 637.6 | 554 | 553.1 | 628.8 | 564.9
1757 | 1521 | 637.3 | 554.3 | 552.9 | 628.9 | 567.3
1758 | 1522 | 637.2 | 555.4 | 551.6 | 628.6 | 569.2
1759 | 1523 | 637 | 556.2 | 551.5 | 628.3 | 569.6
1760 | 1524 | 636.7 | 556.6 | 548.8 | 628.1 | 569
1761 | 1525 | 636.5 | 555.3 | 547.5 | 627.7 | 567.4
1762 | 1526 | 636.1 | 554.4 | 546.6 | 627.5 | 565.9
1763 | 1527 | 635.8 | 554.3 | 545.9 | 627.3 | 565.4
1764 | 1528 | 635.9 | 554.3 | 547 | 627.2 | 566
1765 | 1529 | 636.3 | 554.8 | 549.5 | 627.1 | 566.2
1766 | 1530 | 636.4 | 555 | 548.7 | 626.9 | 565.2
1767 | 1531 | 636.4 | 554.3 | 548.6 | 626.8 | 563.9
1768 | 1532 | 636.1 | 553.5 | 548 | 626.8 | 563.5
1769 | 1533 | 636 | 554.1 | 551.4 | 626.8 | 564.5
1770 | 1534 | 636.2 | 554.1 | 554 | 627.2 | 565.9
1771 | 1535 | 636.3 | 554.6 | 555.6 | 627.5 | 566.3
1772 | 1536 | 636.3 | 555 | 555.9 | 627.5 | 567.2
1773 | 1537 | 636 | 556 | 554.3 | 627.3 | 567.3
1774 | 1538 | 635.6 | 556.4 | 551.8 | 627.1 | 567
1775 | 1539 | 635.8 | 555.3 | 554.3 | 627.1 | 565.7
1776 | 1540 | 636.8 | 555 | 566.2 | 627.5 | 567
1777 | 1541 | 637.5 | 556.1 | 573 | 627.4 | 568.7
1778 | 1542 | 637.8 | 556.8 | 571.6 | 627.4 | 567.5
1779 | 1543 | 638.3 | 557.4 | 574.2 | 627.4 | 566.2
1780 | 1544 | 638.9 | 558 | 580.4 | 627.5 | 566.9
1781 | 1545 | 638.9 | 558.5 | 578.8 | 627.5 | 567.8
1782 | 1546 | 638.6 | 558.6 | 577 | 627.5 | 567.5
1783 | 1547 | 638.7 | 558.2 | 576.1 | 627.4 | 566.8
1784 | 1548 | 638.6 | 557.8 | 574.9 | 627.7 | 566.4
1785 | 1549 | 638.5 | 558 | 573.5 | 627.6 | 566.9
1786 | 1550 | 638.6 | 558.8 | 573.1 | 627.3 | 568
1787 | 1551 | 638.4 | 559 | 570.6 | 627.2 | 568.5
1788 | 1552 | 638 | 558.5 | 567.4 | 627.5 | 568.3
1789 | 1553 | 637.9 | 557.8 | 565.8 | 627.4 | 567.4
1790 | 1554 | 637.6 | 557.2 | 565.2 | 627.2 | 567.2
1791 | 1555 | 637.4 | 557.1 | 564.3 | 627 | 567.5
1792 | 1556 | 637.2 | 557.2 | 560.8 | 627 | 567.1
1793 | 1557 | 637.1 | 557 | 560 | 626.8 | 567.5
1794 | 1558 | 637.1 | 557.2 | 561.6 | 626.7 | 568.4
1795 | 1559 | 637.1 | 557.4 | 561.9 | 627.1 | 568.4
1796 | 1560 | 636.9 | 557.2 | 561.3 | 627.2 | 568.8
1797 | 1561 | 636.6 | 557.2 | 558.7 | 627.2 | 570.2
1798 | 1562 | 636.4 | 557 | 557.5 | 627.2 | 569.5
1799 | 1563 | 636.3 | 556.9 | 555.7 | 627.2 | 568.6
1800 | 1564 | 636 | 557.1 | 553.2 | 627.1 | 568.7
1801 | 1565 | 635.7 | 557 | 549.3 | 627 | 567.8
1802 | 1566 | 635.5 | 556.2 | 549.3 | 627 | 565.7
1803 | 1567 | 635.5 | 555.7 | 550.7 | 627.2 | 564.4
1804 | 1568 | 635.8 | 555 | 553.7 | 627.4 | 564.4
1805 | 1569 | 635.8 | 555 | 554.5 | 628 | 564.9
1806 | 1570 | 635.9 | 555.4 | 557.3 | 628 | 565.6
1807 | 1571 | 635.9 | 556.2 | 559.5 | 628 | 567.1
1808 | 1572 | 636 | 556.3 | 559.6 | 627.7 | 567.9
1809 | 1573 | 635.9 | 556 | 559.3 | 627.7 | 567.8
1810 | 1574 | 635.6 | 555.5 | 558.1 | 627.7 | 567.6
1811 | 1575 | 635.6 | 555.5 | 557.4 | 627.5 | 567.9
1812 | 1576 | 635.4 | 555.9 | 554.5 | 627.4 | 568.1
1813 | 1577 | 635 | 555.3 | 551.4 | 627.2 | 566.9
1814 | 1578 | 634.7 | 554.2 | 549.9 | 627.4 | 566.3
1815 | 1579 | 634.4 | 553.2 | 549.6 | 627.5 | 566.4
1816 | 1580 | 633.9 | 553.4 | 547.5 | 627.5 | 565.6
1817 | 1581 | 633.6 | 553.8 | 546.5 | 627.7 | 565.8
1818 | 1582 | 633.3 | 554.1 | 544.9 | 627.3 | 564.8
1819 | 1583 | 633 | 554.1 | 543.8 | 627.2 | 564.5
1820 | 1584 | 632.7 | 554.7 | 540.6 | 627.2 | 564.7
1821 | 1585 | 632.3 | 554.1 | 538.6 | 627 | 564.6
1822 | 1586 | 632.1 | 553.6 | 538.8 | 627.2 | 564.2
1823 | 1587 | 631.8 | 553.1 | 539.6 | 627 | 562.9
1824 | 1588 | 632 | 553.2 | 543.7 | 627.1 | 562.5
1825 | 1589 | 632 | 553.4 | 544.6 | 627.8 | 561.6
1826 | 1590 | 631.9 | 552.6 | 545 | 627.9 | 560.7
1827 | 1591 | 631.9 | 553.1 | 545.2 | 628.5 | 560.5
1828 | 1592 | 631.6 | 553.1 | 543.7 | 629.1 | 560.7
1829 | 1593 | 631.1 | 552.8 | 541.3 | 628.9 | 561.2
1830 | 1594 | 630.7 | 552.4 | 540.4 | 628.8 | 560
1831 | 1595 | 631.1 | 552.3 | 544 | 628.8 | 559.3
1832 | 1596 | 631.1 | 552.6 | 544.9 | 629.2 | 558.9
1833 | 1597 | 630.9 | 552.8 | 545.1 | 629.7 | 559
1834 | 1598 | 631.1 | 553.3 | 548.8 | 629.4 | 560.2
1835 | 1599 | 631.2 | 553.2 | 549 | 629 | 561.3
1836 | 1600 | 631.4 | 553.3 | 549.6 | 629 | 561.2
1837 | 1601 | 631.4 | 552.8 | 550.1 | 629.2 | 560
1838 | 1602 | 631.1 | 552.4 | 548 | 629.5 | 559.1
1839 | 1603 | 631.1 | 551.9 | 547.6 | 629.7 | 558.6
1840 | 1604 | 631.4 | 552.2 | 549.4 | 629.6 | 559.2
1841 | 1605 | 631.5 | 552.2 | 550 | 629.2 | 560.4
1842 | 1606 | 631.3 | 551.9 | 548.3 | 628.9 | 559.8
1843 | 1607 | 631.1 | 550.9 | 548.9 | 628.5 | 559.6
1844 | 1608 | 631.3 | 551.1 | 555.7 | 628.7 | 560.7
1845 | 1609 | 631.7 | 551.4 | 561.7 | 628.5 | 561.8
1846 | 1610 | 631.6 | 552.5 | 561.7 | 628.8 | 563
1847 | 1611 | 631.1 | 552.9 | 560.2 | 629.1 | 562.3
1848 | 1612 | 631.3 | 552.9 | 562.1 | 629.3 | 561.9
1849 | 1613 | 631.2 | 553.3 | 561 | 629.1 | 561.4
1850 | 1614 | 631 | 553.1 | 560.2 | 629.3 | 561.6
1851 | 1615 | 631.1 | 552.6 | 561.5 | 629 | 560.6
1852 | 1616 | 631.8 | 552.9 | 566.4 | 629.1 | 560.9
1853 | 1617 | 632.1 | 553 | 569.6 | 628.9 | 561.5
1854 | 1618 | 632 | 553.2 | 566.9 | 628.5 | 562.6
1855 | 1619 | 631.8 | 554.5 | 563.8 | 628.4 | 562.9
1856 | 1620 | 631.7 | 554 | 561.2 | 628.3 | 561.9
1857 | 1621 | 631.9 | 553.8 | 563.1 | 628.2 | 562.1
1858 | 1622 | 632.8 | 554.9 | 571.1 | 628.1 | 562.9
1859 | 1623 | 632.9 | 555.5 | 569.6 | 628.3 | 562.4
1860 | 1624 | 632.8 | 555.5 | 567.1 | 628.2 | 561.3
1861 | 1625 | 632.7 | 555.4 | 566.8 | 628.2 | 560.4
1862 | 1626 | 632.8 | 554.9 | 568.3 | 628.4 | 560.5
1863 | 1627 | 633.3 | 555.3 | 573.9 | 628.1 | 562.4
1864 | 1628 | 633.4 | 555.6 | 574.4 | 627.9 | 563.9
1865 | 1629 | 633.2 | 555.6 | 571.8 | 627.8 | 563.7
1866 | 1630 | 633.1 | 555.9 | 570.3 | 628 | 563.1
1867 | 1631 | 632.9 | 555.7 | 569 | 628.2 | 561.9
1868 | 1632 | 632.8 | 555.2 | 569 | 628.3 | 561.4
1869 | 1633 | 632.3 | 555 | 565.7 | 628.7 | 561.5
1870 | 1634 | 632.3 | 554.3 | 565.7 | 628.6 | 561.5
1871 | 1635 | 632.4 | 555 | 568.5 | 628.4 | 563.3
1872 | 1636 | 632.1 | 555.8 | 566.1 | 628.3 | 563.7
1873 | 1637 | 632 | 556.1 | 563.4 | 628.3 | 563.2
1874 | 1638 | 631.6 | 555.3 | 558.8 | 628.2 | 561.7
1875 | 1639 | 631.5 | 553.3 | 556.2 | 628.1 | 559.8
1876 | 1640 | 631.4 | 552.7 | 556.2 | 628.3 | 559.7
1877 | 1641 | 631.3 | 553.5 | 555.6 | 628.4 | 561.2
1878 | 1642 | 631.1 | 554.1 | 553.6 | 627.9 | 562.3
1879 | 1643 | 630.6 | 553.7 | 548.6 | 627.6 | 560.5
1880 | 1644 | 630.5 | 552.1 | 550.8 | 627.2 | 558.6
1881 | 1645 | 630.7 | 551.4 | 554.4 | 627.4 | 558.4
1882 | 1646 | 630.7 | 551.3 | 554.5 | 627.3 | 557.6
1883 | 1647 | 630.5 | 550.8 | 552.8 | 627.1 | 556.5
1884 | 1648 | 630.2 | 550.7 | 550.1 | 627.2 | 555.5
1885 | 1649 | 629.7 | 549.8 | 546 | 627.3 | 554.1
1886 | 1650 | 629.2 | 548.6 | 542.4 | 627.2 | 552.9
1887 | 1651 | 629.2 | 548.2 | 541.5 | 627.4 | 553.1
1888 | 1652 | 629.2 | 548.4 | 546.9 | 627.6 | 554.5
1889 | 1653 | 629.4 | 547.9 | 546.9 | 627.7 | 555.4
1890 | 1654 | 629.4 | 548.9 | 546.4 | 628 | 556.1
1891 | 1655 | 629.4 | 549.8 | 546.2 | 628.1 | 557.3
1892 | 1656 | 629.3 | 550.8 | 543.8 | 628.3 | 558
1893 | 1657 | 629 | 551.1 | 542.1 | 628.2 | 557.5
1894 | 1658 | 628.8 | 551.1 | 542 | 628.1 | 557.8
1895 | 1659 | 628.7 | 550.6 | 542.6 | 627.8 | 556.4
1896 | 1660 | 629 | 550 | 545.8 | 627.3 | 555.6
1897 | 1661 | 629 | 549.4 | 547.3 | 627.5 | 554.6
1898 | 1662 | 628.9 | 548.9 | 546.2 | 627.3 | 553.5
1899 | 1663 | 629 | 548.3 | 546 | 627.8 | 553.2
1900 | 1664 | 628.6 | 548.2 | 544.2 | 628.3 | 553.2
1901 | 1665 | 628.2 | 548.9 | 541.8 | 628.3 | 555
1902 | 1666 | 627.7 | 548.1 | 538.9 | 628.2 | 554.2
1903 | 1667 | 627.5 | 547.4 | 538.9 | 628.1 | 552.5
1904 | 1668 | 627.1 | 546.4 | 536.8 | 628.1 | 551.1
1905 | 1669 | 627.3 | 545.9 | 537.9 | 628 | 550.7
1906 | 1670 | 627.3 | 546.2 | 540.7 | 628.1 | 551.1
1907 | 1671 | 627.4 | 546.3 | 541.4 | 628.4 | 550.9
1908 | 1672 | 627.4 | 546.5 | 544.4 | 628.2 | 551
1909 | 1673 | 627.7 | 547 | 546.9 | 628.5 | 551.6
1910 | 1674 | 628.1 | 548.6 | 554.1 | 628.5 | 553.2
1911 | 1675 | 628.4 | 549.3 | 556.8 | 628.4 | 554.8
1912 | 1676 | 628.9 | 549.4 | 561.3 | 628.6 | 555.4
1913 | 1677 | 628.8 | 549.3 | 560 | 628.8 | 555.7
1914 | 1678 | 628.9 | 549.4 | 561.5 | 628.8 | 555.6
1915 | 1679 | 629 | 550 | 563 | 629.1 | 555.1
1916 | 1680 | 628.8 | 549.5 | 560.3 | 628.9 | 554.1
1917 | 1681 | 628.4 | 549.8 | 558.3 | 628.5 | 553.6
1918 | 1682 | 628.1 | 548.9 | 557.6 | 628.5 | 552.7
1919 | 1683 | 627.8 | 548.3 | 555.7 | 628.2 | 552.4
1920 | 1684 | 627.4 | 547.9 | 553.5 | 627.9 | 551.9
1921 | 1685 | 627.6 | 547.9 | 555.6 | 627.7 | 552.4
1922 | 1686 | 627.4 | 548 | 554.2 | 627.9 | 552.5
1923 | 1687 | 627.1 | 548.2 | 549.9 | 628 | 552.4
1924 | 1688 | 626.7 | 548.8 | 546.5 | 627.9 | 552.1
1925 | 1689 | 626.2 | 548.1 | 542.4 | 627.5 | 550.9
1926 | 1690 | 625.7 | 547 | 539.4 | 627.4 | 549.4
1927 | 1691 | 625.5 | 546.1 | 539.4 | 627.2 | 548.2
1928 | 1692 | 625.4 | 545.8 | 538 | 627.4 | 548.5
1929 | 1693 | 625 | 545.5 | 536.2 | 627.4 | 548.4
1930 | 1694 | 625.1 | 545.4 | 535.9 | 627.4 | 547.8
1931 | 1695 | 625.2 | 545.8 | 536.2 | 627.6 | 546.9
1932 | 1696 | 625.1 | 545.4 | 536.5 | 627.6 | 547
1933 | 1697 | 625.2 | 545.7 | 542 | 628 | 548.2
1934 | 1698 | 625.5 | 546.3 | 546.9 | 628.2 | 549.8
1935 | 1699 | 625.7 | 547.2 | 548.6 | 628.2 | 551.6
1936 | 1700 | 625.6 | 548.2 | 547.5 | 627.9 | 552.4
1937 | 1701 | 625.3 | 547.9 | 547 | 627.7 | 551.2
1938 | 1702 | 625.4 | 547.7 | 548.9 | 627.6 | 551.6
1939 | 1703 | 625.7 | 547.9 | 552.7 | 627.9 | 551.9
1940 | 1704 | 625.8 | 548.2 | 554.5 | 628.1 | 552.9
1941 | 1705 | 625.7 | 548.5 | 554.1 | 627.9 | 552.9
1942 | 1706 | 626.3 | 549.3 | 563.4 | 627.8 | 554.2
1943 | 1707 | 626.5 | 549.9 | 562.5 | 627.7 | 553.3
1944 | 1708 | 626.8 | 550.4 | 562.5 | 627.6 | 554.2
1945 | 1709 | 626.3 | 552.3 | 558.4 | 627.1 | 555.3
1946 | 1710 | 625.8 | 551.1 | 553.5 | 626.8 | 554.1
1947 | 1711 | 625.2 | 549.7 | 551.5 | 626.5 | 552.2
1948 | 1712 | 625.2 | 549.3 | 557.7 | 626.5 | 552.9
1949 | 1713 | 626 | 549.7 | 563.3 | 626.5 | 555.3
1950 | 1714 | 626.1 | 550.4 | 564.7 | 626.3 | 556
1951 | 1715 | 626 | 550.9 | 566.5 | 626 | 555.5
1952 | 1716 | 625.3 | 550 | 562.2 | 625.8 | 553.1
1953 | 1717 | 624.3 | 547.6 | 553.5 | 625.6 | 549.1
1954 | 1718 | 623.1 | 545.2 | 545.5 | 625.2 | 545.6
1955 | 1719 | 622.1 | 541.9 | 538.2 | 624.7 | 542.5
1956 | 1720 | 621 | 538.9 | 531.4 | 624.1 | 540.7
1957 | 1721 | 619.8 | 537.1 | 524.8 | 623.4 | 539
1958 | 1722 | 618.6 | 534.8 | 518.9 | 622.8 | 537.6
1959 | 1723 | 617.5 | 533.3 | 514.1 | 622.1 | 536.2
1960 | 1724 | 616.6 | 531.9 | 510 | 621.5 | 535.3
1961 | 1725 | 615.7 | 529.9 | 505.9 | 621 | 533.9
1962 | 1726 | 614.8 | 528.4 | 501.8 | 620.6 | 532.7
1963 | 1727 | 613.8 | 526.9 | 497.7 | 620.2 | 531.7
1964 | 1728 | 613 | 525.4 | 494.1 | 619.8 | 530.4
1965 | 1729 | 612.2 | 524 | 490.6 | 619.5 | 529
1966 | 1730 | 611.3 | 522.2 | 487.2 | 619 | 528.2
1967 | 1731 | 610.5 | 520.6 | 484.4 | 618.6 | 527.3
1968 | 1732 | 609.8 | 518.9 | 482.3 | 618.3 | 526.5
1969 | 1733 | 608.9 | 516.9 | 479.5 | 617.9 | 525.7
1970 | 1734 | 608 | 515.5 | 477.1 | 617.4 | 524.7
1971 | 1735 | 607.3 | 514.2 | 475.3 | 616.9 | 523
1972 | 1736 | 606.7 | 512.7 | 473 | 616.6 | 521.6
1973 | 1737 | 606 | 511.6 | 471 | 616.2 | 520.8
1974 | 1738 | 605.1 | 510 | 469.3 | 615.8 | 520.3
1975 | 1739 | 604.3 | 509 | 467.4 | 615.3 | 519.5
1976 | 1740 | 603.6 | 507.6 | 465.7 | 614.8 | 518.6
1977 | 1741 | 602.8 | 506.3 | 464.5 | 614.6 | 517.7
1978 | 1742 | 602.1 | 505.5 | 463.6 | 614.3 | 516.6
1979 | 1743 | 601.6 | 504.9 | 462.2 | 614 | 515.3
1980 | 1744 | 601 | 503.7 | 461 | 613.8 | 514.3
1981 | 1745 | 600.5 | 502.6 | 459 | 613.5 | 513.3
1982 | 1746 | 600.1 | 501.8 | 457.5 | 613.2 | 512.3
1983 | 1747 | 599.6 | 501.4 | 456.5 | 613.1 | 511.4
1984 | 1748 | 599.1 | 500.8 | 455.5 | 612.8 | 510.7
1985 | 1749 | 598.6 | 500 | 454.1 | 612.5 | 510.1
1986 | 1750 | 598.1 | 498.9 | 452.8 | 612.4 | 509.1
1987 | 1751 | 597.5 | 498 | 451.5 | 612.3 | 508.1
1988 | 1752 | 596.9 | 497.7 | 450.1 | 612 | 507.1
1989 | 1753 | 596.5 | 497.5 | 448.6 | 611.8 | 506.4
1990 | 1754 | 596 | 497 | 447.5 | 611.6 | 506
1991 | 1755 | 595.5 | 496.5 | 446.6 | 611.2 | 505
1992 | 1756 | 595 | 495.7 | 445.3 | 610.9 | 504.2
1993 | 1757 | 594.4 | 495.2 | 443.9 | 610.5 | 502.9
1994 | 1758 | 593.9 | 494.7 | 443.1 | 610.2 | 501.9
1995 | 1759 | 593.4 | 494.4 | 442 | 609.9 | 501.3
1996 | 1760 | 593 | 493.6 | 441.2 | 609.6 | 500.6
1997 | 1761 | 592.5 | 493 | 440.3 | 609.3 | 500
1998 | 1762 | 591.8 | 492.4 | 439.2 | 609 | 499.7
1999 | 1763 | 591.2 | 491.6 | 438.1 | 608.7 | 498.8
2000 | 1764 | 590.6 | 490.7 | 437.1 | 608.4 | 497.9
2001 | 1765 | 590 | 490.4 | 436.2 | 608 | 497.3
2002 | 1766 | 589.4 | 489.8 | 435.1 | 607.5 | 496.5
2003 | 1767 | 588.8 | 489.4 | 434.3 | 607.2 | 495.4
2004 | 1768 | 588.3 | 488.8 | 433.7 | 607 | 494.4
2005 | 1769 | 587.7 | 488.3 | 432.9 | 606.7 | 493.4
2006 | 1770 | 587.2 | 487.6 | 432.4 | 606.4 | 492.6
2007 | 1771 | 586.7 | 486.9 | 431.5 | 606.1 | 492
2008 | 1772 | 586.1 | 485.8 | 430.8 | 605.8 | 491.2
2009 | 1773 | 585.5 | 485 | 430.2 | 605.6 | 491
2010 | 1774 | 584.9 | 484.9 | 429.4 | 605.3 | 490.3
2011 | 1775 | 584.3 | 484.6 | 428.7 | 604.9 | 489.5
2012 | 1776 | 583.8 | 483.9 | 428.2 | 604.7 | 488.8
2013 | 1777 | 583.2 | 483.4 | 427.6 | 604.4 | 488.3
2014 | 1778 | 582.6 | 483 | 426.8 | 604 | 487.9
2015 | 1779 | 582.1 | 482.5 | 426 | 603.6 | 487.3
2016 | 1780 | 581.6 | 482 | 425.4 | 603.4 | 486.1
2017 | 1781 | 581.1 | 481.6 | 424.7 | 603 | 485.1
2018 | 1782 | 580.5 | 480.8 | 424.1 | 602.8 | 484.4
2019 | 1783 | 580 | 480.1 | 423.2 | 602.5 | 483.4
2020 | 1784 | 579.5 | 479.4 | 422.2 | 602.4 | 482.7
2021 | 1785 | 578.9 | 477.8 | 421.4 | 602.4 | 482.2
2022 | 1786 | 578.3 | 477.4 | 421 | 602.3 | 481.8
2023 | 1787 | 577.7 | 476.4 | 420.3 | 602 | 481.3
2024 | 1788 | 577.1 | 476 | 419.6 | 601.7 | 480.3
2025 | 1789 | 576.6 | 475.3 | 418.7 | 601.5 | 479.5
2026 | 1790 | 576 | 475.5 | 418 | 601.2 | 478.9
2027 | 1791 | 575.4 | 475 | 417.4 | 601 | 478.5
2028 | 1792 | 574.7 | 474.2 | 417.1 | 600.8 | 477.8
2029 | 1793 | 574 | 473.6 | 416.2 | 600.5 | 477
2030 | 1794 | 573.5 | 473.7 | 415.6 | 600.4 | 476.2
2031 | 1795 | 572.9 | 472.8 | 415 | 600.4 | 475.3
2032 | 1796 | 572.5 | 473 | 414.3 | 600.4 | 474.8
2033 | 1797 | 572.1 | 473 | 414 | 600 | 474.3
2034 | 1798 | 571.7 | 472.8 | 413.7 | 599.6 | 473.5
2035 | 1799 | 571.3 | 472.1 | 413.2 | 599.3 | 472.7
2036 | 1800 | 570.8 | 471.5 | 412.7 | 599.1 | 472.1
2037 | 1801 | 570.4 | 470.8 | 412.1 | 599 | 471.5
2038 | 1802 | 570 | 470.1 | 411.6 | 599 | 470.7
2039 | 1803 | 569.5 | 470.1 | 410.8 | 599 | 470.2
2040 | 1804 | 569.1 | 469.7 | 410.3 | 598.5 | 469.9
2041 | 1805 | 568.7 | 469.8 | 410 | 598.2 | 469.7
2042 | 1806 | 568.2 | 469.4 | 409.5 | 597.8 | 469.4
2043 | 1807 | 567.8 | 469.3 | 409.2 | 597.4 | 468.6
2044 | 1808 | 567.2 | 469.1 | 408.8 | 597 | 467.9
2045 | 1809 | 566.8 | 468.2 | 408.3 | 596.8 | 467.2
2046 | 1810 | 566.4 | 467.8 | 408 | 596.7 | 466.2
2047 | 1811 | 565.9 | 467.2 | 407.2 | 596.4 | 465.5
2048 | 1812 | 565.5 | 466.8 | 406.3 | 596 | 465.4
2049 | 1813 | 565 | 466.1 | 405.9 | 595.7 | 465
2050 | 1814 | 564.5 | 465.6 | 405.6 | 595.4 | 464.2
2051 | 1815 | 564 | 465.4 | 405.1 | 595.1 | 463.1
2052 | 1816 | 563.4 | 465.2 | 404.5 | 595 | 462.6
2053 | 1817 | 562.9 | 465 | 403.7 | 594.7 | 462.3
2054 | 1818 | 562.4 | 464.1 | 403.2 | 594.4 | 462.1
2055 | 1819 | 561.9 | 463.6 | 402.7 | 594.3 | 461.7
2056 | 1820 | 561.5 | 463.6 | 401.8 | 594 | 460.9
2057 | 1821 | 561.1 | 463.2 | 401.5 | 593.8 | 460.3
2058 | 1822 | 560.7 | 463.1 | 401 | 593.6 | 459.6
2059 | 1823 | 560.3 | 462.4 | 400.5 | 593.4 | 459.1
2060 | 1824 | 559.9 | 461.1 | 399.8 | 593.3 | 458.5
2061 | 1825 | 559.4 | 460 | 399.6 | 593.3 | 458.2
2062 | 1826 | 558.9 | 459.3 | 399.2 | 593.1 | 457.3
2063 | 1827 | 558.4 | 459.1 | 398.4 | 592.9 | 456.6
2064 | 1828 | 557.9 | 459 | 397.7 | 592.8 | 455.9
2065 | 1829 | 557.4 | 458.8 | 397.4 | 592.6 | 455.3
2066 | 1830 | 557 | 458.6 | 396.9 | 592.4 | 454.9
2067 | 1831 | 556.4 | 458.3 | 396.4 | 592.1 | 454.1
2068 | 1832 | 555.9 | 457.6 | 395.8 | 591.8 | 453.6
2069 | 1833 | 555.5 | 457.5 | 395.2 | 591.6 | 453.4
2070 | 1834 | 555 | 457.4 | 394.6 | 591.5 | 453.2
2071 | 1835 | 554.6 | 457 | 394.2 | 591.5 | 452.6
2072 | 1836 | 554.2 | 455.8 | 393.9 | 591.4 | 451.9
2073 | 1837 | 553.8 | 455.1 | 393.4 | 591.2 | 451.6
2074 | 1838 | 553.3 | 455.3 | 393 | 590.9 | 450.7
2075 | 1839 | 552.9 | 455.3 | 392.7 | 590.5 | 450
2076 | 1840 | 552.5 | 455.3 | 392.6 | 590.3 | 449.5
2077 | 1841 | 552 | 454.3 | 391.8 | 590.1 | 449.6
2078 | 1842 | 551.6 | 454.4 | 391.5 | 589.8 | 448.7
2079 | 1843 | 551 | 454.4 | 391.3 | 589.8 | 448.2
2080 | 1844 | 550.6 | 453.6 | 390.8 | 589.9 | 447.9
2081 | 1845 | 550.2 | 453 | 390 | 589.8 | 447
2082 | 1846 | 549.8 | 453 | 389.2 | 589.5 | 446
2083 | 1847 | 549.3 | 452.8 | 388.7 | 589.2 | 445.5
2084 | 1848 | 548.8 | 451.9 | 388.1 | 589 | 445.2
2085 | 1849 | 548.3 | 451.4 | 387.7 | 588.8 | 445
2086 | 1850 | 548 | 451.7 | 387.1 | 588.5 | 444.4
2087 | 1851 | 547.6 | 451.4 | 386.6 | 588.2 | 443.6
2088 | 1852 | 547.2 | 450.9 | 386.2 | 588.1 | 443.3
2089 | 1853 | 546.8 | 450.8 | 385.8 | 588.2 | 443.1
2090 | 1854 | 546.5 | 449.6 | 385.6 | 588.2 | 442.6
2091 | 1855 | 546 | 448.9 | 385 | 588.1 | 441.9
2092 | 1856 | 545.6 | 448.9 | 384.8 | 588 | 441.5
2093 | 1857 | 545.2 | 448.5 | 384.2 | 587.8 | 440.6
2094 | 1858 | 544.7 | 448.8 | 384.1 | 587.4 | 440.1
2095 | 1859 | 544.2 | 448.5 | 383.6 | 587.2 | 440.1
2096 | 1860 | 543.8 | 448.2 | 383 | 587 | 440
2097 | 1861 | 543.4 | 447.5 | 382.4 | 586.6 | 439.9
2098 | 1862 | 543.1 | 446.8 | 382.2 | 586.4 | 439.8
2099 | 1863 | 542.7 | 446.4 | 382.3 | 586.3 | 439.1
2100 | 1864 | 542.4 | 446 | 381.9 | 586.2 | 438.3
2101 | 1865 | 542 | 445.9 | 381.3 | 585.9 | 437.4
2102 | 1866 | 541.6 | 445.7 | 380.5 | 585.7 | 436.8
2103 | 1867 | 541.1 | 445 | 379.9 | 585.6 | 436.4
2104 | 1868 | 540.7 | 444 | 379.8 | 585.5 | 436.1
2105 | 1869 | 540.3 | 443.4 | 379.5 | 585.5 | 435.5
2106 | 1870 | 539.8 | 443 | 378.7 | 585.4 | 434.9
2107 | 1871 | 539.3 | 442 | 378.3 | 585.3 | 434.5
2108 | 1872 | 538.8 | 441.5 | 377.8 | 585.1 | 434.2
2109 | 1873 | 538.2 | 441.6 | 377.7 | 585 | 433.9
2110 | 1874 | 537.7 | 440.6 | 376.9 | 584.8 | 433.4
2111 | 1875 | 537.4 | 439.9 | 376 | 584.9 | 432.5
2112 | 1876 | 537.1 | 439.7 | 375.7 | 584.8 | 432.3
2113 | 1877 | 536.7 | 439.3 | 375.5 | 584.6 | 432.2
2114 | 1878 | 536.3 | 438.4 | 375 | 584.5 | 431.8
2115 | 1879 | 536 | 438.5 | 374.1 | 584.1 | 431.1
2116 | 1880 | 535.7 | 437.6 | 374 | 583.9 | 430.6
2117 | 1881 | 535.4 | 437.2 | 373.9 | 583.8 | 430.2
2118 | 1882 | 535.1 | 436.7 | 373.5 | 583.5 | 430
2119 | 1883 | 534.8 | 436.6 | 373 | 583.3 | 429.6
2120 | 1884 | 534.5 | 436.7 | 372.7 | 583.4 | 428.8
2121 | 1885 | 534.2 | 436.9 | 372.2 | 583.5 | 428.2
2122 | 1886 | 533.8 | 435.6 | 372.2 | 583.5 | 427.9
2123 | 1887 | 533.5 | 435.8 | 372.1 | 583.3 | 427.6
2124 | 1888 | 533.1 | 436.2 | 371.6 | 583.3 | 427.3
2125 | 1889 | 532.8 | 436.9 | 371.5 | 583.4 | 427
2126 | 1890 | 532.4 | 436.7 | 371.3 | 583.8 | 426.6
2127 | 1891 | 532.1 | 436.3 | 370.9 | 583.9 | 426.5
2128 | 1892 | 531.8 | 435.6 | 370.3 | 583.6 | 426.3
2129 | 1893 | 531.4 | 435.6 | 370.1 | 583.4 | 426
2130 | 1894 | 530.9 | 435.7 | 370.1 | 583.4 | 425.5
2131 | 1895 | 530.6 | 435.9 | 370 | 583.2 | 424.9
2132 | 1896 | 530.1 | 435.1 | 369.1 | 582.9 | 424
2133 | 1897 | 529.6 | 433.9 | 368.5 | 582.8 | 423
2134 | 1898 | 529.2 | 432.6 | 368.2 | 582.9 | 422.8
2135 | 1899 | 528.7 | 432.2 | 367.7 | 583 | 422.2
2136 | 1900 | 528.4 | 430.4 | 367.1 | 583.4 | 421.6
2137 | 1901 | 528 | 430.9 | 366.4 | 583.5 | 421.2
2138 | 1902 | 527.7 | 430.8 | 365.9 | 583.7 | 420.4
2139 | 1903 | 527.5 | 429.5 | 365.6 | 583.6 | 420.2
2140 | 1904 | 527.2 | 429.9 | 365.2 | 583.2 | 420
2141 | 1905 | 527 | 428.6 | 365.1 | 583.2 | 419.4
2142 | 1906 | 526.6 | 428.5 | 364.6 | 583.1 | 419.3
2143 | 1907 | 526.2 | 428.1 | 363.9 | 582.7 | 419.1
2144 | 1908 | 525.7 | 427.9 | 363.3 | 582.6 | 418.6
2145 | 1909 | 525.2 | 427.3 | 363 | 582.3 | 418.3
2146 | 1910 | 524.7 | 426.8 | 362.9 | 582.2 | 418.1
2147 | 1911 | 524.3 | 426.4 | 362.7 | 582.1 | 417.4
2148 | 1912 | 523.7 | 427.1 | 362.3 | 582 | 416.5
2149 | 1913 | 523.3 | 427 | 361.8 | 582.3 | 416
2150 | 1914 | 523.1 | 427.1 | 361.2 | 582 | 416.1
2151 | 1915 | 522.9 | 426.6 | 360.7 | 582 | 416
2152 | 1916 | 522.7 | 426.5 | 360.4 | 581.7 | 415.3
2153 | 1917 | 522.5 | 425.6 | 360.3 | 581.6 | 415.1
2154 | 1918 | 522.2 | 425.6 | 360.4 | 581.6 | 415.2
2155 | 1919 | 522 | 426 | 360 | 581.5 | 415
2156 | 1920 | 521.7 | 425.8 | 359.7 | 581.5 | 414.5
2157 | 1921 | 521.3 | 425.6 | 359.1 | 581.8 | 413.6
2158 | 1922 | 521 | 424.9 | 358 | 581.7 | 412.6
2159 | 1923 | 520.7 | 423.4 | 357.7 | 581.3 | 412
2160 | 1924 | 520.3 | 422.7 | 357.3 | 581.4 | 411.4
2161 | 1925 | 519.9 | 422.2 | 357.2 | 581.3 | 410.9
2162 | 1926 | 519.5 | 421.4 | 356.9 | 581.2 | 410.5
2163 | 1927 | 519.2 | 420.9 | 356.2 | 581 | 410.3
2164 | 1928 | 518.8 | 421.2 | 355.7 | 580.8 | 410.1
2165 | 1929 | 518.6 | 421 | 355.1 | 580.7 | 409.4
2166 | 1930 | 518.4 | 420.7 | 354.7 | 580.6 | 408.7
2167 | 1931 | 518.2 | 421.5 | 354.5 | 580.3 | 408.6
2168 | 1932 | 517.9 | 421.6 | 354.4 | 580 | 408.5
2169 | 1933 | 517.6 | 421.9 | 354.4 | 579.9 | 408.3
2170 | 1934 | 517.4 | 421.4 | 354.6 | 579.8 | 408
2171 | 1935 | 517.1 | 421.3 | 354.5 | 579.6 | 407.7
2172 | 1936 | 516.8 | 420.1 | 353.8 | 579.3 | 407.6
2173 | 1937 | 516.5 | 421.3 | 353.7 | 579.1 | 407.5
2174 | 1938 | 516.1 | 421.6 | 353.7 | 578.8 | 407.1
2175 | 1939 | 515.7 | 421.1 | 353.3 | 578.4 | 406.9
2176 | 1940 | 515.3 | 418.3 | 352.6 | 578 | 406.4
2177 | 1941 | 515 | 418.1 | 352.5 | 577.7 | 405.9
2178 | 1942 | 514.6 | 418.7 | 352.4 | 577.3 | 405.2
2179 | 1943 | 514.3 | 418.9 | 352.6 | 577.1 | 404.9
2180 | 1944 | 514 | 417 | 352.4 | 576.9 | 404.9
2181 | 1945 | 513.6 | 416.8 | 351.8 | 576.5 | 404.4
2182 | 1946 | 513.2 | 417.6 | 351.6 | 576.3 | 404
2183 | 1947 | 512.8 | 417.8 | 351 | 575.9 | 403.2
2184 | 1948 | 512.5 | 417.8 | 350.5 | 575.5 | 402.6
2185 | 1949 | 512.2 | 417.8 | 350.1 | 575.2 | 402.5
2186 | 1950 | 511.8 | 417.7 | 349.8 | 575 | 402.5
2187 | 1951 | 511.5 | 417.8 | 349.5 | 574.7 | 401.9
2188 | 1952 | 511 | 418.3 | 349 | 574.3 | 401.5
2189 | 1953 | 510.5 | 415.8 | 348.9 | 573.8 | 401.3
2190 | 1954 | 510 | 415.9 | 348.7 | 573.4 | 400.7
2191 | 1955 | 509.6 | 416.5 | 348.7 | 573.1 | 400.4
2192 | 1956 | 509.3 | 416.3 | 348.2 | 573 | 400.6
2193 | 1957 | 509.1 | 414.8 | 347.9 | 572.8 | 399.9
2194 | 1958 | 508.8 | 413.8 | 347.5 | 572.8 | 399.7
2195 | 1959 | 508.5 | 414.2 | 346.9 | 572.5 | 399.4
2196 | 1960 | 508.2 | 413.7 | 346.8 | 572.3 | 399.4
2197 | 1961 | 507.8 | 414.4 | 345.8 | 571.9 | 398.9
2198 | 1962 | 507.5 | 414.2 | 345.4 | 571.6 | 398.6
2199 | 1963 | 507 | 414.2 | 344.8 | 571.2 | 398
2200 | 1964 | 506.5 | 413.8 | 344.4 | 571 | 397.6
2201 | 1965 | 506.1 | 413.7 | 344 | 570.7 | 396.8
2202 | 1966 | 505.8 | 413.5 | 343.5 | 570.5 | 396.7
2203 | 1967 | 505.4 | 413.6 | 343.3 | 570.4 | 396.4
2204 | 1968 | 505.2 | 413.6 | 343.3 | 570.4 | 395.9
2205 | 1969 | 504.9 | 413.2 | 343.5 | 570.3 | 395.3
2206 | 1970 | 504.6 | 413.6 | 343.3 | 570.1 | 394.7
2207 | 1971 | 504.2 | 413.4 | 342.8 | 569.9 | 394.6
2208 | 1972 | 503.9 | 412 | 342.5 | 569.6 | 394.7

## Raw IRMS Data
Time | DL1.V2000:B | DL1.V2001:B | DL1.V1500:B | Open Burn Test 14 |  |  | 2006-11-29 | 11:22
39050.4685 | 1 | 0 | 1 | Mixed | 7-C | Tray F | IRMS | 1
39050.469 | 1 | 0 | 1 |  | 300 kW |  | Bundle
39050.4695 | 1 | 0 | 1
39050.47 | 1 | 0 | 1
39050.4705 | 1 | 0 | 1
39050.471 | 1 | 0 | 1
39050.4714 | 1 | 0 | 1
39050.4719 | 1 | 0 | 1
39050.4724 | 1 | 0 | 1
39050.4729 | 1 | 0 | 1
39050.4734 | 1 | 0 | 1
39050.4739 | 1 | 0 | 1
39050.4748 | 1 | 0 | 1
39050.4753 | 1 | 0 | 1
39050.4758 | 1 | 0 | 1
39050.4763 | 1 | 0 | 1
39050.4768 | 1 | 0 | 1
39050.4773 | 1 | 0 | 1
39050.4778 | 2 | 0 | 1
39050.4783 | 61 | 16 | 1
39050.4787 | 525 | 325 | 1
39050.4792 | 1054 | 773 | 1
39050.4797 | 1924 | 74 | 1
39050.4802 | 1848 | 19 | 1
39050.4807 | 2032 | 10 | 1
39050.4812 | 2007 | 5 | 1
39050.4817 | 2409 | 3 | 1
39050.4821 | 1961 | 1 | 1
39050.4826 | 2480 | 0 | 1
39050.4831 | 2280 | 0 | 1
39050.4836 | 2128 | 0 | 1
39050.4841 | 2115 | 0 | 1
39050.4846 | 2360 | 0 | 1
39050.4851 | 2421 | 0 | 1
39050.4855 | 2513 | 0 | 1
39050.486 | 2003 | 0 | 1
39050.4865 | 2457 | 0 | 1
39050.487 | 2022 | 0 | 1
39050.4875 | 2476 | 0 | 1
39050.488 | 2257 | 0 | 1
39050.4885 | 2265 | 0 | 1
39050.4889 | 1943 | 0 | 1
39050.4894 | 2440 | 0 | 1
39050.4899 | 2403 | 0 | 1
39050.4904 | 2226 | 0 | 1
39050.4909 | 2277 | 0 | 1
39050.4914 | 2240 | 0 | 1
39050.4919 | 2225 | 0 | 1
39050.4923 | 2445 | 1 | 1
39050.4928 | 2397 | 6 | 1
39050.4933 | 2180 | 17 | 1
1
39050.4686 | 1 | 0 | 2
39050.469 | 1 | 0 | 2
39050.4695 | 1 | 0 | 2
39050.47 | 1 | 0 | 2
39050.4705 | 0 | 0 | 2
39050.471 | 1 | 0 | 2
39050.4715 | 1 | 0 | 2
39050.472 | 1 | 0 | 2
39050.4724 | 1 | 0 | 2
39050.4729 | 1 | 0 | 2
39050.4734 | 1 | 0 | 2
39050.4739 | 1 | 0 | 2
39050.4744 | 1 | 0 | 2
39050.4749 | 1 | 0 | 2
39050.4754 | 1 | 0 | 2
39050.4758 | 1 | 0 | 2
39050.4763 | 1 | 0 | 2
39050.4768 | 1 | 0 | 2
39050.4773 | 1 | 0 | 2
39050.4778 | 1 | 0 | 2
39050.4783 | 54 | 34 | 2
39050.4788 | 425 | 303 | 2
39050.4792 | 860 | 589 | 2
39050.4797 | 1829 | 61 | 2
39050.4802 | 2387 | 20 | 2
39050.4807 | 2365 | 10 | 2
39050.4812 | 2279 | 4 | 2
39050.4817 | 2060 | 2 | 2
39050.4822 | 2258 | 1 | 2
39050.4827 | 2426 | 0 | 2
39050.4831 | 2077 | 0 | 2
39050.4836 | 2042 | 0 | 2
39050.4841 | 2369 | 0 | 2
39050.4846 | 2059 | 0 | 2
39050.4851 | 2218 | 0 | 2
39050.4856 | 2303 | 0 | 2
39050.486 | 2395 | 0 | 2
39050.4865 | 2195 | 0 | 2
39050.487 | 2449 | 0 | 2
39050.4875 | 2365 | 0 | 2
39050.488 | 2465 | 0 | 2
39050.4885 | 2160 | 0 | 2
39050.489 | 2059 | 0 | 2
39050.4894 | 2154 | 0 | 2
39050.4899 | 2059 | 0 | 2
39050.4904 | 2521 | 0 | 2
39050.4909 | 2221 | 0 | 2
39050.4914 | 2018 | 0 | 2
39050.4919 | 2151 | 0 | 2
39050.4924 | 2265 | 2 | 2
39050.4928 | 2173 | 6 | 2
39050.4933 | 2416 | 18 | 2
2
39050.4686 | 1 | 0 | 3
39050.4691 | 1 | 0 | 3
39050.4695 | 1 | 0 | 3
39050.47 | 1 | 0 | 3
39050.4705 | 1 | 0 | 3
39050.471 | 1 | 0 | 3
39050.4715 | 1 | 0 | 3
39050.472 | 1 | 0 | 3
39050.4725 | 1 | 0 | 3
39050.4729 | 1 | 0 | 3
39050.4734 | 1 | 0 | 3
39050.4739 | 1 | 0 | 3
39050.4744 | 1 | 0 | 3
39050.4749 | 0 | 0 | 3
39050.4754 | 1 | 0 | 3
39050.4759 | 1 | 0 | 3
39050.4763 | 1 | 0 | 3
39050.4768 | 1 | 0 | 3
39050.4773 | 1 | 0 | 3
39050.4778 | 1 | 0 | 3
39050.4783 | 1 | 0 | 3
39050.4788 | 102 | 0 | 3
39050.4793 | 394 | 0 | 3
39050.4797 | 1974 | 0 | 3
39050.4802 | 2009 | 0 | 3
39050.4807 | 2241 | 0 | 3
39050.4812 | 2445 | 0 | 3
39050.4817 | 2334 | 0 | 3
39050.4822 | 1951 | 0 | 3
39050.4827 | 2196 | 0 | 3
39050.4831 | 2379 | 0 | 3
39050.4836 | 2209 | 0 | 3
39050.4841 | 2319 | 0 | 3
39050.4846 | 2453 | 0 | 3
39050.4851 | 2283 | 0 | 3
39050.4856 | 2438 | 0 | 3
39050.4861 | 2145 | 0 | 3
39050.4866 | 2457 | 0 | 3
39050.487 | 2173 | 0 | 3
39050.4875 | 2035 | 0 | 3
39050.488 | 2381 | 0 | 3
39050.4885 | 2014 | 0 | 3
39050.489 | 2482 | 0 | 3
39050.4895 | 2472 | 0 | 3
39050.49 | 2344 | 0 | 3
39050.4904 | 2275 | 0 | 3
39050.4909 | 1967 | 0 | 3
39050.4914 | 2357 | 0 | 3
39050.4919 | 2406 | 0 | 3
39050.4924 | 2081 | 0 | 3
39050.4929 | 2026 | 0 | 3
39050.4934 | 2121 | 0 | 3
3
39050.4686 | 1 | 0 | 4
39050.4691 | 1 | 0 | 4
39050.4695 | 1 | 0 | 4
39050.47 | 1 | 0 | 4
39050.4705 | 1 | 0 | 4
39050.471 | 1 | 0 | 4
39050.4715 | 1 | 0 | 4
39050.472 | 1 | 0 | 4
39050.4725 | 1 | 0 | 4
39050.473 | 1 | 0 | 4
39050.4734 | 1 | 0 | 4
39050.4739 | 1 | 0 | 4
39050.4744 | 1 | 0 | 4
39050.4749 | 1 | 0 | 4
39050.4754 | 1 | 0 | 4
39050.4759 | 1 | 0 | 4
39050.4764 | 61 | 0 | 4
39050.4768 | 1741 | 0 | 4
39050.4773 | 2335 | 0 | 4
39050.4778 | 2403 | 0 | 4
39050.4783 | 2267 | 0 | 4
39050.4788 | 2276 | 0 | 4
39050.4793 | 1920 | 0 | 4
39050.4798 | 2099 | 0 | 4
39050.4802 | 1976 | 0 | 4
39050.4807 | 2463 | 0 | 4
39050.4812 | 2340 | 0 | 4
39050.4817 | 2332 | 0 | 4
39050.4822 | 2258 | 0 | 4
39050.4827 | 2453 | 0 | 4
39050.4832 | 2450 | 0 | 4
39050.4836 | 2019 | 0 | 4
39050.4841 | 2293 | 0 | 4
39050.4846 | 2009 | 0 | 4
39050.4851 | 1989 | 0 | 4
39050.4856 | 1785 | 0 | 4
39050.4861 | 1861 | 0 | 4
39050.4866 | 1858 | 0 | 4
39050.487 | 2248 | 0 | 4
39050.4875 | 2118 | 0 | 4
39050.488 | 1956 | 0 | 4
39050.4885 | 2120 | 0 | 4
39050.489 | 2363 | 0 | 4
39050.4895 | 1986 | 0 | 4
39050.49 | 1953 | 0 | 4
39050.4905 | 2261 | 0 | 4
39050.4909 | 1983 | 0 | 4
39050.4914 | 2148 | 0 | 4
39050.4919 | 2324 | 0 | 4
39050.4924 | 2177 | 0 | 4
39050.4929 | 1951 | 0 | 4
39050.4934 | 2084 | 0 | 4
4
39050.4686 | 1 | 0 | 5
39050.4691 | 1 | 0 | 5
39050.4696 | 1 | 0 | 5
39050.4701 | 0 | 0 | 5
39050.4705 | 1 | 0 | 5
39050.471 | 1 | 0 | 5
39050.4715 | 1 | 0 | 5
39050.472 | 1 | 0 | 5
39050.4725 | 1 | 0 | 5
39050.473 | 1 | 0 | 5
39050.4735 | 1 | 0 | 5
39050.4739 | 1 | 0 | 5
39050.4744 | 1 | 0 | 5
39050.4749 | 1 | 0 | 5
39050.4754 | 1 | 0 | 5
39050.4759 | 1 | 0 | 5
39050.4764 | 1 | 0 | 5
39050.4769 | 1 | 0 | 5
39050.4773 | 1 | 0 | 5
39050.4778 | 1 | 0 | 5
39050.4783 | 4 | 0 | 5
39050.4788 | 197 | 0 | 5
39050.4793 | 458 | 0 | 5
39050.4798 | 2292 | 0 | 5
39050.4803 | 2372 | 0 | 5
39050.4808 | 2124 | 0 | 5
39050.4812 | 2337 | 0 | 5
39050.4817 | 2044 | 0 | 5
39050.4822 | 2006 | 0 | 5
39050.4827 | 1966 | 0 | 5
39050.4832 | 2207 | 0 | 5
39050.4837 | 2205 | 0 | 5
39050.4842 | 1930 | 0 | 5
39050.4846 | 2313 | 0 | 5
39050.4851 | 2451 | 0 | 5
39050.4856 | 2142 | 0 | 5
39050.4861 | 2518 | 0 | 5
39050.4866 | 2064 | 0 | 5
39050.4871 | 2325 | 0 | 5
39050.4876 | 2475 | 0 | 5
39050.488 | 2477 | 0 | 5
39050.4885 | 2327 | 0 | 5
39050.489 | 2437 | 0 | 5
39050.4895 | 2067 | 0 | 5
39050.49 | 2270 | 0 | 5
39050.4905 | 2277 | 0 | 5
39050.491 | 2370 | 0 | 5
39050.4914 | 2003 | 0 | 5
39050.4919 | 2015 | 0 | 5
39050.4924 | 2039 | 0 | 5
39050.4929 | 2333 | 0 | 5
39050.4934 | 2239 | 0 | 5
5
39050.4686 | 1 | 0 | 6
39050.4691 | 1 | 0 | 6
39050.4696 | 1 | 0 | 6
39050.4701 | 1 | 0 | 6
39050.4706 | 1 | 0 | 6
39050.471 | 1 | 0 | 6
39050.4715 | 1 | 0 | 6
39050.472 | 1 | 0 | 6
39050.4725 | 1 | 0 | 6
39050.473 | 1 | 0 | 6
39050.4735 | 1 | 0 | 6
39050.474 | 1 | 0 | 6
39050.4744 | 1 | 0 | 6
39050.4749 | 1 | 0 | 6
39050.4754 | 1 | 0 | 6
39050.4759 | 1 | 0 | 6
39050.4764 | 1 | 0 | 6
39050.4769 | 77 | 0 | 6
39050.4774 | 2204 | 0 | 6
39050.4778 | 2136 | 0 | 6
39050.4783 | 2167 | 0 | 6
39050.4788 | 2266 | 0 | 6
39050.4793 | 2129 | 0 | 6
39050.4798 | 2199 | 0 | 6
39050.4803 | 2520 | 0 | 6
39050.4808 | 2431 | 0 | 6
39050.4812 | 2425 | 0 | 6
39050.4817 | 2268 | 0 | 6
39050.4822 | 1985 | 0 | 6
39050.4827 | 2149 | 0 | 6
39050.4832 | 2139 | 0 | 6
39050.4837 | 2411 | 0 | 6
39050.4842 | 2412 | 0 | 6
39050.4847 | 1951 | 0 | 6
39050.4851 | 1990 | 0 | 6
39050.4856 | 2078 | 0 | 6
39050.4861 | 2398 | 0 | 6
39050.4866 | 1978 | 0 | 6
39050.4871 | 2134 | 0 | 6
39050.4876 | 2132 | 0 | 6
39050.4881 | 2107 | 0 | 6
39050.4885 | 2199 | 0 | 6
39050.489 | 1905 | 0 | 6
39050.4895 | 2366 | 0 | 6
39050.49 | 2121 | 0 | 6
39050.4905 | 2185 | 0 | 6
39050.491 | 2373 | 0 | 6
39050.4915 | 2045 | 0 | 6
39050.4919 | 2274 | 0 | 6
39050.4924 | 1752 | 0 | 6
39050.4929 | 1968 | 0 | 6
39050.4934 | 1754 | 0 | 6
6
39050.4686 | 1 | 0 | 7
39050.4691 | 1 | 0 | 7
39050.4696 | 1 | 0 | 7
39050.4701 | 1 | 0 | 7
39050.4706 | 1 | 0 | 7
39050.4711 | 1 | 0 | 7
39050.4716 | 1 | 0 | 7
39050.472 | 1 | 0 | 7
39050.4725 | 1 | 0 | 7
39050.473 | 1 | 0 | 7
39050.4735 | 1 | 0 | 7
39050.474 | 1 | 0 | 7
39050.4745 | 1 | 0 | 7
39050.475 | 1 | 0 | 7
39050.4754 | 1 | 0 | 7
39050.4759 | 1 | 0 | 7
39050.4764 | 1 | 0 | 7
39050.4769 | 1 | 0 | 7
39050.4774 | 1 | 0 | 7
39050.4779 | 1 | 0 | 7
39050.4784 | 6 | 0 | 7
39050.4788 | 229 | 0 | 7
39050.4793 | 1560 | 0 | 7
39050.4798 | 2344 | 0 | 7
39050.4803 | 1887 | 0 | 7
39050.4808 | 2330 | 0 | 7
39050.4813 | 2450 | 0 | 7
39050.4818 | 2376 | 0 | 7
39050.4822 | 2474 | 0 | 7
39050.4827 | 2193 | 0 | 7
39050.4832 | 2005 | 0 | 7
39050.4837 | 2130 | 0 | 7
39050.4842 | 2350 | 0 | 7
39050.4847 | 2379 | 0 | 7
39050.4852 | 2072 | 0 | 7
39050.4856 | 2210 | 0 | 7
39050.4861 | 2531 | 0 | 7
39050.4866 | 2335 | 0 | 7
39050.4871 | 2499 | 0 | 7
39050.4876 | 1953 | 0 | 7
39050.4881 | 2378 | 0 | 7
39050.4886 | 2519 | 0 | 7
39050.489 | 2073 | 0 | 7
39050.4895 | 2387 | 0 | 7
39050.49 | 2320 | 0 | 7
39050.4905 | 2418 | 0 | 7
39050.491 | 2348 | 0 | 7
39050.4915 | 2328 | 0 | 7
39050.492 | 2480 | 0 | 7
39050.4924 | 2428 | 0 | 7
39050.4929 | 2308 | 0 | 7
39050.4934 | 2002 | 0 | 7
7
39050.4686 | 1 | 0 | 8
39050.4691 | 1 | 0 | 8
39050.4696 | 1 | 0 | 8
39050.4701 | 1 | 0 | 8
39050.4706 | 1 | 0 | 8
39050.4711 | 1 | 0 | 8
39050.4716 | 1 | 0 | 8
39050.472 | 1 | 0 | 8
39050.4725 | 1 | 0 | 8
39050.473 | 1 | 0 | 8
39050.4735 | 1 | 0 | 8
39050.474 | 1 | 0 | 8
39050.4745 | 1 | 0 | 8
39050.475 | 1 | 0 | 8
39050.4755 | 1 | 0 | 8
39050.4759 | 2043 | 0 | 8
39050.4764 | 1353 | 0 | 8
39050.4769 | 1988 | 0 | 8
39050.4774 | 2449 | 0 | 8
39050.4779 | 2532 | 0 | 8
39050.4784 | 2583 | 0 | 8
39050.4789 | 2450 | 0 | 8
39050.4793 | 2299 | 0 | 8
39050.4798 | 2331 | 0 | 8
39050.4803 | 2529 | 0 | 8
39050.4808 | 2212 | 0 | 8
39050.4813 | 2516 | 0 | 8
39050.4818 | 2303 | 0 | 8
39050.4823 | 2352 | 0 | 8
39050.4827 | 2080 | 0 | 8
39050.4832 | 2183 | 0 | 8
39050.4837 | 2257 | 0 | 8
39050.4842 | 2559 | 0 | 8
39050.4847 | 2423 | 0 | 8
39050.4852 | 2309 | 0 | 8
39050.4857 | 2578 | 0 | 8
39050.4861 | 2054 | 0 | 8
39050.4866 | 2081 | 0 | 8
39050.4871 | 2024 | 0 | 8
39050.4876 | 2164 | 0 | 8
39050.4881 | 2322 | 0 | 8
39050.4886 | 2231 | 0 | 8
39050.4891 | 2364 | 0 | 8
39050.4895 | 2574 | 0 | 8
39050.49 | 2526 | 0 | 8
39050.4905 | 2100 | 0 | 8
39050.491 | 2126 | 0 | 8
39050.4915 | 2156 | 0 | 8
39050.492 | 2481 | 0 | 8
39050.4925 | 2163 | 0 | 8
39050.493 | 2366 | 0 | 8
39050.4934 | 2022 | 0 | 8
8
39050.4687 | 1 | 0 | 9
39050.4691 | 1 | 0 | 9
39050.4696 | 1 | 0 | 9
39050.4701 | 1 | 0 | 9
39050.4706 | 0 | 0 | 9
39050.4711 | 1 | 0 | 9
39050.4716 | 1 | 0 | 9
39050.4721 | 1 | 0 | 9
39050.4725 | 1 | 0 | 9
39050.473 | 1 | 0 | 9
39050.4735 | 1 | 0 | 9
39050.474 | 1 | 0 | 9
39050.4745 | 1 | 0 | 9
39050.475 | 0 | 0 | 9
39050.4755 | 1 | 0 | 9
39050.4759 | 1 | 0 | 9
39050.4764 | 1 | 0 | 9
39050.4769 | 1 | 0 | 9
39050.4774 | 1 | 0 | 9
39050.4779 | 1 | 0 | 9
39050.4784 | 2 | 0 | 9
39050.4789 | 239 | 0 | 9
39050.4794 | 1778 | 0 | 9
39050.4798 | 2216 | 0 | 9
39050.4803 | 2019 | 0 | 9
39050.4808 | 2152 | 0 | 9
39050.4813 | 2309 | 0 | 9
39050.4818 | 2472 | 0 | 9
39050.4823 | 2084 | 0 | 9
39050.4828 | 2493 | 0 | 9
39050.4832 | 1957 | 0 | 9
39050.4837 | 2192 | 0 | 9
39050.4842 | 2387 | 0 | 9
39050.4847 | 2123 | 0 | 9
39050.4852 | 2087 | 0 | 9
39050.4857 | 1936 | 0 | 9
39050.4862 | 1933 | 0 | 9
39050.4866 | 2360 | 0 | 9
39050.4871 | 2272 | 0 | 9
39050.4876 | 2078 | 0 | 9
39050.4881 | 1968 | 0 | 9
39050.4886 | 2052 | 0 | 9
39050.4891 | 2075 | 0 | 9
39050.4896 | 2367 | 0 | 9
39050.49 | 2022 | 0 | 9
39050.4905 | 2518 | 0 | 9
39050.491 | 1943 | 0 | 9
39050.4915 | 2501 | 0 | 9
39050.492 | 2472 | 0 | 9
39050.4925 | 1991 | 0 | 9
39050.493 | 2192 | 0 | 9
39050.4934 | 2129 | 0 | 9
9
39050.4687 | 1 | 0 | 10
39050.4692 | 1 | 0 | 10
39050.4697 | 1 | 0 | 10
39050.4701 | 1 | 0 | 10
39050.4706 | 1 | 0 | 10
39050.4711 | 1 | 0 | 10
39050.4716 | 1 | 0 | 10
39050.4721 | 1 | 0 | 10
39050.4726 | 1 | 0 | 10
39050.4731 | 1 | 0 | 10
39050.4735 | 1 | 0 | 10
39050.474 | 1 | 0 | 10
39050.4745 | 1 | 0 | 10
39050.475 | 0 | 0 | 10
39050.4755 | 1 | 0 | 10
39050.476 | 1887 | 0 | 10
39050.4765 | 1974 | 0 | 10
39050.4769 | 2311 | 0 | 10
39050.4774 | 2341 | 0 | 10
39050.4779 | 2199 | 0 | 10
39050.4784 | 2376 | 0 | 10
39050.4789 | 2006 | 0 | 10
39050.4794 | 2054 | 0 | 10
39050.4799 | 2568 | 0 | 10
39050.4803 | 2269 | 0 | 10
39050.4808 | 2539 | 0 | 10
39050.4813 | 2571 | 0 | 10
39050.4818 | 2007 | 0 | 10
39050.4823 | 2407 | 0 | 10
39050.4828 | 2032 | 0 | 10
39050.4833 | 2572 | 0 | 10
39050.4837 | 2478 | 0 | 10
39050.4842 | 2346 | 0 | 10
39050.4847 | 2047 | 0 | 10
39050.4852 | 2525 | 0 | 10
39050.4857 | 2611 | 0 | 10
39050.4862 | 2085 | 0 | 10
39050.4867 | 2530 | 0 | 10
39050.4872 | 2597 | 0 | 10
39050.4876 | 2109 | 0 | 10
39050.4881 | 2293 | 0 | 10
39050.4886 | 2314 | 0 | 10
39050.4891 | 2508 | 0 | 10
39050.4896 | 2384 | 0 | 10
39050.4901 | 2599 | 0 | 10
39050.4906 | 2065 | 0 | 10
39050.491 | 2478 | 0 | 10
39050.4915 | 2006 | 0 | 10
39050.492 | 2069 | 0 | 10
39050.4925 | 2260 | 0 | 10
39050.493 | 2542 | 0 | 10
39050.4935 | 2250 | 0 | 10
10
39050.4687 | 1 | 0 | 11
39050.4692 | 1 | 0 | 11
39050.4697 | 0 | 0 | 11
39050.4702 | 1 | 0 | 11
39050.4706 | 1 | 0 | 11
39050.4711 | 1 | 0 | 11
39050.4716 | 1 | 0 | 11
39050.4721 | 1 | 0 | 11
39050.4726 | 1 | 0 | 11
39050.4731 | 0 | 0 | 11
39050.4736 | 1 | 0 | 11
39050.474 | 1 | 0 | 11
39050.4745 | 1 | 0 | 11
39050.475 | 1 | 0 | 11
39050.4755 | 1 | 0 | 11
39050.476 | 1 | 0 | 11
39050.4765 | 1 | 0 | 11
39050.477 | 1 | 0 | 11
39050.4774 | 1 | 0 | 11
39050.4779 | 2 | 0 | 11
39050.4784 | 1 | 0 | 11
39050.4789 | 285 | 0 | 11
39050.4794 | 1890 | 0 | 11
39050.4799 | 2359 | 0 | 11
39050.4804 | 2279 | 0 | 11
39050.4808 | 1876 | 0 | 11
39050.4813 | 1894 | 0 | 11
39050.4818 | 2435 | 0 | 11
39050.4823 | 2482 | 0 | 11
39050.4828 | 2391 | 0 | 11
39050.4833 | 2464 | 0 | 11
39050.4838 | 2370 | 0 | 11
39050.4842 | 2500 | 0 | 11
39050.4847 | 2196 | 0 | 11
39050.4852 | 2515 | 0 | 11
39050.4857 | 2307 | 0 | 11
39050.4862 | 2400 | 0 | 11
39050.4867 | 2413 | 0 | 11
39050.4872 | 2269 | 0 | 11
39050.4877 | 2114 | 0 | 11
39050.4881 | 2392 | 0 | 11
39050.4886 | 2304 | 0 | 11
39050.4891 | 2456 | 0 | 11
39050.4896 | 1994 | 0 | 11
39050.4901 | 2331 | 0 | 11
39050.4906 | 2216 | 0 | 11
39050.4911 | 2372 | 0 | 11
39050.4915 | 2174 | 0 | 11
39050.492 | 2467 | 0 | 11
39050.4925 | 1944 | 0 | 11
39050.493 | 1868 | 0 | 11
39050.4935 | 1886 | 0 | 11
11
39050.4687 | 1 | 0 | 12
39050.4692 | 1 | 0 | 12
39050.4697 | 1 | 0 | 12
39050.4702 | 1 | 0 | 12
39050.4707 | 1 | 0 | 12
39050.4711 | 1 | 0 | 12
39050.4716 | 1 | 0 | 12
39050.4721 | 1 | 0 | 12
39050.4726 | 1 | 0 | 12
39050.4731 | 1 | 0 | 12
39050.4736 | 1 | 0 | 12
39050.4741 | 1 | 0 | 12
39050.4745 | 1 | 0 | 12
39050.475 | 1 | 0 | 12
39050.4755 | 0 | 0 | 12
39050.476 | 1 | 0 | 12
39050.4765 | 1275 | 0 | 12
39050.477 | 1841 | 0 | 12
39050.4775 | 1967 | 0 | 12
39050.478 | 2463 | 0 | 12
39050.4784 | 1912 | 0 | 12
39050.4789 | 2156 | 0 | 12
39050.4794 | 1870 | 0 | 12
39050.4799 | 2014 | 0 | 12
39050.4804 | 2443 | 0 | 12
39050.4809 | 2561 | 0 | 12
39050.4814 | 2070 | 0 | 12
39050.4818 | 2015 | 0 | 12
39050.4823 | 2115 | 0 | 12
39050.4828 | 2028 | 0 | 12
39050.4833 | 2284 | 0 | 12
39050.4838 | 2511 | 0 | 12
39050.4843 | 2199 | 0 | 12
39050.4847 | 1955 | 0 | 12
39050.4852 | 2158 | 0 | 12
39050.4857 | 1938 | 0 | 12
39050.4862 | 2058 | 0 | 12
39050.4867 | 2313 | 0 | 12
39050.4872 | 2108 | 0 | 12
39050.4877 | 2051 | 0 | 12
39050.4881 | 1972 | 0 | 12
39050.4886 | 1877 | 0 | 12
39050.4891 | 2010 | 0 | 12
39050.4896 | 1893 | 0 | 12
39050.4901 | 2421 | 0 | 12
39050.4906 | 1844 | 0 | 12
39050.4911 | 2409 | 0 | 12
39050.4916 | 2008 | 0 | 12
39050.492 | 2098 | 0 | 12
39050.4925 | 2224 | 0 | 12
39050.493 | 1787 | 0 | 12
39050.4935 | 1830 | 0 | 12
12
39050.4687 | 1 | 0 | 13
39050.4692 | 1 | 0 | 13
39050.4697 | 1 | 0 | 13
39050.4702 | 1 | 0 | 13
39050.4707 | 1 | 0 | 13
39050.4712 | 1 | 0 | 13
39050.4716 | 1 | 0 | 13
39050.4721 | 1 | 0 | 13
39050.4726 | 1 | 0 | 13
39050.4731 | 1 | 0 | 13
39050.4736 | 1 | 0 | 13
39050.4741 | 0 | 0 | 13
39050.4746 | 0 | 0 | 13
39050.475 | 1 | 0 | 13
39050.4755 | 1 | 0 | 13
39050.476 | 1 | 0 | 13
39050.4765 | 1 | 0 | 13
39050.477 | 1 | 0 | 13
39050.4775 | 1 | 0 | 13
39050.478 | 1 | 0 | 13
39050.4784 | 4 | 0 | 13
39050.4789 | 283 | 0 | 13
39050.4794 | 1975 | 0 | 13
39050.4799 | 2249 | 0 | 13
39050.4804 | 1920 | 0 | 13
39050.4809 | 2316 | 0 | 13
39050.4814 | 2262 | 0 | 13
39050.4819 | 1981 | 0 | 13
39050.4823 | 2082 | 0 | 13
39050.4828 | 2467 | 0 | 13
39050.4833 | 1923 | 0 | 13
39050.4838 | 2084 | 0 | 13
39050.4843 | 2507 | 0 | 13
39050.4848 | 1930 | 0 | 13
39050.4853 | 2458 | 0 | 13
39050.4857 | 2373 | 0 | 13
39050.4862 | 2449 | 0 | 13
39050.4867 | 2149 | 0 | 13
39050.4872 | 2046 | 0 | 13
39050.4877 | 2260 | 0 | 13
39050.4882 | 2002 | 0 | 13
39050.4887 | 2453 | 0 | 13
39050.4891 | 2095 | 0 | 13
39050.4896 | 2180 | 0 | 13
39050.4901 | 1941 | 0 | 13
39050.4906 | 2158 | 0 | 13
39050.4911 | 1932 | 0 | 13
39050.4916 | 2482 | 0 | 13
39050.4921 | 2188 | 0 | 13
39050.4925 | 2407 | 0 | 13
39050.493 | 2123 | 0 | 13
39050.4935 | 1993 | 0 | 13
13
39050.4688 | 1 | 0 | 14
39050.4692 | 1 | 0 | 14
39050.4697 | 0 | 0 | 14
39050.4702 | 1 | 0 | 14
39050.4707 | 1 | 0 | 14
39050.4712 | 1 | 0 | 14
39050.4717 | 1 | 0 | 14
39050.4721 | 1 | 0 | 14
39050.4726 | 1 | 0 | 14
39050.4731 | 1 | 0 | 14
39050.4736 | 1 | 0 | 14
39050.4741 | 1 | 0 | 14
39050.4746 | 1 | 0 | 14
39050.4751 | 1 | 0 | 14
39050.4755 | 1 | 0 | 14
39050.476 | 1 | 0 | 14
39050.4765 | 1 | 0 | 14
39050.477 | 1 | 0 | 14
39050.4775 | 1 | 0 | 14
39050.478 | 1 | 0 | 14
39050.4785 | 2 | 0 | 14
39050.4789 | 364 | 0 | 14
39050.4794 | 2123 | 0 | 14
39050.4799 | 2009 | 0 | 14
39050.4804 | 2123 | 0 | 14
39050.4809 | 1886 | 0 | 14
39050.4814 | 2456 | 0 | 14
39050.4819 | 2182 | 0 | 14
39050.4823 | 2137 | 0 | 14
39050.4828 | 1992 | 0 | 14
39050.4833 | 2251 | 0 | 14
39050.4838 | 2119 | 0 | 14
39050.4843 | 2315 | 0 | 14
39050.4853 | 2359 | 0 | 14
39050.4858 | 2195 | 0 | 14
39050.4862 | 2467 | 0 | 14
39050.4867 | 1985 | 0 | 14
39050.4872 | 2367 | 0 | 14
39050.4877 | 2178 | 0 | 14
39050.4882 | 2491 | 0 | 14
39050.4887 | 2039 | 0 | 14
39050.4892 | 1994 | 0 | 14
39050.4896 | 2235 | 0 | 14
39050.4901 | 1990 | 0 | 14
39050.4906 | 2503 | 0 | 14
39050.4911 | 2478 | 0 | 14
39050.4916 | 2232 | 0 | 14
39050.4921 | 2113 | 0 | 14
39050.4926 | 2130 | 0 | 14
39050.493 | 2418 | 0 | 14
39050.4935 | 2406 | 0 | 14
14
39050.4688 | 1 | 0 | 15
39050.4692 | 1 | 0 | 15
39050.4697 | 1 | 0 | 15
39050.4702 | 0 | 0 | 15
39050.4707 | 1 | 0 | 15
39050.4712 | 1 | 0 | 15
39050.4717 | 1 | 0 | 15
39050.4722 | 1 | 0 | 15
39050.4727 | 1 | 0 | 15
39050.4731 | 1 | 0 | 15
39050.4736 | 1 | 0 | 15
39050.4741 | 1 | 0 | 15
39050.4746 | 1 | 0 | 15
39050.4751 | 1 | 0 | 15
39050.4756 | 1 | 0 | 15
39050.4761 | 1 | 0 | 15
39050.4765 | 1 | 0 | 15
39050.477 | 1 | 0 | 15
39050.4775 | 1 | 0 | 15
39050.478 | 1 | 0 | 15
39050.4785 | 3 | 0 | 15
39050.479 | 353 | 0 | 15
39050.4795 | 1774 | 0 | 15
39050.4799 | 1888 | 0 | 15
39050.4804 | 2420 | 0 | 15
39050.4809 | 2257 | 0 | 15
39050.4814 | 2019 | 0 | 15
39050.4819 | 2410 | 0 | 15
39050.4824 | 2155 | 0 | 15
39050.4829 | 2145 | 0 | 15
39050.4833 | 2390 | 0 | 15
39050.4838 | 2400 | 0 | 15
39050.4843 | 2421 | 0 | 15
39050.4848 | 2440 | 0 | 15
39050.4853 | 2125 | 0 | 15
39050.4858 | 2477 | 0 | 15
39050.4863 | 2317 | 0 | 15
39050.4867 | 1983 | 0 | 15
39050.4872 | 2450 | 0 | 15
39050.4877 | 2205 | 0 | 15
39050.4882 | 2388 | 0 | 15
39050.4887 | 2409 | 0 | 15
39050.4892 | 2079 | 0 | 15
39050.4897 | 2010 | 0 | 15
39050.4902 | 2369 | 0 | 15
39050.4906 | 2167 | 0 | 15
39050.4911 | 2282 | 0 | 15
39050.4916 | 2081 | 0 | 15
39050.4921 | 2205 | 0 | 15
39050.4926 | 1928 | 0 | 15
39050.4931 | 2287 | 0 | 15
39050.4936 | 2245 | 0 | 15
15
39050.4688 | 1 | 0 | 16
39050.4693 | 1 | 0 | 16
39050.4697 | 1 | 0 | 16
39050.4702 | 1 | 0 | 16
39050.4707 | 1 | 0 | 16
39050.4712 | 1 | 0 | 16
39050.4717 | 1 | 0 | 16
39050.4722 | 1 | 0 | 16
39050.4727 | 1 | 0 | 16
39050.4731 | 1 | 0 | 16
39050.4736 | 1 | 0 | 16
39050.4741 | 1 | 0 | 16
39050.4746 | 1 | 0 | 16
39050.4751 | 1 | 0 | 16
39050.4756 | 1 | 0 | 16
39050.4761 | 418 | 0 | 16
39050.4766 | 2269 | 0 | 16
39050.477 | 2462 | 0 | 16
39050.4775 | 2599 | 0 | 16
39050.478 | 2585 | 0 | 16
39050.4785 | 2129 | 0 | 16
39050.479 | 2239 | 0 | 16
39050.4795 | 2593 | 0 | 16
39050.48 | 2202 | 0 | 16
39050.4804 | 2578 | 0 | 16
39050.4809 | 2018 | 0 | 16
39050.4814 | 2588 | 0 | 16
39050.4819 | 2598 | 0 | 16
39050.4824 | 2458 | 0 | 16
39050.4829 | 2134 | 0 | 16
39050.4834 | 2371 | 0 | 16
39050.4838 | 2049 | 0 | 16
39050.4843 | 2595 | 0 | 16
39050.4848 | 2461 | 0 | 16
39050.4853 | 2495 | 0 | 16
39050.4858 | 2180 | 0 | 16
39050.4863 | 2554 | 0 | 16
39050.4868 | 2164 | 0 | 16
39050.4872 | 2472 | 0 | 16
39050.4877 | 2055 | 0 | 16
39050.4882 | 2593 | 0 | 16
39050.4887 | 2270 | 0 | 16
39050.4892 | 2296 | 0 | 16
39050.4897 | 2271 | 0 | 16
39050.4902 | 2558 | 0 | 16
39050.4906 | 2347 | 0 | 16
39050.4911 | 2588 | 0 | 16
39050.4916 | 2372 | 0 | 16
39050.4921 | 2505 | 0 | 16
39050.4926 | 2055 | 0 | 16
39050.4931 | 2508 | 0 | 16
39050.4936 | 2165 | 0 | 16
16
39050.4688 | 1 | 0 | 17
39050.4693 | 1 | 0 | 17
39050.4698 | 1 | 0 | 17
39050.4703 | 1 | 0 | 17
39050.4707 | 1 | 0 | 17
39050.4712 | 1 | 0 | 17
39050.4717 | 1 | 0 | 17
39050.4722 | 1 | 0 | 17
39050.4727 | 1 | 0 | 17
39050.4732 | 0 | 0 | 17
39050.4737 | 1 | 0 | 17
39050.4741 | 1 | 0 | 17
39050.4746 | 1 | 0 | 17
39050.4751 | 1 | 0 | 17
39050.4756 | 1 | 0 | 17
39050.4761 | 1 | 0 | 17
39050.4766 | 1 | 0 | 17
39050.4771 | 1 | 0 | 17
39050.4775 | 2 | 0 | 17
39050.478 | 1 | 0 | 17
39050.4785 | 7 | 0 | 17
39050.479 | 491 | 0 | 17
39050.4795 | 2153 | 0 | 17
39050.48 | 1986 | 0 | 17
39050.4805 | 2032 | 0 | 17
39050.4809 | 2032 | 0 | 17
39050.4814 | 1991 | 0 | 17
39050.4819 | 2318 | 0 | 17
39050.4824 | 2327 | 0 | 17
39050.4829 | 2278 | 0 | 17
39050.4834 | 1987 | 0 | 17
39050.4839 | 2337 | 0 | 17
39050.4843 | 2437 | 0 | 17
39050.4848 | 1954 | 0 | 17
39050.4853 | 2247 | 0 | 17
39050.4858 | 1955 | 0 | 17
39050.4863 | 2291 | 0 | 17
39050.4868 | 1939 | 0 | 17
39050.4873 | 2418 | 0 | 17
39050.4877 | 2274 | 0 | 17
39050.4882 | 2415 | 0 | 17
39050.4887 | 2424 | 0 | 17
39050.4892 | 2388 | 0 | 17
39050.4897 | 1997 | 0 | 17
39050.4902 | 2081 | 0 | 17
39050.4907 | 2076 | 0 | 17
39050.4911 | 2127 | 0 | 17
39050.4916 | 2423 | 0 | 17
39050.4921 | 2386 | 0 | 17
39050.4926 | 1926 | 0 | 17
39050.4931 | 2055 | 0 | 17
39050.4936 | 2210 | 0 | 17
17
39050.4693 | 1 | 0 | 18
39050.4698 | 0 | 0 | 18
39050.4703 | 1 | 0 | 18
39050.4708 | 1 | 0 | 18
39050.4712 | 0 | 0 | 18
39050.4717 | 1 | 0 | 18
39050.4722 | 1 | 0 | 18
39050.4727 | 1 | 0 | 18
39050.4732 | 1 | 0 | 18
39050.4737 | 1 | 0 | 18
39050.4742 | 1 | 0 | 18
39050.4746 | 1 | 0 | 18
39050.4751 | 1 | 0 | 18
39050.4756 | 1 | 0 | 18
39050.4761 | 2085 | 0 | 18
39050.4766 | 2385 | 0 | 18
39050.4771 | 2054 | 0 | 18
39050.4776 | 2445 | 0 | 18
39050.478 | 2028 | 0 | 18
39050.4785 | 2534 | 0 | 18
39050.479 | 2560 | 0 | 18
39050.4795 | 2522 | 0 | 18
39050.48 | 2282 | 0 | 18
39050.4805 | 2377 | 0 | 18
39050.481 | 2264 | 0 | 18
39050.4814 | 2517 | 0 | 18
39050.4819 | 2611 | 0 | 18
39050.4824 | 2512 | 0 | 18
39050.4829 | 2117 | 0 | 18
39050.4834 | 2101 | 0 | 18
39050.4839 | 2373 | 0 | 18
39050.4844 | 2452 | 0 | 18
39050.4848 | 2004 | 0 | 18
39050.4853 | 2260 | 0 | 18
39050.4858 | 2546 | 0 | 18
39050.4863 | 2607 | 0 | 18
39050.4868 | 2380 | 0 | 18
39050.4873 | 2146 | 0 | 18
39050.4878 | 2379 | 0 | 18
39050.4883 | 2271 | 0 | 18
39050.4887 | 2372 | 0 | 18
39050.4892 | 2534 | 0 | 18
39050.4897 | 2221 | 0 | 18
39050.4902 | 2255 | 0 | 18
39050.4907 | 2248 | 0 | 18
39050.4912 | 2138 | 0 | 18
39050.4917 | 2353 | 0 | 18
39050.4921 | 2070 | 0 | 18
39050.4926 | 2545 | 0 | 18
39050.4931 | 2135 | 0 | 18
39050.4936 | 2496 | 0 | 18
18
39050.4688 | 1 | 0 | 19
39050.4693 | 1 | 0 | 19
39050.4698 | 1 | 0 | 19
39050.4703 | 1 | 0 | 19
39050.4708 | 1 | 0 | 19
39050.4713 | 1 | 0 | 19
39050.4717 | 1 | 0 | 19
39050.4722 | 1 | 0 | 19
39050.4727 | 1 | 0 | 19
39050.4732 | 1 | 0 | 19
39050.4737 | 1 | 0 | 19
39050.4742 | 1 | 0 | 19
39050.4747 | 1 | 0 | 19
39050.4751 | 1 | 0 | 19
39050.4756 | 1 | 0 | 19
39050.4761 | 1 | 0 | 19
39050.4766 | 1411 | 0 | 19
39050.4771 | 375 | 0 | 19
39050.4776 | 2163 | 1 | 19
39050.4781 | 2038 | 5 | 19
39050.4785 | 2151 | 0 | 19
39050.479 | 2371 | 0 | 19
39050.4795 | 1867 | 12 | 19
39050.48 | 2457 | 0 | 19
39050.4805 | 2474 | 0 | 19
39050.481 | 2475 | 0 | 19
39050.4815 | 2019 | 0 | 19
39050.4819 | 2024 | 0 | 19
39050.4824 | 2349 | 0 | 19
39050.4829 | 2505 | 0 | 19
39050.4834 | 2081 | 0 | 19
39050.4839 | 2456 | 0 | 19
39050.4844 | 1936 | 0 | 19
39050.4849 | 2260 | 0 | 19
39050.4853 | 1926 | 0 | 19
39050.4858 | 1739 | 0 | 19
39050.4863 | 1770 | 0 | 19
39050.4868 | 1959 | 0 | 19
39050.4873 | 1866 | 0 | 19
39050.4878 | 2242 | 0 | 19
39050.4883 | 2111 | 0 | 19
39050.4887 | 2277 | 0 | 19
39050.4892 | 2218 | 0 | 19
39050.4897 | 2295 | 0 | 19
39050.4902 | 2032 | 1 | 19
39050.4907 | 2034 | 1 | 19
39050.4912 | 2359 | 0 | 19
39050.4917 | 2276 | 4 | 19
39050.4922 | 1812 | 24 | 19
39050.4926 | 1771 | 41 | 19
39050.4931 | 2077 | 54 | 19
39050.4936 | 1681 | 78 | 19
19
39050.4688 | 1 | 0 | 20
39050.4693 | 1 | 0 | 20
39050.4698 | 1 | 0 | 20
39050.4703 | 0 | 0 | 20
39050.4708 | 1 | 0 | 20
39050.4713 | 1 | 0 | 20
39050.4718 | 1 | 0 | 20
39050.4722 | 1 | 0 | 20
39050.4727 | 1 | 0 | 20
39050.4732 | 1 | 0 | 20
39050.4737 | 1 | 0 | 20
39050.4742 | 1 | 0 | 20
39050.4747 | 1 | 0 | 20
39050.4752 | 1 | 0 | 20
39050.4756 | 1 | 0 | 20
39050.4761 | 1 | 0 | 20
39050.4766 | 1 | 0 | 20
39050.4771 | 1304 | 0 | 20
39050.4776 | 2002 | 2 | 20
39050.4781 | 2136 | 0 | 20
39050.4786 | 2269 | 0 | 20
39050.4791 | 2399 | 0 | 20
39050.4795 | 1940 | 82 | 20
39050.48 | 2384 | 0 | 20
39050.4805 | 2376 | 0 | 20
39050.481 | 1999 | 0 | 20
39050.4815 | 2402 | 0 | 20
39050.482 | 2205 | 0 | 20
39050.4825 | 2533 | 0 | 20
39050.4829 | 2322 | 0 | 20
39050.4834 | 2502 | 0 | 20
39050.4839 | 1926 | 0 | 20
39050.4844 | 2030 | 0 | 20
39050.4849 | 2307 | 0 | 20
39050.4854 | 1968 | 0 | 20
39050.4859 | 2095 | 0 | 20
39050.4863 | 2392 | 0 | 20
39050.4868 | 2290 | 0 | 20
39050.4873 | 2233 | 0 | 20
39050.4878 | 2022 | 0 | 20
39050.4883 | 2085 | 0 | 20
39050.4888 | 2458 | 0 | 20
39050.4893 | 1938 | 0 | 20
39050.4897 | 2354 | 0 | 20
39050.4902 | 1863 | 1 | 20
39050.4907 | 2071 | 1 | 20
39050.4912 | 1987 | 0 | 20
39050.4917 | 2034 | 16 | 20
39050.4922 | 1789 | 24 | 20
39050.4927 | 1952 | 49 | 20
39050.4931 | 1988 | 59 | 20
39050.4936 | 2006 | 102 | 20
20
39050.4689 | 1 | 0 | 21
39050.4693 | 1 | 0 | 21
39050.4698 | 1 | 0 | 21
39050.4703 | 1 | 0 | 21
39050.4708 | 1 | 0 | 21
39050.4713 | 1 | 0 | 21
39050.4718 | 0 | 0 | 21
39050.4723 | 1 | 0 | 21
39050.4727 | 1 | 0 | 21
39050.4732 | 1 | 0 | 21
39050.4737 | 1 | 0 | 21
39050.4742 | 1 | 0 | 21
39050.4747 | 1 | 0 | 21
39050.4752 | 1 | 0 | 21
39050.4757 | 1 | 0 | 21
39050.4761 | 1 | 0 | 21
39050.4766 | 2275 | 0 | 21
39050.4771 | 1652 | 0 | 21
39050.4776 | 2078 | 0 | 21
39050.4781 | 2352 | 0 | 21
39050.4786 | 2033 | 0 | 21
39050.4791 | 2283 | 0 | 21
39050.4795 | 2069 | 0 | 21
39050.48 | 2474 | 0 | 21
39050.4805 | 2410 | 0 | 21
39050.481 | 2090 | 0 | 21
39050.4815 | 2421 | 0 | 21
39050.482 | 2158 | 0 | 21
39050.4825 | 2053 | 0 | 21
39050.483 | 2095 | 0 | 21
39050.4834 | 2409 | 0 | 21
39050.4839 | 2133 | 0 | 21
39050.4844 | 2109 | 0 | 21
39050.4849 | 1800 | 0 | 21
39050.4854 | 1732 | 0 | 21
39050.4859 | 2214 | 0 | 21
39050.4864 | 1812 | 0 | 21
39050.4868 | 1762 | 0 | 21
39050.4873 | 2160 | 0 | 21
39050.4878 | 2352 | 0 | 21
39050.4883 | 1852 | 0 | 21
39050.4888 | 1992 | 0 | 21
39050.4893 | 2245 | 0 | 21
39050.4898 | 2210 | 0 | 21
39050.4902 | 2365 | 0 | 21
39050.4907 | 2284 | 0 | 21
39050.4912 | 1958 | 0 | 21
39050.4917 | 2292 | 0 | 21
39050.4922 | 2031 | 0 | 21
39050.4927 | 1938 | 0 | 21
39050.4932 | 1755 | 0 | 21
39050.4936 | 1841 | 0 | 21
21
39050.4689 | 1 | 0 | 22
39050.4694 | 1 | 0 | 22
39050.4698 | 1 | 0 | 22
39050.4703 | 1 | 0 | 22
39050.4708 | 1 | 0 | 22
39050.4713 | 1 | 0 | 22
39050.4718 | 1 | 0 | 22
39050.4723 | 1 | 0 | 22
39050.4728 | 1 | 0 | 22
39050.4733 | 1 | 0 | 22
39050.4737 | 0 | 0 | 22
39050.4742 | 1 | 0 | 22
39050.4747 | 1 | 0 | 22
39050.4752 | 1 | 0 | 22
39050.4757 | 3 | 0 | 22
39050.4762 | 2496 | 0 | 22
39050.4767 | 2007 | 0 | 22
39050.4771 | 2207 | 0 | 22
39050.4776 | 1987 | 0 | 22
39050.4781 | 2598 | 0 | 22
39050.4786 | 2430 | 0 | 22
39050.4791 | 2265 | 0 | 22
39050.4796 | 2169 | 0 | 22
39050.4801 | 2426 | 0 | 22
39050.4805 | 2423 | 0 | 22
39050.481 | 2223 | 0 | 22
39050.4815 | 2440 | 0 | 22
39050.482 | 2259 | 0 | 22
39050.4825 | 2285 | 0 | 22
39050.483 | 2232 | 0 | 22
39050.4835 | 2385 | 0 | 22
39050.4839 | 2010 | 0 | 22
39050.4844 | 2471 | 0 | 22
39050.4849 | 2439 | 0 | 22
39050.4854 | 2587 | 0 | 22
39050.4859 | 2537 | 0 | 22
39050.4864 | 2016 | 0 | 22
39050.4869 | 2052 | 0 | 22
39050.4873 | 2345 | 0 | 22
39050.4878 | 2444 | 0 | 22
39050.4883 | 2123 | 0 | 22
39050.4888 | 2014 | 0 | 22
39050.4893 | 2450 | 0 | 22
39050.4898 | 2469 | 0 | 22
39050.4903 | 2118 | 0 | 22
39050.4907 | 2107 | 0 | 22
39050.4912 | 2150 | 0 | 22
39050.4917 | 2011 | 0 | 22
39050.4922 | 2521 | 0 | 22
39050.4927 | 2212 | 0 | 22
39050.4932 | 2024 | 0 | 22
39050.4937 | 2151 | 0 | 22
22
39050.4689 | 1 | 0 | 23
39050.4694 | 1 | 0 | 23
39050.4699 | 1 | 0 | 23
39050.4703 | 1 | 0 | 23
39050.4708 | 1 | 0 | 23
39050.4713 | 1 | 0 | 23
39050.4718 | 1 | 0 | 23
39050.4723 | 1 | 0 | 23
39050.4728 | 1 | 0 | 23
39050.4733 | 1 | 0 | 23
39050.4737 | 1 | 0 | 23
39050.4742 | 1 | 0 | 23
39050.4747 | 1 | 0 | 23
39050.4752 | 1 | 0 | 23
39050.4757 | 1 | 0 | 23
39050.4762 | 1 | 0 | 23
39050.4767 | 1921 | 0 | 23
39050.4772 | 298 | 0 | 23
39050.4776 | 2001 | 0 | 23
39050.4781 | 2267 | 0 | 23
39050.4786 | 2469 | 0 | 23
39050.4791 | 1987 | 0 | 23
39050.4796 | 2170 | 0 | 23
39050.4801 | 2185 | 0 | 23
39050.4806 | 2088 | 0 | 23
39050.481 | 2398 | 0 | 23
39050.4815 | 2468 | 0 | 23
39050.482 | 2310 | 0 | 23
39050.4825 | 2164 | 0 | 23
39050.483 | 2163 | 0 | 23
39050.4835 | 2434 | 0 | 23
39050.484 | 2146 | 0 | 23
39050.4844 | 2410 | 0 | 23
39050.4849 | 2006 | 0 | 23
39050.4854 | 2099 | 0 | 23
39050.4859 | 1793 | 0 | 23
39050.4864 | 1862 | 0 | 23
39050.4869 | 2092 | 0 | 23
39050.4874 | 1887 | 0 | 23
39050.4878 | 1896 | 0 | 23
39050.4883 | 1892 | 0 | 23
39050.4888 | 2095 | 0 | 23
39050.4893 | 2179 | 0 | 23
39050.4898 | 2156 | 0 | 23
39050.4903 | 1984 | 0 | 23
39050.4908 | 1983 | 0 | 23
39050.4912 | 2205 | 0 | 23
39050.4917 | 1812 | 0 | 23
39050.4922 | 2088 | 0 | 23
39050.4927 | 1849 | 0 | 23
39050.4932 | 1951 | 0 | 23
39050.4937 | 1954 | 0 | 23
23
39050.4689 | 1 | 0 | 24
39050.4694 | 1 | 0 | 24
39050.4699 | 0 | 0 | 24
39050.4704 | 1 | 0 | 24
39050.4708 | 1 | 0 | 24
39050.4713 | 1 | 0 | 24
39050.4718 | 1 | 0 | 24
39050.4723 | 1 | 0 | 24
39050.4728 | 1 | 0 | 24
39050.4733 | 1 | 0 | 24
39050.4738 | 1 | 0 | 24
39050.4742 | 1 | 0 | 24
39050.4747 | 1 | 0 | 24
39050.4752 | 1 | 0 | 24
39050.4757 | 1 | 0 | 24
39050.4762 | 1982 | 0 | 24
39050.4767 | 2242 | 0 | 24
39050.4772 | 2146 | 0 | 24
39050.4777 | 2471 | 0 | 24
39050.4781 | 2247 | 0 | 24
39050.4786 | 2336 | 0 | 24
39050.4791 | 2515 | 0 | 24
39050.4796 | 2284 | 0 | 24
39050.4801 | 2043 | 0 | 24
39050.4806 | 2549 | 0 | 24
39050.4811 | 2256 | 0 | 24
39050.4815 | 2528 | 0 | 24
39050.482 | 2212 | 0 | 24
39050.4825 | 2081 | 0 | 24
39050.483 | 2139 | 0 | 24
39050.4835 | 2017 | 0 | 24
39050.484 | 2538 | 0 | 24
39050.4845 | 2030 | 0 | 24
39050.4849 | 2560 | 0 | 24
39050.4854 | 2042 | 0 | 24
39050.4859 | 2260 | 0 | 24
39050.4864 | 2400 | 0 | 24
39050.4869 | 1991 | 0 | 24
39050.4874 | 1986 | 0 | 24
39050.4879 | 2401 | 0 | 24
39050.4883 | 2200 | 0 | 24
39050.4888 | 2327 | 0 | 24
39050.4893 | 2577 | 0 | 24
39050.4898 | 2153 | 0 | 24
39050.4903 | 2195 | 0 | 24
39050.4908 | 2000 | 0 | 24
39050.4913 | 2246 | 0 | 24
39050.4917 | 2584 | 0 | 24
39050.4922 | 2211 | 0 | 24
39050.4927 | 2366 | 0 | 24
39050.4932 | 2032 | 0 | 24
39050.4937 | 2535 | 0 | 24
24
39050.4689 | 1 | 0 | 25
39050.4694 | 1 | 0 | 25
39050.4699 | 1 | 0 | 25
39050.4704 | 1 | 0 | 25
39050.4709 | 1 | 0 | 25
39050.4714 | 1 | 0 | 25
39050.4718 | 1 | 0 | 25
39050.4723 | 1 | 0 | 25
39050.4728 | 1 | 0 | 25
39050.4733 | 1 | 0 | 25
39050.4738 | 1 | 0 | 25
39050.4743 | 1 | 0 | 25
39050.4748 | 1 | 0 | 25
39050.4752 | 1 | 0 | 25
39050.4757 | 1 | 0 | 25
39050.4762 | 1 | 0 | 25
39050.4767 | 1 | 0 | 25
39050.4772 | 1021 | 0 | 25
39050.4777 | 2242 | 0 | 25
39050.4782 | 1914 | 0 | 25
39050.4786 | 2438 | 0 | 25
39050.4791 | 2113 | 0 | 25
39050.4796 | 1836 | 0 | 25
39050.4801 | 2215 | 0 | 25
39050.4806 | 2415 | 0 | 25
39050.4811 | 2016 | 0 | 25
39050.4816 | 2021 | 0 | 25
39050.482 | 2214 | 0 | 25
39050.4825 | 1966 | 0 | 25
39050.483 | 2238 | 0 | 25
39050.4835 | 2434 | 0 | 25
39050.484 | 2447 | 0 | 25
39050.4845 | 2336 | 0 | 25
39050.485 | 2394 | 0 | 25
39050.4855 | 2190 | 0 | 25
39050.4859 | 2081 | 0 | 25
39050.4864 | 2403 | 0 | 25
39050.4869 | 1929 | 0 | 25
39050.4874 | 2029 | 0 | 25
39050.4879 | 2176 | 0 | 25
39050.4884 | 2292 | 0 | 25
39050.4889 | 2357 | 0 | 25
39050.4893 | 2110 | 0 | 25
39050.4898 | 1972 | 0 | 25
39050.4903 | 1842 | 0 | 25
39050.4908 | 2362 | 0 | 25
39050.4913 | 2127 | 0 | 25
39050.4918 | 1790 | 0 | 25
39050.4923 | 1747 | 0 | 25
39050.4927 | 2109 | 0 | 25
39050.4932 | 1796 | 0 | 25
39050.4937 | 2028 | 0 | 25
25
39050.4689 | 1 | 0 | 26
39050.4694 | 1 | 0 | 26
39050.4699 | 1 | 0 | 26
39050.4704 | 1 | 0 | 26
39050.4709 | 1 | 0 | 26
39050.4714 | 1 | 0 | 26
39050.4719 | 1 | 0 | 26
39050.4723 | 1 | 0 | 26
39050.4728 | 1 | 0 | 26
39050.4733 | 1 | 0 | 26
39050.4738 | 1 | 0 | 26
39050.4743 | 1 | 0 | 26
39050.4748 | 1 | 0 | 26
39050.4753 | 1 | 0 | 26
39050.4757 | 1936 | 0 | 26
39050.4762 | 2291 | 0 | 26
39050.4767 | 2092 | 0 | 26
39050.4772 | 2197 | 0 | 26
39050.4777 | 2181 | 0 | 26
39050.4782 | 2158 | 0 | 26
39050.4787 | 2014 | 0 | 26
39050.4791 | 2449 | 0 | 26
39050.4796 | 2270 | 0 | 26
39050.4801 | 2481 | 0 | 26
39050.4806 | 2566 | 0 | 26
39050.4811 | 2266 | 0 | 26
39050.4816 | 2100 | 0 | 26
39050.4821 | 2169 | 0 | 26
39050.4825 | 2184 | 0 | 26
39050.483 | 2483 | 0 | 26
39050.4835 | 2404 | 0 | 26
39050.484 | 2087 | 0 | 26
39050.4845 | 2316 | 0 | 26
39050.485 | 2055 | 0 | 26
39050.4855 | 2568 | 0 | 26
39050.4859 | 2553 | 0 | 26
39050.4864 | 2321 | 0 | 26
39050.4869 | 2053 | 0 | 26
39050.4874 | 2400 | 0 | 26
39050.4879 | 2233 | 0 | 26
39050.4884 | 2584 | 0 | 26
39050.4889 | 2218 | 0 | 26
39050.4894 | 2441 | 0 | 26
39050.4898 | 2153 | 0 | 26
39050.4903 | 2550 | 0 | 26
39050.4908 | 2023 | 0 | 26
39050.4913 | 2500 | 0 | 26
39050.4918 | 2155 | 0 | 26
39050.4923 | 2146 | 0 | 26
39050.4928 | 2307 | 0 | 26
39050.4932 | 2096 | 0 | 26
39050.4937 | 2323 | 0 | 26
26
39050.469 | 1 | 0 | 27
39050.4694 | 1 | 0 | 27
39050.4699 | 1 | 0 | 27
39050.4704 | 1 | 0 | 27
39050.4709 | 1 | 0 | 27
39050.4714 | 1 | 0 | 27
39050.4719 | 1 | 0 | 27
39050.4724 | 1 | 0 | 27
39050.4728 | 1 | 0 | 27
39050.4733 | 1 | 0 | 27
39050.4738 | 1 | 0 | 27
39050.4743 | 0 | 0 | 27
39050.4748 | 1 | 0 | 27
39050.4753 | 1 | 0 | 27
39050.4758 | 1 | 0 | 27
39050.4762 | 1 | 0 | 27
39050.4767 | 1 | 0 | 27
39050.4772 | 1358 | 0 | 27
39050.4777 | 2196 | 0 | 27
39050.4782 | 1954 | 0 | 27
39050.4787 | 2121 | 0 | 27
39050.4792 | 1920 | 0 | 27
39050.4797 | 2322 | 0 | 27
39050.4801 | 2350 | 0 | 27
39050.4806 | 2377 | 0 | 27
39050.4811 | 2484 | 0 | 27
39050.4816 | 2376 | 0 | 27
39050.4821 | 2578 | 0 | 27
39050.4826 | 2368 | 0 | 27
39050.4831 | 2309 | 0 | 27
39050.4835 | 2083 | 0 | 27
39050.484 | 2000 | 0 | 27
39050.4845 | 2036 | 0 | 27
39050.485 | 2295 | 0 | 27
39050.4855 | 2301 | 0 | 27
39050.486 | 1877 | 0 | 27
39050.4864 | 2396 | 0 | 27
39050.4869 | 2347 | 0 | 27
39050.4874 | 1917 | 0 | 27
39050.4879 | 2267 | 0 | 27
39050.4884 | 1881 | 0 | 27
39050.4889 | 2450 | 0 | 27
39050.4894 | 2376 | 0 | 27
39050.4898 | 1888 | 0 | 27
39050.4903 | 2175 | 0 | 27
39050.4908 | 2353 | 0 | 27
39050.4913 | 1866 | 0 | 27
39050.4918 | 2113 | 0 | 27
39050.4923 | 2052 | 0 | 27
39050.4928 | 1783 | 0 | 27
39050.4933 | 2158 | 0 | 27
39050.4937 | 1664 | 0 | 27
27
39050.469 | 1 | 0 | 28
39050.4695 | 1 | 0 | 28
39050.4699 | 1 | 0 | 28
39050.4704 | 1 | 0 | 28
39050.4709 | 1 | 0 | 28
39050.4714 | 1 | 0 | 28
39050.4719 | 1 | 0 | 28
39050.4724 | 1 | 0 | 28
39050.4729 | 1 | 0 | 28
39050.4733 | 1 | 0 | 28
39050.4738 | 0 | 0 | 28
39050.4743 | 1 | 0 | 28
39050.4748 | 1 | 0 | 28
39050.4753 | 1 | 0 | 28
39050.4758 | 1 | 0 | 28
39050.4763 | 2011 | 0 | 28
39050.4767 | 1559 | 0 | 28
39050.4772 | 2231 | 0 | 28
39050.4777 | 2473 | 0 | 28
39050.4782 | 2228 | 0 | 28
39050.4787 | 2034 | 0 | 28
39050.4792 | 2532 | 0 | 28
39050.4797 | 2263 | 0 | 28
39050.4802 | 2027 | 0 | 28
39050.4806 | 2000 | 0 | 28
39050.4811 | 1999 | 0 | 28
39050.4816 | 2168 | 0 | 28
39050.4821 | 2591 | 0 | 28
39050.4826 | 2142 | 0 | 28
39050.4831 | 2199 | 0 | 28
39050.4836 | 2297 | 0 | 28
39050.484 | 1996 | 0 | 28
39050.4845 | 2279 | 0 | 28
39050.485 | 2594 | 0 | 28
39050.4855 | 2464 | 0 | 28
39050.486 | 2446 | 0 | 28
39050.4865 | 2089 | 0 | 28
39050.487 | 2365 | 0 | 28
39050.4874 | 1983 | 0 | 28
39050.4879 | 2108 | 0 | 28
39050.4884 | 2550 | 0 | 28
39050.4889 | 2463 | 0 | 28
39050.4894 | 2598 | 0 | 28
39050.4899 | 2155 | 0 | 28
39050.4904 | 2537 | 0 | 28
39050.4908 | 2154 | 0 | 28
39050.4913 | 2074 | 0 | 28
39050.4918 | 2284 | 0 | 28
39050.4923 | 2463 | 0 | 28
39050.4928 | 2284 | 0 | 28
39050.4933 | 1995 | 0 | 28
39050.4938 | 2173 | 0 | 28
28
39050.469 | 1 | 0 | 29
39050.4695 | 1 | 0 | 29
39050.47 | 1 | 0 | 29
39050.4704 | 1 | 0 | 29
39050.4709 | 1 | 0 | 29
39050.4714 | 1 | 0 | 29
39050.4719 | 1 | 0 | 29
39050.4724 | 1 | 0 | 29
39050.4729 | 1 | 0 | 29
39050.4734 | 1 | 0 | 29
39050.4738 | 1 | 0 | 29
39050.4743 | 1 | 0 | 29
39050.4748 | 1 | 0 | 29
39050.4753 | 1 | 0 | 29
39050.4758 | 1938 | 0 | 29
39050.4763 | 2048 | 0 | 29
39050.4768 | 2411 | 0 | 29
39050.4772 | 2147 | 0 | 29
39050.4777 | 2428 | 0 | 29
39050.4782 | 1990 | 0 | 29
39050.4787 | 2150 | 0 | 29
39050.4792 | 2001 | 0 | 29
39050.4797 | 2126 | 0 | 29
39050.4802 | 2258 | 0 | 29
39050.4806 | 2062 | 0 | 29
39050.4811 | 2589 | 0 | 29
39050.4816 | 2277 | 0 | 29
39050.4821 | 2423 | 0 | 29
39050.4826 | 2270 | 0 | 29
39050.4831 | 2587 | 0 | 29
39050.4836 | 2539 | 0 | 29
39050.4841 | 2275 | 0 | 29
39050.4845 | 2515 | 0 | 29
39050.485 | 2457 | 0 | 29
39050.4855 | 2090 | 0 | 29
39050.486 | 2364 | 0 | 29
39050.4865 | 2157 | 0 | 29
39050.487 | 2134 | 0 | 29
39050.4875 | 2425 | 0 | 29
39050.4879 | 2331 | 0 | 29
39050.4884 | 2011 | 0 | 29
39050.4889 | 2132 | 0 | 29
39050.4894 | 2109 | 0 | 29
39050.4899 | 2303 | 0 | 29
39050.4904 | 2265 | 0 | 29
39050.4909 | 2477 | 0 | 29
39050.4913 | 2115 | 0 | 29
39050.4918 | 2360 | 0 | 29
39050.4923 | 2525 | 0 | 29
39050.4928 | 2108 | 0 | 29
39050.4933 | 2099 | 0 | 29
39050.4938 | 2101 | 0 | 29
29
39050.469 | 1 | 0 | 30
39050.4695 | 1 | 0 | 30
39050.47 | 1 | 0 | 30
39050.4705 | 1 | 0 | 30
39050.4709 | 1 | 0 | 30
39050.4714 | 1 | 0 | 30
39050.4719 | 1 | 0 | 30
39050.4724 | 1 | 0 | 30
39050.4729 | 1 | 0 | 30
39050.4734 | 1 | 0 | 30
39050.4739 | 1 | 0 | 30
39050.4744 | 1 | 0 | 30
39050.4748 | 1 | 0 | 30
39050.4753 | 1 | 0 | 30
39050.4758 | 1 | 0 | 30
39050.4763 | 2204 | 0 | 30
39050.4768 | 409 | 0 | 30
39050.4773 | 2076 | 0 | 30
39050.4778 | 2125 | 0 | 30
39050.4782 | 2080 | 0 | 30
39050.4787 | 2323 | 0 | 30
39050.4792 | 2200 | 0 | 30
39050.4797 | 2031 | 0 | 30
39050.4802 | 2441 | 0 | 30
39050.4807 | 2341 | 0 | 30
39050.4812 | 2350 | 0 | 30
39050.4816 | 2546 | 0 | 30
39050.4821 | 2132 | 0 | 30
39050.4826 | 2601 | 0 | 30
39050.4831 | 2554 | 0 | 30
39050.4836 | 2502 | 0 | 30
39050.4841 | 2511 | 0 | 30
39050.4846 | 2546 | 0 | 30
39050.485 | 2596 | 0 | 30
39050.4855 | 2104 | 0 | 30
39050.486 | 2556 | 0 | 30
39050.4865 | 2338 | 0 | 30
39050.487 | 2056 | 0 | 30
39050.4875 | 2357 | 0 | 30
39050.488 | 2023 | 0 | 30
39050.4884 | 2108 | 0 | 30
39050.4889 | 2014 | 0 | 30
39050.4894 | 2320 | 0 | 30
39050.4899 | 2524 | 0 | 30
39050.4904 | 2320 | 0 | 30
39050.4909 | 2524 | 0 | 30
39050.4914 | 2497 | 0 | 30
39050.4919 | 2140 | 0 | 30
39050.4923 | 2535 | 0 | 30
39050.4928 | 2233 | 0 | 30
39050.4933 | 2174 | 0 | 30
39050.4938 | 1994 | 0 | 30
30

## Test Facts
Last row in IRMS data sheets: | 57
Time when gas burner was ignited: | 632